## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 49
Test conditions: Cable: 7-conductor, 12 AWG, one XLPE insulated control cable with one EPR insulated control cable and one PE insulated control cable (cable items #10, #2 & #15). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable (EPR) was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 125 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
125 | 0 | Initated Penlight Heating
1635 | 1510 | Conductors C5 & C6 short together at less than 100 ohms (64) | Cable C is shorted internally
1784-1787 | 1659-1662 | Conductors B3 & B4 both short to ground at less than 100 ohms (20 & 75) | Cable B shorts to ground
1789 | 1664 | Conductors B3 & B4 short together at less than 1000 ohms (289) | Cable B is shorted internally
1790 | 1665 | Conductor C5 shorts to ground at less than 1000 ohms (315) | Cable C partially shorts to ground
1806 | 1681 | Conductors A1 & A2 short together at less than 1000 ohms (906) | Cable A is shorted internally
1831 | 1706 | The existing short between conductors B3 & B4 decreases to less than 100 ohms (43)
1848 | 1723 | The existing short between conductors A1 & A2 decreases to less than 100 ohms (9)
1854-1863 | 1729-1738 | Conductors A1 & A2 both short to ground at less than 1000 ohms (255 & 307) | Cable A shorts to ground
1873-1876 | 1748-1751 | The existing ground fault on conductor C5 decreases to less than 100 ohms (17), and conductor C6 shorts to ground at less than 1000 ohms (180) | Cable C shorts to ground
2730 | 2605 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures progressed somewhat as expected during this test: the two lower cables (B & C) shorted to ground (at least partially) before the top cable (A)
Observation 2 | It took 1510 seconds (25.2 min.) from the start of Penlight heating for the first internal short to occur, and it took 1659 s (27.7 min.) for the first short to ground failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.
Observation 4 | Several shorting failures, internal and to ground, occurred over a very short time period (1784-1806)

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cable A = XLPE (item #10)
Cable B = EPR (item #2)
Cable C = PE (item #15)
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 49 |  |  | 2006-08-31 | 12:58
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-124.5 | 211201.9994 | -122 | 252337.9994 | -119.5 | 254437.9994 | -116.5 | 243437.9994 | -113.5 | 251137.9994 | -111 | 246837.9994 | -108 | 211002.0947 | -105.5 | 243037.9994 | -102.5 | 244938.0816 | -99.5 | 252238.0792 | -96.5 | 250937.9994 | -94 | 252937.9994 | -91.5 | 253037.9994 | -88.5 | 252837.9994 | -85.5 | 250737.9994 | -124.5 | 211002.0947
-82.5 | 211201.9994 | -80 | 252337.9994 | -77.5 | 254437.9994 | -74.5 | 243437.9994 | -71.5 | 251137.9994 | -68.5 | 246638.081 | -66 | 211201.9994 | -63 | 242838.0823 | -60.5 | 244938.0816 | -57.5 | 252437.9994 | -55 | 250937.9994 | -52 | 252937.9994 | -49 | 253037.9994 | -46.5 | 252837.9994 | -43.5 | 250737.9994 | -82.5 | 211201.9994
-41 | 211201.9994 | -38 | 252337.9994 | -35 | 254437.9994 | -32.5 | 243437.9994 | -29.5 | 251137.9994 | -27 | 246837.9994 | -24 | 211201.9994 | -21 | 243037.9994 | -18.5 | 122518.9988 | -15.5 | 252437.9994 | -12.5 | 250937.9994 | -10 | 252937.9994 | -7.5 | 253037.9994 | -4.5 | 252837.9994 | -1.5 | 250737.9994 | -41 | 122518.9988
1 | 211201.9994 | 4 | 252337.9994 | 7 | 254437.9994 | 9.5 | 243437.9994 | 12.5 | 251137.9994 | 15 | 246837.9994 | 18 | 211201.9994 | 21 | 243037.9994 | 23.5 | 245137.9994 | 26.5 | 252437.9994 | 29 | 250937.9994 | 32 | 252937.9994 | 34.5 | 253037.9994 | 37.5 | 252837.9994 | 40.5 | 250737.9994 | 1 | 211201.9994
43 | 211201.9994 | 46 | 252337.9994 | 48.5 | 254437.9994 | 51.5 | 243437.9994 | 54.5 | 251137.9994 | 57 | 246837.9994 | 60 | 211201.9994 | 63 | 243037.9994 | 65.5 | 245137.9994 | 68.5 | 252437.9994 | 71.5 | 250937.9994 | 74 | 252937.9994 | 76.5 | 253037.9994 | 79.5 | 252837.9994 | 82.5 | 250737.9994 | 43 | 211201.9994
85 | 211201.9994 | 88 | 252337.9994 | 90.5 | 254437.9994 | 93.5 | 243437.9994 | 96.5 | 251137.9994 | 99 | 246837.9994 | 102 | 211201.9994 | 104.5 | 243037.9994 | 107.5 | 245137.9994 | 110.5 | 252437.9994 | 113 | 125418.9988 | 116 | 252937.9994 | 118.5 | 253037.9994 | 121.5 | 252837.9994 | 124.5 | 250737.9994 | 85 | 125418.9988
127.5 | 211201.9994 | 130 | 252337.9994 | 133 | 254437.9994 | 135.5 | 243437.9994 | 138.5 | 251137.9994 | 141 | 246837.9994 | 144 | 211201.9994 | 146.5 | 243037.9994 | 149.5 | 245137.9994 | 152.5 | 252437.9994 | 155 | 250937.9994 | 158 | 252937.9994 | 160.5 | 253037.9994 | 163.5 | 252837.9994 | 166.5 | 250737.9994 | 127.5 | 211201.9994
169 | 211201.9994 | 172 | 252337.9994 | 174.5 | 254437.9994 | 177.5 | 243437.9994 | 180.5 | 251137.9994 | 183 | 246837.9994 | 186 | 211201.9994 | 189 | 243037.9994 | 191.5 | 245137.9994 | 194.5 | 252437.9994 | 197 | 250937.9994 | 200 | 252937.9994 | 202.5 | 253037.9994 | 205.5 | 252837.9994 | 208.5 | 250737.9994 | 169 | 211201.9994
211 | 211201.9994 | 214 | 252337.9994 | 216.5 | 254437.9994 | 219.5 | 243437.9994 | 222.5 | 251137.9994 | 225.5 | 246837.9994 | 228 | 211201.9994 | 230.5 | 243037.9994 | 233.5 | 245137.9994 | 236.5 | 126168.9988 | 239 | 250937.9994 | 242 | 252937.9994 | 244.5 | 253037.9994 | 247.5 | 252837.9994 | 250.5 | 250737.9994 | 211 | 126168.9988
254 | 211201.9994 | 256 | 252337.9994 | 258.5 | 254437.9994 | 261.5 | 243437.9994 | 264.5 | 251137.9994 | 267 | 246638.081 | 270 | 211201.9994 | 272.5 | 243037.9994 | 275.5 | 245137.9994 | 278.5 | 252437.9994 | 281 | 250937.9994 | 284 | 252738.079 | 286.5 | 253037.9994 | 289.5 | 252837.9994 | 292.5 | 250737.9994 | 254 | 211201.9994
295 | 211201.9994 | 298 | 252337.9994 | 300.5 | 254437.9994 | 303.5 | 243437.9994 | 306.5 | 251137.9994 | 309 | 246837.9994 | 312 | 211201.9994 | 314.5 | 243037.9994 | 317.5 | 245137.9994 | 320.5 | 252437.9994 | 323 | 250937.9994 | 326 | 252937.9994 | 328.5 | 253037.9994 | 331.5 | 252837.9994 | 334.5 | 250737.9994 | 295 | 211201.9994
337 | 211201.9994 | 340 | 252337.9994 | 342.5 | 254437.9994 | 345.5 | 243437.9994 | 348.5 | 251137.9994 | 351 | 246837.9994 | 354 | 211201.9994 | 356.5 | 243037.9994 | 359.5 | 245137.9994 | 362.5 | 252437.9994 | 365 | 250937.9994 | 368 | 252937.9994 | 370.5 | 253037.9994 | 373.5 | 252837.9994 | 376.5 | 250737.9994 | 337 | 211201.9994
379 | 211201.9994 | 382 | 252337.9994 | 384.5 | 254437.9994 | 387.5 | 243437.9994 | 390.5 | 251137.9994 | 393 | 246837.9994 | 396 | 211201.9994 | 398.5 | 243037.9994 | 401.5 | 245137.9994 | 404.5 | 252437.9994 | 407 | 250937.9994 | 410 | 252937.9994 | 412.5 | 253037.9994 | 415.5 | 252837.9994 | 418.5 | 250737.9994 | 379 | 211201.9994
421 | 211201.9994 | 424 | 126118.9988 | 426.5 | 254437.9994 | 429.5 | 243437.9994 | 432.5 | 125518.9988 | 435 | 246837.9994 | 438 | 211201.9994 | 440.5 | 243037.9994 | 443.5 | 245137.9994 | 446.5 | 252437.9994 | 449 | 250937.9994 | 452 | 252937.9994 | 454.5 | 253037.9994 | 457.5 | 252837.9994 | 460.5 | 250737.9994 | 421 | 125518.9988
463 | 211201.9994 | 466 | 252337.9994 | 468.5 | 254437.9994 | 471.5 | 243437.9994 | 474.5 | 251137.9994 | 477 | 246837.9994 | 480 | 211201.9994 | 482.5 | 243037.9994 | 485.5 | 245137.9994 | 488.5 | 252437.9994 | 491 | 250937.9994 | 494 | 252937.9994 | 496.5 | 253037.9994 | 499.5 | 252837.9994 | 502.5 | 250737.9994 | 463 | 211201.9994
505 | 211201.9994 | 508 | 252138.0792 | 510.5 | 254437.9994 | 513.5 | 243437.9994 | 516.5 | 251137.9994 | 519 | 246837.9994 | 522 | 211201.9994 | 524.5 | 243037.9994 | 527.5 | 245137.9994 | 530.5 | 252437.9994 | 533 | 250937.9994 | 536 | 252937.9994 | 538.5 | 253037.9994 | 541.5 | 252837.9994 | 544.5 | 250737.9994 | 505 | 211201.9994
547 | 211201.9994 | 550 | 252337.9994 | 552.5 | 254437.9994 | 555.5 | 243437.9994 | 558.5 | 251137.9994 | 561 | 246837.9994 | 564 | 211201.9994 | 566.5 | 243037.9994 | 569.5 | 245137.9994 | 572.5 | 252437.9994 | 575 | 250937.9994 | 578 | 252937.9994 | 580.5 | 253037.9994 | 583.5 | 252837.9994 | 586.5 | 250737.9994 | 547 | 211201.9994
589 | 211201.9994 | 592 | 252337.9994 | 594.5 | 254437.9994 | 597.5 | 243437.9994 | 600.5 | 251137.9994 | 603 | 246837.9994 | 606 | 211201.9994 | 608.5 | 243037.9994 | 611.5 | 245137.9994 | 614.5 | 252437.9994 | 617 | 250937.9994 | 620 | 252937.9994 | 622.5 | 253037.9994 | 625.5 | 252837.9994 | 628.5 | 250737.9994 | 589 | 211201.9994
631 | 211201.9994 | 634 | 252337.9994 | 636.5 | 254437.9994 | 639.5 | 243437.9994 | 642.5 | 251137.9994 | 645 | 246837.9994 | 648 | 211201.9994 | 650.5 | 243037.9994 | 653.5 | 245137.9994 | 656.5 | 252437.9994 | 659 | 250937.9994 | 662 | 252937.9994 | 664.5 | 253037.9994 | 667.5 | 252837.9994 | 670.5 | 250737.9994 | 631 | 211201.9994
673 | 211201.9994 | 676 | 252337.9994 | 678.5 | 254437.9994 | 681.5 | 243437.9994 | 684.5 | 251137.9994 | 687 | 246837.9994 | 690 | 211201.9994 | 692.5 | 243037.9994 | 695.5 | 245137.9994 | 698.5 | 252437.9994 | 701 | 250937.9994 | 704 | 252937.9994 | 706.5 | 253037.9994 | 709.5 | 252837.9994 | 712.5 | 250737.9994 | 673 | 211201.9994
715 | 211201.9994 | 718 | 252337.9994 | 720.5 | 254437.9994 | 723.5 | 243437.9994 | 726.5 | 251137.9994 | 729 | 246837.9994 | 732 | 211201.9994 | 734.5 | 243037.9994 | 737.5 | 245137.9994 | 740.5 | 252437.9994 | 743 | 250937.9994 | 746 | 252937.9994 | 748.5 | 253037.9994 | 751.5 | 252837.9994 | 754.5 | 250737.9994 | 715 | 211201.9994
757 | 211201.9994 | 760 | 252337.9994 | 762.5 | 254437.9994 | 765.5 | 243437.9994 | 768.5 | 251137.9994 | 771 | 246837.9994 | 774 | 211201.9994 | 776.5 | 243037.9994 | 779.5 | 245137.9994 | 782.5 | 252437.9994 | 785 | 250937.9994 | 788 | 252937.9994 | 790.5 | 253037.9994 | 793.5 | 252837.9994 | 796.5 | 250737.9994 | 757 | 211201.9994
799 | 211201.9994 | 802 | 252337.9994 | 804.5 | 254437.9994 | 807.5 | 243437.9994 | 810.5 | 251137.9994 | 813 | 246837.9994 | 816 | 211201.9994 | 818.5 | 243037.9994 | 821.5 | 245137.9994 | 824 | 252437.9994 | 827 | 250937.9994 | 830 | 252937.9994 | 832.5 | 253037.9994 | 835.5 | 252837.9994 | 838.5 | 250737.9994 | 799 | 211201.9994
841 | 211201.9994 | 844 | 252337.9994 | 846.5 | 254437.9994 | 849.5 | 243437.9994 | 852.5 | 251137.9994 | 855 | 246837.9994 | 858 | 211201.9994 | 860.5 | 243037.9994 | 863.5 | 245137.9994 | 866.5 | 252437.9994 | 869 | 250937.9994 | 872 | 252937.9994 | 874.5 | 253037.9994 | 877.5 | 252837.9994 | 880 | 250737.9994 | 841 | 211201.9994
883 | 211201.9994 | 886 | 252337.9994 | 888.5 | 254437.9994 | 891.5 | 243437.9994 | 894.5 | 251137.9994 | 897 | 246837.9994 | 900 | 211201.9994 | 902.5 | 243037.9994 | 905.5 | 245137.9994 | 908.5 | 252437.9994 | 911 | 250937.9994 | 914 | 252937.9994 | 916.5 | 253037.9994 | 919.5 | 252837.9994 | 922.5 | 250737.9994 | 883 | 211201.9994
925 | 211201.9994 | 928 | 252337.9994 | 930.5 | 254437.9994 | 933.5 | 243437.9994 | 936.5 | 251137.9994 | 939 | 246837.9994 | 942 | 211201.9994 | 944.5 | 243037.9994 | 947.5 | 244938.0816 | 950.5 | 252437.9994 | 953 | 250937.9994 | 955.5 | 252937.9994 | 958.5 | 253037.9994 | 961.5 | 126368.9988 | 964.5 | 250737.9994 | 925 | 126368.9988
967 | 211201.9994 | 969.5 | 252337.9994 | 972.5 | 254437.9994 | 975.5 | 243437.9994 | 978.5 | 251137.9994 | 981 | 246837.9994 | 984 | 211201.9994 | 986.5 | 243037.9994 | 989.5 | 245137.9994 | 992.5 | 252437.9994 | 995 | 250937.9994 | 998 | 252937.9994 | 1000.5 | 126468.9988 | 1003.5 | 252837.9994 | 1006 | 250737.9994 | 967 | 126468.9988
1009 | 211201.9994 | 1012 | 252337.9994 | 1014.5 | 254437.9994 | 1017.5 | 243437.9994 | 1020 | 251137.9994 | 1023 | 246837.9994 | 1026 | 211201.9994 | 1028.5 | 243037.9994 | 1031.5 | 245137.9994 | 1034.5 | 252437.9994 | 1037 | 250937.9994 | 1040 | 252937.9994 | 1042.5 | 126468.9988 | 1045.5 | 252837.9994 | 1048 | 250737.9994 | 1009 | 126468.9988
1051 | 211201.9994 | 1053.5 | 252337.9994 | 1056.5 | 254437.9994 | 1059.5 | 243437.9994 | 1062.5 | 251137.9994 | 1065 | 123368.9988 | 1068 | 211201.9994 | 1070.5 | 243037.9994 | 1073.5 | 245137.9994 | 1076.5 | 252437.9994 | 1079 | 250937.9994 | 1082 | 252937.9994 | 1084.5 | 253037.9994 | 1087.5 | 252837.9994 | 1090.5 | 250737.9994 | 1051 | 123368.9988
1093 | 211201.9994 | 1095.5 | 252337.9994 | 1098.5 | 254437.9994 | 1101.5 | 243437.9994 | 1104 | 251137.9994 | 1107 | 246837.9994 | 1110 | 211201.9994 | 1112.5 | 243037.9994 | 1115.5 | 245137.9994 | 1118 | 252437.9994 | 1121 | 250937.9994 | 1123.5 | 252937.9994 | 1126.5 | 253037.9994 | 1129.5 | 252837.9994 | 1132 | 250737.9994 | 1093 | 211201.9994
1135 | 211201.9994 | 1138 | 252337.9994 | 1140.5 | 254437.9994 | 1143.5 | 243437.9994 | 1146.5 | 251137.9994 | 1149 | 123368.9988 | 1152 | 211201.9994 | 1154.5 | 243037.9994 | 1157.5 | 245137.9994 | 1160.5 | 252437.9994 | 1163 | 250937.9994 | 1166 | 252937.9994 | 1168.5 | 253037.9994 | 1171.5 | 252837.9994 | 1174.5 | 250737.9994 | 1135 | 123368.9988
1177 | 211201.9994 | 1179.5 | 252337.9994 | 1182.5 | 254437.9994 | 1185.5 | 243437.9994 | 1188 | 251137.9994 | 1191 | 246837.9994 | 1193.5 | 211201.9994 | 1196.5 | 243037.9994 | 1199.5 | 245137.9994 | 1202 | 252437.9994 | 1205 | 250937.9994 | 1208 | 252937.9994 | 1210.5 | 253037.9994 | 1213.5 | 252837.9994 | 1216.5 | 250737.9994 | 1177 | 211201.9994
1219 | 211201.9994 | 1221.5 | 252337.9994 | 1224.5 | 254437.9994 | 1227.5 | 243437.9994 | 1230.5 | 251137.9994 | 1233 | 246837.9994 | 1235.5 | 211201.9994 | 1238.5 | 243037.9994 | 1241.5 | 245137.9994 | 1244.5 | 252437.9994 | 1247 | 250937.9994 | 1249.5 | 252937.9994 | 1252.5 | 253037.9994 | 1255.5 | 252837.9994 | 1258 | 250737.9994 | 1219 | 211201.9994
1261 | 211201.9994 | 1263.5 | 252337.9994 | 1266.5 | 254437.9994 | 1269.5 | 243437.9994 | 1272.5 | 251137.9994 | 1275 | 246837.9994 | 1278 | 211201.9994 | 1280.5 | 243037.9994 | 1283.5 | 245137.9994 | 1286 | 252437.9994 | 1289 | 250937.9994 | 1291.5 | 252937.9994 | 1294.5 | 253037.9994 | 1297.5 | 252837.9994 | 1300 | 250737.9994 | 1261 | 211201.9994
1303 | 211201.9994 | 1306 | 252337.9994 | 1308.5 | 254437.9994 | 1311.5 | 243437.9994 | 1314 | 251137.9994 | 1317 | 246837.9994 | 1319.5 | 211201.9994 | 1322.5 | 243037.9994 | 1325.5 | 245137.9994 | 1328.5 | 252437.9994 | 1331 | 125418.9988 | 1333.5 | 252937.9994 | 1336.5 | 253037.9994 | 1339.5 | 252837.9994 | 1342 | 250737.9994 | 1303 | 125418.9988
1345 | 211201.9994 | 1347.5 | 126118.9988 | 1350.5 | 254437.9994 | 1353.5 | 243437.9994 | 1356 | 251137.9994 | 1359 | 246837.9994 | 1362 | 211201.9994 | 1364.5 | 243037.9994 | 1367.5 | 245137.9994 | 1370.5 | 252437.9994 | 1373 | 250937.9994 | 1375.5 | 252937.9994 | 1378.5 | 253037.9994 | 1381.5 | 252837.9994 | 1384 | 250737.9994 | 1345 | 126118.9988
1387 | 211201.9994 | 1389.5 | 252337.9994 | 1392.5 | 254437.9994 | 1395.5 | 243437.9994 | 1398 | 251137.9994 | 1401 | 246837.9994 | 1403.5 | 211201.9994 | 1406.5 | 243037.9994 | 1409.5 | 245137.9994 | 1412.5 | 252437.9994 | 1415 | 250937.9994 | 1418 | 252937.9994 | 1420.5 | 253037.9994 | 1423.5 | 252837.9994 | 1426 | 250737.9994 | 1387 | 211201.9994
1429 | 211201.9994 | 1431.5 | 252337.9994 | 1434.5 | 254437.9994 | 1437.5 | 243437.9994 | 1440 | 251137.9994 | 1443 | 246837.9994 | 1446 | 211201.9994 | 1448.5 | 243037.9994 | 1451.5 | 245137.9994 | 1454 | 252437.9994 | 1457 | 250937.9994 | 1459.5 | 252937.9994 | 1462.5 | 253037.9994 | 1465.5 | 252837.9994 | 1468 | 250737.9994 | 1429 | 211201.9994
1471 | 211201.9994 | 1473.5 | 252337.9994 | 1476.5 | 254437.9994 | 1479.5 | 243437.9994 | 1482 | 251137.9994 | 1485 | 246837.9994 | 1488 | 211201.9994 | 1490.5 | 243037.9994 | 1493.5 | 245137.9994 | 1496.5 | 252437.9994 | 1499 | 250937.9994 | 1501.5 | 252937.9994 | 1504.5 | 253037.9994 | 1507.5 | 252837.9994 | 1510 | 63.6781 | 1471 | 63.6781
1513 | 211002.0947 | 1515.5 | 252337.9994 | 1518.5 | 254437.9994 | 1521.5 | 243437.9994 | 1524 | 251137.9994 | 1527 | 246837.9994 | 1529.5 | 211201.9994 | 1532.5 | 243037.9994 | 1535.5 | 245137.9994 | 1538 | 252437.9994 | 1541 | 250937.9994 | 1543.5 | 252937.9994 | 1546.5 | 253037.9994 | 1549.5 | 252837.9994 | 1552 | 87.5016 | 1513 | 87.5016
1555 | 210902.142 | 1557.5 | 252337.9994 | 1560.5 | 254437.9994 | 1563.5 | 243437.9994 | 1566 | 251137.9994 | 1569 | 246837.9994 | 1571.5 | 211201.9994 | 1574.5 | 243037.9994 | 1577.5 | 245137.9994 | 1580.5 | 252437.9994 | 1583 | 250937.9994 | 1585.5 | 252937.9994 | 1588.5 | 253037.9994 | 1591.5 | 252837.9994 | 1594 | 88.0891 | 1555 | 88.0891
1597 | 105201.3549 | 1599.5 | 252337.9994 | 1602.5 | 254437.9994 | 1605.5 | 243437.9994 | 1608 | 251137.9994 | 1611 | 246837.9994 | 1613.5 | 211201.9994 | 1616.5 | 243037.9994 | 1619.5 | 245137.9994 | 1622.5 | 252437.9994 | 1625 | 250937.9994 | 1627.5 | 252937.9994 | 1630.5 | 253037.9994 | 1634 | 252837.9994 | 1636 | 464.1555 | 1597 | 464.1555
1639 | 5177.7945 | 1641.5 | 252337.9994 | 1644.5 | 254238.0786 | 1647.5 | 243138.1232 | 1650 | 251137.9994 | 1653 | 246837.9994 | 1655.5 | 211201.9994 | 1658.5 | 243037.9994 | 1661.5 | 245137.9994 | 1664 | 289.3235 | 1667 | 60214.0044 | 1669.5 | 41721.5052 | 1672.5 | 180095.597 | 1675.5 | 74.5274 | 1678 | 5759.9575 | 1639 | 74.5274
1681 | 906.2563 | 1683.5 | 252337.9994 | 1686.5 | 127168.9988 | 1689.5 | 243437.9994 | 1692 | 251137.9994 | 1695 | 246837.9994 | 1697.5 | 211201.9994 | 1700.5 | 121468.9988 | 1703.5 | 245137.9994 | 1706 | 42.7423 | 1709 | 54294.7093 | 1711.5 | 37808.093 | 1714.5 | 155.8696 | 1717.5 | 136.1813 | 1720 | 8432.4341 | 1681 | 42.7423
1723 | 9.1836 | 1725.5 | 40106.1997 | 1728.5 | 127168.9988 | 1731.5 | 121668.9988 | 1734 | 251137.9994 | 1737 | 246837.9994 | 1739.5 | 105550.9988 | 1742.5 | 121468.9988 | 1745.5 | 122518.9988 | 1748 | 54.384 | 1751 | 5.252 | 1753.5 | 21.3959 | 1756.5 | 6.4697 | 1759.5 | 11.1952 | 1762 | 2006.3678 | 1723 | 5.252
1765 | 4.573 | 1767.5 | 11828.6211 | 1770.5 | 127168.9988 | 1773.5 | 121668.9988 | 1776 | 125518.9988 | 1779 | 123368.9988 | 1781.5 | 105550.9988 | 1784.5 | 121468.9988 | 1787.5 | 122518.9988 | 1790 | 3052.8295 | 1793 | 14.1994 | 1795.5 | 8.1781 | 1798.5 | 3.7423 | 1801.5 | 24.0463 | 1804 | 14.7014 | 1765 | 3.7423
1807 | 24.3717 | 1809.5 | 149649.0373 | 1812.5 | 127168.9988 | 1815.5 | 121668.9988 | 1818 | 125518.9988 | 1821 | 123368.9988 | 1823.5 | 105550.9988 | 1826.5 | 121468.9988 | 1829.5 | 68390.627 | 1832 | 22.1201 | 1835 | 23.9819 | 1837.5 | 1.4866 | 1840.5 | 4.009 | 1843.5 | 16.3884 | 1846 | 18.9748 | 1807 | 1.4866
1849 | 22.5003 | 1851.5 | 1658.1897 | 1854.5 | 127168.9988 | 1857.5 | 121668.9988 | 1860 | 125518.9988 | 1863 | 123368.9988 | 1865.5 | 105550.9988 | 1868.5 | 121468.9988 | 1871.5 | 122518.9988 | 1874 | 7.0101 | 1877 | 18.0301 | 1879.5 | 0.88325 | 1882.5 | 20.5495 | 1885.5 | 0.39212 | 1888 | 42.0931 | 1849 | 0.39212
1891 | 7.0822 | 1893.5 | 16283.4849 | 1896.5 | 16266.3109 | 1899.5 | 121668.9988 | 1902 | 125518.9988 | 1905 | 123368.9988 | 1907.5 | 105550.9988 | 1910.5 | 121468.9988 | 1913.5 | 122518.9988 | 1916 | 0.22314 | 1919 | 0.86581 | 1921.5 | 19.5612 | 1924.5 | 24.7122 | 1927.5 | 0.88238 | 1930 | 21.2896 | 1891 | 0.22314
1933 | 13.513 | 1935.5 | 62544.8509 | 1938.5 | 127168.9988 | 1941.5 | 121668.9988 | 1944 | 125518.9988 | 1947 | 123368.9988 | 1949.5 | 105550.9988 | 1952.5 | 121468.9988 | 1955.5 | 122518.9988 | 1958 | 108.2128 | 1961 | 31.1058 | 1963.5 | 7.3194 | 1966.5 | 29.8443 | 1969.5 | 7.5135 | 1972 | 12.8843 | 1933 | 7.3194
1975 | 0.57732 | 1977.5 | 166001.6872 | 1980.5 | 127168.9988 | 1983.5 | 121668.9988 | 1986 | 125518.9988 | 1989 | 123368.9988 | 1991.5 | 105550.9988 | 1994.5 | 121468.9988 | 1997.5 | 122518.9988 | 2000 | 272.3538 | 2003 | 31.8835 | 2005.5 | 12.522 | 2008.5 | 29.6394 | 2011.5 | 27.5881 | 2014 | 13.148 | 1975 | 0.57732
2017 | 15.5117 | 2019.5 | 91368.6288 | 2022.5 | 127168.9988 | 2025.5 | 121668.9988 | 2028 | 125518.9988 | 2031 | 123368.9988 | 2033.5 | 105550.9988 | 2036.5 | 121468.9988 | 2039.5 | 122518.9988 | 2042 | 2453.118 | 2045 | 18.375 | 2047.5 | 4.1458 | 2050.5 | 8.6558 | 2054 | 21.1077 | 2056 | 10.5126 | 2017 | 4.1458
2059 | 1.0772 | 2061.5 | 64579.4959 | 2064.5 | 127168.9988 | 2067.5 | 121668.9988 | 2070 | 125518.9988 | 2073 | 123368.9988 | 2075.5 | 105550.9988 | 2078.5 | 121468.9988 | 2081.5 | 122518.9988 | 2084 | 1852.3709 | 2087 | 13.0281 | 2089.5 | 9.6389 | 2092.5 | 10.1287 | 2095.5 | 15.2909 | 2098 | 12.5694 | 2059 | 1.0772
2101 | 9.2429 | 2103.5 | 77202.5871 | 2106.5 | 127168.9988 | 2109.5 | 121668.9988 | 2112 | 83645.9982 | 2115 | 123368.9988 | 2117.5 | 105550.9988 | 2120.5 | 121468.9988 | 2123.5 | 122518.9988 | 2126 | 5108.3419 | 2129 | 6.0854 | 2131.5 | 5.1834 | 2134.5 | 25.2841 | 2137.5 | 0.18647 | 2140 | 22.944 | 2101 | 0.18647
2143 | 13.6372 | 2145.5 | 101383.6986 | 2148.5 | 127168.9988 | 2151.5 | 121668.9988 | 2154 | 125518.9988 | 2157 | 123368.9988 | 2159.5 | 105550.9988 | 2162.5 | 121468.9988 | 2165.5 | 245137.9994 | 2168 | 509.8609 | 2171 | 17.3462 | 2173.5 | 3.3473 | 2176.5 | 5.4081 | 2179.5 | 0.59695 | 2182 | 19.5602 | 2143 | 0.59695
2184.5 | 21.3118 | 2187.5 | 63443.7505 | 2190.5 | 127168.9988 | 2193.5 | 121668.9988 | 2196 | 125518.9988 | 2199 | 123368.9988 | 2201.5 | 105550.9988 | 2204.5 | 121468.9988 | 2207 | 122518.9988 | 2210 | 5316.4658 | 2212.5 | 3.2224 | 2215.5 | 4.4145 | 2218.5 | 26.3785 | 2221.5 | 0.76024 | 2224 | 4.9379 | 2184.5 | 0.76024
2227 | 15.9524 | 2229.5 | 10892.3199 | 2232.5 | 84745.9982 | 2235.5 | 121668.9988 | 2238 | 125518.9988 | 2241 | 123368.9988 | 2243.5 | 70333.9982 | 2246.5 | 121468.9988 | 2249.5 | 122518.9988 | 2252 | 8.1056 | 2255 | 4041.2266 | 2257.5 | 14.9574 | 2260.5 | 27.889 | 2263.5 | 0.9382 | 2266 | 25.0907 | 2227 | 0.9382
2269 | 14.5053 | 2271.5 | 116197.4562 | 2274.5 | 84745.9982 | 2277.5 | 121668.9988 | 2280 | 125518.9988 | 2282.5 | 123368.9988 | 2285.5 | 105550.9988 | 2288.5 | 121468.9988 | 2291 | 122518.9988 | 2294 | 26.9892 | 2296.5 | 15.8903 | 2299.5 | 11.7492 | 2302.5 | 21.1446 | 2305.5 | 21.8901 | 2308 | 2.8743 | 2269 | 2.8743
2311 | 15.9969 | 2313.5 | 64312.8226 | 2316.5 | 127168.9988 | 2319.5 | 151297.3897 | 2322 | 125518.9988 | 2325 | 123368.9988 | 2327.5 | 105550.9988 | 2330.5 | 121468.9988 | 2333 | 122518.9988 | 2336 | 14.566 | 2338.5 | 0.21046 | 2341.5 | 17.8361 | 2344.5 | 19.4341 | 2347.5 | 23.7961 | 2350 | 8.9678 | 2311 | 0.21046
2353 | 21.8234 | 2355.5 | 92864.4642 | 2358.5 | 84745.9982 | 2361.5 | 121668.9988 | 2364 | 83645.9982 | 2367 | 82212.6648 | 2369.5 | 70333.9982 | 2372.5 | 121468.9988 | 2375 | 81645.9982 | 2378 | 27.5168 | 2381 | 25.063 | 2383.5 | 6.9419 | 2386.5 | 15.0574 | 2389.5 | 7.1346 | 2392 | 2.4359 | 2353 | 2.4359
2395 | 1.444 | 2397.5 | 5821.9833 | 2400.5 | 84745.9982 | 2403.5 | 81079.3315 | 2406 | 83645.9982 | 2408.5 | 82212.6648 | 2411.5 | 70333.9982 | 2414.5 | 80945.9982 | 2417.5 | 81645.9982 | 2420 | 20.379 | 2423 | 25.063 | 2425.5 | 3.2154 | 2428.5 | 0.88412 | 2431 | 9.0552 | 2434 | 2.8303 | 2395 | 0.88412
2437 | 5.7148 | 2439.5 | 88658.2043 | 2442.5 | 84745.9982 | 2445 | 60784.4976 | 2448 | 62709.4976 | 2450.5 | 61634.4976 | 2453.5 | 52725.4976 | 2456.5 | 48527.5969 | 2459.5 | 61209.4976 | 2462 | 1.5383 | 2465 | 15.835 | 2467.5 | 4.6396 | 2470.5 | 25.9901 | 2473.5 | 8.9576 | 2476 | 6.798 | 2437 | 1.5383
2479 | 3.0697 | 2481.5 | 176758.5486 | 2484.5 | 50807.5969 | 2487.5 | 60784.4976 | 2490 | 50147.5969 | 2493 | 49287.5969 | 2495.5 | 42160.3969 | 2498.5 | 40422.9963 | 2501.5 | 40772.9963 | 2504 | 3.1402 | 2506.5 | 29.1658 | 2509.5 | 10.584 | 2512.5 | 0.14757 | 2515 | 16.057 | 2518 | 18.8003 | 2479 | 0.14757
2521 | 8.3889 | 2523.5 | 86832.5621 | 2526.5 | 36262.5672 | 2529 | 30342.2451 | 2531 | 31304.7451 | 2534.5 | 30767.2451 | 2537.5 | 23377.9945 | 2540.5 | 26915.3278 | 2543.5 | 30554.7451 | 2546 | 0.81824 | 2548.5 | 15.4493 | 2551.5 | 30.342 | 2554.5 | 11.4875 | 2557.5 | 12.4251 | 2560 | 17.0256 | 2521 | 0.81824
2562.5 | 6.9003 | 2565.5 | 48027.8026 | 2568.5 | 25353.7939 | 2571 | 22039.8115 | 2574 | 20836.4927 | 2577 | 17538.42 | 2579.5 | 13986.7908 | 2582.5 | 16109.1908 | 2585 | 16249.1908 | 2588 | 20.7353 | 2590.5 | 5.252 | 2593.5 | 12.9906 | 2596.5 | 26.7692 | 2599 | 0.26882 | 2602 | 7.4162 | 2562.5 | 0.26882
2605 | 11.8664 | 2607.5 | 16729.1908 | 2610.5 | 16869.1908 | 2613.5 | 14225.7543 | 2616 | 12461.8878 | 2618.5 | 11658.9396 | 2621.5 | 10465.0878 | 2624.5 | 10471.2033 | 2627 | 11047.1684 | 2630 | 5.6588 | 2633 | 6.6481 | 2635.5 | 16.2137 | 2638.5 | 27.5576 | 2641 | 9.0064 | 2644 | 4.9379 | 2605 | 4.9379
2646.5 | 10.7325 | 2649.5 | 58797.3627 | 2652.5 | 10081.5047 | 2655 | 8597.7686 | 2658 | 8274.5817 | 2660.5 | 8415.0857 | 2663.5 | 7725.9835 | 2666.5 | 8004.5817 | 2669 | 8356.4651 | 2672 | 12.8691 | 2674.5 | 9.2529 | 2677.5 | 10.0846 | 2680.5 | 24.9658 | 2683 | 0.39212 | 2686 | 31.9198 | 2646.5 | 0.39212
2689 | 4.3852 | 2691.5 | 25224.3872 | 2694.5 | 7172.4929 | 2697 | 7279.9192 | 2700 | 6341.9762 | 2702.5 | 7616.793 | 2705.5 | 5317.9762 | 2708.5 | 5978.4256 | 2711 | 6030.9256 | 2714 | 20.6758 | 2717 | 19.129 | 2719.5 | 5.8709 | 2722.5 | 1.6551 | 2725.5 | 0.89611 | 2728 | 25.2836 | 2689 | 0.89611
2730.5 | 22.4754 | 2733.5 | 18925.5043 | 2736.5 | 5819.4621 | 2739 | 6308.8715 | 2742 | 6027.7311 | 2744.5 | 6231.7198 | 2747.5 | 4493.4937 | 2750.5 | 5554.3458 | 2753.5 | 5117.8011 | 2756 | 1.1136 | 2759 | 1.9106 | 2761.5 | 20.383 | 2764.5 | 0.39424 | 2767 | 18.9332 | 2770 | 2.2181 | 2730.5 | 0.39424
2772.5 | 4.8379 | 2775.5 | 11926.4344 | 2778.5 | 5556.3725 | 2781 | 6308.8715 | 2784 | 6180.9256 | 2787 | 5642.7179 | 2789.5 | 5182.5256 | 2792.5 | 4667.3806 | 2795 | 5738.9744 | 2798 | 27.5168 | 2800.5 | 25.6428 | 2803.5 | 2.9088 | 2806.5 | 2.645 | 2809 | 24.2974 | 2812 | 8.5759 | 2772.5 | 2.645
2814.5 | 14.4493 | 2817.5 | 6527.5586 | 2820.5 | 6598.3452 | 2823 | 5434.9277 | 2826 | 5881.8315 | 2828.5 | 5512.2004 | 2831.5 | 4813.9737 | 2834.5 | 5303.0392 | 2837 | 5231.2328 | 2840 | 3.8034 | 2842.5 | 0.96876 | 2845.5 | 3.1715 | 2848.5 | 17.4311 | 2851 | 0.1028 | 2854 | 29.1302 | 2814.5 | 0.1028
2856.5 | 17.6739 | 2859.5 | 6912.1447 | 2862.5 | 8110.8843 | 2865 | 6308.8715 | 2868 | 6511.5031 | 2870.5 | 7865.723 | 2873.5 | 5937.1786 | 2876.5 | 5688.9744 | 2879 | 6188.13 | 2882 | 130.5453 | 2884.5 | 35.4601 | 2887.5 | 12.4701 | 2890.5 | 29.8443 | 2893 | 36.1925 | 2896 | 12.4648 | 2856.5 | 12.4648
2898.5 | 25.259 | 2901.5 | 7929.739 | 2904.5 | 8677.1547 | 2907.5 | 8919.9094 | 2910 | 7751.168 | 2912.5 | 8415.0857 | 2915.5 | 7446.4829 | 2918.5 | 8583.4829 | 2921 | 8356.4651 | 2924 | 17.4876 | 2926.5 | 24.045 | 2929.5 | 14.3123 | 2932.5 | 0.68319 | 2935 | 2.3462 | 2938 | 9.7101 | 2898.5 | 0.68319
2940.5 | 7.6793 | 2943.5 | 22034.0392 | 2946.5 | 12020.8443 | 2949 | 9266.8303 | 2952 | 11319.8957 | 2954.5 | 11658.9396 | 2957.5 | 10465.0878 | 2960.5 | 10030.7353 | 2963 | 9709.5047 | 2966 | 29.5338 | 2968.5 | 2.0404 | 2971.5 | 3.9673 | 2974.5 | 13.9317 | 2977 | 23.2368 | 2980 | 20.0325 | 2940.5 | 2.0404
2982.5 | 23.0711 | 2985.5 | 24228.7707 | 2988.5 | 16869.1908 | 2991 | 16135.8575 | 2994 | 15602.3652 | 2996.5 | 14425.7543 | 2999.5 | 11638.989 | 3002.5 | 12056.8878 | 3005 | 15227.3652 | 3008 | 3.9371 | 3010.5 | 28.7574 | 3013.5 | 4.9108 | 3016.5 | 21.5647 | 3019 | 19.6301 | 3022 | 19.9732 | 2982.5 | 3.9371
3024.5 | 13.7991 | 3027.5 | 19318.2998 | 3030.5 | 25353.7939 | 3033 | 20194.826 | 3036 | 20836.4927 | 3038.5 | 22348.9024 | 3041.5 | 21030.1939 | 3044.5 | 22003.4478 | 3047 | 20336.4927 | 3050 | 25.6886 | 3052.5 | 7.6948 | 3055.5 | 31.105 | 3058.5 | 22.7804 | 3061.5 | 8.9089 | 3064 | 10.3613 | 3024.5 | 7.6948

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 49 |  |  | 2006-08-31 | 12:58
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-119.2 | 211202 |  | -110.3 | 211202 | -104.6 | 246838 | -101.4 | 211202 | -99.1 | 243038 | -96.8 | 245138 | -119.2 | 211202
-77.2 | 211202 |  | -68.1 | 211202 | -62.6 | 246838 | -59.3 | 211202 | -57 | 243038 | -54.8 | 245138 | -77.2 | 211202
-35.2 | 211202 |  | -26.3 | 105551 | -20.6 | 123369 | -17.3 | 211202 | -15 | 243038 | -12.8 | 63159.5 | -35.2 | 63159.5
6.8 | 211202 |  | 15.7 | 211202 | 21.3 | 246838 | 24.7 | 211202 | 26.9 | 243038 | 29.2 | 245138 | 6.8 | 211202
48.7 | 211202 |  | 57.7 | 105551 | 63.4 | 246838 | 66.6 | 211202 | 69 | 243038 | 71.2 | 245138 | 48.7 | 105551
90.7 | 211202 |  | 99.6 | 211202 | 105.3 | 125419 | 108.6 | 211202 | 110.8 | 243038 | 113.2 | 245138 | 90.7 | 125419
132.9 | 211202 |  | 141.7 | 211202 | 147.3 | 246838 | 150.7 | 211202 | 152.8 | 243038 | 155.2 | 245138 | 132.9 | 211202
174.7 | 211202 |  | 183.7 | 211202 | 189.3 | 246838 | 192.6 | 211202 | 194.9 | 243038 | 197.2 | 245138 | 174.7 | 211202
216.7 | 211202 |  | 225.7 | 211202 | 231.4 | 126169 | 234.6 | 211202 | 236.8 | 243038 | 239.2 | 245138 | 216.7 | 126169
258.9 | 211202 |  | 267.8 | 211202 | 273.3 | 246838 | 276.6 | 211202 | 278.8 | 243038 | 281.2 | 245138 | 258.9 | 211202
300.7 | 211202 |  | 309.6 | 211202 | 315.3 | 246838 | 318.6 | 126169 | 320.8 | 121669 | 323.2 | 245138 | 300.7 | 121669
342.7 | 211202 |  | 351.6 | 211202 | 357.3 | 246838 | 360.6 | 127169 | 362.8 | 243038 | 365.2 | 245138 | 342.7 | 127169
384.7 | 211202 |  | 393.6 | 211202 | 399.3 | 246838 | 402.6 | 211202 | 404.8 | 243038 | 407.2 | 245138 | 384.7 | 211202
426.7 | 125519 |  | 435.6 | 211202 | 441.3 | 246838 | 444.6 | 211202 | 446.8 | 243038 | 449.2 | 245138 | 426.7 | 125519
468.7 | 211202 |  | 477.6 | 211202 | 483.3 | 246838 | 486.6 | 211202 | 488.8 | 243038 | 491.2 | 245138 | 468.7 | 211202
510.7 | 211202 |  | 519.6 | 211202 | 525.3 | 246838 | 528.6 | 126169 | 530.8 | 125419 | 533.2 | 245138 | 510.7 | 125419
552.7 | 211202 |  | 561.6 | 105551 | 567.3 | 246838 | 570.6 | 211202 | 572.8 | 243038 | 575.2 | 245138 | 552.7 | 105551
594.7 | 211202 |  | 603.6 | 211202 | 609.3 | 246838 | 612.6 | 126169 | 614.8 | 243038 | 617.2 | 245138 | 594.7 | 126169
636.7 | 211202 |  | 645.6 | 211202 | 651.3 | 246838 | 654.6 | 211202 | 656.8 | 243038 | 659.2 | 245138 | 636.7 | 211202
678.7 | 211202 |  | 687.6 | 211202 | 693.3 | 246838 | 696.6 | 211202 | 698.8 | 243038 | 701.2 | 125319 | 678.7 | 125319
720.7 | 211202 |  | 729.6 | 211202 | 735.3 | 246838 | 738.6 | 211202 | 740.8 | 243038 | 743.2 | 245138 | 720.7 | 211202
762.7 | 211202 |  | 771.6 | 211202 | 777.3 | 246838 | 780.6 | 211202 | 782.8 | 243038 | 785.2 | 245138 | 762.7 | 211202
804.7 | 211202 |  | 813.6 | 211202 | 819.2 | 246838 | 822.5 | 211202 | 824.8 | 243038 | 827.2 | 245138 | 804.7 | 211202
846.7 | 211202 |  | 855.6 | 211202 | 861.3 | 246838 | 864.6 | 211202 | 866.7 | 243038 | 869.1 | 245138 | 846.7 | 211202
888.7 | 211202 |  | 897.6 | 211202 | 903.3 | 246838 | 906.6 | 211202 | 908.8 | 243038 | 911.2 | 245138 | 888.7 | 211202
930.7 | 211202 |  | 939.6 | 211202 | 945.2 | 246838 | 948.6 | 126369 | 950.8 | 243038 | 953.1 | 245138 | 930.7 | 126369
972.6 | 211202 |  | 981.6 | 211202 | 987.2 | 246838 | 990.6 | 126469 | 992.7 | 243038 | 995.1 | 245138 | 972.6 | 126469
1014.6 | 211202 |  | 1023.6 | 211202 | 1029.3 | 246838 | 1032.6 | 126469 | 1034.7 | 243038 | 1037 | 245138 | 1014.6 | 126469
1056.6 | 211202 |  | 1065.6 | 123369 | 1071.2 | 246838 | 1074.6 | 211202 | 1076.8 | 243038 | 1079.2 | 245138 | 1056.6 | 123369
1098.5 | 211202 |  | 1107.6 | 211202 | 1113 | 246838 | 1116.5 | 211202 | 1118.7 | 125419 | 1120.9 | 245138 | 1098.5 | 125419
1140.7 | 211202 |  | 1149.6 | 123369 | 1155.3 | 246838 | 1158.6 | 211202 | 1160.8 | 243038 | 1163.2 | 245138 | 1140.7 | 123369
1182.5 | 211202 |  | 1191.5 | 211202 | 1197.1 | 246838 | 1200.4 | 211202 | 1202.8 | 243038 | 1205.1 | 245138 | 1182.5 | 211202
1224.6 | 211202 |  | 1233.5 | 211202 | 1239.1 | 246838 | 1242.5 | 211202 | 1244.7 | 243038 | 1247 | 245138 | 1224.6 | 211202
1266.6 | 211202 |  | 1275.6 | 211202 | 1281 | 246838 | 1284.5 | 211202 | 1286.7 | 121669 | 1289 | 245138 | 1266.6 | 121669
1308.6 | 211202 |  | 1317.5 | 211202 | 1323.2 | 125419 | 1326.5 | 211202 | 1328.7 | 243038 | 1330.9 | 245138 | 1308.6 | 125419
1350.5 | 126119 |  | 1359.6 | 211202 | 1365.1 | 246838 | 1368.6 | 211202 | 1370.7 | 243038 | 1372.9 | 125519 | 1350.5 | 125519
1392.5 | 211202 |  | 1401.5 | 211202 | 1407.2 | 246838 | 1410.5 | 211202 | 1412.7 | 243038 | 1415 | 245138 | 1392.5 | 211202
1434.5 | 211202 |  | 1443.6 | 211202 | 1449 | 246838 | 1452.5 | 211202 | 1454.7 | 243038 | 1456.9 | 245138 | 1434.5 | 211202
1476.5 | 211202 |  | 1485.6 | 211202 | 1491.1 | 246838 | 1494.6 | 211202 | 1496.7 | 12551.7415 | 1498.9 | 8794.973 | 1476.5 | 8794.973
1518.5 | 243438 |  | 1527.5 | 211202 | 1533 | 246838 | 1536.4 | 211202 | 1538.7 | 12765.7569 | 1540.9 | 9293.3095 | 1518.5 | 9293.3095
1560.5 | 211202 |  | 1569.5 | 211202 | 1575.1 | 246838 | 1578.5 | 211202 | 1580.7 | 66486.191 | 1582.9 | 6355.985 | 1560.5 | 6355.985
1602.5 | 105601.2139 |  | 1611.5 | 70300.5717 | 1617.1 | 246838 | 1620.6 | 105551 | 1622.7 | 7399.3273 | 1625 | 10027.6899 | 1602.5 | 7399.3273
1644.5 | 35575.5042 |  | 1653.5 | 20860.6141 | 1659 | 19.819 | 1662.4 | 75.4078 | 1664.7 | 314.8424 | 1666.9 | 5169.5417 | 1644.5 | 19.819
1686.5 | 15499.31 |  | 1695.5 | 2097.5616 | 1701 | 17.6456 | 1704.4 | 34.1792 | 1706.7 | 2843.4651 | 1708.9 | 126369 | 1686.5 | 17.6456
1728.5 | 255.1512 |  | 1737.5 | 307.3692 | 1743 | 6.6885 | 1746.4 | 7.902 | 1748.7 | 17.0228 | 1750.9 | 179.6 | 1728.5 | 6.6885
1770.5 | 148.0736 |  | 1779.5 | 178.5092 | 1785 | 4.9202 | 1788.4 | 5.181 | 1790.7 | 10.0079 | 1792.9 | 1668.7972 | 1770.5 | 4.9202
1812.5 | 3174.034 |  | 1821.5 | 9909.592 | 1827 | 2.9866 | 1830.4 | 1.9375 | 1832.7 | 20.2483 | 1834.9 | 29.8297 | 1812.5 | 1.9375
1854.5 | 1658.8474 |  | 1863.5 | 7101.1344 | 1869 | 0.65155 | 1872.4 | 0.64769 | 1874.7 | 5.4101 | 1876.9 | 6.6417 | 1854.5 | 0.64769
1896.5 | 159.3662 |  | 1905.5 | 145.0095 | 1911 | 0.65678 | 1914.4 | 0.65181 | 1916.7 | 8.4567 | 1918.9 | 7.5842 | 1896.5 | 0.65181
1938.5 | 1129.4244 |  | 1947.5 | 2407.4972 | 1953 | 8.74 | 1956.4 | 8.9311 | 1958.7 | 11.6123 | 1960.9 | 4.8474 | 1938.5 | 4.8474
1980.5 | 2852.4554 |  | 1989.5 | 6969.5729 | 1995 | 13.7439 | 1998.4 | 28.7872 | 2000.7 | 3.6394 | 2002.9 | 1.226 | 1980.5 | 1.226
2022.5 | 654.7764 |  | 2031.5 | 782.4211 | 2037 | 5.6085 | 2040.5 | 10.06 | 2042.7 | 8.7709 | 2045 | 5.3886 | 2022.5 | 5.3886
2064.5 | 86.035 |  | 2073.5 | 109.2723 | 2079 | 7.9274 | 2082.4 | 4.0107 | 2084.7 | 6.2712 | 2086.9 | 0.67241 | 2064.5 | 0.67241
2106.5 | 280.8141 |  | 2115.5 | 386.3988 | 2121 | 6.6321 | 2124.4 | 1.3373 | 2126.7 | 14.9968 | 2128.9 | 1.0874 | 2106.5 | 1.0874
2148.5 | 128.3563 |  | 2157.5 | 179.8203 | 2163 | 3.8685 | 2166.4 | 0.93296 | 2168.7 | 13.5919 | 2170.9 | 7.3208 | 2148.5 | 0.93296
2190.4 | 1162.3215 |  | 2199.3 | 3135.6709 | 2204.9 | 4.6864 | 2208.4 | 0.77211 | 2210.6 | 6.3774 | 2212.8 | 2.404 | 2190.4 | 0.77211
2232.5 | 2537.6889 |  | 2241.5 | 6130.9859 | 2247 | 4.515 | 2250.4 | 2.4455 | 2252.7 | 7.171 | 2254.9 | 5.2524 | 2232.5 | 2.4455
2274.5 | 366.232 |  | 2283.3 | 384.2209 | 2288.8 | 0.66775 | 2292.4 | 10.6652 | 2294.6 | 4.3419 | 2296.8 | 8.3246 | 2274.5 | 0.66775
2316.5 | 195.0449 |  | 2325.4 | 294.2713 | 2330.9 | 1.7172 | 2334.4 | 15.8431 | 2336.6 | 4.8009 | 2338.8 | 6.2096 | 2316.5 | 1.7172
2358.5 | 14280.5625 |  | 2367.4 | 1781.3695 | 2373 | 8.3675 | 2376.4 | 0.65285 | 2378.7 | 1.0531 | 2380.8 | 5.8886 | 2358.5 | 0.65285
2400.5 | 2292.0952 |  | 2409.4 | 3731.2151 | 2414.9 | 2.3646 | 2418.3 | 0.65129 | 2420.7 | 4.2985 | 2422.8 | 0.65625 | 2400.5 | 0.65129
2442.4 | 1205.6069 |  | 2451.4 | 11286.162 | 2456.9 | 3.0347 | 2460.4 | 1.9532 | 2462.6 | 8.2131 | 2464.9 | 1.8262 | 2442.4 | 1.8262
2484.5 | 1421.2289 |  | 2493.5 | 8667.2863 | 2498.9 | 1.6206 | 2502.3 | 1.3769 | 2504.6 | 15.6148 | 2506.8 | 7.3252 | 2484.5 | 1.3769
2526.2 | 1904.9767 |  | 2535.4 | 3287.6489 | 2540.8 | 2.325 | 2544.4 | 12.8569 | 2546.5 | 18.3198 | 2548.7 | 0.6573 | 2526.2 | 0.6573
2568.3 | 1455.9889 |  | 2577.3 | 2351.6494 | 2582.9 | 5.6193 | 2586.3 | 1.7859 | 2588.5 | 7.6492 | 2590.7 | 1.5899 | 2568.3 | 1.5899
2610.5 | 82.9944 |  | 2619.3 | 118.0925 | 2624.9 | 3.9739 | 2628.3 | 1.7745 | 2630.7 | 1.4319 | 2632.7 | 4.2613 | 2610.5 | 1.4319
2652.3 | 329.7644 |  | 2661.2 | 425.0166 | 2666.8 | 10.6382 | 2670.3 | 1.1347 | 2672.5 | 7.171 | 2674.7 | 8.9272 | 2652.3 | 1.1347
2694.4 | 1103.0581 |  | 2703.3 | 3854.1453 | 2708.9 | 1.7881 | 2712.4 | 1.2176 | 2714.6 | 4.2543 | 2716.8 | 8.4939 | 2694.4 | 1.2176
2736.3 | 1957.8651 |  | 2745.3 | 1429.3901 | 2750.9 | 2.616 | 2754.3 | 1.1338 | 2756.6 | 3.6949 | 2758.8 | 4.8654 | 2736.3 | 1.1338
2778.3 | 172.8163 |  | 2787.3 | 199.4477 | 2792.9 | 4.3886 | 2796.3 | 4.1292 | 2798.5 | 0.67826 | 2800.7 | 3.0509 | 2778.3 | 0.67826
2820.3 | 186.3762 |  | 2829.2 | 187.0252 | 2834.8 | 2.4645 | 2838.3 | 1.6223 | 2840.5 | 2.2878 | 2842.7 | 2.0974 | 2820.3 | 1.6223
2862.3 | 4185.376 |  | 2871.2 | 1130.5708 | 2876.8 | 4.0124 | 2880.3 | 6.8192 | 2882.5 | 0.67826 | 2884.7 | 0.92099 | 2862.3 | 0.67826
2904.4 | 934.8988 |  | 2913.2 | 7446.5 | 2918.8 | 3.2889 | 2922.3 | 2.1954 | 2924.6 | 11.0886 | 2926.7 | 10.9219 | 2904.4 | 2.1954
2946.3 | 1123.3905 |  | 2955.2 | 4079.4554 | 2960.8 | 3.5208 | 2964.3 | 15.2723 | 2966.5 | 5.3896 | 2968.7 | 2.1743 | 2946.3 | 2.1743
2988.3 | 3199.6692 |  | 2997.2 | 1523.8384 | 3002.8 | 5.3998 | 3006.3 | 9.561 | 3008.5 | 14.2319 | 3010.7 | 3.5196 | 2988.3 | 3.5196
3030.3 | 499.0218 |  | 3039.2 | 736.094 | 3044.8 | 6.8533 | 3048.4 | 10.3088 | 3050.5 | 0.67714 | 3052.8 | 3.1979 | 3030.3 | 0.67714

## C5-C6
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 153.1368 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38960.5395 | 1 | 0 | 38960.5395 | 1 | 0 |  | -85.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.54 | 1 | 0 | 38960.54 | 1 | 0 |  | -43.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5405 | 1 | 0 | 38960.5405 | 1 | 0 |  | -1.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5409 | 1 | 0 | 38960.541 | 1 | 0 |  | 40.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5414 | 1 | 0 | 38960.5414 | 1 | 0 |  | 82.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5419 | 1 | 0 | 38960.5419 | 1 | 0 |  | 124.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5424 | 1 | 0 | 38960.5424 | 1 | 0 |  | 166.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5429 | 1 | 0 | 38960.5429 | 1 | 0 |  | 208.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5434 | 1 | 0 | 38960.5434 | 1 | 0 |  | 250.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5439 | 1 | 0 | 38960.5439 | 1 | 0 |  | 292.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5444 | 1 | 0 | 38960.5444 | 1 | 0 |  | 334.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5448 | 1 | 0 | 38960.5448 | 1 | 0 |  | 376.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5453 | 1 | 0 | 38960.5453 | 1 | 0 |  | 418.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5458 | 1 | 0 | 38960.5458 | 1 | 0 |  | 460.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5463 | 1 | 0 | 38960.5463 | 1 | 0 |  | 502.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5468 | 1 | 0 | 38960.5468 | 1 | 0 |  | 544.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5473 | 1 | 0 | 38960.5473 | 1 | 0 |  | 586.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5478 | 1 | 0 | 38960.5478 | 1 | 0 |  | 628.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5482 | 1 | 0 | 38960.5483 | 1 | 0 |  | 670.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5487 | 1 | 0 | 38960.5487 | 2 | 0 |  | 712.5 | 837.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250738 | 125319 | 250737.9994
38960.5492 | 1 | 0 | 38960.5492 | 1 | 0 |  | 754.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5497 | 1 | 0 | 38960.5497 | 1 | 0 |  | 796.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5502 | 1 | 0 | 38960.5502 | 1 | 0 |  | 838.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5507 | 1 | 0 | 38960.5507 | 1 | 0 |  | 880 | 1005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5512 | 1 | 0 | 38960.5512 | 1 | 0 |  | 922.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5516 | 1 | 0 | 38960.5517 | 1 | 0 |  | 964.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5521 | 1 | 0 | 38960.5521 | 1 | 0 |  | 1006 | 1131 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5526 | 1 | 0 | 38960.5526 | 1 | 0 |  | 1048 | 1173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5531 | 1 | 0 | 38960.5531 | 1 | 0 |  | 1090.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5536 | 1 | 0 | 38960.5536 | 1 | 0 |  | 1132 | 1257 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5541 | 1 | 0 | 38960.5541 | 1 | 0 |  | 1174.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5546 | 1 | 0 | 38960.5546 | 1 | 0 |  | 1216.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.555 | 1 | 0 | 38960.5551 | 1 | 0 |  | 1258 | 1383 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5555 | 1 | 0 | 38960.5555 | 1 | 0 |  | 1300 | 1425 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.556 | 1 | 0 | 38960.556 | 1 | 0 |  | 1342 | 1467 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5565 | 1 | 0 | 38960.5565 | 1 | 0 |  | 1384 | 1509 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.557 | 1 | 0 | 38960.557 | 1 | 0 |  | 1426 | 1551 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.5575 | 1 | 0 | 38960.5575 | 1 | 0 |  | 1468 | 1593 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38960.558 | 963 | 940 | 38960.558 | 976 | 951 |  | 1510 | 1635 | 58.7912 | 57.3871 | 59.5849 | 58.0586 | 0.58791 | 0.57387 | 0.59585 | 0.58059 | 0.014042 | 0.015263 | 12551.7415 | 8794.973 | 63.6781
38960.5584 | 884 | 862 | 38960.5585 | 571 | 644 |  | 1552 | 1677 | 53.9683 | 52.6252 | 34.8596 | 39.3162 | 0.53968 | 0.52625 | 0.3486 | 0.39316 | 0.013431 | 0.044567 | 12765.7569 | 9293.3095 | 87.5016
38960.5589 | 877 | 861 | 38960.5589 | 528 | 560 |  | 1594 | 1719 | 53.5409 | 52.5641 | 32.2344 | 34.188 | 0.53541 | 0.52564 | 0.32234 | 0.34188 | 0.009768 | 0.019536 | 66486.191 | 6355.985 | 88.0891
38960.5594 | 347 | 380 | 38960.5594 | 179 | 205 |  | 1636 | 1761 | 21.1844 | 23.199 | 10.928 | 12.5153 | 0.21184 | 0.23199 | 0.10928 | 0.12515 | 0.020147 | 0.015873 | 7399.3273 | 10027.6899 | 464.1555
38960.5599 | 629 | 32 | 38960.5599 | 851 | 643 |  | 1678 | 1803 | 38.4005 | 1.9536 | 51.9536 | 39.2552 | 0.384 | 0.019536 | 0.51954 | 0.39255 | 0.36447 | 0.12698 | 314.8424 | 43952.4608 | 5759.9575
38960.5604 | 33 | 29 | 38960.5604 | 2 | 1 |  | 1720 | 1845 | 2.0147 | 1.7705 | 0.1221 | 0.06105 | 0.020147 | 0.017705 | 0.001221 | 0.0006105 | 0.002442 | 0.0006105 | 62063.7374 | 251042.4914 | 8432.4341
38960.5609 | 2146 | 17 | 38960.5609 | 38 | 1 |  | 1762 | 1887 | 131.0134 | 1.0379 | 2.3199 | 0.06105 | 1.3101 | 0.010379 | 0.023199 | 0.0006105 | 1.2998 | 0.022589 | 17.0228 | 7936.8254 | 2006.3678
38960.5614 | 2162 | 0 | 38960.5614 | 111 | 0 |  | 1804 | 1929 | 131.9902 | 0 | 6.7766 | 0 | 1.3199 | 0 | 0.067766 | 0 | 1.3199 | 0.067766 | 16.0213 | 2159.8018 | 14.7014
38960.5618 | 2086 | 0 | 38960.5619 | 988 | 1 |  | 1846 | 1971 | 127.3504 | 0 | 60.3175 | 0.06105 | 1.2735 | 0 | 0.60317 | 0.0006105 | 1.2735 | 0.60256 | 20.2483 | 154.1418 | 18.9748
38960.5623 | 2392 | 15 | 38960.5623 | 2374 | 18 |  | 1888 | 2013 | 146.0317 | 0.91575 | 144.9328 | 1.0989 | 1.4603 | 0.0091575 | 1.4493 | 0.010989 | 1.4512 | 1.4383 | 5.4101 | 6.6417 | 42.0931
38960.5628 | 2047 | 0 | 38960.5628 | 2330 | 0 |  | 1930 | 2055 | 124.9695 | 0 | 142.2466 | 0 | 1.2497 | 0 | 1.4225 | 0 | 1.2497 | 1.4225 | 22.5393 | 7.6558 | 21.2896
38960.5633 | 2196 | 0 | 38960.5633 | 2361 | 0 |  | 1972 | 2097 | 134.0659 | 0 | 144.1392 | 0 | 1.3407 | 0 | 1.4414 | 0 | 1.3407 | 1.4414 | 14.225 | 6.2423 | 12.8843
38960.5638 | 2191 | 0 | 38960.5638 | 2478 | 0 |  | 2014 | 2139 | 133.7607 | 0 | 151.2821 | 0 | 1.3376 | 0 | 1.5128 | 0 | 1.3376 | 1.5128 | 14.4856 | 1.226 | 13.148
38960.5643 | 2242 | 0 | 38960.5643 | 1921 | 0 |  | 2056 | 2181 | 136.8742 | 0 | 117.2772 | 0 | 1.3687 | 0 | 1.1728 | 0 | 1.3687 | 1.1728 | 11.8814 | 30.5768 | 10.5126
38960.5648 | 2202 | 0 | 38960.5648 | 2477 | 0 |  | 2098 | 2223 | 134.4322 | 0 | 151.221 | 0 | 1.3443 | 0 | 1.5122 | 0 | 1.3443 | 1.5122 | 13.9137 | 1.2669 | 12.5694
38960.5652 | 2020 | 0 | 38960.5653 | 2302 | 0 |  | 2140 | 2265 | 123.3211 | 0 | 140.5372 | 0 | 1.2332 | 0 | 1.4054 | 0 | 1.2332 | 1.4054 | 24.1772 | 8.9652 | 22.944
38960.5657 | 2076 | 0 | 38960.5658 | 2190 | 0 |  | 2182 | 2307 | 126.7399 | 0 | 133.6996 | 0 | 1.2674 | 0 | 1.337 | 0 | 1.2674 | 1.337 | 20.8276 | 14.5379 | 19.5602
38960.5662 | 2358 | 0 | 38960.5662 | 2286 | 0 |  | 2224 | 2349 | 143.956 | 0 | 139.5604 | 0 | 1.4396 | 0 | 1.3956 | 0 | 1.4396 | 1.3956 | 6.3774 | 9.7279 | 4.9379
38960.5667 | 1986 | 0 | 38960.5667 | 2212 | 0 |  | 2266 | 2391 | 121.2454 | 0 | 135.0427 | 0 | 1.2125 | 0 | 1.3504 | 0 | 1.2125 | 1.3504 | 26.3031 | 13.3987 | 25.0907
38960.5672 | 2404 | 0 | 38960.5672 | 2099 | 0 |  | 2308 | 2433 | 146.7643 | 0 | 128.1441 | 0 | 1.4676 | 0 | 1.2814 | 0 | 1.4676 | 1.2814 | 4.3419 | 19.5036 | 2.8743
38960.5677 | 2273 | 0 | 38960.5677 | 2305 | 0 |  | 2350 | 2475 | 138.7668 | 0 | 140.7204 | 0 | 1.3877 | 0 | 1.4072 | 0 | 1.3877 | 1.4072 | 10.3555 | 8.8234 | 8.9678
38960.5682 | 2414 | 0 | 38960.5682 | 2098 | 0 |  | 2392 | 2517 | 147.3748 | 0 | 128.083 | 0 | 1.4737 | 0 | 1.2808 | 0 | 1.4737 | 1.2808 | 3.9097 | 19.5605 | 2.4359
38960.5686 | 2405 | 0 | 38960.5687 | 2065 | 0 |  | 2434 | 2559 | 146.8254 | 0 | 126.0684 | 0 | 1.4683 | 0 | 1.2607 | 0 | 1.4683 | 1.2607 | 4.2985 | 21.4712 | 2.8303
38960.5691 | 2318 | 0 | 38960.5692 | 2013 | 0 |  | 2476 | 2601 | 141.514 | 0 | 122.8938 | 0 | 1.4151 | 0 | 1.2289 | 0 | 1.4151 | 1.2289 | 8.2131 | 24.609 | 6.798
38960.5696 | 2089 | 0 | 38960.5696 | 1940 | 0 |  | 2518 | 2643 | 127.5336 | 0 | 118.4371 | 0 | 1.2753 | 0 | 1.1844 | 0 | 1.2753 | 1.1844 | 20.0756 | 29.2979 | 18.8003
38960.5701 | 2120 | 0 | 38960.5701 | 2492 | 0 |  | 2560 | 2685 | 129.4261 | 0 | 152.1368 | 0 | 1.2943 | 0 | 1.5214 | 0 | 1.2943 | 1.5214 | 18.3198 | 0.6573 | 17.0256
38960.5706 | 2305 | 0 | 38960.5706 | 2454 | 0 |  | 2602 | 2727 | 140.7204 | 0 | 149.8168 | 0 | 1.4072 | 0 | 1.4982 | 0 | 1.4072 | 1.4982 | 8.8234 | 2.216 | 7.4162
38960.5711 | 2358 | 0 | 38960.5711 | 1950 | 0 |  | 2644 | 2769 | 143.956 | 0 | 119.0476 | 0 | 1.4396 | 0 | 1.1905 | 0 | 1.4396 | 1.1905 | 6.3774 | 28.6349 | 4.9379
38960.5716 | 1885 | 0 | 38960.5716 | 1985 | 0 |  | 2686 | 2811 | 115.0794 | 0 | 121.1844 | 0 | 1.1508 | 0 | 1.2118 | 0 | 1.1508 | 1.2118 | 33.0706 | 26.3668 | 31.9198
38960.572 | 1983 | 0 | 38960.5721 | 2312 | 0 |  | 2728 | 2853 | 121.0623 | 0 | 141.1477 | 0 | 1.2106 | 0 | 1.4115 | 0 | 1.2106 | 1.4115 | 26.4942 | 8.4939 | 25.2836
38960.5725 | 2419 | 0 | 38960.5726 | 2392 | 0 |  | 2770 | 2895 | 147.6801 | 0 | 146.0317 | 0 | 1.4768 | 0 | 1.4603 | 0 | 1.4768 | 1.4603 | 3.6949 | 4.8654 | 2.2181
38960.573 | 2281 | 0 | 38960.573 | 2175 | 0 |  | 2812 | 2937 | 139.2552 | 0 | 132.7839 | 0 | 1.3926 | 0 | 1.3278 | 0 | 1.3926 | 1.3278 | 9.9684 | 15.3278 | 8.5759
38960.5735 | 1925 | 0 | 38960.5735 | 2416 | 0 |  | 2854 | 2979 | 117.5214 | 0 | 147.4969 | 0 | 1.1752 | 0 | 1.475 | 0 | 1.1752 | 1.475 | 30.3055 | 3.8237 | 29.1302
38960.574 | 2204 | 0 | 38960.574 | 2394 | 0 |  | 2896 | 3021 | 134.5543 | 0 | 146.1538 | 0 | 1.3455 | 0 | 1.4615 | 0 | 1.3455 | 1.4615 | 13.8103 | 4.7778 | 12.4648
38960.5745 | 2258 | 0 | 38960.5745 | 2061 | 0 |  | 2938 | 3063 | 137.851 | 0 | 125.8242 | 0 | 1.3785 | 0 | 1.2582 | 0 | 1.3785 | 1.2582 | 11.0886 | 21.7069 | 9.7101
38960.575 | 2068 | 0 | 38960.575 | 2455 | 0 |  | 2980 | 3105 | 126.2515 | 0 | 149.8779 | 0 | 1.2625 | 0 | 1.4988 | 0 | 1.2625 | 1.4988 | 21.295 | 2.1743 | 20.0325
38960.5755 | 2069 | 0 | 38960.5755 | 1933 | 0 |  | 3022 | 3147 | 126.3126 | 0 | 118.0098 | 0 | 1.2631 | 0 | 1.1801 | 0 | 1.2631 | 1.1801 | 21.2363 | 29.7662 | 19.9732
38960.5759 | 2245 | 0 | 38960.576 | 2222 | 0 |  | 3064 | 3189 | 137.0574 | 0 | 135.6532 | 0 | 1.3706 | 0 | 1.3565 | 0 | 1.3706 | 1.3565 | 11.7318 | 12.8884 | 10.3613

## B4-C6
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 154.4188 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38960.5395 | 1 | 0 | 38960.5395 | 1 | 0 |  | -88.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5399 | 1 | 0 | 38960.54 | 1 | 0 |  | -46.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5404 | 1 | 0 | 38960.5404 | 1 | 0 |  | -4.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5409 | 1 | 0 | 38960.5409 | 1 | 0 |  | 37.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5414 | 1 | 0 | 38960.5414 | 1 | 0 |  | 79.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5419 | 1 | 0 | 38960.5419 | 1 | 0 |  | 121.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5424 | 1 | 0 | 38960.5424 | 1 | 0 |  | 163.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5429 | 1 | 0 | 38960.5429 | 1 | 0 |  | 205.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5433 | 1 | 0 | 38960.5434 | 1 | 0 |  | 247.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5438 | 1 | 0 | 38960.5438 | 1 | 0 |  | 289.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5443 | 1 | 0 | 38960.5443 | 1 | 0 |  | 331.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5448 | 1 | 0 | 38960.5448 | 1 | 0 |  | 373.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5453 | 1 | 0 | 38960.5453 | 1 | 0 |  | 415.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5458 | 1 | 0 | 38960.5458 | 1 | 0 |  | 457.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5463 | 1 | 0 | 38960.5463 | 1 | 0 |  | 499.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5467 | 1 | 0 | 38960.5468 | 1 | 0 |  | 541.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5472 | 1 | 0 | 38960.5472 | 1 | 0 |  | 583.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5477 | 1 | 0 | 38960.5477 | 1 | 0 |  | 625.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5482 | 1 | 0 | 38960.5482 | 1 | 0 |  | 667.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5487 | 1 | 0 | 38960.5487 | 1 | 0 |  | 709.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5492 | 1 | 0 | 38960.5492 | 1 | 0 |  | 751.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5497 | 1 | 0 | 38960.5497 | 1 | 0 |  | 793.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5502 | 1 | 0 | 38960.5502 | 1 | 0 |  | 835.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5506 | 1 | 0 | 38960.5506 | 1 | 0 |  | 877.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5511 | 1 | 0 | 38960.5511 | 1 | 0 |  | 919.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5516 | 2 | 0 | 38960.5516 | 1 | 0 |  | 961.5 | 1086.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126369 | 252838 | 126368.9988
38960.5521 | 1 | 0 | 38960.5521 | 1 | 0 |  | 1003.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5526 | 1 | 0 | 38960.5526 | 1 | 0 |  | 1045.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5531 | 1 | 0 | 38960.5531 | 1 | 0 |  | 1087.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5536 | 1 | 0 | 38960.5536 | 1 | 0 |  | 1129.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.554 | 1 | 0 | 38960.5541 | 1 | 0 |  | 1171.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5545 | 1 | 0 | 38960.5545 | 1 | 0 |  | 1213.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.555 | 1 | 0 | 38960.555 | 1 | 0 |  | 1255.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5555 | 1 | 0 | 38960.5555 | 1 | 0 |  | 1297.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.556 | 1 | 0 | 38960.556 | 1 | 0 |  | 1339.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5565 | 1 | 0 | 38960.5565 | 1 | 0 |  | 1381.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.557 | 1 | 0 | 38960.557 | 1 | 0 |  | 1423.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5574 | 1 | 0 | 38960.5575 | 1 | 0 |  | 1465.5 | 1590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5579 | 1 | 0 | 38960.5579 | 1 | 0 |  | 1507.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5584 | 1 | 0 | 38960.5584 | 1 | 0 |  | 1549.5 | 1674.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5589 | 1 | 0 | 38960.5589 | 1 | 0 |  | 1591.5 | 1716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
| 1 | 0 | 38960.5594 | 1 | 0 |  | 1634 | 1759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38960.5599 | 1442 | 0 | 38960.5599 | 57 | 9 |  | 1675.5 | 1800.5 | 88.0342 | 0 | 3.4799 | 0.54945 | 0.88034 | 0 | 0.034799 | 0.0054945 | 0.88034 | 0.029304 | 75.4078 | 5169.5417 | 74.5274
38960.5604 | 1068 | 0 | 38960.5604 | 2 | 0 |  | 1717.5 | 1842.5 | 65.2015 | 0 | 0.1221 | 0 | 0.65201 | 0 | 0.001221 | 0 | 0.65201 | 0.001221 | 136.8333 | 126369 | 136.1813
38960.5608 | 2247 | 0 | 38960.5609 | 2 | 0 |  | 1759.5 | 1884.5 | 137.1795 | 0 | 0.1221 | 0 | 1.3718 | 0 | 0.001221 | 0 | 1.3718 | 0.001221 | 12.567 | 126369 | 11.1952
38960.5613 | 2019 | 0 | 38960.5613 | 143 | 0 |  | 1801.5 | 1926.5 | 123.2601 | 0 | 8.7302 | 0 | 1.2326 | 0 | 0.087302 | 0 | 1.2326 | 0.087302 | 25.2789 | 1668.7972 | 24.0463
38960.5618 | 2149 | 0 | 38960.5618 | 1628 | 17 |  | 1843.5 | 1968.5 | 131.1966 | 0 | 99.3895 | 1.0379 | 1.312 | 0 | 0.99389 | 0.010379 | 1.312 | 0.98352 | 17.7003 | 57.0068 | 16.3884
38960.5623 | 2501 | 0 | 38960.5623 | 1868 | 0 |  | 1885.5 | 2010.5 | 152.6862 | 0 | 114.0415 | 0 | 1.5269 | 0 | 1.1404 | 0 | 1.5269 | 1.1404 | 1.1347 | 35.4058 | 0.39212
38960.5628 | 2513 | 0 | 38960.5628 | 2305 | 0 |  | 1927.5 | 2052.5 | 153.4188 | 0 | 140.7204 | 0 | 1.5342 | 0 | 1.4072 | 0 | 1.5342 | 1.4072 | 0.65181 | 9.7345 | 0.88238
38960.5633 | 2322 | 0 | 38960.5633 | 2040 | 0 |  | 1969.5 | 2094.5 | 141.7582 | 0 | 124.5421 | 0 | 1.4176 | 0 | 1.2454 | 0 | 1.4176 | 1.2454 | 8.9311 | 23.9892 | 7.5135
38960.5638 | 1964 | 0 | 38960.5638 | 2051 | 0 |  | 2011.5 | 2136.5 | 119.9023 | 0 | 125.2137 | 0 | 1.199 | 0 | 1.2521 | 0 | 1.199 | 1.2521 | 28.7872 | 23.3242 | 27.5881
| 2067 | 0 | 38960.5643 | 2240 | 0 |  | 2054 | 2179 | 126.1905 | 0 | 136.7521 | 0 | 1.2619 | 0 | 1.3675 | 0 | 1.2619 | 1.3675 | 22.3696 | 12.9187 | 21.1077
38960.5647 | 2169 | 0 | 38960.5647 | 2146 | 0 |  | 2095.5 | 2220.5 | 132.4176 | 0 | 131.0134 | 0 | 1.3242 | 0 | 1.3101 | 0 | 1.3242 | 1.3101 | 16.615 | 17.8649 | 15.2909
38960.5652 | 2496 | 0 | 38960.5652 | 2052 | 0 |  | 2137.5 | 2262.5 | 152.381 | 0 | 125.2747 | 0 | 1.5238 | 0 | 1.2527 | 0 | 1.5238 | 1.2527 | 1.3373 | 23.2641 | 0.18647
38960.5657 | 2506 | 0 | 38960.5657 | 1949 | 0 |  | 2179.5 | 2304.5 | 152.9915 | 0 | 118.9866 | 0 | 1.5299 | 0 | 1.1899 | 0 | 1.5299 | 1.1899 | 0.93296 | 29.7783 | 0.59695
38960.5662 | 2510 | 0 | 38960.5662 | 2470 | 0 |  | 2221.5 | 2346.5 | 153.2357 | 0 | 150.7937 | 0 | 1.5324 | 0 | 1.5079 | 0 | 1.5324 | 1.5079 | 0.77211 | 2.404 | 0.76024
38960.5667 | 2469 | 0 | 38960.5667 | 2232 | 0 |  | 2263.5 | 2388.5 | 150.7326 | 0 | 136.2637 | 0 | 1.5073 | 0 | 1.3626 | 0 | 1.5073 | 1.3626 | 2.4455 | 13.3235 | 0.9382
38960.5672 | 2054 | 0 | 38960.5672 | 2335 | 0 |  | 2305.5 | 2430.5 | 125.3968 | 0 | 142.5519 | 0 | 1.254 | 0 | 1.4255 | 0 | 1.254 | 1.4255 | 23.1441 | 8.3246 | 21.8901
38960.5677 | 2023 | 0 | 38960.5677 | 2267 | 0 |  | 2347.5 | 2472.5 | 123.5043 | 0 | 138.4005 | 0 | 1.235 | 0 | 1.384 | 0 | 1.235 | 1.384 | 25.0311 | 11.5739 | 23.7961
38960.5681 | 2330 | 0 | 38960.5681 | 2301 | 0 |  | 2389.5 | 2514.5 | 142.2466 | 0 | 140.4762 | 0 | 1.4225 | 0 | 1.4048 | 0 | 1.4225 | 1.4048 | 8.5571 | 9.9252 | 7.1346
38960.5686 | 2290 | 0 | 38960.5686 | 2464 | 0 |  | 2431 | 2556 | 139.8046 | 0 | 150.4274 | 0 | 1.398 | 0 | 1.5043 | 0 | 1.398 | 1.5043 | 10.4533 | 2.6534 | 9.0552
38960.5691 | 2292 | 0 | 38960.5691 | 2112 | 0 |  | 2473.5 | 2598.5 | 139.9267 | 0 | 128.9377 | 0 | 1.3993 | 0 | 1.2894 | 0 | 1.3993 | 1.2894 | 10.3569 | 19.7623 | 8.9576
38960.5696 | 2155 | 0 | 38960.5696 | 2101 | 0 |  | 2515 | 2640 | 131.5629 | 0 | 128.2662 | 0 | 1.3156 | 0 | 1.2827 | 0 | 1.3156 | 1.2827 | 17.3726 | 20.3893 | 16.057
38960.5701 | 2223 | 0 | 38960.5701 | 2085 | 0 |  | 2557.5 | 2682.5 | 135.7143 | 0 | 127.2894 | 0 | 1.3571 | 0 | 1.2729 | 0 | 1.3571 | 1.2729 | 13.7823 | 21.3132 | 12.4251
38960.5706 | 2485 | 0 | 38960.5706 | 1944 | 0 |  | 2599 | 2724 | 151.7094 | 0 | 118.6813 | 0 | 1.5171 | 0 | 1.1868 | 0 | 1.5171 | 1.1868 | 1.7859 | 30.1121 | 0.26882
38960.571 | 2291 | 0 | 38960.5711 | 2426 | 0 |  | 2641 | 2766 | 139.8657 | 0 | 148.1074 | 0 | 1.3987 | 0 | 1.4811 | 0 | 1.3987 | 1.4811 | 10.4051 | 4.2613 | 9.0064
38960.5715 | 2501 | 0 | 38960.5716 | 1974 | 0 |  | 2683 | 2808 | 152.6862 | 0 | 120.5128 | 0 | 1.5269 | 0 | 1.2051 | 0 | 1.5269 | 1.2051 | 1.1347 | 28.1348 | 0.39212
38960.572 | 2470 | 0 | 38960.572 | 1887 | 0 |  | 2725.5 | 2850.5 | 150.7937 | 0 | 115.2015 | 0 | 1.5079 | 0 | 1.152 | 0 | 1.5079 | 1.152 | 2.404 | 34.0424 | 0.89611
38960.5725 | 2104 | 0 | 38960.5725 | 1992 | 0 |  | 2767 | 2892 | 128.4493 | 0 | 121.6117 | 0 | 1.2845 | 0 | 1.2161 | 0 | 1.2845 | 1.2161 | 20.2177 | 26.9769 | 18.9332
38960.573 | 2015 | 0 | 38960.573 | 2235 | 0 |  | 2809 | 2934 | 123.0159 | 0 | 136.4469 | 0 | 1.2302 | 0 | 1.3645 | 0 | 1.2302 | 1.3645 | 25.5275 | 13.1714 | 24.2974
38960.5735 | 2489 | 0 | 38960.5735 | 2445 | 0 |  | 2851 | 2976 | 151.9536 | 0 | 149.2674 | 0 | 1.5195 | 0 | 1.4927 | 0 | 1.5195 | 1.4927 | 1.6223 | 3.4511 | 0.1028
38960.574 | 1842 | 0 | 38960.574 | 2426 | 0 |  | 2893 | 3018 | 112.4542 | 0 | 148.1074 | 0 | 1.1245 | 0 | 1.4811 | 0 | 1.1245 | 1.4811 | 37.317 | 4.2613 | 36.1925
38960.5744 | 2436 | 0 | 38960.5745 | 2186 | 0 |  | 2935 | 3060 | 148.7179 | 0 | 133.4554 | 0 | 1.4872 | 0 | 1.3346 | 0 | 1.4872 | 1.3346 | 3.8333 | 15.7081 | 2.3462
38960.5749 | 2032 | 0 | 38960.575 | 1910 | 0 |  | 2977 | 3102 | 124.0537 | 0 | 116.6056 | 0 | 1.2405 | 0 | 1.1661 | 0 | 1.2405 | 1.1661 | 24.4774 | 32.4283 | 23.2368
38960.5754 | 2092 | 0 | 38960.5754 | 1944 | 0 |  | 3019 | 3144 | 127.7167 | 0 | 118.6813 | 0 | 1.2772 | 0 | 1.1868 | 0 | 1.2772 | 1.1868 | 20.9073 | 30.1121 | 19.6301
38960.5759 | 2293 | 0 | 38960.5759 | 2451 | 0 |  | 3061.5 | 3186.5 | 139.9878 | 0 | 149.6337 | 0 | 1.3999 | 0 | 1.4963 | 0 | 1.3999 | 1.4963 | 10.3088 | 3.1979 | 8.9089

## B4-C5
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 154.5409 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38960.5394 | 1 | 0 | 38960.5394 | 1 | 0 |  | -91.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5399 | 1 | 0 | 38960.5399 | 1 | 0 |  | -49 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5404 | 1 | 0 | 38960.5404 | 1 | 0 |  | -7.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5409 | 1 | 0 | 38960.5409 | 1 | 0 |  | 34.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5414 | 1 | 0 | 38960.5414 | 1 | 0 |  | 76.5 | 201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5419 | 1 | 0 | 38960.5419 | 1 | 0 |  | 118.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5423 | 1 | 0 | 38960.5423 | 1 | 0 |  | 160.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5428 | 1 | 0 | 38960.5428 | 1 | 0 |  | 202.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5433 | 1 | 0 | 38960.5433 | 1 | 0 |  | 244.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5438 | 1 | 0 | 38960.5438 | 1 | 0 |  | 286.5 | 411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5443 | 1 | 0 | 38960.5443 | 1 | 0 |  | 328.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5448 | 1 | 0 | 38960.5448 | 1 | 0 |  | 370.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5453 | 1 | 0 | 38960.5453 | 1 | 0 |  | 412.5 | 537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5457 | 1 | 0 | 38960.5458 | 1 | 0 |  | 454.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5462 | 1 | 0 | 38960.5462 | 1 | 0 |  | 496.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5467 | 1 | 0 | 38960.5467 | 1 | 0 |  | 538.5 | 663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5472 | 1 | 0 | 38960.5472 | 1 | 0 |  | 580.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5477 | 1 | 0 | 38960.5477 | 1 | 0 |  | 622.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5482 | 1 | 0 | 38960.5482 | 1 | 0 |  | 664.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5487 | 1 | 0 | 38960.5487 | 1 | 0 |  | 706.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5491 | 1 | 0 | 38960.5492 | 1 | 0 |  | 748.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5496 | 1 | 0 | 38960.5496 | 1 | 0 |  | 790.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5501 | 1 | 0 | 38960.5501 | 1 | 0 |  | 832.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5506 | 1 | 0 | 38960.5506 | 1 | 0 |  | 874.5 | 999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5511 | 1 | 0 | 38960.5511 | 1 | 0 |  | 916.5 | 1041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5516 | 1 | 0 | 38960.5516 | 1 | 0 |  | 958.5 | 1083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5521 | 2 | 0 | 38960.5521 | 1 | 0 |  | 1000.5 | 1125.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126469 | 253038 | 126468.9988
38960.5525 | 2 | 0 | 38960.5526 | 1 | 0 |  | 1042.5 | 1167.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126469 | 253038 | 126468.9988
38960.553 | 1 | 0 | 38960.553 | 1 | 0 |  | 1084.5 | 1209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5535 | 1 | 0 | 38960.5535 | 1 | 0 |  | 1126.5 | 1251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.554 | 1 | 0 | 38960.554 | 1 | 0 |  | 1168.5 | 1293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5545 | 1 | 0 | 38960.5545 | 1 | 0 |  | 1210.5 | 1335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.555 | 1 | 0 | 38960.555 | 1 | 0 |  | 1252.5 | 1377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5555 | 1 | 0 | 38960.5555 | 1 | 0 |  | 1294.5 | 1419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5559 | 1 | 0 | 38960.556 | 1 | 0 |  | 1336.5 | 1461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5564 | 1 | 0 | 38960.5564 | 1 | 0 |  | 1378.5 | 1503.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5569 | 1 | 0 | 38960.5569 | 1 | 0 |  | 1420.5 | 1545.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5574 | 1 | 0 | 38960.5574 | 1 | 0 |  | 1462.5 | 1587.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5579 | 1 | 0 | 38960.5579 | 1 | 0 |  | 1504.5 | 1629.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5584 | 1 | 0 | 38960.5584 | 1 | 0 |  | 1546.5 | 1671.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5589 | 1 | 0 | 38960.5589 | 1 | 0 |  | 1588.5 | 1713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5594 | 1 | 0 | 38960.5594 | 1 | 0 |  | 1630.5 | 1755.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38960.5598 | 728 | 1 | 38960.5598 | 2 | 0 |  | 1672.5 | 1797.5 | 44.4444 | 0.06105 | 0.1221 | 0 | 0.44444 | 0.0006105 | 0.001221 | 0 | 0.44383 | 0.001221 | 248.058 | 126469 | 180095.597
38960.5603 | 987 | 0 | 38960.5603 | 86 | 0 |  | 1714.5 | 1839.5 | 60.2564 | 0 | 5.2503 | 0 | 0.60256 | 0 | 0.052503 | 0 | 0.60256 | 0.052503 | 156.4721 | 2843.4651 | 155.8696
38960.5608 | 2346 | 0 | 38960.5608 | 1963 | 0 |  | 1756.5 | 1881.5 | 143.2234 | 0 | 119.8413 | 0 | 1.4322 | 0 | 1.1984 | 0 | 1.4322 | 1.1984 | 7.902 | 28.9547 | 6.4697
38960.5613 | 2406 | 0 | 38960.5613 | 2211 | 0 |  | 1798.5 | 1923.5 | 146.8864 | 0 | 134.9817 | 0 | 1.4689 | 0 | 1.3498 | 0 | 1.4689 | 1.3498 | 5.2111 | 14.4903 | 3.7423
38960.5618 | 2400 | 0 | 38960.5618 | 1842 | 0 |  | 1840.5 | 1965.5 | 146.5201 | 0 | 112.4542 | 0 | 1.4652 | 0 | 1.1245 | 0 | 1.4652 | 1.1245 | 5.4742 | 37.4256 | 4.009
38960.5623 | 2078 | 0 | 38960.5623 | 1924 | 0 |  | 1882.5 | 2007.5 | 126.862 | 0 | 117.4603 | 0 | 1.2686 | 0 | 1.1746 | 0 | 1.2686 | 1.1746 | 21.8181 | 31.5686 | 20.5495
38960.5628 | 2010 | 0 | 38960.5628 | 2334 | 0 |  | 1924.5 | 2049.5 | 122.7106 | 0 | 142.4908 | 0 | 1.2271 | 0 | 1.4249 | 0 | 1.2271 | 1.4249 | 25.9393 | 8.4567 | 24.7122
38960.5632 | 1932 | 0 | 38960.5633 | 2128 | 0 |  | 1966.5 | 2091.5 | 117.9487 | 0 | 129.9145 | 0 | 1.1795 | 0 | 1.2991 | 0 | 1.1795 | 1.2991 | 31.0238 | 18.9558 | 29.8443
38960.5637 | 1935 | 0 | 38960.5637 | 2074 | 0 |  | 2008.5 | 2133.5 | 118.1319 | 0 | 126.6178 | 0 | 1.1813 | 0 | 1.2662 | 0 | 1.1813 | 1.2662 | 30.8207 | 22.053 | 29.6394
38960.5642 | 2300 | 0 | 38960.5642 | 2219 | 0 |  | 2050.5 | 2175.5 | 140.4151 | 0 | 135.4701 | 0 | 1.4042 | 0 | 1.3547 | 0 | 1.4042 | 1.3547 | 10.06 | 14.0775 | 8.6558
38960.5647 | 2270 | 0 | 38960.5647 | 2382 | 0 |  | 2092.5 | 2217.5 | 138.5836 | 0 | 145.4212 | 0 | 1.3858 | 0 | 1.4542 | 0 | 1.3858 | 1.4542 | 11.5145 | 6.2712 | 10.1287
38960.5652 | 2001 | 0 | 38960.5652 | 2050 | 0 |  | 2134.5 | 2259.5 | 122.1612 | 0 | 125.1526 | 0 | 1.2216 | 0 | 1.2515 | 0 | 1.2216 | 1.2515 | 26.5057 | 23.482 | 25.2841
38960.5657 | 2369 | 0 | 38960.5657 | 2126 | 0 |  | 2176.5 | 2301.5 | 144.6276 | 0 | 129.7924 | 0 | 1.4463 | 0 | 1.2979 | 0 | 1.4463 | 1.2979 | 6.8544 | 19.0677 | 5.4081
38960.5662 | 1984 | 0 | 38960.5662 | 1869 | 0 |  | 2218.5 | 2343.5 | 121.1233 | 0 | 114.1026 | 0 | 1.2112 | 0 | 1.141 | 0 | 1.2112 | 1.141 | 27.5897 | 35.4403 | 26.3785
38960.5666 | 1961 | 0 | 38960.5667 | 2362 | 0 |  | 2260.5 | 2385.5 | 119.7192 | 0 | 144.2002 | 0 | 1.1972 | 0 | 1.442 | 0 | 1.1972 | 1.442 | 29.0862 | 7.171 | 27.889
38960.5671 | 2068 | 0 | 38960.5671 | 1965 | 0 |  | 2302.5 | 2427.5 | 126.2515 | 0 | 119.9634 | 0 | 1.2625 | 0 | 1.1996 | 0 | 1.2625 | 1.1996 | 22.4072 | 28.8234 | 21.1446
38960.5676 | 2097 | 0 | 38960.5676 | 1884 | 0 |  | 2344.5 | 2469.5 | 128.022 | 0 | 115.0183 | 0 | 1.2802 | 0 | 1.1502 | 0 | 1.2802 | 1.1502 | 20.7144 | 34.362 | 19.4341
38960.5681 | 2175 | 0 | 38960.5681 | 2375 | 0 |  | 2386.5 | 2511.5 | 132.7839 | 0 | 144.9939 | 0 | 1.3278 | 0 | 1.4499 | 0 | 1.3278 | 1.4499 | 16.3853 | 6.5844 | 15.0574
38960.5686 | 2515 | 0 | 38960.5686 | 2099 | 0 |  | 2428.5 | 2553.5 | 153.5409 | 0 | 128.1441 | 0 | 1.5354 | 0 | 1.2814 | 0 | 1.5354 | 1.2814 | 0.65129 | 20.5993 | 0.88412
38960.5691 | 1990 | 0 | 38960.5691 | 2326 | 0 |  | 2470.5 | 2595.5 | 121.4896 | 0 | 142.0024 | 0 | 1.2149 | 0 | 1.42 | 0 | 1.2149 | 1.42 | 27.205 | 8.8298 | 25.9901
38960.5696 | 2497 | 0 | 38960.5696 | 1876 | 0 |  | 2512.5 | 2637.5 | 152.442 | 0 | 114.5299 | 0 | 1.5244 | 0 | 1.1453 | 0 | 1.5244 | 1.1453 | 1.3769 | 34.935 | 0.14757
38960.57 | 2243 | 0 | 38960.5701 | 1923 | 0 |  | 2554.5 | 2679.5 | 136.9353 | 0 | 117.3993 | 0 | 1.3694 | 0 | 1.174 | 0 | 1.3694 | 1.174 | 12.8569 | 31.637 | 11.4875
38960.5705 | 1978 | 0 | 38960.5705 | 1892 | 0 |  | 2596.5 | 2721.5 | 120.757 | 0 | 115.5067 | 0 | 1.2076 | 0 | 1.1551 | 0 | 1.2076 | 1.1551 | 27.9767 | 33.7939 | 26.7692
38960.571 | 1966 | 0 | 38960.571 | 1960 | 0 |  | 2638.5 | 2763.5 | 120.0244 | 0 | 119.6581 | 0 | 1.2002 | 0 | 1.1966 | 0 | 1.2002 | 1.1966 | 28.7579 | 29.152 | 27.5576
38960.5715 | 2006 | 0 | 38960.5715 | 2362 | 0 |  | 2680.5 | 2805.5 | 122.4664 | 0 | 144.2002 | 0 | 1.2247 | 0 | 1.442 | 0 | 1.2247 | 1.442 | 26.1904 | 7.171 | 24.9658
38960.572 | 2454 | 0 | 38960.572 | 1891 | 0 |  | 2722.5 | 2847.5 | 149.8168 | 0 | 115.4457 | 0 | 1.4982 | 0 | 1.1545 | 0 | 1.4982 | 1.1545 | 3.1532 | 33.8646 | 1.6551
38960.5725 | 2503 | 0 | 38960.5725 | 2232 | 0 |  | 2764.5 | 2889.5 | 152.8083 | 0 | 136.2637 | 0 | 1.5281 | 0 | 1.3626 | 0 | 1.5281 | 1.3626 | 1.1338 | 13.4131 | 0.39424
38960.573 | 2431 | 0 | 38960.573 | 2112 | 0 |  | 2806.5 | 2931.5 | 148.4127 | 0 | 128.9377 | 0 | 1.4841 | 0 | 1.2894 | 0 | 1.4841 | 1.2894 | 4.1292 | 19.857 | 2.645
38960.5734 | 2132 | 0 | 38960.5735 | 2316 | 0 |  | 2848.5 | 2973.5 | 130.1587 | 0 | 141.3919 | 0 | 1.3016 | 0 | 1.4139 | 0 | 1.3016 | 1.4139 | 18.7326 | 9.2997 | 17.4311
38960.5739 | 1932 | 0 | 38960.5739 | 2383 | 0 |  | 2890.5 | 3015.5 | 117.9487 | 0 | 145.4823 | 0 | 1.1795 | 0 | 1.4548 | 0 | 1.1795 | 1.4548 | 31.0238 | 6.2266 | 29.8443
38960.5744 | 2477 | 0 | 38960.5744 | 1923 | 0 |  | 2932.5 | 3057.5 | 151.221 | 0 | 117.3993 | 0 | 1.5122 | 0 | 1.174 | 0 | 1.5122 | 1.174 | 2.1954 | 31.637 | 0.68319
38960.5749 | 2196 | 0 | 38960.5749 | 2012 | 0 |  | 2974.5 | 3099.5 | 134.0659 | 0 | 122.8327 | 0 | 1.3407 | 0 | 1.2283 | 0 | 1.3407 | 1.2283 | 15.2723 | 25.8141 | 13.9317
38960.5754 | 2061 | 0 | 38960.5754 | 2216 | 0 |  | 3016.5 | 3141.5 | 125.8242 | 0 | 135.2869 | 0 | 1.2582 | 0 | 1.3529 | 0 | 1.2582 | 1.3529 | 22.8229 | 14.2319 | 21.5647
38960.5759 | 2041 | 0 | 38960.5759 | 2074 | 0 |  | 3058.5 | 3183.5 | 124.6032 | 0 | 126.6178 | 0 | 1.246 | 0 | 1.2662 | 0 | 1.246 | 1.2662 | 24.0265 | 22.053 | 22.7804

## B3-C6
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 154.4799 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38960.5394 | 1 | 0 | 38960.5394 | 1 | 0 |  | -94 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5399 | 1 | 0 | 38960.5399 | 1 | 0 |  | -52 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5404 | 1 | 0 | 38960.5404 | 4 | 0 |  | -10 | 115 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 252938 | 63159.5 | 252937.9994
38960.5408 | 1 | 0 | 38960.5409 | 1 | 0 |  | 32 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5413 | 1 | 0 | 38960.5414 | 1 | 0 |  | 74 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5418 | 1 | 0 | 38960.5418 | 1 | 0 |  | 116 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5423 | 1 | 0 | 38960.5423 | 1 | 0 |  | 158 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5428 | 1 | 0 | 38960.5428 | 1 | 0 |  | 200 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5433 | 1 | 0 | 38960.5433 | 1 | 0 |  | 242 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5438 | 1 | 1 | 38960.5438 | 1 | 0 |  | 284 | 409 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 639776318.44 | 252938 | 252738.079
38960.5442 | 1 | 0 | 38960.5443 | 1 | 0 |  | 326 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5447 | 1 | 0 | 38960.5448 | 1 | 0 |  | 368 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5452 | 1 | 0 | 38960.5452 | 1 | 0 |  | 410 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5457 | 1 | 0 | 38960.5457 | 1 | 0 |  | 452 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5462 | 1 | 0 | 38960.5462 | 1 | 0 |  | 494 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5467 | 1 | 0 | 38960.5467 | 1 | 0 |  | 536 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5472 | 1 | 0 | 38960.5472 | 1 | 0 |  | 578 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5477 | 1 | 0 | 38960.5477 | 1 | 0 |  | 620 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5481 | 1 | 0 | 38960.5482 | 1 | 0 |  | 662 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5486 | 1 | 0 | 38960.5486 | 1 | 0 |  | 704 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5491 | 1 | 0 | 38960.5491 | 1 | 0 |  | 746 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5496 | 1 | 0 | 38960.5496 | 1 | 0 |  | 788 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5501 | 1 | 0 | 38960.5501 | 1 | 0 |  | 830 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5506 | 1 | 0 | 38960.5506 | 1 | 0 |  | 872 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5511 | 1 | 0 | 38960.5511 | 1 | 0 |  | 914 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5515 | 1 | 0 | 38960.5516 | 1 | 0 |  | 955.5 | 1080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.552 | 1 | 0 | 38960.552 | 1 | 0 |  | 998 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5525 | 1 | 0 | 38960.5525 | 1 | 0 |  | 1040 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.553 | 1 | 0 | 38960.553 | 1 | 0 |  | 1082 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5535 | 1 | 0 | 38960.5535 | 1 | 0 |  | 1123.5 | 1248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.554 | 1 | 0 | 38960.554 | 1 | 0 |  | 1166 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5545 | 1 | 0 | 38960.5545 | 1 | 0 |  | 1208 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5549 | 1 | 0 | 38960.555 | 1 | 0 |  | 1249.5 | 1374.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5554 | 1 | 0 | 38960.5554 | 1 | 0 |  | 1291.5 | 1416.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5559 | 1 | 0 | 38960.5559 | 1 | 0 |  | 1333.5 | 1458.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5564 | 1 | 0 | 38960.5564 | 1 | 0 |  | 1375.5 | 1500.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5569 | 1 | 0 | 38960.5569 | 1 | 0 |  | 1418 | 1543 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5574 | 1 | 0 | 38960.5574 | 1 | 0 |  | 1459.5 | 1584.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5579 | 1 | 0 | 38960.5579 | 1 | 0 |  | 1501.5 | 1626.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5583 | 1 | 0 | 38960.5584 | 1 | 0 |  | 1543.5 | 1668.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5588 | 1 | 0 | 38960.5588 | 1 | 0 |  | 1585.5 | 1710.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5593 | 1 | 0 | 38960.5593 | 1 | 0 |  | 1627.5 | 1752.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252938 | 252938 | 252937.9994
38960.5598 | 2112 | 1 | 38960.5598 | 1 | 0 |  | 1669.5 | 1794.5 | 128.9377 | 0.06105 | 0.06105 | 0 | 1.2894 | 0.0006105 | 0.0006105 | 0 | 1.2888 | 0.0006105 | 19.819 | 252938.0001 | 41721.5052
38960.5603 | 2151 | 1 | 38960.5603 | 2 | 0 |  | 1711.5 | 1836.5 | 131.3187 | 0.06105 | 0.1221 | 0 | 1.3132 | 0.0006105 | 0.001221 | 0 | 1.3126 | 0.001221 | 17.6456 | 126419 | 37808.093
38960.5608 | 2063 | 0 | 38960.5608 | 905 | 0 |  | 1753.5 | 1878.5 | 125.9463 | 0 | 55.2503 | 0 | 1.2595 | 0 | 0.5525 | 0 | 1.2595 | 0.5525 | 22.6554 | 179.6 | 21.3959
38960.5613 | 2309 | 0 | 38960.5613 | 24 | 0 |  | 1795.5 | 1920.5 | 140.9646 | 0 | 1.4652 | 0 | 1.4096 | 0 | 0.014652 | 0 | 1.4096 | 0.014652 | 9.5877 | 10443.25 | 8.1781
38960.5617 | 2457 | 0 | 38960.5618 | 1979 | 30 |  | 1837.5 | 1962.5 | 150 | 0 | 120.8181 | 1.8315 | 1.5 | 0 | 1.2082 | 0.018315 | 1.5 | 1.1899 | 2.9866 | 29.8297 | 1.4866
38960.5622 | 2514 | 0 | 38960.5622 | 2227 | 0 |  | 1879.5 | 2004.5 | 153.4799 | 0 | 135.9585 | 0 | 1.5348 | 0 | 1.3596 | 0 | 1.5348 | 1.3596 | 0.65155 | 13.6228 | 0.88325
38960.5627 | 2094 | 0 | 38960.5627 | 2352 | 0 |  | 1921.5 | 2046.5 | 127.8388 | 0 | 143.5897 | 0 | 1.2784 | 0 | 1.4359 | 0 | 1.2784 | 1.4359 | 20.8395 | 7.5842 | 19.5612
38960.5632 | 2327 | 0 | 38960.5632 | 2214 | 0 |  | 1963.5 | 2088.5 | 142.0635 | 0 | 135.1648 | 0 | 1.4206 | 0 | 1.3516 | 0 | 1.4206 | 1.3516 | 8.74 | 14.29 | 7.3194
38960.5637 | 2222 | 0 | 38960.5637 | 2452 | 0 |  | 2005.5 | 2130.5 | 135.6532 | 0 | 149.6947 | 0 | 1.3565 | 0 | 1.4969 | 0 | 1.3565 | 1.4969 | 13.8785 | 3.1966 | 12.522
38960.5642 | 2396 | 0 | 38960.5642 | 2401 | 0 |  | 2047.5 | 2172.5 | 146.2759 | 0 | 146.5812 | 0 | 1.4628 | 0 | 1.4658 | 0 | 1.4628 | 1.4658 | 5.6085 | 5.3886 | 4.1458
38960.5647 | 2279 | 0 | 38960.5647 | 2456 | 0 |  | 2089.5 | 2214.5 | 139.1331 | 0 | 149.9389 | 0 | 1.3913 | 0 | 1.4994 | 0 | 1.3913 | 1.4994 | 11.0303 | 3.0285 | 9.6389
38960.5652 | 2373 | 0 | 38960.5652 | 2060 | 0 |  | 2131.5 | 2256.5 | 144.8718 | 0 | 125.7631 | 0 | 1.4487 | 0 | 1.2576 | 0 | 1.4487 | 1.2576 | 6.6321 | 22.834 | 5.1834
38960.5656 | 2414 | 0 | 38960.5656 | 2188 | 0 |  | 2173.5 | 2298.5 | 147.3748 | 0 | 133.5775 | 0 | 1.4737 | 0 | 1.3358 | 0 | 1.4737 | 1.3358 | 4.821 | 15.6481 | 3.3473
38960.5661 | 2390 | 0 | 38960.5661 | 1952 | 0 |  | 2215.5 | 2340.5 | 145.9096 | 0 | 119.1697 | 0 | 1.4591 | 0 | 1.1917 | 0 | 1.4591 | 1.1917 | 5.8736 | 29.6301 | 4.4145
38960.5666 | 2176 | 0 | 38960.5666 | 2069 | 0 |  | 2257.5 | 2382.5 | 132.8449 | 0 | 126.3126 | 0 | 1.3284 | 0 | 1.2631 | 0 | 1.3284 | 1.2631 | 16.2858 | 22.2997 | 14.9574
38960.5671 | 2237 | 0 | 38960.5671 | 1997 | 0 |  | 2299.5 | 2424.5 | 136.569 | 0 | 121.917 | 0 | 1.3657 | 0 | 1.2192 | 0 | 1.3657 | 1.2192 | 13.1149 | 26.7091 | 11.7492
38960.5676 | 2124 | 0 | 38960.5676 | 2352 | 0 |  | 2341.5 | 2466.5 | 129.6703 | 0 | 143.5897 | 0 | 1.2967 | 0 | 1.4359 | 0 | 1.2967 | 1.4359 | 19.1328 | 7.5842 | 17.8361
38960.5681 | 2335 | 0 | 38960.5681 | 2140 | 0 |  | 2383.5 | 2508.5 | 142.5519 | 0 | 130.6471 | 0 | 1.4255 | 0 | 1.3065 | 0 | 1.4255 | 1.3065 | 8.3675 | 18.2421 | 6.9419
38960.5686 | 2417 | 0 | 38960.5686 | 2025 | 0 |  | 2425.5 | 2550.5 | 147.558 | 0 | 123.6264 | 0 | 1.4756 | 0 | 1.2363 | 0 | 1.4756 | 1.2363 | 4.6909 | 24.957 | 3.2154
38960.569 | 2385 | 0 | 38960.5691 | 2485 | 0 |  | 2467.5 | 2592.5 | 145.6044 | 0 | 151.7094 | 0 | 1.456 | 0 | 1.5171 | 0 | 1.456 | 1.5171 | 6.0956 | 1.8262 | 4.6396
38960.5695 | 2260 | 0 | 38960.5695 | 2244 | 0 |  | 2509.5 | 2634.5 | 137.9731 | 0 | 136.9963 | 0 | 1.3797 | 0 | 1.37 | 0 | 1.3797 | 1.37 | 11.9637 | 12.762 | 10.584
38960.57 | 1924 | 0 | 38960.57 | 1980 | 0 |  | 2551.5 | 2676.5 | 117.4603 | 0 | 120.8791 | 0 | 1.1746 | 0 | 1.2088 | 0 | 1.1746 | 1.2088 | 31.5166 | 27.797 | 30.342
38960.5705 | 2213 | 0 | 38960.5705 | 2035 | 0 |  | 2593.5 | 2718.5 | 135.1038 | 0 | 124.2369 | 0 | 1.351 | 0 | 1.2424 | 0 | 1.351 | 1.2424 | 14.3416 | 24.343 | 12.9906
38960.571 | 2153 | 0 | 38960.571 | 2025 | 0 |  | 2635.5 | 2760.5 | 131.4408 | 0 | 123.6264 | 0 | 1.3144 | 0 | 1.2363 | 0 | 1.3144 | 1.2363 | 17.5281 | 24.957 | 16.2137
38960.5715 | 2270 | 0 | 38960.5715 | 2323 | 0 |  | 2677.5 | 2802.5 | 138.5836 | 0 | 141.8193 | 0 | 1.3858 | 0 | 1.4182 | 0 | 1.3858 | 1.4182 | 11.4705 | 8.9272 | 10.0846
38960.572 | 2358 | 0 | 38960.572 | 2160 | 0 |  | 2719.5 | 2844.5 | 143.956 | 0 | 131.8681 | 0 | 1.4396 | 0 | 1.3187 | 0 | 1.4396 | 1.3187 | 7.3104 | 17.1472 | 5.8709
38960.5724 | 2080 | 0 | 38960.5725 | 2308 | 0 |  | 2761.5 | 2886.5 | 126.9841 | 0 | 140.9035 | 0 | 1.2698 | 0 | 1.409 | 0 | 1.2698 | 1.409 | 21.6529 | 9.6352 | 20.383
38960.5729 | 2424 | 0 | 38960.5729 | 2143 | 0 |  | 2803.5 | 2928.5 | 147.9853 | 0 | 130.8303 | 0 | 1.4799 | 0 | 1.3083 | 0 | 1.4799 | 1.3083 | 4.3886 | 18.0765 | 2.9088
38960.5734 | 2418 | 0 | 38960.5734 | 1964 | 0 |  | 2845.5 | 2970.5 | 147.619 | 0 | 119.9023 | 0 | 1.4762 | 0 | 1.199 | 0 | 1.4762 | 1.199 | 4.6476 | 28.8381 | 3.1715
38960.5739 | 2223 | 0 | 38960.5739 | 2133 | 0 |  | 2887.5 | 3012.5 | 135.7143 | 0 | 130.2198 | 0 | 1.3571 | 0 | 1.3022 | 0 | 1.3571 | 1.3022 | 13.8273 | 18.6301 | 12.4701
38960.5744 | 2188 | 0 | 38960.5744 | 2152 | 0 |  | 2929.5 | 3054.5 | 133.5775 | 0 | 131.3797 | 0 | 1.3358 | 0 | 1.3138 | 0 | 1.3358 | 1.3138 | 15.6481 | 17.5827 | 14.3123
38960.5749 | 2400 | 0 | 38960.5749 | 2219 | 0 |  | 2971.5 | 3096.5 | 146.5201 | 0 | 135.4701 | 0 | 1.4652 | 0 | 1.3547 | 0 | 1.4652 | 1.3547 | 5.4325 | 14.0324 | 3.9673
38960.5754 | 2379 | 0 | 38960.5754 | 2239 | 0 |  | 3013.5 | 3138.5 | 145.2381 | 0 | 136.6911 | 0 | 1.4524 | 0 | 1.3669 | 0 | 1.4524 | 1.3669 | 6.3632 | 13.0138 | 4.9108
38960.5758 | 1913 | 0 | 38960.5759 | 2078 | 0 |  | 3055.5 | 3180.5 | 116.7888 | 0 | 126.862 | 0 | 1.1679 | 0 | 1.2686 | 0 | 1.1679 | 1.2686 | 32.2729 | 21.77 | 31.105

## B3-C5
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 153.2589 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38960.5394 | 1 | 0 | 38960.5394 | 1 | 0 |  | -96.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5398 | 1 | 0 | 38960.5399 | 1 | 0 |  | -55 | 70 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5403 | 1 | 0 | 38960.5403 | 1 | 0 |  | -12.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5408 | 1 | 0 | 38960.5408 | 1 | 0 |  | 29 | 154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5413 | 1 | 0 | 38960.5413 | 1 | 0 |  | 71.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5418 | 2 | 0 | 38960.5418 | 1 | 0 |  | 113 | 238 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125419 | 250938 | 125418.9988
38960.5423 | 1 | 0 | 38960.5423 | 1 | 0 |  | 155 | 280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5428 | 1 | 0 | 38960.5428 | 1 | 0 |  | 197 | 322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5432 | 1 | 0 | 38960.5433 | 1 | 0 |  | 239 | 364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5437 | 1 | 0 | 38960.5437 | 1 | 0 |  | 281 | 406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5442 | 1 | 0 | 38960.5442 | 1 | 0 |  | 323 | 448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5447 | 1 | 0 | 38960.5447 | 1 | 0 |  | 365 | 490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5452 | 1 | 0 | 38960.5452 | 1 | 0 |  | 407 | 532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5457 | 1 | 0 | 38960.5457 | 1 | 0 |  | 449 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5462 | 1 | 0 | 38960.5462 | 1 | 0 |  | 491 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5466 | 1 | 0 | 38960.5467 | 2 | 0 |  | 533 | 658 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250938 | 125419 | 250937.9994
38960.5471 | 1 | 0 | 38960.5472 | 1 | 0 |  | 575 | 700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5476 | 1 | 0 | 38960.5476 | 1 | 0 |  | 617 | 742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5481 | 1 | 0 | 38960.5481 | 1 | 0 |  | 659 | 784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5486 | 1 | 0 | 38960.5486 | 1 | 0 |  | 701 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5491 | 1 | 0 | 38960.5491 | 1 | 0 |  | 743 | 868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5496 | 1 | 0 | 38960.5496 | 1 | 0 |  | 785 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.55 | 1 | 0 | 38960.5501 | 1 | 0 |  | 827 | 952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5505 | 1 | 0 | 38960.5506 | 1 | 0 |  | 869 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.551 | 1 | 0 | 38960.551 | 1 | 0 |  | 911 | 1036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5515 | 1 | 0 | 38960.5515 | 1 | 0 |  | 953 | 1078 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.552 | 1 | 0 | 38960.552 | 1 | 0 |  | 995 | 1120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5525 | 1 | 0 | 38960.5525 | 1 | 0 |  | 1037 | 1162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.553 | 1 | 0 | 38960.553 | 1 | 0 |  | 1079 | 1204 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5534 | 1 | 0 | 38960.5535 | 2 | 0 |  | 1121 | 1246 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250938 | 125419 | 250937.9994
38960.5539 | 1 | 0 | 38960.554 | 1 | 0 |  | 1163 | 1288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5544 | 1 | 0 | 38960.5544 | 1 | 0 |  | 1205 | 1330 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5549 | 1 | 0 | 38960.5549 | 1 | 0 |  | 1247 | 1372 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5554 | 1 | 0 | 38960.5554 | 1 | 0 |  | 1289 | 1414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5559 | 2 | 0 | 38960.5559 | 1 | 0 |  | 1331 | 1456 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125419 | 250938 | 125418.9988
38960.5564 | 1 | 0 | 38960.5564 | 1 | 0 |  | 1373 | 1498 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5569 | 1 | 0 | 38960.5569 | 1 | 0 |  | 1415 | 1540 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5573 | 1 | 0 | 38960.5574 | 1 | 0 |  | 1457 | 1582 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5578 | 1 | 0 | 38960.5578 | 1 | 0 |  | 1499 | 1624 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5583 | 1 | 0 | 38960.5583 | 1 | 0 |  | 1541 | 1666 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5588 | 1 | 0 | 38960.5588 | 1 | 0 |  | 1583 | 1708 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5593 | 1 | 0 | 38960.5593 | 1 | 0 |  | 1625 | 1750 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250938 | 250938 | 250937.9994
38960.5598 | 1907 | 1 | 38960.5598 | 1 | 0 |  | 1667 | 1792 | 116.4225 | 0.06105 | 0.06105 | 0 | 1.1642 | 0.0006105 | 0.0006105 | 0 | 1.1636 | 0.0006105 | 31.6569 | 250938 | 60214.0044
38960.5603 | 1966 | 1 | 38960.5603 | 2 | 0 |  | 1709 | 1834 | 120.0244 | 0.06105 | 0.1221 | 0 | 1.2002 | 0.0006105 | 0.001221 | 0 | 1.1996 | 0.001221 | 27.7038 | 125419 | 54294.7093
38960.5607 | 2353 | 0 | 38960.5608 | 1703 | 0 |  | 1751 | 1876 | 143.6508 | 0 | 103.9683 | 0 | 1.4365 | 0 | 1.0397 | 0 | 1.4365 | 1.0397 | 6.6885 | 47.4093 | 5.252
38960.5612 | 2173 | 0 | 38960.5612 | 2282 | 0 |  | 1793 | 1918 | 132.6618 | 0 | 139.3162 | 0 | 1.3266 | 0 | 1.3932 | 0 | 1.3266 | 1.3932 | 15.526 | 10.0079 | 14.1994
38960.5617 | 2005 | 0 | 38960.5617 | 1783 | 0 |  | 1835 | 1960 | 122.4054 | 0 | 108.8523 | 0 | 1.2241 | 0 | 1.0885 | 0 | 1.2241 | 1.0885 | 25.206 | 40.7953 | 23.9819
38960.5622 | 2104 | 0 | 38960.5622 | 2094 | 0 |  | 1877 | 2002 | 128.4493 | 0 | 127.8388 | 0 | 1.2845 | 0 | 1.2784 | 0 | 1.2845 | 1.2784 | 19.3146 | 19.8844 | 18.0301
38960.5627 | 2494 | 0 | 38960.5627 | 2134 | 0 |  | 1919 | 2044 | 152.2589 | 0 | 130.2808 | 0 | 1.5226 | 0 | 1.3028 | 0 | 1.5226 | 1.3028 | 0.65678 | 17.6373 | 0.86581
38960.5632 | 1898 | 0 | 38960.5632 | 2210 | 0 |  | 1961 | 2086 | 115.873 | 0 | 134.9206 | 0 | 1.1587 | 0 | 1.3492 | 0 | 1.1587 | 1.3492 | 32.2645 | 13.5919 | 31.1058
38960.5637 | 1887 | 0 | 38960.5637 | 2101 | 0 |  | 2003 | 2128 | 115.2015 | 0 | 128.2662 | 0 | 1.152 | 0 | 1.2827 | 0 | 1.152 | 1.2827 | 33.0355 | 19.485 | 31.8835
38960.5641 | 2098 | 0 | 38960.5642 | 1958 | 0 |  | 2045 | 2170 | 128.083 | 0 | 119.536 | 0 | 1.2808 | 0 | 1.1954 | 0 | 1.2808 | 1.1954 | 19.6559 | 28.2114 | 18.375
38960.5646 | 2195 | 0 | 38960.5647 | 2242 | 0 |  | 2087 | 2212 | 134.0049 | 0 | 136.8742 | 0 | 1.34 | 0 | 1.3687 | 0 | 1.34 | 1.3687 | 14.3681 | 11.9706 | 13.0281
38960.5651 | 2335 | 0 | 38960.5651 | 2183 | 0 |  | 2129 | 2254 | 142.5519 | 0 | 133.2723 | 0 | 1.4255 | 0 | 1.3327 | 0 | 1.4255 | 1.3327 | 7.5109 | 14.9968 | 6.0854
38960.5656 | 2116 | 0 | 38960.5656 | 2210 | 0 |  | 2171 | 2296 | 129.1819 | 0 | 134.9206 | 0 | 1.2918 | 0 | 1.3492 | 0 | 1.2918 | 1.3492 | 18.638 | 13.5919 | 17.3462
38960.5661 | 2398 | 0 | 38960.5661 | 2038 | 0 |  | 2212.5 | 2337.5 | 146.398 | 0 | 124.42 | 0 | 1.464 | 0 | 1.2442 | 0 | 1.464 | 1.2442 | 4.6864 | 23.1786 | 3.2224
38960.5666 | 2305 | 1 | 38960.5666 | 2014 | 0 |  | 2255 | 2380 | 140.7204 | 0.06105 | 122.9548 | 0 | 1.4072 | 0.0006105 | 1.2295 | 0 | 1.4066 | 1.2295 | 8.9298 | 24.6465 | 4041.2266
38960.5671 | 2142 | 0 | 38960.5671 | 2140 | 0 |  | 2296.5 | 2421.5 | 130.7692 | 0 | 130.6471 | 0 | 1.3077 | 0 | 1.3065 | 0 | 1.3077 | 1.3065 | 17.1979 | 17.3075 | 15.8903
38960.5675 | 2468 | 0 | 38960.5676 | 2237 | 0 |  | 2338.5 | 2463.5 | 150.6716 | 0 | 136.569 | 0 | 1.5067 | 0 | 1.3657 | 0 | 1.5067 | 1.3657 | 1.7172 | 12.2208 | 0.21046
38960.568 | 1988 | 0 | 38960.5681 | 2097 | 0 |  | 2381 | 2506 | 121.3675 | 0 | 128.022 | 0 | 1.2137 | 0 | 1.2802 | 0 | 1.2137 | 1.2802 | 26.2767 | 19.7129 | 25.063
38960.5685 | 1988 | 0 | 38960.5685 | 1926 | 0 |  | 2423 | 2548 | 121.3675 | 0 | 117.5824 | 0 | 1.2137 | 0 | 1.1758 | 0 | 1.2137 | 1.1758 | 26.2767 | 30.3416 | 25.063
38960.569 | 2143 | 0 | 38960.569 | 1949 | 0 |  | 2465 | 2590 | 130.8303 | 0 | 118.9866 | 0 | 1.3083 | 0 | 1.1899 | 0 | 1.3083 | 1.1899 | 17.1433 | 28.8035 | 15.835
38960.5695 | 1926 | 0 | 38960.5695 | 1959 | 0 |  | 2506.5 | 2631.5 | 117.5824 | 0 | 119.5971 | 0 | 1.1758 | 0 | 1.196 | 0 | 1.1758 | 1.196 | 30.3416 | 28.146 | 29.1658
38960.57 | 2150 | 0 | 38960.57 | 1898 | 0 |  | 2548.5 | 2673.5 | 131.2576 | 0 | 115.873 | 0 | 1.3126 | 0 | 1.1587 | 0 | 1.3126 | 1.1587 | 16.7619 | 32.2645 | 15.4493
38960.5705 | 2353 | 0 | 38960.5705 | 2332 | 0 |  | 2590.5 | 2715.5 | 143.6508 | 0 | 142.3687 | 0 | 1.4365 | 0 | 1.4237 | 0 | 1.4365 | 1.4237 | 6.6885 | 7.6492 | 5.252
38960.5709 | 2323 | 0 | 38960.571 | 2398 | 0 |  | 2633 | 2758 | 141.8193 | 0 | 146.398 | 0 | 1.4182 | 0 | 1.464 | 0 | 1.4182 | 1.464 | 8.0663 | 4.6864 | 6.6481
38960.5714 | 2269 | 0 | 38960.5714 | 1903 | 0 |  | 2674.5 | 2799.5 | 138.5226 | 0 | 116.1783 | 0 | 1.3852 | 0 | 1.1618 | 0 | 1.3852 | 1.1618 | 10.6382 | 31.917 | 9.2529
38960.5719 | 2085 | 0 | 38960.5719 | 2157 | 0 |  | 2717 | 2842 | 127.2894 | 0 | 131.685 | 0 | 1.2729 | 0 | 1.3168 | 0 | 1.2729 | 1.3168 | 20.4019 | 16.3829 | 19.129
38960.5724 | 2428 | 0 | 38960.5724 | 1974 | 0 |  | 2759 | 2884 | 148.2295 | 0 | 120.5128 | 0 | 1.4823 | 0 | 1.2051 | 0 | 1.4823 | 1.2051 | 3.3929 | 27.1722 | 1.9106
38960.5729 | 1979 | 0 | 38960.5729 | 2330 | 0 |  | 2800.5 | 2925.5 | 120.8181 | 0 | 142.2466 | 0 | 1.2082 | 0 | 1.4225 | 0 | 1.2082 | 1.4225 | 26.8509 | 7.7416 | 25.6428
38960.5734 | 2450 | 0 | 38960.5734 | 2171 | 0 |  | 2842.5 | 2967.5 | 149.5726 | 0 | 132.5397 | 0 | 1.4957 | 0 | 1.3254 | 0 | 1.4957 | 1.3254 | 2.4645 | 15.6324 | 0.96876
38960.5739 | 1838 | 0 | 38960.5739 | 1991 | 0 |  | 2884.5 | 3009.5 | 112.21 | 0 | 121.5507 | 0 | 1.1221 | 0 | 1.2155 | 0 | 1.1221 | 1.2155 | 36.5822 | 26.0864 | 35.4601
38960.5744 | 2004 | 0 | 38960.5744 | 1904 | 0 |  | 2926.5 | 3051.5 | 122.3443 | 0 | 116.2393 | 0 | 1.2234 | 0 | 1.1624 | 0 | 1.2234 | 1.1624 | 25.2685 | 31.8477 | 24.045
38960.5748 | 2425 | 0 | 38960.5748 | 2382 | 0 |  | 2968.5 | 3093.5 | 148.0464 | 0 | 145.4212 | 0 | 1.4805 | 0 | 1.4542 | 0 | 1.4805 | 1.4542 | 3.5208 | 5.3896 | 2.0404
38960.5753 | 1932 | 0 | 38960.5753 | 2076 | 0 |  | 3010.5 | 3135.5 | 117.9487 | 0 | 126.7399 | 0 | 1.1795 | 0 | 1.2674 | 0 | 1.1795 | 1.2674 | 29.9369 | 20.9239 | 28.7574
38960.5758 | 2301 | 0 | 38960.5758 | 1989 | 0 |  | 3052.5 | 3177.5 | 140.4762 | 0 | 121.4286 | 0 | 1.4048 | 0 | 1.2143 | 0 | 1.4048 | 1.2143 | 9.0995 | 26.2132 | 7.6948

## B3-B4
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 154.1746 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38960.5393 | 1 | 1 | 38960.5393 | 1 | 0 |  | -99.5 | 25.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 637249438.44 | 252438 | 252238.0792
38960.5398 | 1 | 0 | 38960.5398 | 1 | 0 |  | -57.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5403 | 1 | 0 | 38960.5403 | 1 | 0 |  | -15.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5408 | 1 | 0 | 38960.5408 | 1 | 0 |  | 26.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5413 | 1 | 0 | 38960.5413 | 1 | 0 |  | 68.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5418 | 1 | 0 | 38960.5418 | 1 | 0 |  | 110.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5422 | 1 | 0 | 38960.5423 | 1 | 0 |  | 152.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5427 | 1 | 0 | 38960.5427 | 1 | 0 |  | 194.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5432 | 2 | 0 | 38960.5432 | 1 | 0 |  | 236.5 | 361.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126169 | 252438 | 126168.9988
38960.5437 | 1 | 0 | 38960.5437 | 1 | 0 |  | 278.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5442 | 1 | 0 | 38960.5442 | 2 | 0 |  | 320.5 | 445.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252438 | 126169 | 252437.9994
38960.5447 | 1 | 0 | 38960.5447 | 1 | 0 |  | 362.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5452 | 1 | 0 | 38960.5452 | 1 | 0 |  | 404.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5456 | 1 | 0 | 38960.5457 | 1 | 0 |  | 446.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5461 | 1 | 0 | 38960.5461 | 1 | 0 |  | 488.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5466 | 1 | 0 | 38960.5466 | 2 | 0 |  | 530.5 | 655.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252438 | 126169 | 252437.9994
38960.5471 | 1 | 0 | 38960.5471 | 1 | 0 |  | 572.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5476 | 1 | 0 | 38960.5476 | 2 | 0 |  | 614.5 | 739.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 252438 | 126169 | 252437.9994
38960.5481 | 1 | 0 | 38960.5481 | 1 | 0 |  | 656.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5486 | 1 | 0 | 38960.5486 | 1 | 0 |  | 698.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5491 | 1 | 0 | 38960.5491 | 1 | 0 |  | 740.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5495 | 1 | 0 | 38960.5495 | 1 | 0 |  | 782.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.55 | 1 | 0 | 38960.55 | 1 | 0 |  | 824 | 949 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5505 | 1 | 0 | 38960.5505 | 1 | 0 |  | 866.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.551 | 1 | 0 | 38960.551 | 1 | 0 |  | 908.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5515 | 1 | 0 | 38960.5515 | 1 | 0 |  | 950.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.552 | 1 | 0 | 38960.552 | 1 | 0 |  | 992.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5525 | 1 | 0 | 38960.5525 | 1 | 0 |  | 1034.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5529 | 1 | 0 | 38960.553 | 1 | 0 |  | 1076.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5534 | 1 | 0 | 38960.5534 | 1 | 0 |  | 1118 | 1243 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5539 | 1 | 0 | 38960.5539 | 1 | 0 |  | 1160.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5544 | 1 | 0 | 38960.5544 | 1 | 0 |  | 1202 | 1327 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5549 | 1 | 0 | 38960.5549 | 1 | 0 |  | 1244.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5554 | 1 | 0 | 38960.5554 | 1 | 0 |  | 1286 | 1411 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5559 | 1 | 0 | 38960.5559 | 1 | 0 |  | 1328.5 | 1453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5563 | 1 | 0 | 38960.5564 | 1 | 0 |  | 1370.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5568 | 1 | 0 | 38960.5568 | 1 | 0 |  | 1412.5 | 1537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5573 | 1 | 0 | 38960.5573 | 1 | 0 |  | 1454 | 1579 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5578 | 1 | 0 | 38960.5578 | 1 | 0 |  | 1496.5 | 1621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5583 | 1 | 0 | 38960.5583 | 1 | 0 |  | 1538 | 1663 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5588 | 1 | 0 | 38960.5588 | 1 | 0 |  | 1580.5 | 1705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5593 | 1 | 0 | 38960.5593 | 1 | 0 |  | 1622.5 | 1747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38960.5597 | 648 | 0 | 38960.5598 | 208 | 0 |  | 1664 | 1789 | 39.5604 | 0 | 12.6984 | 0 | 0.3956 | 0 | 0.12698 | 0 | 0.3956 | 0.12698 | 289.7191 | 1114.125 | 289.3235
38960.5602 | 1756 | 0 | 38960.5602 | 1534 | 0 |  | 1706 | 1831 | 107.2039 | 0 | 93.6508 | 0 | 1.072 | 0 | 0.93651 | 0 | 1.072 | 0.93651 | 43.8144 | 64.6271 | 42.7423
38960.5607 | 2161 | 101 | 38960.5607 | 2091 | 79 |  | 1748 | 1873 | 131.9292 | 6.1661 | 127.6557 | 4.823 | 1.3193 | 0.061661 | 1.2766 | 0.04823 | 1.2576 | 1.2283 | 21.7319 | 26.3503 | 54.384
38960.5612 | 2319 | 1 | 38960.5612 | 2150 | 0 |  | 1790 | 1915 | 141.5751 | 0.06105 | 131.2576 | 0 | 1.4158 | 0.0006105 | 1.3126 | 0 | 1.4151 | 1.3126 | 8.9254 | 17.4595 | 3052.8295
38960.5617 | 2047 | 0 | 38960.5617 | 2149 | 0 |  | 1832 | 1957 | 124.9695 | 0 | 131.1966 | 0 | 1.2497 | 0 | 1.312 | 0 | 1.2497 | 1.312 | 23.3698 | 17.5142 | 22.1201
38960.5622 | 2329 | 0 | 38960.5622 | 2213 | 0 |  | 1874 | 1999 | 142.1856 | 0 | 135.1038 | 0 | 1.4219 | 0 | 1.351 | 0 | 1.4219 | 1.351 | 8.4319 | 14.1157 | 7.0101
38960.5627 | 2493 | 0 | 38960.5627 | 2269 | 0 |  | 1916 | 2041 | 152.1978 | 0 | 138.5226 | 0 | 1.522 | 0 | 1.3852 | 0 | 1.522 | 1.3852 | 1.2988 | 11.2993 | 0.22314
38960.5631 | 1878 | 88 | 38960.5632 | 2143 | 90 |  | 1958 | 2083 | 114.652 | 5.3724 | 130.8303 | 5.4945 | 1.1465 | 0.053724 | 1.3083 | 0.054945 | 1.0928 | 1.2534 | 47.5639 | 20.5164 | 108.2128
38960.5636 | 1874 | 56 | 38960.5636 | 1922 | 48 |  | 2000 | 2125 | 114.4078 | 3.4188 | 117.3382 | 2.9304 | 1.1441 | 0.034188 | 1.1734 | 0.029304 | 1.1099 | 1.1441 | 39.3489 | 34.4392 | 272.3538
38960.5641 | 2068 | 4 | 38960.5641 | 1980 | 1 |  | 2042 | 2167 | 126.2515 | 0.2442 | 120.8791 | 0.06105 | 1.2625 | 0.002442 | 1.2088 | 0.0006105 | 1.2601 | 1.2082 | 22.3165 | 27.6209 | 2453.118
38960.5646 | 2044 | 1 | 38960.5646 | 2428 | 0 |  | 2084 | 2209 | 124.7863 | 0.06105 | 148.2295 | 0 | 1.2479 | 0.0006105 | 1.4823 | 0 | 1.2473 | 1.4823 | 23.8535 | 4.0107 | 1852.3709
38960.5651 | 1940 | 1 | 38960.5651 | 2305 | 1 |  | 2126 | 2251 | 118.4371 | 0.06105 | 140.7204 | 0.06105 | 1.1844 | 0.0006105 | 1.4072 | 0.0006105 | 1.1838 | 1.4066 | 30.3532 | 9.5788 | 5108.3419
38960.5656 | 2432 | 1 | 38960.5656 | 2386 | 0 |  | 2168 | 2293 | 148.4737 | 0.06105 | 145.6654 | 0 | 1.4847 | 0.0006105 | 1.4567 | 0 | 1.4841 | 1.4567 | 3.8685 | 5.8416 | 509.8609
38960.5661 | 2205 | 1 | 38960.5661 | 2105 | 0 |  | 2210 | 2335 | 134.6154 | 0.06105 | 128.5104 | 0 | 1.3462 | 0.0006105 | 1.2851 | 0 | 1.3455 | 1.2851 | 14.5694 | 19.9705 | 5316.4658
38960.5665 | 2306 | 0 | 38960.5666 | 2345 | 0 |  | 2252 | 2377 | 140.7814 | 0 | 143.1624 | 0 | 1.4078 | 0 | 1.4316 | 0 | 1.4078 | 1.4316 | 9.5134 | 7.6921 | 8.1056
38960.567 | 1970 | 0 | 38960.567 | 2282 | 0 |  | 2294 | 2419 | 120.2686 | 0 | 139.3162 | 0 | 1.2027 | 0 | 1.3932 | 0 | 1.2027 | 1.3932 | 28.1919 | 10.6652 | 26.9892
38960.5675 | 2179 | 0 | 38960.5675 | 2180 | 0 |  | 2336 | 2461 | 133.0281 | 0 | 133.0891 | 0 | 1.3303 | 0 | 1.3309 | 0 | 1.3303 | 1.3309 | 15.8963 | 15.8431 | 14.566
38960.568 | 1962 | 0 | 38960.568 | 2509 | 0 |  | 2378 | 2503 | 119.7802 | 0 | 153.1746 | 0 | 1.1978 | 0 | 1.5317 | 0 | 1.1978 | 1.5317 | 28.7146 | 0.65285 | 27.5168
38960.5685 | 2076 | 0 | 38960.5685 | 2228 | 0 |  | 2420 | 2545 | 126.7399 | 0 | 136.0195 | 0 | 1.2674 | 0 | 1.3602 | 0 | 1.2674 | 1.3602 | 21.6464 | 13.3474 | 20.379
38960.569 | 2451 | 0 | 38960.569 | 2477 | 0 |  | 2462 | 2587 | 149.6337 | 0 | 151.221 | 0 | 1.4963 | 0 | 1.5122 | 0 | 1.4963 | 1.5122 | 3.0347 | 1.9532 | 1.5383
38960.5695 | 2414 | 0 | 38960.5695 | 2415 | 0 |  | 2504 | 2629 | 147.3748 | 0 | 147.4359 | 0 | 1.4737 | 0 | 1.4744 | 0 | 1.4737 | 1.4744 | 4.6139 | 4.5706 | 3.1402
38960.5699 | 2468 | 0 | 38960.57 | 2104 | 0 |  | 2546 | 2671 | 150.6716 | 0 | 128.4493 | 0 | 1.5067 | 0 | 1.2845 | 0 | 1.5067 | 1.2845 | 2.325 | 20.0276 | 0.81824
38960.5704 | 2070 | 0 | 38960.5705 | 1961 | 0 |  | 2588 | 2713 | 126.3736 | 0 | 119.7192 | 0 | 1.2637 | 0 | 1.1972 | 0 | 1.2637 | 1.1972 | 21.999 | 28.7802 | 20.7353
38960.5709 | 2358 | 0 | 38960.5709 | 2178 | 0 |  | 2630 | 2755 | 143.956 | 0 | 132.967 | 0 | 1.4396 | 0 | 1.3297 | 0 | 1.4396 | 1.3297 | 7.0984 | 15.9495 | 5.6588
38960.5714 | 2211 | 0 | 38960.5714 | 2107 | 0 |  | 2672 | 2797 | 134.9817 | 0 | 128.6325 | 0 | 1.3498 | 0 | 1.2863 | 0 | 1.3498 | 1.2863 | 14.2189 | 19.8567 | 12.8691
38960.5719 | 2071 | 0 | 38960.5719 | 2495 | 0 |  | 2714 | 2839 | 126.4347 | 0 | 152.3199 | 0 | 1.2643 | 0 | 1.5232 | 0 | 1.2643 | 1.5232 | 21.9401 | 1.2176 | 20.6758
38960.5724 | 2461 | 0 | 38960.5724 | 1990 | 0 |  | 2756 | 2881 | 150.2442 | 0 | 121.4896 | 0 | 1.5024 | 0 | 1.2149 | 0 | 1.5024 | 1.2149 | 2.616 | 26.9035 | 1.1136
38960.5729 | 1962 | 0 | 38960.5729 | 2231 | 0 |  | 2798 | 2923 | 119.7802 | 0 | 136.2027 | 0 | 1.1978 | 0 | 1.362 | 0 | 1.1978 | 1.362 | 28.7146 | 13.195 | 27.5168
38960.5733 | 2399 | 0 | 38960.5734 | 1943 | 0 |  | 2840 | 2965 | 146.4591 | 0 | 118.6203 | 0 | 1.4646 | 0 | 1.1862 | 0 | 1.4646 | 1.1862 | 5.268 | 29.9732 | 3.8034
38960.5738 | 1839 | 32 | 38960.5739 | 2370 | 31 |  | 2882 | 3007 | 112.2711 | 1.9536 | 144.6886 | 1.8926 | 1.1227 | 0.019536 | 1.4469 | 0.018926 | 1.1032 | 1.428 | 51.3092 | 6.8192 | 130.5453
38960.5743 | 2126 | 0 | 38960.5743 | 2074 | 0 |  | 2924 | 3049 | 129.7924 | 0 | 126.6178 | 0 | 1.2979 | 0 | 1.2662 | 0 | 1.2979 | 1.2662 | 18.7855 | 21.7637 | 17.4876
38960.5748 | 1932 | 0 | 38960.5748 | 2185 | 0 |  | 2966 | 3091 | 117.9487 | 0 | 133.3944 | 0 | 1.1795 | 0 | 1.3339 | 0 | 1.1795 | 1.3339 | 30.7133 | 15.578 | 29.5338
38960.5753 | 2396 | 0 | 38960.5753 | 2306 | 1 |  | 3008 | 3133 | 146.2759 | 0 | 140.7814 | 0.06105 | 1.4628 | 0 | 1.4078 | 0.0006105 | 1.4628 | 1.4072 | 5.3998 | 9.561 | 3.9371
38960.5758 | 1990 | 0 | 38960.5758 | 2082 | 0 |  | 3050 | 3175 | 121.4896 | 0 | 127.1062 | 0 | 1.2149 | 0 | 1.2711 | 0 | 1.2149 | 1.2711 | 26.9035 | 21.2959 | 25.6886

## A2-C6
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 149.7179 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38960.5393 | 1 | 1 | 38960.5393 | 1 | 0 |  | -102.5 | 22.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600926390.44 | 245138 | 244938.0816
38960.5398 | 1 | 1 | 38960.5398 | 1 | 0 |  | -60.5 | 64.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600926390.44 | 245138 | 244938.0816
38960.5403 | 2 | 0 | 38960.5403 | 1 | 0 |  | -18.5 | 106.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122519 | 245138 | 122518.9988
38960.5408 | 1 | 0 | 38960.5408 | 1 | 0 |  | 23.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5412 | 1 | 0 | 38960.5413 | 1 | 0 |  | 65.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5417 | 1 | 0 | 38960.5417 | 1 | 0 |  | 107.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5422 | 1 | 0 | 38960.5422 | 1 | 0 |  | 149.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5427 | 1 | 0 | 38960.5427 | 1 | 0 |  | 191.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5432 | 1 | 0 | 38960.5432 | 1 | 0 |  | 233.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5437 | 1 | 0 | 38960.5437 | 1 | 0 |  | 275.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5442 | 1 | 0 | 38960.5442 | 1 | 0 |  | 317.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5446 | 1 | 0 | 38960.5447 | 1 | 0 |  | 359.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5451 | 1 | 0 | 38960.5451 | 1 | 0 |  | 401.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5456 | 1 | 0 | 38960.5456 | 1 | 0 |  | 443.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5461 | 1 | 0 | 38960.5461 | 1 | 0 |  | 485.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5466 | 1 | 0 | 38960.5466 | 1 | 0 |  | 527.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5471 | 1 | 0 | 38960.5471 | 1 | 0 |  | 569.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5476 | 1 | 0 | 38960.5476 | 1 | 0 |  | 611.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.548 | 1 | 0 | 38960.5481 | 1 | 0 |  | 653.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5485 | 1 | 0 | 38960.5485 | 1 | 0 |  | 695.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.549 | 1 | 0 | 38960.549 | 1 | 0 |  | 737.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5495 | 1 | 0 | 38960.5495 | 1 | 0 |  | 779.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.55 | 1 | 0 | 38960.55 | 1 | 0 |  | 821.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5505 | 1 | 0 | 38960.5505 | 1 | 0 |  | 863.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.551 | 1 | 0 | 38960.551 | 1 | 0 |  | 905.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5514 | 1 | 1 | 38960.5515 | 1 | 0 |  | 947.5 | 1072.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600926390.44 | 245138 | 244938.0816
38960.5519 | 1 | 0 | 38960.5519 | 1 | 0 |  | 989.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5524 | 1 | 0 | 38960.5524 | 1 | 0 |  | 1031.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5529 | 1 | 0 | 38960.5529 | 1 | 0 |  | 1073.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5534 | 1 | 0 | 38960.5534 | 1 | 0 |  | 1115.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5539 | 1 | 0 | 38960.5539 | 1 | 0 |  | 1157.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5544 | 1 | 0 | 38960.5544 | 1 | 0 |  | 1199.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5548 | 1 | 0 | 38960.5549 | 1 | 0 |  | 1241.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5553 | 1 | 0 | 38960.5553 | 1 | 0 |  | 1283.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5558 | 1 | 0 | 38960.5558 | 1 | 0 |  | 1325.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5563 | 1 | 0 | 38960.5563 | 1 | 0 |  | 1367.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5568 | 1 | 0 | 38960.5568 | 1 | 0 |  | 1409.5 | 1534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5573 | 1 | 0 | 38960.5573 | 1 | 0 |  | 1451.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5578 | 1 | 0 | 38960.5578 | 1 | 0 |  | 1493.5 | 1618.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5583 | 1 | 0 | 38960.5583 | 1 | 0 |  | 1535.5 | 1660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5587 | 1 | 0 | 38960.5587 | 1 | 0 |  | 1577.5 | 1702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5592 | 1 | 0 | 38960.5592 | 1 | 0 |  | 1619.5 | 1744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5597 | 1 | 0 | 38960.5597 | 1 | 0 |  | 1661.5 | 1786.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5602 | 1 | 0 | 38960.5602 | 1 | 0 |  | 1703.5 | 1828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
38960.5607 | 2 | 0 | 38960.5607 | 1 | 0 |  | 1745.5 | 1870.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122519 | 245138 | 122518.9988
38960.5612 | 2 | 0 | 38960.5612 | 2 | 0 |  | 1787.5 | 1912.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122519 | 122519 | 122518.9988
38960.5617 | 2 | 1 | 38960.5617 | 2013 | 0 |  | 1829.5 | 1954.5 | 0.1221 | 0.06105 | 122.8938 | 0 | 0.001221 | 0.0006105 | 1.2289 | 0 | 0.0006105 | 1.2289 | 68418.5486 | 38.7378 | 68390.627
38960.5621 | 2 | 0 | 38960.5622 | 2245 | 0 |  | 1871.5 | 1996.5 | 0.1221 | 0 | 137.0574 | 0 | 0.001221 | 0 | 1.3706 | 0 | 0.001221 | 1.3706 | 122519 | 9.2374 | 122518.9988
38960.5626 | 2 | 0 | 38960.5626 | 2238 | 0 |  | 1913.5 | 2038.5 | 0.1221 | 0 | 136.63 | 0 | 0.001221 | 0 | 1.3663 | 0 | 0.001221 | 1.3663 | 122519 | 9.5791 | 122518.9988
38960.5631 | 2 | 0 | 38960.5631 | 2339 | 0 |  | 1955.5 | 2080.5 | 0.1221 | 0 | 142.7961 | 0 | 0.001221 | 0 | 1.428 | 0 | 0.001221 | 1.428 | 122519 | 4.8474 | 122518.9988
38960.5636 | 2 | 0 | 38960.5636 | 2365 | 0 |  | 1997.5 | 2122.5 | 0.1221 | 0 | 144.3834 | 0 | 0.001221 | 0 | 1.4438 | 0 | 0.001221 | 1.4438 | 122519 | 3.6947 | 122518.9988
38960.5641 | 2 | 0 | 38960.5641 | 2004 | 0 |  | 2039.5 | 2164.5 | 0.1221 | 0 | 122.3443 | 0 | 0.001221 | 0 | 1.2234 | 0 | 0.001221 | 1.2234 | 122519 | 22.3743 | 122518.9988
38960.5646 | 2 | 0 | 38960.5646 | 2436 | 0 |  | 2081.5 | 2206.5 | 0.1221 | 0 | 148.7179 | 0 | 0.001221 | 0 | 1.4872 | 0 | 0.001221 | 1.4872 | 122519 | 0.67241 | 122518.9988
38960.5651 | 2 | 0 | 38960.5651 | 2426 | 0 |  | 2123.5 | 2248.5 | 0.1221 | 0 | 148.1074 | 0 | 0.001221 | 0 | 1.4811 | 0 | 0.001221 | 1.4811 | 122519 | 1.0874 | 122518.9988
38960.5655 | 1 | 0 | 38960.5656 | 2206 | 0 |  | 2165.5 | 2290.5 | 0.06105 | 0 | 134.6764 | 0 | 0.0006105 | 0 | 1.3468 | 0 | 0.0006105 | 1.3468 | 245138 | 11.1686 | 245137.9994
38960.566 | 2 | 0 | 38960.566 | 2084 | 0 |  | 2207 | 2332 | 0.1221 | 0 | 127.2283 | 0 | 0.001221 | 0 | 1.2723 | 0 | 0.001221 | 1.2723 | 122519 | 17.6766 | 122518.9988
38960.5665 | 2 | 0 | 38960.5665 | 2330 | 0 |  | 2249.5 | 2374.5 | 0.1221 | 0 | 142.2466 | 0 | 0.001221 | 0 | 1.4225 | 0 | 0.001221 | 1.4225 | 122519 | 5.2524 | 122518.9988
38960.567 | 2 | 0 | 38960.567 | 2087 | 0 |  | 2291 | 2416 | 0.1221 | 0 | 127.4115 | 0 | 0.001221 | 0 | 1.2741 | 0 | 0.001221 | 1.2741 | 122519 | 17.5074 | 122518.9988
38960.5675 | 2 | 0 | 38960.5675 | 2309 | 0 |  | 2333 | 2458 | 0.1221 | 0 | 140.9646 | 0 | 0.001221 | 0 | 1.4096 | 0 | 0.001221 | 1.4096 | 122519 | 6.2096 | 122518.9988
38960.568 | 3 | 0 | 38960.568 | 2316 | 0 |  | 2375 | 2500 | 0.18315 | 0 | 141.3919 | 0 | 0.0018315 | 0 | 1.4139 | 0 | 0.0018315 | 1.4139 | 81646 | 5.8886 | 81645.9982
38960.5685 | 3 | 0 | 38960.5685 | 1957 | 0 |  | 2417.5 | 2542.5 | 0.18315 | 0 | 119.475 | 0 | 0.0018315 | 0 | 1.1947 | 0 | 0.0018315 | 1.1947 | 81646 | 25.3132 | 81645.9982
38960.5689 | 4 | 0 | 38960.569 | 1953 | 0 |  | 2459.5 | 2584.5 | 0.2442 | 0 | 119.2308 | 0 | 0.002442 | 0 | 1.1923 | 0 | 0.002442 | 1.1923 | 61209.5 | 25.5699 | 61209.4976
38960.5694 | 6 | 0 | 38960.5694 | 2285 | 0 |  | 2501.5 | 2626.5 | 0.3663 | 0 | 139.4994 | 0 | 0.003663 | 0 | 1.395 | 0 | 0.003663 | 1.395 | 40773 | 7.3252 | 40772.9963
38960.5699 | 8 | 0 | 38960.5699 | 2432 | 0 |  | 2543.5 | 2668.5 | 0.4884 | 0 | 148.4737 | 0 | 0.004884 | 0 | 1.4847 | 0 | 0.004884 | 1.4847 | 30554.75 | 0.83799 | 30554.7451
38960.5704 | 15 | 0 | 38960.5704 | 2414 | 0 |  | 2585 | 2710 | 0.91575 | 0 | 147.3748 | 0 | 0.0091575 | 0 | 1.4737 | 0 | 0.0091575 | 1.4737 | 16249.2 | 1.5899 | 16249.1908
38960.5709 | 22 | 0 | 38960.5709 | 2247 | 0 |  | 2627 | 2752 | 1.3431 | 0 | 137.1795 | 0 | 0.013431 | 0 | 1.3718 | 0 | 0.013431 | 1.3718 | 11047.1818 | 9.1402 | 11047.1684
38960.5714 | 29 | 0 | 38960.5714 | 1892 | 0 |  | 2669 | 2794 | 1.7705 | 0 | 115.5067 | 0 | 0.017705 | 0 | 1.1551 | 0 | 0.017705 | 1.1551 | 8356.4828 | 29.6184 | 8356.4651
38960.5719 | 40 | 0 | 38960.5719 | 2157 | 0 |  | 2711 | 2836 | 2.442 | 0 | 131.685 | 0 | 0.02442 | 0 | 1.3168 | 0 | 0.02442 | 1.3168 | 6030.95 | 13.694 | 6030.9256
38960.5723 | 47 | 0 | 38960.5724 | 2114 | 0 |  | 2753.5 | 2878.5 | 2.8694 | 0 | 129.0598 | 0 | 0.028694 | 0 | 1.2906 | 0 | 0.028694 | 1.2906 | 5117.8298 | 16.0066 | 5117.8011
38960.5728 | 42 | 0 | 38960.5728 | 2277 | 0 |  | 2795 | 2920 | 2.5641 | 0 | 139.011 | 0 | 0.025641 | 0 | 1.3901 | 0 | 0.025641 | 1.3901 | 5739 | 7.7022 | 5738.9744
38960.5733 | 46 | 0 | 38960.5733 | 2402 | 0 |  | 2837 | 2962 | 2.8083 | 0 | 146.6422 | 0 | 0.028083 | 0 | 1.4664 | 0 | 0.028083 | 1.4664 | 5231.2609 | 2.0974 | 5231.2328
38960.5738 | 39 | 0 | 38960.5738 | 2430 | 0 |  | 2879 | 3004 | 2.381 | 0 | 148.3516 | 0 | 0.02381 | 0 | 1.4835 | 0 | 0.02381 | 1.4835 | 6188.1538 | 0.92099 | 6188.13
38960.5743 | 29 | 0 | 38960.5743 | 2005 | 0 |  | 2921 | 3046 | 1.7705 | 0 | 122.4054 | 0 | 0.017705 | 0 | 1.2241 | 0 | 0.017705 | 1.2241 | 8356.4828 | 22.3132 | 8356.4651
38960.5748 | 25 | 0 | 38960.5748 | 1986 | 0 |  | 2963 | 3088 | 1.5263 | 0 | 121.2454 | 0 | 0.015263 | 0 | 1.2125 | 0 | 0.015263 | 1.2125 | 9709.52 | 23.4834 | 9709.5047
38960.5753 | 16 | 0 | 38960.5753 | 2369 | 0 |  | 3005 | 3130 | 0.9768 | 0 | 144.6276 | 0 | 0.009768 | 0 | 1.4463 | 0 | 0.009768 | 1.4463 | 15227.375 | 3.5196 | 15227.3652
38960.5757 | 12 | 0 | 38960.5758 | 2028 | 0 |  | 3047 | 3172 | 0.7326 | 0 | 123.8095 | 0 | 0.007326 | 0 | 1.2381 | 0 | 0.007326 | 1.2381 | 20336.5 | 20.926 | 20336.4927

## A2-C5
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 148.4359 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38960.5393 | 1 | 0 | 38960.5393 | 1 | 0 |  | -105.5 | 19.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5397 | 1 | 1 | 38960.5398 | 1 | 0 |  | -63 | 62 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 590674694.44 | 243038 | 242838.0823
38960.5402 | 1 | 0 | 38960.5403 | 1 | 0 |  | -21 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5407 | 1 | 0 | 38960.5407 | 1 | 0 |  | 21 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5412 | 1 | 0 | 38960.5412 | 1 | 0 |  | 63 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5417 | 1 | 0 | 38960.5417 | 1 | 0 |  | 104.5 | 229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5422 | 1 | 0 | 38960.5422 | 1 | 0 |  | 146.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5427 | 1 | 0 | 38960.5427 | 1 | 0 |  | 189 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5431 | 1 | 0 | 38960.5432 | 1 | 0 |  | 230.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5436 | 1 | 0 | 38960.5436 | 1 | 0 |  | 272.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5441 | 1 | 0 | 38960.5441 | 1 | 0 |  | 314.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5446 | 1 | 0 | 38960.5446 | 1 | 0 |  | 356.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5451 | 1 | 0 | 38960.5451 | 1 | 0 |  | 398.5 | 523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5456 | 1 | 0 | 38960.5456 | 1 | 0 |  | 440.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5461 | 1 | 0 | 38960.5461 | 1 | 0 |  | 482.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5466 | 1 | 0 | 38960.5466 | 1 | 0 |  | 524.5 | 649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.547 | 1 | 0 | 38960.547 | 1 | 0 |  | 566.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5475 | 1 | 0 | 38960.5475 | 1 | 0 |  | 608.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.548 | 1 | 0 | 38960.548 | 1 | 0 |  | 650.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5485 | 1 | 0 | 38960.5485 | 1 | 0 |  | 692.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.549 | 1 | 0 | 38960.549 | 1 | 0 |  | 734.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5495 | 1 | 0 | 38960.5495 | 1 | 0 |  | 776.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.55 | 1 | 0 | 38960.55 | 1 | 0 |  | 818.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5504 | 1 | 0 | 38960.5505 | 1 | 0 |  | 860.5 | 985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5509 | 1 | 0 | 38960.5509 | 1 | 0 |  | 902.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5514 | 1 | 0 | 38960.5514 | 1 | 0 |  | 944.5 | 1069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5519 | 1 | 0 | 38960.5519 | 1 | 0 |  | 986.5 | 1111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5524 | 1 | 0 | 38960.5524 | 1 | 0 |  | 1028.5 | 1153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5529 | 1 | 0 | 38960.5529 | 1 | 0 |  | 1070.5 | 1195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5534 | 1 | 0 | 38960.5534 | 1 | 0 |  | 1112.5 | 1237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5538 | 1 | 0 | 38960.5539 | 1 | 0 |  | 1154.5 | 1279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5543 | 1 | 0 | 38960.5543 | 1 | 0 |  | 1196.5 | 1321.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5548 | 1 | 0 | 38960.5548 | 1 | 0 |  | 1238.5 | 1363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5553 | 1 | 0 | 38960.5553 | 1 | 0 |  | 1280.5 | 1405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5558 | 1 | 0 | 38960.5558 | 1 | 0 |  | 1322.5 | 1447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5563 | 1 | 0 | 38960.5563 | 1 | 0 |  | 1364.5 | 1489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5568 | 1 | 0 | 38960.5568 | 1 | 0 |  | 1406.5 | 1531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5572 | 1 | 0 | 38960.5573 | 1 | 0 |  | 1448.5 | 1573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5577 | 1 | 0 | 38960.5577 | 1 | 0 |  | 1490.5 | 1615.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5582 | 1 | 0 | 38960.5582 | 1 | 0 |  | 1532.5 | 1657.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5587 | 1 | 0 | 38960.5587 | 1 | 0 |  | 1574.5 | 1699.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5592 | 1 | 0 | 38960.5592 | 1 | 0 |  | 1616.5 | 1741.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5597 | 1 | 0 | 38960.5597 | 1 | 0 |  | 1658.5 | 1783.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243038 | 243038 | 243037.9994
38960.5602 | 2 | 0 | 38960.5602 | 2 | 0 |  | 1700.5 | 1825.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121469 | 121469 | 121468.9988
38960.5606 | 2 | 0 | 38960.5607 | 3 | 0 |  | 1742.5 | 1867.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 121469 | 80946 | 121468.9988
38960.5611 | 2 | 0 | 38960.5611 | 1825 | 0 |  | 1784.5 | 1909.5 | 0.1221 | 0 | 111.4164 | 0 | 0.001221 | 0 | 1.1142 | 0 | 0.001221 | 1.1142 | 121469 | 33.2263 | 121468.9988
38960.5616 | 2 | 0 | 38960.5616 | 1919 | 0 |  | 1826.5 | 1951.5 | 0.1221 | 0 | 117.1551 | 0 | 0.001221 | 0 | 1.1716 | 0 | 0.001221 | 1.1716 | 121469 | 26.7004 | 121468.9988
38960.5621 | 2 | 0 | 38960.5621 | 1823 | 0 |  | 1868.5 | 1993.5 | 0.1221 | 0 | 111.2943 | 0 | 0.001221 | 0 | 1.1129 | 0 | 0.001221 | 1.1129 | 121469 | 33.3725 | 121468.9988
38960.5626 | 2 | 0 | 38960.5626 | 2227 | 0 |  | 1910.5 | 2035.5 | 0.1221 | 0 | 135.9585 | 0 | 0.001221 | 0 | 1.3596 | 0 | 0.001221 | 1.3596 | 121469 | 9.1774 | 121468.9988
38960.5631 | 2 | 0 | 38960.5631 | 1929 | 0 |  | 1952.5 | 2077.5 | 0.1221 | 0 | 117.7656 | 0 | 0.001221 | 0 | 1.1777 | 0 | 0.001221 | 1.1777 | 121469 | 26.0435 | 121468.9988
38960.5636 | 2 | 0 | 38960.5636 | 2346 | 0 |  | 1994.5 | 2119.5 | 0.1221 | 0 | 143.2234 | 0 | 0.001221 | 0 | 1.4322 | 0 | 0.001221 | 1.4322 | 121469 | 3.6394 | 121468.9988
38960.5641 | 2 | 0 | 38960.5641 | 1946 | 0 |  | 2036.5 | 2161.5 | 0.1221 | 0 | 118.8034 | 0 | 0.001221 | 0 | 1.188 | 0 | 0.001221 | 1.188 | 121469 | 24.9424 | 121468.9988
38960.5645 | 2 | 0 | 38960.5645 | 2074 | 0 |  | 2078.5 | 2203.5 | 0.1221 | 0 | 126.6178 | 0 | 0.001221 | 0 | 1.2662 | 0 | 0.001221 | 1.2662 | 121469 | 17.2314 | 121468.9988
38960.565 | 2 | 0 | 38960.565 | 1850 | 0 |  | 2120.5 | 2245.5 | 0.1221 | 0 | 112.9426 | 0 | 0.001221 | 0 | 1.1294 | 0 | 0.001221 | 1.1294 | 121469 | 31.4259 | 121468.9988
38960.5655 | 2 | 0 | 38960.5655 | 2102 | 0 |  | 2162.5 | 2287.5 | 0.1221 | 0 | 128.3272 | 0 | 0.001221 | 0 | 1.2833 | 0 | 0.001221 | 1.2833 | 121469 | 15.6698 | 121468.9988
38960.566 | 2 | 0 | 38960.566 | 2000 | 0 |  | 2204.5 | 2329.5 | 0.1221 | 0 | 122.1001 | 0 | 0.001221 | 0 | 1.221 | 0 | 0.001221 | 1.221 | 121469 | 21.569 | 121468.9988
38960.5665 | 2 | 0 | 38960.5665 | 2105 | 0 |  | 2246.5 | 2371.5 | 0.1221 | 0 | 128.5104 | 0 | 0.001221 | 0 | 1.2851 | 0 | 0.001221 | 1.2851 | 121469 | 15.505 | 121468.9988
38960.567 | 2 | 0 | 38960.567 | 1923 | 0 |  | 2288.5 | 2413.5 | 0.1221 | 0 | 117.3993 | 0 | 0.001221 | 0 | 1.174 | 0 | 0.001221 | 1.174 | 121469 | 26.4368 | 121468.9988
38960.5675 | 2 | 0 | 38960.5675 | 2320 | 0 |  | 2330.5 | 2455.5 | 0.1221 | 0 | 141.6361 | 0 | 0.001221 | 0 | 1.4164 | 0 | 0.001221 | 1.4164 | 121469 | 4.8009 | 121468.9988
38960.5679 | 2 | 0 | 38960.568 | 2324 | 0 |  | 2372.5 | 2497.5 | 0.1221 | 0 | 141.8803 | 0 | 0.001221 | 0 | 1.4188 | 0 | 0.001221 | 1.4188 | 121469 | 4.6205 | 121468.9988
38960.5684 | 3 | 0 | 38960.5684 | 2174 | 0 |  | 2414.5 | 2539.5 | 0.18315 | 0 | 132.7228 | 0 | 0.0018315 | 0 | 1.3272 | 0 | 0.0018315 | 1.3272 | 80946 | 11.839 | 80945.9982
38960.5689 | 5 | 0 | 38960.5689 | 1986 | 0 |  | 2456.5 | 2581.5 | 0.30525 | 0 | 121.2454 | 0 | 0.0030525 | 0 | 1.2125 | 0 | 0.0030525 | 1.2125 | 48527.6 | 22.426 | 48527.5969
38960.5694 | 6 | 0 | 38960.5694 | 2103 | 0 |  | 2498.5 | 2623.5 | 0.3663 | 0 | 128.3883 | 0 | 0.003663 | 0 | 1.2839 | 0 | 0.003663 | 1.2839 | 40423 | 15.6148 | 40422.9963
38960.5699 | 9 | 0 | 38960.5699 | 1967 | 0 |  | 2540.5 | 2665.5 | 0.54945 | 0 | 120.0855 | 0 | 0.0054945 | 0 | 1.2009 | 0 | 0.0054945 | 1.2009 | 26915.3333 | 23.6085 | 26915.3278
38960.5704 | 15 | 0 | 38960.5704 | 1890 | 0 |  | 2582.5 | 2707.5 | 0.91575 | 0 | 115.3846 | 0 | 0.0091575 | 0 | 1.1538 | 0 | 0.0091575 | 1.1538 | 16109.2 | 28.6444 | 16109.1908
38960.5709 | 23 | 0 | 38960.5709 | 2050 | 0 |  | 2624.5 | 2749.5 | 1.4042 | 0 | 125.1526 | 0 | 0.014042 | 0 | 1.2515 | 0 | 0.014042 | 1.2515 | 10471.2174 | 18.6039 | 10471.2033
38960.5713 | 30 | 0 | 38960.5714 | 1995 | 0 |  | 2666.5 | 2791.5 | 1.8315 | 0 | 121.7949 | 0 | 0.018315 | 0 | 1.2179 | 0 | 0.018315 | 1.2179 | 8004.6 | 21.8737 | 8004.5817
38960.5718 | 40 | 0 | 38960.5718 | 1991 | 0 |  | 2708.5 | 2833.5 | 2.442 | 0 | 121.5507 | 0 | 0.02442 | 0 | 1.2155 | 0 | 0.02442 | 1.2155 | 5978.45 | 22.1185 | 5978.4256
38960.5723 | 43 | 0 | 38960.5723 | 2250 | 0 |  | 2750.5 | 2875.5 | 2.6252 | 0 | 137.3626 | 0 | 0.026252 | 0 | 1.3736 | 0 | 0.026252 | 1.3736 | 5554.3721 | 8.0613 | 5554.3458
38960.5728 | 51 | 0 | 38960.5728 | 2415 | 0 |  | 2792.5 | 2917.5 | 3.1136 | 0 | 147.4359 | 0 | 0.031136 | 0 | 1.4744 | 0 | 0.031136 | 1.4744 | 4667.4118 | 0.67826 | 4667.3806
38960.5733 | 45 | 0 | 38960.5733 | 2377 | 0 |  | 2834.5 | 2959.5 | 2.7473 | 0 | 145.116 | 0 | 0.027473 | 0 | 1.4512 | 0 | 0.027473 | 1.4512 | 5303.0667 | 2.2878 | 5303.0392
38960.5738 | 42 | 0 | 38960.5738 | 2415 | 0 |  | 2876.5 | 3001.5 | 2.5641 | 0 | 147.4359 | 0 | 0.025641 | 0 | 1.4744 | 0 | 0.025641 | 1.4744 | 5689 | 0.67826 | 5688.9744
38960.5743 | 28 | 0 | 38960.5743 | 1884 | 0 |  | 2918.5 | 3043.5 | 1.7094 | 0 | 115.0183 | 0 | 0.017094 | 0 | 1.1502 | 0 | 0.017094 | 1.1502 | 8583.5 | 29.0541 | 8583.4829
38960.5747 | 24 | 0 | 38960.5748 | 2158 | 0 |  | 2960.5 | 3085.5 | 1.4652 | 0 | 131.746 | 0 | 0.014652 | 0 | 1.3175 | 0 | 0.014652 | 1.3175 | 10030.75 | 12.6682 | 10030.7353
38960.5752 | 20 | 0 | 38960.5752 | 2002 | 0 |  | 3002.5 | 3127.5 | 1.221 | 0 | 122.2222 | 0 | 0.01221 | 0 | 1.2222 | 0 | 0.01221 | 1.2222 | 12056.9 | 21.4476 | 12056.8878
38960.5757 | 11 | 0 | 38960.5757 | 2128 | 0 |  | 3044.5 | 3169.5 | 0.67155 | 0 | 129.9145 | 0 | 0.0067155 | 0 | 1.2991 | 0 | 0.0067155 | 1.2991 | 22003.4545 | 14.2566 | 22003.4478

## A2-B4
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 129 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38960.5392 | 1 | 1 | 38960.5392 | 1 | 0 |  | -108 | 17 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38960.5397 | 1 | 0 | 38960.5397 | 1 | 0 |  | -66 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5402 | 1 | 0 | 38960.5402 | 1 | 0 |  | -24 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5407 | 1 | 0 | 38960.5407 | 1 | 0 |  | 18 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5412 | 1 | 0 | 38960.5412 | 1 | 0 |  | 60 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5417 | 1 | 0 | 38960.5417 | 1 | 0 |  | 102 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5421 | 1 | 0 | 38960.5422 | 1 | 0 |  | 144 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5426 | 1 | 0 | 38960.5427 | 1 | 0 |  | 186 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5431 | 1 | 0 | 38960.5431 | 1 | 0 |  | 228 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5436 | 1 | 0 | 38960.5436 | 1 | 0 |  | 270 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5441 | 1 | 0 | 38960.5441 | 1 | 0 |  | 312 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5446 | 1 | 0 | 38960.5446 | 1 | 0 |  | 354 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5451 | 1 | 0 | 38960.5451 | 1 | 0 |  | 396 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5455 | 1 | 0 | 38960.5456 | 1 | 0 |  | 438 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.546 | 1 | 0 | 38960.5461 | 1 | 0 |  | 480 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5465 | 1 | 0 | 38960.5465 | 1 | 0 |  | 522 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.547 | 1 | 0 | 38960.547 | 1 | 0 |  | 564 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5475 | 1 | 0 | 38960.5475 | 1 | 0 |  | 606 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.548 | 1 | 0 | 38960.548 | 1 | 0 |  | 648 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5485 | 1 | 0 | 38960.5485 | 1 | 0 |  | 690 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5489 | 1 | 0 | 38960.549 | 1 | 0 |  | 732 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5494 | 1 | 0 | 38960.5495 | 1 | 0 |  | 774 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5499 | 1 | 0 | 38960.5499 | 1 | 0 |  | 816 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5504 | 1 | 0 | 38960.5504 | 1 | 0 |  | 858 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5509 | 1 | 0 | 38960.5509 | 1 | 0 |  | 900 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5514 | 1 | 0 | 38960.5514 | 1 | 0 |  | 942 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5519 | 1 | 0 | 38960.5519 | 1 | 0 |  | 984 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5523 | 1 | 0 | 38960.5524 | 1 | 0 |  | 1026 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5528 | 1 | 0 | 38960.5529 | 1 | 0 |  | 1068 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5533 | 1 | 0 | 38960.5533 | 1 | 0 |  | 1110 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5538 | 1 | 0 | 38960.5538 | 1 | 0 |  | 1152 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5543 | 1 | 0 | 38960.5543 | 1 | 0 |  | 1193.5 | 1318.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5548 | 1 | 0 | 38960.5548 | 1 | 0 |  | 1235.5 | 1360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5553 | 1 | 0 | 38960.5553 | 1 | 0 |  | 1278 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5558 | 1 | 0 | 38960.5558 | 1 | 0 |  | 1319.5 | 1444.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5562 | 1 | 0 | 38960.5563 | 1 | 0 |  | 1362 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5567 | 1 | 0 | 38960.5567 | 1 | 0 |  | 1403.5 | 1528.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5572 | 1 | 0 | 38960.5572 | 1 | 0 |  | 1446 | 1571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5577 | 1 | 0 | 38960.5577 | 1 | 0 |  | 1488 | 1613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5582 | 1 | 0 | 38960.5582 | 1 | 0 |  | 1529.5 | 1654.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5587 | 1 | 0 | 38960.5587 | 1 | 0 |  | 1571.5 | 1696.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5592 | 1 | 0 | 38960.5592 | 2 | 0 |  | 1613.5 | 1738.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38960.5596 | 1 | 0 | 38960.5597 | 1 | 0 |  | 1655.5 | 1780.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5601 | 1 | 0 | 38960.5601 | 2 | 0 |  | 1697.5 | 1822.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38960.5606 | 2 | 0 | 38960.5606 | 1 | 0 |  | 1739.5 | 1864.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38960.5611 | 2 | 0 | 38960.5611 | 2 | 0 |  | 1781.5 | 1906.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5616 | 2 | 0 | 38960.5616 | 1 | 0 |  | 1823.5 | 1948.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38960.5621 | 2 | 0 | 38960.5621 | 2 | 0 |  | 1865.5 | 1990.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5626 | 2 | 0 | 38960.5626 | 1 | 0 |  | 1907.5 | 2032.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38960.563 | 2 | 0 | 38960.5631 | 1 | 0 |  | 1949.5 | 2074.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38960.5635 | 2 | 0 | 38960.5635 | 2 | 0 |  | 1991.5 | 2116.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.564 | 2 | 0 | 38960.564 | 2 | 0 |  | 2033.5 | 2158.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5645 | 2 | 0 | 38960.5645 | 2 | 0 |  | 2075.5 | 2200.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.565 | 2 | 0 | 38960.565 | 2 | 0 |  | 2117.5 | 2242.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5655 | 2 | 0 | 38960.5655 | 2 | 0 |  | 2159.5 | 2284.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.566 | 2 | 0 | 38960.566 | 2 | 0 |  | 2201.5 | 2326.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5664 | 3 | 0 | 38960.5665 | 2 | 0 |  | 2243.5 | 2368.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38960.5669 | 2 | 0 | 38960.5669 | 2 | 0 |  | 2285.5 | 2410.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5674 | 2 | 0 | 38960.5674 | 2 | 0 |  | 2327.5 | 2452.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38960.5679 | 3 | 0 | 38960.5679 | 2 | 0 |  | 2369.5 | 2494.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38960.5684 | 3 | 0 | 38960.5684 | 3 | 0 |  | 2411.5 | 2536.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38960.5689 | 4 | 0 | 38960.5689 | 4 | 0 |  | 2453.5 | 2578.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38960.5694 | 5 | 0 | 38960.5694 | 5 | 0 |  | 2495.5 | 2620.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38960.5698 | 9 | 0 | 38960.5699 | 10 | 0 |  | 2537.5 | 2662.5 | 0.54945 | 0 | 0.6105 | 0 | 0.0054945 | 0 | 0.006105 | 0 | 0.0054945 | 0.006105 | 23378 | 21030.2 | 23377.9945
38960.5703 | 15 | 0 | 38960.5703 | 14 | 0 |  | 2579.5 | 2704.5 | 0.91575 | 0 | 0.8547 | 0 | 0.0091575 | 0 | 0.008547 | 0 | 0.0091575 | 0.008547 | 13986.8 | 14993 | 13986.7908
38960.5708 | 20 | 0 | 38960.5708 | 22 | 0 |  | 2621.5 | 2746.5 | 1.221 | 0 | 1.3431 | 0 | 0.01221 | 0 | 0.013431 | 0 | 0.01221 | 0.013431 | 10465.1 | 9504.6364 | 10465.0878
38960.5713 | 27 | 0 | 38960.5713 | 29 | 0 |  | 2663.5 | 2788.5 | 1.6484 | 0 | 1.7705 | 0 | 0.016484 | 0 | 0.017705 | 0 | 0.016484 | 0.017705 | 7726 | 7186.2759 | 7725.9835
38960.5718 | 39 | 0 | 38960.5718 | 41 | 0 |  | 2705.5 | 2830.5 | 2.381 | 0 | 2.5031 | 0 | 0.02381 | 0 | 0.025031 | 0 | 0.02381 | 0.025031 | 5318 | 5053.7073 | 5317.9762
38960.5723 | 46 | 0 | 38960.5723 | 39 | 0 |  | 2747.5 | 2872.5 | 2.8083 | 0 | 2.381 | 0 | 0.028083 | 0 | 0.02381 | 0 | 0.028083 | 0.02381 | 4493.5217 | 5318 | 4493.4937
38960.5728 | 40 | 0 | 38960.5728 | 45 | 0 |  | 2789.5 | 2914.5 | 2.442 | 0 | 2.7473 | 0 | 0.02442 | 0 | 0.027473 | 0 | 0.02442 | 0.027473 | 5182.55 | 4595.6 | 5182.5256
38960.5733 | 43 | 0 | 38960.5733 | 38 | 0 |  | 2831.5 | 2956.5 | 2.6252 | 0 | 2.3199 | 0 | 0.026252 | 0 | 0.023199 | 0 | 0.026252 | 0.023199 | 4814 | 5460.5789 | 4813.9737
38960.5737 | 35 | 0 | 38960.5738 | 37 | 0 |  | 2873.5 | 2998.5 | 2.1368 | 0 | 2.2589 | 0 | 0.021368 | 0 | 0.022589 | 0 | 0.021368 | 0.022589 | 5937.2 | 5610.8649 | 5937.1786
38960.5742 | 28 | 0 | 38960.5742 | 33 | 0 |  | 2915.5 | 3040.5 | 1.7094 | 0 | 2.0147 | 0 | 0.017094 | 0 | 0.020147 | 0 | 0.017094 | 0.020147 | 7446.5 | 6303.0909 | 7446.4829
38960.5747 | 20 | 0 | 38960.5747 | 20 | 0 |  | 2957.5 | 3082.5 | 1.221 | 0 | 1.221 | 0 | 0.01221 | 0 | 0.01221 | 0 | 0.01221 | 0.01221 | 10465.1 | 10465.1 | 10465.0878
38960.5752 | 18 | 0 | 38960.5752 | 15 | 0 |  | 2999.5 | 3124.5 | 1.0989 | 0 | 0.91575 | 0 | 0.010989 | 0 | 0.0091575 | 0 | 0.010989 | 0.0091575 | 11639 | 13986.8 | 11638.989
38960.5757 | 10 | 0 | 38960.5757 | 11 | 0 |  | 3041.5 | 3166.5 | 0.6105 | 0 | 0.67155 | 0 | 0.006105 | 0 | 0.0067155 | 0 | 0.006105 | 0.0067155 | 21030.2 | 19109.2727 | 21030.1939

## A2-B3
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 150.7558 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38960.5392 | 1 | 0 | 38960.5392 | 1 | 0 |  | -111 | 14 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5397 | 1 | 1 | 38960.5397 | 1 | 0 |  | -68.5 | 56.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 609289982.44 | 246838 | 246638.081
38960.5402 | 1 | 0 | 38960.5402 | 2 | 0 |  | -27 | 98 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 246838 | 123369 | 246837.9994
38960.5406 | 1 | 0 | 38960.5407 | 1 | 0 |  | 15 | 140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5411 | 1 | 0 | 38960.5412 | 1 | 0 |  | 57 | 182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5416 | 1 | 0 | 38960.5416 | 1 | 0 |  | 99 | 224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5421 | 1 | 0 | 38960.5421 | 1 | 0 |  | 141 | 266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5426 | 1 | 0 | 38960.5426 | 1 | 0 |  | 183 | 308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5431 | 1 | 0 | 38960.5431 | 1 | 0 |  | 225.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5436 | 1 | 1 | 38960.5436 | 1 | 0 |  | 267 | 392 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 609289982.44 | 246838 | 246638.081
38960.5441 | 1 | 0 | 38960.5441 | 1 | 0 |  | 309 | 434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5445 | 1 | 0 | 38960.5446 | 1 | 0 |  | 351 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.545 | 1 | 0 | 38960.545 | 1 | 0 |  | 393 | 518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5455 | 1 | 0 | 38960.5455 | 1 | 0 |  | 435 | 560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.546 | 1 | 0 | 38960.546 | 1 | 0 |  | 477 | 602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5465 | 1 | 0 | 38960.5465 | 1 | 0 |  | 519 | 644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.547 | 1 | 0 | 38960.547 | 1 | 0 |  | 561 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5475 | 1 | 0 | 38960.5475 | 1 | 0 |  | 603 | 728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5479 | 1 | 0 | 38960.548 | 1 | 0 |  | 645 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5484 | 1 | 0 | 38960.5484 | 1 | 0 |  | 687 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5489 | 1 | 0 | 38960.5489 | 1 | 0 |  | 729 | 854 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5494 | 1 | 0 | 38960.5494 | 1 | 0 |  | 771 | 896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5499 | 1 | 0 | 38960.5499 | 1 | 0 |  | 813 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5504 | 1 | 0 | 38960.5504 | 1 | 0 |  | 855 | 980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5509 | 1 | 0 | 38960.5509 | 1 | 0 |  | 897 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5513 | 1 | 0 | 38960.5514 | 1 | 0 |  | 939 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5518 | 1 | 0 | 38960.5519 | 1 | 0 |  | 981 | 1106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5523 | 1 | 0 | 38960.5523 | 1 | 0 |  | 1023 | 1148 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5528 | 2 | 0 | 38960.5528 | 1 | 0 |  | 1065 | 1190 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123369 | 246838 | 123368.9988
38960.5533 | 1 | 0 | 38960.5533 | 1 | 0 |  | 1107 | 1232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5538 | 2 | 0 | 38960.5538 | 1 | 0 |  | 1149 | 1274 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123369 | 246838 | 123368.9988
38960.5543 | 1 | 0 | 38960.5543 | 1 | 0 |  | 1191 | 1316 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5547 | 1 | 0 | 38960.5548 | 1 | 0 |  | 1233 | 1358 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5552 | 1 | 0 | 38960.5553 | 1 | 0 |  | 1275 | 1400 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5557 | 1 | 0 | 38960.5557 | 1 | 0 |  | 1317 | 1442 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5562 | 1 | 0 | 38960.5562 | 1 | 0 |  | 1359 | 1484 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5567 | 1 | 0 | 38960.5567 | 1 | 0 |  | 1401 | 1526 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5572 | 1 | 0 | 38960.5572 | 1 | 0 |  | 1443 | 1568 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5577 | 1 | 0 | 38960.5577 | 1 | 0 |  | 1485 | 1610 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5581 | 1 | 0 | 38960.5582 | 1 | 0 |  | 1527 | 1652 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5586 | 1 | 0 | 38960.5587 | 1 | 0 |  | 1569 | 1694 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5591 | 1 | 0 | 38960.5591 | 1 | 0 |  | 1611 | 1736 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246838 | 246838 | 246837.9994
38960.5596 | 1 | 0 | 38960.5596 | 124 | 0 |  | 1653 | 1778 | 0.06105 | 0 | 7.5702 | 0 | 0.0006105 | 0 | 0.075702 | 0 | 0.0006105 | 0.075702 | 246838 | 1891.4355 | 246837.9994
38960.5601 | 1 | 0 | 38960.5601 | 1786 | 0 |  | 1695 | 1820 | 0.06105 | 0 | 109.0354 | 0 | 0.0006105 | 0 | 1.0904 | 0 | 0.0006105 | 1.0904 | 246838 | 38.2632 | 246837.9994
38960.5606 | 1 | 0 | 38960.5606 | 1947 | 0 |  | 1737 | 1862 | 0.06105 | 0 | 118.8645 | 0 | 0.0006105 | 0 | 1.1886 | 0 | 0.0006105 | 1.1886 | 246838 | 26.83 | 246837.9994
38960.5611 | 2 | 0 | 38960.5611 | 2170 | 0 |  | 1779 | 1904 | 0.1221 | 0 | 132.4786 | 0 | 0.001221 | 0 | 1.3248 | 0 | 0.001221 | 1.3248 | 123369 | 13.7963 | 123368.9988
38960.5616 | 2 | 0 | 38960.5616 | 2333 | 0 |  | 1821 | 1946 | 0.1221 | 0 | 142.4298 | 0 | 0.001221 | 0 | 1.4243 | 0 | 0.001221 | 1.4243 | 123369 | 5.8457 | 123368.9988
38960.562 | 2 | 0 | 38960.5621 | 2210 | 0 |  | 1863 | 1988 | 0.1221 | 0 | 134.9206 | 0 | 0.001221 | 0 | 1.3492 | 0 | 0.001221 | 1.3492 | 123369 | 11.7367 | 123368.9988
38960.5625 | 2 | 0 | 38960.5625 | 2152 | 0 |  | 1905 | 2030 | 0.1221 | 0 | 131.3797 | 0 | 0.001221 | 0 | 1.3138 | 0 | 0.001221 | 1.3138 | 123369 | 14.7481 | 123368.9988
38960.563 | 2 | 0 | 38960.563 | 1832 | 0 |  | 1947 | 2072 | 0.1221 | 0 | 111.8437 | 0 | 0.001221 | 0 | 1.1184 | 0 | 0.001221 | 1.1184 | 123369 | 34.7915 | 123368.9988
38960.5635 | 2 | 0 | 38960.5635 | 2171 | 0 |  | 1989 | 2114 | 0.1221 | 0 | 132.5397 | 0 | 0.001221 | 0 | 1.3254 | 0 | 0.001221 | 1.3254 | 123369 | 13.7439 | 123368.9988
38960.564 | 2 | 0 | 38960.564 | 2017 | 0 |  | 2031 | 2156 | 0.1221 | 0 | 123.138 | 0 | 0.001221 | 0 | 1.2314 | 0 | 0.001221 | 1.2314 | 123369 | 22.4284 | 123368.9988
38960.5645 | 2 | 0 | 38960.5645 | 2288 | 0 |  | 2073 | 2198 | 0.1221 | 0 | 139.6825 | 0 | 0.001221 | 0 | 1.3968 | 0 | 0.001221 | 1.3968 | 123369 | 7.9274 | 123368.9988
38960.565 | 2 | 0 | 38960.565 | 1963 | 0 |  | 2115 | 2240 | 0.1221 | 0 | 119.8413 | 0 | 0.001221 | 0 | 1.1984 | 0 | 0.001221 | 1.1984 | 123369 | 25.7962 | 123368.9988
38960.5654 | 2 | 0 | 38960.5655 | 2081 | 0 |  | 2157 | 2282 | 0.1221 | 0 | 127.0452 | 0 | 0.001221 | 0 | 1.2705 | 0 | 0.001221 | 1.2705 | 123369 | 18.6631 | 123368.9988
38960.5659 | 2 | 0 | 38960.5659 | 2308 | 0 |  | 2199 | 2324 | 0.1221 | 0 | 140.9035 | 0 | 0.001221 | 0 | 1.409 | 0 | 0.001221 | 1.409 | 123369 | 6.9922 | 123368.9988
38960.5664 | 2 | 0 | 38960.5664 | 2178 | 0 |  | 2241 | 2366 | 0.1221 | 0 | 132.967 | 0 | 0.001221 | 0 | 1.3297 | 0 | 0.001221 | 1.3297 | 123369 | 13.3783 | 123368.9988
38960.5669 | 2 | 0 | 38960.5669 | 2453 | 0 |  | 2282.5 | 2407.5 | 0.1221 | 0 | 149.7558 | 0 | 0.001221 | 0 | 1.4976 | 0 | 0.001221 | 1.4976 | 123369 | 0.66775 | 123368.9988
38960.5674 | 2 | 0 | 38960.5674 | 2302 | 0 |  | 2325 | 2450 | 0.1221 | 0 | 140.5372 | 0 | 0.001221 | 0 | 1.4054 | 0 | 0.001221 | 1.4054 | 123369 | 7.2711 | 123368.9988
38960.5679 | 3 | 0 | 38960.5679 | 1948 | 0 |  | 2367 | 2492 | 0.18315 | 0 | 118.9255 | 0 | 0.0018315 | 0 | 1.1893 | 0 | 0.0018315 | 1.1893 | 82212.6667 | 26.7649 | 82212.6648
38960.5684 | 3 | 0 | 38960.5684 | 2219 | 0 |  | 2408.5 | 2533.5 | 0.18315 | 0 | 135.4701 | 0 | 0.0018315 | 0 | 1.3547 | 0 | 0.0018315 | 1.3547 | 82212.6667 | 11.2835 | 82212.6648
38960.5688 | 4 | 0 | 38960.5689 | 1913 | 0 |  | 2450.5 | 2575.5 | 0.2442 | 0 | 116.7888 | 0 | 0.002442 | 0 | 1.1679 | 0 | 0.002442 | 1.1679 | 61634.5 | 29.0842 | 61634.4976
38960.5693 | 5 | 0 | 38960.5694 | 2430 | 0 |  | 2493 | 2618 | 0.30525 | 0 | 148.3516 | 0 | 0.0030525 | 0 | 1.4835 | 0 | 0.0030525 | 1.4835 | 49287.6 | 1.6206 | 49287.5969
38960.5698 | 8 | 0 | 38960.5698 | 2000 | 0 |  | 2534.5 | 2659.5 | 0.4884 | 0 | 122.1001 | 0 | 0.004884 | 0 | 1.221 | 0 | 0.004884 | 1.221 | 30767.25 | 23.469 | 30767.2451
38960.5703 | 14 | 0 | 38960.5703 | 2338 | 0 |  | 2577 | 2702 | 0.8547 | 0 | 142.735 | 0 | 0.008547 | 0 | 1.4274 | 0 | 0.008547 | 1.4274 | 17538.4286 | 5.6193 | 17538.42
38960.5708 | 21 | 0 | 38960.5708 | 2375 | 0 |  | 2618.5 | 2743.5 | 1.2821 | 0 | 144.9939 | 0 | 0.012821 | 0 | 1.4499 | 0 | 0.012821 | 1.4499 | 11658.9524 | 3.9739 | 11658.9396
38960.5713 | 29 | 0 | 38960.5713 | 1935 | 0 |  | 2660.5 | 2785.5 | 1.7705 | 0 | 118.1319 | 0 | 0.017705 | 0 | 1.1813 | 0 | 0.017705 | 1.1813 | 8415.1034 | 27.6165 | 8415.0857
38960.5718 | 32 | 0 | 38960.5718 | 2426 | 0 |  | 2702.5 | 2827.5 | 1.9536 | 0 | 148.1074 | 0 | 0.019536 | 0 | 1.4811 | 0 | 0.019536 | 1.4811 | 7616.8125 | 1.7881 | 7616.793
38960.5722 | 39 | 0 | 38960.5723 | 2253 | 0 |  | 2744.5 | 2869.5 | 2.381 | 0 | 137.5458 | 0 | 0.02381 | 0 | 1.3755 | 0 | 0.02381 | 1.3755 | 6231.7436 | 9.6041 | 6231.7198
38960.5727 | 43 | 0 | 38960.5728 | 1970 | 0 |  | 2787 | 2912 | 2.6252 | 0 | 120.2686 | 0 | 0.026252 | 0 | 1.2027 | 0 | 0.026252 | 1.2027 | 5642.7442 | 25.3492 | 5642.7179
38960.5732 | 44 | 0 | 38960.5732 | 2112 | 0 |  | 2828.5 | 2953.5 | 2.6862 | 0 | 128.9377 | 0 | 0.026862 | 0 | 1.2894 | 0 | 0.026862 | 1.2894 | 5512.2273 | 16.9214 | 5512.2004
38960.5737 | 31 | 0 | 38960.5737 | 1899 | 0 |  | 2870.5 | 2995.5 | 1.8926 | 0 | 115.9341 | 0 | 0.018926 | 0 | 1.1593 | 0 | 0.018926 | 1.1593 | 7865.7419 | 30.0358 | 7865.723
38960.5742 | 29 | 0 | 38960.5742 | 2321 | 0 |  | 2912.5 | 3037.5 | 1.7705 | 0 | 141.6972 | 0 | 0.017705 | 0 | 1.417 | 0 | 0.017705 | 1.417 | 8415.1034 | 6.3929 | 8415.0857
38960.5747 | 21 | 0 | 38960.5747 | 2140 | 0 |  | 2954.5 | 3079.5 | 1.2821 | 0 | 130.6471 | 0 | 0.012821 | 0 | 1.3065 | 0 | 0.012821 | 1.3065 | 11658.9524 | 15.3916 | 11658.9396
38960.5752 | 17 | 0 | 38960.5752 | 1912 | 0 |  | 2996.5 | 3121.5 | 1.0379 | 0 | 116.7277 | 0 | 0.010379 | 0 | 1.1673 | 0 | 0.010379 | 1.1673 | 14425.7647 | 29.1517 | 14425.7543
38960.5756 | 11 | 0 | 38960.5757 | 2311 | 0 |  | 3038.5 | 3163.5 | 0.67155 | 0 | 141.0867 | 0 | 0.0067155 | 0 | 1.4109 | 0 | 0.0067155 | 1.4109 | 22348.9091 | 6.8533 | 22348.9024

## A1-C6
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 153.381 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38960.5392 | 1 | 0 | 38960.5392 | 1 | 0 |  | -113.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5397 | 1 | 0 | 38960.5397 | 1 | 0 |  | -71.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5401 | 1 | 0 | 38960.5402 | 1 | 0 |  | -29.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5406 | 1 | 0 | 38960.5406 | 1 | 0 |  | 12.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5411 | 1 | 0 | 38960.5411 | 1 | 0 |  | 54.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5416 | 1 | 0 | 38960.5416 | 1 | 0 |  | 96.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5421 | 1 | 0 | 38960.5421 | 1 | 0 |  | 138.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5426 | 1 | 0 | 38960.5426 | 1 | 0 |  | 180.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5431 | 1 | 0 | 38960.5431 | 1 | 0 |  | 222.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5435 | 1 | 0 | 38960.5436 | 1 | 0 |  | 264.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.544 | 1 | 0 | 38960.544 | 1 | 0 |  | 306.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5445 | 1 | 0 | 38960.5445 | 1 | 0 |  | 348.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.545 | 1 | 0 | 38960.545 | 1 | 0 |  | 390.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5455 | 2 | 0 | 38960.5455 | 1 | 0 |  | 432.5 | 557.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125519 | 251138 | 125518.9988
38960.546 | 1 | 0 | 38960.546 | 1 | 0 |  | 474.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5465 | 1 | 0 | 38960.5465 | 1 | 0 |  | 516.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5469 | 1 | 0 | 38960.547 | 1 | 0 |  | 558.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5474 | 1 | 0 | 38960.5474 | 1 | 0 |  | 600.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5479 | 1 | 0 | 38960.5479 | 1 | 0 |  | 642.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5484 | 1 | 0 | 38960.5484 | 1 | 0 |  | 684.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5489 | 1 | 0 | 38960.5489 | 1 | 0 |  | 726.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5494 | 1 | 0 | 38960.5494 | 1 | 0 |  | 768.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5499 | 1 | 0 | 38960.5499 | 1 | 0 |  | 810.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5503 | 1 | 0 | 38960.5504 | 1 | 0 |  | 852.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5508 | 1 | 0 | 38960.5508 | 1 | 0 |  | 894.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5513 | 1 | 0 | 38960.5513 | 1 | 0 |  | 936.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5518 | 1 | 0 | 38960.5518 | 1 | 0 |  | 978.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5523 | 1 | 0 | 38960.5523 | 1 | 0 |  | 1020 | 1145 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5528 | 1 | 0 | 38960.5528 | 1 | 0 |  | 1062.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5533 | 1 | 0 | 38960.5533 | 1 | 0 |  | 1104 | 1229 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5537 | 1 | 0 | 38960.5538 | 1 | 0 |  | 1146.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5542 | 1 | 0 | 38960.5542 | 1 | 0 |  | 1188 | 1313 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5547 | 1 | 0 | 38960.5547 | 1 | 0 |  | 1230.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5552 | 1 | 0 | 38960.5552 | 1 | 0 |  | 1272.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5557 | 1 | 0 | 38960.5557 | 1 | 0 |  | 1314 | 1439 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5562 | 1 | 0 | 38960.5562 | 2 | 0 |  | 1356 | 1481 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 251138 | 125519 | 251137.9994
38960.5567 | 1 | 0 | 38960.5567 | 1 | 0 |  | 1398 | 1523 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5571 | 1 | 0 | 38960.5572 | 1 | 0 |  | 1440 | 1565 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5576 | 1 | 0 | 38960.5577 | 1 | 0 |  | 1482 | 1607 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5581 | 1 | 0 | 38960.5581 | 1 | 0 |  | 1524 | 1649 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5586 | 1 | 0 | 38960.5586 | 1 | 0 |  | 1566 | 1691 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5591 | 1 | 0 | 38960.5591 | 1 | 0 |  | 1608 | 1733 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5596 | 1 | 0 | 38960.5596 | 1 | 0 |  | 1650 | 1775 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5601 | 1 | 0 | 38960.5601 | 1 | 0 |  | 1692 | 1817 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251138 | 251138 | 251137.9994
38960.5605 | 1 | 0 | 38960.5606 | 5 | 0 |  | 1734 | 1859 | 0.06105 | 0 | 0.30525 | 0 | 0.0006105 | 0 | 0.0030525 | 0 | 0.0006105 | 0.0030525 | 251138 | 50147.6 | 251137.9994
38960.561 | 2 | 0 | 38960.5611 | 2 | 0 |  | 1776 | 1901 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 125519 | 125519 | 125518.9988
38960.5615 | 2 | 0 | 38960.5615 | 239 | 0 |  | 1818 | 1943 | 0.1221 | 0 | 14.591 | 0 | 0.001221 | 0 | 0.14591 | 0 | 0.001221 | 0.14591 | 125519 | 951.205 | 125518.9988
38960.562 | 2 | 0 | 38960.562 | 287 | 1 |  | 1860 | 1985 | 0.1221 | 0 | 17.5214 | 0.06105 | 0.001221 | 0 | 0.17521 | 0.0006105 | 0.001221 | 0.1746 | 125519 | 778.4545 | 125518.9988
38960.5625 | 2 | 0 | 38960.5625 | 2333 | 0 |  | 1902 | 2027 | 0.1221 | 0 | 142.4298 | 0 | 0.001221 | 0 | 1.4243 | 0 | 0.001221 | 1.4243 | 125519 | 7.6888 | 125518.9988
38960.563 | 2 | 0 | 38960.563 | 2317 | 0 |  | 1944 | 2069 | 0.1221 | 0 | 141.453 | 0 | 0.001221 | 0 | 1.4145 | 0 | 0.001221 | 1.4145 | 125519 | 8.4325 | 125518.9988
38960.5635 | 2 | 0 | 38960.5635 | 2302 | 0 |  | 1986 | 2111 | 0.1221 | 0 | 140.5372 | 0 | 0.001221 | 0 | 1.4054 | 0 | 0.001221 | 1.4054 | 125519 | 9.139 | 125518.9988
38960.5639 | 2 | 0 | 38960.564 | 1953 | 0 |  | 2028 | 2153 | 0.1221 | 0 | 119.2308 | 0 | 0.001221 | 0 | 1.1923 | 0 | 0.001221 | 1.1923 | 125519 | 28.6421 | 125518.9988
38960.5644 | 2 | 0 | 38960.5645 | 2294 | 0 |  | 2070 | 2195 | 0.1221 | 0 | 140.0488 | 0 | 0.001221 | 0 | 1.4005 | 0 | 0.001221 | 1.4005 | 125519 | 9.5196 | 125518.9988
38960.5649 | 3 | 0 | 38960.5649 | 2064 | 0 |  | 2112 | 2237 | 0.18315 | 0 | 126.0073 | 0 | 0.0018315 | 0 | 1.2601 | 0 | 0.0018315 | 1.2601 | 83646 | 21.7238 | 83645.9982
38960.5654 | 2 | 0 | 38960.5654 | 2341 | 0 |  | 2154 | 2279 | 0.1221 | 0 | 142.9182 | 0 | 0.001221 | 0 | 1.4292 | 0 | 0.001221 | 1.4292 | 125519 | 7.3208 | 125518.9988
38960.5659 | 2 | 0 | 38960.5659 | 1929 | 0 |  | 2196 | 2321 | 0.1221 | 0 | 117.7656 | 0 | 0.001221 | 0 | 1.1777 | 0 | 0.001221 | 1.1777 | 125519 | 30.2426 | 125518.9988
38960.5664 | 2 | 0 | 38960.5664 | 2387 | 0 |  | 2238 | 2363 | 0.1221 | 0 | 145.7265 | 0 | 0.001221 | 0 | 1.4573 | 0 | 0.001221 | 1.4573 | 125519 | 5.2526 | 125518.9988
38960.5669 | 2 | 0 | 38960.5669 | 1991 | 0 |  | 2280 | 2405 | 0.1221 | 0 | 121.5507 | 0 | 0.001221 | 0 | 1.2155 | 0 | 0.001221 | 1.2155 | 125519 | 26.1868 | 125518.9988
38960.5673 | 2 | 0 | 38960.5674 | 2020 | 0 |  | 2322 | 2447 | 0.1221 | 0 | 123.3211 | 0 | 0.001221 | 0 | 1.2332 | 0 | 0.001221 | 1.2332 | 125519 | 24.3752 | 125518.9988
38960.5678 | 3 | 0 | 38960.5679 | 2154 | 0 |  | 2364 | 2489 | 0.18315 | 0 | 131.5018 | 0 | 0.0018315 | 0 | 1.315 | 0 | 0.0018315 | 1.315 | 83646 | 16.6379 | 83645.9982
38960.5683 | 3 | 0 | 38960.5683 | 2496 | 0 |  | 2406 | 2531 | 0.18315 | 0 | 152.381 | 0 | 0.0018315 | 0 | 1.5238 | 0 | 0.0018315 | 1.5238 | 83646 | 0.65625 | 83645.9982
38960.5688 | 4 | 0 | 38960.5688 | 2342 | 0 |  | 2448 | 2573 | 0.2442 | 0 | 142.9792 | 0 | 0.002442 | 0 | 1.4298 | 0 | 0.002442 | 1.4298 | 62709.5 | 7.275 | 62709.4976
38960.5693 | 5 | 0 | 38960.5693 | 2052 | 0 |  | 2490 | 2615 | 0.30525 | 0 | 125.2747 | 0 | 0.0030525 | 0 | 1.2527 | 0 | 0.0030525 | 1.2527 | 50147.6 | 22.4357 | 50147.5969
38960.5698 | 8 | 0 |  | 2036 | 0 |  | 2531 | 2656 | 0.4884 | 0 | 124.2979 | 0 | 0.004884 | 0 | 1.243 | 0 | 0.004884 | 1.243 | 31304.75 | 23.3978 | 31304.7451
38960.5703 | 12 | 0 | 38960.5703 | 2019 | 0 |  | 2574 | 2699 | 0.7326 | 0 | 123.2601 | 0 | 0.007326 | 0 | 1.2326 | 0 | 0.007326 | 1.2326 | 20836.5 | 24.4368 | 20836.4927
38960.5708 | 20 | 0 | 38960.5708 | 2241 | 0 |  | 2616 | 2741 | 1.221 | 0 | 136.8132 | 0 | 0.01221 | 0 | 1.3681 | 0 | 0.01221 | 1.3681 | 12461.9 | 12.1098 | 12461.8878
38960.5712 | 30 | 0 | 38960.5713 | 2232 | 0 |  | 2658 | 2783 | 1.8315 | 0 | 136.2637 | 0 | 0.018315 | 0 | 1.3626 | 0 | 0.018315 | 1.3626 | 8274.6 | 12.5618 | 8274.5817
38960.5717 | 39 | 0 | 38960.5717 | 1945 | 0 |  | 2700 | 2825 | 2.381 | 0 | 118.7424 | 0 | 0.02381 | 0 | 1.1874 | 0 | 0.02381 | 1.1874 | 6342 | 29.1712 | 6341.9762
38960.5722 | 41 | 0 | 38960.5722 | 2168 | 0 |  | 2742 | 2867 | 2.5031 | 0 | 132.3565 | 0 | 0.025031 | 0 | 1.3236 | 0 | 0.025031 | 1.3236 | 6027.7561 | 15.8847 | 6027.7311
38960.5727 | 40 | 0 | 38960.5727 | 2438 | 0 |  | 2784 | 2909 | 2.442 | 0 | 148.84 | 0 | 0.02442 | 0 | 1.4884 | 0 | 0.02442 | 1.4884 | 6180.95 | 3.0509 | 6180.9256
38960.5732 | 42 | 0 | 38960.5732 | 1890 | 0 |  | 2826 | 2951 | 2.5641 | 0 | 115.3846 | 0 | 0.025641 | 0 | 1.1538 | 0 | 0.025641 | 1.1538 | 5881.8571 | 32.9302 | 5881.8315
38960.5737 | 38 | 0 | 38960.5737 | 2160 | 0 |  | 2868 | 2993 | 2.3199 | 0 | 131.8681 | 0 | 0.023199 | 0 | 1.3187 | 0 | 0.023199 | 1.3187 | 6511.5263 | 16.3139 | 6511.5031
38960.5742 | 32 | 0 | 38960.5742 | 2265 | 0 |  | 2910 | 3035 | 1.9536 | 0 | 138.2784 | 0 | 0.019536 | 0 | 1.3828 | 0 | 0.019536 | 1.3828 | 7751.1875 | 10.9219 | 7751.168
38960.5746 | 22 | 0 | 38960.5747 | 2174 | 0 |  | 2952 | 3077 | 1.3431 | 0 | 132.7228 | 0 | 0.013431 | 0 | 1.3272 | 0 | 0.013431 | 1.3272 | 11319.9091 | 15.5649 | 11319.8957
38960.5751 | 16 | 0 | 38960.5752 | 2138 | 0 |  | 2994 | 3119 | 0.9768 | 0 | 130.525 | 0 | 0.009768 | 0 | 1.3053 | 0 | 0.009768 | 1.3053 | 15602.375 | 17.5108 | 15602.3652
38960.5756 | 12 | 0 | 38960.5756 | 2350 | 0 |  | 3036 | 3161 | 0.7326 | 0 | 143.4676 | 0 | 0.007326 | 0 | 1.4347 | 0 | 0.007326 | 1.4347 | 20836.5 | 6.9098 | 20836.4927

## A1-C5
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 148.6801 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38960.5391 | 1 | 0 | 38960.5391 | 1 | 0 |  | -116.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5396 | 1 | 0 | 38960.5396 | 1 | 0 |  | -74.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5401 | 1 | 0 | 38960.5401 | 1 | 0 |  | -32.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5406 | 1 | 0 | 38960.5406 | 1 | 0 |  | 9.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5411 | 1 | 0 | 38960.5411 | 1 | 0 |  | 51.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5416 | 1 | 0 | 38960.5416 | 1 | 0 |  | 93.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.542 | 1 | 0 | 38960.5421 | 1 | 0 |  | 135.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5425 | 1 | 0 | 38960.5425 | 1 | 0 |  | 177.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.543 | 1 | 0 | 38960.543 | 1 | 0 |  | 219.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5435 | 1 | 0 | 38960.5435 | 1 | 0 |  | 261.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.544 | 1 | 0 | 38960.544 | 2 | 0 |  | 303.5 | 428.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243438 | 121669 | 243437.9994
38960.5445 | 1 | 0 | 38960.5445 | 1 | 0 |  | 345.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.545 | 1 | 0 | 38960.545 | 1 | 0 |  | 387.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5455 | 1 | 0 | 38960.5455 | 1 | 0 |  | 429.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5459 | 1 | 0 | 38960.5459 | 1 | 0 |  | 471.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5464 | 1 | 0 | 38960.5464 | 1 | 0 |  | 513.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5469 | 1 | 0 | 38960.5469 | 1 | 0 |  | 555.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5474 | 1 | 0 | 38960.5474 | 1 | 0 |  | 597.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5479 | 1 | 0 | 38960.5479 | 1 | 0 |  | 639.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5484 | 1 | 0 | 38960.5484 | 1 | 0 |  | 681.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5489 | 1 | 0 | 38960.5489 | 1 | 0 |  | 723.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5493 | 1 | 0 | 38960.5494 | 1 | 0 |  | 765.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5498 | 1 | 0 | 38960.5498 | 1 | 0 |  | 807.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5503 | 1 | 0 | 38960.5503 | 1 | 0 |  | 849.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5508 | 1 | 0 | 38960.5508 | 1 | 0 |  | 891.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5513 | 1 | 0 | 38960.5513 | 1 | 0 |  | 933.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5518 | 1 | 0 | 38960.5518 | 1 | 0 |  | 975.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5523 | 1 | 0 | 38960.5523 | 1 | 0 |  | 1017.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5527 | 1 | 0 | 38960.5528 | 1 | 0 |  | 1059.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5532 | 1 | 0 | 38960.5532 | 1 | 0 |  | 1101.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5537 | 1 | 0 | 38960.5537 | 1 | 0 |  | 1143.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5542 | 1 | 0 | 38960.5542 | 1 | 0 |  | 1185.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5547 | 1 | 0 | 38960.5547 | 1 | 0 |  | 1227.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5552 | 1 | 0 | 38960.5552 | 2 | 0 |  | 1269.5 | 1394.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243438 | 121669 | 243437.9994
38960.5557 | 1 | 0 | 38960.5557 | 1 | 0 |  | 1311.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5561 | 1 | 0 | 38960.5562 | 1 | 0 |  | 1353.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5566 | 1 | 0 | 38960.5566 | 1 | 0 |  | 1395.5 | 1520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5571 | 1 | 0 | 38960.5571 | 1 | 0 |  | 1437.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5576 | 1 | 0 | 38960.5576 | 1 | 0 |  | 1479.5 | 1604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5581 | 1 | 0 | 38960.5581 | 1 | 0 |  | 1521.5 | 1646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5586 | 1 | 0 | 38960.5586 | 1 | 0 |  | 1563.5 | 1688.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5591 | 1 | 0 | 38960.5591 | 1 | 0 |  | 1605.5 | 1730.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38960.5595 | 2 | 1 | 38960.5596 | 1 | 0 |  | 1647.5 | 1772.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243138.1232
38960.56 | 1 | 0 | 38960.56 | 2 | 0 |  | 1689.5 | 1814.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243438 | 121669 | 243437.9994
38960.5605 | 2 | 0 | 38960.5605 | 46 | 0 |  | 1731.5 | 1856.5 | 0.1221 | 0 | 2.8083 | 0 | 0.001221 | 0 | 0.028083 | 0 | 0.001221 | 0.028083 | 121669 | 5194.3043 | 121668.9988
38960.561 | 2 | 0 | 38960.561 | 1997 | 0 |  | 1773.5 | 1898.5 | 0.1221 | 0 | 121.917 | 0 | 0.001221 | 0 | 1.2192 | 0 | 0.001221 | 1.2192 | 121669 | 21.9519 | 121668.9988
38960.5615 | 2 | 0 | 38960.5615 | 1818 | 0 |  | 1815.5 | 1940.5 | 0.1221 | 0 | 110.989 | 0 | 0.001221 | 0 | 1.1099 | 0 | 0.001221 | 1.1099 | 121669 | 33.9593 | 121668.9988
38960.562 | 2 | 0 | 38960.562 | 2102 | 0 |  | 1857.5 | 1982.5 | 0.1221 | 0 | 128.3272 | 0 | 0.001221 | 0 | 1.2833 | 0 | 0.001221 | 1.2833 | 121669 | 15.8601 | 121668.9988
38960.5625 | 2 | 0 | 38960.5625 | 1909 | 0 |  | 1899.5 | 2024.5 | 0.1221 | 0 | 116.5446 | 0 | 0.001221 | 0 | 1.1654 | 0 | 0.001221 | 1.1654 | 121669 | 27.5736 | 121668.9988
38960.563 | 2 | 0 | 38960.563 | 2182 | 0 |  | 1941.5 | 2066.5 | 0.1221 | 0 | 133.2112 | 0 | 0.001221 | 0 | 1.3321 | 0 | 0.001221 | 1.3321 | 121669 | 11.6123 | 121668.9988
38960.5634 | 2 | 0 | 38960.5634 | 2199 | 0 |  | 1983.5 | 2108.5 | 0.1221 | 0 | 134.2491 | 0 | 0.001221 | 0 | 1.3425 | 0 | 0.001221 | 1.3425 | 121669 | 10.7494 | 121668.9988
38960.5639 | 2 | 0 | 38960.5639 | 2239 | 0 |  | 2025.5 | 2150.5 | 0.1221 | 0 | 136.6911 | 0 | 0.001221 | 0 | 1.3669 | 0 | 0.001221 | 1.3669 | 121669 | 8.7709 | 121668.9988
38960.5644 | 2 | 0 | 38960.5644 | 1880 | 0 |  | 2067.5 | 2192.5 | 0.1221 | 0 | 114.7741 | 0 | 0.001221 | 0 | 1.1477 | 0 | 0.001221 | 1.1477 | 121669 | 29.5415 | 121668.9988
38960.5649 | 2 | 0 | 38960.5649 | 1903 | 0 |  | 2109.5 | 2234.5 | 0.1221 | 0 | 116.1783 | 0 | 0.001221 | 0 | 1.1618 | 0 | 0.001221 | 1.1618 | 121669 | 27.9758 | 121668.9988
38960.5654 | 2 | 0 | 38960.5654 | 1852 | 0 |  | 2151.5 | 2276.5 | 0.1221 | 0 | 113.0647 | 0 | 0.001221 | 0 | 1.1306 | 0 | 0.001221 | 1.1306 | 121669 | 31.5 | 121668.9988
38960.5659 | 2 | 0 | 38960.5659 | 1863 | 0 |  | 2193.5 | 2318.5 | 0.1221 | 0 | 113.7363 | 0 | 0.001221 | 0 | 1.1374 | 0 | 0.001221 | 1.1374 | 121669 | 30.7236 | 121668.9988
38960.5664 | 2 | 0 | 38960.5664 | 2164 | 0 |  | 2235.5 | 2360.5 | 0.1221 | 0 | 132.1123 | 0 | 0.001221 | 0 | 1.3211 | 0 | 0.001221 | 1.3211 | 121669 | 12.5407 | 121668.9988
38960.5668 | 2 | 0 | 38960.5669 | 2323 | 0 |  | 2277.5 | 2402.5 | 0.1221 | 0 | 141.8193 | 0 | 0.001221 | 0 | 1.4182 | 0 | 0.001221 | 1.4182 | 121669 | 4.8377 | 121668.9988
38960.5673 | 3 | 1 | 38960.5673 | 1881 | 0 |  | 2319.5 | 2444.5 | 0.18315 | 0.06105 | 114.8352 | 0 | 0.0018315 | 0.0006105 | 1.1484 | 0 | 0.001221 | 1.1484 | 174617.0652 | 164.7391 | 151297.3897
38960.5678 | 2 | 0 | 38960.5678 | 2410 | 0 |  | 2361.5 | 2486.5 | 0.1221 | 0 | 147.1306 | 0 | 0.001221 | 0 | 1.4713 | 0 | 0.001221 | 1.4713 | 121669 | 1.0531 | 121668.9988
38960.5683 | 3 | 0 | 38960.5683 | 2152 | 0 |  | 2403.5 | 2528.5 | 0.18315 | 0 | 131.3797 | 0 | 0.0018315 | 0 | 1.3138 | 0 | 0.0018315 | 1.3138 | 81079.3333 | 13.1682 | 81079.3315
38960.5688 | 4 | 0 | 38960.5688 | 2234 | 0 |  | 2445 | 2570 | 0.2442 | 0 | 136.3858 | 0 | 0.002442 | 0 | 1.3639 | 0 | 0.002442 | 1.3639 | 60784.5 | 9.0143 | 60784.4976
38960.5693 | 4 | 0 | 38960.5693 | 1999 | 0 |  | 2487.5 | 2612.5 | 0.2442 | 0 | 122.0391 | 0 | 0.002442 | 0 | 1.2204 | 0 | 0.002442 | 1.2204 | 60784.5 | 21.8299 | 60784.4976
38960.5697 | 8 | 0 | 38960.5698 | 2058 | 0 |  | 2529 | 2654 | 0.4884 | 0 | 125.641 | 0 | 0.004884 | 0 | 1.2564 | 0 | 0.004884 | 1.2564 | 30342.25 | 18.3372 | 30342.2451
38960.5702 | 11 | 0 | 38960.5703 | 2117 | 0 |  | 2571 | 2696 | 0.67155 | 0 | 129.243 | 0 | 0.0067155 | 0 | 1.2924 | 0 | 0.0067155 | 1.2924 | 22039.8182 | 15.0392 | 22039.8115
38960.5707 | 17 | 0 | 38960.5707 | 2401 | 0 |  | 2613.5 | 2738.5 | 1.0379 | 0 | 146.5812 | 0 | 0.010379 | 0 | 1.4658 | 0 | 0.010379 | 1.4658 | 14225.7647 | 1.4319 | 14225.7543
38960.5712 | 28 | 0 | 38960.5712 | 1997 | 0 |  | 2655 | 2780 | 1.7094 | 0 | 121.917 | 0 | 0.017094 | 0 | 1.2192 | 0 | 0.017094 | 1.2192 | 8597.7857 | 21.9519 | 8597.7686
38960.5717 | 33 | 0 | 38960.5717 | 2336 | 0 |  | 2697 | 2822 | 2.0147 | 0 | 142.6129 | 0 | 0.020147 | 0 | 1.4261 | 0 | 0.020147 | 1.4261 | 7279.9394 | 4.2543 | 7279.9192
38960.5722 | 38 | 0 | 38960.5722 | 2154 | 0 |  | 2739 | 2864 | 2.3199 | 0 | 131.5018 | 0 | 0.023199 | 0 | 1.315 | 0 | 0.023199 | 1.315 | 6308.8947 | 13.0631 | 6308.8715
38960.5727 | 38 | 0 | 38960.5727 | 2077 | 0 |  | 2781 | 2906 | 2.3199 | 0 | 126.801 | 0 | 0.023199 | 0 | 1.268 | 0 | 0.023199 | 1.268 | 6308.8947 | 17.2547 | 6308.8715
38960.5731 | 44 | 0 | 38960.5732 | 2259 | 0 |  | 2823 | 2948 | 2.6862 | 0 | 137.9121 | 0 | 0.026862 | 0 | 1.3791 | 0 | 0.026862 | 1.3791 | 5434.9545 | 7.8079 | 5434.9277
38960.5736 | 38 | 0 | 38960.5737 | 2406 | 0 |  | 2865 | 2990 | 2.3199 | 0 | 146.8864 | 0 | 0.023199 | 0 | 1.4689 | 0 | 0.023199 | 1.4689 | 6308.8947 | 1.2211 | 6308.8715
38960.5741 | 27 | 0 | 38960.5741 | 1914 | 0 |  | 2907.5 | 3032.5 | 1.6484 | 0 | 116.8498 | 0 | 0.016484 | 0 | 1.1685 | 0 | 0.016484 | 1.1685 | 8919.9259 | 27.2403 | 8919.9094
38960.5746 | 26 | 0 | 38960.5746 | 2061 | 0 |  | 2949 | 3074 | 1.5873 | 0 | 125.8242 | 0 | 0.015873 | 0 | 1.2582 | 0 | 0.015873 | 1.2582 | 9266.8462 | 18.165 | 9266.8303
38960.5751 | 15 | 0 | 38960.5751 | 1906 | 0 |  | 2991 | 3116 | 0.91575 | 0 | 116.3614 | 0 | 0.0091575 | 0 | 1.1636 | 0 | 0.0091575 | 1.1636 | 16135.8667 | 27.7744 | 16135.8575
38960.5756 | 12 | 0 | 38960.5756 | 2419 | 0 |  | 3033 | 3158 | 0.7326 | 0 | 147.6801 | 0 | 0.007326 | 0 | 1.4768 | 0 | 0.007326 | 1.4768 | 20194.8333 | 0.67714 | 20194.826

## A1-B4
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 155.3956 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38960.5391 | 1 | 0 | 38960.5391 | 1 | 0 |  | -119.5 | 5.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5396 | 1 | 0 | 38960.5396 | 1 | 0 |  | -77.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5401 | 1 | 0 | 38960.5401 | 1 | 0 |  | -35 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5406 | 1 | 0 | 38960.5406 | 1 | 0 |  | 7 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.541 | 1 | 0 | 38960.5411 | 1 | 0 |  | 48.5 | 173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5415 | 1 | 0 | 38960.5415 | 1 | 0 |  | 90.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.542 | 1 | 0 | 38960.542 | 1 | 0 |  | 133 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5425 | 1 | 0 | 38960.5425 | 1 | 0 |  | 174.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.543 | 1 | 0 | 38960.543 | 1 | 0 |  | 216.5 | 341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5435 | 1 | 0 | 38960.5435 | 1 | 0 |  | 258.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.544 | 1 | 0 | 38960.544 | 1 | 0 |  | 300.5 | 425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5444 | 1 | 0 | 38960.5445 | 2 | 0 |  | 342.5 | 467.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 254438 | 127169 | 254437.9994
38960.5449 | 1 | 0 | 38960.5449 | 1 | 0 |  | 384.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5454 | 1 | 0 | 38960.5454 | 1 | 0 |  | 426.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5459 | 1 | 0 | 38960.5459 | 1 | 0 |  | 468.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5464 | 1 | 0 | 38960.5464 | 1 | 0 |  | 510.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5469 | 1 | 0 | 38960.5469 | 1 | 0 |  | 552.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5474 | 1 | 0 | 38960.5474 | 1 | 0 |  | 594.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5478 | 1 | 0 | 38960.5479 | 1 | 0 |  | 636.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5483 | 1 | 0 | 38960.5483 | 1 | 0 |  | 678.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5488 | 1 | 0 | 38960.5488 | 1 | 0 |  | 720.5 | 845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5493 | 1 | 0 | 38960.5493 | 1 | 0 |  | 762.5 | 887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5498 | 1 | 0 | 38960.5498 | 1 | 0 |  | 804.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5503 | 1 | 0 | 38960.5503 | 1 | 0 |  | 846.5 | 971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5508 | 1 | 0 | 38960.5508 | 1 | 0 |  | 888.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5512 | 1 | 0 | 38960.5513 | 1 | 0 |  | 930.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5517 | 1 | 0 | 38960.5517 | 1 | 0 |  | 972.5 | 1097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5522 | 1 | 0 | 38960.5522 | 1 | 0 |  | 1014.5 | 1139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5527 | 1 | 0 | 38960.5527 | 1 | 0 |  | 1056.5 | 1181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5532 | 1 | 0 | 38960.5532 | 1 | 0 |  | 1098.5 | 1223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5537 | 1 | 0 | 38960.5537 | 1 | 0 |  | 1140.5 | 1265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5542 | 1 | 0 | 38960.5542 | 1 | 0 |  | 1182.5 | 1307.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5547 | 1 | 0 | 38960.5547 | 1 | 0 |  | 1224.5 | 1349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5551 | 1 | 0 | 38960.5552 | 1 | 0 |  | 1266.5 | 1391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5556 | 1 | 0 | 38960.5556 | 1 | 0 |  | 1308.5 | 1433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5561 | 1 | 0 | 38960.5561 | 1 | 0 |  | 1350.5 | 1475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5566 | 1 | 0 | 38960.5566 | 1 | 0 |  | 1392.5 | 1517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5571 | 1 | 0 | 38960.5571 | 1 | 0 |  | 1434.5 | 1559.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5576 | 1 | 0 | 38960.5576 | 1 | 0 |  | 1476.5 | 1601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5581 | 1 | 0 | 38960.5581 | 1 | 0 |  | 1518.5 | 1643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5585 | 1 | 0 | 38960.5586 | 1 | 0 |  | 1560.5 | 1685.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.559 | 1 | 0 | 38960.559 | 1 | 0 |  | 1602.5 | 1727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38960.5595 | 1 | 1 | 38960.5595 | 1 | 0 |  | 1644.5 | 1769.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 647386958.44 | 254438 | 254238.0786
38960.56 | 2 | 0 | 38960.56 | 1897 | 0 |  | 1686.5 | 1811.5 | 0.1221 | 0 | 115.812 | 0 | 0.001221 | 0 | 1.1581 | 0 | 0.001221 | 1.1581 | 127169 | 34.1792 | 127168.9988
38960.5605 | 2 | 0 | 38960.5605 | 2062 | 0 |  | 1728.5 | 1853.5 | 0.1221 | 0 | 125.8852 | 0 | 0.001221 | 0 | 1.2589 | 0 | 0.001221 | 1.2589 | 127169 | 23.4423 | 127168.9988
38960.561 | 2 | 0 | 38960.561 | 2420 | 0 |  | 1770.5 | 1895.5 | 0.1221 | 0 | 147.7411 | 0 | 0.001221 | 0 | 1.4774 | 0 | 0.001221 | 1.4774 | 127169 | 5.181 | 127168.9988
38960.5615 | 2 | 0 | 38960.5615 | 2497 | 0 |  | 1812.5 | 1937.5 | 0.1221 | 0 | 152.442 | 0 | 0.001221 | 0 | 1.5244 | 0 | 0.001221 | 1.5244 | 127169 | 1.9375 | 127168.9988
38960.5619 | 2 | 0 | 38960.562 | 2529 | 0 |  | 1854.5 | 1979.5 | 0.1221 | 0 | 154.3956 | 0 | 0.001221 | 0 | 1.544 | 0 | 0.001221 | 1.544 | 127169 | 0.64769 | 127168.9988
38960.5624 | 2 | 1 | 38960.5624 | 2401 | 0 |  | 1896.5 | 2021.5 | 0.1221 | 0.06105 | 146.5812 | 0 | 0.001221 | 0.0006105 | 1.4658 | 0 | 0.0006105 | 1.4658 | 16272.7089 | 6.8354 | 16266.3109
38960.5629 | 2 | 0 | 38960.5629 | 2211 | 0 |  | 1938.5 | 2063.5 | 0.1221 | 0 | 134.9817 | 0 | 0.001221 | 0 | 1.3498 | 0 | 0.001221 | 1.3498 | 127169 | 15.1235 | 127168.9988
38960.5634 | 2 | 0 | 38960.5634 | 1889 | 0 |  | 1980.5 | 2105.5 | 0.1221 | 0 | 115.3236 | 0 | 0.001221 | 0 | 1.1532 | 0 | 0.001221 | 1.1532 | 127169 | 34.7475 | 127168.9988
38960.5639 | 2 | 0 | 38960.5639 | 2044 | 0 |  | 2022.5 | 2147.5 | 0.1221 | 0 | 124.7863 | 0 | 0.001221 | 0 | 1.2479 | 0 | 0.001221 | 1.2479 | 127169 | 24.5294 | 127168.9988
38960.5644 | 2 | 0 | 38960.5644 | 2179 | 0 |  | 2064.5 | 2189.5 | 0.1221 | 0 | 133.0281 | 0 | 0.001221 | 0 | 1.3303 | 0 | 0.001221 | 1.3303 | 127169 | 16.8141 | 127168.9988
38960.5649 | 2 | 0 | 38960.5649 | 2435 | 0 |  | 2106.5 | 2231.5 | 0.1221 | 0 | 148.6569 | 0 | 0.001221 | 0 | 1.4866 | 0 | 0.001221 | 1.4866 | 127169 | 4.5331 | 127168.9988
38960.5653 | 2 | 0 | 38960.5654 | 2209 | 0 |  | 2148.5 | 2273.5 | 0.1221 | 0 | 134.8596 | 0 | 0.001221 | 0 | 1.3486 | 0 | 0.001221 | 1.3486 | 127169 | 15.2277 | 127168.9988
38960.5658 | 2 | 0 | 38960.5658 | 2203 | 0 |  | 2190.5 | 2315.5 | 0.1221 | 0 | 134.4933 | 0 | 0.001221 | 0 | 1.3449 | 0 | 0.001221 | 1.3449 | 127169 | 15.5415 | 127168.9988
38960.5663 | 3 | 0 | 38960.5663 | 2284 | 0 |  | 2232.5 | 2357.5 | 0.18315 | 0 | 139.4383 | 0 | 0.0018315 | 0 | 1.3944 | 0 | 0.0018315 | 1.3944 | 84746 | 11.444 | 84745.9982
38960.5668 | 3 | 0 | 38960.5668 | 1974 | 0 |  | 2274.5 | 2399.5 | 0.18315 | 0 | 120.5128 | 0 | 0.0018315 | 0 | 1.2051 | 0 | 0.0018315 | 1.2051 | 84746 | 28.9453 | 84745.9982
38960.5673 | 2 | 0 | 38960.5673 | 2139 | 0 |  | 2316.5 | 2441.5 | 0.1221 | 0 | 130.5861 | 0 | 0.001221 | 0 | 1.3059 | 0 | 0.001221 | 1.3059 | 127169 | 18.9986 | 127168.9988
38960.5678 | 3 | 0 | 38960.5678 | 1983 | 0 |  | 2358.5 | 2483.5 | 0.18315 | 0 | 121.0623 | 0 | 0.0018315 | 0 | 1.2106 | 0 | 0.0018315 | 1.2106 | 84746 | 28.3601 | 84745.9982
38960.5683 | 3 | 0 | 38960.5683 | 1963 | 0 |  | 2400.5 | 2525.5 | 0.18315 | 0 | 119.8413 | 0 | 0.0018315 | 0 | 1.1984 | 0 | 0.0018315 | 1.1984 | 84746 | 29.6679 | 84745.9982
38960.5687 | 3 | 0 | 38960.5688 | 2252 | 0 |  | 2442.5 | 2567.5 | 0.18315 | 0 | 137.4847 | 0 | 0.0018315 | 0 | 1.3748 | 0 | 0.0018315 | 1.3748 | 84746 | 13.0275 | 84745.9982
38960.5692 | 5 | 0 | 38960.5692 | 2027 | 0 |  | 2484.5 | 2609.5 | 0.30525 | 0 | 123.7485 | 0 | 0.0030525 | 0 | 1.2375 | 0 | 0.0030525 | 1.2375 | 50807.6 | 25.5738 | 50807.5969
38960.5697 | 7 | 0 | 38960.5697 | 1969 | 0 |  | 2526.5 | 2651.5 | 0.42735 | 0 | 120.2076 | 0 | 0.0042735 | 0 | 1.2021 | 0 | 0.0042735 | 1.2021 | 36262.5714 | 29.2727 | 36262.5672
38960.5702 | 10 | 0 | 38960.5702 | 2426 | 0 |  | 2568.5 | 2693.5 | 0.6105 | 0 | 148.1074 | 0 | 0.006105 | 0 | 1.4811 | 0 | 0.006105 | 1.4811 | 25353.8 | 4.9209 | 25353.7939
38960.5707 | 15 | 0 | 38960.5707 | 2501 | 0 |  | 2610.5 | 2735.5 | 0.91575 | 0 | 152.6862 | 0 | 0.0091575 | 0 | 1.5269 | 0 | 0.0091575 | 1.5269 | 16869.2 | 1.7745 | 16869.1908
38960.5712 | 25 | 0 | 38960.5712 | 2014 | 0 |  | 2652.5 | 2777.5 | 1.5263 | 0 | 122.9548 | 0 | 0.015263 | 0 | 1.2295 | 0 | 0.015263 | 1.2295 | 10081.52 | 26.3843 | 10081.5047
38960.5717 | 35 | 0 | 38960.5717 | 1946 | 0 |  | 2694.5 | 2819.5 | 2.1368 | 0 | 118.8034 | 0 | 0.021368 | 0 | 1.188 | 0 | 0.021368 | 1.188 | 7172.5143 | 30.8006 | 7172.4929
38960.5722 | 43 | 0 | 38960.5722 | 2130 | 0 |  | 2736.5 | 2861.5 | 2.6252 | 0 | 130.0366 | 0 | 0.026252 | 0 | 1.3004 | 0 | 0.026252 | 1.3004 | 5819.4884 | 19.5014 | 5819.4621
38960.5726 | 45 | 0 | 38960.5727 | 1941 | 0 |  | 2778.5 | 2903.5 | 2.7473 | 0 | 118.4982 | 0 | 0.027473 | 0 | 1.185 | 0 | 0.027473 | 1.185 | 5556.4 | 31.1376 | 5556.3725
38960.5731 | 38 | 0 | 38960.5731 | 1960 | 0 |  | 2820.5 | 2945.5 | 2.3199 | 0 | 119.6581 | 0 | 0.023199 | 0 | 1.1966 | 0 | 0.023199 | 1.1966 | 6598.3684 | 29.8663 | 6598.3452
38960.5736 | 31 | 0 | 38960.5736 | 2028 | 0 |  | 2862.5 | 2987.5 | 1.8926 | 0 | 123.8095 | 0 | 0.018926 | 0 | 1.2381 | 0 | 0.018926 | 1.2381 | 8110.9032 | 25.5118 | 8110.8843
38960.5741 | 29 | 0 | 38960.5741 | 2346 | 0 |  | 2904.5 | 3029.5 | 1.7705 | 0 | 143.2234 | 0 | 0.017705 | 0 | 1.4322 | 0 | 0.017705 | 1.4322 | 8677.1724 | 8.4987 | 8677.1547
38960.5746 | 21 | 0 | 38960.5746 | 2186 | 0 |  | 2946.5 | 3071.5 | 1.2821 | 0 | 133.4554 | 0 | 0.012821 | 0 | 1.3346 | 0 | 0.012821 | 1.3346 | 12020.8571 | 16.4401 | 12020.8443
38960.5751 | 15 | 0 | 38960.5751 | 2054 | 0 |  | 2988.5 | 3113.5 | 0.91575 | 0 | 125.3968 | 0 | 0.0091575 | 0 | 1.254 | 0 | 0.0091575 | 1.254 | 16869.2 | 23.9231 | 16869.1908
38960.5756 | 10 | 0 | 38960.5756 | 2078 | 0 |  | 3030.5 | 3155.5 | 0.6105 | 0 | 126.862 | 0 | 0.006105 | 0 | 1.2686 | 0 | 0.006105 | 1.2686 | 25353.8 | 22.4918 | 25353.7939

## A1-B3
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 154.1136 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38960.5391 | 1 | 0 | 38960.5391 | 1 | 0 |  | -122 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5395 | 1 | 0 | 38960.5396 | 1 | 0 |  | -80 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.54 | 1 | 0 | 38960.5401 | 1 | 0 |  | -38 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5405 | 1 | 0 | 38960.5405 | 1 | 0 |  | 4 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.541 | 1 | 0 | 38960.541 | 1 | 0 |  | 46 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5415 | 1 | 0 | 38960.5415 | 1 | 0 |  | 88 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.542 | 1 | 0 | 38960.542 | 1 | 0 |  | 130 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5425 | 1 | 0 | 38960.5425 | 1 | 0 |  | 172 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.543 | 1 | 0 | 38960.543 | 1 | 0 |  | 214 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5434 | 1 | 0 | 38960.5435 | 1 | 0 |  | 256 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5439 | 1 | 0 | 38960.5439 | 1 | 0 |  | 298 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5444 | 1 | 0 | 38960.5444 | 1 | 0 |  | 340 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5449 | 1 | 0 | 38960.5449 | 1 | 0 |  | 382 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5454 | 2 | 0 | 38960.5454 | 1 | 0 |  | 424 | 549 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126119 | 252338 | 126118.9988
38960.5459 | 1 | 0 | 38960.5459 | 1 | 0 |  | 466 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5464 | 1 | 1 | 38960.5464 | 1 | 0 |  | 508 | 633 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 636744662.44 | 252338 | 252138.0792
38960.5468 | 1 | 0 | 38960.5469 | 1 | 0 |  | 550 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5473 | 1 | 0 | 38960.5473 | 1 | 0 |  | 592 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5478 | 1 | 0 | 38960.5478 | 1 | 0 |  | 634 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5483 | 1 | 0 | 38960.5483 | 1 | 0 |  | 676 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5488 | 1 | 0 | 38960.5488 | 1 | 0 |  | 718 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5493 | 1 | 0 | 38960.5493 | 1 | 0 |  | 760 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5498 | 1 | 0 | 38960.5498 | 1 | 0 |  | 802 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5502 | 1 | 0 | 38960.5503 | 1 | 0 |  | 844 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5507 | 1 | 0 | 38960.5508 | 1 | 0 |  | 886 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5512 | 1 | 0 | 38960.5512 | 1 | 0 |  | 928 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5517 | 1 | 0 | 38960.5517 | 1 | 0 |  | 969.5 | 1094.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5522 | 1 | 0 | 38960.5522 | 1 | 0 |  | 1012 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5527 | 1 | 0 | 38960.5527 | 1 | 0 |  | 1053.5 | 1178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5532 | 1 | 0 | 38960.5532 | 1 | 0 |  | 1095.5 | 1220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5536 | 1 | 0 | 38960.5537 | 1 | 0 |  | 1138 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5541 | 1 | 0 | 38960.5541 | 1 | 0 |  | 1179.5 | 1304.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5546 | 1 | 0 | 38960.5546 | 1 | 0 |  | 1221.5 | 1346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5551 | 1 | 0 | 38960.5551 | 1 | 0 |  | 1263.5 | 1388.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5556 | 1 | 0 | 38960.5556 | 1 | 0 |  | 1306 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5561 | 2 | 0 | 38960.5561 | 1 | 0 |  | 1347.5 | 1472.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126119 | 252338 | 126118.9988
38960.5566 | 1 | 0 | 38960.5566 | 1 | 0 |  | 1389.5 | 1514.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.557 | 1 | 0 | 38960.5571 | 1 | 0 |  | 1431.5 | 1556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5575 | 1 | 0 | 38960.5575 | 1 | 0 |  | 1473.5 | 1598.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.558 | 1 | 0 | 38960.558 | 1 | 0 |  | 1515.5 | 1640.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5585 | 1 | 0 | 38960.5585 | 1 | 0 |  | 1557.5 | 1682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.559 | 1 | 0 | 38960.559 | 1 | 0 |  | 1599.5 | 1724.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.5595 | 1 | 0 | 38960.5595 | 1 | 0 |  | 1641.5 | 1766.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38960.56 | 1 | 0 | 38960.56 | 1930 | 0 |  | 1683.5 | 1808.5 | 0.06105 | 0 | 117.8266 | 0 | 0.0006105 | 0 | 1.1783 | 0 | 0.0006105 | 1.1783 | 252338 | 30.7969 | 252337.9994
38960.5605 | 1 | 1 | 38960.5605 | 2123 | 0 |  | 1725.5 | 1850.5 | 0.06105 | 0.06105 | 129.6093 | 0 | 0.0006105 | 0.0006105 | 1.2961 | 0 | 0 | 1.2961 | 47707.6903 | 18.9063 | 40106.1997
38960.5609 | 1 | 1 | 38960.5609 | 2406 | 0 |  | 1767.5 | 1892.5 | 0.06105 | 0.06105 | 146.8864 | 0 | 0.0006105 | 0.0006105 | 1.4689 | 0 | 0 | 1.4689 | 12415.533 | 4.9202 | 11828.6211
38960.5614 | 2 | 1 | 38960.5614 | 1434 | 0 |  | 1809.5 | 1934.5 | 0.1221 | 0.06105 | 87.5458 | 0 | 0.001221 | 0.0006105 | 0.87546 | 0 | 0.0006105 | 0.87546 | 800405.3036 | 146.0148 | 149649.0373
38960.5619 | 2 | 1 | 38960.5619 | 2508 | 1 |  | 1851.5 | 1976.5 | 0.1221 | 0.06105 | 153.1136 | 0.06105 | 0.001221 | 0.0006105 | 1.5311 | 0.0006105 | 0.0006105 | 1.5305 | 1658.8474 | 0.66201 | 1658.1897
38960.5624 | 2 | 1 | 38960.5624 | 2380 | 0 |  | 1893.5 | 2018.5 | 0.1221 | 0.06105 | 145.2991 | 0 | 0.001221 | 0.0006105 | 1.453 | 0 | 0.0006105 | 1.453 | 16289.943 | 6.904 | 16283.4849
38960.5629 | 2 | 1 | 38960.5629 | 2106 | 1 |  | 1935.5 | 2060.5 | 0.1221 | 0.06105 | 128.5714 | 0.06105 | 0.001221 | 0.0006105 | 1.2857 | 0.0006105 | 0.0006105 | 1.2851 | 62569.6567 | 32.989 | 62544.8509
38960.5634 | 2 | 1 | 38960.5634 | 1807 | 0 |  | 1977.5 | 2102.5 | 0.1221 | 0.06105 | 110.3175 | 0 | 0.001221 | 0.0006105 | 1.1032 | 0 | 0.0006105 | 1.1032 | 166067.5249 | 192.7198 | 166001.6872
38960.5639 | 2 | 1 | 38960.5639 | 1994 | 0 |  | 2019.5 | 2144.5 | 0.1221 | 0.06105 | 121.7338 | 0 | 0.001221 | 0.0006105 | 1.2173 | 0 | 0.0006105 | 1.2173 | 91404.8663 | 56.8321 | 91368.6288
38960.5643 | 2 | 1 | 38960.5644 | 2097 | 1 |  | 2061.5 | 2186.5 | 0.1221 | 0.06105 | 128.022 | 0.06105 | 0.001221 | 0.0006105 | 1.2802 | 0.0006105 | 0.0006105 | 1.2796 | 64605.1087 | 34.4317 | 64579.4959
38960.5648 | 2 | 1 | 38960.5648 | 2045 | 0 |  | 2103.5 | 2228.5 | 0.1221 | 0.06105 | 124.8474 | 0 | 0.001221 | 0.0006105 | 1.2485 | 0 | 0.0006105 | 1.2485 | 77233.2063 | 44.1321 | 77202.5871
38960.5653 | 2 | 1 | 38960.5653 | 1962 | 1 |  | 2145.5 | 2270.5 | 0.1221 | 0.06105 | 119.7802 | 0.06105 | 0.001221 | 0.0006105 | 1.1978 | 0.0006105 | 0.0006105 | 1.1972 | 101423.9082 | 67.2509 | 101383.6986
38960.5658 | 2 | 1 | 38960.5658 | 2102 | 1 |  | 2187.5 | 2312.5 | 0.1221 | 0.06105 | 128.3272 | 0.06105 | 0.001221 | 0.0006105 | 1.2833 | 0.0006105 | 0.0006105 | 1.2827 | 63468.9128 | 33.6225 | 63443.7505
38960.5663 | 2 | 1 | 38960.5663 | 2424 | 0 |  | 2229.5 | 2354.5 | 0.1221 | 0.06105 | 147.9853 | 0 | 0.001221 | 0.0006105 | 1.4799 | 0 | 0.0006105 | 1.4799 | 10896.6399 | 4.515 | 10892.3199
38960.5668 | 2 | 1 | 38960.5668 | 1919 | 0 |  | 2271.5 | 2396.5 | 0.1221 | 0.06105 | 117.1551 | 0 | 0.001221 | 0.0006105 | 1.1716 | 0 | 0.0006105 | 1.1716 | 116243.5411 | 85.4767 | 116197.4562
38960.5673 | 2 | 1 | 38960.5673 | 2098 | 0 |  | 2313.5 | 2438.5 | 0.1221 | 0.06105 | 128.083 | 0 | 0.001221 | 0.0006105 | 1.2808 | 0 | 0.0006105 | 1.2808 | 64338.3295 | 34.2408 | 64312.8226
38960.5677 | 2 | 1 | 38960.5678 | 1989 | 0 |  | 2355.5 | 2480.5 | 0.1221 | 0.06105 | 121.4286 | 0 | 0.001221 | 0.0006105 | 1.2143 | 0 | 0.0006105 | 1.2143 | 92901.295 | 58.305 | 92864.4642
38960.5682 | 3 | 1 | 38960.5682 | 2471 | 0 |  | 2397.5 | 2522.5 | 0.18315 | 0.06105 | 150.8547 | 0 | 0.0018315 | 0.0006105 | 1.5085 | 0 | 0.001221 | 1.5085 | 5692.792 | 2.3646 | 5821.9833
38960.5687 | 4 | 1 | 38960.5687 | 2035 | 0 |  | 2439.5 | 2564.5 | 0.2442 | 0.06105 | 124.2369 | 0 | 0.002442 | 0.0006105 | 1.2424 | 0 | 0.0018315 | 1.2424 | 217588.7458 | 54.2983 | 88658.2043
38960.5692 | 5 | 1 | 38960.5692 | 2230 | 0 |  | 2481.5 | 2606.5 | 0.30525 | 0.06105 | 136.1416 | 0 | 0.0030525 | 0.0006105 | 1.3614 | 0 | 0.002442 | 1.3614 | 70467.3803 | 235.4287 | 176758.5486
38960.5697 | 7 | 1 | 38960.5697 | 2297 | 0 |  | 2523.5 | 2648.5 | 0.42735 | 0.06105 | 140.232 | 0 | 0.0042735 | 0.0006105 | 1.4023 | 0 | 0.003663 | 1.4023 | 61369.0995 | 52.6879 | 86832.5621
38960.5702 | 10 | 1 | 38960.5702 | 2042 | 0 |  | 2565.5 | 2690.5 | 0.6105 | 0.06105 | 124.6642 | 0 | 0.006105 | 0.0006105 | 1.2466 | 0 | 0.0054945 | 1.2466 | 52747.5026 | 23.6229 | 48027.8026
38960.5707 | 15 | 0 | 38960.5707 | 2238 | 0 |  | 2607.5 | 2732.5 | 0.91575 | 0 | 136.63 | 0 | 0.0091575 | 0 | 1.3663 | 0 | 0.0091575 | 1.3663 | 16729.2 | 12.7962 | 16729.1908
38960.5711 | 22 | 1 | 38960.5712 | 1931 | 0 |  | 2649.5 | 2774.5 | 1.3431 | 0.06105 | 117.8877 | 0 | 0.013431 | 0.0006105 | 1.1789 | 0 | 0.012821 | 1.1789 | 14101.2827 | 30.7292 | 58797.3627
38960.5716 | 30 | 1 | 38960.5716 | 2269 | 0 |  | 2691.5 | 2816.5 | 1.8315 | 0.06105 | 138.5226 | 0 | 0.018315 | 0.0006105 | 1.3852 | 0 | 0.017705 | 1.3852 | 12400.4727 | 11.2552 | 25224.3872
38960.5721 | 41 | 1 | 38960.5721 | 2332 | 1 |  | 2733.5 | 2858.5 | 2.5031 | 0.06105 | 142.3687 | 0.06105 | 0.025031 | 0.0006105 | 1.4237 | 0.0006105 | 0.02442 | 1.4231 | 8906.2981 | 8.2532 | 18925.5043
38960.5726 | 43 | 1 | 38960.5726 | 2403 | 0 |  | 2775.5 | 2900.5 | 2.6252 | 0.06105 | 146.7033 | 0 | 0.026252 | 0.0006105 | 1.467 | 0 | 0.025641 | 1.467 | 11176.0436 | 5.0512 | 11926.4344
38960.5731 | 41 | 1 | 38960.5731 | 2458 | 0 |  | 2817.5 | 2942.5 | 2.5031 | 0.06105 | 150.0611 | 0 | 0.025031 | 0.0006105 | 1.5006 | 0 | 0.02442 | 1.5006 | 83593.6939 | 2.7006 | 6527.5586
38960.5736 | 36 | 0 | 38960.5736 | 2427 | 0 |  | 2859.5 | 2984.5 | 2.1978 | 0 | 148.1685 | 0 | 0.021978 | 0 | 1.4817 | 0 | 0.021978 | 1.4817 | 6912.1667 | 4.0124 | 6912.1447
38960.5741 | 33 | 1 | 38960.5741 | 2444 | 0 |  | 2901.5 | 3026.5 | 2.0147 | 0.06105 | 149.2063 | 0 | 0.020147 | 0.0006105 | 1.4921 | 0 | 0.019536 | 1.4921 | 156255.559 | 3.2889 | 7929.739
38960.5745 | 21 | 1 | 38960.5746 | 2442 | 0 |  | 2943.5 | 3068.5 | 1.2821 | 0.06105 | 149.0842 | 0 | 0.012821 | 0.0006105 | 1.4908 | 0 | 0.01221 | 1.4908 | 25960.2775 | 9.6554 | 22034.0392
38960.575 | 18 | 1 | 38960.575 | 2426 | 0 |  | 2985.5 | 3110.5 | 1.0989 | 0.06105 | 148.1074 | 0 | 0.010989 | 0.0006105 | 1.4811 | 0 | 0.010379 | 1.4811 | 32722.5714 | 10.706 | 24228.7707
38960.5755 | 13 | 0 | 38960.5755 | 1934 | 0 |  | 3027.5 | 3152.5 | 0.79365 | 0 | 118.0708 | 0 | 0.0079365 | 0 | 1.1807 | 0 | 0.0079365 | 1.1807 | 19318.3077 | 30.5264 | 19318.2998

## A1-A2
Penlight Test 49 |  |  | 2006-08-31 | 12:58 |  |  | Vs = |  | 129 |  | R = | 100
TS & TP Mix | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38960.539 | 1 | 0 | 38960.5391 | 1 | 0 |  | -124.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5395 | 1 | 0 | 38960.5395 | 1 | 0 |  | -82.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.54 | 1 | 0 | 38960.54 | 2 | 0 |  | -41 | 84 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38960.5405 | 1 | 0 | 38960.5405 | 1 | 0 |  | 1 | 126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.541 | 1 | 0 | 38960.541 | 2 | 0 |  | 43 | 168 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38960.5415 | 1 | 0 | 38960.5415 | 1 | 0 |  | 85 | 210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.542 | 1 | 0 | 38960.542 | 1 | 0 |  | 127.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5424 | 1 | 0 | 38960.5425 | 1 | 0 |  | 169 | 294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5429 | 1 | 0 | 38960.5429 | 1 | 0 |  | 211 | 336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38960.5434 | 1 | 0 |  | 254 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5439 | 1 | 0 | 38960.5439 | 1 | 0 |  | 295 | 420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5444 | 1 | 0 | 38960.5444 | 1 | 0 |  | 337 | 462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5449 | 1 | 0 | 38960.5449 | 1 | 0 |  | 379 | 504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5453 | 1 | 0 | 38960.5454 | 1 | 0 |  | 421 | 546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5458 | 1 | 0 | 38960.5459 | 1 | 0 |  | 463 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5463 | 1 | 0 | 38960.5463 | 1 | 0 |  | 505 | 630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5468 | 1 | 0 | 38960.5468 | 2 | 0 |  | 547 | 672 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38960.5473 | 1 | 0 | 38960.5473 | 1 | 0 |  | 589 | 714 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5478 | 1 | 0 | 38960.5478 | 1 | 0 |  | 631 | 756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5483 | 1 | 0 | 38960.5483 | 1 | 0 |  | 673 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5488 | 1 | 0 | 38960.5488 | 1 | 0 |  | 715 | 840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5492 | 1 | 0 | 38960.5493 | 1 | 0 |  | 757 | 882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5497 | 1 | 0 | 38960.5497 | 1 | 0 |  | 799 | 924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5502 | 1 | 0 | 38960.5502 | 1 | 0 |  | 841 | 966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5507 | 1 | 0 | 38960.5507 | 1 | 0 |  | 883 | 1008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5512 | 1 | 0 | 38960.5512 | 1 | 0 |  | 925 | 1050 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5517 | 1 | 0 | 38960.5517 | 1 | 0 |  | 967 | 1092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5522 | 1 | 0 | 38960.5522 | 1 | 0 |  | 1009 | 1134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5526 | 1 | 0 | 38960.5527 | 1 | 0 |  | 1051 | 1176 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5531 | 1 | 0 | 38960.5531 | 1 | 0 |  | 1093 | 1218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5536 | 1 | 0 | 38960.5536 | 1 | 0 |  | 1135 | 1260 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5541 | 1 | 0 | 38960.5541 | 1 | 0 |  | 1177 | 1302 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5546 | 1 | 0 | 38960.5546 | 1 | 0 |  | 1219 | 1344 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5551 | 1 | 0 | 38960.5551 | 1 | 0 |  | 1261 | 1386 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5556 | 1 | 0 | 38960.5556 | 1 | 0 |  | 1303 | 1428 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.556 | 1 | 0 | 38960.5561 | 1 | 0 |  | 1345 | 1470 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5565 | 1 | 0 | 38960.5566 | 1 | 0 |  | 1387 | 1512 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.557 | 1 | 0 | 38960.557 | 1 | 0 |  | 1429 | 1554 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.5575 | 1 | 0 | 38960.5575 | 1 | 0 |  | 1471 | 1596 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38960.558 | 1 | 1 | 38960.558 | 1 | 0 |  | 1513 | 1638 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38960.5585 | 2 | 1 | 38960.5585 | 2 | 1 |  | 1555 | 1680 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38960.559 | 4 | 2 | 38960.559 | 6 | 3 |  | 1597 | 1722 | 0.2442 | 0.1221 | 0.3663 | 0.18315 | 0.002442 | 0.001221 | 0.003663 | 0.0018315 | 0.001221 | 0.0018315 | 105601.2139 | 70300.5717 | 105201.3549
38960.5594 | 45 | 39 | 38960.5595 | 51 | 41 |  | 1639 | 1764 | 2.7473 | 2.381 | 3.1136 | 2.5031 | 0.027473 | 0.02381 | 0.031136 | 0.025031 | 0.003663 | 0.006105 | 35575.5042 | 20860.6141 | 5177.7945
38960.5599 | 203 | 182 | 38960.56 | 853 | 919 |  | 1681 | 1806 | 12.3932 | 11.1111 | 52.0757 | 56.105 | 0.12393 | 0.11111 | 0.52076 | 0.56105 | 0.012821 | 0.040293 | 15499.31 | 2097.5616 | 906.2563
38960.5604 | 1053 | 945 | 38960.5604 | 1038 | 997 |  | 1723 | 1848 | 64.2857 | 57.6923 | 63.37 | 60.8669 | 0.64286 | 0.57692 | 0.6337 | 0.60867 | 0.065934 | 0.025031 | 255.1512 | 307.3692 | 9.1836
38960.5609 | 1059 | 1135 | 38960.5609 | 1015 | 973 |  | 1765 | 1890 | 64.652 | 69.2918 | 61.9658 | 59.4017 | 0.64652 | 0.69292 | 0.61966 | 0.59402 | 0.046398 | 0.025641 | 148.0736 | 178.5092 | 4.573
38960.5614 | 1222 | 1182 | 38960.5614 | 949 | 992 |  | 1807 | 1932 | 74.6032 | 72.1612 | 57.9365 | 60.5617 | 0.74603 | 0.72161 | 0.57937 | 0.60562 | 0.02442 | 0.026252 | 3174.034 | 9909.592 | 24.3717
38960.5619 | 1193 | 1192 | 38960.5619 | 1184 | 1194 |  | 1849 | 1974 | 72.8327 | 72.7717 | 72.2833 | 72.8938 | 0.72833 | 0.72772 | 0.72283 | 0.72894 | 0.0006105 | 0.006105 | 5172.7054 | 7101.1344 | 22.5003
38960.5624 | 990 | 1003 | 38960.5624 | 1085 | 938 |  | 1891 | 2016 | 60.4396 | 61.2332 | 66.2393 | 57.265 | 0.6044 | 0.61233 | 0.66239 | 0.57265 | 0.0079365 | 0.089744 | 159.3662 | 145.0095 | 7.0822
38960.5628 | 1118 | 1158 | 38960.5629 | 1135 | 1080 |  | 1933 | 2058 | 68.254 | 70.696 | 69.2918 | 65.9341 | 0.68254 | 0.70696 | 0.69292 | 0.65934 | 0.02442 | 0.033578 | 1129.4244 | 2407.4972 | 13.513
38960.5633 | 1079 | 1028 | 38960.5634 | 1135 | 1083 |  | 1975 | 2100 | 65.873 | 62.7595 | 69.2918 | 66.1172 | 0.65873 | 0.62759 | 0.69292 | 0.66117 | 0.031136 | 0.031746 | 2852.4554 | 6969.5729 | 0.57732
38960.5638 | 998 | 949 | 38960.5638 | 1011 | 1027 |  | 2017 | 2142 | 60.928 | 57.9365 | 61.7216 | 62.6984 | 0.60928 | 0.57937 | 0.61722 | 0.62698 | 0.029915 | 0.009768 | 654.7764 | 782.4211 | 15.5117
38960.5643 | 1172 | 922 | 38960.5643 | 1179 | 1123 |  | 2059 | 2184 | 71.5507 | 56.2882 | 71.978 | 68.5592 | 0.71551 | 0.56288 | 0.71978 | 0.68559 | 0.15263 | 0.034188 | 86.035 | 109.2723 | 1.0772
38960.5648 | 1067 | 937 | 38960.5648 | 1004 | 952 |  | 2101 | 2226 | 65.1404 | 57.2039 | 61.2943 | 58.1197 | 0.6514 | 0.57204 | 0.61294 | 0.5812 | 0.079365 | 0.031746 | 280.8141 | 386.3988 | 9.2429
38960.5653 | 1211 | 1145 | 38960.5653 | 970 | 917 |  | 2143 | 2268 | 73.9316 | 69.9023 | 59.2186 | 55.9829 | 0.73932 | 0.69902 | 0.59219 | 0.55983 | 0.040293 | 0.032357 | 128.3563 | 179.8203 | 13.6372
38960.5658 | 1205 | 1164 | 38960.5658 | 1124 | 1064 |  | 2184.5 | 2309.5 | 73.5653 | 71.0623 | 68.6203 | 64.9573 | 0.73565 | 0.71062 | 0.6862 | 0.64957 | 0.025031 | 0.03663 | 1162.3215 | 3135.6709 | 21.3118
38960.5663 | 1009 | 950 | 38960.5663 | 983 | 928 |  | 2227 | 2352 | 61.5995 | 57.9976 | 60.0122 | 56.6545 | 0.616 | 0.57998 | 0.60012 | 0.56654 | 0.03602 | 0.033578 | 2537.6889 | 6130.9859 | 15.9524
38960.5667 | 1000 | 941 | 38960.5668 | 1038 | 1043 |  | 2269 | 2394 | 61.0501 | 57.4481 | 63.37 | 63.6752 | 0.6105 | 0.57448 | 0.6337 | 0.63675 | 0.03602 | 0.0030525 | 366.232 | 384.2209 | 14.5053
38960.5672 | 1215 | 1143 | 38960.5672 | 975 | 913 |  | 2311 | 2436 | 74.1758 | 69.7802 | 59.5238 | 55.7387 | 0.74176 | 0.6978 | 0.59524 | 0.55739 | 0.043956 | 0.037851 | 195.0449 | 294.2713 | 15.9969
38960.5677 | 1225 | 1154 | 38960.5677 | 1041 | 974 |  | 2353 | 2478 | 74.7863 | 70.4518 | 63.5531 | 59.4628 | 0.74786 | 0.70452 | 0.63553 | 0.59463 | 0.043346 | 0.040904 | 14280.5625 | 1781.3695 | 21.8234
38960.5682 | 1085 | 1013 | 38960.5682 | 1038 | 967 |  | 2395 | 2520 | 66.2393 | 61.8437 | 63.37 | 59.0354 | 0.66239 | 0.61844 | 0.6337 | 0.59035 | 0.043956 | 0.043346 | 2292.0952 | 3731.2151 | 1.444
38960.5687 | 1067 | 989 | 38960.5687 | 1183 | 1100 |  | 2437 | 2562 | 65.1404 | 60.3785 | 72.2222 | 67.1551 | 0.6514 | 0.60379 | 0.72222 | 0.67155 | 0.047619 | 0.050672 | 1205.6069 | 11286.162 | 5.7148
38960.5692 | 1083 | 999 | 38960.5692 | 1205 | 1116 |  | 2479 | 2604 | 66.1172 | 60.989 | 73.5653 | 68.1319 | 0.66117 | 0.60989 | 0.73565 | 0.68132 | 0.051282 | 0.054335 | 1421.2289 | 8667.2863 | 3.0697
38960.5697 | 1057 | 972 | 38960.5697 | 998 | 916 |  | 2521 | 2646 | 64.5299 | 59.3407 | 60.928 | 55.9219 | 0.6453 | 0.59341 | 0.60928 | 0.55922 | 0.051893 | 0.050061 | 1904.9767 | 3287.6489 | 8.3889
38960.5701 | 1107 | 1084 | 38960.5702 | 1202 | 1161 |  | 2562.5 | 2687.5 | 67.5824 | 66.1783 | 73.3822 | 70.8791 | 0.67582 | 0.66178 | 0.73382 | 0.70879 | 0.014042 | 0.025031 | 1455.9889 | 2351.6494 | 6.9003
38960.5706 | 1233 | 1127 | 38960.5706 | 1216 | 896 |  | 2605 | 2730 | 75.2747 | 68.8034 | 74.2369 | 54.7009 | 0.75275 | 0.68803 | 0.74237 | 0.54701 | 0.064713 | 0.19536 | 82.9944 | 118.0925 | 11.8664
38960.5711 | 1045 | 943 | 38960.5711 | 974 | 953 |  | 2646.5 | 2771.5 | 63.7973 | 57.5702 | 59.4628 | 58.1807 | 0.63797 | 0.5757 | 0.59463 | 0.58181 | 0.062271 | 0.012821 | 329.7644 | 425.0166 | 10.7325
38960.5716 | 1137 | 1022 | 38960.5716 | 1209 | 1087 |  | 2689 | 2814 | 69.4139 | 62.3932 | 73.8095 | 66.3614 | 0.69414 | 0.62393 | 0.7381 | 0.66361 | 0.070208 | 0.074481 | 1103.0581 | 3854.1453 | 4.3852
38960.5721 | 1254 | 1131 | 38960.5721 | 1149 | 1029 |  | 2730.5 | 2855.5 | 76.5568 | 69.0476 | 70.1465 | 62.8205 | 0.76557 | 0.69048 | 0.70147 | 0.62821 | 0.075092 | 0.07326 | 1957.8651 | 1429.3901 | 22.4754
38960.5726 | 1079 | 964 | 38960.5726 | 986 | 999 |  | 2772.5 | 2897.5 | 65.873 | 58.8523 | 60.1954 | 60.989 | 0.65873 | 0.58852 | 0.60195 | 0.60989 | 0.070208 | 0.0079365 | 172.8163 | 199.4477 | 4.8379
38960.5731 | 1011 | 902 | 38960.5731 | 1059 | 1069 |  | 2814.5 | 2939.5 | 61.7216 | 55.0672 | 64.652 | 65.2625 | 0.61722 | 0.55067 | 0.64652 | 0.65263 | 0.066545 | 0.006105 | 186.3762 | 187.0252 | 14.4493
38960.5735 | 1022 | 915 | 38960.5736 | 1087 | 973 |  | 2856.5 | 2981.5 | 62.3932 | 55.8608 | 66.3614 | 59.4017 | 0.62393 | 0.55861 | 0.66361 | 0.59402 | 0.065324 | 0.069597 | 4185.376 | 1130.5708 | 17.6739
38960.574 | 1252 | 1154 | 38960.574 | 1209 | 1088 |  | 2898.5 | 3023.5 | 76.4347 | 70.4518 | 73.8095 | 66.4225 | 0.76435 | 0.70452 | 0.7381 | 0.66422 | 0.059829 | 0.073871 | 934.8988 | 19551.6107 | 25.259
38960.5745 | 1153 | 1042 | 38960.5745 | 1222 | 1157 |  | 2940.5 | 3065.5 | 70.3907 | 63.6142 | 74.6032 | 70.6349 | 0.70391 | 0.63614 | 0.74603 | 0.70635 | 0.067766 | 0.039683 | 1123.3905 | 4079.4554 | 7.6793
38960.575 | 993 | 899 | 38960.575 | 1064 | 965 |  | 2982.5 | 3107.5 | 60.6227 | 54.884 | 64.9573 | 58.9133 | 0.60623 | 0.54884 | 0.64957 | 0.58913 | 0.057387 | 0.06044 | 3199.6692 | 1523.8384 | 23.0711
38960.5755 | 1028 | 938 | 38960.5755 | 1225 | 1121 |  | 3024.5 | 3149.5 | 62.7595 | 57.265 | 74.7863 | 68.4371 | 0.62759 | 0.57265 | 0.74786 | 0.68437 | 0.054945 | 0.063492 | 499.0218 | 736.094 | 13.7991

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -125 | 21.1 | 32.6 | 23.4 | 31.2 | 36.5 | 32.2 | 29.6 | 56.6 | 28 | 28.4
1 | -124 | 21.1 | 32.6 | 23.4 | 31.3 | 36.5 | 32.3 | 29.6 | 56.8 | 28 | 28.4
2 | -123 | 21.1 | 32.7 | 23.4 | 31.3 | 36.6 | 32.3 | 29.6 | 57 | 28 | 28.4
3 | -122 | 21.1 | 32.7 | 23.3 | 31.3 | 36.7 | 32.3 | 29.6 | 57.1 | 27.9 | 28.4
4 | -121 | 21.1 | 32.6 | 23.5 | 31.2 | 36.6 | 32.2 | 29.6 | 57.3 | 28 | 28.4
5 | -120 | 21.1 | 32.5 | 23.6 | 31.2 | 36.5 | 32.2 | 29.6 | 57.3 | 28 | 28.4
6 | -119 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.5 | 28 | 28.4
7 | -118 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 28 | 28.4
8 | -117 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.7 | 28 | 28.4
9 | -116 | 21.1 | 32.2 | 24.2 | 31 | 36.1 | 32 | 29.6 | 57.6 | 28 | 28.4
10 | -115 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.6 | 27.9 | 28.4
11 | -114 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 28 | 28.4
12 | -113 | 21.1 | 32.3 | 24 | 31.1 | 36.2 | 32.1 | 29.6 | 57.5 | 28 | 28.4
13 | -112 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 27.9 | 28.4
14 | -111 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.5 | 28 | 28.4
15 | -110 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.6 | 28 | 28.4
16 | -109 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 28 | 28.4
17 | -108 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.6 | 28 | 28.4
18 | -107 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.6 | 28 | 28.4
19 | -106 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32.1 | 29.6 | 57.5 | 28 | 28.4
20 | -105 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 27.9 | 28.4
21 | -104 | 21.1 | 32.3 | 23.9 | 31.1 | 36.2 | 32.1 | 29.6 | 57.5 | 27.9 | 28.4
22 | -103 | 21.1 | 32.3 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.7 | 28 | 28.4
23 | -102 | 21.1 | 32.3 | 24 | 31.1 | 36.2 | 32.1 | 29.6 | 57.7 | 28 | 28.4
24 | -101 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.5 | 28 | 28.4
25 | -100 | 21.1 | 32.3 | 24 | 31 | 36.2 | 32 | 29.6 | 57.5 | 28 | 28.4
26 | -99 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.5 | 28 | 28.4
27 | -98 | 21.1 | 32.2 | 24.2 | 31 | 36.1 | 32 | 29.6 | 57.5 | 27.9 | 28.4
28 | -97 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.6 | 28 | 28.4
29 | -96 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.7 | 28 | 28.4
30 | -95 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.7 | 27.9 | 28.4
31 | -94 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.5 | 28 | 28.4
32 | -93 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.3 | 28 | 28.4
33 | -92 | 21.1 | 32.2 | 24.2 | 31 | 36 | 32 | 29.6 | 57.2 | 28 | 28.4
34 | -91 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.2 | 27.9 | 28.4
35 | -90 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 57.2 | 27.9 | 28.4
36 | -89 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 57.3 | 27.9 | 28.4
37 | -88 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.4 | 28 | 28.4
38 | -87 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.3 | 28 | 28.4
39 | -86 | 21.1 | 32.1 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.2 | 27.9 | 28.4
40 | -85 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.2 | 28 | 28.4
41 | -84 | 21.1 | 32.2 | 24.2 | 31 | 36 | 32 | 29.6 | 57.3 | 27.9 | 28.4
42 | -83 | 21.1 | 32.2 | 24.2 | 31 | 36 | 32 | 29.6 | 57.5 | 27.9 | 28.4
43 | -82 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.6 | 27.9 | 28.4
44 | -81 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.7 | 27.9 | 28.4
45 | -80 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.7 | 27.9 | 28.4
46 | -79 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.7 | 27.9 | 28.4
47 | -78 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 57.7 | 27.9 | 28.4
48 | -77 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.6 | 27.9 | 28.4
49 | -76 | 21.1 | 32.2 | 24.2 | 31 | 36 | 32 | 29.6 | 57.7 | 27.9 | 28.4
50 | -75 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.7 | 27.9 | 28.4
51 | -74 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 57.9 | 27.9 | 28.4
52 | -73 | 21.1 | 32.2 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 57.9 | 27.9 | 28.4
53 | -72 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 58 | 27.9 | 28.4
54 | -71 | 21.1 | 32.2 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 58.1 | 27.9 | 28.4
55 | -70 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 58 | 27.9 | 28.4
56 | -69 | 21.1 | 32.2 | 24.2 | 31 | 36 | 31.9 | 29.6 | 58 | 27.9 | 28.4
57 | -68 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57.6 | 27.9 | 28.4
58 | -67 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 57.5 | 27.9 | 28.4
59 | -66 | 21.1 | 32.1 | 24.3 | 30.9 | 35.9 | 31.9 | 29.6 | 57.5 | 27.9 | 28.4
60 | -65 | 21.1 | 32.1 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 57.6 | 27.9 | 28.4
61 | -64 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57.5 | 27.9 | 28.4
62 | -63 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57.2 | 27.9 | 28.4
63 | -62 | 21.1 | 32.1 | 24.3 | 30.9 | 35.9 | 31.9 | 29.6 | 57.1 | 27.9 | 28.4
64 | -61 | 21.1 | 32.2 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 57.1 | 27.9 | 28.4
65 | -60 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 57.3 | 27.9 | 28.4
66 | -59 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 57.3 | 27.9 | 28.4
67 | -58 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 57.2 | 27.9 | 28.4
68 | -57 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 57.2 | 27.9 | 28.4
69 | -56 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 57 | 27.9 | 28.4
70 | -55 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.9 | 27.9 | 28.4
71 | -54 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.7 | 27.9 | 28.4
72 | -53 | 21.1 | 32.2 | 24.1 | 31 | 36.1 | 32 | 29.6 | 56.4 | 27.9 | 28.4
73 | -52 | 21.1 | 32.2 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
74 | -51 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 56.4 | 27.9 | 28.4
75 | -50 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
76 | -49 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
77 | -48 | 21.1 | 32.1 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
78 | -47 | 21.1 | 32.2 | 24.1 | 31 | 36 | 32 | 29.6 | 56.5 | 27.9 | 28.4
79 | -46 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.5 | 27.9 | 28.4
80 | -45 | 21.1 | 32.3 | 24 | 31 | 36.1 | 32 | 29.6 | 56.6 | 27.9 | 28.4
81 | -44 | 21.1 | 32.2 | 24 | 31 | 36.1 | 32 | 29.6 | 56.6 | 27.9 | 28.4
82 | -43 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
83 | -42 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
84 | -41 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
85 | -40 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
86 | -39 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
87 | -38 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.6 | 27.9 | 28.4
88 | -37 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.7 | 27.9 | 28.4
89 | -36 | 21.1 | 32.2 | 24.1 | 31 | 36 | 31.9 | 29.6 | 56.8 | 27.9 | 28.4
90 | -35 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.9 | 27.9 | 28.4
91 | -34 | 21.1 | 32.1 | 24.1 | 30.9 | 35.9 | 31.9 | 29.6 | 56.8 | 27.9 | 28.4
92 | -33 | 21.1 | 32.1 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 56.9 | 27.9 | 28.4
93 | -32 | 21.1 | 32.1 | 24.1 | 30.9 | 35.9 | 31.9 | 29.6 | 57 | 27.9 | 28.4
94 | -31 | 21.1 | 32.1 | 24.2 | 30.9 | 36 | 31.9 | 29.6 | 57.1 | 27.9 | 28.4
95 | -30 | 21.1 | 32.1 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 57 | 27.9 | 28.4
96 | -29 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57 | 27.9 | 28.4
97 | -28 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57.1 | 27.9 | 28.4
98 | -27 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 57 | 27.9 | 28.4
99 | -26 | 21.1 | 32.1 | 24.3 | 30.9 | 35.9 | 31.9 | 29.6 | 57 | 27.9 | 28.4
100 | -25 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.8 | 27.9 | 28.4
101 | -24 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.8 | 27.9 | 28.4
102 | -23 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.7 | 27.9 | 28.4
103 | -22 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.5 | 27.9 | 28.4
104 | -21 | 21.1 | 32.1 | 24.1 | 30.9 | 35.9 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
105 | -20 | 21.1 | 32.1 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.3 | 27.9 | 28.4
106 | -19 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.1 | 27.9 | 28.4
107 | -18 | 21.1 | 32.1 | 24.1 | 30.9 | 35.9 | 31.9 | 29.6 | 56.1 | 27.9 | 28.4
108 | -17 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.1 | 27.9 | 28.4
109 | -16 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.2 | 27.9 | 28.4
110 | -15 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.5 | 27.9 | 28.4
111 | -14 | 21.1 | 32.2 | 24 | 31 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
112 | -13 | 21.1 | 32.1 | 24.2 | 30.9 | 35.9 | 31.9 | 29.6 | 56.3 | 27.9 | 28.4
113 | -12 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
114 | -11 | 21.1 | 32.2 | 24 | 31 | 36 | 31.9 | 29.5 | 56.4 | 27.9 | 28.4
115 | -10 | 21.1 | 32.2 | 24 | 31 | 36 | 31.9 | 29.5 | 56.5 | 27.9 | 28.4
116 | -9 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.6 | 56.4 | 27.9 | 28.4
117 | -8 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.5 | 56.4 | 27.9 | 28.4
118 | -7 | 21.1 | 32.2 | 24 | 31 | 36.1 | 32 | 29.5 | 56.5 | 27.9 | 28.4
119 | -6 | 21.1 | 32.2 | 24.1 | 30.9 | 36 | 31.9 | 29.5 | 56.8 | 27.9 | 28.4
120 | -5 | 21.1 | 32.2 | 24 | 31 | 36.1 | 32 | 29.5 | 56.9 | 27.9 | 28.4
121 | -4 | 21.1 | 32.8 | 22.6 | 31.4 | 36.8 | 32.4 | 29.4 | 56.8 | 27.9 | 28.3
122 | -3 | 21 | 33.7 | 20.8 | 32.1 | 38 | 33.1 | 29.3 | 56.6 | 27.8 | 28.3
123 | -2 | 21.1 | 34 | 20.2 | 32.3 | 38.4 | 33.3 | 29.2 | 56.6 | 27.8 | 28.3
124 | -1 | 21.6 | 34.1 | 20 | 32.4 | 38.6 | 33.4 | 29.2 | 56.6 | 27.8 | 28.2
125 | 0 | 22.6 | 34 | 20.2 | 32.3 | 38.5 | 33.3 | 29.2 | 56.5 | 27.8 | 28.2
126 | 1 | 24.2 | 34 | 20.2 | 32.3 | 38.4 | 33.3 | 29.2 | 56.7 | 27.8 | 28.2
127 | 2 | 26.3 | 34 | 20.3 | 32.3 | 38.4 | 33.3 | 29.2 | 56.9 | 27.8 | 28.2
128 | 3 | 28.8 | 34.1 | 20.1 | 32.4 | 38.5 | 33.3 | 29.2 | 57 | 27.8 | 28.2
129 | 4 | 31.8 | 34.1 | 20.1 | 32.4 | 38.5 | 33.4 | 29.2 | 57 | 27.8 | 28.2
130 | 5 | 35 | 34.1 | 20.2 | 32.4 | 38.5 | 33.3 | 29.2 | 57.1 | 27.8 | 28.2
131 | 6 | 38.6 | 34.2 | 20 | 32.5 | 38.6 | 33.4 | 29.2 | 57.1 | 27.8 | 28.2
132 | 7 | 42.5 | 34 | 20.5 | 32.3 | 38.4 | 33.3 | 29.2 | 57.2 | 27.8 | 28.2
133 | 8 | 46.5 | 34.2 | 20 | 32.5 | 38.7 | 33.4 | 29.2 | 57.3 | 27.8 | 28.2
134 | 9 | 50.8 | 34.1 | 20.4 | 32.4 | 38.4 | 33.3 | 29.2 | 57.2 | 27.8 | 28.2
135 | 10 | 55.2 | 34.3 | 20.2 | 32.5 | 38.6 | 33.4 | 29.2 | 57.1 | 27.8 | 28.2
136 | 11 | 59.9 | 34.2 | 20.6 | 32.5 | 38.4 | 33.3 | 29.2 | 57.2 | 27.8 | 28.2
137 | 12 | 64.6 | 34.3 | 20.4 | 32.6 | 38.6 | 33.4 | 29.2 | 57.1 | 27.8 | 28.2
138 | 13 | 69.6 | 34.3 | 20.7 | 32.6 | 38.5 | 33.3 | 29.2 | 57 | 27.8 | 28.2
139 | 14 | 74.7 | 34.3 | 20.8 | 32.6 | 38.5 | 33.3 | 29.2 | 56.9 | 27.8 | 28.2
140 | 15 | 79.9 | 34.4 | 20.8 | 32.7 | 38.5 | 33.4 | 29.2 | 57 | 27.8 | 28.3
141 | 16 | 85.2 | 34.4 | 21 | 32.7 | 38.5 | 33.3 | 29.2 | 57.1 | 27.8 | 28.3
142 | 17 | 90.6 | 34.5 | 21.1 | 32.8 | 38.5 | 33.3 | 29.2 | 57.1 | 27.8 | 28.2
143 | 18 | 96.1 | 34.5 | 21.4 | 32.8 | 38.4 | 33.3 | 29.2 | 56.9 | 27.8 | 28.3
144 | 19 | 101.7 | 34.7 | 21.3 | 32.9 | 38.5 | 33.4 | 29.2 | 56.7 | 27.8 | 28.3
145 | 20 | 107.4 | 34.7 | 21.6 | 32.9 | 38.5 | 33.3 | 29.2 | 56.9 | 27.8 | 28.3
146 | 21 | 113.1 | 34.8 | 21.6 | 33.1 | 38.5 | 33.4 | 29.2 | 56.9 | 27.7 | 28.3
147 | 22 | 119 | 34.8 | 22 | 33.1 | 38.4 | 33.3 | 29.2 | 56.9 | 27.8 | 28.3
148 | 23 | 124.9 | 35 | 22.1 | 33.2 | 38.5 | 33.3 | 29.2 | 56.7 | 27.8 | 28.3
149 | 24 | 130.7 | 35.1 | 22.3 | 33.3 | 38.5 | 33.3 | 29.2 | 56.6 | 27.7 | 28.3
150 | 25 | 136.6 | 35.2 | 22.6 | 33.4 | 38.5 | 33.3 | 29.2 | 56.7 | 27.8 | 28.3
151 | 26 | 142.6 | 35.3 | 22.8 | 33.5 | 38.5 | 33.3 | 29.2 | 56.9 | 27.8 | 28.3
152 | 27 | 148.6 | 35.4 | 23.1 | 33.6 | 38.5 | 33.3 | 29.2 | 57 | 27.8 | 28.3
153 | 28 | 154.6 | 35.6 | 23.1 | 33.8 | 38.6 | 33.4 | 29.2 | 56.9 | 27.7 | 28.3
154 | 29 | 160.6 | 35.6 | 23.6 | 33.8 | 38.4 | 33.3 | 29.2 | 56.8 | 27.8 | 28.3
155 | 30 | 166.6 | 35.9 | 23.5 | 34.1 | 38.6 | 33.4 | 29.2 | 56.7 | 27.7 | 28.3
156 | 31 | 172.6 | 35.9 | 24.1 | 34.1 | 38.4 | 33.3 | 29.2 | 56.6 | 27.8 | 28.4
157 | 32 | 178.8 | 36.2 | 24.3 | 34.4 | 38.5 | 33.4 | 29.2 | 56.6 | 27.7 | 28.4
158 | 33 | 184.9 | 36.3 | 24.9 | 34.5 | 38.4 | 33.3 | 29.2 | 56.7 | 27.8 | 28.4
159 | 34 | 191 | 36.5 | 25.1 | 34.7 | 38.5 | 33.3 | 29.2 | 56.8 | 27.8 | 28.4
160 | 35 | 197.1 | 36.7 | 25.5 | 34.8 | 38.5 | 33.3 | 29.2 | 56.9 | 27.8 | 28.4
161 | 36 | 203.3 | 36.9 | 26 | 35 | 38.5 | 33.3 | 29.2 | 56.9 | 27.8 | 28.4
162 | 37 | 209.4 | 37.1 | 26.4 | 35.2 | 38.5 | 33.3 | 29.2 | 57 | 27.7 | 28.5
163 | 38 | 215.4 | 37.2 | 27 | 35.3 | 38.4 | 33.3 | 29.2 | 57.2 | 27.8 | 28.5
164 | 39 | 221.5 | 37.6 | 27.1 | 35.7 | 38.5 | 33.3 | 29.2 | 57.3 | 27.8 | 28.5
165 | 40 | 227.6 | 37.7 | 27.8 | 35.8 | 38.4 | 33.3 | 29.2 | 57.2 | 27.8 | 28.5
166 | 41 | 233.7 | 38 | 27.8 | 36.1 | 38.5 | 33.3 | 29.2 | 57.1 | 27.8 | 28.5
167 | 42 | 239.8 | 38.1 | 28.5 | 36.2 | 38.3 | 33.2 | 29.2 | 56.7 | 27.8 | 28.6
168 | 43 | 245.8 | 38.5 | 28.8 | 36.6 | 38.5 | 33.3 | 29.2 | 56.5 | 27.8 | 28.6
169 | 44 | 251.9 | 38.7 | 29.4 | 36.8 | 38.4 | 33.3 | 29.2 | 56.6 | 27.8 | 28.6
170 | 45 | 258 | 39 | 29.9 | 37.1 | 38.5 | 33.3 | 29.2 | 56.6 | 27.8 | 28.7
171 | 46 | 264.1 | 39.3 | 30.3 | 37.3 | 38.4 | 33.3 | 29.2 | 56.6 | 27.8 | 28.7
172 | 47 | 270.1 | 39.6 | 30.8 | 37.6 | 38.4 | 33.3 | 29.3 | 56.6 | 27.8 | 28.7
173 | 48 | 276.1 | 39.9 | 31.4 | 38 | 38.4 | 33.3 | 29.2 | 56.6 | 27.8 | 28.7
174 | 49 | 282.1 | 40.2 | 32.2 | 38.3 | 38.3 | 33.2 | 29.3 | 56.5 | 27.8 | 28.8
175 | 50 | 288.1 | 40.7 | 32.3 | 38.7 | 38.5 | 33.3 | 29.2 | 56.5 | 27.8 | 28.8
176 | 51 | 294 | 40.9 | 33.1 | 38.9 | 38.4 | 33.3 | 29.3 | 56.7 | 27.8 | 28.9
177 | 52 | 299.9 | 41.3 | 33.7 | 39.3 | 38.4 | 33.3 | 29.3 | 56.6 | 27.8 | 28.9
178 | 53 | 305.9 | 41.6 | 34.7 | 39.5 | 38.3 | 33.2 | 29.3 | 56.7 | 27.8 | 29
179 | 54 | 311.8 | 42 | 35.2 | 39.9 | 38.4 | 33.2 | 29.3 | 56.8 | 27.8 | 29
180 | 55 | 317.7 | 42.4 | 36 | 40.3 | 38.3 | 33.2 | 29.3 | 56.9 | 27.8 | 29.1
181 | 56 | 323.5 | 42.9 | 36.5 | 40.8 | 38.4 | 33.3 | 29.3 | 56.8 | 27.8 | 29.1
182 | 57 | 329.3 | 43.3 | 37.2 | 41.2 | 38.4 | 33.3 | 29.3 | 57 | 27.8 | 29.2
183 | 58 | 335.1 | 43.7 | 38 | 41.5 | 38.4 | 33.2 | 29.3 | 57.1 | 27.8 | 29.2
184 | 59 | 340.8 | 44.2 | 38.8 | 42 | 38.4 | 33.3 | 29.3 | 57.2 | 27.8 | 29.3
185 | 60 | 346.6 | 44.6 | 39.8 | 42.5 | 38.3 | 33.2 | 29.3 | 57.4 | 27.9 | 29.4
186 | 61 | 352.3 | 45.2 | 40.4 | 43 | 38.4 | 33.3 | 29.3 | 57.5 | 27.9 | 29.4
187 | 62 | 358 | 45.6 | 41.4 | 43.4 | 38.3 | 33.2 | 29.3 | 57.6 | 27.9 | 29.5
188 | 63 | 363.7 | 46.1 | 42.2 | 43.9 | 38.4 | 33.2 | 29.3 | 57.7 | 27.9 | 29.6
189 | 64 | 369.2 | 46.6 | 43.2 | 44.4 | 38.3 | 33.2 | 29.3 | 57.6 | 27.9 | 29.7
190 | 65 | 374.8 | 47.3 | 43.9 | 44.9 | 38.4 | 33.3 | 29.3 | 57.3 | 27.9 | 29.7
191 | 66 | 380.3 | 47.7 | 45 | 45.4 | 38.3 | 33.2 | 29.4 | 57.5 | 27.9 | 29.8
192 | 67 | 385.8 | 48.3 | 45.8 | 46 | 38.4 | 33.3 | 29.4 | 57.6 | 27.9 | 29.9
193 | 68 | 391.3 | 48.9 | 46.7 | 46.6 | 38.4 | 33.3 | 29.4 | 57.8 | 27.9 | 30
194 | 69 | 396.8 | 49.5 | 47.8 | 47.2 | 38.4 | 33.3 | 29.4 | 57.7 | 27.9 | 30.1
195 | 70 | 402.2 | 50.1 | 48.8 | 47.8 | 38.4 | 33.3 | 29.4 | 57.7 | 27.9 | 30.2
196 | 71 | 407.6 | 50.7 | 49.9 | 48.3 | 38.4 | 33.3 | 29.4 | 57.8 | 28 | 30.3
197 | 72 | 412.9 | 51.5 | 50.8 | 49.1 | 38.5 | 33.3 | 29.4 | 57.9 | 28 | 30.4
198 | 73 | 418.2 | 52 | 52.2 | 49.5 | 38.3 | 33.2 | 29.5 | 57.9 | 28 | 30.5
199 | 74 | 423.4 | 52.7 | 53.2 | 50.2 | 38.4 | 33.3 | 29.5 | 57.9 | 28 | 30.6
200 | 75 | 428.6 | 53.4 | 54.2 | 50.9 | 38.3 | 33.2 | 29.5 | 58 | 28 | 30.7
201 | 76 | 433.8 | 54.1 | 55.4 | 51.6 | 38.3 | 33.2 | 29.5 | 57.9 | 28 | 30.8
202 | 77 | 439 | 54.9 | 56.7 | 52.3 | 38.3 | 33.2 | 29.5 | 58 | 28.1 | 31
203 | 78 | 444.1 | 55.6 | 57.9 | 53 | 38.4 | 33.3 | 29.5 | 58.1 | 28.1 | 31.1
204 | 79 | 449.2 | 56.4 | 59.2 | 53.8 | 38.4 | 33.3 | 29.6 | 58.2 | 28.1 | 31.2
205 | 80 | 454.2 | 57.2 | 60.4 | 54.4 | 38.4 | 33.3 | 29.6 | 58.5 | 28.1 | 31.3
206 | 81 | 459.2 | 58 | 61.6 | 55.2 | 38.4 | 33.3 | 29.6 | 58.6 | 28.1 | 31.5
207 | 82 | 464.2 | 58.8 | 63 | 56 | 38.4 | 33.3 | 29.6 | 58.6 | 28.1 | 31.6
208 | 83 | 469.1 | 59.7 | 64.2 | 56.9 | 38.5 | 33.3 | 29.6 | 58.6 | 28.2 | 31.8
209 | 84 | 474 | 60.5 | 65.7 | 57.7 | 38.4 | 33.3 | 29.7 | 58.8 | 28.2 | 31.9
210 | 85 | 478.9 | 61.4 | 67 | 58.5 | 38.5 | 33.3 | 29.7 | 59 | 28.2 | 32.1
211 | 86 | 483.7 | 61.9 | 69.2 | 59.1 | 37.9 | 33 | 29.8 | 59 | 28.3 | 32.3
212 | 87 | 488.4 | 62.9 | 70.6 | 59.9 | 38.2 | 33.1 | 29.8 | 59 | 28.3 | 32.4
213 | 88 | 493 | 63.7 | 72.2 | 60.7 | 38.1 | 33.1 | 29.8 | 59.1 | 28.3 | 32.6
214 | 89 | 497.2 | 64.7 | 73.5 | 61.6 | 38.2 | 33.1 | 29.9 | 59.4 | 28.3 | 32.8
215 | 90 | 500.8 | 65.6 | 75 | 62.4 | 38.1 | 33.1 | 29.9 | 59.6 | 28.4 | 32.9
216 | 91 | 504.2 | 66.5 | 76.6 | 63.3 | 38 | 33 | 29.9 | 59.6 | 28.4 | 33.1
217 | 92 | 507.4 | 67.4 | 77.9 | 64.4 | 38.1 | 33.1 | 30 | 59.5 | 28.4 | 33.3
218 | 93 | 510.4 | 68.4 | 79.3 | 65.2 | 38.1 | 33.1 | 30 | 59.4 | 28.5 | 33.5
219 | 94 | 513.3 | 69.4 | 80.6 | 66.2 | 38.2 | 33.1 | 30 | 59.7 | 28.5 | 33.7
220 | 95 | 516.1 | 70.3 | 82.1 | 67.1 | 38.3 | 33.2 | 30 | 60 | 28.5 | 33.9
221 | 96 | 518.7 | 71.3 | 83.6 | 68 | 38.3 | 33.1 | 30.1 | 60.2 | 28.6 | 34.1
222 | 97 | 521 | 72.1 | 85.3 | 68.8 | 38.1 | 33.1 | 30.1 | 60.3 | 28.6 | 34.4
223 | 98 | 523.1 | 73 | 86.7 | 69.7 | 37.9 | 33 | 30.2 | 60.4 | 28.7 | 34.6
224 | 99 | 524.9 | 73.7 | 88.6 | 70.5 | 37.4 | 32.8 | 30.3 | 60.5 | 28.7 | 34.8
225 | 100 | 526.5 | 74.5 | 90.4 | 71.2 | 37.1 | 32.7 | 30.4 | 60.6 | 28.8 | 35.1
226 | 101 | 527.7 | 75.2 | 92.2 | 72 | 36.8 | 32.5 | 30.5 | 60.8 | 28.8 | 35.3
227 | 102 | 528.7 | 76 | 93.8 | 72.8 | 36.6 | 32.4 | 30.6 | 60.9 | 28.8 | 35.6
228 | 103 | 529.5 | 76.9 | 95.2 | 73.8 | 36.4 | 32.4 | 30.6 | 61.2 | 28.9 | 35.8
229 | 104 | 530.1 | 77.8 | 96.6 | 74.7 | 36.3 | 32.3 | 30.7 | 61.5 | 28.9 | 36.1
230 | 105 | 530.5 | 78.7 | 98 | 75.5 | 36.3 | 32.3 | 30.7 | 61.5 | 29 | 36.3
231 | 106 | 530.7 | 79.6 | 99.3 | 76.5 | 36.4 | 32.3 | 30.8 | 61.5 | 29 | 36.6
232 | 107 | 530.8 | 80.6 | 100.5 | 77.4 | 36.5 | 32.4 | 30.8 | 61.4 | 29.1 | 36.8
233 | 108 | 530.7 | 81.5 | 101.8 | 78.3 | 36.5 | 32.4 | 30.9 | 61.6 | 29.1 | 37.1
234 | 109 | 530.5 | 82.4 | 103 | 79.2 | 36.4 | 32.4 | 31 | 61.8 | 29.2 | 37.4
235 | 110 | 530.1 | 83.4 | 104.2 | 80.1 | 36.5 | 32.4 | 31 | 61.8 | 29.2 | 37.6
236 | 111 | 529.7 | 84.3 | 105.3 | 81 | 36.6 | 32.5 | 31.1 | 61.7 | 29.3 | 37.9
237 | 112 | 529.3 | 85.3 | 106.4 | 81.8 | 36.7 | 32.6 | 31.1 | 61.5 | 29.4 | 38.2
238 | 113 | 528.8 | 86.3 | 107.4 | 82.8 | 36.8 | 32.7 | 31.2 | 61.4 | 29.4 | 38.5
239 | 114 | 528.4 | 87.2 | 108.5 | 83.8 | 37 | 32.7 | 31.2 | 61.4 | 29.5 | 38.8
240 | 115 | 527.9 | 88.2 | 109.5 | 84.7 | 37.2 | 32.8 | 31.3 | 61.3 | 29.5 | 39
241 | 116 | 527.3 | 89.2 | 110.5 | 85.6 | 37.5 | 33 | 31.3 | 61.2 | 29.6 | 39.3
242 | 117 | 526.7 | 90.2 | 111.4 | 86.6 | 37.7 | 33.1 | 31.4 | 61.4 | 29.7 | 39.6
243 | 118 | 526.2 | 91.2 | 112.3 | 87.5 | 37.8 | 33.2 | 31.4 | 61.5 | 29.7 | 39.9
244 | 119 | 525.6 | 92.2 | 113.2 | 88.4 | 38 | 33.3 | 31.5 | 61.6 | 29.8 | 40.2
245 | 120 | 525.2 | 93.2 | 114.3 | 89.3 | 38.3 | 33.4 | 31.6 | 61.8 | 29.9 | 40.5
246 | 121 | 524.7 | 94.1 | 115.3 | 90.1 | 38.5 | 33.5 | 31.6 | 62.1 | 29.9 | 40.8
247 | 122 | 524.3 | 95.1 | 116.2 | 91 | 38.7 | 33.6 | 31.7 | 62.1 | 30 | 41.1
248 | 123 | 524 | 96 | 117.1 | 91.9 | 38.9 | 33.7 | 31.8 | 62.3 | 30.1 | 41.4
249 | 124 | 523.9 | 96.9 | 118.1 | 92.8 | 39 | 33.8 | 31.8 | 62.5 | 30.1 | 41.7
250 | 125 | 523.7 | 97.8 | 119.3 | 93.7 | 39 | 33.8 | 31.9 | 62.7 | 30.2 | 42
251 | 126 | 523.5 | 98.7 | 120.4 | 94.6 | 39.2 | 33.9 | 32 | 63.1 | 30.3 | 42.3
252 | 127 | 523.3 | 99.6 | 121.5 | 95.5 | 39.3 | 34 | 32.1 | 63.4 | 30.4 | 42.6
253 | 128 | 523.2 | 100.6 | 122.6 | 96.3 | 39.5 | 34.1 | 32.2 | 63.8 | 30.4 | 42.9
254 | 129 | 523.3 | 101.5 | 123.7 | 97.2 | 39.5 | 34.1 | 32.3 | 64 | 30.5 | 43.2
255 | 130 | 523.4 | 102.3 | 125 | 98 | 39.5 | 34.1 | 32.4 | 64.1 | 30.6 | 43.5
256 | 131 | 523.6 | 103.1 | 126.2 | 98.8 | 39.6 | 34.2 | 32.5 | 64.2 | 30.7 | 43.9
257 | 132 | 523.7 | 103.9 | 127.5 | 99.6 | 39.5 | 34.1 | 32.6 | 64.5 | 30.7 | 44.2
258 | 133 | 523.9 | 104.9 | 128.4 | 100.5 | 39.7 | 34.3 | 32.7 | 64.7 | 30.8 | 44.5
259 | 134 | 524.2 | 105.8 | 129.5 | 101.4 | 39.9 | 34.4 | 32.8 | 64.8 | 30.9 | 44.8
260 | 135 | 524.4 | 106.7 | 130.6 | 102.1 | 39.9 | 34.4 | 32.9 | 65.2 | 31 | 45.1
261 | 136 | 524.6 | 107.5 | 131.8 | 102.9 | 40 | 34.5 | 33 | 65.6 | 31.1 | 45.5
262 | 137 | 524.9 | 108.4 | 132.9 | 103.9 | 40 | 34.5 | 33.1 | 65.7 | 31.2 | 45.8
263 | 138 | 525.2 | 109.3 | 133.9 | 104.6 | 40.2 | 34.6 | 33.2 | 65.8 | 31.3 | 46.1
264 | 139 | 525.5 | 110.1 | 135.1 | 105.5 | 40.2 | 34.7 | 33.4 | 66.1 | 31.3 | 46.5
265 | 140 | 525.7 | 111 | 136.3 | 106.3 | 40.3 | 34.7 | 33.5 | 66.2 | 31.4 | 46.8
266 | 141 | 526.1 | 111.8 | 137.4 | 107.2 | 40.4 | 34.8 | 33.6 | 66.4 | 31.5 | 47.1
267 | 142 | 526.4 | 112.7 | 138.5 | 108.1 | 40.4 | 34.8 | 33.7 | 66.6 | 31.6 | 47.5
268 | 143 | 526.7 | 113.5 | 139.7 | 108.9 | 40.5 | 34.9 | 33.9 | 66.8 | 31.7 | 47.8
269 | 144 | 527 | 114.4 | 140.9 | 109.7 | 40.6 | 35 | 34 | 67 | 31.8 | 48.2
270 | 145 | 527.2 | 115.3 | 142 | 110.6 | 40.6 | 35 | 34.1 | 67.3 | 31.9 | 48.5
271 | 146 | 527.5 | 116.1 | 143.1 | 111.4 | 40.6 | 35.1 | 34.3 | 67.5 | 32 | 48.9
272 | 147 | 527.8 | 116.9 | 144.3 | 112.3 | 40.7 | 35.2 | 34.4 | 67.7 | 32.1 | 49.2
273 | 148 | 528 | 117.8 | 145.3 | 113.1 | 40.9 | 35.3 | 34.5 | 67.8 | 32.2 | 49.5
274 | 149 | 528.2 | 118.7 | 146.5 | 113.9 | 40.9 | 35.3 | 34.7 | 68.2 | 32.3 | 49.9
275 | 150 | 528.4 | 119.5 | 147.7 | 114.8 | 41 | 35.4 | 34.8 | 68.6 | 32.4 | 50.3
276 | 151 | 528.5 | 120.3 | 148.8 | 115.5 | 41 | 35.4 | 34.9 | 68.7 | 32.5 | 50.6
277 | 152 | 528.5 | 121.2 | 149.6 | 116.4 | 41.3 | 35.6 | 35.1 | 68.8 | 32.6 | 51
278 | 153 | 528.5 | 122.1 | 150.8 | 117.2 | 41.3 | 35.7 | 35.2 | 68.9 | 32.7 | 51.3
279 | 154 | 528.6 | 123 | 151.9 | 118 | 41.4 | 35.8 | 35.4 | 69.2 | 32.8 | 51.7
280 | 155 | 528.7 | 123.8 | 153 | 118.9 | 41.6 | 35.9 | 35.5 | 69.5 | 32.9 | 52.1
281 | 156 | 528.8 | 124.7 | 154 | 119.7 | 41.8 | 36 | 35.7 | 69.6 | 33 | 52.4
282 | 157 | 528.8 | 125.5 | 155 | 120.5 | 41.9 | 36.1 | 35.8 | 69.8 | 33.1 | 52.8
283 | 158 | 528.9 | 126.4 | 156.1 | 121.3 | 42.1 | 36.2 | 36 | 70.2 | 33.2 | 53.1
284 | 159 | 528.8 | 127.3 | 157 | 122.2 | 42.3 | 36.4 | 36.1 | 70.6 | 33.4 | 53.5
285 | 160 | 528.9 | 128.1 | 158.1 | 123.1 | 42.4 | 36.4 | 36.3 | 70.8 | 33.5 | 53.9
286 | 161 | 528.9 | 128.9 | 159.2 | 123.9 | 42.4 | 36.5 | 36.4 | 71 | 33.6 | 54.3
287 | 162 | 529 | 129.7 | 160.4 | 124.6 | 42.5 | 36.6 | 36.6 | 71.2 | 33.7 | 54.6
288 | 163 | 529.1 | 130.5 | 161.5 | 125.4 | 42.7 | 36.7 | 36.7 | 71.6 | 33.8 | 55
289 | 164 | 529.1 | 131.4 | 162.4 | 126.2 | 42.9 | 36.9 | 36.9 | 72 | 33.9 | 55.4
290 | 165 | 529.1 | 132.3 | 163.3 | 127.1 | 43 | 37 | 37.1 | 72.2 | 34.1 | 55.8
291 | 166 | 529 | 133.1 | 164.4 | 127.9 | 43.1 | 37.1 | 37.2 | 72.4 | 34.2 | 56.1
292 | 167 | 529 | 133.9 | 165.5 | 128.8 | 43.3 | 37.2 | 37.4 | 72.7 | 34.3 | 56.5
293 | 168 | 529 | 134.6 | 166.8 | 129.6 | 43.2 | 37.2 | 37.6 | 73.1 | 34.4 | 56.9
294 | 169 | 529.1 | 135.4 | 167.9 | 130.2 | 43.3 | 37.3 | 37.8 | 73.3 | 34.5 | 57.3
295 | 170 | 529.1 | 136.3 | 168.8 | 131.1 | 43.6 | 37.5 | 37.9 | 73.4 | 34.7 | 57.7
296 | 171 | 529.2 | 137.1 | 169.9 | 131.9 | 43.6 | 37.6 | 38.1 | 73.6 | 34.8 | 58
297 | 172 | 529.2 | 137.9 | 170.9 | 132.7 | 43.9 | 37.7 | 38.3 | 73.9 | 34.9 | 58.4
298 | 173 | 529.2 | 138.8 | 171.8 | 133.5 | 44.1 | 37.9 | 38.5 | 74 | 35.1 | 58.8
299 | 174 | 529.3 | 139.6 | 172.9 | 134.3 | 44.2 | 38 | 38.6 | 74.4 | 35.2 | 59.2
300 | 175 | 529.4 | 140.3 | 174 | 135.1 | 44.4 | 38.2 | 38.8 | 74.7 | 35.3 | 59.5
301 | 176 | 529.4 | 141.2 | 175 | 135.9 | 44.6 | 38.3 | 39 | 75 | 35.5 | 59.9
302 | 177 | 529.4 | 142 | 175.9 | 136.7 | 44.7 | 38.5 | 39.2 | 75.3 | 35.6 | 60.3
303 | 178 | 529.5 | 142.9 | 176.9 | 137.4 | 45 | 38.6 | 39.4 | 75.6 | 35.7 | 60.6
304 | 179 | 529.5 | 143.7 | 178 | 138.2 | 45.1 | 38.8 | 39.5 | 75.8 | 35.9 | 61
305 | 180 | 529.6 | 144.4 | 179 | 139.1 | 45.3 | 38.9 | 39.7 | 76.1 | 36 | 61.4
306 | 181 | 529.6 | 145.2 | 180 | 139.8 | 45.4 | 39 | 39.9 | 76.3 | 36.1 | 61.8
307 | 182 | 529.6 | 146 | 181.1 | 140.6 | 45.6 | 39.2 | 40.1 | 76.3 | 36.3 | 62.1
308 | 183 | 529.6 | 146.8 | 182 | 141.4 | 45.8 | 39.3 | 40.3 | 76.6 | 36.4 | 62.5
309 | 184 | 529.7 | 147.6 | 183 | 142.1 | 46 | 39.5 | 40.5 | 76.8 | 36.6 | 62.9
310 | 185 | 529.7 | 148.4 | 184 | 143 | 46.1 | 39.6 | 40.7 | 77.1 | 36.7 | 63.3
311 | 186 | 529.9 | 149.2 | 185 | 143.8 | 46.3 | 39.7 | 40.9 | 77.4 | 36.9 | 63.6
312 | 187 | 529.9 | 150 | 186.1 | 144.5 | 46.4 | 39.9 | 41.1 | 77.5 | 37 | 64
313 | 188 | 530 | 150.7 | 187.2 | 145.2 | 46.6 | 40 | 41.3 | 77.7 | 37.2 | 64.4
314 | 189 | 530 | 151.5 | 188.2 | 146 | 46.7 | 40.2 | 41.5 | 77.8 | 37.3 | 64.7
315 | 190 | 530 | 152.3 | 189.2 | 146.7 | 46.9 | 40.3 | 41.7 | 78.2 | 37.5 | 65.1
316 | 191 | 530 | 153.1 | 190.1 | 147.5 | 47.1 | 40.5 | 41.9 | 78.7 | 37.6 | 65.4
317 | 192 | 530 | 153.8 | 191.1 | 148.2 | 47.3 | 40.6 | 42.1 | 79.1 | 37.8 | 65.8
318 | 193 | 530 | 154.6 | 192.1 | 149.1 | 47.5 | 40.8 | 42.3 | 79.2 | 37.9 | 66.2
319 | 194 | 530 | 155.4 | 193.1 | 149.9 | 47.7 | 41 | 42.5 | 79.5 | 38.1 | 66.5
320 | 195 | 530 | 156.2 | 194.1 | 150.5 | 47.9 | 41.2 | 42.7 | 80 | 38.2 | 66.9
321 | 196 | 530.1 | 157 | 195.1 | 151.3 | 48.1 | 41.3 | 42.9 | 80.5 | 38.4 | 67.2
322 | 197 | 530 | 157.7 | 196 | 152.1 | 48.3 | 41.5 | 43.1 | 81 | 38.5 | 67.6
323 | 198 | 530 | 158.5 | 197 | 152.8 | 48.5 | 41.7 | 43.3 | 81.2 | 38.7 | 68
324 | 199 | 530 | 159.3 | 197.9 | 153.6 | 48.6 | 41.8 | 43.5 | 81.5 | 38.9 | 68.3
325 | 200 | 530.1 | 160 | 198.9 | 154.4 | 48.8 | 42 | 43.8 | 82 | 39 | 68.7
326 | 201 | 530.1 | 160.8 | 199.8 | 155.1 | 49 | 42.2 | 44 | 82.4 | 39.2 | 69
327 | 202 | 530.1 | 161.5 | 200.8 | 155.9 | 49.2 | 42.3 | 44.2 | 82.6 | 39.4 | 69.4
328 | 203 | 530.1 | 162.2 | 201.8 | 156.6 | 49.4 | 42.5 | 44.4 | 83 | 39.5 | 69.8
329 | 204 | 530.1 | 163 | 202.7 | 157.4 | 49.6 | 42.7 | 44.6 | 83.2 | 39.7 | 70.1
330 | 205 | 530.1 | 163.7 | 203.7 | 158.1 | 49.8 | 42.8 | 44.8 | 83.3 | 39.9 | 70.5
331 | 206 | 530.1 | 164.4 | 204.6 | 158.7 | 49.9 | 43 | 45.1 | 83.6 | 40 | 70.8
332 | 207 | 530 | 165.3 | 205.5 | 159.5 | 50.2 | 43.2 | 45.3 | 84 | 40.2 | 71.2
333 | 208 | 530 | 166 | 206.4 | 160.2 | 50.4 | 43.4 | 45.5 | 84.4 | 40.4 | 71.5
334 | 209 | 529.9 | 166.8 | 207.3 | 161 | 50.7 | 43.6 | 45.7 | 84.9 | 40.5 | 71.9
335 | 210 | 529.8 | 167.5 | 208.3 | 161.7 | 50.9 | 43.7 | 46 | 85.2 | 40.7 | 72.3
336 | 211 | 529.8 | 168.3 | 209.3 | 162.4 | 51.1 | 43.9 | 46.2 | 85.6 | 40.9 | 72.6
337 | 212 | 529.7 | 169.1 | 210.1 | 163.2 | 51.3 | 44.1 | 46.4 | 86 | 41.1 | 73
338 | 213 | 529.8 | 169.8 | 211 | 163.9 | 51.5 | 44.3 | 46.7 | 86.4 | 41.2 | 73.3
339 | 214 | 529.7 | 170.5 | 211.8 | 164.6 | 51.7 | 44.5 | 46.9 | 86.6 | 41.4 | 73.7
340 | 215 | 529.7 | 171.3 | 212.5 | 165.4 | 52.1 | 44.7 | 47.1 | 87.1 | 41.6 | 74
341 | 216 | 529.7 | 172.1 | 213.4 | 166.2 | 52.3 | 44.9 | 47.3 | 87.7 | 41.8 | 74.4
342 | 217 | 529.8 | 172.8 | 214.3 | 166.9 | 52.5 | 45.1 | 47.6 | 88 | 41.9 | 74.8
343 | 218 | 529.8 | 173.5 | 215.3 | 167.6 | 52.7 | 45.3 | 47.8 | 88.2 | 42.1 | 75.2
344 | 219 | 529.8 | 174.3 | 216.3 | 168.4 | 52.9 | 45.5 | 48.1 | 88.5 | 42.3 | 75.5
345 | 220 | 529.8 | 175 | 217.1 | 169 | 53.1 | 45.7 | 48.3 | 88.9 | 42.5 | 75.9
346 | 221 | 529.8 | 175.8 | 217.9 | 169.8 | 53.3 | 45.9 | 48.6 | 89.3 | 42.7 | 76.3
347 | 222 | 529.9 | 176.5 | 218.9 | 170.5 | 53.6 | 46.1 | 48.8 | 89.7 | 42.9 | 76.7
348 | 223 | 529.9 | 177.2 | 219.8 | 171.2 | 53.8 | 46.3 | 49.1 | 90.1 | 43 | 77
349 | 224 | 529.9 | 178 | 220.6 | 172 | 54.1 | 46.5 | 49.3 | 90.3 | 43.2 | 77.4
350 | 225 | 529.9 | 178.7 | 221.5 | 172.8 | 54.3 | 46.7 | 49.6 | 90.5 | 43.4 | 77.8
351 | 226 | 530 | 179.4 | 222.3 | 173.5 | 54.5 | 46.9 | 49.8 | 90.7 | 43.6 | 78.1
352 | 227 | 529.9 | 180.2 | 223.2 | 174.2 | 54.8 | 47.1 | 50.1 | 91 | 43.8 | 78.5
353 | 228 | 529.9 | 180.8 | 224.1 | 174.9 | 55 | 47.3 | 50.3 | 91.2 | 44 | 78.9
354 | 229 | 529.9 | 181.6 | 225 | 175.6 | 55.2 | 47.5 | 50.6 | 91.6 | 44.2 | 79.3
355 | 230 | 529.9 | 182.3 | 225.9 | 176.2 | 55.4 | 47.7 | 50.8 | 92.1 | 44.4 | 79.6
356 | 231 | 529.9 | 183 | 226.8 | 177 | 55.6 | 47.9 | 51.1 | 92.7 | 44.5 | 80
357 | 232 | 529.9 | 183.7 | 227.7 | 177.7 | 55.9 | 48.1 | 51.4 | 93.1 | 44.7 | 80.4
358 | 233 | 529.9 | 184.4 | 228.6 | 178.3 | 56.1 | 48.3 | 51.6 | 93.4 | 44.9 | 80.8
359 | 234 | 530 | 185.1 | 229.6 | 179 | 56.3 | 48.5 | 51.9 | 93.8 | 45.1 | 81.1
360 | 235 | 530 | 185.9 | 230.4 | 179.7 | 56.5 | 48.7 | 52.2 | 94.1 | 45.3 | 81.5
361 | 236 | 530 | 186.6 | 231.3 | 180.5 | 56.7 | 48.9 | 52.4 | 94.3 | 45.5 | 81.9
362 | 237 | 530.1 | 187.3 | 232.3 | 181.2 | 56.9 | 49.1 | 52.7 | 94.7 | 45.7 | 82.3
363 | 238 | 530.1 | 188 | 233.2 | 181.8 | 57.2 | 49.3 | 53 | 95.1 | 45.9 | 82.7
364 | 239 | 530.1 | 188.7 | 234 | 182.5 | 57.5 | 49.5 | 53.2 | 95.4 | 46.1 | 83
365 | 240 | 530.2 | 189.4 | 234.9 | 183.3 | 57.7 | 49.8 | 53.5 | 95.8 | 46.3 | 83.4
366 | 241 | 530.2 | 190.1 | 235.7 | 184 | 57.9 | 50 | 53.8 | 96.1 | 46.5 | 83.8
367 | 242 | 530.1 | 190.8 | 236.6 | 184.7 | 58.2 | 50.2 | 54 | 96.4 | 46.7 | 84.2
368 | 243 | 530.2 | 191.5 | 237.4 | 185.4 | 58.4 | 50.4 | 54.3 | 96.7 | 46.9 | 84.5
369 | 244 | 530.2 | 192.3 | 238.2 | 186.1 | 58.7 | 50.7 | 54.6 | 97 | 47.1 | 84.9
370 | 245 | 530.2 | 193 | 239.1 | 186.8 | 58.9 | 50.9 | 54.9 | 97.4 | 47.3 | 85.3
371 | 246 | 530.1 | 193.6 | 240 | 187.4 | 59.1 | 51.1 | 55.1 | 97.7 | 47.5 | 85.7
372 | 247 | 530.1 | 194.3 | 240.9 | 188.1 | 59.3 | 51.3 | 55.4 | 98 | 47.7 | 86
373 | 248 | 530.1 | 195 | 241.8 | 188.9 | 59.5 | 51.5 | 55.7 | 98.3 | 47.9 | 86.4
374 | 249 | 530.1 | 195.7 | 242.7 | 189.5 | 59.7 | 51.7 | 56 | 98.4 | 48.1 | 86.8
375 | 250 | 530.1 | 196.4 | 243.5 | 190.1 | 60 | 51.9 | 56.3 | 98.8 | 48.3 | 87.2
376 | 251 | 530 | 197.1 | 244.3 | 190.9 | 60.2 | 52.2 | 56.6 | 99.3 | 48.5 | 87.5
377 | 252 | 530 | 197.8 | 245.1 | 191.6 | 60.4 | 52.4 | 56.8 | 99.8 | 48.7 | 87.9
378 | 253 | 530 | 198.5 | 245.9 | 192.3 | 60.8 | 52.6 | 57.1 | 100.2 | 48.9 | 88.3
379 | 254 | 530 | 199.1 | 246.8 | 193 | 60.9 | 52.8 | 57.4 | 100.6 | 49.1 | 88.7
380 | 255 | 529.9 | 199.8 | 247.7 | 193.6 | 61.2 | 53.1 | 57.7 | 100.9 | 49.3 | 89
381 | 256 | 529.9 | 200.5 | 248.6 | 194.2 | 61.4 | 53.3 | 58 | 101.4 | 49.5 | 89.4
382 | 257 | 529.9 | 201.2 | 249.3 | 195 | 61.7 | 53.6 | 58.3 | 101.8 | 49.7 | 89.8
383 | 258 | 529.9 | 201.9 | 250.2 | 195.6 | 62 | 53.8 | 58.6 | 102 | 49.9 | 90.1
384 | 259 | 529.8 | 202.6 | 251 | 196.3 | 62.2 | 54 | 58.8 | 102.3 | 50.1 | 90.5
385 | 260 | 529.7 | 203.3 | 251.7 | 197 | 62.5 | 54.3 | 59.1 | 102.9 | 50.3 | 90.9
386 | 261 | 529.7 | 204 | 252.5 | 197.7 | 62.8 | 54.5 | 59.4 | 103.6 | 50.5 | 91.3
387 | 262 | 529.6 | 204.6 | 253.3 | 198.4 | 63.1 | 54.8 | 59.7 | 104 | 50.8 | 91.6
388 | 263 | 529.6 | 205.3 | 254.1 | 199 | 63.3 | 55 | 60 | 104.6 | 51 | 92
389 | 264 | 529.6 | 206 | 254.9 | 199.7 | 63.5 | 55.3 | 60.3 | 105.1 | 51.2 | 92.4
390 | 265 | 529.5 | 206.7 | 255.7 | 200.3 | 63.8 | 55.5 | 60.6 | 105.5 | 51.4 | 92.8
391 | 266 | 529.5 | 207.3 | 256.5 | 201 | 64 | 55.7 | 60.9 | 105.8 | 51.6 | 93.2
392 | 267 | 529.5 | 208 | 257.3 | 201.7 | 64.3 | 56 | 61.2 | 106.2 | 51.8 | 93.5
393 | 268 | 529.5 | 208.7 | 258.1 | 202.4 | 64.5 | 56.2 | 61.5 | 106.5 | 52 | 93.9
394 | 269 | 529.6 | 209.3 | 259 | 203 | 64.7 | 56.4 | 61.8 | 106.9 | 52.2 | 94.3
395 | 270 | 529.7 | 210 | 259.8 | 203.7 | 64.9 | 56.6 | 62.1 | 107 | 52.4 | 94.7
396 | 271 | 529.7 | 210.6 | 260.6 | 204.3 | 65.1 | 56.9 | 62.4 | 107.3 | 52.6 | 95.1
397 | 272 | 529.7 | 211.3 | 261.5 | 205 | 65.3 | 57.1 | 62.7 | 107.9 | 52.8 | 95.5
398 | 273 | 529.7 | 211.9 | 262.2 | 205.6 | 65.6 | 57.4 | 63 | 108.2 | 53 | 95.9
399 | 274 | 529.7 | 212.5 | 263 | 206.2 | 65.9 | 57.6 | 63.3 | 108.4 | 53.3 | 96.2
400 | 275 | 529.7 | 213.2 | 263.8 | 206.8 | 66.1 | 57.9 | 63.6 | 108.6 | 53.5 | 96.6
401 | 276 | 529.7 | 213.8 | 264.6 | 207.5 | 66.4 | 58.1 | 63.9 | 109.3 | 53.7 | 97
402 | 277 | 529.7 | 214.5 | 265.5 | 208.1 | 66.6 | 58.4 | 64.2 | 109.6 | 53.9 | 97.4
403 | 278 | 529.7 | 215.1 | 266.2 | 208.8 | 66.9 | 58.6 | 64.5 | 109.9 | 54.1 | 97.8
404 | 279 | 529.7 | 215.8 | 267 | 209.5 | 67.1 | 58.9 | 64.8 | 110.6 | 54.3 | 98.2
405 | 280 | 529.7 | 216.4 | 267.8 | 210.1 | 67.3 | 59.1 | 65.2 | 111.1 | 54.5 | 98.5
406 | 281 | 529.6 | 217 | 268.7 | 210.7 | 67.5 | 59.4 | 65.5 | 111.4 | 54.7 | 98.9
407 | 282 | 529.6 | 217.6 | 269.5 | 211.3 | 67.7 | 59.6 | 65.8 | 111.9 | 55 | 99.3
408 | 283 | 529.7 | 218.2 | 270.3 | 211.9 | 67.9 | 59.8 | 66.1 | 112.3 | 55.2 | 99.7
409 | 284 | 529.6 | 218.9 | 271.1 | 212.6 | 68.2 | 60.1 | 66.4 | 112.7 | 55.4 | 100.1
410 | 285 | 529.6 | 219.6 | 271.8 | 213.2 | 68.5 | 60.4 | 66.7 | 113.2 | 55.6 | 100.4
411 | 286 | 529.6 | 220.2 | 272.5 | 213.8 | 68.7 | 60.6 | 67 | 113.5 | 55.8 | 100.8
412 | 287 | 529.5 | 220.8 | 273.3 | 214.4 | 68.9 | 60.9 | 67.4 | 114.2 | 56 | 101.2
413 | 288 | 529.5 | 221.5 | 273.9 | 215.1 | 69.2 | 61.2 | 67.7 | 114.6 | 56.2 | 101.6
414 | 289 | 529.5 | 222.1 | 274.7 | 215.8 | 69.4 | 61.4 | 68 | 114.8 | 56.4 | 101.9
415 | 290 | 529.5 | 222.8 | 275.5 | 216.4 | 69.7 | 61.7 | 68.3 | 115.2 | 56.7 | 102.3
416 | 291 | 529.4 | 223.4 | 276.2 | 217 | 69.9 | 62 | 68.6 | 115.7 | 56.9 | 102.7
417 | 292 | 529.4 | 224 | 276.9 | 217.6 | 70.2 | 62.2 | 69 | 116.2 | 57.1 | 103
418 | 293 | 529.4 | 224.6 | 277.7 | 218.2 | 70.4 | 62.5 | 69.3 | 116.5 | 57.3 | 103.4
419 | 294 | 529.4 | 225.2 | 278.4 | 218.8 | 70.6 | 62.7 | 69.6 | 116.8 | 57.5 | 103.8
420 | 295 | 529.5 | 225.8 | 279.2 | 219.5 | 70.8 | 63 | 69.9 | 117.3 | 57.7 | 104.2
421 | 296 | 529.5 | 226.4 | 280 | 220.1 | 71 | 63.3 | 70.3 | 117.7 | 58 | 104.6
422 | 297 | 529.5 | 227 | 280.8 | 220.7 | 71.2 | 63.5 | 70.6 | 118.1 | 58.2 | 104.9
423 | 298 | 529.4 | 227.7 | 281.5 | 221.3 | 71.5 | 63.8 | 70.9 | 118.7 | 58.4 | 105.3
424 | 299 | 529.4 | 228.3 | 282.2 | 221.9 | 71.7 | 64.1 | 71.2 | 119.2 | 58.6 | 105.7
425 | 300 | 529.4 | 228.9 | 282.9 | 222.5 | 71.9 | 64.3 | 71.6 | 119.6 | 58.8 | 106.1
426 | 301 | 529.4 | 229.5 | 283.7 | 223.1 | 72.2 | 64.6 | 71.9 | 119.9 | 59.1 | 106.4
427 | 302 | 529.4 | 230.1 | 284.4 | 223.7 | 72.4 | 64.9 | 72.2 | 120.4 | 59.3 | 106.8
428 | 303 | 529.4 | 230.7 | 285.2 | 224.3 | 72.6 | 65.1 | 72.6 | 120.7 | 59.5 | 107.2
429 | 304 | 529.4 | 231.3 | 285.9 | 224.9 | 72.9 | 65.4 | 72.9 | 120.9 | 59.7 | 107.6
430 | 305 | 529.4 | 231.9 | 286.6 | 225.5 | 73.1 | 65.7 | 73.2 | 121.3 | 59.9 | 107.9
431 | 306 | 529.4 | 232.6 | 287.2 | 226.1 | 73.4 | 66 | 73.6 | 121.8 | 60.2 | 108.3
432 | 307 | 529.3 | 233.2 | 288 | 226.7 | 73.7 | 66.3 | 73.9 | 122.4 | 60.4 | 108.7
433 | 308 | 529.3 | 233.8 | 288.7 | 227.3 | 73.9 | 66.5 | 74.2 | 122.9 | 60.6 | 109
434 | 309 | 529.4 | 234.4 | 289.4 | 228 | 74.2 | 66.8 | 74.6 | 123.2 | 60.9 | 109.4
435 | 310 | 529.4 | 235 | 290.1 | 228.6 | 74.4 | 67.1 | 74.9 | 123.7 | 61.1 | 109.8
436 | 311 | 529.4 | 235.6 | 290.9 | 229.2 | 74.6 | 67.4 | 75.3 | 124.3 | 61.3 | 110.1
437 | 312 | 529.4 | 236.2 | 291.6 | 229.8 | 74.8 | 67.6 | 75.6 | 124.6 | 61.5 | 110.5
438 | 313 | 529.4 | 236.8 | 292.3 | 230.4 | 75.1 | 67.9 | 76 | 125.2 | 61.8 | 110.9
439 | 314 | 529.3 | 237.4 | 293 | 231 | 75.4 | 68.2 | 76.3 | 125.7 | 62 | 111.3
440 | 315 | 529.3 | 238 | 293.7 | 231.6 | 75.6 | 68.5 | 76.6 | 126.1 | 62.2 | 111.6
441 | 316 | 529.3 | 238.6 | 294.4 | 232.2 | 75.8 | 68.8 | 77 | 126.7 | 62.5 | 112
442 | 317 | 529.3 | 239.2 | 295 | 232.8 | 76.1 | 69.1 | 77.3 | 127.1 | 62.7 | 112.4
443 | 318 | 529.4 | 239.8 | 295.7 | 233.3 | 76.4 | 69.4 | 77.6 | 127.3 | 62.9 | 112.7
444 | 319 | 529.4 | 240.4 | 296.4 | 233.9 | 76.6 | 69.6 | 78 | 127.6 | 63.2 | 113.1
445 | 320 | 529.3 | 241 | 297.1 | 234.4 | 76.9 | 69.9 | 78.3 | 128 | 63.4 | 113.5
446 | 321 | 529.3 | 241.6 | 297.8 | 235 | 77.1 | 70.2 | 78.6 | 128.7 | 63.6 | 113.8
447 | 322 | 529.4 | 242.1 | 298.5 | 235.6 | 77.3 | 70.5 | 79 | 129.2 | 63.9 | 114.2
448 | 323 | 529.4 | 242.7 | 299.2 | 236.2 | 77.6 | 70.8 | 79.3 | 129.5 | 64.1 | 114.6
449 | 324 | 529.3 | 243.3 | 299.9 | 236.7 | 77.8 | 71.1 | 79.7 | 129.6 | 64.3 | 114.9
450 | 325 | 529.3 | 243.9 | 300.5 | 237.3 | 78.1 | 71.4 | 80 | 129.7 | 64.6 | 115.3
451 | 326 | 529.3 | 244.5 | 301.2 | 237.9 | 78.3 | 71.7 | 80.4 | 130.1 | 64.8 | 115.7
452 | 327 | 529.3 | 245.1 | 301.8 | 238.5 | 78.5 | 71.9 | 80.7 | 130.4 | 65.1 | 116.1
453 | 328 | 529.4 | 245.7 | 302.6 | 239 | 78.7 | 72.2 | 81 | 130.8 | 65.3 | 116.4
454 | 329 | 529.4 | 246.3 | 303.3 | 239.6 | 78.9 | 72.4 | 81.4 | 131.1 | 65.6 | 116.8
455 | 330 | 529.4 | 246.9 | 303.9 | 240.2 | 79.2 | 72.7 | 81.7 | 131.5 | 65.8 | 117.1
456 | 331 | 529.4 | 247.5 | 304.6 | 240.8 | 79.4 | 73 | 82.1 | 131.8 | 66.1 | 117.5
457 | 332 | 529.4 | 248 | 305.3 | 241.3 | 79.6 | 73.3 | 82.4 | 132.3 | 66.4 | 117.9
458 | 333 | 529.4 | 248.6 | 306 | 241.9 | 79.9 | 73.6 | 82.7 | 132.8 | 66.6 | 118.2
459 | 334 | 529.4 | 249.2 | 306.6 | 242.5 | 80.1 | 73.9 | 83.1 | 132.9 | 66.9 | 118.6
460 | 335 | 529.4 | 249.8 | 307.2 | 243.1 | 80.4 | 74.2 | 83.4 | 133 | 67.1 | 118.9
461 | 336 | 529.4 | 250.4 | 307.9 | 243.6 | 80.7 | 74.5 | 83.8 | 133.2 | 67.4 | 119.3
462 | 337 | 529.4 | 251 | 308.5 | 244.2 | 81 | 74.9 | 84.1 | 133.5 | 67.7 | 119.6
463 | 338 | 529.3 | 251.6 | 309.2 | 244.7 | 81.4 | 75.2 | 84.4 | 134 | 67.9 | 120
464 | 339 | 529.2 | 252.2 | 309.8 | 245.3 | 81.7 | 75.5 | 84.8 | 134.3 | 68.2 | 120.3
465 | 340 | 529.2 | 252.8 | 310.4 | 245.9 | 82 | 75.8 | 85.1 | 134.8 | 68.4 | 120.6
466 | 341 | 529.2 | 253.3 | 311.1 | 246.5 | 82.2 | 76.1 | 85.5 | 135.1 | 68.7 | 121
467 | 342 | 529.1 | 253.9 | 311.7 | 247 | 82.5 | 76.4 | 85.8 | 135.3 | 69 | 121.4
468 | 343 | 529.1 | 254.5 | 312.4 | 247.5 | 82.8 | 76.8 | 86.1 | 135.6 | 69.2 | 121.7
469 | 344 | 529.1 | 255 | 313 | 248.1 | 83.1 | 77 | 86.5 | 135.8 | 69.5 | 122
470 | 345 | 529.1 | 255.6 | 313.6 | 248.7 | 83.4 | 77.3 | 86.8 | 136.1 | 69.8 | 122.4
471 | 346 | 529.1 | 256.2 | 314.3 | 249.2 | 83.6 | 77.6 | 87.2 | 136.5 | 70.1 | 122.7
472 | 347 | 529.1 | 256.8 | 314.9 | 249.7 | 83.8 | 77.9 | 87.5 | 136.8 | 70.3 | 123.1
473 | 348 | 529.1 | 257.3 | 315.5 | 250.3 | 84.1 | 78.2 | 87.9 | 137.2 | 70.6 | 123.4
474 | 349 | 529.1 | 257.9 | 316.1 | 250.8 | 84.4 | 78.5 | 88.2 | 137.7 | 70.9 | 123.7
475 | 350 | 529.1 | 258.5 | 316.7 | 251.4 | 84.7 | 78.8 | 88.5 | 138.2 | 71.2 | 124.1
476 | 351 | 529.1 | 259.1 | 317.3 | 251.9 | 85.1 | 79.1 | 88.9 | 138.6 | 71.4 | 124.4
477 | 352 | 529.1 | 259.6 | 317.9 | 252.5 | 85.6 | 79.5 | 89.2 | 139.1 | 71.7 | 124.7
478 | 353 | 529.1 | 260.2 | 318.6 | 253 | 85.9 | 79.9 | 89.6 | 139.3 | 72 | 125
479 | 354 | 529.1 | 260.8 | 319.2 | 253.5 | 86.2 | 80.2 | 89.9 | 139.8 | 72.2 | 125.4
480 | 355 | 529.2 | 261.3 | 319.9 | 254 | 86.5 | 80.5 | 90.2 | 140.1 | 72.5 | 125.7
481 | 356 | 529.2 | 261.9 | 320.5 | 254.6 | 86.8 | 80.8 | 90.6 | 140.7 | 72.8 | 126
482 | 357 | 529.2 | 262.5 | 321.1 | 255.2 | 87.1 | 81.1 | 90.9 | 141.1 | 73.1 | 126.3
483 | 358 | 529.2 | 263 | 321.7 | 255.8 | 87.4 | 81.4 | 91.3 | 141.5 | 73.4 | 126.6
484 | 359 | 529.3 | 263.6 | 322.3 | 256.3 | 87.7 | 81.7 | 91.6 | 141.9 | 73.6 | 127
485 | 360 | 529.3 | 264.2 | 322.9 | 256.8 | 88 | 82 | 92 | 142.3 | 73.9 | 127.3
486 | 361 | 529.4 | 264.7 | 323.5 | 257.3 | 88.3 | 82.3 | 92.3 | 142.5 | 74.2 | 127.6
487 | 362 | 529.3 | 265.3 | 324.1 | 257.8 | 88.6 | 82.6 | 92.6 | 142.8 | 74.5 | 127.9
488 | 363 | 529.3 | 265.8 | 324.8 | 258.3 | 88.9 | 82.9 | 93 | 143 | 74.8 | 128.2
489 | 364 | 529.3 | 266.4 | 325.5 | 258.9 | 89.2 | 83.2 | 93.4 | 143.4 | 75.1 | 128.5
490 | 365 | 529.3 | 266.9 | 326.1 | 259.4 | 89.5 | 83.5 | 93.7 | 144.1 | 75.4 | 128.8
491 | 366 | 529.2 | 267.4 | 326.7 | 259.9 | 89.8 | 83.8 | 94.1 | 144.6 | 75.6 | 129.1
492 | 367 | 529.2 | 268 | 327.3 | 260.4 | 90.1 | 84.1 | 94.4 | 144.8 | 75.9 | 129.4
493 | 368 | 529.3 | 268.6 | 327.9 | 260.9 | 90.4 | 84.4 | 94.8 | 145 | 76.2 | 129.8
494 | 369 | 529.3 | 269.1 | 328.4 | 261.5 | 90.7 | 84.7 | 95.2 | 145.1 | 76.5 | 130
495 | 370 | 529.2 | 269.7 | 329 | 262 | 91 | 85 | 95.5 | 145.5 | 76.8 | 130.3
496 | 371 | 529.2 | 270.3 | 329.6 | 262.6 | 91.3 | 85.3 | 95.9 | 145.9 | 77.1 | 130.6
497 | 372 | 529.2 | 270.8 | 330.1 | 263.1 | 91.7 | 85.7 | 96.3 | 146.3 | 77.4 | 130.9
498 | 373 | 529.1 | 271.4 | 330.7 | 263.6 | 92 | 86 | 96.7 | 146.7 | 77.7 | 131.2
499 | 374 | 529.1 | 271.9 | 331.3 | 264.2 | 92.3 | 86.3 | 97.1 | 147 | 78 | 131.5
500 | 375 | 529.1 | 272.5 | 331.8 | 264.7 | 92.6 | 86.6 | 97.5 | 147.4 | 78.2 | 131.7
501 | 376 | 529.1 | 273 | 332.4 | 265.2 | 92.9 | 86.9 | 97.9 | 147.9 | 78.5 | 132
502 | 377 | 529.1 | 273.5 | 332.9 | 265.7 | 93.2 | 87.2 | 98.3 | 148.2 | 78.8 | 132.3
503 | 378 | 529 | 274.1 | 333.5 | 266.2 | 93.5 | 87.5 | 98.7 | 148.2 | 79.1 | 132.6
504 | 379 | 529 | 274.7 | 334 | 266.8 | 93.9 | 87.8 | 99.1 | 148.3 | 79.4 | 132.8
505 | 380 | 529 | 275.2 | 334.6 | 267.3 | 94.3 | 88.1 | 99.5 | 148.6 | 79.7 | 133.1
506 | 381 | 528.9 | 275.7 | 335.1 | 267.8 | 94.6 | 88.4 | 100 | 149 | 80 | 133.4
507 | 382 | 528.9 | 276.3 | 335.6 | 268.3 | 94.9 | 88.8 | 100.4 | 149.4 | 80.3 | 133.7
508 | 383 | 528.9 | 276.8 | 336.2 | 268.9 | 95.2 | 89.1 | 100.8 | 149.7 | 80.6 | 133.9
509 | 384 | 528.9 | 277.4 | 336.8 | 269.4 | 95.5 | 89.4 | 101.3 | 149.8 | 80.9 | 134.2
510 | 385 | 528.9 | 277.9 | 337.3 | 269.8 | 95.9 | 89.7 | 101.7 | 150.3 | 81.2 | 134.5
511 | 386 | 528.9 | 278.4 | 337.8 | 270.3 | 96.2 | 90 | 102.2 | 150.8 | 81.5 | 134.8
512 | 387 | 528.9 | 279 | 338.4 | 270.8 | 96.5 | 90.3 | 102.6 | 151.3 | 81.8 | 135
513 | 388 | 528.9 | 279.5 | 339 | 271.3 | 96.8 | 90.6 | 103.1 | 151.9 | 82.1 | 135.3
514 | 389 | 528.9 | 280 | 339.6 | 271.9 | 97.1 | 90.9 | 103.5 | 152.3 | 82.4 | 135.6
515 | 390 | 528.9 | 280.6 | 340.1 | 272.4 | 97.4 | 91.2 | 104 | 152.5 | 82.7 | 135.9
516 | 391 | 528.9 | 281.1 | 340.7 | 272.9 | 97.7 | 91.5 | 104.5 | 152.7 | 83 | 136.2
517 | 392 | 528.9 | 281.6 | 341.2 | 273.5 | 98 | 91.8 | 105 | 153.2 | 83.3 | 136.5
518 | 393 | 528.9 | 282.1 | 341.8 | 273.9 | 98.3 | 92.1 | 105.4 | 153.9 | 83.6 | 136.7
519 | 394 | 528.9 | 282.7 | 342.3 | 274.4 | 98.6 | 92.4 | 105.9 | 154.3 | 83.9 | 137
520 | 395 | 528.9 | 283.2 | 342.9 | 274.9 | 98.9 | 92.7 | 106.4 | 154.8 | 84.2 | 137.3
521 | 396 | 529 | 283.7 | 343.4 | 275.4 | 99.2 | 92.9 | 106.9 | 155.2 | 84.5 | 137.6
522 | 397 | 528.9 | 284.2 | 343.9 | 275.9 | 99.5 | 93.3 | 107.4 | 155.8 | 84.8 | 137.9
523 | 398 | 528.9 | 284.7 | 344.5 | 276.3 | 99.8 | 93.6 | 107.8 | 156.3 | 85.1 | 138.2
524 | 399 | 528.9 | 285.2 | 345 | 276.8 | 100.1 | 93.9 | 108.3 | 157 | 85.4 | 138.4
525 | 400 | 528.9 | 285.7 | 345.5 | 277.3 | 100.4 | 94.2 | 108.8 | 157.5 | 85.7 | 138.7
526 | 401 | 528.9 | 286.3 | 346.1 | 277.8 | 100.7 | 94.4 | 109.3 | 157.8 | 86 | 139
527 | 402 | 528.9 | 286.8 | 346.6 | 278.3 | 100.9 | 94.7 | 109.8 | 158.4 | 86.3 | 139.3
528 | 403 | 528.9 | 287.3 | 347.2 | 278.8 | 101.2 | 95 | 110.3 | 159.1 | 86.6 | 139.6
529 | 404 | 528.9 | 287.8 | 347.7 | 279.3 | 101.5 | 95.3 | 110.7 | 159.5 | 86.9 | 139.9
530 | 405 | 528.9 | 288.3 | 348.2 | 279.7 | 101.7 | 95.6 | 111.2 | 160 | 87.2 | 140.2
531 | 406 | 528.9 | 288.8 | 348.7 | 280.3 | 102.1 | 95.9 | 111.7 | 160.6 | 87.5 | 140.5
532 | 407 | 528.9 | 289.3 | 349.2 | 280.8 | 102.4 | 96.3 | 112.1 | 161.1 | 87.9 | 140.8
533 | 408 | 528.8 | 289.8 | 349.7 | 281.3 | 102.7 | 96.6 | 112.6 | 161.5 | 88.2 | 141.1
534 | 409 | 528.8 | 290.3 | 350.2 | 281.7 | 103 | 96.9 | 113.1 | 162 | 88.5 | 141.4
535 | 410 | 528.8 | 290.8 | 350.7 | 282.2 | 103.4 | 97.2 | 113.5 | 162.7 | 88.8 | 141.7
536 | 411 | 528.8 | 291.3 | 351.2 | 282.7 | 103.6 | 97.5 | 114 | 163.2 | 89.1 | 142
537 | 412 | 528.9 | 291.8 | 351.7 | 283.2 | 103.9 | 97.8 | 114.4 | 163.6 | 89.4 | 142.3
538 | 413 | 528.9 | 292.3 | 352.2 | 283.6 | 104.2 | 98.2 | 114.9 | 164 | 89.7 | 142.6
539 | 414 | 528.9 | 292.8 | 352.7 | 284.1 | 104.5 | 98.5 | 115.4 | 164.5 | 90 | 142.9
540 | 415 | 528.9 | 293.3 | 353.2 | 284.6 | 104.9 | 98.8 | 115.8 | 165.1 | 90.3 | 143.2
541 | 416 | 528.9 | 293.8 | 353.7 | 285.1 | 105.2 | 99.2 | 116.3 | 165.7 | 90.6 | 143.5
542 | 417 | 528.9 | 294.3 | 354.2 | 285.6 | 105.5 | 99.5 | 116.7 | 166.1 | 90.9 | 143.8
543 | 418 | 528.9 | 294.8 | 354.7 | 286 | 105.8 | 99.9 | 117.2 | 166.5 | 91.2 | 144.1
544 | 419 | 528.9 | 295.3 | 355.2 | 286.5 | 106.2 | 100.3 | 117.7 | 167 | 91.5 | 144.4
545 | 420 | 528.9 | 295.8 | 355.7 | 287 | 106.5 | 100.7 | 118.1 | 167.3 | 91.8 | 144.7
546 | 421 | 528.9 | 296.3 | 356.2 | 287.5 | 106.8 | 101.1 | 118.6 | 167.8 | 92.1 | 145
547 | 422 | 528.9 | 296.8 | 356.7 | 287.9 | 107.2 | 101.5 | 119.1 | 168.5 | 92.4 | 145.3
548 | 423 | 528.9 | 297.3 | 357.2 | 288.4 | 107.5 | 101.9 | 119.6 | 168.9 | 92.7 | 145.6
549 | 424 | 528.9 | 297.8 | 357.6 | 288.9 | 107.9 | 102.4 | 120 | 169.1 | 93 | 145.9
550 | 425 | 528.8 | 298.3 | 358.1 | 289.4 | 108.3 | 102.9 | 120.5 | 169.4 | 93.3 | 146.2
551 | 426 | 528.9 | 298.8 | 358.5 | 289.8 | 108.7 | 103.4 | 121 | 169.8 | 93.7 | 146.5
552 | 427 | 528.8 | 299.2 | 359 | 290.3 | 109 | 103.8 | 121.5 | 170.4 | 94 | 146.9
553 | 428 | 528.8 | 299.7 | 359.5 | 290.8 | 109.3 | 104.3 | 121.9 | 171.1 | 94.3 | 147.2
554 | 429 | 528.8 | 300.2 | 360 | 291.2 | 109.7 | 104.8 | 122.4 | 171.9 | 94.6 | 147.5
555 | 430 | 528.8 | 300.6 | 360.5 | 291.7 | 110.1 | 105.3 | 122.9 | 172.7 | 94.9 | 147.8
556 | 431 | 528.8 | 301.1 | 360.9 | 292.2 | 110.5 | 105.8 | 123.4 | 173.2 | 95.2 | 148.2
557 | 432 | 528.8 | 301.6 | 361.3 | 292.6 | 110.9 | 106.3 | 123.9 | 173.5 | 95.5 | 148.5
558 | 433 | 528.8 | 302.1 | 361.8 | 293.1 | 111.3 | 106.8 | 124.3 | 174.2 | 95.8 | 148.8
559 | 434 | 528.7 | 302.6 | 362.3 | 293.5 | 111.7 | 107.4 | 124.8 | 174.9 | 96.1 | 149.1
560 | 435 | 528.7 | 303 | 362.7 | 294 | 112.1 | 107.9 | 125.3 | 175.6 | 96.4 | 149.5
561 | 436 | 528.7 | 303.5 | 363.2 | 294.5 | 112.5 | 108.4 | 125.8 | 176.2 | 96.7 | 149.8
562 | 437 | 528.7 | 304 | 363.6 | 294.9 | 112.9 | 108.9 | 126.3 | 176.9 | 97.1 | 150.2
563 | 438 | 528.7 | 304.5 | 364.1 | 295.4 | 113.3 | 109.4 | 126.8 | 177.5 | 97.4 | 150.5
564 | 439 | 528.7 | 305 | 364.5 | 295.8 | 113.7 | 109.9 | 127.3 | 178.1 | 97.7 | 150.8
565 | 440 | 528.7 | 305.4 | 365 | 296.3 | 114.1 | 110.4 | 127.8 | 178.8 | 98 | 151.2
566 | 441 | 528.6 | 305.9 | 365.4 | 296.8 | 114.5 | 110.9 | 128.2 | 179.4 | 98.3 | 151.5
567 | 442 | 528.6 | 306.4 | 365.8 | 297.2 | 114.9 | 111.4 | 128.7 | 180.2 | 98.6 | 151.9
568 | 443 | 528.6 | 306.8 | 366.3 | 297.6 | 115.3 | 111.9 | 129.2 | 180.8 | 98.9 | 152.2
569 | 444 | 528.5 | 307.3 | 366.7 | 298.1 | 115.7 | 112.3 | 129.7 | 181.3 | 99.3 | 152.6
570 | 445 | 528.5 | 307.8 | 367.1 | 298.5 | 116.1 | 112.8 | 130.2 | 181.8 | 99.6 | 153
571 | 446 | 528.4 | 308.2 | 367.6 | 299 | 116.4 | 113.3 | 130.7 | 182.2 | 99.9 | 153.3
572 | 447 | 528.4 | 308.7 | 368 | 299.5 | 116.8 | 113.7 | 131.2 | 182.6 | 100.2 | 153.7
573 | 448 | 528.3 | 309.1 | 368.4 | 299.8 | 117.2 | 114.2 | 131.7 | 183.1 | 100.5 | 154.1
574 | 449 | 528.3 | 309.6 | 368.8 | 300.3 | 117.6 | 114.7 | 132.2 | 183.6 | 100.8 | 154.4
575 | 450 | 528.3 | 310 | 369.3 | 300.7 | 118 | 115.2 | 132.7 | 184.1 | 101.1 | 154.8
576 | 451 | 528.3 | 310.5 | 369.7 | 301.2 | 118.4 | 115.6 | 133.2 | 184.7 | 101.4 | 155.2
577 | 452 | 528.3 | 311 | 370.1 | 301.7 | 118.8 | 116.1 | 133.7 | 185.2 | 101.8 | 155.6
578 | 453 | 528.3 | 311.5 | 370.5 | 302.1 | 119.2 | 116.6 | 134.2 | 185.7 | 102.1 | 155.9
579 | 454 | 528.3 | 311.9 | 370.9 | 302.6 | 119.6 | 117.1 | 134.7 | 186.2 | 102.4 | 156.3
580 | 455 | 528.3 | 312.3 | 371.4 | 303 | 120 | 117.5 | 135.2 | 186.8 | 102.7 | 156.7
581 | 456 | 528.4 | 312.8 | 371.8 | 303.4 | 120.4 | 118 | 135.7 | 187.5 | 103 | 157.1
582 | 457 | 528.4 | 313.3 | 372.2 | 303.9 | 120.7 | 118.5 | 136.2 | 187.9 | 103.3 | 157.5
583 | 458 | 528.4 | 313.7 | 372.6 | 304.3 | 121.1 | 118.9 | 136.7 | 188.4 | 103.6 | 157.9
584 | 459 | 528.4 | 314.1 | 373.1 | 304.7 | 121.5 | 119.4 | 137.2 | 189.1 | 104 | 158.3
585 | 460 | 528.5 | 314.6 | 373.5 | 305.2 | 121.8 | 119.9 | 137.7 | 189.5 | 104.3 | 158.7
586 | 461 | 528.5 | 315 | 373.9 | 305.6 | 122.2 | 120.3 | 138.2 | 189.9 | 104.6 | 159.1
587 | 462 | 528.5 | 315.5 | 374.3 | 306 | 122.6 | 120.8 | 138.7 | 190.4 | 104.9 | 159.5
588 | 463 | 528.5 | 315.9 | 374.8 | 306.5 | 123 | 121.3 | 139.3 | 191.1 | 105.2 | 159.9
589 | 464 | 528.5 | 316.4 | 375.2 | 307 | 123.4 | 121.7 | 139.8 | 191.5 | 105.5 | 160.3
590 | 465 | 528.5 | 316.8 | 375.6 | 307.4 | 123.8 | 122.2 | 140.3 | 191.7 | 105.8 | 160.7
591 | 466 | 528.5 | 317.2 | 376 | 307.8 | 124.2 | 122.7 | 140.8 | 192.1 | 106.2 | 161.2
592 | 467 | 528.5 | 317.7 | 376.4 | 308.2 | 124.6 | 123.2 | 141.3 | 192.8 | 106.5 | 161.6
593 | 468 | 528.5 | 318.1 | 376.8 | 308.7 | 125 | 123.7 | 141.8 | 193.4 | 106.8 | 162
594 | 469 | 528.5 | 318.5 | 377.2 | 309.1 | 125.5 | 124.1 | 142.3 | 193.8 | 107.1 | 162.4
595 | 470 | 528.5 | 319 | 377.6 | 309.5 | 125.8 | 124.6 | 142.9 | 194.5 | 107.4 | 162.9
596 | 471 | 528.5 | 319.4 | 378 | 309.9 | 126.3 | 125.1 | 143.4 | 194.9 | 107.7 | 163.3
597 | 472 | 528.5 | 319.8 | 378.3 | 310.3 | 126.6 | 125.5 | 143.9 | 195.3 | 108.1 | 163.7
598 | 473 | 528.5 | 320.3 | 378.7 | 310.8 | 127.1 | 126 | 144.4 | 195.8 | 108.4 | 164.2
599 | 474 | 528.5 | 320.7 | 379.1 | 311.2 | 127.5 | 126.5 | 144.9 | 196.6 | 108.7 | 164.6
600 | 475 | 528.5 | 321.1 | 379.5 | 311.6 | 127.9 | 126.9 | 145.5 | 197.3 | 109 | 165
601 | 476 | 528.5 | 321.5 | 380 | 312 | 128.3 | 127.4 | 146 | 197.6 | 109.3 | 165.5
602 | 477 | 528.5 | 322 | 380.3 | 312.4 | 128.7 | 127.9 | 146.5 | 198 | 109.7 | 165.9
603 | 478 | 528.5 | 322.4 | 380.8 | 312.8 | 129.1 | 128.4 | 147 | 198.7 | 110 | 166.4
604 | 479 | 528.5 | 322.9 | 381.1 | 313.2 | 129.6 | 128.8 | 147.6 | 199.2 | 110.3 | 166.8
605 | 480 | 528.5 | 323.3 | 381.5 | 313.6 | 130 | 129.3 | 148.1 | 199.7 | 110.6 | 167.3
606 | 481 | 528.5 | 323.7 | 381.9 | 314 | 130.4 | 129.8 | 148.6 | 200.3 | 111 | 167.7
607 | 482 | 528.5 | 324.1 | 382.4 | 314.4 | 130.8 | 130.2 | 149.2 | 200.9 | 111.3 | 168.2
608 | 483 | 528.5 | 324.5 | 382.9 | 314.8 | 131.2 | 130.7 | 149.7 | 201.4 | 111.6 | 168.7
609 | 484 | 528.5 | 324.9 | 383.2 | 315.3 | 131.6 | 131.2 | 150.2 | 201.8 | 111.9 | 169.1
610 | 485 | 528.5 | 325.3 | 383.6 | 315.6 | 132.1 | 131.6 | 150.8 | 202.1 | 112.2 | 169.5
611 | 486 | 528.5 | 325.7 | 384 | 316 | 132.5 | 132.1 | 151.3 | 202.7 | 112.6 | 170
612 | 487 | 528.6 | 326.1 | 384.4 | 316.4 | 132.9 | 132.6 | 151.9 | 203.3 | 112.9 | 170.5
613 | 488 | 528.5 | 326.5 | 384.8 | 316.8 | 133.4 | 133 | 152.4 | 203.9 | 113.2 | 170.9
614 | 489 | 528.5 | 326.9 | 385.2 | 317.2 | 133.8 | 133.5 | 153 | 204.4 | 113.5 | 171.4
615 | 490 | 528.5 | 327.3 | 385.6 | 317.6 | 134.2 | 134 | 153.5 | 204.8 | 113.8 | 171.9
616 | 491 | 528.5 | 327.7 | 386 | 318 | 134.6 | 134.4 | 154 | 205.1 | 114.2 | 172.4
617 | 492 | 528.5 | 328.1 | 386.4 | 318.5 | 135.1 | 134.9 | 154.6 | 205.5 | 114.5 | 172.8
618 | 493 | 528.4 | 328.5 | 386.7 | 318.9 | 135.6 | 135.4 | 155.1 | 205.9 | 114.8 | 173.3
619 | 494 | 528.4 | 329 | 387.1 | 319.3 | 136 | 135.9 | 155.6 | 206.2 | 115.1 | 173.7
620 | 495 | 528.3 | 329.4 | 387.5 | 319.6 | 136.5 | 136.4 | 156.2 | 206.6 | 115.4 | 174.2
621 | 496 | 528.2 | 329.8 | 387.8 | 320 | 137 | 136.8 | 156.7 | 207 | 115.8 | 174.7
622 | 497 | 528.2 | 330.2 | 388.1 | 320.4 | 137.5 | 137.3 | 157.2 | 207.3 | 116.1 | 175.1
623 | 498 | 528.1 | 330.6 | 388.5 | 320.8 | 138 | 137.8 | 157.8 | 207.7 | 116.4 | 175.6
624 | 499 | 528.1 | 331 | 388.9 | 321.2 | 138.5 | 138.3 | 158.3 | 208.2 | 116.7 | 176.1
625 | 500 | 528 | 331.4 | 389.2 | 321.6 | 139 | 138.8 | 158.8 | 208.6 | 117 | 176.6
626 | 501 | 528 | 331.8 | 389.6 | 322 | 139.5 | 139.3 | 159.3 | 209 | 117.3 | 177
627 | 502 | 527.9 | 332.2 | 389.9 | 322.4 | 140 | 139.7 | 159.9 | 209.5 | 117.6 | 177.5
628 | 503 | 527.9 | 332.6 | 390.2 | 322.8 | 140.5 | 140.2 | 160.4 | 210.3 | 117.9 | 178
629 | 504 | 527.9 | 333 | 390.6 | 323.2 | 141 | 140.7 | 160.9 | 211 | 118.2 | 178.5
630 | 505 | 527.9 | 333.4 | 390.9 | 323.6 | 141.5 | 141.2 | 161.4 | 211.5 | 118.6 | 179
631 | 506 | 527.9 | 333.8 | 391.2 | 324 | 142 | 141.7 | 162 | 211.9 | 118.9 | 179.5
632 | 507 | 527.9 | 334.2 | 391.6 | 324.4 | 142.5 | 142.1 | 162.5 | 212.3 | 119.2 | 180
633 | 508 | 527.9 | 334.6 | 392 | 324.8 | 143 | 142.6 | 163 | 212.6 | 119.5 | 180.5
634 | 509 | 527.9 | 335 | 392.3 | 325.1 | 143.5 | 143.1 | 163.6 | 213.3 | 119.8 | 181
635 | 510 | 527.9 | 335.3 | 392.6 | 325.5 | 144 | 143.6 | 164.1 | 214 | 120.1 | 181.5
636 | 511 | 527.9 | 335.7 | 393 | 325.9 | 144.5 | 144 | 164.6 | 214.6 | 120.4 | 182
637 | 512 | 527.9 | 336.1 | 393.3 | 326.3 | 145 | 144.5 | 165.1 | 215.1 | 120.7 | 182.5
638 | 513 | 527.9 | 336.5 | 393.7 | 326.6 | 145.6 | 145 | 165.6 | 215.6 | 121 | 183
639 | 514 | 527.9 | 336.9 | 394 | 327 | 146.1 | 145.5 | 166.1 | 216.2 | 121.3 | 183.5
640 | 515 | 527.9 | 337.3 | 394.3 | 327.4 | 146.6 | 146 | 166.6 | 216.6 | 121.6 | 184
641 | 516 | 527.9 | 337.7 | 394.6 | 327.8 | 147.1 | 146.5 | 167.2 | 217 | 122 | 184.5
642 | 517 | 528 | 338.1 | 395 | 328.2 | 147.6 | 146.9 | 167.7 | 217.5 | 122.3 | 185
643 | 518 | 528 | 338.4 | 395.4 | 328.6 | 148 | 147.4 | 168.2 | 218.2 | 122.6 | 185.6
644 | 519 | 528 | 338.8 | 395.7 | 328.9 | 148.5 | 147.9 | 168.7 | 219 | 122.9 | 186.1
645 | 520 | 528 | 339.2 | 396 | 329.3 | 149 | 148.3 | 169.2 | 219.7 | 123.2 | 186.6
646 | 521 | 528.1 | 339.6 | 396.3 | 329.7 | 149.5 | 148.8 | 169.7 | 220.1 | 123.5 | 187.1
647 | 522 | 528.1 | 339.9 | 396.7 | 330.1 | 150 | 149.3 | 170.3 | 220.5 | 123.8 | 187.6
648 | 523 | 528.1 | 340.3 | 397 | 330.4 | 150.5 | 149.8 | 170.8 | 221.2 | 124.1 | 188.2
649 | 524 | 528.1 | 340.7 | 397.3 | 330.8 | 151 | 150.3 | 171.4 | 221.6 | 124.4 | 188.7
650 | 525 | 528.1 | 341 | 397.7 | 331.1 | 151.5 | 150.8 | 171.9 | 222.2 | 124.7 | 189.2
651 | 526 | 528.1 | 341.4 | 398 | 331.5 | 152 | 151.3 | 172.4 | 222.7 | 124.9 | 189.7
652 | 527 | 528.2 | 341.8 | 398.3 | 331.9 | 152.4 | 151.8 | 173 | 223.3 | 125.2 | 190.2
653 | 528 | 528.2 | 342.2 | 398.7 | 332.2 | 152.9 | 152.2 | 173.5 | 223.8 | 125.5 | 190.7
654 | 529 | 528.2 | 342.5 | 399.1 | 332.6 | 153.3 | 152.7 | 174.1 | 224.5 | 125.8 | 191.2
655 | 530 | 528.2 | 342.8 | 399.5 | 332.9 | 153.8 | 153.2 | 174.6 | 225 | 126.1 | 191.7
656 | 531 | 528.3 | 343.2 | 399.8 | 333.2 | 154.2 | 153.7 | 175.1 | 225.4 | 126.4 | 192.1
657 | 532 | 528.2 | 343.5 | 400.2 | 333.6 | 154.7 | 154.1 | 175.6 | 225.8 | 126.7 | 192.6
658 | 533 | 528.3 | 343.9 | 400.5 | 334 | 155.1 | 154.6 | 176.2 | 226.2 | 127 | 193.1
659 | 534 | 528.2 | 344.3 | 400.8 | 334.3 | 155.6 | 155.1 | 176.7 | 226.7 | 127.2 | 193.5
660 | 535 | 528.2 | 344.6 | 401.2 | 334.8 | 156.1 | 155.6 | 177.2 | 227.3 | 127.5 | 194
661 | 536 | 528.2 | 345 | 401.4 | 335.1 | 156.6 | 156.1 | 177.7 | 227.9 | 127.8 | 194.5
662 | 537 | 528.2 | 345.3 | 401.7 | 335.4 | 157.1 | 156.6 | 178.3 | 228.5 | 128.1 | 195
663 | 538 | 528.2 | 345.7 | 402.1 | 335.7 | 157.5 | 157.1 | 178.8 | 229 | 128.3 | 195.5
664 | 539 | 528.2 | 346 | 402.4 | 336.1 | 158 | 157.6 | 179.3 | 229.5 | 128.6 | 196.1
665 | 540 | 528.1 | 346.4 | 402.7 | 336.4 | 158.5 | 158.1 | 179.8 | 230.3 | 128.9 | 196.6
666 | 541 | 528 | 346.8 | 403 | 336.8 | 159 | 158.6 | 180.3 | 230.7 | 129.1 | 197.1
667 | 542 | 527.9 | 347.1 | 403.3 | 337.1 | 159.5 | 159.1 | 180.8 | 231.2 | 129.3 | 197.6
668 | 543 | 527.9 | 347.4 | 403.6 | 337.5 | 159.9 | 159.5 | 181.3 | 231.9 | 129.6 | 198.2
669 | 544 | 527.9 | 347.8 | 403.9 | 337.8 | 160.4 | 160.1 | 181.8 | 232.6 | 129.8 | 198.7
670 | 545 | 527.8 | 348.2 | 404.2 | 338.2 | 160.9 | 160.6 | 182.3 | 233.1 | 130.1 | 199.2
671 | 546 | 527.8 | 348.5 | 404.5 | 338.6 | 161.4 | 161 | 182.8 | 233.6 | 130.3 | 199.7
672 | 547 | 527.8 | 348.8 | 404.8 | 338.9 | 161.9 | 161.5 | 183.3 | 234.1 | 130.6 | 200.2
673 | 548 | 527.7 | 349.2 | 405.1 | 339.2 | 162.4 | 162 | 183.8 | 234.8 | 130.8 | 200.7
674 | 549 | 527.7 | 349.5 | 405.4 | 339.6 | 162.8 | 162.5 | 184.3 | 235.5 | 131 | 201.2
675 | 550 | 527.7 | 349.8 | 405.7 | 339.9 | 163.3 | 163 | 184.8 | 236.2 | 131.2 | 201.8
676 | 551 | 527.7 | 350.2 | 406 | 340.3 | 163.8 | 163.5 | 185.3 | 236.8 | 131.4 | 202.3
677 | 552 | 527.7 | 350.6 | 406.2 | 340.6 | 164.4 | 164 | 185.8 | 237.3 | 131.7 | 202.8
678 | 553 | 527.6 | 350.9 | 406.5 | 341 | 164.8 | 164.5 | 186.3 | 237.7 | 131.9 | 203.4
679 | 554 | 527.6 | 351.3 | 406.8 | 341.3 | 165.4 | 165 | 186.7 | 238.3 | 132.1 | 203.9
680 | 555 | 527.6 | 351.6 | 407.1 | 341.7 | 165.9 | 165.5 | 187.2 | 238.7 | 132.3 | 204.5
681 | 556 | 527.6 | 351.9 | 407.4 | 342 | 166.3 | 166 | 187.7 | 239.3 | 132.5 | 205
682 | 557 | 527.6 | 352.3 | 407.7 | 342.3 | 166.8 | 166.4 | 188.2 | 239.9 | 132.7 | 205.5
683 | 558 | 527.6 | 352.6 | 407.9 | 342.7 | 167.3 | 166.9 | 188.7 | 240.6 | 132.9 | 206
684 | 559 | 527.5 | 353 | 408.2 | 343 | 167.9 | 167.4 | 189.2 | 241.2 | 133.1 | 206.6
685 | 560 | 527.5 | 353.3 | 408.4 | 343.4 | 168.4 | 167.9 | 189.7 | 241.7 | 133.3 | 207.1
686 | 561 | 527.5 | 353.6 | 408.7 | 343.7 | 168.9 | 168.4 | 190.1 | 242.4 | 133.5 | 207.6
687 | 562 | 527.5 | 354 | 408.9 | 344 | 169.4 | 168.9 | 190.6 | 243.1 | 133.8 | 208.2
688 | 563 | 527.5 | 354.3 | 409.2 | 344.3 | 169.9 | 169.4 | 191.1 | 243.8 | 134 | 208.7
689 | 564 | 527.5 | 354.6 | 409.5 | 344.7 | 170.4 | 169.9 | 191.6 | 244.5 | 134.2 | 209.2
690 | 565 | 527.5 | 355 | 409.8 | 345 | 170.8 | 170.4 | 192.1 | 245.3 | 134.5 | 209.8
691 | 566 | 527.5 | 355.3 | 410.1 | 345.3 | 171.3 | 170.8 | 192.6 | 246 | 134.8 | 210.3
692 | 567 | 527.5 | 355.6 | 410.3 | 345.7 | 171.8 | 171.3 | 193 | 246.6 | 135.1 | 210.8
693 | 568 | 527.5 | 355.9 | 410.6 | 346 | 172.3 | 171.8 | 193.5 | 247.5 | 135.4 | 211.3
694 | 569 | 527.5 | 356.3 | 410.9 | 346.3 | 172.8 | 172.3 | 194 | 248.4 | 135.7 | 211.9
695 | 570 | 527.5 | 356.6 | 411.1 | 346.7 | 173.3 | 172.8 | 194.5 | 249.3 | 136.1 | 212.4
696 | 571 | 527.5 | 356.9 | 411.4 | 347 | 173.8 | 173.3 | 195 | 251.1 | 136.5 | 212.9
697 | 572 | 527.5 | 357.2 | 411.6 | 347.3 | 174.3 | 173.8 | 195.4 | 253.1 | 136.8 | 213.5
698 | 573 | 527.5 | 357.6 | 411.9 | 347.6 | 174.7 | 174.2 | 195.9 | 254.4 | 137.2 | 214
699 | 574 | 527.5 | 357.9 | 412.2 | 347.9 | 175.2 | 174.7 | 196.4 | 255.5 | 137.6 | 214.6
700 | 575 | 527.5 | 358.2 | 412.5 | 348.2 | 175.6 | 175.2 | 196.9 | 256.4 | 138 | 215.1
701 | 576 | 527.5 | 358.5 | 412.7 | 348.6 | 176.1 | 175.7 | 197.3 | 257.3 | 138.4 | 215.6
702 | 577 | 527.5 | 358.8 | 413 | 348.9 | 176.5 | 176.1 | 197.8 | 258.3 | 138.8 | 216.2
703 | 578 | 527.5 | 359.1 | 413.3 | 349.2 | 177 | 176.6 | 198.3 | 259.2 | 139.2 | 216.7
704 | 579 | 527.5 | 359.4 | 413.5 | 349.5 | 177.5 | 177.1 | 198.8 | 259.9 | 139.6 | 217.2
705 | 580 | 527.5 | 359.7 | 413.8 | 349.8 | 178 | 177.6 | 199.2 | 260.5 | 140 | 217.7
706 | 581 | 527.5 | 360.1 | 414.1 | 350.2 | 178.4 | 178 | 199.7 | 261.3 | 140.4 | 218.3
707 | 582 | 527.5 | 360.3 | 414.3 | 350.5 | 178.9 | 178.5 | 200.2 | 261.9 | 140.8 | 218.8
708 | 583 | 527.5 | 360.7 | 414.6 | 350.8 | 179.3 | 179 | 200.7 | 262.3 | 141.2 | 219.3
709 | 584 | 527.5 | 361 | 414.8 | 351.1 | 179.8 | 179.4 | 201.1 | 262.8 | 141.6 | 219.8
710 | 585 | 527.4 | 361.3 | 415.1 | 351.4 | 180.2 | 179.9 | 201.6 | 263.4 | 142 | 220.3
711 | 586 | 527.4 | 361.6 | 415.4 | 351.7 | 180.7 | 180.4 | 202.1 | 263.9 | 142.4 | 220.8
712 | 587 | 527.4 | 361.9 | 415.6 | 352 | 181.1 | 180.9 | 202.5 | 264.3 | 142.8 | 221.3
713 | 588 | 527.4 | 362.2 | 415.8 | 352.4 | 181.6 | 181.3 | 203 | 264.9 | 143.2 | 221.8
714 | 589 | 527.4 | 362.5 | 416.1 | 352.7 | 182.1 | 181.8 | 203.5 | 265.5 | 143.6 | 222.3
715 | 590 | 527.4 | 362.8 | 416.3 | 353 | 182.6 | 182.3 | 204 | 266 | 144 | 222.8
716 | 591 | 527.5 | 363.1 | 416.6 | 353.3 | 183 | 182.7 | 204.4 | 266.6 | 144.3 | 223.3
717 | 592 | 527.5 | 363.4 | 416.9 | 353.6 | 183.4 | 183.2 | 204.9 | 267 | 144.7 | 223.8
718 | 593 | 527.5 | 363.7 | 417.1 | 353.9 | 183.9 | 183.7 | 205.4 | 267.5 | 145.1 | 224.2
719 | 594 | 527.5 | 364 | 417.4 | 354.3 | 184.3 | 184.1 | 205.9 | 267.9 | 145.5 | 224.7
720 | 595 | 527.5 | 364.3 | 417.7 | 354.5 | 184.8 | 184.6 | 206.4 | 268.2 | 145.9 | 225.2
721 | 596 | 527.4 | 364.6 | 417.9 | 354.8 | 185.2 | 185.1 | 206.8 | 268.9 | 146.3 | 225.6
722 | 597 | 527.4 | 364.9 | 418.1 | 355.1 | 185.7 | 185.5 | 207.3 | 269.5 | 146.6 | 226.1
723 | 598 | 527.4 | 365.2 | 418.3 | 355.4 | 186.2 | 186 | 207.8 | 270.1 | 147 | 226.6
724 | 599 | 527.4 | 365.4 | 418.6 | 355.7 | 186.6 | 186.5 | 208.2 | 270.6 | 147.4 | 227
725 | 600 | 527.3 | 365.7 | 418.8 | 356 | 187 | 187 | 208.7 | 271.1 | 147.8 | 227.5
726 | 601 | 527.3 | 366 | 419 | 356.4 | 187.5 | 187.4 | 209.1 | 271.8 | 148.1 | 227.9
727 | 602 | 527.3 | 366.3 | 419.3 | 356.7 | 187.9 | 187.9 | 209.6 | 272.3 | 148.5 | 228.4
728 | 603 | 527.3 | 366.6 | 419.5 | 356.9 | 188.4 | 188.4 | 210.1 | 273 | 148.8 | 228.9
729 | 604 | 527.3 | 366.9 | 419.8 | 357.2 | 188.8 | 188.8 | 210.5 | 273.5 | 149.2 | 229.3
730 | 605 | 527.4 | 367.2 | 420 | 357.5 | 189.2 | 189.3 | 211 | 274 | 149.6 | 229.8
731 | 606 | 527.4 | 367.4 | 420.3 | 357.8 | 189.7 | 189.7 | 211.5 | 274.5 | 149.9 | 230.3
732 | 607 | 527.4 | 367.7 | 420.5 | 358.2 | 190.1 | 190.2 | 211.9 | 275.1 | 150.3 | 230.7
733 | 608 | 527.5 | 368 | 420.8 | 358.4 | 190.5 | 190.7 | 212.4 | 275.3 | 150.7 | 231.2
734 | 609 | 527.5 | 368.3 | 421 | 358.7 | 191 | 191.1 | 212.8 | 275.5 | 151 | 231.6
735 | 610 | 527.5 | 368.6 | 421.2 | 359 | 191.5 | 191.6 | 213.3 | 275.9 | 151.4 | 232.1
736 | 611 | 527.5 | 368.9 | 421.5 | 359.3 | 191.9 | 192.1 | 213.7 | 276.2 | 151.8 | 232.5
737 | 612 | 527.5 | 369.1 | 421.7 | 359.6 | 192.4 | 192.5 | 214.2 | 276.5 | 152.1 | 233
738 | 613 | 527.6 | 369.4 | 422 | 359.9 | 192.8 | 193 | 214.6 | 276.8 | 152.5 | 233.4
739 | 614 | 527.6 | 369.7 | 422.2 | 360.1 | 193.2 | 193.4 | 215.1 | 277.4 | 152.8 | 233.8
740 | 615 | 527.6 | 370 | 422.5 | 360.4 | 193.7 | 193.9 | 215.6 | 277.9 | 153.2 | 234.3
741 | 616 | 527.6 | 370.2 | 422.7 | 360.7 | 194.1 | 194.3 | 216 | 278.4 | 153.6 | 234.7
742 | 617 | 527.7 | 370.5 | 423 | 361 | 194.6 | 194.8 | 216.4 | 278.9 | 153.9 | 235.1
743 | 618 | 527.7 | 370.8 | 423.2 | 361.3 | 195 | 195.3 | 216.9 | 279.6 | 154.3 | 235.5
744 | 619 | 527.7 | 371 | 423.5 | 361.6 | 195.4 | 195.7 | 217.3 | 279.9 | 154.6 | 236
745 | 620 | 527.7 | 371.3 | 423.8 | 361.8 | 195.8 | 196.1 | 217.7 | 280.5 | 155 | 236.4
746 | 621 | 527.8 | 371.5 | 424 | 362.1 | 196.2 | 196.6 | 218.2 | 281.1 | 155.3 | 236.8
747 | 622 | 527.8 | 371.8 | 424.3 | 362.4 | 196.6 | 197 | 218.6 | 281.6 | 155.7 | 237.2
748 | 623 | 527.8 | 372 | 424.5 | 362.7 | 197 | 197.4 | 219 | 282 | 156 | 237.7
749 | 624 | 527.8 | 372.3 | 424.8 | 363 | 197.4 | 197.9 | 219.4 | 282.3 | 156.4 | 238.1
750 | 625 | 527.8 | 372.6 | 425 | 363.2 | 197.9 | 198.4 | 219.9 | 282.9 | 156.7 | 238.5
751 | 626 | 527.8 | 372.8 | 425.2 | 363.5 | 198.3 | 198.8 | 220.3 | 283.3 | 157.1 | 238.9
752 | 627 | 527.7 | 373.1 | 425.5 | 363.8 | 198.7 | 199.2 | 220.8 | 283.7 | 157.4 | 239.3
753 | 628 | 527.7 | 373.3 | 425.7 | 364.1 | 199.2 | 199.7 | 221.2 | 284.1 | 157.8 | 239.7
754 | 629 | 527.7 | 373.6 | 425.9 | 364.4 | 199.6 | 200.2 | 221.7 | 284.6 | 158.2 | 240
755 | 630 | 527.6 | 373.9 | 426.1 | 364.7 | 200.1 | 200.6 | 222.1 | 285.2 | 158.5 | 240.4
756 | 631 | 527.6 | 374.1 | 426.3 | 364.9 | 200.5 | 201.1 | 222.6 | 285.6 | 158.9 | 240.8
757 | 632 | 527.6 | 374.4 | 426.6 | 365.2 | 201 | 201.5 | 223 | 286 | 159.2 | 241.2
758 | 633 | 527.6 | 374.6 | 426.8 | 365.4 | 201.4 | 202 | 223.5 | 286.5 | 159.6 | 241.6
759 | 634 | 527.6 | 374.9 | 427 | 365.8 | 201.9 | 202.4 | 223.9 | 287 | 159.9 | 242
760 | 635 | 527.6 | 375.2 | 427.2 | 366 | 202.4 | 202.9 | 224.3 | 287.3 | 160.3 | 242.4
761 | 636 | 527.5 | 375.4 | 427.4 | 366.3 | 202.9 | 203.3 | 224.7 | 287.7 | 160.6 | 242.7
762 | 637 | 527.4 | 375.7 | 427.7 | 366.5 | 203.4 | 203.8 | 225.2 | 288.3 | 161 | 243.1
763 | 638 | 527.4 | 375.9 | 427.9 | 366.8 | 203.9 | 204.2 | 225.6 | 288.7 | 161.3 | 243.5
764 | 639 | 527.4 | 376.2 | 428.1 | 367.1 | 204.3 | 204.7 | 226 | 289 | 161.7 | 243.9
765 | 640 | 527.4 | 376.4 | 428.3 | 367.3 | 204.8 | 205.1 | 226.4 | 289.5 | 162 | 244.3
766 | 641 | 527.3 | 376.7 | 428.5 | 367.6 | 205.3 | 205.5 | 226.9 | 289.8 | 162.4 | 244.7
767 | 642 | 527.3 | 376.9 | 428.7 | 367.9 | 205.8 | 206 | 227.3 | 290.2 | 162.7 | 245.1
768 | 643 | 527.3 | 377.2 | 428.9 | 368.1 | 206.2 | 206.4 | 227.7 | 290.7 | 163.1 | 245.5
769 | 644 | 527.3 | 377.4 | 429.2 | 368.4 | 206.6 | 206.9 | 228.1 | 290.9 | 163.4 | 245.9
770 | 645 | 527.3 | 377.7 | 429.4 | 368.6 | 207.1 | 207.3 | 228.6 | 291.4 | 163.8 | 246.2
771 | 646 | 527.2 | 377.9 | 429.6 | 368.9 | 207.6 | 207.7 | 229 | 291.8 | 164.2 | 246.6
772 | 647 | 527.2 | 378.2 | 429.8 | 369.1 | 208.1 | 208.2 | 229.4 | 292.4 | 164.5 | 247
773 | 648 | 527.2 | 378.5 | 430 | 369.4 | 208.5 | 208.6 | 229.9 | 292.9 | 164.9 | 247.4
774 | 649 | 527.1 | 378.7 | 430.1 | 369.7 | 209.1 | 209.1 | 230.3 | 293.4 | 165.3 | 247.7
775 | 650 | 527.1 | 379 | 430.3 | 370 | 209.6 | 209.5 | 230.7 | 293.9 | 165.6 | 248.1
776 | 651 | 527.1 | 379.2 | 430.5 | 370.2 | 210.1 | 210 | 231.2 | 294.3 | 166 | 248.5
777 | 652 | 527.1 | 379.5 | 430.7 | 370.5 | 210.6 | 210.4 | 231.6 | 294.9 | 166.4 | 248.8
778 | 653 | 527.2 | 379.8 | 430.9 | 370.7 | 211.1 | 210.8 | 232 | 295.3 | 166.8 | 249.2
779 | 654 | 527.2 | 380 | 431.2 | 371 | 211.5 | 211.2 | 232.4 | 295.9 | 167.1 | 249.6
780 | 655 | 527.2 | 380.2 | 431.4 | 371.2 | 211.9 | 211.7 | 232.9 | 296.4 | 167.5 | 249.9
781 | 656 | 527.3 | 380.4 | 431.6 | 371.5 | 212.4 | 212.1 | 233.3 | 296.6 | 167.8 | 250.3
782 | 657 | 527.3 | 380.7 | 431.9 | 371.7 | 212.9 | 212.5 | 233.7 | 297 | 168.2 | 250.7
783 | 658 | 527.3 | 380.9 | 432.1 | 372 | 213.3 | 213 | 234.2 | 297.3 | 168.6 | 251
784 | 659 | 527.3 | 381.2 | 432.3 | 372.2 | 213.8 | 213.4 | 234.6 | 297.6 | 168.9 | 251.4
785 | 660 | 527.3 | 381.4 | 432.5 | 372.5 | 214.3 | 213.8 | 235 | 297.8 | 169.3 | 251.7
786 | 661 | 527.3 | 381.6 | 432.7 | 372.8 | 214.7 | 214.2 | 235.5 | 298.1 | 169.7 | 252.1
787 | 662 | 527.3 | 381.9 | 432.9 | 373 | 215.2 | 214.7 | 235.9 | 298.4 | 170 | 252.5
788 | 663 | 527.3 | 382.2 | 433.1 | 373.3 | 215.7 | 215.1 | 236.3 | 298.7 | 170.4 | 252.8
789 | 664 | 527.3 | 382.4 | 433.3 | 373.5 | 216.1 | 215.6 | 236.7 | 299.1 | 170.8 | 253.2
790 | 665 | 527.4 | 382.6 | 433.6 | 373.7 | 216.4 | 216 | 237.1 | 299.5 | 171.1 | 253.6
791 | 666 | 527.4 | 382.8 | 433.7 | 374 | 216.9 | 216.4 | 237.5 | 299.9 | 171.5 | 253.9
792 | 667 | 527.4 | 383.1 | 433.9 | 374.3 | 217.4 | 216.9 | 237.9 | 300.4 | 171.8 | 254.3
793 | 668 | 527.5 | 383.3 | 434.1 | 374.5 | 217.8 | 217.3 | 238.3 | 300.7 | 172.2 | 254.6
794 | 669 | 527.5 | 383.5 | 434.4 | 374.8 | 218.2 | 217.7 | 238.7 | 301 | 172.6 | 255
795 | 670 | 527.5 | 383.8 | 434.6 | 375 | 218.6 | 218.1 | 239.1 | 301.4 | 172.9 | 255.3
796 | 671 | 527.5 | 384 | 434.7 | 375.3 | 219.1 | 218.5 | 239.6 | 301.7 | 173.3 | 255.7
797 | 672 | 527.5 | 384.3 | 435 | 375.5 | 219.5 | 219 | 240 | 302.1 | 173.7 | 256.1
798 | 673 | 527.5 | 384.5 | 435.1 | 375.8 | 219.9 | 219.4 | 240.4 | 302.6 | 174 | 256.4
799 | 674 | 527.5 | 384.7 | 435.3 | 376 | 220.3 | 219.8 | 240.8 | 303.2 | 174.4 | 256.8
800 | 675 | 527.5 | 384.9 | 435.6 | 376.3 | 220.7 | 220.2 | 241.3 | 303.8 | 174.8 | 257.2
801 | 676 | 527.5 | 385.2 | 435.8 | 376.5 | 221.1 | 220.6 | 241.7 | 304.3 | 175.1 | 257.5
802 | 677 | 527.5 | 385.4 | 435.9 | 376.8 | 221.5 | 221.1 | 242.1 | 304.7 | 175.5 | 257.9
803 | 678 | 527.4 | 385.6 | 436.2 | 377.1 | 221.9 | 221.5 | 242.5 | 305.1 | 175.9 | 258.2
804 | 679 | 527.4 | 385.9 | 436.3 | 377.3 | 222.3 | 221.9 | 242.9 | 305.6 | 176.2 | 258.6
805 | 680 | 527.4 | 386.1 | 436.5 | 377.5 | 222.7 | 222.3 | 243.3 | 306 | 176.6 | 258.9
806 | 681 | 527.3 | 386.3 | 436.7 | 377.8 | 223.1 | 222.7 | 243.7 | 306.4 | 177 | 259.2
807 | 682 | 527.3 | 386.6 | 436.9 | 378 | 223.5 | 223.1 | 244.2 | 306.8 | 177.3 | 259.6
808 | 683 | 527.2 | 386.8 | 437 | 378.3 | 223.9 | 223.6 | 244.6 | 307.3 | 177.7 | 259.9
809 | 684 | 527.2 | 387.1 | 437.2 | 378.5 | 224.3 | 224 | 244.9 | 307.9 | 178 | 260.3
810 | 685 | 527.2 | 387.3 | 437.3 | 378.8 | 224.8 | 224.4 | 245.3 | 308.4 | 178.4 | 260.6
811 | 686 | 527.2 | 387.6 | 437.5 | 379 | 225.2 | 224.8 | 245.7 | 308.6 | 178.7 | 260.9
812 | 687 | 527.1 | 387.8 | 437.6 | 379.3 | 225.6 | 225.3 | 246.1 | 309.2 | 179.1 | 261.3
813 | 688 | 527.1 | 388 | 437.8 | 379.5 | 225.9 | 225.7 | 246.6 | 309.6 | 179.4 | 261.6
814 | 689 | 527.2 | 388.2 | 438 | 379.7 | 226.3 | 226.1 | 247 | 309.8 | 179.8 | 261.9
815 | 690 | 527.2 | 388.4 | 438.2 | 380 | 226.7 | 226.5 | 247.4 | 310.3 | 180.1 | 262.3
816 | 691 | 527.2 | 388.6 | 438.4 | 380.2 | 227 | 226.9 | 247.8 | 310.8 | 180.5 | 262.6
817 | 692 | 527.2 | 388.9 | 438.6 | 380.4 | 227.4 | 227.3 | 248.2 | 311.3 | 180.8 | 262.9
818 | 693 | 527.2 | 389.1 | 438.8 | 380.7 | 227.7 | 227.7 | 248.6 | 311.7 | 181.2 | 263.3
819 | 694 | 527.2 | 389.3 | 438.9 | 380.9 | 228.1 | 228.1 | 249.1 | 311.9 | 181.5 | 263.6
820 | 695 | 527.2 | 389.6 | 439.1 | 381.2 | 228.5 | 228.5 | 249.5 | 312.2 | 181.9 | 264
821 | 696 | 527.2 | 389.8 | 439.3 | 381.4 | 228.9 | 228.9 | 249.9 | 312.7 | 182.2 | 264.3
822 | 697 | 527.2 | 390 | 439.5 | 381.6 | 229.2 | 229.3 | 250.3 | 312.9 | 182.6 | 264.7
823 | 698 | 527.1 | 390.2 | 439.7 | 381.9 | 229.6 | 229.7 | 250.7 | 313.2 | 182.9 | 265
824 | 699 | 527.1 | 390.4 | 439.9 | 382.1 | 230 | 230.1 | 251.1 | 313.7 | 183.3 | 265.4
825 | 700 | 527.1 | 390.7 | 440 | 382.3 | 230.4 | 230.5 | 251.5 | 314.2 | 183.7 | 265.7
826 | 701 | 527.1 | 390.9 | 440.2 | 382.6 | 230.8 | 230.9 | 251.9 | 314.6 | 184 | 266
827 | 702 | 527.1 | 391.1 | 440.4 | 382.8 | 231.2 | 231.3 | 252.3 | 314.9 | 184.4 | 266.4
828 | 703 | 527.1 | 391.3 | 440.6 | 383 | 231.6 | 231.7 | 252.8 | 315.1 | 184.8 | 266.7
829 | 704 | 527.1 | 391.6 | 440.8 | 383.3 | 232 | 232.1 | 253.2 | 315.5 | 185.1 | 267
830 | 705 | 527.1 | 391.8 | 440.9 | 383.5 | 232.4 | 232.5 | 253.7 | 316.1 | 185.5 | 267.4
831 | 706 | 527.1 | 392 | 441.1 | 383.7 | 232.7 | 232.9 | 254.1 | 316.6 | 185.8 | 267.7
832 | 707 | 527 | 392.2 | 441.3 | 384 | 233.1 | 233.3 | 254.5 | 317.1 | 186.1 | 268
833 | 708 | 527.1 | 392.4 | 441.5 | 384.2 | 233.5 | 233.7 | 254.8 | 317.5 | 186.4 | 268.4
834 | 709 | 527.1 | 392.6 | 441.6 | 384.5 | 233.9 | 234.1 | 255.2 | 317.9 | 186.8 | 268.7
835 | 710 | 527.1 | 392.8 | 441.8 | 384.7 | 234.2 | 234.5 | 255.6 | 318.2 | 187.1 | 269
836 | 711 | 527.1 | 393 | 442 | 384.9 | 234.6 | 234.9 | 256 | 318.6 | 187.6 | 269.4
837 | 712 | 527.1 | 393.3 | 442.2 | 385.1 | 235 | 235.3 | 256.4 | 319 | 188 | 269.7
838 | 713 | 527.1 | 393.5 | 442.4 | 385.3 | 235.3 | 235.6 | 256.7 | 319.3 | 188.4 | 270
839 | 714 | 527.1 | 393.7 | 442.5 | 385.5 | 235.7 | 236 | 257.1 | 319.5 | 188.9 | 270.3
840 | 715 | 527.1 | 393.9 | 442.7 | 385.8 | 236 | 236.4 | 257.5 | 319.7 | 189.3 | 270.7
841 | 716 | 527.1 | 394.1 | 442.9 | 386 | 236.4 | 236.8 | 257.9 | 320.3 | 189.7 | 271
842 | 717 | 527.1 | 394.3 | 443.1 | 386.2 | 236.8 | 237.2 | 258.3 | 320.8 | 190.1 | 271.3
843 | 718 | 527.1 | 394.5 | 443.2 | 386.4 | 237.1 | 237.6 | 258.7 | 321.1 | 190.5 | 271.6
844 | 719 | 527.1 | 394.7 | 443.4 | 386.7 | 237.5 | 238 | 259.1 | 321.4 | 190.9 | 271.9
845 | 720 | 527.1 | 394.9 | 443.6 | 386.9 | 237.8 | 238.4 | 259.5 | 321.9 | 191.3 | 272.2
846 | 721 | 527.1 | 395.2 | 443.7 | 387.1 | 238.2 | 238.8 | 259.9 | 322.3 | 191.7 | 272.5
847 | 722 | 527.1 | 395.4 | 443.9 | 387.3 | 238.6 | 239.2 | 260.2 | 322.6 | 192.1 | 272.8
848 | 723 | 527.1 | 395.6 | 444.1 | 387.5 | 238.9 | 239.6 | 260.6 | 322.8 | 192.5 | 273.1
849 | 724 | 527.1 | 395.8 | 444.2 | 387.8 | 239.3 | 240 | 261 | 323.1 | 192.9 | 273.4
850 | 725 | 527 | 396 | 444.4 | 388 | 239.7 | 240.4 | 261.4 | 323.4 | 193.2 | 273.7
851 | 726 | 527 | 396.2 | 444.5 | 388.2 | 240.1 | 240.8 | 261.8 | 323.8 | 193.6 | 274
852 | 727 | 527 | 396.4 | 444.7 | 388.4 | 240.4 | 241.2 | 262.1 | 324.1 | 194 | 274.3
853 | 728 | 527 | 396.6 | 444.9 | 388.7 | 240.8 | 241.5 | 262.5 | 324.5 | 194.4 | 274.6
854 | 729 | 526.9 | 396.8 | 445 | 388.9 | 241.2 | 241.9 | 262.9 | 325 | 194.8 | 274.9
855 | 730 | 526.9 | 397.1 | 445.1 | 389.1 | 241.5 | 242.3 | 263.3 | 325.4 | 195.2 | 275.2
856 | 731 | 526.9 | 397.3 | 445.3 | 389.3 | 241.9 | 242.7 | 263.6 | 325.6 | 195.6 | 275.5
857 | 732 | 526.9 | 397.5 | 445.5 | 389.5 | 242.2 | 243.1 | 264 | 325.8 | 196 | 275.8
858 | 733 | 526.9 | 397.7 | 445.6 | 389.8 | 242.6 | 243.5 | 264.3 | 326.1 | 196.4 | 276.1
859 | 734 | 526.9 | 397.9 | 445.8 | 390 | 242.9 | 243.9 | 264.6 | 326.3 | 196.8 | 276.5
860 | 735 | 526.9 | 398.1 | 446 | 390.2 | 243.3 | 244.2 | 264.9 | 326.4 | 197.2 | 276.8
861 | 736 | 527 | 398.3 | 446.1 | 390.4 | 243.6 | 244.6 | 265.3 | 326.8 | 197.6 | 277.1
862 | 737 | 527 | 398.5 | 446.3 | 390.6 | 244 | 245 | 265.6 | 327.1 | 198.1 | 277.5
863 | 738 | 527 | 398.7 | 446.4 | 390.9 | 244.3 | 245.4 | 266 | 327.5 | 198.4 | 277.8
864 | 739 | 527.1 | 398.9 | 446.6 | 391.1 | 244.6 | 245.7 | 266.4 | 327.9 | 198.8 | 278.1
865 | 740 | 527.1 | 399.1 | 446.8 | 391.4 | 244.9 | 246.1 | 266.8 | 328.4 | 199.2 | 278.4
866 | 741 | 527 | 399.3 | 446.9 | 391.6 | 245.3 | 246.5 | 267.1 | 328.9 | 199.6 | 278.7
867 | 742 | 527 | 399.5 | 447.1 | 391.8 | 245.6 | 246.8 | 267.5 | 329.3 | 200 | 279
868 | 743 | 527 | 399.7 | 447.3 | 392 | 246 | 247.2 | 267.9 | 329.6 | 200.4 | 279.3
869 | 744 | 527 | 399.9 | 447.4 | 392.3 | 246.3 | 247.6 | 268.3 | 329.8 | 200.8 | 279.7
870 | 745 | 527 | 400.1 | 447.6 | 392.5 | 246.6 | 247.9 | 268.7 | 330.2 | 201.2 | 280
871 | 746 | 527.1 | 400.3 | 447.8 | 392.7 | 247 | 248.3 | 269.1 | 330.5 | 201.5 | 280.3
872 | 747 | 527.1 | 400.5 | 448 | 392.9 | 247.3 | 248.7 | 269.5 | 330.9 | 201.9 | 280.6
873 | 748 | 527.1 | 400.6 | 448.1 | 393.1 | 247.7 | 249.1 | 269.8 | 331.4 | 202.3 | 280.9
874 | 749 | 527.2 | 400.8 | 448.3 | 393.3 | 248 | 249.4 | 270.2 | 331.9 | 202.7 | 281.3
875 | 750 | 527.2 | 401 | 448.4 | 393.5 | 248.4 | 249.9 | 270.6 | 332.3 | 203 | 281.6
876 | 751 | 527.2 | 401.2 | 448.6 | 393.7 | 248.7 | 250.2 | 271 | 332.9 | 203.4 | 281.9
877 | 752 | 527.3 | 401.4 | 448.8 | 393.9 | 249 | 250.6 | 271.4 | 333.4 | 203.8 | 282.2
878 | 753 | 527.3 | 401.6 | 448.9 | 394.1 | 249.4 | 251 | 271.7 | 333.8 | 204.1 | 282.5
879 | 754 | 527.3 | 401.8 | 449.1 | 394.3 | 249.7 | 251.4 | 272.1 | 334.4 | 204.5 | 282.8
880 | 755 | 527.2 | 402 | 449.2 | 394.5 | 250.1 | 251.7 | 272.5 | 334.7 | 204.9 | 283.1
881 | 756 | 527.2 | 402.2 | 449.4 | 394.8 | 250.4 | 252.1 | 272.9 | 335.1 | 205.3 | 283.4
882 | 757 | 527.2 | 402.3 | 449.5 | 395 | 250.8 | 252.5 | 273.3 | 335.6 | 205.6 | 283.7
883 | 758 | 527.2 | 402.5 | 449.7 | 395.2 | 251.2 | 252.9 | 273.7 | 335.9 | 206 | 284
884 | 759 | 527.2 | 402.7 | 449.8 | 395.4 | 251.5 | 253.3 | 274.1 | 336.3 | 206.3 | 284.3
885 | 760 | 527.1 | 402.9 | 449.9 | 395.6 | 251.9 | 253.6 | 274.5 | 336.9 | 206.7 | 284.6
886 | 761 | 527.1 | 403.1 | 450.1 | 395.9 | 252.3 | 254 | 274.8 | 337.3 | 207.1 | 284.9
887 | 762 | 527 | 403.3 | 450.2 | 396.1 | 252.6 | 254.4 | 275.2 | 337.9 | 207.4 | 285.2
888 | 763 | 527 | 403.5 | 450.4 | 396.3 | 253 | 254.8 | 275.6 | 338.3 | 207.8 | 285.5
889 | 764 | 526.9 | 403.7 | 450.5 | 396.4 | 253.4 | 255.2 | 276 | 338.7 | 208.1 | 285.7
890 | 765 | 526.9 | 403.9 | 450.6 | 396.6 | 253.8 | 255.5 | 276.3 | 339.3 | 208.5 | 286
891 | 766 | 526.9 | 404.1 | 450.8 | 396.8 | 254.1 | 255.9 | 276.7 | 339.8 | 208.8 | 286.3
892 | 767 | 526.9 | 404.2 | 450.9 | 397 | 254.5 | 256.3 | 277.1 | 340.3 | 209.1 | 286.6
893 | 768 | 526.9 | 404.4 | 451.1 | 397.2 | 254.8 | 256.7 | 277.5 | 340.6 | 209.5 | 286.9
894 | 769 | 526.9 | 404.6 | 451.2 | 397.4 | 255.2 | 257.1 | 277.8 | 340.9 | 209.8 | 287.2
895 | 770 | 526.9 | 404.8 | 451.4 | 397.6 | 255.6 | 257.4 | 278.2 | 341.2 | 210.2 | 287.5
896 | 771 | 526.9 | 405 | 451.5 | 397.8 | 255.9 | 257.8 | 278.5 | 341.5 | 210.5 | 287.7
897 | 772 | 526.9 | 405.1 | 451.7 | 398 | 256.2 | 258.2 | 278.9 | 341.7 | 210.9 | 288
898 | 773 | 527 | 405.3 | 451.9 | 398.2 | 256.6 | 258.5 | 279.2 | 342.1 | 211.2 | 288.3
899 | 774 | 527 | 405.5 | 452 | 398.4 | 256.9 | 258.9 | 279.6 | 342.5 | 211.5 | 288.6
900 | 775 | 527 | 405.7 | 452.1 | 398.6 | 257.2 | 259.3 | 280 | 342.8 | 211.9 | 288.8
901 | 776 | 527 | 405.8 | 452.3 | 398.8 | 257.6 | 259.6 | 280.3 | 343.3 | 212.2 | 289.1
902 | 777 | 527 | 406 | 452.5 | 399 | 257.9 | 260 | 280.7 | 343.8 | 212.5 | 289.4
903 | 778 | 527 | 406.2 | 452.6 | 399.2 | 258.2 | 260.4 | 281.1 | 344.2 | 212.9 | 289.6
904 | 779 | 527 | 406.3 | 452.8 | 399.4 | 258.6 | 260.7 | 281.4 | 344.7 | 213.2 | 289.8
905 | 780 | 527 | 406.5 | 452.9 | 399.6 | 258.9 | 261.1 | 281.8 | 345.1 | 213.5 | 290.1
906 | 781 | 527 | 406.7 | 453 | 399.7 | 259.3 | 261.5 | 282.1 | 345.3 | 213.8 | 290.3
907 | 782 | 527 | 406.9 | 453.1 | 400 | 259.6 | 261.9 | 282.5 | 345.5 | 214.2 | 290.5
908 | 783 | 527 | 407.1 | 453.3 | 400.2 | 260 | 262.2 | 282.9 | 345.5 | 214.5 | 290.8
909 | 784 | 527 | 407.2 | 453.4 | 400.4 | 260.3 | 262.6 | 283.3 | 345.7 | 214.8 | 291
910 | 785 | 527 | 407.4 | 453.6 | 400.5 | 260.7 | 263 | 283.7 | 345.8 | 215.2 | 291.2
911 | 786 | 527 | 407.6 | 453.7 | 400.7 | 261.1 | 263.3 | 284.1 | 346.4 | 215.5 | 291.5
912 | 787 | 527 | 407.8 | 453.8 | 400.9 | 261.4 | 263.7 | 284.4 | 346.9 | 215.8 | 291.7
913 | 788 | 527 | 407.9 | 453.9 | 401.1 | 261.8 | 264.1 | 284.8 | 347.4 | 216.1 | 292
914 | 789 | 527 | 408.1 | 454.1 | 401.3 | 262.1 | 264.4 | 285.2 | 347.8 | 216.5 | 292.2
915 | 790 | 526.9 | 408.3 | 454.3 | 401.5 | 262.5 | 264.8 | 285.6 | 348 | 216.8 | 292.5
916 | 791 | 526.9 | 408.5 | 454.4 | 401.6 | 262.8 | 265.2 | 285.9 | 348.3 | 217.1 | 292.7
917 | 792 | 526.9 | 408.6 | 454.5 | 401.8 | 263.2 | 265.5 | 286.3 | 348.8 | 217.4 | 292.9
918 | 793 | 526.8 | 408.8 | 454.6 | 402 | 263.5 | 265.9 | 286.7 | 349.1 | 217.7 | 293.2
919 | 794 | 526.8 | 409 | 454.8 | 402.2 | 263.8 | 266.3 | 287 | 349.4 | 218 | 293.4
920 | 795 | 526.8 | 409.2 | 454.9 | 402.4 | 264.2 | 266.6 | 287.4 | 349.6 | 218.4 | 293.7
921 | 796 | 526.8 | 409.3 | 455 | 402.6 | 264.6 | 267 | 287.8 | 349.8 | 218.7 | 293.9
922 | 797 | 526.8 | 409.5 | 455.2 | 402.8 | 264.9 | 267.4 | 288.2 | 350 | 219 | 294.2
923 | 798 | 526.8 | 409.7 | 455.3 | 403 | 265.2 | 267.7 | 288.6 | 350.4 | 219.3 | 294.4
924 | 799 | 526.8 | 409.8 | 455.5 | 403.2 | 265.6 | 268.1 | 289 | 350.7 | 219.6 | 294.7
925 | 800 | 526.8 | 410 | 455.6 | 403.4 | 266 | 268.5 | 289.3 | 351.1 | 219.9 | 294.9
926 | 801 | 526.8 | 410.2 | 455.7 | 403.6 | 266.3 | 268.8 | 289.7 | 351.5 | 220.2 | 295.2
927 | 802 | 526.8 | 410.3 | 455.9 | 403.7 | 266.6 | 269.2 | 290.1 | 352.1 | 220.5 | 295.4
928 | 803 | 526.8 | 410.5 | 456 | 403.9 | 266.9 | 269.5 | 290.4 | 352.6 | 220.8 | 295.7
929 | 804 | 526.8 | 410.7 | 456.1 | 404.1 | 267.3 | 269.9 | 290.8 | 353.1 | 221.1 | 296
930 | 805 | 526.8 | 410.8 | 456.3 | 404.2 | 267.6 | 270.3 | 291.2 | 353.3 | 221.5 | 296.2
931 | 806 | 526.8 | 411 | 456.3 | 404.4 | 267.9 | 270.6 | 291.5 | 353.6 | 221.8 | 296.5
932 | 807 | 526.8 | 411.1 | 456.5 | 404.6 | 268.3 | 271 | 291.9 | 354 | 222.1 | 296.7
933 | 808 | 526.8 | 411.3 | 456.7 | 404.8 | 268.6 | 271.3 | 292.2 | 354.3 | 222.4 | 297
934 | 809 | 526.8 | 411.5 | 456.8 | 405 | 268.9 | 271.7 | 292.6 | 354.9 | 222.7 | 297.2
935 | 810 | 526.8 | 411.6 | 456.9 | 405.1 | 269.2 | 272 | 293 | 355.3 | 223 | 297.5
936 | 811 | 526.7 | 411.8 | 457.1 | 405.3 | 269.5 | 272.4 | 293.4 | 355.6 | 223.3 | 297.8
937 | 812 | 526.7 | 411.9 | 457.2 | 405.4 | 269.8 | 272.7 | 293.7 | 355.8 | 223.7 | 298
938 | 813 | 526.7 | 412.1 | 457.3 | 405.6 | 270.2 | 273.1 | 294.1 | 356.2 | 224 | 298.3
939 | 814 | 526.7 | 412.3 | 457.5 | 405.8 | 270.5 | 273.5 | 294.5 | 356.6 | 224.3 | 298.5
940 | 815 | 526.7 | 412.4 | 457.6 | 406 | 270.9 | 273.8 | 294.9 | 357 | 224.6 | 298.8
941 | 816 | 526.7 | 412.6 | 457.7 | 406.2 | 271.2 | 274.2 | 295.2 | 357.3 | 224.9 | 299
942 | 817 | 526.6 | 412.8 | 457.8 | 406.4 | 271.5 | 274.6 | 295.6 | 357.8 | 225.2 | 299.3
943 | 818 | 526.6 | 413 | 457.9 | 406.5 | 271.8 | 275 | 296 | 358.2 | 225.5 | 299.6
944 | 819 | 526.7 | 413.1 | 458.1 | 406.7 | 272.1 | 275.3 | 296.4 | 358.3 | 225.8 | 299.8
945 | 820 | 526.7 | 413.3 | 458.2 | 406.8 | 272.4 | 275.7 | 296.7 | 358.2 | 226.1 | 300.1
946 | 821 | 526.7 | 413.4 | 458.3 | 407 | 272.6 | 276 | 297.1 | 358.5 | 226.4 | 300.4
947 | 822 | 526.7 | 413.6 | 458.4 | 407.2 | 273 | 276.4 | 297.5 | 358.8 | 226.7 | 300.6
948 | 823 | 526.6 | 413.8 | 458.5 | 407.4 | 273.3 | 276.7 | 297.9 | 359.3 | 227 | 300.9
949 | 824 | 526.6 | 413.9 | 458.6 | 407.5 | 273.6 | 277.1 | 298.2 | 359.6 | 227.3 | 301.1
950 | 825 | 526.6 | 414.1 | 458.8 | 407.7 | 274 | 277.4 | 298.6 | 360.2 | 227.6 | 301.4
951 | 826 | 526.6 | 414.3 | 458.9 | 407.8 | 274.3 | 277.8 | 298.9 | 360.3 | 227.9 | 301.6
952 | 827 | 526.6 | 414.4 | 458.9 | 408 | 274.7 | 278.1 | 299.3 | 360.5 | 228.2 | 301.9
953 | 828 | 526.6 | 414.6 | 459.1 | 408.2 | 275 | 278.5 | 299.7 | 360.8 | 228.5 | 302.1
954 | 829 | 526.7 | 414.7 | 459.2 | 408.4 | 275.3 | 278.8 | 300 | 361.1 | 228.8 | 302.4
955 | 830 | 526.7 | 414.9 | 459.3 | 408.6 | 275.7 | 279.2 | 300.4 | 361.3 | 229.1 | 302.7
956 | 831 | 526.7 | 415.1 | 459.4 | 408.7 | 276 | 279.5 | 300.8 | 361.5 | 229.4 | 302.9
957 | 832 | 526.7 | 415.2 | 459.5 | 408.9 | 276.3 | 279.9 | 301.1 | 361.9 | 229.7 | 303.2
958 | 833 | 526.8 | 415.3 | 459.7 | 409 | 276.6 | 280.2 | 301.5 | 362.3 | 230 | 303.5
959 | 834 | 526.8 | 415.5 | 459.8 | 409.2 | 276.9 | 280.6 | 301.8 | 362.5 | 230.3 | 303.7
960 | 835 | 526.9 | 415.7 | 460 | 409.3 | 277.3 | 280.9 | 302.2 | 362.7 | 230.6 | 304
961 | 836 | 526.9 | 415.8 | 460.1 | 409.5 | 277.6 | 281.2 | 302.5 | 363 | 230.9 | 304.3
962 | 837 | 526.9 | 415.9 | 460.2 | 409.7 | 277.9 | 281.6 | 302.9 | 363.5 | 231.2 | 304.5
963 | 838 | 526.9 | 416.1 | 460.3 | 409.8 | 278.2 | 281.9 | 303.2 | 363.8 | 231.5 | 304.8
964 | 839 | 527 | 416.3 | 460.5 | 410 | 278.5 | 282.3 | 303.6 | 364.3 | 231.7 | 305
965 | 840 | 527 | 416.4 | 460.6 | 410.1 | 278.7 | 282.6 | 303.9 | 364.6 | 232 | 305.3
966 | 841 | 527 | 416.6 | 460.7 | 410.3 | 279 | 283 | 304.3 | 365 | 232.3 | 305.6
967 | 842 | 527.1 | 416.7 | 460.8 | 410.4 | 279.3 | 283.3 | 304.7 | 365.3 | 232.6 | 305.8
968 | 843 | 527.1 | 416.9 | 460.9 | 410.6 | 279.6 | 283.7 | 305 | 365.6 | 232.9 | 306.1
969 | 844 | 527.1 | 417 | 461.1 | 410.8 | 280 | 284 | 305.4 | 365.8 | 233.2 | 306.4
970 | 845 | 527.1 | 417.2 | 461.2 | 410.9 | 280.3 | 284.4 | 305.7 | 366 | 233.5 | 306.6
971 | 846 | 527.1 | 417.3 | 461.3 | 411.1 | 280.5 | 284.7 | 306.1 | 366.5 | 233.7 | 306.9
972 | 847 | 527.1 | 417.4 | 461.4 | 411.3 | 280.7 | 285 | 306.4 | 366.8 | 234 | 307.2
973 | 848 | 527.1 | 417.6 | 461.5 | 411.4 | 281 | 285.4 | 306.8 | 367.2 | 234.3 | 307.4
974 | 849 | 527.1 | 417.8 | 461.6 | 411.6 | 281.3 | 285.8 | 307.1 | 367.5 | 234.6 | 307.7
975 | 850 | 527.1 | 417.9 | 461.8 | 411.7 | 281.6 | 286.1 | 307.5 | 367.6 | 234.9 | 308
976 | 851 | 527.2 | 418.1 | 461.9 | 411.9 | 281.9 | 286.4 | 307.9 | 367.6 | 235.2 | 308.2
977 | 852 | 527.2 | 418.2 | 461.9 | 412.1 | 282.2 | 286.8 | 308.2 | 367.8 | 235.5 | 308.5
978 | 853 | 527.1 | 418.4 | 462.1 | 412.2 | 282.5 | 287.2 | 308.6 | 368.1 | 235.7 | 308.8
979 | 854 | 527.1 | 418.5 | 462.2 | 412.4 | 282.7 | 287.5 | 308.9 | 368.5 | 236 | 309
980 | 855 | 527.1 | 418.7 | 462.3 | 412.5 | 283 | 287.9 | 309.3 | 368.9 | 236.3 | 309.3
981 | 856 | 527.1 | 418.8 | 462.4 | 412.7 | 283.4 | 288.2 | 309.6 | 369.3 | 236.6 | 309.5
982 | 857 | 527.1 | 419 | 462.5 | 412.8 | 283.7 | 288.6 | 310 | 369.8 | 236.9 | 309.8
983 | 858 | 527.1 | 419.1 | 462.7 | 413 | 283.9 | 288.9 | 310.3 | 370.4 | 237.1 | 310.1
984 | 859 | 527.1 | 419.2 | 462.8 | 413.1 | 284.1 | 289.2 | 310.6 | 370.8 | 237.4 | 310.3
985 | 860 | 527.1 | 419.4 | 462.8 | 413.3 | 284.4 | 289.6 | 311 | 371.2 | 237.7 | 310.6
986 | 861 | 527.1 | 419.6 | 462.9 | 413.4 | 284.8 | 289.9 | 311.3 | 371.4 | 238 | 310.9
987 | 862 | 527.1 | 419.7 | 463 | 413.6 | 285.1 | 290.3 | 311.7 | 371.5 | 238.2 | 311.1
988 | 863 | 527.1 | 419.9 | 463.1 | 413.7 | 285.5 | 290.6 | 312 | 371.8 | 238.5 | 311.4
989 | 864 | 527.1 | 420 | 463.2 | 413.9 | 285.8 | 291 | 312.4 | 372.3 | 238.8 | 311.7
990 | 865 | 527.1 | 420.1 | 463.3 | 414.1 | 286.1 | 291.3 | 312.7 | 372.5 | 239.1 | 311.9
991 | 866 | 527 | 420.3 | 463.4 | 414.2 | 286.5 | 291.6 | 313.1 | 372.8 | 239.4 | 312.2
992 | 867 | 527 | 420.4 | 463.5 | 414.3 | 286.8 | 292 | 313.4 | 373.1 | 239.6 | 312.5
993 | 868 | 527 | 420.6 | 463.6 | 414.5 | 287.1 | 292.3 | 313.8 | 373.4 | 239.9 | 312.7
994 | 869 | 527 | 420.7 | 463.7 | 414.6 | 287.3 | 292.6 | 314.1 | 373.5 | 240.2 | 313
995 | 870 | 527 | 420.9 | 463.9 | 414.8 | 287.6 | 293 | 314.5 | 373.6 | 240.5 | 313.3
996 | 871 | 527 | 421 | 464 | 414.9 | 287.8 | 293.3 | 314.8 | 373.9 | 240.7 | 313.6
997 | 872 | 527 | 421.1 | 464.1 | 415.1 | 288.2 | 293.6 | 315.1 | 374.4 | 241 | 313.8
998 | 873 | 527 | 421.3 | 464.2 | 415.2 | 288.4 | 294 | 315.5 | 374.8 | 241.3 | 314.1
999 | 874 | 527 | 421.4 | 464.3 | 415.4 | 288.7 | 294.3 | 315.8 | 375.1 | 241.6 | 314.4
1000 | 875 | 527 | 421.5 | 464.5 | 415.5 | 288.9 | 294.7 | 316.2 | 375.5 | 241.8 | 314.7
1001 | 876 | 527 | 421.7 | 464.6 | 415.7 | 289.2 | 295 | 316.5 | 376 | 242.1 | 314.9
1002 | 877 | 527 | 421.8 | 464.7 | 415.8 | 289.5 | 295.4 | 316.9 | 376.3 | 242.4 | 315.2
1003 | 878 | 527 | 421.9 | 464.8 | 415.9 | 289.8 | 295.7 | 317.2 | 376.5 | 242.7 | 315.5
1004 | 879 | 527 | 422.1 | 464.9 | 416.1 | 290.1 | 296 | 317.6 | 376.8 | 242.9 | 315.8
1005 | 880 | 527 | 422.2 | 465 | 416.2 | 290.3 | 296.4 | 317.9 | 377.2 | 243.2 | 316
1006 | 881 | 526.9 | 422.4 | 465.1 | 416.4 | 290.5 | 296.7 | 318.2 | 377.6 | 243.5 | 316.3
1007 | 882 | 526.9 | 422.5 | 465.2 | 416.5 | 290.9 | 297.1 | 318.5 | 377.9 | 243.7 | 316.6
1008 | 883 | 526.9 | 422.6 | 465.3 | 416.7 | 291.2 | 297.4 | 318.9 | 378.2 | 244 | 316.9
1009 | 884 | 526.8 | 422.7 | 465.4 | 416.8 | 291.5 | 297.7 | 319.3 | 378.4 | 244.3 | 317.1
1010 | 885 | 526.8 | 422.9 | 465.6 | 417 | 291.8 | 298 | 319.6 | 378.6 | 244.6 | 317.4
1011 | 886 | 526.8 | 423 | 465.6 | 417.1 | 292 | 298.4 | 319.9 | 378.9 | 244.8 | 317.7
1012 | 887 | 526.8 | 423.2 | 465.7 | 417.3 | 292.4 | 298.7 | 320.3 | 379.2 | 245.1 | 318
1013 | 888 | 526.8 | 423.3 | 465.8 | 417.4 | 292.7 | 299.1 | 320.6 | 379.6 | 245.4 | 318.3
1014 | 889 | 526.8 | 423.4 | 465.9 | 417.5 | 293 | 299.4 | 321 | 380 | 245.6 | 318.5
1015 | 890 | 526.8 | 423.6 | 466 | 417.7 | 293.3 | 299.7 | 321.3 | 380.3 | 245.9 | 318.8
1016 | 891 | 526.8 | 423.7 | 466.1 | 417.8 | 293.7 | 300.1 | 321.7 | 380.6 | 246.2 | 319.1
1017 | 892 | 526.8 | 423.9 | 466.2 | 417.9 | 294.1 | 300.4 | 322 | 381.1 | 246.4 | 319.3
1018 | 893 | 526.8 | 424 | 466.3 | 418.1 | 294.4 | 300.8 | 322.3 | 381.5 | 246.7 | 319.6
1019 | 894 | 526.8 | 424.1 | 466.3 | 418.2 | 294.7 | 301.2 | 322.7 | 381.7 | 247 | 319.9
1020 | 895 | 526.7 | 424.3 | 466.4 | 418.4 | 295 | 301.5 | 323 | 382.1 | 247.3 | 320.2
1021 | 896 | 526.7 | 424.4 | 466.5 | 418.5 | 295.3 | 301.8 | 323.4 | 382.6 | 247.5 | 320.4
1022 | 897 | 526.7 | 424.5 | 466.6 | 418.6 | 295.6 | 302.2 | 323.7 | 382.9 | 247.8 | 320.7
1023 | 898 | 526.7 | 424.7 | 466.7 | 418.8 | 296 | 302.5 | 324 | 383.1 | 248.1 | 321
1024 | 899 | 526.7 | 424.8 | 466.9 | 418.9 | 296.3 | 302.8 | 324.4 | 383.4 | 248.3 | 321.2
1025 | 900 | 526.8 | 424.9 | 466.9 | 419 | 296.7 | 303.2 | 324.7 | 383.7 | 248.6 | 321.5
1026 | 901 | 526.8 | 425.1 | 467.1 | 419.2 | 297 | 303.5 | 325 | 384.2 | 248.9 | 321.8
1027 | 902 | 526.8 | 425.2 | 467.1 | 419.3 | 297.3 | 303.9 | 325.4 | 384.5 | 249.1 | 322
1028 | 903 | 526.8 | 425.3 | 467.2 | 419.4 | 297.7 | 304.2 | 325.7 | 384.9 | 249.4 | 322.3
1029 | 904 | 526.7 | 425.5 | 467.3 | 419.6 | 298.1 | 304.6 | 326 | 385.1 | 249.7 | 322.5
1030 | 905 | 526.7 | 425.6 | 467.4 | 419.7 | 298.4 | 304.9 | 326.4 | 385.3 | 250 | 322.8
1031 | 906 | 526.7 | 425.7 | 467.4 | 419.8 | 298.8 | 305.3 | 326.7 | 385.5 | 250.2 | 323.1
1032 | 907 | 526.7 | 425.9 | 467.5 | 420 | 299 | 305.6 | 327 | 385.8 | 250.5 | 323.4
1033 | 908 | 526.8 | 426 | 467.6 | 420.1 | 299.4 | 306 | 327.3 | 386.2 | 250.7 | 323.6
1034 | 909 | 526.8 | 426.1 | 467.7 | 420.2 | 299.7 | 306.3 | 327.7 | 386.5 | 251 | 323.9
1035 | 910 | 526.8 | 426.2 | 467.8 | 420.4 | 300 | 306.7 | 328 | 386.7 | 251.3 | 324.2
1036 | 911 | 526.8 | 426.4 | 467.9 | 420.5 | 300.3 | 307 | 328.3 | 387 | 251.5 | 324.5
1037 | 912 | 526.8 | 426.5 | 468 | 420.6 | 300.7 | 307.4 | 328.7 | 387.4 | 251.8 | 324.7
1038 | 913 | 526.8 | 426.6 | 468.1 | 420.8 | 301 | 307.7 | 329 | 387.6 | 252.1 | 325
1039 | 914 | 526.8 | 426.7 | 468.2 | 420.9 | 301.3 | 308 | 329.3 | 388 | 252.3 | 325.3
1040 | 915 | 526.9 | 426.9 | 468.3 | 421 | 301.6 | 308.4 | 329.6 | 388.5 | 252.6 | 325.5
1041 | 916 | 526.9 | 427 | 468.4 | 421.1 | 302 | 308.7 | 330 | 388.8 | 252.9 | 325.8
1042 | 917 | 526.9 | 427.1 | 468.5 | 421.3 | 302.4 | 309.1 | 330.3 | 389.1 | 253.1 | 326.1
1043 | 918 | 526.9 | 427.2 | 468.6 | 421.4 | 302.8 | 309.4 | 330.6 | 389.4 | 253.4 | 326.4
1044 | 919 | 526.9 | 427.4 | 468.6 | 421.5 | 303.1 | 309.7 | 330.9 | 389.8 | 253.6 | 326.6
1045 | 920 | 526.9 | 427.5 | 468.7 | 421.7 | 303.4 | 310.1 | 331.2 | 390 | 253.9 | 326.9
1046 | 921 | 527 | 427.6 | 468.8 | 421.8 | 303.7 | 310.4 | 331.5 | 390.4 | 254.2 | 327.2
1047 | 922 | 527 | 427.7 | 468.9 | 421.9 | 304.1 | 310.8 | 331.8 | 390.7 | 254.5 | 327.5
1048 | 923 | 527 | 427.9 | 469 | 422 | 304.4 | 311.1 | 332.1 | 391.2 | 254.7 | 327.7
1049 | 924 | 527 | 428 | 469.1 | 422.1 | 304.8 | 311.4 | 332.4 | 391.8 | 255 | 328
1050 | 925 | 527 | 428.1 | 469.2 | 422.3 | 305.1 | 311.8 | 332.7 | 392.1 | 255.3 | 328.3
1051 | 926 | 526.9 | 428.2 | 469.3 | 422.4 | 305.4 | 312.1 | 333.1 | 392.3 | 255.5 | 328.5
1052 | 927 | 526.9 | 428.4 | 469.3 | 422.6 | 305.8 | 312.5 | 333.4 | 392.7 | 255.8 | 328.8
1053 | 928 | 526.9 | 428.5 | 469.4 | 422.7 | 306.1 | 312.8 | 333.7 | 393 | 256.1 | 329
1054 | 929 | 526.9 | 428.6 | 469.5 | 422.8 | 306.5 | 313.2 | 334 | 393.4 | 256.3 | 329.3
1055 | 930 | 526.9 | 428.7 | 469.6 | 422.9 | 306.8 | 313.5 | 334.3 | 393.7 | 256.6 | 329.6
1056 | 931 | 526.9 | 428.8 | 469.7 | 423 | 307.2 | 313.8 | 334.6 | 394.2 | 256.8 | 329.8
1057 | 932 | 526.9 | 428.9 | 469.8 | 423.1 | 307.5 | 314.2 | 334.9 | 394.4 | 257.1 | 330.1
1058 | 933 | 526.8 | 429.1 | 469.8 | 423.2 | 307.8 | 314.5 | 335.2 | 394.7 | 257.4 | 330.3
1059 | 934 | 526.8 | 429.2 | 469.9 | 423.4 | 308.1 | 314.8 | 335.5 | 394.9 | 257.7 | 330.6
1060 | 935 | 526.8 | 429.3 | 470 | 423.5 | 308.5 | 315.2 | 335.8 | 395.2 | 257.9 | 330.9
1061 | 936 | 526.8 | 429.4 | 470.1 | 423.6 | 308.9 | 315.5 | 336.1 | 395.6 | 258.2 | 331.2
1062 | 937 | 526.8 | 429.6 | 470.2 | 423.8 | 309.2 | 315.8 | 336.4 | 396 | 258.5 | 331.5
1063 | 938 | 526.7 | 429.7 | 470.3 | 423.9 | 309.5 | 316.2 | 336.7 | 396.2 | 258.7 | 331.7
1064 | 939 | 526.7 | 429.8 | 470.3 | 424 | 309.8 | 316.5 | 337 | 396.4 | 259 | 332
1065 | 940 | 526.7 | 429.9 | 470.4 | 424.2 | 310.2 | 316.9 | 337.3 | 396.6 | 259.3 | 332.3
1066 | 941 | 526.7 | 430 | 470.5 | 424.3 | 310.6 | 317.2 | 337.6 | 396.9 | 259.5 | 332.6
1067 | 942 | 526.7 | 430.1 | 470.6 | 424.4 | 310.9 | 317.5 | 337.9 | 397.4 | 259.8 | 332.9
1068 | 943 | 526.7 | 430.3 | 470.7 | 424.5 | 311.2 | 317.9 | 338.2 | 397.8 | 260 | 333.2
1069 | 944 | 526.7 | 430.4 | 470.7 | 424.6 | 311.6 | 318.2 | 338.5 | 398.2 | 260.3 | 333.4
1070 | 945 | 526.7 | 430.5 | 470.8 | 424.8 | 311.9 | 318.5 | 338.8 | 398.7 | 260.6 | 333.7
1071 | 946 | 526.6 | 430.6 | 470.9 | 424.9 | 312.3 | 318.8 | 339.1 | 399.2 | 260.9 | 334
1072 | 947 | 526.6 | 430.7 | 471 | 425 | 312.7 | 319.2 | 339.4 | 399.7 | 261.1 | 334.3
1073 | 948 | 526.6 | 430.9 | 471 | 425.1 | 313 | 319.5 | 339.7 | 400.3 | 261.4 | 334.6
1074 | 949 | 526.6 | 431 | 471.1 | 425.2 | 313.4 | 319.8 | 340 | 400.5 | 261.7 | 334.9
1075 | 950 | 526.6 | 431.1 | 471.2 | 425.4 | 313.8 | 320.2 | 340.3 | 400.9 | 261.9 | 335.2
1076 | 951 | 526.6 | 431.2 | 471.3 | 425.5 | 314.2 | 320.5 | 340.6 | 401.4 | 262.2 | 335.5
1077 | 952 | 526.6 | 431.3 | 471.4 | 425.6 | 314.6 | 320.8 | 340.9 | 402 | 262.4 | 335.8
1078 | 953 | 526.6 | 431.4 | 471.4 | 425.7 | 314.9 | 321.1 | 341.2 | 402.5 | 262.7 | 336
1079 | 954 | 526.6 | 431.6 | 471.4 | 425.9 | 315.3 | 321.5 | 341.5 | 403 | 263 | 336.3
1080 | 955 | 526.6 | 431.7 | 471.5 | 425.9 | 315.7 | 321.8 | 341.7 | 403.3 | 263.2 | 336.6
1081 | 956 | 526.6 | 431.8 | 471.6 | 426.1 | 316.1 | 322.1 | 342 | 403.6 | 263.5 | 336.9
1082 | 957 | 526.6 | 431.9 | 471.6 | 426.2 | 316.4 | 322.5 | 342.3 | 404 | 263.8 | 337.2
1083 | 958 | 526.6 | 432 | 471.7 | 426.3 | 316.8 | 322.8 | 342.6 | 404.3 | 264.1 | 337.6
1084 | 959 | 526.7 | 432.2 | 471.8 | 426.5 | 317.2 | 323.2 | 342.9 | 404.5 | 264.3 | 337.9
1085 | 960 | 526.7 | 432.3 | 471.9 | 426.6 | 317.6 | 323.5 | 343.2 | 404.8 | 264.6 | 338.2
1086 | 961 | 526.6 | 432.4 | 471.9 | 426.7 | 317.9 | 323.8 | 343.5 | 405.2 | 264.9 | 338.5
1087 | 962 | 526.6 | 432.5 | 472 | 426.8 | 318.2 | 324.1 | 343.7 | 405.4 | 265.1 | 338.8
1088 | 963 | 526.5 | 432.6 | 472.1 | 426.9 | 318.5 | 324.5 | 344 | 405.7 | 265.4 | 339.1
1089 | 964 | 526.5 | 432.7 | 472.2 | 427 | 318.9 | 324.8 | 344.3 | 405.9 | 265.7 | 339.4
1090 | 965 | 526.5 | 432.8 | 472.3 | 427.1 | 319.2 | 325.1 | 344.6 | 406.3 | 265.9 | 339.7
1091 | 966 | 526.5 | 432.9 | 472.3 | 427.3 | 319.6 | 325.4 | 344.9 | 406.7 | 266.2 | 339.9
1092 | 967 | 526.5 | 433.1 | 472.4 | 427.4 | 320 | 325.7 | 345.2 | 407 | 266.5 | 340.1
1093 | 968 | 526.5 | 433.2 | 472.5 | 427.5 | 320.3 | 326.1 | 345.4 | 407.3 | 266.7 | 340.4
1094 | 969 | 526.5 | 433.3 | 472.6 | 427.6 | 320.6 | 326.4 | 345.7 | 407.7 | 267 | 340.7
1095 | 970 | 526.6 | 433.4 | 472.7 | 427.7 | 321 | 326.7 | 346 | 408.1 | 267.3 | 340.9
1096 | 971 | 526.6 | 433.5 | 472.8 | 427.8 | 321.3 | 327 | 346.2 | 408.5 | 267.6 | 341
1097 | 972 | 526.6 | 433.6 | 472.8 | 427.9 | 321.7 | 327.4 | 346.5 | 408.6 | 267.9 | 341.2
1098 | 973 | 526.6 | 433.7 | 472.9 | 428 | 322.1 | 327.7 | 346.8 | 408.9 | 268.1 | 341.4
1099 | 974 | 526.6 | 433.8 | 472.9 | 428.2 | 322.4 | 328 | 347.1 | 409.1 | 268.4 | 341.5
1100 | 975 | 526.5 | 433.9 | 473 | 428.3 | 322.6 | 328.3 | 347.3 | 409.4 | 268.7 | 341.6
1101 | 976 | 526.5 | 434 | 473.1 | 428.4 | 323 | 328.6 | 347.6 | 409.8 | 269 | 341.7
1102 | 977 | 526.6 | 434.2 | 473.1 | 428.5 | 323.4 | 329 | 347.9 | 410.3 | 269.3 | 341.8
1103 | 978 | 526.6 | 434.3 | 473.2 | 428.6 | 323.6 | 329.3 | 348.2 | 410.5 | 269.6 | 341.9
1104 | 979 | 526.6 | 434.4 | 473.3 | 428.7 | 324 | 329.6 | 348.4 | 410.8 | 269.9 | 342
1105 | 980 | 526.6 | 434.5 | 473.3 | 428.8 | 324.3 | 329.9 | 348.7 | 411.2 | 270.1 | 342.2
1106 | 981 | 526.6 | 434.6 | 473.4 | 428.9 | 324.6 | 330.3 | 349 | 411.6 | 270.4 | 342.4
1107 | 982 | 526.6 | 434.7 | 473.5 | 429.1 | 324.9 | 330.6 | 349.2 | 412 | 270.7 | 342.7
1108 | 983 | 526.7 | 434.8 | 473.6 | 429.2 | 325.3 | 330.9 | 349.5 | 412.5 | 271 | 342.9
1109 | 984 | 526.7 | 434.9 | 473.7 | 429.3 | 325.6 | 331.2 | 349.7 | 412.9 | 271.2 | 343.2
1110 | 985 | 526.7 | 434.9 | 473.8 | 429.3 | 325.9 | 331.5 | 350 | 413.4 | 271.4 | 343.5
1111 | 986 | 526.7 | 435 | 473.9 | 429.4 | 326.2 | 331.9 | 350.3 | 413.8 | 271.4 | 343.7
1112 | 987 | 526.7 | 435.1 | 474.1 | 429.5 | 326.5 | 332.1 | 350.5 | 414 | 271.5 | 344
1113 | 988 | 526.7 | 435.2 | 474.1 | 429.6 | 326.8 | 332.5 | 350.8 | 414.4 | 271.6 | 344.3
1114 | 989 | 526.7 | 435.3 | 474.2 | 429.7 | 327.1 | 332.8 | 351 | 414.7 | 271.7 | 344.5
1115 | 990 | 526.7 | 435.4 | 474.4 | 429.8 | 327.4 | 333.1 | 351.3 | 414.9 | 271.8 | 344.8
1116 | 991 | 526.7 | 435.5 | 474.4 | 429.9 | 327.7 | 333.4 | 351.6 | 415.2 | 272 | 345
1117 | 992 | 526.6 | 435.6 | 474.4 | 430.1 | 328.1 | 333.7 | 351.8 | 415.5 | 272.2 | 345.3
1118 | 993 | 526.6 | 435.7 | 474.5 | 430.2 | 328.4 | 334 | 352.1 | 415.6 | 272.5 | 345.6
1119 | 994 | 526.6 | 435.8 | 474.6 | 430.3 | 328.7 | 334.4 | 352.4 | 415.8 | 272.6 | 345.9
1120 | 995 | 526.6 | 435.9 | 474.7 | 430.4 | 329 | 334.7 | 352.7 | 416 | 272.8 | 346.1
1121 | 996 | 526.6 | 436 | 474.8 | 430.5 | 329.3 | 335 | 353 | 416.1 | 273.1 | 346.3
1122 | 997 | 526.5 | 436.1 | 474.8 | 430.6 | 329.7 | 335.3 | 353.3 | 416.3 | 273.3 | 346.5
1123 | 998 | 526.5 | 436.3 | 474.8 | 430.7 | 330 | 335.7 | 353.5 | 416.4 | 273.4 | 346.7
1124 | 999 | 526.4 | 436.4 | 474.9 | 430.8 | 330.3 | 336 | 353.8 | 416.6 | 273.6 | 346.9
1125 | 1000 | 526.4 | 436.4 | 475 | 430.9 | 330.6 | 336.3 | 354 | 416.8 | 273.8 | 347.2
1126 | 1001 | 526.3 | 436.5 | 475.1 | 431 | 330.9 | 336.6 | 354.3 | 416.9 | 274 | 347.4
1127 | 1002 | 526.3 | 436.7 | 475.1 | 431.1 | 331.2 | 336.9 | 354.5 | 417.1 | 274.2 | 347.6
1128 | 1003 | 526.3 | 436.8 | 475.2 | 431.2 | 331.6 | 337.2 | 354.8 | 417.4 | 274.4 | 347.8
1129 | 1004 | 526.3 | 436.9 | 475.2 | 431.4 | 331.9 | 337.5 | 355.1 | 417.7 | 274.5 | 348
1130 | 1005 | 526.3 | 437 | 475.3 | 431.5 | 332.2 | 337.8 | 355.3 | 417.9 | 274.7 | 348.3
1131 | 1006 | 526.3 | 437.1 | 475.3 | 431.6 | 332.6 | 338.1 | 355.6 | 418.1 | 274.9 | 348.5
1132 | 1007 | 526.3 | 437.2 | 475.4 | 431.7 | 332.9 | 338.4 | 355.9 | 418.4 | 275.1 | 348.7
1133 | 1008 | 526.3 | 437.3 | 475.5 | 431.8 | 333.2 | 338.7 | 356.2 | 418.8 | 275.3 | 348.9
1134 | 1009 | 526.2 | 437.4 | 475.5 | 431.9 | 333.5 | 339 | 356.4 | 419.1 | 275.5 | 349.1
1135 | 1010 | 526.2 | 437.5 | 475.6 | 432 | 333.8 | 339.2 | 356.7 | 419.5 | 275.7 | 349.4
1136 | 1011 | 526.2 | 437.6 | 475.6 | 432.1 | 334.1 | 339.6 | 357 | 419.6 | 275.9 | 349.6
1137 | 1012 | 526.2 | 437.7 | 475.8 | 432.2 | 334.4 | 339.9 | 357.3 | 419.8 | 276.1 | 349.8
1138 | 1013 | 526.2 | 437.8 | 475.9 | 432.3 | 334.6 | 340.1 | 357.5 | 420 | 276.3 | 350.1
1139 | 1014 | 526.3 | 437.8 | 476 | 432.4 | 334.9 | 340.4 | 357.8 | 420.1 | 276.6 | 350.3
1140 | 1015 | 526.3 | 437.9 | 476 | 432.5 | 335.2 | 340.7 | 358.1 | 420.2 | 276.8 | 350.5
1141 | 1016 | 526.3 | 438 | 476.1 | 432.6 | 335.5 | 341 | 358.4 | 420.4 | 276.9 | 350.7
1142 | 1017 | 526.3 | 438.1 | 476.1 | 432.7 | 335.8 | 341.3 | 358.7 | 420.8 | 277.2 | 350.9
1143 | 1018 | 526.4 | 438.2 | 476.2 | 432.8 | 336.1 | 341.5 | 359 | 421 | 277.4 | 351.1
1144 | 1019 | 526.4 | 438.3 | 476.3 | 432.9 | 336.4 | 341.8 | 359.3 | 421.3 | 277.6 | 351.3
1145 | 1020 | 526.5 | 438.4 | 476.4 | 433 | 336.7 | 342.1 | 359.5 | 421.5 | 277.8 | 351.4
1146 | 1021 | 526.5 | 438.5 | 476.4 | 433.1 | 337 | 342.4 | 359.8 | 421.8 | 278 | 351.6
1147 | 1022 | 526.5 | 438.6 | 476.5 | 433.2 | 337.3 | 342.7 | 360.1 | 422.1 | 278.2 | 351.8
1148 | 1023 | 526.5 | 438.7 | 476.5 | 433.3 | 337.6 | 343 | 360.4 | 422.1 | 278.4 | 352
1149 | 1024 | 526.5 | 438.8 | 476.6 | 433.5 | 337.9 | 343.3 | 360.8 | 422.3 | 278.6 | 352.2
1150 | 1025 | 526.6 | 438.9 | 476.7 | 433.5 | 338.2 | 343.6 | 361.1 | 422.7 | 278.8 | 352.4
1151 | 1026 | 526.6 | 439 | 476.7 | 433.6 | 338.5 | 343.9 | 361.4 | 422.9 | 279 | 352.6
1152 | 1027 | 526.6 | 439.1 | 476.8 | 433.7 | 338.8 | 344.2 | 361.7 | 423.2 | 279.3 | 352.8
1153 | 1028 | 526.7 | 439.2 | 476.9 | 433.8 | 339.1 | 344.5 | 362 | 423.3 | 279.6 | 353
1154 | 1029 | 526.7 | 439.2 | 477 | 433.9 | 339.4 | 344.7 | 362.3 | 423.5 | 279.9 | 353.2
1155 | 1030 | 526.7 | 439.3 | 477 | 434 | 339.7 | 345 | 362.6 | 423.7 | 280.2 | 353.4
1156 | 1031 | 526.8 | 439.4 | 477.1 | 434.1 | 339.9 | 345.3 | 362.9 | 423.8 | 280.5 | 353.6
1157 | 1032 | 526.8 | 439.5 | 477.2 | 434.2 | 340.2 | 345.6 | 363.2 | 423.8 | 280.7 | 353.8
1158 | 1033 | 526.8 | 439.6 | 477.3 | 434.3 | 340.5 | 345.9 | 363.5 | 424 | 281 | 354
1159 | 1034 | 526.8 | 439.7 | 477.4 | 434.4 | 340.8 | 346.2 | 363.8 | 424.1 | 281.2 | 354.2
1160 | 1035 | 526.8 | 439.7 | 477.4 | 434.5 | 341.1 | 346.5 | 364.1 | 424.3 | 281.5 | 354.3
1161 | 1036 | 526.8 | 439.8 | 477.5 | 434.6 | 341.4 | 346.7 | 364.4 | 424.4 | 281.7 | 354.5
1162 | 1037 | 526.8 | 439.9 | 477.6 | 434.7 | 341.7 | 347 | 364.6 | 424.6 | 282 | 354.7
1163 | 1038 | 526.8 | 440 | 477.6 | 434.8 | 341.9 | 347.3 | 364.9 | 424.6 | 282.3 | 354.9
1164 | 1039 | 526.8 | 440.1 | 477.7 | 434.9 | 342.2 | 347.6 | 365.2 | 424.8 | 282.5 | 354.9
1165 | 1040 | 526.8 | 440.2 | 477.8 | 435 | 342.5 | 347.8 | 365.5 | 425 | 282.8 | 354.8
1166 | 1041 | 526.8 | 440.3 | 477.9 | 435.1 | 342.8 | 348.1 | 365.8 | 425.1 | 282.8 | 354.9
1167 | 1042 | 526.8 | 440.4 | 477.9 | 435.2 | 343.1 | 348.4 | 366.1 | 425 | 282.4 | 355.1
1168 | 1043 | 526.8 | 440.5 | 478 | 435.3 | 343.4 | 348.7 | 366.5 | 425.1 | 281.6 | 355.2
1169 | 1044 | 526.7 | 440.6 | 478 | 435.4 | 343.6 | 349 | 366.8 | 425.3 | 281.3 | 355.4
1170 | 1045 | 526.7 | 440.7 | 478.1 | 435.5 | 343.9 | 349.3 | 367.1 | 425.5 | 281.5 | 355.5
1171 | 1046 | 526.7 | 440.7 | 478.1 | 435.6 | 344.2 | 349.6 | 367.4 | 425.7 | 281.8 | 355.7
1172 | 1047 | 526.7 | 440.8 | 478.2 | 435.7 | 344.4 | 349.8 | 367.7 | 426 | 282.1 | 355.9
1173 | 1048 | 526.7 | 440.9 | 478.3 | 435.7 | 344.7 | 350.1 | 368.1 | 426 | 282.4 | 356.1
1174 | 1049 | 526.7 | 441 | 478.4 | 435.8 | 344.9 | 350.3 | 368.4 | 425.9 | 282.7 | 356.3
1175 | 1050 | 526.6 | 441.1 | 478.4 | 436 | 345.2 | 350.6 | 368.7 | 425.9 | 283 | 356.5
1176 | 1051 | 526.6 | 441.2 | 478.4 | 436 | 345.4 | 350.9 | 369 | 426.1 | 283.4 | 356.7
1177 | 1052 | 526.6 | 441.3 | 478.5 | 436.2 | 345.8 | 351.2 | 369.4 | 426.3 | 283.7 | 356.8
1178 | 1053 | 526.6 | 441.4 | 478.5 | 436.2 | 346 | 351.5 | 369.7 | 426.6 | 284.1 | 356.9
1179 | 1054 | 526.6 | 441.5 | 478.6 | 436.4 | 346.3 | 351.8 | 370.1 | 426.8 | 284.5 | 357.1
1180 | 1055 | 526.6 | 441.6 | 478.6 | 436.4 | 346.6 | 352 | 370.4 | 427 | 284.8 | 357.3
1181 | 1056 | 526.6 | 441.7 | 478.7 | 436.5 | 346.8 | 352.3 | 370.7 | 427.1 | 285.2 | 357.4
1182 | 1057 | 526.6 | 441.8 | 478.8 | 436.6 | 347.1 | 352.6 | 371 | 427.3 | 285.6 | 357.6
1183 | 1058 | 526.6 | 441.8 | 478.8 | 436.7 | 347.4 | 352.8 | 371.3 | 427.5 | 285.9 | 357.7
1184 | 1059 | 526.6 | 441.9 | 478.9 | 436.8 | 347.6 | 353.1 | 371.6 | 427.7 | 286.3 | 357.9
1185 | 1060 | 526.5 | 442 | 478.9 | 436.9 | 347.8 | 353.4 | 371.9 | 427.7 | 286.6 | 358.1
1186 | 1061 | 526.5 | 442.1 | 479 | 437 | 348.1 | 353.6 | 372.3 | 427.9 | 286.9 | 358.3
1187 | 1062 | 526.5 | 442.2 | 479 | 437.1 | 348.4 | 353.9 | 372.6 | 428.1 | 287.3 | 358.5
1188 | 1063 | 526.4 | 442.3 | 479.1 | 437.2 | 348.7 | 354.2 | 373 | 428.2 | 287.6 | 358.7
1189 | 1064 | 526.4 | 442.4 | 479.1 | 437.3 | 348.9 | 354.5 | 373.3 | 428.5 | 287.9 | 358.9
1190 | 1065 | 526.4 | 442.4 | 479.2 | 437.4 | 349.2 | 354.7 | 373.7 | 428.8 | 288.2 | 359
1191 | 1066 | 526.4 | 442.5 | 479.3 | 437.5 | 349.4 | 355 | 374 | 428.9 | 288.5 | 359.1
1192 | 1067 | 526.3 | 442.6 | 479.3 | 437.6 | 349.6 | 355.3 | 374.4 | 429.1 | 288.8 | 359.2
1193 | 1068 | 526.3 | 442.7 | 479.4 | 437.7 | 349.9 | 355.5 | 374.7 | 429.4 | 289.1 | 359.3
1194 | 1069 | 526.3 | 442.8 | 479.4 | 437.8 | 350.2 | 355.8 | 375.1 | 429.4 | 289.3 | 359.4
1195 | 1070 | 526.3 | 442.9 | 479.5 | 437.9 | 350.4 | 356.1 | 375.5 | 429.5 | 289.6 | 359.5
1196 | 1071 | 526.2 | 443 | 479.5 | 438 | 350.6 | 356.3 | 375.9 | 429.8 | 289.8 | 359.5
1197 | 1072 | 526.2 | 443 | 479.6 | 438.1 | 350.9 | 356.6 | 376.3 | 430.1 | 289.9 | 359.6
1198 | 1073 | 526.2 | 443.1 | 479.7 | 438.2 | 351.2 | 356.9 | 376.8 | 430.2 | 290.1 | 359.6
1199 | 1074 | 526.3 | 443.2 | 479.7 | 438.3 | 351.4 | 357.1 | 377.2 | 430.5 | 290.3 | 359.6
1200 | 1075 | 526.3 | 443.3 | 479.8 | 438.3 | 351.6 | 357.4 | 377.7 | 430.7 | 290.5 | 359.6
1201 | 1076 | 526.3 | 443.4 | 479.9 | 438.4 | 351.9 | 357.6 | 378.1 | 430.9 | 290.8 | 359.6
1202 | 1077 | 526.3 | 443.5 | 480 | 438.5 | 352.2 | 357.9 | 378.5 | 431.3 | 291.1 | 359.5
1203 | 1078 | 526.3 | 443.5 | 480 | 438.6 | 352.4 | 358.1 | 378.9 | 431.5 | 291.4 | 359.5
1204 | 1079 | 526.3 | 443.6 | 480 | 438.7 | 352.7 | 358.4 | 379.3 | 431.7 | 291.7 | 359.5
1205 | 1080 | 526.2 | 443.7 | 480.1 | 438.8 | 353 | 358.7 | 379.7 | 431.9 | 292 | 359.6
1206 | 1081 | 526.2 | 443.8 | 480.1 | 438.9 | 353.3 | 359 | 380.2 | 432.1 | 292.3 | 359.7
1207 | 1082 | 526.2 | 443.9 | 480.2 | 439 | 353.5 | 359.2 | 380.6 | 432.1 | 292.5 | 359.8
1208 | 1083 | 526.2 | 443.9 | 480.3 | 439.1 | 353.8 | 359.5 | 381 | 432.3 | 292.7 | 360
1209 | 1084 | 526.2 | 444 | 480.3 | 439.2 | 354 | 359.7 | 381.4 | 432.5 | 292.9 | 360.1
1210 | 1085 | 526.1 | 444.1 | 480.4 | 439.3 | 354.2 | 360 | 381.8 | 432.7 | 293.2 | 360.3
1211 | 1086 | 526.2 | 444.2 | 480.4 | 439.4 | 354.5 | 360.2 | 382.2 | 432.8 | 293.5 | 360.5
1212 | 1087 | 526.2 | 444.2 | 480.5 | 439.4 | 354.8 | 360.5 | 382.6 | 433.3 | 293.8 | 360.7
1213 | 1088 | 526.2 | 444.3 | 480.5 | 439.5 | 355 | 360.8 | 383 | 433.6 | 294.1 | 361.3
1214 | 1089 | 526.2 | 444.4 | 480.6 | 439.6 | 355.3 | 361 | 383.4 | 433.9 | 294.4 | 361.5
1215 | 1090 | 526.2 | 444.5 | 480.7 | 439.7 | 355.5 | 361.2 | 383.9 | 434.1 | 294.7 | 361.9
1216 | 1091 | 526.2 | 444.6 | 480.7 | 439.8 | 355.8 | 361.5 | 384.3 | 434.3 | 295 | 362.1
1217 | 1092 | 526.2 | 444.6 | 480.8 | 439.9 | 356.1 | 361.8 | 384.7 | 434.5 | 295.3 | 362.3
1218 | 1093 | 526.2 | 444.7 | 480.9 | 440 | 356.3 | 362 | 385.1 | 434.9 | 295.5 | 362.4
1219 | 1094 | 526.2 | 444.8 | 480.9 | 440.1 | 356.6 | 362.2 | 385.5 | 435.2 | 295.8 | 362.5
1220 | 1095 | 526.1 | 444.9 | 480.9 | 440.1 | 356.8 | 362.5 | 386 | 435.4 | 296 | 362.6
1221 | 1096 | 526.1 | 445 | 481 | 440.2 | 357.1 | 362.8 | 386.5 | 435.7 | 296.2 | 362.8
1222 | 1097 | 526.1 | 445 | 481 | 440.3 | 357.3 | 363 | 387 | 436 | 296.4 | 362.9
1223 | 1098 | 526.1 | 445.1 | 481.1 | 440.4 | 357.5 | 363.2 | 387.5 | 436.4 | 296.5 | 363
1224 | 1099 | 526.1 | 445.2 | 481.1 | 440.5 | 357.8 | 363.5 | 387.9 | 436.7 | 296.7 | 363.2
1225 | 1100 | 526.2 | 445.3 | 481.1 | 440.6 | 358.1 | 363.7 | 388.4 | 437.1 | 296.9 | 363.3
1226 | 1101 | 526.2 | 445.3 | 481.2 | 440.7 | 358.3 | 364 | 388.9 | 437.5 | 297.1 | 363.5
1227 | 1102 | 526.2 | 445.4 | 481.2 | 440.8 | 358.5 | 364.2 | 389.4 | 437.7 | 297.3 | 363.7
1228 | 1103 | 526.2 | 445.5 | 481.3 | 440.9 | 358.7 | 364.5 | 389.9 | 438 | 297.5 | 363.9
1229 | 1104 | 526.3 | 445.6 | 481.4 | 441 | 359 | 364.7 | 390.4 | 438.3 | 297.8 | 364.1
1230 | 1105 | 526.3 | 445.6 | 481.5 | 441 | 359.2 | 365 | 390.8 | 438.5 | 298.1 | 364.3
1231 | 1106 | 526.4 | 445.7 | 481.5 | 441.1 | 359.4 | 365.2 | 391.3 | 438.7 | 298.4 | 364.5
1232 | 1107 | 526.4 | 445.8 | 481.6 | 441.2 | 359.7 | 365.5 | 391.8 | 439.1 | 298.6 | 364.7
1233 | 1108 | 526.4 | 445.8 | 481.7 | 441.3 | 359.9 | 365.7 | 392.2 | 439.4 | 298.9 | 364.8
1234 | 1109 | 526.5 | 445.9 | 481.7 | 441.4 | 360.2 | 366 | 392.7 | 439.7 | 299.2 | 365
1235 | 1110 | 526.5 | 446 | 481.7 | 441.5 | 360.5 | 366.2 | 393.2 | 440 | 299.5 | 365.3
1236 | 1111 | 526.6 | 446 | 481.8 | 441.5 | 360.7 | 366.4 | 393.6 | 440.3 | 299.7 | 365.5
1237 | 1112 | 526.6 | 446.1 | 481.9 | 441.6 | 361 | 366.7 | 394.1 | 440.5 | 300 | 365.7
1238 | 1113 | 526.6 | 446.2 | 481.9 | 441.7 | 361.2 | 366.9 | 394.5 | 440.9 | 300.2 | 365.9
1239 | 1114 | 526.6 | 446.3 | 482 | 441.8 | 361.6 | 367.1 | 394.9 | 441.4 | 300.5 | 366
1240 | 1115 | 526.6 | 446.3 | 482 | 441.9 | 361.8 | 367.3 | 395.4 | 441.8 | 300.8 | 366.2
1241 | 1116 | 526.6 | 446.4 | 482.1 | 442 | 362.1 | 367.5 | 395.8 | 442.2 | 301.1 | 366.4
1242 | 1117 | 526.6 | 446.5 | 482.1 | 442.1 | 362.5 | 367.7 | 396.2 | 442.6 | 301.3 | 366.6
1243 | 1118 | 526.6 | 446.6 | 482.2 | 442.2 | 362.9 | 368 | 396.7 | 443 | 301.6 | 366.9
1244 | 1119 | 526.7 | 446.7 | 482.2 | 442.2 | 363.2 | 368.2 | 397.1 | 443.5 | 301.9 | 367.1
1245 | 1120 | 526.7 | 446.7 | 482.3 | 442.3 | 363.6 | 368.4 | 397.5 | 443.9 | 302.1 | 367.3
1246 | 1121 | 526.6 | 446.8 | 482.3 | 442.4 | 363.9 | 368.6 | 397.9 | 444.1 | 302.4 | 367.5
1247 | 1122 | 526.6 | 446.9 | 482.4 | 442.5 | 364.3 | 368.8 | 398.3 | 444.3 | 302.7 | 367.6
1248 | 1123 | 526.6 | 446.9 | 482.4 | 442.5 | 364.6 | 369 | 398.7 | 444.4 | 302.9 | 367.8
1249 | 1124 | 526.6 | 447 | 482.5 | 442.6 | 364.9 | 369.2 | 399.1 | 444.7 | 303.2 | 367.9
1250 | 1125 | 526.6 | 447.1 | 482.5 | 442.7 | 365.2 | 369.4 | 399.5 | 444.9 | 303.5 | 368
1251 | 1126 | 526.6 | 447.2 | 482.6 | 442.8 | 365.6 | 369.6 | 399.9 | 445.2 | 303.8 | 368.2
1252 | 1127 | 526.6 | 447.2 | 482.6 | 442.9 | 365.9 | 369.8 | 400.3 | 445.7 | 304 | 368.3
1253 | 1128 | 526.5 | 447.2 | 482.7 | 443 | 366.2 | 370 | 400.7 | 446.1 | 304.3 | 368.5
1254 | 1129 | 526.5 | 447.3 | 482.8 | 443 | 366.6 | 370.2 | 401.1 | 446.3 | 304.5 | 368.6
1255 | 1130 | 526.5 | 447.4 | 482.8 | 443.1 | 366.9 | 370.4 | 401.4 | 446.6 | 304.7 | 368.7
1256 | 1131 | 526.4 | 447.5 | 482.9 | 443.2 | 367.3 | 370.6 | 401.8 | 447 | 305 | 368.9
1257 | 1132 | 526.4 | 447.6 | 482.9 | 443.3 | 367.6 | 370.8 | 402.2 | 447.3 | 305.2 | 369
1258 | 1133 | 526.4 | 447.6 | 482.9 | 443.4 | 367.9 | 371 | 402.6 | 447.8 | 305.5 | 369.1
1259 | 1134 | 526.3 | 447.7 | 483 | 443.5 | 368.2 | 371.2 | 403 | 448.3 | 305.7 | 369.2
1260 | 1135 | 526.3 | 447.8 | 483 | 443.5 | 368.6 | 371.3 | 403.4 | 448.8 | 306 | 369.3
1261 | 1136 | 526.3 | 447.8 | 483.1 | 443.6 | 368.9 | 371.5 | 403.8 | 449.3 | 306.3 | 369.5
1262 | 1137 | 526.3 | 447.9 | 483.1 | 443.7 | 369.2 | 371.7 | 404.2 | 449.9 | 306.6 | 369.6
1263 | 1138 | 526.3 | 448 | 483.1 | 443.8 | 369.5 | 371.8 | 404.6 | 450.4 | 307 | 369.7
1264 | 1139 | 526.3 | 448 | 483.2 | 443.9 | 369.8 | 371.9 | 405 | 450.9 | 307.3 | 369.8
1265 | 1140 | 526.3 | 448.1 | 483.2 | 444 | 370.1 | 372.1 | 405.4 | 451.1 | 307.6 | 370.1
1266 | 1141 | 526.3 | 448.2 | 483.2 | 444.1 | 370.4 | 372.3 | 405.8 | 451.4 | 308 | 370.2
1267 | 1142 | 526.2 | 448.3 | 483.3 | 444.1 | 370.7 | 372.4 | 406.2 | 451.7 | 308.3 | 370.3
1268 | 1143 | 526.2 | 448.4 | 483.3 | 444.2 | 371 | 372.5 | 406.6 | 452.1 | 308.7 | 370.6
1269 | 1144 | 526.2 | 448.4 | 483.3 | 444.3 | 371.3 | 372.7 | 406.9 | 452.8 | 309 | 370.7
1270 | 1145 | 526.1 | 448.5 | 483.4 | 444.4 | 371.6 | 372.8 | 407.3 | 453.3 | 309.4 | 370.9
1271 | 1146 | 526.1 | 448.6 | 483.4 | 444.5 | 371.9 | 373 | 407.7 | 453.8 | 309.7 | 371
1272 | 1147 | 526.1 | 448.6 | 483.5 | 444.5 | 372.2 | 373.1 | 408.1 | 454.3 | 310.1 | 371.2
1273 | 1148 | 526.1 | 448.7 | 483.5 | 444.6 | 372.5 | 373.3 | 408.5 | 455 | 310.5 | 371.4
1274 | 1149 | 526.1 | 448.8 | 483.5 | 444.7 | 372.7 | 373.4 | 408.9 | 455.5 | 310.9 | 371.7
1275 | 1150 | 526.2 | 448.8 | 483.6 | 444.8 | 373 | 373.5 | 409.3 | 455.9 | 311.4 | 371.9
1276 | 1151 | 526.2 | 448.9 | 483.6 | 444.9 | 373.3 | 373.7 | 409.7 | 456.4 | 311.7 | 372.2
1277 | 1152 | 526.2 | 449 | 483.6 | 444.9 | 373.6 | 373.8 | 410.1 | 456.8 | 312.2 | 372.5
1278 | 1153 | 526.2 | 449 | 483.7 | 445 | 373.9 | 374 | 410.4 | 457.2 | 312.6 | 372.7
1279 | 1154 | 526.2 | 449.1 | 483.8 | 445.1 | 374.2 | 374.1 | 410.8 | 457.3 | 313 | 372.9
1280 | 1155 | 526.3 | 449.2 | 483.8 | 445.2 | 374.6 | 374.3 | 411.2 | 457.5 | 313.5 | 373.1
1281 | 1156 | 526.3 | 449.2 | 483.8 | 445.3 | 374.9 | 374.5 | 411.6 | 457.8 | 313.9 | 373.3
1282 | 1157 | 526.4 | 449.3 | 483.9 | 445.3 | 375.2 | 374.6 | 412 | 458.1 | 314.3 | 373.5
1283 | 1158 | 526.4 | 449.4 | 484 | 445.4 | 375.5 | 374.8 | 412.4 | 458.6 | 314.7 | 373.7
1284 | 1159 | 526.4 | 449.4 | 484 | 445.5 | 375.7 | 375 | 412.8 | 459 | 315.1 | 373.9
1285 | 1160 | 526.4 | 449.5 | 484.1 | 445.5 | 376 | 375.2 | 413.1 | 459.3 | 315.5 | 374.1
1286 | 1161 | 526.5 | 449.6 | 484.1 | 445.6 | 376.4 | 375.4 | 413.5 | 459.8 | 315.9 | 374.3
1287 | 1162 | 526.5 | 449.6 | 484.1 | 445.7 | 376.7 | 375.6 | 413.9 | 460.1 | 316.3 | 374.5
1288 | 1163 | 526.5 | 449.7 | 484.2 | 445.8 | 376.9 | 375.8 | 414.2 | 460.5 | 316.7 | 374.7
1289 | 1164 | 526.5 | 449.8 | 484.2 | 445.8 | 377.3 | 376 | 414.6 | 460.8 | 317 | 374.9
1290 | 1165 | 526.5 | 449.8 | 484.3 | 445.9 | 377.5 | 376.2 | 414.9 | 461 | 317.4 | 375.1
1291 | 1166 | 526.5 | 449.9 | 484.4 | 446 | 377.8 | 376.4 | 415.3 | 461.5 | 317.8 | 375.3
1292 | 1167 | 526.5 | 450 | 484.4 | 446.1 | 378.2 | 376.6 | 415.6 | 461.8 | 318.2 | 375.5
1293 | 1168 | 526.5 | 450.1 | 484.4 | 446.1 | 378.5 | 376.9 | 416 | 462.1 | 318.6 | 375.7
1294 | 1169 | 526.5 | 450.1 | 484.5 | 446.2 | 378.8 | 377.1 | 416.3 | 462.1 | 319 | 375.9
1295 | 1170 | 526.5 | 450.2 | 484.6 | 446.3 | 379.1 | 377.3 | 416.7 | 462.4 | 319.4 | 376
1296 | 1171 | 526.5 | 450.3 | 484.6 | 446.3 | 379.5 | 377.6 | 417 | 462.7 | 319.7 | 376.2
1297 | 1172 | 526.5 | 450.3 | 484.6 | 446.4 | 379.8 | 377.9 | 417.3 | 462.9 | 320.1 | 376.4
1298 | 1173 | 526.5 | 450.4 | 484.7 | 446.5 | 380.1 | 378.1 | 417.7 | 463.2 | 320.5 | 376.7
1299 | 1174 | 526.5 | 450.5 | 484.7 | 446.6 | 380.4 | 378.4 | 418 | 463.6 | 320.9 | 376.9
1300 | 1175 | 526.5 | 450.5 | 484.8 | 446.6 | 380.7 | 378.6 | 418.4 | 463.7 | 321.3 | 377.1
1301 | 1176 | 526.5 | 450.6 | 484.8 | 446.7 | 381 | 378.9 | 418.7 | 463.9 | 321.7 | 377.3
1302 | 1177 | 526.4 | 450.7 | 484.9 | 446.8 | 381.4 | 379.2 | 419.1 | 464.1 | 322.1 | 377.5
1303 | 1178 | 526.4 | 450.7 | 484.9 | 446.9 | 381.7 | 379.4 | 419.4 | 464.2 | 322.6 | 377.7
1304 | 1179 | 526.3 | 450.8 | 484.9 | 446.9 | 382 | 379.7 | 419.7 | 464.3 | 322.9 | 377.9
1305 | 1180 | 526.3 | 450.9 | 485 | 447 | 382.4 | 380 | 420.1 | 464.3 | 323.3 | 378.1
1306 | 1181 | 526.3 | 451 | 485 | 447.1 | 382.7 | 380.3 | 420.4 | 464.4 | 323.7 | 378.3
1307 | 1182 | 526.2 | 451 | 485 | 447.1 | 383 | 380.6 | 420.7 | 464.6 | 324.1 | 378.5
1308 | 1183 | 526.2 | 451.1 | 485 | 447.2 | 383.3 | 380.8 | 421 | 464.8 | 324.5 | 378.7
1309 | 1184 | 526.1 | 451.2 | 485.1 | 447.3 | 383.6 | 381.1 | 421.4 | 464.9 | 324.9 | 378.9
1310 | 1185 | 526.1 | 451.2 | 485.1 | 447.4 | 383.9 | 381.4 | 421.7 | 465.1 | 325.2 | 379
1311 | 1186 | 526.1 | 451.3 | 485.1 | 447.4 | 384.2 | 381.7 | 422 | 465.2 | 325.6 | 379.2
1312 | 1187 | 526.1 | 451.4 | 485.2 | 447.5 | 384.5 | 382 | 422.4 | 465.1 | 325.9 | 379.4
1313 | 1188 | 526.1 | 451.4 | 485.2 | 447.6 | 384.8 | 382.3 | 422.8 | 465.2 | 326.3 | 379.5
1314 | 1189 | 526.1 | 451.5 | 485.3 | 447.6 | 385.1 | 382.5 | 423.3 | 465.3 | 326.6 | 379.7
1315 | 1190 | 526.1 | 451.6 | 485.3 | 447.7 | 385.4 | 382.8 | 423.7 | 465.4 | 327 | 379.9
1316 | 1191 | 526.2 | 451.6 | 485.4 | 447.8 | 385.7 | 383.1 | 424.1 | 465.6 | 327.3 | 380.1
1317 | 1192 | 526.2 | 451.7 | 485.4 | 447.9 | 386 | 383.4 | 424.5 | 465.7 | 327.7 | 380.3
1318 | 1193 | 526.2 | 451.8 | 485.4 | 447.9 | 386.3 | 383.7 | 425 | 465.7 | 328 | 380.5
1319 | 1194 | 526.2 | 451.8 | 485.5 | 448 | 386.5 | 383.9 | 425.3 | 466 | 328.4 | 380.7
1320 | 1195 | 526.2 | 451.9 | 485.5 | 448.1 | 386.8 | 384.2 | 425.7 | 466.1 | 328.8 | 380.9
1321 | 1196 | 526.2 | 452 | 485.5 | 448.2 | 387.1 | 384.5 | 426.1 | 466.2 | 329.1 | 381.1
1322 | 1197 | 526.3 | 452 | 485.6 | 448.2 | 387.3 | 384.8 | 426.5 | 466.4 | 329.5 | 381.3
1323 | 1198 | 526.3 | 452.1 | 485.7 | 448.3 | 387.6 | 385.1 | 426.9 | 466.5 | 329.9 | 381.5
1324 | 1199 | 526.3 | 452.2 | 485.7 | 448.4 | 387.9 | 385.3 | 427.3 | 466.4 | 330.3 | 381.7
1325 | 1200 | 526.4 | 452.2 | 485.8 | 448.5 | 388.1 | 385.6 | 427.6 | 466.4 | 330.6 | 381.9
1326 | 1201 | 526.4 | 452.3 | 485.8 | 448.5 | 388.3 | 385.8 | 428 | 466.6 | 331 | 382.1
1327 | 1202 | 526.5 | 452.3 | 485.9 | 448.6 | 388.6 | 386.1 | 428.4 | 466.6 | 331.3 | 382.3
1328 | 1203 | 526.5 | 452.4 | 485.9 | 448.7 | 388.8 | 386.4 | 428.7 | 466.5 | 331.7 | 382.5
1329 | 1204 | 526.6 | 452.5 | 486 | 448.7 | 389 | 386.6 | 429.1 | 466.4 | 332.1 | 382.7
1330 | 1205 | 526.6 | 452.5 | 486.1 | 448.8 | 389.3 | 386.9 | 429.4 | 466.4 | 332.4 | 382.8
1331 | 1206 | 526.6 | 452.6 | 486.1 | 448.9 | 389.5 | 387.1 | 429.7 | 466.4 | 332.7 | 383
1332 | 1207 | 526.6 | 452.7 | 486.2 | 448.9 | 389.7 | 387.4 | 430.1 | 466.5 | 333 | 383.1
1333 | 1208 | 526.6 | 452.7 | 486.2 | 449 | 390 | 387.7 | 430.4 | 466.4 | 333.2 | 383.2
1334 | 1209 | 526.6 | 452.8 | 486.2 | 449.1 | 390.2 | 387.9 | 430.7 | 466.7 | 333.5 | 383.3
1335 | 1210 | 526.6 | 452.9 | 486.3 | 449.1 | 390.5 | 388.2 | 431 | 466.9 | 333.7 | 383.5
1336 | 1211 | 526.6 | 452.9 | 486.3 | 449.2 | 390.7 | 388.4 | 431.3 | 467.2 | 334 | 383.6
1337 | 1212 | 526.6 | 453 | 486.4 | 449.3 | 390.9 | 388.7 | 431.6 | 467.5 | 334.3 | 383.7
1338 | 1213 | 526.6 | 453.1 | 486.4 | 449.3 | 391.2 | 389 | 431.9 | 467.5 | 334.6 | 383.9
1339 | 1214 | 526.6 | 453.1 | 486.5 | 449.4 | 391.4 | 389.2 | 432.2 | 467.5 | 334.9 | 384.1
1340 | 1215 | 526.6 | 453.2 | 486.5 | 449.5 | 391.6 | 389.4 | 432.5 | 467.5 | 335.2 | 384.3
1341 | 1216 | 526.6 | 453.2 | 486.5 | 449.6 | 391.8 | 389.7 | 432.7 | 467.5 | 335.5 | 384.5
1342 | 1217 | 526.6 | 453.3 | 486.6 | 449.6 | 392.1 | 389.9 | 432.9 | 467.6 | 335.9 | 384.6
1343 | 1218 | 526.6 | 453.4 | 486.6 | 449.7 | 392.3 | 390.2 | 433.2 | 467.4 | 336.2 | 384.8
1344 | 1219 | 526.6 | 453.4 | 486.6 | 449.8 | 392.5 | 390.4 | 433.5 | 467.5 | 336.6 | 385
1345 | 1220 | 526.5 | 453.5 | 486.7 | 449.9 | 392.8 | 390.7 | 433.7 | 467.3 | 337 | 385.2
1346 | 1221 | 526.5 | 453.6 | 486.7 | 449.9 | 393 | 390.9 | 434 | 467.4 | 337.4 | 385.4
1347 | 1222 | 526.5 | 453.6 | 486.8 | 450 | 393.2 | 391.2 | 434.2 | 467.4 | 337.8 | 385.6
1348 | 1223 | 526.5 | 453.7 | 486.8 | 450 | 393.4 | 391.4 | 434.4 | 467.2 | 338.2 | 385.7
1349 | 1224 | 526.5 | 453.7 | 486.9 | 450.1 | 393.6 | 391.6 | 434.6 | 467.3 | 338.6 | 385.9
1350 | 1225 | 526.5 | 453.8 | 486.9 | 450.2 | 393.8 | 391.9 | 434.8 | 467.3 | 338.9 | 386.1
1351 | 1226 | 526.4 | 453.9 | 486.9 | 450.2 | 394.1 | 392.1 | 435 | 467.2 | 339.2 | 386.2
1352 | 1227 | 526.4 | 453.9 | 487 | 450.3 | 394.3 | 392.4 | 435.1 | 467 | 339.5 | 386.4
1353 | 1228 | 526.3 | 454 | 487 | 450.4 | 394.5 | 392.6 | 435.3 | 466.9 | 339.9 | 386.5
1354 | 1229 | 526.3 | 454.1 | 487 | 450.4 | 394.7 | 392.9 | 435.5 | 466.8 | 340.2 | 386.7
1355 | 1230 | 526.3 | 454.1 | 487.1 | 450.5 | 394.9 | 393.1 | 435.7 | 466.7 | 340.6 | 386.8
1356 | 1231 | 526.3 | 454.2 | 487.1 | 450.6 | 395.2 | 393.3 | 435.9 | 466.6 | 341 | 387
1357 | 1232 | 526.3 | 454.3 | 487.1 | 450.6 | 395.4 | 393.6 | 436 | 466.5 | 341.3 | 387.1
1358 | 1233 | 526.3 | 454.3 | 487.2 | 450.7 | 395.6 | 393.8 | 436.1 | 466.7 | 341.7 | 387.3
1359 | 1234 | 526.3 | 454.4 | 487.2 | 450.8 | 395.8 | 394.1 | 436.3 | 466.9 | 342 | 387.5
1360 | 1235 | 526.3 | 454.4 | 487.3 | 450.8 | 396 | 394.3 | 436.4 | 467 | 342.4 | 387.6
1361 | 1236 | 526.3 | 454.5 | 487.3 | 450.9 | 396.2 | 394.6 | 436.5 | 467 | 342.8 | 387.8
1362 | 1237 | 526.3 | 454.6 | 487.3 | 451 | 396.4 | 394.8 | 436.7 | 467 | 343.2 | 388
1363 | 1238 | 526.3 | 454.6 | 487.3 | 451.1 | 396.6 | 395 | 436.8 | 467 | 343.6 | 388.1
1364 | 1239 | 526.3 | 454.7 | 487.4 | 451.1 | 396.8 | 395.3 | 437 | 466.9 | 344 | 388.3
1365 | 1240 | 526.3 | 454.8 | 487.4 | 451.2 | 397 | 395.5 | 437.1 | 466.8 | 344.4 | 388.5
1366 | 1241 | 526.3 | 454.8 | 487.5 | 451.3 | 397.2 | 395.8 | 437.3 | 466.8 | 344.8 | 388.6
1367 | 1242 | 526.2 | 454.9 | 487.5 | 451.3 | 397.4 | 396 | 437.4 | 466.9 | 345.2 | 388.8
1368 | 1243 | 526.2 | 454.9 | 487.6 | 451.4 | 397.6 | 396.2 | 437.5 | 466.8 | 345.5 | 389
1369 | 1244 | 526.2 | 455 | 487.6 | 451.4 | 397.8 | 396.5 | 437.6 | 466.9 | 345.9 | 389.1
1370 | 1245 | 526.2 | 455.1 | 487.7 | 451.5 | 397.9 | 396.7 | 437.7 | 467 | 346.3 | 389.3
1371 | 1246 | 526.2 | 455.1 | 487.7 | 451.5 | 398.1 | 396.9 | 437.8 | 467 | 346.6 | 389.5
1372 | 1247 | 526.2 | 455.2 | 487.8 | 451.6 | 398.3 | 397.2 | 437.9 | 467.1 | 347 | 389.6
1373 | 1248 | 526.2 | 455.2 | 487.8 | 451.7 | 398.5 | 397.4 | 438 | 467.2 | 347.3 | 389.8
1374 | 1249 | 526.2 | 455.3 | 487.8 | 451.8 | 398.7 | 397.7 | 438.1 | 467.2 | 347.6 | 390
1375 | 1250 | 526.2 | 455.4 | 487.8 | 451.8 | 398.9 | 397.9 | 438.3 | 467.3 | 347.9 | 390.2
1376 | 1251 | 526.2 | 455.4 | 487.9 | 451.9 | 399.1 | 398.2 | 438.3 | 467.4 | 348.3 | 390.3
1377 | 1252 | 526.1 | 455.5 | 487.9 | 452 | 399.3 | 398.4 | 438.4 | 467.4 | 348.6 | 390.5
1378 | 1253 | 526.1 | 455.6 | 487.9 | 452 | 399.4 | 398.7 | 438.5 | 467.3 | 349 | 390.6
1379 | 1254 | 526.1 | 455.6 | 487.9 | 452.1 | 399.6 | 398.9 | 438.6 | 467.3 | 349.3 | 390.8
1380 | 1255 | 526 | 455.7 | 488 | 452.2 | 399.8 | 399.2 | 438.6 | 467.3 | 349.7 | 390.9
1381 | 1256 | 526 | 455.8 | 488 | 452.2 | 400 | 399.4 | 438.6 | 467.2 | 350 | 391.1
1382 | 1257 | 526 | 455.8 | 488.1 | 452.3 | 400.2 | 399.6 | 438.7 | 467 | 350.4 | 391.3
1383 | 1258 | 525.9 | 455.9 | 488.1 | 452.3 | 400.3 | 399.9 | 438.8 | 467 | 350.7 | 391.4
1384 | 1259 | 525.9 | 455.9 | 488.1 | 452.4 | 400.5 | 400.1 | 438.8 | 467.1 | 351 | 391.5
1385 | 1260 | 525.9 | 456 | 488.2 | 452.4 | 400.6 | 400.4 | 438.9 | 466.9 | 351.3 | 391.7
1386 | 1261 | 525.9 | 456.1 | 488.3 | 452.5 | 400.8 | 400.6 | 438.9 | 467 | 351.6 | 391.8
1387 | 1262 | 525.9 | 456.1 | 488.3 | 452.6 | 401 | 400.9 | 439 | 467.1 | 351.9 | 392
1388 | 1263 | 525.8 | 456.2 | 488.3 | 452.6 | 401.1 | 401.1 | 439.1 | 467.2 | 352.2 | 392.2
1389 | 1264 | 525.9 | 456.2 | 488.4 | 452.7 | 401.3 | 401.4 | 439.2 | 467.2 | 352.5 | 392.3
1390 | 1265 | 525.9 | 456.3 | 488.4 | 452.8 | 401.5 | 401.6 | 439.3 | 467.1 | 352.8 | 392.5
1391 | 1266 | 525.9 | 456.4 | 488.4 | 452.8 | 401.7 | 401.9 | 439.4 | 467.1 | 353.1 | 392.6
1392 | 1267 | 525.8 | 456.4 | 488.4 | 452.9 | 401.8 | 402.1 | 439.4 | 467.2 | 353.5 | 392.8
1393 | 1268 | 525.8 | 456.5 | 488.5 | 452.9 | 402 | 402.4 | 439.5 | 467.2 | 353.8 | 392.9
1394 | 1269 | 525.8 | 456.6 | 488.5 | 453 | 402.2 | 402.6 | 439.5 | 467.1 | 354 | 393.1
1395 | 1270 | 525.7 | 456.6 | 488.5 | 453.1 | 402.3 | 402.9 | 439.6 | 467.1 | 354.3 | 393.2
1396 | 1271 | 525.7 | 456.7 | 488.6 | 453.1 | 402.4 | 403.1 | 439.7 | 467 | 354.6 | 393.3
1397 | 1272 | 525.7 | 456.7 | 488.6 | 453.2 | 402.6 | 403.4 | 439.8 | 466.7 | 354.8 | 393.5
1398 | 1273 | 525.7 | 456.8 | 488.6 | 453.3 | 402.8 | 403.7 | 439.9 | 466.7 | 355.1 | 393.6
1399 | 1274 | 525.8 | 456.8 | 488.7 | 453.3 | 402.9 | 403.9 | 440 | 466.7 | 355.3 | 393.7
1400 | 1275 | 525.8 | 456.9 | 488.7 | 453.4 | 403 | 404.2 | 440 | 466.8 | 355.6 | 393.9
1401 | 1276 | 525.8 | 457 | 488.7 | 453.4 | 403.2 | 404.4 | 440.1 | 466.9 | 355.8 | 394
1402 | 1277 | 525.8 | 457 | 488.8 | 453.5 | 403.3 | 404.7 | 440.2 | 466.9 | 356 | 394.1
1403 | 1278 | 525.8 | 457.1 | 488.8 | 453.6 | 403.4 | 404.9 | 440.2 | 466.7 | 356.3 | 394.2
1404 | 1279 | 525.8 | 457.1 | 488.9 | 453.6 | 403.6 | 405.2 | 440.3 | 466.7 | 356.5 | 394.4
1405 | 1280 | 525.8 | 457.2 | 488.9 | 453.7 | 403.7 | 405.4 | 440.3 | 466.5 | 356.7 | 394.5
1406 | 1281 | 525.8 | 457.3 | 489 | 453.7 | 403.9 | 405.7 | 440.4 | 466.5 | 357 | 394.6
1407 | 1282 | 525.8 | 457.3 | 489 | 453.8 | 404 | 405.9 | 440.5 | 466.7 | 357.2 | 394.8
1408 | 1283 | 525.8 | 457.4 | 489 | 453.9 | 404.1 | 406.2 | 440.5 | 466.7 | 357.4 | 394.9
1409 | 1284 | 525.8 | 457.4 | 489.1 | 453.9 | 404.2 | 406.5 | 440.6 | 466.7 | 357.6 | 395
1410 | 1285 | 525.8 | 457.5 | 489.1 | 454 | 404.3 | 406.7 | 440.6 | 466.9 | 357.9 | 395.2
1411 | 1286 | 525.8 | 457.5 | 489.1 | 454.1 | 404.5 | 407 | 440.7 | 466.9 | 358.1 | 395.3
1412 | 1287 | 525.7 | 457.6 | 489.2 | 454.1 | 404.6 | 407.2 | 440.7 | 466.8 | 358.4 | 395.4
1413 | 1288 | 525.7 | 457.7 | 489.2 | 454.2 | 404.7 | 407.5 | 440.8 | 466.7 | 358.6 | 395.6
1414 | 1289 | 525.7 | 457.7 | 489.2 | 454.2 | 404.8 | 407.8 | 440.9 | 466.8 | 358.9 | 395.7
1415 | 1290 | 525.8 | 457.8 | 489.3 | 454.3 | 405 | 408 | 441 | 467 | 359.1 | 395.8
1416 | 1291 | 525.8 | 457.8 | 489.3 | 454.3 | 405.1 | 408.3 | 441.1 | 467.2 | 359.4 | 395.9
1417 | 1292 | 525.8 | 457.9 | 489.3 | 454.4 | 405.2 | 408.6 | 441.1 | 467.2 | 359.6 | 396.1
1418 | 1293 | 525.8 | 457.9 | 489.4 | 454.5 | 405.4 | 408.8 | 441.3 | 467.1 | 359.8 | 396.2
1419 | 1294 | 525.9 | 458 | 489.4 | 454.5 | 405.5 | 409.1 | 441.4 | 466.8 | 360.1 | 396.3
1420 | 1295 | 525.9 | 458 | 489.5 | 454.6 | 405.6 | 409.3 | 441.5 | 466.8 | 360.3 | 396.4
1421 | 1296 | 525.9 | 458.1 | 489.5 | 454.6 | 405.8 | 409.6 | 441.6 | 466.7 | 360.5 | 396.5
1422 | 1297 | 525.9 | 458.1 | 489.5 | 454.7 | 405.9 | 409.9 | 441.7 | 466.7 | 360.7 | 396.7
1423 | 1298 | 525.9 | 458.2 | 489.5 | 454.8 | 406 | 410.1 | 441.8 | 466.8 | 360.9 | 396.8
1424 | 1299 | 526 | 458.2 | 489.6 | 454.8 | 406.1 | 410.4 | 441.9 | 466.8 | 361.1 | 396.9
1425 | 1300 | 526 | 458.3 | 489.6 | 454.9 | 406.3 | 410.6 | 442 | 466.7 | 361.3 | 397
1426 | 1301 | 526 | 458.4 | 489.6 | 455 | 406.4 | 410.9 | 442 | 466.5 | 361.5 | 397.1
1427 | 1302 | 526 | 458.4 | 489.6 | 455 | 406.6 | 411.2 | 442 | 466.4 | 361.7 | 397.2
1428 | 1303 | 526.1 | 458.5 | 489.6 | 455.1 | 406.7 | 411.4 | 442.1 | 466.3 | 361.9 | 397.3
1429 | 1304 | 526.1 | 458.5 | 489.7 | 455.2 | 406.9 | 411.7 | 442.1 | 466.5 | 362.1 | 397.5
1430 | 1305 | 526.2 | 458.6 | 489.8 | 455.2 | 407 | 411.9 | 442.1 | 466.6 | 362.2 | 397.6
1431 | 1306 | 526.2 | 458.6 | 489.8 | 455.3 | 407.1 | 412.2 | 442 | 466.7 | 362.4 | 397.7
1432 | 1307 | 526.2 | 458.7 | 489.8 | 455.3 | 407.3 | 412.4 | 442 | 466.7 | 362.6 | 397.8
1433 | 1308 | 526.3 | 458.7 | 489.9 | 455.4 | 407.4 | 412.7 | 442 | 466.9 | 362.7 | 397.9
1434 | 1309 | 526.4 | 458.8 | 490 | 455.4 | 407.5 | 412.9 | 442.1 | 466.8 | 362.9 | 398
1435 | 1310 | 526.4 | 458.8 | 490 | 455.5 | 407.7 | 413.2 | 442.1 | 466.7 | 363 | 398.1
1436 | 1311 | 526.4 | 458.9 | 490 | 455.5 | 407.8 | 413.4 | 442.2 | 466.8 | 363.2 | 398.2
1437 | 1312 | 526.5 | 459 | 490.1 | 455.6 | 407.9 | 413.7 | 442.2 | 466.9 | 363.3 | 398.3
1438 | 1313 | 526.5 | 459 | 490.1 | 455.7 | 408.1 | 414 | 442.2 | 467.1 | 363.5 | 398.4
1439 | 1314 | 526.5 | 459.1 | 490.1 | 455.7 | 408.2 | 414.2 | 442.3 | 467.1 | 363.6 | 398.6
1440 | 1315 | 526.5 | 459.1 | 490.2 | 455.8 | 408.3 | 414.5 | 442.3 | 467.4 | 363.8 | 398.6
1441 | 1316 | 526.5 | 459.2 | 490.2 | 455.8 | 408.5 | 414.7 | 442.3 | 467.6 | 364 | 398.8
1442 | 1317 | 526.5 | 459.2 | 490.3 | 455.9 | 408.6 | 415 | 442.4 | 467.9 | 364.1 | 398.9
1443 | 1318 | 526.6 | 459.3 | 490.3 | 455.9 | 408.8 | 415.3 | 442.4 | 468.1 | 364.3 | 399
1444 | 1319 | 526.6 | 459.3 | 490.3 | 456 | 408.9 | 415.5 | 442.4 | 468.3 | 364.5 | 399.1
1445 | 1320 | 526.6 | 459.4 | 490.4 | 456.1 | 409 | 415.8 | 442.5 | 468.5 | 364.7 | 399.2
1446 | 1321 | 526.6 | 459.4 | 490.4 | 456.1 | 409.2 | 416 | 442.5 | 468.5 | 364.9 | 399.3
1447 | 1322 | 526.7 | 459.5 | 490.5 | 456.2 | 409.3 | 416.3 | 442.5 | 468.6 | 365.1 | 399.4
1448 | 1323 | 526.7 | 459.5 | 490.5 | 456.2 | 409.4 | 416.6 | 442.5 | 468.6 | 365.3 | 399.5
1449 | 1324 | 526.7 | 459.6 | 490.6 | 456.3 | 409.5 | 416.8 | 442.5 | 468.6 | 365.5 | 399.6
1450 | 1325 | 526.7 | 459.6 | 490.6 | 456.4 | 409.7 | 417.1 | 442.6 | 468.6 | 365.7 | 399.7
1451 | 1326 | 526.6 | 459.7 | 490.6 | 456.4 | 409.7 | 417.3 | 442.6 | 468.6 | 365.9 | 399.8
1452 | 1327 | 526.6 | 459.7 | 490.6 | 456.5 | 409.9 | 417.6 | 442.6 | 468.5 | 366.1 | 400
1453 | 1328 | 526.6 | 459.8 | 490.7 | 456.5 | 410 | 417.8 | 442.7 | 468.6 | 366.3 | 400.1
1454 | 1329 | 526.6 | 459.9 | 490.7 | 456.6 | 410.2 | 418.1 | 442.7 | 468.5 | 366.4 | 400.2
1455 | 1330 | 526.6 | 459.9 | 490.7 | 456.6 | 410.3 | 418.4 | 442.6 | 468.4 | 366.6 | 400.3
1456 | 1331 | 526.6 | 460 | 490.7 | 456.7 | 410.4 | 418.6 | 442.7 | 468.4 | 366.8 | 400.4
1457 | 1332 | 526.6 | 460 | 490.8 | 456.7 | 410.6 | 418.9 | 442.7 | 468.5 | 367 | 400.5
1458 | 1333 | 526.6 | 460.1 | 490.8 | 456.8 | 410.7 | 419.1 | 442.7 | 468.5 | 367.2 | 400.6
1459 | 1334 | 526.5 | 460.1 | 490.8 | 456.9 | 410.8 | 419.4 | 442.8 | 468.5 | 367.3 | 400.7
1460 | 1335 | 526.5 | 460.2 | 490.9 | 456.9 | 410.9 | 419.7 | 442.8 | 468.6 | 367.4 | 400.8
1461 | 1336 | 526.5 | 460.2 | 490.9 | 457 | 410.8 | 419.9 | 442.8 | 468.6 | 367.5 | 400.9
1462 | 1337 | 526.5 | 460.3 | 490.9 | 457 | 410.9 | 420.1 | 442.8 | 468.5 | 367.5 | 400.9
1463 | 1338 | 526.4 | 460.4 | 490.9 | 457.1 | 410.9 | 420.3 | 442.8 | 468.6 | 367.6 | 401
1464 | 1339 | 526.4 | 460.4 | 490.9 | 457.1 | 411 | 420.6 | 442.8 | 468.6 | 367.6 | 401.1
1465 | 1340 | 526.4 | 460.5 | 491 | 457.2 | 411.1 | 420.8 | 442.7 | 468.6 | 367.7 | 401.2
1466 | 1341 | 526.4 | 460.5 | 491 | 457.3 | 411.2 | 421.1 | 442.7 | 468.4 | 367.8 | 401.3
1467 | 1342 | 526.4 | 460.6 | 491 | 457.3 | 411.4 | 421.3 | 442.7 | 468.4 | 367.9 | 401.3
1468 | 1343 | 526.4 | 460.6 | 491.1 | 457.4 | 411.6 | 421.6 | 442.6 | 468.5 | 368 | 401.4
1469 | 1344 | 526.3 | 460.7 | 491.1 | 457.4 | 411.6 | 421.8 | 442.5 | 468.7 | 368.2 | 401.5
1470 | 1345 | 526.3 | 460.8 | 491.1 | 457.5 | 411.8 | 422.1 | 442.5 | 468.9 | 368.4 | 401.6
1471 | 1346 | 526.3 | 460.8 | 491.1 | 457.6 | 411.9 | 422.3 | 442.4 | 468.9 | 368.5 | 401.7
1472 | 1347 | 526.4 | 460.9 | 491.1 | 457.6 | 412 | 422.5 | 442.4 | 468.9 | 368.7 | 401.8
1473 | 1348 | 526.4 | 460.9 | 491.2 | 457.7 | 412.1 | 422.7 | 442.4 | 469 | 368.8 | 401.9
1474 | 1349 | 526.4 | 461 | 491.2 | 457.7 | 412.2 | 423 | 442.3 | 469.3 | 369 | 402
1475 | 1350 | 526.4 | 461 | 491.3 | 457.8 | 412.4 | 423.2 | 442.4 | 469.3 | 369.2 | 402.1
1476 | 1351 | 526.4 | 461.1 | 491.3 | 457.8 | 412.5 | 423.4 | 442.3 | 469.5 | 369.4 | 402.2
1477 | 1352 | 526.4 | 461.1 | 491.3 | 457.9 | 412.6 | 423.6 | 442.3 | 469.7 | 369.6 | 402.3
1478 | 1353 | 526.4 | 461.2 | 491.3 | 458 | 412.7 | 423.9 | 442.3 | 469.6 | 369.8 | 402.4
1479 | 1354 | 526.4 | 461.2 | 491.4 | 458 | 412.9 | 424.1 | 442.3 | 469.5 | 369.9 | 402.5
1480 | 1355 | 526.4 | 461.3 | 491.4 | 458.1 | 412.9 | 424.3 | 442.3 | 469.6 | 370.1 | 402.6
1481 | 1356 | 526.4 | 461.3 | 491.4 | 458.1 | 413.1 | 424.5 | 442.4 | 469.7 | 370.2 | 402.7
1482 | 1357 | 526.4 | 461.4 | 491.5 | 458.2 | 413.2 | 424.8 | 442.4 | 469.7 | 370.3 | 402.8
1483 | 1358 | 526.4 | 461.4 | 491.5 | 458.2 | 413.4 | 425 | 442.4 | 469.8 | 370.5 | 402.9
1484 | 1359 | 526.4 | 461.5 | 491.6 | 458.3 | 413.5 | 425.2 | 442.4 | 469.8 | 370.7 | 403
1485 | 1360 | 526.4 | 461.5 | 491.6 | 458.3 | 413.6 | 425.4 | 442.5 | 469.8 | 370.8 | 403.1
1486 | 1361 | 526.4 | 461.6 | 491.6 | 458.4 | 413.7 | 425.7 | 442.6 | 469.8 | 370.9 | 403.2
1487 | 1362 | 526.4 | 461.6 | 491.6 | 458.4 | 413.9 | 426 | 442.7 | 469.6 | 371 | 403.3
1488 | 1363 | 526.3 | 461.7 | 491.7 | 458.5 | 414 | 426.3 | 442.8 | 469.7 | 371.2 | 403.4
1489 | 1364 | 526.3 | 461.7 | 491.7 | 458.6 | 414.1 | 426.6 | 442.9 | 469.7 | 371.4 | 403.5
1490 | 1365 | 526.3 | 461.8 | 491.8 | 458.6 | 414.2 | 426.9 | 443 | 469.7 | 371.6 | 403.6
1491 | 1366 | 526.3 | 461.8 | 491.8 | 458.6 | 414.3 | 427.1 | 443 | 469.6 | 371.8 | 403.7
1492 | 1367 | 526.3 | 461.9 | 491.9 | 458.7 | 414.4 | 427.3 | 443.1 | 469.8 | 372 | 403.8
1493 | 1368 | 526.3 | 461.9 | 491.9 | 458.7 | 414.5 | 427.5 | 443.3 | 469.8 | 372.1 | 403.9
1494 | 1369 | 526.3 | 461.9 | 492 | 458.8 | 414.6 | 427.7 | 443.4 | 469.7 | 372.3 | 404.1
1495 | 1370 | 526.3 | 462 | 492 | 458.9 | 414.7 | 427.9 | 443.5 | 469.6 | 372.4 | 404.1
1496 | 1371 | 526.3 | 462 | 492 | 458.9 | 414.8 | 428.1 | 443.6 | 469.7 | 372.6 | 404.2
1497 | 1372 | 526.3 | 462.1 | 492 | 458.9 | 414.9 | 428.3 | 443.7 | 469.7 | 372.8 | 404.3
1498 | 1373 | 526.3 | 462.2 | 492 | 459 | 415 | 428.5 | 443.7 | 469.8 | 372.9 | 404.4
1499 | 1374 | 526.3 | 462.2 | 492.1 | 459.1 | 415.1 | 428.7 | 443.8 | 470 | 373.1 | 404.5
1500 | 1375 | 526.3 | 462.2 | 492.1 | 459.1 | 415.2 | 428.9 | 443.9 | 470.1 | 373.2 | 404.6
1501 | 1376 | 526.3 | 462.3 | 492.1 | 459.2 | 415.3 | 429.1 | 444 | 470.2 | 373.4 | 404.7
1502 | 1377 | 526.3 | 462.3 | 492.2 | 459.2 | 415.4 | 429.2 | 444.2 | 470.1 | 373.6 | 404.8
1503 | 1378 | 526.3 | 462.4 | 492.2 | 459.3 | 415.5 | 429.4 | 444.3 | 469.9 | 373.8 | 404.8
1504 | 1379 | 526.3 | 462.5 | 492.2 | 459.3 | 415.6 | 429.6 | 444.4 | 469.8 | 373.9 | 404.9
1505 | 1380 | 526.3 | 462.5 | 492.2 | 459.4 | 415.8 | 429.8 | 444.5 | 469.8 | 374.1 | 405
1506 | 1381 | 526.3 | 462.6 | 492.3 | 459.4 | 415.9 | 430 | 444.6 | 469.8 | 374.3 | 405.1
1507 | 1382 | 526.2 | 462.6 | 492.3 | 459.5 | 416 | 430.2 | 444.7 | 469.8 | 374.5 | 405.2
1508 | 1383 | 526.2 | 462.7 | 492.3 | 459.5 | 416.1 | 430.4 | 444.9 | 469.8 | 374.6 | 405.3
1509 | 1384 | 526.2 | 462.7 | 492.3 | 459.6 | 416.2 | 430.7 | 445 | 469.9 | 374.8 | 405.4
1510 | 1385 | 526.2 | 462.8 | 492.3 | 459.6 | 416.4 | 430.9 | 445.1 | 470.1 | 375 | 405.5
1511 | 1386 | 526.2 | 462.8 | 492.3 | 459.7 | 416.5 | 431.1 | 445.2 | 470 | 375.2 | 405.6
1512 | 1387 | 526.1 | 462.9 | 492.3 | 459.7 | 416.6 | 431.3 | 445.3 | 470.1 | 375.3 | 405.7
1513 | 1388 | 526.1 | 462.9 | 492.4 | 459.8 | 416.7 | 431.5 | 445.4 | 470.1 | 375.5 | 405.8
1514 | 1389 | 526.1 | 463 | 492.4 | 459.8 | 416.8 | 431.7 | 445.6 | 470.2 | 375.7 | 405.9
1515 | 1390 | 526.1 | 463 | 492.5 | 459.9 | 417 | 431.9 | 445.7 | 470.5 | 375.9 | 406
1516 | 1391 | 526.1 | 463.1 | 492.5 | 459.9 | 417.1 | 432.1 | 445.8 | 470.6 | 376 | 406.1
1517 | 1392 | 526.2 | 463.1 | 492.5 | 460 | 417.2 | 432.3 | 445.9 | 470.5 | 376.2 | 406.3
1518 | 1393 | 526.2 | 463.1 | 492.5 | 460 | 417.3 | 432.5 | 446 | 470.3 | 376.4 | 406.4
1519 | 1394 | 526.3 | 463.2 | 492.6 | 460.1 | 417.5 | 432.7 | 446.2 | 470.3 | 376.6 | 406.5
1520 | 1395 | 526.3 | 463.2 | 492.6 | 460.1 | 417.6 | 432.9 | 446.3 | 470.4 | 376.8 | 406.6
1521 | 1396 | 526.3 | 463.3 | 492.7 | 460.2 | 417.8 | 433.1 | 446.4 | 470.3 | 377 | 406.7
1522 | 1397 | 526.3 | 463.3 | 492.7 | 460.2 | 417.9 | 433.3 | 446.5 | 470.2 | 377.2 | 406.8
1523 | 1398 | 526.4 | 463.4 | 492.7 | 460.3 | 418.1 | 433.5 | 446.6 | 470.4 | 377.4 | 406.9
1524 | 1399 | 526.4 | 463.4 | 492.7 | 460.3 | 418.3 | 433.7 | 446.8 | 470.3 | 377.6 | 407
1525 | 1400 | 526.5 | 463.5 | 492.8 | 460.4 | 418.4 | 433.8 | 446.9 | 470.2 | 377.8 | 407.2
1526 | 1401 | 526.5 | 463.5 | 492.8 | 460.4 | 418.6 | 434 | 447 | 469.9 | 377.9 | 407.3
1527 | 1402 | 526.5 | 463.6 | 492.9 | 460.5 | 418.7 | 434.1 | 447.2 | 469.9 | 378.1 | 407.4
1528 | 1403 | 526.5 | 463.6 | 492.9 | 460.5 | 418.9 | 434.2 | 447.3 | 470.2 | 378.2 | 407.5
1529 | 1404 | 526.6 | 463.6 | 493 | 460.6 | 419 | 434.4 | 447.4 | 470.3 | 378.3 | 407.6
1530 | 1405 | 526.6 | 463.7 | 493 | 460.6 | 419.2 | 434.5 | 447.5 | 470 | 378.5 | 407.7
1531 | 1406 | 526.6 | 463.7 | 493 | 460.7 | 419.4 | 434.7 | 447.7 | 470 | 378.6 | 407.9
1532 | 1407 | 526.7 | 463.7 | 493.1 | 460.7 | 419.6 | 434.8 | 447.8 | 470 | 378.7 | 408
1533 | 1408 | 526.7 | 463.8 | 493.1 | 460.8 | 419.8 | 434.9 | 447.9 | 470 | 378.8 | 408
1534 | 1409 | 526.7 | 463.9 | 493.1 | 460.8 | 420 | 435.1 | 448.1 | 470.1 | 379 | 408.1
1535 | 1410 | 526.6 | 463.9 | 493.1 | 460.9 | 420.2 | 435.2 | 448.2 | 470.2 | 379.1 | 408.2
1536 | 1411 | 526.6 | 463.9 | 493.2 | 460.9 | 420.4 | 435.4 | 448.3 | 470.1 | 379.2 | 408.4
1537 | 1412 | 526.6 | 464 | 493.2 | 460.9 | 420.7 | 435.5 | 448.5 | 470.2 | 379.4 | 408.5
1538 | 1413 | 526.6 | 464 | 493.3 | 461 | 420.9 | 435.7 | 448.6 | 470.2 | 379.5 | 408.6
1539 | 1414 | 526.6 | 464 | 493.3 | 461 | 421.1 | 435.8 | 448.7 | 470.1 | 379.7 | 408.7
1540 | 1415 | 526.5 | 464.1 | 493.3 | 461.1 | 421.3 | 436 | 448.8 | 469.8 | 379.8 | 408.8
1541 | 1416 | 526.5 | 464.1 | 493.4 | 461.1 | 421.6 | 436.1 | 449 | 469.7 | 380 | 408.9
1542 | 1417 | 526.5 | 464.2 | 493.4 | 461.2 | 421.8 | 436.2 | 449.1 | 469.7 | 380.2 | 408.9
1543 | 1418 | 526.4 | 464.2 | 493.4 | 461.2 | 422.1 | 436.4 | 449.3 | 469.6 | 380.3 | 409
1544 | 1419 | 526.4 | 464.3 | 493.4 | 461.3 | 422.4 | 436.5 | 449.4 | 469.4 | 380.5 | 409.1
1545 | 1420 | 526.4 | 464.3 | 493.4 | 461.3 | 422.7 | 436.6 | 449.6 | 469.4 | 380.6 | 409.2
1546 | 1421 | 526.3 | 464.4 | 493.4 | 461.4 | 423 | 436.8 | 449.7 | 469.3 | 380.8 | 409.3
1547 | 1422 | 526.3 | 464.4 | 493.4 | 461.4 | 423.3 | 437 | 449.9 | 469.4 | 381 | 409.4
1548 | 1423 | 526.3 | 464.4 | 493.5 | 461.5 | 423.6 | 437.1 | 450.1 | 469.4 | 381.2 | 409.5
1549 | 1424 | 526.2 | 464.5 | 493.5 | 461.5 | 424 | 437.3 | 450.2 | 469.3 | 381.4 | 409.6
1550 | 1425 | 526.2 | 464.6 | 493.5 | 461.6 | 424.3 | 437.4 | 450.4 | 469.2 | 381.6 | 409.7
1551 | 1426 | 526.1 | 464.6 | 493.5 | 461.6 | 424.6 | 437.6 | 450.6 | 469.1 | 381.8 | 409.7
1552 | 1427 | 526.1 | 463.7 | 495.1 | 461.2 | 422.7 | 437.1 | 450.9 | 469.2 | 382.3 | 410.3
1553 | 1428 | 526 | 463.3 | 496 | 460.9 | 422 | 436.8 | 451.2 | 469.3 | 382.7 | 410.6
1554 | 1429 | 526 | 464.5 | 493.9 | 461.7 | 425.2 | 437.8 | 451.1 | 469.1 | 382.3 | 410.1
1555 | 1430 | 526 | 464.8 | 493.6 | 461.9 | 426.1 | 438.1 | 451.2 | 469.1 | 382.4 | 410.1
1556 | 1431 | 525.9 | 464.8 | 493.6 | 461.9 | 426.5 | 438.3 | 451.4 | 469.3 | 382.6 | 410.2
1557 | 1432 | 525.9 | 464.9 | 493.6 | 461.9 | 426.9 | 438.4 | 451.5 | 469.5 | 382.8 | 410.3
1558 | 1433 | 525.9 | 464.9 | 493.6 | 462 | 427.2 | 438.6 | 451.7 | 469.8 | 383 | 410.4
1559 | 1434 | 525.9 | 465 | 493.7 | 462 | 427.6 | 438.7 | 451.8 | 469.9 | 383.1 | 410.5
1560 | 1435 | 525.9 | 465 | 493.7 | 462.1 | 428.1 | 438.9 | 452 | 470 | 383.3 | 410.6
1561 | 1436 | 525.9 | 465 | 493.7 | 462.1 | 428.7 | 439 | 452.1 | 470.1 | 383.5 | 410.7
1562 | 1437 | 525.9 | 465.1 | 493.7 | 462.2 | 429.2 | 439.1 | 452.3 | 470.3 | 383.7 | 410.7
1563 | 1438 | 525.9 | 465.1 | 493.8 | 462.2 | 429.7 | 439.3 | 452.4 | 470.4 | 384 | 410.8
1564 | 1439 | 525.9 | 465.2 | 493.8 | 462.3 | 430.2 | 439.4 | 452.5 | 470.7 | 384.1 | 410.9
1565 | 1440 | 525.8 | 465.2 | 493.8 | 462.3 | 430.7 | 439.5 | 452.7 | 470.7 | 384.3 | 411
1566 | 1441 | 525.8 | 465.2 | 493.9 | 462.3 | 431.1 | 439.7 | 452.8 | 470.7 | 384.5 | 411.1
1567 | 1442 | 525.9 | 465.3 | 493.9 | 462.4 | 431.6 | 439.8 | 452.9 | 470.7 | 384.6 | 411.2
1568 | 1443 | 525.9 | 465.3 | 493.9 | 462.4 | 432.2 | 439.9 | 453.1 | 470.7 | 384.7 | 411.3
1569 | 1444 | 525.9 | 465.3 | 494 | 462.5 | 432.9 | 439.9 | 453.2 | 470.8 | 384.9 | 411.4
1570 | 1445 | 525.9 | 465.4 | 493.9 | 462.5 | 433.7 | 440 | 453.3 | 470.8 | 385 | 411.5
1571 | 1446 | 525.9 | 465.4 | 493.9 | 462.6 | 434.6 | 440.1 | 453.4 | 470.9 | 385.1 | 411.6
1572 | 1447 | 525.9 | 465.5 | 493.9 | 462.6 | 435.4 | 440 | 453.6 | 471.1 | 385.3 | 411.6
1573 | 1448 | 525.9 | 465.5 | 493.9 | 462.7 | 436.2 | 440 | 453.7 | 471.2 | 385.4 | 411.7
1574 | 1449 | 525.9 | 465.6 | 494 | 462.7 | 437.3 | 440 | 453.8 | 471.1 | 385.5 | 411.8
1575 | 1450 | 525.9 | 465.6 | 494 | 462.8 | 438.4 | 440 | 453.9 | 471.3 | 385.7 | 411.9
1576 | 1451 | 526 | 465.6 | 494.1 | 462.8 | 439.5 | 440 | 454 | 471.5 | 385.8 | 412
1577 | 1452 | 526 | 465.7 | 494.1 | 462.9 | 440.6 | 439.9 | 454.1 | 471.6 | 386 | 412
1578 | 1453 | 526 | 465.7 | 494.1 | 462.9 | 441.7 | 439.8 | 454.2 | 471.6 | 386.1 | 412.1
1579 | 1454 | 526 | 465.7 | 494.1 | 463 | 442.7 | 439.9 | 454.3 | 471.4 | 386.3 | 412.2
1580 | 1455 | 526.1 | 465.8 | 494.2 | 463 | 443.7 | 439.9 | 454.4 | 471.4 | 386.4 | 412.3
1581 | 1456 | 526.1 | 465.8 | 494.2 | 463 | 444.5 | 440.1 | 454.5 | 471.4 | 386.6 | 412.4
1582 | 1457 | 526.1 | 465.8 | 494.3 | 463.1 | 445.2 | 440.1 | 454.6 | 471.5 | 386.8 | 412.4
1583 | 1458 | 526.2 | 465.9 | 494.3 | 463.1 | 445.8 | 440 | 454.7 | 471.3 | 387 | 412.5
1584 | 1459 | 526.2 | 465.9 | 494.3 | 463.1 | 446.3 | 440 | 454.8 | 471.1 | 387.1 | 412.6
1585 | 1460 | 526.2 | 465.9 | 494.4 | 463.2 | 446.7 | 440.2 | 454.9 | 471 | 387.3 | 412.6
1586 | 1461 | 526.3 | 466 | 494.4 | 463.2 | 447.1 | 440.3 | 455 | 470.9 | 387.5 | 412.7
1587 | 1462 | 526.3 | 466 | 494.4 | 463.3 | 447.4 | 440.4 | 455.1 | 470.6 | 387.6 | 412.8
1588 | 1463 | 526.3 | 466.1 | 494.4 | 463.3 | 447.6 | 440.5 | 455.1 | 470.4 | 387.8 | 412.9
1589 | 1464 | 526.3 | 466.1 | 494.4 | 463.3 | 447.8 | 440.6 | 455.2 | 470.2 | 388 | 413
1590 | 1465 | 526.3 | 466.1 | 494.4 | 463.4 | 448 | 440.7 | 455.3 | 470.2 | 388.2 | 413.1
1591 | 1466 | 526.3 | 466.2 | 494.4 | 463.4 | 448.2 | 440.9 | 455.4 | 470.2 | 388.3 | 413.1
1592 | 1467 | 526.3 | 466.2 | 494.4 | 463.5 | 448.3 | 441 | 455.4 | 470.3 | 388.5 | 413.2
1593 | 1468 | 526.3 | 466.3 | 494.5 | 463.5 | 448.5 | 441.2 | 455.5 | 470.1 | 388.7 | 413.3
1594 | 1469 | 526.2 | 466.3 | 494.5 | 463.6 | 448.6 | 441.5 | 455.6 | 469.9 | 388.8 | 413.4
1595 | 1470 | 526.2 | 466.3 | 494.5 | 463.6 | 448.8 | 441.8 | 455.6 | 469.9 | 389 | 413.5
1596 | 1471 | 526.2 | 466.4 | 494.5 | 463.7 | 449 | 442 | 455.7 | 469.9 | 389.1 | 413.6
1597 | 1472 | 526.3 | 466.4 | 494.6 | 463.7 | 449.2 | 442.2 | 455.8 | 469.7 | 389.3 | 413.7
1598 | 1473 | 526.3 | 466.5 | 494.6 | 463.7 | 449.4 | 442.4 | 455.8 | 469.7 | 389.4 | 413.7
1599 | 1474 | 526.3 | 466.5 | 494.6 | 463.8 | 449.5 | 442.6 | 455.9 | 469.8 | 389.6 | 413.8
1600 | 1475 | 526.3 | 466.5 | 494.6 | 463.8 | 449.6 | 442.9 | 456 | 470 | 389.7 | 413.8
1601 | 1476 | 526.3 | 466.6 | 494.6 | 463.9 | 449.7 | 443.2 | 456 | 470.1 | 389.9 | 413.9
1602 | 1477 | 526.3 | 466.6 | 494.7 | 463.9 | 449.8 | 443.6 | 456.1 | 470.2 | 390 | 414
1603 | 1478 | 526.3 | 466.7 | 494.7 | 463.9 | 449.9 | 443.8 | 456.1 | 470.3 | 390.2 | 414.1
1604 | 1479 | 526.3 | 466.7 | 494.7 | 464 | 449.9 | 444 | 456.2 | 470.4 | 390.3 | 414.1
1605 | 1480 | 526.3 | 466.7 | 494.8 | 464 | 450.1 | 444.2 | 456.2 | 470.5 | 390.4 | 414.2
1606 | 1481 | 526.3 | 466.8 | 494.8 | 464.1 | 450.1 | 444.4 | 456.3 | 470.5 | 390.5 | 414.3
1607 | 1482 | 526.4 | 466.8 | 494.8 | 464.1 | 450.2 | 444.6 | 456.3 | 470.6 | 390.7 | 414.4
1608 | 1483 | 526.4 | 466.8 | 494.8 | 464.1 | 450.2 | 444.8 | 456.4 | 470.8 | 390.8 | 414.4
1609 | 1484 | 526.4 | 466.9 | 494.8 | 464.2 | 450.3 | 445 | 456.4 | 471.1 | 391 | 414.5
1610 | 1485 | 526.4 | 466.9 | 494.8 | 464.2 | 450.4 | 445.2 | 456.5 | 471.1 | 391.1 | 414.6
1611 | 1486 | 526.4 | 467 | 494.9 | 464.3 | 450.4 | 445.3 | 456.5 | 471.3 | 391.2 | 414.7
1612 | 1487 | 526.4 | 467 | 494.9 | 464.3 | 450.6 | 445.4 | 456.6 | 471.4 | 391.4 | 414.8
1613 | 1488 | 526.4 | 467 | 494.9 | 464.3 | 450.7 | 445.5 | 456.6 | 471.3 | 391.6 | 414.8
1614 | 1489 | 526.4 | 467.1 | 494.9 | 464.4 | 450.8 | 445.7 | 456.7 | 471.2 | 391.7 | 414.9
1615 | 1490 | 526.4 | 467.1 | 494.9 | 464.4 | 450.8 | 445.8 | 456.7 | 471.1 | 391.9 | 415
1616 | 1491 | 526.3 | 467.2 | 495 | 464.5 | 451 | 445.9 | 456.8 | 471 | 392 | 415.1
1617 | 1492 | 526.3 | 467.2 | 495 | 464.5 | 451.1 | 446.1 | 456.8 | 471.1 | 392.2 | 415.1
1618 | 1493 | 526.2 | 467.2 | 495 | 464.6 | 451.2 | 446.2 | 456.9 | 471.1 | 392.3 | 415.2
1619 | 1494 | 526.2 | 467.3 | 495 | 464.6 | 451.3 | 446.3 | 456.9 | 471.1 | 392.5 | 415.3
1620 | 1495 | 526.2 | 467.3 | 495 | 464.6 | 451.4 | 446.5 | 456.9 | 471.1 | 392.6 | 415.4
1621 | 1496 | 526.1 | 467.3 | 495 | 464.7 | 451.6 | 446.5 | 457 | 471 | 392.7 | 415.5
1622 | 1497 | 526.1 | 467.4 | 495.1 | 464.7 | 451.6 | 446.6 | 457 | 471 | 392.9 | 415.6
1623 | 1498 | 526.1 | 467.4 | 495.1 | 464.7 | 451.7 | 446.6 | 457.1 | 471.1 | 393 | 415.6
1624 | 1499 | 526.1 | 467.4 | 495.2 | 464.8 | 451.8 | 446.7 | 457.1 | 471.2 | 393.1 | 415.7
1625 | 1500 | 526.1 | 467.5 | 495.1 | 464.8 | 452 | 446.9 | 457.2 | 471.3 | 393.2 | 415.8
1626 | 1501 | 526.1 | 467.5 | 495.1 | 464.8 | 452.1 | 447 | 457.2 | 471.4 | 393.3 | 415.9
1627 | 1502 | 526.1 | 467.1 | 496 | 464.6 | 451.5 | 446.8 | 457.4 | 471.6 | 393.6 | 416.1
1628 | 1503 | 526 | 467 | 496.2 | 464.6 | 451.4 | 446.8 | 457.4 | 471.8 | 393.8 | 416.3
1629 | 1504 | 526 | 467.1 | 496.2 | 464.6 | 451.5 | 446.9 | 457.5 | 471.9 | 393.9 | 416.4
1630 | 1505 | 526 | 467.1 | 496.2 | 464.6 | 451.7 | 447 | 457.5 | 472.1 | 394.1 | 416.5
1631 | 1506 | 525.9 | 467.1 | 496.2 | 464.7 | 451.8 | 447.1 | 457.5 | 472 | 394.2 | 416.6
1632 | 1507 | 525.9 | 467.2 | 496.2 | 464.7 | 451.9 | 447.2 | 457.6 | 472 | 394.3 | 416.6
1633 | 1508 | 525.9 | 467.2 | 496.2 | 464.8 | 452 | 447.4 | 457.6 | 472.1 | 394.4 | 416.7
1634 | 1509 | 525.9 | 467.3 | 496.2 | 464.8 | 452.1 | 447.4 | 457.7 | 472.1 | 394.6 | 416.7
1635 | 1510 | 525.9 | 467.3 | 496.3 | 464.9 | 452.3 | 447.5 | 457.7 | 471.9 | 394.7 | 416.8
1636 | 1511 | 525.9 | 467.4 | 496.2 | 464.9 | 452.4 | 447.7 | 457.7 | 471.8 | 394.8 | 416.8
1637 | 1512 | 525.9 | 467.4 | 496.3 | 464.9 | 452.5 | 447.8 | 457.8 | 471.7 | 394.9 | 416.9
1638 | 1513 | 525.9 | 467.4 | 496.3 | 465 | 452.6 | 447.9 | 457.8 | 472 | 395 | 417
1639 | 1514 | 525.9 | 467.4 | 496.4 | 465 | 452.6 | 447.9 | 457.9 | 472.2 | 395.2 | 417
1640 | 1515 | 525.9 | 467.5 | 496.4 | 465.1 | 452.7 | 448 | 457.9 | 472.2 | 395.3 | 417.1
1641 | 1516 | 525.8 | 469 | 493.3 | 466.3 | 455.1 | 449.3 | 457.7 | 472.2 | 395 | 416.6
1642 | 1517 | 525.9 | 467.7 | 496 | 465.3 | 453.1 | 448.3 | 458 | 472.2 | 395.6 | 417.2
1643 | 1518 | 526 | 467.6 | 496.4 | 465.2 | 453 | 448.3 | 458 | 472.3 | 395.8 | 417.3
1644 | 1519 | 526 | 467.6 | 496.5 | 465.2 | 453.1 | 448.4 | 458.1 | 472.5 | 395.9 | 417.4
1645 | 1520 | 526.1 | 467.7 | 496.5 | 465.3 | 453.3 | 448.5 | 458.1 | 472.7 | 396 | 417.4
1646 | 1521 | 526.1 | 467.7 | 496.5 | 465.3 | 453.3 | 448.6 | 458.1 | 472.9 | 396.2 | 417.5
1647 | 1522 | 526.1 | 467.7 | 496.5 | 465.3 | 453.4 | 448.7 | 458.2 | 472.9 | 396.3 | 417.6
1648 | 1523 | 526.2 | 467.7 | 496.6 | 465.4 | 453.5 | 448.8 | 458.2 | 473 | 396.5 | 417.6
1649 | 1524 | 526.2 | 467.8 | 496.6 | 465.4 | 453.6 | 448.8 | 458.3 | 473 | 396.6 | 417.7
1650 | 1525 | 526.3 | 467.8 | 496.6 | 465.4 | 453.7 | 448.9 | 458.3 | 473.1 | 396.8 | 417.8
1651 | 1526 | 526.3 | 467.8 | 496.7 | 465.5 | 453.8 | 449 | 458.3 | 473.3 | 396.9 | 417.9
1652 | 1527 | 526.3 | 467.9 | 496.7 | 465.5 | 453.9 | 449.1 | 458.4 | 473.5 | 397 | 417.9
1653 | 1528 | 526.4 | 467.9 | 496.7 | 465.6 | 454 | 449.2 | 458.4 | 473.6 | 397.1 | 418
1654 | 1529 | 526.4 | 467.9 | 496.7 | 465.6 | 454.1 | 449.3 | 458.5 | 473.6 | 397.2 | 418.1
1655 | 1530 | 526.5 | 468 | 496.7 | 465.7 | 454.2 | 449.4 | 458.5 | 473.5 | 397.3 | 418.1
1656 | 1531 | 526.5 | 468 | 496.8 | 465.7 | 454.3 | 449.5 | 458.6 | 473.6 | 397.4 | 418.2
1657 | 1532 | 526.5 | 468 | 496.8 | 465.7 | 454.3 | 449.5 | 458.6 | 473.9 | 397.5 | 418.3
1658 | 1533 | 526.5 | 468.1 | 496.8 | 465.8 | 454.4 | 449.6 | 458.7 | 474 | 397.6 | 418.3
1659 | 1534 | 526.5 | 468.1 | 496.8 | 465.8 | 454.5 | 449.7 | 458.7 | 474 | 397.7 | 418.4
1660 | 1535 | 526.5 | 468.1 | 496.8 | 465.8 | 454.6 | 449.8 | 458.7 | 474.2 | 397.8 | 418.4
1661 | 1536 | 526.6 | 468.2 | 496.9 | 465.9 | 454.7 | 449.8 | 458.8 | 474.3 | 398 | 418.5
1662 | 1537 | 526.6 | 468.2 | 496.9 | 465.9 | 454.8 | 449.9 | 458.8 | 474.4 | 398.1 | 418.5
1663 | 1538 | 526.6 | 468.2 | 496.9 | 466 | 454.9 | 450 | 458.9 | 474.6 | 398.2 | 418.6
1664 | 1539 | 526.6 | 468.3 | 496.9 | 466 | 455 | 450.1 | 458.9 | 474.4 | 398.4 | 418.7
1665 | 1540 | 526.5 | 468.3 | 496.9 | 466 | 455.1 | 450.2 | 459 | 474.4 | 398.5 | 418.7
1666 | 1541 | 526.5 | 468.4 | 496.9 | 466.1 | 455.2 | 450.3 | 459 | 474.5 | 398.6 | 418.8
1667 | 1542 | 526.5 | 468.4 | 496.9 | 466.1 | 455.2 | 450.3 | 459 | 474.6 | 398.7 | 418.8
1668 | 1543 | 526.5 | 468.4 | 496.9 | 466.2 | 455.3 | 450.4 | 459.1 | 474.5 | 398.8 | 418.9
1669 | 1544 | 526.5 | 468.5 | 497 | 466.2 | 455.4 | 450.5 | 459.1 | 474.6 | 398.9 | 418.9
1670 | 1545 | 526.5 | 468.5 | 497 | 466.3 | 455.5 | 450.6 | 459.2 | 474.5 | 399 | 419
1671 | 1546 | 526.5 | 468.5 | 497 | 466.3 | 455.6 | 450.7 | 459.2 | 474.5 | 399.1 | 419
1672 | 1547 | 526.5 | 468.5 | 497 | 466.3 | 455.6 | 450.7 | 459.3 | 474.6 | 399.2 | 419.1
1673 | 1548 | 526.5 | 468.6 | 497 | 466.4 | 455.7 | 450.8 | 459.3 | 474.6 | 399.3 | 419.1
1674 | 1549 | 526.5 | 468.6 | 497 | 466.4 | 455.8 | 450.9 | 459.4 | 474.7 | 399.4 | 419.2
1675 | 1550 | 526.5 | 468.7 | 497 | 466.5 | 455.9 | 451 | 459.4 | 474.8 | 399.5 | 419.2
1676 | 1551 | 526.5 | 468.7 | 497.1 | 466.5 | 455.9 | 451 | 459.4 | 474.7 | 399.6 | 419.3
1677 | 1552 | 526.5 | 468.7 | 497.1 | 466.5 | 456 | 451.1 | 459.5 | 474.7 | 399.6 | 419.4
1678 | 1553 | 526.5 | 468.7 | 497.2 | 466.6 | 456.1 | 451.2 | 459.5 | 474.9 | 399.7 | 419.4
1679 | 1554 | 526.5 | 468.7 | 497.2 | 466.6 | 456.1 | 451.3 | 459.6 | 474.9 | 399.7 | 419.4
1680 | 1555 | 526.4 | 468.8 | 497.2 | 466.6 | 456.2 | 451.3 | 459.6 | 475 | 399.8 | 419.5
1681 | 1556 | 526.2 | 471.6 | 491.4 | 469 | 460.7 | 453.6 | 459.2 | 474.7 | 399 | 418.4
1682 | 1557 | 525.7 | 477.1 | 479.9 | 473.3 | 469.8 | 457.9 | 458.3 | 474 | 397.4 | 416.2
1683 | 1558 | 525.4 | 477.7 | 478.8 | 473.9 | 470.8 | 458.5 | 458.2 | 474 | 397.3 | 416.2
1684 | 1559 | 526.3 | 469.2 | 496.5 | 467 | 457 | 451.9 | 459.7 | 475.3 | 399.9 | 419.6
1685 | 1560 | 526.3 | 468.9 | 497.3 | 466.8 | 456.5 | 451.7 | 459.8 | 475.3 | 400 | 419.8
1686 | 1561 | 526.3 | 468.9 | 497.3 | 466.8 | 456.6 | 451.8 | 459.9 | 475.4 | 400 | 419.8
1687 | 1562 | 526.2 | 468.9 | 497.4 | 466.9 | 456.7 | 451.9 | 459.9 | 475.4 | 400 | 419.9
1688 | 1563 | 526.3 | 469 | 497.4 | 466.9 | 456.8 | 452 | 459.9 | 475.5 | 400.1 | 419.9
1689 | 1564 | 526.2 | 469 | 497.4 | 466.9 | 456.8 | 452.1 | 460 | 475.4 | 400.2 | 420
1690 | 1565 | 526.2 | 469 | 497.5 | 467 | 456.9 | 452.1 | 460 | 475.5 | 400.2 | 420
1691 | 1566 | 526.2 | 469.1 | 497.5 | 467 | 457 | 452.2 | 460 | 475.7 | 400.3 | 420
1692 | 1567 | 526.2 | 469.1 | 497.5 | 467 | 457 | 452.3 | 460.1 | 475.8 | 400.4 | 420
1693 | 1568 | 526.2 | 469.1 | 497.5 | 467.1 | 457.1 | 452.4 | 460.1 | 475.7 | 400.5 | 420.1
1694 | 1569 | 526.2 | 469.2 | 497.5 | 467.1 | 457.2 | 452.4 | 460.1 | 475.9 | 400.6 | 420.1
1695 | 1570 | 526.1 | 469.2 | 497.5 | 467.1 | 457.2 | 452.5 | 460.2 | 476.1 | 400.7 | 420.2
1696 | 1571 | 526.1 | 469.2 | 497.5 | 467.2 | 457.3 | 452.6 | 460.2 | 476.2 | 400.7 | 420.2
1697 | 1572 | 526.1 | 469.2 | 497.5 | 467.2 | 457.4 | 452.7 | 460.3 | 476.2 | 400.7 | 420.2
1698 | 1573 | 526.1 | 469.3 | 497.5 | 467.3 | 457.4 | 452.7 | 460.3 | 476.2 | 400.7 | 420.3
1699 | 1574 | 526.1 | 469.3 | 497.5 | 467.3 | 457.5 | 452.8 | 460.3 | 476.2 | 400.7 | 420.3
1700 | 1575 | 526.1 | 469.3 | 497.5 | 467.3 | 457.6 | 452.9 | 460.4 | 476.3 | 400.7 | 420.3
1701 | 1576 | 526.1 | 469.4 | 497.5 | 467.4 | 457.6 | 453 | 460.4 | 476.3 | 400.7 | 420.4
1702 | 1577 | 526.1 | 469.4 | 497.6 | 467.4 | 457.7 | 453 | 460.4 | 476.4 | 400.7 | 420.4
1703 | 1578 | 526.1 | 469.4 | 497.6 | 467.4 | 457.8 | 453.1 | 460.5 | 476.4 | 400.8 | 420.4
1704 | 1579 | 526.2 | 469.5 | 497.6 | 467.5 | 457.9 | 453.2 | 460.5 | 476.5 | 400.8 | 420.4
1705 | 1580 | 526.2 | 469.5 | 497.6 | 467.5 | 457.9 | 453.2 | 460.5 | 476.6 | 400.9 | 420.5
1706 | 1581 | 526.2 | 469.5 | 497.6 | 467.5 | 458 | 453.3 | 460.6 | 476.6 | 401 | 420.5
1707 | 1582 | 526.2 | 469.5 | 497.7 | 467.6 | 458 | 453.4 | 460.6 | 476.7 | 401.1 | 420.6
1708 | 1583 | 526.2 | 469.6 | 497.7 | 467.6 | 458.1 | 453.4 | 460.6 | 477 | 401.2 | 420.6
1709 | 1584 | 526.2 | 469.6 | 497.7 | 467.6 | 458.1 | 453.5 | 460.7 | 477.1 | 401.3 | 420.6
1710 | 1585 | 526.2 | 469.6 | 497.7 | 467.7 | 458.2 | 453.6 | 460.7 | 477.2 | 401.4 | 420.6
1711 | 1586 | 526.2 | 469.6 | 497.7 | 467.7 | 458.2 | 453.6 | 460.7 | 477.1 | 401.4 | 420.7
1712 | 1587 | 526.2 | 469.7 | 497.7 | 467.7 | 458.3 | 453.7 | 460.8 | 477.2 | 401.5 | 420.7
1713 | 1588 | 526.2 | 469.7 | 497.7 | 467.8 | 458.3 | 453.8 | 460.8 | 477.3 | 401.6 | 420.7
1714 | 1589 | 526.2 | 469.7 | 497.8 | 467.8 | 458.4 | 453.8 | 460.9 | 477.4 | 401.7 | 420.7
1715 | 1590 | 526.2 | 469.8 | 497.8 | 467.8 | 458.4 | 453.9 | 460.9 | 477.5 | 401.7 | 420.8
1716 | 1591 | 526.2 | 469.8 | 497.8 | 467.9 | 458.5 | 454 | 460.9 | 477.6 | 401.8 | 420.8
1717 | 1592 | 526.2 | 469.8 | 497.9 | 467.9 | 458.5 | 454 | 461 | 477.7 | 401.9 | 420.9
1718 | 1593 | 526.3 | 469.9 | 497.9 | 467.9 | 458.6 | 454.1 | 461 | 477.7 | 401.9 | 420.9
1719 | 1594 | 526.3 | 469.9 | 497.9 | 468 | 458.7 | 454.2 | 461 | 477.8 | 401.9 | 420.9
1720 | 1595 | 526.3 | 469.9 | 497.9 | 468 | 458.7 | 454.2 | 461.1 | 477.9 | 402 | 421
1721 | 1596 | 526.3 | 469.9 | 497.9 | 468 | 458.7 | 454.3 | 461.1 | 478.2 | 402 | 421
1722 | 1597 | 526.3 | 470 | 498 | 468.1 | 458.8 | 454.3 | 461.1 | 478.4 | 402.1 | 421
1723 | 1598 | 525.8 | 475.7 | 486.1 | 472.7 | 467.9 | 458.8 | 460.2 | 477.7 | 400.4 | 418.8
1724 | 1599 | 525.2 | 483.3 | 470 | 478.8 | 480.3 | 464.7 | 459 | 476.5 | 398.1 | 415.6
1725 | 1600 | 525.4 | 478.7 | 479.9 | 475.2 | 473.1 | 461.3 | 459.8 | 477.1 | 399.7 | 417.6
1726 | 1601 | 526.2 | 470.3 | 497.5 | 468.3 | 459.3 | 454.8 | 461.2 | 478.3 | 402.3 | 421
1727 | 1602 | 526.2 | 470.1 | 498 | 468.2 | 459 | 454.7 | 461.3 | 478.3 | 402.5 | 421.1
1728 | 1603 | 526.2 | 470.2 | 498 | 468.3 | 459.1 | 454.7 | 461.3 | 478.3 | 402.6 | 421.1
1729 | 1604 | 526.2 | 470.2 | 498 | 468.3 | 459.2 | 454.8 | 461.4 | 478.6 | 402.6 | 421.1
1730 | 1605 | 526.1 | 470.2 | 498 | 468.3 | 459.2 | 454.9 | 461.4 | 478.8 | 402.7 | 421.2
1731 | 1606 | 526.1 | 470.2 | 498.1 | 468.3 | 459.3 | 454.9 | 461.4 | 478.9 | 402.8 | 421.2
1732 | 1607 | 526.1 | 470.3 | 498.1 | 468.4 | 459.3 | 455 | 461.5 | 479 | 402.9 | 421.2
1733 | 1608 | 526 | 470.3 | 498.1 | 468.4 | 459.3 | 455 | 461.5 | 478.9 | 403 | 421.3
1734 | 1609 | 526 | 470.3 | 498.1 | 468.5 | 459.4 | 455.1 | 461.5 | 478.8 | 403.1 | 421.3
1735 | 1610 | 526 | 470.4 | 498.1 | 468.5 | 459.4 | 455.2 | 461.6 | 478.7 | 403.1 | 421.3
1736 | 1611 | 526 | 470.4 | 498.2 | 468.5 | 459.5 | 455.2 | 461.6 | 478.7 | 403.2 | 421.4
1737 | 1612 | 526 | 470.4 | 498.2 | 468.6 | 459.5 | 455.3 | 461.6 | 478.8 | 403.3 | 421.4
1738 | 1613 | 526 | 470.4 | 498.2 | 468.6 | 459.6 | 455.4 | 461.7 | 478.6 | 403.3 | 421.5
1739 | 1614 | 526 | 470.5 | 498.2 | 468.7 | 459.6 | 455.4 | 461.7 | 478.6 | 403.4 | 421.5
1740 | 1615 | 526 | 470.5 | 498.2 | 468.7 | 459.7 | 455.5 | 461.7 | 478.7 | 403.4 | 421.5
1741 | 1616 | 526 | 470.5 | 498.2 | 468.7 | 459.7 | 455.5 | 461.8 | 478.9 | 403.5 | 421.5
1742 | 1617 | 526 | 470.6 | 498.2 | 468.8 | 459.8 | 455.6 | 461.8 | 479.1 | 403.5 | 421.6
1743 | 1618 | 526 | 470.6 | 498.2 | 468.8 | 459.8 | 455.7 | 461.8 | 479.1 | 403.5 | 421.6
1744 | 1619 | 526 | 470.6 | 498.3 | 468.8 | 459.9 | 455.7 | 461.9 | 479.2 | 403.7 | 421.6
1745 | 1620 | 525.9 | 470.7 | 498.3 | 468.9 | 459.9 | 455.8 | 461.9 | 479.2 | 403.7 | 421.6
1746 | 1621 | 525.9 | 470.7 | 498.3 | 468.9 | 459.9 | 455.8 | 462 | 479 | 403.8 | 421.7
1747 | 1622 | 525.9 | 470.7 | 498.3 | 468.9 | 460 | 455.9 | 462 | 479.2 | 403.8 | 421.7
1748 | 1623 | 525.9 | 470.8 | 498.3 | 469 | 460 | 455.9 | 462 | 479.4 | 403.8 | 421.7
1749 | 1624 | 526 | 470.8 | 498.3 | 469 | 460.1 | 456 | 462 | 479.4 | 403.9 | 421.7
1750 | 1625 | 526 | 470.8 | 498.4 | 469 | 460.2 | 456 | 462.1 | 479.4 | 404 | 421.6
1751 | 1626 | 526 | 470.8 | 498.4 | 469.1 | 460.2 | 456.1 | 462.1 | 479.4 | 404.1 | 421.6
1752 | 1627 | 526 | 470.9 | 498.4 | 469.1 | 460.2 | 456.1 | 462.1 | 479.4 | 404.2 | 421.7
1753 | 1628 | 526 | 470.9 | 498.4 | 469.1 | 460.3 | 456.2 | 462.2 | 479.4 | 404.3 | 421.7
1754 | 1629 | 526 | 470.9 | 498.5 | 469.2 | 460.3 | 456.2 | 462.2 | 479.4 | 404.4 | 421.8
1755 | 1630 | 526 | 470.9 | 498.5 | 469.2 | 460.3 | 456.3 | 462.3 | 479.4 | 404.5 | 421.8
1756 | 1631 | 526.1 | 471 | 498.5 | 469.2 | 460.4 | 456.3 | 462.3 | 479.3 | 404.5 | 421.8
1757 | 1632 | 526.1 | 471 | 498.5 | 469.3 | 460.4 | 456.4 | 462.3 | 479.4 | 404.6 | 421.8
1758 | 1633 | 526.1 | 471 | 498.5 | 469.3 | 460.5 | 456.4 | 462.4 | 479.4 | 404.7 | 421.8
1759 | 1634 | 526.1 | 471.1 | 498.5 | 469.3 | 460.5 | 456.5 | 462.4 | 479.2 | 404.8 | 421.9
1760 | 1635 | 526.1 | 471.1 | 498.6 | 469.4 | 460.6 | 456.6 | 462.4 | 479.3 | 404.9 | 421.9
1761 | 1636 | 526.1 | 471.1 | 498.6 | 469.4 | 460.6 | 456.6 | 462.5 | 479.3 | 405 | 421.9
1762 | 1637 | 526.1 | 471.2 | 498.6 | 469.4 | 460.6 | 456.7 | 462.5 | 479.4 | 405.2 | 421.9
1763 | 1638 | 526.1 | 471.2 | 498.6 | 469.5 | 460.7 | 456.7 | 462.5 | 479.4 | 405.3 | 422
1764 | 1639 | 526.1 | 471.2 | 498.6 | 469.5 | 460.7 | 456.8 | 462.6 | 479.5 | 405.4 | 422
1765 | 1640 | 525.6 | 479.1 | 482 | 476 | 473 | 462.9 | 461.3 | 478.7 | 403.2 | 419
1766 | 1641 | 525.7 | 477.2 | 486.3 | 474.3 | 470.4 | 461.4 | 461.7 | 479.1 | 403.8 | 419.6
1767 | 1642 | 526 | 472.4 | 496.5 | 470.5 | 462.6 | 457.7 | 462.5 | 480 | 405.4 | 421.7
1768 | 1643 | 526.1 | 471.3 | 498.7 | 469.7 | 460.9 | 457 | 462.7 | 480.3 | 405.8 | 422.1
1769 | 1644 | 526.1 | 471.4 | 498.7 | 469.7 | 460.9 | 457 | 462.7 | 480.3 | 405.9 | 422.1
1770 | 1645 | 526.1 | 471.4 | 498.7 | 469.7 | 460.9 | 457 | 462.7 | 480.4 | 405.9 | 422.1
1771 | 1646 | 526.1 | 471.4 | 498.7 | 469.8 | 461 | 457.1 | 462.8 | 480.5 | 406 | 422.2
1772 | 1647 | 526.1 | 471.4 | 498.7 | 469.8 | 461 | 457.1 | 462.8 | 480.5 | 406.1 | 422.2
1773 | 1648 | 526.1 | 471.5 | 498.8 | 469.8 | 461 | 457.2 | 462.8 | 480.5 | 406.2 | 422.2
1774 | 1649 | 526.1 | 471.5 | 498.8 | 469.8 | 461.1 | 457.2 | 462.9 | 480.5 | 406.2 | 422.2
1775 | 1650 | 526.1 | 471.5 | 498.8 | 469.9 | 461.1 | 457.3 | 462.9 | 480.6 | 406.3 | 422.3
1776 | 1651 | 526.1 | 471.6 | 498.8 | 469.9 | 461.1 | 457.3 | 462.9 | 480.8 | 406.4 | 422.3
1777 | 1652 | 526.1 | 471.6 | 498.8 | 469.9 | 461.2 | 457.4 | 463 | 480.9 | 406.5 | 422.3
1778 | 1653 | 526.1 | 471.6 | 498.8 | 470 | 461.2 | 457.4 | 463 | 480.8 | 406.6 | 422.3
1779 | 1654 | 526.1 | 471.6 | 498.9 | 470 | 461.3 | 457.4 | 463 | 481.1 | 406.7 | 422.4
1780 | 1655 | 526.1 | 471.7 | 498.9 | 470 | 461.3 | 457.5 | 463.1 | 481.1 | 406.8 | 422.4
1781 | 1656 | 526 | 471.7 | 498.9 | 470.1 | 461.4 | 457.5 | 463.1 | 481.1 | 406.9 | 422.4
1782 | 1657 | 526 | 471.7 | 498.9 | 470.1 | 461.4 | 457.6 | 463.1 | 481.3 | 406.9 | 422.4
1783 | 1658 | 526 | 471.8 | 498.9 | 470.1 | 461.5 | 457.6 | 463.2 | 481.1 | 407 | 422.5
1784 | 1659 | 526 | 471.8 | 498.9 | 470.2 | 461.5 | 457.7 | 463.2 | 481.2 | 406.9 | 422.5
1785 | 1660 | 526 | 471.8 | 498.9 | 470.2 | 461.5 | 457.7 | 463.2 | 481.3 | 406.9 | 422.5
1786 | 1661 | 526 | 471.8 | 499 | 470.2 | 461.6 | 457.7 | 463.3 | 481.4 | 406.9 | 422.5
1787 | 1662 | 526 | 471.8 | 498.9 | 470.3 | 461.7 | 457.8 | 463.3 | 481.5 | 406.9 | 422.5
1788 | 1663 | 526 | 471.9 | 499 | 470.3 | 461.7 | 457.8 | 463.3 | 481.6 | 406.9 | 422.5
1789 | 1664 | 526 | 471.9 | 499 | 470.3 | 461.7 | 457.9 | 463.3 | 481.7 | 407 | 422.5
1790 | 1665 | 526 | 471.9 | 499 | 470.3 | 461.8 | 457.9 | 463.4 | 481.9 | 407 | 422.5
1791 | 1666 | 525.9 | 471.9 | 499 | 470.4 | 461.8 | 457.9 | 463.4 | 481.9 | 407 | 422.5
1792 | 1667 | 526 | 472 | 499 | 470.4 | 461.8 | 458 | 463.4 | 481.8 | 407.1 | 422.5
1793 | 1668 | 526 | 472 | 499.1 | 470.4 | 461.9 | 458 | 463.5 | 481.9 | 407.1 | 422.5
1794 | 1669 | 526 | 472 | 499.1 | 470.5 | 462 | 458.1 | 463.5 | 482.1 | 407.1 | 422.5
1795 | 1670 | 526 | 472.1 | 499.1 | 470.5 | 462.1 | 458.1 | 463.5 | 482 | 407.2 | 422.5
1796 | 1671 | 526 | 472.1 | 499.1 | 470.5 | 462.1 | 458.1 | 463.6 | 482.2 | 407.3 | 422.5
1797 | 1672 | 526 | 472.1 | 499.1 | 470.6 | 462.4 | 458.2 | 463.6 | 482.2 | 407.4 | 422.5
1798 | 1673 | 526 | 472.2 | 499.1 | 470.6 | 462.4 | 458.2 | 463.6 | 482.2 | 407.6 | 422.6
1799 | 1674 | 525.9 | 472.2 | 499.1 | 470.6 | 462.5 | 458.3 | 463.6 | 482.3 | 407.8 | 422.6
1800 | 1675 | 525.9 | 472.3 | 499.1 | 470.7 | 462.7 | 458.3 | 463.7 | 482.3 | 407.9 | 422.6
1801 | 1676 | 525.9 | 472.3 | 499.1 | 470.7 | 462.8 | 458.4 | 463.7 | 482.4 | 408.1 | 422.6
1802 | 1677 | 525.9 | 472.3 | 499.2 | 470.7 | 462.7 | 458.4 | 463.7 | 482.4 | 408.3 | 422.6
1803 | 1678 | 525.9 | 472.3 | 499.1 | 470.8 | 462.8 | 458.4 | 463.8 | 482.4 | 408.4 | 422.6
1804 | 1679 | 526 | 472.4 | 499.1 | 470.8 | 462.9 | 458.5 | 463.8 | 482.2 | 408.6 | 422.6
1805 | 1680 | 526 | 472.4 | 499.2 | 470.8 | 462.9 | 458.5 | 463.8 | 482 | 408.8 | 422.7
1806 | 1681 | 525.9 | 473.1 | 497.8 | 471.4 | 464.2 | 459 | 463.8 | 481.8 | 408.7 | 422.4
1807 | 1682 | 525.9 | 473.5 | 497.1 | 471.7 | 464.6 | 459.3 | 463.8 | 481.6 | 408.8 | 422.4
1808 | 1683 | 525.9 | 473.2 | 497.6 | 471.6 | 464.3 | 459.2 | 463.8 | 481.6 | 409 | 422.6
1809 | 1684 | 525.9 | 473.8 | 496.4 | 472.1 | 465.1 | 459.6 | 463.8 | 481.4 | 409 | 422.3
1810 | 1685 | 526.1 | 472.6 | 499.2 | 471 | 463.1 | 458.7 | 464 | 481.6 | 409.4 | 422.7
1811 | 1686 | 526.1 | 472.6 | 499.3 | 471 | 463.1 | 458.7 | 464 | 481.9 | 409.5 | 422.8
1812 | 1687 | 526.2 | 472.6 | 499.3 | 471.1 | 463.1 | 458.7 | 464.1 | 482 | 409.7 | 422.8
1813 | 1688 | 526.2 | 472.6 | 499.4 | 471.1 | 463.1 | 458.8 | 464.1 | 482 | 409.8 | 422.8
1814 | 1689 | 526.2 | 472.6 | 499.3 | 471.1 | 463.1 | 458.8 | 464.1 | 481.9 | 409.9 | 422.8
1815 | 1690 | 526.2 | 472.7 | 499.3 | 471.2 | 463.2 | 458.9 | 464.2 | 482 | 410.1 | 422.8
1816 | 1691 | 526.2 | 472.7 | 499.4 | 471.2 | 463.1 | 458.9 | 464.2 | 482.1 | 410.2 | 422.9
1817 | 1692 | 526.3 | 472.7 | 499.4 | 471.2 | 463.2 | 459 | 464.2 | 482 | 410.3 | 422.9
1818 | 1693 | 526.3 | 472.8 | 499.3 | 471.2 | 463.3 | 459 | 464.3 | 481.8 | 410.4 | 422.9
1819 | 1694 | 526.3 | 472.8 | 499.4 | 471.3 | 463.3 | 459 | 464.3 | 481.7 | 410.5 | 422.9
1820 | 1695 | 526.3 | 472.8 | 499.4 | 471.3 | 463.3 | 459 | 464.4 | 481.7 | 410.6 | 422.9
1821 | 1696 | 526.3 | 472.8 | 499.4 | 471.3 | 463.4 | 459.1 | 464.4 | 481.7 | 410.6 | 422.9
1822 | 1697 | 526.3 | 472.9 | 499.5 | 471.4 | 463.4 | 459.1 | 464.4 | 481.6 | 410.6 | 423
1823 | 1698 | 526.3 | 472.8 | 499.5 | 471.4 | 463.4 | 459.1 | 464.5 | 481.6 | 410.6 | 423
1824 | 1699 | 526.3 | 472.9 | 499.5 | 471.4 | 463.5 | 459.2 | 464.5 | 481.6 | 410.6 | 423
1825 | 1700 | 526.3 | 472.9 | 499.5 | 471.4 | 463.5 | 459.2 | 464.5 | 481.8 | 410.6 | 422.9
1826 | 1701 | 526.3 | 473 | 499.6 | 471.5 | 463.5 | 459.3 | 464.6 | 481.9 | 410.5 | 422.9
1827 | 1702 | 526.2 | 473 | 499.6 | 471.5 | 463.6 | 459.3 | 464.6 | 482.1 | 410.5 | 422.9
1828 | 1703 | 526.2 | 473 | 499.5 | 471.5 | 463.6 | 459.3 | 464.6 | 482.3 | 410.5 | 422.9
1829 | 1704 | 526.2 | 473.1 | 499.5 | 471.5 | 463.6 | 459.4 | 464.6 | 482.2 | 410.5 | 422.9
1830 | 1705 | 526.2 | 473.1 | 499.6 | 471.6 | 463.6 | 459.4 | 464.7 | 482 | 410.5 | 422.8
1831 | 1706 | 526.1 | 473.1 | 499.6 | 471.6 | 463.8 | 459.4 | 464.7 | 482.1 | 410.5 | 422.8
1832 | 1707 | 526.1 | 473.1 | 499.6 | 471.6 | 463.8 | 459.5 | 464.7 | 482.4 | 410.5 | 422.8
1833 | 1708 | 526.1 | 473.1 | 499.6 | 471.6 | 463.8 | 459.5 | 464.8 | 482.4 | 410.5 | 422.8
1834 | 1709 | 526.1 | 473.2 | 499.6 | 471.7 | 463.8 | 459.5 | 464.8 | 482.4 | 410.6 | 422.7
1835 | 1710 | 526.1 | 473.1 | 499.8 | 471.7 | 463.7 | 459.5 | 464.9 | 482.3 | 410.6 | 422.8
1836 | 1711 | 526 | 472.9 | 500 | 471.6 | 463.3 | 459.4 | 464.9 | 482.5 | 410.8 | 422.8
1837 | 1712 | 526 | 472.9 | 500.1 | 471.6 | 463.1 | 459.4 | 465 | 482.5 | 410.9 | 422.8
1838 | 1713 | 526 | 472.9 | 500.1 | 471.6 | 462.9 | 459.4 | 465 | 482.5 | 411 | 422.8
1839 | 1714 | 526 | 473 | 500.1 | 471.6 | 462.9 | 459.4 | 465.1 | 482.6 | 411.1 | 422.8
1840 | 1715 | 525.9 | 473 | 500.1 | 471.6 | 463 | 459.4 | 465.1 | 482.5 | 411.2 | 422.8
1841 | 1716 | 525.9 | 473 | 500.1 | 471.7 | 463.1 | 459.5 | 465.1 | 482.6 | 411.3 | 422.8
1842 | 1717 | 525.9 | 473 | 500.1 | 471.7 | 463.1 | 459.5 | 465.2 | 482.8 | 411.4 | 422.8
1843 | 1718 | 525.8 | 473.1 | 500.1 | 471.7 | 463.2 | 459.5 | 465.2 | 483 | 411.5 | 422.8
1844 | 1719 | 525.8 | 473.1 | 500.2 | 471.7 | 463.1 | 459.6 | 465.2 | 483.1 | 411.6 | 422.9
1845 | 1720 | 525.8 | 473.1 | 500.1 | 471.8 | 463.1 | 459.6 | 465.2 | 483.3 | 411.8 | 422.9
1846 | 1721 | 525.8 | 473.2 | 500.1 | 471.8 | 463.2 | 459.6 | 465.3 | 483.3 | 411.9 | 422.9
1847 | 1722 | 525.8 | 473.2 | 500.2 | 471.8 | 463.1 | 459.7 | 465.3 | 483.3 | 412 | 422.9
1848 | 1723 | 525.8 | 473.2 | 500.2 | 471.8 | 463 | 459.7 | 465.4 | 483.2 | 412.2 | 422.9
1849 | 1724 | 525.8 | 473.5 | 499.7 | 472.1 | 463.6 | 460 | 465.3 | 483.2 | 412.3 | 422.9
1850 | 1725 | 525.8 | 473.7 | 499.5 | 472.3 | 463.8 | 460.1 | 465.4 | 483.3 | 412.4 | 422.9
1851 | 1726 | 525.9 | 473.4 | 500 | 472 | 463.3 | 459.9 | 465.4 | 483.2 | 412.6 | 423
1852 | 1727 | 525.9 | 473.3 | 500.3 | 472 | 463.2 | 459.8 | 465.5 | 483.2 | 412.8 | 423
1853 | 1728 | 526 | 473.3 | 500.3 | 472 | 463.2 | 459.9 | 465.5 | 483.1 | 413 | 423.1
1854 | 1729 | 526 | 473.3 | 500.3 | 472 | 463.1 | 459.9 | 465.6 | 483 | 413.1 | 423.1
1855 | 1730 | 526 | 473.4 | 500.3 | 472.1 | 463.2 | 459.9 | 465.6 | 483 | 413.2 | 423.1
1856 | 1731 | 526 | 473.4 | 500.3 | 472.1 | 463.2 | 460 | 465.6 | 483 | 413.4 | 423.1
1857 | 1732 | 526 | 473.4 | 500.3 | 472.1 | 463 | 460 | 465.7 | 482.9 | 413.5 | 423.1
1858 | 1733 | 526.1 | 473.5 | 500.4 | 472.2 | 463 | 460 | 465.7 | 482.9 | 413.6 | 423.1
1859 | 1734 | 526.1 | 473.6 | 500.2 | 472.3 | 463.3 | 460.1 | 465.7 | 483.1 | 413.7 | 423.1
1860 | 1735 | 526.1 | 473.5 | 500.4 | 472.2 | 463.2 | 460.1 | 465.7 | 483.2 | 413.8 | 423.1
1861 | 1736 | 526.1 | 473.5 | 500.4 | 472.2 | 463.1 | 460.1 | 465.8 | 483.3 | 413.9 | 423.1
1862 | 1737 | 526.2 | 473.6 | 500.4 | 472.3 | 463.1 | 460.2 | 465.8 | 483.5 | 414 | 423.1
1863 | 1738 | 526.2 | 473.6 | 500.4 | 472.3 | 463.2 | 460.2 | 465.8 | 483.6 | 414.1 | 423.1
1864 | 1739 | 526.2 | 473.6 | 500.4 | 472.3 | 463.2 | 460.2 | 465.9 | 483.8 | 414.1 | 423.1
1865 | 1740 | 526.2 | 473.7 | 500.3 | 472.4 | 463.4 | 460.3 | 465.9 | 484 | 414.2 | 423
1866 | 1741 | 526.3 | 473.7 | 500.4 | 472.4 | 463.4 | 460.3 | 465.9 | 484 | 414.3 | 423
1867 | 1742 | 526.3 | 473.7 | 500.4 | 472.4 | 463.5 | 460.3 | 466 | 483.9 | 414.4 | 423
1868 | 1743 | 526.3 | 473.7 | 500.5 | 472.4 | 463.5 | 460.3 | 466 | 483.6 | 414.5 | 423
1869 | 1744 | 526.3 | 473.8 | 500.5 | 472.5 | 463.5 | 460.3 | 466.1 | 483.7 | 414.7 | 423
1870 | 1745 | 526.3 | 473.8 | 500.5 | 472.5 | 463.6 | 460.4 | 466.1 | 483.7 | 414.8 | 423
1871 | 1746 | 526.3 | 473.8 | 500.5 | 472.5 | 463.6 | 460.4 | 466.1 | 483.5 | 414.9 | 423
1872 | 1747 | 526.3 | 473.8 | 500.5 | 472.5 | 463.6 | 460.4 | 466.2 | 483.3 | 415.1 | 423
1873 | 1748 | 526.3 | 473.9 | 500.5 | 472.6 | 463.7 | 460.5 | 466.2 | 483.2 | 415.2 | 423
1874 | 1749 | 526.3 | 473.9 | 500.5 | 472.6 | 463.8 | 460.5 | 466.2 | 483.2 | 415.3 | 423
1875 | 1750 | 526.3 | 473.9 | 500.6 | 472.6 | 463.8 | 460.5 | 466.3 | 483.3 | 415.4 | 423
1876 | 1751 | 526.3 | 474 | 500.6 | 472.7 | 463.9 | 460.6 | 466.3 | 483.2 | 415.5 | 423.1
1877 | 1752 | 526.2 | 474 | 500.6 | 472.7 | 464 | 460.6 | 466.3 | 483.4 | 415.6 | 423.1
1878 | 1753 | 526.2 | 474 | 500.6 | 472.7 | 464.1 | 460.6 | 466.3 | 483.7 | 415.7 | 423.1
1879 | 1754 | 526.2 | 474 | 500.6 | 472.7 | 464.1 | 460.6 | 466.4 | 483.9 | 415.7 | 423.1
1880 | 1755 | 526.2 | 474.1 | 500.6 | 472.8 | 464.2 | 460.7 | 466.4 | 484.2 | 415.8 | 423.1
1881 | 1756 | 526.1 | 474.1 | 500.5 | 472.8 | 464.2 | 460.7 | 466.4 | 484.2 | 415.9 | 423.1
1882 | 1757 | 526.1 | 474.1 | 500.6 | 472.8 | 464.2 | 460.7 | 466.5 | 484.3 | 416 | 423.1
1883 | 1758 | 526.1 | 474.1 | 500.6 | 472.9 | 464.3 | 460.7 | 466.5 | 484.2 | 416.1 | 423.1
1884 | 1759 | 526 | 474.2 | 500.5 | 472.9 | 464.4 | 460.8 | 466.5 | 484 | 416.3 | 423.1
1885 | 1760 | 526 | 474.2 | 500.5 | 473 | 464.5 | 460.8 | 466.6 | 483.9 | 416.4 | 423.1
1886 | 1761 | 526 | 474.2 | 500.7 | 472.9 | 464.4 | 460.8 | 466.6 | 484 | 416.6 | 423.1
1887 | 1762 | 525.9 | 474.2 | 500.6 | 473 | 464.5 | 460.9 | 466.7 | 484.3 | 416.7 | 423.1
1888 | 1763 | 525.9 | 474.3 | 500.6 | 473 | 464.6 | 460.9 | 466.7 | 484.3 | 416.8 | 423.1
1889 | 1764 | 525.9 | 474.3 | 500.7 | 473 | 464.6 | 460.9 | 466.7 | 484.2 | 417 | 423.1
1890 | 1765 | 525.9 | 474.3 | 500.6 | 473.1 | 464.6 | 460.9 | 466.8 | 484.1 | 417.1 | 423.1
1891 | 1766 | 525.9 | 474.3 | 500.7 | 473.1 | 464.7 | 461 | 466.8 | 484.1 | 417.2 | 423.2
1892 | 1767 | 525.9 | 474.3 | 500.7 | 473.1 | 464.7 | 461 | 466.8 | 484.2 | 417.4 | 423.2
1893 | 1768 | 525.9 | 474.4 | 500.7 | 473.1 | 464.7 | 461 | 466.9 | 484.3 | 417.5 | 423.2
1894 | 1769 | 525.9 | 474.4 | 500.7 | 473.2 | 464.8 | 461 | 466.9 | 484.4 | 417.6 | 423.2
1895 | 1770 | 525.9 | 474.4 | 500.7 | 473.2 | 464.8 | 461.1 | 466.9 | 484.6 | 417.8 | 423.2
1896 | 1771 | 525.9 | 474.4 | 500.8 | 473.2 | 464.8 | 461.1 | 467 | 484.7 | 417.9 | 423.2
1897 | 1772 | 525.9 | 474.4 | 500.8 | 473.2 | 464.9 | 461.1 | 467 | 484.6 | 418 | 423.3
1898 | 1773 | 525.8 | 474.5 | 500.7 | 473.3 | 464.9 | 461.2 | 467 | 484.6 | 418.1 | 423.3
1899 | 1774 | 525.8 | 474.5 | 500.7 | 473.3 | 465 | 461.2 | 467.1 | 484.7 | 418.1 | 423.3
1900 | 1775 | 525.7 | 474.5 | 500.8 | 473.3 | 465 | 461.2 | 467.1 | 484.9 | 418.2 | 423.3
1901 | 1776 | 525.7 | 474.6 | 500.7 | 473.4 | 465.1 | 461.3 | 467.1 | 485.1 | 418.3 | 423.3
1902 | 1777 | 525.7 | 474.6 | 500.7 | 473.4 | 465.2 | 461.3 | 467.2 | 485.3 | 418.3 | 423.3
1903 | 1778 | 525.7 | 474.6 | 500.8 | 473.4 | 465.1 | 461.3 | 467.2 | 485.5 | 418.4 | 423.3
1904 | 1779 | 525.7 | 474.6 | 500.8 | 473.4 | 465.2 | 461.3 | 467.2 | 485.6 | 418.4 | 423.3
1905 | 1780 | 525.7 | 474.7 | 500.8 | 473.5 | 465.3 | 461.4 | 467.3 | 485.4 | 418.4 | 423.3
1906 | 1781 | 525.7 | 474.7 | 500.8 | 473.5 | 465.3 | 461.4 | 467.3 | 485.2 | 418.5 | 423.3
1907 | 1782 | 525.7 | 474.7 | 500.9 | 473.5 | 465.2 | 461.4 | 467.3 | 485.2 | 418.5 | 423.3
1908 | 1783 | 525.7 | 474.7 | 500.8 | 473.6 | 465.4 | 461.5 | 467.3 | 485.1 | 418.5 | 423.3
1909 | 1784 | 525.7 | 474.8 | 500.8 | 473.6 | 465.4 | 461.5 | 467.4 | 485 | 418.5 | 423.3
1910 | 1785 | 525.7 | 474.8 | 500.8 | 473.6 | 465.4 | 461.5 | 467.4 | 485 | 418.6 | 423.3
1911 | 1786 | 525.7 | 474.8 | 500.8 | 473.6 | 465.4 | 461.5 | 467.5 | 485 | 418.6 | 423.3
1912 | 1787 | 525.7 | 474.8 | 500.8 | 473.7 | 465.5 | 461.6 | 467.5 | 484.8 | 418.7 | 423.3
1913 | 1788 | 525.7 | 474.9 | 500.8 | 473.7 | 465.5 | 461.6 | 467.5 | 484.9 | 418.7 | 423.3
1914 | 1789 | 525.6 | 474.8 | 500.9 | 473.7 | 465.5 | 461.6 | 467.5 | 484.9 | 418.8 | 423.3
1915 | 1790 | 525.6 | 474.9 | 500.8 | 473.7 | 465.6 | 461.7 | 467.6 | 485 | 418.9 | 423.3
1916 | 1791 | 525.6 | 474.9 | 500.9 | 473.8 | 465.6 | 461.7 | 467.6 | 485.1 | 419 | 423.3
1917 | 1792 | 525.6 | 474.9 | 501 | 473.8 | 465.5 | 461.7 | 467.7 | 485 | 419.1 | 423.4
1918 | 1793 | 525.7 | 474.9 | 500.9 | 473.8 | 465.6 | 461.7 | 467.7 | 485.2 | 419.2 | 423.4
1919 | 1794 | 525.7 | 475 | 500.9 | 473.8 | 465.6 | 461.8 | 467.7 | 485.1 | 419.2 | 423.4
1920 | 1795 | 525.7 | 475 | 500.9 | 473.9 | 465.7 | 461.8 | 467.7 | 485.2 | 419.3 | 423.4
1921 | 1796 | 525.7 | 475 | 501 | 473.9 | 465.6 | 461.8 | 467.8 | 485.3 | 419.4 | 423.4
1922 | 1797 | 525.8 | 475.1 | 501 | 473.9 | 465.7 | 461.9 | 467.8 | 485.3 | 419.4 | 423.4
1923 | 1798 | 525.8 | 475.1 | 501 | 474 | 465.7 | 461.9 | 467.8 | 485.4 | 419.5 | 423.4
1924 | 1799 | 525.8 | 475.1 | 501 | 474 | 465.8 | 461.9 | 467.9 | 485.4 | 419.6 | 423.4
1925 | 1800 | 525.8 | 475.1 | 501 | 474 | 465.8 | 462 | 467.9 | 485.2 | 419.7 | 423.5
1926 | 1801 | 525.8 | 475.2 | 501 | 474 | 465.9 | 462 | 467.9 | 485.2 | 419.8 | 423.5
1927 | 1802 | 525.9 | 475.2 | 501 | 474.1 | 465.9 | 462 | 468 | 485.1 | 420 | 423.5
1928 | 1803 | 525.9 | 475.1 | 501.1 | 474.1 | 465.8 | 462 | 468 | 485.1 | 420.1 | 423.5
1929 | 1804 | 525.9 | 475.2 | 501.1 | 474.1 | 465.9 | 462.1 | 468 | 485 | 420.1 | 423.6
1930 | 1805 | 525.9 | 475.2 | 501.1 | 474.1 | 465.9 | 462.1 | 468.1 | 485.1 | 420.2 | 423.6
1931 | 1806 | 526 | 475.2 | 501.2 | 474.1 | 465.9 | 462.1 | 468.1 | 485.1 | 420.2 | 423.6
1932 | 1807 | 526 | 475.3 | 501.2 | 474.2 | 465.9 | 462.2 | 468.1 | 485.3 | 420.3 | 423.6
1933 | 1808 | 525.9 | 475.3 | 501.1 | 474.2 | 466 | 462.2 | 468.1 | 485.3 | 420.3 | 423.6
1934 | 1809 | 525.9 | 475.3 | 501.1 | 474.2 | 466 | 462.2 | 468.2 | 485.2 | 420.4 | 423.6
1935 | 1810 | 525.9 | 475.3 | 501.2 | 474.2 | 465.9 | 462.2 | 468.2 | 485.2 | 420.5 | 423.7
1936 | 1811 | 525.9 | 475.3 | 501.2 | 474.2 | 466 | 462.3 | 468.3 | 485.1 | 420.6 | 423.7
1937 | 1812 | 525.9 | 475.4 | 501.1 | 474.3 | 466.1 | 462.4 | 468.3 | 485.1 | 420.6 | 423.7
1938 | 1813 | 526 | 475.4 | 501.2 | 474.3 | 466.1 | 462.4 | 468.3 | 485 | 420.7 | 423.7
1939 | 1814 | 526 | 475.4 | 501.2 | 474.3 | 466.1 | 462.4 | 468.4 | 485.2 | 420.7 | 423.8
1940 | 1815 | 526 | 475.5 | 501.2 | 474.4 | 466.2 | 462.4 | 468.4 | 485.5 | 420.8 | 423.8
1941 | 1816 | 526 | 475.5 | 501.2 | 474.4 | 466.3 | 462.5 | 468.4 | 485.7 | 420.9 | 423.8
1942 | 1817 | 526 | 475.5 | 501.3 | 474.4 | 466.2 | 462.5 | 468.5 | 485.9 | 420.9 | 423.8
1943 | 1818 | 526 | 475.5 | 501.2 | 474.5 | 466.3 | 462.5 | 468.5 | 486 | 421 | 423.8
1944 | 1819 | 526.1 | 475.6 | 501.2 | 474.5 | 466.4 | 462.6 | 468.5 | 485.9 | 421.1 | 423.8
1945 | 1820 | 526.1 | 475.6 | 501.2 | 474.5 | 466.3 | 462.6 | 468.6 | 485.6 | 421.2 | 423.8
1946 | 1821 | 526.1 | 475.6 | 501.2 | 474.5 | 466.4 | 462.6 | 468.6 | 485.4 | 421.2 | 423.9
1947 | 1822 | 526.1 | 475.7 | 501.2 | 474.6 | 466.5 | 462.7 | 468.6 | 485.3 | 421.3 | 423.9
1948 | 1823 | 526 | 475.7 | 501.2 | 474.6 | 466.6 | 462.7 | 468.7 | 485.4 | 421.4 | 423.9
1949 | 1824 | 526 | 475.7 | 501.3 | 474.6 | 466.5 | 462.8 | 468.7 | 485.7 | 421.6 | 423.9
1950 | 1825 | 526 | 475.8 | 501.2 | 474.7 | 466.7 | 462.8 | 468.7 | 485.7 | 421.7 | 423.9
1951 | 1826 | 526 | 475.8 | 501.2 | 474.7 | 466.7 | 462.8 | 468.8 | 485.9 | 421.8 | 424
1952 | 1827 | 526 | 475.8 | 501.3 | 474.7 | 466.7 | 462.9 | 468.8 | 486 | 421.9 | 424
1953 | 1828 | 526 | 475.8 | 501.3 | 474.7 | 466.7 | 462.9 | 468.9 | 486.1 | 421.9 | 424
1954 | 1829 | 526 | 475.8 | 501.3 | 474.8 | 466.7 | 462.9 | 468.9 | 486.3 | 422 | 424.1
1955 | 1830 | 526 | 475.8 | 501.3 | 474.8 | 466.8 | 463 | 468.9 | 486.6 | 422 | 424.1
1956 | 1831 | 526 | 475.8 | 501.4 | 474.8 | 466.7 | 463 | 469 | 486.4 | 422.1 | 424.2
1957 | 1832 | 526 | 475.9 | 501.3 | 474.8 | 466.8 | 463 | 469 | 486.6 | 422.1 | 424.1
1958 | 1833 | 525.9 | 475.9 | 501.4 | 474.9 | 466.8 | 463 | 469 | 486.7 | 422.1 | 424.2
1959 | 1834 | 525.9 | 475.9 | 501.5 | 474.9 | 466.8 | 463 | 469.1 | 486.9 | 422.1 | 424.2
1960 | 1835 | 525.9 | 475.9 | 501.4 | 474.9 | 466.8 | 463.1 | 469.1 | 487 | 422.1 | 424.2
1961 | 1836 | 525.9 | 475.9 | 501.4 | 474.9 | 466.9 | 463.1 | 469.2 | 486.9 | 422.2 | 424.2
1962 | 1837 | 525.9 | 476 | 501.4 | 475 | 466.9 | 463.2 | 469.2 | 486.9 | 422.2 | 424.2
1963 | 1838 | 525.9 | 475.9 | 501.5 | 475 | 466.9 | 463.2 | 469.2 | 487 | 422.3 | 424.2
1964 | 1839 | 525.9 | 476 | 501.5 | 475 | 467 | 463.2 | 469.3 | 487.1 | 422.4 | 424.3
1965 | 1840 | 525.9 | 476 | 501.5 | 475 | 467 | 463.3 | 469.3 | 487.2 | 422.5 | 424.3
1966 | 1841 | 525.9 | 476 | 501.5 | 475.1 | 467 | 463.3 | 469.3 | 487.4 | 422.6 | 424.4
1967 | 1842 | 525.9 | 476.1 | 501.5 | 475.1 | 467 | 463.3 | 469.4 | 487.5 | 422.7 | 424.4
1968 | 1843 | 525.6 | 477.7 | 498.1 | 476.5 | 469.5 | 464.5 | 469.2 | 487.3 | 422.4 | 424
1969 | 1844 | 525.2 | 480.2 | 492.8 | 478.6 | 473.1 | 466.3 | 468.9 | 487 | 421.9 | 423.3
1970 | 1845 | 525.9 | 476.1 | 501.5 | 475.2 | 467.1 | 463.4 | 469.5 | 487.7 | 422.9 | 424.5
1971 | 1846 | 525.9 | 476.2 | 501.5 | 475.2 | 467.2 | 463.5 | 469.5 | 487.8 | 423 | 424.5
1972 | 1847 | 525.9 | 476.2 | 501.5 | 475.2 | 467.3 | 463.5 | 469.6 | 487.8 | 423 | 424.5
1973 | 1848 | 525.9 | 476.2 | 501.6 | 475.2 | 467.2 | 463.5 | 469.6 | 487.9 | 423.1 | 424.5
1974 | 1849 | 525.1 | 480.8 | 491.6 | 479.2 | 474.5 | 467 | 468.9 | 487.5 | 422.1 | 423.2
1975 | 1850 | 525.7 | 477.1 | 499.7 | 476.1 | 468.8 | 464.3 | 469.5 | 487.8 | 423 | 424.4
1976 | 1851 | 525.8 | 476.3 | 501.5 | 475.3 | 467.4 | 463.7 | 469.7 | 487.7 | 423.3 | 424.6
1977 | 1852 | 525.7 | 477.1 | 499.9 | 476.1 | 468.8 | 464.3 | 469.6 | 487.6 | 423.2 | 424.4
1978 | 1853 | 525.8 | 476.3 | 501.6 | 475.4 | 467.4 | 463.7 | 469.8 | 487.8 | 423.4 | 424.7
1979 | 1854 | 525.8 | 476.3 | 501.6 | 475.4 | 467.5 | 463.8 | 469.8 | 487.8 | 423.4 | 424.7
1980 | 1855 | 525.8 | 476.3 | 501.7 | 475.4 | 467.4 | 463.8 | 469.9 | 487.7 | 423.5 | 424.8
1981 | 1856 | 525.7 | 476.4 | 501.7 | 475.4 | 467.4 | 463.8 | 469.9 | 487.9 | 423.5 | 424.8
1982 | 1857 | 525.7 | 476.4 | 501.6 | 475.5 | 467.5 | 463.9 | 470 | 487.8 | 423.6 | 424.8
1983 | 1858 | 525.7 | 476.3 | 501.8 | 475.5 | 467.3 | 463.8 | 470 | 487.9 | 423.7 | 424.9
1984 | 1859 | 525.7 | 476.3 | 501.9 | 475.4 | 467.2 | 463.8 | 470.1 | 488 | 423.7 | 425
1985 | 1860 | 525.7 | 476.3 | 501.9 | 475.5 | 467.3 | 463.9 | 470.1 | 488 | 423.7 | 425
1986 | 1861 | 525.7 | 476.3 | 502 | 475.5 | 467.3 | 463.9 | 470.1 | 488 | 423.8 | 425
1987 | 1862 | 525.7 | 476.3 | 502 | 475.5 | 467.3 | 463.9 | 470.2 | 488.3 | 423.8 | 425.1
1988 | 1863 | 525.7 | 476.4 | 502 | 475.5 | 467.3 | 464 | 470.2 | 488.3 | 423.8 | 425.1
1989 | 1864 | 525.8 | 476.4 | 502 | 475.6 | 467.4 | 464 | 470.2 | 488.3 | 423.8 | 425.1
1990 | 1865 | 525.8 | 476.4 | 502 | 475.6 | 467.4 | 464 | 470.3 | 488.4 | 423.9 | 425.1
1991 | 1866 | 525.8 | 476.5 | 501.8 | 475.7 | 467.6 | 464.1 | 470.3 | 488.4 | 424 | 425.1
1992 | 1867 | 525.8 | 476.5 | 502 | 475.6 | 467.5 | 464.1 | 470.4 | 488.6 | 424 | 425.2
1993 | 1868 | 525.8 | 476.5 | 502 | 475.7 | 467.5 | 464.1 | 470.4 | 488.6 | 424.1 | 425.2
1994 | 1869 | 525.8 | 476.5 | 502.1 | 475.7 | 467.5 | 464.2 | 470.4 | 488.4 | 424.2 | 425.2
1995 | 1870 | 525.8 | 476.5 | 502.1 | 475.7 | 467.5 | 464.2 | 470.5 | 488.5 | 424.2 | 425.2
1996 | 1871 | 525.8 | 476.6 | 502 | 475.8 | 467.6 | 464.2 | 470.5 | 488.7 | 424.2 | 425.3
1997 | 1872 | 525.8 | 476.6 | 502.1 | 475.8 | 467.6 | 464.3 | 470.5 | 488.8 | 424.2 | 425.3
1998 | 1873 | 525.8 | 476.6 | 502.1 | 475.8 | 467.6 | 464.3 | 470.6 | 488.7 | 424.3 | 425.3
1999 | 1874 | 525.8 | 476.6 | 502.1 | 475.8 | 467.7 | 464.3 | 470.6 | 488.6 | 424.3 | 425.4
2000 | 1875 | 525.9 | 476.6 | 502.1 | 475.8 | 467.7 | 464.4 | 470.6 | 488.7 | 424.3 | 425.4
2001 | 1876 | 525.9 | 476.6 | 502.2 | 475.8 | 467.7 | 464.4 | 470.7 | 488.7 | 424.3 | 425.5
2002 | 1877 | 525.9 | 476.6 | 502.2 | 475.9 | 467.7 | 464.4 | 470.7 | 488.9 | 424.3 | 425.5
2003 | 1878 | 525.9 | 476.7 | 502.1 | 475.9 | 467.8 | 464.5 | 470.8 | 488.9 | 424.3 | 425.5
2004 | 1879 | 525.9 | 476.7 | 502.2 | 475.9 | 467.8 | 464.5 | 470.8 | 488.6 | 424.4 | 425.5
2005 | 1880 | 525.9 | 476.7 | 502.2 | 475.9 | 467.8 | 464.5 | 470.9 | 488.6 | 424.5 | 425.5
2006 | 1881 | 525.9 | 476.7 | 502.2 | 476 | 467.8 | 464.6 | 470.9 | 488.6 | 424.5 | 425.5
2007 | 1882 | 525.9 | 476.8 | 502.2 | 476 | 467.9 | 464.6 | 470.9 | 488.5 | 424.4 | 425.6
2008 | 1883 | 525.9 | 476.8 | 502.2 | 476 | 467.9 | 464.6 | 471 | 488.5 | 424.5 | 425.6
2009 | 1884 | 525.9 | 476.8 | 502.3 | 476 | 467.9 | 464.7 | 471 | 488.7 | 424.6 | 425.6
2010 | 1885 | 525.8 | 476.9 | 502.2 | 476.1 | 468 | 464.7 | 471 | 488.8 | 424.5 | 425.6
2011 | 1886 | 525.8 | 476.9 | 502.2 | 476.1 | 468 | 464.8 | 471.1 | 489.1 | 424.5 | 425.7
2012 | 1887 | 525.8 | 476.9 | 502.3 | 476.1 | 467.9 | 464.8 | 471.1 | 489.1 | 424.6 | 425.7
2013 | 1888 | 525.8 | 476.9 | 502.3 | 476.1 | 468 | 464.8 | 471.2 | 489.1 | 424.6 | 425.7
2014 | 1889 | 525.8 | 476.9 | 502.3 | 476.2 | 468.1 | 464.9 | 471.2 | 489 | 424.6 | 425.7
2015 | 1890 | 525.8 | 476.9 | 502.3 | 476.2 | 468 | 464.9 | 471.2 | 489.1 | 424.7 | 425.7
2016 | 1891 | 525.8 | 476.9 | 502.3 | 476.2 | 468 | 464.9 | 471.3 | 488.9 | 424.7 | 425.8
2017 | 1892 | 525.8 | 477 | 502.3 | 476.3 | 468.1 | 465 | 471.3 | 488.8 | 424.7 | 425.8
2018 | 1893 | 525.8 | 477 | 502.3 | 476.3 | 468.1 | 465 | 471.4 | 488.7 | 424.8 | 425.8
2019 | 1894 | 525.8 | 477 | 502.4 | 476.3 | 468.1 | 465 | 471.4 | 488.9 | 424.8 | 425.8
2020 | 1895 | 525.8 | 477.1 | 502.3 | 476.3 | 468.2 | 465.1 | 471.5 | 489.1 | 424.9 | 425.9
2021 | 1896 | 525.8 | 477.1 | 502.3 | 476.4 | 468.2 | 465.1 | 471.5 | 489.1 | 424.9 | 425.9
2022 | 1897 | 525.8 | 477.1 | 502.4 | 476.4 | 468.1 | 465.1 | 471.5 | 489.1 | 425 | 425.9
2023 | 1898 | 525.8 | 477.1 | 502.4 | 476.4 | 468.2 | 465.2 | 471.6 | 489.1 | 425.1 | 425.9
2024 | 1899 | 525.8 | 477.1 | 502.3 | 476.4 | 468.3 | 465.2 | 471.6 | 489.2 | 425.1 | 425.9
2025 | 1900 | 525.9 | 477.2 | 502.3 | 476.5 | 468.3 | 465.3 | 471.7 | 489.3 | 425.2 | 425.9
2026 | 1901 | 525.9 | 477.1 | 502.4 | 476.5 | 468.3 | 465.3 | 471.7 | 489.3 | 425.3 | 426
2027 | 1902 | 525.9 | 477.2 | 502.4 | 476.5 | 468.3 | 465.3 | 471.7 | 489.2 | 425.4 | 426
2028 | 1903 | 526 | 477.2 | 502.4 | 476.5 | 468.4 | 465.4 | 471.8 | 489.1 | 425.5 | 426
2029 | 1904 | 526.1 | 477.2 | 502.4 | 476.5 | 468.3 | 465.4 | 471.8 | 489.1 | 425.5 | 426.1
2030 | 1905 | 526.1 | 477.2 | 502.5 | 476.6 | 468.4 | 465.4 | 471.9 | 489.2 | 425.5 | 426.2
2031 | 1906 | 526.1 | 477.3 | 502.4 | 476.6 | 468.5 | 465.5 | 471.9 | 489.2 | 425.5 | 426.2
2032 | 1907 | 526.1 | 477.3 | 502.5 | 476.6 | 468.5 | 465.5 | 472 | 489.2 | 425.5 | 426.2
2033 | 1908 | 526.1 | 477.3 | 502.5 | 476.6 | 468.4 | 465.5 | 472 | 489.1 | 425.6 | 426.3
2034 | 1909 | 526.1 | 477.3 | 502.5 | 476.7 | 468.5 | 465.6 | 472 | 489.2 | 425.6 | 426.3
2035 | 1910 | 526.1 | 477.3 | 502.5 | 476.7 | 468.5 | 465.6 | 472.1 | 489.3 | 425.7 | 426.3
2036 | 1911 | 526.1 | 477.3 | 502.6 | 476.7 | 468.5 | 465.6 | 472.1 | 489.4 | 425.7 | 426.3
2037 | 1912 | 526.1 | 477.3 | 502.6 | 476.7 | 468.5 | 465.7 | 472.2 | 489.3 | 425.7 | 426.4
2038 | 1913 | 526.1 | 477.4 | 502.6 | 476.7 | 468.6 | 465.7 | 472.2 | 489.3 | 425.7 | 426.4
2039 | 1914 | 526.1 | 477.4 | 502.6 | 476.8 | 468.6 | 465.7 | 472.3 | 489.5 | 425.8 | 426.4
2040 | 1915 | 526.1 | 477.4 | 502.6 | 476.8 | 468.5 | 465.7 | 472.3 | 489.6 | 425.8 | 426.4
2041 | 1916 | 526.1 | 477.4 | 502.6 | 476.8 | 468.6 | 465.8 | 472.3 | 489.8 | 425.9 | 426.5
2042 | 1917 | 526.1 | 477.4 | 502.6 | 476.8 | 468.6 | 465.8 | 472.4 | 489.8 | 425.9 | 426.5
2043 | 1918 | 526.1 | 477.4 | 502.7 | 476.9 | 468.6 | 465.9 | 472.4 | 489.8 | 426 | 426.5
2044 | 1919 | 526.1 | 477.4 | 502.7 | 476.9 | 468.6 | 465.9 | 472.5 | 489.9 | 426 | 426.6
2045 | 1920 | 526.1 | 477.5 | 502.6 | 476.9 | 468.7 | 465.9 | 472.5 | 490 | 426 | 426.6
2046 | 1921 | 526.1 | 477.5 | 502.7 | 476.9 | 468.7 | 466 | 472.5 | 490.2 | 426.1 | 426.6
2047 | 1922 | 526.1 | 477.5 | 502.8 | 476.9 | 468.6 | 466 | 472.6 | 490.3 | 426.2 | 426.7
2048 | 1923 | 526 | 477.5 | 502.7 | 477 | 468.8 | 466 | 472.6 | 490.1 | 426.2 | 426.7
2049 | 1924 | 526 | 477.6 | 502.7 | 477 | 468.8 | 466.1 | 472.7 | 490.1 | 426.3 | 426.7
2050 | 1925 | 526 | 477.6 | 502.7 | 477 | 468.8 | 466.1 | 472.7 | 489.9 | 426.3 | 426.7
2051 | 1926 | 526 | 477.6 | 502.7 | 477 | 468.8 | 466.1 | 472.7 | 489.7 | 426.4 | 426.7
2052 | 1927 | 526 | 477.6 | 502.7 | 477.1 | 468.9 | 466.2 | 472.8 | 489.6 | 426.4 | 426.8
2053 | 1928 | 526 | 477.7 | 502.7 | 477.1 | 468.9 | 466.2 | 472.8 | 489.5 | 426.4 | 426.8
2054 | 1929 | 526 | 477.6 | 502.8 | 477.1 | 468.9 | 466.2 | 472.9 | 489.4 | 426.5 | 426.8
2055 | 1930 | 526 | 477.7 | 502.8 | 477.1 | 469 | 466.3 | 472.9 | 489.3 | 426.5 | 426.9
2056 | 1931 | 526 | 477.7 | 502.8 | 477.2 | 469 | 466.3 | 472.9 | 489.3 | 426.5 | 426.9
2057 | 1932 | 526 | 477.7 | 502.8 | 477.2 | 469 | 466.3 | 473 | 489.8 | 426.7 | 426.9
2058 | 1933 | 526 | 477.7 | 502.8 | 477.2 | 469 | 466.4 | 473 | 490.1 | 426.7 | 426.9
2059 | 1934 | 526 | 477.8 | 502.8 | 477.2 | 469.1 | 466.4 | 473.1 | 490.3 | 426.7 | 427
2060 | 1935 | 526 | 477.8 | 502.8 | 477.3 | 469.1 | 466.4 | 473.1 | 490.2 | 426.8 | 427
2061 | 1936 | 526.1 | 477.8 | 502.9 | 477.3 | 469.1 | 466.5 | 473.1 | 490.2 | 426.8 | 427
2062 | 1937 | 526.1 | 477.8 | 502.8 | 477.3 | 469.2 | 466.5 | 473.2 | 490.3 | 426.9 | 427
2063 | 1938 | 526 | 477.8 | 502.8 | 477.3 | 469.2 | 466.6 | 473.2 | 490.3 | 426.9 | 427
2064 | 1939 | 526 | 477.8 | 502.9 | 477.3 | 469.2 | 466.6 | 473.2 | 490.3 | 427 | 427
2065 | 1940 | 526.1 | 477.9 | 502.9 | 477.4 | 469.2 | 466.6 | 473.3 | 490.4 | 427 | 427
2066 | 1941 | 526.1 | 477.9 | 502.9 | 477.4 | 469.3 | 466.7 | 473.3 | 490.5 | 427 | 427
2067 | 1942 | 526.1 | 477.9 | 502.9 | 477.4 | 469.3 | 466.7 | 473.4 | 490.5 | 427.1 | 427
2068 | 1943 | 526.1 | 477.9 | 503 | 477.4 | 469.2 | 466.7 | 473.4 | 490.6 | 427.1 | 427.1
2069 | 1944 | 526.1 | 477.9 | 503 | 477.4 | 469.3 | 466.8 | 473.4 | 490.8 | 427.2 | 427.1
2070 | 1945 | 526.1 | 477.9 | 502.9 | 477.5 | 469.4 | 466.8 | 473.5 | 491.1 | 427.2 | 427.1
2071 | 1946 | 526.1 | 478 | 503 | 477.5 | 469.4 | 466.8 | 473.5 | 491.4 | 427.3 | 427.2
2072 | 1947 | 526.1 | 478 | 503 | 477.5 | 469.4 | 466.9 | 473.6 | 491.2 | 427.4 | 427.2
2073 | 1948 | 526.1 | 478 | 503 | 477.5 | 469.5 | 466.9 | 473.6 | 491.1 | 427.4 | 427.2
2074 | 1949 | 526.1 | 478 | 503 | 477.6 | 469.6 | 467 | 473.6 | 491 | 427.5 | 427.2
2075 | 1950 | 526.2 | 478 | 503.1 | 477.6 | 469.5 | 467 | 473.7 | 491.1 | 427.5 | 427.3
2076 | 1951 | 526.2 | 478.1 | 503 | 477.6 | 469.6 | 467 | 473.7 | 491 | 427.6 | 427.3
2077 | 1952 | 526.2 | 478.1 | 503.1 | 477.6 | 469.6 | 467 | 473.7 | 491.1 | 427.7 | 427.3
2078 | 1953 | 526.2 | 478.1 | 503.1 | 477.6 | 469.6 | 467.1 | 473.8 | 491.4 | 427.7 | 427.3
2079 | 1954 | 526.2 | 478.1 | 503.1 | 477.7 | 469.6 | 467.1 | 473.8 | 491.5 | 427.8 | 427.3
2080 | 1955 | 526.2 | 478.1 | 503.1 | 477.7 | 469.7 | 467.1 | 473.8 | 491.5 | 427.8 | 427.4
2081 | 1956 | 526.1 | 478.1 | 503.1 | 477.7 | 469.7 | 467.2 | 473.9 | 491.5 | 427.9 | 427.4
2082 | 1957 | 526.1 | 478.1 | 503.2 | 477.7 | 469.7 | 467.2 | 473.9 | 491.6 | 428 | 427.4
2083 | 1958 | 526.1 | 478.2 | 503.1 | 477.7 | 469.8 | 467.3 | 473.9 | 491.7 | 428.1 | 427.5
2084 | 1959 | 526.1 | 478.2 | 503.1 | 477.8 | 469.8 | 467.3 | 474 | 491.9 | 428.1 | 427.5
2085 | 1960 | 526 | 478.2 | 503.2 | 477.8 | 469.8 | 467.3 | 474 | 492.2 | 428.2 | 427.5
2086 | 1961 | 526 | 478.2 | 503.2 | 477.8 | 469.8 | 467.3 | 474.1 | 492.3 | 428.2 | 427.5
2087 | 1962 | 526 | 478.2 | 503.2 | 477.8 | 469.9 | 467.4 | 474.1 | 492.3 | 428.2 | 427.5
2088 | 1963 | 525.9 | 478.3 | 503.2 | 477.9 | 469.9 | 467.4 | 474.1 | 492.3 | 428.3 | 427.6
2089 | 1964 | 525.9 | 478.2 | 503.2 | 477.9 | 469.9 | 467.5 | 474.2 | 492.3 | 428.4 | 427.6
2090 | 1965 | 525.9 | 478.3 | 503.2 | 477.9 | 470 | 467.5 | 474.2 | 492.4 | 428.4 | 427.6
2091 | 1966 | 525.8 | 478.3 | 503.1 | 477.9 | 470 | 467.5 | 474.2 | 492.5 | 428.5 | 427.6
2092 | 1967 | 525.8 | 478.3 | 503.2 | 477.9 | 470 | 467.6 | 474.3 | 492.5 | 428.5 | 427.7
2093 | 1968 | 525.8 | 478.3 | 503.2 | 477.9 | 470 | 467.6 | 474.3 | 492.5 | 428.6 | 427.7
2094 | 1969 | 525.8 | 478.3 | 503.2 | 478 | 470.1 | 467.6 | 474.3 | 492.5 | 428.6 | 427.7
2095 | 1970 | 525.8 | 478.4 | 503.2 | 478 | 470.1 | 467.7 | 474.3 | 492.5 | 428.7 | 427.7
2096 | 1971 | 525.8 | 478.4 | 503.2 | 478 | 470.1 | 467.7 | 474.4 | 492.6 | 428.7 | 427.7
2097 | 1972 | 525.8 | 478.4 | 503.2 | 478 | 470.2 | 467.7 | 474.4 | 492.6 | 428.7 | 427.7
2098 | 1973 | 525.8 | 478.4 | 503.2 | 478 | 470.2 | 467.8 | 474.4 | 492.7 | 428.8 | 427.8
2099 | 1974 | 525.8 | 478.4 | 503.3 | 478.1 | 470.2 | 467.8 | 474.5 | 492.7 | 428.8 | 427.8
2100 | 1975 | 525.8 | 478.4 | 503.3 | 478.1 | 470.2 | 467.8 | 474.5 | 492.7 | 428.8 | 427.8
2101 | 1976 | 525.8 | 478.5 | 503.2 | 478.1 | 470.3 | 467.9 | 474.6 | 492.6 | 428.8 | 427.8
2102 | 1977 | 525.7 | 478.5 | 503.3 | 478.1 | 470.3 | 467.9 | 474.6 | 492.7 | 428.9 | 427.9
2103 | 1978 | 525.7 | 478.5 | 503.3 | 478.1 | 470.3 | 467.9 | 474.6 | 492.8 | 428.9 | 427.9
2104 | 1979 | 525.7 | 478.5 | 503.3 | 478.2 | 470.4 | 468 | 474.7 | 492.7 | 428.9 | 427.9
2105 | 1980 | 525.7 | 478.5 | 503.3 | 478.2 | 470.4 | 468 | 474.7 | 492.7 | 428.9 | 427.9
2106 | 1981 | 525.7 | 478.5 | 503.3 | 478.2 | 470.4 | 468 | 474.7 | 492.4 | 428.9 | 428
2107 | 1982 | 525.7 | 478.5 | 503.4 | 478.2 | 470.4 | 468.1 | 474.8 | 492.3 | 429 | 428
2108 | 1983 | 525.7 | 478.6 | 503.4 | 478.2 | 470.5 | 468.1 | 474.8 | 492.4 | 429 | 428
2109 | 1984 | 525.8 | 478.6 | 503.4 | 478.3 | 470.6 | 468.2 | 474.8 | 492.4 | 429 | 428
2110 | 1985 | 525.8 | 478.6 | 503.5 | 478.3 | 470.5 | 468.2 | 474.9 | 492.5 | 429 | 428.1
2111 | 1986 | 525.8 | 478.6 | 503.4 | 478.3 | 470.6 | 468.2 | 474.9 | 492.5 | 429 | 428.1
2112 | 1987 | 525.8 | 478.6 | 503.4 | 478.3 | 470.7 | 468.2 | 474.9 | 492.6 | 429 | 428.1
2113 | 1988 | 525.9 | 478.6 | 503.5 | 478.3 | 470.7 | 468.3 | 475 | 492.6 | 429.1 | 428.2
2114 | 1989 | 525.9 | 478.6 | 503.5 | 478.3 | 470.7 | 468.3 | 475 | 492.5 | 429.1 | 428.2
2115 | 1990 | 525.9 | 478.7 | 503.5 | 478.4 | 470.8 | 468.4 | 475 | 492.3 | 429.1 | 428.2
2116 | 1991 | 525.9 | 478.7 | 503.5 | 478.4 | 470.8 | 468.4 | 475.1 | 492.2 | 429.2 | 428.2
2117 | 1992 | 525.9 | 478.7 | 503.6 | 478.4 | 470.8 | 468.4 | 475.1 | 492.4 | 429.2 | 428.3
2118 | 1993 | 525.9 | 478.7 | 503.5 | 478.4 | 470.8 | 468.5 | 475.1 | 492.4 | 429.3 | 428.3
2119 | 1994 | 525.9 | 478.7 | 503.5 | 478.5 | 470.9 | 468.5 | 475.2 | 492.5 | 429.3 | 428.3
2120 | 1995 | 525.9 | 478.7 | 503.5 | 478.5 | 470.9 | 468.5 | 475.2 | 492.5 | 429.4 | 428.4
2121 | 1996 | 525.9 | 478.7 | 503.6 | 478.5 | 470.9 | 468.6 | 475.2 | 492.4 | 429.4 | 428.4
2122 | 1997 | 525.8 | 478.8 | 503.5 | 478.5 | 471 | 468.6 | 475.3 | 492.5 | 429.4 | 428.4
2123 | 1998 | 525.8 | 478.8 | 503.5 | 478.5 | 471.1 | 468.7 | 475.3 | 492.5 | 429.5 | 428.5
2124 | 1999 | 525.8 | 478.8 | 503.6 | 478.5 | 471 | 468.7 | 475.3 | 492.5 | 429.5 | 428.5
2125 | 2000 | 525.8 | 478.8 | 503.6 | 478.6 | 471.1 | 468.7 | 475.4 | 492.5 | 429.5 | 428.5
2126 | 2001 | 525.8 | 478.8 | 503.6 | 478.6 | 471.1 | 468.8 | 475.4 | 492.4 | 429.6 | 428.6
2127 | 2002 | 525.8 | 478.8 | 503.6 | 478.6 | 471.1 | 468.8 | 475.4 | 492.4 | 429.6 | 428.6
2128 | 2003 | 525.9 | 478.8 | 503.6 | 478.6 | 471.1 | 468.8 | 475.5 | 492.6 | 429.7 | 428.6
2129 | 2004 | 525.8 | 478.9 | 503.6 | 478.6 | 471.3 | 468.9 | 475.5 | 492.8 | 429.7 | 428.6
2130 | 2005 | 525.8 | 478.9 | 503.6 | 478.7 | 471.3 | 468.9 | 475.5 | 492.9 | 429.7 | 428.7
2131 | 2006 | 525.8 | 478.9 | 503.7 | 478.6 | 471.2 | 468.9 | 475.6 | 493 | 429.7 | 428.7
2132 | 2007 | 525.9 | 478.9 | 503.6 | 478.7 | 471.3 | 469 | 475.6 | 493.1 | 429.7 | 428.7
2133 | 2008 | 525.9 | 478.9 | 503.6 | 478.7 | 471.4 | 469 | 475.6 | 493.1 | 429.7 | 428.7
2134 | 2009 | 525.9 | 478.9 | 503.7 | 478.7 | 471.3 | 469 | 475.7 | 493.1 | 429.7 | 428.8
2135 | 2010 | 525.9 | 478.9 | 503.7 | 478.7 | 471.4 | 469.1 | 475.7 | 493.4 | 429.8 | 428.8
2136 | 2011 | 525.9 | 479 | 503.7 | 478.8 | 471.5 | 469.1 | 475.7 | 493.6 | 429.7 | 428.8
2137 | 2012 | 525.9 | 479 | 503.7 | 478.8 | 471.5 | 469.2 | 475.8 | 493.5 | 429.8 | 428.8
2138 | 2013 | 525.9 | 479 | 503.8 | 478.8 | 471.4 | 469.2 | 475.8 | 493.6 | 429.8 | 428.9
2139 | 2014 | 525.9 | 479 | 503.7 | 478.8 | 471.5 | 469.2 | 475.8 | 493.6 | 429.8 | 428.9
2140 | 2015 | 525.9 | 479 | 503.7 | 478.8 | 471.6 | 469.3 | 475.9 | 493.7 | 429.9 | 428.9
2141 | 2016 | 525.9 | 479 | 503.7 | 478.8 | 471.6 | 469.3 | 475.9 | 493.8 | 429.9 | 429
2142 | 2017 | 525.9 | 479.1 | 503.8 | 478.9 | 471.6 | 469.3 | 475.9 | 493.8 | 430 | 429
2143 | 2018 | 526 | 479.1 | 503.7 | 478.9 | 471.7 | 469.4 | 475.9 | 494 | 430 | 429
2144 | 2019 | 526 | 479.1 | 503.8 | 478.9 | 471.7 | 469.4 | 476 | 494.2 | 430 | 429.1
2145 | 2020 | 526 | 479.1 | 503.9 | 478.9 | 471.7 | 469.4 | 476 | 494.4 | 430.1 | 429.1
2146 | 2021 | 526 | 479.1 | 503.9 | 478.9 | 471.8 | 469.5 | 476 | 494.2 | 430.1 | 429.1
2147 | 2022 | 526 | 479.2 | 503.9 | 479 | 471.9 | 469.5 | 476.1 | 493.9 | 430.2 | 429.2
2148 | 2023 | 526.1 | 479.1 | 503.9 | 479 | 471.9 | 469.6 | 476.1 | 493.9 | 430.2 | 429.2
2149 | 2024 | 526.1 | 479.2 | 503.9 | 479 | 471.9 | 469.6 | 476.1 | 493.7 | 430.3 | 429.3
2150 | 2025 | 526.1 | 479.2 | 503.9 | 479 | 472 | 469.6 | 476.2 | 493.6 | 430.3 | 429.3
2151 | 2026 | 526.1 | 479.2 | 503.9 | 479 | 472 | 469.7 | 476.2 | 493.6 | 430.3 | 429.3
2152 | 2027 | 526.2 | 479.2 | 503.9 | 479 | 472 | 469.7 | 476.2 | 493.5 | 430.4 | 429.4
2153 | 2028 | 526.2 | 479.2 | 503.9 | 479.1 | 472.1 | 469.8 | 476.3 | 493.6 | 430.4 | 429.4
2154 | 2029 | 526.2 | 479.3 | 503.9 | 479.1 | 472.1 | 469.8 | 476.3 | 493.8 | 430.5 | 429.4
2155 | 2030 | 526.2 | 479.3 | 503.9 | 479.1 | 472.1 | 469.8 | 476.3 | 494 | 430.5 | 429.5
2156 | 2031 | 526.3 | 479.3 | 504 | 479.1 | 472.2 | 469.9 | 476.4 | 494 | 430.6 | 429.5
2157 | 2032 | 526.3 | 479.3 | 504 | 479.2 | 472.2 | 469.9 | 476.4 | 493.9 | 430.6 | 429.5
2158 | 2033 | 526.3 | 479.3 | 504 | 479.2 | 472.3 | 469.9 | 476.4 | 494.2 | 430.6 | 429.6
2159 | 2034 | 526.3 | 479.3 | 504.1 | 479.2 | 472.2 | 470 | 476.5 | 494.2 | 430.7 | 429.6
2160 | 2035 | 526.4 | 479.3 | 504 | 479.2 | 472.3 | 470 | 476.5 | 494.3 | 430.7 | 429.6
2161 | 2036 | 526.4 | 479.4 | 504 | 479.2 | 472.4 | 470.1 | 476.5 | 494.3 | 430.8 | 429.7
2162 | 2037 | 526.4 | 479.3 | 504.1 | 479.2 | 472.4 | 470.1 | 476.6 | 494.4 | 430.8 | 429.7
2163 | 2038 | 526.4 | 479.3 | 504.1 | 479.2 | 472.4 | 470.1 | 476.6 | 494.5 | 430.8 | 429.7
2164 | 2039 | 526.4 | 479.4 | 504 | 479.3 | 472.5 | 470.2 | 476.6 | 494.4 | 430.9 | 429.7
2165 | 2040 | 526.4 | 479.4 | 504 | 479.3 | 472.5 | 470.2 | 476.7 | 494.2 | 430.9 | 429.8
2166 | 2041 | 526.4 | 479.4 | 504.1 | 479.3 | 472.5 | 470.2 | 476.7 | 494.2 | 430.9 | 429.8
2167 | 2042 | 526.4 | 479.4 | 504.1 | 479.3 | 472.6 | 470.3 | 476.7 | 494.3 | 431 | 429.8
2168 | 2043 | 526.4 | 479.4 | 504.1 | 479.3 | 472.6 | 470.3 | 476.7 | 494.4 | 431 | 429.8
2169 | 2044 | 526.4 | 479.4 | 504.1 | 479.4 | 472.6 | 470.3 | 476.8 | 494.5 | 431.1 | 429.9
2170 | 2045 | 526.4 | 479.4 | 504.2 | 479.4 | 472.6 | 470.4 | 476.8 | 494.3 | 431.1 | 429.9
2171 | 2046 | 526.4 | 479.5 | 504.1 | 479.4 | 472.7 | 470.4 | 476.8 | 494.1 | 431.1 | 429.9
2172 | 2047 | 526.4 | 479.5 | 504.1 | 479.4 | 472.8 | 470.5 | 476.9 | 494.1 | 431.2 | 430
2173 | 2048 | 526.3 | 479.5 | 504.2 | 479.4 | 472.7 | 470.5 | 476.9 | 494.2 | 431.2 | 430
2174 | 2049 | 526.3 | 479.5 | 504.2 | 479.5 | 472.9 | 470.5 | 476.9 | 494.2 | 431.2 | 430
2175 | 2050 | 526.3 | 479.6 | 504.1 | 479.5 | 472.9 | 470.6 | 477 | 494.3 | 431.2 | 430
2176 | 2051 | 526.3 | 479.5 | 504.2 | 479.5 | 472.9 | 470.6 | 477 | 494.5 | 431.2 | 430.1
2177 | 2052 | 526.3 | 479.5 | 504.2 | 479.5 | 472.9 | 470.6 | 477 | 494.7 | 431.2 | 430.1
2178 | 2053 | 526.3 | 479.6 | 504.2 | 479.5 | 473 | 470.7 | 477.1 | 494.5 | 431.2 | 430.1
2179 | 2054 | 526.2 | 479.6 | 504.2 | 479.6 | 473 | 470.7 | 477.1 | 494.4 | 431.2 | 430.1
2180 | 2055 | 526.2 | 479.6 | 504.3 | 479.6 | 473 | 470.7 | 477.1 | 494.6 | 430.8 | 430.2
2181 | 2056 | 526.2 | 479.6 | 504.2 | 479.6 | 473.1 | 470.8 | 477.2 | 494.8 | 431.2 | 430.2
2182 | 2057 | 526.1 | 479.7 | 504.2 | 479.6 | 473.2 | 470.8 | 477.2 | 494.9 | 431.2 | 430.2
2183 | 2058 | 526.1 | 479.7 | 504.3 | 479.6 | 473.2 | 470.9 | 477.2 | 494.8 | 430.4 | 430.3
2184 | 2059 | 526.1 | 479.7 | 504.3 | 479.6 | 473.2 | 470.9 | 477.3 | 494.7 | 431.2 | 430.3
2185 | 2060 | 526.1 | 479.7 | 504.2 | 479.7 | 473.3 | 470.9 | 477.3 | 494.8 | 431.2 | 430.3
2186 | 2061 | 526.1 | 479.7 | 504.3 | 479.7 | 473.3 | 471 | 477.3 | 494.9 | 431.3 | 430.3
2187 | 2062 | 526.1 | 479.7 | 504.4 | 479.7 | 473.2 | 471 | 477.4 | 494.9 | 431.3 | 430.3
2188 | 2063 | 526.1 | 479.7 | 504.3 | 479.7 | 473.3 | 471 | 477.4 | 494.9 | 431.3 | 430.4
2189 | 2064 | 526.1 | 479.7 | 504.3 | 479.7 | 473.4 | 471.1 | 477.4 | 494.9 | 431.4 | 430.4
2190 | 2065 | 526.1 | 479.7 | 504.4 | 479.7 | 473.4 | 471.1 | 477.5 | 494.9 | 431.4 | 430.4
2191 | 2066 | 526.1 | 479.7 | 504.3 | 479.7 | 473.4 | 471.2 | 477.5 | 495.2 | 431.5 | 430.4
2192 | 2067 | 526 | 479.8 | 504.3 | 479.8 | 473.5 | 471.2 | 477.5 | 495.2 | 430.1 | 430.5
2193 | 2068 | 526 | 479.8 | 504.3 | 479.8 | 473.5 | 471.2 | 477.5 | 495.2 | 429.6 | 430.6
2194 | 2069 | 526 | 479.8 | 504.4 | 479.8 | 473.5 | 471.3 | 477.6 | 495.3 | 431.3 | 430.6
2195 | 2070 | 526 | 479.8 | 504.4 | 479.8 | 473.6 | 471.3 | 477.6 | 495.4 | 430.2 | 430.6
2196 | 2071 | 526 | 479.8 | 504.4 | 479.8 | 473.6 | 471.4 | 477.6 | 495.5 | 430.5 | 430.7
2197 | 2072 | 526 | 479.8 | 504.4 | 479.8 | 473.6 | 471.4 | 477.7 | 495.4 | 431.1 | 430.7
2198 | 2073 | 526 | 479.8 | 504.4 | 479.8 | 473.6 | 471.4 | 477.7 | 495.3 | 431.5 | 430.7
2199 | 2074 | 526 | 479.9 | 504.4 | 479.9 | 473.7 | 471.5 | 477.7 | 495.5 | 431.4 | 430.7
2200 | 2075 | 526 | 479.9 | 504.4 | 479.9 | 473.8 | 471.5 | 477.8 | 495.5 | 431.1 | 430.7
2201 | 2076 | 526 | 479.8 | 504.5 | 479.9 | 473.7 | 471.5 | 477.8 | 495.4 | 431.4 | 430.7
2202 | 2077 | 526 | 479.9 | 504.5 | 479.9 | 473.8 | 471.6 | 477.8 | 495.5 | 430.9 | 430.8
2203 | 2078 | 526 | 479.9 | 504.5 | 479.9 | 473.9 | 471.6 | 477.9 | 495.6 | 430.6 | 430.8
2204 | 2079 | 526 | 479.9 | 504.5 | 479.9 | 473.9 | 471.7 | 477.9 | 495.7 | 430 | 430.9
2205 | 2080 | 526 | 479.9 | 504.5 | 479.9 | 473.9 | 471.7 | 477.9 | 495.9 | 430.5 | 430.9
2206 | 2081 | 526 | 480 | 504.5 | 480 | 474 | 471.8 | 477.9 | 496 | 430.8 | 430.9
2207 | 2082 | 526 | 480 | 504.5 | 480 | 474 | 471.8 | 478 | 496 | 430.9 | 431
2208 | 2083 | 526 | 479.9 | 504.6 | 480 | 474 | 471.8 | 478 | 496.2 | 430.1 | 431
2209 | 2084 | 526 | 480 | 504.5 | 480 | 474.1 | 471.9 | 478 | 496.3 | 431.5 | 431
2210 | 2085 | 526 | 480 | 504.5 | 480 | 474.1 | 471.9 | 478.1 | 496.3 | 431.7 | 431
2211 | 2086 | 526 | 480 | 504.6 | 480 | 474.1 | 471.9 | 478.1 | 496.3 | 431.2 | 431.1
2212 | 2087 | 526 | 480 | 504.6 | 480.1 | 474.1 | 472 | 478.1 | 496.2 | 431.2 | 431.1
2213 | 2088 | 526 | 480 | 504.5 | 480.1 | 474.2 | 472 | 478.2 | 496.3 | 431.1 | 431.1
2214 | 2089 | 525.9 | 480 | 504.6 | 480.1 | 474.3 | 472.1 | 478.2 | 496.4 | 430.8 | 431.2
2215 | 2090 | 525.9 | 480 | 504.7 | 480.1 | 474.2 | 472.1 | 478.2 | 496.5 | 430.4 | 431.2
2216 | 2091 | 525.9 | 480 | 504.6 | 480.1 | 474.3 | 472.1 | 478.3 | 496.4 | 430.8 | 431.2
2217 | 2092 | 525.9 | 480.1 | 504.6 | 480.1 | 474.3 | 472.2 | 478.3 | 496.5 | 431.3 | 431.3
2218 | 2093 | 525.9 | 480.1 | 504.6 | 480.1 | 474.3 | 472.2 | 478.3 | 496.4 | 431.4 | 431.3
2219 | 2094 | 525.9 | 480.1 | 504.7 | 480.2 | 474.4 | 472.2 | 478.4 | 496.5 | 430.7 | 431.3
2220 | 2095 | 525.9 | 480.1 | 504.6 | 480.2 | 474.5 | 472.3 | 478.4 | 496.4 | 431.5 | 431.3
2221 | 2096 | 525.9 | 480.1 | 504.6 | 480.2 | 474.5 | 472.3 | 478.4 | 496.5 | 431.4 | 431.4
2222 | 2097 | 525.9 | 480.1 | 504.7 | 480.2 | 474.4 | 472.3 | 478.4 | 496.3 | 431.6 | 431.4
2223 | 2098 | 526 | 480.1 | 504.6 | 480.2 | 474.5 | 472.4 | 478.5 | 496.2 | 432 | 431.4
2224 | 2099 | 526 | 480.2 | 504.6 | 480.3 | 474.6 | 472.5 | 478.5 | 496.2 | 431.7 | 431.4
2225 | 2100 | 526 | 480.1 | 504.7 | 480.2 | 474.6 | 472.5 | 478.5 | 496.4 | 431.8 | 431.5
2226 | 2101 | 526 | 480.2 | 504.7 | 480.3 | 474.6 | 472.5 | 478.6 | 496.6 | 431.9 | 431.5
2227 | 2102 | 526 | 480.2 | 504.7 | 480.3 | 474.7 | 472.6 | 478.6 | 496.8 | 431.7 | 431.5
2228 | 2103 | 526 | 480.2 | 504.7 | 480.3 | 474.7 | 472.6 | 478.6 | 496.8 | 431.7 | 431.5
2229 | 2104 | 526 | 480.2 | 504.8 | 480.3 | 474.7 | 472.6 | 478.7 | 496.8 | 431.8 | 431.6
2230 | 2105 | 526 | 480.2 | 504.7 | 480.3 | 474.8 | 472.7 | 478.7 | 496.9 | 431.8 | 431.6
2231 | 2106 | 526 | 480.2 | 504.7 | 480.4 | 474.8 | 472.7 | 478.7 | 496.8 | 431.8 | 431.6
2232 | 2107 | 526 | 480.2 | 504.8 | 480.3 | 474.8 | 472.7 | 478.7 | 497 | 431.9 | 431.7
2233 | 2108 | 526 | 480.2 | 504.8 | 480.4 | 474.8 | 472.8 | 478.8 | 497.1 | 431.9 | 431.7
2234 | 2109 | 526 | 480.3 | 504.8 | 480.4 | 474.9 | 472.8 | 478.8 | 497.1 | 432 | 431.7
2235 | 2110 | 526 | 480.3 | 504.8 | 480.4 | 475 | 472.9 | 478.8 | 497 | 432 | 431.7
2236 | 2111 | 526.1 | 480.3 | 504.9 | 480.4 | 474.9 | 472.9 | 478.9 | 497.1 | 432 | 431.8
2237 | 2112 | 526.1 | 480.3 | 504.8 | 480.4 | 475 | 472.9 | 478.9 | 497.3 | 432.1 | 431.8
2238 | 2113 | 526.1 | 480.3 | 504.8 | 480.5 | 475.1 | 473 | 478.9 | 497.4 | 432.1 | 431.8
2239 | 2114 | 526.1 | 480.3 | 504.9 | 480.5 | 475.1 | 473 | 478.9 | 497.4 | 432 | 431.8
2240 | 2115 | 526.1 | 480.3 | 504.9 | 480.5 | 475.1 | 473.1 | 479 | 497.4 | 432 | 431.9
2241 | 2116 | 526.1 | 480.4 | 504.8 | 480.5 | 475.2 | 473.1 | 479 | 497.4 | 432 | 431.9
2242 | 2117 | 526.1 | 480.4 | 504.9 | 480.5 | 475.2 | 473.1 | 479 | 497.4 | 432 | 431.9
2243 | 2118 | 526.1 | 480.3 | 505 | 480.5 | 475.2 | 473.2 | 479.1 | 497.4 | 432 | 431.9
2244 | 2119 | 526.1 | 480.4 | 504.9 | 480.5 | 475.3 | 473.2 | 479.1 | 497.5 | 432.2 | 431.9
2245 | 2120 | 526.1 | 480.4 | 504.9 | 480.6 | 475.3 | 473.3 | 479.1 | 497.6 | 432 | 432
2246 | 2121 | 526.1 | 480.4 | 505 | 480.5 | 475.3 | 473.3 | 479.2 | 497.5 | 432.2 | 432
2247 | 2122 | 526.1 | 480.4 | 505 | 480.6 | 475.3 | 473.3 | 479.2 | 497.3 | 432.1 | 432
2248 | 2123 | 526.1 | 480.4 | 504.9 | 480.6 | 475.4 | 473.4 | 479.2 | 497.2 | 432.1 | 432.1
2249 | 2124 | 526.2 | 480.4 | 505 | 480.6 | 475.4 | 473.4 | 479.2 | 497.2 | 432.1 | 432.1
2250 | 2125 | 526.2 | 480.4 | 505 | 480.6 | 475.4 | 473.4 | 479.3 | 497.3 | 432.2 | 432.1
2251 | 2126 | 526.1 | 480.5 | 505 | 480.6 | 475.5 | 473.5 | 479.3 | 497.4 | 432.2 | 432.2
2252 | 2127 | 526.1 | 480.5 | 505 | 480.6 | 475.5 | 473.5 | 479.3 | 497.5 | 432.3 | 432.2
2253 | 2128 | 526.1 | 480.5 | 505 | 480.6 | 475.5 | 473.5 | 479.4 | 497.6 | 432.3 | 432.2
2254 | 2129 | 526.1 | 480.5 | 505 | 480.6 | 475.5 | 473.6 | 479.4 | 497.7 | 432.3 | 432.3
2255 | 2130 | 526.1 | 480.5 | 505 | 480.7 | 475.7 | 473.6 | 479.4 | 497.6 | 432.3 | 432.3
2256 | 2131 | 526 | 480.5 | 505 | 480.7 | 475.7 | 473.7 | 479.5 | 497.6 | 432.5 | 432.3
2257 | 2132 | 526 | 480.5 | 505.1 | 480.7 | 475.6 | 473.7 | 479.5 | 497.5 | 432.6 | 432.3
2258 | 2133 | 526 | 480.5 | 505 | 480.7 | 475.7 | 473.7 | 479.5 | 497.6 | 432.5 | 432.4
2259 | 2134 | 526 | 480.6 | 505 | 480.7 | 475.8 | 473.8 | 479.6 | 497.6 | 432.6 | 432.4
2260 | 2135 | 526 | 480.6 | 505.1 | 480.7 | 475.8 | 473.8 | 479.6 | 497.6 | 432.5 | 432.4
2261 | 2136 | 526 | 480.6 | 505.1 | 480.8 | 475.8 | 473.8 | 479.6 | 497.7 | 432.7 | 432.4
2262 | 2137 | 525.9 | 480.6 | 505.1 | 480.8 | 475.9 | 473.9 | 479.6 | 497.9 | 432.7 | 432.5
2263 | 2138 | 525.9 | 480.6 | 505.1 | 480.8 | 476 | 473.9 | 479.7 | 498 | 432.7 | 432.5
2264 | 2139 | 525.9 | 480.6 | 505.2 | 480.8 | 475.9 | 473.9 | 479.7 | 498 | 432.9 | 432.5
2265 | 2140 | 525.9 | 480.6 | 505.1 | 480.8 | 476 | 474 | 479.7 | 497.9 | 432.8 | 432.6
2266 | 2141 | 525.9 | 480.6 | 505.1 | 480.8 | 476.1 | 474.1 | 479.8 | 498 | 432.8 | 432.6
2267 | 2142 | 525.8 | 480.6 | 505.1 | 480.8 | 476 | 474.1 | 479.8 | 498 | 433 | 432.6
2268 | 2143 | 525.9 | 480.6 | 505.2 | 480.8 | 476 | 474.1 | 479.8 | 498 | 432.9 | 432.7
2269 | 2144 | 525.8 | 480.7 | 505.1 | 480.9 | 476.1 | 474.2 | 479.9 | 497.9 | 433 | 432.7
2270 | 2145 | 525.8 | 480.7 | 505.1 | 480.9 | 476.2 | 474.2 | 479.9 | 497.9 | 433.3 | 432.7
2271 | 2146 | 525.9 | 480.6 | 505.2 | 480.9 | 476.1 | 474.2 | 479.9 | 497.9 | 433.2 | 432.7
2272 | 2147 | 525.9 | 480.7 | 505.2 | 480.9 | 476.2 | 474.3 | 480 | 498 | 433 | 432.8
2273 | 2148 | 525.9 | 480.7 | 505.2 | 480.9 | 476.3 | 474.3 | 480 | 498 | 433 | 432.8
2274 | 2149 | 525.9 | 480.7 | 505.2 | 480.9 | 476.3 | 474.3 | 480 | 498 | 433.1 | 432.8
2275 | 2150 | 525.9 | 480.7 | 505.3 | 480.9 | 476.3 | 474.4 | 480 | 498.2 | 433.1 | 432.9
2276 | 2151 | 525.9 | 480.7 | 505.2 | 480.9 | 476.4 | 474.4 | 480.1 | 498.4 | 433.1 | 432.9
2277 | 2152 | 525.9 | 480.7 | 505.2 | 481 | 476.4 | 474.5 | 480.1 | 498.6 | 433.2 | 432.9
2278 | 2153 | 526 | 480.7 | 505.3 | 480.9 | 476.4 | 474.5 | 480.1 | 498.7 | 433.3 | 432.9
2279 | 2154 | 526 | 480.8 | 505.2 | 481 | 476.5 | 474.5 | 480.2 | 498.6 | 433.3 | 432.9
2280 | 2155 | 526 | 480.8 | 505.2 | 481 | 476.5 | 474.6 | 480.2 | 498.4 | 433.3 | 432.9
2281 | 2156 | 526 | 480.8 | 505.3 | 481 | 476.5 | 474.6 | 480.2 | 498.2 | 433.4 | 433
2282 | 2157 | 526 | 480.8 | 505.4 | 481 | 476.5 | 474.6 | 480.2 | 498.2 | 433.7 | 433
2283 | 2158 | 525.9 | 480.8 | 505.3 | 481 | 476.6 | 474.7 | 480.3 | 498.4 | 433.4 | 433
2284 | 2159 | 525.9 | 480.8 | 505.3 | 481 | 476.6 | 474.7 | 480.3 | 498.5 | 433.4 | 433
2285 | 2160 | 525.9 | 480.8 | 505.4 | 481 | 476.6 | 474.7 | 480.3 | 498.8 | 433.4 | 433.1
2286 | 2161 | 525.9 | 480.8 | 505.3 | 481.1 | 476.7 | 474.8 | 480.4 | 498.9 | 433.4 | 433.1
2287 | 2162 | 525.9 | 480.9 | 505.3 | 481.1 | 476.8 | 474.8 | 480.4 | 498.9 | 433.4 | 433.1
2288 | 2163 | 525.9 | 480.8 | 505.4 | 481.1 | 476.7 | 474.9 | 480.4 | 499 | 433.6 | 433.1
2289 | 2164 | 525.9 | 480.9 | 505.4 | 481.1 | 476.7 | 474.9 | 480.5 | 498.9 | 433.5 | 433.2
2290 | 2165 | 525.8 | 480.9 | 505.3 | 481.1 | 476.9 | 475 | 480.5 | 498.7 | 433.5 | 433.2
2291 | 2166 | 525.8 | 480.9 | 505.4 | 481.1 | 476.9 | 475 | 480.5 | 498.7 | 433.5 | 433.2
2292 | 2167 | 525.8 | 480.9 | 505.4 | 481.1 | 476.9 | 475 | 480.5 | 498.5 | 433.5 | 433.2
2293 | 2168 | 525.8 | 480.9 | 505.4 | 481.2 | 476.9 | 475.1 | 480.6 | 498.5 | 433.6 | 433.2
2294 | 2169 | 525.7 | 480.9 | 505.4 | 481.2 | 477 | 475.1 | 480.6 | 498.8 | 433.6 | 433.2
2295 | 2170 | 525.7 | 480.9 | 505.4 | 481.2 | 477 | 475.1 | 480.6 | 498.7 | 433.6 | 433.3
2296 | 2171 | 525.7 | 480.9 | 505.4 | 481.2 | 477 | 475.2 | 480.7 | 498.8 | 433.7 | 433.3
2297 | 2172 | 525.7 | 481 | 505.4 | 481.2 | 477.1 | 475.2 | 480.7 | 498.9 | 433.7 | 433.3
2298 | 2173 | 525.7 | 481 | 505.4 | 481.2 | 477.2 | 475.3 | 480.7 | 499 | 433.7 | 433.4
2299 | 2174 | 525.7 | 481 | 505.5 | 481.2 | 477.1 | 475.3 | 480.8 | 499.1 | 433.7 | 433.4
2300 | 2175 | 525.7 | 481 | 505.4 | 481.2 | 477.2 | 475.3 | 480.8 | 499.1 | 433.7 | 433.4
2301 | 2176 | 525.8 | 481 | 505.4 | 481.3 | 477.2 | 475.4 | 480.8 | 499.2 | 433.9 | 433.4
2302 | 2177 | 525.8 | 481 | 505.5 | 481.3 | 477.2 | 475.4 | 480.8 | 499.1 | 433.9 | 433.5
2303 | 2178 | 525.8 | 481 | 505.5 | 481.3 | 477.3 | 475.4 | 480.9 | 499.2 | 433.9 | 433.5
2304 | 2179 | 525.8 | 481.1 | 505.5 | 481.3 | 477.4 | 475.5 | 480.9 | 499.2 | 433.9 | 433.5
2305 | 2180 | 525.8 | 481.1 | 505.5 | 481.3 | 477.4 | 475.5 | 480.9 | 499 | 434 | 433.5
2306 | 2181 | 525.8 | 481 | 505.6 | 481.3 | 477.4 | 475.5 | 481 | 499 | 434 | 433.6
2307 | 2182 | 525.8 | 481.1 | 505.5 | 481.3 | 477.5 | 475.6 | 481 | 499.1 | 434.1 | 433.6
2308 | 2183 | 525.8 | 481.1 | 505.5 | 481.3 | 477.5 | 475.6 | 481 | 499.1 | 434.1 | 433.6
2309 | 2184 | 525.8 | 481.1 | 505.6 | 481.3 | 477.5 | 475.7 | 481.1 | 499.2 | 434.1 | 433.6
2310 | 2185 | 525.9 | 481.1 | 505.6 | 481.4 | 477.5 | 475.7 | 481.1 | 499.3 | 434.2 | 433.7
2311 | 2186 | 525.9 | 481.1 | 505.6 | 481.4 | 477.6 | 475.7 | 481.1 | 499.4 | 434.3 | 433.7
2312 | 2187 | 525.9 | 481.2 | 505.6 | 481.4 | 477.7 | 475.8 | 481.1 | 499.6 | 434.3 | 433.7
2313 | 2188 | 526 | 481.1 | 505.6 | 481.4 | 477.6 | 475.8 | 481.2 | 499.7 | 434.4 | 433.7
2314 | 2189 | 526 | 481.1 | 505.6 | 481.4 | 477.7 | 475.8 | 481.2 | 499.6 | 434.5 | 433.8
2315 | 2190 | 526 | 481.2 | 505.6 | 481.4 | 477.7 | 475.9 | 481.2 | 499.7 | 434.5 | 433.8
2316 | 2191 | 526 | 481.1 | 505.7 | 481.4 | 477.7 | 475.9 | 481.3 | 499.6 | 434.5 | 433.8
2317 | 2192 | 526 | 481.2 | 505.7 | 481.4 | 477.8 | 476 | 481.3 | 499.8 | 434.6 | 433.8
2318 | 2193 | 526 | 481.2 | 505.7 | 481.5 | 477.8 | 476 | 481.3 | 499.9 | 434.5 | 433.8
2319 | 2194 | 526 | 481.2 | 505.7 | 481.5 | 477.9 | 476.1 | 481.4 | 499.9 | 434.5 | 433.9
2320 | 2195 | 526.1 | 481.2 | 505.8 | 481.5 | 477.8 | 476.1 | 481.4 | 499.9 | 434.6 | 433.9
2321 | 2196 | 526.1 | 481.2 | 505.7 | 481.5 | 477.9 | 476.1 | 481.4 | 500 | 434.7 | 433.9
2322 | 2197 | 526 | 481.2 | 505.7 | 481.5 | 478 | 476.2 | 481.4 | 499.9 | 434.6 | 433.9
2323 | 2198 | 526 | 481.2 | 505.7 | 481.5 | 478 | 476.2 | 481.5 | 500.1 | 434.7 | 434
2324 | 2199 | 526 | 481.2 | 505.8 | 481.5 | 478 | 476.2 | 481.5 | 500 | 434.8 | 434
2325 | 2200 | 526 | 481.3 | 505.7 | 481.5 | 478.1 | 476.3 | 481.5 | 500 | 434.8 | 434
2326 | 2201 | 526 | 481.3 | 505.8 | 481.6 | 478.1 | 476.3 | 481.6 | 500 | 434.9 | 434
2327 | 2202 | 526 | 481.3 | 505.8 | 481.5 | 478.1 | 476.4 | 481.6 | 500.1 | 434.9 | 434.1
2328 | 2203 | 526 | 481.3 | 505.8 | 481.6 | 478.2 | 476.4 | 481.6 | 500.2 | 434.9 | 434.1
2329 | 2204 | 526 | 481.3 | 505.8 | 481.6 | 478.2 | 476.5 | 481.7 | 500.4 | 434.9 | 434.1
2330 | 2205 | 525.9 | 481.3 | 505.8 | 481.6 | 478.2 | 476.5 | 481.7 | 500.4 | 435.1 | 434.1
2331 | 2206 | 525.9 | 481.3 | 505.8 | 481.6 | 478.2 | 476.5 | 481.7 | 500.2 | 435 | 434.1
2332 | 2207 | 526 | 481.4 | 505.8 | 481.6 | 478.4 | 476.6 | 481.8 | 500.1 | 435 | 434.2
2333 | 2208 | 526 | 481.4 | 505.8 | 481.6 | 478.4 | 476.6 | 481.8 | 500 | 435.1 | 434.2
2334 | 2209 | 526 | 481.3 | 505.9 | 481.6 | 478.3 | 476.6 | 481.8 | 500.2 | 435.1 | 434.2
2335 | 2210 | 526 | 481.4 | 505.9 | 481.7 | 478.4 | 476.7 | 481.8 | 500.3 | 435.2 | 434.2
2336 | 2211 | 526 | 481.4 | 505.8 | 481.7 | 478.5 | 476.7 | 481.9 | 500.3 | 435.2 | 434.2
2337 | 2212 | 525.9 | 481.4 | 505.9 | 481.7 | 478.5 | 476.7 | 481.9 | 500.4 | 435.2 | 434.3
2338 | 2213 | 525.9 | 481.4 | 505.9 | 481.7 | 478.5 | 476.8 | 481.9 | 500.6 | 435.8 | 434.3
2339 | 2214 | 525.9 | 481.4 | 505.9 | 481.7 | 478.6 | 476.8 | 482 | 500.6 | 435.6 | 434.3
2340 | 2215 | 525.8 | 481.4 | 505.9 | 481.7 | 478.6 | 476.9 | 482 | 500.5 | 435.5 | 434.3
2341 | 2216 | 525.8 | 481.4 | 505.9 | 481.7 | 478.6 | 476.9 | 482 | 500.7 | 435.4 | 434.3
2342 | 2217 | 525.9 | 481.4 | 505.9 | 481.7 | 478.7 | 476.9 | 482 | 500.8 | 435.4 | 434.3
2343 | 2218 | 525.9 | 481.5 | 505.9 | 481.8 | 478.7 | 477 | 482.1 | 500.9 | 435.3 | 434.4
2344 | 2219 | 525.8 | 481.5 | 505.9 | 481.8 | 478.7 | 477 | 482.1 | 501 | 435.5 | 434.4
2345 | 2220 | 525.8 | 481.5 | 506 | 481.8 | 478.8 | 477 | 482.1 | 501.1 | 435.5 | 434.4
2346 | 2221 | 525.8 | 481.5 | 505.9 | 481.8 | 478.9 | 477.1 | 482.2 | 501.3 | 435.6 | 434.4
2347 | 2222 | 525.8 | 481.5 | 505.9 | 481.8 | 478.9 | 477.1 | 482.2 | 501.3 | 435.7 | 434.4
2348 | 2223 | 525.8 | 481.5 | 506 | 481.8 | 478.8 | 477.1 | 482.2 | 501.3 | 435.7 | 434.5
2349 | 2224 | 525.8 | 481.5 | 506 | 481.8 | 478.9 | 477.2 | 482.3 | 501 | 435.7 | 434.5
2350 | 2225 | 525.8 | 481.5 | 506 | 481.8 | 479 | 477.2 | 482.3 | 500.7 | 435.7 | 434.5
2351 | 2226 | 525.8 | 481.5 | 506 | 481.8 | 479 | 477.3 | 482.3 | 500.7 | 435.8 | 434.5
2352 | 2227 | 525.9 | 481.5 | 506.1 | 481.8 | 479 | 477.3 | 482.4 | 500.7 | 435.8 | 434.6
2353 | 2228 | 525.9 | 481.5 | 506 | 481.9 | 479.1 | 477.4 | 482.4 | 500.8 | 435.8 | 434.6
2354 | 2229 | 525.9 | 481.6 | 506 | 481.9 | 479.1 | 477.4 | 482.4 | 500.9 | 435.8 | 434.6
2355 | 2230 | 525.9 | 481.5 | 506.1 | 481.9 | 479.1 | 477.4 | 482.4 | 501.1 | 435.9 | 434.6
2356 | 2231 | 525.8 | 481.6 | 506.1 | 481.9 | 479.2 | 477.5 | 482.5 | 501 | 435.9 | 434.6
2357 | 2232 | 525.8 | 481.6 | 506.1 | 481.9 | 479.2 | 477.5 | 482.5 | 501.2 | 435.9 | 434.7
2358 | 2233 | 525.8 | 481.6 | 506.1 | 481.9 | 479.2 | 477.5 | 482.5 | 501.5 | 435.9 | 434.7
2359 | 2234 | 525.8 | 481.6 | 506.1 | 481.9 | 479.2 | 477.6 | 482.6 | 501.5 | 436 | 434.7
2360 | 2235 | 525.8 | 481.6 | 506.1 | 481.9 | 479.3 | 477.6 | 482.6 | 501.5 | 436.1 | 434.7
2361 | 2236 | 525.8 | 481.6 | 506.1 | 482 | 479.4 | 477.7 | 482.6 | 501.5 | 436 | 434.7
2362 | 2237 | 525.8 | 481.6 | 506.2 | 481.9 | 479.3 | 477.7 | 482.6 | 501.6 | 436.1 | 434.8
2363 | 2238 | 525.8 | 481.6 | 506.1 | 482 | 479.4 | 477.7 | 482.7 | 502 | 436.2 | 434.8
2364 | 2239 | 525.7 | 481.7 | 506.1 | 482 | 479.5 | 477.8 | 482.7 | 502.3 | 436.2 | 434.8
2365 | 2240 | 525.7 | 481.7 | 506.2 | 482 | 479.5 | 477.8 | 482.7 | 502.2 | 436.3 | 434.8
2366 | 2241 | 525.7 | 481.6 | 506.2 | 482 | 479.5 | 477.8 | 482.8 | 502.2 | 436.6 | 434.8
2367 | 2242 | 525.7 | 481.7 | 506.1 | 482 | 479.6 | 477.9 | 482.8 | 502.3 | 436.4 | 434.8
2368 | 2243 | 525.7 | 481.7 | 506.1 | 482 | 479.6 | 477.9 | 482.8 | 502.4 | 436.5 | 434.9
2369 | 2244 | 525.7 | 481.7 | 506.2 | 482 | 479.6 | 477.9 | 482.8 | 502.6 | 436.9 | 434.9
2370 | 2245 | 525.7 | 481.7 | 506.1 | 482.1 | 479.7 | 478 | 482.9 | 502.7 | 436.5 | 434.9
2371 | 2246 | 525.7 | 481.7 | 506.2 | 482.1 | 479.7 | 478 | 482.9 | 502.8 | 436.4 | 434.9
2372 | 2247 | 525.7 | 481.7 | 506.2 | 482.1 | 479.7 | 478.1 | 482.9 | 502.6 | 436.6 | 435
2373 | 2248 | 525.8 | 481.7 | 506.2 | 482.1 | 479.7 | 478.1 | 482.9 | 502.5 | 436.5 | 435
2374 | 2249 | 525.8 | 481.8 | 506.2 | 482.1 | 479.8 | 478.2 | 483 | 502.5 | 436.7 | 435
2375 | 2250 | 525.8 | 481.8 | 506.2 | 482.1 | 479.8 | 478.2 | 483 | 502.5 | 436.5 | 435
2376 | 2251 | 525.8 | 481.7 | 506.3 | 482.1 | 479.8 | 478.2 | 483 | 502.5 | 436.5 | 435.1
2377 | 2252 | 525.9 | 481.8 | 506.3 | 482.1 | 479.9 | 478.3 | 483.1 | 502.4 | 436.6 | 435.1
2378 | 2253 | 525.9 | 481.8 | 506.3 | 482.2 | 479.9 | 478.3 | 483.1 | 502.5 | 436.7 | 435.1
2379 | 2254 | 525.9 | 481.8 | 506.3 | 482.2 | 479.9 | 478.3 | 483.1 | 502.7 | 436.6 | 435.1
2380 | 2255 | 525.9 | 481.8 | 506.3 | 482.2 | 479.9 | 478.4 | 483.2 | 502.9 | 436.6 | 435.1
2381 | 2256 | 525.9 | 481.8 | 506.3 | 482.2 | 480.1 | 478.4 | 483.2 | 503 | 436.6 | 435.1
2382 | 2257 | 525.9 | 481.8 | 506.3 | 482.2 | 480.1 | 478.4 | 483.2 | 503.1 | 436.5 | 435.1
2383 | 2258 | 525.9 | 481.8 | 506.4 | 482.2 | 480 | 478.4 | 483.2 | 503.3 | 436.6 | 435.1
2384 | 2259 | 526 | 481.9 | 506.3 | 482.2 | 480.2 | 478.5 | 483.3 | 503 | 436.6 | 435.2
2385 | 2260 | 526 | 481.9 | 506.3 | 482.2 | 480.2 | 478.5 | 483.3 | 502.9 | 436.7 | 435.2
2386 | 2261 | 526 | 481.9 | 506.4 | 482.2 | 480.2 | 478.6 | 483.3 | 502.7 | 436.9 | 435.2
2387 | 2262 | 526 | 481.9 | 506.4 | 482.2 | 480.2 | 478.6 | 483.4 | 502.7 | 436.4 | 435.2
2388 | 2263 | 526 | 481.9 | 506.4 | 482.3 | 480.3 | 478.6 | 483.4 | 502.8 | 436.8 | 435.3
2389 | 2264 | 526 | 481.9 | 506.4 | 482.3 | 480.4 | 478.7 | 483.4 | 502.8 | 437.1 | 435.3
2390 | 2265 | 526 | 481.9 | 506.5 | 482.3 | 480.3 | 478.7 | 483.5 | 502.5 | 436.4 | 435.3
2391 | 2266 | 526 | 481.9 | 506.5 | 482.3 | 480.4 | 478.8 | 483.5 | 502.4 | 437.1 | 435.3
2392 | 2267 | 526 | 481.9 | 506.5 | 482.3 | 480.5 | 478.8 | 483.5 | 502.5 | 437 | 435.3
2393 | 2268 | 526 | 481.9 | 506.5 | 482.3 | 480.5 | 478.8 | 483.5 | 502.5 | 436.6 | 435.4
2394 | 2269 | 526 | 482 | 506.5 | 482.3 | 480.5 | 478.9 | 483.6 | 502.6 | 437.2 | 435.4
2395 | 2270 | 526 | 482 | 506.5 | 482.4 | 480.6 | 478.9 | 483.6 | 502.5 | 437.2 | 435.4
2396 | 2271 | 526 | 482 | 506.5 | 482.4 | 480.6 | 479 | 483.6 | 502.6 | 437.2 | 435.4
2397 | 2272 | 526 | 482 | 506.5 | 482.4 | 480.5 | 479 | 483.7 | 502.8 | 437.3 | 435.5
2398 | 2273 | 525.9 | 482 | 506.5 | 482.4 | 480.6 | 479 | 483.7 | 502.9 | 437.3 | 435.5
2399 | 2274 | 525.9 | 482 | 506.5 | 482.4 | 480.7 | 479.1 | 483.7 | 503 | 437.3 | 435.6
2400 | 2275 | 525.9 | 482 | 506.6 | 482.4 | 480.7 | 479.1 | 483.8 | 502.9 | 437.4 | 435.6
2401 | 2276 | 525.9 | 482 | 506.6 | 482.4 | 480.7 | 479.1 | 483.8 | 502.8 | 437.4 | 435.6
2402 | 2277 | 525.9 | 482 | 506.5 | 482.4 | 480.8 | 479.2 | 483.8 | 502.8 | 437.3 | 435.7
2403 | 2278 | 525.9 | 482 | 506.6 | 482.4 | 480.8 | 479.2 | 483.8 | 502.7 | 437.3 | 435.7
2404 | 2279 | 525.9 | 482 | 506.6 | 482.4 | 480.8 | 479.2 | 483.9 | 502.7 | 437.5 | 435.7
2405 | 2280 | 525.9 | 482 | 506.6 | 482.4 | 480.9 | 479.3 | 483.9 | 502.8 | 437.3 | 435.7
2406 | 2281 | 525.9 | 482.1 | 506.5 | 482.5 | 481 | 479.3 | 483.9 | 502.9 | 437.5 | 435.7
2407 | 2282 | 525.9 | 482.1 | 506.6 | 482.4 | 480.9 | 479.4 | 484 | 502.9 | 437.6 | 435.7
2408 | 2283 | 525.8 | 482.1 | 506.6 | 482.4 | 480.9 | 479.4 | 484 | 502.9 | 437.6 | 435.7
2409 | 2284 | 525.8 | 482.1 | 506.6 | 482.5 | 481.1 | 479.5 | 484 | 503 | 437.6 | 435.8
2410 | 2285 | 525.8 | 482.1 | 506.6 | 482.5 | 481.1 | 479.5 | 484.1 | 503.3 | 437.7 | 435.8
2411 | 2286 | 525.8 | 482.1 | 506.7 | 482.5 | 481 | 479.5 | 484.1 | 503.3 | 437.7 | 435.8
2412 | 2287 | 525.8 | 482.1 | 506.6 | 482.5 | 481.1 | 479.6 | 484.1 | 503.5 | 437.7 | 435.8
2413 | 2288 | 525.8 | 482.1 | 506.6 | 482.5 | 481.2 | 479.6 | 484.1 | 503.6 | 437.7 | 435.8
2414 | 2289 | 525.8 | 482.1 | 506.6 | 482.5 | 481.2 | 479.6 | 484.2 | 503.6 | 437.3 | 435.9
2415 | 2290 | 525.7 | 482.1 | 506.7 | 482.5 | 481.2 | 479.7 | 484.2 | 503.5 | 437.8 | 435.8
2416 | 2291 | 525.7 | 482.2 | 506.7 | 482.6 | 481.3 | 479.7 | 484.2 | 503.5 | 437.8 | 435.9
2417 | 2292 | 525.7 | 482.2 | 506.6 | 482.6 | 481.4 | 479.8 | 484.3 | 503.7 | 437.8 | 435.9
2418 | 2293 | 525.7 | 482.2 | 506.7 | 482.6 | 481.3 | 479.8 | 484.3 | 503.7 | 437.9 | 435.9
2419 | 2294 | 525.7 | 482.2 | 506.7 | 482.6 | 481.4 | 479.8 | 484.3 | 503.7 | 438.5 | 435.9
2420 | 2295 | 525.6 | 482.2 | 506.7 | 482.6 | 481.5 | 479.9 | 484.3 | 503.6 | 438.5 | 435.9
2421 | 2296 | 525.6 | 482.2 | 506.7 | 482.6 | 481.5 | 479.9 | 484.4 | 503.9 | 438.4 | 435.9
2422 | 2297 | 525.6 | 482.2 | 506.8 | 482.6 | 481.5 | 479.9 | 484.4 | 504.1 | 438.7 | 435.9
2423 | 2298 | 525.6 | 482.2 | 506.7 | 482.6 | 481.6 | 480 | 484.4 | 504.2 | 438.4 | 435.9
2424 | 2299 | 525.6 | 482.2 | 506.7 | 482.6 | 481.6 | 480 | 484.5 | 504.3 | 438.1 | 436
2425 | 2300 | 525.6 | 482.2 | 506.8 | 482.6 | 481.6 | 480 | 484.5 | 504.4 | 438.1 | 436
2426 | 2301 | 525.6 | 482.2 | 506.7 | 482.6 | 481.7 | 480.1 | 484.5 | 504.5 | 437.9 | 436.1
2427 | 2302 | 525.5 | 482.2 | 506.8 | 482.7 | 481.7 | 480.1 | 484.6 | 504.4 | 438.2 | 436.1
2428 | 2303 | 525.5 | 482.2 | 506.8 | 482.7 | 481.7 | 480.2 | 484.6 | 504.3 | 438.6 | 436.1
2429 | 2304 | 525.5 | 482.2 | 506.8 | 482.7 | 481.7 | 480.2 | 484.6 | 503.9 | 437.7 | 436.2
2430 | 2305 | 525.5 | 482.3 | 506.8 | 482.7 | 481.8 | 480.2 | 484.6 | 503.9 | 438.3 | 436.2
2431 | 2306 | 525.5 | 482.3 | 506.8 | 482.7 | 481.9 | 480.3 | 484.7 | 504 | 438.4 | 436.2
2432 | 2307 | 525.5 | 482.3 | 506.8 | 482.7 | 481.8 | 480.3 | 484.7 | 504 | 437.9 | 436.2
2433 | 2308 | 525.6 | 482.3 | 506.8 | 482.7 | 481.9 | 480.4 | 484.7 | 503.8 | 438.4 | 436.2
2434 | 2309 | 525.6 | 482.3 | 506.8 | 482.7 | 482 | 480.4 | 484.8 | 503.7 | 438.4 | 436.2
2435 | 2310 | 525.6 | 482.3 | 506.9 | 482.7 | 482 | 480.4 | 484.8 | 503.8 | 438.4 | 436.3
2436 | 2311 | 525.6 | 482.3 | 506.9 | 482.7 | 482 | 480.5 | 484.8 | 504.1 | 438.5 | 436.3
2437 | 2312 | 525.6 | 482.3 | 506.9 | 482.8 | 482.1 | 480.5 | 484.9 | 504.3 | 438.5 | 436.3
2438 | 2313 | 525.6 | 482.3 | 506.8 | 482.8 | 482.1 | 480.6 | 484.9 | 504.5 | 438.5 | 436.3
2439 | 2314 | 525.6 | 482.3 | 506.9 | 482.8 | 482.1 | 480.6 | 484.9 | 504.3 | 438.6 | 436.3
2440 | 2315 | 525.6 | 482.3 | 506.9 | 482.8 | 482.2 | 480.6 | 485 | 504.1 | 438.6 | 436.4
2441 | 2316 | 525.6 | 482.3 | 506.9 | 482.8 | 482.2 | 480.7 | 485 | 504.2 | 438.6 | 436.4
2442 | 2317 | 525.6 | 482.3 | 507 | 482.8 | 482.2 | 480.7 | 485 | 504.2 | 438.7 | 436.4
2443 | 2318 | 525.6 | 482.3 | 506.9 | 482.8 | 482.2 | 480.7 | 485 | 504.5 | 438.7 | 436.4
2444 | 2319 | 525.6 | 482.4 | 506.9 | 482.8 | 482.3 | 480.8 | 485.1 | 504.5 | 438.4 | 436.4
2445 | 2320 | 525.6 | 482.4 | 506.9 | 482.8 | 482.4 | 480.8 | 485.1 | 504.4 | 438.4 | 436.4
2446 | 2321 | 525.6 | 482.4 | 507 | 482.8 | 482.3 | 480.8 | 485.1 | 504.5 | 438.6 | 436.4
2447 | 2322 | 525.6 | 482.4 | 506.9 | 482.9 | 482.4 | 480.9 | 485.1 | 504.7 | 438.4 | 436.4
2448 | 2323 | 525.6 | 482.4 | 506.9 | 482.9 | 482.5 | 480.9 | 485.2 | 504.7 | 438.6 | 436.4
2449 | 2324 | 525.5 | 482.4 | 507 | 482.9 | 482.5 | 481 | 485.2 | 504.7 | 438.8 | 436.4
2450 | 2325 | 525.5 | 482.4 | 507 | 482.8 | 482.5 | 481 | 485.2 | 504.8 | 439 | 436.4
2451 | 2326 | 525.5 | 482.4 | 507 | 482.9 | 482.6 | 481.1 | 485.2 | 505 | 439.3 | 436.4
2452 | 2327 | 525.5 | 482.4 | 507 | 482.9 | 482.6 | 481.1 | 485.3 | 505 | 439.2 | 436.4
2453 | 2328 | 525.5 | 482.4 | 507 | 482.9 | 482.6 | 481.1 | 485.3 | 505.2 | 439.3 | 436.4
2454 | 2329 | 525.4 | 482.5 | 507 | 482.9 | 482.7 | 481.2 | 485.3 | 505.3 | 439.4 | 436.4
2455 | 2330 | 525.4 | 482.5 | 507 | 482.9 | 482.7 | 481.2 | 485.3 | 505.2 | 439.2 | 436.4
2456 | 2331 | 525.4 | 482.5 | 507 | 482.9 | 482.7 | 481.2 | 485.4 | 505.1 | 438.4 | 436.4
2457 | 2332 | 525.4 | 482.5 | 507 | 482.9 | 482.8 | 481.3 | 485.4 | 505.1 | 439 | 436.4
2458 | 2333 | 525.4 | 482.5 | 507 | 483 | 482.9 | 481.3 | 485.4 | 505.2 | 439 | 436.4
2459 | 2334 | 525.4 | 482.5 | 507 | 483 | 482.9 | 481.4 | 485.5 | 505.4 | 439.1 | 436.4
2460 | 2335 | 525.4 | 482.5 | 507.1 | 482.9 | 482.8 | 481.4 | 485.5 | 505.4 | 439.1 | 436.5
2461 | 2336 | 525.4 | 482.5 | 507.1 | 483 | 482.9 | 481.4 | 485.5 | 505.3 | 439.2 | 436.5
2462 | 2337 | 525.4 | 482.6 | 507.1 | 483 | 483 | 481.5 | 485.5 | 505.5 | 439.3 | 436.5
2463 | 2338 | 525.4 | 482.6 | 507.1 | 483 | 483 | 481.5 | 485.6 | 505.4 | 439.2 | 436.5
2464 | 2339 | 525.4 | 482.5 | 507.1 | 483 | 483 | 481.5 | 485.6 | 505.3 | 439.5 | 436.5
2465 | 2340 | 525.4 | 482.6 | 507.1 | 483 | 483.1 | 481.6 | 485.6 | 505.2 | 439 | 436.6
2466 | 2341 | 525.5 | 482.6 | 507.1 | 483 | 483.1 | 481.6 | 485.7 | 505.2 | 438.9 | 436.6
2467 | 2342 | 525.5 | 482.6 | 507.2 | 483 | 483.1 | 481.6 | 485.7 | 505.3 | 438.8 | 436.7
2468 | 2343 | 525.5 | 482.6 | 507.1 | 483 | 483.1 | 481.7 | 485.7 | 505.4 | 439 | 436.7
2469 | 2344 | 525.5 | 482.6 | 507.1 | 483 | 483.2 | 481.7 | 485.7 | 505.3 | 439.2 | 436.7
2470 | 2345 | 525.6 | 482.6 | 507.2 | 483 | 483.2 | 481.8 | 485.8 | 505.3 | 439.6 | 436.7
2471 | 2346 | 525.6 | 482.6 | 507.2 | 483 | 483.2 | 481.8 | 485.8 | 505.2 | 439.2 | 436.8
2472 | 2347 | 525.6 | 482.7 | 507.2 | 483.1 | 483.3 | 481.8 | 485.8 | 505.3 | 439.5 | 436.8
2473 | 2348 | 525.6 | 482.7 | 507.2 | 483.1 | 483.4 | 481.9 | 485.9 | 505.6 | 439.7 | 436.8
2474 | 2349 | 525.7 | 482.6 | 507.2 | 483.1 | 483.3 | 481.9 | 485.9 | 505.6 | 439.1 | 436.9
2475 | 2350 | 525.7 | 482.7 | 507.2 | 483.1 | 483.4 | 482 | 485.9 | 505.9 | 439.7 | 436.9
2476 | 2351 | 525.7 | 482.7 | 507.2 | 483.1 | 483.4 | 482 | 485.9 | 506.2 | 439.7 | 436.9
2477 | 2352 | 525.7 | 482.7 | 507.2 | 483.1 | 483.4 | 482 | 486 | 506.2 | 439.4 | 437
2478 | 2353 | 525.7 | 482.7 | 507.2 | 483.1 | 483.5 | 482.1 | 486 | 506.3 | 439.8 | 437
2479 | 2354 | 525.7 | 482.7 | 507.2 | 483.1 | 483.6 | 482.1 | 486 | 506.4 | 440.1 | 437
2480 | 2355 | 525.7 | 482.7 | 507.2 | 483.1 | 483.6 | 482.1 | 486.1 | 506.4 | 440.3 | 437
2481 | 2356 | 525.7 | 482.7 | 507.3 | 483.1 | 483.5 | 482.2 | 486.1 | 506.3 | 440.4 | 437
2482 | 2357 | 525.7 | 482.7 | 507.3 | 483.1 | 483.6 | 482.2 | 486.1 | 506.2 | 440.4 | 437.1
2483 | 2358 | 525.7 | 482.8 | 507.3 | 483.2 | 483.7 | 482.3 | 486.1 | 506.3 | 440.4 | 437.1
2484 | 2359 | 525.7 | 482.7 | 507.3 | 483.2 | 483.7 | 482.3 | 486.2 | 506.4 | 440.5 | 437.1
2485 | 2360 | 525.7 | 482.8 | 507.3 | 483.2 | 483.7 | 482.3 | 486.2 | 506.4 | 440.5 | 437.1
2486 | 2361 | 525.6 | 482.8 | 507.3 | 483.2 | 483.8 | 482.4 | 486.2 | 506.4 | 440.2 | 437.2
2487 | 2362 | 525.6 | 482.8 | 507.3 | 483.2 | 483.8 | 482.4 | 486.3 | 506.7 | 439.9 | 437.3
2488 | 2363 | 525.6 | 482.8 | 507.4 | 483.2 | 483.8 | 482.4 | 486.3 | 506.9 | 440.6 | 437.3
2489 | 2364 | 525.6 | 482.8 | 507.3 | 483.2 | 483.9 | 482.5 | 486.3 | 506.9 | 440.1 | 437.3
2490 | 2365 | 525.6 | 482.8 | 507.3 | 483.2 | 483.9 | 482.5 | 486.4 | 506.8 | 440.4 | 437.3
2491 | 2366 | 525.5 | 482.8 | 507.4 | 483.2 | 483.9 | 482.6 | 486.4 | 506.6 | 440.8 | 437.3
2492.1 | 2367.1 | 525.5 | 482.8 | 507.4 | 483.2 | 483.9 | 482.6 | 486.4 | 506.8 | 440.9 | 437.4
2493.1 | 2368.1 | 525.6 | 482.8 | 507.4 | 483.3 | 484.1 | 482.7 | 486.5 | 506.7 | 440.9 | 437.4
2494.1 | 2369.1 | 525.6 | 482.8 | 507.4 | 483.3 | 484.1 | 482.7 | 486.5 | 506.6 | 440.9 | 437.4
2495.1 | 2370.1 | 525.6 | 482.8 | 507.5 | 483.3 | 484 | 482.7 | 486.5 | 506.7 | 441 | 437.5
2496.1 | 2371.1 | 525.5 | 482.8 | 507.4 | 483.3 | 484.1 | 482.8 | 486.5 | 506.7 | 441 | 437.5
2497.1 | 2372.1 | 525.5 | 482.9 | 507.4 | 483.3 | 484.2 | 482.8 | 486.6 | 506.7 | 440.7 | 437.5
2498.1 | 2373.1 | 525.5 | 482.9 | 507.4 | 483.3 | 484.2 | 482.9 | 486.6 | 506.8 | 440 | 437.6
2499.1 | 2374.1 | 525.4 | 482.9 | 507.5 | 483.3 | 484.2 | 482.9 | 486.6 | 507 | 440.8 | 437.6
2500.1 | 2375.1 | 525.4 | 482.9 | 507.4 | 483.3 | 484.3 | 482.9 | 486.7 | 507 | 440.9 | 437.6
2501.1 | 2376.1 | 525.4 | 482.9 | 507.4 | 483.3 | 484.3 | 483 | 486.7 | 507.1 | 440.9 | 437.6
2502.1 | 2377.1 | 525.4 | 482.9 | 507.5 | 483.3 | 484.3 | 483 | 486.7 | 507.2 | 440.8 | 437.6
2503.1 | 2378.1 | 525.3 | 482.9 | 507.5 | 483.3 | 484.4 | 483 | 486.8 | 507.3 | 441.2 | 437.7
2504.1 | 2379.1 | 525.3 | 482.9 | 507.5 | 483.3 | 484.5 | 483.1 | 486.8 | 507.5 | 441.1 | 437.6
2505.1 | 2380.1 | 525.3 | 482.9 | 507.5 | 483.3 | 484.4 | 483.1 | 486.8 | 507.7 | 440.9 | 437.7
2506.1 | 2381.1 | 525.3 | 482.9 | 507.6 | 483.3 | 484.4 | 483.1 | 486.9 | 507.5 | 441.2 | 437.7
2507.1 | 2382.1 | 525.3 | 482.9 | 507.5 | 483.4 | 484.6 | 483.2 | 486.9 | 507.4 | 440.6 | 437.7
2508.1 | 2383.1 | 525.3 | 482.9 | 507.5 | 483.4 | 484.6 | 483.2 | 486.9 | 507.5 | 440.3 | 437.8
2509.1 | 2384.1 | 525.3 | 482.9 | 507.5 | 483.4 | 484.5 | 483.3 | 486.9 | 507.4 | 440 | 437.9
2510.1 | 2385.1 | 525.3 | 483 | 507.5 | 483.4 | 484.6 | 483.3 | 487 | 507.4 | 440.2 | 437.9
2511.1 | 2386.1 | 525.3 | 483 | 507.5 | 483.4 | 484.7 | 483.3 | 487 | 507.6 | 440.7 | 437.9
2512.1 | 2387.1 | 525.3 | 483 | 507.6 | 483.4 | 484.7 | 483.4 | 487 | 507.7 | 440.9 | 437.9
2513.1 | 2388.1 | 525.4 | 483 | 507.6 | 483.4 | 484.7 | 483.4 | 487.1 | 507.8 | 440.2 | 437.9
2514.1 | 2389.1 | 525.4 | 483 | 507.5 | 483.4 | 484.8 | 483.5 | 487.1 | 507.9 | 441 | 437.9
2515.1 | 2390.1 | 525.4 | 483 | 507.5 | 483.4 | 484.8 | 483.5 | 487.1 | 508 | 441 | 437.9
2516.1 | 2391.1 | 525.4 | 483 | 507.6 | 483.4 | 484.8 | 483.5 | 487.1 | 508.1 | 440.3 | 438
2517.1 | 2392.1 | 525.5 | 483 | 507.5 | 483.4 | 484.9 | 483.6 | 487.2 | 508.2 | 441.1 | 437.9
2518.1 | 2393.1 | 525.5 | 483 | 507.5 | 483.4 | 485 | 483.6 | 487.2 | 508.2 | 441.1 | 438
2519.1 | 2394.1 | 525.5 | 483 | 507.6 | 483.4 | 485 | 483.6 | 487.2 | 508.3 | 440.5 | 438
2520.1 | 2395.1 | 525.5 | 483 | 507.6 | 483.4 | 485 | 483.7 | 487.2 | 508.5 | 441.4 | 438
2521.1 | 2396.1 | 525.5 | 483 | 507.5 | 483.5 | 485.1 | 483.7 | 487.3 | 508.8 | 441.5 | 438
2522.1 | 2397.1 | 525.5 | 483 | 507.5 | 483.5 | 485.1 | 483.8 | 487.3 | 508.8 | 441.5 | 438
2523.1 | 2398.1 | 525.5 | 483 | 507.6 | 483.5 | 485.1 | 483.8 | 487.3 | 508.5 | 441.6 | 438.1
2524.1 | 2399.1 | 525.5 | 483 | 507.6 | 483.5 | 485.1 | 483.8 | 487.4 | 508.5 | 441.6 | 438.1
2525.1 | 2400.1 | 525.5 | 483.1 | 507.6 | 483.5 | 485.2 | 483.9 | 487.4 | 508.4 | 441.7 | 438.1
2526.1 | 2401.1 | 525.5 | 483.1 | 507.6 | 483.5 | 485.2 | 483.9 | 487.4 | 508.3 | 441.7 | 438.1
2527.1 | 2402.1 | 525.5 | 483.1 | 507.6 | 483.5 | 485.2 | 483.9 | 487.4 | 508.3 | 441.3 | 438.1
2528.1 | 2403.1 | 525.6 | 483.1 | 507.6 | 483.5 | 485.3 | 484 | 487.5 | 508.4 | 441.2 | 438.2
2529.1 | 2404.1 | 525.6 | 483.1 | 507.7 | 483.5 | 485.3 | 484 | 487.5 | 508.4 | 440.9 | 438.2
2530.1 | 2405.1 | 525.6 | 483.1 | 507.7 | 483.5 | 485.3 | 484 | 487.5 | 508.5 | 441.2 | 438.2
2531.1 | 2406.1 | 525.6 | 483.1 | 507.7 | 483.5 | 485.4 | 484.1 | 487.5 | 508.5 | 441 | 438.2
2532.1 | 2407.1 | 525.7 | 483.1 | 507.7 | 483.6 | 485.4 | 484.2 | 487.6 | 508.5 | 441.1 | 438.3
2533.1 | 2408.1 | 525.7 | 483.1 | 507.7 | 483.6 | 485.4 | 484.2 | 487.6 | 508.4 | 441.3 | 438.3
2534.1 | 2409.1 | 525.7 | 483.1 | 507.8 | 483.6 | 485.4 | 484.2 | 487.6 | 508.4 | 441.8 | 438.3
2535.1 | 2410.1 | 525.7 | 483.2 | 507.7 | 483.6 | 485.5 | 484.3 | 487.6 | 508.5 | 441.6 | 438.2
2536.1 | 2411.1 | 525.7 | 483.2 | 507.7 | 483.6 | 485.6 | 484.3 | 487.7 | 508.6 | 441.5 | 438.3
2537.1 | 2412.1 | 525.7 | 483.1 | 507.8 | 483.6 | 485.5 | 484.3 | 487.7 | 508.7 | 441.8 | 438.3
2538.1 | 2413.1 | 525.7 | 483.2 | 507.7 | 483.6 | 485.6 | 484.4 | 487.7 | 508.6 | 441.5 | 438.3
2539.1 | 2414.1 | 525.8 | 483.2 | 507.7 | 483.6 | 485.7 | 484.4 | 487.7 | 508.7 | 441.4 | 438.3
2540.1 | 2415.1 | 525.8 | 483.2 | 507.8 | 483.6 | 485.7 | 484.4 | 487.8 | 508.8 | 440.9 | 438.3
2541.1 | 2416.1 | 525.9 | 483.2 | 507.8 | 483.6 | 485.7 | 484.5 | 487.8 | 508.8 | 441.5 | 438.3
2542.1 | 2417.1 | 525.9 | 483.2 | 507.8 | 483.6 | 485.8 | 484.5 | 487.8 | 509 | 441.5 | 438.3
2543.1 | 2418.1 | 525.9 | 483.2 | 507.8 | 483.6 | 485.8 | 484.6 | 487.8 | 509.2 | 441.6 | 438.3
2544.1 | 2419.1 | 526 | 483.2 | 507.8 | 483.6 | 485.8 | 484.6 | 487.9 | 509.3 | 441.5 | 438.3
2545.1 | 2420.1 | 526 | 483.3 | 507.8 | 483.7 | 485.8 | 484.6 | 487.9 | 509.3 | 442 | 438.3
2546.1 | 2421.1 | 526 | 483.3 | 507.8 | 483.7 | 485.9 | 484.7 | 487.9 | 509.3 | 442 | 438.3
2547.1 | 2422.1 | 526.1 | 483.3 | 507.8 | 483.7 | 485.9 | 484.7 | 488 | 509.3 | 441.8 | 438.4
2548.1 | 2423.1 | 526.1 | 483.3 | 507.9 | 483.7 | 485.9 | 484.7 | 488 | 509.3 | 442.2 | 438.4
2549.1 | 2424.1 | 526.1 | 483.3 | 507.8 | 483.7 | 486 | 484.8 | 488 | 509.2 | 441.7 | 438.4
2550.1 | 2425.1 | 526.1 | 483.3 | 507.8 | 483.7 | 486.1 | 484.8 | 488 | 509.2 | 441.6 | 438.5
2551.1 | 2426.1 | 526.1 | 483.3 | 507.9 | 483.7 | 486 | 484.8 | 488.1 | 509.2 | 441.3 | 438.5
2552.1 | 2427.1 | 526.1 | 483.3 | 507.9 | 483.7 | 486.1 | 484.9 | 488.1 | 509.2 | 441.6 | 438.5
2553.1 | 2428.1 | 526.1 | 483.3 | 507.9 | 483.7 | 486.2 | 484.9 | 488.1 | 509.2 | 442.1 | 438.5
2554.1 | 2429.1 | 526.2 | 483.3 | 507.9 | 483.7 | 486.2 | 485 | 488.2 | 509.3 | 442.5 | 438.6
2555.1 | 2430.1 | 526.2 | 483.3 | 508 | 483.7 | 486.2 | 485 | 488.2 | 509.4 | 441.4 | 438.6
2556.1 | 2431.1 | 526.2 | 483.4 | 507.9 | 483.8 | 486.3 | 485 | 488.2 | 509.5 | 442.2 | 438.6
2557.1 | 2432.1 | 526.2 | 483.4 | 507.9 | 483.8 | 486.3 | 485.1 | 488.3 | 509.7 | 442.2 | 438.6
2558.1 | 2433.1 | 526.2 | 483.4 | 508 | 483.8 | 486.3 | 485.1 | 488.3 | 509.7 | 441.5 | 438.7
2559.1 | 2434.1 | 526.2 | 483.4 | 508 | 483.8 | 486.4 | 485.1 | 488.3 | 509.7 | 442.3 | 438.7
2560.1 | 2435.1 | 526.3 | 483.4 | 508 | 483.8 | 486.4 | 485.2 | 488.3 | 509.7 | 442.2 | 438.7
2561.1 | 2436.1 | 526.3 | 483.4 | 508 | 483.8 | 486.4 | 485.2 | 488.4 | 509.7 | 441.8 | 438.8
2562.1 | 2437.1 | 526.3 | 483.4 | 508.1 | 483.8 | 486.4 | 485.2 | 488.4 | 509.6 | 442.4 | 438.8
2563.1 | 2438.1 | 526.3 | 483.4 | 508 | 483.8 | 486.5 | 485.3 | 488.4 | 509.6 | 442.4 | 438.8
2564.1 | 2439.1 | 526.2 | 483.5 | 508 | 483.8 | 486.6 | 485.3 | 488.5 | 509.6 | 442.4 | 438.8
2565.1 | 2440.1 | 526.2 | 483.4 | 508.1 | 483.8 | 486.5 | 485.4 | 488.5 | 509.6 | 442.4 | 438.8
2566.1 | 2441.1 | 526.2 | 483.4 | 508.1 | 483.8 | 486.6 | 485.4 | 488.5 | 509.8 | 442.4 | 438.8
2567.1 | 2442.1 | 526.2 | 483.5 | 508.1 | 483.9 | 486.7 | 485.5 | 488.6 | 510.1 | 442.5 | 438.8
2568.1 | 2443.1 | 526.2 | 483.5 | 508.1 | 483.8 | 486.6 | 485.5 | 488.6 | 509.9 | 442.8 | 438.8
2569.1 | 2444.1 | 526.1 | 483.5 | 508.1 | 483.8 | 486.7 | 485.5 | 488.6 | 509.8 | 442.5 | 438.9
2570.1 | 2445.1 | 526 | 483.5 | 508.1 | 483.9 | 486.8 | 485.6 | 488.6 | 509.9 | 442.3 | 438.9
2571.1 | 2446.1 | 526 | 483.5 | 508.1 | 483.9 | 486.8 | 485.6 | 488.7 | 509.9 | 442.2 | 438.9
2572.1 | 2447.1 | 525.9 | 483.5 | 508.2 | 483.9 | 486.8 | 485.6 | 488.7 | 510.1 | 442.5 | 438.9
2573.1 | 2448.1 | 525.9 | 483.5 | 508.1 | 483.9 | 486.8 | 485.7 | 488.7 | 510.1 | 442.2 | 438.9
2574.1 | 2449.1 | 525.9 | 483.5 | 508.1 | 483.9 | 486.9 | 485.7 | 488.8 | 510 | 442.3 | 439
2575.1 | 2450.1 | 525.8 | 483.5 | 508.2 | 483.9 | 486.9 | 485.8 | 488.8 | 509.9 | 442.6 | 439
2576.1 | 2451.1 | 525.8 | 483.5 | 508.2 | 483.9 | 486.9 | 485.8 | 488.8 | 510 | 442.8 | 439
2577.1 | 2452.1 | 525.7 | 483.6 | 508.1 | 483.9 | 487 | 485.8 | 488.8 | 510.2 | 442.8 | 439
2578.1 | 2453.1 | 525.7 | 483.6 | 508.1 | 483.9 | 487.1 | 485.9 | 488.9 | 510.1 | 442.7 | 439
2579.1 | 2454.1 | 525.7 | 483.6 | 508.2 | 483.9 | 487 | 485.9 | 488.9 | 510.2 | 443 | 439
2580.1 | 2455.1 | 525.7 | 483.6 | 508.1 | 483.9 | 487.1 | 486 | 488.9 | 510.4 | 442.7 | 439
2581.1 | 2456.1 | 525.6 | 483.6 | 508.1 | 483.9 | 487.2 | 486 | 488.9 | 510.3 | 442.6 | 439
2582.1 | 2457.1 | 525.6 | 483.6 | 508.1 | 484 | 487.2 | 486 | 489 | 510.3 | 442.3 | 439.1
2583.1 | 2458.1 | 525.5 | 483.6 | 508.2 | 483.9 | 487.2 | 486.1 | 489 | 510.6 | 442.6 | 439.1
2584.1 | 2459.1 | 525.5 | 483.6 | 508.1 | 484 | 487.3 | 486.1 | 489 | 510.6 | 442.8 | 439.1
2585.1 | 2460.1 | 525.4 | 483.6 | 508.1 | 484 | 487.3 | 486.2 | 489.1 | 510.7 | 442.8 | 439.1
2586.1 | 2461.1 | 525.4 | 483.6 | 508.2 | 484 | 487.3 | 486.2 | 489.1 | 510.9 | 442.7 | 439.1
2587.1 | 2462.1 | 525.4 | 483.6 | 508.2 | 484 | 487.4 | 486.2 | 489.1 | 511.2 | 443.2 | 439.1
2588.1 | 2463.1 | 525.4 | 483.7 | 508.2 | 484 | 487.4 | 486.3 | 489.1 | 511.4 | 443.1 | 439.1
2589.1 | 2464.1 | 525.4 | 483.7 | 508.2 | 484 | 487.4 | 486.3 | 489.2 | 511.4 | 442.8 | 439.2
2590.1 | 2465.1 | 525.4 | 483.7 | 508.3 | 484 | 487.4 | 486.3 | 489.2 | 511.3 | 443.3 | 439.2
2591.1 | 2466.1 | 525.4 | 483.7 | 508.2 | 484 | 487.5 | 486.4 | 489.2 | 511.2 | 442.8 | 439.2
2592.1 | 2467.1 | 525.4 | 483.7 | 508.2 | 484 | 487.6 | 486.4 | 489.3 | 511.2 | 442.8 | 439.2
2593.1 | 2468.1 | 525.4 | 483.7 | 508.3 | 484 | 487.5 | 486.4 | 489.3 | 511.1 | 442.5 | 439.3
2594.1 | 2469.1 | 525.5 | 483.7 | 508.3 | 484 | 487.6 | 486.5 | 489.3 | 511.1 | 442.6 | 439.3
2595.1 | 2470.1 | 525.5 | 483.7 | 508.3 | 484.1 | 487.7 | 486.5 | 489.3 | 511.1 | 443 | 439.3
2596.1 | 2471.1 | 525.5 | 483.7 | 508.3 | 484 | 487.7 | 486.5 | 489.4 | 511.1 | 443.5 | 439.3
2597.1 | 2472.1 | 525.6 | 483.7 | 508.3 | 484 | 487.7 | 486.6 | 489.4 | 511.3 | 442.5 | 439.4
2598.1 | 2473.1 | 525.6 | 483.8 | 508.3 | 484.1 | 487.8 | 486.6 | 489.4 | 511.3 | 443.3 | 439.4
2599.1 | 2474.1 | 525.6 | 483.8 | 508.3 | 484.1 | 487.8 | 486.7 | 489.4 | 511.2 | 443.5 | 439.4
2600.1 | 2475.1 | 525.7 | 483.7 | 508.4 | 484.1 | 487.8 | 486.7 | 489.5 | 511.2 | 442.7 | 439.4
2601.1 | 2476.1 | 525.7 | 483.8 | 508.3 | 484.1 | 487.9 | 486.7 | 489.5 | 511.2 | 443.6 | 439.4
2602.1 | 2477.1 | 525.7 | 483.8 | 508.3 | 484.1 | 487.9 | 486.8 | 489.5 | 511.2 | 443.4 | 439.4
2603.1 | 2478.1 | 525.8 | 483.8 | 508.4 | 484.1 | 487.9 | 486.8 | 489.6 | 511.3 | 442.9 | 439.5
2604.1 | 2479.1 | 525.8 | 483.8 | 508.4 | 484.1 | 487.9 | 486.8 | 489.6 | 511.1 | 443.4 | 439.5
2605.1 | 2480.1 | 525.8 | 483.8 | 508.3 | 484.1 | 488 | 486.9 | 489.6 | 511.1 | 443.4 | 439.5
2606.1 | 2481.1 | 525.8 | 483.8 | 508.4 | 484.1 | 488.1 | 486.9 | 489.7 | 511.1 | 443.4 | 439.5
2607.1 | 2482.1 | 525.9 | 483.8 | 508.4 | 484.1 | 488 | 486.9 | 489.7 | 511.2 | 443.5 | 439.5
2608.1 | 2483.1 | 525.9 | 483.8 | 508.4 | 484.1 | 488.1 | 487 | 489.7 | 511.4 | 443.6 | 439.5
2609.1 | 2484.1 | 525.9 | 483.9 | 508.4 | 484.1 | 488.2 | 487 | 489.7 | 511.4 | 443.7 | 439.5
2610.1 | 2485.1 | 525.9 | 483.8 | 508.5 | 484.1 | 488.2 | 487.1 | 489.8 | 511.1 | 443.5 | 439.5
2611.1 | 2486.1 | 525.9 | 483.9 | 508.5 | 484.1 | 488.2 | 487.1 | 489.8 | 511 | 443.5 | 439.6
2612.1 | 2487.1 | 525.9 | 483.9 | 508.4 | 484.2 | 488.3 | 487.2 | 489.8 | 511 | 443.2 | 439.6
2613.1 | 2488.1 | 525.9 | 483.9 | 508.4 | 484.1 | 488.3 | 487.2 | 489.8 | 511.2 | 443.3 | 439.6
2614.1 | 2489.1 | 525.9 | 483.9 | 508.5 | 484.1 | 488.2 | 487.2 | 489.9 | 511.5 | 443.3 | 439.6
2615.1 | 2490.1 | 525.9 | 483.9 | 508.5 | 484.1 | 488.3 | 487.3 | 489.9 | 511.5 | 443.5 | 439.7
2616.1 | 2491.1 | 525.9 | 483.9 | 508.5 | 484.2 | 488.4 | 487.3 | 489.9 | 511.3 | 443.4 | 439.7
2617.1 | 2492.1 | 525.9 | 483.9 | 508.5 | 484.2 | 488.4 | 487.3 | 490 | 511.2 | 443.3 | 439.7
2618.1 | 2493.1 | 525.9 | 483.9 | 508.6 | 484.2 | 488.4 | 487.4 | 490 | 511.1 | 443.5 | 439.7
2619.1 | 2494.1 | 525.9 | 483.9 | 508.5 | 484.2 | 488.5 | 487.4 | 490 | 511 | 443.5 | 439.7
2620.1 | 2495.1 | 525.9 | 484 | 508.5 | 484.2 | 488.6 | 487.5 | 490 | 511.1 | 443.7 | 439.7
2621.1 | 2496.1 | 525.9 | 483.9 | 508.6 | 484.2 | 488.5 | 487.5 | 490.1 | 511.3 | 444.1 | 439.8
2622.1 | 2497.1 | 525.9 | 484 | 508.5 | 484.2 | 488.6 | 487.5 | 490.1 | 511.4 | 443.8 | 439.8
2623.1 | 2498.1 | 525.9 | 484 | 508.5 | 484.2 | 488.7 | 487.6 | 490.1 | 511.5 | 443.8 | 439.8
2624.1 | 2499.1 | 525.9 | 484 | 508.5 | 484.2 | 488.7 | 487.6 | 490.2 | 511.8 | 443.4 | 439.8
2625.1 | 2500.1 | 525.9 | 484 | 508.6 | 484.2 | 488.6 | 487.6 | 490.2 | 511.8 | 443.7 | 439.8
2626.1 | 2501.1 | 525.8 | 484 | 508.5 | 484.2 | 488.8 | 487.7 | 490.2 | 511.8 | 443.9 | 439.8
2627.1 | 2502.1 | 525.8 | 484 | 508.5 | 484.3 | 488.8 | 487.7 | 490.2 | 511.7 | 444 | 439.9
2628.1 | 2503.1 | 525.8 | 484 | 508.6 | 484.2 | 488.8 | 487.7 | 490.3 | 511.8 | 443.9 | 439.9
2629.1 | 2504.1 | 525.7 | 484 | 508.6 | 484.2 | 488.8 | 487.8 | 490.3 | 511.8 | 444.4 | 439.9
2630.1 | 2505.1 | 525.7 | 484 | 508.6 | 484.2 | 488.9 | 487.8 | 490.3 | 512.1 | 444.3 | 439.9
2631.1 | 2506.1 | 525.6 | 484 | 508.6 | 484.3 | 488.9 | 487.9 | 490.4 | 512.1 | 444.1 | 440
2632.1 | 2507.1 | 525.6 | 484 | 508.6 | 484.3 | 488.9 | 487.9 | 490.4 | 512.3 | 444.5 | 440
2633.1 | 2508.1 | 525.5 | 484.1 | 508.5 | 484.3 | 489 | 487.9 | 490.4 | 512.3 | 444 | 440
2634.1 | 2509.1 | 525.5 | 484.1 | 508.6 | 484.3 | 489.1 | 488 | 490.5 | 512.2 | 443.6 | 440.1
2635.1 | 2510.1 | 525.5 | 484.1 | 508.6 | 484.3 | 489 | 488 | 490.5 | 512 | 443.5 | 440.1
2636.1 | 2511.1 | 525.4 | 484.1 | 508.6 | 484.3 | 489.1 | 488 | 490.5 | 512 | 443.7 | 440.1
2637.1 | 2512.1 | 525.4 | 484.1 | 508.6 | 484.3 | 489.2 | 488.1 | 490.5 | 511.9 | 444 | 440.1
2638.1 | 2513.1 | 525.4 | 484.1 | 508.6 | 484.3 | 489.2 | 488.1 | 490.6 | 511.9 | 444.2 | 440.1
2639.1 | 2514.1 | 525.4 | 484.1 | 508.7 | 484.3 | 489.2 | 488.1 | 490.6 | 512 | 443.5 | 440.2
2640.1 | 2515.1 | 525.3 | 484.1 | 508.6 | 484.3 | 489.3 | 488.2 | 490.6 | 512.1 | 444.1 | 440.2
2641.1 | 2516.1 | 525.3 | 484.1 | 508.6 | 484.3 | 489.3 | 488.2 | 490.7 | 512.1 | 444.1 | 440.2
2642.1 | 2517.1 | 525.3 | 484.1 | 508.7 | 484.3 | 489.3 | 488.2 | 490.7 | 512.2 | 443.7 | 440.2
2643.1 | 2518.1 | 525.3 | 484.1 | 508.7 | 484.3 | 489.4 | 488.3 | 490.7 | 512.5 | 444.3 | 440.2
2644.1 | 2519.1 | 525.3 | 484.1 | 508.6 | 484.3 | 489.4 | 488.3 | 490.8 | 512.5 | 444.1 | 440.2
2645.1 | 2520.1 | 525.3 | 484.1 | 508.7 | 484.3 | 489.4 | 488.4 | 490.8 | 512.5 | 444 | 440.2
2646.1 | 2521.1 | 525.3 | 484.1 | 508.7 | 484.3 | 489.4 | 488.4 | 490.8 | 512.9 | 444.5 | 440.3
2647.1 | 2522.1 | 525.3 | 484.2 | 508.6 | 484.4 | 489.6 | 488.4 | 490.8 | 513.1 | 444.5 | 440.3
2648.1 | 2523.1 | 525.3 | 484.2 | 508.7 | 484.4 | 489.6 | 488.5 | 490.9 | 512.9 | 444.4 | 440.3
2649.1 | 2524.1 | 525.3 | 484.2 | 508.7 | 484.4 | 489.5 | 488.5 | 490.9 | 512.8 | 444.4 | 440.3
2650.1 | 2525.1 | 525.3 | 484.2 | 508.7 | 484.4 | 489.6 | 488.6 | 490.9 | 512.8 | 444.4 | 440.3
2651.1 | 2526.1 | 525.3 | 484.2 | 508.7 | 484.4 | 489.6 | 488.6 | 491 | 512.8 | 444.4 | 440.3
2652.1 | 2527.1 | 525.3 | 484.2 | 508.8 | 484.4 | 489.6 | 488.6 | 491 | 512.8 | 444.5 | 440.4
2653.1 | 2528.1 | 525.4 | 484.2 | 508.8 | 484.4 | 489.6 | 488.6 | 491 | 513 | 444.3 | 440.4
2654.1 | 2529.1 | 525.4 | 484.2 | 508.8 | 484.4 | 489.8 | 488.7 | 491 | 513.2 | 444.2 | 440.4
2655.1 | 2530.1 | 525.4 | 484.2 | 508.8 | 484.4 | 489.8 | 488.7 | 491.1 | 513 | 444.4 | 440.4
2656.1 | 2531.1 | 525.4 | 484.2 | 508.9 | 484.4 | 489.7 | 488.8 | 491.1 | 513 | 444.4 | 440.4
2657.1 | 2532.1 | 525.5 | 484.2 | 508.8 | 484.4 | 489.8 | 488.8 | 491.1 | 513 | 444.4 | 440.4
2658.1 | 2533.1 | 525.5 | 484.3 | 508.8 | 484.4 | 489.9 | 488.9 | 491.2 | 513.1 | 444.4 | 440.5
2659.1 | 2534.1 | 525.5 | 484.2 | 508.8 | 484.4 | 489.9 | 488.9 | 491.2 | 513.2 | 444.6 | 440.5
2660.1 | 2535.1 | 525.5 | 484.2 | 508.8 | 484.4 | 489.9 | 488.9 | 491.2 | 513.3 | 445.1 | 440.5
2661.1 | 2536.1 | 525.5 | 484.3 | 508.8 | 484.5 | 490 | 489 | 491.2 | 513.3 | 444.9 | 440.5
2662.1 | 2537.1 | 525.5 | 484.3 | 508.8 | 484.5 | 490.1 | 489 | 491.3 | 513.4 | 444.9 | 440.5
2663.1 | 2538.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490 | 489 | 491.3 | 513.4 | 445.2 | 440.5
2664.1 | 2539.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.1 | 489.1 | 491.3 | 513.3 | 444.9 | 440.6
2665.1 | 2540.1 | 525.6 | 484.3 | 508.8 | 484.5 | 490.2 | 489.1 | 491.4 | 513.1 | 444.8 | 440.6
2666.1 | 2541.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.1 | 489.2 | 491.4 | 513.2 | 444.6 | 440.6
2667.1 | 2542.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.2 | 489.2 | 491.4 | 513.3 | 444.7 | 440.7
2668.1 | 2543.1 | 525.6 | 484.3 | 508.8 | 484.5 | 490.3 | 489.2 | 491.4 | 513.4 | 444.9 | 440.7
2669.1 | 2544.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.3 | 489.3 | 491.5 | 513.6 | 445 | 440.7
2670.1 | 2545.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.3 | 489.3 | 491.5 | 513.7 | 444.7 | 440.7
2671.1 | 2546.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.3 | 489.3 | 491.5 | 513.7 | 445.4 | 440.7
2672.1 | 2547.1 | 525.6 | 484.4 | 508.9 | 484.5 | 490.4 | 489.4 | 491.5 | 513.7 | 445.3 | 440.7
2673.1 | 2548.1 | 525.6 | 484.4 | 508.9 | 484.5 | 490.4 | 489.4 | 491.6 | 513.9 | 444.9 | 440.7
2674.1 | 2549.1 | 525.6 | 484.3 | 508.9 | 484.5 | 490.4 | 489.4 | 491.6 | 513.9 | 445.5 | 440.7
2675.1 | 2550.1 | 525.7 | 484.4 | 508.9 | 484.5 | 490.5 | 489.5 | 491.6 | 513.8 | 445 | 440.7
2676.1 | 2551.1 | 525.7 | 484.4 | 508.9 | 484.5 | 490.5 | 489.5 | 491.7 | 513.9 | 445 | 440.8
2677.1 | 2552.1 | 525.7 | 484.4 | 509 | 484.5 | 490.5 | 489.5 | 491.7 | 514 | 444.8 | 440.8
2678.1 | 2553.1 | 525.7 | 484.4 | 509 | 484.5 | 490.6 | 489.6 | 491.7 | 514.1 | 444.9 | 440.8
2679.1 | 2554.1 | 525.7 | 484.4 | 509 | 484.6 | 490.6 | 489.6 | 491.7 | 514 | 445.3 | 440.8
2680.1 | 2555.1 | 525.7 | 484.4 | 509 | 484.6 | 490.7 | 489.6 | 491.8 | 514 | 445.6 | 440.8
2681.1 | 2556.1 | 525.6 | 484.4 | 509 | 484.5 | 490.7 | 489.7 | 491.8 | 514 | 444.8 | 440.9
2682.1 | 2557.1 | 525.6 | 484.5 | 508.9 | 484.6 | 490.8 | 489.7 | 491.8 | 514.1 | 445.5 | 440.9
2683.1 | 2558.1 | 525.6 | 484.5 | 508.9 | 484.6 | 490.8 | 489.8 | 491.9 | 513.9 | 445.6 | 440.8
2684.1 | 2559.1 | 525.6 | 484.4 | 509 | 484.6 | 490.7 | 489.8 | 491.9 | 513.8 | 445 | 440.9
2685.1 | 2560.1 | 525.6 | 484.5 | 509 | 484.6 | 490.8 | 489.8 | 491.9 | 513.7 | 445.7 | 440.9
2686.1 | 2561.1 | 525.6 | 484.5 | 509 | 484.6 | 490.9 | 489.9 | 492 | 514 | 445.5 | 440.9
2687.1 | 2562.1 | 525.6 | 484.5 | 509 | 484.6 | 490.9 | 489.9 | 492 | 514.1 | 445.2 | 441
2688.1 | 2563.1 | 525.7 | 484.5 | 509.1 | 484.6 | 490.9 | 489.9 | 492 | 514.2 | 445.8 | 441
2689.1 | 2564.1 | 525.7 | 484.5 | 509 | 484.6 | 491 | 490 | 492 | 514.1 | 445.9 | 440.9
2690.1 | 2565.1 | 525.7 | 484.5 | 509.1 | 484.6 | 491 | 490 | 492.1 | 514 | 445.9 | 441
2691.1 | 2566.1 | 525.7 | 484.5 | 509.1 | 484.6 | 491 | 490 | 492.1 | 514.3 | 445.9 | 441
2692.1 | 2567.1 | 525.8 | 484.5 | 509.1 | 484.6 | 491 | 490.1 | 492.1 | 514.3 | 445.8 | 441
2693.1 | 2568.1 | 525.8 | 484.5 | 509.1 | 484.6 | 491.1 | 490.1 | 492.2 | 514.5 | 445.9 | 441
2694.1 | 2569.1 | 525.8 | 484.5 | 509.2 | 484.6 | 491 | 490.1 | 492.2 | 514.6 | 445.9 | 441
2695.1 | 2570.1 | 525.8 | 484.5 | 509.2 | 484.6 | 491.1 | 490.1 | 492.2 | 514.6 | 445.4 | 441
2696.1 | 2571.1 | 525.8 | 484.5 | 509.1 | 484.6 | 491.2 | 490.2 | 492.2 | 514.7 | 445.6 | 441.1
2697.1 | 2572.1 | 525.8 | 484.6 | 509.1 | 484.6 | 491.2 | 490.3 | 492.3 | 514.7 | 445.7 | 441.1
2698.1 | 2573.1 | 525.8 | 484.5 | 509.2 | 484.6 | 491.2 | 490.3 | 492.3 | 514.8 | 445.5 | 441.1
2699.1 | 2574.1 | 525.8 | 484.6 | 509.2 | 484.6 | 491.3 | 490.3 | 492.3 | 514.9 | 445.7 | 441.1
2700.1 | 2575.1 | 525.8 | 484.6 | 509.1 | 484.7 | 491.3 | 490.4 | 492.3 | 514.8 | 445.8 | 441.1
2701.1 | 2576.1 | 525.8 | 484.6 | 509.2 | 484.6 | 491.3 | 490.4 | 492.4 | 514.5 | 445.8 | 441.1
2702.1 | 2577.1 | 525.8 | 484.6 | 509.2 | 484.6 | 491.3 | 490.4 | 492.4 | 514.4 | 446.2 | 441.1
2703.1 | 2578.1 | 525.7 | 484.6 | 509.1 | 484.7 | 491.4 | 490.5 | 492.4 | 514.4 | 446 | 441.1
2704.1 | 2579.1 | 525.7 | 484.6 | 509.1 | 484.7 | 491.5 | 490.5 | 492.4 | 514.4 | 445.9 | 441.2
2705.1 | 2580.1 | 525.8 | 484.6 | 509.2 | 484.6 | 491.4 | 490.5 | 492.5 | 514.6 | 446.2 | 441.2
2706.1 | 2581.1 | 525.8 | 484.6 | 509.2 | 484.7 | 491.5 | 490.6 | 492.5 | 514.7 | 445.9 | 441.2
2707.1 | 2582.1 | 525.8 | 484.6 | 509.2 | 484.7 | 491.6 | 490.6 | 492.5 | 514.9 | 445.8 | 441.2
2708.1 | 2583.1 | 525.8 | 484.6 | 509.2 | 484.7 | 491.6 | 490.6 | 492.5 | 515.1 | 445.8 | 441.2
2709.1 | 2584.1 | 525.8 | 484.6 | 509.3 | 484.7 | 491.5 | 490.6 | 492.6 | 514.8 | 446 | 441.2
2710.1 | 2585.1 | 525.8 | 484.7 | 509.2 | 484.7 | 491.6 | 490.7 | 492.6 | 514.8 | 445.9 | 441.3
2711.1 | 2586.1 | 525.8 | 484.7 | 509.2 | 484.7 | 491.7 | 490.7 | 492.6 | 515.1 | 445.8 | 441.3
2712.1 | 2587.1 | 525.8 | 484.6 | 509.3 | 484.7 | 491.6 | 490.7 | 492.6 | 515.3 | 445.9 | 441.3
2713.1 | 2588.1 | 525.8 | 484.7 | 509.3 | 484.7 | 491.7 | 490.8 | 492.7 | 515.2 | 446 | 441.3
2714.1 | 2589.1 | 525.8 | 484.7 | 509.2 | 484.7 | 491.8 | 490.8 | 492.7 | 515.2 | 446 | 441.3
2715.1 | 2590.1 | 525.8 | 484.7 | 509.3 | 484.7 | 491.8 | 490.9 | 492.7 | 515.3 | 445.9 | 441.3
2716.1 | 2591.1 | 525.8 | 484.7 | 509.3 | 484.7 | 491.8 | 490.9 | 492.8 | 515.4 | 445.9 | 441.4
2717.1 | 2592.1 | 525.8 | 484.7 | 509.2 | 484.7 | 491.9 | 490.9 | 492.8 | 515.5 | 445.5 | 441.4
2718.1 | 2593.1 | 525.9 | 484.7 | 509.2 | 484.7 | 491.9 | 491 | 492.8 | 515.5 | 445.5 | 441.4
2719.1 | 2594.1 | 525.9 | 484.7 | 509.3 | 484.7 | 491.9 | 491 | 492.9 | 515.5 | 445.5 | 441.4
2720.1 | 2595.1 | 525.9 | 484.7 | 509.3 | 484.7 | 492 | 491 | 492.9 | 515.6 | 445.8 | 441.4
2721.1 | 2596.1 | 525.9 | 484.8 | 509.3 | 484.7 | 492 | 491.1 | 492.9 | 515.6 | 446 | 441.5
2722.1 | 2597.1 | 525.9 | 484.7 | 509.3 | 484.7 | 492 | 491.1 | 492.9 | 515.5 | 446.4 | 441.5
2723.1 | 2598.1 | 525.9 | 484.6 | 509.5 | 484.7 | 491.8 | 491 | 493 | 515.6 | 445.7 | 441.6
2724.1 | 2599.1 | 525.9 | 484.5 | 509.8 | 484.6 | 491.5 | 491 | 493 | 515.5 | 446.4 | 441.6
2725.1 | 2600.1 | 525.9 | 484.4 | 510 | 484.5 | 491.4 | 490.9 | 493.1 | 515.5 | 446.3 | 441.6
2726.1 | 2601.1 | 525.8 | 484.4 | 510.1 | 484.4 | 491.3 | 490.9 | 493.1 | 515.4 | 445.6 | 441.7
2727.1 | 2602.1 | 525.6 | 484.4 | 510 | 484.4 | 491.4 | 491 | 493.1 | 515.6 | 446.5 | 441.7
2728.1 | 2603.1 | 525.3 | 484.4 | 510 | 484.5 | 491.5 | 491 | 493.2 | 515.6 | 446.3 | 441.7
2729.1 | 2604.1 | 524.9 | 484.4 | 510 | 484.4 | 491.5 | 491.1 | 493.2 | 515.6 | 445.8 | 441.7
2730.1 | 2605.1 | 524.5 | 484.4 | 510 | 484.4 | 491.5 | 491.1 | 493.2 | 515.6 | 446.5 | 441.8
2731.1 | 2606.1 | 524 | 484.4 | 509.9 | 484.4 | 491.6 | 491.1 | 493.3 | 515.3 | 446.5 | 441.8
2732.1 | 2607.1 | 523.4 | 484.4 | 509.8 | 484.4 | 491.6 | 491.2 | 493.3 | 515.2 | 446.5 | 441.8
2733.1 | 2608.1 | 522.9 | 484.3 | 509.8 | 484.4 | 491.6 | 491.2 | 493.3 | 515.3 | 446.4 | 441.8
2734.1 | 2609.1 | 522.3 | 484.3 | 509.8 | 484.3 | 491.6 | 491.2 | 493.3 | 515.3 | 446.3 | 441.8
2735.1 | 2610.1 | 521.6 | 484.3 | 509.7 | 484.3 | 491.7 | 491.3 | 493.3 | 515.2 | 446.4 | 441.8
2736.1 | 2611.1 | 520.9 | 484.3 | 509.7 | 484.3 | 491.7 | 491.3 | 493.4 | 515.4 | 446.4 | 441.9
2737.1 | 2612.1 | 520.2 | 484.2 | 509.7 | 484.3 | 491.7 | 491.3 | 493.4 | 515.7 | 445.9 | 441.9
2738.1 | 2613.1 | 519.5 | 484.2 | 509.5 | 484.3 | 491.8 | 491.4 | 493.4 | 515.8 | 446.3 | 441.9
2739.1 | 2614.1 | 518.8 | 484.2 | 509.5 | 484.2 | 491.8 | 491.4 | 493.4 | 515.8 | 446.4 | 441.9
2740.1 | 2615.1 | 518 | 484.1 | 509.5 | 484.2 | 491.8 | 491.4 | 493.5 | 515.8 | 446.4 | 441.9
2741.1 | 2616.1 | 517.3 | 484.1 | 509.3 | 484.2 | 491.8 | 491.5 | 493.5 | 515.8 | 446.2 | 441.9
2742.1 | 2617.1 | 516.6 | 484.1 | 509.2 | 484.1 | 491.9 | 491.5 | 493.5 | 515.8 | 446.5 | 441.9
2743.1 | 2618.1 | 515.8 | 484.1 | 509.2 | 484.1 | 491.9 | 491.5 | 493.6 | 515.8 | 446.5 | 442
2744.1 | 2619.1 | 515 | 484 | 509.1 | 484 | 491.9 | 491.6 | 493.6 | 515.9 | 447.1 | 442
2745.1 | 2620.1 | 514.2 | 484 | 509 | 484 | 492 | 491.6 | 493.6 | 516 | 446.9 | 441.9
2746.1 | 2621.1 | 513.4 | 484 | 508.9 | 484 | 492 | 491.7 | 493.6 | 516.1 | 446.8 | 442
2747.1 | 2622.1 | 512.6 | 483.9 | 508.9 | 483.9 | 492 | 491.7 | 493.7 | 516.3 | 447.2 | 442
2748.1 | 2623.1 | 511.8 | 483.8 | 508.8 | 483.8 | 492 | 491.7 | 493.7 | 516.4 | 446.8 | 442
2749.1 | 2624.1 | 511 | 483.8 | 508.7 | 483.8 | 492.1 | 491.7 | 493.7 | 516.6 | 446.6 | 442
2750.1 | 2625.1 | 510.2 | 483.7 | 508.5 | 483.8 | 492.1 | 491.8 | 493.7 | 516.8 | 446.5 | 442
2751.1 | 2626.1 | 509.4 | 483.7 | 508.4 | 483.7 | 492.1 | 491.8 | 493.7 | 516.6 | 446.6 | 442
2752.1 | 2627.1 | 508.6 | 483.6 | 508.3 | 483.6 | 492.2 | 491.8 | 493.7 | 516.6 | 446.9 | 442
2753.1 | 2628.1 | 507.8 | 483.6 | 508.2 | 483.6 | 492.2 | 491.8 | 493.8 | 516.5 | 446.9 | 442
2754.1 | 2629.1 | 506.9 | 483.5 | 508.2 | 483.5 | 492.1 | 491.8 | 493.8 | 516.6 | 446.6 | 442
2755.1 | 2630.1 | 506.1 | 483.4 | 508.1 | 483.5 | 492.2 | 491.9 | 493.8 | 516.8 | 447.3 | 442
2756.1 | 2631.1 | 505.3 | 483.4 | 507.9 | 483.4 | 492.3 | 491.9 | 493.8 | 516.9 | 447.2 | 442
2757.1 | 2632.1 | 504.5 | 483.3 | 507.8 | 483.3 | 492.3 | 491.9 | 493.8 | 516.9 | 446.6 | 442
2758.1 | 2633.1 | 503.6 | 483.2 | 507.7 | 483.2 | 492.2 | 491.9 | 493.8 | 516.9 | 447.4 | 442
2759.1 | 2634.1 | 502.8 | 483.2 | 507.5 | 483.2 | 492.3 | 492 | 493.8 | 516.8 | 446.9 | 442
2760.1 | 2635.1 | 502 | 483.1 | 507.4 | 483.1 | 492.3 | 492 | 493.8 | 516.9 | 446.8 | 442
2761.1 | 2636.1 | 501.2 | 483 | 507.3 | 483 | 492.3 | 492 | 493.8 | 517.1 | 446.6 | 442
2762.1 | 2637.1 | 500.4 | 482.9 | 507.2 | 482.9 | 492.3 | 492 | 493.8 | 516.9 | 446.8 | 442
2763.1 | 2638.1 | 499.7 | 482.8 | 507 | 482.9 | 492.4 | 492 | 493.8 | 517 | 447 | 442
2764.1 | 2639.1 | 499 | 482.8 | 506.9 | 482.8 | 492.3 | 492 | 493.8 | 517 | 447.2 | 442
2765.1 | 2640.1 | 498.2 | 482.7 | 506.8 | 482.7 | 492.3 | 492 | 493.8 | 516.7 | 446.5 | 442
2766.1 | 2641.1 | 497.4 | 482.6 | 506.6 | 482.6 | 492.4 | 492.1 | 493.8 | 516.4 | 447.3 | 442
2767.1 | 2642.1 | 496.6 | 482.5 | 506.4 | 482.5 | 492.4 | 492.1 | 493.8 | 516.3 | 447.4 | 442
2768.1 | 2643.1 | 495.9 | 482.4 | 506.4 | 482.4 | 492.4 | 492.1 | 493.8 | 516.4 | 446.6 | 442
2769.1 | 2644.1 | 495.1 | 482.3 | 506.2 | 482.3 | 492.4 | 492.1 | 493.8 | 516.3 | 447.4 | 442
2770.1 | 2645.1 | 494.3 | 482.2 | 506.1 | 482.2 | 492.4 | 492.1 | 493.8 | 516.1 | 447.1 | 442
2771.1 | 2646.1 | 493.5 | 482.1 | 505.9 | 482.1 | 492.4 | 492.1 | 493.8 | 515.9 | 446.8 | 442
2772.1 | 2647.1 | 492.8 | 482 | 505.8 | 482 | 492.4 | 492.1 | 493.8 | 516 | 447.4 | 442
2773.1 | 2648.1 | 492 | 481.9 | 505.5 | 481.9 | 492.5 | 492.2 | 493.8 | 516.1 | 447.3 | 441.9
2774.1 | 2649.1 | 491.2 | 481.8 | 505.4 | 481.8 | 492.5 | 492.2 | 493.8 | 516.2 | 447.3 | 441.9
2775.1 | 2650.1 | 490.4 | 481.7 | 505.3 | 481.7 | 492.4 | 492.2 | 493.8 | 515.9 | 447.6 | 441.9
2776.1 | 2651.1 | 489.6 | 481.6 | 505.1 | 481.6 | 492.4 | 492.2 | 493.8 | 515.8 | 447.4 | 441.9
2777.1 | 2652.1 | 488.9 | 481.5 | 504.9 | 481.5 | 492.5 | 492.2 | 493.8 | 515.8 | 447.3 | 441.9
2778.1 | 2653.1 | 488.1 | 481.4 | 504.8 | 481.4 | 492.4 | 492.2 | 493.7 | 515.4 | 447.4 | 441.9
2779.1 | 2654.1 | 487.3 | 481.3 | 504.6 | 481.3 | 492.4 | 492.2 | 493.7 | 515.2 | 446.9 | 441.9
2780.1 | 2655.1 | 486.6 | 481.2 | 504.4 | 481.2 | 492.5 | 492.2 | 493.7 | 515.1 | 447.1 | 441.9
2781.1 | 2656.1 | 485.8 | 481.1 | 504.2 | 481.1 | 492.5 | 492.2 | 493.7 | 515.1 | 447.1 | 441.9
2782.1 | 2657.1 | 485 | 480.9 | 504.1 | 480.9 | 492.4 | 492.2 | 493.7 | 515 | 447.4 | 441.9
2783.1 | 2658.1 | 484.3 | 480.8 | 503.9 | 480.8 | 492.4 | 492.2 | 493.6 | 515 | 447.1 | 441.9
2784.1 | 2659.1 | 483.6 | 480.7 | 503.7 | 480.7 | 492.5 | 492.2 | 493.6 | 514.9 | 447.2 | 441.8
2785.1 | 2660.1 | 482.8 | 480.6 | 503.5 | 480.6 | 492.4 | 492.2 | 493.6 | 514.8 | 447 | 441.8
2786.1 | 2661.1 | 482 | 480.4 | 503.4 | 480.5 | 492.4 | 492.2 | 493.6 | 514.7 | 447.7 | 441.8
2787.1 | 2662.1 | 481.3 | 480.3 | 503.1 | 480.3 | 492.4 | 492.2 | 493.5 | 514.9 | 447.4 | 441.8
2788.1 | 2663.1 | 480.6 | 480.2 | 503 | 480.2 | 492.4 | 492.2 | 493.5 | 514.9 | 447.4 | 441.8
2789.1 | 2664.1 | 479.9 | 480 | 502.8 | 480.1 | 492.3 | 492.2 | 493.5 | 514.9 | 447.6 | 441.7
2790.1 | 2665.1 | 479.1 | 479.9 | 502.6 | 479.9 | 492.3 | 492.2 | 493.4 | 515 | 447.2 | 441.7
2791.1 | 2666.1 | 478.4 | 479.8 | 502.4 | 479.8 | 492.4 | 492.2 | 493.4 | 515.2 | 447.3 | 441.7
2792.1 | 2667.1 | 477.7 | 479.7 | 502.2 | 479.7 | 492.3 | 492.2 | 493.4 | 515.3 | 447 | 441.7
2793.1 | 2668.1 | 477 | 479.5 | 502.1 | 479.5 | 492.3 | 492.1 | 493.3 | 515.3 | 447.2 | 441.6
2794.1 | 2669.1 | 476.3 | 479.4 | 501.8 | 479.4 | 492.3 | 492.2 | 493.3 | 515.3 | 447.4 | 441.6
2795.1 | 2670.1 | 475.6 | 479.2 | 501.6 | 479.3 | 492.3 | 492.1 | 493.2 | 515.3 | 447.4 | 441.6
2796.1 | 2671.1 | 474.8 | 479.1 | 501.5 | 479.1 | 492.2 | 492.1 | 493.2 | 515.2 | 447.2 | 441.5
2797.1 | 2672.1 | 474.1 | 479 | 501.3 | 479 | 492.2 | 492.1 | 493.1 | 515.3 | 447.8 | 441.5
2798.1 | 2673.1 | 473.4 | 478.8 | 501 | 478.9 | 492.2 | 492.1 | 493.1 | 515.4 | 447.7 | 441.4
2799.1 | 2674.1 | 472.7 | 478.7 | 500.8 | 478.7 | 492.2 | 492 | 493 | 515.6 | 447.2 | 441.4
2800.1 | 2675.1 | 472 | 478.5 | 500.7 | 478.5 | 492.1 | 492 | 493 | 515.8 | 447.5 | 441.4
2801.1 | 2676.1 | 471.2 | 478.4 | 500.4 | 478.4 | 492.1 | 492 | 492.9 | 515.7 | 447.2 | 441.4
2802.1 | 2677.1 | 470.5 | 478.2 | 500.2 | 478.3 | 492.1 | 491.9 | 492.9 | 515.5 | 447.1 | 441.3
2803.1 | 2678.1 | 469.8 | 478.1 | 500 | 478.1 | 492 | 491.9 | 492.8 | 515.5 | 447.1 | 441.3
2804.1 | 2679.1 | 469.1 | 477.9 | 499.9 | 478 | 492 | 491.9 | 492.8 | 515.5 | 447.1 | 441.3
2805.1 | 2680.1 | 468.3 | 477.8 | 499.7 | 477.8 | 492 | 491.9 | 492.7 | 515.3 | 447.4 | 441.2
2806.1 | 2681.1 | 467.6 | 477.6 | 499.5 | 477.7 | 491.9 | 491.8 | 492.7 | 515.3 | 447.7 | 441.1
2807.1 | 2682.1 | 466.9 | 477.5 | 499.3 | 477.5 | 491.9 | 491.8 | 492.6 | 515.4 | 447 | 441.1
2808.1 | 2683.1 | 466.2 | 477.3 | 499 | 477.4 | 491.9 | 491.8 | 492.6 | 515.4 | 447.3 | 441.1
2809.1 | 2684.1 | 465.5 | 477.2 | 498.8 | 477.2 | 491.9 | 491.8 | 492.5 | 515.2 | 447.4 | 441
2810.1 | 2685.1 | 464.8 | 477 | 498.7 | 477 | 491.8 | 491.7 | 492.5 | 514.9 | 446.9 | 441
2811.1 | 2686.1 | 464.1 | 476.8 | 498.5 | 476.9 | 491.7 | 491.7 | 492.4 | 514.8 | 447.6 | 440.9
2812.1 | 2687.1 | 463.4 | 476.7 | 498.2 | 476.8 | 491.7 | 491.6 | 492.3 | 514.8 | 447.5 | 440.9
2813.1 | 2688.1 | 462.7 | 476.5 | 498 | 476.6 | 491.7 | 491.6 | 492.3 | 514.8 | 446.9 | 440.9
2814.1 | 2689.1 | 462 | 476.3 | 497.8 | 476.4 | 491.6 | 491.5 | 492.2 | 514.7 | 447.3 | 440.8
2815.1 | 2690.1 | 461.3 | 476.2 | 497.6 | 476.3 | 491.6 | 491.5 | 492.2 | 514.4 | 447.3 | 440.8
2816.1 | 2691.1 | 460.6 | 476 | 497.4 | 476.1 | 491.5 | 491.5 | 492.1 | 514.3 | 447.4 | 440.7
2817.1 | 2692.1 | 459.9 | 475.8 | 497.2 | 475.9 | 491.4 | 491.4 | 492 | 514.3 | 447.2 | 440.7
2818.1 | 2693.1 | 459.2 | 475.7 | 496.9 | 475.8 | 491.4 | 491.4 | 491.9 | 514.2 | 447.1 | 440.6
2819.1 | 2694.1 | 458.5 | 475.5 | 496.7 | 475.6 | 491.4 | 491.4 | 491.8 | 514.2 | 447.3 | 440.5
2820.1 | 2695.1 | 457.9 | 475.3 | 496.5 | 475.5 | 491.3 | 491.3 | 491.8 | 514 | 447.3 | 440.5
2821.1 | 2696.1 | 457.2 | 475.2 | 496.3 | 475.3 | 491.2 | 491.3 | 491.7 | 513.8 | 447.1 | 440.4
2822.1 | 2697.1 | 456.5 | 475 | 496 | 475.1 | 491.2 | 491.2 | 491.6 | 513.8 | 447.1 | 440.4
2823.1 | 2698.1 | 455.9 | 474.9 | 495.7 | 475 | 491.2 | 491.2 | 491.5 | 513.9 | 447.1 | 440.3
2824.1 | 2699.1 | 455.2 | 474.7 | 495.6 | 474.8 | 491 | 491.1 | 491.4 | 514 | 446.9 | 440.3
2825.1 | 2700.1 | 454.5 | 474.5 | 495.3 | 474.6 | 491 | 491 | 491.4 | 513.9 | 446.9 | 440.2
2826.1 | 2701.1 | 453.8 | 474.3 | 495.1 | 474.5 | 491 | 491 | 491.3 | 514.1 | 447 | 440.1
2827.1 | 2702.1 | 453.2 | 474.1 | 494.9 | 474.3 | 490.9 | 490.9 | 491.2 | 514.2 | 446.9 | 440.1
2828.1 | 2703.1 | 452.6 | 473.9 | 494.7 | 474 | 490.8 | 490.8 | 491.1 | 514.1 | 447.3 | 440
2829.1 | 2704.1 | 451.9 | 473.8 | 494.3 | 473.9 | 490.8 | 490.8 | 491 | 513.9 | 447 | 439.9
2830.1 | 2705.1 | 451.3 | 473.6 | 494.1 | 473.7 | 490.7 | 490.7 | 490.9 | 513.8 | 446.9 | 439.9
2831.1 | 2706.1 | 450.6 | 473.4 | 493.9 | 473.5 | 490.6 | 490.7 | 490.8 | 513.9 | 447.3 | 439.8
2832.1 | 2707.1 | 450 | 473.2 | 493.6 | 473.3 | 490.6 | 490.6 | 490.7 | 514 | 446.8 | 439.7
2833.1 | 2708.1 | 449.4 | 473.1 | 493.4 | 473.2 | 490.5 | 490.5 | 490.6 | 514 | 446.8 | 439.7
2834.1 | 2709.1 | 448.7 | 472.9 | 493.2 | 473 | 490.4 | 490.5 | 490.5 | 513.9 | 446.8 | 439.6
2835.1 | 2710.1 | 448.1 | 472.7 | 493 | 472.8 | 490.3 | 490.4 | 490.5 | 513.7 | 446.6 | 439.6
2836.1 | 2711.1 | 447.4 | 472.5 | 492.7 | 472.6 | 490.3 | 490.3 | 490.3 | 513.8 | 446.7 | 439.5
2837.1 | 2712.1 | 446.8 | 472.3 | 492.4 | 472.4 | 490.2 | 490.3 | 490.2 | 513.6 | 446.8 | 439.4
2838.1 | 2713.1 | 446.2 | 472.1 | 492.2 | 472.2 | 490.1 | 490.2 | 490.2 | 513.3 | 446.5 | 439.4
2839.1 | 2714.1 | 445.5 | 471.9 | 492 | 472 | 490 | 490.1 | 490.1 | 513.2 | 447 | 439.3
2840.1 | 2715.1 | 444.9 | 471.8 | 491.7 | 471.9 | 490 | 490.1 | 490 | 513.4 | 446.9 | 439.2
2841.1 | 2716.1 | 444.3 | 471.6 | 491.5 | 471.7 | 489.9 | 490 | 489.9 | 513.5 | 446.5 | 439.2
2842.1 | 2717.1 | 443.7 | 471.3 | 491.3 | 471.4 | 489.8 | 489.9 | 489.8 | 513.5 | 446.9 | 439.1
2843.1 | 2718.1 | 443.1 | 471.2 | 490.9 | 471.3 | 489.8 | 489.9 | 489.7 | 513.2 | 446.6 | 439
2844.1 | 2719.1 | 442.4 | 471 | 490.7 | 471.1 | 489.7 | 489.8 | 489.6 | 513.1 | 446.4 | 439
2845.1 | 2720.1 | 441.8 | 470.8 | 490.6 | 470.9 | 489.5 | 489.7 | 489.5 | 512.9 | 446.4 | 438.9
2846.1 | 2721.1 | 441.2 | 470.6 | 490.2 | 470.7 | 489.5 | 489.6 | 489.4 | 512.7 | 446.3 | 438.8
2847.1 | 2722.1 | 440.6 | 470.4 | 489.9 | 470.6 | 489.4 | 489.5 | 489.2 | 512.6 | 446.5 | 438.7
2848.1 | 2723.1 | 440 | 470.2 | 489.7 | 470.4 | 489.3 | 489.4 | 489.1 | 512.4 | 446.7 | 438.6
2849.1 | 2724.1 | 439.4 | 470 | 489.5 | 470.1 | 489.2 | 489.3 | 489 | 512.4 | 446.2 | 438.6
2850.1 | 2725.1 | 438.8 | 469.8 | 489.2 | 469.9 | 489.2 | 489.3 | 488.9 | 512.3 | 446.6 | 438.5
2851.1 | 2726.1 | 438.2 | 469.6 | 489 | 469.8 | 489.1 | 489.2 | 488.8 | 512.2 | 446.6 | 438.4
2852.1 | 2727.1 | 437.6 | 469.4 | 488.8 | 469.5 | 488.9 | 489.1 | 488.7 | 512.2 | 446.1 | 438.4
2853.1 | 2728.1 | 437 | 469.2 | 488.5 | 469.3 | 488.9 | 489 | 488.6 | 512.2 | 446.5 | 438.3
2854.1 | 2729.1 | 436.4 | 469 | 488.2 | 469.2 | 488.8 | 488.9 | 488.5 | 511.9 | 446.4 | 438.2
2855.1 | 2730.1 | 435.8 | 468.8 | 488 | 469 | 488.7 | 488.8 | 488.4 | 511.7 | 446 | 438.1
2856.1 | 2731.1 | 435.2 | 468.6 | 487.8 | 468.8 | 488.5 | 488.7 | 488.2 | 511.7 | 446.4 | 438
2857.1 | 2732.1 | 434.6 | 468.4 | 487.5 | 468.6 | 488.5 | 488.7 | 488.1 | 511.6 | 446.4 | 437.9
2858.1 | 2733.1 | 434.1 | 468.2 | 487.2 | 468.4 | 488.4 | 488.6 | 488 | 511.6 | 446.3 | 437.8
2859.1 | 2734.1 | 433.5 | 468 | 486.9 | 468.1 | 488.3 | 488.4 | 487.9 | 511.3 | 446.3 | 437.8
2860.1 | 2735.1 | 432.9 | 467.8 | 486.7 | 467.9 | 488.2 | 488.4 | 487.7 | 511.1 | 446.2 | 437.7
2861.1 | 2736.1 | 432.3 | 467.6 | 486.4 | 467.7 | 488.1 | 488.3 | 487.6 | 510.9 | 446.1 | 437.6
2862.1 | 2737.1 | 431.7 | 467.4 | 486.1 | 467.5 | 488 | 488.2 | 487.5 | 510.8 | 446.1 | 437.5
2863.1 | 2738.1 | 431.1 | 467.2 | 485.9 | 467.3 | 487.8 | 488 | 487.3 | 510.5 | 445.5 | 437.5
2864.1 | 2739.1 | 430.6 | 467 | 485.6 | 467.1 | 487.8 | 488 | 487.2 | 510.3 | 445.6 | 437.3
2865.1 | 2740.1 | 430 | 466.8 | 485.3 | 466.9 | 487.7 | 487.9 | 487.1 | 510.2 | 445.7 | 437.3
2866.1 | 2741.1 | 429.4 | 466.6 | 485.1 | 466.7 | 487.5 | 487.7 | 486.9 | 510.3 | 445.5 | 437.2
2867.1 | 2742.1 | 428.9 | 466.4 | 484.8 | 466.5 | 487.5 | 487.6 | 486.8 | 510.1 | 445.5 | 437.1
2868.1 | 2743.1 | 428.3 | 466.2 | 484.5 | 466.3 | 487.4 | 487.6 | 486.7 | 509.9 | 445.5 | 437
2869.1 | 2744.1 | 427.7 | 465.9 | 484.3 | 466.1 | 487.2 | 487.4 | 486.5 | 509.8 | 445.3 | 436.9
2870.1 | 2745.1 | 427.2 | 465.7 | 484.1 | 465.9 | 487.1 | 487.3 | 486.4 | 509.9 | 445.6 | 436.8
2871.1 | 2746.1 | 426.6 | 465.5 | 483.7 | 465.7 | 487.1 | 487.2 | 486.3 | 509.9 | 445.4 | 436.7
2872.1 | 2747.1 | 426.1 | 465.3 | 483.5 | 465.5 | 486.9 | 487.1 | 486.1 | 509.9 | 445.1 | 436.6
2873.1 | 2748.1 | 425.5 | 465.1 | 483.3 | 465.2 | 486.8 | 487 | 486 | 510.1 | 445.5 | 436.5
2874.1 | 2749.1 | 424.9 | 464.9 | 483 | 465 | 486.7 | 486.9 | 485.8 | 510 | 445 | 436.4
2875.1 | 2750.1 | 424.3 | 464.7 | 482.7 | 464.8 | 486.6 | 486.8 | 485.7 | 509.9 | 444.9 | 436.3
2876.1 | 2751.1 | 423.7 | 464.5 | 482.4 | 464.6 | 486.4 | 486.7 | 485.6 | 510 | 444.9 | 436.3
2877.1 | 2752.1 | 423.1 | 464.2 | 482.2 | 464.4 | 486.3 | 486.6 | 485.4 | 509.7 | 444.7 | 436.2
2878.1 | 2753.1 | 422.6 | 464 | 481.8 | 464.2 | 486.2 | 486.5 | 485.3 | 509.2 | 444.7 | 436
2879.1 | 2754.1 | 422 | 463.8 | 481.6 | 463.9 | 486.1 | 486.3 | 485.2 | 508.9 | 444.7 | 436
2880.1 | 2755.1 | 421.4 | 463.6 | 481.4 | 463.7 | 485.9 | 486.2 | 485 | 508.7 | 444.5 | 435.9
2881.1 | 2756.1 | 420.9 | 463.4 | 481.1 | 463.5 | 485.8 | 486.1 | 484.9 | 508.5 | 444.9 | 435.8
2882.1 | 2757.1 | 420.3 | 463.2 | 480.8 | 463.3 | 485.8 | 486 | 484.7 | 508.4 | 444.7 | 435.6
2883.1 | 2758.1 | 419.8 | 462.9 | 480.5 | 463.1 | 485.6 | 485.9 | 484.6 | 508.2 | 444.4 | 435.6
2884.1 | 2759.1 | 419.2 | 462.7 | 480.3 | 462.8 | 485.4 | 485.8 | 484.5 | 508.1 | 444.8 | 435.5
2885.1 | 2760.1 | 418.7 | 462.5 | 480 | 462.7 | 485.4 | 485.7 | 484.3 | 508.1 | 444.4 | 435.4
2886.1 | 2761.1 | 418.2 | 462.3 | 479.7 | 462.4 | 485.3 | 485.5 | 484.2 | 507.9 | 444.4 | 435.3
2887.1 | 2762.1 | 417.6 | 462.1 | 479.5 | 462.2 | 485.1 | 485.4 | 484 | 507.7 | 444.1 | 435.2
2888.1 | 2763.1 | 417.1 | 461.9 | 479.2 | 462 | 485 | 485.3 | 483.9 | 507.7 | 444.1 | 435.1
2889.1 | 2764.1 | 416.5 | 461.6 | 478.9 | 461.8 | 484.9 | 485.2 | 483.7 | 507.3 | 444.3 | 435
2890.1 | 2765.1 | 416 | 461.4 | 478.7 | 461.6 | 484.7 | 485 | 483.6 | 507.2 | 444.4 | 434.8
2891.1 | 2766.1 | 415.5 | 461.2 | 478.4 | 461.3 | 484.5 | 484.9 | 483.4 | 507.2 | 443.7 | 434.8
2892.1 | 2767.1 | 414.9 | 461 | 478.1 | 461.1 | 484.5 | 484.8 | 483.3 | 507.3 | 444.2 | 434.6
2893.1 | 2768.1 | 414.4 | 460.8 | 477.8 | 460.9 | 484.3 | 484.7 | 483.1 | 507.2 | 444.1 | 434.5
2894.1 | 2769.1 | 413.8 | 460.5 | 477.6 | 460.7 | 484.2 | 484.5 | 483 | 507 | 443.7 | 434.4
2895.1 | 2770.1 | 413.3 | 460.3 | 477.3 | 460.5 | 484.1 | 484.4 | 482.8 | 506.7 | 444 | 434.3
2896.1 | 2771.1 | 412.8 | 460.1 | 477 | 460.2 | 484 | 484.3 | 482.6 | 506.6 | 443.8 | 434.2
2897.1 | 2772.1 | 412.3 | 459.9 | 476.7 | 460 | 483.8 | 484.1 | 482.5 | 506.6 | 443.6 | 434.1
2898.1 | 2773.1 | 411.7 | 459.6 | 476.5 | 459.8 | 483.6 | 484 | 482.3 | 506.5 | 443.8 | 434
2899.1 | 2774.1 | 411.2 | 459.4 | 476.2 | 459.6 | 483.5 | 483.9 | 482.2 | 506.3 | 443.8 | 433.8
2900.1 | 2775.1 | 410.7 | 459.2 | 475.9 | 459.4 | 483.4 | 483.7 | 482 | 506 | 443.7 | 433.7
2901.1 | 2776.1 | 410.2 | 458.9 | 475.7 | 459.1 | 483.2 | 483.6 | 481.8 | 505.8 | 443.6 | 433.6
2902.1 | 2777.1 | 409.6 | 458.7 | 475.4 | 458.9 | 483.1 | 483.5 | 481.7 | 505.8 | 443.4 | 433.5
2903.1 | 2778.1 | 409.1 | 458.5 | 475.1 | 458.7 | 483 | 483.3 | 481.5 | 505.7 | 443.3 | 433.4
2904.1 | 2779.1 | 408.6 | 458.3 | 474.8 | 458.5 | 482.8 | 483.2 | 481.4 | 505.5 | 443.2 | 433.3
2905.1 | 2780.1 | 408 | 458 | 474.6 | 458.3 | 482.7 | 483 | 481.2 | 505.1 | 442.7 | 433.2
2906.1 | 2781.1 | 407.5 | 457.8 | 474.2 | 458.1 | 482.6 | 482.9 | 481 | 504.9 | 442.9 | 433.1
2907.1 | 2782.1 | 407 | 457.6 | 473.9 | 457.8 | 482.4 | 482.8 | 480.8 | 504.9 | 442.8 | 432.9
2908.1 | 2783.1 | 406.5 | 457.4 | 473.7 | 457.6 | 482.2 | 482.6 | 480.7 | 504.9 | 442.5 | 432.8
2909.1 | 2784.1 | 406 | 457.2 | 473.4 | 457.3 | 482.1 | 482.5 | 480.5 | 504.9 | 442.6 | 432.7
2910.1 | 2785.1 | 405.5 | 456.9 | 473.1 | 457.1 | 482 | 482.4 | 480.3 | 504.8 | 442.6 | 432.6
2911.1 | 2786.1 | 405 | 456.7 | 472.8 | 456.9 | 481.8 | 482.2 | 480.2 | 504.6 | 442.4 | 432.5
2912.1 | 2787.1 | 404.5 | 456.5 | 472.6 | 456.7 | 481.6 | 482 | 480 | 504.3 | 442.7 | 432.4
2913.1 | 2788.1 | 404 | 456.3 | 472.3 | 456.5 | 481.6 | 481.9 | 479.8 | 504.2 | 442.4 | 432.2
2914.1 | 2789.1 | 403.5 | 456 | 472 | 456.2 | 481.4 | 481.8 | 479.6 | 504.1 | 442.3 | 432.1
2915.1 | 2790.1 | 403 | 455.8 | 471.8 | 456 | 481.2 | 481.6 | 479.5 | 503.7 | 442.4 | 432
2916.1 | 2791.1 | 402.5 | 455.6 | 471.4 | 455.8 | 481.1 | 481.5 | 479.3 | 503.4 | 442 | 431.8
2917.1 | 2792.1 | 402 | 455.4 | 471.2 | 455.5 | 481 | 481.3 | 479.1 | 503.1 | 441.8 | 431.7
2918.1 | 2793.1 | 401.5 | 455.1 | 470.9 | 455.3 | 480.8 | 481.2 | 478.9 | 503.1 | 441.8 | 431.6
2919.1 | 2794.1 | 401 | 454.9 | 470.6 | 455.1 | 480.6 | 481 | 478.7 | 502.9 | 441.5 | 431.5
2920.1 | 2795.1 | 400.5 | 454.7 | 470.3 | 454.8 | 480.5 | 480.9 | 478.6 | 502.8 | 441.5 | 431.4
2921.1 | 2796.1 | 400 | 454.4 | 470 | 454.6 | 480.4 | 480.7 | 478.4 | 502.6 | 441.6 | 431.2
2922.1 | 2797.1 | 399.5 | 454.2 | 469.8 | 454.3 | 480.1 | 480.5 | 478.2 | 502.6 | 441.1 | 431.1
2923.1 | 2798.1 | 399 | 454 | 469.5 | 454.1 | 480 | 480.4 | 478 | 502.5 | 441.6 | 431
2924.1 | 2799.1 | 398.5 | 453.7 | 469.2 | 453.9 | 479.9 | 480.3 | 477.9 | 502.4 | 441.4 | 430.8
2925.1 | 2800.1 | 398 | 453.5 | 468.9 | 453.7 | 479.7 | 480.1 | 477.7 | 502.5 | 441 | 430.7
2926.1 | 2801.1 | 397.5 | 453.2 | 468.7 | 453.4 | 479.5 | 479.9 | 477.5 | 502.5 | 441.4 | 430.6
2927.1 | 2802.1 | 397.1 | 453 | 468.3 | 453.2 | 479.4 | 479.8 | 477.3 | 502.4 | 441.1 | 430.5
2928.1 | 2803.1 | 396.6 | 452.8 | 468.1 | 453 | 479.3 | 479.7 | 477.2 | 502.4 | 440.9 | 430.4
2929.1 | 2804.1 | 396.1 | 452.6 | 467.8 | 452.7 | 479 | 479.5 | 477 | 502.2 | 440.7 | 430.3
2930.1 | 2805.1 | 395.6 | 452.3 | 467.5 | 452.5 | 478.9 | 479.3 | 476.8 | 501.8 | 440.6 | 430.1
2931.1 | 2806.1 | 395.1 | 452.1 | 467.2 | 452.3 | 478.8 | 479.2 | 476.6 | 501.5 | 440.7 | 430
2932.1 | 2807.1 | 394.6 | 451.9 | 467 | 452.1 | 478.6 | 479 | 476.5 | 501.2 | 440.8 | 429.9
2933.1 | 2808.1 | 394.2 | 451.6 | 466.8 | 451.8 | 478.4 | 478.8 | 476.3 | 501.1 | 440.3 | 429.7
2934.1 | 2809.1 | 393.7 | 451.4 | 466.4 | 451.6 | 478.3 | 478.7 | 476.1 | 501.1 | 440.5 | 429.6
2935.1 | 2810.1 | 393.2 | 451.2 | 466.1 | 451.3 | 478.1 | 478.5 | 475.9 | 501 | 440.5 | 429.4
2936.1 | 2811.1 | 392.8 | 450.9 | 465.9 | 451.1 | 477.9 | 478.3 | 475.7 | 500.8 | 440 | 429.4
2937.1 | 2812.1 | 392.3 | 450.7 | 465.6 | 450.9 | 477.8 | 478.2 | 475.5 | 500.5 | 440.3 | 429.2
2938.1 | 2813.1 | 391.8 | 450.5 | 465.3 | 450.7 | 477.6 | 478 | 475.3 | 500.4 | 440.1 | 429.1
2939.1 | 2814.1 | 391.4 | 450.2 | 465 | 450.4 | 477.4 | 477.9 | 475.2 | 500.3 | 439.8 | 429
2940.1 | 2815.1 | 390.9 | 450 | 464.8 | 450.2 | 477.2 | 477.7 | 475 | 500 | 440 | 428.8
2941.1 | 2816.1 | 390.4 | 449.8 | 464.4 | 450 | 477.1 | 477.5 | 474.8 | 500 | 440 | 428.6
2942.1 | 2817.1 | 389.9 | 449.6 | 464.2 | 449.7 | 477 | 477.4 | 474.6 | 499.9 | 439.9 | 428.5
2943.1 | 2818.1 | 389.5 | 449.3 | 463.9 | 449.5 | 476.7 | 477.2 | 474.4 | 499.6 | 439.8 | 428.4
2944.1 | 2819.1 | 389 | 449.1 | 463.6 | 449.2 | 476.6 | 477 | 474.2 | 499.4 | 439.5 | 428.3
2945.1 | 2820.1 | 388.5 | 448.8 | 463.3 | 449 | 476.5 | 476.9 | 474 | 499 | 439.4 | 428.1
2946.1 | 2821.1 | 388.1 | 448.6 | 463.1 | 448.8 | 476.3 | 476.7 | 473.8 | 498.7 | 439.4 | 428
2947.1 | 2822.1 | 387.6 | 448.4 | 462.8 | 448.5 | 476.1 | 476.5 | 473.6 | 498.5 | 438.7 | 427.9
2948.1 | 2823.1 | 387.1 | 448.2 | 462.5 | 448.3 | 476 | 476.4 | 473.4 | 498.4 | 438.8 | 427.8
2949.1 | 2824.1 | 386.7 | 447.9 | 462.2 | 448.1 | 475.8 | 476.2 | 473.2 | 498.3 | 438.7 | 427.6
2950.1 | 2825.1 | 386.2 | 447.7 | 462 | 447.8 | 475.5 | 476 | 473.1 | 498.1 | 438.5 | 427.5
2951.1 | 2826.1 | 385.7 | 447.4 | 461.7 | 447.6 | 475.4 | 475.9 | 472.9 | 497.8 | 438.6 | 427.3
2952.1 | 2827.1 | 385.2 | 447.2 | 461.3 | 447.3 | 475.3 | 475.7 | 472.7 | 497.6 | 438.5 | 427.2
2953.1 | 2828.1 | 384.8 | 447 | 461.1 | 447.1 | 475.1 | 475.6 | 472.5 | 497.4 | 438.3 | 427.1
2954.1 | 2829.1 | 384.3 | 446.7 | 460.9 | 446.8 | 474.8 | 475.4 | 472.3 | 497.3 | 438.6 | 426.9
2955.1 | 2830.1 | 383.8 | 446.5 | 460.5 | 446.6 | 474.7 | 475.2 | 472.1 | 497.2 | 438.3 | 426.8
2956.1 | 2831.1 | 383.4 | 446.3 | 460.2 | 446.4 | 474.6 | 475.1 | 471.9 | 497.2 | 438.1 | 426.6
2957.1 | 2832.1 | 382.9 | 446 | 460 | 446.1 | 474.3 | 474.9 | 471.7 | 497.2 | 438.3 | 426.5
2958.1 | 2833.1 | 382.5 | 445.8 | 459.7 | 445.9 | 474.2 | 474.7 | 471.5 | 497 | 437.8 | 426.3
2959.1 | 2834.1 | 382 | 445.6 | 459.4 | 445.7 | 474 | 474.5 | 471.3 | 496.6 | 437.8 | 426.2
2960.1 | 2835.1 | 381.5 | 445.3 | 459.1 | 445.4 | 473.8 | 474.4 | 471.1 | 496.5 | 437.6 | 426.1
2961.1 | 2836.1 | 381.1 | 445.1 | 458.9 | 445.2 | 473.6 | 474.2 | 470.9 | 496.4 | 437.4 | 425.9
2962.1 | 2837.1 | 380.7 | 444.9 | 458.5 | 445 | 473.5 | 474 | 470.7 | 496.2 | 437.4 | 425.8
2963.1 | 2838.1 | 380.2 | 444.6 | 458.3 | 444.7 | 473.3 | 473.8 | 470.5 | 496.1 | 437.3 | 425.6
2964.1 | 2839.1 | 379.8 | 444.4 | 458.1 | 444.5 | 473.1 | 473.6 | 470.3 | 495.8 | 437.1 | 425.5
2965.1 | 2840.1 | 379.4 | 444.1 | 457.7 | 444.2 | 472.9 | 473.5 | 470.1 | 495.4 | 437.3 | 425.4
2966.1 | 2841.1 | 378.9 | 443.9 | 457.5 | 444 | 472.8 | 473.3 | 469.9 | 495.2 | 437.1 | 425.2
2967.1 | 2842.1 | 378.5 | 443.7 | 457.2 | 443.7 | 472.6 | 473.1 | 469.7 | 495.3 | 436.8 | 425.1
2968.1 | 2843.1 | 378.1 | 443.4 | 457 | 443.5 | 472.3 | 472.9 | 469.5 | 495.2 | 437 | 424.9
2969.1 | 2844.1 | 377.7 | 443.2 | 456.6 | 443.3 | 472.2 | 472.8 | 469.3 | 495.1 | 436.7 | 424.8
2970.1 | 2845.1 | 377.2 | 443 | 456.3 | 443.1 | 472 | 472.6 | 469.1 | 494.8 | 436.5 | 424.6
2971.1 | 2846.1 | 376.8 | 442.7 | 456.1 | 442.8 | 471.8 | 472.4 | 468.9 | 494.7 | 436.3 | 424.5
2972.1 | 2847.1 | 376.4 | 442.5 | 455.8 | 442.6 | 471.6 | 472.2 | 468.7 | 494.6 | 436.1 | 424.4
2973.1 | 2848.1 | 376 | 442.3 | 455.5 | 442.4 | 471.5 | 472 | 468.5 | 494.3 | 436.3 | 424.2
2974.1 | 2849.1 | 375.6 | 442 | 455.2 | 442.1 | 471.3 | 471.8 | 468.3 | 494.3 | 436.3 | 424
2975.1 | 2850.1 | 375.2 | 441.7 | 455 | 441.9 | 471.1 | 471.6 | 468.1 | 494.2 | 435.7 | 423.9
2976.1 | 2851.1 | 374.7 | 441.5 | 454.7 | 441.6 | 471 | 471.5 | 467.9 | 494 | 436 | 423.7
2977.1 | 2852.1 | 374.3 | 441.3 | 454.4 | 441.4 | 470.8 | 471.3 | 467.7 | 493.9 | 435.9 | 423.6
2978.1 | 2853.1 | 373.9 | 441 | 454.2 | 441.2 | 470.5 | 471.1 | 467.5 | 493.8 | 435.4 | 423.5
2979.1 | 2854.1 | 373.5 | 440.8 | 453.9 | 440.9 | 470.4 | 470.9 | 467.3 | 493.6 | 435.7 | 423.3
2980.1 | 2855.1 | 373.1 | 440.6 | 453.6 | 440.7 | 470.2 | 470.8 | 467.1 | 493.3 | 435.4 | 423.1
2981.1 | 2856.1 | 372.7 | 440.3 | 453.3 | 440.4 | 470 | 470.6 | 466.9 | 493 | 435 | 423
2982.1 | 2857.1 | 372.2 | 440.1 | 453 | 440.2 | 469.8 | 470.4 | 466.7 | 492.9 | 435.3 | 422.8
2983.1 | 2858.1 | 371.8 | 439.9 | 452.7 | 440 | 469.7 | 470.2 | 466.5 | 492.7 | 435.2 | 422.7
2984.1 | 2859.1 | 371.4 | 439.7 | 452.4 | 439.7 | 469.5 | 470 | 466.3 | 492.4 | 435.1 | 422.5
2985.1 | 2860.1 | 371 | 439.4 | 452.2 | 439.5 | 469.2 | 469.8 | 466.1 | 492.1 | 435 | 422.4
2986.1 | 2861.1 | 370.6 | 439.1 | 451.9 | 439.2 | 469.1 | 469.6 | 465.9 | 491.9 | 434.7 | 422.2
2987.1 | 2862.1 | 370.2 | 438.9 | 451.6 | 439 | 468.9 | 469.5 | 465.7 | 491.7 | 434.6 | 422.1
2988.1 | 2863.1 | 369.8 | 438.7 | 451.3 | 438.8 | 468.7 | 469.3 | 465.5 | 491.4 | 434.4 | 421.9
2989.1 | 2864.1 | 369.3 | 438.4 | 451.1 | 438.5 | 468.5 | 469.1 | 465.3 | 491 | 434 | 421.8
2990.1 | 2865.1 | 368.9 | 438.2 | 450.8 | 438.3 | 468.4 | 468.9 | 465.1 | 490.7 | 434.1 | 421.7
2991.1 | 2866.1 | 368.5 | 438 | 450.5 | 438.1 | 468.2 | 468.8 | 464.8 | 490.8 | 433.8 | 421.5
2992.1 | 2867.1 | 368.1 | 437.7 | 450.3 | 437.8 | 467.9 | 468.5 | 464.6 | 490.7 | 433.6 | 421.4
2993.1 | 2868.1 | 367.6 | 437.5 | 449.9 | 437.6 | 467.7 | 468.4 | 464.4 | 490.7 | 433.6 | 421.2
2994.1 | 2869.1 | 367.2 | 437.2 | 449.6 | 437.3 | 467.6 | 468.2 | 464.2 | 490.5 | 433.4 | 421.1
2995.1 | 2870.1 | 366.8 | 437 | 449.4 | 437.1 | 467.4 | 468 | 464 | 490.4 | 433.3 | 420.9
2996.1 | 2871.1 | 366.4 | 436.7 | 449.1 | 436.8 | 467.1 | 467.8 | 463.8 | 490.1 | 433.6 | 420.7
2997.1 | 2872.1 | 366 | 436.5 | 448.8 | 436.6 | 467 | 467.6 | 463.6 | 490 | 433.1 | 420.6
2998.1 | 2873.1 | 365.6 | 436.3 | 448.5 | 436.4 | 466.8 | 467.4 | 463.4 | 489.7 | 433 | 420.4
2999.1 | 2874.1 | 365.2 | 436 | 448.3 | 436.1 | 466.6 | 467.2 | 463.1 | 489.6 | 433.2 | 420.2
3000.1 | 2875.1 | 364.8 | 435.8 | 448 | 435.9 | 466.4 | 467 | 462.9 | 489.5 | 432.6 | 420.1
3001.1 | 2876.1 | 364.4 | 435.5 | 447.7 | 435.6 | 466.2 | 466.8 | 462.7 | 489.3 | 432.7 | 419.9
3002.1 | 2877.1 | 364 | 435.3 | 447.5 | 435.4 | 466 | 466.6 | 462.5 | 489.1 | 432.5 | 419.8
3003.1 | 2878.1 | 363.6 | 435 | 447.2 | 435.1 | 465.8 | 466.4 | 462.3 | 489.1 | 432.1 | 419.6
3004.1 | 2879.1 | 363.2 | 434.8 | 446.9 | 434.9 | 465.6 | 466.2 | 462 | 489 | 432.2 | 419.4
3005.1 | 2880.1 | 362.8 | 434.6 | 446.6 | 434.7 | 465.4 | 466 | 461.8 | 488.8 | 432 | 419.2
3006.1 | 2881.1 | 362.4 | 434.3 | 446.4 | 434.4 | 465.2 | 465.8 | 461.6 | 488.5 | 431.9 | 419.1
3007.1 | 2882.1 | 362 | 434.1 | 446.1 | 434.2 | 465 | 465.6 | 461.4 | 488.5 | 432.1 | 418.9
3008.1 | 2883.1 | 361.6 | 433.9 | 445.8 | 433.9 | 464.8 | 465.4 | 461.2 | 488.4 | 431.9 | 418.7
3009.1 | 2884.1 | 361.2 | 433.6 | 445.5 | 433.7 | 464.6 | 465.2 | 461 | 488 | 431.6 | 418.6
3010.1 | 2885.1 | 360.8 | 433.4 | 445.3 | 433.4 | 464.4 | 465 | 460.8 | 487.8 | 431.7 | 418.4
3011.1 | 2886.1 | 360.4 | 433.2 | 444.9 | 433.2 | 464.3 | 464.8 | 460.6 | 487.7 | 431.6 | 418.2
3012.1 | 2887.1 | 360 | 432.9 | 444.7 | 433 | 464 | 464.6 | 460.4 | 487.7 | 431.4 | 418.1
3013.1 | 2888.1 | 359.7 | 432.7 | 444.4 | 432.7 | 463.8 | 464.4 | 460.1 | 487.5 | 431.3 | 417.9
3014.1 | 2889.1 | 359.2 | 432.4 | 444.1 | 432.5 | 463.6 | 464.2 | 459.9 | 487.3 | 431.2 | 417.7
3015.1 | 2890.1 | 358.9 | 432.2 | 443.8 | 432.2 | 463.4 | 464.1 | 459.7 | 487.2 | 431 | 417.6
3016.1 | 2891.1 | 358.5 | 432 | 443.6 | 432 | 463.2 | 463.9 | 459.5 | 486.8 | 430.9 | 417.4
3017.1 | 2892.1 | 358.1 | 431.7 | 443.4 | 431.7 | 463 | 463.6 | 459.3 | 486.5 | 430.7 | 417.3
3018.1 | 2893.1 | 357.7 | 431.5 | 443 | 431.5 | 462.9 | 463.5 | 459.1 | 486.3 | 430.6 | 417.1
3019.1 | 2894.1 | 357.3 | 431.3 | 442.8 | 431.3 | 462.7 | 463.3 | 458.9 | 486.1 | 430.5 | 416.9
3020.1 | 2895.1 | 356.9 | 431 | 442.5 | 431 | 462.4 | 463 | 458.7 | 485.8 | 430.3 | 416.8
3021.1 | 2896.1 | 356.6 | 430.8 | 442.2 | 430.8 | 462.2 | 462.8 | 458.4 | 485.6 | 430.2 | 416.6
3022.1 | 2897.1 | 356.2 | 430.6 | 441.9 | 430.5 | 462 | 462.6 | 458.2 | 485.4 | 430 | 416.4
3023.1 | 2898.1 | 355.8 | 430.3 | 441.7 | 430.3 | 461.8 | 462.4 | 458 | 485 | 429.9 | 416.3
3024.1 | 2899.1 | 355.4 | 430 | 441.4 | 430 | 461.6 | 462.2 | 457.8 | 484.7 | 429.8 | 416.1
3025.1 | 2900.1 | 355 | 429.8 | 441.1 | 429.8 | 461.4 | 462 | 457.6 | 484.6 | 429.6 | 415.9
3026.1 | 2901.1 | 354.6 | 429.6 | 440.8 | 429.6 | 461.2 | 461.8 | 457.3 | 484.7 | 429.5 | 415.7
3027.1 | 2902.1 | 354.2 | 429.3 | 440.6 | 429.3 | 461 | 461.6 | 457.1 | 484.4 | 429.3 | 415.6
3028.1 | 2903.1 | 353.9 | 429.1 | 440.3 | 429.1 | 460.8 | 461.4 | 456.9 | 484.2 | 429.1 | 415.4
3029.1 | 2904.1 | 353.5 | 428.9 | 440 | 428.8 | 460.6 | 461.2 | 456.7 | 484 | 428.9 | 415.2
3030.1 | 2905.1 | 353.1 | 428.6 | 439.8 | 428.6 | 460.4 | 461 | 456.5 | 484 | 428.7 | 415.1
3031.1 | 2906.1 | 352.7 | 428.4 | 439.5 | 428.3 | 460.1 | 460.8 | 456.2 | 483.9 | 428.6 | 414.9
3032.1 | 2907.1 | 352.3 | 428.2 | 439.2 | 428.1 | 460 | 460.6 | 456 | 483.7 | 428.5 | 414.7
3033.1 | 2908.1 | 351.9 | 427.9 | 438.9 | 427.9 | 459.8 | 460.4 | 455.8 | 483.4 | 428.3 | 414.6
3034.1 | 2909.1 | 351.5 | 427.7 | 438.7 | 427.6 | 459.6 | 460.2 | 455.6 | 483.2 | 428 | 414.4
3035.1 | 2910.1 | 351.2 | 427.4 | 438.4 | 427.4 | 459.4 | 460 | 455.4 | 483.2 | 427.8 | 414.2
3036.1 | 2911.1 | 350.8 | 427.2 | 438.1 | 427.2 | 459.2 | 459.8 | 455.1 | 482.9 | 427.8 | 414.1
3037.1 | 2912.1 | 350.4 | 427 | 437.8 | 426.9 | 459 | 459.6 | 454.9 | 482.7 | 427.6 | 413.9
3038.1 | 2913.1 | 350 | 426.7 | 437.6 | 426.7 | 458.7 | 459.3 | 454.7 | 482.5 | 427.7 | 413.7
3039.1 | 2914.1 | 349.7 | 426.5 | 437.3 | 426.4 | 458.6 | 459.2 | 454.5 | 482.4 | 427.4 | 413.5
3040.1 | 2915.1 | 349.3 | 426.3 | 437 | 426.2 | 458.4 | 458.9 | 454.3 | 482.2 | 427.2 | 413.4
3041.1 | 2916.1 | 348.9 | 426 | 436.8 | 425.9 | 458.1 | 458.7 | 454 | 482 | 427.3 | 413.2
3042.1 | 2917.1 | 348.5 | 425.8 | 436.5 | 425.7 | 457.9 | 458.5 | 453.8 | 481.8 | 426.9 | 413
3043.1 | 2918.1 | 348.2 | 425.6 | 436.2 | 425.5 | 457.8 | 458.3 | 453.6 | 481.7 | 426.8 | 412.9
3044.1 | 2919.1 | 347.8 | 425.3 | 435.9 | 425.2 | 457.5 | 458.1 | 453.4 | 481.6 | 426.6 | 412.7
3045.1 | 2920.1 | 347.4 | 425.1 | 435.7 | 425 | 457.3 | 457.9 | 453.2 | 481.4 | 426.4 | 412.5
3046.1 | 2921.1 | 347.1 | 424.9 | 435.4 | 424.8 | 457.2 | 457.7 | 452.9 | 481.1 | 426.4 | 412.3
3047.1 | 2922.1 | 346.7 | 424.6 | 435.1 | 424.5 | 457 | 457.5 | 452.7 | 480.9 | 426.2 | 412.2
3048.1 | 2923.1 | 346.3 | 424.4 | 434.9 | 424.3 | 456.7 | 457.3 | 452.5 | 480.8 | 426 | 412
3049.1 | 2924.1 | 346 | 424.1 | 434.6 | 424 | 456.5 | 457.1 | 452.3 | 480.8 | 426.1 | 411.8
3050.1 | 2925.1 | 345.6 | 423.9 | 434.3 | 423.8 | 456.3 | 456.9 | 452 | 480.7 | 425.9 | 411.6
3051.1 | 2926.1 | 345.2 | 423.7 | 434.1 | 423.5 | 456.1 | 456.7 | 451.8 | 480.5 | 425.6 | 411.5
3052.1 | 2927.1 | 344.9 | 423.4 | 433.8 | 423.3 | 455.9 | 456.5 | 451.6 | 480.3 | 425.7 | 411.3
3053.1 | 2928.1 | 344.5 | 423.2 | 433.5 | 423.1 | 455.7 | 456.3 | 451.4 | 480.1 | 425.4 | 411.1
3054.1 | 2929.1 | 344.2 | 423 | 433.2 | 422.8 | 455.5 | 456.1 | 451.2 | 479.8 | 425.1 | 411
3055.1 | 2930.1 | 343.8 | 422.7 | 433 | 422.6 | 455.2 | 455.8 | 451 | 479.7 | 424.9 | 410.8
3056.1 | 2931.1 | 343.4 | 422.5 | 432.7 | 422.3 | 455 | 455.6 | 450.7 | 479.5 | 424.8 | 410.6
3057.1 | 2932.1 | 343.1 | 422.3 | 432.4 | 422.1 | 454.9 | 455.4 | 450.5 | 479.5 | 424.8 | 410.4
3058.1 | 2933.1 | 342.7 | 422 | 432.2 | 421.9 | 454.6 | 455.2 | 450.3 | 479.4 | 424.8 | 410.3
3059.1 | 2934.1 | 342.4 | 421.8 | 431.9 | 421.6 | 454.4 | 455 | 450.1 | 479 | 424.5 | 410.1
3060.1 | 2935.1 | 342.1 | 421.5 | 431.6 | 421.4 | 454.2 | 454.8 | 449.8 | 478.8 | 424.4 | 409.9
3061.1 | 2936.1 | 341.7 | 421.3 | 431.4 | 421.2 | 454 | 454.6 | 449.6 | 478.6 | 424.3 | 409.7
3062.1 | 2937.1 | 341.4 | 421 | 431.1 | 420.9 | 453.8 | 454.4 | 449.4 | 478.4 | 423.9 | 409.6
3063.1 | 2938.1 | 341.1 | 420.8 | 430.8 | 420.7 | 453.6 | 454.2 | 449.2 | 477.9 | 424 | 409.4
3064.1 | 2939.1 | 340.7 | 420.6 | 430.5 | 420.5 | 453.4 | 454 | 449 | 477.5 | 423.7 | 409.2
3065.1 | 2940.1 | 340.4 | 420.4 | 430.3 | 420.2 | 453.2 | 453.8 | 448.7 | 477 | 423.5 | 409.1
3066.1 | 2941.1 | 340.1 | 420.1 | 430.1 | 419.9 | 452.9 | 453.5 | 448.5 | 476.7 | 423.5 | 408.9
3067.1 | 2942.1 | 339.7 | 419.9 | 429.7 | 419.7 | 452.8 | 453.4 | 448.3 | 476.5 | 423.4 | 408.7
3068.1 | 2943.1 | 339.4 | 419.7 | 429.5 | 419.5 | 452.6 | 453.2 | 448.1 | 476.1 | 423.2 | 408.5
3069.1 | 2944.1 | 339.1 | 419.4 | 429.3 | 419.2 | 452.3 | 452.9 | 447.8 | 476 | 423.1 | 408.3
3070.1 | 2945.1 | 338.7 | 419.2 | 429 | 419 | 452.1 | 452.7 | 447.6 | 475.7 | 422.8 | 408.1
3071.1 | 2946.1 | 338.4 | 418.9 | 428.7 | 418.8 | 451.9 | 452.5 | 447.4 | 475.5 | 422.6 | 407.9
3072.1 | 2947.1 | 338 | 418.7 | 428.4 | 418.5 | 451.7 | 452.3 | 447.2 | 475.3 | 422.4 | 407.8
3073.1 | 2948.1 | 337.7 | 418.4 | 428.2 | 418.3 | 451.4 | 452.1 | 447 | 475.2 | 422.1 | 407.6
3074.1 | 2949.1 | 337.3 | 418.2 | 427.9 | 418.1 | 451.3 | 451.9 | 446.7 | 475 | 422.1 | 407.4
3075.1 | 2950.1 | 337 | 418 | 427.6 | 417.8 | 451.1 | 451.7 | 446.5 | 474.8 | 422.1 | 407.2
3076.1 | 2951.1 | 336.6 | 417.7 | 427.4 | 417.6 | 450.8 | 451.5 | 446.3 | 474.7 | 421.7 | 407.1
3077.1 | 2952.1 | 336.3 | 417.5 | 427.1 | 417.3 | 450.6 | 451.3 | 446.1 | 474.5 | 421.6 | 406.9
3078.1 | 2953.1 | 335.9 | 417.3 | 426.8 | 417.1 | 450.4 | 451.1 | 445.8 | 474.5 | 421.5 | 406.7
3079.1 | 2954.1 | 335.6 | 417.1 | 426.6 | 416.9 | 450.2 | 450.9 | 445.6 | 474.2 | 421.3 | 406.6
3080.1 | 2955.1 | 335.3 | 416.8 | 426.4 | 416.6 | 450 | 450.6 | 445.4 | 473.9 | 421.4 | 406.4
3081.1 | 2956.1 | 334.9 | 416.6 | 426 | 416.4 | 449.8 | 450.5 | 445.2 | 473.6 | 421.1 | 406.2
3082.1 | 2957.1 | 334.6 | 416.4 | 425.8 | 416.2 | 449.6 | 450.2 | 445 | 473.3 | 421 | 406
3083.1 | 2958.1 | 334.2 | 416.1 | 425.6 | 415.9 | 449.4 | 450 | 444.7 | 473.1 | 421 | 405.8
3084.1 | 2959.1 | 333.9 | 415.9 | 425.3 | 415.7 | 449.2 | 449.8 | 444.5 | 472.9 | 420.6 | 405.7
3085.1 | 2960.1 | 333.6 | 415.7 | 425 | 415.4 | 449 | 449.6 | 444.3 | 472.7 | 420.5 | 405.5
3086.1 | 2961.1 | 333.2 | 415.4 | 424.8 | 415.2 | 448.8 | 449.4 | 444.1 | 472.7 | 420.3 | 405.3
3087.1 | 2962.1 | 332.9 | 415.2 | 424.5 | 414.9 | 448.5 | 449.2 | 443.8 | 472.5 | 420 | 405.1
3088.1 | 2963.1 | 332.5 | 415 | 424.2 | 414.7 | 448.4 | 449 | 443.6 | 472.3 | 420 | 405
3089.1 | 2964.1 | 332.2 | 414.7 | 423.9 | 414.5 | 448.1 | 448.8 | 443.4 | 472 | 419.7 | 404.8
3090.1 | 2965.1 | 331.9 | 414.5 | 423.7 | 414.3 | 447.9 | 448.5 | 443.2 | 471.8 | 419.6 | 404.6
3091.1 | 2966.1 | 331.5 | 414.2 | 423.5 | 414 | 447.7 | 448.3 | 442.9 | 471.7 | 419.7 | 404.4
3092.1 | 2967.1 | 331.2 | 414 | 423.1 | 413.8 | 447.5 | 448.1 | 442.7 | 471.5 | 419.5 | 404.2
3093.1 | 2968.1 | 330.9 | 413.8 | 422.9 | 413.5 | 447.3 | 447.9 | 442.5 | 471.4 | 419.1 | 404.1
3094.1 | 2969.1 | 330.6 | 413.5 | 422.7 | 413.3 | 447 | 447.7 | 442.3 | 471.4 | 419.2 | 403.9
3095.1 | 2970.1 | 330.2 | 413.3 | 422.4 | 413.1 | 446.9 | 447.5 | 442.1 | 471 | 419 | 403.7
3096.1 | 2971.1 | 329.9 | 413.1 | 422.1 | 412.8 | 446.6 | 447.3 | 441.8 | 470.6 | 418.7 | 403.5
3097.1 | 2972.1 | 329.6 | 412.8 | 421.9 | 412.6 | 446.4 | 447 | 441.6 | 470.4 | 418.4 | 403.4
3098.1 | 2973.1 | 329.2 | 412.6 | 421.6 | 412.3 | 446.2 | 446.8 | 441.4 | 470.5 | 418.4 | 403.2
3099.1 | 2974.1 | 328.9 | 412.4 | 421.3 | 412.1 | 446 | 446.6 | 441.2 | 470.3 | 418.4 | 403
3100.1 | 2975.1 | 328.6 | 412.2 | 421.1 | 411.9 | 445.8 | 446.4 | 440.9 | 470.2 | 418.3 | 402.8
3101.1 | 2976.1 | 328.3 | 411.9 | 420.9 | 411.7 | 445.5 | 446.2 | 440.7 | 469.9 | 417.8 | 402.7
3102.1 | 2977.1 | 327.9 | 411.7 | 420.5 | 411.4 | 445.4 | 446 | 440.5 | 469.8 | 417.9 | 402.5
3103.1 | 2978.1 | 327.6 | 411.5 | 420.3 | 411.2 | 445.2 | 445.8 | 440.2 | 469.6 | 417.8 | 402.3
3104.1 | 2979.1 | 327.2 | 411.2 | 420.1 | 410.9 | 444.9 | 445.6 | 440 | 469.2 | 417.5 | 402.1
3105.1 | 2980.1 | 326.9 | 411 | 419.8 | 410.7 | 444.7 | 445.3 | 439.8 | 468.8 | 417.5 | 401.9
3106.1 | 2981.1 | 326.6 | 410.8 | 419.5 | 410.5 | 444.5 | 445.1 | 439.6 | 468.6 | 417.3 | 401.7
3107.1 | 2982.1 | 326.3 | 410.5 | 419.3 | 410.3 | 444.3 | 444.9 | 439.3 | 468.3 | 416.9 | 401.6
3108.1 | 2983.1 | 326 | 410.3 | 419.1 | 410 | 444 | 444.7 | 439.1 | 467.9 | 417 | 401.4
3109.1 | 2984.1 | 325.6 | 410.1 | 418.7 | 409.8 | 443.9 | 444.5 | 438.9 | 467.9 | 416.9 | 401.2
3110.1 | 2985.1 | 325.3 | 409.8 | 418.5 | 409.5 | 443.7 | 444.3 | 438.7 | 467.7 | 416.7 | 401
3111.1 | 2986.1 | 325 | 409.6 | 418.3 | 409.3 | 443.4 | 444.1 | 438.5 | 467.4 | 416.5 | 400.8
3112.1 | 2987.1 | 324.7 | 409.4 | 418 | 409.1 | 443.2 | 443.9 | 438.2 | 467 | 416.2 | 400.6
3113.1 | 2988.1 | 324.4 | 409.2 | 417.7 | 408.8 | 443 | 443.6 | 438 | 466.7 | 416 | 400.5
3114.1 | 2989.1 | 324.1 | 408.9 | 417.5 | 408.6 | 442.8 | 443.4 | 437.8 | 466.5 | 415.8 | 400.3
3115.1 | 2990.1 | 323.7 | 408.7 | 417.2 | 408.3 | 442.5 | 443.2 | 437.5 | 466.3 | 415.5 | 400.1
3116.1 | 2991.1 | 323.4 | 408.5 | 416.9 | 408.1 | 442.4 | 443 | 437.3 | 466.3 | 415.4 | 399.9
3117.1 | 2992.1 | 323.1 | 408.2 | 416.7 | 407.9 | 442.1 | 442.8 | 437.1 | 466.1 | 415.2 | 399.7
3118.1 | 2993.1 | 322.8 | 408 | 416.5 | 407.7 | 441.9 | 442.6 | 436.9 | 465.8 | 415 | 399.5
3119.1 | 2994.1 | 322.5 | 407.8 | 416.2 | 407.5 | 441.7 | 442.4 | 436.6 | 465.5 | 414.8 | 399.4
3120.1 | 2995.1 | 322.2 | 407.5 | 416 | 407.2 | 441.3 | 442.1 | 436.4 | 465.1 | 414.8 | 399.2
3121.1 | 2996.1 | 321.9 | 407.1 | 416 | 406.9 | 440.6 | 441.8 | 436.2 | 465 | 414.7 | 399.1
3122.1 | 2997.1 | 321.6 | 407.1 | 415.5 | 406.7 | 441 | 441.7 | 436 | 464.6 | 414.6 | 398.8
3123.1 | 2998.1 | 321.3 | 406.9 | 415.2 | 406.5 | 440.8 | 441.5 | 435.7 | 464.3 | 414.4 | 398.6
3124.1 | 2999.1 | 321 | 406.6 | 414.9 | 406.3 | 440.6 | 441.3 | 435.5 | 464.2 | 414.1 | 398.4
3125.1 | 3000.1 | 320.7 | 406.4 | 414.7 | 406 | 440.3 | 441.1 | 435.3 | 464 | 414.1 | 398.2
3126.1 | 3001.1 | 320.4 | 406.2 | 414.4 | 405.8 | 440.1 | 440.9 | 435.1 | 463.7 | 413.8 | 398
3127.1 | 3002.1 | 320.1 | 406 | 414.1 | 405.6 | 440 | 440.7 | 434.8 | 463.5 | 413.6 | 397.8
3128.1 | 3003.1 | 319.8 | 405.7 | 413.9 | 405.3 | 439.7 | 440.4 | 434.6 | 463.4 | 413.3 | 397.7
3129.1 | 3004.1 | 319.5 | 405.5 | 413.7 | 405.1 | 439.5 | 440.2 | 434.4 | 463.3 | 413.4 | 397.5
3130.1 | 3005.1 | 319.2 | 405.3 | 413.4 | 404.9 | 439.3 | 440 | 434.1 | 463.1 | 413.2 | 397.3
3131.1 | 3006.1 | 318.9 | 405 | 413.1 | 404.6 | 439.1 | 439.8 | 433.9 | 463.1 | 413 | 397.1
3132.1 | 3007.1 | 318.6 | 404.8 | 412.9 | 404.4 | 438.8 | 439.6 | 433.7 | 462.9 | 412.7 | 396.9
3133.1 | 3008.1 | 318.3 | 404.9 | 412 | 404.4 | 439.3 | 439.6 | 433.4 | 462.5 | 412.7 | 396.6
3134.1 | 3009.1 | 318 | 404.7 | 411.6 | 404.3 | 439.3 | 439.4 | 433.2 | 462.5 | 412.5 | 396.4
3135.1 | 3010.1 | 317.7 | 404.5 | 411.4 | 404 | 439.1 | 439.2 | 432.9 | 462.2 | 412.2 | 396.2
3136.1 | 3011.1 | 317.4 | 404.2 | 411.2 | 403.7 | 438.8 | 438.9 | 432.7 | 462.1 | 412.2 | 396
3137.1 | 3012.1 | 317.1 | 404 | 410.9 | 403.5 | 438.7 | 438.8 | 432.5 | 462 | 411.8 | 395.8
3138.1 | 3013.1 | 316.8 | 403.8 | 410.6 | 403.3 | 438.5 | 438.5 | 432.3 | 461.8 | 411.5 | 395.7
3139.1 | 3014.1 | 316.5 | 403.6 | 410.4 | 403.1 | 438.2 | 438.3 | 432.1 | 461.6 | 411.2 | 395.5
3140.1 | 3015.1 | 316.2 | 403.3 | 410.2 | 402.8 | 438 | 438.1 | 431.8 | 461.5 | 411.3 | 395.3
3141.1 | 3016.1 | 315.9 | 403.2 | 409.9 | 402.6 | 437.8 | 437.9 | 431.6 | 461.1 | 411.3 | 395.1
3142.1 | 3017.1 | 315.6 | 402.9 | 409.7 | 402.4 | 437.6 | 437.6 | 431.4 | 460.8 | 411.2 | 394.9
3143.1 | 3018.1 | 315.3 | 402.6 | 409.5 | 402.1 | 437.3 | 437.4 | 431.2 | 460.7 | 410.5 | 394.8
3144.1 | 3019.1 | 315 | 402.4 | 409.2 | 401.9 | 437.1 | 437.2 | 430.9 | 460.4 | 410.8 | 394.5
3145.1 | 3020.1 | 314.7 | 402.2 | 408.9 | 401.7 | 437 | 437 | 430.7 | 460.3 | 410.7 | 394.3
3146.1 | 3021.1 | 314.4 | 402 | 408.7 | 401.4 | 436.7 | 436.7 | 430.5 | 460 | 410.1 | 394.2
3147.1 | 3022.1 | 314.1 | 401.8 | 408.5 | 401.2 | 436.5 | 436.5 | 430.3 | 459.7 | 410.4 | 394
3148.1 | 3023.1 | 313.8 | 401.6 | 408.1 | 401 | 436.3 | 436.3 | 430 | 459.6 | 410.2 | 393.8
3149.1 | 3024.1 | 313.6 | 401.3 | 407.9 | 400.7 | 436.1 | 436.1 | 429.8 | 459.3 | 409.6 | 393.6
3150.1 | 3025.1 | 313.3 | 401.1 | 407.7 | 400.5 | 435.8 | 435.9 | 429.6 | 458.9 | 410 | 393.4
3151.1 | 3026.1 | 313 | 400.9 | 407.4 | 400.3 | 435.7 | 435.7 | 429.4 | 458.7 | 409.8 | 393.2
3152.1 | 3027.1 | 312.7 | 400.6 | 407.2 | 400.1 | 435.4 | 435.4 | 429.1 | 458.5 | 409.7 | 393
3153.1 | 3028.1 | 312.4 | 400.4 | 407 | 399.8 | 435.1 | 435.2 | 428.9 | 458.3 | 409.6 | 392.8
3154.1 | 3029.1 | 312.1 | 400.2 | 406.7 | 399.6 | 435 | 435 | 428.7 | 458.2 | 409.1 | 392.7
3155.1 | 3030.1 | 311.8 | 400 | 406.4 | 399.4 | 434.8 | 434.8 | 428.5 | 458 | 408.8 | 392.5
3156.1 | 3031.1 | 311.5 | 399.7 | 406.2 | 399.1 | 434.6 | 434.6 | 428.2 | 457.8 | 408.7 | 392.3
3157.1 | 3032.1 | 311.2 | 399.5 | 406 | 398.9 | 434.3 | 434.4 | 428 | 457.5 | 408.1 | 392.1
3158.1 | 3033.1 | 310.9 | 399.3 | 405.7 | 398.7 | 434.2 | 434.2 | 427.8 | 457.2 | 408.2 | 391.9
3159.1 | 3034.1 | 310.6 | 399.1 | 405.4 | 398.5 | 433.9 | 434 | 427.6 | 456.9 | 408 | 391.7
3160.1 | 3035.1 | 310.3 | 398.8 | 405.2 | 398.2 | 433.7 | 433.7 | 427.3 | 456.6 | 407.8 | 391.6
3161.1 | 3036.1 | 310 | 398.6 | 405 | 398 | 433.5 | 433.5 | 427.1 | 456.4 | 407.7 | 391.4
3162.1 | 3037.1 | 309.7 | 398.4 | 404.7 | 397.8 | 433.3 | 433.3 | 426.9 | 456.3 | 407.7 | 391.2
3163.1 | 3038.1 | 309.4 | 398.2 | 404.4 | 397.6 | 433.1 | 433.1 | 426.7 | 456.3 | 407.4 | 391
3164.1 | 3039.1 | 309.1 | 397.9 | 404.2 | 397.3 | 432.8 | 432.9 | 426.4 | 456.2 | 407.6 | 390.8
3165.1 | 3040.1 | 308.9 | 397.7 | 403.9 | 397.1 | 432.7 | 432.7 | 426.2 | 456.2 | 407.2 | 390.6
3166.1 | 3041.1 | 308.6 | 397.5 | 403.7 | 396.9 | 432.5 | 432.4 | 426 | 455.9 | 407 | 390.5
3167.1 | 3042.1 | 308.3 | 397.2 | 403.5 | 396.6 | 432.2 | 432.2 | 425.8 | 455.5 | 407.1 | 390.3
3168.1 | 3043.1 | 308 | 397 | 403.2 | 396.4 | 432 | 432 | 425.5 | 455.3 | 406.6 | 390.1
3169.1 | 3044.1 | 307.7 | 396.8 | 402.9 | 396.2 | 431.8 | 431.8 | 425.3 | 455.2 | 406.4 | 389.9
3170.1 | 3045.1 | 307.4 | 396.6 | 402.7 | 396 | 431.6 | 431.6 | 425.1 | 455 | 406.2 | 389.7
3171.1 | 3046.1 | 307.1 | 396.3 | 402.5 | 395.8 | 431.3 | 431.3 | 424.9 | 455 | 405.8 | 389.5
3172.1 | 3047.1 | 306.9 | 396.2 | 402.2 | 395.6 | 431.2 | 431.1 | 424.6 | 454.9 | 405.9 | 389.3
3173.1 | 3048.1 | 306.6 | 395.9 | 402 | 395.3 | 431 | 430.9 | 424.4 | 454.8 | 405.7 | 389.1
3174.1 | 3049.1 | 306.3 | 395.7 | 401.8 | 395.1 | 430.7 | 430.7 | 424.2 | 454.7 | 405.2 | 389
3175.1 | 3050.1 | 306 | 395.5 | 401.5 | 394.9 | 430.5 | 430.5 | 424 | 454.7 | 405.7 | 388.8
3176.1 | 3051.1 | 305.8 | 395.3 | 401.2 | 394.7 | 430.3 | 430.3 | 423.7 | 454.5 | 405.4 | 388.6
3177.1 | 3052.1 | 305.5 | 395 | 401 | 394.4 | 430.1 | 430.1 | 423.5 | 454.2 | 405 | 388.4
3178.1 | 3053.1 | 305.2 | 394.8 | 400.8 | 394.2 | 429.8 | 429.8 | 423.3 | 453.8 | 405.3 | 388.2
3179.1 | 3054.1 | 304.9 | 394.6 | 400.5 | 394 | 429.7 | 429.6 | 423.1 | 453.6 | 404.8 | 388
3180.1 | 3055.1 | 304.6 | 394.4 | 400.3 | 393.8 | 429.5 | 429.4 | 422.8 | 453.5 | 404.4 | 387.9
3181.1 | 3056.1 | 304.4 | 394.1 | 400.1 | 393.5 | 429.2 | 429.2 | 422.6 | 453.3 | 404.1 | 387.7
3182.1 | 3057.1 | 304.1 | 393.9 | 399.8 | 393.3 | 429 | 429 | 422.4 | 453 | 404 | 387.5
3183.1 | 3058.1 | 303.8 | 393.7 | 399.5 | 393.1 | 428.8 | 428.8 | 422.2 | 452.9 | 404.2 | 387.3
3184.1 | 3059.1 | 303.5 | 393.5 | 399.3 | 392.8 | 428.6 | 428.5 | 421.9 | 452.4 | 404.3 | 387
3185.1 | 3060.1 | 303.2 | 393.2 | 399.1 | 392.6 | 428.3 | 428.3 | 421.7 | 452.1 | 403.4 | 386.9
3186.1 | 3061.1 | 303 | 393.1 | 398.8 | 392.4 | 428.2 | 428.1 | 421.5 | 451.8 | 403.8 | 386.7
3187.1 | 3062.1 | 302.7 | 392.8 | 398.5 | 392.2 | 428 | 427.9 | 421.3 | 451.7 | 403.7 | 386.5
3188.1 | 3063.1 | 302.4 | 392.6 | 398.3 | 391.9 | 427.7 | 427.7 | 421 | 451.7 | 402.9 | 386.3
3189.1 | 3064.1 | 302.2 | 392.4 | 398.1 | 391.7 | 427.5 | 427.4 | 420.8 | 451.3 | 403.4 | 386.1
3190.1 | 3065.1 | 301.9 | 392.2 | 397.8 | 391.5 | 427.3 | 427.2 | 420.6 | 450.9 | 403 | 385.9
3191.1 | 3066.1 | 301.6 | 392 | 397.6 | 391.3 | 427.1 | 427 | 420.4 | 450.7 | 402.4 | 385.8
3192.1 | 3067.1 | 301.3 | 391.7 | 397.5 | 391 | 426.8 | 426.8 | 420.2 | 450.7 | 402.9 | 385.6
3193.1 | 3068.1 | 301.1 | 391.5 | 397.2 | 390.8 | 426.7 | 426.6 | 419.9 | 450.6 | 402.8 | 385.4
3194.1 | 3069.1 | 300.8 | 391.3 | 396.9 | 390.6 | 426.5 | 426.4 | 419.7 | 450.5 | 402.7 | 385.1

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 49 |  |  | 2006-08-31 | 12:58
38960.539 | 1 | 0 | 1 | TS & TP Mix | 7-C | Conduit
38960.5395 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38960.54 | 1 | 0 | 1
38960.5405 | 1 | 0 | 1
38960.541 | 1 | 0 | 1
38960.5415 | 1 | 0 | 1
38960.542 | 1 | 0 | 1
38960.5424 | 1 | 0 | 1
38960.5429 | 1 | 0 | 1
38960.5439 | 1 | 0 | 1
38960.5444 | 1 | 0 | 1
38960.5449 | 1 | 0 | 1
38960.5453 | 1 | 0 | 1
38960.5458 | 1 | 0 | 1
38960.5463 | 1 | 0 | 1
38960.5468 | 1 | 0 | 1
38960.5473 | 1 | 0 | 1
38960.5478 | 1 | 0 | 1
38960.5483 | 1 | 0 | 1
38960.5488 | 1 | 0 | 1
38960.5492 | 1 | 0 | 1
38960.5497 | 1 | 0 | 1
38960.5502 | 1 | 0 | 1
38960.5507 | 1 | 0 | 1
38960.5512 | 1 | 0 | 1
38960.5517 | 1 | 0 | 1
38960.5522 | 1 | 0 | 1
38960.5526 | 1 | 0 | 1
38960.5531 | 1 | 0 | 1
38960.5536 | 1 | 0 | 1
38960.5541 | 1 | 0 | 1
38960.5546 | 1 | 0 | 1
38960.5551 | 1 | 0 | 1
38960.5556 | 1 | 0 | 1
38960.556 | 1 | 0 | 1
38960.5565 | 1 | 0 | 1
38960.557 | 1 | 0 | 1
38960.5575 | 1 | 0 | 1
38960.558 | 1 | 1 | 1
38960.5585 | 2 | 1 | 1
38960.559 | 4 | 2 | 1
38960.5594 | 45 | 39 | 1
38960.5599 | 203 | 182 | 1
38960.5604 | 1053 | 945 | 1
38960.5609 | 1059 | 1135 | 1
38960.5614 | 1222 | 1182 | 1
38960.5619 | 1193 | 1192 | 1
38960.5624 | 990 | 1003 | 1
38960.5628 | 1118 | 1158 | 1
38960.5633 | 1079 | 1028 | 1
38960.5638 | 998 | 949 | 1
38960.5643 | 1172 | 922 | 1
38960.5648 | 1067 | 937 | 1
38960.5653 | 1211 | 1145 | 1
38960.5658 | 1205 | 1164 | 1
38960.5663 | 1009 | 950 | 1
38960.5667 | 1000 | 941 | 1
38960.5672 | 1215 | 1143 | 1
38960.5677 | 1225 | 1154 | 1
38960.5682 | 1085 | 1013 | 1
38960.5687 | 1067 | 989 | 1
38960.5692 | 1083 | 999 | 1
38960.5697 | 1057 | 972 | 1
38960.5701 | 1107 | 1084 | 1
38960.5706 | 1233 | 1127 | 1
38960.5711 | 1045 | 943 | 1
38960.5716 | 1137 | 1022 | 1
38960.5721 | 1254 | 1131 | 1
38960.5726 | 1079 | 964 | 1
38960.5731 | 1011 | 902 | 1
38960.5735 | 1022 | 915 | 1
38960.574 | 1252 | 1154 | 1
38960.5745 | 1153 | 1042 | 1
38960.575 | 993 | 899 | 1
38960.5755 | 1028 | 938 | 1
1
38960.5391 | 1 | 0 | 2
38960.5395 | 1 | 0 | 2
38960.54 | 2 | 0 | 2
38960.5405 | 1 | 0 | 2
38960.541 | 2 | 0 | 2
38960.5415 | 1 | 0 | 2
38960.542 | 1 | 0 | 2
38960.5425 | 1 | 0 | 2
38960.5429 | 1 | 0 | 2
38960.5434 | 1 | 1 | 2
38960.5439 | 1 | 0 | 2
38960.5444 | 1 | 0 | 2
38960.5449 | 1 | 0 | 2
38960.5454 | 1 | 0 | 2
38960.5459 | 1 | 0 | 2
38960.5463 | 1 | 0 | 2
38960.5468 | 2 | 0 | 2
38960.5473 | 1 | 0 | 2
38960.5478 | 1 | 0 | 2
38960.5483 | 1 | 0 | 2
38960.5488 | 1 | 0 | 2
38960.5493 | 1 | 0 | 2
38960.5497 | 1 | 0 | 2
38960.5502 | 1 | 0 | 2
38960.5507 | 1 | 0 | 2
38960.5512 | 1 | 0 | 2
38960.5517 | 1 | 0 | 2
38960.5522 | 1 | 0 | 2
38960.5527 | 1 | 0 | 2
38960.5531 | 1 | 0 | 2
38960.5536 | 1 | 0 | 2
38960.5541 | 1 | 0 | 2
38960.5546 | 1 | 0 | 2
38960.5551 | 1 | 0 | 2
38960.5556 | 1 | 0 | 2
38960.5561 | 1 | 0 | 2
38960.5566 | 1 | 0 | 2
38960.557 | 1 | 0 | 2
38960.5575 | 1 | 0 | 2
38960.558 | 1 | 0 | 2
38960.5585 | 2 | 1 | 2
38960.559 | 6 | 3 | 2
38960.5595 | 51 | 41 | 2
38960.56 | 853 | 919 | 2
38960.5604 | 1038 | 997 | 2
38960.5609 | 1015 | 973 | 2
38960.5614 | 949 | 992 | 2
38960.5619 | 1184 | 1194 | 2
38960.5624 | 1085 | 938 | 2
38960.5629 | 1135 | 1080 | 2
38960.5634 | 1135 | 1083 | 2
38960.5638 | 1011 | 1027 | 2
38960.5643 | 1179 | 1123 | 2
38960.5648 | 1004 | 952 | 2
38960.5653 | 970 | 917 | 2
38960.5658 | 1124 | 1064 | 2
38960.5663 | 983 | 928 | 2
38960.5668 | 1038 | 1043 | 2
38960.5672 | 975 | 913 | 2
38960.5677 | 1041 | 974 | 2
38960.5682 | 1038 | 967 | 2
38960.5687 | 1183 | 1100 | 2
38960.5692 | 1205 | 1116 | 2
38960.5697 | 998 | 916 | 2
38960.5702 | 1202 | 1161 | 2
38960.5706 | 1216 | 896 | 2
38960.5711 | 974 | 953 | 2
38960.5716 | 1209 | 1087 | 2
38960.5721 | 1149 | 1029 | 2
38960.5726 | 986 | 999 | 2
38960.5731 | 1059 | 1069 | 2
38960.5736 | 1087 | 973 | 2
38960.574 | 1209 | 1088 | 2
38960.5745 | 1222 | 1157 | 2
38960.575 | 1064 | 965 | 2
38960.5755 | 1225 | 1121 | 2
2
38960.5391 | 1 | 0 | 3
38960.5395 | 1 | 0 | 3
38960.54 | 1 | 0 | 3
38960.5405 | 1 | 0 | 3
38960.541 | 1 | 0 | 3
38960.5415 | 1 | 0 | 3
38960.542 | 1 | 0 | 3
38960.5425 | 1 | 0 | 3
38960.543 | 1 | 0 | 3
38960.5434 | 1 | 0 | 3
38960.5439 | 1 | 0 | 3
38960.5444 | 1 | 0 | 3
38960.5449 | 1 | 0 | 3
38960.5454 | 2 | 0 | 3
38960.5459 | 1 | 0 | 3
38960.5464 | 1 | 1 | 3
38960.5468 | 1 | 0 | 3
38960.5473 | 1 | 0 | 3
38960.5478 | 1 | 0 | 3
38960.5483 | 1 | 0 | 3
38960.5488 | 1 | 0 | 3
38960.5493 | 1 | 0 | 3
38960.5498 | 1 | 0 | 3
38960.5502 | 1 | 0 | 3
38960.5507 | 1 | 0 | 3
38960.5512 | 1 | 0 | 3
38960.5517 | 1 | 0 | 3
38960.5522 | 1 | 0 | 3
38960.5527 | 1 | 0 | 3
38960.5532 | 1 | 0 | 3
38960.5536 | 1 | 0 | 3
38960.5541 | 1 | 0 | 3
38960.5546 | 1 | 0 | 3
38960.5551 | 1 | 0 | 3
38960.5556 | 1 | 0 | 3
38960.5561 | 2 | 0 | 3
38960.5566 | 1 | 0 | 3
38960.557 | 1 | 0 | 3
38960.5575 | 1 | 0 | 3
38960.558 | 1 | 0 | 3
38960.5585 | 1 | 0 | 3
38960.559 | 1 | 0 | 3
38960.5595 | 1 | 0 | 3
38960.56 | 1 | 0 | 3
38960.5605 | 1 | 1 | 3
38960.5609 | 1 | 1 | 3
38960.5614 | 2 | 1 | 3
38960.5619 | 2 | 1 | 3
38960.5624 | 2 | 1 | 3
38960.5629 | 2 | 1 | 3
38960.5634 | 2 | 1 | 3
38960.5639 | 2 | 1 | 3
38960.5643 | 2 | 1 | 3
38960.5648 | 2 | 1 | 3
38960.5653 | 2 | 1 | 3
38960.5658 | 2 | 1 | 3
38960.5663 | 2 | 1 | 3
38960.5668 | 2 | 1 | 3
38960.5673 | 2 | 1 | 3
38960.5677 | 2 | 1 | 3
38960.5682 | 3 | 1 | 3
38960.5687 | 4 | 1 | 3
38960.5692 | 5 | 1 | 3
38960.5697 | 7 | 1 | 3
38960.5702 | 10 | 1 | 3
38960.5707 | 15 | 0 | 3
38960.5711 | 22 | 1 | 3
38960.5716 | 30 | 1 | 3
38960.5721 | 41 | 1 | 3
38960.5726 | 43 | 1 | 3
38960.5731 | 41 | 1 | 3
38960.5736 | 36 | 0 | 3
38960.5741 | 33 | 1 | 3
38960.5745 | 21 | 1 | 3
38960.575 | 18 | 1 | 3
38960.5755 | 13 | 0 | 3
3
38960.5391 | 1 | 1 | 4
38960.5396 | 1 | 0 | 4
38960.5401 | 1 | 0 | 4
38960.5405 | 1 | 1 | 4
38960.541 | 1 | 0 | 4
38960.5415 | 1 | 0 | 4
38960.542 | 1 | 0 | 4
38960.5425 | 1 | 0 | 4
38960.543 | 1 | 0 | 4
38960.5435 | 1 | 0 | 4
38960.5439 | 1 | 0 | 4
38960.5444 | 1 | 0 | 4
38960.5449 | 1 | 0 | 4
38960.5454 | 1 | 0 | 4
38960.5459 | 1 | 0 | 4
38960.5464 | 1 | 0 | 4
38960.5469 | 1 | 0 | 4
38960.5473 | 1 | 0 | 4
38960.5478 | 1 | 0 | 4
38960.5483 | 1 | 0 | 4
38960.5488 | 1 | 0 | 4
38960.5493 | 1 | 0 | 4
38960.5498 | 1 | 0 | 4
38960.5503 | 1 | 0 | 4
38960.5508 | 1 | 0 | 4
38960.5512 | 1 | 0 | 4
38960.5517 | 1 | 0 | 4
38960.5522 | 1 | 0 | 4
38960.5527 | 1 | 0 | 4
38960.5532 | 1 | 0 | 4
38960.5537 | 1 | 0 | 4
38960.5541 | 1 | 0 | 4
38960.5546 | 1 | 0 | 4
38960.5551 | 1 | 0 | 4
38960.5556 | 1 | 0 | 4
38960.5561 | 1 | 0 | 4
38960.5566 | 1 | 0 | 4
38960.5571 | 1 | 0 | 4
38960.5575 | 1 | 0 | 4
38960.558 | 1 | 0 | 4
38960.5585 | 1 | 0 | 4
38960.559 | 1 | 0 | 4
38960.5595 | 1 | 0 | 4
38960.56 | 1930 | 0 | 4
38960.5605 | 2123 | 0 | 4
38960.5609 | 2406 | 0 | 4
38960.5614 | 1434 | 0 | 4
38960.5619 | 2508 | 1 | 4
38960.5624 | 2380 | 0 | 4
38960.5629 | 2106 | 1 | 4
38960.5634 | 1807 | 0 | 4
38960.5639 | 1994 | 0 | 4
38960.5644 | 2097 | 1 | 4
38960.5648 | 2045 | 0 | 4
38960.5653 | 1962 | 1 | 4
38960.5658 | 2102 | 1 | 4
38960.5663 | 2424 | 0 | 4
38960.5668 | 1919 | 0 | 4
38960.5673 | 2098 | 0 | 4
38960.5678 | 1989 | 0 | 4
38960.5682 | 2471 | 0 | 4
38960.5687 | 2035 | 0 | 4
38960.5692 | 2230 | 0 | 4
38960.5697 | 2297 | 0 | 4
38960.5702 | 2042 | 0 | 4
38960.5707 | 2238 | 0 | 4
38960.5712 | 1931 | 0 | 4
38960.5716 | 2269 | 0 | 4
38960.5721 | 2332 | 1 | 4
38960.5726 | 2403 | 0 | 4
38960.5731 | 2458 | 0 | 4
38960.5736 | 2427 | 0 | 4
38960.5741 | 2444 | 0 | 4
38960.5746 | 2442 | 0 | 4
38960.575 | 2426 | 0 | 4
38960.5755 | 1934 | 0 | 4
4
38960.5391 | 1 | 0 | 5
38960.5396 | 1 | 0 | 5
38960.5401 | 1 | 0 | 5
38960.5406 | 1 | 0 | 5
38960.541 | 1 | 0 | 5
38960.5415 | 1 | 0 | 5
38960.542 | 1 | 0 | 5
38960.5425 | 1 | 0 | 5
38960.543 | 1 | 0 | 5
38960.5435 | 1 | 0 | 5
38960.544 | 1 | 0 | 5
38960.5444 | 1 | 0 | 5
38960.5449 | 1 | 0 | 5
38960.5454 | 1 | 0 | 5
38960.5459 | 1 | 0 | 5
38960.5464 | 1 | 0 | 5
38960.5469 | 1 | 0 | 5
38960.5474 | 1 | 0 | 5
38960.5478 | 1 | 0 | 5
38960.5483 | 1 | 0 | 5
38960.5488 | 1 | 0 | 5
38960.5493 | 1 | 0 | 5
38960.5498 | 1 | 0 | 5
38960.5503 | 1 | 0 | 5
38960.5508 | 1 | 0 | 5
38960.5512 | 1 | 0 | 5
38960.5517 | 1 | 0 | 5
38960.5522 | 1 | 0 | 5
38960.5527 | 1 | 0 | 5
38960.5532 | 1 | 0 | 5
38960.5537 | 1 | 0 | 5
38960.5542 | 1 | 0 | 5
38960.5547 | 1 | 0 | 5
38960.5551 | 1 | 0 | 5
38960.5556 | 1 | 0 | 5
38960.5561 | 1 | 0 | 5
38960.5566 | 1 | 0 | 5
38960.5571 | 1 | 0 | 5
38960.5576 | 1 | 0 | 5
38960.5581 | 1 | 0 | 5
38960.5585 | 1 | 0 | 5
38960.559 | 1 | 0 | 5
38960.5595 | 1 | 1 | 5
38960.56 | 2 | 0 | 5
38960.5605 | 2 | 0 | 5
38960.561 | 2 | 0 | 5
38960.5615 | 2 | 0 | 5
38960.5619 | 2 | 0 | 5
38960.5624 | 2 | 1 | 5
38960.5629 | 2 | 0 | 5
38960.5634 | 2 | 0 | 5
38960.5639 | 2 | 0 | 5
38960.5644 | 2 | 0 | 5
38960.5649 | 2 | 0 | 5
38960.5653 | 2 | 0 | 5
38960.5658 | 2 | 0 | 5
38960.5663 | 3 | 0 | 5
38960.5668 | 3 | 0 | 5
38960.5673 | 2 | 0 | 5
38960.5678 | 3 | 0 | 5
38960.5683 | 3 | 0 | 5
38960.5687 | 3 | 0 | 5
38960.5692 | 5 | 0 | 5
38960.5697 | 7 | 0 | 5
38960.5702 | 10 | 0 | 5
38960.5707 | 15 | 0 | 5
38960.5712 | 25 | 0 | 5
38960.5717 | 35 | 0 | 5
38960.5722 | 43 | 0 | 5
38960.5726 | 45 | 0 | 5
38960.5731 | 38 | 0 | 5
38960.5736 | 31 | 0 | 5
38960.5741 | 29 | 0 | 5
38960.5746 | 21 | 0 | 5
38960.5751 | 15 | 0 | 5
38960.5756 | 10 | 0 | 5
5
38960.5391 | 1 | 0 | 6
38960.5396 | 1 | 1 | 6
38960.5401 | 1 | 1 | 6
38960.5406 | 1 | 0 | 6
38960.5411 | 1 | 0 | 6
38960.5415 | 1 | 0 | 6
38960.542 | 1 | 0 | 6
38960.5425 | 1 | 0 | 6
38960.543 | 1 | 0 | 6
38960.5435 | 1 | 0 | 6
38960.544 | 1 | 0 | 6
38960.5445 | 2 | 0 | 6
38960.5449 | 1 | 0 | 6
38960.5454 | 1 | 0 | 6
38960.5459 | 1 | 0 | 6
38960.5464 | 1 | 0 | 6
38960.5469 | 1 | 0 | 6
38960.5474 | 1 | 0 | 6
38960.5479 | 1 | 0 | 6
38960.5483 | 1 | 0 | 6
38960.5488 | 1 | 0 | 6
38960.5493 | 1 | 0 | 6
38960.5498 | 1 | 0 | 6
38960.5503 | 1 | 0 | 6
38960.5508 | 1 | 0 | 6
38960.5513 | 1 | 0 | 6
38960.5517 | 1 | 0 | 6
38960.5522 | 1 | 0 | 6
38960.5527 | 1 | 0 | 6
38960.5532 | 1 | 0 | 6
38960.5537 | 1 | 0 | 6
38960.5542 | 1 | 0 | 6
38960.5547 | 1 | 0 | 6
38960.5552 | 1 | 0 | 6
38960.5556 | 1 | 0 | 6
38960.5561 | 1 | 0 | 6
38960.5566 | 1 | 0 | 6
38960.5571 | 1 | 0 | 6
38960.5576 | 1 | 0 | 6
38960.5581 | 1 | 0 | 6
38960.5586 | 1 | 0 | 6
38960.559 | 1 | 0 | 6
38960.5595 | 1 | 0 | 6
38960.56 | 1897 | 0 | 6
38960.5605 | 2062 | 0 | 6
38960.561 | 2420 | 0 | 6
38960.5615 | 2497 | 0 | 6
38960.562 | 2529 | 0 | 6
38960.5624 | 2401 | 0 | 6
38960.5629 | 2211 | 0 | 6
38960.5634 | 1889 | 0 | 6
38960.5639 | 2044 | 0 | 6
38960.5644 | 2179 | 0 | 6
38960.5649 | 2435 | 0 | 6
38960.5654 | 2209 | 0 | 6
38960.5658 | 2203 | 0 | 6
38960.5663 | 2284 | 0 | 6
38960.5668 | 1974 | 0 | 6
38960.5673 | 2139 | 0 | 6
38960.5678 | 1983 | 0 | 6
38960.5683 | 1963 | 0 | 6
38960.5688 | 2252 | 0 | 6
38960.5692 | 2027 | 0 | 6
38960.5697 | 1969 | 0 | 6
38960.5702 | 2426 | 0 | 6
38960.5707 | 2501 | 0 | 6
38960.5712 | 2014 | 0 | 6
38960.5717 | 1946 | 0 | 6
38960.5722 | 2130 | 0 | 6
38960.5727 | 1941 | 0 | 6
38960.5731 | 1960 | 0 | 6
38960.5736 | 2028 | 0 | 6
38960.5741 | 2346 | 0 | 6
38960.5746 | 2186 | 0 | 6
38960.5751 | 2054 | 0 | 6
38960.5756 | 2078 | 0 | 6
6
38960.5391 | 1 | 0 | 7
38960.5396 | 1 | 0 | 7
38960.5401 | 1 | 0 | 7
38960.5406 | 1 | 0 | 7
38960.5411 | 1 | 0 | 7
38960.5416 | 1 | 0 | 7
38960.542 | 1 | 0 | 7
38960.5425 | 1 | 0 | 7
38960.543 | 1 | 0 | 7
38960.5435 | 1 | 0 | 7
38960.544 | 1 | 0 | 7
38960.5445 | 1 | 0 | 7
38960.545 | 1 | 0 | 7
38960.5455 | 1 | 0 | 7
38960.5459 | 1 | 0 | 7
38960.5464 | 1 | 0 | 7
38960.5469 | 1 | 0 | 7
38960.5474 | 1 | 0 | 7
38960.5479 | 1 | 0 | 7
38960.5484 | 1 | 0 | 7
38960.5489 | 1 | 0 | 7
38960.5493 | 1 | 0 | 7
38960.5498 | 1 | 0 | 7
38960.5503 | 1 | 0 | 7
38960.5508 | 1 | 0 | 7
38960.5513 | 1 | 0 | 7
38960.5518 | 1 | 0 | 7
38960.5523 | 1 | 0 | 7
38960.5527 | 1 | 0 | 7
38960.5532 | 1 | 0 | 7
38960.5537 | 1 | 0 | 7
38960.5542 | 1 | 0 | 7
38960.5547 | 1 | 0 | 7
38960.5552 | 1 | 0 | 7
38960.5557 | 1 | 0 | 7
38960.5561 | 1 | 0 | 7
38960.5566 | 1 | 0 | 7
38960.5571 | 1 | 0 | 7
38960.5576 | 1 | 0 | 7
38960.5581 | 1 | 0 | 7
38960.5586 | 1 | 0 | 7
38960.5591 | 1 | 0 | 7
38960.5595 | 2 | 1 | 7
38960.56 | 1 | 0 | 7
38960.5605 | 2 | 0 | 7
38960.561 | 2 | 0 | 7
38960.5615 | 2 | 0 | 7
38960.562 | 2 | 0 | 7
38960.5625 | 2 | 0 | 7
38960.563 | 2 | 0 | 7
38960.5634 | 2 | 0 | 7
38960.5639 | 2 | 0 | 7
38960.5644 | 2 | 0 | 7
38960.5649 | 2 | 0 | 7
38960.5654 | 2 | 0 | 7
38960.5659 | 2 | 0 | 7
38960.5664 | 2 | 0 | 7
38960.5668 | 2 | 0 | 7
38960.5673 | 3 | 1 | 7
38960.5678 | 2 | 0 | 7
38960.5683 | 3 | 0 | 7
38960.5688 | 4 | 0 | 7
38960.5693 | 4 | 0 | 7
38960.5697 | 8 | 0 | 7
38960.5702 | 11 | 0 | 7
38960.5707 | 17 | 0 | 7
38960.5712 | 28 | 0 | 7
38960.5717 | 33 | 0 | 7
38960.5722 | 38 | 0 | 7
38960.5727 | 38 | 0 | 7
38960.5731 | 44 | 0 | 7
38960.5736 | 38 | 0 | 7
38960.5741 | 27 | 0 | 7
38960.5746 | 26 | 0 | 7
38960.5751 | 15 | 0 | 7
38960.5756 | 12 | 0 | 7
7
38960.5391 | 1 | 1 | 8
38960.5396 | 1 | 0 | 8
38960.5401 | 1 | 0 | 8
38960.5406 | 1 | 1 | 8
38960.5411 | 1 | 0 | 8
38960.5416 | 1 | 0 | 8
38960.5421 | 1 | 0 | 8
38960.5425 | 1 | 0 | 8
38960.543 | 1 | 0 | 8
38960.5435 | 1 | 0 | 8
38960.544 | 2 | 0 | 8
38960.5445 | 1 | 0 | 8
38960.545 | 1 | 0 | 8
38960.5455 | 1 | 0 | 8
38960.5459 | 1 | 0 | 8
38960.5464 | 1 | 0 | 8
38960.5469 | 1 | 0 | 8
38960.5474 | 1 | 0 | 8
38960.5479 | 1 | 0 | 8
38960.5484 | 1 | 0 | 8
38960.5489 | 1 | 0 | 8
38960.5494 | 1 | 0 | 8
38960.5498 | 1 | 0 | 8
38960.5503 | 1 | 0 | 8
38960.5508 | 1 | 0 | 8
38960.5513 | 1 | 0 | 8
38960.5518 | 1 | 0 | 8
38960.5523 | 1 | 0 | 8
38960.5528 | 1 | 0 | 8
38960.5532 | 1 | 0 | 8
38960.5537 | 1 | 0 | 8
38960.5542 | 1 | 0 | 8
38960.5547 | 1 | 0 | 8
38960.5552 | 2 | 0 | 8
38960.5557 | 1 | 0 | 8
38960.5562 | 1 | 0 | 8
38960.5566 | 1 | 0 | 8
38960.5571 | 1 | 0 | 8
38960.5576 | 1 | 0 | 8
38960.5581 | 1 | 0 | 8
38960.5586 | 1 | 0 | 8
38960.5591 | 1 | 0 | 8
38960.5596 | 1 | 0 | 8
38960.56 | 2 | 0 | 8
38960.5605 | 46 | 0 | 8
38960.561 | 1997 | 0 | 8
38960.5615 | 1818 | 0 | 8
38960.562 | 2102 | 0 | 8
38960.5625 | 1909 | 0 | 8
38960.563 | 2182 | 0 | 8
38960.5634 | 2199 | 0 | 8
38960.5639 | 2239 | 0 | 8
38960.5644 | 1880 | 0 | 8
38960.5649 | 1903 | 0 | 8
38960.5654 | 1852 | 0 | 8
38960.5659 | 1863 | 0 | 8
38960.5664 | 2164 | 0 | 8
38960.5669 | 2323 | 0 | 8
38960.5673 | 1881 | 0 | 8
38960.5678 | 2410 | 0 | 8
38960.5683 | 2152 | 0 | 8
38960.5688 | 2234 | 0 | 8
38960.5693 | 1999 | 0 | 8
38960.5698 | 2058 | 0 | 8
38960.5703 | 2117 | 0 | 8
38960.5707 | 2401 | 0 | 8
38960.5712 | 1997 | 0 | 8
38960.5717 | 2336 | 0 | 8
38960.5722 | 2154 | 0 | 8
38960.5727 | 2077 | 0 | 8
38960.5732 | 2259 | 0 | 8
38960.5737 | 2406 | 0 | 8
38960.5741 | 1914 | 0 | 8
38960.5746 | 2061 | 0 | 8
38960.5751 | 1906 | 0 | 8
38960.5756 | 2419 | 0 | 8
8
38960.5392 | 1 | 0 | 9
38960.5397 | 1 | 0 | 9
38960.5401 | 1 | 0 | 9
38960.5406 | 1 | 0 | 9
38960.5411 | 1 | 0 | 9
38960.5416 | 1 | 0 | 9
38960.5421 | 1 | 0 | 9
38960.5426 | 1 | 0 | 9
38960.5431 | 1 | 0 | 9
38960.5435 | 1 | 0 | 9
38960.544 | 1 | 0 | 9
38960.5445 | 1 | 0 | 9
38960.545 | 1 | 0 | 9
38960.5455 | 2 | 0 | 9
38960.546 | 1 | 0 | 9
38960.5465 | 1 | 0 | 9
38960.5469 | 1 | 0 | 9
38960.5474 | 1 | 0 | 9
38960.5479 | 1 | 0 | 9
38960.5484 | 1 | 0 | 9
38960.5489 | 1 | 0 | 9
38960.5494 | 1 | 0 | 9
38960.5499 | 1 | 0 | 9
38960.5503 | 1 | 0 | 9
38960.5508 | 1 | 0 | 9
38960.5513 | 1 | 0 | 9
38960.5518 | 1 | 0 | 9
38960.5523 | 1 | 0 | 9
38960.5528 | 1 | 0 | 9
38960.5533 | 1 | 0 | 9
38960.5537 | 1 | 0 | 9
38960.5542 | 1 | 0 | 9
38960.5547 | 1 | 0 | 9
38960.5552 | 1 | 0 | 9
38960.5557 | 1 | 0 | 9
38960.5562 | 1 | 0 | 9
38960.5567 | 1 | 0 | 9
38960.5571 | 1 | 0 | 9
38960.5576 | 1 | 0 | 9
38960.5581 | 1 | 0 | 9
38960.5586 | 1 | 0 | 9
38960.5591 | 1 | 0 | 9
38960.5596 | 1 | 0 | 9
38960.5601 | 1 | 0 | 9
38960.5605 | 1 | 0 | 9
38960.561 | 2 | 0 | 9
38960.5615 | 2 | 0 | 9
38960.562 | 2 | 0 | 9
38960.5625 | 2 | 0 | 9
38960.563 | 2 | 0 | 9
38960.5635 | 2 | 0 | 9
38960.5639 | 2 | 0 | 9
38960.5644 | 2 | 0 | 9
38960.5649 | 3 | 0 | 9
38960.5654 | 2 | 0 | 9
38960.5659 | 2 | 0 | 9
38960.5664 | 2 | 0 | 9
38960.5669 | 2 | 0 | 9
38960.5673 | 2 | 0 | 9
38960.5678 | 3 | 0 | 9
38960.5683 | 3 | 0 | 9
38960.5688 | 4 | 0 | 9
38960.5693 | 5 | 0 | 9
38960.5698 | 8 | 0 | 9
38960.5703 | 12 | 0 | 9
38960.5708 | 20 | 0 | 9
38960.5712 | 30 | 0 | 9
38960.5717 | 39 | 0 | 9
38960.5722 | 41 | 0 | 9
38960.5727 | 40 | 0 | 9
38960.5732 | 42 | 0 | 9
38960.5737 | 38 | 0 | 9
38960.5742 | 32 | 0 | 9
38960.5746 | 22 | 0 | 9
38960.5751 | 16 | 0 | 9
38960.5756 | 12 | 0 | 9
9
38960.5392 | 1 | 0 | 10
38960.5397 | 1 | 0 | 10
38960.5402 | 1 | 0 | 10
38960.5406 | 1 | 0 | 10
38960.5411 | 1 | 0 | 10
38960.5416 | 1 | 0 | 10
38960.5421 | 1 | 0 | 10
38960.5426 | 1 | 0 | 10
38960.5431 | 1 | 0 | 10
38960.5436 | 1 | 0 | 10
38960.544 | 1 | 0 | 10
38960.5445 | 1 | 0 | 10
38960.545 | 1 | 0 | 10
38960.5455 | 1 | 0 | 10
38960.546 | 1 | 0 | 10
38960.5465 | 1 | 0 | 10
38960.547 | 1 | 0 | 10
38960.5474 | 1 | 0 | 10
38960.5479 | 1 | 0 | 10
38960.5484 | 1 | 0 | 10
38960.5489 | 1 | 0 | 10
38960.5494 | 1 | 0 | 10
38960.5499 | 1 | 0 | 10
38960.5504 | 1 | 0 | 10
38960.5508 | 1 | 0 | 10
38960.5513 | 1 | 0 | 10
38960.5518 | 1 | 0 | 10
38960.5523 | 1 | 0 | 10
38960.5528 | 1 | 0 | 10
38960.5533 | 1 | 0 | 10
38960.5538 | 1 | 0 | 10
38960.5542 | 1 | 0 | 10
38960.5547 | 1 | 0 | 10
38960.5552 | 1 | 0 | 10
38960.5557 | 1 | 0 | 10
38960.5562 | 2 | 0 | 10
38960.5567 | 1 | 0 | 10
38960.5572 | 1 | 0 | 10
38960.5577 | 1 | 0 | 10
38960.5581 | 1 | 0 | 10
38960.5586 | 1 | 0 | 10
38960.5591 | 1 | 0 | 10
38960.5596 | 1 | 0 | 10
38960.5601 | 1 | 0 | 10
38960.5606 | 5 | 0 | 10
38960.5611 | 2 | 0 | 10
38960.5615 | 239 | 0 | 10
38960.562 | 287 | 1 | 10
38960.5625 | 2333 | 0 | 10
38960.563 | 2317 | 0 | 10
38960.5635 | 2302 | 0 | 10
38960.564 | 1953 | 0 | 10
38960.5645 | 2294 | 0 | 10
38960.5649 | 2064 | 0 | 10
38960.5654 | 2341 | 0 | 10
38960.5659 | 1929 | 0 | 10
38960.5664 | 2387 | 0 | 10
38960.5669 | 1991 | 0 | 10
38960.5674 | 2020 | 0 | 10
38960.5679 | 2154 | 0 | 10
38960.5683 | 2496 | 0 | 10
38960.5688 | 2342 | 0 | 10
38960.5693 | 2052 | 0 | 10
38960.5703 | 2019 | 0 | 10
38960.5708 | 2241 | 0 | 10
38960.5713 | 2232 | 0 | 10
38960.5717 | 1945 | 0 | 10
38960.5722 | 2168 | 0 | 10
38960.5727 | 2438 | 0 | 10
38960.5732 | 1890 | 0 | 10
38960.5737 | 2160 | 0 | 10
38960.5742 | 2265 | 0 | 10
38960.5747 | 2174 | 0 | 10
38960.5752 | 2138 | 0 | 10
38960.5756 | 2350 | 0 | 10
10
38960.5392 | 1 | 0 | 11
38960.5397 | 1 | 1 | 11
38960.5402 | 1 | 0 | 11
38960.5406 | 1 | 0 | 11
38960.5411 | 1 | 0 | 11
38960.5416 | 1 | 0 | 11
38960.5421 | 1 | 0 | 11
38960.5426 | 1 | 0 | 11
38960.5431 | 1 | 0 | 11
38960.5436 | 1 | 1 | 11
38960.5441 | 1 | 0 | 11
38960.5445 | 1 | 0 | 11
38960.545 | 1 | 0 | 11
38960.5455 | 1 | 0 | 11
38960.546 | 1 | 0 | 11
38960.5465 | 1 | 0 | 11
38960.547 | 1 | 0 | 11
38960.5475 | 1 | 0 | 11
38960.5479 | 1 | 0 | 11
38960.5484 | 1 | 0 | 11
38960.5489 | 1 | 0 | 11
38960.5494 | 1 | 0 | 11
38960.5499 | 1 | 0 | 11
38960.5504 | 1 | 0 | 11
38960.5509 | 1 | 0 | 11
38960.5513 | 1 | 0 | 11
38960.5518 | 1 | 0 | 11
38960.5523 | 1 | 0 | 11
38960.5528 | 2 | 0 | 11
38960.5533 | 1 | 0 | 11
38960.5538 | 2 | 0 | 11
38960.5543 | 1 | 0 | 11
38960.5547 | 1 | 0 | 11
38960.5552 | 1 | 0 | 11
38960.5557 | 1 | 0 | 11
38960.5562 | 1 | 0 | 11
38960.5567 | 1 | 0 | 11
38960.5572 | 1 | 0 | 11
38960.5577 | 1 | 0 | 11
38960.5581 | 1 | 0 | 11
38960.5586 | 1 | 0 | 11
38960.5591 | 1 | 0 | 11
38960.5596 | 1 | 0 | 11
38960.5601 | 1 | 0 | 11
38960.5606 | 1 | 0 | 11
38960.5611 | 2 | 0 | 11
38960.5616 | 2 | 0 | 11
38960.562 | 2 | 0 | 11
38960.5625 | 2 | 0 | 11
38960.563 | 2 | 0 | 11
38960.5635 | 2 | 0 | 11
38960.564 | 2 | 0 | 11
38960.5645 | 2 | 0 | 11
38960.565 | 2 | 0 | 11
38960.5654 | 2 | 0 | 11
38960.5659 | 2 | 0 | 11
38960.5664 | 2 | 0 | 11
38960.5669 | 2 | 0 | 11
38960.5674 | 2 | 0 | 11
38960.5679 | 3 | 0 | 11
38960.5684 | 3 | 0 | 11
38960.5688 | 4 | 0 | 11
38960.5693 | 5 | 0 | 11
38960.5698 | 8 | 0 | 11
38960.5703 | 14 | 0 | 11
38960.5708 | 21 | 0 | 11
38960.5713 | 29 | 0 | 11
38960.5718 | 32 | 0 | 11
38960.5722 | 39 | 0 | 11
38960.5727 | 43 | 0 | 11
38960.5732 | 44 | 0 | 11
38960.5737 | 31 | 0 | 11
38960.5742 | 29 | 0 | 11
38960.5747 | 21 | 0 | 11
38960.5752 | 17 | 0 | 11
38960.5756 | 11 | 0 | 11
11
38960.5392 | 1 | 0 | 12
38960.5397 | 1 | 0 | 12
38960.5402 | 2 | 0 | 12
38960.5407 | 1 | 0 | 12
38960.5412 | 1 | 0 | 12
38960.5416 | 1 | 0 | 12
38960.5421 | 1 | 0 | 12
38960.5426 | 1 | 0 | 12
38960.5431 | 1 | 0 | 12
38960.5436 | 1 | 0 | 12
38960.5441 | 1 | 0 | 12
38960.5446 | 1 | 0 | 12
38960.545 | 1 | 0 | 12
38960.5455 | 1 | 0 | 12
38960.546 | 1 | 0 | 12
38960.5465 | 1 | 0 | 12
38960.547 | 1 | 0 | 12
38960.5475 | 1 | 0 | 12
38960.548 | 1 | 0 | 12
38960.5484 | 1 | 0 | 12
38960.5489 | 1 | 0 | 12
38960.5494 | 1 | 0 | 12
38960.5499 | 1 | 0 | 12
38960.5504 | 1 | 0 | 12
38960.5509 | 1 | 0 | 12
38960.5514 | 1 | 0 | 12
38960.5519 | 1 | 0 | 12
38960.5523 | 1 | 0 | 12
38960.5528 | 1 | 0 | 12
38960.5533 | 1 | 0 | 12
38960.5538 | 1 | 0 | 12
38960.5543 | 1 | 0 | 12
38960.5548 | 1 | 0 | 12
38960.5553 | 1 | 0 | 12
38960.5557 | 1 | 0 | 12
38960.5562 | 1 | 0 | 12
38960.5567 | 1 | 0 | 12
38960.5572 | 1 | 0 | 12
38960.5577 | 1 | 0 | 12
38960.5582 | 1 | 0 | 12
38960.5587 | 1 | 0 | 12
38960.5591 | 1 | 0 | 12
38960.5596 | 124 | 0 | 12
38960.5601 | 1786 | 0 | 12
38960.5606 | 1947 | 0 | 12
38960.5611 | 2170 | 0 | 12
38960.5616 | 2333 | 0 | 12
38960.5621 | 2210 | 0 | 12
38960.5625 | 2152 | 0 | 12
38960.563 | 1832 | 0 | 12
38960.5635 | 2171 | 0 | 12
38960.564 | 2017 | 0 | 12
38960.5645 | 2288 | 0 | 12
38960.565 | 1963 | 0 | 12
38960.5655 | 2081 | 0 | 12
38960.5659 | 2308 | 0 | 12
38960.5664 | 2178 | 0 | 12
38960.5669 | 2453 | 0 | 12
38960.5674 | 2302 | 0 | 12
38960.5679 | 1948 | 0 | 12
38960.5684 | 2219 | 0 | 12
38960.5689 | 1913 | 0 | 12
38960.5694 | 2430 | 0 | 12
38960.5698 | 2000 | 0 | 12
38960.5703 | 2338 | 0 | 12
38960.5708 | 2375 | 0 | 12
38960.5713 | 1935 | 0 | 12
38960.5718 | 2426 | 0 | 12
38960.5723 | 2253 | 0 | 12
38960.5728 | 1970 | 0 | 12
38960.5732 | 2112 | 0 | 12
38960.5737 | 1899 | 0 | 12
38960.5742 | 2321 | 0 | 12
38960.5747 | 2140 | 0 | 12
38960.5752 | 1912 | 0 | 12
38960.5757 | 2311 | 0 | 12
12
38960.5392 | 1 | 1 | 13
38960.5397 | 1 | 0 | 13
38960.5402 | 1 | 0 | 13
38960.5407 | 1 | 0 | 13
38960.5412 | 1 | 0 | 13
38960.5417 | 1 | 0 | 13
38960.5421 | 1 | 0 | 13
38960.5426 | 1 | 0 | 13
38960.5431 | 1 | 0 | 13
38960.5436 | 1 | 0 | 13
38960.5441 | 1 | 0 | 13
38960.5446 | 1 | 0 | 13
38960.5451 | 1 | 0 | 13
38960.5455 | 1 | 0 | 13
38960.546 | 1 | 0 | 13
38960.5465 | 1 | 0 | 13
38960.547 | 1 | 0 | 13
38960.5475 | 1 | 0 | 13
38960.548 | 1 | 0 | 13
38960.5485 | 1 | 0 | 13
38960.5489 | 1 | 0 | 13
38960.5494 | 1 | 0 | 13
38960.5499 | 1 | 0 | 13
38960.5504 | 1 | 0 | 13
38960.5509 | 1 | 0 | 13
38960.5514 | 1 | 0 | 13
38960.5519 | 1 | 0 | 13
38960.5523 | 1 | 0 | 13
38960.5528 | 1 | 0 | 13
38960.5533 | 1 | 0 | 13
38960.5538 | 1 | 0 | 13
38960.5543 | 1 | 0 | 13
38960.5548 | 1 | 0 | 13
38960.5553 | 1 | 0 | 13
38960.5558 | 1 | 0 | 13
38960.5562 | 1 | 0 | 13
38960.5567 | 1 | 0 | 13
38960.5572 | 1 | 0 | 13
38960.5577 | 1 | 0 | 13
38960.5582 | 1 | 0 | 13
38960.5587 | 1 | 0 | 13
38960.5592 | 1 | 0 | 13
38960.5596 | 1 | 0 | 13
38960.5601 | 1 | 0 | 13
38960.5606 | 2 | 0 | 13
38960.5611 | 2 | 0 | 13
38960.5616 | 2 | 0 | 13
38960.5621 | 2 | 0 | 13
38960.5626 | 2 | 0 | 13
38960.563 | 2 | 0 | 13
38960.5635 | 2 | 0 | 13
38960.564 | 2 | 0 | 13
38960.5645 | 2 | 0 | 13
38960.565 | 2 | 0 | 13
38960.5655 | 2 | 0 | 13
38960.566 | 2 | 0 | 13
38960.5664 | 3 | 0 | 13
38960.5669 | 2 | 0 | 13
38960.5674 | 2 | 0 | 13
38960.5679 | 3 | 0 | 13
38960.5684 | 3 | 0 | 13
38960.5689 | 4 | 0 | 13
38960.5694 | 5 | 0 | 13
38960.5698 | 9 | 0 | 13
38960.5703 | 15 | 0 | 13
38960.5708 | 20 | 0 | 13
38960.5713 | 27 | 0 | 13
38960.5718 | 39 | 0 | 13
38960.5723 | 46 | 0 | 13
38960.5728 | 40 | 0 | 13
38960.5733 | 43 | 0 | 13
38960.5737 | 35 | 0 | 13
38960.5742 | 28 | 0 | 13
38960.5747 | 20 | 0 | 13
38960.5752 | 18 | 0 | 13
38960.5757 | 10 | 0 | 13
13
38960.5392 | 1 | 0 | 14
38960.5397 | 1 | 0 | 14
38960.5402 | 1 | 0 | 14
38960.5407 | 1 | 0 | 14
38960.5412 | 1 | 0 | 14
38960.5417 | 1 | 0 | 14
38960.5422 | 1 | 0 | 14
38960.5427 | 1 | 0 | 14
38960.5431 | 1 | 0 | 14
38960.5436 | 1 | 0 | 14
38960.5441 | 1 | 0 | 14
38960.5446 | 1 | 0 | 14
38960.5451 | 1 | 1 | 14
38960.5456 | 1 | 0 | 14
38960.5461 | 1 | 0 | 14
38960.5465 | 1 | 0 | 14
38960.547 | 1 | 0 | 14
38960.5475 | 1 | 0 | 14
38960.548 | 1 | 0 | 14
38960.5485 | 1 | 0 | 14
38960.549 | 1 | 0 | 14
38960.5495 | 1 | 0 | 14
38960.5499 | 1 | 0 | 14
38960.5504 | 1 | 0 | 14
38960.5509 | 1 | 0 | 14
38960.5514 | 1 | 0 | 14
38960.5519 | 1 | 0 | 14
38960.5524 | 1 | 0 | 14
38960.5529 | 1 | 0 | 14
38960.5533 | 1 | 0 | 14
38960.5538 | 1 | 0 | 14
38960.5543 | 1 | 0 | 14
38960.5548 | 1 | 0 | 14
38960.5553 | 1 | 0 | 14
38960.5558 | 1 | 0 | 14
38960.5563 | 1 | 0 | 14
38960.5567 | 1 | 0 | 14
38960.5572 | 1 | 0 | 14
38960.5577 | 1 | 0 | 14
38960.5582 | 1 | 0 | 14
38960.5587 | 1 | 0 | 14
38960.5592 | 2 | 0 | 14
38960.5597 | 1 | 0 | 14
38960.5601 | 2 | 0 | 14
38960.5606 | 1 | 0 | 14
38960.5611 | 2 | 0 | 14
38960.5616 | 1 | 0 | 14
38960.5621 | 2 | 0 | 14
38960.5626 | 1 | 0 | 14
38960.5631 | 1 | 0 | 14
38960.5635 | 2 | 0 | 14
38960.564 | 2 | 0 | 14
38960.5645 | 2 | 0 | 14
38960.565 | 2 | 0 | 14
38960.5655 | 2 | 0 | 14
38960.566 | 2 | 0 | 14
38960.5665 | 2 | 0 | 14
38960.5669 | 2 | 0 | 14
38960.5674 | 2 | 0 | 14
38960.5679 | 2 | 0 | 14
38960.5684 | 3 | 0 | 14
38960.5689 | 4 | 0 | 14
38960.5694 | 5 | 0 | 14
38960.5699 | 10 | 0 | 14
38960.5703 | 14 | 0 | 14
38960.5708 | 22 | 0 | 14
38960.5713 | 29 | 0 | 14
38960.5718 | 41 | 0 | 14
38960.5723 | 39 | 0 | 14
38960.5728 | 45 | 0 | 14
38960.5733 | 38 | 0 | 14
38960.5738 | 37 | 0 | 14
38960.5742 | 33 | 0 | 14
38960.5747 | 20 | 0 | 14
38960.5752 | 15 | 0 | 14
38960.5757 | 11 | 0 | 14
14
38960.5393 | 1 | 0 | 15
38960.5397 | 1 | 1 | 15
38960.5402 | 1 | 0 | 15
38960.5407 | 1 | 0 | 15
38960.5412 | 1 | 0 | 15
38960.5417 | 1 | 0 | 15
38960.5422 | 1 | 0 | 15
38960.5427 | 1 | 0 | 15
38960.5431 | 1 | 0 | 15
38960.5436 | 1 | 0 | 15
38960.5441 | 1 | 0 | 15
38960.5446 | 1 | 0 | 15
38960.5451 | 1 | 0 | 15
38960.5456 | 1 | 0 | 15
38960.5461 | 1 | 0 | 15
38960.5466 | 1 | 0 | 15
38960.547 | 1 | 0 | 15
38960.5475 | 1 | 0 | 15
38960.548 | 1 | 0 | 15
38960.5485 | 1 | 0 | 15
38960.549 | 1 | 0 | 15
38960.5495 | 1 | 0 | 15
38960.55 | 1 | 0 | 15
38960.5504 | 1 | 0 | 15
38960.5509 | 1 | 0 | 15
38960.5514 | 1 | 0 | 15
38960.5519 | 1 | 0 | 15
38960.5524 | 1 | 0 | 15
38960.5529 | 1 | 0 | 15
38960.5534 | 1 | 0 | 15
38960.5538 | 1 | 0 | 15
38960.5543 | 1 | 0 | 15
38960.5548 | 1 | 0 | 15
38960.5553 | 1 | 0 | 15
38960.5558 | 1 | 0 | 15
38960.5563 | 1 | 0 | 15
38960.5568 | 1 | 0 | 15
38960.5572 | 1 | 0 | 15
38960.5577 | 1 | 0 | 15
38960.5582 | 1 | 0 | 15
38960.5587 | 1 | 0 | 15
38960.5592 | 1 | 0 | 15
38960.5597 | 1 | 0 | 15
38960.5602 | 2 | 0 | 15
38960.5606 | 2 | 0 | 15
38960.5611 | 2 | 0 | 15
38960.5616 | 2 | 0 | 15
38960.5621 | 2 | 0 | 15
38960.5626 | 2 | 0 | 15
38960.5631 | 2 | 0 | 15
38960.5636 | 2 | 0 | 15
38960.5641 | 2 | 0 | 15
38960.5645 | 2 | 0 | 15
38960.565 | 2 | 0 | 15
38960.5655 | 2 | 0 | 15
38960.566 | 2 | 0 | 15
38960.5665 | 2 | 0 | 15
38960.567 | 2 | 0 | 15
38960.5675 | 2 | 0 | 15
38960.5679 | 2 | 0 | 15
38960.5684 | 3 | 0 | 15
38960.5689 | 5 | 0 | 15
38960.5694 | 6 | 0 | 15
38960.5699 | 9 | 0 | 15
38960.5704 | 15 | 0 | 15
38960.5709 | 23 | 0 | 15
38960.5713 | 30 | 0 | 15
38960.5718 | 40 | 0 | 15
38960.5723 | 43 | 0 | 15
38960.5728 | 51 | 0 | 15
38960.5733 | 45 | 0 | 15
38960.5738 | 42 | 0 | 15
38960.5743 | 28 | 0 | 15
38960.5747 | 24 | 0 | 15
38960.5752 | 20 | 0 | 15
38960.5757 | 11 | 0 | 15
15
38960.5393 | 1 | 0 | 16
38960.5398 | 1 | 0 | 16
38960.5403 | 1 | 0 | 16
38960.5407 | 1 | 1 | 16
38960.5412 | 1 | 0 | 16
38960.5417 | 1 | 0 | 16
38960.5422 | 1 | 0 | 16
38960.5427 | 1 | 0 | 16
38960.5432 | 1 | 0 | 16
38960.5436 | 1 | 0 | 16
38960.5441 | 1 | 0 | 16
38960.5446 | 1 | 0 | 16
38960.5451 | 1 | 0 | 16
38960.5456 | 1 | 0 | 16
38960.5461 | 1 | 0 | 16
38960.5466 | 1 | 0 | 16
38960.547 | 1 | 0 | 16
38960.5475 | 1 | 0 | 16
38960.548 | 1 | 0 | 16
38960.5485 | 1 | 0 | 16
38960.549 | 1 | 0 | 16
38960.5495 | 1 | 0 | 16
38960.55 | 1 | 0 | 16
38960.5505 | 1 | 0 | 16
38960.5509 | 1 | 0 | 16
38960.5514 | 1 | 0 | 16
38960.5519 | 1 | 0 | 16
38960.5524 | 1 | 0 | 16
38960.5529 | 1 | 0 | 16
38960.5534 | 1 | 0 | 16
38960.5539 | 1 | 0 | 16
38960.5543 | 1 | 0 | 16
38960.5548 | 1 | 0 | 16
38960.5553 | 1 | 0 | 16
38960.5558 | 1 | 0 | 16
38960.5563 | 1 | 0 | 16
38960.5568 | 1 | 0 | 16
38960.5573 | 1 | 0 | 16
38960.5577 | 1 | 0 | 16
38960.5582 | 1 | 0 | 16
38960.5587 | 1 | 1 | 16
38960.5592 | 1 | 0 | 16
38960.5597 | 1 | 0 | 16
38960.5602 | 2 | 0 | 16
38960.5607 | 3 | 0 | 16
38960.5611 | 1825 | 0 | 16
38960.5616 | 1919 | 0 | 16
38960.5621 | 1823 | 0 | 16
38960.5626 | 2227 | 0 | 16
38960.5631 | 1929 | 0 | 16
38960.5636 | 2346 | 0 | 16
38960.5641 | 1946 | 0 | 16
38960.5645 | 2074 | 0 | 16
38960.565 | 1850 | 0 | 16
38960.5655 | 2102 | 0 | 16
38960.566 | 2000 | 0 | 16
38960.5665 | 2105 | 0 | 16
38960.567 | 1923 | 0 | 16
38960.5675 | 2320 | 0 | 16
38960.568 | 2324 | 0 | 16
38960.5684 | 2174 | 0 | 16
38960.5689 | 1986 | 0 | 16
38960.5694 | 2103 | 0 | 16
38960.5699 | 1967 | 0 | 16
38960.5704 | 1890 | 0 | 16
38960.5709 | 2050 | 0 | 16
38960.5714 | 1995 | 0 | 16
38960.5718 | 1991 | 0 | 16
38960.5723 | 2250 | 0 | 16
38960.5728 | 2415 | 0 | 16
38960.5733 | 2377 | 0 | 16
38960.5738 | 2415 | 0 | 16
38960.5743 | 1884 | 0 | 16
38960.5748 | 2158 | 0 | 16
38960.5752 | 2002 | 0 | 16
38960.5757 | 2128 | 0 | 16
16
38960.5393 | 1 | 1 | 17
38960.5398 | 1 | 1 | 17
38960.5403 | 2 | 0 | 17
38960.5408 | 1 | 0 | 17
38960.5412 | 1 | 0 | 17
38960.5417 | 1 | 0 | 17
38960.5422 | 1 | 0 | 17
38960.5427 | 1 | 0 | 17
38960.5432 | 1 | 0 | 17
38960.5437 | 1 | 0 | 17
38960.5442 | 1 | 0 | 17
38960.5446 | 1 | 0 | 17
38960.5451 | 1 | 0 | 17
38960.5456 | 1 | 0 | 17
38960.5461 | 1 | 0 | 17
38960.5466 | 1 | 0 | 17
38960.5471 | 1 | 0 | 17
38960.5476 | 1 | 0 | 17
38960.548 | 1 | 0 | 17
38960.5485 | 1 | 0 | 17
38960.549 | 1 | 0 | 17
38960.5495 | 1 | 0 | 17
38960.55 | 1 | 0 | 17
38960.5505 | 1 | 0 | 17
38960.551 | 1 | 0 | 17
38960.5514 | 1 | 1 | 17
38960.5519 | 1 | 0 | 17
38960.5524 | 1 | 0 | 17
38960.5529 | 1 | 0 | 17
38960.5534 | 1 | 0 | 17
38960.5539 | 1 | 0 | 17
38960.5544 | 1 | 0 | 17
38960.5548 | 1 | 0 | 17
38960.5553 | 1 | 0 | 17
38960.5558 | 1 | 0 | 17
38960.5563 | 1 | 0 | 17
38960.5568 | 1 | 0 | 17
38960.5573 | 1 | 0 | 17
38960.5578 | 1 | 0 | 17
38960.5583 | 1 | 0 | 17
38960.5587 | 1 | 0 | 17
38960.5592 | 1 | 0 | 17
38960.5597 | 1 | 0 | 17
38960.5602 | 1 | 0 | 17
38960.5607 | 2 | 0 | 17
38960.5612 | 2 | 0 | 17
38960.5617 | 2 | 1 | 17
38960.5621 | 2 | 0 | 17
38960.5626 | 2 | 0 | 17
38960.5631 | 2 | 0 | 17
38960.5636 | 2 | 0 | 17
38960.5641 | 2 | 0 | 17
38960.5646 | 2 | 0 | 17
38960.5651 | 2 | 0 | 17
38960.5655 | 1 | 0 | 17
38960.566 | 2 | 0 | 17
38960.5665 | 2 | 0 | 17
38960.567 | 2 | 0 | 17
38960.5675 | 2 | 0 | 17
38960.568 | 3 | 0 | 17
38960.5685 | 3 | 0 | 17
38960.5689 | 4 | 0 | 17
38960.5694 | 6 | 0 | 17
38960.5699 | 8 | 0 | 17
38960.5704 | 15 | 0 | 17
38960.5709 | 22 | 0 | 17
38960.5714 | 29 | 0 | 17
38960.5719 | 40 | 0 | 17
38960.5723 | 47 | 0 | 17
38960.5728 | 42 | 0 | 17
38960.5733 | 46 | 0 | 17
38960.5738 | 39 | 0 | 17
38960.5743 | 29 | 0 | 17
38960.5748 | 25 | 0 | 17
38960.5753 | 16 | 0 | 17
38960.5757 | 12 | 0 | 17
17
38960.5393 | 1 | 0 | 18
38960.5398 | 1 | 0 | 18
38960.5403 | 1 | 0 | 18
38960.5408 | 1 | 0 | 18
38960.5413 | 1 | 0 | 18
38960.5417 | 1 | 0 | 18
38960.5422 | 1 | 0 | 18
38960.5427 | 1 | 0 | 18
38960.5432 | 1 | 0 | 18
38960.5437 | 1 | 0 | 18
38960.5442 | 1 | 0 | 18
38960.5447 | 1 | 0 | 18
38960.5451 | 1 | 0 | 18
38960.5456 | 1 | 0 | 18
38960.5461 | 1 | 0 | 18
38960.5466 | 1 | 0 | 18
38960.5471 | 1 | 0 | 18
38960.5476 | 1 | 0 | 18
38960.5481 | 1 | 0 | 18
38960.5485 | 1 | 0 | 18
38960.549 | 1 | 0 | 18
38960.5495 | 1 | 0 | 18
38960.55 | 1 | 0 | 18
38960.5505 | 1 | 0 | 18
38960.551 | 1 | 0 | 18
38960.5515 | 1 | 1 | 18
38960.5519 | 1 | 0 | 18
38960.5524 | 1 | 0 | 18
38960.5529 | 1 | 0 | 18
38960.5534 | 1 | 0 | 18
38960.5539 | 1 | 0 | 18
38960.5544 | 1 | 0 | 18
38960.5549 | 1 | 0 | 18
38960.5553 | 1 | 0 | 18
38960.5558 | 1 | 0 | 18
38960.5563 | 1 | 0 | 18
38960.5568 | 1 | 0 | 18
38960.5573 | 1 | 0 | 18
38960.5578 | 1 | 0 | 18
38960.5583 | 1 | 0 | 18
38960.5587 | 1 | 0 | 18
38960.5592 | 1 | 0 | 18
38960.5597 | 1 | 0 | 18
38960.5602 | 1 | 0 | 18
38960.5607 | 1 | 0 | 18
38960.5612 | 2 | 0 | 18
38960.5617 | 2013 | 0 | 18
38960.5622 | 2245 | 0 | 18
38960.5626 | 2238 | 0 | 18
38960.5631 | 2339 | 0 | 18
38960.5636 | 2365 | 0 | 18
38960.5641 | 2004 | 0 | 18
38960.5646 | 2436 | 0 | 18
38960.5651 | 2426 | 0 | 18
38960.5656 | 2206 | 0 | 18
38960.566 | 2084 | 0 | 18
38960.5665 | 2330 | 0 | 18
38960.567 | 2087 | 0 | 18
38960.5675 | 2309 | 0 | 18
38960.568 | 2316 | 0 | 18
38960.5685 | 1957 | 0 | 18
38960.569 | 1953 | 0 | 18
38960.5694 | 2285 | 0 | 18
38960.5699 | 2432 | 0 | 18
38960.5704 | 2414 | 0 | 18
38960.5709 | 2247 | 0 | 18
38960.5714 | 1892 | 0 | 18
38960.5719 | 2157 | 0 | 18
38960.5724 | 2114 | 0 | 18
38960.5728 | 2277 | 0 | 18
38960.5733 | 2402 | 0 | 18
38960.5738 | 2430 | 0 | 18
38960.5743 | 2005 | 0 | 18
38960.5748 | 1986 | 0 | 18
38960.5753 | 2369 | 0 | 18
38960.5758 | 2028 | 0 | 18
18
38960.5393 | 1 | 1 | 19
38960.5398 | 1 | 0 | 19
38960.5403 | 1 | 0 | 19
38960.5408 | 1 | 0 | 19
38960.5413 | 1 | 0 | 19
38960.5418 | 1 | 0 | 19
38960.5422 | 1 | 0 | 19
38960.5427 | 1 | 0 | 19
38960.5432 | 2 | 0 | 19
38960.5437 | 1 | 0 | 19
38960.5442 | 1 | 0 | 19
38960.5447 | 1 | 0 | 19
38960.5452 | 1 | 0 | 19
38960.5456 | 1 | 0 | 19
38960.5461 | 1 | 0 | 19
38960.5466 | 1 | 0 | 19
38960.5471 | 1 | 0 | 19
38960.5476 | 1 | 0 | 19
38960.5481 | 1 | 0 | 19
38960.5486 | 1 | 0 | 19
38960.5491 | 1 | 0 | 19
38960.5495 | 1 | 0 | 19
38960.55 | 1 | 0 | 19
38960.5505 | 1 | 0 | 19
38960.551 | 1 | 0 | 19
38960.5515 | 1 | 0 | 19
38960.552 | 1 | 0 | 19
38960.5525 | 1 | 0 | 19
38960.5529 | 1 | 0 | 19
38960.5534 | 1 | 0 | 19
38960.5539 | 1 | 0 | 19
38960.5544 | 1 | 0 | 19
38960.5549 | 1 | 0 | 19
38960.5554 | 1 | 0 | 19
38960.5559 | 1 | 0 | 19
38960.5563 | 1 | 0 | 19
38960.5568 | 1 | 0 | 19
38960.5573 | 1 | 0 | 19
38960.5578 | 1 | 0 | 19
38960.5583 | 1 | 0 | 19
38960.5588 | 1 | 0 | 19
38960.5593 | 1 | 0 | 19
38960.5597 | 648 | 0 | 19
38960.5602 | 1756 | 0 | 19
38960.5607 | 2161 | 101 | 19
38960.5612 | 2319 | 1 | 19
38960.5617 | 2047 | 0 | 19
38960.5622 | 2329 | 0 | 19
38960.5627 | 2493 | 0 | 19
38960.5631 | 1878 | 88 | 19
38960.5636 | 1874 | 56 | 19
38960.5641 | 2068 | 4 | 19
38960.5646 | 2044 | 1 | 19
38960.5651 | 1940 | 1 | 19
38960.5656 | 2432 | 1 | 19
38960.5661 | 2205 | 1 | 19
38960.5665 | 2306 | 0 | 19
38960.567 | 1970 | 0 | 19
38960.5675 | 2179 | 0 | 19
38960.568 | 1962 | 0 | 19
38960.5685 | 2076 | 0 | 19
38960.569 | 2451 | 0 | 19
38960.5695 | 2414 | 0 | 19
38960.5699 | 2468 | 0 | 19
38960.5704 | 2070 | 0 | 19
38960.5709 | 2358 | 0 | 19
38960.5714 | 2211 | 0 | 19
38960.5719 | 2071 | 0 | 19
38960.5724 | 2461 | 0 | 19
38960.5729 | 1962 | 0 | 19
38960.5733 | 2399 | 0 | 19
38960.5738 | 1839 | 32 | 19
38960.5743 | 2126 | 0 | 19
38960.5748 | 1932 | 0 | 19
38960.5753 | 2396 | 0 | 19
38960.5758 | 1990 | 0 | 19
19
38960.5393 | 1 | 0 | 20
38960.5398 | 1 | 0 | 20
38960.5403 | 1 | 0 | 20
38960.5408 | 1 | 0 | 20
38960.5413 | 1 | 0 | 20
38960.5418 | 1 | 0 | 20
38960.5423 | 1 | 0 | 20
38960.5427 | 1 | 0 | 20
38960.5432 | 1 | 0 | 20
38960.5437 | 1 | 0 | 20
38960.5442 | 2 | 0 | 20
38960.5447 | 1 | 0 | 20
38960.5452 | 1 | 0 | 20
38960.5457 | 1 | 0 | 20
38960.5461 | 1 | 0 | 20
38960.5466 | 2 | 0 | 20
38960.5471 | 1 | 0 | 20
38960.5476 | 2 | 0 | 20
38960.5481 | 1 | 0 | 20
38960.5486 | 1 | 0 | 20
38960.5491 | 1 | 0 | 20
38960.5495 | 1 | 0 | 20
38960.55 | 1 | 0 | 20
38960.5505 | 1 | 0 | 20
38960.551 | 1 | 0 | 20
38960.5515 | 1 | 0 | 20
38960.552 | 1 | 0 | 20
38960.5525 | 1 | 0 | 20
38960.553 | 1 | 0 | 20
38960.5534 | 1 | 0 | 20
38960.5539 | 1 | 0 | 20
38960.5544 | 1 | 0 | 20
38960.5549 | 1 | 0 | 20
38960.5554 | 1 | 0 | 20
38960.5559 | 1 | 0 | 20
38960.5564 | 1 | 0 | 20
38960.5568 | 1 | 0 | 20
38960.5573 | 1 | 0 | 20
38960.5578 | 1 | 0 | 20
38960.5583 | 1 | 0 | 20
38960.5588 | 1 | 0 | 20
38960.5593 | 1 | 0 | 20
38960.5598 | 208 | 0 | 20
38960.5602 | 1534 | 0 | 20
38960.5607 | 2091 | 79 | 20
38960.5612 | 2150 | 0 | 20
38960.5617 | 2149 | 0 | 20
38960.5622 | 2213 | 0 | 20
38960.5627 | 2269 | 0 | 20
38960.5632 | 2143 | 90 | 20
38960.5636 | 1922 | 48 | 20
38960.5641 | 1980 | 1 | 20
38960.5646 | 2428 | 0 | 20
38960.5651 | 2305 | 1 | 20
38960.5656 | 2386 | 0 | 20
38960.5661 | 2105 | 0 | 20
38960.5666 | 2345 | 0 | 20
38960.567 | 2282 | 0 | 20
38960.5675 | 2180 | 0 | 20
38960.568 | 2509 | 0 | 20
38960.5685 | 2228 | 0 | 20
38960.569 | 2477 | 0 | 20
38960.5695 | 2415 | 0 | 20
38960.57 | 2104 | 0 | 20
38960.5705 | 1961 | 0 | 20
38960.5709 | 2178 | 0 | 20
38960.5714 | 2107 | 0 | 20
38960.5719 | 2495 | 0 | 20
38960.5724 | 1990 | 0 | 20
38960.5729 | 2231 | 0 | 20
38960.5734 | 1943 | 0 | 20
38960.5739 | 2370 | 31 | 20
38960.5743 | 2074 | 0 | 20
38960.5748 | 2185 | 0 | 20
38960.5753 | 2306 | 1 | 20
38960.5758 | 2082 | 0 | 20
20
38960.5394 | 1 | 0 | 21
38960.5398 | 1 | 0 | 21
38960.5403 | 1 | 0 | 21
38960.5408 | 1 | 0 | 21
38960.5413 | 1 | 0 | 21
38960.5418 | 2 | 0 | 21
38960.5423 | 1 | 0 | 21
38960.5428 | 1 | 0 | 21
38960.5432 | 1 | 0 | 21
38960.5437 | 1 | 0 | 21
38960.5442 | 1 | 0 | 21
38960.5447 | 1 | 0 | 21
38960.5452 | 1 | 0 | 21
38960.5457 | 1 | 0 | 21
38960.5462 | 1 | 0 | 21
38960.5466 | 1 | 0 | 21
38960.5471 | 1 | 0 | 21
38960.5476 | 1 | 0 | 21
38960.5481 | 1 | 0 | 21
38960.5486 | 1 | 0 | 21
38960.5491 | 1 | 0 | 21
38960.5496 | 1 | 0 | 21
38960.55 | 1 | 0 | 21
38960.5505 | 1 | 0 | 21
38960.551 | 1 | 0 | 21
38960.5515 | 1 | 0 | 21
38960.552 | 1 | 0 | 21
38960.5525 | 1 | 0 | 21
38960.553 | 1 | 0 | 21
38960.5534 | 1 | 0 | 21
38960.5539 | 1 | 0 | 21
38960.5544 | 1 | 0 | 21
38960.5549 | 1 | 0 | 21
38960.5554 | 1 | 0 | 21
38960.5559 | 2 | 0 | 21
38960.5564 | 1 | 0 | 21
38960.5569 | 1 | 0 | 21
38960.5573 | 1 | 0 | 21
38960.5578 | 1 | 0 | 21
38960.5583 | 1 | 0 | 21
38960.5588 | 1 | 0 | 21
38960.5593 | 1 | 0 | 21
38960.5598 | 1907 | 0 | 21
38960.5603 | 1966 | 0 | 21
38960.5607 | 2353 | 0 | 21
38960.5612 | 2173 | 0 | 21
38960.5617 | 2005 | 0 | 21
38960.5622 | 2104 | 0 | 21
38960.5627 | 2494 | 0 | 21
38960.5632 | 1898 | 0 | 21
38960.5637 | 1887 | 0 | 21
38960.5641 | 2098 | 0 | 21
38960.5646 | 2195 | 0 | 21
38960.5651 | 2335 | 0 | 21
38960.5656 | 2116 | 0 | 21
38960.5661 | 2398 | 0 | 21
38960.5666 | 2305 | 1 | 21
38960.5671 | 2142 | 0 | 21
38960.5675 | 2468 | 0 | 21
38960.568 | 1988 | 0 | 21
38960.5685 | 1988 | 0 | 21
38960.569 | 2143 | 0 | 21
38960.5695 | 1926 | 0 | 21
38960.57 | 2150 | 0 | 21
38960.5705 | 2353 | 0 | 21
38960.5709 | 2323 | 0 | 21
38960.5714 | 2269 | 0 | 21
38960.5719 | 2085 | 0 | 21
38960.5724 | 2428 | 0 | 21
38960.5729 | 1979 | 0 | 21
38960.5734 | 2450 | 0 | 21
38960.5739 | 1838 | 0 | 21
38960.5744 | 2004 | 0 | 21
38960.5748 | 2425 | 0 | 21
38960.5753 | 1932 | 0 | 21
38960.5758 | 2301 | 0 | 21
21
38960.5394 | 1 | 0 | 22
38960.5399 | 1 | 0 | 22
38960.5403 | 1 | 0 | 22
38960.5408 | 1 | 0 | 22
38960.5413 | 1 | 0 | 22
38960.5418 | 1 | 0 | 22
38960.5423 | 1 | 0 | 22
38960.5428 | 1 | 0 | 22
38960.5433 | 1 | 0 | 22
38960.5437 | 1 | 0 | 22
38960.5442 | 1 | 0 | 22
38960.5447 | 1 | 0 | 22
38960.5452 | 1 | 0 | 22
38960.5457 | 1 | 0 | 22
38960.5462 | 1 | 0 | 22
38960.5467 | 2 | 0 | 22
38960.5472 | 1 | 0 | 22
38960.5476 | 1 | 0 | 22
38960.5481 | 1 | 0 | 22
38960.5486 | 1 | 0 | 22
38960.5491 | 1 | 0 | 22
38960.5496 | 1 | 0 | 22
38960.5501 | 1 | 0 | 22
38960.5506 | 1 | 0 | 22
38960.551 | 1 | 0 | 22
38960.5515 | 1 | 0 | 22
38960.552 | 1 | 0 | 22
38960.5525 | 1 | 0 | 22
38960.553 | 1 | 0 | 22
38960.5535 | 2 | 0 | 22
38960.554 | 1 | 1 | 22
38960.5544 | 1 | 0 | 22
38960.5549 | 1 | 0 | 22
38960.5554 | 1 | 0 | 22
38960.5559 | 1 | 0 | 22
38960.5564 | 1 | 0 | 22
38960.5569 | 1 | 0 | 22
38960.5574 | 1 | 0 | 22
38960.5578 | 1 | 0 | 22
38960.5583 | 1 | 0 | 22
38960.5588 | 1 | 0 | 22
38960.5593 | 1 | 0 | 22
38960.5598 | 1 | 0 | 22
38960.5603 | 2 | 0 | 22
38960.5608 | 1703 | 0 | 22
38960.5612 | 2282 | 0 | 22
38960.5617 | 1783 | 0 | 22
38960.5622 | 2094 | 0 | 22
38960.5627 | 2134 | 0 | 22
38960.5632 | 2210 | 0 | 22
38960.5637 | 2101 | 0 | 22
38960.5642 | 1958 | 0 | 22
38960.5647 | 2242 | 0 | 22
38960.5651 | 2183 | 0 | 22
38960.5656 | 2210 | 0 | 22
38960.5661 | 2038 | 0 | 22
38960.5666 | 2014 | 0 | 22
38960.5671 | 2140 | 0 | 22
38960.5676 | 2237 | 0 | 22
38960.5681 | 2097 | 0 | 22
38960.5685 | 1926 | 0 | 22
38960.569 | 1949 | 0 | 22
38960.5695 | 1959 | 0 | 22
38960.57 | 1898 | 0 | 22
38960.5705 | 2332 | 0 | 22
38960.571 | 2398 | 0 | 22
38960.5714 | 1903 | 0 | 22
38960.5719 | 2157 | 0 | 22
38960.5724 | 1974 | 0 | 22
38960.5729 | 2330 | 0 | 22
38960.5734 | 2171 | 0 | 22
38960.5739 | 1991 | 0 | 22
38960.5744 | 1904 | 0 | 22
38960.5748 | 2382 | 0 | 22
38960.5753 | 2076 | 0 | 22
38960.5758 | 1989 | 0 | 22
22
38960.5394 | 1 | 0 | 23
38960.5399 | 1 | 0 | 23
38960.5404 | 1 | 0 | 23
38960.5408 | 1 | 0 | 23
38960.5413 | 1 | 0 | 23
38960.5418 | 1 | 0 | 23
38960.5423 | 1 | 0 | 23
38960.5428 | 1 | 0 | 23
38960.5433 | 1 | 0 | 23
38960.5438 | 1 | 1 | 23
38960.5442 | 1 | 0 | 23
38960.5447 | 1 | 0 | 23
38960.5452 | 1 | 0 | 23
38960.5457 | 1 | 0 | 23
38960.5462 | 1 | 0 | 23
38960.5467 | 1 | 0 | 23
38960.5472 | 1 | 0 | 23
38960.5477 | 1 | 0 | 23
38960.5481 | 1 | 0 | 23
38960.5486 | 1 | 0 | 23
38960.5491 | 1 | 0 | 23
38960.5496 | 1 | 0 | 23
38960.5501 | 1 | 0 | 23
38960.5506 | 1 | 0 | 23
38960.5511 | 1 | 0 | 23
38960.5515 | 1 | 0 | 23
38960.552 | 1 | 0 | 23
38960.5525 | 1 | 0 | 23
38960.553 | 1 | 0 | 23
38960.5535 | 1 | 0 | 23
38960.554 | 1 | 0 | 23
38960.5545 | 1 | 0 | 23
38960.5549 | 1 | 0 | 23
38960.5554 | 1 | 0 | 23
38960.5559 | 1 | 0 | 23
38960.5564 | 1 | 0 | 23
38960.5569 | 1 | 0 | 23
38960.5574 | 1 | 0 | 23
38960.5579 | 1 | 0 | 23
38960.5583 | 1 | 0 | 23
38960.5588 | 1 | 0 | 23
38960.5593 | 1 | 0 | 23
38960.5598 | 2112 | 0 | 23
38960.5603 | 2151 | 0 | 23
38960.5608 | 2063 | 0 | 23
38960.5613 | 2309 | 0 | 23
38960.5617 | 2457 | 0 | 23
38960.5622 | 2514 | 0 | 23
38960.5627 | 2094 | 0 | 23
38960.5632 | 2327 | 0 | 23
38960.5637 | 2222 | 0 | 23
38960.5642 | 2396 | 0 | 23
38960.5647 | 2279 | 0 | 23
38960.5652 | 2373 | 0 | 23
38960.5656 | 2414 | 0 | 23
38960.5661 | 2390 | 0 | 23
38960.5666 | 2176 | 0 | 23
38960.5671 | 2237 | 0 | 23
38960.5676 | 2124 | 0 | 23
38960.5681 | 2335 | 0 | 23
38960.5686 | 2417 | 0 | 23
38960.569 | 2385 | 0 | 23
38960.5695 | 2260 | 0 | 23
38960.57 | 1924 | 0 | 23
38960.5705 | 2213 | 0 | 23
38960.571 | 2153 | 0 | 23
38960.5715 | 2270 | 0 | 23
38960.572 | 2358 | 0 | 23
38960.5724 | 2080 | 0 | 23
38960.5729 | 2424 | 0 | 23
38960.5734 | 2418 | 0 | 23
38960.5739 | 2223 | 0 | 23
38960.5744 | 2188 | 0 | 23
38960.5749 | 2400 | 0 | 23
38960.5754 | 2379 | 0 | 23
38960.5758 | 1913 | 0 | 23
23
38960.5394 | 1 | 0 | 24
38960.5399 | 1 | 0 | 24
38960.5404 | 4 | 0 | 24
38960.5409 | 1 | 0 | 24
38960.5414 | 1 | 0 | 24
38960.5418 | 1 | 0 | 24
38960.5423 | 1 | 0 | 24
38960.5428 | 1 | 0 | 24
38960.5433 | 1 | 0 | 24
38960.5438 | 1 | 0 | 24
38960.5443 | 1 | 0 | 24
38960.5448 | 1 | 0 | 24
38960.5452 | 1 | 0 | 24
38960.5457 | 1 | 0 | 24
38960.5462 | 1 | 0 | 24
38960.5467 | 1 | 0 | 24
38960.5472 | 1 | 0 | 24
38960.5477 | 1 | 0 | 24
38960.5482 | 1 | 0 | 24
38960.5486 | 1 | 0 | 24
38960.5491 | 1 | 0 | 24
38960.5496 | 1 | 0 | 24
38960.5501 | 1 | 0 | 24
38960.5506 | 1 | 0 | 24
38960.5511 | 1 | 0 | 24
38960.5516 | 1 | 0 | 24
38960.552 | 1 | 0 | 24
38960.5525 | 1 | 0 | 24
38960.553 | 1 | 0 | 24
38960.5535 | 1 | 0 | 24
38960.554 | 1 | 0 | 24
38960.5545 | 1 | 0 | 24
38960.555 | 1 | 0 | 24
38960.5554 | 1 | 0 | 24
38960.5559 | 1 | 0 | 24
38960.5564 | 1 | 0 | 24
38960.5569 | 1 | 0 | 24
38960.5574 | 1 | 0 | 24
38960.5579 | 1 | 0 | 24
38960.5584 | 1 | 0 | 24
38960.5588 | 1 | 0 | 24
38960.5593 | 1 | 0 | 24
38960.5598 | 1 | 0 | 24
38960.5603 | 2 | 0 | 24
38960.5608 | 905 | 0 | 24
38960.5613 | 24 | 0 | 24
38960.5618 | 1979 | 30 | 24
38960.5622 | 2227 | 0 | 24
38960.5627 | 2352 | 0 | 24
38960.5632 | 2214 | 0 | 24
38960.5637 | 2452 | 0 | 24
38960.5642 | 2401 | 0 | 24
38960.5647 | 2456 | 0 | 24
38960.5652 | 2060 | 0 | 24
38960.5656 | 2188 | 0 | 24
38960.5661 | 1952 | 0 | 24
38960.5666 | 2069 | 0 | 24
38960.5671 | 1997 | 0 | 24
38960.5676 | 2352 | 0 | 24
38960.5681 | 2140 | 0 | 24
38960.5686 | 2025 | 0 | 24
38960.5691 | 2485 | 0 | 24
38960.5695 | 2244 | 0 | 24
38960.57 | 1980 | 0 | 24
38960.5705 | 2035 | 0 | 24
38960.571 | 2025 | 0 | 24
38960.5715 | 2323 | 0 | 24
38960.572 | 2160 | 0 | 24
38960.5725 | 2308 | 0 | 24
38960.5729 | 2143 | 0 | 24
38960.5734 | 1964 | 0 | 24
38960.5739 | 2133 | 0 | 24
38960.5744 | 2152 | 0 | 24
38960.5749 | 2219 | 0 | 24
38960.5754 | 2239 | 0 | 24
38960.5759 | 2078 | 0 | 24
24
38960.5394 | 1 | 0 | 25
38960.5399 | 1 | 0 | 25
38960.5404 | 1 | 0 | 25
38960.5409 | 1 | 0 | 25
38960.5414 | 1 | 0 | 25
38960.5419 | 1 | 0 | 25
38960.5423 | 1 | 0 | 25
38960.5428 | 1 | 0 | 25
38960.5433 | 1 | 0 | 25
38960.5438 | 1 | 0 | 25
38960.5443 | 1 | 0 | 25
38960.5448 | 1 | 0 | 25
38960.5453 | 1 | 0 | 25
38960.5457 | 1 | 0 | 25
38960.5462 | 1 | 0 | 25
38960.5467 | 1 | 0 | 25
38960.5472 | 1 | 0 | 25
38960.5477 | 1 | 0 | 25
38960.5482 | 1 | 0 | 25
38960.5487 | 1 | 0 | 25
38960.5491 | 1 | 0 | 25
38960.5496 | 1 | 0 | 25
38960.5501 | 1 | 0 | 25
38960.5506 | 1 | 0 | 25
38960.5511 | 1 | 0 | 25
38960.5516 | 1 | 0 | 25
38960.5521 | 2 | 0 | 25
38960.5525 | 2 | 0 | 25
38960.553 | 1 | 0 | 25
38960.5535 | 1 | 0 | 25
38960.554 | 1 | 0 | 25
38960.5545 | 1 | 0 | 25
38960.555 | 1 | 0 | 25
38960.5555 | 1 | 0 | 25
38960.5559 | 1 | 0 | 25
38960.5564 | 1 | 0 | 25
38960.5569 | 1 | 0 | 25
38960.5574 | 1 | 0 | 25
38960.5579 | 1 | 0 | 25
38960.5584 | 1 | 0 | 25
38960.5589 | 1 | 0 | 25
38960.5594 | 1 | 0 | 25
38960.5598 | 728 | 0 | 25
38960.5603 | 987 | 0 | 25
38960.5608 | 2346 | 0 | 25
38960.5613 | 2406 | 0 | 25
38960.5618 | 2400 | 0 | 25
38960.5623 | 2078 | 0 | 25
38960.5628 | 2010 | 0 | 25
38960.5632 | 1932 | 0 | 25
38960.5637 | 1935 | 0 | 25
38960.5642 | 2300 | 0 | 25
38960.5647 | 2270 | 0 | 25
38960.5652 | 2001 | 0 | 25
38960.5657 | 2369 | 0 | 25
38960.5662 | 1984 | 0 | 25
38960.5666 | 1961 | 0 | 25
38960.5671 | 2068 | 0 | 25
38960.5676 | 2097 | 0 | 25
38960.5681 | 2175 | 0 | 25
38960.5686 | 2515 | 0 | 25
38960.5691 | 1990 | 0 | 25
38960.5696 | 2497 | 0 | 25
38960.57 | 2243 | 0 | 25
38960.5705 | 1978 | 0 | 25
38960.571 | 1966 | 0 | 25
38960.5715 | 2006 | 0 | 25
38960.572 | 2454 | 0 | 25
38960.5725 | 2503 | 0 | 25
38960.573 | 2431 | 0 | 25
38960.5734 | 2132 | 0 | 25
38960.5739 | 1932 | 0 | 25
38960.5744 | 2477 | 0 | 25
38960.5749 | 2196 | 0 | 25
38960.5754 | 2061 | 0 | 25
38960.5759 | 2041 | 0 | 25
25
38960.5394 | 1 | 0 | 26
38960.5399 | 1 | 0 | 26
38960.5404 | 1 | 0 | 26
38960.5409 | 1 | 0 | 26
38960.5414 | 1 | 0 | 26
38960.5419 | 1 | 0 | 26
38960.5423 | 1 | 0 | 26
38960.5428 | 1 | 0 | 26
38960.5433 | 1 | 0 | 26
38960.5438 | 1 | 0 | 26
38960.5443 | 1 | 0 | 26
38960.5448 | 1 | 0 | 26
38960.5453 | 1 | 0 | 26
38960.5458 | 1 | 0 | 26
38960.5462 | 1 | 0 | 26
38960.5467 | 1 | 0 | 26
38960.5472 | 1 | 0 | 26
38960.5477 | 1 | 0 | 26
38960.5482 | 1 | 0 | 26
38960.5487 | 1 | 0 | 26
38960.5492 | 1 | 0 | 26
38960.5496 | 1 | 0 | 26
38960.5501 | 1 | 0 | 26
38960.5506 | 1 | 0 | 26
38960.5511 | 1 | 0 | 26
38960.5516 | 1 | 0 | 26
38960.5521 | 1 | 0 | 26
38960.5526 | 1 | 0 | 26
38960.553 | 1 | 0 | 26
38960.5535 | 1 | 0 | 26
38960.554 | 1 | 0 | 26
38960.5545 | 1 | 0 | 26
38960.555 | 1 | 0 | 26
38960.5555 | 1 | 0 | 26
38960.556 | 1 | 0 | 26
38960.5564 | 1 | 0 | 26
38960.5569 | 1 | 0 | 26
38960.5574 | 1 | 0 | 26
38960.5579 | 1 | 0 | 26
38960.5584 | 1 | 0 | 26
38960.5589 | 1 | 0 | 26
38960.5594 | 1 | 0 | 26
38960.5598 | 2 | 0 | 26
38960.5603 | 86 | 0 | 26
38960.5608 | 1963 | 0 | 26
38960.5613 | 2211 | 0 | 26
38960.5618 | 1842 | 0 | 26
38960.5623 | 1924 | 0 | 26
38960.5628 | 2334 | 0 | 26
38960.5633 | 2128 | 0 | 26
38960.5637 | 2074 | 0 | 26
38960.5642 | 2219 | 0 | 26
38960.5647 | 2382 | 0 | 26
38960.5652 | 2050 | 0 | 26
38960.5657 | 2126 | 0 | 26
38960.5662 | 1869 | 0 | 26
38960.5667 | 2362 | 0 | 26
38960.5671 | 1965 | 0 | 26
38960.5676 | 1884 | 0 | 26
38960.5681 | 2375 | 0 | 26
38960.5686 | 2099 | 0 | 26
38960.5691 | 2326 | 0 | 26
38960.5696 | 1876 | 0 | 26
38960.5701 | 1923 | 0 | 26
38960.5705 | 1892 | 0 | 26
38960.571 | 1960 | 0 | 26
38960.5715 | 2362 | 0 | 26
38960.572 | 1891 | 0 | 26
38960.5725 | 2232 | 0 | 26
38960.573 | 2112 | 0 | 26
38960.5735 | 2316 | 0 | 26
38960.5739 | 2383 | 0 | 26
38960.5744 | 1923 | 0 | 26
38960.5749 | 2012 | 0 | 26
38960.5754 | 2216 | 0 | 26
38960.5759 | 2074 | 0 | 26
26
38960.5395 | 1 | 0 | 27
38960.5399 | 1 | 0 | 27
38960.5404 | 1 | 0 | 27
38960.5409 | 1 | 0 | 27
38960.5414 | 1 | 0 | 27
38960.5419 | 1 | 0 | 27
38960.5424 | 1 | 0 | 27
38960.5429 | 1 | 0 | 27
38960.5433 | 1 | 0 | 27
38960.5438 | 1 | 0 | 27
38960.5443 | 1 | 0 | 27
38960.5448 | 1 | 0 | 27
38960.5453 | 1 | 0 | 27
38960.5458 | 1 | 0 | 27
38960.5463 | 1 | 0 | 27
38960.5467 | 1 | 0 | 27
38960.5472 | 1 | 0 | 27
38960.5477 | 1 | 0 | 27
38960.5482 | 1 | 0 | 27
38960.5487 | 1 | 0 | 27
38960.5492 | 1 | 0 | 27
38960.5497 | 1 | 0 | 27
38960.5502 | 1 | 0 | 27
38960.5506 | 1 | 0 | 27
38960.5511 | 1 | 0 | 27
38960.5516 | 2 | 0 | 27
38960.5521 | 1 | 0 | 27
38960.5526 | 1 | 0 | 27
38960.5531 | 1 | 0 | 27
38960.5536 | 1 | 0 | 27
38960.554 | 1 | 0 | 27
38960.5545 | 1 | 0 | 27
38960.555 | 1 | 0 | 27
38960.5555 | 1 | 0 | 27
38960.556 | 1 | 0 | 27
38960.5565 | 1 | 0 | 27
38960.557 | 1 | 0 | 27
38960.5574 | 1 | 0 | 27
38960.5579 | 1 | 0 | 27
38960.5584 | 1 | 0 | 27
38960.5589 | 1 | 0 | 27
38960.5599 | 1442 | 0 | 27
38960.5604 | 1068 | 0 | 27
38960.5608 | 2247 | 0 | 27
38960.5613 | 2019 | 0 | 27
38960.5618 | 2149 | 0 | 27
38960.5623 | 2501 | 0 | 27
38960.5628 | 2513 | 0 | 27
38960.5633 | 2322 | 0 | 27
38960.5638 | 1964 | 0 | 27
38960.5647 | 2169 | 0 | 27
38960.5652 | 2496 | 0 | 27
38960.5657 | 2506 | 0 | 27
38960.5662 | 2510 | 0 | 27
38960.5667 | 2469 | 0 | 27
38960.5672 | 2054 | 0 | 27
38960.5677 | 2023 | 0 | 27
38960.5681 | 2330 | 0 | 27
38960.5686 | 2290 | 0 | 27
38960.5691 | 2292 | 0 | 27
38960.5696 | 2155 | 0 | 27
38960.5701 | 2223 | 0 | 27
38960.5706 | 2485 | 0 | 27
38960.571 | 2291 | 0 | 27
38960.5715 | 2501 | 0 | 27
38960.572 | 2470 | 0 | 27
38960.5725 | 2104 | 0 | 27
38960.573 | 2015 | 0 | 27
38960.5735 | 2489 | 0 | 27
38960.574 | 1842 | 0 | 27
38960.5744 | 2436 | 0 | 27
38960.5749 | 2032 | 0 | 27
38960.5754 | 2092 | 0 | 27
38960.5759 | 2293 | 0 | 27
27
38960.5395 | 1 | 0 | 28
38960.54 | 1 | 0 | 28
38960.5404 | 1 | 0 | 28
38960.5409 | 1 | 1 | 28
38960.5414 | 1 | 0 | 28
38960.5419 | 1 | 0 | 28
38960.5424 | 1 | 0 | 28
38960.5429 | 1 | 0 | 28
38960.5434 | 1 | 0 | 28
38960.5438 | 1 | 0 | 28
38960.5443 | 1 | 0 | 28
38960.5448 | 1 | 0 | 28
38960.5453 | 1 | 0 | 28
38960.5458 | 1 | 0 | 28
38960.5463 | 1 | 0 | 28
38960.5468 | 1 | 0 | 28
38960.5472 | 1 | 0 | 28
38960.5477 | 1 | 0 | 28
38960.5482 | 1 | 0 | 28
38960.5487 | 1 | 0 | 28
38960.5492 | 1 | 0 | 28
38960.5497 | 1 | 0 | 28
38960.5502 | 1 | 0 | 28
38960.5506 | 1 | 0 | 28
38960.5511 | 1 | 0 | 28
38960.5516 | 1 | 0 | 28
38960.5521 | 1 | 0 | 28
38960.5526 | 1 | 0 | 28
38960.5531 | 1 | 0 | 28
38960.5536 | 1 | 0 | 28
38960.5541 | 1 | 0 | 28
38960.5545 | 1 | 0 | 28
38960.555 | 1 | 0 | 28
38960.5555 | 1 | 0 | 28
38960.556 | 1 | 0 | 28
38960.5565 | 1 | 0 | 28
38960.557 | 1 | 0 | 28
38960.5575 | 1 | 0 | 28
38960.5579 | 1 | 0 | 28
38960.5584 | 1 | 0 | 28
38960.5589 | 1 | 0 | 28
38960.5594 | 1 | 0 | 28
38960.5599 | 57 | 9 | 28
38960.5604 | 2 | 0 | 28
38960.5609 | 2 | 0 | 28
38960.5613 | 143 | 0 | 28
38960.5618 | 1628 | 17 | 28
38960.5623 | 1868 | 0 | 28
38960.5628 | 2305 | 0 | 28
38960.5633 | 2040 | 0 | 28
38960.5638 | 2051 | 0 | 28
38960.5643 | 2240 | 0 | 28
38960.5647 | 2146 | 0 | 28
38960.5652 | 2052 | 0 | 28
38960.5657 | 1949 | 0 | 28
38960.5662 | 2470 | 0 | 28
38960.5667 | 2232 | 0 | 28
38960.5672 | 2335 | 0 | 28
38960.5677 | 2267 | 0 | 28
38960.5681 | 2301 | 0 | 28
38960.5686 | 2464 | 0 | 28
38960.5691 | 2112 | 0 | 28
38960.5696 | 2101 | 0 | 28
38960.5701 | 2085 | 0 | 28
38960.5706 | 1944 | 0 | 28
38960.5711 | 2426 | 0 | 28
38960.5716 | 1974 | 0 | 28
38960.572 | 1887 | 0 | 28
38960.5725 | 1992 | 0 | 28
38960.573 | 2235 | 0 | 28
38960.5735 | 2445 | 0 | 28
38960.574 | 2426 | 0 | 28
38960.5745 | 2186 | 0 | 28
38960.575 | 1910 | 0 | 28
38960.5754 | 1944 | 0 | 28
38960.5759 | 2451 | 0 | 28
28
38960.5395 | 1 | 0 | 29
38960.54 | 1 | 0 | 29
38960.5405 | 1 | 0 | 29
38960.5409 | 1 | 0 | 29
38960.5414 | 1 | 0 | 29
38960.5419 | 1 | 0 | 29
38960.5424 | 1 | 0 | 29
38960.5429 | 1 | 0 | 29
38960.5434 | 1 | 0 | 29
38960.5439 | 1 | 0 | 29
38960.5444 | 1 | 0 | 29
38960.5448 | 1 | 0 | 29
38960.5453 | 1 | 0 | 29
38960.5458 | 1 | 0 | 29
38960.5463 | 1 | 0 | 29
38960.5468 | 1 | 0 | 29
38960.5473 | 1 | 0 | 29
38960.5478 | 1 | 0 | 29
38960.5482 | 1 | 0 | 29
38960.5487 | 1 | 0 | 29
38960.5492 | 1 | 0 | 29
38960.5497 | 1 | 0 | 29
38960.5502 | 1 | 0 | 29
38960.5507 | 1 | 0 | 29
38960.5512 | 1 | 0 | 29
38960.5516 | 1 | 0 | 29
38960.5521 | 1 | 0 | 29
38960.5526 | 1 | 0 | 29
38960.5531 | 1 | 0 | 29
38960.5536 | 1 | 0 | 29
38960.5541 | 1 | 0 | 29
38960.5546 | 1 | 0 | 29
38960.555 | 1 | 0 | 29
38960.5555 | 1 | 0 | 29
38960.556 | 1 | 0 | 29
38960.5565 | 1 | 0 | 29
38960.557 | 1 | 0 | 29
38960.5575 | 1 | 0 | 29
38960.558 | 963 | 940 | 29
38960.5584 | 884 | 862 | 29
38960.5589 | 877 | 861 | 29
38960.5594 | 347 | 380 | 29
38960.5599 | 629 | 32 | 29
38960.5604 | 33 | 29 | 29
38960.5609 | 2146 | 17 | 29
38960.5614 | 2162 | 0 | 29
38960.5618 | 2086 | 0 | 29
38960.5623 | 2392 | 15 | 29
38960.5628 | 2047 | 0 | 29
38960.5633 | 2196 | 0 | 29
38960.5638 | 2191 | 0 | 29
38960.5643 | 2242 | 0 | 29
38960.5648 | 2202 | 0 | 29
38960.5652 | 2020 | 0 | 29
38960.5657 | 2076 | 0 | 29
38960.5662 | 2358 | 0 | 29
38960.5667 | 1986 | 0 | 29
38960.5672 | 2404 | 0 | 29
38960.5677 | 2273 | 0 | 29
38960.5682 | 2414 | 0 | 29
38960.5686 | 2405 | 0 | 29
38960.5691 | 2318 | 0 | 29
38960.5696 | 2089 | 0 | 29
38960.5701 | 2120 | 0 | 29
38960.5706 | 2305 | 0 | 29
38960.5711 | 2358 | 0 | 29
38960.5716 | 1885 | 0 | 29
38960.572 | 1983 | 0 | 29
38960.5725 | 2419 | 0 | 29
38960.573 | 2281 | 0 | 29
38960.5735 | 1925 | 0 | 29
38960.574 | 2204 | 0 | 29
38960.5745 | 2258 | 0 | 29
38960.575 | 2068 | 0 | 29
38960.5755 | 2069 | 0 | 29
38960.5759 | 2245 | 0 | 29
29
38960.5395 | 1 | 0 | 30
38960.54 | 1 | 0 | 30
38960.5405 | 1 | 0 | 30
38960.541 | 1 | 0 | 30
38960.5414 | 1 | 0 | 30
38960.5419 | 1 | 0 | 30
38960.5424 | 1 | 0 | 30
38960.5429 | 1 | 0 | 30
38960.5434 | 1 | 0 | 30
38960.5439 | 1 | 0 | 30
38960.5444 | 1 | 0 | 30
38960.5448 | 1 | 0 | 30
38960.5453 | 1 | 0 | 30
38960.5458 | 1 | 0 | 30
38960.5463 | 1 | 0 | 30
38960.5468 | 1 | 0 | 30
38960.5473 | 1 | 0 | 30
38960.5478 | 1 | 0 | 30
38960.5483 | 1 | 0 | 30
38960.5487 | 2 | 0 | 30
38960.5492 | 1 | 0 | 30
38960.5497 | 1 | 0 | 30
38960.5502 | 1 | 0 | 30
38960.5507 | 1 | 0 | 30
38960.5512 | 1 | 0 | 30
38960.5517 | 1 | 0 | 30
38960.5521 | 1 | 0 | 30
38960.5526 | 1 | 0 | 30
38960.5531 | 1 | 0 | 30
38960.5536 | 1 | 0 | 30
38960.5541 | 1 | 0 | 30
38960.5546 | 1 | 0 | 30
38960.5551 | 1 | 0 | 30
38960.5555 | 1 | 0 | 30
38960.556 | 1 | 0 | 30
38960.5565 | 1 | 0 | 30
38960.557 | 1 | 0 | 30
38960.5575 | 1 | 0 | 30
38960.558 | 976 | 951 | 30
38960.5585 | 571 | 644 | 30
38960.5589 | 528 | 560 | 30
38960.5594 | 179 | 205 | 30
38960.5599 | 851 | 643 | 30
38960.5604 | 2 | 1 | 30
38960.5609 | 38 | 1 | 30
38960.5614 | 111 | 0 | 30
38960.5619 | 988 | 1 | 30
38960.5623 | 2374 | 18 | 30
38960.5628 | 2330 | 0 | 30
38960.5633 | 2361 | 0 | 30
38960.5638 | 2478 | 0 | 30
38960.5643 | 1921 | 0 | 30
38960.5648 | 2477 | 0 | 30
38960.5653 | 2302 | 0 | 30
38960.5658 | 2190 | 0 | 30
38960.5662 | 2286 | 0 | 30
38960.5667 | 2212 | 0 | 30
38960.5672 | 2099 | 0 | 30
38960.5677 | 2305 | 0 | 30
38960.5682 | 2098 | 0 | 30
38960.5687 | 2065 | 0 | 30
38960.5692 | 2013 | 0 | 30
38960.5696 | 1940 | 0 | 30
38960.5701 | 2492 | 0 | 30
38960.5706 | 2454 | 0 | 30
38960.5711 | 1950 | 0 | 30
38960.5716 | 1985 | 0 | 30
38960.5721 | 2312 | 0 | 30
38960.5726 | 2392 | 0 | 30
38960.573 | 2175 | 0 | 30
38960.5735 | 2416 | 0 | 30
38960.574 | 2394 | 0 | 30
38960.5745 | 2061 | 0 | 30
38960.575 | 2455 | 0 | 30
38960.5755 | 1933 | 0 | 30
38960.576 | 2222 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 81
Time when Penlight power was initiated: | 125