## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number Contingency 1 - Circuit Simulator Data Only
Test Date: | 2010-03-26
DCSim DAQ Start Time | 10:52
DCSim Time for Synchronization | 11:39
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 11:38
Heat Source Start Time | 12:00
DCSim Offset | 1:08 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 4080 | seconds
Heat Source Offset | 0:22 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1318 | seconds
Heat Source Stop Time | 12:17
Test Duration | 0:17 | hour:minutes:seconds
| 1020 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPO/XLPO, 12 AWG, 7/C |  | Cable thermocouples were not used for this test. | Channel 2 represents the air temperature in the center of the tray located in B Position. It is labeled as "B Position - Middle".
SWGR Trip | XLPO/XLPO, 12 AWG, 7/C |  | Cable thermocouples were not used for this test. | Channel 2 represents the air temperature in the center of the tray located in B Position. It is labeled as "B Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.21875 | 125.0381 | -62.4023 | 62.3749 | -0.00061033 | 0.062711 | 0.058405 | 0.0017753 | -0.0054003 | 0.065636 | 0.068985 | 62.5717 | 62.1094 | -62.233 | 62.3474 | -62.2559 | -62.3978 | -0.059509 | 0.064087 | 62.2467 | -62.3932 | 0.16937 | -0.2655 | 124.9741 | 124.7498 | -124.6307 | 0.009156 | -0.12817 | 124.8047 | 62.3428 | 62.4664 | 0.14648 | 124.5117 | 124.9741 | 124.649 | 0.004578 | 0.009156 | 124.5117 | 124.9741 | 0.004578 | 0.14648 | 124.649 | -124.6078 | -124.7681
0.78125 | 125.0793 | -62.3154 | 62.352 | 0.0070192 | 0.060575 | 0.056055 | -0.0003611 | -0.0077503 | 0.065208 | 0.069626 | 62.6358 | 62.1231 | -62.1918 | 62.3978 | -62.2192 | -62.352 | -0.073242 | 0.10529 | 62.2375 | -62.3795 | 0.1236 | -0.22888 | 124.9512 | 124.7131 | -124.5712 | -0.064087 | -0.11444 | 124.8276 | 62.2421 | 62.4207 | 0.096131 | 124.4385 | 124.9512 | 124.5529 | -0.036621 | -0.064087 | 124.4385 | 124.9512 | -0.036621 | 0.096131 | 124.5529 | -124.5438 | -124.7314
1.7969 | 125.061 | -62.3154 | 62.3886 | 0.0070192 | 0.065275 | 0.063745 | 0.0004935 | -0.0056141 | 0.067131 | 0.069626 | 62.6633 | 62.1094 | -62.2009 | 62.4207 | -62.2055 | -62.3291 | -0.045776 | 0.16022 | 62.2192 | -62.3978 | 0.11444 | -0.27924 | 124.9786 | 124.736 | -124.5941 | -0.082397 | -0.16937 | 124.8642 | 62.2696 | 62.4756 | 0.10986 | 124.4247 | 124.9786 | 124.5346 | -0.013733 | -0.082397 | 124.4247 | 124.9786 | -0.013733 | 0.10986 | 124.5346 | -124.5895 | -124.7864
2.7812 | 125.0473 | -62.3428 | 62.3749 | -0.0082398 | 0.062925 | 0.060327 | 0.0011343 | -0.0077503 | 0.065636 | 0.070053 | 62.59 | 62.0865 | -62.233 | 62.3657 | -62.233 | -62.3703 | -0.054932 | 0.10071 | 62.2742 | -62.3611 | 0.10986 | -0.28839 | 124.9329 | 124.7086 | -124.6078 | -0.018311 | -0.10071 | 124.823 | 62.2879 | 62.4435 | 0.10986 | 124.4293 | 124.9329 | 124.617 | -0.027466 | -0.018311 | 124.4293 | 124.9329 | -0.027466 | 0.10986 | 124.617 | -124.6078 | -124.736
3.7812 | 125.029 | -62.4069 | 62.3337 | -0.0082398 | 0.063352 | 0.061609 | 0.0026297 | -0.0051867 | 0.067772 | 0.070481 | 62.5946 | 62.0773 | -62.233 | 62.3337 | -62.2879 | -62.3978 | -0.11902 | 0.036621 | 62.2284 | -62.3932 | 0.17395 | -0.25635 | 125.0015 | 124.7406 | -124.6216 | 0.013733 | -0.10528 | 124.8276 | 62.2879 | 62.4435 | 0.11902 | 124.4843 | 125.0015 | 124.6353 | 0.009155 | 0.013733 | 124.4843 | 125.0015 | 0.009155 | 0.11902 | 124.6353 | -124.5666 | -124.7269
4.7812 | 125.0153 | -62.384 | 62.3566 | -0.00061033 | 0.060361 | 0.059259 | 0.0017753 | -0.0066821 | 0.066704 | 0.070481 | 62.5763 | 62.0956 | -62.2421 | 62.3291 | -62.2971 | -62.4252 | -0.086975 | 0.009155 | 62.2192 | -62.4023 | 0.14191 | -0.26093 | 124.9603 | 124.7131 | -124.6536 | -0.018311 | -0.13733 | 124.8184 | 62.2971 | 62.3932 | 0.086975 | 124.4797 | 124.9603 | 124.6033 | -0.041199 | -0.018311 | 124.4797 | 124.9603 | -0.041199 | 0.086975 | 124.6033 | -124.5987 | -124.7589
5.7812 | 124.9969 | -62.3886 | 62.3611 | -0.0082398 | 0.061857 | 0.063104 | 0.0015615 | -0.0071093 | 0.068413 | 0.069413 | 62.5671 | 62.1094 | -62.2375 | 62.3108 | -62.2971 | -62.4344 | -0.068665 | 0.009155 | 62.2238 | -62.3978 | 0.15106 | -0.25177 | 124.9557 | 124.6994 | -124.6582 | -0.009155 | -0.13733 | 124.8047 | 62.3199 | 62.3978 | 0.091553 | 124.498 | 124.9557 | 124.6124 | -0.045776 | -0.009155 | 124.498 | 124.9557 | -0.045776 | 0.091553 | 124.6124 | -124.5987 | -124.7589
6.7969 | 125.061 | -62.3749 | 62.3245 | 0.0070192 | 0.063138 | 0.060327 | 0.0043387 | -0.0049731 | 0.067985 | 0.06984 | 62.5992 | 62.1002 | -62.2513 | 62.3474 | -62.2742 | -62.4023 | -0.1831 | 0.027466 | 62.1643 | -62.4435 | 0.1236 | -0.2243 | 124.9741 | 124.7223 | -124.5987 | -0.068664 | -0.16022 | 124.8505 | 62.1918 | 62.4023 | 0.10071 | 124.4751 | 124.9741 | 124.5392 | -0.027466 | -0.068664 | 124.4751 | 124.9741 | -0.027466 | 0.10071 | 124.5392 | -124.5758 | -124.7681
7.7812 | 124.9878 | -62.352 | 62.3474 | -0.00061033 | 0.061643 | 0.061182 | 6.6302e-05 | -0.0073229 | 0.067131 | 0.06984 | 62.558 | 62.0911 | -62.2467 | 62.3108 | -62.2971 | -62.4115 | -0.041199 | 0.027466 | 62.1964 | -62.3932 | 0.10529 | -0.25635 | 124.91 | 124.6628 | -124.6445 | -0.041198 | -0.15106 | 124.8047 | 62.3108 | 62.3795 | 0.054932 | 124.4431 | 124.91 | 124.5483 | -0.059509 | -0.041198 | 124.4431 | 124.91 | -0.059509 | 0.054932 | 124.5483 | -124.5941 | -124.7406
8.7812 | 124.9969 | -62.3749 | 62.3383 | -0.00061033 | 0.06442 | 0.06225 | 0.0015615 | -0.0049731 | 0.06649 | 0.068344 | 62.6083 | 62.0636 | -62.2375 | 62.3383 | -62.2604 | -62.4069 | -0.1236 | 0.032043 | 62.1872 | -62.4207 | 0.13733 | -0.27466 | 124.9832 | 124.7131 | -124.5987 | -0.045776 | -0.15106 | 124.8459 | 62.2513 | 62.4069 | 0.11444 | 124.4385 | 124.9832 | 124.5621 | -0.032043 | -0.045776 | 124.4385 | 124.9832 | -0.032043 | 0.11444 | 124.5621 | -124.5758 | -124.7589
9.7812 | 125.0061 | -62.3474 | 62.3749 | 0.0070192 | 0.062711 | 0.062677 | 0.0017753 | -0.0045459 | 0.068626 | 0.068344 | 62.5671 | 62.0636 | -62.2192 | 62.3199 | -62.2879 | -62.4207 | -0.082397 | 0.018311 | 62.2192 | -62.4115 | 0.12817 | -0.31128 | 124.9146 | 124.6674 | -124.6628 | -0.064087 | -0.15564 | 124.7864 | 62.265 | 62.3657 | 0.059509 | 124.411 | 124.9146 | 124.5666 | -0.073242 | -0.064087 | 124.411 | 124.9146 | -0.073242 | 0.059509 | 124.5666 | -124.5941 | -124.7864
10.7812 | 125.0061 | -62.352 | 62.3383 | 0.0070192 | 0.064206 | 0.059473 | 0.0017753 | -0.0060413 | 0.065422 | 0.068558 | 62.5946 | 62.1002 | -62.2284 | 62.3199 | -62.2742 | -62.4069 | -0.10986 | 0.022888 | 62.2238 | -62.4069 | 0.1236 | -0.23804 | 124.9466 | 124.6719 | -124.6124 | -0.054931 | -0.11444 | 124.823 | 62.2421 | 62.3749 | 0.07782 | 124.4522 | 124.9466 | 124.5758 | -0.054931 | -0.054931 | 124.4522 | 124.9466 | -0.054931 | 0.07782 | 124.5758 | -124.5667 | -124.7452
11.7812 | 125.029 | -62.3428 | 62.3199 | -0.00061033 | 0.062925 | 0.063318 | 0.0034841 | -0.0064685 | 0.067772 | 0.06984 | 62.6038 | 62.0865 | -62.2375 | 62.3291 | -62.265 | -62.3886 | -0.16479 | 0.036621 | 62.1826 | -62.4298 | 0.10529 | -0.23346 | 124.9466 | 124.6719 | -124.585 | -0.086976 | -0.13733 | 124.8413 | 62.178 | 62.3795 | 0.077819 | 124.4293 | 124.9466 | 124.5255 | -0.045777 | -0.086976 | 124.4293 | 124.9466 | -0.045777 | 0.077819 | 124.5255 | -124.5575 | -124.7498
12.7812 | 125.0153 | -62.3428 | 62.3749 | -0.00061033 | 0.061429 | 0.059045 | 0.0011343 | -0.0064685 | 0.066704 | 0.070267 | 62.5534 | 62.114 | -62.2375 | 62.3337 | -62.2742 | -62.4023 | -0.050354 | 0.050354 | 62.2238 | -62.3886 | 0.10529 | -0.26093 | 124.8962 | 124.6765 | -124.649 | -0.045777 | -0.15106 | 124.791 | 62.2925 | 62.3932 | 0.068664 | 124.4568 | 124.8962 | 124.5667 | -0.05951 | -0.045777 | 124.4568 | 124.8962 | -0.05951 | 0.068664 | 124.5667 | -124.6124 | -124.7635
13.7812 | 125.0244 | -62.3703 | 62.3383 | -0.00061033 | 0.067197 | 0.061182 | 0.0066885 | -0.0021961 | 0.066063 | 0.068772 | 62.5671 | 62.146 | -62.2513 | 62.3108 | -62.3199 | -62.4298 | -0.1236 | -0.018311 | 62.1918 | -62.4481 | 0.11902 | -0.19226 | 124.9374 | 124.6811 | -124.6582 | -0.07782 | -0.14648 | 124.8184 | 62.2467 | 62.352 | 0.050354 | 124.5163 | 124.9374 | 124.5621 | -0.05951 | -0.07782 | 124.5163 | 124.9374 | -0.05951 | 0.050354 | 124.5621 | -124.5895 | -124.7864
14.7812 | 125.0336 | -62.3749 | 62.3245 | -0.00061033 | 0.064634 | 0.0646 | 0.0032705 | -0.0045459 | 0.063713 | 0.069413 | 62.6129 | 62.059 | -62.233 | 62.352 | -62.2467 | -62.3795 | -0.1831 | 0.036621 | 62.178 | -62.4069 | 0.14191 | -0.2655 | 124.9878 | 124.7269 | -124.5712 | -0.032043 | -0.14648 | 124.8459 | 62.1918 | 62.4115 | 0.12817 | 124.4339 | 124.9878 | 124.5529 | -0.004578 | -0.032043 | 124.4339 | 124.9878 | -0.004578 | 0.12817 | 124.5529 | -124.5575 | -124.7314
15.7812 | 125.0427 | -62.3749 | 62.352 | -0.0082398 | 0.068693 | 0.062463 | 0.0045523 | -0.0019825 | 0.06649 | 0.070481 | 62.5488 | 62.1231 | -62.2604 | 62.2925 | -62.3245 | -62.4435 | -0.12817 | -0.018311 | 62.2009 | -62.4619 | 0.11444 | -0.22888 | 124.9237 | 124.6674 | -124.6765 | -0.086975 | -0.15106 | 124.8093 | 62.2467 | 62.3566 | 0.050354 | 124.498 | 124.9237 | 124.5758 | -0.068664 | -0.086975 | 124.498 | 124.9237 | -0.068664 | 0.050354 | 124.5758 | -124.6124 | -124.8138
16.7969 | 124.9146 | -62.3932 | 62.3428 | 0.0070192 | 0.068052 | 0.062677 | 0.0051931 | -0.0021961 | 0.066704 | 0.070694 | 62.5488 | 62.1689 | -62.2696 | 62.2513 | -62.3611 | -62.5076 | 0.027466 | -0.064087 | 62.2375 | -62.5031 | 0.1236 | -0.17395 | 124.942 | 124.6445 | -124.704 | -0.10986 | -0.10529 | 124.8184 | 62.4207 | 62.3291 | 0.032043 | 124.5621 | 124.942 | 124.6307 | -0.11444 | -0.10986 | 124.5621 | 124.942 | -0.11444 | 0.032043 | 124.6307 | -124.6124 | -124.8459
17.7812 | 124.9283 | -62.3886 | 62.352 | -0.0082398 | 0.068479 | 0.062463 | 0.0013479 | -0.0039051 | 0.067985 | 0.069626 | 62.5076 | 62.1735 | -62.2971 | 62.2238 | -62.3795 | -62.5122 | 0 | -0.10529 | 62.2192 | -62.4893 | 0.091553 | -0.17853 | 124.8962 | 124.6124 | -124.7314 | -0.10071 | -0.13275 | 124.8047 | 62.3886 | 62.2833 | 0.009155 | 124.5621 | 124.8962 | 124.6078 | -0.1236 | -0.10071 | 124.5621 | 124.8962 | -0.1236 | 0.009155 | 124.6078 | -124.649 | -124.8413
18.7812 | 124.9557 | -62.384 | 62.3108 | -0.0082398 | 0.06912 | 0.060754 | 0.0019889 | -5.99e-05 | 0.069054 | 0.071549 | 62.5031 | 62.1643 | -62.2833 | 62.233 | -62.3703 | -62.4802 | -0.050354 | -0.07782 | 62.2375 | -62.4939 | 0.10071 | -0.14648 | 124.8871 | 124.617 | -124.6811 | -0.10986 | -0.073242 | 124.7864 | 62.3337 | 62.3062 | 0.013733 | 124.5483 | 124.8871 | 124.6216 | -0.096131 | -0.10986 | 124.5483 | 124.8871 | -0.096131 | 0.013733 | 124.6216 | -124.5941 | -124.8047
19.7812 | 124.9237 | -62.3932 | 62.3474 | -0.015869 | 0.066984 | 0.063959 | 0.0028433 | -0.0019825 | 0.066917 | 0.068985 | 62.4939 | 62.1735 | -62.2925 | 62.2055 | -62.3886 | -62.5168 | 0.004578 | -0.07782 | 62.265 | -62.471 | 0.10071 | -0.17395 | 124.8871 | 124.5987 | -124.736 | -0.07782 | -0.082397 | 124.7864 | 62.3978 | 62.3154 | 0.004577 | 124.5667 | 124.8871 | 124.6582 | -0.1236 | -0.07782 | 124.5667 | 124.8871 | -0.1236 | 0.004577 | 124.6582 | -124.6399 | -124.8184
20.7812 | 124.9191 | -62.384 | 62.352 | 0.0070192 | 0.06677 | 0.065241 | 0.0032705 | -0.0030505 | 0.068199 | 0.06984 | 62.4756 | 62.1506 | -62.3016 | 62.2101 | -62.4023 | -62.5214 | 0.009155 | -0.10529 | 62.2559 | -62.5076 | 0.082397 | -0.20142 | 124.8596 | 124.5941 | -124.7543 | -0.1236 | -0.096131 | 124.7772 | 62.3932 | 62.2787 | -0.018311 | 124.5346 | 124.8596 | 124.6399 | -0.13733 | -0.1236 | 124.5346 | 124.8596 | -0.13733 | -0.018311 | 124.6399 | -124.6536 | -124.8596
21.7812 | 124.9374 | -62.3932 | 62.3474 | -0.00061033 | 0.068052 | 0.065027 | 0.0041251 | -0.0021961 | 0.067772 | 0.069626 | 62.5031 | 62.1689 | -62.2604 | 62.2009 | -62.3795 | -62.5122 | 0 | -0.10071 | 62.2375 | -62.4802 | 0.13275 | -0.17853 | 124.8962 | 124.5941 | -124.7269 | -0.086976 | -0.10986 | 124.7635 | 62.3932 | 62.2925 | 0.013732 | 124.5621 | 124.8962 | 124.6307 | -0.11902 | -0.086976 | 124.5621 | 124.8962 | -0.11902 | 0.013732 | 124.6307 | -124.6078 | -124.8276
22.7812 | 124.9374 | -62.3978 | 62.3199 | -0.0082398 | 0.067624 | 0.063532 | 0.0036979 | -0.0017687 | 0.068413 | 0.069199 | 62.4893 | 62.1689 | -62.2833 | 62.1918 | -62.3978 | -62.5351 | 0.009155 | -0.09613 | 62.265 | -62.4893 | 0.11444 | -0.15106 | 124.8871 | 124.5895 | -124.7177 | -0.091553 | -0.054931 | 124.7726 | 62.4069 | 62.3016 | 0 | 124.5666 | 124.8871 | 124.6628 | -0.13733 | -0.091553 | 124.5666 | 124.8871 | -0.13733 | 0 | 124.6628 | -124.6033 | -124.8093
23.7812 | 124.9146 | -62.3932 | 62.3566 | -0.00061033 | 0.068906 | 0.061395 | 0.0026297 | -0.0009143 | 0.067772 | 0.070694 | 62.5168 | 62.1643 | -62.2971 | 62.2238 | -62.3703 | -62.5259 | 0.041199 | -0.073242 | 62.2559 | -62.4985 | 0.09613 | -0.19226 | 124.91 | 124.617 | -124.7269 | -0.10529 | -0.10071 | 124.8138 | 62.4344 | 62.3199 | 0.022888 | 124.5575 | 124.91 | 124.649 | -0.13275 | -0.10529 | 124.5575 | 124.91 | -0.13275 | 0.022888 | 124.649 | -124.6536 | -124.855
24.7812 | 124.9146 | -62.3749 | 62.3428 | -0.00061033 | 0.069974 | 0.066095 | 0.0019889 | 0.0001539 | 0.066277 | 0.06984 | 62.5305 | 62.1735 | -62.265 | 62.2467 | -62.3428 | -62.4893 | 0.032043 | -0.036621 | 62.2467 | -62.4939 | 0.10986 | -0.16937 | 124.9054 | 124.6216 | -124.6857 | -0.11902 | -0.09613 | 124.7955 | 62.4069 | 62.3383 | 0.032044 | 124.5483 | 124.9054 | 124.6216 | -0.11444 | -0.11902 | 124.5483 | 124.9054 | -0.11444 | 0.032044 | 124.6216 | -124.6078 | -124.8367
25.7812 | 124.9008 | -62.4023 | 62.3703 | 0.0070192 | 0.067838 | 0.063532 | 0.0030569 | -0.0007007 | 0.068413 | 0.069413 | 62.5076 | 62.1872 | -62.2925 | 62.2009 | -62.384 | -62.5214 | 0.036621 | -0.07782 | 62.2696 | -62.4847 | 0.10986 | -0.1831 | 124.91 | 124.6033 | -124.7543 | -0.082397 | -0.10071 | 124.8001 | 62.439 | 62.3245 | 0.018311 | 124.5895 | 124.91 | 124.6719 | -0.11902 | -0.082397 | 124.5895 | 124.91 | -0.11902 | 0.018311 | 124.6719 | -124.6628 | -124.855
26.7969 | 124.9146 | -62.3611 | 62.3703 | 0.0070192 | 0.065488 | 0.0599 | -0.0012155 | -0.0002735 | 0.066704 | 0.070267 | 62.5122 | 62.2192 | -62.2513 | 62.2284 | -62.3154 | -62.4939 | 0.16937 | 0 | 62.2925 | -62.4573 | 0.10986 | -0.15106 | 124.8734 | 124.5895 | -124.6857 | -0.09613 | -0.07782 | 124.7635 | 62.5305 | 62.3611 | 0.045776 | 124.5804 | 124.8734 | 124.6536 | -0.13275 | -0.09613 | 124.5804 | 124.8734 | -0.13275 | 0.045776 | 124.6536 | -124.6216 | -124.8276
27.7812 | 124.9466 | -62.3795 | 62.3886 | -0.00061033 | 0.067411 | 0.064172 | 0.0030569 | -0.0011279 | 0.069694 | 0.068985 | 62.5626 | 62.1735 | -62.2421 | 62.2421 | -62.3245 | -62.4664 | 0.041199 | -0.004578 | 62.2604 | -62.471 | 0.13733 | -0.21515 | 124.942 | 124.6216 | -124.7131 | -0.091552 | -0.12817 | 124.8047 | 62.4207 | 62.3749 | 0.054932 | 124.5529 | 124.942 | 124.6399 | -0.086975 | -0.091552 | 124.5529 | 124.942 | -0.086975 | 0.054932 | 124.6399 | -124.6307 | -124.8596
28.7812 | 124.91 | -62.3978 | 62.3703 | -0.00061033 | 0.06912 | 0.063745 | 0.0026297 | -0.0011279 | 0.06649 | 0.068344 | 62.4985 | 62.1552 | -62.2879 | 62.2055 | -62.3886 | -62.5122 | 0.054932 | -0.054932 | 62.265 | -62.5122 | 0.10986 | -0.21515 | 124.8962 | 124.6033 | -124.7589 | -0.11444 | -0.10529 | 124.7864 | 62.4527 | 62.3428 | 0.009155 | 124.5529 | 124.8962 | 124.6628 | -0.11444 | -0.11444 | 124.5529 | 124.8962 | -0.11444 | 0.009155 | 124.6628 | -124.6582 | -124.8825
29.7812 | 124.9741 | -62.3657 | 62.3932 | -0.00061033 | 0.068906 | 0.065241 | 0.0019889 | -5.99e-05 | 0.06649 | 0.069626 | 62.5671 | 62.1918 | -62.2513 | 62.2879 | -62.2971 | -62.4527 | 0.041199 | 0.045776 | 62.2833 | -62.4298 | 0.11444 | -0.20142 | 124.9329 | 124.6536 | -124.6902 | -0.064087 | -0.10986 | 124.8184 | 62.4069 | 62.4115 | 0.068665 | 124.5575 | 124.9329 | 124.649 | -0.086975 | -0.064087 | 124.5575 | 124.9329 | -0.086975 | 0.068665 | 124.649 | -124.6445 | -124.823
30.7812 | 124.9649 | -62.3657 | 62.3749 | 0.0070192 | 0.067624 | 0.062463 | 0.0011343 | -0.0026233 | 0.067985 | 0.070694 | 62.5717 | 62.1964 | -62.2421 | 62.2879 | -62.3016 | -62.4481 | 0.036621 | 0.050354 | 62.2879 | -62.4619 | 0.1236 | -0.17853 | 124.9374 | 124.6536 | -124.6765 | -0.09613 | -0.086975 | 124.8138 | 62.4023 | 62.4161 | 0.064087 | 124.5621 | 124.9374 | 124.6536 | -0.082397 | -0.09613 | 124.5621 | 124.9374 | -0.082397 | 0.064087 | 124.6536 | -124.617 | -124.8367
31.7812 | 124.9603 | -62.3566 | 62.3611 | -0.0082398 | 0.068693 | 0.060541 | 0.0017753 | -0.0019825 | 0.06649 | 0.069199 | 62.5717 | 62.1918 | -62.2513 | 62.2833 | -62.3016 | -62.4573 | 0.041199 | 0.036621 | 62.2879 | -62.4619 | 0.10528 | -0.16937 | 124.9283 | 124.6399 | -124.6628 | -0.10529 | -0.073242 | 124.823 | 62.3978 | 62.3932 | 0.054931 | 124.5483 | 124.9283 | 124.6445 | -0.10071 | -0.10529 | 124.5483 | 124.9283 | -0.10071 | 0.054931 | 124.6445 | -124.6124 | -124.823
32.7812 | 124.9649 | -62.3611 | 62.3749 | -0.00061033 | 0.070188 | 0.062463 | 0.0026297 | -0.0015551 | 0.067345 | 0.068985 | 62.5626 | 62.1872 | -62.265 | 62.2925 | -62.3016 | -62.439 | 0.036621 | 0.059509 | 62.2696 | -62.4619 | 0.09613 | -0.18768 | 124.9237 | 124.6536 | -124.6765 | -0.10071 | -0.10529 | 124.8276 | 62.3978 | 62.4207 | 0.059509 | 124.5483 | 124.9237 | 124.6307 | -0.07782 | -0.10071 | 124.5483 | 124.9237 | -0.07782 | 0.059509 | 124.6307 | -124.6399 | -124.8367
33.7812 | 124.9786 | -62.3611 | 62.352 | -0.015869 | 0.067838 | 0.066309 | 0.0017753 | -0.0013415 | 0.068199 | 0.06984 | 62.5763 | 62.1872 | -62.2604 | 62.2879 | -62.3062 | -62.4481 | 0.045776 | 0.050354 | 62.2833 | -62.4527 | 0.10071 | -0.16479 | 124.9374 | 124.649 | -124.6582 | -0.091553 | -0.068665 | 124.8367 | 62.4069 | 62.4115 | 0.054932 | 124.5483 | 124.9374 | 124.6445 | -0.086975 | -0.091553 | 124.5483 | 124.9374 | -0.086975 | 0.054932 | 124.6445 | -124.6124 | -124.8047
34.7812 | 124.9786 | -62.384 | 62.3611 | -0.0082398 | 0.06677 | 0.063532 | -0.0016427 | -0.0004871 | 0.070122 | 0.070053 | 62.5717 | 62.2055 | -62.2787 | 62.2833 | -62.3062 | -62.4298 | 0.041199 | 0.045776 | 62.2787 | -62.471 | 0.10529 | -0.15564 | 124.9557 | 124.6674 | -124.6674 | -0.086975 | -0.082397 | 124.8505 | 62.4252 | 62.4298 | 0.07782 | 124.5895 | 124.9557 | 124.6628 | -0.045777 | -0.086975 | 124.5895 | 124.9557 | -0.045777 | 0.07782 | 124.6628 | -124.6399 | -124.8322
35.7812 | 124.9695 | -62.3611 | 62.3886 | -0.00061033 | 0.069761 | 0.063745 | -0.0005747 | -0.0013415 | 0.069481 | 0.069199 | 62.5442 | 62.2009 | -62.2513 | 62.2604 | -62.3154 | -62.4619 | 0.09613 | 0.027466 | 62.2787 | -62.471 | 0.10986 | -0.18768 | 124.9054 | 124.6216 | -124.704 | -0.10986 | -0.10986 | 124.7955 | 62.4573 | 62.3886 | 0.045776 | 124.5621 | 124.9054 | 124.6399 | -0.10071 | -0.10986 | 124.5621 | 124.9054 | -0.10071 | 0.045776 | 124.6399 | -124.6399 | -124.8596
36.7969 | 125.0427 | -62.3703 | 62.3566 | -0.0082398 | 0.060361 | 0.06225 | -0.0044199 | -0.0024097 | 0.066277 | 0.070481 | 62.6404 | 62.1048 | -62.1826 | 62.3795 | -62.1918 | -62.3383 | -0.045776 | 0.14648 | 62.265 | -62.3978 | 0.18768 | -0.25177 | 125.0107 | 124.7498 | -124.5483 | -0.027466 | -0.091552 | 124.823 | 62.3245 | 62.5168 | 0.17853 | 124.4751 | 125.0107 | 124.6353 | 0.032043 | -0.027466 | 124.4751 | 125.0107 | 0.032043 | 0.17853 | 124.6353 | -124.5392 | -124.7543
37.7812 | 124.9191 | -62.3886 | 62.4161 | -0.00061033 | 0.065488 | 0.063532 | 0.0017753 | -0.0045459 | 0.067345 | 0.069413 | 62.5259 | 62.1964 | -62.2375 | 62.2513 | -62.3383 | -62.4893 | 0.17395 | 0.022888 | 62.3154 | -62.4527 | 0.15106 | -0.21973 | 124.9146 | 124.6399 | -124.7543 | -0.064087 | -0.10071 | 124.7635 | 62.5626 | 62.4115 | 0.050354 | 124.585 | 124.9146 | 124.704 | -0.10071 | -0.064087 | 124.585 | 124.9146 | -0.10071 | 0.050354 | 124.704 | -124.6536 | -124.8688
38.7812 | 124.9237 | -62.3978 | 62.4069 | -0.0082398 | 0.065915 | 0.060968 | 0.0019889 | -0.0043323 | 0.067985 | 0.070908 | 62.5259 | 62.2192 | -62.265 | 62.233 | -62.3428 | -62.4893 | 0.14191 | 0.009155 | 62.3199 | -62.471 | 0.13275 | -0.18768 | 124.9237 | 124.6307 | -124.7498 | -0.073242 | -0.086975 | 124.791 | 62.5397 | 62.4069 | 0.054932 | 124.617 | 124.9237 | 124.7177 | -0.091553 | -0.073242 | 124.617 | 124.9237 | -0.091553 | 0.054932 | 124.7177 | -124.6719 | -124.8779
39.7812 | 124.9466 | -62.3978 | 62.3611 | -0.00061033 | 0.067411 | 0.06225 | 0.0026297 | -0.0041187 | 0.069481 | 0.069413 | 62.5442 | 62.2055 | -62.2421 | 62.265 | -62.3245 | -62.4756 | 0.10071 | 0.032043 | 62.2787 | -62.4664 | 0.15564 | -0.15564 | 124.942 | 124.6628 | -124.6857 | -0.068665 | -0.082397 | 124.7864 | 62.4985 | 62.4298 | 0.073242 | 124.6033 | 124.942 | 124.6765 | -0.07782 | -0.068665 | 124.6033 | 124.942 | -0.07782 | 0.073242 | 124.6765 | -124.6033 | -124.8276
40.7812 | 124.942 | -62.4023 | 62.384 | -0.00061033 | 0.067624 | 0.061182 | -0.0001473 | -0.0015551 | 0.067131 | 0.068344 | 62.5305 | 62.2101 | -62.2467 | 62.2467 | -62.3291 | -62.471 | 0.11444 | 0.027466 | 62.3108 | -62.4619 | 0.15564 | -0.17395 | 124.9329 | 124.649 | -124.7131 | -0.059509 | -0.073242 | 124.7772 | 62.5168 | 62.4298 | 0.073242 | 124.6124 | 124.9329 | 124.7131 | -0.068664 | -0.059509 | 124.6124 | 124.9329 | -0.068664 | 0.073242 | 124.7131 | -124.6307 | -124.8459
41.7812 | 124.9695 | -62.3795 | 62.3795 | -0.00061033 | 0.068693 | 0.065668 | 0.0015615 | -0.0002735 | 0.067131 | 0.068985 | 62.5671 | 62.1872 | -62.2375 | 62.2696 | -62.3062 | -62.471 | 0.054932 | 0.036621 | 62.2971 | -62.4664 | 0.14191 | -0.19226 | 124.9466 | 124.649 | -124.6857 | -0.086975 | -0.082398 | 124.8047 | 62.4344 | 62.4161 | 0.073243 | 124.5667 | 124.9466 | 124.6765 | -0.091552 | -0.086975 | 124.5667 | 124.9466 | -0.091552 | 0.073243 | 124.6765 | -124.617 | -124.8459
42.7812 | 124.9191 | -62.3978 | 62.4023 | -0.00061033 | 0.065061 | 0.059259 | 0.0002799 | -0.0017687 | 0.069908 | 0.069413 | 62.5122 | 62.1689 | -62.265 | 62.2421 | -62.3245 | -62.4847 | 0.14191 | 0.013733 | 62.3245 | -62.4435 | 0.13275 | -0.23346 | 124.91 | 124.6399 | -124.7269 | -0.045776 | -0.07782 | 124.7772 | 62.5397 | 62.4115 | 0.073242 | 124.5666 | 124.91 | 124.7223 | -0.086975 | -0.045776 | 124.5666 | 124.91 | -0.086975 | 0.073242 | 124.7223 | -124.6674 | -124.8459
43.7812 | 124.9649 | -62.3749 | 62.384 | -0.0082398 | 0.066129 | 0.058832 | 0.0019889 | -0.0019825 | 0.067985 | 0.069199 | 62.5397 | 62.1872 | -62.2513 | 62.2604 | -62.3291 | -62.4619 | 0.082397 | 0.027466 | 62.3199 | -62.4435 | 0.1236 | -0.19684 | 124.9146 | 124.6353 | -124.7131 | -0.068664 | -0.064087 | 124.791 | 62.4573 | 62.4023 | 0.045776 | 124.5621 | 124.9146 | 124.6948 | -0.086975 | -0.068664 | 124.5621 | 124.9146 | -0.086975 | 0.045776 | 124.6948 | -124.6353 | -124.8276
44.7812 | 124.9146 | -62.3657 | 62.3886 | -0.00061033 | 0.066129 | 0.061823 | -0.0020701 | -0.0030505 | 0.068199 | 0.070053 | 62.5168 | 62.233 | -62.2467 | 62.2421 | -62.3337 | -62.4802 | 0.14648 | 0.013733 | 62.3199 | -62.4619 | 0.11902 | -0.15564 | 124.8825 | 124.6078 | -124.7223 | -0.09613 | -0.068665 | 124.7635 | 62.5122 | 62.3795 | 0.032044 | 124.5987 | 124.8825 | 124.6857 | -0.11444 | -0.09613 | 124.5987 | 124.8825 | -0.11444 | 0.032044 | 124.6857 | -124.6353 | -124.8505
45.7812 | 124.942 | -62.3886 | 62.4023 | -0.0082398 | 0.06677 | 0.062036 | 0.0002799 | -0.0024097 | 0.06649 | 0.070053 | 62.5259 | 62.1918 | -62.2513 | 62.2604 | -62.3245 | -62.471 | 0.11444 | 0.022888 | 62.3016 | -62.4619 | 0.13733 | -0.21057 | 124.9146 | 124.649 | -124.7269 | -0.073242 | -0.10071 | 124.7772 | 62.5031 | 62.4115 | 0.064087 | 124.5804 | 124.9146 | 124.6902 | -0.082397 | -0.073242 | 124.5804 | 124.9146 | -0.082397 | 0.064087 | 124.6902 | -124.6536 | -124.8642
46.7969 | 124.9146 | -62.4023 | 62.3795 | -0.0082398 | 0.065915 | 0.062036 | -0.0005747 | -0.0028369 | 0.066063 | 0.070694 | 62.5214 | 62.2009 | -62.2513 | 62.233 | -62.3337 | -62.4893 | 0.14648 | 0.009155 | 62.3245 | -62.4619 | 0.15106 | -0.17853 | 124.9237 | 124.6353 | -124.7131 | -0.059509 | -0.054932 | 124.7726 | 62.5488 | 62.4115 | 0.068665 | 124.6033 | 124.9237 | 124.7269 | -0.086975 | -0.059509 | 124.6033 | 124.9237 | -0.086975 | 0.068665 | 124.7269 | -124.6307 | -124.8413
47.7812 | 124.9054 | -62.3932 | 62.4023 | -0.00061033 | 0.064634 | 0.060968 | -0.0012155 | -0.0036915 | 0.068413 | 0.068344 | 62.5351 | 62.1872 | -62.2742 | 62.2604 | -62.3245 | -62.4802 | 0.16479 | 0.022888 | 62.3383 | -62.4298 | 0.11902 | -0.21515 | 124.9283 | 124.6536 | -124.7269 | -0.036622 | -0.064087 | 124.8093 | 62.558 | 62.4161 | 0.068664 | 124.5804 | 124.9283 | 124.7314 | -0.086976 | -0.036622 | 124.5804 | 124.9283 | -0.086976 | 0.068664 | 124.7314 | -124.6765 | -124.8322
48.7812 | 124.9466 | -62.3978 | 62.3932 | -0.00061033 | 0.066984 | 0.064813 | 0.0017753 | -0.0024097 | 0.066704 | 0.06984 | 62.5488 | 62.1872 | -62.2559 | 62.2604 | -62.3108 | -62.4619 | 0.054932 | 0.045776 | 62.2925 | -62.4847 | 0.14191 | -0.20599 | 124.9466 | 124.6582 | -124.704 | -0.086975 | -0.10071 | 124.8047 | 62.4527 | 62.4435 | 0.086975 | 124.585 | 124.9466 | 124.6902 | -0.064087 | -0.086975 | 124.585 | 124.9466 | -0.064087 | 0.086975 | 124.6902 | -124.649 | -124.8779
49.7812 | 124.9283 | -62.384 | 62.3932 | -0.015869 | 0.06677 | 0.060114 | -0.0014291 | -0.0015551 | 0.068626 | 0.070694 | 62.5076 | 62.2009 | -62.2421 | 62.2238 | -62.3291 | -62.4985 | 0.14191 | 0.009155 | 62.3245 | -62.4344 | 0.14191 | -0.19226 | 124.8917 | 124.6078 | -124.7223 | -0.050354 | -0.068664 | 124.7498 | 62.5259 | 62.3932 | 0.054931 | 124.585 | 124.8917 | 124.7086 | -0.11444 | -0.050354 | 124.585 | 124.8917 | -0.11444 | 0.054931 | 124.7086 | -124.6353 | -124.8276
50.7812 | 124.9512 | -62.3886 | 62.3932 | 0.0070192 | 0.067197 | 0.057764 | 0.0041251 | -0.0036915 | 0.06649 | 0.068985 | 62.5351 | 62.1918 | -62.265 | 62.2559 | -62.3154 | -62.4664 | 0.086975 | 0.032043 | 62.3016 | -62.4619 | 0.1236 | -0.20142 | 124.9237 | 124.6445 | -124.7086 | -0.073242 | -0.091552 | 124.8001 | 62.4756 | 62.4207 | 0.073242 | 124.5804 | 124.9237 | 124.6902 | -0.07782 | -0.073242 | 124.5804 | 124.9237 | -0.07782 | 0.073242 | 124.6902 | -124.6582 | -124.855
51.7812 | 124.8962 | -62.3703 | 62.384 | -0.0082398 | 0.067197 | 0.062677 | 0.0002799 | -0.0034777 | 0.066917 | 0.06749 | 62.5214 | 62.2147 | -62.2284 | 62.2421 | -62.3337 | -62.4893 | 0.13733 | 0.009155 | 62.3245 | -62.4802 | 0.14191 | -0.16937 | 124.8917 | 124.6124 | -124.7177 | -0.10986 | -0.059509 | 124.7498 | 62.5076 | 62.3795 | 0.036621 | 124.585 | 124.8917 | 124.6948 | -0.11902 | -0.10986 | 124.585 | 124.8917 | -0.11902 | 0.036621 | 124.6948 | -124.6124 | -124.8642
52.7812 | 124.91 | -62.3566 | 62.3978 | -0.00061033 | 0.067838 | 0.061182 | -0.0033517 | -0.0017687 | 0.068199 | 0.072617 | 62.4985 | 62.2055 | -62.2696 | 62.2467 | -62.3337 | -62.4893 | 0.14648 | 0.013733 | 62.3291 | -62.4435 | 0.086975 | -0.19226 | 124.855 | 124.6033 | -124.7314 | -0.086975 | -0.068664 | 124.7681 | 62.5031 | 62.3703 | 0.022888 | 124.5621 | 124.855 | 124.6857 | -0.13275 | -0.086975 | 124.5621 | 124.855 | -0.13275 | 0.022888 | 124.6857 | -124.6674 | -124.8413
53.7812 | 124.9191 | -62.3611 | 62.3886 | -0.023499 | 0.066343 | 0.057123 | 0.0019889 | -0.0034777 | 0.070335 | 0.068772 | 62.5214 | 62.2009 | -62.2467 | 62.2421 | -62.3291 | -62.4893 | 0.13275 | 0.013733 | 62.3108 | -62.4573 | 0.11444 | -0.18768 | 124.8825 | 124.6033 | -124.7177 | -0.09613 | -0.07782 | 124.7681 | 62.4939 | 62.3749 | 0.032043 | 124.5621 | 124.8825 | 124.6719 | -0.12817 | -0.09613 | 124.5621 | 124.8825 | -0.12817 | 0.032043 | 124.6719 | -124.6353 | -124.8459
54.7812 | 124.9054 | -62.3795 | 62.3978 | -0.0082398 | 0.068052 | 0.0599 | 6.6302e-05 | -0.0043323 | 0.067985 | 0.070267 | 62.5214 | 62.2101 | -62.2559 | 62.2375 | -62.3428 | -62.4893 | 0.13275 | 0.018311 | 62.3154 | -62.4664 | 0.1236 | -0.18768 | 124.9008 | 124.617 | -124.7406 | -0.086975 | -0.082397 | 124.7772 | 62.5122 | 62.3978 | 0.036622 | 124.5895 | 124.9008 | 124.6948 | -0.10986 | -0.086975 | 124.5895 | 124.9008 | -0.10986 | 0.036622 | 124.6948 | -124.6536 | -124.8642
55.7812 | 124.9512 | -62.3566 | 62.3886 | -0.00061033 | 0.069333 | 0.060754 | -0.0001473 | -0.0021961 | 0.065849 | 0.068131 | 62.5488 | 62.2009 | -62.2467 | 62.2559 | -62.3062 | -62.471 | 0.07782 | 0.022888 | 62.2925 | -62.4664 | 0.10986 | -0.18768 | 124.9054 | 124.6124 | -124.6948 | -0.10986 | -0.096131 | 124.7955 | 62.4344 | 62.3795 | 0.050354 | 124.5575 | 124.9054 | 124.649 | -0.11444 | -0.10986 | 124.5575 | 124.9054 | -0.11444 | 0.050354 | 124.649 | -124.6353 | -124.855
56.7969 | 124.9786 | -62.3749 | 62.3703 | -0.0082398 | 0.061643 | 0.06225 | -0.0054879 | -0.0041187 | 0.067558 | 0.067917 | 62.5534 | 62.0956 | -62.2147 | 62.265 | -62.2925 | -62.4115 | -0.054932 | 0.009155 | 62.2513 | -62.4252 | 0.16022 | -0.27466 | 124.9283 | 124.6399 | -124.6628 | -0.050354 | -0.11902 | 124.7681 | 62.3199 | 62.384 | 0.082398 | 124.4705 | 124.9283 | 124.6262 | -0.036621 | -0.050354 | 124.4705 | 124.9283 | -0.036621 | 0.082398 | 124.6262 | -124.585 | -124.7955
57.7812 | 124.91 | -62.4115 | 62.3795 | -0.0082398 | 0.066343 | 0.060754 | 0.0026297 | -0.0051867 | 0.068626 | 0.068772 | 62.5122 | 62.2055 | -62.2559 | 62.2559 | -62.3154 | -62.4939 | 0.15564 | 0.018311 | 62.3016 | -62.4802 | 0.15564 | -0.17395 | 124.9237 | 124.6674 | -124.6948 | -0.068665 | -0.07782 | 124.7681 | 62.5671 | 62.4298 | 0.09613 | 124.617 | 124.9237 | 124.7131 | -0.082397 | -0.068665 | 124.617 | 124.9237 | -0.082397 | 0.09613 | 124.7131 | -124.6353 | -124.8596
58.7812 | 124.8962 | -62.3932 | 62.3795 | -0.00061033 | 0.065702 | 0.059473 | -0.0010019 | -0.0047595 | 0.068413 | 0.068558 | 62.5351 | 62.2147 | -62.2421 | 62.2604 | -62.3383 | -62.4802 | 0.15106 | 0.022888 | 62.2971 | -62.4344 | 0.15106 | -0.16479 | 124.9283 | 124.6536 | -124.7177 | -0.041199 | -0.082398 | 124.7772 | 62.5443 | 62.4161 | 0.054931 | 124.6078 | 124.9283 | 124.6902 | -0.086976 | -0.041199 | 124.6078 | 124.9283 | -0.086976 | 0.054931 | 124.6902 | -124.6216 | -124.8138
59.7812 | 124.9008 | -62.3703 | 62.4161 | -0.0082398 | 0.065488 | 0.063318 | 0.0013479 | -0.0041187 | 0.066277 | 0.070267 | 62.5305 | 62.1872 | -62.2513 | 62.2742 | -62.3199 | -62.4756 | 0.14648 | 0.027466 | 62.3108 | -62.4344 | 0.11902 | -0.22888 | 124.9008 | 124.6445 | -124.736 | -0.064087 | -0.10529 | 124.7818 | 62.5168 | 62.3978 | 0.050354 | 124.5575 | 124.9008 | 124.6811 | -0.10529 | -0.064087 | 124.5575 | 124.9008 | -0.10529 | 0.050354 | 124.6811 | -124.6674 | -124.8505
60.7812 | 124.8871 | -62.3749 | 62.3978 | -0.00061033 | 0.065915 | 0.060541 | 0.0004935 | -0.0026233 | 0.066704 | 0.068344 | 62.5076 | 62.2101 | -62.2421 | 62.233 | -62.3474 | -62.4893 | 0.14191 | 0.004578 | 62.3016 | -62.4619 | 0.13275 | -0.18768 | 124.8825 | 124.6078 | -124.7452 | -0.086975 | -0.09613 | 124.7498 | 62.5168 | 62.3795 | 0.027466 | 124.585 | 124.8825 | 124.6765 | -0.11444 | -0.086975 | 124.585 | 124.8825 | -0.11444 | 0.027466 | 124.6765 | -124.6399 | -124.8596
61.7812 | 124.9008 | -62.3932 | 62.3932 | 0.0070192 | 0.065061 | 0.060968 | 0.0002799 | -0.0039051 | 0.066917 | 0.069626 | 62.5168 | 62.2009 | -62.2513 | 62.2375 | -62.3474 | -62.4802 | 0.12817 | 0 | 62.352 | -62.4527 | 0.14191 | -0.19226 | 124.91 | 124.6307 | -124.7406 | -0.05951 | -0.041198 | 124.7681 | 62.5214 | 62.3932 | 0.045776 | 124.5941 | 124.91 | 124.7452 | -0.086976 | -0.05951 | 124.5941 | 124.91 | -0.086976 | 0.045776 | 124.7452 | -124.6445 | -124.8459
62.7812 | 124.9466 | -62.3932 | 62.3932 | -0.00061033 | 0.066343 | 0.060114 | 0.0017753 | -0.0011279 | 0.066063 | 0.06749 | 62.5305 | 62.2055 | -62.2559 | 62.2604 | -62.3154 | -62.4802 | 0.10986 | 0.009155 | 62.3016 | -62.471 | 0.13733 | -0.18768 | 124.9237 | 124.6536 | -124.7086 | -0.07782 | -0.091552 | 124.7864 | 62.5031 | 62.4023 | 0.077819 | 124.5987 | 124.9237 | 124.6948 | -0.086976 | -0.07782 | 124.5987 | 124.9237 | -0.086976 | 0.077819 | 124.6948 | -124.649 | -124.8642
63.7812 | 124.8962 | -62.384 | 62.4023 | -0.00061033 | 0.066129 | 0.059045 | -0.0010019 | -0.0043323 | 0.068626 | 0.069199 | 62.5305 | 62.178 | -62.2421 | 62.2421 | -62.3337 | -62.4847 | 0.16479 | 0.013733 | 62.3199 | -62.4344 | 0.14191 | -0.2243 | 124.9146 | 124.6262 | -124.736 | -0.050354 | -0.082398 | 124.7726 | 62.5488 | 62.3978 | 0.050354 | 124.5621 | 124.9146 | 124.704 | -0.10071 | -0.050354 | 124.5621 | 124.9146 | -0.10071 | 0.050354 | 124.704 | -124.6445 | -124.8367
64.7812 | 124.9557 | -62.4023 | 62.3749 | -0.00061033 | 0.067411 | 0.063745 | 0.0017753 | -0.0030505 | 0.067985 | 0.067704 | 62.5626 | 62.1964 | -62.2513 | 62.2787 | -62.2971 | -62.4481 | 0.059509 | 0.036621 | 62.2742 | -62.4664 | 0.15106 | -0.17853 | 124.9649 | 124.6811 | -124.6719 | -0.064087 | -0.10071 | 124.8138 | 62.4619 | 62.439 | 0.10529 | 124.5987 | 124.9649 | 124.6765 | -0.045776 | -0.064087 | 124.5987 | 124.9649 | -0.045776 | 0.10529 | 124.6765 | -124.6262 | -124.8413
65.7812 | 124.942 | -62.3749 | 62.3657 | -0.00061033 | 0.065275 | 0.059686 | -0.0014291 | -0.0017687 | 0.066704 | 0.06984 | 62.5946 | 62.1643 | -62.2009 | 62.3154 | -62.2559 | -62.4161 | 0.059509 | 0.086975 | 62.2833 | -62.4069 | 0.17395 | -0.20142 | 124.9695 | 124.6902 | -124.6216 | -0.032043 | -0.082398 | 124.7955 | 62.4344 | 62.4619 | 0.11902 | 124.5392 | 124.9695 | 124.6582 | -0.041199 | -0.032043 | 124.5392 | 124.9695 | -0.041199 | 0.11902 | 124.6582 | -124.5667 | -124.7726
66.7969 | 124.9329 | -62.3657 | 62.3886 | 0.0070192 | 0.064634 | 0.060327 | -0.0014291 | -0.0054003 | 0.065208 | 0.068985 | 62.5763 | 62.1277 | -62.233 | 62.2925 | -62.2787 | -62.4344 | 0.091553 | 0.068665 | 62.2787 | -62.4207 | 0.13275 | -0.26093 | 124.942 | 124.6582 | -124.6674 | -0.054931 | -0.10986 | 124.8093 | 62.4573 | 62.4344 | 0.086975 | 124.4934 | 124.942 | 124.6445 | -0.068664 | -0.054931 | 124.4934 | 124.942 | -0.068664 | 0.086975 | 124.6445 | -124.6216 | -124.8093
67.7812 | 124.9054 | -62.3749 | 62.4161 | 0.0070192 | 0.065702 | 0.058618 | -0.0020701 | -0.0075367 | 0.069054 | 0.068772 | 62.5351 | 62.1689 | -62.2375 | 62.265 | -62.3108 | -62.4664 | 0.13275 | 0.022888 | 62.2879 | -62.4161 | 0.13733 | -0.24719 | 124.91 | 124.6399 | -124.7269 | -0.041199 | -0.12817 | 124.7726 | 62.5076 | 62.3978 | 0.064087 | 124.5438 | 124.91 | 124.6628 | -0.091553 | -0.041199 | 124.5438 | 124.91 | -0.091553 | 0.064087 | 124.6628 | -124.6536 | -124.8322
68.7812 | 124.91 | -62.3749 | 62.4023 | 0.014648 | 0.066129 | 0.057977 | 0.0009207 | -0.0060413 | 0.067772 | 0.069626 | 62.5122 | 62.1872 | -62.2513 | 62.2375 | -62.3291 | -62.4985 | 0.14191 | 0.004578 | 62.3062 | -62.4344 | 0.1236 | -0.21515 | 124.8871 | 124.6124 | -124.7314 | -0.059509 | -0.096131 | 124.7635 | 62.5168 | 62.3795 | 0.045776 | 124.5621 | 124.8871 | 124.6811 | -0.1236 | -0.059509 | 124.5621 | 124.8871 | -0.1236 | 0.045776 | 124.6811 | -124.6536 | -124.8367
69.7812 | 124.9283 | -62.3886 | 62.3703 | -0.00061033 | 0.068479 | 0.059473 | 0.0024161 | -0.0013415 | 0.068626 | 0.067917 | 62.5259 | 62.2101 | -62.2421 | 62.265 | -62.3108 | -62.471 | 0.10529 | 0.027466 | 62.2879 | -62.4573 | 0.14648 | -0.16022 | 124.9146 | 124.6536 | -124.6811 | -0.068664 | -0.082397 | 124.7681 | 62.4939 | 62.4161 | 0.07782 | 124.5987 | 124.9146 | 124.6765 | -0.082397 | -0.068664 | 124.5987 | 124.9146 | -0.082397 | 0.07782 | 124.6765 | -124.6124 | -124.8276
70.7812 | 124.9008 | -62.4069 | 62.3886 | -0.0082398 | 0.06677 | 0.060327 | 0.0004935 | -0.0039051 | 0.066917 | 0.068558 | 62.5122 | 62.1872 | -62.2421 | 62.2375 | -62.3245 | -62.471 | 0.15564 | 0.004578 | 62.3245 | -62.4298 | 0.16479 | -0.20142 | 124.9191 | 124.6445 | -124.7131 | -0.022889 | -0.064087 | 124.7543 | 62.5626 | 62.4115 | 0.082397 | 124.5941 | 124.9191 | 124.7314 | -0.064087 | -0.022889 | 124.5941 | 124.9191 | -0.064087 | 0.082397 | 124.7314 | -124.6307 | -124.8184
71.7812 | 124.9329 | -62.3795 | 62.3795 | -0.015869 | 0.065061 | 0.06225 | 0.0019889 | -0.0026233 | 0.067131 | 0.067276 | 62.5351 | 62.1964 | -62.2421 | 62.265 | -62.3199 | -62.4664 | 0.13275 | 0.018311 | 62.2787 | -62.4619 | 0.13733 | -0.18311 | 124.9146 | 124.6445 | -124.6994 | -0.082397 | -0.10071 | 124.7772 | 62.5122 | 62.3978 | 0.05951 | 124.5758 | 124.9146 | 124.6582 | -0.086975 | -0.082397 | 124.5758 | 124.9146 | -0.086975 | 0.05951 | 124.6582 | -124.6216 | -124.8413
72.7969 | 124.9924 | -62.3657 | 62.3383 | -0.00061033 | 0.068052 | 0.060327 | -0.0005747 | -0.0030505 | 0.068626 | 0.069626 | 62.5214 | 62.1414 | -62.2879 | 62.2375 | -62.3291 | -62.4481 | -0.10529 | -0.036621 | 62.233 | -62.439 | 0.07782 | -0.19684 | 124.8871 | 124.6033 | -124.6674 | -0.073242 | -0.10529 | 124.8093 | 62.2604 | 62.3291 | 0.036621 | 124.5071 | 124.8871 | 124.5987 | -0.082397 | -0.073242 | 124.5071 | 124.8871 | -0.082397 | 0.036621 | 124.5987 | -124.6262 | -124.7772
73.7812 | 124.8825 | -62.3474 | 62.3795 | -0.015869 | 0.066556 | 0.062891 | -0.0007883 | -0.0043323 | 0.068626 | 0.069413 | 62.5076 | 62.2055 | -62.233 | 62.2467 | -62.3245 | -62.4619 | 0.16022 | 0.027466 | 62.2879 | -62.439 | 0.11444 | -0.17395 | 124.855 | 124.5941 | -124.704 | -0.091553 | -0.091553 | 124.7406 | 62.5076 | 62.3749 | 0.022888 | 124.5529 | 124.855 | 124.6353 | -0.11444 | -0.091553 | 124.5529 | 124.855 | -0.11444 | 0.022888 | 124.6353 | -124.6124 | -124.8184
74.7812 | 124.9054 | -62.3611 | 62.384 | -0.00061033 | 0.065915 | 0.056909 | 0.0015615 | -0.0026233 | 0.067985 | 0.070908 | 62.5168 | 62.1872 | -62.2467 | 62.233 | -62.3337 | -62.4756 | 0.13275 | 0.022888 | 62.2925 | -62.4527 | 0.11444 | -0.19684 | 124.8779 | 124.5941 | -124.7177 | -0.091553 | -0.091553 | 124.7635 | 62.4939 | 62.384 | 0.027466 | 124.5483 | 124.8779 | 124.6536 | -0.11444 | -0.091553 | 124.5483 | 124.8779 | -0.11444 | 0.027466 | 124.6536 | -124.6307 | -124.8367
75.7812 | 124.9329 | -62.3566 | 62.3703 | -0.015869 | 0.067411 | 0.061395 | 0.0022025 | -0.0028369 | 0.066704 | 0.069626 | 62.5351 | 62.1918 | -62.2742 | 62.2742 | -62.2971 | -62.4619 | 0.091553 | 0.027466 | 62.2559 | -62.4619 | 0.082397 | -0.17853 | 124.8917 | 124.6307 | -124.6674 | -0.10529 | -0.11444 | 124.8093 | 62.4481 | 62.384 | 0.059509 | 124.5483 | 124.8917 | 124.6124 | -0.10529 | -0.10529 | 124.5483 | 124.8917 | -0.10529 | 0.059509 | 124.6124 | -124.6445 | -124.8322
76.7969 | 125.029 | -62.3337 | 62.3474 | -0.00061033 | 0.061857 | 0.056696 | -0.0037789 | -0.0043323 | 0.067772 | 0.070694 | 62.6083 | 62.1231 | -62.1918 | 62.384 | -62.2101 | -62.3428 | -0.041199 | 0.15106 | 62.2467 | -62.3611 | 0.14191 | -0.2243 | 124.942 | 124.7177 | -124.5575 | -0.027466 | -0.10071 | 124.8001 | 62.2925 | 62.4847 | 0.1236 | 124.4568 | 124.942 | 124.5804 | -0.009155 | -0.027466 | 124.4568 | 124.942 | -0.009155 | 0.1236 | 124.5804 | -124.5392 | -124.7086
77.7812 | 124.8962 | -62.3932 | 62.3611 | -0.0082398 | 0.068265 | 0.062463 | 0.0034841 | -0.0036915 | 0.068199 | 0.069199 | 62.5031 | 62.1826 | -62.265 | 62.2101 | -62.3795 | -62.5031 | 0.022888 | -0.054932 | 62.265 | -62.4893 | 0.12817 | -0.17853 | 124.8962 | 124.6033 | -124.7406 | -0.096131 | -0.09613 | 124.7681 | 62.4161 | 62.3383 | 0.013732 | 124.5758 | 124.8962 | 124.6582 | -0.10986 | -0.096131 | 124.5758 | 124.8962 | -0.10986 | 0.013732 | 124.6582 | -124.6262 | -124.8505
78.7812 | 124.8917 | -62.3749 | 62.439 | 0.0070192 | 0.065275 | 0.061395 | 0.0011343 | -0.0019825 | 0.068199 | 0.068985 | 62.5122 | 62.1826 | -62.2513 | 62.265 | -62.3199 | -62.4802 | 0.16479 | 0.032043 | 62.3199 | -62.4252 | 0.1236 | -0.25635 | 124.8871 | 124.6399 | -124.7589 | -0.050354 | -0.11902 | 124.7635 | 62.5397 | 62.4069 | 0.054932 | 124.5575 | 124.8871 | 124.6948 | -0.10529 | -0.050354 | 124.5575 | 124.8871 | -0.10529 | 0.054932 | 124.6948 | -124.6902 | -124.8642
79.7812 | 124.8917 | -62.3657 | 62.3978 | -0.015869 | 0.068265 | 0.061609 | -0.0010019 | -0.0051867 | 0.067131 | 0.06984 | 62.5259 | 62.2055 | -62.2147 | 62.2559 | -62.3108 | -62.4664 | 0.14648 | 0.041199 | 62.3016 | -62.4344 | 0.15106 | -0.19226 | 124.8917 | 124.6216 | -124.7086 | -0.068664 | -0.09613 | 124.7406 | 62.5122 | 62.4069 | 0.054932 | 124.5712 | 124.8917 | 124.6674 | -0.10071 | -0.068664 | 124.5712 | 124.8917 | -0.10071 | 0.054932 | 124.6674 | -124.6124 | -124.8322
80.7812 | 124.8962 | -62.3703 | 62.4023 | -0.0082398 | 0.066984 | 0.057764 | -0.0007883 | -0.0045459 | 0.068626 | 0.06984 | 62.5168 | 62.2101 | -62.2421 | 62.2513 | -62.3245 | -62.4802 | 0.16479 | 0.009155 | 62.3016 | -62.4344 | 0.12817 | -0.19226 | 124.8871 | 124.6216 | -124.7269 | -0.064087 | -0.10071 | 124.7589 | 62.5351 | 62.3795 | 0.045776 | 124.5804 | 124.8871 | 124.6719 | -0.10986 | -0.064087 | 124.5804 | 124.8871 | -0.10986 | 0.045776 | 124.6719 | -124.6445 | -124.8367
81.7812 | 124.8962 | -62.3749 | 62.4069 | 0.0070192 | 0.063352 | 0.059473 | -0.0007883 | -0.0036915 | 0.066704 | 0.068985 | 62.5122 | 62.2009 | -62.233 | 62.2513 | -62.3199 | -62.4573 | 0.15106 | 0.022888 | 62.3291 | -62.4344 | 0.14191 | -0.20599 | 124.8871 | 124.6262 | -124.7269 | -0.059509 | -0.077819 | 124.7452 | 62.5259 | 62.3978 | 0.054932 | 124.5758 | 124.8871 | 124.704 | -0.082397 | -0.059509 | 124.5758 | 124.8871 | -0.082397 | 0.054932 | 124.704 | -124.6399 | -124.8413
82.7969 | 124.9741 | -62.3428 | 62.3291 | -0.0082398 | 0.063779 | 0.0552 | 0.0030569 | -0.0028369 | 0.066917 | 0.068558 | 62.5214 | 62.1368 | -62.2879 | 62.2742 | -62.3291 | -62.4435 | -0.10529 | -0.022888 | 62.233 | -62.4527 | 0.054931 | -0.19226 | 124.8642 | 124.617 | -124.6582 | -0.10986 | -0.096131 | 124.8093 | 62.2375 | 62.3199 | 0.013732 | 124.4797 | 124.8642 | 124.5758 | -0.10071 | -0.10986 | 124.4797 | 124.8642 | -0.10071 | 0.013732 | 124.5758 | -124.617 | -124.7818
83.7812 | 124.9374 | -62.352 | 62.3749 | -0.00061033 | 0.062925 | 0.0599 | -0.0001473 | -0.0036915 | 0.065636 | 0.067704 | 62.59 | 62.1689 | -62.2101 | 62.3199 | -62.2559 | -62.3932 | 0.064087 | 0.086975 | 62.2604 | -62.4252 | 0.14191 | -0.20599 | 124.942 | 124.6719 | -124.6307 | -0.073242 | -0.11444 | 124.8001 | 62.4161 | 62.439 | 0.096131 | 124.5209 | 124.942 | 124.6124 | -0.041198 | -0.073242 | 124.5209 | 124.942 | -0.041198 | 0.096131 | 124.6124 | -124.585 | -124.8001
84.7812 | 124.9146 | -62.3703 | 62.4115 | -0.0082398 | 0.065488 | 0.063104 | 0.0011343 | -0.0047595 | 0.066063 | 0.071122 | 62.5442 | 62.1872 | -62.2101 | 62.2787 | -62.3016 | -62.4435 | 0.11444 | 0.045776 | 62.2925 | -62.4527 | 0.16022 | -0.2243 | 124.9145 | 124.649 | -124.7131 | -0.082398 | -0.11902 | 124.7543 | 62.4847 | 62.4161 | 0.068664 | 124.5575 | 124.9145 | 124.6628 | -0.073242 | -0.082398 | 124.5575 | 124.9145 | -0.073242 | 0.068664 | 124.6628 | -124.6216 | -124.8642
85.7812 | 124.9649 | -62.3611 | 62.3978 | -0.00061033 | 0.06207 | 0.060327 | -0.0007883 | -0.0043323 | 0.066063 | 0.071335 | 62.5946 | 62.1414 | -62.2192 | 62.3199 | -62.2375 | -62.3978 | 0.059509 | 0.09613 | 62.2742 | -62.4069 | 0.14191 | -0.25635 | 124.9557 | 124.6811 | -124.6353 | -0.045776 | -0.1236 | 124.8138 | 62.4207 | 62.4573 | 0.1236 | 124.5026 | 124.9557 | 124.6353 | -0.036621 | -0.045776 | 124.5026 | 124.9557 | -0.036621 | 0.1236 | 124.6353 | -124.617 | -124.8047
86.7969 | 125.0153 | -62.3428 | 62.3474 | -0.00061033 | 0.060361 | 0.058832 | 0.0026297 | -0.0056141 | 0.06649 | 0.069626 | 62.6266 | 62.1231 | -62.1918 | 62.3749 | -62.178 | -62.3428 | -0.054932 | 0.15564 | 62.233 | -62.3886 | 0.15106 | -0.2243 | 124.9695 | 124.7177 | -124.5255 | -0.045777 | -0.11444 | 124.8184 | 62.2879 | 62.4985 | 0.16479 | 124.4659 | 124.9695 | 124.5758 | 0 | -0.045777 | 124.4659 | 124.9695 | 0 | 0.16479 | 124.5758 | -124.5392 | -124.736
87.7812 | 124.9329 | -62.3795 | 62.3749 | -0.00061033 | 0.066343 | 0.062036 | 0.0051931 | -0.0036915 | 0.068626 | 0.067704 | 62.5397 | 62.1918 | -62.233 | 62.2787 | -62.2971 | -62.4619 | 0.082397 | 0.041199 | 62.2742 | -62.4756 | 0.14648 | -0.18311 | 124.9191 | 124.6582 | -124.6719 | -0.09613 | -0.10071 | 124.7726 | 62.4619 | 62.4207 | 0.082398 | 124.5712 | 124.9191 | 124.6536 | -0.082397 | -0.09613 | 124.5712 | 124.9191 | -0.082397 | 0.082398 | 124.6536 | -124.6078 | -124.8505
88.7812 | 125.0244 | -62.3154 | 62.352 | -0.00061033 | 0.060148 | 0.061395 | -0.0012155 | -0.0045459 | 0.066704 | 0.068772 | 62.6038 | 62.1323 | -62.2101 | 62.3703 | -62.2101 | -62.352 | -0.068665 | 0.1236 | 62.2559 | -62.4023 | 0.10529 | -0.21973 | 124.9191 | 124.6857 | -124.5621 | -0.086975 | -0.096131 | 124.8138 | 62.2467 | 62.439 | 0.10529 | 124.4476 | 124.9191 | 124.5712 | -0.036621 | -0.086975 | 124.4476 | 124.9191 | -0.036621 | 0.10529 | 124.5712 | -124.5621 | -124.7543
89.7812 | 125.0244 | -62.3383 | 62.3474 | 0.0070192 | 0.061643 | 0.060114 | -0.0027109 | -0.0051867 | 0.065849 | 0.067704 | 62.6175 | 62.114 | -62.2101 | 62.3657 | -62.2055 | -62.3291 | -0.07782 | 0.14648 | 62.233 | -62.3611 | 0.12817 | -0.23346 | 124.9557 | 124.704 | -124.5529 | -0.022888 | -0.11444 | 124.8276 | 62.2604 | 62.4847 | 0.13275 | 124.4522 | 124.9557 | 124.5712 | 0.009155 | -0.022888 | 124.4522 | 124.9557 | 0.009155 | 0.13275 | 124.5712 | -124.5575 | -124.7086
90.7812 | 125.0244 | -62.3291 | 62.3657 | -0.00061033 | 0.061643 | 0.060541 | -0.0016427 | -0.0066821 | 0.067131 | 0.068558 | 62.6266 | 62.0911 | -62.2101 | 62.3886 | -62.1689 | -62.3016 | -0.054932 | 0.14191 | 62.2009 | -62.384 | 0.11902 | -0.27466 | 124.9557 | 124.7177 | -124.5346 | -0.054931 | -0.1648 | 124.8367 | 62.2742 | 62.471 | 0.16022 | 124.4202 | 124.9557 | 124.53 | 0.027466 | -0.054931 | 124.4202 | 124.9557 | 0.027466 | 0.16022 | 124.53 | -124.5758 | -124.7498
91.7812 | 125.0061 | -62.3383 | 62.3474 | 0.014648 | 0.061857 | 0.059473 | 0.0004935 | -0.0043323 | 0.070549 | 0.068772 | 62.5534 | 62.1002 | -62.2192 | 62.3199 | -62.2604 | -62.3932 | -0.07782 | 0.064087 | 62.233 | -62.3978 | 0.11902 | -0.24719 | 124.8917 | 124.6582 | -124.6078 | -0.059509 | -0.11444 | 124.7726 | 62.2604 | 62.4023 | 0.07782 | 124.4385 | 124.8917 | 124.5712 | -0.054931 | -0.059509 | 124.4385 | 124.8917 | -0.054931 | 0.07782 | 124.5712 | -124.5666 | -124.7452
92.7969 | 124.8734 | -62.4298 | 62.352 | -0.00061033 | 0.068052 | 0.064813 | 0.0075431 | -0.0047595 | 0.068413 | 0.070481 | 62.4802 | 62.1506 | -62.2604 | 62.2101 | -62.3886 | -62.5351 | 0.054932 | -0.091553 | 62.2467 | -62.4939 | 0.16937 | -0.20142 | 124.91 | 124.6399 | -124.7406 | -0.064086 | -0.10529 | 124.7406 | 62.4847 | 62.3383 | 0.041199 | 124.5804 | 124.91 | 124.6765 | -0.10528 | -0.064086 | 124.5804 | 124.91 | -0.10528 | 0.041199 | 124.6765 | -124.6124 | -124.8459
93.7812 | 124.9786 | -62.3383 | 62.3291 | -0.0082398 | 0.06207 | 0.054132 | -0.0014291 | -0.0039051 | 0.066917 | 0.068985 | 62.558 | 62.0682 | -62.2238 | 62.3016 | -62.2696 | -62.4023 | -0.10529 | 0.032043 | 62.2284 | -62.4023 | 0.11444 | -0.26093 | 124.8962 | 124.6399 | -124.5987 | -0.064087 | -0.10071 | 124.7818 | 62.233 | 62.3703 | 0.068665 | 124.4064 | 124.8962 | 124.5667 | -0.064087 | -0.064087 | 124.4064 | 124.8962 | -0.064087 | 0.068665 | 124.5667 | -124.5529 | -124.7314
94.7969 | 124.9008 | -62.3657 | 62.3978 | -0.0082398 | 0.06442 | 0.058618 | 0.0028433 | -0.0051867 | 0.068199 | 0.065567 | 62.5076 | 62.2009 | -62.2559 | 62.265 | -62.3108 | -62.4802 | 0.13275 | 0.022888 | 62.2696 | -62.4527 | 0.10986 | -0.19684 | 124.8734 | 124.6307 | -124.7086 | -0.086975 | -0.12817 | 124.7635 | 62.4985 | 62.3886 | 0.054932 | 124.5667 | 124.8734 | 124.6353 | -0.11444 | -0.086975 | 124.5667 | 124.8734 | -0.11444 | 0.054932 | 124.6353 | -124.6536 | -124.8505
95.7812 | 124.9695 | -62.3337 | 62.3245 | -0.0082398 | 0.061002 | 0.056482 | 6.6302e-05 | -0.0039051 | 0.066704 | 0.071335 | 62.5534 | 62.1094 | -62.2513 | 62.3154 | -62.2604 | -62.3978 | -0.11902 | 0.027466 | 62.2009 | -62.4069 | 0.082397 | -0.21515 | 124.8871 | 124.649 | -124.585 | -0.073242 | -0.1236 | 124.8047 | 62.2147 | 62.3611 | 0.073242 | 124.4431 | 124.8871 | 124.5346 | -0.064087 | -0.073242 | 124.4431 | 124.8871 | -0.064087 | 0.073242 | 124.5346 | -124.5758 | -124.7314
96.7969 | 124.9191 | -62.3978 | 62.3245 | -0.0082398 | 0.06442 | 0.060541 | 0.0060477 | -0.0036915 | 0.067558 | 0.071122 | 62.4939 | 62.1689 | -62.2833 | 62.2101 | -62.3611 | -62.5031 | -0.064087 | -0.086975 | 62.2192 | -62.4939 | 0.11444 | -0.15564 | 124.8917 | 124.6078 | -124.6857 | -0.09613 | -0.10529 | 124.7772 | 62.3337 | 62.3108 | 0.036621 | 124.5666 | 124.8917 | 124.617 | -0.10529 | -0.09613 | 124.5666 | 124.8917 | -0.10529 | 0.036621 | 124.617 | -124.6078 | -124.8184
97.7812 | 125.029 | -62.2925 | 62.3291 | -0.0082398 | 0.061429 | 0.059686 | -0.0020701 | -0.0062549 | 0.067345 | 0.071122 | 62.5992 | 62.1231 | -62.2055 | 62.3611 | -62.2009 | -62.3383 | -0.086975 | 0.1236 | 62.2513 | -62.3932 | 0.086975 | -0.20599 | 124.8917 | 124.6536 | -124.53 | -0.10071 | -0.07782 | 124.8047 | 62.2055 | 62.4161 | 0.091552 | 124.4156 | 124.8917 | 124.5438 | -0.045777 | -0.10071 | 124.4156 | 124.8917 | -0.045777 | 0.091552 | 124.5438 | -124.5346 | -124.7223
98.7812 | 125.0015 | -62.3245 | 62.3108 | -0.0082398 | 0.061216 | 0.059473 | 0.0017753 | -0.0051867 | 0.066917 | 0.069626 | 62.5671 | 62.0819 | -62.2284 | 62.3199 | -62.2467 | -62.3703 | -0.16479 | 0.045776 | 62.1643 | -62.4115 | 0.09613 | -0.22888 | 124.8917 | 124.6445 | -124.5575 | -0.086975 | -0.14648 | 124.7955 | 62.1597 | 62.3703 | 0.07782 | 124.4064 | 124.8917 | 124.4888 | -0.045776 | -0.086975 | 124.4064 | 124.8917 | -0.045776 | 0.07782 | 124.4888 | -124.5392 | -124.7223
99.7812 | 125.0107 | -62.3611 | 62.3016 | -0.015869 | 0.061643 | 0.063745 | 0.0007071 | -0.0068957 | 0.067772 | 0.068985 | 62.59 | 62.0682 | -62.2467 | 62.3154 | -62.2421 | -62.3703 | -0.1831 | 0.050354 | 62.1826 | -62.4161 | 0.11444 | -0.23346 | 124.9512 | 124.6765 | -124.5438 | -0.054932 | -0.11902 | 124.8367 | 62.178 | 62.4115 | 0.11902 | 124.4293 | 124.9512 | 124.5438 | -0.009155 | -0.054932 | 124.4293 | 124.9512 | -0.009155 | 0.11902 | 124.5438 | -124.5483 | -124.7177
100.7812 | 124.9786 | -62.3337 | 62.3154 | -0.0082398 | 0.061216 | 0.062677 | 0.0011343 | -0.0034777 | 0.068626 | 0.070053 | 62.5809 | 62.1002 | -62.233 | 62.3245 | -62.265 | -62.384 | -0.16937 | 0.041199 | 62.178 | -62.4298 | 0.10071 | -0.21515 | 124.9146 | 124.6582 | -124.5804 | -0.096131 | -0.13733 | 124.8138 | 62.1643 | 62.3749 | 0.068664 | 124.4339 | 124.9146 | 124.5117 | -0.050354 | -0.096131 | 124.4339 | 124.9146 | -0.050354 | 0.068664 | 124.5117 | -124.5483 | -124.7452
101.7812 | 125.0015 | -62.3383 | 62.3062 | 0.0070192 | 0.063779 | 0.062891 | 0.0015615 | -0.0051867 | 0.067985 | 0.06984 | 62.5854 | 62.0956 | -62.233 | 62.3428 | -62.2559 | -62.3749 | -0.17853 | 0.045776 | 62.1689 | -62.4207 | 0.10529 | -0.21057 | 124.9237 | 124.6811 | -124.5621 | -0.082397 | -0.13733 | 124.8184 | 62.1597 | 62.384 | 0.082398 | 124.4339 | 124.9237 | 124.5071 | -0.036621 | -0.082397 | 124.4339 | 124.9237 | -0.036621 | 0.082398 | 124.5071 | -124.5392 | -124.7269
102.7812 | 125.0061 | -62.3383 | 62.2971 | -0.00061033 | 0.063138 | 0.058405 | 0.0036979 | -0.0051867 | 0.066704 | 0.069199 | 62.59 | 62.1002 | -62.2421 | 62.3337 | -62.2467 | -62.3886 | -0.19684 | 0.027466 | 62.1735 | -62.4481 | 0.096131 | -0.19684 | 124.9283 | 124.6719 | -124.5438 | -0.10986 | -0.1236 | 124.8322 | 62.1414 | 62.3657 | 0.091553 | 124.4385 | 124.9283 | 124.5117 | -0.050354 | -0.10986 | 124.4385 | 124.9283 | -0.050354 | 0.091553 | 124.5117 | -124.5392 | -124.7452
103.7812 | 125.0153 | -62.352 | 62.3199 | 0.0070192 | 0.063779 | 0.060327 | 0.0043387 | -0.0034777 | 0.066704 | 0.067917 | 62.5809 | 62.0956 | -62.2284 | 62.3062 | -62.2559 | -62.3978 | -0.17395 | 0.027466 | 62.1872 | -62.4435 | 0.1236 | -0.2243 | 124.9329 | 124.6582 | -124.5758 | -0.091552 | -0.13275 | 124.8093 | 62.178 | 62.3795 | 0.096131 | 124.4476 | 124.9329 | 124.5392 | -0.045776 | -0.091552 | 124.4476 | 124.9329 | -0.045776 | 0.096131 | 124.5392 | -124.5483 | -124.7635
104.7812 | 124.9603 | -62.3474 | 62.3245 | -0.00061033 | 0.061002 | 0.059686 | -0.0014291 | -0.0056141 | 0.06649 | 0.06984 | 62.5214 | 62.1048 | -62.2375 | 62.2833 | -62.2833 | -62.4069 | -0.07782 | 0.018311 | 62.2284 | -62.4115 | 0.10986 | -0.21973 | 124.8688 | 124.6307 | -124.6078 | -0.064087 | -0.09613 | 124.7589 | 62.2696 | 62.3657 | 0.064087 | 124.4522 | 124.8688 | 124.5758 | -0.059509 | -0.064087 | 124.4522 | 124.8688 | -0.059509 | 0.064087 | 124.5758 | -124.5621 | -124.736
105.7812 | 124.9695 | -62.3657 | 62.3108 | -0.0082398 | 0.065488 | 0.061609 | 0.0054069 | -0.0036915 | 0.067345 | 0.069199 | 62.5168 | 62.1323 | -62.2604 | 62.2604 | -62.3154 | -62.4435 | -0.10529 | -0.018311 | 62.1964 | -62.4664 | 0.10529 | -0.17853 | 124.8825 | 124.6262 | -124.6262 | -0.10071 | -0.11444 | 124.7772 | 62.2604 | 62.3474 | 0.050354 | 124.498 | 124.8825 | 124.5621 | -0.077819 | -0.10071 | 124.498 | 124.8825 | -0.077819 | 0.050354 | 124.5621 | -124.5712 | -124.7772
106.7969 | 124.8642 | -62.3703 | 62.352 | -0.00061033 | 0.068265 | 0.064813 | 0.0032705 | -0.0019825 | 0.066917 | 0.069413 | 62.4664 | 62.178 | -62.2833 | 62.1689 | -62.4023 | -62.5305 | 0.009155 | -0.10071 | 62.2055 | -62.4939 | 0.086975 | -0.17395 | 124.8367 | 124.5392 | -124.7543 | -0.1236 | -0.14648 | 124.7498 | 62.3795 | 62.2696 | -0.032044 | 124.5483 | 124.8367 | 124.5758 | -0.16022 | -0.1236 | 124.5483 | 124.8367 | -0.16022 | -0.032044 | 124.5758 | -124.6353 | -124.8459
107.7812 | 124.8734 | -62.3886 | 62.3245 | -0.0082398 | 0.066343 | 0.064172 | 0.0034841 | -0.0026233 | 0.067131 | 0.070053 | 62.4664 | 62.1689 | -62.2833 | 62.1826 | -62.3749 | -62.5168 | 0.018311 | -0.10986 | 62.2467 | -62.4664 | 0.10529 | -0.15564 | 124.855 | 124.5712 | -124.6994 | -0.07782 | -0.07782 | 124.7498 | 62.4069 | 62.2787 | 0.013733 | 124.5575 | 124.855 | 124.6353 | -0.12817 | -0.07782 | 124.5575 | 124.855 | -0.12817 | 0.013733 | 124.6353 | -124.6078 | -124.791
108.7812 | 124.8825 | -62.3749 | 62.3383 | -0.0082398 | 0.068265 | 0.064172 | 0.0022025 | -0.0017687 | 0.069481 | 0.070481 | 62.4802 | 62.1643 | -62.2833 | 62.1826 | -62.3657 | -62.5076 | 0 | -0.082397 | 62.2284 | -62.4893 | 0.091553 | -0.17395 | 124.855 | 124.5575 | -124.704 | -0.11444 | -0.10986 | 124.7635 | 62.3749 | 62.2925 | 0.009155 | 124.5392 | 124.855 | 124.6033 | -0.13275 | -0.11444 | 124.5392 | 124.855 | -0.13275 | 0.009155 | 124.6033 | -124.6216 | -124.8276
109.7812 | 124.9557 | -62.3611 | 62.3474 | -0.00061033 | 0.065702 | 0.060754 | 0.0007071 | -0.0034777 | 0.067985 | 0.070053 | 62.4939 | 62.1735 | -62.2879 | 62.2055 | -62.3337 | -62.471 | -0.073242 | -0.059509 | 62.2238 | -62.4619 | 0.073242 | -0.17395 | 124.855 | 124.5667 | -124.6811 | -0.10071 | -0.1236 | 124.7818 | 62.2879 | 62.3016 | 0.027466 | 124.5346 | 124.855 | 124.585 | -0.10986 | -0.10071 | 124.5346 | 124.855 | -0.10986 | 0.027466 | 124.585 | -124.6353 | -124.8093
110.7812 | 124.9969 | -62.3108 | 62.3016 | 0.0070192 | 0.064847 | 0.066095 | -0.0001473 | -0.0041187 | 0.066917 | 0.069413 | 62.5442 | 62.1368 | -62.2604 | 62.2787 | -62.2742 | -62.4069 | -0.13733 | 0.009155 | 62.2101 | -62.4481 | 0.050354 | -0.1648 | 124.855 | 124.5895 | -124.5758 | -0.13733 | -0.091553 | 124.8047 | 62.1735 | 62.3199 | 0.036621 | 124.4476 | 124.855 | 124.5209 | -0.09613 | -0.13733 | 124.4476 | 124.855 | -0.09613 | 0.036621 | 124.5209 | -124.5621 | -124.7498
111.7812 | 124.8917 | -62.3611 | 62.3383 | 0.0070192 | 0.067197 | 0.064813 | 0.0017753 | -0.0028369 | 0.069267 | 0.06749 | 62.471 | 62.178 | -62.2742 | 62.2009 | -62.3657 | -62.4939 | 0 | -0.086975 | 62.2467 | -62.4756 | 0.086975 | -0.16022 | 124.8322 | 124.5621 | -124.704 | -0.11444 | -0.091553 | 124.7452 | 62.3611 | 62.2742 | -0.004578 | 124.5392 | 124.8322 | 124.6078 | -0.13275 | -0.11444 | 124.5392 | 124.8322 | -0.13275 | -0.004578 | 124.6078 | -124.6124 | -124.8138
112.8438 | 124.9924 | -62.3108 | 62.3154 | -0.0082398 | 0.062284 | 0.064386 | -0.0014291 | -0.0028369 | 0.067558 | 0.068985 | 62.5809 | 62.0865 | -62.233 | 62.3199 | -62.2375 | -62.3566 | -0.16022 | 0.059509 | 62.1826 | -62.4435 | 0.07782 | -0.22888 | 124.8917 | 124.6307 | -124.5529 | -0.13275 | -0.13275 | 124.8138 | 62.1506 | 62.3703 | 0.073242 | 124.3973 | 124.8917 | 124.4934 | -0.045776 | -0.13275 | 124.3973 | 124.8917 | -0.045776 | 0.073242 | 124.4934 | -124.5483 | -124.7589
113.7969 | 125.0015 | -62.3154 | 62.3566 | 0.0070192 | 0.061857 | 0.05755 | 0.0002799 | -0.0058277 | 0.067131 | 0.070694 | 62.6129 | 62.1185 | -62.178 | 62.3566 | -62.2009 | -62.3383 | -0.032043 | 0.14191 | 62.233 | -62.384 | 0.13733 | -0.23804 | 124.9283 | 124.6719 | -124.5575 | -0.068664 | -0.1236 | 124.791 | 62.2833 | 62.4573 | 0.11444 | 124.4339 | 124.9283 | 124.5483 | -0.022888 | -0.068664 | 124.4339 | 124.9283 | -0.022888 | 0.11444 | 124.5483 | -124.5346 | -124.7406
114.7812 | 125.0153 | -62.3383 | 62.3108 | 0.0070192 | 0.064634 | 0.0599 | 0.0011343 | -0.0043323 | 0.067345 | 0.070908 | 62.5763 | 62.1048 | -62.2421 | 62.3108 | -62.2467 | -62.3703 | -0.20142 | 0.036621 | 62.146 | -62.4115 | 0.096131 | -0.20599 | 124.9146 | 124.649 | -124.5575 | -0.073242 | -0.1648 | 124.8184 | 62.1368 | 62.3749 | 0.091553 | 124.4431 | 124.9146 | 124.4843 | -0.032043 | -0.073242 | 124.4431 | 124.9146 | -0.032043 | 0.091553 | 124.4843 | -124.5529 | -124.7223
115.7969 | 124.9649 | -62.2833 | 62.384 | -0.00061033 | 0.062497 | 0.060541 | -0.0005747 | -0.0062549 | 0.066063 | 0.068772 | 62.6083 | 62.1277 | -62.2009 | 62.3428 | -62.2147 | -62.3703 | 0.036621 | 0.1236 | 62.2467 | -62.3978 | 0.082397 | -0.25635 | 124.8917 | 124.6262 | -124.5987 | -0.11444 | -0.13733 | 124.8093 | 62.3199 | 62.4069 | 0.068664 | 124.411 | 124.8917 | 124.53 | -0.086975 | -0.11444 | 124.411 | 124.8917 | -0.086975 | 0.068664 | 124.53 | -124.585 | -124.7818
116.7969 | 124.9969 | -62.3291 | 62.3611 | -0.00061033 | 0.061643 | 0.058405 | 0.0004935 | -0.0060413 | 0.066063 | 0.068344 | 62.6175 | 62.1002 | -62.1689 | 62.384 | -62.1872 | -62.3199 | -0.045776 | 0.16479 | 62.2375 | -62.3795 | 0.16022 | -0.26093 | 124.9466 | 124.7131 | -124.5483 | -0.050354 | -0.1236 | 124.7864 | 62.2833 | 62.4939 | 0.14191 | 124.4293 | 124.9466 | 124.5667 | 0.009156 | -0.050354 | 124.4293 | 124.9466 | 0.009156 | 0.14191 | 124.5667 | -124.53 | -124.7406
117.7812 | 124.8596 | -62.384 | 62.3291 | -0.00061033 | 0.067838 | 0.060541 | 0.0039115 | -0.0032641 | 0.065208 | 0.068558 | 62.471 | 62.1597 | -62.2833 | 62.1918 | -62.3886 | -62.5214 | 0 | -0.09613 | 62.2238 | -62.5214 | 0.10071 | -0.16937 | 124.855 | 124.5758 | -124.7177 | -0.13733 | -0.10529 | 124.7543 | 62.384 | 62.2879 | -0.004578 | 124.5438 | 124.855 | 124.6078 | -0.13733 | -0.13733 | 124.5438 | 124.855 | -0.13733 | -0.004578 | 124.6078 | -124.6124 | -124.8505
118.8125 | 125.0107 | -62.3383 | 62.3337 | -0.0082398 | 0.060148 | 0.058618 | -0.0005747 | -0.0056141 | 0.064568 | 0.069626 | 62.6083 | 62.1094 | -62.2009 | 62.352 | -62.2101 | -62.3337 | -0.086975 | 0.13733 | 62.2421 | -62.3703 | 0.13733 | -0.2243 | 124.9466 | 124.6902 | -124.5438 | -0.032043 | -0.091553 | 124.8093 | 62.2513 | 62.4756 | 0.12817 | 124.4476 | 124.9466 | 124.5804 | 0.004578 | -0.032043 | 124.4476 | 124.9466 | 0.004578 | 0.12817 | 124.5804 | -124.5346 | -124.704
119.7969 | 124.8779 | -62.4069 | 62.3337 | -0.00061033 | 0.066556 | 0.058832 | 0.0054069 | -0.0049731 | 0.068626 | 0.068772 | 62.4619 | 62.1735 | -62.2742 | 62.1826 | -62.384 | -62.5259 | 0.018311 | -0.091553 | 62.2513 | -62.5076 | 0.13275 | -0.16022 | 124.8688 | 124.5895 | -124.7177 | -0.10071 | -0.082397 | 124.736 | 62.4252 | 62.3154 | 0.022888 | 124.5804 | 124.8688 | 124.6582 | -0.11902 | -0.10071 | 124.5804 | 124.8688 | -0.11902 | 0.022888 | 124.6582 | -124.6078 | -124.8413
120.7812 | 124.855 | -62.3703 | 62.352 | -0.00061033 | 0.067197 | 0.063745 | 0.0041251 | -0.0028369 | 0.067131 | 0.067704 | 62.4802 | 62.178 | -62.2879 | 62.1872 | -62.3886 | -62.5259 | 0.054932 | -0.09613 | 62.2421 | -62.4985 | 0.082397 | -0.17395 | 124.8505 | 124.5575 | -124.7406 | -0.12817 | -0.10986 | 124.7681 | 62.4252 | 62.2742 | -0.018311 | 124.5483 | 124.8505 | 124.6124 | -0.15564 | -0.12817 | 124.5483 | 124.8505 | -0.15564 | -0.018311 | 124.6124 | -124.6399 | -124.8505
121.7812 | 124.8642 | -62.3428 | 62.3611 | -0.00061033 | 0.068906 | 0.060327 | 0.0041251 | -0.0019825 | 0.067345 | 0.069626 | 62.4847 | 62.1506 | -62.2925 | 62.1872 | -62.3795 | -62.5305 | 0.054932 | -0.073242 | 62.233 | -62.4802 | 0.050354 | -0.21057 | 124.8276 | 124.53 | -124.7406 | -0.13733 | -0.12817 | 124.7772 | 62.3978 | 62.2696 | -0.036622 | 124.4934 | 124.8276 | 124.5758 | -0.18768 | -0.13733 | 124.4934 | 124.8276 | -0.18768 | -0.036622 | 124.5758 | -124.6536 | -124.8413
122.7812 | 124.8596 | -62.3795 | 62.3199 | 0.0070192 | 0.066556 | 0.060968 | 0.0030569 | -0.0002735 | 0.068626 | 0.068985 | 62.4664 | 62.1826 | -62.265 | 62.1552 | -62.3932 | -62.5214 | 0.032043 | -0.091553 | 62.2421 | -62.4802 | 0.11444 | -0.13733 | 124.8459 | 124.5346 | -124.7131 | -0.10071 | -0.07782 | 124.7314 | 62.4115 | 62.2879 | -0.013732 | 124.5621 | 124.8459 | 124.6216 | -0.14191 | -0.10071 | 124.5621 | 124.8459 | -0.14191 | -0.013732 | 124.6216 | -124.585 | -124.8001
123.7812 | 124.8505 | -62.3749 | 62.3337 | -0.0082398 | 0.068052 | 0.0646 | 0.0024161 | -0.0007007 | 0.070549 | 0.070694 | 62.4847 | 62.1918 | -62.265 | 62.1918 | -62.3703 | -62.5168 | 0.041199 | -0.09613 | 62.2375 | -62.4802 | 0.10986 | -0.14191 | 124.8596 | 124.5667 | -124.704 | -0.10529 | -0.09613 | 124.7498 | 62.4161 | 62.2787 | 0.004578 | 124.5667 | 124.8596 | 124.6124 | -0.14191 | -0.10529 | 124.5667 | 124.8596 | -0.14191 | 0.004578 | 124.6124 | -124.5987 | -124.8138
124.7969 | 124.9466 | -62.3245 | 62.3245 | -0.00061033 | 0.060575 | 0.058405 | -0.0052743 | -0.0041187 | 0.068199 | 0.069626 | 62.5214 | 62.1002 | -62.2467 | 62.265 | -62.2833 | -62.4023 | -0.073242 | 0.022888 | 62.2421 | -62.3978 | 0.07782 | -0.2243 | 124.8459 | 124.5895 | -124.6078 | -0.073242 | -0.082398 | 124.7681 | 62.2513 | 62.3474 | 0.041199 | 124.4247 | 124.8459 | 124.5666 | -0.07782 | -0.073242 | 124.4247 | 124.8459 | -0.07782 | 0.041199 | 124.5666 | -124.5712 | -124.7223
125.7812 | 124.8688 | -62.3474 | 62.3428 | -0.00061033 | 0.069333 | 0.063532 | 0.0049795 | -0.0026233 | 0.070122 | 0.070694 | 62.5076 | 62.1643 | -62.2879 | 62.2009 | -62.3611 | -62.5076 | 0.032043 | -0.064087 | 62.2284 | -62.5168 | 0.059509 | -0.17853 | 124.855 | 124.5483 | -124.704 | -0.16937 | -0.11444 | 124.7955 | 62.3795 | 62.2833 | -0.013733 | 124.5117 | 124.855 | 124.5758 | -0.16022 | -0.16937 | 124.5117 | 124.855 | -0.16022 | -0.013733 | 124.5758 | -124.6307 | -124.8596
126.7969 | 124.8871 | -62.352 | 62.3291 | -0.00061033 | 0.066556 | 0.063104 | 0.0015615 | -0.0017687 | 0.06884 | 0.069626 | 62.471 | 62.1872 | -62.2559 | 62.1826 | -62.3611 | -62.5031 | 0.013733 | -0.086975 | 62.2238 | -62.4893 | 0.096131 | -0.14191 | 124.823 | 124.5346 | -124.6902 | -0.13733 | -0.10529 | 124.7269 | 62.3657 | 62.265 | -0.009155 | 124.5392 | 124.823 | 124.5758 | -0.15106 | -0.13733 | 124.5392 | 124.823 | -0.15106 | -0.009155 | 124.5758 | -124.585 | -124.8184
127.7812 | 124.91 | -62.3474 | 62.3383 | -0.00061033 | 0.067411 | 0.063959 | 0.0028433 | -0.0013415 | 0.069054 | 0.070053 | 62.5397 | 62.1918 | -62.2467 | 62.2604 | -62.3062 | -62.4619 | 0.036621 | 0.009155 | 62.2467 | -62.471 | 0.10071 | -0.14648 | 124.8871 | 124.6078 | -124.6445 | -0.1236 | -0.091553 | 124.7864 | 62.384 | 62.3566 | 0.041199 | 124.5392 | 124.8871 | 124.5941 | -0.11444 | -0.1236 | 124.5392 | 124.8871 | -0.11444 | 0.041199 | 124.5941 | -124.585 | -124.8093
128.7812 | 124.9283 | -62.3383 | 62.3474 | -0.00061033 | 0.06677 | 0.063104 | 0.0002799 | -0.0013415 | 0.066277 | 0.06749 | 62.5488 | 62.2055 | -62.2421 | 62.2742 | -62.2742 | -62.439 | 0.022888 | 0.022888 | 62.265 | -62.4619 | 0.096131 | -0.14191 | 124.8871 | 124.6124 | -124.6216 | -0.1236 | -0.082397 | 124.791 | 62.3611 | 62.3611 | 0.064087 | 124.5438 | 124.8871 | 124.6033 | -0.10071 | -0.1236 | 124.5438 | 124.8871 | -0.10071 | 0.064087 | 124.6033 | -124.5895 | -124.8093
129.7812 | 124.8871 | -62.3703 | 62.352 | -0.00061033 | 0.068479 | 0.062891 | 0.0011343 | -0.0004871 | 0.067558 | 0.070481 | 62.5259 | 62.1689 | -62.2513 | 62.2284 | -62.3245 | -62.4847 | 0.036621 | -0.036621 | 62.2559 | -62.4802 | 0.11902 | -0.18311 | 124.8962 | 124.5987 | -124.6765 | -0.10986 | -0.096131 | 124.7772 | 62.4069 | 62.3337 | 0.045776 | 124.5392 | 124.8962 | 124.6262 | -0.11444 | -0.10986 | 124.5392 | 124.8962 | -0.11444 | 0.045776 | 124.6262 | -124.6033 | -124.8322
130.7812 | 124.8505 | -62.3657 | 62.352 | -0.00061033 | 0.067197 | 0.063104 | 0.0028433 | -0.0004871 | 0.066704 | 0.069413 | 62.4756 | 62.1689 | -62.2787 | 62.2009 | -62.3749 | -62.5076 | 0.050354 | -0.059509 | 62.2375 | -62.4893 | 0.086975 | -0.18311 | 124.8413 | 124.5667 | -124.7269 | -0.1236 | -0.11444 | 124.7543 | 62.4161 | 62.3062 | -0.009155 | 124.5346 | 124.8413 | 124.6033 | -0.14191 | -0.1236 | 124.5346 | 124.8413 | -0.14191 | -0.009155 | 124.6033 | -124.6307 | -124.8413
131.7812 | 124.9191 | -62.3383 | 62.3383 | -0.015869 | 0.067197 | 0.065454 | 0.0028433 | -0.0002735 | 0.069054 | 0.06984 | 62.5534 | 62.2009 | -62.2375 | 62.2787 | -62.2787 | -62.4344 | 0.036621 | 0.050354 | 62.2696 | -62.4664 | 0.10071 | -0.13733 | 124.8917 | 124.617 | -124.617 | -0.12817 | -0.068665 | 124.791 | 62.3749 | 62.3886 | 0.059509 | 124.5392 | 124.8917 | 124.6078 | -0.09613 | -0.12817 | 124.5392 | 124.8917 | -0.09613 | 0.059509 | 124.6078 | -124.5758 | -124.8047
132.7969 | 124.9741 | -62.3428 | 62.3383 | -0.0082398 | 0.059507 | 0.058618 | -0.0067697 | -0.0019825 | 0.064781 | 0.070908 | 62.5397 | 62.1094 | -62.233 | 62.2879 | -62.2513 | -62.3886 | -0.032043 | 0.054932 | 62.2604 | -62.3978 | 0.10986 | -0.22888 | 124.8825 | 124.6307 | -124.5895 | -0.054932 | -0.07782 | 124.7726 | 62.3108 | 62.3978 | 0.091552 | 124.4522 | 124.8825 | 124.6033 | -0.045777 | -0.054932 | 124.4522 | 124.8825 | -0.045777 | 0.091552 | 124.6033 | -124.5712 | -124.736
133.7812 | 124.9191 | -62.3428 | 62.384 | -0.0082398 | 0.066984 | 0.063104 | 0.0017753 | -0.0026233 | 0.067985 | 0.070053 | 62.558 | 62.1918 | -62.2696 | 62.2787 | -62.2833 | -62.4298 | 0.036621 | 0.059509 | 62.2604 | -62.4756 | 0.073242 | -0.19226 | 124.9008 | 124.6216 | -124.6674 | -0.13275 | -0.1236 | 124.8276 | 62.3795 | 62.4023 | 0.059509 | 124.5346 | 124.9008 | 124.6033 | -0.086976 | -0.13275 | 124.5346 | 124.9008 | -0.086976 | 0.059509 | 124.6033 | -124.6536 | -124.8596
134.7812 | 124.9191 | -62.352 | 62.3703 | -0.00061033 | 0.067624 | 0.062036 | 0.0013479 | -0.0028369 | 0.06649 | 0.070908 | 62.5488 | 62.1826 | -62.2421 | 62.2742 | -62.2787 | -62.439 | 0.054932 | 0.059509 | 62.2833 | -62.4481 | 0.10986 | -0.18768 | 124.9008 | 124.6262 | -124.649 | -0.09613 | -0.086975 | 124.791 | 62.4069 | 62.4115 | 0.073242 | 124.5346 | 124.9008 | 124.6353 | -0.086975 | -0.09613 | 124.5346 | 124.9008 | -0.086975 | 0.073242 | 124.6353 | -124.6124 | -124.8184
135.8125 | 124.8459 | -62.3749 | 62.3474 | -0.0082398 | 0.064847 | 0.061395 | 0.0019889 | -0.0021961 | 0.06649 | 0.06984 | 62.4756 | 62.1597 | -62.2787 | 62.1918 | -62.3749 | -62.5122 | 0.064087 | -0.07782 | 62.2513 | -62.4939 | 0.09613 | -0.18768 | 124.8505 | 124.5667 | -124.7223 | -0.11902 | -0.09613 | 124.7543 | 62.439 | 62.2971 | 0 | 124.5346 | 124.8505 | 124.6262 | -0.13733 | -0.11902 | 124.5346 | 124.8505 | -0.13733 | 0 | 124.6262 | -124.6262 | -124.8413
136.8281 | 124.8917 | -62.352 | 62.3337 | -0.00061033 | 0.066343 | 0.061609 | 6.6302e-05 | -0.0028369 | 0.067985 | 0.068772 | 62.4664 | 62.1735 | -62.2559 | 62.1918 | -62.3566 | -62.4847 | -0.013733 | -0.082397 | 62.2513 | -62.5031 | 0.096131 | -0.16022 | 124.8184 | 124.5438 | -124.6902 | -0.15106 | -0.082397 | 124.7223 | 62.3383 | 62.2696 | -0.004577 | 124.5255 | 124.8184 | 124.6033 | -0.13275 | -0.15106 | 124.5255 | 124.8184 | -0.13275 | -0.004577 | 124.6033 | -124.5895 | -124.8367
137.7812 | 124.9283 | -62.3199 | 62.3428 | -0.00061033 | 0.066556 | 0.06225 | 0.0028433 | -0.0019825 | 0.068199 | 0.067917 | 62.5488 | 62.1872 | -62.2421 | 62.265 | -62.2971 | -62.4298 | 0.041199 | 0.054932 | 62.2467 | -62.4756 | 0.07782 | -0.15564 | 124.8688 | 124.585 | -124.6399 | -0.15564 | -0.09613 | 124.791 | 62.3611 | 62.3749 | 0.022888 | 124.5071 | 124.8688 | 124.5667 | -0.10986 | -0.15564 | 124.5071 | 124.8688 | -0.10986 | 0.022888 | 124.5667 | -124.585 | -124.8184
138.7812 | 124.91 | -62.3657 | 62.3199 | -0.0082398 | 0.067624 | 0.065454 | 0.0028433 | -0.0026233 | 0.067985 | 0.067276 | 62.5488 | 62.178 | -62.2375 | 62.2513 | -62.2879 | -62.4573 | 0.036621 | 0.018311 | 62.2467 | -62.4573 | 0.12817 | -0.14191 | 124.9146 | 124.617 | -124.6078 | -0.091552 | -0.073242 | 124.7864 | 62.4023 | 62.384 | 0.07782 | 124.5438 | 124.9146 | 124.6124 | -0.091552 | -0.091552 | 124.5438 | 124.9146 | -0.091552 | 0.07782 | 124.6124 | -124.5575 | -124.7772
139.8125 | 125.0153 | -62.3245 | 62.3383 | -0.00061033 | 0.059293 | 0.062463 | -0.0042063 | -0.0036915 | 0.067985 | 0.06984 | 62.6083 | 62.1094 | -62.2101 | 62.3657 | -62.1735 | -62.3154 | -0.045776 | 0.16937 | 62.2559 | -62.3749 | 0.11444 | -0.22888 | 124.9329 | 124.6902 | -124.5117 | -0.050354 | -0.082398 | 124.8184 | 62.2787 | 62.4939 | 0.15106 | 124.4339 | 124.9329 | 124.5804 | 0.009155 | -0.050354 | 124.4339 | 124.9329 | 0.009155 | 0.15106 | 124.5804 | -124.5483 | -124.7131
140.8125 | 124.9924 | -62.3337 | 62.352 | -0.00061033 | 0.05972 | 0.0599 | -0.0016427 | -0.0036915 | 0.066917 | 0.06984 | 62.558 | 62.1048 | -62.2101 | 62.3062 | -62.2055 | -62.3245 | -0.054932 | 0.10986 | 62.2421 | -62.3795 | 0.1236 | -0.24719 | 124.8917 | 124.6399 | -124.5575 | -0.045777 | -0.10986 | 124.7681 | 62.2787 | 62.4435 | 0.12817 | 124.4385 | 124.8917 | 124.5758 | 0.009155 | -0.045777 | 124.4385 | 124.8917 | 0.009155 | 0.12817 | 124.5758 | -124.5621 | -124.7314
141.7812 | 124.8642 | -62.3611 | 62.3611 | -0.0082398 | 0.06677 | 0.062036 | 0.0036979 | -0.0049731 | 0.064995 | 0.068985 | 62.5076 | 62.2009 | -62.2375 | 62.2421 | -62.3154 | -62.4802 | 0.15106 | 0.032043 | 62.2925 | -62.4344 | 0.1236 | -0.16022 | 124.8688 | 124.6033 | -124.6765 | -0.073242 | -0.068665 | 124.7452 | 62.5122 | 62.3932 | 0.045776 | 124.5621 | 124.8688 | 124.6536 | -0.11902 | -0.073242 | 124.5621 | 124.8688 | -0.11902 | 0.045776 | 124.6536 | -124.5987 | -124.7955
142.7969 | 124.91 | -62.3474 | 62.3428 | -0.0082398 | 0.068052 | 0.06225 | 0.0041251 | -0.0021961 | 0.069267 | 0.069413 | 62.5671 | 62.178 | -62.2375 | 62.2696 | -62.3108 | -62.4481 | 0.041199 | 0.036621 | 62.2513 | -62.4664 | 0.10986 | -0.16479 | 124.9146 | 124.617 | -124.6536 | -0.11902 | -0.091552 | 124.8047 | 62.3886 | 62.384 | 0.036621 | 124.5255 | 124.9146 | 124.5987 | -0.10071 | -0.11902 | 124.5255 | 124.9146 | -0.10071 | 0.036621 | 124.5987 | -124.5804 | -124.8093
143.9062 | 124.8688 | -62.384 | 62.3199 | 0.0070192 | 0.064847 | 0.062036 | 0.0011343 | -0.0028369 | 0.067345 | 0.06984 | 62.4573 | 62.1689 | -62.2513 | 62.178 | -62.3703 | -62.4939 | 0.009155 | -0.082397 | 62.265 | -62.4939 | 0.13275 | -0.15106 | 124.8413 | 124.5621 | -124.6902 | -0.10986 | -0.054931 | 124.7086 | 62.3932 | 62.3016 | 0.013733 | 124.5529 | 124.8413 | 124.649 | -0.10986 | -0.10986 | 124.5529 | 124.8413 | -0.10986 | 0.013733 | 124.649 | -124.5712 | -124.8138
144.7969 | 124.8779 | -62.3932 | 62.3199 | -0.0082398 | 0.064847 | 0.062036 | 0.0022025 | -0.0004871 | 0.067985 | 0.067917 | 62.471 | 62.1872 | -62.2604 | 62.178 | -62.3749 | -62.4985 | 0.022888 | -0.09613 | 62.2604 | -62.4893 | 0.13275 | -0.13275 | 124.8642 | 124.5712 | -124.6948 | -0.096131 | -0.059509 | 124.7314 | 62.4161 | 62.2971 | 0.01831 | 124.5804 | 124.8642 | 124.6536 | -0.10529 | -0.096131 | 124.5804 | 124.8642 | -0.10529 | 0.01831 | 124.6536 | -124.5804 | -124.8093
145.7812 | 124.8642 | -62.352 | 62.3703 | -0.00061033 | 0.069333 | 0.063104 | 0.0032705 | -0.0011279 | 0.06649 | 0.068131 | 62.4756 | 62.1643 | -62.2833 | 62.178 | -62.3703 | -62.5259 | 0.064087 | -0.073242 | 62.2696 | -62.4847 | 0.068665 | -0.20599 | 124.8276 | 124.53 | -124.7406 | -0.13275 | -0.10071 | 124.7589 | 62.4161 | 62.2787 | -0.01831 | 124.5163 | 124.8276 | 124.6216 | -0.17395 | -0.13275 | 124.5163 | 124.8276 | -0.17395 | -0.01831 | 124.6216 | -124.6536 | -124.855
146.7812 | 124.9191 | -62.352 | 62.3611 | 0.0070192 | 0.067624 | 0.063104 | 0.0007071 | 0.0003675 | 0.066704 | 0.068985 | 62.5397 | 62.1964 | -62.2238 | 62.2742 | -62.265 | -62.4481 | 0.045776 | 0.041199 | 62.2879 | -62.4619 | 0.12817 | -0.16479 | 124.8917 | 124.6262 | -124.6262 | -0.10986 | -0.073242 | 124.7635 | 62.3978 | 62.3932 | 0.086975 | 124.5483 | 124.8917 | 124.6399 | -0.09613 | -0.10986 | 124.5483 | 124.8917 | -0.09613 | 0.086975 | 124.6399 | -124.585 | -124.823
147.7812 | 124.8962 | -62.3337 | 62.3245 | -0.00061033 | 0.067411 | 0.063532 | 0.0032705 | -0.0032641 | 0.069267 | 0.069626 | 62.5626 | 62.1826 | -62.2284 | 62.2467 | -62.2742 | -62.4298 | 0.032043 | 0.018311 | 62.2559 | -62.4664 | 0.10528 | -0.14191 | 124.8962 | 124.5804 | -124.5987 | -0.13275 | -0.068665 | 124.791 | 62.3657 | 62.352 | 0.059509 | 124.5163 | 124.8962 | 124.5895 | -0.096131 | -0.13275 | 124.5163 | 124.8962 | -0.096131 | 0.059509 | 124.5895 | -124.5529 | -124.791
148.7969 | 125.0061 | -62.3199 | 62.3383 | -0.00061033 | 0.057798 | 0.057336 | -0.0052743 | -0.0030505 | 0.067345 | 0.069626 | 62.5946 | 62.1002 | -62.1964 | 62.3611 | -62.178 | -62.3108 | -0.073242 | 0.16022 | 62.2513 | -62.3566 | 0.1236 | -0.23804 | 124.9145 | 124.6811 | -124.5163 | -0.036621 | -0.086975 | 124.791 | 62.2467 | 62.4802 | 0.14191 | 124.4202 | 124.9145 | 124.5712 | 0.009155 | -0.036621 | 124.4202 | 124.9145 | 0.009155 | 0.14191 | 124.5712 | -124.5346 | -124.6948
149.7812 | 124.9008 | -62.3611 | 62.3474 | -0.0082398 | 0.067624 | 0.057977 | 0.0043387 | -0.0034777 | 0.068626 | 0.069199 | 62.5397 | 62.1826 | -62.2147 | 62.2559 | -62.2833 | -62.439 | 0.064087 | 0.041199 | 62.2787 | -62.4573 | 0.14648 | -0.16479 | 124.9008 | 124.617 | -124.6307 | -0.09613 | -0.068664 | 124.7543 | 62.4252 | 62.4023 | 0.07782 | 124.5438 | 124.9008 | 124.6399 | -0.07782 | -0.09613 | 124.5438 | 124.9008 | -0.07782 | 0.07782 | 124.6399 | -124.5621 | -124.8047
150.7812 | 124.9237 | -62.3474 | 62.3337 | -0.0082398 | 0.064847 | 0.063532 | 0.0022025 | -0.0024097 | 0.067772 | 0.068772 | 62.4802 | 62.1506 | -62.2604 | 62.2101 | -62.3154 | -62.4481 | -0.064087 | -0.045776 | 62.2467 | -62.4664 | 0.086975 | -0.1831 | 124.8276 | 124.5575 | -124.649 | -0.11902 | -0.086975 | 124.7406 | 62.2833 | 62.3016 | 0.032043 | 124.498 | 124.8276 | 124.5941 | -0.10071 | -0.11902 | 124.498 | 124.8276 | -0.10071 | 0.032043 | 124.5941 | -124.5941 | -124.8001
151.7812 | 124.942 | -62.3566 | 62.3383 | -0.00061033 | 0.067411 | 0.066309 | 0.0024161 | -0.0021961 | 0.067985 | 0.070267 | 62.5442 | 62.1597 | -62.2513 | 62.2833 | -62.2742 | -62.4435 | 0.032043 | 0.050354 | 62.2513 | -62.4527 | 0.10528 | -0.17853 | 124.9008 | 124.6399 | -124.6124 | -0.096131 | -0.086975 | 124.7955 | 62.3886 | 62.4069 | 0.082397 | 124.5163 | 124.9008 | 124.6078 | -0.086975 | -0.096131 | 124.5163 | 124.9008 | -0.086975 | 0.082397 | 124.6078 | -124.5895 | -124.791
152.7969 | 124.855 | -62.3611 | 62.3428 | -0.0082398 | 0.065915 | 0.060754 | -0.0001473 | -0.0041187 | 0.067558 | 0.06749 | 62.4893 | 62.1826 | -62.2421 | 62.2238 | -62.3108 | -62.4481 | 0.17853 | 0.018311 | 62.3291 | -62.4573 | 0.11902 | -0.16022 | 124.8505 | 124.585 | -124.6536 | -0.09613 | -0.013732 | 124.7314 | 62.5397 | 62.3795 | 0.050354 | 124.5438 | 124.8505 | 124.6902 | -0.086975 | -0.09613 | 124.5438 | 124.8505 | -0.086975 | 0.050354 | 124.6902 | -124.585 | -124.8001
153.7812 | 124.9832 | -62.3428 | 62.3016 | -0.00061033 | 0.061857 | 0.05755 | 0.0004935 | -0.0049731 | 0.067985 | 0.069626 | 62.5488 | 62.1231 | -62.2375 | 62.265 | -62.2559 | -62.3795 | -0.15564 | 0.022888 | 62.2375 | -62.4481 | 0.10529 | -0.17853 | 124.8917 | 124.6078 | -124.5575 | -0.10529 | -0.064087 | 124.7864 | 62.1872 | 62.3657 | 0.086975 | 124.4659 | 124.8917 | 124.5804 | -0.036622 | -0.10529 | 124.4659 | 124.8917 | -0.036622 | 0.086975 | 124.5804 | -124.5392 | -124.7498
154.7812 | 124.8871 | -62.3428 | 62.3108 | -0.00061033 | 0.069974 | 0.063959 | 0.0056205 | -0.0034777 | 0.06884 | 0.068131 | 62.5351 | 62.1597 | -62.2604 | 62.2421 | -62.3154 | -62.4985 | 0.045776 | 0 | 62.2559 | -62.4756 | 0.082397 | -0.15106 | 124.8779 | 124.585 | -124.6262 | -0.13275 | -0.054932 | 124.7955 | 62.3886 | 62.3428 | 0.027465 | 124.5026 | 124.8779 | 124.5987 | -0.15564 | -0.13275 | 124.5026 | 124.8779 | -0.15564 | 0.027465 | 124.5987 | -124.5712 | -124.7864
155.7812 | 124.8779 | -62.3383 | 62.3291 | -0.00061033 | 0.06912 | 0.0599 | 0.0054069 | -0.0026233 | 0.067558 | 0.069626 | 62.5397 | 62.1552 | -62.2467 | 62.2467 | -62.3016 | -62.4619 | 0.027466 | -0.004578 | 62.2742 | -62.4664 | 0.091553 | -0.17395 | 124.8779 | 124.585 | -124.6307 | -0.12817 | -0.054932 | 124.7864 | 62.3657 | 62.3337 | 0.036621 | 124.4934 | 124.8779 | 124.6124 | -0.1236 | -0.12817 | 124.4934 | 124.8779 | -0.1236 | 0.036621 | 124.6124 | -124.5758 | -124.7955
156.7812 | 124.8413 | -62.3795 | 62.352 | -0.015869 | 0.065915 | 0.0599 | 0.0015615 | -0.0007007 | 0.067345 | 0.068985 | 62.4756 | 62.1643 | -62.2696 | 62.1735 | -62.3703 | -62.4985 | 0.054932 | -0.068665 | 62.2696 | -62.4664 | 0.10986 | -0.18768 | 124.855 | 124.5529 | -124.7223 | -0.086975 | -0.082398 | 124.7452 | 62.4344 | 62.3108 | 0.009156 | 124.5438 | 124.855 | 124.649 | -0.11902 | -0.086975 | 124.5438 | 124.855 | -0.11902 | 0.009156 | 124.649 | -124.6216 | -124.8184
157.7812 | 124.9146 | -62.3291 | 62.352 | -0.0082398 | 0.065702 | 0.063959 | 0.0030569 | -0.0021961 | 0.06649 | 0.069626 | 62.5488 | 62.178 | -62.2559 | 62.2696 | -62.2833 | -62.439 | 0.041199 | 0.054932 | 62.2742 | -62.4435 | 0.073243 | -0.17395 | 124.8779 | 124.5987 | -124.6353 | -0.11444 | -0.07782 | 124.8047 | 62.3703 | 62.384 | 0.045777 | 124.5071 | 124.8779 | 124.6033 | -0.10986 | -0.11444 | 124.5071 | 124.8779 | -0.10986 | 0.045777 | 124.6033 | -124.6078 | -124.7955
158.8125 | 124.9969 | -62.3383 | 62.2971 | -0.00061033 | 0.061216 | 0.063745 | -0.0018563 | -0.0032641 | 0.067345 | 0.069626 | 62.558 | 62.0819 | -62.2467 | 62.2833 | -62.2467 | -62.3749 | -0.16937 | 0.022888 | 62.2147 | -62.4115 | 0.091553 | -0.21515 | 124.8962 | 124.6216 | -124.5438 | -0.073242 | -0.082397 | 124.8047 | 62.1689 | 62.3611 | 0.091553 | 124.4202 | 124.8962 | 124.5529 | -0.036621 | -0.073242 | 124.4202 | 124.8962 | -0.036621 | 0.091553 | 124.5529 | -124.5438 | -124.7086
159.7812 | 124.855 | -62.3611 | 62.3428 | -0.023499 | 0.069547 | 0.060968 | 0.0028433 | -0.0024097 | 0.069481 | 0.068558 | 62.471 | 62.1689 | -62.2696 | 62.1735 | -62.3611 | -62.5076 | 0.054932 | -0.082397 | 62.2559 | -62.471 | 0.091553 | -0.17395 | 124.8322 | 124.5346 | -124.704 | -0.10986 | -0.086975 | 124.7406 | 62.4161 | 62.2787 | 0 | 124.53 | 124.8322 | 124.617 | -0.14648 | -0.10986 | 124.53 | 124.8322 | -0.14648 | 0 | 124.617 | -124.6124 | -124.8138
160.7812 | 124.855 | -62.3611 | 62.3199 | -0.0082398 | 0.067197 | 0.062891 | 6.6302e-05 | -0.0004871 | 0.068626 | 0.068558 | 62.4481 | 62.178 | -62.2879 | 62.1552 | -62.3703 | -62.5122 | 0.022888 | -0.091553 | 62.265 | -62.5031 | 0.073242 | -0.14191 | 124.8093 | 124.5163 | -124.6902 | -0.14191 | -0.054931 | 124.736 | 62.384 | 62.2696 | -0.009155 | 124.5392 | 124.8093 | 124.6262 | -0.15106 | -0.14191 | 124.5392 | 124.8093 | -0.15106 | -0.009155 | 124.6262 | -124.6078 | -124.823
161.7812 | 124.9146 | -62.3199 | 62.3428 | -0.00061033 | 0.068693 | 0.057764 | 0.0032705 | -0.0028369 | 0.066917 | 0.069626 | 62.5351 | 62.1826 | -62.2513 | 62.265 | -62.2879 | -62.4344 | 0.045776 | 0.041199 | 62.2513 | -62.4573 | 0.068664 | -0.16022 | 124.855 | 124.585 | -124.6307 | -0.13733 | -0.091552 | 124.7864 | 62.3657 | 62.3611 | 0.032043 | 124.5026 | 124.855 | 124.5712 | -0.11444 | -0.13733 | 124.5026 | 124.855 | -0.11444 | 0.032043 | 124.5712 | -124.5941 | -124.8001
162.7812 | 124.8871 | -62.3749 | 62.3062 | -0.00061033 | 0.065061 | 0.066522 | 0.0004935 | -0.0028369 | 0.068413 | 0.070694 | 62.4573 | 62.1643 | -62.2742 | 62.1689 | -62.3566 | -62.4756 | -0.013733 | -0.082397 | 62.2375 | -62.4527 | 0.10071 | -0.14191 | 124.8322 | 124.5438 | -124.6628 | -0.07782 | -0.068664 | 124.7314 | 62.3611 | 62.2925 | 0.018311 | 124.5392 | 124.8322 | 124.6124 | -0.10071 | -0.07782 | 124.5392 | 124.8322 | -0.10071 | 0.018311 | 124.6124 | -124.5804 | -124.7589
163.7812 | 124.9695 | -62.3199 | 62.2971 | -0.015869 | 0.062284 | 0.060754 | -0.0005747 | -0.0017687 | 0.068199 | 0.072403 | 62.5168 | 62.1323 | -62.2421 | 62.2559 | -62.2742 | -62.3932 | -0.12817 | 0.009155 | 62.2055 | -62.4252 | 0.07782 | -0.16479 | 124.8367 | 124.5758 | -124.5712 | -0.10529 | -0.091553 | 124.7589 | 62.1918 | 62.3291 | 0.045776 | 124.4522 | 124.8367 | 124.5255 | -0.073242 | -0.10529 | 124.4522 | 124.8367 | -0.073242 | 0.045776 | 124.5255 | -124.5392 | -124.7223
164.7969 | 124.8779 | -62.3428 | 62.3154 | -0.0082398 | 0.066129 | 0.062891 | 0.0030569 | -0.0013415 | 0.067131 | 0.068344 | 62.5351 | 62.1735 | -62.265 | 62.2284 | -62.3199 | -62.4756 | 0.036621 | -0.027466 | 62.2604 | -62.4802 | 0.077819 | -0.14191 | 124.8779 | 124.5712 | -124.6353 | -0.13733 | -0.054932 | 124.8001 | 62.3795 | 62.3154 | 0.022888 | 124.5163 | 124.8779 | 124.6033 | -0.13275 | -0.13733 | 124.5163 | 124.8779 | -0.13275 | 0.022888 | 124.6033 | -124.5804 | -124.7955
165.7812 | 124.8596 | -62.3337 | 62.3383 | -0.0082398 | 0.067624 | 0.059259 | 0.0028433 | -0.0015551 | 0.06649 | 0.070267 | 62.4847 | 62.1643 | -62.2513 | 62.1872 | -62.352 | -62.5168 | 0.054932 | -0.059509 | 62.2559 | -62.4802 | 0.082397 | -0.17395 | 124.8184 | 124.5209 | -124.6902 | -0.14649 | -0.082398 | 124.736 | 62.3886 | 62.2742 | -0.018311 | 124.498 | 124.8184 | 124.5895 | -0.18311 | -0.14649 | 124.498 | 124.8184 | -0.18311 | -0.018311 | 124.5895 | -124.5895 | -124.8184
166.7812 | 124.9969 | -62.3108 | 62.3016 | -0.00061033 | 0.062497 | 0.06225 | -0.0022837 | -0.0019825 | 0.066277 | 0.070481 | 62.5671 | 62.0773 | -62.2696 | 62.2971 | -62.2421 | -62.3611 | -0.16937 | 0.032043 | 62.2192 | -62.4115 | 0.041199 | -0.2243 | 124.8779 | 124.6078 | -124.5438 | -0.10071 | -0.082398 | 124.8367 | 62.1414 | 62.3428 | 0.068665 | 124.3881 | 124.8779 | 124.53 | -0.050354 | -0.10071 | 124.3881 | 124.8779 | -0.050354 | 0.068665 | 124.53 | -124.5712 | -124.7131
167.7812 | 124.8642 | -62.3657 | 62.3245 | -0.0082398 | 0.067411 | 0.065668 | 0.0058341 | -0.0026233 | 0.067131 | 0.06984 | 62.4847 | 62.1826 | -62.2787 | 62.1826 | -62.3474 | -62.4985 | 0.059509 | -0.064087 | 62.2467 | -62.4847 | 0.086975 | -0.14191 | 124.8505 | 124.5483 | -124.6719 | -0.11902 | -0.07782 | 124.7635 | 62.4252 | 62.3016 | 0.018311 | 124.5483 | 124.8505 | 124.6124 | -0.13275 | -0.11902 | 124.5483 | 124.8505 | -0.13275 | 0.018311 | 124.6124 | -124.6033 | -124.8093
168.7812 | 124.9695 | -62.2787 | 62.3474 | -0.0082398 | 0.05908 | 0.058405 | -0.0037789 | -0.0049731 | 0.067772 | 0.070908 | 62.5305 | 62.1002 | -62.2375 | 62.2742 | -62.2375 | -62.3657 | -0.032043 | 0.059509 | 62.2513 | -62.3703 | 0.041199 | -0.24719 | 124.8093 | 124.5529 | -124.585 | -0.091552 | -0.09613 | 124.7681 | 62.2467 | 62.3383 | 0.041199 | 124.379 | 124.8093 | 124.53 | -0.086975 | -0.091552 | 124.379 | 124.8093 | -0.086975 | 0.041199 | 124.53 | -124.585 | -124.7177
169.7812 | 124.8596 | -62.3566 | 62.3383 | 0.0070192 | 0.066984 | 0.061609 | 0.0022025 | -0.0026233 | 0.068199 | 0.067917 | 62.4893 | 62.1597 | -62.2742 | 62.1826 | -62.3749 | -62.5168 | 0.054932 | -0.054932 | 62.2559 | -62.4756 | 0.082397 | -0.17853 | 124.8459 | 124.5392 | -124.7131 | -0.11902 | -0.082398 | 124.7635 | 62.4115 | 62.3016 | -0.018311 | 124.5163 | 124.8459 | 124.6124 | -0.16022 | -0.11902 | 124.5163 | 124.8459 | -0.16022 | -0.018311 | 124.6124 | -124.6124 | -124.8138
170.7969 | 124.9649 | -62.3291 | 62.2879 | -0.0082398 | 0.065702 | 0.057123 | -0.0001473 | -0.0021961 | 0.067345 | 0.06984 | 62.5259 | 62.1048 | -62.2284 | 62.265 | -62.2787 | -62.3795 | -0.1236 | 0.004578 | 62.2284 | -62.4252 | 0.10071 | -0.18311 | 124.855 | 124.5941 | -124.5667 | -0.09613 | -0.059509 | 124.7543 | 62.2055 | 62.3337 | 0.050354 | 124.4339 | 124.855 | 124.5575 | -0.050354 | -0.09613 | 124.4339 | 124.855 | -0.050354 | 0.050354 | 124.5575 | -124.5163 | -124.7131
171.7969 | 124.8505 | -62.3703 | 62.3291 | -0.015869 | 0.066984 | 0.062463 | 0.0039115 | -0.0026233 | 0.068413 | 0.067917 | 62.471 | 62.1872 | -62.2742 | 62.1826 | -62.3611 | -62.5076 | 0.054932 | -0.07782 | 62.265 | -62.4802 | 0.09613 | -0.14191 | 124.8413 | 124.5529 | -124.6902 | -0.10986 | -0.064087 | 124.7452 | 62.4252 | 62.2925 | 0.009155 | 124.5575 | 124.8413 | 124.6353 | -0.13733 | -0.10986 | 124.5575 | 124.8413 | -0.13733 | 0.009155 | 124.6353 | -124.6033 | -124.8093
172.7812 | 124.9786 | -62.3016 | 62.3016 | -0.0082398 | 0.060148 | 0.059686 | 6.6302e-05 | -0.0026233 | 0.064781 | 0.070481 | 62.5626 | 62.0544 | -62.233 | 62.2971 | -62.233 | -62.3566 | -0.16022 | 0.050354 | 62.2101 | -62.4161 | 0.068665 | -0.24719 | 124.8642 | 124.5987 | -124.5346 | -0.11444 | -0.091553 | 124.7955 | 62.1414 | 62.352 | 0.068665 | 124.3561 | 124.8642 | 124.5117 | -0.054931 | -0.11444 | 124.3561 | 124.8642 | -0.054931 | 0.068665 | 124.5117 | -124.5346 | -124.7177
173.7812 | 124.8367 | -62.3611 | 62.3383 | -0.015869 | 0.068693 | 0.063959 | 0.0060477 | -0.0024097 | 0.065849 | 0.070481 | 62.4802 | 62.1735 | -62.2513 | 62.1735 | -62.3749 | -62.5122 | 0.064087 | -0.091553 | 62.2559 | -62.4939 | 0.10986 | -0.16479 | 124.8413 | 124.5346 | -124.7131 | -0.13275 | -0.082398 | 124.7314 | 62.4252 | 62.2696 | -0.013733 | 124.5346 | 124.8413 | 124.617 | -0.15106 | -0.13275 | 124.5346 | 124.8413 | -0.15106 | -0.013733 | 124.617 | -124.5895 | -124.8322
174.7812 | 124.8459 | -62.3474 | 62.3566 | -0.0082398 | 0.067411 | 0.061609 | 0.0051931 | -0.0015551 | 0.067985 | 0.068985 | 62.4619 | 62.1872 | -62.2513 | 62.1826 | -62.3749 | -62.5122 | 0.082397 | -0.09613 | 62.2238 | -62.4939 | 0.09613 | -0.16937 | 124.8093 | 124.53 | -124.7314 | -0.14648 | -0.13275 | 124.7131 | 62.4298 | 62.2513 | -0.027466 | 124.5346 | 124.8093 | 124.5712 | -0.16479 | -0.14648 | 124.5346 | 124.8093 | -0.16479 | -0.027466 | 124.5712 | -124.6078 | -124.8505
175.7812 | 124.8367 | -62.3428 | 62.3474 | -0.0082398 | 0.066984 | 0.060541 | 0.0019889 | -0.0021961 | 0.067772 | 0.068985 | 62.4619 | 62.1826 | -62.2696 | 62.1826 | -62.3611 | -62.5031 | 0.07782 | -0.082397 | 62.2604 | -62.4802 | 0.073242 | -0.16479 | 124.8047 | 124.5255 | -124.7086 | -0.13733 | -0.086975 | 124.7314 | 62.4207 | 62.2604 | -0.018311 | 124.5255 | 124.8047 | 124.6033 | -0.16022 | -0.13733 | 124.5255 | 124.8047 | -0.16022 | -0.018311 | 124.6033 | -124.617 | -124.8276
176.7812 | 124.9649 | -62.3474 | 62.2833 | 0.0070192 | 0.065488 | 0.062036 | 0.0022025 | -0.0036915 | 0.067985 | 0.071335 | 62.5122 | 62.1185 | -62.2696 | 62.2559 | -62.2742 | -62.4069 | -0.11444 | -0.013733 | 62.2192 | -62.4023 | 0.07782 | -0.16479 | 124.8596 | 124.6033 | -124.5575 | -0.054932 | -0.064087 | 124.7818 | 62.233 | 62.3337 | 0.073242 | 124.4659 | 124.8596 | 124.5666 | -0.059509 | -0.054932 | 124.4659 | 124.8596 | -0.059509 | 0.073242 | 124.5666 | -124.5529 | -124.6857
177.7812 | 124.8688 | -62.3657 | 62.352 | -0.0082398 | 0.067411 | 0.063532 | 0.0034841 | -0.0002735 | 0.068626 | 0.068985 | 62.4985 | 62.1689 | -62.265 | 62.2147 | -62.3383 | -62.5031 | 0.054932 | -0.064087 | 62.2513 | -62.471 | 0.10071 | -0.18311 | 124.8642 | 124.5804 | -124.6902 | -0.10528 | -0.10071 | 124.7635 | 62.4207 | 62.3016 | 0.027466 | 124.5346 | 124.8642 | 124.617 | -0.13733 | -0.10528 | 124.5346 | 124.8642 | -0.13733 | 0.027466 | 124.617 | -124.617 | -124.823
178.7969 | 124.8917 | -62.3383 | 62.3474 | 0.0070192 | 0.06677 | 0.059473 | 0.0022025 | -0.0024097 | 0.06649 | 0.069413 | 62.5214 | 62.2009 | -62.2421 | 62.2604 | -62.265 | -62.4435 | 0.07782 | 0.036621 | 62.2879 | -62.4298 | 0.096131 | -0.14648 | 124.8596 | 124.5987 | -124.6124 | -0.091553 | -0.059509 | 124.7635 | 62.4161 | 62.3749 | 0.073242 | 124.5392 | 124.8596 | 124.6262 | -0.10529 | -0.091553 | 124.5392 | 124.8596 | -0.10529 | 0.073242 | 124.6262 | -124.5895 | -124.7772
179.7812 | 124.8459 | -62.3611 | 62.3337 | -0.0082398 | 0.066556 | 0.060327 | 6.6302e-05 | -0.0024097 | 0.06884 | 0.070481 | 62.4573 | 62.1826 | -62.265 | 62.1597 | -62.3795 | -62.5076 | 0.054932 | -0.11444 | 62.265 | -62.471 | 0.09613 | -0.15106 | 124.8184 | 124.5209 | -124.7131 | -0.10986 | -0.068664 | 124.7223 | 62.4161 | 62.2467 | -0.018311 | 124.5438 | 124.8184 | 124.6262 | -0.14648 | -0.10986 | 124.5438 | 124.8184 | -0.14648 | -0.018311 | 124.6262 | -124.5987 | -124.8047
180.7812 | 124.9557 | -62.3199 | 62.2879 | 0.0070192 | 0.067838 | 0.061609 | 6.6302e-05 | -0.0009143 | 0.06649 | 0.071122 | 62.5031 | 62.1323 | -62.2696 | 62.2604 | -62.2696 | -62.4023 | -0.091553 | -0.004578 | 62.2513 | -62.4527 | 0.050354 | -0.15564 | 124.823 | 124.5804 | -124.5575 | -0.13275 | -0.036621 | 124.7726 | 62.2284 | 62.3154 | 0.050354 | 124.4522 | 124.823 | 124.5712 | -0.082398 | -0.13275 | 124.4522 | 124.823 | -0.082398 | 0.050354 | 124.5712 | -124.5575 | -124.7406
181.7812 | 124.8505 | -62.3566 | 62.3245 | -0.00061033 | 0.066556 | 0.063318 | 0.0034841 | -0.0019825 | 0.069267 | 0.068344 | 62.4893 | 62.1643 | -62.2696 | 62.178 | -62.3337 | -62.4985 | 0.068665 | -0.068665 | 62.233 | -62.4802 | 0.086975 | -0.16022 | 124.8459 | 124.5346 | -124.6582 | -0.1236 | -0.091553 | 124.7589 | 62.4252 | 62.2879 | 0.022888 | 124.5209 | 124.8459 | 124.5895 | -0.14191 | -0.1236 | 124.5209 | 124.8459 | -0.14191 | 0.022888 | 124.5895 | -124.5941 | -124.8047
182.7812 | 124.8596 | -62.3383 | 62.3154 | -0.00061033 | 0.068052 | 0.063104 | 0.0026297 | -0.0026233 | 0.067131 | 0.070908 | 62.5076 | 62.1643 | -62.2421 | 62.2101 | -62.3199 | -62.4893 | 0.059509 | -0.036621 | 62.2192 | -62.4756 | 0.096131 | -0.15106 | 124.8459 | 124.5483 | -124.6353 | -0.13733 | -0.096131 | 124.7498 | 62.3978 | 62.3016 | 0.018311 | 124.5026 | 124.8459 | 124.5575 | -0.15106 | -0.13733 | 124.5026 | 124.8459 | -0.15106 | 0.018311 | 124.5575 | -124.5575 | -124.791
183.7812 | 124.8779 | -62.3337 | 62.3428 | 0.0070192 | 0.067197 | 0.064386 | 0.0004935 | -0.0021961 | 0.06649 | 0.068558 | 62.5305 | 62.1918 | -62.2192 | 62.2238 | -62.2925 | -62.4664 | 0.054932 | -0.013733 | 62.2833 | -62.4481 | 0.11444 | -0.15106 | 124.8642 | 124.5575 | -124.6353 | -0.11444 | -0.059509 | 124.7498 | 62.3886 | 62.3199 | 0.041199 | 124.5255 | 124.8642 | 124.617 | -0.13275 | -0.11444 | 124.5255 | 124.8642 | -0.13275 | 0.041199 | 124.617 | -124.5621 | -124.791
184.7812 | 124.8459 | -62.3474 | 62.3245 | -0.023499 | 0.066556 | 0.062463 | 0.0019889 | -0.0034777 | 0.067345 | 0.068344 | 62.471 | 62.1506 | -62.2833 | 62.1872 | -62.352 | -62.5076 | 0.091553 | -0.082397 | 62.2559 | -62.4802 | 0.064087 | -0.17395 | 124.8184 | 124.5346 | -124.6765 | -0.13275 | -0.068665 | 124.7543 | 62.439 | 62.265 | -0.004578 | 124.498 | 124.8184 | 124.6033 | -0.16022 | -0.13275 | 124.498 | 124.8184 | -0.16022 | -0.004578 | 124.6033 | -124.6078 | -124.8047
185.7812 | 124.8322 | -62.3566 | 62.3199 | -0.023499 | 0.067411 | 0.065454 | 0.0022025 | -0.0017687 | 0.069908 | 0.069413 | 62.4435 | 62.178 | -62.2925 | 62.1552 | -62.3932 | -62.5442 | 0.086975 | -0.11444 | 62.2421 | -62.4756 | 0.064087 | -0.14191 | 124.8001 | 124.5117 | -124.7131 | -0.11902 | -0.07782 | 124.736 | 62.4435 | 62.2421 | -0.036621 | 124.5346 | 124.8001 | 124.5987 | -0.18768 | -0.11902 | 124.5346 | 124.8001 | -0.18768 | -0.036621 | 124.5987 | -124.6124 | -124.7955
186.7969 | 124.8917 | -62.3245 | 62.3383 | -0.015869 | 0.066556 | 0.058618 | 0.0039115 | -0.0024097 | 0.067345 | 0.069199 | 62.5305 | 62.1872 | -62.2238 | 62.2559 | -62.2696 | -62.4344 | 0.091553 | 0.022888 | 62.2696 | -62.4435 | 0.10071 | -0.15106 | 124.855 | 124.5804 | -124.6078 | -0.11902 | -0.068665 | 124.7543 | 62.4161 | 62.3474 | 0.054932 | 124.5117 | 124.855 | 124.5941 | -0.10986 | -0.11902 | 124.5117 | 124.855 | -0.10986 | 0.054932 | 124.5941 | -124.5621 | -124.7818
187.7812 | 124.8688 | -62.352 | 62.3291 | -0.0082398 | 0.067838 | 0.063532 | 0.0017753 | -0.0004871 | 0.066704 | 0.070694 | 62.5305 | 62.1643 | -62.2375 | 62.233 | -62.3062 | -62.4619 | 0.073242 | -0.036621 | 62.2833 | -62.4527 | 0.11444 | -0.16479 | 124.8825 | 124.585 | -124.6353 | -0.10071 | -0.045777 | 124.7681 | 62.4252 | 62.3154 | 0.045777 | 124.5163 | 124.8825 | 124.6353 | -0.10986 | -0.10071 | 124.5163 | 124.8825 | -0.10986 | 0.045777 | 124.6353 | -124.5667 | -124.7818
188.7812 | 124.9557 | -62.3199 | 62.3108 | -0.00061033 | 0.066984 | 0.062463 | -0.0027109 | -0.0007007 | 0.06884 | 0.06984 | 62.5031 | 62.1597 | -62.2375 | 62.2513 | -62.2696 | -62.4023 | -0.068665 | -0.022888 | 62.233 | -62.4298 | 0.082397 | -0.15106 | 124.823 | 124.5712 | -124.5804 | -0.10986 | -0.07782 | 124.7406 | 62.2513 | 62.2971 | 0.050354 | 124.4797 | 124.823 | 124.5529 | -0.082398 | -0.10986 | 124.4797 | 124.823 | -0.082398 | 0.050354 | 124.5529 | -124.5483 | -124.7406
189.7812 | 124.8962 | -62.3291 | 62.3337 | -0.0082398 | 0.06677 | 0.063104 | 0.0011343 | -0.0041187 | 0.068413 | 0.068558 | 62.5351 | 62.2055 | -62.2467 | 62.2559 | -62.2742 | -62.4435 | 0.09613 | 0.009155 | 62.2604 | -62.471 | 0.082398 | -0.12817 | 124.8642 | 124.585 | -124.6078 | -0.14191 | -0.073242 | 124.7818 | 62.4252 | 62.3383 | 0.054932 | 124.5346 | 124.8642 | 124.5895 | -0.11444 | -0.14191 | 124.5346 | 124.8642 | -0.11444 | 0.054932 | 124.5895 | -124.5804 | -124.8047
190.7812 | 124.9054 | -62.3291 | 62.3428 | -0.015869 | 0.065702 | 0.0599 | 0.0034841 | -0.0011279 | 0.067131 | 0.068985 | 62.5214 | 62.1918 | -62.2421 | 62.2604 | -62.2696 | -62.4161 | 0.09613 | 0.032043 | 62.2787 | -62.4664 | 0.086976 | -0.15106 | 124.8505 | 124.5895 | -124.6124 | -0.13733 | -0.064086 | 124.7635 | 62.4252 | 62.3611 | 0.05951 | 124.5209 | 124.8505 | 124.6078 | -0.086975 | -0.13733 | 124.5209 | 124.8505 | -0.086975 | 0.05951 | 124.6078 | -124.585 | -124.8093
191.7812 | 124.8688 | -62.3428 | 62.3383 | -0.0082398 | 0.068265 | 0.06225 | 0.0009207 | -0.0013415 | 0.069054 | 0.070267 | 62.5168 | 62.1964 | -62.2421 | 62.2238 | -62.2925 | -62.4573 | 0.09613 | -0.032043 | 62.2787 | -62.4756 | 0.10071 | -0.14191 | 124.8596 | 124.5667 | -124.6307 | -0.13275 | -0.059509 | 124.7589 | 62.439 | 62.3108 | 0.050354 | 124.5392 | 124.8596 | 124.6216 | -0.11444 | -0.13275 | 124.5392 | 124.8596 | -0.11444 | 0.050354 | 124.6216 | -124.5804 | -124.8138
192.7812 | 124.8779 | -62.3245 | 62.3291 | -0.0082398 | 0.068479 | 0.059259 | 0.0024161 | -5.99e-05 | 0.067131 | 0.068985 | 62.5397 | 62.1735 | -62.2284 | 62.2375 | -62.2833 | -62.439 | 0.10071 | -0.018311 | 62.2925 | -62.4344 | 0.09613 | -0.15564 | 124.8642 | 124.5621 | -124.6124 | -0.10986 | -0.036622 | 124.7681 | 62.4252 | 62.3062 | 0.041199 | 124.498 | 124.8642 | 124.617 | -0.11444 | -0.10986 | 124.498 | 124.8642 | -0.11444 | 0.041199 | 124.617 | -124.5575 | -124.7635
193.7812 | 124.8413 | -62.3337 | 62.3474 | -0.00061033 | 0.068479 | 0.065454 | 0.0041251 | -0.0017687 | 0.067131 | 0.070267 | 62.4802 | 62.1735 | -62.2742 | 62.1826 | -62.352 | -62.4985 | 0.10071 | -0.082397 | 62.2467 | -62.4802 | 0.059509 | -0.17395 | 124.8138 | 124.5163 | -124.6994 | -0.14649 | -0.10071 | 124.7543 | 62.4344 | 62.2513 | -0.018311 | 124.5071 | 124.8138 | 124.5804 | -0.1648 | -0.14649 | 124.5071 | 124.8138 | -0.1648 | -0.018311 | 124.5804 | -124.6216 | -124.8276
194.7812 | 124.8962 | -62.3108 | 62.3154 | 0.0070192 | 0.068052 | 0.063745 | 0.0032705 | -0.0032641 | 0.067345 | 0.068985 | 62.5397 | 62.1689 | -62.2513 | 62.265 | -62.2787 | -62.4161 | 0.10071 | 0 | 62.2742 | -62.4435 | 0.059509 | -0.14648 | 124.8505 | 124.5758 | -124.5941 | -0.13275 | -0.041199 | 124.791 | 62.4115 | 62.3108 | 0.032043 | 124.4797 | 124.8505 | 124.585 | -0.10529 | -0.13275 | 124.4797 | 124.8505 | -0.10529 | 0.032043 | 124.585 | -124.5667 | -124.7589
195.7812 | 124.9832 | -62.265 | 62.352 | -0.0082398 | 0.061643 | 0.059045 | -0.0052743 | -0.0056141 | 0.066277 | 0.067704 | 62.5809 | 62.1323 | -62.1872 | 62.3337 | -62.1826 | -62.3245 | 0.022888 | 0.073242 | 62.265 | -62.3611 | 0.07782 | -0.21973 | 124.8459 | 124.5987 | -124.5346 | -0.09613 | -0.086975 | 124.7681 | 62.2879 | 62.3383 | 0.082398 | 124.3973 | 124.8459 | 124.53 | -0.059509 | -0.09613 | 124.3973 | 124.8459 | -0.059509 | 0.082398 | 124.53 | -124.5392 | -124.7131
196.7812 | 124.9054 | -62.3383 | 62.3474 | -0.015869 | 0.067838 | 0.061395 | 0.0028433 | -0.0019825 | 0.067558 | 0.068131 | 62.5488 | 62.2055 | -62.2192 | 62.2513 | -62.2787 | -62.4161 | 0.1236 | 0.009155 | 62.2787 | -62.471 | 0.11902 | -0.14191 | 124.8871 | 124.5895 | -124.6262 | -0.13275 | -0.068664 | 124.7681 | 62.4619 | 62.3474 | 0.059509 | 124.5438 | 124.8871 | 124.617 | -0.07782 | -0.13275 | 124.5438 | 124.8871 | -0.07782 | 0.059509 | 124.617 | -124.5666 | -124.8184
197.7812 | 124.8871 | -62.3016 | 62.3474 | -0.0082398 | 0.068479 | 0.060327 | 0.0017753 | -0.0007007 | 0.068626 | 0.070053 | 62.5259 | 62.1964 | -62.233 | 62.2559 | -62.2604 | -62.4252 | 0.13275 | -0.009155 | 62.2787 | -62.4435 | 0.068665 | -0.15106 | 124.8276 | 124.5575 | -124.6078 | -0.14191 | -0.068664 | 124.7589 | 62.4344 | 62.2925 | 0.041199 | 124.498 | 124.8276 | 124.5804 | -0.1236 | -0.14191 | 124.498 | 124.8276 | -0.1236 | 0.041199 | 124.5804 | -124.5804 | -124.791
198.7812 | 124.8779 | -62.3245 | 62.3474 | -0.00061033 | 0.065488 | 0.059686 | 0.0039115 | -0.0021961 | 0.067772 | 0.069413 | 62.5442 | 62.2055 | -62.2421 | 62.2513 | -62.2787 | -62.4207 | 0.11444 | -0.013733 | 62.3016 | -62.4435 | 0.082398 | -0.14191 | 124.8688 | 124.5758 | -124.6262 | -0.11902 | -0.045776 | 124.7864 | 62.439 | 62.3108 | 0.045776 | 124.53 | 124.8688 | 124.6262 | -0.09613 | -0.11902 | 124.53 | 124.8688 | -0.09613 | 0.045776 | 124.6262 | -124.5895 | -124.791
199.8125 | 124.8917 | -62.3474 | 62.3611 | -0.015869 | 0.062711 | 0.059045 | -0.0005747 | -0.0017687 | 0.066704 | 0.069413 | 62.4939 | 62.178 | -62.265 | 62.2375 | -62.2787 | -62.4344 | 0.17853 | -0.027466 | 62.3062 | -62.4115 | 0.082397 | -0.1831 | 124.8413 | 124.585 | -124.6399 | -0.064087 | -0.054932 | 124.7589 | 62.5259 | 62.3199 | 0.068664 | 124.5255 | 124.8413 | 124.6536 | -0.086975 | -0.064087 | 124.5255 | 124.8413 | -0.086975 | 0.068664 | 124.6536 | -124.6262 | -124.7726
200.7812 | 124.8734 | -62.3383 | 62.3566 | 0.0070192 | 0.069333 | 0.058191 | 0.0022025 | -0.0032641 | 0.064995 | 0.068772 | 62.5397 | 62.1918 | -62.2238 | 62.2101 | -62.2971 | -62.4573 | 0.12817 | -0.068665 | 62.2742 | -62.4481 | 0.11444 | -0.16479 | 124.8779 | 124.5483 | -124.6536 | -0.10986 | -0.082397 | 124.7635 | 62.4664 | 62.2696 | 0.041199 | 124.53 | 124.8779 | 124.6124 | -0.11902 | -0.10986 | 124.53 | 124.8779 | -0.11902 | 0.041199 | 124.6124 | -124.5804 | -124.8047
201.7812 | 124.8322 | -62.3611 | 62.352 | -0.0082398 | 0.066556 | 0.0599 | 0.0015615 | -0.0034777 | 0.065636 | 0.068772 | 62.439 | 62.1826 | -62.2879 | 62.1552 | -62.3657 | -62.5122 | 0.13733 | -0.17853 | 62.265 | -62.4619 | 0.073242 | -0.16937 | 124.8001 | 124.5163 | -124.7177 | -0.10071 | -0.086975 | 124.7269 | 62.4985 | 62.1826 | -0.004578 | 124.5438 | 124.8001 | 124.6262 | -0.15106 | -0.10071 | 124.5438 | 124.8001 | -0.15106 | -0.004578 | 124.6262 | -124.6399 | -124.8138
202.7812 | 124.8917 | -62.3154 | 62.3383 | -0.00061033 | 0.066129 | 0.061182 | -0.0007883 | -0.0028369 | 0.067131 | 0.06984 | 62.5305 | 62.2055 | -62.2192 | 62.2696 | -62.2604 | -62.4344 | 0.16937 | -0.032043 | 62.3016 | -62.4527 | 0.096131 | -0.13275 | 124.8459 | 124.585 | -124.5987 | -0.13733 | -0.036621 | 124.7498 | 62.4847 | 62.2833 | 0.054932 | 124.5209 | 124.8459 | 124.617 | -0.11902 | -0.13733 | 124.5209 | 124.8459 | -0.11902 | 0.054932 | 124.617 | -124.5575 | -124.791
203.7969 | 124.9786 | -62.3154 | 62.2742 | -0.00061033 | 0.062497 | 0.060327 | -0.0037789 | -0.0011279 | 0.067345 | 0.068772 | 62.5442 | 62.0865 | -62.2284 | 62.2971 | -62.2284 | -62.3566 | -0.050354 | -0.045776 | 62.233 | -62.3932 | 0.086975 | -0.18768 | 124.8596 | 124.6124 | -124.5026 | -0.077819 | -0.041199 | 124.7726 | 62.265 | 62.2696 | 0.086975 | 124.4019 | 124.8596 | 124.5483 | -0.041198 | -0.077819 | 124.4019 | 124.8596 | -0.041198 | 0.086975 | 124.5483 | -124.5026 | -124.6674
204.7812 | 124.8871 | -62.3291 | 62.3383 | -0.015869 | 0.067197 | 0.063745 | 0.0026297 | -0.0034777 | 0.067772 | 0.067063 | 62.5351 | 62.1597 | -62.233 | 62.2604 | -62.265 | -62.4252 | 0.16937 | -0.041199 | 62.2604 | -62.4619 | 0.096131 | -0.17853 | 124.8642 | 124.5895 | -124.6033 | -0.13275 | -0.07782 | 124.7681 | 62.4985 | 62.2879 | 0.064087 | 124.4888 | 124.8642 | 124.5895 | -0.09613 | -0.13275 | 124.4888 | 124.8642 | -0.09613 | 0.064087 | 124.5895 | -124.5712 | -124.8001
205.7812 | 124.8276 | -62.3291 | 62.3199 | -0.0082398 | 0.063779 | 0.060541 | 0.0032705 | -0.0019825 | 0.068626 | 0.070267 | 62.4344 | 62.1918 | -62.2787 | 62.1506 | -62.352 | -62.5259 | 0.16479 | -0.20599 | 62.2467 | -62.4985 | 0.050354 | -0.12817 | 124.7635 | 124.4797 | -124.6719 | -0.16937 | -0.073242 | 124.7131 | 62.4939 | 62.1231 | -0.022888 | 124.5209 | 124.7635 | 124.5758 | -0.19684 | -0.16937 | 124.5209 | 124.7635 | -0.19684 | -0.022888 | 124.5758 | -124.5987 | -124.8184
206.7812 | 124.8734 | -62.3245 | 62.3383 | -0.015869 | 0.065702 | 0.062036 | 0.0039115 | -0.0021961 | 0.067558 | 0.070694 | 62.5259 | 62.2147 | -62.2513 | 62.2559 | -62.2513 | -62.4115 | 0.20599 | -0.054932 | 62.2833 | -62.4527 | 0.073242 | -0.1236 | 124.8505 | 124.5804 | -124.5895 | -0.12817 | -0.054932 | 124.7772 | 62.5305 | 62.2696 | 0.073242 | 124.5392 | 124.8505 | 124.6078 | -0.086975 | -0.12817 | 124.5392 | 124.8505 | -0.086975 | 0.073242 | 124.6078 | -124.5895 | -124.791
207.7969 | 124.9237 | -62.2971 | 62.3245 | -0.0082398 | 0.062497 | 0.056909 | -0.0027109 | -0.0036915 | 0.069054 | 0.070053 | 62.5168 | 62.1643 | -62.1964 | 62.2513 | -62.2467 | -62.384 | 0.091553 | -0.10071 | 62.2513 | -62.4115 | 0.10071 | -0.16022 | 124.8138 | 124.5483 | -124.5712 | -0.11444 | -0.073242 | 124.7131 | 62.3886 | 62.1964 | 0.050354 | 124.4614 | 124.8138 | 124.5483 | -0.086975 | -0.11444 | 124.4614 | 124.8138 | -0.086975 | 0.050354 | 124.5483 | -124.5209 | -124.736
208.7812 | 124.8734 | -62.3474 | 62.352 | -0.0082398 | 0.066343 | 0.060114 | 0.0019889 | -0.0039051 | 0.066917 | 0.06984 | 62.5076 | 62.1872 | -62.233 | 62.2421 | -62.2925 | -62.4481 | 0.23804 | -0.09613 | 62.2879 | -62.4481 | 0.11444 | -0.16479 | 124.855 | 124.5895 | -124.6445 | -0.10071 | -0.064087 | 124.7406 | 62.5854 | 62.2513 | 0.054932 | 124.5346 | 124.855 | 124.6353 | -0.10071 | -0.10071 | 124.5346 | 124.855 | -0.10071 | 0.054932 | 124.6353 | -124.585 | -124.8001
209.7812 | 124.8367 | -62.3428 | 62.3383 | -0.00061033 | 0.067624 | 0.063532 | 0.0019889 | -0.0034777 | 0.067345 | 0.069199 | 62.4573 | 62.1735 | -62.265 | 62.1414 | -62.3703 | -62.5259 | 0.20599 | -0.2243 | 62.2513 | -62.4893 | 0.077819 | -0.16479 | 124.8001 | 124.4843 | -124.7086 | -0.14648 | -0.086975 | 124.7223 | 62.5488 | 62.1185 | -0.027466 | 124.5163 | 124.8001 | 124.5941 | -0.18311 | -0.14648 | 124.5163 | 124.8001 | -0.18311 | -0.027466 | 124.5941 | -124.6033 | -124.8276
210.7812 | 124.8413 | -62.3291 | 62.384 | -0.00061033 | 0.064206 | 0.060327 | -0.0007883 | -0.0032641 | 0.070335 | 0.069199 | 62.4802 | 62.1918 | -62.2192 | 62.2192 | -62.2742 | -62.4527 | 0.36621 | -0.10071 | 62.3291 | -62.4207 | 0.10986 | -0.19226 | 124.8093 | 124.5483 | -124.6582 | -0.091552 | -0.054931 | 124.6994 | 62.6953 | 62.2284 | 0.054932 | 124.5209 | 124.8093 | 124.6582 | -0.1236 | -0.091552 | 124.5209 | 124.8093 | -0.1236 | 0.054932 | 124.6582 | -124.6033 | -124.8047
211.7812 | 124.8322 | -62.3428 | 62.3337 | -0.00061033 | 0.065488 | 0.062463 | 0.0026297 | -0.0034777 | 0.068413 | 0.068131 | 62.439 | 62.1552 | -62.2925 | 62.1643 | -62.3657 | -62.5122 | 0.2243 | -0.24719 | 62.2559 | -62.471 | 0.050354 | -0.17853 | 124.7818 | 124.5071 | -124.6994 | -0.12817 | -0.07782 | 124.7314 | 62.5671 | 62.0956 | -0.022889 | 124.498 | 124.7818 | 124.5987 | -0.16937 | -0.12817 | 124.498 | 124.7818 | -0.16937 | -0.022889 | 124.5987 | -124.6262 | -124.8047
212.7812 | 124.8413 | -62.3474 | 62.3291 | -0.0082398 | 0.063352 | 0.060754 | 0.0028433 | -0.0024097 | 0.069267 | 0.070694 | 62.4298 | 62.1918 | -62.265 | 62.1506 | -62.3749 | -62.5397 | 0.24719 | -0.24261 | 62.2559 | -62.471 | 0.082397 | -0.13733 | 124.7772 | 124.498 | -124.704 | -0.1236 | -0.073243 | 124.6948 | 62.5946 | 62.1048 | -0.027466 | 124.5392 | 124.7772 | 124.6033 | -0.19226 | -0.1236 | 124.5392 | 124.7772 | -0.19226 | -0.027466 | 124.6033 | -124.5941 | -124.8001
213.7812 | 124.8962 | -62.3337 | 62.3337 | -0.015869 | 0.068052 | 0.058191 | 6.6302e-05 | -0.0024097 | 0.066063 | 0.070053 | 62.5259 | 62.1735 | -62.2467 | 62.2513 | -62.2604 | -62.4161 | 0.27466 | -0.10986 | 62.2833 | -62.439 | 0.086975 | -0.16022 | 124.8596 | 124.585 | -124.5941 | -0.10529 | -0.050354 | 124.7726 | 62.6083 | 62.2238 | 0.073242 | 124.5071 | 124.8596 | 124.617 | -0.082398 | -0.10529 | 124.5071 | 124.8596 | -0.082398 | 0.073242 | 124.617 | -124.5804 | -124.7726
214.7812 | 124.8642 | -62.3245 | 62.3611 | 0.0070192 | 0.063352 | 0.053278 | 6.6302e-05 | -0.0019825 | 0.068199 | 0.069626 | 62.4802 | 62.2009 | -62.233 | 62.2009 | -62.2879 | -62.439 | 0.39825 | -0.16022 | 62.3108 | -62.4069 | 0.091553 | -0.16022 | 124.8047 | 124.5255 | -124.649 | -0.082397 | -0.050354 | 124.7131 | 62.7228 | 62.1643 | 0.036621 | 124.5255 | 124.8047 | 124.6353 | -0.11444 | -0.082397 | 124.5255 | 124.8047 | -0.11444 | 0.036621 | 124.6353 | -124.5941 | -124.7681
215.7969 | 124.942 | -62.2925 | 62.3108 | -0.00061033 | 0.063566 | 0.061609 | -0.0022837 | -0.0039051 | 0.067772 | 0.069413 | 62.5488 | 62.1185 | -62.2009 | 62.2696 | -62.233 | -62.3749 | 0.16022 | -0.16022 | 62.2284 | -62.4252 | 0.091552 | -0.19226 | 124.8413 | 124.5621 | -124.5438 | -0.13275 | -0.082397 | 124.7498 | 62.4527 | 62.1323 | 0.059509 | 124.411 | 124.8413 | 124.5209 | -0.082398 | -0.13275 | 124.411 | 124.8413 | -0.082398 | 0.059509 | 124.5209 | -124.5117 | -124.736
216.7812 | 124.8413 | -62.3245 | 62.3795 | -0.00061033 | 0.061002 | 0.056055 | 0.0004935 | -0.0054003 | 0.06884 | 0.070053 | 62.4893 | 62.1735 | -62.233 | 62.2147 | -62.2833 | -62.4619 | 0.44861 | -0.14648 | 62.2879 | -62.4023 | 0.091553 | -0.20599 | 124.8138 | 124.5392 | -124.6628 | -0.07782 | -0.091553 | 124.7223 | 62.7731 | 62.178 | 0.041199 | 124.498 | 124.8138 | 124.6124 | -0.13733 | -0.07782 | 124.498 | 124.8138 | -0.13733 | 0.041199 | 124.6124 | -124.6124 | -124.7818
217.7812 | 124.823 | -62.3291 | 62.3611 | -0.0082398 | 0.066984 | 0.058405 | 0.0022025 | -0.0068957 | 0.06649 | 0.06984 | 62.4893 | 62.2055 | -62.233 | 62.2009 | -62.2971 | -62.4573 | 0.4715 | -0.19226 | 62.3062 | -62.4344 | 0.096131 | -0.15564 | 124.8184 | 124.53 | -124.6582 | -0.10529 | -0.054932 | 124.7223 | 62.8006 | 62.1368 | 0.032044 | 124.5346 | 124.8184 | 124.6353 | -0.12817 | -0.10529 | 124.5346 | 124.8184 | -0.12817 | 0.032044 | 124.6353 | -124.5941 | -124.7955
218.7812 | 124.8734 | -62.3245 | 62.3611 | -0.0082398 | 0.063566 | 0.056055 | -0.0010019 | -0.0058277 | 0.068413 | 0.06749 | 62.558 | 62.1506 | -62.2055 | 62.3062 | -62.2192 | -62.3978 | 0.37994 | -0.11902 | 62.2833 | -62.3795 | 0.11902 | -0.21057 | 124.8825 | 124.6307 | -124.5804 | -0.054932 | -0.07782 | 124.7635 | 62.7045 | 62.2055 | 0.10529 | 124.4751 | 124.8825 | 124.6078 | -0.073242 | -0.054932 | 124.4751 | 124.8825 | -0.073242 | 0.10529 | 124.6078 | -124.5667 | -124.7406
219.7812 | 124.8413 | -62.3428 | 62.3795 | -0.00061033 | 0.064206 | 0.055414 | -0.0003611 | -0.0060413 | 0.066917 | 0.068131 | 62.4893 | 62.1872 | -62.2192 | 62.2421 | -62.265 | -62.4344 | 0.46692 | -0.19226 | 62.3016 | -62.4115 | 0.1236 | -0.19226 | 124.8322 | 124.585 | -124.6445 | -0.068665 | -0.07782 | 124.7086 | 62.8098 | 62.1506 | 0.077819 | 124.53 | 124.8322 | 124.6445 | -0.091553 | -0.068665 | 124.53 | 124.8322 | -0.091553 | 0.077819 | 124.6445 | -124.5987 | -124.791
220.7969 | 124.9557 | -62.3383 | 62.3062 | -0.0082398 | 0.063779 | 0.054559 | 0.0019889 | -0.0030505 | 0.065636 | 0.069199 | 62.5534 | 62.114 | -62.2192 | 62.2879 | -62.233 | -62.3703 | 0.1831 | -0.22888 | 62.1872 | -62.4481 | 0.11902 | -0.19226 | 124.8917 | 124.6262 | -124.5392 | -0.10986 | -0.11902 | 124.7726 | 62.5214 | 62.1094 | 0.10529 | 124.4522 | 124.8917 | 124.5255 | -0.032043 | -0.10986 | 124.4522 | 124.8917 | -0.032043 | 0.10529 | 124.5255 | -124.5255 | -124.7543
221.7812 | 124.8734 | -62.3245 | 62.3383 | -0.00061033 | 0.068265 | 0.060754 | 0.0026297 | -0.0021961 | 0.069054 | 0.068985 | 62.5397 | 62.1964 | -62.2467 | 62.2604 | -62.2696 | -62.439 | 0.42114 | -0.21973 | 62.2604 | -62.4481 | 0.07782 | -0.14191 | 124.8642 | 124.585 | -124.6078 | -0.1236 | -0.07782 | 124.7864 | 62.7457 | 62.1048 | 0.054932 | 124.5209 | 124.8642 | 124.585 | -0.11444 | -0.1236 | 124.5209 | 124.8642 | -0.11444 | 0.054932 | 124.585 | -124.585 | -124.7864
222.7812 | 124.942 | -62.2833 | 62.3337 | -0.00061033 | 0.059934 | 0.056696 | -0.0007883 | -0.0062549 | 0.065849 | 0.068772 | 62.5809 | 62.1323 | -62.2147 | 62.3291 | -62.1735 | -62.3291 | 0.39368 | -0.14191 | 62.2559 | -62.3611 | 0.068664 | -0.20142 | 124.8642 | 124.6124 | -124.5071 | -0.07782 | -0.07782 | 124.7955 | 62.677 | 62.1414 | 0.10986 | 124.4156 | 124.8642 | 124.5392 | -0.045777 | -0.07782 | 124.4156 | 124.8642 | -0.045777 | 0.10986 | 124.5392 | -124.5483 | -124.6948
223.7969 | 124.9512 | -62.3154 | 62.2971 | 0.0070192 | 0.06442 | 0.062036 | 0.0013479 | -0.0032641 | 0.065849 | 0.06749 | 62.558 | 62.1368 | -62.2284 | 62.265 | -62.2467 | -62.3703 | 0.27924 | -0.27008 | 62.1964 | -62.4435 | 0.086975 | -0.16022 | 124.8734 | 124.5804 | -124.5438 | -0.12817 | -0.10071 | 124.7864 | 62.5946 | 62.0453 | 0.068665 | 124.4522 | 124.8734 | 124.5117 | -0.054931 | -0.12817 | 124.4522 | 124.8734 | -0.054931 | 0.068665 | 124.5117 | -124.5255 | -124.7406
224.7812 | 124.9878 | -62.2787 | 62.3291 | -0.0082398 | 0.058866 | 0.059045 | -0.0016427 | -0.0066821 | 0.066277 | 0.06749 | 62.5809 | 62.114 | -62.2192 | 62.3474 | -62.1643 | -62.3108 | 0.37994 | -0.1831 | 62.2055 | -62.3474 | 0.05951 | -0.21515 | 124.8596 | 124.6262 | -124.4934 | -0.068664 | -0.1236 | 124.8001 | 62.6587 | 62.0956 | 0.11444 | 124.3927 | 124.8596 | 124.4843 | -0.032043 | -0.068664 | 124.3927 | 124.8596 | -0.032043 | 0.11444 | 124.4843 | -124.5483 | -124.6765
225.7812 | 124.8596 | -62.3154 | 62.3611 | -0.00061033 | 0.063566 | 0.061395 | 0.0019889 | -0.0060413 | 0.065208 | 0.071335 | 62.5351 | 62.1414 | -62.1918 | 62.2604 | -62.2467 | -62.4115 | 0.59967 | -0.28839 | 62.2559 | -62.4161 | 0.1236 | -0.21973 | 124.8505 | 124.5758 | -124.6078 | -0.10071 | -0.10529 | 124.7269 | 62.915 | 62.027 | 0.068665 | 124.4568 | 124.8505 | 124.5712 | -0.09613 | -0.10071 | 124.4568 | 124.8505 | -0.09613 | 0.068665 | 124.5712 | -124.5529 | -124.7772
226.7812 | 124.8825 | -62.352 | 62.3474 | 0.022278 | 0.063352 | 0.057123 | 0.0004935 | -0.0058277 | 0.066917 | 0.067917 | 62.5626 | 62.1277 | -62.1872 | 62.3108 | -62.2147 | -62.384 | 0.57678 | -0.27466 | 62.2696 | -62.3795 | 0.16479 | -0.21973 | 124.9146 | 124.6628 | -124.5621 | -0.027466 | -0.07782 | 124.7498 | 62.9288 | 62.0773 | 0.13733 | 124.4797 | 124.9146 | 124.6216 | -0.032043 | -0.027466 | 124.4797 | 124.9146 | -0.032043 | 0.13733 | 124.6216 | -124.5346 | -124.7269
227.7812 | 124.823 | -62.3749 | 62.3703 | -0.00061033 | 0.064634 | 0.056696 | 0.0019889 | -0.0047595 | 0.065208 | 0.06749 | 62.4847 | 62.1643 | -62.2055 | 62.2192 | -62.3062 | -62.4619 | 0.71411 | -0.3891 | 62.2833 | -62.4115 | 0.16937 | -0.20599 | 124.8596 | 124.5941 | -124.6765 | -0.036621 | -0.086975 | 124.6902 | 63.089 | 61.9858 | 0.068665 | 124.5392 | 124.8596 | 124.6582 | -0.086975 | -0.036621 | 124.5392 | 124.8596 | -0.086975 | 0.068665 | 124.6582 | -124.5758 | -124.7818
228.7969 | 124.9695 | -62.3199 | 62.3291 | -0.0082398 | 0.058866 | 0.056268 | -0.0020701 | -0.0047595 | 0.067772 | 0.068131 | 62.59 | 62.0956 | -62.2055 | 62.3383 | -62.1597 | -62.3062 | 0.49896 | -0.2655 | 62.2284 | -62.3428 | 0.11444 | -0.23346 | 124.91 | 124.6582 | -124.4888 | -0.022888 | -0.10071 | 124.7955 | 62.8189 | 62.0544 | 0.16022 | 124.4156 | 124.91 | 124.5483 | 0.013733 | -0.022888 | 124.4156 | 124.91 | 0.013733 | 0.16022 | 124.5483 | -124.5346 | -124.6719
229.7812 | 124.9466 | -62.3199 | 62.3383 | -0.015869 | 0.062497 | 0.056482 | 0.0007071 | -0.0062549 | 0.067558 | 0.069413 | 62.5946 | 62.1002 | -62.1964 | 62.3428 | -62.1643 | -62.3337 | 0.57678 | -0.27008 | 62.2147 | -62.352 | 0.1236 | -0.23804 | 124.9145 | 124.6628 | -124.5026 | -0.032044 | -0.1236 | 124.791 | 62.8967 | 62.0499 | 0.15564 | 124.4202 | 124.9145 | 124.5346 | -0.013733 | -0.032044 | 124.4202 | 124.9145 | -0.013733 | 0.15564 | 124.5346 | -124.5346 | -124.6902
230.7812 | 124.9649 | -62.3108 | 62.3245 | -0.0082398 | 0.061002 | 0.054132 | -0.0003611 | -0.0077503 | 0.065208 | 0.069626 | 62.5809 | 62.1231 | -62.1964 | 62.3474 | -62.146 | -62.3199 | 0.59967 | -0.28381 | 62.2467 | -62.3428 | 0.11444 | -0.20142 | 124.8917 | 124.6582 | -124.4705 | -0.032043 | -0.07782 | 124.7772 | 62.9105 | 62.027 | 0.1648 | 124.4339 | 124.8917 | 124.5575 | -0.009155 | -0.032043 | 124.4339 | 124.8917 | -0.009155 | 0.1648 | 124.5575 | -124.5209 | -124.6674
231.7969 | 124.8962 | -62.3566 | 62.3016 | -0.0082398 | 0.065061 | 0.062677 | 0.0036979 | -0.0039051 | 0.067345 | 0.067917 | 62.4756 | 62.1323 | -62.265 | 62.2101 | -62.2879 | -62.4344 | 0.62714 | -0.49896 | 62.1964 | -62.4298 | 0.091552 | -0.16937 | 124.8322 | 124.5666 | -124.5895 | -0.073243 | -0.10529 | 124.7406 | 62.9837 | 61.8576 | 0.068664 | 124.4888 | 124.8322 | 124.5529 | -0.07782 | -0.073243 | 124.4888 | 124.8322 | -0.07782 | 0.068664 | 124.5529 | -124.5667 | -124.7314
232.7812 | 124.9557 | -62.2971 | 62.3428 | -0.00061033 | 0.058439 | 0.060114 | 0.0002799 | -0.0073229 | 0.067985 | 0.067276 | 62.5214 | 62.1002 | -62.1826 | 62.3245 | -62.1735 | -62.3199 | 0.6958 | -0.39368 | 62.2375 | -62.3428 | 0.11444 | -0.24261 | 124.8184 | 124.6216 | -124.5163 | -0.045776 | -0.10529 | 124.704 | 62.9929 | 61.9034 | 0.1236 | 124.3973 | 124.8184 | 124.5346 | -0.022888 | -0.045776 | 124.3973 | 124.8184 | -0.022888 | 0.1236 | 124.5346 | -124.5255 | -124.6857
233.7812 | 124.9649 | -62.3199 | 62.2971 | -0.0082398 | 0.061429 | 0.056268 | -0.0018563 | -0.0054003 | 0.067345 | 0.068131 | 62.5717 | 62.1002 | -62.1826 | 62.3383 | -62.1643 | -62.3062 | 0.70953 | -0.37537 | 62.2147 | -62.3474 | 0.13733 | -0.19684 | 124.8917 | 124.6582 | -124.4614 | -0.027466 | -0.082397 | 124.7543 | 63.0295 | 61.9446 | 0.15564 | 124.4202 | 124.8917 | 124.5346 | 0.013733 | -0.027466 | 124.4202 | 124.8917 | 0.013733 | 0.15564 | 124.5346 | -124.4797 | -124.6445
234.7812 | 124.9649 | -62.2696 | 62.3383 | -0.0082398 | 0.059293 | 0.058191 | -0.0012155 | -0.0071093 | 0.064995 | 0.068985 | 62.6083 | 62.1002 | -62.1872 | 62.3611 | -62.1277 | -62.3108 | 0.78278 | -0.39825 | 62.2421 | -62.3611 | 0.082397 | -0.23804 | 124.8779 | 124.6307 | -124.4659 | -0.091553 | -0.096131 | 124.7955 | 63.0524 | 61.8713 | 0.14191 | 124.3698 | 124.8779 | 124.5117 | -0.041199 | -0.091553 | 124.3698 | 124.8779 | -0.041199 | 0.14191 | 124.5117 | -124.5255 | -124.6994
235.7812 | 124.9466 | -62.3016 | 62.3383 | -0.0082398 | 0.061429 | 0.059473 | 0.0017753 | -0.0068957 | 0.067131 | 0.066422 | 62.5763 | 62.1277 | -62.1826 | 62.3611 | -62.1552 | -62.3154 | 0.86975 | -0.4303 | 62.2421 | -62.3566 | 0.11902 | -0.21057 | 124.8779 | 124.6628 | -124.4934 | -0.054931 | -0.096131 | 124.7589 | 63.1714 | 61.8713 | 0.14649 | 124.4293 | 124.8779 | 124.5438 | -0.013733 | -0.054931 | 124.4293 | 124.8779 | -0.013733 | 0.14649 | 124.5438 | -124.5209 | -124.6948
236.7969 | 124.9557 | -62.3245 | 62.3016 | -0.015869 | 0.061429 | 0.058191 | 0.0034841 | -0.0060413 | 0.066277 | 0.067063 | 62.5488 | 62.0773 | -62.2055 | 62.2879 | -62.2055 | -62.3474 | 0.76446 | -0.58136 | 62.1826 | -62.384 | 0.11902 | -0.2243 | 124.8734 | 124.6124 | -124.5071 | -0.059509 | -0.11902 | 124.7543 | 63.089 | 61.7432 | 0.11902 | 124.4019 | 124.8734 | 124.5071 | -0.022888 | -0.059509 | 124.4019 | 124.8734 | -0.022888 | 0.11902 | 124.5071 | -124.5071 | -124.6857
237.7812 | 124.9649 | -62.3108 | 62.3062 | 0.0070192 | 0.058225 | 0.054559 | 0.0009207 | -0.0068957 | 0.068626 | 0.069413 | 62.5763 | 62.0956 | -62.1918 | 62.352 | -62.1506 | -62.3062 | 0.92926 | -0.51727 | 62.2055 | -62.3428 | 0.11902 | -0.21057 | 124.8871 | 124.6628 | -124.4568 | -0.032043 | -0.10071 | 124.7681 | 63.2401 | 61.7935 | 0.16022 | 124.4064 | 124.8871 | 124.5163 | 0.004578 | -0.032043 | 124.4064 | 124.8871 | 0.004578 | 0.16022 | 124.5163 | -124.498 | -124.649
238.7812 | 124.9374 | -62.3291 | 62.3337 | -0.00061033 | 0.059293 | 0.054132 | -0.0016427 | -0.0075367 | 0.067345 | 0.070267 | 62.5214 | 62.0865 | -62.2192 | 62.2787 | -62.2147 | -62.3795 | 1.03 | -0.62714 | 62.2147 | -62.3703 | 0.10986 | -0.24719 | 124.8505 | 124.6078 | -124.5483 | -0.041198 | -0.11902 | 124.7406 | 63.3591 | 61.702 | 0.11444 | 124.4156 | 124.8505 | 124.5438 | -0.050354 | -0.041198 | 124.4156 | 124.8505 | -0.050354 | 0.11444 | 124.5438 | -124.5529 | -124.704
239.8125 | 124.9466 | -62.3108 | 62.3062 | 0.0070192 | 0.066129 | 0.060114 | 0.0058341 | -0.0068957 | 0.067558 | 0.068344 | 62.5305 | 62.1185 | -62.2284 | 62.2513 | -62.265 | -62.4023 | 0.99335 | -0.72327 | 62.1826 | -62.4573 | 0.082397 | -0.18768 | 124.8413 | 124.5621 | -124.5712 | -0.14648 | -0.1236 | 124.7589 | 63.3041 | 61.5875 | 0.045776 | 124.4293 | 124.8413 | 124.4934 | -0.091553 | -0.14648 | 124.4293 | 124.8413 | -0.091553 | 0.045776 | 124.4934 | -124.5346 | -124.7635
240.7812 | 124.942 | -62.2879 | 62.3337 | -0.00061033 | 0.061216 | 0.057123 | 0.0026297 | -0.0071093 | 0.064781 | 0.068344 | 62.5809 | 62.0819 | -62.1872 | 62.3428 | -62.1643 | -62.3199 | 1.1856 | -0.62256 | 62.2467 | -62.3657 | 0.10071 | -0.25177 | 124.8688 | 124.6307 | -124.498 | -0.07782 | -0.086975 | 124.7681 | 63.4735 | 61.6653 | 0.1236 | 124.3698 | 124.8688 | 124.5346 | -0.032043 | -0.07782 | 124.3698 | 124.8688 | -0.032043 | 0.1236 | 124.5346 | -124.5209 | -124.6994
241.7812 | 124.9557 | -62.2971 | 62.3428 | -0.015869 | 0.059293 | 0.056055 | -0.0014291 | -0.0068957 | 0.067772 | 0.068985 | 62.5534 | 62.0956 | -62.2009 | 62.3245 | -62.1643 | -62.3154 | 1.2131 | -0.71869 | 62.2238 | -62.3383 | 0.09613 | -0.24719 | 124.8505 | 124.6216 | -124.5071 | -0.041199 | -0.11902 | 124.7543 | 63.5101 | 61.5784 | 0.13275 | 124.3927 | 124.8505 | 124.5209 | -0.018311 | -0.041199 | 124.3927 | 124.8505 | -0.018311 | 0.13275 | 124.5209 | -124.5438 | -124.6811
242.7812 | 124.9741 | -62.2971 | 62.3337 | 0.0070192 | 0.05908 | 0.057123 | 0.0015615 | -0.0077503 | 0.067345 | 0.068985 | 62.5854 | 62.0819 | -62.2009 | 62.3703 | -62.1414 | -62.2879 | 1.2772 | -0.70038 | 62.2101 | -62.3337 | 0.09613 | -0.25177 | 124.8825 | 124.6674 | -124.4751 | -0.036621 | -0.1236 | 124.7864 | 63.5742 | 61.5967 | 0.15564 | 124.379 | 124.8825 | 124.5071 | 0.009155 | -0.036621 | 124.379 | 124.8825 | 0.009155 | 0.15564 | 124.5071 | -124.5346 | -124.6674
243.7812 | 124.823 | -62.3383 | 62.3611 | 0.0070192 | 0.064847 | 0.055414 | 0.0047659 | -0.0075367 | 0.066063 | 0.069626 | 62.471 | 62.178 | -62.2375 | 62.2192 | -62.265 | -62.4573 | 1.5701 | -0.86975 | 62.2696 | -62.4069 | 0.10071 | -0.1831 | 124.8093 | 124.5575 | -124.6262 | -0.068664 | -0.091553 | 124.7086 | 63.9084 | 61.4685 | 0.073242 | 124.5163 | 124.8093 | 124.6078 | -0.11902 | -0.068664 | 124.5163 | 124.8093 | -0.11902 | 0.073242 | 124.6078 | -124.5987 | -124.7681
244.8125 | 124.8367 | -62.3383 | 62.3703 | -0.00061033 | 0.066984 | 0.057336 | 0.0039115 | -0.0058277 | 0.067985 | 0.06749 | 62.4802 | 62.1918 | -62.2238 | 62.2192 | -62.2742 | -62.4573 | 1.6296 | -0.91553 | 62.2742 | -62.4344 | 0.11444 | -0.17853 | 124.8184 | 124.5575 | -124.6445 | -0.09613 | -0.09613 | 124.704 | 63.9679 | 61.4227 | 0.064087 | 124.53 | 124.8184 | 124.6124 | -0.11902 | -0.09613 | 124.53 | 124.8184 | -0.11902 | 0.064087 | 124.6124 | -124.5941 | -124.8047
245.7812 | 124.9603 | -62.2971 | 62.3108 | 0.0070192 | 0.060575 | 0.060541 | -0.0005747 | -0.0056141 | 0.068199 | 0.068131 | 62.5809 | 62.0911 | -62.1872 | 62.3428 | -62.1597 | -62.3199 | 1.5335 | -0.84228 | 62.2467 | -62.3383 | 0.10986 | -0.21973 | 124.8779 | 124.6399 | -124.4705 | -0.041199 | -0.064087 | 124.7681 | 63.8306 | 61.4548 | 0.13733 | 124.3881 | 124.8779 | 124.5438 | -0.022888 | -0.041199 | 124.3881 | 124.8779 | -0.022888 | 0.13733 | 124.5438 | -124.498 | -124.649
246.7812 | 124.9603 | -62.2971 | 62.3291 | -0.0082398 | 0.061643 | 0.057123 | -0.0001473 | -0.0077503 | 0.065422 | 0.066849 | 62.5763 | 62.0865 | -62.1872 | 62.3383 | -62.1643 | -62.3108 | 1.5564 | -0.91553 | 62.2055 | -62.3383 | 0.10986 | -0.24262 | 124.8734 | 124.6353 | -124.4934 | -0.041199 | -0.1236 | 124.7635 | 63.8535 | 61.3815 | 0.13275 | 124.3835 | 124.8734 | 124.5026 | -0.013733 | -0.041199 | 124.3835 | 124.8734 | -0.013733 | 0.13275 | 124.5026 | -124.5163 | -124.6674
247.7969 | 124.8779 | -62.3657 | 62.3337 | 0.0070192 | 0.063779 | 0.060754 | 0.0047659 | -0.0054003 | 0.064568 | 0.067063 | 62.5122 | 62.1323 | -62.2513 | 62.2421 | -62.2467 | -62.4161 | 1.767 | -1.0437 | 62.2238 | -62.3932 | 0.11444 | -0.20142 | 124.8779 | 124.6078 | -124.5804 | -0.027465 | -0.10986 | 124.7635 | 64.1327 | 61.322 | 0.11902 | 124.498 | 124.8779 | 124.5895 | -0.050354 | -0.027465 | 124.498 | 124.8779 | -0.050354 | 0.11902 | 124.5895 | -124.585 | -124.7269
248.7812 | 124.942 | -62.3291 | 62.3428 | -0.015869 | 0.062711 | 0.059259 | -0.0027109 | -0.0043323 | 0.064568 | 0.069199 | 62.5763 | 62.1048 | -62.2055 | 62.3108 | -62.1826 | -62.3337 | 1.8036 | -1.0025 | 62.2284 | -62.3566 | 0.1236 | -0.23804 | 124.9054 | 124.6399 | -124.5255 | -0.027465 | -0.11444 | 124.7818 | 64.1327 | 61.3266 | 0.14648 | 124.4339 | 124.9054 | 124.5575 | -0.004577 | -0.027465 | 124.4339 | 124.9054 | -0.004577 | 0.14648 | 124.5575 | -124.5483 | -124.6994
249.7969 | 124.9146 | -62.3016 | 62.3611 | -0.0082398 | 0.060789 | 0.057336 | 0.0004935 | -0.0066821 | 0.065849 | 0.070267 | 62.5534 | 62.1048 | -62.1735 | 62.3154 | -62.1735 | -62.3428 | 1.918 | -1.0483 | 62.2513 | -62.352 | 0.12817 | -0.25635 | 124.855 | 124.617 | -124.5346 | -0.050354 | -0.10986 | 124.7269 | 64.2197 | 61.2534 | 0.12817 | 124.4064 | 124.855 | 124.5529 | -0.041198 | -0.050354 | 124.4064 | 124.855 | -0.041198 | 0.12817 | 124.5529 | -124.5346 | -124.7131
250.7812 | 124.9512 | -62.3062 | 62.3062 | -0.0082398 | 0.056943 | 0.060968 | -0.0016427 | -0.0075367 | 0.065422 | 0.067917 | 62.5946 | 62.0911 | -62.1643 | 62.3611 | -62.1323 | -62.2925 | 1.9272 | -1.0757 | 62.2513 | -62.3154 | 0.14191 | -0.21515 | 124.9008 | 124.6674 | -124.4385 | -0.009156 | -0.054931 | 124.7589 | 64.2334 | 61.2305 | 0.17395 | 124.3973 | 124.9008 | 124.5575 | 0.013733 | -0.009156 | 124.3973 | 124.9008 | 0.013733 | 0.17395 | 124.5575 | -124.4705 | -124.6216
251.7812 | 124.8688 | -62.352 | 62.3566 | -0.0082398 | 0.061002 | 0.054987 | 0.0011343 | -0.0081775 | 0.066917 | 0.071549 | 62.5626 | 62.1368 | -62.2101 | 62.2559 | -62.2147 | -62.3795 | 2.1698 | -1.1719 | 62.2467 | -62.3749 | 0.14191 | -0.21973 | 124.9146 | 124.6078 | -124.5712 | -0.022888 | -0.10986 | 124.7726 | 64.5218 | 61.1801 | 0.13733 | 124.4888 | 124.9146 | 124.5987 | -0.027466 | -0.022888 | 124.4888 | 124.9146 | -0.027466 | 0.13733 | 124.5987 | -124.5666 | -124.7314
252.7812 | 124.9008 | -62.3337 | 62.3062 | 0.0070192 | 0.060361 | 0.053278 | -0.0010019 | -0.0060413 | 0.066277 | 0.06984 | 62.4985 | 62.0819 | -62.2101 | 62.2238 | -62.2513 | -62.3932 | 2.1286 | -1.3092 | 62.2192 | -62.3566 | 0.1236 | -0.2243 | 124.8322 | 124.5575 | -124.5575 | -0.022888 | -0.086975 | 124.7086 | 64.4623 | 61.0245 | 0.082397 | 124.4156 | 124.8322 | 124.5529 | -0.059509 | -0.022888 | 124.4156 | 124.8322 | -0.059509 | 0.082397 | 124.5529 | -124.5163 | -124.6628
253.7812 | 124.9512 | -62.3199 | 62.3383 | -0.00061033 | 0.059934 | 0.056482 | 0.0002799 | -0.0071093 | 0.067558 | 0.068558 | 62.59 | 62.0956 | -62.1964 | 62.3383 | -62.1643 | -62.3108 | 2.2247 | -1.1948 | 62.1826 | -62.3383 | 0.1236 | -0.24262 | 124.91 | 124.6582 | -124.5026 | -0.018311 | -0.15564 | 124.7864 | 64.5447 | 61.1252 | 0.15564 | 124.4156 | 124.91 | 124.5026 | 0.009155 | -0.018311 | 124.4156 | 124.91 | 0.009155 | 0.15564 | 124.5026 | -124.5346 | -124.6765
254.7969 | 124.9283 | -62.3657 | 62.2879 | -0.015869 | 0.061857 | 0.060754 | 0.0054069 | -0.0047595 | 0.065422 | 0.06749 | 62.4939 | 62.0819 | -62.233 | 62.2284 | -62.2696 | -62.3932 | 2.243 | -1.4328 | 62.1826 | -62.3978 | 0.13275 | -0.20599 | 124.8596 | 124.5941 | -124.5575 | -0.032043 | -0.10529 | 124.7269 | 64.6088 | 60.9329 | 0.096131 | 124.4476 | 124.8596 | 124.5483 | -0.027465 | -0.032043 | 124.4476 | 124.8596 | -0.027465 | 0.096131 | 124.5483 | -124.5209 | -124.6857
255.7812 | 124.8322 | -62.3474 | 62.3337 | -0.00061033 | 0.062711 | 0.056909 | 0.0024161 | -0.0066821 | 0.064354 | 0.069626 | 62.5122 | 62.1414 | -62.2009 | 62.2284 | -62.2604 | -62.4252 | 2.6093 | -1.4191 | 62.265 | -62.3932 | 0.14648 | -0.19226 | 124.8596 | 124.5758 | -124.5941 | -0.045776 | -0.068664 | 124.7131 | 64.9567 | 60.9283 | 0.086975 | 124.4888 | 124.8596 | 124.6124 | -0.07782 | -0.045776 | 124.4888 | 124.8596 | -0.07782 | 0.086975 | 124.6124 | -124.5346 | -124.7269
256.7812 | 124.9329 | -62.3108 | 62.3199 | -0.0082398 | 0.063566 | 0.056696 | 0.0024161 | -0.0071093 | 0.068199 | 0.068985 | 62.5671 | 62.1002 | -62.1918 | 62.2971 | -62.1552 | -62.3245 | 2.5772 | -1.3779 | 62.2192 | -62.3428 | 0.11902 | -0.21973 | 124.8779 | 124.6078 | -124.4751 | -0.032043 | -0.10071 | 124.7589 | 64.888 | 60.9329 | 0.15564 | 124.411 | 124.8779 | 124.53 | -0.013733 | -0.032043 | 124.411 | 124.8779 | -0.013733 | 0.15564 | 124.53 | -124.5117 | -124.6628
257.7969 | 124.9695 | -62.2833 | 62.3062 | -0.0082398 | 0.062925 | 0.058191 | -0.0003611 | -0.0064685 | 0.065208 | 0.067276 | 62.5671 | 62.1185 | -62.1918 | 62.3108 | -62.1597 | -62.3154 | 2.6459 | -1.4328 | 62.1826 | -62.3703 | 0.091553 | -0.18768 | 124.8505 | 124.5941 | -124.4659 | -0.086975 | -0.1236 | 124.7589 | 64.9292 | 60.8505 | 0.1236 | 124.4019 | 124.8505 | 124.4659 | -0.032044 | -0.086975 | 124.4019 | 124.8505 | -0.032044 | 0.1236 | 124.4659 | -124.498 | -124.6765
258.7812 | 124.942 | -62.3016 | 62.3245 | -0.0082398 | 0.061643 | 0.061395 | -0.0012155 | -0.0066821 | 0.066277 | 0.067917 | 62.5305 | 62.1094 | -62.1964 | 62.2925 | -62.1689 | -62.3154 | 2.7695 | -1.5152 | 62.2192 | -62.3474 | 0.10529 | -0.21515 | 124.8322 | 124.5941 | -124.4934 | -0.045776 | -0.10529 | 124.7269 | 65.0711 | 60.7864 | 0.13275 | 124.411 | 124.8322 | 124.5209 | -0.013733 | -0.045776 | 124.411 | 124.8322 | -0.013733 | 0.13275 | 124.5209 | -124.5209 | -124.6719
259.7969 | 124.7955 | -62.4069 | 62.3245 | -0.0082398 | 0.065915 | 0.061609 | 0.0069021 | -0.0068957 | 0.065208 | 0.070267 | 62.4344 | 62.1368 | -62.2604 | 62.1277 | -62.3566 | -62.4985 | 2.9938 | -1.8356 | 62.2147 | -62.471 | 0.14648 | -0.18768 | 124.8413 | 124.5346 | -124.6811 | -0.064087 | -0.10986 | 124.6948 | 65.4007 | 60.5713 | 0.050354 | 124.5438 | 124.8413 | 124.6216 | -0.091553 | -0.064087 | 124.5438 | 124.8413 | -0.091553 | 0.050354 | 124.6216 | -124.585 | -124.7955
260.7812 | 124.9512 | -62.3199 | 62.3383 | -0.00061033 | 0.058439 | 0.057336 | -0.0022837 | -0.0064685 | 0.06884 | 0.067917 | 62.5397 | 62.0911 | -62.2055 | 62.2696 | -62.1689 | -62.3108 | 3.0029 | -1.68 | 62.2375 | -62.3474 | 0.11444 | -0.24719 | 124.8596 | 124.5895 | -124.5071 | -0.027466 | -0.10071 | 124.7452 | 65.3229 | 60.64 | 0.15106 | 124.411 | 124.8596 | 124.5575 | 0.009155 | -0.027466 | 124.411 | 124.8596 | 0.009155 | 0.15106 | 124.5575 | -124.5438 | -124.6857
261.7812 | 124.8322 | -62.3383 | 62.3611 | -0.00061033 | 0.063352 | 0.060114 | 0.0041251 | -0.0079639 | 0.064995 | 0.06984 | 62.4664 | 62.1826 | -62.233 | 62.1826 | -62.2696 | -62.4527 | 3.3188 | -1.8356 | 62.2467 | -62.3795 | 0.10529 | -0.17853 | 124.8047 | 124.5209 | -124.6307 | -0.041199 | -0.11444 | 124.6994 | 65.657 | 60.5026 | 0.068665 | 124.5209 | 124.8047 | 124.585 | -0.11444 | -0.041199 | 124.5209 | 124.8047 | -0.11444 | 0.068665 | 124.585 | -124.5941 | -124.7406
262.7812 | 124.9695 | -62.3016 | 62.3291 | 0.0070192 | 0.061216 | 0.054132 | -0.0012155 | -0.0049731 | 0.066277 | 0.068131 | 62.5809 | 62.0728 | -62.1918 | 62.3062 | -62.1231 | -62.2925 | 3.2867 | -1.767 | 62.233 | -62.3383 | 0.10986 | -0.25635 | 124.8825 | 124.6078 | -124.4522 | -0.036621 | -0.096131 | 124.7726 | 65.5884 | 60.5347 | 0.17853 | 124.3744 | 124.8825 | 124.5346 | 0.009156 | -0.036621 | 124.3744 | 124.8825 | 0.009156 | 0.17853 | 124.5346 | -124.5209 | -124.6674
263.7969 | 124.823 | -62.3428 | 62.3154 | -0.0082398 | 0.065915 | 0.061823 | 0.0062613 | -0.0056141 | 0.068626 | 0.070908 | 62.5031 | 62.1552 | -62.2604 | 62.1918 | -62.2971 | -62.4802 | 3.4973 | -2.0187 | 62.2238 | -62.4344 | 0.082397 | -0.16022 | 124.8459 | 124.5346 | -124.6124 | -0.091553 | -0.091553 | 124.7635 | 65.8401 | 60.3241 | 0.045776 | 124.498 | 124.8459 | 124.5667 | -0.13733 | -0.091553 | 124.498 | 124.8459 | -0.13733 | 0.045776 | 124.5667 | -124.5758 | -124.7498
264.7969 | 124.8917 | -62.2971 | 62.2833 | -0.023499 | 0.061643 | 0.056268 | -0.0016427 | -0.0058277 | 0.066063 | 0.068131 | 62.4893 | 62.1277 | -62.1964 | 62.2101 | -62.2284 | -62.3749 | 3.5431 | -2.0554 | 62.2147 | -62.3886 | 0.10071 | -0.15564 | 124.7864 | 124.5071 | -124.5117 | -0.091553 | -0.068664 | 124.6857 | 65.8401 | 60.2417 | 0.068664 | 124.4247 | 124.7864 | 124.5117 | -0.07782 | -0.091553 | 124.4247 | 124.7864 | -0.07782 | 0.068664 | 124.5117 | -124.4797 | -124.6719
265.7812 | 124.9374 | -62.2925 | 62.3337 | 0.0070192 | 0.061643 | 0.056482 | 0.0015615 | -0.0064685 | 0.066063 | 0.070694 | 62.5534 | 62.0819 | -62.2009 | 62.2971 | -62.1552 | -62.3245 | 3.6804 | -2.0233 | 62.2147 | -62.3337 | 0.091552 | -0.25177 | 124.8459 | 124.5895 | -124.4888 | -0.041199 | -0.11902 | 124.7543 | 65.9729 | 60.2692 | 0.13733 | 124.3744 | 124.8459 | 124.5071 | -0.032044 | -0.041199 | 124.3744 | 124.8459 | -0.032044 | 0.13733 | 124.5071 | -124.5346 | -124.6674
266.7812 | 124.9557 | -62.2879 | 62.3062 | -0.00061033 | 0.061002 | 0.057764 | -0.0010019 | -0.0062549 | 0.064995 | 0.068985 | 62.5763 | 62.1002 | -62.2101 | 62.3199 | -62.1323 | -62.2971 | 3.8132 | -2.1011 | 62.2192 | -62.3428 | 0.07782 | -0.20599 | 124.8642 | 124.6078 | -124.4385 | -0.054931 | -0.086975 | 124.7864 | 66.1011 | 60.1868 | 0.15564 | 124.3881 | 124.8642 | 124.5071 | -0.009155 | -0.054931 | 124.3881 | 124.8642 | -0.009155 | 0.15564 | 124.5071 | -124.5163 | -124.649
267.7969 | 124.823 | -62.3474 | 62.352 | -0.0082398 | 0.062711 | 0.06225 | 0.0022025 | -0.0090319 | 0.067772 | 0.069199 | 62.4481 | 62.1323 | -62.233 | 62.1552 | -62.2925 | -62.4527 | 4.1885 | -2.3346 | 62.265 | -62.3932 | 0.11444 | -0.21973 | 124.7955 | 124.5026 | -124.6445 | -0.045776 | -0.086975 | 124.6811 | 66.5359 | 60.0128 | 0.054932 | 124.4797 | 124.7955 | 124.6124 | -0.10529 | -0.045776 | 124.4797 | 124.7955 | -0.10529 | 0.054932 | 124.6124 | -124.585 | -124.7452
268.7812 | 124.8367 | -62.3245 | 62.352 | -0.00061033 | 0.060148 | 0.053278 | 6.6302e-05 | -0.0058277 | 0.067345 | 0.068558 | 62.5214 | 62.1414 | -62.2147 | 62.2192 | -62.2238 | -62.3886 | 4.2526 | -2.3758 | 62.2467 | -62.3749 | 0.10986 | -0.21057 | 124.8459 | 124.5438 | -124.5758 | -0.050354 | -0.10529 | 124.736 | 66.5771 | 59.9487 | 0.10071 | 124.4659 | 124.8459 | 124.5712 | -0.064087 | -0.050354 | 124.4659 | 124.8459 | -0.064087 | 0.10071 | 124.5712 | -124.5667 | -124.7269
269.7812 | 124.8093 | -62.3611 | 62.352 | -0.0082398 | 0.06207 | 0.0599 | 0.0030569 | -0.0045459 | 0.067772 | 0.068558 | 62.4756 | 62.1506 | -62.2101 | 62.1597 | -62.2742 | -62.4344 | 4.4998 | -2.4994 | 62.2742 | -62.4023 | 0.15106 | -0.20142 | 124.8367 | 124.5209 | -124.6262 | -0.041199 | -0.07782 | 124.6857 | 66.861 | 59.8618 | 0.086975 | 124.5117 | 124.8367 | 124.6353 | -0.073242 | -0.041199 | 124.5117 | 124.8367 | -0.073242 | 0.086975 | 124.6353 | -124.5621 | -124.7543
270.7812 | 124.9466 | -62.3245 | 62.2971 | -0.015869 | 0.058652 | 0.060114 | 0.0002799 | -0.0056141 | 0.065422 | 0.069626 | 62.5717 | 62.0956 | -62.178 | 62.2925 | -62.146 | -62.3108 | 4.454 | -2.4399 | 62.2559 | -62.3428 | 0.14648 | -0.20142 | 124.8962 | 124.617 | -124.4431 | -0.01831 | -0.041199 | 124.7498 | 66.7786 | 59.8846 | 0.17853 | 124.4202 | 124.8962 | 124.5804 | 0.013733 | -0.01831 | 124.4202 | 124.8962 | 0.013733 | 0.17853 | 124.5804 | -124.4751 | -124.6399
271.7812 | 124.8138 | -62.3383 | 62.3657 | -0.0082398 | 0.063779 | 0.060114 | 0.0041251 | -0.0054003 | 0.064568 | 0.068344 | 62.4756 | 62.1689 | -62.2192 | 62.1735 | -62.2971 | -62.4435 | 4.7791 | -2.6642 | 62.2833 | -62.3932 | 0.11902 | -0.19684 | 124.8138 | 124.5117 | -124.6628 | -0.054931 | -0.082398 | 124.6948 | 67.1173 | 59.6741 | 0.041199 | 124.5071 | 124.8138 | 124.6216 | -0.10529 | -0.054931 | 124.5071 | 124.8138 | -0.10529 | 0.041199 | 124.6216 | -124.585 | -124.7589
272.7812 | 124.8688 | -62.3428 | 62.3383 | 0.0070192 | 0.062711 | 0.05285 | 0.0009207 | -0.0045459 | 0.067131 | 0.069626 | 62.5671 | 62.1506 | -62.1689 | 62.233 | -62.2101 | -62.3886 | 4.8477 | -2.6596 | 62.2559 | -62.3474 | 0.17395 | -0.18768 | 124.91 | 124.5758 | -124.5483 | -0.004578 | -0.082398 | 124.736 | 67.1906 | 59.6832 | 0.13275 | 124.4934 | 124.91 | 124.5987 | -0.045777 | -0.004578 | 124.4934 | 124.91 | -0.045777 | 0.13275 | 124.5987 | -124.5071 | -124.6857
273.7812 | 124.9191 | -62.2925 | 62.3383 | -0.00061033 | 0.061002 | 0.0599 | -0.0012155 | -0.0051867 | 0.063927 | 0.066422 | 62.5946 | 62.1094 | -62.178 | 62.2787 | -62.146 | -62.3154 | 4.9118 | -2.6962 | 62.2238 | -62.3199 | 0.11444 | -0.22888 | 124.8871 | 124.5712 | -124.4843 | -0.027466 | -0.11444 | 124.7726 | 67.2043 | 59.5963 | 0.14648 | 124.4019 | 124.8871 | 124.5163 | -0.022889 | -0.027466 | 124.4019 | 124.8871 | -0.022889 | 0.14648 | 124.5163 | -124.5163 | -124.6582
274.7812 | 124.8734 | -62.3245 | 62.3154 | -0.015869 | 0.06677 | 0.057336 | 0.0081839 | -0.0045459 | 0.066917 | 0.069199 | 62.5214 | 62.178 | -62.2375 | 62.1918 | -62.2513 | -62.4207 | 5.1544 | -2.8885 | 62.2055 | -62.4252 | 0.086975 | -0.13733 | 124.8459 | 124.5163 | -124.5667 | -0.10071 | -0.10986 | 124.7589 | 67.4789 | 59.436 | 0.073242 | 124.5026 | 124.8459 | 124.53 | -0.09613 | -0.10071 | 124.5026 | 124.8459 | -0.09613 | 0.073242 | 124.53 | -124.5529 | -124.7406
275.7812 | 124.8138 | -62.3474 | 62.3474 | -0.00061033 | 0.064847 | 0.059045 | 0.0028433 | -0.0060413 | 0.066277 | 0.070908 | 62.4619 | 62.1826 | -62.2009 | 62.1368 | -62.2787 | -62.4573 | 5.4245 | -3.0121 | 62.2879 | -62.3978 | 0.14648 | -0.16479 | 124.8093 | 124.4843 | -124.6262 | -0.050354 | -0.059509 | 124.6628 | 67.7719 | 59.3353 | 0.068664 | 124.53 | 124.8093 | 124.6353 | -0.10986 | -0.050354 | 124.53 | 124.8093 | -0.10986 | 0.068664 | 124.6353 | -124.5483 | -124.7452
276.7812 | 124.7955 | -62.3383 | 62.3383 | -0.00061033 | 0.065275 | 0.058832 | 0.0002799 | -0.0049731 | 0.068199 | 0.070694 | 62.4802 | 62.1964 | -62.2192 | 62.1552 | -62.2696 | -62.4435 | 5.5801 | -3.067 | 62.2971 | -62.3749 | 0.11902 | -0.14191 | 124.8184 | 124.4934 | -124.6078 | -0.036621 | -0.041199 | 124.6994 | 67.9184 | 59.2712 | 0.068665 | 124.5346 | 124.8184 | 124.6353 | -0.10529 | -0.036621 | 124.5346 | 124.8184 | -0.10529 | 0.068665 | 124.6353 | -124.5575 | -124.7131
277.7969 | 124.8505 | -62.3474 | 62.3245 | -0.00061033 | 0.064634 | 0.05755 | 0.0032705 | -0.0032641 | 0.065422 | 0.070053 | 62.4985 | 62.1414 | -62.2375 | 62.1918 | -62.233 | -62.3932 | 5.6442 | -3.1128 | 62.2604 | -62.384 | 0.10986 | -0.18311 | 124.8459 | 124.5392 | -124.5575 | -0.036621 | -0.064087 | 124.736 | 67.9916 | 59.2346 | 0.11444 | 124.4888 | 124.8459 | 124.6078 | -0.045776 | -0.036621 | 124.4888 | 124.8459 | -0.045776 | 0.11444 | 124.6078 | -124.5621 | -124.7086
278.7812 | 124.8276 | -62.3383 | 62.3749 | -0.00061033 | 0.061429 | 0.056055 | -0.0029245 | -0.0041187 | 0.065849 | 0.069626 | 62.5305 | 62.1552 | -62.1735 | 62.1964 | -62.2192 | -62.384 | 5.8685 | -3.1677 | 62.2971 | -62.352 | 0.16479 | -0.21973 | 124.8688 | 124.5346 | -124.5941 | -0.013733 | -0.07782 | 124.704 | 68.2068 | 59.1705 | 0.11902 | 124.4934 | 124.8688 | 124.6353 | -0.045776 | -0.013733 | 124.4934 | 124.8688 | -0.045776 | 0.11902 | 124.6353 | -124.5483 | -124.7269
279.7969 | 124.9191 | -62.2696 | 62.3291 | -0.00061033 | 0.060148 | 0.060114 | -0.0031381 | -0.0062549 | 0.065208 | 0.068131 | 62.5168 | 62.146 | -62.1826 | 62.1964 | -62.1964 | -62.3383 | 5.8365 | -3.2455 | 62.2421 | -62.352 | 0.086975 | -0.18311 | 124.7864 | 124.4659 | -124.5255 | -0.082398 | -0.086976 | 124.6994 | 68.1061 | 59.024 | 0.073242 | 124.4156 | 124.7864 | 124.5117 | -0.068665 | -0.082398 | 124.4156 | 124.7864 | -0.068665 | 0.073242 | 124.5117 | -124.5117 | -124.6811
280.7812 | 124.8688 | -62.3016 | 62.3337 | -0.00061033 | 0.062497 | 0.057336 | 0.0002799 | -0.0062549 | 0.067345 | 0.068985 | 62.5763 | 62.1689 | -62.146 | 62.2055 | -62.1826 | -62.3611 | 6.134 | -3.2684 | 62.2513 | -62.3474 | 0.15564 | -0.16479 | 124.8779 | 124.5071 | -124.5163 | -0.045776 | -0.082397 | 124.7223 | 68.4357 | 59.0332 | 0.11902 | 124.4705 | 124.8779 | 124.5529 | -0.059509 | -0.045776 | 124.4705 | 124.8779 | -0.059509 | 0.11902 | 124.5529 | -124.4797 | -124.6811
281.7812 | 124.8596 | -62.3154 | 62.3428 | -0.0082398 | 0.066129 | 0.060968 | 0.0081839 | -0.0041187 | 0.065849 | 0.068131 | 62.5305 | 62.1964 | -62.2009 | 62.178 | -62.2467 | -62.3932 | 6.2805 | -3.3508 | 62.265 | -62.4115 | 0.11444 | -0.14648 | 124.8459 | 124.4934 | -124.5895 | -0.09613 | -0.077819 | 124.7314 | 68.5959 | 58.9645 | 0.068665 | 124.5117 | 124.8459 | 124.5804 | -0.077819 | -0.09613 | 124.5117 | 124.8459 | -0.077819 | 0.068665 | 124.5804 | -124.5438 | -124.7543
282.7812 | 124.8962 | -62.3062 | 62.3383 | 0.0070192 | 0.06207 | 0.059473 | -0.0012155 | -0.0060413 | 0.064781 | 0.066208 | 62.5717 | 62.114 | -62.1826 | 62.265 | -62.1506 | -62.3245 | 6.4774 | -3.3234 | 62.2696 | -62.3428 | 0.1236 | -0.2243 | 124.8779 | 124.5712 | -124.4888 | -0.036621 | -0.068665 | 124.7543 | 68.7836 | 58.9828 | 0.15564 | 124.4202 | 124.8779 | 124.5758 | -0.018311 | -0.036621 | 124.4202 | 124.8779 | -0.018311 | 0.15564 | 124.5758 | -124.5209 | -124.6811
283.7812 | 124.8459 | -62.3337 | 62.3611 | -0.00061033 | 0.065061 | 0.059473 | 0.0013479 | -0.0030505 | 0.064781 | 0.068772 | 62.4893 | 62.178 | -62.2192 | 62.146 | -62.2467 | -62.4252 | 6.7245 | -3.5065 | 62.2742 | -62.384 | 0.11444 | -0.1831 | 124.823 | 124.4797 | -124.6078 | -0.050354 | -0.086975 | 124.7086 | 69.0582 | 58.8272 | 0.086975 | 124.5117 | 124.823 | 124.6078 | -0.091553 | -0.050354 | 124.5117 | 124.823 | -0.091553 | 0.086975 | 124.6078 | -124.5804 | -124.7452
284.7812 | 124.8505 | -62.3245 | 62.3566 | 0.0070192 | 0.066343 | 0.060754 | 0.0041251 | -0.0041187 | 0.065422 | 0.067276 | 62.5076 | 62.1964 | -62.2192 | 62.1735 | -62.233 | -62.4069 | 6.8253 | -3.598 | 62.2787 | -62.3703 | 0.10529 | -0.16022 | 124.8322 | 124.498 | -124.5895 | -0.045776 | -0.077819 | 124.7269 | 69.1498 | 58.7265 | 0.091553 | 124.5209 | 124.8322 | 124.6033 | -0.082397 | -0.045776 | 124.5209 | 124.8322 | -0.082397 | 0.091553 | 124.6033 | -124.5758 | -124.7269
285.7812 | 124.8505 | -62.3154 | 62.352 | 0.0070192 | 0.060361 | 0.056696 | 0.0004935 | -0.0030505 | 0.065208 | 0.069413 | 62.5397 | 62.1323 | -62.1964 | 62.178 | -62.2055 | -62.3749 | 6.9992 | -3.6942 | 62.3016 | -62.3474 | 0.11902 | -0.21973 | 124.855 | 124.4934 | -124.5575 | -0.032043 | -0.050354 | 124.736 | 69.3146 | 58.6212 | 0.10986 | 124.4476 | 124.855 | 124.617 | -0.059509 | -0.032043 | 124.4476 | 124.855 | -0.059509 | 0.10986 | 124.617 | -124.5483 | -124.6994
286.7812 | 124.9283 | -62.2742 | 62.3428 | -0.0082398 | 0.060148 | 0.05755 | -0.0010019 | -0.0058277 | 0.063927 | 0.067063 | 62.5992 | 62.1277 | -62.1918 | 62.2421 | -62.1323 | -62.2879 | 6.9901 | -3.7079 | 62.2559 | -62.3245 | 0.082398 | -0.21515 | 124.8734 | 124.5163 | -124.4751 | -0.050354 | -0.086975 | 124.791 | 69.2642 | 58.5663 | 0.14191 | 124.4019 | 124.8734 | 124.53 | -0.013733 | -0.050354 | 124.4019 | 124.8734 | -0.013733 | 0.14191 | 124.53 | -124.5346 | -124.6674
287.7969 | 124.8459 | -62.3245 | 62.3566 | 0.0070192 | 0.060148 | 0.057977 | 0.0007071 | -0.0071093 | 0.065849 | 0.068772 | 62.5305 | 62.1323 | -62.2101 | 62.1826 | -62.2009 | -62.3566 | 7.0953 | -3.9413 | 62.265 | -62.3337 | 0.11444 | -0.2243 | 124.855 | 124.5071 | -124.5575 | -0.009155 | -0.091552 | 124.7406 | 69.4199 | 58.3832 | 0.1236 | 124.4568 | 124.855 | 124.5895 | -0.032043 | -0.009155 | 124.4568 | 124.855 | -0.032043 | 0.1236 | 124.5895 | -124.5666 | -124.6902
288.7812 | 124.8138 | -62.3291 | 62.3749 | -0.00061033 | 0.062284 | 0.056696 | 0.0002799 | -0.0064685 | 0.066917 | 0.068344 | 62.5031 | 62.1918 | -62.1872 | 62.146 | -62.233 | -62.3978 | 7.338 | -3.9413 | 62.3062 | -62.3749 | 0.14191 | -0.18311 | 124.8322 | 124.4751 | -124.6078 | -0.045776 | -0.068665 | 124.6902 | 69.6671 | 58.3878 | 0.096131 | 124.5209 | 124.8322 | 124.6353 | -0.068664 | -0.045776 | 124.5209 | 124.8322 | -0.068664 | 0.096131 | 124.6353 | -124.5621 | -124.7498
289.7969 | 124.8276 | -62.3383 | 62.352 | -0.0082398 | 0.065702 | 0.054773 | 0.0041251 | -0.0066821 | 0.066704 | 0.070481 | 62.4435 | 62.1826 | -62.2375 | 62.059 | -62.3062 | -62.4619 | 7.2739 | -4.2389 | 62.2559 | -62.4252 | 0.10071 | -0.16937 | 124.7818 | 124.3973 | -124.6582 | -0.086975 | -0.096131 | 124.6811 | 69.6121 | 58.0994 | 0.032044 | 124.5209 | 124.7818 | 124.5941 | -0.1236 | -0.086975 | 124.5209 | 124.7818 | -0.1236 | 0.032044 | 124.5941 | -124.5895 | -124.7772
290.7812 | 124.9374 | -62.2742 | 62.3474 | -0.0082398 | 0.059934 | 0.059686 | -0.0003611 | -0.0054003 | 0.066063 | 0.068558 | 62.5992 | 62.1048 | -62.1735 | 62.2467 | -62.1323 | -62.2833 | 7.2876 | -4.01 | 62.2742 | -62.2971 | 0.10071 | -0.24262 | 124.8734 | 124.5209 | -124.4797 | -0.022888 | -0.073242 | 124.7726 | 69.5618 | 58.2642 | 0.14191 | 124.379 | 124.8734 | 124.5483 | -0.009155 | -0.022888 | 124.379 | 124.8734 | -0.009155 | 0.14191 | 124.5483 | -124.5209 | -124.6445
291.7812 | 124.9557 | -62.2604 | 62.3016 | -0.015869 | 0.063566 | 0.057336 | 0.0026297 | -0.0039051 | 0.067985 | 0.067917 | 62.558 | 62.146 | -62.1918 | 62.1689 | -62.1964 | -62.3337 | 7.283 | -4.1794 | 62.2147 | -62.3978 | 0.068665 | -0.15564 | 124.8184 | 124.4293 | -124.498 | -0.13733 | -0.086975 | 124.7498 | 69.5435 | 58.0811 | 0.064087 | 124.4064 | 124.8184 | 124.4751 | -0.073242 | -0.13733 | 124.4064 | 124.8184 | -0.073242 | 0.064087 | 124.4751 | -124.4934 | -124.6994
292.7812 | 124.8184 | -62.3016 | 62.3566 | -0.0082398 | 0.061002 | 0.058405 | 0.0011343 | -0.0075367 | 0.066063 | 0.068985 | 62.5259 | 62.1506 | -62.2055 | 62.1414 | -62.2192 | -62.3932 | 7.6538 | -4.3671 | 62.2787 | -62.3703 | 0.096131 | -0.20599 | 124.8276 | 124.4431 | -124.5758 | -0.068664 | -0.077819 | 124.7314 | 69.9554 | 57.9346 | 0.082398 | 124.4522 | 124.8276 | 124.5804 | -0.091552 | -0.068664 | 124.4522 | 124.8276 | -0.091552 | 0.082398 | 124.5804 | -124.5621 | -124.7269
293.7812 | 124.9557 | -62.2604 | 62.3016 | -0.00061033 | 0.060148 | 0.056268 | -0.0012155 | -0.0068957 | 0.065636 | 0.067276 | 62.5854 | 62.1002 | -62.178 | 62.2238 | -62.1323 | -62.2742 | 7.5439 | -4.3991 | 62.2467 | -62.3199 | 0.082397 | -0.20142 | 124.8459 | 124.4843 | -124.4339 | -0.059509 | -0.054932 | 124.7635 | 69.8044 | 57.8613 | 0.12817 | 124.3607 | 124.8459 | 124.5071 | -0.013733 | -0.059509 | 124.3607 | 124.8459 | -0.013733 | 0.12817 | 124.5071 | -124.4797 | -124.6216
294.7812 | 124.9374 | -62.2971 | 62.3199 | -0.0082398 | 0.061002 | 0.056909 | 0.0009207 | -0.0086047 | 0.066277 | 0.068772 | 62.5763 | 62.1277 | -62.1689 | 62.2192 | -62.1414 | -62.2696 | 7.6721 | -4.4174 | 62.2467 | -62.3245 | 0.12817 | -0.19226 | 124.8734 | 124.5163 | -124.4614 | -0.027466 | -0.073242 | 124.7452 | 69.9692 | 57.8796 | 0.15564 | 124.4247 | 124.8734 | 124.5438 | 0.027466 | -0.027466 | 124.4247 | 124.8734 | 0.027466 | 0.15564 | 124.5438 | -124.4888 | -124.6445
295.7812 | 124.9466 | -62.2787 | 62.3383 | -0.0082398 | 0.060361 | 0.054559 | -0.0003611 | -0.0083911 | 0.066277 | 0.069199 | 62.5992 | 62.1368 | -62.1552 | 62.2284 | -62.1323 | -62.2879 | 7.9285 | -4.4907 | 62.2742 | -62.3199 | 0.1236 | -0.20142 | 124.8779 | 124.5071 | -124.4705 | -0.041198 | -0.064087 | 124.7543 | 70.2072 | 57.7881 | 0.14648 | 124.4156 | 124.8779 | 124.5529 | -0.009155 | -0.041198 | 124.4156 | 124.8779 | -0.009155 | 0.14648 | 124.5529 | -124.4934 | -124.6582
296.7812 | 124.942 | -62.2879 | 62.3474 | -0.0082398 | 0.058652 | 0.059686 | 0.0013479 | -0.0079639 | 0.065208 | 0.068985 | 62.5763 | 62.1094 | -62.146 | 62.1918 | -62.1414 | -62.3062 | 8.1116 | -4.5456 | 62.2513 | -62.3062 | 0.14191 | -0.23804 | 124.8642 | 124.4797 | -124.4888 | -0.01831 | -0.09613 | 124.7223 | 70.3995 | 57.7423 | 0.14648 | 124.3973 | 124.8642 | 124.5392 | -0.01831 | -0.01831 | 124.3973 | 124.8642 | -0.01831 | 0.14648 | 124.5392 | -124.4934 | -124.6536
297.8281 | 124.7955 | -62.3199 | 62.3978 | -0.0082398 | 0.06442 | 0.055627 | 0.0032705 | -0.0073229 | 0.065849 | 0.067917 | 62.4664 | 62.1689 | -62.2009 | 62.0819 | -62.2559 | -62.4252 | 8.4229 | -4.7379 | 62.2879 | -62.3383 | 0.11902 | -0.22888 | 124.7864 | 124.4019 | -124.6536 | -0.018311 | -0.10986 | 124.6674 | 70.7428 | 57.5821 | 0.064087 | 124.4888 | 124.7864 | 124.6078 | -0.10529 | -0.018311 | 124.4888 | 124.7864 | -0.10529 | 0.064087 | 124.6078 | -124.5987 | -124.736
298.7812 | 124.9329 | -62.2742 | 62.3245 | 0.0070192 | 0.059293 | 0.056696 | -0.0003611 | -0.0081775 | 0.066917 | 0.067276 | 62.5488 | 62.1185 | -62.1368 | 62.178 | -62.1323 | -62.2833 | 8.1757 | -4.7241 | 62.265 | -62.3016 | 0.13733 | -0.20599 | 124.823 | 124.4522 | -124.4568 | -0.027466 | -0.059509 | 124.6857 | 70.4498 | 57.55 | 0.14191 | 124.3927 | 124.823 | 124.5392 | -0.009155 | -0.027466 | 124.3927 | 124.823 | -0.009155 | 0.14191 | 124.5392 | -124.4614 | -124.6262
299.7969 | 124.9283 | -62.2879 | 62.2879 | -0.00061033 | 0.063779 | 0.059686 | 0.0017753 | -0.0068957 | 0.068626 | 0.067276 | 62.5626 | 62.1094 | -62.1689 | 62.1414 | -62.1826 | -62.3154 | 7.8873 | -5.0903 | 62.1826 | -62.3657 | 0.11902 | -0.17853 | 124.8505 | 124.4293 | -124.4705 | -0.07782 | -0.10529 | 124.7314 | 70.1752 | 57.1976 | 0.10529 | 124.3973 | 124.8505 | 124.4705 | -0.027466 | -0.07782 | 124.3973 | 124.8505 | -0.027466 | 0.10529 | 124.4705 | -124.4568 | -124.6536
300.7812 | 124.9054 | -62.2467 | 62.352 | -0.00061033 | 0.060789 | 0.059686 | -0.0003611 | -0.0066821 | 0.069267 | 0.066849 | 62.5214 | 62.1277 | -62.178 | 62.1185 | -62.1689 | -62.3108 | 8.1161 | -5.1041 | 62.3016 | -62.2971 | 0.068664 | -0.2243 | 124.7681 | 124.3652 | -124.5209 | -0.050354 | -0.050354 | 124.6994 | 70.3629 | 57.1426 | 0.07782 | 124.3744 | 124.7681 | 124.5483 | -0.064087 | -0.050354 | 124.3744 | 124.7681 | -0.064087 | 0.07782 | 124.5483 | -124.53 | -124.649
301.7969 | 124.8138 | -62.2742 | 62.3795 | -0.00061033 | 0.067838 | 0.058832 | 0.0054069 | -0.0083911 | 0.066063 | 0.067917 | 62.4985 | 62.2009 | -62.1918 | 62.0728 | -62.2467 | -62.4115 | 8.2352 | -5.3696 | 62.3154 | -62.4023 | 0.082398 | -0.17853 | 124.7726 | 124.3469 | -124.6262 | -0.12817 | -0.064087 | 124.6902 | 70.5093 | 56.9046 | 0.027466 | 124.4751 | 124.7726 | 124.5895 | -0.13733 | -0.12817 | 124.4751 | 124.7726 | -0.13733 | 0.027466 | 124.5895 | -124.5712 | -124.7818
302.7812 | 124.9283 | -62.2467 | 62.352 | 0.0070192 | 0.057584 | 0.052637 | -0.0016427 | -0.0073229 | 0.066704 | 0.06984 | 62.5397 | 62.1185 | -62.1597 | 62.1506 | -62.146 | -62.2925 | 8.1161 | -5.4199 | 62.2833 | -62.2879 | 0.086975 | -0.23346 | 124.7864 | 124.3973 | -124.498 | -0.041199 | -0.068665 | 124.6994 | 70.3629 | 56.8268 | 0.10071 | 124.3652 | 124.7864 | 124.53 | -0.045776 | -0.041199 | 124.3652 | 124.7864 | -0.045776 | 0.10071 | 124.53 | -124.5117 | -124.6399
303.8281 | 124.8459 | -62.3108 | 62.352 | -0.00061033 | 0.06677 | 0.060968 | 0.0064749 | -0.0062549 | 0.067985 | 0.068985 | 62.5259 | 62.178 | -62.1872 | 62.0819 | -62.2101 | -62.3932 | 8.194 | -5.7083 | 62.2696 | -62.384 | 0.1236 | -0.17395 | 124.8367 | 124.3927 | -124.5621 | -0.073242 | -0.082398 | 124.7131 | 70.5048 | 56.6025 | 0.10071 | 124.4888 | 124.8367 | 124.5804 | -0.082397 | -0.073242 | 124.4888 | 124.8367 | -0.082397 | 0.10071 | 124.5804 | -124.5392 | -124.736
304.7812 | 124.9329 | -62.2284 | 62.3749 | -0.00061033 | 0.05673 | 0.060541 | -0.0016427 | -0.0068957 | 0.066277 | 0.068985 | 62.5671 | 62.178 | -62.1414 | 62.1643 | -62.1002 | -62.2604 | 8.139 | -5.7632 | 62.3108 | -62.2604 | 0.086976 | -0.19684 | 124.7955 | 124.3927 | -124.4751 | -0.032043 | -0.064087 | 124.7086 | 70.3674 | 56.4651 | 0.12817 | 124.4064 | 124.7955 | 124.5392 | -0.032043 | -0.032043 | 124.4064 | 124.7955 | -0.032043 | 0.12817 | 124.5392 | -124.5163 | -124.6353
305.7812 | 124.9512 | -62.233 | 62.3428 | -0.00061033 | 0.057798 | 0.057977 | 0.0002799 | -0.0088183 | 0.066704 | 0.068344 | 62.6038 | 62.1323 | -62.1414 | 62.1735 | -62.1048 | -62.2513 | 7.9697 | -5.9875 | 62.2833 | -62.265 | 0.091553 | -0.21057 | 124.8367 | 124.4064 | -124.4476 | -0.032044 | -0.059509 | 124.7452 | 70.2026 | 56.2454 | 0.12817 | 124.3652 | 124.8367 | 124.5163 | -0.018311 | -0.032044 | 124.3652 | 124.8367 | -0.018311 | 0.12817 | 124.5163 | -124.4843 | -124.6078
306.7812 | 124.8779 | -62.265 | 62.3383 | -0.00061033 | 0.059507 | 0.054773 | 0.0004935 | -0.0066821 | 0.064781 | 0.071335 | 62.5214 | 62.1323 | -62.1918 | 62.0773 | -62.2009 | -62.3291 | 8.02 | -6.3034 | 62.2421 | -62.3108 | 0.073243 | -0.20599 | 124.7864 | 124.3423 | -124.5392 | -0.045776 | -0.096131 | 124.7131 | 70.285 | 55.9616 | 0.064087 | 124.3973 | 124.7864 | 124.5071 | -0.064087 | -0.045776 | 124.3973 | 124.7864 | -0.064087 | 0.064087 | 124.5071 | -124.53 | -124.649
307.7969 | 124.9191 | -62.2559 | 62.2971 | -0.0082398 | 0.065275 | 0.060968 | 0.0041251 | -0.0068957 | 0.066277 | 0.070053 | 62.5626 | 62.1414 | -62.178 | 62.0865 | -62.1964 | -62.3108 | 7.9056 | -6.4407 | 62.2284 | -62.3474 | 0.077819 | -0.15564 | 124.8184 | 124.3423 | -124.4934 | -0.091553 | -0.068664 | 124.7406 | 70.1614 | 55.8151 | 0.059509 | 124.3973 | 124.8184 | 124.4843 | -0.054932 | -0.091553 | 124.3973 | 124.8184 | -0.054932 | 0.059509 | 124.4843 | -124.4751 | -124.6445
308.7812 | 124.8688 | -62.2604 | 62.3428 | -0.00061033 | 0.059293 | 0.059045 | -0.0007883 | -0.0068957 | 0.06414 | 0.069199 | 62.5488 | 62.1368 | -62.1552 | 62.0728 | -62.1826 | -62.3108 | 8.0154 | -6.5231 | 62.2787 | -62.3062 | 0.10529 | -0.20599 | 124.8093 | 124.3332 | -124.5255 | -0.045776 | -0.064086 | 124.704 | 70.2759 | 55.7373 | 0.07782 | 124.3973 | 124.8093 | 124.5392 | -0.050354 | -0.045776 | 124.3973 | 124.8093 | -0.050354 | 0.07782 | 124.5392 | -124.498 | -124.649
309.7812 | 124.9466 | -62.2421 | 62.3428 | 0.0070192 | 0.058225 | 0.059045 | 0.0022025 | -0.0075367 | 0.065849 | 0.069413 | 62.5946 | 62.1368 | -62.1231 | 62.1277 | -62.1094 | -62.2513 | 7.5439 | -6.958 | 62.2696 | -62.2925 | 0.11902 | -0.20599 | 124.8367 | 124.3698 | -124.4522 | -0.050354 | -0.073242 | 124.7177 | 69.7861 | 55.2841 | 0.13275 | 124.379 | 124.8367 | 124.5117 | -0.009156 | -0.050354 | 124.379 | 124.8367 | -0.009156 | 0.13275 | 124.5117 | -124.4659 | -124.6353
310.7812 | 124.8779 | -62.2513 | 62.3428 | 0.014648 | 0.060148 | 0.058405 | 0.0013479 | -0.0083911 | 0.066704 | 0.067917 | 62.558 | 62.1368 | -62.1506 | 62.0636 | -62.1735 | -62.3154 | 7.4478 | -7.283 | 62.2742 | -62.2925 | 0.10071 | -0.20599 | 124.8093 | 124.3149 | -124.5163 | -0.041198 | -0.068664 | 124.7086 | 69.6991 | 54.9683 | 0.07782 | 124.3881 | 124.8093 | 124.5255 | -0.064087 | -0.041198 | 124.3881 | 124.8093 | -0.064087 | 0.07782 | 124.5255 | -124.4934 | -124.6353
311.7812 | 124.9283 | -62.2192 | 62.3566 | -0.015869 | 0.060148 | 0.054987 | -0.0005747 | -0.0090319 | 0.066277 | 0.068558 | 62.6129 | 62.146 | -62.1185 | 62.1414 | -62.0911 | -62.233 | 7.2922 | -7.2281 | 62.2742 | -62.265 | 0.10071 | -0.21057 | 124.8322 | 124.3607 | -124.4476 | -0.045777 | -0.082397 | 124.7314 | 69.5114 | 54.9911 | 0.12817 | 124.3652 | 124.8322 | 124.4934 | -0.013733 | -0.045777 | 124.3652 | 124.8322 | -0.013733 | 0.12817 | 124.4934 | -124.4751 | -124.6216
312.7812 | 124.8871 | -62.2421 | 62.3428 | -0.0082398 | 0.060148 | 0.060114 | 0.0011343 | -0.0101 | 0.065849 | 0.070481 | 62.5717 | 62.114 | -62.1597 | 62.0407 | -62.1735 | -62.2971 | 7.3334 | -7.5623 | 62.2375 | -62.3245 | 0.082397 | -0.22888 | 124.8138 | 124.2828 | -124.5163 | -0.082398 | -0.10529 | 124.7314 | 69.5755 | 54.6799 | 0.068664 | 124.3561 | 124.8138 | 124.4797 | -0.054932 | -0.082398 | 124.3561 | 124.8138 | -0.054932 | 0.068664 | 124.4797 | -124.5026 | -124.6674
313.7812 | 124.8779 | -62.2604 | 62.3428 | -0.0082398 | 0.060575 | 0.059473 | 0.0017753 | -0.0092457 | 0.06649 | 0.069626 | 62.5168 | 62.1277 | -62.1918 | 61.9904 | -62.1964 | -62.3383 | 8.1436 | -7.0724 | 62.2375 | -62.3383 | 0.068665 | -0.21515 | 124.7772 | 124.2508 | -124.5392 | -0.07782 | -0.10529 | 124.7086 | 70.4041 | 55.188 | 0.064087 | 124.3881 | 124.7772 | 124.498 | -0.07782 | -0.07782 | 124.3881 | 124.7772 | -0.07782 | 0.064087 | 124.498 | -124.5346 | -124.6811
314.7812 | 124.8779 | -62.265 | 62.3383 | -0.00061033 | 0.05908 | 0.05755 | 0.0011343 | -0.0079639 | 0.064354 | 0.068344 | 62.5214 | 62.1048 | -62.1826 | 61.9812 | -62.1872 | -62.3291 | 8.2214 | -7.0541 | 62.2467 | -62.3199 | 0.082398 | -0.23346 | 124.7864 | 124.2462 | -124.5255 | -0.054931 | -0.091553 | 124.704 | 70.4865 | 55.2109 | 0.07782 | 124.3698 | 124.7864 | 124.5117 | -0.064087 | -0.054931 | 124.3698 | 124.7864 | -0.064087 | 0.07782 | 124.5117 | -124.5209 | -124.6582
315.7812 | 124.8734 | -62.2604 | 62.2971 | -0.00061033 | 0.058439 | 0.056909 | 0.0032705 | -0.0081775 | 0.064781 | 0.070694 | 62.5442 | 62.1094 | -62.1689 | 61.9949 | -62.1872 | -62.3291 | 7.8461 | -7.3654 | 62.2147 | -62.2833 | 0.091553 | -0.18768 | 124.8047 | 124.2554 | -124.4843 | -0.022888 | -0.082397 | 124.7131 | 70.1065 | 54.895 | 0.073242 | 124.3698 | 124.8047 | 124.4751 | -0.068665 | -0.022888 | 124.3698 | 124.8047 | -0.068665 | 0.073242 | 124.4751 | -124.4659 | -124.5804
316.7812 | 124.9008 | -62.2696 | 62.3199 | -0.00061033 | 0.05908 | 0.057977 | 0.0058341 | -0.0066821 | 0.065422 | 0.068558 | 62.5671 | 62.1002 | -62.1735 | 61.9995 | -62.178 | -62.2833 | 7.457 | -7.8735 | 62.2101 | -62.3428 | 0.09613 | -0.21973 | 124.8367 | 124.2691 | -124.498 | -0.073242 | -0.10986 | 124.7406 | 69.7266 | 54.3961 | 0.091552 | 124.3698 | 124.8367 | 124.4797 | -0.013733 | -0.073242 | 124.3698 | 124.8367 | -0.013733 | 0.091552 | 124.4797 | -124.4934 | -124.6628
317.7969 | 124.8138 | -62.265 | 62.3932 | 0.0070192 | 0.065915 | 0.057977 | 0.0071157 | -0.0073229 | 0.065208 | 0.068985 | 62.5122 | 62.2147 | -62.1826 | 61.9308 | -62.2101 | -62.3886 | 7.5394 | -8.1528 | 62.3199 | -62.3566 | 0.082398 | -0.17853 | 124.7772 | 124.1959 | -124.6033 | -0.091552 | -0.073242 | 124.6948 | 69.8044 | 54.1122 | 0.054932 | 124.4797 | 124.7772 | 124.585 | -0.1236 | -0.091552 | 124.4797 | 124.7772 | -0.1236 | 0.054932 | 124.585 | -124.5758 | -124.7498
318.7812 | 124.9191 | -62.2467 | 62.3154 | -0.00061033 | 0.060148 | 0.059473 | 0.0024161 | -0.0039051 | 0.066063 | 0.070481 | 62.5992 | 62.146 | -62.1552 | 62.0087 | -62.1185 | -62.2971 | 7.132 | -8.4 | 62.2375 | -62.3016 | 0.091553 | -0.16937 | 124.8459 | 124.2554 | -124.4339 | -0.054932 | -0.07782 | 124.7543 | 69.3787 | 53.8467 | 0.12817 | 124.3927 | 124.8459 | 124.4843 | -0.050354 | -0.054932 | 124.3927 | 124.8459 | -0.050354 | 0.12817 | 124.4843 | -124.4705 | -124.617
319.7812 | 124.9283 | -62.1964 | 62.3474 | 0.0070192 | 0.061857 | 0.060327 | 0.0028433 | -0.0062549 | 0.066917 | 0.068558 | 62.5946 | 62.1552 | -62.1323 | 61.9949 | -62.1094 | -62.2375 | 6.8573 | -8.7021 | 62.2513 | -62.2833 | 0.064087 | -0.19226 | 124.791 | 124.1913 | -124.4568 | -0.086975 | -0.09613 | 124.7269 | 69.0537 | 53.4943 | 0.086975 | 124.3515 | 124.791 | 124.4476 | -0.041199 | -0.086975 | 124.3515 | 124.791 | -0.041199 | 0.086975 | 124.4476 | -124.4797 | -124.6307
320.7812 | 124.9237 | -62.2101 | 62.3703 | -0.00061033 | 0.062497 | 0.057977 | 0.0036979 | -0.0036915 | 0.064354 | 0.071762 | 62.6266 | 62.1597 | -62.1231 | 61.9995 | -62.1094 | -62.2375 | 6.8069 | -9.0958 | 62.2513 | -62.2833 | 0.086975 | -0.21057 | 124.8367 | 124.2096 | -124.4797 | -0.073242 | -0.11902 | 124.7498 | 69.017 | 53.1143 | 0.10071 | 124.3698 | 124.8367 | 124.4614 | -0.027466 | -0.073242 | 124.3698 | 124.8367 | -0.027466 | 0.10071 | 124.4614 | -124.4934 | -124.6536
321.7812 | 124.9283 | -62.178 | 62.4115 | -0.0082398 | 0.061643 | 0.060114 | 0.0030569 | -0.0043323 | 0.066917 | 0.068772 | 62.6175 | 62.2101 | -62.1094 | 61.972 | -62.0773 | -62.2284 | 6.7886 | -9.1324 | 62.3154 | -62.2513 | 0.068665 | -0.20142 | 124.7955 | 124.1501 | -124.4888 | -0.073242 | -0.09613 | 124.7269 | 68.9667 | 53.0457 | 0.10071 | 124.3881 | 124.7955 | 124.4934 | -0.050354 | -0.073242 | 124.3881 | 124.7955 | -0.050354 | 0.10071 | 124.4934 | -124.5209 | -124.6628
322.7812 | 124.8596 | -62.1597 | 62.4161 | -0.0082398 | 0.064206 | 0.061395 | 0.0032705 | -0.0032641 | 0.06649 | 0.068985 | 62.59 | 62.2559 | -62.0819 | 61.9125 | -62.1414 | -62.265 | 6.7978 | -9.5261 | 62.3611 | -62.2513 | 0.07782 | -0.16022 | 124.7498 | 124.0723 | -124.5575 | -0.091553 | -0.054932 | 124.6719 | 68.9575 | 52.6337 | 0.018311 | 124.4156 | 124.7498 | 124.5209 | -0.10529 | -0.091553 | 124.4156 | 124.7498 | -0.10529 | 0.018311 | 124.5209 | -124.498 | -124.6674
323.7812 | 124.8184 | -62.1414 | 62.4664 | -0.0082398 | 0.065488 | 0.060968 | 0.0066885 | -0.0039051 | 0.066277 | 0.06984 | 62.5992 | 62.3245 | -62.059 | 61.8759 | -62.146 | -62.265 | 6.7474 | -9.7687 | 62.4161 | -62.2375 | 0.082397 | -0.14191 | 124.7406 | 124.0173 | -124.6124 | -0.096131 | -0.050354 | 124.6582 | 68.8889 | 52.3727 | -0.004578 | 124.4659 | 124.7406 | 124.5575 | -0.1236 | -0.096131 | 124.4659 | 124.7406 | -0.1236 | -0.004578 | 124.5575 | -124.5255 | -124.704
324.7812 | 124.855 | -62.1002 | 62.4756 | -0.00061033 | 0.064847 | 0.063104 | 0.0039115 | -0.0024097 | 0.067985 | 0.069199 | 62.6541 | 62.3657 | -62.0407 | 61.8988 | -62.1002 | -62.2192 | 6.2988 | -10.0845 | 62.4344 | -62.1826 | 0.05951 | -0.10986 | 124.7543 | 123.999 | -124.5758 | -0.082397 | -0.041199 | 124.6948 | 68.399 | 52.0157 | 0 | 124.4659 | 124.7543 | 124.5346 | -0.11902 | -0.082397 | 124.4659 | 124.7543 | -0.11902 | 0 | 124.5346 | -124.5163 | -124.6582
325.7812 | 124.7955 | -62.0773 | 62.558 | -0.00061033 | 0.063566 | 0.058405 | 0.0056205 | -0.0015551 | 0.066704 | 0.070908 | 62.6587 | 62.384 | -62.0041 | 61.8896 | -62.0819 | -62.233 | 6.72 | -10.0845 | 62.4893 | -62.1735 | 0.073243 | -0.17395 | 124.736 | 123.967 | -124.6399 | -0.09613 | -0.068664 | 124.6628 | 68.7973 | 51.9928 | -0.004577 | 124.4614 | 124.736 | 124.5667 | -0.15564 | -0.09613 | 124.4614 | 124.736 | -0.15564 | -0.004577 | 124.5667 | -124.5621 | -124.7314
326.7812 | 124.7955 | -62.0773 | 62.5626 | -0.015869 | 0.067624 | 0.057977 | 0.0064749 | -0.0017687 | 0.066704 | 0.069413 | 62.7045 | 62.4069 | -61.9904 | 61.8805 | -62.0682 | -62.2238 | 6.9214 | -9.993 | 62.4985 | -62.1643 | 0.086976 | -0.15564 | 124.7818 | 123.9578 | -124.6307 | -0.086975 | -0.064087 | 124.6948 | 68.9987 | 52.0844 | 0.009156 | 124.4843 | 124.7818 | 124.5758 | -0.14648 | -0.086975 | 124.4843 | 124.7818 | -0.14648 | 0.009156 | 124.5758 | -124.5529 | -124.7269
327.7812 | 124.9008 | -61.9308 | 62.6129 | -0.00061033 | 0.060361 | 0.05755 | -0.0003611 | -0.0049731 | 0.067345 | 0.068131 | 62.8647 | 62.4069 | -61.8713 | 62.0819 | -61.8301 | -61.972 | 6.7154 | -9.7687 | 62.5626 | -61.9995 | 0.059509 | -0.20599 | 124.7955 | 124.0128 | -124.4431 | -0.068665 | -0.050354 | 124.736 | 68.6462 | 52.1622 | 0.10071 | 124.3378 | 124.7955 | 124.4934 | -0.041199 | -0.068665 | 124.3378 | 124.7955 | -0.041199 | 0.10071 | 124.4934 | -124.4843 | -124.6124
328.7812 | 124.8413 | -61.94 | 62.6587 | -0.015869 | 0.067197 | 0.060541 | 0.0047659 | -0.0024097 | 0.067131 | 0.068344 | 62.8784 | 62.5351 | -61.8759 | 62.0224 | -61.8805 | -62.0361 | 7.0175 | -9.8465 | 62.6083 | -62.0453 | 0.064086 | -0.1236 | 124.8184 | 123.9624 | -124.5392 | -0.10529 | -0.050354 | 124.7543 | 68.9575 | 52.0935 | 0.059509 | 124.4751 | 124.8184 | 124.5483 | -0.096131 | -0.10529 | 124.4751 | 124.8184 | -0.096131 | 0.059509 | 124.5483 | -124.5346 | -124.704
329.7812 | 124.8001 | -61.8896 | 62.7548 | -0.0082398 | 0.067624 | 0.055627 | 0.0034841 | -0.0028369 | 0.067131 | 0.068985 | 62.9105 | 62.6038 | -61.821 | 62.0316 | -61.8805 | -61.9995 | 7.3746 | -9.6039 | 62.6633 | -61.9812 | 0.068664 | -0.15106 | 124.8001 | 123.9212 | -124.6353 | -0.091553 | -0.091553 | 124.7314 | 69.2642 | 52.2858 | 0.009155 | 124.4934 | 124.8001 | 124.5529 | -0.10986 | -0.091553 | 124.4934 | 124.8001 | -0.10986 | 0.009155 | 124.5529 | -124.5758 | -124.736
330.7812 | 124.7681 | -61.8027 | 62.8235 | -0.00061033 | 0.063779 | 0.05755 | 0.0036979 | -0.0019825 | 0.066063 | 0.070694 | 62.9562 | 62.677 | -61.734 | 62.0224 | -61.821 | -61.9629 | 7.5119 | -9.5993 | 62.7777 | -61.8851 | 0.068664 | -0.14648 | 124.7589 | 123.8251 | -124.6445 | -0.082398 | -0.045776 | 124.6902 | 69.3146 | 52.2034 | -0.018311 | 124.4797 | 124.7589 | 124.5804 | -0.16022 | -0.082398 | 124.4797 | 124.7589 | -0.16022 | -0.018311 | 124.5804 | -124.5575 | -124.7086
331.7812 | 124.8413 | -61.6104 | 62.9929 | -0.00061033 | 0.065488 | 0.061182 | 0.0034841 | -0.0039051 | 0.067558 | 0.071122 | 63.1714 | 62.8418 | -61.5646 | 62.2787 | -61.5646 | -61.6928 | 7.8415 | -9.3201 | 62.9608 | -61.7065 | 0.045777 | -0.15106 | 124.7818 | 123.8892 | -124.5575 | -0.09613 | -0.032044 | 124.736 | 69.4519 | 52.2903 | 0.045777 | 124.4522 | 124.7818 | 124.5712 | -0.082397 | -0.09613 | 124.4522 | 124.7818 | -0.082397 | 0.045777 | 124.5712 | -124.5575 | -124.6994
332.7812 | 124.8413 | -61.5417 | 63.0707 | -0.00061033 | 0.067197 | 0.062036 | 0.0030569 | -0.0019825 | 0.065422 | 0.068344 | 63.2675 | 62.9379 | -61.4594 | 62.3245 | -61.4868 | -61.6196 | 8.2947 | -9.2102 | 63.0203 | -61.6425 | 0.082397 | -0.13275 | 124.8093 | 123.8663 | -124.5575 | -0.10071 | -0.050354 | 124.7269 | 69.8364 | 52.3315 | 0.054932 | 124.4797 | 124.8093 | 124.5621 | -0.07782 | -0.10071 | 124.4797 | 124.8093 | -0.07782 | 0.054932 | 124.5621 | -124.53 | -124.7131
333.7812 | 124.8276 | -61.5143 | 63.1348 | -0.0082398 | 0.065915 | 0.060754 | 0.0022025 | -0.0017687 | 0.067558 | 0.070267 | 63.2584 | 62.9791 | -61.4273 | 62.2971 | -61.4502 | -61.6104 | 8.313 | -9.5947 | 63.0707 | -61.6013 | 0.086975 | -0.15564 | 124.7726 | 123.8113 | -124.585 | -0.086975 | -0.064087 | 124.6857 | 69.8273 | 51.9196 | 0.064087 | 124.4934 | 124.7726 | 124.585 | -0.096131 | -0.086975 | 124.4934 | 124.7726 | -0.096131 | 0.064087 | 124.585 | -124.5621 | -124.736
334.7812 | 124.8093 | -61.3953 | 63.2401 | -0.0082398 | 0.065061 | 0.056055 | 0.0024161 | -0.0049731 | 0.065849 | 0.070694 | 63.3591 | 63.0844 | -61.3174 | 62.352 | -61.3678 | -61.5234 | 8.2535 | -9.9197 | 63.1714 | -61.496 | 0.07782 | -0.15564 | 124.7543 | 123.7473 | -124.6078 | -0.10071 | -0.068664 | 124.6765 | 69.6487 | 51.4755 | 0.027466 | 124.4797 | 124.7543 | 124.5667 | -0.12817 | -0.10071 | 124.4797 | 124.7543 | -0.12817 | 0.027466 | 124.5667 | -124.5575 | -124.736
335.7969 | 124.8871 | -61.3815 | 63.2263 | -0.0082398 | 0.059507 | 0.056055 | -0.0033517 | -0.0039051 | 0.067985 | 0.071122 | 63.4094 | 62.9974 | -61.29 | 62.3886 | -61.3037 | -61.409 | 8.2809 | -9.8648 | 63.1302 | -61.4456 | 0.091553 | -0.22888 | 124.791 | 123.7701 | -124.53 | -0.064087 | -0.09613 | 124.6994 | 69.6625 | 51.5167 | 0.07782 | 124.379 | 124.791 | 124.5117 | -0.027466 | -0.064087 | 124.379 | 124.791 | -0.027466 | 0.07782 | 124.5117 | -124.5163 | -124.6719
336.7812 | 124.7818 | -61.3403 | 63.2858 | -0.00061033 | 0.062925 | 0.057336 | 0.0017753 | -0.0071093 | 0.066917 | 0.067917 | 63.4003 | 63.1302 | -61.2488 | 62.3474 | -61.3129 | -61.4594 | 7.9147 | -10.6979 | 63.2538 | -61.4136 | 0.091553 | -0.15564 | 124.7406 | 123.6877 | -124.5987 | -0.073242 | -0.032044 | 124.649 | 69.2551 | 50.6424 | 0.027466 | 124.4705 | 124.7406 | 124.5941 | -0.11902 | -0.073242 | 124.4705 | 124.7406 | -0.11902 | 0.027466 | 124.5941 | -124.5346 | -124.6994
337.7969 | 124.9054 | -61.2946 | 63.2721 | -0.0082398 | 0.062711 | 0.060754 | 0.0004935 | -0.0043323 | 0.066704 | 0.06984 | 63.5193 | 63.0478 | -61.2122 | 62.4023 | -61.2259 | -61.3358 | 7.869 | -10.6659 | 63.1622 | -61.3953 | 0.082398 | -0.2243 | 124.8138 | 123.6969 | -124.498 | -0.10071 | -0.10986 | 124.7314 | 69.1635 | 50.6287 | 0.068665 | 124.3423 | 124.8138 | 124.4568 | -0.041198 | -0.10071 | 124.3423 | 124.8138 | -0.041198 | 0.068665 | 124.4568 | -124.4843 | -124.6674
338.7812 | 124.8322 | -61.2488 | 63.382 | -0.0082398 | 0.06442 | 0.059473 | 0.0039115 | -0.0047595 | 0.06649 | 0.070908 | 63.5284 | 63.2492 | -61.1298 | 62.3795 | -61.1938 | -61.3449 | 7.8644 | -11.0504 | 63.3545 | -61.3312 | 0.11902 | -0.13275 | 124.7772 | 123.6282 | -124.5758 | -0.082398 | -0.027466 | 124.6582 | 69.1132 | 50.1984 | 0.054931 | 124.498 | 124.7772 | 124.6033 | -0.096131 | -0.082398 | 124.498 | 124.7772 | -0.096131 | 0.054931 | 124.6033 | -124.5117 | -124.7131
339.7812 | 124.7818 | -61.171 | 63.4964 | 0.0070192 | 0.063566 | 0.05755 | 0.0011343 | -0.0051867 | 0.066704 | 0.069413 | 63.588 | 63.3087 | -61.0703 | 62.3932 | -61.1298 | -61.2808 | 7.3013 | -11.7462 | 63.446 | -61.2442 | 0.10071 | -0.18768 | 124.7589 | 123.5641 | -124.6262 | -0.073243 | -0.050354 | 124.6582 | 68.4723 | 49.4247 | 0.041198 | 124.4797 | 124.7589 | 124.617 | -0.10986 | -0.073243 | 124.4797 | 124.7589 | -0.10986 | 0.041198 | 124.617 | -124.5666 | -124.7406
340.7812 | 124.7772 | -61.1114 | 63.5513 | -0.0082398 | 0.064847 | 0.059473 | 0.0028433 | -0.0058277 | 0.066063 | 0.068558 | 63.6703 | 63.4003 | -61.0016 | 62.4069 | -61.0703 | -61.2167 | 7.5073 | -11.4944 | 63.5376 | -61.1664 | 0.10986 | -0.15106 | 124.7818 | 123.5184 | -124.6216 | -0.054932 | -0.013733 | 124.6719 | 68.6188 | 49.617 | 0.041199 | 124.5117 | 124.7818 | 124.649 | -0.10529 | -0.054932 | 124.5117 | 124.7818 | -0.10529 | 0.041199 | 124.649 | -124.5529 | -124.7177
341.7812 | 124.8001 | -61.3998 | 63.2401 | -0.015869 | 0.062711 | 0.053705 | 0.0022025 | -0.0056141 | 0.069908 | 0.070053 | 63.3774 | 63.0615 | -61.3083 | 62.0819 | -61.3541 | -61.496 | 6.1066 | -13.3301 | 63.1897 | -61.4639 | 0.091552 | -0.17853 | 124.7772 | 123.4818 | -124.5941 | -0.064087 | -0.050354 | 124.6857 | 67.5064 | 48.0698 | 0.045776 | 124.4614 | 124.7772 | 124.5895 | -0.096131 | -0.064087 | 124.4614 | 124.7772 | -0.096131 | 0.045776 | 124.5895 | -124.5483 | -124.704
342.7812 | 124.7772 | -61.3174 | 63.3362 | -0.00061033 | 0.065488 | 0.062463 | 0.0026297 | -0.0045459 | 0.067131 | 0.068131 | 63.4186 | 63.1622 | -61.2305 | 62.0819 | -61.29 | -61.4502 | 6.5964 | -13.0325 | 63.2446 | -61.4136 | 0.086975 | -0.17395 | 124.736 | 123.3994 | -124.6262 | -0.09613 | -0.091553 | 124.649 | 67.9138 | 48.2849 | 0.027466 | 124.4797 | 124.736 | 124.5621 | -0.13275 | -0.09613 | 124.4797 | 124.736 | -0.13275 | 0.027466 | 124.5621 | -124.5667 | -124.7498
343.7812 | 124.7955 | -61.3907 | 63.2675 | -0.015869 | 0.063138 | 0.058191 | 0.0028433 | -0.0060413 | 0.067345 | 0.069626 | 63.3682 | 63.0936 | -61.29 | 61.9812 | -61.3403 | -61.496 | 6.0699 | -13.7192 | 63.2034 | -61.4456 | 0.10071 | -0.17395 | 124.7589 | 123.3719 | -124.6078 | -0.054932 | -0.064087 | 124.6582 | 67.4606 | 47.6715 | 0.050354 | 124.4843 | 124.7589 | 124.5941 | -0.10529 | -0.054932 | 124.4843 | 124.7589 | -0.10529 | 0.050354 | 124.5941 | -124.5575 | -124.7131
344.7812 | 124.791 | -61.0794 | 63.588 | 0.014648 | 0.063779 | 0.059686 | 0.0026297 | -0.0064685 | 0.066704 | 0.070267 | 63.6841 | 63.3774 | -60.9695 | 62.2238 | -61.0336 | -61.1847 | 6.5735 | -13.1104 | 63.5147 | -61.1389 | 0.10986 | -0.21057 | 124.7635 | 123.3032 | -124.6216 | -0.059509 | -0.073243 | 124.6536 | 67.6529 | 47.9691 | 0.045777 | 124.4568 | 124.7635 | 124.5941 | -0.10528 | -0.059509 | 124.4568 | 124.7635 | -0.10528 | 0.045777 | 124.5941 | -124.5575 | -124.7269
345.7812 | 124.7864 | -60.9695 | 63.6703 | -0.0082398 | 0.065488 | 0.058191 | 0.0060477 | -0.0049731 | 0.064568 | 0.068558 | 63.8031 | 63.5147 | -60.8826 | 62.2467 | -60.9879 | -61.116 | 6.427 | -13.2706 | 63.588 | -61.0748 | 0.086975 | -0.15564 | 124.7726 | 123.2162 | -124.6582 | -0.10529 | -0.082397 | 124.6857 | 67.3965 | 47.699 | -0.018311 | 124.4843 | 124.7726 | 124.5575 | -0.14648 | -0.10529 | 124.4843 | 124.7726 | -0.14648 | -0.018311 | 124.5575 | -124.5529 | -124.7452
346.7812 | 124.7818 | -60.8734 | 63.7985 | -0.015869 | 0.063779 | 0.053918 | 0.0015615 | -0.0047595 | 0.065208 | 0.068558 | 63.8809 | 63.62 | -60.759 | 62.2925 | -60.8185 | -60.9695 | 6.2027 | -13.5406 | 63.7482 | -60.9283 | 0.11444 | -0.17853 | 124.7543 | 123.1659 | -124.617 | -0.054932 | -0.050354 | 124.6399 | 67.0761 | 47.3328 | 0.054932 | 124.4934 | 124.7543 | 124.6216 | -0.09613 | -0.054932 | 124.4934 | 124.7543 | -0.09613 | 0.054932 | 124.6216 | -124.5575 | -124.7269
347.7969 | 124.9237 | -60.7361 | 63.8077 | -0.00061033 | 0.064847 | 0.0599 | 0.0002799 | -0.0028369 | 0.065849 | 0.071335 | 64.0732 | 63.652 | -60.6537 | 62.3886 | -60.672 | -60.7819 | 5.4108 | -13.9984 | 63.7939 | -60.8139 | 0.082397 | -0.15564 | 124.8093 | 123.1247 | -124.4797 | -0.07782 | -0.013733 | 124.7269 | 66.1469 | 46.7377 | 0.064087 | 124.3881 | 124.8093 | 124.53 | -0.045776 | -0.07782 | 124.3881 | 124.8093 | -0.045776 | 0.064087 | 124.53 | -124.4614 | -124.6216
348.7812 | 124.91 | -60.6216 | 63.9908 | -0.0082398 | 0.060361 | 0.060968 | -0.0014291 | -0.0051867 | 0.066277 | 0.070053 | 64.2059 | 63.7527 | -60.5347 | 62.471 | -60.498 | -60.6171 | 5.3925 | -14.1083 | 63.8992 | -60.6628 | 0.086975 | -0.23804 | 124.8276 | 123.0927 | -124.4888 | -0.041199 | -0.091553 | 124.7406 | 66.0141 | 46.5134 | 0.1236 | 124.3744 | 124.8276 | 124.5209 | 0.004578 | -0.041199 | 124.3744 | 124.8276 | 0.004578 | 0.1236 | 124.5209 | -124.5255 | -124.6536
349.7812 | 124.855 | -60.5026 | 64.1418 | -0.0082398 | 0.062284 | 0.055841 | 0.0034841 | -0.0077503 | 0.063927 | 0.071762 | 64.3478 | 63.9084 | -60.379 | 62.5031 | -60.3973 | -60.5255 | 5.4108 | -14.2319 | 64.0411 | -60.5484 | 0.1236 | -0.23346 | 124.8505 | 123.0057 | -124.5392 | -0.045776 | -0.10071 | 124.7269 | 65.9134 | 46.2708 | 0.10529 | 124.411 | 124.8505 | 124.5438 | -0.022888 | -0.045776 | 124.411 | 124.8505 | -0.022888 | 0.10529 | 124.5438 | -124.5209 | -124.6902
350.7812 | 124.8047 | -60.91 | 63.7482 | -0.00061033 | 0.063138 | 0.057123 | 0.0015615 | -0.0064685 | 0.067985 | 0.070267 | 63.8901 | 63.5742 | -60.7956 | 61.9949 | -60.8368 | -60.9833 | 4.422 | -15.9348 | 63.7115 | -60.9421 | 0.11444 | -0.17395 | 124.8001 | 122.905 | -124.585 | -0.032044 | -0.036621 | 124.6857 | 65.332 | 44.9753 | 0.073242 | 124.4843 | 124.8001 | 124.6216 | -0.073242 | -0.032044 | 124.4843 | 124.8001 | -0.073242 | 0.073242 | 124.6216 | -124.5438 | -124.6902
351.7812 | 124.791 | -60.8734 | 63.8031 | -0.00061033 | 0.060575 | 0.056696 | 0.0011343 | -0.0045459 | 0.066917 | 0.068558 | 63.9359 | 63.5696 | -60.759 | 61.8988 | -60.7956 | -60.9467 | 3.2867 | -16.9052 | 63.739 | -60.9329 | 0.11444 | -0.23346 | 124.8093 | 122.7722 | -124.5987 | -0.059509 | -0.064087 | 124.6948 | 64.1602 | 43.9682 | 0.07782 | 124.4431 | 124.8093 | 124.6124 | -0.073242 | -0.059509 | 124.4431 | 124.8093 | -0.073242 | 0.07782 | 124.6124 | -124.5621 | -124.736
352.7812 | 124.7772 | -60.6125 | 64.0732 | -0.015869 | 0.062711 | 0.055841 | 0.0015615 | -0.0056141 | 0.064781 | 0.071335 | 64.1464 | 63.858 | -60.5347 | 62.0178 | -60.5713 | -60.7315 | 3.3371 | -16.7175 | 64.0091 | -60.6674 | 0.07782 | -0.21515 | 124.7589 | 122.6303 | -124.6445 | -0.054931 | -0.064087 | 124.6811 | 63.9496 | 43.895 | 0.041199 | 124.4705 | 124.7589 | 124.6216 | -0.11902 | -0.054931 | 124.4705 | 124.7589 | -0.11902 | 0.041199 | 124.6216 | -124.6078 | -124.7406
353.7812 | 124.823 | -60.379 | 64.2563 | -0.0082398 | 0.065275 | 0.056909 | 0.0051931 | -0.0032641 | 0.065636 | 0.07219 | 64.3845 | 64.0869 | -60.2921 | 62.1872 | -60.3424 | -60.4706 | 3.6438 | -15.9668 | 64.1739 | -60.4294 | 0.086975 | -0.16937 | 124.7635 | 122.5662 | -124.5987 | -0.050354 | -0.082398 | 124.6765 | 64.0228 | 44.4122 | 0.036621 | 124.4659 | 124.7635 | 124.5529 | -0.091553 | -0.050354 | 124.4659 | 124.7635 | -0.091553 | 0.036621 | 124.5529 | -124.5483 | -124.6857
354.7969 | 124.7772 | -60.2325 | 64.4485 | -0.00061033 | 0.064847 | 0.056909 | 0.0034841 | -0.0043323 | 0.066277 | 0.06984 | 64.5493 | 64.2838 | -60.1227 | 62.2238 | -60.1685 | -60.3149 | 3.6896 | -16.4474 | 64.3982 | -60.2737 | 0.10986 | -0.16479 | 124.7818 | 122.4564 | -124.617 | -0.041199 | -0.050354 | 124.6719 | 63.9221 | 43.7851 | 0.064087 | 124.5163 | 124.7818 | 124.6307 | -0.082397 | -0.041199 | 124.5163 | 124.7818 | -0.082397 | 0.064087 | 124.6307 | -124.5712 | -124.7223
355.7969 | 124.8459 | -59.9808 | 64.6362 | -0.0082398 | 0.062284 | 0.060541 | -0.0003611 | -0.0039051 | 0.067985 | 0.07219 | 64.8376 | 64.444 | -59.8892 | 62.384 | -59.8801 | -60.0266 | 3.7857 | -16.7862 | 64.5584 | -60.0769 | 0.091553 | -0.19226 | 124.8184 | 122.3648 | -124.5163 | -0.09613 | -0.077819 | 124.7269 | 63.7665 | 43.1946 | 0.10071 | 124.4247 | 124.8184 | 124.5392 | -0.045776 | -0.09613 | 124.4247 | 124.8184 | -0.045776 | 0.10071 | 124.5392 | -124.5255 | -124.7131
356.7812 | 124.8871 | -59.8343 | 64.7598 | -0.0082398 | 0.06207 | 0.053918 | -0.0001473 | -0.0066821 | 0.06649 | 0.072403 | 64.9841 | 64.5538 | -59.7427 | 62.439 | -59.7198 | -59.8434 | 3.2867 | -16.9968 | 64.6912 | -59.903 | 0.091553 | -0.20599 | 124.8184 | 122.2733 | -124.4797 | -0.068664 | -0.068665 | 124.7269 | 63.121 | 42.8375 | 0.11444 | 124.3881 | 124.8184 | 124.5255 | -0.009155 | -0.068664 | 124.3881 | 124.8184 | -0.009155 | 0.11444 | 124.5255 | -124.5026 | -124.6628
357.8125 | 124.8596 | -59.8709 | 64.7461 | -0.015869 | 0.058652 | 0.057764 | 0.0019889 | -0.0056141 | 0.065636 | 0.070694 | 64.9612 | 64.5218 | -59.7748 | 62.2742 | -59.7519 | -59.8892 | 3.598 | -16.9968 | 64.7003 | -59.8801 | 0.096131 | -0.2243 | 124.8322 | 122.1451 | -124.498 | -0.009155 | -0.045777 | 124.736 | 63.4689 | 42.8741 | 0.11902 | 124.3927 | 124.8322 | 124.5712 | -0.01831 | -0.009155 | 124.3927 | 124.8322 | -0.01831 | 0.11902 | 124.5712 | -124.5209 | -124.6262
358.7812 | 124.7772 | -59.9396 | 64.7552 | 0.0070192 | 0.065488 | 0.052637 | 0.0024161 | -0.0041187 | 0.068199 | 0.071976 | 64.8468 | 64.563 | -59.8068 | 62.0132 | -59.8572 | -59.9899 | 2.5726 | -18.1229 | 64.7003 | -59.9625 | 0.13275 | -0.19226 | 124.7864 | 121.9528 | -124.6124 | -0.022888 | -0.054932 | 124.6536 | 62.5122 | 41.8167 | 0.082397 | 124.5026 | 124.7864 | 124.6399 | -0.050354 | -0.022888 | 124.5026 | 124.7864 | -0.050354 | 0.082397 | 124.6399 | -124.5621 | -124.7177
359.7969 | 124.8093 | -59.935 | 64.7095 | -0.0082398 | 0.062497 | 0.058618 | 0.0047659 | -0.0043323 | 0.068413 | 0.072617 | 64.8331 | 64.5355 | -59.8434 | 61.8256 | -59.9167 | -60.0311 | 1.8311 | -19.0659 | 64.6317 | -60.0311 | 0.091553 | -0.17395 | 124.7681 | 121.7606 | -124.6262 | -0.09613 | -0.07782 | 124.6765 | 61.7661 | 40.8691 | 0.018311 | 124.4705 | 124.7681 | 124.5667 | -0.09613 | -0.09613 | 124.4705 | 124.7681 | -0.09613 | 0.018311 | 124.5667 | -124.5529 | -124.7406
360.7812 | 124.8917 | -60.3012 | 64.3341 | 0.0070192 | 0.061857 | 0.058618 | 0.0013479 | -0.0066821 | 0.066277 | 0.072617 | 64.5447 | 64.1373 | -60.2005 | 61.3449 | -60.173 | -60.2737 | 0.54932 | -20.137 | 64.2242 | -60.3241 | 0.10071 | -0.19684 | 124.8459 | 121.6461 | -124.5071 | -0.022889 | -0.10986 | 124.7452 | 60.8505 | 40.1642 | 0.12817 | 124.4385 | 124.8459 | 124.5255 | 0.027465 | -0.022889 | 124.4385 | 124.8459 | 0.027465 | 0.12817 | 124.5255 | -124.5346 | -124.6582
361.7812 | 124.7589 | -60.3058 | 64.3799 | -0.0082398 | 0.063779 | 0.059473 | 0.0011343 | -0.0043323 | 0.065636 | 0.071976 | 64.4943 | 64.2059 | -60.173 | 61.116 | -60.2188 | -60.3653 | 0.44403 | -20.4346 | 64.3662 | -60.3333 | 0.13275 | -0.17395 | 124.8001 | 121.4218 | -124.5987 | -0.027466 | -0.013733 | 124.6674 | 60.7498 | 39.8712 | 0.086975 | 124.5117 | 124.8001 | 124.6719 | -0.059509 | -0.027466 | 124.5117 | 124.8001 | -0.059509 | 0.086975 | 124.6719 | -124.5529 | -124.7131
362.7812 | 124.8093 | -60.1044 | 64.5447 | -0.00061033 | 0.063138 | 0.057764 | 0.0022025 | -0.0045459 | 0.066277 | 0.070694 | 64.7186 | 64.3707 | -59.9854 | 61.1755 | -59.9854 | -60.1318 | 0.018311 | -20.6268 | 64.4852 | -60.141 | 0.11902 | -0.17395 | 124.823 | 121.2799 | -124.53 | -0.036621 | -0.05951 | 124.704 | 60.1227 | 39.4775 | 0.11902 | 124.4751 | 124.823 | 124.5895 | -0.027466 | -0.036621 | 124.4751 | 124.823 | -0.027466 | 0.11902 | 124.5895 | -124.53 | -124.6857
363.7812 | 124.8138 | -59.9854 | 64.6866 | -0.0082398 | 0.065702 | 0.057977 | 0.0071157 | -0.0030505 | 0.063713 | 0.071335 | 64.8239 | 64.5172 | -59.8755 | 61.0565 | -59.9075 | -60.0311 | -0.27924 | -20.8374 | 64.6179 | -60.0494 | 0.10986 | -0.16937 | 124.8093 | 121.0419 | -124.5941 | -0.064086 | -0.068664 | 124.6994 | 59.7061 | 39.1479 | 0.07782 | 124.5026 | 124.8093 | 124.6033 | -0.045776 | -0.064086 | 124.5026 | 124.8093 | -0.045776 | 0.07782 | 124.6033 | -124.5621 | -124.736
364.7812 | 124.7772 | -59.6924 | 65.007 | -0.00061033 | 0.065061 | 0.059686 | 0.0030569 | -0.0028369 | 0.065208 | 0.072617 | 65.126 | 64.8376 | -59.5505 | 61.1206 | -59.6008 | -59.7473 | -0.35248 | -20.842 | 64.9384 | -59.7015 | 0.14191 | -0.16937 | 124.8184 | 120.813 | -124.6078 | -0.009155 | -0.068665 | 124.6765 | 59.3399 | 38.8504 | 0.091553 | 124.53 | 124.8184 | 124.6307 | -0.054931 | -0.009155 | 124.53 | 124.8184 | -0.054931 | 0.091553 | 124.6307 | -124.5575 | -124.7086
365.7812 | 124.7818 | -59.7015 | 64.9658 | -0.00061033 | 0.065061 | 0.059259 | 0.0024161 | -0.0034777 | 0.065208 | 0.071762 | 65.0711 | 64.801 | -59.5779 | 60.9604 | -59.6329 | -59.761 | -0.70953 | -21.5698 | 64.9063 | -59.7107 | 0.1236 | -0.16479 | 124.7726 | 120.6619 | -124.5987 | -0.009155 | -0.059509 | 124.649 | 58.992 | 38.1317 | 0.068664 | 124.5026 | 124.7726 | 124.6078 | -0.059509 | -0.009155 | 124.5026 | 124.7726 | -0.059509 | 0.068664 | 124.6078 | -124.5438 | -124.6765
366.7812 | 124.8001 | -59.404 | 65.2496 | -0.00061033 | 0.063138 | 0.058618 | 0.0009207 | -0.0047595 | 0.064781 | 0.071762 | 65.3961 | 65.0665 | -59.2667 | 60.9375 | -59.3262 | -59.4452 | -1.1124 | -21.7621 | 65.2084 | -59.4086 | 0.13733 | -0.18311 | 124.8001 | 120.3415 | -124.5758 | -0.004577 | -0.041199 | 124.6628 | 58.2916 | 37.6419 | 0.07782 | 124.4705 | 124.8001 | 124.6124 | -0.041198 | -0.004577 | 124.4705 | 124.8001 | -0.041198 | 0.07782 | 124.6124 | -124.5163 | -124.6582
367.7969 | 124.8596 | -58.4244 | 66.1697 | 0.0070192 | 0.05908 | 0.056482 | -0.0005747 | -0.0047595 | 0.064995 | 0.073258 | 66.3849 | 65.9683 | -58.3237 | 61.4044 | -58.3237 | -58.4244 | -1.8951 | -22.4304 | 66.1194 | -58.4747 | 0.10071 | -0.20142 | 124.8093 | 119.8288 | -124.4934 | -0.050354 | -0.050354 | 124.7086 | 56.5292 | 35.994 | 0.10071 | 124.3927 | 124.8093 | 124.5438 | 0 | -0.050354 | 124.3927 | 124.8093 | 0 | 0.10071 | 124.5438 | -124.4934 | -124.6445
368.7812 | 124.7864 | -58.7585 | 65.9088 | -0.00061033 | 0.063138 | 0.056696 | 0.0034841 | -0.0041187 | 0.065422 | 0.074326 | 66.0782 | 65.6891 | -58.6075 | 60.228 | -58.6533 | -58.754 | -2.3712 | -23.4879 | 65.8447 | -58.7585 | 0.15106 | -0.21973 | 124.8367 | 118.9865 | -124.5621 | 0 | -0.064086 | 124.6857 | 56.3873 | 35.2707 | 0.10529 | 124.4476 | 124.8367 | 124.6033 | 0.004578 | 0 | 124.4476 | 124.8367 | 0.004578 | 0.10529 | 124.6033 | -124.5163 | -124.6674
369.7812 | 124.8276 | -58.8867 | 65.7715 | -0.00061033 | 0.067624 | 0.057977 | 0.0060477 | 0.0005811 | 0.065422 | 0.074112 | 65.9363 | 65.6113 | -58.7814 | 59.5139 | -58.8043 | -58.9005 | -2.774 | -23.5703 | 65.6937 | -58.96 | 0.10529 | -0.16022 | 124.823 | 118.4006 | -124.5758 | -0.073242 | -0.077819 | 124.7177 | 56.1127 | 35.3165 | 0.082398 | 124.498 | 124.823 | 124.5804 | -0.013733 | -0.073242 | 124.498 | 124.823 | -0.013733 | 0.082398 | 124.5804 | -124.5529 | -124.7314
370.7812 | 124.8322 | -58.699 | 65.9592 | -0.0082398 | 0.063993 | 0.053278 | 0.0002799 | -0.0036915 | 0.064568 | 0.074967 | 66.1697 | 65.7669 | -58.5297 | 58.5617 | -58.58 | -58.6487 | -3.1998 | -23.909 | 65.918 | -58.7128 | 0.16937 | -0.19226 | 124.8688 | 117.2607 | -124.5392 | -0.013733 | -0.041198 | 124.6994 | 55.4993 | 34.79 | 0.11902 | 124.4659 | 124.8688 | 124.617 | 0.050354 | -0.013733 | 124.4659 | 124.8688 | 0.050354 | 0.11902 | 124.617 | -124.4888 | -124.6719
371.7812 | 124.8322 | -59.5413 | 65.0803 | 0.0070192 | 0.060361 | 0.061823 | 0.0015615 | -0.0007007 | 0.065636 | 0.078171 | 65.2954 | 64.8788 | -59.4223 | 55.1743 | -59.4177 | -59.4864 | -4.2068 | -25.2319 | 65.0208 | -59.5688 | 0.11902 | -0.20142 | 124.8367 | 114.7156 | -124.498 | -0.027466 | -0.059509 | 124.7177 | 55.3345 | 34.3094 | 0.1236 | 124.4202 | 124.8367 | 124.5621 | 0.054932 | -0.027466 | 124.4202 | 124.8367 | 0.054932 | 0.1236 | 124.5621 | -124.5026 | -124.649
372.7812 | 124.7864 | -58.699 | 65.9683 | -0.00061033 | 0.062925 | 0.055627 | 0.0049795 | -5.99e-05 | 0.064995 | 0.079026 | 66.0645 | 65.7806 | -58.5938 | 53.4668 | -58.6395 | -58.6441 | -3.685 | -24.1516 | 65.8813 | -58.7357 | 0.10529 | -0.18768 | 124.7635 | 112.1658 | -124.6078 | -0.036621 | -0.086975 | 124.6582 | 55.014 | 34.5474 | 0.05951 | 124.4797 | 124.7635 | 124.5804 | 0.054932 | -0.036621 | 124.4797 | 124.7635 | 0.054932 | 0.05951 | 124.5804 | -124.5621 | -124.704
373.7812 | 124.7726 | -57.5546 | 67.1173 | -0.00061033 | 0.064634 | 0.058191 | 0.0034841 | 0.0035717 | 0.065636 | 0.079666 | 67.2226 | 66.9388 | -57.431 | 52.1347 | -57.4905 | -57.4722 | -3.9597 | -24.2752 | 67.0853 | -57.5592 | 0.1236 | -0.17853 | 124.7772 | 109.6893 | -124.6079 | -0.004578 | -0.032044 | 124.6536 | 53.595 | 33.2794 | 0.064086 | 124.4934 | 124.7772 | 124.6399 | 0.082397 | -0.004578 | 124.4934 | 124.7772 | 0.082397 | 0.064086 | 124.6399 | -124.5483 | -124.6765
374.7812 | 124.8367 | -57.1518 | 67.4973 | -0.0082398 | 0.06677 | 0.058618 | 0.0079703 | 0.0048535 | 0.068413 | 0.080094 | 67.6529 | 67.3187 | -57.0419 | 49.9603 | -57.074 | -56.9275 | -3.4973 | -23.9502 | 67.4423 | -57.1884 | 0.10986 | -0.17853 | 124.8047 | 107.1121 | -124.5712 | -0.036622 | -0.054931 | 124.6948 | 53.6545 | 33.2016 | 0.077819 | 124.4705 | 124.8047 | 124.5941 | 0.2243 | -0.036622 | 124.4705 | 124.8047 | 0.2243 | 0.077819 | 124.5941 | -124.5392 | -124.6857
375.7812 | 124.7772 | -56.8817 | 67.7902 | 0.0070192 | 0.063779 | 0.060327 | 0.0022025 | 0.0046399 | 0.066917 | 0.083939 | 67.9184 | 67.5613 | -56.7719 | 48.0148 | -56.8039 | -56.7398 | -3.7994 | -23.9639 | 67.7307 | -56.8863 | 0.10986 | -0.22888 | 124.8001 | 104.8965 | -124.5941 | -0.004578 | -0.059509 | 124.6902 | 53.0823 | 32.9178 | 0.07782 | 124.4431 | 124.8001 | 124.6124 | 0.14191 | -0.004578 | 124.4431 | 124.8001 | 0.14191 | 0.07782 | 124.6124 | -124.5621 | -124.6765
376.7812 | 124.9008 | -55.7236 | 68.8705 | -0.0082398 | 0.062925 | 0.057336 | -0.0014291 | 0.0061353 | 0.06414 | 0.085221 | 69.1498 | 68.6691 | -55.5908 | 44.4168 | -55.5862 | -55.4214 | -4.4952 | -23.5428 | 68.8248 | -55.7144 | 0.13275 | -0.20142 | 124.8734 | 100.1404 | -124.4568 | 0.009155 | -0.045776 | 124.7406 | 51.2283 | 32.1808 | 0.13733 | 124.3927 | 124.8734 | 124.5483 | 0.30212 | 0.009155 | 124.3927 | 124.8734 | 0.30212 | 0.13733 | 124.5483 | -124.4614 | -124.585
377.7969 | 124.7726 | -60.2234 | 64.4302 | -0.00061033 | 0.062284 | 0.053278 | 0.0030569 | 0.015321 | 0.066917 | 0.095475 | 64.5584 | 64.238 | -60.1089 | 24.7238 | -60.1501 | -59.848 | -8.5098 | -27.3926 | 64.3478 | -60.2509 | 0.11444 | -0.19226 | 124.7818 | 84.9472 | -124.5804 | -0.027465 | -0.082398 | 124.6674 | 51.7136 | 32.8308 | 0.073243 | 124.4614 | 124.7818 | 124.5712 | 0.37537 | -0.027465 | 124.4614 | 124.7818 | 0.37537 | 0.073243 | 124.5712 | -124.5392 | -124.6811
378.7812 | 124.7543 | -61.0886 | 63.5834 | -0.015869 | 0.065061 | 0.055841 | 0.0034841 | 0.013612 | 0.066063 | 0.096756 | 63.6978 | 63.414 | -60.9421 | 23.4009 | -61.0382 | -60.7864 | -8.9355 | -28.2303 | 63.4872 | -61.1481 | 0.14648 | -0.16937 | 124.7864 | 84.4894 | -124.6216 | -0.059509 | -0.09613 | 124.6399 | 52.153 | 32.8583 | 0.050354 | 124.5026 | 124.7864 | 124.5758 | 0.30212 | -0.059509 | 124.5026 | 124.7864 | 0.30212 | 0.050354 | 124.5758 | -124.5255 | -124.7314
379.7969 | 124.8917 | -59.3491 | 65.1901 | -0.015869 | 0.062925 | 0.058191 | 0.0015615 | 0.01938 | 0.066704 | 0.10017 | 65.4327 | 65.0162 | -59.2392 | 20.2744 | -59.23 | -58.8593 | -9.9747 | -28.3722 | 65.1489 | -59.3903 | 0.10986 | -0.17395 | 124.7818 | 79.6234 | -124.4202 | -0.041199 | -0.041199 | 124.6719 | 49.3744 | 30.9769 | 0.11902 | 124.3652 | 124.7818 | 124.498 | 0.48981 | -0.041199 | 124.3652 | 124.7818 | 0.48981 | 0.11902 | 124.498 | -124.4293 | -124.5804
380.7812 | 124.8184 | -59.0744 | 65.5197 | -0.0082398 | 0.065275 | 0.060968 | 0.0036979 | 0.018953 | 0.065422 | 0.10017 | 65.7303 | 65.3458 | -58.9462 | 18.782 | -58.9645 | -58.6166 | -10.1807 | -31.1188 | 65.4739 | -59.111 | 0.12817 | -0.17395 | 124.8047 | 77.8564 | -124.4843 | -0.036621 | -0.045776 | 124.6765 | 48.8937 | 27.9556 | 0.10986 | 124.4202 | 124.8047 | 124.5483 | 0.45776 | -0.036621 | 124.4202 | 124.8047 | 0.45776 | 0.10986 | 124.5483 | -124.4659 | -124.6307
381.7812 | 124.7818 | -55.7098 | 68.9713 | -0.00061033 | 0.06677 | 0.060754 | 0.0066885 | 0.021089 | 0.066063 | 0.10082 | 69.0582 | 68.7973 | -55.5908 | 19.1986 | -55.6503 | -55.2246 | -9.5261 | -30.6061 | 68.898 | -55.719 | 0.11902 | -0.17395 | 124.7681 | 74.9084 | -124.6216 | -0.009155 | -0.073242 | 124.649 | 46.1838 | 25.1038 | 0.059509 | 124.5071 | 124.7681 | 124.6078 | 0.48523 | -0.009155 | 124.5071 | 124.7681 | 0.48523 | 0.059509 | 124.6078 | -124.5621 | -124.6902
382.7812 | 124.7498 | -54.7073 | 69.9692 | 0.0070192 | 0.068265 | 0.058191 | 0.0032705 | 0.022157 | 0.063713 | 0.10616 | 70.0287 | 69.7357 | -54.6341 | 18.0496 | -54.6387 | -54.2038 | -9.5947 | -29.9377 | 69.9234 | -54.6982 | 0.073242 | -0.23346 | 124.736 | 72.757 | -124.6078 | 0.009155 | -0.045776 | 124.6628 | 45.1126 | 24.7696 | 0.068664 | 124.4431 | 124.736 | 124.6307 | 0.50354 | 0.009155 | 124.4431 | 124.736 | 0.50354 | 0.068664 | 124.6307 | -124.6033 | -124.6674
383.7812 | 124.7955 | -53.2883 | 71.3608 | 0.0070192 | 0.072751 | 0.059259 | 0.0083975 | 0.020448 | 0.065849 | 0.10786 | 71.4615 | 71.1914 | -53.1876 | 17.5369 | -53.2333 | -52.7206 | -10.1349 | -31.7184 | 71.2921 | -53.3203 | 0.10071 | -0.16937 | 124.7498 | 70.8252 | -124.5941 | -0.032043 | -0.068665 | 124.649 | 43.1534 | 21.5698 | 0.054932 | 124.4797 | 124.7498 | 124.5804 | 0.56763 | -0.032043 | 124.4797 | 124.7498 | 0.56763 | 0.054932 | 124.5804 | -124.5483 | -124.6811
384.7812 | 124.8596 | -51.8784 | 72.7249 | -0.00061033 | 0.06912 | 0.058191 | 0.0030569 | 0.023225 | 0.065208 | 0.11043 | 73.0865 | 72.6288 | -51.6266 | 16.4154 | -51.7639 | -51.2146 | -12.7991 | -29.8416 | 72.6837 | -51.8555 | 0.25177 | -0.096131 | 124.9649 | 68.2938 | -124.4888 | 0.022888 | -0.041199 | 124.7131 | 39.0793 | 22.0367 | 0.11444 | 124.5071 | 124.9649 | 124.5621 | 0.66376 | 0.022888 | 124.5071 | 124.9649 | 0.66376 | 0.11444 | 124.5621 | -124.3515 | -124.5804
385.7812 | 124.7589 | -57.2891 | 67.3462 | -0.0082398 | 0.073392 | 0.060114 | 0.0041251 | 0.023652 | 0.065208 | 0.10893 | 67.392 | 67.1219 | -57.2571 | 13.2706 | -57.2845 | -56.9321 | -15.8386 | -32.9178 | 67.2272 | -57.3944 | 0.032044 | -0.2243 | 124.6811 | 70.5597 | -124.6307 | -0.10529 | -0.11902 | 124.649 | 41.4505 | 24.3713 | 0.004578 | 124.411 | 124.6811 | 124.5163 | 0.35706 | -0.10529 | 124.411 | 124.6811 | 0.35706 | 0.004578 | 124.5163 | -124.6033 | -124.7406
386.7812 | 124.7406 | -60.498 | 64.2105 | -0.0082398 | 0.075742 | 0.058832 | 0.0041251 | 0.019807 | 0.067131 | 0.10658 | 64.3341 | 64.1785 | -60.2234 | 16.095 | -60.5438 | -60.1181 | -14.6164 | -35.5362 | 63.9999 | -60.5759 | 0.27466 | -0.032043 | 124.8322 | 76.593 | -124.7543 | -0.07782 | -0.21057 | 124.5575 | 45.8817 | 24.9619 | -0.045776 | 124.6765 | 124.8322 | 124.498 | 0.37994 | -0.07782 | 124.6765 | 124.8322 | 0.37994 | -0.045776 | 124.498 | -124.4339 | -124.7864
387.7969 | 124.7818 | -57.1243 | 67.5293 | -0.015869 | 0.084714 | 0.057764 | 0.0064749 | 0.023439 | 0.065849 | 0.12218 | 67.6987 | 67.3782 | -56.9687 | 14.4699 | -56.9916 | -56.5018 | -15.4312 | -34.4513 | 67.4881 | -57.1243 | 0.15564 | -0.15106 | 124.823 | 71.5942 | -124.5209 | 0 | -0.041199 | 124.6674 | 41.6931 | 22.673 | 0.13275 | 124.5026 | 124.823 | 124.6124 | 0.62256 | 0 | 124.5026 | 124.823 | 0.62256 | 0.13275 | 124.6124 | -124.498 | -124.6536
388.7812 | 124.791 | -48.7335 | 75.9384 | -0.0082398 | 0.18939 | 0.060114 | 0.0092521 | 0.031557 | 0.064781 | 0.23241 | 75.9979 | 75.705 | -48.6603 | 8.2489 | -48.6374 | -45.5795 | -15.3809 | -34.552 | 75.8331 | -48.7473 | 0.073243 | -0.23346 | 124.7314 | 56.9824 | -124.5758 | -0.013732 | -0.10529 | 124.6582 | 33.3527 | 14.1815 | 0.096131 | 124.4385 | 124.7314 | 124.5667 | 3.154 | -0.013732 | 124.4385 | 124.7314 | 3.154 | 0.096131 | 124.5667 | -124.5987 | -124.6857
389.7969 | 124.7681 | -40.3564 | 84.3384 | -0.0082398 | 0.22357 | 0.061395 | 0.0058341 | 0.040101 | 0.066063 | 0.27705 | 84.4482 | 84.1141 | -40.1962 | 2.7512 | -40.2649 | -36.969 | -12.2864 | -28.7521 | 84.2239 | -40.3656 | 0.16022 | -0.2243 | 124.8047 | 43.1076 | -124.6033 | -0.009156 | -0.11444 | 124.6445 | 28.0701 | 11.6043 | 0.091552 | 124.4705 | 124.8047 | 124.5804 | 3.3875 | -0.009156 | 124.4705 | 124.8047 | 3.3875 | 0.091552 | 124.5804 | -124.5346 | -124.704
390.7812 | 124.8093 | -69.3054 | 55.2979 | 0.0070192 | 0.22378 | 0.061395 | 0.0026297 | 0.015535 | 0.066917 | 0.25398 | 55.2567 | 54.9042 | -69.3741 | 17.4683 | -69.1956 | -68.2388 | -24.1928 | -51.2695 | 54.9866 | -69.5343 | -0.068664 | -0.39368 | 124.5621 | 86.7737 | -124.4934 | -0.22888 | -0.31128 | 124.6307 | 45.1126 | 18.0359 | 0.10986 | 124.2096 | 124.5621 | 124.292 | 1.0666 | -0.22888 | 124.2096 | 124.5621 | 1.0666 | 0.10986 | 124.292 | -124.6719 | -124.8322
391.7812 | 124.7314 | -59.111 | 65.5243 | -0.00061033 | 0.41263 | 0.060968 | 0.0077567 | 0.020448 | 0.066704 | 0.44347 | 65.4831 | 65.2954 | -59.0652 | 20.0775 | -58.2687 | -60.4248 | -18.6722 | -44.014 | 65.5701 | -59.0378 | 0.045776 | -0.22888 | 124.5941 | 79.1885 | -123.793 | 0.073242 | 0.045776 | 124.5483 | 40.4388 | 15.097 | 0.84229 | 124.4064 | 124.5941 | 124.6811 | -1.3138 | 0.073242 | 124.4064 | 124.5941 | -1.3138 | 0.84229 | 124.6811 | -124.5895 | -124.5621
392.7812 | 124.8276 | -47.9095 | 76.7212 | -0.00061033 | 0.31991 | 0.059473 | 0.0026297 | 0.027284 | 0.064781 | 0.36314 | 77.2064 | 76.7532 | -47.4335 | 18.6584 | -47.6807 | -42.897 | -7.3837 | -33.4351 | 76.6159 | -47.8729 | 0.47607 | 0.032044 | 125.116 | 66.568 | -124.4019 | 0.036621 | -0.10529 | 124.6399 | 40.5258 | 14.4745 | 0.22888 | 124.6628 | 125.116 | 124.5255 | 5.0125 | 0.036621 | 124.6628 | 125.116 | 5.0125 | 0.22888 | 124.5255 | -124.1547 | -124.5941
393.7812 | 124.7269 | -41.1484 | 83.6334 | -0.00061033 | 0.55255 | 0.058832 | 0.0073295 | 0.023866 | 0.067558 | 0.60155 | 83.6472 | 83.4869 | -40.8966 | 26.5457 | -41.011 | -30.4413 | -4.5136 | -28.7064 | 83.3038 | -41.2445 | 0.25177 | -0.14648 | 124.7955 | 67.6941 | -124.6445 | -0.096131 | -0.32959 | 124.5438 | 36.6348 | 12.442 | 0.13733 | 124.6353 | 124.7955 | 124.4522 | 10.7071 | -0.096131 | 124.6353 | 124.7955 | 10.7071 | 0.13733 | 124.4522 | -124.53 | -124.8779
394.7812 | 124.6948 | -44.9112 | 79.6463 | -0.0082398 | 1.0182 | 0.062677 | 0.0094657 | 0.028779 | 0.06649 | 1.0228 | 79.7562 | 79.39 | -44.7647 | 19.7617 | -44.3619 | -27.7039 | -5.9372 | -32.3959 | 79.5868 | -44.8288 | 0.14648 | -0.25635 | 124.6674 | 64.6729 | -124.0082 | 0.082398 | -0.059509 | 124.5209 | 38.974 | 12.5153 | 0.54932 | 124.3011 | 124.6674 | 124.498 | 17.2073 | 0.082398 | 124.3011 | 124.6674 | 17.2073 | 0.54932 | 124.498 | -124.411 | -124.4751
395.7812 | 124.585 | -47.9004 | 76.5839 | -0.00061033 | 2.3295 | 0.063318 | 0.0071157 | 0.026643 | 0.064781 | 2.4293 | 77.4673 | 77.2659 | -46.7834 | 23.2407 | -46.0556 | -19.6655 | -5.6946 | -33.3023 | 76.3962 | -47.8363 | 1.1169 | 0.68207 | 125.3677 | 71.1411 | -122.6395 | 0.064087 | -0.18768 | 124.2508 | 42.2058 | 14.5981 | 1.8448 | 125.1663 | 125.3677 | 124.2966 | 28.2349 | 0.064087 | 125.1663 | 125.3677 | 28.2349 | 1.8448 | 124.2966 | -123.3673 | -124.4202
396.7812 | 124.6216 | -49.5987 | 74.7253 | -0.0082398 | 1.754 | 0.060327 | 0.0017753 | 0.025789 | 0.064568 | 1.8139 | 74.556 | 74.3362 | -49.498 | 18.4845 | -48.7289 | -17.4179 | -1.9775 | -34.9869 | 74.7391 | -49.4247 | 0.10071 | -0.3891 | 124.1547 | 68.0832 | -123.4543 | 0.17395 | 0.013733 | 124.054 | 47.6212 | 14.6118 | 0.86975 | 123.9349 | 124.1547 | 124.3378 | 32.1808 | 0.17395 | 123.9349 | 124.1547 | 32.1808 | 0.86975 | 124.3378 | -124.2233 | -124.1501
397.7969 | 124.5712 | -46.0648 | 78.2593 | -0.00061033 | 2.3899 | 0.060327 | 0.0022025 | 0.026002 | 0.065208 | 2.4287 | 78.3005 | 77.8381 | -45.9595 | 17.3126 | -44.4763 | -10.8994 | -2.0462 | -34.9457 | 78.2089 | -45.8862 | 0.10528 | -0.42114 | 124.3652 | 63.3774 | -122.7356 | 0.17853 | -0.050354 | 124.2599 | 44.0186 | 11.1191 | 1.5884 | 123.9029 | 124.3652 | 124.2737 | 35.1654 | 0.17853 | 123.9029 | 124.3652 | 35.1654 | 1.5884 | 124.2737 | -124.2188 | -124.1455
398.7812 | 124.53 | -42.8375 | 81.4362 | -0.0082398 | 3.571 | 0.060541 | 0.0058341 | 0.035829 | 0.062859 | 3.6485 | 81.3034 | 80.9006 | -42.7551 | 3.5477 | -40.1367 | -1.4145 | -1.8631 | -32.9864 | 81.3171 | -42.5858 | 0.082397 | -0.53558 | 124.1409 | 46.3852 | -121.5729 | 0.25177 | -0.11902 | 124.0585 | 40.9744 | 9.8511 | 2.7008 | 123.7381 | 124.1409 | 124.1547 | 41.423 | 0.25177 | 123.7381 | 124.1409 | 41.423 | 2.7008 | 124.1547 | -124.1913 | -124.0219
399.7812 | 124.5346 | -38.9374 | 85.3912 | -0.0082398 | 1.958 | 0.060114 | 0.0056205 | 0.037538 | 0.068199 | 2.0397 | 85.4004 | 84.9976 | -38.8229 | 0.65918 | -37.8571 | -3.5522 | -1.7441 | -32.3502 | 85.1944 | -38.8412 | 0.11444 | -0.39368 | 124.3378 | 39.5966 | -123.2483 | 0.09613 | -0.19684 | 124.2233 | 37.1933 | 6.5872 | 1.0803 | 123.9349 | 124.3378 | 124.1318 | 35.3851 | 0.09613 | 123.9349 | 124.3378 | 35.3851 | 1.0803 | 124.1318 | -124.2142 | -124.2325
400.7812 | 124.5346 | -24.5682 | 99.9619 | -0.0082398 | 0.078519 | 0.056055 | 0.0094657 | 0.05591 | 0.06649 | 0.17281 | 99.9207 | 99.7147 | -24.4308 | -20.7001 | -24.5636 | -23.14 | -1.0437 | -22.261 | 99.8978 | -24.4858 | 0.13733 | -0.24719 | 124.4888 | 3.8681 | -124.5255 | 0.082397 | -0.064087 | 124.3515 | 23.5245 | 2.3071 | 0.004577 | 124.2828 | 124.4888 | 124.4659 | 1.4282 | 0.082397 | 124.2828 | 124.4888 | 1.4282 | 0.004577 | 124.4659 | -124.3927 | -124.4476
401.7812 | 124.5666 | -31.9427 | 92.3676 | -0.0082398 | 1.2528 | 0.057977 | 0.0071157 | 0.046937 | 0.065208 | 1.2807 | 91.5527 | 91.2735 | -32.7209 | -11.7233 | -30.6793 | -10.7025 | -1.2863 | -28.6743 | 92.601 | -31.7093 | -0.7782 | -1.0941 | 123.4955 | 20.2194 | -123.0469 | 0.23346 | 0.23346 | 124.2737 | 30.6564 | 3.2684 | 1.2634 | 123.2162 | 123.4955 | 124.5438 | 21.2402 | 0.23346 | 123.2162 | 123.4955 | 21.2402 | 1.2634 | 124.5438 | -125.0885 | -124.0768
402.7812 | 124.5987 | -37.6053 | 86.7554 | -0.0082398 | 2.0308 | 0.069299 | 0.0069021 | 0.036043 | 0.066063 | 2.1084 | 86.3342 | 85.7986 | -37.9303 | 4.6234 | -36.4426 | 1.181 | -1.5884 | -34.3048 | 86.4899 | -37.5458 | -0.32501 | -0.95673 | 123.9395 | 42.2287 | -123.1979 | 0.05951 | -0.2655 | 124.2645 | 36.0168 | 3.3005 | 1.1627 | 123.4039 | 123.9395 | 124.0952 | 38.7863 | 0.05951 | 123.4039 | 123.9395 | 38.7863 | 1.1627 | 124.0952 | -124.6857 | -124.3011
403.7969 | 124.4339 | -37.3398 | 87.0346 | -0.00061033 | 2.7133 | 0.069299 | 0.01267 | 0.034334 | 0.066917 | 2.7737 | 86.8515 | 86.618 | -37.2528 | 11.9568 | -35.6552 | 9.7824 | -2.0279 | -33.284 | 86.9797 | -37.1155 | 0.086975 | -0.41656 | 124.1913 | 49.2966 | -122.6898 | 0.2243 | -0.054932 | 124.1043 | 35.3119 | 4.0558 | 1.6846 | 123.9578 | 124.1913 | 124.3195 | 47.1222 | 0.2243 | 123.9578 | 124.1913 | 47.1222 | 1.6846 | 124.3195 | -124.2874 | -124.1501
404.7812 | 124.5438 | -27.7359 | 96.048 | -0.0082398 | 1.3173 | 0.066949 | 0.0073295 | 0.053987 | 0.063927 | 1.3689 | 98.8586 | 97.9523 | -25.6805 | -11.5494 | -25.6531 | -12.1811 | -1.8127 | -24.3896 | 97.7509 | -26.7105 | 2.0554 | 1.9043 | 126.5945 | 16.1865 | -121.701 | 1.0254 | 1.7029 | 124.5392 | 25.9232 | 3.3463 | 2.0828 | 125.6882 | 126.5945 | 125.4868 | 15.5548 | 1.0254 | 125.6882 | 126.5945 | 15.5548 | 2.0828 | 125.4868 | -121.7285 | -122.7585
405.7812 | 124.173 | -30.7526 | 93.2007 | 0.0070192 | 7.0076 | 5.358 | 0.0066885 | 0.040742 | 0.063713 | 1.9886 | 92.3996 | 91.8137 | -30.8304 | 1.9592 | -29.6127 | 0.59052 | -3.0441 | -27.3605 | 93.0771 | -30.6427 | -0.07782 | -1.387 | 123.1522 | 32.7118 | -122.8134 | 0.10986 | -0.1236 | 123.23 | 27.7084 | 3.392 | 1.1398 | 122.5662 | 123.1522 | 123.8297 | 31.3431 | 0.10986 | 122.5662 | 123.1522 | 31.3431 | 1.1398 | 123.8297 | -124.0311 | -123.8434
406.7812 | 123.912 | -27.6581 | 96.0388 | -0.00061033 | 0.33188 | 0.066309 | 0.069707 | 0.057619 | -0.00058736 | 0.42937 | 96.2082 | 95.8008 | -27.4384 | -22.348 | 95.7733 | -24.0921 | -2.5085 | -20.9839 | 96.0251 | -27.5253 | 0.21973 | -0.23804 | 123.8663 | 5.3101 | -0.2655 | 0.13275 | -0.013733 | 123.6465 | 25.1495 | 6.6742 | 123.4314 | 123.4589 | 123.8663 | 123.6832 | 3.566 | 0.13275 | 123.4589 | 123.8663 | 3.566 | 123.4314 | 123.6832 | -123.4772 | -123.5641
407.7969 | 121.5637 | -53.1326 | 68.8293 | 0.0070192 | 0.18683 | 0.080194 | 6.943 | 0.018098 | 0.015648 | 7.0028 | 69.191 | 68.8751 | -52.9678 | 27.2278 | 31.8649 | 26.152 | -3.9368 | -27.7496 | 63.4048 | -48.6694 | 0.16479 | 0.045776 | 122.3236 | 80.3604 | -36.9644 | 4.4632 | -5.4245 | 122.1588 | 49.1959 | 25.383 | 84.9976 | 122.0078 | 122.3236 | 116.5375 | 79.2847 | 4.4632 | 122.0078 | 122.3236 | 79.2847 | 84.9976 | 116.5375 | -121.7972 | -117.4988
408.7812 | 123.5641 | -47.8088 | 75.6317 | -0.015869 | 7.0076 | 6.1133 | 0.059881 | 0.022584 | -0.0025102 | 4.6277 | 74.9313 | 74.4003 | -47.3831 | 23.7625 | 75.5035 | -9.0134 | -6.221 | -32.2495 | 75.3204 | -47.7081 | 0.42572 | -1.2314 | 122.7402 | 71.5713 | -0.12817 | 0.10071 | -0.31128 | 122.3145 | 41.5878 | 15.5594 | 123.3124 | 122.2092 | 122.7402 | 123.1293 | 38.7955 | 0.10071 | 122.2092 | 122.7402 | 38.7955 | 123.3124 | 123.1293 | -123.0148 | -123.3398
409.7812 | 123.5046 | -81.7566 | 41.4322 | -0.00061033 | 0.10949 | 0.093225 | 0.079107 | -0.0013415 | 0.065636 | 0.15871 | 41.8808 | 41.3177 | -81.5506 | 37.3947 | -80.5984 | 34.6344 | -5.5573 | -23.259 | 41.3406 | -81.8436 | 0.20599 | -0.11444 | 123.6374 | 119.1513 | -122.0306 | -0.086975 | -0.091553 | 123.4314 | 76.1993 | 58.4976 | 1.1581 | 123.0743 | 123.6374 | 123.0972 | 116.391 | -0.086975 | 123.0743 | 123.6374 | 116.391 | 1.1581 | 123.0972 | -122.9828 | -123.2758
410.7812 | 124.0036 | -10.0616 | 113.7543 | -0.0082398 | 0.2492 | 1.0718 | 0.90818 | 0.0076307 | -0.0025102 | 0.09932 | 113.5162 | 113.0997 | -10.2264 | 85.9268 | 112.8067 | 86.6592 | 11.38 | 21.1945 | 113.6765 | -10.1074 | -0.16479 | -0.6546 | 123.5779 | 95.9885 | -0.94757 | -0.045776 | -0.077819 | 123.7427 | 21.4417 | 31.2561 | 122.8683 | 123.1613 | 123.5779 | 123.7381 | 96.7209 | -0.045776 | 123.1613 | 123.5779 | 96.7209 | 122.8683 | 123.7381 | -123.9807 | -123.8617
411.7812 | 124.0311 | -4.6555 | 119.3481 | -0.023499 | 4.6426 | 5.2005 | 0.81418 | -0.0002735 | 0.033165 | 0.24843 | 118.8034 | 118.3823 | -4.1702 | 106.7963 | 59.642 | 103.4775 | 37.1658 | 72.3312 | 119.0094 | -4.6005 | 0.48523 | -0.96588 | 123.4589 | 111.4517 | -59.7061 | 0.054932 | -0.33875 | 122.9736 | 41.8213 | 76.9867 | 64.2975 | 123.0377 | 123.4589 | 123.6649 | 108.1329 | 0.054932 | 123.0377 | 123.4589 | 108.1329 | 64.2975 | 123.6649 | -123.5184 | -123.9487
412.7812 | 124.1135 | -3.4607 | 120.4651 | 0.0070192 | 0.43442 | 1.0947 | 0.91971 | 0.0014355 | 0.00048064 | 0.35909 | 120.488 | 120.108 | -3.3325 | 106.6177 | 118.8126 | 105.7434 | 26.2619 | 31.0135 | 120.3827 | -3.2272 | 0.12817 | -0.35706 | 123.9487 | 110.0784 | -1.6525 | 0.23346 | -0.082398 | 123.8205 | 29.7226 | 34.4742 | 122.2733 | 123.5687 | 123.9487 | 123.8434 | 109.2041 | 0.23346 | 123.5687 | 123.9487 | 109.2041 | 122.2733 | 123.8434 | -123.7976 | -123.6923
413.7812 | 123.912 | -2.6093 | 121.1609 | -0.0082398 | 0.86316 | 0.8627 | 0.30555 | 0.03882 | 0.0038986 | 0.36229 | 121.1655 | 120.7901 | -2.4216 | 35.2707 | 115.9607 | 34.5428 | 26.8478 | 0.14648 | 121.0968 | -2.5085 | 0.18768 | -0.37079 | 123.7747 | 37.8799 | -5.2002 | 0.10071 | -0.064087 | 123.587 | 29.4571 | 2.7557 | 118.5699 | 123.3994 | 123.7747 | 123.7061 | 37.1521 | 0.10071 | 123.3994 | 123.7747 | 37.1521 | 118.5699 | 123.7061 | -123.5825 | -123.6694
414.7812 | 123.6511 | -2.8427 | 121.0236 | -0.0082398 | 1.1167 | 1.0003 | 0.7815 | 0.024934 | -0.0025102 | 0.79765 | 120.8908 | 120.6665 | -2.5909 | 64.8056 | 119.101 | 65.1123 | 57.9758 | 1.6708 | 120.9503 | -2.6138 | 0.25177 | -0.35706 | 123.7335 | 67.6483 | -1.9226 | 0.22888 | -0.073243 | 123.4818 | 60.8185 | 4.5135 | 121.9437 | 123.5092 | 123.7335 | 123.793 | 67.955 | 0.22888 | 123.5092 | 123.7335 | 67.955 | 121.9437 | 123.793 | -123.6145 | -123.6374
415.7812 | 123.6969 | -1.149 | 122.3694 | -0.00061033 | 0.78903 | 0.4927 | 0.027196 | 0.02643 | 0.064354 | 0.44197 | 122.3923 | 121.9894 | -1.0437 | 61.4914 | 2.2751 | 61.4731 | 54.9179 | 29.4983 | 122.3236 | -1.062 | 0.10529 | -0.37994 | 123.5413 | 62.6404 | -120.0943 | 0.086975 | -0.045777 | 123.436 | 56.0669 | 30.6473 | 3.4241 | 123.1384 | 123.5413 | 123.4726 | 62.6221 | 0.086975 | 123.1384 | 123.5413 | 62.6221 | 3.4241 | 123.4726 | -123.4131 | -123.4314
416.7812 | 123.7061 | -3.0716 | 120.5383 | 0.014648 | 1.5153 | 1.6418 | 0.17524 | 0.022584 | 0.0015488 | 0.077744 | 120.4376 | 120.0806 | -2.7832 | 69.5938 | 115.1871 | 98.2635 | 57.4539 | 46.0281 | 120.4651 | -3.0075 | 0.28839 | -0.45776 | 123.5092 | 72.6654 | -5.3513 | 0.064087 | -0.073242 | 123.2208 | 60.5255 | 49.0997 | 118.2587 | 123.1522 | 123.5092 | 123.5367 | 101.3351 | 0.064087 | 123.1522 | 123.5092 | 101.3351 | 118.2587 | 123.5367 | -123.3215 | -123.5458
417.7969 | 123.8342 | -5.1544 | 118.4143 | -0.00061033 | 0.14261 | 1.821 | 1.8355 | 0.0057081 | 0.0011214 | 0.11064 | 118.9545 | 118.2495 | -4.9255 | 101.9577 | 112.4313 | 117.1967 | 43.2083 | 96.1441 | 118.3731 | -5.0354 | 0.22888 | -0.16479 | 124.1089 | 107.1121 | -5.983 | 0.11902 | -0.041199 | 123.88 | 48.3627 | 101.2985 | 117.5858 | 123.4039 | 124.1089 | 123.5275 | 122.3511 | 0.11902 | 123.4039 | 124.1089 | 122.3511 | 117.5858 | 123.5275 | -123.3398 | -123.4497
418.7812 | 123.9029 | -0.91095 | 122.8958 | -0.00061033 | 0.19366 | 0.42819 | 0.31281 | 0.01703 | -0.0012284 | 0.10786 | 122.8958 | 122.5662 | -0.74158 | 77.9388 | 118.8583 | 122.9553 | 5.3055 | 66.6641 | 122.85 | -0.8194 | 0.16937 | -0.32959 | 123.8068 | 78.8498 | -4.0375 | 0.091553 | -0.045776 | 123.6374 | 6.2164 | 67.5751 | 119.7693 | 123.4772 | 123.8068 | 123.761 | 123.8663 | 0.091553 | 123.4772 | 123.8068 | 123.8663 | 119.7693 | 123.761 | -123.6374 | -123.7152
419.7812 | 123.7656 | -27.2964 | 96.4828 | -0.0082398 | 0.18854 | 1.2442 | 1.2856 | -0.0045459 | -0.0012284 | 0.19823 | 95.5261 | 95.9518 | -27.2964 | 95.4071 | 92.395 | 95.5353 | 44.7144 | 44.0414 | 96.1899 | -27.3148 | 0 | -0.53101 | 122.8226 | 122.7036 | -4.0878 | -0.01831 | -0.29297 | 122.8226 | 72.0108 | 71.3379 | 119.6915 | 123.2483 | 122.8226 | 123.4863 | 122.8317 | -0.01831 | 123.2483 | 122.8226 | 122.8317 | 119.6915 | 123.4863 | -123.7793 | -123.7976
420.7812 | 123.7106 | -29.0909 | 94.519 | 0.0070192 | 0.22592 | 1.5766 | 1.9671 | -0.0075367 | -0.0020828 | 0.65089 | 94.7617 | 94.3405 | -28.7018 | 93.5257 | 89.6301 | 93.9743 | 33.49 | 35.614 | 94.4183 | -28.8849 | 0.3891 | -0.17853 | 123.8525 | 122.6166 | -4.8889 | 0.20599 | -0.10071 | 123.4634 | 62.5809 | 64.7049 | 118.721 | 123.4314 | 123.8525 | 123.5092 | 123.0652 | 0.20599 | 123.4314 | 123.8525 | 123.0652 | 118.721 | 123.5092 | -123.2208 | -123.4039
421.7812 | 122.8363 | -33.8745 | 88.9709 | 0.0070192 | 0.3855 | 1.4294 | 1.0861 | -0.0064685 | 0.0096664 | 0.1006 | 88.9206 | 88.6139 | -33.577 | 88.559 | 67.7399 | 88.8062 | 6.2302 | 6.4774 | 88.6871 | -33.8745 | 0.29755 | -0.35705 | 122.7951 | 122.4335 | -21.2311 | 0 | -0.28381 | 122.4976 | 40.1047 | 40.3519 | 101.6144 | 122.4884 | 122.7951 | 122.5616 | 122.6807 | 0 | 122.4884 | 122.7951 | 122.6807 | 101.6144 | 122.5616 | -122.5479 | -122.8455
422.7812 | 123.3902 | -123.0972 | 0.16022 | -0.00061033 | 0.015287 | 0.0041444 | 0.12739 | -0.0051867 | -0.00080116 | 0.12132 | 0.19684 | 0.068665 | 0.17395 | 0.20599 | -0.42114 | 0.29297 | 0.009155 | 0.14648 | 0.054932 | -123.175 | 123.2712 | -0.091552 | 123.2941 | 123.3032 | -0.58136 | -0.07782 | -0.10528 | 0.022888 | 123.1064 | 123.2437 | 122.6761 | 123.1659 | 123.2941 | 123.1522 | 123.3902 | -0.07782 | 123.1659 | 123.2941 | 123.3902 | 122.6761 | 123.1522 | 0.013733 | -123.3353
423.7812 | 123.3948 | -123.1888 | 0.13275 | -0.015869 | 0.013364 | 0.0090576 | 0.012456 | -0.0058277 | -0.00058736 | 0.011734 | 0.16022 | 0.050354 | 0.16022 | 0.21057 | -0.62256 | 0.23804 | 0.082397 | 0.11444 | 0.064087 | -123.262 | 123.349 | -0.082397 | 123.349 | 123.3994 | -0.75531 | -0.073242 | -0.068664 | 0 | 123.2712 | 123.3032 | 122.5662 | 123.2391 | 123.349 | 123.2529 | 123.4268 | -0.073242 | 123.2391 | 123.349 | 123.4268 | 122.5662 | 123.2529 | 0.027466 | -123.3948
424.7812 | 123.6237 | -123.2574 | 0.1236 | -0.00061033 | 0.01251 | 0.0045716 | 0.012456 | -0.0071093 | -0.001442 | 0.014298 | 0.18768 | 0.036621 | 0.18768 | 0.23804 | -1.149 | 0.31128 | -0.022888 | 0.20142 | 0.041199 | -123.3398 | 123.4451 | -0.086975 | 123.4451 | 123.4955 | -1.2726 | -0.082398 | -0.082397 | 0 | 123.2346 | 123.4589 | 122.1085 | 123.2941 | 123.4451 | 123.2986 | 123.5687 | -0.082398 | 123.2941 | 123.4451 | 123.5687 | 122.1085 | 123.2986 | 0.064087 | -123.4634
425.7812 | 123.6786 | -123.317 | 0.1236 | -0.00061033 | 0.011228 | 0.0047852 | 0.042791 | -0.0083911 | -0.004219 | 0.043991 | 0.15106 | 0.054932 | 0.19226 | 0.20142 | -0.94757 | 0.2655 | -0.009155 | 0.1236 | 0.041199 | -123.4085 | 123.5092 | -0.068664 | 123.468 | 123.5184 | -1.0712 | -0.091552 | -0.082397 | -0.041199 | 123.3078 | 123.4406 | 122.3694 | 123.3719 | 123.468 | 123.3582 | 123.5825 | -0.091552 | 123.3719 | 123.468 | 123.5825 | 122.3694 | 123.3582 | 0.068665 | -123.5321
426.7812 | 123.6465 | -123.3719 | 0.1236 | 0.014648 | 0.011228 | 0.005426 | 0.040014 | -0.0098865 | -0.0012284 | 0.032669 | 0.14648 | 0.045776 | 0.20599 | 0.19684 | -0.63171 | 0.25635 | -0.018311 | 0.11902 | 0.041199 | -123.4543 | 123.5779 | -0.07782 | 123.5184 | 123.5687 | -0.75531 | -0.082398 | -0.082397 | -0.05951 | 123.3536 | 123.4909 | 122.7402 | 123.4177 | 123.5184 | 123.4131 | 123.6282 | -0.082398 | 123.4177 | 123.5184 | 123.6282 | 122.7402 | 123.4131 | 0.082398 | -123.5779
427.7969 | 123.7335 | -123.3536 | 0.10529 | -0.015869 | 0.016569 | 0.0090576 | 0.051763 | -0.0062549 | -0.0033646 | 0.042496 | 0.21973 | 0.041199 | 0.2243 | 0.25177 | -1.0254 | 0.31586 | -0.11444 | 0.16022 | 0.027466 | -123.5046 | 123.5779 | -0.064087 | 123.5733 | 123.6053 | -1.1307 | -0.15106 | -0.07782 | -0.004577 | 123.2391 | 123.5138 | 122.3282 | 123.3948 | 123.5733 | 123.381 | 123.6694 | -0.15106 | 123.3948 | 123.5733 | 123.6694 | 122.3282 | 123.381 | 0.11902 | -123.6099
428.7812 | 123.6053 | -123.1705 | 0.17853 | -0.0082398 | 0.019346 | 0.0056396 | 0.25406 | -0.0058277 | 0.026756 | 0.27962 | 0.25177 | 0.10071 | 0.25177 | 0.25177 | -47.5937 | 0.32501 | -0.032043 | 0.20142 | 0.073242 | -123.2666 | 123.4222 | -0.07782 | 123.4222 | 123.4222 | -47.7722 | -0.096131 | -0.10529 | 0 | 123.1384 | 123.3719 | 75.5768 | 123.2712 | 123.4222 | 123.2437 | 123.4955 | -0.096131 | 123.2712 | 123.4222 | 123.4955 | 75.5768 | 123.2437 | 0.073242 | -123.4451
429.7812 | 123.587 | -123.3627 | 0.1236 | 0.0070192 | 0.013364 | 0.0062806 | 0.057745 | -0.0047595 | -0.0037918 | 0.037583 | 0.09613 | 0.091553 | 0.16479 | 0.12817 | -0.22888 | 0.17395 | 0.059509 | 0.036621 | 0.050354 | -123.4909 | 123.5275 | -0.032043 | 123.4589 | 123.4909 | -0.35248 | -0.12817 | -0.073242 | -0.068665 | 123.4222 | 123.3994 | 123.1338 | 123.4543 | 123.4589 | 123.4131 | 123.5367 | -0.12817 | 123.4543 | 123.4589 | 123.5367 | 123.1338 | 123.4131 | 0.041199 | -123.6145
430.7812 | 123.6099 | -123.3307 | 0.11902 | -0.0082398 | 0.0093055 | 0.0047852 | 0.055181 | -0.0051867 | -0.0010148 | 0.044419 | 0.15564 | 0.032043 | 0.20142 | 0.17853 | -0.054932 | 0.25635 | -0.022888 | 0.10986 | 0.032043 | -123.436 | 123.5321 | -0.086976 | 123.4863 | 123.5092 | -0.17395 | -0.10529 | -0.086976 | -0.045776 | 123.3078 | 123.4406 | 123.2758 | 123.3627 | 123.4863 | 123.3627 | 123.587 | -0.10529 | 123.3627 | 123.4863 | 123.587 | 123.2758 | 123.3627 | 0.082397 | -123.555
431.7812 | 123.7427 | -123.3627 | 0.10986 | 0.0070192 | 0.0063147 | 0.0056396 | 0.092351 | -0.0051867 | -0.0027238 | 0.075608 | 0.18768 | 0.018311 | 0.22888 | 0.23346 | -0.27466 | 0.29297 | -0.091553 | 0.14191 | 0 | -123.4543 | 123.5916 | -0.091552 | 123.5504 | 123.5962 | -0.38452 | -0.091553 | -0.10986 | -0.041199 | 123.2712 | 123.5046 | 123.0881 | 123.381 | 123.5504 | 123.3627 | 123.6557 | -0.091553 | 123.381 | 123.5504 | 123.6557 | 123.0881 | 123.3627 | 0.11902 | -123.5641
432.7969 | 123.4772 | -123.2025 | 0.1236 | -0.0082398 | 0.016782 | 0.011621 | 0.047491 | -0.0030505 | -0.00058736 | 0.029038 | 0.11444 | 0.059509 | 0.1831 | 0.13275 | 0.045776 | 0.19226 | 0.018311 | 0.027466 | 0.027466 | -123.4314 | 123.3856 | -0.064087 | 123.317 | 123.3353 | -0.07782 | -0.22888 | -0.09613 | -0.068664 | 123.2208 | 123.23 | 123.2483 | 123.262 | 123.317 | 123.23 | 123.3948 | -0.22888 | 123.262 | 123.317 | 123.3948 | 123.2483 | 123.23 | 0.059509 | -123.555
433.7812 | 123.6008 | -123.2712 | 0.11444 | -0.00061033 | 0.010801 | 0.0099122 | 0.047063 | -0.0060413 | -0.00080116 | 0.039078 | 0.13733 | 0.009155 | 0.18768 | 0.16937 | 0.022888 | 0.26093 | -0.036621 | 0.10986 | 0.013733 | -123.4314 | 123.4589 | -0.10529 | 123.4085 | 123.4406 | -0.091553 | -0.16022 | -0.10071 | -0.050354 | 123.2346 | 123.381 | 123.2941 | 123.2803 | 123.4085 | 123.2849 | 123.5321 | -0.16022 | 123.2803 | 123.4085 | 123.5321 | 123.2941 | 123.2849 | 0.073242 | -123.5458
434.7812 | 123.6877 | -123.2895 | 0.14191 | -0.0082398 | 0.012937 | 0.0058534 | 0.2547 | -0.0071093 | -0.003151 | 0.25056 | 0.20142 | 0.054932 | 0.21973 | 0.21973 | -0.17395 | 0.29755 | -0.050354 | 0.16937 | 0.050354 | -123.3948 | 123.5092 | -0.086975 | 123.4909 | 123.5092 | -0.31586 | -0.10528 | -0.091553 | -0.018311 | 123.2391 | 123.4589 | 123.1155 | 123.3444 | 123.4909 | 123.3398 | 123.587 | -0.10528 | 123.3444 | 123.4909 | 123.587 | 123.1155 | 123.3398 | 0.07782 | -123.5367
435.7812 | 123.3307 | -122.9553 | 0.10071 | -0.0082398 | 0.014005 | 0.0064942 | 0.064367 | -0.0062549 | 0.00069424 | 0.05745 | 0.14191 | 0.036621 | 0.1831 | 0.19226 | -1.0529 | 0.26093 | -0.045776 | 0.14648 | 0.009155 | -123.1247 | 123.1384 | -0.064087 | 123.0972 | 123.1476 | -1.1536 | -0.16937 | -0.091553 | -0.041198 | 122.9095 | 123.1018 | 121.9025 | 122.9919 | 123.0972 | 122.9645 | 123.2162 | -0.16937 | 122.9919 | 123.0972 | 123.2162 | 121.9025 | 122.9645 | 0.082397 | -123.2254
436.7969 | 123.4497 | -123.2071 | 0.14191 | -0.00061033 | 0.017637 | 0.010553 | 0.13593 | -0.0071093 | 0.023338 | 0.15422 | 0.16937 | 0.045776 | 0.16022 | 0.18768 | -44.87 | 0.21057 | 0.059509 | 0.10071 | 0.036621 | -123.3353 | 123.3673 | -0.096131 | 123.3765 | 123.3948 | -45.0119 | -0.12817 | -0.10529 | 0.009156 | 123.2666 | 123.3078 | 78.3371 | 123.2529 | 123.3765 | 123.2437 | 123.4177 | -0.12817 | 123.2529 | 123.3765 | 123.4177 | 78.3371 | 123.2437 | 0.01831 | -123.4772
437.7812 | 123.5779 | -123.1338 | 0.19684 | -0.0082398 | 0.016141 | 0.0079896 | 0.55185 | -0.0054003 | 0.00048064 | 0.5443 | 0.32044 | 0.12817 | 0.27924 | 0.22888 | -6.8527 | 0.30212 | -0.13275 | 0.13733 | 0.064087 | -123.2071 | 123.4131 | -0.068664 | 123.4543 | 123.3627 | -7.0496 | -0.073242 | -0.13275 | 0.041199 | 123.0011 | 123.2712 | 116.2811 | 123.262 | 123.4543 | 123.1979 | 123.436 | -0.073242 | 123.262 | 123.4543 | 123.436 | 116.2811 | 123.1979 | 0.082398 | -123.4039
438.7812 | 123.6191 | -123.262 | 0.10529 | -0.00061033 | 0.01251 | 0.0094848 | 0.1355 | -0.0041187 | -0.0029374 | 0.11 | 0.16937 | 0.027466 | 0.18768 | 0.21973 | 0.018311 | 0.28839 | -0.091553 | 0.13733 | -0.004578 | -123.4039 | 123.4497 | -0.07782 | 123.4314 | 123.4818 | -0.086975 | -0.14191 | -0.10986 | -0.01831 | 123.1705 | 123.3994 | 123.2803 | 123.2895 | 123.4314 | 123.2574 | 123.5504 | -0.14191 | 123.2895 | 123.4314 | 123.5504 | 123.2803 | 123.2574 | 0.082397 | -123.5092
439.7812 | 123.6282 | -123.2346 | 0.10986 | -0.00061033 | 0.013364 | 0.0094848 | 0.22437 | -0.0058277 | -0.0033646 | 0.2151 | 0.2243 | 0.032043 | 0.21515 | 0.23346 | 0.073242 | 0.28381 | -0.1236 | 0.14648 | 0.022888 | -123.3856 | 123.4497 | -0.07782 | 123.4589 | 123.468 | -0.036621 | -0.15106 | -0.086975 | 0.009155 | 123.111 | 123.381 | 123.3078 | 123.2666 | 123.4589 | 123.2574 | 123.5184 | -0.15106 | 123.2666 | 123.4589 | 123.5184 | 123.3078 | 123.2574 | 0.10529 | -123.4955
440.7812 | 123.0789 | -122.8638 | 0.11444 | -0.00061033 | 0.020414 | 0.0067078 | 0.014379 | -0.0041187 | -0.0020828 | 0.00853 | 0.10529 | 0.036621 | 0.1236 | 0.11902 | 0.027466 | 0.16479 | 0.013733 | 0.027466 | 0.009155 | -123.0835 | 122.9874 | -0.07782 | 122.9691 | 122.9828 | -0.086975 | -0.21973 | -0.10529 | -0.01831 | 122.8775 | 122.8912 | 122.8912 | 122.9004 | 122.9691 | 122.8729 | 123.0286 | -0.21973 | 122.9004 | 122.9691 | 123.0286 | 122.8912 | 122.8729 | 0.009155 | -123.1979
441.7812 | 123.5413 | -123.2025 | 0.07782 | -0.00061033 | 0.010801 | 0.0067078 | 0.01502 | -0.0062549 | -0.0018692 | 0.014298 | 0.1236 | 0.004578 | 0.15106 | 0.16937 | 0.07782 | 0.25177 | -0.041199 | 0.13275 | -0.022888 | -123.3215 | 123.3536 | -0.073242 | 123.3261 | 123.3719 | 0 | -0.11902 | -0.10071 | -0.027466 | 123.1613 | 123.3353 | 123.2803 | 123.2071 | 123.3261 | 123.1796 | 123.4543 | -0.11902 | 123.2071 | 123.3261 | 123.4543 | 123.2803 | 123.1796 | 0.073242 | -123.3994
442.7812 | 123.4314 | -123.2437 | 0.11902 | 0.0070192 | 0.020414 | 0.011194 | 0.0445 | -0.0043323 | -0.0018692 | 0.035233 | 0.07782 | 0.045776 | 0.1236 | 0.086975 | -0.086975 | 0.16479 | 0.036621 | 0.013733 | 0 | -123.4268 | 123.3673 | -0.073243 | 123.3215 | 123.3307 | -0.20599 | -0.18311 | -0.11902 | -0.045776 | 123.2803 | 123.2574 | 123.1567 | 123.2895 | 123.3215 | 123.2437 | 123.4085 | -0.18311 | 123.2895 | 123.3215 | 123.4085 | 123.1567 | 123.2437 | 0.004577 | -123.5458
443.7812 | 123.587 | -123.23 | 0.15106 | -0.00061033 | 0.019559 | 0.0069214 | 0.23142 | -0.0043323 | -0.003151 | 0.24202 | 0.13275 | 0.082397 | 0.13275 | 0.1236 | -0.86517 | 0.19226 | -0.013733 | 0.027466 | 0.041199 | -123.3765 | 123.3627 | -0.068665 | 123.3627 | 123.3536 | -1.0162 | -0.14648 | -0.10986 | 0 | 123.2162 | 123.2574 | 122.3648 | 123.3124 | 123.3627 | 123.2712 | 123.4222 | -0.14648 | 123.3124 | 123.3627 | 123.4222 | 122.3648 | 123.2712 | -0.018311 | -123.5275
444.7812 | 123.587 | -123.1613 | 0.17395 | -0.00061033 | 0.022764 | 0.012048 | 0.36814 | -0.0036915 | -0.0012284 | 0.35524 | 0.19684 | 0.10986 | 0.17853 | 0.14648 | -1.355 | 0.22888 | -0.064087 | 0.082397 | 0.036621 | -123.3261 | 123.3398 | -0.064087 | 123.3582 | 123.3078 | -1.5289 | -0.16479 | -0.13733 | 0.01831 | 123.0972 | 123.2437 | 121.8063 | 123.2712 | 123.3582 | 123.1979 | 123.3902 | -0.16479 | 123.2712 | 123.3582 | 123.3902 | 121.8063 | 123.1979 | 0.004578 | -123.5001
445.7812 | 123.5092 | -123.3078 | 0.10071 | -0.00061033 | 0.019132 | 0.011194 | 0.137 | -0.0047595 | -0.0029374 | 0.085221 | 0.064087 | 0.041199 | 0.15106 | 0.10529 | -0.10986 | 0.17395 | 0 | 0.013733 | 0.009155 | -123.4726 | 123.4589 | -0.059509 | 123.3719 | 123.4131 | -0.21057 | -0.16479 | -0.091553 | -0.086975 | 123.3078 | 123.3215 | 123.1979 | 123.349 | 123.3719 | 123.317 | 123.4818 | -0.16479 | 123.349 | 123.3719 | 123.4818 | 123.1979 | 123.317 | 0.050354 | -123.5733
446.7812 | 123.2941 | -123.0286 | 0.050354 | 0.0070192 | 0.017637 | 0.003717 | 0.018224 | -0.0043323 | -0.0037918 | 0.02327 | 0.16022 | -0.032043 | 0.16022 | 0.19684 | 0.12817 | 0.28381 | -0.11902 | 0.15564 | -0.041199 | -123.1613 | 123.1888 | -0.082397 | 123.1888 | 123.2254 | 0.07782 | -0.13275 | -0.091553 | 0 | 122.9095 | 123.1842 | 123.1567 | 122.9965 | 123.1888 | 122.9874 | 123.3124 | -0.13275 | 122.9965 | 123.1888 | 123.3124 | 123.1567 | 122.9874 | 0.10986 | -123.2117
447.7969 | 123.4222 | -123.0881 | 0.054932 | 0.0070192 | 0.024045 | 0.010553 | 0.025915 | -0.0041187 | -0.0035782 | 0.029251 | 0.16479 | -0.013733 | 0.18768 | 0.20599 | 0.1236 | 0.27466 | -0.13733 | 0.13275 | -0.045776 | -123.2941 | 123.2758 | -0.068665 | 123.2529 | 123.2941 | 0.068664 | -0.20599 | -0.10071 | -0.022888 | 122.9507 | 123.2208 | 123.2117 | 123.0743 | 123.2529 | 123.0423 | 123.3627 | -0.20599 | 123.0743 | 123.2529 | 123.3627 | 123.2117 | 123.0423 | 0.13275 | -123.349
448.7812 | 123.3398 | -123.1659 | 0.09613 | 0.0070192 | 0.024686 | 0.0086304 | 0.026128 | -0.0047595 | -0.001442 | 0.025193 | 0.045776 | 0.027466 | 0.13733 | 0.059509 | -0.027466 | 0.12817 | 0.041199 | -0.018311 | 0 | -123.3765 | 123.3032 | -0.068664 | 123.2117 | 123.2254 | -0.1236 | -0.21057 | -0.09613 | -0.091553 | 123.2071 | 123.1476 | 123.1384 | 123.1934 | 123.2117 | 123.1659 | 123.2941 | -0.21057 | 123.1934 | 123.2117 | 123.2941 | 123.1384 | 123.1659 | 0.041199 | -123.4726
449.7812 | 123.5138 | -123.1567 | 0.068665 | -0.0082398 | 0.023832 | 0.0075622 | 0.037878 | -0.0030505 | -0.0035782 | 0.030747 | 0.15106 | 0.004578 | 0.17395 | 0.19684 | 0.036621 | 0.2655 | -0.11444 | 0.11902 | -0.036621 | -123.3536 | 123.3307 | -0.064087 | 123.3078 | 123.3536 | -0.032044 | -0.19684 | -0.10529 | -0.022888 | 123.0423 | 123.2758 | 123.1934 | 123.1613 | 123.3078 | 123.1201 | 123.4222 | -0.19684 | 123.1613 | 123.3078 | 123.4222 | 123.1934 | 123.1201 | 0.10528 | -123.4222
450.7812 | 123.4177 | -123.2208 | 0.11444 | -0.0082398 | 0.026182 | 0.0058534 | 0.098547 | -0.0054003 | -0.0035782 | 0.1226 | 0.045776 | 0.032043 | 0.15106 | 0.064087 | -0.6134 | 0.1236 | 0.032043 | -0.041199 | 0.022888 | -123.4039 | 123.3719 | -0.082398 | 123.2666 | 123.2849 | -0.72784 | -0.18311 | -0.091553 | -0.10529 | 123.2529 | 123.1796 | 122.6074 | 123.2529 | 123.2666 | 123.2437 | 123.3444 | -0.18311 | 123.2529 | 123.2666 | 123.3444 | 122.6074 | 123.2437 | 0.036621 | -123.5184
451.7812 | 123.5458 | -123.1888 | 0.064087 | -0.015869 | 0.023832 | 0.0096986 | 0.030828 | -0.0045459 | -0.0020828 | 0.034592 | 0.16479 | -0.022888 | 0.17853 | 0.19684 | 0.073242 | 0.29297 | -0.12817 | 0.13733 | -0.027466 | -123.4177 | 123.3673 | -0.086975 | 123.3536 | 123.3856 | 0.009155 | -0.22888 | -0.091553 | -0.013733 | 123.0606 | 123.3261 | 123.262 | 123.1659 | 123.3536 | 123.1613 | 123.4818 | -0.22888 | 123.1659 | 123.3536 | 123.4818 | 123.262 | 123.1613 | 0.11444 | -123.4818
452.7812 | 123.4726 | -123.2803 | 0.082397 | -0.00061033 | 0.023618 | 0.0052124 | 0.030828 | -0.0043323 | -0.0033646 | 0.040787 | 0.059509 | 0.022888 | 0.13733 | 0.09613 | -0.036621 | 0.16937 | 0.054932 | 0.045776 | 0 | -123.4818 | 123.4177 | -0.059509 | 123.3398 | 123.3765 | -0.11902 | -0.20142 | -0.082397 | -0.07782 | 123.3353 | 123.3261 | 123.2437 | 123.3032 | 123.3398 | 123.2803 | 123.4497 | -0.20142 | 123.3032 | 123.3398 | 123.4497 | 123.2437 | 123.2803 | 0.054932 | -123.5641
453.7812 | 123.5138 | -123.2346 | 0.10071 | -0.00061033 | 0.03259 | 0.0056396 | 0.20814 | -0.0030505 | -0.0027238 | 0.22002 | 0.12817 | 0.036621 | 0.16937 | 0.11902 | -0.10071 | 0.15564 | 0.009155 | 0.045776 | 0.018311 | -123.4314 | 123.4039 | -0.064087 | 123.3627 | 123.3536 | -0.20142 | -0.19684 | -0.082397 | -0.041199 | 123.2437 | 123.2803 | 123.1339 | 123.2712 | 123.3627 | 123.2529 | 123.3902 | -0.19684 | 123.2712 | 123.3627 | 123.3902 | 123.1339 | 123.2529 | 0.068665 | -123.5321
454.7812 | 123.5367 | -123.262 | 0.09613 | -0.023499 | 0.029172 | 0.013971 | 0.13764 | -0.0036915 | -0.0046464 | 0.088852 | 0.11902 | 0.018311 | 0.16022 | 0.15106 | 0.004578 | 0.1831 | 0.004578 | 0.07782 | 0.036621 | -123.4543 | 123.4222 | -0.077819 | 123.381 | 123.4131 | -0.091552 | -0.19226 | -0.059509 | -0.041198 | 123.2666 | 123.3398 | 123.2666 | 123.2803 | 123.381 | 123.2986 | 123.4451 | -0.19226 | 123.2803 | 123.381 | 123.4451 | 123.2666 | 123.2986 | 0.064087 | -123.5504
455.7812 | 123.5184 | -123.2254 | 0.13275 | -0.00061033 | 0.034513 | 0.0082032 | 0.35767 | -0.0043323 | -0.0044328 | 0.37874 | 0.15106 | 0.064087 | 0.19226 | 0.10529 | 0 | 0.16022 | -0.032043 | 0.036621 | 0.027466 | -123.3994 | 123.4177 | -0.068664 | 123.3765 | 123.3307 | -0.13275 | -0.17395 | -0.10529 | -0.041199 | 123.1934 | 123.262 | 123.2254 | 123.2895 | 123.3765 | 123.2529 | 123.3856 | -0.17395 | 123.2895 | 123.3765 | 123.3856 | 123.2254 | 123.2529 | 0.05951 | -123.5321
456.7969 | 123.5046 | -123.2666 | 0.073242 | -0.0082398 | 0.021055 | 0.0049988 | 0.036596 | -0.0051867 | -0.0010148 | 0.035874 | 0.10071 | -0.013733 | 0.16937 | 0.12817 | 0.073242 | 0.21973 | -0.050354 | 0.082397 | -0.027466 | -123.4772 | 123.436 | -0.086975 | 123.3673 | 123.3948 | 0 | -0.21057 | -0.10071 | -0.068665 | 123.2162 | 123.349 | 123.3398 | 123.2529 | 123.3673 | 123.2391 | 123.4863 | -0.21057 | 123.2529 | 123.3673 | 123.4863 | 123.3398 | 123.2391 | 0.096131 | -123.5504
457.7969 | 123.5092 | -123.3215 | 0.073242 | -0.015869 | 0.019987 | 0.0086304 | 0.039159 | -0.0036915 | -0.004219 | 0.040146 | 0.10529 | 0.018311 | 0.14191 | 0.14191 | 0.036621 | 0.1831 | 0.009155 | 0.068665 | 0.018311 | -123.4589 | 123.4634 | -0.054931 | 123.4268 | 123.4634 | -0.036621 | -0.13733 | -0.054931 | -0.036621 | 123.3307 | 123.3902 | 123.3582 | 123.3398 | 123.4268 | 123.3398 | 123.5046 | -0.13733 | 123.3398 | 123.4268 | 123.5046 | 123.3582 | 123.3398 | 0.068665 | -123.5321
458.7812 | 123.5504 | -123.2849 | 0.09613 | -0.0082398 | 0.025327 | 0.0073486 | 0.17225 | -0.0054003 | -0.0035782 | 0.18007 | 0.15106 | 0.032043 | 0.16937 | 0.11902 | 0.064087 | 0.17853 | -0.004578 | 0.045776 | 0.009155 | -123.3582 | 123.4543 | -0.064087 | 123.436 | 123.4039 | -0.032043 | -0.073242 | -0.086975 | -0.018311 | 123.2803 | 123.3307 | 123.349 | 123.317 | 123.436 | 123.2941 | 123.4634 | -0.073242 | 123.317 | 123.436 | 123.4634 | 123.349 | 123.2941 | 0.073243 | -123.4543
459.7812 | 123.5413 | -123.3307 | 0.09613 | -0.015869 | 0.020414 | 0.0052124 | 0.037878 | -0.0049731 | -0.0063554 | 0.03032 | 0.07782 | 0.009155 | 0.13733 | 0.11902 | 0.041199 | 0.17395 | 0.059509 | 0.050354 | 0.009155 | -123.5092 | 123.468 | -0.086975 | 123.4085 | 123.4497 | -0.054931 | -0.17853 | -0.086975 | -0.059509 | 123.3902 | 123.381 | 123.3719 | 123.3398 | 123.4085 | 123.3398 | 123.5046 | -0.17853 | 123.3398 | 123.4085 | 123.5046 | 123.3719 | 123.3398 | 0.041199 | -123.6053
460.7812 | 123.6328 | -123.3353 | 0.10529 | -0.0082398 | 0.019559 | 0.010126 | 0.065008 | -0.0041187 | -0.003151 | 0.065567 | 0.064087 | 0.041199 | 0.13275 | 0.10071 | -0.004578 | 0.16937 | 0.086975 | 0.041199 | 0 | -123.4955 | 123.468 | -0.064087 | 123.3994 | 123.436 | -0.10986 | -0.16022 | -0.10529 | -0.068664 | 123.4222 | 123.3765 | 123.3307 | 123.3765 | 123.3994 | 123.3353 | 123.5046 | -0.16022 | 123.3765 | 123.3994 | 123.5046 | 123.3307 | 123.3353 | 0.027465 | -123.6008
461.7812 | 123.4955 | -123.349 | 0.10071 | -0.0082398 | 0.023404 | 0.006067 | 0.1073 | -0.0030505 | -0.0037918 | 0.11534 | 0.082397 | 0.054932 | 0.1236 | 0.091553 | 0.036621 | 0.15564 | 0.082397 | 0.045776 | 0.013733 | -123.4909 | 123.4726 | -0.045776 | 123.4314 | 123.4406 | -0.064087 | -0.14191 | -0.086975 | -0.041199 | 123.4314 | 123.3948 | 123.3856 | 123.4039 | 123.4314 | 123.3627 | 123.5046 | -0.14191 | 123.4039 | 123.4314 | 123.5046 | 123.3856 | 123.3627 | 0.022888 | -123.5916
462.7812 | 123.5733 | -123.3673 | 0.082397 | -0.0082398 | 0.024686 | 0.010126 | 0.11286 | -0.0043323 | -0.0018692 | 0.11064 | 0.1236 | 0.036621 | 0.14648 | 0.1236 | 0.027466 | 0.17395 | 0.018311 | 0.073242 | 0.009155 | -123.5184 | 123.5138 | -0.045776 | 123.4909 | 123.4909 | -0.054931 | -0.15106 | -0.073242 | -0.022888 | 123.3856 | 123.4406 | 123.3948 | 123.4039 | 123.4909 | 123.3765 | 123.5413 | -0.15106 | 123.4039 | 123.4909 | 123.5413 | 123.3948 | 123.3765 | 0.064087 | -123.6008
463.7812 | 122.8729 | -122.6395 | 0.082397 | -0.015869 | 0.031309 | 0.010553 | 0.0083975 | -0.0034777 | -0.0046464 | 0.00083956 | 0.11902 | 0.004578 | 0.15106 | 0.12817 | 0.073242 | 0.1831 | -0.022888 | 0.054932 | 0 | -122.8226 | 122.7905 | -0.077819 | 122.7585 | 122.7676 | -0.009155 | -0.18311 | -0.082397 | -0.032043 | 122.6166 | 122.6944 | 122.7127 | 122.644 | 122.7585 | 122.6395 | 122.8226 | -0.18311 | 122.644 | 122.7585 | 122.8226 | 122.7127 | 122.6395 | 0.068665 | -122.905
464.7812 | 123.056 | -122.8546 | 0.073242 | -0.0082398 | 0.028531 | 0.0075622 | 0.0069021 | -0.0019825 | -0.0040054 | 0.00041236 | 0.064087 | 0.004578 | 0.11444 | 0.09613 | -0.84686 | 0.14648 | 0.018311 | 0.032043 | -0.004578 | -123.0057 | 122.9691 | -0.068664 | 122.9187 | 122.9507 | -0.92011 | -0.15106 | -0.07782 | -0.050354 | 122.8729 | 122.8867 | 122.0078 | 122.8592 | 122.9187 | 122.85 | 123.0011 | -0.15106 | 122.8592 | 122.9187 | 123.0011 | 122.0078 | 122.85 | 0.041199 | -123.0789
465.7812 | 123.1247 | -122.9279 | 0.064087 | 0.0070192 | 0.03024 | 0.006067 | 0.0066885 | -0.0028369 | -0.0022964 | 0.0031894 | 0.073242 | 0.013733 | 0.10986 | 0.082397 | -0.10986 | 0.14648 | 0.022888 | 0.036621 | 0.004578 | -123.0972 | 123.0377 | -0.050354 | 123.0011 | 123.0103 | -0.17395 | -0.16937 | -0.059509 | -0.036621 | 122.9507 | 122.9645 | 122.818 | 122.9416 | 123.0011 | 122.9324 | 123.0743 | -0.16937 | 122.9416 | 123.0011 | 123.0743 | 122.818 | 122.9324 | 0.045776 | -123.1613
466.7812 | 123.175 | -122.9645 | 0.086975 | -0.0082398 | 0.031949 | 0.010126 | 0.012243 | -0.0028369 | -0.0025102 | 0.0076756 | 0.054932 | 0.018311 | 0.13733 | 0.073242 | -0.64545 | 0.11902 | 0.018311 | 0.009155 | -0.004578 | -123.1338 | 123.1018 | -0.068664 | 123.0194 | 123.0377 | -0.73242 | -0.16937 | -0.091553 | -0.082397 | 122.9828 | 122.9736 | 122.319 | 122.9828 | 123.0194 | 122.9599 | 123.0835 | -0.16937 | 122.9828 | 123.0194 | 123.0835 | 122.319 | 122.9599 | 0.050354 | -123.2208
467.7969 | 123.1796 | -123.0377 | 0.10071 | -0.00061033 | 0.031522 | 0.004358 | 0.014165 | -0.0026233 | -0.00080116 | 0.011734 | 0.032043 | 0.004578 | 0.1236 | 0.022888 | -2.0508 | 0.091553 | 0.027466 | -0.041199 | 0.009155 | -123.143 | 123.1613 | -0.09613 | 123.0698 | 123.0606 | -2.1515 | -0.10529 | -0.091553 | -0.091553 | 123.0652 | 122.9965 | 120.9869 | 123.0423 | 123.0698 | 123.0469 | 123.1293 | -0.10529 | 123.0423 | 123.0698 | 123.1293 | 120.9869 | 123.0469 | 0.022888 | -123.2437
468.7812 | 123.2071 | -123.0331 | 0.064087 | -0.00061033 | 0.033658 | 0.01098 | 0.010747 | -0.0036915 | 0.059013 | 0.073258 | 0.11444 | 0.004578 | 0.13275 | 0.10071 | -112.5366 | 0.15106 | -0.013733 | 0.036621 | 0 | -123.1979 | 123.1659 | -0.059509 | 123.1476 | 123.1338 | -112.6007 | -0.16479 | -0.064087 | -0.01831 | 123.0194 | 123.0698 | 10.4965 | 123.0377 | 123.1476 | 123.0331 | 123.1842 | -0.16479 | 123.0377 | 123.1476 | 123.1842 | 10.4965 | 123.0331 | 0.068664 | -123.262
469.7812 | 123.2574 | -123.0606 | 0.086975 | -0.00061033 | 0.032377 | 0.011408 | 0.011388 | -0.0036915 | 0.060509 | 0.075394 | 0.11902 | 0.013733 | 0.15564 | 0.10529 | -115.86 | 0.15564 | -0.009155 | 0.041199 | -0.018311 | -123.2162 | 123.2162 | -0.073242 | 123.1796 | 123.1659 | -115.947 | -0.15564 | -0.10529 | -0.036621 | 123.0515 | 123.1018 | 7.2006 | 123.0743 | 123.1796 | 123.0423 | 123.2162 | -0.15564 | 123.0743 | 123.1796 | 123.2162 | 7.2006 | 123.0423 | 0.068665 | -123.3032
470.7812 | 123.2986 | -123.0698 | 0.073242 | -0.00061033 | 0.037076 | 0.0064942 | 0.011602 | -0.0036915 | 0.064781 | 0.078171 | 0.09613 | 0.027466 | 0.15106 | 0.10071 | -115.6311 | 0.15106 | 0.013733 | 0.036621 | -0.018311 | -123.262 | 123.2208 | -0.045776 | 123.1659 | 123.1705 | -115.7043 | -0.19226 | -0.091553 | -0.054932 | 123.0835 | 123.1064 | 7.4387 | 123.0972 | 123.1659 | 123.0515 | 123.2208 | -0.19226 | 123.0972 | 123.1659 | 123.2208 | 7.4387 | 123.0515 | 0.07782 | -123.3353
471.7812 | 123.3536 | -123.0789 | 0.09613 | -0.0082398 | 0.037076 | 0.010553 | 0.011602 | -0.0032641 | 0.062645 | 0.082016 | 0.10529 | 0.032043 | 0.13733 | 0.11902 | -117.5812 | 0.15106 | -0.018311 | 0.054932 | -0.009155 | -123.2437 | 123.2162 | -0.064087 | 123.1842 | 123.1979 | -117.6773 | -0.16479 | -0.10528 | -0.032043 | 123.0606 | 123.1338 | 5.4977 | 123.111 | 123.1842 | 123.0698 | 123.23 | -0.16479 | 123.111 | 123.1842 | 123.23 | 5.4977 | 123.0698 | 0.041199 | -123.3398
472.7812 | 123.2437 | -123.1064 | 0.091553 | -0.0082398 | 0.040494 | 0.0069214 | 0.033819 | -0.0051867 | 0.064568 | 0.11214 | 0.07782 | 0.032043 | 0.16479 | 0.091553 | -117.8375 | 0.14648 | 0.004578 | 0.022888 | -0.009155 | -123.2712 | 123.2712 | -0.05951 | 123.1842 | 123.1979 | -117.9291 | -0.16479 | -0.10071 | -0.086975 | 123.111 | 123.1293 | 5.2689 | 123.1384 | 123.1842 | 123.0972 | 123.2529 | -0.16479 | 123.1384 | 123.1842 | 123.2529 | 5.2689 | 123.0972 | 0.073242 | -123.3627
473.7812 | 123.3078 | -123.0881 | 0.068665 | 0.0070192 | 0.034727 | 0.0082032 | 0.020361 | -0.0034777 | 0.064568 | 0.088425 | 0.073242 | 0.027466 | 0.14648 | 0.082397 | -119.4214 | 0.12817 | 0.018311 | 0.018311 | 0 | -123.2849 | 123.2346 | -0.041199 | 123.1613 | 123.1705 | -119.4901 | -0.19684 | -0.068665 | -0.073242 | 123.1064 | 123.1064 | 3.6667 | 123.1155 | 123.1613 | 123.0881 | 123.2162 | -0.19684 | 123.1155 | 123.1613 | 123.2162 | 3.6667 | 123.0881 | 0.077819 | -123.3536
474.7812 | 123.3444 | -123.0927 | 0.082397 | -0.00061033 | 0.03964 | 0.011408 | 0.017156 | -0.0054003 | 0.064354 | 0.090561 | 0.10986 | 0.018311 | 0.14648 | 0.10986 | -119.6457 | 0.15106 | -0.032043 | 0.032043 | -0.009155 | -123.2803 | 123.2391 | -0.064086 | 123.2025 | 123.2025 | -119.7281 | -0.18768 | -0.091552 | -0.036621 | 123.0606 | 123.1247 | 3.447 | 123.111 | 123.2025 | 123.0835 | 123.2437 | -0.18768 | 123.111 | 123.2025 | 123.2437 | 3.447 | 123.0835 | 0.064087 | -123.3627
475.7812 | 123.2803 | -123.1064 | 0.082397 | -0.00061033 | 0.036435 | 0.010339 | 0.020147 | -0.0015551 | 0.064354 | 0.087571 | 0.086975 | 0.009155 | 0.12817 | 0.045776 | -119.4763 | 0.1236 | 0.004578 | -0.032043 | -0.004578 | -123.3353 | 123.2346 | -0.073242 | 123.1934 | 123.1522 | -119.5587 | -0.22888 | -0.086975 | -0.041199 | 123.111 | 123.0743 | 3.6301 | 123.1155 | 123.1934 | 123.1018 | 123.23 | -0.22888 | 123.1155 | 123.1934 | 123.23 | 3.6301 | 123.1018 | 0.045777 | -123.4177
476.7812 | 123.3307 | -123.1247 | 0.073242 | -0.0082398 | 0.032804 | 0.011194 | 0.035528 | -0.0034777 | 0.063072 | 0.096543 | 0.082397 | 0.009155 | 0.14191 | 0.10986 | -119.4763 | 0.15106 | -0.004578 | 0.036621 | -0.018311 | -123.2986 | 123.2666 | -0.064087 | 123.2071 | 123.2346 | -119.5496 | -0.17395 | -0.091553 | -0.05951 | 123.1201 | 123.1613 | 3.6484 | 123.1339 | 123.2071 | 123.1064 | 123.2758 | -0.17395 | 123.1339 | 123.2071 | 123.2758 | 3.6484 | 123.1064 | 0.068665 | -123.3719
477.7969 | 123.3902 | -123.143 | 0.064087 | -0.00061033 | 0.0296 | 0.0075622 | 0.05219 | -0.0024097 | 0.062431 | 0.10872 | 0.086975 | 0.013733 | 0.14648 | 0.10071 | -120.8496 | 0.14648 | -0.004578 | 0.041199 | -0.018311 | -123.2758 | 123.2895 | -0.050354 | 123.23 | 123.2437 | -120.9137 | -0.13275 | -0.082398 | -0.059509 | 123.1384 | 123.1842 | 2.2934 | 123.1567 | 123.23 | 123.1247 | 123.2895 | -0.13275 | 123.1567 | 123.23 | 123.2895 | 2.2934 | 123.1247 | 0.082397 | -123.3398
478.7812 | 123.2803 | -123.1476 | 0.07782 | -0.00061033 | 0.035795 | 0.0096986 | 0.076971 | -0.0049731 | 0.065422 | 0.14696 | 0.1236 | 0 | 0.16479 | 0.11444 | -121.5271 | 0.16022 | -0.018311 | 0.064087 | 0.004578 | -123.2895 | 123.3124 | -0.07782 | 123.2712 | 123.262 | -121.6049 | -0.14191 | -0.073242 | -0.041199 | 123.1293 | 123.2117 | 1.6205 | 123.1476 | 123.2712 | 123.1522 | 123.3078 | -0.14191 | 123.1476 | 123.2712 | 123.3078 | 1.6205 | 123.1522 | 0.086975 | -123.3673
479.7812 | 123.3353 | -123.1384 | 0.1236 | -0.0082398 | 0.057798 | 0.0082032 | 0.013738 | -0.0049731 | 0.066277 | 0.11577 | 0.073242 | 0.050354 | 0.16022 | -0.013733 | -121.7194 | 0.050354 | 0.018311 | -0.059509 | 0.041199 | -123.3032 | 123.2986 | -0.073242 | 123.2117 | 123.1247 | -121.843 | -0.16479 | -0.082397 | -0.086975 | 123.1567 | 123.0789 | 1.4191 | 123.1888 | 123.2117 | 123.1796 | 123.1888 | -0.16479 | 123.1888 | 123.2117 | 123.1888 | 1.4191 | 123.1796 | 0.036621 | -123.4268
480.7812 | 123.2941 | -123.1705 | 0.086975 | -0.0082398 | 0.034727 | 0.005426 | 0.014593 | -0.0060413 | 0.064995 | 0.087571 | 0.036621 | 0.027466 | 0.13733 | 0.027466 | -122.2183 | 0.09613 | 0.068665 | -0.018311 | 0.009155 | -123.3353 | 123.3078 | -0.059509 | 123.2071 | 123.1979 | -122.3053 | -0.16479 | -0.07782 | -0.10071 | 123.2391 | 123.1522 | 0.95215 | 123.1979 | 123.2071 | 123.1796 | 123.2666 | -0.16479 | 123.1979 | 123.2071 | 123.2666 | 0.95215 | 123.1796 | 0.050354 | -123.4222
481.7812 | 123.3627 | -123.143 | 0.09613 | -0.00061033 | 0.041562 | 0.0094848 | 0.018224 | -0.0043323 | 0.064781 | 0.097824 | 0.11902 | 0.018311 | 0.15564 | 0.073242 | -122.1039 | 0.13275 | -0.018311 | 0.013733 | 0.004578 | -123.3444 | 123.2986 | -0.077819 | 123.262 | 123.2162 | -122.2 | -0.20142 | -0.091552 | -0.036621 | 123.1247 | 123.1567 | 1.0391 | 123.1613 | 123.262 | 123.1476 | 123.2758 | -0.20142 | 123.1613 | 123.262 | 123.2758 | 1.0391 | 123.1476 | 0.05951 | -123.4406
482.7812 | 123.3948 | -123.1338 | 0.10986 | -0.023499 | 0.050107 | 0.0092712 | 0.012884 | -0.0045459 | 0.065208 | 0.10359 | 0.09613 | 0.027466 | 0.16022 | 0.059509 | -122.1039 | 0.09613 | -0.009155 | 0 | 0.041199 | -123.317 | 123.2941 | -0.082397 | 123.23 | 123.1934 | -122.2137 | -0.18311 | -0.068664 | -0.064087 | 123.1247 | 123.1338 | 1.03 | 123.1613 | 123.23 | 123.175 | 123.23 | -0.18311 | 123.1613 | 123.23 | 123.23 | 1.03 | 123.175 | 0.050354 | -123.4268
483.7812 | 123.4039 | -123.1613 | 0.091553 | -0.015869 | 0.041135 | 0.008844 | 0.019506 | -0.0039051 | 0.062859 | 0.095261 | 0.12817 | 0.032043 | 0.16479 | 0.09613 | -122.1313 | 0.13275 | -0.018311 | 0.027466 | 0.004578 | -123.3536 | 123.3261 | -0.05951 | 123.2895 | 123.2574 | -122.2229 | -0.19226 | -0.086975 | -0.036621 | 123.143 | 123.1888 | 1.03 | 123.1934 | 123.2895 | 123.1659 | 123.2941 | -0.19226 | 123.1934 | 123.2895 | 123.2941 | 1.03 | 123.1659 | 0.073242 | -123.4451
484.7812 | 123.3627 | -123.1659 | 0.10071 | -0.0082398 | 0.038999 | 0.0094848 | 0.018011 | -0.0051867 | 0.064781 | 0.094406 | 0.059509 | 0.059509 | 0.14648 | 0.041199 | -122.1817 | 0.10529 | 0.050354 | -0.013733 | 0.009155 | -123.3398 | 123.3124 | -0.041199 | 123.2254 | 123.2071 | -122.2824 | -0.17395 | -0.091553 | -0.086975 | 123.2162 | 123.1522 | 0.98419 | 123.2254 | 123.2254 | 123.175 | 123.2712 | -0.17395 | 123.2254 | 123.2254 | 123.2712 | 0.98419 | 123.175 | 0.045776 | -123.4406
485.7812 | 123.4406 | -123.2071 | 0.09613 | -0.015869 | 0.042844 | 0.008844 | 0.016943 | -0.0032641 | 0.063499 | 0.10231 | 0.064087 | 0.022888 | 0.14191 | 0.054932 | -122.1359 | 0.11444 | 0.027466 | 0.004578 | 0.009155 | -123.3444 | 123.349 | -0.073242 | 123.2712 | 123.262 | -122.2321 | -0.13733 | -0.086975 | -0.07782 | 123.2346 | 123.2117 | 1.0712 | 123.23 | 123.2712 | 123.2162 | 123.3215 | -0.13733 | 123.23 | 123.2712 | 123.3215 | 1.0712 | 123.2162 | 0.045777 | -123.4406
486.7812 | 123.4268 | -123.1934 | 0.086975 | -0.015869 | 0.030881 | 0.0058534 | 0.011816 | -0.0054003 | 0.065208 | 0.091416 | 0.11444 | -0.009155 | 0.16937 | 0.10071 | -122.1725 | 0.14191 | 0.004578 | 0.032043 | 0.022888 | -123.3398 | 123.3627 | -0.09613 | 123.3078 | 123.2941 | -122.2595 | -0.14648 | -0.064087 | -0.054932 | 123.1979 | 123.2254 | 1.0208 | 123.1842 | 123.3078 | 123.2162 | 123.3353 | -0.14648 | 123.1842 | 123.3078 | 123.3353 | 1.0208 | 123.2162 | 0.082398 | -123.4268
487.7969 | 123.3627 | -123.2391 | 0.091553 | -0.00061033 | 0.040922 | 0.0035034 | 0.019292 | -0.0049731 | 0.062645 | 0.099533 | 0.041199 | 0.041199 | 0.14191 | 0.050354 | -122.1771 | 0.082397 | 0.041199 | -0.018311 | 0.013733 | -123.349 | 123.381 | -0.050354 | 123.2803 | 123.2895 | -122.2687 | -0.10986 | -0.07782 | -0.10071 | 123.2803 | 123.2208 | 1.062 | 123.2803 | 123.2803 | 123.2529 | 123.3215 | -0.10986 | 123.2803 | 123.2803 | 123.3215 | 1.062 | 123.2529 | 0.050354 | -123.4406
488.7812 | 122.9233 | -122.6852 | 0.3067 | 0.0070192 | 0.085782 | 0.004358 | 0.034887 | -0.0058277 | 0.03701 | 0.34135 | 0.12817 | 0.091553 | 0.24261 | -0.70038 | -73.7961 | -0.66834 | -0.36163 | -0.14191 | 0.38452 | -122.8088 | 122.9279 | -0.21515 | 122.8134 | 121.9849 | -74.1028 | -0.1236 | 0.077819 | -0.11444 | 122.3236 | 122.5433 | 48.8892 | 122.7768 | 122.8134 | 123.0698 | 122.0169 | -0.1236 | 122.7768 | 122.8134 | 122.0169 | 48.8892 | 123.0698 | -0.064087 | -123.1155
489.7812 | 123.2574 | -123.0652 | 0.10071 | -0.0082398 | 0.036863 | 0.0041444 | 0.063726 | -0.0049731 | -0.0016556 | 0.08992 | 0.054932 | 0.004578 | 0.15106 | 0.054932 | -7.5348 | 0.086975 | 0.045776 | 0 | 0.027466 | -123.1522 | 123.2162 | -0.09613 | 123.1201 | 123.1201 | -7.6355 | -0.086975 | -0.073242 | -0.09613 | 123.111 | 123.0652 | 115.5304 | 123.0698 | 123.1201 | 123.0927 | 123.1522 | -0.086975 | 123.0698 | 123.1201 | 123.1522 | 115.5304 | 123.0927 | 0.050354 | -123.2529
490.7812 | 123.175 | -123.0743 | 0.10529 | -0.015869 | 0.037504 | 0.0049988 | 0.018011 | -0.0043323 | -0.00016016 | 0.046341 | 0.11444 | 0.009155 | 0.17395 | 0.068665 | -8.1985 | 0.11902 | 0.004578 | 0.004578 | 0.009155 | -123.2025 | 123.2483 | -0.096131 | 123.1888 | 123.143 | -8.3038 | -0.12817 | -0.096131 | -0.059509 | 123.0789 | 123.0789 | 114.8758 | 123.0835 | 123.1888 | 123.0835 | 123.1934 | -0.12817 | 123.0835 | 123.1888 | 123.1934 | 114.8758 | 123.0835 | 0.068664 | -123.3078
491.7812 | 123.2346 | -123.111 | 0.11902 | 0.0070192 | 0.039213 | 0.0056396 | 0.019933 | -0.0068957 | -0.0018692 | 0.034806 | 0.059509 | 0.013733 | 0.16022 | 0.045776 | -2.4994 | 0.091553 | 0.050354 | 0 | 0.022888 | -123.262 | 123.2712 | -0.10529 | 123.1705 | 123.1567 | -2.6184 | -0.15106 | -0.096131 | -0.10071 | 123.1613 | 123.111 | 120.6116 | 123.1247 | 123.1705 | 123.1338 | 123.2025 | -0.15106 | 123.1247 | 123.1705 | 123.2025 | 120.6116 | 123.1338 | 0.041198 | -123.381
492.7812 | 123.4451 | -123.0881 | 0.09613 | -0.00061033 | 0.033445 | 0.0073486 | 0.012029 | -0.0079639 | 0.0028304 | 0.03032 | 0.15564 | -0.027466 | 0.1831 | 0.16937 | -10.5927 | 0.21515 | -0.073242 | 0.13275 | -0.022888 | -123.2162 | 123.2712 | -0.1236 | 123.2437 | 123.2574 | -10.6888 | -0.12817 | -0.11902 | -0.027465 | 123.0148 | 123.2208 | 112.4954 | 123.0606 | 123.2437 | 123.0652 | 123.3032 | -0.12817 | 123.0606 | 123.2437 | 123.3032 | 112.4954 | 123.0652 | 0.086975 | -123.3124
493.7812 | 123.3902 | -123.1338 | 0.059509 | -0.0082398 | 0.035367 | 0.0032898 | 0.011388 | -0.0068957 | 0.0013352 | 0.028183 | 0.17395 | -0.036621 | 0.19684 | 0.17395 | -7.0541 | 0.2243 | -0.12817 | 0.14191 | -0.027466 | -123.2666 | 123.3307 | -0.09613 | 123.3078 | 123.3078 | -7.1136 | -0.13275 | -0.086975 | -0.022888 | 123.0057 | 123.2758 | 116.0797 | 123.0972 | 123.3078 | 123.1064 | 123.3582 | -0.13275 | 123.0972 | 123.3078 | 123.3582 | 116.0797 | 123.1064 | 0.13733 | -123.3261
494.7812 | 123.4406 | -123.1293 | 0.068665 | -0.0082398 | 0.034727 | 0.0047852 | 0.013097 | -0.0066821 | 0.0038986 | 0.034165 | 0.1831 | -0.013733 | 0.1831 | 0.16479 | -13.623 | 0.21973 | -0.13275 | 0.14191 | -0.013733 | -123.2529 | 123.3124 | -0.082398 | 123.3124 | 123.2941 | -13.6917 | -0.1236 | -0.082398 | 0 | 122.9965 | 123.2712 | 109.5062 | 123.1155 | 123.3124 | 123.1155 | 123.349 | -0.1236 | 123.1155 | 123.3124 | 123.349 | 109.5062 | 123.1155 | 0.11444 | -123.3215
495.7812 | 123.5046 | -123.1338 | 0.068665 | -0.0082398 | 0.037931 | 0.002008 | 0.013525 | -0.0083911 | -0.00037376 | 0.029892 | 0.16937 | -0.032043 | 0.19684 | 0.16937 | -6.4407 | 0.24261 | -0.16479 | 0.13733 | -0.013733 | -123.2254 | 123.3307 | -0.10071 | 123.3032 | 123.3032 | -6.5094 | -0.091553 | -0.082398 | -0.027465 | 122.9691 | 123.2712 | 116.6931 | 123.1018 | 123.3032 | 123.1201 | 123.3765 | -0.091553 | 123.1018 | 123.3032 | 123.3765 | 116.6931 | 123.1201 | 0.12817 | -123.2941
496.7812 | 123.4634 | -123.1201 | 0.068665 | -0.00061033 | 0.033872 | 0.0035034 | 0.013097 | -0.0064685 | 0.0028304 | 0.032883 | 0.15564 | -0.027466 | 0.19226 | 0.17853 | -10.3455 | 0.21515 | -0.14191 | 0.13733 | -0.009155 | -123.262 | 123.3124 | -0.096131 | 123.2758 | 123.2986 | -10.4141 | -0.14191 | -0.07782 | -0.036621 | 122.9782 | 123.2574 | 112.7747 | 123.0927 | 123.2758 | 123.111 | 123.3353 | -0.14191 | 123.0927 | 123.2758 | 123.3353 | 112.7747 | 123.111 | 0.1236 | -123.3307
497.7969 | 118.1671 | -90.6006 | 27.2919 | -0.015869 | 3.4869 | 0.0056396 | 6.943 | 0.010835 | 0.015648 | 7.0028 | 26.9028 | 26.5503 | 9.4254 | -25.9598 | -26.944 | -26.1566 | -26.3809 | -26.1337 | 13.9709 | -77.655 | 100.0259 | -0.74158 | 117.5034 | 64.6408 | -54.2358 | 12.9456 | -13.3209 | 17.4774 | 64.2197 | 64.4669 | 63.6566 | 117.1509 | 117.5034 | 104.5715 | 64.444 | 12.9456 | 117.1509 | 117.5034 | 64.444 | 63.6566 | 104.5715 | -17.8665 | -104.9469
498.7812 | 122.9645 | -122.5571 | 0.050354 | -0.00061033 | 0.028531 | 0.0024354 | 0.0094657 | -0.0054003 | -0.0025102 | 0.019638 | 0.15564 | -0.050354 | 0.16479 | 0.18768 | -0.79193 | 0.22888 | -0.14191 | 0.13275 | -0.036621 | -122.7768 | 122.7219 | -0.10071 | 122.7127 | 122.7448 | -0.84229 | -0.21973 | -0.086975 | -0.009155 | 122.4152 | 122.6898 | 121.7651 | 122.5067 | 122.7127 | 122.5204 | 122.7859 | -0.21973 | 122.5067 | 122.7127 | 122.7859 | 121.7651 | 122.5204 | 0.11444 | -122.8271
499.7812 | 123.0698 | -122.7585 | 0.050354 | -0.015869 | 0.029813 | 0.0049988 | 0.012884 | -0.0075367 | 0.049187 | 0.07518 | 0.14648 | -0.054932 | 0.16937 | 0.18768 | -97.2977 | 0.21057 | -0.13275 | 0.14191 | -0.059509 | -122.9095 | 122.9279 | -0.10529 | 122.905 | 122.9462 | -97.348 | -0.15106 | -0.10986 | -0.022889 | 122.6257 | 122.9004 | 25.4608 | 122.7036 | 122.905 | 122.699 | 122.9691 | -0.15106 | 122.7036 | 122.905 | 122.9691 | 25.4608 | 122.699 | 0.11902 | -122.9599
500.7812 | 123.0469 | -122.8546 | 0.041199 | -0.00061033 | 0.029172 | 0.0045716 | 0.013311 | -0.0073229 | -0.00016016 | 0.024552 | 0.086975 | -0.050354 | 0.16022 | 0.10986 | -3.0716 | 0.18768 | -0.09613 | 0.036621 | -0.036621 | -122.9462 | 123.0148 | -0.091553 | 122.9416 | 122.9645 | -3.1128 | -0.091553 | -0.07782 | -0.073242 | 122.7585 | 122.8912 | 119.783 | 122.8043 | 122.9416 | 122.818 | 123.0423 | -0.091553 | 122.8043 | 122.9416 | 123.0423 | 119.783 | 122.818 | 0.11902 | -122.9874
501.7812 | 123.1201 | -122.8867 | 0.045776 | 0.0070192 | 0.030454 | 0.003717 | 0.01267 | -0.0079639 | -0.0022964 | 0.024765 | 0.07782 | -0.045776 | 0.15106 | 0.10071 | -1.5152 | 0.16479 | -0.082397 | 0.036621 | -0.064087 | -122.9782 | 123.0377 | -0.091552 | 122.9645 | 122.9874 | -1.561 | -0.091552 | -0.10986 | -0.073242 | 122.8043 | 122.9233 | 121.3715 | 122.8409 | 122.9645 | 122.8226 | 123.0515 | -0.091552 | 122.8409 | 122.9645 | 123.0515 | 121.3715 | 122.8226 | 0.10529 | -123.024
502.7812 | 122.5296 | -122.2778 | 0.064087 | -0.015869 | 0.030881 | 0.0045716 | 0.0069021 | -0.0071093 | -0.00058736 | 0.010453 | 0.091553 | -0.027466 | 0.15106 | 0.10986 | -0.064087 | 0.1831 | -0.10071 | 0.059509 | -0.018311 | -122.4152 | 122.4289 | -0.091553 | 122.3694 | 122.3877 | -0.12817 | -0.13733 | -0.082398 | -0.059509 | 122.1771 | 122.3373 | 122.2137 | 122.2504 | 122.3694 | 122.2595 | 122.4609 | -0.13733 | 122.2504 | 122.3694 | 122.4609 | 122.2137 | 122.2595 | 0.086975 | -122.4792
503.7812 | 122.9736 | -122.7264 | 0.054932 | 0.0070192 | 0.030454 | 0.0058534 | 0.01267 | -0.0077503 | -0.0029374 | 0.012375 | 0.09613 | -0.032043 | 0.17395 | 0.14648 | 0.073242 | 0.21057 | -0.11444 | 0.082397 | -0.045776 | -122.7997 | 122.9004 | -0.086975 | 122.8226 | 122.8729 | 0.01831 | -0.073243 | -0.10071 | -0.07782 | 122.612 | 122.8088 | 122.7997 | 122.6944 | 122.8226 | 122.6807 | 122.937 | -0.073243 | 122.6944 | 122.8226 | 122.937 | 122.7997 | 122.6807 | 0.11902 | -122.8546
504.7812 | 123.0194 | -122.8043 | 0.041199 | -0.0082398 | 0.030881 | 0.005426 | 0.013311 | -0.0094593 | -0.0040054 | 0.013871 | 0.091553 | -0.045776 | 0.16479 | 0.14191 | 0.050354 | 0.17853 | -0.10529 | 0.050354 | -0.045776 | -122.8912 | 122.9691 | -0.086975 | 122.8958 | 122.9462 | 0.009155 | -0.086975 | -0.086975 | -0.073242 | 122.699 | 122.8546 | 122.8546 | 122.7585 | 122.8958 | 122.7585 | 122.9828 | -0.086975 | 122.7585 | 122.8958 | 122.9828 | 122.8546 | 122.7585 | 0.1236 | -122.9324
505.7812 | 123.0469 | -122.8317 | 0.050354 | -0.0082398 | 0.030454 | 0.0015808 | 0.016729 | -0.0079639 | -0.00486 | 0.016007 | 0.11902 | -0.064087 | 0.1831 | 0.14648 | 0.086975 | 0.20599 | -0.11902 | 0.059509 | -0.059509 | -122.9279 | 123.0148 | -0.11444 | 122.9507 | 122.9782 | 0.036621 | -0.09613 | -0.10986 | -0.064086 | 122.7127 | 122.8912 | 122.9187 | 122.7676 | 122.9507 | 122.7722 | 123.0377 | -0.09613 | 122.7676 | 122.9507 | 123.0377 | 122.9187 | 122.7722 | 0.13275 | -122.9782
506.7812 | 123.0927 | -122.8134 | 0.036621 | -0.00061033 | 0.03024 | 0.0058534 | 0.015874 | -0.0071093 | -0.004219 | 0.014511 | 0.13733 | -0.054932 | 0.17853 | 0.17853 | 0.10529 | 0.21973 | -0.15564 | 0.07782 | -0.054932 | -122.9874 | 122.9919 | -0.091553 | 122.9507 | 122.9919 | 0.068665 | -0.17395 | -0.091553 | -0.041199 | 122.6578 | 122.8912 | 122.9187 | 122.7585 | 122.9507 | 122.7585 | 123.0331 | -0.17395 | 122.7585 | 122.9507 | 123.0331 | 122.9187 | 122.7585 | 0.14191 | -123.024
507.7969 | 123.1201 | -122.8134 | 0.059509 | 0.0070192 | 0.034086 | 0.0090576 | 0.016943 | -0.0088183 | -0.0020828 | 0.013016 | 0.15564 | -0.036621 | 0.16937 | 0.1831 | 0.11444 | 0.23346 | -0.16937 | 0.086975 | -0.064087 | -123.0148 | 122.9828 | -0.09613 | 122.9691 | 122.9965 | 0.054932 | -0.20142 | -0.1236 | -0.013733 | 122.644 | 122.9004 | 122.9279 | 122.7768 | 122.9691 | 122.7493 | 123.0469 | -0.20142 | 122.7768 | 122.9691 | 123.0469 | 122.9279 | 122.7493 | 0.10986 | -123.0743
508.7812 | 123.1659 | -122.8317 | 0.050354 | -0.00061033 | 0.03259 | 0.0084168 | 0.01972 | -0.0086047 | -0.0020828 | 0.020279 | 0.16479 | -0.036621 | 0.16937 | 0.17853 | 0.086975 | 0.23346 | -0.19226 | 0.07782 | -0.059509 | -122.9965 | 123.0011 | -0.086975 | 122.9965 | 123.0103 | 0.036621 | -0.16479 | -0.10986 | -0.004578 | 122.6395 | 122.9095 | 122.9187 | 122.7951 | 122.9965 | 122.7722 | 123.0652 | -0.16479 | 122.7951 | 122.9965 | 123.0652 | 122.9187 | 122.7722 | 0.11902 | -123.0469
509.7812 | 123.1705 | -122.8638 | 0.041199 | -0.00061033 | 0.033231 | 0.007776 | 0.019933 | -0.0068957 | -0.0025102 | 0.019638 | 0.15564 | -0.050354 | 0.18768 | 0.1831 | 0.091553 | 0.22888 | -0.18768 | 0.082397 | -0.064087 | -123.0194 | 123.0515 | -0.091553 | 123.0194 | 123.0469 | 0.050354 | -0.15564 | -0.10529 | -0.032043 | 122.6761 | 122.9462 | 122.9553 | 122.8134 | 123.0194 | 122.7997 | 123.0927 | -0.15564 | 122.8134 | 123.0194 | 123.0927 | 122.9553 | 122.7997 | 0.14648 | -123.0606
510.7812 | 123.175 | -122.8775 | 0.045776 | -0.015869 | 0.034513 | 0.0062806 | 0.021856 | -0.0068957 | -0.0020828 | 0.022202 | 0.16937 | -0.054932 | 0.18768 | 0.17853 | 0.11444 | 0.2243 | -0.19684 | 0.064087 | -0.064087 | -123.0377 | 123.0652 | -0.10071 | 123.0469 | 123.056 | 0.068665 | -0.16022 | -0.10986 | -0.01831 | 122.6807 | 122.9416 | 122.9919 | 122.8226 | 123.0469 | 122.8134 | 123.1018 | -0.16022 | 122.8226 | 123.0469 | 123.1018 | 122.9919 | 122.8134 | 0.14191 | -123.0835
511.7812 | 123.1842 | -122.8134 | 0.082397 | -0.00061033 | 0.078092 | 0.0028626 | 0.048772 | -0.0056141 | -0.0037918 | 0.095902 | 0.20142 | -0.004578 | 0.2243 | -0.018311 | -0.10071 | 0.032043 | -0.37079 | -0.3891 | -0.009155 | -122.9828 | 123.0377 | -0.086975 | 123.0148 | 122.7951 | -0.18311 | -0.16937 | -0.091552 | -0.022888 | 122.4426 | 122.4243 | 122.7127 | 122.8088 | 123.0148 | 122.8043 | 122.8455 | -0.16937 | 122.8088 | 123.0148 | 122.8455 | 122.7127 | 122.8043 | 0.14191 | -123.0652
512.7812 | 123.1934 | -122.6669 | 0.24261 | -0.00061033 | 0.21097 | 0.0099122 | 0.17118 | -0.0062549 | -0.0022964 | 0.34563 | 0.31128 | 0.16479 | 0.31128 | -0.54016 | -0.61798 | -0.48065 | -0.85602 | -2.3849 | 0.13733 | -122.8455 | 122.9782 | -0.07782 | 122.9782 | 122.1268 | -0.8606 | -0.17853 | -0.10529 | 0 | 121.8109 | 120.282 | 122.049 | 122.8317 | 122.9782 | 122.8043 | 122.1863 | -0.17853 | 122.8317 | 122.9782 | 122.1863 | 122.049 | 122.8043 | 0.068664 | -123.0881
513.7812 | 123.2117 | -122.8775 | 0.041199 | -0.00061033 | 0.040494 | 0.0041444 | 0.034887 | -0.0054003 | -0.0050736 | 0.043137 | 0.16022 | -0.032043 | 0.17853 | 0.13733 | 0.027466 | 0.20142 | -0.23346 | -0.07782 | -0.059509 | -123.0652 | 123.056 | -0.073242 | 123.0377 | 123.0148 | -0.013733 | -0.18768 | -0.10071 | -0.018311 | 122.644 | 122.7997 | 122.905 | 122.8455 | 123.0377 | 122.818 | 123.0789 | -0.18768 | 122.8455 | 123.0377 | 123.0789 | 122.905 | 122.818 | 0.13733 | -123.1064
514.7812 | 121.6049 | -121.4767 | 0.11444 | -0.00061033 | 0.060575 | 0.012476 | 0.010107 | -0.0032641 | -0.0012284 | 0.037369 | 0.10986 | 0.041199 | 0.17853 | -0.28381 | -0.34332 | -0.25635 | -0.33417 | -0.41199 | 0.018311 | -121.6141 | 121.6553 | -0.073242 | 121.5866 | 121.1929 | -0.45776 | -0.13733 | -0.09613 | -0.068665 | 121.1426 | 121.0648 | 121.1334 | 121.5179 | 121.5866 | 121.4951 | 121.2204 | -0.13733 | 121.5179 | 121.5866 | 121.2204 | 121.1334 | 121.4951 | 0.064087 | -121.7285
515.7812 | 122.5525 | -121.9254 | 0.57678 | -0.00061033 | 0.53225 | 0.0099122 | 0.013097 | -0.0013415 | -0.00016016 | 0.51204 | 0.5127 | 0.48523 | 0.56305 | -2.7008 | -2.7328 | -2.6596 | -2.7328 | -3.2867 | 0.50354 | -122.0352 | 122.4884 | -0.091553 | 122.438 | 119.2245 | -3.3096 | -0.10986 | -0.073242 | -0.050354 | 119.1925 | 118.6386 | 119.1925 | 122.4106 | 122.438 | 122.4289 | 119.2657 | -0.10986 | 122.4106 | 122.438 | 119.2657 | 119.1925 | 122.4289 | -0.013733 | -122.612
516.7812 | 122.6852 | -122.493 | 0.09613 | -0.00061033 | 0.060361 | 0.0099122 | 0.013738 | -0.0036915 | 0.00069424 | 0.042069 | 0.068665 | 0.027466 | 0.16022 | -0.086975 | -0.1236 | -0.018311 | -0.11444 | -0.19684 | 0.018311 | -122.699 | 122.6532 | -0.068664 | 122.5616 | 122.406 | -0.21973 | -0.20599 | -0.077819 | -0.091552 | 122.3785 | 122.2961 | 122.3694 | 122.5204 | 122.5616 | 122.5113 | 122.4747 | -0.20599 | 122.5204 | 122.5616 | 122.4747 | 122.3694 | 122.5113 | 0.064087 | -122.7951
517.7969 | 122.7173 | -122.2641 | 0.37994 | -0.00061033 | 0.31885 | 0.010339 | 0.056676 | -0.0019825 | -0.0016556 | 0.31316 | 0.32959 | 0.27466 | 0.37079 | -1.181 | -1.2772 | -1.1673 | -1.3229 | -1.7944 | 0.27466 | -122.3923 | 122.6349 | -0.10529 | 122.5937 | 121.0831 | -1.6571 | -0.12817 | -0.10529 | -0.041199 | 120.9412 | 120.4697 | 120.9869 | 122.5388 | 122.5937 | 122.5388 | 121.0968 | -0.12817 | 122.5388 | 122.5937 | 121.0968 | 120.9869 | 122.5388 | -0.009155 | -122.7722
518.7812 | 122.4243 | -122.2092 | 0.073242 | -0.0082398 | 0.034727 | 0.0064942 | 0.027624 | -0.0028369 | -0.004219 | 0.021347 | 0.054932 | 0.013733 | 0.13275 | 0.064087 | 0.018311 | 0.11902 | 0.027466 | -0.050354 | 0 | -122.4335 | 122.3419 | -0.059509 | 122.2641 | 122.2733 | -0.054931 | -0.22431 | -0.073242 | -0.077819 | 122.2366 | 122.1588 | 122.2275 | 122.2229 | 122.2641 | 122.2092 | 122.3282 | -0.22431 | 122.2229 | 122.2641 | 122.3282 | 122.2275 | 122.2092 | 0.059509 | -122.5067
519.7812 | 122.6349 | -122.4014 | 0.054932 | -0.015869 | 0.03494 | 0.0079896 | 0.026342 | -0.0045459 | -0.0022964 | 0.023056 | 0.045776 | 0.004578 | 0.13275 | 0.059509 | 0.018311 | 0.13275 | 0 | -0.027466 | -0.036621 | -122.5891 | 122.5342 | -0.050354 | 122.4472 | 122.4609 | -0.036621 | -0.18768 | -0.091553 | -0.086975 | 122.4014 | 122.374 | 122.4197 | 122.406 | 122.4472 | 122.3648 | 122.5342 | -0.18768 | 122.406 | 122.4472 | 122.5342 | 122.4197 | 122.3648 | 0.077819 | -122.644
520.7812 | 122.6395 | -122.4747 | 0.07782 | -0.00061033 | 0.03729 | 0.0075622 | 0.027196 | -0.0034777 | -0.0035782 | 0.027542 | 0.050354 | 0.022888 | 0.1236 | 0.050354 | -0.018311 | 0.10529 | 0.050354 | -0.064087 | -0.018311 | -122.699 | 122.5983 | -0.054932 | 122.525 | 122.525 | -0.096131 | -0.22431 | -0.096131 | -0.073242 | 122.525 | 122.4106 | 122.4564 | 122.4976 | 122.525 | 122.4564 | 122.58 | -0.22431 | 122.4976 | 122.525 | 122.58 | 122.4564 | 122.4564 | 0.045776 | -122.7768
521.7812 | 122.6852 | -122.5296 | 0.07782 | 0.0070192 | 0.037504 | 0.0075622 | 0.032537 | -0.0051867 | -0.0044328 | 0.026902 | 0.059509 | 0 | 0.13275 | 0.082397 | 0.009155 | 0.10986 | 0.027466 | -0.022888 | -0.009155 | -122.7219 | 122.6624 | -0.07782 | 122.5891 | 122.612 | -0.068665 | -0.19226 | -0.086975 | -0.073242 | 122.5571 | 122.5067 | 122.5388 | 122.5296 | 122.5891 | 122.5204 | 122.6395 | -0.19226 | 122.5296 | 122.5891 | 122.6395 | 122.5388 | 122.5204 | 0.054931 | -122.7997
522.7812 | 122.612 | -122.3831 | 0.059509 | -0.015869 | 0.027677 | 0.007776 | 0.033178 | -0.0024097 | -0.0022964 | 0.022202 | 0.082397 | 0.004578 | 0.14191 | 0.07782 | 0.022888 | 0.1236 | 0.009155 | -0.027466 | -0.013733 | -122.6349 | 122.525 | -0.054931 | 122.4655 | 122.4609 | -0.036621 | -0.25177 | -0.073242 | -0.05951 | 122.3923 | 122.3557 | 122.406 | 122.3877 | 122.4655 | 122.3694 | 122.5067 | -0.25177 | 122.3877 | 122.4655 | 122.5067 | 122.406 | 122.3694 | 0.082398 | -122.6944
523.7812 | 122.7081 | -122.5388 | 0.068665 | -0.00061033 | 0.024259 | 0.011408 | 0.019933 | -0.0019825 | -0.0035782 | 0.010239 | 0.064087 | 0.009155 | 0.13275 | 0.050354 | 0.013733 | 0.12817 | 0.036621 | -0.041199 | -0.009155 | -122.7036 | 122.6715 | -0.05951 | 122.6028 | 122.5891 | -0.054932 | -0.16479 | -0.07782 | -0.068664 | 122.5754 | 122.4976 | 122.5525 | 122.5479 | 122.6028 | 122.5296 | 122.6669 | -0.16479 | 122.5479 | 122.6028 | 122.6669 | 122.5525 | 122.5296 | 0.064086 | -122.7722
524.7812 | 122.6944 | -122.3511 | 0.25177 | -0.0082398 | 0.17145 | 0.0094848 | 0.56531 | -0.0043323 | -0.0025102 | 0.71199 | 0.24719 | 0.16937 | 0.28839 | -0.78735 | -2.2202 | -0.76446 | -0.8606 | -0.89264 | 0.10529 | -122.4884 | 122.6395 | -0.082397 | 122.5983 | 121.5637 | -2.4719 | -0.13733 | -0.14648 | -0.041199 | 121.4905 | 121.4584 | 120.1309 | 122.5204 | 122.5983 | 122.4564 | 121.5866 | -0.13733 | 122.5204 | 122.5983 | 121.5866 | 120.1309 | 122.4564 | 0.036621 | -122.7402
525.7812 | 122.7539 | -122.5479 | 0.082397 | -0.00061033 | 0.031522 | 0.0079896 | 0.02506 | -0.0034777 | -0.004219 | 0.018357 | 0.086975 | 0 | 0.13733 | 0.10986 | 0.059509 | 0.15106 | 0 | 0.013733 | -0.022888 | -122.7768 | 122.6852 | -0.082397 | 122.6349 | 122.6578 | -0.022888 | -0.22888 | -0.10528 | -0.050354 | 122.5479 | 122.5616 | 122.6074 | 122.5479 | 122.6349 | 122.525 | 122.699 | -0.22888 | 122.5479 | 122.6349 | 122.699 | 122.6074 | 122.525 | 0.054932 | -122.8592
526.7812 | 122.8043 | -122.5708 | 0.073242 | -0.0082398 | 0.031522 | 0.0099122 | 0.025701 | -0.0028369 | -0.0016556 | 0.018998 | 0.11902 | -0.009155 | 0.13733 | 0.11444 | 0.082397 | 0.16937 | -0.009155 | 0.050354 | -0.018311 | -122.7997 | 122.7081 | -0.082397 | 122.6898 | 122.6852 | 0.009155 | -0.22888 | -0.091553 | -0.01831 | 122.5616 | 122.6212 | 122.6532 | 122.5616 | 122.6898 | 122.5525 | 122.7402 | -0.22888 | 122.5616 | 122.6898 | 122.7402 | 122.6532 | 122.5525 | 0.064087 | -122.8729
527.8125 | 122.7448 | -122.3969 | 0.2243 | -0.0082398 | 0.17209 | -0.0016236 | 0.57065 | -0.0049731 | -0.0010148 | 0.70045 | 0.24719 | 0.12817 | 0.32044 | -0.52643 | -1.4694 | -0.41657 | -0.68207 | -0.58136 | 0.10529 | -122.4838 | 122.7173 | -0.09613 | 122.644 | 121.8704 | -1.6937 | -0.086975 | -0.11902 | -0.073243 | 121.7148 | 121.8155 | 120.9274 | 122.525 | 122.644 | 122.5021 | 121.9803 | -0.086975 | 122.525 | 122.644 | 121.9803 | 120.9274 | 122.5021 | 0.096131 | -122.7081
528.7812 | 122.8363 | -122.6212 | 0.073242 | -0.0082398 | 0.030881 | 0.005426 | 0.029333 | -0.0045459 | -0.0033646 | 0.020279 | 0.10071 | 0.013733 | 0.14648 | 0.13275 | 0.086975 | 0.19226 | 0.004578 | 0.07782 | -0.004578 | -122.8271 | 122.7676 | -0.059509 | 122.7219 | 122.7539 | 0.013733 | -0.20599 | -0.07782 | -0.045776 | 122.6257 | 122.699 | 122.7081 | 122.6349 | 122.7219 | 122.6166 | 122.8134 | -0.20599 | 122.6349 | 122.7219 | 122.8134 | 122.7081 | 122.6166 | 0.073242 | -122.9004
529.7812 | 122.8546 | -122.6349 | 0.050354 | -0.0082398 | 0.031522 | 0.0073486 | 0.026128 | -0.0036915 | -0.0022964 | 0.018998 | 0.091553 | 0.009155 | 0.14191 | 0.13275 | 0.07782 | 0.17853 | 0.009155 | 0.068665 | -0.004578 | -122.8134 | 122.7768 | -0.041199 | 122.7264 | 122.7676 | 0.027466 | -0.17853 | -0.054932 | -0.050354 | 122.644 | 122.7036 | 122.7127 | 122.644 | 122.7264 | 122.6303 | 122.8134 | -0.17853 | 122.644 | 122.7264 | 122.8134 | 122.7127 | 122.6303 | 0.091553 | -122.8638
530.7812 | 122.3007 | -121.6507 | 0.49896 | -0.0082398 | 0.41369 | 0.0049988 | 0.16114 | -0.0004871 | -0.00016016 | 0.53383 | 0.47607 | 0.42114 | 0.50354 | -1.6205 | -2.3026 | -1.5656 | -1.7075 | -37.2986 | 0.39825 | -121.8246 | 122.1542 | -0.077819 | 122.1268 | 120.0302 | -2.8015 | -0.17395 | -0.10071 | -0.027466 | 119.9432 | 84.3521 | 119.3481 | 122.0718 | 122.1268 | 122.0489 | 120.0851 | -0.17395 | 122.0718 | 122.1268 | 120.0851 | 119.3481 | 122.0489 | 0.004578 | -122.3236
531.7812 | 122.5525 | -122.3465 | 0.073242 | -0.00061033 | 0.038144 | 0.0067078 | 0.032751 | -0.0064685 | -0.0029374 | 0.027542 | 0.1236 | -0.013733 | 0.15106 | 0.11902 | 0.082397 | 0.17853 | -0.004578 | -56.0486 | -0.032043 | -122.525 | 122.4976 | -0.086975 | 122.4701 | 122.4655 | 0.009155 | -0.17853 | -0.10529 | -0.027466 | 122.3419 | 66.2979 | 122.4289 | 122.3328 | 122.4701 | 122.3145 | 122.525 | -0.17853 | 122.3328 | 122.4701 | 122.525 | 122.4289 | 122.3145 | 0.07782 | -122.5983
532.7969 | 122.7081 | -122.3923 | 0.036621 | -0.0082398 | 0.031736 | 0.0075622 | 0.027624 | -0.0026233 | -0.003151 | 0.030747 | 0.14648 | -0.045776 | 0.17853 | 0.1831 | 0.14648 | 0.26093 | -0.14191 | -57.3898 | -0.07782 | -122.5662 | 122.5708 | -0.082397 | 122.5388 | 122.5754 | 0.10986 | -0.17395 | -0.11444 | -0.032044 | 122.2504 | 65.0024 | 122.5388 | 122.3465 | 122.5388 | 122.3145 | 122.6532 | -0.17395 | 122.3465 | 122.5388 | 122.6532 | 122.5388 | 122.3145 | 0.14191 | -122.6028
533.7812 | 122.6715 | -122.4701 | 0.07782 | -0.00061033 | 0.036008 | 0.0079896 | 0.032751 | -0.0054003 | -0.0029374 | 0.031388 | 0.059509 | -0.004578 | 0.13275 | 0.091553 | 0.054932 | 0.14191 | 0.041199 | -45.5292 | -0.032043 | -122.6486 | 122.6028 | -0.082398 | 122.5296 | 122.5616 | -0.022888 | -0.17853 | -0.10986 | -0.073242 | 122.5113 | 76.9409 | 122.525 | 122.4655 | 122.5296 | 122.4381 | 122.612 | -0.17853 | 122.4655 | 122.5296 | 122.612 | 122.525 | 122.4381 | 0.054931 | -122.7264
534.7812 | 122.4838 | -122.3373 | 0.073242 | -0.00061033 | 0.033872 | 0.0067078 | 0.019506 | -0.0051867 | -0.0016556 | 0.011521 | 0.027466 | 0.004578 | 0.1236 | 0.068665 | 0.036621 | 0.13275 | 0.086975 | -32.5836 | -0.004578 | -122.5021 | 122.4609 | -0.068664 | 122.3648 | 122.406 | -0.036621 | -0.16479 | -0.07782 | -0.09613 | 122.4243 | 89.7537 | 122.374 | 122.3419 | 122.3648 | 122.3328 | 122.4701 | -0.16479 | 122.3419 | 122.3648 | 122.4701 | 122.374 | 122.3328 | 0.050354 | -122.5754
535.7812 | 122.58 | -122.4335 | 0.068665 | -0.0082398 | 0.032804 | 0.0075622 | 0.017797 | -0.0041187 | -0.0018692 | 0.0098118 | 0.041199 | 0.032043 | 0.13733 | 0.068665 | 0.022888 | 0.12817 | 0.10071 | 0.004578 | -0.009155 | -122.6028 | 122.5708 | -0.036622 | 122.4747 | 122.5021 | -0.045777 | -0.16937 | -0.07782 | -0.09613 | 122.5342 | 122.438 | 122.4564 | 122.4655 | 122.4747 | 122.4243 | 122.5616 | -0.16937 | 122.4655 | 122.4747 | 122.5616 | 122.4564 | 122.4243 | 0.068664 | -122.6715
536.7812 | 122.6028 | -122.4564 | 0.073242 | -0.015869 | 0.0296 | 0.0045716 | 0.018438 | -0.0064685 | -0.0037918 | 0.011093 | 0.027466 | 0.004578 | 0.12817 | 0.059509 | 0.032043 | 0.1236 | 0.091553 | 0.013733 | 0.009155 | -122.644 | 122.5845 | -0.068664 | 122.4838 | 122.5159 | -0.041199 | -0.18768 | -0.064087 | -0.10071 | 122.5479 | 122.4701 | 122.4884 | 122.4609 | 122.4838 | 122.4655 | 122.58 | -0.18768 | 122.4609 | 122.4838 | 122.58 | 122.4884 | 122.4655 | 0.054932 | -122.7173
537.7969 | 122.7219 | -122.4243 | 0.064087 | -0.015869 | 0.028531 | 0.003717 | 0.016088 | -0.0056141 | -0.0050736 | 0.010453 | 0.1236 | -0.036621 | 0.16937 | 0.17395 | 0.1236 | 0.24719 | -0.12817 | 0.10071 | -0.050354 | -122.6166 | 122.5937 | -0.10071 | 122.5479 | 122.5983 | 0.059509 | -0.19226 | -0.11444 | -0.045777 | 122.2961 | 122.525 | 122.5479 | 122.3877 | 122.5479 | 122.374 | 122.6715 | -0.19226 | 122.3877 | 122.5479 | 122.6715 | 122.5479 | 122.374 | 0.10529 | -122.6807
538.7812 | 122.6486 | -122.5159 | 0.07782 | -0.015869 | 0.0296 | 0.0049988 | 0.02207 | -0.0060413 | -0.0037918 | 0.011093 | 0.027466 | 0.009155 | 0.1236 | 0.07782 | 0.041199 | 0.11902 | 0.091553 | 0 | 0.004578 | -122.6807 | 122.6395 | -0.068665 | 122.5433 | 122.5937 | -0.036621 | -0.16479 | -0.073242 | -0.09613 | 122.6074 | 122.5159 | 122.5571 | 122.525 | 122.5433 | 122.5204 | 122.6349 | -0.16479 | 122.525 | 122.5433 | 122.6349 | 122.5571 | 122.5204 | 0.045776 | -122.7585
539.7812 | 122.6761 | -122.5296 | 0.064087 | -0.0082398 | 0.028959 | 0.0047852 | 0.022497 | -0.0062549 | -0.0035782 | 0.012375 | 0.050354 | 0.004578 | 0.13275 | 0.073242 | 0.050354 | 0.12817 | 0.068665 | 0.032043 | -0.009155 | -122.6807 | 122.6624 | -0.059509 | 122.58 | 122.6028 | -0.013733 | -0.15106 | -0.073242 | -0.082397 | 122.5983 | 122.5616 | 122.58 | 122.5342 | 122.58 | 122.5204 | 122.6578 | -0.15106 | 122.5342 | 122.58 | 122.6578 | 122.58 | 122.5204 | 0.068664 | -122.7448
540.7812 | 122.1542 | -122.049 | 0.073242 | -0.0082398 | 0.023191 | 0.0094848 | 0.01502 | -0.0071093 | -0.0025102 | 0.0012668 | 0.032043 | 0.009155 | 0.11444 | 0.059509 | 0.036621 | 0.10529 | 0.09613 | 0.027466 | 0.004578 | -122.2183 | 122.1634 | -0.064087 | 122.081 | 122.1085 | -0.036621 | -0.16937 | -0.068664 | -0.082398 | 122.1451 | 122.0764 | 122.0856 | 122.0581 | 122.081 | 122.0535 | 122.1542 | -0.16937 | 122.0581 | 122.081 | 122.1542 | 122.0856 | 122.0535 | 0.041199 | -122.2916
541.7812 | 122.3602 | -122.2504 | 0.064087 | 0.0070192 | 0.021482 | 0.006067 | 0.01267 | -0.0058277 | -0.0029374 | 0.0012668 | 0.036621 | 0 | 0.12817 | 0.082397 | 0.032043 | 0.12817 | 0.091553 | 0.018311 | -0.009155 | -122.4014 | 122.3785 | -0.064087 | 122.287 | 122.3328 | -0.032044 | -0.15106 | -0.073242 | -0.091553 | 122.3419 | 122.2687 | 122.2824 | 122.2504 | 122.287 | 122.2412 | 122.3785 | -0.15106 | 122.2504 | 122.287 | 122.3785 | 122.2824 | 122.2412 | 0.064087 | -122.4655
542.7812 | 122.4792 | -122.2961 | 0.086975 | -0.0082398 | 0.025113 | 0.007135 | 0.016088 | -0.0043323 | -0.0018692 | 0.00041236 | 0.059509 | 0.009155 | 0.1236 | 0.10529 | 0.036621 | 0.13275 | 0.068665 | 0.041199 | -0.013733 | -122.4747 | 122.4197 | -0.07782 | 122.3557 | 122.4014 | -0.050354 | -0.17853 | -0.10071 | -0.064087 | 122.3648 | 122.3373 | 122.3328 | 122.3053 | 122.3557 | 122.2824 | 122.4289 | -0.17853 | 122.3053 | 122.3557 | 122.4289 | 122.3328 | 122.2824 | 0.036621 | -122.5616
543.7812 | 122.5204 | -122.3328 | 0.073242 | -0.015869 | 0.022123 | 0.002008 | 0.01267 | -0.0047595 | -0.00486 | 0.00041236 | 0.11902 | -0.022888 | 0.16479 | 0.14648 | 0.10529 | 0.19226 | -0.004578 | 0.086975 | -0.013733 | -122.5067 | 122.4976 | -0.09613 | 122.4518 | 122.4792 | 0.032044 | -0.17395 | -0.086975 | -0.045776 | 122.3282 | 122.4197 | 122.4381 | 122.3099 | 122.4518 | 122.319 | 122.525 | -0.17395 | 122.3099 | 122.4518 | 122.525 | 122.4381 | 122.319 | 0.091553 | -122.58
544.7812 | 122.6532 | -122.3557 | 0.045776 | 0.0070192 | 0.018491 | 0.0062806 | 0.011602 | -0.0056141 | -0.0055008 | 0.00083956 | 0.13733 | -0.041199 | 0.17853 | 0.19684 | 0.16937 | 0.28381 | -0.10529 | 0.17395 | -0.045776 | -122.493 | 122.5342 | -0.086975 | 122.493 | 122.5525 | 0.1236 | -0.13733 | -0.091552 | -0.041199 | 122.2504 | 122.5296 | 122.525 | 122.3145 | 122.493 | 122.3099 | 122.6395 | -0.13733 | 122.3145 | 122.493 | 122.6395 | 122.525 | 122.3099 | 0.13275 | -122.5388
545.7812 | 122.6761 | -122.4014 | 0.041199 | -0.0082398 | 0.021482 | 0.0039306 | 0.012029 | -0.0092457 | -0.0025102 | 0.0010532 | 0.12817 | -0.041199 | 0.16479 | 0.20142 | 0.15564 | 0.2655 | -0.10071 | 0.17853 | -0.032043 | -122.5204 | 122.5662 | -0.082398 | 122.5296 | 122.6028 | 0.11444 | -0.11902 | -0.073242 | -0.036621 | 122.3007 | 122.58 | 122.5571 | 122.3602 | 122.5296 | 122.3694 | 122.6669 | -0.11902 | 122.3602 | 122.5296 | 122.6669 | 122.5571 | 122.3694 | 0.1236 | -122.5616
546.7812 | 122.699 | -122.438 | 0.027466 | -0.00061033 | 0.018918 | 0.0032898 | 0.013738 | -0.0079639 | -0.004219 | 0.0025486 | 0.15564 | -0.045776 | 0.16479 | 0.21057 | 0.16022 | 0.2655 | -0.09613 | 0.17395 | -0.027466 | -122.5342 | 122.6028 | -0.073242 | 122.5937 | 122.6486 | 0.13275 | -0.096131 | -0.054932 | -0.009155 | 122.3419 | 122.612 | 122.5983 | 122.3923 | 122.5937 | 122.4106 | 122.7036 | -0.096131 | 122.3923 | 122.5937 | 122.7036 | 122.5983 | 122.4106 | 0.13733 | -122.5616
547.8125 | 122.6074 | -122.4838 | 0.068665 | -0.00061033 | 0.025754 | 0.0067078 | 0.021001 | -0.0047595 | -0.003151 | 0.00041236 | 0.09613 | 0.004578 | 0.13275 | 0.12817 | 0.041199 | 0.13275 | 0.018311 | 0.027466 | -0.018311 | -122.644 | 122.6166 | -0.064087 | 122.58 | 122.612 | -0.027466 | -0.16022 | -0.086976 | -0.036621 | 122.5021 | 122.5113 | 122.525 | 122.4884 | 122.58 | 122.4655 | 122.6166 | -0.16022 | 122.4884 | 122.58 | 122.6166 | 122.525 | 122.4655 | 0.064086 | -122.7127
548.7812 | 122.7356 | -122.4335 | 0.054932 | -0.0082398 | 0.018918 | 0.0039306 | 0.013311 | -0.0073229 | -0.004219 | 0.0019076 | 0.14191 | -0.050354 | 0.17853 | 0.21057 | 0.16937 | 0.25177 | -0.10529 | 0.17853 | -0.041199 | -122.58 | 122.612 | -0.10529 | 122.5754 | 122.644 | 0.11444 | -0.14648 | -0.096131 | -0.036621 | 122.3282 | 122.612 | 122.6028 | 122.3831 | 122.5754 | 122.3923 | 122.6852 | -0.14648 | 122.3831 | 122.5754 | 122.6852 | 122.6028 | 122.3923 | 0.1236 | -122.6349
549.7812 | 122.7173 | -122.4518 | 0.045776 | -0.00061033 | 0.019773 | 0.0022218 | 0.012884 | -0.0081775 | -0.0029374 | 0.0025486 | 0.082397 | -0.050354 | 0.15564 | 0.14648 | 0.1236 | 0.2243 | -0.073242 | 0.10071 | -0.045776 | -122.6028 | 122.6074 | -0.09613 | 122.5342 | 122.5983 | 0.07782 | -0.15106 | -0.091552 | -0.073243 | 122.3785 | 122.5525 | 122.5754 | 122.4014 | 122.5342 | 122.406 | 122.6761 | -0.15106 | 122.4014 | 122.5342 | 122.6761 | 122.5754 | 122.406 | 0.10986 | -122.6486
550.7812 | 122.7036 | -122.4838 | 0.054932 | -0.00061033 | 0.021055 | 0.0030762 | 0.013738 | -0.0066821 | -0.00486 | 0.00062596 | 0.073242 | -0.036621 | 0.16022 | 0.12817 | 0.086975 | 0.20142 | -0.064087 | 0.082397 | -0.013733 | -122.5983 | 122.644 | -0.091553 | 122.5571 | 122.612 | 0.032043 | -0.11444 | -0.068665 | -0.086975 | 122.4197 | 122.5662 | 122.5708 | 122.4472 | 122.5571 | 122.4701 | 122.6852 | -0.11444 | 122.4472 | 122.5571 | 122.6852 | 122.5708 | 122.4701 | 0.10528 | -122.6532
551.7812 | 122.7127 | -122.4976 | 0.050354 | -0.015869 | 0.018064 | 0.0011536 | 0.014593 | -0.0098865 | -0.0063554 | 0.0029758 | 0.064087 | -0.045776 | 0.17395 | 0.15106 | 0.09613 | 0.21515 | -0.073242 | 0.10529 | -0.027466 | -122.6166 | 122.6715 | -0.09613 | 122.5616 | 122.6486 | 0.045776 | -0.11902 | -0.07782 | -0.10986 | 122.4243 | 122.6028 | 122.5937 | 122.4518 | 122.5616 | 122.4701 | 122.7127 | -0.11902 | 122.4518 | 122.5616 | 122.7127 | 122.5937 | 122.4701 | 0.1236 | -122.6669
552.7812 | 122.6807 | -122.5021 | 0.059509 | 0.0070192 | 0.024473 | 0.0039306 | 0.022497 | -0.0062549 | -0.004219 | 0.0036166 | 0.10529 | -0.018311 | 0.14191 | 0.15106 | 0.086975 | 0.17395 | -0.022888 | 0.068665 | -0.018311 | -122.6578 | 122.644 | -0.07782 | 122.6074 | 122.6532 | 0.027466 | -0.15564 | -0.07782 | -0.036621 | 122.4792 | 122.5708 | 122.5891 | 122.4838 | 122.6074 | 122.4838 | 122.6761 | -0.15564 | 122.4838 | 122.6074 | 122.6761 | 122.5891 | 122.4838 | 0.082398 | -122.7173
553.7812 | 122.731 | -122.4976 | 0.068665 | -0.0082398 | 0.019773 | 0.0022218 | 0.037023 | -0.0079639 | -0.0040054 | 0.029679 | 0.07782 | -0.036621 | 0.15564 | 0.1236 | 0.082397 | 0.19226 | -0.068665 | 0.082397 | -0.032043 | -122.6166 | 122.6532 | -0.10529 | 122.5754 | 122.6212 | 0.013732 | -0.11902 | -0.10071 | -0.07782 | 122.4289 | 122.58 | 122.58 | 122.4609 | 122.5754 | 122.4655 | 122.6898 | -0.11902 | 122.4609 | 122.5754 | 122.6898 | 122.58 | 122.4655 | 0.086975 | -122.6852
554.7812 | 122.7493 | -122.493 | 0.041199 | -0.00061033 | 0.019559 | 0.0045716 | 0.026342 | -0.0064685 | -0.0044328 | 0.017075 | 0.13733 | -0.045776 | 0.16937 | 0.17395 | 0.1236 | 0.2243 | -0.10986 | 0.10071 | -0.045776 | -122.644 | 122.6624 | -0.086975 | 122.6303 | 122.6669 | 0.082397 | -0.15106 | -0.086975 | -0.032044 | 122.3831 | 122.5937 | 122.6166 | 122.4472 | 122.6303 | 122.4472 | 122.7173 | -0.15106 | 122.4472 | 122.6303 | 122.7173 | 122.6166 | 122.4472 | 0.12817 | -122.6852
555.7812 | 122.7631 | -122.4884 | 0.041199 | -0.0082398 | 0.020841 | 0.003717 | 0.026983 | -0.010314 | -0.003151 | 0.015366 | 0.14648 | -0.059509 | 0.16479 | 0.18768 | 0.13733 | 0.24719 | -0.14191 | 0.1236 | -0.054932 | -122.6532 | 122.6532 | -0.10071 | 122.6349 | 122.6761 | 0.09613 | -0.16479 | -0.096131 | -0.018311 | 122.3465 | 122.612 | 122.6257 | 122.4289 | 122.6349 | 122.4335 | 122.7356 | -0.16479 | 122.4289 | 122.6349 | 122.7356 | 122.6257 | 122.4335 | 0.1236 | -122.6944
556.7812 | 122.7905 | -122.4747 | 0.045776 | -0.00061033 | 0.018918 | 0.0073486 | 0.029119 | -0.0079639 | -0.0044328 | 0.016434 | 0.16022 | -0.059509 | 0.1831 | 0.21057 | 0.15106 | 0.2655 | -0.16022 | 0.13733 | -0.068665 | -122.6532 | 122.6578 | -0.10528 | 122.6349 | 122.6852 | 0.10529 | -0.17853 | -0.11444 | -0.022888 | 122.3145 | 122.612 | 122.6257 | 122.4152 | 122.6349 | 122.406 | 122.7402 | -0.17853 | 122.4152 | 122.6349 | 122.7402 | 122.6257 | 122.406 | 0.13733 | -122.699
557.7969 | 122.7859 | -122.438 | 0.041199 | -0.00061033 | 0.018918 | 0.010553 | 0.028905 | -0.0066821 | -0.003151 | 0.017502 | 0.15106 | -0.041199 | 0.17853 | 0.17395 | 0.13275 | 0.25635 | -0.15564 | 0.11444 | -0.059509 | -122.6761 | 122.6166 | -0.082398 | 122.5891 | 122.612 | 0.091552 | -0.23804 | -0.10071 | -0.027466 | 122.2824 | 122.5525 | 122.5708 | 122.3969 | 122.5891 | 122.3785 | 122.6944 | -0.23804 | 122.3969 | 122.5891 | 122.6944 | 122.5708 | 122.3785 | 0.13733 | -122.7173
558.7812 | 122.7676 | -122.4838 | 0.018311 | -0.00061033 | 0.021268 | 0.0075622 | 0.029974 | -0.0066821 | -0.0050736 | 0.017929 | 0.14648 | -0.050354 | 0.16937 | 0.20599 | 0.14191 | 0.2655 | -0.16022 | 0.14191 | -0.054932 | -122.6669 | 122.6532 | -0.068665 | 122.6303 | 122.6898 | 0.1236 | -0.18311 | -0.073243 | -0.022889 | 122.3236 | 122.6257 | 122.6257 | 122.4335 | 122.6303 | 122.4289 | 122.7493 | -0.18311 | 122.4335 | 122.6303 | 122.7493 | 122.6257 | 122.4289 | 0.15106 | -122.6852
559.7812 | 122.8134 | -122.4747 | 0.036621 | 0.0070192 | 0.021055 | 0.0032898 | 0.027624 | -0.0071093 | -0.0046464 | 0.019211 | 0.16937 | -0.054932 | 0.16937 | 0.20599 | 0.14191 | 0.2655 | -0.16937 | 0.12817 | -0.054932 | -122.699 | 122.644 | -0.091553 | 122.644 | 122.6807 | 0.10529 | -0.22431 | -0.091553 | 0 | 122.3053 | 122.6028 | 122.6166 | 122.4197 | 122.644 | 122.4197 | 122.7402 | -0.22431 | 122.4197 | 122.644 | 122.7402 | 122.6166 | 122.4197 | 0.13275 | -122.7356
560.7812 | 122.8226 | -122.493 | 0.036621 | -0.0082398 | 0.019987 | 0.0052124 | 0.031896 | -0.0056141 | -0.0052872 | 0.017075 | 0.13733 | -0.045776 | 0.15564 | 0.17395 | 0.14191 | 0.25177 | -0.14648 | 0.11444 | -0.050354 | -122.6944 | 122.6486 | -0.082397 | 122.6303 | 122.6669 | 0.10529 | -0.20142 | -0.086975 | -0.018311 | 122.3465 | 122.6074 | 122.6349 | 122.4472 | 122.6303 | 122.4426 | 122.7448 | -0.20142 | 122.4472 | 122.6303 | 122.7448 | 122.6349 | 122.4426 | 0.11902 | -122.731
561.7812 | 122.8317 | -122.4884 | 0.027466 | -0.00061033 | 0.021268 | 0.0049988 | 0.030187 | -0.0051867 | -0.0040054 | 0.017075 | 0.16479 | -0.054932 | 0.17853 | 0.20599 | 0.15564 | 0.27008 | -0.16022 | 0.1236 | -0.036621 | -122.7036 | 122.6669 | -0.082398 | 122.6532 | 122.6944 | 0.12817 | -0.21515 | -0.064087 | -0.013733 | 122.3282 | 122.612 | 122.644 | 122.4335 | 122.6532 | 122.4518 | 122.7585 | -0.21515 | 122.4335 | 122.6532 | 122.7585 | 122.644 | 122.4518 | 0.15106 | -122.731
562.7812 | 122.6852 | -122.5433 | 0.082397 | -0.0082398 | 0.025541 | 0.0067078 | 0.033178 | -0.0058277 | -0.004219 | 0.019425 | 0.059509 | 0 | 0.13275 | 0.059509 | 0.027466 | 0.12817 | 0.032043 | -0.036621 | -0.004578 | -122.7631 | 122.6761 | -0.082397 | 122.6028 | 122.6028 | -0.054931 | -0.21973 | -0.086975 | -0.073242 | 122.5754 | 122.5067 | 122.5708 | 122.5433 | 122.6028 | 122.5388 | 122.6715 | -0.21973 | 122.5433 | 122.6028 | 122.6715 | 122.5708 | 122.5388 | 0.050354 | -122.8455
563.7812 | 122.6898 | -122.5388 | 0.091553 | -0.00061033 | 0.025113 | 0.0058534 | 0.037023 | -0.0036915 | -0.0067826 | 0.027329 | 0.041199 | 0 | 0.11902 | 0.054932 | 0 | 0.10986 | 0.059509 | -0.041199 | -0.018311 | -122.7585 | 122.6578 | -0.091553 | 122.58 | 122.5937 | -0.091553 | -0.21973 | -0.10986 | -0.07782 | 122.5983 | 122.4976 | 122.5388 | 122.5388 | 122.58 | 122.5204 | 122.6486 | -0.21973 | 122.5388 | 122.58 | 122.6486 | 122.5388 | 122.5204 | 0.027466 | -122.85
564.7812 | 122.7585 | -122.5433 | 0.073242 | -0.0082398 | 0.02255 | 0.0075622 | 0.030828 | -0.0047595 | -0.0040054 | 0.022202 | 0.054932 | -0.013733 | 0.11902 | 0.10071 | 0.054932 | 0.14648 | -0.018311 | -0.009155 | -0.027466 | -122.7402 | 122.6624 | -0.086975 | 122.5983 | 122.644 | -0.01831 | -0.19684 | -0.10071 | -0.064087 | 122.525 | 122.5342 | 122.5983 | 122.5296 | 122.5983 | 122.5159 | 122.6898 | -0.19684 | 122.5296 | 122.5983 | 122.6898 | 122.5983 | 122.5159 | 0.045777 | -122.8134
565.7812 | 122.7173 | -122.5433 | 0.086975 | -0.015869 | 0.025113 | 0.0086304 | 0.036596 | -0.0058277 | -0.0022964 | 0.024979 | 0.054932 | -0.004578 | 0.1236 | 0.054932 | 0.032043 | 0.12817 | 0.027466 | -0.018311 | -0.009155 | -122.7676 | 122.6669 | -0.091553 | 122.5983 | 122.5983 | -0.054932 | -0.2243 | -0.09613 | -0.068664 | 122.5708 | 122.525 | 122.5754 | 122.5388 | 122.5983 | 122.5342 | 122.6715 | -0.2243 | 122.5388 | 122.5983 | 122.6715 | 122.5754 | 122.5342 | 0.036621 | -122.8546
566.7812 | 122.731 | -122.5388 | 0.086975 | -0.00061033 | 0.025113 | 0.0075622 | 0.034673 | -0.0043323 | -0.0033646 | 0.023484 | 0.050354 | 0.013733 | 0.13733 | 0.068665 | 0.027466 | 0.13275 | 0.027466 | -0.036621 | -0.013733 | -122.8088 | 122.6761 | -0.073242 | 122.5891 | 122.6074 | -0.059509 | -0.27008 | -0.10071 | -0.086975 | 122.5662 | 122.5021 | 122.5662 | 122.5525 | 122.5891 | 122.525 | 122.6715 | -0.27008 | 122.5525 | 122.5891 | 122.6715 | 122.5662 | 122.525 | 0.050354 | -122.8958
567.7969 | 122.7356 | -122.5708 | 0.073242 | 0.0070192 | 0.023404 | 0.007135 | 0.035101 | -0.0036915 | -0.0035782 | 0.024338 | 0.050354 | 0.004578 | 0.12817 | 0.086975 | 0.036621 | 0.12817 | 0.036621 | -0.009155 | -0.009155 | -122.7402 | 122.699 | -0.068664 | 122.6212 | 122.6578 | -0.036621 | -0.16937 | -0.082397 | -0.07782 | 122.6074 | 122.5616 | 122.6074 | 122.5754 | 122.6212 | 122.5616 | 122.699 | -0.16937 | 122.5754 | 122.6212 | 122.699 | 122.6074 | 122.5616 | 0.054932 | -122.8134
568.7812 | 122.6761 | -122.5845 | 0.073242 | -0.00061033 | 0.022977 | 0.0039306 | 0.036596 | -0.0036915 | -0.0029374 | 0.025193 | 0.041199 | 0 | 0.11902 | 0.064087 | 0.027466 | 0.11444 | 0.027466 | -0.036621 | -0.004578 | -122.7905 | 122.7036 | -0.073242 | 122.6257 | 122.6486 | -0.045776 | -0.20599 | -0.07782 | -0.07782 | 122.612 | 122.5479 | 122.612 | 122.5845 | 122.6257 | 122.58 | 122.699 | -0.20599 | 122.5845 | 122.6257 | 122.699 | 122.612 | 122.58 | 0.045777 | -122.8638
569.7812 | 122.6761 | -122.5571 | 0.091553 | -0.00061033 | 0.027677 | 0.0099122 | 0.045354 | -0.0036915 | -0.0046464 | 0.033951 | 0.036621 | 0.004578 | 0.15106 | 0.059509 | 0 | 0.11444 | 0.054932 | -0.050354 | -0.004578 | -122.7951 | 122.7081 | -0.086975 | 122.5937 | 122.6166 | -0.091553 | -0.23804 | -0.096131 | -0.11444 | 122.612 | 122.5067 | 122.5571 | 122.5616 | 122.5937 | 122.5525 | 122.6715 | -0.23804 | 122.5616 | 122.5937 | 122.6715 | 122.5571 | 122.5525 | 0.059509 | -122.8867
570.7812 | 122.7814 | -122.5342 | 0.059509 | -0.0082398 | 0.023191 | 0.0075622 | 0.038091 | -0.0034777 | -0.0029374 | 0.022843 | 0.091553 | 0.004578 | 0.13275 | 0.13733 | 0.082397 | 0.18768 | 0.004578 | 0.073242 | -0.004578 | -122.7951 | 122.6669 | -0.054931 | 122.6257 | 122.6715 | 0.022888 | -0.26093 | -0.064087 | -0.041198 | 122.5388 | 122.6074 | 122.6166 | 122.5388 | 122.6257 | 122.5296 | 122.7219 | -0.26093 | 122.5388 | 122.6257 | 122.7219 | 122.6166 | 122.5296 | 0.073242 | -122.8546
571.7812 | 122.7722 | -122.5662 | 0.064087 | -0.015869 | 0.026822 | 0.010553 | 0.039159 | -0.0028369 | -0.003151 | 0.02797 | 0.073242 | -0.013733 | 0.13733 | 0.07782 | 0.059509 | 0.13733 | 0.022888 | 0.009155 | -0.018311 | -122.7951 | 122.7036 | -0.07782 | 122.6395 | 122.644 | -0.004578 | -0.22888 | -0.082398 | -0.064087 | 122.5891 | 122.5754 | 122.6257 | 122.5525 | 122.6395 | 122.5479 | 122.7036 | -0.22888 | 122.5525 | 122.6395 | 122.7036 | 122.6257 | 122.5479 | 0.073242 | -122.8592
572.7812 | 123.2071 | -122.5616 | 0.07782 | -0.0082398 | 0.025327 | 0.0064942 | 0.043432 | -0.0032641 | -0.0018692 | 0.034165 | 0.11902 | 0 | 0.13733 | 0.10986 | 0.068665 | 0.16022 | 0.009155 | 0.045776 | -0.013733 | -122.818 | 122.699 | -0.07782 | 122.6807 | 122.6715 | -0.009155 | -0.25635 | -0.091553 | -0.01831 | 122.5708 | 122.6074 | 122.6303 | 122.5616 | 122.6807 | 122.5479 | 122.7219 | -0.25635 | 122.5616 | 122.6807 | 122.7219 | 122.6303 | 122.5479 | 0.059509 | -122.8958
573.7812 | 122.7539 | -122.5662 | 0.082397 | -0.00061033 | 0.02725 | 0.010126 | 0.060522 | -0.0047595 | -0.0044328 | 0.060868 | 0.09613 | 0.004578 | 0.15106 | 0.13275 | 0.07782 | 0.1831 | 0 | 0.07782 | -0.045776 | -122.7951 | 122.7173 | -0.077819 | 122.6624 | 122.699 | -0.004577 | -0.22888 | -0.12817 | -0.054932 | 122.5662 | 122.644 | 122.644 | 122.5708 | 122.6624 | 122.5204 | 122.7493 | -0.22888 | 122.5708 | 122.6624 | 122.7493 | 122.644 | 122.5204 | 0.068665 | -122.8775
574.7812 | 122.8363 | -122.5845 | 0.082397 | -0.00061033 | 0.026182 | 0.0058534 | 0.041296 | -0.0036915 | -0.0037918 | 0.03096 | 0.086975 | -0.009155 | 0.12817 | 0.1236 | 0.091553 | 0.19226 | 0.004578 | 0.086975 | -0.032043 | -122.8043 | 122.7127 | -0.091552 | 122.6715 | 122.7081 | 0.009156 | -0.21973 | -0.11444 | -0.041199 | 122.5891 | 122.6715 | 122.6761 | 122.5754 | 122.6715 | 122.5525 | 122.7768 | -0.21973 | 122.5754 | 122.6715 | 122.7768 | 122.6761 | 122.5525 | 0.045777 | -122.8867
575.7812 | 122.818 | -122.5845 | 0.068665 | -0.00061033 | 0.025754 | 0.0064942 | 0.037878 | -0.0034777 | -0.003151 | 0.03032 | 0.086975 | 0.004578 | 0.15106 | 0.11902 | 0.091553 | 0.16937 | 0.013733 | 0.054932 | -0.013733 | -122.8226 | 122.7356 | -0.064087 | 122.6715 | 122.7036 | 0.022888 | -0.23804 | -0.082398 | -0.064087 | 122.5983 | 122.6395 | 122.6761 | 122.5891 | 122.6715 | 122.5708 | 122.7539 | -0.23804 | 122.5891 | 122.6715 | 122.7539 | 122.6761 | 122.5708 | 0.082397 | -122.8912
576.7812 | 122.7905 | -122.5937 | 0.07782 | -0.0082398 | 0.027677 | 0.0075622 | 0.072698 | -0.0066821 | -0.0035782 | 0.070267 | 0.073242 | 0.009155 | 0.13275 | 0.10529 | 0.068665 | 0.15564 | 0.032043 | 0.045776 | -0.004578 | -122.8271 | 122.7264 | -0.068665 | 122.6669 | 122.699 | -0.009155 | -0.23346 | -0.082398 | -0.059509 | 122.6257 | 122.6395 | 122.6624 | 122.6028 | 122.6669 | 122.5891 | 122.7493 | -0.23346 | 122.6028 | 122.6669 | 122.7493 | 122.6624 | 122.5891 | 0.054931 | -122.905
577.7969 | 122.8455 | -122.5616 | 0.050354 | -0.015869 | 0.022123 | 0.0062806 | 0.042577 | -0.0034777 | -0.0050736 | 0.036515 | 0.10071 | -0.059509 | 0.16022 | 0.10986 | 0.10071 | 0.23346 | -0.086975 | 0.086975 | -0.041199 | -122.818 | 122.7219 | -0.10986 | 122.6624 | 122.6715 | 0.050354 | -0.25635 | -0.091553 | -0.059509 | 122.4747 | 122.6486 | 122.6624 | 122.5021 | 122.6624 | 122.5204 | 122.7951 | -0.25635 | 122.5021 | 122.6624 | 122.7951 | 122.6624 | 122.5204 | 0.10986 | -122.8683
578.7812 | 122.7585 | -122.5204 | 0.14191 | -0.0082398 | 0.063993 | 0.006067 | 0.75821 | -0.0056141 | -0.0033646 | 0.7968 | 0.13733 | 0.073242 | 0.17853 | 0.004578 | -0.99335 | 0.041199 | -0.082397 | -0.064087 | -0.018311 | -122.6669 | 122.699 | -0.068665 | 122.6578 | 122.525 | -1.1353 | -0.14648 | -0.16022 | -0.041199 | 122.4381 | 122.4564 | 121.5271 | 122.5937 | 122.6578 | 122.5021 | 122.5616 | -0.14648 | 122.5937 | 122.6578 | 122.5616 | 121.5271 | 122.5021 | 0.036621 | -122.8088
579.7812 | 122.7814 | -122.612 | 0.086975 | -0.0082398 | 0.033445 | 0.007776 | 0.24039 | -0.0073229 | -0.003151 | 0.23262 | 0.082397 | 0.022888 | 0.14648 | 0.064087 | -0.21973 | 0.10529 | 0.041199 | 0.013733 | 0.004578 | -122.8088 | 122.7585 | -0.064087 | 122.6944 | 122.6761 | -0.3067 | -0.19684 | -0.082397 | -0.064087 | 122.6532 | 122.6257 | 122.3923 | 122.6349 | 122.6944 | 122.6166 | 122.7173 | -0.19684 | 122.6349 | 122.6944 | 122.7173 | 122.3923 | 122.6166 | 0.059509 | -122.8958
580.7812 | 122.8088 | -122.5571 | 0.17395 | -0.00061033 | 0.024686 | 0.0096986 | 0.053045 | -0.0056141 | -0.0027238 | 0.081375 | 0.050354 | 0.009155 | 0.13275 | 0.15106 | 0.13275 | 0.22888 | 0.16479 | 0.11444 | 0.064087 | -122.7127 | 122.6898 | -0.16479 | 122.6074 | 122.7081 | -0.041199 | -0.15564 | -0.10986 | -0.082397 | 122.7219 | 122.6715 | 122.6898 | 122.5662 | 122.6074 | 122.6212 | 122.7859 | -0.15564 | 122.5662 | 122.6074 | 122.7859 | 122.6898 | 122.6212 | -0.041199 | -122.8867
581.7812 | 122.8638 | -122.6578 | 0.086975 | -0.00061033 | 0.021482 | 0.0064942 | 0.055181 | -0.0066821 | -0.0037918 | 0.044846 | 0.068665 | -0.004578 | 0.13733 | 0.09613 | 0.059509 | 0.15106 | 0.027466 | 0.041199 | 0 | -122.8271 | 122.7951 | -0.091553 | 122.7264 | 122.7539 | -0.027466 | -0.16937 | -0.086975 | -0.068664 | 122.6852 | 122.699 | 122.7173 | 122.6532 | 122.7264 | 122.6578 | 122.8088 | -0.16937 | 122.6532 | 122.7264 | 122.8088 | 122.7173 | 122.6578 | 0.050354 | -122.9141
582.7812 | 122.8134 | -122.6669 | 0.059509 | -0.0082398 | 0.018918 | 0.0039306 | 0.05219 | -0.0060413 | -0.0018692 | 0.051041 | 0.018311 | -0.009155 | 0.11902 | 0.059509 | 0.032043 | 0.12817 | 0.09613 | 0.018311 | 0.004578 | -122.8683 | 122.7859 | -0.068664 | 122.6852 | 122.7264 | -0.027466 | -0.20142 | -0.054931 | -0.10071 | 122.7631 | 122.6852 | 122.699 | 122.6578 | 122.6852 | 122.6715 | 122.7951 | -0.20142 | 122.6578 | 122.6852 | 122.7951 | 122.699 | 122.6715 | 0.05951 | -122.9279
583.7812 | 122.8317 | -122.6395 | 0.068665 | -0.00061033 | 0.016569 | 0.008844 | 0.046636 | -0.0060413 | -0.00486 | 0.037369 | 0.12817 | -0.059509 | 0.16022 | 0.16479 | 0.11444 | 0.20142 | -0.018311 | 0.1236 | -0.027466 | -122.7997 | 122.7997 | -0.12817 | 122.7676 | 122.8043 | 0.045776 | -0.16022 | -0.096131 | -0.032043 | 122.6212 | 122.7631 | 122.7539 | 122.58 | 122.7676 | 122.612 | 122.8409 | -0.16022 | 122.58 | 122.7676 | 122.8409 | 122.7539 | 122.612 | 0.091552 | -122.8683
584.7812 | 122.7951 | -122.6944 | 0.064087 | -0.015869 | 0.017423 | 0.006067 | 0.048986 | -0.0060413 | -0.0016556 | 0.037369 | 0.086975 | -0.027466 | 0.15106 | 0.09613 | 0.041199 | 0.16022 | 0.050354 | 0.045776 | -0.004578 | -122.8134 | 122.8455 | -0.091553 | 122.7814 | 122.7905 | -0.022888 | -0.11902 | -0.068665 | -0.064087 | 122.7448 | 122.7402 | 122.7356 | 122.6669 | 122.7814 | 122.6898 | 122.8546 | -0.11902 | 122.6669 | 122.7814 | 122.8546 | 122.7356 | 122.6898 | 0.086975 | -122.8775
585.7812 | 122.8043 | -122.6761 | 0.073242 | 0.0070192 | 0.019987 | 0.0041444 | 0.052618 | -0.0049731 | -0.0016556 | 0.043564 | 0.036621 | -0.022888 | 0.1236 | 0.073242 | 0.045776 | 0.10986 | 0.07782 | 0.032043 | 0.004578 | -122.8546 | 122.7997 | -0.09613 | 122.7127 | 122.7493 | -0.027466 | -0.17853 | -0.068664 | -0.086975 | 122.7539 | 122.7081 | 122.7219 | 122.6532 | 122.7127 | 122.6807 | 122.7859 | -0.17853 | 122.6532 | 122.7127 | 122.7859 | 122.7219 | 122.6807 | 0.050354 | -122.9279
586.7812 | 122.7859 | -122.699 | 0.082397 | 0.0070192 | 0.019559 | 0.00051276 | 0.052618 | -0.0066821 | -0.0037918 | 0.041642 | 0.073242 | -0.027466 | 0.13733 | 0.091553 | 0.036621 | 0.11902 | 0.041199 | 0.041199 | 0.013733 | -122.8271 | 122.8363 | -0.10986 | 122.7722 | 122.7905 | -0.045776 | -0.12817 | -0.068664 | -0.064087 | 122.7402 | 122.7402 | 122.7356 | 122.6715 | 122.7722 | 122.7127 | 122.818 | -0.12817 | 122.6715 | 122.7722 | 122.818 | 122.7356 | 122.7127 | 0.054932 | -122.9095
587.7969 | 122.8134 | -122.6898 | 0.082397 | -0.00061033 | 0.019559 | 0.00093996 | 0.058172 | -0.0066821 | -0.0033646 | 0.046769 | 0.027466 | 0.004578 | 0.11444 | 0.068665 | 0.022888 | 0.09613 | 0.082397 | 0.018311 | 0.013733 | -122.8134 | 122.8043 | -0.077819 | 122.7173 | 122.7585 | -0.059509 | -0.1236 | -0.068664 | -0.086975 | 122.7722 | 122.7081 | 122.7127 | 122.6944 | 122.7173 | 122.7036 | 122.7859 | -0.1236 | 122.6944 | 122.7173 | 122.7859 | 122.7127 | 122.7036 | 0.032044 | -122.8958
588.7812 | 122.8088 | -122.7036 | 0.068665 | -0.00061033 | 0.018705 | 0.0067078 | 0.061163 | -0.0073229 | -0.0033646 | 0.0551 | 0.068665 | -0.009155 | 0.13275 | 0.091553 | 0.032043 | 0.13275 | 0.068665 | 0.032043 | -0.004578 | -122.8409 | 122.8363 | -0.07782 | 122.7722 | 122.7951 | -0.036622 | -0.13733 | -0.073243 | -0.064086 | 122.7722 | 122.7356 | 122.7356 | 122.6944 | 122.7722 | 122.699 | 122.8363 | -0.13733 | 122.6944 | 122.7722 | 122.8363 | 122.7356 | 122.699 | 0.064086 | -122.9095
589.7812 | 122.9095 | -122.6715 | 0.073242 | -0.00061033 | 0.021268 | 0.004358 | 0.1167 | -0.0081775 | -0.0035782 | 0.11748 | 0.10071 | -0.032043 | 0.16479 | 0.10529 | 0.054932 | 0.12817 | 0.009155 | 0.064087 | -0.022888 | -122.8271 | 122.8363 | -0.10529 | 122.7722 | 122.7768 | -0.01831 | -0.15564 | -0.09613 | -0.064087 | 122.6807 | 122.7356 | 122.7264 | 122.6395 | 122.7722 | 122.6486 | 122.7997 | -0.15564 | 122.6395 | 122.7722 | 122.7997 | 122.7264 | 122.6486 | 0.091553 | -122.9004
590.7812 | 122.9553 | -122.3877 | 0.24261 | -0.00061033 | 0.1755 | 0.002008 | 0.11735 | -0.0068957 | -0.0052872 | 0.25676 | 0.35706 | 0.16479 | 0.31586 | 0.38452 | 0.33417 | 0.46234 | -0.041199 | 0.26093 | 0.15564 | -122.5296 | 122.7036 | -0.07782 | 122.7448 | 122.7722 | 0.091552 | -0.14191 | -0.086975 | 0.041199 | 122.3465 | 122.6486 | 122.7219 | 122.5525 | 122.7448 | 122.5433 | 122.85 | -0.14191 | 122.5525 | 122.7448 | 122.85 | 122.7219 | 122.5433 | 0.073242 | -122.7722
591.7812 | 122.9004 | -122.6486 | 0.054932 | -0.0082398 | 0.016782 | 0.008844 | 0.063299 | -0.0088183 | -0.00486 | 0.057663 | 0.13275 | -0.032043 | 0.17853 | 0.18768 | 0.13275 | 0.23346 | -0.064087 | 0.14648 | -0.032043 | -122.8134 | 122.8271 | -0.086975 | 122.7814 | 122.8363 | 0.077819 | -0.16479 | -0.086975 | -0.045777 | 122.5845 | 122.7951 | 122.7814 | 122.6166 | 122.7814 | 122.6166 | 122.8821 | -0.16479 | 122.6166 | 122.7814 | 122.8821 | 122.7814 | 122.6166 | 0.1236 | -122.8683
592.7812 | 122.9279 | -122.5388 | 0.16479 | -0.00061033 | 0.10138 | 0.0045716 | 0.1182 | -0.0081775 | -0.00486 | 0.19994 | 0.2655 | 0.059509 | 0.26093 | 0.32959 | 0.25177 | 0.3891 | -0.009155 | 0.29297 | 0.07782 | -122.6303 | 122.7997 | -0.10529 | 122.8043 | 122.8683 | 0.086975 | -0.091553 | -0.086975 | 0.004578 | 122.5296 | 122.8317 | 122.7905 | 122.5983 | 122.8043 | 122.6166 | 122.9279 | -0.091553 | 122.5983 | 122.8043 | 122.9279 | 122.7905 | 122.6166 | 0.09613 | -122.7951
593.7812 | 122.7768 | -122.4838 | 0.16022 | -0.00061033 | 0.19238 | 0.0032898 | 0.63025 | -0.0088183 | -0.0037918 | 0.72759 | 0.36163 | 0.1831 | 0.36163 | 0.16937 | -0.29297 | 0.21515 | -0.032043 | 0.16022 | 0.045776 | -122.5662 | 122.8455 | 0.022888 | 122.8455 | 122.6532 | -0.45319 | -0.082397 | -0.11444 | 0 | 122.4518 | 122.644 | 122.1909 | 122.6669 | 122.8455 | 122.5296 | 122.699 | -0.082397 | 122.6669 | 122.8455 | 122.699 | 122.1909 | 122.5296 | 0.20142 | -122.7264
594.7812 | 122.0673 | -121.4127 | 0.37537 | -0.00061033 | 0.18768 | -0.00098264 | 0.041082 | -0.0049731 | -0.00486 | 0.2527 | 0.44861 | 0.20142 | 0.3891 | -0.4303 | -0.44861 | -0.43945 | -0.80566 | -1.8951 | 0.26093 | -121.5591 | 121.8018 | -0.17395 | 121.8613 | 120.9824 | -0.82397 | -0.14648 | -0.11444 | 0.059509 | 120.607 | 119.5175 | 120.9641 | 121.6141 | 121.8613 | 121.6736 | 120.9732 | -0.14648 | 121.6141 | 121.8613 | 120.9732 | 120.9641 | 121.6736 | 0.013733 | -121.9345
595.7812 | 122.2961 | -122.0123 | 0.064087 | -0.00061033 | 0.036649 | 0.003717 | 0.024206 | -0.0083911 | -0.0055008 | 0.031815 | 0.15564 | -0.032043 | 0.16937 | 0.1831 | -0.32044 | 0.21973 | -0.13275 | 0.10986 | -0.022888 | -122.1085 | 122.1817 | -0.09613 | 122.168 | 122.1954 | -0.38452 | -0.09613 | -0.086975 | -0.013733 | 121.8796 | 122.1222 | 121.6919 | 121.9803 | 122.168 | 121.9894 | 122.2321 | -0.09613 | 121.9803 | 122.168 | 122.2321 | 121.6919 | 121.9894 | 0.10529 | -122.1725
596.7812 | 122.3831 | -122.0993 | 0.068665 | -0.0082398 | 0.037931 | 0.0028626 | 0.02271 | -0.0083911 | -0.0044328 | 0.032242 | 0.13733 | -0.041199 | 0.19226 | 0.13733 | 0.009155 | 0.19684 | -0.14648 | 0.036621 | -0.013733 | -122.2046 | 122.2916 | -0.10986 | 122.2366 | 122.2366 | -0.05951 | -0.10529 | -0.082398 | -0.054932 | 121.9528 | 122.1359 | 122.1085 | 122.0581 | 122.2366 | 122.0856 | 122.2961 | -0.10529 | 122.0581 | 122.2366 | 122.2961 | 122.1085 | 122.0856 | 0.1236 | -122.2733
597.7969 | 122.3465 | -121.2021 | 0.91553 | -0.00061033 | 0.63543 | 0.0084168 | 0.38437 | -0.0077503 | -0.0012284 | 1.0083 | 0.92926 | 0.73242 | 0.83771 | -1.5152 | 0.45776 | -1.474 | -1.8219 | -4.6921 | 0.79651 | -121.3028 | 122.0398 | -0.1831 | 122.1313 | 119.6869 | -0.45776 | -0.10071 | -0.11902 | 0.091552 | 119.3802 | 116.51 | 121.6599 | 121.9345 | 122.1313 | 121.9986 | 119.7281 | -0.10071 | 121.9345 | 122.1313 | 119.7281 | 121.6599 | 121.9986 | -0.077819 | -122.2183
598.7812 | 122.4152 | -122.1863 | 0.068665 | -0.00061033 | 0.03259 | 0.0039306 | 0.028051 | -0.0064685 | -0.0029374 | 0.033097 | 0.091553 | -0.036621 | 0.14648 | 0.10986 | 0.054932 | 0.16022 | -0.10529 | 0.009155 | -0.018311 | -122.319 | 122.3328 | -0.10529 | 122.2778 | 122.2961 | -0.013733 | -0.13275 | -0.086976 | -0.054931 | 122.081 | 122.1954 | 122.2412 | 122.1497 | 122.2778 | 122.168 | 122.3465 | -0.13275 | 122.1497 | 122.2778 | 122.3465 | 122.2412 | 122.168 | 0.077819 | -122.3877
599.7812 | 122.4518 | -122.2092 | 0.054932 | -0.00061033 | 0.032163 | 0.0011536 | 0.03211 | -0.0101 | -0.0040054 | 0.031388 | 0.09613 | -0.032043 | 0.13733 | 0.14191 | 0.07782 | 0.20599 | -0.09613 | 0.054932 | -0.027466 | -122.3602 | 122.3465 | -0.086975 | 122.3053 | 122.3511 | 0.022888 | -0.15106 | -0.082398 | -0.041199 | 122.113 | 122.2641 | 122.287 | 122.1771 | 122.3053 | 122.1817 | 122.4152 | -0.15106 | 122.1771 | 122.3053 | 122.4152 | 122.287 | 122.1817 | 0.082397 | -122.4152
600.7812 | 122.4609 | -122.2229 | 0.054932 | -0.0082398 | 0.030668 | 0.0096986 | 0.02976 | -0.0071093 | -0.0050736 | 0.03032 | 0.082397 | -0.027466 | 0.16022 | 0.10986 | 0.064087 | 0.16937 | -0.086975 | 0.032043 | -0.013733 | -122.3511 | 122.3831 | -0.082398 | 122.3053 | 122.3328 | 0.009155 | -0.12817 | -0.068665 | -0.07782 | 122.1359 | 122.2549 | 122.287 | 122.1954 | 122.3053 | 122.2092 | 122.3923 | -0.12817 | 122.1954 | 122.3053 | 122.3923 | 122.287 | 122.2092 | 0.10528 | -122.406
601.7812 | 122.5113 | -122.2778 | 0.064087 | -0.0082398 | 0.030881 | 0.0056396 | 0.030187 | -0.0098865 | -0.0044328 | 0.02797 | 0.07782 | -0.041199 | 0.16937 | 0.13733 | -0.10986 | 0.20599 | -0.09613 | 0.064087 | -0.041199 | -122.3831 | 122.4472 | -0.10529 | 122.3557 | 122.4152 | -0.17395 | -0.10529 | -0.10529 | -0.091553 | 122.1817 | 122.3419 | 122.168 | 122.2366 | 122.3557 | 122.2366 | 122.4838 | -0.10529 | 122.2366 | 122.3557 | 122.4838 | 122.168 | 122.2366 | 0.10529 | -122.4472
602.7812 | 122.5296 | -122.2641 | 0.045776 | 0.0070192 | 0.030881 | 0.0017944 | 0.033605 | -0.0101 | -0.0035782 | 0.03331 | 0.10529 | -0.059509 | 0.17853 | 0.15564 | -0.18768 | 0.18768 | -0.10986 | 0.050354 | -0.045776 | -122.4243 | 122.4426 | -0.10528 | 122.3694 | 122.4197 | -0.23346 | -0.16022 | -0.091552 | -0.073242 | 122.1542 | 122.3145 | 122.0764 | 122.2046 | 122.3694 | 122.2183 | 122.4518 | -0.16022 | 122.2046 | 122.3694 | 122.4518 | 122.0764 | 122.2183 | 0.13275 | -122.4701
603.7812 | 122.4838 | -122.2641 | 0.054932 | 0.0070192 | 0.034299 | 0.0049988 | 0.040014 | -0.0088183 | -0.00486 | 0.037369 | 0.14191 | -0.054932 | 0.1831 | 0.16479 | -0.11902 | 0.20142 | -0.13733 | 0.059509 | -0.045776 | -122.4335 | 122.4472 | -0.10986 | 122.406 | 122.4289 | -0.17395 | -0.16937 | -0.10071 | -0.041198 | 122.1268 | 122.3236 | 122.1451 | 122.2092 | 122.406 | 122.2183 | 122.4655 | -0.16937 | 122.2092 | 122.406 | 122.4655 | 122.1451 | 122.2183 | 0.12817 | -122.4884
604.7812 | 122.6074 | -122.2366 | 0.036621 | -0.00061033 | 0.040708 | 0.0082032 | 0.033819 | -0.0081775 | -0.00486 | 0.035447 | 0.17853 | -0.041199 | 0.18768 | 0.20142 | -0.46234 | 0.22888 | -0.19684 | 0.068665 | -0.041199 | -122.438 | 122.4243 | -0.07782 | 122.4152 | 122.438 | -0.49896 | -0.20142 | -0.07782 | -0.009155 | 122.0398 | 122.3053 | 121.7743 | 122.1954 | 122.4152 | 122.1954 | 122.4655 | -0.20142 | 122.1954 | 122.4152 | 122.4655 | 121.7743 | 122.1954 | 0.15106 | -122.4747
605.7812 | 122.5937 | -122.2549 | 0.059509 | -0.00061033 | 0.046262 | 0.0030762 | 0.035955 | -0.0098865 | -0.0027238 | 0.042282 | 0.16937 | -0.009155 | 0.1831 | 0.16479 | -0.37079 | 0.21057 | -0.16937 | 0.032043 | -0.027466 | -122.4747 | 122.438 | -0.068664 | 122.4243 | 122.4197 | -0.4303 | -0.21973 | -0.086975 | -0.013732 | 122.0856 | 122.287 | 121.8842 | 122.2458 | 122.4243 | 122.2275 | 122.4655 | -0.21973 | 122.2458 | 122.4243 | 122.4655 | 121.8842 | 122.2275 | 0.1236 | -122.5342
606.7812 | 122.612 | -122.2595 | 0.073242 | -0.00061033 | 0.051389 | 0.010126 | 0.032751 | -0.0071093 | -0.0025102 | 0.042923 | 0.17395 | -0.032043 | 0.19226 | 0.16479 | -0.48523 | 0.20599 | -0.2243 | 0.018311 | -0.027466 | -122.4564 | 122.4518 | -0.10529 | 122.4335 | 122.4243 | -0.55847 | -0.19684 | -0.10071 | -0.018311 | 122.0352 | 122.2778 | 121.7743 | 122.2275 | 122.4335 | 122.2321 | 122.4655 | -0.19684 | 122.2275 | 122.4335 | 122.4655 | 121.7743 | 122.2321 | 0.11902 | -122.5296
607.7969 | 122.5754 | -122.2229 | 0.07782 | -0.00061033 | 0.056089 | 0.0086304 | 0.033819 | -0.0051867 | -0.0022964 | 0.05275 | 0.21057 | -0.009155 | 0.20142 | 0.15106 | -0.3479 | 0.18768 | -0.23346 | -0.022888 | -0.022888 | -122.4701 | 122.4243 | -0.086975 | 122.4335 | 122.374 | -0.42572 | -0.24719 | -0.10071 | 0.009155 | 121.9894 | 122.2 | 121.875 | 122.2137 | 122.4335 | 122.2 | 122.4106 | -0.24719 | 122.2137 | 122.4335 | 122.4106 | 121.875 | 122.2 | 0.1236 | -122.5479
608.7812 | 122.5937 | -122.2595 | 0.064087 | -0.00061033 | 0.048398 | 0.0094848 | 0.027196 | -0.0066821 | -0.0035782 | 0.043991 | 0.16937 | -0.022888 | 0.20599 | 0.13733 | -0.30212 | 0.21057 | -0.21057 | -0.004578 | -0.027466 | -122.4655 | 122.4655 | -0.086975 | 122.4289 | 122.3969 | -0.36621 | -0.20599 | -0.091553 | -0.036621 | 122.049 | 122.2549 | 121.9574 | 122.2366 | 122.4289 | 122.2321 | 122.4701 | -0.20599 | 122.2366 | 122.4289 | 122.4701 | 121.9574 | 122.2321 | 0.14191 | -122.5296
609.7812 | 122.6166 | -122.287 | 0.07782 | 0.0070192 | 0.055448 | 0.0086304 | 0.032537 | -0.0041187 | -0.0033646 | 0.052323 | 0.16937 | -0.004578 | 0.20599 | 0.13733 | -0.37079 | 0.19226 | -0.21973 | -0.027466 | -0.018311 | -122.4884 | 122.493 | -0.082398 | 122.4564 | 122.4243 | -0.44861 | -0.20142 | -0.096131 | -0.036621 | 122.0673 | 122.2595 | 121.9162 | 122.2824 | 122.4564 | 122.2687 | 122.4792 | -0.20142 | 122.2824 | 122.4564 | 122.4792 | 121.9162 | 122.2687 | 0.12817 | -122.5662
610.7812 | 122.6486 | -122.2641 | 0.1236 | -0.015869 | 0.065275 | 0.008844 | 0.033819 | -0.0064685 | -0.0027238 | 0.061295 | 0.16937 | 0.036621 | 0.21973 | 0.10986 | -0.6134 | 0.073242 | -0.32959 | -0.24719 | 0.013733 | -122.5067 | 122.4838 | -0.086975 | 122.4335 | 122.374 | -0.737 | -0.24262 | -0.10986 | -0.050354 | 121.9345 | 122.0169 | 121.6507 | 122.3007 | 122.4335 | 122.2778 | 122.3373 | -0.24262 | 122.3007 | 122.4335 | 122.3373 | 121.6507 | 122.2778 | 0.096131 | -122.6303
611.7812 | 122.5937 | -122.2687 | 0.11444 | -0.00061033 | 0.054593 | 0.0099122 | 0.050268 | -0.0062549 | -0.0025102 | 0.047837 | 0.13275 | 0.022888 | 0.18768 | 0.082397 | -0.80109 | 0.15564 | -0.33417 | -0.31128 | 0.027466 | -122.5067 | 122.4564 | -0.091553 | 122.4014 | 122.3511 | -0.91553 | -0.23804 | -0.086975 | -0.054932 | 121.9345 | 121.9574 | 121.4676 | 122.2916 | 122.4014 | 122.2961 | 122.4243 | -0.23804 | 122.2916 | 122.4014 | 122.4243 | 121.4676 | 122.2961 | 0.073242 | -122.6212
612.7812 | 122.5708 | -122.3099 | 0.14648 | -0.00061033 | 0.097318 | 0.0064942 | 0.050054 | -0.0066821 | -0.0033646 | 0.056595 | 0.16022 | 0.082397 | 0.19684 | 0.004578 | -1.062 | 0.018311 | -0.16022 | -0.44861 | 0.068665 | -122.5433 | 122.5067 | -0.064087 | 122.4701 | 122.3145 | -1.2085 | -0.23346 | -0.077819 | -0.036621 | 122.1497 | 121.8613 | 121.2479 | 122.3923 | 122.4701 | 122.3785 | 122.3282 | -0.23346 | 122.3923 | 122.4701 | 122.3282 | 121.2479 | 122.3785 | 0.050354 | -122.6898
613.7812 | 122.6349 | -122.2916 | 0.082397 | -0.0082398 | 0.051603 | 0.0067078 | 0.029974 | -0.0041187 | -0.0016556 | 0.040787 | 0.14648 | 0.013733 | 0.1831 | 0.14191 | -1.1902 | 0.19684 | -0.15106 | 0.032043 | -0.013733 | -122.5296 | 122.4747 | -0.068664 | 122.438 | 122.4335 | -1.2726 | -0.23804 | -0.09613 | -0.036621 | 122.1405 | 122.3236 | 121.1014 | 122.3053 | 122.438 | 122.2778 | 122.4884 | -0.23804 | 122.3053 | 122.438 | 122.4884 | 121.1014 | 122.2778 | 0.10071 | -122.612
614.7812 | 122.6715 | -122.3053 | 0.073242 | 0.0070192 | 0.051603 | 0.0094848 | 0.029119 | -0.0049731 | -0.0025102 | 0.046555 | 0.11902 | 0.022888 | 0.16022 | 0.10529 | -1.5198 | 0.16022 | -0.1236 | -0.022888 | -0.013733 | -122.5342 | 122.4655 | -0.050354 | 122.4243 | 122.4106 | -1.593 | -0.22888 | -0.086975 | -0.041198 | 122.1817 | 122.2824 | 120.7855 | 122.3282 | 122.4243 | 122.2916 | 122.4655 | -0.22888 | 122.3282 | 122.4243 | 122.4655 | 120.7855 | 122.2916 | 0.086975 | -122.6074
615.7812 | 122.6074 | -122.3511 | 0.086975 | -0.0082398 | 0.050535 | 0.007776 | 0.029333 | -0.0056141 | 5.3436e-05 | 0.043564 | 0.086975 | 0.041199 | 0.15564 | 0.068665 | -4.6234 | 0.1236 | -0.064087 | -0.036621 | 0.004578 | -122.5845 | 122.5067 | -0.045776 | 122.438 | 122.4197 | -4.7104 | -0.23346 | -0.082397 | -0.068665 | 122.287 | 122.3145 | 117.7277 | 122.3923 | 122.438 | 122.3557 | 122.4747 | -0.23346 | 122.3923 | 122.438 | 122.4747 | 117.7277 | 122.3557 | 0.068665 | -122.6715
616.7812 | 122.5937 | -122.374 | 0.082397 | -0.015869 | 0.050748 | 0.0062806 | 0.031469 | -0.0077503 | -0.00058736 | 0.044846 | 0.07782 | 0.032043 | 0.14648 | 0.036621 | -3.6667 | 0.10071 | -0.022888 | -0.091553 | 0.009155 | -122.6028 | 122.5204 | -0.050354 | 122.4518 | 122.4106 | -3.7491 | -0.22888 | -0.073242 | -0.068664 | 122.3511 | 122.2824 | 118.7073 | 122.406 | 122.4518 | 122.3831 | 122.4747 | -0.22888 | 122.406 | 122.4518 | 122.4747 | 118.7073 | 122.3831 | 0.064087 | -122.6852
617.7969 | 122.5937 | -122.3877 | 0.10529 | -0.00061033 | 0.04968 | 0.0056396 | 0.030401 | -0.0045459 | -0.0022964 | 0.043564 | 0.054932 | 0.013733 | 0.14648 | 0.045776 | -3.5889 | 0.09613 | -0.013733 | -0.07782 | 0.022888 | -122.5937 | 122.5342 | -0.091553 | 122.4426 | 122.4335 | -3.6942 | -0.20599 | -0.082398 | -0.091552 | 122.374 | 122.3099 | 118.7988 | 122.4014 | 122.4426 | 122.4106 | 122.4838 | -0.20599 | 122.4014 | 122.4426 | 122.4838 | 118.7988 | 122.4106 | 0.041198 | -122.699
618.7812 | 122.6303 | -122.3923 | 0.09613 | -0.00061033 | 0.045621 | 0.010339 | 0.032751 | -0.0041187 | 0.0041122 | 0.044419 | 0.064087 | 0.022888 | 0.16022 | 0.018311 | -10.7758 | 0.082397 | -0.013733 | -0.10071 | 0.004578 | -122.6257 | 122.5525 | -0.073242 | 122.4564 | 122.4106 | -10.8719 | -0.23346 | -0.091552 | -0.09613 | 122.3785 | 122.2916 | 111.6165 | 122.4152 | 122.4564 | 122.3969 | 122.4747 | -0.23346 | 122.4152 | 122.4564 | 122.4747 | 111.6165 | 122.3969 | 0.064087 | -122.7219
619.7812 | 122.612 | -122.3923 | 0.091553 | -0.015869 | 0.043912 | 0.0073486 | 0.037664 | -0.0032641 | 0.0024032 | 0.0457 | 0.041199 | 0.009155 | 0.14191 | 0.032043 | -11.2885 | 0.091553 | 0 | -0.091553 | 0.013733 | -122.5983 | 122.5342 | -0.082398 | 122.4335 | 122.4243 | -11.38 | -0.20599 | -0.07782 | -0.10071 | 122.3923 | 122.3007 | 111.1038 | 122.4014 | 122.4335 | 122.406 | 122.4838 | -0.20599 | 122.4014 | 122.4335 | 122.4838 | 111.1038 | 122.406 | 0.050354 | -122.6898
620.7812 | 122.6166 | -122.2275 | 0.2655 | 0.0070192 | 0.10885 | 0.0084168 | 0.032751 | -0.0028369 | 0.034874 | 0.16789 | 0.15564 | 0.10986 | 0.23346 | 0 | -61.7432 | 0.054932 | 0 | -0.11444 | 0.17395 | -122.438 | 122.4609 | -0.15564 | 122.3831 | 122.2275 | -62.0087 | -0.21057 | -0.091553 | -0.077819 | 122.2275 | 122.113 | 60.4843 | 122.3373 | 122.3831 | 122.4014 | 122.2824 | -0.21057 | 122.3373 | 122.3831 | 122.2824 | 60.4843 | 122.4014 | -0.032044 | -122.7036
621.7812 | 122.5983 | -122.4197 | 0.10071 | -0.00061033 | 0.048612 | 0.0073486 | 0.027196 | -0.0039051 | 0.0017624 | 0.041001 | 0.073242 | 0.041199 | 0.14191 | 0.036621 | -8.7021 | 0.11902 | -0.032043 | -0.07782 | 0.004578 | -122.6028 | 122.5616 | -0.059509 | 122.493 | 122.4564 | -8.8028 | -0.1831 | -0.09613 | -0.068665 | 122.3877 | 122.3419 | 113.7177 | 122.4609 | 122.493 | 122.4243 | 122.5388 | -0.1831 | 122.4609 | 122.493 | 122.5388 | 113.7177 | 122.4243 | 0.041199 | -122.7036
622.7812 | 122.5845 | -122.4243 | 0.10529 | -0.00061033 | 0.048398 | 0.012689 | 0.030401 | -0.0030505 | 0.0013352 | 0.041428 | 0.068665 | 0.036621 | 0.15564 | 0.004578 | -7.6584 | 0.073242 | 0.018311 | -0.10986 | 0.027466 | -122.6486 | 122.58 | -0.068665 | 122.493 | 122.4289 | -7.7637 | -0.22431 | -0.07782 | -0.086975 | 122.4426 | 122.3145 | 114.7659 | 122.4609 | 122.493 | 122.4518 | 122.4976 | -0.22431 | 122.4609 | 122.493 | 122.4976 | 114.7659 | 122.4518 | 0.050354 | -122.7539
623.7969 | 122.7127 | -122.4152 | 0.068665 | 0.0070192 | 0.041349 | 0.0058534 | 0.023138 | -0.0041187 | 0.0013352 | 0.044419 | 0.091553 | -0.022888 | 0.16937 | 0.086975 | -7.1136 | 0.16479 | -0.10529 | 0.013733 | 0 | -122.5662 | 122.5845 | -0.091553 | 122.5067 | 122.5021 | -7.1823 | -0.15106 | -0.068665 | -0.07782 | 122.3099 | 122.4289 | 115.3015 | 122.3923 | 122.5067 | 122.4152 | 122.58 | -0.15106 | 122.3923 | 122.5067 | 122.58 | 115.3015 | 122.4152 | 0.10071 | -122.6349
624.7812 | 122.6028 | -122.4426 | 0.10529 | -0.00061033 | 0.049039 | 0.006067 | 0.028692 | -0.0045459 | 0.00090784 | 0.044632 | 0.10986 | 0.022888 | 0.15564 | 0.045776 | -8.67 | 0.11444 | -0.013733 | -0.064087 | 0.018311 | -122.6486 | 122.5983 | -0.082398 | 122.5525 | 122.4884 | -8.7753 | -0.20599 | -0.086975 | -0.045777 | 122.4289 | 122.3785 | 113.7726 | 122.4655 | 122.5525 | 122.4609 | 122.5571 | -0.20599 | 122.4655 | 122.5525 | 122.5571 | 113.7726 | 122.4609 | 0.050354 | -122.7539
625.7812 | 122.6669 | -122.406 | 0.09613 | -0.015869 | 0.052244 | 0.003717 | 0.030828 | -0.0036915 | 0.0011214 | 0.047623 | 0.12817 | 0.036621 | 0.16937 | 0.09613 | -12.5931 | 0.14648 | -0.041199 | -0.004578 | 0.022888 | -122.6349 | 122.5754 | -0.059509 | 122.5342 | 122.5021 | -12.6892 | -0.22888 | -0.073242 | -0.041199 | 122.3648 | 122.4014 | 109.8129 | 122.4426 | 122.5342 | 122.4289 | 122.5525 | -0.22888 | 122.4426 | 122.5342 | 122.5525 | 109.8129 | 122.4289 | 0.073243 | -122.731
626.7812 | 122.6212 | -121.0098 | 1.4603 | -0.0082398 | 0.94369 | 0.003717 | 0.041936 | -0.0039051 | 0.021416 | 0.98201 | 1.4008 | 1.3046 | 1.2589 | 0.050354 | -44.1193 | 0.082397 | -0.07782 | -0.068665 | 1.3687 | -121.1609 | 122.2687 | -0.15564 | 122.4106 | 121.0602 | -45.5795 | -0.15106 | -0.091553 | 0.14191 | 120.932 | 120.9412 | 76.8906 | 122.3145 | 122.4106 | 122.3785 | 121.0922 | -0.15106 | 122.3145 | 122.4106 | 121.0922 | 76.8906 | 122.3785 | -0.20142 | -122.6212
627.7969 | 122.6166 | -122.4197 | 0.1236 | -0.015869 | 0.063779 | 0.007776 | 0.047491 | -0.0034777 | -0.0040054 | 0.068131 | 0.13733 | 0.036621 | 0.17395 | 0.032043 | -2.0325 | 0.073242 | -0.050354 | -0.10986 | 0.027466 | -122.5891 | 122.5937 | -0.086975 | 122.5571 | 122.4518 | -2.1561 | -0.16937 | -0.09613 | -0.036621 | 122.3694 | 122.3099 | 120.3873 | 122.4564 | 122.5571 | 122.4472 | 122.493 | -0.16937 | 122.4564 | 122.5571 | 122.493 | 120.3873 | 122.4472 | 0.050354 | -122.7127
628.7969 | 122.7631 | -122.4243 | 0.082397 | -0.00061033 | 0.052457 | 0.0011536 | 0.026769 | -0.0047595 | -0.0029374 | 0.053818 | 0.13275 | -0.009155 | 0.19226 | 0.073242 | -1.4053 | 0.17853 | -0.13275 | -0.004578 | -0.013733 | -122.5708 | 122.6166 | -0.091552 | 122.5571 | 122.4976 | -1.4877 | -0.14648 | -0.09613 | -0.05951 | 122.2916 | 122.4197 | 121.019 | 122.4152 | 122.5571 | 122.4106 | 122.6028 | -0.14648 | 122.4152 | 122.5571 | 122.6028 | 121.019 | 122.4106 | 0.10986 | -122.6532
629.7812 | 122.6669 | -122.4335 | 0.1236 | -0.00061033 | 0.059507 | 0.0094848 | 0.037237 | -0.0060413 | -0.0044328 | 0.062149 | 0.16022 | 0.041199 | 0.19226 | 0.059509 | -1.0071 | 0.086975 | -0.064087 | -0.054932 | 0.027466 | -122.644 | 122.6257 | -0.082397 | 122.5937 | 122.493 | -1.1307 | -0.21057 | -0.09613 | -0.032044 | 122.3694 | 122.3785 | 121.4264 | 122.4747 | 122.5937 | 122.4609 | 122.5204 | -0.21057 | 122.4747 | 122.5937 | 122.5204 | 121.4264 | 122.4609 | 0.068665 | -122.7676
630.7812 | 122.6395 | -122.4106 | 0.13275 | -0.00061033 | 0.068052 | 0.010553 | 0.035314 | -0.0064685 | -0.0018692 | 0.068985 | 0.14191 | 0.054932 | 0.1831 | 0.054932 | -2.8564 | 0.10071 | -0.054932 | -0.09613 | 0.050354 | -122.612 | 122.5937 | -0.077819 | 122.5525 | 122.4655 | -2.9892 | -0.20142 | -0.082397 | -0.041198 | 122.3557 | 122.3145 | 119.5541 | 122.4655 | 122.5525 | 122.4609 | 122.5113 | -0.20142 | 122.4655 | 122.5525 | 122.5113 | 119.5541 | 122.4609 | 0.050354 | -122.7448
631.7812 | 122.7219 | -122.4243 | 0.11902 | -0.00061033 | 0.067197 | 0.0049988 | 0.040441 | -0.0054003 | -0.0035782 | 0.060227 | 0.15564 | 0.059509 | 0.19226 | 0.045776 | -1.7578 | 0.10071 | -0.07782 | -0.027466 | 0.027466 | -122.6166 | 122.6166 | -0.05951 | 122.58 | 122.4701 | -1.8768 | -0.19226 | -0.091553 | -0.036621 | 122.3465 | 122.3969 | 120.6665 | 122.4838 | 122.58 | 122.4518 | 122.525 | -0.19226 | 122.4838 | 122.58 | 122.525 | 120.6665 | 122.4518 | 0.073242 | -122.7356
632.7812 | 122.6303 | -122.4609 | 0.10529 | -0.00061033 | 0.051603 | 0.0075622 | 0.035955 | -0.0075367 | -0.0033646 | 0.060868 | 0.059509 | 0.018311 | 0.16479 | 0.013733 | -1.7395 | 0.064087 | 0.050354 | -0.064087 | 0.041199 | -122.6349 | 122.6257 | -0.086975 | 122.5204 | 122.4747 | -1.8448 | -0.17395 | -0.064087 | -0.10529 | 122.5113 | 122.3969 | 120.7214 | 122.4792 | 122.5204 | 122.5021 | 122.525 | -0.17395 | 122.4792 | 122.5204 | 122.525 | 120.7214 | 122.5021 | 0.059509 | -122.7402
633.7969 | 122.7448 | -122.406 | 0.082397 | -0.00061033 | 0.049466 | 0.006067 | 0.091497 | -0.0032641 | -0.0016556 | 0.11107 | 0.15106 | -0.004578 | 0.18768 | 0.12817 | -2.1286 | 0.20599 | -0.15564 | 0.054932 | -0.009155 | -122.6074 | 122.5937 | -0.086975 | 122.5571 | 122.5342 | -2.211 | -0.20142 | -0.091552 | -0.036621 | 122.2504 | 122.4609 | 120.2774 | 122.4014 | 122.5571 | 122.3969 | 122.612 | -0.20142 | 122.4014 | 122.5571 | 122.612 | 120.2774 | 122.3969 | 0.10529 | -122.6898
634.7812 | 122.6532 | -122.4884 | 0.10071 | -0.015869 | 0.046262 | 0.0049988 | 0.043645 | -0.0077503 | -0.0033646 | 0.057877 | 0.041199 | 0.045776 | 0.14648 | 0.036621 | -1.3458 | 0.07782 | 0.064087 | -0.022888 | 0.018311 | -122.6852 | 122.6349 | -0.054932 | 122.5296 | 122.525 | -1.4465 | -0.19684 | -0.082397 | -0.10529 | 122.5525 | 122.4655 | 121.1426 | 122.5342 | 122.5296 | 122.5067 | 122.5662 | -0.19684 | 122.5342 | 122.5296 | 122.5662 | 121.1426 | 122.5067 | 0.045776 | -122.7859
635.7812 | 122.5937 | -122.5113 | 0.10986 | -0.0082398 | 0.056302 | 0.007776 | 0.055822 | -0.0071093 | -0.0016556 | 0.079453 | 0.07782 | 0.041199 | 0.16479 | 0.022888 | -2.0233 | 0.07782 | 0.041199 | -0.036621 | 0.050354 | -122.6486 | 122.6761 | -0.068664 | 122.5891 | 122.5342 | -2.1332 | -0.13733 | -0.059509 | -0.086975 | 122.5525 | 122.4747 | 120.488 | 122.5525 | 122.5891 | 122.5616 | 122.5891 | -0.13733 | 122.5525 | 122.5891 | 122.5891 | 120.488 | 122.5616 | 0.054932 | -122.7585
636.7812 | 122.6212 | -122.3511 | 0.25177 | -0.00061033 | 0.12851 | 0.006067 | 0.19724 | -0.0071093 | 0.0045394 | 0.31187 | 0.18768 | 0.14648 | 0.24719 | 0.036621 | -14.328 | 0.073242 | 0.054932 | -0.022888 | 0.16479 | -122.5021 | 122.5983 | -0.10529 | 122.5388 | 122.3877 | -14.5798 | -0.15106 | -0.086975 | -0.059509 | 122.406 | 122.3282 | 108.0231 | 122.4976 | 122.5388 | 122.5159 | 122.4243 | -0.15106 | 122.4976 | 122.5388 | 122.4243 | 108.0231 | 122.5159 | -0.004578 | -122.7539
637.7969 | 122.699 | -122.4792 | 0.12817 | -0.00061033 | 0.058652 | 0.010126 | 0.041296 | -0.0039051 | -0.0025102 | 0.061081 | 0.12817 | 0.041199 | 0.15106 | 0.091553 | -0.35706 | 0.1236 | -0.022888 | 0.027466 | 0.041199 | -122.6212 | 122.6303 | -0.086975 | 122.6074 | 122.5708 | -0.48523 | -0.14191 | -0.086975 | -0.022888 | 122.4564 | 122.5067 | 122.1222 | 122.5204 | 122.6074 | 122.5204 | 122.6028 | -0.14191 | 122.5204 | 122.6074 | 122.6028 | 122.1222 | 122.5204 | 0.022888 | -122.7493
638.7812 | 122.7081 | -122.4197 | 0.10529 | -0.0082398 | 0.063566 | 0.0075622 | 0.047063 | -0.0043323 | -0.0018692 | 0.072831 | 0.13733 | 0.041199 | 0.18768 | 0.07782 | -0.76904 | 0.14648 | -0.09613 | 0.013733 | 0.041199 | -122.6303 | 122.6074 | -0.064087 | 122.5571 | 122.4976 | -0.87433 | -0.21057 | -0.064087 | -0.050354 | 122.3236 | 122.4335 | 121.6507 | 122.4609 | 122.5571 | 122.4609 | 122.5662 | -0.21057 | 122.4609 | 122.5571 | 122.5662 | 121.6507 | 122.4609 | 0.082397 | -122.7356
639.7812 | 122.7264 | -122.4518 | 0.13733 | -0.00061033 | 0.071683 | 0.0094848 | 0.045782 | -0.0058277 | -0.0037918 | 0.085648 | 0.16022 | 0.036621 | 0.21515 | 0.086975 | -0.81024 | 0.12817 | 0.009155 | 0.032043 | 0.050354 | -122.612 | 122.6669 | -0.10071 | 122.612 | 122.5388 | -0.94757 | -0.16022 | -0.086975 | -0.054932 | 122.4609 | 122.4838 | 121.6415 | 122.4884 | 122.612 | 122.5021 | 122.58 | -0.16022 | 122.4884 | 122.612 | 122.58 | 121.6415 | 122.5021 | 0.07782 | -122.7493
640.7812 | 121.9208 | -121.8018 | 0.07782 | -0.015869 | 0.029813 | 8.5364e-05 | 0.042791 | -0.0066821 | -0.0055008 | 0.030747 | 0.054932 | -0.009155 | 0.12817 | 0.07782 | 0.041199 | 0.10529 | 0.07782 | 0.022888 | -0.009155 | -121.9391 | 121.9299 | -0.086975 | 121.8567 | 121.8796 | -0.036621 | -0.13733 | -0.086975 | -0.073242 | 121.8796 | 121.8246 | 121.843 | 121.7926 | 121.8567 | 121.7926 | 121.907 | -0.13733 | 121.7926 | 121.8567 | 121.907 | 121.843 | 121.7926 | 0.050354 | -122.0169
641.7812 | 122.2229 | -122.0444 | 0.07782 | -0.00061033 | 0.030027 | 0.0035034 | 0.060949 | -0.0075367 | -0.0018692 | 0.060227 | 0.07782 | -0.022888 | 0.13733 | 0.082397 | 0.041199 | 0.12817 | 0.050354 | 0.009155 | 0.009155 | -122.1909 | 122.1817 | -0.10071 | 122.1222 | 122.1268 | -0.036621 | -0.14648 | -0.068665 | -0.059509 | 122.0947 | 122.0535 | 122.0856 | 122.0215 | 122.1222 | 122.0535 | 122.1725 | -0.14648 | 122.0215 | 122.1222 | 122.1725 | 122.0856 | 122.0535 | 0.059509 | -122.2687
642.7812 | 122.1405 | -122.0947 | 0.073242 | -0.0082398 | 0.026822 | 0.0035034 | 0.041723 | -0.0073229 | -0.0033646 | 0.033097 | 0.10071 | -0.045776 | 0.15564 | 0.13275 | 0.07782 | 0.17395 | 0.018311 | 0.064087 | -0.009155 | -122.2504 | 122.2504 | -0.11902 | 122.1954 | 122.2275 | 0.004578 | -0.15564 | -0.082397 | -0.054932 | 122.113 | 122.1588 | 122.1725 | 122.049 | 122.1954 | 122.0856 | 122.2687 | -0.15564 | 122.049 | 122.1954 | 122.2687 | 122.1725 | 122.0856 | 0.082398 | -122.3236
643.7969 | 122.2733 | -122.113 | 0.07782 | 0.014648 | 0.042417 | 0.0099122 | 0.15409 | -0.0071093 | -0.0033646 | 0.15999 | 0.068665 | 0.013733 | 0.16022 | 0.068665 | -0.050354 | 0.11902 | -0.036621 | -0.068665 | -0.004578 | -122.2824 | 122.2733 | -0.064087 | 122.1817 | 122.1817 | -0.12817 | -0.16937 | -0.082398 | -0.091552 | 122.0764 | 122.0444 | 122.0627 | 122.1268 | 122.1817 | 122.1085 | 122.2321 | -0.16937 | 122.1268 | 122.1817 | 122.2321 | 122.0627 | 122.1085 | 0.082397 | -122.3602
644.7812 | 122.3877 | -122.2092 | 0.064087 | -0.00061033 | 0.037717 | 0.0011536 | 0.062017 | -0.0079639 | -0.0037918 | 0.085862 | 0.13733 | -0.054932 | 0.17395 | 0.19226 | 0.10071 | 0.21973 | -0.086975 | 0.054932 | -0.036621 | -122.3511 | 122.3831 | -0.11902 | 122.3465 | 122.4014 | 0.036621 | -0.14191 | -0.10071 | -0.036621 | 122.1222 | 122.2641 | 122.3099 | 122.1542 | 122.3465 | 122.1725 | 122.4289 | -0.14191 | 122.1542 | 122.3465 | 122.4289 | 122.3099 | 122.1725 | 0.10986 | -122.4152
645.7812 | 122.438 | -122.168 | 0.050354 | -0.00061033 | 0.02255 | 0.002649 | 0.033392 | -0.0058277 | -0.0057144 | 0.032669 | 0.14191 | -0.059509 | 0.15564 | 0.19684 | 0.15564 | 0.25177 | -0.091553 | 0.16022 | -0.041199 | -122.3053 | 122.3236 | -0.10986 | 122.3099 | 122.3648 | 0.10529 | -0.13733 | -0.091553 | -0.013733 | 122.0764 | 122.3282 | 122.3236 | 122.1085 | 122.3099 | 122.1268 | 122.4197 | -0.13733 | 122.1085 | 122.3099 | 122.4197 | 122.3236 | 122.1268 | 0.10529 | -122.3557
646.7812 | 122.4243 | -122.2275 | 0.045776 | -0.0082398 | 0.027677 | 0.0015808 | 0.072057 | -0.0066821 | -0.004219 | 0.068131 | 0.14191 | -0.036621 | 0.17853 | 0.2243 | 0.11902 | 0.25177 | -0.11444 | 0.15564 | -0.036621 | -122.3419 | 122.406 | -0.082397 | 122.3694 | 122.4518 | 0.073243 | -0.11444 | -0.082397 | -0.036621 | 122.113 | 122.3831 | 122.3465 | 122.1909 | 122.3694 | 122.1909 | 122.4792 | -0.11444 | 122.1909 | 122.3694 | 122.4792 | 122.3465 | 122.1909 | 0.13275 | -122.3877
647.7969 | 122.4609 | -122.2321 | 0.054932 | -0.0082398 | 0.021695 | 0.0032898 | 0.038091 | -0.0094593 | -0.0074234 | 0.033524 | 0.14191 | -0.064087 | 0.16937 | 0.19684 | 0.13733 | 0.21515 | -0.032043 | 0.14191 | -0.041199 | -122.3831 | 122.4014 | -0.11902 | 122.374 | 122.4289 | 0.082397 | -0.15106 | -0.096131 | -0.027466 | 122.2 | 122.374 | 122.3694 | 122.168 | 122.374 | 122.1909 | 122.4472 | -0.15106 | 122.168 | 122.374 | 122.4472 | 122.3694 | 122.1909 | 0.11444 | -122.438
648.7812 | 122.4106 | -122.287 | 0.082397 | -0.00061033 | 0.026609 | 0.0099122 | 0.036596 | -0.0056141 | -0.0055008 | 0.026261 | 0.032043 | -0.013733 | 0.12817 | 0.059509 | 0.022888 | 0.10529 | 0.036621 | -0.027466 | -0.009155 | -122.4243 | 122.4152 | -0.09613 | 122.319 | 122.3465 | -0.059509 | -0.13733 | -0.091552 | -0.096131 | 122.3236 | 122.2595 | 122.3099 | 122.2733 | 122.319 | 122.2778 | 122.3923 | -0.13733 | 122.2733 | 122.319 | 122.3923 | 122.3099 | 122.2778 | 0.045777 | -122.5067
649.7812 | 122.5342 | -122.2641 | 0.054932 | -0.00061033 | 0.025754 | 0.0045716 | 0.032751 | -0.0077503 | -0.0052872 | 0.027329 | 0.14648 | -0.068665 | 0.17395 | 0.18768 | 0.13275 | 0.21973 | -0.059509 | 0.13275 | -0.054932 | -122.3831 | 122.438 | -0.1236 | 122.4106 | 122.4518 | 0.077819 | -0.11902 | -0.10986 | -0.027466 | 122.2046 | 122.3969 | 122.3969 | 122.1954 | 122.4106 | 122.2092 | 122.4838 | -0.11902 | 122.1954 | 122.4106 | 122.4838 | 122.3969 | 122.2092 | 0.11902 | -122.438
650.7812 | 122.4976 | -122.2504 | 0.050354 | 0.0070192 | 0.024686 | 0.0028626 | 0.044073 | -0.0086047 | -0.0052872 | 0.037796 | 0.14191 | -0.059509 | 0.15564 | 0.21515 | 0.16022 | 0.24719 | -0.082397 | 0.15106 | -0.050354 | -122.406 | 122.406 | -0.10986 | 122.3923 | 122.4655 | 0.10986 | -0.15564 | -0.10071 | -0.013733 | 122.168 | 122.4014 | 122.4106 | 122.1909 | 122.3923 | 122.2 | 122.4976 | -0.15564 | 122.1909 | 122.3923 | 122.4976 | 122.4106 | 122.2 | 0.10529 | -122.4564
651.7812 | 122.58 | -122.2824 | 0.041199 | 0.0070192 | 0.025541 | 0.002649 | 0.062017 | -0.0077503 | -0.0044328 | 0.04805 | 0.14648 | -0.045776 | 0.15564 | 0.21515 | 0.14648 | 0.25177 | -0.13275 | 0.15564 | -0.054932 | -122.406 | 122.4381 | -0.086975 | 122.4289 | 122.4976 | 0.10529 | -0.1236 | -0.096131 | -0.009156 | 122.1497 | 122.4381 | 122.4289 | 122.2366 | 122.4289 | 122.2275 | 122.5342 | -0.1236 | 122.2366 | 122.4289 | 122.5342 | 122.4289 | 122.2275 | 0.11444 | -122.4472
652.7812 | 122.4609 | -122.2916 | 0.050354 | -0.0082398 | 0.025327 | 0.005426 | 0.037878 | -0.0090319 | -0.0046464 | 0.035019 | 0.13275 | -0.054932 | 0.17395 | 0.19684 | 0.15106 | 0.21973 | -0.086975 | 0.13733 | -0.036621 | -122.4655 | 122.4655 | -0.10529 | 122.4243 | 122.4884 | 0.10071 | -0.17395 | -0.086975 | -0.041199 | 122.2046 | 122.4289 | 122.4426 | 122.2366 | 122.4243 | 122.2549 | 122.5113 | -0.17395 | 122.2366 | 122.4243 | 122.5113 | 122.4426 | 122.2549 | 0.1236 | -122.5159
653.7812 | 122.612 | -122.2961 | 0.036621 | 0.0070192 | 0.023191 | -0.00012824 | 0.039587 | -0.0077503 | -0.0044328 | 0.035447 | 0.15564 | -0.054932 | 0.16022 | 0.22888 | 0.17395 | 0.27924 | -0.1236 | 0.1831 | -0.059509 | -122.4152 | 122.4564 | -0.091553 | 122.4518 | 122.525 | 0.13733 | -0.11902 | -0.09613 | -0.004577 | 122.1725 | 122.4792 | 122.4701 | 122.2412 | 122.4518 | 122.2366 | 122.5754 | -0.11902 | 122.2412 | 122.4518 | 122.5754 | 122.4701 | 122.2366 | 0.1236 | -122.4518
654.7812 | 121.9116 | -121.6873 | 0.086975 | -0.00061033 | 0.046903 | 0.011194 | 0.31922 | -0.0058277 | -0.0020828 | 0.34691 | 0.13275 | -0.018311 | 0.16937 | 0.041199 | 0.009155 | 0.11444 | -0.19684 | -0.009155 | -0.022888 | -121.7697 | 121.8567 | -0.10529 | 121.8201 | 121.7285 | -0.07782 | -0.082397 | -0.10986 | -0.036622 | 121.4905 | 121.6782 | 121.6965 | 121.669 | 121.8201 | 121.6644 | 121.8018 | -0.082397 | 121.669 | 121.8201 | 121.8018 | 121.6965 | 121.6644 | 0.082398 | -121.8567
655.7812 | 121.9894 | -121.8796 | 0.07782 | -0.0082398 | 0.028959 | 0.0075622 | 0.065008 | -0.0094593 | -0.0040054 | 0.057022 | 0.045776 | -0.009155 | 0.11444 | 0.082397 | 0.013733 | 0.10071 | 0.082397 | 0.032043 | 0.013733 | -122.0306 | 121.994 | -0.086975 | 121.9254 | 121.962 | -0.064087 | -0.15106 | -0.064087 | -0.068665 | 121.962 | 121.9116 | 121.8933 | 121.8704 | 121.9254 | 121.8933 | 121.9803 | -0.15106 | 121.8704 | 121.9254 | 121.9803 | 121.8933 | 121.8933 | 0.036621 | -122.1085
656.7812 | 122.1405 | -121.9345 | 0.045776 | -0.0082398 | 0.025541 | 0.0017944 | 0.050054 | -0.0094593 | -0.0037918 | 0.048905 | 0.073242 | -0.045776 | 0.14648 | 0.15564 | 0.11444 | 0.22888 | -0.091553 | 0.10071 | -0.036621 | -122.0352 | 122.081 | -0.091552 | 122.0078 | 122.0901 | 0.068665 | -0.10071 | -0.082397 | -0.073242 | 121.843 | 122.0352 | 122.049 | 121.8887 | 122.0078 | 121.8979 | 122.1634 | -0.10071 | 121.8887 | 122.0078 | 122.1634 | 122.049 | 121.8979 | 0.10071 | -122.081
657.7969 | 122.1863 | -121.9482 | 0.050354 | -0.00061033 | 0.024259 | 0.0041444 | 0.038518 | -0.0092457 | -0.0020828 | 0.033738 | 0.091553 | -0.050354 | 0.14648 | 0.15564 | 0.11444 | 0.21057 | -0.07782 | 0.10071 | -0.054932 | -122.1451 | 122.0947 | -0.10071 | 122.0398 | 122.1039 | 0.064087 | -0.19684 | -0.10529 | -0.054931 | 121.8704 | 122.0489 | 122.0627 | 121.8979 | 122.0398 | 121.8933 | 122.1588 | -0.19684 | 121.8979 | 122.0398 | 122.1588 | 122.0627 | 121.8933 | 0.09613 | -122.1954
658.7812 | 121.7789 | -121.5134 | 0.045776 | 0.0070192 | 0.015928 | 0.002649 | 0.01972 | -0.0056141 | -0.004219 | 0.0087436 | 0.09613 | -0.050354 | 0.15564 | 0.17395 | 0.10986 | 0.22888 | -0.086975 | -19.1483 | -0.045776 | -121.6644 | 121.669 | -0.09613 | 121.6095 | 121.6873 | 0.064087 | -0.15106 | -0.091552 | -0.05951 | 121.4264 | 102.3651 | 121.6232 | 121.463 | 121.6095 | 121.4676 | 121.7422 | -0.15106 | 121.463 | 121.6095 | 121.7422 | 121.6232 | 121.4676 | 0.10986 | -121.7102
659.7812 | 121.9528 | -121.7468 | 0.036621 | -0.0082398 | 0.016996 | 0.0017944 | 0.026769 | -0.0060413 | -0.0029374 | 0.014725 | 0.068665 | -0.041199 | 0.13275 | 0.14191 | 0.09613 | 0.21057 | -0.073242 | -61.4548 | -0.045776 | -121.8246 | 121.8796 | -0.07782 | 121.8155 | 121.8887 | 0.059509 | -0.07782 | -0.082397 | -0.064086 | 121.6736 | 60.2921 | 121.843 | 121.7056 | 121.8155 | 121.701 | 121.9574 | -0.07782 | 121.7056 | 121.8155 | 121.9574 | 121.843 | 121.701 | 0.09613 | -121.8613
660.7812 | 122.0306 | -121.7606 | 0.032043 | -0.00061033 | 0.01785 | 0.0049988 | 0.035741 | -0.0073229 | -0.0050736 | 0.022415 | 0.13733 | -0.054932 | 0.15564 | 0.19684 | 0.14648 | 0.24719 | -0.14648 | -62.3062 | -0.09613 | -121.9299 | 121.9162 | -0.086975 | 121.8979 | 121.9574 | 0.11444 | -0.16937 | -0.12817 | -0.018311 | 121.6141 | 59.4543 | 121.907 | 121.7056 | 121.8979 | 121.6644 | 122.0078 | -0.16937 | 121.7056 | 121.8979 | 122.0078 | 121.907 | 121.6644 | 0.1236 | -121.962
661.7812 | 122.0123 | -121.843 | 0.032043 | -0.0082398 | 0.019132 | 0.0011536 | 0.037237 | -0.0088183 | -0.0057144 | 0.030533 | 0.082397 | -0.054932 | 0.16937 | 0.13733 | 0.086975 | 0.20142 | -0.07782 | -7.4478 | -0.054932 | -121.9803 | 122.0123 | -0.086975 | 121.9254 | 121.9803 | 0.054932 | -0.13733 | -0.086975 | -0.086976 | 121.7651 | 114.3951 | 121.9299 | 121.788 | 121.9254 | 121.788 | 122.0444 | -0.13733 | 121.788 | 121.9254 | 122.0444 | 121.9299 | 121.788 | 0.13733 | -122.0123
662.7812 | 122.1085 | -121.8292 | 0.050354 | -0.00061033 | 0.035795 | 0.0064942 | 0.2844 | -0.0094593 | -0.0040054 | 0.29158 | 0.11902 | -0.032043 | 0.15564 | 0.10529 | 0.059509 | 0.15106 | -0.1236 | -1.593 | -0.041199 | -121.962 | 121.9849 | -0.082397 | 121.9482 | 121.9345 | 0.009155 | -0.13275 | -0.091553 | -0.036621 | 121.7056 | 120.2362 | 121.8887 | 121.7972 | 121.9482 | 121.788 | 121.9803 | -0.13275 | 121.7972 | 121.9482 | 121.9803 | 121.8887 | 121.788 | 0.10529 | -122.0123
663.7812 | 121.2479 | -121.019 | 0.027466 | -0.00061033 | 0.00033325 | 0.0047852 | 0.046423 | -0.0056141 | -0.0046464 | 0.036301 | 0.10529 | -0.054932 | 0.14648 | 0.15564 | 0.09613 | 0.19684 | -0.12817 | -6.8665 | -0.054932 | -121.1884 | 121.1655 | -0.082398 | 121.1243 | 121.1746 | 0.068664 | -0.16937 | -0.082398 | -0.041198 | 120.8908 | 114.1525 | 121.1151 | 120.9641 | 121.1243 | 120.9641 | 121.2158 | -0.16937 | 120.9641 | 121.1243 | 121.2158 | 121.1151 | 120.9641 | 0.11902 | -121.2158
664.7812 | 122.113 | -121.8246 | 0.045776 | -0.00061033 | 0.010801 | 0.0064942 | 0.036382 | -0.0054003 | -0.0027238 | 0.027329 | 0.13275 | -0.064087 | 0.15564 | 0.19226 | 0.11902 | 0.24719 | -0.16022 | 0.009155 | -0.050354 | -122.0261 | 121.9803 | -0.10986 | 121.9574 | 122.0169 | 0.073243 | -0.20142 | -0.09613 | -0.022889 | 121.6644 | 121.8338 | 121.9437 | 121.7606 | 121.9574 | 121.7743 | 122.0718 | -0.20142 | 121.7606 | 121.9574 | 122.0718 | 121.9437 | 121.7743 | 0.10986 | -122.0718
665.7812 | 122.1359 | -121.8475 | 0.054932 | -0.00061033 | 0.016782 | 0.0052124 | 0.035955 | -0.0081775 | -0.0046464 | 0.033738 | 0.13275 | -0.068665 | 0.17853 | 0.20599 | 0.13275 | 0.25177 | -0.13275 | -0.19226 | -0.064087 | -122.0352 | 122.0261 | -0.1236 | 121.9803 | 122.0535 | 0.077819 | -0.18768 | -0.11902 | -0.045777 | 121.7148 | 121.6553 | 121.9803 | 121.7789 | 121.9803 | 121.7834 | 122.0993 | -0.18768 | 121.7789 | 121.9803 | 122.0993 | 121.9803 | 121.7834 | 0.1236 | -122.0901
666.7812 | 122.1725 | -121.8933 | 0.009155 | -0.00061033 | 0.020414 | 0.004358 | 0.035741 | -0.0058277 | -0.004219 | 0.031601 | 0.15106 | -0.050354 | 0.17395 | 0.20599 | 0.14191 | 0.27008 | -0.16937 | -0.17853 | -0.064087 | -122.0718 | 122.0673 | -0.059509 | 122.0444 | 122.0993 | 0.13275 | -0.17853 | -0.073242 | -0.022888 | 121.7239 | 121.7148 | 122.0352 | 121.843 | 122.0444 | 121.8292 | 122.1634 | -0.17853 | 121.843 | 122.0444 | 122.1634 | 122.0352 | 121.8292 | 0.16479 | -122.081
667.7969 | 122.2275 | -121.9254 | 0.054932 | -0.015869 | 0.024686 | 0.0049988 | 0.12269 | -0.010741 | -0.0029374 | 0.12923 | 0.13275 | -0.050354 | 0.17395 | 0.19684 | 0.1236 | 0.24719 | -0.13733 | -0.13733 | -0.064087 | -122.0856 | 122.0993 | -0.10529 | 122.0581 | 122.1222 | 0.068664 | -0.16022 | -0.11902 | -0.041199 | 121.788 | 121.788 | 122.049 | 121.875 | 122.0581 | 121.8613 | 122.1725 | -0.16022 | 121.875 | 122.0581 | 122.1725 | 122.049 | 121.8613 | 0.11902 | -122.1405
668.7812 | 122.2229 | -121.9025 | 0.054932 | 0.0070192 | 0.033658 | 0.002649 | 0.2045 | -0.0081775 | -0.0052872 | 0.21745 | 0.14648 | -0.045776 | 0.18768 | 0.17395 | 0.1236 | 0.21973 | -0.1831 | -2.6459 | -0.059509 | -122.0993 | 122.0901 | -0.10071 | 122.049 | 122.0764 | 0.068664 | -0.19684 | -0.11444 | -0.041199 | 121.7194 | 119.2566 | 122.0261 | 121.8567 | 122.049 | 121.843 | 122.1222 | -0.19684 | 121.8567 | 122.049 | 122.1222 | 122.0261 | 121.843 | 0.13275 | -122.1542
669.7812 | 122.493 | -121.9482 | 0.036621 | -0.0082398 | 0.036649 | 0.0062806 | 0.038091 | -0.0056141 | -0.0055008 | 0.093338 | 0.12817 | -0.050354 | 0.16022 | 0.16937 | 0.14191 | 0.2243 | -0.1236 | -1.3138 | -0.050354 | -122.0993 | 122.1085 | -0.086975 | 122.0764 | 122.1176 | 0.10529 | -0.15106 | -0.086975 | -0.032043 | 121.8246 | 120.6345 | 122.0901 | 121.8979 | 122.0764 | 121.8979 | 122.1725 | -0.15106 | 121.8979 | 122.0764 | 122.1725 | 122.0901 | 121.8979 | 0.1236 | -122.1359
670.7812 | 122.2549 | -121.9116 | 0.064087 | -0.00061033 | 0.23254 | 0.007135 | 0.069067 | -0.0086047 | -0.00486 | 0.27898 | 0.16479 | -0.036621 | 0.16479 | 0.22888 | 0.18768 | 0.28839 | -0.16022 | -0.17395 | -0.032043 | -122.0856 | 122.0764 | -0.10071 | 122.0764 | 122.1405 | 0.1236 | -0.17395 | -0.09613 | 0 | 121.7514 | 121.7377 | 122.0993 | 121.875 | 122.0764 | 121.8796 | 122.2 | -0.17395 | 121.875 | 122.0764 | 122.2 | 122.0993 | 121.8796 | 0.10071 | -122.1497
671.7812 | 122.2412 | -121.8567 | 0.091553 | -0.0082398 | 0.36093 | 0.0041444 | 0.1323 | -0.0068957 | -0.003151 | 0.49025 | 0.17395 | -0.041199 | 0.17395 | 0.24719 | 0.16937 | 0.28381 | -0.10986 | -1.799 | -0.004578 | -122.0306 | 122.0306 | -0.13275 | 122.0306 | 122.1039 | 0.07782 | -0.17395 | -0.096131 | 0 | 121.7468 | 120.0577 | 122.0261 | 121.8155 | 122.0306 | 121.8521 | 122.1405 | -0.17395 | 121.8155 | 122.0306 | 122.1405 | 122.0261 | 121.8521 | 0.082397 | -122.1222
672.7812 | 122.2504 | -121.8979 | 0.059509 | -0.015869 | 0.060361 | 0.0064942 | 0.49653 | -0.0068957 | -0.0027238 | 0.53041 | 0.15106 | -0.022888 | 0.16937 | 0.10986 | 0.050354 | 0.16022 | -0.23804 | -0.34332 | -0.045776 | -122.0856 | 122.0673 | -0.082397 | 122.0489 | 122.0078 | -0.009155 | -0.18768 | -0.10528 | -0.018311 | 121.6599 | 121.5546 | 121.9482 | 121.875 | 122.0489 | 121.8521 | 122.0581 | -0.18768 | 121.875 | 122.0489 | 122.0581 | 121.9482 | 121.8521 | 0.10986 | -122.1451
673.7812 | 122.1909 | -121.9116 | 0.054932 | -0.00061033 | 0.068479 | 0.0079896 | 0.068853 | -0.0054003 | -0.0025102 | 0.10829 | 0.10529 | -0.045776 | 0.14191 | 0.16022 | 0.10071 | 0.22888 | -0.11444 | -0.51727 | -0.045776 | -122.1313 | 122.0535 | -0.10071 | 122.0169 | 122.0718 | 0.045776 | -0.21973 | -0.10071 | -0.036621 | 121.7972 | 121.3943 | 122.0123 | 121.8658 | 122.0169 | 121.8658 | 122.1405 | -0.21973 | 121.8658 | 122.0169 | 122.1405 | 122.0123 | 121.8658 | 0.086975 | -122.1863
674.7812 | 122.1542 | -121.9666 | 0.10071 | -0.0082398 | 0.11355 | 0.0082032 | 0.061163 | -0.0060413 | -0.0020828 | 0.13756 | 0.045776 | -0.004578 | 0.11902 | 0.073242 | 0.036621 | 0.12817 | 0.027466 | -0.52185 | 0 | -122.1909 | 122.0856 | -0.10529 | 122.0123 | 122.0398 | -0.064087 | -0.2243 | -0.10071 | -0.073243 | 121.994 | 121.4447 | 122.0032 | 121.962 | 122.0123 | 121.9666 | 122.0947 | -0.2243 | 121.962 | 122.0123 | 122.0947 | 122.0032 | 121.9666 | 0.018311 | -122.2916
675.7812 | 122.287 | -121.9162 | 0.054932 | -0.00061033 | 0.18683 | 0.007135 | 0.072698 | -0.0039051 | -0.0037918 | 0.23198 | 0.15106 | -0.032043 | 0.16479 | 0.21057 | 0.15106 | 0.27008 | -0.11902 | -1.3092 | -0.022888 | -122.1222 | 122.081 | -0.086975 | 122.0673 | 122.1268 | 0.09613 | -0.20599 | -0.07782 | -0.013733 | 121.7972 | 120.607 | 122.0673 | 121.8842 | 122.0673 | 121.8933 | 122.1863 | -0.20599 | 121.8842 | 122.0673 | 122.1863 | 122.0673 | 121.8933 | 0.10986 | -122.1771
676.7812 | 122.2458 | -121.8109 | 0.11444 | -0.00061033 | 0.29535 | 0.0039306 | 1.2972 | -0.0043323 | -0.0033646 | 1.5661 | 0.23346 | 0.027466 | 0.2243 | -0.032043 | -0.059509 | 0.059509 | -0.37994 | -1.1078 | -0.086975 | -121.8887 | 122.0352 | -0.086975 | 122.0444 | 121.7789 | -0.17395 | -0.07782 | -0.20142 | 0.009155 | 121.431 | 120.7031 | 121.7514 | 121.8384 | 122.0444 | 121.7239 | 121.8704 | -0.07782 | 121.8384 | 122.0444 | 121.8704 | 121.7514 | 121.7239 | 0.10986 | -122.0032
677.7969 | 121.4355 | -121.1151 | 0.10529 | 0.0070192 | 0.037504 | 0.0039306 | 0.12931 | -0.0043323 | -0.0020828 | 0.18605 | 0.16479 | -0.013733 | 0.20599 | -0.009155 | -0.045776 | 0.082397 | -0.32044 | -0.022888 | -0.013733 | -121.4813 | 121.3211 | -0.11902 | 121.2799 | 121.106 | -0.15106 | -0.36621 | -0.11902 | -0.041199 | 120.7947 | 121.0922 | 121.0693 | 121.1014 | 121.2799 | 121.1014 | 121.1975 | -0.36621 | 121.1014 | 121.2799 | 121.1975 | 121.0693 | 121.1014 | 0.10071 | -121.5866
678.7812 | 121.8704 | -121.5546 | 0.045776 | -0.00061033 | 0.031949 | 0.010126 | 0.077825 | -0.0064685 | -0.0022964 | 0.07219 | 0.15106 | -0.036621 | 0.16937 | 0.16022 | 0.10071 | 0.21973 | -0.16479 | -0.42572 | -0.059509 | -121.7743 | 121.7239 | -0.082397 | 121.7056 | 121.7148 | 0.054932 | -0.21973 | -0.10528 | -0.018311 | 121.3898 | 121.1288 | 121.6553 | 121.5179 | 121.7056 | 121.4951 | 121.7743 | -0.21973 | 121.5179 | 121.7056 | 121.7743 | 121.6553 | 121.4951 | 0.1236 | -121.8201
679.7812 | 121.994 | -121.637 | 0.036621 | -0.0082398 | 0.035795 | 0.008844 | 0.15088 | -0.0043323 | -0.0033646 | 0.14589 | 0.11902 | -0.036621 | 0.16479 | 0.14191 | 0.11444 | 0.21515 | -0.14648 | 0.068665 | -0.059509 | -121.8796 | 121.8018 | -0.073242 | 121.756 | 121.7789 | 0.07782 | -0.24262 | -0.09613 | -0.045776 | 121.4905 | 121.7056 | 121.7514 | 121.6003 | 121.756 | 121.5775 | 121.8521 | -0.24262 | 121.6003 | 121.756 | 121.8521 | 121.7514 | 121.5775 | 0.12817 | -121.9162
680.7812 | 121.7056 | -121.5225 | 0.059509 | -0.0082398 | 0.037504 | 0.0035034 | 0.01972 | -0.0041187 | -0.0012284 | 0.015793 | 0.045776 | -0.018311 | 0.1236 | 0.054932 | 0.004578 | 0.09613 | -0.004578 | -0.050354 | 0 | -121.7285 | 121.6461 | -0.07782 | 121.5683 | 121.5775 | -0.054931 | -0.20599 | -0.059509 | -0.07782 | 121.5179 | 121.4722 | 121.5271 | 121.5042 | 121.5683 | 121.5225 | 121.6187 | -0.20599 | 121.5042 | 121.5683 | 121.6187 | 121.5271 | 121.5225 | 0.064087 | -121.788
681.7812 | 121.8155 | -121.6232 | 0.091553 | -0.0082398 | 0.038785 | 0.0069214 | 0.021001 | -0.0019825 | -0.00486 | 0.019425 | 0.050354 | 0.004578 | 0.1236 | 0.032043 | -0.009155 | 0.09613 | 0.013733 | -0.07782 | 0.004578 | -121.8704 | 121.7468 | -0.086975 | 121.6736 | 121.6553 | -0.10071 | -0.24719 | -0.086975 | -0.073242 | 121.637 | 121.5454 | 121.6141 | 121.6278 | 121.6736 | 121.6278 | 121.7194 | -0.24719 | 121.6278 | 121.6736 | 121.7194 | 121.6141 | 121.6278 | 0.032043 | -121.962
682.7812 | 121.9391 | -121.637 | 0.045776 | -0.0082398 | 0.036863 | 0.0062806 | 0.033819 | -0.0041187 | -0.00486 | 0.046555 | 0.13275 | -0.041199 | 0.16022 | 0.15564 | 0.10986 | 0.2243 | -0.16937 | 0.050354 | -0.050354 | -121.8658 | 121.7972 | -0.086975 | 121.7697 | 121.7926 | 0.064087 | -0.22888 | -0.09613 | -0.027466 | 121.4676 | 121.6873 | 121.7468 | 121.5958 | 121.7697 | 121.5866 | 121.8613 | -0.22888 | 121.5958 | 121.7697 | 121.8613 | 121.7468 | 121.5866 | 0.11444 | -121.9116
683.7812 | 121.9666 | -121.6461 | 0.041199 | -0.00061033 | 0.039213 | 0.0067078 | 0.24808 | -0.0075367 | -0.0040054 | 0.25526 | 0.1236 | -0.022888 | 0.16479 | 0.13733 | 0.091553 | 0.21057 | -0.15564 | 0.054932 | -0.073242 | -121.8933 | 121.8109 | -0.064087 | 121.7697 | 121.7834 | 0.050354 | -0.24719 | -0.11444 | -0.041199 | 121.4905 | 121.701 | 121.7377 | 121.6232 | 121.7697 | 121.5729 | 121.8567 | -0.24719 | 121.6232 | 121.7697 | 121.8567 | 121.7377 | 121.5729 | 0.1236 | -121.9345
684.7812 | 121.6187 | -121.4172 | 0.091553 | -0.0082398 | 0.03494 | 0.007135 | 0.018438 | -0.0068957 | -0.0033646 | 0.015793 | 0.064087 | 0.009155 | 0.14191 | -0.009155 | -0.041199 | 0.054932 | -0.064087 | -1.4786 | 0.009155 | -121.6782 | 121.5591 | -0.082398 | 121.4813 | 121.4081 | -0.13275 | -0.26093 | -0.082398 | -0.07782 | 121.3531 | 119.9387 | 121.376 | 121.4264 | 121.4813 | 121.4264 | 121.4722 | -0.26093 | 121.4264 | 121.4813 | 121.4722 | 121.376 | 121.4264 | 0.050354 | -121.7697
685.7812 | 121.9208 | -121.5637 | 0.041199 | -0.00061033 | 0.027036 | 0.0075622 | 0.026556 | -0.0045459 | -0.0029374 | 0.016007 | 0.07782 | -0.013733 | 0.15564 | 0.10529 | 0.064087 | 0.17395 | -0.09613 | -0.98877 | -0.022888 | -121.8018 | 121.7194 | -0.054932 | 121.6415 | 121.669 | 0.022888 | -0.23804 | -0.064087 | -0.07782 | 121.4676 | 120.575 | 121.6278 | 121.55 | 121.6415 | 121.5408 | 121.7377 | -0.23804 | 121.55 | 121.6415 | 121.7377 | 121.6278 | 121.5408 | 0.11444 | -121.843
686.7812 | 121.8796 | -121.6232 | 0.073242 | -0.0082398 | 0.033445 | 0.0052124 | 0.025701 | -0.0036915 | -0.0012284 | 0.022629 | 0.036621 | 0.004578 | 0.13275 | 0.041199 | -0.013733 | 0.086975 | 0 | -3.2639 | -0.009155 | -121.8979 | 121.756 | -0.068664 | 121.6599 | 121.6644 | -0.086975 | -0.27466 | -0.082397 | -0.09613 | 121.6232 | 118.3594 | 121.6095 | 121.6278 | 121.6599 | 121.6141 | 121.7102 | -0.27466 | 121.6278 | 121.6599 | 121.7102 | 121.6095 | 121.6141 | 0.059509 | -121.9711
687.7812 | 121.6095 | -121.4355 | 0.068665 | -0.0082398 | 0.038572 | 0.014612 | 0.0088247 | -0.0026233 | -0.0033646 | 0.0053256 | 0.050354 | 0.009155 | 0.12817 | 0.018311 | -0.022888 | 0.091553 | 0 | -29.3106 | 0.004578 | -121.6782 | 121.5637 | -0.05951 | 121.4859 | 121.4539 | -0.091553 | -0.24262 | -0.064087 | -0.07782 | 121.4355 | 92.1249 | 121.4127 | 121.4447 | 121.4859 | 121.4401 | 121.5271 | -0.24262 | 121.4447 | 121.4859 | 121.5271 | 121.4127 | 121.4401 | 0.059509 | -121.7468
688.7812 | 121.6599 | -121.5317 | 0.09613 | -0.0082398 | 0.037076 | 0.007776 | 0.016943 | -0.0039051 | -0.0040054 | 0.026047 | 0.045776 | -0.004578 | 0.14191 | -0.022888 | -0.054932 | 0.032043 | -0.045776 | -0.51727 | 0.004578 | -121.7834 | 121.6736 | -0.10071 | 121.5775 | 121.5088 | -0.15106 | -0.25177 | -0.091552 | -0.096131 | 121.4859 | 121.0144 | 121.4767 | 121.5271 | 121.5775 | 121.5363 | 121.5637 | -0.25177 | 121.5271 | 121.5775 | 121.5637 | 121.4767 | 121.5363 | 0.045777 | -121.8796
689.7812 | 121.8384 | -121.582 | 0.068665 | -0.00061033 | 0.03729 | 0.0090576 | 0.031042 | -0.0028369 | -0.0020828 | 0.033524 | 0.036621 | -0.009155 | 0.14648 | 0.004578 | -0.022888 | 0.073242 | -0.045776 | -0.11444 | 0 | -121.875 | 121.7285 | -0.07782 | 121.6187 | 121.5866 | -0.091553 | -0.29297 | -0.068665 | -0.10986 | 121.5363 | 121.4676 | 121.5591 | 121.5729 | 121.6187 | 121.582 | 121.6553 | -0.29297 | 121.5729 | 121.6187 | 121.6553 | 121.5591 | 121.582 | 0.077819 | -121.9437
690.7812 | 121.7468 | -121.4584 | 0.050354 | -0.00061033 | 0.038358 | 0.00029916 | 0.024633 | -0.0047595 | -0.0044328 | 0.026047 | 0.086975 | -0.022888 | 0.11902 | 0.050354 | 0.027466 | 0.1236 | -0.11902 | -0.70496 | -0.009155 | -121.7148 | 121.5775 | -0.073242 | 121.5454 | 121.5088 | -0.022888 | -0.25635 | -0.059509 | -0.032044 | 121.3394 | 120.7535 | 121.4859 | 121.4355 | 121.5454 | 121.4493 | 121.582 | -0.25635 | 121.4355 | 121.5454 | 121.582 | 121.4859 | 121.4493 | 0.068665 | -121.7651
691.7812 | 121.788 | -121.5912 | 0.07782 | -0.0082398 | 0.038999 | 0.007135 | 0.017156 | -0.0060413 | -0.0037918 | 0.018357 | 0.041199 | 0.013733 | 0.13275 | 0 | -0.036621 | 0.068665 | -0.027466 | -0.1831 | 0 | -121.8521 | 121.7239 | -0.064087 | 121.6324 | 121.5912 | -0.11444 | -0.26093 | -0.07782 | -0.091552 | 121.5637 | 121.4081 | 121.5546 | 121.6049 | 121.6324 | 121.5912 | 121.6599 | -0.26093 | 121.6049 | 121.6324 | 121.6599 | 121.5546 | 121.5912 | 0.054931 | -121.9299
692.7969 | 121.8109 | -121.6461 | 0.086975 | -0.0082398 | 0.038785 | 0.005426 | 0.022924 | -0.0043323 | -0.004219 | 0.02092 | 0.054932 | 0.004578 | 0.13733 | 0.004578 | -0.036621 | 0.054932 | 0.004578 | -0.44861 | 0 | -121.8979 | 121.7834 | -0.082397 | 121.701 | 121.6507 | -0.1236 | -0.25177 | -0.086975 | -0.082397 | 121.6507 | 121.1975 | 121.6095 | 121.6507 | 121.701 | 121.6461 | 121.701 | -0.25177 | 121.6507 | 121.701 | 121.701 | 121.6095 | 121.6461 | 0.050354 | -121.9849
693.7812 | 121.8384 | -121.6324 | 0.073242 | 0.0070192 | 0.038358 | 0.0062806 | 0.18805 | -0.0047595 | -0.0037918 | 0.1899 | 0.032043 | 0.013733 | 0.1236 | 0.018311 | -0.018311 | 0.082397 | -0.009155 | -0.22888 | -0.004578 | -121.907 | 121.756 | -0.059509 | 121.6644 | 121.6507 | -0.091553 | -0.27466 | -0.07782 | -0.091553 | 121.6232 | 121.4035 | 121.6141 | 121.6461 | 121.6644 | 121.6278 | 121.7148 | -0.27466 | 121.6461 | 121.6644 | 121.7148 | 121.6141 | 121.6278 | 0.050354 | -121.9803
694.7812 | 121.669 | -121.4813 | 0.073242 | -0.0082398 | 0.033445 | 0.0035034 | 0.016088 | -0.0045459 | -0.0044328 | 0.014084 | 0.036621 | 0.004578 | 0.1236 | 0.013733 | -0.027466 | 0.086975 | 0.041199 | -0.27008 | 0 | -121.7834 | 121.6049 | -0.068664 | 121.5179 | 121.4951 | -0.10071 | -0.30212 | -0.073242 | -0.086975 | 121.5225 | 121.2112 | 121.4539 | 121.4859 | 121.5179 | 121.4813 | 121.5683 | -0.30212 | 121.4859 | 121.5179 | 121.5683 | 121.4539 | 121.4813 | 0.050354 | -121.8567
695.7812 | 121.756 | -121.6141 | 0.068665 | -0.0082398 | 0.032804 | 0.0056396 | 0.30149 | -0.0051867 | -0.0040054 | 0.35652 | 0.041199 | 0.004578 | 0.13275 | 0.045776 | 0 | 0.10986 | 0.013733 | -0.27924 | -0.032043 | -121.8384 | 121.7468 | -0.064087 | 121.6553 | 121.6599 | -0.068665 | -0.2243 | -0.10071 | -0.091552 | 121.6278 | 121.3348 | 121.6141 | 121.6187 | 121.6553 | 121.582 | 121.7239 | -0.2243 | 121.6187 | 121.6553 | 121.7239 | 121.6141 | 121.582 | 0.064086 | -121.907
696.7812 | 121.8155 | -121.6187 | 0.068665 | -0.0082398 | 0.030881 | 0.0047852 | 0.0094657 | -0.0073229 | -0.0035782 | 0.00062596 | 0.050354 | 0.009155 | 0.11902 | 0.045776 | 0.009155 | 0.11444 | 0 | -0.032043 | -0.018311 | -121.875 | 121.7377 | -0.05951 | 121.669 | 121.6644 | -0.05951 | -0.25635 | -0.086976 | -0.068665 | 121.6187 | 121.5866 | 121.6278 | 121.6278 | 121.669 | 121.6003 | 121.7331 | -0.25635 | 121.6278 | 121.669 | 121.7331 | 121.6278 | 121.6003 | 0.050354 | -121.9437
697.7812 | 121.8018 | -121.6553 | 0.068665 | -0.00061033 | 0.032804 | 0.0073486 | 0.029333 | -0.0041187 | -0.0016556 | 0.023056 | 0.050354 | 0.027466 | 0.12817 | 0.027466 | -0.009155 | 0.082397 | 0.036621 | -0.064087 | -0.013733 | -121.9345 | 121.7834 | -0.041199 | 121.7056 | 121.6827 | -0.07782 | -0.27924 | -0.082398 | -0.07782 | 121.6919 | 121.5912 | 121.6461 | 121.6827 | 121.7056 | 121.6415 | 121.7377 | -0.27924 | 121.6827 | 121.7056 | 121.7377 | 121.6461 | 121.6415 | 0.059509 | -122.0032
698.7812 | 121.8475 | -121.6599 | 0.073242 | -0.023499 | 0.036222 | 0.011194 | 0.023138 | -0.0041187 | -0.00486 | 0.01558 | 0.050354 | 0 | 0.11444 | 0.018311 | -0.027466 | 0.07782 | -0.004578 | -0.091553 | -0.004578 | -121.9482 | 121.7743 | -0.073242 | 121.7102 | 121.6782 | -0.10071 | -0.28839 | -0.07782 | -0.064087 | 121.6553 | 121.5683 | 121.6324 | 121.6599 | 121.7102 | 121.6553 | 121.7377 | -0.28839 | 121.6599 | 121.7102 | 121.7377 | 121.6324 | 121.6553 | 0.041199 | -122.0215
699.7812 | 121.8796 | -121.6873 | 0.064087 | -0.015869 | 0.035795 | 0.004358 | 0.024847 | -0.0039051 | -0.004219 | 0.017716 | 0.082397 | -0.004578 | 0.13733 | 0.054932 | 0.013733 | 0.10986 | -0.013733 | -0.041199 | -0.013733 | -121.9437 | 121.8246 | -0.068665 | 121.7697 | 121.7422 | -0.050354 | -0.25635 | -0.07782 | -0.054932 | 121.6736 | 121.6461 | 121.701 | 121.6827 | 121.7697 | 121.6736 | 121.7972 | -0.25635 | 121.6827 | 121.7697 | 121.7972 | 121.701 | 121.6736 | 0.073242 | -122.0078
700.7812 | 121.8384 | -121.6965 | 0.073242 | -0.015869 | 0.036435 | 0.005426 | 0.036169 | -0.0019825 | -0.0037918 | 0.032669 | 0.036621 | 0.018311 | 0.10986 | 0.013733 | -0.009155 | 0.07782 | 0.009155 | -0.13733 | -0.004578 | -121.9711 | 121.8063 | -0.054931 | 121.7331 | 121.7102 | -0.082397 | -0.27466 | -0.07782 | -0.073242 | 121.7056 | 121.5591 | 121.6873 | 121.7148 | 121.7331 | 121.6919 | 121.7743 | -0.27466 | 121.7148 | 121.7331 | 121.7743 | 121.6873 | 121.6919 | 0.036621 | -122.0444
701.7812 | 121.9391 | -121.7056 | 0.059509 | -0.0082398 | 0.037076 | 0.010339 | 0.075048 | -0.0043323 | -0.0035782 | 0.091843 | 0.11902 | -0.009155 | 0.15564 | 0.082397 | 0.027466 | 0.1236 | -0.027466 | 0.004578 | -0.022888 | -121.9757 | 121.8613 | -0.068664 | 121.8246 | 121.788 | -0.032043 | -0.27008 | -0.082397 | -0.036621 | 121.6782 | 121.7102 | 121.7331 | 121.6965 | 121.8246 | 121.6827 | 121.8292 | -0.27008 | 121.6965 | 121.8246 | 121.8292 | 121.7331 | 121.6827 | 0.096131 | -122.0352
702.7969 | 121.9528 | -121.6095 | 0.14648 | -0.00061033 | 0.10309 | 0.0073486 | 0.026769 | -0.0036915 | -0.0037918 | 0.095047 | 0.14648 | 0.050354 | 0.1831 | -0.32044 | -0.37537 | -0.28839 | -0.49896 | -1.0529 | 0.068665 | -121.8979 | 121.7926 | -0.09613 | 121.756 | 121.2891 | -0.52185 | -0.28839 | -0.077819 | -0.036621 | 121.1105 | 120.5566 | 121.2341 | 121.6599 | 121.756 | 121.6782 | 121.3211 | -0.28839 | 121.6599 | 121.756 | 121.3211 | 121.2341 | 121.6782 | 0.036621 | -122.0444
703.7812 | 121.8155 | -121.3486 | 0.35248 | -0.00061033 | 0.22207 | 0.010767 | 0.099401 | -0.0028369 | -0.001442 | 0.32896 | 0.35248 | 0.22888 | 0.36621 | -1.506 | -1.5244 | -1.4557 | -1.6342 | -40.6219 | 0.26093 | -121.582 | 121.7148 | -0.1236 | 121.7011 | 119.8425 | -1.8768 | -0.23346 | -0.091553 | -0.013733 | 119.7144 | 80.7266 | 119.8242 | 121.5775 | 121.7011 | 121.6095 | 119.8929 | -0.23346 | 121.5775 | 121.7011 | 119.8929 | 119.8242 | 121.6095 | 0.013733 | -121.9345
704.7812 | 121.8842 | -121.6827 | 0.091553 | -0.00061033 | 0.038144 | 0.008844 | 0.040655 | -0.0041187 | -0.0061416 | 0.032456 | 0.086975 | -0.009155 | 0.13275 | 0.073242 | 0.032043 | 0.1236 | 0.009155 | -0.091553 | -0.004578 | -121.9391 | 121.8155 | -0.10071 | 121.7697 | 121.756 | -0.05951 | -0.25635 | -0.096131 | -0.045776 | 121.6919 | 121.5912 | 121.7148 | 121.6736 | 121.7697 | 121.6782 | 121.8063 | -0.25635 | 121.6736 | 121.7697 | 121.8063 | 121.7148 | 121.6782 | 0.041198 | -122.0306
705.7812 | 121.9254 | -121.7148 | 0.064087 | -0.015869 | 0.034513 | 0.0064942 | 0.030614 | -0.0030505 | -0.0040054 | 0.024765 | 0.10071 | 0 | 0.13275 | 0.13275 | 0.073242 | 0.16937 | -0.013733 | -0.064087 | -0.018311 | -121.9757 | 121.8475 | -0.064087 | 121.8155 | 121.8475 | 0.009155 | -0.26093 | -0.082398 | -0.032043 | 121.701 | 121.6507 | 121.788 | 121.7148 | 121.8155 | 121.6965 | 121.8842 | -0.26093 | 121.7148 | 121.8155 | 121.8842 | 121.788 | 121.6965 | 0.068664 | -122.0398
706.7812 | 121.962 | -121.7422 | 0.064087 | -0.00061033 | 0.034513 | 0.0069214 | 0.025487 | -0.0028369 | -0.0022964 | 0.02092 | 0.10071 | -0.013733 | 0.13275 | 0.11902 | 0.091553 | 0.17395 | -0.027466 | -0.054932 | -0.013733 | -122.0261 | 121.875 | -0.07782 | 121.843 | 121.8613 | 0.027466 | -0.28381 | -0.07782 | -0.032043 | 121.7148 | 121.6873 | 121.8338 | 121.7285 | 121.843 | 121.7285 | 121.9162 | -0.28381 | 121.7285 | 121.843 | 121.9162 | 121.8338 | 121.7285 | 0.068664 | -122.0901
707.7812 | 121.9711 | -121.756 | 0.064087 | -0.0082398 | 0.036863 | 0.0056396 | 0.032537 | -0.0039051 | -0.001442 | 0.033097 | 0.10986 | 0 | 0.14648 | 0.11902 | 0.07782 | 0.15106 | -0.022888 | -0.41657 | -0.013733 | -122.0123 | 121.9025 | -0.064087 | 121.8658 | 121.875 | 0.013733 | -0.25635 | -0.07782 | -0.036621 | 121.7331 | 121.3394 | 121.8338 | 121.756 | 121.8658 | 121.7422 | 121.907 | -0.25635 | 121.756 | 121.8658 | 121.907 | 121.8338 | 121.7422 | 0.082397 | -122.0764
708.7812 | 121.9574 | -121.788 | 0.064087 | -0.00061033 | 0.034086 | 0.007776 | 0.023992 | -0.0039051 | -0.0033646 | 0.019638 | 0.041199 | 0.022888 | 0.11444 | 0.07782 | 0.027466 | 0.11444 | 0.054932 | -0.11902 | 0.004578 | -122.0261 | 121.9025 | -0.041199 | 121.8292 | 121.8658 | -0.036621 | -0.23804 | -0.059509 | -0.073242 | 121.843 | 121.669 | 121.8155 | 121.8109 | 121.8292 | 121.7926 | 121.9025 | -0.23804 | 121.8109 | 121.8292 | 121.9025 | 121.8155 | 121.7926 | 0.050354 | -122.0901
709.7812 | 121.2936 | -120.9732 | 0.11902 | -0.015869 | 0.039213 | 0.0049988 | 0.02976 | -0.0039051 | -0.003151 | 0.035233 | 0.068665 | 0.032043 | 0.12817 | -0.041199 | -0.07782 | 0.018311 | -0.09613 | -0.073242 | 0.013733 | -121.2799 | 121.1014 | -0.086976 | 121.0419 | 120.932 | -0.19684 | -0.3067 | -0.10529 | -0.059509 | 120.8771 | 120.9 | 120.8954 | 121.0052 | 121.0419 | 120.9869 | 120.9915 | -0.3067 | 121.0052 | 121.0419 | 120.9915 | 120.8954 | 120.9869 | 0.009155 | -121.3989
710.7812 | 121.8933 | -121.5363 | 0.1831 | -0.015869 | 0.10714 | 0.010126 | 0.058813 | -0.0043323 | -0.00486 | 0.13008 | 0.17853 | 0.086975 | 0.20599 | -0.50812 | -0.56763 | -0.4715 | -0.62256 | -40.7959 | 0.07782 | -121.8201 | 121.7422 | -0.09613 | 121.7148 | 121.0281 | -0.75073 | -0.28381 | -0.10528 | -0.027466 | 120.9137 | 80.7404 | 120.9686 | 121.6232 | 121.7148 | 121.6141 | 121.0648 | -0.28381 | 121.6232 | 121.7148 | 121.0648 | 120.9686 | 121.6141 | 0.022889 | -122.0032
711.7812 | 121.8933 | -121.7148 | 0.086975 | 0.0070192 | 0.029172 | 0.0032898 | 0.018652 | -0.0034777 | -0.0018692 | 0.015366 | 0.027466 | -0.004578 | 0.091553 | 0.022888 | -0.009155 | 0.07782 | 0.045776 | -1.3596 | 0.013733 | -121.994 | 121.8063 | -0.091553 | 121.7422 | 121.7377 | -0.09613 | -0.27924 | -0.073242 | -0.064087 | 121.7606 | 120.3552 | 121.7056 | 121.7102 | 121.7422 | 121.7285 | 121.7926 | -0.27924 | 121.7102 | 121.7422 | 121.7926 | 121.7056 | 121.7285 | 0.004578 | -122.081
712.7969 | 122.0123 | -121.7606 | 0.064087 | 0.0070192 | 0.026395 | 0.0035034 | 0.018652 | -0.0060413 | -0.0050736 | 0.019211 | 0.11902 | -0.036621 | 0.16022 | 0.1236 | 0.10071 | 0.19226 | -0.073242 | -1.5335 | -0.013733 | -121.9482 | 121.9208 | -0.10071 | 121.8796 | 121.8842 | 0.036621 | -0.18768 | -0.07782 | -0.041198 | 121.6873 | 120.2271 | 121.8613 | 121.7239 | 121.8796 | 121.7468 | 121.9528 | -0.18768 | 121.7239 | 121.8796 | 121.9528 | 121.8613 | 121.7468 | 0.09613 | -122.0123
713.7812 | 121.9391 | -121.8246 | 0.073242 | -0.0082398 | 0.027677 | 0.0030762 | 0.028478 | -0.0075367 | -0.0050736 | 0.024338 | 0.032043 | -0.013733 | 0.11902 | 0.064087 | 0.041199 | 0.10071 | 0.054932 | -2.298 | 0.004578 | -122.0215 | 121.9437 | -0.086975 | 121.8567 | 121.8887 | -0.032043 | -0.19684 | -0.068664 | -0.086976 | 121.8796 | 119.5267 | 121.8658 | 121.8109 | 121.8567 | 121.8292 | 121.9254 | -0.19684 | 121.8109 | 121.8567 | 121.9254 | 121.8658 | 121.8292 | 0.045777 | -122.0947
714.7812 | 121.9437 | -121.7834 | 0.086975 | -0.00061033 | 0.034086 | 0.007135 | 0.02976 | -0.0060413 | -0.0018692 | 0.020279 | 0.091553 | -0.009155 | 0.12817 | 0.091553 | 0.032043 | 0.10986 | 0 | -0.75531 | -0.018311 | -122.0673 | 121.9116 | -0.09613 | 121.875 | 121.875 | -0.054932 | -0.28381 | -0.10529 | -0.036621 | 121.7834 | 121.0281 | 121.8155 | 121.7743 | 121.875 | 121.7651 | 121.8933 | -0.28381 | 121.7743 | 121.875 | 121.8933 | 121.8155 | 121.7651 | 0.041199 | -122.1542
715.7812 | 122.0627 | -121.756 | 0.054932 | -0.00061033 | 0.03024 | 0.0017944 | 0.28611 | -0.0056141 | -0.00486 | 0.27321 | 0.15106 | -0.036621 | 0.16479 | 0.13275 | 0.091553 | 0.17395 | -0.1831 | -61.8256 | -0.082397 | -121.9345 | 121.9208 | -0.091553 | 121.907 | 121.8887 | 0.036621 | -0.17853 | -0.13733 | -0.013733 | 121.5729 | 59.9304 | 121.8475 | 121.7194 | 121.907 | 121.6736 | 121.9299 | -0.17853 | 121.7194 | 121.907 | 121.9299 | 121.8475 | 121.6736 | 0.10986 | -121.9894
716.7812 | 122.081 | -121.8109 | 0.054932 | -0.00061033 | 0.025754 | 0.0052124 | 0.075475 | -0.0081775 | -0.00486 | 0.023484 | 0.13733 | -0.054932 | 0.15564 | 0.18768 | 0.12817 | 0.2243 | -0.091553 | -3.6301 | -0.036621 | -122.0215 | 121.9666 | -0.10986 | 121.9482 | 121.9986 | 0.073242 | -0.21057 | -0.091553 | -0.018311 | 121.7194 | 118.1808 | 121.9391 | 121.756 | 121.9482 | 121.7743 | 122.0352 | -0.21057 | 121.756 | 121.9482 | 122.0352 | 121.9391 | 121.7743 | 0.10071 | -122.0764
717.7812 | 122.0306 | -121.843 | 0.050354 | -0.00061033 | 0.051175 | 0.004358 | 0.29102 | -0.0081775 | -0.004219 | 0.23689 | 0.15564 | -0.009155 | 0.17853 | -0.054932 | -0.10529 | 0.059509 | -0.11444 | -3.5889 | 0 | -122.0352 | 122.0215 | -0.059509 | 121.9986 | 121.788 | -0.15564 | -0.19226 | -0.050354 | -0.022888 | 121.7285 | 118.2541 | 121.7377 | 121.8338 | 121.9986 | 121.843 | 121.9025 | -0.19226 | 121.8338 | 121.9986 | 121.9025 | 121.7377 | 121.843 | 0.12817 | -122.0856
718.7812 | 121.9254 | -121.5912 | 0.31586 | -0.00061033 | 0.23575 | 0.006067 | 0.40146 | -0.0075367 | -0.0020828 | 0.59343 | 0.27924 | 0.19684 | 0.33875 | -1.4786 | -1.5289 | -1.4603 | -1.5198 | -69.9738 | 0.19684 | -121.7651 | 121.9299 | -0.11902 | 121.8704 | 120.1126 | -1.8448 | -0.17395 | -0.11902 | -0.059509 | 120.0714 | 51.6174 | 120.0623 | 121.788 | 121.8704 | 121.788 | 120.1309 | -0.17395 | 121.788 | 121.8704 | 120.1309 | 120.0623 | 121.788 | 0.022888 | -122.081
719.7969 | 121.669 | -121.5317 | 0.073242 | -0.015869 | 0.032377 | 0.0069214 | 0.033605 | -0.0066821 | -0.0037918 | 0.021775 | 0.10986 | -0.004578 | 0.13275 | 0.10986 | 0.041199 | 0.11444 | 0 | 0.032043 | -0.004578 | -121.7697 | 121.6644 | -0.07782 | 121.6415 | 121.6415 | -0.032043 | -0.23804 | -0.07782 | -0.022888 | 121.5317 | 121.5637 | 121.5729 | 121.5271 | 121.6415 | 121.5271 | 121.6461 | -0.23804 | 121.5271 | 121.6415 | 121.6461 | 121.5729 | 121.5271 | 0.059509 | -121.843
720.7812 | 121.8933 | -121.6232 | 0.045776 | -0.0082398 | 0.022123 | 0.0035034 | 0.040655 | -0.0068957 | -0.0022964 | 0.027756 | 0.13275 | -0.045776 | 0.16022 | 0.20599 | 0.15106 | 0.23804 | -0.12817 | 0.15564 | -0.036621 | -121.8201 | 121.7834 | -0.091552 | 121.756 | 121.8292 | 0.10529 | -0.19684 | -0.082397 | -0.027466 | 121.4951 | 121.7789 | 121.7743 | 121.5775 | 121.756 | 121.5866 | 121.8613 | -0.19684 | 121.5775 | 121.756 | 121.8613 | 121.7743 | 121.5866 | 0.11444 | -121.8658
721.7812 | 121.8933 | -121.6599 | 0.041199 | 0.0070192 | 0.026822 | 0.0058534 | 0.20493 | -0.0071093 | -0.0037918 | 0.19887 | 0.13275 | -0.050354 | 0.17853 | 0.17853 | 0.1236 | 0.20599 | -0.10986 | 0.11444 | -0.045776 | -121.8338 | 121.8384 | -0.091553 | 121.7926 | 121.8384 | 0.082397 | -0.17395 | -0.086975 | -0.045777 | 121.55 | 121.7743 | 121.7834 | 121.6095 | 121.7926 | 121.6141 | 121.8658 | -0.17395 | 121.6095 | 121.7926 | 121.8658 | 121.7834 | 121.6141 | 0.13733 | -121.875
722.8125 | 121.8384 | -121.701 | 0.073242 | -0.023499 | 0.033872 | 0.0090576 | 0.031469 | -0.0077503 | -0.0040054 | 0.018357 | 0.09613 | -0.004578 | 0.14191 | 0.091553 | 0.027466 | 0.10529 | 0.004578 | 0.009155 | -0.013733 | -121.9666 | 121.843 | -0.07782 | 121.7972 | 121.7926 | -0.045776 | -0.2655 | -0.086975 | -0.045777 | 121.7056 | 121.7102 | 121.7285 | 121.6965 | 121.7972 | 121.6873 | 121.8063 | -0.2655 | 121.6965 | 121.7972 | 121.8063 | 121.7285 | 121.6873 | 0.068665 | -122.0398
723.7812 | 122.0032 | -121.7285 | 0.036621 | -0.00061033 | 0.025754 | 0.0015808 | 0.028692 | -0.0075367 | -0.0033646 | 0.023911 | 0.12817 | -0.050354 | 0.14648 | 0.17853 | 0.14648 | 0.23804 | -0.14191 | 0.13733 | -0.041199 | -121.9208 | 121.875 | -0.086975 | 121.8567 | 121.907 | 0.10986 | -0.19226 | -0.07782 | -0.01831 | 121.5866 | 121.8658 | 121.875 | 121.6782 | 121.8567 | 121.6873 | 121.9666 | -0.19226 | 121.6782 | 121.8567 | 121.9666 | 121.875 | 121.6873 | 0.10986 | -121.9574
724.7969 | 121.9299 | -121.7102 | 0.073242 | -0.015869 | 0.033872 | 0.0056396 | 0.062231 | -0.0062549 | -0.004219 | 0.060868 | 0.10986 | -0.013733 | 0.13275 | 0.11902 | 0.041199 | 0.11902 | -0.059509 | 0.036621 | -0.009155 | -121.9803 | 121.843 | -0.086975 | 121.8201 | 121.8292 | -0.032043 | -0.27008 | -0.082397 | -0.022888 | 121.6507 | 121.7468 | 121.7514 | 121.6965 | 121.8201 | 121.701 | 121.8292 | -0.27008 | 121.6965 | 121.8201 | 121.8292 | 121.7514 | 121.701 | 0.059509 | -122.0535
725.7812 | 121.7514 | -121.4127 | 0.032043 | -0.0082398 | 0.02725 | 0.002649 | 0.01267 | -0.0068957 | -0.0050736 | 0.0083164 | 0.14191 | -0.064087 | 0.17395 | 0.17395 | 0.14648 | 0.22888 | -0.16022 | 0.15106 | -0.022888 | -121.6232 | 121.5866 | -0.09613 | 121.5546 | 121.5866 | 0.11444 | -0.21057 | -0.054931 | -0.032043 | 121.2524 | 121.5637 | 121.5591 | 121.3486 | 121.5546 | 121.3898 | 121.6415 | -0.21057 | 121.3486 | 121.5546 | 121.6415 | 121.5591 | 121.3898 | 0.14191 | -121.6553
726.7812 | 121.9391 | -121.6461 | 0.045776 | -0.00061033 | 0.02725 | 0.0058534 | 0.020147 | -0.0073229 | -0.003151 | 0.013871 | 0.15106 | -0.059509 | 0.16479 | 0.16479 | 0.13275 | 0.23346 | -0.15106 | 0.14648 | -0.027466 | -121.8384 | 121.8109 | -0.10528 | 121.7972 | 121.8109 | 0.086975 | -0.19226 | -0.073242 | -0.013733 | 121.4951 | 121.7926 | 121.7789 | 121.5866 | 121.7972 | 121.6187 | 121.8796 | -0.19226 | 121.5866 | 121.7972 | 121.8796 | 121.7789 | 121.6187 | 0.11902 | -121.8842
727.7812 | 122.0169 | -121.701 | 0.054932 | -0.0082398 | 0.027677 | 0.002649 | 0.049413 | -0.0096729 | -0.0037918 | 0.044205 | 0.11444 | -0.050354 | 0.17853 | 0.15564 | 0.11444 | 0.21973 | -0.14191 | 0.11444 | -0.041199 | -121.8704 | 121.8796 | -0.10529 | 121.8155 | 121.8567 | 0.059509 | -0.16937 | -0.096131 | -0.064087 | 121.5591 | 121.8155 | 121.8155 | 121.6507 | 121.8155 | 121.6599 | 121.9208 | -0.16937 | 121.6507 | 121.8155 | 121.9208 | 121.8155 | 121.6599 | 0.1236 | -121.9254
728.7812 | 122.0306 | -121.7102 | 0.050354 | -0.00061033 | 0.027463 | 0.0013672 | 0.02207 | -0.0096729 | -0.0037918 | 0.01857 | 0.14191 | -0.050354 | 0.16479 | 0.19226 | 0.15106 | 0.23346 | -0.16937 | 0.16022 | -0.022888 | -121.9208 | 121.875 | -0.10071 | 121.8521 | 121.9025 | 0.10071 | -0.21057 | -0.073242 | -0.022888 | 121.5408 | 121.8704 | 121.8613 | 121.6599 | 121.8521 | 121.6873 | 121.9437 | -0.21057 | 121.6599 | 121.8521 | 121.9437 | 121.8613 | 121.6873 | 0.11444 | -121.9711
729.7969 | 121.962 | -121.7331 | 0.086975 | -0.015869 | 0.035154 | 0.0079896 | 0.070989 | -0.0075367 | -0.004219 | 0.055313 | 0.059509 | 0.009155 | 0.13733 | 0.068665 | 0.018311 | 0.09613 | 0 | -0.004578 | -0.013733 | -121.9894 | 121.8704 | -0.07782 | 121.7926 | 121.8018 | -0.068664 | -0.25635 | -0.10071 | -0.07782 | 121.7331 | 121.7285 | 121.7514 | 121.7422 | 121.7926 | 121.7194 | 121.8292 | -0.25635 | 121.7422 | 121.7926 | 121.8292 | 121.7514 | 121.7194 | 0.050354 | -122.0764
730.7812 | 122.0078 | -121.7377 | 0.050354 | -0.00061033 | 0.030668 | 0.003717 | 0.05689 | -0.0086047 | -0.004219 | 0.054459 | 0.064087 | -0.027466 | 0.15564 | 0.11902 | 0.073242 | 0.15564 | -0.1236 | 0.045776 | 0.004578 | -121.8796 | 121.8933 | -0.07782 | 121.8018 | 121.8567 | 0.022888 | -0.14191 | -0.045776 | -0.091553 | 121.6141 | 121.7834 | 121.8109 | 121.7102 | 121.8018 | 121.7422 | 121.8933 | -0.14191 | 121.7102 | 121.8018 | 121.8933 | 121.8109 | 121.7422 | 0.10529 | -121.9299
731.7812 | 122.0398 | -121.7651 | 0.050354 | -0.0082398 | 0.030027 | -0.0016236 | 0.025487 | -0.0098865 | -0.0033646 | 0.021561 | 0.10529 | -0.059509 | 0.13275 | 0.13275 | 0.091553 | 0.19226 | -0.15106 | 0.086975 | -0.050354 | -121.9757 | 121.8979 | -0.10986 | 121.8704 | 121.8979 | 0.041199 | -0.21057 | -0.10071 | -0.027465 | 121.6141 | 121.8521 | 121.8567 | 121.7056 | 121.8704 | 121.7148 | 121.9574 | -0.21057 | 121.7056 | 121.8704 | 121.9574 | 121.8567 | 121.7148 | 0.082397 | -122.0261
732.7969 | 122.0581 | -121.7514 | 0.032043 | -0.00061033 | 0.0296 | 0.0062806 | 0.042577 | -0.0092457 | -0.0050736 | 0.026047 | 0.1236 | -0.041199 | 0.16022 | 0.1831 | 0.1236 | 0.21515 | -0.15106 | 0.10071 | -0.050354 | -121.9666 | 121.9116 | -0.073242 | 121.875 | 121.9345 | 0.091553 | -0.21515 | -0.082397 | -0.036621 | 121.6003 | 121.8521 | 121.875 | 121.7102 | 121.875 | 121.701 | 121.9666 | -0.21515 | 121.7102 | 121.875 | 121.9666 | 121.875 | 121.701 | 0.12817 | -121.9986
733.7812 | 122.0718 | -121.7926 | 0.027466 | -0.015869 | 0.023618 | 0.00072636 | 0.07868 | -0.0088183 | -0.004219 | 0.079026 | 0.073242 | -0.036621 | 0.15106 | 0.13733 | 0.10071 | 0.20142 | -0.086975 | 0.09613 | -0.059509 | -121.9254 | 121.9437 | -0.064087 | 121.8658 | 121.9299 | 0.073242 | -0.13275 | -0.086975 | -0.07782 | 121.7056 | 121.8887 | 121.8933 | 121.756 | 121.8658 | 121.7331 | 121.994 | -0.13275 | 121.756 | 121.8658 | 121.994 | 121.8933 | 121.7331 | 0.1236 | -121.9528
734.7812 | 121.637 | -121.3715 | 0.21515 | -0.00061033 | 0.11548 | 0.0039306 | 0.059026 | -0.0071093 | -0.00058736 | 0.13948 | 0.17395 | 0.1236 | 0.24261 | -0.71869 | -0.75073 | -0.67291 | -0.69122 | -0.79651 | 0.11902 | -121.5591 | 121.6141 | -0.091553 | 121.5454 | 120.6528 | -0.96588 | -0.18768 | -0.09613 | -0.068665 | 120.6802 | 120.575 | 120.6207 | 121.4951 | 121.5454 | 121.4905 | 120.6985 | -0.18768 | 121.4951 | 121.5454 | 120.6985 | 120.6207 | 121.4905 | 0.027466 | -121.7743
735.7812 | 121.3943 | -107.3914 | 2.9892 | -0.0082398 | 0.010373 | 0.0015808 | 0.025487 | -0.0041187 | -0.0012284 | 0.010666 | 0.068665 | -0.068665 | 0.11902 | 0.20599 | 0.16479 | 0.27008 | 0.013733 | 0.16479 | 2.9114 | -118.4235 | 107.5104 | -3.0579 | 107.46 | 107.5974 | -2.8244 | -11.0321 | -0.07782 | -0.050354 | 107.4051 | 107.5562 | 107.5562 | 107.3227 | 107.46 | 110.3027 | 107.6614 | -11.0321 | 107.3227 | 107.46 | 107.6614 | 107.5562 | 110.3027 | -2.8702 | -121.4127
736.7812 | 121.788 | -120.1859 | 1.4282 | -0.0082398 | 0.010373 | 0.00072636 | 0.032323 | -0.0073229 | -0.0027238 | 0.012802 | 0.059509 | -0.064087 | 0.1236 | 0.21515 | 0.16937 | 0.26093 | 0.013733 | 0.14648 | 1.3367 | -120.2911 | 120.3094 | -1.4923 | 120.2454 | 120.401 | -1.2589 | -0.10529 | -0.091553 | -0.064087 | 120.1996 | 120.3323 | 120.3552 | 120.1218 | 120.2454 | 121.5225 | 120.4468 | -0.10529 | 120.1218 | 120.2454 | 120.4468 | 120.3552 | 121.5225 | -1.3046 | -121.7194
737.7812 | 121.8155 | -119.8517 | 1.8036 | -0.0082398 | 0.0099463 | -0.00034184 | 0.038091 | -0.0092457 | -0.00080116 | 0.025193 | 0.068665 | -0.064087 | 0.1236 | 0.23804 | 0.19684 | 0.28839 | -0.004578 | 0.18768 | 1.6251 | -120.0394 | 119.9753 | -1.8677 | 119.9203 | 120.0897 | -1.6068 | -0.18768 | -0.17853 | -0.054931 | 119.8471 | 120.0394 | 120.0485 | 119.7876 | 119.9203 | 121.4767 | 120.1401 | -0.18768 | 119.7876 | 119.9203 | 120.1401 | 120.0485 | 121.4767 | -1.68 | -121.843
738.7812 | 121.875 | -109.4604 | 12.1994 | -0.00061033 | 0.010801 | 0.00072636 | 0.27649 | -0.0026233 | 0.0038986 | 0.26595 | 0.091553 | -0.07782 | 0.14191 | 0.26093 | 0.21515 | 0.31586 | -0.064087 | 0.21515 | 12.0483 | -109.5566 | 109.6024 | -12.2772 | 109.552 | 109.7214 | -11.9843 | -0.096131 | -0.15106 | -0.050354 | 109.3964 | 109.6756 | 109.6756 | 109.3826 | 109.552 | 121.5088 | 109.7763 | -0.096131 | 109.3826 | 109.552 | 109.7763 | 109.6756 | 121.5088 | -12.0575 | -121.756
739.7812 | 121.8109 | -118.3594 | 3.3554 | -0.00061033 | 0.011014 | 0.0062806 | 0.073339 | -0.0058277 | -0.0035782 | 0.024552 | 0.013733 | -0.036621 | 0.10529 | 0.14648 | 0.086975 | 0.17395 | 0.091553 | 0.050354 | 3.2822 | -118.5516 | 118.4647 | -3.392 | 118.3731 | 118.5059 | -3.2684 | -0.19226 | -0.073242 | -0.091553 | 118.4509 | 118.4097 | 118.4463 | 118.3228 | 118.3731 | 121.6415 | 118.5333 | -0.19226 | 118.3228 | 118.3731 | 118.5333 | 118.4463 | 121.6415 | -3.2501 | -121.907
740.7812 | 121.8521 | -99.2294 | 22.3892 | 0.0070192 | 0.010801 | 0.00093996 | 1.3655 | 0.0039991 | 0.0058212 | 1.377 | 0.068665 | -0.064087 | 0.11902 | 0.21057 | 0.17395 | 0.28381 | -0.086975 | 0.15564 | 22.2748 | -99.1562 | 99.3484 | -22.4533 | 99.2981 | 99.44 | -22.2153 | 0.073242 | -0.11444 | -0.050354 | 99.1425 | 99.3851 | 99.4034 | 99.1653 | 99.2981 | 121.5042 | 99.5132 | 0.073242 | 99.1653 | 99.2981 | 99.5132 | 99.4034 | 121.5042 | -22.2702 | -121.5454
741.7812 | 121.9345 | -121.3669 | 0.36163 | 0.014648 | 0.010801 | 0.0045716 | 0.057531 | -0.0086047 | -0.0018692 | 0.050186 | 0.073242 | -0.064087 | 0.15106 | 0.20142 | 0.17395 | 0.25177 | -0.009155 | 0.13733 | 0.27924 | -121.5546 | 121.5179 | -0.42572 | 121.4401 | 121.5683 | -0.18768 | -0.18768 | -0.082397 | -0.07782 | 121.3577 | 121.5042 | 121.5408 | 121.3028 | 121.4401 | 121.6461 | 121.6187 | -0.18768 | 121.3028 | 121.4401 | 121.6187 | 121.5408 | 121.6461 | -0.21057 | -121.9162
742.7969 | 121.8979 | -121.3852 | 0.37537 | -0.0082398 | 0.019987 | 0.0062806 | 0.096838 | -0.0062549 | -0.0025102 | 0.037796 | 0.073242 | -0.041199 | 0.13733 | 0.20599 | 0.17395 | 0.26093 | -0.032043 | 0.12817 | 0.27924 | -121.5775 | 121.5225 | -0.41656 | 121.4584 | 121.5912 | -0.20142 | -0.19226 | -0.09613 | -0.064087 | 121.3531 | 121.5134 | 121.5591 | 121.344 | 121.4584 | 121.6644 | 121.6461 | -0.19226 | 121.344 | 121.4584 | 121.6461 | 121.5591 | 121.6644 | -0.23804 | -121.9528
743.7812 | 121.9299 | -121.2708 | 0.4303 | -0.00061033 | 0.0097327 | 0.0022218 | 0.43671 | -0.0075367 | -0.0037918 | 0.4157 | 0.10529 | -0.059509 | 0.14648 | 0.25635 | 0.20599 | 0.31586 | -0.07782 | 0.16479 | 0.3067 | -121.4218 | 121.4172 | -0.48981 | 121.376 | 121.5271 | -0.2243 | -0.15106 | -0.1236 | -0.041198 | 121.1929 | 121.4355 | 121.4767 | 121.2112 | 121.376 | 121.5775 | 121.5866 | -0.15106 | 121.2112 | 121.376 | 121.5866 | 121.4767 | 121.5775 | -0.28381 | -121.8521
744.7812 | 121.6782 | -121.3577 | 0.15106 | -0.0082398 | 0.011014 | 0.0015808 | 0.1417 | -0.0071093 | -0.0020828 | 0.13799 | 0.068665 | -0.068665 | 0.11444 | 0.1831 | 0.16022 | 0.23804 | 0.004578 | 0.13733 | 0.032043 | -121.5271 | 121.4722 | -0.21973 | 121.4264 | 121.5408 | 0.009155 | -0.16937 | -0.11902 | -0.045776 | 121.3623 | 121.4951 | 121.5179 | 121.2891 | 121.4264 | 121.3898 | 121.5958 | -0.16937 | 121.2891 | 121.4264 | 121.5958 | 121.5179 | 121.3898 | -0.036621 | -121.6782
745.7812 | 121.7834 | -121.5317 | 0.11444 | 0.0070192 | 0.010587 | 0.0045716 | 0.034887 | -0.0060413 | -0.00486 | 0.019425 | 0.059509 | -0.064087 | 0.15106 | 0.19684 | 0.15564 | 0.24719 | -0.013733 | 0.13733 | 0.041199 | -121.6599 | 121.6827 | -0.17853 | 121.5912 | 121.7285 | 0.041199 | -0.12817 | -0.073242 | -0.091553 | 121.5179 | 121.669 | 121.6873 | 121.4676 | 121.5912 | 121.5729 | 121.7789 | -0.12817 | 121.4676 | 121.5912 | 121.7789 | 121.6873 | 121.5729 | 0.036621 | -121.7743
746.7812 | 121.8567 | -121.4951 | 0.17853 | -0.00061033 | 0.0071693 | 0.0017944 | 0.17246 | -0.0083911 | -0.0037918 | 0.17473 | 0.12817 | -0.086975 | 0.14648 | 0.28839 | 0.21973 | 0.32501 | -0.050354 | 0.23346 | 0.082397 | -121.5683 | 121.6415 | -0.2655 | 121.6232 | 121.7834 | 0.041199 | -0.073242 | -0.096131 | -0.01831 | 121.4447 | 121.7285 | 121.7148 | 121.4081 | 121.6232 | 121.5775 | 121.8201 | -0.073242 | 121.4081 | 121.6232 | 121.8201 | 121.7148 | 121.5775 | -0.032044 | -121.7468
747.7812 | 121.8704 | -121.5271 | 0.10071 | -0.00061033 | 0.0097327 | -0.00098264 | 0.034887 | -0.0068957 | -0.0037918 | 0.018357 | 0.07782 | -0.064087 | 0.15106 | 0.21515 | 0.16022 | 0.25177 | -0.032043 | 0.15106 | 0.004578 | -121.7239 | 121.6782 | -0.1648 | 121.6049 | 121.7422 | 0.059509 | -0.19684 | -0.09613 | -0.073242 | 121.4951 | 121.6782 | 121.6873 | 121.463 | 121.6049 | 121.5317 | 121.7789 | -0.19684 | 121.463 | 121.6049 | 121.7789 | 121.6873 | 121.5317 | 0.050354 | -121.8246
748.7812 | 121.9025 | -121.5637 | 0.11902 | -0.00061033 | 0.01016 | 0.0062806 | 0.057104 | -0.0094593 | -0.0025102 | 0.037583 | 0.073242 | -0.064087 | 0.13733 | 0.20599 | 0.15106 | 0.24719 | -0.022888 | 0.12817 | 0.027466 | -121.7468 | 121.701 | -0.18311 | 121.637 | 121.7697 | 0.032043 | -0.1831 | -0.091553 | -0.064087 | 121.5408 | 121.6919 | 121.7148 | 121.4996 | 121.637 | 121.5912 | 121.8109 | -0.1831 | 121.4996 | 121.637 | 121.8109 | 121.7148 | 121.5912 | 0.01831 | -121.8658
749.7812 | 121.8887 | -121.6095 | 0.11444 | -0.00061033 | 0.011228 | 0.00051276 | 0.044927 | -0.0088183 | -0.0040054 | 0.024338 | 0.068665 | -0.073242 | 0.13733 | 0.21057 | 0.15564 | 0.25635 | -0.013733 | 0.15106 | 0.009155 | -121.7606 | 121.7468 | -0.18768 | 121.6782 | 121.8201 | 0.041199 | -0.15106 | -0.10529 | -0.068664 | 121.5958 | 121.7606 | 121.7651 | 121.5363 | 121.6782 | 121.6187 | 121.8658 | -0.15106 | 121.5363 | 121.6782 | 121.8658 | 121.7651 | 121.6187 | 0.022888 | -121.875
750.7812 | 121.8933 | -121.582 | 0.12817 | 0.0070192 | 0.0082373 | 0.003717 | 0.041082 | -0.0094593 | -0.0052872 | 0.020066 | 0.064087 | -0.064087 | 0.14191 | 0.20599 | 0.14648 | 0.25635 | -0.027466 | 0.14191 | 0.022888 | -121.7651 | 121.7239 | -0.19226 | 121.6461 | 121.788 | 0.01831 | -0.18311 | -0.10529 | -0.07782 | 121.5546 | 121.7239 | 121.7285 | 121.5179 | 121.6461 | 121.6049 | 121.8384 | -0.18311 | 121.5179 | 121.6461 | 121.8384 | 121.7285 | 121.6049 | 0.013733 | -121.8933
751.7812 | 121.5271 | -86.4166 | 34.8953 | 0.43427 | 0.0043921 | 0.0011536 | 0.13807 | 0.014894 | 0.015861 | 0.15871 | 0.064087 | -0.086975 | 0.1236 | 0.17395 | 0.10986 | 0.21057 | -0.10071 | 0.09613 | 34.1354 | -87.4329 | 86.5402 | -34.9823 | 86.4807 | 86.5906 | -34.7855 | -1.0162 | -0.75989 | -0.059509 | 86.3159 | 86.5128 | 86.5265 | 86.3297 | 86.4807 | 120.5521 | 86.6272 | -1.0162 | 86.3297 | 86.4807 | 86.6272 | 86.5265 | 120.5521 | -34.7717 | -122.3282
752.7969 | 121.9025 | -121.4905 | 0.16479 | -0.00061033 | 0.014432 | 0.007135 | 0.27009 | -0.0041187 | -0.003151 | 0.23988 | 0.073242 | -0.041199 | 0.12817 | 0.21515 | 0.14191 | 0.25177 | -0.050354 | 0.13733 | 0.07782 | -121.7194 | 121.6187 | -0.20599 | 121.5637 | 121.7056 | -0.022888 | -0.22888 | -0.086975 | -0.054932 | 121.4401 | 121.6278 | 121.6324 | 121.4493 | 121.5637 | 121.5683 | 121.7422 | -0.22888 | 121.4493 | 121.5637 | 121.7422 | 121.6324 | 121.5683 | -0.036621 | -121.8842
753.7812 | 120.3369 | -97.8516 | 22.1237 | -0.015869 | 0.011228 | 0.005426 | 0.47965 | 0.0042127 | 0.0075302 | 0.48683 | 0.10986 | -0.07782 | 0.13275 | 0.21515 | 0.16937 | 0.25635 | -0.12817 | 0.1236 | 21.6202 | -98.1628 | 97.9843 | -22.2015 | 97.9614 | 98.0667 | -21.9543 | -0.31128 | -0.50354 | -0.022888 | 97.7234 | 97.9752 | 98.0209 | 97.7737 | 97.9614 | 119.4717 | 98.1079 | -0.31128 | 97.7737 | 97.9614 | 98.1079 | 98.0209 | 119.4717 | -21.991 | -120.2866
754.7812 | 121.7148 | -121.3898 | 0.10529 | 0.0070192 | 0.0073829 | 0.007135 | 0.029119 | -0.0073229 | -0.0029374 | 0.010666 | 0.073242 | -0.07782 | 0.13733 | 0.21515 | 0.15564 | 0.25635 | -0.036621 | 0.15106 | 0.004578 | -121.5912 | 121.5271 | -0.18311 | 121.463 | 121.6049 | 0.050354 | -0.20142 | -0.10071 | -0.064087 | 121.3531 | 121.5408 | 121.5454 | 121.312 | 121.463 | 121.3943 | 121.6461 | -0.20142 | 121.312 | 121.463 | 121.6461 | 121.5454 | 121.3943 | 0.032043 | -121.6965
755.7812 | 118.2587 | -97.934 | 19.7617 | -0.0082398 | 0.013791 | -0.0020508 | 6.943 | -0.0024097 | 0.0056076 | 7.0028 | 0.07782 | -0.082397 | 0.12817 | 0.19684 | 0.16937 | 0.16937 | -0.07782 | 0.054932 | 13.2523 | -92.0013 | 98.0621 | -19.8441 | 98.0118 | 98.1308 | -19.5923 | 5.9326 | -6.5094 | -0.050354 | 97.8561 | 97.9889 | 98.1033 | 97.8516 | 98.0118 | 111.1862 | 98.1033 | 5.9326 | 97.8516 | 98.0118 | 98.1033 | 98.1033 | 111.1862 | -19.6335 | -111.763
756.7812 | 121.3531 | -120.9869 | 0.091553 | -0.00061033 | 0.011228 | 0.0064942 | 0.0398 | -0.0071093 | -0.0022964 | 0.01558 | 0.12817 | -0.07782 | 0.14191 | 0.27924 | 0.19684 | 0.31128 | -0.10986 | -5.2094 | 0 | -121.1517 | 121.1288 | -0.16937 | 121.1151 | 121.2662 | 0.10529 | -0.16479 | -0.091553 | -0.013733 | 120.8771 | 115.7776 | 121.1838 | 120.9091 | 121.1151 | 120.9869 | 121.2982 | -0.16479 | 120.9091 | 121.1151 | 121.2982 | 121.1838 | 120.9869 | 0.050354 | -121.2433
757.7812 | 120.8084 | -121.1288 | 0.091553 | -0.015869 | 0.011655 | 0.005426 | 0.023565 | -0.0060413 | -0.0040054 | 0.0029758 | 0.13275 | -0.068665 | 0.16479 | 0.2655 | 0.21515 | 0.31586 | -0.11902 | -2.4811 | 0.004578 | -121.2845 | 121.2936 | -0.16022 | 121.2616 | 121.3943 | 0.1236 | -0.15564 | -0.086975 | -0.032044 | 121.0098 | 118.6478 | 121.344 | 121.0602 | 121.2616 | 121.1334 | 121.4447 | -0.15564 | 121.0602 | 121.2616 | 121.4447 | 121.344 | 121.1334 | 0.073242 | -121.376
758.7812 | 121.4767 | -121.2158 | 0.11444 | -0.00061033 | 0.0099463 | 0.0024354 | 0.02207 | -0.0083911 | -0.004219 | 0.0012668 | 0.082397 | -0.041199 | 0.12817 | 0.21515 | 0.17395 | 0.26093 | -0.036621 | -2.6138 | 0.013733 | -121.3852 | 121.344 | -0.15564 | 121.2982 | 121.431 | 0.059509 | -0.16937 | -0.10071 | -0.045777 | 121.1792 | 118.602 | 121.3898 | 121.1746 | 121.2982 | 121.2296 | 121.4767 | -0.16937 | 121.1746 | 121.2982 | 121.4767 | 121.3898 | 121.2296 | 0.013733 | -121.4996
759.7812 | 121.1563 | -121.0739 | 0.091553 | -0.0082398 | 0.011014 | 0.005426 | 0.025915 | -0.0071093 | -0.0037918 | 0.003403 | 0.1236 | -0.07782 | 0.15106 | 0.2655 | 0.19684 | 0.30212 | -0.11444 | 0.10071 | -0.018311 | -121.4218 | 121.225 | -0.16937 | 121.1975 | 121.3394 | 0.10529 | -0.3479 | -0.10986 | -0.027466 | 120.9595 | 121.1746 | 121.2708 | 120.9961 | 121.1975 | 121.0556 | 121.376 | -0.3479 | 120.9961 | 121.1975 | 121.376 | 121.2708 | 121.0556 | 0.059509 | -121.5134
760.7812 | 121.1517 | -120.8954 | 0.07782 | -0.0082398 | 0.012937 | 0.006067 | 0.029333 | -0.0066821 | -0.0044328 | 0.0044712 | 0.13733 | -0.068665 | 0.15564 | 0.27008 | 0.21515 | 0.31586 | -0.11902 | 0.16937 | -0.009155 | -121.4493 | 121.051 | -0.14649 | 121.0327 | 121.1655 | 0.13733 | -0.55389 | -0.086975 | -0.018311 | 120.7764 | 121.0648 | 121.1105 | 120.8267 | 121.0327 | 120.8862 | 121.2112 | -0.55389 | 120.8267 | 121.0327 | 121.2112 | 121.1105 | 120.8862 | 0.07782 | -121.5271
761.7812 | 121.6415 | -121.0007 | 0.23346 | -0.0082398 | 0.010801 | 0.002649 | 0.028478 | -0.0058277 | -0.0044328 | 0.0048984 | 0.11902 | -0.073242 | 0.15106 | 0.25635 | 0.19226 | 0.30212 | -0.09613 | 0.15564 | 0.1236 | -121.3531 | 121.1517 | -0.3067 | 121.1197 | 121.257 | -0.041198 | -0.35248 | -0.10986 | -0.032043 | 120.9045 | 121.1563 | 121.1929 | 120.9274 | 121.1197 | 121.1243 | 121.3028 | -0.35248 | 120.9274 | 121.1197 | 121.3028 | 121.1929 | 121.1243 | -0.082397 | -121.5866
762.7969 | 121.019 | -121.2753 | 0.27466 | -0.015869 | 0.016355 | 0.0058534 | 0.045141 | -0.0071093 | -0.0027238 | 0.015793 | 0.018311 | -0.013733 | 0.10529 | 0.14191 | 0.082397 | 0.15106 | 0.064087 | -0.004578 | 0.1831 | -121.463 | 121.3806 | -0.28839 | 121.2936 | 121.4172 | -0.19226 | -0.18768 | -0.091553 | -0.086975 | 121.3394 | 121.2708 | 121.3577 | 121.2616 | 121.2936 | 121.4584 | 121.4264 | -0.18768 | 121.2616 | 121.2936 | 121.4264 | 121.3577 | 121.4584 | -0.16937 | -121.7377
763.7812 | 121.6644 | -120.845 | 0.25177 | 0.0070192 | 0.014432 | 0.003717 | 0.04215 | -0.0060413 | -0.0050736 | 0.014939 | 0.041199 | -0.036621 | 0.11444 | 0.17853 | 0.11902 | 0.2243 | -0.018311 | 0.064087 | 0.17395 | -121.4172 | 120.9595 | -0.28839 | 120.8862 | 121.0236 | -0.13275 | -0.5722 | -0.07782 | -0.073242 | 120.8267 | 120.9091 | 120.9641 | 120.8084 | 120.8862 | 121.019 | 121.0693 | -0.5722 | 120.8084 | 120.8862 | 121.0693 | 120.9641 | 121.019 | -0.13733 | -121.669
764.7812 | 121.756 | -121.225 | 0.26093 | -0.00061033 | 0.011228 | 0.00051276 | 0.03745 | -0.0047595 | -0.005928 | 0.016007 | 0.13275 | -0.064087 | 0.15564 | 0.27008 | 0.21515 | 0.31128 | -0.11444 | 0.17853 | 0.15106 | -121.3898 | 121.3806 | -0.32501 | 121.3577 | 121.4951 | -0.045776 | -0.16479 | -0.10986 | -0.022889 | 121.1105 | 121.4035 | 121.4401 | 121.1609 | 121.3577 | 121.376 | 121.5363 | -0.16479 | 121.1609 | 121.3577 | 121.5363 | 121.4401 | 121.376 | -0.10529 | -121.6507
765.7812 | 121.2616 | -114.3539 | 6.5277 | -0.015869 | 0.011228 | 0.0045716 | 0.018224 | -0.0004871 | -0.00037376 | 0.0027622 | 0.14648 | -0.082397 | 0.16022 | 0.22888 | 0.19226 | 0.28839 | -0.13275 | 0.12817 | 6.4407 | -114.5782 | 114.5142 | -6.6101 | 114.5004 | 114.5828 | -6.3354 | -0.2243 | -0.086975 | -0.013733 | 114.2212 | 114.4821 | 114.5462 | 114.2715 | 114.5004 | 120.7947 | 114.6423 | -0.2243 | 114.2715 | 114.5004 | 114.6423 | 114.5462 | 120.7947 | -6.3675 | -121.106
766.7812 | 121.4859 | -120.1538 | 0.98419 | -0.0082398 | 0.010801 | 0.0013672 | 0.028692 | -0.0056141 | -0.0012284 | 0.0095982 | 0.13275 | -0.082397 | 0.13733 | 0.23804 | 0.1831 | 0.29755 | -0.10986 | 0.6546 | 0.90179 | -120.4147 | 120.2911 | -1.0666 | 120.2866 | 120.3918 | -0.80109 | -0.26093 | -0.082398 | -0.004578 | 120.0439 | 120.8084 | 120.3369 | 120.0714 | 120.2866 | 121.0556 | 120.4514 | -0.26093 | 120.0714 | 120.2866 | 120.4514 | 120.3369 | 121.0556 | -0.84686 | -121.3989
767.7812 | 121.6049 | -119.902 | 1.3779 | -0.0082398 | 0.012296 | 0.0024354 | 0.040868 | -0.0043323 | -0.003151 | 0.020707 | 0.12817 | -0.07782 | 0.14648 | 0.24261 | 0.17853 | 0.30212 | -0.13733 | 0.40283 | 1.2039 | -120.1767 | 120.0485 | -1.4557 | 120.0302 | 120.1447 | -1.1993 | -0.27466 | -0.17395 | -0.01831 | 119.7647 | 120.3049 | 120.0806 | 119.8242 | 120.0302 | 121.106 | 120.2042 | -0.27466 | 119.8242 | 120.0302 | 120.2042 | 120.0806 | 121.106 | -1.2314 | -121.5546
768.7812 | 121.6232 | -120.5154 | 0.80109 | -0.0082398 | 0.010801 | 0.0041444 | 0.032964 | -0.0066821 | -0.0046464 | 0.010453 | 0.1236 | -0.064087 | 0.15564 | 0.23804 | 0.19226 | 0.28839 | -0.10529 | 0.43945 | 0.71869 | -120.7581 | 120.6711 | -0.86517 | 120.639 | 120.7535 | -0.60882 | -0.24262 | -0.082397 | -0.032044 | 120.4102 | 120.9549 | 120.7077 | 120.4514 | 120.639 | 121.2341 | 120.8038 | -0.24262 | 120.4514 | 120.639 | 120.8038 | 120.7077 | 121.2341 | -0.64545 | -121.5591
769.7812 | 121.6599 | -120.0439 | 1.3184 | -0.00061033 | 0.0155 | 0.002649 | 0.044927 | -0.0064685 | -0.0040054 | 0.019425 | 0.12817 | -0.059509 | 0.15106 | 0.22888 | 0.16937 | 0.29297 | -0.10529 | 0.71869 | 1.1993 | -120.2591 | 120.195 | -1.3779 | 120.1721 | 120.2728 | -1.149 | -0.21515 | -0.11902 | -0.022888 | 119.9387 | 120.7626 | 120.2133 | 119.9844 | 120.1721 | 121.2433 | 120.3369 | -0.21515 | 119.9844 | 120.1721 | 120.3369 | 120.2133 | 121.2433 | -1.1673 | -121.5775
770.7812 | 121.6599 | -120.369 | 1.0117 | -0.00061033 | 0.014005 | 0.0067078 | 0.044286 | -0.0041187 | -0.004219 | 0.018784 | 0.10529 | -0.041199 | 0.14648 | 0.23804 | 0.17853 | 0.27924 | -0.10529 | 0.46692 | 0.91553 | -120.5887 | 120.5154 | -1.0529 | 120.4742 | 120.607 | -0.83313 | -0.21973 | -0.096131 | -0.041198 | 120.2637 | 120.8359 | 120.5475 | 120.3278 | 120.4742 | 121.2845 | 120.6482 | -0.21973 | 120.3278 | 120.4742 | 120.6482 | 120.5475 | 121.2845 | -0.86517 | -121.6003
771.7812 | 121.6919 | -120.1538 | 1.2863 | -0.015869 | 0.013791 | 0.0058534 | 0.094274 | -0.0054003 | -0.0040054 | 0.069413 | 0.091553 | -0.041199 | 0.12817 | 0.21515 | 0.15106 | 0.27466 | -0.086975 | 0.3891 | 1.1627 | -120.3506 | 120.282 | -1.3275 | 120.2454 | 120.369 | -1.1353 | -0.19684 | -0.1236 | -0.036621 | 120.0668 | 120.5429 | 120.3049 | 120.1126 | 120.2454 | 121.3165 | 120.4285 | -0.19684 | 120.1126 | 120.2454 | 120.4285 | 120.3049 | 121.3165 | -1.1581 | -121.637
772.7969 | 121.6141 | -119.4534 | 1.6937 | -0.00061033 | 0.017209 | 0.0028626 | 0.10047 | -0.0041187 | -0.0044328 | 0.064072 | 0.022888 | -0.013733 | 0.11444 | 0.13275 | 0.07782 | 0.1831 | -0.004578 | 0.086975 | 1.7899 | -119.7052 | 119.5679 | -1.7075 | 119.4763 | 119.5862 | -1.6159 | -0.25177 | 0.09613 | -0.091553 | 119.4489 | 119.5404 | 119.5312 | 119.4397 | 119.4763 | 121.2433 | 119.6365 | -0.25177 | 119.4397 | 119.4763 | 119.6365 | 119.5312 | 121.2433 | -1.5793 | -121.3989
773.7812 | 121.0739 | -104.393 | 16.4566 | -0.00061033 | 0.013578 | 0.0052124 | 0.70481 | 0.0039991 | 0.0043258 | 0.70259 | 0.12817 | -0.073242 | 0.15106 | 0.20599 | 0.16937 | 0.2655 | -0.14648 | 3.2364 | 15.8432 | -105.4321 | 104.5441 | -16.5298 | 104.5212 | 104.599 | -16.2872 | -1.0391 | -0.6134 | -0.022888 | 104.2465 | 107.6294 | 104.5624 | 104.3198 | 104.5212 | 120.2362 | 104.6585 | -1.0391 | 104.3198 | 104.5212 | 104.6585 | 104.5624 | 120.2362 | -16.3055 | -121.8887
774.7812 | 121.7285 | -117.778 | 3.5843 | -0.0082398 | 0.011869 | 0.00093996 | 0.034673 | -0.0045459 | -0.0022964 | 0.017929 | 0.1236 | -0.073242 | 0.14648 | 0.23346 | 0.20142 | 0.31128 | -0.11902 | 0.3479 | 3.511 | -118.0527 | 117.9245 | -3.6575 | 117.9016 | 118.0115 | -3.3829 | -0.27466 | -0.073243 | -0.022888 | 117.659 | 118.1259 | 117.9794 | 117.7048 | 117.9016 | 121.2891 | 118.0893 | -0.27466 | 117.7048 | 117.9016 | 118.0893 | 117.9794 | 121.2891 | -3.4378 | -121.637
775.7812 | 121.2296 | -60.7361 | 59.7153 | -0.0082398 | 0.014646 | 0.007135 | 0.0064749 | 0.027711 | 0.028465 | 0.064499 | 0.10986 | -0.068665 | 0.09613 | 0.15106 | 0.10071 | 0.21515 | -0.1831 | 0.082397 | 59.9808 | -60.8871 | 60.8322 | -59.7839 | 60.8459 | 60.8871 | -59.6146 | -0.15106 | 0.2655 | 0.013733 | 60.553 | 60.8185 | 60.8368 | 60.6674 | 60.8459 | 120.7169 | 60.9512 | -0.15106 | 60.6674 | 60.8459 | 60.9512 | 60.8368 | 120.7169 | -59.6191 | -120.6024
776.7812 | 121.3669 | -108.9981 | 12.0941 | -0.0082398 | 0.0099463 | 0.002649 | 0.54694 | -5.99e-05 | 0.0032578 | 0.53874 | 0.082397 | -0.068665 | 0.12817 | 0.19226 | 0.16479 | 0.23804 | 0.009155 | 0.14648 | 11.9659 | -109.1446 | 109.1263 | -12.1628 | 109.0805 | 109.1904 | -11.9293 | -0.14648 | -0.12817 | -0.045777 | 109.0073 | 109.1446 | 109.1629 | 108.9294 | 109.0805 | 120.9641 | 109.2361 | -0.14648 | 108.9294 | 109.0805 | 109.2361 | 109.1629 | 120.9641 | -11.9659 | -121.2387
777.7812 | 121.4951 | -118.1763 | 3.0624 | -0.00061033 | 0.013364 | 0.0047852 | 0.17246 | -0.0024097 | -0.00058736 | 0.15251 | 0.07782 | -0.027466 | 0.14191 | 0.21973 | 0.16022 | 0.27466 | -0.091553 | -0.63629 | 2.9526 | -118.3456 | 118.3182 | -3.0899 | 118.2541 | 118.396 | -2.9022 | -0.16937 | -0.10986 | -0.064087 | 118.0847 | 117.54 | 118.3365 | 118.1488 | 118.2541 | 121.1288 | 118.4509 | -0.16937 | 118.1488 | 118.2541 | 118.4509 | 118.3365 | 121.1288 | -2.9205 | -121.4081
778.7812 | 120.5887 | -109.465 | 10.6888 | -0.00061033 | 0.015073 | 0.0024354 | 0.0077567 | 0.0005811 | 0.00026704 | -0.0019376 | 0.082397 | -0.050354 | 0.11444 | 0.18768 | 0.12817 | 0.25635 | -0.091553 | 0.12817 | 10.6201 | -109.7946 | 109.5795 | -10.7391 | 109.5474 | 109.6527 | -10.5606 | -0.32959 | -0.068665 | -0.032044 | 109.3735 | 109.5932 | 109.5932 | 109.4147 | 109.5474 | 120.0851 | 109.7214 | -0.32959 | 109.4147 | 109.5474 | 109.7214 | 109.5932 | 120.0851 | -10.5743 | -120.4834
779.7812 | 121.4722 | -110.408 | 10.7254 | 0.0070192 | 0.011228 | 0.002008 | 0.010961 | 0.0001539 | 0.00026704 | 0.001694 | 0.13275 | -0.068665 | 0.14648 | 0.21973 | 0.1831 | 0.28381 | -0.13733 | 0.17853 | 10.6476 | -110.5911 | 110.5545 | -10.7941 | 110.5408 | 110.6277 | -10.5423 | -0.18311 | -0.07782 | -0.013733 | 110.2707 | 110.5865 | 110.5911 | 110.3394 | 110.5408 | 121.0556 | 110.6918 | -0.18311 | 110.3394 | 110.5408 | 110.6918 | 110.5911 | 121.0556 | -10.5789 | -121.3165
780.7812 | 121.4905 | -110.614 | 10.6018 | -0.015869 | 0.01016 | 0.0024354 | 0.012029 | -0.0017687 | 0.001976 | 0.0025486 | 0.10986 | -0.059509 | 0.13275 | 0.20599 | 0.16937 | 0.27466 | -0.11444 | 0.15564 | 10.5286 | -110.8017 | 110.7468 | -10.6613 | 110.7239 | 110.82 | -10.4324 | -0.18768 | -0.073243 | -0.022888 | 110.4996 | 110.7697 | 110.7834 | 110.5545 | 110.7239 | 121.1426 | 110.8887 | -0.18768 | 110.5545 | 110.7239 | 110.8887 | 110.7834 | 121.1426 | -10.4691 | -121.4035
781.7812 | 121.5958 | -110.5041 | 10.7666 | -0.0082398 | 0.012723 | 0.0056396 | 0.054967 | -0.0004871 | 0.00026704 | 0.047409 | 0.13275 | -0.059509 | 0.15564 | 0.24261 | 0.19226 | 0.29755 | -0.14648 | 0.18768 | 10.6476 | -110.6827 | 110.6598 | -10.8261 | 110.6369 | 110.7468 | -10.5743 | -0.17853 | -0.11902 | -0.022889 | 110.3577 | 110.6918 | 110.6964 | 110.4446 | 110.6369 | 121.1517 | 110.8017 | -0.17853 | 110.4446 | 110.6369 | 110.8017 | 110.6964 | 121.1517 | -10.611 | -121.4493
782.7812 | 121.5729 | -110.8612 | 10.3134 | -0.015869 | 0.0097327 | 0.0096986 | 0.018011 | -0.0019825 | 0.001976 | 0.01088 | 0.11444 | -0.064087 | 0.13275 | 0.23804 | 0.16937 | 0.27924 | -0.11444 | 0.16937 | 10.2585 | -111.1084 | 110.994 | -10.3775 | 110.9756 | 111.0992 | -10.144 | -0.24719 | -0.054932 | -0.01831 | 110.7468 | 111.0306 | 111.0306 | 110.7971 | 110.9756 | 121.1197 | 111.1404 | -0.24719 | 110.7971 | 110.9756 | 111.1404 | 111.0306 | 121.1197 | -10.1807 | -121.4218
783.7812 | 121.4447 | -111.5112 | 9.8053 | 0.0070192 | 0.0088783 | 0.0047852 | 0.029119 | -0.0043323 | 0.0013352 | 0.018784 | 0.050354 | -0.07782 | 0.14648 | 0.18768 | 0.13275 | 0.26093 | -0.050354 | 0.14648 | 9.7092 | -111.6669 | 111.6577 | -9.8831 | 111.5616 | 111.6989 | -9.6725 | -0.15564 | -0.096131 | -0.09613 | 111.4609 | 111.6577 | 111.644 | 111.4334 | 111.5616 | 121.2204 | 111.7722 | -0.15564 | 111.4334 | 111.5616 | 111.7722 | 111.644 | 121.2204 | -9.6588 | -121.4722
784.7812 | 121.6141 | -112.2253 | 9.0363 | -0.0082398 | 0.012296 | 0.0067078 | 0.033178 | -0.0019825 | 0.001976 | 0.014084 | 0.1236 | -0.07782 | 0.15106 | 0.27008 | 0.19226 | 0.29297 | -0.11902 | 0.20142 | 8.9767 | -112.4542 | 112.3764 | -9.1141 | 112.3489 | 112.4954 | -8.844 | -0.22888 | -0.059509 | -0.027466 | 112.1063 | 112.4268 | 112.4176 | 112.1475 | 112.3489 | 121.2021 | 112.5183 | -0.22888 | 112.1475 | 112.3489 | 112.5183 | 112.4176 | 121.2021 | -8.8852 | -121.4905
785.7812 | 121.6278 | -112.9807 | 8.3817 | -0.00061033 | 0.0097327 | 0.0022218 | 0.016729 | -0.0024097 | 0.00026704 | 0.0048984 | 0.10071 | -0.073242 | 0.14191 | 0.2243 | 0.1831 | 0.27924 | -0.091553 | 0.17395 | 8.2855 | -113.1363 | 113.1226 | -8.4549 | 113.0814 | 113.205 | -8.1985 | -0.15564 | -0.096131 | -0.041199 | 112.8891 | 113.1546 | 113.1638 | 112.9074 | 113.0814 | 121.2662 | 113.2599 | -0.15564 | 112.9074 | 113.0814 | 113.2599 | 113.1638 | 121.2662 | -8.2397 | -121.5179
786.7812 | 121.6507 | -112.9715 | 8.4045 | -0.0082398 | 0.0097327 | -0.00012824 | 0.020147 | -0.0045459 | -0.0012284 | 0.010666 | 0.11902 | -0.073242 | 0.14648 | 0.22888 | 0.17395 | 0.27466 | -0.09613 | 0.16937 | 8.3038 | -113.1454 | 113.118 | -8.4778 | 113.0905 | 113.2004 | -8.2306 | -0.17395 | -0.10071 | -0.027465 | 112.8754 | 113.1409 | 113.1454 | 112.8983 | 113.0905 | 121.2753 | 113.2462 | -0.17395 | 112.8983 | 113.0905 | 113.2462 | 113.1454 | 121.2753 | -8.2581 | -121.55
787.7969 | 121.6919 | -114.2761 | 7.0404 | -0.00061033 | 0.013151 | 0.0067078 | 0.021642 | -0.0039051 | -0.0029374 | 0.0057528 | 0.13733 | -0.073242 | 0.15106 | 0.2655 | 0.19226 | 0.28381 | -0.10986 | 0.19684 | 6.9077 | -114.5645 | 114.4272 | -7.1136 | 114.4135 | 114.5416 | -6.8481 | -0.28839 | -0.13275 | -0.013733 | 114.1663 | 114.473 | 114.4684 | 114.2029 | 114.4135 | 121.1838 | 114.5599 | -0.28839 | 114.2029 | 114.4135 | 114.5599 | 114.4684 | 121.1838 | -6.8893 | -121.6049
788.7812 | 121.669 | -115.1779 | 6.2393 | -0.00061033 | 0.0099463 | 0.00093996 | 0.33118 | -0.0066821 | -0.0025102 | 0.33516 | 0.10986 | -0.073242 | 0.15564 | 0.2243 | 0.15106 | 0.26093 | -0.07782 | 0.16022 | 6.1203 | -115.3336 | 115.3336 | -6.3126 | 115.2878 | 115.4022 | -6.0883 | -0.15564 | -0.11902 | -0.045777 | 115.1001 | 115.3381 | 115.329 | 115.1047 | 115.2878 | 121.2982 | 115.4388 | -0.15564 | 115.1047 | 115.2878 | 115.4388 | 115.329 | 121.2982 | -6.0837 | -121.5729
789.7812 | 121.6644 | -115.7043 | 5.7312 | -0.00061033 | 0.010587 | 0.005426 | 0.023351 | -0.0068957 | -0.0025102 | 0.0083164 | 0.068665 | -0.073242 | 0.12817 | 0.17395 | 0.14648 | 0.23346 | -0.013733 | 0.14191 | 5.658 | -115.8554 | 115.8325 | -5.8044 | 115.773 | 115.8783 | -5.5847 | -0.15106 | -0.073242 | -0.059509 | 115.6906 | 115.8463 | 115.8508 | 115.6311 | 115.773 | 121.3623 | 115.9378 | -0.15106 | 115.6311 | 115.773 | 115.9378 | 115.8508 | 121.3623 | -5.603 | -121.5866
790.7812 | 121.6919 | -116.1072 | 5.3513 | -0.00061033 | 0.0088783 | 8.5364e-05 | 0.068212 | -0.0073229 | -0.0016556 | 0.057236 | 0.064087 | -0.073242 | 0.1236 | 0.21515 | 0.16022 | 0.24261 | -0.027466 | 0.13733 | 5.2963 | -116.2354 | 116.2308 | -5.4245 | 116.1713 | 116.3223 | -5.191 | -0.12817 | -0.054931 | -0.059509 | 116.0797 | 116.2445 | 116.2674 | 116.0339 | 116.1713 | 121.4035 | 116.3498 | -0.12817 | 116.0339 | 116.1713 | 116.3498 | 116.2674 | 121.4035 | -5.2277 | -121.5866
791.7812 | 121.701 | -114.4913 | 6.9214 | -0.00061033 | 0.0093055 | 0.0032898 | 0.018224 | -0.0054003 | 0.00048064 | 0.0042576 | 0.10071 | -0.068665 | 0.12817 | 0.2243 | 0.16937 | 0.25635 | -0.064087 | 0.15564 | 6.8161 | -114.7018 | 114.6194 | -6.9901 | 114.592 | 114.7156 | -6.752 | -0.21057 | -0.10529 | -0.027466 | 114.4272 | 114.6469 | 114.6606 | 114.4226 | 114.592 | 121.3074 | 114.7476 | -0.21057 | 114.4226 | 114.592 | 114.7476 | 114.6606 | 121.3074 | -6.7932 | -121.6232
792.7812 | 121.7056 | -114.7202 | 6.7017 | 0.0070192 | 0.0090919 | 0.0041444 | 0.028265 | -0.0056141 | -0.00058736 | 0.013016 | 0.09613 | -0.091553 | 0.15564 | 0.22888 | 0.16479 | 0.27008 | -0.068665 | 0.16937 | 6.6193 | -114.9216 | 114.8758 | -6.7932 | 114.8163 | 114.949 | -6.5369 | -0.20142 | -0.082397 | -0.05951 | 114.6515 | 114.8895 | 114.8849 | 114.6286 | 114.8163 | 121.3394 | 114.9902 | -0.20142 | 114.6286 | 114.8163 | 114.9902 | 114.8849 | 121.3394 | -6.546 | -121.6232
793.7812 | 121.6141 | -115.9058 | 5.6259 | -0.0082398 | 0.0095191 | 0.0049988 | 0.036809 | -0.0060413 | -0.0037918 | 0.01323 | 0.050354 | -0.050354 | 0.13275 | 0.20142 | 0.15564 | 0.23804 | -0.032043 | 0.16479 | 5.5389 | -116.0248 | 116.0385 | -5.6763 | 115.9561 | 116.1072 | -5.4703 | -0.11902 | -0.086976 | -0.082397 | 115.8737 | 116.0706 | 116.0614 | 115.8554 | 115.9561 | 121.4447 | 116.1438 | -0.11902 | 115.8554 | 115.9561 | 116.1438 | 116.0614 | 121.4447 | -5.4932 | -121.6507
794.7812 | 121.756 | -115.6403 | 5.9143 | -0.0082398 | 0.0075965 | 0.002008 | 0.02741 | -0.0051867 | -0.0033646 | 0.012802 | 0.064087 | -0.045776 | 0.14191 | 0.18768 | 0.13733 | 0.25177 | -0.022888 | 0.13275 | 5.7449 | -115.7684 | 115.7822 | -5.9601 | 115.7043 | 115.8279 | -5.777 | -0.12817 | -0.16937 | -0.07782 | 115.6174 | 115.773 | 115.7776 | 115.5945 | 115.7043 | 121.3852 | 115.892 | -0.12817 | 115.5945 | 115.7043 | 115.892 | 115.7776 | 121.3852 | -5.7724 | -121.6827
795.7812 | 121.756 | -82.0084 | 39.386 | -0.0082398 | 0.0086645 | -0.00098264 | 0.051549 | 0.010408 | 0.015221 | 0.079239 | 0.018311 | -0.068665 | 0.10071 | 0.15106 | 0.10071 | 0.19684 | -0.073242 | 0.032043 | 39.3036 | -82.2144 | 82.1091 | -39.4547 | 82.0267 | 82.1594 | -39.2853 | -0.20599 | -0.082397 | -0.082397 | 81.9351 | 82.0404 | 82.1091 | 81.9397 | 82.0267 | 121.312 | 82.2052 | -0.20599 | 81.9397 | 82.0267 | 82.2052 | 82.1091 | 121.312 | -39.2853 | -121.6003
796.7812 | 121.7789 | -113.1683 | 8.226 | -0.00061033 | 0.011014 | 0.0024354 | 0.036596 | -0.0054003 | -0.001442 | 0.023697 | 0.068665 | -0.068665 | 0.14191 | 0.19226 | 0.14648 | 0.24719 | -0.032043 | 0.13733 | 8.0429 | -113.4384 | 113.3102 | -8.2947 | 113.237 | 113.3606 | -8.0795 | -0.27008 | -0.1831 | -0.073242 | 113.1363 | 113.3057 | 113.3148 | 113.0997 | 113.237 | 121.2112 | 113.4155 | -0.27008 | 113.0997 | 113.237 | 113.4155 | 113.3148 | 121.2112 | -8.0841 | -121.6644
797.7969 | 121.7697 | -113.031 | 8.5007 | -0.0082398 | 0.014646 | 0.00072636 | 0.041296 | -0.0051867 | 0.0024032 | 0.029251 | 0.086975 | -0.050354 | 0.13275 | 0.18768 | 0.13733 | 0.23804 | -0.036621 | 0.1236 | 8.2123 | -113.2828 | 113.1638 | -8.551 | 113.118 | 113.2187 | -8.3633 | -0.25177 | -0.28839 | -0.045776 | 112.9944 | 113.1546 | 113.1683 | 112.9807 | 113.118 | 121.2433 | 113.269 | -0.25177 | 112.9807 | 113.118 | 113.269 | 113.1683 | 121.2433 | -8.3679 | -121.7834
798.7812 | 121.7377 | -115.5396 | 5.9692 | -0.0082398 | 0.011228 | 0.0079896 | 0.03446 | -0.0066821 | -0.0018692 | 0.01857 | 0.064087 | -0.068665 | 0.12817 | 0.19684 | 0.14191 | 0.24719 | -0.050354 | 0.15106 | 5.928 | -115.7089 | 115.6677 | -6.0379 | 115.6036 | 115.7364 | -5.8273 | -0.16937 | -0.041198 | -0.064087 | 115.4892 | 115.6906 | 115.6815 | 115.4709 | 115.6036 | 121.4676 | 115.7867 | -0.16937 | 115.4709 | 115.6036 | 115.7867 | 115.6815 | 121.4676 | -5.8411 | -121.6782
799.7812 | 121.7697 | -115.6815 | 5.7724 | -0.00061033 | 0.0099463 | 0.0062806 | 0.032751 | -0.0068957 | 0.00026704 | 0.013443 | 0.068665 | -0.068665 | 0.14191 | 0.21515 | 0.15564 | 0.24719 | -0.045776 | 0.13733 | 6.1386 | -115.7822 | 115.8234 | -5.8411 | 115.7501 | 115.8966 | -5.6168 | -0.10071 | 0.36621 | -0.073242 | 115.6357 | 115.8188 | 115.8371 | 115.6128 | 115.7501 | 121.8201 | 115.9287 | -0.10071 | 115.6128 | 115.7501 | 115.9287 | 115.8371 | 121.8201 | -5.6305 | -121.5546
800.7812 | 121.5637 | -101.2436 | 20.4941 | -0.00061033 | 0.012296 | -0.00055544 | 0.046423 | 0.0016491 | 0.006462 | 0.044632 | 0.059509 | -0.073242 | 0.11902 | 0.16479 | 0.1236 | 0.20599 | -0.045776 | 0.068665 | 19.2032 | -102.2186 | 101.3626 | -20.5673 | 101.3031 | 101.4084 | -20.3705 | -0.97504 | -1.2909 | -0.05951 | 101.1978 | 101.3123 | 101.3672 | 101.1703 | 101.3031 | 120.4468 | 101.4496 | -0.97504 | 101.1703 | 101.3031 | 101.4496 | 101.3672 | 120.4468 | -20.3751 | -122.7127
801.7812 | 121.8155 | -114.2899 | 7.1823 | -0.0082398 | 0.0095191 | 0.0022218 | 0.031469 | -0.0064685 | 0.00048064 | 0.019638 | 0.07782 | -0.054932 | 0.12817 | 0.21515 | 0.15564 | 0.25177 | -0.036621 | 0.15106 | 7.1045 | -114.5142 | 114.418 | -7.2372 | 114.3677 | 114.505 | -7.0267 | -0.2243 | -0.07782 | -0.050354 | 114.2532 | 114.4409 | 114.4455 | 114.2349 | 114.3677 | 121.3943 | 114.5416 | -0.2243 | 114.2349 | 114.3677 | 114.5416 | 114.4455 | 121.3943 | -7.0541 | -121.6965
802.7812 | 121.756 | -118.5974 | 2.9709 | 0.0070192 | 0.0086645 | 0.0045716 | 0.03745 | -0.0090319 | -0.0029374 | 0.019425 | 0.064087 | -0.064087 | 0.13275 | 0.20142 | 0.14648 | 0.25177 | -0.041199 | 0.14648 | 2.8793 | -118.7668 | 118.7302 | -3.035 | 118.6615 | 118.7988 | -2.8244 | -0.16937 | -0.091553 | -0.068664 | 118.5562 | 118.7439 | 118.7439 | 118.5333 | 118.6615 | 121.4767 | 118.8492 | -0.16937 | 118.5333 | 118.6615 | 118.8492 | 118.7439 | 121.4767 | -2.8381 | -121.7377
803.7812 | 121.8063 | -119.5358 | 2.0508 | -0.0082398 | 0.010587 | 0.0013672 | 0.03446 | -0.010314 | -0.0037918 | 0.017716 | 0.045776 | -0.059509 | 0.11444 | 0.21515 | 0.16937 | 0.25635 | -0.022888 | 0.15106 | 1.9913 | -119.6777 | 119.6503 | -2.1103 | 119.5816 | 119.751 | -1.8814 | -0.14191 | -0.059509 | -0.068665 | 119.5129 | 119.6869 | 119.7052 | 119.4763 | 119.5816 | 121.5271 | 119.7922 | -0.14191 | 119.4763 | 119.5816 | 119.7922 | 119.7052 | 121.5271 | -1.9363 | -121.7285
804.7812 | 121.7651 | -117.7826 | 3.7308 | 0.0070192 | 0.012082 | 0.0035034 | 0.035528 | -0.0079639 | -0.0020828 | 0.017502 | 0.068665 | -0.068665 | 0.12817 | 0.21515 | 0.16479 | 0.2655 | -0.041199 | 0.15564 | 3.6346 | -117.9886 | 117.9108 | -3.7994 | 117.8513 | 117.9977 | -3.566 | -0.20599 | -0.09613 | -0.059509 | 117.7414 | 117.9382 | 117.9474 | 117.7139 | 117.8513 | 121.4172 | 118.0481 | -0.20599 | 117.7139 | 117.8513 | 118.0481 | 117.9474 | 121.4172 | -3.6026 | -121.7194
805.7812 | 121.7972 | -118.7073 | 2.8015 | -0.0082398 | 0.0095191 | 0.0032898 | 0.03745 | -0.010527 | -0.0029374 | 0.02092 | 0.073242 | -0.068665 | 0.13275 | 0.21973 | 0.16022 | 0.25177 | -0.050354 | 0.15564 | 2.8107 | -118.9453 | 118.84 | -2.8702 | 118.7805 | 118.927 | -2.6413 | -0.23804 | 0.009155 | -0.059509 | 118.6569 | 118.8629 | 118.8675 | 118.6386 | 118.7805 | 121.5179 | 118.959 | -0.23804 | 118.6386 | 118.7805 | 118.959 | 118.8675 | 121.5179 | -2.6688 | -121.7468
806.7812 | 121.8063 | -119.2017 | 2.3254 | 0.0070192 | 0.0090919 | 0.0022218 | 0.038518 | -0.0086047 | -0.0046464 | 0.017075 | 0.082397 | -0.082397 | 0.1236 | 0.22888 | 0.17395 | 0.27008 | -0.050354 | 0.17853 | 2.2156 | -119.4351 | 119.3253 | -2.4078 | 119.2841 | 119.4305 | -2.1515 | -0.23346 | -0.10986 | -0.041199 | 119.1513 | 119.3802 | 119.3756 | 119.1193 | 119.2841 | 121.4172 | 119.4717 | -0.23346 | 119.1193 | 119.2841 | 119.4717 | 119.3756 | 121.4172 | -2.2018 | -121.7606
807.7969 | 121.7926 | -119.5404 | 2.0782 | 0.0070192 | 0.011014 | 0.0013672 | 0.042364 | -0.0077503 | -0.0020828 | 0.021561 | 0.073242 | -0.041199 | 0.13275 | 0.20599 | 0.16022 | 0.25177 | -0.022888 | 0.14648 | 2.0508 | -119.7327 | 119.6732 | -2.1194 | 119.6136 | 119.7464 | -1.918 | -0.19226 | -0.027466 | -0.059509 | 119.5175 | 119.6869 | 119.7006 | 119.4992 | 119.6136 | 121.5912 | 119.7922 | -0.19226 | 119.4992 | 119.6136 | 119.7922 | 119.7006 | 121.5912 | -1.9455 | -121.8109
808.7812 | 121.8475 | -120.4468 | 1.2085 | -0.00061033 | 0.0099463 | 0.0011536 | 0.044714 | -0.0086047 | -0.0044328 | 0.030106 | 0.041199 | -0.050354 | 0.14191 | 0.20599 | 0.15106 | 0.25635 | -0.004578 | 0.15106 | 1.1032 | -120.5978 | 120.5887 | -1.2589 | 120.488 | 120.6528 | -1.0574 | -0.15106 | -0.10529 | -0.10071 | 120.4422 | 120.5978 | 120.5978 | 120.3964 | 120.488 | 121.55 | 120.7031 | -0.15106 | 120.3964 | 120.488 | 120.7031 | 120.5978 | 121.55 | -1.0666 | -121.8063
809.7969 | 121.7239 | -121.019 | 0.69122 | -0.0082398 | 0.01251 | 0.002008 | 0.043432 | -0.010954 | -0.0040054 | 0.01857 | 0.013733 | -0.032043 | 0.11444 | 0.17395 | 0.10071 | 0.17853 | 0.11902 | 0.10529 | 0.60883 | -121.1792 | 121.1334 | -0.72327 | 121.0327 | 121.1929 | -0.59052 | -0.16022 | -0.082397 | -0.10071 | 121.138 | 121.1243 | 121.1197 | 120.9869 | 121.0327 | 121.6278 | 121.1975 | -0.16022 | 120.9869 | 121.0327 | 121.1975 | 121.1197 | 121.6278 | -0.57678 | -121.8704
810.7812 | 121.843 | -120.9549 | 0.70038 | 0.0070192 | 0.011014 | 8.5364e-05 | 0.042364 | -0.0096729 | -0.004219 | 0.019638 | 0.086975 | -0.059509 | 0.13733 | 0.24719 | 0.16937 | 0.27924 | -0.041199 | 0.17395 | 0.60425 | -121.1243 | 121.0922 | -0.75989 | 121.0419 | 121.2021 | -0.531 | -0.16937 | -0.09613 | -0.050354 | 120.9137 | 121.1288 | 121.1243 | 120.8954 | 121.0419 | 121.5591 | 121.2341 | -0.16937 | 120.8954 | 121.0419 | 121.2341 | 121.1243 | 121.5591 | -0.56305 | -121.8246
811.7812 | 121.8384 | -120.9686 | 0.70496 | -0.00061033 | 0.011014 | 0.0058534 | 0.043432 | -0.011168 | -0.00486 | 0.021988 | 0.073242 | -0.064087 | 0.12817 | 0.21973 | 0.16479 | 0.26093 | -0.018311 | 0.15564 | 0.60883 | -121.1014 | 121.0968 | -0.76904 | 121.0419 | 121.1884 | -0.54016 | -0.13275 | -0.09613 | -0.054932 | 120.9503 | 121.1243 | 121.1334 | 120.9045 | 121.0419 | 121.5775 | 121.2296 | -0.13275 | 120.9045 | 121.0419 | 121.2296 | 121.1334 | 121.5775 | -0.57678 | -121.8063
812.7812 | 121.8475 | -119.7968 | 1.7761 | -0.00061033 | 0.01016 | -0.00012824 | 0.049413 | -0.0083911 | -0.0052872 | 0.024765 | 0.11902 | -0.068665 | 0.15106 | 0.2655 | 0.18768 | 0.31586 | -0.082397 | 0.21057 | 1.7166 | -119.9982 | 119.9478 | -1.8448 | 119.9158 | 120.0623 | -1.5884 | -0.20142 | -0.059509 | -0.032043 | 119.7144 | 120.0073 | 119.9844 | 119.7281 | 119.9158 | 121.5134 | 120.1126 | -0.20142 | 119.7281 | 119.9158 | 120.1126 | 119.9844 | 121.5134 | -1.6251 | -121.7743
813.7812 | 121.8292 | -119.989 | 1.6296 | -0.0082398 | 0.0086645 | 0.0015808 | 0.11735 | -0.0090319 | -0.004219 | 0.095902 | 0.082397 | -0.059509 | 0.15106 | 0.22888 | 0.1831 | 0.27466 | -0.050354 | 0.15564 | 1.5106 | -120.1721 | 120.1401 | -1.6891 | 120.0714 | 120.2179 | -1.4465 | -0.1831 | -0.11902 | -0.068665 | 119.9387 | 120.1447 | 120.1721 | 119.9295 | 120.0714 | 121.4996 | 120.2637 | -0.1831 | 119.9295 | 120.0714 | 120.2637 | 120.1721 | 121.4996 | -1.4786 | -121.8018
814.7812 | 121.8842 | -120.9274 | 0.7782 | 0.0070192 | 0.010373 | 0.002008 | 0.056036 | -0.0094593 | -0.0055008 | 0.030533 | 0.11444 | -0.073242 | 0.14648 | 0.27924 | 0.21515 | 0.30212 | -0.004578 | 0.22888 | 0.70953 | -121.0419 | 121.0739 | -0.85144 | 121.0419 | 121.2067 | -0.56305 | -0.11444 | -0.068664 | -0.032043 | 120.9229 | 121.1563 | 121.1426 | 120.8542 | 121.0419 | 121.637 | 121.2296 | -0.11444 | 120.8542 | 121.0419 | 121.2296 | 121.1426 | 121.637 | -0.63171 | -121.8201
815.7969 | 121.8613 | -120.1767 | 1.5564 | -0.0082398 | 0.01251 | 8.5364e-05 | 0.098119 | -0.0101 | -0.0044328 | 0.082657 | 0.082397 | -0.050354 | 0.13733 | 0.20599 | 0.15106 | 0.21515 | 0.10071 | 0.15106 | 1.4511 | -120.3415 | 120.314 | -1.6067 | 120.2591 | 120.3827 | -1.4053 | -0.16479 | -0.10528 | -0.054932 | 120.2774 | 120.3278 | 120.3278 | 120.1263 | 120.2591 | 121.6278 | 120.3918 | -0.16479 | 120.1263 | 120.2591 | 120.3918 | 120.3278 | 121.6278 | -1.4191 | -121.8979
816.7812 | 121.8521 | -119.4946 | 2.1378 | -0.00061033 | 0.01016 | 0.002008 | 0.15323 | -0.0064685 | -0.0046464 | 0.12688 | 0.11902 | -0.064087 | 0.16022 | 0.2655 | 0.20142 | 0.3067 | -0.091553 | 0.073242 | 1.9318 | -119.6869 | 119.6548 | -2.2018 | 119.6136 | 119.7601 | -1.9363 | -0.19226 | -0.20599 | -0.041198 | 119.4031 | 119.5679 | 119.696 | 119.4305 | 119.6136 | 121.4264 | 119.8013 | -0.19226 | 119.4305 | 119.6136 | 119.8013 | 119.696 | 121.4264 | -1.9775 | -121.8246
817.7812 | 121.875 | -117.8009 | 3.7857 | -0.00061033 | 0.010801 | 0.002649 | 0.22843 | -0.0083911 | -0.0037918 | 0.23219 | 0.07782 | -0.07782 | 0.10986 | 0.21057 | 0.16022 | 0.25177 | -0.032043 | 0.2243 | 3.4149 | -118.0618 | 117.9108 | -3.8635 | 117.8787 | 118.0115 | -3.6255 | -0.26093 | -0.37079 | -0.032043 | 117.7689 | 118.0252 | 117.9611 | 117.7231 | 117.8787 | 121.2158 | 118.0527 | -0.26093 | 117.7231 | 117.8787 | 118.0527 | 117.9611 | 121.2158 | -3.6758 | -121.8475
818.7812 | 121.8842 | -120.1996 | 1.4008 | -0.015869 | 0.011228 | 0.00029916 | 0.09876 | -0.0094593 | -0.0046464 | 0.074753 | 0.09613 | -0.07782 | 0.14648 | 0.23804 | 0.1831 | 0.27924 | -0.032043 | 0.16479 | 1.149 | -120.4193 | 120.3461 | -1.4786 | 120.2957 | 120.4376 | -1.2177 | -0.21973 | -0.25177 | -0.050354 | 120.1675 | 120.3644 | 120.3827 | 120.1218 | 120.2957 | 121.3486 | 120.4788 | -0.21973 | 120.1218 | 120.2957 | 120.4788 | 120.3827 | 121.3486 | -1.2543 | -121.8201
819.7812 | 121.9345 | -121.0327 | 0.6134 | -0.00061033 | 0.010801 | 0.0030762 | 0.056036 | -0.0090319 | -0.0046464 | 0.034165 | 0.1236 | -0.07782 | 0.15106 | 0.2655 | 0.2243 | 0.31586 | -0.09613 | 0.19226 | 0.5127 | -121.1929 | 121.1838 | -0.69122 | 121.1563 | 121.2982 | -0.3891 | -0.16022 | -0.10071 | -0.027466 | 120.9366 | 121.225 | 121.257 | 120.9549 | 121.1563 | 121.5454 | 121.3486 | -0.16022 | 120.9549 | 121.1563 | 121.3486 | 121.257 | 121.5454 | -0.46234 | -121.8063
820.7969 | 121.788 | -121.0968 | 0.66376 | -0.00061033 | 0.016996 | 0.003717 | 0.080389 | -0.0083911 | -0.005928 | 0.054673 | 0.022888 | -0.018311 | 0.10986 | 0.16479 | 0.10986 | 0.1831 | 0.11902 | 0.10071 | 0.58594 | -121.2891 | 121.2067 | -0.68207 | 121.1197 | 121.2616 | -0.55389 | -0.19226 | -0.07782 | -0.086975 | 121.2158 | 121.1975 | 121.2067 | 121.0785 | 121.1197 | 121.6827 | 121.2799 | -0.19226 | 121.0785 | 121.1197 | 121.2799 | 121.2067 | 121.6827 | -0.55389 | -121.9528
821.7812 | 121.8521 | -120.5933 | 0.95673 | -0.00061033 | 0.014432 | 0.0028626 | 0.055181 | -0.0083911 | -0.0052872 | 0.03096 | 0.11444 | -0.073242 | 0.12817 | 0.25635 | 0.21515 | 0.29755 | -0.082397 | 0.20599 | 0.89722 | -120.8542 | 120.7214 | -1.03 | 120.7077 | 120.8496 | -0.74158 | -0.26093 | -0.059509 | -0.013733 | 120.5109 | 120.7993 | 120.8084 | 120.52 | 120.7077 | 121.4905 | 120.8908 | -0.26093 | 120.52 | 120.7077 | 120.8908 | 120.8084 | 121.4905 | -0.82855 | -121.8109
822.7812 | 120.8725 | -40.4984 | 80.4428 | -0.00061033 | 0.011014 | 0.0013672 | 0.13444 | 0.032197 | 0.04171 | 0.19609 | 0.036621 | -0.10986 | 0.10986 | 0.032043 | 0.013733 | 0.11444 | -0.16479 | 0.091553 | 81.4178 | -38.8962 | 40.6082 | -80.5527 | 40.535 | 40.5304 | -80.4291 | 1.6022 | 0.97504 | -0.073242 | 40.3336 | 40.5899 | 40.5121 | 40.3885 | 40.535 | 121.9162 | 40.6128 | 1.6022 | 40.3885 | 40.535 | 40.6128 | 40.5121 | 121.9162 | -80.3329 | -119.339
823.7812 | 121.4676 | -49.6811 | 70.8984 | -0.00061033 | 0.010587 | 0.002649 | 0.01502 | 0.030275 | 0.036797 | 0.090561 | 0.050354 | -0.11444 | 0.086975 | 0.09613 | 0.050354 | 0.14648 | -0.16022 | 0.041199 | 71.0953 | -49.9466 | 49.7681 | -71.0129 | 49.7314 | 49.7772 | -70.8481 | -0.2655 | 0.19684 | -0.036621 | 49.5209 | 49.7223 | 49.7314 | 49.5667 | 49.7314 | 120.7764 | 49.8276 | -0.2655 | 49.5667 | 49.7314 | 49.8276 | 49.7314 | 120.7764 | -70.8115 | -120.845
824.7812 | 121.5866 | -116.9952 | 4.3396 | -0.00061033 | 0.012296 | 0.0011536 | 0.032751 | -0.0066821 | -0.0025102 | 0.020493 | 0.13733 | -0.064087 | 0.13275 | 0.27924 | 0.20599 | 0.32959 | -0.073242 | 0.22888 | 4.541 | -117.1829 | 117.128 | -4.4037 | 117.1326 | 117.2745 | -4.1336 | -0.18768 | 0.20142 | 0.004578 | 116.922 | 117.2241 | 117.2012 | 116.9312 | 117.1326 | 121.5363 | 117.3248 | -0.18768 | 116.9312 | 117.1326 | 117.3248 | 117.2012 | 121.5363 | -4.2068 | -121.5225
825.7969 | 121.5408 | -119.9753 | 1.4465 | -0.00061033 | 0.0155 | 0.0045716 | 0.04215 | -0.0081775 | -0.0037918 | 0.018357 | 0.004578 | -0.004578 | 0.11444 | 0.16937 | 0.11902 | 0.20599 | 0.16937 | 0.11444 | 1.387 | -120.1859 | 120.0897 | -1.4511 | 119.9799 | 120.1447 | -1.3275 | -0.21057 | -0.059509 | -0.10986 | 120.1447 | 120.0897 | 120.0943 | 119.9707 | 119.9799 | 121.3623 | 120.1813 | -0.21057 | 119.9707 | 119.9799 | 120.1813 | 120.0943 | 121.3623 | -1.3321 | -121.6324
826.7812 | 121.6599 | -119.5358 | 1.6754 | -0.015869 | 0.011869 | 0.007776 | 0.038305 | -0.0047595 | -0.0027238 | 0.01323 | 0.12817 | -0.054932 | 0.13733 | 0.27924 | 0.23346 | 0.32959 | -0.082397 | 0.2243 | 1.268 | -119.9112 | 119.6732 | -1.7303 | 119.664 | 119.8151 | -1.442 | -0.37537 | -0.40741 | -0.009155 | 119.4534 | 119.7601 | 119.7693 | 119.4809 | 119.664 | 120.8038 | 119.8654 | -0.37537 | 119.4809 | 119.664 | 119.8654 | 119.7693 | 120.8038 | -1.5381 | -121.5866
827.7969 | 112.9761 | -53.4256 | 59.2896 | -0.0082398 | 0.0097327 | 0.0030762 | 0.087011 | 0.027498 | 0.031456 | 0.14119 | 0.050354 | -0.09613 | 0.10529 | 0.12817 | 0.054932 | 0.16937 | -0.14648 | -0.013733 | 65.3275 | -55.2383 | 53.5309 | -59.3857 | 53.476 | 53.5538 | -59.2346 | -1.8127 | 6.0379 | -0.054932 | 53.2791 | 53.4119 | 53.4805 | 53.3295 | 53.476 | 118.7531 | 53.595 | -1.8127 | 53.3295 | 53.476 | 53.595 | 53.4805 | 118.7531 | -59.1843 | -114.5279
828.7812 | 121.6278 | -102.0355 | 18.837 | -0.00061033 | 0.0099463 | 0.002008 | 0.297 | 0.0037855 | 0.0066756 | 0.36421 | 0.036621 | -0.073242 | 0.11444 | 0.16022 | 0.1236 | 0.23804 | -0.036621 | 0.11902 | 25.7309 | -99.7284 | 102.15 | -18.9102 | 102.0721 | 102.1957 | -18.7134 | 2.3071 | 6.8939 | -0.07782 | 101.9989 | 102.1545 | 102.1591 | 101.9623 | 102.0721 | 127.7664 | 102.2736 | 2.3071 | 101.9623 | 102.0721 | 102.2736 | 102.1591 | 127.7664 | -18.7225 | -118.5654
829.7812 | 121.8521 | -112.8113 | 8.5556 | -0.00061033 | 0.0090919 | 0.0035034 | 0.099187 | -0.0043323 | 0.00048064 | 0.10146 | 0.054932 | -0.059509 | 0.12817 | 0.20599 | 0.17853 | 0.27466 | 0.004578 | 0.14191 | 8.4137 | -112.706 | 112.9395 | -8.6151 | 112.8662 | 113.0173 | -8.3771 | 0.10528 | -0.14191 | -0.073242 | 112.8159 | 112.9532 | 112.9898 | 112.7518 | 112.8662 | 121.225 | 113.0859 | 0.10528 | 112.7518 | 112.8662 | 113.0859 | 112.9898 | 121.225 | -8.4274 | -121.2616
830.7969 | 121.6095 | -106.1691 | 15.0146 | -0.00061033 | 0.014219 | 0.0024354 | 0.37049 | -0.0015551 | 0.003685 | 0.37148 | 0.041199 | -0.032043 | 0.09613 | 0.17853 | 0.1236 | 0.20142 | 0.10071 | 0.086975 | 15.3625 | -106.3751 | 106.2653 | -15.0467 | 106.2103 | 106.3477 | -14.8911 | -0.20599 | 0.3479 | -0.054931 | 106.2698 | 106.2561 | 106.2927 | 106.1371 | 106.2103 | 121.5317 | 106.3705 | -0.20599 | 106.1371 | 106.2103 | 106.3705 | 106.2927 | 121.5317 | -14.9185 | -121.3898
831.7812 | 121.5363 | -118.6295 | 2.3438 | 0.0070192 | 0.0073829 | 0.0011536 | 0.057317 | -0.0073229 | -0.0069962 | 0.027329 | 0.054932 | -0.045776 | 0.14648 | 0.23804 | 0.19226 | 0.28381 | 0.027466 | 0.17853 | 1.7029 | -119.8196 | 118.7759 | -2.3895 | 118.6844 | 118.8675 | -2.1515 | -1.1902 | -0.64087 | -0.091552 | 118.6569 | 118.808 | 118.8217 | 118.5837 | 118.6844 | 120.3323 | 118.9133 | -1.1902 | 118.5837 | 118.6844 | 118.9133 | 118.8217 | 120.3323 | -2.1973 | -122.1634
832.7812 | 121.756 | -82.7042 | 38.4613 | -0.00061033 | 0.010801 | 0.005426 | 0.7266 | 0.011903 | 0.015221 | 0.76433 | 0.09613 | -0.09613 | 0.13733 | 0.21973 | 0.15106 | 0.25635 | -0.13733 | -0.013733 | 38.5254 | -82.7408 | 82.8415 | -38.5574 | 82.8003 | 82.9239 | -38.3102 | -0.036621 | 0.064087 | -0.041199 | 82.5668 | 82.6904 | 82.8552 | 82.608 | 82.8003 | 121.2296 | 82.9605 | -0.036621 | 82.608 | 82.8003 | 82.9605 | 82.8552 | 121.2296 | -38.324 | -121.2021
833.7812 | 121.344 | -120.5704 | 0.54932 | -0.0082398 | 0.0088783 | 0.0039306 | 0.029333 | -0.0043323 | -0.0035782 | 0.010666 | 0.082397 | -0.068665 | 0.13275 | 0.25177 | 0.20599 | 0.31128 | 0.004578 | 0.19684 | 0.48981 | -120.7581 | 120.7031 | -0.61798 | 120.6528 | 120.8221 | -0.34332 | -0.18768 | -0.059509 | -0.050354 | 120.575 | 120.7672 | 120.7764 | 120.5017 | 120.6528 | 121.0602 | 120.8817 | -0.18768 | 120.5017 | 120.6528 | 120.8817 | 120.7764 | 121.0602 | -0.41657 | -121.3074
834.7812 | 121.4905 | -120.6894 | 0.63171 | -0.0082398 | 0.011442 | 0.0015808 | 0.030614 | -0.0073229 | -0.0016556 | 0.013871 | 0.054932 | -0.045776 | 0.13733 | 0.22888 | 0.18768 | 0.29755 | 0.036621 | 0.20142 | 0.52643 | -120.813 | 120.8267 | -0.67749 | 120.7443 | 120.9183 | -0.44403 | -0.1236 | -0.10529 | -0.082397 | 120.726 | 120.8908 | 120.8771 | 120.6436 | 120.7443 | 121.2158 | 120.9869 | -0.1236 | 120.6436 | 120.7443 | 120.9869 | 120.8771 | 121.2158 | -0.49438 | -121.4447
835.7812 | 121.5912 | -120.7306 | 0.64087 | -0.0082398 | 0.0099463 | -0.0011962 | 0.031469 | -0.0098865 | -0.0037918 | 0.012162 | 0.073242 | -0.054932 | 0.12817 | 0.27008 | 0.22888 | 0.33417 | -0.004578 | 0.24719 | 0.55847 | -120.8817 | 120.8588 | -0.6958 | 120.8038 | 121.0007 | -0.41199 | -0.15106 | -0.082397 | -0.054932 | 120.726 | 120.9778 | 120.9595 | 120.6757 | 120.8038 | 121.2891 | 121.0648 | -0.15106 | 120.6757 | 120.8038 | 121.0648 | 120.9595 | 121.2891 | -0.5127 | -121.5225
836.7812 | 121.5866 | -120.5887 | 0.79193 | -0.0082398 | 0.01016 | 0.00072636 | 0.03446 | -0.012023 | -0.0055008 | 0.013657 | 0.054932 | -0.054932 | 0.11444 | 0.22888 | 0.20142 | 0.27466 | 0.041199 | 0.19684 | 0.71869 | -120.7672 | 120.7031 | -0.84686 | 120.6436 | 120.8176 | -0.59052 | -0.17853 | -0.073242 | -0.059509 | 120.6299 | 120.7855 | 120.7901 | 120.5338 | 120.6436 | 121.3074 | 120.8633 | -0.17853 | 120.5338 | 120.6436 | 120.8633 | 120.7901 | 121.3074 | -0.67749 | -121.5591
837.7812 | 121.2158 | -114.4363 | 7.0358 | -0.0082398 | 0.0093055 | -0.00012824 | 0.26774 | -0.0068957 | -0.0012284 | 0.26573 | 0.082397 | -0.054932 | 0.14191 | 0.2655 | 0.21973 | 0.31128 | -0.027466 | 0.19226 | 7.4936 | -114.5645 | 114.5782 | -7.0908 | 114.5187 | 114.7018 | -6.8161 | -0.12817 | 0.45776 | -0.05951 | 114.4089 | 114.6286 | 114.6561 | 114.3814 | 114.5187 | 121.9299 | 114.7476 | -0.12817 | 114.3814 | 114.5187 | 114.7476 | 114.6561 | 121.9299 | -6.8939 | -121.6003
838.7812 | 121.6278 | -120.7031 | 0.78278 | -0.00061033 | 0.0095191 | 0.0035034 | 0.038518 | -0.012663 | -0.0052872 | 0.017502 | 0.041199 | -0.064087 | 0.12817 | 0.24719 | 0.20142 | 0.28839 | 0.018311 | 0.20599 | 0.65918 | -120.8496 | 120.8313 | -0.84686 | 120.7443 | 120.9503 | -0.58136 | -0.14648 | -0.1236 | -0.086975 | 120.7214 | 120.9091 | 120.9045 | 120.639 | 120.7443 | 121.3623 | 120.9915 | -0.14648 | 120.639 | 120.7443 | 120.9915 | 120.9045 | 121.3623 | -0.6546 | -121.6324
839.7812 | 121.6965 | -70.2713 | 50.7889 | -0.00061033 | 0.0084509 | -0.0026916 | 0.15067 | 0.018098 | 0.022911 | 0.18156 | 0.050354 | -0.09613 | 0.11444 | 0.1831 | 0.13733 | 0.23346 | -0.13275 | 0.10529 | 50.5692 | -70.6421 | 70.3857 | -50.885 | 70.3217 | 70.4544 | -50.6516 | -0.37079 | -0.21973 | -0.064087 | 70.1385 | 70.3766 | 70.4086 | 70.1752 | 70.3217 | 120.8405 | 70.5048 | -0.37079 | 70.1752 | 70.3217 | 70.5048 | 70.4086 | 120.8405 | -50.6744 | -121.431
840.7812 | 121.6644 | -111.6623 | 9.7137 | -0.0082398 | 0.0073829 | -0.00098264 | 0.023778 | -0.0039051 | 0.00069424 | 0.016861 | 0.045776 | -0.064087 | 0.11902 | 0.23804 | 0.16479 | 0.27008 | 0.004578 | 0.18768 | 9.6359 | -111.85 | 111.7813 | -9.7778 | 111.7081 | 111.9003 | -9.5489 | -0.18768 | -0.07782 | -0.073243 | 111.6669 | 111.85 | 111.8271 | 111.5982 | 111.7081 | 121.2982 | 111.9324 | -0.18768 | 111.5982 | 111.7081 | 111.9324 | 111.8271 | 121.2982 | -9.5947 | -121.5637
841.7812 | 121.6873 | -120.2499 | 1.1948 | 0.0070192 | 0.0099463 | 0.0015808 | 0.033392 | -0.0090319 | -0.0057144 | 0.011093 | 0.054932 | -0.050354 | 0.12817 | 0.25635 | 0.20599 | 0.29297 | 0.027466 | 0.20599 | 1.1215 | -120.4193 | 120.3781 | -1.2451 | 120.3049 | 120.5063 | -0.98877 | -0.16937 | -0.073242 | -0.073242 | 120.2774 | 120.4559 | 120.4559 | 120.1996 | 120.3049 | 121.3715 | 120.5429 | -0.16937 | 120.1996 | 120.3049 | 120.5429 | 120.4559 | 121.3715 | -1.0666 | -121.6141
842.7812 | 121.7285 | -120.3506 | 1.1581 | 0.0070192 | 0.0090919 | 0.0024354 | 0.037878 | -0.0090319 | -0.0040054 | 0.01323 | 0.12817 | -0.054932 | 0.14191 | 0.33417 | 0.27924 | 0.35706 | 0.004578 | 0.30212 | 0.97961 | -120.4651 | 120.4926 | -1.2131 | 120.4788 | 120.6848 | -0.87891 | -0.11444 | -0.17853 | -0.013733 | 120.3552 | 120.6528 | 120.6299 | 120.2957 | 120.4788 | 121.3303 | 120.7077 | -0.11444 | 120.2957 | 120.4788 | 120.7077 | 120.6299 | 121.3303 | -1.0162 | -121.6232
843.7812 | 121.7606 | -120.0623 | 1.3962 | -0.00061033 | 0.0065283 | -0.0029052 | 0.034246 | -0.010741 | -0.0055008 | 0.016648 | 0.09613 | -0.050354 | 0.14648 | 0.31586 | 0.27466 | 0.35248 | -0.009155 | 0.27924 | 1.3504 | -120.2499 | 120.2087 | -1.4465 | 120.1584 | 120.3781 | -1.1215 | -0.18768 | -0.045776 | -0.050354 | 120.0531 | 120.3415 | 120.3369 | 120.0119 | 120.1584 | 121.4127 | 120.4147 | -0.18768 | 120.0119 | 120.1584 | 120.4147 | 120.3369 | 121.4127 | -1.2497 | -121.6461
844.7812 | 121.7926 | -118.6844 | 2.8061 | -0.0082398 | 0.0090919 | 0.0041444 | 0.10239 | -0.0079639 | -0.0050736 | 0.076462 | 0.11444 | -0.073242 | 0.13733 | 0.32044 | 0.26093 | 0.35248 | -0.022888 | 0.32044 | 2.6962 | -118.8675 | 118.8217 | -2.8793 | 118.7988 | 119.0048 | -2.5452 | -0.18311 | -0.10986 | -0.022888 | 118.6615 | 119.0048 | 118.9453 | 118.6111 | 118.7988 | 121.3806 | 119.0369 | -0.18311 | 118.6111 | 118.7988 | 119.0369 | 118.9453 | 121.3806 | -2.6688 | -121.6736
845.7812 | 121.7606 | -110.1242 | 11.9431 | -0.0082398 | 0.0097327 | 0.0035034 | 0.099615 | -0.011168 | -0.0027238 | 0.063004 | 0.082397 | -0.059509 | 0.14191 | 0.30212 | 0.25177 | 0.34332 | -0.036621 | 0.17395 | 6.7337 | -110.3577 | 110.2661 | -12.0026 | 110.2066 | 110.4263 | -11.6913 | -0.23346 | -5.2093 | -0.05951 | 110.0876 | 110.2982 | 110.376 | 110.0647 | 110.2066 | 116.8579 | 110.4675 | -0.23346 | 110.0647 | 110.2066 | 110.4675 | 110.376 | 116.8579 | -11.8011 | -122.3007
846.7812 | 121.7514 | -57.5134 | 62.9333 | -0.00061033 | 0.0088783 | 0.00093996 | 0.17032 | 0.022798 | 0.030388 | 0.29158 | 0.068665 | -0.09613 | 0.10529 | 0.16937 | 0.10529 | 0.20599 | -0.16479 | 0.11902 | 64.4485 | -57.0877 | 57.6187 | -63.0295 | 57.5821 | 57.6828 | -62.8281 | 0.42572 | 1.5152 | -0.036621 | 57.3486 | 57.6324 | 57.6187 | 57.4173 | 57.5821 | 121.962 | 57.7194 | 0.42572 | 57.4173 | 57.5821 | 57.7194 | 57.6187 | 121.962 | -62.8281 | -120.0211
847.7812 | 121.7834 | -120.9503 | 0.52185 | -0.00061033 | 0.0073829 | 0.0015808 | 0.035314 | -0.011168 | -0.0055008 | 0.014298 | 0.10071 | -0.050354 | 0.13275 | 0.32959 | 0.27466 | 0.35706 | 0 | 0.29297 | 0.44861 | -121.1563 | 121.0831 | -0.5722 | 121.051 | 121.2799 | -0.24719 | -0.20599 | -0.073243 | -0.032043 | 120.9503 | 121.2433 | 121.225 | 120.9 | 121.051 | 121.3989 | 121.3074 | -0.20599 | 120.9 | 121.051 | 121.3074 | 121.225 | 121.3989 | -0.3891 | -121.6782
848.7812 | 121.8155 | -121.0693 | 0.49439 | -0.00061033 | 0.0088783 | 0.0017944 | 0.035741 | -0.010527 | -0.0052872 | 0.013443 | 0.11444 | -0.068665 | 0.15564 | 0.3479 | 0.28839 | 0.36621 | 0.013733 | 0.31128 | 0.43488 | -121.17 | 121.225 | -0.56305 | 121.1838 | 121.4172 | -0.20599 | -0.10071 | -0.05951 | -0.041199 | 121.0831 | 121.3806 | 121.3577 | 121.0007 | 121.1838 | 121.5042 | 121.4355 | -0.10071 | 121.0007 | 121.1838 | 121.4355 | 121.3577 | 121.5042 | -0.33875 | -121.6644
849.7812 | 121.7606 | -120.7306 | 0.8606 | -0.00061033 | 0.012082 | -0.00034184 | 0.078893 | -0.010314 | -0.0029374 | 0.038224 | 0.1236 | -0.059509 | 0.15564 | 0.33417 | 0.26093 | 0.3479 | 0.022888 | 0.27924 | 0.80109 | -120.813 | 120.8862 | -0.92011 | 120.8542 | 121.0648 | -0.59967 | -0.082397 | -0.05951 | -0.032044 | 120.7535 | 121.0098 | 120.9915 | 120.6711 | 120.8542 | 121.5317 | 121.0785 | -0.082397 | 120.6711 | 120.8542 | 121.0785 | 120.9915 | 121.5317 | -0.70496 | -121.6736
850.7812 | 121.7148 | -120.8862 | 0.7782 | -0.0082398 | 0.016141 | 0.00072636 | 0.057745 | -0.0071093 | -0.0063554 | 0.032029 | 0.045776 | -0.004578 | 0.082397 | 0.22888 | 0.17395 | 0.23346 | 0.16937 | 0.15564 | 0.6958 | -121.0464 | 120.9686 | -0.78278 | 120.932 | 121.1151 | -0.60425 | -0.16022 | -0.082397 | -0.036621 | 121.0556 | 121.0419 | 121.0602 | 120.8817 | 120.932 | 121.582 | 121.1197 | -0.16022 | 120.8817 | 120.932 | 121.1197 | 121.0602 | 121.582 | -0.6958 | -121.8246
851.7812 | 121.7789 | -120.163 | 1.2634 | -0.00061033 | 0.0093055 | 0.00029916 | 0.077825 | -0.0068957 | -0.0050736 | 0.058304 | 0.11902 | -0.064087 | 0.13275 | 0.33417 | 0.29297 | 0.37079 | 0 | 0.31128 | 1.1719 | -120.3735 | 120.2957 | -1.3275 | 120.282 | 120.4971 | -0.97046 | -0.21057 | -0.091553 | -0.013732 | 120.163 | 120.4742 | 120.4559 | 120.0989 | 120.282 | 121.3348 | 120.5338 | -0.21057 | 120.0989 | 120.282 | 120.5338 | 120.4559 | 121.3348 | -1.1307 | -121.637
852.7812 | 121.8063 | -117.6132 | 3.9917 | -0.0082398 | 0.011228 | 0.00093996 | 0.23996 | -0.0081775 | -0.0037918 | 0.22087 | 0.10986 | -0.073242 | 0.12817 | 0.32501 | 0.27008 | 0.34332 | 0.018311 | 0.23346 | 3.8818 | -117.7872 | 117.7414 | -4.0649 | 117.7231 | 117.9382 | -3.7216 | -0.17395 | -0.10986 | -0.018311 | 117.6315 | 117.8467 | 117.8833 | 117.54 | 117.7231 | 121.4951 | 117.9565 | -0.17395 | 117.54 | 117.7231 | 117.9565 | 117.8833 | 121.4951 | -3.8635 | -121.7789
853.7812 | 121.8246 | -121.1426 | 0.43945 | -0.00061033 | 0.01016 | 0.003717 | 0.048132 | -0.0096729 | -0.0044328 | 0.025406 | 0.13275 | -0.068665 | 0.13275 | 0.3479 | 0.28381 | 0.37079 | 0.009155 | 0.29755 | 0.37079 | -121.3028 | 121.2753 | -0.50812 | 121.2753 | 121.4905 | -0.15564 | -0.16022 | -0.068664 | 0 | 121.1517 | 121.4401 | 121.4264 | 121.0739 | 121.2753 | 121.5134 | 121.5134 | -0.16022 | 121.0739 | 121.2753 | 121.5134 | 121.4264 | 121.5134 | -0.3067 | -121.7422
854.7812 | 121.7789 | -119.7098 | 1.9455 | 0.0070192 | 0.0093055 | -0.00055544 | 0.16498 | -0.0098865 | -0.005928 | 0.14482 | 0.1236 | -0.068665 | 0.15106 | 0.33875 | 0.28381 | 0.37079 | 0.022888 | 0.31586 | 1.8906 | -119.7968 | 119.8608 | -2.0142 | 119.8334 | 120.0485 | -1.6617 | -0.086975 | -0.054932 | -0.027466 | 119.7327 | 120.0256 | 119.9936 | 119.6411 | 119.8334 | 121.6003 | 120.0806 | -0.086975 | 119.6411 | 119.8334 | 120.0806 | 119.9936 | 121.6003 | -1.7944 | -121.7422
855.7812 | 121.8338 | -120.8908 | 0.737 | 0.0070192 | 0.010587 | 0.00051276 | 0.079534 | -0.0096729 | -0.0067826 | 0.054459 | 0.1236 | -0.064087 | 0.1236 | 0.3479 | 0.30212 | 0.36621 | 0.022888 | 0.29755 | 0.66834 | -121.0098 | 121.0144 | -0.80109 | 121.0144 | 121.2387 | -0.43488 | -0.11902 | -0.068665 | 0 | 120.9137 | 121.1884 | 121.1929 | 120.8267 | 121.0144 | 121.5591 | 121.257 | -0.11902 | 120.8267 | 121.0144 | 121.257 | 121.1929 | 121.5591 | -0.6134 | -121.7468
856.7812 | 121.7651 | -121.0327 | 0.64545 | 0.0070192 | 0.0086645 | 0.002008 | 0.10154 | -0.010314 | -0.00486 | 0.072403 | 0.10529 | -0.036621 | 0.1236 | 0.28839 | 0.2243 | 0.32044 | 0.10529 | 0.23346 | 0.56305 | -121.1838 | 121.1563 | -0.68207 | 121.138 | 121.3211 | -0.42114 | -0.15106 | -0.082398 | -0.01831 | 121.138 | 121.2662 | 121.257 | 120.9961 | 121.138 | 121.5958 | 121.3531 | -0.15106 | 120.9961 | 121.138 | 121.3531 | 121.257 | 121.5958 | -0.52185 | -121.8292
857.7812 | 121.8201 | -119.9295 | 1.7395 | -0.0082398 | 0.0093055 | -0.00098264 | 1.6516 | -0.010314 | -0.0044328 | 1.672 | 0.11902 | -0.073242 | 0.14191 | 0.33875 | 0.27466 | 0.35706 | 0.009155 | 0.28839 | 1.5564 | -119.8791 | 120.0714 | -1.8127 | 120.0485 | 120.2682 | -1.4648 | 0.050354 | -0.18311 | -0.022888 | 119.9387 | 120.2179 | 120.2042 | 119.8563 | 120.0485 | 121.4859 | 120.2866 | 0.050354 | 119.8563 | 120.0485 | 120.2866 | 120.2042 | 121.4859 | -1.5976 | -121.6187
858.7812 | 121.4401 | -115.5487 | 5.8914 | -0.00061033 | 0.013364 | 0.0041444 | 0.72703 | -0.0073229 | -0.0061416 | 0.71349 | 0.10071 | -0.064087 | 0.10986 | 0.29297 | 0.25177 | 0.34332 | 0.086975 | 0.073242 | 2.98 | -116.716 | 115.6586 | -5.9555 | 115.6494 | 115.8417 | -5.6396 | -1.1673 | -2.9114 | -0.009155 | 115.6357 | 115.6219 | 115.8005 | 115.4846 | 115.6494 | 118.5287 | 115.892 | -1.1673 | 115.4846 | 115.6494 | 115.892 | 115.8005 | 118.5287 | -5.7816 | -122.6074
859.7812 | 121.8658 | -120.8176 | 0.7782 | 0.0070192 | 0.01016 | 0.0039306 | 0.095129 | -0.0090319 | -0.0069962 | 0.09697 | 0.11902 | -0.07782 | 0.15106 | 0.33417 | 0.27924 | 0.36621 | 0.013733 | 0.28381 | 0.59509 | -120.9869 | 120.9686 | -0.85602 | 120.9366 | 121.1517 | -0.49896 | -0.16937 | -0.1831 | -0.032043 | 120.8313 | 121.1014 | 121.0968 | 120.7397 | 120.9366 | 121.4127 | 121.1838 | -0.16937 | 120.7397 | 120.9366 | 121.1838 | 121.0968 | 121.4127 | -0.62714 | -121.7651
860.7812 | 121.8292 | -120.52 | 0.96588 | 0.0070192 | 0.012082 | 0.0056396 | 0.20194 | -0.0098865 | -0.00486 | 0.18498 | 0.10986 | -0.068665 | 0.14191 | 0.31128 | 0.27924 | 0.37079 | -0.004578 | 0.29755 | 0.85602 | -120.7443 | 120.6619 | -1.0345 | 120.6299 | 120.8313 | -0.68664 | -0.2243 | -0.10986 | -0.032044 | 120.5154 | 120.8176 | 120.7993 | 120.4514 | 120.6299 | 121.376 | 120.8908 | -0.2243 | 120.4514 | 120.6299 | 120.8908 | 120.7993 | 121.376 | -0.82397 | -121.7102
861.7812 | 121.0831 | -10.6934 | 110.2524 | -0.015869 | 0.0099463 | 0.0011536 | 0.019506 | 0.05356 | 0.057091 | 0.15251 | 0.09613 | -0.14191 | 0.073242 | 0.086975 | 0.027466 | 0.11902 | -0.25177 | 0.050354 | 110.1196 | -10.7437 | 10.7666 | -110.3943 | 10.7895 | 10.7803 | -110.2249 | -0.050354 | -0.13275 | 0.022888 | 10.4416 | 10.7437 | 10.7208 | 10.5515 | 10.7895 | 120.813 | 10.8124 | -0.050354 | 10.5515 | 10.7895 | 10.8124 | 10.7208 | 120.813 | -110.1791 | -120.9961
862.7812 | 121.3898 | -8.7845 | 111.9919 | -0.0082398 | 0.011442 | 8.5364e-05 | 0.036169 | 0.052705 | 0.059868 | 0.16576 | 0.068665 | -0.13275 | 0.086975 | 0.091553 | 0.027466 | 0.10529 | -0.24261 | 0.027466 | 112.3398 | -8.8257 | 8.8715 | -112.1246 | 8.8531 | 8.876 | -111.9644 | -0.041199 | 0.3479 | -0.01831 | 8.5419 | 8.812 | 8.812 | 8.6517 | 8.8531 | 121.1243 | 8.8898 | -0.041199 | 8.6517 | 8.8531 | 8.8898 | 8.812 | 121.1243 | -111.9049 | -120.8176
863.7812 | 121.1746 | -7.7499 | 109.8267 | -0.00061033 | 0.010373 | 0.003717 | 0.02207 | 0.050142 | 0.057732 | 0.15273 | 0.036621 | -0.11444 | 0.082397 | 0.045776 | -0.018311 | 0.059509 | -0.16937 | -0.027466 | 113.5071 | -7.7408 | 7.8323 | -109.9411 | 7.7866 | 7.7957 | -109.845 | 0.009155 | 3.6804 | -0.045776 | 7.5806 | 7.7225 | 7.7316 | 7.6355 | 7.7866 | 121.257 | 7.8094 | 0.009155 | 7.6355 | 7.7866 | 7.8094 | 7.7316 | 121.257 | -109.7443 | -117.5674
864.7812 | 121.6095 | -9.6313 | 110.9619 | -0.0082398 | 0.012082 | -0.0022644 | 0.058172 | 0.05121 | 0.055168 | 0.18456 | 0.054932 | -0.11902 | 0.073242 | 0.09613 | 0.032043 | 0.11444 | -0.24719 | 0.041199 | 111.6669 | -9.5947 | 9.7046 | -111.0809 | 9.6863 | 9.7275 | -110.9299 | 0.036621 | 0.70496 | -0.01831 | 9.3842 | 9.6725 | 9.6634 | 9.5123 | 9.6863 | 121.2982 | 9.7458 | 0.036621 | 9.5123 | 9.6863 | 9.7458 | 9.6634 | 121.2982 | -110.8887 | -120.5566
865.7812 | 120.813 | -13.9023 | 103.949 | -0.00061033 | 0.010373 | 0.0041444 | 0.098547 | 0.05121 | 0.054954 | 0.21126 | 0.045776 | -0.11902 | 0.068665 | 0.082397 | 0.013733 | 0.12817 | -0.22888 | 0.013733 | 108.4534 | -12.9547 | 13.9709 | -104.068 | 13.9481 | 13.9847 | -103.9352 | 0.94757 | 4.5044 | -0.022889 | 13.6734 | 13.916 | 13.916 | 13.7833 | 13.9481 | 122.3557 | 14.0305 | 0.94757 | 13.7833 | 13.9481 | 14.0305 | 13.916 | 122.3557 | -103.8803 | -116.9037
866.7812 | 121.5088 | -71.5759 | 49.6674 | -0.00061033 | 0.0095191 | 0.0013672 | 0.87656 | 0.016389 | 0.021202 | 0.91451 | 0.091553 | -0.091553 | 0.10986 | 0.20142 | 0.1236 | 0.20599 | -0.11902 | 0.16479 | 49.5712 | -71.5759 | 71.6858 | -49.7589 | 71.6675 | 71.7773 | -49.5438 | 0 | -0.09613 | -0.01831 | 71.4569 | 71.7407 | 71.6995 | 71.4844 | 71.6675 | 121.1472 | 71.7819 | 0 | 71.4844 | 71.6675 | 71.7819 | 71.6995 | 121.1472 | -49.5575 | -121.2433
867.7812 | 121.637 | -121.0144 | 0.35248 | -0.0082398 | 0.0088783 | 0.002008 | 0.034673 | -0.0081775 | -0.0061416 | 0.01323 | 0.1236 | -0.073242 | 0.12817 | 0.29297 | 0.24719 | 0.33417 | -0.054932 | 0.27466 | 0.2655 | -121.1746 | 121.1426 | -0.42572 | 121.138 | 121.3074 | -0.10529 | -0.16022 | -0.086975 | -0.004578 | 120.9595 | 121.2891 | 121.2616 | 120.9412 | 121.138 | 121.2799 | 121.3486 | -0.16022 | 120.9412 | 121.138 | 121.3486 | 121.2616 | 121.2799 | -0.2243 | -121.5271
868.7812 | 121.669 | -120.9503 | 0.54016 | -0.00061033 | 0.0095191 | 0.0022218 | 0.049627 | -0.0077503 | -0.0044328 | 0.027756 | 0.11444 | -0.073242 | 0.14191 | 0.27466 | 0.23346 | 0.32044 | -0.064087 | 0.26093 | 0.46692 | -121.0052 | 121.0922 | -0.6134 | 121.0648 | 121.225 | -0.3067 | -0.054932 | -0.073242 | -0.027466 | 120.8862 | 121.2112 | 121.1838 | 120.8771 | 121.0648 | 121.4172 | 121.2708 | -0.054932 | 120.8771 | 121.0648 | 121.2708 | 121.1838 | 121.4172 | -0.39825 | -121.5454
869.7812 | 121.1655 | -120.2866 | 0.58136 | -0.015869 | 0.010801 | 0.0011536 | 0.021215 | -0.0075367 | -0.0040054 | -0.00022864 | 0.13733 | -0.091553 | 0.13275 | 0.27008 | 0.22888 | 0.31128 | -0.045776 | 0.24261 | 0.5127 | -120.4468 | 120.4193 | -0.67291 | 120.4239 | 120.5566 | -0.35248 | -0.16022 | -0.068665 | 0.004578 | 120.2408 | 120.5292 | 120.5154 | 120.195 | 120.4239 | 120.7993 | 120.5978 | -0.16022 | 120.195 | 120.4239 | 120.5978 | 120.5154 | 120.7993 | -0.44861 | -121.0281
870.7812 | 121.5546 | -120.5429 | 0.85144 | -0.0082398 | 0.0095191 | 0.00029916 | 0.024419 | -0.0079639 | -0.0029374 | -0.00022864 | 0.12817 | -0.068665 | 0.13275 | 0.27924 | 0.22888 | 0.29755 | -0.041199 | 0.22888 | 0.75531 | -120.607 | 120.6757 | -0.9201 | 120.6711 | 120.8221 | -0.62256 | -0.064087 | -0.09613 | -0.004577 | 120.5017 | 120.7718 | 120.7718 | 120.4742 | 120.6711 | 121.2982 | 120.8405 | -0.064087 | 120.4742 | 120.6711 | 120.8405 | 120.7718 | 121.2982 | -0.71869 | -121.4584
871.7812 | 121.6232 | -120.7077 | 0.71411 | -0.00061033 | 0.0090919 | 0.002008 | 0.025915 | -0.010527 | -0.0044328 | 0.0042576 | 0.10071 | -0.073242 | 0.12817 | 0.27466 | 0.2243 | 0.32959 | -0.050354 | 0.24719 | 0.64087 | -120.7672 | 120.8359 | -0.78735 | 120.8084 | 120.9824 | -0.48981 | -0.059509 | -0.073242 | -0.027466 | 120.6573 | 120.9549 | 120.932 | 120.6345 | 120.8084 | 121.3486 | 121.0373 | -0.059509 | 120.6345 | 120.8084 | 121.0373 | 120.932 | 121.3486 | -0.58594 | -121.4813
872.7969 | 121.6278 | -120.7901 | 0.66376 | -0.00061033 | 0.0080237 | 0.0022218 | 0.030614 | -0.010314 | -0.0029374 | 0.0072482 | 0.073242 | -0.064087 | 0.1236 | 0.21057 | 0.16479 | 0.2655 | 0 | 0.15564 | 0.58594 | -120.9274 | 120.9137 | -0.72784 | 120.8633 | 121.0007 | -0.49896 | -0.13733 | -0.07782 | -0.050354 | 120.7901 | 120.9457 | 120.9549 | 120.726 | 120.8633 | 121.376 | 121.0556 | -0.13733 | 120.726 | 120.8633 | 121.0556 | 120.9549 | 121.376 | -0.54016 | -121.5912
873.7812 | 121.669 | -120.8725 | 0.62256 | -0.00061033 | 0.0088783 | 0.002008 | 0.029119 | -0.012023 | -0.0050736 | 0.0057528 | 0.068665 | -0.054932 | 0.12817 | 0.25635 | 0.21057 | 0.31128 | -0.032043 | 0.23804 | 0.52643 | -120.9778 | 121.0007 | -0.67749 | 120.9412 | 121.1288 | -0.41199 | -0.10529 | -0.096131 | -0.059509 | 120.8405 | 121.1105 | 121.0831 | 120.8176 | 120.9412 | 121.3989 | 121.1838 | -0.10529 | 120.8176 | 120.9412 | 121.1838 | 121.0831 | 121.3989 | -0.49438 | -121.6003
874.7812 | 121.6187 | -120.575 | 0.87891 | -0.0082398 | 0.0090919 | 0.0022218 | 0.041936 | -0.010741 | -0.0033646 | 0.017289 | 0.064087 | -0.041199 | 0.13733 | 0.24719 | 0.19226 | 0.28381 | 0 | 0.20599 | 0.77362 | -120.7123 | 120.7123 | -0.9201 | 120.639 | 120.8221 | -0.68664 | -0.13733 | -0.10528 | -0.073242 | 120.575 | 120.7809 | 120.7672 | 120.5338 | 120.639 | 121.3486 | 120.8588 | -0.13733 | 120.5338 | 120.639 | 120.8588 | 120.7672 | 121.3486 | -0.74158 | -121.5912
875.7812 | 121.6553 | -120.7855 | 0.72327 | -0.0082398 | 0.0078101 | 0.0039306 | 0.038091 | -0.012023 | -0.0050736 | 0.014939 | 0.054932 | -0.041199 | 0.12817 | 0.22888 | 0.17853 | 0.29755 | 0.022888 | 0.20142 | 0.64545 | -120.8908 | 120.9137 | -0.76447 | 120.8405 | 121.0144 | -0.54474 | -0.10529 | -0.07782 | -0.073242 | 120.8084 | 120.9869 | 120.9641 | 120.7443 | 120.8405 | 121.431 | 121.0831 | -0.10529 | 120.7443 | 120.8405 | 121.0831 | 120.9641 | 121.431 | -0.59509 | -121.6141
876.7812 | 121.701 | -120.726 | 0.79193 | -0.00061033 | 0.010373 | 0.0017944 | 0.040227 | -0.012236 | -0.0057144 | 0.017502 | 0.07782 | -0.045776 | 0.13275 | 0.27924 | 0.24719 | 0.33875 | 0.032043 | 0.24719 | 0.68207 | -120.8588 | 120.8588 | -0.83771 | 120.8038 | 121.0052 | -0.54474 | -0.13275 | -0.10986 | -0.054931 | 120.7581 | 120.9732 | 120.9732 | 120.6802 | 120.8038 | 121.4081 | 121.0648 | -0.13275 | 120.6802 | 120.8038 | 121.0648 | 120.9732 | 121.4081 | -0.65918 | -121.6507
877.7812 | 121.7606 | -120.7169 | 0.78278 | 0.0070192 | 0.0090919 | -0.00098264 | 0.039159 | -0.013304 | -0.006569 | 0.01088 | 0.10071 | -0.068665 | 0.14648 | 0.33875 | 0.27008 | 0.36163 | -0.013733 | 0.29755 | 0.67291 | -120.8405 | 120.8633 | -0.85144 | 120.8176 | 121.0556 | -0.5127 | -0.1236 | -0.10986 | -0.045776 | 120.7031 | 121.0144 | 120.9869 | 120.6482 | 120.8176 | 121.3898 | 121.0785 | -0.1236 | 120.6482 | 120.8176 | 121.0785 | 120.9869 | 121.3898 | -0.63629 | -121.6232
878.7812 | 121.701 | -120.4605 | 1.0162 | -0.0082398 | 0.0099463 | -0.00098264 | 0.051122 | -0.0081775 | -0.0050736 | 0.026047 | 0.054932 | -0.059509 | 0.1236 | 0.25635 | 0.21515 | 0.31586 | 0.027466 | 0.2243 | 0.92468 | -120.6299 | 120.5841 | -1.0757 | 120.5154 | 120.7169 | -0.80109 | -0.16937 | -0.091552 | -0.068664 | 120.488 | 120.6848 | 120.6757 | 120.401 | 120.5154 | 121.3852 | 120.7764 | -0.16937 | 120.401 | 120.5154 | 120.7764 | 120.6757 | 121.3852 | -0.89264 | -121.6461
879.7812 | 121.7697 | -120.6436 | 0.83771 | -0.0082398 | 0.0078101 | 0.00093996 | 0.047704 | -0.0092457 | -0.0040054 | 0.039292 | 0.082397 | -0.064087 | 0.14648 | 0.29297 | 0.24719 | 0.33417 | 0.009155 | 0.25177 | 0.75989 | -120.8176 | 120.7901 | -0.9018 | 120.726 | 120.9366 | -0.59052 | -0.17395 | -0.07782 | -0.064087 | 120.6528 | 120.8954 | 120.8908 | 120.5795 | 120.726 | 121.4035 | 120.9778 | -0.17395 | 120.5795 | 120.726 | 120.9778 | 120.8908 | 121.4035 | -0.69122 | -121.6553
880.7812 | 121.7606 | -119.8837 | 1.6754 | 0.0070192 | 0.010373 | 0.00051276 | 0.079748 | -0.011382 | -0.003151 | 0.063431 | 0.059509 | -0.045776 | 0.12817 | 0.25635 | 0.21515 | 0.30212 | -0.009155 | 0.21515 | 1.442 | -120.0577 | 120.0119 | -1.7212 | 119.9432 | 120.1401 | -1.4603 | -0.17395 | -0.23346 | -0.068665 | 119.8746 | 120.0989 | 120.0989 | 119.838 | 119.9432 | 121.3257 | 120.1859 | -0.17395 | 119.838 | 119.9432 | 120.1859 | 120.0989 | 121.3257 | -1.5472 | -121.7331
881.7812 | 121.6919 | -120.6665 | 0.90179 | -0.00061033 | 0.0093055 | -0.0031188 | 0.054113 | -0.011809 | -0.0061416 | 0.032242 | 0.064087 | -0.073242 | 0.14191 | 0.22888 | 0.1831 | 0.28381 | 0.013733 | 0.1831 | 0.81024 | -120.7718 | 120.8084 | -0.97504 | 120.7306 | 120.8954 | -0.71869 | -0.10529 | -0.091552 | -0.07782 | 120.6802 | 120.8496 | 120.8496 | 120.5933 | 120.7306 | 121.4767 | 120.9503 | -0.10529 | 120.5933 | 120.7306 | 120.9503 | 120.8496 | 121.4767 | -0.75989 | -121.6736
882.7812 | 121.7102 | -120.3232 | 1.4053 | -0.00061033 | 0.0075965 | -0.00055544 | 0.089788 | -0.0086047 | -0.004219 | 0.080521 | 0.059509 | -0.059509 | 0.13733 | 0.23804 | 0.16937 | 0.28839 | 0.004578 | 0.1831 | 1.4648 | -120.2682 | 120.4605 | -1.4648 | 120.3827 | 120.5612 | -1.236 | 0.054931 | 0.05951 | -0.07782 | 120.3278 | 120.5063 | 120.4926 | 120.2637 | 120.3827 | 121.788 | 120.6116 | 0.054931 | 120.2637 | 120.3827 | 120.6116 | 120.4926 | 121.788 | -1.268 | -121.6736
883.7812 | 121.756 | -120.932 | 0.62714 | -0.00061033 | 0.0084509 | 0.0035034 | 0.05219 | -0.011809 | -0.0025102 | 0.030106 | 0.041199 | -0.050354 | 0.11902 | 0.23346 | 0.19226 | 0.29297 | 0.041199 | 0.17853 | 0.52643 | -121.0602 | 121.051 | -0.67749 | 120.9732 | 121.1655 | -0.43488 | -0.12817 | -0.10071 | -0.07782 | 120.9732 | 121.1105 | 121.1243 | 120.8817 | 120.9732 | 121.4584 | 121.225 | -0.12817 | 120.8817 | 120.9732 | 121.225 | 121.1243 | 121.4584 | -0.50812 | -121.6873
884.7812 | 121.8018 | -120.7901 | 0.80109 | -0.00061033 | 0.0080237 | 0.0039306 | 0.060522 | -0.010741 | -0.004219 | 0.038224 | 0.068665 | -0.073242 | 0.12817 | 0.27466 | 0.2243 | 0.32044 | 0.004578 | 0.22888 | 0.66376 | -120.8862 | 120.9183 | -0.87433 | 120.8588 | 121.0648 | -0.57678 | -0.09613 | -0.13733 | -0.059509 | 120.7947 | 121.019 | 121.0144 | 120.7169 | 120.8588 | 121.4539 | 121.1105 | -0.09613 | 120.7169 | 120.8588 | 121.1105 | 121.0144 | 121.4539 | -0.67291 | -121.6873
885.7812 | 121.7514 | -120.8221 | 0.77362 | -0.0082398 | 0.0095191 | 0.0024354 | 0.071416 | -0.0096729 | -0.0046464 | 0.049973 | 0.064087 | -0.032043 | 0.12817 | 0.2243 | 0.19226 | 0.28381 | 0.018311 | 0.1831 | 0.70038 | -120.9137 | 120.9503 | -0.80566 | 120.8862 | 121.0464 | -0.58136 | -0.091552 | -0.073243 | -0.064087 | 120.8405 | 121.0052 | 121.0144 | 120.7901 | 120.8862 | 121.5225 | 121.106 | -0.091552 | 120.7901 | 120.8862 | 121.106 | 121.0144 | 121.5225 | -0.64545 | -121.6873
886.7812 | 121.7148 | -120.7306 | 0.85144 | 0.0070192 | 0.0063147 | 0.0011536 | 0.072485 | -0.0096729 | -0.0046464 | 0.048264 | 0.041199 | -0.050354 | 0.13275 | 0.24719 | 0.18768 | 0.29755 | 0.009155 | 0.20599 | 0.74616 | -120.8725 | 120.8633 | -0.90179 | 120.7718 | 120.9778 | -0.66376 | -0.14191 | -0.10528 | -0.091552 | 120.7397 | 120.9366 | 120.9183 | 120.6802 | 120.7718 | 121.4767 | 121.0281 | -0.14191 | 120.6802 | 120.7718 | 121.0281 | 120.9183 | 121.4767 | -0.71869 | -121.7239
887.7812 | 121.7789 | -117.5125 | 4.2023 | -0.015869 | 0.0097327 | -0.0026916 | 0.32157 | -0.0092457 | -0.0033646 | 0.23048 | 0.059509 | -0.050354 | 0.11902 | 0.23804 | 0.17395 | 0.28381 | 0.018311 | 0.18768 | 3.8589 | -117.2333 | 117.6315 | -4.2526 | 117.572 | 117.7505 | -4.0283 | 0.27924 | -0.34332 | -0.05951 | 117.5308 | 117.7002 | 117.6865 | 117.4622 | 117.572 | 121.3715 | 117.7963 | 0.27924 | 117.4622 | 117.572 | 117.7963 | 117.6865 | 121.3715 | -4.0833 | -121.4355
888.7812 | 121.8063 | -121.0968 | 0.49439 | -0.015869 | 0.0095191 | -0.00076904 | 0.087011 | -0.011168 | -0.0046464 | 0.023911 | 0.082397 | -0.050354 | 0.13275 | 0.25635 | 0.21973 | 0.31586 | -0.009155 | 0.21515 | 0.58594 | -121.2341 | 121.2296 | -0.54474 | 121.1792 | 121.3531 | -0.27466 | -0.13733 | 0.091552 | -0.050354 | 121.0876 | 121.312 | 121.3165 | 121.0464 | 121.1792 | 121.6827 | 121.4127 | -0.13733 | 121.0464 | 121.1792 | 121.4127 | 121.3165 | 121.6827 | -0.36163 | -121.7285
889.7812 | 121.7651 | -121.1197 | 0.48065 | -0.00061033 | 0.0088783 | 0.0030762 | 0.053258 | -0.0086047 | -0.0033646 | 0.02562 | 0.10071 | -0.064087 | 0.11902 | 0.27924 | 0.21973 | 0.31586 | 0 | 0.21057 | 0.3891 | -121.257 | 121.2387 | -0.54474 | 121.2204 | 121.3989 | -0.26093 | -0.13733 | -0.091553 | -0.018311 | 121.1197 | 121.3303 | 121.3394 | 121.0556 | 121.2204 | 121.5088 | 121.4355 | -0.13733 | 121.0556 | 121.2204 | 121.4355 | 121.3394 | 121.5088 | -0.36163 | -121.7377
890.7812 | 121.7148 | -120.9091 | 0.68665 | 0.0070192 | 0.0082373 | 0.005426 | 0.096624 | -0.0098865 | -0.0052872 | 0.050614 | 0.041199 | -0.068665 | 0.21057 | 0.25177 | 0.23804 | 0.31128 | 0.032043 | 0.22888 | 0.61798 | -113.4521 | 121.1197 | -0.75531 | 120.9503 | 121.1609 | -0.44861 | 7.457 | -0.068665 | -0.16937 | 120.9412 | 121.138 | 121.1472 | 120.8405 | 120.9503 | 121.5271 | 121.2204 | 7.457 | 120.8405 | 120.9503 | 121.2204 | 121.1472 | 121.5271 | -0.47607 | -114.1388
891.7812 | 121.7972 | -118.1305 | 3.4058 | -0.0082398 | 0.0099463 | -0.00098264 | 0.41001 | -0.010527 | -0.0029374 | 0.3907 | 0.059509 | -0.064087 | 0.13275 | 0.25177 | 0.20142 | 0.29297 | 0.013733 | 0.20142 | 3.4927 | -118.2678 | 118.2632 | -3.4698 | 118.19 | 118.3823 | -3.2043 | -0.13733 | 0.086975 | -0.073242 | 118.1442 | 118.3319 | 118.3319 | 118.0664 | 118.19 | 121.6232 | 118.4235 | -0.13733 | 118.0664 | 118.19 | 118.4235 | 118.3319 | 121.6232 | -3.273 | -121.6736
892.7812 | 121.7331 | -120.7855 | 0.84228 | -0.00061033 | 0.0099463 | 0.0015808 | 0.093206 | -0.011168 | -0.0040054 | 0.068344 | 0.050354 | -0.041199 | 0.12817 | 0.25177 | 0.19684 | 0.3067 | 0.032043 | 0.19684 | 0.74158 | -120.9366 | 120.9137 | -0.88348 | 120.8359 | 121.0373 | -0.64545 | -0.15106 | -0.10071 | -0.07782 | 120.8176 | 120.9824 | 120.9824 | 120.7443 | 120.8359 | 121.5271 | 121.0922 | -0.15106 | 120.7443 | 120.8359 | 121.0922 | 120.9824 | 121.5271 | -0.71411 | -121.7789
893.7812 | 121.8384 | -113.3377 | 8.194 | -0.00061033 | 0.010587 | 8.5364e-05 | 0.97996 | -0.0049731 | 0.0017624 | 0.95873 | 0.10986 | -0.086975 | 0.12817 | 0.27008 | 0.21057 | 0.31128 | -0.032043 | 0.21515 | 7.9788 | -113.4247 | 113.4659 | -8.2809 | 113.4476 | 113.6078 | -7.9834 | -0.086975 | -0.21515 | -0.018311 | 113.3057 | 113.5529 | 113.5483 | 113.2507 | 113.4476 | 121.3165 | 113.649 | -0.086975 | 113.2507 | 113.4476 | 113.649 | 113.5483 | 121.3165 | -8.0658 | -121.6187
894.7812 | 121.7972 | -118.4647 | 3.0396 | -0.00061033 | 0.0093055 | 0.0062806 | 0.46705 | -0.0092457 | -0.0033646 | 0.44603 | 0.07782 | -0.07782 | 0.13733 | 0.24261 | 0.20142 | 0.29755 | 0.004578 | 0.18768 | 2.9068 | -118.6249 | 118.602 | -3.1174 | 118.5425 | 118.7073 | -2.8381 | -0.16022 | -0.13275 | -0.059509 | 118.4692 | 118.6523 | 118.6661 | 118.3868 | 118.5425 | 121.3715 | 118.7622 | -0.16022 | 118.3868 | 118.5425 | 118.7622 | 118.6661 | 121.3715 | -2.9022 | -121.6644
895.7812 | 121.701 | -115.3107 | 6.221 | -0.0082398 | 0.0099463 | 0.0041444 | 1.1459 | -0.0049731 | -0.0012284 | 1.1933 | 0.1236 | -0.073242 | 0.1236 | 0.31128 | 0.23804 | 0.34332 | -0.073242 | 0.25177 | 6.102 | -115.3107 | 115.4343 | -6.2942 | 115.4343 | 115.6219 | -5.983 | 0 | -0.11902 | 0 | 115.2374 | 115.5624 | 115.5487 | 115.2374 | 115.4343 | 121.4127 | 115.654 | 0 | 115.2374 | 115.4343 | 115.654 | 115.5487 | 121.4127 | -6.0974 | -121.5317
896.7812 | 121.8658 | -120.0989 | 1.3962 | -0.0082398 | 0.011442 | 0.0094848 | 0.11414 | -0.0049731 | -0.0055008 | 0.086716 | 0.14191 | -0.073242 | 0.13275 | 0.32044 | 0.24719 | 0.35248 | -0.07782 | 0.25635 | 1.2726 | -120.2911 | 120.2316 | -1.4694 | 120.2408 | 120.4193 | -1.149 | -0.19226 | -0.1236 | 0.009156 | 120.0211 | 120.3552 | 120.3461 | 120.0256 | 120.2408 | 121.3715 | 120.4514 | -0.19226 | 120.0256 | 120.2408 | 120.4514 | 120.3461 | 121.3715 | -1.2634 | -121.6873
897.7969 | 121.7743 | -110.0739 | 11.4532 | -0.00061033 | 0.0088783 | 8.5364e-05 | 0.87208 | -0.0039051 | 0.0021896 | 0.86473 | 0.091553 | -0.07782 | 0.13733 | 0.28381 | 0.2243 | 0.33875 | -0.018311 | 0.24261 | 11.0458 | -110.3027 | 110.2112 | -11.5311 | 110.1654 | 110.3577 | -11.2289 | -0.22888 | -0.40741 | -0.045776 | 110.0555 | 110.3165 | 110.2982 | 109.996 | 110.1654 | 121.1197 | 110.4126 | -0.22888 | 109.996 | 110.1654 | 110.4126 | 110.2982 | 121.1197 | -11.3159 | -121.756
898.7812 | 121.8018 | -114.4547 | 7.0175 | -0.0082398 | 0.0075965 | 0.0028626 | 0.75394 | -0.0066821 | -0.0010148 | 0.70665 | 0.10986 | -0.064087 | 0.13275 | 0.27008 | 0.21973 | 0.32044 | -0.018311 | 0.21057 | 6.9077 | -114.5966 | 114.5874 | -7.0816 | 114.5645 | 114.7247 | -6.7978 | -0.14191 | -0.10986 | -0.022888 | 114.4363 | 114.6652 | 114.6744 | 114.3906 | 114.5645 | 121.3623 | 114.7751 | -0.14191 | 114.3906 | 114.5645 | 114.7751 | 114.6744 | 121.3623 | -6.8848 | -121.6141
899.7812 | 121.843 | -121.0419 | 0.48981 | 0.0070192 | 0.010587 | 0.00093996 | 0.060094 | -0.0081775 | -0.003151 | 0.049332 | 0.1236 | -0.068665 | 0.14648 | 0.31586 | 0.26093 | 0.37079 | -0.022888 | 0.24719 | 0.4715 | -121.2524 | 121.1884 | -0.55847 | 121.1655 | 121.3577 | -0.22888 | -0.21057 | -0.01831 | -0.022888 | 121.019 | 121.2891 | 121.3028 | 120.9732 | 121.1655 | 121.5134 | 121.4127 | -0.21057 | 120.9732 | 121.1655 | 121.4127 | 121.3028 | 121.5134 | -0.34332 | -121.7422
900.7812 | 121.8338 | -120.9915 | 0.49896 | -0.015869 | 0.012937 | 0.0045716 | 0.080389 | -0.0096729 | -0.0061416 | 0.038651 | 0.14648 | -0.050354 | 0.14191 | 0.32044 | 0.27466 | 0.37537 | -0.041199 | 0.2655 | 0.47607 | -121.3074 | 121.1334 | -0.54932 | 121.138 | 121.312 | -0.2243 | -0.31586 | -0.022888 | 0.004577 | 120.9503 | 121.257 | 121.2662 | 120.9412 | 121.138 | 121.4676 | 121.3669 | -0.31586 | 120.9412 | 121.138 | 121.3669 | 121.2662 | 121.4676 | -0.35706 | -121.8063
901.7812 | 121.875 | -118.4692 | 3.1265 | -0.015869 | 0.011228 | 0.0013672 | 0.29401 | -0.0064685 | -0.003151 | 0.27342 | 0.12817 | -0.073242 | 0.14648 | 0.32501 | 0.27924 | 0.37079 | -0.045776 | 0.2655 | 2.9846 | -118.6661 | 118.6157 | -3.1998 | 118.5974 | 118.7943 | -2.8473 | -0.19684 | -0.14191 | -0.01831 | 118.4235 | 118.7347 | 118.7485 | 118.396 | 118.5974 | 121.4539 | 118.84 | -0.19684 | 118.396 | 118.5974 | 118.84 | 118.7485 | 121.4539 | -2.98 | -121.7926
902.7812 | 121.8567 | -121.0648 | 0.54474 | -0.0082398 | 0.010801 | 0.005426 | 0.057104 | -0.0083911 | -0.0050736 | 0.031815 | 0.073242 | -0.036621 | 0.10529 | 0.31586 | 0.25635 | 0.35248 | 0.009155 | 0.25635 | 0.44403 | -121.3028 | 121.17 | -0.58136 | 121.138 | 121.3806 | -0.28839 | -0.23804 | -0.10071 | -0.032044 | 121.0739 | 121.3211 | 121.3211 | 121.0281 | 121.138 | 121.5088 | 121.4172 | -0.23804 | 121.0281 | 121.138 | 121.4172 | 121.3211 | 121.5088 | -0.43945 | -121.8475
903.7812 | 121.7789 | -120.8908 | 0.71411 | -0.015869 | 0.013578 | 0.004358 | 0.066289 | -0.0062549 | -0.0035782 | 0.042069 | 0.041199 | -0.045776 | 0.11444 | 0.26093 | 0.21973 | 0.32501 | 0.059509 | 0.20142 | 0.59509 | -121.1472 | 121.0052 | -0.75989 | 120.932 | 121.1517 | -0.49438 | -0.25635 | -0.11902 | -0.073242 | 120.9503 | 121.0922 | 121.1105 | 120.845 | 120.932 | 121.4859 | 121.2158 | -0.25635 | 120.845 | 120.932 | 121.2158 | 121.1105 | 121.4859 | -0.59967 | -121.8613
904.7812 | 121.9162 | -120.0989 | 1.5747 | -0.00061033 | 0.013151 | 0.00072636 | 0.15238 | -0.0058277 | -0.0057144 | 0.1068 | 0.13275 | -0.054932 | 0.14648 | 0.32501 | 0.28381 | 0.39825 | -0.041199 | 0.28381 | 1.5106 | -120.2316 | 120.2454 | -1.6296 | 120.2316 | 120.4239 | -1.2909 | -0.13275 | -0.064087 | -0.013733 | 120.0577 | 120.3827 | 120.3827 | 120.0439 | 120.2316 | 121.6095 | 120.4971 | -0.13275 | 120.0439 | 120.2316 | 120.4971 | 120.3827 | 121.6095 | -1.4282 | -121.8063
905.7812 | 121.907 | -118.6844 | 2.829 | -0.00061033 | 0.014432 | 0.0017944 | 0.29743 | -0.0049731 | -0.0033646 | 0.23582 | 0.068665 | -0.013733 | 0.11902 | 0.28381 | 0.22888 | 0.33417 | 0.022888 | 0.21515 | 2.7374 | -118.9453 | 118.8034 | -2.8427 | 118.7531 | 118.9682 | -2.6001 | -0.26093 | -0.091552 | -0.050354 | 118.7073 | 118.8995 | 118.9133 | 118.6707 | 118.7531 | 121.4218 | 119.0186 | -0.26093 | 118.6707 | 118.7531 | 119.0186 | 118.9133 | 121.4218 | -2.71 | -121.7743
906.7812 | 121.9528 | -120.9869 | 0.64087 | -0.0082398 | 0.013578 | 0.004358 | 0.10431 | -0.0047595 | -0.004219 | 0.072831 | 0.11902 | -0.059509 | 0.12817 | 0.32044 | 0.27008 | 0.37994 | -0.027466 | 0.25635 | 0.737 | -121.2296 | 121.1151 | -0.70038 | 121.106 | 121.3074 | -0.37079 | -0.24262 | 0.096131 | -0.009155 | 120.9595 | 121.2433 | 121.257 | 120.9274 | 121.106 | 121.7239 | 121.3669 | -0.24262 | 120.9274 | 121.106 | 121.3669 | 121.257 | 121.7239 | -0.5127 | -121.8704
907.7812 | 121.8246 | -118.2312 | 3.4424 | -0.00061033 | 0.014219 | 0.004358 | 0.35895 | -0.0043323 | -0.0020828 | 0.32811 | 0.027466 | -0.018311 | 0.10071 | 0.21057 | 0.16022 | 0.25177 | 0.10529 | 0.13275 | 3.3829 | -118.4052 | 118.3319 | -3.4607 | 118.2587 | 118.4418 | -3.2822 | -0.17395 | -0.059509 | -0.073242 | 118.3365 | 118.364 | 118.3914 | 118.2129 | 118.2587 | 121.6141 | 118.483 | -0.17395 | 118.2129 | 118.2587 | 118.483 | 118.3914 | 121.6141 | -3.3417 | -121.8475
908.7812 | 121.8658 | -121.0876 | 0.50812 | -0.0082398 | 0.015287 | 0.0047852 | 0.058599 | -0.0071093 | -0.004219 | 0.033951 | 0.064087 | -0.022888 | 0.11902 | 0.24261 | 0.21973 | 0.31128 | 0.050354 | 0.21057 | 0.42114 | -121.3669 | 121.2067 | -0.53101 | 121.1517 | 121.3303 | -0.28839 | -0.27924 | -0.086975 | -0.054932 | 121.138 | 121.2982 | 121.3074 | 121.0648 | 121.1517 | 121.5088 | 121.3989 | -0.27924 | 121.0648 | 121.1517 | 121.3989 | 121.3074 | 121.5088 | -0.3891 | -121.875
909.7812 | 121.7743 | -121.1243 | 0.49439 | -0.00061033 | 0.016569 | 0.0039306 | 0.056676 | -0.0041187 | -0.0055008 | 0.033097 | 0.022888 | -0.022888 | 0.10529 | 0.1831 | 0.14648 | 0.24261 | 0.15106 | 0.11444 | 0.46692 | -121.3943 | 121.2296 | -0.51727 | 121.1472 | 121.3074 | -0.3479 | -0.27008 | -0.027466 | -0.082398 | 121.2753 | 121.2387 | 121.2708 | 121.1014 | 121.1472 | 121.5912 | 121.3669 | -0.27008 | 121.1014 | 121.1472 | 121.3669 | 121.2708 | 121.5912 | -0.3891 | -121.8887
910.7812 | 121.8109 | -114.5508 | 6.9946 | 0.0070192 | 0.013151 | 0.006067 | 0.81717 | -0.0036915 | 0.00090784 | 0.79915 | 0.07782 | -0.050354 | 0.10529 | 0.24719 | 0.21515 | 0.32044 | 0 | 0.21515 | 6.8253 | -114.6973 | 114.6561 | -7.045 | 114.6286 | 114.798 | -6.7795 | -0.14648 | -0.16937 | -0.027466 | 114.5508 | 114.7659 | 114.7659 | 114.5004 | 114.6286 | 121.376 | 114.8712 | -0.14648 | 114.5004 | 114.6286 | 114.8712 | 114.7659 | 121.376 | -6.8893 | -121.6919
911.7969 | 121.8018 | -119.4809 | 2.1973 | -0.0082398 | 0.011228 | 0.0039306 | 0.20109 | -0.0036915 | -0.003151 | 0.18114 | 0.091553 | -0.032043 | 0.091553 | 0.27008 | 0.21973 | 0.29297 | 0.13733 | 0.19684 | 2.1698 | -119.6548 | 119.5724 | -2.2293 | 119.5724 | 119.751 | -1.9775 | -0.17395 | -0.027466 | 0 | 119.6182 | 119.6777 | 119.7006 | 119.4489 | 119.5724 | 121.6507 | 119.7739 | -0.17395 | 119.4489 | 119.5724 | 119.7739 | 119.7006 | 121.6507 | -2.1057 | -121.8521
912.7812 | 121.7697 | -112.3535 | 9.1965 | -0.0082398 | 0.015928 | 0.007135 | 1.3525 | 0.0012219 | -0.0012284 | 1.3018 | 0.009155 | -0.009155 | 0.082397 | 0.16479 | 0.15106 | 0.25177 | 0.12817 | 0.10529 | 9.1278 | -112.5458 | 112.4359 | -9.2056 | 112.3627 | 112.5183 | -9.0454 | -0.19226 | -0.068664 | -0.073242 | 112.4817 | 112.4588 | 112.5046 | 112.3444 | 112.3627 | 121.4813 | 112.6053 | -0.19226 | 112.3444 | 112.3627 | 112.6053 | 112.5046 | 121.4813 | -9.1141 | -121.7422
913.7812 | 120.3003 | -20.7413 | 97.5632 | -0.0082398 | 0.015928 | 0.007135 | 0.14277 | 0.056123 | 0.055809 | 0.26402 | 0.027466 | -0.10071 | 0.050354 | -0.022888 | -0.073242 | 0.11444 | -0.22888 | -0.032043 | 101.1063 | -20.1965 | 20.7916 | -97.6639 | 20.7687 | 20.7184 | -97.6364 | 0.54474 | 3.5431 | -0.022888 | 20.5124 | 20.7092 | 20.668 | 20.6406 | 20.7687 | 121.8475 | 20.8557 | 0.54474 | 20.6406 | 20.7687 | 20.8557 | 20.668 | 121.8475 | -97.5128 | -117.7597
914.7812 | 120.6024 | -18.2327 | 81.4133 | -0.0082398 | 0.015928 | 0.0017944 | 0.3079 | 0.050996 | 0.051109 | 0.44988 | -0.032043 | -0.059509 | 0.16022 | -0.073242 | -0.1236 | -0.018311 | -0.086975 | -0.15564 | 100.6851 | -22.0139 | 18.3929 | -81.4728 | 18.2007 | 18.1595 | -81.5369 | -3.7811 | 19.2719 | -0.19226 | 18.1458 | 18.0771 | 18.1091 | 18.1732 | 18.2007 | 118.9178 | 18.2144 | -3.7811 | 18.1732 | 18.2007 | 18.2144 | 18.1091 | 118.9178 | -81.2531 | -103.4271
915.7812 | 120.7535 | -7.1457 | 92.6514 | -0.00061033 | 0.015714 | 0.0017944 | 0.21561 | 0.056764 | 0.057732 | 0.34306 | -0.041199 | -0.045776 | 0.041199 | -0.09613 | -0.1236 | -0.050354 | -0.14648 | -0.16937 | 113.7085 | -7.695 | 7.1869 | -92.6971 | 7.1045 | 7.0496 | -92.775 | -0.54932 | 21.0571 | -0.082398 | 6.9992 | 6.9763 | 7.0221 | 7.0999 | 7.1045 | 120.8542 | 7.0953 | -0.54932 | 7.0999 | 7.1045 | 7.0953 | 7.0221 | 120.8542 | -92.6102 | -100.3464
916.7812 | 121.6095 | -5.7175 | 112.4863 | -0.00061033 | 0.012937 | 0.005426 | 0.30619 | 0.058473 | 0.060081 | 0.44881 | 0.059509 | -0.13275 | 0.082397 | 0.041199 | -0.013733 | 0.073242 | -0.33417 | -0.027466 | 115.5899 | -5.7404 | 5.7999 | -112.619 | 5.777 | 5.7587 | -112.5 | -0.022888 | 3.1036 | -0.022888 | 5.3833 | 5.69 | 5.7037 | 5.5847 | 5.777 | 121.3074 | 5.7907 | -0.022888 | 5.5847 | 5.777 | 5.7907 | 5.7037 | 121.3074 | -112.4039 | -118.2266
917.7812 | 120.5841 | -3.566 | 92.2989 | 0.0070192 | 0.015073 | 0.005426 | 0.11243 | 0.058046 | 0.058372 | 0.27171 | -0.041199 | -0.073242 | 0.041199 | -0.091553 | -0.15564 | -0.073242 | -0.13275 | -0.18768 | 117.5903 | -3.8773 | 3.6072 | -92.3721 | 3.5248 | 3.4744 | -92.4545 | -0.31128 | 25.2914 | -0.082398 | 3.4332 | 3.3783 | 3.4103 | 3.4927 | 3.5248 | 121.1563 | 3.4927 | -0.31128 | 3.4927 | 3.5248 | 3.4927 | 3.4103 | 121.1563 | -92.2577 | -96.1761
918.7812 | 121.2387 | -7.1457 | 95.4025 | -0.0082398 | 0.016141 | 0.0058534 | 0.1402 | 0.058046 | 0.058372 | 0.27535 | -0.027466 | -0.082397 | 0.054932 | -0.10529 | -0.15106 | -0.064087 | -0.15106 | -0.1831 | 113.9053 | -7.4799 | 7.2006 | -95.4849 | 7.1182 | 7.0404 | -95.5536 | -0.33417 | 18.5028 | -0.082398 | 6.9946 | 6.9626 | 6.9946 | 7.0633 | 7.1182 | 121.051 | 7.0816 | -0.33417 | 7.0633 | 7.1182 | 7.0816 | 6.9946 | 121.051 | -95.3476 | -102.8824
919.7812 | 121.4951 | -120.488 | 0.16479 | -0.00061033 | 0.015287 | 0.004358 | 0.048345 | -0.0030505 | -0.0052872 | 0.024124 | 0.045776 | -0.022888 | 0.11444 | 0.19226 | 0.15564 | 0.22888 | 0.13275 | 0.13275 | 0.79193 | -120.8359 | 120.6024 | -0.18768 | 120.5338 | 120.6802 | -0.009155 | -0.3479 | 0.62714 | -0.068665 | 120.6207 | 120.6207 | 120.6436 | 120.4651 | 120.5338 | 121.2799 | 120.7169 | -0.3479 | 120.4651 | 120.5338 | 120.7169 | 120.6436 | 121.2799 | -0.050354 | -121.0007
920.7812 | 121.5042 | -98.3643 | 22.316 | -0.0082398 | 0.017423 | 0.0049988 | 0.70267 | 0.0061353 | 0.0068894 | 0.68828 | 0.027466 | -0.018311 | 0.086975 | 0.10986 | 0.050354 | 0.15564 | 0.068665 | 0.041199 | 22.0551 | -99.1653 | 98.4512 | -22.3343 | 98.3917 | 98.4741 | -22.2656 | -0.80109 | -0.26093 | -0.059509 | 98.4329 | 98.4055 | 98.4146 | 98.3459 | 98.3917 | 120.4193 | 98.5199 | -0.80109 | 98.3459 | 98.3917 | 98.5199 | 98.4146 | 120.4193 | -22.229 | -121.4813
921.7812 | 121.6553 | -115.7547 | 5.5756 | -0.0082398 | 0.013578 | 0.002008 | 0.2468 | -0.0021961 | -0.003151 | 0.23967 | 0.11902 | -0.059509 | 0.15564 | 0.2655 | 0.24261 | 0.35248 | -0.073242 | 0.24261 | 5.2689 | -116.0568 | 115.9103 | -5.6351 | 115.8737 | 116.0202 | -5.3329 | -0.30212 | -0.3067 | -0.036621 | 115.6815 | 115.9973 | 115.9973 | 115.6952 | 115.8737 | 121.0236 | 116.1072 | -0.30212 | 115.6952 | 115.8737 | 116.1072 | 115.9973 | 121.0236 | -5.4199 | -121.6324
922.7969 | 121.5866 | -120.6528 | 0.81482 | -0.0082398 | 0.011869 | 0.0075622 | 0.054967 | -0.0088183 | -0.004219 | 0.030747 | 0 | -0.009155 | 0.09613 | 0.19226 | 0.15564 | 0.22888 | 0.1831 | 0.15106 | 0.73242 | -120.9 | 120.7489 | -0.82397 | 120.6528 | 120.845 | -0.65918 | -0.24719 | -0.082397 | -0.09613 | 120.8359 | 120.8038 | 120.8084 | 120.6436 | 120.6528 | 121.3852 | 120.8817 | -0.24719 | 120.6436 | 120.6528 | 120.8817 | 120.8084 | 121.3852 | -0.71869 | -121.7148
923.7812 | 121.6507 | -120.2682 | 1.1536 | -0.0082398 | 0.016355 | 0.0047852 | 0.097478 | -0.0039051 | -0.0037918 | 0.068985 | 0.091553 | 0 | 0.11444 | 0.25635 | 0.19684 | 0.27924 | 0.11902 | 0.20599 | 1.0162 | -120.6024 | 120.3827 | -1.1536 | 120.3598 | 120.5246 | -0.95673 | -0.33417 | -0.13733 | -0.022888 | 120.3873 | 120.4742 | 120.4651 | 120.2682 | 120.3598 | 121.2845 | 120.5475 | -0.33417 | 120.2682 | 120.3598 | 120.5475 | 120.4651 | 121.2845 | -1.0391 | -121.756
924.7812 | 121.3074 | -120.575 | 0.56305 | 0.0070192 | 0.017423 | 0.007776 | 0.058599 | -0.0056141 | -0.0050736 | 0.023911 | 0.068665 | -0.004578 | 0.10986 | 0.20599 | 0.1831 | 0.26093 | 0.15564 | 0.16022 | 0.54474 | -121.1746 | 120.6848 | -0.56763 | 120.6436 | 120.7809 | -0.37994 | -0.59967 | -0.01831 | -0.041198 | 120.7306 | 120.7352 | 120.7581 | 120.5704 | 120.6436 | 121.1197 | 120.8359 | -0.59967 | 120.5704 | 120.6436 | 120.8359 | 120.7581 | 121.1197 | -0.45319 | -121.7377
925.7812 | 121.6095 | -119.5404 | 1.3733 | -0.015869 | 0.015073 | 0.0067078 | 0.1402 | -0.0045459 | -0.0044328 | 0.11107 | 0.013733 | 0.009155 | 0.09613 | 0.17853 | 0.14648 | 0.24719 | 0.20142 | 0.11444 | 1.5289 | -120.369 | 119.6365 | -1.3641 | 119.5541 | 119.7189 | -1.2268 | -0.82855 | 0.15564 | -0.082397 | 119.7418 | 119.6548 | 119.6869 | 119.5496 | 119.5541 | 121.0693 | 119.7876 | -0.82855 | 119.5496 | 119.5541 | 119.7876 | 119.6869 | 121.0693 | -1.2772 | -121.7422
926.7969 | 121.7102 | -120.9503 | 0.56305 | -0.00061033 | 0.010587 | 8.5364e-05 | 0.045568 | -0.0041187 | -0.005928 | 0.02562 | 0.059509 | -0.054932 | 0.13733 | 0.27008 | 0.24261 | 0.36163 | 0.086975 | 0.25177 | 0.44403 | -121.1517 | 121.0876 | -0.61798 | 121.0098 | 121.2204 | -0.32043 | -0.20142 | -0.11902 | -0.07782 | 121.0373 | 121.2021 | 121.1929 | 120.8954 | 121.0098 | 121.3943 | 121.3119 | -0.20142 | 120.8954 | 121.0098 | 121.3119 | 121.1929 | 121.3943 | -0.42572 | -121.7148
927.7812 | 121.669 | -120.5109 | 0.49439 | -0.023499 | 0.017423 | 0.0011536 | 0.055608 | -0.0066821 | -0.0035782 | 0.031174 | 0.07782 | -0.013733 | 0.10986 | 0.27466 | 0.2243 | 0.31128 | 0.16479 | 0.22888 | 0.5127 | -121.2479 | 120.6207 | -0.50812 | 120.5887 | 120.7855 | -0.27008 | -0.737 | 0.01831 | -0.032043 | 120.6757 | 120.7397 | 120.7352 | 120.4971 | 120.5887 | 121.0236 | 120.8221 | -0.737 | 120.4971 | 120.5887 | 120.8221 | 120.7352 | 121.0236 | -0.38452 | -121.7422
928.7812 | 121.5912 | -120.7672 | 0.75073 | -0.015869 | 0.018064 | 0.0017944 | 0.072912 | -0.0036915 | -0.0029374 | 0.028183 | 0.036621 | -0.004578 | 0.091553 | 0.21515 | 0.16937 | 0.2655 | 0.20142 | 0.15564 | 0.7782 | -121.0098 | 120.8588 | -0.75531 | 120.8038 | 120.9824 | -0.58136 | -0.24262 | 0.027466 | -0.054932 | 120.9686 | 120.9229 | 120.9366 | 120.7626 | 120.8038 | 121.5454 | 121.0327 | -0.24262 | 120.7626 | 120.8038 | 121.0327 | 120.9366 | 121.5454 | -0.65918 | -121.7606
929.7812 | 121.582 | -120.5017 | 0.91095 | -0.00061033 | 0.016782 | 0.0064942 | 0.053472 | -0.0049731 | -0.0040054 | 0.029465 | 0.036621 | -0.013733 | 0.09613 | 0.23346 | 0.19226 | 0.28381 | 0.21057 | 0.18768 | 0.87891 | -120.8405 | 120.5978 | -0.92468 | 120.5383 | 120.7352 | -0.71869 | -0.33874 | -0.032044 | -0.059509 | 120.7123 | 120.6894 | 120.694 | 120.488 | 120.5383 | 121.3806 | 120.7855 | -0.33874 | 120.488 | 120.5383 | 120.7855 | 120.694 | 121.3806 | -0.81482 | -121.7514
930.7812 | 121.6507 | -120.6436 | 0.80566 | -0.00061033 | 0.015714 | 0.0073486 | 0.14341 | -0.0043323 | -0.00486 | 0.12025 | 0.082397 | -0.018311 | 0.10071 | 0.31128 | 0.25177 | 0.3479 | 0.17853 | 0.24261 | 0.98877 | -120.8908 | 120.7443 | -0.82398 | 120.726 | 120.9549 | -0.55389 | -0.24719 | 0.18311 | -0.018311 | 120.8221 | 120.8862 | 120.8954 | 120.6253 | 120.726 | 121.6324 | 120.9915 | -0.24719 | 120.6253 | 120.726 | 120.9915 | 120.8954 | 121.6324 | -0.70496 | -121.6965
931.7812 | 121.756 | -120.5841 | 0.92468 | -0.0082398 | 0.011442 | 0.00093996 | 0.063299 | -0.0068957 | -0.00486 | 0.044419 | 0.11902 | -0.045776 | 0.14191 | 0.34332 | 0.31128 | 0.39825 | 0.12817 | 0.34332 | 0.80109 | -120.8862 | 120.726 | -0.97046 | 120.7031 | 120.9274 | -0.6134 | -0.30212 | -0.1236 | -0.022888 | 120.7123 | 120.9274 | 120.8954 | 120.5383 | 120.7031 | 121.3852 | 120.9824 | -0.30212 | 120.5383 | 120.7031 | 120.9824 | 120.8954 | 121.3852 | -0.78278 | -121.8109
932.7812 | 121.6324 | -120.2042 | 1.3687 | -0.0082398 | 0.016355 | 0.0058534 | 0.12739 | -0.0054003 | -0.0046464 | 0.10295 | 0.018311 | 0 | 0.10529 | 0.2243 | 0.16937 | 0.27008 | 0.19684 | 0.16022 | 1.2543 | -120.4834 | 120.3094 | -1.3687 | 120.2225 | 120.4285 | -1.1993 | -0.27923 | -0.11444 | -0.086975 | 120.401 | 120.3644 | 120.3735 | 120.2042 | 120.2225 | 121.4584 | 120.4742 | -0.27923 | 120.2042 | 120.2225 | 120.4742 | 120.3735 | 121.4584 | -1.2634 | -121.8521
933.7812 | 121.5866 | -120.0943 | 1.5015 | -0.0082398 | 0.01785 | 0.0039306 | 0.097692 | -0.0045459 | -0.0063554 | 0.086716 | 0.068665 | -0.009155 | 0.10071 | 0.24719 | 0.20142 | 0.28381 | 0.19684 | 0.18768 | 1.0757 | -120.4102 | 120.195 | -1.5106 | 120.163 | 120.3415 | -1.3 | -0.31586 | -0.42572 | -0.032043 | 120.2911 | 120.282 | 120.2957 | 120.0851 | 120.163 | 121.17 | 120.3781 | -0.31586 | 120.0851 | 120.163 | 120.3781 | 120.2957 | 121.17 | -1.4008 | -121.9116
934.7812 | 121.6736 | -121.019 | 0.46692 | -0.00061033 | 0.015928 | 0.0035034 | 0.044286 | -0.0049731 | -0.0040054 | 0.019852 | 0.022888 | 0 | 0.073242 | 0.20599 | 0.17395 | 0.27466 | 0.21057 | 0.17395 | 0.37079 | -121.3806 | 121.0922 | -0.46692 | 121.0419 | 121.225 | -0.29297 | -0.36163 | -0.09613 | -0.050354 | 121.2296 | 121.1929 | 121.1929 | 121.019 | 121.0419 | 121.3898 | 121.2936 | -0.36163 | 121.019 | 121.0419 | 121.2936 | 121.1929 | 121.3898 | -0.39368 | -121.8475
935.7812 | 121.6919 | -119.9341 | 1.6342 | -0.015869 | 0.015287 | 0.0049988 | 0.1073 | -0.0028369 | -0.0046464 | 0.085862 | 0.009155 | 0 | 0.09613 | 0.2243 | 0.18768 | 0.25177 | 0.21515 | 0.15106 | 1.561 | -120.1767 | 120.0302 | -1.6342 | 119.9432 | 120.1584 | -1.4465 | -0.24262 | -0.073242 | -0.086975 | 120.1492 | 120.0851 | 120.1218 | 119.9341 | 119.9432 | 121.4951 | 120.1859 | -0.24262 | 119.9341 | 119.9432 | 120.1859 | 120.1218 | 121.4951 | -1.5381 | -121.8109
936.7812 | 121.7331 | -120.8221 | 0.71411 | -0.0082398 | 0.013578 | 0.0030762 | 0.038946 | -0.0041187 | -0.0037918 | 0.015366 | 0.036621 | -0.027466 | 0.09613 | 0.27466 | 0.25177 | 0.33417 | 0.11444 | 0.23804 | 0.64087 | -121.1243 | 120.9183 | -0.74158 | 120.8588 | 121.0968 | -0.46234 | -0.30212 | -0.073242 | -0.059509 | 120.9366 | 121.0602 | 121.0739 | 120.7947 | 120.8588 | 121.463 | 121.1563 | -0.30212 | 120.7947 | 120.8588 | 121.1563 | 121.0739 | 121.463 | -0.61798 | -121.8384
937.7812 | 121.7102 | -120.7123 | 0.90179 | -0.00061033 | 0.016782 | 0.0030762 | 0.048772 | -0.0039051 | -0.0027238 | 0.021561 | 0.073242 | -0.027466 | 0.11444 | 0.28381 | 0.24261 | 0.32959 | 0.20142 | 0.2243 | 0.84228 | -120.9686 | 120.8267 | -0.92926 | 120.7855 | 120.9961 | -0.65918 | -0.25635 | -0.059509 | -0.041199 | 120.9137 | 120.9366 | 120.9549 | 120.6848 | 120.7855 | 121.5546 | 121.0419 | -0.25635 | 120.6848 | 120.7855 | 121.0419 | 120.9549 | 121.5546 | -0.78735 | -121.8704
938.7812 | 121.701 | -120.3964 | 1.1124 | 0.0070192 | 0.015287 | 0.0039306 | 0.034673 | -0.0045459 | -0.0050736 | 0.010025 | 0.036621 | 0 | 0.10071 | 0.23346 | 0.20142 | 0.28381 | 0.23346 | 0.17395 | 1.0162 | -120.7535 | 120.4971 | -1.1124 | 120.433 | 120.6299 | -0.91095 | -0.35706 | -0.096131 | -0.064087 | 120.6299 | 120.5704 | 120.5978 | 120.3964 | 120.433 | 121.4127 | 120.6802 | -0.35706 | 120.3964 | 120.433 | 120.6802 | 120.5978 | 121.4127 | -1.0117 | -121.8658
939.7812 | 121.6827 | -120.9 | 0.75531 | -0.0082398 | 0.015287 | 0.0056396 | 0.038305 | -0.0060413 | -0.0037918 | 0.011948 | 0.022888 | 0.004578 | 0.086975 | 0.22888 | 0.21057 | 0.3067 | 0.21057 | 0.17395 | 0.70038 | -121.1288 | 120.9869 | -0.75073 | 120.9229 | 121.1288 | -0.54474 | -0.22888 | -0.054932 | -0.064087 | 121.1105 | 121.0739 | 121.1105 | 120.9045 | 120.9229 | 121.6003 | 121.2067 | -0.22888 | 120.9045 | 120.9229 | 121.2067 | 121.1105 | 121.6003 | -0.66834 | -121.8842
940.7812 | 121.6965 | -121.0602 | 0.60425 | -0.00061033 | 0.016569 | 0.0058534 | 0.052831 | -0.0047595 | -0.0055008 | 0.025406 | 0.027466 | -0.013733 | 0.09613 | 0.23804 | 0.19684 | 0.28839 | 0.21057 | 0.1831 | 0.51727 | -121.2982 | 121.1563 | -0.61798 | 121.0876 | 121.2982 | -0.40741 | -0.23804 | -0.086975 | -0.068664 | 121.2708 | 121.2433 | 121.257 | 121.0464 | 121.0876 | 121.5775 | 121.3486 | -0.23804 | 121.0464 | 121.0876 | 121.3486 | 121.257 | 121.5775 | -0.50812 | -121.9025
941.7812 | 121.701 | -121.1426 | 0.49896 | -0.0082398 | 0.016141 | 0.006067 | 0.041296 | -0.0047595 | -0.0046464 | 0.01558 | 0.009155 | -0.004578 | 0.10529 | 0.24261 | 0.20142 | 0.29755 | 0.21973 | 0.19226 | 0.39825 | -121.4218 | 121.2479 | -0.50354 | 121.1517 | 121.3852 | -0.29755 | -0.27924 | -0.10071 | -0.096131 | 121.3623 | 121.3348 | 121.344 | 121.138 | 121.1517 | 121.5408 | 121.4401 | -0.27924 | 121.138 | 121.1517 | 121.4401 | 121.344 | 121.5408 | -0.39368 | -121.9208
942.7812 | 121.7422 | -121.106 | 0.52185 | -0.0082398 | 0.014005 | 0.0032898 | 0.041296 | -0.0045459 | -0.0035782 | 0.014939 | 0.009155 | -0.004578 | 0.11444 | 0.24719 | 0.21057 | 0.29297 | 0.21057 | 0.19226 | 0.4715 | -121.4172 | 121.2204 | -0.52643 | 121.1151 | 121.3531 | -0.31128 | -0.31128 | -0.050354 | -0.10529 | 121.3165 | 121.2982 | 121.3165 | 121.1014 | 121.1151 | 121.5775 | 121.3989 | -0.31128 | 121.1014 | 121.1151 | 121.3989 | 121.3165 | 121.5775 | -0.40741 | -121.9391
943.7812 | 121.7285 | -120.9869 | 0.55847 | -0.015869 | 0.015714 | 0.0052124 | 0.046209 | -0.0045459 | -0.0040054 | 0.019425 | 0.059509 | 0.009155 | 0.10071 | 0.27008 | 0.24719 | 0.31586 | 0.20599 | 0.21515 | 0.48981 | -121.3852 | 121.0876 | -0.54932 | 121.0464 | 121.257 | -0.31128 | -0.39826 | -0.068665 | -0.041199 | 121.1929 | 121.2021 | 121.2341 | 120.9961 | 121.0464 | 121.4767 | 121.3028 | -0.39826 | 120.9961 | 121.0464 | 121.3028 | 121.2341 | 121.4767 | -0.45776 | -121.9437
944.7812 | 121.7606 | -118.8171 | 2.2018 | -0.00061033 | 0.0155 | 0.002649 | 0.19809 | -0.0030505 | -0.0040054 | 0.17815 | 0.07782 | -0.009155 | 0.11444 | 0.27924 | 0.2243 | 0.31128 | 0.18768 | 0.21973 | 2.0782 | -119.6869 | 118.9316 | -2.211 | 118.895 | 119.0964 | -1.9775 | -0.86975 | -0.1236 | -0.036621 | 119.0048 | 119.0369 | 119.0414 | 118.808 | 118.895 | 120.8954 | 119.1284 | -0.86975 | 118.808 | 118.895 | 119.1284 | 119.0414 | 120.8954 | -2.0874 | -121.8887
945.7812 | 121.7651 | -120.4742 | 0.65002 | -0.0082398 | 0.016141 | 0.0069214 | 0.056676 | -0.0021961 | -0.0050736 | 0.024765 | 0.032043 | -0.009155 | 0.10071 | 0.23804 | 0.20142 | 0.27008 | 0.2243 | 0.17395 | 0.52643 | -121.3348 | 120.575 | -0.65918 | 120.5063 | 120.7123 | -0.44861 | -0.8606 | -0.1236 | -0.068665 | 120.6985 | 120.6482 | 120.6757 | 120.4651 | 120.5063 | 121.0007 | 120.7443 | -0.8606 | 120.4651 | 120.5063 | 120.7443 | 120.6757 | 121.0007 | -0.54932 | -121.9849
946.7812 | 121.7285 | -119.7693 | 1.3504 | -0.0082398 | 0.016782 | 0.0075622 | 0.17075 | -0.0034777 | -0.0035782 | 0.14653 | 0.027466 | -0.009155 | 0.086975 | 0.23346 | 0.20142 | 0.29755 | 0.21515 | 0.17853 | 1.2497 | -120.5933 | 119.8563 | -1.3596 | 119.7968 | 120.0027 | -1.149 | -0.82397 | -0.10071 | -0.059509 | 119.9844 | 119.9478 | 119.9707 | 119.7601 | 119.7968 | 121.019 | 120.0668 | -0.82397 | 119.7601 | 119.7968 | 120.0668 | 119.9707 | 121.019 | -1.2634 | -121.9437
947.7812 | 121.7422 | -119.7189 | 1.3275 | -0.0082398 | 0.018705 | 0.0056396 | 0.20151 | -0.0054003 | -0.0044328 | 0.17452 | 0.036621 | -0.013733 | 0.10071 | 0.26093 | 0.21057 | 0.29755 | 0.21057 | 0.18768 | 1.2314 | -120.6162 | 119.8196 | -1.3412 | 119.7556 | 119.9799 | -1.1169 | -0.89722 | -0.096131 | -0.064087 | 119.9295 | 119.9066 | 119.9295 | 119.7052 | 119.7556 | 120.9503 | 120.0165 | -0.89722 | 119.7052 | 119.7556 | 120.0165 | 119.9295 | 120.9503 | -1.2268 | -121.9437
948.7812 | 121.7331 | -120.6757 | 0.62256 | -0.023499 | 0.016141 | 0.0049988 | 0.059881 | -0.0054003 | -0.0046464 | 0.036301 | 0.013733 | -0.013733 | 0.091553 | 0.23804 | 0.19684 | 0.29297 | 0.2243 | 0.1831 | 0.54474 | -121.3394 | 120.7672 | -0.63629 | 120.6894 | 120.9137 | -0.42572 | -0.66376 | -0.07782 | -0.07782 | 120.9 | 120.8588 | 120.8725 | 120.6619 | 120.6894 | 121.2204 | 120.9686 | -0.66376 | 120.6619 | 120.6894 | 120.9686 | 120.8725 | 121.2204 | -0.53101 | -121.962
949.7812 | 121.9574 | -120.694 | 0.75531 | -0.0082398 | 0.016141 | 0.00029916 | 0.060735 | -0.0047595 | -0.0046464 | 0.083298 | 0.059509 | -0.009155 | 0.11902 | 0.27008 | 0.23804 | 0.31586 | 0.20599 | 0.21057 | 0.69122 | -121.1197 | 120.813 | -0.76447 | 120.7535 | 120.9641 | -0.51727 | -0.42572 | -0.064087 | -0.05951 | 120.9 | 120.9045 | 120.932 | 120.6848 | 120.7535 | 121.3852 | 121.0098 | -0.42572 | 120.6848 | 120.7535 | 121.0098 | 120.932 | 121.3852 | -0.63629 | -121.875
950.7812 | 121.8063 | -121.1746 | 0.5127 | -0.0082398 | 0.015287 | 0.0013672 | 0.053686 | -0.0051867 | -0.0046464 | 0.026047 | 0.068665 | -0.004578 | 0.10529 | 0.28839 | 0.22888 | 0.31586 | 0.20142 | 0.22888 | 0.45776 | -121.431 | 121.2799 | -0.51727 | 121.2433 | 121.463 | -0.28381 | -0.25635 | -0.054931 | -0.036621 | 121.376 | 121.4035 | 121.4035 | 121.17 | 121.2433 | 121.6324 | 121.4905 | -0.25635 | 121.17 | 121.2433 | 121.4905 | 121.4035 | 121.6324 | -0.40741 | -121.9437
951.7812 | 121.7468 | -120.108 | 1.5564 | -0.0082398 | 0.016996 | 0.0028626 | 0.19831 | -0.0039051 | -0.0027238 | 0.16811 | 0.059509 | -0.009155 | 0.11444 | 0.27466 | 0.23804 | 0.30212 | 0.1831 | 0.2243 | 1.4832 | -120.3598 | 120.2225 | -1.5656 | 120.1675 | 120.3827 | -1.3184 | -0.25177 | -0.073242 | -0.054932 | 120.2911 | 120.3323 | 120.3461 | 120.0989 | 120.1675 | 121.5912 | 120.4102 | -0.25177 | 120.0989 | 120.1675 | 120.4102 | 120.3461 | 121.5912 | -1.442 | -121.9162
952.7812 | 121.7285 | -119.5084 | 2.1561 | -0.015869 | 0.016782 | 0.0069214 | 0.27543 | -0.0036915 | -0.0044328 | 0.2668 | 0.022888 | 0.022888 | 0.10529 | 0.2243 | 0.17853 | 0.25177 | 0.21515 | 0.16937 | 1.9958 | -119.8105 | 119.6136 | -2.1332 | 119.5312 | 119.7327 | -1.9775 | -0.30212 | -0.16022 | -0.082398 | 119.7235 | 119.6777 | 119.6869 | 119.5312 | 119.5312 | 121.5042 | 119.7601 | -0.30212 | 119.5312 | 119.5312 | 119.7601 | 119.6869 | 121.5042 | -2.0508 | -121.9666
953.7812 | 121.8018 | -120.9137 | 0.75989 | -0.0082398 | 0.016569 | 0.004358 | 0.082525 | -0.0043323 | -0.0025102 | 0.06044 | 0.022888 | -0.009155 | 0.082397 | 0.21973 | 0.17853 | 0.28839 | 0.21973 | 0.17853 | 0.68665 | -121.2021 | 120.9961 | -0.76904 | 120.9366 | 121.1334 | -0.58136 | -0.28839 | -0.073242 | -0.059509 | 121.1334 | 121.0922 | 121.0922 | 120.9045 | 120.9366 | 121.6003 | 121.2021 | -0.28839 | 120.9045 | 120.9366 | 121.2021 | 121.0922 | 121.6003 | -0.67749 | -121.962
954.7812 | 121.8384 | -119.4077 | 2.2339 | -0.0082398 | 0.016355 | 0.00051276 | 0.28397 | -0.0024097 | -0.0044328 | 0.26466 | 0.022888 | -0.004578 | 0.09613 | 0.22888 | 0.1831 | 0.2655 | 0.21057 | 0.18768 | 1.9821 | -119.6274 | 119.5038 | -2.2385 | 119.4305 | 119.6365 | -2.0508 | -0.21973 | -0.25177 | -0.073242 | 119.6182 | 119.5953 | 119.5908 | 119.4031 | 119.4305 | 121.3898 | 119.6732 | -0.21973 | 119.4031 | 119.4305 | 119.6732 | 119.5908 | 121.3898 | -2.1378 | -121.8613
955.7812 | 121.1746 | -119.5862 | 1.442 | -0.0082398 | 0.016996 | 0.0041444 | 0.092565 | -0.0032641 | -0.005928 | 0.071335 | 0.027466 | -0.004578 | 0.10071 | 0.14648 | 0.09613 | 0.21057 | 0.13275 | 0.091553 | 1.387 | -119.87 | 119.6869 | -1.4465 | 119.6136 | 119.7327 | -1.3458 | -0.28381 | -0.054932 | -0.073242 | 119.7189 | 119.6777 | 119.6823 | 119.5816 | 119.6136 | 120.9732 | 119.7968 | -0.28381 | 119.5816 | 119.6136 | 119.7968 | 119.6823 | 120.9732 | -1.3412 | -121.312
956.7812 | 121.4401 | -115.8691 | 5.4794 | -0.0082398 | 0.01785 | 0.0030762 | 0.54609 | -0.0013415 | -0.003151 | 0.52806 | 0.032043 | -0.004578 | 0.10529 | 0.16937 | 0.11444 | 0.21515 | 0.14191 | 0.12817 | 5.4565 | -115.9882 | 115.9744 | -5.484 | 115.9012 | 116.0385 | -5.365 | -0.11902 | -0.022888 | -0.073243 | 116.011 | 115.9973 | 115.9836 | 115.8646 | 115.9012 | 121.3257 | 116.0843 | -0.11902 | 115.8646 | 115.9012 | 116.0843 | 115.9836 | 121.3257 | -5.3741 | -121.4676
957.7812 | 121.1105 | -105.3406 | 14.6484 | -0.0082398 | 0.018705 | 0.0049988 | 0.034673 | 0.0042127 | 0.0011214 | 0.025406 | 0.013733 | -0.027466 | 0.091553 | 0.14191 | 0.11902 | 0.18768 | 0.14648 | 0.11902 | 15.3351 | -106.0501 | 105.4321 | -14.6759 | 105.3543 | 105.4825 | -14.5294 | -0.70953 | 0.68665 | -0.07782 | 105.4871 | 105.4596 | 105.4596 | 105.3131 | 105.3543 | 120.6757 | 105.5283 | -0.70953 | 105.3131 | 105.3543 | 105.5283 | 105.4596 | 120.6757 | -14.5569 | -120.6985
958.7812 | 121.376 | -120.5933 | 0.65918 | -0.0082398 | 0.013364 | 0.0075622 | 0.043645 | -0.0045459 | -0.0033646 | 0.020066 | 0.045776 | -0.013733 | 0.10071 | 0.20599 | 0.15564 | 0.24719 | 0.17853 | 0.14191 | 0.60425 | -120.8954 | 120.694 | -0.67291 | 120.639 | 120.7993 | -0.50354 | -0.30212 | -0.054932 | -0.054932 | 120.7718 | 120.7352 | 120.7489 | 120.5795 | 120.639 | 121.1975 | 120.8405 | -0.30212 | 120.5795 | 120.639 | 120.8405 | 120.7489 | 121.1975 | -0.55847 | -121.5546
959.7812 | 121.4584 | -119.7418 | 1.4236 | -0.0082398 | 0.0155 | 0.0082032 | 0.044073 | -0.0043323 | -0.005928 | 0.023484 | 0.045776 | -0.018311 | 0.10071 | 0.20142 | 0.16479 | 0.27924 | 0.14191 | 0.16479 | 1.3916 | -120.1538 | 119.8425 | -1.442 | 119.7876 | 119.9432 | -1.2589 | -0.41199 | -0.032043 | -0.054932 | 119.8837 | 119.9066 | 119.9066 | 119.7235 | 119.7876 | 121.1334 | 120.0211 | -0.41199 | 119.7235 | 119.7876 | 120.0211 | 119.9066 | 121.1334 | -1.3229 | -121.5775
960.7812 | 121.4172 | -50.2441 | 51.6449 | -0.023499 | 0.016569 | 0.0073486 | 0.1182 | 0.031557 | 0.032524 | 0.18819 | -0.013733 | -0.045776 | 0.068665 | -0.022888 | -0.068665 | 0.022888 | -0.041199 | -0.086975 | 72.4228 | -48.9441 | 50.3128 | -51.6907 | 50.2304 | 50.2213 | -51.7136 | 1.3 | 20.7779 | -0.082398 | 50.2029 | 50.1572 | 50.1755 | 50.1984 | 50.2304 | 122.6669 | 50.267 | 1.3 | 50.1984 | 50.2304 | 50.267 | 50.1755 | 122.6669 | -51.5762 | -100.589
961.7812 | 121.5088 | -120.9961 | 0.40283 | -0.00061033 | 0.015073 | 0.0039306 | 0.037237 | -0.0058277 | -0.0029374 | 0.013016 | 0.018311 | -0.018311 | 0.091553 | 0.21973 | 0.17853 | 0.27924 | 0.13733 | 0.16022 | 0.36163 | -121.2616 | 121.0876 | -0.42114 | 121.0144 | 121.2158 | -0.2243 | -0.2655 | -0.041199 | -0.073242 | 121.1334 | 121.1563 | 121.1746 | 120.9778 | 121.0144 | 121.3577 | 121.2753 | -0.2655 | 120.9778 | 121.0144 | 121.2753 | 121.1746 | 121.3577 | -0.31128 | -121.6644
962.7812 | 121.5454 | -111.232 | 9.9564 | -0.0082398 | 0.015287 | 0.004358 | 0.026556 | -0.0024097 | 0.0011214 | 0.017075 | 0.022888 | -0.013733 | 0.082397 | 0.17395 | 0.12817 | 0.20599 | 0.14191 | 0.10071 | 4.6417 | -111.5616 | 111.3144 | -9.9701 | 111.2549 | 111.4059 | -9.8282 | -0.32959 | -5.3146 | -0.059509 | 111.3739 | 111.3327 | 111.3602 | 111.2183 | 111.2549 | 115.8737 | 111.438 | -0.32959 | 111.2183 | 111.2549 | 111.438 | 111.3602 | 115.8737 | -9.874 | -121.5179
963.7812 | 121.582 | -115.7043 | 6.2302 | -0.0082398 | 0.015714 | 0.0039306 | 0.034887 | -0.0047595 | -0.00058736 | 0.019638 | 0.027466 | -0.013733 | 0.10529 | 0.19226 | 0.15106 | 0.25635 | 0.073242 | 0.14648 | 6.5643 | -114.7751 | 115.8096 | -6.2439 | 115.7318 | 115.8966 | -6.0791 | 0.92926 | 0.33417 | -0.07782 | 115.7776 | 115.8508 | 115.8554 | 115.6906 | 115.7318 | 122.2687 | 115.9607 | 0.92926 | 115.6906 | 115.7318 | 115.9607 | 115.8554 | 122.2687 | -6.1249 | -121.0052
964.7812 | 121.5271 | -118.4601 | 2.9068 | -0.00061033 | 0.016355 | 0.005426 | 0.037237 | -0.0026233 | -0.00080116 | 0.018357 | 0.004578 | -0.013733 | 0.10529 | 0.19226 | 0.14191 | 0.24261 | 0.15564 | 0.13275 | 2.8336 | -118.8263 | 118.5654 | -2.9205 | 118.4647 | 118.6523 | -2.7649 | -0.36621 | -0.073242 | -0.10071 | 118.6157 | 118.5928 | 118.602 | 118.4463 | 118.4647 | 121.2936 | 118.7027 | -0.36621 | 118.4463 | 118.4647 | 118.7027 | 118.602 | 121.2936 | -2.8015 | -121.7331
965.7812 | 120.4651 | -57.5317 | 62.7228 | -0.015869 | 0.017637 | 0.0086304 | 0.033178 | 0.031343 | 0.02932 | 0.073899 | -0.013733 | -0.032043 | 0.068665 | 0.013733 | -0.041199 | 0.050354 | -0.041199 | -0.068665 | 63.446 | -57.1243 | 57.6004 | -62.7548 | 57.518 | 57.5455 | -62.764 | 0.40741 | 0.72327 | -0.082398 | 57.4905 | 57.4631 | 57.4905 | 57.4997 | 57.518 | 120.9778 | 57.5821 | 0.40741 | 57.4997 | 57.518 | 57.5821 | 57.4905 | 120.9778 | -62.6541 | -119.8471
966.7812 | 121.4493 | -55.8701 | 65.0848 | -0.0082398 | 0.014005 | 0.0015808 | 0.05924 | 0.030061 | 0.028892 | 0.12068 | 0.022888 | -0.082397 | 0.086975 | 0.082397 | 0.027466 | 0.13733 | -0.16479 | 0.041199 | 65.3595 | -55.8609 | 55.957 | -65.1672 | 55.8929 | 55.9525 | -65.0574 | 0.009155 | 0.27466 | -0.064087 | 55.7053 | 55.9113 | 55.8975 | 55.7877 | 55.8929 | 121.2296 | 56.0074 | 0.009155 | 55.7877 | 55.8929 | 56.0074 | 55.8975 | 121.2296 | -64.9979 | -120.9457
967.7969 | 121.4859 | -43.6249 | 78.1219 | -0.0082398 | 0.013151 | 0.005426 | 0.079107 | 0.033693 | 0.037437 | 0.16298 | 0.10071 | -0.09613 | 0.09613 | 0.10529 | 0.059509 | 0.15564 | -0.27008 | 0.07782 | 75.8286 | -45.2637 | 43.721 | -78.2181 | 43.7256 | 43.7302 | -78.0624 | -1.6388 | -2.2934 | 0.004578 | 43.3548 | 43.7027 | 43.6844 | 43.5287 | 43.7256 | 119.4534 | 43.7805 | -1.6388 | 43.5287 | 43.7256 | 43.7805 | 43.6844 | 119.4534 | -78.0258 | -123.3856
968.7812 | 88.2156 | -113.4384 | 7.4661 | -0.023499 | 0.013578 | 0.0082032 | 0.029546 | -0.0034777 | 0.0015488 | 0.017502 | 0.054932 | -0.050354 | 0.10986 | 0.24719 | 0.13275 | 0.30212 | 0.013733 | 0.21515 | 9.7046 | -113.0722 | 113.5483 | -7.5165 | 113.4933 | 113.6856 | -7.3334 | 0.36621 | 2.2385 | -0.054931 | 113.4521 | 113.6536 | 113.5712 | 113.3881 | 113.4933 | 123.143 | 113.7405 | 0.36621 | 113.3881 | 113.4933 | 113.7405 | 113.5712 | 123.143 | -7.3563 | -120.5383
969.7812 | 121.4539 | -16.452 | 104.5898 | -0.0082398 | 0.014219 | 0.0035034 | 0.47217 | 0.049714 | 0.05175 | 0.58916 | -0.013733 | -0.091553 | 0.073242 | -0.050354 | -0.11444 | -0.004578 | -0.25635 | -0.10529 | 104.837 | -16.4108 | 16.5253 | -104.6814 | 16.4383 | 16.4017 | -104.7043 | 0.041198 | 0.24719 | -0.086975 | 16.1957 | 16.3467 | 16.3376 | 16.3605 | 16.4383 | 121.2891 | 16.4474 | 0.041198 | 16.3605 | 16.4383 | 16.4474 | 16.3376 | 121.2891 | -104.5166 | -121.0007
970.7812 | 111.2869 | -6.8069 | 92.7841 | -0.0082398 | 0.014005 | 0.0049988 | 0.13871 | 0.054414 | 0.058372 | 0.25185 | -0.022888 | -0.082397 | 0.036621 | -0.13733 | -0.19226 | -0.11902 | -0.20142 | -0.21515 | 114.7705 | -6.7429 | 6.8436 | -92.8665 | 6.7841 | 6.6696 | -92.9764 | 0.064087 | 21.9864 | -0.059509 | 6.6055 | 6.5918 | 6.6147 | 6.7245 | 6.7841 | 121.5775 | 6.6879 | 0.064087 | 6.7245 | 6.7841 | 6.6879 | 6.6147 | 121.5775 | -92.7475 | -99.527
971.7812 | 121.6187 | -7.5623 | 113.6078 | -0.00061033 | 0.013791 | 0.0073486 | 0.32477 | 0.05655 | 0.0588 | 0.55818 | 0.059509 | -0.1236 | 0.064087 | 0.009155 | -0.064087 | 0.054932 | -0.35706 | -0.054932 | 114.1983 | -6.8848 | 7.6263 | -113.7314 | 7.6218 | 7.5714 | -113.6719 | 0.67749 | 0.59051 | -0.004578 | 7.2052 | 7.5073 | 7.4982 | 7.4387 | 7.6218 | 121.7606 | 7.6172 | 0.67749 | 7.4387 | 7.6218 | 7.6172 | 7.4982 | 121.7606 | -113.5437 | -120.4926
972.7812 | 121.2204 | -2.8473 | 95.4346 | -0.00061033 | 0.015073 | 0.004358 | 0.40702 | 0.057191 | 0.060722 | 0.51588 | -0.050354 | -0.073242 | 0.018311 | -0.13733 | -0.17395 | -0.10071 | -0.17853 | -0.20599 | 118.2861 | -3.2913 | 2.8656 | -95.5078 | 2.7969 | 2.71 | -95.6085 | -0.44403 | 22.8516 | -0.068665 | 2.6688 | 2.6413 | 2.6733 | 2.774 | 2.7969 | 121.1334 | 2.7466 | -0.44403 | 2.774 | 2.7969 | 2.7466 | 2.6733 | 121.1334 | -95.4163 | -98.7259
973.7812 | 120.5933 | -61.0336 | 59.6558 | -0.015869 | 0.013151 | 0.00093996 | 0.15964 | 0.025575 | 0.028465 | 0.2119 | 0.082397 | -0.07782 | 0.09613 | 0.11444 | 0.086975 | 0.18768 | -0.17395 | 0.09613 | 57.8156 | -62.2787 | 61.1298 | -59.7336 | 61.116 | 61.1481 | -59.5688 | -1.2451 | -1.8402 | -0.013733 | 60.8597 | 61.1298 | 61.1206 | 60.9558 | 61.116 | 118.8492 | 61.2213 | -1.2451 | 60.9558 | 61.116 | 61.2213 | 61.1206 | 118.8492 | -59.5596 | -121.9345
974.7812 | 121.1792 | -119.9432 | 1.0849 | -0.0082398 | 0.013791 | 0.0064942 | 0.045568 | -0.0064685 | -0.0020828 | 0.018998 | 0.027466 | -0.013733 | 0.086975 | 0.17395 | 0.13275 | 0.23346 | 0.073242 | 0.11444 | 1.0529 | -120.1675 | 120.0302 | -1.0986 | 119.9707 | 120.1172 | -0.95215 | -0.22431 | -0.032044 | -0.059509 | 120.0165 | 120.0577 | 120.076 | 119.9295 | 119.9707 | 120.9961 | 120.1767 | -0.22431 | 119.9295 | 119.9707 | 120.1767 | 120.076 | 120.9961 | -0.99792 | -121.2524
975.7812 | 121.3669 | -120.0073 | 1.149 | -0.015869 | 0.012937 | 0.0028626 | 0.045568 | -0.0036915 | -0.005928 | 0.024124 | 0.07782 | -0.036621 | 0.11444 | 0.25177 | 0.20142 | 0.31128 | -0.022888 | 0.21515 | 1.0803 | -120.1767 | 120.1218 | -1.1856 | 120.0851 | 120.2591 | -0.94757 | -0.16937 | -0.068665 | -0.036621 | 119.9844 | 120.2225 | 120.2087 | 119.9707 | 120.0851 | 121.0876 | 120.3186 | -0.16937 | 119.9707 | 120.0851 | 120.3186 | 120.2087 | 121.0876 | -1.0345 | -121.3257
976.7812 | 121.3028 | -119.5221 | 1.6205 | -0.015869 | 0.016355 | 0.0047852 | 0.049627 | -0.0047595 | -0.0040054 | 0.022629 | 0.022888 | -0.009155 | 0.091553 | 0.15564 | 0.10986 | 0.21515 | 0.09613 | 0.10529 | 1.5839 | -119.7876 | 119.6136 | -1.6296 | 119.545 | 119.6777 | -1.5106 | -0.2655 | -0.036621 | -0.068665 | 119.6182 | 119.6274 | 119.632 | 119.5129 | 119.545 | 121.106 | 119.7372 | -0.2655 | 119.5129 | 119.545 | 119.7372 | 119.632 | 121.106 | -1.5289 | -121.4081
977.7812 | 121.4172 | -119.8334 | 1.3412 | -0.0082398 | 0.01486 | 0.0086304 | 0.045354 | -0.0068957 | -0.004219 | 0.024338 | 0.041199 | -0.022888 | 0.10529 | 0.20142 | 0.15564 | 0.26093 | 0.032043 | 0.15564 | 1.3184 | -120.108 | 119.9387 | -1.3641 | 119.8746 | 120.0348 | -1.1856 | -0.27466 | -0.022889 | -0.064087 | 119.8654 | 119.989 | 119.989 | 119.8105 | 119.8746 | 121.1517 | 120.0943 | -0.27466 | 119.8105 | 119.8746 | 120.0943 | 119.989 | 121.1517 | -1.236 | -121.4493
978.7812 | 121.3715 | -120.2271 | 0.99335 | -0.0082398 | 0.015928 | 0.0045716 | 0.044714 | -0.0051867 | -0.0020828 | 0.019638 | 0.018311 | 0.009155 | 0.09613 | 0.15106 | 0.10071 | 0.19684 | 0.09613 | 0.082397 | 0.95215 | -120.5383 | 120.3232 | -0.98419 | 120.2454 | 120.3781 | -0.89264 | -0.31128 | -0.041199 | -0.077819 | 120.3232 | 120.3094 | 120.3278 | 120.2362 | 120.2454 | 121.1792 | 120.4239 | -0.31128 | 120.2362 | 120.2454 | 120.4239 | 120.3278 | 121.1792 | -0.89722 | -121.5317
979.7812 | 121.4355 | -115.5762 | 5.7587 | -0.015869 | 0.015287 | 0.00093996 | 0.16221 | -0.0041187 | -0.0018692 | 0.14674 | 0.027466 | -0.009155 | 0.07782 | 0.14191 | 0.082397 | 0.17853 | 0.10071 | 0.073242 | 5.6625 | -115.8096 | 115.654 | -5.7678 | 115.6036 | 115.7181 | -5.6763 | -0.23346 | -0.09613 | -0.050354 | 115.6769 | 115.6494 | 115.6586 | 115.567 | 115.6036 | 121.2387 | 115.7547 | -0.23346 | 115.567 | 115.6036 | 115.7547 | 115.6586 | 121.2387 | -5.6808 | -121.5683
980.7812 | 121.5363 | -119.9799 | 1.2314 | -0.0082398 | 0.013151 | 0.00051276 | 0.048986 | -0.0034777 | -0.0052872 | 0.023056 | 0.054932 | -0.022888 | 0.11444 | 0.21973 | 0.16022 | 0.27466 | 0.004578 | 0.17853 | 1.1856 | -120.2866 | 120.0943 | -1.2543 | 120.0348 | 120.1996 | -1.0712 | -0.3067 | -0.045776 | -0.059509 | 119.9844 | 120.1584 | 120.1401 | 119.957 | 120.0348 | 121.1655 | 120.2545 | -0.3067 | 119.957 | 120.0348 | 120.2545 | 120.1401 | 121.1655 | -1.1169 | -121.5179
981.7812 | 121.4996 | -120.0897 | 1.2405 | -0.0082398 | 0.014219 | 0.0069214 | 0.048345 | -0.0056141 | -0.0029374 | 0.027542 | 0.032043 | -0.022888 | 0.09613 | 0.17395 | 0.14648 | 0.23804 | 0.022888 | 0.11902 | 1.1765 | -120.3323 | 120.1859 | -1.2634 | 120.1218 | 120.2637 | -1.0941 | -0.24261 | -0.064087 | -0.064087 | 120.1126 | 120.2087 | 120.2362 | 120.0668 | 120.1218 | 121.2662 | 120.3278 | -0.24261 | 120.0668 | 120.1218 | 120.3278 | 120.2362 | 121.2662 | -1.1444 | -121.5729
982.7812 | 109.6664 | -94.4778 | 15.8524 | -0.0082398 | 0.017637 | 0.0022218 | 0.56019 | 0.0020765 | 0.006462 | 0.55519 | 0.032043 | -0.027466 | 0.082397 | 0.11444 | 0.073242 | 0.16022 | 0.059509 | -1.387 | 15.9943 | -105.4138 | 94.5602 | -15.8798 | 94.5099 | 94.5923 | -15.7791 | -10.936 | 0.14191 | -0.050354 | 94.5374 | 93.0908 | 94.5511 | 94.4504 | 94.5099 | 110.4721 | 94.6381 | -10.936 | 94.4504 | 94.5099 | 94.6381 | 94.5511 | 110.4721 | -15.77 | -121.2662
983.7812 | 121.3715 | -76.0025 | 44.3619 | -0.00061033 | 0.017209 | 0.006067 | 0.83213 | 0.018953 | 0.019066 | 0.88908 | 0.004578 | -0.032043 | 0.059509 | 0.064087 | 0.032043 | 0.11444 | 0.004578 | -2.5085 | 44.7601 | -76.3962 | 76.062 | -44.3939 | 76.0071 | 76.0666 | -44.3298 | -0.39368 | 0.39825 | -0.054931 | 76.0071 | 73.494 | 76.0345 | 75.9705 | 76.0071 | 120.7626 | 76.1169 | -0.39368 | 75.9705 | 76.0071 | 76.1169 | 76.0345 | 120.7626 | -44.3024 | -120.7581
984.7812 | 121.4539 | -88.9389 | 32.2906 | -0.0082398 | 0.014646 | 0.007776 | 0.50913 | 0.011903 | 0.01458 | 0.52785 | 0.018311 | -0.032043 | 0.068665 | 0.07782 | 0.032043 | 0.13275 | 0.027466 | -1.4603 | 32.2266 | -89.122 | 89.0076 | -32.3227 | 88.9572 | 89.0167 | -32.2586 | -0.18311 | -0.064087 | -0.050354 | 88.9664 | 87.4786 | 88.9709 | 88.9069 | 88.9572 | 121.1655 | 89.0717 | -0.18311 | 88.9069 | 88.9572 | 89.0717 | 88.9709 | 121.1655 | -32.222 | -121.4127
985.7812 | 121.4401 | -120.1859 | 1.149 | -0.0082398 | 0.017423 | 0.0062806 | 0.046636 | -0.0041187 | -0.0035782 | 0.021347 | 0.018311 | 0 | 0.086975 | 0.14191 | 0.09613 | 0.17395 | 0.10071 | 0.059509 | 1.0986 | -120.4926 | 120.2728 | -1.149 | 120.2042 | 120.3278 | -1.0529 | -0.3067 | -0.050354 | -0.068664 | 120.2866 | 120.2454 | 120.282 | 120.1859 | 120.2042 | 121.2845 | 120.3598 | -0.3067 | 120.1859 | 120.2042 | 120.3598 | 120.282 | 121.2845 | -1.062 | -121.6415
986.7812 | 120.9091 | -120.163 | 0.58594 | -0.0082398 | 0.014646 | 0.007776 | 0.036596 | -0.0039051 | -0.0044328 | 0.013443 | 0.013733 | -0.004578 | 0.10529 | 0.12817 | 0.086975 | 0.1831 | 0.11902 | 0.073242 | 0.55389 | -120.5017 | 120.2683 | -0.59052 | 120.1767 | 120.2911 | -0.49896 | -0.33875 | -0.032043 | -0.091553 | 120.282 | 120.2362 | 120.2499 | 120.1584 | 120.1767 | 120.7169 | 120.3461 | -0.33875 | 120.1584 | 120.1767 | 120.3461 | 120.2499 | 120.7169 | -0.48065 | -121.0876
987.7812 | 121.2204 | -120.2682 | 0.88806 | -0.0082398 | 0.015287 | 0.0017944 | 0.045995 | -0.0079639 | -0.004219 | 0.023056 | 0.018311 | -0.018311 | 0.082397 | 0.13733 | 0.091553 | 0.20142 | 0.091553 | 0.10071 | 0.67749 | -120.4926 | 120.3506 | -0.90637 | 120.2866 | 120.4056 | -0.79651 | -0.2243 | -0.21057 | -0.064086 | 120.3598 | 120.369 | 120.3598 | 120.2499 | 120.2866 | 120.9457 | 120.4697 | -0.2243 | 120.2499 | 120.2866 | 120.4697 | 120.3598 | 120.9457 | -0.80567 | -121.3806
988.7812 | 121.2936 | -120.2179 | 0.67291 | -0.0082398 | 0.01486 | 0.0039306 | 0.050695 | -0.0034777 | -0.0057144 | 0.03096 | 0.018311 | 0.004578 | 0.091553 | 0.11444 | 0.086975 | 0.16937 | 0.10071 | 0.082397 | 0.57678 | -120.8496 | 120.3094 | -0.66834 | 120.2362 | 120.3323 | -0.58594 | -0.63171 | -0.096131 | -0.073242 | 120.3186 | 120.3003 | 120.3049 | 120.2225 | 120.2362 | 120.7947 | 120.3873 | -0.63171 | 120.2225 | 120.2362 | 120.3873 | 120.3049 | 120.7947 | -0.58136 | -121.5225
989.7812 | 121.4035 | -119.9295 | 0.58136 | -0.0082398 | 0.01785 | 0.0013672 | 0.046636 | -0.0043323 | -0.00486 | 0.019211 | 0.045776 | 0.009155 | 0.10071 | 0.15564 | 0.10529 | 0.1831 | 0.091553 | 0.086975 | 0.56763 | -120.9183 | 120.0302 | -0.5722 | 119.9753 | 120.0851 | -0.47607 | -0.98877 | -0.013733 | -0.054932 | 120.0211 | 120.0165 | 120.0348 | 119.9387 | 119.9753 | 120.4971 | 120.1126 | -0.98877 | 119.9387 | 119.9753 | 120.1126 | 120.0348 | 120.4971 | -0.48065 | -121.4996
990.7812 | 121.376 | -120.488 | 0.43945 | -0.00061033 | 0.016782 | 0.0028626 | 0.040227 | -0.0041187 | -0.0057144 | 0.016007 | 0.009155 | -0.009155 | 0.09613 | 0.10071 | 0.064087 | 0.16022 | 0.10071 | 0.086975 | 0.36163 | -121.1334 | 120.5841 | -0.44861 | 120.4971 | 120.5887 | -0.37537 | -0.64545 | -0.07782 | -0.086975 | 120.5887 | 120.575 | 120.5521 | 120.4788 | 120.4971 | 120.8496 | 120.6482 | -0.64545 | 120.4788 | 120.4971 | 120.6482 | 120.5521 | 120.8496 | -0.34332 | -121.5729
991.7812 | 121.1746 | -111.0626 | 10.0342 | -0.00061033 | 0.015928 | 0.0041444 | 0.76505 | -0.0009143 | 0.00048064 | 0.74467 | 0.009155 | -0.004578 | 0.091553 | 0.11902 | 0.059509 | 0.16022 | 0.10071 | -0.77362 | 10.1486 | -111.1954 | 111.1542 | -10.0388 | 111.0718 | 111.1816 | -9.9747 | -0.13275 | 0.11444 | -0.082398 | 111.1633 | 110.289 | 111.1221 | 111.058 | 111.0718 | 121.2112 | 111.2228 | -0.13275 | 111.058 | 111.0718 | 111.2228 | 111.1221 | 121.2112 | -9.9426 | -121.2296
992.7969 | 121.5225 | -120.2499 | 0.34332 | -0.00061033 | 0.016996 | 0.0041444 | 0.041509 | -0.0049731 | -0.0033646 | 0.018143 | 0.07782 | -0.013733 | 0.09613 | 0.17395 | 0.14191 | 0.21515 | 0.068665 | 0.11902 | 0.42572 | -121.1243 | 120.3461 | -0.35706 | 120.3278 | 120.4239 | -0.20142 | -0.87433 | 0.082397 | -0.01831 | 120.3186 | 120.369 | 120.3918 | 120.2362 | 120.3278 | 120.6757 | 120.4651 | -0.87433 | 120.2362 | 120.3278 | 120.4651 | 120.3918 | 120.6757 | -0.24719 | -121.4676
993.7812 | 121.5134 | -120.0806 | 0.61798 | -0.0082398 | 0.018064 | 0.0032898 | 0.048986 | -0.0036915 | -0.0040054 | 0.02562 | 0.041199 | -0.004578 | 0.086975 | 0.15106 | 0.11902 | 0.19226 | 0.09613 | 0.10529 | 0.54474 | -121.019 | 120.1675 | -0.62256 | 120.1218 | 120.2316 | -0.49896 | -0.93842 | -0.073242 | -0.045776 | 120.1767 | 120.1859 | 120.1996 | 120.076 | 120.1218 | 120.6253 | 120.2728 | -0.93842 | 120.076 | 120.1218 | 120.2728 | 120.1996 | 120.6253 | -0.53101 | -121.637
994.7812 | 121.4493 | -119.7876 | 0.85144 | -0.0082398 | 0.015928 | 0.0058534 | 0.05689 | -0.0051867 | -0.0035782 | 0.03331 | 0.009155 | -0.009155 | 0.09613 | 0.10529 | 0.073242 | 0.17395 | 0.11902 | 0.07782 | 0.75531 | -120.8176 | 119.8837 | -0.86059 | 119.7968 | 119.8929 | -0.7782 | -1.03 | -0.09613 | -0.086975 | 119.9066 | 119.8654 | 119.8608 | 119.7784 | 119.7968 | 120.5429 | 119.9615 | -1.03 | 119.7784 | 119.7968 | 119.9615 | 119.8608 | 120.5429 | -0.75531 | -121.669
995.7812 | 121.463 | -119.8196 | 0.81482 | -0.023499 | 0.015287 | 0.004358 | 0.056249 | -0.0049731 | -0.0044328 | 0.034592 | 0.068665 | -0.032043 | 0.10986 | 0.1831 | 0.13733 | 0.21973 | 0.064087 | 0.14191 | 0.71411 | -120.845 | 119.9295 | -0.84686 | 119.8883 | 120.0027 | -0.67749 | -1.0254 | -0.10071 | -0.041198 | 119.8837 | 119.9615 | 119.957 | 119.7876 | 119.8883 | 120.5338 | 120.0394 | -1.0254 | 119.7876 | 119.8883 | 120.0394 | 119.957 | 120.5338 | -0.70496 | -121.6599
996.7812 | 122.9279 | -106.7551 | 6.1844 | -0.015869 | 0.015928 | 0.0064942 | 0.35361 | 0.0012219 | -0.0018692 | 0.342 | 0.027466 | -0.027466 | 0.09613 | 0.1236 | 0.073242 | 0.16479 | 0.091553 | 0.49439 | 6.0562 | -115.4434 | 106.8512 | -6.2119 | 106.7825 | 106.8787 | -6.1111 | -8.6884 | -0.12817 | -0.068664 | 106.8466 | 107.2495 | 106.8283 | 106.7276 | 106.7825 | 112.8113 | 106.9199 | -8.6884 | 106.7276 | 106.7825 | 106.9199 | 106.8283 | 112.8113 | -6.0883 | -121.6278
997.7812 | 121.5912 | -116.1575 | 4.6417 | -0.00061033 | 0.016569 | 0.0030762 | 0.34742 | -0.0021961 | -0.004219 | 0.33174 | 0.086975 | -0.032043 | 0.1236 | 0.21057 | 0.16022 | 0.23346 | 0.059509 | 0.55389 | 4.3991 | -116.9678 | 116.2811 | -4.6738 | 116.2445 | 116.3681 | -4.4815 | -0.81024 | -0.24261 | -0.036621 | 116.217 | 116.7114 | 116.3177 | 116.1255 | 116.2445 | 120.5566 | 116.391 | -0.81024 | 116.1255 | 116.2445 | 116.391 | 116.3177 | 120.5566 | -4.5181 | -121.6095
998.7812 | 121.5591 | -117.6682 | 3.5431 | -0.0082398 | 0.016355 | 0.002649 | 0.22522 | -0.0021961 | -0.0033646 | 0.23988 | 0.059509 | -0.018311 | 0.10529 | 0.16479 | 0.1236 | 0.20142 | 0.082397 | 0.43488 | 3.186 | -118.1992 | 117.7734 | -3.5614 | 117.7277 | 117.8329 | -3.4195 | -0.53101 | -0.35706 | -0.045777 | 117.7505 | 118.103 | 117.7917 | 117.6498 | 117.7277 | 120.8542 | 117.8696 | -0.53101 | 117.6498 | 117.7277 | 117.8696 | 117.7917 | 120.8542 | -3.4378 | -121.7422
999.7812 | 121.6095 | -119.9249 | 1.2909 | -0.0082398 | 0.015928 | 0.0067078 | 0.11008 | -0.0058277 | -0.0033646 | 0.093766 | 0.082397 | 0.009155 | 0.09613 | 0.21973 | 0.17395 | 0.24719 | 0.068665 | 0.14648 | 1.268 | -120.3964 | 120.0211 | -1.2817 | 120.0073 | 120.1447 | -1.1169 | -0.4715 | -0.022889 | -0.013733 | 119.9936 | 120.0714 | 120.0989 | 119.9341 | 120.0073 | 121.1929 | 120.1721 | -0.4715 | 119.9341 | 120.0073 | 120.1721 | 120.0989 | 121.1929 | -1.1948 | -121.6873
1000.7812 | 121.5775 | -120.7993 | 0.48065 | -0.0082398 | 0.015714 | 0.0024354 | 0.047704 | -0.0047595 | -0.0069962 | 0.024765 | 0.086975 | -0.013733 | 0.11444 | 0.20599 | 0.14648 | 0.24261 | 0.082397 | 0.17853 | 0.42572 | -121.2296 | 120.9137 | -0.49439 | 120.8862 | 121.0052 | -0.33417 | -0.4303 | -0.054932 | -0.027466 | 120.8817 | 120.9778 | 120.9457 | 120.7855 | 120.8862 | 121.225 | 121.0419 | -0.4303 | 120.7855 | 120.8862 | 121.0419 | 120.9457 | 121.225 | -0.36621 | -121.7102
1001.7812 | 121.5134 | -120.9778 | 0.46692 | -0.00061033 | 0.016782 | 0.0030762 | 0.04685 | -0.0036915 | -0.0061416 | 0.024765 | 0.041199 | -0.018311 | 0.10071 | 0.17395 | 0.10986 | 0.21057 | 0.11444 | 0.1236 | 0.37994 | -121.2753 | 121.0785 | -0.48523 | 121.019 | 121.1517 | -0.35706 | -0.29755 | -0.086975 | -0.059509 | 121.0922 | 121.1014 | 121.0876 | 120.9595 | 121.019 | 121.3577 | 121.1884 | -0.29755 | 120.9595 | 121.019 | 121.1884 | 121.0876 | 121.3577 | -0.36621 | -121.7422
1002.7969 | 121.6553 | -116.5192 | 4.8935 | -0.0082398 | 0.010801 | 0.00051276 | 0.48542 | -0.0030505 | -0.0033646 | 0.46397 | 0.036621 | -0.054932 | 0.11902 | 0.19684 | 0.17853 | 0.29297 | 0.013733 | -0.082397 | 4.7974 | -116.6656 | 116.6382 | -4.9484 | 116.5558 | 116.716 | -4.715 | -0.14648 | -0.096131 | -0.082398 | 116.5329 | 116.4368 | 116.6977 | 116.4642 | 116.5558 | 121.3165 | 116.8121 | -0.14648 | 116.4642 | 116.5558 | 116.8121 | 116.6977 | 121.3165 | -4.7745 | -121.5591
1003.7812 | 121.6278 | -120.9091 | 0.51727 | -0.015869 | 0.019346 | 0.003717 | 0.058385 | -0.0073229 | -0.004219 | 0.03331 | 0.086975 | -0.027466 | 0.09613 | 0.23804 | 0.18768 | 0.27924 | 0.073242 | 0.22888 | 0.43945 | -121.257 | 121.0052 | -0.54474 | 120.9961 | 121.1472 | -0.32959 | -0.3479 | -0.07782 | -0.009155 | 120.9824 | 121.138 | 121.0968 | 120.8817 | 120.9961 | 121.3486 | 121.1884 | -0.3479 | 120.8817 | 120.9961 | 121.1884 | 121.0968 | 121.3486 | -0.42114 | -121.7743
1004.7812 | 121.6278 | -120.5521 | 0.83313 | 0.014648 | 0.016141 | 0.0032898 | 0.082738 | -0.0051867 | -0.00486 | 0.058518 | 0.068665 | -0.013733 | 0.10529 | 0.20599 | 0.14191 | 0.24719 | 0.082397 | 0.20599 | 0.75989 | -120.932 | 120.6573 | -0.84686 | 120.6207 | 120.7581 | -0.69122 | -0.37994 | -0.073242 | -0.036621 | 120.6345 | 120.7581 | 120.694 | 120.5383 | 120.6207 | 121.312 | 120.7993 | -0.37994 | 120.5383 | 120.6207 | 120.7993 | 120.694 | 121.312 | -0.72784 | -121.7651
1005.7812 | 121.6278 | -120.9183 | 0.54474 | -0.015869 | 0.018278 | 0.0024354 | 0.055181 | -0.0043323 | -0.005928 | 0.029465 | 0.091553 | -0.013733 | 0.10986 | 0.20142 | 0.16022 | 0.24261 | 0.086975 | 0.19226 | 0.46234 | -121.2204 | 121.0281 | -0.55847 | 121.0098 | 121.1197 | -0.38452 | -0.30212 | -0.082398 | -0.01831 | 121.0052 | 121.1105 | 121.0785 | 120.9045 | 121.0098 | 121.3806 | 121.1609 | -0.30212 | 120.9045 | 121.0098 | 121.1609 | 121.0785 | 121.3806 | -0.43488 | -121.7651
1006.7812 | 121.6095 | -121.0007 | 0.51727 | -0.0082398 | 0.016141 | 0.002649 | 0.051549 | -0.0047595 | -0.0046464 | 0.028824 | 0.07782 | 0 | 0.082397 | 0.22888 | 0.16937 | 0.23804 | 0.10071 | 0.21515 | 0.46234 | -121.2158 | 121.0831 | -0.51727 | 121.0785 | 121.2296 | -0.3479 | -0.21515 | -0.054932 | -0.004577 | 121.1014 | 121.2158 | 121.17 | 121.0007 | 121.0785 | 121.463 | 121.2387 | -0.21515 | 121.0007 | 121.0785 | 121.2387 | 121.17 | 121.463 | -0.43488 | -121.7331
1007.7812 | 121.5958 | -121.019 | 0.48523 | -0.015869 | 0.012723 | 0.003717 | 0.053472 | -0.0056141 | -0.0050736 | 0.025193 | 0.018311 | -0.009155 | 0.086975 | 0.14648 | 0.09613 | 0.19684 | 0.10071 | 0.12817 | 0.46234 | -121.2708 | 121.106 | -0.49438 | 121.0373 | 121.1655 | -0.3891 | -0.25177 | -0.022888 | -0.068664 | 121.1197 | 121.1472 | 121.1151 | 121.0098 | 121.0373 | 121.4813 | 121.2158 | -0.25177 | 121.0098 | 121.0373 | 121.2158 | 121.1151 | 121.4813 | -0.39825 | -121.756
1008.7812 | 121.6965 | -120.9457 | 0.55847 | -0.023499 | 0.017209 | 0.0028626 | 0.060522 | -0.0058277 | -0.0027238 | 0.032883 | 0.082397 | -0.013733 | 0.10071 | 0.24261 | 0.19684 | 0.27924 | 0.086975 | 0.21973 | 0.48981 | -121.2021 | 121.0464 | -0.5722 | 121.0281 | 121.1884 | -0.36163 | -0.25635 | -0.068665 | -0.018311 | 121.0327 | 121.1655 | 121.1426 | 120.932 | 121.0281 | 121.4355 | 121.225 | -0.25635 | 120.932 | 121.0281 | 121.225 | 121.1426 | 121.4355 | -0.45776 | -121.7606
1009.7812 | 121.6736 | -120.9 | 0.6134 | -0.015869 | 0.017423 | 0.0017944 | 0.060735 | -0.0043323 | -0.0027238 | 0.039292 | 0.07782 | 0.004578 | 0.11444 | 0.19226 | 0.15564 | 0.23346 | 0.091553 | 0.19684 | 0.55847 | -121.1609 | 121.0144 | -0.60883 | 120.9778 | 121.0922 | -0.45776 | -0.26093 | -0.054931 | -0.036621 | 120.9915 | 121.0968 | 121.0556 | 120.9045 | 120.9778 | 121.4584 | 121.1334 | -0.26093 | 120.9045 | 120.9778 | 121.1334 | 121.0556 | 121.4584 | -0.49896 | -121.7743
1010.7812 | 121.6141 | -120.9824 | 0.52185 | -0.0082398 | 0.016569 | 0.002649 | 0.057317 | -0.0045459 | -0.0044328 | 0.03032 | 0.068665 | 0.004578 | 0.082397 | 0.22888 | 0.17395 | 0.25177 | 0.07782 | 0.21515 | 0.45319 | -121.257 | 121.0648 | -0.51727 | 121.051 | 121.2112 | -0.3479 | -0.27466 | -0.068665 | -0.013732 | 121.0602 | 121.1975 | 121.1563 | 120.9869 | 121.051 | 121.4355 | 121.2341 | -0.27466 | 120.9869 | 121.051 | 121.2341 | 121.1563 | 121.4355 | -0.43945 | -121.7789
1011.7812 | 121.6736 | -121.0236 | 0.48981 | -0.015869 | 0.01785 | 0.004358 | 0.050268 | -0.0034777 | -0.004219 | 0.032029 | 0.086975 | -0.009155 | 0.11444 | 0.21973 | 0.17853 | 0.2655 | 0.050354 | 0.20142 | 0.41657 | -121.3074 | 121.138 | -0.49896 | 121.1105 | 121.2433 | -0.31128 | -0.28381 | -0.073242 | -0.027466 | 121.0739 | 121.225 | 121.2021 | 121.0144 | 121.1105 | 121.4401 | 121.2891 | -0.28381 | 121.0144 | 121.1105 | 121.2891 | 121.2021 | 121.4401 | -0.37537 | -121.7972
1012.7969 | 121.7651 | -120.932 | 0.51727 | -0.00061033 | 0.0088783 | 0.0047852 | 0.055181 | -0.0064685 | -0.004219 | 0.039292 | 0.1236 | -0.064087 | 0.13733 | 0.27924 | 0.23346 | 0.33875 | -0.082397 | 0.27008 | 0.43945 | -121.1838 | 121.0693 | -0.58136 | 121.0556 | 121.2112 | -0.28381 | -0.25177 | -0.07782 | -0.013733 | 120.8496 | 121.2021 | 121.1655 | 120.8679 | 121.0556 | 121.3715 | 121.2708 | -0.25177 | 120.8679 | 121.0556 | 121.2708 | 121.1655 | 121.3715 | -0.37994 | -121.7011
1013.7812 | 121.6827 | -121.0236 | 0.53101 | -0.0082398 | 0.016355 | 0.0062806 | 0.062017 | -0.0077503 | -0.0046464 | 0.037583 | 0.022888 | -0.013733 | 0.10071 | 0.16479 | 0.1236 | 0.21515 | 0.1236 | 0.18768 | 0.44861 | -121.2845 | 121.1243 | -0.54474 | 121.0464 | 121.1884 | -0.40741 | -0.26093 | -0.082398 | -0.07782 | 121.1472 | 121.2112 | 121.1472 | 121.0098 | 121.0464 | 121.4722 | 121.2387 | -0.26093 | 121.0098 | 121.0464 | 121.2387 | 121.1472 | 121.4722 | -0.4303 | -121.8155
1014.7812 | 121.7056 | -120.9091 | 0.65918 | -0.0082398 | 0.016355 | 0.0030762 | 0.075475 | -0.0041187 | -0.0029374 | 0.054673 | 0.086975 | -0.027466 | 0.11444 | 0.2243 | 0.17395 | 0.26093 | 0.059509 | 0.20599 | 0.5722 | -121.1472 | 121.0236 | -0.68665 | 120.9961 | 121.1334 | -0.48523 | -0.23804 | -0.086975 | -0.027466 | 120.9686 | 121.1151 | 121.0831 | 120.8817 | 120.9961 | 121.4813 | 121.17 | -0.23804 | 120.8817 | 120.9961 | 121.17 | 121.0831 | 121.4813 | -0.54474 | -121.8063
1015.7812 | 121.7056 | -121.0281 | 0.54474 | -0.00061033 | 0.015928 | 0.0069214 | 0.079961 | -0.0041187 | -0.0044328 | 0.053177 | 0.086975 | -0.009155 | 0.12817 | 0.20142 | 0.14648 | 0.23346 | 0.07782 | 0.16937 | 0.53558 | -121.2753 | 121.1563 | -0.55389 | 121.1151 | 121.2296 | -0.39825 | -0.24719 | -0.009156 | -0.041199 | 121.106 | 121.1975 | 121.1746 | 121.019 | 121.1151 | 121.5637 | 121.2616 | -0.24719 | 121.019 | 121.1151 | 121.2616 | 121.1746 | 121.5637 | -0.41656 | -121.8201
1016.7812 | 121.7102 | -121.0648 | 0.53558 | -0.015869 | 0.014005 | 0.0022218 | 0.060949 | -0.0041187 | -0.0063554 | 0.036515 | 0.027466 | -0.009155 | 0.07782 | 0.17395 | 0.14648 | 0.21057 | 0.13275 | 0.17853 | 0.45319 | -121.2936 | 121.1426 | -0.54474 | 121.0922 | 121.2387 | -0.3891 | -0.22888 | -0.082397 | -0.050354 | 121.1975 | 121.2433 | 121.2112 | 121.0556 | 121.0922 | 121.5179 | 121.2753 | -0.22888 | 121.0556 | 121.0922 | 121.2753 | 121.2112 | 121.5179 | -0.45776 | -121.8292
1017.7812 | 121.6599 | -117.4393 | 4.0237 | -0.015869 | 0.011442 | -0.0022644 | 0.34357 | -0.0054003 | -0.00016016 | 0.32726 | 0.050354 | -0.050354 | 0.10529 | 0.20599 | 0.16937 | 0.29297 | 0.009155 | 0.54474 | 4.0878 | -117.6361 | 117.5446 | -4.0741 | 117.4896 | 117.6453 | -3.8544 | -0.19684 | 0.064087 | -0.054932 | 117.4484 | 117.984 | 117.6086 | 117.3889 | 117.4896 | 121.5271 | 117.7322 | -0.19684 | 117.3889 | 117.4896 | 117.7322 | 117.6086 | 121.5271 | -3.9185 | -121.6599
1018.7812 | 121.6095 | -117.2379 | 4.129 | -0.00061033 | 0.015073 | 0.005426 | 0.48777 | -0.0045459 | -0.00016016 | 0.37724 | 0.045776 | -0.004578 | 0.091553 | 0.17853 | 0.12817 | 0.2243 | 0.086975 | 0.59509 | 4.2801 | -117.5125 | 117.3294 | -4.1336 | 117.2836 | 117.4164 | -4.0009 | -0.27466 | 0.15106 | -0.045777 | 117.3248 | 117.8329 | 117.366 | 117.2333 | 117.2836 | 121.5179 | 117.4622 | -0.27466 | 117.2333 | 117.2836 | 117.4622 | 117.366 | 121.5179 | -4.0375 | -121.6415
1019.7812 | 121.7468 | -119.6503 | 2.005 | -0.0082398 | 0.018491 | 0.0024354 | 0.11542 | -0.0045459 | -0.0052872 | 0.14055 | 0.022888 | -0.018311 | 0.091553 | 0.17853 | 0.12817 | 0.20599 | 0.13733 | 0.21515 | 2.2202 | -119.8151 | 119.7418 | -2.0233 | 119.6732 | 119.8288 | -1.8768 | -0.16479 | 0.21515 | -0.068665 | 119.7876 | 119.8654 | 119.7784 | 119.632 | 119.6732 | 121.8704 | 119.8563 | -0.16479 | 119.632 | 119.6732 | 119.8563 | 119.7784 | 121.8704 | -1.9135 | -121.8201
1020.7812 | 121.6644 | -111.0626 | 10.5194 | -0.0082398 | 0.012937 | 0.002649 | 0.78834 | -0.0034777 | 0.0024032 | 0.75066 | 0 | -0.013733 | 0.091553 | 0.13275 | 0.09613 | 0.16937 | 0.15106 | 0.83771 | 10.3363 | -111.2 | 111.1542 | -10.5331 | 111.0626 | 111.1954 | -10.4233 | -0.13733 | -0.1831 | -0.091553 | 111.2137 | 111.9003 | 111.1588 | 111.0489 | 111.0626 | 121.3989 | 111.232 | -0.13733 | 111.0489 | 111.0626 | 111.232 | 111.1588 | 121.3989 | -10.4279 | -121.7194

## Thermal Data
Fire Time | B Position - Middle
-0.9021 | 12.4248
0.0979 | 12.4194
1.0979 | 12.4195
2.0979 | 12.4278
3.0979 | 12.4199
4.0979 | 12.422
5.0979 | 12.4273
6.0979 | 13.2026
7.0979 | 13.4236
8.0979 | 13.6443
9.0979 | 14.1442
10.0979 | 14.9579
11.0979 | 16.9094
12.0979 | 17.1679
13.0979 | 18.5089
14.0979 | 18.3965
15.0979 | 19.4401
16.0979 | 19.9018
17.0979 | 20.2582
18.0979 | 21.2737
19.0979 | 23.4313
20.0979 | 26.1188
21.0979 | 27.645
22.0979 | 28.7643
23.0979 | 30.3151
24.0979 | 32.3859
25.0979 | 34.7686
26.0979 | 39.9496
27.0979 | 42.8876
28.0979 | 45.5607
29.0979 | 46.8623
30.0979 | 47.8927
31.0979 | 51.0908
32.0979 | 51.2
33.0979 | 52.1037
34.0979 | 53.0037
35.0979 | 54.8225
36.0979 | 58.7841
37.0979 | 57.4749
38.0979 | 60.3661
39.0979 | 61.2323
40.0979 | 63.6351
41.0979 | 65.6248
42.0979 | 67.5683
43.0979 | 70.0146
44.0979 | 70.1027
45.0979 | 69.7944
46.0979 | 70.458
47.0979 | 71.431
48.0979 | 72.679
49.0979 | 76.7946
50.0979 | 76.0023
51.0979 | 76.0302
52.0979 | 76.8785
53.0979 | 75.7511
54.0979 | 75.1871
55.0979 | 73.7693
56.0979 | 72.8148
57.0979 | 73.8271
58.0979 | 73.7949
59.0979 | 73.6375
60.0979 | 72.2813
61.0979 | 72.3154
62.0979 | 72.979
63.0979 | 71.786
64.0979 | 72.4561
65.0979 | 72.4912
66.0979 | 73.2679
67.0979 | 74.6676
68.0979 | 74.3001
69.0979 | 72.7189
70.0979 | 72.8289
71.0979 | 72.3916
72.0979 | 72.7606
73.0979 | 73.8991
74.0979 | 73.871
75.0979 | 77.4048
76.0979 | 76.6547
77.0979 | 74.9384
78.0979 | 74.86
79.0979 | 76.5132
80.0979 | 75.8837
81.0979 | 75.9611
82.0979 | 74.4168
83.0979 | 73.4459
84.0979 | 72.854
85.0979 | 72.3122
86.0979 | 71.4312
87.0979 | 70.3928
88.0979 | 69.3083
89.0979 | 71.0801
90.0979 | 70.6923
91.0979 | 69.9783
92.0979 | 69.5352
93.0979 | 69.3395
94.0979 | 70.7416
95.0979 | 69.3117
96.0979 | 71.8248
97.0979 | 71.9254
98.0979 | 73.5958
99.0979 | 72.0458
100.0979 | 71.6389
101.0979 | 72.4386
102.0979 | 72.0336
103.0979 | 74.6338
104.0979 | 75.9065
105.0979 | 75.1669
106.0979 | 77.1999
107.0979 | 77.0284
108.0979 | 78.0959
109.0979 | 78.8604
110.0979 | 79.5925
111.0979 | 79.7802
112.0979 | 79.9815
113.0979 | 83.0714
114.0979 | 83.5685
115.0979 | 84.3063
116.0979 | 83.7776
117.0979 | 85.0175
118.0979 | 88.5611
119.0979 | 86.3847
120.0979 | 86.3987
121.0979 | 85.4815
122.0979 | 85.4688
123.0979 | 83.6677
124.0979 | 82.3
125.0979 | 83.8645
126.0979 | 85.788
127.0979 | 84.0212
128.0979 | 84.1433
129.0979 | 85.9215
130.0979 | 84.2051
131.0979 | 84.5409
132.0979 | 86.4085
133.0979 | 86.4405
134.0979 | 87.1464
135.0979 | 85.6286
136.0979 | 85.0412
137.0979 | 84.3733
138.0979 | 86.1056
139.0979 | 85.876
140.0979 | 86.938
141.0979 | 86.4661
142.0979 | 85.9451
143.0979 | 89.8215
144.0979 | 89.3292
145.0979 | 87.9008
146.0979 | 87.3108
147.0979 | 86.2657
148.0979 | 85.1717
149.0979 | 86.0393
150.0979 | 85.3492
151.0979 | 86.1343
152.0979 | 86.4905
153.0979 | 84.988
154.0979 | 86.157
155.0979 | 87.0284
156.0979 | 85.5896
157.0979 | 85.1504
158.0979 | 84.1937
159.0979 | 85.8313
160.0979 | 87.2393
161.0979 | 86.9385
162.0979 | 86.8536
163.0979 | 86.6305
164.0979 | 87.7285
165.0979 | 87.9525
166.0979 | 85.8081
167.0979 | 86.4318
168.0979 | 86.985
169.0979 | 87.3176
170.0979 | 86.7508
171.0979 | 86.2539
172.0979 | 85.5792
173.0979 | 84.8547
174.0979 | 83.405
175.0979 | 83.4628
176.0979 | 81.7485
177.0979 | 81.5824
178.0979 | 80.899
179.0979 | 81.212
180.0979 | 80.8815
181.0979 | 81.4489
182.0979 | 80.8876
183.0979 | 82.0376
184.0979 | 82.0931
185.0979 | 83.2608
186.0979 | 82.9176
187.0979 | 85.7872
188.0979 | 87.6688
189.0979 | 89.4864
190.0979 | 88.8548
191.0979 | 87.5467
192.0979 | 87.6712
193.0979 | 90.8696
194.0979 | 90.7134
195.0979 | 90.4475
196.0979 | 92.0803
197.0979 | 92.8254
198.0979 | 92.5638
199.0979 | 92.9415
200.0979 | 93.6747
201.0979 | 95.292
202.0979 | 99.8764
203.0979 | 100.4915
204.0979 | 102.2295
205.0979 | 102.9811
206.0979 | 104.3471
207.0979 | 104.2377
208.0979 | 103.8709
209.0979 | 101.8837
210.0979 | 102.6125
211.0979 | 101.636
212.0979 | 103.7477
213.0979 | 103.6703
214.0979 | 103.2004
215.0979 | 104.6668
216.0979 | 103.1932
217.0979 | 103.3288
218.0979 | 103.0775
219.0979 | 105.9076
220.0979 | 107.3663
221.0979 | 107.2511
222.0979 | 107.6922
223.0979 | 107.8803
224.0979 | 107.2259
225.0979 | 107.9683
226.0979 | 109.9763
227.0979 | 108.7321
228.0979 | 107.1589
229.0979 | 105.0743
230.0979 | 105.8797
231.0979 | 107.5934
232.0979 | 108.2386
233.0979 | 107.7935
234.0979 | 108.9873
235.0979 | 107.8312
236.0979 | 107.1615
237.0979 | 107.9036
238.0979 | 111.4328
239.0979 | 111.7456
240.0979 | 111.5348
241.0979 | 112.5077
242.0979 | 111.7826
243.0979 | 110.7408
244.0979 | 111.2283
245.0979 | 109.262
246.0979 | 108.2856
247.0979 | 109.6501
248.0979 | 108.9112
249.0979 | 108.714
250.0979 | 109.8418
251.1135 | 110.716
252.0979 | 108.7906
253.0979 | 107.9683
254.0979 | 108.8986
255.0979 | 110.4748
256.0979 | 111.0705
257.0979 | 111.1623
258.0979 | 111.2592
259.0979 | 112.4195
260.0979 | 113.4415
261.0979 | 112.3183
262.0979 | 111.5805
263.0979 | 110.6552
264.0979 | 110.4851
265.0979 | 111.1619
266.0979 | 111.7948
267.0979 | 112.9275
268.0979 | 114.0588
269.0979 | 111.9906
270.0979 | 110.7091
271.0979 | 111.4761
272.0979 | 113.181
273.0979 | 113.6711
274.0979 | 114.6004
275.0979 | 115.5174
276.0979 | 115.6882
277.0979 | 115.2209
278.0979 | 114.8883
279.0979 | 115.0663
280.0979 | 115.011
281.0979 | 114.7964
282.0979 | 113.857
283.0979 | 114.2496
284.0979 | 115.1008
285.0979 | 114.8453
286.0979 | 113.7925
287.0979 | 115.6487
288.0979 | 116.1016
289.0979 | 118.2112
290.0979 | 120.6426
291.0979 | 120.0458
292.0979 | 119.8267
293.0979 | 119.5657
294.0979 | 120.3717
295.0979 | 122.7377
296.0979 | 122.2446
297.0979 | 121.7529
298.0979 | 120.9577
299.0979 | 120.8357
300.0979 | 120.765
301.0979 | 120.8051
302.0979 | 120.4835
303.0979 | 122.4999
304.0979 | 124.097
305.0979 | 124.1622
306.0979 | 122.2919
307.0979 | 122.1575
308.0979 | 121.3192
309.0979 | 121.1208
310.0979 | 121.0758
311.0979 | 122.0479
312.0979 | 123.0029
313.0979 | 122.1306
314.0979 | 122.8712
315.0979 | 121.4896
316.0979 | 121.4166
317.0979 | 121.9556
318.0979 | 121.4645
319.0979 | 123.4744
320.0979 | 124.862
321.0979 | 123.3342
322.0979 | 121.8357
323.0979 | 120.1634
324.0979 | 117.8637
325.0979 | 116.7117
326.0979 | 117.5858
327.0979 | 117.8972
328.0979 | 118.1728
329.0979 | 120.1049
330.0979 | 118.8987
331.0979 | 120.4715
332.0979 | 122.0624
333.0979 | 123.106
334.0979 | 124.1831
335.0979 | 125.7473
336.0979 | 125.0007
337.0979 | 124.3006
338.0979 | 123.9825
339.0979 | 124.2817
340.0979 | 125.2324
341.0979 | 125.6898
342.0979 | 126.849
343.0979 | 126.4871
344.0979 | 125.3778
345.0979 | 123.9444
346.0979 | 123.1213
347.0979 | 122.221
348.0979 | 121.331
349.0979 | 123.2025
350.0979 | 124.457
351.0979 | 125.3085
352.0979 | 124.497
353.0979 | 122.5681
354.0979 | 123.2116
355.0979 | 121.9329
356.0979 | 120.3367
357.0979 | 123.0441
358.0979 | 122.0677
359.0979 | 120.4105
360.0979 | 120.4535
361.0979 | 122.898
362.0979 | 122.8915
363.0979 | 120.8159
364.0979 | 119.9812
365.0979 | 121.5464
366.0979 | 121.7186
367.0979 | 122.0878
368.0979 | 123.6953
369.0979 | 123.6726
370.0979 | 125.1955
371.0979 | 124.7613
372.0979 | 127.4088
373.0979 | 127.8932
374.0979 | 127.6729
375.0979 | 127.3099
376.0979 | 128.2299
377.0979 | 129.9094
378.0979 | 130.0367
379.0979 | 131.2217
380.0979 | 132.0797
381.0979 | 134.679
382.0979 | 135.5843
383.0979 | 135.6244
384.0979 | 135.3584
385.0979 | 138.0016
386.0979 | 138.9162
387.0979 | 138.843
388.0979 | 139.9762
389.0979 | 139.7835
390.0979 | 141.9665
391.0979 | 142.045
392.0979 | 140.2903
393.0979 | 138.4191
394.0979 | 136.7977
395.0979 | 134.8196
396.0979 | 133.5635
397.0979 | 130.4928
398.0979 | 129.6665
399.0979 | 130.4579
400.0979 | 133.3321
401.0979 | 132.8613
402.0979 | 131.938
403.0979 | 136.1903
404.0979 | 137.0725
405.0979 | 137.2454
406.0979 | 136.0964
407.0979 | 134.8715
408.0979 | 134.0563
409.0979 | 135.5673
410.0979 | 136.807
411.0979 | 136.3602
412.0979 | 136.153
413.0979 | 138.2321
414.0979 | 139.0623
415.0979 | 140.7922
416.0979 | 141.0607
417.0979 | 142.4797
418.0979 | 143.2541
419.0979 | 143.9784
420.0979 | 146.235
421.0979 | 147.2895
422.0979 | 148.5042
423.0979 | 151.4904
424.0979 | 155.2442
425.0979 | 155.5251
426.0979 | 156.4056
427.0979 | 158.4126
428.0979 | 158.3931
429.0979 | 158.3214
430.0979 | 158.949
431.0979 | 161.6839
432.0979 | 161.2102
433.0979 | 161.3612
434.0979 | 163.5499
435.0979 | 160.4741
436.0979 | 156.7762
437.1135 | 159.8811
438.0979 | 162.3111
439.0979 | 162.8025
440.0979 | 164.9404
441.0979 | 164.9161
442.0979 | 166.293
443.0979 | 167.1137
444.0979 | 166.3321
445.0979 | 164.9619
446.0979 | 164.3308
447.0979 | 161.0404
448.0979 | 163.6486
449.0979 | 164.5486
450.0979 | 164.2959
451.0979 | 162.5482
452.0979 | 157.5197
453.0979 | 155.7443
454.0979 | 153.6323
455.0979 | 151.7936
456.0979 | 152.5
457.0979 | 151.9202
458.0979 | 150.6504
459.0979 | 150.523
460.0979 | 152.1559
461.0979 | 149.5902
462.0979 | 147.3373
463.0979 | 149.9062
464.0979 | 150.4883
465.0979 | 156.1747
466.0979 | 162.7087
467.0979 | 161.9675
468.0979 | 163.3205
469.0979 | 168.0185
470.0979 | 172.0243
471.0979 | 172.0618
472.0979 | 170.5201
473.0979 | 170.7034
474.0979 | 171.8073
475.0979 | 171.1958
476.0979 | 170.3841
477.0979 | 169.3692
478.0979 | 166.6631
479.0979 | 166.483
480.0979 | 164.3063
481.0979 | 162.8078
482.0979 | 160.6907
483.0979 | 158.4203
484.0979 | 157.816
485.0979 | 156.0007
486.0979 | 155.8719
487.0979 | 156.3057
488.0979 | 156.6672
489.0979 | 156.7158
490.0979 | 154.268
491.0979 | 155.6894
492.0979 | 157.4825
493.0979 | 157.8756
494.0979 | 158.3467
495.0979 | 160.8357
496.0979 | 164.3651
497.0979 | 162.8321
498.0979 | 162.9551
499.0979 | 163.5963
500.0979 | 170.2753
501.0979 | 170.8746
502.0979 | 169.7726
503.0979 | 167.9022
504.0979 | 165.9217
505.0979 | 171.8546
506.0979 | 172.9399
507.0979 | 174.1997
508.0979 | 173.4895
509.0979 | 175.3996
510.0979 | 174.7393
511.0979 | 176.5056
512.0979 | 172.8097
513.0979 | 170.1092
514.0979 | 168.3375
515.0979 | 168.3369
516.0979 | 168.302
517.0979 | 173.7488
518.0979 | 177.0777
519.0979 | 178.12
520.0979 | 177.6565
521.0979 | 178.7892
522.0979 | 177.0016
523.0979 | 176.4848
524.0979 | 179.2689
525.0979 | 178.1297
526.0979 | 178.5382
527.0979 | 181.4223
528.0979 | 178.5054
529.0979 | 175.1131
530.0979 | 175.4089
531.0979 | 172.3473
532.0979 | 178.3665
533.0979 | 178.0875
534.0979 | 176.961
535.0979 | 181.4752
536.0979 | 184.5115
537.0979 | 184.6748
538.0979 | 183.269
539.0979 | 183.5456
540.0979 | 181.2394
541.0979 | 178.434
542.0979 | 177.3456
543.0979 | 176.1296
544.0979 | 174.4551
545.0979 | 172.4953
546.0979 | 168.3126
547.0979 | 165.6505
548.0979 | 165.6028
549.0979 | 167.5097
550.0979 | 167.1565
551.0979 | 169.0736
552.0979 | 167.2478
553.0979 | 169.9957
554.0979 | 169.9046
555.0979 | 169.187
556.0979 | 167.7387
557.0979 | 166.7174
558.0979 | 168.6547
559.0979 | 172.1463
560.0979 | 173.9354
561.0979 | 176.6298
562.0979 | 177.9977
563.0979 | 178.4447
564.0979 | 178.6592
565.0979 | 178.9003
566.0979 | 179.6358
567.0979 | 181.1233
568.0979 | 181.77
569.0979 | 182.6861
570.0979 | 184.2505
571.0979 | 183.9321
572.0979 | 182.3587
573.0979 | 180.8138
574.0979 | 179.5701
575.0979 | 181.0217
576.0979 | 181.8082
577.0979 | 179.8211
578.0979 | 177.7269
579.0979 | 176.833
580.0979 | 176.3414
581.0979 | 177.4456
582.0979 | 176.5282
583.0979 | 176.6474
584.0979 | 177.0787
585.0979 | 175.7917
586.0979 | 173.6642
587.0979 | 172.2189
588.0979 | 171.9191
589.0979 | 171.5415
590.0979 | 169.4017
591.0979 | 168.7261
592.0979 | 168.6168
593.0979 | 169.6993
594.0979 | 169.5453
595.0979 | 171.1943
596.0979 | 172.2528
597.0979 | 174.39
598.0979 | 173.948
599.0979 | 172.7132
600.0979 | 172.1151
601.0979 | 170.5016
602.0979 | 169.059
603.0979 | 168.4785
604.0979 | 168.2502
605.0979 | 168.2667
606.0979 | 166.6368
607.0979 | 169.3544
608.0979 | 168.588
609.0979 | 168.1826
610.0979 | 169.0789
611.0979 | 169.9191
612.0979 | 168.8497
613.0979 | 168.7303
614.0979 | 169.9034
615.0979 | 169.8558
616.0979 | 166.6856
617.0979 | 165.1069
618.0979 | 166.127
619.0979 | 166.8886
620.0979 | 166.6794
621.0979 | 168.9633
622.0979 | 167.5557
623.0979 | 164.4076
624.0979 | 164.1642
625.0979 | 164.2084
626.0979 | 164.3791
627.0979 | 163.696
628.0979 | 163.2695
629.0979 | 161.7368
630.0979 | 160.0754
631.0979 | 159.1778
632.0979 | 157.4002
633.0979 | 155.8028
634.0979 | 158.663
635.0979 | 160.585
636.0979 | 162.6593
637.0979 | 162.8242
638.0979 | 162.4346
639.0979 | 163.1345
640.0979 | 165.2414
641.0979 | 164.8487
642.0979 | 165.4158
643.0979 | 162.3062
644.0979 | 161.4739
645.0979 | 160.2767
646.0979 | 161.8815
647.0979 | 159.2961
648.0979 | 158.4288
649.0979 | 160.5935
650.0979 | 159.0614
651.0979 | 157.0191
652.0979 | 156.7014
653.0979 | 161.03
654.0979 | 161.8869
655.0979 | 161.9469
656.0979 | 158.7877
657.1135 | 155.62
658.0979 | 155.3134
659.0979 | 154.6623
660.0979 | 155.1004
661.0979 | 156.9018
662.0979 | 157.6368
663.0979 | 157.5334
664.0979 | 160.2006
665.0979 | 160.5961
666.0979 | 161.0209
667.0979 | 161.1058
668.0979 | 162.2884
669.0979 | 161.594
670.0979 | 162.6266
671.0979 | 161.2426
672.0979 | 162.1851
673.0979 | 163.0692
674.0979 | 164.2701
675.0979 | 163.796
676.0979 | 164.5886
677.0979 | 162.8974
678.0979 | 161.9164
679.0979 | 163.4864
680.0979 | 162.1678
681.0979 | 162.2342
682.0979 | 165.8203
683.0979 | 165.0931
684.0979 | 164.8503
685.0979 | 166.2024
686.0979 | 164.3985
687.0979 | 159.9237
688.0979 | 158.7074
689.0979 | 157.2014
690.0979 | 154.1279
691.0979 | 155.6221
692.0979 | 155.0468
693.0979 | 156.0698
694.0979 | 154.1083
695.0979 | 155.1673
696.0979 | 156.0136
697.0979 | 159.5345
698.0979 | 161.7843
699.0979 | 161.1719
700.0979 | 159.9982
701.0979 | 158.2796
702.0979 | 156.5695
703.0979 | 158.5213
704.0979 | 157.88
705.0979 | 158.5808
706.0979 | 160.4657
707.0979 | 161.5839
708.0979 | 158.846
709.0979 | 156.7666
710.0979 | 157.6205
711.0979 | 156.3322
712.0979 | 154.1539
713.0979 | 153.3074
714.0979 | 157.3676
715.0979 | 155.8331
716.0979 | 158.5565
717.1135 | 156.9456
718.0979 | 153.3738
719.0979 | 152.7178
720.0979 | 152.9215
721.0979 | 153.28
722.0979 | 154.6625
723.0979 | 157.7781
724.0979 | 155.3844
725.0979 | 155.6549
726.0979 | 155.1586
727.0979 | 154.7434
728.0979 | 156.2466
729.0979 | 156.0554
730.0979 | 158.8649
731.0979 | 159.9008
732.0979 | 162.6418
733.0979 | 161.2305
734.0979 | 159.3202
735.0979 | 158.3314
736.0979 | 159.2456
737.0979 | 158.1385
738.0979 | 158.0219
739.0979 | 157.4052
740.0979 | 156.7849
741.0979 | 155.8713
742.0979 | 154.4381
743.0979 | 155.3523
744.0979 | 154.8375
745.0979 | 155.7744
746.0979 | 152.7954
747.0979 | 153.0061
748.0979 | 153.0975
749.0979 | 153.2988
750.0979 | 152.912
751.0979 | 151.6754
752.0979 | 151.4288
753.0979 | 152.1393
754.0979 | 153.1061
755.0979 | 153.5096
756.0979 | 154.7201
757.0979 | 154.0736
758.0979 | 151.6135
759.0979 | 150.0054
760.0979 | 148.0541
761.0979 | 146.1714
762.0979 | 144.833
763.0979 | 142.4319
764.0979 | 143.0349
765.0979 | 142.9338
766.0979 | 142.9624
767.0979 | 143.2015
768.0979 | 142.8798
769.0979 | 142.0324
770.0979 | 141.2218
771.0979 | 140.6634
772.0979 | 140.3087
773.0979 | 138.8218
774.0979 | 139.3904
775.0979 | 139.1309
776.0979 | 146.1643
777.1135 | 146.7585
778.0979 | 152.605
779.0979 | 155.1085
780.0979 | 157.0106
781.0979 | 159.1724
782.0979 | 158.5116
783.0979 | 156.7879
784.0979 | 156.3877
785.0979 | 156.1791
786.0979 | 155.9201
787.0979 | 156.3672
788.0979 | 158.0611
789.0979 | 157.2709
790.0979 | 157.0604
791.0979 | 156.5127
792.0979 | 157.3817
793.0979 | 156.3522
794.0979 | 158.5625
795.0979 | 156.4754
796.0979 | 158.5698
797.0979 | 161.1861
798.0979 | 160.495
799.0979 | 162.964
800.0979 | 161.6396
801.0979 | 161.4148
802.0979 | 163.5775
803.0979 | 163.9714
804.0979 | 165.2394
805.0979 | 165.3338
806.0979 | 165.4511
807.0979 | 165.2706
808.0979 | 163.7622
809.0979 | 163.4799
810.0979 | 164.89
811.0979 | 164.7708
812.0979 | 165.6447
813.0979 | 162.8727
814.0979 | 161.9649
815.0979 | 161.8984
816.0979 | 161.3514
817.0979 | 160.7276
818.0979 | 161.2636
819.0979 | 160.3888
820.0979 | 161.4138
821.0979 | 160.8699
822.0979 | 159.1156
823.0979 | 160.6317
824.0979 | 158.3286
825.0979 | 156.52
826.0979 | 155.7871
827.0979 | 154.6846
828.0979 | 156.4901
829.0979 | 158.0984
830.0979 | 157.263
831.0979 | 156.8873
832.0979 | 153.9804
833.0979 | 152.4252
834.0979 | 153.112
835.0979 | 153.262
836.0979 | 152.0123
837.0979 | 150.095
838.0979 | 150.4925
839.0979 | 149.9291
840.0979 | 149.0446
841.0979 | 149.4936
842.0979 | 149.8943
843.0979 | 150.6511
844.0979 | 148.3864
845.0979 | 146.2625
846.0979 | 145.215
847.0979 | 148.0673
848.0979 | 148.3011
849.0979 | 147.8196
850.0979 | 146.7767
851.0979 | 146.907
852.0979 | 149.6075
853.0979 | 154.2994
854.0979 | 153.2131
855.0979 | 153.7399
856.0979 | 155.5653
857.0979 | 158.0017
858.0979 | 157.1177
859.0979 | 158.1021
860.0979 | 157.7165
861.0979 | 155.3652
862.0979 | 153.5208
863.0979 | 153.1704
864.0979 | 151.1862
865.0979 | 149.0905
866.0979 | 148.6394
867.0979 | 150.8313
868.0979 | 148.5429
869.0979 | 147.6058
870.0979 | 149.701
871.0979 | 151.1105
872.0979 | 151.0995
873.0979 | 149.4428
874.0979 | 149.3944
875.0979 | 148.0629
876.0979 | 148.087
877.0979 | 148.9627
878.0979 | 147.7368
879.0979 | 146.5891
880.0979 | 146.6354
881.0979 | 144.7403
882.0979 | 145.1069
883.0979 | 143.8097
884.0979 | 143.3575
885.0979 | 143.1084
886.0979 | 141.9617
887.0979 | 141.7777
888.0979 | 143.0188
889.0979 | 144.1914
890.0979 | 145.4042
891.0979 | 145.2066
892.0979 | 147.2506
893.0979 | 148.203
894.0979 | 149.7113
895.0979 | 148.2304
896.0979 | 146.0397
897.1135 | 145.8469
898.0979 | 144.8858
899.0979 | 146.2823
900.0979 | 147.8566
901.0979 | 147.686
902.0979 | 148.5843
903.0979 | 148.8908
904.0979 | 150.5415
905.0979 | 153.6985
906.0979 | 151.3176
907.0979 | 148.7792
908.0979 | 148.3647
909.0979 | 148.552
910.0979 | 150.7849
911.0979 | 149.8191
912.0979 | 148.3728
913.0979 | 149.2486
914.0979 | 149.9954
915.0979 | 151.5581
916.0979 | 149.9228
917.0979 | 148.7075
918.0979 | 149.0012
919.0979 | 150.4697
920.0979 | 151.1554
921.0979 | 150.5643
922.0979 | 150.6032
923.0979 | 154.8074
924.0979 | 156.5089
925.0979 | 157.2629
926.0979 | 157.5581
927.0979 | 158.7529
928.0979 | 159.6159
929.0979 | 158.756
930.0979 | 159.6799
931.0979 | 159.831
932.0979 | 160.5567
933.0979 | 160.0388
934.0979 | 159.1628
935.0979 | 160.65
936.0979 | 161.0901
937.0979 | 161.1126
938.0979 | 160.1672
939.0979 | 161.8177
940.0979 | 163.2679
941.0979 | 163.1007
942.0979 | 163.3504
943.0979 | 164.9363
944.0979 | 164.7518
945.0979 | 165.5742
946.0979 | 167.0528
947.0979 | 164.8288
948.0979 | 163.9235
949.0979 | 164.7551
950.0979 | 164.0929
951.0979 | 162.6358
952.0979 | 161.3224
953.0979 | 162.3085
954.0979 | 162.0647
955.0979 | 161.2024
956.0979 | 162.2173
957.0979 | 161.4185
958.0979 | 159.428
959.0979 | 159.2888
960.0979 | 157.3058
961.0979 | 157.7971
962.0979 | 156.9904
963.0979 | 156.8055
964.0979 | 159.8713
965.0979 | 160.6844
966.0979 | 160.4333
967.0979 | 160.217
968.0979 | 162.8896
969.0979 | 162.7906
970.0979 | 162.5925
971.0979 | 162.6439
972.0979 | 161.5221
973.0979 | 159.5123
974.0979 | 158.9645
975.0979 | 161.6068
976.0979 | 163.9845
977.0979 | 164.1155
978.0979 | 163.7783
979.0979 | 162.8354
980.0979 | 163.2348
981.0979 | 162.2652
982.0979 | 163.4933
983.0979 | 163.448
984.0979 | 165.8618
985.0979 | 165.8298
986.0979 | 167.4568
987.0979 | 167.2458
988.0979 | 166.2386
989.0979 | 166.2786
990.0979 | 165.7928
991.0979 | 164.9164
992.0979 | 165.105
993.0979 | 164.8765
994.0979 | 164.8886
995.0979 | 165.4657
996.0979 | 165.2625
997.0979 | 165.3023
998.0979 | 163.9889
999.0979 | 165.1749
1000.0979 | 164.6455
1001.0979 | 162.6712
1002.0979 | 161.8622
1003.0979 | 161.8079
1004.0979 | 160.8511
1005.0979 | 160.4784
1006.0979 | 161.5377
1007.0979 | 161.9885
1008.0979 | 162.8617
1009.0979 | 163.6157
1010.0979 | 164.3656
1011.0979 | 163.968
1012.0979 | 165.0468
1013.0979 | 166.7475
1014.0979 | 164.5132
1015.0979 | 163.2241
1016.0979 | 163.0555
1017.0979 | 164.1307
1018.0979 | 165.6112
1019.0979 | 163.9536
1020.0979 | 163.582