## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number Contingency 2 - Circuit Simulator Data Only
Test Date: | 2010-03-29
DCSim DAQ Start Time | 11:36
DCSim Time for Synchronization | 11:36
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 11:35
Heat Source Start Time | 12:10
DCSim Offset | 0:34 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2055 | seconds
Heat Source Offset | 0:36 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2141 | seconds
Heat Source Stop Time | 12:27
Test Duration | 0:17 | hour:minutes:seconds
| 1005 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPO/XLPO, 12 AWG, 7/C |  | Cable thermocouples were not used for this test. | Channel 2 represents the air temperature in the center of the tray located in B Position. It is labeled as "B Position - Middle".
SWGR Trip | XLPO/XLPO, 12 AWG, 7/C |  | Cable thermocouples were not used for this test. | Channel 2 represents the air temperature in the center of the tray located in B Position. It is labeled as "B Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.32812 | 122.6715 | -61.2442 | 61.2396 | -0.003128 | 0.046952 | 0.037803 | -0.0021235 | -0.0055179 | 0.066048 | 0.064234 | 61.3495 | 61.1526 | -61.2122 | 61.1343 | -61.2671 | -61.441 | -0.004578 | -0.059509 | 61.2305 | -61.3953 | 0.032044 | -0.086975 | 122.5937 | 122.3785 | -122.5067 | -0.15106 | -0.009155 | 122.5616 | 61.2396 | 61.1847 | -0.022888 | 122.3969 | 122.5937 | 122.4747 | -0.19684 | -0.15106 | 122.3969 | 122.5937 | -0.19684 | -0.022888 | 122.4747 | -122.4518 | -122.6349
0.67188 | 122.7722 | -61.1893 | 61.2122 | 0.01213 | 0.042893 | 0.035453 | -0.0029779 | -0.0035953 | 0.065834 | 0.063807 | 61.4227 | 61.1252 | -61.1755 | 61.2213 | -61.1481 | -61.3129 | -0.17853 | 0.059509 | 61.1847 | -61.3586 | 0.013733 | -0.086975 | 122.612 | 122.4106 | -122.3602 | -0.16937 | -0.027466 | 122.5983 | 61.0107 | 61.2488 | 0.041199 | 122.3145 | 122.612 | 122.374 | -0.1236 | -0.16937 | 122.3145 | 122.612 | -0.1236 | 0.041199 | 122.374 | -122.3877 | -122.5708
1.6719 | 122.6486 | -61.2305 | 61.2534 | 0.0045015 | 0.046098 | 0.041221 | -0.0021235 | -0.0046633 | 0.067543 | 0.063166 | 61.377 | 61.1755 | -61.2076 | 61.1572 | -61.2442 | -61.4227 | 0.009155 | -0.018311 | 61.2259 | -61.3998 | 0.022888 | -0.07782 | 122.6074 | 122.3877 | -122.4976 | -0.16937 | -0.027466 | 122.5845 | 61.2396 | 61.2122 | -0.013733 | 122.406 | 122.6074 | 122.4564 | -0.19226 | -0.16937 | 122.406 | 122.6074 | -0.19226 | -0.013733 | 122.4564 | -122.4609 | -122.6532
2.6719 | 122.6669 | -61.2396 | 61.235 | -0.003128 | 0.04503 | 0.038657 | -0.0014825 | -0.0046633 | 0.065194 | 0.06338 | 61.3678 | 61.1481 | -61.203 | 61.1343 | -61.2442 | -61.4136 | -0.032043 | -0.036621 | 61.2396 | -61.4044 | 0.036621 | -0.086975 | 122.6074 | 122.374 | -122.4792 | -0.16479 | 0.004578 | 122.5708 | 61.2076 | 61.203 | -0.004578 | 122.3877 | 122.6074 | 122.4792 | -0.17395 | -0.16479 | 122.3877 | 122.6074 | -0.17395 | -0.004578 | 122.4792 | -122.438 | -122.6395
3.6719 | 122.6624 | -61.1984 | 61.235 | -0.018387 | 0.043107 | 0.038444 | 1.2902e-05 | -0.0046633 | 0.064553 | 0.063593 | 61.3586 | 61.1572 | -61.2396 | 61.1206 | -61.2625 | -61.4227 | -0.004578 | -0.045776 | 61.2534 | -61.4044 | -0.041199 | -0.077819 | 122.5571 | 122.319 | -122.4976 | -0.20599 | 0.018311 | 122.5983 | 61.1938 | 61.1526 | -0.064087 | 122.3557 | 122.5571 | 122.4518 | -0.2243 | -0.20599 | 122.3557 | 122.5571 | -0.2243 | -0.064087 | 122.4518 | -122.4747 | -122.6395
4.6719 | 122.6898 | -61.235 | 61.2671 | -0.010758 | 0.045243 | 0.036735 | 0.0008673 | -0.0046633 | 0.066048 | 0.064021 | 61.4319 | 61.171 | -61.203 | 61.1938 | -61.2122 | -61.3998 | -0.013733 | 0.009155 | 61.235 | -61.4319 | 0.032043 | -0.096131 | 122.6669 | 122.4289 | -122.4792 | -0.19684 | -0.032044 | 122.6349 | 61.2213 | 61.2442 | 0.022888 | 122.406 | 122.6669 | 122.4701 | -0.1648 | -0.19684 | 122.406 | 122.6669 | -0.1648 | 0.022888 | 122.4701 | -122.4701 | -122.699
5.6719 | 122.6852 | -61.2305 | 61.2305 | -0.010758 | 0.044389 | 0.036094 | -0.0044733 | -0.0040225 | 0.066262 | 0.06573 | 61.3815 | 61.1755 | -61.2213 | 61.1389 | -61.2396 | -61.3998 | -0.082397 | -0.032043 | 61.2167 | -61.3953 | 0.009156 | -0.054932 | 122.612 | 122.3694 | -122.4701 | -0.16479 | -0.013733 | 122.6028 | 61.1481 | 61.1984 | -0.009155 | 122.406 | 122.612 | 122.4472 | -0.16937 | -0.16479 | 122.406 | 122.612 | -0.16937 | -0.009155 | 122.4472 | -122.4518 | -122.6257
6.6719 | 122.6898 | -61.235 | 61.2579 | -0.003128 | 0.044389 | 0.040366 | -0.0029779 | -0.0050907 | 0.068184 | 0.065302 | 61.3678 | 61.1664 | -61.1984 | 61.1526 | -61.2396 | -61.3861 | -0.045776 | -0.027466 | 61.2259 | -61.3907 | 0.036621 | -0.091553 | 122.6028 | 122.3877 | -122.4976 | -0.15564 | -0.032044 | 122.5662 | 61.1893 | 61.2076 | -0.004578 | 122.4014 | 122.6028 | 122.4609 | -0.15106 | -0.15564 | 122.4014 | 122.6028 | -0.15106 | -0.004578 | 122.4609 | -122.4564 | -122.6486
7.6719 | 122.6578 | -61.2213 | 61.2396 | -0.010758 | 0.043962 | 0.04058 | -0.0027643 | -0.0057315 | 0.064339 | 0.064021 | 61.3403 | 61.1481 | -61.2167 | 61.1252 | -61.2717 | -61.4502 | 0 | -0.059509 | 61.2488 | -61.4273 | 0.004577 | -0.091553 | 122.5616 | 122.3465 | -122.5113 | -0.20599 | 0.009155 | 122.5571 | 61.2213 | 61.1618 | -0.050354 | 122.3694 | 122.5616 | 122.4701 | -0.22888 | -0.20599 | 122.3694 | 122.5616 | -0.22888 | -0.050354 | 122.4701 | -122.4564 | -122.6669
8.6719 | 122.6669 | -61.235 | 61.2534 | -0.010758 | 0.044389 | 0.037589 | -0.0023371 | -0.0042361 | 0.065621 | 0.064875 | 61.3907 | 61.1389 | -61.2213 | 61.1572 | -61.2305 | -61.4227 | -0.004578 | -0.018311 | 61.2122 | -61.4227 | 0.013733 | -0.11444 | 122.6257 | 122.3923 | -122.4838 | -0.18768 | -0.041199 | 122.612 | 61.2305 | 61.2167 | 0.004577 | 122.374 | 122.6257 | 122.4472 | -0.18768 | -0.18768 | 122.374 | 122.6257 | -0.18768 | 0.004577 | 122.4472 | -122.4747 | -122.6761
9.6719 | 122.6669 | -61.2167 | 61.2488 | -0.003128 | 0.044816 | 0.043143 | -0.0002009 | -0.0027407 | 0.065407 | 0.064448 | 61.3998 | 61.1526 | -61.2305 | 61.1481 | -61.2396 | -61.4044 | -0.013733 | -0.004578 | 61.235 | -61.409 | -0.013733 | -0.09613 | 122.6166 | 122.3648 | -122.4884 | -0.19226 | -0.013733 | 122.6303 | 61.203 | 61.2122 | -0.022888 | 122.3694 | 122.6166 | 122.4518 | -0.18768 | -0.19226 | 122.3694 | 122.6166 | -0.18768 | -0.022888 | 122.4518 | -122.4792 | -122.6578
10.6719 | 122.7676 | -61.1435 | 61.2488 | -0.018387 | 0.041612 | 0.037589 | -0.010668 | -0.0061587 | 0.065194 | 0.062739 | 61.4456 | 61.1343 | -61.1526 | 61.2396 | -61.1526 | -61.2808 | -0.073242 | 0.11902 | 61.2305 | -61.3678 | -0.009155 | -0.11444 | 122.5891 | 122.3831 | -122.4014 | -0.2243 | -0.01831 | 122.5983 | 61.0703 | 61.2625 | -0.009155 | 122.2778 | 122.5891 | 122.374 | -0.13733 | -0.2243 | 122.2778 | 122.5891 | -0.13733 | -0.009155 | 122.374 | -122.4014 | -122.6166
11.6719 | 122.6395 | -61.2534 | 61.2488 | 0.0045015 | 0.046311 | 0.037803 | -0.0023371 | -0.0057315 | 0.067757 | 0.065943 | 61.3586 | 61.171 | -61.2305 | 61.1343 | -61.2625 | -61.4548 | 0.009155 | -0.036621 | 61.235 | -61.4365 | 0.022888 | -0.07782 | 122.612 | 122.3877 | -122.5113 | -0.1831 | -0.013733 | 122.5891 | 61.2625 | 61.2167 | -0.009155 | 122.4243 | 122.612 | 122.4884 | -0.20142 | -0.1831 | 122.4243 | 122.612 | -0.20142 | -0.009155 | 122.4884 | -122.4792 | -122.6852
12.6719 | 122.6852 | -61.2213 | 61.2396 | -0.018387 | 0.044389 | 0.041221 | -0.0002009 | -0.0059451 | 0.064766 | 0.064448 | 61.4319 | 61.171 | -61.2076 | 61.1847 | -61.2259 | -61.3998 | -0.022888 | 0.027466 | 61.2259 | -61.4319 | 0.013732 | -0.068665 | 122.6532 | 122.406 | -122.4655 | -0.21057 | -0.013733 | 122.6395 | 61.1984 | 61.2488 | -0.004578 | 122.3923 | 122.6532 | 122.4472 | -0.17853 | -0.21057 | 122.3923 | 122.6532 | -0.17853 | -0.004578 | 122.4472 | -122.4472 | -122.6715
13.6719 | 122.6532 | -61.2396 | 61.2854 | -0.003128 | 0.044389 | 0.042716 | -0.0014825 | -0.0050907 | 0.066262 | 0.063593 | 61.3861 | 61.1526 | -61.2213 | 61.1343 | -61.2671 | -61.4365 | 0.009155 | -0.036621 | 61.2671 | -61.3953 | 0.018311 | -0.13275 | 122.6257 | 122.374 | -122.5525 | -0.15564 | -0.01831 | 122.6074 | 61.2488 | 61.203 | -0.027466 | 122.3923 | 122.6257 | 122.5067 | -0.19684 | -0.15564 | 122.3923 | 122.6257 | -0.19684 | -0.027466 | 122.5067 | -122.5067 | -122.6807
14.6719 | 122.6852 | -61.2259 | 61.2305 | -0.018387 | 0.045671 | 0.040793 | -0.0036187 | -0.0046633 | 0.06733 | 0.064661 | 61.377 | 61.1526 | -61.2213 | 61.1435 | -61.2213 | -61.3953 | -0.073242 | -0.027466 | 61.2167 | -61.4182 | 0.004578 | -0.07782 | 122.6028 | 122.3694 | -122.4518 | -0.19226 | -0.013733 | 122.5983 | 61.1526 | 61.1984 | 0.004578 | 122.3785 | 122.6028 | 122.4426 | -0.16937 | -0.19226 | 122.3785 | 122.6028 | -0.16937 | 0.004578 | 122.4426 | -122.4518 | -122.6486
15.6719 | 122.699 | -61.1893 | 61.2305 | -0.010758 | 0.043321 | 0.036521 | -0.0021235 | -0.0061587 | 0.066475 | 0.063166 | 61.3953 | 61.1526 | -61.235 | 61.1572 | -61.2488 | -61.409 | -0.054932 | -0.032043 | 61.2396 | -61.3815 | -0.045776 | -0.07782 | 122.5845 | 122.3465 | -122.4792 | -0.19226 | 0.009155 | 122.6303 | 61.1343 | 61.1572 | -0.059509 | 122.3419 | 122.5845 | 122.4289 | -0.21973 | -0.19226 | 122.3419 | 122.5845 | -0.21973 | -0.059509 | 122.4289 | -122.4655 | -122.612
16.6719 | 122.6486 | -61.2213 | 61.2534 | -0.003128 | 0.046739 | 0.036521 | -0.0029779 | -0.0050907 | 0.067971 | 0.063166 | 61.377 | 61.1481 | -61.2305 | 61.1481 | -61.2488 | -61.4319 | -0.004578 | -0.009155 | 61.2259 | -61.4319 | -0.009156 | -0.10529 | 122.5983 | 122.3694 | -122.5021 | -0.21057 | -0.027466 | 122.6074 | 61.2167 | 61.2122 | -0.027466 | 122.3694 | 122.5983 | 122.4472 | -0.21057 | -0.21057 | 122.3694 | 122.5983 | -0.21057 | -0.027466 | 122.4472 | -122.4838 | -122.6852
17.6719 | 122.6624 | -61.2305 | 61.2396 | -0.003128 | 0.043962 | 0.035666 | -0.0049005 | -0.0038089 | 0.067971 | 0.062739 | 61.3907 | 61.1618 | -61.2442 | 61.1481 | -61.2534 | -61.4273 | -0.004578 | -0.018311 | 61.2488 | -61.4044 | -0.013733 | -0.07782 | 122.6212 | 122.3785 | -122.493 | -0.17395 | 0.009155 | 122.6349 | 61.2259 | 61.2122 | -0.022888 | 122.3923 | 122.6212 | 122.4792 | -0.19684 | -0.17395 | 122.3923 | 122.6212 | -0.19684 | -0.022888 | 122.4792 | -122.4838 | -122.644
18.6719 | 122.699 | -61.2259 | 61.2442 | -0.010758 | 0.045243 | 0.036948 | -0.0031915 | -0.0042361 | 0.067116 | 0.064661 | 61.3632 | 61.171 | -61.2076 | 61.1252 | -61.2488 | -61.4319 | -0.022888 | -0.036621 | 61.2442 | -61.4182 | 0.01831 | -0.073243 | 122.5891 | 122.3511 | -122.493 | -0.19226 | 0 | 122.5708 | 61.203 | 61.1893 | -0.022888 | 122.3969 | 122.5891 | 122.4701 | -0.20599 | -0.19226 | 122.3969 | 122.5891 | -0.20599 | -0.022888 | 122.4701 | -122.4518 | -122.6624
19.6719 | 122.6532 | -61.2213 | 61.2534 | -0.010758 | 0.044816 | 0.041434 | -0.0023371 | -0.0042361 | 0.066903 | 0.063807 | 61.3586 | 61.1618 | -61.1938 | 61.1114 | -61.2717 | -61.441 | -0.009155 | -0.045776 | 61.2305 | -61.441 | 0.027465 | -0.091553 | 122.58 | 122.3328 | -122.525 | -0.21973 | -0.022888 | 122.5525 | 61.2122 | 61.1755 | -0.050354 | 122.3831 | 122.58 | 122.4518 | -0.21973 | -0.21973 | 122.3831 | 122.58 | -0.21973 | -0.050354 | 122.4518 | -122.4472 | -122.6944
20.6719 | 122.8043 | -61.1206 | 61.2762 | -0.003128 | 0.042253 | 0.037162 | -0.0096003 | -0.0057315 | 0.068398 | 0.063593 | 61.4502 | 61.1618 | -61.1343 | 61.2717 | -61.0977 | -61.2671 | -0.082397 | 0.15564 | 61.235 | -61.3358 | -0.013733 | -0.11444 | 122.5708 | 122.3923 | -122.374 | -0.21515 | -0.041199 | 122.5845 | 61.0382 | 61.2762 | 0.022888 | 122.2824 | 122.5708 | 122.3557 | -0.14649 | -0.21515 | 122.2824 | 122.5708 | -0.14649 | 0.022888 | 122.3557 | -122.4106 | -122.612
21.6719 | 122.6486 | -61.2442 | 61.2305 | -0.010758 | 0.045243 | 0.039725 | -0.0008417 | -0.0063723 | 0.065834 | 0.063593 | 61.3678 | 61.1664 | -61.2259 | 61.1252 | -61.29 | -61.4319 | -0.009155 | -0.041199 | 61.2396 | -61.4273 | 0.018311 | -0.064087 | 122.612 | 122.3694 | -122.5204 | -0.1831 | 0.009155 | 122.5937 | 61.235 | 61.203 | -0.045776 | 122.4106 | 122.612 | 122.4838 | -0.18768 | -0.1831 | 122.4106 | 122.612 | -0.18768 | -0.045776 | 122.4838 | -122.4564 | -122.6578
22.6719 | 122.7493 | -61.2122 | 61.2305 | -0.010758 | 0.04268 | 0.038444 | -0.0023371 | -0.0063723 | 0.067116 | 0.063166 | 61.3953 | 61.1526 | -61.203 | 61.1938 | -61.203 | -61.3586 | -0.14648 | 0.032043 | 61.203 | -61.409 | 0.009155 | -0.07782 | 122.6074 | 122.406 | -122.4335 | -0.19684 | -0.027466 | 122.5983 | 61.0657 | 61.2442 | 0.009155 | 122.3648 | 122.6074 | 122.4152 | -0.14648 | -0.19684 | 122.3648 | 122.6074 | -0.14648 | 0.009155 | 122.4152 | -122.4335 | -122.6395
23.6719 | 122.7448 | -61.1893 | 61.2396 | -0.010758 | 0.044389 | 0.03823 | -0.0006281 | -0.0059451 | 0.06733 | 0.064875 | 61.3953 | 61.1343 | -61.2213 | 61.1893 | -61.203 | -61.3495 | -0.14191 | 0.032043 | 61.2259 | -61.4044 | -0.032043 | -0.10529 | 122.5845 | 122.3785 | -122.4426 | -0.21515 | -0.013733 | 122.6166 | 61.0474 | 61.2213 | -0.013733 | 122.3236 | 122.5845 | 122.4152 | -0.16022 | -0.21515 | 122.3236 | 122.5845 | -0.16022 | -0.013733 | 122.4152 | -122.4609 | -122.644
24.6719 | 122.7859 | -61.1755 | 61.1984 | -0.010758 | 0.040757 | 0.041221 | -0.0066095 | -0.0072269 | 0.066475 | 0.065302 | 61.4731 | 61.0657 | -61.1847 | 61.2762 | -61.1252 | -61.2854 | -0.1831 | 0.10071 | 61.1893 | -61.3358 | -0.009155 | -0.13275 | 122.6486 | 122.4518 | -122.3236 | -0.16022 | -0.009155 | 122.6578 | 60.9924 | 61.2762 | 0.050354 | 122.2412 | 122.6486 | 122.3648 | -0.10986 | -0.16022 | 122.2412 | 122.6486 | -0.10986 | 0.050354 | 122.3648 | -122.3831 | -122.5342
25.6719 | 122.7859 | -61.1847 | 61.2213 | 0.0045015 | 0.044389 | 0.042075 | -0.0040461 | -0.0063723 | 0.066262 | 0.063593 | 61.4777 | 61.1298 | -61.1755 | 61.2534 | -61.1389 | -61.2991 | -0.22888 | 0.07782 | 61.1847 | -61.3815 | 0.009155 | -0.091552 | 122.6624 | 122.438 | -122.3602 | -0.19684 | -0.036621 | 122.6532 | 60.9558 | 61.2625 | 0.045776 | 122.3145 | 122.6624 | 122.3694 | -0.11444 | -0.19684 | 122.3145 | 122.6624 | -0.11444 | 0.045776 | 122.3694 | -122.3969 | -122.6028
26.6719 | 122.6761 | -61.2167 | 61.2762 | -0.010758 | 0.04503 | 0.038657 | -0.0016961 | -0.0059451 | 0.066689 | 0.064875 | 61.3815 | 61.1481 | -61.2305 | 61.1481 | -61.2488 | -61.4319 | -0.018311 | -0.036621 | 61.2305 | -61.4456 | -0.013733 | -0.12817 | 122.5983 | 122.3648 | -122.525 | -0.22888 | -0.045776 | 122.612 | 61.1984 | 61.1801 | -0.032043 | 122.3648 | 122.5983 | 122.4472 | -0.21515 | -0.22888 | 122.3648 | 122.5983 | -0.21515 | -0.032043 | 122.4472 | -122.5067 | -122.7219
27.6719 | 122.6624 | -61.235 | 61.2671 | -0.003128 | 0.044816 | 0.036735 | -0.0006281 | -0.0053043 | 0.067116 | 0.062952 | 61.3724 | 61.1526 | -61.2076 | 61.1343 | -61.2579 | -61.4273 | -0.018311 | -0.036621 | 61.2396 | -61.3953 | 0.027465 | -0.11444 | 122.6074 | 122.3694 | -122.525 | -0.16022 | -0.027466 | 122.58 | 61.2167 | 61.1984 | -0.022889 | 122.3877 | 122.6074 | 122.4747 | -0.19226 | -0.16022 | 122.3877 | 122.6074 | -0.19226 | -0.022889 | 122.4747 | -122.4747 | -122.6624
28.6719 | 122.7676 | -61.1664 | 61.2122 | -0.010758 | 0.043321 | 0.037803 | -0.0053277 | -0.0082949 | 0.066475 | 0.065302 | 61.4639 | 61.1023 | -61.171 | 61.2579 | -61.1298 | -61.2946 | -0.16937 | 0.082397 | 61.1938 | -61.3724 | -0.004577 | -0.10986 | 122.6303 | 122.4243 | -122.3419 | -0.20599 | -0.01831 | 122.6349 | 60.997 | 61.2488 | 0.036621 | 122.2687 | 122.6303 | 122.3602 | -0.12817 | -0.20599 | 122.2687 | 122.6303 | -0.12817 | 0.036621 | 122.3602 | -122.3831 | -122.5845
29.6719 | 122.7859 | -61.1618 | 61.2717 | 0.01213 | 0.038194 | 0.036735 | -0.0070367 | -0.0097903 | 0.064553 | 0.06338 | 61.5097 | 61.1023 | -61.171 | 61.3358 | -61.0703 | -61.2488 | -0.073242 | 0.21057 | 61.235 | -61.3083 | -0.009155 | -0.16937 | 122.6715 | 122.4976 | -122.3419 | -0.14649 | -0.036621 | 122.6807 | 61.0886 | 61.3724 | 0.091553 | 122.2641 | 122.6715 | 122.3969 | -0.086975 | -0.14649 | 122.2641 | 122.6715 | -0.086975 | 0.091553 | 122.3969 | -122.4426 | -122.58
30.6719 | 122.7356 | -61.1938 | 61.2717 | -0.003128 | 0.041612 | 0.041007 | -0.0034051 | -0.0070133 | 0.06733 | 0.064448 | 61.4319 | 61.1252 | -61.1755 | 61.2259 | -61.1664 | -61.3174 | -0.1236 | 0.054932 | 61.2396 | -61.3541 | 0.018311 | -0.14648 | 122.6257 | 122.4197 | -122.438 | -0.16022 | -0.032043 | 122.6074 | 61.0703 | 61.2488 | 0.027466 | 122.319 | 122.6257 | 122.4335 | -0.1236 | -0.16022 | 122.319 | 122.6257 | -0.1236 | 0.027466 | 122.4335 | -122.4472 | -122.6257
31.6719 | 122.7768 | -61.1893 | 61.2396 | -0.003128 | 0.041612 | 0.040153 | -0.0008417 | -0.0063723 | 0.066689 | 0.064234 | 61.4319 | 61.116 | -61.1847 | 61.235 | -61.1664 | -61.3358 | -0.1831 | 0.059509 | 61.1847 | -61.377 | 0.004578 | -0.1236 | 122.6212 | 122.4243 | -122.406 | -0.18768 | -0.054932 | 122.6166 | 61.0062 | 61.2488 | 0.022888 | 122.3053 | 122.6212 | 122.374 | -0.14648 | -0.18768 | 122.3053 | 122.6212 | -0.14648 | 0.022888 | 122.374 | -122.4243 | -122.6166
32.6719 | 122.6761 | -61.2076 | 61.2534 | -0.003128 | 0.039689 | 0.041007 | 1.2902e-05 | -0.0076541 | 0.069039 | 0.06338 | 61.3861 | 61.1664 | -61.1984 | 61.1572 | -61.2442 | -61.4182 | -0.041199 | -0.032043 | 61.2396 | -61.4136 | 0.009156 | -0.086975 | 122.5937 | 122.3648 | -122.4976 | -0.20599 | -0.013733 | 122.5845 | 61.1664 | 61.1755 | -0.036621 | 122.374 | 122.5937 | 122.4472 | -0.21057 | -0.20599 | 122.374 | 122.5937 | -0.21057 | -0.036621 | 122.4472 | -122.4518 | -122.6669
33.6719 | 122.7722 | -61.1801 | 61.2259 | -0.003128 | 0.04268 | 0.036307 | -0.0016961 | -0.0050907 | 0.065407 | 0.065089 | 61.4365 | 61.0977 | -61.2076 | 61.235 | -61.1847 | -61.3358 | -0.15106 | 0.045776 | 61.2076 | -61.3678 | -0.027466 | -0.12817 | 122.6166 | 122.4152 | -122.4106 | -0.18768 | -0.01831 | 122.644 | 61.0291 | 61.2259 | -0.004577 | 122.2778 | 122.6166 | 122.3877 | -0.15564 | -0.18768 | 122.2778 | 122.6166 | -0.15564 | -0.004577 | 122.3877 | -122.4335 | -122.5937
34.6719 | 122.7905 | -61.1389 | 61.2625 | -0.003128 | 0.041612 | 0.033957 | -0.0096003 | -0.0070133 | 0.067116 | 0.064661 | 61.4502 | 61.0931 | -61.1618 | 61.29 | -61.0931 | -61.2534 | -0.07782 | 0.16479 | 61.2213 | -61.3083 | -0.022888 | -0.16937 | 122.5891 | 122.4289 | -122.3557 | -0.16937 | -0.041199 | 122.612 | 61.0611 | 61.3037 | 0.045776 | 122.2321 | 122.5891 | 122.3602 | -0.11444 | -0.16937 | 122.2321 | 122.5891 | -0.11444 | 0.045776 | 122.3602 | -122.4243 | -122.5708
35.6719 | 122.7493 | -61.1481 | 61.2259 | -0.003128 | 0.039903 | 0.033957 | -0.0014825 | -0.0072269 | 0.066903 | 0.064875 | 61.4639 | 61.1023 | -61.1618 | 61.2762 | -61.1298 | -61.2946 | -0.20142 | 0.086975 | 61.1984 | -61.3586 | -0.013733 | -0.1236 | 122.612 | 122.4243 | -122.3557 | -0.21057 | -0.027466 | 122.6257 | 60.9467 | 61.235 | 0.01831 | 122.2504 | 122.612 | 122.3465 | -0.14648 | -0.21057 | 122.2504 | 122.612 | -0.14648 | 0.01831 | 122.3465 | -122.3877 | -122.5845
36.6719 | 122.7356 | -61.1435 | 61.2625 | -0.018387 | 0.041184 | 0.037803 | -0.0046869 | -0.0089359 | 0.067543 | 0.062739 | 61.4319 | 61.1114 | -61.1893 | 61.2305 | -61.1526 | -61.3358 | -0.086975 | 0.073242 | 61.1984 | -61.3541 | -0.045776 | -0.15106 | 122.5754 | 122.374 | -122.4152 | -0.21057 | -0.064087 | 122.6212 | 61.0565 | 61.2167 | -0.009155 | 122.2549 | 122.5754 | 122.3419 | -0.19226 | -0.21057 | 122.2549 | 122.5754 | -0.19226 | -0.009155 | 122.3419 | -122.4518 | -122.6166
37.6719 | 122.7539 | -61.2305 | 61.2213 | -0.010758 | 0.042893 | 0.038016 | 0.0010809 | -0.0087223 | 0.065834 | 0.062312 | 61.3998 | 61.1298 | -61.2122 | 61.1938 | -61.1984 | -61.3815 | -0.13733 | 0 | 61.1893 | -61.3953 | 0.018311 | -0.091552 | 122.6303 | 122.4243 | -122.4197 | -0.16479 | -0.032043 | 122.612 | 61.0931 | 61.2305 | 0.032044 | 122.3602 | 122.6303 | 122.4197 | -0.15106 | -0.16479 | 122.3602 | 122.6303 | -0.15106 | 0.032044 | 122.4197 | -122.4335 | -122.6166
38.6719 | 122.6578 | -61.235 | 61.2625 | -0.010758 | 0.045243 | 0.037375 | 0.0021491 | -0.0061587 | 0.066475 | 0.06338 | 61.3724 | 61.1298 | -61.2442 | 61.1435 | -61.2671 | -61.441 | -0.027466 | -0.054932 | 61.2305 | -61.409 | -0.009156 | -0.13275 | 122.6074 | 122.3785 | -122.5296 | -0.17395 | -0.032043 | 122.6166 | 61.2076 | 61.1801 | -0.032044 | 122.3648 | 122.6074 | 122.4655 | -0.20599 | -0.17395 | 122.3648 | 122.6074 | -0.20599 | -0.032044 | 122.4655 | -122.5067 | -122.6715
39.6719 | 122.8363 | -61.1114 | 61.2534 | -0.003128 | 0.039475 | 0.037589 | -0.0057551 | -0.0076541 | 0.066048 | 0.063807 | 61.5005 | 61.1206 | -61.1298 | 61.3312 | -61.0657 | -61.2488 | -0.09613 | 0.19226 | 61.2259 | -61.3266 | -0.018311 | -0.13275 | 122.612 | 122.4426 | -122.319 | -0.21515 | -0.027466 | 122.6303 | 61.0153 | 61.3037 | 0.045776 | 122.2321 | 122.612 | 122.3373 | -0.13733 | -0.21515 | 122.2321 | 122.612 | -0.13733 | 0.045776 | 122.3373 | -122.3831 | -122.58
40.6719 | 122.7036 | -61.2259 | 61.2167 | -0.003128 | 0.042893 | 0.038016 | 0.0004401 | -0.0050907 | 0.067757 | 0.064021 | 61.3861 | 61.1206 | -61.2259 | 61.1847 | -61.235 | -61.3998 | -0.10986 | -0.036621 | 61.2122 | -61.3953 | 0 | -0.096131 | 122.612 | 122.4106 | -122.4518 | -0.16937 | -0.004578 | 122.612 | 61.116 | 61.1893 | -0.009155 | 122.3465 | 122.612 | 122.438 | -0.17395 | -0.16937 | 122.3465 | 122.612 | -0.17395 | -0.009155 | 122.438 | -122.4426 | -122.612
41.6719 | 122.6898 | -61.2259 | 61.2396 | 0.0045015 | 0.044389 | 0.040153 | -0.0002009 | -0.0053043 | 0.065834 | 0.06338 | 61.3953 | 61.1435 | -61.2167 | 61.1572 | -61.2259 | -61.4136 | -0.091553 | -0.041199 | 61.235 | -61.3907 | 0.009155 | -0.09613 | 122.6212 | 122.3831 | -122.4655 | -0.1648 | -0.004578 | 122.612 | 61.1343 | 61.1847 | 0 | 122.3694 | 122.6212 | 122.4609 | -0.18768 | -0.1648 | 122.3694 | 122.6212 | -0.18768 | 0 | 122.4609 | -122.4564 | -122.6303
42.6719 | 122.6807 | -61.2305 | 61.2442 | -0.003128 | 0.043321 | 0.03823 | -0.0014825 | -0.0080813 | 0.068184 | 0.066157 | 61.3724 | 61.171 | -61.2213 | 61.1526 | -61.2396 | -61.4227 | -0.054932 | -0.045776 | 61.2259 | -61.409 | 0.009156 | -0.073243 | 122.6028 | 122.3831 | -122.4838 | -0.17853 | -0.018311 | 122.5937 | 61.1755 | 61.1847 | -0.009155 | 122.4014 | 122.6028 | 122.4564 | -0.19226 | -0.17853 | 122.4014 | 122.6028 | -0.19226 | -0.009155 | 122.4564 | -122.4655 | -122.6532
43.6719 | 122.7905 | -61.1389 | 61.2213 | -0.010758 | 0.040757 | 0.035453 | -0.0023371 | -0.0035953 | 0.064339 | 0.064448 | 61.4731 | 61.0657 | -61.1893 | 61.2671 | -61.1481 | -61.2991 | -0.23804 | 0.091553 | 61.1801 | -61.3586 | -0.050354 | -0.15564 | 122.612 | 122.406 | -122.3694 | -0.21973 | -0.041198 | 122.6624 | 60.9009 | 61.2305 | -0.009155 | 122.2046 | 122.612 | 122.319 | -0.16022 | -0.21973 | 122.2046 | 122.612 | -0.16022 | -0.009155 | 122.319 | -122.4106 | -122.58
44.6719 | 122.7631 | -61.1389 | 61.2625 | -0.003128 | 0.040757 | 0.039298 | -0.0025507 | -0.0044497 | 0.066262 | 0.064448 | 61.4777 | 61.116 | -61.1664 | 61.2854 | -61.1206 | -61.2854 | -0.19684 | 0.10071 | 61.2122 | -61.3724 | -0.027466 | -0.14648 | 122.6166 | 122.4243 | -122.3831 | -0.23346 | -0.050354 | 122.644 | 60.9421 | 61.2396 | 0.018311 | 122.2549 | 122.6166 | 122.3511 | -0.14648 | -0.23346 | 122.2549 | 122.6166 | -0.14648 | 0.018311 | 122.3511 | -122.4289 | -122.6349
45.6562 | 122.6532 | -61.2305 | 61.2396 | -0.010758 | 0.044602 | 0.039939 | -0.0004145 | -0.0076541 | 0.067543 | 0.06573 | 61.3678 | 61.1435 | -61.2396 | 61.1252 | -61.2625 | -61.4227 | -0.027466 | -0.050354 | 61.2259 | -61.4136 | -0.009155 | -0.09613 | 122.5983 | 122.3557 | -122.5021 | -0.1831 | -0.013733 | 122.6074 | 61.203 | 61.1801 | -0.032043 | 122.374 | 122.5983 | 122.4564 | -0.19226 | -0.1831 | 122.374 | 122.5983 | -0.19226 | -0.032043 | 122.4564 | -122.4792 | -122.6532
46.6562 | 122.6486 | -61.235 | 61.2854 | 0.0045015 | 0.045243 | 0.036307 | 0.0004401 | -0.0055179 | 0.064125 | 0.064234 | 61.3724 | 61.1618 | -61.2076 | 61.1618 | -61.2579 | -61.4365 | 0.018311 | -0.054932 | 61.2442 | -61.4182 | 0.027465 | -0.1236 | 122.6074 | 122.3969 | -122.5433 | -0.18311 | -0.041198 | 122.58 | 61.2534 | 61.1801 | -0.022889 | 122.3969 | 122.6074 | 122.4792 | -0.20142 | -0.18311 | 122.3969 | 122.6074 | -0.20142 | -0.022889 | 122.4792 | -122.493 | -122.7036
47.6719 | 122.7768 | -61.2076 | 61.2167 | -0.003128 | 0.041825 | 0.036948 | -0.0016961 | -0.0042361 | 0.063485 | 0.068079 | 61.4365 | 61.0886 | -61.1893 | 61.2442 | -61.1435 | -61.3083 | -0.18768 | 0.064087 | 61.1847 | -61.3586 | 0.018311 | -0.12817 | 122.644 | 122.4518 | -122.3602 | -0.15106 | -0.032044 | 122.6257 | 61.0199 | 61.2717 | 0.064087 | 122.2961 | 122.644 | 122.3923 | -0.10071 | -0.15106 | 122.2961 | 122.644 | -0.10071 | 0.064087 | 122.3923 | -122.406 | -122.5754
48.6719 | 122.7905 | -61.1572 | 61.2259 | -0.010758 | 0.041184 | 0.035666 | -0.0044733 | -0.0053043 | 0.065194 | 0.065302 | 61.4502 | 61.0748 | -61.203 | 61.2671 | -61.1114 | -61.2854 | -0.21973 | 0.09613 | 61.1801 | -61.3632 | -0.045776 | -0.15106 | 122.6074 | 122.4243 | -122.3373 | -0.20599 | -0.045776 | 122.6532 | 60.9375 | 61.2534 | 0.045777 | 122.2321 | 122.6074 | 122.3373 | -0.12817 | -0.20599 | 122.2321 | 122.6074 | -0.12817 | 0.045777 | 122.3373 | -122.4289 | -122.5891
49.6719 | 122.7722 | -61.1572 | 61.2305 | 0.01213 | 0.040544 | 0.036307 | -0.0040461 | -0.0076541 | 0.065407 | 0.062952 | 61.4639 | 61.0474 | -61.1847 | 61.2579 | -61.116 | -61.2854 | -0.1831 | 0.091553 | 61.1801 | -61.3541 | -0.027465 | -0.18311 | 122.6212 | 122.4152 | -122.3465 | -0.19684 | -0.050354 | 122.6486 | 60.9741 | 61.2488 | 0.041199 | 122.2046 | 122.6212 | 122.3373 | -0.12817 | -0.19684 | 122.2046 | 122.6212 | -0.12817 | 0.041199 | 122.3373 | -122.4152 | -122.5845
50.6719 | 122.7264 | -61.1847 | 61.235 | -0.003128 | 0.039689 | 0.035666 | -0.0055413 | -0.0076541 | 0.066689 | 0.06338 | 61.4594 | 61.0931 | -61.1664 | 61.2488 | -61.1481 | -61.3037 | -0.14648 | 0.086975 | 61.1893 | -61.3403 | 0.01831 | -0.14191 | 122.644 | 122.4335 | -122.3831 | -0.15564 | -0.045776 | 122.6257 | 61.0382 | 61.2717 | 0.036621 | 122.2778 | 122.644 | 122.374 | -0.11902 | -0.15564 | 122.2778 | 122.644 | -0.11902 | 0.036621 | 122.374 | -122.4014 | -122.5754
51.6719 | 122.7905 | -61.1572 | 61.203 | -0.010758 | 0.042466 | 0.041862 | -0.0008417 | -0.0050907 | 0.066475 | 0.064234 | 61.4365 | 61.0977 | -61.1938 | 61.2488 | -61.1526 | -61.2991 | -0.20599 | 0.082397 | 61.1893 | -61.3495 | -0.036621 | -0.10529 | 122.5937 | 122.406 | -122.3557 | -0.19226 | -0.013733 | 122.6303 | 60.9512 | 61.2396 | 0.004578 | 122.2549 | 122.5937 | 122.3465 | -0.14191 | -0.19226 | 122.2549 | 122.5937 | -0.14191 | 0.004578 | 122.3465 | -122.3969 | -122.5525
52.6719 | 122.644 | -61.235 | 61.2671 | 0.0045015 | 0.043321 | 0.037375 | 0.0010809 | -0.0059451 | 0.065407 | 0.06573 | 61.3449 | 61.1435 | -61.2167 | 61.1435 | -61.2488 | -61.441 | -0.022888 | -0.068665 | 61.2122 | -61.4136 | 0.01831 | -0.1236 | 122.58 | 122.3785 | -122.5159 | -0.17853 | -0.054932 | 122.5616 | 61.2122 | 61.1664 | -0.013733 | 122.3785 | 122.58 | 122.4472 | -0.20599 | -0.17853 | 122.3785 | 122.58 | -0.20599 | -0.013733 | 122.4472 | -122.4838 | -122.6807
53.6719 | 122.6349 | -61.203 | 61.2625 | -0.010758 | 0.043321 | 0.039725 | 0.0015081 | -0.0055179 | 0.066475 | 0.061884 | 61.3632 | 61.1435 | -61.1984 | 61.1298 | -61.2625 | -61.4548 | 0 | -0.036621 | 61.2396 | -61.4182 | 0.004578 | -0.11902 | 122.5662 | 122.3328 | -122.525 | -0.21515 | -0.022888 | 122.5616 | 61.203 | 61.1664 | -0.059509 | 122.3465 | 122.5662 | 122.4426 | -0.25177 | -0.21515 | 122.3465 | 122.5662 | -0.25177 | -0.059509 | 122.4426 | -122.4609 | -122.6807
54.6719 | 122.7036 | -61.2305 | 61.2534 | -0.010758 | 0.044175 | 0.035239 | -0.0044733 | -0.0033817 | 0.063912 | 0.06573 | 61.3678 | 61.1481 | -61.203 | 61.1755 | -61.2213 | -61.4044 | -0.091553 | -0.018311 | 61.2259 | -61.4182 | 0.027466 | -0.10529 | 122.5983 | 122.406 | -122.4747 | -0.18768 | -0.027466 | 122.5708 | 61.1389 | 61.2122 | 0.009156 | 122.3785 | 122.5983 | 122.4564 | -0.17395 | -0.18768 | 122.3785 | 122.5983 | -0.17395 | 0.009156 | 122.4564 | -122.4564 | -122.6715
55.6719 | 122.6715 | -61.203 | 61.235 | -0.010758 | 0.043748 | 0.037803 | -0.0031915 | -0.0059451 | 0.065834 | 0.066798 | 61.3541 | 61.1664 | -61.2259 | 61.1389 | -61.2442 | -61.4227 | -0.045776 | -0.045776 | 61.203 | -61.409 | -0.022888 | -0.068664 | 122.5571 | 122.3419 | -122.4792 | -0.20599 | -0.032043 | 122.58 | 61.1572 | 61.1572 | -0.041199 | 122.3694 | 122.5571 | 122.406 | -0.21973 | -0.20599 | 122.3694 | 122.5571 | -0.21973 | -0.041199 | 122.406 | -122.4609 | -122.644
56.6719 | 122.6624 | -61.2259 | 61.2442 | -0.010758 | 0.041612 | 0.038016 | -0.0006281 | -0.0055179 | 0.063912 | 0.063166 | 61.3541 | 61.1481 | -61.2213 | 61.1206 | -61.2579 | -61.4227 | -0.013733 | -0.050354 | 61.2122 | -61.4273 | 0.004578 | -0.096131 | 122.58 | 122.3465 | -122.5021 | -0.20142 | -0.032044 | 122.5754 | 61.2122 | 61.1755 | -0.032044 | 122.374 | 122.58 | 122.438 | -0.19684 | -0.20142 | 122.374 | 122.58 | -0.19684 | -0.032044 | 122.438 | -122.4655 | -122.6715
57.6719 | 122.6578 | -61.2213 | 61.2534 | -0.018387 | 0.045457 | 0.038016 | -0.0016961 | -0.0053043 | 0.065407 | 0.062098 | 61.3632 | 61.1755 | -61.2213 | 61.1343 | -61.2488 | -61.441 | -0.009155 | -0.050354 | 61.2442 | -61.4182 | 0 | -0.07782 | 122.5845 | 122.3557 | -122.5021 | -0.19684 | -0.009155 | 122.5845 | 61.2122 | 61.171 | -0.027466 | 122.3969 | 122.5845 | 122.4655 | -0.21973 | -0.19684 | 122.3969 | 122.5845 | -0.21973 | -0.027466 | 122.4655 | -122.4747 | -122.6715
58.6719 | 122.6349 | -61.235 | 61.2305 | -0.003128 | 0.043107 | 0.037589 | -0.0025507 | -0.0061587 | 0.066903 | 0.064448 | 61.3495 | 61.1801 | -61.2396 | 61.1252 | -61.2625 | -61.4548 | -0.004578 | -0.050354 | 61.2167 | -61.4227 | -0.004578 | -0.050354 | 122.5845 | 122.3602 | -122.493 | -0.18768 | -0.013733 | 122.5891 | 61.2305 | 61.1847 | -0.027466 | 122.4152 | 122.5845 | 122.4518 | -0.21973 | -0.18768 | 122.4152 | 122.5845 | -0.21973 | -0.027466 | 122.4518 | -122.4701 | -122.6532
59.6719 | 122.6257 | -61.2076 | 61.2396 | -0.010758 | 0.046311 | 0.036948 | -0.0004145 | -0.0035953 | 0.065407 | 0.065302 | 61.3586 | 61.171 | -61.2305 | 61.1572 | -61.2396 | -61.441 | 0.013733 | -0.027466 | 61.2534 | -61.3998 | -0.022888 | -0.068665 | 122.5662 | 122.3648 | -122.4792 | -0.19226 | 0.013733 | 122.5891 | 61.2213 | 61.1801 | -0.032043 | 122.3785 | 122.5662 | 122.4609 | -0.23346 | -0.19226 | 122.3785 | 122.5662 | -0.23346 | -0.032043 | 122.4609 | -122.4701 | -122.6395
60.6719 | 122.699 | -61.1893 | 61.2442 | 0.0045015 | 0.045884 | 0.035666 | -0.0034051 | -0.0050907 | 0.064766 | 0.065302 | 61.4319 | 61.1664 | -61.1938 | 61.235 | -61.1755 | -61.3815 | -0.013733 | 0.068665 | 61.2534 | -61.4044 | -0.004578 | -0.07782 | 122.6212 | 122.4243 | -122.4197 | -0.21515 | 0.009155 | 122.6257 | 61.1755 | 61.2579 | 0.013733 | 122.3557 | 122.6212 | 122.4426 | -0.19226 | -0.21515 | 122.3557 | 122.6212 | -0.19226 | 0.013733 | 122.4426 | -122.4381 | -122.6486
61.6719 | 122.644 | -61.2122 | 61.2442 | -0.003128 | 0.043321 | 0.036735 | -0.0019099 | -0.0038089 | 0.064766 | 0.064021 | 61.3724 | 61.1618 | -61.2259 | 61.1343 | -61.2396 | -61.4365 | 0.022888 | -0.045776 | 61.2671 | -61.4136 | -0.013733 | -0.082398 | 122.5845 | 122.3465 | -122.4838 | -0.20142 | 0.022888 | 122.5983 | 61.235 | 61.1664 | -0.027466 | 122.374 | 122.5845 | 122.4792 | -0.2243 | -0.20142 | 122.374 | 122.5845 | -0.2243 | -0.027466 | 122.4792 | -122.4701 | -122.6578
62.6719 | 122.6395 | -61.2213 | 61.2579 | -0.018387 | 0.041825 | 0.037589 | -0.0025507 | -0.0053043 | 0.065621 | 0.064021 | 61.3861 | 61.1618 | -61.2213 | 61.1481 | -61.2305 | -61.4227 | 0.009155 | -0.013733 | 61.2259 | -61.4227 | 0 | -0.096131 | 122.6074 | 122.3694 | -122.4884 | -0.20142 | -0.032044 | 122.6074 | 61.2305 | 61.2076 | -0.009156 | 122.3831 | 122.6074 | 122.4472 | -0.20142 | -0.20142 | 122.3831 | 122.6074 | -0.20142 | -0.009156 | 122.4472 | -122.4792 | -122.6807
63.6719 | 122.6715 | -61.2305 | 61.2625 | -0.003128 | 0.045457 | 0.037162 | -0.0023371 | -0.0061587 | 0.064125 | 0.064661 | 61.409 | 61.1664 | -61.2167 | 61.171 | -61.2167 | -61.3998 | 0.004578 | -0.004578 | 61.2396 | -61.4136 | 0.013733 | -0.09613 | 122.6395 | 122.4014 | -122.4792 | -0.1831 | -0.022888 | 122.6257 | 61.235 | 61.2259 | 0.013733 | 122.3969 | 122.6395 | 122.4701 | -0.16937 | -0.1831 | 122.3969 | 122.6395 | -0.16937 | 0.013733 | 122.4701 | -122.4792 | -122.6761
64.6719 | 122.6852 | -61.2076 | 61.2534 | -0.003128 | 0.045243 | 0.041434 | -0.0025507 | -0.0065859 | 0.067116 | 0.064021 | 61.4365 | 61.1801 | -61.1847 | 61.2076 | -61.1938 | -61.3861 | -0.022888 | 0.054932 | 61.2396 | -61.3953 | 0.022889 | -0.073242 | 122.644 | 122.4152 | -122.4472 | -0.18768 | -0.013733 | 122.6212 | 61.1847 | 61.2625 | 0.013733 | 122.3877 | 122.644 | 122.4472 | -0.17853 | -0.18768 | 122.3877 | 122.644 | -0.17853 | 0.013733 | 122.4472 | -122.438 | -122.6486
65.6719 | 122.7036 | -61.2076 | 61.2488 | -0.010758 | 0.045671 | 0.039939 | -0.0027643 | -0.0012453 | 0.065194 | 0.063593 | 61.441 | 61.1755 | -61.2076 | 61.2259 | -61.1755 | -61.3495 | -0.018311 | 0.07782 | 61.2946 | -61.377 | 0 | -0.073242 | 122.6486 | 122.4335 | -122.4243 | -0.16937 | 0.045777 | 122.6486 | 61.1893 | 61.2854 | 0.032044 | 122.3831 | 122.6486 | 122.5021 | -0.14191 | -0.16937 | 122.3831 | 122.6486 | -0.14191 | 0.032044 | 122.5021 | -122.4564 | -122.6257
66.6719 | 122.6944 | -61.1938 | 61.29 | -0.010758 | 0.045243 | 0.037803 | -0.0019099 | -0.0053043 | 0.064766 | 0.064021 | 61.4319 | 61.1755 | -61.1984 | 61.2213 | -61.1526 | -61.3541 | 0.032043 | 0.091553 | 61.2808 | -61.3678 | -0.004577 | -0.11444 | 122.6257 | 122.4152 | -122.4426 | -0.17395 | -0.009155 | 122.6303 | 61.2259 | 61.2854 | 0.041199 | 122.3694 | 122.6257 | 122.4747 | -0.16022 | -0.17395 | 122.3694 | 122.6257 | -0.16022 | 0.041199 | 122.4747 | -122.4884 | -122.6578
67.6719 | 122.6944 | -61.1984 | 61.2854 | -0.003128 | 0.043534 | 0.037589 | -0.0027643 | -0.0055179 | 0.065834 | 0.063807 | 61.4182 | 61.1847 | -61.1801 | 61.2167 | -61.1755 | -61.3586 | 0.054932 | 0.073242 | 61.2808 | -61.3907 | 0.01831 | -0.10071 | 122.6166 | 122.4152 | -122.4609 | -0.19226 | -0.004577 | 122.5983 | 61.2534 | 61.2717 | 0.022888 | 122.3831 | 122.6166 | 122.4792 | -0.16022 | -0.19226 | 122.3831 | 122.6166 | -0.16022 | 0.022888 | 122.4792 | -122.4655 | -122.6761
68.6719 | 122.7036 | -61.1938 | 61.2579 | -0.010758 | 0.043534 | 0.040366 | -0.0019099 | -0.0050907 | 0.065834 | 0.064234 | 61.4502 | 61.1755 | -61.2076 | 61.2213 | -61.1572 | -61.3449 | -0.018311 | 0.082397 | 61.2488 | -61.3724 | -0.013733 | -0.082398 | 122.644 | 122.4152 | -122.4152 | -0.17853 | -0.009156 | 122.6578 | 61.1755 | 61.2762 | 0.036621 | 122.3694 | 122.644 | 122.4426 | -0.15106 | -0.17853 | 122.3694 | 122.644 | -0.15106 | 0.036621 | 122.4426 | -122.4655 | -122.6303
69.6719 | 122.7036 | -61.203 | 61.2717 | -0.003128 | 0.044389 | 0.038657 | -0.0029779 | -0.0040225 | 0.063057 | 0.064661 | 61.4365 | 61.1755 | -61.1664 | 61.2305 | -61.1755 | -61.3449 | -0.004578 | 0.086975 | 61.2579 | -61.3953 | 0.036621 | -0.09613 | 122.6395 | 122.4335 | -122.4472 | -0.19226 | -0.013732 | 122.6028 | 61.1984 | 61.29 | 0.027466 | 122.3785 | 122.6395 | 122.4609 | -0.14191 | -0.19226 | 122.3785 | 122.6395 | -0.14191 | 0.027466 | 122.4609 | -122.438 | -122.6669
70.6719 | 122.7081 | -61.1938 | 61.2488 | 0.0045015 | 0.043748 | 0.039084 | -0.0023371 | -0.0033817 | 0.066262 | 0.061884 | 61.441 | 61.1572 | -61.1984 | 61.235 | -61.1618 | -61.3541 | 0.004578 | 0.091553 | 61.2534 | -61.377 | -0.004577 | -0.091552 | 122.6349 | 122.4289 | -122.4106 | -0.1831 | 0.004578 | 122.6395 | 61.1984 | 61.2854 | 0.032044 | 122.3511 | 122.6349 | 122.4472 | -0.16022 | -0.1831 | 122.3511 | 122.6349 | -0.16022 | 0.032044 | 122.4472 | -122.4472 | -122.6257
71.6719 | 122.7036 | -61.1893 | 61.2625 | -0.010758 | 0.045884 | 0.035666 | -0.0044733 | -0.0061587 | 0.063912 | 0.062312 | 61.441 | 61.1618 | -61.1938 | 61.2259 | -61.1618 | -61.3586 | 0.022888 | 0.10071 | 61.2808 | -61.3586 | -0.004578 | -0.10071 | 122.6303 | 122.4152 | -122.4243 | -0.16937 | 0.018311 | 122.6349 | 61.2122 | 61.29 | 0.027466 | 122.3511 | 122.6303 | 122.4701 | -0.16937 | -0.16937 | 122.3511 | 122.6303 | -0.16937 | 0.027466 | 122.4701 | -122.4564 | -122.6212
72.6719 | 122.6898 | -61.2076 | 61.2625 | -0.010758 | 0.044175 | 0.038657 | -0.0025507 | -0.0025271 | 0.066048 | 0.064875 | 61.4227 | 61.1664 | -61.171 | 61.2259 | -61.1572 | -61.3586 | 0.045776 | 0.09613 | 61.3174 | -61.3953 | 0.036622 | -0.09613 | 122.6303 | 122.4335 | -122.4197 | -0.18768 | 0.054932 | 122.5937 | 61.2534 | 61.3037 | 0.050354 | 122.374 | 122.6303 | 122.525 | -0.15106 | -0.18768 | 122.374 | 122.6303 | -0.15106 | 0.050354 | 122.525 | -122.4335 | -122.6578
73.6719 | 122.6532 | -61.2213 | 61.3037 | -0.003128 | 0.043748 | 0.035453 | -0.0057551 | -0.0050907 | 0.066262 | 0.064021 | 61.3953 | 61.1984 | -61.1847 | 61.1755 | -61.1984 | -61.3998 | 0.11902 | 0.068665 | 61.3129 | -61.3586 | 0.036621 | -0.10529 | 122.6166 | 122.3969 | -122.5021 | -0.13733 | 0.009155 | 122.58 | 61.3403 | 61.29 | 0.022888 | 122.4197 | 122.6166 | 122.5342 | -0.17853 | -0.13733 | 122.4197 | 122.6166 | -0.17853 | 0.022888 | 122.5342 | -122.4884 | -122.6624
74.6719 | 122.6486 | -61.2076 | 61.29 | -0.003128 | 0.043534 | 0.036307 | -0.0046869 | -0.0046633 | 0.066048 | 0.065089 | 61.3998 | 61.203 | -61.1801 | 61.1847 | -61.1893 | -61.3953 | 0.13733 | 0.073242 | 61.3312 | -61.3495 | 0.027466 | -0.086975 | 122.6074 | 122.3923 | -122.4792 | -0.14191 | 0.041199 | 122.58 | 61.3449 | 61.2808 | 0.018311 | 122.4106 | 122.6074 | 122.5388 | -0.18768 | -0.14191 | 122.4106 | 122.6074 | -0.18768 | 0.018311 | 122.5388 | -122.4701 | -122.6395
75.6719 | 122.7036 | -61.2122 | 61.2854 | 0.0045015 | 0.043962 | 0.04058 | -0.0008417 | -0.0044497 | 0.066048 | 0.060816 | 61.4365 | 61.1801 | -61.1984 | 61.2396 | -61.1572 | -61.3632 | 0.027466 | 0.091553 | 61.2717 | -61.3815 | 0.013733 | -0.10529 | 122.6486 | 122.4518 | -122.4426 | -0.16937 | -0.013733 | 122.6349 | 61.2396 | 61.3037 | 0.054931 | 122.3923 | 122.6486 | 122.4838 | -0.15106 | -0.16937 | 122.3923 | 122.6486 | -0.15106 | 0.054931 | 122.4838 | -122.4838 | -122.6669
76.6719 | 122.6944 | -61.2213 | 61.2625 | -0.003128 | 0.043107 | 0.036735 | -0.0019099 | -0.0029543 | 0.066048 | 0.062952 | 61.4273 | 61.1847 | -61.1847 | 61.2167 | -61.1664 | -61.3449 | 0.032043 | 0.07782 | 61.2808 | -61.377 | 0.036621 | -0.07782 | 122.6486 | 122.438 | -122.4289 | -0.15564 | 0.018311 | 122.612 | 61.2534 | 61.2991 | 0.054931 | 122.406 | 122.6486 | 122.5021 | -0.1236 | -0.15564 | 122.406 | 122.6486 | -0.1236 | 0.054931 | 122.5021 | -122.4472 | -122.6395
77.6719 | 122.7036 | -61.2213 | 61.2854 | -0.018387 | 0.043534 | 0.038016 | -0.0019099 | -0.0050907 | 0.064553 | 0.062952 | 61.4044 | 61.1938 | -61.2076 | 61.1938 | -61.1801 | -61.377 | 0.054932 | 0.082397 | 61.2808 | -61.3632 | 0.013732 | -0.091552 | 122.6257 | 122.4152 | -122.4655 | -0.14191 | -0.004577 | 122.612 | 61.2762 | 61.3037 | 0.041198 | 122.4152 | 122.6257 | 122.5021 | -0.15564 | -0.14191 | 122.4152 | 122.6257 | -0.15564 | 0.041198 | 122.5021 | -122.493 | -122.6486
78.6719 | 122.6898 | -61.2534 | 61.2808 | -0.010758 | 0.043534 | 0.036948 | -0.0029779 | -0.0046633 | 0.064125 | 0.063807 | 61.4136 | 61.1618 | -61.1984 | 61.203 | -61.1801 | -61.3586 | 0.091553 | 0.086975 | 61.3129 | -61.3541 | 0.054932 | -0.11902 | 122.6669 | 122.4564 | -122.4609 | -0.10071 | 0.032043 | 122.612 | 61.3449 | 61.3403 | 0.073242 | 122.4152 | 122.6669 | 122.5662 | -0.10529 | -0.10071 | 122.4152 | 122.6669 | -0.10529 | 0.073242 | 122.5662 | -122.4792 | -122.6349
79.6719 | 122.6807 | -61.2122 | 61.2854 | -0.003128 | 0.043534 | 0.035453 | -0.0036187 | -0.0035953 | 0.065834 | 0.064021 | 61.4136 | 61.1801 | -61.1938 | 61.1893 | -61.1847 | -61.3861 | 0.09613 | 0.073242 | 61.2808 | -61.3541 | 0.01831 | -0.10529 | 122.6257 | 122.4014 | -122.4701 | -0.14191 | -0.004577 | 122.6074 | 61.3083 | 61.2854 | 0.027466 | 122.3923 | 122.6257 | 122.493 | -0.17395 | -0.14191 | 122.3923 | 122.6257 | -0.17395 | 0.027466 | 122.493 | -122.4792 | -122.6395
80.6719 | 122.6532 | -61.203 | 61.2808 | 0.0045015 | 0.044175 | 0.036307 | -0.0057551 | -0.0042361 | 0.067971 | 0.065089 | 61.3998 | 61.2076 | -61.1893 | 61.1801 | -61.1618 | -61.3815 | 0.13275 | 0.091553 | 61.3266 | -61.3632 | 0.013733 | -0.073242 | 122.6028 | 122.3831 | -122.4426 | -0.16022 | 0.045776 | 122.5891 | 61.3358 | 61.2946 | 0.041199 | 122.4106 | 122.6028 | 122.5296 | -0.17853 | -0.16022 | 122.4106 | 122.6028 | -0.17853 | 0.041199 | 122.5296 | -122.4701 | -122.644
81.6719 | 122.6624 | -61.2122 | 61.3312 | -0.010758 | 0.04268 | 0.033957 | -0.0061823 | -0.0061587 | 0.065407 | 0.06338 | 61.3998 | 61.1618 | -61.1984 | 61.1938 | -61.1801 | -61.3815 | 0.12817 | 0.091553 | 61.3174 | -61.3449 | 0.013733 | -0.16937 | 122.612 | 122.406 | -122.5113 | -0.13275 | -0.013733 | 122.5983 | 61.3403 | 61.3037 | 0.032043 | 122.374 | 122.612 | 122.5296 | -0.16937 | -0.13275 | 122.374 | 122.612 | -0.16937 | 0.032043 | 122.5296 | -122.5296 | -122.6761
82.6719 | 122.6944 | -61.2396 | 61.3083 | -0.010758 | 0.043534 | 0.034812 | -0.0021235 | -0.0044497 | 0.064766 | 0.064661 | 61.4273 | 61.1755 | -61.1938 | 61.1984 | -61.171 | -61.3632 | 0.068665 | 0.082397 | 61.2808 | -61.377 | 0.045776 | -0.13275 | 122.6669 | 122.438 | -122.4792 | -0.13733 | -0.027466 | 122.6212 | 61.3083 | 61.322 | 0.068665 | 122.4152 | 122.6669 | 122.5204 | -0.1236 | -0.13733 | 122.4152 | 122.6669 | -0.1236 | 0.068665 | 122.5204 | -122.5021 | -122.6852
83.6719 | 122.6852 | -61.2305 | 61.2946 | -0.003128 | 0.04503 | 0.035239 | -0.0016961 | -0.0031681 | 0.063912 | 0.063166 | 61.3953 | 61.1755 | -61.1847 | 61.2076 | -61.1984 | -61.3815 | 0.091553 | 0.064087 | 61.2762 | -61.3632 | 0.045777 | -0.11902 | 122.6257 | 122.4381 | -122.493 | -0.13275 | -0.018311 | 122.58 | 61.322 | 61.2946 | 0.032044 | 122.406 | 122.6257 | 122.5067 | -0.15106 | -0.13275 | 122.406 | 122.6257 | -0.15106 | 0.032044 | 122.5067 | -122.4792 | -122.6578
84.6719 | 122.6761 | -61.2259 | 61.2854 | -0.010758 | 0.043962 | 0.036307 | -0.0042597 | -0.0059451 | 0.065194 | 0.061884 | 61.4044 | 61.1938 | -61.203 | 61.1893 | -61.1938 | -61.4044 | 0.091553 | 0.064087 | 61.3358 | -61.3586 | 0.022888 | -0.091552 | 122.6303 | 122.4152 | -122.4792 | -0.13275 | 0.050354 | 122.6074 | 61.3174 | 61.29 | 0.032043 | 122.4197 | 122.6303 | 122.5616 | -0.17853 | -0.13275 | 122.4197 | 122.6303 | -0.17853 | 0.032043 | 122.5616 | -122.4884 | -122.644
85.6719 | 122.6578 | -61.2442 | 61.2808 | -0.010758 | 0.042253 | 0.032462 | -0.0038325 | -0.0042361 | 0.065194 | 0.064875 | 61.3815 | 61.1938 | -61.1801 | 61.1755 | -61.203 | -61.3953 | 0.10986 | 0.07782 | 61.322 | -61.3678 | 0.064087 | -0.086975 | 122.6257 | 122.4197 | -122.4838 | -0.1236 | 0.041198 | 122.5616 | 61.3541 | 61.322 | 0.041199 | 122.4381 | 122.6257 | 122.5662 | -0.15106 | -0.1236 | 122.4381 | 122.6257 | -0.15106 | 0.041199 | 122.5662 | -122.4609 | -122.6486
86.6719 | 122.6624 | -61.2259 | 61.3037 | -0.003128 | 0.041398 | 0.035666 | -0.0057551 | -0.0061587 | 0.06263 | 0.064234 | 61.3998 | 61.1893 | -61.1938 | 61.1755 | -61.1938 | -61.3907 | 0.12817 | 0.07782 | 61.3083 | -61.3449 | 0.032043 | -0.11444 | 122.6257 | 122.4014 | -122.4976 | -0.11902 | 0.004578 | 122.5937 | 61.3541 | 61.3037 | 0.032043 | 122.4152 | 122.6257 | 122.5342 | -0.1648 | -0.11902 | 122.4152 | 122.6257 | -0.1648 | 0.032043 | 122.5342 | -122.4976 | -122.6486
87.6719 | 122.6761 | -61.2076 | 61.2946 | -0.003128 | 0.040757 | 0.032462 | -0.0059687 | -0.0053043 | 0.066689 | 0.063166 | 61.4685 | 61.1206 | -61.1481 | 61.2396 | -61.1343 | -61.3449 | 0.073242 | 0.12817 | 61.322 | -61.3174 | 0.05951 | -0.17395 | 122.6761 | 122.4472 | -122.4289 | -0.10986 | 0.027465 | 122.6166 | 61.2808 | 61.3358 | 0.073243 | 122.3282 | 122.6761 | 122.5296 | -0.13733 | -0.10986 | 122.3282 | 122.6761 | -0.13733 | 0.073243 | 122.5296 | -122.4426 | -122.612
88.6719 | 122.7264 | -61.1984 | 61.29 | -0.003128 | 0.039475 | 0.034385 | -0.0049005 | -0.0065859 | 0.063912 | 0.064661 | 61.4822 | 61.1206 | -61.1389 | 61.2854 | -61.1023 | -61.29 | 0.018311 | 0.17853 | 61.3037 | -61.3174 | 0.059509 | -0.16937 | 122.6807 | 122.4838 | -122.3923 | -0.11902 | 0.013733 | 122.6212 | 61.2167 | 61.377 | 0.09613 | 122.319 | 122.6807 | 122.5021 | -0.091553 | -0.11902 | 122.319 | 122.6807 | -0.091553 | 0.09613 | 122.5021 | -122.4289 | -122.6074
89.6719 | 122.6486 | -61.2488 | 61.3083 | -0.018387 | 0.042039 | 0.037589 | -0.0040461 | -0.0087223 | 0.066689 | 0.062312 | 61.3953 | 61.1618 | -61.1847 | 61.1801 | -61.1984 | -61.3998 | 0.13733 | 0.068665 | 61.2991 | -61.3678 | 0.064087 | -0.14649 | 122.644 | 122.4289 | -122.5067 | -0.11902 | -0.009156 | 122.58 | 61.3861 | 61.3174 | 0.050354 | 122.4106 | 122.644 | 122.5479 | -0.15106 | -0.11902 | 122.4106 | 122.644 | -0.15106 | 0.050354 | 122.5479 | -122.493 | -122.6761
90.6719 | 122.6578 | -61.2305 | 61.29 | -0.003128 | 0.041184 | 0.032676 | -0.0036187 | -0.0070133 | 0.064339 | 0.064021 | 61.3907 | 61.1526 | -61.1938 | 61.1938 | -61.1893 | -61.3953 | 0.11902 | 0.082397 | 61.3358 | -61.3403 | 0.036621 | -0.13733 | 122.6212 | 122.4243 | -122.4792 | -0.10986 | 0.045776 | 122.5845 | 61.3495 | 61.3129 | 0.041199 | 122.3831 | 122.6212 | 122.5662 | -0.16479 | -0.10986 | 122.3831 | 122.6212 | -0.16479 | 0.041199 | 122.5662 | -122.4838 | -122.6303
91.6719 | 122.6761 | -61.235 | 61.3037 | -0.003128 | 0.039903 | 0.035026 | -0.0044733 | -0.0061587 | 0.066475 | 0.063593 | 61.4136 | 61.1481 | -61.1984 | 61.2167 | -61.1664 | -61.3953 | 0.10071 | 0.09613 | 61.3129 | -61.3449 | 0.036621 | -0.15564 | 122.6486 | 122.4518 | -122.4701 | -0.10986 | 0.009155 | 122.612 | 61.3358 | 61.3312 | 0.068664 | 122.3831 | 122.6486 | 122.5479 | -0.16022 | -0.10986 | 122.3831 | 122.6486 | -0.16022 | 0.068664 | 122.5479 | -122.5021 | -122.6486
92.6719 | 122.6715 | -61.2213 | 61.2991 | -0.018387 | 0.04033 | 0.035666 | -0.0034051 | -0.0063723 | 0.064766 | 0.063593 | 61.4456 | 61.1298 | -61.1618 | 61.2305 | -61.1481 | -61.3449 | 0.064087 | 0.11902 | 61.2991 | -61.3632 | 0.059509 | -0.16937 | 122.6669 | 122.4518 | -122.4472 | -0.14191 | 0 | 122.6074 | 61.2854 | 61.3403 | 0.073242 | 122.3511 | 122.6669 | 122.5204 | -0.1236 | -0.14191 | 122.3511 | 122.6669 | -0.1236 | 0.073242 | 122.5204 | -122.4609 | -122.6624
93.6719 | 122.7219 | -61.235 | 61.3037 | -0.003128 | 0.041184 | 0.032462 | -0.0042597 | -0.0072269 | 0.063698 | 0.064448 | 61.4868 | 61.116 | -61.1526 | 61.29 | -61.1206 | -61.3083 | 0.027466 | 0.16937 | 61.2671 | -61.3266 | 0.082397 | -0.18768 | 122.7219 | 122.525 | -122.4243 | -0.091553 | -0.036621 | 122.6395 | 61.2625 | 61.4044 | 0.11444 | 122.3511 | 122.7219 | 122.5021 | -0.073243 | -0.091553 | 122.3511 | 122.7219 | -0.073243 | 0.11444 | 122.5021 | -122.4564 | -122.6303
94.6719 | 122.7722 | -61.1984 | 61.2396 | -0.010758 | 0.040757 | 0.034385 | -0.0055413 | -0.0082949 | 0.063485 | 0.064234 | 61.5051 | 61.0886 | -61.1343 | 61.3403 | -61.0382 | -61.2305 | -0.082397 | 0.21973 | 61.2625 | -61.29 | 0.064087 | -0.15106 | 122.7036 | 122.5388 | -122.2778 | -0.091553 | 0.022888 | 122.6395 | 61.116 | 61.4182 | 0.16022 | 122.287 | 122.7036 | 122.4609 | -0.032044 | -0.091553 | 122.287 | 122.7036 | -0.032044 | 0.16022 | 122.4609 | -122.374 | -122.5296
95.6719 | 122.7951 | -61.1847 | 61.2717 | -0.003128 | 0.037553 | 0.033103 | -0.0063959 | -0.0095767 | 0.065834 | 0.062312 | 61.5143 | 61.0794 | -61.1343 | 61.3449 | -61.0382 | -61.2396 | -0.082397 | 0.20142 | 61.235 | -61.29 | 0.050354 | -0.19226 | 122.699 | 122.5296 | -122.3099 | -0.10529 | -0.036621 | 122.6486 | 61.1023 | 61.3861 | 0.14648 | 122.2641 | 122.699 | 122.4197 | -0.054932 | -0.10529 | 122.2641 | 122.699 | -0.054932 | 0.14648 | 122.4197 | -122.406 | -122.5616
96.6719 | 122.7219 | -61.2213 | 61.2762 | -0.003128 | 0.04033 | 0.038871 | -0.0034051 | -0.0097903 | 0.063485 | 0.061457 | 61.496 | 61.1069 | -61.1389 | 61.2946 | -61.0977 | -61.29 | 0.022888 | 0.16479 | 61.2762 | -61.3037 | 0.082397 | -0.16937 | 122.7173 | 122.5159 | -122.374 | -0.082398 | 0 | 122.6349 | 61.2442 | 61.3861 | 0.1236 | 122.3282 | 122.7173 | 122.4976 | -0.068665 | -0.082398 | 122.3282 | 122.7173 | -0.068665 | 0.1236 | 122.4976 | -122.4152 | -122.58
97.6719 | 122.7585 | -61.2213 | 61.29 | -0.003128 | 0.037126 | 0.036094 | -0.0025507 | -0.0082949 | 0.062416 | 0.066157 | 61.5051 | 61.084 | -61.1389 | 61.3083 | -61.0748 | -61.2671 | -0.018311 | 0.20599 | 61.2579 | -61.3083 | 0.082397 | -0.20599 | 122.7264 | 122.5296 | -122.3648 | -0.086976 | -0.032043 | 122.644 | 61.203 | 61.4273 | 0.14648 | 122.3053 | 122.7264 | 122.4792 | -0.045777 | -0.086976 | 122.3053 | 122.7264 | -0.045777 | 0.14648 | 122.4792 | -122.4289 | -122.5983
98.6719 | 122.7722 | -61.2305 | 61.2579 | 0.0045015 | 0.039689 | 0.038016 | -0.0044733 | -0.0078677 | 0.066262 | 0.06103 | 61.5005 | 61.0794 | -61.1526 | 61.3174 | -61.084 | -61.2671 | -0.068665 | 0.19684 | 61.2579 | -61.2854 | 0.07782 | -0.17853 | 122.731 | 122.5479 | -122.3419 | -0.054931 | 0 | 122.6532 | 61.1618 | 61.4273 | 0.14648 | 122.3099 | 122.731 | 122.4884 | -0.036621 | -0.054931 | 122.3099 | 122.731 | -0.036621 | 0.14648 | 122.4884 | -122.4106 | -122.5433
99.6719 | 122.7859 | -61.1847 | 61.2442 | -0.010758 | 0.036485 | 0.033957 | -0.0034051 | -0.0089359 | 0.064553 | 0.060816 | 61.5143 | 61.0565 | -61.1298 | 61.3312 | -61.0382 | -61.2488 | -0.064087 | 0.21515 | 61.2534 | -61.3129 | 0.054931 | -0.18768 | 122.699 | 122.5159 | -122.2824 | -0.12817 | 0.009155 | 122.644 | 61.1206 | 61.3998 | 0.14648 | 122.2412 | 122.699 | 122.438 | -0.064087 | -0.12817 | 122.2412 | 122.699 | -0.064087 | 0.14648 | 122.438 | -122.374 | -122.5571
100.6719 | 122.7951 | -61.1847 | 61.2579 | -0.018387 | 0.036485 | 0.030539 | -0.0019099 | -0.0091495 | 0.063912 | 0.060603 | 61.5234 | 61.0931 | -61.1526 | 61.3495 | -61.0519 | -61.2625 | -0.082397 | 0.21973 | 61.2671 | -61.2946 | 0.032043 | -0.1648 | 122.7081 | 122.5342 | -122.3099 | -0.10986 | 0.009155 | 122.6761 | 61.1023 | 61.4044 | 0.13275 | 122.2778 | 122.7081 | 122.4518 | -0.07782 | -0.10986 | 122.2778 | 122.7081 | -0.07782 | 0.13275 | 122.4518 | -122.4106 | -122.5525
101.6719 | 122.8043 | -61.2396 | 61.2488 | 0.0045015 | 0.036698 | 0.038871 | -0.0038325 | -0.011072 | 0.064553 | 0.063593 | 61.496 | 61.0931 | -61.1664 | 61.3174 | -61.0748 | -61.2534 | -0.10529 | 0.19684 | 61.2076 | -61.2946 | 0.073242 | -0.15564 | 122.7356 | 122.5571 | -122.3236 | -0.054932 | -0.041198 | 122.6624 | 61.1343 | 61.4365 | 0.16479 | 122.3328 | 122.7356 | 122.4472 | -0.013733 | -0.054932 | 122.3328 | 122.7356 | -0.013733 | 0.16479 | 122.4472 | -122.4152 | -122.5433
102.6719 | 122.7905 | -61.1893 | 61.2671 | -0.003128 | 0.037126 | 0.032676 | -0.0012689 | -0.0089359 | 0.062844 | 0.062525 | 61.5234 | 61.0565 | -61.1389 | 61.3449 | -61.0703 | -61.2534 | -0.091553 | 0.21515 | 61.2488 | -61.2808 | 0.050354 | -0.21057 | 122.7127 | 122.5342 | -122.3373 | -0.091553 | -0.018311 | 122.6624 | 61.0977 | 61.4044 | 0.11902 | 122.2458 | 122.7127 | 122.438 | -0.064087 | -0.091553 | 122.2458 | 122.7127 | -0.064087 | 0.11902 | 122.438 | -122.406 | -122.5479
103.6719 | 122.7722 | -61.2213 | 61.2625 | -0.003128 | 0.040757 | 0.033103 | -0.0019099 | -0.0074405 | 0.06498 | 0.063166 | 61.5143 | 61.084 | -61.1435 | 61.3312 | -61.0703 | -61.2579 | -0.064087 | 0.20142 | 61.2396 | -61.3083 | 0.077819 | -0.17853 | 122.7356 | 122.5525 | -122.3328 | -0.086976 | -0.022888 | 122.6578 | 61.1572 | 61.4227 | 0.15106 | 122.3053 | 122.7356 | 122.4609 | -0.036622 | -0.086976 | 122.3053 | 122.7356 | -0.036622 | 0.15106 | 122.4609 | -122.406 | -122.5708
104.6719 | 122.7768 | -61.2076 | 61.2534 | -0.010758 | 0.039048 | 0.035239 | -0.0021235 | -0.0074405 | 0.06263 | 0.062098 | 61.5051 | 61.084 | -61.1206 | 61.3358 | -61.0657 | -61.2442 | -0.07782 | 0.20142 | 61.2488 | -61.2717 | 0.086976 | -0.16937 | 122.7127 | 122.5433 | -122.319 | -0.064086 | -0.004578 | 122.6257 | 61.1298 | 61.409 | 0.14191 | 122.2916 | 122.7127 | 122.4564 | -0.036621 | -0.064086 | 122.2916 | 122.7127 | -0.036621 | 0.14191 | 122.4564 | -122.374 | -122.525
105.6719 | 122.7859 | -61.2122 | 61.2625 | 0.0045015 | 0.038407 | 0.031394 | -0.0038325 | -0.0074405 | 0.066262 | 0.061457 | 61.5189 | 61.0886 | -61.1389 | 61.3495 | -61.0565 | -61.2442 | -0.091553 | 0.20142 | 61.2579 | -61.2625 | 0.073242 | -0.17395 | 122.731 | 122.5616 | -122.319 | -0.050354 | -0.004577 | 122.6578 | 61.1206 | 61.4136 | 0.15564 | 122.3007 | 122.731 | 122.4701 | -0.032044 | -0.050354 | 122.3007 | 122.731 | -0.032044 | 0.15564 | 122.4701 | -122.4014 | -122.525
106.6719 | 122.7951 | -61.203 | 61.2854 | -0.010758 | 0.038194 | 0.032676 | -0.0040461 | -0.0089359 | 0.06498 | 0.062952 | 61.5234 | 61.1069 | -61.1343 | 61.3495 | -61.0519 | -61.2579 | -0.10071 | 0.21973 | 61.2396 | -61.2717 | 0.068665 | -0.17853 | 122.7264 | 122.5525 | -122.3373 | -0.068664 | -0.045776 | 122.6578 | 61.1023 | 61.4227 | 0.15106 | 122.3099 | 122.7264 | 122.4426 | -0.054932 | -0.068664 | 122.3099 | 122.7264 | -0.054932 | 0.15106 | 122.4426 | -122.4197 | -122.5571
107.6719 | 122.8043 | -61.1893 | 61.2808 | -0.003128 | 0.039262 | 0.033317 | -0.0044733 | -0.0091495 | 0.063057 | 0.06338 | 61.5189 | 61.0931 | -61.1526 | 61.3495 | -61.0565 | -61.2305 | -0.091553 | 0.21973 | 61.2213 | -61.3129 | 0.036621 | -0.18768 | 122.7081 | 122.5388 | -122.3373 | -0.1236 | -0.05951 | 122.6715 | 61.0977 | 61.409 | 0.13275 | 122.2824 | 122.7081 | 122.4106 | -0.041199 | -0.1236 | 122.2824 | 122.7081 | -0.041199 | 0.13275 | 122.4106 | -122.4335 | -122.5937
108.6719 | 122.6303 | -61.2488 | 61.2946 | 0.0045015 | 0.042039 | 0.034385 | -0.0004145 | -0.0089359 | 0.06498 | 0.06338 | 61.4044 | 61.1664 | -61.171 | 61.2213 | -61.1893 | -61.3907 | 0.11902 | 0.086975 | 61.2762 | -61.3541 | 0.07782 | -0.12817 | 122.6532 | 122.4701 | -122.4838 | -0.10529 | -0.018311 | 122.5754 | 61.3678 | 61.3358 | 0.059509 | 122.4152 | 122.6532 | 122.525 | -0.14191 | -0.10529 | 122.4152 | 122.6532 | -0.14191 | 0.059509 | 122.525 | -122.4655 | -122.6486
109.6719 | 122.7722 | -61.203 | 61.2671 | -0.003128 | 0.038835 | 0.033957 | -0.0057551 | -0.010004 | 0.064339 | 0.063166 | 61.5097 | 61.0794 | -61.1481 | 61.3449 | -61.0474 | -61.2579 | -0.073242 | 0.20142 | 61.2396 | -61.2488 | 0.054932 | -0.18768 | 122.7127 | 122.5479 | -122.3145 | -0.045776 | -0.027466 | 122.6578 | 61.1298 | 61.4044 | 0.15564 | 122.2824 | 122.7127 | 122.4426 | -0.054932 | -0.045776 | 122.2824 | 122.7127 | -0.054932 | 0.15564 | 122.4426 | -122.4152 | -122.5159
110.6875 | 122.7722 | -61.203 | 61.2122 | -0.018387 | 0.041825 | 0.034598 | -0.0002009 | -0.0067995 | 0.062203 | 0.063166 | 61.4456 | 61.0703 | -61.1938 | 61.2442 | -61.1389 | -61.3129 | -0.19684 | 0.064087 | 61.1801 | -61.3403 | 0.009155 | -0.14191 | 122.6486 | 122.4472 | -122.3511 | -0.13733 | -0.032043 | 122.6395 | 61.0062 | 61.2671 | 0.064087 | 122.2733 | 122.6486 | 122.3831 | -0.10986 | -0.13733 | 122.2733 | 122.6486 | -0.10986 | 0.064087 | 122.3831 | -122.406 | -122.5525
111.7344 | 122.731 | -61.1755 | 61.2534 | 0.0045015 | 0.038621 | 0.029471 | -0.0029779 | -0.010218 | 0.064553 | 0.064234 | 61.4182 | 61.0977 | -61.171 | 61.2305 | -61.1435 | -61.322 | -0.10071 | 0.064087 | 61.2442 | -61.3266 | 0.004578 | -0.15564 | 122.5937 | 122.406 | -122.3969 | -0.15106 | -0.009155 | 122.5891 | 61.0748 | 61.2396 | 0.032043 | 122.2733 | 122.5937 | 122.4197 | -0.14648 | -0.15106 | 122.2733 | 122.5937 | -0.14648 | 0.032043 | 122.4197 | -122.4243 | -122.58
112.6719 | 122.8088 | -61.1801 | 61.2305 | -0.010758 | 0.036912 | 0.035026 | -0.0049005 | -0.0078677 | 0.064553 | 0.060816 | 61.5005 | 61.0931 | -61.1618 | 61.3449 | -61.0565 | -61.2259 | -0.086975 | 0.20599 | 61.1984 | -61.2854 | 0.018311 | -0.13733 | 122.6807 | 122.525 | -122.287 | -0.10529 | -0.032044 | 122.6624 | 61.0931 | 61.3861 | 0.1236 | 122.2733 | 122.6807 | 122.3785 | -0.045776 | -0.10529 | 122.2733 | 122.6807 | -0.045776 | 0.1236 | 122.3785 | -122.3923 | -122.5159
113.6719 | 122.8134 | -61.2122 | 61.2488 | -0.003128 | 0.038621 | 0.037162 | -0.0042597 | -0.0082949 | 0.065194 | 0.06338 | 61.4822 | 61.0748 | -61.1526 | 61.3312 | -61.0474 | -61.2396 | -0.11444 | 0.20599 | 61.2396 | -61.2625 | 0.059509 | -0.17395 | 122.6944 | 122.5433 | -122.2961 | -0.050354 | -0.009155 | 122.6349 | 61.0977 | 61.4182 | 0.1648 | 122.287 | 122.6944 | 122.4518 | -0.027466 | -0.050354 | 122.287 | 122.6944 | -0.027466 | 0.1648 | 122.4518 | -122.4014 | -122.5113
114.6719 | 122.7631 | -61.2259 | 61.2671 | -0.003128 | 0.035844 | 0.038016 | -0.0040461 | -0.0093631 | 0.064553 | 0.06338 | 61.4365 | 61.0565 | -61.1801 | 61.2625 | -61.0931 | -61.2854 | -0.068665 | 0.13733 | 61.2305 | -61.29 | 0.045776 | -0.21057 | 122.6624 | 122.4884 | -122.3602 | -0.064087 | -0.036621 | 122.6166 | 61.1572 | 61.3632 | 0.13275 | 122.2824 | 122.6624 | 122.4564 | -0.059509 | -0.064087 | 122.2824 | 122.6624 | -0.059509 | 0.13275 | 122.4564 | -122.4472 | -122.5571
115.6719 | 122.6395 | -61.2305 | 61.2991 | -0.003128 | 0.041398 | 0.034171 | -0.0012689 | -0.0097903 | 0.065194 | 0.062312 | 61.4182 | 61.1847 | -61.171 | 61.2122 | -61.1755 | -61.3953 | 0.1236 | 0.07782 | 61.2671 | -61.3586 | 0.05951 | -0.11444 | 122.6486 | 122.4426 | -122.4747 | -0.12817 | -0.032043 | 122.5891 | 61.3541 | 61.3083 | 0.054932 | 122.4152 | 122.6486 | 122.4976 | -0.16479 | -0.12817 | 122.4152 | 122.6486 | -0.16479 | 0.054932 | 122.4976 | -122.4701 | -122.6578
116.6719 | 122.7997 | -61.1847 | 61.2488 | 0.0045015 | 0.037766 | 0.036307 | -0.0027643 | -0.010431 | 0.063271 | 0.062525 | 61.5051 | 61.0474 | -61.1435 | 61.3586 | -61.0336 | -61.2259 | -0.07782 | 0.21057 | 61.2442 | -61.2991 | 0.041198 | -0.20142 | 122.6898 | 122.5433 | -122.2824 | -0.11444 | -0.004577 | 122.6486 | 61.1069 | 61.3953 | 0.15106 | 122.2321 | 122.6898 | 122.4289 | -0.041199 | -0.11444 | 122.2321 | 122.6898 | -0.041199 | 0.15106 | 122.4289 | -122.3923 | -122.5479
117.6719 | 122.8134 | -61.2076 | 61.2396 | -0.003128 | 0.036698 | 0.033744 | -0.0029779 | -0.0097903 | 0.061776 | 0.06338 | 61.5051 | 61.0931 | -61.1435 | 61.3495 | -61.0519 | -61.2213 | -0.09613 | 0.2243 | 61.2305 | -61.2946 | 0.064087 | -0.14648 | 122.7127 | 122.5571 | -122.2916 | -0.086975 | -0.009155 | 122.6486 | 61.1115 | 61.4319 | 0.15564 | 122.3007 | 122.7127 | 122.4381 | -0.013732 | -0.086975 | 122.3007 | 122.7127 | -0.013732 | 0.15564 | 122.4381 | -122.3831 | -122.5342
118.6719 | 122.8043 | -61.2259 | 61.2442 | 0.0045015 | 0.039262 | 0.034171 | -0.0036187 | -0.010004 | 0.063698 | 0.062098 | 61.496 | 61.0703 | -61.1298 | 61.3358 | -61.0474 | -61.2396 | -0.10986 | 0.21057 | 61.203 | -61.2854 | 0.09613 | -0.17395 | 122.7219 | 122.5616 | -122.2916 | -0.059509 | -0.041199 | 122.6257 | 61.116 | 61.4365 | 0.17853 | 122.2961 | 122.7219 | 122.4289 | -0.013733 | -0.059509 | 122.2961 | 122.7219 | -0.013733 | 0.17853 | 122.4289 | -122.374 | -122.5296
119.6719 | 122.7951 | -61.1938 | 61.2488 | -0.010758 | 0.037339 | 0.034171 | -0.0044733 | -0.011286 | 0.063271 | 0.063166 | 61.4822 | 61.084 | -61.1206 | 61.3266 | -61.0519 | -61.2534 | -0.10986 | 0.19226 | 61.235 | -61.29 | 0.073243 | -0.16479 | 122.6761 | 122.5204 | -122.3007 | -0.09613 | -0.013733 | 122.6028 | 61.084 | 61.3861 | 0.14191 | 122.2778 | 122.6761 | 122.4289 | -0.059509 | -0.09613 | 122.2778 | 122.6761 | -0.059509 | 0.14191 | 122.4289 | -122.3694 | -122.5388
120.6719 | 122.644 | -61.2762 | 61.2762 | 0.0045015 | 0.044602 | 0.038657 | 0.0027899 | -0.0061587 | 0.061989 | 0.062525 | 61.3861 | 61.1206 | -61.203 | 61.1801 | -61.2442 | -61.4273 | -0.013733 | -0.009155 | 61.2396 | -61.3998 | 0.073242 | -0.15564 | 122.6624 | 122.4564 | -122.5204 | -0.1236 | -0.036621 | 122.5891 | 61.2625 | 61.2671 | 0.032043 | 122.3969 | 122.6624 | 122.5159 | -0.15106 | -0.1236 | 122.3969 | 122.6624 | -0.15106 | 0.032043 | 122.5159 | -122.4792 | -122.6761
121.6719 | 122.7402 | -61.203 | 61.2579 | -0.003128 | 0.035417 | 0.037375 | -0.0068231 | -0.0074405 | 0.064125 | 0.064234 | 61.4136 | 61.0703 | -61.1664 | 61.2442 | -61.116 | -61.3083 | -0.073242 | 0.10986 | 61.2259 | -61.3266 | 0.036621 | -0.18768 | 122.6166 | 122.4472 | -122.374 | -0.1236 | -0.032044 | 122.58 | 61.1298 | 61.3129 | 0.086975 | 122.2733 | 122.6166 | 122.4289 | -0.10529 | -0.1236 | 122.2733 | 122.6166 | -0.10529 | 0.086975 | 122.4289 | -122.4243 | -122.5845
122.6719 | 122.7905 | -61.1847 | 61.2488 | -0.010758 | 0.036698 | 0.033957 | -0.0055413 | -0.010004 | 0.063912 | 0.06338 | 61.4777 | 61.1023 | -61.1252 | 61.3312 | -61.0565 | -61.2442 | -0.091553 | 0.17395 | 61.2213 | -61.2946 | 0.059509 | -0.14648 | 122.6624 | 122.5159 | -122.3053 | -0.10986 | -0.027466 | 122.6028 | 61.0931 | 61.3586 | 0.12817 | 122.287 | 122.6624 | 122.406 | -0.05951 | -0.10986 | 122.287 | 122.6624 | -0.05951 | 0.12817 | 122.406 | -122.374 | -122.5433
123.6719 | 122.7951 | -61.2122 | 61.2534 | 0.01213 | 0.037766 | 0.03353 | -0.0038325 | -0.0091495 | 0.064125 | 0.063166 | 61.5051 | 61.0794 | -61.1389 | 61.3541 | -61.0336 | -61.2213 | -0.086975 | 0.21057 | 61.2259 | -61.2717 | 0.073242 | -0.17395 | 122.7173 | 122.5662 | -122.287 | -0.059509 | -0.027466 | 122.644 | 61.1252 | 61.4227 | 0.17853 | 122.2916 | 122.7173 | 122.438 | -0.009155 | -0.059509 | 122.2916 | 122.7173 | -0.009155 | 0.17853 | 122.438 | -122.3923 | -122.525
124.6719 | 122.8043 | -61.2213 | 61.2625 | 0.0045015 | 0.036698 | 0.031821 | -0.0053277 | -0.0078677 | 0.065194 | 0.062952 | 61.496 | 61.0657 | -61.1435 | 61.3403 | -61.0565 | -61.2259 | -0.12817 | 0.23346 | 61.235 | -61.2625 | 0.077819 | -0.19684 | 122.7173 | 122.5616 | -122.319 | -0.041199 | -0.027466 | 122.6395 | 61.0931 | 61.4548 | 0.16479 | 122.287 | 122.7173 | 122.4564 | -0.004578 | -0.041199 | 122.287 | 122.7173 | -0.004578 | 0.16479 | 122.4564 | -122.406 | -122.525
125.6719 | 122.699 | -61.2717 | 61.2671 | -0.003128 | 0.042039 | 0.036735 | 0.0027899 | -0.0053043 | 0.063057 | 0.062739 | 61.4227 | 61.1847 | -61.1801 | 61.2259 | -61.1572 | -61.3724 | 0.054932 | 0.068665 | 61.235 | -61.3358 | 0.091552 | -0.082398 | 122.6944 | 122.4976 | -122.4243 | -0.064087 | -0.032044 | 122.6028 | 61.3266 | 61.3403 | 0.11444 | 122.4564 | 122.6944 | 122.5067 | -0.10071 | -0.064087 | 122.4564 | 122.6944 | -0.10071 | 0.11444 | 122.5067 | -122.4472 | -122.6028
126.6719 | 122.7951 | -61.203 | 61.2259 | -0.003128 | 0.038621 | 0.036948 | -0.0049005 | -0.0078677 | 0.064553 | 0.065089 | 61.4777 | 61.084 | -61.1389 | 61.3266 | -61.0519 | -61.2305 | -0.10529 | 0.20142 | 61.2305 | -61.2762 | 0.064087 | -0.14191 | 122.6807 | 122.5296 | -122.2778 | -0.073242 | 0.004578 | 122.6166 | 61.0977 | 61.4044 | 0.15106 | 122.287 | 122.6807 | 122.4335 | -0.027466 | -0.073242 | 122.287 | 122.6807 | -0.027466 | 0.15106 | 122.4335 | -122.3648 | -122.5021
127.6719 | 122.7905 | -61.2122 | 61.2488 | 0.01213 | 0.037126 | 0.03353 | -0.0059687 | -0.0093631 | 0.06498 | 0.064234 | 61.4822 | 61.1069 | -61.1252 | 61.3174 | -61.0748 | -61.2442 | -0.086975 | 0.19684 | 61.2259 | -61.2808 | 0.086975 | -0.14191 | 122.6944 | 122.5296 | -122.3236 | -0.068665 | -0.022888 | 122.6074 | 61.1252 | 61.409 | 0.13733 | 122.319 | 122.6944 | 122.438 | -0.032044 | -0.068665 | 122.319 | 122.6944 | -0.032044 | 0.13733 | 122.438 | -122.374 | -122.5296
128.6719 | 122.7493 | -61.2442 | 61.2579 | -0.003128 | 0.038407 | 0.034598 | -0.0031915 | -0.0085085 | 0.064125 | 0.060816 | 61.4044 | 61.0794 | -61.1572 | 61.2442 | -61.1435 | -61.3174 | -0.068665 | 0.09613 | 61.2167 | -61.3037 | 0.086975 | -0.17853 | 122.6486 | 122.4884 | -122.4014 | -0.059509 | -0.041199 | 122.5616 | 61.1755 | 61.3403 | 0.10071 | 122.3236 | 122.6486 | 122.4609 | -0.073242 | -0.059509 | 122.3236 | 122.6486 | -0.073242 | 0.10071 | 122.4609 | -122.4152 | -122.5616
129.6719 | 122.7356 | -61.2076 | 61.2396 | -0.010758 | 0.035844 | 0.032035 | -0.0025507 | -0.010645 | 0.063698 | 0.062952 | 61.4044 | 61.0519 | -61.1801 | 61.2305 | -61.1435 | -61.3266 | -0.073242 | 0.068665 | 61.2259 | -61.3037 | 0.027466 | -0.18768 | 122.612 | 122.4381 | -122.3831 | -0.09613 | -0.013733 | 122.5845 | 61.1343 | 61.2762 | 0.064087 | 122.2595 | 122.612 | 122.4335 | -0.11902 | -0.09613 | 122.2595 | 122.612 | -0.11902 | 0.064087 | 122.4335 | -122.4197 | -122.5433
130.6719 | 122.699 | -61.2167 | 61.2671 | 0.0045015 | 0.039475 | 0.039084 | 0.0021491 | -0.0078677 | 0.06498 | 0.062525 | 61.4502 | 61.1755 | -61.1801 | 61.2579 | -61.1664 | -61.3586 | 0 | 0.10071 | 61.2442 | -61.3403 | 0.036621 | -0.091553 | 122.6669 | 122.4747 | -122.4335 | -0.1236 | -0.022888 | 122.6303 | 61.2167 | 61.3174 | 0.050354 | 122.3923 | 122.6669 | 122.4609 | -0.14191 | -0.1236 | 122.3923 | 122.6669 | -0.14191 | 0.050354 | 122.4609 | -122.4472 | -122.6074
131.6719 | 122.7859 | -61.1893 | 61.2259 | 0.01213 | 0.036912 | 0.035026 | -0.0072503 | -0.010004 | 0.06733 | 0.063166 | 61.4685 | 61.0794 | -61.1526 | 61.322 | -61.0657 | -61.2671 | -0.091553 | 0.21057 | 61.1893 | -61.2808 | 0.036621 | -0.14648 | 122.6578 | 122.5113 | -122.2916 | -0.091553 | -0.036621 | 122.6212 | 61.0977 | 61.3998 | 0.1236 | 122.2687 | 122.6578 | 122.3785 | -0.07782 | -0.091553 | 122.2687 | 122.6578 | -0.07782 | 0.1236 | 122.3785 | -122.3785 | -122.5067
132.6719 | 122.7951 | -61.1984 | 61.2717 | -0.010758 | 0.034776 | 0.033744 | -0.0046869 | -0.0078677 | 0.063912 | 0.062952 | 61.4777 | 61.0931 | -61.1435 | 61.2991 | -61.0703 | -61.2534 | -0.10071 | 0.1831 | 61.2442 | -61.2808 | 0.054931 | -0.17853 | 122.6761 | 122.4976 | -122.3419 | -0.082398 | -0.027465 | 122.6212 | 61.0977 | 61.3815 | 0.12817 | 122.2916 | 122.6761 | 122.4426 | -0.054932 | -0.082398 | 122.2916 | 122.6761 | -0.054932 | 0.12817 | 122.4426 | -122.4152 | -122.5525
133.6719 | 122.7722 | -61.2167 | 61.2488 | -0.003128 | 0.036698 | 0.036094 | -0.0066095 | -0.0087223 | 0.062844 | 0.063807 | 61.4502 | 61.0931 | -61.1572 | 61.2762 | -61.0748 | -61.2625 | -0.07782 | 0.15564 | 61.2213 | -61.2854 | 0.059509 | -0.15564 | 122.6669 | 122.493 | -122.3236 | -0.068664 | -0.027466 | 122.6074 | 61.1389 | 61.3724 | 0.14191 | 122.3099 | 122.6669 | 122.438 | -0.045776 | -0.068664 | 122.3099 | 122.6669 | -0.045776 | 0.14191 | 122.438 | -122.406 | -122.5342
134.6719 | 122.7539 | -61.2122 | 61.2534 | 0.0045015 | 0.037126 | 0.032248 | -0.0044733 | -0.0091495 | 0.063485 | 0.063807 | 61.441 | 61.1069 | -61.1526 | 61.2671 | -61.1023 | -61.2854 | -0.068665 | 0.1236 | 61.2259 | -61.2854 | 0.059509 | -0.14648 | 122.6532 | 122.4792 | -122.3557 | -0.073242 | -0.027466 | 122.5937 | 61.1435 | 61.3358 | 0.10986 | 122.319 | 122.6532 | 122.438 | -0.073242 | -0.073242 | 122.319 | 122.6532 | -0.073242 | 0.10986 | 122.438 | -122.406 | -122.5388
135.6719 | 122.7264 | -61.235 | 61.2534 | 0.0045015 | 0.034776 | 0.033744 | -0.0046869 | -0.0085085 | 0.06263 | 0.064661 | 61.409 | 61.0703 | -61.1801 | 61.2259 | -61.1526 | -61.3174 | -0.091553 | 0.086975 | 61.2076 | -61.3174 | 0.054931 | -0.18311 | 122.644 | 122.4609 | -122.406 | -0.082398 | -0.045776 | 122.5891 | 61.1435 | 61.322 | 0.082397 | 122.3053 | 122.644 | 122.4426 | -0.082398 | -0.082398 | 122.3053 | 122.644 | -0.082398 | 0.082397 | 122.4426 | -122.4335 | -122.5708
136.6719 | 122.7173 | -61.2534 | 61.2442 | -0.003128 | 0.03798 | 0.036307 | -0.0038325 | -0.0076541 | 0.064553 | 0.062312 | 61.4227 | 61.0428 | -61.1801 | 61.2488 | -61.1526 | -61.3083 | -0.11444 | 0.073242 | 61.2076 | -61.3312 | 0.073242 | -0.20142 | 122.6761 | 122.5021 | -122.3969 | -0.07782 | -0.036621 | 122.6028 | 61.1389 | 61.3266 | 0.10071 | 122.2961 | 122.6761 | 122.4609 | -0.054932 | -0.07782 | 122.2961 | 122.6761 | -0.054932 | 0.10071 | 122.4609 | -122.4243 | -122.5754
137.6719 | 122.7722 | -61.2259 | 61.2305 | 0.0045015 | 0.037339 | 0.032889 | -0.0034051 | -0.010431 | 0.062844 | 0.064661 | 61.4456 | 61.0519 | -61.1755 | 61.2762 | -61.1069 | -61.2991 | -0.091553 | 0.14648 | 61.2122 | -61.2854 | 0.050354 | -0.17853 | 122.6715 | 122.5021 | -122.3373 | -0.059509 | -0.018311 | 122.6212 | 61.1343 | 61.3724 | 0.11902 | 122.2778 | 122.6715 | 122.438 | -0.073242 | -0.059509 | 122.2778 | 122.6715 | -0.073242 | 0.11902 | 122.438 | -122.406 | -122.5159
138.6719 | 122.7356 | -61.2259 | 61.2854 | -0.003128 | 0.035203 | 0.035026 | -0.0014825 | -0.0095767 | 0.064339 | 0.06338 | 61.4182 | 61.0794 | -61.1801 | 61.2625 | -61.1298 | -61.3037 | -0.073242 | 0.10986 | 61.2213 | -61.2991 | 0.045776 | -0.20599 | 122.644 | 122.4884 | -122.4152 | -0.073242 | -0.064087 | 122.5983 | 61.1526 | 61.3358 | 0.09613 | 122.3053 | 122.644 | 122.4472 | -0.07782 | -0.073242 | 122.3053 | 122.644 | -0.07782 | 0.09613 | 122.4472 | -122.4655 | -122.5845
139.6719 | 122.7356 | -61.2488 | 61.2396 | -0.003128 | 0.037339 | 0.035026 | -0.0025507 | -0.0093631 | 0.063485 | 0.062525 | 61.4136 | 61.0748 | -61.1572 | 61.2305 | -61.1343 | -61.322 | -0.068665 | 0.082397 | 61.2122 | -61.29 | 0.091552 | -0.16479 | 122.6624 | 122.4792 | -122.374 | -0.041199 | -0.027466 | 122.5708 | 61.1801 | 61.3312 | 0.11444 | 122.3236 | 122.6624 | 122.4609 | -0.073242 | -0.041199 | 122.3236 | 122.6624 | -0.073242 | 0.11444 | 122.4609 | -122.3969 | -122.5296
140.6719 | 122.731 | -61.2167 | 61.2259 | -0.003128 | 0.037126 | 0.035453 | -0.0029779 | -0.010645 | 0.062416 | 0.060389 | 61.4227 | 61.0703 | -61.1755 | 61.2396 | -61.1526 | -61.3174 | -0.091553 | 0.073242 | 61.2213 | -61.3174 | 0.041199 | -0.15564 | 122.6395 | 122.4564 | -122.3785 | -0.10071 | -0.004578 | 122.5983 | 61.1252 | 61.29 | 0.064087 | 122.287 | 122.6395 | 122.438 | -0.10071 | -0.10071 | 122.287 | 122.6395 | -0.10071 | 0.064087 | 122.438 | -122.4014 | -122.5433
141.6719 | 122.7264 | -61.2259 | 61.2534 | -0.003128 | 0.038407 | 0.036948 | -0.0019099 | -0.0070133 | 0.064339 | 0.061884 | 61.4182 | 61.0657 | -61.1938 | 61.2396 | -61.1435 | -61.3174 | -0.091553 | 0.082397 | 61.2259 | -61.3358 | 0.032043 | -0.18768 | 122.644 | 122.4655 | -122.3969 | -0.10986 | -0.027466 | 122.612 | 61.1343 | 61.3083 | 0.082397 | 122.2916 | 122.644 | 122.4518 | -0.091553 | -0.10986 | 122.2916 | 122.644 | -0.091553 | 0.082397 | 122.4518 | -122.4472 | -122.5891
142.6719 | 122.7585 | -61.235 | 61.2213 | -0.010758 | 0.038835 | 0.033317 | -0.0027643 | -0.0082949 | 0.063057 | 0.064234 | 61.4594 | 61.0382 | -61.1618 | 61.2808 | -61.1298 | -61.2991 | -0.19226 | 0.11444 | 61.203 | -61.3037 | 0.073242 | -0.18311 | 122.6944 | 122.5159 | -122.3511 | -0.068665 | -0.01831 | 122.6212 | 61.0428 | 61.3495 | 0.10528 | 122.2733 | 122.6944 | 122.438 | -0.064087 | -0.068665 | 122.2733 | 122.6944 | -0.064087 | 0.10528 | 122.438 | -122.3831 | -122.525
143.6719 | 122.7676 | -61.2122 | 61.2167 | 0.0045015 | 0.037126 | 0.031394 | -0.0006281 | -0.0085085 | 0.06263 | 0.063166 | 61.4685 | 61.0153 | -61.1572 | 61.2854 | -61.1206 | -61.2991 | -0.20142 | 0.10529 | 61.1618 | -61.3174 | 0.054931 | -0.20142 | 122.6807 | 122.4976 | -122.3373 | -0.10529 | -0.054932 | 122.6257 | 61.0107 | 61.3174 | 0.091553 | 122.2275 | 122.6807 | 122.374 | -0.086975 | -0.10529 | 122.2275 | 122.6807 | -0.086975 | 0.091553 | 122.374 | -122.374 | -122.5342
144.6719 | 122.731 | -61.2213 | 61.2625 | 0.0045015 | 0.038835 | 0.032035 | -0.0016961 | -0.0080813 | 0.062844 | 0.06338 | 61.409 | 61.0794 | -61.1801 | 61.2305 | -61.1481 | -61.3129 | -0.091553 | 0.073242 | 61.1938 | -61.2946 | 0.041198 | -0.1831 | 122.6303 | 122.4518 | -122.4106 | -0.073243 | -0.068664 | 122.5891 | 61.1298 | 61.2946 | 0.073242 | 122.3007 | 122.6303 | 122.4152 | -0.091553 | -0.073243 | 122.3007 | 122.6303 | -0.091553 | 0.073242 | 122.4152 | -122.4426 | -122.5571
145.6719 | 122.7356 | -61.235 | 61.2534 | -0.010758 | 0.034989 | 0.035453 | -0.0021235 | -0.0089359 | 0.064125 | 0.064021 | 61.4136 | 61.0565 | -61.1755 | 61.235 | -61.1481 | -61.3312 | -0.09613 | 0.073242 | 61.1801 | -61.322 | 0.059509 | -0.19684 | 122.6486 | 122.4701 | -122.4014 | -0.086975 | -0.073242 | 122.5891 | 61.1389 | 61.3083 | 0.086975 | 122.2916 | 122.6486 | 122.4152 | -0.096131 | -0.086975 | 122.2916 | 122.6486 | -0.096131 | 0.086975 | 122.4152 | -122.4289 | -122.5754
146.6719 | 122.7173 | -61.235 | 61.235 | -0.010758 | 0.039475 | 0.035453 | -0.0012689 | -0.0070133 | 0.060494 | 0.064234 | 61.4456 | 61.0565 | -61.1526 | 61.2442 | -61.1572 | -61.322 | -0.1236 | 0.086975 | 61.2122 | -61.3037 | 0.082397 | -0.17853 | 122.6807 | 122.4792 | -122.3923 | -0.068665 | -0.022888 | 122.5983 | 61.1114 | 61.322 | 0.077819 | 122.2916 | 122.6807 | 122.4472 | -0.086975 | -0.068665 | 122.2916 | 122.6807 | -0.086975 | 0.077819 | 122.4472 | -122.3877 | -122.5388
147.6719 | 122.7539 | -61.1893 | 61.2259 | 0.0045015 | 0.037553 | 0.030539 | -0.0034051 | -0.0074405 | 0.062844 | 0.064234 | 61.4456 | 61.0474 | -61.171 | 61.2442 | -61.1389 | -61.3129 | -0.16479 | 0.086975 | 61.1847 | -61.3403 | 0.018311 | -0.17853 | 122.6349 | 122.4335 | -122.3648 | -0.15106 | -0.041199 | 122.6166 | 61.0245 | 61.2762 | 0.050354 | 122.2366 | 122.6349 | 122.374 | -0.1236 | -0.15106 | 122.2366 | 122.6349 | -0.1236 | 0.050354 | 122.374 | -122.3969 | -122.5662
148.6719 | 122.7631 | -61.1984 | 61.2396 | 0.0045015 | 0.037766 | 0.03588 | -0.0010553 | -0.0080813 | 0.061989 | 0.064234 | 61.4685 | 61.0382 | -61.1755 | 61.2854 | -61.1114 | -61.2946 | -0.19226 | 0.09613 | 61.171 | -61.3586 | 0.022888 | -0.20142 | 122.6669 | 122.4838 | -122.3511 | -0.16022 | -0.068665 | 122.644 | 61.0062 | 61.2946 | 0.086975 | 122.2366 | 122.6669 | 122.3694 | -0.096131 | -0.16022 | 122.2366 | 122.6669 | -0.096131 | 0.086975 | 122.3694 | -122.4152 | -122.5983
149.6719 | 122.7905 | -61.1893 | 61.1984 | -0.010758 | 0.040757 | 0.035453 | -0.0010553 | -0.0076541 | 0.065194 | 0.061884 | 61.4594 | 61.0886 | -61.1984 | 61.2671 | -61.1069 | -61.3037 | -0.2243 | 0.07782 | 61.1435 | -61.3403 | -0.009155 | -0.10986 | 122.6486 | 122.4564 | -122.3053 | -0.15106 | -0.054931 | 122.6578 | 60.965 | 61.2671 | 0.082397 | 122.2778 | 122.6486 | 122.3328 | -0.11444 | -0.15106 | 122.2778 | 122.6486 | -0.11444 | 0.082397 | 122.3328 | -122.3969 | -122.5388
150.6719 | 122.7814 | -61.203 | 61.2305 | -0.010758 | 0.040544 | 0.036094 | 0.0002265 | -0.0070133 | 0.063912 | 0.062739 | 61.4273 | 61.1069 | -61.203 | 61.2717 | -61.1389 | -61.3174 | -0.19226 | 0.073242 | 61.1755 | -61.3632 | 0 | -0.1236 | 122.6303 | 122.4747 | -122.3694 | -0.16022 | -0.054932 | 122.6303 | 61.0107 | 61.2762 | 0.064087 | 122.3099 | 122.6303 | 122.3785 | -0.11444 | -0.16022 | 122.3099 | 122.6303 | -0.11444 | 0.064087 | 122.3785 | -122.4335 | -122.5937
151.6719 | 122.7676 | -61.171 | 61.2167 | 0.0045015 | 0.039689 | 0.03588 | -0.0029779 | -0.0089359 | 0.063057 | 0.062525 | 61.4594 | 61.0611 | -61.1481 | 61.2762 | -61.1206 | -61.2854 | -0.19226 | 0.10529 | 61.1847 | -61.2991 | 0.022888 | -0.15564 | 122.6303 | 122.4472 | -122.3373 | -0.12817 | -0.032044 | 122.6074 | 60.9787 | 61.2762 | 0.050354 | 122.2321 | 122.6303 | 122.3557 | -0.11444 | -0.12817 | 122.2321 | 122.6303 | -0.11444 | 0.050354 | 122.3557 | -122.3648 | -122.5159
152.6719 | 122.7814 | -61.203 | 61.2305 | 0.0045015 | 0.039262 | 0.037375 | -0.0002009 | -0.0076541 | 0.064125 | 0.064234 | 61.4731 | 61.0886 | -61.171 | 61.2762 | -61.1114 | -61.2854 | -0.20599 | 0.10529 | 61.1664 | -61.3266 | 0.032044 | -0.14191 | 122.6761 | 122.4792 | -122.3419 | -0.1236 | -0.064087 | 122.644 | 60.997 | 61.3083 | 0.091553 | 122.2916 | 122.6761 | 122.3694 | -0.082397 | -0.1236 | 122.2916 | 122.6761 | -0.082397 | 0.091553 | 122.3694 | -122.4014 | -122.5571
153.6719 | 122.7722 | -61.203 | 61.2213 | 0.0045015 | 0.039262 | 0.037375 | -0.0012689 | -0.0070133 | 0.06498 | 0.062312 | 61.4639 | 61.0611 | -61.171 | 61.2762 | -61.1206 | -61.29 | -0.2243 | 0.09613 | 61.1435 | -61.3678 | 0.032044 | -0.16022 | 122.6669 | 122.4792 | -122.3419 | -0.16479 | -0.077819 | 122.6349 | 60.9787 | 61.2991 | 0.082398 | 122.2641 | 122.6669 | 122.3465 | -0.086975 | -0.16479 | 122.2641 | 122.6669 | -0.086975 | 0.082398 | 122.3465 | -122.3923 | -122.5891
154.6719 | 122.7859 | -61.203 | 61.203 | 0.0045015 | 0.041184 | 0.033317 | -0.0008417 | -0.0061587 | 0.064553 | 0.06338 | 61.4639 | 61.0931 | -61.1801 | 61.2671 | -61.1206 | -61.2854 | -0.21057 | 0.082397 | 61.1389 | -61.3358 | 0.022888 | -0.10986 | 122.6669 | 122.4701 | -122.3236 | -0.13275 | -0.064087 | 122.644 | 60.9924 | 61.2854 | 0.082398 | 122.2961 | 122.6669 | 122.3419 | -0.082397 | -0.13275 | 122.2961 | 122.6669 | -0.082397 | 0.082398 | 122.3419 | -122.3831 | -122.5388
155.6719 | 122.7768 | -61.1984 | 61.203 | -0.010758 | 0.043962 | 0.038657 | -0.0010553 | -0.0072269 | 0.065834 | 0.062952 | 61.4365 | 61.0794 | -61.203 | 61.2625 | -61.1298 | -61.3129 | -0.19226 | 0.07782 | 61.1618 | -61.3586 | -0.004578 | -0.1236 | 122.6349 | 122.4609 | -122.3328 | -0.16022 | -0.041199 | 122.6395 | 61.0062 | 61.2762 | 0.068664 | 122.2778 | 122.6349 | 122.3602 | -0.11444 | -0.16022 | 122.2778 | 122.6349 | -0.11444 | 0.068664 | 122.3602 | -122.406 | -122.5616
156.6719 | 122.6532 | -61.2213 | 61.2488 | 0.0045015 | 0.045457 | 0.039084 | -0.0010553 | -0.0063723 | 0.064125 | 0.062739 | 61.3449 | 61.1481 | -61.2259 | 61.1435 | -61.2259 | -61.409 | -0.032043 | -0.036621 | 61.2076 | -61.4044 | -0.004578 | -0.10071 | 122.5662 | 122.3648 | -122.4747 | -0.18311 | -0.041198 | 122.5708 | 61.1893 | 61.1847 | -0.004578 | 122.3694 | 122.5662 | 122.4289 | -0.18768 | -0.18311 | 122.3694 | 122.5662 | -0.18768 | -0.004578 | 122.4289 | -122.4747 | -122.6532
157.6719 | 122.644 | -61.235 | 61.2534 | -0.018387 | 0.042466 | 0.037162 | 0.0004401 | -0.0067995 | 0.065194 | 0.062525 | 61.3586 | 61.1389 | -61.2076 | 61.1298 | -61.2579 | -61.4319 | -0.009155 | -0.045776 | 61.2305 | -61.409 | 0.027465 | -0.11444 | 122.5937 | 122.3648 | -122.5113 | -0.17395 | -0.022888 | 122.5662 | 61.2259 | 61.1893 | -0.022889 | 122.374 | 122.5937 | 122.4655 | -0.19684 | -0.17395 | 122.374 | 122.5937 | -0.19684 | -0.022889 | 122.4655 | -122.4609 | -122.6624
158.6719 | 122.7539 | -61.171 | 61.2259 | -0.003128 | 0.039475 | 0.040366 | -0.0014825 | -0.0072269 | 0.063271 | 0.063593 | 61.441 | 61.116 | -61.1984 | 61.2442 | -61.1206 | -61.29 | -0.20599 | 0.086975 | 61.1664 | -61.3312 | -0.027466 | -0.10986 | 122.612 | 122.4152 | -122.3465 | -0.16022 | -0.059509 | 122.6395 | 60.965 | 61.2579 | 0.050354 | 122.287 | 122.612 | 122.3373 | -0.11902 | -0.16022 | 122.287 | 122.612 | -0.11902 | 0.050354 | 122.3373 | -122.4243 | -122.5571
159.6719 | 122.7722 | -61.1984 | 61.1893 | -0.003128 | 0.040971 | 0.036521 | -0.0025507 | -0.0059451 | 0.064339 | 0.062312 | 61.3998 | 61.0886 | -61.1984 | 61.2122 | -61.1572 | -61.3129 | -0.16937 | 0.064087 | 61.1847 | -61.3632 | 0 | -0.10071 | 122.5983 | 122.4106 | -122.3465 | -0.16479 | -0.004578 | 122.5983 | 61.0291 | 61.2625 | 0.041198 | 122.287 | 122.5983 | 122.3831 | -0.11444 | -0.16479 | 122.287 | 122.5983 | -0.11444 | 0.041198 | 122.3831 | -122.3877 | -122.5525
160.6719 | 122.7264 | -61.203 | 61.2076 | -0.010758 | 0.042039 | 0.038444 | -0.0010553 | -0.0080813 | 0.065194 | 0.064234 | 61.4044 | 61.1206 | -61.2076 | 61.2122 | -61.1801 | -61.3403 | -0.15106 | 0.032043 | 61.1801 | -61.3678 | -0.004578 | -0.086976 | 122.6074 | 122.4152 | -122.3877 | -0.16479 | -0.027466 | 122.612 | 61.0519 | 61.235 | 0.022888 | 122.3236 | 122.6074 | 122.3831 | -0.13733 | -0.16479 | 122.3236 | 122.6074 | -0.13733 | 0.022888 | 122.3831 | -122.4152 | -122.5754
161.6719 | 122.7173 | -61.203 | 61.2076 | 0.0045015 | 0.04268 | 0.038657 | 1.2902e-05 | -0.0080813 | 0.066048 | 0.063593 | 61.3678 | 61.1114 | -61.2076 | 61.1801 | -61.1938 | -61.3724 | -0.11902 | 0.013733 | 61.1893 | -61.3678 | -0.004578 | -0.096131 | 122.5708 | 122.3831 | -122.4014 | -0.16479 | -0.018311 | 122.5754 | 61.084 | 61.2167 | 0.009155 | 122.3145 | 122.5708 | 122.3923 | -0.16937 | -0.16479 | 122.3145 | 122.5708 | -0.16937 | 0.009155 | 122.3923 | -122.4152 | -122.5754
162.6719 | 122.6944 | -61.1847 | 61.2167 | -0.018387 | 0.042039 | 0.036094 | -0.0008417 | -0.0067995 | 0.064553 | 0.062312 | 61.3632 | 61.1618 | -61.2213 | 61.1618 | -61.2167 | -61.3861 | -0.10529 | -0.013733 | 61.1984 | -61.3907 | -0.036621 | -0.054932 | 122.5479 | 122.3465 | -122.4335 | -0.20599 | -0.018311 | 122.5845 | 61.0794 | 61.171 | -0.032044 | 122.3465 | 122.5479 | 122.3831 | -0.20142 | -0.20599 | 122.3465 | 122.5479 | -0.20142 | -0.032044 | 122.3831 | -122.438 | -122.6074
163.6719 | 122.644 | -61.2213 | 61.2396 | 0.0045015 | 0.042039 | 0.039084 | -0.0021235 | -0.0040225 | 0.064553 | 0.061884 | 61.3495 | 61.1435 | -61.2396 | 61.1206 | -61.2534 | -61.4319 | -0.009155 | -0.045776 | 61.235 | -61.4182 | -0.018311 | -0.09613 | 122.5708 | 122.3419 | -122.493 | -0.19684 | -0.004578 | 122.5891 | 61.2122 | 61.1755 | -0.032044 | 122.3648 | 122.5708 | 122.4564 | -0.21057 | -0.19684 | 122.3648 | 122.5708 | -0.21057 | -0.032044 | 122.4564 | -122.4792 | -122.6578
164.6719 | 122.6532 | -61.2396 | 61.2442 | -0.003128 | 0.043748 | 0.036094 | -0.0002009 | -0.0063723 | 0.064553 | 0.065089 | 61.3358 | 61.1755 | -61.2396 | 61.1252 | -61.2442 | -61.4319 | -0.009155 | -0.045776 | 61.2167 | -61.409 | 0 | -0.068665 | 122.5754 | 122.3648 | -122.4884 | -0.16937 | -0.027466 | 122.5754 | 61.2305 | 61.1938 | -0.004578 | 122.4152 | 122.5754 | 122.4564 | -0.19226 | -0.16937 | 122.4152 | 122.5754 | -0.19226 | -0.004578 | 122.4564 | -122.4838 | -122.6532
165.6719 | 122.7448 | -61.171 | 61.2259 | -0.003128 | 0.041398 | 0.034385 | -0.0027643 | -0.0044497 | 0.066048 | 0.06338 | 61.3998 | 61.1069 | -61.203 | 61.2122 | -61.1618 | -61.322 | -0.16022 | 0.059509 | 61.2076 | -61.3586 | -0.032044 | -0.11902 | 122.5708 | 122.3831 | -122.3877 | -0.18768 | -0.01831 | 122.6028 | 61.0107 | 61.2305 | 0.009155 | 122.2778 | 122.5708 | 122.3785 | -0.15106 | -0.18768 | 122.2778 | 122.5708 | -0.15106 | 0.009155 | 122.3785 | -122.4289 | -122.5845
166.6719 | 122.7448 | -61.1847 | 61.2122 | -0.010758 | 0.042039 | 0.039084 | -0.0019099 | -0.0035953 | 0.066475 | 0.06338 | 61.3815 | 61.1206 | -61.2213 | 61.1847 | -61.1847 | -61.3586 | -0.14648 | 0.045776 | 61.1801 | -61.3953 | -0.036621 | -0.091553 | 122.5662 | 122.3694 | -122.3969 | -0.21057 | -0.032043 | 122.6028 | 61.0382 | 61.2305 | 0 | 122.3053 | 122.5662 | 122.3648 | -0.17395 | -0.21057 | 122.3053 | 122.5662 | -0.17395 | 0 | 122.3648 | -122.4335 | -122.6074
167.6719 | 122.7036 | -61.1984 | 61.2259 | 0.0045015 | 0.041612 | 0.038871 | -0.0016961 | -0.0053043 | 0.066475 | 0.063807 | 61.3724 | 61.1206 | -61.2213 | 61.1801 | -61.1938 | -61.3541 | -0.12817 | 0.013733 | 61.2259 | -61.3678 | -0.022888 | -0.10529 | 122.5708 | 122.3785 | -122.4197 | -0.16937 | 0 | 122.5937 | 61.0703 | 61.2122 | 0.004577 | 122.319 | 122.5708 | 122.4243 | -0.15564 | -0.16937 | 122.319 | 122.5708 | -0.15564 | 0.004577 | 122.4243 | -122.4472 | -122.5937
168.6719 | 122.6807 | -61.1893 | 61.2396 | -0.003128 | 0.041612 | 0.034812 | -0.0021235 | -0.0063723 | 0.063698 | 0.064875 | 61.3815 | 61.1572 | -61.2122 | 61.1618 | -61.2213 | -61.3907 | -0.10529 | -0.004578 | 61.1984 | -61.4136 | -0.022888 | -0.082397 | 122.5708 | 122.3511 | -122.4609 | -0.2243 | -0.041199 | 122.5937 | 61.084 | 61.1847 | -0.032043 | 122.3465 | 122.5708 | 122.3877 | -0.20142 | -0.2243 | 122.3465 | 122.5708 | -0.20142 | -0.032043 | 122.3877 | -122.4518 | -122.6532
169.6719 | 122.6715 | -61.1893 | 61.2305 | -0.003128 | 0.043321 | 0.036094 | -0.0021235 | -0.0048769 | 0.064766 | 0.063166 | 61.3541 | 61.1526 | -61.2076 | 61.1435 | -61.235 | -61.4136 | -0.068665 | -0.022888 | 61.2076 | -61.4044 | -0.018311 | -0.07782 | 122.5433 | 122.3328 | -122.4655 | -0.21515 | -0.022888 | 122.5616 | 61.1206 | 61.1664 | -0.045776 | 122.3419 | 122.5433 | 122.3969 | -0.2243 | -0.21515 | 122.3419 | 122.5433 | -0.2243 | -0.045776 | 122.3969 | -122.4381 | -122.6349
170.6719 | 122.6303 | -61.2305 | 61.2396 | -0.003128 | 0.04503 | 0.038444 | -0.0010553 | -0.0076541 | 0.065621 | 0.06338 | 61.3403 | 61.1664 | -61.2259 | 61.1069 | -61.2488 | -61.4365 | -0.009155 | -0.045776 | 61.2213 | -61.4182 | 0.004578 | -0.073242 | 122.5708 | 122.3373 | -122.4884 | -0.18768 | -0.018311 | 122.5662 | 61.2213 | 61.1847 | -0.01831 | 122.3969 | 122.5708 | 122.4518 | -0.20599 | -0.18768 | 122.3969 | 122.5708 | -0.20599 | -0.01831 | 122.4518 | -122.4655 | -122.6578
171.6719 | 122.7402 | -61.1755 | 61.2122 | -0.003128 | 0.043107 | 0.037375 | -0.0046869 | -0.0055179 | 0.064766 | 0.06338 | 61.3953 | 61.1343 | -61.2076 | 61.2122 | -61.171 | -61.3403 | -0.15106 | 0.036621 | 61.1847 | -61.3678 | -0.032044 | -0.07782 | 122.5708 | 122.3877 | -122.3831 | -0.19226 | -0.027466 | 122.6028 | 61.0245 | 61.2122 | 0.004578 | 122.3099 | 122.5708 | 122.3602 | -0.16479 | -0.19226 | 122.3099 | 122.5708 | -0.16479 | 0.004578 | 122.3602 | -122.4197 | -122.58
172.6719 | 122.7219 | -61.1801 | 61.2076 | -0.010758 | 0.043321 | 0.033317 | -0.0012689 | -0.0029543 | 0.065407 | 0.063593 | 61.3678 | 61.1343 | -61.2167 | 61.1801 | -61.1893 | -61.3632 | -0.12817 | 0.022888 | 61.2213 | -61.3998 | -0.036621 | -0.073243 | 122.5479 | 122.3602 | -122.3969 | -0.21973 | 0.013732 | 122.5845 | 61.0519 | 61.203 | -0.009155 | 122.3145 | 122.5479 | 122.4014 | -0.1831 | -0.21973 | 122.3145 | 122.5479 | -0.1831 | -0.009155 | 122.4014 | -122.4243 | -122.6074
173.6719 | 122.6944 | -61.1938 | 61.2305 | -0.003128 | 0.04268 | 0.039725 | -0.0029779 | -0.0048769 | 0.065407 | 0.063593 | 61.3724 | 61.1435 | -61.2122 | 61.1481 | -61.235 | -61.3998 | -0.10529 | -0.022888 | 61.2076 | -61.3953 | -0.01831 | -0.086975 | 122.5662 | 122.3419 | -122.4655 | -0.20142 | -0.022888 | 122.5845 | 61.0886 | 61.171 | -0.041198 | 122.3373 | 122.5662 | 122.4014 | -0.20599 | -0.20142 | 122.3373 | 122.5662 | -0.20599 | -0.041198 | 122.4014 | -122.4426 | -122.6257
174.6719 | 122.6807 | -61.2076 | 61.2396 | -0.003128 | 0.044389 | 0.03588 | -0.0025507 | -0.0063723 | 0.065407 | 0.061671 | 61.3586 | 61.1618 | -61.2213 | 61.1481 | -61.235 | -61.4044 | -0.073242 | -0.036621 | 61.2305 | -61.4044 | -0.013732 | -0.07782 | 122.5662 | 122.3557 | -122.4747 | -0.19684 | -0.009155 | 122.58 | 61.1343 | 61.171 | -0.027465 | 122.3694 | 122.5662 | 122.4381 | -0.19684 | -0.19684 | 122.3694 | 122.5662 | -0.19684 | -0.027465 | 122.4381 | -122.4609 | -122.644
175.6719 | 122.6669 | -61.2259 | 61.2488 | -0.010758 | 0.04268 | 0.034812 | -0.0016961 | -0.0057315 | 0.067971 | 0.065302 | 61.3586 | 61.1435 | -61.235 | 61.1206 | -61.2396 | -61.409 | -0.036621 | -0.022888 | 61.2442 | -61.409 | -0.009155 | -0.10529 | 122.5845 | 122.3465 | -122.4884 | -0.18311 | -0.004577 | 122.5937 | 61.1893 | 61.203 | -0.013733 | 122.3694 | 122.5845 | 122.4701 | -0.18311 | -0.18311 | 122.3694 | 122.5845 | -0.18311 | -0.013733 | 122.4701 | -122.4838 | -122.6578
176.6719 | 122.6578 | -61.203 | 61.2717 | -0.018387 | 0.04503 | 0.038871 | -0.0016961 | -0.0061587 | 0.063057 | 0.064661 | 61.3403 | 61.1481 | -61.2259 | 61.1298 | -61.2442 | -61.4044 | -0.018311 | -0.036621 | 61.2534 | -61.4319 | -0.022888 | -0.1236 | 122.5433 | 122.3328 | -122.5159 | -0.22888 | -0.01831 | 122.5662 | 61.1847 | 61.1664 | -0.041199 | 122.3511 | 122.5433 | 122.4564 | -0.20142 | -0.22888 | 122.3511 | 122.5433 | -0.20142 | -0.041199 | 122.4564 | -122.4976 | -122.7036
177.6719 | 122.6166 | -61.2488 | 61.2717 | -0.010758 | 0.044816 | 0.039512 | -0.0004145 | -0.0059451 | 0.064553 | 0.064234 | 61.3495 | 61.1572 | -61.2259 | 61.1343 | -61.2671 | -61.4639 | 0.013733 | -0.041199 | 61.235 | -61.3998 | 0.022888 | -0.11444 | 122.5983 | 122.3831 | -122.5388 | -0.15106 | -0.036621 | 122.5754 | 61.2625 | 61.2076 | -0.018311 | 122.406 | 122.5983 | 122.4838 | -0.21515 | -0.15106 | 122.406 | 122.5983 | -0.21515 | -0.018311 | 122.4838 | -122.4976 | -122.6715
178.6719 | 122.6807 | -61.203 | 61.2305 | -0.003128 | 0.042466 | 0.039939 | -0.0019099 | -0.0046633 | 0.066903 | 0.062098 | 61.3495 | 61.1481 | -61.235 | 61.1572 | -61.2259 | -61.409 | -0.07782 | -0.036621 | 61.2076 | -61.3953 | -0.032043 | -0.082398 | 122.5525 | 122.3602 | -122.4564 | -0.19226 | -0.022888 | 122.5845 | 61.1252 | 61.1664 | -0.022888 | 122.3511 | 122.5525 | 122.4106 | -0.20599 | -0.19226 | 122.3511 | 122.5525 | -0.20599 | -0.022888 | 122.4106 | -122.4655 | -122.6257
179.6719 | 122.6715 | -61.2076 | 61.235 | -0.003128 | 0.043107 | 0.04058 | -0.0012689 | -0.0053043 | 0.069252 | 0.064661 | 61.3541 | 61.171 | -61.203 | 61.1298 | -61.2305 | -61.409 | -0.036621 | -0.013733 | 61.2396 | -61.3907 | 0.004578 | -0.064087 | 122.5616 | 122.3373 | -122.4655 | -0.18311 | 0.004578 | 122.5571 | 61.171 | 61.1938 | -0.022888 | 122.3785 | 122.5616 | 122.4472 | -0.20142 | -0.18311 | 122.3785 | 122.5616 | -0.20142 | -0.022888 | 122.4472 | -122.438 | -122.6257
180.6719 | 122.644 | -61.2213 | 61.2488 | -0.010758 | 0.043962 | 0.03118 | -0.0014825 | -0.0055179 | 0.066475 | 0.067225 | 61.3403 | 61.1343 | -61.2305 | 61.1343 | -61.2442 | -61.4227 | -0.004578 | -0.036621 | 61.2534 | -61.409 | -0.009156 | -0.11444 | 122.5616 | 122.3557 | -122.493 | -0.18768 | 0.004578 | 122.5708 | 61.2167 | 61.1847 | -0.022889 | 122.3557 | 122.5616 | 122.4747 | -0.20142 | -0.18768 | 122.3557 | 122.5616 | -0.20142 | -0.022889 | 122.4747 | -122.4792 | -122.6578
181.6719 | 122.644 | -61.2259 | 61.2808 | -0.010758 | 0.044175 | 0.036521 | -0.0019099 | -0.0070133 | 0.067543 | 0.061884 | 61.3403 | 61.1664 | -61.2213 | 61.1206 | -61.2534 | -61.4365 | -0.004578 | -0.045776 | 61.2259 | -61.4319 | 0.004578 | -0.11444 | 122.5662 | 122.3465 | -122.5342 | -0.20599 | -0.054932 | 122.5616 | 61.2213 | 61.1801 | -0.027466 | 122.3923 | 122.5662 | 122.4518 | -0.21057 | -0.20599 | 122.3923 | 122.5662 | -0.21057 | -0.027466 | 122.4518 | -122.5021 | -122.7127
182.6719 | 122.612 | -61.2259 | 61.2213 | -0.003128 | 0.043748 | 0.043998 | -0.0002009 | -0.0050907 | 0.065194 | 0.063166 | 61.3312 | 61.1847 | -61.235 | 61.1114 | -61.2762 | -61.4594 | -0.009155 | -0.036621 | 61.2534 | -61.4227 | -0.009155 | -0.036621 | 122.5571 | 122.3373 | -122.4976 | -0.19684 | 0.032044 | 122.5662 | 61.2167 | 61.1893 | -0.050354 | 122.4106 | 122.5571 | 122.4792 | -0.23346 | -0.19684 | 122.4106 | 122.5571 | -0.23346 | -0.050354 | 122.4792 | -122.4564 | -122.644
183.6719 | 122.6715 | -61.1984 | 61.2488 | 0.0045015 | 0.047807 | 0.037162 | -0.0023371 | -0.0055179 | 0.065834 | 0.061671 | 61.4273 | 61.1755 | -61.2122 | 61.1847 | -61.1984 | -61.3953 | -0.018311 | 0.054932 | 61.2717 | -61.3861 | -0.013733 | -0.073242 | 122.6257 | 122.3831 | -122.4472 | -0.18768 | 0.022888 | 122.6395 | 61.1801 | 61.2534 | 0 | 122.374 | 122.6257 | 122.4701 | -0.19684 | -0.18768 | 122.374 | 122.6257 | -0.19684 | 0 | 122.4701 | -122.4609 | -122.6349
184.6719 | 122.6852 | -61.171 | 61.2442 | -0.026017 | 0.044602 | 0.036948 | -0.0029779 | -0.0040225 | 0.066689 | 0.062098 | 61.4319 | 61.1938 | -61.2076 | 61.2213 | -61.1481 | -61.3541 | -0.013733 | 0.086975 | 61.2534 | -61.3815 | -0.036622 | -0.050354 | 122.6028 | 122.3923 | -122.3923 | -0.21057 | 0.009155 | 122.6395 | 61.1572 | 61.2579 | 0.022888 | 122.3648 | 122.6028 | 122.4243 | -0.18311 | -0.21057 | 122.3648 | 122.6028 | -0.18311 | 0.022888 | 122.4243 | -122.4518 | -122.6257
185.6719 | 122.644 | -61.1801 | 61.2671 | -0.018387 | 0.04503 | 0.036094 | -0.0004145 | -0.0053043 | 0.063912 | 0.065516 | 61.3678 | 61.1801 | -61.2122 | 61.1298 | -61.235 | -61.4273 | 0.022888 | -0.022888 | 61.2579 | -61.4044 | -0.032043 | -0.086975 | 122.5479 | 122.3099 | -122.5021 | -0.2243 | -0.009155 | 122.58 | 61.203 | 61.1572 | -0.054931 | 122.3602 | 122.5479 | 122.4381 | -0.24719 | -0.2243 | 122.3602 | 122.5479 | -0.24719 | -0.054931 | 122.4381 | -122.4792 | -122.6715
186.6719 | 122.6578 | -61.2305 | 61.2259 | -0.018387 | 0.044602 | 0.038657 | -0.0034051 | -0.0038089 | 0.066262 | 0.062525 | 61.3998 | 61.1755 | -61.2122 | 61.1526 | -61.2122 | -61.4182 | -0.004578 | 0.004578 | 61.2213 | -61.4227 | 0.018311 | -0.050354 | 122.6303 | 122.3831 | -122.438 | -0.19226 | -0.004578 | 122.612 | 61.2259 | 61.235 | 0.018311 | 122.406 | 122.6303 | 122.4518 | -0.18768 | -0.19226 | 122.406 | 122.6303 | -0.18768 | 0.018311 | 122.4518 | -122.438 | -122.6486
187.6719 | 122.6578 | -61.1984 | 61.2579 | -0.018387 | 0.045457 | 0.040793 | -0.0023371 | -0.0038089 | 0.065834 | 0.063807 | 61.4502 | 61.1664 | -61.2122 | 61.2076 | -61.1801 | -61.377 | -0.004578 | 0.07782 | 61.2579 | -61.3907 | -0.013733 | -0.091553 | 122.6486 | 122.406 | -122.4381 | -0.19226 | 0 | 122.6624 | 61.1938 | 61.2762 | 0.01831 | 122.3648 | 122.6486 | 122.4564 | -0.17853 | -0.19226 | 122.3648 | 122.6486 | -0.17853 | 0.01831 | 122.4564 | -122.4701 | -122.6486
188.6719 | 122.7127 | -61.235 | 61.2579 | -0.003128 | 0.04738 | 0.035666 | -0.0042597 | -0.0048769 | 0.066689 | 0.064661 | 61.4365 | 61.171 | -61.2076 | 61.2259 | -61.1618 | -61.3495 | 0 | 0.091553 | 61.2762 | -61.3861 | 0.027465 | -0.086976 | 122.6715 | 122.4609 | -122.4197 | -0.15106 | 0.01831 | 122.644 | 61.235 | 61.3266 | 0.073242 | 122.406 | 122.6715 | 122.5113 | -0.11444 | -0.15106 | 122.406 | 122.6715 | -0.11444 | 0.073242 | 122.5113 | -122.4655 | -122.644
189.6719 | 122.6944 | -61.1893 | 61.2762 | -0.010758 | 0.042253 | 0.035026 | -0.0031915 | -0.0044497 | 0.063698 | 0.064234 | 61.4227 | 61.1572 | -61.1847 | 61.2122 | -61.1618 | -61.3358 | 0.018311 | 0.11902 | 61.2808 | -61.3724 | 0.004578 | -0.11902 | 122.612 | 122.4014 | -122.438 | -0.1831 | 0.004578 | 122.6074 | 61.2076 | 61.3083 | 0.027466 | 122.3465 | 122.612 | 122.4701 | -0.14648 | -0.1831 | 122.3465 | 122.612 | -0.14648 | 0.027466 | 122.4701 | -122.4609 | -122.6486
190.6719 | 122.6486 | -61.1938 | 61.29 | -0.003128 | 0.041612 | 0.039084 | -0.0042597 | -0.0048769 | 0.066262 | 0.062525 | 61.3907 | 61.2305 | -61.1801 | 61.171 | -61.1801 | -61.377 | 0.11444 | 0.073242 | 61.3129 | -61.3312 | 0.013733 | -0.059509 | 122.5845 | 122.3648 | -122.4701 | -0.13733 | 0.022888 | 122.5708 | 61.3083 | 61.2671 | 0.013733 | 122.4243 | 122.5845 | 122.5067 | -0.1831 | -0.13733 | 122.4243 | 122.5845 | -0.1831 | 0.013733 | 122.5067 | -122.4701 | -122.6212
191.6719 | 122.644 | -61.1801 | 61.2854 | -0.003128 | 0.042253 | 0.034385 | -0.0068231 | -0.0063723 | 0.064553 | 0.063166 | 61.3861 | 61.2076 | -61.203 | 61.1755 | -61.1847 | -61.3861 | 0.12817 | 0.091553 | 61.3037 | -61.377 | -0.022888 | -0.077819 | 122.5662 | 122.3557 | -122.4701 | -0.19684 | 0.018311 | 122.5891 | 61.3083 | 61.2717 | -0.004577 | 122.3877 | 122.5662 | 122.4838 | -0.20599 | -0.19684 | 122.3877 | 122.5662 | -0.20599 | -0.004577 | 122.4838 | -122.4884 | -122.6624
192.6719 | 122.6761 | -61.2259 | 61.2671 | -0.003128 | 0.04268 | 0.035239 | -0.0006281 | -0.0046633 | 0.067116 | 0.061244 | 61.4227 | 61.1984 | -61.2122 | 61.1938 | -61.1847 | -61.377 | 0.059509 | 0.10071 | 61.2946 | -61.3541 | 0.013733 | -0.068665 | 122.6486 | 122.4197 | -122.4518 | -0.12817 | 0.027466 | 122.6349 | 61.2854 | 61.3266 | 0.041199 | 122.4243 | 122.6486 | 122.5204 | -0.15106 | -0.12817 | 122.4243 | 122.6486 | -0.15106 | 0.041199 | 122.5204 | -122.4792 | -122.6212
193.6719 | 122.6578 | -61.203 | 61.29 | 0.0045015 | 0.042893 | 0.032676 | -0.0038325 | -0.0063723 | 0.064553 | 0.062739 | 61.3907 | 61.1847 | -61.1938 | 61.1847 | -61.1893 | -61.3861 | 0.09613 | 0.082397 | 61.3174 | -61.3632 | 0.009155 | -0.10529 | 122.5937 | 122.3877 | -122.4792 | -0.16022 | 0.027466 | 122.5845 | 61.2991 | 61.2854 | 0.013733 | 122.3877 | 122.5937 | 122.5204 | -0.1831 | -0.16022 | 122.3877 | 122.5937 | -0.1831 | 0.013733 | 122.5204 | -122.4838 | -122.6532
194.6719 | 122.6395 | -61.2396 | 61.2946 | -0.003128 | 0.043962 | 0.036307 | -0.0051141 | -0.0078677 | 0.06263 | 0.063593 | 61.3907 | 61.1664 | -61.1893 | 61.171 | -61.1847 | -61.3861 | 0.11902 | 0.073242 | 61.3266 | -61.3541 | 0.050354 | -0.12817 | 122.6303 | 122.4106 | -122.4792 | -0.11444 | 0.032043 | 122.58 | 61.3586 | 61.3129 | 0.054932 | 122.406 | 122.6303 | 122.5662 | -0.14648 | -0.11444 | 122.406 | 122.6303 | -0.14648 | 0.054932 | 122.5662 | -122.4838 | -122.6486
195.6719 | 122.644 | -61.1938 | 61.2946 | -0.003128 | 0.040116 | 0.032462 | -0.0072503 | -0.0070133 | 0.064553 | 0.062739 | 61.3724 | 61.1526 | -61.1755 | 61.1938 | -61.1938 | -61.3815 | 0.13733 | 0.091553 | 61.3174 | -61.3495 | 0.018311 | -0.14191 | 122.5662 | 122.3877 | -122.4884 | -0.15564 | 0.022888 | 122.5479 | 61.3312 | 61.2854 | 0 | 122.3465 | 122.5662 | 122.5113 | -0.18768 | -0.15564 | 122.3465 | 122.5662 | -0.18768 | 0 | 122.5113 | -122.4701 | -122.644
196.6719 | 122.6578 | -61.2122 | 61.2946 | 0.0045015 | 0.037553 | 0.030112 | -0.0055413 | -0.0080813 | 0.061989 | 0.064875 | 61.4136 | 61.1618 | -61.1801 | 61.1938 | -61.1664 | -61.3724 | 0.09613 | 0.091553 | 61.3266 | -61.3403 | 0.032043 | -0.13275 | 122.6257 | 122.406 | -122.4609 | -0.12817 | 0.032043 | 122.5937 | 61.3083 | 61.3037 | 0.045776 | 122.374 | 122.6257 | 122.5388 | -0.16022 | -0.12817 | 122.374 | 122.6257 | -0.16022 | 0.045776 | 122.5388 | -122.4747 | -122.6349
197.6719 | 122.7814 | -61.1801 | 61.2579 | -0.010758 | 0.038621 | 0.035026 | -0.0066095 | -0.0082949 | 0.063057 | 0.059321 | 61.5005 | 61.116 | -61.1389 | 61.2991 | -61.0703 | -61.2579 | -0.064087 | 0.21057 | 61.2717 | -61.2854 | 0.041199 | -0.14191 | 122.6807 | 122.4792 | -122.3282 | -0.10529 | 0.013732 | 122.6395 | 61.116 | 61.3907 | 0.10986 | 122.2961 | 122.6807 | 122.4518 | -0.07782 | -0.10529 | 122.2961 | 122.6807 | -0.07782 | 0.10986 | 122.4518 | -122.3969 | -122.5433
198.6719 | 122.7722 | -61.1847 | 61.2442 | -0.003128 | 0.04033 | 0.034171 | -0.0093867 | -0.0074405 | 0.063057 | 0.061671 | 61.5097 | 61.0794 | -61.1526 | 61.3174 | -61.0474 | -61.235 | -0.068665 | 0.25177 | 61.2808 | -61.2854 | 0.032043 | -0.16479 | 122.6944 | 122.5021 | -122.2916 | -0.10071 | 0.036621 | 122.6624 | 61.116 | 61.4365 | 0.13733 | 122.2641 | 122.6944 | 122.4655 | -0.050354 | -0.10071 | 122.2641 | 122.6944 | -0.050354 | 0.13733 | 122.4655 | -122.3969 | -122.5296
199.6719 | 122.6807 | -61.2213 | 61.2854 | -0.010758 | 0.040544 | 0.037589 | -0.0034051 | -0.0087223 | 0.063698 | 0.061671 | 61.4548 | 61.1069 | -61.1389 | 61.2442 | -61.1343 | -61.3449 | 0.073242 | 0.15564 | 61.2946 | -61.3312 | 0.082397 | -0.17853 | 122.6761 | 122.4655 | -122.4197 | -0.10986 | 0.009156 | 122.5937 | 61.2946 | 61.377 | 0.086975 | 122.3282 | 122.6761 | 122.5159 | -0.1236 | -0.10986 | 122.3282 | 122.6761 | -0.1236 | 0.086975 | 122.5159 | -122.4243 | -122.6166
200.6719 | 122.7127 | -61.2076 | 61.29 | -0.003128 | 0.037766 | 0.033103 | -0.0066095 | -0.0078677 | 0.063698 | 0.061671 | 61.4914 | 61.1069 | -61.1664 | 61.2946 | -61.0886 | -61.2991 | 0.018311 | 0.19226 | 61.2808 | -61.29 | 0.041199 | -0.1831 | 122.699 | 122.5021 | -122.3785 | -0.082397 | -0.009155 | 122.6578 | 61.2259 | 61.3998 | 0.11902 | 122.3145 | 122.699 | 122.4884 | -0.091552 | -0.082397 | 122.3145 | 122.699 | -0.091552 | 0.11902 | 122.4884 | -122.4564 | -122.58
201.6719 | 122.7539 | -61.1984 | 61.2762 | -0.003128 | 0.039262 | 0.032035 | -0.0061823 | -0.0091495 | 0.063698 | 0.062952 | 61.5097 | 61.084 | -61.1618 | 61.3037 | -61.0703 | -61.2717 | -0.036621 | 0.20142 | 61.2762 | -61.2946 | 0.036621 | -0.19226 | 122.7081 | 122.5021 | -122.3465 | -0.096131 | 0 | 122.6715 | 61.1618 | 61.3998 | 0.12817 | 122.2824 | 122.7081 | 122.4747 | -0.073242 | -0.096131 | 122.2824 | 122.7081 | -0.073242 | 0.12817 | 122.4747 | -122.438 | -122.5708
202.6719 | 122.7676 | -61.2076 | 61.2488 | -0.003128 | 0.037339 | 0.032035 | -0.0044733 | -0.0078677 | 0.062203 | 0.061671 | 61.5051 | 61.084 | -61.1526 | 61.3312 | -61.0565 | -61.2488 | -0.068665 | 0.22888 | 61.2717 | -61.29 | 0.054932 | -0.16479 | 122.7127 | 122.5388 | -122.3053 | -0.082397 | 0.022888 | 122.6578 | 61.1389 | 61.4365 | 0.15106 | 122.2916 | 122.7127 | 122.4792 | -0.041198 | -0.082397 | 122.2916 | 122.7127 | -0.041198 | 0.15106 | 122.4792 | -122.4014 | -122.5388
203.6719 | 122.7722 | -61.1618 | 61.2625 | -0.003128 | 0.036698 | 0.036521 | -0.0025507 | -0.0097903 | 0.064766 | 0.061884 | 61.5143 | 61.0703 | -61.1435 | 61.3312 | -61.0657 | -61.2488 | -0.068665 | 0.22888 | 61.2762 | -61.29 | 0.01831 | -0.19226 | 122.6761 | 122.493 | -122.3282 | -0.12817 | 0.013733 | 122.6578 | 61.0931 | 61.3907 | 0.09613 | 122.2321 | 122.6761 | 122.438 | -0.086975 | -0.12817 | 122.2321 | 122.6761 | -0.086975 | 0.09613 | 122.438 | -122.406 | -122.5525
204.6719 | 122.7631 | -61.1984 | 61.2488 | -0.003128 | 0.036485 | 0.031608 | -0.0053277 | -0.0087223 | 0.063485 | 0.063807 | 61.4777 | 61.0657 | -61.1435 | 61.3083 | -61.084 | -61.2625 | -0.091553 | 0.19684 | 61.2671 | -61.2717 | 0.054931 | -0.1831 | 122.6761 | 122.5067 | -122.3328 | -0.073242 | 0.018311 | 122.6212 | 61.1069 | 61.3953 | 0.11444 | 122.2641 | 122.6761 | 122.4655 | -0.064087 | -0.073242 | 122.2641 | 122.6761 | -0.064087 | 0.11444 | 122.4655 | -122.3923 | -122.5204
205.6719 | 122.7631 | -61.203 | 61.2854 | -0.010758 | 0.037126 | 0.031821 | -0.0036187 | -0.010218 | 0.063698 | 0.060603 | 61.4685 | 61.0931 | -61.1343 | 61.2625 | -61.084 | -61.2671 | -0.073242 | 0.16937 | 61.2625 | -61.2946 | 0.068665 | -0.19226 | 122.6715 | 122.4655 | -122.3694 | -0.091553 | -0.022888 | 122.6028 | 61.1298 | 61.3724 | 0.11902 | 122.2961 | 122.6715 | 122.4655 | -0.064087 | -0.091553 | 122.2961 | 122.6715 | -0.064087 | 0.11902 | 122.4655 | -122.4197 | -122.58
206.6719 | 122.7676 | -61.1984 | 61.2717 | -0.003128 | 0.036057 | 0.032676 | -0.0031915 | -0.0078677 | 0.063057 | 0.061671 | 61.5189 | 61.084 | -61.1481 | 61.3403 | -61.0474 | -61.2534 | -0.082397 | 0.23804 | 61.2762 | -61.2717 | 0.050354 | -0.18768 | 122.7173 | 122.5388 | -122.319 | -0.073242 | 0.004578 | 122.6669 | 61.116 | 61.4365 | 0.15106 | 122.2824 | 122.7173 | 122.4747 | -0.054932 | -0.073242 | 122.2824 | 122.7173 | -0.054932 | 0.15106 | 122.4747 | -122.4197 | -122.5433
207.6719 | 122.7997 | -61.1618 | 61.2671 | -0.003128 | 0.036912 | 0.033957 | -0.0040461 | -0.0091495 | 0.060067 | 0.060816 | 61.5234 | 61.0703 | -61.1435 | 61.3678 | -61.0519 | -61.235 | -0.082397 | 0.23346 | 61.2579 | -61.2854 | 0.01831 | -0.19684 | 122.6852 | 122.5296 | -122.319 | -0.1236 | -0.009155 | 122.6669 | 61.0794 | 61.3953 | 0.10986 | 122.2321 | 122.6852 | 122.4197 | -0.073242 | -0.1236 | 122.2321 | 122.6852 | -0.073242 | 0.10986 | 122.4197 | -122.4106 | -122.5525
208.6719 | 122.8088 | -61.1984 | 61.2534 | -0.003128 | 0.036271 | 0.030753 | -0.0046869 | -0.0082949 | 0.063698 | 0.062098 | 61.5051 | 61.0794 | -61.1526 | 61.3312 | -61.0428 | -61.2442 | -0.11902 | 0.20599 | 61.2396 | -61.2671 | 0.045776 | -0.17395 | 122.7036 | 122.5296 | -122.2961 | -0.068665 | -0.013733 | 122.6578 | 61.0794 | 61.4044 | 0.15564 | 122.2778 | 122.7036 | 122.438 | -0.045777 | -0.068665 | 122.2778 | 122.7036 | -0.045777 | 0.15564 | 122.438 | -122.406 | -122.5204
209.6719 | 122.7951 | -61.1984 | 61.2396 | -0.003128 | 0.037126 | 0.035666 | -0.0049005 | -0.0078677 | 0.064125 | 0.063593 | 61.5051 | 61.0931 | -61.1481 | 61.3312 | -61.0703 | -61.2625 | -0.11902 | 0.20599 | 61.2167 | -61.3083 | 0.050354 | -0.14648 | 122.7036 | 122.5296 | -122.3099 | -0.10986 | -0.022888 | 122.6532 | 61.0794 | 61.4044 | 0.12817 | 122.2916 | 122.7036 | 122.4152 | -0.064087 | -0.10986 | 122.2916 | 122.7036 | -0.064087 | 0.12817 | 122.4152 | -122.3877 | -122.5479
210.6719 | 122.7859 | -61.1984 | 61.2488 | 0.01213 | 0.03563 | 0.036094 | -0.0038325 | -0.0091495 | 0.064125 | 0.064234 | 61.4822 | 61.084 | -61.1435 | 61.3129 | -61.084 | -61.2625 | -0.086975 | 0.1831 | 61.2305 | -61.2717 | 0.054931 | -0.16479 | 122.6807 | 122.5113 | -122.3328 | -0.073242 | -0.01831 | 122.6257 | 61.1114 | 61.3815 | 0.11444 | 122.2824 | 122.6807 | 122.4289 | -0.064087 | -0.073242 | 122.2824 | 122.6807 | -0.064087 | 0.11444 | 122.4289 | -122.3923 | -122.5204
211.6719 | 122.6761 | -61.2259 | 61.2854 | 0.0045015 | 0.043321 | 0.038871 | 0.0051397 | -0.0070133 | 0.063912 | 0.060389 | 61.4548 | 61.1526 | -61.1801 | 61.2396 | -61.1938 | -61.3907 | -0.022888 | 0.054932 | 61.2579 | -61.3632 | 0.045776 | -0.13275 | 122.6807 | 122.4655 | -122.4792 | -0.13733 | -0.027465 | 122.6349 | 61.203 | 61.2808 | 0.032043 | 122.3785 | 122.6807 | 122.4838 | -0.1648 | -0.13733 | 122.3785 | 122.6807 | -0.1648 | 0.032043 | 122.4838 | -122.4655 | -122.6486
212.6719 | 122.7219 | -61.2076 | 61.2396 | -0.018387 | 0.034562 | 0.031821 | -0.0051141 | -0.0093631 | 0.063485 | 0.063166 | 61.4136 | 61.0657 | -61.1847 | 61.235 | -61.1481 | -61.322 | -0.10071 | 0.073242 | 61.2122 | -61.3037 | 0.022889 | -0.17395 | 122.6212 | 122.4426 | -122.3877 | -0.09613 | -0.027466 | 122.5983 | 61.1069 | 61.2808 | 0.05951 | 122.2733 | 122.6212 | 122.4197 | -0.11444 | -0.09613 | 122.2733 | 122.6212 | -0.11444 | 0.05951 | 122.4197 | -122.4243 | -122.5433
213.6719 | 122.7585 | -61.1847 | 61.2579 | -0.003128 | 0.035844 | 0.032676 | -0.0053277 | -0.0089359 | 0.064125 | 0.062952 | 61.4594 | 61.0748 | -61.1435 | 61.3083 | -61.0703 | -61.2488 | -0.07782 | 0.17395 | 61.235 | -61.3037 | 0.041198 | -0.18311 | 122.644 | 122.493 | -122.3282 | -0.11902 | -0.022889 | 122.6028 | 61.1069 | 61.3586 | 0.11444 | 122.2595 | 122.644 | 122.4197 | -0.064087 | -0.11902 | 122.2595 | 122.644 | -0.064087 | 0.11444 | 122.4197 | -122.4014 | -122.5616
214.6719 | 122.7402 | -61.235 | 61.2579 | 0.0045015 | 0.036485 | 0.031394 | -0.0044733 | -0.0095767 | 0.063698 | 0.062739 | 61.4365 | 61.0886 | -61.1893 | 61.2671 | -61.1252 | -61.29 | -0.082397 | 0.1236 | 61.2534 | -61.2854 | 0.045776 | -0.16937 | 122.6715 | 122.5021 | -122.3831 | -0.050354 | -0.004578 | 122.6257 | 61.1526 | 61.3586 | 0.10986 | 122.3236 | 122.6715 | 122.4884 | -0.054932 | -0.050354 | 122.3236 | 122.6715 | -0.054932 | 0.10986 | 122.4884 | -122.4472 | -122.5433
215.6719 | 122.7402 | -61.2305 | 61.2488 | 0.0045015 | 0.035844 | 0.034598 | -0.0046869 | -0.010859 | 0.064766 | 0.062739 | 61.4044 | 61.0657 | -61.1893 | 61.2305 | -61.1481 | -61.3358 | -0.09613 | 0.10529 | 61.2167 | -61.3037 | 0.041199 | -0.1831 | 122.6349 | 122.4609 | -122.3969 | -0.073242 | -0.032043 | 122.5937 | 61.1343 | 61.3358 | 0.082398 | 122.2961 | 122.6349 | 122.4472 | -0.10529 | -0.073242 | 122.2961 | 122.6349 | -0.10529 | 0.082398 | 122.4472 | -122.438 | -122.5525
216.6719 | 122.7356 | -61.2122 | 61.2762 | -0.010758 | 0.039475 | 0.039512 | -0.0023371 | -0.010004 | 0.064339 | 0.063166 | 61.496 | 61.0931 | -61.1389 | 61.3083 | -61.0748 | -61.2762 | 0.009155 | 0.21057 | 61.2534 | -61.2717 | 0.073242 | -0.18311 | 122.7081 | 122.5204 | -122.3511 | -0.059509 | -0.022888 | 122.6349 | 61.2213 | 61.4227 | 0.13733 | 122.3053 | 122.7081 | 122.4655 | -0.064087 | -0.059509 | 122.3053 | 122.7081 | -0.064087 | 0.13733 | 122.4655 | -122.4152 | -122.5479
217.6719 | 122.7264 | -61.2167 | 61.2762 | 0.0045015 | 0.03798 | 0.030753 | -0.0055413 | -0.0085085 | 0.06263 | 0.06338 | 61.4227 | 61.0565 | -61.1847 | 61.2396 | -61.1572 | -61.3312 | -0.10071 | 0.073242 | 61.2076 | -61.3129 | 0.032044 | -0.21973 | 122.6395 | 122.4564 | -122.4335 | -0.09613 | -0.068664 | 122.6074 | 61.116 | 61.29 | 0.059509 | 122.2733 | 122.6395 | 122.4243 | -0.11444 | -0.09613 | 122.2733 | 122.6395 | -0.11444 | 0.059509 | 122.4243 | -122.4609 | -122.5891
218.6719 | 122.7585 | -61.1984 | 61.2122 | -0.003128 | 0.040971 | 0.035453 | -0.0019099 | -0.0082949 | 0.063698 | 0.061457 | 61.4502 | 61.0428 | -61.1847 | 61.2808 | -61.116 | -61.29 | -0.19684 | 0.09613 | 61.1664 | -61.3037 | 0.013733 | -0.16937 | 122.6486 | 122.4792 | -122.3282 | -0.10529 | -0.045776 | 122.6349 | 61.0016 | 61.2946 | 0.082397 | 122.2412 | 122.6486 | 122.3648 | -0.091553 | -0.10529 | 122.2412 | 122.6486 | -0.091553 | 0.082397 | 122.3648 | -122.3969 | -122.5159
219.6719 | 122.7722 | -61.1984 | 61.1938 | -0.010758 | 0.037766 | 0.033317 | 1.2902e-05 | -0.0085085 | 0.062844 | 0.061457 | 61.4639 | 61.0382 | -61.1893 | 61.2717 | -61.116 | -61.2808 | -0.21515 | 0.09613 | 61.1755 | -61.3266 | 0.009155 | -0.15564 | 122.6624 | 122.4701 | -122.3099 | -0.12817 | -0.018311 | 122.6532 | 60.9833 | 61.2946 | 0.082397 | 122.2366 | 122.6624 | 122.374 | -0.082398 | -0.12817 | 122.2366 | 122.6624 | -0.082398 | 0.082397 | 122.374 | -122.3831 | -122.5204
220.6719 | 122.7219 | -61.2076 | 61.2305 | -0.003128 | 0.036912 | 0.029258 | -0.0051141 | -0.0097903 | 0.063912 | 0.065943 | 61.4319 | 61.0565 | -61.1893 | 61.235 | -61.1435 | -61.3174 | -0.13275 | 0.068665 | 61.1847 | -61.3266 | 0.018311 | -0.17395 | 122.6395 | 122.4426 | -122.374 | -0.11902 | -0.045777 | 122.6212 | 61.0748 | 61.2762 | 0.064087 | 122.2641 | 122.6395 | 122.3923 | -0.10986 | -0.11902 | 122.2641 | 122.6395 | -0.10986 | 0.064087 | 122.3923 | -122.4197 | -122.5571
221.6719 | 122.6898 | -61.2488 | 61.2579 | 0.0045015 | 0.044175 | 0.033744 | 0.0017217 | -0.0072269 | 0.063057 | 0.062525 | 61.4273 | 61.1938 | -61.1893 | 61.2534 | -61.1664 | -61.3586 | 0.07782 | 0.082397 | 61.2488 | -61.3495 | 0.059509 | -0.064087 | 122.6761 | 122.5021 | -122.4243 | -0.10071 | -0.009156 | 122.6166 | 61.3266 | 61.3312 | 0.082397 | 122.4426 | 122.6761 | 122.4976 | -0.10986 | -0.10071 | 122.4426 | 122.6761 | -0.10986 | 0.082397 | 122.4976 | -122.4472 | -122.6074
222.6719 | 122.7493 | -61.1847 | 61.1938 | -0.003128 | 0.035417 | 0.035239 | -0.0044733 | -0.0050907 | 0.063485 | 0.062525 | 61.4548 | 61.0703 | -61.1847 | 61.2717 | -61.1298 | -61.3037 | -0.17853 | 0.091553 | 61.1938 | -61.3083 | 0 | -0.1236 | 122.6395 | 122.4564 | -122.3236 | -0.1236 | 0 | 122.6395 | 61.0062 | 61.2762 | 0.054931 | 122.2549 | 122.6395 | 122.3785 | -0.11902 | -0.1236 | 122.2549 | 122.6395 | -0.11902 | 0.054931 | 122.3785 | -122.3785 | -122.5021
223.6719 | 122.7402 | -61.1801 | 61.203 | -0.010758 | 0.038621 | 0.035453 | -0.0016961 | -0.0089359 | 0.064766 | 0.062525 | 61.4548 | 61.0657 | -61.1847 | 61.2717 | -61.1023 | -61.29 | -0.19226 | 0.091553 | 61.171 | -61.3312 | -0.004577 | -0.13733 | 122.6349 | 122.4518 | -122.3053 | -0.15106 | -0.032044 | 122.6395 | 60.9879 | 61.2717 | 0.07782 | 122.2458 | 122.6349 | 122.3511 | -0.10986 | -0.15106 | 122.2458 | 122.6349 | -0.10986 | 0.07782 | 122.3511 | -122.3877 | -122.5342
224.6719 | 122.7631 | -61.2076 | 61.2076 | -0.003128 | 0.039475 | 0.03588 | -0.0008417 | -0.0093631 | 0.063271 | 0.063593 | 61.4548 | 61.0428 | -61.203 | 61.2717 | -61.1114 | -61.2717 | -0.20142 | 0.10529 | 61.1572 | -61.3403 | 0.004578 | -0.16479 | 122.6624 | 122.4792 | -122.319 | -0.13275 | -0.050354 | 122.6578 | 61.0062 | 61.3129 | 0.096131 | 122.2504 | 122.6624 | 122.3648 | -0.064086 | -0.13275 | 122.2504 | 122.6624 | -0.064086 | 0.096131 | 122.3648 | -122.4106 | -122.5479
225.6719 | 122.7814 | -61.171 | 61.2305 | -0.010758 | 0.039689 | 0.035239 | 0.0004401 | -0.0087223 | 0.064339 | 0.064234 | 61.4182 | 61.0886 | -61.203 | 61.2579 | -61.116 | -61.3083 | -0.18768 | 0.082397 | 61.1481 | -61.3266 | -0.032044 | -0.14191 | 122.5891 | 122.4289 | -122.3465 | -0.15564 | -0.082398 | 122.6212 | 60.9833 | 61.2534 | 0.054931 | 122.2595 | 122.5891 | 122.319 | -0.13733 | -0.15564 | 122.2595 | 122.5891 | -0.13733 | 0.054931 | 122.319 | -122.4335 | -122.5571
226.6719 | 122.7997 | -61.1664 | 61.2762 | -0.003128 | 0.037766 | 0.030967 | -0.0036187 | -0.0082949 | 0.063698 | 0.063807 | 61.5005 | 61.0886 | -61.1343 | 61.3449 | -61.0519 | -61.2213 | -0.09613 | 0.21057 | 61.2122 | -61.2762 | 0.032044 | -0.18768 | 122.6669 | 122.5113 | -122.3282 | -0.10986 | -0.064087 | 122.6349 | 61.0703 | 61.377 | 0.11444 | 122.2549 | 122.6669 | 122.3785 | -0.054931 | -0.10986 | 122.2549 | 122.6669 | -0.054931 | 0.11444 | 122.3785 | -122.4106 | -122.5525
227.6719 | 122.7676 | -61.1938 | 61.2167 | 0.0045015 | 0.038621 | 0.032248 | -0.0023371 | -0.0087223 | 0.062203 | 0.062952 | 61.4777 | 61.084 | -61.1847 | 61.2762 | -61.1114 | -61.2854 | -0.17853 | 0.10071 | 61.1526 | -61.3358 | 0.009156 | -0.13275 | 122.6715 | 122.4701 | -122.3282 | -0.14191 | -0.064087 | 122.6624 | 61.0153 | 61.2946 | 0.082398 | 122.2778 | 122.6715 | 122.3465 | -0.091552 | -0.14191 | 122.2778 | 122.6715 | -0.091552 | 0.082398 | 122.3465 | -122.4014 | -122.5525
228.6719 | 122.7676 | -61.1847 | 61.2167 | 0.01213 | 0.04033 | 0.036948 | -0.0031915 | -0.0067995 | 0.063485 | 0.065089 | 61.4548 | 61.0703 | -61.1664 | 61.2717 | -61.116 | -61.2854 | -0.19684 | 0.10986 | 61.1526 | -61.3358 | 0.01831 | -0.14648 | 122.6395 | 122.4564 | -122.3328 | -0.15106 | -0.064087 | 122.6212 | 60.9879 | 61.2946 | 0.068664 | 122.2549 | 122.6395 | 122.3373 | -0.10071 | -0.15106 | 122.2549 | 122.6395 | -0.10071 | 0.068664 | 122.3373 | -122.3831 | -122.5525
229.6719 | 122.7859 | -61.203 | 61.1801 | -0.003128 | 0.04033 | 0.032248 | 0.0006537 | -0.0078677 | 0.064125 | 0.063807 | 61.4777 | 61.0794 | -61.1984 | 61.2717 | -61.1069 | -61.2854 | -0.21973 | 0.09613 | 61.1664 | -61.3449 | 0.004578 | -0.10071 | 122.6807 | 122.4747 | -122.287 | -0.14191 | -0.013733 | 122.6761 | 60.9833 | 61.2991 | 0.09613 | 122.2824 | 122.6807 | 122.3694 | -0.082397 | -0.14191 | 122.2824 | 122.6807 | -0.082397 | 0.09613 | 122.3694 | -122.3785 | -122.525
230.6719 | 122.7722 | -61.1938 | 61.2076 | -0.003128 | 0.038407 | 0.037162 | -0.0016961 | -0.0080813 | 0.064553 | 0.062952 | 61.4594 | 61.0748 | -61.1755 | 61.2534 | -61.1206 | -61.2946 | -0.21057 | 0.09613 | 61.171 | -61.3495 | 0.018311 | -0.13275 | 122.6532 | 122.4472 | -122.3282 | -0.15564 | -0.036622 | 122.6349 | 60.9833 | 61.29 | 0.073243 | 122.2687 | 122.6532 | 122.3648 | -0.10071 | -0.15564 | 122.2687 | 122.6532 | -0.10071 | 0.073243 | 122.3648 | -122.3831 | -122.5571
231.6719 | 122.7585 | -61.1984 | 61.1984 | -0.003128 | 0.038621 | 0.036521 | -0.0010553 | -0.0089359 | 0.063912 | 0.062952 | 61.4319 | 61.0931 | -61.1755 | 61.2579 | -61.1298 | -61.2946 | -0.18768 | 0.086975 | 61.171 | -61.3541 | 0.022888 | -0.10529 | 122.6303 | 122.4564 | -122.3282 | -0.15564 | -0.027466 | 122.6074 | 61.0107 | 61.2854 | 0.068664 | 122.2916 | 122.6303 | 122.3694 | -0.096131 | -0.15564 | 122.2916 | 122.6303 | -0.096131 | 0.068664 | 122.3694 | -122.374 | -122.5525
232.6719 | 122.6578 | -61.2534 | 61.2625 | -0.003128 | 0.043107 | 0.036307 | -0.0008417 | -0.0048769 | 0.065834 | 0.063593 | 61.3632 | 61.1435 | -61.2259 | 61.1526 | -61.235 | -61.4182 | -0.036621 | -0.036621 | 61.2213 | -61.3861 | 0.027466 | -0.11902 | 122.6166 | 122.406 | -122.4976 | -0.13275 | -0.041199 | 122.5891 | 61.2167 | 61.2167 | 0.018311 | 122.3969 | 122.6166 | 122.4747 | -0.16479 | -0.13275 | 122.3969 | 122.6166 | -0.16479 | 0.018311 | 122.4747 | -122.4884 | -122.6486
233.6719 | 122.6395 | -61.203 | 61.235 | 0.0045015 | 0.041612 | 0.036735 | 0.0012945 | -0.0085085 | 0.062844 | 0.063807 | 61.3403 | 61.1435 | -61.2076 | 61.1389 | -61.2396 | -61.4182 | -0.022888 | -0.054932 | 61.2259 | -61.3907 | -0.004578 | -0.091552 | 122.5433 | 122.3419 | -122.4747 | -0.18768 | -0.009155 | 122.5479 | 61.1801 | 61.1481 | -0.036621 | 122.3465 | 122.5433 | 122.4289 | -0.21515 | -0.18768 | 122.3465 | 122.5433 | -0.21515 | -0.036621 | 122.4289 | -122.4426 | -122.6257
234.6719 | 122.7722 | -61.1893 | 61.1664 | -0.010758 | 0.039048 | 0.036307 | -0.0025507 | -0.0074405 | 0.064339 | 0.06338 | 61.4182 | 61.1069 | -61.2076 | 61.2488 | -61.1343 | -61.3083 | -0.17853 | 0.082397 | 61.1755 | -61.3449 | -0.018311 | -0.059509 | 122.6074 | 122.438 | -122.3007 | -0.15564 | 0.009155 | 122.6257 | 61.0107 | 61.2717 | 0.054932 | 122.2961 | 122.6074 | 122.3648 | -0.11902 | -0.15564 | 122.2961 | 122.6074 | -0.11902 | 0.054932 | 122.3648 | -122.374 | -122.5113
235.6719 | 122.7448 | -61.1755 | 61.2076 | 0.0045015 | 0.043321 | 0.039084 | -0.0027643 | -0.0067995 | 0.064553 | 0.06573 | 61.3861 | 61.1298 | -61.1893 | 61.2122 | -61.1618 | -61.3358 | -0.15564 | 0.041199 | 61.2167 | -61.3815 | -0.013733 | -0.07782 | 122.5616 | 122.3877 | -122.3694 | -0.20599 | 0.009155 | 122.5754 | 61.0199 | 61.2167 | 0.013733 | 122.3053 | 122.5616 | 122.3923 | -0.16022 | -0.20599 | 122.3053 | 122.5616 | -0.16022 | 0.013733 | 122.3923 | -122.3969 | -122.5891
236.6719 | 122.6898 | -61.2167 | 61.2488 | -0.010758 | 0.042466 | 0.035666 | -0.0025507 | -0.0067995 | 0.066903 | 0.063166 | 61.3586 | 61.1481 | -61.2122 | 61.1618 | -61.203 | -61.377 | -0.11902 | 0 | 61.2122 | -61.3953 | 0.004578 | -0.10071 | 122.5754 | 122.3785 | -122.4518 | -0.17853 | -0.036621 | 122.5708 | 61.0977 | 61.2167 | 0.013733 | 122.3648 | 122.5754 | 122.4289 | -0.16022 | -0.17853 | 122.3648 | 122.5754 | -0.16022 | 0.013733 | 122.4289 | -122.4609 | -122.644
237.6719 | 122.6578 | -61.1938 | 61.2442 | -0.003128 | 0.042466 | 0.03823 | -0.0023371 | -0.0025271 | 0.063698 | 0.065302 | 61.3541 | 61.1389 | -61.2076 | 61.1526 | -61.235 | -61.3998 | -0.045776 | -0.027466 | 61.2122 | -61.3998 | -0.013733 | -0.10529 | 122.5479 | 122.3465 | -122.4792 | -0.20599 | -0.032044 | 122.5616 | 61.1481 | 61.1664 | -0.041198 | 122.3328 | 122.5479 | 122.406 | -0.20599 | -0.20599 | 122.3328 | 122.5479 | -0.20599 | -0.041198 | 122.406 | -122.4518 | -122.644
238.6719 | 122.6578 | -61.2213 | 61.2625 | -0.018387 | 0.044175 | 0.036735 | -0.0004145 | -0.0082949 | 0.067543 | 0.062525 | 61.3495 | 61.1664 | -61.2259 | 61.1389 | -61.235 | -61.4227 | -0.004578 | -0.036621 | 61.2076 | -61.4044 | -0.004578 | -0.09613 | 122.5708 | 122.3602 | -122.4976 | -0.18311 | -0.054931 | 122.5754 | 61.2167 | 61.1847 | -0.013733 | 122.3877 | 122.5708 | 122.4289 | -0.20142 | -0.18311 | 122.3877 | 122.5708 | -0.20142 | -0.013733 | 122.4289 | -122.4884 | -122.6669
239.6719 | 122.6166 | -61.203 | 61.2762 | -0.018387 | 0.045671 | 0.035453 | -0.0025507 | -0.0065859 | 0.063912 | 0.063166 | 61.3312 | 61.1664 | -61.2488 | 61.1298 | -61.2396 | -61.4365 | 0.027466 | -0.045776 | 61.2167 | -61.4273 | -0.045776 | -0.10986 | 122.5342 | 122.3328 | -122.5159 | -0.2243 | -0.059509 | 122.58 | 61.2305 | 61.1572 | -0.036621 | 122.3694 | 122.5342 | 122.4197 | -0.23346 | -0.2243 | 122.3694 | 122.5342 | -0.23346 | -0.036621 | 122.4197 | -122.525 | -122.7036
240.6719 | 122.6303 | -61.203 | 61.2671 | -0.003128 | 0.044816 | 0.038016 | -0.0002009 | -0.0057315 | 0.064766 | 0.061671 | 61.3358 | 61.1526 | -61.2579 | 61.1252 | -61.2534 | -61.441 | -0.009155 | -0.054932 | 61.2305 | -61.4136 | -0.054932 | -0.11444 | 122.5388 | 122.3282 | -122.5204 | -0.21057 | -0.036621 | 122.5937 | 61.1938 | 61.1481 | -0.050354 | 122.3557 | 122.5388 | 122.4335 | -0.23804 | -0.21057 | 122.3557 | 122.5388 | -0.23804 | -0.050354 | 122.4335 | -122.525 | -122.6807
241.6719 | 122.644 | -61.2213 | 61.2579 | -0.003128 | 0.044389 | 0.036307 | -0.0012689 | -0.0050907 | 0.066262 | 0.063593 | 61.3449 | 61.1801 | -61.2259 | 61.1252 | -61.2305 | -61.4273 | 0.004578 | -0.027466 | 61.1984 | -61.4227 | -0.004578 | -0.07782 | 122.5662 | 122.3465 | -122.4884 | -0.20142 | -0.05951 | 122.5708 | 61.2259 | 61.1938 | -0.009156 | 122.4014 | 122.5662 | 122.4197 | -0.20599 | -0.20142 | 122.4014 | 122.5662 | -0.20599 | -0.009156 | 122.4197 | -122.4838 | -122.6807
242.6719 | 122.6303 | -61.2167 | 61.2396 | 0.0045015 | 0.044389 | 0.037589 | -0.0006281 | -0.0044497 | 0.065407 | 0.064875 | 61.3358 | 61.1801 | -61.2305 | 61.1114 | -61.2579 | -61.4365 | -0.004578 | -0.068665 | 61.235 | -61.3998 | -0.013733 | -0.059509 | 122.5525 | 122.3282 | -122.4976 | -0.18311 | -0.004578 | 122.5662 | 61.2122 | 61.1481 | -0.041199 | 122.3969 | 122.5525 | 122.4518 | -0.21973 | -0.18311 | 122.3969 | 122.5525 | -0.21973 | -0.041199 | 122.4518 | -122.4701 | -122.6395
243.6719 | 122.644 | -61.2122 | 61.2442 | -0.010758 | 0.042253 | 0.036521 | -0.0004145 | -0.0035953 | 0.06733 | 0.061884 | 61.3403 | 61.1618 | -61.2442 | 61.1069 | -61.2488 | -61.4227 | 0.013733 | -0.041199 | 61.2442 | -61.4136 | -0.032044 | -0.082398 | 122.5525 | 122.319 | -122.493 | -0.20142 | 0 | 122.5845 | 61.2259 | 61.171 | -0.036621 | 122.374 | 122.5525 | 122.4564 | -0.21057 | -0.20142 | 122.374 | 122.5525 | -0.21057 | -0.036621 | 122.4564 | -122.4884 | -122.6578
244.6719 | 122.6212 | -61.2076 | 61.2488 | -0.003128 | 0.041398 | 0.036948 | -0.0006281 | -0.0027407 | 0.065194 | 0.064661 | 61.3541 | 61.1801 | -61.2213 | 61.1206 | -61.2442 | -61.4273 | 0.032043 | -0.041199 | 61.2259 | -61.4182 | -0.013732 | -0.068664 | 122.5616 | 122.3282 | -122.493 | -0.21057 | -0.022888 | 122.5754 | 61.2396 | 61.1664 | -0.036621 | 122.3877 | 122.5616 | 122.4335 | -0.21973 | -0.21057 | 122.3877 | 122.5616 | -0.21973 | -0.036621 | 122.4335 | -122.4701 | -122.6669
245.6719 | 122.6303 | -61.2213 | 61.2534 | -0.010758 | 0.046311 | 0.035453 | -0.0023371 | -0.0053043 | 0.067116 | 0.063807 | 61.3632 | 61.1664 | -61.235 | 61.1298 | -61.2167 | -61.4273 | 0.009155 | -0.032043 | 61.2488 | -61.4044 | -0.013733 | -0.086975 | 122.5845 | 122.3511 | -122.4701 | -0.18311 | -0.004578 | 122.5983 | 61.2305 | 61.1893 | 0.004577 | 122.3877 | 122.5845 | 122.4701 | -0.20599 | -0.18311 | 122.3877 | 122.5845 | -0.20599 | 0.004577 | 122.4701 | -122.4884 | -122.6578
246.6719 | 122.6898 | -61.1847 | 61.2305 | 0.0045015 | 0.043534 | 0.039084 | -0.0016961 | -0.0044497 | 0.06733 | 0.064234 | 61.4273 | 61.1938 | -61.1984 | 61.2305 | -61.1664 | -61.3495 | 0.013733 | 0.086975 | 61.235 | -61.3861 | -0.013733 | -0.036621 | 122.612 | 122.4152 | -122.3969 | -0.20142 | 0.004577 | 122.6257 | 61.1984 | 61.2717 | 0.01831 | 122.3785 | 122.612 | 122.4197 | -0.1648 | -0.20142 | 122.3785 | 122.612 | -0.1648 | 0.01831 | 122.4197 | -122.4289 | -122.6166
247.6719 | 122.6578 | -61.1893 | 61.2717 | -0.010758 | 0.044602 | 0.034598 | -0.0016961 | -0.0050907 | 0.064553 | 0.06338 | 61.4044 | 61.1893 | -61.1847 | 61.1938 | -61.203 | -61.3815 | 0.018311 | 0.027466 | 61.2579 | -61.4182 | 0.004578 | -0.082397 | 122.5937 | 122.3831 | -122.4747 | -0.22888 | -0.013732 | 122.5891 | 61.2076 | 61.2167 | -0.013733 | 122.3785 | 122.5937 | 122.4472 | -0.19226 | -0.22888 | 122.3785 | 122.5937 | -0.19226 | -0.013733 | 122.4472 | -122.4564 | -122.6898
248.6719 | 122.6395 | -61.2076 | 61.2488 | -0.018387 | 0.046098 | 0.037589 | -0.0023371 | -0.0050907 | 0.066689 | 0.06573 | 61.3678 | 61.1847 | -61.2167 | 61.1298 | -61.2076 | -61.4227 | 0.027466 | -0.027466 | 61.2259 | -61.4044 | -0.009155 | -0.064087 | 122.5754 | 122.3373 | -122.4564 | -0.19684 | -0.022888 | 122.5845 | 61.235 | 61.1801 | 0 | 122.3923 | 122.5754 | 122.4335 | -0.21515 | -0.19684 | 122.3923 | 122.5754 | -0.21515 | 0 | 122.4335 | -122.4655 | -122.6532
249.6719 | 122.6669 | -61.1984 | 61.2213 | -0.003128 | 0.044816 | 0.038871 | -0.0023371 | -0.0044497 | 0.065621 | 0.062952 | 61.4227 | 61.1801 | -61.1938 | 61.1801 | -61.1893 | -61.3907 | 0.022888 | 0.022888 | 61.2534 | -61.3632 | 0.004577 | -0.041198 | 122.6212 | 122.3785 | -122.4106 | -0.16479 | 0.032044 | 122.6166 | 61.2213 | 61.2213 | 0.009155 | 122.3785 | 122.6212 | 122.4518 | -0.19226 | -0.16479 | 122.3785 | 122.6212 | -0.19226 | 0.009155 | 122.4518 | -122.4152 | -122.5845
250.6719 | 122.6807 | -61.203 | 61.2488 | -0.003128 | 0.043962 | 0.035026 | -0.0019099 | -0.0050907 | 0.065834 | 0.062525 | 61.4319 | 61.171 | -61.2076 | 61.203 | -61.1572 | -61.3586 | 0.018311 | 0.064087 | 61.2396 | -61.3815 | -0.004578 | -0.07782 | 122.6349 | 122.406 | -122.406 | -0.17853 | -0.009155 | 122.6395 | 61.2213 | 61.2671 | 0.045776 | 122.374 | 122.6349 | 122.4426 | -0.15564 | -0.17853 | 122.374 | 122.6349 | -0.15564 | 0.045776 | 122.4426 | -122.4564 | -122.6303
251.6719 | 122.6898 | -61.1938 | 61.2534 | -0.003128 | 0.044175 | 0.037375 | -0.0027643 | -0.0050907 | 0.063271 | 0.063593 | 61.4365 | 61.1938 | -61.1938 | 61.203 | -61.1435 | -61.3495 | 0.032043 | 0.073242 | 61.2717 | -61.3632 | 0 | -0.059509 | 122.6303 | 122.3969 | -122.3969 | -0.16937 | 0.01831 | 122.6303 | 61.2259 | 61.2671 | 0.050354 | 122.3877 | 122.6303 | 122.4655 | -0.15564 | -0.16937 | 122.3877 | 122.6303 | -0.15564 | 0.050354 | 122.4655 | -122.4472 | -122.6166
252.6719 | 122.6852 | -61.2122 | 61.2808 | -0.018387 | 0.043534 | 0.037162 | -0.0042597 | -0.0059451 | 0.06263 | 0.063593 | 61.409 | 61.2122 | -61.2259 | 61.1984 | -61.171 | -61.377 | 0.11902 | 0.050354 | 61.3129 | -61.3495 | -0.013733 | -0.068665 | 122.6212 | 122.4106 | -122.4518 | -0.13733 | 0.032043 | 122.6349 | 61.3312 | 61.2625 | 0.041199 | 122.4243 | 122.6212 | 122.525 | -0.16479 | -0.13733 | 122.4243 | 122.6212 | -0.16479 | 0.041199 | 122.525 | -122.5067 | -122.6303
253.6719 | 122.6486 | -61.2396 | 61.2808 | -0.010758 | 0.041825 | 0.03588 | -0.0034051 | -0.0046633 | 0.064339 | 0.063166 | 61.3815 | 61.203 | -61.1755 | 61.1893 | -61.1893 | -61.3998 | 0.14191 | 0.032043 | 61.2854 | -61.3861 | 0.064087 | -0.07782 | 122.6212 | 122.4289 | -122.4701 | -0.14648 | 0.004577 | 122.5571 | 61.3815 | 61.2717 | 0.050354 | 122.4426 | 122.6212 | 122.525 | -0.16022 | -0.14648 | 122.4426 | 122.6212 | -0.16022 | 0.050354 | 122.525 | -122.4564 | -122.6669
254.6719 | 122.699 | -61.1847 | 61.2579 | -0.003128 | 0.046952 | 0.037589 | -0.0027643 | -0.0042361 | 0.063698 | 0.064661 | 61.4319 | 61.1984 | -61.1984 | 61.2305 | -61.1664 | -61.3678 | 0.050354 | 0.068665 | 61.29 | -61.3678 | -0.013733 | -0.05951 | 122.6166 | 122.4152 | -122.4243 | -0.18311 | 0.032043 | 122.6303 | 61.235 | 61.2534 | 0.01831 | 122.3831 | 122.6166 | 122.4747 | -0.18311 | -0.18311 | 122.3831 | 122.6166 | -0.18311 | 0.01831 | 122.4747 | -122.4564 | -122.6257
255.6719 | 122.6715 | -61.1801 | 61.2534 | 0.0045015 | 0.044816 | 0.037375 | -0.0031915 | -0.0061587 | 0.063698 | 0.063166 | 61.4273 | 61.2076 | -61.203 | 61.2213 | -61.1572 | -61.3586 | 0.07782 | 0.068665 | 61.29 | -61.3953 | -0.022888 | -0.045776 | 122.6074 | 122.4014 | -122.4106 | -0.21515 | 0.036621 | 122.6303 | 61.2579 | 61.2488 | 0.022888 | 122.3877 | 122.6074 | 122.4701 | -0.17853 | -0.21515 | 122.3877 | 122.6074 | -0.17853 | 0.022888 | 122.4701 | -122.4564 | -122.6486
256.7188 | 122.7219 | -61.2259 | 61.2534 | -0.018387 | 0.03563 | 0.033317 | -0.011095 | -0.0070133 | 0.062416 | 0.064448 | 61.4044 | 61.116 | -61.1755 | 61.203 | -61.1435 | -61.3083 | -0.009155 | 0.059509 | 61.2671 | -61.3403 | 0.050354 | -0.13733 | 122.6303 | 122.4289 | -122.3969 | -0.11444 | 0.013733 | 122.58 | 61.2167 | 61.2854 | 0.082397 | 122.3419 | 122.6303 | 122.493 | -0.082398 | -0.11444 | 122.3419 | 122.6303 | -0.082398 | 0.082397 | 122.493 | -122.4289 | -122.5937
257.6719 | 122.6669 | -61.2259 | 61.29 | -0.003128 | 0.043962 | 0.036094 | -0.0042597 | -0.0072269 | 0.065407 | 0.064234 | 61.3953 | 61.1938 | -61.203 | 61.1801 | -61.1755 | -61.3861 | 0.14191 | 0.041199 | 61.2625 | -61.3495 | 0.022888 | -0.09613 | 122.6212 | 122.406 | -122.4655 | -0.1236 | -0.027466 | 122.5983 | 61.3678 | 61.2671 | 0.050354 | 122.4197 | 122.6212 | 122.4884 | -0.16022 | -0.1236 | 122.4197 | 122.6212 | -0.16022 | 0.050354 | 122.4884 | -122.493 | -122.6395
258.6719 | 122.6486 | -61.2213 | 61.2671 | -0.003128 | 0.042466 | 0.034385 | -0.0019099 | -0.0076541 | 0.066048 | 0.060816 | 61.3953 | 61.171 | -61.1847 | 61.1893 | -61.1847 | -61.4044 | 0.16479 | 0.027466 | 61.2946 | -61.3312 | 0.036621 | -0.096131 | 122.6166 | 122.4106 | -122.4518 | -0.10986 | 0.027466 | 122.58 | 61.3861 | 61.2488 | 0.036621 | 122.3923 | 122.6166 | 122.5159 | -0.18311 | -0.10986 | 122.3923 | 122.6166 | -0.18311 | 0.036621 | 122.5159 | -122.4518 | -122.5983
259.6719 | 122.6578 | -61.2122 | 61.2762 | -0.003128 | 0.038621 | 0.032248 | -0.0051141 | -0.0082949 | 0.063485 | 0.062952 | 61.4319 | 61.1435 | -61.1572 | 61.2076 | -61.1526 | -61.3632 | 0.15564 | 0.064087 | 61.3129 | -61.3586 | 0.054931 | -0.13275 | 122.644 | 122.4197 | -122.4289 | -0.14648 | 0.036621 | 122.5891 | 61.3678 | 61.2762 | 0.059509 | 122.3557 | 122.644 | 122.525 | -0.15106 | -0.14648 | 122.3557 | 122.644 | -0.15106 | 0.059509 | 122.525 | -122.4335 | -122.6349
260.6719 | 122.6761 | -61.2122 | 61.2808 | 0.0045015 | 0.041398 | 0.033957 | -0.0046869 | -0.0070133 | 0.063057 | 0.063166 | 61.4731 | 61.1389 | -61.1618 | 61.2488 | -61.1298 | -61.3312 | 0.11902 | 0.091553 | 61.2946 | -61.3312 | 0.050354 | -0.14191 | 122.6852 | 122.4609 | -122.4106 | -0.11902 | 0.013733 | 122.6349 | 61.3312 | 61.3037 | 0.082397 | 122.3511 | 122.6852 | 122.5067 | -0.11902 | -0.11902 | 122.3511 | 122.6852 | -0.11902 | 0.082397 | 122.5067 | -122.4426 | -122.612
261.6719 | 122.6395 | -61.2213 | 61.2946 | -0.003128 | 0.041612 | 0.034598 | -0.0044733 | -0.0048769 | 0.063698 | 0.062952 | 61.3998 | 61.203 | -61.1755 | 61.1893 | -61.1938 | -61.3724 | 0.19226 | 0.009155 | 61.3174 | -61.3632 | 0.045776 | -0.091553 | 122.6212 | 122.4106 | -122.4884 | -0.14191 | 0.022888 | 122.5754 | 61.4136 | 61.2305 | 0.027465 | 122.4243 | 122.6212 | 122.5388 | -0.15106 | -0.14191 | 122.4243 | 122.6212 | -0.15106 | 0.027465 | 122.5388 | -122.4701 | -122.6578
262.6719 | 122.6349 | -61.2213 | 61.3037 | -0.010758 | 0.040757 | 0.036521 | -0.0038325 | -0.0074405 | 0.063271 | 0.064021 | 61.3907 | 61.1618 | -61.1755 | 61.203 | -61.1618 | -61.3907 | 0.21973 | 0.022888 | 61.3174 | -61.322 | 0.045776 | -0.14191 | 122.612 | 122.4243 | -122.4655 | -0.10071 | 0.013733 | 122.5662 | 61.441 | 61.2442 | 0.059509 | 122.3831 | 122.612 | 122.5388 | -0.16937 | -0.10071 | 122.3831 | 122.612 | -0.16937 | 0.059509 | 122.5388 | -122.4792 | -122.6257
263.6719 | 122.6532 | -61.2488 | 61.322 | 0.0045015 | 0.039903 | 0.034598 | -0.0051141 | -0.0067995 | 0.063912 | 0.062525 | 61.3861 | 61.1847 | -61.1389 | 61.1984 | -61.1847 | -61.3678 | 0.20599 | 0.022888 | 61.3037 | -61.322 | 0.10986 | -0.13733 | 122.6349 | 122.4472 | -122.5067 | -0.073242 | -0.01831 | 122.525 | 61.4548 | 61.2717 | 0.064087 | 122.4335 | 122.6349 | 122.5525 | -0.11902 | -0.073242 | 122.4335 | 122.6349 | -0.11902 | 0.064087 | 122.5525 | -122.4609 | -122.644
264.6719 | 122.6532 | -61.2259 | 61.2946 | -0.010758 | 0.039903 | 0.034812 | -0.0025507 | -0.0087223 | 0.063057 | 0.062952 | 61.4136 | 61.1389 | -61.1847 | 61.2122 | -61.1664 | -61.377 | 0.17853 | 0.032043 | 61.3266 | -61.3174 | 0.041199 | -0.15564 | 122.6395 | 122.438 | -122.4609 | -0.091553 | 0.032043 | 122.5983 | 61.4044 | 61.2579 | 0.059509 | 122.3648 | 122.6395 | 122.5525 | -0.15106 | -0.091553 | 122.3648 | 122.6395 | -0.15106 | 0.059509 | 122.5525 | -122.4792 | -122.612
265.6719 | 122.6761 | -61.2122 | 61.2762 | -0.010758 | 0.03798 | 0.034385 | -0.0055413 | -0.0082949 | 0.064125 | 0.066157 | 61.4639 | 61.1481 | -61.171 | 61.2396 | -61.1206 | -61.3312 | 0.14191 | 0.086975 | 61.29 | -61.3174 | 0.041199 | -0.12817 | 122.6761 | 122.4518 | -122.3969 | -0.10529 | 0.013733 | 122.6349 | 61.3541 | 61.2991 | 0.091553 | 122.3602 | 122.6761 | 122.5021 | -0.11902 | -0.10529 | 122.3602 | 122.6761 | -0.11902 | 0.091553 | 122.5021 | -122.4472 | -122.5937
266.6719 | 122.7631 | -61.1847 | 61.2671 | -0.010758 | 0.03798 | 0.031608 | -0.0061823 | -0.0085085 | 0.063698 | 0.062525 | 61.5097 | 61.0886 | -61.1389 | 61.3312 | -61.0565 | -61.2488 | 0.027466 | 0.15106 | 61.2671 | -61.29 | 0.045776 | -0.17853 | 122.6944 | 122.5159 | -122.3236 | -0.10529 | 0 | 122.6486 | 61.2122 | 61.3358 | 0.12817 | 122.2733 | 122.6944 | 122.4518 | -0.064087 | -0.10529 | 122.2733 | 122.6944 | -0.064087 | 0.12817 | 122.4518 | -122.406 | -122.5571
267.6719 | 122.7814 | -61.1801 | 61.2762 | 0.0045015 | 0.037126 | 0.033957 | -0.0070367 | -0.0093631 | 0.064766 | 0.06103 | 61.5005 | 61.116 | -61.1526 | 61.3174 | -61.0519 | -61.2213 | 0.022888 | 0.15564 | 61.2534 | -61.2991 | 0.027466 | -0.16022 | 122.6807 | 122.4976 | -122.3282 | -0.11902 | -0.022888 | 122.6532 | 61.203 | 61.3358 | 0.12817 | 122.2961 | 122.6807 | 122.4335 | -0.041198 | -0.11902 | 122.2961 | 122.6807 | -0.041198 | 0.12817 | 122.4335 | -122.4289 | -122.5754
268.6719 | 122.6669 | -61.2122 | 61.2991 | -0.010758 | 0.039262 | 0.034171 | -0.0051141 | -0.0082949 | 0.06498 | 0.061457 | 61.4594 | 61.116 | -61.1435 | 61.2534 | -61.1343 | -61.3403 | 0.19226 | 0.045776 | 61.2946 | -61.3174 | 0.068664 | -0.1831 | 122.6715 | 122.4655 | -122.4335 | -0.10529 | -0.004577 | 122.6028 | 61.4044 | 61.2579 | 0.07782 | 122.3282 | 122.6715 | 122.5067 | -0.12817 | -0.10529 | 122.3282 | 122.6715 | -0.12817 | 0.07782 | 122.5067 | -122.4426 | -122.6166
269.6719 | 122.7081 | -61.2122 | 61.2762 | 0.0045015 | 0.037339 | 0.033317 | -0.0016961 | -0.0070133 | 0.064125 | 0.061244 | 61.4914 | 61.1206 | -61.1298 | 61.2762 | -61.1114 | -61.3129 | 0.14648 | 0.086975 | 61.29 | -61.3083 | 0.082397 | -0.15564 | 122.7036 | 122.4884 | -122.3877 | -0.096131 | 0.013733 | 122.6212 | 61.3586 | 61.2991 | 0.10071 | 122.3328 | 122.7036 | 122.5021 | -0.10071 | -0.096131 | 122.3328 | 122.7036 | -0.10071 | 0.10071 | 122.5021 | -122.406 | -122.5845
270.6719 | 122.7448 | -61.1984 | 61.2808 | -0.003128 | 0.037553 | 0.033957 | -0.0049005 | -0.0080813 | 0.065834 | 0.061244 | 61.4731 | 61.0931 | -61.1664 | 61.3083 | -61.0748 | -61.2762 | 0.14648 | 0.11902 | 61.3129 | -61.3174 | 0.032043 | -0.18768 | 122.6715 | 122.5067 | -122.3557 | -0.11902 | 0.032043 | 122.6395 | 61.3449 | 61.3174 | 0.1236 | 122.2916 | 122.6715 | 122.5113 | -0.07782 | -0.11902 | 122.2916 | 122.6715 | -0.07782 | 0.1236 | 122.5113 | -122.4472 | -122.5983
271.6719 | 122.7356 | -61.1893 | 61.2762 | -0.010758 | 0.037339 | 0.039298 | -0.0025507 | -0.0091495 | 0.064339 | 0.060175 | 61.496 | 61.0977 | -61.1252 | 61.3174 | -61.0703 | -61.2717 | 0.1236 | 0.12817 | 61.2534 | -61.2762 | 0.064087 | -0.17853 | 122.6852 | 122.5067 | -122.3465 | -0.086975 | -0.022888 | 122.6212 | 61.3129 | 61.3174 | 0.11902 | 122.287 | 122.6852 | 122.4426 | -0.082397 | -0.086975 | 122.287 | 122.6852 | -0.082397 | 0.11902 | 122.4426 | -122.4014 | -122.5525
272.6719 | 122.7631 | -61.2076 | 61.2762 | -0.010758 | 0.036057 | 0.035666 | -0.0021235 | -0.0089359 | 0.063271 | 0.061884 | 61.496 | 61.1069 | -61.1572 | 61.3174 | -61.084 | -61.2579 | 0.11902 | 0.13275 | 61.2579 | -61.2762 | 0.050354 | -0.16937 | 122.7036 | 122.525 | -122.3602 | -0.068664 | -0.01831 | 122.6532 | 61.3266 | 61.3403 | 0.1236 | 122.3145 | 122.7036 | 122.4655 | -0.050354 | -0.068664 | 122.3145 | 122.7036 | -0.050354 | 0.1236 | 122.4655 | -122.4335 | -122.5525
273.6719 | 122.7997 | -61.1938 | 61.2534 | 0.0045015 | 0.036912 | 0.025413 | -0.0057551 | -0.0095767 | 0.063057 | 0.061671 | 61.5051 | 61.084 | -61.1664 | 61.3358 | -61.0336 | -61.2442 | 0.091553 | 0.15106 | 61.2396 | -61.2854 | 0.027466 | -0.16937 | 122.699 | 122.5296 | -122.287 | -0.091552 | -0.013733 | 122.6715 | 61.2854 | 61.3449 | 0.16022 | 122.2778 | 122.699 | 122.4335 | -0.050354 | -0.091552 | 122.2778 | 122.699 | -0.050354 | 0.16022 | 122.4335 | -122.4197 | -122.5388
274.6719 | 122.7768 | -61.2076 | 61.2488 | 0.0045015 | 0.038407 | 0.030967 | -0.0027643 | -0.0076541 | 0.064339 | 0.060389 | 61.4914 | 61.0977 | -61.1481 | 61.3266 | -61.0519 | -61.2534 | 0.10071 | 0.15106 | 61.2305 | -61.2579 | 0.05951 | -0.15106 | 122.699 | 122.5342 | -122.3007 | -0.050354 | -0.01831 | 122.6395 | 61.3083 | 61.3586 | 0.15564 | 122.3053 | 122.699 | 122.4381 | -0.045776 | -0.050354 | 122.3053 | 122.699 | -0.045776 | 0.15564 | 122.4381 | -122.3969 | -122.5067
275.6719 | 122.7402 | -61.2122 | 61.2762 | -0.010758 | 0.037766 | 0.030112 | -0.0034051 | -0.0097903 | 0.061989 | 0.060603 | 61.4822 | 61.1206 | -61.1481 | 61.3037 | -61.0794 | -61.2717 | 0.19684 | 0.15106 | 61.2396 | -61.322 | 0.064087 | -0.15564 | 122.6944 | 122.5159 | -122.3557 | -0.10986 | -0.036621 | 122.6303 | 61.409 | 61.3632 | 0.13275 | 122.3328 | 122.6944 | 122.4518 | -0.059509 | -0.10986 | 122.3328 | 122.6944 | -0.059509 | 0.13275 | 122.4518 | -122.4243 | -122.5983
276.6719 | 122.7493 | -61.2167 | 61.2625 | -0.018387 | 0.039475 | 0.032889 | -0.0025507 | -0.0091495 | 0.061989 | 0.062098 | 61.5051 | 61.0748 | -61.1618 | 61.322 | -61.0657 | -61.2579 | 0.17395 | 0.14648 | 61.2488 | -61.29 | 0.054932 | -0.18768 | 122.7219 | 122.5388 | -122.3282 | -0.073242 | -0.013733 | 122.6669 | 61.3907 | 61.3632 | 0.15106 | 122.2916 | 122.7219 | 122.4655 | -0.041199 | -0.073242 | 122.2916 | 122.7219 | -0.041199 | 0.15106 | 122.4655 | -122.4243 | -122.5525
277.6719 | 122.7539 | -61.203 | 61.2488 | 0.0045015 | 0.036057 | 0.032889 | -0.0029779 | -0.010218 | 0.063485 | 0.061244 | 61.496 | 61.0886 | -61.1435 | 61.3266 | -61.0519 | -61.2671 | 0.18768 | 0.15106 | 61.235 | -61.2946 | 0.059509 | -0.16022 | 122.699 | 122.5296 | -122.3007 | -0.091553 | -0.013733 | 122.6395 | 61.3907 | 61.3541 | 0.15106 | 122.2916 | 122.699 | 122.438 | -0.064087 | -0.091553 | 122.2916 | 122.699 | -0.064087 | 0.15106 | 122.438 | -122.3923 | -122.5433
278.6719 | 122.7768 | -61.1893 | 61.235 | -0.003128 | 0.034135 | 0.031394 | -0.0049005 | -0.0095767 | 0.061135 | 0.061244 | 61.5097 | 61.0886 | -61.1664 | 61.3312 | -61.0474 | -61.2534 | 0.20599 | 0.16479 | 61.2488 | -61.2579 | 0.022888 | -0.14648 | 122.699 | 122.5204 | -122.2824 | -0.068665 | 0.013733 | 122.6761 | 61.3953 | 61.3541 | 0.14191 | 122.2778 | 122.699 | 122.438 | -0.064087 | -0.068665 | 122.2778 | 122.699 | -0.064087 | 0.14191 | 122.438 | -122.4014 | -122.493
279.6719 | 122.7722 | -61.1984 | 61.2762 | -0.003128 | 0.035844 | 0.033317 | -0.0021235 | -0.011286 | 0.063485 | 0.061884 | 61.4914 | 61.0931 | -61.1481 | 61.3403 | -61.0291 | -61.2625 | 0.2243 | 0.16479 | 61.2305 | -61.2671 | 0.050354 | -0.18311 | 122.6898 | 122.5388 | -122.3053 | -0.068665 | -0.045776 | 122.6395 | 61.4227 | 61.3632 | 0.16937 | 122.2916 | 122.6898 | 122.4289 | -0.064087 | -0.068665 | 122.2916 | 122.6898 | -0.064087 | 0.16937 | 122.4289 | -122.4243 | -122.5433
280.6719 | 122.7676 | -61.203 | 61.235 | 0.01213 | 0.03563 | 0.034171 | -0.0046869 | -0.0089359 | 0.063912 | 0.062098 | 61.4868 | 61.0657 | -61.1343 | 61.3129 | -61.0565 | -61.2488 | 0.22888 | 0.12817 | 61.2534 | -61.29 | 0.068665 | -0.16937 | 122.6898 | 122.5159 | -122.2916 | -0.086975 | 0.018311 | 122.6212 | 61.4319 | 61.3312 | 0.14648 | 122.2687 | 122.6898 | 122.4564 | -0.045776 | -0.086975 | 122.2687 | 122.6898 | -0.045776 | 0.14648 | 122.4564 | -122.3694 | -122.525
281.6719 | 122.7585 | -61.2259 | 61.2442 | 0.01213 | 0.034989 | 0.029899 | -0.0042597 | -0.0097903 | 0.06498 | 0.062312 | 61.4685 | 61.0977 | -61.1435 | 61.3174 | -61.0703 | -61.2625 | 0.25635 | 0.1236 | 61.235 | -61.2854 | 0.082397 | -0.14648 | 122.6944 | 122.5433 | -122.3145 | -0.059509 | -0.009156 | 122.612 | 61.4822 | 61.3495 | 0.15564 | 122.3236 | 122.6944 | 122.4609 | -0.036621 | -0.059509 | 122.3236 | 122.6944 | -0.036621 | 0.15564 | 122.4609 | -122.3877 | -122.5296
282.6719 | 122.7585 | -61.2213 | 61.2579 | 0.0045015 | 0.038407 | 0.033317 | -0.0031915 | -0.010218 | 0.061776 | 0.061884 | 61.5097 | 61.0886 | -61.1618 | 61.3403 | -61.0474 | -61.2488 | 0.29297 | 0.16479 | 61.2213 | -61.2762 | 0.059509 | -0.16937 | 122.731 | 122.5616 | -122.3053 | -0.054932 | -0.036622 | 122.6715 | 61.5143 | 61.3861 | 0.17395 | 122.3099 | 122.731 | 122.4426 | -0.027466 | -0.054932 | 122.3099 | 122.731 | -0.027466 | 0.17395 | 122.4426 | -122.4197 | -122.5342
283.6719 | 122.7631 | -61.203 | 61.2579 | -0.003128 | 0.038621 | 0.034171 | -0.0036187 | -0.0085085 | 0.062203 | 0.061244 | 61.5051 | 61.1023 | -61.1526 | 61.3358 | -61.0519 | -61.2442 | 0.31586 | 0.16937 | 61.235 | -61.2808 | 0.050354 | -0.15564 | 122.7081 | 122.5388 | -122.3099 | -0.07782 | -0.022889 | 122.6578 | 61.5189 | 61.3724 | 0.15106 | 122.3053 | 122.7081 | 122.438 | -0.041199 | -0.07782 | 122.3053 | 122.7081 | -0.041199 | 0.15106 | 122.438 | -122.4106 | -122.5388
284.6719 | 122.7722 | -61.2076 | 61.2717 | 0.01213 | 0.037126 | 0.032676 | -0.0021235 | -0.0093631 | 0.063912 | 0.060816 | 61.5189 | 61.0886 | -61.1343 | 61.3449 | -61.0519 | -61.2579 | 0.32501 | 0.17395 | 61.2259 | -61.2625 | 0.073243 | -0.1831 | 122.7264 | 122.5525 | -122.3236 | -0.054931 | -0.045776 | 122.6532 | 61.5326 | 61.3815 | 0.15564 | 122.2961 | 122.7264 | 122.4335 | -0.050354 | -0.054931 | 122.2961 | 122.7264 | -0.050354 | 0.15564 | 122.4335 | -122.406 | -122.5342
285.6719 | 122.7859 | -61.171 | 61.2442 | -0.010758 | 0.035844 | 0.035239 | -0.0036187 | -0.010431 | 0.06028 | 0.06338 | 61.5189 | 61.0748 | -61.1481 | 61.3495 | -61.0336 | -61.2442 | 0.34332 | 0.1831 | 61.2167 | -61.2579 | 0.022888 | -0.16937 | 122.6898 | 122.5204 | -122.2778 | -0.086976 | -0.027466 | 122.6669 | 61.5143 | 61.3541 | 0.13733 | 122.2458 | 122.6898 | 122.3877 | -0.073243 | -0.086976 | 122.2458 | 122.6898 | -0.073243 | 0.13733 | 122.3877 | -122.3923 | -122.5021
286.6719 | 122.7951 | -61.2122 | 61.2579 | -0.003128 | 0.035203 | 0.033957 | -0.0055413 | -0.0097903 | 0.062203 | 0.063807 | 61.5143 | 61.084 | -61.1526 | 61.3449 | -61.0428 | -61.2259 | 0.3479 | 0.16479 | 61.2305 | -61.2488 | 0.059509 | -0.17395 | 122.7264 | 122.5571 | -122.3007 | -0.036621 | -0.027466 | 122.6669 | 61.5601 | 61.377 | 0.16937 | 122.2961 | 122.7264 | 122.4426 | -0.013733 | -0.036621 | 122.2961 | 122.7264 | -0.013733 | 0.16937 | 122.4426 | -122.4106 | -122.5067
287.6719 | 122.7676 | -61.2167 | 61.2671 | 0.0045015 | 0.033921 | 0.031608 | -0.0044733 | -0.010859 | 0.062416 | 0.062952 | 61.4319 | 61.1069 | -61.1755 | 61.2854 | -61.0703 | -61.2671 | 0.39825 | 0.10529 | 61.2167 | -61.2762 | 0.041199 | -0.16022 | 122.6486 | 122.5021 | -122.3373 | -0.059509 | -0.050354 | 122.6074 | 61.615 | 61.322 | 0.14648 | 122.3236 | 122.6486 | 122.4335 | -0.050354 | -0.059509 | 122.3236 | 122.6486 | -0.050354 | 0.14648 | 122.4335 | -122.4426 | -122.5433
288.6719 | 122.7859 | -61.2122 | 61.2534 | -0.003128 | 0.036057 | 0.032462 | -0.0044733 | -0.010218 | 0.062203 | 0.061884 | 61.496 | 61.0886 | -61.1572 | 61.3174 | -61.0519 | -61.2488 | 0.37537 | 0.16022 | 61.2122 | -61.2854 | 0.054931 | -0.16479 | 122.7081 | 122.5296 | -122.3053 | -0.073242 | -0.041199 | 122.6532 | 61.5875 | 61.3724 | 0.16022 | 122.3007 | 122.7081 | 122.4243 | -0.036621 | -0.073242 | 122.3007 | 122.7081 | -0.036621 | 0.16022 | 122.4243 | -122.4106 | -122.5388
289.6719 | 122.7768 | -61.2076 | 61.2488 | 0.0045015 | 0.035844 | 0.031821 | -0.0034051 | -0.011286 | 0.063485 | 0.061244 | 61.5143 | 61.0748 | -61.1435 | 61.3449 | -61.0382 | -61.2442 | 0.43488 | 0.19226 | 61.2076 | -61.2579 | 0.064087 | -0.17395 | 122.7219 | 122.5525 | -122.287 | -0.050354 | -0.041198 | 122.6578 | 61.6425 | 61.3998 | 0.16937 | 122.2824 | 122.7219 | 122.4152 | -0.036621 | -0.050354 | 122.2824 | 122.7219 | -0.036621 | 0.16937 | 122.4152 | -122.3923 | -122.5067
290.6719 | 122.7951 | -61.1801 | 61.2762 | -0.010758 | 0.037553 | 0.030539 | -0.0068231 | -0.0089359 | 0.061989 | 0.060603 | 61.5051 | 61.0703 | -61.1572 | 61.3449 | -61.0245 | -61.235 | 0.45319 | 0.17395 | 61.2396 | -61.2488 | 0.022888 | -0.20599 | 122.6852 | 122.525 | -122.3007 | -0.068664 | -0.036621 | 122.6624 | 61.6333 | 61.3541 | 0.15564 | 122.2504 | 122.6852 | 122.4197 | -0.054931 | -0.068664 | 122.2504 | 122.6852 | -0.054931 | 0.15564 | 122.4197 | -122.4335 | -122.525
291.6719 | 122.7768 | -61.2213 | 61.2534 | -0.003128 | 0.03798 | 0.032462 | -0.0034051 | -0.0093631 | 0.064125 | 0.061671 | 61.496 | 61.0794 | -61.1847 | 61.3358 | -61.0565 | -61.2396 | 0.46234 | 0.19226 | 61.2167 | -61.2579 | 0.036621 | -0.17395 | 122.7173 | 122.5571 | -122.3099 | -0.036622 | -0.036621 | 122.6807 | 61.6837 | 61.4136 | 0.16479 | 122.3007 | 122.7173 | 122.438 | -0.018311 | -0.036622 | 122.3007 | 122.7173 | -0.018311 | 0.16479 | 122.438 | -122.438 | -122.5113
292.6719 | 122.7814 | -61.2259 | 61.2579 | -0.010758 | 0.037766 | 0.029471 | -0.0046869 | -0.010859 | 0.062416 | 0.062952 | 61.4685 | 61.0703 | -61.1435 | 61.3266 | -61.0611 | -61.2579 | 0.49439 | 0.15564 | 61.2122 | -61.2579 | 0.082397 | -0.18768 | 122.6944 | 122.5525 | -122.319 | -0.032044 | -0.045777 | 122.612 | 61.7203 | 61.3815 | 0.16479 | 122.2961 | 122.6944 | 122.438 | -0.032044 | -0.032044 | 122.2961 | 122.6944 | -0.032044 | 0.16479 | 122.438 | -122.4014 | -122.5159
293.6719 | 122.7631 | -61.2213 | 61.2442 | -0.003128 | 0.035417 | 0.032035 | -0.0036187 | -0.0097903 | 0.06498 | 0.061244 | 61.4685 | 61.1069 | -61.1664 | 61.3083 | -61.0703 | -61.2488 | 0.5722 | 0.14648 | 61.2213 | -61.2946 | 0.054931 | -0.13733 | 122.6898 | 122.5296 | -122.3145 | -0.073243 | -0.022889 | 122.6349 | 61.7935 | 61.3678 | 0.15106 | 122.3282 | 122.6898 | 122.4426 | -0.027466 | -0.073243 | 122.3282 | 122.6898 | -0.027466 | 0.15106 | 122.4426 | -122.4106 | -122.5388
294.6719 | 122.7127 | -61.2579 | 61.2259 | -0.010758 | 0.03798 | 0.029044 | -0.0027643 | -0.010859 | 0.064766 | 0.062098 | 61.3998 | 61.0611 | -61.1893 | 61.2305 | -61.1435 | -61.3312 | 0.58594 | 0.041199 | 61.1801 | -61.2946 | 0.068665 | -0.16479 | 122.6578 | 122.4884 | -122.3694 | -0.036621 | -0.045776 | 122.5891 | 61.8439 | 61.2991 | 0.11444 | 122.319 | 122.6578 | 122.4381 | -0.073242 | -0.036621 | 122.319 | 122.6578 | -0.073242 | 0.11444 | 122.4381 | -122.4152 | -122.5204
295.6719 | 122.7356 | -61.2579 | 61.2579 | -0.010758 | 0.036698 | 0.028831 | -0.0044733 | -0.011072 | 0.063485 | 0.062952 | 61.4136 | 61.0931 | -61.1618 | 61.2534 | -61.1114 | -61.2946 | 0.64087 | 0.10529 | 61.1893 | -61.2808 | 0.096131 | -0.1648 | 122.6715 | 122.5113 | -122.3694 | -0.022888 | -0.068665 | 122.5754 | 61.8988 | 61.3632 | 0.14649 | 122.3511 | 122.6715 | 122.4472 | -0.036621 | -0.022888 | 122.3511 | 122.6715 | -0.036621 | 0.14649 | 122.4472 | -122.4197 | -122.5388
296.6719 | 122.7676 | -61.2122 | 61.2396 | -0.010758 | 0.035417 | 0.030967 | -0.0061823 | -0.0091495 | 0.063912 | 0.063166 | 61.4548 | 61.0931 | -61.1526 | 61.3083 | -61.0703 | -61.2488 | 0.66834 | 0.16479 | 61.2259 | -61.2717 | 0.059509 | -0.14648 | 122.6669 | 122.5204 | -122.3099 | -0.059509 | -0.013733 | 122.6074 | 61.8805 | 61.377 | 0.14191 | 122.3053 | 122.6669 | 122.438 | -0.036621 | -0.059509 | 122.3053 | 122.6669 | -0.036621 | 0.14191 | 122.438 | -122.3923 | -122.5113
297.6719 | 122.7493 | -61.2213 | 61.2762 | -0.003128 | 0.036057 | 0.032248 | -0.0029779 | -0.010645 | 0.064766 | 0.062312 | 61.4456 | 61.0748 | -61.1801 | 61.2854 | -61.0886 | -61.2488 | 0.71411 | 0.15106 | 61.1893 | -61.2671 | 0.041198 | -0.20142 | 122.6669 | 122.5067 | -122.3648 | -0.045777 | -0.086975 | 122.6257 | 61.9354 | 61.3724 | 0.13275 | 122.2961 | 122.6669 | 122.4106 | -0.027466 | -0.045777 | 122.2961 | 122.6669 | -0.027466 | 0.13275 | 122.4106 | -122.4564 | -122.5433
298.6719 | 122.7539 | -61.2396 | 61.2534 | 0.0045015 | 0.034776 | 0.032676 | -0.0068231 | -0.0078677 | 0.061989 | 0.062739 | 61.4273 | 61.0748 | -61.1618 | 61.2488 | -61.1252 | -61.29 | 0.74616 | 0.1236 | 61.1938 | -61.3037 | 0.07782 | -0.17853 | 122.6669 | 122.4884 | -122.3785 | -0.064087 | -0.059509 | 122.5891 | 61.9858 | 61.3632 | 0.11444 | 122.3145 | 122.6669 | 122.4335 | -0.050354 | -0.064087 | 122.3145 | 122.6669 | -0.050354 | 0.11444 | 122.4335 | -122.4152 | -122.5571
299.6719 | 122.7264 | -61.2488 | 61.2305 | -0.003128 | 0.034562 | 0.030753 | -0.0044733 | -0.011072 | 0.062844 | 0.062739 | 61.409 | 61.084 | -61.171 | 61.2396 | -61.1252 | -61.3266 | 0.80566 | 0.082397 | 61.1893 | -61.2946 | 0.07782 | -0.14648 | 122.6578 | 122.4884 | -122.3557 | -0.045777 | -0.041199 | 122.58 | 62.0544 | 61.3312 | 0.1236 | 122.3328 | 122.6578 | 122.438 | -0.07782 | -0.045777 | 122.3328 | 122.6578 | -0.07782 | 0.1236 | 122.438 | -122.4014 | -122.525
300.6719 | 122.7081 | -61.2305 | 61.2488 | 0.0045015 | 0.037126 | 0.032676 | -0.0027643 | -0.010004 | 0.064553 | 0.065516 | 61.3907 | 61.0794 | -61.203 | 61.2259 | -61.1435 | -61.3449 | 0.8606 | 0.082397 | 61.1984 | -61.2762 | 0.027466 | -0.16937 | 122.6212 | 122.4564 | -122.3923 | -0.045776 | -0.050354 | 122.5937 | 62.0911 | 61.3129 | 0.086975 | 122.3099 | 122.6212 | 122.4289 | -0.11444 | -0.045776 | 122.3099 | 122.6212 | -0.11444 | 0.086975 | 122.4289 | -122.4518 | -122.525
301.6719 | 122.7036 | -61.2305 | 61.203 | -0.003128 | 0.036485 | 0.033103 | -0.0038325 | -0.010004 | 0.064766 | 0.060389 | 61.4319 | 61.0382 | -61.171 | 61.235 | -61.1435 | -61.3312 | 0.81482 | 0.086975 | 61.1801 | -61.3358 | 0.05951 | -0.1648 | 122.6624 | 122.4655 | -122.3465 | -0.10529 | -0.022888 | 122.6028 | 62.0453 | 61.3174 | 0.086975 | 122.2687 | 122.6624 | 122.4106 | -0.10071 | -0.10529 | 122.2687 | 122.6624 | -0.10071 | 0.086975 | 122.4106 | -122.374 | -122.5388
302.6719 | 122.7264 | -61.2259 | 61.235 | -0.010758 | 0.03563 | 0.030753 | -0.0042597 | -0.011072 | 0.06263 | 0.061884 | 61.3998 | 61.0748 | -61.1664 | 61.2305 | -61.1343 | -61.3129 | 0.95215 | 0.10986 | 61.1938 | -61.2946 | 0.059509 | -0.16022 | 122.6257 | 122.4564 | -122.3694 | -0.068665 | -0.041198 | 122.5662 | 62.178 | 61.3358 | 0.091553 | 122.3007 | 122.6257 | 122.4197 | -0.086975 | -0.068665 | 122.3007 | 122.6257 | -0.086975 | 0.091553 | 122.4197 | -122.4014 | -122.5296
303.6719 | 122.7219 | -61.2396 | 61.2396 | -0.003128 | 0.036485 | 0.030326 | -0.0051141 | -0.012781 | 0.065834 | 0.062098 | 61.3998 | 61.1023 | -61.1938 | 61.2305 | -61.1526 | -61.322 | 1.0025 | 0.11444 | 61.1755 | -61.3083 | 0.045776 | -0.13733 | 122.6395 | 122.4701 | -122.3923 | -0.068665 | -0.064087 | 122.5937 | 62.2421 | 61.3541 | 0.086975 | 122.3419 | 122.6395 | 122.4152 | -0.082397 | -0.068665 | 122.3419 | 122.6395 | -0.082397 | 0.086975 | 122.4152 | -122.4335 | -122.5479
304.6719 | 122.7173 | -61.2305 | 61.235 | 0.0045015 | 0.036698 | 0.035453 | -0.0034051 | -0.011072 | 0.063271 | 0.061244 | 61.3953 | 61.0657 | -61.1618 | 61.2122 | -61.1481 | -61.3449 | 1.0712 | 0.10071 | 61.203 | -61.2854 | 0.068665 | -0.16937 | 122.6257 | 122.4426 | -122.3831 | -0.054931 | -0.032043 | 122.5571 | 62.3016 | 61.3312 | 0.082398 | 122.2961 | 122.6257 | 122.4335 | -0.11444 | -0.054931 | 122.2961 | 122.6257 | -0.11444 | 0.082398 | 122.4335 | -122.3969 | -122.5204
305.6719 | 122.7081 | -61.2442 | 61.2259 | -0.010758 | 0.034776 | 0.035026 | -0.0040461 | -0.011286 | 0.063057 | 0.062952 | 61.409 | 61.0886 | -61.1984 | 61.2167 | -61.1481 | -61.3312 | 1.1627 | 0.09613 | 61.1664 | -61.3083 | 0.045777 | -0.13733 | 122.6532 | 122.4609 | -122.374 | -0.064087 | -0.059509 | 122.6074 | 62.4069 | 61.3403 | 0.096131 | 122.3328 | 122.6532 | 122.4106 | -0.086975 | -0.064087 | 122.3328 | 122.6532 | -0.086975 | 0.096131 | 122.4106 | -122.4243 | -122.5342
306.6719 | 122.7173 | -61.2305 | 61.2305 | -0.003128 | 0.038194 | 0.033317 | -0.0029779 | -0.010218 | 0.061989 | 0.062525 | 61.3998 | 61.0748 | -61.1847 | 61.2213 | -61.1389 | -61.3312 | 1.1856 | 0.10529 | 61.1893 | -61.2946 | 0.045777 | -0.15564 | 122.6303 | 122.4518 | -122.3694 | -0.064087 | -0.041199 | 122.5845 | 62.4161 | 61.3358 | 0.091553 | 122.3053 | 122.6303 | 122.4197 | -0.10071 | -0.064087 | 122.3053 | 122.6303 | -0.10071 | 0.091553 | 122.4197 | -122.4152 | -122.525
307.6719 | 122.6532 | -61.2488 | 61.2762 | -0.003128 | 0.043748 | 0.038444 | 0.0004401 | -0.0093631 | 0.064553 | 0.061884 | 61.3953 | 61.1801 | -61.1847 | 61.1938 | -61.1893 | -61.4044 | 1.4648 | 0.10986 | 61.2259 | -61.3541 | 0.064087 | -0.09613 | 122.644 | 122.4426 | -122.4655 | -0.10529 | -0.050354 | 122.58 | 62.7136 | 61.3586 | 0.059509 | 122.4289 | 122.644 | 122.4747 | -0.15564 | -0.10529 | 122.4289 | 122.644 | -0.15564 | 0.059509 | 122.4747 | -122.4609 | -122.6303
308.6719 | 122.7402 | -61.2396 | 61.171 | -0.003128 | 0.036485 | 0.035026 | -0.0029779 | -0.0065859 | 0.061348 | 0.061671 | 61.4456 | 61.0382 | -61.2213 | 61.2488 | -61.1114 | -61.3083 | 1.2497 | 0.13733 | 61.1755 | -61.2854 | 0.018311 | -0.13275 | 122.6852 | 122.4884 | -122.2824 | -0.045776 | 0.004578 | 122.6669 | 62.4893 | 61.377 | 0.12817 | 122.2778 | 122.6852 | 122.4152 | -0.068665 | -0.045776 | 122.2778 | 122.6852 | -0.068665 | 0.12817 | 122.4152 | -122.3923 | -122.4564
309.6719 | 122.7173 | -61.2305 | 61.1938 | -0.003128 | 0.034776 | 0.033744 | -0.0046869 | -0.010218 | 0.064125 | 0.062952 | 61.3907 | 61.0611 | -61.1755 | 61.2259 | -61.1435 | -61.3266 | 1.4145 | 0.13275 | 61.1572 | -61.3083 | 0.054932 | -0.13275 | 122.6212 | 122.4564 | -122.3373 | -0.07782 | -0.036621 | 122.5662 | 62.645 | 61.3632 | 0.086975 | 122.2916 | 122.6212 | 122.3877 | -0.09613 | -0.07782 | 122.2916 | 122.6212 | -0.09613 | 0.086975 | 122.3877 | -122.3694 | -122.5021
310.6719 | 122.699 | -61.2442 | 61.2305 | -0.003128 | 0.036912 | 0.030539 | -0.0053277 | -0.010218 | 0.063912 | 0.065302 | 61.3907 | 61.0886 | -61.1801 | 61.2122 | -61.1435 | -61.3312 | 1.5106 | 0.14648 | 61.203 | -61.2991 | 0.064087 | -0.14191 | 122.6349 | 122.4564 | -122.374 | -0.054931 | -0.027466 | 122.5708 | 62.7548 | 61.3907 | 0.10071 | 122.3328 | 122.6349 | 122.4472 | -0.086975 | -0.054931 | 122.3328 | 122.6349 | -0.086975 | 0.10071 | 122.4472 | -122.4106 | -122.5296
311.6719 | 122.7173 | -61.235 | 61.2167 | -0.010758 | 0.035844 | 0.032035 | -0.0031915 | -0.011072 | 0.063485 | 0.060816 | 61.3998 | 61.0794 | -61.1755 | 61.2167 | -61.1526 | -61.3266 | 1.6205 | 0.15564 | 61.1938 | -61.3312 | 0.059509 | -0.13733 | 122.6349 | 122.4518 | -122.3694 | -0.096131 | -0.022888 | 122.5754 | 62.8555 | 61.3907 | 0.082397 | 122.3145 | 122.6349 | 122.4289 | -0.091553 | -0.096131 | 122.3145 | 122.6349 | -0.091553 | 0.082397 | 122.4289 | -122.3923 | -122.5479
312.6719 | 122.6898 | -61.2259 | 61.2213 | 0.0045015 | 0.040971 | 0.036307 | 0.0006537 | -0.0082949 | 0.06498 | 0.062952 | 61.4227 | 61.1664 | -61.2167 | 61.2122 | -61.1664 | -61.377 | 1.767 | 0.16937 | 61.1984 | -61.3815 | 0.009155 | -0.054931 | 122.6486 | 122.438 | -122.3877 | -0.15564 | -0.022888 | 122.6395 | 62.9929 | 61.3953 | 0.059509 | 122.3923 | 122.6486 | 122.4243 | -0.15106 | -0.15564 | 122.3923 | 122.6486 | -0.15106 | 0.059509 | 122.4243 | -122.438 | -122.6028
313.6719 | 122.7173 | -61.2442 | 61.2305 | -0.003128 | 0.036912 | 0.033317 | -0.0055413 | -0.0076541 | 0.063057 | 0.061244 | 61.3998 | 61.0657 | -61.1847 | 61.2167 | -61.1572 | -61.3266 | 1.6479 | 0.15564 | 61.1984 | -61.3129 | 0.05951 | -0.16479 | 122.644 | 122.4609 | -122.3877 | -0.068664 | -0.032044 | 122.5845 | 62.8922 | 61.3998 | 0.086975 | 122.3099 | 122.644 | 122.4426 | -0.082397 | -0.068664 | 122.3099 | 122.644 | -0.082397 | 0.086975 | 122.4426 | -122.4152 | -122.5433
314.6719 | 122.7219 | -61.203 | 61.2122 | 0.0045015 | 0.035844 | 0.030753 | -0.0051141 | -0.0091495 | 0.062844 | 0.063593 | 61.3953 | 61.0657 | -61.1755 | 61.2122 | -61.1481 | -61.322 | 1.7624 | 0.15564 | 61.1618 | -61.3129 | 0.027466 | -0.14648 | 122.5983 | 122.4152 | -122.3602 | -0.10986 | -0.050354 | 122.5708 | 62.9654 | 61.3586 | 0.054932 | 122.2687 | 122.5983 | 122.3648 | -0.11902 | -0.10986 | 122.2687 | 122.5983 | -0.11902 | 0.054932 | 122.3648 | -122.3877 | -122.525
315.6719 | 122.7631 | -61.2259 | 61.1938 | 0.0045015 | 0.037339 | 0.038657 | -0.0023371 | -0.010218 | 0.063271 | 0.062312 | 61.4456 | 61.0291 | -61.2076 | 61.2488 | -61.1114 | -61.3083 | 1.7166 | 0.19226 | 61.1572 | -61.3174 | 0.01831 | -0.1648 | 122.6715 | 122.4747 | -122.3053 | -0.091553 | -0.036621 | 122.6532 | 62.9425 | 61.4182 | 0.11444 | 122.2549 | 122.6715 | 122.3831 | -0.082398 | -0.091553 | 122.2549 | 122.6715 | -0.082398 | 0.11444 | 122.3831 | -122.4014 | -122.5113
316.6719 | 122.731 | -61.235 | 61.2122 | 0.0045015 | 0.036057 | 0.037162 | -0.0021235 | -0.0078677 | 0.063698 | 0.063166 | 61.4227 | 61.0611 | -61.1938 | 61.2122 | -61.1481 | -61.3174 | 1.7807 | 0.17853 | 61.1618 | -61.3174 | 0.041198 | -0.15106 | 122.6578 | 122.4472 | -122.3602 | -0.082398 | -0.050354 | 122.6166 | 63.0157 | 61.4136 | 0.086975 | 122.2961 | 122.6578 | 122.3969 | -0.082398 | -0.082398 | 122.2961 | 122.6578 | -0.082398 | 0.086975 | 122.3969 | -122.406 | -122.5296
317.6719 | 122.6395 | -61.2625 | 61.2534 | -0.010758 | 0.042466 | 0.033957 | 0.0004401 | -0.010004 | 0.065407 | 0.062952 | 61.3861 | 61.1664 | -61.1984 | 61.171 | -61.1893 | -61.4044 | 2.211 | 0.16479 | 61.2396 | -61.3586 | 0.064087 | -0.086975 | 122.6486 | 122.4335 | -122.4426 | -0.096131 | -0.013733 | 122.5845 | 63.4735 | 61.4273 | 0.073242 | 122.4289 | 122.6486 | 122.5021 | -0.14191 | -0.096131 | 122.4289 | 122.6486 | -0.14191 | 0.073242 | 122.5021 | -122.4518 | -122.612
318.6719 | 122.7219 | -61.203 | 61.2076 | -0.010758 | 0.037339 | 0.033103 | -0.0053277 | -0.0076541 | 0.063485 | 0.062312 | 61.3953 | 61.0519 | -61.2076 | 61.2076 | -61.1481 | -61.3358 | 1.9409 | 0.17395 | 61.1938 | -61.3129 | -0.004578 | -0.15564 | 122.5983 | 122.4106 | -122.3557 | -0.10986 | -0.013733 | 122.6028 | 63.1439 | 61.377 | 0.054932 | 122.2549 | 122.5983 | 122.3969 | -0.13275 | -0.10986 | 122.2549 | 122.5983 | -0.13275 | 0.054932 | 122.3969 | -122.4152 | -122.5204
319.6719 | 122.7219 | -61.2122 | 61.2076 | -0.003128 | 0.034776 | 0.032035 | -0.0044733 | -0.0080813 | 0.064339 | 0.063807 | 61.409 | 61.0291 | -61.2259 | 61.2167 | -61.1481 | -61.3312 | 2.0004 | 0.20142 | 61.1664 | -61.3403 | -0.013733 | -0.17853 | 122.6212 | 122.4289 | -122.3557 | -0.12817 | -0.041199 | 122.6349 | 63.2126 | 61.4136 | 0.064087 | 122.2412 | 122.6212 | 122.3785 | -0.11902 | -0.12817 | 122.2412 | 122.6212 | -0.11902 | 0.064087 | 122.3785 | -122.4335 | -122.5479
320.6719 | 122.731 | -61.2259 | 61.1984 | 0.0045015 | 0.037126 | 0.034812 | -0.0025507 | -0.0091495 | 0.06263 | 0.064448 | 61.4136 | 61.0565 | -61.203 | 61.1984 | -61.1572 | -61.3266 | 2.2064 | 0.23346 | 61.171 | -61.3358 | 0.022888 | -0.14191 | 122.6395 | 122.4243 | -122.3557 | -0.10986 | -0.027466 | 122.6166 | 63.4323 | 61.4594 | 0.068664 | 122.2824 | 122.6395 | 122.3969 | -0.10071 | -0.10986 | 122.2824 | 122.6395 | -0.10071 | 0.068664 | 122.3969 | -122.4014 | -122.5342
321.6719 | 122.731 | -61.2122 | 61.1847 | -0.003128 | 0.037339 | 0.035666 | -0.0027643 | -0.0091495 | 0.065407 | 0.064234 | 61.4182 | 61.0291 | -61.1984 | 61.2167 | -61.1343 | -61.3174 | 2.1835 | 0.23804 | 61.1298 | -61.3403 | 0.013733 | -0.15564 | 122.6303 | 122.4289 | -122.319 | -0.12817 | -0.054931 | 122.6166 | 63.3957 | 61.4502 | 0.07782 | 122.2412 | 122.6303 | 122.3419 | -0.10529 | -0.12817 | 122.2412 | 122.6303 | -0.10529 | 0.07782 | 122.3419 | -122.3831 | -122.525
322.6719 | 122.7219 | -61.1938 | 61.2488 | -0.010758 | 0.037553 | 0.033957 | -0.0042597 | -0.012568 | 0.062416 | 0.061884 | 61.4548 | 61.1069 | -61.1847 | 61.2579 | -61.1069 | -61.2991 | 2.4857 | 0.31128 | 61.2076 | -61.3083 | 0.009156 | -0.14191 | 122.6486 | 122.4518 | -122.3557 | -0.11444 | -0.041198 | 122.6395 | 63.6795 | 61.5051 | 0.086975 | 122.3007 | 122.6486 | 122.4014 | -0.10528 | -0.11444 | 122.3007 | 122.6486 | -0.10528 | 0.086975 | 122.4014 | -122.4335 | -122.5571
323.6719 | 122.7219 | -61.2305 | 61.2076 | -0.003128 | 0.036271 | 0.033103 | -0.0023371 | -0.010859 | 0.063271 | 0.062098 | 61.3998 | 61.0565 | -61.203 | 61.2076 | -61.1435 | -61.3266 | 2.243 | 0.21973 | 61.1755 | -61.3129 | 0.027466 | -0.15106 | 122.6303 | 122.4381 | -122.3511 | -0.082397 | -0.032044 | 122.6028 | 63.4735 | 61.4502 | 0.086975 | 122.287 | 122.6303 | 122.406 | -0.09613 | -0.082397 | 122.287 | 122.6303 | -0.09613 | 0.086975 | 122.406 | -122.4106 | -122.5204
324.6719 | 122.7264 | -61.2442 | 61.2167 | -0.003128 | 0.039903 | 0.033744 | -0.0021235 | -0.0097903 | 0.061776 | 0.064448 | 61.409 | 61.0519 | -61.2076 | 61.203 | -61.1572 | -61.322 | 2.3621 | 0.23804 | 61.1618 | -61.3449 | 0.036621 | -0.16479 | 122.6532 | 122.4472 | -122.374 | -0.10071 | -0.054932 | 122.6166 | 63.6063 | 61.4822 | 0.086975 | 122.2961 | 122.6532 | 122.406 | -0.077819 | -0.10071 | 122.2961 | 122.6532 | -0.077819 | 0.086975 | 122.406 | -122.4243 | -122.5616
325.6719 | 122.7127 | -61.203 | 61.1847 | 0.0045015 | 0.037339 | 0.033317 | -0.0023371 | -0.0072269 | 0.065834 | 0.06338 | 61.4273 | 61.0474 | -61.2167 | 61.2167 | -61.1435 | -61.3174 | 2.5131 | 0.27008 | 61.1755 | -61.3358 | -0.013733 | -0.13733 | 122.6303 | 122.4197 | -122.3282 | -0.13275 | -0.009155 | 122.644 | 63.7161 | 61.4731 | 0.059509 | 122.2504 | 122.6303 | 122.3785 | -0.11444 | -0.13275 | 122.2504 | 122.6303 | -0.11444 | 0.059509 | 122.3785 | -122.4014 | -122.5204
326.6719 | 122.7493 | -61.2076 | 61.1893 | -0.010758 | 0.038194 | 0.036521 | -0.0006281 | -0.011713 | 0.064553 | 0.064448 | 61.4319 | 61.0474 | -61.1893 | 61.235 | -61.1389 | -61.322 | 2.5452 | 0.29755 | 61.1206 | -61.3495 | 0.018311 | -0.14191 | 122.6395 | 122.4426 | -122.3282 | -0.14191 | -0.068665 | 122.6212 | 63.7527 | 61.5051 | 0.068665 | 122.2549 | 122.6395 | 122.3282 | -0.11444 | -0.14191 | 122.2549 | 122.6395 | -0.11444 | 0.068665 | 122.3282 | -122.3785 | -122.5388
327.6719 | 122.7585 | -61.2076 | 61.203 | 0.0045015 | 0.039903 | 0.03588 | 0.0006537 | -0.0091495 | 0.06498 | 0.062525 | 61.441 | 61.0474 | -61.2396 | 61.2259 | -61.1343 | -61.3174 | 2.6184 | 0.30212 | 61.1389 | -61.3266 | -0.032043 | -0.15564 | 122.6486 | 122.4335 | -122.3373 | -0.11902 | -0.064087 | 122.6807 | 63.826 | 61.5097 | 0.073243 | 122.2549 | 122.6486 | 122.3465 | -0.10986 | -0.11902 | 122.2549 | 122.6486 | -0.10986 | 0.073243 | 122.3465 | -122.4426 | -122.5296
328.6719 | 122.7493 | -61.2442 | 61.1984 | -0.010758 | 0.039048 | 0.035239 | 0.0004401 | -0.0087223 | 0.064339 | 0.063166 | 61.3815 | 61.0657 | -61.235 | 61.1801 | -61.171 | -61.3541 | 2.8198 | 0.28381 | 61.1664 | -61.3403 | 0.009156 | -0.13275 | 122.6257 | 122.4243 | -122.3694 | -0.09613 | -0.032043 | 122.6166 | 64.064 | 61.528 | 0.073243 | 122.3099 | 122.6257 | 122.4106 | -0.10986 | -0.09613 | 122.3099 | 122.6257 | -0.10986 | 0.073243 | 122.4106 | -122.4335 | -122.5388
329.6719 | 122.7081 | -61.2167 | 61.2076 | -0.026017 | 0.041825 | 0.033957 | -0.0012689 | -0.0065859 | 0.06498 | 0.062952 | 61.3541 | 61.0977 | -61.2488 | 61.1435 | -61.1893 | -61.3861 | 2.7649 | 0.2243 | 61.1984 | -61.3907 | -0.032043 | -0.10986 | 122.5708 | 122.3602 | -122.3969 | -0.17395 | -0.009156 | 122.6028 | 63.9816 | 61.441 | 0.027466 | 122.3145 | 122.5708 | 122.4152 | -0.16937 | -0.17395 | 122.3145 | 122.5708 | -0.16937 | 0.027466 | 122.4152 | -122.4564 | -122.5983
330.6719 | 121.3715 | -0.10529 | 116.8076 | 0.01213 | 0.028153 | 0.022422 | -0.0034051 | -0.0025271 | -0.0044476 | 0.011469 | 121.8018 | 121.4951 | -0.14648 | 121.3165 | 121.5683 | 0.10529 | 6.6193 | 1.8631 | 121.7056 | -0.17853 | -0.041198 | 4.6875 | 121.907 | 121.4218 | 4.7607 | -0.073242 | 4.8981 | 121.9482 | 6.7245 | 1.9684 | 121.6736 | 121.6003 | 121.907 | 121.8109 | 0.21057 | -0.073242 | 121.6003 | 121.907 | 0.21057 | 121.6736 | 121.8109 | -116.954 | -116.9861
331.6719 | 117.9428 | -91.3513 | 26.1703 | 0.0045015 | 0.023667 | 0.024558 | 6.9321 | 3.6276e-05 | 0.0030292 | 6.9969 | 26.1978 | 25.9094 | -91.658 | 0.70953 | 0.79651 | 0.75989 | -0.54932 | -0.52643 | 17.8116 | -82.9193 | -0.3067 | -0.26093 | 117.5491 | 92.0609 | -25.3738 | 8.432 | -8.3588 | 117.8558 | 90.802 | 90.8249 | 92.1478 | 117.2607 | 117.5491 | 109.1629 | 92.1112 | 8.432 | 117.2607 | 117.5491 | 92.1112 | 92.1478 | 109.1629 | -117.8284 | -109.0897
332.6719 | 117.5491 | -91.4795 | 25.6851 | -0.010758 | 0.025376 | 0.022208 | 6.9321 | 0.0013181 | 0.0049518 | 6.9969 | 25.9094 | 25.6577 | -91.4749 | 0.46234 | 0.67291 | 0.51727 | 0.091553 | -66.5359 | 17.2989 | -83.3771 | 0.004577 | -0.027466 | 117.3889 | 91.9418 | -25.0122 | 8.1024 | -8.3862 | 117.3843 | 91.571 | 24.9435 | 92.1524 | 117.1371 | 117.3889 | 108.7784 | 91.9968 | 8.1024 | 117.1371 | 117.3889 | 91.9968 | 92.1524 | 108.7784 | -117.16 | -109.0622
333.6719 | 98.3139 | -2.2247 | 117.1509 | 0.0045015 | 0.031571 | 0.018363 | 0.12306 | 0.058996 | -0.005943 | 0.20565 | 116.7068 | 116.3452 | -2.9068 | -2.1332 | 116.8716 | 117.2745 | -2.3209 | -2.0554 | 117.1738 | -2.2202 | -0.68207 | -0.80566 | 118.9316 | 0.091552 | -0.27924 | 0.004577 | 0.022888 | 119.6136 | -0.096131 | 0.16937 | 119.0964 | 118.5699 | 118.9316 | 119.3985 | 119.4992 | 0.004577 | 118.5699 | 118.9316 | 119.4992 | 119.0964 | 119.3985 | -120.0577 | -119.371
334.6719 | 120.163 | -1.8951 | 118.4463 | 0.0045015 | 0.027085 | 0.026267 | 0.046796 | 0.059637 | -0.0050884 | 0.12661 | 118.9682 | 118.721 | -1.8539 | -1.6663 | 118.7851 | 119.0826 | -2.0462 | -1.6708 | 118.9362 | -1.8906 | 0.041199 | 0.27466 | 120.8633 | 0.22888 | 0.33875 | 0.004578 | 0.48981 | 120.8221 | -0.15106 | 0.22431 | 120.6802 | 120.6162 | 120.8633 | 120.8313 | 120.9778 | 0.004578 | 120.6162 | 120.8633 | 120.9778 | 120.6802 | 120.8313 | -120.3003 | -120.3369
335.6719 | 99.5544 | -0.46234 | 90.1978 | -0.003128 | 0.029435 | 0.02114 | 0.016035 | 0.060064 | -0.00060245 | 0.095423 | 119.5358 | 119.4809 | -0.48523 | -0.37537 | 119.2841 | 119.6228 | -0.44403 | -0.43945 | 119.6503 | -0.5127 | -0.022888 | 29.2831 | 119.9982 | 0.086975 | 29.0863 | -0.050354 | 29.4525 | 120.0211 | 0.01831 | 0.022888 | 119.7464 | 119.9432 | 119.9982 | 120.1126 | 120.0851 | -0.050354 | 119.9432 | 119.9982 | 120.0851 | 119.7464 | 120.1126 | -90.683 | -90.7104
336.6719 | 113.4796 | -56.4743 | 56.6986 | -0.003128 | 0.026444 | 0.021781 | 6.9321 | 0.0064451 | 0.012642 | 6.9969 | 56.9275 | 56.7169 | -56.5475 | 0.16479 | 0.10071 | 0.17395 | -0.036621 | 0.07782 | 37.5183 | -37.5595 | -0.073242 | 0.018311 | 113.4018 | 56.6391 | -56.5979 | 18.9148 | -19.1803 | 113.475 | 56.4377 | 56.5521 | 56.575 | 113.1912 | 113.4018 | 93.9926 | 56.6483 | 18.9148 | 113.1912 | 113.4018 | 56.6483 | 56.575 | 93.9926 | -113.2462 | -94.2581
337.6719 | 120.3369 | -119.9341 | 0.35706 | -0.003128 | 0.031571 | 0.021567 | 0.025434 | -0.0035953 | -0.0033794 | 0.0052743 | 0.31586 | 0.34332 | -119.9799 | 0.33875 | 0.29755 | 0.36163 | 0.32044 | 0.28839 | 0.3479 | 0.25177 | -0.045776 | -0.013733 | 120.2499 | 120.2728 | -0.05951 | 120.1859 | -0.009156 | 120.2957 | 120.2545 | 120.2225 | 120.2316 | 120.2774 | 120.2499 | 120.282 | 120.2957 | 120.1859 | 120.2774 | 120.2499 | 120.2957 | 120.2316 | 120.282 | -120.3369 | -0.10529
338.6719 | 120.6299 | -120.2545 | 0.1831 | -0.003128 | 0.022599 | 0.021354 | 0.014539 | -0.0033817 | -0.0020978 | 0.0052743 | 0.21057 | 0.13275 | -120.2454 | 0.29755 | 0.2655 | 0.35248 | 0.022888 | 0.31128 | 0.15564 | 0.15106 | 0.009156 | -0.050354 | 120.4651 | 120.5521 | 0.082398 | 120.4056 | -0.027465 | 120.4559 | 120.2774 | 120.5658 | 120.52 | 120.3873 | 120.4651 | 120.4102 | 120.607 | 120.4056 | 120.3873 | 120.4651 | 120.607 | 120.52 | 120.4102 | -120.4285 | -0.032043
339.6719 | 120.5978 | -120.3094 | 0.19684 | -0.010758 | 0.03029 | 0.024772 | 0.026716 | -0.0046633 | -0.0010296 | 0.0035653 | 0.19684 | 0.16022 | -120.2957 | 0.2243 | 0.16022 | 0.23346 | 0.07782 | 0.16022 | 0.14648 | 0.09613 | 0.013733 | -0.036621 | 120.5063 | 120.5338 | -0.036621 | 120.4056 | -0.050354 | 120.4926 | 120.3873 | 120.4697 | 120.4697 | 120.4697 | 120.5063 | 120.4559 | 120.5429 | 120.4056 | 120.4697 | 120.5063 | 120.5429 | 120.4697 | 120.4559 | -120.4926 | -0.10071
340.6719 | 120.6162 | -120.3186 | 0.23804 | -0.010758 | 0.028367 | 0.023063 | 0.024793 | -0.0046633 | -0.0029522 | 0.0054879 | 0.22888 | 0.20599 | -120.3186 | 0.24719 | 0.19684 | 0.25635 | 0.15106 | 0.19684 | 0.20142 | 0.1236 | 0 | -0.032043 | 120.5475 | 120.5658 | -0.041199 | 120.4422 | -0.036621 | 120.5475 | 120.4697 | 120.5154 | 120.5154 | 120.5246 | 120.5475 | 120.52 | 120.575 | 120.4422 | 120.5246 | 120.5475 | 120.575 | 120.5154 | 120.52 | -120.5566 | -0.11444
341.6562 | 120.6482 | -120.3186 | 0.27008 | -0.010758 | 0.030076 | 0.02349 | 0.023725 | -0.0050907 | -0.0014568 | 0.0031381 | 0.21973 | 0.22888 | -120.2957 | 0.25635 | 0.20599 | 0.27466 | 0.17853 | 0.20142 | 0.21973 | 0.15564 | 0.022889 | -0.041199 | 120.5383 | 120.575 | -0.064087 | 120.4742 | -0.050354 | 120.5154 | 120.4971 | 120.52 | 120.5246 | 120.5475 | 120.5383 | 120.5383 | 120.5933 | 120.4742 | 120.5475 | 120.5383 | 120.5933 | 120.5246 | 120.5383 | -120.5658 | -0.11444
342.6562 | 120.7169 | -120.3461 | 0.29755 | -0.010758 | 0.030503 | 0.020499 | 0.017744 | -0.0057315 | -0.002525 | 0.0044199 | 0.21515 | 0.26093 | -120.3644 | 0.27466 | 0.24719 | 0.31586 | 0.22888 | 0.24719 | 0.24261 | 0.16479 | -0.018311 | -0.036621 | 120.5612 | 120.6207 | -0.050354 | 120.5109 | -0.054931 | 120.5795 | 120.575 | 120.5933 | 120.5933 | 120.607 | 120.5612 | 120.5887 | 120.6619 | 120.5109 | 120.607 | 120.5612 | 120.6619 | 120.5933 | 120.5887 | -120.6619 | -0.13275
343.6719 | 120.7535 | -120.3735 | 0.27466 | -0.003128 | 0.031999 | 0.020499 | 0.020307 | -0.0063723 | -0.0055156 | 0.0022837 | 0.21973 | 0.21973 | -120.3964 | 0.26093 | 0.23804 | 0.30212 | 0.21973 | 0.24261 | 0.2243 | 0.16937 | -0.022888 | -0.054931 | 120.5933 | 120.6345 | -0.036621 | 120.5429 | -0.050354 | 120.6162 | 120.5933 | 120.6162 | 120.6116 | 120.5933 | 120.5933 | 120.5978 | 120.6757 | 120.5429 | 120.5933 | 120.5933 | 120.6757 | 120.6116 | 120.5978 | -120.6711 | -0.10529
344.6719 | 120.7993 | -120.4102 | 0.2655 | -0.010758 | 0.029862 | 0.023917 | 0.01988 | -0.0044497 | -0.0050884 | 0.0031381 | 0.21515 | 0.22888 | -120.4193 | 0.28381 | 0.25635 | 0.32501 | 0.18768 | 0.2655 | 0.21057 | 0.16022 | -0.009156 | -0.036621 | 120.6253 | 120.694 | -0.009155 | 120.5704 | -0.054932 | 120.6345 | 120.5978 | 120.6757 | 120.6665 | 120.639 | 120.6253 | 120.6207 | 120.7352 | 120.5704 | 120.639 | 120.6253 | 120.7352 | 120.6665 | 120.6207 | -120.6848 | -0.10529
345.6719 | 120.7764 | -120.433 | 0.28381 | -0.003128 | 0.028581 | 0.021781 | 0.018812 | -0.0063723 | -0.0038068 | 0.0037791 | 0.21515 | 0.24261 | -120.3964 | 0.26093 | 0.23804 | 0.29755 | 0.22888 | 0.23804 | 0.23346 | 0.16479 | 0.036621 | -0.041198 | 120.6482 | 120.694 | -0.045776 | 120.5978 | -0.050354 | 120.6116 | 120.6619 | 120.6711 | 120.6711 | 120.6757 | 120.6482 | 120.6665 | 120.7306 | 120.5978 | 120.6757 | 120.6482 | 120.7306 | 120.6711 | 120.6665 | -120.6802 | -0.11902
346.6562 | 120.845 | -120.433 | 0.29755 | -0.003128 | 0.029008 | 0.022208 | 0.020948 | -0.0055179 | -0.0029522 | 0.0057017 | 0.25635 | 0.23804 | -120.4102 | 0.32501 | 0.28381 | 0.3479 | 0.20142 | 0.30212 | 0.24261 | 0.20599 | 0.022888 | -0.059509 | 120.6894 | 120.7581 | -0.013733 | 120.639 | -0.054931 | 120.6665 | 120.6345 | 120.7352 | 120.7169 | 120.6711 | 120.6894 | 120.6757 | 120.7809 | 120.639 | 120.6711 | 120.6894 | 120.7809 | 120.7169 | 120.6757 | -120.7077 | -0.091552
347.6562 | 120.845 | -120.4697 | 0.28839 | -0.010758 | 0.028581 | 0.021567 | 0.01988 | -0.0061587 | -0.0040204 | 0.0037791 | 0.23346 | 0.25635 | -120.4468 | 0.29297 | 0.24719 | 0.32501 | 0.2655 | 0.2655 | 0.26093 | 0.21515 | 0.022889 | -0.032043 | 120.7031 | 120.7626 | -0.041199 | 120.6848 | -0.027466 | 120.6802 | 120.7352 | 120.7352 | 120.7169 | 120.726 | 120.7031 | 120.7306 | 120.7947 | 120.6848 | 120.726 | 120.7031 | 120.7947 | 120.7169 | 120.7306 | -120.7352 | -0.073242
348.6562 | 120.8313 | -120.52 | 0.27466 | -0.003128 | 0.02559 | 0.018577 | 0.018812 | -0.0053043 | -0.005302 | 0.0029245 | 0.19226 | 0.22888 | -120.488 | 0.24719 | 0.23804 | 0.30212 | 0.2655 | 0.24261 | 0.24261 | 0.18768 | 0.032044 | -0.045776 | 120.7123 | 120.7672 | -0.036621 | 120.7077 | -0.032043 | 120.6802 | 120.7855 | 120.7626 | 120.7581 | 120.7489 | 120.7123 | 120.7626 | 120.8221 | 120.7077 | 120.7489 | 120.7123 | 120.8221 | 120.7581 | 120.7626 | -120.7626 | -0.086975
349.6562 | 120.9869 | -120.4971 | 0.26093 | -0.003128 | 0.024308 | 0.024344 | 0.015394 | -0.0061587 | -0.0050884 | 0.0037791 | 0.3067 | 0.19226 | -120.4422 | 0.3891 | 0.3479 | 0.43945 | 0.091553 | 0.41657 | 0.20599 | 0.23346 | 0.054931 | -0.068664 | 120.8038 | 120.8862 | 0.086975 | 120.7306 | -0.054931 | 120.7489 | 120.5887 | 120.9137 | 120.845 | 120.6894 | 120.8038 | 120.7031 | 120.9366 | 120.7306 | 120.6894 | 120.8038 | 120.9366 | 120.845 | 120.7031 | -120.7031 | -0.027466
350.6562 | 121.0144 | -120.5429 | 0.24719 | -0.003128 | 0.022599 | 0.020286 | 0.017957 | -0.0059451 | -0.0046612 | 0.0046335 | 0.31586 | 0.17853 | -120.4376 | 0.37079 | 0.35248 | 0.45319 | 0.050354 | 0.40283 | 0.20142 | 0.23346 | 0.10529 | -0.068664 | 120.8588 | 120.9137 | 0.10529 | 120.7764 | -0.045776 | 120.7535 | 120.5933 | 120.9457 | 120.8954 | 120.7214 | 120.8588 | 120.7443 | 120.9961 | 120.7764 | 120.7214 | 120.8588 | 120.9961 | 120.8954 | 120.7443 | -120.6848 | -0.013733
351.6719 | 121.0052 | -120.5704 | 0.23804 | -0.003128 | 0.022172 | 0.021781 | 0.019025 | -0.0085085 | -0.0085064 | 0.0029245 | 0.30212 | 0.1831 | -120.4742 | 0.37994 | 0.33875 | 0.41657 | 0.064087 | 0.3891 | 0.17395 | 0.20599 | 0.096131 | -0.054932 | 120.8725 | 120.9503 | 0.10071 | 120.7764 | -0.064087 | 120.7764 | 120.6345 | 120.9595 | 120.9091 | 120.7535 | 120.8725 | 120.7443 | 120.9869 | 120.7764 | 120.7535 | 120.8725 | 120.9869 | 120.9091 | 120.7443 | -120.7123 | -0.032043
352.6719 | 121.0419 | -120.575 | 0.23804 | -0.010758 | 0.021318 | 0.020713 | 0.019239 | -0.0097903 | -0.0063702 | 0.0020701 | 0.31128 | 0.16022 | -120.5475 | 0.37537 | 0.32959 | 0.40741 | 0.045776 | 0.38452 | 0.17395 | 0.19684 | 0.027466 | -0.07782 | 120.8862 | 120.9503 | 0.091553 | 120.7718 | -0.064087 | 120.8588 | 120.6207 | 120.9595 | 120.9045 | 120.7352 | 120.8862 | 120.7489 | 120.9824 | 120.7718 | 120.7352 | 120.8862 | 120.9824 | 120.9045 | 120.7489 | -120.7855 | -0.041199
353.6562 | 121.0281 | -120.5612 | 0.22888 | 0.0045015 | -0.012008 | -0.019876 | 0.018598 | -0.010004 | -0.007011 | 0.0042063 | -66.7969 | -9.3063 | -120.52 | 0.36621 | 0.30212 | 0.3891 | 0.068665 | 0.36163 | 0.16937 | 0.19684 | 0.041198 | -9.5352 | 53.7643 | 120.9274 | 0.073242 | 120.7581 | -0.059509 | 53.7231 | 120.6299 | 120.9229 | 120.8633 | 111.2549 | 53.7643 | 120.7306 | 120.9503 | 120.7581 | 111.2549 | 53.7643 | 120.9503 | 120.8633 | 120.7306 | -120.7489 | -0.032044
354.6562 | 121.0373 | -120.5933 | 0.22888 | 0.0045015 | -0.012862 | -0.014321 | 0.018812 | -0.0078677 | -0.0057294 | 0.0033517 | -120.4788 | -9.3201 | -120.5612 | 0.37079 | 0.33417 | 0.42114 | 0.045776 | 0.39368 | 0.17395 | 0.20142 | 0.032044 | -9.5489 | 0.11444 | 120.9641 | 0.10528 | 120.7947 | -0.054932 | 0.082397 | 120.639 | 120.9869 | 120.9274 | 111.2732 | 0.11444 | 120.7672 | 121.0144 | 120.7947 | 111.2732 | 0.11444 | 121.0144 | 120.9274 | 120.7672 | -120.7901 | -0.027466
355.6562 | 121.1014 | -120.6116 | 0.23804 | -0.003128 | -0.011367 | -0.014321 | 0.020521 | -0.0091495 | -0.0038068 | 0.0033517 | -120.4834 | -9.3201 | -120.5521 | 0.40741 | 0.36163 | 0.44403 | 0.022888 | 0.39825 | 0.20599 | 0.2243 | 0.059509 | -9.5581 | 0.12817 | 121.019 | 0.1236 | 120.8359 | -0.032043 | 0.068665 | 120.6345 | 121.0098 | 120.9732 | 111.2915 | 0.12817 | 120.8176 | 121.0556 | 120.8359 | 111.2915 | 0.12817 | 121.0556 | 120.9732 | 120.8176 | -120.7901 | -0.013733
356.6562 | 121.0236 | -120.6116 | 0.25635 | -0.003128 | -0.01094 | -0.017526 | 0.018171 | -0.0091495 | -0.0055156 | 0.0039927 | -120.5338 | -9.343 | -120.5612 | 0.3479 | 0.29297 | 0.3891 | 0.086975 | 0.32044 | 0.20142 | 0.2243 | 0.050354 | -9.5993 | 0.07782 | 120.9595 | 0.036621 | 120.8359 | -0.054932 | 0.027466 | 120.6985 | 120.932 | 120.9045 | 111.2686 | 0.07782 | 120.813 | 121.0007 | 120.8359 | 111.2686 | 0.07782 | 121.0007 | 120.9045 | 120.813 | -120.8176 | -0.032044
357.6719 | 121.0419 | -120.5887 | 0.29755 | -0.003128 | -0.011367 | -0.016244 | 0.018384 | -0.0093631 | -0.0033794 | 0.0016427 | -120.52 | -9.3338 | -120.5338 | 0.37994 | 0.32501 | 0.41657 | 0.1236 | 0.3479 | 0.24719 | 0.25635 | 0.054932 | -9.6313 | 0.068664 | 120.9686 | 0.027466 | 120.845 | -0.050354 | 0.013732 | 120.7123 | 120.9366 | 120.9137 | 111.2549 | 0.068664 | 120.8359 | 121.0052 | 120.845 | 111.2549 | 0.068664 | 121.0052 | 120.9137 | 120.8359 | -120.8313 | -0.041198
358.6719 | 121.0327 | -120.5933 | 0.31586 | -0.003128 | -0.012221 | -0.019448 | 0.020734 | -0.0089359 | -0.0027386 | 0.0037791 | -120.5154 | -9.3201 | -120.5292 | 0.38452 | 0.32044 | 0.42114 | 0.14648 | 0.35248 | 0.25177 | 0.2655 | 0.064087 | -9.6359 | 0.07782 | 120.9778 | 0.004578 | 120.8588 | -0.064087 | 0.013733 | 120.7397 | 120.9457 | 120.9137 | 111.2732 | 0.07782 | 120.845 | 121.0144 | 120.8588 | 111.2732 | 0.07782 | 121.0144 | 120.9137 | 120.845 | -120.845 | -0.050354
359.6719 | 121.0602 | -120.5795 | 0.27924 | -0.010758 | -0.012008 | -0.013253 | 0.021802 | -0.012354 | -0.0046612 | 0.0027109 | -120.5383 | -9.3384 | -120.5566 | 0.38452 | 0.32501 | 0.42572 | 0.10529 | 0.3479 | 0.21973 | 0.25635 | 0.022888 | -9.6176 | 0.041199 | 120.9641 | 0.045776 | 120.8359 | -0.059509 | 0.018311 | 120.6848 | 120.9274 | 120.9045 | 111.2411 | 0.041199 | 120.7993 | 121.0052 | 120.8359 | 111.2411 | 0.041199 | 121.0052 | 120.9045 | 120.7993 | -120.8359 | -0.022888
360.6562 | 121.0648 | -120.5887 | 0.3067 | -0.003128 | -0.011153 | -0.014535 | 0.020521 | -0.0097903 | -0.004234 | 0.0031381 | -120.5704 | -9.3292 | -120.5658 | 0.36163 | 0.31128 | 0.41199 | 0.13275 | 0.34332 | 0.24261 | 0.24261 | 0.022888 | -9.6359 | 0.01831 | 120.9503 | 0.004577 | 120.8313 | -0.064087 | -0.004578 | 120.7214 | 120.932 | 120.9 | 111.2595 | 0.01831 | 120.8313 | 121.0007 | 120.8313 | 111.2595 | 0.01831 | 121.0007 | 120.9 | 120.8313 | -120.8725 | -0.064087
361.6562 | 121.0785 | -120.5704 | 0.29297 | -0.026017 | -0.012649 | -0.016244 | 0.022016 | -0.0097903 | -0.0040204 | 0.0024973 | -120.5658 | -9.3292 | -120.5704 | 0.36163 | 0.30212 | 0.39368 | 0.11902 | 0.34332 | 0.24719 | 0.23346 | 0 | -9.6222 | 0.004578 | 120.932 | 0.009155 | 120.8038 | -0.045777 | 0.004578 | 120.6894 | 120.9137 | 120.8725 | 111.2412 | 0.004578 | 120.8176 | 120.9641 | 120.8038 | 111.2412 | 0.004578 | 120.9641 | 120.8725 | 120.8176 | -120.8633 | -0.05951
362.6562 | 121.1014 | -120.6116 | 0.27924 | 0.0045015 | -0.010726 | -0.019662 | 0.021802 | -0.0091495 | -0.005302 | 0.0014291 | -120.5658 | -9.3384 | -120.5795 | 0.38452 | 0.32501 | 0.41199 | 0.086975 | 0.3479 | 0.21515 | 0.25635 | 0.032043 | -9.6176 | 0.045776 | 120.9961 | 0.045776 | 120.8679 | -0.064087 | 0.013733 | 120.6985 | 120.9595 | 120.9366 | 111.2732 | 0.045776 | 120.8267 | 121.0236 | 120.8679 | 111.2732 | 0.045776 | 121.0236 | 120.9366 | 120.8267 | -120.8588 | -0.022888
363.6562 | 121.0785 | -120.6436 | 0.29297 | -0.003128 | -0.0051719 | -0.013467 | 0.025861 | -0.0082949 | -0.0055156 | 0.0020701 | -120.6253 | -9.3246 | -120.6253 | 0.32501 | 0.2655 | 0.35248 | 0.15106 | 0.27008 | 0.24261 | 0.21515 | 0.018311 | -9.6176 | 0.018311 | 120.9686 | -0.027466 | 120.8588 | -0.050354 | 0 | 120.7947 | 120.9137 | 120.9091 | 111.319 | 0.018311 | 120.8862 | 120.9961 | 120.8588 | 111.319 | 0.018311 | 120.9961 | 120.9091 | 120.8862 | -120.9183 | -0.07782
364.6719 | 121.1197 | -120.6436 | 0.27924 | -0.018387 | -0.0079489 | -0.015389 | 0.024152 | -0.0067995 | -0.0033794 | 0.0010019 | -120.6162 | -9.3246 | -120.6345 | 0.36163 | 0.3067 | 0.39368 | 0.091553 | 0.32501 | 0.21515 | 0.22888 | 0.009156 | -9.6039 | 0.027466 | 121.0052 | 0.027466 | 120.8725 | -0.064087 | 0.01831 | 120.7352 | 120.9686 | 120.9503 | 111.319 | 0.027466 | 120.8588 | 121.0373 | 120.8725 | 111.319 | 0.027466 | 121.0373 | 120.9503 | 120.8588 | -120.9137 | -0.050354
365.6719 | 121.1792 | -120.6207 | 0.2655 | -0.010758 | -0.0077353 | -0.01603 | 0.021589 | -0.0065859 | -0.0038068 | 0.0031381 | -120.5841 | -9.3292 | -120.6299 | 0.41199 | 0.35248 | 0.4303 | 0.050354 | 0.34332 | 0.18768 | 0.25177 | -0.009155 | -9.5947 | 0.036622 | 121.0327 | 0.086975 | 120.8725 | -0.07782 | 0.045777 | 120.6711 | 120.9641 | 120.9732 | 111.2915 | 0.036622 | 120.8084 | 121.051 | 120.8725 | 111.2915 | 0.036622 | 121.051 | 120.9732 | 120.8084 | -120.8954 | -0.013733
366.6719 | 121.1517 | -120.6345 | 0.24719 | -0.003128 | -0.0073081 | -0.01368 | 0.023084 | -0.0067995 | -0.0014568 | 0.0031381 | -120.6619 | -9.3246 | -120.6528 | 0.36163 | 0.31128 | 0.3891 | 0.082397 | 0.3067 | 0.20599 | 0.21973 | -0.018311 | -9.5718 | -0.027466 | 120.9961 | 0.064087 | 120.8542 | -0.041198 | -0.009155 | 120.7169 | 120.9412 | 120.9457 | 111.3098 | -0.027466 | 120.8405 | 121.0236 | 120.8542 | 111.3098 | -0.027466 | 121.0236 | 120.9457 | 120.8405 | -120.9 | -0.027465
367.6719 | 121.1838 | -120.6482 | 0.24261 | 0.0045015 | -0.0096579 | -0.011758 | 0.019666 | -0.0050907 | -0.0020978 | 0.0039927 | -120.6116 | -9.3246 | -120.694 | 0.3891 | 0.33417 | 0.43945 | 0.013733 | 0.3479 | 0.18768 | 0.23804 | -0.045777 | -9.5673 | 0.036621 | 121.0373 | 0.091552 | 120.8862 | -0.054932 | 0.082398 | 120.6619 | 120.9961 | 120.9824 | 111.3235 | 0.036621 | 120.8359 | 121.0876 | 120.8862 | 111.3235 | 0.036621 | 121.0876 | 120.9824 | 120.8359 | -120.9366 | -0.004578
368.6719 | 121.1792 | -120.6757 | 0.27008 | -0.010758 | -0.0073081 | -0.01304 | 0.022871 | -0.0059451 | -0.002525 | 0.0037791 | -120.6436 | -9.3292 | -120.7031 | 0.37537 | 0.31128 | 0.40741 | 0.041199 | 0.33417 | 0.19226 | 0.23346 | -0.027466 | -9.5993 | 0.032043 | 121.051 | 0.041198 | 120.9091 | -0.07782 | 0.059509 | 120.7169 | 121.0098 | 120.9869 | 111.3464 | 0.032043 | 120.8679 | 121.0831 | 120.9091 | 111.3464 | 0.032043 | 121.0831 | 120.9869 | 120.8679 | -120.9732 | -0.036622
369.6719 | 121.1884 | -120.6711 | 0.26093 | -0.003128 | -0.0073081 | -0.011758 | 0.021375 | -0.0059451 | -0.0023114 | 0.0054879 | -120.6848 | -9.3292 | -120.7123 | 0.33875 | 0.29297 | 0.37079 | 0.07782 | 0.30212 | 0.21057 | 0.22888 | -0.041198 | -9.5901 | -0.013732 | 121.0098 | 0.032044 | 120.9 | -0.050354 | 0.027466 | 120.7489 | 120.9732 | 120.9641 | 111.3419 | -0.013732 | 120.8817 | 121.0419 | 120.9 | 111.3419 | -0.013732 | 121.0419 | 120.9641 | 120.8817 | -120.9732 | -0.032043
370.6719 | 121.0831 | -120.7031 | 0.28839 | -0.010758 | -0.0053855 | -0.012826 | 0.023511 | -0.0063723 | -0.0014568 | 0.0033517 | -120.7489 | -9.3338 | -120.7443 | 0.27008 | 0.21973 | 0.30212 | 0.18768 | 0.20599 | 0.23804 | 0.18768 | -0.041199 | -9.6222 | -0.045776 | 120.9732 | -0.068664 | 120.8908 | -0.050354 | -0.004577 | 120.8908 | 120.9091 | 120.9229 | 111.3693 | -0.045776 | 120.9412 | 121.0052 | 120.8908 | 111.3693 | -0.045776 | 121.0052 | 120.9229 | 120.9412 | -121.0327 | -0.10071
371.6719 | 121.1334 | -120.7352 | 0.27008 | -0.003128 | -0.0079489 | -0.016244 | 0.020948 | -0.0048769 | -0.0046612 | 0.00078828 | -120.7489 | -9.3246 | -120.7718 | 0.27008 | 0.22888 | 0.31128 | 0.15564 | 0.22888 | 0.21973 | 0.19226 | -0.036622 | -9.5947 | -0.013733 | 121.0052 | -0.041199 | 120.9274 | -0.050354 | 0.022889 | 120.8908 | 120.9641 | 120.9641 | 111.4105 | -0.013733 | 120.9549 | 121.0464 | 120.9274 | 111.4105 | -0.013733 | 121.0464 | 120.9641 | 120.9549 | -121.0419 | -0.07782
372.6719 | 121.2021 | -120.7077 | 0.23346 | -0.003128 | -0.0045309 | -0.019021 | 0.022871 | -0.0048769 | -0.0020978 | 0.0024973 | -120.7306 | -9.3338 | -120.7581 | 0.32959 | 0.29755 | 0.36621 | 0.068665 | 0.28381 | 0.19226 | 0.17853 | -0.050354 | -9.5673 | -0.022888 | 121.0373 | 0.064087 | 120.8862 | -0.041198 | 0.027466 | 120.7764 | 120.9915 | 121.0052 | 111.3739 | -0.022888 | 120.9 | 121.0739 | 120.8862 | 111.3739 | -0.022888 | 121.0739 | 121.0052 | 120.9 | -120.9915 | -0.054931
373.6719 | 121.1609 | -120.7397 | 0.26093 | -0.010758 | -0.0075217 | -0.013253 | 0.023084 | -0.0057315 | -0.0031658 | 0.0033517 | -120.7489 | -9.3338 | -120.7672 | 0.28839 | 0.25635 | 0.33875 | 0.09613 | 0.24261 | 0.21515 | 0.20142 | -0.027466 | -9.5947 | -0.009155 | 121.0281 | -0.004577 | 120.9412 | -0.045776 | 0.018311 | 120.8359 | 120.9824 | 120.9961 | 111.4059 | -0.009155 | 120.9549 | 121.0785 | 120.9412 | 111.4059 | -0.009155 | 121.0785 | 120.9961 | 120.9549 | -121.0281 | -0.059509
374.6719 | 121.1563 | -120.7306 | 0.27466 | -0.010758 | -0.0045309 | -0.014321 | 0.022657 | -0.0048769 | -0.0040204 | 0.0059153 | -120.7718 | -9.3338 | -120.7581 | 0.2655 | 0.23346 | 0.32501 | 0.15564 | 0.24719 | 0.21973 | 0.19226 | -0.027466 | -9.6085 | -0.041199 | 120.9961 | -0.041199 | 120.9229 | -0.054931 | -0.013733 | 120.8862 | 120.9778 | 120.9641 | 111.3968 | -0.041199 | 120.9503 | 121.0556 | 120.9229 | 111.3968 | -0.041199 | 121.0556 | 120.9641 | 120.9503 | -121.0327 | -0.082397
375.6719 | 121.1288 | -120.7581 | 0.27008 | -0.003128 | -0.0049583 | -0.014962 | 0.020521 | -0.0053043 | -0.0029522 | 0.0057017 | -120.8038 | -9.3292 | -120.7764 | 0.25635 | 0.22888 | 0.31128 | 0.17395 | 0.21515 | 0.21515 | 0.16937 | -0.01831 | -9.5993 | -0.045776 | 121.0144 | -0.041199 | 120.9274 | -0.054932 | -0.027466 | 120.932 | 120.9732 | 120.9869 | 111.4288 | -0.045776 | 120.9732 | 121.0693 | 120.9274 | 111.4288 | -0.045776 | 121.0693 | 120.9869 | 120.9732 | -121.0464 | -0.10071
376.6719 | 121.1563 | -120.7672 | 0.2655 | -0.003128 | -0.0058127 | -0.012399 | 0.021375 | -0.0061587 | -0.0023114 | 0.0035653 | -120.8313 | -9.3292 | -120.7855 | 0.22888 | 0.19684 | 0.29297 | 0.1831 | 0.19684 | 0.21973 | 0.15564 | -0.01831 | -9.5947 | -0.064087 | 120.9961 | -0.068665 | 120.9229 | -0.045776 | -0.045777 | 120.9503 | 120.9641 | 120.9641 | 111.438 | -0.064087 | 120.9869 | 121.0602 | 120.9229 | 111.438 | -0.064087 | 121.0602 | 120.9641 | 120.9869 | -121.051 | -0.10986
377.6719 | 121.1334 | -120.7764 | 0.28381 | -0.018387 | -0.0045309 | -0.011758 | 0.024366 | -0.0059451 | -0.0027386 | 0.0033517 | -120.813 | -9.3292 | -120.8038 | 0.2243 | 0.20599 | 0.27924 | 0.23346 | 0.19226 | 0.2243 | 0.1831 | -0.027466 | -9.613 | -0.036621 | 121.0007 | -0.077819 | 120.9595 | -0.059509 | -0.009155 | 121.0098 | 120.9686 | 120.9824 | 111.4471 | -0.036621 | 121.0007 | 121.0556 | 120.9595 | 111.4471 | -0.036621 | 121.0556 | 120.9824 | 121.0007 | -121.0876 | -0.10071
378.6719 | 121.1609 | -120.7901 | 0.27466 | -0.003128 | -0.0049583 | -0.016671 | 0.021802 | -0.0072269 | -0.0048748 | 0.0033517 | -120.8176 | -9.3338 | -120.8313 | 0.24719 | 0.21057 | 0.28839 | 0.20599 | 0.19684 | 0.22888 | 0.16022 | -0.041199 | -9.6085 | -0.027466 | 121.0373 | -0.064087 | 120.9503 | -0.045776 | 0.013733 | 120.9961 | 120.9869 | 121.0007 | 111.4563 | -0.027466 | 121.019 | 121.0785 | 120.9503 | 111.4563 | -0.027466 | 121.0785 | 121.0007 | 121.019 | -121.106 | -0.11444
379.6719 | 121.1929 | -120.7764 | 0.26093 | -0.010758 | -0.0070945 | -0.014749 | 0.018598 | -0.0067995 | -0.003593 | 0.0027109 | -120.813 | -9.3292 | -120.8038 | 0.27924 | 0.24719 | 0.34332 | 0.11444 | 0.24719 | 0.2243 | 0.20599 | -0.027466 | -9.5901 | -0.036621 | 121.0556 | -0.013733 | 120.9824 | -0.036621 | -0.009155 | 120.8908 | 121.0236 | 121.0236 | 111.4471 | -0.036621 | 121.0007 | 121.1197 | 120.9824 | 111.4471 | -0.036621 | 121.1197 | 121.0236 | 121.0007 | -121.0648 | -0.054931
380.6719 | 121.2204 | -120.8038 | 0.25177 | -0.003128 | -0.0047447 | -0.014108 | 0.019239 | -0.0080813 | -0.0031658 | 0.0037791 | -120.8267 | -9.3292 | -120.8405 | 0.2655 | 0.23346 | 0.32959 | 0.10529 | 0.23804 | 0.19684 | 0.1831 | -0.036621 | -9.581 | -0.022888 | 121.0693 | -0.018311 | 120.9869 | -0.054932 | 0.013733 | 120.9091 | 121.0419 | 121.0373 | 111.4746 | -0.022888 | 121.0007 | 121.1334 | 120.9869 | 111.4746 | -0.022888 | 121.1334 | 121.0373 | 121.0007 | -121.0922 | -0.068665
381.6719 | 121.225 | -120.7809 | 0.25177 | -0.018387 | -0.0075217 | -0.014321 | 0.021375 | -0.0050907 | -0.0023114 | 0.0018565 | -120.8267 | -9.3338 | -120.8267 | 0.26093 | 0.21515 | 0.32044 | 0.1236 | 0.23346 | 0.20142 | 0.1831 | -0.045776 | -9.5856 | -0.045776 | 121.0419 | -0.036621 | 120.9641 | -0.050354 | 0 | 120.9045 | 121.0144 | 120.9961 | 111.4471 | -0.045776 | 120.9824 | 121.1014 | 120.9641 | 111.4471 | -0.045776 | 121.1014 | 120.9961 | 120.9824 | -121.0785 | -0.068665
382.6719 | 121.2479 | -120.7947 | 0.26093 | -0.003128 | -0.0062399 | -0.014108 | 0.023084 | -0.0061587 | -0.004234 | 0.0024973 | -120.8496 | -9.3338 | -120.845 | 0.25177 | 0.2243 | 0.31586 | 0.1236 | 0.23346 | 0.17853 | 0.17395 | -0.050354 | -9.5947 | -0.054931 | 121.0464 | -0.036621 | 120.9686 | -0.082397 | -0.004577 | 120.9183 | 121.0281 | 121.019 | 111.4609 | -0.054931 | 120.9732 | 121.1105 | 120.9686 | 111.4609 | -0.054931 | 121.1105 | 121.019 | 120.9732 | -121.106 | -0.086975
383.6719 | 121.2479 | -120.8267 | 0.24719 | -0.010758 | -0.0064535 | -0.014535 | 0.022871 | -0.0059451 | -0.0038068 | 0.0054879 | -120.8542 | -9.3292 | -120.8542 | 0.24719 | 0.21973 | 0.31586 | 0.10529 | 0.22888 | 0.20599 | 0.17395 | -0.027466 | -9.5764 | -0.027466 | 121.0739 | -0.027465 | 121.0007 | -0.041198 | 0 | 120.932 | 121.0556 | 121.0464 | 111.4975 | -0.027466 | 121.0327 | 121.1426 | 121.0007 | 111.4975 | -0.027466 | 121.1426 | 121.0464 | 121.0327 | -121.1014 | -0.073242
384.6719 | 121.1929 | -120.8267 | 0.2655 | -0.018387 | -0.0051719 | -0.014108 | 0.021802 | -0.0070133 | -0.004234 | 0.0020701 | -120.8862 | -9.3384 | -120.845 | 0.2243 | 0.20142 | 0.27466 | 0.18768 | 0.17395 | 0.21973 | 0.14191 | -0.018311 | -9.6039 | -0.059509 | 121.051 | -0.064087 | 120.9686 | -0.045776 | -0.041198 | 121.0144 | 121.0007 | 121.0281 | 111.4883 | -0.059509 | 121.0464 | 121.1014 | 120.9686 | 111.4883 | -0.059509 | 121.1014 | 121.0281 | 121.0464 | -121.1105 | -0.1236
385.6719 | 121.2479 | -120.845 | 0.23804 | -0.010758 | -0.0081625 | -0.013894 | 0.019025 | -0.0048769 | -0.0023114 | 0.0020701 | -120.8679 | -9.3338 | -120.8771 | 0.24261 | 0.21057 | 0.31128 | 0.10986 | 0.23346 | 0.1831 | 0.17853 | -0.032043 | -9.5718 | -0.022888 | 121.0876 | -0.027466 | 121.0236 | -0.054932 | 0.009155 | 120.9549 | 121.0785 | 121.0556 | 111.5112 | -0.022888 | 121.0281 | 121.1563 | 121.0236 | 111.5112 | -0.022888 | 121.1563 | 121.0556 | 121.0281 | -121.1151 | -0.059509
386.6719 | 121.3303 | -120.845 | 0.23804 | -0.003128 | -0.0081625 | -0.014321 | 0.020307 | -0.0091495 | -0.004234 | 0.0035653 | -120.7993 | -9.3338 | -120.8267 | 0.34332 | 0.29755 | 0.39368 | 0.013733 | 0.33417 | 0.15106 | 0.20142 | 0.018311 | -9.5718 | 0.045777 | 121.1884 | 0.059509 | 121.0464 | -0.086975 | 0.027466 | 120.8588 | 121.1792 | 121.1426 | 111.5112 | 0.045777 | 120.9961 | 121.2387 | 121.0464 | 111.5112 | 0.045777 | 121.2387 | 121.1426 | 120.9961 | -121.0648 | -0.036621
387.6719 | 121.3531 | -120.8176 | 0.21515 | -0.003128 | -0.010299 | -0.01069 | 0.020307 | -0.0065859 | -0.0038068 | 0.0033517 | -120.7993 | -9.3384 | -120.8496 | 0.33875 | 0.30212 | 0.41657 | 0.004578 | 0.32959 | 0.15564 | 0.19226 | -0.032043 | -9.5535 | 0.018311 | 121.1563 | 0.086975 | 121.0098 | -0.059509 | 0.050354 | 120.8221 | 121.1472 | 121.1197 | 111.4792 | 0.018311 | 120.9732 | 121.2341 | 121.0098 | 111.4792 | 0.018311 | 121.2341 | 121.1197 | 120.9732 | -121.0648 | -0.022888
388.6719 | 121.3669 | -120.8359 | 0.21515 | -0.010758 | -0.010299 | -0.011971 | 0.019025 | -0.0072269 | -0.0020978 | 0.0014291 | -120.7993 | -9.3338 | -120.8496 | 0.34332 | 0.30212 | 0.42114 | 0.009155 | 0.32501 | 0.16937 | 0.20599 | -0.013733 | -9.5489 | 0.036621 | 121.1792 | 0.086975 | 121.0419 | -0.045776 | 0.050354 | 120.845 | 121.1609 | 121.138 | 111.5021 | 0.036621 | 121.0052 | 121.257 | 121.0419 | 111.5021 | 0.036621 | 121.257 | 121.138 | 121.0052 | -121.0648 | -0.009155
389.6562 | 121.3577 | -120.8313 | 0.21973 | -0.003128 | -0.0077353 | -0.017098 | 0.020734 | -0.0074405 | -0.003593 | 0.0010019 | -120.813 | -9.3338 | -120.8359 | 0.34332 | 0.30212 | 0.40741 | -0.022888 | 0.35706 | 0.16937 | 0.18768 | -0.004577 | -9.5535 | 0.018311 | 121.1746 | 0.082397 | 121.019 | -0.050354 | 0.022888 | 120.8084 | 121.1884 | 121.1334 | 111.4975 | 0.018311 | 121.0007 | 121.2387 | 121.019 | 111.4975 | 0.018311 | 121.2387 | 121.1334 | 121.0007 | -121.0556 | -0.032044
390.6719 | 121.3852 | -120.8496 | 0.21973 | -0.010758 | -0.0094443 | -0.015817 | 0.021589 | -0.0070133 | -0.0018842 | 0.0018565 | -120.8267 | -9.3384 | -120.8542 | 0.33875 | 0.3067 | 0.41657 | 0.013733 | 0.32501 | 0.16022 | 0.19684 | -0.004578 | -9.5581 | 0.022888 | 121.1884 | 0.086975 | 121.0464 | -0.05951 | 0.027466 | 120.8633 | 121.1746 | 121.1563 | 111.5112 | 0.022888 | 121.0098 | 121.2662 | 121.0464 | 111.5112 | 0.022888 | 121.2662 | 121.1563 | 121.0098 | -121.0739 | -0.022889
391.6719 | 121.3028 | -120.8817 | 0.22888 | -0.018387 | -0.0045309 | -0.012185 | 0.020734 | -0.0070133 | -0.0031658 | 0.0031381 | -120.9091 | -9.3292 | -120.932 | 0.2655 | 0.21973 | 0.29755 | 0.091553 | 0.23804 | 0.1831 | 0.16937 | -0.050354 | -9.5581 | -0.027466 | 121.1472 | -0.009155 | 121.051 | -0.045777 | 0.022888 | 120.9732 | 121.1197 | 121.1014 | 111.5524 | -0.027466 | 121.0648 | 121.1792 | 121.051 | 111.5524 | -0.027466 | 121.1792 | 121.1014 | 121.0648 | -121.1609 | -0.059509
392.6719 | 121.3852 | -120.8679 | 0.20599 | -0.010758 | -0.011153 | -0.019021 | 0.020307 | -0.0085085 | -0.0055156 | 0.0024973 | -120.845 | -9.3384 | -120.9137 | 0.35248 | 0.3067 | 0.40283 | -0.018311 | 0.32959 | 0.15106 | 0.19684 | -0.045776 | -9.5444 | 0.022888 | 121.2204 | 0.10071 | 121.0648 | -0.054932 | 0.068664 | 120.8496 | 121.1975 | 121.1746 | 111.5295 | 0.022888 | 121.019 | 121.2708 | 121.0648 | 111.5295 | 0.022888 | 121.2708 | 121.1746 | 121.019 | -121.1197 | -0.009156
393.6719 | 121.3806 | -120.8679 | 0.21515 | -0.010758 | -0.0085899 | -0.015817 | 0.019666 | -0.0082949 | -0.0029522 | 0.0016427 | -120.8313 | -9.3384 | -120.9045 | 0.36163 | 0.3067 | 0.3891 | -0.009155 | 0.32501 | 0.15106 | 0.20142 | -0.036621 | -9.5535 | 0.036621 | 121.2296 | 0.091553 | 121.0693 | -0.064087 | 0.073242 | 120.8588 | 121.1929 | 121.1746 | 111.5295 | 0.036621 | 121.019 | 121.257 | 121.0693 | 111.5295 | 0.036621 | 121.257 | 121.1746 | 121.019 | -121.1197 | -0.013733
394.6719 | 121.3852 | -120.8908 | 0.21973 | -0.010758 | -0.01094 | -0.020516 | 0.021162 | -0.0072269 | -0.0031658 | 0.0029245 | -120.8496 | -9.3384 | -120.9091 | 0.34332 | 0.29755 | 0.39825 | -0.009155 | 0.33875 | 0.15564 | 0.19226 | -0.018311 | -9.5581 | 0.041199 | 121.2341 | 0.077819 | 121.0831 | -0.064087 | 0.05951 | 120.8817 | 121.2296 | 121.1884 | 111.5524 | 0.041199 | 121.0464 | 121.2891 | 121.0831 | 111.5524 | 0.041199 | 121.2891 | 121.1884 | 121.0464 | -121.1288 | -0.027466
395.6719 | 121.3898 | -120.9183 | 0.21057 | -0.003128 | -0.010299 | -0.014535 | 0.01988 | -0.0082949 | -0.0046612 | 0.00057468 | -120.8405 | -9.3384 | -120.9137 | 0.37537 | 0.30212 | 0.41199 | -0.013733 | 0.36163 | 0.16022 | 0.21057 | 0.004578 | -9.5489 | 0.07782 | 121.2936 | 0.091553 | 121.1288 | -0.050354 | 0.073242 | 120.9045 | 121.2799 | 121.2204 | 111.5799 | 0.07782 | 121.0785 | 121.3303 | 121.1288 | 111.5799 | 0.07782 | 121.3303 | 121.2204 | 121.0785 | -121.1243 | 0
396.6719 | 121.3943 | -120.932 | 0.17395 | -0.003128 | -0.0090171 | -0.017526 | 0.020307 | -0.0070133 | -0.0040204 | 0.0016427 | -120.8817 | -9.3384 | -120.9412 | 0.31128 | 0.28381 | 0.37537 | -0.059509 | 0.29755 | 0.12817 | 0.17853 | -0.009155 | -9.5123 | 0.050354 | 121.2433 | 0.10986 | 121.1105 | -0.045776 | 0.059509 | 120.8725 | 121.2296 | 121.2158 | 111.5936 | 0.050354 | 121.0602 | 121.3074 | 121.1105 | 111.5936 | 0.050354 | 121.3074 | 121.2158 | 121.0602 | -121.1151 | 0.004578
397.6719 | 121.4127 | -120.9595 | 0.16937 | -0.010758 | -0.0092307 | -0.014535 | 0.02223 | -0.0085085 | -0.0050884 | 0.0018565 | -120.8908 | -9.3338 | -120.9366 | 0.31586 | 0.2655 | 0.37537 | -0.068665 | 0.29297 | 0.12817 | 0.16937 | 0.022889 | -9.5032 | 0.068665 | 121.2753 | 0.09613 | 121.1288 | -0.041199 | 0.045776 | 120.8908 | 121.2524 | 121.225 | 111.6257 | 0.068665 | 121.0876 | 121.3348 | 121.1288 | 111.6257 | 0.068665 | 121.3348 | 121.225 | 121.0876 | -121.106 | 0
398.6719 | 121.4355 | -120.9366 | 0.17395 | 0.0045015 | -0.011153 | -0.011758 | 0.021375 | -0.0070133 | -0.0038068 | 0.0022837 | -120.8954 | -9.3384 | -120.9824 | 0.32044 | 0.27008 | 0.36621 | -0.073242 | 0.29297 | 0.1236 | 0.16937 | -0.045777 | -9.5123 | 0.041198 | 121.257 | 0.096131 | 121.106 | -0.050354 | 0.086975 | 120.8633 | 121.2296 | 121.2067 | 111.5982 | 0.041198 | 121.0602 | 121.3028 | 121.106 | 111.5982 | 0.041198 | 121.3028 | 121.2067 | 121.0602 | -121.1563 | -0.004577
399.6719 | 121.4264 | -120.9412 | 0.17853 | -0.010758 | -0.0083763 | -0.016244 | 0.023084 | -0.0078677 | -0.0040204 | 0.00057468 | -120.932 | -9.3338 | -120.9869 | 0.31128 | 0.27008 | 0.35706 | -0.036621 | 0.28839 | 0.13275 | 0.17395 | -0.045776 | -9.5123 | 0.009155 | 121.2524 | 0.091553 | 121.1151 | -0.045777 | 0.054931 | 120.9045 | 121.2296 | 121.2112 | 111.6074 | 0.009155 | 121.0739 | 121.2982 | 121.1151 | 111.6074 | 0.009155 | 121.2982 | 121.2112 | 121.0739 | -121.1655 | -0.004578
400.6719 | 121.4035 | -120.9641 | 0.16937 | -0.003128 | -0.013717 | -0.013253 | 0.021162 | -0.0093631 | -0.0040204 | 0.0022837 | -120.9229 | -9.343 | -120.9686 | 0.30212 | 0.25635 | 0.35248 | -0.041199 | 0.27924 | 0.11902 | 0.16479 | -0.004578 | -9.5123 | 0.041198 | 121.2662 | 0.086975 | 121.1288 | -0.050354 | 0.045776 | 120.9229 | 121.2433 | 121.2204 | 111.6211 | 0.041198 | 121.0831 | 121.3165 | 121.1288 | 111.6211 | 0.041198 | 121.3165 | 121.2204 | 121.0831 | -121.138 | -0.004578
401.6719 | 121.4355 | -120.9778 | 0.17395 | 0.0045015 | -0.010299 | -0.014749 | 0.023298 | -0.0087223 | -0.0040204 | 0.0012155 | -120.9183 | -9.3338 | -120.9686 | 0.31128 | 0.2655 | 0.36621 | -0.059509 | 0.29297 | 0.1236 | 0.16937 | 0.009155 | -9.5078 | 0.059509 | 121.2891 | 0.091553 | 121.1472 | -0.050354 | 0.050354 | 120.9183 | 121.2708 | 121.2433 | 111.644 | 0.059509 | 121.1014 | 121.344 | 121.1472 | 111.644 | 0.059509 | 121.344 | 121.2433 | 121.1014 | -121.1426 | -0.004577
402.6719 | 121.4401 | -120.9732 | 0.16479 | -0.010758 | -0.0092307 | -0.013467 | 0.021802 | -0.0072269 | -0.0033794 | 0.0027109 | -120.932 | -9.3384 | -120.9915 | 0.29755 | 0.25635 | 0.35706 | -0.032043 | 0.27008 | 0.1236 | 0.15564 | -0.01831 | -9.5032 | 0.041199 | 121.2708 | 0.091553 | 121.1288 | -0.041199 | 0.059509 | 120.9412 | 121.2433 | 121.2296 | 111.6348 | 0.041199 | 121.0968 | 121.3303 | 121.1288 | 111.6348 | 0.041199 | 121.3303 | 121.2296 | 121.0968 | -121.1563 | -0.009155
403.6719 | 121.4447 | -121.0236 | 0.17395 | -0.003128 | -0.013076 | -0.01368 | 0.016462 | -0.011072 | -0.0018842 | 0.0031381 | -121.0052 | -9.343 | -121.0281 | 0.28839 | 0.26093 | 0.3479 | 0.009155 | 0.29297 | 0.1236 | 0.13733 | -0.004577 | -9.5169 | 0.018311 | 121.312 | 0.086975 | 121.1609 | -0.050354 | 0.022888 | 121.0327 | 121.3165 | 121.2845 | 111.6806 | 0.018311 | 121.1472 | 121.3715 | 121.1609 | 111.6806 | 0.018311 | 121.3715 | 121.2845 | 121.1472 | -121.2021 | -0.036621
404.6719 | 121.3303 | -121.0281 | 0.20599 | 0.0045015 | -0.0058127 | -0.015603 | 0.02458 | -0.0072269 | -0.0046612 | 0.0016427 | -121.0648 | -9.343 | -121.0236 | 0.18768 | 0.12817 | 0.21515 | 0.11902 | 0.1236 | 0.15564 | 0.11444 | 0.004577 | -9.549 | -0.036621 | 121.2158 | -0.07782 | 121.1426 | -0.050354 | -0.041198 | 121.1472 | 121.1517 | 121.1563 | 111.6852 | -0.036621 | 121.1838 | 121.2433 | 121.1426 | 111.6852 | -0.036621 | 121.2433 | 121.1563 | 121.1838 | -121.2296 | -0.091553
405.6719 | 121.3028 | -121.0236 | 0.20142 | 0.0045015 | -0.0058127 | -0.017526 | 0.024366 | -0.0063723 | -0.0033794 | 0.0018565 | -121.0693 | -9.3384 | -121.0419 | 0.18768 | 0.12817 | 0.21515 | 0.11902 | 0.1236 | 0.15564 | 0.10071 | -0.01831 | -9.5398 | -0.045776 | 121.2112 | -0.073242 | 121.1243 | -0.045776 | -0.027466 | 121.1426 | 121.1472 | 121.1517 | 111.6852 | -0.045776 | 121.1792 | 121.2387 | 121.1243 | 111.6852 | -0.045776 | 121.2387 | 121.1517 | 121.1792 | -121.2433 | -0.10071
406.6719 | 121.4127 | -120.9961 | 0.15564 | 0.0045015 | -0.0053855 | -0.014535 | 0.023084 | -0.0059451 | -0.003593 | 0.0016427 | -121.0464 | -9.3384 | -121.0556 | 0.23804 | 0.18768 | 0.27008 | 0.018311 | 0.1831 | 0.1236 | 0.12817 | -0.059509 | -9.494 | -0.050354 | 121.2341 | 0.032043 | 121.1243 | -0.032044 | 0.009155 | 121.0144 | 121.1792 | 121.1838 | 111.6577 | -0.050354 | 121.1197 | 121.2662 | 121.1243 | 111.6577 | -0.050354 | 121.2662 | 121.1838 | 121.1197 | -121.2112 | -0.027466
407.6719 | 121.3715 | -121.0373 | 0.19226 | -0.010758 | -0.0064535 | -0.01368 | 0.022871 | -0.0063723 | -0.0027386 | 0.0024973 | -121.0556 | -9.3338 | -121.0739 | 0.19684 | 0.15106 | 0.24719 | 0.082397 | 0.13733 | 0.13275 | 0.11444 | -0.036622 | -9.5261 | -0.018311 | 121.2341 | -0.041199 | 121.1517 | -0.05951 | 0.018311 | 121.1197 | 121.1746 | 121.1884 | 111.7035 | -0.018311 | 121.17 | 121.2845 | 121.1517 | 111.7035 | -0.018311 | 121.2845 | 121.1884 | 121.17 | -121.2662 | -0.07782
408.6719 | 121.4218 | -121.0236 | 0.17395 | -0.003128 | -0.0094443 | -0.015603 | 0.016035 | -0.0085085 | -0.0044476 | 0.0024973 | -121.0327 | -9.343 | -121.0602 | 0.23804 | 0.21057 | 0.3067 | 0.041199 | 0.23804 | 0.11902 | 0.14191 | -0.036621 | -9.5169 | -0.009155 | 121.2616 | 0.036621 | 121.1655 | -0.054931 | 0.027466 | 121.0648 | 121.2616 | 121.2341 | 111.6806 | -0.009155 | 121.1426 | 121.3303 | 121.1655 | 111.6806 | -0.009155 | 121.3303 | 121.2341 | 121.1426 | -121.2341 | -0.032043
409.6719 | 121.3486 | -121.0464 | 0.21515 | -0.003128 | -0.0066673 | -0.015603 | 0.02458 | -0.0072269 | -0.0016704 | 0.00036108 | -121.0968 | -9.3384 | -121.0693 | 0.17853 | 0.14191 | 0.20599 | 0.13733 | 0.13733 | 0.16022 | 0.12817 | -0.022888 | -9.5535 | -0.050354 | 121.225 | -0.073242 | 121.1746 | -0.054932 | -0.027466 | 121.1838 | 121.1838 | 121.1884 | 111.7081 | -0.050354 | 121.2067 | 121.2524 | 121.1746 | 111.7081 | -0.050354 | 121.2524 | 121.1884 | 121.2067 | -121.2845 | -0.086975
410.6719 | 121.3394 | -121.0327 | 0.21057 | -0.010758 | -0.0041037 | -0.011117 | 0.023939 | -0.0065859 | -0.0048748 | 0.0010019 | -121.0739 | -9.343 | -121.0739 | 0.17853 | 0.11902 | 0.20599 | 0.1236 | 0.14648 | 0.15564 | 0.11444 | -0.041199 | -9.5535 | -0.041199 | 121.2112 | -0.091552 | 121.1472 | -0.054931 | 0 | 121.1563 | 121.1792 | 121.1517 | 111.6898 | -0.041199 | 121.1884 | 121.2387 | 121.1472 | 111.6898 | -0.041199 | 121.2387 | 121.1517 | 121.1884 | -121.2845 | -0.09613
411.6719 | 121.3852 | -121.0327 | 0.20142 | -0.010758 | -0.0043173 | -0.014749 | 0.023939 | -0.0038089 | -0.003593 | -6.6324e-05 | -121.0236 | -9.3292 | -121.0693 | 0.24719 | 0.19226 | 0.25177 | 0.082397 | 0.18768 | 0.13275 | 0.1236 | -0.036621 | -9.5306 | 0.009155 | 121.2799 | -0.009155 | 121.1563 | -0.068665 | 0.045776 | 121.1151 | 121.2204 | 121.225 | 111.7035 | 0.009155 | 121.1655 | 121.2845 | 121.1563 | 111.7035 | 0.009155 | 121.2845 | 121.225 | 121.1655 | -121.2708 | -0.07782
412.6719 | 121.4127 | -121.0602 | 0.1831 | -0.010758 | -0.0038901 | -0.012185 | 0.020948 | -0.0076541 | -0.005302 | 0.0016427 | -121.0373 | -9.3338 | -121.0739 | 0.24719 | 0.20142 | 0.28381 | 0.068665 | 0.21057 | 0.13733 | 0.10071 | -0.013733 | -9.5169 | 0.022889 | 121.3074 | 0.018311 | 121.1609 | -0.045776 | 0.036622 | 121.1288 | 121.2708 | 121.2616 | 111.7264 | 0.022889 | 121.1975 | 121.344 | 121.1609 | 111.7264 | 0.022889 | 121.344 | 121.2616 | 121.1975 | -121.257 | -0.082397
413.6719 | 121.4493 | -121.0098 | 0.16479 | -0.010758 | -0.01094 | -0.014962 | 0.016035 | -0.0061587 | -0.0010296 | 0.0027109 | -121.0281 | -9.343 | -121.0922 | 0.27924 | 0.25177 | 0.32959 | -0.050354 | 0.27008 | 0.091553 | 0.15564 | -0.082397 | -9.5078 | -0.01831 | 121.2891 | 0.086975 | 121.1655 | -0.073242 | 0.064087 | 120.9595 | 121.2799 | 121.2616 | 111.6669 | -0.01831 | 121.1014 | 121.3394 | 121.1655 | 111.6669 | -0.01831 | 121.3394 | 121.2616 | 121.1014 | -121.257 | -0.009155
414.6719 | 121.3898 | -121.0831 | 0.19226 | -0.010758 | -0.0060263 | -0.0091943 | 0.023725 | -0.0087223 | -0.0031658 | 0.0027109 | -121.0556 | -9.3292 | -121.0876 | 0.20142 | 0.15106 | 0.22888 | 0.10529 | 0.14648 | 0.14191 | 0.10529 | -0.004577 | -9.5215 | 0.027466 | 121.2845 | -0.041199 | 121.1884 | -0.050354 | 0.032043 | 121.1884 | 121.2296 | 121.2341 | 111.7538 | 0.027466 | 121.225 | 121.312 | 121.1884 | 111.7538 | 0.027466 | 121.312 | 121.2341 | 121.225 | -121.2799 | -0.086975
415.6719 | 121.4081 | -121.0785 | 0.18768 | -0.018387 | -0.0053855 | -0.015176 | 0.022016 | -0.0046633 | -0.0031658 | 0.0024973 | -121.0556 | -9.3338 | -121.1243 | 0.22888 | 0.1831 | 0.26093 | 0.086975 | 0.17853 | 0.14191 | 0.10529 | -0.045777 | -9.5215 | 0.022888 | 121.3074 | -0.004578 | 121.1838 | -0.045776 | 0.068665 | 121.1655 | 121.257 | 121.2616 | 111.7447 | 0.022888 | 121.2204 | 121.3394 | 121.1838 | 111.7447 | 0.022888 | 121.3394 | 121.2616 | 121.2204 | -121.312 | -0.082397
416.6719 | 121.4401 | -121.0785 | 0.16937 | -0.018387 | -0.0047447 | -0.014535 | 0.023939 | -0.0059451 | -0.0046612 | 0.0020701 | -121.0556 | -9.3292 | -121.1105 | 0.23804 | 0.20142 | 0.27466 | 0.068665 | 0.21973 | 0.14191 | 0.10986 | -0.032044 | -9.4986 | 0.022888 | 121.3165 | 0.032043 | 121.1884 | -0.027466 | 0.054932 | 121.1472 | 121.2982 | 121.2799 | 111.7493 | 0.022888 | 121.2204 | 121.3531 | 121.1884 | 111.7493 | 0.022888 | 121.3531 | 121.2799 | 121.2204 | -121.2799 | -0.05951
417.6719 | 121.431 | -121.106 | 0.1831 | -0.003128 | -0.0043173 | -0.011331 | 0.021375 | -0.0055179 | -0.003593 | 0.0012155 | -121.0739 | -9.3338 | -121.1105 | 0.24719 | 0.20599 | 0.2655 | 0.07782 | 0.21515 | 0.13275 | 0.11444 | -0.004578 | -9.5169 | 0.032043 | 121.3531 | 0.022889 | 121.2204 | -0.050354 | 0.036621 | 121.1838 | 121.3211 | 121.312 | 111.7722 | 0.032043 | 121.2387 | 121.3715 | 121.2204 | 111.7722 | 0.032043 | 121.3715 | 121.312 | 121.2387 | -121.2936 | -0.068664
418.6719 | 121.4401 | -121.1288 | 0.17853 | -0.003128 | -0.0075217 | -0.017526 | 0.022657 | -0.0050907 | -0.0044476 | 0.0020701 | -121.0648 | -9.3384 | -121.106 | 0.24719 | 0.21515 | 0.28381 | 0.07782 | 0.2243 | 0.13733 | 0.11902 | 0.022888 | -9.5169 | 0.064087 | 121.376 | 0.036621 | 121.2479 | -0.041199 | 0.041199 | 121.2067 | 121.3531 | 121.344 | 111.7905 | 0.064087 | 121.2662 | 121.4127 | 121.2479 | 111.7905 | 0.064087 | 121.4127 | 121.344 | 121.2662 | -121.2845 | -0.059509
419.6719 | 121.4035 | -121.138 | 0.21057 | 0.0045015 | -0.0055991 | -0.014321 | 0.018384 | -0.0048769 | -0.003593 | 0.0018565 | -121.1426 | -9.3292 | -121.1563 | 0.17853 | 0.14648 | 0.20599 | 0.17395 | 0.15106 | 0.16022 | 0.10071 | -0.018311 | -9.5398 | -0.004578 | 121.3165 | -0.064087 | 121.2387 | -0.050354 | 0.013733 | 121.312 | 121.2891 | 121.2845 | 111.8088 | -0.004578 | 121.2982 | 121.344 | 121.2387 | 111.8088 | -0.004578 | 121.344 | 121.2845 | 121.2982 | -121.3669 | -0.10986
420.6719 | 121.4493 | -121.1243 | 0.19226 | -0.010758 | -0.0051719 | -0.011331 | 0.023511 | -0.0050907 | -0.0044476 | -0.00070712 | -121.0922 | -9.3338 | -121.1151 | 0.23346 | 0.19226 | 0.26093 | 0.09613 | 0.21973 | 0.13733 | 0.11902 | 0.009156 | -9.5261 | 0.032044 | 121.3577 | 0 | 121.2433 | -0.054932 | 0.022888 | 121.2204 | 121.344 | 121.3165 | 111.7905 | 0.032044 | 121.2616 | 121.3852 | 121.2433 | 111.7905 | 0.032044 | 121.3852 | 121.3165 | 121.2616 | -121.3074 | -0.073242
421.6719 | 121.4539 | -121.1472 | 0.19226 | -0.010758 | -0.0062399 | -0.017312 | 0.022016 | -0.0042361 | -0.0029522 | 0.00036108 | -121.1288 | -9.3338 | -121.1792 | 0.19226 | 0.17853 | 0.24261 | 0.14648 | 0.19226 | 0.14648 | 0.1236 | -0.032043 | -9.5261 | 0.018311 | 121.3394 | -0.013733 | 121.2708 | -0.045777 | 0.050354 | 121.2936 | 121.3394 | 121.3257 | 111.8134 | 0.018311 | 121.2936 | 121.3898 | 121.2708 | 111.8134 | 0.018311 | 121.3898 | 121.3257 | 121.2936 | -121.3715 | -0.068665
422.6719 | 121.4172 | -121.2021 | 0.18768 | 0.0045015 | -0.0077353 | -0.013894 | 0.020521 | -0.0061587 | -0.0040204 | -6.6324e-05 | -121.1563 | -9.3338 | -121.1517 | 0.16937 | 0.14191 | 0.22888 | 0.15106 | 0.15564 | 0.14648 | 0.11444 | 0.050354 | -9.5215 | 0.045776 | 121.3715 | -0.045776 | 121.3165 | -0.041199 | -0.004578 | 121.3531 | 121.3577 | 121.344 | 111.8683 | 0.045776 | 121.3486 | 121.431 | 121.3165 | 111.8683 | 0.045776 | 121.431 | 121.344 | 121.3486 | -121.3394 | -0.073242
423.6719 | 121.3989 | -121.1655 | 0.17853 | -0.003128 | -0.0090171 | -0.014321 | 0.019239 | -0.0061587 | -0.004234 | 0.0022837 | -121.1746 | -9.3384 | -121.1746 | 0.16022 | 0.14648 | 0.20142 | 0.17395 | 0.15564 | 0.15564 | 0.10071 | -0.009156 | -9.5169 | -0.009156 | 121.3257 | -0.032044 | 121.2662 | -0.022888 | 0 | 121.3394 | 121.3211 | 121.3119 | 111.8271 | -0.009156 | 121.3211 | 121.3669 | 121.2662 | 111.8271 | -0.009156 | 121.3669 | 121.3119 | 121.3211 | -121.3531 | -0.07782
424.6719 | 121.4081 | -121.1929 | 0.19684 | 0.01213 | -0.0088035 | -0.017312 | 0.01988 | -0.0065859 | -0.0012432 | 0.0033517 | -121.1792 | -9.343 | -121.1929 | 0.17853 | 0.13733 | 0.21973 | 0.19226 | 0.16937 | 0.15106 | 0.09613 | 0 | -9.5398 | 0.013733 | 121.3715 | -0.059509 | 121.2891 | -0.045776 | 0.013733 | 121.3852 | 121.3623 | 121.3303 | 111.85 | 0.013733 | 121.344 | 121.4127 | 121.2891 | 111.85 | 0.013733 | 121.4127 | 121.3303 | 121.344 | -121.3898 | -0.10071
425.6719 | 121.5134 | -121.1472 | 0.20599 | -0.010758 | -0.011153 | -0.017526 | 0.016035 | -0.0085085 | -0.0031658 | 0.0014291 | -121.0831 | -9.3475 | -121.1014 | 0.28381 | 0.26093 | 0.33417 | 0.07782 | 0.29755 | 0.12817 | 0.16022 | 0.045777 | -9.5535 | 0.064087 | 121.431 | 0.054931 | 121.3074 | -0.07782 | 0.01831 | 121.225 | 121.4447 | 121.4081 | 111.7996 | 0.064087 | 121.2753 | 121.4813 | 121.3074 | 111.7996 | 0.064087 | 121.4813 | 121.4081 | 121.2753 | -121.3074 | -0.045777
426.6719 | 121.5454 | -121.1563 | 0.16937 | -0.018387 | -0.010299 | -0.017953 | 0.017957 | -0.0087223 | -0.0040204 | 0.0012155 | -121.0831 | -9.3338 | -121.1517 | 0.30212 | 0.27008 | 0.36621 | 0.009155 | 0.32501 | 0.11902 | 0.15106 | 0.004578 | -9.5032 | 0.073242 | 121.4584 | 0.10071 | 121.3074 | -0.050354 | 0.068664 | 121.1655 | 121.4813 | 121.4264 | 111.8225 | 0.073242 | 121.2753 | 121.5225 | 121.3074 | 111.8225 | 0.073242 | 121.5225 | 121.4264 | 121.2753 | -121.3211 | -0.018311
427.6719 | 121.4401 | -121.2204 | 0.18768 | -0.003128 | -0.010726 | -0.016244 | 0.021589 | -0.0091495 | -0.0046612 | 0.0010019 | -121.1655 | -9.343 | -121.1884 | 0.1831 | 0.16022 | 0.23346 | 0.16022 | 0.17853 | 0.14191 | 0.11444 | 0.032044 | -9.5306 | 0.054932 | 121.4035 | -0.027466 | 121.3348 | -0.045776 | 0.022888 | 121.3806 | 121.3989 | 121.3806 | 111.8774 | 0.054932 | 121.3623 | 121.4539 | 121.3348 | 111.8774 | 0.054932 | 121.4539 | 121.3806 | 121.3623 | -121.376 | -0.073242
428.6719 | 121.4813 | -121.1884 | 0.17395 | -0.003128 | -0.010299 | -0.01368 | 0.019453 | -0.0095767 | -0.007652 | 0.0010019 | -121.1105 | -9.3384 | -121.1746 | 0.25177 | 0.19684 | 0.27008 | 0.10071 | 0.23804 | 0.12817 | 0.1236 | 0.013732 | -9.5123 | 0.077819 | 121.4401 | 0.022888 | 121.312 | -0.045776 | 0.064087 | 121.2891 | 121.4264 | 121.3852 | 111.85 | 0.077819 | 121.3165 | 121.4584 | 121.312 | 111.85 | 0.077819 | 121.4584 | 121.3852 | 121.3165 | -121.3486 | -0.050354
429.6719 | 121.5454 | -121.2067 | 0.16937 | -0.010758 | -0.011153 | -0.019021 | 0.019453 | -0.0093631 | -0.0078656 | 0.0027109 | -121.0876 | -9.343 | -121.1517 | 0.28839 | 0.24261 | 0.31586 | 0.036621 | 0.29755 | 0.11444 | 0.13733 | 0.054932 | -9.5123 | 0.11902 | 121.4951 | 0.073242 | 121.344 | -0.054932 | 0.064087 | 121.2433 | 121.5042 | 121.4493 | 111.8637 | 0.11902 | 121.3211 | 121.5225 | 121.344 | 111.8637 | 0.11902 | 121.5225 | 121.4493 | 121.3211 | -121.3211 | -0.032044
430.6719 | 121.5729 | -121.1792 | 0.16479 | 0.0045015 | -0.012221 | -0.01838 | 0.021162 | -0.0097903 | -0.0038068 | 0.0018565 | -121.0876 | -9.3384 | -121.1563 | 0.32959 | 0.2655 | 0.35248 | -0.013733 | 0.31586 | 0.10986 | 0.15106 | 0.022888 | -9.5032 | 0.091553 | 121.5088 | 0.10071 | 121.3303 | -0.054932 | 0.068665 | 121.1655 | 121.4951 | 121.4447 | 111.8408 | 0.091553 | 121.2891 | 121.5317 | 121.3303 | 111.8408 | 0.091553 | 121.5317 | 121.4447 | 121.2891 | -121.3211 | -0.013733
431.6719 | 121.5775 | -121.2158 | 0.17395 | -0.010758 | -0.012435 | -0.021157 | 0.019025 | -0.010004 | -0.007652 | 0.0029245 | -121.0785 | -9.3475 | -121.138 | 0.32501 | 0.27008 | 0.35706 | -0.022888 | 0.32044 | 0.11444 | 0.14648 | 0.07782 | -9.5215 | 0.13733 | 121.5408 | 0.096131 | 121.3623 | -0.059509 | 0.059509 | 121.1929 | 121.5363 | 121.4859 | 111.8683 | 0.13733 | 121.3303 | 121.5729 | 121.3623 | 111.8683 | 0.13733 | 121.5729 | 121.4859 | 121.3303 | -121.312 | -0.027466
432.6719 | 121.5866 | -121.2067 | 0.16937 | -0.003128 | -0.011794 | -0.017953 | 0.019025 | -0.0095767 | -0.005943 | 0.0016427 | -121.1288 | -9.343 | -121.17 | 0.28381 | 0.23346 | 0.32501 | 0 | 0.30212 | 0.11902 | 0.15564 | 0.036621 | -9.5123 | 0.07782 | 121.4905 | 0.064086 | 121.3623 | -0.050354 | 0.041199 | 121.2067 | 121.5088 | 121.4401 | 111.8637 | 0.07782 | 121.3257 | 121.5317 | 121.3623 | 111.8637 | 0.07782 | 121.5317 | 121.4401 | 121.3257 | -121.3394 | -0.013733
433.6719 | 121.6003 | -121.1884 | 0.16479 | 0.0045015 | -0.013076 | -0.018594 | 0.020307 | -0.011072 | -0.0072246 | 0.0014291 | -121.1105 | -9.3475 | -121.1609 | 0.32044 | 0.26093 | 0.36163 | -0.013733 | 0.32959 | 0.1236 | 0.16479 | 0.027465 | -9.5123 | 0.077819 | 121.5088 | 0.09613 | 121.3531 | -0.041199 | 0.050354 | 121.1746 | 121.5179 | 121.4493 | 111.8408 | 0.077819 | 121.312 | 121.55 | 121.3531 | 111.8408 | 0.077819 | 121.55 | 121.4493 | 121.312 | -121.3257 | 0
434.6719 | 121.6003 | -121.2112 | 0.17395 | -0.003128 | -0.012862 | -0.021371 | 0.021375 | -0.0097903 | -0.0046612 | -0.00070712 | -121.0922 | -9.3521 | -121.17 | 0.32959 | 0.27008 | 0.37537 | -0.050354 | 0.3479 | 0.12817 | 0.16937 | 0.041199 | -9.5261 | 0.11902 | 121.5408 | 0.096131 | 121.3806 | -0.045776 | 0.07782 | 121.1609 | 121.5591 | 121.4813 | 111.8591 | 0.11902 | 121.3394 | 121.5866 | 121.3806 | 111.8591 | 0.11902 | 121.5866 | 121.4813 | 121.3394 | -121.344 | -0.004577
435.6719 | 121.6003 | -121.2158 | 0.14648 | -0.018387 | -0.011794 | -0.016885 | 0.02223 | -0.012781 | -0.0046612 | 0.0010019 | -121.1197 | -9.343 | -121.1746 | 0.31128 | 0.27008 | 0.3479 | -0.009155 | 0.32501 | 0.11902 | 0.14648 | 0.041198 | -9.4894 | 0.09613 | 121.5271 | 0.1236 | 121.3623 | -0.027465 | 0.054932 | 121.2067 | 121.5408 | 121.4859 | 111.8729 | 0.09613 | 121.3348 | 121.5637 | 121.3623 | 111.8729 | 0.09613 | 121.5637 | 121.4859 | 121.3348 | -121.3211 | 0
436.6719 | 121.5729 | -121.2433 | 0.17853 | -0.003128 | -0.013076 | -0.022225 | 0.018598 | -0.010004 | -0.0050884 | 0.00078828 | -121.1472 | -9.3475 | -121.17 | 0.29297 | 0.23804 | 0.31586 | 0.004578 | 0.28381 | 0.10529 | 0.13275 | 0.073242 | -9.5261 | 0.09613 | 121.5363 | 0.059509 | 121.376 | -0.073242 | 0.022888 | 121.2479 | 121.5271 | 121.4813 | 111.8958 | 0.09613 | 121.3486 | 121.5591 | 121.376 | 111.8958 | 0.09613 | 121.5591 | 121.4813 | 121.3486 | -121.3486 | -0.045777
437.6719 | 121.5637 | -121.225 | 0.17395 | -0.003128 | -0.014571 | -0.017526 | 0.020948 | -0.0093631 | -0.0057294 | 0.00078828 | -121.1746 | -9.3384 | -121.1884 | 0.2655 | 0.20599 | 0.3067 | 0.018311 | 0.26093 | 0.12817 | 0.13733 | 0.036622 | -9.5123 | 0.050354 | 121.4905 | 0.032044 | 121.3623 | -0.045776 | 0.013732 | 121.2433 | 121.4859 | 121.431 | 111.8866 | 0.050354 | 121.3531 | 121.5317 | 121.3623 | 111.8866 | 0.050354 | 121.5317 | 121.431 | 121.3531 | -121.3623 | -0.036621
438.6719 | 121.55 | -121.2021 | 0.16937 | 0.0045015 | -0.012862 | -0.018807 | 0.023298 | -0.011286 | -0.004234 | -0.00027992 | -121.1609 | -9.343 | -121.1929 | 0.25177 | 0.21057 | 0.29297 | 0.027466 | 0.23346 | 0.11902 | 0.14191 | 0.009155 | -9.5123 | 0.041198 | 121.4539 | 0.041198 | 121.344 | -0.050354 | 0.032043 | 121.2296 | 121.4355 | 121.4127 | 111.8591 | 0.041198 | 121.3211 | 121.4951 | 121.344 | 111.8591 | 0.041198 | 121.4951 | 121.4127 | 121.3211 | -121.3623 | -0.027466
439.6719 | 121.5683 | -121.2067 | 0.16479 | -0.003128 | -0.01158 | -0.01838 | 0.022657 | -0.010859 | -0.0038068 | 0.0018565 | -121.1197 | -9.3521 | -121.1975 | 0.31128 | 0.25177 | 0.33875 | -0.054932 | 0.27008 | 0.11444 | 0.16022 | 0.009155 | -9.5169 | 0.086975 | 121.5179 | 0.086975 | 121.3669 | -0.050354 | 0.07782 | 121.1517 | 121.4767 | 121.4584 | 111.8546 | 0.086975 | 121.3211 | 121.5454 | 121.3669 | 111.8546 | 0.086975 | 121.5454 | 121.4584 | 121.3211 | -121.3623 | -0.004578
440.6719 | 121.5637 | -121.2158 | 0.1831 | -0.010758 | -0.011794 | -0.015176 | 0.024152 | -0.010859 | -0.0057294 | -0.00092072 | -121.1517 | -9.3567 | -121.1838 | 0.27924 | 0.22888 | 0.32501 | 0.004578 | 0.25635 | 0.11902 | 0.15106 | 0.032043 | -9.5398 | 0.064087 | 121.4951 | 0.045777 | 121.3669 | -0.064086 | 0.032044 | 121.2204 | 121.4722 | 121.4447 | 111.8591 | 0.064087 | 121.3348 | 121.5408 | 121.3669 | 111.8591 | 0.064087 | 121.5408 | 121.4447 | 121.3348 | -121.3669 | -0.032043
441.6719 | 121.5637 | -121.2112 | 0.16479 | -0.003128 | -0.012221 | -0.018167 | 0.022016 | -0.011286 | -0.0044476 | 0.00078828 | -121.1884 | -9.343 | -121.17 | 0.27466 | 0.21057 | 0.30212 | 0.009155 | 0.23804 | 0.11444 | 0.15106 | 0.041199 | -9.5078 | 0.022889 | 121.4859 | 0.045776 | 121.3623 | -0.050354 | -0.01831 | 121.2204 | 121.4493 | 121.4218 | 111.8683 | 0.022889 | 121.3257 | 121.5134 | 121.3623 | 111.8683 | 0.022889 | 121.5134 | 121.4218 | 121.3257 | -121.3348 | -0.013733
442.6719 | 121.5775 | -121.1929 | 0.16479 | -0.003128 | -0.01158 | -0.017098 | 0.022657 | -0.010645 | -0.0057294 | 0.0018565 | -121.17 | -9.3475 | -121.2112 | 0.28839 | 0.22888 | 0.30212 | -0.004578 | 0.24261 | 0.10986 | 0.16022 | -0.018311 | -9.5123 | 0.022888 | 121.4813 | 0.064087 | 121.3531 | -0.054932 | 0.041199 | 121.1884 | 121.4355 | 121.4218 | 111.8454 | 0.022888 | 121.3028 | 121.4951 | 121.3531 | 111.8454 | 0.022888 | 121.4951 | 121.4218 | 121.3028 | -121.376 | -0.004578
443.6719 | 121.5729 | -121.2112 | 0.15564 | -0.003128 | -0.0092307 | -0.013253 | 0.023084 | -0.010431 | -0.0044476 | 0.0020701 | -121.1472 | -9.3475 | -121.1929 | 0.3067 | 0.26093 | 0.32959 | -0.050354 | 0.25635 | 0.11444 | 0.13275 | 0.018311 | -9.5032 | 0.064087 | 121.5179 | 0.10529 | 121.344 | -0.041199 | 0.045776 | 121.1609 | 121.4676 | 121.4722 | 111.8637 | 0.064087 | 121.3257 | 121.5408 | 121.344 | 111.8637 | 0.064087 | 121.5408 | 121.4722 | 121.3257 | -121.3486 | -0.022889
444.6719 | 121.6049 | -121.1838 | 0.16937 | 0.0045015 | -0.010726 | -0.015817 | 0.025648 | -0.0093631 | -0.005943 | 0.0012155 | -121.1288 | -9.343 | -121.1746 | 0.32501 | 0.2655 | 0.36163 | -0.059509 | 0.27924 | 0.09613 | 0.16022 | 0.009155 | -9.5123 | 0.054932 | 121.5088 | 0.09613 | 121.344 | -0.073243 | 0.045777 | 121.1243 | 121.463 | 121.4493 | 111.8408 | 0.054932 | 121.2799 | 121.5454 | 121.344 | 111.8408 | 0.054932 | 121.5454 | 121.4493 | 121.2799 | -121.344 | -0.009156
445.6719 | 121.637 | -121.1929 | 0.15564 | 0.0045015 | -0.0081625 | -0.012826 | 0.024152 | -0.0091495 | -0.0048748 | 0.0020701 | -121.1243 | -9.343 | -121.1929 | 0.35706 | 0.27008 | 0.36621 | -0.073242 | 0.29297 | 0.10986 | 0.16479 | 0 | -9.4986 | 0.068664 | 121.55 | 0.11444 | 121.3577 | -0.045777 | 0.068664 | 121.1197 | 121.4859 | 121.463 | 111.85 | 0.068664 | 121.3028 | 121.5591 | 121.3577 | 111.85 | 0.068664 | 121.5591 | 121.463 | 121.3028 | -121.3486 | 0.009155
446.6719 | 121.5912 | -121.2067 | 0.19226 | -0.003128 | -0.0066673 | -0.011971 | 0.023511 | -0.0089359 | -0.004234 | 0.0016427 | -121.2112 | -9.3338 | -121.2296 | 0.27466 | 0.19226 | 0.27924 | 0.018311 | 0.21057 | 0.11444 | 0.13275 | -0.022888 | -9.5261 | -0.004578 | 121.4813 | 0 | 121.3394 | -0.07782 | 0.01831 | 121.225 | 121.4172 | 121.3989 | 111.8729 | -0.004578 | 121.3211 | 121.4859 | 121.3394 | 111.8729 | -0.004578 | 121.4859 | 121.3989 | 121.3211 | -121.4218 | -0.05951
447.6719 | 121.6324 | -121.2067 | 0.16022 | 0.01213 | -0.0066673 | -0.01603 | 0.025434 | -0.0085085 | -0.005943 | 0.0022837 | -121.17 | -9.3475 | -121.2479 | 0.32044 | 0.23804 | 0.3479 | -0.045776 | 0.26093 | 0.10529 | 0.14648 | -0.041199 | -9.5078 | 0.036621 | 121.5271 | 0.07782 | 121.3531 | -0.054931 | 0.07782 | 121.1609 | 121.4676 | 121.4447 | 111.8591 | 0.036621 | 121.312 | 121.5546 | 121.3531 | 111.8591 | 0.036621 | 121.5546 | 121.4447 | 121.312 | -121.4081 | -0.013733
448.6719 | 121.6415 | -121.2021 | 0.1831 | -0.003128 | -0.01094 | -0.012185 | 0.02223 | -0.0076541 | -0.0050884 | 0.0012155 | -121.138 | -9.343 | -121.2433 | 0.32501 | 0.27008 | 0.37079 | -0.07782 | 0.27008 | 0.10529 | 0.15564 | -0.041199 | -9.5261 | 0.064087 | 121.5271 | 0.086976 | 121.3577 | -0.077819 | 0.10529 | 121.1243 | 121.4722 | 121.4722 | 111.8591 | 0.064087 | 121.3074 | 121.5729 | 121.3577 | 111.8591 | 0.064087 | 121.5729 | 121.4722 | 121.3074 | -121.4264 | -0.027465
449.6719 | 121.6324 | -121.1884 | 0.17395 | -0.010758 | -0.0079489 | -0.011117 | 0.023511 | -0.0076541 | -0.004234 | -6.6324e-05 | -121.17 | -9.3384 | -121.2433 | 0.31128 | 0.2655 | 0.34332 | -0.032043 | 0.27008 | 0.10986 | 0.15564 | -0.054932 | -9.5123 | 0.01831 | 121.4996 | 0.091553 | 121.344 | -0.064087 | 0.073242 | 121.1563 | 121.4584 | 121.4539 | 111.85 | 0.01831 | 121.2982 | 121.5317 | 121.344 | 111.85 | 0.01831 | 121.5317 | 121.4539 | 121.2982 | -121.4172 | -0.01831
450.6719 | 121.6324 | -121.1792 | 0.17395 | -0.018387 | -0.0077353 | -0.018167 | 0.02522 | -0.0065859 | -0.003593 | 0.00057468 | -121.2112 | -9.3475 | -121.2341 | 0.2655 | 0.22888 | 0.31586 | 0.013733 | 0.22888 | 0.11444 | 0.12817 | -0.054932 | -9.5215 | -0.032044 | 121.4447 | 0.054932 | 121.3074 | -0.059509 | 0.022888 | 121.1929 | 121.4081 | 121.4081 | 111.8317 | -0.032044 | 121.2936 | 121.4951 | 121.3074 | 111.8317 | -0.032044 | 121.4951 | 121.4081 | 121.2936 | -121.4081 | -0.045776
451.6719 | 121.5683 | -121.1975 | 0.19226 | -0.003128 | -0.0075217 | -0.013253 | 0.024793 | -0.0078677 | -0.005943 | 0.0027109 | -121.2296 | -9.3384 | -121.2387 | 0.22888 | 0.18768 | 0.26093 | 0.059509 | 0.16479 | 0.13733 | 0.15106 | -0.041198 | -9.5306 | -0.032043 | 121.4264 | -0.004578 | 121.3486 | -0.054932 | 0.009155 | 121.257 | 121.3623 | 121.3852 | 111.8591 | -0.032043 | 121.3348 | 121.4584 | 121.3486 | 111.8591 | -0.032043 | 121.4584 | 121.3852 | 121.3348 | -121.431 | -0.041199
452.6719 | 121.5363 | -121.2112 | 0.21057 | -0.003128 | -0.0077353 | -0.013894 | 0.029279 | -0.0074405 | -0.0023114 | 0.0031381 | -121.2616 | -9.3292 | -121.2662 | 0.21515 | 0.16022 | 0.24719 | 0.10529 | 0.15564 | 0.16022 | 0.13275 | -0.054931 | -9.5398 | -0.050354 | 121.4264 | -0.050354 | 121.344 | -0.050354 | 0.004577 | 121.3165 | 121.3669 | 121.3715 | 111.882 | -0.050354 | 121.3715 | 121.4584 | 121.344 | 111.882 | -0.050354 | 121.4584 | 121.3715 | 121.3715 | -121.4767 | -0.07782
453.6719 | 121.5042 | -121.2021 | 0.23346 | -0.010758 | -0.0049583 | -0.0076989 | 0.029493 | -0.0063723 | -0.0033794 | 0.00036108 | -121.225 | -9.3338 | -121.2341 | 0.21057 | 0.16479 | 0.24261 | 0.16022 | 0.16022 | 0.16479 | 0.13275 | -0.032044 | -9.5673 | -0.022889 | 121.4127 | -0.068664 | 121.3348 | -0.068664 | 0.009155 | 121.3623 | 121.3623 | 121.3669 | 111.8683 | -0.022889 | 121.3669 | 121.4447 | 121.3348 | 111.8683 | -0.022889 | 121.4447 | 121.3669 | 121.3669 | -121.4676 | -0.10071
454.6719 | 121.5317 | -121.225 | 0.21973 | 0.0045015 | -0.0030357 | -0.0081261 | 0.027357 | -0.0050907 | -0.0020978 | 0.0010019 | -121.2616 | -9.343 | -121.2753 | 0.20599 | 0.16022 | 0.23346 | 0.14648 | 0.12817 | 0.17853 | 0.12817 | -0.050354 | -9.5627 | -0.036621 | 121.431 | -0.05951 | 121.3531 | -0.041199 | 0.013733 | 121.3715 | 121.3531 | 121.3852 | 111.882 | -0.036621 | 121.4035 | 121.4584 | 121.3531 | 111.882 | -0.036621 | 121.4584 | 121.3852 | 121.4035 | -121.4951 | -0.091553
455.6719 | 121.5317 | -121.1746 | 0.23804 | -0.018387 | -0.0073081 | -0.0064171 | 0.028638 | -0.0063723 | -0.0023114 | 0.0016427 | -121.2433 | -9.343 | -121.2296 | 0.21515 | 0.17853 | 0.27008 | 0.16022 | 0.16937 | 0.1831 | 0.15106 | -0.054931 | -9.581 | -0.068664 | 121.3898 | -0.059509 | 121.3257 | -0.054932 | -0.013733 | 121.3348 | 121.344 | 121.3531 | 111.8317 | -0.068664 | 121.3577 | 121.4447 | 121.3257 | 111.8317 | -0.068664 | 121.4447 | 121.3531 | 121.3577 | -121.4676 | -0.086975
456.6719 | 121.5546 | -121.2112 | 0.23346 | -0.003128 | -0.0058127 | -0.010049 | 0.02458 | -0.0059451 | -0.004234 | 0.0018565 | -121.2616 | -9.3384 | -121.2204 | 0.21057 | 0.15106 | 0.2655 | 0.16022 | 0.16022 | 0.19226 | 0.15564 | -0.009155 | -9.5718 | -0.050354 | 121.4218 | -0.082397 | 121.3669 | -0.041198 | -0.041199 | 121.3715 | 121.3715 | 121.3623 | 111.8729 | -0.050354 | 121.4035 | 121.4767 | 121.3669 | 111.8729 | -0.050354 | 121.4767 | 121.3623 | 121.4035 | -121.4539 | -0.077819
457.6719 | 121.4676 | -121.2753 | 0.068665 | -0.010758 | -0.0055991 | -0.0094079 | 0.016035 | -0.0044497 | -0.0057294 | 0.0014291 | -0.045776 | 0 | -0.054932 | 0.050354 | 0.013733 | 0.09613 | 0.041199 | 0 | 0.022888 | -0.009155 | 121.2204 | -0.068665 | 121.2296 | 121.3257 | -0.054932 | 121.2662 | -0.045777 | 0.009156 | 121.3165 | 121.2753 | 121.2891 | 121.2753 | 121.2296 | 121.2982 | 121.3715 | 121.2662 | 121.2753 | 121.2296 | 121.3715 | 121.2891 | 121.2982 | -0.1236 | -0.07782
458.6719 | 121.5088 | -121.3257 | 0.082397 | -0.003128 | -0.0060263 | -0.012612 | 0.020307 | -0.0070133 | -0.0057294 | 0.00036108 | 0.004578 | 0.013733 | -0.027466 | 0.082397 | 0.018311 | 0.10529 | 0.027466 | 0.013733 | 0.027466 | 0 | 121.2982 | -0.068664 | 121.3303 | 121.4081 | -0.064086 | 121.3257 | -0.054931 | 0.032044 | 121.3531 | 121.3394 | 121.344 | 121.3394 | 121.3303 | 121.3531 | 121.431 | 121.3257 | 121.3394 | 121.3303 | 121.431 | 121.344 | 121.3531 | -0.10986 | -0.082397
459.6719 | 121.5363 | -121.3669 | 0.082397 | -0.026017 | -0.0053855 | -0.011331 | 0.021589 | -0.0061587 | -0.0057294 | 0.00078828 | 0.018311 | -0.009155 | -0.022888 | 0.091553 | 0.041199 | 0.11902 | 0.004578 | 0.036621 | 0.018311 | 0.009155 | 121.344 | -0.091552 | 121.3852 | 121.4584 | -0.041198 | 121.376 | -0.064086 | 0.041199 | 121.3715 | 121.4035 | 121.4081 | 121.3577 | 121.3852 | 121.3852 | 121.4859 | 121.376 | 121.3577 | 121.3852 | 121.4859 | 121.4081 | 121.3852 | -0.10528 | -0.073242
460.6719 | 121.5912 | -121.344 | 0.064087 | -0.003128 | -0.0058127 | -0.0091943 | 0.01988 | -0.0065859 | -0.0033794 | 0.0012155 | 0.054932 | 0.032043 | -0.022888 | 0.14191 | 0.091553 | 0.17853 | -0.032043 | 0.10071 | 0.036621 | 0.004578 | 121.3211 | -0.032044 | 121.3989 | 121.4859 | 0.027466 | 121.3486 | -0.027466 | 0.07782 | 121.312 | 121.4447 | 121.4355 | 121.376 | 121.3989 | 121.3806 | 121.5225 | 121.3486 | 121.376 | 121.3989 | 121.5225 | 121.4355 | 121.3806 | -0.086975 | -0.059509
461.6719 | 121.5683 | -121.3852 | 0.064087 | -0.010758 | -0.0023947 | -0.0096215 | 0.021589 | -0.0050907 | -0.005302 | 0.00014748 | 0.086975 | 0.027466 | -0.004578 | 0.11444 | 0.073242 | 0.15564 | -0.032043 | 0.091553 | 0.022888 | 0.027466 | 121.3806 | -0.036621 | 121.4722 | 121.4996 | 0.009155 | 121.4127 | -0.041199 | 0.091553 | 121.3531 | 121.4767 | 121.4584 | 121.4127 | 121.4722 | 121.4081 | 121.5408 | 121.4127 | 121.4127 | 121.4722 | 121.5408 | 121.4584 | 121.4081 | -0.068665 | -0.036621
462.6719 | 121.55 | -121.3806 | 0.07782 | -0.010758 | -0.0049583 | -0.012185 | 0.024152 | -0.0042361 | -0.0027386 | 0.00014748 | 0.036621 | 0.004578 | -0.013733 | 0.091553 | 0.045776 | 0.13275 | -0.004578 | 0.054932 | 0.032043 | -0.004578 | 121.3669 | -0.073242 | 121.4172 | 121.4722 | -0.032044 | 121.376 | -0.045777 | 0.050354 | 121.376 | 121.4355 | 121.4264 | 121.3852 | 121.4172 | 121.4127 | 121.5134 | 121.376 | 121.3852 | 121.4172 | 121.5134 | 121.4264 | 121.4127 | -0.091553 | -0.082398
463.6719 | 121.5775 | -121.3669 | 0.068665 | -0.010758 | -0.0055991 | -0.017739 | 0.022871 | -0.0048769 | -0.0063702 | 0.0029245 | 0.045776 | 0.018311 | -0.022888 | 0.10986 | 0.064087 | 0.13733 | 0 | 0.07782 | 0.022888 | 0.013733 | 121.344 | -0.050354 | 121.4127 | 121.4767 | -0.004578 | 121.3806 | -0.045777 | 0.068664 | 121.3669 | 121.4447 | 121.431 | 121.3852 | 121.4127 | 121.3898 | 121.5042 | 121.3806 | 121.3852 | 121.4127 | 121.5042 | 121.431 | 121.3898 | -0.091553 | -0.054932
464.6719 | 121.6095 | -121.3577 | 0.054932 | -0.010758 | -0.0055991 | -0.013467 | 0.022443 | -0.0048769 | -0.003593 | 0.0020701 | 0.073242 | 0.009155 | 0.004578 | 0.12817 | 0.082397 | 0.16022 | -0.018311 | 0.09613 | 0.013733 | -0.027466 | 121.3623 | -0.045777 | 121.431 | 121.4859 | 0.027465 | 121.3303 | -0.041199 | 0.068664 | 121.3394 | 121.4539 | 121.4401 | 121.3669 | 121.431 | 121.3715 | 121.5179 | 121.3303 | 121.3669 | 121.431 | 121.5179 | 121.4401 | 121.3715 | -0.050354 | -0.082398
465.6719 | 121.6003 | -121.3577 | 0.07782 | -0.010758 | -0.0017539 | -0.014321 | 0.021589 | -0.0040225 | -0.0050884 | 0.00036108 | 0.073242 | 0 | -0.022888 | 0.14648 | 0.082397 | 0.17853 | -0.032043 | 0.11444 | 0.036621 | 0.004578 | 121.3348 | -0.07782 | 121.431 | 121.5042 | 0.004577 | 121.3623 | -0.041199 | 0.09613 | 121.3257 | 121.4722 | 121.4401 | 121.3577 | 121.431 | 121.3943 | 121.5363 | 121.3623 | 121.3577 | 121.431 | 121.5363 | 121.4401 | 121.3943 | -0.10071 | -0.073242
466.6719 | 121.6278 | -121.3852 | 0.073242 | -0.003128 | -0.0045309 | -0.011971 | 0.020948 | -0.0048769 | -0.004234 | 0.0016427 | 0.050354 | 0.009155 | -0.027466 | 0.13733 | 0.082397 | 0.16479 | -0.022888 | 0.1236 | 0.009155 | 0.009155 | 121.3577 | -0.064087 | 121.4355 | 121.5225 | 0.009155 | 121.3943 | -0.064087 | 0.07782 | 121.3623 | 121.5088 | 121.4676 | 121.3943 | 121.4355 | 121.3943 | 121.55 | 121.3943 | 121.3943 | 121.4355 | 121.55 | 121.4676 | 121.3943 | -0.10071 | -0.064087
467.6719 | 121.6187 | -121.4127 | 0.086975 | -0.018387 | -0.0070945 | -0.014321 | 0.021162 | -0.0072269 | -0.0046612 | 0.0014291 | 0.013733 | 0.032043 | -0.013733 | 0.10071 | 0.068665 | 0.13733 | 0.022888 | 0.09613 | 0.045776 | -0.009155 | 121.3989 | -0.054932 | 121.4264 | 121.5134 | -0.01831 | 121.4035 | -0.041199 | 0.027466 | 121.4355 | 121.5088 | 121.4813 | 121.4447 | 121.4264 | 121.4584 | 121.55 | 121.4035 | 121.4447 | 121.4264 | 121.55 | 121.4813 | 121.4584 | -0.10071 | -0.09613
468.6719 | 121.6324 | -121.376 | 0.07782 | -0.003128 | -0.0045309 | -0.011331 | 0.021375 | -0.0055179 | -0.0048748 | 0.00078828 | 0.054932 | 0.009155 | -0.004578 | 0.11902 | 0.086975 | 0.16937 | -0.022888 | 0.10529 | 0.032043 | 0 | 121.3715 | -0.068665 | 121.431 | 121.4951 | 0.009155 | 121.376 | -0.045777 | 0.05951 | 121.3531 | 121.4813 | 121.463 | 121.3852 | 121.431 | 121.4081 | 121.5454 | 121.376 | 121.3852 | 121.431 | 121.5454 | 121.463 | 121.4081 | -0.082398 | -0.07782
469.6719 | 121.6324 | -121.3898 | 0.07782 | -0.003128 | -0.0060263 | -0.012399 | 0.021589 | -0.0057315 | -0.0050884 | 0.00057468 | 0.050354 | -0.018311 | -0.032043 | 0.13275 | 0.073242 | 0.17395 | -0.022888 | 0.10986 | 0.041199 | 0.004578 | 121.3577 | -0.096131 | 121.4401 | 121.5225 | -0.004578 | 121.3943 | -0.036621 | 0.082397 | 121.3669 | 121.4996 | 121.463 | 121.3715 | 121.4401 | 121.431 | 121.5637 | 121.3943 | 121.3715 | 121.4401 | 121.5637 | 121.463 | 121.431 | -0.10986 | -0.073242
470.6719 | 121.6324 | -121.4081 | 0.068665 | -0.003128 | -0.0049583 | -0.013253 | 0.019666 | -0.0040225 | -0.005302 | 0.0039927 | 0.054932 | -0.004578 | -0.009155 | 0.13733 | 0.09613 | 0.16479 | -0.027466 | 0.12817 | 0.027466 | 0.004578 | 121.3989 | -0.073243 | 121.463 | 121.5454 | 0.027465 | 121.4127 | -0.041199 | 0.064087 | 121.3806 | 121.5363 | 121.5042 | 121.4035 | 121.463 | 121.4355 | 121.5729 | 121.4127 | 121.4035 | 121.463 | 121.5729 | 121.5042 | 121.4355 | -0.07782 | -0.064087
471.6719 | 121.6415 | -121.3898 | 0.059509 | 0.0045015 | -0.0053855 | -0.010263 | 0.022657 | -0.0050907 | -0.0046612 | 0.0035653 | 0.054932 | 0.013733 | -0.013733 | 0.12817 | 0.10071 | 0.17395 | -0.022888 | 0.14648 | 0.027466 | -0.013733 | 121.376 | -0.045776 | 121.4447 | 121.5179 | 0.041199 | 121.376 | -0.032043 | 0.068665 | 121.3669 | 121.5363 | 121.4905 | 121.4035 | 121.4447 | 121.4172 | 121.5637 | 121.376 | 121.4035 | 121.4447 | 121.5637 | 121.4905 | 121.4172 | -0.073242 | -0.073242
472.6719 | 121.6415 | -121.4218 | 0.073242 | -0.003128 | -0.0051719 | -0.01368 | 0.022016 | -0.0040225 | -0.0050884 | 0.0010019 | 0.059509 | 0.018311 | -0.032043 | 0.1236 | 0.082397 | 0.15106 | -0.018311 | 0.11902 | 0.013733 | 0.004578 | 121.3898 | -0.054931 | 121.4813 | 121.5454 | 0.009155 | 121.4264 | -0.059509 | 0.091552 | 121.4035 | 121.5408 | 121.5042 | 121.4401 | 121.4813 | 121.4355 | 121.5729 | 121.4264 | 121.4401 | 121.4813 | 121.5729 | 121.5042 | 121.4355 | -0.10529 | -0.068664
473.6562 | 121.5729 | -121.4539 | 0.064087 | -0.003128 | -0.0062399 | -0.014749 | 0.017744 | -0.0063723 | -0.0050884 | 0.00057468 | -0.004578 | 0.050354 | -0.004578 | 0.064087 | 0.018311 | 0.10071 | 0.07782 | 0.050354 | 0.045776 | -0.004578 | 121.4493 | -0.013733 | 121.4493 | 121.5179 | -0.045776 | 121.4493 | -0.018311 | 0 | 121.5317 | 121.5042 | 121.4722 | 121.5042 | 121.4493 | 121.4996 | 121.5546 | 121.4493 | 121.5042 | 121.4493 | 121.5546 | 121.4722 | 121.4996 | -0.068665 | -0.068665
474.6562 | 121.5729 | -121.4355 | 0.07782 | -0.010758 | -0.0073081 | -0.015603 | 0.020307 | -0.0061587 | -0.003593 | 0.0016427 | 0 | 0.018311 | 0.009155 | 0.064087 | 0.027466 | 0.09613 | 0.068665 | 0.059509 | 0.036621 | 0.013733 | 121.4447 | -0.059509 | 121.4355 | 121.4996 | -0.050354 | 121.4493 | -0.041199 | -0.009155 | 121.5042 | 121.4951 | 121.463 | 121.4539 | 121.4355 | 121.4722 | 121.5317 | 121.4493 | 121.4539 | 121.4355 | 121.5317 | 121.463 | 121.4722 | -0.068665 | -0.064087
475.6719 | 121.6553 | -121.4493 | 0.07782 | 0.0045015 | -0.0038901 | -0.017312 | 0.021802 | -0.0057315 | -0.004234 | -0.0013479 | 0.064087 | 0.013733 | 0.009155 | 0.13733 | 0.082397 | 0.13733 | -0.018311 | 0.11902 | 0.036621 | 0.013733 | 121.4584 | -0.064087 | 121.5134 | 121.5866 | 0.004577 | 121.463 | -0.041199 | 0.054932 | 121.431 | 121.5683 | 121.5317 | 121.463 | 121.5134 | 121.4859 | 121.5866 | 121.463 | 121.463 | 121.5134 | 121.5866 | 121.5317 | 121.4859 | -0.068665 | -0.064087
476.6719 | 121.6553 | -121.4127 | 0.059509 | -0.026017 | -0.0064535 | -0.016244 | 0.021589 | -0.0044497 | -0.0029522 | 0.00057468 | 0.07782 | -0.004578 | 0.018311 | 0.14191 | 0.10071 | 0.16479 | -0.036621 | 0.10986 | 0.018311 | 0 | 121.431 | -0.064087 | 121.4905 | 121.5546 | 0.041199 | 121.4127 | -0.041198 | 0.059509 | 121.376 | 121.5225 | 121.5134 | 121.4081 | 121.4905 | 121.431 | 121.5775 | 121.4127 | 121.4081 | 121.4905 | 121.5775 | 121.5134 | 121.431 | -0.041198 | -0.059509
477.6719 | 121.6507 | -121.4355 | 0.068665 | -0.003128 | -0.0043173 | -0.014108 | 0.023084 | -0.0048769 | -0.0050884 | -6.6324e-05 | 0.07782 | 0.018311 | 0.018311 | 0.12817 | 0.086975 | 0.16022 | -0.032043 | 0.12817 | 0.036621 | 0.009155 | 121.4539 | -0.050354 | 121.5134 | 121.5637 | 0.01831 | 121.4447 | -0.032044 | 0.059509 | 121.4035 | 121.5637 | 121.5225 | 121.4539 | 121.5134 | 121.4722 | 121.5958 | 121.4447 | 121.4539 | 121.5134 | 121.5958 | 121.5225 | 121.4722 | -0.050354 | -0.05951
478.6719 | 121.6553 | -121.4264 | 0.082397 | 0.0045015 | -0.0064535 | -0.014321 | 0.021162 | -0.0074405 | -0.0044476 | 0.0014291 | 0.068665 | 0.018311 | 0.004578 | 0.13275 | 0.07782 | 0.16479 | -0.032043 | 0.11902 | 0.027466 | -0.009155 | 121.431 | -0.064086 | 121.4951 | 121.5591 | -0.004577 | 121.4172 | -0.054931 | 0.064087 | 121.3943 | 121.5454 | 121.5042 | 121.4447 | 121.4951 | 121.4539 | 121.5912 | 121.4172 | 121.4447 | 121.4951 | 121.5912 | 121.5042 | 121.4539 | -0.077819 | -0.091552
479.6719 | 121.6507 | -121.4447 | 0.064087 | 0.0045015 | -0.0060263 | -0.012185 | 0.019453 | -0.0061587 | -0.003593 | 0.0010019 | 0.068665 | 0.004578 | 0.036621 | 0.12817 | 0.091553 | 0.14648 | -0.009155 | 0.1236 | 0.036621 | 0.009155 | 121.4813 | -0.059509 | 121.5134 | 121.5729 | 0.027466 | 121.4539 | -0.027466 | 0.032044 | 121.4355 | 121.5683 | 121.5363 | 121.4493 | 121.5134 | 121.4813 | 121.5912 | 121.4539 | 121.4493 | 121.5134 | 121.5912 | 121.5363 | 121.4813 | -0.027466 | -0.054932
480.6719 | 121.6599 | -121.4447 | 0.064087 | -0.010758 | -0.0062399 | -0.011971 | 0.019453 | -0.0057315 | -0.0027386 | 0.0016427 | 0.091553 | 0.027466 | 0.022888 | 0.13275 | 0.064087 | 0.14648 | -0.022888 | 0.11444 | 0.027466 | -0.013733 | 121.4676 | -0.036621 | 121.5363 | 121.5775 | 0 | 121.431 | -0.036621 | 0.068665 | 121.4218 | 121.5591 | 121.5088 | 121.4722 | 121.5363 | 121.4722 | 121.5912 | 121.431 | 121.4722 | 121.5363 | 121.5912 | 121.5088 | 121.4722 | -0.041199 | -0.07782
481.6719 | 121.6507 | -121.4539 | 0.10071 | -0.010758 | -0.0070945 | -0.014321 | 0.020093 | -0.0050907 | -0.0055156 | 0.0012155 | 0.027466 | 0.041199 | 0.004578 | 0.082397 | 0.054932 | 0.10071 | 0.036621 | 0.073242 | 0.027466 | -0.018311 | 121.4584 | -0.059509 | 121.4813 | 121.5363 | -0.045776 | 121.4355 | -0.073242 | 0.022888 | 121.4905 | 121.5271 | 121.5088 | 121.4951 | 121.4813 | 121.4813 | 121.5546 | 121.4355 | 121.4951 | 121.4813 | 121.5546 | 121.5088 | 121.4813 | -0.09613 | -0.11902
482.6719 | 121.6782 | -121.4493 | 0.068665 | -0.003128 | -0.0060263 | -0.014749 | 0.021162 | -0.0053043 | -0.007011 | 0.0012155 | 0.091553 | 0.022888 | 0.018311 | 0.13733 | 0.07782 | 0.16937 | -0.032043 | 0.10529 | 0.036621 | 0.009155 | 121.4676 | -0.045777 | 121.5408 | 121.5866 | 0.009155 | 121.4584 | -0.032044 | 0.073242 | 121.4172 | 121.5546 | 121.5271 | 121.4722 | 121.5408 | 121.4859 | 121.6187 | 121.4584 | 121.4722 | 121.5408 | 121.6187 | 121.5271 | 121.4859 | -0.050354 | -0.05951
483.6719 | 121.6827 | -121.4539 | 0.073242 | -0.010758 | -0.0053855 | -0.016458 | 0.019025 | -0.0070133 | -0.0061566 | 0.00078828 | 0.086975 | 0.036621 | 0.022888 | 0.12817 | 0.07782 | 0.15564 | -0.032043 | 0.11444 | 0.027466 | 0.004578 | 121.4767 | -0.036621 | 121.5408 | 121.582 | 0.004578 | 121.4584 | -0.045776 | 0.064087 | 121.4218 | 121.5683 | 121.5317 | 121.4905 | 121.5408 | 121.4813 | 121.6095 | 121.4584 | 121.4905 | 121.5408 | 121.6095 | 121.5317 | 121.4813 | -0.050354 | -0.068664
484.6719 | 121.6873 | -121.4539 | 0.064087 | -0.010758 | -0.0053855 | -0.01304 | 0.020093 | -0.0063723 | -0.0046612 | 0.0022837 | 0.086975 | 0.018311 | 0.013733 | 0.13275 | 0.086975 | 0.15564 | -0.027466 | 0.11902 | 0.036621 | -0.004578 | 121.4676 | -0.045776 | 121.5408 | 121.5866 | 0.022888 | 121.4493 | -0.027466 | 0.073242 | 121.4264 | 121.5729 | 121.5408 | 121.4722 | 121.5408 | 121.4905 | 121.6095 | 121.4493 | 121.4722 | 121.5408 | 121.6095 | 121.5408 | 121.4905 | -0.050354 | -0.068665
485.6719 | 121.6827 | -121.4676 | 0.073242 | -0.003128 | -0.0064535 | -0.010476 | 0.020521 | -0.0070133 | -0.0027386 | 0.00078828 | 0.073242 | 0.032043 | 0 | 0.1236 | 0.082397 | 0.14191 | -0.013733 | 0.1236 | 0.050354 | -0.018311 | 121.4676 | -0.041199 | 121.5408 | 121.5912 | 0.009155 | 121.4493 | -0.022888 | 0.073242 | 121.4539 | 121.5912 | 121.55 | 121.4996 | 121.5408 | 121.5179 | 121.6095 | 121.4493 | 121.4996 | 121.5408 | 121.6095 | 121.55 | 121.5179 | -0.073242 | -0.091553
486.6719 | 121.669 | -121.4584 | 0.059509 | -0.010758 | -0.0030357 | -0.01304 | 0.020948 | -0.0061587 | -0.0044476 | 0.0010019 | 0.068665 | 0.032043 | 0.013733 | 0.1236 | 0.068665 | 0.16479 | -0.009155 | 0.09613 | 0.018311 | 0.004578 | 121.4722 | -0.027466 | 121.5271 | 121.582 | 0.009156 | 121.463 | -0.041198 | 0.054932 | 121.4493 | 121.5546 | 121.5271 | 121.4905 | 121.5271 | 121.4767 | 121.6232 | 121.463 | 121.4905 | 121.5271 | 121.6232 | 121.5271 | 121.4767 | -0.045776 | -0.054931
487.6719 | 121.6461 | -121.4905 | 0.086975 | -0.003128 | -0.0068809 | -0.0087671 | 0.018598 | -0.0059451 | -0.0050884 | 0.0029245 | 0.022888 | 0.050354 | 0.013733 | 0.07782 | 0.041199 | 0.09613 | 0.045776 | 0.036621 | 0.036621 | -0.022888 | 121.5042 | -0.036621 | 121.5134 | 121.5683 | -0.045776 | 121.4676 | -0.050354 | 0.009155 | 121.5363 | 121.5271 | 121.5317 | 121.5408 | 121.5134 | 121.5271 | 121.5866 | 121.4676 | 121.5408 | 121.5134 | 121.5866 | 121.5317 | 121.5271 | -0.073242 | -0.10986
488.6719 | 121.6461 | -121.5179 | 0.082397 | -0.010758 | -0.0066673 | -0.017526 | 0.018598 | -0.0074405 | -0.0029522 | 0.00078828 | 0.013733 | 0.032043 | 0.013733 | 0.050354 | 0.022888 | 0.09613 | 0.068665 | 0.054932 | 0.036621 | -0.027466 | 121.5317 | -0.050354 | 121.5317 | 121.5683 | -0.059509 | 121.4905 | -0.045776 | 0 | 121.5866 | 121.5729 | 121.5408 | 121.55 | 121.5317 | 121.5546 | 121.6141 | 121.4905 | 121.55 | 121.5317 | 121.6141 | 121.5408 | 121.5546 | -0.068664 | -0.10986
489.6719 | 121.6827 | -121.463 | 0.068665 | -0.010758 | -0.0062399 | -0.014749 | 0.01988 | -0.0061587 | -0.002525 | 0.0010019 | 0.068665 | 0.032043 | 0.027466 | 0.11444 | 0.091553 | 0.14191 | -0.022888 | 0.10986 | 0.050354 | 0.004578 | 121.4905 | -0.036622 | 121.5317 | 121.5775 | 0.022888 | 121.4676 | -0.018311 | 0.041199 | 121.4401 | 121.5729 | 121.5546 | 121.4951 | 121.5317 | 121.5134 | 121.6049 | 121.4676 | 121.4951 | 121.5317 | 121.6049 | 121.5546 | 121.5134 | -0.041199 | -0.064087
490.6719 | 121.669 | -121.4722 | 0.068665 | 0.0045015 | -0.0064535 | -0.012185 | 0.020307 | -0.0072269 | -0.004234 | 0.00036108 | 0.050354 | 0.022888 | 0.013733 | 0.11444 | 0.068665 | 0.12817 | 0 | 0.09613 | 0.041199 | -0.018311 | 121.4859 | -0.045777 | 121.5225 | 121.5866 | 0 | 121.4539 | -0.027466 | 0.036621 | 121.4722 | 121.5683 | 121.5408 | 121.4951 | 121.5225 | 121.5134 | 121.6003 | 121.4539 | 121.4951 | 121.5225 | 121.6003 | 121.5408 | 121.5134 | -0.054932 | -0.086976
491.6719 | 121.6873 | -121.4905 | 0.068665 | -0.018387 | -0.0073081 | -0.012185 | 0.020307 | -0.0082949 | -0.005302 | 0.0024973 | 0.027466 | 0.036621 | 0.009155 | 0.09613 | 0.059509 | 0.14191 | 0.013733 | 0.07782 | 0.036621 | -0.004578 | 121.4996 | -0.032044 | 121.5179 | 121.5866 | -0.009156 | 121.4859 | -0.032044 | 0.018311 | 121.5042 | 121.5683 | 121.55 | 121.5271 | 121.5179 | 121.5271 | 121.6324 | 121.4859 | 121.5271 | 121.5179 | 121.6324 | 121.55 | 121.5271 | -0.05951 | -0.073243
492.6719 | 121.6827 | -121.5317 | 0.064087 | -0.003128 | -0.0066673 | -0.014108 | 0.01988 | -0.0074405 | -0.0057294 | 0.00036108 | 0.018311 | 0.027466 | 0.032043 | 0.09613 | 0.036621 | 0.11444 | 0.041199 | 0.073242 | 0.022888 | -0.013733 | 121.5637 | -0.036621 | 121.55 | 121.6278 | -0.027466 | 121.5179 | -0.041199 | -0.013732 | 121.5729 | 121.6049 | 121.5683 | 121.5591 | 121.55 | 121.5546 | 121.6461 | 121.5179 | 121.5591 | 121.55 | 121.6461 | 121.5683 | 121.5546 | -0.032044 | -0.07782
493.6719 | 121.6644 | -121.5179 | 0.073242 | -0.010758 | -0.0062399 | -0.014108 | 0.020948 | -0.0082949 | -0.0033794 | 0.0010019 | 0.018311 | 0.027466 | 0.009155 | 0.064087 | 0.041199 | 0.10986 | 0.054932 | 0.059509 | 0.054932 | 0 | 121.5271 | -0.045776 | 121.5363 | 121.582 | -0.032043 | 121.5179 | -0.01831 | 0.009156 | 121.5729 | 121.5775 | 121.5591 | 121.5454 | 121.5363 | 121.5729 | 121.6278 | 121.5179 | 121.5454 | 121.5363 | 121.6278 | 121.5591 | 121.5729 | -0.064087 | -0.073242
494.6719 | 121.788 | -121.463 | 0.045776 | -0.018387 | -0.010726 | -0.016244 | 0.018812 | -0.0057315 | -0.004234 | 0.0012155 | 0.11444 | -0.027466 | 0.054932 | 0.19226 | 0.13275 | 0.24719 | -0.1831 | 0.17853 | -0.004578 | 0.036621 | 121.5179 | -0.073242 | 121.5775 | 121.6553 | 0.086975 | 121.4996 | -0.050354 | 0.059509 | 121.2799 | 121.6415 | 121.5958 | 121.4355 | 121.5775 | 121.4584 | 121.7102 | 121.4996 | 121.4355 | 121.5775 | 121.7102 | 121.5958 | 121.4584 | 0.009156 | -0.009155
495.6719 | 121.669 | -121.5317 | 0.07782 | -0.018387 | -0.0068809 | -0.017739 | 0.020521 | -0.0078677 | -0.0055156 | 0.0018565 | 0.013733 | 0.036621 | 0.009155 | 0.064087 | 0.018311 | 0.091553 | 0.082397 | 0.059509 | 0.032043 | -0.032043 | 121.5408 | -0.041199 | 121.5454 | 121.5958 | -0.059509 | 121.4996 | -0.045777 | 0.004578 | 121.6141 | 121.5912 | 121.55 | 121.5683 | 121.5454 | 121.5637 | 121.6232 | 121.4996 | 121.5683 | 121.5454 | 121.6232 | 121.55 | 121.5637 | -0.068665 | -0.10986
496.6719 | 121.6873 | -121.55 | 0.050354 | -0.003128 | -0.0077353 | -0.014321 | 0.020521 | -0.0082949 | -0.0044476 | 0.0027109 | 0.032043 | 0.022888 | 0.022888 | 0.068665 | 0.041199 | 0.091553 | 0.064087 | 0.059509 | 0.041199 | -0.004578 | 121.5729 | -0.027466 | 121.582 | 121.6187 | -0.009155 | 121.5454 | -0.009155 | 0.009155 | 121.6141 | 121.6095 | 121.5912 | 121.5729 | 121.582 | 121.5912 | 121.6415 | 121.5454 | 121.5729 | 121.582 | 121.6415 | 121.5912 | 121.5912 | -0.027466 | -0.054932
497.6719 | 121.6599 | -121.5408 | 0.086975 | -0.003128 | -0.0060263 | -0.015603 | 0.020307 | -0.0072269 | -0.0057294 | 0.00057468 | 0.013733 | 0.032043 | 0.032043 | 0.07782 | 0.032043 | 0.10071 | 0.050354 | 0.073242 | 0.041199 | 0 | 121.5729 | -0.054932 | 121.5546 | 121.6187 | -0.054932 | 121.5408 | -0.045776 | -0.01831 | 121.5912 | 121.6141 | 121.5729 | 121.5729 | 121.5546 | 121.582 | 121.6415 | 121.5408 | 121.5729 | 121.5546 | 121.6415 | 121.5729 | 121.582 | -0.054932 | -0.086975
498.6719 | 121.6599 | -121.5729 | 0.064087 | -0.003128 | -0.0047447 | -0.013894 | 0.021162 | -0.0072269 | -0.0044476 | 0.0016427 | 0.018311 | 0.027466 | 0.018311 | 0.064087 | 0.022888 | 0.10986 | 0.068665 | 0.050354 | 0.059509 | -0.018311 | 121.5912 | -0.036621 | 121.5912 | 121.637 | -0.041199 | 121.5546 | -0.004578 | 0 | 121.6415 | 121.6232 | 121.5958 | 121.6003 | 121.5912 | 121.6324 | 121.6827 | 121.5546 | 121.6003 | 121.5912 | 121.6827 | 121.5958 | 121.6324 | -0.045776 | -0.082398
499.6719 | 121.6553 | -121.5363 | 0.07782 | -0.003128 | -0.0062399 | -0.011544 | 0.023939 | -0.0053043 | -0.0055156 | 0.00036108 | 0.018311 | 0.018311 | 0.009155 | 0.041199 | 0.018311 | 0.082397 | 0.032043 | 0.013733 | 0.027466 | -0.009155 | 121.5454 | -0.059509 | 121.5546 | 121.5775 | -0.059509 | 121.5271 | -0.050354 | 0.009156 | 121.5683 | 121.55 | 121.5546 | 121.5546 | 121.5546 | 121.5637 | 121.6187 | 121.5271 | 121.5546 | 121.5546 | 121.6187 | 121.5546 | 121.5637 | -0.068665 | -0.086975
500.6719 | 121.669 | -121.5363 | 0.07782 | -0.010758 | -0.0098715 | -0.016885 | 0.019239 | -0.0080813 | -0.0038068 | 0.0031381 | 0.013733 | 0.032043 | 0.032043 | 0.073242 | 0.032043 | 0.091553 | 0.059509 | 0.073242 | 0.036621 | -0.018311 | 121.5683 | -0.045777 | 121.55 | 121.6095 | -0.045777 | 121.5179 | -0.041199 | -0.01831 | 121.5958 | 121.6095 | 121.5683 | 121.5683 | 121.55 | 121.5729 | 121.6278 | 121.5179 | 121.5683 | 121.55 | 121.6278 | 121.5683 | 121.5729 | -0.045777 | -0.096131
501.6719 | 121.7468 | -121.5271 | 0.068665 | -0.003128 | -0.0094443 | -0.01603 | 0.018812 | -0.010218 | -0.0050884 | 0.00036108 | 0.11444 | 0 | 0.059509 | 0.16022 | 0.11444 | 0.19684 | -0.054932 | 0.1831 | 0.013733 | 0.018311 | 121.5866 | -0.068665 | 121.6415 | 121.6873 | 0.045776 | 121.5454 | -0.054932 | 0.054932 | 121.4722 | 121.7102 | 121.6415 | 121.5271 | 121.6415 | 121.5408 | 121.7239 | 121.5454 | 121.5271 | 121.6415 | 121.7239 | 121.6415 | 121.5408 | -0.009156 | -0.050354
502.6719 | 121.6919 | -121.5683 | 0.07782 | -0.018387 | -0.0090171 | -0.012826 | 0.020307 | -0.0078677 | -0.0057294 | 0.0016427 | 0.059509 | 0.022888 | 0.036621 | 0.10986 | 0.050354 | 0.10986 | 0.027466 | 0.09613 | 0.027466 | -0.009155 | 121.6049 | -0.054932 | 121.6278 | 121.6782 | -0.027466 | 121.5591 | -0.050354 | 0.022888 | 121.5958 | 121.6644 | 121.6187 | 121.5912 | 121.6278 | 121.5958 | 121.6782 | 121.5591 | 121.5912 | 121.6278 | 121.6782 | 121.6187 | 121.5958 | -0.041199 | -0.086975
503.6719 | 121.6736 | -121.5958 | 0.086975 | 0.0045015 | -0.0088035 | -0.015176 | 0.022016 | -0.0093631 | -0.005943 | 0.0022837 | 0.009155 | 0.041199 | 0.027466 | 0.082397 | 0.027466 | 0.091553 | 0.059509 | 0.064087 | 0.041199 | -0.013733 | 121.6232 | -0.045776 | 121.6049 | 121.6782 | -0.059509 | 121.582 | -0.045776 | -0.018311 | 121.6553 | 121.6599 | 121.6232 | 121.637 | 121.6049 | 121.637 | 121.6873 | 121.582 | 121.637 | 121.6049 | 121.6873 | 121.6232 | 121.637 | -0.059509 | -0.10071
504.6719 | 121.6599 | -121.5317 | 0.086975 | -0.018387 | -0.0055991 | -0.015176 | 0.023939 | -0.0055179 | -0.0050884 | -0.00027992 | 0.032043 | 0.027466 | 0.013733 | 0.07782 | 0.009155 | 0.09613 | 0.013733 | 0.027466 | 0.041199 | -0.009155 | 121.5454 | -0.059509 | 121.5637 | 121.6095 | -0.07782 | 121.5225 | -0.045776 | 0.01831 | 121.5454 | 121.5591 | 121.5408 | 121.5591 | 121.5637 | 121.5729 | 121.6278 | 121.5225 | 121.5591 | 121.5637 | 121.6278 | 121.5408 | 121.5729 | -0.073242 | -0.09613
505.6719 | 121.701 | -121.5912 | 0.073242 | -0.003128 | -0.010085 | -0.013894 | 0.018171 | -0.0076541 | -0.0055156 | 0.00036108 | 0.036621 | 0.018311 | 0.032043 | 0.10071 | 0.050354 | 0.11902 | 0.027466 | 0.086975 | 0.036621 | -0.004578 | 121.6232 | -0.054931 | 121.6278 | 121.6919 | -0.022888 | 121.5866 | -0.036621 | 0.004578 | 121.6187 | 121.6782 | 121.6415 | 121.6095 | 121.6278 | 121.6278 | 121.7102 | 121.5866 | 121.6095 | 121.6278 | 121.7102 | 121.6415 | 121.6278 | -0.041199 | -0.07782
506.6719 | 121.7422 | -121.5912 | 0.073242 | -0.010758 | -0.011153 | -0.012399 | 0.016889 | -0.0076541 | -0.005943 | 0.0018565 | 0.07782 | 0 | 0.027466 | 0.11902 | 0.064087 | 0.13733 | 0 | 0.11444 | 0.036621 | 0 | 121.6187 | -0.073242 | 121.669 | 121.7102 | -0.009155 | 121.5912 | -0.036621 | 0.050354 | 121.5912 | 121.7056 | 121.6553 | 121.5912 | 121.669 | 121.6278 | 121.7285 | 121.5912 | 121.5912 | 121.669 | 121.7285 | 121.6553 | 121.6278 | -0.045776 | -0.073242
507.6719 | 121.7422 | -121.582 | 0.054932 | 0.0045015 | -0.011153 | -0.015603 | 0.019239 | -0.0097903 | -0.0055156 | 0.0010019 | 0.10071 | 0.009155 | 0.050354 | 0.16022 | 0.10071 | 0.16022 | -0.027466 | 0.13733 | 0 | 0.018311 | 121.6324 | -0.045777 | 121.6827 | 121.7422 | 0.045776 | 121.6003 | -0.054932 | 0.050354 | 121.5546 | 121.7194 | 121.6827 | 121.5912 | 121.6827 | 121.582 | 121.7422 | 121.6003 | 121.5912 | 121.6827 | 121.7422 | 121.6827 | 121.582 | -0.004578 | -0.036621
508.6719 | 121.8292 | -121.5546 | 0.036621 | -0.003128 | -0.011153 | -0.015176 | 0.019239 | -0.0078677 | -0.0040204 | 0.0018565 | 0.12817 | -0.027466 | 0.064087 | 0.21057 | 0.16022 | 0.23804 | -0.1236 | 0.21973 | 0.009155 | 0.032043 | 121.6187 | -0.064087 | 121.6827 | 121.7651 | 0.1236 | 121.5866 | -0.027466 | 0.064087 | 121.431 | 121.7743 | 121.7148 | 121.5271 | 121.6827 | 121.5637 | 121.7926 | 121.5866 | 121.5271 | 121.6827 | 121.7926 | 121.7148 | 121.5637 | 0.027466 | -0.004578
509.6719 | 121.7377 | -121.5637 | 0.068665 | -0.003128 | -0.0062399 | -0.015176 | 0.025648 | -0.0082949 | -0.0050884 | -0.0011343 | 0.09613 | 0.022888 | 0.027466 | 0.13733 | 0.091553 | 0.15564 | -0.009155 | 0.10986 | 0.013733 | 0.009155 | 121.5912 | -0.045777 | 121.6599 | 121.701 | 0.022888 | 121.5729 | -0.054932 | 0.068664 | 121.5546 | 121.6736 | 121.6553 | 121.5866 | 121.6599 | 121.5775 | 121.7194 | 121.5729 | 121.5866 | 121.6599 | 121.7194 | 121.6553 | 121.5775 | -0.041199 | -0.05951
510.6719 | 121.7194 | -121.5912 | 0.059509 | -0.010758 | -0.01158 | -0.017312 | 0.019239 | -0.0082949 | -0.0074384 | -0.0019889 | 0.07782 | 0 | 0.027466 | 0.11444 | 0.068665 | 0.13275 | -0.004578 | 0.10986 | 0.027466 | -0.009155 | 121.6187 | -0.059509 | 121.669 | 121.7056 | 0.009156 | 121.582 | -0.032043 | 0.050354 | 121.5866 | 121.7011 | 121.6599 | 121.5912 | 121.669 | 121.6187 | 121.7239 | 121.582 | 121.5912 | 121.669 | 121.7239 | 121.6599 | 121.6187 | -0.032043 | -0.068664
511.6719 | 121.7606 | -121.582 | 0.07782 | -0.010758 | -0.0092307 | -0.014749 | 0.01988 | -0.0074405 | -0.0057294 | -6.6324e-05 | 0.10071 | -0.013733 | 0.054932 | 0.14648 | 0.09613 | 0.17395 | -0.041199 | 0.14191 | 0.009155 | -0.004578 | 121.637 | -0.091553 | 121.6827 | 121.7285 | 0.01831 | 121.5775 | -0.068665 | 0.045776 | 121.5408 | 121.7239 | 121.6782 | 121.5683 | 121.6827 | 121.5912 | 121.756 | 121.5775 | 121.5683 | 121.6827 | 121.756 | 121.6782 | 121.5912 | -0.022888 | -0.082398
512.6719 | 121.8018 | -121.5912 | 0.068665 | 0.0045015 | -0.012649 | -0.018167 | 0.01753 | -0.0082949 | -0.0055156 | 0.0010019 | 0.10986 | 0.009155 | 0.041199 | 0.19226 | 0.11902 | 0.19226 | -0.054932 | 0.16937 | 0.013733 | 0.009155 | 121.6324 | -0.05951 | 121.7011 | 121.7834 | 0.050354 | 121.6003 | -0.054932 | 0.068664 | 121.5363 | 121.7606 | 121.7102 | 121.6003 | 121.7011 | 121.6049 | 121.7834 | 121.6003 | 121.6003 | 121.7011 | 121.7834 | 121.7102 | 121.6049 | -0.027466 | -0.05951
513.6719 | 121.8155 | -121.5912 | 0.068665 | 0.0045015 | -0.012221 | -0.019448 | 0.020948 | -0.0095767 | -0.0074384 | -0.00070712 | 0.11902 | -0.027466 | 0.064087 | 0.20599 | 0.14648 | 0.21515 | -0.07782 | 0.17853 | -0.013733 | 0.018311 | 121.6553 | -0.096131 | 121.7102 | 121.7972 | 0.077819 | 121.6095 | -0.082398 | 0.054932 | 121.5134 | 121.7697 | 121.7377 | 121.5637 | 121.7102 | 121.5775 | 121.8063 | 121.6095 | 121.5637 | 121.7102 | 121.8063 | 121.7377 | 121.5775 | -0.004578 | -0.050354
514.6719 | 121.8201 | -121.5866 | 0.050354 | -0.003128 | -0.013503 | -0.015389 | 0.019239 | -0.0087223 | -0.0080792 | -0.0028433 | 0.12817 | -0.018311 | 0.073242 | 0.20599 | 0.14191 | 0.21057 | -0.091553 | 0.20142 | 0.009155 | 0.041199 | 121.6599 | -0.068665 | 121.7148 | 121.7926 | 0.091553 | 121.6278 | -0.041199 | 0.054932 | 121.4951 | 121.788 | 121.7285 | 121.5683 | 121.7148 | 121.5958 | 121.7972 | 121.6278 | 121.5683 | 121.7148 | 121.7972 | 121.7285 | 121.5958 | 0.022888 | -0.009155
515.6562 | 121.8521 | -121.6003 | 0.041199 | -0.003128 | -0.012862 | -0.020516 | 0.018384 | -0.0097903 | -0.005943 | 0.0012155 | 0.09613 | -0.013733 | 0.068665 | 0.19226 | 0.13275 | 0.23346 | -0.1236 | 0.17395 | -0.004578 | 0.036621 | 121.669 | -0.054932 | 121.6965 | 121.7926 | 0.091552 | 121.637 | -0.045777 | 0.027465 | 121.4767 | 121.7743 | 121.7331 | 121.5866 | 121.6965 | 121.5958 | 121.8338 | 121.637 | 121.5866 | 121.6965 | 121.8338 | 121.7331 | 121.5958 | 0.027466 | -0.004578
516.6719 | 121.8384 | -121.5958 | 0.041199 | 0.01213 | -0.012862 | -0.01603 | 0.022443 | -0.0076541 | -0.0063702 | 0.0010019 | 0.1236 | -0.018311 | 0.07782 | 0.21057 | 0.15106 | 0.2243 | -0.1236 | 0.20142 | -0.013733 | 0.045776 | 121.6736 | -0.05951 | 121.7194 | 121.8063 | 0.10986 | 121.6415 | -0.054932 | 0.045776 | 121.4722 | 121.7972 | 121.7468 | 121.5775 | 121.7194 | 121.582 | 121.8201 | 121.6415 | 121.5775 | 121.7194 | 121.8201 | 121.7468 | 121.582 | 0.036621 | 0.004577
517.6719 | 121.8292 | -121.6049 | 0.041199 | -0.003128 | -0.012435 | -0.019235 | 0.021589 | -0.01214 | -0.0063702 | 0.0029245 | 0.13275 | -0.018311 | 0.050354 | 0.2243 | 0.16022 | 0.2243 | -0.12817 | 0.21057 | -0.009155 | 0.036621 | 121.6553 | -0.05951 | 121.7377 | 121.8292 | 0.11902 | 121.6415 | -0.050354 | 0.082397 | 121.4767 | 121.8155 | 121.7651 | 121.5866 | 121.7377 | 121.5958 | 121.8292 | 121.6415 | 121.5866 | 121.7377 | 121.8292 | 121.7651 | 121.5958 | 0.009155 | -0.004578
518.6719 | 121.8521 | -121.6049 | 0.054932 | -0.010758 | -0.013717 | -0.016458 | 0.01988 | -0.0082949 | -0.005302 | -0.00027992 | 0.12817 | -0.027466 | 0.082397 | 0.22888 | 0.16937 | 0.22888 | -0.12817 | 0.22888 | -0.004578 | 0.050354 | 121.6873 | -0.082398 | 121.7331 | 121.8338 | 0.11444 | 121.6553 | -0.05951 | 0.045777 | 121.4767 | 121.8338 | 121.7743 | 121.5775 | 121.7331 | 121.6003 | 121.8338 | 121.6553 | 121.5775 | 121.7331 | 121.8338 | 121.7743 | 121.6003 | 0.027465 | -0.004578
519.6562 | 121.7514 | -121.6553 | 0.07782 | -0.003128 | -0.012008 | -0.017953 | 0.020521 | -0.0082949 | -0.005302 | 0.00014748 | 0.082397 | 0.004578 | 0.050354 | 0.1236 | 0.068665 | 0.1236 | 0.004578 | 0.10071 | 0.041199 | -0.004578 | 121.7056 | -0.073242 | 121.7377 | 121.7789 | -0.009155 | 121.6507 | -0.036621 | 0.032043 | 121.6599 | 121.756 | 121.7239 | 121.6599 | 121.7377 | 121.6965 | 121.7789 | 121.6507 | 121.6599 | 121.7377 | 121.7789 | 121.7239 | 121.6965 | -0.027466 | -0.082398
520.6562 | 121.7331 | -121.6095 | 0.073242 | 0.0045015 | -0.012008 | -0.021157 | 0.022871 | -0.011286 | -0.0029522 | 0.0014291 | 0.082397 | 0.009155 | 0.041199 | 0.13733 | 0.086975 | 0.13275 | -0.004578 | 0.10986 | 0.022888 | 0.004578 | 121.6507 | -0.064087 | 121.6919 | 121.7468 | 0.013733 | 121.6141 | -0.050354 | 0.041198 | 121.6049 | 121.7194 | 121.6965 | 121.6187 | 121.6919 | 121.6324 | 121.7422 | 121.6141 | 121.6187 | 121.6919 | 121.7422 | 121.6965 | 121.6324 | -0.032043 | -0.068664
521.6562 | 121.7514 | -121.6599 | 0.073242 | 0.0045015 | -0.01094 | -0.01603 | 0.021589 | -0.011286 | -0.005302 | 0.0037791 | 0.064087 | 0 | 0.054932 | 0.15564 | 0.086975 | 0.13275 | 0 | 0.091553 | 0.018311 | 0.013733 | 121.7148 | -0.073242 | 121.7239 | 121.8155 | 0.013733 | 121.6736 | -0.054931 | 0.009155 | 121.6599 | 121.7514 | 121.7468 | 121.6599 | 121.7239 | 121.6782 | 121.7926 | 121.6736 | 121.6599 | 121.7239 | 121.7926 | 121.7468 | 121.6782 | -0.01831 | -0.059509
522.6562 | 121.8704 | -121.6415 | 0.054932 | 0.0045015 | -0.014571 | -0.02073 | 0.017957 | -0.011072 | -0.0057294 | -0.00070712 | 0.11902 | -0.004578 | 0.054932 | 0.20599 | 0.14648 | 0.22888 | -0.13275 | 0.20142 | -0.009155 | 0.054932 | 121.6965 | -0.05951 | 121.7606 | 121.8475 | 0.091552 | 121.6965 | -0.064087 | 0.064087 | 121.5088 | 121.843 | 121.788 | 121.637 | 121.7606 | 121.6324 | 121.8704 | 121.6965 | 121.637 | 121.7606 | 121.8704 | 121.788 | 121.6324 | 0 | 0
523.6719 | 121.8796 | -121.6141 | 0.041199 | 0.0045015 | -0.010512 | -0.017739 | 0.021375 | -0.010859 | -0.0085064 | 0.00078828 | 0.12817 | -0.009155 | 0.068665 | 0.23346 | 0.16479 | 0.24719 | -0.14191 | 0.21515 | -0.027466 | 0.027466 | 121.6827 | -0.050354 | 121.7422 | 121.8475 | 0.1236 | 121.6415 | -0.068665 | 0.059509 | 121.4722 | 121.8292 | 121.7789 | 121.6049 | 121.7422 | 121.5866 | 121.8613 | 121.6415 | 121.6049 | 121.7422 | 121.8613 | 121.7789 | 121.5866 | 0.027466 | -0.013733
524.6719 | 121.8567 | -121.6187 | 0.050354 | 0.01213 | -0.014358 | -0.018594 | 0.018384 | -0.011499 | -0.0072246 | 0.0010019 | 0.13275 | -0.013733 | 0.068665 | 0.21515 | 0.15564 | 0.2243 | -0.10529 | 0.19226 | -0.027466 | 0.036621 | 121.6873 | -0.064087 | 121.7514 | 121.8338 | 0.10529 | 121.6553 | -0.07782 | 0.064086 | 121.5134 | 121.8109 | 121.7743 | 121.6049 | 121.7514 | 121.5912 | 121.843 | 121.6553 | 121.6049 | 121.7514 | 121.843 | 121.7743 | 121.5912 | 0.018311 | -0.013733
525.6719 | 121.8567 | -121.6278 | 0.054932 | -0.010758 | -0.013076 | -0.011758 | 0.019666 | -0.0089359 | -0.0063702 | 0.00036108 | 0.13275 | -0.009155 | 0.068665 | 0.21515 | 0.14648 | 0.2243 | -0.10071 | 0.19226 | 0.013733 | 0.032043 | 121.6965 | -0.064087 | 121.7606 | 121.843 | 0.091552 | 121.6599 | -0.041199 | 0.064086 | 121.5271 | 121.8201 | 121.7743 | 121.6187 | 121.7606 | 121.6415 | 121.8521 | 121.6599 | 121.6187 | 121.7606 | 121.8521 | 121.7743 | 121.6415 | 0.013733 | -0.022889
526.6562 | 121.7377 | -121.6507 | 0.073242 | -0.003128 | -0.0096579 | -0.015603 | 0.023084 | -0.0095767 | -0.007011 | 0.00078828 | 0.022888 | 0.032043 | 0.036621 | 0.10071 | 0.036621 | 0.091553 | 0.059509 | 0.064087 | 0.036621 | -0.004578 | 121.6873 | -0.041199 | 121.6736 | 121.7514 | -0.036621 | 121.6461 | -0.036621 | -0.013733 | 121.7102 | 121.7148 | 121.6873 | 121.6827 | 121.6736 | 121.6873 | 121.7422 | 121.6461 | 121.6827 | 121.6736 | 121.7422 | 121.6873 | 121.6873 | -0.036621 | -0.07782
527.6562 | 121.7422 | -121.6782 | 0.073242 | -0.003128 | -0.011367 | -0.015389 | 0.022016 | -0.0082949 | -0.0085064 | -0.0017751 | 0.027466 | 0.036621 | 0.022888 | 0.086975 | 0.036621 | 0.082397 | 0.059509 | 0.059509 | 0.032043 | -0.018311 | 121.701 | -0.036621 | 121.7056 | 121.7651 | -0.036621 | 121.6599 | -0.041199 | 0.004578 | 121.7377 | 121.7377 | 121.7148 | 121.7148 | 121.7056 | 121.7102 | 121.7606 | 121.6599 | 121.7148 | 121.7056 | 121.7606 | 121.7148 | 121.7102 | -0.050354 | -0.091553
528.6562 | 121.7468 | -121.6965 | 0.07782 | -0.003128 | -0.0094443 | -0.014962 | 0.023084 | -0.0074405 | -0.0067974 | 0.0010019 | 0.032043 | 0.050354 | 0.045776 | 0.082397 | 0.032043 | 0.09613 | 0.064087 | 0.054932 | 0.041199 | -0.022888 | 121.7422 | -0.027466 | 121.7285 | 121.7789 | -0.045777 | 121.6736 | -0.036621 | -0.013733 | 121.7606 | 121.7514 | 121.7285 | 121.7468 | 121.7285 | 121.7377 | 121.7926 | 121.6736 | 121.7468 | 121.7285 | 121.7926 | 121.7285 | 121.7377 | -0.032044 | -0.10071
529.6562 | 121.8842 | -121.6415 | 0.036621 | 0.0045015 | -0.011794 | -0.017098 | 0.017957 | -0.0089359 | -0.0057294 | 0.0018565 | 0.13275 | -0.032043 | 0.068665 | 0.21515 | 0.17853 | 0.23346 | -0.13275 | 0.21057 | 0 | 0.050354 | 121.7102 | -0.068664 | 121.7743 | 121.8567 | 0.14191 | 121.6919 | -0.036621 | 0.064086 | 121.5088 | 121.8521 | 121.8201 | 121.6095 | 121.7743 | 121.6415 | 121.875 | 121.6919 | 121.6095 | 121.7743 | 121.875 | 121.8201 | 121.6415 | 0.032044 | 0.013733
530.6719 | 121.8475 | -121.6003 | 0.041199 | 0.0045015 | -0.012649 | -0.019021 | 0.01988 | -0.011286 | -0.0063702 | 0.00078828 | 0.1236 | -0.018311 | 0.068665 | 0.21515 | 0.15564 | 0.21057 | -0.082397 | 0.19684 | 0.027466 | 0.027466 | 121.669 | -0.05951 | 121.7239 | 121.8155 | 0.11444 | 121.6278 | -0.013733 | 0.054931 | 121.5179 | 121.7972 | 121.756 | 121.582 | 121.7239 | 121.6278 | 121.8109 | 121.6278 | 121.582 | 121.7239 | 121.8109 | 121.756 | 121.6278 | 0.027466 | -0.013733
531.6719 | 121.7697 | -121.6415 | 0.064087 | -0.018387 | -0.0083763 | -0.019021 | 0.021802 | -0.0095767 | -0.0044476 | 0.00057468 | 0.064087 | 0.032043 | 0.050354 | 0.10071 | 0.050354 | 0.11902 | 0.022888 | 0.086975 | 0.018311 | -0.009155 | 121.6919 | -0.032044 | 121.7056 | 121.7422 | -0.013733 | 121.6324 | -0.045776 | 0.013733 | 121.6644 | 121.7285 | 121.6919 | 121.6736 | 121.7056 | 121.6599 | 121.7606 | 121.6324 | 121.6736 | 121.7056 | 121.7606 | 121.6919 | 121.6599 | -0.013733 | -0.073242
532.6719 | 121.7697 | -121.6507 | 0.07782 | -0.010758 | -0.0081625 | -0.013894 | 0.02223 | -0.0080813 | -0.0057294 | 0.00078828 | 0.059509 | 0 | 0.059509 | 0.10071 | 0.050354 | 0.11902 | 0.036621 | 0.09613 | 0.032043 | 0.013733 | 121.7102 | -0.07782 | 121.7102 | 121.7514 | -0.027466 | 121.6644 | -0.045777 | 0 | 121.6873 | 121.7468 | 121.701 | 121.6507 | 121.7102 | 121.6827 | 121.7697 | 121.6644 | 121.6507 | 121.7102 | 121.7697 | 121.701 | 121.6827 | -0.018311 | -0.064087
533.6562 | 121.7743 | -121.6507 | 0.07782 | -0.003128 | -0.0085899 | -0.016244 | 0.025007 | -0.0093631 | -0.0061566 | 0.0037791 | 0.032043 | 0.036621 | 0.022888 | 0.10529 | 0.041199 | 0.10986 | 0.050354 | 0.07782 | 0.045776 | 0.013733 | 121.6736 | -0.041199 | 121.6827 | 121.756 | -0.036621 | 121.6644 | -0.032044 | 0.009155 | 121.701 | 121.7285 | 121.6919 | 121.6873 | 121.6827 | 121.6965 | 121.7606 | 121.6644 | 121.6873 | 121.6827 | 121.7606 | 121.6919 | 121.6965 | -0.054932 | -0.064087
534.6562 | 121.7834 | -121.6507 | 0.073242 | 0.0045015 | -0.0077353 | -0.016671 | 0.022871 | -0.0076541 | -0.0080792 | 0.00036108 | 0.027466 | 0.032043 | 0.036621 | 0.09613 | 0.032043 | 0.10986 | 0.050354 | 0.082397 | 0.041199 | 0.009155 | 121.6873 | -0.041199 | 121.6782 | 121.7468 | -0.041199 | 121.6599 | -0.032043 | -0.009155 | 121.701 | 121.7331 | 121.6827 | 121.6827 | 121.6782 | 121.6919 | 121.7606 | 121.6599 | 121.6827 | 121.6782 | 121.7606 | 121.6827 | 121.6919 | -0.036621 | -0.064087
535.6562 | 121.7834 | -121.6644 | 0.091553 | -0.003128 | -0.010299 | -0.01838 | 0.020521 | -0.0078677 | -0.007011 | 0.0012155 | 0.041199 | 0.059509 | 0.032043 | 0.09613 | 0.050354 | 0.11902 | 0.050354 | 0.07782 | 0.050354 | 0.009155 | 121.6965 | -0.032044 | 121.7056 | 121.7606 | -0.041199 | 121.6736 | -0.041199 | 0.009156 | 121.7148 | 121.7422 | 121.7148 | 121.7239 | 121.7056 | 121.7148 | 121.7834 | 121.6736 | 121.7239 | 121.7056 | 121.7834 | 121.7148 | 121.7148 | -0.05951 | -0.082398
536.6562 | 121.8796 | -121.6461 | 0.050354 | -0.003128 | -0.010512 | -0.016458 | 0.017957 | -0.0095767 | -0.0065838 | 0.0020701 | 0.11902 | -0.013733 | 0.064087 | 0.19684 | 0.16022 | 0.23346 | -0.091553 | 0.19226 | 0 | 0.036621 | 121.7102 | -0.064087 | 121.7651 | 121.843 | 0.10986 | 121.6827 | -0.050354 | 0.054932 | 121.5546 | 121.8384 | 121.8063 | 121.6324 | 121.7651 | 121.6461 | 121.8796 | 121.6827 | 121.6324 | 121.7651 | 121.8796 | 121.8063 | 121.6461 | 0.013733 | -0.013733
537.6719 | 121.7743 | -121.6644 | 0.091553 | 0.0045015 | -0.0090171 | -0.013467 | 0.023084 | -0.0093631 | -0.0048748 | 0.0012155 | 0.022888 | 0.050354 | 0.036621 | 0.082397 | 0.041199 | 0.10071 | 0.068665 | 0.082397 | 0.032043 | 0.004578 | 121.701 | -0.041199 | 121.6873 | 121.7468 | -0.050354 | 121.669 | -0.05951 | -0.013733 | 121.7331 | 121.7468 | 121.7056 | 121.7148 | 121.6873 | 121.6965 | 121.7651 | 121.669 | 121.7148 | 121.6873 | 121.7651 | 121.7056 | 121.6965 | -0.054932 | -0.086975
538.6719 | 121.7743 | -121.6919 | 0.073242 | -0.003128 | -0.0073081 | -0.017953 | 0.02223 | -0.0078677 | -0.007011 | 0.0027109 | 0.027466 | 0.041199 | 0.045776 | 0.082397 | 0.036621 | 0.10529 | 0.07782 | 0.064087 | 0.032043 | 0 | 121.7377 | -0.032043 | 121.7194 | 121.7743 | -0.036621 | 121.6919 | -0.041199 | -0.01831 | 121.7697 | 121.756 | 121.7285 | 121.7331 | 121.7194 | 121.7239 | 121.7972 | 121.6919 | 121.7331 | 121.7194 | 121.7972 | 121.7285 | 121.7239 | -0.027466 | -0.073242
539.6719 | 121.7743 | -121.669 | 0.068665 | -0.010758 | -0.011367 | -0.016244 | 0.018384 | -0.0070133 | -0.007011 | -0.00092072 | 0.027466 | 0.041199 | 0.036621 | 0.09613 | 0.041199 | 0.10986 | 0.054932 | 0.07782 | 0.036621 | -0.004578 | 121.7056 | -0.027466 | 121.6965 | 121.7651 | -0.027466 | 121.6644 | -0.032044 | -0.009155 | 121.7239 | 121.7468 | 121.7102 | 121.7102 | 121.6965 | 121.7056 | 121.7789 | 121.6644 | 121.7102 | 121.6965 | 121.7789 | 121.7102 | 121.7056 | -0.032044 | -0.073243
540.6562 | 121.8246 | -121.6507 | 0.068665 | 0.0045015 | -0.0096579 | -0.017739 | 0.020734 | -0.0070133 | -0.005943 | -0.00070712 | 0.041199 | 0.041199 | 0.054932 | 0.10529 | 0.050354 | 0.11444 | 0.041199 | 0.07782 | 0.032043 | -0.013733 | 121.7056 | -0.027466 | 121.6919 | 121.756 | -0.018311 | 121.637 | -0.036622 | -0.013733 | 121.6919 | 121.7285 | 121.701 | 121.6919 | 121.6919 | 121.6827 | 121.7651 | 121.637 | 121.6919 | 121.6919 | 121.7651 | 121.701 | 121.6827 | -0.013733 | -0.082398
541.6562 | 121.7789 | -121.6553 | 0.07782 | 0.0045015 | -0.0094443 | -0.011971 | 0.020307 | -0.0061587 | -0.005943 | -0.0013479 | 0.022888 | 0.045776 | 0.032043 | 0.086975 | 0.045776 | 0.10071 | 0.050354 | 0.068665 | 0.036621 | -0.004578 | 121.6873 | -0.032044 | 121.6782 | 121.7422 | -0.032044 | 121.6507 | -0.041199 | -0.009155 | 121.7056 | 121.7239 | 121.701 | 121.701 | 121.6782 | 121.6919 | 121.756 | 121.6507 | 121.701 | 121.6782 | 121.756 | 121.701 | 121.6919 | -0.045777 | -0.082398
542.6562 | 121.8018 | -121.6782 | 0.07782 | -0.003128 | -0.0090171 | -0.014962 | 0.020307 | -0.0078677 | -0.0061566 | 0.00057468 | 0.022888 | 0.045776 | 0.036621 | 0.086975 | 0.032043 | 0.10071 | 0.050354 | 0.059509 | 0.041199 | 0 | 121.7148 | -0.032044 | 121.701 | 121.7651 | -0.045777 | 121.6782 | -0.036621 | -0.013733 | 121.7285 | 121.7377 | 121.7102 | 121.7239 | 121.701 | 121.7194 | 121.7789 | 121.6782 | 121.7239 | 121.701 | 121.7789 | 121.7102 | 121.7194 | -0.041199 | -0.07782
543.6562 | 121.9025 | -121.637 | 0.050354 | -0.003128 | -0.011153 | -0.014962 | 0.018812 | -0.0093631 | -0.0063702 | 0.0012155 | 0.10986 | -0.022888 | 0.07782 | 0.21515 | 0.15564 | 0.23346 | -0.1236 | 0.20599 | -0.018311 | 0.041199 | 121.7148 | -0.073242 | 121.7468 | 121.8521 | 0.10529 | 121.6782 | -0.068665 | 0.032043 | 121.5134 | 121.843 | 121.7926 | 121.6141 | 121.7468 | 121.6187 | 121.8704 | 121.6782 | 121.6141 | 121.7468 | 121.8704 | 121.7926 | 121.6187 | 0.027466 | -0.009155
544.6719 | 121.8658 | -121.6507 | 0.054932 | -0.003128 | -0.01094 | -0.01838 | 0.019025 | -0.010218 | -0.0050884 | 0.00036108 | 0.11902 | -0.013733 | 0.064087 | 0.17395 | 0.12817 | 0.20599 | -0.064087 | 0.18768 | 0 | 0.022888 | 121.7148 | -0.068665 | 121.7697 | 121.8246 | 0.073242 | 121.6736 | -0.054932 | 0.054932 | 121.5866 | 121.8384 | 121.7789 | 121.637 | 121.7697 | 121.6507 | 121.8567 | 121.6736 | 121.637 | 121.7697 | 121.8567 | 121.7789 | 121.6507 | 0.009155 | -0.032044
545.6719 | 121.8063 | -121.7056 | 0.082397 | -0.018387 | -0.013503 | -0.017739 | 0.01988 | -0.0085085 | -0.0057294 | 0.0027109 | 0.073242 | 0 | 0.041199 | 0.10986 | 0.059509 | 0.12817 | 0.027466 | 0.086975 | 0.036621 | -0.013733 | 121.7468 | -0.082397 | 121.7789 | 121.8155 | -0.022888 | 121.6919 | -0.045776 | 0.032043 | 121.7331 | 121.7926 | 121.7651 | 121.7056 | 121.7789 | 121.7422 | 121.8338 | 121.6919 | 121.7056 | 121.7789 | 121.8338 | 121.7651 | 121.7422 | -0.041198 | -0.09613
546.6719 | 121.8201 | -121.701 | 0.059509 | -0.010758 | -0.0098715 | -0.015389 | 0.021162 | -0.0095767 | -0.005943 | -0.0011343 | 0.091553 | 0 | 0.064087 | 0.1236 | 0.082397 | 0.15106 | 0 | 0.13275 | 0.018311 | -0.004578 | 121.7651 | -0.059509 | 121.7926 | 121.8246 | 0.022888 | 121.6965 | -0.041198 | 0.027466 | 121.701 | 121.8338 | 121.7834 | 121.701 | 121.7926 | 121.7194 | 121.8521 | 121.6965 | 121.701 | 121.7926 | 121.8521 | 121.7834 | 121.7194 | 0.004578 | -0.064087
547.6562 | 121.7789 | -121.7194 | 0.082397 | 0.0045015 | -0.0090171 | -0.020089 | 0.019025 | -0.010859 | -0.0061566 | 0.0022837 | 0.032043 | 0.050354 | 0.045776 | 0.082397 | 0.027466 | 0.091553 | 0.07782 | 0.064087 | 0.036621 | -0.009155 | 121.7651 | -0.032043 | 121.7514 | 121.8018 | -0.054931 | 121.7102 | -0.045776 | -0.013733 | 121.7972 | 121.7834 | 121.7468 | 121.7697 | 121.7514 | 121.756 | 121.8109 | 121.7102 | 121.7697 | 121.7514 | 121.8109 | 121.7468 | 121.756 | -0.036621 | -0.091552
548.6562 | 121.7972 | -121.7148 | 0.068665 | -0.018387 | -0.01094 | -0.016885 | 0.021162 | -0.0095767 | -0.00872 | 0.0018565 | 0.027466 | 0.027466 | 0.022888 | 0.07782 | 0.022888 | 0.10986 | 0.07782 | 0.082397 | 0.041199 | -0.009155 | 121.7377 | -0.041199 | 121.7422 | 121.7926 | -0.045777 | 121.7056 | -0.027466 | 0.004578 | 121.7926 | 121.7972 | 121.7377 | 121.7422 | 121.7422 | 121.756 | 121.8246 | 121.7056 | 121.7422 | 121.7422 | 121.8246 | 121.7377 | 121.756 | -0.045777 | -0.07782
549.6562 | 121.9482 | -121.6919 | 0.045776 | 0.01213 | -0.014144 | -0.018167 | 0.016889 | -0.0076541 | -0.0063702 | 0.0014291 | 0.1236 | -0.032043 | 0.059509 | 0.20142 | 0.16479 | 0.26093 | -0.13275 | 0.2243 | 0.009155 | 0.032043 | 121.7514 | -0.077819 | 121.8155 | 121.8933 | 0.11902 | 121.7239 | -0.036621 | 0.064087 | 121.5591 | 121.9162 | 121.8567 | 121.6599 | 121.8155 | 121.7011 | 121.9528 | 121.7239 | 121.6599 | 121.8155 | 121.9528 | 121.8567 | 121.7011 | 0.013733 | -0.013733
550.6562 | 121.9528 | -121.6782 | 0.036621 | -0.003128 | -0.013717 | -0.017098 | 0.019666 | -0.011499 | -0.005302 | -0.0011343 | 0.11902 | -0.027466 | 0.054932 | 0.21973 | 0.16479 | 0.25177 | -0.14191 | 0.23346 | -0.009155 | 0.041199 | 121.7331 | -0.064087 | 121.7972 | 121.8979 | 0.12817 | 121.7194 | -0.045776 | 0.064087 | 121.5363 | 121.9116 | 121.843 | 121.6507 | 121.7972 | 121.669 | 121.9299 | 121.7194 | 121.6507 | 121.7972 | 121.9299 | 121.843 | 121.669 | 0.018311 | 0.004578
551.6719 | 121.8979 | -121.6644 | 0.059509 | 0.0045015 | -0.010299 | -0.017098 | 0.019239 | -0.011286 | -0.0063702 | -0.00027992 | 0.10986 | -0.009155 | 0.07782 | 0.19226 | 0.13733 | 0.20142 | -0.054932 | 0.18768 | 0 | 0.027466 | 121.7422 | -0.068664 | 121.7743 | 121.8567 | 0.07782 | 121.6919 | -0.059509 | 0.032043 | 121.6095 | 121.8521 | 121.8018 | 121.6553 | 121.7743 | 121.6644 | 121.8658 | 121.6919 | 121.6553 | 121.7743 | 121.8658 | 121.8018 | 121.6644 | 0.018311 | -0.032043
552.6719 | 121.9116 | -121.6965 | 0.045776 | -0.003128 | -0.010726 | -0.016244 | 0.01988 | -0.0095767 | -0.0078656 | 0.0014291 | 0.1236 | -0.032043 | 0.073242 | 0.18768 | 0.15106 | 0.21515 | -0.10071 | 0.20142 | -0.004578 | 0.036621 | 121.7697 | -0.077819 | 121.8201 | 121.8842 | 0.10529 | 121.7331 | -0.050354 | 0.050354 | 121.5958 | 121.8979 | 121.8475 | 121.6644 | 121.8201 | 121.6919 | 121.9116 | 121.7331 | 121.6644 | 121.8201 | 121.9116 | 121.8475 | 121.6919 | 0.027466 | -0.009155
553.6719 | 121.9574 | -121.6827 | 0.045776 | -0.003128 | -0.012862 | -0.014749 | 0.021802 | -0.010645 | -0.007011 | 0.0016427 | 0.11902 | -0.009155 | 0.073242 | 0.20599 | 0.14648 | 0.23346 | -0.11444 | 0.21057 | -0.027466 | 0.036621 | 121.756 | -0.054931 | 121.8018 | 121.8887 | 0.10071 | 121.7194 | -0.073242 | 0.045777 | 121.5683 | 121.8933 | 121.8292 | 121.6736 | 121.8018 | 121.6553 | 121.9162 | 121.7194 | 121.6736 | 121.8018 | 121.9162 | 121.8292 | 121.6553 | 0.027466 | -0.009155
554.6562 | 121.8109 | -121.7194 | 0.07782 | -0.003128 | -0.010726 | -0.018807 | 0.020521 | -0.010431 | -0.0063702 | 0.0010019 | 0.050354 | 0.027466 | 0.054932 | 0.10071 | 0.045776 | 0.10986 | 0.022888 | 0.082397 | 0.027466 | 0.004578 | 121.7743 | -0.050354 | 121.7697 | 121.8201 | -0.032044 | 121.7239 | -0.050354 | -0.004578 | 121.7422 | 121.8018 | 121.7651 | 121.7468 | 121.7697 | 121.7468 | 121.8292 | 121.7239 | 121.7468 | 121.7697 | 121.8292 | 121.7651 | 121.7468 | -0.022888 | -0.073242
555.6562 | 121.8246 | -121.7331 | 0.086975 | -0.018387 | -0.012008 | -0.017312 | 0.023298 | -0.0093631 | -0.0072246 | 0.0010019 | 0.073242 | 0.018311 | 0.054932 | 0.10986 | 0.064087 | 0.13733 | 0.018311 | 0.09613 | 0.022888 | -0.013733 | 121.788 | -0.068664 | 121.8063 | 121.843 | -0.022888 | 121.7194 | -0.064087 | 0.01831 | 121.7514 | 121.8292 | 121.7972 | 121.7514 | 121.8063 | 121.756 | 121.8704 | 121.7194 | 121.7514 | 121.8063 | 121.8704 | 121.7972 | 121.756 | -0.032043 | -0.10071
556.6562 | 121.9528 | -121.6965 | 0.027466 | -0.003128 | -0.013503 | -0.01838 | 0.016248 | -0.010645 | -0.0063702 | 0.0016427 | 0.09613 | -0.004578 | 0.068665 | 0.20142 | 0.14191 | 0.23346 | -0.1236 | 0.20599 | 0.009155 | 0.036621 | 121.7651 | -0.032044 | 121.7926 | 121.8979 | 0.11444 | 121.7331 | -0.018311 | 0.027465 | 121.5729 | 121.9025 | 121.8384 | 121.6919 | 121.7926 | 121.7056 | 121.9299 | 121.7331 | 121.6919 | 121.7926 | 121.9299 | 121.8384 | 121.7056 | 0.041199 | 0.009155
557.6562 | 121.9528 | -121.6827 | 0.054932 | -0.003128 | -0.013076 | -0.016244 | 0.017316 | -0.010004 | -0.005943 | -0.00027992 | 0.07782 | -0.045776 | 0.027466 | 0.19226 | 0.13733 | 0.21973 | -0.1236 | 0.19226 | 0 | 0.050354 | 121.7102 | -0.10071 | 121.7606 | 121.875 | 0.082397 | 121.7331 | -0.054932 | 0.050354 | 121.5591 | 121.875 | 121.8201 | 121.637 | 121.7606 | 121.6827 | 121.9025 | 121.7331 | 121.637 | 121.7606 | 121.9025 | 121.8201 | 121.6827 | -0.027466 | -0.004578
558.6719 | 121.9437 | -121.7194 | 0.050354 | -0.010758 | -0.012435 | -0.017312 | 0.020093 | -0.0097903 | -0.0031658 | 0.0014291 | 0.1236 | -0.018311 | 0.068665 | 0.23346 | 0.16479 | 0.23346 | -0.12817 | 0.21057 | -0.013733 | 0.027466 | 121.788 | -0.068665 | 121.843 | 121.9528 | 0.11444 | 121.7468 | -0.064087 | 0.054931 | 121.5912 | 121.9299 | 121.8842 | 121.701 | 121.843 | 121.7056 | 121.9528 | 121.7468 | 121.701 | 121.843 | 121.9528 | 121.8842 | 121.7056 | 0.018311 | -0.022888
559.6719 | 121.9482 | -121.7056 | 0.036621 | -0.003128 | -0.015426 | -0.015389 | 0.020307 | -0.012568 | -0.0057294 | 0.00036108 | 0.13275 | -0.004578 | 0.068665 | 0.21973 | 0.16937 | 0.2243 | -0.13275 | 0.23346 | -0.018311 | 0.032043 | 121.7743 | -0.041199 | 121.8384 | 121.9254 | 0.13275 | 121.7377 | -0.054932 | 0.064086 | 121.5729 | 121.9391 | 121.875 | 121.701 | 121.8384 | 121.6873 | 121.9299 | 121.7377 | 121.701 | 121.8384 | 121.9299 | 121.875 | 121.6873 | 0.032044 | -0.004578
560.6719 | 121.9666 | -121.6965 | 0.041199 | 0.0045015 | -0.014358 | -0.016671 | 0.022443 | -0.010859 | -0.0072246 | 0.0010019 | 0.1236 | -0.027466 | 0.050354 | 0.21973 | 0.16937 | 0.22888 | -0.13733 | 0.21515 | -0.018311 | 0.041199 | 121.7468 | -0.068665 | 121.8201 | 121.9162 | 0.12817 | 121.7377 | -0.05951 | 0.073242 | 121.5591 | 121.9116 | 121.8658 | 121.669 | 121.8201 | 121.6782 | 121.9254 | 121.7377 | 121.669 | 121.8201 | 121.9254 | 121.8658 | 121.6782 | 0.009155 | 0
561.6562 | 121.8796 | -121.7422 | 0.07782 | 0.0045015 | -0.01158 | -0.01304 | 0.021802 | -0.011286 | -0.007011 | 0.00014748 | 0.10071 | 0.004578 | 0.050354 | 0.16479 | 0.10529 | 0.16022 | -0.022888 | 0.13275 | 0.004578 | 0.022888 | 121.7926 | -0.073242 | 121.843 | 121.907 | 0.027466 | 121.7651 | -0.073242 | 0.050354 | 121.7194 | 121.875 | 121.8475 | 121.7468 | 121.843 | 121.7468 | 121.9025 | 121.7651 | 121.7468 | 121.843 | 121.9025 | 121.8475 | 121.7468 | -0.027466 | -0.054932
562.6562 | 121.907 | -121.7331 | 0.064087 | -0.003128 | -0.01094 | -0.012185 | 0.021375 | -0.010004 | -0.0082928 | 0.00036108 | 0.12817 | -0.027466 | 0.064087 | 0.1831 | 0.13275 | 0.17853 | -0.041199 | 0.16479 | 0 | 0.018311 | 121.7972 | -0.091553 | 121.8613 | 121.9162 | 0.068664 | 121.7514 | -0.064087 | 0.064087 | 121.6919 | 121.8979 | 121.8658 | 121.7056 | 121.8613 | 121.7331 | 121.9116 | 121.7514 | 121.7056 | 121.8613 | 121.9116 | 121.8658 | 121.7331 | 0 | -0.045776
563.6562 | 121.9528 | -121.7148 | 0.045776 | -0.003128 | -0.011794 | -0.019235 | 0.01988 | -0.0097903 | -0.003593 | 0.0014291 | 0.054932 | -0.036621 | 0.036621 | 0.1831 | 0.13733 | 0.20599 | -0.11444 | 0.1831 | -0.009155 | 0.013733 | 121.7514 | -0.082397 | 121.7697 | 121.8979 | 0.091553 | 121.7285 | -0.054931 | 0.018311 | 121.6003 | 121.8979 | 121.8521 | 121.6782 | 121.7697 | 121.7056 | 121.9208 | 121.7285 | 121.6782 | 121.7697 | 121.9208 | 121.8521 | 121.7056 | -0.009155 | -0.032043
564.6719 | 121.9757 | -121.7194 | 0.045776 | -0.003128 | -0.011794 | -0.023721 | 0.020093 | -0.011286 | -0.007652 | 0.00057468 | 0.11444 | -0.027466 | 0.064087 | 0.21973 | 0.15564 | 0.24719 | -0.14191 | 0.2243 | -0.013733 | 0.032043 | 121.7834 | -0.073242 | 121.8338 | 121.9391 | 0.10986 | 121.7514 | -0.059509 | 0.050354 | 121.5775 | 121.9437 | 121.875 | 121.6919 | 121.8338 | 121.7056 | 121.9666 | 121.7514 | 121.6919 | 121.8338 | 121.9666 | 121.875 | 121.7056 | 0.018311 | -0.013733
565.6719 | 121.9666 | -121.7194 | 0.050354 | -0.010758 | -0.012435 | -0.019876 | 0.020093 | -0.011286 | -0.0080792 | 0.00014748 | 0.13275 | -0.050354 | 0.068665 | 0.21973 | 0.17853 | 0.25177 | -0.13275 | 0.21973 | -0.009155 | 0.032043 | 121.788 | -0.10071 | 121.8521 | 121.9391 | 0.12817 | 121.7514 | -0.059509 | 0.064086 | 121.5866 | 121.9391 | 121.8979 | 121.669 | 121.8521 | 121.7102 | 121.9711 | 121.7514 | 121.669 | 121.8521 | 121.9711 | 121.8979 | 121.7102 | 0.018311 | -0.018311
566.6719 | 121.9849 | -121.6965 | 0.036621 | -0.018387 | -0.012649 | -0.018167 | 0.019453 | -0.011499 | -0.0074384 | -0.0011343 | 0.13275 | -0.032043 | 0.045776 | 0.24261 | 0.17853 | 0.26093 | -0.14648 | 0.21973 | -0.004578 | 0.041199 | 121.7422 | -0.068664 | 121.8292 | 121.9391 | 0.14191 | 121.7377 | -0.041199 | 0.086975 | 121.55 | 121.9162 | 121.875 | 121.6644 | 121.8292 | 121.6919 | 121.9574 | 121.7377 | 121.6644 | 121.8292 | 121.9574 | 121.875 | 121.6919 | 0.009155 | 0.004578
567.6719 | 121.9894 | -121.6919 | 0.041199 | 0.0045015 | -0.013076 | -0.017526 | 0.022016 | -0.01214 | -0.005943 | 0.00078828 | 0.11902 | -0.013733 | 0.045776 | 0.22888 | 0.16479 | 0.26093 | -0.14191 | 0.22888 | -0.013733 | 0.050354 | 121.7377 | -0.054932 | 121.8109 | 121.9208 | 0.1236 | 121.7422 | -0.054932 | 0.073243 | 121.55 | 121.9208 | 121.8567 | 121.6782 | 121.8109 | 121.6782 | 121.9528 | 121.7422 | 121.6782 | 121.8109 | 121.9528 | 121.8567 | 121.6782 | 0.004577 | 0.009155
568.6562 | 121.9666 | -121.7422 | 0.059509 | -0.003128 | -0.013076 | -0.014962 | 0.020093 | -0.011499 | -0.0057294 | 0.00078828 | 0.1236 | -0.018311 | 0.086975 | 0.22888 | 0.16022 | 0.21515 | -0.1236 | 0.21973 | 0.009155 | 0.041199 | 121.8292 | -0.07782 | 121.8658 | 121.9711 | 0.10071 | 121.7834 | -0.050354 | 0.036621 | 121.6187 | 121.962 | 121.9025 | 121.7239 | 121.8658 | 121.7514 | 121.9574 | 121.7834 | 121.7239 | 121.8658 | 121.9574 | 121.9025 | 121.7514 | 0.027466 | -0.01831
569.6562 | 121.9849 | -121.7422 | 0.045776 | -0.003128 | -0.013289 | -0.016671 | 0.022016 | -0.010004 | -0.0080792 | 0.0014291 | 0.1236 | -0.013733 | 0.082397 | 0.23346 | 0.16479 | 0.23346 | -0.13733 | 0.22888 | -0.013733 | 0.036621 | 121.8246 | -0.059509 | 121.8658 | 121.9757 | 0.11902 | 121.7789 | -0.059509 | 0.041199 | 121.6049 | 121.9711 | 121.907 | 121.7285 | 121.8658 | 121.7285 | 121.9757 | 121.7789 | 121.7285 | 121.8658 | 121.9757 | 121.907 | 121.7285 | 0.036621 | -0.009155
570.6562 | 121.9254 | -121.756 | 0.050354 | -0.003128 | -0.01094 | -0.017098 | 0.020307 | -0.0089359 | -0.0063702 | -0.00070712 | 0.022888 | -0.059509 | 0.009155 | 0.13275 | 0.10071 | 0.1831 | -0.091553 | 0.13733 | 0.004578 | 0.022888 | 121.7651 | -0.10986 | 121.7789 | 121.8887 | 0.050354 | 121.7789 | -0.045776 | 0.013733 | 121.6644 | 121.8933 | 121.8567 | 121.6965 | 121.7789 | 121.7606 | 121.9391 | 121.7789 | 121.6965 | 121.7789 | 121.9391 | 121.8567 | 121.7606 | -0.041199 | -0.027466
571.6719 | 121.9666 | -121.7194 | 0.045776 | -0.010758 | -0.01393 | -0.01368 | 0.020734 | -0.011713 | -0.0055156 | 0.00078828 | 0.041199 | -0.050354 | 0.032043 | 0.1831 | 0.13733 | 0.20599 | -0.09613 | 0.16479 | 0.004578 | 0.045776 | 121.7514 | -0.09613 | 121.7606 | 121.9025 | 0.091553 | 121.7651 | -0.041198 | 0.009156 | 121.6232 | 121.8842 | 121.8567 | 121.669 | 121.7606 | 121.7239 | 121.9254 | 121.7651 | 121.669 | 121.7606 | 121.9254 | 121.8567 | 121.7239 | -0.013733 | 0
572.6719 | 121.9849 | -121.7148 | 0.059509 | -0.003128 | -0.01393 | -0.017098 | 0.020307 | -0.010004 | -0.0057294 | 0.00078828 | 0.091553 | -0.032043 | 0.050354 | 0.24261 | 0.17395 | 0.2655 | -0.10071 | 0.23346 | 0.013733 | 0.064087 | 121.7651 | -0.091552 | 121.8063 | 121.9574 | 0.11444 | 121.7789 | -0.045776 | 0.041199 | 121.6141 | 121.9482 | 121.8887 | 121.6827 | 121.8063 | 121.7285 | 121.9803 | 121.7789 | 121.6827 | 121.8063 | 121.9803 | 121.8887 | 121.7285 | -0.009155 | 0.004578
573.6719 | 121.9803 | -121.2479 | 0.52185 | 0.0045015 | -0.013289 | -0.016244 | 0.022657 | -0.0095767 | -0.0029522 | -0.0013479 | 0.2243 | 0.12817 | 0.21057 | 0.67749 | 0.61798 | 0.72327 | 0.37994 | 0.68207 | 0.48523 | 0.51727 | 121.4584 | -0.39368 | 121.4722 | 121.9254 | 0.09613 | 121.7651 | -0.036622 | 0.013733 | 121.6278 | 121.9299 | 121.8658 | 121.376 | 121.4722 | 121.7331 | 121.9711 | 121.7651 | 121.376 | 121.4722 | 121.9711 | 121.8658 | 121.7331 | -0.31128 | -0.004578
574.6719 | 121.9711 | -121.5363 | 0.2655 | 0.01213 | -0.013289 | -0.019235 | 0.021375 | -0.010859 | -0.005943 | 0.00036108 | 0.10986 | 0.032043 | 0.1236 | 0.39368 | 0.34332 | 0.42114 | 0.10529 | 0.37537 | 0.21973 | 0.23346 | 121.6599 | -0.23346 | 121.6461 | 121.9299 | 0.07782 | 121.7697 | -0.045776 | -0.013733 | 121.6415 | 121.9116 | 121.8796 | 121.5683 | 121.6461 | 121.756 | 121.9574 | 121.7697 | 121.5683 | 121.6461 | 121.9574 | 121.8796 | 121.756 | -0.14191 | -0.032044
575.6562 | 121.994 | -120.3186 | 1.4557 | -0.003128 | -0.01094 | -0.014321 | 0.019025 | -0.011713 | -0.0055156 | -0.0011343 | 0.5722 | 0.42114 | 0.5127 | 1.6251 | 1.5564 | 1.6525 | 1.2726 | 1.6342 | 1.3779 | 1.4236 | 120.8313 | -1.0345 | 120.8908 | 121.9437 | 0.10071 | 121.7422 | -0.077819 | 0.05951 | 121.5912 | 121.9528 | 121.875 | 120.7397 | 120.8908 | 121.6965 | 121.9711 | 121.7422 | 120.7397 | 120.8908 | 121.9711 | 121.875 | 121.6965 | -0.94299 | -0.032043
576.6562 | 122.0123 | -119.9844 | 1.767 | -0.003128 | -0.011794 | -0.018594 | 0.020093 | -0.0093631 | -0.005302 | 0.0010019 | 0.68207 | 0.52185 | 0.62256 | 1.9592 | 1.8814 | 1.9821 | 1.5793 | 1.9409 | 1.6937 | 1.7624 | 120.607 | -1.2451 | 120.6665 | 121.9437 | 0.11444 | 121.7468 | -0.073242 | 0.059509 | 121.5637 | 121.9254 | 121.8658 | 120.5063 | 120.6665 | 121.6782 | 121.9666 | 121.7468 | 120.5063 | 120.6665 | 121.9666 | 121.8658 | 121.6782 | -1.1444 | -0.004578
577.6562 | 121.9528 | -119.2337 | 2.536 | -0.003128 | -0.01158 | -0.015603 | 0.020521 | -0.010859 | -0.0065838 | -0.00049352 | 0.84228 | 0.737 | 0.83771 | 2.6505 | 2.5772 | 2.6688 | 2.3712 | 2.6047 | 2.4765 | 2.4948 | 120.0714 | -1.799 | 120.076 | 121.8842 | 0.041198 | 121.7285 | -0.05951 | 0.004577 | 121.6049 | 121.8384 | 121.8109 | 119.9707 | 120.076 | 121.7102 | 121.9025 | 121.7285 | 119.9707 | 120.076 | 121.9025 | 121.8109 | 121.7102 | -1.6983 | -0.041199
578.6719 | 121.9254 | -119.7281 | 2.0554 | -0.003128 | -0.012862 | -0.016244 | 0.021162 | -0.013636 | -0.0057294 | 0.0010019 | 0.63171 | 0.55847 | 0.64087 | 2.1561 | 2.0828 | 2.1927 | 1.918 | 2.1286 | 1.9775 | 2.0187 | 120.369 | -1.4969 | 120.3598 | 121.8842 | 0.027466 | 121.7468 | -0.07782 | -0.009155 | 121.6461 | 121.8567 | 121.8109 | 120.2866 | 120.3598 | 121.7056 | 121.9208 | 121.7468 | 120.2866 | 120.3598 | 121.9208 | 121.8109 | 121.7056 | -1.4145 | -0.036621
579.6719 | 121.9574 | -118.4601 | 3.3096 | 0.0045015 | -0.015212 | -0.017098 | 0.01753 | -0.011072 | -0.0057294 | 0.00078828 | 1.0254 | 1.0071 | 1.0757 | 3.447 | 3.3646 | 3.479 | 3.1769 | 3.392 | 3.2776 | 3.2913 | 119.5358 | -2.3026 | 119.4855 | 121.907 | 0.054932 | 121.7514 | -0.032043 | -0.050354 | 121.637 | 121.8521 | 121.8246 | 119.4672 | 119.4855 | 121.7377 | 121.9391 | 121.7514 | 119.4672 | 119.4855 | 121.9391 | 121.8246 | 121.7377 | -2.2339 | -0.01831
580.6719 | 121.9437 | -119.7098 | 2.0508 | 0.01213 | -0.011794 | -0.020303 | 0.019239 | -0.011286 | -0.005302 | -6.6324e-05 | 0.66376 | 0.59052 | 0.67291 | 2.1561 | 2.092 | 2.1881 | 1.9272 | 2.1286 | 1.9913 | 2.0325 | 120.3827 | -1.4603 | 120.3735 | 121.8658 | 0.041199 | 121.7422 | -0.059509 | -0.009156 | 121.637 | 121.8384 | 121.8018 | 120.3003 | 120.3735 | 121.701 | 121.8979 | 121.7422 | 120.3003 | 120.3735 | 121.8979 | 121.8018 | 121.701 | -1.3779 | -0.01831
581.6562 | 121.994 | -117.2379 | 4.5364 | -0.003128 | -0.015639 | -0.01603 | 0.019666 | -0.011713 | -0.0050884 | 0.0018565 | 1.5976 | 1.474 | 1.5472 | 4.6967 | 4.6234 | 4.715 | 4.3808 | 4.6738 | 4.4678 | 4.4952 | 118.7851 | -3.0624 | 118.8354 | 121.9345 | 0.086975 | 121.7331 | -0.068665 | 0.050354 | 121.6187 | 121.9116 | 121.8613 | 118.7119 | 118.8354 | 121.7056 | 121.9528 | 121.7331 | 118.7119 | 118.8354 | 121.9528 | 121.8613 | 121.7056 | -2.9892 | -0.041199
582.6562 | 121.994 | -118.4555 | 3.3096 | -0.003128 | -0.012435 | -0.015176 | 0.017957 | -0.011072 | -0.0057294 | 0.0018565 | 1.0849 | 0.98877 | 1.0803 | 3.4561 | 3.3508 | 3.4698 | 3.1677 | 3.4195 | 3.2501 | 3.2684 | 119.5358 | -2.3209 | 119.5404 | 121.9116 | 0.041199 | 121.7239 | -0.059509 | 0.004578 | 121.6232 | 121.875 | 121.8063 | 119.4443 | 119.5404 | 121.7056 | 121.9254 | 121.7239 | 119.4443 | 119.5404 | 121.9254 | 121.8063 | 121.7056 | -2.2293 | -0.041198
583.6562 | 121.9757 | -119.6686 | 2.1103 | 0.0045015 | -0.011367 | -0.021585 | 0.020521 | -0.010859 | -0.0057294 | -0.00027992 | 0.65002 | 0.58594 | 0.6546 | 2.2064 | 2.1606 | 2.243 | 1.9592 | 2.1973 | 2.0416 | 2.0691 | 120.3232 | -1.5244 | 120.3186 | 121.875 | 0.050354 | 121.7377 | -0.068665 | -0.004578 | 121.6278 | 121.8658 | 121.8292 | 120.2545 | 120.3186 | 121.7102 | 121.9116 | 121.7377 | 120.2545 | 120.3186 | 121.9116 | 121.8292 | 121.7102 | -1.4557 | -0.041199
584.6562 | 122.0215 | -120.8267 | 0.93384 | -0.003128 | -0.011794 | -0.01069 | 0.023084 | -0.010004 | -0.005943 | 0.0016427 | 0.32501 | 0.16937 | 0.26093 | 1.1215 | 1.03 | 1.1169 | 0.70496 | 1.0666 | 0.87891 | 0.92468 | 121.0876 | -0.76446 | 121.1517 | 121.9482 | 0.09613 | 121.7514 | -0.054932 | 0.064087 | 121.5317 | 121.8933 | 121.8567 | 120.9961 | 121.1517 | 121.7056 | 121.9437 | 121.7514 | 120.9961 | 121.1517 | 121.9437 | 121.8567 | 121.7056 | -0.67291 | -0.009155
585.6719 | 121.9849 | -121.4081 | 0.34332 | -0.010758 | -0.011794 | -0.019876 | 0.020521 | -0.0082949 | -0.0072246 | 0.0016427 | 0.13275 | -0.018311 | 0.091553 | 0.50812 | 0.43945 | 0.52643 | 0.13733 | 0.46692 | 0.29297 | 0.35248 | 121.4996 | -0.36163 | 121.5408 | 121.9162 | 0.09613 | 121.7606 | -0.050354 | 0.041198 | 121.5454 | 121.875 | 121.8475 | 121.3898 | 121.5408 | 121.701 | 121.9345 | 121.7606 | 121.3898 | 121.5408 | 121.9345 | 121.8475 | 121.701 | -0.25177 | 0.009155
586.6719 | 121.9711 | -121.3211 | 0.44403 | -0.003128 | -0.011367 | -0.013253 | 0.021162 | -0.011499 | -0.005943 | 0.0020701 | 0.14648 | 0.018311 | 0.13733 | 0.57678 | 0.50354 | 0.59509 | 0.27008 | 0.54474 | 0.36621 | 0.44403 | 121.4584 | -0.42572 | 121.4676 | 121.8979 | 0.059509 | 121.7651 | -0.07782 | 0.009155 | 121.5912 | 121.8658 | 121.8246 | 121.3394 | 121.4676 | 121.6873 | 121.9162 | 121.7651 | 121.3394 | 121.4676 | 121.9162 | 121.8246 | 121.6873 | -0.3067 | 0
587.6719 | 121.9803 | -121.5317 | 0.22888 | -0.003128 | -0.011367 | -0.018594 | 0.022016 | -0.010645 | -0.0029522 | 0.0010019 | 0.10071 | -0.050354 | 0.045776 | 0.38452 | 0.31586 | 0.41199 | 0.018311 | 0.35248 | 0.17395 | 0.22888 | 121.5775 | -0.27924 | 121.6324 | 121.9162 | 0.086975 | 121.7606 | -0.054932 | 0.054932 | 121.55 | 121.8842 | 121.8475 | 121.4813 | 121.6324 | 121.7056 | 121.9437 | 121.7606 | 121.4813 | 121.6324 | 121.9437 | 121.8475 | 121.7056 | -0.18311 | 0
588.6562 | 121.962 | -121.5408 | 0.21515 | 0.0045015 | -0.014144 | -0.016885 | 0.019239 | -0.010218 | -0.0063702 | 0.0029245 | 0.064087 | -0.013733 | 0.054932 | 0.32959 | 0.27466 | 0.35248 | 0.082397 | 0.29297 | 0.17395 | 0.21515 | 121.5958 | -0.22888 | 121.6049 | 121.8704 | 0.059509 | 121.756 | -0.041199 | 0.009155 | 121.6232 | 121.8338 | 121.8155 | 121.5271 | 121.6049 | 121.7148 | 121.8933 | 121.756 | 121.5271 | 121.6049 | 121.8933 | 121.8155 | 121.7148 | -0.16022 | 0
589.6562 | 121.9803 | -121.3577 | 0.40283 | -0.003128 | -0.012862 | -0.011971 | 0.022016 | -0.0091495 | -0.0067974 | 0.00014748 | 0.11902 | 0.027466 | 0.10986 | 0.5127 | 0.45776 | 0.54016 | 0.25635 | 0.48981 | 0.35706 | 0.37079 | 121.4676 | -0.37537 | 121.4767 | 121.8704 | 0.054932 | 121.7285 | -0.045776 | 0.009156 | 121.6141 | 121.8475 | 121.8155 | 121.3852 | 121.4767 | 121.7148 | 121.8979 | 121.7285 | 121.3852 | 121.4767 | 121.8979 | 121.8155 | 121.7148 | -0.29297 | -0.032043
590.6719 | 121.9208 | -121.5729 | 0.26093 | 0.0045015 | -0.0098715 | -0.014749 | 0.020093 | -0.010859 | -0.0063702 | -0.00027992 | 0.14648 | 0.050354 | 0.10529 | 0.3479 | 0.27008 | 0.34332 | 0.19226 | 0.28381 | 0.20599 | 0.20599 | 121.6782 | -0.21057 | 121.7194 | 121.9208 | 0.009156 | 121.7789 | -0.054931 | 0.041198 | 121.7651 | 121.8567 | 121.843 | 121.6232 | 121.7194 | 121.7789 | 121.9162 | 121.7789 | 121.6232 | 121.7194 | 121.9162 | 121.843 | 121.7789 | -0.15564 | -0.054931
591.6562 | 121.9803 | -121.5637 | 0.25177 | -0.010758 | -0.011794 | -0.015389 | 0.023511 | -0.010218 | -0.0055156 | 0.00014748 | 0.054932 | -0.027466 | 0.036621 | 0.35248 | 0.29755 | 0.39368 | 0.036621 | 0.32501 | 0.18768 | 0.19684 | 121.6003 | -0.27924 | 121.6187 | 121.9162 | 0.045776 | 121.7606 | -0.064087 | 0.018311 | 121.6003 | 121.8887 | 121.8613 | 121.5363 | 121.6187 | 121.7514 | 121.9574 | 121.7606 | 121.5363 | 121.6187 | 121.9574 | 121.8613 | 121.7514 | -0.21515 | -0.054932
592.6719 | 122.0123 | -120.9778 | 0.7782 | -0.003128 | -0.01158 | -0.016458 | 0.023084 | -0.0082949 | -0.0063702 | 0.0022837 | 0.27924 | 0.12817 | 0.21515 | 0.94757 | 0.87891 | 0.97961 | 0.55389 | 0.89722 | 0.71869 | 0.7782 | 121.1929 | -0.65002 | 121.257 | 121.9254 | 0.10071 | 121.756 | -0.059509 | 0.064087 | 121.5317 | 121.875 | 121.8567 | 121.106 | 121.257 | 121.6965 | 121.9574 | 121.756 | 121.106 | 121.257 | 121.9574 | 121.8567 | 121.6965 | -0.56305 | 0
593.6719 | 122.0215 | -120.7489 | 1.0025 | -0.003128 | -0.010085 | -0.014108 | 0.021162 | -0.0093631 | -0.0038068 | -0.00070712 | 0.32959 | 0.19684 | 0.27008 | 1.1719 | 1.1032 | 1.1948 | 0.77362 | 1.1536 | 0.93384 | 0.99792 | 121.019 | -0.80566 | 121.0785 | 121.9208 | 0.10071 | 121.7468 | -0.068664 | 0.059509 | 121.5225 | 121.9025 | 121.8521 | 120.9457 | 121.0785 | 121.6827 | 121.9437 | 121.7468 | 120.9457 | 121.0785 | 121.9437 | 121.8521 | 121.6827 | -0.73242 | -0.004577
594.6719 | 122.0352 | -121.0831 | 0.64087 | 0.0045015 | -0.0088035 | -0.013467 | 0.020093 | -0.010431 | -0.0063702 | 0.0016427 | 0.22888 | 0.068665 | 0.16937 | 0.8194 | 0.76904 | 0.84228 | 0.41657 | 0.78735 | 0.56763 | 0.65002 | 121.2524 | -0.5722 | 121.312 | 121.9025 | 0.12817 | 121.7331 | -0.073242 | 0.059509 | 121.4996 | 121.8704 | 121.8521 | 121.1517 | 121.312 | 121.6507 | 121.9254 | 121.7331 | 121.1517 | 121.312 | 121.9254 | 121.8521 | 121.6507 | -0.4715 | 0.009155
595.6719 | 122.0261 | -121.5637 | 0.2243 | -0.010758 | -0.013289 | -0.017953 | 0.017316 | -0.010431 | -0.0046612 | 0.00036108 | 0.1831 | 0.032043 | 0.11444 | 0.39825 | 0.3479 | 0.42572 | 0.045776 | 0.40741 | 0.16022 | 0.21515 | 121.6782 | -0.19226 | 121.7468 | 121.962 | 0.1236 | 121.7789 | -0.064087 | 0.068664 | 121.6095 | 121.9711 | 121.9116 | 121.5958 | 121.7468 | 121.7239 | 121.9894 | 121.7789 | 121.5958 | 121.7468 | 121.9894 | 121.9116 | 121.7239 | -0.10986 | -0.009155
596.6562 | 122.0032 | -121.582 | 0.1831 | -0.003128 | -0.012221 | -0.016244 | 0.020093 | -0.0091495 | -0.0040204 | -0.00027992 | 0.091553 | -0.054932 | 0.064087 | 0.34332 | 0.27466 | 0.37537 | -0.009155 | 0.3067 | 0.14648 | 0.19226 | 121.6461 | -0.23804 | 121.6736 | 121.9254 | 0.091553 | 121.7743 | -0.036621 | 0.027466 | 121.5729 | 121.8887 | 121.8567 | 121.5271 | 121.6736 | 121.7285 | 121.9574 | 121.7743 | 121.5271 | 121.6736 | 121.9574 | 121.8567 | 121.7285 | -0.11902 | 0.009156
597.6562 | 122.0078 | -121.6278 | 0.14648 | -0.003128 | -0.011153 | -0.014321 | 0.020734 | -0.010645 | -0.0065838 | 0.0033517 | 0.082397 | -0.064087 | 0.041199 | 0.30212 | 0.24261 | 0.31128 | -0.068665 | 0.27466 | 0.082397 | 0.13275 | 121.669 | -0.21057 | 121.7102 | 121.9299 | 0.096131 | 121.7606 | -0.064087 | 0.041198 | 121.5591 | 121.9025 | 121.8704 | 121.5637 | 121.7102 | 121.7102 | 121.9391 | 121.7606 | 121.5637 | 121.7102 | 121.9391 | 121.8704 | 121.7102 | -0.10529 | -0.013733
598.6562 | 121.9208 | -121.6599 | 0.16937 | -0.003128 | -0.0068809 | -0.019876 | 0.024793 | -0.0087223 | -0.0067974 | 0.0022837 | 0 | -0.004578 | 0.004578 | 0.17853 | 0.11444 | 0.19684 | 0.07782 | 0.1236 | 0.11902 | 0.073242 | 121.6644 | -0.17395 | 121.6599 | 121.8384 | -0.054932 | 121.7331 | -0.050354 | -0.004578 | 121.7377 | 121.7834 | 121.7743 | 121.6553 | 121.6599 | 121.7789 | 121.8567 | 121.7331 | 121.6553 | 121.6599 | 121.8567 | 121.7743 | 121.7789 | -0.16479 | -0.096131
599.6719 | 121.994 | -121.6232 | 0.14191 | -0.010758 | -0.0090171 | -0.014535 | 0.025007 | -0.0080813 | -0.0038068 | 0.0022837 | 0.004578 | -0.009155 | -0.004578 | 0.21973 | 0.16937 | 0.25177 | 0 | 0.1831 | 0.086975 | 0.09613 | 121.6187 | -0.15106 | 121.6278 | 121.843 | 0.027466 | 121.7194 | -0.054932 | 0.009156 | 121.6232 | 121.8063 | 121.7926 | 121.6141 | 121.6278 | 121.7102 | 121.875 | 121.7194 | 121.6141 | 121.6278 | 121.875 | 121.7926 | 121.7102 | -0.14649 | -0.045777
600.6719 | 122.0581 | -121.669 | 0.14648 | -0.003128 | -0.011367 | -0.013894 | 0.016889 | -0.0095767 | -0.004234 | 0.0031381 | 0.11444 | 0 | 0.091553 | 0.29297 | 0.24719 | 0.3479 | -0.032043 | 0.3067 | 0.086975 | 0.11444 | 121.7606 | -0.14648 | 121.7834 | 121.962 | 0.10071 | 121.7834 | -0.059509 | 0.022888 | 121.637 | 121.9757 | 121.9162 | 121.669 | 121.7834 | 121.756 | 122.0169 | 121.7834 | 121.669 | 121.7834 | 122.0169 | 121.9162 | 121.756 | -0.054931 | -0.032043
601.6719 | 122.0261 | -121.5591 | 0.18768 | -0.010758 | -0.0085899 | -0.012612 | 0.022657 | -0.0082949 | -0.004234 | 0.00014748 | 0.082397 | -0.018311 | 0.032043 | 0.32501 | 0.2655 | 0.37537 | 0.004578 | 0.32044 | 0.14191 | 0.18768 | 121.5912 | -0.20599 | 121.6415 | 121.8842 | 0.07782 | 121.7468 | -0.045776 | 0.050354 | 121.5637 | 121.8796 | 121.8246 | 121.5408 | 121.6415 | 121.7011 | 121.9345 | 121.7468 | 121.5408 | 121.6415 | 121.9345 | 121.8246 | 121.7011 | -0.15564 | 0
602.6562 | 122.0352 | -121.3394 | 0.41657 | -0.003128 | -0.011153 | -0.015389 | 0.020093 | -0.0093631 | -0.005943 | -6.6324e-05 | 0.15564 | 0.004578 | 0.10071 | 0.59052 | 0.50812 | 0.61798 | 0.20599 | 0.56305 | 0.3479 | 0.40283 | 121.4401 | -0.41199 | 121.4951 | 121.9299 | 0.091553 | 121.7422 | -0.068665 | 0.054932 | 121.5454 | 121.9025 | 121.8475 | 121.344 | 121.4951 | 121.6873 | 121.9574 | 121.7422 | 121.344 | 121.4951 | 121.9574 | 121.8475 | 121.6873 | -0.31586 | -0.013733
603.6562 | 122.0398 | -121.3898 | 0.35706 | -0.010758 | -0.0083763 | -0.013467 | 0.023084 | -0.0076541 | -0.0067974 | -0.00092072 | 0.14648 | 0 | 0.086975 | 0.53558 | 0.46234 | 0.56763 | 0.1236 | 0.49896 | 0.30212 | 0.35248 | 121.4767 | -0.35706 | 121.5363 | 121.9254 | 0.10529 | 121.7422 | -0.054932 | 0.059509 | 121.5134 | 121.8887 | 121.8521 | 121.3898 | 121.5363 | 121.6919 | 121.9574 | 121.7422 | 121.3898 | 121.5363 | 121.9574 | 121.8521 | 121.6919 | -0.27008 | -0.004578
604.6562 | 122.0444 | -121.4172 | 0.31128 | -0.003128 | -0.0096579 | -0.019235 | 0.024793 | -0.0085085 | -0.0072246 | 0.0016427 | 0.13733 | 0.009155 | 0.068665 | 0.48065 | 0.43488 | 0.53101 | 0.10529 | 0.44861 | 0.25635 | 0.31128 | 121.4859 | -0.30212 | 121.5546 | 121.8979 | 0.1236 | 121.7285 | -0.054931 | 0.068664 | 121.5225 | 121.8658 | 121.8521 | 121.4264 | 121.5546 | 121.6736 | 121.9482 | 121.7285 | 121.4264 | 121.5546 | 121.9482 | 121.8521 | 121.6736 | -0.24261 | 0
605.6719 | 122.0444 | -121.3623 | 0.42572 | -0.010758 | -0.012435 | -0.019662 | 0.018171 | -0.011927 | -0.0046612 | 0.0016427 | 0.15106 | 0.050354 | 0.13733 | 0.54016 | 0.49439 | 0.56763 | 0.24719 | 0.54016 | 0.3479 | 0.39825 | 121.4996 | -0.37537 | 121.5134 | 121.9025 | 0.068665 | 121.7606 | -0.07782 | 0.013733 | 121.6095 | 121.9025 | 121.8567 | 121.4127 | 121.5134 | 121.7102 | 121.9299 | 121.7606 | 121.4127 | 121.5134 | 121.9299 | 121.8567 | 121.7102 | -0.28839 | -0.027466
606.6719 | 121.9162 | -120.2362 | 1.593 | -0.003128 | -0.0077353 | -0.017312 | 0.024793 | -0.0089359 | -0.0050884 | -0.00027992 | 0.40741 | 0.3891 | 0.41657 | 1.6022 | 1.5335 | 1.6159 | 1.5198 | 1.5427 | 1.5747 | 1.5015 | 120.6528 | -1.2039 | 120.6436 | 121.8384 | -0.05951 | 121.7377 | -0.018311 | -0.009155 | 121.756 | 121.7789 | 121.7697 | 120.6253 | 120.6436 | 121.8109 | 121.8521 | 121.7377 | 120.6253 | 120.6436 | 121.8521 | 121.7697 | 121.8109 | -1.1765 | -0.091553
607.6719 | 121.9666 | -120.2499 | 1.5244 | -0.003128 | -0.0077353 | -0.014108 | 0.023084 | -0.0061587 | -0.007011 | 0.00036108 | 0.39368 | 0.37079 | 0.38452 | 1.561 | 1.4832 | 1.5884 | 1.4099 | 1.5015 | 1.4969 | 1.4511 | 120.6345 | -1.1536 | 120.6436 | 121.8109 | -0.041199 | 121.701 | -0.027466 | 0.009156 | 121.6599 | 121.7514 | 121.7331 | 120.6207 | 120.6436 | 121.7468 | 121.8384 | 121.701 | 120.6207 | 120.6436 | 121.8384 | 121.7331 | 121.7468 | -1.1398 | -0.073242
608.6719 | 121.9345 | -119.7968 | 1.9821 | -0.003128 | -0.0066673 | -0.012399 | 0.022871 | -0.0078677 | -0.0048748 | 0.0016427 | 0.46692 | 0.48981 | 0.47607 | 1.9913 | 1.9409 | 2.0416 | 1.8997 | 1.9455 | 1.9272 | 1.9043 | 120.2728 | -1.4923 | 120.2637 | 121.788 | -0.041199 | 121.701 | -0.054932 | -0.009155 | 121.6965 | 121.7422 | 121.7377 | 120.2866 | 120.2637 | 121.7239 | 121.8384 | 121.701 | 120.2866 | 120.2637 | 121.8384 | 121.7377 | 121.7239 | -1.506 | -0.07782
609.6562 | 122.0535 | -120.2225 | 1.5335 | 0.0045015 | -0.0081625 | -0.015389 | 0.022657 | -0.0078677 | -0.0048748 | 0.00014748 | 0.41657 | 0.31586 | 0.36621 | 1.6891 | 1.6342 | 1.7349 | 1.3412 | 1.6708 | 1.4786 | 1.5381 | 120.5887 | -1.2177 | 120.639 | 121.9116 | 0.10071 | 121.7606 | -0.054931 | 0.050354 | 121.5637 | 121.8933 | 121.8567 | 120.5383 | 120.639 | 121.701 | 121.9574 | 121.7606 | 120.5383 | 120.639 | 121.9574 | 121.8567 | 121.701 | -1.1673 | 0.004578
610.6562 | 122.0398 | -120.488 | 1.2726 | -0.018387 | -0.0092307 | -0.012185 | 0.022657 | -0.0080813 | -0.0031658 | 0.0033517 | 0.33417 | 0.26093 | 0.30212 | 1.4008 | 1.3229 | 1.4374 | 1.0849 | 1.3733 | 1.1993 | 1.2405 | 120.7901 | -1.0117 | 120.8221 | 121.8887 | 0.050354 | 121.7285 | -0.073242 | 0.032043 | 121.5729 | 121.8613 | 121.8109 | 120.7489 | 120.8221 | 121.6873 | 121.9254 | 121.7285 | 120.7489 | 120.8221 | 121.9254 | 121.8109 | 121.6873 | -0.97046 | -0.032043
611.6562 | 122.0261 | -120.5841 | 1.1902 | 0.0045015 | -0.0068809 | -0.014535 | 0.02223 | -0.0082949 | -0.004234 | 0.00078828 | 0.28381 | 0.23804 | 0.2655 | 1.2772 | 1.2268 | 1.3321 | 1.0162 | 1.2634 | 1.1261 | 1.1444 | 120.8496 | -0.95215 | 120.8679 | 121.8613 | 0.036621 | 121.7285 | -0.064087 | 0.01831 | 121.6003 | 121.8475 | 121.8109 | 120.8221 | 120.8679 | 121.7102 | 121.9162 | 121.7285 | 120.8221 | 120.8679 | 121.9162 | 121.8109 | 121.7102 | -0.92468 | -0.045777
612.6562 | 121.9208 | -119.9478 | 1.8814 | -0.010758 | -0.0066673 | -0.012826 | 0.022443 | -0.0082949 | -0.0038068 | 0.0033517 | 0.45319 | 0.44403 | 0.43945 | 1.8951 | 1.8265 | 1.9089 | 1.799 | 1.8356 | 1.8219 | 1.7899 | 120.3873 | -1.4374 | 120.401 | 121.843 | -0.054932 | 121.7377 | -0.05951 | 0.013733 | 121.7468 | 121.7834 | 121.7743 | 120.3918 | 120.401 | 121.7697 | 121.8567 | 121.7377 | 120.3918 | 120.401 | 121.8567 | 121.7743 | 121.7697 | -1.442 | -0.091553
613.6719 | 121.9482 | -119.7006 | 2.124 | -0.003128 | -0.0060263 | -0.0094079 | 0.021162 | -0.0059451 | -0.0048748 | 0.00057468 | 0.4715 | 0.49896 | 0.46692 | 2.1149 | 2.0645 | 2.1652 | 2.0599 | 2.0782 | 2.0782 | 2.0416 | 120.1675 | -1.6251 | 120.1721 | 121.8155 | -0.059509 | 121.7422 | -0.045776 | 0.004578 | 121.7606 | 121.7789 | 121.7651 | 120.1996 | 120.1721 | 121.7789 | 121.8658 | 121.7422 | 120.1996 | 120.1721 | 121.8658 | 121.7651 | 121.7789 | -1.6571 | -0.082397
614.6719 | 121.9345 | -120.1035 | 1.7258 | -0.003128 | -0.0055991 | -0.011971 | 0.021162 | -0.0076541 | -0.003593 | 0.0010019 | 0.37079 | 0.37079 | 0.38452 | 1.6983 | 1.6479 | 1.7487 | 1.6479 | 1.6571 | 1.6571 | 1.6296 | 120.488 | -1.355 | 120.4742 | 121.8018 | -0.07782 | 121.7331 | -0.068665 | -0.013732 | 121.7514 | 121.7606 | 121.7514 | 120.4742 | 120.4742 | 121.7606 | 121.8521 | 121.7331 | 120.4742 | 120.4742 | 121.8521 | 121.7514 | 121.7606 | -1.3412 | -0.09613
615.6719 | 121.9437 | -120.0714 | 1.7349 | 0.0045015 | -0.0075217 | -0.013253 | 0.020734 | -0.0044497 | -0.0044476 | 0.00036108 | 0.3891 | 0.40283 | 0.39825 | 1.7303 | 1.68 | 1.7624 | 1.6754 | 1.6937 | 1.7029 | 1.6525 | 120.4697 | -1.3321 | 120.4605 | 121.8018 | -0.054931 | 121.7239 | -0.032043 | -0.009155 | 121.7468 | 121.7651 | 121.7514 | 120.4742 | 120.4605 | 121.7743 | 121.8338 | 121.7239 | 120.4742 | 120.4605 | 121.8338 | 121.7514 | 121.7743 | -1.3367 | -0.082397
616.6562 | 122.0261 | -119.0414 | 2.7328 | -0.010758 | -0.0064535 | -0.013467 | 0.022657 | -0.0059451 | -0.0038068 | 0.00036108 | 0.70038 | 0.66376 | 0.6546 | 2.7969 | 2.7328 | 2.8564 | 2.5681 | 2.774 | 2.6962 | 2.6688 | 119.696 | -2.0691 | 119.7418 | 121.8384 | 0 | 121.7102 | -0.036621 | 0.045776 | 121.6095 | 121.8155 | 121.7743 | 119.7052 | 119.7418 | 121.7377 | 121.8979 | 121.7102 | 119.7052 | 119.7418 | 121.8979 | 121.7743 | 121.7377 | -2.0782 | -0.064087
617.6562 | 122.0078 | -119.2062 | 2.5543 | -0.003128 | -0.0068809 | -0.011117 | 0.018812 | -0.0061587 | -0.0018842 | 0.0020701 | 0.63629 | 0.62714 | 0.64087 | 2.623 | 2.5543 | 2.6688 | 2.449 | 2.5909 | 2.5223 | 2.5177 | 119.8471 | -1.9272 | 119.8425 | 121.8292 | 0 | 121.7239 | -0.032043 | -0.004577 | 121.6553 | 121.7972 | 121.7606 | 119.8334 | 119.8425 | 121.7285 | 121.875 | 121.7239 | 119.8334 | 119.8425 | 121.875 | 121.7606 | 121.7285 | -1.9135 | -0.036621
618.6562 | 121.9803 | -119.6411 | 2.1515 | -0.010758 | -0.0047447 | -0.017098 | 0.021375 | -0.0070133 | -0.0033794 | 0.0027109 | 0.49439 | 0.49439 | 0.50354 | 2.1698 | 2.1103 | 2.2202 | 2.0416 | 2.1515 | 2.1149 | 2.0874 | 120.1447 | -1.6571 | 120.1355 | 121.8109 | -0.041198 | 121.7285 | -0.036621 | -0.009155 | 121.6827 | 121.7926 | 121.7514 | 120.1355 | 120.1355 | 121.756 | 121.8613 | 121.7285 | 120.1355 | 120.1355 | 121.8613 | 121.7514 | 121.756 | -1.6479 | -0.064087
619.6562 | 121.9711 | -120.1126 | 1.7258 | -0.010758 | -0.0053855 | -0.016458 | 0.020734 | -0.0067995 | -0.005302 | 0.00057468 | 0.45319 | 0.42114 | 0.42114 | 1.7624 | 1.6983 | 1.7715 | 1.6251 | 1.7212 | 1.6708 | 1.6205 | 120.5338 | -1.3046 | 120.5658 | 121.875 | -0.027466 | 121.7331 | -0.054932 | 0.032043 | 121.7377 | 121.8338 | 121.8109 | 120.5338 | 120.5658 | 121.7834 | 121.8842 | 121.7331 | 120.5338 | 120.5658 | 121.8842 | 121.8109 | 121.7834 | -1.3046 | -0.10529
620.6719 | 121.9482 | -120.3873 | 1.4374 | -0.003128 | -0.0049583 | -0.015817 | 0.021802 | -0.0065859 | -0.0033794 | -0.0011343 | 0.32501 | 0.33875 | 0.32501 | 1.4282 | 1.3779 | 1.4648 | 1.3687 | 1.3962 | 1.3824 | 1.3687 | 120.7123 | -1.0986 | 120.7123 | 121.8155 | -0.059509 | 121.756 | -0.054932 | 0 | 121.756 | 121.7834 | 121.7651 | 120.726 | 120.7123 | 121.7697 | 121.8521 | 121.756 | 120.726 | 120.7123 | 121.8521 | 121.7651 | 121.7697 | -1.1124 | -0.068665
621.6719 | 121.9482 | -120.5521 | 1.3046 | -0.010758 | -0.0053855 | -0.013467 | 0.021589 | -0.0061587 | -0.005943 | 0.00078828 | 0.25635 | 0.27466 | 0.29297 | 1.2817 | 1.236 | 1.3321 | 1.2497 | 1.2543 | 1.268 | 1.2268 | 120.845 | -1.03 | 120.8084 | 121.8338 | -0.068664 | 121.7789 | -0.036621 | -0.036621 | 121.8018 | 121.8063 | 121.788 | 120.8267 | 120.8084 | 121.8201 | 121.8842 | 121.7789 | 120.8267 | 120.8084 | 121.8842 | 121.788 | 121.8201 | -1.0117 | -0.077819
622.6719 | 121.9254 | -120.4514 | 1.4008 | -0.010758 | -0.0075217 | -0.012612 | 0.021589 | -0.0078677 | -0.0031658 | 0.0012155 | 0.30212 | 0.32501 | 0.31128 | 1.387 | 1.3412 | 1.4328 | 1.3412 | 1.3458 | 1.3458 | 1.3138 | 120.7626 | -1.0757 | 120.7535 | 121.8384 | -0.059509 | 121.7651 | -0.054932 | -0.009155 | 121.7926 | 121.7972 | 121.7926 | 120.7764 | 120.7535 | 121.7972 | 121.8842 | 121.7651 | 120.7764 | 120.7535 | 121.8842 | 121.7926 | 121.7972 | -1.0895 | -0.086975
623.6562 | 121.9803 | -120.3369 | 1.4877 | -0.010758 | -0.0079489 | -0.016671 | 0.018384 | -0.0067995 | -0.0033794 | 0.0022837 | 0.32044 | 0.34332 | 0.33417 | 1.5015 | 1.4511 | 1.5564 | 1.3733 | 1.4694 | 1.4465 | 1.4053 | 120.6711 | -1.1444 | 120.6573 | 121.8384 | -0.036621 | 121.7422 | -0.041199 | -0.013732 | 121.7102 | 121.8063 | 121.788 | 120.6802 | 120.6573 | 121.7834 | 121.8933 | 121.7422 | 120.6802 | 120.6573 | 121.8933 | 121.788 | 121.7834 | -1.1536 | -0.082398
624.6562 | 121.9849 | -120.2637 | 1.5793 | -0.003128 | -0.0073081 | -0.01603 | 0.018812 | -0.0063723 | -0.003593 | 0.00036108 | 0.35248 | 0.36621 | 0.35706 | 1.561 | 1.5152 | 1.6159 | 1.4786 | 1.5427 | 1.5289 | 1.4877 | 120.6207 | -1.2131 | 120.6162 | 121.8246 | -0.064087 | 121.7514 | -0.050354 | -0.004578 | 121.7422 | 121.8063 | 121.7789 | 120.6299 | 120.6162 | 121.7926 | 121.8796 | 121.7514 | 120.6299 | 120.6162 | 121.8796 | 121.7789 | 121.7926 | -1.2222 | -0.091553
625.6562 | 121.9666 | -119.8563 | 1.9958 | -0.010758 | -0.0060263 | -0.016244 | 0.020948 | -0.0082949 | -0.0029522 | 0.0014291 | 0.45319 | 0.46692 | 0.47607 | 1.9821 | 1.9135 | 2.0233 | 1.8997 | 1.9501 | 1.9318 | 1.9135 | 120.3323 | -1.5289 | 120.3094 | 121.8384 | -0.082398 | 121.7697 | -0.064087 | -0.022888 | 121.756 | 121.8063 | 121.7697 | 120.3232 | 120.3094 | 121.788 | 121.8796 | 121.7697 | 120.3232 | 120.3094 | 121.8796 | 121.7697 | 121.788 | -1.5198 | -0.082398
626.6719 | 121.9574 | -119.9203 | 1.9135 | 0.01213 | -0.0077353 | -0.01368 | 0.020093 | -0.0057315 | -0.0063702 | -0.00049352 | 0.46692 | 0.45776 | 0.4715 | 1.9089 | 1.8539 | 1.9455 | 1.8448 | 1.886 | 1.8768 | 1.8448 | 120.3918 | -1.4557 | 120.3873 | 121.8292 | -0.059509 | 121.7651 | -0.036621 | -0.004578 | 121.7651 | 121.8063 | 121.7743 | 120.3781 | 120.3873 | 121.7972 | 121.8658 | 121.7651 | 120.3781 | 120.3873 | 121.8658 | 121.7743 | 121.7972 | -1.442 | -0.068664
627.6719 | 121.9528 | -120.0027 | 1.8585 | -0.018387 | -0.0051719 | -0.011331 | 0.020948 | -0.0057315 | -0.0050884 | 0.0044199 | 0.39825 | 0.42572 | 0.42114 | 1.8448 | 1.7715 | 1.8585 | 1.7853 | 1.7807 | 1.799 | 1.7395 | 120.4239 | -1.4328 | 120.401 | 121.8475 | -0.086976 | 121.7422 | -0.05951 | -0.022889 | 121.788 | 121.7834 | 121.7743 | 120.4285 | 120.401 | 121.8018 | 121.8613 | 121.7422 | 120.4285 | 120.401 | 121.8613 | 121.7743 | 121.8018 | -1.4374 | -0.11902
628.6719 | 121.9574 | -115.773 | 6.0745 | -0.018387 | -0.0045309 | -0.014535 | 0.020307 | -0.0057315 | -0.0033794 | 0.0014291 | 1.6342 | 1.6525 | 1.6388 | 6.0791 | 5.9921 | 6.1066 | 6.0471 | 6.0242 | 6.0379 | 5.9189 | 117.4118 | -4.422 | 117.4072 | 121.8521 | -0.082398 | 121.6919 | -0.036621 | -0.004578 | 121.8201 | 121.7972 | 121.7651 | 117.4255 | 117.4072 | 121.8109 | 121.8796 | 121.6919 | 117.4255 | 117.4072 | 121.8796 | 121.7651 | 121.8109 | -4.4357 | -0.15564
629.6719 | 121.9528 | -114.7522 | 7.1045 | -0.003128 | -0.0053855 | -0.017953 | 0.01988 | -0.0033817 | -0.0055156 | 0.0016427 | 1.9638 | 1.9547 | 1.9638 | 7.1091 | 7.0084 | 7.1503 | 7.077 | 7.0587 | 7.0541 | 6.9214 | 116.716 | -5.1498 | 116.716 | 121.8613 | -0.09613 | 121.6736 | -0.050354 | 0 | 121.8292 | 121.8109 | 121.7606 | 116.7068 | 116.716 | 121.8063 | 121.9025 | 121.6736 | 116.7068 | 116.716 | 121.9025 | 121.7606 | 121.8063 | -5.1407 | -0.1831
630.6562 | 121.9849 | -115.8966 | 5.9463 | -0.003128 | -0.0049583 | -0.012399 | 0.017316 | -0.0050907 | -0.0031658 | 0.0024973 | 1.6434 | 1.6159 | 1.6251 | 5.9967 | 5.9189 | 6.0379 | 5.9052 | 5.9143 | 5.9097 | 5.8044 | 117.5217 | -4.3304 | 117.54 | 121.8933 | -0.027466 | 121.701 | -0.036621 | 0.018311 | 121.8018 | 121.8109 | 121.8155 | 117.5125 | 117.54 | 121.8063 | 121.9345 | 121.701 | 117.5125 | 117.54 | 121.9345 | 121.8155 | 121.8063 | -4.3213 | -0.14191
631.6562 | 121.9803 | -118.9087 | 2.916 | -0.003128 | -0.0070945 | -0.015176 | 0.018598 | -0.0048769 | -0.0018842 | 0.0012155 | 0.71411 | 0.72327 | 0.71869 | 2.8976 | 2.8381 | 2.948 | 2.8519 | 2.8748 | 2.8793 | 2.8198 | 119.6274 | -2.1927 | 119.6228 | 121.8063 | -0.07782 | 121.7285 | -0.036622 | -0.004578 | 121.7606 | 121.7834 | 121.7468 | 119.632 | 119.6228 | 121.788 | 121.8567 | 121.7285 | 119.632 | 119.6228 | 121.8567 | 121.7468 | 121.788 | -2.1973 | -0.096131
632.6562 | 122.0032 | -119.6274 | 2.1881 | -0.010758 | -0.0062399 | -0.015176 | 0.021375 | -0.0074405 | -0.0038068 | 0.0020701 | 0.61798 | 0.54932 | 0.56763 | 2.2385 | 2.1698 | 2.2705 | 2.0874 | 2.2202 | 2.1606 | 2.124 | 120.195 | -1.6388 | 120.2454 | 121.8658 | -0.01831 | 121.7514 | -0.027465 | 0.050354 | 121.7148 | 121.8475 | 121.7972 | 120.1767 | 120.2454 | 121.788 | 121.8979 | 121.7514 | 120.1767 | 120.2454 | 121.8979 | 121.7972 | 121.788 | -1.6205 | -0.064087
633.6719 | 121.9757 | -119.6411 | 2.2339 | -0.010758 | -0.0062399 | -0.0098351 | 0.022016 | -0.0057315 | -0.0048748 | 0.00057468 | 0.54474 | 0.53101 | 0.54016 | 2.2293 | 2.1698 | 2.2568 | 2.1652 | 2.1835 | 2.1927 | 2.1378 | 120.1813 | -1.7029 | 120.1859 | 121.8704 | -0.064087 | 121.7789 | -0.041199 | 0.004578 | 121.8063 | 121.8246 | 121.8109 | 120.1721 | 120.1859 | 121.8338 | 121.8979 | 121.7789 | 120.1721 | 120.1859 | 121.8979 | 121.8109 | 121.8338 | -1.6937 | -0.096131
634.6719 | 121.962 | -118.8171 | 3.0579 | -0.010758 | -0.0060263 | -0.015817 | 0.019025 | -0.0076541 | -0.004234 | 0.0014291 | 0.73242 | 0.76904 | 0.75531 | 3.0304 | 2.9663 | 3.067 | 2.9892 | 2.9846 | 3.0167 | 2.948 | 119.5724 | -2.2888 | 119.5496 | 121.8475 | -0.091552 | 121.7651 | -0.041198 | -0.022888 | 121.8063 | 121.8018 | 121.7834 | 119.5862 | 119.5496 | 121.8338 | 121.8842 | 121.7651 | 119.5862 | 119.5496 | 121.8842 | 121.7834 | 121.8338 | -2.3026 | -0.10986
635.6719 | 121.9666 | -117.2928 | 4.6005 | -0.003128 | -0.0094443 | -0.014962 | 0.020734 | -0.0046633 | -0.0046612 | 0.0024973 | 1.149 | 1.1902 | 1.1673 | 4.5364 | 4.4861 | 4.5868 | 4.4998 | 4.509 | 4.5227 | 4.4632 | 118.4601 | -3.4103 | 118.4418 | 121.8292 | -0.11444 | 121.756 | -0.07782 | -0.01831 | 121.7926 | 121.8018 | 121.7789 | 118.483 | 118.4418 | 121.8155 | 121.8796 | 121.756 | 118.483 | 118.4418 | 121.8796 | 121.7789 | 121.8155 | -3.4332 | -0.13733
636.6719 | 121.962 | -115.3793 | 6.4957 | -0.003128 | -0.0062399 | -0.01304 | 0.02223 | -0.0078677 | -0.0050884 | 0.0022837 | 1.6891 | 1.7029 | 1.7029 | 6.4682 | 6.3721 | 6.5002 | 6.427 | 6.4362 | 6.4178 | 6.3034 | 117.0822 | -4.7928 | 117.0685 | 121.8475 | -0.1236 | 121.6827 | -0.07782 | -0.013733 | 121.8063 | 121.8155 | 121.7514 | 117.0822 | 117.0685 | 121.7972 | 121.8796 | 121.6827 | 117.0822 | 117.0685 | 121.8796 | 121.7514 | 121.7972 | -4.7928 | -0.19226
637.6562 | 122.0169 | -114.3036 | 7.5165 | -0.010758 | -0.0068809 | -0.011971 | 0.018171 | -0.0055179 | -0.0055156 | 0.0027109 | 2.0416 | 2.0554 | 2.0462 | 7.4661 | 7.4203 | 7.5989 | 7.4249 | 7.5119 | 7.4249 | 7.283 | 116.3498 | -5.4611 | 116.3452 | 121.7697 | -0.09613 | 121.5866 | -0.091552 | -0.004578 | 121.7285 | 121.8155 | 121.7239 | 116.3589 | 116.3452 | 121.7285 | 121.9025 | 121.5866 | 116.3589 | 116.3452 | 121.9025 | 121.7239 | 121.7285 | -5.4703 | -0.23346
638.6562 | 122.0123 | -113.7955 | 8.0292 | -0.010758 | -0.0053855 | -0.01304 | 0.019025 | -0.0057315 | -0.0040204 | -0.00092072 | 2.1652 | 2.1469 | 2.1423 | 8.0704 | 7.9697 | 8.1161 | 7.9605 | 8.02 | 7.9697 | 7.782 | 115.9378 | -5.8823 | 115.9607 | 121.8658 | -0.059509 | 121.5775 | -0.059509 | 0.022888 | 121.756 | 121.8155 | 121.7651 | 115.9424 | 115.9607 | 121.7651 | 121.9116 | 121.5775 | 115.9424 | 115.9607 | 121.9116 | 121.7651 | 121.7651 | -5.8868 | -0.24719
639.6562 | 121.994 | -113.8 | 8.0383 | -0.010758 | -0.0058127 | -0.011971 | 0.019666 | -0.0072269 | -0.0046612 | 0.0016427 | 2.2293 | 2.211 | 2.2202 | 8.1436 | 8.0246 | 8.1482 | 8.0017 | 8.0521 | 8.0109 | 7.7957 | 116.0202 | -5.8273 | 116.0294 | 121.9437 | -0.013733 | 121.5958 | -0.027466 | 0.009155 | 121.8018 | 121.8521 | 121.8246 | 116.011 | 116.0294 | 121.8109 | 121.9482 | 121.5958 | 116.011 | 116.0294 | 121.9482 | 121.8246 | 121.8109 | -5.8182 | -0.24261
640.6719 | 121.9849 | -113.9603 | 7.8735 | -0.010758 | -0.0058127 | -0.015603 | 0.020948 | -0.0074405 | -0.004234 | 0.0022837 | 2.1973 | 2.2064 | 2.1744 | 7.901 | 7.7957 | 7.9239 | 7.8461 | 7.8369 | 7.8461 | 7.6492 | 116.1346 | -5.6671 | 116.1575 | 121.8613 | -0.07782 | 121.6095 | -0.027466 | 0.022889 | 121.8063 | 121.7972 | 121.756 | 116.1667 | 116.1575 | 121.8063 | 121.8842 | 121.6095 | 116.1667 | 116.1575 | 121.8842 | 121.756 | 121.8063 | -5.6992 | -0.2243
641.6719 | 121.9757 | -114.1434 | 7.7133 | -0.018387 | -0.0058127 | -0.020516 | 0.018812 | -0.0063723 | -0.0029522 | 0.00057468 | 2.0645 | 2.0737 | 2.0737 | 7.7271 | 7.6218 | 7.7408 | 7.6447 | 7.6492 | 7.6584 | 7.4753 | 116.217 | -5.6396 | 116.2079 | 121.8704 | -0.091553 | 121.6187 | -0.054932 | -0.009155 | 121.788 | 121.7926 | 121.7651 | 116.217 | 116.2079 | 121.8018 | 121.8842 | 121.6187 | 116.217 | 116.2079 | 121.8842 | 121.7651 | 121.8018 | -5.6396 | -0.23804
642.6719 | 121.9849 | -114.3677 | 7.4936 | 0.0045015 | -0.0075217 | -0.014321 | 0.020521 | -0.0063723 | -0.0029522 | 0.0016427 | 2.005 | 2.0325 | 2.0233 | 7.5027 | 7.4066 | 7.5348 | 7.4478 | 7.4524 | 7.4524 | 7.2739 | 116.391 | -5.4611 | 116.3727 | 121.8704 | -0.086975 | 121.6415 | -0.041198 | -0.01831 | 121.8155 | 121.8201 | 121.7743 | 116.4001 | 116.3727 | 121.8201 | 121.9025 | 121.6415 | 116.4001 | 116.3727 | 121.9025 | 121.7743 | 121.8201 | -5.4703 | -0.21973
643.6719 | 121.9894 | -114.3951 | 7.4341 | -0.003128 | -0.0064535 | -0.012399 | 0.01988 | -0.0057315 | -0.0055156 | 0.0016427 | 1.9775 | 1.9913 | 2.0004 | 7.4799 | 7.3929 | 7.4982 | 7.4112 | 7.4158 | 7.4112 | 7.2556 | 116.3956 | -5.4428 | 116.3727 | 121.875 | -0.041199 | 121.6507 | -0.022888 | -0.022888 | 121.8063 | 121.8109 | 121.788 | 116.3864 | 116.3727 | 121.8063 | 121.8933 | 121.6507 | 116.3864 | 116.3727 | 121.8933 | 121.788 | 121.8063 | -5.4337 | -0.17853
644.6562 | 122.0306 | -114.3585 | 7.457 | -0.003128 | -0.0043173 | -0.014108 | 0.020307 | -0.0074405 | -0.003593 | 0.0044199 | 1.9958 | 1.9775 | 1.9821 | 7.5394 | 7.4341 | 7.5623 | 7.37 | 7.4799 | 7.4387 | 7.283 | 116.3406 | -5.4794 | 116.3544 | 121.8979 | -0.022888 | 121.6415 | -0.01831 | 0.013733 | 121.7285 | 121.8384 | 121.7926 | 116.3361 | 116.3544 | 121.7972 | 121.9208 | 121.6415 | 116.3361 | 116.3544 | 121.9208 | 121.7926 | 121.7972 | -5.4749 | -0.17395
645.6562 | 122.0123 | -114.1068 | 7.7179 | -0.010758 | -0.0064535 | -0.015603 | 0.019025 | -0.0053043 | -0.0027386 | 0.0042063 | 2.0325 | 2.0279 | 2.0142 | 7.7774 | 7.6721 | 7.814 | 7.6584 | 7.7225 | 7.7133 | 7.5119 | 116.1209 | -5.69 | 116.1392 | 121.8842 | -0.045777 | 121.6187 | -0.004578 | 0.018311 | 121.7651 | 121.8292 | 121.7789 | 116.1346 | 116.1392 | 121.8201 | 121.9208 | 121.6187 | 116.1346 | 116.1392 | 121.9208 | 121.7789 | 121.8201 | -5.7037 | -0.20599
646.6562 | 122.0261 | -114.3219 | 7.5531 | -0.003128 | -0.0053855 | -0.01304 | 0.023084 | -0.0078677 | -0.007011 | 0.0018565 | 2.0554 | 2.0187 | 2.0279 | 7.6309 | 7.5119 | 7.6492 | 7.4753 | 7.5668 | 7.5119 | 7.3425 | 116.3498 | -5.5344 | 116.3773 | 121.9528 | -0.041199 | 121.6644 | -0.041199 | 0.027466 | 121.7972 | 121.8887 | 121.8338 | 116.3406 | 116.3773 | 121.8338 | 121.9711 | 121.6644 | 116.3406 | 116.3773 | 121.9711 | 121.8338 | 121.8338 | -5.5252 | -0.21057
647.6719 | 121.9803 | -114.3906 | 7.4753 | -0.010758 | -0.0047447 | -0.012826 | 0.019025 | -0.0076541 | -0.0046612 | 0.0012155 | 1.9684 | 1.973 | 1.9592 | 7.4982 | 7.3792 | 7.5027 | 7.4112 | 7.4387 | 7.4158 | 7.251 | 116.3498 | -5.5023 | 116.3589 | 121.8887 | -0.096131 | 121.6415 | -0.05951 | 0.009155 | 121.8018 | 121.8292 | 121.7697 | 116.3635 | 116.3589 | 121.8063 | 121.8933 | 121.6415 | 116.3635 | 116.3589 | 121.8933 | 121.7697 | 121.8063 | -5.5161 | -0.2243
648.6719 | 121.9757 | -114.6515 | 7.2144 | -0.010758 | -0.0058127 | -0.012399 | 0.020521 | -0.0076541 | -0.0023114 | 0.0033517 | 1.8677 | 1.8906 | 1.8723 | 7.2372 | 7.1274 | 7.2876 | 7.196 | 7.1732 | 7.196 | 7.045 | 116.5237 | -5.3238 | 116.5192 | 121.8887 | -0.086975 | 121.6965 | -0.01831 | -0.004577 | 121.8475 | 121.8246 | 121.7789 | 116.5421 | 116.5192 | 121.8475 | 121.9391 | 121.6965 | 116.5421 | 116.5192 | 121.9391 | 121.7789 | 121.8475 | -5.3421 | -0.16937
649.6719 | 121.9849 | -114.4638 | 7.4112 | 0.0045015 | -0.0066673 | -0.015176 | 0.019025 | -0.0057315 | -0.0063702 | 0.0018565 | 1.9226 | 1.9363 | 1.9363 | 7.4295 | 7.3196 | 7.457 | 7.3837 | 7.37 | 7.3792 | 7.2052 | 116.4001 | -5.4749 | 116.3864 | 121.8933 | -0.091553 | 121.669 | -0.032044 | -0.013733 | 121.8475 | 121.8338 | 121.7834 | 116.4001 | 116.3864 | 121.843 | 121.9208 | 121.669 | 116.4001 | 116.3864 | 121.9208 | 121.7834 | 121.843 | -5.4749 | -0.20599
650.6719 | 121.9894 | -118.6707 | 3.1998 | -0.010758 | -0.0079489 | -0.0098351 | 0.01988 | -0.0061587 | -0.0029522 | 0.0018565 | 0.76904 | 0.77362 | 0.75989 | 3.1998 | 3.1311 | 3.2043 | 3.154 | 3.154 | 3.1631 | 3.1082 | 119.4305 | -2.4261 | 119.4397 | 121.8704 | -0.068664 | 121.7789 | -0.036621 | 0.009155 | 121.8246 | 121.8246 | 121.8018 | 119.4443 | 119.4397 | 121.8338 | 121.875 | 121.7789 | 119.4443 | 119.4397 | 121.875 | 121.8018 | 121.8338 | -2.4399 | -0.091553
651.6562 | 122.0032 | -118.277 | 3.6118 | -0.010758 | -0.0038901 | -0.01304 | 0.021375 | -0.0072269 | -0.0044476 | 0.0014291 | 0.84228 | 0.84686 | 0.8606 | 3.5934 | 3.5156 | 3.6484 | 3.5385 | 3.566 | 3.5706 | 3.5065 | 119.1376 | -2.7649 | 119.1193 | 121.8704 | -0.09613 | 121.7834 | -0.041198 | -0.018311 | 121.8155 | 121.843 | 121.7926 | 119.1238 | 119.1193 | 121.8475 | 121.9254 | 121.7834 | 119.1238 | 119.1193 | 121.9254 | 121.7926 | 121.8475 | -2.7512 | -0.10528
652.6562 | 121.9986 | -119.2703 | 2.6321 | -0.010758 | -0.0047447 | -0.015176 | 0.02223 | -0.0067995 | -0.0027386 | 0.0024973 | 0.59967 | 0.62714 | 0.62714 | 2.6138 | 2.5543 | 2.6596 | 2.5589 | 2.5772 | 2.5726 | 2.5452 | 119.8975 | -2.005 | 119.87 | 121.8842 | -0.07782 | 121.8155 | -0.059509 | -0.027466 | 121.8292 | 121.8475 | 121.8246 | 119.8975 | 119.87 | 121.843 | 121.9299 | 121.8155 | 119.8975 | 119.87 | 121.9299 | 121.8246 | 121.843 | -2.005 | -0.086975
653.6562 | 122.0627 | -118.5791 | 3.2776 | 0.0045015 | -0.0066673 | -0.01368 | 0.019453 | -0.0063723 | -0.0055156 | 0.0018565 | 0.88348 | 0.81482 | 0.81482 | 3.3508 | 3.2639 | 3.3691 | 3.186 | 3.3188 | 3.2455 | 3.2043 | 119.3939 | -2.4628 | 119.4626 | 121.9299 | -0.013733 | 121.7834 | -0.032044 | 0.068665 | 121.7651 | 121.8979 | 121.843 | 119.3939 | 119.4626 | 121.8246 | 121.9482 | 121.7834 | 119.3939 | 119.4626 | 121.9482 | 121.843 | 121.8246 | -2.4628 | -0.073242
654.6719 | 122.0444 | -117.3523 | 4.5319 | 0.0045015 | -0.0055991 | -0.016458 | 0.020521 | -0.0035953 | -0.0055156 | 0.0014291 | 1.3046 | 1.268 | 1.2634 | 4.953 | 4.8477 | 4.953 | 4.7562 | 4.4815 | 4.8065 | 4.7287 | 118.6157 | -3.2639 | 118.6569 | 122.3053 | 0.31586 | 122.081 | 0.27466 | 0.041198 | 122.1085 | 121.8338 | 122.2 | 118.6203 | 118.6569 | 122.1588 | 122.3053 | 122.081 | 118.6203 | 118.6569 | 122.3053 | 122.2 | 122.1588 | -3.2684 | 0.19684
655.6719 | 121.9849 | -113.8 | 8.0978 | -0.010758 | -0.0053855 | -0.01368 | 0.016676 | -0.0067995 | -0.0044476 | 0.0012155 | 2.1011 | 2.092 | 2.0874 | 8.1573 | 8.0246 | 8.1573 | 8.0429 | 8.075 | 8.0383 | 7.8278 | 115.8875 | -6.0059 | 115.9012 | 121.9574 | -0.073242 | 121.6278 | -0.059509 | 0.013733 | 121.843 | 121.875 | 121.8246 | 115.892 | 115.9012 | 121.8384 | 121.9574 | 121.6278 | 115.892 | 115.9012 | 121.9574 | 121.8246 | 121.8384 | -6.0104 | -0.27008
656.6719 | 122.0261 | -113.3469 | 8.5236 | 0.0045015 | -0.0053855 | -0.015817 | 0.018812 | -0.0061587 | -0.0048748 | 0.0024973 | 2.2385 | 2.2018 | 2.1973 | 8.5831 | 8.4915 | 8.606 | 8.4595 | 8.5236 | 8.4824 | 8.1802 | 115.5441 | -6.3217 | 115.5853 | 121.9299 | -0.032044 | 121.5271 | -0.041199 | 0.041198 | 121.8063 | 121.8704 | 121.8384 | 115.5487 | 115.5853 | 121.8292 | 121.9528 | 121.5271 | 115.5487 | 115.5853 | 121.9528 | 121.8384 | 121.8292 | -6.3263 | -0.34332
657.6562 | 122.0123 | -113.4293 | 8.4457 | -0.010758 | -0.0070945 | -0.016458 | 0.021162 | -0.0072269 | -0.005302 | 0.00036108 | 2.1332 | 2.1881 | 2.1698 | 8.4686 | 8.3588 | 8.5007 | 8.4137 | 8.4045 | 8.3908 | 8.1116 | 115.5991 | -6.2576 | 115.5624 | 121.8979 | -0.086975 | 121.5408 | -0.054932 | -0.036621 | 121.843 | 121.8338 | 121.788 | 115.6174 | 115.5624 | 121.8201 | 121.9299 | 121.5408 | 115.6174 | 115.5624 | 121.9299 | 121.788 | 121.8201 | -6.2759 | -0.33417
658.6562 | 122.0032 | -113.1454 | 8.725 | -0.010758 | -0.0055991 | -0.011758 | 0.019239 | -0.0078677 | -0.0046612 | 0.00036108 | 2.2522 | 2.2797 | 2.2751 | 8.7433 | 8.6426 | 8.7845 | 8.6975 | 8.7021 | 8.6884 | 8.3405 | 115.4205 | -6.4453 | 115.3976 | 121.8887 | -0.082398 | 121.4859 | -0.036622 | -0.022888 | 121.843 | 121.8475 | 121.788 | 115.4251 | 115.3976 | 121.8338 | 121.9299 | 121.4859 | 115.4251 | 115.3976 | 121.9299 | 121.788 | 121.8338 | -6.4499 | -0.38452
659.6562 | 121.9849 | -113.1271 | 8.7524 | -0.003128 | -0.0043173 | -0.012612 | 0.020734 | -0.0053043 | -0.0040204 | 0.0010019 | 2.2751 | 2.2797 | 2.2751 | 8.7799 | 8.67 | 8.8074 | 8.7479 | 8.7204 | 8.7296 | 8.345 | 115.4022 | -6.4728 | 115.4022 | 121.907 | -0.082397 | 121.4722 | -0.022888 | 0 | 121.875 | 121.8475 | 121.7972 | 115.4068 | 115.4022 | 121.8567 | 121.9345 | 121.4722 | 115.4068 | 115.4022 | 121.9345 | 121.7972 | 121.8567 | -6.4774 | -0.40741
660.6562 | 122.0673 | -112.8983 | 8.9767 | -0.003128 | -0.0070945 | -0.01603 | 0.018171 | -0.0072269 | -0.0046612 | 0.0018565 | 2.4353 | 2.4078 | 2.4033 | 9.1187 | 8.9996 | 9.1187 | 8.9539 | 9.0454 | 8.9447 | 8.5144 | 115.3015 | -6.5689 | 115.3336 | 122.0169 | 0.022888 | 121.4127 | -0.032044 | 0.032044 | 121.8521 | 121.9437 | 121.8979 | 115.3061 | 115.3336 | 121.843 | 122.0169 | 121.4127 | 115.3061 | 115.3336 | 122.0169 | 121.8979 | 121.843 | -6.5735 | -0.46234
661.6719 | 122.0718 | -114.386 | 7.489 | -0.003128 | -0.0073081 | -0.011758 | 0.019453 | -0.0055179 | -0.0046612 | 0.00036108 | 2.005 | 1.9455 | 1.9638 | 7.5943 | 7.4936 | 7.6218 | 7.4203 | 7.5485 | 7.4707 | 7.3059 | 116.3498 | -5.5435 | 116.391 | 121.9803 | 0.004577 | 121.6919 | -0.018311 | 0.041199 | 121.8063 | 121.9345 | 121.8796 | 116.3315 | 116.391 | 121.8567 | 122.0078 | 121.6919 | 116.3315 | 116.391 | 122.0078 | 121.8796 | 121.8567 | -5.5252 | -0.18311
662.6719 | 122.049 | -113.7497 | 8.1345 | -0.018387 | -0.0051719 | -0.014108 | 0.01988 | -0.0048769 | -0.0029522 | 0.0020701 | 2.1744 | 2.124 | 2.1286 | 8.2443 | 8.1299 | 8.2535 | 8.0658 | 8.1665 | 8.0978 | 7.8827 | 115.8783 | -6.0104 | 115.9241 | 121.994 | -0.004577 | 121.6324 | -0.036621 | 0.045776 | 121.8155 | 121.9162 | 121.8796 | 115.8737 | 115.9241 | 121.8475 | 122.0032 | 121.6324 | 115.8737 | 115.9241 | 122.0032 | 121.8796 | 121.8475 | -6.0059 | -0.25177
663.6719 | 122.0627 | -113.7726 | 8.1207 | -0.010758 | -0.0055991 | -0.01603 | 0.018384 | -0.0059451 | -0.004234 | 0.00078828 | 2.2156 | 2.1515 | 2.1835 | 8.2443 | 8.1207 | 8.2535 | 8.075 | 8.1802 | 8.0978 | 7.869 | 115.9561 | -5.9692 | 115.9882 | 122.0169 | 0 | 121.6415 | -0.022889 | 0.032043 | 121.8475 | 121.9528 | 121.8933 | 115.9241 | 115.9882 | 121.8704 | 122.0261 | 121.6415 | 115.9241 | 115.9882 | 122.0261 | 121.8933 | 121.8704 | -5.9372 | -0.25177
664.6562 | 122.0123 | -113.6719 | 8.2443 | -0.003128 | -0.0049583 | -0.017312 | 0.018812 | -0.0048769 | -0.0050884 | 0.0024973 | 2.1561 | 2.1744 | 2.1744 | 8.2672 | 8.1665 | 8.2901 | 8.2169 | 8.2123 | 8.1985 | 7.9514 | 115.8463 | -6.0699 | 115.8279 | 121.9391 | -0.07782 | 121.6232 | -0.045777 | -0.01831 | 121.8887 | 121.8842 | 121.8384 | 115.8463 | 115.8279 | 121.8704 | 121.962 | 121.6232 | 115.8463 | 115.8279 | 121.962 | 121.8384 | 121.8704 | -6.0699 | -0.29297
665.6562 | 122.0123 | -113.3743 | 8.5602 | -0.003128 | -0.0081625 | -0.013894 | 0.020307 | -0.0046633 | -0.0072246 | 0.0010019 | 2.2797 | 2.2934 | 2.2751 | 8.606 | 8.4915 | 8.6197 | 8.5236 | 8.5236 | 8.5098 | 8.2077 | 115.6494 | -6.2668 | 115.654 | 121.9803 | -0.068665 | 121.582 | -0.050354 | 0.004578 | 121.8979 | 121.8979 | 121.8658 | 115.6677 | 115.654 | 121.8842 | 121.994 | 121.582 | 115.6677 | 115.654 | 121.994 | 121.8658 | 121.8842 | -6.2851 | -0.35248
666.6562 | 122.0398 | -113.1134 | 8.7982 | -0.010758 | -0.0053855 | -0.012185 | 0.020093 | -0.0055179 | -0.003593 | 0.0024973 | 2.3392 | 2.3529 | 2.3483 | 8.8486 | 8.7387 | 8.8806 | 8.7708 | 8.7845 | 8.7708 | 8.3862 | 115.4617 | -6.4453 | 115.4526 | 121.962 | -0.05951 | 121.4996 | -0.027466 | -0.009156 | 121.8842 | 121.8979 | 121.8521 | 115.4663 | 115.4526 | 121.8842 | 121.994 | 121.4996 | 115.4663 | 115.4526 | 121.994 | 121.8521 | 121.8842 | -6.4499 | -0.41199
667.6562 | 122.0627 | -113.6307 | 8.2672 | -0.003128 | -0.0043173 | -0.017953 | 0.01753 | -0.0065859 | -0.0038068 | -6.6324e-05 | 2.2293 | 2.2156 | 2.2202 | 8.3542 | 8.2443 | 8.3862 | 8.2489 | 8.313 | 8.2352 | 7.9788 | 115.8508 | -6.0516 | 115.86 | 121.9849 | -0.022888 | 121.6095 | -0.032044 | 0.009155 | 121.8796 | 121.9437 | 121.875 | 115.8463 | 115.86 | 121.8658 | 122.0169 | 121.6095 | 115.8463 | 115.86 | 122.0169 | 121.875 | 121.8658 | -6.0471 | -0.28839
668.6719 | 122.081 | -113.6536 | 8.2123 | -0.026017 | -0.0058127 | -0.016244 | 0.018171 | -0.0061587 | -0.0046612 | -0.00027992 | 2.2842 | 2.2293 | 2.2476 | 8.3221 | 8.2123 | 8.3496 | 8.139 | 8.2672 | 8.1711 | 7.9376 | 115.9012 | -5.983 | 115.9378 | 121.9757 | 0 | 121.5912 | -0.041198 | 0.036621 | 121.7926 | 121.9208 | 121.8658 | 115.8829 | 115.9378 | 121.8246 | 122.0032 | 121.5912 | 115.8829 | 115.9378 | 122.0032 | 121.8658 | 121.8246 | -5.9647 | -0.27466
669.6719 | 122.0673 | -113.4155 | 8.4549 | -0.003128 | -0.0055991 | -0.013467 | 0.018384 | -0.0044497 | -0.005302 | -6.6324e-05 | 2.3071 | 2.243 | 2.243 | 8.5602 | 8.4366 | 8.5648 | 8.3817 | 8.4869 | 8.4229 | 8.1161 | 115.6586 | -6.2119 | 115.7227 | 121.9757 | -0.018311 | 121.5317 | -0.032043 | 0.064087 | 121.7972 | 121.9025 | 121.8521 | 115.6586 | 115.7227 | 121.8384 | 121.9803 | 121.5317 | 115.6586 | 115.7227 | 121.9803 | 121.8521 | 121.8384 | -6.2119 | -0.33875
670.6719 | 122.0901 | -113.0585 | 8.8257 | -0.010758 | -0.0034629 | -0.012612 | 0.018171 | -0.0063723 | -0.0033794 | 0.0016427 | 2.417 | 2.3392 | 2.3483 | 8.931 | 8.8165 | 8.9539 | 8.7524 | 8.8715 | 8.7799 | 8.4 | 115.4068 | -6.4865 | 115.4755 | 121.9894 | -0.009156 | 121.4584 | -0.045777 | 0.068664 | 121.8109 | 121.9299 | 121.875 | 115.3976 | 115.4755 | 121.8384 | 122.0123 | 121.4584 | 115.3976 | 115.4755 | 122.0123 | 121.875 | 121.8384 | -6.4774 | -0.42572
671.6562 | 122.0215 | -113.7634 | 8.1665 | -0.003128 | -0.0041037 | -0.011331 | 0.018598 | -0.0057315 | -0.0050884 | 0.0033517 | 2.0966 | 2.124 | 2.1011 | 8.1894 | 8.0841 | 8.2077 | 8.1345 | 8.107 | 8.1024 | 7.8735 | 115.8646 | -6.0425 | 115.86 | 121.9528 | -0.082398 | 121.637 | -0.064087 | -0.004577 | 121.8979 | 121.8704 | 121.8475 | 115.8875 | 115.86 | 121.8658 | 121.9711 | 121.637 | 115.8875 | 115.86 | 121.9711 | 121.8475 | 121.8658 | -6.0654 | -0.29297
672.6562 | 122.0215 | -112.8571 | 9.0454 | -0.010758 | -0.0066673 | -0.014535 | 0.02223 | -0.0063723 | -0.0055156 | 0.0022837 | 2.3438 | 2.3483 | 2.33 | 9.0775 | 8.9859 | 9.1049 | 9.0317 | 9.0042 | 9.0317 | 8.5419 | 115.1871 | -6.6971 | 115.2008 | 121.9345 | -0.059509 | 121.3989 | -0.013733 | 0.013733 | 121.8887 | 121.8613 | 121.843 | 115.2054 | 115.2008 | 121.8887 | 121.962 | 121.3989 | 115.2054 | 115.2008 | 121.962 | 121.843 | 121.8887 | -6.7154 | -0.50354
673.6562 | 122.0261 | -113.0173 | 8.8852 | -0.010758 | -0.0041037 | -0.016885 | 0.020521 | -0.0072269 | -0.0048748 | 0.00036108 | 2.2888 | 2.2934 | 2.2842 | 8.9172 | 8.812 | 8.9493 | 8.8669 | 8.8531 | 8.8486 | 8.4412 | 115.3015 | -6.5918 | 115.3061 | 121.9345 | -0.073242 | 121.4584 | -0.036621 | 0.004577 | 121.8842 | 121.8704 | 121.8292 | 115.3107 | 115.3061 | 121.8658 | 121.9666 | 121.4584 | 115.3107 | 115.3061 | 121.9666 | 121.8292 | 121.8658 | -6.601 | -0.44403
674.6562 | 122.1039 | -113.118 | 8.7845 | -0.003128 | -0.0079489 | -0.016671 | 0.01988 | -0.0063723 | -0.0040204 | 0.00078828 | 2.4033 | 2.3483 | 2.3438 | 8.8943 | 8.7662 | 8.8943 | 8.7204 | 8.8394 | 8.7433 | 8.3633 | 115.4617 | -6.4362 | 115.5212 | 122.0123 | -0.018311 | 121.4813 | -0.041199 | 0.059509 | 121.8384 | 121.9574 | 121.8842 | 115.4663 | 115.5212 | 121.8613 | 122.0123 | 121.4813 | 115.4663 | 115.5212 | 122.0123 | 121.8842 | 121.8613 | -6.4407 | -0.42114
675.6719 | 122.0673 | -112.8296 | 9.0637 | 0.01213 | -0.0036765 | -0.017526 | 0.018598 | -0.0044497 | -0.0040204 | 0.0024973 | 2.5177 | 2.4399 | 2.4582 | 9.1873 | 9.0591 | 9.1965 | 8.9996 | 9.1187 | 9.0317 | 8.5556 | 115.2878 | -6.6238 | 115.3473 | 122.0169 | -0.004578 | 121.3852 | -0.032044 | 0.059509 | 121.8292 | 121.9482 | 121.8887 | 115.2695 | 115.3473 | 121.8613 | 122.0261 | 121.3852 | 115.2695 | 115.3473 | 122.0261 | 121.8887 | 121.8613 | -6.6055 | -0.50812
676.6719 | 122.049 | -112.9578 | 8.9584 | -0.018387 | -0.0070945 | -0.011758 | 0.018598 | -0.0042361 | -0.003593 | 0.0024973 | 2.3987 | 2.3987 | 2.3895 | 8.9996 | 8.8989 | 9.0363 | 8.9081 | 8.931 | 8.9035 | 8.4686 | 115.3473 | -6.5598 | 115.3564 | 121.9574 | -0.059509 | 121.4264 | -0.054932 | 0.009156 | 121.8658 | 121.8887 | 121.8567 | 115.3564 | 115.3564 | 121.8613 | 121.994 | 121.4264 | 115.3564 | 115.3564 | 121.994 | 121.8567 | 121.8613 | -6.5689 | -0.48981
677.6719 | 122.049 | -112.2986 | 9.6176 | -0.010758 | -0.0055991 | -0.012612 | 0.018384 | -0.0038089 | -0.003593 | 0.0024973 | 2.536 | 2.5681 | 2.5726 | 9.668 | 9.5444 | 9.7 | 9.5993 | 9.5856 | 9.5856 | 8.8165 | 114.8712 | -7.0496 | 114.8346 | 121.9666 | -0.073242 | 121.1151 | -0.032044 | -0.036621 | 121.8979 | 121.8842 | 121.843 | 114.8666 | 114.8346 | 121.8842 | 121.9986 | 121.1151 | 114.8666 | 114.8346 | 121.9986 | 121.843 | 121.8842 | -7.045 | -0.80109
678.6562 | 122.0535 | -112.6968 | 9.2285 | -0.010758 | -0.0062399 | -0.015176 | 0.016889 | -0.0044497 | -0.0014568 | 0.00036108 | 2.4216 | 2.4261 | 2.4216 | 9.2285 | 9.1415 | 9.2834 | 9.1599 | 9.1965 | 9.1507 | 8.6105 | 115.1184 | -6.8024 | 115.1184 | 121.9254 | -0.086975 | 121.3074 | -0.07782 | 0 | 121.8567 | 121.8933 | 121.8384 | 115.123 | 115.1184 | 121.8475 | 121.9803 | 121.3074 | 115.123 | 115.1184 | 121.9803 | 121.8384 | 121.8475 | -6.8069 | -0.61798
679.6562 | 122.0627 | -116.2079 | 5.6946 | -0.010758 | -0.0081625 | -0.015817 | 0.021375 | -0.0065859 | -0.0046612 | -0.00049352 | 1.4374 | 1.4236 | 1.4374 | 5.7266 | 5.6305 | 5.7495 | 5.6305 | 5.6854 | 5.6534 | 5.5801 | 117.6453 | -4.2709 | 117.6453 | 121.9345 | -0.064087 | 121.788 | -0.041199 | 0 | 121.8384 | 121.8933 | 121.8384 | 117.6315 | 117.6453 | 121.8613 | 121.9574 | 121.788 | 117.6315 | 117.6453 | 121.9574 | 121.8384 | 121.8613 | -4.2572 | -0.11444
680.6562 | 122.0764 | -116.5283 | 5.3879 | -0.018387 | -0.0053855 | -0.011971 | 0.019453 | -0.0080813 | -0.0038068 | 0.0037791 | 1.3229 | 1.3184 | 1.3229 | 5.4199 | 5.3284 | 5.4565 | 5.2826 | 5.3696 | 5.3513 | 5.2826 | 117.8513 | -4.0695 | 117.8513 | 121.9482 | -0.059509 | 121.8109 | -0.036621 | 0 | 121.8109 | 121.8979 | 121.8567 | 117.8467 | 117.8513 | 121.8796 | 121.9849 | 121.8109 | 117.8467 | 117.8513 | 121.9849 | 121.8567 | 121.8796 | -4.0649 | -0.10528
681.6562 | 122.0627 | -115.8646 | 6.0516 | -0.003128 | -0.0058127 | -0.011758 | 0.01988 | -0.0070133 | -0.005302 | 0.00014748 | 1.5198 | 1.5335 | 1.5289 | 6.0883 | 5.9921 | 6.1066 | 6.0104 | 6.0379 | 6.0379 | 5.928 | 117.3935 | -4.5181 | 117.3843 | 121.9528 | -0.05951 | 121.7926 | -0.013733 | -0.009156 | 121.875 | 121.9025 | 121.8567 | 117.3981 | 117.3843 | 121.9025 | 121.9711 | 121.7926 | 117.3981 | 117.3843 | 121.9711 | 121.8567 | 121.9025 | -4.5227 | -0.1236
682.6719 | 122.049 | -117.1829 | 4.7379 | 0.0045015 | -0.0064535 | -0.017953 | 0.018598 | -0.0076541 | -0.0044476 | 0.0018565 | 1.0895 | 1.0895 | 1.0941 | 4.6875 | 4.6234 | 4.7424 | 4.6646 | 4.6738 | 4.6783 | 4.5776 | 118.277 | -3.6484 | 118.2724 | 121.8704 | -0.11444 | 121.7606 | -0.059509 | -0.004577 | 121.8475 | 121.8567 | 121.8063 | 118.2724 | 118.2724 | 121.8613 | 121.9254 | 121.7606 | 118.2724 | 118.2724 | 121.9254 | 121.8063 | 121.8613 | -3.6438 | -0.16022
683.6719 | 122.0856 | -118.2083 | 3.685 | -0.003128 | -0.0083763 | -0.013253 | 0.01988 | -0.0078677 | -0.005943 | 0.00014748 | 0.8194 | 0.82398 | 0.81482 | 3.7262 | 3.6438 | 3.772 | 3.5843 | 3.7125 | 3.6667 | 3.6438 | 119.0231 | -2.861 | 119.0277 | 121.9345 | -0.041199 | 121.8521 | -0.018311 | 0.004578 | 121.7926 | 121.9208 | 121.8521 | 119.0323 | 119.0277 | 121.875 | 121.9803 | 121.8521 | 119.0323 | 119.0277 | 121.9803 | 121.8521 | 121.875 | -2.8702 | -0.041199
684.6719 | 122.1497 | -117.6041 | 4.2709 | 0.0045015 | -0.0081625 | -0.020089 | 0.020307 | -0.0076541 | -0.0020978 | 0.0035653 | 0.98877 | 0.9613 | 0.98877 | 4.3442 | 4.2801 | 4.39 | 4.1336 | 4.3213 | 4.2343 | 4.216 | 118.5928 | -3.3096 | 118.5928 | 121.9482 | 0.009155 | 121.8201 | -0.036621 | 0 | 121.7377 | 121.9254 | 121.8842 | 118.5654 | 118.5928 | 121.8384 | 121.994 | 121.8201 | 118.5654 | 118.5928 | 121.994 | 121.8842 | 121.8384 | -3.2822 | -0.054932
685.6562 | 122.1725 | -116.7664 | 5.0949 | -0.010758 | -0.010085 | -0.01368 | 0.01518 | -0.0063723 | -0.0012432 | 0.0010019 | 1.2955 | 1.1307 | 1.2177 | 5.2643 | 5.1773 | 5.2917 | 4.8843 | 5.246 | 5.0629 | 5.0491 | 117.984 | -3.9642 | 118.0618 | 122.0306 | 0.082397 | 121.8155 | -0.032044 | 0.07782 | 121.6507 | 122.0123 | 121.9437 | 117.897 | 118.0618 | 121.8292 | 122.0581 | 121.8155 | 117.897 | 118.0618 | 122.0581 | 121.9437 | 121.8292 | -3.8773 | -0.045777
686.6719 | 122.168 | -117.1051 | 4.8294 | -0.010758 | -0.012862 | -0.02073 | 0.016889 | -0.010218 | -0.0063702 | 0.00078828 | 1.2863 | 1.1719 | 1.2451 | 4.9942 | 4.9118 | 4.9988 | 4.6829 | 4.9942 | 4.7836 | 4.7791 | 118.3502 | -3.6575 | 118.3914 | 122.0993 | 0.082397 | 121.8842 | -0.045777 | 0.041199 | 121.788 | 122.0993 | 122.0169 | 118.277 | 118.3914 | 121.8887 | 122.1039 | 121.8842 | 118.277 | 118.3914 | 122.1039 | 122.0169 | 121.8887 | -3.5843 | -0.050354
687.6562 | 122.1634 | -117.5766 | 4.2984 | -0.003128 | -0.0083763 | -0.017312 | 0.017744 | -0.0097903 | -0.0065838 | 0.0022837 | 1.0895 | 0.95673 | 1.062 | 4.4449 | 4.3625 | 4.4952 | 4.1016 | 4.4266 | 4.2618 | 4.2709 | 118.6386 | -3.3417 | 118.6661 | 122.0215 | 0.064087 | 121.8475 | -0.036621 | 0.027466 | 121.6782 | 122.0032 | 121.9391 | 118.5333 | 118.6661 | 121.8384 | 122.0718 | 121.8475 | 118.5333 | 118.6661 | 122.0718 | 121.9391 | 121.8384 | -3.2364 | -0.027466
688.6562 | 122.1588 | -117.7002 | 4.1977 | 0.0045015 | -0.0085899 | -0.011971 | 0.021162 | -0.0074405 | -0.0050884 | -0.00027992 | 1.0162 | 0.96588 | 0.99335 | 4.2755 | 4.1931 | 4.3259 | 4.0146 | 4.2664 | 4.1336 | 4.129 | 118.6935 | -3.2318 | 118.7164 | 121.9757 | -0.004578 | 121.8292 | -0.064087 | 0.022888 | 121.7148 | 121.9666 | 121.8933 | 118.6661 | 118.7164 | 121.8338 | 122.0261 | 121.8292 | 118.6661 | 118.7164 | 122.0261 | 121.8933 | 121.8338 | -3.2043 | -0.068665
689.6719 | 122.1909 | -114.7522 | 7.1457 | -0.003128 | -0.0085899 | -0.013894 | 0.017316 | -0.0089359 | -0.0063702 | 0.0020701 | 1.8494 | 1.6983 | 1.8082 | 7.3517 | 7.2235 | 7.3746 | 6.926 | 7.3013 | 7.0908 | 7.0312 | 116.5604 | -5.4474 | 116.6016 | 122.1039 | 0.07782 | 121.7834 | -0.054932 | 0.041198 | 121.6782 | 122.0535 | 121.9757 | 116.4505 | 116.6016 | 121.843 | 122.1268 | 121.7834 | 116.4505 | 116.6016 | 122.1268 | 121.9757 | 121.843 | -5.3375 | -0.11444
690.6719 | 122.1542 | -117.5812 | 4.335 | -0.010758 | -0.012862 | -0.014535 | 0.018171 | -0.010859 | -0.0065838 | -0.00049352 | 1.0849 | 0.94299 | 1.0574 | 4.4586 | 4.3854 | 4.4998 | 4.1428 | 4.4266 | 4.2801 | 4.2847 | 118.6386 | -3.392 | 118.6661 | 122.0398 | 0.050354 | 121.8658 | -0.054932 | 0.027466 | 121.7239 | 122.0078 | 121.9666 | 118.5242 | 118.6661 | 121.8613 | 122.081 | 121.8658 | 118.5242 | 118.6661 | 122.081 | 121.9666 | 121.8613 | -3.2776 | -0.050354
691.6719 | 122.1725 | -117.4484 | 4.5227 | -0.010758 | -0.01393 | -0.021157 | 0.018384 | -0.011713 | -0.0061566 | 0.00078828 | 1.1948 | 1.0849 | 1.1581 | 4.6692 | 4.5593 | 4.6646 | 4.3945 | 4.6509 | 4.454 | 4.4678 | 118.6066 | -3.4378 | 118.6432 | 122.1176 | 0.036621 | 121.9162 | -0.068664 | 0.036621 | 121.843 | 122.0993 | 122.0078 | 118.5333 | 118.6432 | 121.9025 | 122.113 | 121.9162 | 118.5333 | 118.6432 | 122.113 | 122.0078 | 121.9025 | -3.3646 | -0.054932
692.6562 | 122.1817 | -117.5308 | 4.4403 | -0.010758 | -0.014358 | -0.01838 | 0.018598 | -0.0087223 | -0.004234 | 0.0035653 | 1.1032 | 1.0117 | 1.0803 | 4.5547 | 4.454 | 4.5731 | 4.2801 | 4.5319 | 4.3945 | 4.3808 | 118.6111 | -3.4287 | 118.634 | 122.0856 | 0.013733 | 121.9116 | -0.045777 | 0.022888 | 121.8109 | 122.0627 | 121.9849 | 118.5425 | 118.634 | 121.9254 | 122.1039 | 121.9116 | 118.5425 | 118.634 | 122.1039 | 121.9849 | 121.9254 | -3.36 | -0.05951
693.6562 | 122.168 | -114.8575 | 7.0862 | -0.003128 | -0.017135 | -0.017098 | 0.016676 | -0.011286 | -0.0065838 | 0.00078828 | 1.8265 | 1.7532 | 1.8219 | 7.2372 | 7.1503 | 7.283 | 6.9534 | 7.2281 | 7.0404 | 6.9626 | 116.6794 | -5.3329 | 116.684 | 122.0947 | 0.064087 | 121.8201 | -0.045777 | 0.004578 | 121.8109 | 122.0856 | 122.0078 | 116.6107 | 116.684 | 121.8979 | 122.1405 | 121.8201 | 116.6107 | 116.684 | 122.1405 | 122.0078 | 121.8979 | -5.2643 | -0.1236
694.6562 | 122.1909 | -115.5304 | 6.395 | 0.0045015 | -0.012435 | -0.017739 | 0.016462 | -0.011927 | -0.0063702 | 0.0014291 | 1.6617 | 1.5793 | 1.6251 | 6.5506 | 6.4453 | 6.5918 | 6.2668 | 6.5414 | 6.3766 | 6.308 | 117.1555 | -4.8157 | 117.1921 | 122.081 | 0.050354 | 121.8384 | -0.01831 | 0.036621 | 121.7972 | 122.0718 | 121.9757 | 117.1097 | 117.1921 | 121.907 | 122.1222 | 121.8384 | 117.1097 | 117.1921 | 122.1222 | 121.9757 | 121.907 | -4.7699 | -0.086975
695.6562 | 122.168 | -115.6494 | 6.2851 | 0.0045015 | -0.013717 | -0.019662 | 0.019453 | -0.011072 | -0.0040204 | 0.0024973 | 1.5884 | 1.442 | 1.5427 | 6.4545 | 6.34 | 6.4728 | 6.1111 | 6.4178 | 6.2302 | 6.221 | 117.1921 | -4.8431 | 117.2379 | 122.1039 | 0.054932 | 121.8704 | -0.054931 | 0.045776 | 121.7606 | 122.0673 | 121.9894 | 117.0914 | 117.2379 | 121.8796 | 122.1222 | 121.8704 | 117.0914 | 117.2379 | 122.1222 | 121.9894 | 121.8796 | -4.7424 | -0.064087
696.6719 | 122.081 | -115.8005 | 6.2439 | -0.003128 | -0.0077353 | -0.017098 | 0.022657 | -0.010645 | -0.0029522 | -6.6324e-05 | 1.5518 | 1.5198 | 1.5198 | 6.3171 | 6.2027 | 6.3034 | 6.2439 | 6.2714 | 6.2073 | 6.1111 | 117.3203 | -4.7241 | 117.3523 | 122.1176 | -0.041198 | 121.9116 | -0.036621 | 0.032044 | 122.0444 | 122.0718 | 122.0032 | 117.3203 | 117.3523 | 122.0078 | 122.1039 | 121.9116 | 117.3203 | 117.3523 | 122.1039 | 122.0032 | 122.0078 | -4.7241 | -0.13275
697.6719 | 122.1909 | -115.8234 | 6.1569 | 0.0045015 | -0.013503 | -0.021157 | 0.016462 | -0.0085085 | -0.0061566 | 0.0014291 | 1.4557 | 1.3824 | 1.4374 | 6.3171 | 6.221 | 6.3446 | 6.0287 | 6.2897 | 6.1066 | 6.0699 | 117.2607 | -4.7745 | 117.2791 | 122.1405 | 0.064087 | 121.8933 | -0.050354 | 0.01831 | 121.8521 | 122.113 | 122.0444 | 117.2058 | 117.2791 | 121.9299 | 122.168 | 121.8933 | 117.2058 | 117.2791 | 122.168 | 122.0444 | 121.9299 | -4.7195 | -0.086975
698.6719 | 122.2092 | -115.8096 | 6.1569 | -0.003128 | -0.013717 | -0.019662 | 0.017316 | -0.010431 | -0.007652 | 0.0010019 | 1.474 | 1.3687 | 1.4511 | 6.3309 | 6.221 | 6.34 | 6.0242 | 6.308 | 6.1157 | 6.0883 | 117.2607 | -4.7882 | 117.2836 | 122.1405 | 0.064087 | 121.8979 | -0.041198 | 0.022888 | 121.8338 | 122.1176 | 122.0306 | 117.1783 | 117.2836 | 121.9254 | 122.1497 | 121.8979 | 117.1783 | 117.2836 | 122.1497 | 122.0306 | 121.9254 | -4.7058 | -0.068664
699.6562 | 122.2137 | -115.8096 | 6.1386 | -0.003128 | -0.01393 | -0.020089 | 0.019453 | -0.013208 | -0.0065838 | 0.0016427 | 1.5244 | 1.3641 | 1.4648 | 6.3721 | 6.2622 | 6.3766 | 5.9921 | 6.3538 | 6.0928 | 6.0837 | 117.2745 | -4.7745 | 117.334 | 122.1817 | 0.1236 | 121.8933 | -0.045777 | 0.059509 | 121.8018 | 122.1634 | 122.0718 | 117.1738 | 117.334 | 121.9025 | 122.1863 | 121.8933 | 117.1738 | 117.334 | 122.1863 | 122.0718 | 121.9025 | -4.6738 | -0.054932
700.6562 | 122.2046 | -115.8005 | 6.1661 | -0.003128 | -0.013076 | -0.021371 | 0.019025 | -0.011286 | -0.0067974 | -0.00070712 | 1.5198 | 1.3687 | 1.4603 | 6.3538 | 6.2531 | 6.3721 | 5.9921 | 6.3263 | 6.1111 | 6.0837 | 117.2607 | -4.7974 | 117.3203 | 122.1542 | 0.086975 | 121.8842 | -0.054932 | 0.059509 | 121.7926 | 122.1268 | 122.0535 | 117.1692 | 117.3203 | 121.9116 | 122.1725 | 121.8842 | 117.1692 | 117.3203 | 122.1725 | 122.0535 | 121.9116 | -4.7058 | -0.082398
701.6719 | 122.1497 | -115.7867 | 6.2302 | -0.003128 | -0.0060263 | -0.014962 | 0.023939 | -0.010004 | -0.0063702 | 0.0014291 | 1.5198 | 1.4511 | 1.4786 | 6.3629 | 6.2302 | 6.3446 | 6.1432 | 6.2851 | 6.1752 | 6.102 | 117.2653 | -4.7791 | 117.3065 | 122.1497 | 0 | 121.8887 | -0.054932 | 0.041198 | 121.9299 | 122.0718 | 122.0169 | 117.2379 | 117.3065 | 121.962 | 122.1313 | 121.8887 | 117.2379 | 117.3065 | 122.1313 | 122.0169 | 121.962 | -4.7516 | -0.12817
702.6719 | 122.2183 | -115.7043 | 6.2576 | 0.0045015 | -0.01393 | -0.019235 | 0.016676 | -0.010004 | -0.0048748 | 0.00057468 | 1.5427 | 1.4282 | 1.4969 | 6.459 | 6.3766 | 6.4819 | 6.1203 | 6.4224 | 6.2256 | 6.189 | 117.2012 | -4.8294 | 117.247 | 122.1634 | 0.11902 | 121.8933 | -0.032043 | 0.045777 | 121.8246 | 122.1268 | 122.081 | 117.1326 | 117.247 | 121.9299 | 122.1863 | 121.8933 | 117.1326 | 117.247 | 122.1863 | 122.081 | 121.9299 | -4.7607 | -0.068664
703.6719 | 122.2275 | -115.7455 | 6.2302 | 0.0045015 | -0.013503 | -0.019235 | 0.017103 | -0.0087223 | -0.0050884 | 0.00057468 | 1.5244 | 1.4191 | 1.506 | 6.4316 | 6.3354 | 6.4362 | 6.0608 | 6.3995 | 6.1661 | 6.1478 | 117.2516 | -4.8111 | 117.2699 | 122.1771 | 0.10528 | 121.8933 | -0.064087 | 0.018311 | 121.8063 | 122.1451 | 122.081 | 117.1646 | 117.2699 | 121.9116 | 122.1817 | 121.8933 | 117.1646 | 117.2699 | 122.1817 | 122.081 | 121.9116 | -4.7241 | -0.082398
704.6719 | 122.2183 | -117.9108 | 4.0604 | 0.0045015 | -0.013076 | -0.020516 | 0.019453 | -0.01214 | -0.0082928 | 0.0020701 | 0.97961 | 0.83313 | 0.93842 | 4.2709 | 4.1977 | 4.2755 | 3.891 | 4.2572 | 4.0237 | 4.0421 | 118.8492 | -3.2272 | 118.8904 | 122.1817 | 0.13733 | 121.9528 | -0.036621 | 0.041198 | 121.8018 | 122.168 | 122.1085 | 118.7439 | 118.8904 | 121.9345 | 122.1863 | 121.9528 | 118.7439 | 118.8904 | 122.1863 | 122.1085 | 121.9345 | -3.1219 | -0.018311
705.6719 | 122.2366 | -118.0527 | 3.9322 | -0.010758 | -0.012221 | -0.021585 | 0.020307 | -0.011927 | -0.0061566 | 0.0010019 | 0.98419 | 0.82855 | 0.92926 | 4.129 | 4.0466 | 4.1428 | 3.772 | 4.1153 | 3.8956 | 3.9139 | 118.9819 | -3.1036 | 119.0369 | 122.1817 | 0.11444 | 121.9666 | -0.036621 | 0.054932 | 121.8246 | 122.168 | 122.0993 | 118.8812 | 119.0369 | 121.9482 | 122.1954 | 121.9666 | 118.8812 | 119.0369 | 122.1954 | 122.0993 | 121.9482 | -3.0029 | -0.018311
706.6562 | 122.1268 | -118.4601 | 3.598 | 0.0045015 | -0.012862 | -0.019876 | 0.021802 | -0.012568 | -0.0065838 | 0.00057468 | 0.87891 | 0.79193 | 0.85602 | 3.6804 | 3.5934 | 3.6804 | 3.4973 | 3.6484 | 3.5385 | 3.511 | 119.3161 | -2.8061 | 119.339 | 122.1405 | -0.004577 | 121.9711 | -0.059509 | 0.022888 | 121.9574 | 122.1085 | 122.0535 | 119.252 | 119.339 | 121.9986 | 122.1405 | 121.9711 | 119.252 | 119.339 | 122.1405 | 122.0535 | 121.9986 | -2.742 | -0.086975
707.6562 | 122.1268 | -118.3777 | 3.6804 | -0.010758 | -0.012008 | -0.016885 | 0.021802 | -0.0097903 | -0.0074384 | -6.6324e-05 | 0.89722 | 0.80566 | 0.86975 | 3.7537 | 3.6896 | 3.7628 | 3.5797 | 3.7262 | 3.6209 | 3.5889 | 119.2474 | -2.8748 | 119.2749 | 122.1313 | 0.009155 | 121.9666 | -0.059509 | 0.027466 | 121.9574 | 122.1039 | 122.0673 | 119.1833 | 119.2749 | 121.9986 | 122.1405 | 121.9666 | 119.1833 | 119.2749 | 122.1405 | 122.0673 | 121.9986 | -2.8107 | -0.091553
708.6562 | 122.2321 | -118.3182 | 3.717 | 0.0045015 | -0.014785 | -0.017953 | 0.018171 | -0.011499 | -0.007011 | 0.00036108 | 0.89722 | 0.76904 | 0.86975 | 3.891 | 3.804 | 3.9368 | 3.5294 | 3.8864 | 3.6713 | 3.6896 | 119.1879 | -2.948 | 119.2154 | 122.2092 | 0.086975 | 122.0078 | -0.045776 | 0.027466 | 121.8475 | 122.2046 | 122.1222 | 119.0872 | 119.2154 | 121.9894 | 122.2549 | 122.0078 | 119.0872 | 119.2154 | 122.2549 | 122.1222 | 121.9894 | -2.8473 | -0.027466
709.6719 | 122.2366 | -117.9749 | 4.0329 | -0.010758 | -0.012862 | -0.020303 | 0.019453 | -0.010859 | -0.0044476 | 0.0012155 | 0.98419 | 0.82398 | 0.92468 | 4.248 | 4.1473 | 4.248 | 3.8589 | 4.2297 | 4.0054 | 4.0009 | 118.8995 | -3.2089 | 118.959 | 122.2229 | 0.11444 | 121.9757 | -0.027466 | 0.059509 | 121.8338 | 122.2046 | 122.1222 | 118.7988 | 118.959 | 121.9803 | 122.2229 | 121.9757 | 118.7988 | 118.959 | 122.2229 | 122.1222 | 121.9803 | -3.1082 | -0.032044
710.6719 | 122.2046 | -117.6132 | 4.4037 | -0.003128 | -0.012221 | -0.016458 | 0.019453 | -0.011499 | -0.0080792 | 0.00078828 | 1.0895 | 0.95673 | 1.0529 | 4.5593 | 4.4907 | 4.5776 | 4.2801 | 4.5502 | 4.335 | 4.3488 | 118.6661 | -3.447 | 118.7027 | 122.1725 | 0.086975 | 121.962 | -0.068665 | 0.036622 | 121.8933 | 122.1634 | 122.1039 | 118.5699 | 118.7027 | 121.9482 | 122.1909 | 121.962 | 118.5699 | 118.7027 | 122.1909 | 122.1039 | 121.9482 | -3.3508 | -0.054932
711.6719 | 122.1954 | -117.4896 | 4.5456 | -0.010758 | -0.0094443 | -0.014321 | 0.02223 | -0.0095767 | -0.0061566 | 0.00057468 | 1.1261 | 0.99792 | 1.0895 | 4.6967 | 4.5914 | 4.7058 | 4.4174 | 4.6646 | 4.4769 | 4.4678 | 118.5791 | -3.5477 | 118.6157 | 122.1863 | 0.045777 | 121.9574 | -0.068664 | 0.036621 | 121.907 | 122.1542 | 122.081 | 118.4875 | 118.6157 | 121.9666 | 122.1954 | 121.9574 | 118.4875 | 118.6157 | 122.1954 | 122.081 | 121.9666 | -3.4561 | -0.07782
712.6719 | 122.1817 | -118.071 | 3.9505 | -0.003128 | -0.012008 | -0.020089 | 0.020307 | -0.0097903 | -0.0091472 | 0.0018565 | 0.97961 | 0.85144 | 0.92926 | 4.1016 | 4.0054 | 4.0924 | 3.8269 | 4.0741 | 3.891 | 3.891 | 119.0002 | -3.0991 | 119.0506 | 122.1725 | 0.054932 | 121.962 | -0.059509 | 0.050354 | 121.8979 | 122.1451 | 122.0764 | 118.9224 | 119.0506 | 121.962 | 122.1634 | 121.962 | 118.9224 | 119.0506 | 122.1634 | 122.0764 | 121.962 | -3.0212 | -0.059509
713.6562 | 122.0856 | -117.897 | 4.1611 | -0.003128 | -0.010085 | -0.017526 | 0.023298 | -0.0097903 | -0.0044476 | -0.00092072 | 0.95215 | 0.95673 | 0.9613 | 4.184 | 4.097 | 4.1931 | 4.1428 | 4.1336 | 4.1061 | 4.0558 | 118.8583 | -3.2043 | 118.8492 | 122.081 | -0.064087 | 121.9528 | -0.054932 | -0.009156 | 122.0398 | 122.0306 | 121.994 | 118.8538 | 118.8492 | 122.0032 | 122.0901 | 121.9528 | 118.8538 | 118.8492 | 122.0901 | 121.994 | 122.0032 | -3.1998 | -0.10529
714.6562 | 122.113 | -117.6315 | 4.4266 | -0.003128 | -0.011153 | -0.021157 | 0.021162 | -0.0078677 | -0.0061566 | -0.00070712 | 0.98877 | 1.0025 | 1.0117 | 4.4769 | 4.3854 | 4.4861 | 4.454 | 4.4357 | 4.4174 | 4.3396 | 118.6432 | -3.4241 | 118.6203 | 122.1085 | -0.041199 | 121.9711 | -0.009156 | -0.022888 | 122.0856 | 122.0673 | 122.0169 | 118.634 | 118.6203 | 122.0489 | 122.1176 | 121.9711 | 118.634 | 118.6203 | 122.1176 | 122.0169 | 122.0489 | -3.4149 | -0.086975
715.6562 | 122.2412 | -117.7963 | 4.1794 | -0.010758 | -0.015212 | -0.021585 | 0.017316 | -0.0095767 | -0.0078656 | 0.0010019 | 1.0391 | 0.89722 | 0.98419 | 4.3945 | 4.3076 | 4.3991 | 4.0375 | 4.3945 | 4.1519 | 4.1794 | 118.7805 | -3.2822 | 118.8354 | 122.1909 | 0.12817 | 121.9757 | -0.027465 | 0.054932 | 121.8338 | 122.1909 | 122.1039 | 118.6935 | 118.8354 | 121.9482 | 122.1954 | 121.9757 | 118.6935 | 118.8354 | 122.1954 | 122.1039 | 121.9482 | -3.1952 | 0
716.6719 | 122.1909 | -116.4185 | 5.5939 | 0.0045015 | -0.010299 | -0.014749 | 0.020948 | -0.0091495 | -0.007652 | -0.00027992 | 1.3687 | 1.2131 | 1.3184 | 5.7495 | 5.6534 | 5.7587 | 5.4886 | 5.7083 | 5.5344 | 5.5069 | 117.7368 | -4.3808 | 117.7872 | 122.168 | 0.059509 | 121.9254 | -0.059509 | 0.050354 | 121.907 | 122.1268 | 122.0718 | 117.6315 | 117.7872 | 121.9528 | 122.1771 | 121.9254 | 117.6315 | 117.7872 | 122.1771 | 122.0718 | 121.9528 | -4.2755 | -0.086975
717.6719 | 122.113 | -115.4434 | 6.6376 | -0.003128 | -0.010512 | -0.015389 | 0.019239 | -0.0087223 | -0.0085064 | 0.00078828 | 1.4557 | 1.4328 | 1.442 | 6.6238 | 6.5414 | 6.665 | 6.5781 | 6.6284 | 6.546 | 6.4087 | 116.8854 | -5.2048 | 116.8991 | 122.0673 | -0.09613 | 121.8521 | -0.091552 | 0.013732 | 122.0215 | 122.0718 | 121.9849 | 116.8762 | 116.8991 | 121.9894 | 122.1085 | 121.8521 | 116.8762 | 116.8991 | 122.1085 | 121.9849 | 121.9894 | -5.1956 | -0.22888
718.6719 | 122.1039 | -115.2649 | 6.7795 | -0.010758 | -0.010726 | -0.014321 | 0.019025 | -0.0080813 | -0.0082928 | 0.0024973 | 1.6296 | 1.5976 | 1.6205 | 6.8619 | 6.7612 | 6.8619 | 6.7749 | 6.8069 | 6.7337 | 6.633 | 116.8854 | -5.1819 | 116.8945 | 122.1268 | -0.018311 | 121.8979 | -0.045776 | 0.009156 | 122.0398 | 122.0718 | 122.0261 | 116.8625 | 116.8945 | 121.9986 | 122.1268 | 121.8979 | 116.8625 | 116.8945 | 122.1268 | 122.0261 | 121.9986 | -5.159 | -0.14648
719.6719 | 122.1268 | -115.9836 | 6.0654 | -0.003128 | -0.010299 | -0.018594 | 0.018384 | -0.010218 | -0.0078656 | 0.0018565 | 1.4282 | 1.387 | 1.4099 | 6.1478 | 6.0471 | 6.1523 | 6.0333 | 6.0974 | 6.0287 | 5.9509 | 117.3935 | -4.6783 | 117.4118 | 122.1313 | -0.018311 | 121.9345 | -0.036621 | 0.018311 | 122.0169 | 122.081 | 122.0306 | 117.3706 | 117.4118 | 122.0123 | 122.1359 | 121.9345 | 117.3706 | 117.4118 | 122.1359 | 122.0306 | 122.0123 | -4.6555 | -0.11444
720.6562 | 122.1176 | -115.7867 | 6.2485 | -0.010758 | -0.0085899 | -0.019021 | 0.021589 | -0.0095767 | -0.0078656 | 0.0010019 | 1.4282 | 1.4557 | 1.4511 | 6.3126 | 6.2119 | 6.3171 | 6.2622 | 6.2622 | 6.2164 | 6.1203 | 117.2379 | -4.7928 | 117.215 | 122.0993 | -0.036621 | 121.907 | -0.032043 | -0.022888 | 122.049 | 122.049 | 121.9986 | 117.2424 | 117.215 | 122.0032 | 122.1039 | 121.907 | 117.2424 | 117.215 | 122.1039 | 121.9986 | 122.0032 | -4.7974 | -0.12817
721.6562 | 122.113 | -115.0085 | 7.0404 | -0.010758 | -0.0088035 | -0.011971 | 0.020093 | -0.010645 | -0.0078656 | 0.0018565 | 1.6342 | 1.6159 | 1.6296 | 7.0724 | 6.9809 | 7.0862 | 7.0541 | 7.0358 | 6.9992 | 6.8298 | 116.6382 | -5.4245 | 116.6428 | 122.081 | -0.059509 | 121.8384 | -0.041198 | 0.004577 | 122.0627 | 122.0444 | 121.9894 | 116.6245 | 116.6428 | 122.0078 | 122.0947 | 121.8384 | 116.6245 | 116.6428 | 122.0947 | 121.9894 | 122.0078 | -5.4108 | -0.21057
722.6562 | 122.2458 | -114.6149 | 7.3746 | -0.003128 | -0.012435 | -0.016458 | 0.018171 | -0.010645 | -0.005943 | 0.0012155 | 1.799 | 1.6617 | 1.7624 | 7.5989 | 7.5027 | 7.6126 | 7.2235 | 7.5623 | 7.3334 | 7.283 | 116.3773 | -5.7129 | 116.4139 | 122.2137 | 0.12817 | 121.8979 | -0.041199 | 0.036621 | 121.8384 | 122.1771 | 122.1176 | 116.2766 | 116.4139 | 121.9482 | 122.2275 | 121.8979 | 116.2766 | 116.4139 | 122.2275 | 122.1176 | 121.9482 | -5.6122 | -0.091553
723.6719 | 122.1817 | -113.356 | 8.6563 | -0.003128 | -0.011367 | -0.017312 | 0.018598 | -0.0097903 | -0.0065838 | 0.0012155 | 2.0966 | 1.9867 | 2.0508 | 8.8211 | 8.7067 | 8.8303 | 8.5876 | 8.7891 | 8.6014 | 8.3038 | 115.4068 | -6.6696 | 115.4526 | 122.1771 | 0.050354 | 121.6599 | -0.054932 | 0.045777 | 121.9437 | 122.1451 | 122.0627 | 115.3427 | 115.4526 | 121.9574 | 122.1863 | 121.6599 | 115.3427 | 115.4526 | 122.1863 | 122.0627 | 121.9574 | -6.6055 | -0.35248
724.6719 | 122.1222 | -111.6531 | 10.3912 | -0.010758 | -0.011794 | -0.019662 | 0.017957 | -0.010004 | -0.007652 | -0.00092072 | 2.4765 | 2.4902 | 2.5131 | 10.4965 | 10.3775 | 10.524 | 10.4187 | 10.4416 | 10.3455 | 9.0317 | 114.1663 | -7.901 | 114.1296 | 122.1497 | -0.013733 | 120.6848 | -0.045776 | -0.036622 | 122.0718 | 122.0947 | 122.0306 | 114.1434 | 114.1296 | 121.9986 | 122.1771 | 120.6848 | 114.1434 | 114.1296 | 122.1771 | 122.0306 | 121.9986 | -7.8781 | -1.3596
725.6719 | 122.1359 | -110.2295 | 11.8103 | -0.010758 | -0.010085 | -0.019662 | 0.01753 | -0.0087223 | -0.0061566 | 0.0010019 | 2.8519 | 2.8198 | 2.8473 | 11.9202 | 11.8149 | 11.9431 | 11.8332 | 11.8744 | 11.7645 | 9.1278 | 113.0768 | -8.9905 | 113.0814 | 122.1497 | 0.004577 | 119.3573 | -0.045777 | 0.004578 | 122.0627 | 122.1039 | 122.0444 | 113.0493 | 113.0814 | 121.994 | 122.1725 | 119.3573 | 113.0493 | 113.0814 | 122.1725 | 122.0444 | 121.994 | -8.963 | -2.6825
726.6719 | 122.1451 | -111.438 | 10.6018 | 0.0045015 | -0.0079489 | -0.015817 | 0.019453 | -0.0087223 | -0.0067974 | -6.6324e-05 | 2.5681 | 2.5223 | 2.5589 | 10.7254 | 10.6247 | 10.7391 | 10.6247 | 10.675 | 10.5881 | 9.0408 | 113.9969 | -8.0795 | 114.006 | 122.1634 | 0.022888 | 120.4788 | -0.013733 | 0.009155 | 122.0627 | 122.113 | 122.0627 | 113.9603 | 114.006 | 122.0261 | 122.1771 | 120.4788 | 113.9603 | 114.006 | 122.1771 | 122.0627 | 122.0261 | -8.0429 | -1.561
727.6562 | 122.1313 | -110.733 | 11.3388 | -0.010758 | -0.0088035 | -0.017526 | 0.019453 | -0.0089359 | -0.0080792 | 0.0014291 | 2.7374 | 2.7374 | 2.7328 | 11.4395 | 11.3251 | 11.4532 | 11.3937 | 11.38 | 11.3159 | 9.1095 | 113.4659 | -8.6014 | 113.4705 | 122.1725 | -0.013733 | 119.8425 | -0.022888 | 0.004578 | 122.1268 | 122.113 | 122.0581 | 113.4705 | 113.4705 | 122.0489 | 122.1863 | 119.8425 | 113.4705 | 113.4705 | 122.1863 | 122.0581 | 122.0489 | -8.606 | -2.2293
728.6562 | 122.1222 | -110.939 | 11.1191 | -0.003128 | -0.0090171 | -0.018807 | 0.019025 | -0.0085085 | -0.0074384 | 0.00014748 | 2.6413 | 2.6688 | 2.6596 | 11.2152 | 11.0962 | 11.2106 | 11.1694 | 11.1465 | 11.087 | 9.0958 | 113.5986 | -8.4503 | 113.5803 | 122.1542 | -0.022889 | 120.0348 | -0.032044 | -0.018311 | 122.1085 | 122.0856 | 122.0352 | 113.6078 | 113.5803 | 122.0261 | 122.1497 | 120.0348 | 113.6078 | 113.5803 | 122.1497 | 122.0352 | 122.0261 | -8.4595 | -2.0233
729.6562 | 122.2641 | -110.9482 | 11.0367 | -0.010758 | -0.014785 | -0.017526 | 0.016676 | -0.0091495 | -0.0065838 | 0.0016427 | 2.7145 | 2.5635 | 2.655 | 11.2701 | 11.1557 | 11.2793 | 10.9131 | 11.2244 | 10.9726 | 9.0912 | 113.6032 | -8.4732 | 113.6627 | 122.2183 | 0.11902 | 120.0394 | -0.064087 | 0.05951 | 121.8613 | 122.1725 | 122.1039 | 113.5117 | 113.6627 | 121.9208 | 122.2275 | 120.0394 | 113.5117 | 113.6627 | 122.2275 | 122.1039 | 121.9208 | -8.3817 | -1.9455
730.6719 | 122.1863 | -110.9116 | 11.1053 | -0.010758 | -0.010085 | -0.017526 | 0.019453 | -0.010645 | -0.0074384 | -6.6324e-05 | 2.6779 | 2.5406 | 2.6276 | 11.2885 | 11.1694 | 11.2976 | 11.0413 | 11.2427 | 11.0413 | 9.0958 | 113.5391 | -8.5648 | 113.5895 | 122.2 | 0.064087 | 120.0073 | -0.064087 | 0.050354 | 121.9528 | 122.1542 | 122.081 | 113.4521 | 113.5895 | 121.9528 | 122.2092 | 120.0073 | 113.4521 | 113.5895 | 122.2092 | 122.081 | 121.9528 | -8.4778 | -2.0096
731.6719 | 122.1405 | -111.676 | 10.3638 | 0.0045015 | -0.010726 | -0.01603 | 0.021802 | -0.011286 | -0.0074384 | -0.00027992 | 2.3895 | 2.3941 | 2.3987 | 10.4507 | 10.3592 | 10.4691 | 10.4004 | 10.4141 | 10.3363 | 9.0179 | 114.0747 | -7.9697 | 114.0656 | 122.1268 | -0.004578 | 120.694 | -0.027466 | -0.009156 | 122.0764 | 122.0901 | 122.0352 | 114.0701 | 114.0656 | 122.0123 | 122.1451 | 120.694 | 114.0701 | 114.0656 | 122.1451 | 122.0352 | 122.0123 | -7.9651 | -1.3458
732.6719 | 122.1359 | -111.319 | 10.7574 | -0.003128 | -0.01094 | -0.018807 | 0.019025 | -0.0091495 | -0.0048748 | 0.0029245 | 2.504 | 2.4765 | 2.4948 | 10.8307 | 10.7208 | 10.8261 | 10.7346 | 10.7666 | 10.6796 | 9.0591 | 113.8138 | -8.2809 | 113.8229 | 122.1497 | -0.036621 | 120.3781 | -0.07782 | 0.009155 | 122.0535 | 122.0856 | 122.0398 | 113.7955 | 113.8229 | 121.9986 | 122.1451 | 120.3781 | 113.7955 | 113.8229 | 122.1451 | 122.0398 | 121.9986 | -8.2626 | -1.6983
733.6719 | 122.1405 | -112.2391 | 9.8328 | -0.010758 | -0.0096579 | -0.01838 | 0.017744 | -0.010004 | -0.0033794 | 0.0014291 | 2.2522 | 2.1835 | 2.2385 | 9.9197 | 9.8007 | 9.9197 | 9.8282 | 9.8831 | 9.7687 | 8.8898 | 114.4775 | -7.6492 | 114.4913 | 122.1588 | -0.032044 | 121.1288 | -0.064087 | 0.013733 | 122.0673 | 122.1222 | 122.0398 | 114.4226 | 114.4913 | 122.0078 | 122.1588 | 121.1288 | 114.4226 | 114.4913 | 122.1588 | 122.0398 | 122.0078 | -7.5943 | -0.94299
734.6562 | 122.1313 | -113.3148 | 8.7708 | 0.0045015 | -0.010085 | -0.017526 | 0.020948 | -0.0087223 | -0.007652 | 0.0024973 | 1.68 | 1.4328 | 1.4557 | 8.7616 | 8.7112 | 8.8531 | 8.7982 | 8.7708 | 8.7158 | 8.4 | 114.7705 | -7.338 | 114.9948 | 122.0764 | -0.059509 | 121.7148 | -0.054932 | 0.2243 | 122.113 | 122.0856 | 122.0261 | 114.7476 | 114.9948 | 122.0306 | 122.168 | 121.7148 | 114.7476 | 114.9948 | 122.168 | 122.0261 | 122.0306 | -7.3151 | -0.37079
735.6562 | 122.1222 | -111.4471 | 10.6339 | -0.003128 | -0.011794 | -0.020089 | 0.019666 | -0.0080813 | -0.0080792 | 0.00036108 | 2.417 | 2.4536 | 2.449 | 10.7071 | 10.6018 | 10.7117 | 10.643 | 10.643 | 10.5881 | 9.0408 | 113.8962 | -8.1802 | 113.8641 | 122.1542 | -0.032043 | 120.488 | -0.045776 | -0.032044 | 122.0901 | 122.0901 | 122.049 | 113.9008 | 113.8641 | 122.0352 | 122.1588 | 120.488 | 113.9008 | 113.8641 | 122.1588 | 122.049 | 122.0352 | -8.1848 | -1.593
736.6719 | 122.1954 | -111.6806 | 10.3546 | -0.010758 | -0.010512 | -0.019021 | 0.018812 | -0.0089359 | -0.0082928 | -0.0015615 | 2.4353 | 2.3529 | 2.4216 | 10.5194 | 10.4141 | 10.5103 | 10.3088 | 10.4507 | 10.3226 | 9.0179 | 114.1022 | -8.0017 | 114.1159 | 122.2 | 0.05951 | 120.6985 | -0.032043 | 0.013733 | 121.9894 | 122.1313 | 122.0947 | 114.0335 | 114.1159 | 122.0032 | 122.1909 | 120.6985 | 114.0335 | 114.1159 | 122.1909 | 122.0947 | 122.0032 | -7.933 | -1.3367
737.6719 | 122.1359 | -112.381 | 9.6771 | -0.003128 | -0.0092307 | -0.017526 | 0.017957 | -0.0087223 | -0.0046612 | -6.6324e-05 | 2.2339 | 2.2385 | 2.2293 | 9.7366 | 9.6451 | 9.7595 | 9.6954 | 9.7 | 9.6451 | 8.844 | 114.6103 | -7.4387 | 114.6149 | 122.1176 | -0.032043 | 121.225 | -0.032043 | 0.004578 | 122.0764 | 122.081 | 122.0261 | 114.6194 | 114.6149 | 122.0261 | 122.1405 | 121.225 | 114.6194 | 114.6149 | 122.1405 | 122.0261 | 122.0261 | -7.4478 | -0.83313
738.6719 | 122.1542 | -112.4588 | 9.6176 | -0.010758 | -0.0090171 | -0.019235 | 0.018812 | -0.0080813 | -0.0061566 | -0.0013479 | 2.1973 | 2.2202 | 2.2064 | 9.6817 | 9.581 | 9.7 | 9.6542 | 9.6313 | 9.5993 | 8.8211 | 114.6652 | -7.3975 | 114.6561 | 122.1405 | -0.036621 | 121.2799 | -0.018311 | -0.009155 | 122.113 | 122.0901 | 122.0398 | 114.679 | 114.6561 | 122.0581 | 122.1588 | 121.2799 | 114.679 | 114.6561 | 122.1588 | 122.0398 | 122.0581 | -7.4112 | -0.79651
739.6719 | 122.1405 | -115.8234 | 6.2576 | 0.0045015 | -0.0073081 | -0.017526 | 0.020307 | -0.0087223 | -0.0050884 | 0.0020701 | 1.3641 | 1.3824 | 1.387 | 6.2759 | 6.189 | 6.2897 | 6.2485 | 6.2439 | 6.221 | 6.102 | 117.2104 | -4.8752 | 117.1875 | 122.0993 | -0.068664 | 121.9254 | -0.036621 | -0.022888 | 122.0718 | 122.0673 | 122.0123 | 117.2058 | 117.1875 | 122.0444 | 122.113 | 121.9254 | 117.2058 | 117.1875 | 122.113 | 122.0123 | 122.0444 | -4.8706 | -0.15564
740.6719 | 122.1268 | -115.8188 | 6.2439 | -0.018387 | -0.0077353 | -0.012826 | 0.017957 | -0.0080813 | -0.0048748 | 0.0010019 | 1.3779 | 1.3916 | 1.3687 | 6.2805 | 6.1798 | 6.2897 | 6.2714 | 6.2531 | 6.2256 | 6.1066 | 117.1875 | -4.8523 | 117.1967 | 122.0993 | -0.064086 | 121.9254 | -0.01831 | 0.009156 | 122.0901 | 122.0718 | 121.9986 | 117.2104 | 117.1967 | 122.0444 | 122.1085 | 121.9254 | 117.2104 | 117.1967 | 122.1085 | 121.9986 | 122.0444 | -4.8752 | -0.13733
741.6719 | 122.1268 | -115.9927 | 6.0516 | -0.003128 | -0.0094443 | -0.018807 | 0.019239 | -0.0089359 | -0.0082928 | -0.00027992 | 1.3046 | 1.3458 | 1.3229 | 6.1111 | 6.0242 | 6.102 | 6.0745 | 6.0562 | 6.0379 | 5.9143 | 117.3157 | -4.7058 | 117.2974 | 122.1039 | -0.027466 | 121.907 | -0.013733 | -0.018311 | 122.0673 | 122.049 | 122.0169 | 117.3386 | 117.2974 | 122.0306 | 122.0947 | 121.907 | 117.3386 | 117.2974 | 122.0947 | 122.0169 | 122.0306 | -4.7287 | -0.13733
742.6719 | 122.1313 | -116.0202 | 6.0471 | 0.0045015 | -0.0090171 | -0.015603 | 0.019666 | -0.0067995 | -0.0048748 | 0.0014291 | 1.2909 | 1.3184 | 1.3229 | 6.0654 | 5.983 | 6.0791 | 6.0516 | 6.0287 | 6.0013 | 5.9006 | 117.3431 | -4.7287 | 117.3111 | 122.0856 | -0.064087 | 121.9208 | -0.045776 | -0.032043 | 122.0718 | 122.049 | 122.0032 | 117.3386 | 117.3111 | 122.0215 | 122.0993 | 121.9208 | 117.3386 | 117.3111 | 122.0993 | 122.0032 | 122.0215 | -4.7241 | -0.14648
743.6719 | 122.1634 | -115.892 | 6.189 | 0.0045015 | -0.0096579 | -0.015176 | 0.018812 | -0.0076541 | -0.0074384 | -6.6324e-05 | 1.3641 | 1.3046 | 1.3504 | 6.2485 | 6.1569 | 6.2485 | 6.1478 | 6.221 | 6.1295 | 6.0471 | 117.2424 | -4.8843 | 117.2562 | 122.1405 | -0.032044 | 121.9391 | -0.059509 | 0.013733 | 122.0398 | 122.113 | 122.0489 | 117.1967 | 117.2562 | 122.0215 | 122.1405 | 121.9391 | 117.1967 | 117.2562 | 122.1405 | 122.0489 | 122.0215 | -4.8386 | -0.14191
744.6719 | 122.1313 | -115.5487 | 6.5506 | -0.010758 | -0.0081625 | -0.016885 | 0.020734 | -0.010218 | -0.0080792 | 0.0010019 | 1.4053 | 1.4236 | 1.4374 | 6.5689 | 6.4636 | 6.5735 | 6.5369 | 6.5231 | 6.5002 | 6.3538 | 116.9861 | -5.127 | 116.954 | 122.1176 | -0.086975 | 121.9025 | -0.050354 | -0.032044 | 122.0856 | 122.0718 | 122.0123 | 116.9724 | 116.954 | 122.0489 | 122.1222 | 121.9025 | 116.9724 | 116.954 | 122.1222 | 122.0123 | 122.0489 | -5.1132 | -0.19684
745.6719 | 122.1725 | -115.1871 | 6.8985 | 0.0045015 | -0.0060263 | -0.017526 | 0.021162 | -0.0085085 | -0.0050884 | 0.0020701 | 1.4923 | 1.506 | 1.4832 | 6.9443 | 6.8481 | 6.9534 | 6.8802 | 6.8939 | 6.8481 | 6.7245 | 116.6702 | -5.3925 | 116.6794 | 122.1313 | -0.050354 | 121.9116 | -0.050354 | 0.009156 | 122.0673 | 122.081 | 122.0352 | 116.6931 | 116.6794 | 122.0352 | 122.1405 | 121.9116 | 116.6931 | 116.6794 | 122.1405 | 122.0352 | 122.0352 | -5.4153 | -0.17395
746.6719 | 122.1771 | -115.3336 | 6.7337 | -0.003128 | -0.010085 | -0.016671 | 0.020734 | -0.0091495 | -0.007011 | 0.0024973 | 1.4328 | 1.4328 | 1.4374 | 6.7841 | 6.7017 | 6.7749 | 6.7291 | 6.752 | 6.7017 | 6.5735 | 116.7709 | -5.3009 | 116.7664 | 122.1176 | -0.032044 | 121.907 | -0.032044 | -0.004578 | 122.0627 | 122.0856 | 122.0352 | 116.7664 | 116.7664 | 122.0352 | 122.1085 | 121.907 | 116.7664 | 116.7664 | 122.1085 | 122.0352 | 122.0352 | -5.2963 | -0.16022
747.6719 | 122.1725 | -115.3564 | 6.7383 | -0.003128 | -0.0062399 | -0.016885 | 0.018812 | -0.0070133 | -0.0057294 | -0.00049352 | 1.4236 | 1.4191 | 1.4145 | 6.7612 | 6.6696 | 6.7703 | 6.72 | 6.7383 | 6.6971 | 6.5552 | 116.7709 | -5.3192 | 116.7801 | 122.1176 | -0.068664 | 121.9116 | -0.041198 | 0.009155 | 122.0764 | 122.0947 | 122.0261 | 116.7755 | 116.7801 | 122.0535 | 122.1268 | 121.9116 | 116.7755 | 116.7801 | 122.1268 | 122.0261 | 122.0535 | -5.3238 | -0.1831
748.6719 | 122.1588 | -115.3152 | 6.752 | -0.003128 | -0.0079489 | -0.019021 | 0.021589 | -0.0074405 | -0.0055156 | -0.00092072 | 1.4053 | 1.4053 | 1.4053 | 6.7886 | 6.7245 | 6.8161 | 6.7612 | 6.7795 | 6.7337 | 6.601 | 116.7206 | -5.3467 | 116.7206 | 122.1039 | -0.027466 | 121.9162 | -0.01831 | 0 | 122.0764 | 122.0947 | 122.0398 | 116.7206 | 116.7206 | 122.049 | 122.1313 | 121.9162 | 116.7206 | 116.7206 | 122.1313 | 122.0398 | 122.049 | -5.3467 | -0.15106
749.6719 | 122.1725 | -115.2969 | 6.8253 | -0.010758 | -0.010085 | -0.012185 | 0.019453 | -0.0097903 | -0.0065838 | 0.0014291 | 1.4465 | 1.474 | 1.4511 | 6.8527 | 6.752 | 6.8665 | 6.8115 | 6.8161 | 6.7795 | 6.6238 | 116.748 | -5.3513 | 116.7435 | 122.1497 | -0.073242 | 121.9208 | -0.045776 | -0.004578 | 122.1085 | 122.113 | 122.049 | 116.7709 | 116.7435 | 122.0764 | 122.1634 | 121.9208 | 116.7709 | 116.7435 | 122.1634 | 122.049 | 122.0764 | -5.3741 | -0.20142
750.6719 | 122.1634 | -115.274 | 6.7841 | -0.018387 | -0.0098715 | -0.010476 | 0.018171 | -0.0080813 | -0.0040204 | 0.0010019 | 1.4328 | 1.4511 | 1.4511 | 6.8436 | 6.7474 | 6.8573 | 6.7886 | 6.8024 | 6.7657 | 6.633 | 116.7252 | -5.3329 | 116.7068 | 122.1176 | -0.036621 | 121.907 | -0.018311 | -0.018311 | 122.0627 | 122.0764 | 122.0215 | 116.7252 | 116.7068 | 122.0398 | 122.1313 | 121.907 | 116.7252 | 116.7068 | 122.1313 | 122.0215 | 122.0398 | -5.3329 | -0.15106
751.6719 | 122.168 | -115.2466 | 6.8298 | -0.010758 | -0.0055991 | -0.013467 | 0.021162 | -0.0076541 | -0.0061566 | 0.0018565 | 1.4694 | 1.4786 | 1.4694 | 6.8893 | 6.7886 | 6.8939 | 6.8253 | 6.8436 | 6.7978 | 6.6605 | 116.716 | -5.3513 | 116.716 | 122.1359 | -0.041199 | 121.907 | -0.032043 | 0 | 122.0718 | 122.0901 | 122.0352 | 116.7252 | 116.716 | 122.0444 | 122.1405 | 121.907 | 116.7252 | 116.716 | 122.1405 | 122.0352 | 122.0444 | -5.3604 | -0.16937
752.6719 | 122.2 | -115.0589 | 6.9809 | -0.003128 | -0.0062399 | -0.015603 | 0.021802 | -0.0065859 | -0.0072246 | 0.00036108 | 1.506 | 1.4694 | 1.4648 | 7.077 | 6.9809 | 7.0862 | 6.9305 | 7.0404 | 6.9443 | 6.8207 | 116.5237 | -5.5115 | 116.5649 | 122.1359 | 0 | 121.8796 | -0.036621 | 0.041198 | 121.9894 | 122.0993 | 122.0398 | 116.5283 | 116.5649 | 122.0032 | 122.1451 | 121.8796 | 116.5283 | 116.5649 | 122.1451 | 122.0398 | 122.0032 | -5.5161 | -0.16022
753.6719 | 122.2 | -114.9536 | 7.0862 | -0.018387 | -0.0058127 | -0.013894 | 0.022016 | -0.0063723 | -0.0057294 | -0.0017751 | 1.5427 | 1.506 | 1.4969 | 7.1686 | 7.0679 | 7.1869 | 7.0175 | 7.132 | 7.0358 | 6.8985 | 116.4505 | -5.5801 | 116.4963 | 122.1222 | -0.018311 | 121.8521 | -0.050354 | 0.045777 | 121.9711 | 122.0856 | 122.0215 | 116.4597 | 116.4963 | 121.9894 | 122.1405 | 121.8521 | 116.4597 | 116.4963 | 122.1405 | 122.0215 | 121.9894 | -5.5893 | -0.18768
754.6719 | 122.2 | -115.0085 | 7.0221 | -0.010758 | -0.0058127 | -0.015389 | 0.020093 | -0.0055179 | -0.0065838 | 0.0022837 | 1.5472 | 1.4923 | 1.5244 | 7.0862 | 6.9946 | 7.1091 | 6.9443 | 7.0679 | 6.9946 | 6.8527 | 116.5329 | -5.5298 | 116.5558 | 122.0947 | -0.027466 | 121.8613 | -0.027466 | 0.022888 | 121.9528 | 122.0764 | 122.0032 | 116.5009 | 116.5558 | 122.0032 | 122.1176 | 121.8613 | 116.5009 | 116.5558 | 122.1176 | 122.0032 | 122.0032 | -5.4977 | -0.16937
755.6719 | 122.2 | -115.1779 | 6.8436 | -0.010758 | -0.0053855 | -0.015603 | 0.021162 | -0.0050907 | -0.0044476 | 0.0010019 | 1.474 | 1.4145 | 1.4557 | 6.9489 | 6.8481 | 6.9672 | 6.7703 | 6.9122 | 6.8069 | 6.6879 | 116.6336 | -5.4291 | 116.6519 | 122.1268 | 0.004578 | 121.8658 | -0.036621 | 0.018311 | 121.9482 | 122.0901 | 122.0261 | 116.5924 | 116.6519 | 121.9849 | 122.1451 | 121.8658 | 116.5924 | 116.6519 | 122.1451 | 122.0261 | 121.9849 | -5.3879 | -0.15564
756.6719 | 122.1909 | -111.8362 | 10.2264 | -0.003128 | -0.0062399 | -0.01838 | 0.017103 | -0.0067995 | -0.0048748 | 0.0031381 | 2.2934 | 2.2705 | 2.2659 | 10.35 | 10.2493 | 10.3638 | 10.2173 | 10.2951 | 10.2356 | 8.9767 | 114.1022 | -7.9559 | 114.1296 | 122.1863 | 0.022889 | 120.813 | 0.009156 | 0.027466 | 122.0535 | 122.1313 | 122.0856 | 114.1068 | 114.1296 | 122.0718 | 122.2 | 120.813 | 114.1068 | 114.1296 | 122.2 | 122.0856 | 122.0718 | -7.9605 | -1.2497
757.6562 | 122.1497 | -111.9781 | 10.1028 | -0.010758 | -0.0085899 | -0.020303 | 0.013044 | -0.0072269 | -0.0061566 | 0.0012155 | 2.1927 | 2.211 | 2.2247 | 10.1624 | 10.0662 | 10.1944 | 10.1212 | 10.112 | 10.0662 | 8.9539 | 114.2029 | -7.8918 | 114.1708 | 122.1405 | -0.036621 | 120.932 | -0.036621 | -0.032043 | 122.0993 | 122.0901 | 122.0444 | 114.1891 | 114.1708 | 122.0444 | 122.1725 | 120.932 | 114.1891 | 114.1708 | 122.1725 | 122.0444 | 122.0444 | -7.8781 | -1.149
758.6719 | 122.1588 | -112.4268 | 9.6588 | 0.0045015 | -0.0075217 | -0.017953 | 0.017957 | -0.0076541 | -0.0065838 | 0.0024973 | 2.0874 | 2.1194 | 2.1149 | 9.7 | 9.613 | 9.7275 | 9.6863 | 9.6634 | 9.6176 | 8.8257 | 114.5416 | -7.5394 | 114.5142 | 122.1268 | -0.045776 | 121.2524 | -0.041198 | -0.027466 | 122.113 | 122.0901 | 122.0398 | 114.5462 | 114.5142 | 122.0444 | 122.1542 | 121.2524 | 114.5462 | 114.5142 | 122.1542 | 122.0398 | 122.0444 | -7.5439 | -0.83313
759.6719 | 122.1909 | -111.9873 | 10.08 | -0.003128 | -0.0055991 | -0.014962 | 0.019453 | -0.0078677 | -0.0072246 | 0.0016427 | 2.1927 | 2.1973 | 2.2018 | 10.1807 | 10.0662 | 10.1852 | 10.0983 | 10.1212 | 10.0616 | 8.9447 | 114.1891 | -7.8827 | 114.18 | 122.168 | -0.013733 | 120.932 | -0.01831 | -0.009155 | 122.0856 | 122.1085 | 122.0535 | 114.1846 | 114.18 | 122.049 | 122.1725 | 120.932 | 114.1846 | 114.18 | 122.1725 | 122.0535 | 122.049 | -7.8781 | -1.1353
760.6719 | 122.1863 | -112.2849 | 9.7778 | -0.010758 | -0.0094443 | -0.014321 | 0.019239 | -0.0067995 | -0.0061566 | 0.00036108 | 2.1149 | 2.1286 | 2.1103 | 9.8694 | 9.7641 | 9.874 | 9.7916 | 9.8053 | 9.7412 | 8.8669 | 114.3951 | -7.6492 | 114.3997 | 122.1542 | -0.013733 | 121.1517 | -0.036621 | 0.004577 | 122.0764 | 122.0901 | 122.049 | 114.4135 | 114.3997 | 122.0261 | 122.1588 | 121.1517 | 114.4135 | 114.3997 | 122.1588 | 122.049 | 122.0261 | -7.6675 | -0.91095
761.6562 | 122.2046 | -112.6419 | 9.4208 | -0.003128 | -0.0077353 | -0.015603 | 0.020948 | -0.0070133 | -0.005302 | -6.6324e-05 | 2.0462 | 2.0004 | 2.0096 | 9.5489 | 9.4482 | 9.5535 | 9.3613 | 9.5078 | 9.3842 | 8.7387 | 114.6515 | -7.4203 | 114.6881 | 122.1909 | 0.027466 | 121.3806 | -0.036621 | 0.036621 | 122.0032 | 122.1497 | 122.0901 | 114.6423 | 114.6881 | 122.0261 | 122.1954 | 121.3806 | 114.6423 | 114.6881 | 122.1954 | 122.0901 | 122.0261 | -7.4112 | -0.68207
762.6562 | 122.2183 | -112.7792 | 9.2514 | -0.003128 | -0.0096579 | -0.016885 | 0.019666 | -0.0057315 | -0.0061566 | 0.0012155 | 2.0187 | 1.9638 | 1.9867 | 9.375 | 9.2697 | 9.3979 | 9.1965 | 9.3292 | 9.2422 | 8.67 | 114.7659 | -7.2876 | 114.798 | 122.1542 | 0.01831 | 121.4493 | -0.009155 | 0.032044 | 121.9757 | 122.1085 | 122.0489 | 114.743 | 114.798 | 122.0215 | 122.1771 | 121.4493 | 114.743 | 114.798 | 122.1771 | 122.0489 | 122.0215 | -7.2647 | -0.58136
763.6562 | 122.2321 | -112.4725 | 9.6039 | 0.0045015 | -0.0060263 | -0.013467 | 0.020734 | -0.0055179 | -0.0061566 | 0.0010019 | 2.0737 | 2.0325 | 2.0599 | 9.7412 | 9.613 | 9.7458 | 9.5764 | 9.6817 | 9.5718 | 8.812 | 114.5325 | -7.5714 | 114.5462 | 122.2137 | 0.009155 | 121.2845 | -0.032044 | 0.013732 | 122.0489 | 122.1542 | 122.0856 | 114.505 | 114.5462 | 122.0444 | 122.2183 | 121.2845 | 114.505 | 114.5462 | 122.2183 | 122.0856 | 122.0444 | -7.5439 | -0.79193
764.6719 | 122.1725 | -112.6465 | 9.4254 | -0.003128 | -0.0083763 | -0.016244 | 0.01753 | -0.0091495 | -0.005302 | 0.0022837 | 1.9684 | 1.9775 | 1.9684 | 9.4803 | 9.3842 | 9.5123 | 9.4666 | 9.4299 | 9.407 | 8.7387 | 114.6149 | -7.4478 | 114.6149 | 122.1268 | -0.041199 | 121.3852 | -0.018311 | 0 | 122.113 | 122.0764 | 122.0306 | 114.624 | 114.6149 | 122.0535 | 122.1588 | 121.3852 | 114.624 | 114.6149 | 122.1588 | 122.0306 | 122.0535 | -7.457 | -0.68665
765.6719 | 122.1634 | -112.3718 | 9.7458 | -0.010758 | -0.0079489 | -0.02073 | 0.017316 | -0.0072269 | -0.0044476 | -0.00092072 | 2.0828 | 2.1103 | 2.1103 | 9.7733 | 9.7092 | 9.8145 | 9.787 | 9.7549 | 9.7183 | 8.8623 | 114.4821 | -7.6355 | 114.4547 | 122.1451 | -0.036622 | 121.2341 | -0.027466 | -0.027466 | 122.1588 | 122.1268 | 122.081 | 114.4821 | 114.4547 | 122.0901 | 122.1863 | 121.2341 | 114.4821 | 114.4547 | 122.1863 | 122.081 | 122.0901 | -7.6355 | -0.88348
766.6719 | 122.1909 | -111.8088 | 10.2859 | -0.003128 | -0.010512 | -0.017953 | 0.014753 | -0.0053043 | -0.005943 | 0.00036108 | 2.2018 | 2.2522 | 2.2522 | 10.3729 | 10.2539 | 10.3912 | 10.3134 | 10.318 | 10.2859 | 8.9951 | 114.061 | -8.0338 | 114.0106 | 122.1817 | -0.032044 | 120.8038 | 0 | -0.050354 | 122.1222 | 122.1268 | 122.0627 | 114.061 | 114.0106 | 122.0947 | 122.2 | 120.8038 | 114.061 | 114.0106 | 122.2 | 122.0627 | 122.0947 | -8.0338 | -1.2909
767.6719 | 122.1817 | -110.9848 | 11.1053 | 0.0045015 | -0.0073081 | -0.01838 | 0.019025 | -0.0067995 | -0.0057294 | 0.00078828 | 2.3941 | 2.4216 | 2.4078 | 11.1832 | 11.0733 | 11.2015 | 11.1603 | 11.1374 | 11.1053 | 9.0866 | 113.3926 | -8.6838 | 113.3789 | 122.168 | -0.032044 | 120.0714 | 0 | -0.013733 | 122.1451 | 122.1222 | 122.0581 | 113.4064 | 113.3789 | 122.0901 | 122.1863 | 120.0714 | 113.4064 | 113.3789 | 122.1863 | 122.0581 | 122.0901 | -8.6975 | -2.0187
768.6562 | 122.2229 | -110.376 | 11.6867 | -0.010758 | -0.0085899 | -0.018594 | 0.021375 | -0.0046633 | -0.0089336 | 0.00014748 | 2.5864 | 2.5635 | 2.5497 | 11.8149 | 11.7096 | 11.8515 | 11.6776 | 11.7737 | 11.6821 | 9.1187 | 112.9257 | -9.1232 | 112.9623 | 122.1909 | 0.022888 | 119.4946 | -0.004578 | 0.036621 | 122.0535 | 122.1497 | 122.0856 | 112.9395 | 112.9623 | 122.0581 | 122.2275 | 119.4946 | 112.9395 | 112.9623 | 122.2275 | 122.0856 | 122.0581 | -9.137 | -2.5681
769.7188 | 122.2961 | -111.9965 | 10.0159 | -0.003128 | -0.01158 | -0.024789 | 0.011976 | -0.0085085 | -0.0050884 | 0.0029245 | 2.1423 | 2.0966 | 2.1378 | 10.1578 | 10.0662 | 10.2219 | 9.9197 | 10.1486 | 9.9701 | 8.9493 | 114.1342 | -7.9193 | 114.1388 | 122.1542 | 0.050354 | 120.9457 | -0.045776 | 0.004578 | 121.9162 | 122.1451 | 122.0627 | 114.093 | 114.1388 | 121.9666 | 122.2183 | 120.9457 | 114.093 | 114.1388 | 122.2183 | 122.0627 | 121.9666 | -7.8781 | -1.0666
770.6562 | 122.2183 | -115.0497 | 7.0358 | -0.003128 | -0.0094443 | -0.015176 | 0.019453 | -0.0091495 | -0.0048748 | 0.0022837 | 1.4557 | 1.4694 | 1.4648 | 7.0953 | 6.9855 | 7.0999 | 7.0129 | 7.0541 | 6.9946 | 6.8573 | 116.5146 | -5.5664 | 116.5054 | 122.1451 | -0.050354 | 121.907 | -0.041199 | -0.009156 | 122.0627 | 122.1039 | 122.0352 | 116.5192 | 116.5054 | 122.0444 | 122.1497 | 121.907 | 116.5192 | 116.5054 | 122.1497 | 122.0352 | 122.0444 | -5.571 | -0.17853
771.6719 | 122.1909 | -113.6032 | 8.5052 | -0.010758 | -0.011794 | -0.018594 | 0.017103 | -0.010218 | -0.005943 | 0.0024973 | 1.8036 | 1.767 | 1.8036 | 8.5693 | 8.4732 | 8.5693 | 8.4961 | 8.5281 | 8.4549 | 8.1619 | 115.4068 | -6.7383 | 115.4068 | 122.1725 | -0.032043 | 121.7651 | -0.050354 | 0 | 122.0993 | 122.1313 | 122.0764 | 115.3702 | 115.4068 | 122.0581 | 122.1725 | 121.7651 | 115.3702 | 115.4068 | 122.1725 | 122.0764 | 122.0581 | -6.7017 | -0.34332
772.6719 | 122.1954 | -112.5641 | 9.4757 | -0.003128 | -0.0098715 | -0.019235 | 0.01753 | -0.010431 | -0.0072246 | 0.00078828 | 2.1011 | 2.0828 | 2.1057 | 9.787 | 9.5856 | 9.613 | 9.462 | 9.5261 | 9.5398 | 8.8669 | 114.6698 | -7.3929 | 114.6652 | 122.3511 | 0.10986 | 121.431 | 0.064087 | -0.004578 | 122.0261 | 122.0901 | 122.1497 | 114.6469 | 114.6652 | 122.1039 | 122.1771 | 121.431 | 114.6469 | 114.6652 | 122.1771 | 122.1497 | 122.1039 | -7.37 | -0.60883
773.6719 | 122.1725 | -116.4459 | 5.6259 | -0.018387 | -0.010512 | -0.01838 | 0.01988 | -0.010218 | -0.0065838 | 0.00057468 | 1.1032 | 1.1307 | 1.1444 | 5.6717 | 5.5801 | 5.6763 | 5.6442 | 5.658 | 5.6259 | 5.5161 | 117.5903 | -4.4952 | 117.5491 | 122.1176 | -0.045777 | 121.962 | 0 | -0.041199 | 122.0901 | 122.1039 | 122.0261 | 117.5766 | 117.5491 | 122.0718 | 122.1222 | 121.962 | 117.5766 | 117.5491 | 122.1222 | 122.0261 | 122.0718 | -4.4815 | -0.10986
774.6719 | 122.1771 | -116.2994 | 5.8456 | -0.010758 | -0.010512 | -0.018807 | 0.01988 | -0.0082949 | -0.0065838 | 0.0010019 | 1.1581 | 1.1719 | 1.1673 | 5.8777 | 5.7907 | 5.8914 | 5.8456 | 5.864 | 5.8319 | 5.7083 | 117.4667 | -4.6738 | 117.4576 | 122.1771 | -0.054932 | 122.0078 | -0.013733 | -0.009155 | 122.1451 | 122.1634 | 122.0901 | 117.4713 | 117.4576 | 122.1313 | 122.1909 | 122.0078 | 117.4713 | 117.4576 | 122.1909 | 122.0901 | 122.1313 | -4.6783 | -0.13733
775.6562 | 122.2092 | -116.0706 | 6.0608 | -0.010758 | -0.0094443 | -0.01368 | 0.021802 | -0.0074405 | -0.009361 | 0.00057468 | 1.2085 | 1.2131 | 1.2222 | 6.0791 | 5.983 | 6.0883 | 6.015 | 6.0471 | 6.0059 | 5.9006 | 117.2928 | -4.8477 | 117.2791 | 122.1497 | -0.07782 | 121.9711 | -0.054932 | -0.013733 | 122.0856 | 122.1176 | 122.0535 | 117.2836 | 117.2791 | 122.0764 | 122.1588 | 121.9711 | 117.2836 | 117.2791 | 122.1588 | 122.0535 | 122.0764 | -4.8386 | -0.16022
776.6562 | 122.2 | -115.6036 | 6.5369 | 0.0045015 | -0.0098715 | -0.016458 | 0.019453 | -0.0089359 | -0.0072246 | 0.00078828 | 1.2863 | 1.3092 | 1.3184 | 6.5826 | 6.4911 | 6.601 | 6.5369 | 6.5506 | 6.5094 | 6.3995 | 116.922 | -5.2277 | 116.89 | 122.1863 | -0.045776 | 122.0032 | -0.027466 | -0.032043 | 122.1405 | 122.1542 | 122.0947 | 116.9128 | 116.89 | 122.113 | 122.2046 | 122.0032 | 116.9128 | 116.89 | 122.2046 | 122.0947 | 122.113 | -5.2185 | -0.13733
777.6562 | 122.1909 | -115.9973 | 6.1295 | -0.010758 | -0.0077353 | -0.014962 | 0.020521 | -0.0080813 | -0.0067974 | 0.0014291 | 1.2085 | 1.2451 | 1.2543 | 6.1707 | 6.0837 | 6.1752 | 6.134 | 6.1295 | 6.1111 | 5.9967 | 117.2516 | -4.8843 | 117.2058 | 122.168 | -0.045777 | 121.994 | -0.018311 | -0.045776 | 122.1313 | 122.1268 | 122.081 | 117.2424 | 117.2058 | 122.1085 | 122.1725 | 121.994 | 117.2424 | 117.2058 | 122.1725 | 122.081 | 122.1085 | -4.8752 | -0.13275
778.6719 | 122.2275 | -115.0772 | 7.0175 | 0.0045015 | -0.01158 | -0.019876 | 0.017103 | -0.0074405 | -0.0067974 | 0.00078828 | 1.474 | 1.3916 | 1.4374 | 7.1182 | 7.0404 | 7.1411 | 6.9672 | 7.0953 | 6.9901 | 6.871 | 116.5146 | -5.6259 | 116.5512 | 122.1954 | 0.022888 | 121.9482 | -0.027466 | 0.036621 | 122.0444 | 122.1725 | 122.1176 | 116.4688 | 116.5512 | 122.0673 | 122.2183 | 121.9482 | 116.4688 | 116.5512 | 122.2183 | 122.1176 | 122.0673 | -5.5801 | -0.14648
779.6719 | 122.2549 | -113.6627 | 8.4595 | -0.003128 | -0.0098715 | -0.014962 | 0.01753 | -0.0095767 | -0.0063702 | 0.00036108 | 1.7807 | 1.7075 | 1.767 | 8.5831 | 8.4778 | 8.5876 | 8.3725 | 8.551 | 8.4091 | 8.1345 | 115.4297 | -6.752 | 115.4434 | 122.2458 | 0.01831 | 121.7972 | -0.050354 | 0.013733 | 122.0352 | 122.2137 | 122.1405 | 115.3702 | 115.4434 | 122.0718 | 122.2504 | 121.7972 | 115.3702 | 115.4434 | 122.2504 | 122.1405 | 122.0718 | -6.6925 | -0.32501
780.6719 | 122.1909 | -115.242 | 6.8848 | -0.003128 | -0.0088035 | -0.014749 | 0.019666 | -0.0089359 | -0.0057294 | -6.6324e-05 | 1.3641 | 1.355 | 1.3733 | 6.926 | 6.8253 | 6.9351 | 6.871 | 6.8939 | 6.839 | 6.7245 | 116.6153 | -5.5298 | 116.6061 | 122.168 | -0.05951 | 121.9666 | -0.045777 | -0.009155 | 122.113 | 122.1359 | 122.0673 | 116.597 | 116.6061 | 122.081 | 122.1771 | 121.9666 | 116.597 | 116.6061 | 122.1771 | 122.0673 | 122.081 | -5.5115 | -0.16022
781.6719 | 122.2046 | -115.004 | 7.1182 | -0.003128 | -0.0094443 | -0.01603 | 0.018171 | -0.010004 | -0.0061566 | 0.00057468 | 1.3733 | 1.3596 | 1.3962 | 7.196 | 7.0908 | 7.196 | 7.1182 | 7.1548 | 7.0862 | 6.958 | 116.4001 | -5.7587 | 116.3773 | 122.2 | -0.027466 | 121.962 | -0.032043 | -0.022888 | 122.1222 | 122.1588 | 122.0947 | 116.3635 | 116.3773 | 122.0901 | 122.2 | 121.962 | 116.3635 | 116.3773 | 122.2 | 122.0947 | 122.0901 | -5.722 | -0.16022
782.6562 | 122.2092 | -114.505 | 7.6172 | -0.003128 | -0.0083763 | -0.014535 | 0.018598 | -0.0087223 | -0.0072246 | 0.00057468 | 1.5106 | 1.506 | 1.5106 | 7.6996 | 7.576 | 7.6904 | 7.6309 | 7.6447 | 7.6126 | 7.4112 | 116.0156 | -6.1111 | 116.0156 | 122.2046 | -0.041198 | 121.9162 | -0.004577 | 0 | 122.1359 | 122.1497 | 122.081 | 116.011 | 116.0156 | 122.1176 | 122.1954 | 121.9162 | 116.011 | 116.0156 | 122.1954 | 122.081 | 122.1176 | -6.1066 | -0.20599
783.6562 | 122.1909 | -114.7247 | 7.3929 | -0.018387 | -0.010726 | -0.019235 | 0.019666 | -0.0070133 | -0.007011 | -0.00049352 | 1.4648 | 1.4832 | 1.506 | 7.457 | 7.3471 | 7.4661 | 7.402 | 7.4158 | 7.3883 | 7.2052 | 116.2308 | -5.9097 | 116.1896 | 122.1817 | -0.045776 | 121.9299 | -0.004577 | -0.041198 | 122.1268 | 122.1405 | 122.0718 | 116.2079 | 116.1896 | 122.113 | 122.1909 | 121.9299 | 116.2079 | 116.1896 | 122.1909 | 122.0718 | 122.113 | -5.8868 | -0.18768
784.6562 | 122.2137 | -113.6673 | 8.4686 | -0.003128 | -0.0088035 | -0.012826 | 0.018812 | -0.0082949 | -0.0072246 | 0.0022837 | 1.68 | 1.7075 | 1.6937 | 8.5327 | 8.4274 | 8.5464 | 8.4732 | 8.4686 | 8.4366 | 8.1299 | 115.361 | -6.7612 | 115.3473 | 122.2 | -0.041199 | 121.7972 | -0.032044 | -0.013733 | 122.1405 | 122.1359 | 122.0947 | 115.3748 | 115.3473 | 122.1039 | 122.2137 | 121.7972 | 115.3748 | 115.3473 | 122.2137 | 122.0947 | 122.1039 | -6.7749 | -0.33875
785.6719 | 122.2321 | -112.4313 | 9.6634 | -0.010758 | -0.0098715 | -0.01603 | 0.017103 | -0.0078677 | -0.005302 | 0.0027109 | 1.9775 | 1.8997 | 1.9592 | 9.7916 | 9.6725 | 9.8145 | 9.6542 | 9.7412 | 9.613 | 8.8394 | 114.3906 | -7.7637 | 114.4089 | 122.2229 | 0.009155 | 121.2708 | -0.050354 | 0.01831 | 122.0856 | 122.1725 | 122.1039 | 114.3311 | 114.4089 | 122.0444 | 122.2458 | 121.2708 | 114.3311 | 114.4089 | 122.2458 | 122.1039 | 122.0444 | -7.7042 | -0.82397
786.6719 | 122.2046 | -107.9361 | 14.2044 | -0.010758 | -0.0090171 | -0.019235 | 0.017744 | -0.0089359 | -0.0074384 | 0.00078828 | 2.9846 | 2.98 | 2.9846 | 14.3005 | 14.1815 | 14.3051 | 14.2502 | 14.241 | 14.1769 | 9.1324 | 110.9207 | -11.2244 | 110.9207 | 122.2366 | -0.022888 | 117.0685 | -0.027466 | 0 | 122.1863 | 122.1771 | 122.1176 | 110.9161 | 110.9207 | 122.113 | 122.2412 | 117.0685 | 110.9161 | 110.9207 | 122.2412 | 122.1176 | 122.113 | -11.2198 | -5.072
787.6719 | 122.1817 | -113.3972 | 8.6746 | -0.010758 | -0.0062399 | -0.014962 | 0.020093 | -0.0076541 | -0.007652 | 0.0016427 | 1.5793 | 1.6022 | 1.6205 | 8.7204 | 8.606 | 8.7067 | 8.6472 | 8.6334 | 8.6288 | 8.3221 | 115.0177 | -7.0724 | 114.9765 | 122.1176 | -0.068665 | 121.7194 | -0.045777 | -0.041198 | 122.0444 | 122.0306 | 122.0032 | 114.9994 | 114.9765 | 122.0261 | 122.1039 | 121.7194 | 114.9994 | 114.9765 | 122.1039 | 122.0032 | 122.0261 | -7.0541 | -0.35248
788.6719 | 122.2092 | -110.0327 | 12.0712 | 0.0045015 | -0.0070945 | -0.016458 | 0.017744 | -0.0095767 | -0.0065838 | 0.0010019 | 2.3941 | 2.4078 | 2.4033 | 12.1674 | 12.0529 | 12.1857 | 12.117 | 12.117 | 12.0575 | 9.1278 | 112.4359 | -9.6634 | 112.4268 | 122.2 | -0.018311 | 119.1605 | -0.013733 | -0.009155 | 122.1497 | 122.1497 | 122.0856 | 112.4405 | 112.4268 | 122.0901 | 122.2183 | 119.1605 | 112.4405 | 112.4268 | 122.2183 | 122.0856 | 122.0901 | -9.668 | -2.9434
789.6562 | 122.2549 | -110.5087 | 11.6226 | -0.010758 | -0.0070945 | -0.016244 | 0.020093 | -0.0065859 | -0.0048748 | 0.00078828 | 2.2476 | 2.2476 | 2.2385 | 11.7416 | 11.6226 | 11.7416 | 11.6318 | 11.6684 | 11.5997 | 9.1141 | 112.7472 | -9.375 | 112.7563 | 122.2504 | 0 | 119.6228 | -0.022889 | 0.009156 | 122.1405 | 122.1771 | 122.1313 | 112.7563 | 112.7563 | 122.1085 | 122.2504 | 119.6228 | 112.7563 | 112.7563 | 122.2504 | 122.1313 | 122.1085 | -9.3842 | -2.5085
790.6562 | 122.2549 | -110.5728 | 11.499 | -0.003128 | -0.0090171 | -0.017739 | 0.020093 | -0.0072269 | -0.0061566 | 0.0012155 | 2.2842 | 2.2888 | 2.2751 | 11.6272 | 11.5311 | 11.6455 | 11.5448 | 11.5631 | 11.499 | 9.1095 | 112.8479 | -9.2102 | 112.8571 | 122.2 | 0.032044 | 119.6823 | 0 | 0.009156 | 122.1176 | 122.1359 | 122.1039 | 112.8616 | 112.8571 | 122.0718 | 122.2183 | 119.6823 | 112.8616 | 112.8571 | 122.2183 | 122.1039 | 122.0718 | -9.2239 | -2.3895
791.6719 | 122.2092 | -110.1379 | 11.9614 | 0.0045015 | -0.0083763 | -0.019021 | 0.019453 | -0.0078677 | -0.0055156 | 0.0010019 | 2.3712 | 2.3987 | 2.417 | 12.0575 | 11.9385 | 12.0621 | 12.0117 | 12.0026 | 11.9568 | 9.1232 | 112.5549 | -9.5627 | 112.5092 | 122.1954 | -0.022888 | 119.2612 | -0.004578 | -0.045776 | 122.1497 | 122.1405 | 122.0764 | 112.5366 | 112.5092 | 122.0947 | 122.2 | 119.2612 | 112.5366 | 112.5092 | 122.2 | 122.0764 | 122.0947 | -9.5444 | -2.8381
792.6719 | 122.2229 | -111.0855 | 11.0046 | -0.010758 | -0.0064535 | -0.018167 | 0.019239 | -0.0065859 | -0.0044476 | 0.0020701 | 2.0874 | 2.0828 | 2.0828 | 11.0825 | 10.9589 | 11.1099 | 10.9451 | 10.9909 | 10.968 | 9.0775 | 113.1683 | -8.9218 | 113.1729 | 122.168 | -0.045777 | 120.163 | -0.036621 | 0.004577 | 122.0306 | 122.0764 | 122.0444 | 113.1683 | 113.1729 | 122.0535 | 122.1954 | 120.163 | 113.1683 | 113.1729 | 122.1954 | 122.0444 | 122.0535 | -8.9218 | -1.9272
793.6719 | 122.2092 | -109.6527 | 12.4283 | -0.010758 | -0.0090171 | -0.017312 | 0.016035 | -0.0091495 | -0.0061566 | 0.00057468 | 2.4536 | 2.4673 | 2.4582 | 12.5336 | 12.3962 | 12.5427 | 12.4924 | 12.4695 | 12.41 | 9.1415 | 112.1109 | -9.9609 | 112.1063 | 122.1863 | -0.032044 | 118.7943 | -0.018311 | -0.004578 | 122.1451 | 122.1222 | 122.049 | 112.1201 | 112.1063 | 122.0627 | 122.1954 | 118.7943 | 112.1201 | 112.1063 | 122.1954 | 122.049 | 122.0627 | -9.9701 | -3.2867
794.6719 | 122.2595 | -109.433 | 12.6526 | 0.0045015 | -0.0053855 | -0.014535 | 0.018598 | -0.0057315 | -0.0080792 | 0.0020701 | 2.5177 | 2.536 | 2.5131 | 12.7762 | 12.6572 | 12.8036 | 12.7029 | 12.7258 | 12.6389 | 9.1278 | 111.9461 | -10.1166 | 111.9507 | 122.2092 | 0.004578 | 118.5608 | -0.013733 | 0.004577 | 122.1359 | 122.1588 | 122.0901 | 111.969 | 111.9507 | 122.0718 | 122.2366 | 118.5608 | 111.969 | 111.9507 | 122.2366 | 122.0901 | 122.0718 | -10.1395 | -3.5248
795.6719 | 122.2458 | -112.0926 | 9.9838 | -0.010758 | -0.0058127 | -0.017312 | 0.018598 | -0.0078677 | -0.0050884 | 0.0020701 | 1.9363 | 1.9547 | 1.9318 | 10.0845 | 9.9792 | 10.1074 | 10.0067 | 10.025 | 9.9792 | 8.9264 | 114.0244 | -8.0292 | 114.0289 | 122.1771 | -0.004578 | 121.019 | -0.004578 | 0.004577 | 122.0993 | 122.1176 | 122.0718 | 114.0472 | 114.0289 | 122.0718 | 122.2 | 121.019 | 114.0472 | 114.0289 | 122.2 | 122.0718 | 122.0718 | -8.0521 | -1.0574
796.6719 | 122.2412 | -111.8958 | 10.2219 | -0.018387 | -0.0085899 | -0.012399 | 0.016889 | -0.010004 | -0.0074384 | -0.00049352 | 2.0325 | 2.0279 | 2.0142 | 10.2905 | 10.2539 | 10.35 | 10.2036 | 10.2127 | 10.1852 | 8.9447 | 113.9099 | -8.194 | 113.9282 | 122.1863 | 0.032043 | 120.8405 | -0.036621 | 0.018311 | 122.0993 | 122.1085 | 122.1497 | 113.9236 | 113.9282 | 122.081 | 122.2458 | 120.8405 | 113.9236 | 113.9282 | 122.2458 | 122.1497 | 122.081 | -8.2077 | -1.2772
797.6719 | 122.3465 | -107.0114 | 14.9918 | -0.010758 | -0.010512 | -0.018807 | 0.016248 | -0.0048769 | -0.0055156 | 0.0022837 | 3.0716 | 2.9709 | 3.0121 | 15.2206 | 15.1108 | 15.2756 | 14.8224 | 15.152 | 14.9323 | 9.1232 | 110.0235 | -12.0209 | 110.083 | 122.2321 | 0.11902 | 116.1346 | -0.059509 | 0.059509 | 121.8338 | 122.1634 | 122.1222 | 109.9823 | 110.083 | 121.9437 | 122.287 | 116.1346 | 109.9823 | 110.083 | 122.287 | 122.1222 | 121.9437 | -11.9797 | -5.8685
798.6719 | 122.2595 | -107.8125 | 14.2364 | -0.010758 | -0.0051719 | -0.014962 | 0.020734 | -0.0063723 | -0.0046612 | -6.6324e-05 | 2.8336 | 2.7695 | 2.774 | 14.4333 | 14.3051 | 14.447 | 14.2136 | 14.3326 | 14.2181 | 9.137 | 110.5865 | -11.467 | 110.6461 | 122.2458 | 0.068665 | 116.9495 | -0.01831 | 0.059509 | 122.0261 | 122.1451 | 122.1176 | 110.582 | 110.6461 | 122.0306 | 122.2595 | 116.9495 | 110.582 | 110.6461 | 122.2595 | 122.1176 | 122.0306 | -11.4624 | -5.0995
799.6719 | 122.2321 | -107.7026 | 14.3692 | -0.010758 | -0.0079489 | -0.017739 | 0.017316 | -0.0067995 | -0.0055156 | 0.0014291 | 2.948 | 2.9709 | 2.9663 | 14.4241 | 14.3143 | 14.4882 | 14.4241 | 14.4333 | 14.3463 | 9.1278 | 110.6689 | -11.3983 | 110.6506 | 122.1268 | -0.054932 | 116.8304 | -0.022889 | -0.018311 | 122.1268 | 122.1359 | 122.0169 | 110.6735 | 110.6506 | 122.0489 | 122.1909 | 116.8304 | 110.6735 | 110.6506 | 122.1909 | 122.0169 | 122.0489 | -11.4029 | -5.2414
800.6719 | 122.2549 | -111.8683 | 10.2036 | -0.003128 | -0.0077353 | -0.016885 | 0.018812 | -0.0085085 | -0.004234 | 0.0027109 | 1.8814 | 2.0416 | 2.0416 | 10.1532 | 10.0754 | 10.2036 | 10.1532 | 10.199 | 10.0571 | 8.9401 | 113.9099 | -8.1619 | 113.7497 | 122.0215 | -0.12817 | 120.8084 | -0.14648 | -0.16022 | 122.0215 | 122.0673 | 121.9437 | 113.9099 | 113.7497 | 121.9254 | 122.0718 | 120.8084 | 113.9099 | 113.7497 | 122.0718 | 121.9437 | 121.9254 | -8.1619 | -1.2634
801.6719 | 122.2733 | -113.237 | 8.8394 | -0.003128 | -0.0068809 | -0.017526 | 0.021589 | -0.0059451 | -0.0048748 | 0.0018565 | 1.6617 | 1.6067 | 1.6159 | 8.9584 | 8.844 | 8.9676 | 8.7753 | 8.9081 | 8.7936 | 8.4137 | 114.8529 | -7.2327 | 114.8987 | 122.1954 | 0.004577 | 121.6507 | -0.045777 | 0.045776 | 122.0123 | 122.1451 | 122.081 | 114.8438 | 114.8987 | 122.0306 | 122.2046 | 121.6507 | 114.8438 | 114.8987 | 122.2046 | 122.081 | 122.0306 | -7.2235 | -0.42572
802.6719 | 122.319 | -109.7534 | 12.2452 | -0.003128 | -0.0083763 | -0.013894 | 0.014326 | -0.0057315 | -0.0046612 | 0.0016427 | 2.449 | 2.3392 | 2.4124 | 12.4603 | 12.3322 | 12.4741 | 12.0621 | 12.3962 | 12.1719 | 9.1278 | 112.1658 | -9.906 | 112.2025 | 122.2137 | 0.086975 | 118.8812 | -0.073242 | 0.036621 | 121.8155 | 122.1497 | 122.0856 | 112.0926 | 112.2025 | 121.9254 | 122.2275 | 118.8812 | 112.0926 | 112.2025 | 122.2275 | 122.0856 | 121.9254 | -9.8328 | -3.1174
803.6719 | 122.2641 | -115.9973 | 6.0791 | -0.003128 | -0.0077353 | -0.016244 | 0.021589 | -0.0070133 | -0.0072246 | 0.0012155 | 1.1673 | 1.1169 | 1.1307 | 6.1798 | 6.0791 | 6.1844 | 5.9967 | 6.1203 | 6.0516 | 5.9555 | 117.128 | -4.9622 | 117.1646 | 122.1771 | 0 | 121.9528 | -0.027466 | 0.036621 | 121.994 | 122.1176 | 122.0764 | 117.1143 | 117.1646 | 122.049 | 122.1817 | 121.9528 | 117.1143 | 117.1646 | 122.1817 | 122.0764 | 122.049 | -4.9484 | -0.1236
804.6719 | 122.2641 | -115.3656 | 6.7245 | -0.003128 | -0.0068809 | -0.018167 | 0.019453 | -0.0072269 | -0.0048748 | 0.0016427 | 1.236 | 1.2177 | 1.2222 | 6.8481 | 6.7474 | 6.8298 | 6.6742 | 6.7932 | 6.7108 | 6.5918 | 116.5878 | -5.5069 | 116.6016 | 122.2137 | 0.022889 | 121.9574 | -0.013733 | 0.013733 | 122.0398 | 122.1588 | 122.113 | 116.5833 | 116.6016 | 122.0764 | 122.1954 | 121.9574 | 116.5833 | 116.6016 | 122.1954 | 122.113 | 122.0764 | -5.5023 | -0.13275
805.6719 | 122.2504 | -115.5121 | 6.5918 | -0.010758 | -0.0073081 | -0.016244 | 0.020307 | -0.0070133 | -0.0038068 | -0.00070712 | 1.2543 | 1.268 | 1.236 | 6.6513 | 6.5506 | 6.6605 | 6.5826 | 6.6376 | 6.5872 | 6.4499 | 116.748 | -5.3238 | 116.7664 | 122.1634 | -0.041199 | 121.962 | -0.004578 | 0.01831 | 122.0947 | 122.1497 | 122.0627 | 116.7801 | 116.7664 | 122.0993 | 122.1725 | 121.962 | 116.7801 | 116.7664 | 122.1725 | 122.0627 | 122.0993 | -5.3558 | -0.14191
806.6719 | 122.2641 | -114.8849 | 7.1915 | 0.0045015 | -0.0053855 | -0.016458 | 0.021162 | -0.0072269 | -0.0046612 | 0.00036108 | 1.387 | 1.3321 | 1.3275 | 7.3059 | 7.2006 | 7.3105 | 7.1411 | 7.2739 | 7.1823 | 7.0267 | 116.2125 | -5.8594 | 116.272 | 122.1909 | 0.009156 | 121.9116 | -0.009155 | 0.059509 | 122.0261 | 122.1588 | 122.0856 | 116.217 | 116.272 | 122.0673 | 122.1954 | 121.9116 | 116.217 | 116.272 | 122.1954 | 122.0856 | 122.0673 | -5.864 | -0.1648
807.6719 | 122.2733 | -114.8254 | 7.251 | -0.010758 | -0.0043173 | -0.015817 | 0.020307 | -0.0057315 | -0.0072246 | 0.00014748 | 1.3596 | 1.2772 | 1.3229 | 7.37 | 7.2647 | 7.3746 | 7.1732 | 7.3288 | 7.2189 | 7.0908 | 116.1484 | -5.9738 | 116.185 | 122.1954 | 0.013732 | 121.9162 | -0.032044 | 0.036621 | 121.9986 | 122.1542 | 122.0901 | 116.1026 | 116.185 | 122.0444 | 122.2 | 121.9162 | 116.1026 | 116.185 | 122.2 | 122.0901 | 122.0444 | -5.928 | -0.16022
808.6719 | 122.2412 | -115.4297 | 6.6788 | -0.003128 | -0.0051719 | -0.014749 | 0.020521 | -0.0072269 | -0.0038068 | 0.00036108 | 1.1902 | 1.1719 | 1.1765 | 6.7383 | 6.633 | 6.7383 | 6.6238 | 6.6833 | 6.6284 | 6.5186 | 116.6061 | -5.5069 | 116.6199 | 122.168 | -0.045776 | 121.9482 | -0.050354 | 0.013733 | 122.0535 | 122.113 | 122.0627 | 116.6016 | 116.6199 | 122.0581 | 122.168 | 121.9482 | 116.6016 | 116.6199 | 122.168 | 122.0627 | 122.0581 | -5.5023 | -0.16022
809.6719 | 122.2641 | -114.6194 | 7.489 | -0.010758 | -0.0064535 | -0.013894 | 0.019453 | -0.0050907 | -0.0074384 | 0.0010019 | 1.3184 | 1.3 | 1.2955 | 7.5394 | 7.4661 | 7.5851 | 7.4203 | 7.5211 | 7.4432 | 7.2693 | 115.9149 | -6.189 | 115.9378 | 122.1588 | -0.022889 | 121.8887 | -0.045777 | 0.022888 | 122.0398 | 122.1405 | 122.0856 | 115.9195 | 115.9378 | 122.0627 | 122.2046 | 121.8887 | 115.9195 | 115.9378 | 122.2046 | 122.0856 | 122.0627 | -6.1935 | -0.21973
810.6562 | 122.2687 | -115.5029 | 6.6376 | -0.010758 | -0.0055991 | -0.017953 | 0.018384 | -0.0070133 | -0.0050884 | 0.00057468 | 1.1536 | 1.1078 | 1.0941 | 6.7245 | 6.601 | 6.72 | 6.5552 | 6.6605 | 6.5826 | 6.4957 | 116.597 | -5.5298 | 116.6565 | 122.2275 | -0.036621 | 121.9986 | -0.054931 | 0.059509 | 122.0581 | 122.1634 | 122.1039 | 116.6107 | 116.6565 | 122.0856 | 122.2229 | 121.9986 | 116.6107 | 116.6565 | 122.2229 | 122.1039 | 122.0856 | -5.5435 | -0.14191
811.6719 | 122.2824 | -114.8117 | 7.2647 | -0.010758 | -0.0075217 | -0.014535 | 0.020093 | -0.0055179 | -0.0080792 | 0.0024973 | 1.2314 | 1.2085 | 1.2085 | 7.3746 | 7.283 | 7.3746 | 7.2052 | 7.338 | 7.251 | 7.0999 | 116.0202 | -6.0562 | 116.0431 | 122.1863 | 0.018311 | 121.9116 | -0.013732 | 0.022888 | 122.0169 | 122.1497 | 122.0947 | 116.0202 | 116.0431 | 122.0627 | 122.1863 | 121.9116 | 116.0202 | 116.0431 | 122.1863 | 122.0947 | 122.0627 | -6.0562 | -0.16479
812.6562 | 122.2458 | -115.8783 | 6.2485 | -0.010758 | -0.0088035 | -0.015603 | 0.018384 | -0.0059451 | -0.0063702 | 0.0022837 | 1.0117 | 1.0391 | 1.0391 | 6.2668 | 6.1798 | 6.2942 | 6.2622 | 6.2393 | 6.2164 | 6.0791 | 116.9174 | -5.2093 | 116.89 | 122.1451 | -0.068664 | 121.9574 | -0.032043 | -0.027466 | 122.1405 | 122.1176 | 122.0581 | 116.9174 | 116.89 | 122.0947 | 122.1725 | 121.9574 | 116.9174 | 116.89 | 122.1725 | 122.0581 | 122.0947 | -5.2093 | -0.16937
813.6719 | 122.2961 | -114.4135 | 7.6447 | -0.010758 | -0.0070945 | -0.013253 | 0.020307 | -0.0078677 | -0.0057294 | -0.0015615 | 1.3824 | 1.3596 | 1.3824 | 7.7683 | 7.6767 | 7.7774 | 7.6172 | 7.7133 | 7.6126 | 7.457 | 115.7959 | -6.2851 | 115.7959 | 122.1817 | 0.032044 | 121.8704 | -0.032043 | 0 | 122.0306 | 122.1268 | 122.0901 | 115.773 | 115.7959 | 122.0261 | 122.1909 | 121.8704 | 115.773 | 115.7959 | 122.1909 | 122.0901 | 122.0261 | -6.2622 | -0.18768
814.6719 | 122.2824 | -114.6744 | 7.4249 | -0.003128 | -0.0068809 | -0.012185 | 0.018171 | -0.0063723 | -0.0057294 | 0.0016427 | 1.355 | 1.3138 | 1.3 | 7.4982 | 7.402 | 7.5256 | 7.3517 | 7.4844 | 7.37 | 7.1869 | 115.9744 | -6.1111 | 116.0294 | 122.1725 | -0.022888 | 121.8613 | -0.054932 | 0.054931 | 122.0261 | 122.1588 | 122.0764 | 115.9882 | 116.0294 | 122.0444 | 122.2 | 121.8613 | 115.9882 | 116.0294 | 122.2 | 122.0764 | 122.0444 | -6.1249 | -0.23804
815.6719 | 122.2778 | -114.1342 | 7.988 | -0.003128 | -0.0075217 | -0.018167 | 0.020948 | -0.0063723 | -0.0046612 | 0.0010019 | 1.3412 | 1.3229 | 1.3275 | 8.0704 | 7.9742 | 8.1024 | 7.9559 | 8.0521 | 7.9788 | 7.7728 | 115.4617 | -6.665 | 115.4755 | 122.2046 | -0.013733 | 121.907 | -0.009155 | 0.013733 | 122.0901 | 122.1863 | 122.1085 | 115.4572 | 115.4755 | 122.113 | 122.2366 | 121.907 | 115.4572 | 115.4755 | 122.2366 | 122.1085 | 122.113 | -6.6605 | -0.21515
816.6719 | 122.2641 | -115.5029 | 6.6147 | -0.003128 | -0.0073081 | -0.015817 | 0.020307 | -0.0070133 | -0.0048748 | 0.0018565 | 1.1627 | 1.1673 | 1.1581 | 6.6696 | 6.5918 | 6.7108 | 6.5735 | 6.6605 | 6.5781 | 6.4636 | 116.6611 | -5.4474 | 116.6656 | 122.1725 | -0.022888 | 121.9666 | -0.036621 | 0.004578 | 122.0764 | 122.1634 | 122.0947 | 116.6702 | 116.6656 | 122.081 | 122.2137 | 121.9666 | 116.6702 | 116.6656 | 122.2137 | 122.0947 | 122.081 | -5.4565 | -0.15106
817.6562 | 122.2733 | -115.4205 | 6.7108 | -0.010758 | -0.0081625 | -0.014962 | 0.019239 | -0.0044497 | -0.0063702 | 0.0012155 | 1.1948 | 1.1307 | 1.1353 | 6.8069 | 6.7017 | 6.8207 | 6.6422 | 6.7749 | 6.6742 | 6.5552 | 116.5558 | -5.5801 | 116.6153 | 122.2275 | -0.009155 | 121.9757 | -0.036621 | 0.059509 | 122.0627 | 122.1954 | 122.1222 | 116.5512 | 116.6153 | 122.0947 | 122.2412 | 121.9757 | 116.5512 | 116.6153 | 122.2412 | 122.1222 | 122.0947 | -5.5756 | -0.15564
818.6719 | 122.2275 | -115.2878 | 6.839 | 0.0045015 | -0.0055991 | -0.011971 | 0.017957 | -0.0072269 | -0.0048748 | 0.00036108 | 1.0712 | 1.0941 | 1.0895 | 6.8436 | 6.7566 | 6.8939 | 6.7932 | 6.8024 | 6.8253 | 6.6559 | 116.3773 | -5.7449 | 116.3589 | 122.1313 | -0.082397 | 121.9437 | -0.013733 | -0.018311 | 122.081 | 122.0901 | 122.0444 | 116.3818 | 116.3589 | 122.113 | 122.1817 | 121.9437 | 116.3818 | 116.3589 | 122.1817 | 122.0444 | 122.113 | -5.7495 | -0.1831
819.6562 | 122.2321 | -113.9145 | 8.2077 | -0.018387 | -0.0088035 | -0.01603 | 0.017103 | -0.0080813 | -0.005302 | -6.6324e-05 | 1.4099 | 1.4282 | 1.4145 | 8.2397 | 8.1436 | 8.2626 | 8.2214 | 8.2123 | 8.1757 | 7.8964 | 115.329 | -6.7795 | 115.3244 | 122.1542 | -0.064087 | 121.8109 | -0.032044 | -0.004578 | 122.1359 | 122.1268 | 122.0581 | 115.3427 | 115.3244 | 122.0901 | 122.1771 | 121.8109 | 115.3427 | 115.3244 | 122.1771 | 122.0581 | 122.0901 | -6.7932 | -0.31128
820.6719 | 122.2778 | -114.8666 | 7.2693 | -0.018387 | -0.0083763 | -0.014749 | 0.019025 | -0.0050907 | -0.0048748 | 0.0031381 | 1.2451 | 1.2589 | 1.2497 | 7.3288 | 7.2189 | 7.3471 | 7.251 | 7.2876 | 7.2372 | 7.0816 | 116.1163 | -6.0104 | 116.1118 | 122.1954 | -0.050354 | 121.9482 | -0.032043 | -0.004578 | 122.1176 | 122.1542 | 122.0856 | 116.1255 | 116.1118 | 122.1039 | 122.2137 | 121.9482 | 116.1255 | 116.1118 | 122.2137 | 122.0856 | 122.1039 | -6.0196 | -0.18768
821.6719 | 122.287 | -112.8983 | 9.2148 | -0.018387 | -0.0068809 | -0.019021 | 0.018812 | -0.0059451 | -0.0067974 | 0.0016427 | 1.6067 | 1.5793 | 1.6022 | 9.3201 | 9.2056 | 9.3155 | 9.1461 | 9.2697 | 9.1644 | 8.6151 | 114.5004 | -7.6355 | 114.505 | 122.2183 | -0.009156 | 121.5134 | -0.050354 | 0.004577 | 122.0444 | 122.168 | 122.1039 | 114.4775 | 114.505 | 122.0627 | 122.2137 | 121.5134 | 114.4775 | 114.505 | 122.2137 | 122.1039 | 122.0627 | -7.6126 | -0.59967
822.6719 | 122.287 | -114.0381 | 8.0887 | -0.010758 | -0.0085899 | -0.014108 | 0.019025 | -0.0072269 | -0.005943 | -0.00027992 | 1.355 | 1.3275 | 1.3092 | 8.2031 | 8.0887 | 8.2077 | 8.0338 | 8.1619 | 8.075 | 7.8323 | 115.3473 | -6.7612 | 115.3931 | 122.2412 | 0 | 121.8704 | -0.013733 | 0.045776 | 122.0718 | 122.2 | 122.1268 | 115.3656 | 115.3931 | 122.113 | 122.2458 | 121.8704 | 115.3656 | 115.3931 | 122.2458 | 122.1268 | 122.113 | -6.7795 | -0.25635
823.6719 | 122.3648 | -114.9857 | 7.0724 | -0.010758 | -0.0092307 | -0.014535 | 0.01753 | -0.0063723 | -0.005302 | 0.0016427 | 1.1032 | 0.98877 | 1.0666 | 7.2372 | 7.1548 | 7.3059 | 6.8527 | 7.2098 | 7.0404 | 6.9626 | 116.0522 | -6.0837 | 116.0889 | 122.2229 | 0.082397 | 121.9482 | -0.032044 | 0.036621 | 121.8384 | 122.1954 | 122.1405 | 115.9744 | 116.0889 | 122.0261 | 122.2916 | 121.9482 | 115.9744 | 116.0889 | 122.2916 | 122.1405 | 122.0261 | -6.0059 | -0.10986
824.6562 | 122.2595 | -114.8071 | 7.3059 | -0.018387 | -0.0068809 | -0.013894 | 0.020734 | -0.0061587 | -0.0046612 | 0.00014748 | 1.1169 | 1.0941 | 1.0986 | 7.3975 | 7.2876 | 7.4066 | 7.2601 | 7.3242 | 7.283 | 7.132 | 115.9058 | -6.2119 | 115.9241 | 122.2046 | -0.01831 | 121.9391 | -0.022888 | 0.01831 | 122.0673 | 122.1313 | 122.0947 | 115.9012 | 115.9241 | 122.0901 | 122.2137 | 121.9391 | 115.9012 | 115.9241 | 122.2137 | 122.0947 | 122.0901 | -6.2073 | -0.17395
825.6562 | 122.2549 | -113.8962 | 8.2352 | -0.010758 | -0.0081625 | -0.01304 | 0.020948 | -0.0059451 | -0.0048748 | 0.00036108 | 1.2772 | 1.2497 | 1.268 | 8.3038 | 8.2031 | 8.3176 | 8.1619 | 8.2489 | 8.194 | 7.9376 | 115.1642 | -6.9855 | 115.1733 | 122.2 | -0.032043 | 121.8338 | -0.041198 | 0.009156 | 122.0581 | 122.1451 | 122.0993 | 115.1459 | 115.1733 | 122.0901 | 122.2137 | 121.8338 | 115.1459 | 115.1733 | 122.2137 | 122.0993 | 122.0901 | -6.9672 | -0.29755
826.6562 | 122.2641 | -115.3427 | 6.752 | -0.018387 | -0.0070945 | -0.015389 | 0.020734 | -0.0063723 | -0.0040204 | -0.00092072 | 1.0071 | 1.03 | 0.99335 | 6.8024 | 6.7154 | 6.8253 | 6.7566 | 6.7841 | 6.7337 | 6.601 | 116.3361 | -5.722 | 116.3498 | 122.1451 | -0.036621 | 121.9437 | -0.01831 | 0.013733 | 122.0993 | 122.1268 | 122.0581 | 116.3727 | 116.3498 | 122.0764 | 122.168 | 121.9437 | 116.3727 | 116.3498 | 122.168 | 122.0581 | 122.0764 | -5.7587 | -0.15106
827.6719 | 122.2824 | -114.5187 | 7.5989 | -0.003128 | -0.01094 | -0.01838 | 0.019025 | -0.0065859 | -0.007011 | -0.00027992 | 1.2039 | 1.1673 | 1.181 | 7.6767 | 7.5714 | 7.6859 | 7.5211 | 7.6538 | 7.5577 | 7.37 | 115.6998 | -6.4316 | 115.7227 | 122.1954 | -0.027466 | 121.8887 | -0.041199 | 0.022888 | 122.0398 | 122.1725 | 122.0901 | 115.686 | 115.7227 | 122.0764 | 122.2046 | 121.8887 | 115.686 | 115.7227 | 122.2046 | 122.0901 | 122.0764 | -6.4178 | -0.22888
828.6719 | 122.3236 | -109.0759 | 13.0051 | -0.003128 | -0.012221 | -0.019448 | 0.012403 | -0.0070133 | -0.0050884 | 0.0046335 | 2.0691 | 2.0325 | 2.0782 | 13.1699 | 13.0875 | 13.2477 | 12.9684 | 13.1516 | 13.0005 | 9.1278 | 111.1542 | -10.9726 | 111.145 | 122.2458 | 0.082397 | 118.2037 | -0.004578 | -0.009155 | 122.0444 | 122.2275 | 122.1634 | 111.1084 | 111.145 | 122.0764 | 122.3236 | 118.2037 | 111.1084 | 111.145 | 122.3236 | 122.1634 | 122.0764 | -10.9268 | -3.8773
829.6719 | 122.2824 | -109.021 | 13.0646 | -0.010758 | -0.0045309 | -0.014962 | 0.019239 | -0.010004 | -0.0061566 | 0.0024973 | 2.2247 | 2.1652 | 2.1744 | 13.2294 | 13.1012 | 13.2294 | 13.0371 | 13.1561 | 13.0371 | 9.1232 | 111.1954 | -10.8994 | 111.2457 | 122.2504 | 0.036621 | 118.1442 | -0.027466 | 0.050354 | 122.0581 | 122.1771 | 122.1222 | 111.1862 | 111.2457 | 122.0581 | 122.2504 | 118.1442 | 111.1862 | 111.2457 | 122.2504 | 122.1222 | 122.0581 | -10.8902 | -3.9413
830.6562 | 122.2321 | -109.3414 | 12.8128 | -0.003128 | -0.0058127 | -0.017098 | 0.019453 | -0.0070133 | -0.0027386 | 0.0018565 | 2.0782 | 2.124 | 2.0737 | 12.8769 | 12.7487 | 12.8952 | 12.8311 | 12.7899 | 12.7945 | 9.1324 | 111.4151 | -10.6888 | 111.4197 | 122.2183 | -0.064087 | 118.4738 | -0.01831 | 0.004578 | 122.1725 | 122.1313 | 122.0901 | 111.4655 | 111.4197 | 122.1359 | 122.2366 | 118.4738 | 111.4655 | 111.4197 | 122.2366 | 122.0901 | 122.1359 | -10.7391 | -3.6804
831.6562 | 122.2458 | -109.227 | 12.8723 | -0.010758 | -0.0066673 | -0.013253 | 0.020734 | -0.0057315 | -0.0057294 | 0.0018565 | 2.0554 | 2.0828 | 2.0782 | 12.9456 | 12.8174 | 12.9547 | 12.9089 | 12.8677 | 12.8723 | 9.1278 | 111.3052 | -10.7895 | 111.2823 | 122.1725 | -0.054931 | 118.3548 | 0 | -0.022888 | 122.1359 | 122.0947 | 122.0444 | 111.3098 | 111.2823 | 122.0993 | 122.1817 | 118.3548 | 111.3098 | 111.2823 | 122.1817 | 122.0444 | 122.0993 | -10.7941 | -3.7445
832.6719 | 122.2458 | -109.3506 | 12.7396 | -0.010758 | -0.0060263 | -0.01368 | 0.018812 | -0.0063723 | -0.0033794 | -6.6324e-05 | 2.0599 | 2.0599 | 2.0416 | 12.8128 | 12.6892 | 12.8265 | 12.7396 | 12.7304 | 12.7121 | 9.1324 | 111.3922 | -10.6796 | 111.4105 | 122.1634 | -0.050354 | 118.483 | -0.027466 | 0.018311 | 122.0901 | 122.081 | 122.0398 | 111.4105 | 111.4105 | 122.0627 | 122.1771 | 118.483 | 111.4105 | 111.4105 | 122.1771 | 122.0398 | 122.0627 | -10.6979 | -3.6072
833.6719 | 122.2366 | -109.4696 | 12.6389 | 0.0045015 | -0.0070945 | -0.01368 | 0.017957 | -0.0055179 | -0.0031658 | 0.0022837 | 2.0462 | 2.0599 | 2.0645 | 12.7167 | 12.6068 | 12.7396 | 12.648 | 12.6297 | 12.6205 | 9.1278 | 111.5341 | -10.5789 | 111.5158 | 122.1863 | -0.032043 | 118.5974 | -0.018311 | -0.01831 | 122.1176 | 122.0993 | 122.0764 | 111.5295 | 111.5158 | 122.0901 | 122.2092 | 118.5974 | 111.5295 | 111.5158 | 122.2092 | 122.0764 | 122.0901 | -10.5743 | -3.511
834.6719 | 122.2595 | -109.6985 | 12.442 | -0.003128 | -0.0068809 | -0.01603 | 0.016676 | -0.0091495 | -0.0040204 | 0.0035653 | 2.0554 | 2.0645 | 2.0874 | 12.4969 | 12.3734 | 12.5198 | 12.4054 | 12.4008 | 12.3962 | 9.1278 | 111.7859 | -10.3775 | 111.7538 | 122.1954 | -0.068665 | 118.8263 | -0.045777 | -0.032043 | 122.1039 | 122.0993 | 122.0718 | 111.763 | 111.7538 | 122.0947 | 122.2183 | 118.8263 | 111.763 | 111.7538 | 122.2183 | 122.0718 | 122.0947 | -10.3546 | -3.3142
835.6719 | 122.2687 | -109.845 | 12.2406 | -0.003128 | -0.0066673 | -0.014962 | 0.018384 | -0.0061587 | -0.0033794 | 0.0018565 | 1.9684 | 1.9867 | 1.9547 | 12.3093 | 12.1857 | 12.3276 | 12.236 | 12.2314 | 12.2406 | 9.1187 | 111.7996 | -10.2539 | 111.8134 | 122.1542 | -0.054932 | 118.9636 | 0 | 0.013733 | 122.081 | 122.0764 | 122.0306 | 111.8317 | 111.8134 | 122.0856 | 122.1725 | 118.9636 | 111.8317 | 111.8134 | 122.1725 | 122.0306 | 122.0856 | -10.2859 | -3.1219
836.6719 | 122.3419 | -109.6527 | 12.41 | -0.010758 | -0.0081625 | -0.01838 | 0.017316 | -0.0067995 | -0.0040204 | 0.00078828 | 2.0737 | 2.0508 | 2.0554 | 12.5839 | 12.4603 | 12.6068 | 12.3413 | 12.5061 | 12.4008 | 9.1324 | 111.7081 | -10.3592 | 111.7264 | 122.2366 | 0.050354 | 118.7851 | -0.009155 | 0.01831 | 121.994 | 122.1588 | 122.113 | 111.7035 | 111.7264 | 122.0535 | 122.2595 | 118.7851 | 111.7035 | 111.7264 | 122.2595 | 122.113 | 122.0535 | -10.3546 | -3.2776
837.6719 | 122.3557 | -109.2682 | 12.822 | -0.003128 | -0.01393 | -0.018594 | 0.011121 | -0.0091495 | -0.0055156 | 0.0018565 | 2.0966 | 1.9913 | 2.0874 | 12.9868 | 12.8952 | 13.0508 | 12.7167 | 12.941 | 12.7762 | 9.1324 | 111.3556 | -10.8307 | 111.3647 | 122.2549 | 0.073243 | 118.4006 | -0.045776 | 0.009156 | 121.9849 | 122.2092 | 122.1634 | 111.2595 | 111.3647 | 122.0444 | 122.319 | 118.4006 | 111.2595 | 111.3647 | 122.319 | 122.1634 | 122.0444 | -10.7346 | -3.6896
838.6875 | 122.3831 | -109.3918 | 12.6938 | -0.010758 | -0.011153 | -0.018167 | 0.016462 | -0.0070133 | -0.003593 | 0.0020701 | 2.0966 | 2.0004 | 2.0645 | 12.8906 | 12.7762 | 12.9501 | 12.5198 | 12.854 | 12.6297 | 9.137 | 111.4563 | -10.6934 | 111.4883 | 122.2824 | 0.082397 | 118.5287 | -0.064087 | 0.032044 | 121.9116 | 122.2458 | 122.168 | 111.3922 | 111.4883 | 122.0215 | 122.3419 | 118.5287 | 111.3922 | 111.4883 | 122.3419 | 122.168 | 122.0215 | -10.6293 | -3.5568
839.6719 | 122.3373 | -109.6664 | 12.3917 | -0.003128 | -0.012862 | -0.019448 | 0.014753 | -0.0093631 | -0.0067974 | 0.0012155 | 2.0737 | 1.9455 | 2.0187 | 12.616 | 12.4924 | 12.6434 | 12.2543 | 12.5565 | 12.3642 | 9.1232 | 111.6852 | -10.4462 | 111.7401 | 122.2824 | 0.10071 | 118.7897 | -0.027466 | 0.054931 | 121.9208 | 122.2229 | 122.1588 | 111.6119 | 111.7401 | 122.0306 | 122.3099 | 118.7897 | 111.6119 | 111.7401 | 122.3099 | 122.1588 | 122.0306 | -10.3729 | -3.2684
840.6719 | 122.3007 | -109.6573 | 12.4466 | -0.003128 | -0.0085899 | -0.014962 | 0.01988 | -0.0080813 | -0.0063702 | 0.0020701 | 2.0187 | 1.9958 | 2.0142 | 12.5839 | 12.442 | 12.6022 | 12.4008 | 12.4924 | 12.4283 | 9.1187 | 111.6714 | -10.4507 | 111.676 | 122.2412 | -0.004577 | 118.7759 | -0.01831 | 0.004578 | 122.0581 | 122.1497 | 122.0993 | 111.6531 | 111.676 | 122.0856 | 122.2595 | 118.7759 | 111.6531 | 111.676 | 122.2595 | 122.0993 | 122.0856 | -10.4324 | -3.3279
841.6719 | 122.3923 | -109.758 | 12.3138 | -0.010758 | -0.013503 | -0.017312 | 0.017316 | -0.010004 | -0.005943 | 0.0014291 | 2.0325 | 1.886 | 1.9821 | 12.561 | 12.4329 | 12.5885 | 12.149 | 12.5061 | 12.291 | 9.1324 | 111.7401 | -10.4279 | 111.7905 | 122.319 | 0.11902 | 118.8904 | -0.022888 | 0.050354 | 121.907 | 122.2641 | 122.1909 | 111.644 | 111.7905 | 122.049 | 122.3465 | 118.8904 | 111.644 | 111.7905 | 122.3465 | 122.1909 | 122.049 | -10.3317 | -3.1815
842.6719 | 122.3877 | -109.7992 | 12.2589 | -0.010758 | -0.013503 | -0.017953 | 0.015607 | -0.0085085 | -0.0048748 | 0.00014748 | 2.037 | 1.8677 | 1.9867 | 12.4878 | 12.3688 | 12.5244 | 12.0895 | 12.4329 | 12.2131 | 9.1187 | 111.7859 | -10.3912 | 111.8362 | 122.287 | 0.10986 | 118.9178 | -0.045776 | 0.050354 | 121.8887 | 122.2321 | 122.168 | 111.6669 | 111.8362 | 122.0123 | 122.3236 | 118.9178 | 111.6669 | 111.8362 | 122.3236 | 122.168 | 122.0123 | -10.2722 | -3.1403
843.6875 | 122.3694 | -109.79 | 12.2543 | -0.003128 | -0.014571 | -0.020089 | 0.016035 | -0.010645 | -0.0063702 | -0.00092072 | 2.0325 | 1.8997 | 1.9821 | 12.4878 | 12.3642 | 12.529 | 12.1262 | 12.4374 | 12.2223 | 9.1278 | 111.7722 | -10.3546 | 111.8225 | 122.2778 | 0.10986 | 118.9178 | -0.032043 | 0.050354 | 121.9162 | 122.2275 | 122.1542 | 111.6898 | 111.8225 | 122.0123 | 122.319 | 118.9178 | 111.6898 | 111.8225 | 122.319 | 122.1542 | 122.0123 | -10.2722 | -3.1265
844.6719 | 122.3877 | -109.1675 | 12.8998 | -0.010758 | -0.010512 | -0.019021 | 0.017103 | -0.010004 | -0.0046612 | 0.0018565 | 2.1515 | 2.0004 | 2.1149 | 13.1378 | 13.0051 | 13.1653 | 12.7396 | 13.0829 | 12.854 | 9.1278 | 111.2823 | -10.8994 | 111.319 | 122.3053 | 0.10529 | 118.2953 | -0.045776 | 0.036621 | 121.907 | 122.2504 | 122.1725 | 111.1679 | 111.319 | 122.0215 | 122.3328 | 118.2953 | 111.1679 | 111.319 | 122.3328 | 122.1725 | 122.0215 | -10.7849 | -3.772
845.6719 | 122.3419 | -109.3918 | 12.7487 | -0.018387 | -0.013503 | -0.019021 | 0.016676 | -0.011286 | -0.007011 | 0.00036108 | 2.0737 | 2.0233 | 2.092 | 12.9044 | 12.7579 | 12.9364 | 12.6434 | 12.8494 | 12.6801 | 9.1324 | 111.4838 | -10.7254 | 111.4655 | 122.2961 | 0.009156 | 118.5242 | -0.068664 | -0.018311 | 122.0352 | 122.2412 | 122.1497 | 111.4151 | 111.4655 | 122.0718 | 122.3282 | 118.5242 | 111.4151 | 111.4655 | 122.3282 | 122.1497 | 122.0718 | -10.6567 | -3.6163
846.6719 | 122.3465 | -109.5245 | 12.6572 | 0.0045015 | -0.015426 | -0.019876 | 0.01518 | -0.012568 | -0.007011 | 0.0010019 | 2.0554 | 1.9913 | 2.0645 | 12.8311 | 12.6892 | 12.8494 | 12.5748 | 12.7762 | 12.616 | 9.1324 | 111.5891 | -10.6659 | 111.5799 | 122.3557 | 0.032043 | 118.6569 | -0.041199 | -0.009155 | 122.0993 | 122.3007 | 122.2137 | 111.5158 | 111.5799 | 122.1405 | 122.374 | 118.6569 | 111.5158 | 111.5799 | 122.374 | 122.2137 | 122.1405 | -10.5927 | -3.5248
847.6719 | 122.3877 | -109.3506 | 12.767 | 0.0045015 | -0.012221 | -0.019235 | 0.019025 | -0.011713 | -0.0063702 | 0.00014748 | 2.2156 | 2.0645 | 2.1835 | 13.0783 | 12.9272 | 13.0417 | 12.6846 | 12.9822 | 12.7441 | 9.1324 | 111.5341 | -10.7025 | 111.5662 | 122.4289 | 0.16022 | 118.483 | -0.022888 | 0.032043 | 122.0352 | 122.3328 | 122.2778 | 111.4151 | 111.5662 | 122.0947 | 122.3923 | 118.483 | 111.4151 | 111.5662 | 122.3923 | 122.2778 | 122.0947 | -10.5835 | -3.6346
848.6719 | 122.4106 | -109.1766 | 12.9089 | -0.003128 | -0.01094 | -0.013894 | 0.018384 | -0.0080813 | -0.0080792 | -6.6324e-05 | 2.1744 | 2.0096 | 2.1011 | 13.1607 | 13.028 | 13.1607 | 12.7396 | 13.092 | 12.854 | 9.137 | 111.2778 | -10.8994 | 111.351 | 122.3373 | 0.11902 | 118.3136 | -0.054932 | 0.073242 | 121.9162 | 122.2687 | 122.2046 | 111.1862 | 111.351 | 122.0306 | 122.3373 | 118.3136 | 111.1862 | 111.351 | 122.3373 | 122.2046 | 122.0306 | -10.8078 | -3.772
849.6719 | 122.3694 | -109.5016 | 12.5931 | 0.0045015 | -0.015212 | -0.021157 | 0.014112 | -0.011072 | -0.0029522 | 0.0014291 | 2.0782 | 2.0004 | 2.0554 | 12.8311 | 12.7029 | 12.8448 | 12.5427 | 12.7579 | 12.5977 | 9.1324 | 111.557 | -10.5927 | 111.5799 | 122.3328 | 0.10986 | 118.634 | 0.004577 | 0.022888 | 122.0444 | 122.2595 | 122.2046 | 111.5021 | 111.5799 | 122.0993 | 122.3465 | 118.634 | 111.5021 | 111.5799 | 122.3465 | 122.2046 | 122.0993 | -10.5377 | -3.4607
850.6719 | 122.3465 | -108.6044 | 13.5544 | -0.010758 | -0.014998 | -0.020944 | 0.015394 | -0.010645 | -0.005302 | -6.6324e-05 | 2.2247 | 2.1606 | 2.2339 | 13.7466 | 13.6047 | 13.7695 | 13.4857 | 13.6642 | 13.5086 | 9.1324 | 110.8383 | -11.3937 | 110.8292 | 122.3511 | 0.050354 | 117.7368 | -0.045776 | -0.009156 | 122.0901 | 122.2687 | 122.2092 | 110.7651 | 110.8292 | 122.113 | 122.374 | 117.7368 | 110.7651 | 110.8292 | 122.374 | 122.2092 | 122.113 | -11.3205 | -4.422
851.6719 | 122.3007 | -110.2936 | 11.8332 | -0.003128 | -0.0068809 | -0.016244 | 0.024152 | -0.0091495 | -0.0065838 | 0.00014748 | 1.7578 | 1.7807 | 1.8082 | 11.9385 | 11.7966 | 11.9476 | 11.7874 | 11.8469 | 11.7966 | 9.1141 | 112.1017 | -10.0525 | 112.0514 | 122.2321 | -0.036621 | 119.4077 | -0.036621 | -0.050355 | 122.081 | 122.1405 | 122.0901 | 112.0743 | 112.0514 | 122.0901 | 122.2412 | 119.4077 | 112.0743 | 112.0514 | 122.2412 | 122.0901 | 122.0901 | -10.025 | -2.7191
852.6719 | 122.3969 | -113.0676 | 9.05 | -0.003128 | -0.014358 | -0.01603 | 0.016248 | -0.011927 | -0.0057294 | 0.00014748 | 1.3229 | 1.2314 | 1.3 | 9.2651 | 9.1599 | 9.2834 | 8.9355 | 9.2285 | 9.0179 | 8.6243 | 114.3677 | -7.8186 | 114.3906 | 122.3328 | 0.10986 | 121.6919 | -0.032044 | 0.022888 | 122.0032 | 122.2961 | 122.2275 | 114.299 | 114.3906 | 122.0856 | 122.3511 | 121.6919 | 114.299 | 114.3906 | 122.3511 | 122.2275 | 122.0856 | -7.7499 | -0.42572
853.6875 | 122.3511 | -111.6257 | 10.4919 | 0.0045015 | -0.014785 | -0.019662 | 0.017316 | -0.013208 | -0.0063702 | 0.0020701 | 1.6525 | 1.5793 | 1.6296 | 10.6476 | 10.5331 | 10.6796 | 10.3867 | 10.5972 | 10.4187 | 9.0225 | 113.2553 | -8.9127 | 113.2782 | 122.2733 | 0.041199 | 120.6482 | -0.073242 | 0.022888 | 122.0123 | 122.2229 | 122.1588 | 113.205 | 113.2782 | 122.0444 | 122.3053 | 120.6482 | 113.205 | 113.2782 | 122.3053 | 122.1588 | 122.0444 | -8.8623 | -1.4694
854.6719 | 122.406 | -110.7147 | 11.4304 | 0.0045015 | -0.012008 | -0.017526 | 0.016889 | -0.011072 | -0.0044476 | 0.00078828 | 1.9272 | 1.7807 | 1.8585 | 11.6913 | 11.5494 | 11.7004 | 11.3159 | 11.6272 | 11.4029 | 9.1095 | 112.5732 | -9.6497 | 112.6419 | 122.406 | 0.11902 | 119.8242 | -0.027466 | 0.068664 | 122.0306 | 122.3419 | 122.2641 | 112.4954 | 112.6419 | 122.1176 | 122.4152 | 119.8242 | 112.4954 | 112.6419 | 122.4152 | 122.2641 | 122.1176 | -9.5718 | -2.3209
855.6719 | 122.3007 | -114.5279 | 7.695 | -0.010758 | -0.0092307 | -0.020944 | 0.01988 | -0.013422 | -0.005943 | 0.0016427 | 1.1948 | 1.1398 | 1.181 | 7.7683 | 7.663 | 7.7499 | 7.6675 | 7.7225 | 7.6721 | 7.4844 | 115.7089 | -6.5552 | 115.7227 | 122.2961 | -0.032043 | 122.0123 | -0.022888 | 0.013733 | 122.1954 | 122.2504 | 122.1909 | 115.6677 | 115.7227 | 122.2 | 122.2778 | 122.0123 | 115.6677 | 115.7227 | 122.2778 | 122.1909 | 122.2 | -6.514 | -0.21057
856.6719 | 122.4014 | -116.0065 | 6.1478 | -0.003128 | -0.01158 | -0.020303 | 0.018812 | -0.011499 | -0.005943 | -0.00027992 | 0.87433 | 0.83313 | 0.86517 | 6.3217 | 6.221 | 6.3492 | 6.015 | 6.2988 | 6.1203 | 6.0928 | 116.8716 | -5.3146 | 116.8808 | 122.3282 | 0.073242 | 122.0993 | -0.027466 | 0.009156 | 122.0215 | 122.3053 | 122.2275 | 116.8396 | 116.8808 | 122.1268 | 122.3557 | 122.0993 | 116.8396 | 116.8808 | 122.3557 | 122.2275 | 122.1268 | -5.2826 | -0.054932
857.6719 | 122.406 | -115.9607 | 6.2164 | 0.01976 | -0.013289 | -0.019448 | 0.020093 | -0.012568 | -0.007652 | 0.0024973 | 0.97961 | 0.84686 | 0.93842 | 6.4316 | 6.308 | 6.4133 | 6.0562 | 6.395 | 6.1569 | 6.1295 | 116.8991 | -5.3696 | 116.9403 | 122.3923 | 0.091552 | 122.0901 | -0.05951 | 0.041198 | 122.0169 | 122.3557 | 122.2687 | 116.8076 | 116.9403 | 122.1176 | 122.374 | 122.0901 | 116.8076 | 116.9403 | 122.374 | 122.2687 | 122.1176 | -5.278 | -0.086975
858.6719 | 122.2733 | -115.9653 | 6.2851 | -0.018387 | -0.012221 | -0.020303 | 0.01988 | -0.01214 | -0.0089336 | 0.00036108 | 0.90637 | 0.92468 | 0.91095 | 6.3354 | 6.221 | 6.3217 | 6.2714 | 6.2988 | 6.2439 | 6.1249 | 116.8762 | -5.3604 | 116.8716 | 122.3007 | -0.064087 | 122.0901 | -0.041199 | -0.004578 | 122.2366 | 122.2641 | 122.1863 | 116.89 | 116.8716 | 122.2092 | 122.287 | 122.0901 | 116.89 | 116.8716 | 122.287 | 122.1863 | 122.2092 | -5.3741 | -0.16022
859.6719 | 122.4518 | -115.2924 | 6.8344 | 0.01213 | -0.01393 | -0.017098 | 0.018384 | -0.0089359 | -0.005943 | 0.0010019 | 1.0941 | 0.92926 | 1.0208 | 7.077 | 6.9534 | 7.0999 | 6.665 | 7.0587 | 6.8115 | 6.7337 | 116.3132 | -5.9052 | 116.3864 | 122.3694 | 0.11902 | 122.0261 | -0.022889 | 0.073242 | 121.9574 | 122.3511 | 122.2458 | 116.2216 | 116.3864 | 122.1039 | 122.3923 | 122.0261 | 116.2216 | 116.3864 | 122.3923 | 122.2458 | 122.1039 | -5.8136 | -0.10071
860.6719 | 122.4106 | -115.2054 | 6.9534 | -0.003128 | -0.014785 | -0.019662 | 0.018384 | -0.010218 | -0.005943 | 0.0020701 | 1.03 | 0.93842 | 1.0071 | 7.1457 | 7.0496 | 7.1915 | 6.8253 | 7.1182 | 6.9351 | 6.8436 | 116.2125 | -6.015 | 116.2354 | 122.3511 | 0.096131 | 122.0489 | -0.01831 | 0.022888 | 122.0306 | 122.3236 | 122.2549 | 116.1438 | 116.2354 | 122.1405 | 122.3969 | 122.0489 | 116.1438 | 116.2354 | 122.3969 | 122.2549 | 122.1405 | -5.9463 | -0.10986
861.6719 | 122.4152 | -115.4938 | 6.6833 | 0.0045015 | -0.01393 | -0.022012 | 0.020521 | -0.011072 | -0.0085064 | -0.00027992 | 1.062 | 0.9201 | 1.0117 | 6.8756 | 6.7795 | 6.8802 | 6.5323 | 6.8665 | 6.6467 | 6.5735 | 116.5054 | -5.7632 | 116.5558 | 122.3694 | 0.09613 | 122.0673 | -0.036621 | 0.050354 | 122.0261 | 122.3602 | 122.2733 | 116.4139 | 116.5558 | 122.1405 | 122.374 | 122.0673 | 116.4139 | 116.5558 | 122.374 | 122.2733 | 122.1405 | -5.6717 | -0.10986
862.6719 | 122.406 | -114.2899 | 7.869 | -0.010758 | -0.012649 | -0.017098 | 0.020093 | -0.010859 | -0.007652 | -0.00070712 | 1.2634 | 1.1398 | 1.2085 | 8.1161 | 8.0017 | 8.107 | 7.7499 | 8.075 | 7.8232 | 7.7087 | 115.4984 | -6.7291 | 115.5533 | 122.406 | 0.13275 | 121.9986 | -0.045777 | 0.054932 | 122.0398 | 122.3648 | 122.2916 | 115.4297 | 115.5533 | 122.113 | 122.3969 | 121.9986 | 115.4297 | 115.5533 | 122.3969 | 122.2916 | 122.113 | -6.6605 | -0.16022
863.6719 | 122.319 | -115.3519 | 6.8298 | 0.0045015 | -0.010085 | -0.015176 | 0.024793 | -0.0080813 | -0.0080792 | 0.0024973 | 0.92926 | 0.91553 | 0.9201 | 6.9077 | 6.7886 | 6.9305 | 6.6879 | 6.8481 | 6.7566 | 6.6696 | 116.272 | -5.9143 | 116.2811 | 122.2595 | -0.041199 | 122.0215 | -0.073242 | 0.009155 | 122.0398 | 122.2 | 122.1405 | 116.2674 | 116.2811 | 122.1085 | 122.2824 | 122.0215 | 116.2674 | 116.2811 | 122.2824 | 122.1405 | 122.1085 | -5.9097 | -0.16022
864.6719 | 122.4289 | -114.8666 | 7.3105 | -0.010758 | -0.012221 | -0.017953 | 0.019025 | -0.0091495 | -0.0061566 | 0.0018565 | 1.1444 | 1.0025 | 1.0849 | 7.5256 | 7.4158 | 7.5211 | 7.1548 | 7.4936 | 7.251 | 7.1777 | 115.9515 | -6.308 | 116.011 | 122.3923 | 0.10529 | 122.0444 | -0.059509 | 0.059509 | 122.0215 | 122.3602 | 122.2824 | 115.8691 | 116.011 | 122.1176 | 122.3877 | 122.0444 | 115.8691 | 116.011 | 122.3877 | 122.2824 | 122.1176 | -6.2256 | -0.13275
865.6719 | 122.3099 | -114.83 | 7.37 | -0.010758 | -0.012435 | -0.022225 | 0.018598 | -0.011713 | -0.005943 | -0.00027992 | 1.149 | 1.0437 | 1.1215 | 7.5211 | 7.4158 | 7.5119 | 7.3334 | 7.4707 | 7.3471 | 7.2235 | 115.9515 | -6.3263 | 115.979 | 122.3511 | 0.045776 | 122.0535 | -0.022888 | 0.027466 | 122.1634 | 122.3007 | 122.2458 | 115.8737 | 115.979 | 122.1771 | 122.3419 | 122.0535 | 115.8737 | 115.979 | 122.3419 | 122.2458 | 122.1771 | -6.2485 | -0.14648
866.6719 | 122.4197 | -114.6011 | 7.5806 | 0.0045015 | -0.012008 | -0.017098 | 0.017957 | -0.010645 | -0.0072246 | -0.00092072 | 1.1948 | 1.0483 | 1.149 | 7.8003 | 7.6859 | 7.7957 | 7.4249 | 7.7637 | 7.5256 | 7.4341 | 115.7501 | -6.5323 | 115.7959 | 122.4014 | 0.10529 | 122.0352 | -0.054931 | 0.045776 | 122.0261 | 122.3648 | 122.287 | 115.6494 | 115.7959 | 122.1268 | 122.3969 | 122.0352 | 115.6494 | 115.7959 | 122.3969 | 122.287 | 122.1268 | -6.4316 | -0.14648
867.6719 | 122.4289 | -115.0955 | 7.0999 | 0.0045015 | -0.01628 | -0.017953 | 0.018171 | -0.010645 | -0.0061566 | 0.0018565 | 1.1032 | 0.95673 | 1.0345 | 7.3242 | 7.2281 | 7.3471 | 6.9443 | 7.2968 | 7.0633 | 6.9901 | 116.1301 | -6.1432 | 116.1987 | 122.4197 | 0.12817 | 122.0856 | -0.036622 | 0.068664 | 122.0398 | 122.3923 | 122.3236 | 116.0522 | 116.1987 | 122.1588 | 122.4426 | 122.0856 | 116.0522 | 116.1987 | 122.4426 | 122.3236 | 122.1588 | -6.0654 | -0.10986
868.6719 | 122.2916 | -114.5599 | 7.6218 | -0.010758 | -0.0064535 | -0.014962 | 0.023511 | -0.0076541 | -0.0074384 | -0.00070712 | 1.0437 | 1.0391 | 1.0254 | 7.6767 | 7.5668 | 7.6767 | 7.5943 | 7.5943 | 7.5989 | 7.4112 | 115.5853 | -6.5826 | 115.6036 | 122.2366 | -0.054932 | 121.9711 | -0.022888 | 0.01831 | 122.1542 | 122.1542 | 122.1268 | 115.5991 | 115.6036 | 122.1588 | 122.2366 | 121.9711 | 115.5991 | 115.6036 | 122.2366 | 122.1268 | 122.1588 | -6.5964 | -0.21057
869.6719 | 122.4197 | -114.4959 | 7.663 | -0.003128 | -0.012649 | -0.018807 | 0.018171 | -0.0087223 | -0.00872 | 0.0012155 | 1.181 | 1.0757 | 1.1261 | 7.8735 | 7.7591 | 7.8781 | 7.5119 | 7.8461 | 7.5989 | 7.4936 | 115.6219 | -6.5872 | 115.6769 | 122.3694 | 0.09613 | 121.9894 | -0.064087 | 0.054931 | 122.0078 | 122.3419 | 122.2549 | 115.5716 | 115.6769 | 122.0947 | 122.374 | 121.9894 | 115.5716 | 115.6769 | 122.374 | 122.2549 | 122.0947 | -6.5369 | -0.16937
870.6719 | 122.3831 | -112.9303 | 9.2697 | -0.018387 | -0.01393 | -0.019448 | 0.017957 | -0.0089359 | -0.007652 | -6.6324e-05 | 1.4511 | 1.3138 | 1.4008 | 9.462 | 9.343 | 9.4528 | 9.1736 | 9.4208 | 9.2285 | 8.6838 | 114.3311 | -7.9559 | 114.3814 | 122.3923 | 0.073243 | 121.6141 | -0.041198 | 0.050354 | 122.1039 | 122.3511 | 122.2733 | 114.2441 | 114.3814 | 122.1588 | 122.3831 | 121.6141 | 114.2441 | 114.3814 | 122.3831 | 122.2733 | 122.1588 | -7.869 | -0.58594
871.6719 | 122.3145 | -110.0189 | 12.1948 | -0.003128 | -0.0055991 | -0.014535 | 0.022871 | -0.0091495 | -0.0072246 | 0.00036108 | 1.8814 | 1.8814 | 1.8906 | 12.3322 | 12.2086 | 12.3184 | 12.2269 | 12.2543 | 12.1445 | 9.1232 | 111.9095 | -10.3134 | 111.9003 | 122.3511 | 0.013733 | 119.1422 | -0.050354 | -0.009155 | 122.2458 | 122.2733 | 122.2275 | 111.9003 | 111.9003 | 122.1634 | 122.3373 | 119.1422 | 111.9003 | 111.9003 | 122.3373 | 122.2275 | 122.1634 | -10.3043 | -3.0716
872.6719 | 122.4426 | -110.2753 | 11.8744 | -0.010758 | -0.012008 | -0.019235 | 0.015821 | -0.010645 | -0.0078656 | 0.00036108 | 1.9455 | 1.7761 | 1.8723 | 12.149 | 12.0392 | 12.1582 | 11.7783 | 12.1078 | 11.824 | 9.1187 | 112.1475 | -10.0983 | 112.2208 | 122.4243 | 0.16479 | 119.3939 | -0.050354 | 0.073243 | 122.0535 | 122.3831 | 122.3145 | 112.0514 | 112.2208 | 122.0993 | 122.4335 | 119.3939 | 112.0514 | 112.2208 | 122.4335 | 122.3145 | 122.0993 | -10.0021 | -2.7557
873.6719 | 122.3053 | -110.3302 | 11.8744 | 0.0045015 | -0.0066673 | -0.021371 | 0.020734 | -0.0093631 | -0.0044476 | 0.00014748 | 1.7807 | 1.799 | 1.7899 | 11.9659 | 11.8378 | 11.9705 | 11.8652 | 11.8423 | 11.8057 | 9.1187 | 112.1201 | -10.0754 | 112.1109 | 122.2961 | -0.036621 | 119.4489 | -0.068665 | -0.009155 | 122.1954 | 122.1725 | 122.168 | 112.1292 | 112.1109 | 122.1359 | 122.3007 | 119.4489 | 112.1292 | 112.1109 | 122.3007 | 122.168 | 122.1359 | -10.0845 | -2.7557
874.6719 | 122.4243 | -110.1105 | 12.0392 | -0.003128 | -0.012862 | -0.014108 | 0.014539 | -0.0080813 | -0.0082928 | 0.0012155 | 1.9867 | 1.8448 | 1.9363 | 12.291 | 12.1765 | 12.3047 | 11.9247 | 12.2498 | 11.9934 | 9.1232 | 112.0468 | -10.1944 | 112.0972 | 122.4014 | 0.13733 | 119.2337 | -0.045777 | 0.050354 | 122.0352 | 122.3602 | 122.287 | 111.9553 | 112.0972 | 122.1039 | 122.4152 | 119.2337 | 111.9553 | 112.0972 | 122.4152 | 122.287 | 122.1039 | -10.1028 | -2.916
875.6719 | 122.2961 | -116.7847 | 5.4703 | 0.0045015 | -0.01094 | -0.022866 | 0.020307 | -0.0097903 | -0.005302 | 0.00078828 | 0.69122 | 0.70038 | 0.70496 | 5.5023 | 5.4199 | 5.5115 | 5.4428 | 5.4794 | 5.4382 | 5.3329 | 117.4896 | -4.7699 | 117.4759 | 122.287 | -0.050354 | 122.1176 | -0.032044 | -0.013733 | 122.2275 | 122.2641 | 122.2046 | 117.485 | 117.4759 | 122.2229 | 122.2961 | 122.1176 | 117.485 | 117.4759 | 122.2961 | 122.2046 | 122.2229 | -4.7653 | -0.13733
876.6719 | 122.4564 | -116.2399 | 5.928 | -0.010758 | -0.016494 | -0.024575 | 0.015607 | -0.0093631 | -0.0057294 | 0.00078828 | 0.86975 | 0.75073 | 0.84228 | 6.134 | 6.0471 | 6.1615 | 5.7861 | 6.1157 | 5.8914 | 5.8731 | 117.0822 | -5.1773 | 117.1097 | 122.374 | 0.11902 | 122.113 | -0.036622 | 0.027466 | 122.0261 | 122.3557 | 122.287 | 116.9907 | 117.1097 | 122.1313 | 122.4014 | 122.113 | 116.9907 | 117.1097 | 122.4014 | 122.287 | 122.1313 | -5.0858 | -0.054932
877.6719 | 122.3145 | -115.7364 | 6.4865 | -0.003128 | -0.012008 | -0.020944 | 0.01988 | -0.010859 | -0.0074384 | 0.00036108 | 0.98877 | 0.92468 | 0.96588 | 6.5643 | 6.4636 | 6.5781 | 6.4499 | 6.5323 | 6.4362 | 6.3583 | 116.7023 | -5.5618 | 116.7252 | 122.3007 | -0.022888 | 122.0947 | -0.050354 | 0.022889 | 122.1863 | 122.2687 | 122.2 | 116.6611 | 116.7252 | 122.1725 | 122.3145 | 122.0947 | 116.6611 | 116.7252 | 122.3145 | 122.2 | 122.1725 | -5.5206 | -0.12817
878.6875 | 122.4564 | -115.4251 | 6.7612 | -0.003128 | -0.013076 | -0.02073 | 0.014753 | -0.0093631 | -0.0061566 | 0.0016427 | 0.92926 | 0.83771 | 0.92468 | 6.9626 | 6.8665 | 6.9992 | 6.6422 | 6.9534 | 6.7245 | 6.7017 | 116.3498 | -5.9235 | 116.3544 | 122.3877 | 0.10529 | 122.1268 | -0.036621 | 0.004577 | 122.0673 | 122.3785 | 122.2916 | 116.2628 | 116.3544 | 122.1497 | 122.4243 | 122.1268 | 116.2628 | 116.3544 | 122.4243 | 122.2916 | 122.1497 | -5.8365 | -0.059509
879.6719 | 122.3007 | -114.6194 | 7.6263 | -0.010758 | -0.0085899 | -0.020516 | 0.02223 | -0.010218 | -0.0078656 | 0.0018565 | 1.0941 | 1.1261 | 1.1124 | 7.6813 | 7.5668 | 7.6859 | 7.6401 | 7.6492 | 7.5989 | 7.3929 | 115.7318 | -6.5002 | 115.7135 | 122.3007 | -0.05951 | 122.0123 | -0.027466 | -0.018311 | 122.2595 | 122.2687 | 122.1863 | 115.7455 | 115.7135 | 122.2183 | 122.3053 | 122.0123 | 115.7455 | 115.7135 | 122.3053 | 122.1863 | 122.2183 | -6.514 | -0.23346
880.6719 | 122.4472 | -114.8987 | 7.2556 | 0.01213 | -0.013289 | -0.019876 | 0.017957 | -0.010218 | -0.0080792 | 0.0022837 | 1.0986 | 0.9613 | 1.0574 | 7.4478 | 7.3517 | 7.489 | 7.0999 | 7.4478 | 7.2189 | 7.1365 | 115.9561 | -6.2942 | 115.9973 | 122.3465 | 0.096131 | 122.0352 | -0.036621 | 0.041199 | 121.9986 | 122.3465 | 122.2504 | 115.86 | 115.9973 | 122.1176 | 122.3877 | 122.0352 | 115.86 | 115.9973 | 122.3877 | 122.2504 | 122.1176 | -6.1981 | -0.11902
881.6719 | 122.3282 | -114.9261 | 7.3196 | -0.010758 | -0.011367 | -0.019448 | 0.018812 | -0.010645 | -0.0065838 | -6.6324e-05 | 1.0529 | 1.0117 | 1.0529 | 7.4112 | 7.2968 | 7.4112 | 7.3013 | 7.3563 | 7.283 | 7.1457 | 115.979 | -6.308 | 115.979 | 122.3373 | -0.022888 | 122.0718 | -0.036621 | 0 | 122.2275 | 122.2824 | 122.2229 | 115.9378 | 115.979 | 122.2092 | 122.3373 | 122.0718 | 115.9378 | 115.979 | 122.3373 | 122.2229 | 122.2092 | -6.2668 | -0.17395
882.6719 | 122.438 | -114.9033 | 7.2784 | -0.010758 | -0.014358 | -0.020516 | 0.016035 | -0.010218 | -0.0074384 | -0.00070712 | 1.0483 | 0.93842 | 1.0345 | 7.4615 | 7.3654 | 7.489 | 7.1457 | 7.4478 | 7.2235 | 7.1365 | 115.9378 | -6.34 | 115.9515 | 122.3648 | 0.086975 | 122.0398 | -0.054931 | 0.013733 | 122.049 | 122.3511 | 122.2687 | 115.8417 | 115.9515 | 122.1268 | 122.3923 | 122.0398 | 115.8417 | 115.9515 | 122.3923 | 122.2687 | 122.1268 | -6.2439 | -0.14191
883.6875 | 122.3923 | -114.5737 | 7.5943 | -0.003128 | -0.014785 | -0.021371 | 0.017316 | -0.01214 | -0.007011 | 0.00014748 | 1.0529 | 1.0071 | 1.062 | 7.7499 | 7.6309 | 7.7911 | 7.4844 | 7.7225 | 7.576 | 7.4387 | 115.6357 | -6.5872 | 115.6265 | 122.3236 | 0.036621 | 122.0123 | -0.01831 | -0.009156 | 122.0581 | 122.2961 | 122.2046 | 115.5807 | 115.6265 | 122.1497 | 122.3648 | 122.0123 | 115.5807 | 115.6265 | 122.3648 | 122.2046 | 122.1497 | -6.5323 | -0.15564
884.6719 | 122.4472 | -116.7801 | 5.4199 | -0.010758 | -0.012862 | -0.016244 | 0.01988 | -0.0087223 | -0.0065838 | 0.00014748 | 0.8194 | 0.67749 | 0.78735 | 5.603 | 5.5115 | 5.6351 | 5.2231 | 5.5939 | 5.3604 | 5.365 | 117.5674 | -4.7424 | 117.5995 | 122.3831 | 0.091553 | 122.1451 | -0.059509 | 0.032043 | 122.0032 | 122.374 | 122.2916 | 117.4576 | 117.5995 | 122.1405 | 122.4152 | 122.1451 | 117.4576 | 117.5995 | 122.4152 | 122.2916 | 122.1405 | -4.6326 | -0.054932
885.6719 | 122.4106 | -116.5604 | 5.658 | -0.018387 | -0.01094 | -0.01603 | 0.020948 | -0.01214 | -0.0063702 | -6.6324e-05 | 0.87433 | 0.74158 | 0.83313 | 5.8319 | 5.7266 | 5.8273 | 5.5298 | 5.8182 | 5.5893 | 5.5939 | 117.3935 | -4.9164 | 117.4347 | 122.3923 | 0.068665 | 122.1542 | -0.068665 | 0.041199 | 122.0901 | 122.3785 | 122.287 | 117.3019 | 117.4347 | 122.1497 | 122.3877 | 122.1542 | 117.3019 | 117.4347 | 122.3877 | 122.287 | 122.1497 | -4.8248 | -0.064087
886.6719 | 122.4564 | -116.6794 | 5.5389 | 0.0045015 | -0.014571 | -0.02308 | 0.01988 | -0.011286 | -0.0082928 | -6.6324e-05 | 0.84686 | 0.69122 | 0.79651 | 5.7266 | 5.6213 | 5.7449 | 5.3741 | 5.7129 | 5.4794 | 5.4749 | 117.4759 | -4.8477 | 117.5262 | 122.406 | 0.082398 | 122.1542 | -0.059509 | 0.050354 | 122.0535 | 122.3923 | 122.3007 | 117.3706 | 117.5262 | 122.1588 | 122.4243 | 122.1542 | 117.3706 | 117.5262 | 122.4243 | 122.3007 | 122.1588 | -4.7424 | -0.064086
887.6719 | 122.3053 | -115.6357 | 6.6284 | 0.0045015 | -0.01158 | -0.019021 | 0.022657 | -0.010004 | -0.0063702 | -0.00049352 | 0.92468 | 0.94299 | 0.95673 | 6.6925 | 6.5735 | 6.6833 | 6.6238 | 6.6422 | 6.5918 | 6.4636 | 116.5924 | -5.6854 | 116.5604 | 122.3282 | -0.054932 | 122.0993 | -0.036621 | -0.032043 | 122.2595 | 122.2778 | 122.2092 | 116.5787 | 116.5604 | 122.2275 | 122.319 | 122.0993 | 116.5787 | 116.5604 | 122.319 | 122.2092 | 122.2275 | -5.6717 | -0.16479
888.6719 | 122.3145 | -116.4825 | 5.7358 | -0.010758 | -0.0083763 | -0.012826 | 0.024152 | -0.0072269 | -0.0082928 | 0.00057468 | 0.74158 | 0.76446 | 0.74158 | 5.7678 | 5.6305 | 5.7587 | 5.658 | 5.6763 | 5.69 | 5.5984 | 117.2241 | -4.9713 | 117.2241 | 122.2504 | -0.10529 | 122.081 | -0.045777 | 0 | 122.1405 | 122.1588 | 122.113 | 117.247 | 117.2241 | 122.1725 | 122.2412 | 122.081 | 117.247 | 117.2241 | 122.2412 | 122.113 | 122.1725 | -4.9942 | -0.13733
889.6719 | 122.4609 | -116.2216 | 5.9555 | -0.003128 | -0.014571 | -0.017953 | 0.014967 | -0.0091495 | -0.005302 | 0.00078828 | 0.91553 | 0.7782 | 0.86517 | 6.1615 | 6.0837 | 6.1935 | 5.8136 | 6.1523 | 5.9372 | 5.9006 | 117.0868 | -5.1773 | 117.1371 | 122.3831 | 0.12817 | 122.1222 | -0.01831 | 0.050354 | 122.0352 | 122.374 | 122.3053 | 116.9998 | 117.1371 | 122.1588 | 122.4152 | 122.1222 | 116.9998 | 117.1371 | 122.4152 | 122.3053 | 122.1588 | -5.0903 | -0.054931
890.6719 | 122.4518 | -114.7156 | 7.4753 | -0.003128 | -0.014998 | -0.018167 | 0.017103 | -0.0089359 | -0.0072246 | 0.0010019 | 1.1215 | 0.97961 | 1.0757 | 7.6721 | 7.576 | 7.6996 | 7.3334 | 7.6584 | 7.4432 | 7.3151 | 115.7913 | -6.4957 | 115.8371 | 122.3877 | 0.10071 | 122.0306 | -0.032044 | 0.045776 | 122.049 | 122.374 | 122.2916 | 115.6952 | 115.8371 | 122.1588 | 122.4152 | 122.0306 | 115.6952 | 115.8371 | 122.4152 | 122.2916 | 122.1588 | -6.3995 | -0.16022
891.6719 | 122.2961 | -116.0248 | 6.2485 | -0.010758 | -0.0085899 | -0.017312 | 0.020093 | -0.01214 | -0.007652 | -0.00027992 | 0.87891 | 0.89722 | 0.90179 | 6.2942 | 6.1752 | 6.2668 | 6.2531 | 6.2393 | 6.1981 | 6.0837 | 116.9266 | -5.3513 | 116.9037 | 122.319 | -0.073242 | 122.1085 | -0.050354 | -0.022888 | 122.2778 | 122.2641 | 122.2 | 116.922 | 116.9037 | 122.2229 | 122.2916 | 122.1085 | 116.922 | 116.9037 | 122.2916 | 122.2 | 122.2229 | -5.3467 | -0.16479
892.6719 | 122.4289 | -115.6631 | 6.5369 | -0.003128 | -0.012862 | -0.018807 | 0.017957 | -0.011713 | -0.005943 | -0.00027992 | 0.93842 | 0.83771 | 0.91095 | 6.7154 | 6.6147 | 6.7429 | 6.3858 | 6.6879 | 6.5002 | 6.4316 | 116.5741 | -5.6992 | 116.6016 | 122.3785 | 0.07782 | 122.0947 | -0.036621 | 0.027466 | 122.0489 | 122.3511 | 122.2778 | 116.5009 | 116.6016 | 122.1634 | 122.406 | 122.0947 | 116.5009 | 116.6016 | 122.406 | 122.2778 | 122.1634 | -5.6259 | -0.10528
893.6719 | 122.3419 | -114.9078 | 7.2876 | 0.0045015 | -0.0070945 | -0.015176 | 0.026502 | -0.0080813 | -0.0061566 | 0.00036108 | 1.1078 | 1.0162 | 1.03 | 7.4158 | 7.2556 | 7.3105 | 7.1686 | 7.2968 | 7.2418 | 7.0999 | 115.9378 | -6.2714 | 116.0156 | 122.3236 | -0.032044 | 122.0078 | -0.045777 | 0.07782 | 122.0764 | 122.2046 | 122.1634 | 115.9241 | 116.0156 | 122.1497 | 122.2183 | 122.0078 | 115.9241 | 116.0156 | 122.2183 | 122.1634 | 122.1497 | -6.2576 | -0.18768
894.6719 | 122.4792 | -113.2919 | 8.8623 | -0.003128 | -0.013076 | -0.02073 | 0.015821 | -0.011286 | -0.0050884 | 0.0012155 | 1.4008 | 1.268 | 1.3596 | 9.1141 | 9.0042 | 9.1324 | 8.7204 | 9.0958 | 8.8028 | 8.4503 | 114.6515 | -7.5943 | 114.6927 | 122.406 | 0.14191 | 121.7422 | -0.05951 | 0.041199 | 122.0123 | 122.3877 | 122.2961 | 114.5599 | 114.6927 | 122.0947 | 122.4243 | 121.7422 | 114.5599 | 114.6927 | 122.4243 | 122.2961 | 122.0947 | -7.5027 | -0.41199
895.6719 | 122.3282 | -115.2008 | 7.0587 | -0.018387 | -0.0096579 | -0.019662 | 0.019453 | -0.010218 | -0.0061566 | 0.0027109 | 1.0254 | 1.0345 | 1.0529 | 7.1182 | 7.0129 | 7.1228 | 7.0541 | 7.077 | 7.0129 | 6.8665 | 116.2537 | -6.0242 | 116.2262 | 122.319 | -0.045777 | 122.0673 | -0.045777 | -0.027465 | 122.2549 | 122.2778 | 122.2137 | 116.2354 | 116.2262 | 122.2137 | 122.3236 | 122.0673 | 116.2354 | 116.2262 | 122.3236 | 122.2137 | 122.2137 | -6.0059 | -0.19226
896.6719 | 122.4609 | -114.7522 | 7.4524 | -0.010758 | -0.012435 | -0.020944 | 0.016462 | -0.010859 | -0.0063702 | 0.0016427 | 1.1627 | 1.0208 | 1.1353 | 7.6584 | 7.5623 | 7.6813 | 7.2968 | 7.6492 | 7.3837 | 7.2968 | 115.8875 | -6.4316 | 115.9149 | 122.4106 | 0.10986 | 122.0489 | -0.068665 | 0.027466 | 122.0489 | 122.4014 | 122.3145 | 115.773 | 115.9149 | 122.1359 | 122.4335 | 122.0489 | 115.773 | 115.9149 | 122.4335 | 122.3145 | 122.1359 | -6.3171 | -0.15564
897.6719 | 122.4609 | -110.9299 | 11.2473 | -0.003128 | -0.014998 | -0.019876 | 0.016248 | -0.011286 | -0.0057294 | 0.0010019 | 1.7899 | 1.6525 | 1.7487 | 11.5128 | 11.3983 | 11.5356 | 11.1191 | 11.4716 | 11.2381 | 9.0958 | 112.6785 | -9.5947 | 112.7197 | 122.4426 | 0.15106 | 120.0256 | -0.009155 | 0.041199 | 122.049 | 122.4014 | 122.3282 | 112.5824 | 112.7197 | 122.168 | 122.4655 | 120.0256 | 112.5824 | 112.7197 | 122.4655 | 122.3282 | 122.168 | -9.4986 | -2.1515
898.6719 | 122.3648 | -110.7651 | 11.4395 | -0.010758 | -0.0073081 | -0.017312 | 0.023084 | -0.0087223 | -0.0082928 | -0.00027992 | 1.8127 | 1.7303 | 1.7532 | 11.6272 | 11.467 | 11.6089 | 11.4166 | 11.5128 | 11.3983 | 9.1049 | 112.5183 | -9.7092 | 112.5778 | 122.3923 | 0.027466 | 119.87 | -0.041199 | 0.059509 | 122.1817 | 122.2778 | 122.2321 | 112.4954 | 112.5778 | 122.1634 | 122.374 | 119.87 | 112.4954 | 112.5778 | 122.374 | 122.2321 | 122.1634 | -9.6863 | -2.3346
899.6719 | 122.3328 | -110.376 | 11.8561 | -0.003128 | -0.010512 | -0.019662 | 0.018384 | -0.010218 | -0.0063702 | 0.0033517 | 1.8356 | 1.8219 | 1.8448 | 11.9522 | 11.8195 | 11.9568 | 11.8744 | 11.8927 | 11.8011 | 9.1095 | 112.2208 | -10.0342 | 112.2116 | 122.3282 | -0.036621 | 119.4855 | -0.054932 | -0.009156 | 122.2504 | 122.2687 | 122.1954 | 112.1979 | 112.2116 | 122.1771 | 122.3328 | 119.4855 | 112.1979 | 112.2116 | 122.3328 | 122.1954 | 122.1771 | -10.0113 | -2.7466
900.6719 | 122.4106 | -111.3327 | 10.8856 | -0.010758 | -0.011153 | -0.01838 | 0.015394 | -0.010218 | -0.0085064 | -0.00027992 | 1.799 | 1.6296 | 1.7166 | 11.1282 | 11.0046 | 11.1191 | 10.8444 | 11.0733 | 10.849 | 9.0591 | 113.0493 | -9.256 | 113.1317 | 122.4609 | 0.11902 | 120.3918 | -0.036621 | 0.082397 | 122.1771 | 122.406 | 122.3373 | 112.9623 | 113.1317 | 122.1817 | 122.4518 | 120.3918 | 112.9623 | 113.1317 | 122.4518 | 122.3373 | 122.1817 | -9.169 | -1.8265
901.6719 | 122.3236 | -112.1796 | 10.0845 | -0.010758 | -0.010726 | -0.016458 | 0.018384 | -0.010859 | -0.00872 | -6.6324e-05 | 1.4191 | 1.4694 | 1.5106 | 10.1486 | 10.0342 | 10.1669 | 10.0891 | 10.1074 | 10.0067 | 8.9584 | 113.6902 | -8.6151 | 113.5986 | 122.3282 | -0.050354 | 121.138 | -0.07782 | -0.091553 | 122.2687 | 122.287 | 122.2137 | 113.649 | 113.5986 | 122.1863 | 122.3465 | 121.138 | 113.649 | 113.5986 | 122.3465 | 122.2137 | 122.1863 | -8.5739 | -1.1261
902.6719 | 122.4655 | -111.7172 | 10.4919 | -0.010758 | -0.015853 | -0.019235 | 0.016676 | -0.0076541 | -0.0074384 | 0.0010019 | 1.6617 | 1.5289 | 1.6205 | 10.7162 | 10.6155 | 10.7437 | 10.3546 | 10.675 | 10.4462 | 9.0225 | 113.3377 | -8.963 | 113.3789 | 122.4335 | 0.1236 | 120.7397 | -0.045776 | 0.041199 | 122.0718 | 122.3923 | 122.3328 | 113.2462 | 113.3789 | 122.1634 | 122.4609 | 120.7397 | 113.2462 | 113.3789 | 122.4609 | 122.3328 | 122.1634 | -8.8715 | -1.4694
903.6719 | 122.319 | -112.7747 | 9.4208 | -0.010758 | -0.0079489 | -0.012612 | 0.022657 | -0.0085085 | -0.0057294 | 0.0024973 | 1.3641 | 1.3687 | 1.355 | 9.4711 | 9.3658 | 9.4894 | 9.3796 | 9.3887 | 9.3979 | 8.725 | 114.1296 | -8.0521 | 114.1388 | 122.2458 | -0.054931 | 121.4996 | -0.022888 | 0.009156 | 122.1542 | 122.1634 | 122.1405 | 114.1434 | 114.1388 | 122.1725 | 122.2641 | 121.4996 | 114.1434 | 114.1388 | 122.2641 | 122.1405 | 122.1725 | -8.0658 | -0.6958
904.6719 | 122.4289 | -112.619 | 9.5398 | -0.003128 | -0.012649 | -0.014962 | 0.015607 | -0.0074405 | -0.0074384 | 0.0027109 | 1.5152 | 1.3916 | 1.4832 | 9.7733 | 9.6359 | 9.787 | 9.4528 | 9.7321 | 9.494 | 8.812 | 114.1022 | -8.1482 | 114.1342 | 122.3923 | 0.09613 | 121.431 | -0.045776 | 0.032044 | 122.0718 | 122.3511 | 122.2549 | 114.0106 | 114.1342 | 122.113 | 122.406 | 121.431 | 114.0106 | 114.1342 | 122.406 | 122.2549 | 122.113 | -8.0566 | -0.72784
905.6719 | 122.4335 | -111.2 | 11.0092 | -0.003128 | -0.014785 | -0.017526 | 0.016035 | -0.010218 | -0.0067974 | 0.0016427 | 1.7899 | 1.6846 | 1.7487 | 11.2244 | 11.1191 | 11.2564 | 10.9314 | 11.1969 | 10.968 | 9.0729 | 112.9486 | -9.3246 | 112.9898 | 122.4243 | 0.10986 | 120.2728 | -0.041198 | 0.041199 | 122.1313 | 122.3969 | 122.319 | 112.8845 | 112.9898 | 122.168 | 122.4564 | 120.2728 | 112.8845 | 112.9898 | 122.4564 | 122.319 | 122.168 | -9.2606 | -1.9363
906.6719 | 122.4518 | -110.6003 | 11.5814 | 0.0045015 | -0.014571 | -0.017312 | 0.015394 | -0.010218 | -0.0080792 | 0.0014291 | 1.9089 | 1.7532 | 1.8585 | 11.8652 | 11.7233 | 11.8607 | 11.4624 | 11.8103 | 11.5448 | 9.1187 | 112.4588 | -9.8282 | 112.5092 | 122.4655 | 0.14191 | 119.7189 | -0.036621 | 0.050354 | 122.0627 | 122.4106 | 122.3236 | 112.3535 | 112.5092 | 122.1451 | 122.4609 | 119.7189 | 112.3535 | 112.5092 | 122.4609 | 122.3236 | 122.1451 | -9.7229 | -2.4628
907.6719 | 122.374 | -110.1974 | 12.0529 | -0.010758 | -0.0088035 | -0.017098 | 0.02223 | -0.011072 | -0.0040204 | -0.0015615 | 1.973 | 1.9638 | 1.9547 | 12.1674 | 12.0163 | 12.1582 | 12.0804 | 12.0895 | 12.0209 | 9.1187 | 112.1521 | -10.0891 | 112.1704 | 122.3648 | -0.036621 | 119.3161 | -0.032043 | 0.01831 | 122.2778 | 122.287 | 122.2137 | 112.1613 | 112.1704 | 122.2183 | 122.3557 | 119.3161 | 112.1613 | 112.1704 | 122.3557 | 122.2137 | 122.2183 | -10.0983 | -2.9343
908.6719 | 122.3648 | -116.0385 | 6.2302 | -0.003128 | -0.0090171 | -0.019876 | 0.022443 | -0.0080813 | -0.010002 | -6.6324e-05 | 0.9201 | 0.94757 | 0.9201 | 6.2805 | 6.1844 | 6.2576 | 6.2073 | 6.2347 | 6.1707 | 6.0745 | 116.9586 | -5.2826 | 116.9586 | 122.319 | -0.045777 | 122.113 | -0.05951 | 0 | 122.2458 | 122.2733 | 122.2229 | 116.9861 | 116.9586 | 122.2092 | 122.2961 | 122.113 | 116.9861 | 116.9586 | 122.2961 | 122.2229 | 122.2092 | -5.3101 | -0.15564
909.6719 | 122.4838 | -114.4318 | 7.7545 | -0.003128 | -0.014144 | -0.020303 | 0.014967 | -0.0085085 | -0.0089336 | 0.00057468 | 1.236 | 1.0941 | 1.181 | 7.9651 | 7.8644 | 8.0017 | 7.608 | 7.9559 | 7.7133 | 7.5806 | 115.6128 | -6.6605 | 115.6677 | 122.3969 | 0.10986 | 122.0123 | -0.041199 | 0.054932 | 122.0398 | 122.3877 | 122.2961 | 115.5258 | 115.6677 | 122.1451 | 122.4335 | 122.0123 | 115.5258 | 115.6677 | 122.4335 | 122.2961 | 122.1451 | -6.5735 | -0.17395
910.6719 | 122.4701 | -113.2095 | 9.0042 | -0.003128 | -0.015426 | -0.025216 | 0.015821 | -0.011286 | -0.0065838 | 0.0014291 | 1.236 | 1.1032 | 1.1765 | 9.2377 | 9.1232 | 9.2468 | 8.8715 | 9.2148 | 8.9813 | 8.5419 | 114.386 | -7.901 | 114.4455 | 122.4472 | 0.11902 | 121.7514 | -0.022888 | 0.059509 | 122.081 | 122.4243 | 122.3328 | 114.3127 | 114.4455 | 122.1909 | 122.4564 | 121.7514 | 114.3127 | 114.4455 | 122.4564 | 122.3328 | 122.1909 | -7.8278 | -0.46234
911.6719 | 122.3145 | -110.463 | 11.7554 | -0.010758 | -0.0073081 | -0.01603 | 0.02458 | -0.010431 | -0.0072246 | -0.00027992 | 1.1215 | 1.1444 | 1.1353 | 11.911 | 11.7508 | 11.8835 | 11.7691 | 11.7416 | 11.7828 | 9.1141 | 111.5982 | -10.611 | 111.5845 | 122.374 | -0.004578 | 119.577 | 0.027466 | -0.013733 | 122.2321 | 122.2046 | 122.2137 | 111.6074 | 111.5845 | 122.2458 | 122.3465 | 119.577 | 111.6074 | 111.5845 | 122.3465 | 122.2137 | 122.2458 | -10.6201 | -2.6413
912.6719 | 122.3465 | -110.5637 | 11.6913 | -0.003128 | -0.0066673 | -0.017953 | 0.019025 | -0.01214 | -0.0055156 | 0.0016427 | 1.1078 | 1.1444 | 1.1261 | 11.7599 | 11.6409 | 11.7508 | 11.7325 | 11.705 | 11.6364 | 9.1049 | 111.6898 | -10.5469 | 111.6714 | 122.3236 | -0.050354 | 119.6686 | -0.054931 | -0.018311 | 122.2961 | 122.2687 | 122.2046 | 111.7081 | 111.6714 | 122.2 | 122.3145 | 119.6686 | 111.7081 | 111.6714 | 122.3145 | 122.2046 | 122.2 | -10.5652 | -2.5864
913.6719 | 122.438 | -110.3119 | 11.8607 | 0.0045015 | -0.010085 | -0.016671 | 0.020093 | -0.0063723 | -0.0048748 | 0.0014291 | 1.1993 | 1.1124 | 1.1536 | 12.03 | 11.911 | 12.0575 | 11.7508 | 11.9659 | 11.824 | 9.1141 | 111.4655 | -10.7483 | 111.5112 | 122.3419 | 0.050354 | 119.426 | -0.036621 | 0.045777 | 122.0627 | 122.2778 | 122.2229 | 111.4243 | 111.5112 | 122.1359 | 122.3694 | 119.426 | 111.4243 | 111.5112 | 122.3694 | 122.2229 | 122.1359 | -10.7071 | -2.7466
914.6719 | 122.438 | -110.1151 | 12.0895 | -0.010758 | -0.012649 | -0.020944 | 0.016248 | -0.012568 | -0.0072246 | 0.0010019 | 1.3275 | 1.2177 | 1.3138 | 12.3322 | 12.2269 | 12.3505 | 12.0209 | 12.2955 | 12.0392 | 9.1141 | 111.4288 | -10.8719 | 111.4426 | 122.4472 | 0.13733 | 119.2291 | -0.050354 | 0.013733 | 122.1359 | 122.4106 | 122.3419 | 111.3327 | 111.4426 | 122.1542 | 122.4655 | 119.2291 | 111.3327 | 111.4426 | 122.4655 | 122.3419 | 122.1542 | -10.7758 | -2.9755
915.6719 | 122.3373 | -111.1862 | 11.0779 | -0.003128 | -0.010512 | -0.021798 | 0.016462 | -0.01449 | -0.0055156 | 0.0010019 | 0.78278 | 0.74158 | 0.78735 | 11.1877 | 11.055 | 11.1832 | 11.055 | 11.0962 | 11.0275 | 9.0775 | 111.9736 | -10.3363 | 111.969 | 122.374 | -0.022888 | 120.2637 | -0.050354 | -0.004578 | 122.2412 | 122.2824 | 122.2412 | 111.9278 | 111.969 | 122.2137 | 122.3694 | 120.2637 | 111.9278 | 111.969 | 122.3694 | 122.2412 | 122.2137 | -10.2905 | -2.0004
916.6719 | 122.3511 | -110.3027 | 11.9293 | -0.018387 | -0.0081625 | -0.020303 | 0.017316 | -0.0093631 | -0.007652 | 0.0024973 | 0.58136 | 0.54932 | 0.5722 | 12.0575 | 11.9568 | 12.0621 | 11.9431 | 12.0209 | 11.9293 | 9.1141 | 110.8749 | -11.38 | 110.8841 | 122.3602 | 0.027466 | 119.4168 | 0 | 0.009155 | 122.2458 | 122.3236 | 122.2595 | 110.8521 | 110.8841 | 122.2321 | 122.3648 | 119.4168 | 110.8521 | 110.8841 | 122.3648 | 122.2595 | 122.2321 | -11.3571 | -2.8152
917.6719 | 122.4655 | -110.5179 | 11.7188 | -0.003128 | -0.011153 | -0.019021 | 0.017103 | -0.0095767 | -0.0080792 | 0.0012155 | 0.76446 | 0.62714 | 0.71411 | 11.9568 | 11.8149 | 11.9751 | 11.6272 | 11.911 | 11.6776 | 9.1095 | 111.232 | -11.0916 | 111.2823 | 122.4747 | 0.09613 | 119.6274 | -0.041199 | 0.050354 | 122.1451 | 122.4289 | 122.3328 | 111.145 | 111.2823 | 122.1954 | 122.493 | 119.6274 | 111.145 | 111.2823 | 122.493 | 122.3328 | 122.1954 | -11.0046 | -2.6093
918.6719 | 122.3511 | -110.7468 | 11.5036 | -0.003128 | -0.0094443 | -0.015817 | 0.020307 | -0.010431 | -0.0055156 | 0.0018565 | 0.51727 | 0.60883 | 0.59509 | 11.6913 | 11.5402 | 11.6592 | 11.5677 | 11.5494 | 11.5311 | 9.1049 | 111.3419 | -10.8948 | 111.264 | 122.438 | 0.036621 | 119.8517 | 0.027466 | -0.07782 | 122.3145 | 122.2961 | 122.287 | 111.3556 | 111.264 | 122.2778 | 122.406 | 119.8517 | 111.3556 | 111.264 | 122.406 | 122.287 | 122.2778 | -10.9085 | -2.3987
919.6719 | 122.3511 | -110.5545 | 11.7233 | -0.018387 | -0.0073081 | -0.02308 | 0.019025 | -0.0085085 | -0.005943 | 0.0012155 | 0.48523 | 0.49896 | 0.48065 | 11.792 | 11.6638 | 11.8011 | 11.7233 | 11.7416 | 11.6638 | 9.1049 | 111.0352 | -11.2244 | 111.0397 | 122.3465 | -0.05951 | 119.6594 | -0.05951 | 0.004577 | 122.2778 | 122.2961 | 122.2183 | 111.0535 | 111.0397 | 122.2183 | 122.3557 | 119.6594 | 111.0535 | 111.0397 | 122.3557 | 122.2183 | 122.2183 | -11.2427 | -2.6184
920.6719 | 122.3557 | -110.3989 | 11.8607 | -0.003128 | -0.011153 | -0.019235 | 0.018812 | -0.0085085 | -0.0082928 | 0.00036108 | 0.40283 | 0.42572 | 0.39368 | 11.9339 | 11.8057 | 11.9247 | 11.8698 | 11.8698 | 11.8103 | 9.1095 | 110.7925 | -11.4349 | 110.8017 | 122.3328 | -0.054932 | 119.5084 | -0.050354 | 0.009155 | 122.2687 | 122.2687 | 122.2046 | 110.8246 | 110.8017 | 122.2092 | 122.3236 | 119.5084 | 110.8246 | 110.8017 | 122.3236 | 122.2046 | 122.2092 | -11.467 | -2.7512
921.6719 | 122.3328 | -110.7193 | 11.5677 | -0.018387 | -0.010299 | -0.020944 | 0.015821 | -0.0078677 | -0.0080792 | -0.00027992 | 0.54016 | 0.55389 | 0.55389 | 11.6501 | 11.5265 | 11.6409 | 11.5952 | 11.586 | 11.5219 | 9.0958 | 111.2732 | -11.0138 | 111.2595 | 122.3694 | -0.041199 | 119.8151 | -0.045776 | -0.013733 | 122.3145 | 122.3053 | 122.2458 | 111.2732 | 111.2595 | 122.2412 | 122.3602 | 119.8151 | 111.2732 | 111.2595 | 122.3602 | 122.2458 | 122.2412 | -11.0138 | -2.4719
922.6719 | 122.4014 | -110.3668 | 11.8561 | -0.003128 | -0.010299 | -0.02073 | 0.015394 | -0.0095767 | -0.0063702 | 0.0016427 | 0.46234 | 0.36163 | 0.42114 | 12.0712 | 11.9385 | 12.0758 | 11.8423 | 11.998 | 11.8515 | 9.1141 | 110.788 | -11.4944 | 110.8292 | 122.438 | 0.082398 | 119.4809 | -0.004578 | 0.041198 | 122.2092 | 122.3648 | 122.3053 | 110.7285 | 110.8292 | 122.2183 | 122.4426 | 119.4809 | 110.7285 | 110.8292 | 122.4426 | 122.3053 | 122.2183 | -11.4349 | -2.742
923.6719 | 122.3877 | -110.4263 | 11.8149 | -0.018387 | -0.0070945 | -0.014108 | 0.021162 | -0.0082949 | -0.005302 | 0.0014291 | 0.44403 | 0.38452 | 0.39368 | 11.9431 | 11.8057 | 11.9431 | 11.7554 | 11.8607 | 11.7645 | 9.1095 | 110.82 | -11.4304 | 110.8704 | 122.3694 | -0.009155 | 119.5358 | -0.050354 | 0.050354 | 122.1817 | 122.287 | 122.2321 | 110.8109 | 110.8704 | 122.1909 | 122.3694 | 119.5358 | 110.8109 | 110.8704 | 122.3694 | 122.2321 | 122.1909 | -11.4212 | -2.7054
924.6719 | 122.3511 | -110.7742 | 11.467 | -0.010758 | -0.010726 | -0.016885 | 0.016248 | -0.0087223 | -0.0048748 | 0.00078828 | 0.50354 | 0.51727 | 0.50812 | 11.5585 | 11.467 | 11.5814 | 11.5036 | 11.5036 | 11.4304 | 9.0958 | 111.2823 | -10.9497 | 111.2778 | 122.3328 | 0 | 119.87 | -0.036621 | -0.004578 | 122.2778 | 122.2778 | 122.2412 | 111.2915 | 111.2778 | 122.2046 | 122.3557 | 119.87 | 111.2915 | 111.2778 | 122.3557 | 122.2412 | 122.2046 | -10.9589 | -2.3712
925.6719 | 122.3465 | -110.3531 | 11.9522 | -0.010758 | -0.01158 | -0.021157 | 0.017103 | -0.0093631 | -0.0029522 | 0.00036108 | 0.49439 | 0.48523 | 0.48981 | 12.0255 | 11.9247 | 12.0483 | 11.9476 | 11.9659 | 11.9064 | 9.1049 | 110.8429 | -11.467 | 110.8475 | 122.3785 | -0.027465 | 119.458 | -0.045776 | 0.004578 | 122.3007 | 122.319 | 122.2778 | 110.8383 | 110.8475 | 122.2595 | 122.4014 | 119.458 | 110.8383 | 110.8475 | 122.4014 | 122.2778 | 122.2595 | -11.4624 | -2.8473
926.6719 | 122.3511 | -110.4675 | 11.8286 | -0.003128 | -0.0098715 | -0.017312 | 0.017957 | -0.010645 | -0.005943 | 0.0014291 | 0.5127 | 0.49439 | 0.52185 | 11.9156 | 11.8057 | 11.9385 | 11.8561 | 11.8744 | 11.8011 | 9.1095 | 110.9894 | -11.3342 | 110.9802 | 122.3831 | -0.022888 | 119.577 | -0.027466 | -0.009156 | 122.3236 | 122.3419 | 122.2733 | 110.9619 | 110.9802 | 122.2687 | 122.406 | 119.577 | 110.9619 | 110.9802 | 122.406 | 122.2733 | 122.2687 | -11.3068 | -2.7191
927.6719 | 122.3969 | -110.9436 | 11.2976 | -0.010758 | -0.0066673 | -0.018167 | 0.020734 | -0.0080813 | -0.0050884 | 0.0010019 | 0.4303 | 0.37994 | 0.3891 | 11.4441 | 11.3022 | 11.4304 | 11.261 | 11.3754 | 11.2381 | 9.082 | 111.3327 | -10.9177 | 111.3739 | 122.3877 | 0.004578 | 120.0256 | -0.059509 | 0.041199 | 122.2046 | 122.319 | 122.2458 | 111.3235 | 111.3739 | 122.1817 | 122.374 | 120.0256 | 111.3235 | 111.3739 | 122.374 | 122.2458 | 122.1817 | -10.9085 | -2.2156
928.6719 | 122.3969 | -111.0535 | 11.1557 | -0.010758 | -0.0060263 | -0.019021 | 0.020948 | -0.0055179 | -0.0055156 | -0.00092072 | 0.39368 | 0.36163 | 0.37994 | 11.3159 | 11.1694 | 11.3022 | 11.1237 | 11.2381 | 11.1328 | 9.0866 | 111.4334 | -10.7941 | 111.4471 | 122.3694 | 0.013733 | 120.1401 | -0.022889 | 0.013733 | 122.1771 | 122.2916 | 122.2229 | 111.4151 | 111.4471 | 122.1863 | 122.3557 | 120.1401 | 111.4151 | 111.4471 | 122.3557 | 122.2229 | 122.1863 | -10.7758 | -2.0691
929.6719 | 122.3465 | -110.1334 | 12.0987 | -0.003128 | -0.0051719 | -0.017953 | 0.019025 | -0.0050907 | -0.0082928 | -0.00049352 | 0.53558 | 0.51727 | 0.52643 | 12.1811 | 12.0666 | 12.204 | 12.0575 | 12.0987 | 12.0483 | 9.1141 | 110.6598 | -11.5814 | 110.6689 | 122.3145 | -0.032044 | 119.2474 | -0.050354 | 0.009155 | 122.1909 | 122.2321 | 122.2 | 110.6506 | 110.6689 | 122.1817 | 122.3373 | 119.2474 | 110.6506 | 110.6689 | 122.3373 | 122.2 | 122.1817 | -11.5723 | -2.9846
930.6719 | 122.3785 | -110.5316 | 11.6959 | -0.018387 | -0.0096579 | -0.019235 | 0.01283 | -0.0076541 | -0.0046612 | 0.0018565 | 0.42114 | 0.39825 | 0.43488 | 11.8195 | 11.705 | 11.8423 | 11.7142 | 11.7737 | 11.6821 | 9.1003 | 110.9665 | -11.2976 | 110.9528 | 122.3511 | 0.009155 | 119.632 | -0.013733 | -0.013732 | 122.2458 | 122.3053 | 122.2366 | 110.9299 | 110.9528 | 122.2137 | 122.374 | 119.632 | 110.9299 | 110.9528 | 122.374 | 122.2366 | 122.2137 | -11.261 | -2.5955
931.6719 | 122.3648 | -111.8271 | 10.4004 | -0.010758 | -0.0081625 | -0.017312 | 0.020734 | -0.0080813 | -0.0061566 | 0.0010019 | 0.42572 | 0.44403 | 0.41657 | 10.4736 | 10.3638 | 10.5057 | 10.4141 | 10.437 | 10.3775 | 8.9951 | 112.2437 | -9.9564 | 112.2528 | 122.3007 | -0.036621 | 120.8221 | -0.022889 | 0.009155 | 122.2412 | 122.2641 | 122.1909 | 112.2711 | 112.2528 | 122.2046 | 122.3328 | 120.8221 | 112.2711 | 112.2528 | 122.3328 | 122.1909 | 122.2046 | -9.9838 | -1.4053
932.6719 | 122.3831 | -110.6461 | 11.5997 | -0.010758 | -0.0068809 | -0.019876 | 0.016889 | -0.0063723 | -0.0055156 | -0.00092072 | 0.31586 | 0.32959 | 0.32501 | 11.6913 | 11.5814 | 11.705 | 11.6501 | 11.6409 | 11.5814 | 9.1003 | 110.9711 | -11.2701 | 110.9619 | 122.3373 | -0.01831 | 119.7464 | -0.01831 | -0.009155 | 122.2961 | 122.287 | 122.2275 | 110.9756 | 110.9619 | 122.2275 | 122.3511 | 119.7464 | 110.9756 | 110.9619 | 122.3511 | 122.2275 | 122.2275 | -11.2747 | -2.4994
933.6719 | 122.3557 | -110.5591 | 11.7188 | -0.018387 | -0.010085 | -0.016885 | 0.016889 | -0.0078677 | -0.0061566 | 0.0029245 | 0.27008 | 0.28381 | 0.2655 | 11.7828 | 11.673 | 11.8103 | 11.7371 | 11.7416 | 11.6959 | 9.0958 | 110.8246 | -11.4349 | 110.8292 | 122.3419 | -0.045776 | 119.6548 | -0.022888 | 0.004578 | 122.2961 | 122.3007 | 122.2321 | 110.8429 | 110.8292 | 122.2549 | 122.3694 | 119.6548 | 110.8429 | 110.8292 | 122.3694 | 122.2321 | 122.2549 | -11.4532 | -2.623
934.6719 | 122.3419 | -110.4172 | 11.8561 | -0.003128 | -0.010085 | -0.018807 | 0.016035 | -0.0085085 | -0.0057294 | 0.0029245 | 0.27008 | 0.31128 | 0.32501 | 11.9247 | 11.8057 | 11.9431 | 11.8881 | 11.8835 | 11.824 | 9.1141 | 110.7422 | -11.5448 | 110.6873 | 122.3419 | -0.050354 | 119.5312 | -0.032043 | -0.054931 | 122.3053 | 122.3007 | 122.2229 | 110.7285 | 110.6873 | 122.2412 | 122.3602 | 119.5312 | 110.7285 | 110.6873 | 122.3602 | 122.2229 | 122.2412 | -11.5311 | -2.742
935.6719 | 122.4152 | -110.5865 | 11.6226 | -0.003128 | -0.0083763 | -0.01603 | 0.017957 | -0.0070133 | -0.0072246 | 0.0031381 | 0.32501 | 0.27924 | 0.29755 | 11.8057 | 11.6821 | 11.792 | 11.6043 | 11.7279 | 11.6272 | 9.1049 | 110.8841 | -11.3434 | 110.9116 | 122.3923 | 0.059509 | 119.6915 | 0.004577 | 0.027466 | 122.1909 | 122.3145 | 122.2687 | 110.8658 | 110.9116 | 122.2137 | 122.3785 | 119.6915 | 110.8658 | 110.9116 | 122.3785 | 122.2687 | 122.2137 | -11.3251 | -2.5177
936.6719 | 122.3511 | -110.6918 | 11.5814 | -0.010758 | -0.0098715 | -0.014962 | 0.016676 | -0.0093631 | -0.0044476 | 0.00036108 | 0.2243 | 0.2655 | 0.26093 | 11.6409 | 11.5311 | 11.6638 | 11.6226 | 11.5952 | 11.5585 | 9.1049 | 110.9528 | -11.3159 | 110.9161 | 122.3328 | -0.050354 | 119.7968 | -0.022888 | -0.036621 | 122.3145 | 122.287 | 122.2229 | 110.9573 | 110.9161 | 122.2504 | 122.3557 | 119.7968 | 110.9573 | 110.9161 | 122.3557 | 122.2229 | 122.2504 | -11.3205 | -2.4765
937.6719 | 122.3602 | -110.7559 | 11.5036 | -0.003128 | -0.0073081 | -0.016885 | 0.020093 | -0.0065859 | -0.0057294 | 0.0018565 | 0.29755 | 0.31586 | 0.30212 | 11.5494 | 11.4441 | 11.5906 | 11.4807 | 11.4761 | 11.4487 | 9.0912 | 111.058 | -11.1877 | 111.0535 | 122.3053 | -0.059509 | 119.8471 | -0.054932 | -0.004578 | 122.2366 | 122.2321 | 122.2 | 111.0718 | 111.0535 | 122.2046 | 122.3465 | 119.8471 | 111.0718 | 111.0535 | 122.3465 | 122.2 | 122.2046 | -11.2015 | -2.4124
938.6719 | 122.3877 | -110.6918 | 11.499 | -0.003128 | -0.0077353 | -0.017098 | 0.018171 | -0.0074405 | -0.0057294 | 0.00014748 | 0.2655 | 0.2655 | 0.29297 | 11.6043 | 11.4899 | 11.6089 | 11.5128 | 11.5677 | 11.4899 | 9.1003 | 110.9848 | -11.2335 | 110.9573 | 122.2961 | -0.009155 | 119.7922 | -0.009155 | -0.027466 | 122.2046 | 122.2595 | 122.1817 | 110.9573 | 110.9573 | 122.1817 | 122.3007 | 119.7922 | 110.9573 | 110.9573 | 122.3007 | 122.1817 | 122.1817 | -11.2061 | -2.3987
939.6719 | 122.406 | -110.5957 | 11.6226 | -0.018387 | -0.0079489 | -0.011758 | 0.019239 | -0.0061587 | -0.005302 | 0.0014291 | 0.28839 | 0.26093 | 0.25177 | 11.7737 | 11.6409 | 11.7737 | 11.586 | 11.7233 | 11.6089 | 9.1095 | 110.8475 | -11.3617 | 110.8841 | 122.3694 | 0.01831 | 119.7052 | -0.013733 | 0.036621 | 122.1817 | 122.319 | 122.2366 | 110.8566 | 110.8841 | 122.2046 | 122.3694 | 119.7052 | 110.8566 | 110.8841 | 122.3694 | 122.2366 | 122.2046 | -11.3708 | -2.5131
940.6719 | 122.3877 | -110.6735 | 11.5814 | 0.0045015 | -0.0085899 | -0.017098 | 0.018598 | -0.0076541 | -0.0048748 | -0.00092072 | 0.21515 | 0.25177 | 0.24261 | 11.673 | 11.5402 | 11.6913 | 11.5997 | 11.6135 | 11.5631 | 9.0958 | 110.9161 | -11.3297 | 110.8887 | 122.3465 | -0.041199 | 119.7693 | -0.018311 | -0.027466 | 122.2733 | 122.287 | 122.2137 | 110.9253 | 110.8887 | 122.2366 | 122.3648 | 119.7693 | 110.9253 | 110.8887 | 122.3648 | 122.2137 | 122.2366 | -11.3388 | -2.4857
941.6719 | 122.374 | -110.9024 | 11.3754 | -0.003128 | -0.0064535 | -0.020089 | 0.017957 | -0.0074405 | -0.0057294 | -0.0011343 | 0.21515 | 0.24261 | 0.23346 | 11.4578 | 11.3617 | 11.4807 | 11.4212 | 11.4029 | 11.3709 | 9.0958 | 111.1359 | -11.1328 | 111.1176 | 122.3602 | -0.013733 | 119.9982 | -0.004577 | -0.01831 | 122.3236 | 122.3053 | 122.2641 | 111.145 | 111.1176 | 122.2733 | 122.3831 | 119.9982 | 111.145 | 111.1176 | 122.3831 | 122.2641 | 122.2733 | -11.142 | -2.2797
942.6719 | 122.3648 | -111.058 | 11.2473 | -0.003128 | -0.0081625 | -0.017526 | 0.014539 | -0.010218 | -0.005943 | 0.00057468 | 0.34332 | 0.38452 | 0.35248 | 11.3113 | 11.2061 | 11.3297 | 11.2839 | 11.2656 | 11.2152 | 9.0866 | 111.4105 | -10.8627 | 111.4014 | 122.3694 | -0.041198 | 120.1447 | -0.032043 | -0.009155 | 122.3419 | 122.3236 | 122.2641 | 111.4426 | 111.4014 | 122.2733 | 122.3877 | 120.1447 | 111.4426 | 111.4014 | 122.3877 | 122.2641 | 122.2733 | -10.8948 | -2.1606
943.6719 | 122.4197 | -111.145 | 11.1053 | -0.010758 | -0.0079489 | -0.016458 | 0.018384 | -0.0093631 | -0.0057294 | -0.0019889 | 0.48981 | 0.48065 | 0.4715 | 11.2427 | 11.1053 | 11.2518 | 11.1008 | 11.1786 | 11.0825 | 9.0683 | 111.6165 | -10.6247 | 111.6348 | 122.3877 | 0 | 120.2133 | -0.022889 | 0.01831 | 122.2458 | 122.3236 | 122.2504 | 111.6257 | 111.6348 | 122.2275 | 122.3969 | 120.2133 | 111.6257 | 111.6348 | 122.3969 | 122.2504 | 122.2275 | -10.6339 | -2.037
944.6719 | 122.3694 | -111.1725 | 11.1282 | -0.010758 | -0.0092307 | -0.02073 | 0.014326 | -0.0085085 | -0.005943 | 0.00014748 | 0.28839 | 0.32044 | 0.29755 | 11.2152 | 11.1008 | 11.2198 | 11.1557 | 11.1649 | 11.1053 | 9.0729 | 111.47 | -10.8078 | 111.4609 | 122.3877 | -0.027466 | 120.2454 | -0.022888 | -0.009155 | 122.3282 | 122.3373 | 122.2733 | 111.4929 | 111.4609 | 122.2778 | 122.3923 | 120.2454 | 111.4929 | 111.4609 | 122.3923 | 122.2733 | 122.2778 | -10.8307 | -2.0554
945.6719 | 122.374 | -110.8978 | 11.3983 | -0.010758 | -0.0077353 | -0.01838 | 0.016889 | -0.0085085 | -0.0085064 | 0.0012155 | 0.22888 | 0.26093 | 0.23346 | 11.4487 | 11.3297 | 11.4761 | 11.4395 | 11.4166 | 11.3571 | 9.0912 | 111.1313 | -11.1374 | 111.1267 | 122.3465 | -0.068664 | 119.989 | -0.041198 | -0.004577 | 122.3373 | 122.3145 | 122.2275 | 111.1588 | 111.1267 | 122.2549 | 122.374 | 119.989 | 111.1588 | 111.1267 | 122.374 | 122.2275 | 122.2549 | -11.1649 | -2.3071
946.6719 | 122.3465 | -110.527 | 11.7416 | -0.018387 | -0.0088035 | -0.017098 | 0.016248 | -0.0097903 | -0.0061566 | 0.0010019 | 0.25177 | 0.25635 | 0.25177 | 11.8332 | 11.7096 | 11.8515 | 11.7966 | 11.7737 | 11.7325 | 9.1095 | 110.7788 | -11.4853 | 110.7788 | 122.3602 | -0.032043 | 119.6365 | -0.009155 | 0 | 122.3236 | 122.3007 | 122.2366 | 110.7834 | 110.7788 | 122.2595 | 122.3785 | 119.6365 | 110.7834 | 110.7788 | 122.3785 | 122.2366 | 122.2595 | -11.4899 | -2.6321
947.6719 | 122.3969 | -110.6232 | 11.6364 | -0.010758 | -0.0064535 | -0.020303 | 0.018812 | -0.0070133 | -0.00872 | 0.00078828 | 0.2243 | 0.23346 | 0.20599 | 11.7416 | 11.6272 | 11.7416 | 11.6638 | 11.6867 | 11.6501 | 9.0958 | 110.8292 | -11.4029 | 110.8475 | 122.3648 | -0.009156 | 119.7189 | 0.013732 | 0.01831 | 122.287 | 122.3099 | 122.2504 | 110.8566 | 110.8475 | 122.2733 | 122.3648 | 119.7189 | 110.8566 | 110.8475 | 122.3648 | 122.2504 | 122.2733 | -11.4304 | -2.5406
948.6719 | 122.3969 | -110.3806 | 11.8835 | -0.003128 | -0.0092307 | -0.019235 | 0.016462 | -0.0055179 | -0.0065838 | -0.00092072 | 0.20142 | 0.21057 | 0.1831 | 11.9751 | 11.8652 | 11.9888 | 11.9202 | 11.9293 | 11.8607 | 9.1095 | 110.5637 | -11.673 | 110.582 | 122.3557 | -0.018311 | 119.4901 | -0.022888 | 0.018311 | 122.3007 | 122.3099 | 122.2458 | 110.5911 | 110.582 | 122.2412 | 122.3694 | 119.4901 | 110.5911 | 110.582 | 122.3694 | 122.2458 | 122.2412 | -11.7004 | -2.774
949.6719 | 122.3694 | -108.4671 | 13.8336 | -0.018387 | -0.0096579 | -0.019021 | 0.014112 | -0.0074405 | -0.0072246 | -0.00027992 | 0.21515 | 0.21973 | 0.21973 | 13.9069 | 13.8016 | 13.9343 | 13.884 | 13.8474 | 13.829 | 9.1232 | 108.6868 | -13.6139 | 108.6823 | 122.374 | -0.032043 | 117.5903 | -0.004577 | -0.004578 | 122.3511 | 122.3145 | 122.2687 | 108.6868 | 108.6823 | 122.2961 | 122.4014 | 117.5903 | 108.6868 | 108.6823 | 122.4014 | 122.2687 | 122.2961 | -13.6139 | -4.7104
950.6719 | 122.3648 | -108.4671 | 13.8565 | 0.0045015 | -0.0073081 | -0.017739 | 0.014967 | -0.0074405 | -0.007011 | 0.0010019 | 0.21057 | 0.23346 | 0.21515 | 13.9206 | 13.8153 | 13.9389 | 13.9069 | 13.8748 | 13.8245 | 9.1095 | 108.6823 | -13.623 | 108.6777 | 122.3877 | -0.041198 | 117.5766 | -0.032043 | -0.004578 | 122.374 | 122.3419 | 122.2824 | 108.7006 | 108.6777 | 122.2916 | 122.406 | 117.5766 | 108.7006 | 108.6777 | 122.406 | 122.2824 | 122.2916 | -13.6414 | -4.747
951.6719 | 122.3923 | -110.4904 | 11.7645 | -0.010758 | -0.0066673 | -0.019235 | 0.018171 | -0.0065859 | -0.005302 | -0.00049352 | 0.27466 | 0.30212 | 0.29297 | 11.8469 | 11.7279 | 11.8561 | 11.7828 | 11.8057 | 11.7233 | 9.1003 | 110.7834 | -11.4624 | 110.7651 | 122.3373 | -0.036621 | 119.5908 | -0.041198 | -0.018311 | 122.2733 | 122.2961 | 122.2183 | 110.7925 | 110.7651 | 122.2137 | 122.3465 | 119.5908 | 110.7925 | 110.7651 | 122.3465 | 122.2183 | 122.2137 | -11.4716 | -2.6642
952.6719 | 122.4014 | -109.5886 | 12.6663 | -0.003128 | -0.0066673 | -0.01603 | 0.017103 | -0.0076541 | -0.0031658 | -0.00092072 | 0.33875 | 0.35706 | 0.33875 | 12.767 | 12.6572 | 12.7625 | 12.6938 | 12.6984 | 12.648 | 9.1187 | 109.9274 | -12.3093 | 109.9274 | 122.3557 | -0.009155 | 118.7073 | -0.018311 | 0 | 122.2824 | 122.287 | 122.2458 | 109.9457 | 109.9274 | 122.2366 | 122.3511 | 118.7073 | 109.9457 | 109.9274 | 122.3511 | 122.2458 | 122.2366 | -12.3276 | -3.5477
953.6719 | 122.3785 | -109.9045 | 12.355 | -0.003128 | -0.0096579 | -0.017098 | 0.019666 | -0.0061587 | -0.0057294 | 0.00078828 | 0.28839 | 0.29755 | 0.27924 | 12.4283 | 12.3184 | 12.4512 | 12.3276 | 12.3413 | 12.3276 | 9.1232 | 110.1837 | -12.0575 | 110.1929 | 122.3328 | -0.036622 | 119.0277 | -0.027466 | 0.009155 | 122.2321 | 122.2458 | 122.2229 | 110.202 | 110.1929 | 122.2321 | 122.3557 | 119.0277 | 110.202 | 110.1929 | 122.3557 | 122.2229 | 122.2321 | -12.0758 | -3.2318
954.6719 | 122.3969 | -109.3964 | 12.854 | -0.010758 | -0.0092307 | -0.019662 | 0.017957 | -0.0076541 | -0.0061566 | 0.0016427 | 0.26093 | 0.27924 | 0.26093 | 12.9501 | 12.8357 | 12.9684 | 12.8906 | 12.9089 | 12.8357 | 9.1095 | 109.6573 | -12.5748 | 109.6573 | 122.3465 | -0.018311 | 118.5059 | -0.018311 | 0 | 122.287 | 122.3053 | 122.2321 | 109.6756 | 109.6573 | 122.2321 | 122.3648 | 118.5059 | 109.6756 | 109.6573 | 122.3648 | 122.2321 | 122.2321 | -12.5931 | -3.7445
955.6719 | 122.4289 | -109.259 | 12.941 | -0.003128 | -0.0062399 | -0.013253 | 0.017957 | -0.0078677 | -0.0040204 | 0.00078828 | 0.32044 | 0.25635 | 0.25635 | 13.1332 | 13.0005 | 13.1332 | 12.9089 | 13.0463 | 12.9456 | 9.1187 | 109.5154 | -12.6846 | 109.5795 | 122.3923 | 0.059509 | 118.3777 | 0.004578 | 0.064087 | 122.168 | 122.3053 | 122.2595 | 109.5154 | 109.5795 | 122.2046 | 122.3923 | 118.3777 | 109.5154 | 109.5795 | 122.3923 | 122.2595 | 122.2046 | -12.6846 | -3.8223
956.6719 | 122.4335 | -109.3277 | 12.8998 | -0.018387 | -0.0060263 | -0.017098 | 0.019239 | -0.0061587 | -0.0029522 | 0.00057468 | 0.23804 | 0.20599 | 0.21515 | 13.0508 | 12.9135 | 13.06 | 12.8769 | 12.9913 | 12.886 | 9.1187 | 109.5428 | -12.6938 | 109.5657 | 122.3785 | 0.013733 | 118.4463 | -0.013733 | 0.022888 | 122.2046 | 122.319 | 122.2412 | 109.5337 | 109.5657 | 122.2137 | 122.3877 | 118.4463 | 109.5337 | 109.5657 | 122.3877 | 122.2412 | 122.2137 | -12.6846 | -3.7811
957.6719 | 122.4014 | -112.9623 | 9.2743 | -0.010758 | -0.0090171 | -0.01838 | 0.01753 | -0.0085085 | -0.005943 | 0.0014291 | 0.13275 | 0.16479 | 0.15106 | 9.375 | 9.2422 | 9.3521 | 9.2789 | 9.3063 | 9.2514 | 8.6517 | 113.1134 | -9.1095 | 113.0951 | 122.3373 | -0.032043 | 121.6141 | -0.022888 | -0.018311 | 122.2412 | 122.2687 | 122.2046 | 113.1271 | 113.0951 | 122.2137 | 122.3145 | 121.6141 | 113.1271 | 113.0951 | 122.3145 | 122.2046 | 122.2137 | -9.1232 | -0.62256
958.6719 | 122.4289 | -111.8637 | 10.3775 | -0.003128 | -0.0073081 | -0.016458 | 0.019453 | -0.0082949 | -0.005302 | 0.0016427 | 0.22888 | 0.16937 | 0.17853 | 10.5103 | 10.3867 | 10.5103 | 10.3043 | 10.4416 | 10.3226 | 8.9905 | 112.0422 | -10.2081 | 112.0926 | 122.374 | 0.009156 | 120.8542 | -0.054931 | 0.050354 | 122.168 | 122.3053 | 122.2504 | 112.0331 | 112.0926 | 122.1863 | 122.374 | 120.8542 | 112.0331 | 112.0926 | 122.374 | 122.2504 | 122.1863 | -10.199 | -1.387
959.6719 | 122.4243 | -110.7971 | 11.4166 | -0.003128 | -0.0060263 | -0.014535 | 0.018598 | -0.0044497 | -0.0065838 | -0.00092072 | 0.22888 | 0.21057 | 0.21057 | 11.5677 | 11.4578 | 11.5677 | 11.4029 | 11.5219 | 11.4166 | 9.0775 | 111.0077 | -11.2061 | 111.026 | 122.3648 | 0.041199 | 119.8746 | 0 | 0.018311 | 122.2 | 122.319 | 122.2549 | 111.0077 | 111.026 | 122.2137 | 122.3648 | 119.8746 | 111.0077 | 111.026 | 122.3648 | 122.2549 | 122.2137 | -11.2061 | -2.3392
960.6719 | 122.4106 | -116.0751 | 6.1798 | -0.003128 | -0.0083763 | -0.0098351 | 0.018812 | -0.0065859 | -0.0061566 | 0.00036108 | 0.15564 | 0.1236 | 0.1236 | 6.2531 | 6.1661 | 6.2668 | 6.0974 | 6.2164 | 6.1386 | 6.0379 | 116.1987 | -6.0562 | 116.2308 | 122.3282 | -0.013733 | 122.113 | -0.041199 | 0.032044 | 122.1725 | 122.2916 | 122.2412 | 116.1987 | 116.2308 | 122.2137 | 122.3419 | 122.113 | 116.1987 | 116.2308 | 122.3419 | 122.2412 | 122.2137 | -6.0562 | -0.14191
961.6719 | 122.3557 | -116.8854 | 5.4153 | -0.010758 | -0.0066673 | -0.01304 | 0.018812 | -0.0061587 | -0.005943 | 0.00014748 | 0.073242 | 0.086975 | 0.10071 | 5.4199 | 5.3192 | 5.4245 | 5.3696 | 5.3604 | 5.3741 | 5.2872 | 116.9861 | -5.3284 | 116.9586 | 122.3053 | -0.09613 | 122.1725 | -0.041198 | -0.027466 | 122.2549 | 122.2458 | 122.2046 | 116.9724 | 116.9586 | 122.2595 | 122.3099 | 122.1725 | 116.9724 | 116.9586 | 122.3099 | 122.2046 | 122.2595 | -5.3146 | -0.12817
962.6719 | 122.4197 | -116.9312 | 5.3192 | -0.010758 | -0.0062399 | -0.019235 | 0.020948 | -0.0091495 | -0.0057294 | 0.00036108 | 0.15564 | 0.14191 | 0.13275 | 5.3741 | 5.3055 | 5.4108 | 5.2505 | 5.3604 | 5.2826 | 5.191 | 117.0639 | -5.1773 | 117.0868 | 122.3053 | -0.013733 | 122.1222 | -0.036621 | 0.022889 | 122.1817 | 122.2916 | 122.2366 | 117.0731 | 117.0868 | 122.2137 | 122.3419 | 122.1222 | 117.0731 | 117.0868 | 122.3419 | 122.2366 | 122.2137 | -5.1865 | -0.12817
963.6719 | 122.3877 | -117.0776 | 5.2002 | -0.018387 | -0.0062399 | -0.015603 | 0.018598 | -0.0067995 | -0.0050884 | 0.0012155 | 0.09613 | 0.12817 | 0.11444 | 5.1773 | 5.0949 | 5.2048 | 5.1224 | 5.1361 | 5.1727 | 5.0583 | 117.1921 | -5.072 | 117.1738 | 122.2549 | -0.10529 | 122.1359 | -0.027466 | -0.018311 | 122.2 | 122.2137 | 122.1725 | 117.2058 | 117.1738 | 122.2504 | 122.2824 | 122.1359 | 117.2058 | 117.1738 | 122.2824 | 122.1725 | 122.2504 | -5.0858 | -0.14191
964.6719 | 122.4243 | -116.7664 | 5.4794 | -0.003128 | -0.0058127 | -0.016458 | 0.021162 | -0.0057315 | -0.0061566 | 0.0031381 | 0.17853 | 0.12817 | 0.13275 | 5.5664 | 5.484 | 5.571 | 5.397 | 5.5344 | 5.4474 | 5.3558 | 116.8991 | -5.3513 | 116.9449 | 122.3328 | 0.004578 | 122.1222 | -0.032043 | 0.045777 | 122.1634 | 122.3007 | 122.2504 | 116.8945 | 116.9449 | 122.2137 | 122.3373 | 122.1222 | 116.8945 | 116.9449 | 122.3373 | 122.2504 | 122.2137 | -5.3467 | -0.1236
965.6719 | 122.3694 | -116.8396 | 5.4199 | -0.003128 | -0.0094443 | -0.019876 | 0.020948 | -0.0050907 | -0.0055156 | 0.0029245 | 0.10986 | 0.11444 | 0.11902 | 5.4245 | 5.3421 | 5.452 | 5.3604 | 5.3879 | 5.3833 | 5.2917 | 116.9586 | -5.3055 | 116.9495 | 122.2641 | -0.07782 | 122.1313 | -0.036621 | -0.009156 | 122.2 | 122.2275 | 122.1817 | 116.954 | 116.9495 | 122.2229 | 122.2916 | 122.1313 | 116.954 | 116.9495 | 122.2916 | 122.1817 | 122.2229 | -5.3009 | -0.12817
966.6719 | 122.4243 | -116.7252 | 5.5206 | -0.003128 | -0.0068809 | -0.015389 | 0.019025 | -0.0080813 | -0.0023114 | 0.0014291 | 0.11444 | 0.14191 | 0.1236 | 5.5618 | 5.4703 | 5.5939 | 5.4886 | 5.5481 | 5.4794 | 5.3925 | 116.8488 | -5.3787 | 116.8396 | 122.287 | -0.050354 | 122.1176 | -0.041199 | -0.009155 | 122.2137 | 122.2733 | 122.1954 | 116.8671 | 116.8396 | 122.2046 | 122.319 | 122.1176 | 116.8671 | 116.8396 | 122.319 | 122.1954 | 122.2046 | -5.397 | -0.12817
967.6719 | 122.3877 | -116.7343 | 5.5527 | -0.010758 | -0.0058127 | -0.020303 | 0.022657 | -0.0070133 | -0.0044476 | 0.00057468 | 0.14191 | 0.14648 | 0.13275 | 5.5344 | 5.4657 | 5.5618 | 5.4611 | 5.5115 | 5.5023 | 5.3741 | 116.8671 | -5.4062 | 116.8762 | 122.2687 | -0.086975 | 122.1085 | -0.050354 | 0.009156 | 122.1954 | 122.2458 | 122.2 | 116.8808 | 116.8762 | 122.2366 | 122.2961 | 122.1085 | 116.8808 | 116.8762 | 122.2961 | 122.2 | 122.2366 | -5.4199 | -0.17853
968.6719 | 122.3694 | -116.6931 | 5.5573 | -0.010758 | -0.0064535 | -0.013253 | 0.018384 | -0.0059451 | -0.0048748 | 0.0024973 | 0.091553 | 0.12817 | 0.09613 | 5.5298 | 5.4337 | 5.5618 | 5.5161 | 5.4932 | 5.5206 | 5.4016 | 116.7892 | -5.4291 | 116.7847 | 122.2229 | -0.1236 | 122.0947 | -0.036621 | -0.004577 | 122.2092 | 122.1863 | 122.1268 | 116.8213 | 116.7847 | 122.2137 | 122.2549 | 122.0947 | 116.8213 | 116.7847 | 122.2549 | 122.1268 | 122.2137 | -5.4611 | -0.15564
969.6719 | 122.4838 | -116.6931 | 5.5527 | -0.018387 | -0.016067 | -0.015817 | 0.014539 | -0.0093631 | -0.0057294 | 0.00014748 | 0.16479 | 0.068665 | 0.15106 | 5.6717 | 5.5939 | 5.7312 | 5.3833 | 5.6808 | 5.5252 | 5.4886 | 116.8442 | -5.484 | 116.8579 | 122.3648 | 0.041199 | 122.1817 | -0.027465 | 0.013733 | 122.0764 | 122.374 | 122.287 | 116.7618 | 116.8579 | 122.2183 | 122.4243 | 122.1817 | 116.7618 | 116.8579 | 122.4243 | 122.287 | 122.2183 | -5.4016 | -0.064087
970.6719 | 122.438 | -116.7252 | 5.5344 | -0.010758 | -0.0075217 | -0.014749 | 0.021162 | -0.010004 | -0.0061566 | 0.00014748 | 0.12817 | 0.1236 | 0.14191 | 5.603 | 5.5115 | 5.6122 | 5.4611 | 5.5847 | 5.5481 | 5.4062 | 116.8671 | -5.4108 | 116.8533 | 122.3282 | -0.022888 | 122.1313 | 0.013733 | -0.013733 | 122.1863 | 122.3099 | 122.2366 | 116.8488 | 116.8533 | 122.2733 | 122.3373 | 122.1313 | 116.8488 | 116.8533 | 122.3373 | 122.2366 | 122.2733 | -5.3925 | -0.12817
971.6719 | 122.4243 | -116.7664 | 5.4977 | -0.010758 | -0.0075217 | -0.012399 | 0.019666 | -0.0085085 | -0.0074384 | 0.0022837 | 0.09613 | 0.11902 | 0.11444 | 5.5161 | 5.4291 | 5.5435 | 5.3879 | 5.4886 | 5.4565 | 5.3696 | 116.8808 | -5.3787 | 116.8625 | 122.2824 | -0.068665 | 122.1359 | -0.041199 | -0.018311 | 122.1542 | 122.2549 | 122.1954 | 116.8854 | 116.8625 | 122.2229 | 122.3099 | 122.1359 | 116.8854 | 116.8625 | 122.3099 | 122.1954 | 122.2229 | -5.3833 | -0.12817
972.6719 | 122.4289 | -116.8121 | 5.4657 | 0.0045015 | -0.0073081 | -0.017312 | 0.019025 | -0.010431 | -0.0023114 | 0.00078828 | 0.11902 | 0.13733 | 0.10071 | 5.5161 | 5.4199 | 5.5344 | 5.4382 | 5.4977 | 5.4337 | 5.3329 | 116.9128 | -5.3284 | 116.9312 | 122.3282 | -0.045776 | 122.1451 | -0.032043 | 0.018311 | 122.2504 | 122.3099 | 122.2321 | 116.9495 | 116.9312 | 122.2458 | 122.3465 | 122.1451 | 116.9495 | 116.9312 | 122.3465 | 122.2321 | 122.2458 | -5.365 | -0.13275
973.6719 | 122.3694 | -116.7618 | 5.4932 | -0.003128 | -0.0070945 | -0.018807 | 0.020307 | -0.0074405 | -0.0061566 | -0.0011343 | 0.064087 | 0.11902 | 0.10986 | 5.5206 | 5.4199 | 5.5298 | 5.4611 | 5.4657 | 5.4886 | 5.3741 | 116.8716 | -5.3741 | 116.8259 | 122.2824 | -0.073242 | 122.1359 | -0.004578 | -0.045776 | 122.2229 | 122.2275 | 122.1817 | 116.8808 | 116.8259 | 122.2504 | 122.2916 | 122.1359 | 116.8808 | 116.8259 | 122.2916 | 122.1817 | 122.2504 | -5.3833 | -0.11902
974.6719 | 122.4747 | -116.7206 | 5.5069 | 0.0045015 | -0.013076 | -0.020944 | 0.013471 | -0.010218 | -0.0057294 | 0.0027109 | 0.09613 | 0.054932 | 0.10529 | 5.5939 | 5.5435 | 5.6625 | 5.3879 | 5.5939 | 5.4794 | 5.4245 | 116.8259 | -5.452 | 116.8167 | 122.3145 | 0.036621 | 122.1451 | -0.027466 | -0.009156 | 122.1085 | 122.3145 | 122.2641 | 116.7755 | 116.8167 | 122.2 | 122.3831 | 122.1451 | 116.7755 | 116.8167 | 122.3831 | 122.2641 | 122.2 | -5.4016 | -0.082397
975.6719 | 122.4289 | -116.7023 | 5.5435 | -0.003128 | -0.0079489 | -0.016671 | 0.022443 | -0.0097903 | -0.005302 | 0.00057468 | 0.15106 | 0.086975 | 0.10071 | 5.6625 | 5.5481 | 5.6442 | 5.452 | 5.5984 | 5.5252 | 5.4199 | 116.803 | -5.4565 | 116.8533 | 122.3648 | 0.004578 | 122.1222 | -0.01831 | 0.050354 | 122.1542 | 122.3007 | 122.2504 | 116.7892 | 116.8533 | 122.2275 | 122.3465 | 122.1222 | 116.7892 | 116.8533 | 122.3465 | 122.2504 | 122.2275 | -5.4428 | -0.1236
976.6719 | 122.438 | -116.1804 | 6.0883 | -0.010758 | -0.0090171 | -0.016885 | 0.021375 | -0.0082949 | -0.0055156 | 0.00036108 | 0.14191 | 0.10986 | 0.09613 | 6.189 | 6.0837 | 6.1752 | 6.0196 | 6.1432 | 6.0516 | 5.9509 | 116.2766 | -5.9784 | 116.3223 | 122.3694 | -0.004578 | 122.1313 | -0.036621 | 0.045777 | 122.2 | 122.3236 | 122.2641 | 116.2903 | 116.3223 | 122.2321 | 122.3557 | 122.1313 | 116.2903 | 116.3223 | 122.3557 | 122.2641 | 122.2321 | -5.9921 | -0.13733
977.6719 | 122.3969 | -117.1875 | 5.0858 | -0.018387 | -0.0075217 | -0.015176 | 0.019666 | -0.0074405 | -0.0046612 | 0.0014291 | 0.07782 | 0.10071 | 0.068665 | 5.0949 | 5.0079 | 5.1453 | 5.0262 | 5.0629 | 5.0858 | 4.9713 | 117.2562 | -4.985 | 117.2653 | 122.2824 | -0.077819 | 122.1588 | 0 | 0.009155 | 122.2137 | 122.2504 | 122.1954 | 117.2882 | 117.2653 | 122.2733 | 122.3328 | 122.1588 | 117.2882 | 117.2653 | 122.3328 | 122.1954 | 122.2733 | -5.0171 | -0.11444
978.6719 | 122.4655 | -116.7938 | 5.4016 | -0.010758 | -0.0092307 | -0.014108 | 0.018171 | -0.0074405 | -0.0044476 | 0.0010019 | 0.10071 | 0.086975 | 0.10071 | 5.4977 | 5.4108 | 5.5298 | 5.2734 | 5.4474 | 5.3925 | 5.3192 | 116.8945 | -5.3146 | 116.8945 | 122.2916 | 0.009156 | 122.113 | -0.009155 | 0 | 122.0673 | 122.2412 | 122.2046 | 116.8808 | 116.8945 | 122.1863 | 122.3236 | 122.113 | 116.8808 | 116.8945 | 122.3236 | 122.2046 | 122.1863 | -5.3009 | -0.082397
979.6719 | 122.5296 | -116.7068 | 5.4657 | -0.010758 | -0.0098715 | -0.016885 | 0.016889 | -0.0065859 | -0.0057294 | 0.0022837 | 0.17395 | 0.068665 | 0.12817 | 5.6213 | 5.5298 | 5.658 | 5.2505 | 5.6122 | 5.4153 | 5.397 | 116.835 | -5.397 | 116.8808 | 122.3282 | 0.064087 | 122.1039 | -0.050354 | 0.045776 | 121.9574 | 122.319 | 122.2366 | 116.7755 | 116.8808 | 122.1222 | 122.3648 | 122.1039 | 116.7755 | 116.8808 | 122.3648 | 122.2366 | 122.1222 | -5.3375 | -0.068664
980.6719 | 122.4472 | -116.3864 | 5.8456 | -0.010758 | -0.0066673 | -0.020944 | 0.023084 | -0.0076541 | -0.0067974 | -6.6324e-05 | 0.14648 | 0.091553 | 0.10529 | 5.9647 | 5.8502 | 5.9555 | 5.7724 | 5.9418 | 5.809 | 5.7312 | 116.4917 | -5.7541 | 116.5329 | 122.3511 | 0.004578 | 122.1176 | -0.036621 | 0.041198 | 122.1588 | 122.3282 | 122.2366 | 116.478 | 116.5329 | 122.1954 | 122.3419 | 122.1176 | 116.478 | 116.5329 | 122.3419 | 122.2366 | 122.1954 | -5.7404 | -0.11444
981.6719 | 122.3923 | -114.6698 | 7.5897 | -0.003128 | -0.0060263 | -0.015176 | 0.020734 | -0.0055179 | -0.005943 | 0.0012155 | 0.09613 | 0.1236 | 0.1236 | 7.6218 | 7.5165 | 7.6401 | 7.5348 | 7.5577 | 7.5851 | 7.37 | 114.7934 | -7.4661 | 114.7659 | 122.2916 | -0.073243 | 122.0398 | -0.004578 | -0.027466 | 122.2046 | 122.2275 | 122.1863 | 114.7934 | 114.7659 | 122.2549 | 122.3099 | 122.0398 | 114.7934 | 114.7659 | 122.3099 | 122.1863 | 122.2549 | -7.4661 | -0.21973
982.6719 | 122.4472 | -113.1958 | 9.05 | -0.010758 | -0.0064535 | -0.016885 | 0.021162 | -0.0067995 | -0.0063702 | 0.00014748 | 0.20599 | 0.17853 | 0.16937 | 9.1736 | 9.0637 | 9.1919 | 8.9951 | 9.1278 | 9.0271 | 8.5419 | 113.3652 | -8.8715 | 113.4018 | 122.3694 | 0.013733 | 121.7377 | -0.022888 | 0.036621 | 122.1909 | 122.3236 | 122.2595 | 113.3743 | 113.4018 | 122.2229 | 122.3877 | 121.7377 | 113.3743 | 113.4018 | 122.3877 | 122.2595 | 122.2229 | -8.8806 | -0.50812
983.6719 | 122.3831 | -119.2017 | 3.0487 | -0.003128 | -0.0066673 | -0.014535 | 0.02223 | -0.0053043 | -0.0048748 | 0.0016427 | 0.050354 | 0.073242 | 0.054932 | 3.035 | 2.9709 | 3.067 | 2.98 | 3.0121 | 3.0304 | 2.948 | 119.2566 | -2.9755 | 119.252 | 122.2366 | -0.07782 | 122.1497 | -0.01831 | -0.004578 | 122.1817 | 122.2137 | 122.1725 | 119.2749 | 119.252 | 122.2321 | 122.2687 | 122.1497 | 119.2749 | 119.252 | 122.2687 | 122.1725 | 122.2321 | -2.9938 | -0.10071
984.6719 | 122.4564 | -118.9224 | 3.3234 | -0.018387 | -0.0077353 | -0.015817 | 0.022871 | -0.0072269 | -0.0050884 | -6.6324e-05 | 0.1236 | 0.07782 | 0.07782 | 3.4287 | 3.3508 | 3.4287 | 3.2318 | 3.4012 | 3.3051 | 3.2364 | 119.0002 | -3.2455 | 119.046 | 122.3511 | 0.027466 | 122.1588 | -0.01831 | 0.045776 | 122.1542 | 122.3236 | 122.2733 | 119.0002 | 119.046 | 122.2275 | 122.3511 | 122.1588 | 119.0002 | 119.046 | 122.3511 | 122.2733 | 122.2275 | -3.2455 | -0.086975
985.6719 | 122.3969 | -118.8034 | 3.4836 | -0.010758 | -0.0066673 | -0.016458 | 0.019666 | -0.0087223 | -0.0050884 | 0.0022837 | 0.022888 | 0.027466 | 0.009155 | 3.447 | 3.3737 | 3.4927 | 3.4058 | 3.4103 | 3.4332 | 3.3279 | 118.8126 | -3.4561 | 118.8263 | 122.2504 | -0.10986 | 122.1313 | -0.050354 | 0.013733 | 122.2092 | 122.2137 | 122.1771 | 118.8309 | 118.8263 | 122.2366 | 122.2961 | 122.1313 | 118.8309 | 118.8263 | 122.2961 | 122.1771 | 122.2366 | -3.4744 | -0.15564
986.6719 | 122.3923 | -119.6823 | 2.5955 | -0.018387 | -0.0073081 | -0.016244 | 0.021162 | -0.0085085 | -0.0031658 | 0.0010019 | 0.041199 | 0.073242 | 0.054932 | 2.5635 | 2.5131 | 2.6047 | 2.5314 | 2.5543 | 2.5406 | 2.4811 | 119.7372 | -2.5223 | 119.7235 | 122.2458 | -0.082397 | 122.1634 | -0.054932 | -0.013733 | 122.2137 | 122.2366 | 122.1954 | 119.7556 | 119.7235 | 122.2229 | 122.287 | 122.1634 | 119.7556 | 119.7235 | 122.287 | 122.1954 | 122.2229 | -2.5406 | -0.11444
987.6719 | 122.4014 | -119.8517 | 2.4399 | -0.003128 | -0.0060263 | -0.012826 | 0.021802 | -0.0059451 | -0.007011 | 0.0012155 | 0.054932 | 0.073242 | 0.068665 | 2.4307 | 2.3758 | 2.449 | 2.3712 | 2.3895 | 2.4216 | 2.3392 | 119.9203 | -2.3666 | 119.9066 | 122.2824 | -0.064087 | 122.1909 | -0.01831 | -0.013733 | 122.2229 | 122.2412 | 122.2275 | 119.9249 | 119.9066 | 122.2733 | 122.3007 | 122.1909 | 119.9249 | 119.9066 | 122.3007 | 122.2275 | 122.2733 | -2.3712 | -0.10071
988.6719 | 122.4014 | -119.2795 | 3.0167 | -0.010758 | -0.0045309 | -0.014108 | 0.020307 | -0.0059451 | -0.003593 | -0.00027992 | 0.050354 | 0.10529 | 0.064087 | 2.9892 | 2.9297 | 3.0167 | 2.9388 | 2.948 | 2.9892 | 2.8885 | 119.3436 | -2.9114 | 119.3298 | 122.2687 | -0.086976 | 122.168 | -0.027466 | -0.013733 | 122.2183 | 122.2275 | 122.2092 | 119.3848 | 119.3298 | 122.2687 | 122.2961 | 122.168 | 119.3848 | 119.3298 | 122.2961 | 122.2092 | 122.2687 | -2.9526 | -0.12817
989.6719 | 122.438 | -119.2337 | 3.0121 | -0.010758 | -0.0085899 | -0.017739 | 0.020307 | -0.0061587 | -0.0050884 | 0.0029245 | 0.059509 | 0.068665 | 0.073242 | 3.0121 | 2.9663 | 3.067 | 2.8885 | 2.9892 | 2.9938 | 2.9114 | 119.3069 | -2.9434 | 119.2932 | 122.2458 | -0.045776 | 122.1451 | -0.018311 | -0.013733 | 122.1222 | 122.2229 | 122.2 | 119.3024 | 119.2932 | 122.2275 | 122.3007 | 122.1451 | 119.3024 | 119.2932 | 122.3007 | 122.2 | 122.2275 | -2.9388 | -0.10071
990.6719 | 122.438 | -119.8471 | 2.4216 | -0.010758 | -0.0079489 | -0.012826 | 0.021802 | -0.0061587 | -0.0038068 | 0.00057468 | 0.1236 | 0.064087 | 0.054932 | 2.4673 | 2.3987 | 2.4857 | 2.3254 | 2.4445 | 2.3758 | 2.33 | 119.902 | -2.3575 | 119.9707 | 122.3145 | -0.022888 | 122.1771 | -0.045777 | 0.068664 | 122.1725 | 122.2916 | 122.2458 | 119.9112 | 119.9707 | 122.2229 | 122.3328 | 122.1771 | 119.9112 | 119.9707 | 122.3328 | 122.2458 | 122.2229 | -2.3666 | -0.091553
991.6719 | 122.3969 | -120.0439 | 2.2842 | 0.0045015 | -0.0062399 | -0.012399 | 0.020521 | -0.0053043 | -0.0033794 | 0.0022837 | 0.059509 | 0.07782 | 0.041199 | 2.2614 | 2.2064 | 2.2797 | 2.1973 | 2.2339 | 2.2385 | 2.1652 | 120.0851 | -2.2064 | 120.1035 | 122.3053 | -0.07782 | 122.2092 | -0.045777 | 0.01831 | 122.2412 | 122.2778 | 122.2504 | 120.1218 | 120.1035 | 122.2824 | 122.3236 | 122.2092 | 120.1218 | 120.1035 | 122.3236 | 122.2504 | 122.2824 | -2.243 | -0.11902
992.6719 | 122.438 | -120.0256 | 2.243 | -0.003128 | -0.0047447 | -0.013894 | 0.02223 | -0.0078677 | -0.0044476 | 0.0016427 | 0.11444 | 0.054932 | 0.073242 | 2.2934 | 2.2339 | 2.3163 | 2.1469 | 2.2934 | 2.2293 | 2.1652 | 120.0989 | -2.1881 | 120.1401 | 122.319 | -0.009155 | 122.1909 | -0.013733 | 0.041199 | 122.1725 | 122.319 | 122.2595 | 120.0806 | 120.1401 | 122.2549 | 122.3419 | 122.1909 | 120.0806 | 120.1401 | 122.3419 | 122.2595 | 122.2549 | -2.1698 | -0.07782
993.6719 | 122.5067 | -119.9249 | 2.33 | -0.010758 | -0.0096579 | -0.020516 | 0.018384 | -0.0074405 | -0.0038068 | 0.0010019 | 0.086975 | 0.036621 | 0.07782 | 2.4033 | 2.3529 | 2.4765 | 2.1423 | 2.4033 | 2.2888 | 2.2751 | 120.0027 | -2.2934 | 120.0119 | 122.3282 | 0.022888 | 122.2 | -0.041199 | 0.009155 | 122.0673 | 122.3282 | 122.2778 | 119.9615 | 120.0119 | 122.2137 | 122.4014 | 122.2 | 119.9615 | 120.0119 | 122.4014 | 122.2778 | 122.2137 | -2.2522 | -0.054932
994.6719 | 122.3923 | -120.2454 | 2.0737 | -0.010758 | -0.0062399 | -0.019876 | 0.021802 | -0.0085085 | -0.0040204 | 0.0022837 | 0.032043 | 0.054932 | 0.032043 | 2.0233 | 1.9821 | 2.0782 | 1.9958 | 2.0187 | 2.0416 | 1.9455 | 120.2774 | -2.0187 | 120.2774 | 122.2687 | -0.091552 | 122.1909 | -0.032043 | 0 | 122.2412 | 122.2641 | 122.2275 | 120.3003 | 120.2774 | 122.287 | 122.3236 | 122.1909 | 120.3003 | 120.2774 | 122.3236 | 122.2275 | 122.287 | -2.0416 | -0.12817
995.6719 | 122.3877 | -120.1904 | 2.1011 | -0.010758 | -0.0058127 | -0.016885 | 0.021375 | -0.0067995 | -0.0038068 | 0.0016427 | 0.036621 | 0.050354 | 0.050354 | 2.0599 | 2.0233 | 2.0874 | 2.0462 | 2.0416 | 2.0554 | 1.9913 | 120.2408 | -2.0508 | 120.2271 | 122.2504 | -0.07782 | 122.1817 | -0.045776 | -0.013733 | 122.2366 | 122.2321 | 122.2137 | 120.2408 | 120.2271 | 122.2458 | 122.2778 | 122.1817 | 120.2408 | 120.2271 | 122.2778 | 122.2137 | 122.2458 | -2.0508 | -0.10986
996.6719 | 122.4289 | -119.751 | 2.4994 | -0.003128 | -0.0058127 | -0.014962 | 0.020093 | -0.0078677 | -0.0020978 | 0.00057468 | 0.091553 | 0.082397 | 0.073242 | 2.536 | 2.4765 | 2.5635 | 2.4124 | 2.5223 | 2.4765 | 2.4261 | 119.8242 | -2.417 | 119.8425 | 122.287 | -0.022889 | 122.1771 | -0.022889 | 0.018311 | 122.1634 | 122.2733 | 122.2275 | 119.8334 | 119.8425 | 122.2275 | 122.3145 | 122.1771 | 119.8334 | 119.8425 | 122.3145 | 122.2275 | 122.2275 | -2.4261 | -0.073243
997.6719 | 122.5296 | -120.1447 | 2.0599 | -0.003128 | -0.0088035 | -0.015817 | 0.017957 | -0.0080813 | -0.0055156 | 0.0031381 | 0.10529 | 0.022888 | 0.073242 | 2.1835 | 2.1423 | 2.2339 | 1.8814 | 2.1881 | 2.037 | 2.0462 | 120.2179 | -2.037 | 120.2499 | 122.3282 | 0.082397 | 122.1909 | -0.022889 | 0.032044 | 122.0261 | 122.3328 | 122.287 | 120.1675 | 120.2499 | 122.1817 | 122.3785 | 122.1909 | 120.1675 | 120.2499 | 122.3785 | 122.287 | 122.1817 | -1.9867 | -0.013733
998.6719 | 122.4243 | -120.5704 | 1.7532 | -0.003128 | -0.0085899 | -0.014962 | 0.021802 | -0.0074405 | -0.0061566 | 0.0010019 | 0.036621 | 0.045776 | 0.041199 | 1.7487 | 1.6846 | 1.7853 | 1.6663 | 1.7075 | 1.7303 | 1.6617 | 120.6116 | -1.7075 | 120.607 | 122.319 | -0.068665 | 122.2321 | -0.022888 | -0.004578 | 122.2366 | 122.2778 | 122.2549 | 120.6162 | 120.607 | 122.3007 | 122.3557 | 122.2321 | 120.6162 | 120.607 | 122.3557 | 122.2549 | 122.3007 | -1.712 | -0.091553
999.6719 | 122.406 | -120.5017 | 1.7761 | 0.0045015 | -0.0062399 | -0.018594 | 0.023298 | -0.0080813 | -0.0061566 | 0.0012155 | 0.064087 | 0.050354 | 0.059509 | 1.7853 | 1.7349 | 1.7899 | 1.6937 | 1.767 | 1.7578 | 1.6754 | 120.5612 | -1.7258 | 120.5658 | 122.287 | -0.041199 | 122.1771 | -0.018311 | 0.004578 | 122.1954 | 122.2687 | 122.2366 | 120.5521 | 120.5658 | 122.2595 | 122.2916 | 122.1771 | 120.5521 | 120.5658 | 122.2916 | 122.2366 | 122.2595 | -1.7166 | -0.10071
1000.6719 | 122.4792 | -120.1172 | 2.1423 | -0.010758 | -0.0075217 | -0.018167 | 0.01988 | -0.0082949 | -0.0029522 | 0.0012155 | 0.10529 | 0.054932 | 0.073242 | 2.2156 | 2.1286 | 2.2247 | 2.0416 | 2.211 | 2.092 | 2.0416 | 120.1904 | -2.0874 | 120.2225 | 122.3328 | -0.013733 | 122.1588 | -0.050354 | 0.032044 | 122.1588 | 122.3282 | 122.2458 | 120.1721 | 120.2225 | 122.2092 | 122.3419 | 122.1588 | 120.1721 | 120.2225 | 122.3419 | 122.2458 | 122.2092 | -2.0691 | -0.10071
1001.6719 | 122.4197 | -120.401 | 1.9043 | -0.003128 | -0.0073081 | -0.016458 | 0.018812 | -0.0070133 | -0.0063702 | 0.0012155 | 0.036621 | 0.073242 | 0.045776 | 1.8768 | 1.8219 | 1.9272 | 1.8356 | 1.8448 | 1.8677 | 1.8082 | 120.4468 | -1.8311 | 120.4376 | 122.2778 | -0.082398 | 122.2092 | -0.036621 | -0.009155 | 122.2366 | 122.2458 | 122.2229 | 120.4742 | 120.4376 | 122.2687 | 122.3282 | 122.2092 | 120.4742 | 120.4376 | 122.3282 | 122.2229 | 122.2687 | -1.8585 | -0.09613
1002.6719 | 122.406 | -120.4971 | 1.799 | -0.010758 | -0.0083763 | -0.014535 | 0.017316 | -0.0078677 | -0.0012432 | -6.6324e-05 | 0.022888 | 0.064087 | 0.041199 | 1.7761 | 1.7258 | 1.8036 | 1.7303 | 1.7441 | 1.7395 | 1.6754 | 120.5383 | -1.7349 | 120.52 | 122.2733 | -0.073242 | 122.1725 | -0.059509 | -0.018311 | 122.2275 | 122.2412 | 122.2229 | 120.5612 | 120.52 | 122.2366 | 122.3007 | 122.1725 | 120.5612 | 120.52 | 122.3007 | 122.2229 | 122.2366 | -1.7578 | -0.1236
1003.6719 | 122.4884 | -119.577 | 2.7008 | -0.003128 | -0.0090171 | -0.016671 | 0.01988 | -0.0065859 | -0.0046612 | 0.0027109 | 0.059509 | 0.073242 | 0.059509 | 2.7557 | 2.6917 | 2.8015 | 2.5452 | 2.742 | 2.6642 | 2.6413 | 119.6365 | -2.6276 | 119.6365 | 122.3328 | -0.009156 | 122.2183 | -0.036621 | 0 | 122.1222 | 122.319 | 122.2687 | 119.6503 | 119.6365 | 122.2412 | 122.3785 | 122.2183 | 119.6503 | 119.6365 | 122.3785 | 122.2687 | 122.2412 | -2.6413 | -0.05951
1004.6719 | 122.4747 | -118.1808 | 4.0787 | -0.010758 | -0.0060263 | -0.015817 | 0.020307 | -0.0059451 | -0.0044476 | 0.0012155 | 0.12817 | 0.073242 | 0.086975 | 4.1611 | 4.0833 | 4.1748 | 3.9825 | 4.1565 | 4.0649 | 3.9871 | 118.2678 | -4.0054 | 118.309 | 122.3419 | 0.004578 | 122.168 | -0.013733 | 0.041199 | 122.1634 | 122.3373 | 122.2641 | 118.2541 | 118.309 | 122.2458 | 122.3557 | 122.168 | 118.2541 | 118.309 | 122.3557 | 122.2641 | 122.2458 | -3.9917 | -0.091552
1005.6719 | 122.4472 | -118.428 | 3.8589 | -0.003128 | -0.0047447 | -0.014962 | 0.019025 | -0.0059451 | -0.0055156 | 0.00014748 | 0.11902 | 0.068665 | 0.073242 | 3.9047 | 3.8315 | 3.9185 | 3.7628 | 3.8773 | 3.8315 | 3.7582 | 118.5013 | -3.7903 | 118.5471 | 122.3328 | -0.027466 | 122.1863 | -0.027466 | 0.045777 | 122.1909 | 122.3053 | 122.2595 | 118.4967 | 118.5471 | 122.2595 | 122.3465 | 122.1863 | 118.4967 | 118.5471 | 122.3465 | 122.2595 | 122.2595 | -3.7857 | -0.10071

## Thermal Data
Fire Time | B Position - Middle
-0.6365 | 9.8935
0.3635 | 10.5009
1.3635 | 11.9398
2.3635 | 13.9534
3.3635 | 16.5473
4.3635 | 20.6529
5.3635 | 26.9561
6.3635 | 33.4413
7.3635 | 37.3199
8.3635 | 39.9198
9.3635 | 43.7411
10.3635 | 46.8904
11.3635 | 48.8062
12.3635 | 49.3031
13.3948 | 49.9696
14.5823 | 50.9708
15.7542 | 53.526
16.4729 | 54.218
17.4417 | 56.3826
18.4104 | 57.9066
19.3792 | 61.6615
20.3792 | 65.875
21.3635 | 73.5937
22.3635 | 73.4478
23.3635 | 80.0657
24.3635 | 81.114
25.3635 | 85.0322
26.3792 | 86.133
27.3792 | 92.6196
28.3635 | 94.0351
29.3635 | 98.3553
30.3635 | 99.8819
31.3635 | 100.1759
32.3635 | 98.8797
33.3635 | 98.2147
34.3635 | 96.2749
35.3635 | 94.5775
36.3635 | 95.9654
37.3635 | 94.779
38.3635 | 93.7302
39.3635 | 91.9807
40.3635 | 91.82
41.3635 | 89.1677
42.3635 | 87.4228
43.3635 | 82.8088
44.3635 | 79.6294
45.3635 | 78.3541
46.3792 | 77.0912
47.3635 | 74.3542
48.3635 | 72.0079
49.3635 | 70.4782
50.3635 | 68.6378
51.3635 | 67.2272
52.3635 | 65.6347
53.3635 | 64.764
54.3635 | 63.5282
55.3635 | 62.5093
56.3635 | 61.5935
57.3635 | 60.0879
58.3635 | 58.3894
59.3792 | 58.2939
60.3635 | 57.9251
61.3792 | 57.209
62.3635 | 57.2905
63.3792 | 56.5411
64.3635 | 57.4465
65.3635 | 57.7704
66.3635 | 56.3344
67.3635 | 54.6828
68.3635 | 53.6619
69.3635 | 53.4899
70.3635 | 53.0323
71.3635 | 53.7585
72.3635 | 52.767
73.3635 | 52.7255
74.3792 | 51.9248
75.3635 | 51.169
76.3635 | 51.5041
77.3635 | 51.5423
78.3635 | 50.6005
79.3635 | 50.0885
80.3635 | 49.5382
81.3635 | 49.1178
82.3635 | 49.1371
83.3635 | 48.4452
84.3635 | 47.953
85.3635 | 47.9764
86.3635 | 47.4142
87.3635 | 46.8662
88.3792 | 46.3383
89.3635 | 45.8081
90.3635 | 46.7534
91.3635 | 46.7204
92.3635 | 46.4907
93.3635 | 46.4939
94.3635 | 46.0992
95.3635 | 46.5215
96.3635 | 47.6157
97.3635 | 47.1913
98.3635 | 48.5487
99.3635 | 48.4104
100.3635 | 48.7313
101.3635 | 49.9469
102.3635 | 50.4361
103.3635 | 50.7338
104.3635 | 51.214
105.3635 | 50.5597
106.3635 | 50.1761
107.3635 | 50.2251
108.3635 | 49.9397
109.3635 | 50.2108
110.3635 | 50.5294
111.3635 | 50.8512
112.3635 | 51.0734
113.3635 | 50.7347
114.3635 | 50.905
115.3635 | 51.9783
116.3635 | 51.6563
117.3635 | 51.8454
118.3635 | 55.465
119.3635 | 55.8045
120.3635 | 57.2676
121.3792 | 56.5568
122.3635 | 55.4454
123.3635 | 55.5504
124.3635 | 56.0609
125.3635 | 55.6931
126.3635 | 54.9965
127.3635 | 54.1961
128.3792 | 53.9591
129.3792 | 54.0013
130.3792 | 53.5251
131.3635 | 52.6872
132.3792 | 52.5517
133.3792 | 51.6312
134.3635 | 51.1058
135.3635 | 50.2288
136.3635 | 50.1163
137.3635 | 50.4236
138.3792 | 50.1088
139.3635 | 49.5543
140.3635 | 49.4599
141.3635 | 50.4511
142.3635 | 50.879
143.3635 | 50.9357
144.3635 | 50.7143
145.3635 | 50.6212
146.3635 | 51.9163
147.3635 | 54.0602
148.3635 | 53.2707
149.3635 | 52.855
150.3635 | 52.4086
151.3635 | 52.4421
152.3635 | 52.2766
153.3635 | 54.4839
154.3635 | 55.5659
155.3635 | 54.8296
156.3635 | 54.6551
157.3635 | 53.6574
158.3635 | 52.8514
159.3635 | 51.8626
160.3635 | 51.7748
161.3635 | 51.2564
162.3792 | 50.6403
163.3948 | 50.5675
164.3948 | 50.3898
165.3792 | 49.871
166.3948 | 49.5713
167.3792 | 49.2629
168.3635 | 49.2789
169.3792 | 49.9895
170.3792 | 49.4813
171.3792 | 50.3266
172.3792 | 50.3133
173.3635 | 51.7016
174.3635 | 51.8665
175.3635 | 52.2429
176.3635 | 52.5478
177.3635 | 53.5404
178.3635 | 53.2752
179.3635 | 53.2846
180.3635 | 52.3905
181.3792 | 52.1798
182.3635 | 51.4196
183.3635 | 51.7727
184.3635 | 51.8476
185.3635 | 52.4412
186.3635 | 52.8805
187.3635 | 53.4496
188.3792 | 53.0669
189.3635 | 53.0665
190.3635 | 53.2048
191.3635 | 53.2721
192.3635 | 53.8217
193.3635 | 54.2922
194.3635 | 54.1744
195.3635 | 53.8468
196.3635 | 53.9691
197.3635 | 54.4134
198.3792 | 54.9157
199.4104 | 55.7975
200.3792 | 56.0981
201.3792 | 55.869
202.3792 | 56.912
203.3792 | 56.9726
204.3635 | 57.7626
205.3635 | 58.7953
206.3635 | 59.1812
207.3635 | 59.6909
208.3635 | 59.1036
209.3635 | 59.4212
210.3635 | 59.6493
211.3635 | 61.1835
212.3635 | 61.6987
213.3635 | 61.5047
214.3635 | 62.2796
215.3635 | 61.778
216.3635 | 61.7268
217.3635 | 61.2905
218.3635 | 62.5665
219.3635 | 63.9305
220.3635 | 65.2916
221.3635 | 65.094
222.3635 | 64.5195
223.3635 | 64.7407
224.3635 | 65.236
225.3635 | 64.5813
226.3635 | 64.8166
227.3635 | 66.051
228.3635 | 65.8282
229.3635 | 64.8133
230.3635 | 65.1905
231.3635 | 64.9535
232.3635 | 64.3257
233.3635 | 66.1867
234.3635 | 65.547
235.3635 | 65.1784
236.3635 | 65.3462
237.3635 | 65.2713
238.3635 | 65.9156
239.3635 | 65.3837
240.3635 | 67.0493
241.3792 | 66.8535
242.3635 | 68.7231
243.3635 | 71.8947
244.3635 | 75.1022
245.3635 | 73.868
246.3635 | 72.7113
247.3635 | 72.2952
248.3635 | 71.4843
249.3635 | 71.7221
250.3635 | 71.4896
251.3635 | 74.1525
252.3635 | 73.3663
253.3635 | 73.6174
254.3635 | 73.2828
255.3635 | 72.6326
256.3635 | 73.5179
257.3635 | 75.0064
258.3635 | 74.8615
259.3635 | 74.1686
260.3635 | 73.9858
261.3635 | 73.7823
262.3635 | 73.0307
263.3635 | 74.4456
264.3635 | 76.2063
265.3635 | 77.6588
266.3635 | 78.1576
267.3635 | 77.8562
268.3635 | 79.4991
269.3635 | 79.999
270.3948 | 79.3704
271.3635 | 78.6734
272.3635 | 79.6647
273.3635 | 79.152
274.3635 | 78.2281
275.3635 | 79.3729
276.3635 | 78.2068
277.3635 | 77.5134
278.3635 | 77.1576
279.3635 | 76.4254
280.3635 | 78.7766
281.3635 | 78.5822
282.3635 | 78.8419
283.3792 | 79.0212
284.3635 | 78.0369
285.3635 | 77.8912
286.3635 | 79.7596
287.3635 | 79.4448
288.3792 | 79.4752
289.3792 | 79.3291
290.3635 | 79.0874
291.3635 | 78.9735
292.3635 | 78.552
293.3635 | 78.7144
294.3635 | 78.528
295.3635 | 79.0587
296.3635 | 79.2018
297.3635 | 82.4706
298.3635 | 83.3396
299.3635 | 85.1532
300.3635 | 84.5572
301.3792 | 84.7609
302.3635 | 84.4877
303.3792 | 84.1144
304.3792 | 85.8062
305.3635 | 86.5229
306.3635 | 86.3687
307.3635 | 85.7554
308.3635 | 86.444
309.3635 | 86.0293
310.3635 | 89.3846
311.3635 | 89.5372
312.3635 | 92.3737
313.3635 | 90.5855
314.3635 | 89.8848
315.3635 | 89.3242
316.3635 | 89.5076
317.3635 | 91.364
318.3635 | 90.2798
319.3635 | 89.6081
320.3635 | 89.8688
321.3635 | 90.8289
322.3635 | 89.3011
323.3635 | 89.2803
324.3635 | 88.7642
325.3635 | 89.5681
326.3635 | 88.4265
327.3635 | 91.3709
328.3635 | 90.335
329.3635 | 90.8269
330.3635 | 92.728
331.3635 | 92.4852
332.3635 | 92.6918
333.3635 | 96.7314
334.3635 | 96.8595
335.3635 | 98.2008
336.3635 | 97.3824
337.3635 | 96.4297
338.3635 | 96.4877
339.3635 | 96.2783
340.3635 | 95.9427
341.3635 | 94.979
342.3635 | 94.454
343.3635 | 95.5372
344.3635 | 96.6318
345.3635 | 97.4827
346.3635 | 98.1104
347.3635 | 97.9397
348.3635 | 97.5165
349.3635 | 98.5533
350.3635 | 99.5317
351.3635 | 100.1062
352.3635 | 98.7639
353.3792 | 98.3666
354.3635 | 98.8954
355.3635 | 99.3031
356.3635 | 100.2248
357.3635 | 101.557
358.3635 | 100.9878
359.3635 | 100.0682
360.3635 | 103.1916
361.3792 | 103.7118
362.3635 | 102.8904
363.3635 | 103.3433
364.3635 | 105.4504
365.3635 | 109.8932
366.3635 | 109.926
367.3635 | 109.2138
368.3792 | 108.9181
369.3635 | 110.7675
370.3635 | 109.2507
371.3635 | 107.8309
372.3635 | 109.1882
373.3635 | 109.8657
374.3635 | 108.8273
375.3635 | 109.8779
376.3635 | 110.17
377.3635 | 110.0406
378.3635 | 107.8904
379.3635 | 104.9716
380.3635 | 103.6901
381.3635 | 102.5303
382.3635 | 103.4875
383.3635 | 106.1446
384.3635 | 104.0557
385.3635 | 105.8129
386.3635 | 104.778
387.3635 | 103.9419
388.3635 | 105.1551
389.3635 | 105.242
390.3635 | 103.1566
391.3635 | 104.8512
392.3635 | 104.4976
393.3635 | 108.0735
394.3635 | 109.4608
395.3635 | 108.2091
396.3635 | 109.7799
397.3635 | 108.9218
398.3635 | 106.6434
399.3635 | 105.6168
400.3635 | 103.2237
401.3635 | 103.2032
402.3635 | 102.478
403.3635 | 101.0154
404.3635 | 100.5455
405.3635 | 101.1263
406.3635 | 101.3588
407.3635 | 100.7139
408.3635 | 100.2879
409.3635 | 99.394
410.3635 | 98.9235
411.3635 | 97.2099
412.3635 | 95.6168
413.3635 | 94.8587
414.3635 | 93.8552
415.3635 | 94.0187
416.3635 | 94.501
417.3635 | 96.4392
418.3635 | 98.957
419.3635 | 99.6402
420.3635 | 99.5891
421.3792 | 98.1645
422.3635 | 98.2156
423.3635 | 99.2781
424.3635 | 97.9971
425.3635 | 96.8198
426.3635 | 95.6894
427.3635 | 94.5651
428.3635 | 95.7164
429.3635 | 97.6557
430.3635 | 95.6906
431.3635 | 94.948
432.3635 | 95.9039
433.3635 | 96.9928
434.3635 | 95.1172
435.3635 | 94.2759
436.3635 | 93.8103
437.3635 | 94.9732
438.3792 | 94.1001
439.3635 | 94.2966
440.3635 | 94.4457
441.3635 | 93.6086
442.3635 | 93.6738
443.3635 | 94.4859
444.3635 | 94.2972
445.3635 | 93.7243
446.3635 | 94.0217
447.3635 | 93.1891
448.3635 | 92.7927
449.3635 | 92.435
450.3635 | 91.8072
451.3635 | 90.7714
452.3635 | 90.3547
453.3792 | 91.2324
454.3635 | 91.0693
455.3635 | 90.9059
456.3635 | 91.5694
457.3635 | 92.9714
458.3635 | 94.204
459.3635 | 93.6921
460.3635 | 94.512
461.3635 | 94.3169
462.3635 | 93.0421
463.3635 | 94.3222
464.3635 | 94.6273
465.3635 | 92.8468
466.3635 | 92.2077
467.3635 | 93.824
468.3635 | 94.692
469.3635 | 94.9796
470.3635 | 94.0706
471.3635 | 94.2028
472.3635 | 93.5976
473.3635 | 94.2847
474.3635 | 95.5968
475.3635 | 96.046
476.3635 | 95.3312
477.3635 | 97.1529
478.3635 | 97.1859
479.3635 | 97.0945
480.3635 | 98.5817
481.3792 | 99.8351
482.3635 | 103.3756
483.3635 | 104.2372
484.3635 | 103.648
485.3635 | 102.3601
486.3635 | 102.2415
487.3635 | 101.1513
488.3635 | 103.4469
489.3635 | 103.8972
490.3635 | 103.3423
491.3635 | 103.004
492.3635 | 104.3947
493.3635 | 105.126
494.3635 | 105.8978
495.3635 | 106.8986
496.3635 | 107.6332
497.3635 | 107.5454
498.3635 | 106.512
499.3635 | 105.1218
500.3635 | 104.5504
501.3635 | 103.7567
502.3635 | 102.8118
503.3635 | 103.6939
504.3635 | 107.1455
505.3635 | 108.7962
506.3635 | 108.239
507.3635 | 107.2148
508.3635 | 106.5735
509.3635 | 107.4172
510.3635 | 106.6401
511.3635 | 106.1071
512.3635 | 107.6029
513.3635 | 106.6074
514.3635 | 106.8566
515.3635 | 105.6354
516.3635 | 105.6059
517.3635 | 107.3126
518.3635 | 108.6395
519.3635 | 108.6166
520.3635 | 108.9502
521.3635 | 109.7208
522.3635 | 109.8726
523.3635 | 109.7506
524.3635 | 110.9408
525.3635 | 110.6171
526.3635 | 110.681
527.3635 | 110.657
528.3792 | 109.31
529.3635 | 108.8978
530.3635 | 108.1977
531.3635 | 108.6193
532.3635 | 109.3229
533.3635 | 110.7337
534.3635 | 110.0132
535.3635 | 109.8097
536.3635 | 110.9232
537.3635 | 111.64
538.3635 | 113.9053
539.3635 | 113.8846
540.3635 | 113.8126
541.3792 | 112.8804
542.3635 | 113.5174
543.3635 | 114.4425
544.3635 | 113.2736
545.3635 | 113.2892
546.3635 | 112.1713
547.3635 | 112.2962
548.3635 | 112.3604
549.3635 | 112.581
550.3635 | 113.4653
551.3635 | 113.5336
552.3635 | 113.6847
553.3635 | 117.7781
554.3635 | 120.0584
555.3635 | 119.1976
556.3635 | 119.1225
557.3635 | 119.5892
558.3635 | 117.42
559.3635 | 116.1803
560.3635 | 117.5201
561.3635 | 118.4761
562.3635 | 120.0001
563.3635 | 118.4553
564.3635 | 118.4691
565.3635 | 118.3496
566.3635 | 119.551
567.3635 | 122.2527
568.3635 | 122.9347
569.3635 | 122.7398
570.3635 | 123.3764
571.3635 | 122.5571
572.3635 | 123.1439
573.3635 | 121.7868
574.3635 | 121.7603
575.3635 | 121.6394
576.3635 | 122.8397
577.3635 | 124.4615
578.3792 | 127.0577
579.3635 | 128.0091
580.3635 | 128.3585
581.3635 | 127.855
582.3635 | 126.1221
583.3635 | 125.1818
584.3635 | 126.9713
585.3635 | 126.2327
586.3635 | 126.3324
587.3635 | 124.7772
588.3635 | 124.1734
589.3635 | 126.1146
590.3635 | 125.3249
591.3792 | 123.9687
592.3635 | 123.2064
593.3635 | 123.6743
594.3635 | 123.3689
595.3635 | 124.071
596.3635 | 123.0763
597.3635 | 122.3298
598.3635 | 123.1058
599.3635 | 123.8413
600.3635 | 122.4986
601.3635 | 121.3234
602.3635 | 121.3682
603.3792 | 120.9696
604.3635 | 122.1985
605.3635 | 122.3668
606.3635 | 123.6426
607.3635 | 123.5787
608.3635 | 124.1122
609.3635 | 124.8589
610.3635 | 123.8598
611.3792 | 123.1977
612.3635 | 123.6934
613.3635 | 124.8319
614.3635 | 125.6225
615.3635 | 125.1106
616.3635 | 124.0156
617.3635 | 122.7528
618.3635 | 123.4763
619.3635 | 123.7913
620.3635 | 122.8077
621.3635 | 121.2173
622.3635 | 119.5887
623.3635 | 118.882
624.3635 | 120.6826
625.3635 | 121.7106
626.3635 | 122.7384
627.3635 | 122.6116
628.3792 | 123.1381
629.3635 | 122.5571
630.3635 | 121.6552
631.3635 | 121.771
632.3635 | 121.36
633.3635 | 121.044
634.3948 | 121.9434
635.3635 | 122.1207
636.3635 | 122.2788
637.3635 | 122.4598
638.3635 | 124.1261
639.3635 | 124.3398
640.3635 | 123.0041
641.3635 | 122.6312
642.3635 | 121.6323
643.3792 | 123.7089
644.3635 | 122.041
645.3635 | 123.5368
646.3635 | 123.4396
647.3635 | 123.683
648.3635 | 123.0621
649.3635 | 122.0213
650.3635 | 122.5624
651.3635 | 121.1182
652.3635 | 119.2705
653.3635 | 119.4762
654.3635 | 119.9605
655.3635 | 119.297
656.3635 | 119.5366
657.3635 | 118.6293
658.3635 | 118.1063
659.3635 | 119.3954
660.3635 | 121.6926
661.3635 | 122.5729
662.3635 | 125.2082
663.3635 | 125.224
664.3635 | 125.3526
665.3635 | 125.8804
666.3635 | 125.7554
667.3635 | 124.9442
668.3635 | 124.3934
669.3635 | 124.3751
670.3635 | 124.1992
671.3635 | 123.1583
672.3635 | 125.8126
673.3635 | 126.9693
674.3635 | 126.3533
675.3635 | 126.8891
676.3635 | 127.7075
677.3635 | 125.259
678.3635 | 123.8042
679.3635 | 124.9152
680.3635 | 124.1531
681.3635 | 123.0273
682.3635 | 122.6473
683.3635 | 121.1726
684.3635 | 120.7162
685.3635 | 119.4888
686.3635 | 119.3617
687.3635 | 118.263
688.3635 | 119.0033
689.3635 | 120.9565
690.3635 | 120.8071
691.3635 | 121.9132
692.3635 | 122.2175
693.3635 | 122.1654
694.3635 | 121.9297
695.3635 | 123.8054
696.3635 | 122.9271
697.3635 | 123.8249
698.3635 | 123.1015
699.3635 | 124.7442
700.3635 | 124.1106
701.3635 | 123.4723
702.3635 | 124.0564
703.3635 | 126.3053
704.3635 | 128.7605
705.3635 | 128.2463
706.3792 | 126.6474
707.3635 | 127.354
708.3635 | 127.4365
709.3635 | 129.7957
710.3635 | 129.1074
711.3635 | 128.285
712.3635 | 128.3983
713.3635 | 128.2493
714.3635 | 128.8357
715.3635 | 128.7077
716.3635 | 127.4036
717.3635 | 126.2446
718.3635 | 125.3993
719.3635 | 126.362
720.3635 | 129.69
721.3635 | 131.1265
722.3635 | 132.8333
723.3635 | 129.9146
724.3635 | 131.4909
725.3635 | 132.7815
726.3635 | 132.0412
727.3635 | 132.0901
728.3792 | 131.6814
729.3635 | 131.6796
730.3635 | 130.5134
731.3635 | 131.0831
732.3635 | 131.4614
733.3635 | 131.3989
734.3635 | 129.9909
735.3635 | 129.2439
736.3792 | 129.6567
737.3635 | 129.4483
738.3635 | 128.4937
739.3635 | 126.4228
740.3635 | 126.0052
741.3635 | 129.0998
742.3635 | 129.0725
743.3792 | 129.7732
744.3635 | 129.3582
745.3635 | 128.037
746.3635 | 125.802
747.3635 | 124.6932
748.3635 | 124.9129
749.3635 | 126.006
750.3635 | 125.4573
751.3635 | 124.3581
752.3635 | 125.1411
753.3635 | 125.9794
754.3635 | 125.9867
755.3635 | 128.3036
756.3635 | 127.1916
757.3635 | 128.1444
758.3635 | 127.145
759.3635 | 130.5681
760.3635 | 129.6208
761.3635 | 129.7214
762.3635 | 128.5748
763.3635 | 129.2613
764.3635 | 130.5312
765.3635 | 130.565
766.3635 | 129.315
767.3635 | 128.4604
768.3635 | 127.1746
769.3635 | 126.6291
770.3635 | 124.9715
771.3635 | 124.4829
772.3635 | 125.3274
773.3635 | 123.6175
774.3635 | 122.7692
775.3635 | 122.7871
776.3635 | 123.4366
777.3635 | 122.7024
778.3635 | 122.4735
779.3635 | 122.801
780.3635 | 122.0428
781.3792 | 122.3643
782.3635 | 122.5915
783.3635 | 123.1835
784.3635 | 124.0727
785.3635 | 122.1579
786.3635 | 122.9694
787.3635 | 123.312
788.3635 | 123.8463
789.3635 | 125.6256
790.3635 | 127.4232
791.3635 | 128.7118
792.3635 | 128.6094
793.3792 | 130.1975
794.3635 | 129.7562
795.3635 | 129.5179
796.3792 | 127.9629
797.3635 | 128.2354
798.3635 | 126.7055
799.3635 | 127.025
800.3635 | 125.5556
801.3635 | 124.3429
802.3635 | 124.9945
803.3635 | 124.7208
804.3635 | 123.4525
805.3635 | 123.3331
806.3635 | 122.1095
807.3635 | 121.9996
808.3792 | 124.2764
809.3635 | 125.352
810.3635 | 125.7438
811.3635 | 126.2344
812.3635 | 124.9278
813.3635 | 124.7145
814.3635 | 125.0777
815.3635 | 125.3796
816.3635 | 125.5799
817.3635 | 123.687
818.3635 | 125.0537
819.3635 | 125.38
820.3635 | 125.7631
821.3635 | 126.2175
822.3635 | 126.2843
823.3635 | 124.7024
824.3635 | 125.1712
825.3635 | 125.4695
826.3792 | 123.6041
827.3635 | 123.0917
828.3635 | 124.0992
829.3635 | 124.5545
830.3635 | 124.9027
831.3635 | 126.8485
832.3635 | 127.1111
833.3635 | 126.0272
834.3635 | 125.6491
835.3635 | 125.103
836.3635 | 124.6713
837.3635 | 125.454
838.3635 | 126.1737
839.3635 | 125.6694
840.3635 | 125.3139
841.3792 | 125.3712
842.3635 | 123.7073
843.3635 | 122.6053
844.3635 | 122.2473
845.3635 | 122.7177
846.3635 | 122.1551
847.3635 | 122.7678
848.3635 | 122.372
849.3635 | 121.7081
850.3635 | 121.6187
851.3635 | 122.1045
852.3635 | 121.4302
853.3635 | 122.4535
854.3635 | 124.8405
855.3635 | 124.959
856.3635 | 124.7214
857.3635 | 126.927
858.3635 | 125.4193
859.3635 | 124.1249
860.3635 | 124.3125
861.3635 | 125.0324
862.3635 | 126.0136
863.3635 | 125.169
864.3635 | 124.5578
865.3635 | 124.2773
866.3635 | 123.3717
867.3635 | 123.9192
868.3635 | 125.9889
869.3635 | 127.1873
870.3635 | 125.7341
871.3635 | 127.0941
872.3635 | 126.5563
873.3635 | 125.8832
874.3635 | 126.0377
875.3635 | 126.8001
876.3635 | 126.9085
877.3635 | 127.9613
878.3792 | 128.6637
879.3635 | 128.9017
880.3635 | 127.9173
881.3635 | 126.3863
882.3635 | 126.2264
883.3635 | 126.2914
884.3635 | 127.4711
885.3635 | 127.226
886.3635 | 128.5617
887.3635 | 130.7943
888.3635 | 131.9111
889.3635 | 131.5147
890.3635 | 134.1603
891.3635 | 134.5978
892.3635 | 133.783
893.3792 | 131.5504
894.3635 | 131.0652
895.3635 | 130.1797
896.3635 | 130.4624
897.3635 | 131.0797
898.3635 | 132.6832
899.3635 | 132.0401
900.3635 | 132.0582
901.3635 | 129.9429
902.3635 | 128.9795
903.3635 | 127.8374
904.3635 | 126.5879
905.3635 | 125.5965
906.3635 | 126.2439
907.3635 | 127.2972
908.3635 | 126.9987
909.3635 | 126.3539
910.3635 | 127.2721
911.3635 | 128.4826
912.3635 | 126.5646
913.3635 | 125.1671
914.3635 | 125.044
915.3635 | 125.5674
916.3635 | 126.988
917.3635 | 127.1136
918.3635 | 126.3477
919.3635 | 126.9769
920.3635 | 127.0105
921.3635 | 127.5233
922.3635 | 126.0177
923.3635 | 124.6826
924.3635 | 123.9072
925.3635 | 122.5726
926.3635 | 123.7298
927.3635 | 123.3346
928.3635 | 124.2972
929.3635 | 124.1598
930.3635 | 123.1237
931.3635 | 123.2288
932.3635 | 123.9137
933.3635 | 124.639
934.3635 | 126.2348
935.3635 | 125.2813
936.3635 | 125.9093
937.3635 | 124.905
938.3635 | 127.132
939.3635 | 126.1085
940.3635 | 124.6592
941.3635 | 124.7585
942.3635 | 123.5387
943.3635 | 123.4884
944.3635 | 123.7764
945.3635 | 124.3617
946.3635 | 123.7228
947.3635 | 122.9249
948.3635 | 122.6894
949.3635 | 121.3005
950.3635 | 119.8028
951.3635 | 118.6868
952.3635 | 117.766
953.3635 | 116.7344
954.3635 | 117.5843
955.3635 | 117.4887
956.3635 | 116.6096
957.3635 | 116.5147
958.3635 | 117.4163
959.3635 | 116.9215
960.3635 | 117.4554
961.3635 | 117.6964
962.3635 | 117.4265
963.3635 | 118.1483
964.3635 | 119.8764
965.3635 | 119.2191
966.3635 | 117.3925
967.3635 | 116.2718
968.3635 | 116.5157
969.3635 | 116.0108
970.3635 | 117.3453
971.3635 | 117.6999
972.3635 | 117.9328
973.3635 | 118.426
974.3635 | 118.8778
975.3635 | 119.4421
976.3635 | 118.3952
977.3635 | 118.1525
978.3635 | 116.5667
979.3635 | 116.6773
980.3635 | 116.3767
981.3635 | 117.1985
982.3635 | 116.8997
983.3635 | 116.294
984.3635 | 115.9401
985.3635 | 116.192
986.3635 | 116.0117
987.3635 | 115.3343
988.3635 | 114.45
989.3635 | 115.1571
990.3635 | 115.2933
991.3635 | 115.5872
992.3635 | 114.7736
993.3635 | 115.0648
994.3635 | 114.3794
995.3635 | 113.0455
996.3635 | 113.3084
997.3635 | 114.5681
998.3635 | 114.683
999.3635 | 113.8663
1000.3635 | 113.2579
1001.3635 | 112.1464
1002.3635 | 111.9332
1003.3635 | 111.6732
1004.3635 | 110.6616
1005.3635 | 110.7071