## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number Prelim 1 - Circuit Simulator Data Only
Test Date: | 2009-11-06
DCSim DAQ Start Time | 13:36
DCSim Time for Synchronization | 13:37
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:35
Heat Source Start Time | 14:12
DCSim Offset | 0:36 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2160 | seconds
Heat Source Offset | 0:37 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2192 | seconds
Heat Source Stop Time | 15:37
Test Duration | 1:25 | hour:minutes:seconds
| 5100 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the middle of the tray located in B Position. It is labeled as "north top"
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the middle of the tray located in B Position. It is labeled as "north top"
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.65625 | 122.818 | -60.7452 | 61.7432 | -0.19753 | 0.011989 | 0.0080024 | 0.00093576 | 0.060075 | -0.0050671 | 0.067949 | -60.8231 | 61.6791 | -60.8826 | -60.8414 | 61.5829 | 0.3067 | 0.059509 | 0.33417 | 61.6791 | -60.9467 | -0.13733 | -0.064087 | -0.07782 | -0.096131 | -0.16022 | -0.20142 | -0.064087 | 0.059509 | 60.8047 | 61.0794 | 122.3282 | 122.4243 | -0.07782 | 122.4243 | 61.0519 | -0.20142 | 122.4243 | -0.07782 | 61.0519 | 122.3282 | 122.4243 | -122.6257 | -122.6898
1.0156 | 122.7219 | -60.8322 | 61.7889 | 0.1458 | 0.014338 | 0.0097114 | 0.0032856 | 0.063707 | -0.0063489 | 0.066668 | -60.8368 | 61.6791 | -60.9055 | -60.878 | 61.5463 | 0.17395 | -0.25635 | 0.032043 | 61.6928 | -60.9283 | -0.073243 | -0.10986 | -0.004578 | -0.045777 | -0.24261 | -0.096131 | -0.09613 | 0.068665 | 60.5759 | 60.8643 | 122.3785 | 122.5113 | -0.004578 | 122.525 | 61.0062 | -0.096131 | 122.5113 | -0.004578 | 61.0062 | 122.3785 | 122.525 | -122.6944 | -122.7173
2.7656 | 122.731 | -60.8139 | 61.8027 | -0.0067901 | 0.013057 | 0.0086432 | 0.0081988 | 0.06157 | -0.0069897 | 0.067522 | -60.8734 | 61.6974 | -60.9512 | -60.9146 | 61.4868 | 0.15564 | 0 | 0.032043 | 61.7203 | -60.9604 | -0.13733 | -0.10529 | -0.059509 | -0.10071 | -0.31586 | -0.14648 | -0.082397 | 0.07782 | 60.8139 | 60.8459 | 122.3007 | 122.5113 | -0.059509 | 122.5342 | 60.9695 | -0.14648 | 122.5113 | -0.059509 | 60.9695 | 122.3007 | 122.5342 | -122.7539 | -122.7631
4.4375 | 122.8363 | -60.7773 | 61.7661 | -0.21278 | 0.013057 | 0.0088568 | 0.00093576 | 0.058793 | -0.0031445 | 0.067522 | -60.8414 | 61.6699 | -60.91 | -60.8597 | 61.5555 | 0.28381 | 0.10071 | 0.28839 | 61.6608 | -60.9421 | -0.13275 | -0.09613 | -0.064087 | -0.082397 | -0.21057 | -0.1648 | -0.10529 | 0.068664 | 60.878 | 61.0657 | 122.3328 | 122.4472 | -0.064087 | 122.4381 | 61.0611 | -0.1648 | 122.4472 | -0.064087 | 61.0611 | 122.3328 | 122.4381 | -122.6761 | -122.7081
6.1875 | 122.8455 | -60.759 | 61.7569 | -0.01442 | 0.014338 | 0.0037298 | 0.0011494 | 0.057939 | -0.0033581 | 0.066668 | -60.8963 | 61.6562 | -60.8917 | -60.9192 | 61.5234 | 0.21057 | -0.009155 | 0.18768 | 61.6974 | -60.9604 | -0.13275 | -0.10071 | -0.13733 | -0.16022 | -0.23346 | -0.20142 | -0.059509 | -0.004577 | 60.7498 | 60.9467 | 122.2824 | 122.4152 | -0.13733 | 122.4564 | 60.9695 | -0.20142 | 122.4152 | -0.13733 | 60.9695 | 122.2824 | 122.4564 | -122.6486 | -122.7173
7.9219 | 122.8088 | -60.8002 | 61.7935 | -0.21278 | 0.012843 | 0.0071478 | 0.0020038 | 0.060289 | -0.0037853 | 0.068377 | -60.8322 | 61.6791 | -60.8917 | -60.8459 | 61.5692 | 0.30212 | 0.022888 | 0.31128 | 61.6791 | -60.9695 | -0.091553 | -0.11444 | -0.032043 | -0.045776 | -0.2243 | -0.16937 | -0.11444 | 0.05951 | 60.8231 | 61.1114 | 122.3694 | 122.4792 | -0.032043 | 122.4792 | 61.1023 | -0.16937 | 122.4792 | -0.032043 | 61.1023 | 122.3694 | 122.4792 | -122.6852 | -122.7631
9.5938 | 122.8638 | -60.7407 | 61.7569 | 0.016098 | 0.012416 | 0.009925 | 0.0015766 | 0.059648 | -0.0031445 | 0.069231 | -60.9009 | 61.6745 | -60.9192 | -60.9238 | 61.5051 | 0.18768 | -0.018311 | 0.14648 | 61.6928 | -60.9558 | -0.17853 | -0.082397 | -0.16022 | -0.1831 | -0.25177 | -0.21515 | -0.064087 | 0.01831 | 60.7224 | 60.8871 | 122.2458 | 122.4152 | -0.16022 | 122.4335 | 60.9283 | -0.21515 | 122.4152 | -0.16022 | 60.9283 | 122.2458 | 122.4335 | -122.6761 | -122.7127
11.3281 | 122.8043 | -60.7727 | 61.7752 | 0.10002 | 0.01327 | 0.0094978 | 0.0069172 | 0.060502 | -0.0057079 | 0.070513 | -60.9238 | 61.7203 | -60.9467 | -60.9604 | 61.441 | 0.07782 | -0.068665 | -0.059509 | 61.734 | -60.9558 | -0.17395 | -0.054932 | -0.15106 | -0.18768 | -0.33417 | -0.18311 | -0.041199 | 0.022888 | 60.704 | 60.7132 | 122.2137 | 122.493 | -0.15106 | 122.5067 | 60.8505 | -0.18311 | 122.493 | -0.15106 | 60.8505 | 122.2137 | 122.5067 | -122.7219 | -122.731
13.0625 | 122.8775 | -60.759 | 61.7432 | -0.23567 | 0.011348 | 0.0086432 | 0.0054218 | 0.059648 | -0.0067761 | 0.068163 | -60.9467 | 61.6882 | -60.9741 | -60.9512 | 61.4456 | 0.19684 | 0.19684 | 0.13275 | 61.7569 | -60.9421 | -0.21515 | -0.054932 | -0.18768 | -0.19226 | -0.29755 | -0.18311 | 0.013733 | 0.027466 | 60.9558 | 60.8917 | 122.2046 | 122.4472 | -0.18768 | 122.5159 | 60.9558 | -0.18311 | 122.4472 | -0.18768 | 60.9558 | 122.2046 | 122.5159 | -122.7173 | -122.6852
14.7969 | 122.818 | -60.7819 | 61.7935 | -0.15938 | 0.013698 | 0.0086432 | 0.0071308 | 0.06093 | -0.0084851 | 0.069017 | -60.8963 | 61.6928 | -60.9467 | -60.91 | 61.5097 | 0.2243 | 0.082397 | 0.12817 | 61.7294 | -60.9192 | -0.16479 | -0.10071 | -0.11444 | -0.12817 | -0.28381 | -0.13733 | -0.064087 | 0.050354 | 60.8643 | 60.91 | 122.2916 | 122.4747 | -0.11444 | 122.5113 | 61.0062 | -0.13733 | 122.4747 | -0.11444 | 61.0062 | 122.2916 | 122.5113 | -122.7402 | -122.7127
16.4688 | 122.8592 | -60.759 | 61.7615 | -0.23567 | 0.017329 | 0.0058662 | 0.0028584 | 0.059007 | -0.0059217 | 0.068163 | -60.9329 | 61.7203 | -60.9375 | -60.9467 | 61.4639 | 0.19226 | 0.19226 | 0.1236 | 61.7157 | -60.9604 | -0.17853 | -0.041199 | -0.17395 | -0.18768 | -0.29755 | -0.20142 | -0.045777 | 0.004578 | 60.9512 | 60.8826 | 122.2229 | 122.4792 | -0.17395 | 122.4747 | 60.9512 | -0.20142 | 122.4792 | -0.17395 | 60.9512 | 122.2229 | 122.4747 | -122.699 | -122.7219
18.1875 | 122.7264 | -60.8047 | 61.7798 | 0.19157 | 0.013698 | 0.0060798 | 0.0039264 | 0.062639 | -0.0059217 | 0.069445 | -60.8643 | 61.6516 | -60.9238 | -60.878 | 61.5189 | 0.16479 | -0.20142 | 0.050354 | 61.6882 | -60.9329 | -0.11902 | -0.12817 | -0.059509 | -0.073242 | -0.26093 | -0.12817 | -0.091553 | 0.059509 | 60.6033 | 60.8551 | 122.3236 | 122.4564 | -0.059509 | 122.493 | 60.9695 | -0.12817 | 122.4564 | -0.059509 | 60.9695 | 122.3236 | 122.493 | -122.7036 | -122.7127
19.9219 | 122.7539 | -60.8047 | 61.7889 | 0.13817 | 0.012629 | 0.013343 | 0.003072 | 0.058152 | -0.0031445 | 0.067522 | -60.8505 | 61.6379 | -60.9055 | -60.8871 | 61.528 | 0.19226 | -0.15106 | 0.10071 | 61.6882 | -60.9604 | -0.10071 | -0.15106 | -0.045776 | -0.082397 | -0.26092 | -0.15564 | -0.10071 | 0.054932 | 60.6537 | 60.9055 | 122.3328 | 122.4426 | -0.045776 | 122.493 | 60.997 | -0.15564 | 122.4426 | -0.045776 | 60.997 | 122.3328 | 122.493 | -122.6944 | -122.7493
21.5938 | 122.7264 | -60.8276 | 61.7706 | 0.1992 | 0.011348 | 0.012702 | 0.0043536 | 0.060075 | -0.0039989 | 0.067522 | -60.8276 | 61.647 | -60.91 | -60.8505 | 61.5601 | 0.20599 | -0.22888 | 0.086975 | 61.6425 | -60.9238 | -0.082397 | -0.1236 | 0 | -0.022888 | -0.21057 | -0.09613 | -0.12817 | 0.082397 | 60.5988 | 60.9146 | 122.3877 | 122.4747 | 0 | 122.4701 | 61.0336 | -0.09613 | 122.4747 | 0 | 61.0336 | 122.3877 | 122.4701 | -122.6807 | -122.6944
23.3125 | 122.8683 | -60.7864 | 61.7523 | -0.044937 | 0.012843 | 0.0090704 | 0.0034992 | 0.058793 | -0.0014355 | 0.06859 | -60.8826 | 61.6837 | -60.9009 | -60.8963 | 61.5555 | 0.25177 | -0.013733 | 0.23804 | 61.6791 | -60.965 | -0.11444 | -0.068664 | -0.09613 | -0.10986 | -0.19684 | -0.17853 | -0.073242 | 0.018311 | 60.7727 | 61.0245 | 122.3419 | 122.4701 | -0.09613 | 122.4655 | 61.0382 | -0.17853 | 122.4701 | -0.09613 | 61.0382 | 122.3419 | 122.4655 | -122.6532 | -122.7173
24.9688 | 122.7631 | -60.8185 | 61.8164 | -0.10597 | 0.011348 | 0.0071478 | 0.0077716 | 0.058152 | -0.0059217 | 0.069017 | -60.8826 | 61.702 | -60.9558 | -60.9009 | 61.496 | 0.2243 | 0.036621 | 0.11902 | 61.6974 | -60.9238 | -0.13733 | -0.11444 | -0.064087 | -0.082398 | -0.32043 | -0.10529 | -0.11902 | 0.073243 | 60.8551 | 60.9375 | 122.3145 | 122.5204 | -0.064087 | 122.5159 | 61.0428 | -0.10529 | 122.5204 | -0.064087 | 61.0428 | 122.3145 | 122.5159 | -122.7722 | -122.7402
26.7031 | 122.7585 | -60.8139 | 61.8027 | -0.090714 | 0.014552 | 0.0088568 | 0.0079852 | 0.060075 | -0.0065625 | 0.068377 | -60.878 | 61.6791 | -60.9329 | -60.8871 | 61.5189 | 0.21515 | 0.036621 | 0.10986 | 61.7203 | -60.965 | -0.11902 | -0.1236 | -0.064087 | -0.073242 | -0.28381 | -0.15106 | -0.082397 | 0.054931 | 60.8505 | 60.9238 | 122.3328 | 122.493 | -0.064087 | 122.5342 | 61.0291 | -0.15106 | 122.493 | -0.064087 | 61.0291 | 122.3328 | 122.5342 | -122.7356 | -122.7676
28.4219 | 122.7585 | -60.7681 | 61.8073 | -0.1136 | 0.01327 | 0.010352 | 0.0071308 | 0.059861 | -0.0061353 | 0.067949 | -60.8826 | 61.6974 | -60.9375 | -60.9009 | 61.5234 | 0.23804 | 0.059509 | 0.11444 | 61.7523 | -60.9421 | -0.16937 | -0.10986 | -0.11444 | -0.13275 | -0.28381 | -0.17395 | -0.054932 | 0.054932 | 60.8276 | 60.8826 | 122.2916 | 122.4655 | -0.11444 | 122.5204 | 61.0062 | -0.17395 | 122.4655 | -0.11444 | 61.0062 | 122.2916 | 122.5204 | -122.7448 | -122.7493
30.1406 | 122.8363 | -60.759 | 61.7935 | -0.1899 | 0.012202 | 0.0052252 | -0.0012006 | 0.058152 | -0.0031445 | 0.067949 | -60.8643 | 61.6699 | -60.8917 | -60.8597 | 61.5555 | 0.29297 | 0.068665 | 0.27924 | 61.6745 | -60.9375 | -0.13275 | -0.1236 | -0.10529 | -0.10071 | -0.23804 | -0.17853 | -0.11902 | 0.027466 | 60.8276 | 61.0382 | 122.3145 | 122.4289 | -0.10529 | 122.4335 | 61.0519 | -0.17853 | 122.4289 | -0.10529 | 61.0519 | 122.3145 | 122.4335 | -122.6852 | -122.731
31.8906 | 122.8683 | -60.7864 | 61.7294 | 0.023727 | 0.012843 | 0.0073614 | 0.00050836 | 0.058366 | -0.0050671 | 0.069017 | -60.8917 | 61.6791 | -60.8826 | -60.9283 | 61.496 | 0.16937 | -0.032043 | 0.13733 | 61.6882 | -60.9375 | -0.09613 | -0.050354 | -0.10529 | -0.14191 | -0.23346 | -0.15106 | -0.041199 | -0.009156 | 60.7544 | 60.9238 | 122.2824 | 122.4655 | -0.10529 | 122.4747 | 60.9558 | -0.15106 | 122.4655 | -0.10529 | 60.9558 | 122.2824 | 122.4747 | -122.612 | -122.6669
33.625 | 122.7448 | -60.8139 | 61.7981 | -0.090714 | 0.013484 | 0.009284 | 0.0094806 | 0.05858 | -0.0076305 | 0.068163 | -60.8734 | 61.6928 | -60.9512 | -60.8871 | 61.5143 | 0.2243 | 0.050354 | 0.10986 | 61.734 | -60.9329 | -0.13733 | -0.10529 | -0.059509 | -0.073242 | -0.28381 | -0.11902 | -0.064087 | 0.07782 | 60.8643 | 60.9238 | 122.3282 | 122.5067 | -0.059509 | 122.5479 | 61.0382 | -0.11902 | 122.5067 | -0.059509 | 61.0382 | 122.3282 | 122.5479 | -122.7493 | -122.731
35.3438 | 122.8226 | -60.7636 | 61.7523 | -0.16701 | 0.013484 | 0.0075752 | 0.0022174 | 0.059861 | -0.0035717 | 0.069231 | -60.8368 | 61.6882 | -60.8917 | -60.8551 | 61.5646 | 0.28839 | -0.009155 | 0.29755 | 61.6791 | -60.9375 | -0.12817 | -0.064087 | -0.073242 | -0.091553 | -0.18768 | -0.17395 | -0.073242 | 0.054932 | 60.7544 | 61.0611 | 122.3282 | 122.4518 | -0.073242 | 122.4426 | 61.0519 | -0.17395 | 122.4518 | -0.073242 | 61.0519 | 122.3282 | 122.4426 | -122.644 | -122.6898
37.0156 | 122.7859 | -60.791 | 61.8073 | 0.10002 | 0.013911 | 0.010779 | 0.00649 | 0.061143 | -0.0046399 | 0.068377 | -60.9421 | 61.6974 | -60.9512 | -60.9787 | 61.4365 | 0.086975 | -0.018311 | -0.068665 | 61.7111 | -60.9512 | -0.16022 | -0.10986 | -0.15106 | -0.18768 | -0.37079 | -0.16022 | -0.09613 | 0.009155 | 60.7727 | 60.7224 | 122.2275 | 122.4884 | -0.15106 | 122.5021 | 60.878 | -0.16022 | 122.4884 | -0.15106 | 60.878 | 122.2275 | 122.5021 | -122.7585 | -122.7585
38.75 | 122.7814 | -60.7956 | 61.7706 | 0.11528 | 0.014766 | 0.009284 | 0.0052082 | 0.062639 | -0.0050671 | 0.067308 | -60.9329 | 61.6928 | -60.9192 | -60.9604 | 61.4594 | 0.09613 | -0.064087 | -0.07782 | 61.7249 | -60.9375 | -0.1236 | -0.07782 | -0.13733 | -0.1648 | -0.31128 | -0.14191 | -0.045776 | -0.013733 | 60.7315 | 60.7178 | 122.2549 | 122.4884 | -0.13733 | 122.5204 | 60.8917 | -0.14191 | 122.4884 | -0.13733 | 60.8917 | 122.2549 | 122.5204 | -122.6898 | -122.7081
40.4375 | 122.7768 | -60.8185 | 61.7844 | 0.023727 | 0.014552 | 0.015266 | 0.0069172 | 0.062639 | -0.0044263 | 0.06859 | -60.91 | 61.702 | -60.9512 | -60.9467 | 61.4548 | 0.1236 | 0 | -0.041199 | 61.7203 | -60.9375 | -0.13275 | -0.082398 | -0.091553 | -0.12817 | -0.32959 | -0.11902 | -0.064087 | 0.041199 | 60.8185 | 60.7773 | 122.2733 | 122.5204 | -0.091553 | 122.5388 | 60.9421 | -0.11902 | 122.5204 | -0.091553 | 60.9421 | 122.2733 | 122.5388 | -122.7356 | -122.7219
42.1562 | 122.7722 | -60.7956 | 61.7981 | 0.077133 | 0.014125 | 0.009284 | 0.0067036 | 0.06093 | -0.0037853 | 0.070086 | -60.9375 | 61.7111 | -60.9467 | -60.9787 | 61.4182 | 0.09613 | -0.004578 | -0.07782 | 61.7432 | -60.9695 | -0.15106 | -0.086975 | -0.14191 | -0.18311 | -0.37994 | -0.17395 | -0.054932 | 0.009155 | 60.791 | 60.7178 | 122.2137 | 122.5067 | -0.14191 | 122.5388 | 60.8917 | -0.17395 | 122.5067 | -0.14191 | 60.8917 | 122.2137 | 122.5388 | -122.7448 | -122.7676
43.8281 | 122.8317 | -60.7498 | 61.7661 | -0.12123 | 0.014552 | 0.009925 | -0.00077324 | 0.057725 | -0.0031445 | 0.067736 | -60.8414 | 61.6653 | -60.8688 | -60.8597 | 61.5829 | 0.27466 | -0.022888 | 0.2655 | 61.6699 | -60.9375 | -0.11902 | -0.10071 | -0.091553 | -0.10986 | -0.18311 | -0.18768 | -0.09613 | 0.027465 | 60.7269 | 61.0153 | 122.3328 | 122.4152 | -0.091553 | 122.4197 | 61.0245 | -0.18768 | 122.4152 | -0.091553 | 61.0245 | 122.3328 | 122.4197 | -122.6349 | -122.7036
45.5625 | 122.8729 | -60.7864 | 61.7615 | 0.054245 | 0.011561 | 0.0062934 | 0.001363 | 0.058366 | -0.0046399 | 0.066668 | -60.9009 | 61.6516 | -60.9421 | -60.9375 | 61.5097 | 0.17853 | -0.036621 | 0.1236 | 61.6791 | -60.9604 | -0.15564 | -0.10986 | -0.11444 | -0.15106 | -0.25177 | -0.17395 | -0.082398 | 0.041199 | 60.7498 | 60.91 | 122.2961 | 122.438 | -0.11444 | 122.4655 | 60.965 | -0.17395 | 122.438 | -0.11444 | 60.965 | 122.2961 | 122.4655 | -122.7036 | -122.7219
47.25 | 122.8638 | -60.7498 | 61.7889 | -0.23567 | 0.013484 | 0.0073614 | 0.0077716 | 0.057939 | -0.0020763 | 0.069872 | -60.9192 | 61.7432 | -60.91 | -60.9467 | 61.4502 | 0.1831 | 0.21057 | 0.10986 | 61.7157 | -60.9558 | -0.16022 | -0.045776 | -0.16937 | -0.19684 | -0.33874 | -0.20599 | -0.073242 | -0.009155 | 60.9604 | 60.8597 | 122.2 | 122.493 | -0.16937 | 122.4655 | 60.9329 | -0.20599 | 122.493 | -0.16937 | 60.9329 | 122.2 | 122.4655 | -122.699 | -122.7448
49.0156 | 122.7859 | -60.7956 | 61.7706 | 0.15343 | 0.016047 | 0.01142 | 0.0039264 | 0.05858 | -0.0031445 | 0.069872 | -60.878 | 61.6745 | -60.9192 | -60.9146 | 61.5189 | 0.17395 | -0.11444 | 0.10986 | 61.6608 | -60.9604 | -0.1236 | -0.09613 | -0.082398 | -0.11902 | -0.25177 | -0.1648 | -0.10986 | 0.041198 | 60.6812 | 60.9055 | 122.3145 | 122.4701 | -0.082398 | 122.4564 | 60.9695 | -0.1648 | 122.4701 | -0.082398 | 60.9695 | 122.3145 | 122.4564 | -122.6898 | -122.731
50.7031 | 122.8317 | -60.7819 | 61.7523 | -0.14412 | 0.013057 | 0.0090704 | -0.00034604 | 0.059007 | -0.0020763 | 0.068804 | -60.8276 | 61.702 | -60.9146 | -60.8551 | 61.5646 | 0.28839 | -0.013733 | 0.28381 | 61.6974 | -60.9467 | -0.13275 | -0.050354 | -0.045777 | -0.073243 | -0.18768 | -0.16479 | -0.054931 | 0.086975 | 60.7681 | 61.0657 | 122.3465 | 122.4838 | -0.045777 | 122.4792 | 61.0703 | -0.16479 | 122.4838 | -0.045777 | 61.0703 | 122.3465 | 122.4792 | -122.6669 | -122.699
52.375 | 122.7402 | -60.8139 | 61.7706 | 0.22972 | 0.013057 | 0.0088568 | 0.0081988 | 0.060716 | -0.0074169 | 0.066668 | -60.878 | 61.702 | -60.9375 | -60.8871 | 61.5051 | 0.15106 | -0.17395 | 0.027466 | 61.6745 | -60.9375 | -0.1236 | -0.068665 | -0.064087 | -0.073242 | -0.2655 | -0.1236 | -0.09613 | 0.059509 | 60.64 | 60.8414 | 122.319 | 122.5159 | -0.064087 | 122.4884 | 60.965 | -0.1236 | 122.5159 | -0.064087 | 60.965 | 122.319 | 122.4884 | -122.7081 | -122.7081
54.0469 | 122.7402 | -60.8185 | 61.7889 | 0.13054 | 0.013057 | 0.0060798 | 0.0032856 | 0.06157 | -0.0052807 | 0.068163 | -60.8368 | 61.615 | -60.8871 | -60.8643 | 61.5463 | 0.1831 | -0.1831 | 0.09613 | 61.6791 | -60.9192 | -0.068665 | -0.17395 | -0.018311 | -0.045777 | -0.24261 | -0.10071 | -0.10986 | 0.050354 | 60.6354 | 60.9146 | 122.3648 | 122.4335 | -0.018311 | 122.4976 | 61.0016 | -0.10071 | 122.4335 | -0.018311 | 61.0016 | 122.3648 | 122.4976 | -122.6761 | -122.7081
55.7656 | 122.818 | -60.7864 | 61.7798 | -0.12123 | 0.011134 | 0.011207 | 0.0028584 | 0.057298 | -0.0044263 | 0.06859 | -60.8185 | 61.6653 | -60.9055 | -60.8231 | 61.5784 | 0.29755 | -0.013733 | 0.31586 | 61.6653 | -60.9329 | -0.11902 | -0.11444 | -0.032043 | -0.036621 | -0.20142 | -0.14648 | -0.11444 | 0.086976 | 60.7727 | 61.1023 | 122.3648 | 122.4518 | -0.032043 | 122.4518 | 61.084 | -0.14648 | 122.4518 | -0.032043 | 61.084 | 122.3648 | 122.4518 | -122.6852 | -122.7127
57.4375 | 122.7768 | -60.7864 | 61.7935 | 0.061874 | 0.013057 | 0.0080024 | 0.0071308 | 0.059007 | -0.0050671 | 0.070513 | -60.9238 | 61.7157 | -60.9421 | -60.9604 | 61.4502 | 0.10986 | -0.009155 | -0.059509 | 61.7569 | -60.9558 | -0.15564 | -0.07782 | -0.13733 | -0.17395 | -0.34332 | -0.16937 | -0.036621 | 0.018311 | 60.7773 | 60.7269 | 122.2366 | 122.5021 | -0.13733 | 122.5433 | 60.8963 | -0.16937 | 122.5021 | -0.13733 | 60.8963 | 122.2366 | 122.5433 | -122.7356 | -122.7493
59.125 | 122.6944 | -60.8047 | 61.7706 | 0.19157 | 0.012629 | 0.011848 | 0.0060626 | 0.062639 | -0.0035717 | 0.069231 | -60.8688 | 61.6837 | -60.9283 | -60.8963 | 61.5234 | 0.16022 | -0.18768 | 0.018311 | 61.6974 | -60.9238 | -0.1236 | -0.086975 | -0.064086 | -0.091552 | -0.24719 | -0.11902 | -0.073242 | 0.05951 | 60.6171 | 60.8231 | 122.3282 | 122.4884 | -0.064086 | 122.5021 | 60.965 | -0.11902 | 122.4884 | -0.064086 | 60.965 | 122.3282 | 122.5021 | -122.699 | -122.6944
60.7969 | 122.8775 | -60.7544 | 61.7661 | -0.25093 | 0.013698 | 0.01612 | 0.004781 | 0.059434 | -0.0039989 | 0.067308 | -60.9467 | 61.6974 | -60.965 | -60.9512 | 61.4639 | 0.19684 | 0.2243 | 0.14648 | 61.7661 | -60.9512 | -0.21057 | -0.068664 | -0.19226 | -0.19684 | -0.30212 | -0.19684 | 0 | 0.018311 | 60.9787 | 60.9009 | 122.2183 | 122.4518 | -0.19226 | 122.5204 | 60.9512 | -0.19684 | 122.4518 | -0.19226 | 60.9512 | 122.2183 | 122.5204 | -122.731 | -122.7173
62.4844 | 122.8775 | -60.7636 | 61.7798 | -0.21278 | 0.014552 | 0.0069342 | 0.0045672 | 0.060716 | -0.0052807 | 0.067095 | -60.9146 | 61.6882 | -60.9467 | -60.9421 | 61.4731 | 0.21515 | 0.19684 | 0.18768 | 61.7432 | -60.9329 | -0.1831 | -0.091553 | -0.15106 | -0.17853 | -0.3067 | -0.16937 | -0.036621 | 0.032043 | 60.9604 | 60.9512 | 122.2366 | 122.4518 | -0.15106 | 122.5067 | 60.9787 | -0.16937 | 122.4518 | -0.15106 | 60.9787 | 122.2366 | 122.5067 | -122.7264 | -122.7127
64.1719 | 122.8592 | -60.7864 | 61.7615 | -0.1899 | 0.014338 | 0.0043708 | 0.00649 | 0.059434 | -0.0048535 | 0.069231 | -60.9192 | 61.7203 | -60.9192 | -60.9512 | 61.4731 | 0.17853 | 0.16022 | 0.1236 | 61.7294 | -60.9604 | -0.13275 | -0.041199 | -0.13275 | -0.1648 | -0.28839 | -0.17395 | -0.032044 | 0 | 60.9467 | 60.91 | 122.2595 | 122.5067 | -0.13275 | 122.5159 | 60.965 | -0.17395 | 122.5067 | -0.13275 | 60.965 | 122.2595 | 122.5159 | -122.6807 | -122.7219
65.8438 | 122.8363 | -60.7727 | 61.7569 | -0.18227 | 0.012202 | 0.0090704 | 0.00072196 | 0.057725 | -0.0042127 | 0.069231 | -60.8185 | 61.6745 | -60.8963 | -60.8414 | 61.5967 | 0.3067 | 0.022888 | 0.3067 | 61.6608 | -60.9695 | -0.1236 | -0.082397 | -0.045776 | -0.068665 | -0.16022 | -0.19684 | -0.09613 | 0.07782 | 60.7956 | 61.0794 | 122.3694 | 122.4472 | -0.045776 | 122.4335 | 61.0794 | -0.19684 | 122.4472 | -0.045776 | 61.0794 | 122.3694 | 122.4335 | -122.6532 | -122.7264
67.5625 | 122.7539 | -60.8002 | 61.8027 | 0.016098 | 0.014766 | 0.011848 | 0.0052082 | 0.060716 | -0.0084851 | 0.069017 | -60.8826 | 61.7065 | -60.9512 | -60.9238 | 61.4594 | 0.14191 | -0.013733 | 0 | 61.7386 | -60.9238 | -0.15106 | -0.09613 | -0.082397 | -0.1236 | -0.34332 | -0.1236 | -0.064087 | 0.068665 | 60.7864 | 60.8002 | 122.2595 | 122.5067 | -0.082397 | 122.5388 | 60.9421 | -0.1236 | 122.5067 | -0.082397 | 60.9421 | 122.2595 | 122.5388 | -122.7539 | -122.7264
69.2344 | 122.7493 | -60.8276 | 61.7981 | -0.1136 | 0.012843 | 0.009925 | 0.0069172 | 0.061784 | -0.0037853 | 0.067736 | -60.8688 | 61.7157 | -60.9283 | -60.8871 | 61.528 | 0.2243 | 0.036621 | 0.10529 | 61.7111 | -60.9604 | -0.10071 | -0.082398 | -0.041198 | -0.059509 | -0.27008 | -0.13275 | -0.086975 | 0.05951 | 60.8643 | 60.9329 | 122.3557 | 122.5433 | -0.041198 | 122.5388 | 61.0519 | -0.13275 | 122.5433 | -0.041198 | 61.0519 | 122.3557 | 122.5388 | -122.7264 | -122.7585
70.9219 | 122.7997 | -60.7819 | 61.7706 | -0.14412 | 0.014552 | 0.0080024 | 0.005849 | 0.059648 | -0.0042127 | 0.067308 | -60.9009 | 61.7111 | -60.9467 | -60.9055 | 61.5143 | 0.22888 | 0.09613 | 0.11902 | 61.7157 | -60.9467 | -0.16479 | -0.059509 | -0.11902 | -0.1236 | -0.25635 | -0.16479 | -0.054932 | 0.045776 | 60.878 | 60.9009 | 122.2961 | 122.493 | -0.11902 | 122.4976 | 61.0107 | -0.16479 | 122.493 | -0.11902 | 61.0107 | 122.2961 | 122.4976 | -122.7173 | -122.7173
72.625 | 122.7402 | -60.8322 | 61.821 | -0.060196 | 0.014766 | 0.0050116 | 0.0037128 | 0.061357 | -0.0061353 | 0.068804 | -60.8597 | 61.6928 | -60.9558 | -60.9055 | 61.5143 | 0.20142 | 0.018311 | 0.059509 | 61.7249 | -60.9375 | -0.1236 | -0.12817 | -0.027466 | -0.073243 | -0.3067 | -0.10529 | -0.09613 | 0.096131 | 60.8505 | 60.8917 | 122.3465 | 122.525 | -0.027466 | 122.5571 | 61.0336 | -0.10529 | 122.525 | -0.027466 | 61.0336 | 122.3465 | 122.5571 | -122.7768 | -122.7585
74.2969 | 122.7402 | -60.8047 | 61.7935 | 0.19157 | 0.013484 | 0.01142 | 0.001363 | 0.061143 | -0.0039989 | 0.069658 | -60.878 | 61.6745 | -60.9375 | -60.8963 | 61.5646 | 0.18768 | -0.21973 | 0.050354 | 61.6791 | -60.9283 | -0.13275 | -0.11902 | -0.073242 | -0.091552 | -0.22888 | -0.1236 | -0.11444 | 0.059509 | 60.585 | 60.8551 | 122.3694 | 122.4792 | -0.073242 | 122.4838 | 60.9924 | -0.1236 | 122.4792 | -0.073242 | 60.9924 | 122.3694 | 122.4838 | -122.731 | -122.7219
76.0469 | 122.8683 | -60.7727 | 61.7523 | 0.038986 | 0.014125 | 0.010352 | -0.0016278 | 0.059007 | -0.0018627 | 0.069658 | -60.8917 | 61.6791 | -60.9009 | -60.9421 | 61.5097 | 0.1831 | -0.009155 | 0.13275 | 61.6699 | -60.9512 | -0.12817 | -0.073242 | -0.11902 | -0.16937 | -0.24261 | -0.17853 | -0.082397 | 0.009155 | 60.7636 | 60.9055 | 122.2824 | 122.4518 | -0.11902 | 122.4426 | 60.9558 | -0.17853 | 122.4518 | -0.11902 | 60.9558 | 122.2824 | 122.4426 | -122.6532 | -122.7036
77.7188 | 122.7448 | -60.8002 | 61.8256 | -0.067826 | 0.01327 | 0.006507 | 0.0052082 | 0.058152 | -0.0080579 | 0.067308 | -60.8597 | 61.6837 | -60.9604 | -60.8917 | 61.5234 | 0.21057 | -0.004578 | 0.091553 | 61.7111 | -60.9329 | -0.16022 | -0.14191 | -0.059509 | -0.091553 | -0.30212 | -0.13275 | -0.11444 | 0.10071 | 60.7956 | 60.8917 | 122.3236 | 122.4838 | -0.059509 | 122.5113 | 61.0107 | -0.13275 | 122.4838 | -0.059509 | 61.0107 | 122.3236 | 122.5113 | -122.7859 | -122.7585
79.4531 | 122.8226 | -60.759 | 61.7661 | -0.1136 | 0.01327 | 0.013984 | -0.00055964 | 0.060075 | -0.0054943 | 0.067522 | -60.8231 | 61.6791 | -60.9009 | -60.8551 | 61.5875 | 0.31586 | -0.009155 | 0.3067 | 61.6928 | -60.9512 | -0.14191 | -0.086975 | -0.064087 | -0.096131 | -0.17853 | -0.19226 | -0.073242 | 0.07782 | 60.7498 | 61.0657 | 122.3465 | 122.438 | -0.064087 | 122.4518 | 61.0748 | -0.19226 | 122.438 | -0.064087 | 61.0748 | 122.3465 | 122.4518 | -122.6669 | -122.7173
81.1094 | 122.7493 | -60.8139 | 61.8347 | -0.067826 | 0.011561 | 0.010139 | 0.0079852 | 0.061784 | -0.0065625 | 0.067308 | -60.8643 | 61.6791 | -60.9421 | -60.8871 | 61.4914 | 0.20142 | 0 | 0.059509 | 61.7157 | -60.9375 | -0.12817 | -0.15564 | -0.050354 | -0.073242 | -0.34332 | -0.1236 | -0.11902 | 0.07782 | 60.8139 | 60.8734 | 122.3053 | 122.493 | -0.050354 | 122.5296 | 61.0153 | -0.1236 | 122.493 | -0.050354 | 61.0153 | 122.3053 | 122.5296 | -122.7768 | -122.7722
82.7656 | 122.7493 | -60.8322 | 61.7615 | 0.13817 | 0.011989 | 0.012275 | 0.00072196 | 0.060289 | -0.0069897 | 0.067095 | -60.8414 | 61.6562 | -60.9192 | -60.8826 | 61.5326 | 0.1831 | -0.16937 | 0.09613 | 61.6974 | -60.9695 | -0.086975 | -0.10529 | -0.009156 | -0.050354 | -0.22888 | -0.13733 | -0.064087 | 0.077819 | 60.6628 | 60.9283 | 122.3648 | 122.4884 | -0.009156 | 122.5296 | 61.0153 | -0.13733 | 122.4884 | -0.009156 | 61.0153 | 122.3648 | 122.5296 | -122.6807 | -122.731
84.4844 | 122.7814 | -60.8047 | 61.7844 | 0.16869 | 0.015407 | 0.004798 | 0.0017902 | 0.05858 | -0.0035717 | 0.069872 | -60.8597 | 61.6608 | -60.9009 | -60.8963 | 61.5234 | 0.17853 | -0.13275 | 0.1236 | 61.6791 | -60.9558 | -0.09613 | -0.1236 | -0.054931 | -0.091552 | -0.26093 | -0.15106 | -0.10529 | 0.041199 | 60.672 | 60.9283 | 122.3282 | 122.4655 | -0.054931 | 122.4838 | 60.9833 | -0.15106 | 122.4655 | -0.054931 | 60.9833 | 122.3282 | 122.4838 | -122.6852 | -122.7402
86.1406 | 122.8683 | -60.8002 | 61.7798 | -0.22804 | 0.01327 | 0.0073614 | 0.00414 | 0.059221 | -0.0057079 | 0.067736 | -60.9375 | 61.7203 | -60.9421 | -60.9558 | 61.4639 | 0.19226 | 0.21057 | 0.14648 | 61.734 | -60.965 | -0.14191 | -0.059509 | -0.13733 | -0.15564 | -0.31586 | -0.16479 | -0.045776 | 0.004578 | 61.0107 | 60.9467 | 122.2641 | 122.5204 | -0.13733 | 122.5342 | 60.9924 | -0.16479 | 122.5204 | -0.13733 | 60.9924 | 122.2641 | 122.5342 | -122.7219 | -122.7448
87.8438 | 122.7356 | -60.7956 | 61.8027 | 0.1458 | 0.01327 | 0.014838 | 0.0056354 | 0.061143 | -0.0035717 | 0.067736 | -60.8185 | 61.6653 | -60.9146 | -60.8597 | 61.5555 | 0.20142 | -0.18768 | 0.11902 | 61.6653 | -60.9421 | -0.11902 | -0.13733 | -0.022888 | -0.064087 | -0.24719 | -0.14649 | -0.13733 | 0.096131 | 60.6079 | 60.9146 | 122.3511 | 122.4609 | -0.022888 | 122.4609 | 60.997 | -0.14649 | 122.4609 | -0.022888 | 60.997 | 122.3511 | 122.4609 | -122.7173 | -122.7448
89.5156 | 122.8683 | -60.7636 | 61.7798 | -0.27382 | 0.011134 | 0.003089 | 0.002431 | 0.056443 | -0.0035717 | 0.066668 | -60.8826 | 61.6699 | -60.9375 | -60.8871 | 61.5234 | 0.24719 | 0.14648 | 0.23804 | 61.7111 | -60.9558 | -0.17395 | -0.10986 | -0.11902 | -0.1236 | -0.25635 | -0.19226 | -0.068664 | 0.054932 | 60.91 | 61.0016 | 122.287 | 122.4335 | -0.11902 | 122.4747 | 61.0107 | -0.19226 | 122.4335 | -0.11902 | 61.0107 | 122.287 | 122.4747 | -122.7173 | -122.7356
91.1719 | 122.7722 | -60.8002 | 61.8073 | 0.069504 | 0.013484 | 0.014838 | 0.0079852 | 0.061357 | -0.0065625 | 0.069231 | -60.9192 | 61.7203 | -60.9512 | -60.965 | 61.4227 | 0.09613 | 0.009155 | -0.050354 | 61.7523 | -60.965 | -0.15106 | -0.086975 | -0.11902 | -0.16479 | -0.38452 | -0.16479 | -0.054932 | 0.032044 | 60.8093 | 60.7498 | 122.2229 | 122.5204 | -0.11902 | 122.5525 | 60.8963 | -0.16479 | 122.5204 | -0.11902 | 60.8963 | 122.2229 | 122.5525 | -122.7585 | -122.7722
92.8438 | 122.8134 | -60.7727 | 61.7523 | -0.13649 | 0.015407 | 0.0054388 | -0.0014142 | 0.058366 | -0.0054943 | 0.06859 | -60.8459 | 61.6745 | -60.9055 | -60.8276 | 61.5875 | 0.29755 | -0.018311 | 0.31128 | 61.6837 | -60.9558 | -0.13275 | -0.077819 | -0.073242 | -0.054932 | -0.16479 | -0.18311 | -0.068664 | 0.05951 | 60.7544 | 61.084 | 122.3602 | 122.4472 | -0.073242 | 122.4564 | 61.0703 | -0.18311 | 122.4472 | -0.073242 | 61.0703 | 122.3602 | 122.4564 | -122.6578 | -122.7081
94.5156 | 122.7859 | -60.7864 | 61.7752 | 0.061874 | 0.012416 | 0.01377 | 0.0069172 | 0.061143 | -0.0072033 | 0.066881 | -60.91 | 61.7157 | -60.9421 | -60.9787 | 61.4136 | 0.091553 | 0.004578 | -0.082397 | 61.7798 | -60.9604 | -0.15564 | -0.05951 | -0.1236 | -0.19226 | -0.36163 | -0.17395 | 0.004577 | 0.032044 | 60.791 | 60.704 | 122.2 | 122.5021 | -0.1236 | 122.5662 | 60.878 | -0.17395 | 122.5021 | -0.1236 | 60.878 | 122.2 | 122.5662 | -122.7173 | -122.7356
96.1875 | 122.7264 | -60.791 | 61.8164 | 0.19157 | 0.013911 | 0.0090704 | 0.0052082 | 0.062852 | -0.0057079 | 0.06624 | -60.8597 | 61.7111 | -60.9055 | -60.8917 | 61.5326 | 0.16937 | -0.19226 | 0.036621 | 61.6928 | -60.965 | -0.11444 | -0.10529 | -0.068664 | -0.10071 | -0.28381 | -0.17395 | -0.1236 | 0.045777 | 60.5988 | 60.8276 | 122.3236 | 122.5021 | -0.068664 | 122.4838 | 60.9604 | -0.17395 | 122.5021 | -0.068664 | 60.9604 | 122.3236 | 122.4838 | -122.7219 | -122.7814
97.8438 | 122.8683 | -60.7727 | 61.7065 | 0.031357 | 0.012202 | 0.0054388 | -0.00034604 | 0.059007 | -0.0033581 | 0.066881 | -60.91 | 61.6837 | -60.9009 | -60.9421 | 61.496 | 0.18768 | -0.013733 | 0.16479 | 61.6653 | -60.9467 | -0.12817 | -0.022888 | -0.13733 | -0.16937 | -0.21057 | -0.17395 | -0.041199 | -0.009155 | 60.759 | 60.9375 | 122.2687 | 122.4564 | -0.13733 | 122.438 | 60.9604 | -0.17395 | 122.4564 | -0.13733 | 60.9604 | 122.2687 | 122.438 | -122.6074 | -122.6532
99.5156 | 122.7814 | -60.791 | 61.7798 | 0.13817 | 0.012629 | 0.0069342 | 0.0028584 | 0.060289 | -0.0044263 | 0.066881 | -60.8688 | 61.6699 | -60.9192 | -60.8963 | 61.5234 | 0.17395 | -0.10529 | 0.10986 | 61.6425 | -60.9695 | -0.12817 | -0.10986 | -0.077819 | -0.10529 | -0.25635 | -0.17853 | -0.13733 | 0.050354 | 60.6857 | 60.9009 | 122.3145 | 122.4609 | -0.077819 | 122.4335 | 60.965 | -0.17853 | 122.4609 | -0.077819 | 60.965 | 122.3145 | 122.4335 | -122.699 | -122.7493
101.1719 | 122.7905 | -60.8047 | 61.7935 | 0.11528 | 0.014125 | 0.0086432 | 0.0094806 | 0.061143 | -0.0048535 | 0.070299 | -60.9329 | 61.6974 | -60.9879 | -60.9924 | 61.4136 | 0.086975 | -0.022888 | -0.068665 | 61.7477 | -60.9604 | -0.1831 | -0.09613 | -0.12817 | -0.18768 | -0.37994 | -0.15564 | -0.045776 | 0.054932 | 60.7819 | 60.7361 | 122.2183 | 122.5021 | -0.12817 | 122.5525 | 60.8917 | -0.15564 | 122.5021 | -0.12817 | 60.8917 | 122.2183 | 122.5525 | -122.7814 | -122.7539
102.8438 | 122.8638 | -60.7681 | 61.7752 | -0.25856 | 0.011348 | 0.0090704 | 0.0022174 | 0.057725 | -0.0054943 | 0.068163 | -60.8734 | 61.6745 | -60.9192 | -60.9055 | 61.5051 | 0.22888 | 0.16022 | 0.21515 | 61.7249 | -60.9924 | -0.15106 | -0.10071 | -0.10529 | -0.13733 | -0.27008 | -0.22431 | -0.050354 | 0.045776 | 60.9283 | 60.9833 | 122.2733 | 122.4426 | -0.10529 | 122.493 | 60.997 | -0.22431 | 122.4426 | -0.10529 | 60.997 | 122.2733 | 122.493 | -122.6944 | -122.7676
104.5156 | 122.7402 | -60.8322 | 61.7889 | 0.20683 | 0.012416 | 0.0080024 | 0.0079852 | 0.061143 | -0.0078443 | 0.06859 | -60.878 | 61.6837 | -60.9467 | -60.9055 | 61.5005 | 0.15564 | -0.17853 | 0.013733 | 61.6974 | -60.9375 | -0.11444 | -0.10528 | -0.045777 | -0.073243 | -0.28839 | -0.10529 | -0.091552 | 0.068664 | 60.6537 | 60.8459 | 122.3328 | 122.5159 | -0.045777 | 122.5296 | 60.9879 | -0.10529 | 122.5159 | -0.045777 | 60.9879 | 122.3328 | 122.5296 | -122.7356 | -122.7264
106.1875 | 122.7448 | -60.8368 | 61.8073 | -0.037308 | 0.014125 | 0.010779 | 0.0073444 | 0.06093 | -0.0078443 | 0.068163 | -60.8597 | 61.7065 | -60.91 | -60.9009 | 61.4914 | 0.18768 | -0.004578 | 0.050354 | 61.7294 | -60.9604 | -0.073242 | -0.10071 | -0.022888 | -0.064087 | -0.31586 | -0.1236 | -0.07782 | 0.050354 | 60.8322 | 60.8871 | 122.3282 | 122.5433 | -0.022888 | 122.5662 | 61.0245 | -0.1236 | 122.5433 | -0.022888 | 61.0245 | 122.3282 | 122.5662 | -122.7173 | -122.7676
107.8438 | 122.7127 | -60.8093 | 61.7798 | 0.22209 | 0.012629 | 0.0058662 | 0.0045672 | 0.061143 | -0.0069897 | 0.067736 | -60.8597 | 61.6837 | -60.9283 | -60.8826 | 61.5372 | 0.17395 | -0.21057 | 0.045776 | 61.6745 | -60.9192 | -0.11902 | -0.09613 | -0.050354 | -0.073242 | -0.24261 | -0.10986 | -0.10528 | 0.068665 | 60.5988 | 60.8551 | 122.3465 | 122.493 | -0.050354 | 122.4838 | 60.9833 | -0.10986 | 122.493 | -0.050354 | 60.9833 | 122.3465 | 122.4838 | -122.7081 | -122.699
109.5156 | 122.8363 | -60.7498 | 61.7706 | -0.1899 | 0.011775 | 0.010352 | 8.1156e-05 | 0.060075 | -0.0054943 | 0.067095 | -60.8414 | 61.6653 | -60.91 | -60.8734 | 61.5601 | 0.29297 | 0.064087 | 0.30212 | 61.6791 | -60.9833 | -0.16022 | -0.10529 | -0.091553 | -0.1236 | -0.21057 | -0.23346 | -0.091553 | 0.068664 | 60.8139 | 61.0519 | 122.3099 | 122.4152 | -0.091553 | 122.4289 | 61.0428 | -0.23346 | 122.4152 | -0.091553 | 61.0428 | 122.3099 | 122.4289 | -122.6807 | -122.7539
111.1875 | 122.818 | -60.7819 | 61.7661 | -0.14412 | 0.012629 | 0.0075752 | 0.001363 | 0.058366 | -0.0044263 | 0.06624 | -60.8139 | 61.6837 | -60.8963 | -60.8093 | 61.6058 | 0.3067 | 0.018311 | 0.3067 | 61.6562 | -60.9741 | -0.11444 | -0.082397 | -0.032044 | -0.027466 | -0.16022 | -0.19226 | -0.10986 | 0.082397 | 60.8002 | 61.0886 | 122.3877 | 122.4655 | -0.032044 | 122.438 | 61.0886 | -0.19226 | 122.4655 | -0.032044 | 61.0886 | 122.3877 | 122.438 | -122.6624 | -122.7402
112.8594 | 122.8317 | -60.7498 | 61.7752 | -0.15938 | 0.011348 | 0.010566 | 0.0022174 | 0.056657 | -0.0025037 | 0.067095 | -60.8459 | 61.6608 | -60.9283 | -60.8643 | 61.5601 | 0.30212 | 0.082397 | 0.29755 | 61.6928 | -60.9467 | -0.17853 | -0.11444 | -0.09613 | -0.11444 | -0.21515 | -0.19684 | -0.082398 | 0.082398 | 60.8322 | 61.0474 | 122.3099 | 122.4106 | -0.09613 | 122.4426 | 61.0519 | -0.19684 | 122.4106 | -0.09613 | 61.0519 | 122.3099 | 122.4426 | -122.7036 | -122.7219
114.5312 | 122.7631 | -60.8093 | 61.7706 | 0.13054 | 0.014979 | 0.0058662 | 0.0067036 | 0.061784 | -0.0048535 | 0.067736 | -60.9192 | 61.7203 | -60.9558 | -60.9558 | 61.4594 | 0.09613 | -0.11444 | -0.054932 | 61.7386 | -60.9512 | -0.14648 | -0.050354 | -0.10986 | -0.14648 | -0.31128 | -0.14191 | -0.032044 | 0.036622 | 60.6949 | 60.7544 | 122.2687 | 122.5296 | -0.10986 | 122.5479 | 60.9055 | -0.14191 | 122.5296 | -0.10986 | 60.9055 | 122.2687 | 122.5479 | -122.7264 | -122.7219
116.2031 | 122.7768 | -60.7773 | 61.7798 | 0.1458 | 0.013911 | 0.013343 | 0.0071308 | 0.062425 | -0.0095531 | 0.069445 | -60.9192 | 61.702 | -60.9512 | -60.9695 | 61.441 | 0.091553 | -0.054932 | -0.064087 | 61.7523 | -60.9467 | -0.17395 | -0.07782 | -0.14191 | -0.19226 | -0.33874 | -0.16937 | -0.027466 | 0.032044 | 60.7224 | 60.7132 | 122.2183 | 122.4792 | -0.14191 | 122.5296 | 60.8688 | -0.16937 | 122.4792 | -0.14191 | 60.8688 | 122.2183 | 122.5296 | -122.731 | -122.7264
117.875 | 122.8592 | -60.791 | 61.7523 | -0.2433 | 0.011989 | 0.0075752 | 0.0015766 | 0.058366 | -0.0052807 | 0.068377 | -60.8597 | 61.6653 | -60.9421 | -60.8917 | 61.528 | 0.26093 | 0.14191 | 0.24719 | 61.7111 | -60.9421 | -0.15106 | -0.086975 | -0.068664 | -0.10071 | -0.2243 | -0.15106 | -0.041198 | 0.082398 | 60.9329 | 61.0382 | 122.319 | 122.4564 | -0.068664 | 122.5021 | 61.0519 | -0.15106 | 122.4564 | -0.068664 | 61.0519 | 122.319 | 122.5021 | -122.6944 | -122.6944
119.5938 | 122.8455 | -60.7636 | 61.7477 | 0.038986 | 0.014338 | 0.0060798 | -0.00013244 | 0.060075 | -0.0031445 | 0.067522 | -60.878 | 61.6516 | -60.9146 | -60.9283 | 61.5051 | 0.16937 | -0.050354 | 0.10986 | 61.6928 | -60.965 | -0.15106 | -0.096131 | -0.11444 | -0.16479 | -0.24262 | -0.20142 | -0.054932 | 0.036621 | 60.7132 | 60.8734 | 122.2687 | 122.4152 | -0.11444 | 122.4564 | 60.9329 | -0.20142 | 122.4152 | -0.11444 | 60.9329 | 122.2687 | 122.4564 | -122.6624 | -122.7127
121.25 | 122.7585 | -60.7956 | 61.7981 | -0.0067901 | 0.013911 | 0.0050116 | 0.0088398 | 0.059434 | -0.0072033 | 0.069017 | -60.8734 | 61.7111 | -60.9695 | -60.9283 | 61.4731 | 0.15106 | -0.018311 | 0.004578 | 61.7249 | -60.9238 | -0.17395 | -0.086975 | -0.07782 | -0.13275 | -0.32501 | -0.12817 | -0.073242 | 0.09613 | 60.7773 | 60.8002 | 122.2687 | 122.5067 | -0.07782 | 122.5204 | 60.9467 | -0.12817 | 122.5067 | -0.07782 | 60.9467 | 122.2687 | 122.5204 | -122.7676 | -122.7219
122.9844 | 122.7127 | -60.8047 | 61.7981 | 0.1458 | 0.014125 | 0.010352 | 0.0037128 | 0.059221 | -0.0052807 | 0.067308 | -60.8322 | 61.6791 | -60.8871 | -60.8597 | 61.5372 | 0.1831 | -0.21973 | 0.054932 | 61.6882 | -60.9604 | -0.082397 | -0.11902 | -0.027465 | -0.054931 | -0.26093 | -0.15564 | -0.10986 | 0.054932 | 60.585 | 60.8597 | 122.3419 | 122.4838 | -0.027465 | 122.493 | 60.9879 | -0.15564 | 122.4838 | -0.027465 | 60.9879 | 122.3419 | 122.493 | -122.6852 | -122.7585
124.6562 | 122.8867 | -60.7773 | 61.7615 | -0.20515 | 0.01327 | 0.0073614 | 0.0039264 | 0.059648 | -0.0052807 | 0.066454 | -60.9192 | 61.7157 | -60.9604 | -60.9467 | 61.4594 | 0.21515 | 0.19684 | 0.16937 | 61.7386 | -60.9787 | -0.18311 | -0.045777 | -0.14191 | -0.16937 | -0.30212 | -0.20142 | -0.022889 | 0.041199 | 60.9741 | 60.9467 | 122.2366 | 122.493 | -0.14191 | 122.5159 | 60.9924 | -0.20142 | 122.493 | -0.14191 | 60.9924 | 122.2366 | 122.5159 | -122.7219 | -122.7402
126.3438 | 122.7448 | -60.8414 | 61.7752 | 0.20683 | 0.01028 | 0.0075752 | 0.0032856 | 0.062211 | -0.0063489 | 0.069872 | -60.8139 | 61.6699 | -60.9009 | -60.8551 | 61.5601 | 0.20599 | -0.21057 | 0.09613 | 61.6837 | -60.9238 | -0.059509 | -0.10529 | 0.027466 | -0.013733 | -0.21515 | -0.082397 | -0.091553 | 0.086975 | 60.6308 | 60.9375 | 122.4014 | 122.5113 | 0.027466 | 122.525 | 61.0474 | -0.082397 | 122.5113 | 0.027466 | 61.0474 | 122.4014 | 122.525 | -122.6761 | -122.699
128.0156 | 122.8226 | -60.7819 | 61.7706 | -0.17464 | 0.0092115 | 0.0086432 | 0.0022174 | 0.057939 | -0.0048535 | 0.068804 | -60.8093 | 61.6699 | -60.9055 | -60.8414 | 61.5738 | 0.32501 | 0.027466 | 0.32044 | 61.7111 | -60.9558 | -0.1236 | -0.10071 | -0.027466 | -0.05951 | -0.19684 | -0.17395 | -0.059509 | 0.096131 | 60.8093 | 61.1023 | 122.3557 | 122.4518 | -0.027466 | 122.493 | 61.1069 | -0.17395 | 122.4518 | -0.027466 | 61.1069 | 122.3557 | 122.493 | -122.6761 | -122.7264
129.6719 | 122.731 | -60.8047 | 61.7661 | 0.20683 | 0.011561 | 0.0058662 | 0.0052082 | 0.062211 | -0.0065625 | 0.068804 | -60.8276 | 61.6562 | -60.91 | -60.8505 | 61.528 | 0.19684 | -0.2243 | 0.091553 | 61.6699 | -60.9238 | -0.10529 | -0.10986 | -0.022888 | -0.045776 | -0.23804 | -0.11902 | -0.09613 | 0.082397 | 60.5804 | 60.8963 | 122.3328 | 122.4609 | -0.022888 | 122.4747 | 61.0016 | -0.11902 | 122.4609 | -0.022888 | 61.0016 | 122.3328 | 122.4747 | -122.6761 | -122.6898
131.3438 | 122.7631 | -60.8002 | 61.7615 | 0.1458 | 0.012202 | 0.011207 | 0.0037128 | 0.059648 | -0.0044263 | 0.067736 | -60.8368 | 61.6379 | -60.8734 | -60.9009 | 61.5143 | 0.17853 | -0.13733 | 0.10529 | 61.702 | -60.9467 | -0.073242 | -0.1236 | -0.036621 | -0.10071 | -0.24719 | -0.14648 | -0.05951 | 0.036621 | 60.6628 | 60.9055 | 122.3145 | 122.438 | -0.036621 | 122.5021 | 60.9787 | -0.14648 | 122.438 | -0.036621 | 60.9787 | 122.3145 | 122.5021 | -122.6349 | -122.7081
133.0312 | 122.8592 | -60.7636 | 61.7706 | -0.21278 | 0.012416 | 0.0043708 | 0.0052082 | 0.058152 | -0.0072033 | 0.068804 | -60.9146 | 61.702 | -60.9787 | -60.9604 | 61.4594 | 0.19226 | 0.19226 | 0.14648 | 61.7111 | -60.9787 | -0.21515 | -0.068665 | -0.15106 | -0.19684 | -0.31128 | -0.21515 | -0.059509 | 0.064087 | 60.9558 | 60.91 | 122.2229 | 122.4655 | -0.15106 | 122.4747 | 60.9558 | -0.21515 | 122.4655 | -0.15106 | 60.9558 | 122.2229 | 122.4747 | -122.7493 | -122.7493
134.6875 | 122.8455 | -60.7773 | 61.7615 | 0.077133 | 0.013911 | 0.010779 | 0.00093576 | 0.05858 | -0.0050671 | 0.066454 | -60.8871 | 61.6699 | -60.91 | -60.9146 | 61.5005 | 0.17395 | -0.059509 | 0.12817 | 61.6699 | -60.9375 | -0.13275 | -0.091553 | -0.10986 | -0.13733 | -0.26093 | -0.16022 | -0.091553 | 0.022888 | 60.7178 | 60.9055 | 122.2778 | 122.4472 | -0.10986 | 122.4472 | 60.9512 | -0.16022 | 122.4472 | -0.10986 | 60.9512 | 122.2778 | 122.4472 | -122.6715 | -122.699
136.375 | 122.7493 | -60.8276 | 61.7706 | 0.15343 | 0.011775 | 0.0097114 | 0.0045672 | 0.060502 | -0.0054943 | 0.067949 | -60.8276 | 61.6562 | -60.9192 | -60.8459 | 61.5372 | 0.19684 | -0.19226 | 0.10986 | 61.6745 | -60.9283 | -0.091552 | -0.11444 | 0 | -0.01831 | -0.23346 | -0.10071 | -0.09613 | 0.091552 | 60.6354 | 60.9375 | 122.3648 | 122.4838 | 0 | 122.5021 | 61.0245 | -0.10071 | 122.4838 | 0 | 61.0245 | 122.3648 | 122.5021 | -122.6898 | -122.699
138.0312 | 122.7402 | -60.8231 | 61.8164 | -0.067826 | 0.016261 | 0.0077888 | 0.010976 | 0.060716 | -0.0084851 | 0.068804 | -60.8505 | 61.6928 | -60.9238 | -60.878 | 61.4822 | 0.20142 | -0.009155 | 0.086975 | 61.7249 | -60.9238 | -0.10071 | -0.1236 | -0.027466 | -0.054932 | -0.33417 | -0.10071 | -0.091552 | 0.073242 | 60.8139 | 60.91 | 122.3053 | 122.5159 | -0.027466 | 122.5479 | 61.0245 | -0.10071 | 122.5159 | -0.027466 | 61.0245 | 122.3053 | 122.5479 | -122.7402 | -122.7402
139.7031 | 122.85 | -60.7681 | 61.7661 | 0.077133 | 0.013698 | 0.0090704 | 0.0017902 | 0.060289 | -0.0031445 | 0.068163 | -60.8688 | 61.6653 | -60.8963 | -60.9192 | 61.5189 | 0.17395 | -0.07782 | 0.12817 | 61.6928 | -60.9787 | -0.12817 | -0.10071 | -0.10071 | -0.15106 | -0.24719 | -0.21057 | -0.073242 | 0.027466 | 60.6903 | 60.8963 | 122.287 | 122.4335 | -0.10071 | 122.4609 | 60.9421 | -0.21057 | 122.4335 | -0.10071 | 60.9421 | 122.287 | 122.4609 | -122.6624 | -122.7448
141.375 | 122.8592 | -60.7681 | 61.7889 | -0.26619 | 0.011561 | 0.0039436 | 0.0060626 | 0.057939 | -0.0042127 | 0.067736 | -60.9558 | 61.702 | -60.9467 | -60.9512 | 61.4594 | 0.19226 | 0.21057 | 0.15106 | 61.734 | -60.9695 | -0.17853 | -0.086975 | -0.18768 | -0.18311 | -0.32959 | -0.20142 | -0.054931 | -0.009156 | 60.9787 | 60.9192 | 122.2275 | 122.4701 | -0.18768 | 122.5021 | 60.9604 | -0.20142 | 122.4701 | -0.18768 | 60.9604 | 122.2275 | 122.5021 | -122.7356 | -122.7585
143.0469 | 122.7448 | -60.8139 | 61.7615 | 0.22209 | 0.013911 | 0.0086432 | 0.007558 | 0.059648 | -0.0059217 | 0.066881 | -60.8917 | 61.7249 | -60.9238 | -60.91 | 61.4822 | 0.13733 | -0.16937 | -0.004578 | 61.7294 | -60.9558 | -0.10986 | -0.036621 | -0.07782 | -0.09613 | -0.27924 | -0.14191 | -0.032044 | 0.032043 | 60.6445 | 60.8093 | 122.2961 | 122.5388 | -0.07782 | 122.5433 | 60.9512 | -0.14191 | 122.5388 | -0.07782 | 60.9512 | 122.2961 | 122.5433 | -122.6852 | -122.7173
144.7188 | 122.8271 | -60.7773 | 61.7889 | -0.22041 | 0.012629 | 0.010139 | 0.0020038 | 0.058366 | -0.0048535 | 0.066668 | -60.8459 | 61.6562 | -60.9055 | -60.8322 | 61.5875 | 0.29755 | 0.027466 | 0.32501 | 61.6653 | -60.9421 | -0.12817 | -0.13275 | -0.068664 | -0.054931 | -0.20142 | -0.1648 | -0.1236 | 0.05951 | 60.8047 | 61.1023 | 122.3648 | 122.4335 | -0.068664 | 122.4426 | 61.0748 | -0.1648 | 122.4335 | -0.068664 | 61.0748 | 122.3648 | 122.4426 | -122.6944 | -122.731
146.3906 | 122.8043 | -60.7498 | 61.7798 | -0.20515 | 0.011989 | 0.0073614 | 0.0084126 | 0.059861 | -0.0065625 | 0.066881 | -60.8871 | 61.702 | -60.9695 | -60.9009 | 61.496 | 0.23346 | 0.086975 | 0.12817 | 61.7523 | -60.9375 | -0.21973 | -0.07782 | -0.13733 | -0.15106 | -0.28381 | -0.18768 | -0.027466 | 0.082397 | 60.8368 | 60.878 | 122.2458 | 122.4518 | -0.13733 | 122.5021 | 60.9833 | -0.18768 | 122.4518 | -0.13733 | 60.9833 | 122.2458 | 122.5021 | -122.7493 | -122.7173
148.0625 | 122.7676 | -60.791 | 61.7844 | 0.13054 | 0.013057 | 0.011207 | 0.0052082 | 0.059221 | -0.0065625 | 0.067949 | -60.9055 | 61.6974 | -60.9329 | -60.9512 | 61.4639 | 0.10529 | -0.11444 | -0.045776 | 61.7157 | -60.9558 | -0.14191 | -0.086975 | -0.11444 | -0.16022 | -0.32043 | -0.16479 | -0.068665 | 0.027465 | 60.6766 | 60.7452 | 122.2549 | 122.4884 | -0.11444 | 122.5067 | 60.8963 | -0.16479 | 122.4884 | -0.11444 | 60.8963 | 122.2549 | 122.5067 | -122.7173 | -122.7402
149.7344 | 122.8683 | -60.7544 | 61.7432 | 0.031357 | 0.013698 | 0.0056524 | -0.00077324 | 0.059648 | -0.0037853 | 0.066668 | -60.878 | 61.6653 | -60.9192 | -60.9192 | 61.5051 | 0.16022 | -0.050354 | 0.12817 | 61.6882 | -60.9558 | -0.16479 | -0.07782 | -0.1236 | -0.16479 | -0.23804 | -0.20142 | -0.054932 | 0.041198 | 60.704 | 60.8826 | 122.2595 | 122.4197 | -0.1236 | 122.4426 | 60.9146 | -0.20142 | 122.4197 | -0.1236 | 60.9146 | 122.2595 | 122.4426 | -122.6624 | -122.699
151.4531 | 122.8134 | -60.7636 | 61.7432 | -0.19753 | 0.012202 | 0.0058662 | 0.003072 | 0.05623 | -0.0050671 | 0.067095 | -60.8276 | 61.6653 | -60.9009 | -60.8368 | 61.5784 | 0.3067 | 0.032043 | 0.31586 | 61.6653 | -60.9695 | -0.13733 | -0.07782 | -0.064087 | -0.073242 | -0.16479 | -0.20599 | -0.07782 | 0.073242 | 60.7956 | 61.0794 | 122.3419 | 122.4289 | -0.064087 | 122.4289 | 61.0703 | -0.20599 | 122.4289 | -0.064087 | 61.0703 | 122.3419 | 122.4289 | -122.644 | -122.7127
153.125 | 122.8271 | -60.7773 | 61.7615 | -0.18227 | 0.014338 | 0.0084296 | 0.0079852 | 0.060716 | -0.0082715 | 0.071154 | -60.8871 | 61.6974 | -60.965 | -60.9055 | 61.4914 | 0.23346 | 0.10529 | 0.13275 | 61.7386 | -60.9741 | -0.18768 | -0.064087 | -0.10986 | -0.12817 | -0.27008 | -0.19684 | -0.022889 | 0.07782 | 60.8826 | 60.91 | 122.2687 | 122.4747 | -0.10986 | 122.5159 | 61.0107 | -0.19684 | 122.4747 | -0.10986 | 61.0107 | 122.2687 | 122.5159 | -122.7264 | -122.7356
154.8281 | 122.7722 | -60.7956 | 61.7706 | 0.13817 | 0.014979 | 0.0090704 | 0.0056354 | 0.061998 | -0.0059217 | 0.067949 | -60.9146 | 61.7477 | -60.9467 | -60.965 | 61.441 | 0.10986 | -0.082397 | -0.054932 | 61.734 | -60.9512 | -0.15106 | -0.022888 | -0.11902 | -0.16937 | -0.32959 | -0.15564 | -0.036621 | 0.032043 | 60.7132 | 60.7407 | 122.2366 | 122.5433 | -0.11902 | 122.5296 | 60.9055 | -0.15564 | 122.5433 | -0.11902 | 60.9055 | 122.2366 | 122.5296 | -122.7173 | -122.7219
156.5 | 122.8409 | -60.7819 | 61.7523 | 0.031357 | 0.013484 | 0.0077888 | -0.00013244 | 0.059007 | -0.0048535 | 0.068377 | -60.9055 | 61.7157 | -60.9146 | -60.9329 | 61.5097 | 0.17395 | -0.054932 | 0.11902 | 61.6699 | -60.9741 | -0.13275 | -0.036621 | -0.1236 | -0.15106 | -0.24261 | -0.19226 | -0.082397 | 0.009155 | 60.7269 | 60.9009 | 122.2916 | 122.4976 | -0.1236 | 122.4518 | 60.9558 | -0.19226 | 122.4976 | -0.1236 | 60.9558 | 122.2916 | 122.4518 | -122.6669 | -122.7264
158.1719 | 122.7859 | -60.7819 | 61.7889 | 0.1458 | 0.012629 | 0.0080024 | 0.0062762 | 0.06157 | -0.0069897 | 0.070086 | -60.9192 | 61.7111 | -60.9741 | -60.9741 | 61.4365 | 0.10071 | -0.050354 | -0.068665 | 61.734 | -60.9512 | -0.19226 | -0.077819 | -0.13733 | -0.19226 | -0.35248 | -0.16937 | -0.054931 | 0.054932 | 60.7315 | 60.7132 | 122.2183 | 122.493 | -0.13733 | 122.5159 | 60.8826 | -0.16937 | 122.493 | -0.13733 | 60.8826 | 122.2183 | 122.5159 | -122.7631 | -122.7402
159.8438 | 122.8455 | -60.7498 | 61.7477 | -0.1899 | 0.012629 | 0.003089 | 0.003072 | 0.057725 | -0.0069897 | 0.065386 | -60.8414 | 61.6974 | -60.9146 | -60.8688 | 61.5601 | 0.27466 | 0.10986 | 0.3067 | 61.702 | -60.965 | -0.16479 | -0.050354 | -0.091553 | -0.11902 | -0.18768 | -0.21515 | -0.045777 | 0.073242 | 60.8597 | 61.0565 | 122.3099 | 122.4472 | -0.091553 | 122.4518 | 61.0245 | -0.21515 | 122.4472 | -0.091553 | 61.0245 | 122.3099 | 122.4518 | -122.6624 | -122.7127
161.5156 | 122.7356 | -60.8139 | 61.8118 | 0.17632 | 0.013057 | 0.014197 | 0.0054218 | 0.060075 | -0.0052807 | 0.067949 | -60.8231 | 61.702 | -60.9146 | -60.8551 | 61.5417 | 0.18768 | -0.21515 | 0.064087 | 61.702 | -60.9329 | -0.10071 | -0.10986 | -0.009155 | -0.041199 | -0.27008 | -0.11902 | -0.10986 | 0.091553 | 60.5988 | 60.878 | 122.3557 | 122.5159 | -0.009155 | 122.5159 | 61.0016 | -0.11902 | 122.5159 | -0.009155 | 61.0016 | 122.3557 | 122.5159 | -122.7264 | -122.7448
163.1875 | 122.8271 | -60.7681 | 61.7844 | -0.22041 | 0.012416 | 0.0075752 | 0.0032856 | 0.057298 | -0.0057079 | 0.067308 | -60.8322 | 61.6745 | -60.91 | -60.8368 | 61.5738 | 0.3067 | 0.022888 | 0.32044 | 61.6562 | -60.9283 | -0.14191 | -0.10986 | -0.064087 | -0.068665 | -0.21057 | -0.16022 | -0.12817 | 0.07782 | 60.791 | 61.0886 | 122.3419 | 122.4426 | -0.064087 | 122.4243 | 61.0748 | -0.16022 | 122.4426 | -0.064087 | 61.0748 | 122.3419 | 122.4243 | -122.6944 | -122.7127
164.8594 | 122.7402 | -60.8139 | 61.8164 | -0.098343 | 0.014125 | 0.010993 | 0.0088398 | 0.060502 | -0.0065625 | 0.064104 | -60.8597 | 61.7294 | -60.9604 | -60.8963 | 61.5143 | 0.2243 | 0.013733 | 0.11902 | 61.7523 | -60.9375 | -0.14648 | -0.086975 | -0.045776 | -0.082397 | -0.30212 | -0.1236 | -0.064087 | 0.10071 | 60.8276 | 60.9329 | 122.3282 | 122.5433 | -0.045776 | 122.5662 | 61.0382 | -0.1236 | 122.5433 | -0.045776 | 61.0382 | 122.3282 | 122.5662 | -122.7768 | -122.7539
166.5312 | 122.8683 | -60.7498 | 61.734 | 0.046615 | 0.012629 | 0.0088568 | -0.00098684 | 0.059648 | -0.0033581 | 0.066454 | -60.8917 | 61.6882 | -60.9375 | -60.9238 | 61.496 | 0.16937 | -0.036621 | 0.12817 | 61.7111 | -60.9558 | -0.18768 | -0.045777 | -0.14191 | -0.17395 | -0.23804 | -0.20599 | -0.022888 | 0.045776 | 60.7132 | 60.878 | 122.2458 | 122.438 | -0.14191 | 122.4609 | 60.9192 | -0.20599 | 122.438 | -0.14191 | 60.9192 | 122.2458 | 122.4609 | -122.6715 | -122.6898
168.2031 | 122.7631 | -60.8047 | 61.8073 | 0.016098 | 0.01327 | 0.0056524 | 0.010762 | 0.06093 | -0.0074169 | 0.069445 | -60.8963 | 61.7065 | -60.9741 | -60.9238 | 61.4502 | 0.15564 | -0.022888 | -0.013733 | 61.7111 | -60.9512 | -0.16937 | -0.10071 | -0.091552 | -0.11902 | -0.35706 | -0.14648 | -0.09613 | 0.07782 | 60.7819 | 60.791 | 122.2549 | 122.5113 | -0.091552 | 122.5159 | 60.9604 | -0.14648 | 122.5113 | -0.091552 | 60.9604 | 122.2549 | 122.5159 | -122.7814 | -122.7585
169.8594 | 122.8363 | -60.7452 | 61.7569 | -0.17464 | 0.011775 | 0.004798 | 0.00093576 | 0.061357 | -0.0057079 | 0.065813 | -60.8459 | 61.6653 | -60.9375 | -60.8734 | 61.5417 | 0.3067 | 0.091553 | 0.29755 | 61.7111 | -60.9512 | -0.19226 | -0.091553 | -0.10071 | -0.12817 | -0.21515 | -0.20599 | -0.045776 | 0.091553 | 60.8368 | 61.0428 | 122.287 | 122.4106 | -0.10071 | 122.4564 | 61.0519 | -0.20599 | 122.4106 | -0.10071 | 61.0519 | 122.287 | 122.4564 | -122.6944 | -122.7081
171.5156 | 122.7356 | -60.7773 | 61.8073 | -0.1136 | 0.014125 | 0.0094978 | 0.0077716 | 0.060716 | -0.0035717 | 0.068377 | -60.8734 | 61.7111 | -60.9512 | -60.8917 | 61.496 | 0.22888 | 0.036621 | 0.10986 | 61.7432 | -60.9329 | -0.17395 | -0.09613 | -0.09613 | -0.11444 | -0.31128 | -0.15564 | -0.064087 | 0.07782 | 60.8139 | 60.8871 | 122.2733 | 122.4884 | -0.09613 | 122.5204 | 61.0062 | -0.15564 | 122.4884 | -0.09613 | 61.0062 | 122.2733 | 122.5204 | -122.7585 | -122.7402
173.1875 | 122.8683 | -60.7727 | 61.7386 | 0.016098 | 0.013911 | 0.0052252 | 0.00050836 | 0.059861 | -0.0039989 | 0.069017 | -60.8917 | 61.6745 | -60.9009 | -60.9283 | 61.5143 | 0.1831 | -0.032043 | 0.16479 | 61.6928 | -60.9695 | -0.12817 | -0.064086 | -0.11902 | -0.15564 | -0.2243 | -0.19684 | -0.045776 | 0.009155 | 60.7407 | 60.9375 | 122.287 | 122.4472 | -0.11902 | 122.4655 | 60.9558 | -0.19684 | 122.4472 | -0.11902 | 60.9558 | 122.287 | 122.4655 | -122.6395 | -122.7081
174.8438 | 122.8134 | -60.7773 | 61.7798 | -0.1899 | 0.014552 | 0.011634 | 0.0071308 | 0.060716 | -0.0052807 | 0.067308 | -60.8917 | 61.7249 | -60.9833 | -60.8963 | 61.5005 | 0.23346 | 0.086975 | 0.13275 | 61.7432 | -60.965 | -0.20599 | -0.054931 | -0.11444 | -0.11902 | -0.27924 | -0.18768 | -0.036621 | 0.091552 | 60.8643 | 60.91 | 122.2778 | 122.5021 | -0.11444 | 122.5204 | 61.0107 | -0.18768 | 122.5021 | -0.11444 | 61.0107 | 122.2778 | 122.5204 | -122.7631 | -122.7448
176.5156 | 122.7722 | -60.8047 | 61.7661 | 0.1458 | 0.014125 | 0.0077888 | 0.0022174 | 0.059221 | -0.0033581 | 0.067308 | -60.8551 | 61.6745 | -60.9055 | -60.8963 | 61.528 | 0.17395 | -0.11444 | 0.1236 | 61.6791 | -60.9375 | -0.10071 | -0.091552 | -0.050354 | -0.091552 | -0.23804 | -0.13275 | -0.086975 | 0.050354 | 60.6903 | 60.9283 | 122.3328 | 122.4792 | -0.050354 | 122.4838 | 60.9787 | -0.13275 | 122.4792 | -0.050354 | 60.9787 | 122.3328 | 122.4838 | -122.6715 | -122.7036
178.1875 | 122.8088 | -60.7819 | 61.7752 | -0.18227 | 0.012202 | 0.0054388 | 0.0034992 | 0.059007 | -0.0057079 | 0.067522 | -60.8047 | 61.6882 | -60.9329 | -60.8414 | 61.5738 | 0.31128 | 0.022888 | 0.33417 | 61.7065 | -60.9421 | -0.15106 | -0.086976 | -0.022889 | -0.05951 | -0.20142 | -0.16022 | -0.068665 | 0.12817 | 60.8047 | 61.116 | 122.3557 | 122.4701 | -0.022889 | 122.4884 | 61.0931 | -0.16022 | 122.4701 | -0.022889 | 61.0931 | 122.3557 | 122.4884 | -122.7081 | -122.7173
179.8438 | 122.85 | -60.7681 | 61.7661 | -0.2433 | 0.013698 | 0.0028754 | 0.004781 | 0.057939 | -0.0044263 | 0.067949 | -60.878 | 61.6974 | -60.9512 | -60.9009 | 61.496 | 0.23346 | 0.15106 | 0.2243 | 61.7111 | -60.9833 | -0.18311 | -0.068664 | -0.10986 | -0.13275 | -0.27008 | -0.21515 | -0.054931 | 0.073242 | 60.9192 | 60.9924 | 122.2641 | 122.4655 | -0.10986 | 122.4792 | 61.0016 | -0.21515 | 122.4655 | -0.10986 | 61.0016 | 122.2641 | 122.4792 | -122.7173 | -122.7493
181.5312 | 122.8409 | -60.7727 | 61.7798 | -0.1899 | 0.012629 | 0.0071478 | 0.0069172 | 0.059861 | -0.0059217 | 0.067308 | -60.9238 | 61.734 | -60.9604 | -60.9055 | 61.4868 | 0.21973 | 0.11444 | 0.13733 | 61.734 | -60.9833 | -0.18768 | -0.045776 | -0.15106 | -0.13275 | -0.29297 | -0.21057 | -0.045776 | 0.036621 | 60.8871 | 60.91 | 122.2595 | 122.5067 | -0.15106 | 122.5067 | 60.9924 | -0.21057 | 122.5067 | -0.15106 | 60.9924 | 122.2595 | 122.5067 | -122.7402 | -122.7631
183.1875 | 122.7539 | -60.8093 | 61.7844 | -0.052567 | 0.011775 | 0.0045844 | 0.0079852 | 0.06093 | -0.0061353 | 0.068804 | -60.8459 | 61.6882 | -60.9283 | -60.9009 | 61.5097 | 0.20142 | 0 | 0.068665 | 61.7294 | -60.9238 | -0.11902 | -0.096131 | -0.036621 | -0.091553 | -0.27466 | -0.11444 | -0.054932 | 0.082398 | 60.8093 | 60.878 | 122.319 | 122.4976 | -0.036621 | 122.5388 | 61.0107 | -0.11444 | 122.4976 | -0.036621 | 61.0107 | 122.319 | 122.5388 | -122.7127 | -122.7081
184.8594 | 122.7264 | -60.8231 | 61.7661 | 0.22972 | 0.014338 | 0.0094978 | 0.0043536 | 0.060075 | -0.0052807 | 0.069231 | -60.8093 | 61.6745 | -60.8963 | -60.8597 | 61.5417 | 0.20142 | -0.22888 | 0.09613 | 61.6974 | -60.9512 | -0.073242 | -0.091552 | 0.013733 | -0.036621 | -0.2243 | -0.12817 | -0.068664 | 0.086975 | 60.5942 | 60.9192 | 122.3648 | 122.4976 | 0.013733 | 122.5204 | 61.0245 | -0.12817 | 122.4976 | 0.013733 | 61.0245 | 122.3648 | 122.5204 | -122.6624 | -122.7173
186.5312 | 122.7905 | -60.7956 | 61.7798 | 0.1458 | 0.012202 | 0.010779 | 0.0079852 | 0.062211 | -0.0067761 | 0.067736 | -60.9375 | 61.7249 | -60.965 | -60.9741 | 61.4319 | 0.10071 | -0.032043 | -0.054932 | 61.7661 | -60.9467 | -0.16937 | -0.054931 | -0.14191 | -0.17853 | -0.3479 | -0.15106 | -0.013733 | 0.027466 | 60.7635 | 60.7407 | 122.2275 | 122.5204 | -0.14191 | 122.5616 | 60.8963 | -0.15106 | 122.5204 | -0.14191 | 60.8963 | 122.2275 | 122.5616 | -122.7448 | -122.7264
188.2031 | 122.8088 | -60.7956 | 61.7844 | -0.16701 | 0.010921 | 0.009284 | 0.0017902 | 0.057298 | -0.0042127 | 0.068804 | -60.8231 | 61.6837 | -60.8963 | -60.8551 | 61.5738 | 0.3067 | 0.027466 | 0.32044 | 61.6745 | -60.9421 | -0.10071 | -0.10071 | -0.027466 | -0.05951 | -0.21057 | -0.14649 | -0.10986 | 0.073242 | 60.8231 | 61.116 | 122.3694 | 122.4792 | -0.027466 | 122.4701 | 61.1023 | -0.14649 | 122.4792 | -0.027466 | 61.1023 | 122.3694 | 122.4701 | -122.6807 | -122.7264
189.875 | 122.7905 | -60.8047 | 61.7706 | 0.13817 | 0.014552 | 0.0056524 | 0.009267 | 0.059861 | -0.0054943 | 0.068804 | -60.9146 | 61.7203 | -60.9375 | -60.9787 | 61.441 | 0.10529 | -0.036621 | -0.073242 | 61.7386 | -60.9879 | -0.13275 | -0.050354 | -0.10986 | -0.17395 | -0.32959 | -0.1831 | -0.032044 | 0.022888 | 60.7681 | 60.7315 | 122.2458 | 122.525 | -0.10986 | 122.5433 | 60.91 | -0.1831 | 122.525 | -0.10986 | 60.91 | 122.2458 | 122.5433 | -122.7081 | -122.7585
191.5469 | 122.8546 | -60.7773 | 61.7615 | -0.23567 | 0.014338 | 0.010779 | 0.0026446 | 0.060502 | -0.0052807 | 0.067736 | -60.8459 | 61.6974 | -60.91 | -60.8917 | 61.5326 | 0.27466 | 0.13275 | 0.27008 | 61.7249 | -60.9787 | -0.13275 | -0.064087 | -0.068664 | -0.11444 | -0.22888 | -0.20142 | -0.036621 | 0.064087 | 60.91 | 61.0474 | 122.3099 | 122.4747 | -0.068664 | 122.5021 | 61.0519 | -0.20142 | 122.4747 | -0.068664 | 61.0519 | 122.3099 | 122.5021 | -122.6715 | -122.7402
193.2031 | 122.7585 | -60.8093 | 61.7798 | 0.15343 | 0.012629 | 0.004798 | 0.00414 | 0.059861 | -0.0050671 | 0.067095 | -60.8368 | 61.6379 | -60.9421 | -60.8826 | 61.5463 | 0.19684 | -0.17853 | 0.11444 | 61.7065 | -60.9467 | -0.13275 | -0.14191 | -0.027466 | -0.073242 | -0.23346 | -0.13733 | -0.073242 | 0.10529 | 60.6308 | 60.9238 | 122.3557 | 122.4472 | -0.027466 | 122.5159 | 61.0062 | -0.13733 | 122.4472 | -0.027466 | 61.0062 | 122.3557 | 122.5159 | -122.7219 | -122.7264
194.8594 | 122.85 | -60.7452 | 61.7752 | -0.21278 | 0.010066 | 0.0028754 | 0.0026446 | 0.05858 | -0.0044263 | 0.066454 | -60.8826 | 61.734 | -60.9238 | -60.9192 | 61.4822 | 0.22888 | 0.1831 | 0.20599 | 61.7294 | -60.9741 | -0.17853 | -0.041199 | -0.13733 | -0.17395 | -0.29297 | -0.22888 | -0.045777 | 0.041199 | 60.9283 | 60.9512 | 122.2275 | 122.4792 | -0.13733 | 122.4747 | 60.9741 | -0.22888 | 122.4792 | -0.13733 | 60.9741 | 122.2275 | 122.4747 | -122.699 | -122.7493
196.5312 | 122.7219 | -60.7956 | 61.7981 | 0.18394 | 0.012416 | 0.0054388 | 0.0043536 | 0.061784 | -0.0063489 | 0.067949 | -60.8276 | 61.6699 | -60.91 | -60.8597 | 61.5326 | 0.19684 | -0.21973 | 0.07782 | 61.6974 | -60.9512 | -0.11444 | -0.12817 | -0.032044 | -0.064087 | -0.2655 | -0.15564 | -0.10071 | 0.082397 | 60.5759 | 60.8734 | 122.3282 | 122.4655 | -0.032044 | 122.493 | 60.9924 | -0.15564 | 122.4655 | -0.032044 | 60.9924 | 122.3282 | 122.493 | -122.7081 | -122.7493
198.2031 | 122.7448 | -60.7956 | 61.8073 | -0.044937 | 0.013911 | 0.009284 | 0.0090534 | 0.061998 | -0.0059217 | 0.067522 | -60.878 | 61.7111 | -60.965 | -60.9192 | 61.4777 | 0.1831 | -0.004578 | 0.041199 | 61.7203 | -60.9695 | -0.16937 | -0.09613 | -0.082398 | -0.1236 | -0.32959 | -0.17395 | -0.086975 | 0.086975 | 60.791 | 60.8368 | 122.2733 | 122.5067 | -0.082398 | 122.5159 | 60.9787 | -0.17395 | 122.5067 | -0.082398 | 60.9787 | 122.2733 | 122.5159 | -122.7722 | -122.7768
199.8594 | 122.8043 | -60.7773 | 61.7615 | -0.18227 | 0.014552 | 0.0086432 | 0.0026446 | 0.059007 | -0.0065625 | 0.067095 | -60.8185 | 61.6745 | -60.8688 | -60.8459 | 61.5738 | 0.30212 | 0.027466 | 0.32044 | 61.702 | -60.965 | -0.091552 | -0.086975 | -0.041198 | -0.068664 | -0.18768 | -0.18768 | -0.05951 | 0.050354 | 60.8047 | 61.0977 | 122.3511 | 122.4518 | -0.041198 | 122.4792 | 61.0794 | -0.18768 | 122.4518 | -0.041198 | 61.0794 | 122.3511 | 122.4792 | -122.6303 | -122.7264
201.5156 | 122.7585 | -60.8047 | 61.7935 | 0.0084684 | 0.012843 | 0.012275 | 0.0079852 | 0.058366 | -0.0074169 | 0.069017 | -60.8826 | 61.7249 | -60.9604 | -60.9283 | 61.4594 | 0.14648 | -0.013733 | 0.009155 | 61.7203 | -60.9558 | -0.15564 | -0.068664 | -0.077819 | -0.1236 | -0.33417 | -0.15106 | -0.073242 | 0.07782 | 60.791 | 60.8139 | 122.2641 | 122.5296 | -0.077819 | 122.525 | 60.9512 | -0.15106 | 122.5296 | -0.077819 | 60.9512 | 122.2641 | 122.525 | -122.7539 | -122.7493
203.1719 | 122.7493 | -60.8139 | 61.7752 | 0.13817 | 0.014338 | 0.009284 | 0.0026446 | 0.06093 | -0.0054943 | 0.06859 | -60.8459 | 61.6562 | -60.91 | -60.8917 | 61.528 | 0.17395 | -0.15564 | 0.11902 | 61.6882 | -60.9467 | -0.09613 | -0.11902 | -0.032043 | -0.07782 | -0.24719 | -0.13275 | -0.086976 | 0.064087 | 60.6583 | 60.9329 | 122.3419 | 122.4701 | -0.032043 | 122.5021 | 60.9879 | -0.13275 | 122.4701 | -0.032043 | 60.9879 | 122.3419 | 122.5021 | -122.6852 | -122.7219
204.8438 | 122.7905 | -60.791 | 61.7844 | -0.14412 | 0.012416 | 0.008216 | 0.0073444 | 0.06157 | -0.0076305 | 0.066027 | -60.878 | 61.6928 | -60.9604 | -60.9192 | 61.5005 | 0.22888 | 0.054932 | 0.13275 | 61.7523 | -60.965 | -0.16937 | -0.091553 | -0.086975 | -0.12817 | -0.28381 | -0.17395 | -0.032044 | 0.082397 | 60.8459 | 60.9238 | 122.2916 | 122.4838 | -0.086975 | 122.5433 | 61.0199 | -0.17395 | 122.4838 | -0.086975 | 61.0199 | 122.2916 | 122.5433 | -122.7448 | -122.7493
206.5156 | 122.7219 | -60.8505 | 61.7706 | 0.20683 | 0.011989 | 0.011848 | 0.0034992 | 0.060075 | -0.0065625 | 0.067522 | -60.8139 | 61.702 | -60.9055 | -60.8505 | 61.5555 | 0.19226 | -0.21515 | 0.11444 | 61.6882 | -60.9467 | -0.054932 | -0.068665 | 0.036621 | 0 | -0.21515 | -0.09613 | -0.082398 | 0.091553 | 60.6354 | 60.965 | 122.406 | 122.5525 | 0.036621 | 122.5388 | 61.0428 | -0.09613 | 122.5525 | 0.036621 | 61.0428 | 122.406 | 122.5388 | -122.6761 | -122.7173
208.1875 | 122.8638 | -60.7727 | 61.7432 | 0.016098 | 0.011134 | 0.0080024 | 0.0020038 | 0.058366 | -0.0050671 | 0.069017 | -60.9009 | 61.6928 | -60.9146 | -60.9192 | 61.5051 | 0.20142 | 0 | 0.1831 | 61.6791 | -60.9879 | -0.14191 | -0.050354 | -0.12817 | -0.14648 | -0.23804 | -0.21515 | -0.064087 | 0.013733 | 60.7727 | 60.9558 | 122.2778 | 122.4655 | -0.12817 | 122.4518 | 60.9741 | -0.21515 | 122.4655 | -0.12817 | 60.9741 | 122.2778 | 122.4518 | -122.6578 | -122.731
209.8594 | 122.7814 | -60.7864 | 61.7798 | 0.15343 | 0.012629 | 0.0088568 | 0.0049946 | 0.060289 | -0.0057079 | 0.069445 | -60.8643 | 61.6562 | -60.9467 | -60.8871 | 61.5005 | 0.17395 | -0.10529 | 0.1236 | 61.6974 | -60.9467 | -0.16022 | -0.1236 | -0.07782 | -0.10071 | -0.27924 | -0.16022 | -0.082397 | 0.082397 | 60.6812 | 60.91 | 122.287 | 122.4426 | -0.07782 | 122.4838 | 60.9604 | -0.16022 | 122.4426 | -0.07782 | 60.9604 | 122.287 | 122.4838 | -122.7264 | -122.7264
211.5469 | 122.7722 | -60.7956 | 61.7935 | 0.10002 | 0.01327 | 0.008216 | 0.0094806 | 0.06157 | -0.0063489 | 0.067949 | -60.8963 | 61.7294 | -60.9558 | -60.9421 | 61.4456 | 0.10986 | -0.082397 | -0.050354 | 61.7661 | -60.9558 | -0.16022 | -0.064087 | -0.10071 | -0.14649 | -0.3479 | -0.16022 | -0.027466 | 0.05951 | 60.7132 | 60.7452 | 122.2412 | 122.525 | -0.10071 | 122.5616 | 60.9055 | -0.16022 | 122.525 | -0.10071 | 60.9055 | 122.2412 | 122.5616 | -122.7493 | -122.7493
213.2188 | 122.8226 | -60.7727 | 61.7752 | -0.1136 | 0.011775 | 0.0086432 | 0.0026446 | 0.056871 | -0.0050671 | 0.067095 | -60.8231 | 61.6653 | -60.9055 | -60.8322 | 61.6058 | 0.29297 | 0.022888 | 0.33417 | 61.6928 | -60.9512 | -0.13275 | -0.10986 | -0.050354 | -0.059509 | -0.16937 | -0.17853 | -0.082398 | 0.082398 | 60.7956 | 61.1069 | 122.3785 | 122.438 | -0.050354 | 122.4655 | 61.0657 | -0.17853 | 122.438 | -0.050354 | 61.0657 | 122.3785 | 122.4655 | -122.6807 | -122.7264
214.9375 | 122.7768 | -60.8002 | 61.7889 | 0.13817 | 0.014125 | 0.010993 | 0.007558 | 0.060075 | -0.0046399 | 0.066881 | -60.9238 | 61.7065 | -60.9833 | -60.9467 | 61.441 | 0.09613 | -0.091553 | -0.041199 | 61.734 | -60.9695 | -0.1831 | -0.082397 | -0.1236 | -0.14648 | -0.3479 | -0.16937 | -0.054931 | 0.059509 | 60.7086 | 60.759 | 122.2412 | 122.5067 | -0.1236 | 122.5342 | 60.8963 | -0.16937 | 122.5067 | -0.1236 | 60.8963 | 122.2412 | 122.5342 | -122.7722 | -122.7585
216.6094 | 122.7448 | -60.8185 | 61.8164 | -0.022049 | 0.012202 | 0.013984 | 0.0067036 | 0.060075 | -0.0061353 | 0.071367 | -60.878 | 61.7157 | -60.9467 | -60.91 | 61.4731 | 0.16937 | -0.018311 | 0.041199 | 61.7569 | -60.9695 | -0.12817 | -0.10071 | -0.05951 | -0.091553 | -0.34332 | -0.15106 | -0.059509 | 0.068664 | 60.8002 | 60.8597 | 122.2916 | 122.5342 | -0.05951 | 122.5754 | 60.9879 | -0.15106 | 122.5342 | -0.05951 | 60.9879 | 122.2916 | 122.5754 | -122.7631 | -122.7859
218.2969 | 122.8546 | -60.7681 | 61.7798 | -0.17464 | 0.012843 | 0.011848 | 0.0022174 | 0.059648 | -0.0067761 | 0.067949 | -60.8459 | 61.7249 | -60.91 | -60.8688 | 61.5509 | 0.29297 | 0.086975 | 0.31586 | 61.7111 | -60.965 | -0.14191 | -0.054931 | -0.07782 | -0.10071 | -0.22888 | -0.19684 | -0.068664 | 0.064087 | 60.8551 | 61.084 | 122.319 | 122.493 | -0.07782 | 122.4792 | 61.0611 | -0.19684 | 122.493 | -0.07782 | 61.0611 | 122.319 | 122.4792 | -122.6898 | -122.7448
220.0156 | 122.7814 | -60.7681 | 61.7798 | 0.11528 | 0.013484 | 0.0052252 | 0.0054218 | 0.060716 | -0.0080579 | 0.068804 | -60.9375 | 61.7157 | -60.9695 | -60.965 | 61.4319 | 0.09613 | -0.036621 | -0.050354 | 61.7615 | -60.9512 | -0.20142 | -0.064087 | -0.16937 | -0.19684 | -0.3479 | -0.18311 | -0.01831 | 0.032043 | 60.7315 | 60.7178 | 122.2 | 122.4838 | -0.16937 | 122.5296 | 60.8643 | -0.18311 | 122.4838 | -0.16937 | 60.8643 | 122.2 | 122.5296 | -122.7493 | -122.731
221.6875 | 122.8409 | -60.7681 | 61.7432 | -0.044937 | 0.012202 | 0.0067206 | -0.00055964 | 0.058366 | -0.0035717 | 0.068163 | -60.8688 | 61.6699 | -60.9146 | -60.8871 | 61.5417 | 0.25635 | -0.004578 | 0.25177 | 61.7111 | -60.9512 | -0.14648 | -0.073242 | -0.10071 | -0.11902 | -0.20142 | -0.18311 | -0.032043 | 0.045777 | 60.7635 | 61.0199 | 122.3099 | 122.438 | -0.10071 | 122.4792 | 61.0245 | -0.18311 | 122.438 | -0.10071 | 61.0245 | 122.3099 | 122.4792 | -122.6578 | -122.6944
223.3594 | 122.8683 | -60.7681 | 61.7798 | -0.17464 | 0.01327 | 0.0073614 | 0.0060626 | 0.05858 | -0.0063489 | 0.067308 | -60.9329 | 61.7111 | -60.965 | -60.9512 | 61.4594 | 0.21515 | 0.16937 | 0.15106 | 61.7569 | -60.965 | -0.19684 | -0.068664 | -0.16479 | -0.18311 | -0.32043 | -0.19684 | -0.022888 | 0.032044 | 60.9375 | 60.9192 | 122.2275 | 122.4792 | -0.16479 | 122.525 | 60.9833 | -0.19684 | 122.4792 | -0.16479 | 60.9833 | 122.2275 | 122.525 | -122.7448 | -122.7448
225.0312 | 122.818 | -60.7773 | 61.7798 | -0.18227 | 0.011989 | 0.0052252 | 0.00072196 | 0.057084 | -0.0050671 | 0.064959 | -60.8276 | 61.6837 | -60.9329 | -60.8551 | 61.5646 | 0.3067 | 0.054932 | 0.32501 | 61.6791 | -60.9787 | -0.15564 | -0.09613 | -0.050354 | -0.07782 | -0.21515 | -0.20142 | -0.10071 | 0.10528 | 60.8322 | 61.1023 | 122.3419 | 122.4609 | -0.050354 | 122.4564 | 61.084 | -0.20142 | 122.4609 | -0.050354 | 61.084 | 122.3419 | 122.4564 | -122.7127 | -122.7585
226.6875 | 122.7448 | -60.8002 | 61.7981 | 0.16869 | 0.013484 | 0.0073614 | 0.00649 | 0.060289 | -0.0063489 | 0.069017 | -60.9146 | 61.7157 | -60.965 | -60.9283 | 61.4502 | 0.1236 | -0.13733 | -0.022888 | 61.734 | -60.9604 | -0.16479 | -0.082398 | -0.11444 | -0.12817 | -0.3479 | -0.16022 | -0.064087 | 0.050354 | 60.6628 | 60.7773 | 122.2504 | 122.5159 | -0.11444 | 122.5342 | 60.9238 | -0.16022 | 122.5159 | -0.11444 | 60.9238 | 122.2504 | 122.5342 | -122.7631 | -122.7585
228.3438 | 122.8775 | -60.7636 | 61.7706 | -0.22041 | 0.012416 | 0.0035162 | 0.00649 | 0.059007 | -0.0050671 | 0.068804 | -60.8688 | 61.6974 | -60.9467 | -60.9283 | 61.5005 | 0.24261 | 0.17395 | 0.21973 | 61.7477 | -60.9787 | -0.1831 | -0.073242 | -0.10528 | -0.16479 | -0.27008 | -0.21515 | -0.022888 | 0.07782 | 60.9375 | 60.9833 | 122.2641 | 122.4609 | -0.10528 | 122.5113 | 61.0062 | -0.21515 | 122.4609 | -0.10528 | 61.0062 | 122.2641 | 122.5113 | -122.7173 | -122.7493
230.0312 | 122.7493 | -60.8093 | 61.7706 | 0.20683 | 0.012629 | 0.0060798 | 0.0060626 | 0.060289 | -0.0052807 | 0.06859 | -60.8643 | 61.6974 | -60.9283 | -60.8826 | 61.5372 | 0.17853 | -0.19684 | 0.059509 | 61.734 | -60.9604 | -0.11902 | -0.073242 | -0.054932 | -0.073242 | -0.23346 | -0.15106 | -0.036621 | 0.064087 | 60.6125 | 60.8688 | 122.3465 | 122.5067 | -0.054932 | 122.5433 | 60.9879 | -0.15106 | 122.5067 | -0.054932 | 60.9879 | 122.3465 | 122.5433 | -122.699 | -122.731
231.7031 | 122.818 | -60.7864 | 61.7798 | -0.17464 | 0.0098523 | 0.0062934 | 0.0011494 | 0.059648 | -0.0057079 | 0.065599 | -60.8414 | 61.6699 | -60.9283 | -60.8597 | 61.5601 | 0.31128 | 0.027466 | 0.33875 | 61.7157 | -60.9467 | -0.14191 | -0.10986 | -0.054932 | -0.073242 | -0.21973 | -0.16022 | -0.064087 | 0.086975 | 60.8139 | 61.1252 | 122.3465 | 122.4564 | -0.054932 | 122.5021 | 61.0977 | -0.16022 | 122.4564 | -0.054932 | 61.0977 | 122.3465 | 122.5021 | -122.7081 | -122.7264
233.4062 | 122.7814 | -60.8139 | 61.8073 | 0.077133 | 0.01327 | 0.010139 | 0.0088398 | 0.059221 | -0.0067761 | 0.066881 | -60.9283 | 61.734 | -60.9695 | -60.9787 | 61.4273 | 0.09613 | 0 | -0.054932 | 61.7523 | -60.9604 | -0.15564 | -0.073242 | -0.11444 | -0.16479 | -0.37994 | -0.14648 | -0.054932 | 0.041198 | 60.8139 | 60.759 | 122.2412 | 122.5479 | -0.11444 | 122.5662 | 60.91 | -0.14648 | 122.5479 | -0.11444 | 60.91 | 122.2412 | 122.5662 | -122.7768 | -122.7676
235.0781 | 122.7814 | -60.8093 | 61.7752 | 0.16869 | 0.012202 | 0.0071478 | 0.0017902 | 0.057939 | -0.0057079 | 0.067095 | -60.8688 | 61.6699 | -60.9009 | -60.8963 | 61.5097 | 0.16937 | -0.10986 | 0.14191 | 61.6974 | -60.9467 | -0.091553 | -0.10529 | -0.059509 | -0.086975 | -0.2655 | -0.13733 | -0.07782 | 0.032044 | 60.6995 | 60.9512 | 122.319 | 122.4792 | -0.059509 | 122.5067 | 60.9787 | -0.13733 | 122.4792 | -0.059509 | 60.9787 | 122.319 | 122.5067 | -122.6761 | -122.7219
236.7344 | 122.7264 | -60.8047 | 61.8073 | -0.098343 | 0.016047 | 0.012275 | 0.0081988 | 0.060502 | -0.0067761 | 0.06859 | -60.8688 | 61.702 | -60.9833 | -60.8871 | 61.5097 | 0.21515 | 0.018311 | 0.14191 | 61.7432 | -60.9604 | -0.17853 | -0.10529 | -0.064086 | -0.082397 | -0.29755 | -0.15564 | -0.064087 | 0.11444 | 60.8231 | 60.9467 | 122.3145 | 122.5067 | -0.064086 | 122.5479 | 61.0199 | -0.15564 | 122.5067 | -0.064086 | 61.0199 | 122.3145 | 122.5479 | -122.7905 | -122.7676
238.4688 | 122.7219 | -60.8047 | 61.7798 | 0.19157 | 0.012843 | 0.010779 | 0.0028584 | 0.061998 | -0.0067761 | 0.068163 | -60.8322 | 61.6745 | -60.9329 | -60.8597 | 61.5555 | 0.2243 | -0.21515 | 0.11902 | 61.6837 | -60.9192 | -0.12817 | -0.10528 | -0.027465 | -0.054931 | -0.2243 | -0.11444 | -0.09613 | 0.10071 | 60.5896 | 60.9238 | 122.3602 | 122.4792 | -0.027465 | 122.4884 | 61.0291 | -0.11444 | 122.4792 | -0.027465 | 61.0291 | 122.3602 | 122.4884 | -122.7127 | -122.699
240.1406 | 122.8912 | -60.7452 | 61.7706 | -0.23567 | 0.013484 | 0.0043708 | 0.0045672 | 0.056657 | -0.0059217 | 0.067736 | -60.9329 | 61.7065 | -60.9695 | -60.9467 | 61.4777 | 0.20142 | 0.20142 | 0.16022 | 61.734 | -60.997 | -0.2243 | -0.064087 | -0.18768 | -0.20142 | -0.29297 | -0.25177 | -0.036621 | 0.036621 | 60.9467 | 60.9055 | 122.2229 | 122.4518 | -0.18768 | 122.4792 | 60.9467 | -0.25177 | 122.4518 | -0.18768 | 60.9467 | 122.2229 | 122.4792 | -122.7402 | -122.7676
241.8125 | 122.818 | -60.7773 | 61.7844 | -0.19753 | 0.012416 | 0.0060798 | 0.0026446 | 0.059648 | -0.0042127 | 0.067308 | -60.8322 | 61.6745 | -60.9192 | -60.8368 | 61.5784 | 0.31128 | 0.027466 | 0.34332 | 61.7065 | -60.965 | -0.14191 | -0.10986 | -0.054931 | -0.059509 | -0.20599 | -0.18768 | -0.07782 | 0.086975 | 60.8047 | 61.1206 | 122.3557 | 122.4518 | -0.054931 | 122.4838 | 61.0886 | -0.18768 | 122.4518 | -0.054931 | 61.0886 | 122.3557 | 122.4838 | -122.7036 | -122.7493
243.5156 | 122.7356 | -60.8276 | 61.7889 | 0.16869 | 0.01562 | 0.0022346 | 0.0088398 | 0.061143 | -0.0061353 | 0.067095 | -60.8185 | 61.6837 | -60.91 | -60.8643 | 61.5372 | 0.20142 | -0.21515 | 0.086975 | 61.7249 | -60.9421 | -0.082397 | -0.10528 | 0.009156 | -0.036621 | -0.25177 | -0.11444 | -0.064086 | 0.091553 | 60.6125 | 60.9146 | 122.3648 | 122.5113 | 0.009156 | 122.5525 | 61.0291 | -0.11444 | 122.5113 | 0.009156 | 61.0291 | 122.3648 | 122.5525 | -122.699 | -122.731
245.1875 | 122.8088 | -60.759 | 61.7798 | -0.17464 | 0.012416 | 0.0073614 | 0.003072 | 0.057725 | -0.0063489 | 0.066027 | -60.8185 | 61.702 | -60.9146 | -60.8459 | 61.5555 | 0.31128 | 0.041199 | 0.32959 | 61.702 | -60.9558 | -0.15564 | -0.07782 | -0.059509 | -0.086975 | -0.2243 | -0.19684 | -0.07782 | 0.096131 | 60.8002 | 61.0886 | 122.3145 | 122.4609 | -0.059509 | 122.4609 | 61.0703 | -0.19684 | 122.4609 | -0.059509 | 61.0703 | 122.3145 | 122.4609 | -122.6944 | -122.7356
246.8594 | 122.8546 | -60.7544 | 61.7569 | -0.15175 | 0.012202 | 0.0086432 | 0.004781 | 0.059648 | -0.0082715 | 0.068163 | -60.9192 | 61.7111 | -60.9833 | -60.9238 | 61.4639 | 0.21973 | 0.16937 | 0.13733 | 61.7477 | -60.9741 | -0.22888 | -0.045776 | -0.16479 | -0.16937 | -0.29297 | -0.21973 | -0.009155 | 0.064087 | 60.9238 | 60.8917 | 122.2183 | 122.4655 | -0.16479 | 122.5021 | 60.9741 | -0.21973 | 122.4655 | -0.16479 | 60.9741 | 122.2183 | 122.5021 | -122.7402 | -122.731
248.5469 | 122.8958 | -60.7498 | 61.7798 | -0.22804 | 0.013911 | 0.0037298 | 0.0049946 | 0.058152 | -0.0054943 | 0.067736 | -60.9283 | 61.7203 | -60.9787 | -60.9467 | 61.4639 | 0.21057 | 0.20599 | 0.16937 | 61.7935 | -60.9741 | -0.22888 | -0.059509 | -0.17853 | -0.19684 | -0.31586 | -0.2243 | 0.013733 | 0.050354 | 60.9558 | 60.9192 | 122.2137 | 122.4701 | -0.17853 | 122.5433 | 60.9604 | -0.2243 | 122.4701 | -0.17853 | 60.9604 | 122.2137 | 122.5433 | -122.7585 | -122.7539
250.2188 | 122.7539 | -60.8093 | 61.7798 | 0.16869 | 0.012629 | 0.009925 | 0.0034992 | 0.060075 | -0.0050671 | 0.066668 | -60.8185 | 61.6837 | -60.9146 | -60.8459 | 61.5646 | 0.20599 | -0.20142 | 0.13275 | 61.7065 | -60.9558 | -0.10529 | -0.09613 | -0.009155 | -0.036621 | -0.21515 | -0.14648 | -0.073242 | 0.096131 | 60.6079 | 60.9421 | 122.374 | 122.493 | -0.009155 | 122.5159 | 61.0153 | -0.14648 | 122.493 | -0.009155 | 61.0153 | 122.374 | 122.5159 | -122.6944 | -122.7356
251.9062 | 122.7585 | -60.8322 | 61.7798 | -0.083084 | 0.013057 | 0.010352 | 0.0073444 | 0.059007 | -0.0069897 | 0.070726 | -60.8643 | 61.7065 | -60.965 | -60.8917 | 61.5051 | 0.22888 | 0.004578 | 0.13275 | 61.7523 | -60.9604 | -0.13275 | -0.073242 | -0.032044 | -0.05951 | -0.27466 | -0.12817 | -0.027466 | 0.10071 | 60.8368 | 60.965 | 122.3373 | 122.5388 | -0.032044 | 122.5845 | 61.0611 | -0.12817 | 122.5388 | -0.032044 | 61.0611 | 122.3373 | 122.5845 | -122.7448 | -122.7402
253.5781 | 122.8638 | -60.7773 | 61.7477 | 0.00083945 | 0.012202 | 0.0067206 | 0.00093576 | 0.059007 | -0.0037853 | 0.067522 | -60.8963 | 61.7065 | -60.8963 | -60.9146 | 61.5143 | 0.21973 | -0.009155 | 0.19684 | 61.7386 | -60.9604 | -0.11902 | -0.041199 | -0.11902 | -0.13733 | -0.23346 | -0.18311 | -0.009156 | 0 | 60.7681 | 60.9741 | 122.2916 | 122.4838 | -0.11902 | 122.5159 | 60.997 | -0.18311 | 122.4838 | -0.11902 | 60.997 | 122.2916 | 122.5159 | -122.644 | -122.7081
255.25 | 122.8317 | -60.7819 | 61.7981 | -0.20515 | 0.016047 | 0.0054388 | 0.00414 | 0.05858 | -0.0063489 | 0.066454 | -60.8917 | 61.7249 | -60.9467 | -60.9146 | 61.4914 | 0.23346 | 0.10529 | 0.14648 | 61.7569 | -60.9924 | -0.16479 | -0.073242 | -0.10986 | -0.13275 | -0.3067 | -0.21057 | -0.041199 | 0.054931 | 60.8871 | 60.9283 | 122.2733 | 122.5067 | -0.10986 | 122.5388 | 61.0153 | -0.21057 | 122.5067 | -0.10986 | 61.0153 | 122.2733 | 122.5388 | -122.7448 | -122.7905
256.9688 | 122.85 | -60.7636 | 61.7661 | -0.044937 | 0.013484 | 0.0060798 | 8.1156e-05 | 0.059648 | -0.0044263 | 0.066668 | -60.878 | 61.6974 | -60.91 | -60.878 | 61.5509 | 0.25635 | -0.009155 | 0.25177 | 61.7249 | -60.9375 | -0.14648 | -0.068664 | -0.11444 | -0.11444 | -0.21515 | -0.17395 | -0.041198 | 0.032043 | 60.7544 | 61.0153 | 122.3145 | 122.4609 | -0.11444 | 122.4884 | 61.0199 | -0.17395 | 122.4609 | -0.11444 | 61.0199 | 122.3145 | 122.4884 | -122.6761 | -122.7036
258.625 | 122.7722 | -60.8139 | 61.7798 | 0.11528 | 0.012202 | 0.008216 | 0.0084126 | 0.060502 | -0.0067761 | 0.068377 | -60.9192 | 61.7157 | -60.9741 | -60.9558 | 61.4365 | 0.1236 | 0.004578 | -0.022888 | 61.7569 | -60.9741 | -0.16022 | -0.064087 | -0.10529 | -0.14191 | -0.34332 | -0.16022 | -0.022888 | 0.054932 | 60.8185 | 60.791 | 122.2504 | 122.5296 | -0.10529 | 122.5708 | 60.9375 | -0.16022 | 122.5296 | -0.10529 | 60.9375 | 122.2504 | 122.5708 | -122.7539 | -122.7539
260.3125 | 122.7448 | -60.8139 | 61.7935 | 0.12291 | 0.013698 | 0.012275 | -0.00034604 | 0.059221 | -0.0074169 | 0.068804 | -60.8185 | 61.6837 | -60.91 | -60.8963 | 61.5555 | 0.19226 | -0.19226 | 0.11902 | 61.6928 | -60.9787 | -0.09613 | -0.10986 | -0.004577 | -0.082397 | -0.23804 | -0.16479 | -0.10071 | 0.091553 | 60.6216 | 60.9329 | 122.3694 | 122.4976 | -0.004577 | 122.5067 | 61.0062 | -0.16479 | 122.4976 | -0.004577 | 61.0062 | 122.3694 | 122.5067 | -122.7036 | -122.7722
262.0312 | 122.8271 | -60.7636 | 61.7752 | -0.13649 | 0.011134 | 0.0090704 | 0.0037128 | 0.057512 | -0.0050671 | 0.069658 | -60.8185 | 61.6699 | -60.9421 | -60.8551 | 61.5555 | 0.31128 | 0.050354 | 0.32501 | 61.6745 | -60.9558 | -0.17853 | -0.10529 | -0.054931 | -0.091553 | -0.21973 | -0.19226 | -0.10071 | 0.1236 | 60.8139 | 61.0886 | 122.319 | 122.4335 | -0.054931 | 122.4381 | 61.0748 | -0.19226 | 122.4335 | -0.054931 | 61.0748 | 122.319 | 122.4381 | -122.7173 | -122.731
263.7031 | 122.7356 | -60.8139 | 61.7981 | 0.21446 | 0.015193 | 0.0080024 | 0.0062762 | 0.057298 | -0.0052807 | 0.068163 | -60.8917 | 61.7065 | -60.9695 | -60.91 | 61.4868 | 0.14648 | -0.15564 | 0 | 61.7203 | -60.9787 | -0.15564 | -0.091553 | -0.07782 | -0.09613 | -0.31128 | -0.16479 | -0.07782 | 0.077819 | 60.6583 | 60.8139 | 122.3007 | 122.5204 | -0.07782 | 122.5342 | 60.9604 | -0.16479 | 122.5204 | -0.07782 | 60.9604 | 122.3007 | 122.5342 | -122.7676 | -122.7768
265.3594 | 122.7448 | -60.8139 | 61.7981 | -0.067826 | 0.012629 | 0.006507 | 0.007558 | 0.060075 | -0.0072033 | 0.066668 | -60.8643 | 61.7203 | -60.9604 | -60.8871 | 61.5097 | 0.22888 | 0.022888 | 0.13275 | 61.7477 | -60.9558 | -0.14648 | -0.07782 | -0.050354 | -0.073242 | -0.28839 | -0.14191 | -0.050354 | 0.09613 | 60.8368 | 60.9467 | 122.3236 | 122.5342 | -0.050354 | 122.5616 | 61.0428 | -0.14191 | 122.5342 | -0.050354 | 61.0428 | 122.3236 | 122.5616 | -122.7585 | -122.7539
267.0312 | 122.7402 | -60.8139 | 61.7935 | -0.10597 | 0.014338 | 0.0080024 | 0.00649 | 0.058366 | -0.0078443 | 0.067949 | -60.8643 | 61.6928 | -60.9467 | -60.878 | 61.528 | 0.22888 | 0 | 0.11902 | 61.7798 | -60.9695 | -0.13275 | -0.10071 | -0.050354 | -0.064087 | -0.2655 | -0.15564 | -0.013733 | 0.082397 | 60.8139 | 60.9329 | 122.3419 | 122.5067 | -0.050354 | 122.5937 | 61.0428 | -0.15564 | 122.5067 | -0.050354 | 61.0428 | 122.3419 | 122.5937 | -122.7402 | -122.7631
268.6875 | 122.8592 | -60.7636 | 61.7386 | 0.0084684 | 0.013698 | 0.0037298 | 0.00029476 | 0.057939 | -0.0037853 | 0.068163 | -60.9055 | 61.702 | -60.9375 | -60.9238 | 61.5189 | 0.2243 | -0.022888 | 0.21057 | 61.7386 | -60.9741 | -0.17395 | -0.036621 | -0.14191 | -0.16022 | -0.21973 | -0.21057 | 0 | 0.032043 | 60.7407 | 60.9741 | 122.2824 | 122.4655 | -0.14191 | 122.5021 | 60.9879 | -0.21057 | 122.4655 | -0.14191 | 60.9879 | 122.2824 | 122.5021 | -122.6761 | -122.7127
270.375 | 122.85 | -60.7727 | 61.7569 | 0.00083945 | 0.011348 | 0.0077888 | 0.0032856 | 0.06093 | -0.0046399 | 0.06624 | -60.8871 | 61.6699 | -60.9192 | -60.9192 | 61.5005 | 0.18768 | -0.045776 | 0.14648 | 61.7249 | -60.9879 | -0.14648 | -0.086975 | -0.11444 | -0.14648 | -0.25635 | -0.21515 | -0.032043 | 0.032043 | 60.7269 | 60.9192 | 122.2733 | 122.4426 | -0.11444 | 122.4976 | 60.9604 | -0.21515 | 122.4426 | -0.11444 | 60.9604 | 122.2733 | 122.4976 | -122.6761 | -122.7448
272.0469 | 122.8134 | -60.7773 | 61.7798 | -0.22804 | 0.01327 | 0.006507 | 0.0069172 | 0.056657 | -0.0067761 | 0.066027 | -60.8826 | 61.7386 | -60.9695 | -60.9009 | 61.4914 | 0.22888 | 0.10529 | 0.14648 | 61.7569 | -60.9741 | -0.19226 | -0.041199 | -0.10529 | -0.1236 | -0.28839 | -0.19684 | -0.022888 | 0.086975 | 60.8826 | 60.9238 | 122.2687 | 122.5159 | -0.10529 | 122.5342 | 61.0062 | -0.19684 | 122.5159 | -0.10529 | 61.0062 | 122.2687 | 122.5342 | -122.7493 | -122.7539
273.7031 | 122.7631 | -60.791 | 61.7569 | 0.17632 | 0.013484 | 0.0088568 | 0.00093576 | 0.058793 | -0.0061353 | 0.06859 | -60.8688 | 61.6653 | -60.9283 | -60.8917 | 61.5097 | 0.1831 | -0.1236 | 0.12817 | 61.7111 | -60.9512 | -0.13733 | -0.091553 | -0.077819 | -0.10071 | -0.24719 | -0.16022 | -0.045776 | 0.05951 | 60.6674 | 60.9192 | 122.3007 | 122.4564 | -0.077819 | 122.5021 | 60.9741 | -0.16022 | 122.4564 | -0.077819 | 60.9741 | 122.3007 | 122.5021 | -122.6852 | -122.7081
275.3906 | 122.8226 | -60.7864 | 61.7615 | -0.18227 | 0.011348 | 0.008216 | 0.0017902 | 0.057725 | -0.0063489 | 0.06624 | -60.8047 | 61.6837 | -60.9146 | -60.8368 | 61.5692 | 0.31128 | 0.013733 | 0.3479 | 61.7203 | -60.9375 | -0.12817 | -0.07782 | -0.018311 | -0.050354 | -0.19226 | -0.15106 | -0.041199 | 0.10986 | 60.8002 | 61.1343 | 122.3557 | 122.4701 | -0.018311 | 122.5067 | 61.0977 | -0.15106 | 122.4701 | -0.018311 | 61.0977 | 122.3557 | 122.5067 | -122.6761 | -122.699
277.0625 | 122.7264 | -60.8231 | 61.7935 | -0.060196 | 0.010066 | 0.011634 | 0.0077716 | 0.058152 | -0.0067761 | 0.067308 | -60.8505 | 61.702 | -60.965 | -60.8917 | 61.5005 | 0.2243 | -0.018311 | 0.11444 | 61.7523 | -60.9421 | -0.14191 | -0.091553 | -0.027466 | -0.068665 | -0.29297 | -0.11902 | -0.041199 | 0.11444 | 60.8047 | 60.9375 | 122.3236 | 122.525 | -0.027466 | 122.5754 | 61.0474 | -0.11902 | 122.525 | -0.027466 | 61.0474 | 122.3236 | 122.5754 | -122.7585 | -122.7356
278.7344 | 122.7402 | -60.8002 | 61.7706 | 0.19157 | 0.013698 | 0.0052252 | 0.0045672 | 0.060502 | -0.0065625 | 0.067522 | -60.8276 | 61.702 | -60.9192 | -60.8551 | 61.5509 | 0.21973 | -0.21515 | 0.11902 | 61.6791 | -60.9512 | -0.11902 | -0.068665 | -0.027466 | -0.054932 | -0.21973 | -0.15106 | -0.091553 | 0.091552 | 60.585 | 60.9192 | 122.3511 | 122.5021 | -0.027466 | 122.4792 | 61.0199 | -0.15106 | 122.5021 | -0.027466 | 61.0199 | 122.3511 | 122.4792 | -122.6898 | -122.7219
280.4531 | 122.7768 | -60.8093 | 61.7706 | 0.13817 | 0.013484 | 0.012061 | 0.0049946 | 0.059861 | -0.0067761 | 0.07094 | -60.9192 | 61.7157 | -60.9467 | -60.9512 | 61.4594 | 0.10986 | -0.10986 | -0.036621 | 61.7432 | -60.9604 | -0.13733 | -0.054932 | -0.10986 | -0.14191 | -0.31128 | -0.15106 | -0.027466 | 0.027466 | 60.6995 | 60.7727 | 122.2687 | 122.525 | -0.10986 | 122.5525 | 60.9192 | -0.15106 | 122.525 | -0.10986 | 60.9192 | 122.2687 | 122.5525 | -122.7173 | -122.731
282.125 | 122.7493 | -60.7864 | 61.8256 | -0.044937 | 0.011561 | 0.011634 | 0.007558 | 0.060075 | -0.0063489 | 0.068377 | -60.8643 | 61.7157 | -60.965 | -60.8871 | 61.5189 | 0.2243 | 0 | 0.11444 | 61.7661 | -60.9558 | -0.17853 | -0.10986 | -0.07782 | -0.10071 | -0.3067 | -0.16937 | -0.05951 | 0.10071 | 60.7864 | 60.9009 | 122.3053 | 122.5021 | -0.07782 | 122.5525 | 61.0107 | -0.16937 | 122.5021 | -0.07782 | 61.0107 | 122.3053 | 122.5525 | -122.7905 | -122.7814
283.7969 | 122.8409 | -60.7636 | 61.7569 | -0.075455 | 0.012629 | 0.0094978 | -0.00077324 | 0.057084 | -0.0046399 | 0.068163 | -60.8459 | 61.702 | -60.8826 | -60.8597 | 61.5509 | 0.27924 | -0.013733 | 0.28381 | 61.702 | -60.9695 | -0.11902 | -0.054932 | -0.082397 | -0.09613 | -0.20599 | -0.20599 | -0.054932 | 0.036621 | 60.7498 | 61.0474 | 122.3145 | 122.4655 | -0.082397 | 122.4655 | 61.0428 | -0.20599 | 122.4655 | -0.082397 | 61.0428 | 122.3145 | 122.4655 | -122.6395 | -122.7264
285.5 | 122.7264 | -60.8231 | 61.8073 | 0.1992 | 0.013698 | 0.0050116 | 0.0060626 | 0.057725 | -0.0048535 | 0.067308 | -60.8322 | 61.6837 | -60.9467 | -60.8597 | 61.528 | 0.18768 | -0.21973 | 0.07782 | 61.6928 | -60.9695 | -0.1236 | -0.1236 | -0.009155 | -0.036621 | -0.27924 | -0.14648 | -0.11444 | 0.11444 | 60.6033 | 60.9009 | 122.3511 | 122.5067 | -0.009155 | 122.5159 | 61.0107 | -0.14648 | 122.5067 | -0.009155 | 61.0107 | 122.3511 | 122.5159 | -122.7539 | -122.7768
287.1719 | 122.8592 | -60.7773 | 61.7477 | 0.077133 | 0.010066 | 0.0060798 | 0.00050836 | 0.06093 | -0.0069897 | 0.06859 | -60.8963 | 61.7065 | -60.9146 | -60.9283 | 61.4914 | 0.17853 | -0.054932 | 0.13275 | 61.6928 | -60.9879 | -0.13733 | -0.041199 | -0.11902 | -0.15106 | -0.25635 | -0.21057 | -0.054932 | 0.018311 | 60.7224 | 60.91 | 122.2687 | 122.4838 | -0.11902 | 122.4701 | 60.9558 | -0.21057 | 122.4838 | -0.11902 | 60.9558 | 122.2687 | 122.4701 | -122.6624 | -122.7356
288.8438 | 122.8546 | -60.759 | 61.7706 | -0.18227 | 0.013057 | 0.0062934 | 0.0062762 | 0.059434 | -0.0059217 | 0.067949 | -60.9283 | 61.702 | -60.9924 | -60.9375 | 61.4594 | 0.21057 | 0.16937 | 0.14191 | 61.7569 | -60.9558 | -0.23346 | -0.068665 | -0.16937 | -0.17853 | -0.31128 | -0.19684 | -0.013733 | 0.064087 | 60.9283 | 60.9009 | 122.2183 | 122.4609 | -0.16937 | 122.5159 | 60.9695 | -0.19684 | 122.4609 | -0.16937 | 60.9695 | 122.2183 | 122.5159 | -122.7631 | -122.7264
290.5156 | 122.7402 | -60.8047 | 61.7661 | 0.19157 | 0.012416 | 0.013129 | 0.0056354 | 0.058793 | -0.0039989 | 0.066454 | -60.8231 | 61.702 | -60.8963 | -60.8551 | 61.5555 | 0.22888 | -0.21515 | 0.10986 | 61.7065 | -60.9467 | -0.091552 | -0.064087 | -0.01831 | -0.050354 | -0.21057 | -0.14191 | -0.059509 | 0.073242 | 60.5896 | 60.9146 | 122.3602 | 122.5067 | -0.01831 | 122.5113 | 61.0336 | -0.14191 | 122.5067 | -0.01831 | 61.0336 | 122.3602 | 122.5113 | -122.6624 | -122.7127
292.2031 | 122.7264 | -60.791 | 61.7889 | 0.1458 | 0.014552 | 0.0086432 | 0.0056354 | 0.059648 | -0.0065625 | 0.06624 | -60.8322 | 61.702 | -60.91 | -60.8505 | 61.5417 | 0.20142 | -0.23346 | 0.082397 | 61.6791 | -60.9741 | -0.11902 | -0.086975 | -0.041198 | -0.059509 | -0.24719 | -0.1831 | -0.10986 | 0.07782 | 60.5576 | 60.8734 | 122.3328 | 122.493 | -0.041198 | 122.4701 | 60.9924 | -0.1831 | 122.493 | -0.041198 | 60.9924 | 122.3328 | 122.4701 | -122.699 | -122.7631
293.875 | 122.8592 | -60.759 | 61.7432 | -0.22804 | 0.012843 | 0.0045844 | 0.0043536 | 0.057512 | -0.0072033 | 0.067522 | -60.9421 | 61.7386 | -60.9695 | -60.9467 | 61.4594 | 0.19684 | 0.21973 | 0.16022 | 61.7706 | -60.9833 | -0.21057 | -0.004578 | -0.18311 | -0.18768 | -0.28381 | -0.2243 | 0.027466 | 0.027465 | 60.9787 | 60.9192 | 122.2183 | 122.4976 | -0.18311 | 122.5296 | 60.9558 | -0.2243 | 122.4976 | -0.18311 | 60.9558 | 122.2183 | 122.5296 | -122.7127 | -122.7264
295.5469 | 122.7539 | -60.8231 | 61.7752 | 0.18394 | 0.01327 | 0.0060798 | 0.009267 | 0.060716 | -0.0059217 | 0.066881 | -60.8963 | 61.7386 | -60.9375 | -60.9329 | 61.4731 | 0.12817 | -0.14191 | -0.013733 | 61.7432 | -60.9741 | -0.11444 | -0.036622 | -0.073242 | -0.10986 | -0.30212 | -0.15106 | -0.032044 | 0.041199 | 60.6812 | 60.8093 | 122.2961 | 122.5616 | -0.073242 | 122.5662 | 60.9512 | -0.15106 | 122.5616 | -0.073242 | 60.9512 | 122.2961 | 122.5662 | -122.7127 | -122.7493
297.2344 | 122.85 | -60.7727 | 61.7981 | -0.17464 | 0.013911 | 0.006507 | 0.0054218 | 0.060075 | -0.0063489 | 0.068163 | -60.9146 | 61.7752 | -60.965 | -60.9238 | 61.4639 | 0.21973 | 0.17395 | 0.15106 | 61.7935 | -60.997 | -0.19226 | -0.022888 | -0.14191 | -0.15106 | -0.33417 | -0.2243 | -0.004578 | 0.050354 | 60.9467 | 60.9238 | 122.2366 | 122.5479 | -0.14191 | 122.5662 | 60.9924 | -0.2243 | 122.5479 | -0.14191 | 60.9924 | 122.2366 | 122.5662 | -122.7631 | -122.7951
298.9375 | 122.7631 | -60.8047 | 61.7889 | 0.10002 | 0.013698 | 0.006507 | 0.0084126 | 0.062639 | -0.0078443 | 0.067522 | -60.9146 | 61.7249 | -60.9924 | -60.9467 | 61.4365 | 0.13275 | -0.009155 | -0.013733 | 61.7706 | -60.9558 | -0.18768 | -0.064086 | -0.10986 | -0.14191 | -0.35248 | -0.15106 | -0.01831 | 0.07782 | 60.7956 | 60.791 | 122.2412 | 122.5296 | -0.10986 | 122.5754 | 60.9375 | -0.15106 | 122.5296 | -0.10986 | 60.9375 | 122.2412 | 122.5754 | -122.7814 | -122.7448
300.5938 | 122.8592 | -60.7498 | 61.7477 | -0.0067901 | 0.011134 | 0.0035162 | -0.0012006 | 0.058152 | -0.0042127 | 0.068804 | -60.8871 | 61.702 | -60.9238 | -60.9055 | 61.5143 | 0.24261 | 0 | 0.21057 | 61.7111 | -60.997 | -0.17395 | -0.045777 | -0.13733 | -0.15564 | -0.23346 | -0.24719 | -0.036621 | 0.036621 | 60.7498 | 60.9604 | 122.2641 | 122.4518 | -0.13733 | 122.4609 | 60.9924 | -0.24719 | 122.4518 | -0.13733 | 60.9924 | 122.2641 | 122.4609 | -122.6715 | -122.7448
302.2656 | 122.8683 | -60.7681 | 61.7706 | -0.2433 | 0.012416 | 0.0084296 | 0.00414 | 0.057084 | -0.0046399 | 0.068804 | -60.9055 | 61.7294 | -60.9375 | -60.9421 | 61.4685 | 0.23804 | 0.17853 | 0.21973 | 61.7386 | -60.997 | -0.16937 | -0.041199 | -0.13733 | -0.17395 | -0.30212 | -0.22888 | -0.032044 | 0.032043 | 60.9467 | 60.9879 | 122.2366 | 122.4976 | -0.13733 | 122.5067 | 61.0062 | -0.22888 | 122.4976 | -0.13733 | 61.0062 | 122.2366 | 122.5067 | -122.7081 | -122.7676
303.9844 | 122.8592 | -60.759 | 61.7798 | -0.16701 | 0.014766 | 0.010352 | 0.0073444 | 0.059861 | -0.0076305 | 0.067949 | -60.9238 | 61.734 | -60.9924 | -60.9375 | 61.4594 | 0.21057 | 0.16479 | 0.15106 | 61.7798 | -60.965 | -0.23346 | -0.045776 | -0.16479 | -0.17853 | -0.32043 | -0.20599 | 0 | 0.068665 | 60.9238 | 60.91 | 122.2183 | 122.493 | -0.16479 | 122.5388 | 60.9695 | -0.20599 | 122.493 | -0.16479 | 60.9695 | 122.2183 | 122.5388 | -122.7722 | -122.7448
305.6562 | 122.7264 | -60.8139 | 61.7844 | 0.20683 | 0.012202 | 0.0086432 | 0.0028584 | 0.06093 | -0.0069897 | 0.067949 | -60.8231 | 61.6837 | -60.9283 | -60.8459 | 61.5463 | 0.21515 | -0.20142 | 0.1236 | 61.7065 | -60.9604 | -0.11444 | -0.10071 | -0.009155 | -0.032043 | -0.23804 | -0.14648 | -0.07782 | 0.10529 | 60.6125 | 60.9375 | 122.3602 | 122.4976 | -0.009155 | 122.5204 | 61.0291 | -0.14648 | 122.4976 | -0.009155 | 61.0291 | 122.3602 | 122.5204 | -122.7127 | -122.7448
307.3438 | 122.8638 | -60.7361 | 61.7432 | 0.00083945 | 0.013484 | 0.0054388 | 0.001363 | 0.059221 | -0.0037853 | 0.067308 | -60.8734 | 61.7111 | -60.9238 | -60.9055 | 61.5097 | 0.2243 | -0.018311 | 0.20599 | 61.734 | -60.965 | -0.18768 | -0.032043 | -0.13733 | -0.16937 | -0.23346 | -0.22888 | -0.009155 | 0.050354 | 60.7178 | 60.9421 | 122.2458 | 122.4472 | -0.13733 | 122.4701 | 60.9604 | -0.22888 | 122.4472 | -0.13733 | 60.9604 | 122.2458 | 122.4701 | -122.6669 | -122.7081
309.0469 | 122.7493 | -60.7773 | 61.8027 | -0.037308 | 0.011561 | 0.0084296 | 0.0079852 | 0.063279 | -0.0091259 | 0.070299 | -60.8597 | 61.7111 | -60.9695 | -60.9055 | 61.4731 | 0.19684 | 0 | 0.059509 | 61.7661 | -60.965 | -0.19226 | -0.091552 | -0.082397 | -0.12817 | -0.32959 | -0.18768 | -0.036621 | 0.10986 | 60.7773 | 60.8368 | 122.2504 | 122.4884 | -0.082397 | 122.5433 | 60.9741 | -0.18768 | 122.4884 | -0.082397 | 60.9741 | 122.2504 | 122.5433 | -122.7722 | -122.7676
310.7188 | 122.8546 | -60.759 | 61.7523 | 0.092392 | 0.01327 | 0.0080024 | 0.00093576 | 0.059434 | -0.0057079 | 0.067522 | -60.8826 | 61.702 | -60.9283 | -60.9146 | 61.4822 | 0.18768 | -0.045776 | 0.14191 | 61.702 | -60.9787 | -0.16937 | -0.050354 | -0.1236 | -0.15564 | -0.27008 | -0.21973 | -0.050354 | 0.045777 | 60.7132 | 60.9009 | 122.2412 | 122.4609 | -0.1236 | 122.4609 | 60.9467 | -0.21973 | 122.4609 | -0.1236 | 60.9467 | 122.2412 | 122.4609 | -122.6807 | -122.731
312.4219 | 122.8226 | -60.7819 | 61.7615 | -0.14412 | 0.014979 | 0.0058662 | 0.0015766 | 0.056871 | -0.0042127 | 0.070513 | -60.8322 | 61.6882 | -60.9375 | -60.8414 | 61.5646 | 0.31128 | -0.018311 | 0.31128 | 61.7065 | -60.9741 | -0.15564 | -0.073243 | -0.050354 | -0.05951 | -0.19684 | -0.19226 | -0.054932 | 0.10529 | 60.7635 | 61.0931 | 122.3465 | 122.4701 | -0.050354 | 122.4884 | 61.0931 | -0.19226 | 122.4701 | -0.050354 | 61.0931 | 122.3465 | 122.4884 | -122.699 | -122.7356
314.1094 | 122.7997 | -60.8047 | 61.7798 | 0.16869 | 0.013057 | 0.008216 | 0.009267 | 0.059861 | -0.0067761 | 0.066454 | -60.9192 | 61.702 | -60.9558 | -60.9558 | 61.4548 | 0.10529 | -0.068665 | -0.041199 | 61.7615 | -60.965 | -0.15106 | -0.07782 | -0.11444 | -0.15106 | -0.32501 | -0.16022 | -0.01831 | 0.036622 | 60.7361 | 60.7636 | 122.2595 | 122.5067 | -0.11444 | 122.5662 | 60.91 | -0.16022 | 122.5067 | -0.11444 | 60.91 | 122.2595 | 122.5662 | -122.7356 | -122.7448
315.7656 | 122.8683 | -60.7498 | 61.7661 | -0.23567 | 0.011989 | 0.006507 | 0.0052082 | 0.059221 | -0.0074169 | 0.069445 | -60.9329 | 61.7157 | -60.965 | -60.9512 | 61.4548 | 0.21515 | 0.21973 | 0.16479 | 61.7752 | -60.9833 | -0.21515 | -0.050354 | -0.1831 | -0.20142 | -0.31128 | -0.23346 | 0.009156 | 0.032044 | 60.9695 | 60.9146 | 122.2046 | 122.4655 | -0.1831 | 122.525 | 60.965 | -0.23346 | 122.4655 | -0.1831 | 60.965 | 122.2046 | 122.525 | -122.731 | -122.7493
317.4375 | 122.8271 | -60.7819 | 61.7569 | -0.17464 | 0.013057 | 0.0052252 | 0.0020038 | 0.060075 | -0.0054943 | 0.066668 | -60.8459 | 61.6745 | -60.9558 | -60.8414 | 61.5463 | 0.31128 | 0.045776 | 0.33417 | 61.7157 | -60.9604 | -0.17395 | -0.082397 | -0.064087 | -0.05951 | -0.21057 | -0.17853 | -0.041199 | 0.10986 | 60.8276 | 61.116 | 122.3282 | 122.4564 | -0.064087 | 122.4976 | 61.0931 | -0.17853 | 122.4564 | -0.064087 | 61.0931 | 122.3282 | 122.4976 | -122.7127 | -122.7173
319.1094 | 122.8638 | -60.7636 | 61.7523 | 0.031357 | 0.011348 | 0.0041572 | 0.0015766 | 0.056871 | -0.0010083 | 0.068377 | -60.8963 | 61.702 | -60.9238 | -60.9146 | 61.496 | 0.19684 | -0.050354 | 0.14191 | 61.7386 | -60.9787 | -0.16022 | -0.050354 | -0.13275 | -0.15106 | -0.25635 | -0.21515 | -0.013733 | 0.027466 | 60.7132 | 60.9055 | 122.2595 | 122.4655 | -0.13275 | 122.5021 | 60.9604 | -0.21515 | 122.4655 | -0.13275 | 60.9604 | 122.2595 | 122.5021 | -122.6761 | -122.731
320.7812 | 122.7631 | -60.7819 | 61.7935 | -0.10597 | 0.011989 | 0.0071478 | 0.01119 | 0.060716 | -0.0086987 | 0.066027 | -60.878 | 61.7157 | -60.9924 | -60.878 | 61.5005 | 0.23804 | 0.036621 | 0.13733 | 61.7432 | -60.9879 | -0.21057 | -0.07782 | -0.096131 | -0.096131 | -0.29297 | -0.20599 | -0.050354 | 0.11444 | 60.8185 | 60.9192 | 122.2824 | 122.4976 | -0.096131 | 122.525 | 61.0199 | -0.20599 | 122.4976 | -0.096131 | 61.0199 | 122.2824 | 122.525 | -122.7859 | -122.7814
322.4531 | 122.7722 | -60.7681 | 61.7935 | 0.16106 | 0.013911 | 0.0054388 | 0.0015766 | 0.059434 | -0.0048535 | 0.068804 | -60.8597 | 61.6791 | -60.9375 | -60.9055 | 61.5051 | 0.18768 | -0.11902 | 0.13733 | 61.6974 | -60.9695 | -0.16937 | -0.11444 | -0.091553 | -0.13733 | -0.28839 | -0.20142 | -0.09613 | 0.07782 | 60.6491 | 60.9055 | 122.2733 | 122.4472 | -0.091553 | 122.4655 | 60.9558 | -0.20142 | 122.4472 | -0.091553 | 60.9558 | 122.2733 | 122.4655 | -122.731 | -122.7631
324.125 | 122.7768 | -60.7819 | 61.7752 | 0.069504 | 0.013911 | 0.009284 | 0.007558 | 0.060502 | -0.0065625 | 0.067949 | -60.9146 | 61.734 | -60.9833 | -60.9512 | 61.4273 | 0.10986 | 0 | -0.032043 | 61.7661 | -60.9787 | -0.20142 | -0.041199 | -0.13275 | -0.16937 | -0.3479 | -0.19684 | -0.009156 | 0.068664 | 60.7819 | 60.7498 | 122.2092 | 122.5159 | -0.13275 | 122.5479 | 60.8917 | -0.19684 | 122.5159 | -0.13275 | 60.8917 | 122.2092 | 122.5479 | -122.7585 | -122.7539
325.7812 | 122.8546 | -60.7498 | 61.7798 | -0.22804 | 0.013484 | 0.0050116 | 0.003072 | 0.057725 | -0.0035717 | 0.066881 | -60.8505 | 61.7157 | -60.9421 | -60.8734 | 61.528 | 0.27924 | 0.13733 | 0.27924 | 61.7569 | -60.9604 | -0.19226 | -0.064087 | -0.10071 | -0.1236 | -0.25177 | -0.21057 | -0.022888 | 0.091553 | 60.8871 | 61.0291 | 122.2778 | 122.4655 | -0.10071 | 122.5067 | 61.0291 | -0.21057 | 122.4655 | -0.10071 | 61.0291 | 122.2778 | 122.5067 | -122.7219 | -122.7402
327.4531 | 122.7768 | -60.8231 | 61.7706 | 0.13054 | 0.013698 | 0.012061 | 0.0079852 | 0.060502 | -0.0065625 | 0.067308 | -60.9009 | 61.7523 | -60.9833 | -60.9467 | 61.441 | 0.12817 | -0.10986 | -0.027466 | 61.7615 | -60.9833 | -0.16022 | -0.018311 | -0.07782 | -0.1236 | -0.32959 | -0.16022 | -0.009155 | 0.082397 | 60.7132 | 60.7956 | 122.2641 | 122.5754 | -0.07782 | 122.5845 | 60.9512 | -0.16022 | 122.5754 | -0.07782 | 60.9512 | 122.2641 | 122.5845 | -122.7539 | -122.7539
329.125 | 122.85 | -60.7636 | 61.7386 | 0.061874 | 0.013698 | 0.01142 | 0.00050836 | 0.058366 | -0.0052807 | 0.069445 | -60.8871 | 61.7157 | -60.9375 | -60.91 | 61.5189 | 0.1831 | -0.073242 | 0.13733 | 61.7111 | -60.9787 | -0.17395 | -0.022888 | -0.1236 | -0.14648 | -0.21973 | -0.21515 | -0.027465 | 0.050354 | 60.6903 | 60.9009 | 122.2824 | 122.4792 | -0.1236 | 122.4747 | 60.9467 | -0.21515 | 122.4792 | -0.1236 | 60.9467 | 122.2824 | 122.4747 | -122.6761 | -122.7173
330.7969 | 122.7402 | -60.7956 | 61.8027 | -0.075455 | 0.01327 | 0.0058662 | 0.0090534 | 0.06093 | -0.0089123 | 0.069231 | -60.8505 | 61.7111 | -60.9879 | -60.8826 | 61.5189 | 0.23346 | 0.004578 | 0.1236 | 61.7752 | -60.965 | -0.19226 | -0.091552 | -0.054932 | -0.086975 | -0.28381 | -0.16937 | -0.027465 | 0.13733 | 60.8002 | 60.9192 | 122.3145 | 122.5067 | -0.054932 | 122.5708 | 61.0291 | -0.16937 | 122.5067 | -0.054932 | 61.0291 | 122.3145 | 122.5708 | -122.7905 | -122.7676
332.4688 | 122.818 | -60.7773 | 61.7706 | -0.15938 | 0.012416 | 0.006507 | 0.00093576 | 0.058366 | -0.0035717 | 0.066881 | -60.8276 | 61.6745 | -60.91 | -60.8414 | 61.5829 | 0.31586 | 0.013733 | 0.34332 | 61.7111 | -60.9512 | -0.13275 | -0.09613 | -0.050354 | -0.064087 | -0.18768 | -0.17395 | -0.059509 | 0.082397 | 60.791 | 61.1206 | 122.3602 | 122.4518 | -0.050354 | 122.4884 | 61.0931 | -0.17395 | 122.4518 | -0.050354 | 61.0931 | 122.3602 | 122.4884 | -122.6807 | -122.7219
334.1406 | 122.8638 | -60.7727 | 61.7752 | -0.25856 | 0.013057 | 0.00095277 | 0.0045672 | 0.057084 | -0.0065625 | 0.068163 | -60.9375 | 61.7203 | -60.965 | -60.9512 | 61.4502 | 0.21515 | 0.21515 | 0.17395 | 61.7706 | -60.9833 | -0.19226 | -0.054932 | -0.16479 | -0.17853 | -0.32501 | -0.21057 | -0.004578 | 0.027466 | 60.9879 | 60.9467 | 122.2229 | 122.493 | -0.16479 | 122.5433 | 60.9879 | -0.21057 | 122.493 | -0.16479 | 60.9879 | 122.2229 | 122.5433 | -122.7402 | -122.7585
335.7969 | 122.8821 | -60.759 | 61.7386 | 0.038986 | 0.012843 | 0.0050116 | 0.0039264 | 0.057084 | -0.0042127 | 0.065813 | -60.9009 | 61.6791 | -60.9192 | -60.9283 | 61.4914 | 0.18768 | -0.050354 | 0.14648 | 61.7203 | -60.9741 | -0.16022 | -0.059509 | -0.14191 | -0.16937 | -0.24719 | -0.21515 | -0.01831 | 0.01831 | 60.7086 | 60.9055 | 122.2504 | 122.438 | -0.14191 | 122.4792 | 60.9467 | -0.21515 | 122.438 | -0.14191 | 60.9467 | 122.2504 | 122.4792 | -122.6578 | -122.7127
337.4688 | 122.8455 | -60.7636 | 61.7798 | -0.17464 | 0.0094251 | 0.0050116 | 0.00414 | 0.059221 | -0.0054943 | 0.068377 | -60.9283 | 61.7386 | -60.9741 | -60.9192 | 61.4685 | 0.2243 | 0.14191 | 0.16479 | 61.7706 | -60.965 | -0.21057 | -0.041199 | -0.16479 | -0.15564 | -0.31128 | -0.20142 | -0.009155 | 0.045776 | 60.9055 | 60.9283 | 122.2321 | 122.5021 | -0.16479 | 122.5342 | 60.9879 | -0.20142 | 122.5021 | -0.16479 | 60.9879 | 122.2321 | 122.5342 | -122.7539 | -122.7448
339.1406 | 122.7036 | -60.8368 | 61.8027 | 0.17632 | 0.011348 | 0.009284 | 0.0045672 | 0.062211 | -0.0054943 | 0.069231 | -60.8139 | 61.6928 | -60.9421 | -60.8505 | 61.5417 | 0.21515 | -0.23346 | 0.11444 | 61.6974 | -60.9467 | -0.10529 | -0.10986 | 0.022888 | -0.013733 | -0.26093 | -0.10986 | -0.10529 | 0.12817 | 60.6033 | 60.9512 | 122.3785 | 122.5296 | 0.022888 | 122.5342 | 61.0519 | -0.10986 | 122.5296 | 0.022888 | 61.0519 | 122.3785 | 122.5342 | -122.7448 | -122.7493
340.8125 | 122.818 | -60.7773 | 61.7706 | -0.12123 | 0.012202 | 0.0035162 | 0.002431 | 0.057084 | -0.0065625 | 0.069872 | -60.8368 | 61.6745 | -60.9283 | -60.8414 | 61.5784 | 0.31128 | -0.036621 | 0.33417 | 61.702 | -60.9558 | -0.15106 | -0.09613 | -0.059509 | -0.064087 | -0.19226 | -0.17853 | -0.068665 | 0.091553 | 60.7407 | 61.1114 | 122.3557 | 122.4518 | -0.059509 | 122.4792 | 61.0886 | -0.17853 | 122.4518 | -0.059509 | 61.0886 | 122.3557 | 122.4792 | -122.699 | -122.7264
342.4844 | 122.7859 | -60.791 | 61.7844 | 0.16106 | 0.013698 | 0.01142 | 0.0084126 | 0.061357 | -0.0072033 | 0.067949 | -60.9238 | 61.7569 | -60.9695 | -60.9421 | 61.4365 | 0.10071 | -0.068665 | -0.059509 | 61.7935 | -60.9695 | -0.17853 | -0.027466 | -0.13275 | -0.15106 | -0.3479 | -0.17853 | 0.009155 | 0.045776 | 60.7224 | 60.7315 | 122.2275 | 122.5479 | -0.13275 | 122.5845 | 60.8917 | -0.17853 | 122.5479 | -0.13275 | 60.8917 | 122.2275 | 122.5845 | -122.7539 | -122.7539
344.1562 | 122.818 | -60.791 | 61.7798 | -0.18227 | 0.012202 | 0.011634 | 0.0067036 | 0.060075 | -0.0057079 | 0.06624 | -60.8826 | 61.7432 | -60.9741 | -60.91 | 61.5326 | 0.24261 | -0.013733 | 0.14648 | 61.7615 | -60.9924 | -0.1831 | -0.036621 | -0.091552 | -0.11902 | -0.24719 | -0.20142 | -0.01831 | 0.091553 | 60.7773 | 60.9375 | 122.3236 | 122.5342 | -0.091552 | 122.5525 | 61.0336 | -0.20142 | 122.5342 | -0.091552 | 61.0336 | 122.3236 | 122.5525 | -122.7539 | -122.7722
345.8281 | 122.818 | -60.7819 | 61.7798 | -0.13649 | 0.012843 | 0.0060798 | 0.00093576 | 0.05858 | -0.0067761 | 0.067736 | -60.8185 | 61.6837 | -60.9146 | -60.8414 | 61.5738 | 0.31586 | -0.11902 | 0.34332 | 61.6974 | -60.9604 | -0.13275 | -0.09613 | -0.036621 | -0.05951 | -0.20599 | -0.17853 | -0.082397 | 0.096131 | 60.6628 | 61.1252 | 122.3557 | 122.4655 | -0.036621 | 122.4792 | 61.0977 | -0.17853 | 122.4655 | -0.036621 | 61.0977 | 122.3557 | 122.4792 | -122.6944 | -122.7402
347.5 | 122.7676 | -60.8047 | 61.7844 | 0.15343 | 0.011775 | 0.0056524 | 0.0032856 | 0.058366 | -0.0074169 | 0.067522 | -60.8551 | 61.6882 | -60.9512 | -60.8963 | 61.5234 | 0.19226 | -0.3891 | 0.12817 | 61.7111 | -60.965 | -0.14648 | -0.096131 | -0.050354 | -0.091552 | -0.26093 | -0.16022 | -0.073242 | 0.09613 | 60.4156 | 60.9329 | 122.3282 | 122.493 | -0.050354 | 122.5159 | 60.997 | -0.16022 | 122.493 | -0.050354 | 60.997 | 122.3282 | 122.5159 | -122.7356 | -122.7493
349.1562 | 122.9004 | -60.7452 | 61.7752 | -0.2433 | 0.011775 | 0.0084296 | 0.0060626 | 0.055162 | -0.0048535 | 0.067949 | -60.9238 | 61.7569 | -60.9604 | -60.9283 | 61.4731 | 0.21973 | -0.1831 | 0.11902 | 61.7661 | -60.9879 | -0.21515 | -0.018311 | -0.17853 | -0.18311 | -0.30212 | -0.24262 | -0.009156 | 0.036621 | 60.5621 | 60.8643 | 122.2183 | 122.5021 | -0.17853 | 122.5113 | 60.965 | -0.24262 | 122.5021 | -0.17853 | 60.965 | 122.2183 | 122.5113 | -122.7356 | -122.7631
350.8125 | 122.8592 | -60.759 | 61.7615 | 0.046615 | 0.011134 | 0.0069342 | 0.003072 | 0.059861 | -0.0044263 | 0.069017 | -60.8826 | 61.702 | -60.9146 | -60.91 | 61.5051 | 0.16937 | -0.54474 | 0.004578 | 61.7386 | -60.9467 | -0.15564 | -0.05951 | -0.1236 | -0.15106 | -0.25635 | -0.18768 | -0.022889 | 0.032044 | 60.2142 | 60.7636 | 122.2641 | 122.4609 | -0.1236 | 122.4976 | 60.9283 | -0.18768 | 122.4609 | -0.1236 | 60.9283 | 122.2641 | 122.4976 | -122.6761 | -122.7081
352.4844 | 122.7448 | -60.791 | 61.8347 | -0.067826 | 0.010707 | 0.011207 | 0.010976 | 0.059861 | -0.0067761 | 0.066881 | -60.8368 | 61.7203 | -60.9787 | -60.8597 | 61.5097 | 0.2243 | -0.61798 | -0.086975 | 61.7706 | -60.9604 | -0.18768 | -0.11444 | -0.045776 | -0.068664 | -0.32501 | -0.16937 | -0.064087 | 0.14191 | 60.173 | 60.704 | 122.3007 | 122.5113 | -0.045776 | 122.5616 | 61.0153 | -0.16937 | 122.5113 | -0.045776 | 61.0153 | 122.3007 | 122.5616 | -122.8134 | -122.7951
354.1562 | 122.8638 | -60.7498 | 61.7752 | 0.00083945 | 0.012629 | 0.0084296 | 0.0028584 | 0.059434 | -0.0031445 | 0.068377 | -60.8551 | 61.7294 | -60.8871 | -60.8688 | 61.5555 | 0.24261 | -0.76904 | -0.045776 | 61.7386 | -60.965 | -0.13733 | -0.045777 | -0.10529 | -0.11902 | -0.21973 | -0.21515 | -0.036622 | 0.032043 | 59.9808 | 60.704 | 122.3053 | 122.4792 | -0.10529 | 122.4884 | 60.9924 | -0.21515 | 122.4792 | -0.10529 | 60.9924 | 122.3053 | 122.4884 | -122.6624 | -122.7402
355.8281 | 122.7859 | -60.7819 | 61.7981 | 0.1458 | 0.013057 | 0.0080024 | 0.0073444 | 0.058793 | -0.0052807 | 0.068377 | -60.9146 | 61.7432 | -60.9467 | -60.9421 | 61.4502 | 0.082397 | -1.0986 | -0.41657 | 61.7661 | -60.9604 | -0.16479 | -0.054932 | -0.13275 | -0.16022 | -0.3479 | -0.17853 | -0.032044 | 0.032043 | 59.6832 | 60.3653 | 122.2321 | 122.525 | -0.13275 | 122.5479 | 60.8643 | -0.17853 | 122.525 | -0.13275 | 60.8643 | 122.2321 | 122.5479 | -122.7448 | -122.7585
357.5156 | 122.7631 | -60.7544 | 61.8256 | -0.098343 | 0.013484 | 0.0088568 | 0.0071308 | 0.059648 | -0.0074169 | 0.068804 | -60.8414 | 61.734 | -60.9421 | -60.8597 | 61.5143 | 0.2243 | -1.268 | -0.42572 | 61.8027 | -60.9283 | -0.18768 | -0.091553 | -0.086975 | -0.10528 | -0.31128 | -0.17395 | -0.022889 | 0.10071 | 59.4864 | 60.3287 | 122.2687 | 122.4884 | -0.086975 | 122.5571 | 60.9787 | -0.17395 | 122.4884 | -0.086975 | 60.9787 | 122.2687 | 122.5571 | -122.7676 | -122.7539
359.1875 | 122.7585 | -60.7819 | 61.8347 | 0.15343 | 0.010707 | 0.0062934 | 0.0026446 | 0.06157 | -0.0046399 | 0.069445 | -60.7956 | 61.7249 | -60.8871 | -60.8276 | 61.5738 | 0.19684 | -1.9363 | -0.74616 | 61.7569 | -60.9009 | -0.10529 | -0.10986 | -0.013733 | -0.045777 | -0.26093 | -0.11902 | -0.07782 | 0.091553 | 58.8455 | 60.0357 | 122.3557 | 122.5067 | -0.013733 | 122.5388 | 60.9787 | -0.11902 | 122.5067 | -0.013733 | 60.9787 | 122.3557 | 122.5388 | -122.7219 | -122.7356
360.8594 | 122.9004 | -60.7224 | 61.7889 | -0.21278 | 0.01028 | 0.0052252 | 0.0056354 | 0.057298 | -0.0059217 | 0.067095 | -60.8871 | 61.7661 | -60.9238 | -60.91 | 61.5005 | 0.20142 | -2.0737 | -1.1124 | 61.8073 | -60.9421 | -0.20142 | -0.022888 | -0.16479 | -0.18768 | -0.28839 | -0.21973 | 0.018311 | 0.036621 | 58.6487 | 59.61 | 122.2229 | 122.4884 | -0.16479 | 122.5296 | 60.9238 | -0.21973 | 122.4884 | -0.16479 | 60.9238 | 122.2229 | 122.5296 | -122.7127 | -122.731
362.5625 | 122.85 | -60.7132 | 61.8164 | -0.17464 | 0.011775 | 0.0077888 | 0.0054218 | 0.059648 | -0.0082715 | 0.066668 | -60.8734 | 61.7752 | -60.9283 | -60.878 | 61.5189 | 0.20142 | -2.6779 | -1.6113 | 61.8301 | -60.9192 | -0.21515 | -0.041198 | -0.16022 | -0.16479 | -0.29755 | -0.20599 | 0.013733 | 0.054932 | 58.0353 | 59.1019 | 122.2321 | 122.4884 | -0.16022 | 122.5433 | 60.9146 | -0.20599 | 122.4884 | -0.16022 | 60.9146 | 122.2321 | 122.5433 | -122.7448 | -122.7356
364.2344 | 122.8271 | -60.6857 | 61.8256 | -0.060196 | 0.01327 | 0.0045844 | 0.00093576 | 0.057725 | -0.0057079 | 0.067949 | -60.8093 | 61.7615 | -60.8551 | -60.7956 | 61.6196 | 0.24261 | -3.3005 | -2.0096 | 61.7752 | -60.9146 | -0.16937 | -0.064087 | -0.1236 | -0.10986 | -0.20599 | -0.22888 | -0.050354 | 0.045777 | 57.3853 | 58.6761 | 122.3053 | 122.4472 | -0.1236 | 122.4609 | 60.9283 | -0.22888 | 122.4472 | -0.1236 | 60.9283 | 122.3053 | 122.4609 | -122.6807 | -122.7402
365.9062 | 122.7905 | -60.7132 | 61.8622 | 0.13817 | 0.013057 | 0.0069342 | 0.010335 | 0.060502 | -0.0074169 | 0.067095 | -60.8322 | 61.8118 | -60.8871 | -60.8917 | 61.496 | 0.054932 | -4.2023 | -3.1265 | 61.8713 | -60.8963 | -0.17395 | -0.050354 | -0.11902 | -0.17853 | -0.36621 | -0.1831 | 0.009155 | 0.054932 | 56.5109 | 57.5867 | 122.2092 | 122.525 | -0.11902 | 122.5845 | 60.7681 | -0.1831 | 122.525 | -0.11902 | 60.7681 | 122.2092 | 122.5845 | -122.7493 | -122.7585
367.5781 | 122.7905 | -60.6857 | 61.8805 | 0.18394 | 0.013057 | 0.0060798 | 0.00093576 | 0.061143 | -0.0035717 | 0.067308 | -60.7773 | 61.7615 | -60.8368 | -60.8093 | 61.6058 | 0.1236 | -5.2002 | -3.8498 | 61.7935 | -60.8688 | -0.15106 | -0.11902 | -0.091553 | -0.1236 | -0.27466 | -0.1831 | -0.086975 | 0.059509 | 55.4855 | 56.8359 | 122.2916 | 122.4472 | -0.091553 | 122.4792 | 60.8093 | -0.1831 | 122.4472 | -0.091553 | 60.8093 | 122.2916 | 122.4792 | -122.7173 | -122.7493
369.25 | 122.8729 | -60.6537 | 61.853 | 0.031357 | 0.011989 | 0.0073614 | 0.001363 | 0.056443 | -0.0042127 | 0.068377 | -60.8047 | 61.8118 | -60.8276 | -60.8047 | 61.5921 | 0.082397 | -5.8594 | -4.6417 | 61.8027 | -60.8871 | -0.17395 | -0.041198 | -0.15106 | -0.15106 | -0.26093 | -0.23346 | -0.050354 | 0.022888 | 54.7943 | 56.012 | 122.2458 | 122.4655 | -0.15106 | 122.4564 | 60.7361 | -0.23346 | 122.4655 | -0.15106 | 60.7361 | 122.2458 | 122.4564 | -122.6807 | -122.7402
370.9062 | 122.7219 | -60.6766 | 61.9583 | -0.098343 | 0.013057 | 0.006507 | 0.0096942 | 0.058152 | -0.0095531 | 0.066881 | -60.7407 | 61.8347 | -60.8597 | -60.7315 | 61.6196 | 0.068665 | -6.7703 | -5.6351 | 61.8622 | -60.8368 | -0.1831 | -0.1236 | -0.064087 | -0.054931 | -0.33874 | -0.16022 | -0.09613 | 0.11902 | 53.9062 | 55.0415 | 122.2961 | 122.5113 | -0.064087 | 122.5388 | 60.7452 | -0.16022 | 122.5113 | -0.064087 | 60.7452 | 122.2961 | 122.5388 | -122.818 | -122.7951
372.5938 | 122.7859 | -60.6308 | 61.9354 | 0.092392 | 0.010921 | 0.0062934 | 0.0071308 | 0.061357 | -0.0052807 | 0.068163 | -60.7864 | 61.8896 | -60.8414 | -60.8459 | 61.5692 | -0.11444 | -8.0292 | -7.3151 | 61.8896 | -60.8139 | -0.21057 | -0.045777 | -0.15564 | -0.21515 | -0.36621 | -0.18311 | -0.045777 | 0.054932 | 52.6016 | 53.3157 | 122.2 | 122.5204 | -0.15564 | 122.5204 | 60.5164 | -0.18311 | 122.5204 | -0.15564 | 60.5164 | 122.2 | 122.5204 | -122.7768 | -122.7493
374.25 | 122.8775 | -60.585 | 61.9263 | -0.25856 | 0.011989 | 0.0052252 | 0.0020038 | 0.059007 | -0.0067761 | 0.069017 | -60.7178 | 61.9171 | -60.7681 | -60.7636 | 61.6516 | -0.032043 | -9.4025 | -8.7982 | 61.9125 | -60.8002 | -0.1831 | -0.009156 | -0.13275 | -0.17853 | -0.27466 | -0.21515 | -0.013733 | 0.050354 | 51.1826 | 51.7868 | 122.2366 | 122.5021 | -0.13275 | 122.4976 | 60.553 | -0.21515 | 122.5021 | -0.13275 | 60.553 | 122.2366 | 122.4976 | -122.6944 | -122.7264
375.9844 | 122.8912 | -60.5484 | 61.9675 | -0.22041 | 0.012202 | 0.0075752 | 0.005849 | 0.060502 | -0.0065625 | 0.066454 | -60.7315 | 61.9263 | -60.7819 | -60.7407 | 61.6562 | -0.13275 | -10.9955 | -10.7025 | 62.0041 | -60.7636 | -0.23346 | -0.041198 | -0.18311 | -0.19226 | -0.31128 | -0.21515 | 0.036621 | 0.050354 | 49.5529 | 49.8459 | 122.2046 | 122.4747 | -0.18311 | 122.5525 | 60.4156 | -0.21515 | 122.4747 | -0.18311 | 60.4156 | 122.2046 | 122.5525 | -122.7493 | -122.731
377.6562 | 122.731 | -60.5713 | 62.0224 | 0.20683 | 0.012843 | 0.0088568 | 0.0056354 | 0.060289 | -0.0059217 | 0.067522 | -60.5988 | 61.908 | -60.6903 | -60.6354 | 61.7432 | -0.21515 | -12.5931 | -12.3276 | 61.9492 | -60.7407 | -0.11902 | -0.11444 | -0.027466 | -0.064087 | -0.27924 | -0.16937 | -0.073242 | 0.091553 | 47.9782 | 48.2437 | 122.3145 | 122.4792 | -0.027466 | 122.5204 | 60.3561 | -0.16937 | 122.4792 | -0.027466 | 60.3561 | 122.3145 | 122.5204 | -122.7127 | -122.7631
379.3438 | 122.7631 | -60.5301 | 62.0636 | -0.10597 | 0.012416 | 0.0058662 | 0.0077716 | 0.063279 | -0.0065625 | 0.066881 | -60.6125 | 62.0041 | -60.7224 | -60.6171 | 61.7432 | -0.23346 | -12.8632 | -13.0829 | 62.0361 | -60.6857 | -0.19226 | -0.05951 | -0.082398 | -0.086975 | -0.32044 | -0.15564 | -0.027466 | 0.10986 | 47.6669 | 47.4472 | 122.2733 | 122.5342 | -0.082398 | 122.5662 | 60.2966 | -0.15564 | 122.5342 | -0.082398 | 60.2966 | 122.2733 | 122.5662 | -122.786 | -122.7493
381.0156 | 122.7402 | -60.5209 | 62.0911 | 0.13054 | 0.012843 | 0.0084296 | 0.00414 | 0.059434 | -0.0063489 | 0.069445 | -60.5347 | 61.9904 | -60.6125 | -60.5576 | 61.8164 | -0.43488 | -14.1541 | -14.4516 | 62.0453 | -60.6674 | -0.091553 | -0.10071 | -0.013733 | -0.036621 | -0.27466 | -0.14648 | -0.045776 | 0.07782 | 46.3669 | 46.0693 | 122.3373 | 122.5113 | -0.013733 | 122.5662 | 60.0861 | -0.14648 | 122.5113 | -0.013733 | 60.0861 | 122.3373 | 122.5662 | -122.7036 | -122.7585
382.6719 | 122.7402 | -60.4385 | 62.1826 | -0.037308 | 0.012843 | 0.004798 | 0.0079852 | 0.059434 | -0.0069897 | 0.067308 | -60.5026 | 62.059 | -60.6033 | -60.5392 | 61.7981 | -0.6134 | -15.8203 | -16.5298 | 62.1048 | -60.6079 | -0.16479 | -0.1236 | -0.064087 | -0.10071 | -0.38452 | -0.16937 | -0.07782 | 0.10071 | 44.6182 | 43.9087 | 122.2366 | 122.4976 | -0.064087 | 122.5433 | 59.8251 | -0.16937 | 122.4976 | -0.064087 | 59.8251 | 122.2366 | 122.5433 | -122.7859 | -122.7905
384.3438 | 122.8271 | -60.3333 | 62.2101 | -0.19753 | 0.010493 | 0.0062934 | 0.00072196 | 0.059221 | -0.0044263 | 0.067095 | -60.4294 | 62.1002 | -60.4889 | -60.434 | 61.9308 | -0.60883 | -15.3259 | -15.9164 | 62.1506 | -60.5392 | -0.15564 | -0.10986 | -0.09613 | -0.10071 | -0.27924 | -0.20599 | -0.059509 | 0.05951 | 45.0073 | 44.4168 | 122.2641 | 122.4335 | -0.09613 | 122.4838 | 59.7244 | -0.20599 | 122.4335 | -0.09613 | 59.7244 | 122.2641 | 122.4838 | -122.699 | -122.7493
386.0469 | 122.8958 | -60.3561 | 62.178 | -0.2433 | 0.013057 | 0.0080024 | 0.0039264 | 0.05623 | -0.0050671 | 0.068163 | -60.5301 | 62.146 | -60.5804 | -60.5347 | 61.7935 | -1.1673 | -20.4117 | -21.4233 | 62.1597 | -60.5713 | -0.2243 | -0.032044 | -0.17395 | -0.17853 | -0.38452 | -0.21515 | -0.018311 | 0.050354 | 39.9445 | 38.9328 | 122.1497 | 122.5021 | -0.17395 | 122.5159 | 59.1888 | -0.21515 | 122.5021 | -0.17395 | 59.1888 | 122.1497 | 122.5159 | -122.7585 | -122.7493
387.7188 | 122.8592 | -60.3104 | 62.233 | 0.054245 | 0.01327 | 0.0060798 | 0.00029476 | 0.057298 | -0.0031445 | 0.069017 | -60.4202 | 62.1597 | -60.4706 | -60.4706 | 61.853 | -1.5656 | -22.0596 | -22.7692 | 62.178 | -60.5347 | -0.16022 | -0.073242 | -0.10986 | -0.16022 | -0.37994 | -0.2243 | -0.054931 | 0.050354 | 38.2507 | 37.5412 | 122.1634 | 122.4701 | -0.10986 | 122.4884 | 58.7448 | -0.2243 | 122.4701 | -0.10986 | 58.7448 | 122.1634 | 122.4884 | -122.7036 | -122.7676
389.375 | 122.7951 | -60.2966 | 62.3062 | 0.046615 | 0.012843 | 0.0033026 | 0.010121 | 0.060075 | -0.0059217 | 0.067522 | -60.4111 | 62.2513 | -60.4614 | -60.4477 | 61.8027 | -1.6983 | -24.0463 | -25.09 | 62.2787 | -60.4797 | -0.1648 | -0.054931 | -0.11444 | -0.15106 | -0.50354 | -0.18311 | -0.027465 | 0.050354 | 36.2503 | 35.2066 | 122.0993 | 122.5479 | -0.11444 | 122.5754 | 58.5983 | -0.18311 | 122.5479 | -0.11444 | 58.5983 | 122.0993 | 122.5754 | -122.7676 | -122.7859
391.0312 | 122.8683 | -60.2188 | 62.2879 | 0.0084684 | 0.012843 | 0.0073614 | 0.0022174 | 0.057939 | -0.0027173 | 0.065172 | -60.3516 | 62.233 | -60.3745 | -60.3699 | 61.8988 | -1.5518 | -26.5411 | -27.2415 | 62.2696 | -60.4156 | -0.15564 | -0.054932 | -0.13275 | -0.15106 | -0.3891 | -0.19684 | -0.018311 | 0.022889 | 33.6777 | 32.9773 | 122.1176 | 122.4518 | -0.13275 | 122.4884 | 58.667 | -0.19684 | 122.4518 | -0.13275 | 58.667 | 122.1176 | 122.4884 | -122.6624 | -122.7036
392.7031 | 122.8729 | -60.0769 | 62.4527 | -0.0067901 | 0.011561 | 0.0050116 | 0.0045672 | 0.059221 | -0.0052807 | 0.067522 | -60.2005 | 62.4161 | -60.26 | -60.2097 | 62.027 | -1.5518 | -25.502 | -25.9964 | 62.4161 | -60.2692 | -0.18311 | -0.036621 | -0.1236 | -0.13275 | -0.42572 | -0.19226 | -0.036621 | 0.05951 | 34.5749 | 34.0805 | 122.1039 | 122.493 | -0.1236 | 122.493 | 58.5251 | -0.19226 | 122.493 | -0.1236 | 58.5251 | 122.1039 | 122.493 | -122.7127 | -122.7219
394.3594 | 122.7905 | -60.1273 | 62.4344 | 0.077133 | 0.013698 | 0.010352 | 0.009267 | 0.06093 | -0.0074169 | 0.06859 | -60.2463 | 62.3703 | -60.347 | -60.3241 | 61.8347 | -1.4282 | -28.7842 | -30.0018 | 62.4298 | -60.3195 | -0.21973 | -0.064087 | -0.11902 | -0.19684 | -0.59967 | -0.19226 | -0.004577 | 0.10071 | 31.3431 | 30.1254 | 121.962 | 122.4976 | -0.11902 | 122.5571 | 58.699 | -0.19226 | 122.4976 | -0.11902 | 58.699 | 121.962 | 122.5571 | -122.7814 | -122.7539
396.0312 | 122.8226 | -60.0357 | 62.5259 | -0.1899 | 0.010066 | 0.0077888 | 0.0037128 | 0.057084 | -0.0061353 | 0.067095 | -60.0952 | 62.4252 | -60.1959 | -60.0906 | 61.9949 | -1.7349 | -28.6789 | -29.7318 | 62.4161 | -60.2417 | -0.16022 | -0.10071 | -0.059509 | -0.054931 | -0.53101 | -0.20599 | -0.10986 | 0.10071 | 31.3568 | 30.304 | 122.0306 | 122.4609 | -0.059509 | 122.4518 | 58.3008 | -0.20599 | 122.4609 | -0.059509 | 58.3008 | 122.0306 | 122.4518 | -122.7219 | -122.7676
397.7031 | 122.7905 | -59.9762 | 62.6358 | 0.17632 | 0.016047 | 0.011207 | 0.0073444 | 0.058793 | -0.0067761 | 0.06859 | -60.0449 | 62.5992 | -60.1227 | -60.1135 | 61.8759 | -2.5314 | -29.5258 | -30.6656 | 62.6083 | -60.1181 | -0.14648 | -0.036621 | -0.068665 | -0.13733 | -0.75989 | -0.14191 | -0.027466 | 0.07782 | 30.4504 | 29.3106 | 121.8521 | 122.5754 | -0.068665 | 122.5845 | 57.4448 | -0.14191 | 122.5754 | -0.068665 | 57.4448 | 121.8521 | 122.5845 | -122.7585 | -122.7539
399.3906 | 122.7859 | -59.8068 | 62.764 | 0.1458 | 0.013911 | 0.004798 | 0.00649 | 0.056871 | -0.0095531 | 0.068377 | -59.967 | 62.709 | -60.022 | -59.9899 | 61.9034 | -3.035 | -30.8258 | -30.7571 | 62.7411 | -60.0037 | -0.21515 | -0.054932 | -0.16022 | -0.1831 | -0.8606 | -0.19684 | -0.022888 | 0.054932 | 28.981 | 29.0497 | 121.7102 | 122.5159 | -0.16022 | 122.5479 | 56.7719 | -0.19684 | 122.5159 | -0.16022 | 56.7719 | 121.7102 | 122.5479 | -122.7859 | -122.7676
401.1406 | 122.7448 | -59.697 | 62.915 | 0.21446 | 0.011348 | 0.006507 | 0.0034992 | 0.061143 | -0.0044263 | 0.068377 | -59.6649 | 62.8418 | -59.7885 | -59.7244 | 62.0773 | -3.5385 | -32.1396 | -31.5216 | 62.8326 | -59.8343 | -0.091553 | -0.073242 | 0.032043 | -0.027466 | -0.83771 | -0.13733 | -0.082397 | 0.1236 | 27.5574 | 28.1754 | 121.7743 | 122.5388 | 0.032043 | 122.5296 | 56.1584 | -0.13733 | 122.5388 | 0.032043 | 56.1584 | 121.7743 | 122.5296 | -122.7036 | -122.7493
402.8906 | 122.8409 | -59.3948 | 63.1165 | 0.023727 | 0.011775 | 0.004798 | 0.0022174 | 0.059007 | -0.0059217 | 0.065172 | -59.4818 | 63.0936 | -59.5184 | -59.5551 | 62.1368 | -3.6484 | -31.6772 | -32.4097 | 63.1027 | -59.6191 | -0.1236 | -0.022888 | -0.086976 | -0.16022 | -0.97961 | -0.22431 | -0.013733 | 0.036621 | 27.7176 | 26.9852 | 121.5317 | 122.4884 | -0.086976 | 122.4976 | 55.7465 | -0.22431 | 122.4884 | -0.086976 | 55.7465 | 121.5317 | 122.4976 | -122.6349 | -122.7356
404.5781 | 122.8683 | -59.1293 | 63.3728 | 0.0084684 | 0.010707 | 0.0071478 | 0.004781 | 0.055803 | -0.0072033 | 0.067736 | -59.2163 | 63.3453 | -59.3124 | -59.2804 | 62.3154 | -3.4836 | -31.6406 | -31.5216 | 63.3453 | -59.3674 | -0.18311 | -0.027466 | -0.086976 | -0.15106 | -1.0574 | -0.23804 | -0.027466 | 0.09613 | 27.4887 | 27.6077 | 121.4447 | 122.4747 | -0.086976 | 122.4747 | 55.6458 | -0.23804 | 122.4747 | -0.086976 | 55.6458 | 121.4447 | 122.4747 | -122.6852 | -122.7402
406.3125 | 122.8363 | -58.905 | 63.6703 | -0.25093 | 0.010707 | 0.0041572 | 0.0049946 | 0.057512 | -0.0059217 | 0.068804 | -58.9462 | 63.5513 | -59.1019 | -59.0286 | 62.4161 | -3.5568 | -32.1854 | -32.4509 | 63.6246 | -59.111 | -0.19684 | -0.11902 | -0.041199 | -0.1236 | -1.2543 | -0.20599 | -0.045776 | 0.15564 | 26.7197 | 26.4542 | 121.3211 | 122.4564 | -0.041199 | 122.5296 | 55.3482 | -0.20599 | 122.4564 | -0.041199 | 55.3482 | 121.3211 | 122.5296 | -122.7722 | -122.7814
408.0469 | 122.7127 | -58.5754 | 64.0228 | 0.16106 | 0.013911 | 0.010993 | 0.0084126 | 0.059007 | -0.0048535 | 0.06859 | -58.548 | 63.8855 | -58.7448 | -58.6395 | 62.5992 | -4.1199 | -32.6752 | -32.666 | 63.913 | -58.7402 | -0.16937 | -0.13733 | 0.027465 | -0.064087 | -1.4236 | -0.16479 | -0.10986 | 0.19684 | 25.9003 | 25.9094 | 121.1746 | 122.4609 | 0.027465 | 122.4884 | 54.4556 | -0.16479 | 122.4609 | 0.027465 | 54.4556 | 121.1746 | 122.4884 | -122.7676 | -122.7631
409.7188 | 122.7676 | -58.1406 | 64.476 | 0.069504 | 0.011989 | 0.0054388 | 0.0094806 | 0.05858 | -0.0076305 | 0.069872 | -58.1406 | 64.4211 | -58.3099 | -58.2687 | 62.8418 | -3.7262 | -33.4671 | -33.8379 | 64.4577 | -58.2733 | -0.16937 | -0.054931 | 0 | -0.12817 | -1.6342 | -0.13275 | -0.01831 | 0.16937 | 24.6735 | 24.3027 | 120.9824 | 122.5616 | 0 | 122.5983 | 54.4144 | -0.13275 | 122.5616 | 0 | 54.4144 | 120.9824 | 122.5983 | -122.7859 | -122.7493
411.4531 | 122.8592 | -57.4768 | 65.062 | -0.18227 | 0.01327 | 0.0084296 | 0.005849 | 0.057512 | -0.0054943 | 0.068163 | -57.5592 | 65.0299 | -57.6599 | -57.6691 | 63.2309 | -4.6143 | -34.3689 | -34.671 | 65.0208 | -57.7011 | -0.1831 | -0.032044 | -0.082397 | -0.19226 | -1.8311 | -0.2243 | -0.041199 | 0.10071 | 23.1079 | 22.8058 | 120.7077 | 122.5067 | -0.082397 | 122.4976 | 52.8625 | -0.2243 | 122.5067 | -0.082397 | 52.8625 | 120.7077 | 122.4976 | -122.7219 | -122.7631
413.125 | 122.8455 | -56.7032 | 65.8356 | -0.022049 | 0.014125 | 0.0060798 | 0.0026446 | 0.057298 | -0.0039989 | 0.069872 | -56.6711 | 65.7852 | -56.8451 | -56.8314 | 63.8855 | -5.4474 | -35.4355 | -35.3622 | 65.8081 | -56.8909 | -0.14191 | -0.050354 | 0.032043 | -0.12817 | -1.9501 | -0.18768 | -0.027466 | 0.17395 | 21.2677 | 21.3409 | 120.5887 | 122.4884 | 0.032043 | 122.5113 | 51.2558 | -0.18768 | 122.4884 | 0.032043 | 51.2558 | 120.5887 | 122.5113 | -122.6807 | -122.7264
414.8594 | 122.7585 | -56.0669 | 66.5451 | 0.10765 | 0.013484 | 0.0086432 | 0.007558 | 0.058152 | -0.0069897 | 0.067308 | -56.0669 | 66.4307 | -56.2546 | -56.2363 | 64.1006 | -8.7021 | -36.026 | -36.2091 | 66.4948 | -56.218 | -0.18768 | -0.11444 | 0 | -0.16937 | -2.4445 | -0.15106 | -0.050354 | 0.18768 | 20.0409 | 19.8578 | 120.1675 | 122.4976 | 0 | 122.5616 | 47.3648 | -0.15106 | 122.4976 | 0 | 47.3648 | 120.1675 | 122.5616 | -122.7997 | -122.7631
416.5781 | 122.8638 | -55.0369 | 67.4927 | 0.00083945 | 0.014338 | 0.0041572 | 0.0015766 | 0.057512 | -0.0044263 | 0.069872 | -54.9728 | 67.4881 | -55.1788 | -55.1559 | 64.8376 | -10.2722 | -36.882 | -37.3398 | 67.4927 | -55.1971 | -0.14191 | -0.004578 | 0.064087 | -0.11902 | -2.655 | -0.16022 | 0 | 0.20599 | 18.1549 | 17.6971 | 119.8746 | 122.525 | 0.064087 | 122.5296 | 44.7647 | -0.16022 | 122.525 | 0.064087 | 44.7647 | 119.8746 | 122.5296 | -122.6715 | -122.6898
418.3125 | 122.7448 | -53.5812 | 69.0399 | 0.016098 | 0.01327 | 0.0071478 | 0.0090534 | 0.057725 | -0.0057079 | 0.069872 | -53.5263 | 68.9438 | -53.7781 | -53.7231 | 65.8859 | -9.7733 | -31.5582 | -37.1338 | 68.9667 | -53.7552 | -0.19684 | -0.09613 | 0.054932 | -0.14191 | -3.154 | -0.17395 | -0.073242 | 0.25177 | 22.023 | 16.4474 | 119.4672 | 122.525 | 0.054932 | 122.5479 | 43.808 | -0.17395 | 122.525 | 0.054932 | 43.808 | 119.4672 | 122.5479 | -122.818 | -122.7951
420.0625 | 122.7264 | -52.684 | 69.96 | 0.1992 | 0.010921 | 0.01142 | 0.0056354 | 0.060075 | -0.0057079 | 0.073503 | -52.5101 | 69.8914 | -52.771 | -52.7115 | 66.4215 | -12.6022 | -33.9249 | -39.3356 | 69.9051 | -52.771 | -0.086975 | -0.068665 | 0.17395 | -0.027466 | -3.5385 | -0.086975 | -0.054932 | 0.26092 | 18.7592 | 13.3484 | 119.1055 | 122.5754 | 0.17395 | 122.5891 | 40.0818 | -0.086975 | 122.5754 | 0.17395 | 40.0818 | 119.1055 | 122.5891 | -122.731 | -122.731
421.7188 | 122.7356 | -52.2629 | 70.3629 | -0.037308 | 0.015407 | 0.0041572 | 0.0088398 | 0.057939 | -0.0063489 | 0.072435 | -52.1805 | 70.166 | -52.4918 | -52.4185 | 66.4307 | -11.1328 | -34.5016 | -39.5325 | 70.2896 | -52.4277 | -0.22888 | -0.19684 | 0.082397 | -0.15564 | -3.9322 | -0.16479 | -0.073242 | 0.31128 | 17.7612 | 12.7304 | 118.6935 | 122.4289 | 0.082397 | 122.5525 | 41.1301 | -0.16479 | 122.4289 | 0.082397 | 41.1301 | 118.6935 | 122.5525 | -122.8546 | -122.7905
423.4531 | 122.85 | -50.8209 | 71.6995 | 0.016098 | 0.013484 | 0.002021 | 0.00093576 | 0.058366 | -0.0029309 | 0.072008 | -50.7294 | 71.6537 | -50.9949 | -51.0178 | 67.3874 | -11.0001 | -33.0276 | -38.9511 | 71.6675 | -51.0269 | -0.17395 | -0.045776 | 0.091553 | -0.19684 | -4.3121 | -0.20599 | -0.032044 | 0.2655 | 17.7933 | 11.8698 | 118.2083 | 122.4747 | 0.091553 | 122.4884 | 39.8209 | -0.20599 | 122.4747 | 0.091553 | 39.8209 | 118.2083 | 122.4884 | -122.6944 | -122.7264
425.2031 | 122.7448 | -50.1068 | 72.5281 | 0.16106 | 0.013698 | 0.0071478 | 0.0056354 | 0.057939 | -0.0012219 | 0.072863 | -49.9146 | 72.4319 | -50.2029 | -50.1617 | 67.5751 | -11.8011 | -34.1721 | -38.4933 | 72.4091 | -50.2579 | -0.09613 | -0.09613 | 0.19226 | -0.054931 | -4.953 | -0.15106 | -0.11902 | 0.28839 | 15.9348 | 11.6135 | 117.6819 | 122.5388 | 0.19226 | 122.5159 | 38.3057 | -0.15106 | 122.5388 | 0.19226 | 38.3057 | 117.6819 | 122.5159 | -122.731 | -122.7859
426.9375 | 122.8043 | -48.2391 | 74.3317 | -0.12123 | 0.010921 | 0.010352 | 0.002431 | 0.055375 | -0.0010083 | 0.072863 | -48.0972 | 74.231 | -48.4085 | -48.3307 | 68.6096 | -10.849 | -33.1879 | -36.8225 | 74.2035 | -48.4589 | -0.16937 | -0.10071 | 0.14191 | -0.091552 | -5.722 | -0.21973 | -0.12817 | 0.31128 | 15.0513 | 11.4166 | 116.8488 | 122.4701 | 0.14191 | 122.4426 | 37.3901 | -0.21973 | 122.4701 | 0.14191 | 37.3901 | 116.8488 | 122.4426 | -122.7402 | -122.7905
428.6094 | 122.7539 | -46.3943 | 76.2039 | 0.15343 | 0.011348 | 0.0080024 | 0.0049946 | 0.057298 | -0.0022901 | 0.072863 | -46.4905 | 75.7919 | -46.843 | -46.8155 | 68.6874 | -8.3771 | -30.0797 | -35.3165 | 75.824 | -46.8658 | -0.44861 | -0.41199 | -0.096131 | -0.42114 | -7.5165 | -0.4715 | -0.37994 | 0.35248 | 16.3147 | 11.0779 | 115.0818 | 122.1863 | -0.096131 | 122.2183 | 38.0173 | -0.4715 | 122.1863 | -0.096131 | 38.0173 | 115.0818 | 122.2183 | -123.0469 | -123.0698
430.3594 | 122.8043 | -45.3186 | 77.211 | -0.075455 | 0.012843 | 0.0077888 | 0.002431 | 0.057084 | 0.0021961 | 0.078203 | -45.1447 | 77.179 | -45.4468 | -45.433 | 62.352 | 1.9592 | -29.8416 | -33.7372 | 77.2202 | -45.4834 | -0.12817 | -0.032044 | 0.17395 | -0.11444 | -14.859 | -0.16479 | 0.009155 | 0.30212 | 15.477 | 11.5814 | 107.6706 | 122.4976 | 0.17395 | 122.5388 | 47.2778 | -0.16479 | 122.4976 | 0.17395 | 47.2778 | 107.6706 | 122.5388 | -122.6578 | -122.6944
432.0938 | 122.7402 | -43.1122 | 79.5593 | -0.098343 | 0.01028 | 0.0075752 | 0.010549 | 0.058152 | 0.0028369 | 0.081194 | -42.8558 | 79.4586 | -43.2587 | -43.19 | 59.6649 | 2.0462 | -28.45 | -32.3959 | 79.4998 | -43.2449 | -0.14648 | -0.10071 | 0.25635 | -0.077819 | -19.8944 | -0.13275 | -0.059509 | 0.40283 | 14.6622 | 10.7162 | 102.7771 | 122.5708 | 0.25635 | 122.612 | 45.1584 | -0.13275 | 122.5708 | 0.25635 | 45.1584 | 102.7771 | 122.612 | -122.818 | -122.8043
433.7656 | 122.7905 | -39.6881 | 82.8964 | -0.13649 | 0.013698 | 0.0069342 | 0.0020038 | 0.060502 | 0.0090321 | 0.086107 | -39.5599 | 82.8003 | -39.8529 | -39.8163 | 57.5592 | 2.9205 | -25.9186 | -30.2444 | 82.8049 | -39.8941 | -0.16479 | -0.09613 | 0.12817 | -0.12817 | -25.3372 | -0.20599 | -0.091552 | 0.29297 | 13.7695 | 9.4437 | 97.2473 | 122.4884 | 0.12817 | 122.493 | 42.6086 | -0.20599 | 122.4884 | 0.12817 | 42.6086 | 97.2473 | 122.493 | -122.7493 | -122.7905
435.5 | 122.85 | -38.1088 | 84.4666 | -0.26619 | 0.014766 | 0.0090704 | 0.0067036 | 0.057084 | 0.013091 | 0.092516 | -37.9623 | 84.4437 | -38.3148 | -38.3423 | 48.9304 | 2.0096 | -23.5703 | -27.6489 | 84.4528 | -38.356 | -0.20599 | -0.022888 | 0.14648 | -0.23346 | -35.5362 | -0.24719 | -0.013733 | 0.35248 | 14.5386 | 10.4599 | 87.0392 | 122.5525 | 0.14648 | 122.5616 | 40.1184 | -0.24719 | 122.5525 | 0.14648 | 40.1184 | 87.0392 | 122.5616 | -122.7814 | -122.8226
437.2344 | 122.7539 | -36.8866 | 85.7391 | 0.13054 | 0.012629 | 0.004798 | 0.0067036 | 0.057512 | 0.016722 | 0.097216 | -36.6302 | 85.6705 | -37.056 | -37.088 | 42.6041 | 0.32044 | -23.3459 | -26.4908 | 85.6842 | -37.0834 | -0.16937 | -0.068665 | 0.25635 | -0.20142 | -43.1351 | -0.19684 | -0.054932 | 0.42572 | 13.5407 | 10.3958 | 79.4907 | 122.5571 | 0.25635 | 122.5708 | 37.207 | -0.19684 | 122.5571 | 0.25635 | 37.207 | 79.4907 | 122.5708 | -122.7951 | -122.8226
438.9688 | 122.7173 | -36.3693 | 86.2839 | 0.1992 | 0.012416 | 0.0077888 | 0.0081988 | 0.059221 | 0.019499 | 0.1017 | -35.9802 | 86.1969 | -36.5204 | -36.5204 | 36.0672 | -2.0279 | -24.4949 | -26.8616 | 86.2335 | -36.5067 | -0.15106 | -0.086976 | 0.3891 | -0.15106 | -50.2167 | -0.13733 | -0.050354 | 0.54016 | 11.8744 | 9.5078 | 72.4365 | 122.5662 | 0.3891 | 122.6028 | 34.3414 | -0.13733 | 122.5662 | 0.3891 | 34.3414 | 72.4365 | 122.6028 | -122.8043 | -122.7905
440.7188 | 122.7127 | -35.1196 | 87.5244 | -0.067826 | 0.012202 | 0.0094978 | 0.0088398 | 0.059861 | 0.023986 | 0.10384 | -34.6893 | 87.4512 | -35.289 | -35.2249 | 31.1966 | -3.7949 | -25.2457 | -27.8595 | 87.5061 | -35.2478 | -0.16937 | -0.073242 | 0.4303 | -0.10529 | -56.3278 | -0.12817 | -0.01831 | 0.59967 | 9.874 | 7.2601 | 66.3162 | 122.5708 | 0.4303 | 122.6257 | 31.3248 | -0.12817 | 122.5708 | 0.4303 | 31.3248 | 66.3162 | 122.6257 | -122.8134 | -122.7722
442.3906 | 122.7081 | -33.3939 | 89.2319 | -0.052567 | 0.012202 | 0.0094978 | 0.0094806 | 0.058366 | 0.047698 | 0.12712 | -32.8171 | 89.2319 | -33.4808 | -33.3435 | -11.8744 | -18.1641 | -27.2186 | -30.3268 | 89.3784 | -33.3527 | -0.086975 | 0 | 0.57678 | 0.050354 | -101.1063 | 0.041199 | 0.14648 | 0.66376 | 6.1752 | 3.067 | 21.5195 | 122.6257 | 0.57678 | 122.7722 | 15.2298 | 0.041199 | 122.6257 | 0.57678 | 15.2298 | 21.5195 | 122.7722 | -122.7127 | -122.5845
444.1094 | 122.7264 | -34.4604 | 88.1332 | 0.13817 | 0.012202 | 0.0058662 | 0.0022174 | 0.057939 | 0.050048 | 0.12969 | -33.8837 | 88.06 | -34.5932 | -34.5978 | -13.797 | -20.4575 | -29.805 | -31.8832 | 88.0875 | -34.6115 | -0.13275 | -0.073242 | 0.57678 | -0.13733 | -101.9302 | -0.15106 | -0.045777 | 0.70953 | 4.6555 | 2.5772 | 20.6635 | 122.5204 | 0.57678 | 122.5479 | 14.003 | -0.15106 | 122.5204 | 0.57678 | 14.003 | 20.6635 | 122.5479 | -122.7264 | -122.7448
445.8438 | 122.7997 | -38.4384 | 84.0958 | 0.084762 | 0.013698 | 0.0097114 | -0.002055 | 0.055803 | 0.051116 | 0.12712 | -37.5458 | 84.0088 | -38.6444 | -38.6581 | -20.5124 | -24.2889 | -36.2228 | -36.6898 | 84.0317 | -38.6444 | -0.20599 | -0.086975 | 0.89264 | -0.21973 | -104.6082 | -0.20599 | -0.064087 | 1.0986 | 2.2156 | 1.7487 | 17.926 | 122.4472 | 0.89264 | 122.4701 | 14.1495 | -0.20599 | 122.4472 | 0.89264 | 14.1495 | 17.926 | 122.4701 | -122.7402 | -122.7402
447.5156 | 122.7219 | -38.1271 | 84.5215 | -0.022049 | 0.011348 | 0.010779 | 0.0077716 | 0.058793 | 0.049407 | 0.1284 | -36.9278 | 84.4391 | -38.2645 | -38.2553 | -21.0938 | -24.9435 | -36.4426 | -36.8958 | 84.5032 | -38.2416 | -0.13733 | -0.082397 | 1.1993 | -0.12817 | -105.6152 | -0.11444 | -0.01831 | 1.3367 | 1.6846 | 1.2314 | 17.0334 | 122.5662 | 1.1993 | 122.6303 | 13.1836 | -0.11444 | 122.5662 | 1.1993 | 13.1836 | 17.0334 | 122.6303 | -122.7859 | -122.7631
449.25 | 122.8226 | -36.85 | 85.6842 | 0.038986 | 0.010493 | 0.0067206 | 0.0015766 | 0.055375 | 0.05197 | 0.13033 | -35.6827 | 85.6522 | -36.9827 | -37.0102 | -20.6314 | -24.4034 | -34.4833 | -34.8495 | 85.6888 | -36.969 | -0.13275 | -0.032043 | 1.1673 | -0.16022 | -106.3156 | -0.11902 | 0.004578 | 1.3 | 2.3666 | 2.0004 | 16.2186 | 122.5021 | 1.1673 | 122.5388 | 12.4466 | -0.11902 | 122.5021 | 1.1673 | 12.4466 | 16.2186 | 122.5388 | -122.6669 | -122.6532
451 | 122.6624 | -31.279 | 91.3605 | 0.13817 | 0.011775 | 0.0097114 | 0.0049946 | 0.059434 | 0.052184 | 0.13011 | -30.098 | 91.2872 | -31.3797 | -31.366 | -16.246 | -20.517 | -27.388 | -29.4479 | 91.2918 | -31.3705 | -0.10071 | -0.073243 | 1.181 | -0.086975 | -107.6065 | -0.091552 | -0.068665 | 1.2817 | 3.891 | 1.8311 | 15.033 | 122.5662 | 1.181 | 122.5708 | 10.762 | -0.091552 | 122.5662 | 1.181 | 10.762 | 15.033 | 122.5708 | -122.7402 | -122.731
452.6719 | 122.7448 | -29.3152 | 93.3151 | 0.12291 | 0.012629 | 0.0075752 | 0.0079852 | 0.059648 | 0.049834 | 0.13396 | -28.1662 | 93.2602 | -29.4342 | -29.5029 | -14.5844 | -18.6356 | -25.7309 | -27.9877 | 93.2831 | -29.4754 | -0.11902 | -0.054932 | 1.149 | -0.18768 | -107.8995 | -0.16022 | -0.032044 | 1.268 | 3.5843 | 1.3275 | 14.7308 | 122.5754 | 1.149 | 122.5983 | 10.6796 | -0.16022 | 122.5754 | 1.149 | 10.6796 | 14.7308 | 122.5983 | -122.7493 | -122.7905
454.3906 | 122.7173 | -29.8691 | 92.7292 | 0.1458 | 0.011348 | 0.0088568 | 0.00414 | 0.060502 | 0.052611 | 0.12947 | -28.5507 | 92.6971 | -29.9332 | -29.9973 | -11.5128 | -16.6489 | -25.6622 | -28.1937 | 92.6743 | -30.0064 | -0.064087 | -0.032043 | 1.3184 | -0.12817 | -104.2419 | -0.13733 | -0.054932 | 1.3824 | 4.2068 | 1.6754 | 18.3563 | 122.5662 | 1.3184 | 122.5433 | 13.2202 | -0.13733 | 122.5662 | 1.3184 | 13.2202 | 18.3563 | 122.5433 | -122.6624 | -122.7356
456.125 | 122.6898 | -24.8978 | 97.7646 | 0.13817 | 0.011134 | 0.0052252 | 0.0056354 | 0.060075 | 0.05197 | 0.13353 | -24.2569 | 97.6089 | -25.0031 | -24.9664 | -7.0084 | -14.0671 | -23.8632 | -24.2203 | 97.6593 | -25.0168 | -0.10529 | -0.15564 | 0.64087 | -0.068665 | -104.7729 | -0.11902 | -0.10529 | 0.74616 | 1.0345 | 0.67749 | 17.8894 | 122.5067 | 0.64087 | 122.5571 | 10.8307 | -0.11902 | 122.5067 | 0.64087 | 10.8307 | 17.8894 | 122.5571 | -122.7676 | -122.7814
457.8438 | 122.7905 | -36.7996 | 85.7208 | -0.16701 | 0.010493 | 0.011634 | 0.00414 | 0.056016 | 0.053038 | 0.12798 | -35.6369 | 85.6705 | -36.9736 | -36.9232 | -19.5648 | -25.4517 | -35.7513 | -36.0443 | 85.6522 | -37.001 | -0.17395 | -0.050354 | 1.1627 | -0.1236 | -105.2856 | -0.20142 | -0.068664 | 1.3367 | 1.0483 | 0.75531 | 17.2348 | 122.4701 | 1.1627 | 122.4518 | 11.348 | -0.20142 | 122.4701 | 1.1627 | 11.348 | 17.2348 | 122.4518 | -122.6944 | -122.7219
459.5156 | 122.7036 | -35.7147 | 86.9293 | 0.15343 | 0.012202 | 0.0052252 | 0.00649 | 0.058366 | 0.05432 | 0.13118 | -34.4788 | 86.7279 | -35.9253 | -35.8841 | -20.2332 | -24.1333 | -34.8129 | -34.9411 | 86.7004 | -35.9299 | -0.21057 | -0.20142 | 1.236 | -0.16937 | -107.1625 | -0.21515 | -0.22888 | 1.4465 | 0.90179 | 0.77362 | 15.4816 | 122.4426 | 1.236 | 122.4152 | 11.5814 | -0.21515 | 122.4426 | 1.236 | 11.5814 | 15.4816 | 122.4152 | -122.8546 | -122.8592
461.25 | 122.7402 | -34.0759 | 88.5315 | 0.10765 | 0.011775 | 0.010139 | 0.0099078 | 0.057298 | 0.051329 | 0.13289 | -32.8949 | 88.4583 | -34.2636 | -34.2819 | -19.3863 | -22.7234 | -32.9178 | -33.2932 | 88.4811 | -34.2407 | -0.18768 | -0.073242 | 1.181 | -0.20599 | -107.9178 | -0.1648 | -0.050354 | 1.3687 | 1.1581 | 0.78278 | 14.6896 | 122.5342 | 1.181 | 122.5571 | 11.3525 | -0.1648 | 122.5342 | 1.181 | 11.3525 | 14.6896 | 122.5571 | -122.7951 | -122.7722
462.9844 | 122.818 | -34.8129 | 87.7121 | -0.21278 | 0.014338 | 0.014625 | 0.0049946 | 0.057298 | 0.054106 | 0.13097 | -33.9478 | 87.6572 | -34.9823 | -34.9777 | -20.5719 | -24.5041 | -33.5541 | -33.6685 | 87.6709 | -35.0327 | -0.16937 | -0.054931 | 0.86517 | -0.16479 | -108.284 | -0.21973 | -0.041199 | 1.0345 | 1.2589 | 1.1444 | 14.241 | 122.4701 | 0.86517 | 122.4838 | 10.3088 | -0.21973 | 122.4701 | 0.86517 | 10.3088 | 14.241 | 122.4838 | -122.6944 | -122.7448
464.7031 | 122.699 | -32.0892 | 90.5136 | 0.29839 | 0.0072889 | 0.012488 | 0.021871 | 0.059861 | 0.053893 | 0.14827 | -31.4163 | 90.4037 | -32.1991 | -32.1625 | -18.2465 | -21.8948 | -26.651 | -23.8449 | 90.4495 | -32.1991 | -0.10986 | -0.10986 | 0.67291 | -0.073243 | -108.7601 | -0.10986 | -0.064087 | 0.78278 | 5.4382 | 8.2443 | 13.8428 | 122.493 | 0.67291 | 122.5388 | 10.1944 | -0.10986 | 122.493 | 0.67291 | 10.1944 | 13.8428 | 122.5388 | -122.7127 | -122.7127
466.375 | 122.7356 | -30.0797 | 92.45 | -0.12886 | 0.0087841 | 0.0067206 | 0.06075 | 0.058793 | 0.054961 | 0.1848 | -29.4891 | 92.3904 | -29.8141 | -30.098 | -17.4591 | -18.8324 | -9.9426 | -1.9272 | 91.6122 | -30.8807 | 0.2655 | -0.059509 | 0.59051 | -0.01831 | -109.9091 | -0.80109 | -0.83771 | 0.32501 | 20.137 | 28.1525 | 12.6205 | 122.4701 | 0.59051 | 121.6919 | 11.2473 | -0.80109 | 122.4701 | 0.59051 | 11.2473 | 12.6205 | 121.6919 | -122.2641 | -123.3307
468.1094 | 122.4747 | -54.3823 | 67.662 | -0.22041 | 0.01028 | 0.017402 | 0.058614 | -0.0055072 | -0.0014355 | 0.040606 | -53.1143 | 67.6117 | -54.7073 | 67.6392 | 62.851 | 41.7252 | 64.4073 | 67.5705 | 67.6712 | -54.6616 | -0.32501 | -0.050354 | 1.268 | 122.0215 | -4.8111 | -0.27924 | 0.009156 | 1.593 | 118.7897 | 121.9528 | 117.2333 | 121.994 | 1.268 | 122.0535 | 96.1075 | -0.27924 | 121.994 | 1.268 | 96.1075 | 117.2333 | 122.0535 | -122.3694 | -122.3236
469.8438 | 122.5525 | -55.7556 | 66.4261 | -0.0067901 | 0.010707 | 0.017829 | 0.046651 | -0.0065754 | -0.0029309 | 0.032488 | -54.2404 | 66.3712 | -55.957 | 66.4307 | 63.4323 | 50.679 | 66.275 | 66.4078 | 66.3803 | -56.0211 | -0.20142 | -0.054931 | 1.5152 | 122.1863 | -2.9938 | -0.2655 | -0.045776 | 1.7166 | 122.0306 | 122.1634 | 119.1879 | 122.1268 | 1.5152 | 122.1359 | 106.4346 | -0.2655 | 122.1268 | 1.5152 | 106.4346 | 119.1879 | 122.1359 | -122.3831 | -122.4472
471.5156 | 122.6212 | -58.5342 | 63.6429 | -0.25856 | 0.0094251 | 0.01847 | 0.08254 | -0.009566 | -0.0033581 | 0.060045 | -56.9962 | 63.7161 | -58.7448 | 63.7482 | 62.2467 | 48.793 | 63.7939 | 63.6703 | 63.7894 | -58.6807 | -0.21057 | 0.073242 | 1.5381 | 122.2824 | -1.3962 | -0.14648 | 0.14649 | 1.7487 | 122.3282 | 122.2046 | 120.7809 | 122.2504 | 1.5381 | 122.3236 | 107.3273 | -0.14648 | 122.2504 | 1.5381 | 107.3273 | 120.7809 | 122.3236 | -122.3877 | -122.3236
473.25 | 122.58 | -55.5496 | 66.6962 | -0.19753 | 0.01327 | 0.015479 | 0.062032 | -0.0097796 | -0.0022901 | 0.039324 | -53.8559 | 66.7191 | -55.7465 | 66.7328 | 60.0266 | 57.3303 | 66.7236 | 66.6275 | 66.7465 | -55.7739 | -0.19684 | 0.022888 | 1.6937 | 122.2824 | -6.6696 | -0.2243 | 0.050354 | 1.8906 | 122.2733 | 122.1771 | 115.5762 | 122.2687 | 1.6937 | 122.2961 | 112.8799 | -0.2243 | 122.2687 | 1.6937 | 112.8799 | 115.5762 | 122.2961 | -122.4426 | -122.4701
474.9688 | 122.5571 | -60.91 | 61.3953 | 0.17632 | 0.0096387 | 0.019324 | 0.054982 | -0.0057208 | -0.0050671 | 0.028429 | -58.6212 | 61.441 | -61.0107 | 61.3861 | 58.8455 | 53.801 | 61.4548 | 61.3541 | 61.4822 | -61.0153 | -0.10071 | 0.045776 | 2.2888 | 122.2961 | -2.5497 | -0.10529 | 0.086975 | 2.3895 | 122.3648 | 122.2641 | 119.7556 | 122.3511 | 2.2888 | 122.3923 | 114.711 | -0.10529 | 122.3511 | 2.2888 | 114.711 | 119.7556 | 122.3923 | -122.406 | -122.4106
476.7188 | 122.5204 | -64.4943 | 57.9254 | 0.16869 | 0.0096387 | 0.01847 | 0.069081 | -0.006789 | -0.0089123 | 0.036547 | -61.8851 | 57.7011 | -64.682 | 57.7423 | 57.6416 | 57.8247 | 57.5729 | 57.7835 | 57.724 | -64.7324 | -0.18768 | -0.2243 | 2.6093 | 122.2366 | -0.28381 | -0.23804 | -0.20142 | 2.7969 | 122.0673 | 122.2778 | 122.1359 | 122.1954 | 2.6093 | 122.2183 | 122.319 | -0.23804 | 122.1954 | 2.6093 | 122.319 | 122.1359 | 122.2183 | -122.6074 | -122.6578
478.4688 | 121.1517 | -33.316 | 87.5427 | 0.031357 | 0.0087841 | 0.0086432 | 0.03127 | 0.057512 | 0.063292 | 0.16066 | -32.2678 | 87.4924 | -33.5037 | -32.8812 | -33.3939 | -32.8079 | 87.355 | 87.4878 | 87.4832 | -33.522 | -0.18768 | -0.050354 | 1.0483 | 0.43487 | -120.9366 | -0.20599 | -0.05951 | 1.236 | 120.6711 | 120.8038 | -0.07782 | 120.8084 | 1.0483 | 120.7993 | 0.50812 | -0.20599 | 120.8084 | 1.0483 | 0.50812 | -0.07782 | 120.7993 | -121.0464 | -121.0648
480.1406 | 121.7102 | -30.0842 | 91.4566 | 0.092392 | 0.0087841 | 0.0080024 | 0.042165 | 0.058366 | 0.062224 | 0.17006 | -27.9465 | 92.5598 | -29.0176 | -27.3926 | -28.9352 | -27.3285 | 92.4133 | 92.5278 | 92.5827 | -29.0222 | 1.0666 | 1.1032 | 2.1378 | 2.6917 | -120.3918 | 1.062 | 1.1261 | 1.0712 | 122.4976 | 122.612 | 1.149 | 122.644 | 2.1378 | 122.6669 | 2.7557 | 1.062 | 122.644 | 2.1378 | 2.7557 | 1.149 | 122.6669 | -120.4742 | -120.4788
481.875 | 121.8201 | -35.2386 | 86.2793 | 0.00083945 | 0.0089979 | 0.013129 | 0.046865 | 0.056443 | 0.060515 | 0.17262 | -34.14 | 85.8444 | -35.8383 | -35.2386 | -35.6735 | -35.1791 | 85.7803 | 85.8902 | 85.8719 | -35.7971 | -0.59967 | -0.43488 | 1.0986 | 0 | -121.9528 | -0.55847 | -0.40741 | 1.6983 | 121.019 | 121.1288 | -0.43488 | 121.0831 | 1.0986 | 121.1105 | 0.059509 | -0.55847 | 121.0831 | 1.0986 | 0.059509 | -0.43488 | 121.1105 | -122.1176 | -122.0764
483.5469 | 121.6141 | -46.2387 | 75.1923 | 0.22209 | 0.01028 | 0.015479 | 0.044728 | -0.0070026 | -0.0025037 | 0.022875 | -43.4326 | 75.1785 | -46.3211 | 75.4166 | 75.2563 | 75.4303 | 75.2747 | 75.2792 | 75.3616 | -46.225 | -0.082398 | -0.013733 | 2.8061 | 121.6553 | 0.064087 | 0.013732 | 0.16937 | 2.8885 | 121.5134 | 121.5179 | 121.4951 | 121.4172 | 2.8061 | 121.6003 | 121.669 | 0.013732 | 121.4172 | 2.8061 | 121.669 | 121.4951 | 121.6003 | -121.5134 | -121.4172
485.2969 | 121.5729 | -44.8929 | 76.5564 | 0.19157 | 0.0094251 | 0.015693 | 0.036824 | -0.0072162 | -0.0039989 | 0.018175 | -42.5674 | 76.6525 | -44.9066 | 76.7212 | 75.4211 | 76.7395 | 76.5381 | 76.5884 | 76.6708 | -44.9341 | -0.013733 | 0.096131 | 2.3254 | 121.6141 | -1.1353 | -0.041199 | 0.11444 | 2.3392 | 121.431 | 121.4813 | 120.314 | 121.5454 | 2.3254 | 121.5637 | 121.6324 | -0.041199 | 121.5454 | 2.3254 | 121.6324 | 120.314 | 121.5637 | -121.463 | -121.4905
487.0312 | 121.7514 | -45.9595 | 75.5402 | -0.21278 | 0.011561 | 0.013343 | 0.03597 | -0.008498 | -0.0018627 | 0.016039 | -43.5242 | 75.4395 | -46.1655 | 75.6454 | 75.4715 | 75.6592 | 75.3983 | 75.5905 | 75.5173 | -46.1563 | -0.20599 | -0.10071 | 2.4353 | 121.6049 | -0.068664 | -0.19684 | -0.022888 | 2.6413 | 121.3577 | 121.55 | 121.431 | 121.3989 | 2.4353 | 121.4767 | 121.6187 | -0.19684 | 121.3989 | 2.4353 | 121.6187 | 121.431 | 121.4767 | -121.7056 | -121.6965
488.7031 | 121.9482 | -73.526 | 47.905 | 0.016098 | 0.01028 | 0.029365 | 0.05605 | -0.0087116 | -0.0037853 | 0.02202 | -68.1061 | 48.1064 | -73.5306 | 48.2071 | 46.3394 | 48.2483 | 48.0377 | 48.1247 | 48.1064 | -73.613 | -0.004578 | 0.20142 | 5.4199 | 121.7331 | -1.5656 | -0.086975 | 0.20142 | 5.4245 | 121.5637 | 121.6507 | 119.8654 | 121.6324 | 5.4199 | 121.6324 | 121.7743 | -0.086975 | 121.6324 | 5.4199 | 121.7743 | 119.8654 | 121.6324 | -121.4355 | -121.5179
490.4688 | 121.8292 | -89.7354 | 31.8054 | 0.12291 | 0.011348 | 0.042609 | 0.079976 | -0.0072162 | -0.0033581 | 0.023088 | -82.5851 | 31.8695 | -89.8087 | 31.8558 | 30.368 | 32.0709 | 31.7871 | 31.9794 | 31.8329 | -89.9139 | -0.073242 | 0.064087 | 7.1503 | 121.5912 | -1.4374 | -0.17853 | 0.027466 | 7.2235 | 121.5225 | 121.7148 | 120.1035 | 121.6049 | 7.1503 | 121.5683 | 121.8063 | -0.17853 | 121.6049 | 7.1503 | 121.8063 | 120.1035 | 121.5683 | -121.6141 | -121.7194
492.2031 | 120.8496 | -60.704 | 60.0082 | 0.16869 | 0.01028 | 0.032355 | 0.10155 | -0.0065754 | 0.02014 | 0.087816 | -54.8035 | 60.4706 | -60.2829 | 60.5255 | 12.9868 | 60.5301 | 60.4935 | 60.3516 | 60.5164 | -60.3104 | 0.42114 | 0.46234 | 5.9006 | 121.2296 | -47.0215 | 0.39368 | 0.50812 | 5.4794 | 121.1975 | 121.0556 | 73.6908 | 121.1746 | 5.9006 | 121.2204 | 121.2341 | 0.39368 | 121.1746 | 5.9006 | 121.2341 | 73.6908 | 121.2204 | -120.2911 | -120.3186
493.9375 | 121.8109 | -91.0172 | 30.4504 | -0.20515 | 0.0055799 | 0.043037 | 0.085958 | -0.010421 | 0.00048708 | 0.03676 | -85.3867 | 30.368 | -91.2323 | 30.574 | 21.4325 | 30.574 | 30.3314 | 30.5832 | 30.4092 | -91.2415 | -0.21515 | -0.082397 | 5.6305 | 121.5912 | -9.0179 | -0.2243 | -0.041198 | 5.8456 | 121.3486 | 121.6003 | 112.4496 | 121.3852 | 5.6305 | 121.4264 | 121.5912 | -0.2243 | 121.3852 | 5.6305 | 121.5912 | 112.4496 | 121.4264 | -121.6827 | -121.6919
495.6875 | 121.8201 | -93.5623 | 27.9877 | -0.17464 | 0.013057 | 0.051154 | 0.11287 | -0.0065754 | -0.0031445 | 0.062395 | -83.9584 | 28.244 | -93.457 | 27.0813 | 20.9152 | 27.6627 | 27.713 | 27.7176 | 27.6031 | -94.0659 | 0.10529 | 0.25635 | 9.6039 | 120.6436 | -7.0724 | -0.50354 | -0.38452 | 9.4986 | 121.2753 | 121.2799 | 114.4775 | 121.8063 | 9.6039 | 121.1655 | 121.225 | -0.50354 | 121.8063 | 9.6039 | 121.225 | 114.4775 | 121.1655 | -121.4447 | -122.0535
497.3594 | 121.8887 | -115.2054 | 6.3538 | -0.2433 | 0.010707 | 0.073157 | 0.88363 | -0.0076434 | -0.0046399 | 0.79106 | -110.9207 | 6.2714 | -115.4388 | 6.0196 | 2.3941 | 5.9647 | 6.0883 | 5.8319 | 6.3171 | -115.3976 | -0.23346 | -0.082398 | 4.2847 | 121.225 | -3.9597 | -0.19226 | -0.036621 | 4.5181 | 121.2936 | 121.0373 | 117.5995 | 121.4767 | 4.2847 | 121.5225 | 121.17 | -0.19226 | 121.4767 | 4.2847 | 121.17 | 117.5995 | 121.5225 | -121.7926 | -121.7514
499.0312 | 121.8658 | -114.6378 | 7.077 | -0.21278 | 0.014766 | 0.094306 | 0.17782 | -0.007857 | -0.0033581 | 0.061754 | -108.5083 | 7.077 | -114.7018 | 6.9031 | 1.9821 | 6.8527 | 7.0404 | 7.0312 | 7.1136 | -114.7705 | -0.064087 | 0 | 6.1295 | 121.5408 | -5.0949 | -0.13275 | 0.036621 | 6.1935 | 121.6782 | 121.669 | 116.6199 | 121.7148 | 6.1295 | 121.7514 | 121.4905 | -0.13275 | 121.7148 | 6.1295 | 121.4905 | 116.6199 | 121.7514 | -121.7789 | -121.8475
500.7656 | 121.7651 | -118.6798 | 2.9709 | -0.1899 | 0.0096387 | 0.094947 | 0.68154 | -0.0099934 | -0.0059217 | 0.53664 | -115.274 | 2.9022 | -118.7805 | 2.7512 | 1.8219 | 2.7374 | 2.5635 | 2.7695 | 2.9068 | -118.84 | -0.10071 | -0.068664 | 3.4058 | 121.431 | -1.149 | -0.16022 | -0.064087 | 3.5065 | 121.2433 | 121.4493 | 120.5017 | 121.582 | 3.4058 | 121.5866 | 121.4172 | -0.16022 | 121.582 | 3.4058 | 121.4172 | 120.5017 | 121.5866 | -121.7514 | -121.8109
502.5 | 121.6919 | -119.2841 | 2.1973 | 0.054245 | 1.33 | 1.4226 | 4.5101 | -0.007857 | -0.0052807 | 3.9773 | -29.4067 | 14.6255 | -107.373 | 10.2219 | 1.0941 | 8.4503 | 10.0159 | 9.8236 | 10.9772 | -110.2936 | 11.911 | 12.4283 | 89.8773 | 129.5059 | -1.1032 | 8.9905 | 8.7799 | 77.9663 | 129.2999 | 129.1077 | 120.3781 | 133.9096 | 89.8773 | 130.2612 | 127.7344 | 8.9905 | 133.9096 | 89.8773 | 127.7344 | 120.3781 | 130.2612 | -109.5703 | -112.4908
504.1719 | 121.7102 | -114.798 | 6.7795 | -0.075455 | 0.02032 | 0.78879 | 1.9152 | -0.007857 | -0.0029309 | 1.1209 | -113.205 | -8.9584 | -112.9669 | 8.1528 | 2.4811 | 7.4158 | 8.0338 | 8.1024 | 8.5144 | -113.0814 | 1.8311 | -15.7379 | 1.593 | 122.9507 | -4.2984 | 1.7166 | 1.7349 | -0.23804 | 122.8317 | 122.9004 | 117.2791 | 105.8395 | 1.593 | 123.3124 | 122.2137 | 1.7166 | 105.8395 | 1.593 | 122.2137 | 117.2791 | 123.3124 | -119.7464 | -119.8608
505.9062 | 121.5637 | -3.4607 | 117.9703 | 0.061874 | 0.018825 | 0.034919 | 0.44079 | -0.0080706 | 0.059874 | 0.49263 | -4.8019 | -4.9118 | -5.2917 | 116.4505 | 0.082397 | 116.3589 | 116.2582 | 116.3773 | 116.5421 | -5.0125 | -1.8311 | -122.8821 | -1.3412 | 119.9112 | -117.8879 | -1.5518 | -1.4282 | 0.48981 | 119.7189 | 119.838 | 3.5431 | -1.4511 | -1.3412 | 120.0027 | 119.8196 | -1.5518 | -1.4511 | -1.3412 | 119.8196 | 3.5431 | 120.0027 | -123.262 | -122.9828
507.6406 | 121.3623 | -0.3067 | 121.1105 | 0.10765 | 0.019252 | 0.010779 | 0.7249 | -0.009566 | 0.061583 | 0.78765 | -0.2655 | -0.032043 | -0.42572 | 120.6894 | 0.009155 | 0.022888 | 120.8313 | 120.7031 | 121.0693 | -0.39368 | -0.11902 | -121.1426 | 0.041199 | 120.9961 | -121.1014 | -0.086975 | -0.041199 | 0.16022 | 121.138 | 121.0098 | 0.31586 | 0.27466 | 0.041199 | 121.376 | 0.32959 | -0.086975 | 0.27466 | 0.041199 | 0.32959 | 0.31586 | 121.376 | -121.5363 | -121.5042
509.3125 | 121.3074 | -0.073242 | 121.0785 | -0.19753 | 0.017543 | 0.012488 | 0.18273 | -0.0091388 | 0.06201 | 0.25936 | -0.11902 | 0.073242 | -0.29297 | 120.9686 | 0.036621 | 0.018311 | 120.9732 | 15.6097 | 121.0968 | -0.29755 | -0.21973 | -121.0052 | -0.045777 | 121.0419 | -121.0419 | -0.2243 | 0.018311 | 0.17395 | 121.0464 | 15.683 | 0.10986 | 0.14648 | -0.045777 | 121.17 | 0.091553 | -0.2243 | 0.14648 | -0.045777 | 0.091553 | 0.10986 | 121.17 | -121.3715 | -121.376
511.0469 | 121.6003 | -0.09613 | 121.3852 | -0.25856 | 0.018397 | 0.010139 | 0.037679 | -0.0099934 | 0.062651 | 0.11196 | -0.091553 | 0.11444 | -0.2655 | 121.312 | 0.018311 | 0.018311 | 121.3165 | 0.10529 | 121.3943 | -0.27008 | -0.16937 | -121.2708 | 0.004577 | 121.4081 | -121.3669 | -0.17395 | 0.009155 | 0.17395 | 121.4127 | 0.20142 | 0.11444 | 0.21057 | 0.004577 | 121.4905 | 0.11444 | -0.17395 | 0.21057 | 0.004577 | 0.11444 | 0.11444 | 121.4905 | -121.6507 | -121.6553
512.7812 | 117.5034 | -36.7859 | 80.8182 | 0.046615 | 0.018184 | 0.074012 | 6.9497 | -0.010421 | 0.027403 | 7.0205 | -40.0772 | -8.9401 | -39.9765 | 57.1701 | 0.068665 | 0.10071 | 60.0861 | 0.23804 | 62.9471 | -26.9028 | -3.1906 | -89.7583 | -3.2913 | 93.956 | -80.7495 | 9.8831 | -17.8711 | -0.10071 | 96.8719 | 37.0239 | 36.8546 | 27.8458 | -3.2913 | 99.733 | 36.8866 | 9.8831 | 27.8458 | -3.2913 | 36.8866 | 36.8546 | 99.733 | -120.7947 | -107.7209
514.5156 | 116.4688 | -43.0618 | 73.0911 | -0.12123 | 0.018825 | 0.30344 | 6.9497 | -0.003371 | 0.017363 | 7.0205 | -44.1055 | -8.9401 | -44.0872 | 52.1622 | 0.064087 | 0.045776 | 52.0935 | 0.33417 | 58.8455 | -29.0863 | -1.0254 | -82.0312 | -1.0437 | 95.224 | -73.027 | 13.9755 | -14.2456 | -0.018311 | 95.1553 | 43.396 | 43.1259 | 34.1217 | -1.0437 | 101.9073 | 43.1076 | 13.9755 | 34.1217 | -1.0437 | 43.1076 | 43.1259 | 101.9073 | -117.1783 | -102.1774
516.1875 | 121.0373 | -16.5024 | 104.6127 | 0.16106 | 0.017116 | 0.13254 | 0.022084 | 0.051957 | 0.051543 | 0.016253 | -16.5848 | -8.931 | -16.5802 | 0.11902 | 0.10986 | 0.16479 | -0.11902 | 0.14648 | 104.5029 | -16.5985 | -0.07782 | -113.5437 | -0.082398 | 16.6214 | -104.5029 | -0.096131 | -0.10986 | -0.004578 | 16.3834 | 16.6489 | 16.6122 | 7.5714 | -0.082398 | 121.0052 | 16.6672 | -0.096131 | 7.5714 | -0.082398 | 16.6672 | 16.6122 | 121.0052 | -121.1929 | -121.2112
517.9219 | 121.2982 | -21.8079 | 99.2889 | -0.2433 | 0.020106 | 0.12144 | 0.024221 | 0.04619 | 0.048979 | 0.017748 | -22.1237 | -8.9355 | -22.0322 | -0.009155 | 0.018311 | 0.022888 | 0.10986 | 0.045776 | 99.2523 | -22.0139 | -0.22431 | -108.2245 | -0.31586 | 21.7987 | -99.2706 | -0.20599 | -0.036621 | -0.091552 | 21.9177 | 21.8536 | 21.8262 | 12.8723 | -0.31586 | 121.0602 | 21.8307 | -0.20599 | 12.8723 | -0.31586 | 21.8307 | 21.8262 | 121.0602 | -121.3211 | -121.3028
519.5938 | 121.3028 | -19.1345 | 102.0172 | -0.17464 | 0.017756 | 0.1334 | 0.021871 | 0.046403 | 0.050475 | 0.015825 | -19.2947 | -8.9264 | -19.2719 | 0.1236 | 0.14648 | 0.16479 | -0.07782 | 0.20142 | 101.9852 | -19.3039 | -0.13733 | -110.9436 | -0.16022 | 19.2581 | -101.8707 | -0.16937 | -0.032044 | -0.022888 | 19.0567 | 19.3359 | 19.281 | 10.2081 | -0.16022 | 121.1197 | 19.2993 | -0.16937 | 10.2081 | -0.16022 | 19.2993 | 19.281 | 121.1197 | -121.2891 | -121.3211
521.3281 | 121.2845 | -63.8947 | 57.2479 | 0.19157 | 0.016688 | 0.037696 | 0.028279 | 0.024827 | 0.023986 | 0.051928 | -63.9771 | -8.9584 | -64.0732 | 0.082397 | 0.11902 | 0.17853 | -0.13733 | 0.13275 | 57.1976 | -64.032 | -0.17853 | -66.2064 | -0.082398 | 63.977 | -57.1289 | -0.13733 | -0.050354 | 0.09613 | 63.7573 | 64.0274 | 64.0137 | 54.9362 | -0.082398 | 121.0922 | 64.0732 | -0.13733 | 54.9362 | -0.082398 | 64.0732 | 64.0137 | 121.0922 | -121.3211 | -121.2799
523 | 121.3852 | -61.8027 | 59.3674 | 0.15343 | 0.018397 | 0.035346 | 0.027639 | 0.025468 | 0.028472 | 0.059191 | -59.4223 | -8.9447 | -59.4223 | -0.018311 | -0.004578 | 0.027466 | 0.073242 | 0.018311 | 61.9583 | -59.3948 | 2.3804 | -68.3121 | 2.3804 | 61.7844 | -59.3719 | 2.4078 | 2.5909 | 0 | 61.8759 | 61.821 | 61.7981 | 52.858 | 2.3804 | 123.761 | 61.8301 | 2.4078 | 52.858 | 2.3804 | 61.8301 | 61.7981 | 123.761 | -118.7897 | -118.7622
524.7344 | 121.2891 | -85.4736 | 35.4858 | 0.077133 | 0.015834 | 0.0456 | 0.018666 | 0.011583 | 0.014586 | 0.012194 | -82.5897 | -8.9539 | -83.9905 | 0.027466 | 0.07782 | 0.11902 | -0.041199 | 0.1236 | 36.0489 | -84.4803 | 1.4832 | -44.4397 | 2.8839 | 85.5011 | -35.408 | 0.99335 | 0.56305 | 1.4008 | 85.4324 | 85.5972 | 85.5515 | 76.5198 | 2.8839 | 121.5225 | 85.5927 | 0.99335 | 76.5198 | 2.8839 | 85.5927 | 85.5515 | 121.5225 | -119.4763 | -119.9661
526.4688 | 120.8313 | -60.2646 | 61.0062 | 0.046615 | 0.019252 | 0.050941 | 0.027211 | 0.026109 | 0.026122 | 0.040178 | -60.4385 | -8.9539 | -60.4431 | -0.018311 | -0.022888 | 0.004578 | 0.086975 | 0.009155 | 60.9238 | -60.434 | -0.17853 | -69.96 | -0.17395 | 60.2463 | -61.0291 | -0.16937 | -0.082398 | 0.004577 | 60.3516 | 60.2737 | 60.2417 | 51.3107 | -0.17395 | 121.1884 | 60.2692 | -0.16937 | 51.3107 | -0.17395 | 60.2692 | 60.2417 | 121.1884 | -121.4493 | -121.4401
528.25 | 121.4172 | -112.7747 | 8.4 | 0.16106 | 0.020961 | 0.1381 | 0.33376 | -0.00059378 | -0.00036752 | 0.191 | -112.8021 | -8.9676 | -112.9578 | -0.018311 | 0.027466 | 0.068665 | -0.036621 | 0.33875 | 8.5144 | -112.912 | -0.18311 | -17.3676 | -0.027466 | 112.7563 | -8.3725 | -0.13733 | 0.11444 | 0.15564 | 112.738 | 113.1134 | 112.8021 | 103.8071 | -0.027466 | 121.2891 | 112.8433 | -0.13733 | 103.8071 | -0.027466 | 112.8433 | 112.8021 | 121.2891 | -121.3577 | -121.3119
529.9844 | 121.4676 | -114.8346 | 6.3675 | -0.17464 | 0.017756 | 0.35343 | 0.38012 | -0.0048664 | -0.0018627 | 0.014971 | -115.2878 | -8.9859 | -115.448 | 0.082397 | 0.13275 | 0.16022 | -0.07782 | 0.60425 | 5.9052 | -115.5853 | -0.6134 | -15.3534 | -0.45319 | 114.917 | -6.2347 | -0.75073 | -0.46234 | 0.16022 | 114.7568 | 115.4388 | 114.9673 | 105.8487 | -0.45319 | 120.7397 | 114.9948 | -0.75073 | 105.8487 | -0.45319 | 114.9948 | 114.9673 | 120.7397 | -121.8155 | -121.9528
531.7656 | 121.3257 | -98.9456 | 22.3068 | 0.19157 | 0.019038 | 0.97956 | 1.0485 | 0.0049604 | 0.0068957 | 0.024157 | -98.7442 | -8.963 | -99.0509 | 0.032043 | -0.018311 | 0.022888 | 0.13275 | 0.56305 | 22.0917 | -99.2203 | -0.10529 | -31.2698 | 0.20142 | 98.9777 | -22.3251 | -0.27466 | -0.21515 | 0.3067 | 99.0784 | 99.5087 | 98.9273 | 89.9826 | 0.20142 | 121.0373 | 98.9685 | -0.27466 | 89.9826 | 0.20142 | 98.9685 | 98.9273 | 121.0373 | -121.3577 | -121.5271
533.4531 | 121.2936 | -6.134 | 115.1001 | -0.060196 | 0.018184 | 0.1522 | 0.028066 | 0.052598 | 0.056883 | 0.018175 | -6.0699 | -5.8502 | -6.2439 | 0.31128 | 0.12817 | 0.16479 | 0.14191 | 0.21057 | 115.0772 | -6.2897 | -0.10986 | -120.9503 | 0.064087 | 6.4453 | -114.9719 | -0.15564 | -0.022889 | 0.17395 | 6.2759 | 6.3446 | 6.2622 | 0.28381 | 0.064087 | 121.2112 | 6.2988 | -0.15564 | 0.28381 | 0.064087 | 6.2988 | 6.2622 | 121.2112 | -121.344 | -121.3898
535.125 | 121.312 | -4.7836 | 116.6016 | -0.1136 | 0.021174 | 0.16074 | 0.039388 | 0.053025 | 0.057524 | 0.01967 | -4.747 | -4.4952 | -4.921 | 0.32501 | 0.050354 | 0.073242 | 0.32501 | 0.11902 | 116.5604 | -4.9484 | -0.13733 | -121.0968 | 0.036621 | 5.1086 | -116.5512 | -0.1648 | -0.041198 | 0.17395 | 5.1086 | 4.9026 | 4.834 | 0.28839 | 0.036621 | 121.344 | 4.8569 | -0.1648 | 0.28839 | 0.036621 | 4.8569 | 4.834 | 121.344 | -121.5225 | -121.55
536.8594 | 121.3211 | -4.8248 | 116.629 | -0.090714 | 0.017329 | 0.15797 | 0.041097 | 0.055375 | 0.053893 | 0.018175 | -4.7424 | -4.5456 | -4.9301 | 0.24719 | 0.064087 | 0.086975 | 0.20142 | 0.12817 | 116.5695 | -4.9438 | -0.10529 | -121.1746 | 0.082397 | 5.072 | -116.5649 | -0.11902 | -0.059509 | 0.18768 | 5.0262 | 4.953 | 4.8889 | 0.27924 | 0.082397 | 121.3943 | 4.9118 | -0.11902 | 0.27924 | 0.082397 | 4.9118 | 4.8889 | 121.3943 | -121.5591 | -121.5729
538.5781 | 121.3715 | -4.6692 | 116.7938 | -0.090714 | 0.020534 | 0.15668 | 0.039815 | 0.056443 | 0.056883 | 0.017962 | -4.5776 | -4.3808 | -4.7607 | 0.045776 | 0.059509 | 0.091553 | -0.018311 | 0.09613 | 116.7435 | -4.8019 | -0.091553 | -121.1746 | 0.091552 | 4.715 | -116.7343 | -0.13275 | -0.050354 | 0.1831 | 4.6509 | 4.7653 | 4.7287 | 0.28839 | 0.091552 | 121.4127 | 4.7607 | -0.13275 | 0.28839 | 0.091552 | 4.7607 | 4.7287 | 121.4127 | -121.5546 | -121.5958
540.2812 | 120.6802 | -90.5869 | 29.7638 | 0.1458 | 0.022883 | 1.5055 | 1.4882 | 0.0098736 | 0.010741 | 0.01903 | -91.2323 | -8.9584 | -91.6672 | 0.013733 | 0.004578 | 0.009155 | 0.12817 | 0.70496 | 28.8208 | 8.8165 | -1.0803 | -38.7222 | -0.64545 | 90.6006 | -29.7592 | 99.4034 | -0.94299 | 0.43488 | 90.715 | 91.2918 | 90.5914 | 81.6284 | -0.64545 | 119.4077 | 90.596 | 99.4034 | 81.6284 | -0.64545 | 90.596 | 90.5914 | 119.4077 | -121.431 | -20.9473
542.0312 | 120.8862 | -109.7305 | 10.9177 | -0.052567 | 0.017543 | 0.0088568 | 0.029988 | -0.0012348 | 0.00027348 | 0.020739 | -0.013733 | 0.10071 | -0.21515 | 0 | 0.059509 | 0.073242 | -0.004578 | 0.10071 | 10.9314 | 8.7204 | 109.5154 | -10.817 | 109.7168 | 109.7305 | -10.8582 | 118.4509 | 0.013732 | 0.20142 | 109.726 | 109.8312 | 109.79 | 109.8312 | 109.7168 | 120.6619 | 109.8038 | 118.4509 | 109.8312 | 109.7168 | 109.8038 | 109.79 | 120.6619 | -11.1328 | -2.1973
543.7344 | 120.9824 | -109.8999 | 10.8948 | 0.16106 | 0.018397 | 0.012275 | 0.025289 | -0.0020892 | 0.0021961 | 0.01903 | 0.036621 | 0.086975 | -0.17853 | 0.050354 | 0.13275 | 0.17853 | -0.14191 | 0.1831 | 10.8536 | 8.7204 | 109.7214 | -10.8078 | 109.9365 | 109.9503 | -10.762 | 118.6203 | -0.041198 | 0.21515 | 109.758 | 110.083 | 110.0327 | 109.9869 | 109.9365 | 120.7535 | 110.0784 | 118.6203 | 109.9869 | 109.9365 | 110.0784 | 110.0327 | 120.7535 | -11.0733 | -2.1744
545.5 | 121.0373 | -119.3939 | 1.5015 | 0.18394 | 0.018611 | 0.0090704 | 0.040242 | -0.006789 | -0.0044263 | 0.020311 | 0.050354 | 0.086975 | -0.17853 | 0.068665 | 0.11902 | 0.16937 | -0.16022 | 0.17395 | 1.4465 | 1.1581 | 119.2154 | -1.4145 | 119.4443 | 119.4626 | -1.3824 | 120.5521 | -0.054932 | 0.22888 | 119.2337 | 119.5679 | 119.5129 | 119.4809 | 119.4443 | 120.8405 | 119.5633 | 120.5521 | 119.4809 | 119.4443 | 119.5633 | 119.5129 | 120.8405 | -1.68 | -0.34332
547.1875 | 121.1014 | -119.9524 | 1.03 | -0.12123 | 0.02032 | 0.010779 | 0.044515 | -0.0087116 | -0.0074169 | 0.01967 | -0.009155 | 0.13275 | -0.21515 | 0.022888 | 0.082397 | 0.09613 | -0.018311 | 0.11902 | 1.0162 | 0.6546 | 119.7372 | -0.89722 | 119.9432 | 119.9753 | -0.94757 | 120.607 | -0.013733 | 0.20599 | 119.9341 | 120.0714 | 120.0348 | 120.0851 | 119.9432 | 120.9686 | 120.0485 | 120.607 | 120.0851 | 119.9432 | 120.0485 | 120.0348 | 120.9686 | -1.2451 | -0.37537
548.8906 | 121.1517 | -119.9295 | 1.1353 | 0.13817 | 0.019465 | 0.012275 | 0.039174 | -0.0093524 | -0.0063489 | 0.017748 | 0.045776 | 0.091553 | -0.17395 | 0.059509 | 0.09613 | 0.15106 | -0.13733 | 0.16479 | 1.0941 | 0.78278 | 119.7556 | -1.0437 | 119.9753 | 119.989 | -1.0391 | 120.7123 | -0.041199 | 0.21973 | 119.7922 | 120.0943 | 120.0256 | 120.0211 | 119.9753 | 121.0236 | 120.0806 | 120.7123 | 120.0211 | 119.9753 | 120.0806 | 120.0256 | 121.0236 | -1.3092 | -0.35248
550.5625 | 121.17 | -119.9661 | 1.1398 | -0.037308 | 0.020106 | 0.010779 | 0.044942 | -0.0076434 | -0.0063489 | 0.01967 | -0.009155 | 0.11444 | -0.21973 | 0.009155 | 0.036621 | 0.064087 | -0.009155 | 0.07782 | 1.1307 | 0.76904 | 119.7464 | -1.0254 | 119.957 | 119.9753 | -1.1032 | 120.7352 | -0.009156 | 0.21057 | 119.957 | 120.0439 | 120.0027 | 120.0806 | 119.957 | 121.0968 | 120.0302 | 120.7352 | 120.0806 | 119.957 | 120.0302 | 120.0027 | 121.0968 | -1.3596 | -0.37079
552.2344 | 121.3303 | -120.1401 | 0.90179 | -0.16701 | 0.02032 | 0.013129 | 0.043019 | -0.0097796 | -0.0069897 | 0.018602 | -0.073242 | 0.13275 | -0.21057 | -0.041199 | 0.018311 | 0.027466 | 0.059509 | 0.068665 | 0.97046 | 0.57678 | 119.9295 | -0.76904 | 120.0668 | 120.0989 | -0.88348 | 120.7169 | 0.068665 | 0.13733 | 120.1996 | 120.2087 | 120.1584 | 120.2728 | 120.0668 | 121.1105 | 120.1675 | 120.7169 | 120.2728 | 120.0668 | 120.1675 | 120.1584 | 121.1105 | -1.1124 | -0.32501
553.9219 | 121.257 | -120.5887 | 0.54016 | 0.10765 | 0.019038 | 0.0069342 | 0.045369 | -0.0074298 | -0.0063489 | 0.018389 | -0.064087 | 0.12817 | -0.21515 | -0.064087 | 0.004578 | 0.050354 | 0 | 0.041199 | 0.56305 | 0.16479 | 120.3735 | -0.41199 | 120.5246 | 120.5246 | -0.53558 | 120.7535 | 0.022888 | 0.15106 | 120.5887 | 120.6299 | 120.5933 | 120.7169 | 120.5246 | 121.1517 | 120.639 | 120.7535 | 120.7169 | 120.5246 | 120.639 | 120.5933 | 121.1517 | -0.75531 | -0.37537
555.6094 | 121.3898 | -120.6985 | 0.4303 | -0.2433 | 0.016902 | 0.012702 | 0.042379 | -0.0089252 | -0.0052807 | 0.018389 | -0.073242 | 0.12817 | -0.22888 | -0.059509 | 0.022888 | 0.027466 | 0.10071 | 0.073242 | 0.47607 | 0.10071 | 120.4697 | -0.30212 | 120.6253 | 120.639 | -0.40741 | 120.7993 | 0.045776 | 0.15564 | 120.7993 | 120.7718 | 120.7214 | 120.8267 | 120.6253 | 121.1746 | 120.726 | 120.7993 | 120.8267 | 120.6253 | 120.726 | 120.7214 | 121.1746 | -0.65918 | -0.32959
557.2812 | 121.3531 | -120.6619 | 0.51727 | -0.13649 | 0.019252 | 0.0080024 | 0.037679 | -0.0091388 | -0.0052807 | 0.018602 | 0.050354 | 0.086975 | -0.16937 | 0.054932 | 0.13733 | 0.17853 | -0.1236 | 0.2243 | 0.50812 | 0.18768 | 120.4926 | -0.4303 | 120.7123 | 120.7169 | -0.37994 | 120.8496 | -0.009155 | 0.21973 | 120.5383 | 120.8862 | 120.7993 | 120.7489 | 120.7123 | 121.17 | 120.8405 | 120.8496 | 120.7489 | 120.7123 | 120.8405 | 120.7993 | 121.17 | -0.68665 | -0.32959
558.9375 | 121.3348 | -120.7855 | 0.39825 | 0.10002 | 0.019465 | 0.009284 | 0.048787 | -0.0089252 | -0.0069897 | 0.01967 | -0.07782 | 0.1236 | -0.23804 | -0.054932 | -0.004578 | 0.027466 | 0.032043 | 0.018311 | 0.44861 | 0.068665 | 120.5475 | -0.27466 | 120.7077 | 120.7306 | -0.40283 | 120.8542 | 0.050354 | 0.16022 | 120.8176 | 120.8038 | 120.7809 | 120.9091 | 120.7077 | 121.2341 | 120.813 | 120.8542 | 120.9091 | 120.7077 | 120.813 | 120.7809 | 121.2341 | -0.63629 | -0.32959
560.625 | 121.344 | -120.845 | 0.39825 | 0.00083945 | 0.018611 | 0.011207 | 0.047078 | -0.010207 | -0.0072033 | 0.01903 | -0.027466 | 0.13733 | -0.22888 | -0.013733 | -0.004578 | 0.027466 | 0.022888 | 0.050354 | 0.40741 | 0.027466 | 120.6162 | -0.26092 | 120.8176 | 120.8313 | -0.40283 | 120.8725 | 0.009156 | 0.20142 | 120.8679 | 120.8954 | 120.8405 | 120.9824 | 120.8176 | 121.2524 | 120.8725 | 120.8725 | 120.9824 | 120.8176 | 120.8725 | 120.8405 | 121.2524 | -0.62714 | -0.37079
562.2969 | 121.4813 | -120.8405 | 0.37537 | -0.19753 | 0.019252 | 0.0077888 | 0.044301 | -0.010634 | -0.0061353 | 0.017107 | -0.054932 | 0.13275 | -0.19226 | -0.036621 | 0.013733 | 0.041199 | 0.073242 | 0.082397 | 0.43488 | 0.027466 | 120.6482 | -0.24261 | 120.7855 | 120.8038 | -0.36163 | 120.8679 | 0.059509 | 0.13733 | 120.9137 | 120.9229 | 120.8542 | 120.9732 | 120.7855 | 121.2753 | 120.8817 | 120.8679 | 120.9732 | 120.7855 | 120.8817 | 120.8542 | 121.2753 | -0.56763 | -0.3479
564.0156 | 121.3898 | -120.4559 | 0.8194 | 0.13054 | 0.019038 | 0.012916 | 0.044515 | -0.0059344 | -0.0067761 | 0.019243 | -0.036621 | 0.1236 | -0.21057 | -0.018311 | 0.018311 | 0.059509 | -0.036621 | 0.073242 | 0.83313 | 0.48981 | 120.2454 | -0.6958 | 120.4193 | 120.4376 | -0.80109 | 120.9457 | 0.013733 | 0.17395 | 120.4193 | 120.5292 | 120.4742 | 120.5795 | 120.4193 | 121.2891 | 120.5154 | 120.9457 | 120.5795 | 120.4193 | 120.5154 | 120.4742 | 121.2891 | -1.03 | -0.32959
565.6875 | 121.3531 | -120.5292 | 0.79651 | -0.052567 | 0.017543 | 0.0086432 | 0.043019 | -0.008498 | -0.0048535 | 0.017748 | -0.004578 | 0.086975 | -0.21057 | 0.022888 | 0.064087 | 0.086975 | -0.009155 | 0.1236 | 0.79193 | 0.44403 | 120.3186 | -0.70953 | 120.5246 | 120.5521 | -0.73242 | 120.9732 | -0.004578 | 0.20599 | 120.52 | 120.6528 | 120.5933 | 120.6161 | 120.5246 | 121.3211 | 120.6161 | 120.9732 | 120.6161 | 120.5246 | 120.6161 | 120.5933 | 121.3211 | -1.0071 | -0.35248
567.3594 | 121.3989 | -120.5978 | 0.76904 | -0.083084 | 0.019893 | 0.0075752 | 0.044728 | -0.0074298 | -0.0082715 | 0.019243 | 0 | 0.1236 | -0.20599 | 0.032043 | 0.073242 | 0.086975 | 0.009155 | 0.11444 | 0.7782 | 0.41199 | 120.3918 | -0.64545 | 120.5978 | 120.6299 | -0.6958 | 121.0098 | 0.009155 | 0.20599 | 120.607 | 120.7123 | 120.6711 | 120.7214 | 120.5978 | 121.376 | 120.6848 | 121.0098 | 120.7214 | 120.5978 | 120.6848 | 120.6711 | 121.376 | -0.97504 | -0.35706
569.0469 | 121.4539 | -120.5978 | 0.75073 | 0.077133 | 0.018397 | 0.008216 | 0.04366 | -0.0072162 | -0.0059217 | 0.018602 | -0.022888 | 0.11902 | -0.21515 | -0.036621 | 0.004578 | 0.022888 | 0.041199 | 0.036621 | 0.75989 | 0.37537 | 120.3827 | -0.63171 | 120.575 | 120.5612 | -0.74615 | 120.9732 | 0.009156 | 0.19226 | 120.639 | 120.6345 | 120.6024 | 120.7169 | 120.575 | 121.3577 | 120.6207 | 120.9732 | 120.7169 | 120.575 | 120.6207 | 120.6024 | 121.3577 | -0.96588 | -0.37537
570.7188 | 121.4539 | -120.6482 | 0.70496 | 0.13817 | 0.017329 | 0.010352 | 0.044942 | -0.0099934 | -0.0078443 | 0.018602 | -0.082397 | 0.14648 | -0.2243 | -0.054932 | -0.013733 | 0.027466 | 0.068665 | 0.018311 | 0.72327 | 0.33417 | 120.4239 | -0.55847 | 120.5658 | 120.5933 | -0.71869 | 120.9824 | 0.018311 | 0.14191 | 120.7169 | 120.6665 | 120.6345 | 120.7947 | 120.5658 | 121.3715 | 120.6757 | 120.9824 | 120.7947 | 120.5658 | 120.6757 | 120.6345 | 121.3715 | -0.92926 | -0.37079
572.3906 | 121.431 | -120.6482 | 0.76904 | 0.15343 | 0.01797 | 0.0088568 | 0.040242 | -0.0099934 | -0.0059217 | 0.017534 | 0.045776 | 0.082397 | -0.16937 | 0.059509 | 0.12817 | 0.17853 | -0.12817 | 0.18768 | 0.69122 | 0.42114 | 120.4788 | -0.68665 | 120.694 | 120.7077 | -0.64087 | 121.0693 | -0.07782 | 0.21515 | 120.52 | 120.8359 | 120.7764 | 120.7306 | 120.694 | 121.3394 | 120.8267 | 121.0693 | 120.7306 | 120.694 | 120.8267 | 120.7764 | 121.3394 | -0.93842 | -0.3479
574.0625 | 121.4951 | -120.7352 | 0.65918 | 0.077133 | 0.01797 | 0.010139 | 0.045583 | -0.008498 | -0.0061353 | 0.020739 | -0.064087 | 0.1236 | -0.21057 | -0.032043 | -0.013733 | 0.018311 | 0.07782 | 0.032043 | 0.67749 | 0.29297 | 120.5246 | -0.53558 | 120.6711 | 120.7031 | -0.67291 | 121.0281 | 0.01831 | 0.14648 | 120.813 | 120.7672 | 120.7214 | 120.8588 | 120.6711 | 121.4127 | 120.7535 | 121.0281 | 120.8588 | 120.6711 | 120.7535 | 120.7214 | 121.4127 | -0.86975 | -0.36621
575.7344 | 121.5042 | -120.7947 | 0.57678 | -0.15175 | 0.017543 | 0.01142 | 0.043019 | -0.0076434 | -0.0065625 | 0.017321 | -0.018311 | 0.12817 | -0.20142 | 0.013733 | 0.059509 | 0.07782 | 0.018311 | 0.1236 | 0.59509 | 0.24261 | 120.5933 | -0.44861 | 120.7764 | 120.8084 | -0.51727 | 121.0373 | 0.018311 | 0.18311 | 120.813 | 120.9183 | 120.8542 | 120.9229 | 120.7764 | 121.3898 | 120.8725 | 121.0373 | 120.9229 | 120.7764 | 120.8725 | 120.8542 | 121.3898 | -0.7782 | -0.33417
577.4062 | 121.6187 | -120.8908 | 0.4715 | -0.2433 | 0.018184 | 0.0058662 | 0.042592 | -0.0076434 | -0.0065625 | 0.01903 | -0.068665 | 0.13275 | -0.21515 | -0.032043 | 0.013733 | 0.022888 | 0.09613 | 0.068665 | 0.51727 | 0.12817 | 120.6757 | -0.33875 | 120.8221 | 120.8588 | -0.45776 | 121.019 | 0.045776 | 0.14648 | 120.9869 | 120.9595 | 120.9045 | 121.0236 | 120.8221 | 121.4081 | 120.9137 | 121.019 | 121.0236 | 120.8221 | 120.9137 | 120.9045 | 121.4081 | -0.68665 | -0.34332
579.0781 | 121.5317 | -121.0144 | 0.43488 | 0.15343 | 0.018397 | 0.009284 | 0.041524 | -0.0074298 | -0.0084851 | 0.017748 | -0.050354 | 0.11902 | -0.19226 | -0.022888 | 0.022888 | 0.059509 | -0.022888 | 0.064087 | 0.44403 | 0.082397 | 120.8221 | -0.31586 | 120.9641 | 120.9915 | -0.41199 | 121.0968 | 0.009156 | 0.14191 | 120.9915 | 121.0785 | 121.0373 | 121.1334 | 120.9641 | 121.4584 | 121.0739 | 121.0968 | 121.1334 | 120.9641 | 121.0739 | 121.0373 | 121.4584 | -0.62714 | -0.35248
580.7812 | 121.5042 | -121.019 | 0.42572 | 0.16869 | 0.019679 | 0.009925 | 0.044728 | -0.0065754 | -0.0046399 | 0.017534 | 0.032043 | 0.09613 | -0.1831 | 0.059509 | 0.091553 | 0.16479 | -0.11444 | 0.14648 | 0.40283 | 0.10986 | 120.8359 | -0.32959 | 121.051 | 121.0785 | -0.33417 | 121.1288 | -0.022888 | 0.21515 | 120.9045 | 121.1655 | 121.1105 | 121.1151 | 121.051 | 121.4218 | 121.1838 | 121.1288 | 121.1151 | 121.051 | 121.1838 | 121.1105 | 121.4218 | -0.60882 | -0.31586
582.4531 | 121.6415 | -121.0236 | 0.42572 | -0.18227 | 0.018825 | 0.0058662 | 0.043233 | -0.0091388 | -0.0069897 | 0.017534 | -0.068665 | 0.11902 | -0.20599 | -0.018311 | 0.027466 | 0.036621 | 0.09613 | 0.07782 | 0.44861 | 0.068665 | 120.8176 | -0.3067 | 120.9549 | 121.0052 | -0.39825 | 121.0922 | 0.022888 | 0.13733 | 121.1197 | 121.1014 | 121.051 | 121.1426 | 120.9549 | 121.4722 | 121.0602 | 121.0922 | 121.1426 | 120.9549 | 121.0602 | 121.051 | 121.4722 | -0.63171 | -0.35706
584.125 | 121.6782 | -121.0419 | 0.37537 | -0.2433 | 0.019679 | 0.0090704 | 0.042165 | -0.01213 | -0.0054943 | 0.019243 | -0.045776 | 0.10986 | -0.19684 | -0.013733 | 0.018311 | 0.045776 | 0.064087 | 0.09613 | 0.42114 | 0.032043 | 120.845 | -0.2655 | 120.9961 | 121.0281 | -0.35705 | 121.0739 | 0.045777 | 0.15106 | 121.106 | 121.138 | 121.0602 | 121.1517 | 120.9961 | 121.463 | 121.0876 | 121.0739 | 121.1517 | 120.9961 | 121.0876 | 121.0602 | 121.463 | -0.5722 | -0.34332
585.7969 | 121.6461 | -121.1334 | 0.30212 | -0.20515 | 0.017329 | 0.0041572 | 0.040456 | -0.010207 | -0.0039989 | 0.016466 | 0.032043 | 0.10071 | -0.16937 | 0.073242 | 0.11444 | 0.13275 | -0.032043 | 0.20142 | 0.29297 | -0.009155 | 120.9641 | -0.20142 | 121.1655 | 121.2067 | -0.18768 | 121.1243 | -0.009155 | 0.20142 | 121.1014 | 121.3348 | 121.2479 | 121.2341 | 121.1655 | 121.4264 | 121.2662 | 121.1243 | 121.2341 | 121.1655 | 121.2662 | 121.2479 | 121.4264 | -0.4715 | -0.31128
587.5156 | 121.701 | -121.1563 | 0.32044 | -0.22804 | 0.018825 | 0.0069342 | 0.046437 | -0.011275 | -0.0078443 | 0.018602 | -0.068665 | 0.13733 | -0.2243 | -0.050354 | 0.018311 | 0.022888 | 0.10529 | 0.064087 | 0.32959 | -0.054932 | 120.932 | -0.18311 | 121.0876 | 121.106 | -0.30212 | 121.1014 | 0.009155 | 0.15564 | 121.2616 | 121.2204 | 121.1746 | 121.2936 | 121.0876 | 121.4859 | 121.1792 | 121.1014 | 121.2936 | 121.0876 | 121.1792 | 121.1746 | 121.4859 | -0.54474 | -0.37537
589.1719 | 121.5591 | -121.1838 | 0.32044 | 0.16869 | 0.01797 | 0.009284 | 0.043233 | -0.009566 | -0.0057079 | 0.018389 | 0.068665 | 0.059509 | -0.16937 | 0.064087 | 0.10529 | 0.16022 | -0.17395 | 0.18768 | 0.29297 | -0.013733 | 121.0144 | -0.26093 | 121.2524 | 121.2479 | -0.21515 | 121.17 | -0.027466 | 0.23804 | 121.0098 | 121.3715 | 121.2891 | 121.2433 | 121.2524 | 121.4767 | 121.344 | 121.17 | 121.2433 | 121.2524 | 121.344 | 121.2891 | 121.4767 | -0.48981 | -0.33417
590.8438 | 121.6095 | -121.225 | 0.30212 | -0.044937 | 0.018611 | 0.012916 | 0.047292 | -0.0076434 | -0.0072033 | 0.020098 | 0 | 0.11902 | -0.20142 | -0.004578 | 0.041199 | 0.064087 | 0 | 0.091553 | 0.32044 | -0.045776 | 121.0236 | -0.18311 | 121.225 | 121.2204 | -0.26093 | 121.1792 | 0.018311 | 0.20142 | 121.225 | 121.3165 | 121.2662 | 121.344 | 121.225 | 121.5454 | 121.2891 | 121.1792 | 121.344 | 121.225 | 121.2891 | 121.2662 | 121.5454 | -0.50354 | -0.3479
592.5156 | 121.7514 | -121.2158 | 0.27466 | -0.23567 | 0.018825 | 0.008216 | 0.044088 | -0.011061 | -0.0057079 | 0.016253 | -0.059509 | 0.13733 | -0.2243 | -0.045776 | 0.009155 | 0.036621 | 0.09613 | 0.073242 | 0.32044 | -0.082397 | 120.9915 | -0.13733 | 121.1563 | 121.17 | -0.2655 | 121.1334 | 0.045777 | 0.16479 | 121.3119 | 121.2891 | 121.225 | 121.3531 | 121.1563 | 121.5363 | 121.2524 | 121.1334 | 121.3531 | 121.1563 | 121.2524 | 121.225 | 121.5363 | -0.49896 | -0.35706
594.1719 | 121.7468 | -121.2387 | 0.26093 | 0.069504 | 0.017543 | 0.009925 | 0.040883 | -0.0082844 | -0.0044263 | 0.017534 | 0 | 0.09613 | -0.16937 | -0.004578 | 0.073242 | 0.10986 | -0.07782 | 0.12817 | 0.28839 | -0.027466 | 121.0693 | -0.1648 | 121.2387 | 121.2341 | -0.18768 | 121.2112 | 0.027466 | 0.16937 | 121.1609 | 121.3669 | 121.3119 | 121.3348 | 121.2387 | 121.5271 | 121.3486 | 121.2112 | 121.3348 | 121.2387 | 121.3486 | 121.3119 | 121.5271 | -0.4303 | -0.28839
595.8438 | 121.669 | -121.3074 | 0.27008 | 0.077133 | 0.017116 | 0.014838 | 0.047933 | -0.010207 | -0.0063489 | 0.01668 | -0.064087 | 0.12817 | -0.21515 | -0.068665 | -0.036621 | 0 | 0.027466 | 0.036621 | 0.30212 | -0.073242 | 121.0922 | -0.14191 | 121.2433 | 121.2387 | -0.3067 | 121.2341 | 0.032043 | 0.15106 | 121.3348 | 121.344 | 121.2708 | 121.4355 | 121.2433 | 121.6095 | 121.3074 | 121.2341 | 121.4355 | 121.2433 | 121.3074 | 121.2708 | 121.6095 | -0.48523 | -0.34332
597.5469 | 121.6599 | -121.3348 | 0.29297 | -0.037308 | 0.017329 | 0.009284 | 0.048574 | -0.009566 | -0.0069897 | 0.01967 | -0.013733 | 0.10986 | -0.19684 | -0.018311 | 0.036621 | 0.054932 | -0.009155 | 0.073242 | 0.27008 | -0.068665 | 121.138 | -0.18311 | 121.3211 | 121.3165 | -0.25635 | 121.2662 | -0.022888 | 0.18311 | 121.3257 | 121.4081 | 121.3715 | 121.4447 | 121.3211 | 121.6049 | 121.3898 | 121.2662 | 121.4447 | 121.3211 | 121.3898 | 121.3715 | 121.6049 | -0.48981 | -0.36163
599.2188 | 121.8063 | -121.2799 | 0.21057 | -0.22041 | 0.018397 | 0.0067206 | 0.041951 | -0.011702 | -0.0050671 | 0.017534 | -0.041199 | 0.12817 | -0.20142 | -0.036621 | 0.018311 | 0.027466 | 0.064087 | 0.091553 | 0.26093 | -0.10071 | 121.0785 | -0.082397 | 121.2387 | 121.2433 | -0.19226 | 121.1792 | 0.050354 | 0.16022 | 121.344 | 121.3715 | 121.2982 | 121.4081 | 121.2387 | 121.5408 | 121.3074 | 121.1792 | 121.4081 | 121.2387 | 121.3074 | 121.2982 | 121.5408 | -0.41199 | -0.31128
600.9688 | 121.6919 | -121.3486 | 0.2655 | -0.029679 | 0.019038 | 0.01142 | 0.046865 | -0.006789 | -0.0057079 | 0.016253 | -0.004578 | 0.1236 | -0.20142 | -0.009155 | 0.022888 | 0.054932 | 0 | 0.07782 | 0.25635 | -0.09613 | 121.1472 | -0.14191 | 121.344 | 121.3394 | -0.24261 | 121.2524 | -0.009155 | 0.19684 | 121.3486 | 121.4264 | 121.3715 | 121.4722 | 121.344 | 121.6049 | 121.4035 | 121.2524 | 121.4722 | 121.344 | 121.4035 | 121.3715 | 121.6049 | -0.46692 | -0.36163
602.7344 | 121.7606 | -121.3348 | 0.21515 | -0.13649 | 0.016688 | 0.010566 | 0.037892 | -0.0091388 | -0.0050671 | 0.016893 | 0.032043 | 0.073242 | -0.17853 | 0.073242 | 0.13275 | 0.16937 | -0.11902 | 0.21057 | 0.19684 | -0.091553 | 121.1563 | -0.14191 | 121.3669 | 121.4081 | -0.082398 | 121.2433 | -0.018311 | 0.21057 | 121.2158 | 121.5454 | 121.4676 | 121.4081 | 121.3669 | 121.5317 | 121.5042 | 121.2433 | 121.4081 | 121.3669 | 121.5042 | 121.4676 | 121.5317 | -0.39368 | -0.3067
604.4844 | 121.7331 | -121.4127 | 0.21973 | 0.10765 | 0.016261 | 0.010779 | 0.047078 | -0.0087116 | -0.0074169 | 0.016039 | -0.064087 | 0.10529 | -0.21515 | -0.050354 | -0.027466 | 0.022888 | 0.027466 | 0.041199 | 0.2243 | -0.1236 | 121.1975 | -0.11444 | 121.3486 | 121.3623 | -0.24719 | 121.2891 | 0.004577 | 0.15106 | 121.4401 | 121.4539 | 121.3852 | 121.5179 | 121.3486 | 121.637 | 121.4355 | 121.2891 | 121.5179 | 121.3486 | 121.4355 | 121.3852 | 121.637 | -0.43488 | -0.34332
606.1719 | 121.7743 | -121.3898 | 0.21057 | -0.17464 | 0.018397 | 0.011848 | 0.039601 | -0.011061 | -0.0050671 | 0.018389 | 0.032043 | 0.082397 | -0.16022 | 0.073242 | 0.1236 | 0.17853 | -0.10529 | 0.2243 | 0.18768 | -0.091553 | 121.2296 | -0.12817 | 121.4218 | 121.463 | -0.086975 | 121.2982 | -0.022888 | 0.19226 | 121.2845 | 121.6141 | 121.5134 | 121.4722 | 121.4218 | 121.5775 | 121.5683 | 121.2982 | 121.4722 | 121.4218 | 121.5683 | 121.5134 | 121.5775 | -0.37079 | -0.30212
607.9062 | 121.8521 | -121.3806 | 0.17395 | 0.016098 | 0.019893 | 0.0080024 | 0.041524 | -0.011916 | -0.0025037 | 0.016466 | -0.013733 | 0.10986 | -0.1831 | 0 | 0.068665 | 0.10529 | -0.086975 | 0.14648 | 0.20599 | -0.12817 | 121.1975 | -0.064087 | 121.3669 | 121.3806 | -0.10528 | 121.2524 | 0.032044 | 0.16937 | 121.2936 | 121.5271 | 121.4493 | 121.4905 | 121.3669 | 121.5866 | 121.4859 | 121.2524 | 121.4905 | 121.3669 | 121.4859 | 121.4493 | 121.5866 | -0.35706 | -0.30212
609.6406 | 121.7697 | -121.4539 | 0.20599 | 0.16869 | 0.019038 | 0.008216 | 0.042379 | -0.0099934 | -0.0046399 | 0.016039 | 0.032043 | 0.091553 | -0.16022 | 0.032043 | 0.082397 | 0.13275 | -0.11444 | 0.14648 | 0.1831 | -0.11444 | 121.2936 | -0.11444 | 121.4859 | 121.4859 | -0.1236 | 121.3394 | -0.022889 | 0.19226 | 121.3394 | 121.6003 | 121.5363 | 121.5454 | 121.4859 | 121.637 | 121.5866 | 121.3394 | 121.5454 | 121.4859 | 121.5866 | 121.5363 | 121.637 | -0.36621 | -0.32044
611.375 | 121.875 | -121.4493 | 0.17853 | -0.18227 | 0.019252 | 0.0094978 | 0.046437 | -0.01277 | -0.0065625 | 0.015612 | -0.068665 | 0.10986 | -0.21973 | -0.027466 | -0.004578 | 0.013733 | 0.073242 | 0.091553 | 0.22888 | -0.15564 | 121.2296 | -0.068665 | 121.3806 | 121.4218 | -0.18311 | 121.2936 | 0.050354 | 0.15106 | 121.5225 | 121.5408 | 121.4447 | 121.5591 | 121.3806 | 121.6782 | 121.463 | 121.2936 | 121.5591 | 121.3806 | 121.463 | 121.4447 | 121.6782 | -0.39826 | -0.33417
613.1094 | 121.7606 | -121.4584 | 0.20599 | -0.12886 | 0.017329 | 0.0071478 | 0.048574 | -0.010421 | -0.0080579 | 0.018389 | -0.013733 | 0.11902 | -0.2243 | 0.018311 | 0.041199 | 0.068665 | 0 | 0.1236 | 0.2243 | -0.13275 | 121.2341 | -0.086975 | 121.4447 | 121.4767 | -0.1648 | 121.3257 | 0.01831 | 0.21057 | 121.4584 | 121.582 | 121.4996 | 121.5775 | 121.4447 | 121.6827 | 121.5271 | 121.3257 | 121.5775 | 121.4447 | 121.5271 | 121.4996 | 121.6827 | -0.4303 | -0.33875
614.8438 | 121.8887 | -121.4539 | 0.17853 | -0.22041 | 0.019893 | 0.010352 | 0.044728 | -0.010848 | -0.0063489 | 0.016039 | -0.045776 | 0.11444 | -0.19684 | -0.036621 | 0.009155 | 0.036621 | 0.050354 | 0.09613 | 0.21057 | -0.14648 | 121.257 | -0.064087 | 121.4081 | 121.4172 | -0.16937 | 121.3074 | 0.032043 | 0.15106 | 121.5042 | 121.55 | 121.463 | 121.5683 | 121.4081 | 121.6644 | 121.4905 | 121.3074 | 121.5683 | 121.4081 | 121.4905 | 121.463 | 121.6644 | -0.37537 | -0.32501
616.5156 | 121.7789 | -121.4722 | 0.20142 | 0.12291 | 0.017756 | 0.010352 | 0.042165 | -0.0087116 | -0.0065625 | 0.01668 | 0.054932 | 0.091553 | -0.16022 | 0.045776 | 0.07782 | 0.16022 | -0.16022 | 0.16937 | 0.19226 | -0.10986 | 121.312 | -0.10986 | 121.5271 | 121.5179 | -0.1236 | 121.3623 | -0.009155 | 0.21515 | 121.312 | 121.6415 | 121.55 | 121.5637 | 121.5271 | 121.6644 | 121.6324 | 121.3623 | 121.5637 | 121.5271 | 121.6324 | 121.55 | 121.6644 | -0.36163 | -0.31128
618.2656 | 121.8979 | -121.4584 | 0.18768 | -0.01442 | 0.017329 | 0.0026618 | 0.042379 | -0.010207 | -0.0048535 | 0.018175 | 0.004578 | 0.10071 | -0.16937 | 0.032043 | 0.091553 | 0.13275 | -0.086975 | 0.16479 | 0.20142 | -0.11902 | 121.2891 | -0.086975 | 121.463 | 121.4905 | -0.09613 | 121.3394 | 0.013733 | 0.17395 | 121.3715 | 121.6232 | 121.55 | 121.5591 | 121.463 | 121.6599 | 121.5912 | 121.3394 | 121.5591 | 121.463 | 121.5912 | 121.55 | 121.6599 | -0.35706 | -0.3067
619.9375 | 121.7468 | -121.4859 | 0.21973 | 0.17632 | 0.018825 | 0.010139 | 0.048146 | -0.0091388 | -0.0089123 | 0.017962 | 0.068665 | 0.082397 | -0.15106 | 0.068665 | 0.10071 | 0.16937 | -0.17853 | 0.18768 | 0.16937 | -0.07782 | 121.3348 | -0.13733 | 121.5546 | 121.5546 | -0.11902 | 121.4081 | -0.050354 | 0.21973 | 121.3074 | 121.6736 | 121.5866 | 121.5683 | 121.5546 | 121.6553 | 121.6553 | 121.4081 | 121.5683 | 121.5546 | 121.6553 | 121.5866 | 121.6553 | -0.37079 | -0.29755
621.6719 | 121.8613 | -121.4722 | 0.17853 | -0.20515 | 0.016475 | 0.0058662 | 0.044088 | -0.011489 | -0.0065625 | 0.016466 | 0.059509 | 0.091553 | -0.16937 | 0.09613 | 0.1236 | 0.15106 | -0.091553 | 0.21973 | 0.18768 | -0.10986 | 121.3028 | -0.086975 | 121.5317 | 121.5683 | -0.054932 | 121.3623 | 0.009155 | 0.22888 | 121.3806 | 121.6919 | 121.5958 | 121.5637 | 121.5317 | 121.6599 | 121.6232 | 121.3623 | 121.5637 | 121.5317 | 121.6232 | 121.5958 | 121.6599 | -0.3479 | -0.28839
623.4219 | 121.8018 | -121.4584 | 0.29297 | 0.1992 | 0.017543 | 0.015052 | 0.04836 | -0.0089252 | -0.0061353 | 0.018389 | 0.004578 | 0.1236 | -0.19226 | 0.027466 | 0.059509 | 0.11444 | -0.10986 | 0.11902 | 0.26093 | -0.045776 | 121.2662 | -0.16937 | 121.463 | 121.4859 | -0.23346 | 121.4127 | -0.032044 | 0.19684 | 121.3486 | 121.5775 | 121.5179 | 121.582 | 121.463 | 121.7194 | 121.5729 | 121.4127 | 121.582 | 121.463 | 121.5729 | 121.5179 | 121.7194 | -0.48523 | -0.33874
625.1406 | 121.9208 | -120.8908 | 0.77362 | -0.01442 | 0.019252 | 0.012702 | 0.043447 | -0.011702 | -0.0044263 | 0.018389 | 0.013733 | 0.091553 | -0.18768 | 0.045776 | 0.10071 | 0.12817 | -0.082397 | 0.1831 | 0.80109 | 0.48981 | 120.7031 | -0.68207 | 120.9045 | 120.9366 | -0.67291 | 121.3806 | 0.027465 | 0.20142 | 120.8084 | 121.0739 | 120.9915 | 120.9824 | 120.9045 | 121.6919 | 121.019 | 121.3806 | 120.9824 | 120.9045 | 121.019 | 120.9915 | 121.6919 | -0.9613 | -0.28381
626.8125 | 121.9254 | -120.9412 | 0.75073 | -0.22041 | 0.020534 | 0.0080024 | 0.047078 | -0.008498 | -0.0076305 | 0.020098 | -0.036621 | 0.13275 | -0.21973 | -0.032043 | 0 | 0.032043 | 0.054932 | 0.07782 | 0.78278 | 0.41199 | 120.7214 | -0.61798 | 120.9045 | 120.9091 | -0.75073 | 121.3531 | 0.032044 | 0.18311 | 120.9961 | 121.019 | 120.9412 | 121.0739 | 120.9045 | 121.7239 | 120.9732 | 121.3531 | 121.0739 | 120.9045 | 120.9732 | 120.9412 | 121.7239 | -0.97046 | -0.33874
628.5469 | 121.8246 | -121.0327 | 0.73242 | 0.1992 | 0.018611 | 0.0018072 | 0.049642 | -0.008498 | -0.0065625 | 0.01668 | -0.032043 | 0.11902 | -0.20599 | 0.004578 | 0.041199 | 0.086975 | -0.07782 | 0.09613 | 0.71411 | 0.39825 | 120.8267 | -0.6134 | 121.0007 | 121.0373 | -0.69122 | 121.431 | -0.018311 | 0.17395 | 120.9549 | 121.1288 | 121.0739 | 121.1517 | 121.0007 | 121.7468 | 121.1197 | 121.431 | 121.1517 | 121.0007 | 121.1197 | 121.0739 | 121.7468 | -0.93842 | -0.33417
630.2188 | 121.8246 | -121.1014 | 0.65918 | 0.15343 | 0.016261 | 0.0069342 | 0.043019 | -0.010207 | -0.0059217 | 0.016466 | 0.050354 | 0.059509 | -0.16479 | 0.073242 | 0.11444 | 0.16022 | -0.15106 | 0.19226 | 0.62714 | 0.3479 | 120.9366 | -0.59967 | 121.1517 | 121.1746 | -0.54474 | 121.4493 | -0.032044 | 0.21515 | 120.9503 | 121.2936 | 121.2158 | 121.1609 | 121.1517 | 121.7285 | 121.2616 | 121.4493 | 121.1609 | 121.1517 | 121.2616 | 121.2158 | 121.7285 | -0.82398 | -0.31128
631.9375 | 121.9666 | -121.1197 | 0.59967 | -0.022049 | 0.019465 | 0.0054388 | 0.041524 | -0.009566 | -0.0046399 | 0.017321 | 0.004578 | 0.10071 | -0.17395 | 0.041199 | 0.09613 | 0.11902 | -0.091553 | 0.16937 | 0.59967 | 0.27924 | 120.9457 | -0.49896 | 121.1243 | 121.1609 | -0.50354 | 121.3989 | 0 | 0.17853 | 121.0281 | 121.2891 | 121.2158 | 121.2204 | 121.1243 | 121.7194 | 121.2387 | 121.3989 | 121.2204 | 121.1243 | 121.2387 | 121.2158 | 121.7194 | -0.77362 | -0.32043
633.6719 | 121.8658 | -121.1884 | 0.60425 | 0.10002 | 0.018184 | 0.011634 | 0.042592 | -0.0093524 | -0.0061353 | 0.017321 | 0.041199 | 0.086975 | -0.16937 | 0.068665 | 0.09613 | 0.14648 | -0.14648 | 0.17395 | 0.5722 | 0.2655 | 121.019 | -0.51727 | 121.2296 | 121.257 | -0.50812 | 121.4539 | -0.032043 | 0.21057 | 121.0419 | 121.3623 | 121.2845 | 121.2753 | 121.2296 | 121.7606 | 121.3348 | 121.4539 | 121.2753 | 121.2296 | 121.3348 | 121.2845 | 121.7606 | -0.77362 | -0.33875
635.3438 | 121.907 | -121.2158 | 0.57678 | 0.13817 | 0.019038 | 0.011634 | 0.050924 | -0.0097796 | -0.0076305 | 0.017534 | -0.059509 | 0.10986 | -0.20599 | -0.050354 | -0.004578 | 0.032043 | 0.018311 | 0.036621 | 0.5722 | 0.21973 | 121.0098 | -0.46692 | 121.1563 | 121.1655 | -0.58136 | 121.4355 | -0.004577 | 0.14649 | 121.2341 | 121.2524 | 121.2112 | 121.3257 | 121.1563 | 121.788 | 121.2479 | 121.4355 | 121.3257 | 121.1563 | 121.2479 | 121.2112 | 121.788 | -0.78278 | -0.35706
637.0781 | 121.8979 | -121.1975 | 0.58594 | 0.092392 | 0.019679 | 0.0086432 | 0.046865 | -0.0091388 | -0.0074169 | 0.016893 | -0.068665 | 0.1236 | -0.21515 | -0.045776 | -0.004578 | 0.032043 | 0.027466 | 0.027466 | 0.59509 | 0.21515 | 120.9824 | -0.46234 | 121.1288 | 121.1517 | -0.59052 | 121.4127 | 0.009156 | 0.14648 | 121.225 | 121.225 | 121.1929 | 121.3211 | 121.1288 | 121.7926 | 121.2296 | 121.4127 | 121.3211 | 121.1288 | 121.2296 | 121.1929 | 121.7926 | -0.80109 | -0.37079
638.75 | 121.8338 | -121.2341 | 0.55389 | 0.1992 | 0.017543 | 0.0086432 | 0.046224 | -0.009566 | -0.0069897 | 0.017748 | 0.054932 | 0.082397 | -0.16479 | 0.073242 | 0.11444 | 0.16937 | -0.16937 | 0.1831 | 0.52643 | 0.24261 | 121.0693 | -0.4715 | 121.2891 | 121.3074 | -0.43945 | 121.4767 | -0.027466 | 0.21973 | 121.0648 | 121.4172 | 121.3486 | 121.3165 | 121.2891 | 121.7606 | 121.4035 | 121.4767 | 121.3165 | 121.2891 | 121.4035 | 121.3486 | 121.7606 | -0.71869 | -0.31128
640.4844 | 121.8887 | -121.2982 | 0.53101 | -0.044937 | 0.017756 | 0.0088568 | 0.049428 | -0.0074298 | -0.0080579 | 0.017962 | -0.013733 | 0.10529 | -0.20599 | 0.009155 | 0.036621 | 0.064087 | 0 | 0.10529 | 0.53101 | 0.19226 | 121.0922 | -0.42572 | 121.2845 | 121.3074 | -0.49438 | 121.4905 | 0 | 0.19226 | 121.2982 | 121.4035 | 121.3348 | 121.4035 | 121.2845 | 121.8292 | 121.3623 | 121.4905 | 121.4035 | 121.2845 | 121.3623 | 121.3348 | 121.8292 | -0.737 | -0.33874
642.1562 | 121.9666 | -121.4172 | 0.32959 | -0.16701 | 0.016688 | 0.0080024 | 0.042806 | -0.012343 | -0.0059217 | 0.016893 | 0.032043 | 0.086975 | -0.16022 | 0.073242 | 0.1236 | 0.14648 | -0.091553 | 0.21973 | 0.33875 | 0.032043 | 121.257 | -0.24261 | 121.4493 | 121.4905 | -0.20599 | 121.4493 | 0.009155 | 0.19226 | 121.3257 | 121.637 | 121.5408 | 121.5042 | 121.4493 | 121.756 | 121.5637 | 121.4493 | 121.5042 | 121.4493 | 121.5637 | 121.5408 | 121.756 | -0.48981 | -0.29755
643.8906 | 121.8842 | -121.4905 | 0.35248 | 0.18394 | 0.018825 | 0.0094978 | 0.046865 | -0.0089252 | -0.0078443 | 0.016893 | 0.059509 | 0.09613 | -0.16937 | 0.059509 | 0.11902 | 0.17395 | -0.16022 | 0.1831 | 0.32044 | 0.027466 | 121.3211 | -0.25635 | 121.55 | 121.55 | -0.23346 | 121.5179 | -0.032043 | 0.22888 | 121.3303 | 121.6736 | 121.6095 | 121.5866 | 121.55 | 121.8109 | 121.6644 | 121.5179 | 121.5866 | 121.55 | 121.6644 | 121.6095 | 121.8109 | -0.52185 | -0.32501
645.625 | 122.0169 | -121.4722 | 0.31128 | 0.054245 | 0.016902 | 0.0088568 | 0.04067 | -0.011061 | -0.0050671 | 0.016253 | -0.022888 | 0.091553 | -0.17395 | 0.022888 | 0.064087 | 0.13275 | -0.073242 | 0.14648 | 0.3067 | -0.004578 | 121.2982 | -0.21973 | 121.4493 | 121.4951 | -0.24719 | 121.4676 | -0.004577 | 0.15106 | 121.3989 | 121.6187 | 121.5363 | 121.5637 | 121.4493 | 121.7789 | 121.6049 | 121.4676 | 121.5637 | 121.4493 | 121.6049 | 121.5363 | 121.7789 | -0.48523 | -0.31586
647.3438 | 122.049 | -121.5134 | 0.29297 | -0.28145 | 0.02032 | 0.0024482 | 0.045369 | -0.012984 | -0.0063489 | 0.014116 | -0.064087 | 0.13733 | -0.19684 | -0.041199 | -0.004578 | 0.032043 | 0.07782 | 0.07782 | 0.3479 | -0.054932 | 121.3165 | -0.15564 | 121.4493 | 121.4722 | -0.29755 | 121.4584 | 0.054931 | 0.13275 | 121.5912 | 121.5912 | 121.5088 | 121.6507 | 121.4493 | 121.8613 | 121.5454 | 121.4584 | 121.6507 | 121.4493 | 121.5454 | 121.5088 | 121.8613 | -0.48981 | -0.3479
649.0312 | 121.9482 | -121.5454 | 0.3067 | 0.13817 | 0.019465 | 0.010779 | 0.047078 | -0.0089252 | -0.0050671 | 0.016253 | -0.059509 | 0.11444 | -0.20599 | -0.027466 | 0.013733 | 0.050354 | -0.022888 | 0.064087 | 0.31586 | -0.032043 | 121.3394 | -0.19226 | 121.4859 | 121.5179 | -0.29297 | 121.5134 | 0.009155 | 0.14649 | 121.5225 | 121.6095 | 121.5591 | 121.6599 | 121.4859 | 121.8613 | 121.5958 | 121.5134 | 121.6599 | 121.4859 | 121.5958 | 121.5591 | 121.8613 | -0.5127 | -0.33874
650.7656 | 122.0444 | -121.5134 | 0.27924 | -0.17464 | 0.02032 | 0.010139 | 0.044301 | -0.0087116 | -0.0080579 | 0.018389 | -0.054932 | 0.13733 | -0.20142 | -0.036621 | 0.009155 | 0.050354 | 0.059509 | 0.086975 | 0.32044 | -0.032043 | 121.312 | -0.14191 | 121.4584 | 121.4767 | -0.27008 | 121.4813 | 0.041199 | 0.14648 | 121.5729 | 121.6003 | 121.5225 | 121.6507 | 121.4584 | 121.8338 | 121.5637 | 121.4813 | 121.6507 | 121.4584 | 121.5637 | 121.5225 | 121.8338 | -0.48065 | -0.31128
652.4375 | 122.0169 | -121.5591 | 0.27924 | -0.17464 | 0.017543 | 0.010566 | 0.042806 | -0.007857 | -0.0050671 | 0.01668 | 0.036621 | 0.09613 | -0.17853 | 0.091553 | 0.12817 | 0.17853 | -0.10986 | 0.24261 | 0.28381 | 0 | 121.3806 | -0.18311 | 121.5958 | 121.6507 | -0.15106 | 121.5591 | 0.004577 | 0.21515 | 121.4493 | 121.8018 | 121.6873 | 121.6553 | 121.5958 | 121.843 | 121.7377 | 121.5591 | 121.6553 | 121.5958 | 121.7377 | 121.6873 | 121.843 | -0.45776 | -0.27924
654.1719 | 122.049 | -121.5683 | 0.2655 | 0.054245 | 0.019252 | 0.008216 | 0.042806 | -0.010634 | -0.0067761 | 0.019243 | -0.018311 | 0.086975 | -0.16479 | 0.009155 | 0.064087 | 0.1236 | -0.082397 | 0.14191 | 0.27924 | -0.045776 | 121.4035 | -0.17853 | 121.55 | 121.5775 | -0.20142 | 121.5225 | 0.013733 | 0.14648 | 121.4859 | 121.7102 | 121.6324 | 121.6553 | 121.55 | 121.8475 | 121.6919 | 121.5225 | 121.6553 | 121.55 | 121.6919 | 121.6324 | 121.8475 | -0.4303 | -0.31128
655.9062 | 122.0306 | -121.6507 | 0.20142 | -0.18227 | 0.01797 | 0.0052252 | 0.044728 | -0.012984 | -0.0054943 | 0.017321 | 0.050354 | 0.09613 | -0.16479 | 0.086975 | 0.1236 | 0.17395 | -0.10986 | 0.2243 | 0.20142 | -0.07782 | 121.4859 | -0.10529 | 121.701 | 121.7377 | -0.07782 | 121.5729 | 0 | 0.21515 | 121.5408 | 121.875 | 121.7743 | 121.7468 | 121.701 | 121.8521 | 121.8246 | 121.5729 | 121.7468 | 121.701 | 121.8246 | 121.7743 | 121.8521 | -0.36621 | -0.27924
657.5781 | 122.0215 | -121.6415 | 0.20599 | -0.19753 | 0.019252 | 0.008216 | 0.049642 | -0.0093524 | -0.0048535 | 0.016039 | -0.022888 | 0.13275 | -0.19684 | 0.013733 | 0.022888 | 0.064087 | 0.027466 | 0.11444 | 0.23346 | -0.11902 | 121.4447 | -0.073243 | 121.6187 | 121.6553 | -0.18311 | 121.5225 | 0.027465 | 0.17395 | 121.669 | 121.756 | 121.6644 | 121.7743 | 121.6187 | 121.875 | 121.7056 | 121.5225 | 121.7743 | 121.6187 | 121.7056 | 121.6644 | 121.875 | -0.40283 | -0.32501
659.3125 | 121.9528 | -121.7285 | 0.17395 | 0.1458 | 0.018397 | 0.0090704 | 0.045797 | -0.008498 | -0.0065625 | 0.01668 | 0.036621 | 0.091553 | -0.15564 | 0.082397 | 0.10986 | 0.15564 | -0.14648 | 0.1831 | 0.15564 | -0.11444 | 121.5729 | -0.082397 | 121.7651 | 121.8109 | -0.064087 | 121.6141 | -0.01831 | 0.19226 | 121.582 | 121.9116 | 121.8384 | 121.8201 | 121.7651 | 121.8842 | 121.8842 | 121.6141 | 121.8201 | 121.7651 | 121.8842 | 121.8384 | 121.8842 | -0.32959 | -0.28839
661.0469 | 122.0993 | -121.637 | 0.16479 | -0.0067901 | 0.018825 | 0.0090704 | 0.044942 | -0.010207 | -0.0065625 | 0.018816 | -0.022888 | 0.11444 | -0.15564 | 0.022888 | 0.068665 | 0.11444 | -0.086975 | 0.15106 | 0.17853 | -0.13733 | 121.4813 | -0.050354 | 121.6141 | 121.6599 | -0.09613 | 121.4996 | 0.013733 | 0.13275 | 121.55 | 121.788 | 121.7056 | 121.7514 | 121.6141 | 121.8155 | 121.7514 | 121.4996 | 121.7514 | 121.6141 | 121.7514 | 121.7056 | 121.8155 | -0.32044 | -0.30212
662.7969 | 121.9574 | -121.7239 | 0.18768 | 0.18394 | 0.018397 | 0.0069342 | 0.046651 | -0.0099934 | -0.0046399 | 0.016039 | 0.07782 | 0.082397 | -0.16022 | 0.068665 | 0.11444 | 0.16479 | -0.17395 | 0.19226 | 0.14648 | -0.1236 | 121.5637 | -0.10529 | 121.8018 | 121.7926 | -0.073242 | 121.6003 | -0.041199 | 0.23804 | 121.55 | 121.9162 | 121.8384 | 121.8063 | 121.8018 | 121.8704 | 121.8887 | 121.6003 | 121.8063 | 121.8018 | 121.8887 | 121.8384 | 121.8704 | -0.3479 | -0.31128
664.4688 | 122.0718 | -121.7148 | 0.16937 | -0.20515 | 0.016261 | 0.010779 | 0.049001 | -0.0099934 | -0.0086987 | 0.018816 | -0.032043 | 0.10529 | -0.19684 | 0.009155 | 0.032043 | 0.041199 | 0.027466 | 0.10529 | 0.19684 | -0.16022 | 121.5179 | -0.064087 | 121.6827 | 121.7239 | -0.13733 | 121.5546 | 0.027465 | 0.1648 | 121.7422 | 121.8201 | 121.7468 | 121.8201 | 121.6827 | 121.9116 | 121.756 | 121.5546 | 121.8201 | 121.6827 | 121.756 | 121.7468 | 121.9116 | -0.36621 | -0.32959
666.2031 | 122.0718 | -121.7148 | 0.16022 | -0.12886 | 0.017756 | 0.0033026 | 0.042165 | -0.01213 | -0.0076305 | 0.019243 | 0.045776 | 0.086975 | -0.16022 | 0.073242 | 0.12817 | 0.16479 | -0.1236 | 0.2243 | 0.16937 | -0.14648 | 121.5546 | -0.073242 | 121.7606 | 121.788 | -0.032043 | 121.5683 | 0.009156 | 0.20599 | 121.5912 | 121.9391 | 121.843 | 121.8018 | 121.7606 | 121.8842 | 121.8796 | 121.5683 | 121.8018 | 121.7606 | 121.8796 | 121.843 | 121.8842 | -0.32043 | -0.3067
667.9531 | 122.0901 | -121.7285 | 0.1831 | -0.18227 | 0.016047 | 0.0062934 | 0.045583 | -0.012984 | -0.0069897 | 0.018175 | 0.022888 | 0.082397 | -0.16937 | 0.054932 | 0.091553 | 0.14191 | -0.018311 | 0.17395 | 0.15564 | -0.15106 | 121.5591 | -0.10071 | 121.7514 | 121.7834 | -0.091552 | 121.5775 | -0.027465 | 0.19226 | 121.7102 | 121.9025 | 121.8201 | 121.8109 | 121.7514 | 121.8842 | 121.8704 | 121.5775 | 121.8109 | 121.7514 | 121.8704 | 121.8201 | 121.8842 | -0.35248 | -0.33417
669.625 | 122.1268 | -121.7194 | 0.14648 | -0.26619 | 0.017543 | 0.0058662 | 0.047078 | -0.011489 | -0.0067761 | 0.01668 | -0.059509 | 0.14191 | -0.21515 | -0.022888 | 0.004578 | 0.022888 | 0.09613 | 0.07782 | 0.19226 | -0.16937 | 121.5042 | -0.004577 | 121.6599 | 121.6965 | -0.14191 | 121.55 | 0.045777 | 0.15564 | 121.8155 | 121.7972 | 121.7239 | 121.8613 | 121.6599 | 121.9116 | 121.7422 | 121.55 | 121.8613 | 121.6599 | 121.7422 | 121.7239 | 121.9116 | -0.36163 | -0.31586
671.3594 | 122.0627 | -121.756 | 0.1831 | 0.13817 | 0.018184 | 0.013129 | 0.046437 | -0.0082844 | -0.0059217 | 0.018602 | -0.045776 | 0.1236 | -0.20599 | -0.050354 | -0.013733 | 0.036621 | 0.013733 | 0.045776 | 0.21515 | -0.16479 | 121.55 | -0.059509 | 121.7102 | 121.7056 | -0.19684 | 121.5912 | 0.032044 | 0.16022 | 121.7697 | 121.8018 | 121.7422 | 121.8796 | 121.7102 | 121.9711 | 121.7926 | 121.5912 | 121.8796 | 121.7102 | 121.7926 | 121.7422 | 121.9711 | -0.3891 | -0.3479
673.0938 | 121.9986 | -121.756 | 0.19226 | -0.037308 | 0.018397 | 0.0058662 | 0.047719 | -0.007857 | -0.0091259 | 0.019457 | 0 | 0.11902 | -0.19226 | 0.004578 | 0.027466 | 0.064087 | 0.009155 | 0.091553 | 0.20142 | -0.15564 | 121.5637 | -0.073242 | 121.756 | 121.7606 | -0.16479 | 121.6003 | 0.009155 | 0.19226 | 121.7651 | 121.8475 | 121.7834 | 121.875 | 121.756 | 121.9574 | 121.8201 | 121.6003 | 121.875 | 121.756 | 121.8201 | 121.7834 | 121.9574 | -0.38452 | -0.3479
674.8281 | 121.9986 | -121.7926 | 0.18768 | 0.19157 | 0.019679 | 0.0090704 | 0.04131 | -0.009566 | -0.0076305 | 0.017107 | 0.045776 | 0.091553 | -0.15564 | 0.059509 | 0.10529 | 0.1831 | -0.17395 | 0.18768 | 0.15106 | -0.10986 | 121.637 | -0.09613 | 121.8384 | 121.8521 | -0.082397 | 121.6827 | -0.036621 | 0.20142 | 121.6187 | 121.9803 | 121.8979 | 121.8842 | 121.8384 | 121.9437 | 121.9757 | 121.6827 | 121.8842 | 121.8384 | 121.9757 | 121.8979 | 121.9437 | -0.34332 | -0.29755
676.5625 | 122.1405 | -121.7239 | 0.17395 | -0.2433 | 0.019252 | 0.010352 | 0.042165 | -0.011275 | -0.0078443 | 0.017321 | -0.064087 | 0.14191 | -0.21515 | -0.050354 | -0.009155 | 0.027466 | 0.091553 | 0.064087 | 0.21973 | -0.14648 | 121.5088 | -0.032043 | 121.6599 | 121.6736 | -0.1831 | 121.5775 | 0.045777 | 0.15106 | 121.8155 | 121.788 | 121.7148 | 121.8658 | 121.6599 | 121.9437 | 121.7514 | 121.5775 | 121.8658 | 121.6599 | 121.7514 | 121.7148 | 121.9437 | -0.3891 | -0.32043
678.2344 | 122.0398 | -121.669 | 0.29755 | 0.10765 | 0.018397 | 0.0056524 | 0.044088 | -0.011489 | -0.0046399 | 0.020525 | 0.018311 | 0.086975 | -0.16937 | 0.068665 | 0.091553 | 0.15564 | -0.13275 | 0.17395 | 0.27924 | 0.004578 | 121.4996 | -0.21057 | 121.6873 | 121.7377 | -0.20599 | 121.6736 | -0.01831 | 0.18768 | 121.5363 | 121.843 | 121.7606 | 121.756 | 121.6873 | 121.9482 | 121.8246 | 121.6736 | 121.756 | 121.6873 | 121.8246 | 121.7606 | 121.9482 | -0.46692 | -0.29297
679.9688 | 122.1359 | -121.6415 | 0.28381 | -0.16701 | 0.02032 | 0.009284 | 0.047078 | -0.011702 | -0.0076305 | 0.018175 | -0.064087 | 0.13733 | -0.20599 | 0.004578 | 0.022888 | 0.041199 | 0.059509 | 0.10071 | 0.33417 | -0.013733 | 121.4355 | -0.14648 | 121.5775 | 121.6461 | -0.26092 | 121.6278 | 0.050354 | 0.14191 | 121.7011 | 121.7422 | 121.6644 | 121.7789 | 121.5775 | 121.9757 | 121.6827 | 121.6278 | 121.7789 | 121.5775 | 121.6827 | 121.6644 | 121.9757 | -0.48981 | -0.29755
681.7031 | 122.1313 | -121.6232 | 0.29297 | -0.037308 | 0.019893 | 0.0097114 | 0.041738 | -0.011489 | -0.0061353 | 0.017321 | 0.009155 | 0.10986 | -0.18768 | 0.045776 | 0.09613 | 0.16479 | -0.07782 | 0.20599 | 0.3067 | -0.009155 | 121.4355 | -0.18311 | 121.6324 | 121.669 | -0.19684 | 121.6141 | 0.013733 | 0.19684 | 121.5454 | 121.8292 | 121.7194 | 121.7331 | 121.6324 | 121.9299 | 121.788 | 121.6141 | 121.7331 | 121.6324 | 121.788 | 121.7194 | 121.9299 | -0.48065 | -0.30212
683.3906 | 122.0993 | -121.6553 | 0.31586 | 0.13054 | 0.018825 | 0.0090704 | 0.048146 | -0.009566 | -0.0076305 | 0.016466 | -0.045776 | 0.11902 | -0.18768 | -0.054932 | -0.022888 | 0.036621 | 0.022888 | 0.036621 | 0.31586 | -0.032043 | 121.4676 | -0.19684 | 121.6095 | 121.6003 | -0.33875 | 121.6232 | 0 | 0.14191 | 121.6782 | 121.6919 | 121.6324 | 121.7743 | 121.6095 | 121.9711 | 121.6919 | 121.6232 | 121.7743 | 121.6095 | 121.6919 | 121.6324 | 121.9711 | -0.50354 | -0.3479
685.2344 | 122.1039 | -121.6644 | 0.30212 | -0.14412 | 0.019679 | 0.0090704 | 0.047292 | -0.0097796 | -0.0080579 | 0.015398 | -0.013733 | 0.11902 | -0.19684 | 0.004578 | 0.041199 | 0.07782 | 0.022888 | 0.11444 | 0.32501 | -0.032043 | 121.4676 | -0.18311 | 121.6507 | 121.669 | -0.26093 | 121.6324 | 0.022888 | 0.18311 | 121.6873 | 121.7789 | 121.7056 | 121.7834 | 121.6507 | 121.9894 | 121.7422 | 121.6324 | 121.7834 | 121.6507 | 121.7422 | 121.7056 | 121.9894 | -0.49896 | -0.33417
687.0156 | 122.1039 | -121.701 | 0.29755 | 0.13817 | 0.018825 | 0.0090704 | 0.043447 | -0.010207 | -0.0046399 | 0.017107 | 0.032043 | 0.09613 | -0.17853 | 0.032043 | 0.086975 | 0.13733 | -0.11444 | 0.15106 | 0.2655 | -0.027466 | 121.5225 | -0.20142 | 121.7331 | 121.7331 | -0.21057 | 121.6736 | -0.032043 | 0.21057 | 121.5866 | 121.8521 | 121.788 | 121.7972 | 121.7331 | 121.9666 | 121.8384 | 121.6736 | 121.7972 | 121.7331 | 121.8384 | 121.788 | 121.9666 | -0.47607 | -0.32501
688.9219 | 122.1039 | -121.6736 | 0.32044 | 0.13054 | 0.020106 | 0.0088568 | 0.047933 | -0.0080706 | -0.0054943 | 0.017534 | -0.036621 | 0.13275 | -0.19684 | -0.032043 | 0.004578 | 0.054932 | -0.022888 | 0.045776 | 0.31586 | -0.027466 | 121.4767 | -0.18768 | 121.637 | 121.6415 | -0.31586 | 121.6461 | -0.004578 | 0.16022 | 121.6507 | 121.7194 | 121.6782 | 121.8063 | 121.637 | 121.9894 | 121.7285 | 121.6461 | 121.8063 | 121.637 | 121.7285 | 121.6782 | 121.9894 | -0.51727 | -0.3479
692.25 | 122.1954 | -121.6599 | 0.31128 | -0.2433 | 0.017116 | 0.010779 | 0.046224 | -0.011275 | -0.0065625 | 0.016253 | -0.009155 | 0.10529 | -0.19684 | -0.018311 | 0.036621 | 0.059509 | 0.059509 | 0.11444 | 0.35248 | -0.032043 | 121.463 | -0.20599 | 121.6507 | 121.6415 | -0.27466 | 121.6278 | 0.041199 | 0.18768 | 121.7194 | 121.7743 | 121.6965 | 121.7651 | 121.6507 | 122.0123 | 121.7194 | 121.6278 | 121.7651 | 121.6507 | 121.7194 | 121.6965 | 122.0123 | -0.50812 | -0.34332
695.4375 | 122.2183 | -121.6415 | 0.28839 | 0.031357 | 0.016475 | 0.0080024 | 0.041097 | -0.012557 | -0.0078443 | 0.017321 | -0.032043 | 0.068665 | -0.17853 | 0.004578 | 0.059509 | 0.09613 | -0.059509 | 0.13275 | 0.32959 | -0.009155 | 121.463 | -0.21973 | 121.6095 | 121.6461 | -0.22888 | 121.6324 | 0.041199 | 0.14648 | 121.582 | 121.7743 | 121.7011 | 121.7102 | 121.6095 | 121.9711 | 121.7377 | 121.6324 | 121.7102 | 121.6095 | 121.7377 | 121.7011 | 121.9711 | -0.46692 | -0.29755
697.5 | 122.0947 | -121.843 | 0.13275 | 0.10765 | 0.01797 | 0.010566 | 0.04366 | -0.0099934 | -0.0050671 | 0.015825 | 0.027466 | 0.091553 | -0.15564 | 0.041199 | 0.086975 | 0.14648 | -0.13275 | 0.17395 | 0.1236 | -0.16022 | 121.6873 | -0.041198 | 121.8704 | 121.8842 | -0.045776 | 121.6827 | -0.009155 | 0.18311 | 121.7102 | 122.0169 | 121.9299 | 121.9345 | 121.8704 | 121.9666 | 121.9894 | 121.6827 | 121.9345 | 121.8704 | 121.9894 | 121.9299 | 121.9666 | -0.28839 | -0.29297
699.25 | 122.1085 | -121.8704 | 0.15564 | 0.1992 | 0.019679 | 0.0080024 | 0.046865 | -0.010207 | -0.0076305 | 0.016893 | -0.041199 | 0.086975 | -0.21057 | 0 | 0.004578 | 0.091553 | -0.07782 | 0.09613 | 0.16937 | -0.16479 | 121.6599 | -0.068665 | 121.8292 | 121.8704 | -0.15106 | 121.7056 | 0.013733 | 0.16937 | 121.7926 | 121.9666 | 121.875 | 121.9574 | 121.8292 | 122.0398 | 121.962 | 121.7056 | 121.9574 | 121.8292 | 121.962 | 121.875 | 122.0398 | -0.36621 | -0.32044
701.125 | 122.1176 | -121.8933 | 0.15106 | -0.022049 | 0.020747 | 0.004798 | 0.047078 | -0.0087116 | -0.0097669 | 0.018175 | 0.013733 | 0.12817 | -0.19226 | -0.009155 | 0.013733 | 0.036621 | -0.013733 | 0.07782 | 0.1831 | -0.18768 | 121.701 | -0.022888 | 121.907 | 121.8842 | -0.13733 | 121.7056 | 0.032043 | 0.20599 | 121.8796 | 121.9711 | 121.907 | 122.0215 | 121.907 | 122.0764 | 121.9299 | 121.7056 | 122.0215 | 121.907 | 121.9299 | 121.907 | 122.0764 | -0.34332 | -0.33874
706.3438 | 122.2275 | -121.8521 | 0.13275 | 0.0084684 | 0.019465 | 0.0071478 | 0.038106 | -0.011061 | -0.0078443 | 0.015612 | 0.004578 | 0.10071 | -0.16479 | 0.013733 | 0.073242 | 0.12817 | -0.082397 | 0.16937 | 0.14191 | -0.17395 | 121.6873 | -0.032043 | 121.8567 | 121.8658 | -0.059509 | 121.6782 | 0.009156 | 0.16937 | 121.7697 | 122.0215 | 121.9254 | 121.9528 | 121.8567 | 121.994 | 121.9803 | 121.6782 | 121.9528 | 121.8567 | 121.9803 | 121.9254 | 121.994 | -0.29755 | -0.3067
708.1562 | 122.2321 | -121.8658 | 0.14191 | -0.18227 | 0.018184 | 0.011848 | 0.047292 | -0.011275 | -0.0078443 | 0.017107 | -0.054932 | 0.11902 | -0.23346 | -0.022888 | 0.018311 | 0.045776 | 0.068665 | 0.086975 | 0.17395 | -0.20599 | 121.6324 | -0.022888 | 121.8109 | 121.843 | -0.1236 | 121.6599 | 0.032043 | 0.17853 | 121.9345 | 121.9528 | 121.8842 | 121.9849 | 121.8109 | 122.0398 | 121.9116 | 121.6599 | 121.9849 | 121.8109 | 121.9116 | 121.8842 | 122.0398 | -0.37537 | -0.3479
709.8438 | 122.2504 | -121.8842 | 0.13733 | -0.2433 | 0.019252 | 0.0060798 | 0.045369 | -0.011061 | -0.0086987 | 0.018175 | -0.073242 | 0.11902 | -0.2243 | -0.050354 | 0.004578 | 0.018311 | 0.086975 | 0.068665 | 0.18768 | -0.17853 | 121.6599 | -0.01831 | 121.8109 | 121.8338 | -0.13275 | 121.7056 | 0.050354 | 0.15106 | 121.9711 | 121.9528 | 121.8887 | 122.0032 | 121.8109 | 122.0718 | 121.9025 | 121.7056 | 122.0032 | 121.8109 | 121.9025 | 121.8887 | 122.0718 | -0.36163 | -0.31586
711.5781 | 122.1771 | -121.8979 | 0.14648 | 0.13054 | 0.017329 | 0.0088568 | 0.046651 | -0.011061 | -0.0061353 | 0.017962 | -0.068665 | 0.10986 | -0.21515 | -0.064087 | -0.018311 | 0.013733 | 0.027466 | 0.036621 | 0.17395 | -0.21057 | 121.6827 | -0.036621 | 121.8292 | 121.8338 | -0.16479 | 121.6873 | 0.027466 | 0.14648 | 121.9254 | 121.9345 | 121.8796 | 122.0078 | 121.8292 | 122.0718 | 121.9116 | 121.6873 | 122.0078 | 121.8292 | 121.9116 | 121.8796 | 122.0718 | -0.36163 | -0.35706
713.25 | 122.1542 | -121.9254 | 0.15106 | 0.13054 | 0.01797 | 0.010566 | 0.047292 | -0.006789 | -0.0063489 | 0.016466 | -0.050354 | 0.11902 | -0.20142 | -0.050354 | 0 | 0.050354 | -0.036621 | 0.068665 | 0.16022 | -0.17395 | 121.7239 | -0.032043 | 121.875 | 121.875 | -0.15106 | 121.7514 | 0.009155 | 0.15106 | 121.8887 | 121.994 | 121.9254 | 122.0444 | 121.875 | 122.0856 | 121.9757 | 121.7514 | 122.0444 | 121.875 | 121.9757 | 121.9254 | 122.0856 | -0.35248 | -0.32501
715 | 122.2275 | -121.8979 | 0.14648 | 0.069504 | 0.018397 | 0.01142 | 0.040456 | -0.011916 | -0.0057079 | 0.017107 | 0.004578 | 0.086975 | -0.17395 | 0.004578 | 0.073242 | 0.12817 | -0.082397 | 0.13733 | 0.13733 | -0.1831 | 121.7239 | -0.059509 | 121.9025 | 121.9025 | -0.073242 | 121.7148 | -0.009155 | 0.17853 | 121.8155 | 122.0352 | 121.9711 | 121.9849 | 121.9025 | 122.0352 | 122.0261 | 121.7148 | 121.9849 | 121.9025 | 122.0261 | 121.9711 | 122.0352 | -0.32043 | -0.32959
716.7344 | 122.1909 | -121.9162 | 0.15564 | -0.14412 | 0.018397 | 0.0052252 | 0.049428 | -0.009566 | -0.0072033 | 0.016039 | -0.009155 | 0.13275 | -0.19226 | 0.013733 | 0.045776 | 0.068665 | 0.013733 | 0.13733 | 0.16022 | -0.19226 | 121.7239 | -0.022889 | 121.907 | 121.9299 | -0.10986 | 121.7239 | 0.004577 | 0.18311 | 121.9299 | 122.0535 | 121.962 | 122.049 | 121.907 | 122.0764 | 121.9849 | 121.7239 | 122.049 | 121.907 | 121.9849 | 121.962 | 122.0764 | -0.3479 | -0.3479
718.4062 | 122.2549 | -121.9025 | 0.13733 | -0.21278 | 0.018825 | 0.0088568 | 0.04131 | -0.011275 | -0.0076305 | 0.016893 | 0 | 0.086975 | -0.1831 | 0.050354 | 0.09613 | 0.12817 | -0.022888 | 0.18768 | 0.15106 | -0.17395 | 121.7194 | -0.050354 | 121.9025 | 121.9528 | -0.041199 | 121.7285 | 0.013733 | 0.1831 | 121.8796 | 122.0901 | 121.9986 | 121.9894 | 121.9025 | 122.0535 | 122.0306 | 121.7285 | 121.9894 | 121.9025 | 122.0306 | 121.9986 | 122.0535 | -0.32043 | -0.31128
720.1406 | 122.1542 | -121.9208 | 0.16937 | 0.17632 | 0.015834 | 0.0056524 | 0.044515 | -0.0091388 | -0.0059217 | 0.019884 | 0.041199 | 0.086975 | -0.17395 | 0.068665 | 0.09613 | 0.16022 | -0.16022 | 0.1831 | 0.13275 | -0.15106 | 121.7468 | -0.082398 | 121.962 | 121.9894 | -0.073243 | 121.7697 | -0.036622 | 0.21515 | 121.7606 | 122.1039 | 122.0169 | 122.0078 | 121.962 | 122.0535 | 122.081 | 121.7697 | 122.0078 | 121.962 | 122.081 | 122.0169 | 122.0535 | -0.34332 | -0.32044
721.875 | 122.3007 | -121.9116 | 0.1236 | -0.21278 | 0.018825 | 0.010993 | 0.044942 | -0.012557 | -0.0054943 | 0.018175 | -0.068665 | 0.10986 | -0.2243 | -0.041199 | 0.013733 | 0.018311 | 0.10986 | 0.073242 | 0.18768 | -0.20599 | 121.6873 | -0.013733 | 121.843 | 121.8704 | -0.10986 | 121.7056 | 0.064087 | 0.15564 | 122.0215 | 121.9849 | 121.9254 | 122.0215 | 121.843 | 122.0993 | 121.9299 | 121.7056 | 122.0215 | 121.843 | 121.9299 | 121.9254 | 122.0993 | -0.3479 | -0.32959
723.5469 | 122.287 | -121.907 | 0.1236 | 0.016098 | 0.01797 | 0.0052252 | 0.041738 | -0.014052 | -0.0046399 | 0.016893 | -0.018311 | 0.09613 | -0.16022 | 0.009155 | 0.059509 | 0.10986 | -0.068665 | 0.14191 | 0.14648 | -0.16937 | 121.7468 | -0.027466 | 121.8887 | 121.9162 | -0.064087 | 121.7377 | 0.022888 | 0.14191 | 121.8384 | 122.049 | 121.9666 | 122.0032 | 121.8887 | 122.0535 | 122.0169 | 121.7377 | 122.0032 | 121.8887 | 122.0169 | 121.9666 | 122.0535 | -0.28381 | -0.29297
725.2969 | 122.2778 | -121.9254 | 0.13733 | -0.20515 | 0.016902 | 0.0097114 | 0.045583 | -0.011489 | -0.0078443 | 0.016039 | 0.032043 | 0.10986 | -0.16937 | 0.054932 | 0.073242 | 0.11444 | -0.032043 | 0.18768 | 0.16479 | -0.16937 | 121.756 | -0.027466 | 121.9574 | 121.9803 | -0.064087 | 121.756 | 0.027466 | 0.20142 | 121.8933 | 122.113 | 121.9986 | 122.0352 | 121.9574 | 122.0901 | 122.0398 | 121.756 | 122.0352 | 121.9574 | 122.0398 | 121.9986 | 122.0901 | -0.3067 | -0.3067
726.9531 | 122.1863 | -121.9528 | 0.15564 | 0.13817 | 0.01797 | 0.013984 | 0.041951 | -0.011275 | -0.0057079 | 0.018389 | 0.041199 | 0.07782 | -0.16479 | 0.045776 | 0.073242 | 0.14648 | -0.14191 | 0.17395 | 0.12817 | -0.16937 | 121.788 | -0.07782 | 121.994 | 121.9986 | -0.082398 | 121.7834 | -0.027466 | 0.20599 | 121.8109 | 122.1268 | 122.0261 | 122.0306 | 121.994 | 122.081 | 122.0993 | 121.7834 | 122.0306 | 121.994 | 122.0993 | 122.0261 | 122.081 | -0.32044 | -0.32501
728.6875 | 122.1954 | -121.962 | 0.15106 | 0.11528 | 0.020747 | 0.0071478 | 0.044942 | -0.010848 | -0.0063489 | 0.016893 | 0.045776 | 0.073242 | -0.14648 | 0.045776 | 0.091553 | 0.13733 | -0.12817 | 0.1831 | 0.13275 | -0.16022 | 121.8155 | -0.07782 | 122.0078 | 122.0078 | -0.059509 | 121.8018 | -0.018311 | 0.19226 | 121.8338 | 122.1451 | 122.0535 | 122.0352 | 122.0078 | 122.0947 | 122.0993 | 121.8018 | 122.0352 | 122.0078 | 122.0993 | 122.0535 | 122.0947 | -0.29755 | -0.31128
730.4375 | 122.1954 | -121.9711 | 0.15564 | -0.0067901 | 0.018825 | 0.0052252 | 0.050283 | -0.010421 | -0.0080579 | 0.018389 | -0.018311 | 0.10529 | -0.21057 | -0.004578 | 0.013733 | 0.041199 | 0 | 0.068665 | 0.17853 | -0.1831 | 121.7606 | -0.050354 | 121.9528 | 121.9666 | -0.14191 | 121.788 | 0.022888 | 0.19226 | 121.9711 | 122.0398 | 121.9849 | 122.0764 | 121.9528 | 122.1497 | 122.0123 | 121.788 | 122.0764 | 121.9528 | 122.0123 | 121.9849 | 122.1497 | -0.36621 | -0.33874
732.1719 | 122.1725 | -121.962 | 0.15564 | 0.20683 | 0.018397 | 0.015693 | 0.044515 | -0.009566 | -0.0059217 | 0.018602 | 0.045776 | 0.086975 | -0.16022 | 0.068665 | 0.10529 | 0.17853 | -0.17395 | 0.19684 | 0.14191 | -0.16479 | 121.8018 | -0.068665 | 122.0078 | 122.0306 | -0.050354 | 121.7972 | -0.013733 | 0.20599 | 121.788 | 122.1588 | 122.0673 | 122.0489 | 122.0078 | 122.1039 | 122.1405 | 121.7972 | 122.0489 | 122.0078 | 122.1405 | 122.0673 | 122.1039 | -0.31586 | -0.32044
733.8281 | 122.2275 | -121.9666 | 0.14191 | 0.12291 | 0.017543 | 0.0086432 | 0.048146 | -0.011061 | -0.0076305 | 0.017962 | -0.059509 | 0.11444 | -0.21515 | -0.050354 | -0.013733 | 0.027466 | 0.004578 | 0.045776 | 0.17853 | -0.20142 | 121.7514 | -0.027466 | 121.907 | 121.9162 | -0.15564 | 121.7651 | 0.036621 | 0.15564 | 121.9711 | 122.0123 | 121.9528 | 122.081 | 121.907 | 122.1451 | 121.994 | 121.7651 | 122.081 | 121.907 | 121.994 | 121.9528 | 122.1451 | -0.35706 | -0.34332
735.5625 | 122.1954 | -121.9849 | 0.15564 | 0.21446 | 0.017756 | 0.008216 | 0.046224 | -0.0089252 | -0.0074169 | 0.016893 | -0.036621 | 0.10071 | -0.20142 | -0.018311 | 0.027466 | 0.086975 | -0.073242 | 0.09613 | 0.14191 | -0.19226 | 121.7834 | -0.054932 | 121.9482 | 121.9666 | -0.12817 | 121.7926 | -0.013733 | 0.1648 | 121.9116 | 122.081 | 122.0123 | 122.0856 | 121.9482 | 122.1268 | 122.0718 | 121.7926 | 122.0856 | 121.9482 | 122.0718 | 122.0123 | 122.1268 | -0.35706 | -0.3479
737.2344 | 122.1954 | -121.9894 | 0.15564 | -0.098343 | 0.017329 | 0.0080024 | 0.047719 | -0.010634 | -0.0078443 | 0.017534 | 0.009155 | 0.1236 | -0.20142 | 0.013733 | 0.059509 | 0.082397 | -0.027466 | 0.12817 | 0.16937 | -0.1831 | 121.788 | -0.032044 | 121.9986 | 122.0032 | -0.096131 | 121.8063 | 0.013733 | 0.21057 | 121.962 | 122.1176 | 122.049 | 122.113 | 121.9986 | 122.1588 | 122.0718 | 121.8063 | 122.113 | 121.9986 | 122.0718 | 122.049 | 122.1588 | -0.35706 | -0.33874
738.9688 | 122.3145 | -121.9482 | 0.13733 | -0.037308 | 0.01562 | 0.0086432 | 0.042592 | -0.011061 | -0.0042127 | 0.017107 | -0.009155 | 0.09613 | -0.15564 | 0.036621 | 0.09613 | 0.14648 | -0.09613 | 0.18768 | 0.15106 | -0.16937 | 121.7926 | -0.041199 | 121.9391 | 121.9849 | -0.041199 | 121.7789 | 0.013733 | 0.14649 | 121.8521 | 122.1359 | 122.0444 | 122.0444 | 121.9391 | 122.0993 | 122.0947 | 121.7789 | 122.0444 | 121.9391 | 122.0947 | 122.0444 | 122.0993 | -0.29297 | -0.3067
740.6406 | 122.3373 | -121.9757 | 0.1236 | -0.22804 | 0.018611 | 0.0045844 | 0.047719 | -0.011916 | -0.0054943 | 0.016466 | -0.07782 | 0.12817 | -0.19226 | -0.045776 | 0 | 0.032043 | 0.10071 | 0.082397 | 0.1831 | -0.21057 | 121.7834 | 0.004578 | 121.8979 | 121.9299 | -0.1236 | 121.7651 | 0.059509 | 0.11444 | 122.0764 | 122.0581 | 121.9757 | 122.1039 | 121.8979 | 122.1588 | 122.0078 | 121.7651 | 122.1039 | 121.8979 | 122.0078 | 121.9757 | 122.1588 | -0.31586 | -0.33417
742.375 | 122.2046 | -121.9849 | 0.16479 | 0.1458 | 0.019252 | 0.0058662 | 0.046651 | -0.0089252 | -0.0067761 | 0.017748 | 0.045776 | 0.10071 | -0.16479 | 0.059509 | 0.10529 | 0.16937 | -0.14191 | 0.18768 | 0.12817 | -0.15564 | 121.8201 | -0.064087 | 122.0306 | 122.0444 | -0.059509 | 121.8292 | -0.036621 | 0.21057 | 121.843 | 122.1725 | 122.0901 | 122.0856 | 122.0306 | 122.113 | 122.1542 | 121.8292 | 122.0856 | 122.0306 | 122.1542 | 122.0901 | 122.113 | -0.32959 | -0.32044
744.1094 | 122.3373 | -121.962 | 0.1236 | -0.21278 | 0.016047 | 0.0069342 | 0.046865 | -0.011489 | -0.0091259 | 0.017534 | -0.068665 | 0.14648 | -0.21973 | -0.050354 | -0.004578 | 0.022888 | 0.068665 | 0.07782 | 0.1831 | -0.20142 | 121.7422 | 0.022888 | 121.8933 | 121.9116 | -0.12817 | 121.7606 | 0.059509 | 0.15106 | 122.0306 | 122.0398 | 121.9574 | 122.1085 | 121.8933 | 122.1451 | 121.9849 | 121.7606 | 122.1085 | 121.8933 | 121.9849 | 121.9574 | 122.1451 | -0.34332 | -0.32501
745.7812 | 122.2595 | -122.0032 | 0.15106 | 0.1458 | 0.017756 | 0.0035162 | 0.047078 | -0.010421 | -0.0086987 | 0.017962 | -0.082397 | 0.11444 | -0.21515 | -0.054932 | -0.022888 | 0.013733 | 0.004578 | 0.041199 | 0.16022 | -0.19226 | 121.788 | -0.036621 | 121.9208 | 121.9482 | -0.17395 | 121.8109 | 0.009155 | 0.13275 | 122.0078 | 122.0444 | 121.9803 | 122.1176 | 121.9208 | 122.1634 | 122.0169 | 121.8109 | 122.1176 | 121.9208 | 122.0169 | 121.9803 | 122.1634 | -0.36621 | -0.34332
747.5156 | 122.3511 | -121.9666 | 0.11444 | -0.22804 | 0.017756 | 0.0094978 | 0.043447 | -0.010421 | -0.0097669 | 0.017321 | -0.036621 | 0.13275 | -0.18768 | -0.032043 | 0.022888 | 0.041199 | 0.054932 | 0.09613 | 0.16479 | -0.20142 | 121.7789 | 0.01831 | 121.9299 | 121.9345 | -0.091553 | 121.7651 | 0.050354 | 0.15106 | 122.0215 | 122.0627 | 121.9894 | 122.0993 | 121.9299 | 122.1313 | 122.0078 | 121.7651 | 122.0993 | 121.9299 | 122.0078 | 121.9894 | 122.1313 | -0.30212 | -0.31586
749.25 | 122.2549 | -122.0261 | 0.14648 | 0.13817 | 0.016261 | 0.009284 | 0.04131 | -0.011916 | -0.0078443 | 0.015184 | 0.013733 | 0.073242 | -0.1831 | 0.027466 | 0.086975 | 0.16022 | -0.15106 | 0.16479 | 0.1236 | -0.16479 | 121.843 | -0.073242 | 122.0398 | 122.0535 | -0.059509 | 121.8613 | -0.022888 | 0.19684 | 121.875 | 122.1909 | 122.113 | 122.0993 | 122.0398 | 122.1497 | 122.1863 | 121.8613 | 122.0993 | 122.0398 | 122.1863 | 122.113 | 122.1497 | -0.32959 | -0.31128
750.9844 | 122.2366 | -122.0032 | 0.16479 | 0.10765 | 0.018397 | 0.0058662 | 0.042806 | -0.0089252 | -0.0061353 | 0.015825 | 0.054932 | 0.073242 | -0.15106 | 0.054932 | 0.09613 | 0.15106 | -0.15106 | 0.16022 | 0.13733 | -0.16479 | 121.8521 | -0.091553 | 122.0581 | 122.0581 | -0.068665 | 121.8384 | -0.027466 | 0.20599 | 121.8521 | 122.1634 | 122.0993 | 122.0764 | 122.0581 | 122.1405 | 122.1542 | 121.8384 | 122.0764 | 122.0581 | 122.1542 | 122.0993 | 122.1405 | -0.31586 | -0.32959
752.7188 | 122.3145 | -121.994 | 0.14648 | -0.22041 | 0.01797 | 0.011634 | 0.043874 | -0.01213 | -0.0067761 | 0.015184 | 0.073242 | 0.086975 | -0.15564 | 0.086975 | 0.1236 | 0.15564 | -0.10071 | 0.2243 | 0.13275 | -0.16022 | 121.8384 | -0.059509 | 122.0673 | 122.081 | -0.022888 | 121.8338 | -0.013733 | 0.22888 | 121.8933 | 122.2183 | 122.1176 | 122.081 | 122.0673 | 122.1268 | 122.1497 | 121.8338 | 122.081 | 122.0673 | 122.1497 | 122.1176 | 122.1268 | -0.30212 | -0.3067
754.3906 | 122.3465 | -121.9666 | 0.13275 | -0.029679 | 0.017116 | 0.008216 | 0.044728 | -0.013198 | -0.0054943 | 0.01668 | 0 | 0.11444 | -0.1831 | 0.032043 | 0.073242 | 0.13275 | -0.10071 | 0.17853 | 0.15564 | -0.16479 | 121.7834 | -0.01831 | 121.9666 | 121.9986 | -0.059509 | 121.8018 | 0.022889 | 0.1831 | 121.8658 | 122.1451 | 122.0398 | 122.081 | 121.9666 | 122.1222 | 122.0993 | 121.8018 | 122.081 | 121.9666 | 122.0993 | 122.0398 | 122.1222 | -0.31586 | -0.29755
756.1406 | 122.3831 | -121.9803 | 0.12817 | -0.19753 | 0.018184 | 0.009284 | 0.049001 | -0.013411 | -0.0069897 | 0.017748 | -0.045776 | 0.10986 | -0.21515 | -0.022888 | 0.032043 | 0.036621 | 0.073242 | 0.10529 | 0.16937 | -0.19684 | 121.7651 | -0.018311 | 121.9345 | 121.9574 | -0.096131 | 121.7834 | 0.041199 | 0.16937 | 122.0535 | 122.0856 | 122.0123 | 122.0901 | 121.9345 | 122.1497 | 122.0169 | 121.7834 | 122.0901 | 121.9345 | 122.0169 | 122.0123 | 122.1497 | -0.34332 | -0.32501
757.8125 | 122.3785 | -122.0169 | 0.11444 | -0.2433 | 0.020747 | 0.008216 | 0.047506 | -0.010848 | -0.0057079 | 0.017107 | -0.064087 | 0.14191 | -0.22888 | -0.032043 | -0.009155 | 0.013733 | 0.086975 | 0.073242 | 0.17853 | -0.20142 | 121.788 | 0.027466 | 121.9528 | 121.9849 | -0.1236 | 121.8155 | 0.064087 | 0.16479 | 122.1039 | 122.0901 | 122.0078 | 122.1588 | 121.9528 | 122.1954 | 122.0306 | 121.8155 | 122.1588 | 121.9528 | 122.0306 | 122.0078 | 122.1954 | -0.34332 | -0.31586
759.5469 | 122.3648 | -121.9894 | 0.12817 | 0.054245 | 0.019893 | 0.013343 | 0.041738 | -0.011916 | -0.0039989 | 0.01903 | -0.013733 | 0.091553 | -0.17853 | 0.018311 | 0.054932 | 0.11444 | -0.082397 | 0.14648 | 0.13733 | -0.17853 | 121.8109 | -0.036621 | 121.9757 | 122.0078 | -0.073242 | 121.8109 | 0.009155 | 0.16479 | 121.907 | 122.1359 | 122.0444 | 122.081 | 121.9757 | 122.1268 | 122.1039 | 121.8109 | 122.081 | 121.9757 | 122.1039 | 122.0444 | 122.1268 | -0.3067 | -0.3067
761.2812 | 122.3648 | -121.9849 | 0.12817 | 0.061874 | 0.016261 | 0.0086432 | 0.044088 | -0.011916 | -0.0063489 | 0.016253 | -0.013733 | 0.09613 | -0.16479 | 0.022888 | 0.059509 | 0.11444 | -0.07782 | 0.15106 | 0.14648 | -0.16479 | 121.8201 | -0.032044 | 121.9711 | 122.0078 | -0.068665 | 121.8201 | 0.01831 | 0.15106 | 121.907 | 122.1359 | 122.0444 | 122.081 | 121.9711 | 122.1313 | 122.0993 | 121.8201 | 122.081 | 121.9711 | 122.0993 | 122.0444 | 122.1313 | -0.29297 | -0.29297
762.9531 | 122.374 | -122.0032 | 0.13275 | -0.20515 | 0.019038 | 0.004798 | 0.049428 | -0.012557 | -0.0059217 | 0.01668 | -0.059509 | 0.1236 | -0.20142 | -0.027466 | -0.009155 | 0.018311 | 0.059509 | 0.082397 | 0.19684 | -0.19684 | 121.8018 | -0.009155 | 121.9437 | 121.9757 | -0.14191 | 121.8063 | 0.064087 | 0.14191 | 122.0627 | 122.0856 | 121.994 | 122.1268 | 121.9437 | 122.2 | 122.0215 | 121.8063 | 122.1268 | 121.9437 | 122.0215 | 121.994 | 122.2 | -0.33417 | -0.32959
764.6875 | 122.2549 | -122.0535 | 0.16022 | 0.21446 | 0.017543 | 0.0090704 | 0.045369 | -0.011061 | -0.0095531 | 0.018175 | 0.059509 | 0.064087 | -0.16937 | 0.068665 | 0.10986 | 0.17395 | -0.17853 | 0.20142 | 0.12817 | -0.15106 | 121.8842 | -0.09613 | 122.113 | 122.1222 | -0.050354 | 121.9025 | -0.032043 | 0.22888 | 121.875 | 122.2549 | 122.1634 | 122.1176 | 122.113 | 122.1817 | 122.2275 | 121.9025 | 122.1176 | 122.113 | 122.2275 | 122.1634 | 122.1817 | -0.32959 | -0.31128
766.4375 | 122.2458 | -122.0718 | 0.15564 | 0.13054 | 0.018611 | 0.0062934 | 0.046865 | -0.0076434 | -0.0076305 | 0.016253 | 0.054932 | 0.09613 | -0.16937 | 0.059509 | 0.10529 | 0.16022 | -0.15564 | 0.18768 | 0.13275 | -0.15564 | 121.9025 | -0.05951 | 122.1268 | 122.1313 | -0.050354 | 121.9162 | -0.022889 | 0.22431 | 121.9162 | 122.2595 | 122.1771 | 122.168 | 122.1268 | 122.2046 | 122.2321 | 121.9162 | 122.168 | 122.1268 | 122.2321 | 122.1771 | 122.2046 | -0.32501 | -0.31128
768.1094 | 122.2961 | -122.049 | 0.15564 | 0.11528 | 0.021388 | 0.0097114 | 0.048574 | -0.010634 | -0.0084851 | 0.016039 | -0.086975 | 0.11902 | -0.20599 | -0.059509 | -0.013733 | 0 | 0.022888 | 0.036621 | 0.17853 | -0.20599 | 121.843 | -0.036621 | 121.962 | 121.9894 | -0.16937 | 121.843 | 0.022888 | 0.11902 | 122.0718 | 122.0856 | 122.0352 | 122.168 | 121.962 | 122.2275 | 122.049 | 121.843 | 122.168 | 121.962 | 122.049 | 122.0352 | 122.2275 | -0.36163 | -0.36163
769.8281 | 122.319 | -122.0398 | 0.14648 | -0.18227 | 0.019893 | 0.0035162 | 0.04067 | -0.01277 | -0.0074169 | 0.016039 | 0.059509 | 0.07782 | -0.16022 | 0.091553 | 0.1236 | 0.17853 | -0.10986 | 0.22888 | 0.12817 | -0.15564 | 121.8796 | -0.068664 | 122.0993 | 122.1313 | -0.022888 | 121.8842 | -0.01831 | 0.21973 | 121.9299 | 122.2687 | 122.1634 | 122.1176 | 122.0993 | 122.168 | 122.2183 | 121.8842 | 122.1176 | 122.0993 | 122.2183 | 122.1634 | 122.168 | -0.3067 | -0.30212
771.5 | 122.3785 | -122.0078 | 0.1236 | -0.22041 | 0.019252 | 0.0080024 | 0.045797 | -0.0093524 | -0.0059217 | 0.016466 | -0.054932 | 0.13275 | -0.23804 | -0.041199 | -0.004578 | 0.022888 | 0.059509 | 0.073242 | 0.1831 | -0.19684 | 121.7697 | 0.009155 | 121.9528 | 121.9666 | -0.12817 | 121.8109 | 0.059509 | 0.1831 | 122.0673 | 122.081 | 122.0032 | 122.1405 | 121.9528 | 122.1909 | 122.0306 | 121.8109 | 122.1405 | 121.9528 | 122.0306 | 122.0032 | 122.1909 | -0.36163 | -0.32043
773.2344 | 122.3969 | -122.0306 | 0.10986 | 0.023727 | 0.018184 | 0.0090704 | 0.042165 | -0.01213 | -0.0072033 | 0.016466 | -0.045776 | 0.086975 | -0.17853 | -0.004578 | 0.064087 | 0.10529 | -0.086975 | 0.15106 | 0.13733 | -0.15564 | 121.8521 | -0.022888 | 121.9849 | 122.0261 | -0.045776 | 121.875 | 0.027466 | 0.13275 | 121.9437 | 122.1817 | 122.0947 | 122.1176 | 121.9849 | 122.168 | 122.1359 | 121.875 | 122.1176 | 121.9849 | 122.1359 | 122.0947 | 122.168 | -0.28839 | -0.2655
774.9844 | 122.3831 | -122.0261 | 0.12817 | -0.21278 | 0.020106 | 0.011634 | 0.049428 | -0.0093524 | -0.0082715 | 0.015398 | -0.036621 | 0.15106 | -0.22888 | -0.032043 | 0.009155 | 0.036621 | 0.073242 | 0.086975 | 0.1831 | -0.20599 | 121.7972 | 0.022888 | 121.9894 | 121.994 | -0.11902 | 121.8201 | 0.054931 | 0.19226 | 122.0993 | 122.113 | 122.0352 | 122.1771 | 121.9894 | 122.2092 | 122.0627 | 121.8201 | 122.1771 | 121.9894 | 122.0627 | 122.0352 | 122.2092 | -0.35706 | -0.33417
776.7188 | 122.4014 | -122.0261 | 0.11902 | 0.0084684 | 0.018397 | 0.0077888 | 0.040242 | -0.010848 | -0.0067761 | 0.016253 | -0.027466 | 0.091553 | -0.19226 | 0 | 0.054932 | 0.11902 | -0.068665 | 0.16022 | 0.14648 | -0.1831 | 121.8338 | -0.027466 | 121.9986 | 122.0261 | -0.064087 | 121.843 | 0.027465 | 0.16479 | 121.9574 | 122.1863 | 122.081 | 122.1176 | 121.9986 | 122.1725 | 122.1451 | 121.843 | 122.1176 | 121.9986 | 122.1451 | 122.081 | 122.1725 | -0.31128 | -0.30212
778.3906 | 122.3511 | -122.0856 | 0.13275 | 0.12291 | 0.021388 | 0.002021 | 0.04366 | -0.010207 | -0.0052807 | 0.017962 | 0.004578 | 0.091553 | -0.1831 | 0.027466 | 0.073242 | 0.11902 | -0.09613 | 0.15564 | 0.12817 | -0.16022 | 121.9025 | -0.041198 | 122.0901 | 122.113 | -0.059509 | 121.9254 | -0.004577 | 0.18768 | 121.9894 | 122.2412 | 122.1588 | 122.1771 | 122.0901 | 122.2137 | 122.2046 | 121.9254 | 122.1771 | 122.0901 | 122.2046 | 122.1588 | 122.2137 | -0.31586 | -0.29297
780.125 | 122.4106 | -122.049 | 0.13275 | 0.069504 | 0.018825 | 0.0077888 | 0.044301 | -0.011061 | -0.0057079 | 0.01668 | 0.004578 | 0.082397 | -0.16479 | 0.004578 | 0.050354 | 0.11902 | -0.082397 | 0.13275 | 0.15564 | -0.1831 | 121.8842 | -0.050354 | 122.0535 | 122.0535 | -0.082397 | 121.8658 | 0.022889 | 0.16937 | 121.9666 | 122.1817 | 122.0993 | 122.1313 | 122.0535 | 122.2046 | 122.168 | 121.8658 | 122.1313 | 122.0535 | 122.168 | 122.0993 | 122.2046 | -0.29755 | -0.31586
781.8594 | 122.3373 | -122.0901 | 0.16937 | 0.054245 | 0.017756 | 0.011207 | 0.051564 | -0.010421 | -0.010194 | 0.018389 | -0.059509 | 0.10529 | -0.2243 | -0.064087 | -0.036621 | 0.004578 | 0.027466 | 0.045776 | 0.16937 | -0.19684 | 121.8658 | -0.064087 | 122.0306 | 122.0261 | -0.20599 | 121.8933 | 0 | 0.16479 | 122.1176 | 122.1359 | 122.0535 | 122.1954 | 122.0306 | 122.2595 | 122.0947 | 121.8933 | 122.1954 | 122.0306 | 122.0947 | 122.0535 | 122.2595 | -0.39368 | -0.36621
783.5312 | 122.2916 | -122.1039 | 0.16479 | -0.12886 | 0.019252 | 0.009284 | 0.048146 | -0.0091388 | -0.0086987 | 0.018816 | 0.004578 | 0.13275 | -0.21973 | 0.036621 | 0.041199 | 0.068665 | -0.004578 | 0.11902 | 0.16937 | -0.1831 | 121.8842 | -0.032044 | 122.1085 | 122.1405 | -0.1236 | 121.9208 | 0.004578 | 0.22431 | 122.0993 | 122.2229 | 122.1451 | 122.2366 | 122.1085 | 122.2733 | 122.1725 | 121.9208 | 122.2366 | 122.1085 | 122.1725 | 122.1451 | 122.2733 | -0.38452 | -0.3479
785.3906 | 122.3007 | -122.0627 | 0.16479 | 0.18394 | 0.019893 | 0.012702 | 0.04601 | -0.010634 | -0.010621 | 0.01967 | -0.027466 | 0.10529 | -0.19226 | 0.004578 | 0.022888 | 0.091553 | -0.091553 | 0.13275 | 0.15564 | -0.17395 | 121.8704 | -0.059509 | 122.0352 | 122.0673 | -0.14191 | 121.8887 | -0.009155 | 0.16479 | 121.9711 | 122.1954 | 122.0856 | 122.168 | 122.0352 | 122.2183 | 122.1542 | 121.8887 | 122.168 | 122.0352 | 122.1542 | 122.0856 | 122.2183 | -0.35706 | -0.33874
787.1406 | 122.2961 | -122.1313 | 0.15106 | 0.16869 | 0.016047 | 0.012275 | 0.044515 | -0.0087116 | -0.0061353 | 0.017107 | 0.050354 | 0.068665 | -0.16022 | 0.050354 | 0.10986 | 0.16479 | -0.16022 | 0.19226 | 0.14191 | -0.16937 | 121.9711 | -0.082397 | 122.1817 | 122.1817 | -0.041199 | 121.962 | -0.009155 | 0.21057 | 121.9711 | 122.3236 | 122.2412 | 122.2 | 122.1817 | 122.2733 | 122.2961 | 121.962 | 122.2 | 122.1817 | 122.2961 | 122.2412 | 122.2733 | -0.31128 | -0.32044
788.875 | 122.287 | -122.1039 | 0.16479 | 0.17632 | 0.018397 | 0.012061 | 0.047719 | -0.011275 | -0.0067761 | 0.016893 | 0.036621 | 0.086975 | -0.17395 | 0.064087 | 0.07782 | 0.14191 | -0.13275 | 0.16479 | 0.12817 | -0.16022 | 121.9299 | -0.07782 | 122.1405 | 122.168 | -0.086975 | 121.9437 | -0.036621 | 0.21057 | 121.9711 | 122.2687 | 122.1817 | 122.1909 | 122.1405 | 122.2321 | 122.2458 | 121.9437 | 122.1909 | 122.1405 | 122.2458 | 122.1817 | 122.2321 | -0.33874 | -0.32501
790.625 | 122.3969 | -122.0627 | 0.13275 | 0.084762 | 0.015193 | 0.0088568 | 0.042592 | -0.011702 | -0.0069897 | 0.017748 | 0.004578 | 0.091553 | -0.17395 | 0.004578 | 0.064087 | 0.11444 | -0.091553 | 0.14191 | 0.1236 | -0.1831 | 121.8887 | -0.041198 | 122.0673 | 122.0673 | -0.068664 | 121.8796 | -0.009155 | 0.17853 | 121.9711 | 122.2046 | 122.1268 | 122.1542 | 122.0673 | 122.1863 | 122.1771 | 121.8796 | 122.1542 | 122.0673 | 122.1771 | 122.1268 | 122.1863 | -0.3067 | -0.31586
792.2969 | 122.3007 | -122.0627 | 0.13733 | 0.16869 | 0.016902 | 0.015052 | 0.045156 | -0.011275 | -0.0078443 | 0.018602 | 0.041199 | 0.086975 | -0.16479 | 0.073242 | 0.11444 | 0.15564 | -0.16479 | 0.19684 | 0.12817 | -0.16022 | 121.8979 | -0.050354 | 122.1039 | 122.1359 | -0.022888 | 121.9025 | -0.009155 | 0.20599 | 121.8979 | 122.2595 | 122.1771 | 122.1497 | 122.1039 | 122.1909 | 122.2183 | 121.9025 | 122.1497 | 122.1039 | 122.2183 | 122.1771 | 122.1909 | -0.30212 | -0.29755
793.9844 | 122.4106 | -122.0581 | 0.13275 | 0.092392 | 0.017329 | 0.0073614 | 0.043447 | -0.012343 | -0.0069897 | 0.018816 | 0.004578 | 0.10071 | -0.16479 | 0.013733 | 0.059509 | 0.12817 | -0.10071 | 0.13733 | 0.14648 | -0.17853 | 121.8933 | -0.032043 | 122.0627 | 122.0718 | -0.073242 | 121.8796 | 0.013733 | 0.16937 | 121.9574 | 122.1954 | 122.1176 | 122.1588 | 122.0627 | 122.2046 | 122.1863 | 121.8796 | 122.1588 | 122.0627 | 122.1863 | 122.1176 | 122.2046 | -0.29755 | -0.31128
795.6875 | 122.3007 | -122.113 | 0.16022 | -0.060196 | 0.017756 | 0.0080024 | 0.050924 | -0.010634 | -0.0080579 | 0.018602 | 0.009155 | 0.082397 | -0.21515 | 0.041199 | 0.032043 | 0.064087 | -0.032043 | 0.11902 | 0.16022 | -0.17853 | 121.8979 | -0.07782 | 122.1222 | 122.1542 | -0.12817 | 121.9345 | 0 | 0.2243 | 122.081 | 122.2321 | 122.1451 | 122.1954 | 122.1222 | 122.2733 | 122.1771 | 121.9345 | 122.1954 | 122.1222 | 122.1771 | 122.1451 | 122.2733 | -0.37537 | -0.33874
797.3594 | 122.3602 | -122.1039 | 0.16479 | 0.16869 | 0.018825 | 0.0086432 | 0.049215 | -0.010848 | -0.0082715 | 0.016039 | -0.059509 | 0.13733 | -0.21973 | -0.059509 | -0.036621 | 0.027466 | 0.013733 | 0.036621 | 0.18768 | -0.18768 | 121.8842 | -0.027466 | 122.0444 | 122.0444 | -0.20142 | 121.9162 | 0.022888 | 0.16022 | 122.1176 | 122.1405 | 122.0673 | 122.2412 | 122.0444 | 122.2916 | 122.1313 | 121.9162 | 122.2412 | 122.0444 | 122.1313 | 122.0673 | 122.2916 | -0.38452 | -0.35248
799.0625 | 122.3282 | -122.0718 | 0.15564 | 0.1458 | 0.016261 | 0.0075752 | 0.042379 | -0.010207 | -0.0074169 | 0.016466 | 0.041199 | 0.054932 | -0.16937 | 0.064087 | 0.10071 | 0.15106 | -0.14191 | 0.19226 | 0.13275 | -0.14191 | 121.9025 | -0.10071 | 122.113 | 122.1359 | -0.054932 | 121.9299 | -0.022889 | 0.21057 | 121.9299 | 122.2641 | 122.1725 | 122.1268 | 122.113 | 122.2046 | 122.2229 | 121.9299 | 122.1268 | 122.113 | 122.2229 | 122.1725 | 122.2046 | -0.32501 | -0.29755
800.75 | 122.3602 | -122.0718 | 0.16937 | 0.13054 | 0.019893 | 0.0071478 | 0.048574 | -0.007857 | -0.0078443 | 0.017748 | -0.036621 | 0.11444 | -0.21973 | -0.050354 | 0 | 0.059509 | -0.045776 | 0.068665 | 0.15106 | -0.19226 | 121.8521 | -0.054932 | 122.0352 | 122.0215 | -0.16937 | 121.8796 | -0.018311 | 0.18311 | 122.0261 | 122.1405 | 122.0718 | 122.1863 | 122.0352 | 122.2229 | 122.1313 | 121.8796 | 122.1863 | 122.0352 | 122.1313 | 122.0718 | 122.2229 | -0.3891 | -0.36163
802.4531 | 122.4609 | -122.0856 | 0.11902 | -0.19753 | 0.018397 | 0.0080024 | 0.04366 | -0.010848 | -0.0080579 | 0.018175 | -0.068665 | 0.11902 | -0.21057 | -0.032043 | -0.009155 | 0.027466 | 0.07782 | 0.091553 | 0.18768 | -0.17853 | 121.875 | 0 | 122.0169 | 122.0535 | -0.12817 | 121.907 | 0.068664 | 0.14191 | 122.1634 | 122.1771 | 122.0764 | 122.2046 | 122.0169 | 122.2733 | 122.113 | 121.907 | 122.2046 | 122.0169 | 122.113 | 122.0764 | 122.2733 | -0.32959 | -0.29755
804.1562 | 122.4014 | -122.0993 | 0.15106 | 0.11528 | 0.01797 | 0.0060798 | 0.041951 | -0.011275 | -0.0069897 | 0.016893 | -0.004578 | 0.07782 | -0.17853 | 0.018311 | 0.07782 | 0.12817 | -0.091553 | 0.15106 | 0.14648 | -0.16479 | 121.9208 | -0.073242 | 122.0947 | 122.1176 | -0.073242 | 121.9345 | -0.004578 | 0.17395 | 122.0078 | 122.2504 | 122.1771 | 122.1771 | 122.0947 | 122.2458 | 122.2275 | 121.9345 | 122.1771 | 122.0947 | 122.2275 | 122.1771 | 122.2458 | -0.32959 | -0.31586
805.8281 | 122.3557 | -122.1176 | 0.16479 | 0.13054 | 0.018611 | 0.0090704 | 0.048574 | -0.009566 | -0.0048535 | 0.017748 | -0.032043 | 0.11902 | -0.21057 | -0.036621 | 0.018311 | 0.054932 | -0.045776 | 0.07782 | 0.16479 | -0.19684 | 121.907 | -0.045776 | 122.0856 | 122.081 | -0.14648 | 121.9208 | 0 | 0.17853 | 122.0718 | 122.1954 | 122.1359 | 122.2366 | 122.0856 | 122.2824 | 122.1725 | 121.9208 | 122.2366 | 122.0856 | 122.1725 | 122.1359 | 122.2824 | -0.37537 | -0.36163
807.5312 | 122.3648 | -122.1222 | 0.16937 | 0.11528 | 0.016475 | 0.011634 | 0.046437 | -0.009566 | -0.0084851 | 0.018175 | -0.059509 | 0.12817 | -0.19684 | -0.032043 | 0 | 0.064087 | -0.027466 | 0.059509 | 0.1831 | -0.1831 | 121.9254 | -0.041199 | 122.0627 | 122.0901 | -0.16937 | 121.9391 | 0.013732 | 0.13733 | 122.0947 | 122.1817 | 122.1222 | 122.2504 | 122.0627 | 122.3053 | 122.1863 | 121.9391 | 122.2504 | 122.0627 | 122.1863 | 122.1222 | 122.3053 | -0.36621 | -0.35248
809.2344 | 122.3328 | -122.1588 | 0.17395 | -0.037308 | 0.018184 | 0.0058662 | 0.047933 | -0.0093524 | -0.0067761 | 0.016466 | 0.004578 | 0.11444 | -0.19226 | 0.013733 | 0.041199 | 0.073242 | -0.013733 | 0.11444 | 0.1831 | -0.17395 | 121.9666 | -0.059509 | 122.1634 | 122.1725 | -0.13275 | 121.9849 | 0.009155 | 0.19684 | 122.1451 | 122.2733 | 122.2 | 122.2733 | 122.1634 | 122.3419 | 122.2321 | 121.9849 | 122.2733 | 122.1634 | 122.2321 | 122.2 | 122.3419 | -0.36621 | -0.3479
810.9688 | 122.3648 | -122.1405 | 0.16937 | 0.0084684 | 0.019465 | 0.0069342 | 0.047719 | -0.009566 | -0.0072033 | 0.017962 | -0.032043 | 0.13275 | -0.21057 | -0.022888 | 0.009155 | 0.032043 | 0.013733 | 0.064087 | 0.16479 | -0.21057 | 121.9299 | -0.036622 | 122.1085 | 122.1176 | -0.16022 | 121.9299 | -0.004578 | 0.17853 | 122.1542 | 122.2046 | 122.1497 | 122.2733 | 122.1085 | 122.3053 | 122.1725 | 121.9299 | 122.2733 | 122.1085 | 122.1725 | 122.1497 | 122.3053 | -0.37994 | -0.37994
812.6719 | 122.3465 | -122.1268 | 0.16937 | -0.098343 | 0.017543 | 0.010779 | 0.046437 | -0.010848 | -0.0082715 | 0.019243 | -0.022888 | 0.12817 | -0.21057 | 0.013733 | 0.045776 | 0.07782 | -0.004578 | 0.13275 | 0.17395 | -0.16937 | 121.9162 | -0.041199 | 122.1039 | 122.1405 | -0.1236 | 121.9574 | 0.004577 | 0.18768 | 122.1222 | 122.2595 | 122.1725 | 122.2549 | 122.1039 | 122.3007 | 122.2046 | 121.9574 | 122.2549 | 122.1039 | 122.2046 | 122.1725 | 122.3007 | -0.37994 | -0.33875
814.3594 | 122.3328 | -122.1405 | 0.19684 | -0.060196 | 0.017543 | 0.0067206 | 0.045797 | -0.010207 | -0.0078443 | 0.017107 | -0.009155 | 0.10986 | -0.20142 | 0.018311 | 0.068665 | 0.091553 | -0.018311 | 0.12817 | 0.17395 | -0.17853 | 121.9391 | -0.086975 | 122.1313 | 122.1588 | -0.12817 | 121.962 | -0.022888 | 0.19226 | 122.1222 | 122.2687 | 122.2092 | 122.2504 | 122.1313 | 122.3145 | 122.2321 | 121.962 | 122.2504 | 122.1313 | 122.2321 | 122.2092 | 122.3145 | -0.39825 | -0.37537
816.1094 | 122.4014 | -122.1176 | 0.15106 | 0.12291 | 0.018397 | 0.0077888 | 0.044942 | -0.011275 | -0.0074169 | 0.018175 | -0.082397 | 0.13275 | -0.20599 | -0.073242 | -0.013733 | 0.045776 | 0.013733 | 0.041199 | 0.18768 | -0.20142 | 121.9116 | -0.018311 | 122.0352 | 122.0444 | -0.16479 | 121.9162 | 0.036621 | 0.1236 | 122.1313 | 122.1588 | 122.1039 | 122.2504 | 122.0352 | 122.3053 | 122.1634 | 121.9162 | 122.2504 | 122.0352 | 122.1634 | 122.1039 | 122.3053 | -0.35706 | -0.35248
817.7812 | 122.4014 | -122.113 | 0.14648 | 0.1458 | 0.01797 | 0.0060798 | 0.044088 | -0.011489 | -0.0063489 | 0.018175 | -0.086975 | 0.12817 | -0.21515 | -0.07782 | -0.032043 | 0.036621 | 0.027466 | 0.036621 | 0.16937 | -0.18768 | 121.8979 | -0.01831 | 122.0261 | 122.0352 | -0.17853 | 121.9254 | 0.022889 | 0.12817 | 122.1405 | 122.1497 | 122.081 | 122.2412 | 122.0261 | 122.2824 | 122.1497 | 121.9254 | 122.2412 | 122.0261 | 122.1497 | 122.081 | 122.2824 | -0.36163 | -0.33417
819.4844 | 122.3511 | -122.1359 | 0.16479 | 0.1992 | 0.017543 | 0.0086432 | 0.042592 | -0.0089252 | -0.0072033 | 0.018816 | 0.036621 | 0.086975 | -0.14648 | 0.054932 | 0.10529 | 0.16937 | -0.17395 | 0.21057 | 0.13275 | -0.16022 | 121.9894 | -0.07782 | 122.1725 | 122.1909 | -0.059509 | 121.9757 | -0.032044 | 0.18311 | 121.962 | 122.3465 | 122.2412 | 122.2229 | 122.1725 | 122.2687 | 122.3053 | 121.9757 | 122.2229 | 122.1725 | 122.3053 | 122.2412 | 122.2687 | -0.31128 | -0.32501
821.1719 | 122.4426 | -122.0947 | 0.12817 | -0.1136 | 0.017756 | 0.0058662 | 0.041738 | -0.012557 | -0.0042127 | 0.017962 | 0.045776 | 0.09613 | -0.16479 | 0.073242 | 0.11444 | 0.18768 | -0.12817 | 0.22888 | 0.15106 | -0.16937 | 121.9299 | -0.032044 | 122.1405 | 122.168 | -0.013733 | 121.9254 | 0.022888 | 0.21057 | 121.9666 | 122.3236 | 122.2092 | 122.1909 | 122.1405 | 122.2458 | 122.2824 | 121.9254 | 122.1909 | 122.1405 | 122.2824 | 122.2092 | 122.2458 | -0.29297 | -0.29755
822.875 | 122.3877 | -122.1085 | 0.15106 | 0.1458 | 0.019679 | 0.008216 | 0.047933 | -0.01213 | -0.0061353 | 0.015398 | -0.059509 | 0.12817 | -0.21057 | -0.059509 | -0.022888 | 0.036621 | 0 | 0.054932 | 0.16479 | -0.17853 | 121.8979 | -0.022888 | 122.0489 | 122.0489 | -0.17395 | 121.9299 | 0.013733 | 0.15106 | 122.1085 | 122.1634 | 122.0856 | 122.2366 | 122.0489 | 122.2733 | 122.1451 | 121.9299 | 122.2366 | 122.0489 | 122.1451 | 122.0856 | 122.2733 | -0.36163 | -0.32959
824.5938 | 122.4152 | -122.1222 | 0.15106 | -0.18227 | 0.014979 | 0.0084296 | 0.041524 | -0.012343 | -0.0057079 | 0.017107 | 0.045776 | 0.086975 | -0.17395 | 0.086975 | 0.12817 | 0.17853 | -0.10071 | 0.24719 | 0.1236 | -0.16937 | 121.9482 | -0.064087 | 122.168 | 122.2092 | -0.022888 | 121.9528 | -0.027466 | 0.21973 | 122.0215 | 122.3694 | 122.2504 | 122.2092 | 122.168 | 122.2458 | 122.3007 | 121.9528 | 122.2092 | 122.168 | 122.3007 | 122.2504 | 122.2458 | -0.32501 | -0.32044
826.2812 | 122.4197 | -122.1313 | 0.15564 | -0.15175 | 0.019679 | 0.0075752 | 0.048574 | -0.010421 | -0.0089123 | 0.018175 | -0.022888 | 0.1236 | -0.20599 | -0.004578 | 0.032043 | 0.064087 | 0.013733 | 0.13275 | 0.17395 | -0.20142 | 121.9254 | -0.032044 | 122.1085 | 122.1268 | -0.1236 | 121.9299 | 0.01831 | 0.18311 | 122.1451 | 122.2641 | 122.1634 | 122.2549 | 122.1085 | 122.3053 | 122.1954 | 121.9299 | 122.2549 | 122.1085 | 122.1954 | 122.1634 | 122.3053 | -0.36163 | -0.35706
828.0156 | 122.3648 | -122.1634 | 0.16479 | 0.22209 | 0.017329 | 0.010779 | 0.047506 | -0.0093524 | -0.0076305 | 0.017321 | -0.032043 | 0.10529 | -0.19226 | 0.004578 | 0.054932 | 0.09613 | -0.1236 | 0.14648 | 0.16022 | -0.16022 | 121.9711 | -0.059509 | 122.1313 | 122.168 | -0.10986 | 122.0032 | -0.004578 | 0.16022 | 122.0398 | 122.3099 | 122.2183 | 122.2687 | 122.1313 | 122.3236 | 122.2595 | 122.0032 | 122.2687 | 122.1313 | 122.2595 | 122.2183 | 122.3236 | -0.35706 | -0.32501
829.6875 | 122.406 | -122.1359 | 0.16479 | 0.13817 | 0.017116 | 0.0069342 | 0.04601 | -0.0093524 | -0.0074169 | 0.017107 | -0.073242 | 0.12817 | -0.18768 | -0.050354 | -0.013733 | 0.041199 | 0 | 0.059509 | 0.20599 | -0.19226 | 121.9482 | -0.036621 | 122.0627 | 122.0856 | -0.17853 | 121.9437 | 0.041199 | 0.11444 | 122.1359 | 122.1954 | 122.1222 | 122.2641 | 122.0627 | 122.3419 | 122.1771 | 121.9437 | 122.2641 | 122.0627 | 122.1771 | 122.1222 | 122.3419 | -0.35248 | -0.35706
831.3906 | 122.3785 | -122.1497 | 0.1831 | -0.052567 | 0.016902 | 0.009925 | 0.047506 | -0.011061 | -0.0084851 | 0.018816 | -0.013733 | 0.1236 | -0.20599 | 0.022888 | 0.050354 | 0.07782 | -0.018311 | 0.12817 | 0.16937 | -0.21057 | 121.9437 | -0.059509 | 122.1359 | 122.1725 | -0.13275 | 121.9391 | -0.013732 | 0.19226 | 122.1313 | 122.2778 | 122.2 | 122.2733 | 122.1359 | 122.319 | 122.2275 | 121.9391 | 122.2733 | 122.1359 | 122.2275 | 122.2 | 122.319 | -0.3891 | -0.39368
833.1094 | 122.4792 | -122.1634 | 0.14191 | -0.1899 | 0.018825 | 0.0052252 | 0.042379 | -0.010421 | -0.0050671 | 0.015612 | 0.036621 | 0.082397 | -0.16022 | 0.036621 | 0.086975 | 0.11902 | -0.022888 | 0.1831 | 0.16937 | -0.17395 | 122.0032 | -0.05951 | 122.2 | 122.2 | -0.054932 | 121.9894 | 0.027466 | 0.19684 | 122.1405 | 122.3465 | 122.2504 | 122.2458 | 122.2 | 122.3328 | 122.2824 | 121.9894 | 122.2458 | 122.2 | 122.2824 | 122.2504 | 122.3328 | -0.30212 | -0.31586
834.7812 | 122.5204 | -122.1222 | 0.1236 | -0.1899 | 0.01797 | 0.0097114 | 0.043874 | -0.01213 | -0.0089123 | 0.015184 | -0.054932 | 0.13275 | -0.20142 | -0.036621 | 0.004578 | 0.018311 | 0.07782 | 0.09613 | 0.19684 | -0.20599 | 121.9208 | 0.009155 | 122.0673 | 122.0856 | -0.11902 | 121.9162 | 0.073242 | 0.14648 | 122.2 | 122.2183 | 122.1268 | 122.2549 | 122.0673 | 122.319 | 122.1405 | 121.9162 | 122.2549 | 122.0673 | 122.1405 | 122.1268 | 122.319 | -0.32501 | -0.32959
836.4688 | 122.3602 | -122.168 | 0.16937 | 0.20683 | 0.019465 | 0.0090704 | 0.044301 | -0.010207 | -0.0052807 | 0.018602 | 0.050354 | 0.082397 | -0.16937 | 0.050354 | 0.10986 | 0.16937 | -0.16937 | 0.19226 | 0.1236 | -0.15106 | 121.9986 | -0.086976 | 122.2183 | 122.2183 | -0.05951 | 122.0169 | -0.045777 | 0.21973 | 121.9986 | 122.3602 | 122.2778 | 122.2504 | 122.2183 | 122.2916 | 122.3373 | 122.0169 | 122.2504 | 122.2183 | 122.3373 | 122.2778 | 122.2916 | -0.33875 | -0.32044
838.1719 | 122.3694 | -122.2046 | 0.17395 | -0.067826 | 0.017116 | 0.0062934 | 0.050496 | -0.011702 | -0.0084851 | 0.017962 | 0.004578 | 0.13733 | -0.2243 | 0.004578 | 0.032043 | 0.082397 | -0.013733 | 0.12817 | 0.17853 | -0.19684 | 121.9803 | -0.036621 | 122.2092 | 122.2092 | -0.14191 | 122.0078 | 0.004578 | 0.22888 | 122.1909 | 122.3328 | 122.2366 | 122.3419 | 122.2092 | 122.3831 | 122.287 | 122.0078 | 122.3419 | 122.2092 | 122.287 | 122.2366 | 122.3831 | -0.39825 | -0.37079
839.8594 | 122.3923 | -122.1405 | 0.15564 | 0.15343 | 0.019465 | 0.0088568 | 0.045797 | -0.010421 | -0.0063489 | 0.016253 | -0.036621 | 0.11902 | -0.20599 | -0.022888 | 0.018311 | 0.073242 | -0.059509 | 0.091553 | 0.15106 | -0.17395 | 121.9345 | -0.036621 | 122.1039 | 122.1176 | -0.13733 | 121.9666 | -0.004578 | 0.16937 | 122.081 | 122.2321 | 122.1588 | 122.2595 | 122.1039 | 122.2916 | 122.2137 | 121.9666 | 122.2595 | 122.1039 | 122.2137 | 122.1588 | 122.2916 | -0.36163 | -0.32959
841.5625 | 122.4014 | -122.2 | 0.13275 | 0.17632 | 0.020106 | 0.012275 | 0.04601 | -0.011061 | -0.0063489 | 0.01903 | -0.054932 | 0.1236 | -0.18768 | -0.045776 | 0.004578 | 0.059509 | -0.064087 | 0.073242 | 0.16022 | -0.20599 | 122.0123 | -0.009155 | 122.1451 | 122.1542 | -0.12817 | 121.994 | 0.027466 | 0.13275 | 122.1359 | 122.2733 | 122.2046 | 122.3236 | 122.1451 | 122.3602 | 122.2595 | 121.994 | 122.3236 | 122.1451 | 122.2595 | 122.2046 | 122.3602 | -0.32043 | -0.33875
843.2656 | 122.5067 | -122.1405 | 0.1236 | 0.046615 | 0.017329 | 0.006507 | 0.042165 | -0.011275 | -0.0048535 | 0.016466 | -0.041199 | 0.10986 | -0.18768 | -0.013733 | 0.064087 | 0.11444 | -0.07782 | 0.14191 | 0.15106 | -0.17853 | 121.9528 | -0.013733 | 122.0993 | 122.1268 | -0.059509 | 121.962 | 0.027466 | 0.14648 | 122.0627 | 122.2824 | 122.2046 | 122.2504 | 122.0993 | 122.2916 | 122.2549 | 121.962 | 122.2504 | 122.0993 | 122.2549 | 122.2046 | 122.2916 | -0.31128 | -0.30212
845 | 122.4655 | -122.1451 | 0.14191 | -0.21278 | 0.018397 | 0.0043708 | 0.041951 | -0.011702 | -0.0054943 | 0.016039 | 0.041199 | 0.07782 | -0.17395 | 0.09613 | 0.13275 | 0.17395 | -0.10529 | 0.23804 | 0.11444 | -0.15106 | 121.9711 | -0.064087 | 122.1863 | 122.2412 | -0.009156 | 121.994 | -0.027466 | 0.21515 | 122.0398 | 122.3831 | 122.2778 | 122.2229 | 122.1863 | 122.2595 | 122.319 | 121.994 | 122.2229 | 122.1863 | 122.319 | 122.2778 | 122.2595 | -0.31586 | -0.29297
846.7031 | 122.5204 | -122.1176 | 0.1236 | 0.031357 | 0.017543 | 0.010779 | 0.043447 | -0.011275 | -0.0052807 | 0.016253 | -0.018311 | 0.091553 | -0.17853 | 0.004578 | 0.07782 | 0.11902 | -0.086975 | 0.16022 | 0.13733 | -0.18768 | 121.9391 | -0.032043 | 122.0993 | 122.1222 | -0.045776 | 121.9299 | 0.013733 | 0.16022 | 122.0306 | 122.2778 | 122.1954 | 122.2092 | 122.0993 | 122.2549 | 122.2366 | 121.9299 | 122.2092 | 122.0993 | 122.2366 | 122.1954 | 122.2549 | -0.30212 | -0.31128
848.4062 | 122.4014 | -122.2046 | 0.17395 | -0.022049 | 0.016261 | 0.0073614 | 0.051564 | -0.01213 | -0.0095531 | 0.018389 | -0.022888 | 0.1236 | -0.20599 | -0.004578 | 0 | 0.050354 | -0.004578 | 0.10529 | 0.16479 | -0.18768 | 121.9986 | -0.050354 | 122.1817 | 122.2 | -0.17395 | 122.0169 | -0.009155 | 0.18311 | 122.2 | 122.3099 | 122.2046 | 122.3282 | 122.1817 | 122.3694 | 122.2549 | 122.0169 | 122.3282 | 122.1817 | 122.2549 | 122.2046 | 122.3694 | -0.37994 | -0.36163
850.1094 | 122.4747 | -122.1497 | 0.11902 | -0.060196 | 0.019038 | 0.0035162 | 0.041738 | -0.013411 | -0.0025037 | 0.017321 | 0.009155 | 0.086975 | -0.16937 | 0.036621 | 0.10529 | 0.14648 | -0.10529 | 0.21973 | 0.13275 | -0.19226 | 121.9803 | -0.032044 | 122.1588 | 122.1863 | -0.013733 | 121.9574 | 0.013732 | 0.17853 | 122.0444 | 122.3694 | 122.2549 | 122.2366 | 122.1588 | 122.2824 | 122.2961 | 121.9574 | 122.2366 | 122.1588 | 122.2961 | 122.2549 | 122.2824 | -0.28839 | -0.31128
851.7812 | 122.5204 | -122.1405 | 0.14648 | -0.037308 | 0.016902 | 0.0080024 | 0.042806 | -0.01277 | -0.0037853 | 0.017107 | -0.009155 | 0.09613 | -0.18768 | 0.018311 | 0.064087 | 0.12817 | -0.10071 | 0.17395 | 0.11902 | -0.18768 | 121.9528 | -0.050354 | 122.1313 | 122.1588 | -0.082397 | 121.9528 | -0.027465 | 0.17853 | 122.0398 | 122.3145 | 122.2046 | 122.2366 | 122.1313 | 122.2595 | 122.2687 | 121.9528 | 122.2366 | 122.1313 | 122.2687 | 122.2046 | 122.2595 | -0.33417 | -0.33417
853.4844 | 122.493 | -122.1634 | 0.1236 | -0.15938 | 0.018184 | 0.0069342 | 0.044728 | -0.015761 | -0.0067761 | 0.017321 | 0.027466 | 0.10071 | -0.1831 | 0.07782 | 0.10529 | 0.15564 | -0.12817 | 0.22888 | 0.13275 | -0.17395 | 121.9803 | -0.022888 | 122.1909 | 122.2412 | -0.01831 | 121.9894 | 0.009155 | 0.21057 | 122.0352 | 122.3923 | 122.2687 | 122.2641 | 122.1909 | 122.2961 | 122.319 | 121.9894 | 122.2641 | 122.1909 | 122.319 | 122.2687 | 122.2961 | -0.3067 | -0.29755
855.1875 | 122.4564 | -122.1817 | 0.16022 | 0.13817 | 0.017116 | 0.010139 | 0.048787 | -0.0097796 | -0.0078443 | 0.015825 | -0.054932 | 0.13275 | -0.21515 | -0.045776 | -0.036621 | 0.018311 | 0.018311 | 0.045776 | 0.16937 | -0.19684 | 121.9666 | -0.027466 | 122.1268 | 122.1359 | -0.19684 | 121.9849 | 0.009156 | 0.16022 | 122.2 | 122.2275 | 122.1451 | 122.3145 | 122.1268 | 122.3511 | 122.2 | 121.9849 | 122.3145 | 122.1268 | 122.2 | 122.1451 | 122.3511 | -0.37537 | -0.35706
856.8906 | 122.5296 | -122.2 | 0.1236 | -0.23567 | 0.018825 | 0.0062934 | 0.044942 | -0.011702 | -0.0069897 | 0.017534 | -0.022888 | 0.11444 | -0.19226 | 0.004578 | 0.045776 | 0.054932 | 0.009155 | 0.13733 | 0.16479 | -0.18768 | 122.0078 | -0.009155 | 122.1771 | 122.2046 | -0.07782 | 122.0123 | 0.041199 | 0.16937 | 122.2092 | 122.3373 | 122.2458 | 122.3145 | 122.1771 | 122.3648 | 122.2549 | 122.0123 | 122.3145 | 122.1771 | 122.2549 | 122.2458 | 122.3648 | -0.31586 | -0.31128
858.5625 | 122.5433 | -122.1725 | 0.11902 | -0.23567 | 0.017116 | 0.006507 | 0.046437 | -0.01213 | -0.0084851 | 0.015825 | -0.068665 | 0.14191 | -0.24261 | -0.036621 | -0.022888 | 0.018311 | 0.073242 | 0.091553 | 0.17853 | -0.19684 | 121.9299 | 0.022888 | 122.1039 | 122.1359 | -0.14191 | 121.9757 | 0.059509 | 0.17395 | 122.2458 | 122.2641 | 122.1497 | 122.3145 | 122.1039 | 122.3511 | 122.1909 | 121.9757 | 122.3145 | 122.1039 | 122.1909 | 122.1497 | 122.3511 | -0.36163 | -0.31586
860.2656 | 122.4976 | -122.1634 | 0.14191 | -0.13649 | 0.017329 | 0.0024482 | 0.042592 | -0.010848 | -0.0082715 | 0.015825 | 0.054932 | 0.091553 | -0.16479 | 0.09613 | 0.11902 | 0.16937 | -0.14191 | 0.24261 | 0.12817 | -0.16937 | 121.9986 | -0.050354 | 122.2183 | 122.2595 | -0.022888 | 121.994 | -0.013733 | 0.21973 | 122.0215 | 122.406 | 122.2824 | 122.2549 | 122.2183 | 122.2916 | 122.3328 | 121.994 | 122.2549 | 122.2183 | 122.3328 | 122.2824 | 122.2916 | -0.3067 | -0.31128
861.9844 | 122.406 | -122.1909 | 0.17395 | -0.052567 | 0.018397 | 0.006507 | 0.049642 | -0.010207 | -0.0072033 | 0.016466 | 0.013733 | 0.10529 | -0.19684 | 0.022888 | 0.054932 | 0.086975 | -0.027466 | 0.13733 | 0.16022 | -0.18768 | 121.994 | -0.068664 | 122.2046 | 122.2137 | -0.11902 | 122.0032 | -0.013733 | 0.21057 | 122.1634 | 122.3282 | 122.2458 | 122.2961 | 122.2046 | 122.3511 | 122.2778 | 122.0032 | 122.2961 | 122.2046 | 122.2778 | 122.2458 | 122.3511 | -0.37079 | -0.36163
863.6719 | 122.438 | -122.2183 | 0.14191 | -0.14412 | 0.017116 | 0.006507 | 0.048146 | -0.008498 | -0.0093395 | 0.018389 | -0.004578 | 0.10529 | -0.21057 | 0.018311 | 0.036621 | 0.082397 | -0.013733 | 0.1236 | 0.17853 | -0.18768 | 122.0078 | -0.036621 | 122.2137 | 122.2366 | -0.10529 | 122.0306 | 0.036621 | 0.20599 | 122.2046 | 122.3419 | 122.2549 | 122.3236 | 122.2137 | 122.3969 | 122.3007 | 122.0306 | 122.3236 | 122.2137 | 122.3007 | 122.2549 | 122.3969 | -0.35248 | -0.32959
865.3594 | 122.3969 | -122.2229 | 0.17395 | -0.098343 | 0.017543 | 0.0077888 | 0.047933 | -0.010848 | -0.0093395 | 0.018389 | 0.004578 | 0.11902 | -0.20599 | 0.022888 | 0.050354 | 0.068665 | -0.013733 | 0.13733 | 0.16937 | -0.1831 | 122.0169 | -0.054931 | 122.2275 | 122.2458 | -0.1236 | 122.0398 | -0.004577 | 0.21057 | 122.2092 | 122.3602 | 122.2733 | 122.3419 | 122.2275 | 122.3923 | 122.2916 | 122.0398 | 122.3419 | 122.2275 | 122.2916 | 122.2733 | 122.3923 | -0.37994 | -0.35706
867.0781 | 122.493 | -122.1954 | 0.11902 | -0.075455 | 0.017756 | 0.0015936 | 0.038106 | -0.010421 | -0.0054943 | 0.018602 | 0.054932 | 0.10529 | -0.16022 | 0.082397 | 0.13733 | 0.1831 | -0.14648 | 0.26093 | 0.15564 | -0.16022 | 122.0352 | -0.013733 | 122.2504 | 122.2778 | 0.01831 | 122.0352 | 0.036621 | 0.21515 | 122.049 | 122.4564 | 122.3328 | 122.3007 | 122.2504 | 122.3511 | 122.3785 | 122.0352 | 122.3007 | 122.2504 | 122.3785 | 122.3328 | 122.3511 | -0.27924 | -0.27924
868.7812 | 122.4197 | -122.2183 | 0.14648 | 0.20683 | 0.015834 | 0.006507 | 0.046437 | -0.0093524 | -0.0089123 | 0.016893 | 0.07782 | 0.082397 | -0.15106 | 0.073242 | 0.11902 | 0.17395 | -0.18768 | 0.21057 | 0.13733 | -0.14648 | 122.0673 | -0.064087 | 122.2961 | 122.2916 | -0.027465 | 122.0718 | -0.009155 | 0.22888 | 122.0306 | 122.4289 | 122.3373 | 122.3007 | 122.2961 | 122.3557 | 122.3923 | 122.0718 | 122.3007 | 122.2961 | 122.3923 | 122.3373 | 122.3557 | -0.29755 | -0.29297
870.4531 | 122.4106 | -122.2137 | 0.16479 | 0.22209 | 0.016902 | 0.009925 | 0.046651 | -0.0097796 | -0.0067761 | 0.016893 | 0.064087 | 0.059509 | -0.15564 | 0.068665 | 0.1236 | 0.16937 | -0.17395 | 0.20142 | 0.14191 | -0.15106 | 122.0581 | -0.10529 | 122.2778 | 122.2824 | -0.041199 | 122.0627 | -0.022888 | 0.21973 | 122.0398 | 122.4152 | 122.3373 | 122.2733 | 122.2778 | 122.3557 | 122.3831 | 122.0627 | 122.2733 | 122.2778 | 122.3831 | 122.3373 | 122.3557 | -0.32044 | -0.31586
872.125 | 122.5113 | -122.2092 | 0.13275 | -0.17464 | 0.018184 | 9.8166e-05 | 0.044515 | -0.011061 | -0.0061353 | 0.018389 | 0.036621 | 0.073242 | -0.16479 | 0.073242 | 0.11902 | 0.15564 | -0.086975 | 0.2243 | 0.14648 | -0.16022 | 122.0444 | -0.059509 | 122.2458 | 122.2824 | -0.013732 | 122.0489 | 0.013733 | 0.20142 | 122.1222 | 122.4335 | 122.3282 | 122.2824 | 122.2458 | 122.3557 | 122.3648 | 122.0489 | 122.2824 | 122.2458 | 122.3648 | 122.3282 | 122.3557 | -0.29755 | -0.29297
873.7969 | 122.4884 | -122.1909 | 0.14191 | 0.077133 | 0.017329 | 0.0086432 | 0.042592 | -0.011916 | -0.0059217 | 0.017107 | 0.018311 | 0.11444 | -0.17853 | 0.022888 | 0.054932 | 0.11444 | -0.10986 | 0.14648 | 0.14648 | -0.1831 | 122.0123 | -0.027466 | 122.2092 | 122.2137 | -0.086975 | 122.0078 | 0.004577 | 0.19684 | 122.081 | 122.3373 | 122.2458 | 122.3053 | 122.2092 | 122.3373 | 122.3053 | 122.0078 | 122.3053 | 122.2092 | 122.3053 | 122.2458 | 122.3373 | -0.32044 | -0.32501
875.4688 | 122.438 | -122.2137 | 0.15564 | 0.10765 | 0.017116 | 0.0071478 | 0.04601 | -0.011489 | -0.0084851 | 0.017534 | 0.041199 | 0.068665 | -0.17395 | 0.064087 | 0.10071 | 0.15564 | -0.16937 | 0.19684 | 0.13275 | -0.15564 | 122.0398 | -0.086975 | 122.2549 | 122.2778 | -0.054932 | 122.0581 | -0.022889 | 0.21515 | 122.0444 | 122.4106 | 122.3145 | 122.2824 | 122.2549 | 122.3465 | 122.3694 | 122.0581 | 122.2824 | 122.2549 | 122.3694 | 122.3145 | 122.3465 | -0.32959 | -0.31128
877.1406 | 122.4884 | -122.1909 | 0.16479 | 0.054245 | 0.017756 | 0.011634 | 0.049215 | -0.010848 | -0.0097669 | 0.018389 | -0.064087 | 0.13733 | -0.21515 | -0.059509 | -0.036621 | 0 | 0.032043 | 0.027466 | 0.16937 | -0.19226 | 121.9757 | -0.027466 | 122.1268 | 122.1313 | -0.20142 | 121.9986 | 0.004578 | 0.15106 | 122.2229 | 122.2183 | 122.1542 | 122.3282 | 122.1268 | 122.3602 | 122.1909 | 121.9986 | 122.3282 | 122.1268 | 122.1909 | 122.1542 | 122.3602 | -0.37994 | -0.35706
878.8594 | 122.438 | -122.2092 | 0.15106 | 0.1992 | 0.01797 | 0.0069342 | 0.04836 | -0.012557 | -0.0080579 | 0.019243 | -0.013733 | 0.11902 | -0.20142 | 0.004578 | 0.045776 | 0.10529 | -0.10529 | 0.14648 | 0.15106 | -0.1831 | 122.0078 | -0.032043 | 122.1954 | 122.2137 | -0.10529 | 122.0261 | 0 | 0.18768 | 122.1039 | 122.3557 | 122.2549 | 122.3282 | 122.1954 | 122.3602 | 122.3145 | 122.0261 | 122.3282 | 122.1954 | 122.3145 | 122.2549 | 122.3602 | -0.35248 | -0.33417
880.5625 | 122.4701 | -122.2137 | 0.16022 | 0.10002 | 0.016475 | 0.0069342 | 0.047506 | -0.010848 | -0.0074169 | 0.01668 | -0.082397 | 0.11902 | -0.22888 | -0.068665 | -0.036621 | 0.018311 | 0.032043 | 0.027466 | 0.16479 | -0.18768 | 121.9849 | -0.041198 | 122.1313 | 122.1451 | -0.19684 | 122.0261 | 0.004578 | 0.14649 | 122.2458 | 122.2412 | 122.1771 | 122.3328 | 122.1313 | 122.3785 | 122.2321 | 122.0261 | 122.3328 | 122.1313 | 122.2321 | 122.1771 | 122.3785 | -0.3891 | -0.3479
882.2344 | 122.4564 | -122.2275 | 0.17395 | -0.01442 | 0.018825 | 0.0045844 | 0.045797 | -0.009566 | -0.0086987 | 0.016466 | -0.013733 | 0.10986 | -0.19226 | -0.018311 | 0.018311 | 0.045776 | 0.004578 | 0.086975 | 0.16937 | -0.20142 | 122.0352 | -0.064087 | 122.2137 | 122.2092 | -0.15564 | 122.0261 | -0.004577 | 0.17853 | 122.2321 | 122.3145 | 122.2458 | 122.3373 | 122.2137 | 122.3969 | 122.2733 | 122.0261 | 122.3373 | 122.2137 | 122.2733 | 122.2458 | 122.3969 | -0.36621 | -0.37537
883.9688 | 122.5662 | -122.2 | 0.11444 | 0.031357 | 0.016261 | 0.0071478 | 0.038747 | -0.011275 | -0.0067761 | 0.018602 | -0.032043 | 0.091553 | -0.18768 | 0.004578 | 0.068665 | 0.10071 | -0.082397 | 0.14191 | 0.16022 | -0.16937 | 122.0123 | -0.022888 | 122.168 | 122.2046 | -0.045776 | 122.0306 | 0.045776 | 0.15564 | 122.1176 | 122.3419 | 122.2687 | 122.2916 | 122.168 | 122.3602 | 122.3007 | 122.0306 | 122.2916 | 122.168 | 122.3007 | 122.2687 | 122.3602 | -0.30212 | -0.28381
885.6406 | 122.5479 | -122.2 | 0.14191 | -0.052567 | 0.016688 | 0.0045844 | 0.039815 | -0.011916 | -0.0069897 | 0.016466 | 0.018311 | 0.09613 | -0.1831 | 0.059509 | 0.10986 | 0.16022 | -0.10071 | 0.21515 | 0.14191 | -0.16022 | 122.0169 | -0.045777 | 122.2183 | 122.2595 | -0.032044 | 122.0398 | 0 | 0.20142 | 122.0993 | 122.4152 | 122.3099 | 122.2961 | 122.2183 | 122.3419 | 122.3602 | 122.0398 | 122.2961 | 122.2183 | 122.3602 | 122.3099 | 122.3419 | -0.32501 | -0.30212
887.3281 | 122.5845 | -122.2046 | 0.13275 | -0.0067901 | 0.018397 | 0.0071478 | 0.04131 | -0.014052 | -0.0059217 | 0.01668 | -0.036621 | 0.09613 | -0.17395 | 0.009155 | 0.041199 | 0.10986 | -0.068665 | 0.14648 | 0.14191 | -0.17853 | 122.0306 | -0.036621 | 122.168 | 122.2137 | -0.091552 | 122.0261 | 0.009156 | 0.13733 | 122.1359 | 122.3511 | 122.2458 | 122.3007 | 122.168 | 122.3465 | 122.3145 | 122.0261 | 122.3007 | 122.168 | 122.3145 | 122.2458 | 122.3465 | -0.3067 | -0.31128
889 | 122.438 | -122.2229 | 0.16479 | 0.18394 | 0.016475 | 0.015266 | 0.046865 | -0.011916 | -0.0082715 | 0.016039 | 0.054932 | 0.068665 | -0.18768 | 0.086975 | 0.091553 | 0.16479 | -0.1831 | 0.21515 | 0.13733 | -0.15106 | 122.0352 | -0.09613 | 122.2778 | 122.3099 | -0.073242 | 122.0718 | -0.027466 | 0.24261 | 122.0398 | 122.438 | 122.3145 | 122.2916 | 122.2778 | 122.3602 | 122.3877 | 122.0718 | 122.2916 | 122.2778 | 122.3877 | 122.3145 | 122.3602 | -0.35248 | -0.31586
890.6719 | 122.4655 | -122.2183 | 0.16937 | 0.20683 | 0.017543 | 0.0077888 | 0.047506 | -0.012343 | -0.0061353 | 0.016893 | 0.045776 | 0.068665 | -0.16022 | 0.07782 | 0.10529 | 0.17395 | -0.17853 | 0.21057 | 0.14648 | -0.16479 | 122.0581 | -0.10071 | 122.2641 | 122.2961 | -0.064087 | 122.0535 | -0.022889 | 0.20599 | 122.0398 | 122.4289 | 122.3236 | 122.287 | 122.2641 | 122.3648 | 122.3923 | 122.0535 | 122.287 | 122.2641 | 122.3923 | 122.3236 | 122.3648 | -0.32959 | -0.33417
892.4062 | 122.5296 | -122.2046 | 0.15106 | 0.031357 | 0.015834 | 0.008216 | 0.042806 | -0.014479 | -0.0042127 | 0.016466 | 0.045776 | 0.09613 | -0.16479 | 0.11444 | 0.14191 | 0.19684 | -0.13733 | 0.25635 | 0.15564 | -0.16479 | 122.0398 | -0.054932 | 122.2504 | 122.319 | -0.009155 | 122.0398 | 0.004578 | 0.21057 | 122.0673 | 122.4609 | 122.3465 | 122.3007 | 122.2504 | 122.3602 | 122.4014 | 122.0398 | 122.3007 | 122.2504 | 122.4014 | 122.3465 | 122.3602 | -0.31586 | -0.31586
894.0938 | 122.5891 | -122.2 | 0.15106 | -0.22041 | 0.016688 | 0.0035162 | 0.045156 | -0.013198 | -0.010621 | 0.01668 | -0.036621 | 0.13275 | -0.20599 | -0.018311 | 0.022888 | 0.036621 | 0.054932 | 0.11444 | 0.19684 | -0.19226 | 121.994 | -0.018311 | 122.1634 | 122.1817 | -0.12817 | 122.0078 | 0.045776 | 0.16937 | 122.2549 | 122.3145 | 122.2229 | 122.3328 | 122.1634 | 122.3969 | 122.2366 | 122.0078 | 122.3328 | 122.1634 | 122.2366 | 122.2229 | 122.3969 | -0.35706 | -0.34332
895.7812 | 122.4884 | -122.2229 | 0.17853 | 0.038986 | 0.019038 | 0.0050116 | 0.049001 | -0.010421 | -0.0093395 | 0.016466 | -0.022888 | 0.1236 | -0.21973 | 0.050354 | 0.050354 | 0.045776 | 0.004578 | 0.13275 | 0.19226 | -0.16937 | 122.0032 | -0.054932 | 122.2 | 122.2733 | -0.12817 | 122.0535 | 0.013733 | 0.19684 | 122.2275 | 122.3557 | 122.2733 | 122.3465 | 122.2 | 122.4152 | 122.2687 | 122.0535 | 122.3465 | 122.2 | 122.2687 | 122.2733 | 122.4152 | -0.39826 | -0.3479
897.4844 | 122.5845 | -122.1725 | 0.16022 | -0.25093 | 0.016261 | 0.0071478 | 0.044942 | -0.011275 | -0.0084851 | 0.017321 | -0.082397 | 0.11902 | -0.23346 | -0.032043 | -0.009155 | 0.022888 | 0.09613 | 0.068665 | 0.20142 | -0.16022 | 121.9391 | -0.041198 | 122.0901 | 122.1405 | -0.16937 | 122.0123 | 0.041199 | 0.15106 | 122.2687 | 122.2412 | 122.1634 | 122.2916 | 122.0901 | 122.374 | 122.1954 | 122.0123 | 122.2916 | 122.0901 | 122.1954 | 122.1634 | 122.374 | -0.39368 | -0.32043
899.2031 | 122.6212 | -122.1771 | 0.16937 | -0.20515 | 0.016475 | 0.0054388 | 0.044942 | -0.011061 | -0.0074169 | 0.018389 | -0.07782 | 0.11444 | -0.20599 | -0.004578 | 0.004578 | 0.004578 | 0.07782 | 0.07782 | 0.2243 | -0.16937 | 121.9711 | -0.054932 | 122.0993 | 122.1725 | -0.16479 | 122.0078 | 0.054931 | 0.12817 | 122.2549 | 122.2549 | 122.1817 | 122.2916 | 122.0993 | 122.4014 | 122.1817 | 122.0078 | 122.2916 | 122.0993 | 122.1817 | 122.1817 | 122.4014 | -0.37537 | -0.33875
900.8906 | 122.5708 | -122.1909 | 0.16022 | -0.21278 | 0.018397 | 0.0058662 | 0.044301 | -0.0091388 | -0.0072033 | 0.01668 | 0.032043 | 0.10986 | -0.19226 | 0.059509 | 0.10529 | 0.1236 | -0.022888 | 0.1831 | 0.17853 | -0.14648 | 121.9986 | -0.050354 | 122.2229 | 122.2504 | -0.054931 | 122.0444 | 0.018311 | 0.2243 | 122.168 | 122.374 | 122.2961 | 122.3007 | 122.2229 | 122.3694 | 122.3145 | 122.0444 | 122.3007 | 122.2229 | 122.3145 | 122.2961 | 122.3694 | -0.35248 | -0.3067
902.625 | 122.58 | -122.1954 | 0.16937 | -0.15938 | 0.018184 | 0.009925 | 0.046437 | -0.010848 | -0.010621 | 0.016466 | -0.045776 | 0.13275 | -0.21515 | 0.009155 | 0.022888 | 0.041199 | 0.050354 | 0.10071 | 0.20142 | -0.19684 | 121.9803 | -0.036622 | 122.1497 | 122.2046 | -0.14649 | 121.9986 | 0.032043 | 0.16937 | 122.2458 | 122.2961 | 122.2183 | 122.3282 | 122.1497 | 122.3969 | 122.2366 | 121.9986 | 122.3282 | 122.1497 | 122.2366 | 122.2183 | 122.3969 | -0.38452 | -0.36621
904.3281 | 122.4976 | -122.2046 | 0.18768 | 0.077133 | 0.019679 | 0.009284 | 0.049001 | -0.0099934 | -0.010621 | 0.017962 | -0.064087 | 0.11902 | -0.21057 | -0.045776 | -0.013733 | 0.018311 | 0.036621 | 0.032043 | 0.20599 | -0.16937 | 121.994 | -0.068664 | 122.1405 | 122.1588 | -0.20142 | 122.0352 | 0.018311 | 0.14648 | 122.2412 | 122.2366 | 122.1909 | 122.3236 | 122.1405 | 122.4106 | 122.2229 | 122.0352 | 122.3236 | 122.1405 | 122.2229 | 122.1909 | 122.4106 | -0.39825 | -0.35706
906.0312 | 122.5433 | -122.1954 | 0.15564 | 0.092392 | 0.017543 | 0.01142 | 0.040242 | -0.01213 | -0.0057079 | 0.017748 | 0.013733 | 0.09613 | -0.1831 | 0.027466 | 0.073242 | 0.10986 | -0.091553 | 0.14191 | 0.1831 | -0.16937 | 122.0123 | -0.05951 | 122.2092 | 122.2229 | -0.082398 | 122.0261 | 0.027465 | 0.19684 | 122.1039 | 122.3373 | 122.2687 | 122.2916 | 122.2092 | 122.3785 | 122.3053 | 122.0261 | 122.2916 | 122.2092 | 122.3053 | 122.2687 | 122.3785 | -0.33874 | -0.32501
907.7344 | 122.5845 | -122.1817 | 0.16937 | -0.0067901 | 0.019465 | 0.002021 | 0.041951 | -0.012557 | -0.0078443 | 0.015398 | 0 | 0.10986 | -0.17395 | 0.054932 | 0.09613 | 0.13733 | -0.091553 | 0.17853 | 0.16479 | -0.14191 | 122.0078 | -0.05951 | 122.1817 | 122.2366 | -0.073243 | 122.0398 | -0.004578 | 0.17395 | 122.0901 | 122.3602 | 122.2778 | 122.2916 | 122.1817 | 122.3465 | 122.319 | 122.0398 | 122.2916 | 122.1817 | 122.319 | 122.2778 | 122.3465 | -0.34332 | -0.31128
909.4688 | 122.5159 | -122.2504 | 0.1831 | 0.084762 | 0.01797 | 0.0071478 | 0.048787 | -0.011702 | -0.0095531 | 0.016253 | -0.059509 | 0.14191 | -0.2243 | -0.068665 | -0.027466 | 0.013733 | 0.027466 | 0.045776 | 0.21973 | -0.16022 | 122.0261 | -0.041198 | 122.1909 | 122.1817 | -0.21057 | 122.0901 | 0.036622 | 0.16479 | 122.2778 | 122.2961 | 122.2229 | 122.3923 | 122.1909 | 122.4701 | 122.2641 | 122.0901 | 122.3923 | 122.1909 | 122.2641 | 122.2229 | 122.4701 | -0.40741 | -0.34332
911.1719 | 122.5479 | -122.2137 | 0.16479 | -0.18227 | 0.014552 | 0.0073614 | 0.043019 | -0.011275 | -0.0089123 | 0.016253 | 0.045776 | 0.086975 | -0.16937 | 0.091553 | 0.10529 | 0.16937 | -0.068665 | 0.22888 | 0.15106 | -0.14191 | 122.0444 | -0.07782 | 122.2595 | 122.3053 | -0.059509 | 122.0718 | -0.013733 | 0.21515 | 122.1451 | 122.4426 | 122.319 | 122.3007 | 122.2595 | 122.3648 | 122.3831 | 122.0718 | 122.3007 | 122.2595 | 122.3831 | 122.319 | 122.3648 | -0.33417 | -0.3067
912.8594 | 122.5891 | -122.1863 | 0.15564 | 0.0084684 | 0.016902 | 0.0090704 | 0.041951 | -0.011702 | -0.0065625 | 0.018602 | -0.032043 | 0.10071 | -0.18768 | 0.032043 | 0.059509 | 0.11444 | -0.064087 | 0.16022 | 0.16937 | -0.14191 | 121.9986 | -0.054932 | 122.1542 | 122.2183 | -0.096131 | 122.0444 | 0.013733 | 0.15564 | 122.1222 | 122.3465 | 122.2458 | 122.287 | 122.1542 | 122.3557 | 122.3007 | 122.0444 | 122.287 | 122.1542 | 122.3007 | 122.2458 | 122.3557 | -0.34332 | -0.29755
914.5312 | 122.5937 | -122.2137 | 0.15564 | -0.0067901 | 0.018397 | 0.011848 | 0.042165 | -0.011275 | -0.0059217 | 0.016893 | -0.022888 | 0.10071 | -0.20142 | 0.041199 | 0.073242 | 0.12817 | -0.068665 | 0.16022 | 0.16937 | -0.15106 | 122.0123 | -0.054932 | 122.1909 | 122.2549 | -0.082398 | 122.0627 | 0.013733 | 0.17853 | 122.1451 | 122.374 | 122.287 | 122.3145 | 122.1909 | 122.3831 | 122.3419 | 122.0627 | 122.3145 | 122.1909 | 122.3419 | 122.287 | 122.3831 | -0.35706 | -0.3067
916.2031 | 122.5296 | -122.2458 | 0.17395 | 0.1458 | 0.018184 | 0.0071478 | 0.045156 | -0.011275 | -0.0086987 | 0.017962 | 0.027466 | 0.091553 | -0.17853 | 0.054932 | 0.059509 | 0.12817 | -0.10071 | 0.16937 | 0.17395 | -0.14191 | 122.0673 | -0.082397 | 122.2733 | 122.3007 | -0.11444 | 122.1039 | 0 | 0.20599 | 122.1451 | 122.4152 | 122.3053 | 122.3373 | 122.2733 | 122.4197 | 122.374 | 122.1039 | 122.3373 | 122.2733 | 122.374 | 122.3053 | 122.4197 | -0.35248 | -0.31586
917.875 | 122.4655 | -122.2641 | 0.17853 | 0.21446 | 0.019465 | 0.012061 | 0.047078 | -0.013411 | -0.0078443 | 0.017748 | 0.027466 | 0.10986 | -0.19226 | 0.082397 | 0.086975 | 0.13733 | -0.13733 | 0.17853 | 0.16479 | -0.14191 | 122.0718 | -0.068665 | 122.2916 | 122.3465 | -0.091553 | 122.1222 | -0.013733 | 0.21973 | 122.1268 | 122.4426 | 122.3511 | 122.374 | 122.2916 | 122.4289 | 122.4014 | 122.1222 | 122.374 | 122.2916 | 122.4014 | 122.3511 | 122.4289 | -0.37079 | -0.32044
919.5469 | 122.4747 | -122.2504 | 0.20599 | 0.1458 | 0.018184 | 0.0060798 | 0.047933 | -0.011275 | -0.0093395 | 0.019457 | 0.027466 | 0.07782 | -0.1831 | 0.091553 | 0.091553 | 0.15106 | -0.13733 | 0.1831 | 0.15564 | -0.14648 | 122.0673 | -0.12817 | 122.2778 | 122.3419 | -0.11444 | 122.1039 | -0.050354 | 0.21057 | 122.113 | 122.4335 | 122.3419 | 122.3282 | 122.2778 | 122.406 | 122.4014 | 122.1039 | 122.3282 | 122.2778 | 122.4014 | 122.3419 | 122.406 | -0.3891 | -0.35248
921.2188 | 122.5204 | -122.2458 | 0.17853 | -0.01442 | 0.018611 | 0.0054388 | 0.049855 | -0.011702 | -0.0065625 | 0.01668 | -0.068665 | 0.10529 | -0.21973 | -0.064087 | -0.036621 | 0.013733 | 0.032043 | 0.027466 | 0.19226 | -0.17395 | 122.0261 | -0.073242 | 122.1771 | 122.1817 | -0.21515 | 122.0718 | 0.013733 | 0.15106 | 122.2778 | 122.2733 | 122.2092 | 122.3511 | 122.1771 | 122.4381 | 122.2595 | 122.0718 | 122.3511 | 122.1771 | 122.2595 | 122.2092 | 122.4381 | -0.39826 | -0.35248
922.9375 | 122.5754 | -122.2275 | 0.17853 | -0.17464 | 0.017116 | 0.009925 | 0.04836 | -0.011275 | -0.0093395 | 0.01903 | -0.050354 | 0.12817 | -0.21973 | -0.004578 | 0.032043 | 0.036621 | 0.050354 | 0.11444 | 0.19684 | -0.16937 | 122.0078 | -0.050354 | 122.1771 | 122.2229 | -0.14648 | 122.0581 | 0.01831 | 0.16937 | 122.2778 | 122.3419 | 122.2595 | 122.3557 | 122.1771 | 122.4243 | 122.2641 | 122.0581 | 122.3557 | 122.1771 | 122.2641 | 122.2595 | 122.4243 | -0.39826 | -0.3479
924.6094 | 122.5571 | -122.2458 | 0.16022 | -0.21278 | 0.018184 | 0.009284 | 0.04601 | -0.010207 | -0.010408 | 0.017107 | -0.041199 | 0.11444 | -0.2243 | 0.013733 | 0.036621 | 0.054932 | 0.045776 | 0.1236 | 0.20599 | -0.16479 | 122.0215 | -0.045776 | 122.2046 | 122.2595 | -0.1236 | 122.081 | 0.045777 | 0.18311 | 122.2916 | 122.3694 | 122.2824 | 122.3602 | 122.2046 | 122.4518 | 122.3007 | 122.081 | 122.3602 | 122.2046 | 122.3007 | 122.2824 | 122.4518 | -0.38452 | -0.32501
926.2812 | 122.6532 | -122.2092 | 0.17395 | -0.28145 | 0.017543 | 0.0073614 | 0.043019 | -0.01277 | -0.010408 | 0.018175 | -0.082397 | 0.11902 | -0.22888 | -0.032043 | 0.013733 | 0.027466 | 0.086975 | 0.086975 | 0.21515 | -0.17853 | 121.9803 | -0.054931 | 122.1268 | 122.1771 | -0.16022 | 122.0306 | 0.041199 | 0.14649 | 122.2961 | 122.2961 | 122.2229 | 122.3282 | 122.1268 | 122.4243 | 122.2366 | 122.0306 | 122.3282 | 122.1268 | 122.2366 | 122.2229 | 122.4243 | -0.40283 | -0.35248
927.9531 | 122.6395 | -122.2046 | 0.17395 | -0.23567 | 0.018825 | 0.0073614 | 0.044301 | -0.011061 | -0.0059217 | 0.018175 | -0.054932 | 0.1236 | -0.22888 | -0.009155 | 0.013733 | 0.036621 | 0.10529 | 0.07782 | 0.2243 | -0.17853 | 121.9757 | -0.050354 | 122.1497 | 122.1954 | -0.16022 | 122.0261 | 0.050354 | 0.17395 | 122.3099 | 122.2824 | 122.2183 | 122.3282 | 122.1497 | 122.4289 | 122.2412 | 122.0261 | 122.3282 | 122.1497 | 122.2412 | 122.2183 | 122.4289 | -0.40283 | -0.35248
929.625 | 122.6166 | -122.2275 | 0.17395 | -0.27382 | 0.016902 | 0.0069342 | 0.043874 | -0.011489 | -0.0093395 | 0.016893 | 0.009155 | 0.10529 | -0.17853 | 0.045776 | 0.073242 | 0.091553 | 0.022888 | 0.16022 | 0.20142 | -0.15564 | 122.049 | -0.068664 | 122.2366 | 122.2733 | -0.10071 | 122.0718 | 0.027466 | 0.18768 | 122.2504 | 122.3877 | 122.3007 | 122.3328 | 122.2366 | 122.4289 | 122.319 | 122.0718 | 122.3328 | 122.2366 | 122.319 | 122.3007 | 122.4289 | -0.35248 | -0.32959
931.2969 | 122.5845 | -122.2549 | 0.16479 | -0.067826 | 0.016902 | 0.0050116 | 0.041951 | -0.011275 | -0.0059217 | 0.018389 | 0.013733 | 0.091553 | -0.17853 | 0.09613 | 0.12817 | 0.16479 | -0.091553 | 0.21973 | 0.16937 | -0.13275 | 122.0764 | -0.073242 | 122.2687 | 122.3511 | -0.036621 | 122.1222 | 0.004578 | 0.19226 | 122.1634 | 122.4747 | 122.3831 | 122.3465 | 122.2687 | 122.4243 | 122.4197 | 122.1222 | 122.3465 | 122.2687 | 122.4197 | 122.3831 | 122.4243 | -0.34332 | -0.29755
933.0156 | 122.6349 | -122.2092 | 0.17853 | -0.25856 | 0.016902 | 0.0050116 | 0.045369 | -0.015761 | -0.0078443 | 0.017321 | -0.068665 | 0.13733 | -0.21515 | 0 | -0.009155 | 0.018311 | 0.10986 | 0.09613 | 0.20599 | -0.16022 | 121.994 | -0.041199 | 122.1405 | 122.2092 | -0.18768 | 122.0489 | 0.027466 | 0.14648 | 122.319 | 122.3053 | 122.2 | 122.3465 | 122.1405 | 122.4152 | 122.2275 | 122.0489 | 122.3465 | 122.1405 | 122.2275 | 122.2 | 122.4152 | -0.39368 | -0.33874
934.6875 | 122.6166 | -122.2 | 0.16937 | -0.18227 | 0.017116 | 0.0067206 | 0.046865 | -0.010634 | -0.0089123 | 0.017107 | -0.054932 | 0.13733 | -0.24719 | -0.009155 | 0.013733 | 0.041199 | 0.082397 | 0.10529 | 0.2243 | -0.15564 | 121.9528 | -0.032044 | 122.1451 | 122.1909 | -0.15564 | 122.0444 | 0.054931 | 0.19226 | 122.2824 | 122.3053 | 122.2137 | 122.3373 | 122.1451 | 122.4243 | 122.2412 | 122.0444 | 122.3373 | 122.1451 | 122.2412 | 122.2137 | 122.4243 | -0.41656 | -0.32501
936.3594 | 122.644 | -122.2275 | 0.16937 | -0.22041 | 0.016047 | 0.011207 | 0.047078 | -0.010207 | -0.0084851 | 0.016466 | -0.073242 | 0.12817 | -0.21515 | -0.004578 | 0 | 0.027466 | 0.11902 | 0.09613 | 0.2243 | -0.16937 | 122.0123 | -0.041199 | 122.1542 | 122.2229 | -0.16937 | 122.0581 | 0.054931 | 0.14191 | 122.3465 | 122.3236 | 122.2275 | 122.3557 | 122.1542 | 122.4518 | 122.2549 | 122.0581 | 122.3557 | 122.1542 | 122.2549 | 122.2275 | 122.4518 | -0.38452 | -0.33875
938.0469 | 122.5754 | -122.2321 | 0.16937 | -0.13649 | 0.018184 | 0.0052252 | 0.040029 | -0.01277 | -0.0067761 | 0.017962 | 0.045776 | 0.07782 | -0.16022 | 0.12817 | 0.15106 | 0.18768 | -0.09613 | 0.27008 | 0.1831 | -0.12817 | 122.0718 | -0.091553 | 122.2778 | 122.3602 | -0.018311 | 122.1039 | 0.013732 | 0.20599 | 122.1359 | 122.5021 | 122.3831 | 122.3099 | 122.2778 | 122.4152 | 122.4197 | 122.1039 | 122.3099 | 122.2778 | 122.4197 | 122.3831 | 122.4152 | -0.32959 | -0.29755
939.7188 | 122.6074 | -122.2092 | 0.14191 | -0.037308 | 0.017756 | 0.0062934 | 0.043447 | -0.013625 | -0.0069897 | 0.01903 | 0.004578 | 0.10986 | -0.1831 | 0.082397 | 0.09613 | 0.14648 | -0.064087 | 0.21057 | 0.16937 | -0.14191 | 122.0261 | -0.032044 | 122.2137 | 122.2916 | -0.045777 | 122.0673 | 0.027466 | 0.18768 | 122.1451 | 122.4197 | 122.3053 | 122.319 | 122.2137 | 122.3785 | 122.3557 | 122.0673 | 122.319 | 122.2137 | 122.3557 | 122.3053 | 122.3785 | -0.32501 | -0.28381
941.4062 | 122.5021 | -122.2778 | 0.21057 | 0.15343 | 0.016902 | 0.0058662 | 0.045583 | -0.010634 | -0.0067761 | 0.01668 | 0.064087 | 0.073242 | -0.16937 | 0.10529 | 0.10071 | 0.16479 | -0.13733 | 0.19226 | 0.18768 | -0.1236 | 122.1085 | -0.13733 | 122.3419 | 122.3831 | -0.10986 | 122.1542 | -0.022888 | 0.23346 | 122.1405 | 122.4701 | 122.3785 | 122.3511 | 122.3419 | 122.4655 | 122.4426 | 122.1542 | 122.3511 | 122.3419 | 122.4426 | 122.3785 | 122.4655 | -0.37994 | -0.33417
943.0781 | 122.5479 | -122.2458 | 0.20599 | 0.12291 | 0.019252 | 0.0088568 | 0.05071 | -0.011702 | -0.0084851 | 0.018602 | -0.086975 | 0.13275 | -0.2243 | -0.009155 | -0.018311 | 0.032043 | 0.045776 | 0.041199 | 0.24261 | -0.16022 | 122.0215 | -0.073243 | 122.1588 | 122.2366 | -0.22431 | 122.0856 | 0.036621 | 0.13733 | 122.2916 | 122.287 | 122.2275 | 122.3785 | 122.1588 | 122.4884 | 122.2778 | 122.0856 | 122.3785 | 122.1588 | 122.2778 | 122.2275 | 122.4884 | -0.4303 | -0.36621
944.75 | 122.5204 | -122.2458 | 0.18768 | 0.1458 | 0.019252 | 0.0080024 | 0.041951 | -0.010848 | -0.0080579 | 0.017748 | 0.022888 | 0.086975 | -0.17853 | 0.09613 | 0.10071 | 0.13275 | -0.10986 | 0.17395 | 0.16479 | -0.13275 | 122.0673 | -0.10071 | 122.2687 | 122.3419 | -0.086975 | 122.113 | -0.022888 | 0.20142 | 122.1359 | 122.4197 | 122.3465 | 122.3328 | 122.2687 | 122.4106 | 122.3785 | 122.113 | 122.3328 | 122.2687 | 122.3785 | 122.3465 | 122.4106 | -0.36621 | -0.32043
946.4844 | 122.5754 | -122.2549 | 0.19684 | -0.19753 | 0.018397 | 0.011848 | 0.047506 | -0.012343 | -0.0089123 | 0.015184 | -0.041199 | 0.12817 | -0.24261 | 0.041199 | 0.036621 | 0.068665 | 0.041199 | 0.13275 | 0.21973 | -0.14648 | 122.0123 | -0.068664 | 122.2137 | 122.2961 | -0.16022 | 122.1085 | 0.022889 | 0.20142 | 122.2961 | 122.3877 | 122.2916 | 122.3831 | 122.2137 | 122.4747 | 122.3236 | 122.1085 | 122.3831 | 122.2137 | 122.3236 | 122.2916 | 122.4747 | -0.43945 | -0.34332
948.1719 | 122.5479 | -122.2549 | 0.21057 | 0.00083945 | 0.019038 | 0.010779 | 0.049642 | -0.011275 | -0.0082715 | 0.018602 | -0.050354 | 0.12817 | -0.21057 | -0.004578 | -0.009155 | 0.013733 | 0.041199 | 0.068665 | 0.21515 | -0.15106 | 122.0444 | -0.082397 | 122.2046 | 122.2504 | -0.21973 | 122.1039 | 0.004578 | 0.16022 | 122.2961 | 122.3236 | 122.2458 | 122.3831 | 122.2046 | 122.4701 | 122.2687 | 122.1039 | 122.3831 | 122.2046 | 122.2687 | 122.2458 | 122.4701 | -0.42114 | -0.36163
949.875 | 122.6028 | -122.2458 | 0.17853 | -0.17464 | 0.019465 | 0.0080024 | 0.046651 | -0.010421 | -0.0089123 | 0.018602 | -0.045776 | 0.12817 | -0.21057 | 0.022888 | 0.032043 | 0.045776 | 0.068665 | 0.1236 | 0.21057 | -0.15106 | 122.0352 | -0.050354 | 122.2 | 122.2687 | -0.14648 | 122.0947 | 0.032043 | 0.1648 | 122.3145 | 122.3694 | 122.2778 | 122.374 | 122.2 | 122.4564 | 122.2916 | 122.0947 | 122.374 | 122.2 | 122.2916 | 122.2778 | 122.4564 | -0.3891 | -0.32959
951.5625 | 122.5845 | -122.2549 | 0.17395 | -0.20515 | 0.016047 | 0.0043708 | 0.039815 | -0.01213 | -0.0059217 | 0.015398 | 0.041199 | 0.082397 | -0.17853 | 0.11902 | 0.15106 | 0.16937 | -0.091553 | 0.24719 | 0.18768 | -0.14648 | 122.0764 | -0.091553 | 122.2961 | 122.374 | -0.022888 | 122.1085 | 0.013733 | 0.21973 | 122.1634 | 122.5021 | 122.406 | 122.3373 | 122.2961 | 122.4426 | 122.4243 | 122.1085 | 122.3373 | 122.2961 | 122.4243 | 122.406 | 122.4426 | -0.35248 | -0.32043
953.25 | 122.6578 | -122.2412 | 0.16022 | -0.28145 | 0.016261 | 0.0050116 | 0.044942 | -0.011275 | -0.0084851 | 0.016466 | -0.064087 | 0.14191 | -0.21973 | -0.022888 | 0 | 0.009155 | 0.09613 | 0.09613 | 0.23346 | -0.1831 | 122.0215 | -0.01831 | 122.1771 | 122.2183 | -0.16022 | 122.0581 | 0.073242 | 0.15564 | 122.3373 | 122.3373 | 122.2412 | 122.3831 | 122.1771 | 122.4747 | 122.2504 | 122.0581 | 122.3831 | 122.1771 | 122.2504 | 122.2412 | 122.4747 | -0.37994 | -0.34332
954.9844 | 122.6578 | -122.2458 | 0.15564 | -0.22804 | 0.018397 | 0.0033026 | 0.042806 | -0.01277 | -0.0099805 | 0.015398 | -0.082397 | 0.12817 | -0.21973 | -0.004578 | 0.004578 | 0.018311 | 0.10529 | 0.07782 | 0.2243 | -0.17395 | 122.0261 | -0.027466 | 122.1634 | 122.2412 | -0.15106 | 122.0718 | 0.068664 | 0.13733 | 122.3511 | 122.3236 | 122.2504 | 122.374 | 122.1634 | 122.4701 | 122.2641 | 122.0718 | 122.374 | 122.1634 | 122.2641 | 122.2504 | 122.4701 | -0.37537 | -0.32959
956.6562 | 122.612 | -122.2641 | 0.17395 | -0.14412 | 0.019038 | 0.0067206 | 0.042592 | -0.011916 | -0.0063489 | 0.014544 | 0.032043 | 0.10071 | -0.17853 | 0.10071 | 0.1236 | 0.14648 | -0.036621 | 0.21515 | 0.1831 | -0.12817 | 122.0856 | -0.073242 | 122.2961 | 122.3648 | -0.050354 | 122.1359 | 0.009155 | 0.21057 | 122.2275 | 122.4792 | 122.3877 | 122.3648 | 122.2961 | 122.4472 | 122.4106 | 122.1359 | 122.3648 | 122.2961 | 122.4106 | 122.3877 | 122.4472 | -0.35248 | -0.30212
958.3438 | 122.5937 | -122.2458 | 0.17853 | -0.1899 | 0.01797 | 0.0073614 | 0.041524 | -0.01213 | -0.0078443 | 0.017107 | 0.045776 | 0.082397 | -0.19226 | 0.10986 | 0.15106 | 0.16479 | -0.091553 | 0.25635 | 0.17395 | -0.12817 | 122.0535 | -0.096131 | 122.2916 | 122.3557 | -0.027466 | 122.1176 | -0.004578 | 0.23804 | 122.1542 | 122.5021 | 122.3969 | 122.3282 | 122.2916 | 122.4197 | 122.4106 | 122.1176 | 122.3282 | 122.2916 | 122.4106 | 122.3969 | 122.4197 | -0.37079 | -0.3067
960.0469 | 122.5662 | -122.2504 | 0.20142 | 0.1458 | 0.018825 | 0.010352 | 0.047933 | -0.010421 | -0.010194 | 0.020098 | -0.054932 | 0.13733 | -0.2243 | -0.004578 | 0.009155 | 0.045776 | 0.013733 | 0.059509 | 0.21057 | -0.15106 | 122.0261 | -0.064087 | 122.1954 | 122.2458 | -0.19226 | 122.0993 | 0.009155 | 0.16937 | 122.2641 | 122.3099 | 122.2595 | 122.3877 | 122.1954 | 122.4609 | 122.2961 | 122.0993 | 122.3877 | 122.1954 | 122.2961 | 122.2595 | 122.4609 | -0.42572 | -0.35248
961.7188 | 122.5433 | -122.2824 | 0.20142 | 0.023727 | 0.017329 | 0.0071478 | 0.047506 | -0.010421 | -0.0084851 | 0.016466 | -0.032043 | 0.14191 | -0.21057 | 0.004578 | -0.004578 | 0.032043 | 0.036621 | 0.064087 | 0.22888 | -0.15106 | 122.0718 | -0.059509 | 122.2504 | 122.287 | -0.20599 | 122.1313 | 0.027466 | 0.17853 | 122.319 | 122.3465 | 122.2778 | 122.4243 | 122.2504 | 122.5113 | 122.3145 | 122.1313 | 122.4243 | 122.2504 | 122.3145 | 122.2778 | 122.5113 | -0.41199 | -0.35248
963.3906 | 122.525 | -122.2733 | 0.19684 | 0.1992 | 0.018397 | 0.0056524 | 0.043874 | -0.010421 | -0.0097669 | 0.017321 | -0.032043 | 0.12817 | -0.21973 | 0.022888 | 0.050354 | 0.09613 | -0.064087 | 0.11902 | 0.1831 | -0.13733 | 122.0535 | -0.068664 | 122.2412 | 122.2961 | -0.14648 | 122.1359 | -0.013733 | 0.18768 | 122.2092 | 122.3923 | 122.3236 | 122.4014 | 122.2412 | 122.4564 | 122.3694 | 122.1359 | 122.4014 | 122.2412 | 122.3694 | 122.3236 | 122.4564 | -0.41657 | -0.33417
965.0781 | 122.5983 | -122.3007 | 0.17395 | -0.22041 | 0.017756 | 0.0045844 | 0.042165 | -0.011061 | -0.0084851 | 0.015612 | 0.041199 | 0.07782 | -0.19684 | 0.10986 | 0.14191 | 0.16937 | -0.091553 | 0.26093 | 0.19684 | -0.13275 | 122.1039 | -0.09613 | 122.3419 | 122.4106 | -0.032043 | 122.168 | 0.022888 | 0.23804 | 122.2092 | 122.5616 | 122.4426 | 122.3785 | 122.3419 | 122.4976 | 122.4701 | 122.168 | 122.3785 | 122.3419 | 122.4701 | 122.4426 | 122.4976 | -0.37079 | -0.3067
966.75 | 122.6212 | -122.2824 | 0.15106 | -0.15175 | 0.018184 | 0.0090704 | 0.041738 | -0.010848 | -0.0057079 | 0.014544 | 0.041199 | 0.10986 | -0.16479 | 0.086975 | 0.10071 | 0.13733 | -0.050354 | 0.22888 | 0.17853 | -0.14191 | 122.1176 | -0.041199 | 122.3236 | 122.3694 | -0.050354 | 122.1405 | 0.027466 | 0.20599 | 122.2321 | 122.5113 | 122.3831 | 122.3923 | 122.3236 | 122.4609 | 122.4197 | 122.1405 | 122.3923 | 122.3236 | 122.4197 | 122.3831 | 122.4609 | -0.31586 | -0.29297
968.4375 | 122.5754 | -122.3007 | 0.19226 | 0.13054 | 0.02032 | 0.008216 | 0.048574 | -0.010634 | -0.010621 | 0.018389 | -0.050354 | 0.13275 | -0.23804 | -0.027466 | 0 | 0.041199 | 0.018311 | 0.064087 | 0.21057 | -0.18768 | 122.0627 | -0.05951 | 122.2504 | 122.2733 | -0.19226 | 122.113 | 0.01831 | 0.18768 | 122.319 | 122.3648 | 122.3007 | 122.4335 | 122.2504 | 122.5113 | 122.3419 | 122.113 | 122.4335 | 122.2504 | 122.3419 | 122.3007 | 122.5113 | -0.4303 | -0.37994
970.1406 | 122.6578 | -122.3007 | 0.15106 | -0.25093 | 0.017329 | 0.0052252 | 0.044088 | -0.010848 | -0.0089123 | 0.017534 | -0.013733 | 0.11902 | -0.19684 | 0.013733 | 0.022888 | 0.050354 | 0.050354 | 0.13275 | 0.19684 | -0.17395 | 122.1039 | -0.032043 | 122.287 | 122.3145 | -0.12817 | 122.1268 | 0.045776 | 0.18311 | 122.3511 | 122.4335 | 122.3236 | 122.4197 | 122.287 | 122.4976 | 122.3511 | 122.1268 | 122.4197 | 122.287 | 122.3511 | 122.3236 | 122.4976 | -0.3479 | -0.32501
971.8594 | 122.5479 | -122.2916 | 0.20142 | 0.12291 | 0.016261 | 0.0052252 | 0.04366 | -0.012984 | -0.0076305 | 0.017107 | 0.036621 | 0.07782 | -0.16937 | 0.07782 | 0.10986 | 0.15564 | -0.14191 | 0.18768 | 0.16022 | -0.14648 | 122.1222 | -0.1236 | 122.3282 | 122.3694 | -0.091553 | 122.1451 | -0.041199 | 0.20599 | 122.1497 | 122.4792 | 122.4014 | 122.3694 | 122.3282 | 122.4518 | 122.4472 | 122.1451 | 122.3694 | 122.3282 | 122.4472 | 122.4014 | 122.4518 | -0.37079 | -0.3479
973.5312 | 122.5067 | -122.3145 | 0.20599 | 0.1992 | 0.018825 | 0.013984 | 0.045797 | -0.012557 | -0.0095531 | 0.017107 | 0.054932 | 0.086975 | -0.19226 | 0.091553 | 0.11444 | 0.16479 | -0.1831 | 0.20599 | 0.14191 | -0.14191 | 122.1222 | -0.11902 | 122.3694 | 122.406 | -0.091553 | 122.1725 | -0.064087 | 0.24719 | 122.1313 | 122.5204 | 122.4289 | 122.4014 | 122.3694 | 122.4564 | 122.4792 | 122.1725 | 122.4014 | 122.3694 | 122.4792 | 122.4289 | 122.4564 | -0.39826 | -0.3479
975.2344 | 122.5204 | -122.3007 | 0.18768 | 0.20683 | 0.016047 | 0.013557 | 0.043874 | -0.012343 | -0.0065625 | 0.018175 | 0.041199 | 0.086975 | -0.16937 | 0.082397 | 0.11444 | 0.16479 | -0.1831 | 0.21515 | 0.14648 | -0.1236 | 122.1313 | -0.10071 | 122.3419 | 122.3831 | -0.073242 | 122.1771 | -0.041199 | 0.21057 | 122.1176 | 122.5159 | 122.4152 | 122.3877 | 122.3419 | 122.4472 | 122.4655 | 122.1771 | 122.3877 | 122.3419 | 122.4655 | 122.4152 | 122.4472 | -0.35706 | -0.31128
976.9688 | 122.612 | -122.2961 | 0.16479 | -0.20515 | 0.017116 | 0.0060798 | 0.041738 | -0.013411 | -0.0061353 | 0.016039 | 0.041199 | 0.086975 | -0.17853 | 0.10529 | 0.14648 | 0.15564 | -0.10529 | 0.23346 | 0.16479 | -0.14648 | 122.1176 | -0.07782 | 122.3373 | 122.4014 | -0.018311 | 122.1497 | 0 | 0.21973 | 122.1909 | 122.5296 | 122.4426 | 122.3831 | 122.3373 | 122.4609 | 122.4518 | 122.1497 | 122.3831 | 122.3373 | 122.4518 | 122.4426 | 122.4609 | -0.34332 | -0.31128
978.6562 | 122.6212 | -122.287 | 0.16022 | -0.12886 | 0.015834 | 0.006507 | 0.042379 | -0.015548 | -0.0097669 | 0.015825 | 0.050354 | 0.086975 | -0.18768 | 0.11444 | 0.13733 | 0.16937 | -0.13275 | 0.23804 | 0.15106 | -0.15106 | 122.0993 | -0.073242 | 122.3373 | 122.4014 | -0.022888 | 122.1359 | -0.009155 | 0.23804 | 122.1542 | 122.525 | 122.4243 | 122.374 | 122.3373 | 122.438 | 122.4564 | 122.1359 | 122.374 | 122.3373 | 122.4564 | 122.4243 | 122.438 | -0.3479 | -0.31128
980.3281 | 122.6212 | -122.3007 | 0.15106 | -0.12123 | 0.016902 | 0.0073614 | 0.043019 | -0.013411 | -0.0084851 | 0.016466 | 0.054932 | 0.086975 | -0.16022 | 0.11444 | 0.14648 | 0.1831 | -0.13275 | 0.26093 | 0.16479 | -0.13733 | 122.1405 | -0.064087 | 122.3557 | 122.4152 | -0.004578 | 122.1634 | 0.013733 | 0.21515 | 122.168 | 122.5616 | 122.4472 | 122.3877 | 122.3557 | 122.4655 | 122.4838 | 122.1634 | 122.3877 | 122.3557 | 122.4838 | 122.4472 | 122.4655 | -0.31128 | -0.28839
982.0156 | 122.5479 | -122.3373 | 0.21057 | -0.060196 | 0.016475 | 0.0069342 | 0.049642 | -0.011275 | -0.0097669 | 0.016039 | 0.013733 | 0.12817 | -0.21057 | 0.041199 | 0.054932 | 0.073242 | -0.009155 | 0.14191 | 0.19226 | -0.17853 | 122.1268 | -0.082397 | 122.3511 | 122.3785 | -0.15564 | 122.1588 | -0.01831 | 0.2243 | 122.3282 | 122.4792 | 122.3923 | 122.4655 | 122.3511 | 122.5296 | 122.4106 | 122.1588 | 122.4655 | 122.3511 | 122.4106 | 122.3923 | 122.5296 | -0.42114 | -0.3891
983.6875 | 122.5388 | -122.3236 | 0.16479 | -0.052567 | 0.017116 | 0.0033026 | 0.048574 | -0.006789 | -0.010835 | 0.016466 | 0 | 0.11902 | -0.21057 | 0.041199 | 0.054932 | 0.054932 | -0.004578 | 0.12817 | 0.1831 | -0.16022 | 122.113 | -0.045776 | 122.3236 | 122.3648 | -0.10986 | 122.1634 | 0.01831 | 0.21057 | 122.319 | 122.4518 | 122.3785 | 122.4426 | 122.3236 | 122.5067 | 122.3785 | 122.1634 | 122.4426 | 122.3236 | 122.3785 | 122.3785 | 122.5067 | -0.37537 | -0.32501
985.3594 | 122.5433 | -122.3099 | 0.16022 | 0.22209 | 0.017116 | 0.0028754 | 0.044728 | -0.011061 | -0.0080579 | 0.017107 | 0.045776 | 0.091553 | -0.17853 | 0.086975 | 0.13275 | 0.16022 | -0.16479 | 0.20599 | 0.16479 | -0.14191 | 122.1313 | -0.068664 | 122.3557 | 122.3969 | -0.027466 | 122.168 | 0.004578 | 0.2243 | 122.1451 | 122.5159 | 122.4426 | 122.4014 | 122.3557 | 122.4747 | 122.4701 | 122.168 | 122.4014 | 122.3557 | 122.4701 | 122.4426 | 122.4747 | -0.33874 | -0.30212
987.0469 | 122.5571 | -122.3511 | 0.20142 | -0.075455 | 0.016688 | 0.0073614 | 0.049215 | -0.011702 | -0.010194 | 0.017534 | 0.004578 | 0.11902 | -0.21973 | 0.050354 | 0.068665 | 0.068665 | -0.009155 | 0.15106 | 0.20142 | -0.17395 | 122.1313 | -0.082397 | 122.3557 | 122.4014 | -0.13275 | 122.1771 | 0 | 0.22431 | 122.3419 | 122.5021 | 122.4197 | 122.4701 | 122.3557 | 122.5525 | 122.4197 | 122.1771 | 122.4701 | 122.3557 | 122.4197 | 122.4197 | 122.5525 | -0.42114 | -0.37537
988.7188 | 122.5845 | -122.319 | 0.16937 | -0.13649 | 0.017756 | 0.0054388 | 0.04601 | -0.011061 | -0.0067761 | 0.014544 | -0.013733 | 0.11902 | -0.21057 | 0.032043 | 0.050354 | 0.073242 | 0.018311 | 0.12817 | 0.19684 | -0.18768 | 122.1085 | -0.050354 | 122.3053 | 122.3511 | -0.11902 | 122.1313 | 0.027465 | 0.19684 | 122.3373 | 122.4472 | 122.3694 | 122.438 | 122.3053 | 122.5159 | 122.3923 | 122.1313 | 122.438 | 122.3053 | 122.3923 | 122.3694 | 122.5159 | -0.37994 | -0.35706
990.3906 | 122.6669 | -122.2595 | 0.12817 | 0.016098 | 0.017329 | 0.008216 | 0.038533 | -0.013625 | -0.0054943 | 0.016253 | -0.018311 | 0.10071 | -0.17395 | 0 | 0.082397 | 0.10071 | -0.07782 | 0.15106 | 0.17853 | -0.16479 | 122.0856 | -0.027466 | 122.2412 | 122.2595 | -0.045777 | 122.0947 | 0.050354 | 0.15564 | 122.1817 | 122.4106 | 122.3419 | 122.3602 | 122.2412 | 122.438 | 122.3602 | 122.0947 | 122.3602 | 122.2412 | 122.3602 | 122.3419 | 122.438 | -0.30212 | -0.29297
992.0625 | 122.5479 | -122.3557 | 0.19684 | -0.090714 | 0.019252 | 0.0062934 | 0.04601 | -0.012343 | -0.0091259 | 0.018816 | 0.004578 | 0.1236 | -0.23346 | 0.050354 | 0.059509 | 0.082397 | -0.009155 | 0.14191 | 0.18768 | -0.16022 | 122.1222 | -0.073242 | 122.3602 | 122.406 | -0.13733 | 122.1954 | -0.009155 | 0.23804 | 122.3465 | 122.4976 | 122.4152 | 122.4792 | 122.3602 | 122.5433 | 122.438 | 122.1954 | 122.4792 | 122.3602 | 122.438 | 122.4152 | 122.5433 | -0.4303 | -0.35706
993.75 | 122.5433 | -122.3282 | 0.16937 | 0.20683 | 0.018611 | 0.010779 | 0.044728 | -0.011489 | -0.0091259 | 0.018389 | 0.054932 | 0.086975 | -0.16937 | 0.086975 | 0.13275 | 0.17395 | -0.16479 | 0.21057 | 0.1236 | -0.16022 | 122.1588 | -0.082398 | 122.3831 | 122.4152 | -0.036622 | 122.168 | -0.045777 | 0.22431 | 122.1634 | 122.5388 | 122.4609 | 122.4152 | 122.3831 | 122.4518 | 122.5021 | 122.168 | 122.4152 | 122.3831 | 122.5021 | 122.4609 | 122.4518 | -0.33875 | -0.32959
995.4219 | 122.6395 | -122.2916 | 0.12817 | -0.037308 | 0.018397 | 0.0073614 | 0.037892 | -0.012343 | -0.0054943 | 0.016893 | 0.009155 | 0.11444 | -0.1831 | 0.054932 | 0.1236 | 0.16022 | -0.091553 | 0.22888 | 0.16479 | -0.16479 | 122.1085 | -0.013733 | 122.3007 | 122.3465 | -0.004578 | 122.1268 | 0.036621 | 0.19226 | 122.2 | 122.5204 | 122.4152 | 122.406 | 122.3007 | 122.4564 | 122.4518 | 122.1268 | 122.406 | 122.3007 | 122.4518 | 122.4152 | 122.4564 | -0.31128 | -0.29297
997.1094 | 122.5983 | -122.319 | 0.16022 | 0.11528 | 0.018611 | 0.009925 | 0.047078 | -0.011489 | -0.0099805 | 0.015612 | -0.064087 | 0.1236 | -0.21057 | -0.041199 | 0.004578 | 0.041199 | -0.004578 | 0.068665 | 0.17853 | -0.17395 | 122.1085 | -0.036621 | 122.2549 | 122.2778 | -0.15564 | 122.1451 | 0.018311 | 0.14648 | 122.3145 | 122.3877 | 122.3236 | 122.4426 | 122.2549 | 122.4976 | 122.3602 | 122.1451 | 122.4426 | 122.2549 | 122.3602 | 122.3236 | 122.4976 | -0.37079 | -0.33417
998.7812 | 122.6074 | -122.3145 | 0.17853 | 0.13054 | 0.019252 | 0.0045844 | 0.047078 | -0.01213 | -0.0067761 | 0.017962 | -0.068665 | 0.11444 | -0.2243 | -0.050354 | -0.013733 | 0.027466 | 0.013733 | 0.045776 | 0.17853 | -0.20142 | 122.0901 | -0.064087 | 122.2458 | 122.2641 | -0.19226 | 122.113 | 0 | 0.15564 | 122.3282 | 122.3602 | 122.3007 | 122.4289 | 122.2458 | 122.493 | 122.3419 | 122.113 | 122.4289 | 122.2458 | 122.3419 | 122.3007 | 122.493 | -0.40283 | -0.37994
1000.4531 | 122.612 | -122.3419 | 0.17853 | 0.1458 | 0.016902 | 0.0060798 | 0.046224 | -0.011489 | -0.0089123 | 0.018602 | -0.064087 | 0.13275 | -0.22888 | -0.059509 | -0.013733 | 0.018311 | 0.018311 | 0.041199 | 0.20142 | -0.18768 | 122.113 | -0.045777 | 122.2778 | 122.2824 | -0.19226 | 122.1542 | 0.022888 | 0.16479 | 122.3602 | 122.3831 | 122.3282 | 122.4747 | 122.2778 | 122.5433 | 122.3602 | 122.1542 | 122.4747 | 122.2778 | 122.3602 | 122.3282 | 122.5433 | -0.40741 | -0.36621
1002.1406 | 122.5479 | -122.3511 | 0.17395 | 0.16106 | 0.016902 | 0.0035162 | 0.043233 | -0.011916 | -0.0095531 | 0.020311 | 0.027466 | 0.086975 | -0.16479 | 0.073242 | 0.11902 | 0.16479 | -0.16937 | 0.19684 | 0.15106 | -0.13275 | 122.1863 | -0.086975 | 122.3785 | 122.4243 | -0.054931 | 122.2183 | -0.022888 | 0.19226 | 122.1817 | 122.5479 | 122.4701 | 122.438 | 122.3785 | 122.5021 | 122.5159 | 122.2183 | 122.438 | 122.3785 | 122.5159 | 122.4701 | 122.5021 | -0.33874 | -0.3067
1003.8906 | 122.6074 | -122.3511 | 0.17395 | -0.14412 | 0.016688 | 0.0062934 | 0.046224 | -0.010421 | -0.0097669 | 0.016253 | -0.022888 | 0.082397 | -0.23346 | 0.027466 | 0.041199 | 0.068665 | 0.004578 | 0.15564 | 0.20599 | -0.17395 | 122.1176 | -0.091553 | 122.3282 | 122.3785 | -0.13275 | 122.1771 | 0.032044 | 0.21057 | 122.3557 | 122.5067 | 122.3923 | 122.4335 | 122.3282 | 122.5571 | 122.4197 | 122.1771 | 122.4335 | 122.3282 | 122.4197 | 122.3923 | 122.5571 | -0.40741 | -0.3479
1005.625 | 122.6944 | -122.287 | 0.14648 | -0.23567 | 0.018397 | 0.0058662 | 0.040029 | -0.013411 | -0.0076305 | 0.015612 | -0.022888 | 0.11444 | -0.18768 | -0.018311 | 0.045776 | 0.041199 | 0.032043 | 0.12817 | 0.19684 | -0.21057 | 122.0993 | -0.032043 | 122.2641 | 122.2687 | -0.10071 | 122.0764 | 0.050354 | 0.16479 | 122.319 | 122.4152 | 122.3328 | 122.4014 | 122.2641 | 122.4838 | 122.3282 | 122.0764 | 122.4014 | 122.2641 | 122.3282 | 122.3328 | 122.4838 | -0.33417 | -0.35706
1007.375 | 122.6715 | -122.3053 | 0.15106 | -0.29671 | 0.016475 | 0.0045844 | 0.041524 | -0.011702 | -0.0089123 | 0.017534 | -0.018311 | 0.10071 | -0.19226 | 0.027466 | 0.082397 | 0.09613 | -0.013733 | 0.16937 | 0.18768 | -0.17853 | 122.113 | -0.050354 | 122.287 | 122.3328 | -0.068665 | 122.1268 | 0.036621 | 0.17395 | 122.2916 | 122.4747 | 122.3877 | 122.406 | 122.287 | 122.493 | 122.4014 | 122.1268 | 122.406 | 122.287 | 122.4014 | 122.3877 | 122.493 | -0.34332 | -0.32959
1009.125 | 122.6166 | -122.3465 | 0.17395 | 0.092392 | 0.019893 | 0.0039436 | 0.046865 | -0.011489 | -0.0076305 | 0.017748 | -0.082397 | 0.12817 | -0.22888 | -0.041199 | -0.013733 | 0.027466 | 0.022888 | 0.045776 | 0.19226 | -0.19684 | 122.1176 | -0.045776 | 122.2641 | 122.3053 | -0.18768 | 122.1497 | 0.018311 | 0.14649 | 122.3694 | 122.3923 | 122.3328 | 122.4747 | 122.2641 | 122.5388 | 122.374 | 122.1497 | 122.4747 | 122.2641 | 122.374 | 122.3328 | 122.5388 | -0.40283 | -0.37079
1010.875 | 122.6074 | -122.3373 | 0.1831 | -0.12123 | 0.017116 | 0.0026618 | 0.046224 | -0.01213 | -0.0084851 | 0.017748 | -0.032043 | 0.10529 | -0.2243 | 0.018311 | 0.054932 | 0.068665 | -0.013733 | 0.14191 | 0.18768 | -0.17395 | 122.113 | -0.077819 | 122.3053 | 122.3557 | -0.12817 | 122.1634 | 0.004578 | 0.19226 | 122.3236 | 122.4792 | 122.3923 | 122.4426 | 122.3053 | 122.525 | 122.406 | 122.1634 | 122.4426 | 122.3053 | 122.406 | 122.3923 | 122.525 | -0.40741 | -0.35706
1012.5469 | 122.5662 | -122.3648 | 0.18768 | -0.075455 | 0.018184 | 0.0060798 | 0.045583 | -0.010848 | -0.0084851 | 0.01668 | -0.004578 | 0.1236 | -0.21515 | 0.036621 | 0.068665 | 0.086975 | -0.018311 | 0.15106 | 0.18768 | -0.18768 | 122.1497 | -0.064087 | 122.3602 | 122.4014 | -0.11902 | 122.1771 | 0 | 0.21057 | 122.3465 | 122.5159 | 122.4335 | 122.4884 | 122.3602 | 122.5525 | 122.4518 | 122.1771 | 122.4884 | 122.3602 | 122.4518 | 122.4335 | 122.5525 | -0.40283 | -0.37537
1014.2969 | 122.5983 | -122.3557 | 0.16479 | 0.12291 | 0.018184 | 0.0043708 | 0.040029 | -0.012343 | -0.0086987 | 0.017534 | 0.032043 | 0.068665 | -0.17395 | 0.041199 | 0.091553 | 0.15106 | -0.14648 | 0.1831 | 0.14648 | -0.16022 | 122.1817 | -0.09613 | 122.3877 | 122.3969 | -0.073242 | 122.1954 | -0.018311 | 0.20599 | 122.2092 | 122.5388 | 122.4472 | 122.4243 | 122.3877 | 122.5021 | 122.5067 | 122.1954 | 122.4243 | 122.3877 | 122.5067 | 122.4472 | 122.5021 | -0.33874 | -0.32501
1016.0312 | 122.6761 | -122.3282 | 0.14191 | -0.17464 | 0.017543 | 0.003089 | 0.044728 | -0.011916 | -0.0074169 | 0.015825 | -0.068665 | 0.11902 | -0.24719 | -0.027466 | 0.018311 | 0.027466 | 0.068665 | 0.10529 | 0.18768 | -0.19226 | 122.081 | -0.022888 | 122.2595 | 122.3007 | -0.1236 | 122.1359 | 0.045776 | 0.17853 | 122.3969 | 122.4335 | 122.3465 | 122.4472 | 122.2595 | 122.5159 | 122.3557 | 122.1359 | 122.4472 | 122.2595 | 122.3557 | 122.3465 | 122.5159 | -0.3891 | -0.33417
1017.7656 | 122.58 | -122.3282 | 0.17395 | 0.25261 | 0.019893 | 0.0045844 | 0.04366 | -0.0099934 | -0.0080579 | 0.018175 | -0.027466 | 0.10986 | -0.21973 | 0.013733 | 0.059509 | 0.09613 | -0.10529 | 0.14648 | 0.17395 | -0.15564 | 122.1085 | -0.064087 | 122.3007 | 122.3419 | -0.11444 | 122.1725 | 0 | 0.19226 | 122.2229 | 122.4747 | 122.3877 | 122.438 | 122.3007 | 122.5021 | 122.4243 | 122.1725 | 122.438 | 122.3007 | 122.4243 | 122.3877 | 122.5021 | -0.39368 | -0.32959
1019.5 | 122.6715 | -122.319 | 0.12817 | -0.022049 | 0.017329 | 0.003089 | 0.040456 | -0.013198 | -0.0059217 | 0.017962 | 0 | 0.10986 | -0.17853 | 0.073242 | 0.10986 | 0.14648 | -0.10071 | 0.2243 | 0.16479 | -0.16937 | 122.1405 | -0.018311 | 122.319 | 122.3923 | -0.018311 | 122.1497 | 0.036621 | 0.17853 | 122.2183 | 122.5433 | 122.4289 | 122.4289 | 122.319 | 122.4838 | 122.4655 | 122.1497 | 122.4289 | 122.319 | 122.4655 | 122.4289 | 122.4838 | -0.3067 | -0.29755
1021.1719 | 122.7036 | -122.3145 | 0.14191 | 0.023727 | 0.017329 | 0.0069342 | 0.041524 | -0.013839 | -0.0091259 | 0.017107 | -0.018311 | 0.10529 | -0.19684 | 0.022888 | 0.064087 | 0.09613 | -0.082397 | 0.16937 | 0.15564 | -0.16022 | 122.1176 | -0.036621 | 122.2961 | 122.3373 | -0.07782 | 122.1542 | 0.013733 | 0.17853 | 122.2321 | 122.4838 | 122.3785 | 122.4197 | 122.2961 | 122.4701 | 122.4106 | 122.1542 | 122.4197 | 122.2961 | 122.4106 | 122.3785 | 122.4701 | -0.33875 | -0.30212
1022.9219 | 122.7036 | -122.319 | 0.14191 | -0.0067901 | 0.016688 | 0.0067206 | 0.041738 | -0.011916 | -0.0059217 | 0.017534 | -0.027466 | 0.10071 | -0.20142 | 0.032043 | 0.073242 | 0.1236 | -0.086975 | 0.1831 | 0.16479 | -0.15564 | 122.1176 | -0.041199 | 122.2916 | 122.3511 | -0.068665 | 122.1634 | 0.022888 | 0.17395 | 122.2321 | 122.5021 | 122.3923 | 122.4197 | 122.2916 | 122.4838 | 122.4426 | 122.1634 | 122.4197 | 122.2916 | 122.4426 | 122.3923 | 122.4838 | -0.34332 | -0.29755
1024.6562 | 122.6715 | -122.3282 | 0.15564 | -0.22041 | 0.017116 | 0.0088568 | 0.048146 | -0.010634 | -0.011049 | 0.017107 | -0.045776 | 0.12817 | -0.23804 | 0.022888 | 0.045776 | 0.059509 | 0.013733 | 0.12817 | 0.19226 | -0.1831 | 122.0901 | -0.027466 | 122.2824 | 122.3511 | -0.10986 | 122.1451 | 0.036621 | 0.19226 | 122.3419 | 122.4564 | 122.374 | 122.4564 | 122.2824 | 122.5204 | 122.3877 | 122.1451 | 122.4564 | 122.2824 | 122.3877 | 122.374 | 122.5204 | -0.39368 | -0.33874
1026.3438 | 122.731 | -122.3511 | 0.13733 | -0.23567 | 0.018825 | 0.00138 | 0.044301 | -0.011061 | -0.0082715 | 0.017534 | -0.07782 | 0.12817 | -0.23346 | -0.036621 | 0.018311 | 0.018311 | 0.086975 | 0.09613 | 0.21515 | -0.19226 | 122.1176 | -0.009155 | 122.2733 | 122.3145 | -0.11902 | 122.1588 | 0.07782 | 0.15564 | 122.438 | 122.4472 | 122.3694 | 122.4792 | 122.2733 | 122.5662 | 122.3694 | 122.1588 | 122.4792 | 122.2733 | 122.3694 | 122.3694 | 122.5662 | -0.37079 | -0.32959
1028.0781 | 122.6578 | -122.3511 | 0.16937 | -0.21278 | 0.016047 | 0.0050116 | 0.041951 | -0.012557 | -0.0080579 | 0.015184 | 0.045776 | 0.091553 | -0.1831 | 0.073242 | 0.11444 | 0.13733 | -0.07782 | 0.22888 | 0.15106 | -0.16479 | 122.168 | -0.07782 | 122.3969 | 122.4243 | -0.054932 | 122.1863 | -0.018311 | 0.22888 | 122.2733 | 122.58 | 122.4655 | 122.4426 | 122.3969 | 122.5021 | 122.4884 | 122.1863 | 122.4426 | 122.3969 | 122.4884 | 122.4655 | 122.5021 | -0.35248 | -0.33417
1029.8125 | 122.7127 | -122.3373 | 0.13733 | -0.19753 | 0.016475 | 0.0054388 | 0.044301 | -0.013839 | -0.0065625 | 0.015825 | -0.07782 | 0.12817 | -0.21973 | -0.022888 | 0.022888 | 0.022888 | 0.059509 | 0.10986 | 0.20599 | -0.1831 | 122.1176 | -0.009155 | 122.2595 | 122.3145 | -0.11444 | 122.1542 | 0.068665 | 0.14191 | 122.3969 | 122.4472 | 122.3602 | 122.4655 | 122.2595 | 122.5433 | 122.3602 | 122.1542 | 122.4655 | 122.2595 | 122.3602 | 122.3602 | 122.5433 | -0.35706 | -0.32043
1031.4844 | 122.7264 | -122.3145 | 0.16479 | -0.22041 | 0.017756 | 0.0041572 | 0.044301 | -0.011702 | -0.0095531 | 0.016039 | -0.064087 | 0.1236 | -0.23804 | -0.027466 | 0.022888 | 0.018311 | 0.068665 | 0.11444 | 0.21515 | -0.19684 | 122.0764 | -0.041199 | 122.2504 | 122.287 | -0.14191 | 122.1176 | 0.050354 | 0.17395 | 122.3831 | 122.4289 | 122.3373 | 122.438 | 122.2504 | 122.5296 | 122.3328 | 122.1176 | 122.438 | 122.2504 | 122.3328 | 122.3373 | 122.5296 | -0.40283 | -0.36163
1033.2188 | 122.6486 | -122.3648 | 0.17853 | 0.13817 | 0.015193 | 0.0069342 | 0.039174 | -0.011275 | -0.0078443 | 0.016039 | -0.004578 | 0.086975 | -0.19684 | 0.041199 | 0.07782 | 0.10986 | -0.11902 | 0.16479 | 0.16937 | -0.16937 | 122.168 | -0.091553 | 122.3602 | 122.406 | -0.10071 | 122.1954 | -0.009155 | 0.19226 | 122.2458 | 122.5296 | 122.4426 | 122.4518 | 122.3602 | 122.5342 | 122.4747 | 122.1954 | 122.4518 | 122.3602 | 122.4747 | 122.4426 | 122.5342 | -0.37537 | -0.3479
1034.9688 | 122.5708 | -122.3648 | 0.1831 | 0.16106 | 0.014979 | 0.0077888 | 0.046437 | -0.010421 | -0.0086987 | 0.016893 | 0.068665 | 0.09613 | -0.17395 | 0.09613 | 0.11444 | 0.16479 | -0.17395 | 0.20142 | 0.14191 | -0.15564 | 122.1909 | -0.086975 | 122.4335 | 122.4609 | -0.068664 | 122.2092 | -0.041198 | 0.24261 | 122.1909 | 122.5662 | 122.4792 | 122.4609 | 122.4335 | 122.5067 | 122.5296 | 122.2092 | 122.4609 | 122.4335 | 122.5296 | 122.4792 | 122.5067 | -0.35706 | -0.33874
1036.6406 | 122.5616 | -122.3969 | 0.16937 | 0.13817 | 0.016902 | 0.0069342 | 0.046865 | -0.011702 | -0.0086987 | 0.017107 | 0.032043 | 0.086975 | -0.1831 | 0.086975 | 0.11444 | 0.16937 | -0.19684 | 0.20599 | 0.14648 | -0.16022 | 122.2137 | -0.082398 | 122.4289 | 122.4838 | -0.054932 | 122.2366 | -0.022889 | 0.21515 | 122.2 | 122.6028 | 122.5113 | 122.4838 | 122.4289 | 122.5433 | 122.5662 | 122.2366 | 122.4838 | 122.4289 | 122.5662 | 122.5113 | 122.5433 | -0.35248 | -0.32959
1038.375 | 122.58 | -122.3511 | 0.18768 | 0.18394 | 0.016047 | 0.0069342 | 0.042806 | -0.011489 | -0.011049 | 0.018602 | 0.009155 | 0.09613 | -0.19684 | 0.068665 | 0.1236 | 0.14191 | -0.13733 | 0.1831 | 0.15106 | -0.13733 | 122.1542 | -0.091553 | 122.3602 | 122.4197 | -0.064087 | 122.2137 | -0.036621 | 0.20599 | 122.2137 | 122.5342 | 122.4747 | 122.4472 | 122.3602 | 122.5021 | 122.493 | 122.2137 | 122.4472 | 122.3602 | 122.493 | 122.4747 | 122.5021 | -0.38452 | -0.32501
1040.1094 | 122.6624 | -122.3602 | 0.15106 | -0.17464 | 0.017329 | 0.0054388 | 0.046437 | -0.010207 | -0.011903 | 0.018175 | -0.032043 | 0.11444 | -0.20599 | 0.004578 | 0.041199 | 0.059509 | 0.018311 | 0.13733 | 0.18768 | -0.18768 | 122.1542 | -0.036621 | 122.3282 | 122.3648 | -0.10986 | 122.1725 | 0.036621 | 0.17395 | 122.3785 | 122.4976 | 122.4014 | 122.4747 | 122.3282 | 122.5479 | 122.4197 | 122.1725 | 122.4747 | 122.3282 | 122.4197 | 122.4014 | 122.5479 | -0.35706 | -0.33874
1041.7812 | 122.5937 | -122.3831 | 0.16022 | -0.022049 | 0.016902 | 0.0062934 | 0.04601 | -0.0097796 | -0.0086987 | 0.016466 | -0.018311 | 0.11444 | -0.20599 | 0.013733 | 0.027466 | 0.059509 | -0.009155 | 0.10529 | 0.1831 | -0.19226 | 122.1771 | -0.045776 | 122.3648 | 122.3969 | -0.13275 | 122.1909 | 0.022888 | 0.18768 | 122.374 | 122.4884 | 122.4106 | 122.4976 | 122.3648 | 122.5662 | 122.4426 | 122.1909 | 122.4976 | 122.3648 | 122.4426 | 122.4106 | 122.5662 | -0.36621 | -0.35248
1043.5156 | 122.5845 | -122.3923 | 0.18768 | -0.060196 | 0.018611 | 0.0052252 | 0.043233 | -0.0091388 | -0.0089123 | 0.016893 | 0 | 0.1236 | -0.19226 | 0.032043 | 0.068665 | 0.086975 | -0.013733 | 0.14191 | 0.1831 | -0.17395 | 122.2 | -0.064087 | 122.3923 | 122.4243 | -0.11902 | 122.2183 | -0.004578 | 0.19226 | 122.3785 | 122.5342 | 122.4609 | 122.5159 | 122.3923 | 122.5754 | 122.4792 | 122.2183 | 122.5159 | 122.3923 | 122.4792 | 122.4609 | 122.5754 | -0.37994 | -0.36163
1045.2656 | 122.6349 | -122.3877 | 0.16937 | 0.12291 | 0.019038 | 0.0071478 | 0.042806 | -0.0093524 | -0.010835 | 0.018389 | -0.050354 | 0.13275 | -0.21515 | -0.045776 | 0.009155 | 0.045776 | -0.022888 | 0.073242 | 0.19226 | -0.1831 | 122.1725 | -0.036622 | 122.3373 | 122.3419 | -0.16022 | 122.2046 | 0.022888 | 0.16479 | 122.3648 | 122.4609 | 122.3969 | 122.5204 | 122.3373 | 122.58 | 122.4335 | 122.2046 | 122.5204 | 122.3373 | 122.4335 | 122.3969 | 122.58 | -0.38452 | -0.35248
1046.9375 | 122.699 | -122.3419 | 0.12817 | -0.1899 | 0.018397 | 0.003089 | 0.042806 | -0.012343 | -0.0086987 | 0.018175 | -0.064087 | 0.14191 | -0.23346 | -0.022888 | 0.018311 | 0.045776 | 0.068665 | 0.10529 | 0.17853 | -0.21057 | 122.1085 | 0.013733 | 122.2778 | 122.319 | -0.10986 | 122.1313 | 0.050354 | 0.16937 | 122.4106 | 122.4472 | 122.3602 | 122.4838 | 122.2778 | 122.5204 | 122.3877 | 122.1313 | 122.4838 | 122.2778 | 122.3877 | 122.3602 | 122.5204 | -0.36163 | -0.33875
1048.6875 | 122.6669 | -122.3648 | 0.14648 | -0.20515 | 0.016047 | 0.006507 | 0.04067 | -0.011916 | -0.0063489 | 0.018389 | 0.041199 | 0.11444 | -0.16022 | 0.064087 | 0.14191 | 0.16479 | -0.086975 | 0.24261 | 0.15564 | -0.15564 | 122.2046 | -0.032043 | 122.406 | 122.4289 | -0.004577 | 122.2092 | 0.009156 | 0.20142 | 122.2778 | 122.6074 | 122.5067 | 122.4792 | 122.406 | 122.5204 | 122.5296 | 122.2092 | 122.4792 | 122.406 | 122.5296 | 122.5067 | 122.5204 | -0.3067 | -0.30212
1050.375 | 122.7127 | -122.3557 | 0.13733 | 0.061874 | 0.016261 | 0.0060798 | 0.040456 | -0.012984 | -0.0052807 | 0.018602 | -0.022888 | 0.091553 | -0.18768 | 0.009155 | 0.082397 | 0.11902 | -0.064087 | 0.15564 | 0.16479 | -0.19684 | 122.168 | -0.045776 | 122.3328 | 122.3648 | -0.054932 | 122.1588 | 0.027466 | 0.16479 | 122.2916 | 122.5113 | 122.438 | 122.4472 | 122.3328 | 122.5204 | 122.4747 | 122.1588 | 122.4472 | 122.3328 | 122.4747 | 122.438 | 122.5204 | -0.32501 | -0.33417
1052.1094 | 122.5845 | -122.3923 | 0.16937 | 0.19157 | 0.013911 | 0.0043708 | 0.044301 | -0.011702 | -0.0054943 | 0.017962 | 0.050354 | 0.10071 | -0.1831 | 0.07782 | 0.1236 | 0.17395 | -0.17395 | 0.2243 | 0.12817 | -0.16022 | 122.2092 | -0.068665 | 122.4426 | 122.4701 | -0.045777 | 122.2321 | -0.041199 | 0.23346 | 122.2183 | 122.6166 | 122.5159 | 122.493 | 122.4426 | 122.5204 | 122.5662 | 122.2321 | 122.493 | 122.4426 | 122.5662 | 122.5159 | 122.5204 | -0.35248 | -0.32959
1053.8438 | 122.6898 | -122.3648 | 0.15106 | 0.092392 | 0.018825 | 0.0052252 | 0.042165 | -0.013411 | -0.0061353 | 0.017534 | -0.004578 | 0.086975 | -0.19684 | 0.018311 | 0.073242 | 0.1236 | -0.091553 | 0.15564 | 0.16937 | -0.19226 | 122.168 | -0.064087 | 122.3602 | 122.3831 | -0.07782 | 122.1725 | 0.018311 | 0.19226 | 122.2733 | 122.5204 | 122.438 | 122.4518 | 122.3602 | 122.5342 | 122.4884 | 122.1725 | 122.4518 | 122.3602 | 122.4884 | 122.438 | 122.5342 | -0.3479 | -0.34332
1055.5156 | 122.7173 | -122.3328 | 0.14191 | 0.023727 | 0.018611 | 0.0043708 | 0.043233 | -0.015334 | -0.0063489 | 0.018602 | -0.009155 | 0.09613 | -0.20142 | 0.032043 | 0.068665 | 0.11444 | -0.07782 | 0.15564 | 0.15564 | -0.17395 | 122.1313 | -0.045777 | 122.3236 | 122.3648 | -0.073242 | 122.1588 | 0.013733 | 0.19226 | 122.2549 | 122.4884 | 122.4014 | 122.4289 | 122.3236 | 122.4884 | 122.4472 | 122.1588 | 122.4289 | 122.3236 | 122.4472 | 122.4014 | 122.4884 | -0.34332 | -0.31586
1057.2656 | 122.7356 | -122.3602 | 0.14648 | 0.016098 | 0.015834 | 0.006507 | 0.04366 | -0.011061 | -0.0078443 | 0.015398 | -0.022888 | 0.11444 | -0.19684 | 0.004578 | 0.068665 | 0.10071 | -0.086975 | 0.16022 | 0.17395 | -0.14648 | 122.1634 | -0.032043 | 122.3373 | 122.3648 | -0.077819 | 122.2137 | 0.027466 | 0.17395 | 122.2733 | 122.5204 | 122.4289 | 122.4747 | 122.3373 | 122.5342 | 122.4609 | 122.2137 | 122.4747 | 122.3373 | 122.4609 | 122.4289 | 122.5342 | -0.34332 | -0.29297
1059.0156 | 122.6578 | -122.4106 | 0.1831 | 0.10765 | 0.016261 | 0.0067206 | 0.049001 | -0.010634 | -0.0093395 | 0.017321 | -0.045776 | 0.12817 | -0.23346 | -0.013733 | 0.004578 | 0.009155 | 0.036621 | 0.068665 | 0.20142 | -0.19226 | 122.1771 | -0.054931 | 122.3648 | 122.3969 | -0.17853 | 122.2183 | 0.018311 | 0.18768 | 122.4472 | 122.4792 | 122.4152 | 122.5388 | 122.3648 | 122.612 | 122.4197 | 122.2183 | 122.5388 | 122.3648 | 122.4197 | 122.4152 | 122.612 | -0.41656 | -0.37537
1060.6875 | 122.6349 | -122.374 | 0.14648 | 0.15343 | 0.016047 | 0.0060798 | 0.045797 | -0.011489 | -0.0063489 | 0.018389 | -0.059509 | 0.12817 | -0.21515 | -0.013733 | 0.009155 | 0.059509 | -0.045776 | 0.082397 | 0.17395 | -0.20142 | 122.1588 | -0.01831 | 122.3145 | 122.3602 | -0.13733 | 122.1725 | 0.027466 | 0.15564 | 122.3282 | 122.4564 | 122.3831 | 122.5021 | 122.3145 | 122.5479 | 122.4335 | 122.1725 | 122.5021 | 122.3145 | 122.4335 | 122.3831 | 122.5479 | -0.36163 | -0.3479
1062.4219 | 122.6852 | -122.3785 | 0.15106 | -0.20515 | 0.016047 | 0.0058662 | 0.038747 | -0.011702 | -0.0095531 | 0.018389 | 0.018311 | 0.073242 | -0.17853 | 0.10529 | 0.13733 | 0.17395 | -0.1236 | 0.26093 | 0.14191 | -0.16937 | 122.2 | -0.07782 | 122.3969 | 122.4838 | -0.013733 | 122.2092 | -0.009155 | 0.19684 | 122.2549 | 122.6395 | 122.5159 | 122.4518 | 122.3969 | 122.5204 | 122.5525 | 122.2092 | 122.4518 | 122.3969 | 122.5525 | 122.5159 | 122.5204 | -0.32959 | -0.32044
1064.1719 | 122.6944 | -122.3648 | 0.15106 | -0.19753 | 0.015834 | 0.0056524 | 0.040242 | -0.011916 | -0.0078443 | 0.01903 | 0.050354 | 0.082397 | -0.18768 | 0.09613 | 0.14191 | 0.18768 | -0.1236 | 0.25635 | 0.13733 | -0.16479 | 122.1771 | -0.068665 | 122.4152 | 122.4609 | -0.009155 | 122.2 | -0.013733 | 0.23804 | 122.2412 | 122.6212 | 122.5067 | 122.4472 | 122.4152 | 122.5021 | 122.5525 | 122.2 | 122.4472 | 122.4152 | 122.5525 | 122.5067 | 122.5021 | -0.33874 | -0.31586
1065.8438 | 122.6807 | -122.374 | 0.16022 | -0.1899 | 0.015834 | 0.0060798 | 0.04366 | -0.011702 | -0.0089123 | 0.01668 | 0.068665 | 0.10071 | -0.17395 | 0.10986 | 0.14648 | 0.16022 | -0.10986 | 0.26093 | 0.14648 | -0.16937 | 122.2 | -0.059509 | 122.4426 | 122.4838 | -0.013733 | 122.2046 | -0.013733 | 0.24261 | 122.2641 | 122.6349 | 122.5204 | 122.4747 | 122.4426 | 122.5204 | 122.5342 | 122.2046 | 122.4747 | 122.4426 | 122.5342 | 122.5204 | 122.5204 | -0.33417 | -0.32959
1067.625 | 122.7264 | -122.3602 | 0.14191 | -0.17464 | 0.016902 | 0.0045844 | 0.045369 | -0.014266 | -0.0095531 | 0.015825 | -0.041199 | 0.1236 | -0.23804 | -0.009155 | 0.027466 | 0.032043 | 0.054932 | 0.10986 | 0.20142 | -0.19684 | 122.1222 | -0.018311 | 122.319 | 122.3511 | -0.11444 | 122.1634 | 0.059509 | 0.19684 | 122.4152 | 122.4701 | 122.3877 | 122.4838 | 122.319 | 122.5616 | 122.3923 | 122.1634 | 122.4838 | 122.319 | 122.3923 | 122.3877 | 122.5616 | -0.37994 | -0.33875
1069.375 | 122.699 | -122.3831 | 0.13275 | -0.16701 | 0.017116 | 0.0043708 | 0.041738 | -0.011702 | -0.0052807 | 0.016039 | 0.059509 | 0.091553 | -0.1831 | 0.13275 | 0.15564 | 0.16479 | -0.11444 | 0.25635 | 0.14648 | -0.17395 | 122.2 | -0.041198 | 122.4426 | 122.5159 | 0.022889 | 122.2092 | 0.013733 | 0.24261 | 122.2687 | 122.6395 | 122.5388 | 122.4747 | 122.4426 | 122.5296 | 122.5479 | 122.2092 | 122.4747 | 122.4426 | 122.5479 | 122.5388 | 122.5296 | -0.31586 | -0.3067
1071.0781 | 122.6166 | -122.4243 | 0.17395 | -0.037308 | 0.018611 | 0.0037298 | 0.048574 | -0.0089252 | -0.010621 | 0.017107 | -0.009155 | 0.10071 | -0.20599 | 0.018311 | 0.041199 | 0.054932 | -0.013733 | 0.10529 | 0.17853 | -0.20599 | 122.2183 | -0.073242 | 122.4152 | 122.4426 | -0.13275 | 122.2183 | 0.004578 | 0.19684 | 122.4106 | 122.5296 | 122.4655 | 122.525 | 122.4152 | 122.6028 | 122.4792 | 122.2183 | 122.525 | 122.4152 | 122.4792 | 122.4655 | 122.6028 | -0.37994 | -0.37994
1072.75 | 122.6028 | -122.406 | 0.18768 | 0.17632 | 0.018397 | 0.0075752 | 0.046224 | -0.01213 | -0.0076305 | 0.015398 | 0.036621 | 0.09613 | -0.17853 | 0.068665 | 0.11444 | 0.16479 | -0.16937 | 0.19226 | 0.1236 | -0.16479 | 122.2275 | -0.091553 | 122.4426 | 122.4747 | -0.073242 | 122.2412 | -0.064087 | 0.21515 | 122.2366 | 122.5983 | 122.5204 | 122.5021 | 122.4426 | 122.5296 | 122.5708 | 122.2412 | 122.5021 | 122.4426 | 122.5708 | 122.5204 | 122.5296 | -0.36621 | -0.35248
1074.4375 | 122.7402 | -122.374 | 0.14648 | -0.23567 | 0.015193 | 0.0043708 | 0.042165 | -0.011275 | -0.0089123 | 0.01668 | 0.009155 | 0.10071 | -0.21057 | 0.045776 | 0.09613 | 0.10529 | -0.027466 | 0.17395 | 0.16937 | -0.17395 | 122.1634 | -0.045776 | 122.3831 | 122.4197 | -0.050354 | 122.2 | 0.022889 | 0.21973 | 122.3465 | 122.5479 | 122.4701 | 122.4747 | 122.3831 | 122.5433 | 122.4792 | 122.2 | 122.4747 | 122.3831 | 122.4792 | 122.4701 | 122.5433 | -0.35706 | -0.32043
1076.1406 | 122.5891 | -122.4152 | 0.16937 | 0.23735 | 0.017329 | 0.0090704 | 0.045369 | -0.012557 | -0.0067761 | 0.01668 | 0.054932 | 0.086975 | -0.18768 | 0.07782 | 0.12817 | 0.17395 | -0.16479 | 0.20142 | 0.14191 | -0.16479 | 122.2275 | -0.082398 | 122.4701 | 122.493 | -0.041199 | 122.2504 | -0.027466 | 0.24261 | 122.2504 | 122.6166 | 122.5433 | 122.5021 | 122.4701 | 122.5571 | 122.5891 | 122.2504 | 122.5021 | 122.4701 | 122.5891 | 122.5433 | 122.5571 | -0.35706 | -0.33417
1077.8281 | 122.7402 | -122.3694 | 0.12817 | -0.25856 | 0.017543 | 0.0054388 | 0.04366 | -0.013198 | -0.0089123 | 0.017748 | -0.013733 | 0.10986 | -0.21057 | 0 | 0.041199 | 0.059509 | 0.022888 | 0.13733 | 0.17395 | -0.20599 | 122.1588 | -0.018311 | 122.3557 | 122.3694 | -0.086975 | 122.1634 | 0.045776 | 0.19684 | 122.3923 | 122.5067 | 122.4106 | 122.4792 | 122.3557 | 122.5433 | 122.4289 | 122.1634 | 122.4792 | 122.3557 | 122.4289 | 122.4106 | 122.5433 | -0.33875 | -0.33417
1079.5 | 122.7264 | -122.3831 | 0.15564 | -0.22804 | 0.014766 | 0.0039436 | 0.043233 | -0.013839 | -0.0059217 | 0.017962 | 0.022888 | 0.091553 | -0.18768 | 0.054932 | 0.09613 | 0.13275 | -0.027466 | 0.19226 | 0.16022 | -0.19684 | 122.1954 | -0.064087 | 122.406 | 122.438 | -0.05951 | 122.1863 | 0.004577 | 0.21057 | 122.3557 | 122.5754 | 122.4792 | 122.4747 | 122.406 | 122.5433 | 122.5159 | 122.1863 | 122.4747 | 122.406 | 122.5159 | 122.4792 | 122.5433 | -0.34332 | -0.35248
1081.1719 | 122.7127 | -122.3557 | 0.15106 | -0.022049 | 0.018184 | 0.0060798 | 0.039388 | -0.01213 | -0.0052807 | 0.017321 | 0 | 0.10986 | -0.16937 | 0.054932 | 0.10071 | 0.13275 | -0.10071 | 0.19226 | 0.13733 | -0.16937 | 122.1863 | -0.041199 | 122.3557 | 122.4106 | -0.050354 | 122.1863 | -0.013733 | 0.16937 | 122.2549 | 122.5479 | 122.4564 | 122.4655 | 122.3557 | 122.493 | 122.4884 | 122.1863 | 122.4655 | 122.3557 | 122.4884 | 122.4564 | 122.493 | -0.32044 | -0.32044
1082.8594 | 122.7539 | -122.3969 | 0.14191 | 0.0084684 | 0.017116 | 0.006507 | 0.044088 | -0.013625 | -0.0067761 | 0.017534 | -0.027466 | 0.10529 | -0.18768 | 0.032043 | 0.07782 | 0.11902 | -0.082397 | 0.16022 | 0.17395 | -0.16479 | 122.2092 | -0.036621 | 122.3694 | 122.4289 | -0.064087 | 122.2321 | 0.032043 | 0.16022 | 122.3145 | 122.5571 | 122.4747 | 122.5021 | 122.3694 | 122.5708 | 122.5159 | 122.2321 | 122.5021 | 122.3694 | 122.5159 | 122.4747 | 122.5708 | -0.32959 | -0.3067
1084.5469 | 122.5983 | -122.4152 | 0.16479 | 0.20683 | 0.018184 | 0.009284 | 0.046651 | -0.011489 | -0.0097669 | 0.017534 | 0.059509 | 0.10071 | -0.17853 | 0.091553 | 0.12817 | 0.16022 | -0.1831 | 0.21057 | 0.14648 | -0.16022 | 122.2366 | -0.064087 | 122.4747 | 122.5067 | -0.036621 | 122.2549 | -0.018311 | 0.23804 | 122.2321 | 122.6257 | 122.5433 | 122.5159 | 122.4747 | 122.5616 | 122.5754 | 122.2549 | 122.5159 | 122.4747 | 122.5754 | 122.5433 | 122.5616 | -0.34332 | -0.32501
1086.2344 | 122.6074 | -122.4289 | 0.19226 | -0.10597 | 0.019252 | 0.0060798 | 0.048146 | -0.010634 | -0.0095531 | 0.016893 | -0.013733 | 0.13275 | -0.23346 | 0.041199 | 0.064087 | 0.073242 | -0.013733 | 0.15106 | 0.19226 | -0.1831 | 122.1954 | -0.05951 | 122.4152 | 122.4701 | -0.12817 | 122.2458 | 0 | 0.21973 | 122.4152 | 122.58 | 122.493 | 122.5616 | 122.4152 | 122.6212 | 122.5021 | 122.2458 | 122.5616 | 122.4152 | 122.5021 | 122.493 | 122.6212 | -0.42572 | -0.37537
1087.9688 | 122.7631 | -122.3785 | 0.13733 | -0.23567 | 0.015834 | 0.0069342 | 0.042592 | -0.012557 | -0.0078443 | 0.015398 | -0.018311 | 0.10986 | -0.2243 | -0.013733 | 0.059509 | 0.050354 | 0.041199 | 0.13275 | 0.18768 | -0.21057 | 122.1542 | -0.027466 | 122.3602 | 122.3648 | -0.07782 | 122.168 | 0.050354 | 0.20599 | 122.4197 | 122.5113 | 122.438 | 122.4884 | 122.3602 | 122.5662 | 122.4289 | 122.168 | 122.4884 | 122.3602 | 122.4289 | 122.438 | 122.5662 | -0.36163 | -0.3479
1089.6719 | 122.6166 | -122.4106 | 0.17853 | 0.1992 | 0.019465 | 0.0043708 | 0.046224 | -0.010421 | -0.0076305 | 0.01903 | 0 | 0.10529 | -0.21057 | 0.050354 | 0.082397 | 0.13275 | -0.12817 | 0.16937 | 0.13733 | -0.16022 | 122.2 | -0.073242 | 122.4106 | 122.4609 | -0.096131 | 122.2504 | -0.041199 | 0.21057 | 122.2824 | 122.58 | 122.493 | 122.5159 | 122.4106 | 122.5479 | 122.5433 | 122.2504 | 122.5159 | 122.4106 | 122.5433 | 122.493 | 122.5479 | -0.3891 | -0.33874
1091.4531 | 122.6944 | -122.4106 | 0.15106 | -0.16701 | 0.017116 | 0.0033026 | 0.039601 | -0.011916 | -0.0093395 | 0.01903 | 0.045776 | 0.086975 | -0.17853 | 0.10529 | 0.13733 | 0.16937 | -0.12817 | 0.25635 | 0.16022 | -0.16479 | 122.2321 | -0.064087 | 122.4564 | 122.5159 | -0.013733 | 122.2458 | 0.009155 | 0.2243 | 122.2824 | 122.6669 | 122.5479 | 122.4976 | 122.4564 | 122.5708 | 122.58 | 122.2458 | 122.4976 | 122.4564 | 122.58 | 122.5479 | 122.5708 | -0.32959 | -0.31586
1093.1406 | 122.7539 | -122.3602 | 0.13275 | -0.22804 | 0.016261 | 0.0058662 | 0.042806 | -0.011916 | -0.0076305 | 0.01668 | -0.045776 | 0.11902 | -0.23804 | -0.013733 | 0.032043 | 0.045776 | 0.045776 | 0.12817 | 0.19226 | -0.21515 | 122.1222 | -0.013732 | 122.3145 | 122.3465 | -0.10071 | 122.1451 | 0.05951 | 0.19226 | 122.406 | 122.4884 | 122.3923 | 122.4792 | 122.3145 | 122.5525 | 122.406 | 122.1451 | 122.4792 | 122.3145 | 122.406 | 122.3923 | 122.5525 | -0.37079 | -0.3479
1094.8281 | 122.7585 | -122.3694 | 0.14191 | -0.20515 | 0.017116 | 0.0043708 | 0.045156 | -0.01277 | -0.0082715 | 0.014971 | -0.041199 | 0.1236 | -0.23804 | -0.018311 | 0.022888 | 0.022888 | 0.07782 | 0.10986 | 0.19684 | -0.21057 | 122.1313 | -0.018311 | 122.3282 | 122.3511 | -0.11902 | 122.1588 | 0.054931 | 0.19684 | 122.4472 | 122.4792 | 122.3923 | 122.493 | 122.3282 | 122.5662 | 122.3923 | 122.1588 | 122.493 | 122.3282 | 122.3923 | 122.3923 | 122.5662 | -0.37994 | -0.35248
1096.5 | 122.7722 | -122.3923 | 0.12817 | -0.21278 | 0.019893 | 0.0075752 | 0.043233 | -0.012343 | -0.011262 | 0.014971 | -0.054932 | 0.10986 | -0.21057 | -0.027466 | 0.018311 | 0.032043 | 0.064087 | 0.10986 | 0.21515 | -0.20599 | 122.1817 | -0.018311 | 122.3373 | 122.3648 | -0.10986 | 122.1863 | 0.086975 | 0.15564 | 122.4564 | 122.5021 | 122.4106 | 122.5021 | 122.3373 | 122.6074 | 122.4243 | 122.1863 | 122.5021 | 122.3373 | 122.4243 | 122.4106 | 122.6074 | -0.33875 | -0.33417
1098.1875 | 122.7585 | -122.3877 | 0.13275 | -0.0067901 | 0.016261 | 0.0073614 | 0.041097 | -0.011916 | -0.0084851 | 0.015184 | -0.013733 | 0.10529 | -0.18768 | 0.032043 | 0.09613 | 0.13275 | -0.091553 | 0.18768 | 0.16479 | -0.1831 | 122.2 | -0.027465 | 122.374 | 122.4197 | -0.036621 | 122.2046 | 0.032044 | 0.17395 | 122.2961 | 122.5754 | 122.4838 | 122.493 | 122.374 | 122.5525 | 122.5204 | 122.2046 | 122.493 | 122.374 | 122.5204 | 122.4838 | 122.5525 | -0.32043 | -0.31586
1099.8594 | 122.7676 | -122.4014 | 0.1236 | -0.25093 | 0.018397 | 0.0077888 | 0.04601 | -0.012557 | -0.011903 | 0.016466 | -0.059509 | 0.12817 | -0.23346 | -0.027466 | 0.004578 | 0.018311 | 0.07782 | 0.10529 | 0.19226 | -0.20599 | 122.168 | 0.004578 | 122.3419 | 122.374 | -0.11902 | 122.1954 | 0.068665 | 0.17395 | 122.4792 | 122.5067 | 122.406 | 122.5296 | 122.3419 | 122.5937 | 122.4197 | 122.1954 | 122.5296 | 122.3419 | 122.4197 | 122.406 | 122.5937 | -0.35706 | -0.32959
1101.5312 | 122.7081 | -122.3831 | 0.13733 | -0.20515 | 0.017756 | 0.0018072 | 0.046651 | -0.010207 | -0.0091259 | 0.017534 | -0.045776 | 0.11902 | -0.21973 | 0.018311 | 0.036621 | 0.054932 | 0.032043 | 0.1236 | 0.20142 | -0.18768 | 122.1634 | -0.01831 | 122.3373 | 122.4014 | -0.10071 | 122.1954 | 0.064087 | 0.17395 | 122.4152 | 122.5067 | 122.4197 | 122.5021 | 122.3373 | 122.5845 | 122.438 | 122.1954 | 122.5021 | 122.3373 | 122.438 | 122.4197 | 122.5845 | -0.35706 | -0.32501
1103.2188 | 122.7448 | -122.3694 | 0.14191 | 0.054245 | 0.016902 | 0.0067206 | 0.03832 | -0.01277 | -0.0080579 | 0.019243 | -0.036621 | 0.086975 | -0.20599 | 0.013733 | 0.068665 | 0.10986 | -0.068665 | 0.15106 | 0.15106 | -0.1831 | 122.1634 | -0.054932 | 122.3328 | 122.3831 | -0.073242 | 122.1863 | 0.009155 | 0.16937 | 122.3007 | 122.5204 | 122.438 | 122.4564 | 122.3328 | 122.5204 | 122.4792 | 122.1863 | 122.4564 | 122.3328 | 122.4792 | 122.438 | 122.5204 | -0.3479 | -0.32501
1104.9375 | 122.7448 | -122.3648 | 0.14191 | -0.0067901 | 0.018184 | 0.0069342 | 0.040456 | -0.014052 | -0.0065625 | 0.018389 | 0 | 0.086975 | -0.18768 | 0.041199 | 0.11444 | 0.12817 | -0.10529 | 0.20599 | 0.15106 | -0.19226 | 122.1771 | -0.054932 | 122.3648 | 122.406 | -0.027466 | 122.1725 | 0.009155 | 0.18768 | 122.2595 | 122.5708 | 122.4792 | 122.4518 | 122.3648 | 122.5159 | 122.493 | 122.1725 | 122.4518 | 122.3648 | 122.493 | 122.4792 | 122.5159 | -0.32959 | -0.33417
1106.6094 | 122.7356 | -122.3969 | 0.13733 | -0.052567 | 0.016688 | 0.0062934 | 0.042165 | -0.014693 | -0.0076305 | 0.017321 | 0.013733 | 0.086975 | -0.18768 | 0.068665 | 0.11902 | 0.15564 | -0.086975 | 0.2243 | 0.15564 | -0.16937 | 122.2092 | -0.050354 | 122.4106 | 122.4655 | -0.01831 | 122.2275 | 0.018311 | 0.20142 | 122.3099 | 122.6212 | 122.5159 | 122.4838 | 122.4106 | 122.5525 | 122.5525 | 122.2275 | 122.4838 | 122.4106 | 122.5525 | 122.5159 | 122.5525 | -0.32501 | -0.3067
1108.2812 | 122.7676 | -122.3831 | 0.14191 | -0.27382 | 0.017116 | 0.0058662 | 0.045156 | -0.013839 | -0.0076305 | 0.016893 | -0.018311 | 0.10529 | -0.21057 | 0.027466 | 0.045776 | 0.064087 | 0.027466 | 0.14191 | 0.18768 | -0.17853 | 122.1725 | -0.036621 | 122.3648 | 122.4106 | -0.096131 | 122.2046 | 0.045776 | 0.19226 | 122.4106 | 122.525 | 122.4289 | 122.4884 | 122.3648 | 122.5708 | 122.4472 | 122.2046 | 122.4884 | 122.3648 | 122.4472 | 122.4289 | 122.5708 | -0.35248 | -0.32044
1109.9844 | 122.6715 | -122.4197 | 0.16479 | 0.054245 | 0.014125 | 0.0086432 | 0.046437 | -0.010421 | -0.011262 | 0.017321 | -0.068665 | 0.13275 | -0.21973 | -0.050354 | -0.009155 | 0.004578 | 0.036621 | 0.041199 | 0.18768 | -0.18768 | 122.2 | -0.032044 | 122.3511 | 122.3694 | -0.17395 | 122.2321 | 0.022888 | 0.15106 | 122.4564 | 122.4609 | 122.4106 | 122.5525 | 122.3511 | 122.6074 | 122.4243 | 122.2321 | 122.5525 | 122.3511 | 122.4243 | 122.4106 | 122.6074 | -0.38452 | -0.35248
1111.6562 | 122.6349 | -122.438 | 0.16937 | -0.022049 | 0.018397 | 0.010779 | 0.047933 | -0.0087116 | -0.01233 | 0.017107 | 0.004578 | 0.11902 | -0.2243 | 0.036621 | 0.032043 | 0.064087 | -0.022888 | 0.13275 | 0.18768 | -0.17853 | 122.2137 | -0.050354 | 122.4426 | 122.4747 | -0.13733 | 122.2595 | 0.01831 | 0.22888 | 122.4152 | 122.5708 | 122.4701 | 122.5571 | 122.4426 | 122.6257 | 122.5021 | 122.2595 | 122.5571 | 122.4426 | 122.5021 | 122.4701 | 122.6257 | -0.39368 | -0.3479
1113.3438 | 122.6349 | -122.438 | 0.19226 | -0.060196 | 0.016902 | 0.0069342 | 0.047506 | -0.011061 | -0.010194 | 0.017107 | 0 | 0.11444 | -0.22888 | 0.045776 | 0.07782 | 0.07782 | -0.022888 | 0.14191 | 0.17395 | -0.18768 | 122.2092 | -0.07782 | 122.438 | 122.4838 | -0.11444 | 122.2504 | -0.018311 | 0.22888 | 122.4152 | 122.58 | 122.5159 | 122.5525 | 122.438 | 122.612 | 122.5159 | 122.2504 | 122.5525 | 122.438 | 122.5159 | 122.5159 | 122.612 | -0.42114 | -0.37994
1115.0312 | 122.6715 | -122.406 | 0.17395 | 0.092392 | 0.018184 | 0.0060798 | 0.044301 | -0.0091388 | -0.011049 | 0.017107 | -0.073242 | 0.1236 | -0.2243 | -0.045776 | 0 | 0.009155 | 0.027466 | 0.054932 | 0.19684 | -0.18768 | 122.1817 | -0.050354 | 122.3328 | 122.3602 | -0.17395 | 122.2183 | 0.022888 | 0.15106 | 122.4335 | 122.4609 | 122.406 | 122.5296 | 122.3328 | 122.6028 | 122.4152 | 122.2183 | 122.5296 | 122.3328 | 122.4152 | 122.406 | 122.6028 | -0.39825 | -0.36163
1116.7031 | 122.7448 | -122.3923 | 0.15106 | -0.15175 | 0.019038 | 0.0033026 | 0.043233 | -0.010848 | -0.0095531 | 0.016893 | -0.054932 | 0.13275 | -0.23804 | -0.009155 | 0.041199 | 0.041199 | 0.068665 | 0.11444 | 0.21057 | -0.21515 | 122.1542 | -0.018311 | 122.3373 | 122.3831 | -0.10986 | 122.1771 | 0.059509 | 0.1831 | 122.4609 | 122.5067 | 122.4335 | 122.525 | 122.3373 | 122.6028 | 122.4335 | 122.1771 | 122.525 | 122.3373 | 122.4335 | 122.4335 | 122.6028 | -0.3891 | -0.36621
1118.3906 | 122.7219 | -122.4106 | 0.13733 | -0.14412 | 0.01797 | 0.0097114 | 0.036611 | -0.011061 | -0.0067761 | 0.017107 | 0.032043 | 0.086975 | -0.17853 | 0.086975 | 0.15564 | 0.18768 | -0.14191 | 0.26093 | 0.14648 | -0.16937 | 122.2321 | -0.050354 | 122.4426 | 122.4976 | 0.018311 | 122.2412 | 0.009155 | 0.21057 | 122.2687 | 122.6715 | 122.5662 | 122.4976 | 122.4426 | 122.5571 | 122.5983 | 122.2412 | 122.4976 | 122.4426 | 122.5983 | 122.5662 | 122.5571 | -0.31586 | -0.3067
1120.0781 | 122.6212 | -122.4472 | 0.18768 | 0.18394 | 0.018611 | 0.009284 | 0.043874 | -0.010848 | -0.0082715 | 0.018602 | 0.050354 | 0.091553 | -0.17853 | 0.064087 | 0.11444 | 0.16479 | -0.16937 | 0.21057 | 0.16479 | -0.16937 | 122.2687 | -0.09613 | 122.4976 | 122.5113 | -0.073242 | 122.2778 | -0.022888 | 0.22888 | 122.2778 | 122.6578 | 122.5616 | 122.5388 | 122.4976 | 122.612 | 122.612 | 122.2778 | 122.5388 | 122.4976 | 122.612 | 122.5616 | 122.612 | -0.36621 | -0.35706
1121.75 | 122.6166 | -122.4335 | 0.16937 | 0.18394 | 0.014979 | 0.0043708 | 0.044515 | -0.011275 | -0.0078443 | 0.01668 | 0.032043 | 0.09613 | -0.19684 | 0.07782 | 0.13275 | 0.17395 | -0.16937 | 0.21973 | 0.14191 | -0.15106 | 122.2366 | -0.073243 | 122.4655 | 122.5113 | -0.036622 | 122.2824 | -0.027466 | 0.22888 | 122.2641 | 122.6532 | 122.5662 | 122.5296 | 122.4655 | 122.5754 | 122.6074 | 122.2824 | 122.5296 | 122.4655 | 122.6074 | 122.5662 | 122.5754 | -0.36621 | -0.32044
1123.4219 | 122.7127 | -122.3923 | 0.15564 | -0.21278 | 0.013698 | 0.0041572 | 0.042592 | -0.012557 | -0.0065625 | 0.018602 | 0.045776 | 0.10529 | -0.19684 | 0.09613 | 0.13733 | 0.16022 | -0.10071 | 0.25177 | 0.14648 | -0.16937 | 122.1954 | -0.050354 | 122.438 | 122.4884 | -0.018311 | 122.2229 | -0.009156 | 0.24261 | 122.2916 | 122.644 | 122.5296 | 122.4976 | 122.438 | 122.5388 | 122.5525 | 122.2229 | 122.4976 | 122.438 | 122.5525 | 122.5296 | 122.5388 | -0.35248 | -0.32501
1125.1094 | 122.6532 | -122.4289 | 0.18768 | 0.23735 | 0.016902 | 0.0086432 | 0.045583 | -0.013411 | -0.0084851 | 0.017962 | -0.004578 | 0.13733 | -0.20599 | 0.032043 | 0.073242 | 0.11902 | -0.09613 | 0.16022 | 0.17853 | -0.17853 | 122.2229 | -0.050354 | 122.4243 | 122.4609 | -0.11444 | 122.2504 | -0.009155 | 0.20142 | 122.3328 | 122.5891 | 122.5021 | 122.5662 | 122.4243 | 122.6074 | 122.5479 | 122.2504 | 122.5662 | 122.4243 | 122.5479 | 122.5021 | 122.6074 | -0.39368 | -0.36621
1126.7969 | 122.7493 | -122.3694 | 0.14648 | 0.069504 | 0.016902 | 0.0056524 | 0.039388 | -0.013625 | -0.0063489 | 0.018389 | -0.009155 | 0.10071 | -0.19226 | 0.027466 | 0.07782 | 0.1236 | -0.07782 | 0.17395 | 0.17395 | -0.17853 | 122.1771 | -0.045776 | 122.3602 | 122.3969 | -0.068664 | 122.1909 | 0.027466 | 0.18311 | 122.2916 | 122.5433 | 122.4472 | 122.4701 | 122.3602 | 122.5433 | 122.493 | 122.1909 | 122.4701 | 122.3602 | 122.493 | 122.4472 | 122.5433 | -0.33874 | -0.32501
1128.4688 | 122.644 | -122.4197 | 0.17853 | 0.19157 | 0.015407 | 0.010779 | 0.045583 | -0.011061 | -0.0080579 | 0.017748 | 0.064087 | 0.086975 | -0.15564 | 0.10529 | 0.13733 | 0.1831 | -0.16022 | 0.22888 | 0.15564 | -0.14191 | 122.2641 | -0.091553 | 122.4838 | 122.525 | -0.041199 | 122.2778 | -0.022888 | 0.21973 | 122.2595 | 122.6486 | 122.5571 | 122.5067 | 122.4838 | 122.5754 | 122.6028 | 122.2778 | 122.5067 | 122.4838 | 122.6028 | 122.5571 | 122.5754 | -0.33417 | -0.32044
1130.1562 | 122.7859 | -122.3648 | 0.15564 | -0.21278 | 0.017756 | 0.0033026 | 0.046651 | -0.011061 | -0.0072033 | 0.018175 | -0.07782 | 0.15106 | -0.21973 | 0 | 0.022888 | 0.041199 | 0.082397 | 0.10986 | 0.21057 | -0.21057 | 122.1451 | -0.004578 | 122.287 | 122.3648 | -0.13275 | 122.1542 | 0.054931 | 0.14191 | 122.4472 | 122.4747 | 122.3877 | 122.5159 | 122.287 | 122.5754 | 122.406 | 122.1542 | 122.5159 | 122.287 | 122.406 | 122.3877 | 122.5754 | -0.37537 | -0.36621
1131.8281 | 122.6532 | -122.4472 | 0.17395 | 0.084762 | 0.017543 | 0.0069342 | 0.047933 | -0.012557 | -0.0063489 | 0.017748 | 0.059509 | 0.11444 | -0.16479 | 0.086975 | 0.13733 | 0.17853 | -0.16937 | 0.21057 | 0.15564 | -0.14191 | 122.2824 | -0.059509 | 122.5067 | 122.5342 | -0.036621 | 122.3053 | -0.01831 | 0.2243 | 122.2778 | 122.6578 | 122.5845 | 122.5616 | 122.5067 | 122.6028 | 122.6257 | 122.3053 | 122.5616 | 122.5067 | 122.6257 | 122.5845 | 122.6028 | -0.33874 | -0.31586
1133.5 | 122.6944 | -122.4289 | 0.17853 | 0.17632 | 0.016475 | 0.0075752 | 0.046651 | -0.0099934 | -0.0082715 | 0.018175 | -0.054932 | 0.14648 | -0.2243 | -0.032043 | 0.018311 | 0.050354 | 0.018311 | 0.082397 | 0.21515 | -0.18768 | 122.2046 | -0.032044 | 122.374 | 122.3969 | -0.16022 | 122.2412 | 0.036621 | 0.16937 | 122.4472 | 122.5113 | 122.4472 | 122.5754 | 122.374 | 122.644 | 122.4792 | 122.2412 | 122.5754 | 122.374 | 122.4792 | 122.4472 | 122.644 | -0.40283 | -0.36621
1135.1719 | 122.7219 | -122.406 | 0.16937 | -0.15938 | 0.016902 | 0.008216 | 0.04601 | -0.01213 | -0.0093395 | 0.015825 | -0.032043 | 0.13275 | -0.21057 | 0.027466 | 0.064087 | 0.086975 | 0.027466 | 0.15106 | 0.19226 | -0.17853 | 122.1954 | -0.036622 | 122.374 | 122.4335 | -0.10529 | 122.2275 | 0.022888 | 0.17853 | 122.4335 | 122.5571 | 122.4701 | 122.5388 | 122.374 | 122.5983 | 122.493 | 122.2275 | 122.5388 | 122.374 | 122.493 | 122.4701 | 122.5983 | -0.37994 | -0.3479
1136.8438 | 122.731 | -122.406 | 0.16937 | -0.17464 | 0.017543 | 0.0080024 | 0.040029 | -0.011061 | -0.0089123 | 0.017321 | 0.050354 | 0.09613 | -0.17395 | 0.10071 | 0.16022 | 0.16022 | -0.09613 | 0.24261 | 0.15564 | -0.16479 | 122.2321 | -0.073243 | 122.4564 | 122.5067 | -0.009156 | 122.2412 | -0.013733 | 0.2243 | 122.3099 | 122.6486 | 122.5662 | 122.5021 | 122.4564 | 122.5616 | 122.5662 | 122.2412 | 122.5021 | 122.4564 | 122.5662 | 122.5662 | 122.5616 | -0.34332 | -0.33417
1138.5312 | 122.7585 | -122.406 | 0.17853 | -0.21278 | 0.018397 | 0.0067206 | 0.045369 | -0.011489 | -0.010194 | 0.016039 | -0.027466 | 0.13733 | -0.20142 | 0.013733 | 0.045776 | 0.082397 | 0.041199 | 0.14648 | 0.21515 | -0.17395 | 122.2046 | -0.041199 | 122.3785 | 122.4197 | -0.13275 | 122.2321 | 0.036621 | 0.17395 | 122.4472 | 122.5525 | 122.4518 | 122.5433 | 122.3785 | 122.6212 | 122.4884 | 122.2321 | 122.5433 | 122.3785 | 122.4884 | 122.4518 | 122.6212 | -0.37994 | -0.35248
1140.2031 | 122.7585 | -122.4106 | 0.15564 | -0.1899 | 0.017116 | 0.0060798 | 0.045797 | -0.012557 | -0.011049 | 0.018175 | -0.045776 | 0.15106 | -0.21973 | -0.009155 | 0.045776 | 0.050354 | 0.073242 | 0.11444 | 0.21057 | -0.19226 | 122.1909 | -0.004578 | 122.3648 | 122.4014 | -0.10986 | 122.2183 | 0.054931 | 0.17395 | 122.4838 | 122.525 | 122.4564 | 122.5616 | 122.3648 | 122.6212 | 122.4609 | 122.2183 | 122.5616 | 122.3648 | 122.4609 | 122.4564 | 122.6212 | -0.37537 | -0.3479
1141.8906 | 122.7768 | -122.4243 | 0.14648 | -0.22041 | 0.017116 | 0.0075752 | 0.040456 | -0.012343 | -0.0072033 | 0.016039 | 0.018311 | 0.11444 | -0.1831 | 0.064087 | 0.11444 | 0.12817 | -0.013733 | 0.21515 | 0.1831 | -0.17853 | 122.2412 | -0.032043 | 122.4426 | 122.4884 | -0.032043 | 122.2458 | 0.036621 | 0.20142 | 122.4106 | 122.6395 | 122.5388 | 122.5388 | 122.4426 | 122.6074 | 122.5525 | 122.2458 | 122.5388 | 122.4426 | 122.5525 | 122.5388 | 122.6074 | -0.32959 | -0.32501
1143.5625 | 122.7264 | -122.3877 | 0.14648 | -0.15938 | 0.016047 | 0.0026618 | 0.041097 | -0.013839 | -0.0063489 | 0.018816 | 0.045776 | 0.10529 | -0.16022 | 0.086975 | 0.14191 | 0.18768 | -0.11444 | 0.24719 | 0.17395 | -0.16022 | 122.2275 | -0.041198 | 122.4335 | 122.4747 | -0.004577 | 122.2275 | 0.027466 | 0.20599 | 122.2733 | 122.6349 | 122.5296 | 122.493 | 122.4335 | 122.5616 | 122.5754 | 122.2275 | 122.493 | 122.4335 | 122.5754 | 122.5296 | 122.5616 | -0.3067 | -0.3067
1145.2344 | 122.7814 | -122.374 | 0.14648 | 0.023727 | 0.016261 | 0.0071478 | 0.040242 | -0.014266 | -0.0067761 | 0.017748 | -0.022888 | 0.10529 | -0.17395 | 0.022888 | 0.07782 | 0.1236 | -0.059509 | 0.16937 | 0.1831 | -0.15564 | 122.2 | -0.041198 | 122.3511 | 122.3969 | -0.068664 | 122.2183 | 0.036621 | 0.15106 | 122.3145 | 122.5433 | 122.4518 | 122.4792 | 122.3511 | 122.5571 | 122.4976 | 122.2183 | 122.4792 | 122.3511 | 122.4976 | 122.4518 | 122.5571 | -0.32043 | -0.30212
1146.9219 | 122.7356 | -122.406 | 0.15564 | -0.12123 | 0.016047 | 0.0037298 | 0.041951 | -0.01213 | -0.0059217 | 0.016466 | 0.054932 | 0.10071 | -0.16937 | 0.09613 | 0.14648 | 0.17395 | -0.10529 | 0.2655 | 0.18768 | -0.16022 | 122.2366 | -0.054932 | 122.4609 | 122.5021 | -0.009156 | 122.2458 | 0.032043 | 0.22431 | 122.3007 | 122.6715 | 122.5525 | 122.5067 | 122.4609 | 122.5937 | 122.58 | 122.2458 | 122.5067 | 122.4609 | 122.58 | 122.5525 | 122.5937 | -0.32501 | -0.31586
1148.5938 | 122.7585 | -122.3831 | 0.16479 | 0.084762 | 0.015834 | 0.0075752 | 0.044088 | -0.014266 | -0.0069897 | 0.015612 | 0 | 0.10529 | -0.16937 | 0.045776 | 0.082397 | 0.1236 | -0.082397 | 0.16937 | 0.16479 | -0.15564 | 122.2137 | -0.059509 | 122.3831 | 122.4289 | -0.082398 | 122.2275 | 0 | 0.16937 | 122.3007 | 122.5525 | 122.4655 | 122.4884 | 122.3831 | 122.5479 | 122.5067 | 122.2275 | 122.4884 | 122.3831 | 122.5067 | 122.4655 | 122.5479 | -0.33417 | -0.32044
1150.2969 | 122.6761 | -122.438 | 0.19684 | -0.075455 | 0.017543 | 0.0069342 | 0.049001 | -0.01213 | -0.0084851 | 0.016039 | 0.013733 | 0.13275 | -0.20599 | 0.059509 | 0.068665 | 0.091553 | 0 | 0.16022 | 0.19226 | -0.16937 | 122.2321 | -0.064087 | 122.4518 | 122.4976 | -0.12817 | 122.2687 | -0.004577 | 0.21973 | 122.438 | 122.5983 | 122.5067 | 122.5708 | 122.4518 | 122.6303 | 122.5296 | 122.2687 | 122.5708 | 122.4518 | 122.5296 | 122.5067 | 122.6303 | -0.40283 | -0.36621
1152.0156 | 122.7036 | -122.4335 | 0.17853 | 0.054245 | 0.016475 | 0.0097114 | 0.049001 | -0.011061 | -0.0091259 | 0.019457 | -0.050354 | 0.15106 | -0.21057 | -0.013733 | 0 | 0.027466 | 0.050354 | 0.082397 | 0.20599 | -0.19226 | 122.2229 | -0.027466 | 122.3831 | 122.4197 | -0.17853 | 122.2412 | 0.027466 | 0.16022 | 122.4838 | 122.5159 | 122.4335 | 122.5845 | 122.3831 | 122.6395 | 122.4609 | 122.2412 | 122.5845 | 122.3831 | 122.4609 | 122.4335 | 122.6395 | -0.3891 | -0.37079
1153.6875 | 122.6852 | -122.4335 | 0.17853 | 0.038986 | 0.017116 | 0.0062934 | 0.04601 | -0.008498 | -0.0089123 | 0.017748 | -0.027466 | 0.14648 | -0.21515 | -0.018311 | 0.013733 | 0.041199 | 0.032043 | 0.09613 | 0.20599 | -0.19226 | 122.2183 | -0.032044 | 122.406 | 122.4152 | -0.16479 | 122.2412 | 0.027466 | 0.18768 | 122.4655 | 122.5296 | 122.4472 | 122.58 | 122.406 | 122.6395 | 122.4747 | 122.2412 | 122.58 | 122.406 | 122.4747 | 122.4472 | 122.6395 | -0.39368 | -0.37079
1155.375 | 122.644 | -122.4518 | 0.18768 | 0.19157 | 0.019252 | 0.009925 | 0.043874 | -0.0093524 | -0.0084851 | 0.017748 | 0.068665 | 0.10529 | -0.17395 | 0.086975 | 0.12817 | 0.17395 | -0.16022 | 0.22888 | 0.16479 | -0.14648 | 122.2778 | -0.082397 | 122.5204 | 122.5388 | -0.059509 | 122.3053 | -0.022888 | 0.24261 | 122.2916 | 122.6807 | 122.58 | 122.5571 | 122.5204 | 122.6166 | 122.6257 | 122.3053 | 122.5571 | 122.5204 | 122.6257 | 122.58 | 122.6166 | -0.36163 | -0.33417
1157.0469 | 122.7036 | -122.438 | 0.1831 | 0.11528 | 0.019252 | 0.0043708 | 0.047078 | -0.013198 | -0.011049 | 0.017962 | -0.07782 | 0.13275 | -0.21973 | -0.050354 | -0.004578 | 0.027466 | 0.022888 | 0.054932 | 0.20142 | -0.19226 | 122.2183 | -0.050354 | 122.3602 | 122.3877 | -0.18768 | 122.2458 | 0.018311 | 0.14191 | 122.4609 | 122.493 | 122.4335 | 122.5708 | 122.3602 | 122.6395 | 122.4655 | 122.2458 | 122.5708 | 122.3602 | 122.4655 | 122.4335 | 122.6395 | -0.40283 | -0.37537
1158.7188 | 122.6532 | -122.4609 | 0.18768 | -0.037308 | 0.018611 | 0.0080024 | 0.043874 | -0.011702 | -0.0095531 | 0.016893 | 0.018311 | 0.13275 | -0.20599 | 0.036621 | 0.082397 | 0.09613 | -0.013733 | 0.16479 | 0.18768 | -0.18768 | 122.2549 | -0.054932 | 122.4792 | 122.4976 | -0.10529 | 122.2733 | 0 | 0.22431 | 122.4472 | 122.6257 | 122.5433 | 122.5937 | 122.4792 | 122.6486 | 122.5571 | 122.2733 | 122.5937 | 122.4792 | 122.5571 | 122.5433 | 122.6486 | -0.39368 | -0.37537
1160.4062 | 122.7997 | -122.438 | 0.14191 | -0.25856 | 0.017116 | 0.0067206 | 0.039388 | -0.010421 | -0.0072033 | 0.01668 | 0.009155 | 0.13275 | -0.1831 | 0.027466 | 0.09613 | 0.1236 | 0 | 0.18768 | 0.19226 | -0.17853 | 122.2549 | -0.009156 | 122.4472 | 122.4655 | -0.045777 | 122.2595 | 0.050354 | 0.19226 | 122.438 | 122.6257 | 122.5342 | 122.5708 | 122.4472 | 122.6303 | 122.5616 | 122.2595 | 122.5708 | 122.4472 | 122.5616 | 122.5342 | 122.6303 | -0.32501 | -0.32044
1162.0938 | 122.7127 | -122.4335 | 0.18768 | 0.13054 | 0.017116 | 0.0071478 | 0.046865 | -0.011702 | -0.0072033 | 0.019457 | -0.045776 | 0.14648 | -0.2243 | -0.027466 | 0.027466 | 0.050354 | 0.013733 | 0.086975 | 0.20142 | -0.18768 | 122.2092 | -0.041199 | 122.3877 | 122.406 | -0.16022 | 122.2458 | 0.013733 | 0.17853 | 122.4472 | 122.5204 | 122.4609 | 122.58 | 122.3877 | 122.6349 | 122.4838 | 122.2458 | 122.58 | 122.3877 | 122.4838 | 122.4609 | 122.6349 | -0.41199 | -0.37537
1163.7656 | 122.6944 | -122.4518 | 0.17395 | 0.15343 | 0.016475 | 0.0056524 | 0.045369 | -0.011916 | -0.0099805 | 0.017107 | -0.045776 | 0.14191 | -0.21515 | -0.013733 | 0.036621 | 0.07782 | -0.054932 | 0.10071 | 0.19684 | -0.17395 | 122.2366 | -0.032043 | 122.406 | 122.438 | -0.13733 | 122.2778 | 0.022888 | 0.16937 | 122.3969 | 122.5525 | 122.4884 | 122.5937 | 122.406 | 122.6486 | 122.5296 | 122.2778 | 122.5937 | 122.406 | 122.5296 | 122.4884 | 122.6486 | -0.3891 | -0.3479
1165.5 | 122.7448 | -122.4426 | 0.14648 | -0.15938 | 0.017756 | 0.0041572 | 0.038533 | -0.013198 | -0.0063489 | 0.019884 | 0.045776 | 0.10986 | -0.16479 | 0.11444 | 0.17395 | 0.20599 | -0.1236 | 0.26093 | 0.17395 | -0.16937 | 122.2778 | -0.036621 | 122.4884 | 122.5571 | 0.027466 | 122.2733 | 0.027466 | 0.21057 | 122.319 | 122.7036 | 122.6166 | 122.5525 | 122.4884 | 122.6166 | 122.6486 | 122.2733 | 122.5525 | 122.4884 | 122.6486 | 122.6166 | 122.6166 | -0.31128 | -0.31586
1167.1719 | 122.699 | -122.4747 | 0.19226 | -0.0067901 | 0.018184 | 0.006507 | 0.046224 | -0.010421 | -0.010835 | 0.018175 | -0.018311 | 0.14191 | -0.21515 | -0.004578 | 0.022888 | 0.059509 | 0.009155 | 0.082397 | 0.18768 | -0.18768 | 122.2595 | -0.050354 | 122.4564 | 122.4701 | -0.16937 | 122.287 | -0.004578 | 0.19684 | 122.4838 | 122.5571 | 122.4976 | 122.6166 | 122.4564 | 122.6624 | 122.5342 | 122.287 | 122.6166 | 122.4564 | 122.5342 | 122.4976 | 122.6624 | -0.40741 | -0.37994
1168.8438 | 122.7219 | -122.4609 | 0.15564 | 0.10765 | 0.01797 | 0.0069342 | 0.045583 | -0.011702 | -0.0091259 | 0.016039 | -0.064087 | 0.14648 | -0.23346 | -0.041199 | 0.009155 | 0.041199 | 0.009155 | 0.064087 | 0.18768 | -0.21515 | 122.2275 | -0.009156 | 122.3969 | 122.4197 | -0.14649 | 122.2458 | 0.032043 | 0.16937 | 122.4701 | 122.525 | 122.4701 | 122.6074 | 122.3969 | 122.6486 | 122.5021 | 122.2458 | 122.6074 | 122.3969 | 122.5021 | 122.4701 | 122.6486 | -0.3891 | -0.37079
1170.5156 | 122.6761 | -122.4747 | 0.18768 | -0.075455 | 0.017543 | 0.0045844 | 0.043874 | -0.013411 | -0.010408 | 0.01967 | -0.018311 | 0.14191 | -0.20599 | 0.032043 | 0.073242 | 0.086975 | -0.004578 | 0.16479 | 0.17853 | -0.18768 | 122.2687 | -0.045776 | 122.4564 | 122.5067 | -0.11444 | 122.287 | -0.009155 | 0.18768 | 122.4701 | 122.6395 | 122.5479 | 122.6166 | 122.4564 | 122.6532 | 122.5616 | 122.287 | 122.6166 | 122.4564 | 122.5616 | 122.5479 | 122.6532 | -0.39368 | -0.37537
1172.2031 | 122.8088 | -122.4609 | 0.13275 | -0.25093 | 0.016902 | 0.0039436 | 0.040883 | -0.012343 | -0.0086987 | 0.016893 | -0.086975 | 0.13275 | -0.21057 | -0.041199 | 0.027466 | 0.041199 | 0.086975 | 0.10529 | 0.20599 | -0.2243 | 122.2504 | 0 | 122.374 | 122.4197 | -0.10529 | 122.2366 | 0.073243 | 0.1236 | 122.5479 | 122.5662 | 122.4884 | 122.5937 | 122.374 | 122.6669 | 122.5021 | 122.2366 | 122.5937 | 122.374 | 122.5021 | 122.4884 | 122.6669 | -0.34332 | -0.35706
1173.8906 | 122.6852 | -122.4884 | 0.1831 | -0.083084 | 0.01797 | 0.0056524 | 0.046224 | -0.0087116 | -0.0082715 | 0.018389 | 0.018311 | 0.15106 | -0.20142 | 0.036621 | 0.064087 | 0.09613 | -0.032043 | 0.16937 | 0.19226 | -0.19684 | 122.287 | -0.032043 | 122.5067 | 122.525 | -0.11902 | 122.2916 | 0.009156 | 0.21973 | 122.4564 | 122.6578 | 122.5525 | 122.6395 | 122.5067 | 122.6807 | 122.5845 | 122.2916 | 122.6395 | 122.5067 | 122.5845 | 122.5525 | 122.6807 | -0.38452 | -0.37994
1175.5625 | 122.7219 | -122.4564 | 0.16022 | 0.10002 | 0.015834 | 0.0077888 | 0.046224 | -0.0099934 | -0.010835 | 0.01903 | -0.068665 | 0.14648 | -0.2243 | -0.064087 | 0 | 0.032043 | 0.022888 | 0.064087 | 0.1831 | -0.20142 | 122.2321 | -0.013733 | 122.3877 | 122.3923 | -0.16022 | 122.2549 | 0.022888 | 0.15564 | 122.4792 | 122.5204 | 122.4564 | 122.6028 | 122.3877 | 122.6395 | 122.4884 | 122.2549 | 122.6028 | 122.3877 | 122.4884 | 122.4564 | 122.6395 | -0.38452 | -0.36163
1177.2344 | 122.7173 | -122.4609 | 0.16937 | 0.069504 | 0.01797 | 0.0033026 | 0.046224 | -0.010634 | -0.0078443 | 0.018816 | -0.068665 | 0.15564 | -0.21973 | -0.059509 | -0.013733 | 0.009155 | 0.036621 | 0.068665 | 0.20599 | -0.19684 | 122.2412 | -0.013733 | 122.3923 | 122.4014 | -0.18311 | 122.2641 | 0.036621 | 0.15106 | 122.4976 | 122.5296 | 122.4472 | 122.6166 | 122.3923 | 122.6669 | 122.4701 | 122.2641 | 122.6166 | 122.3923 | 122.4701 | 122.4472 | 122.6669 | -0.3891 | -0.36621
1178.9375 | 122.6532 | -122.4747 | 0.17853 | 0.20683 | 0.016902 | 0.00138 | 0.043233 | -0.010634 | -0.0072033 | 0.01668 | 0.064087 | 0.09613 | -0.1831 | 0.068665 | 0.13733 | 0.16937 | -0.17395 | 0.20599 | 0.15106 | -0.16022 | 122.2916 | -0.082398 | 122.5388 | 122.5433 | -0.041199 | 122.3145 | -0.027466 | 0.24719 | 122.3007 | 122.6807 | 122.612 | 122.5708 | 122.5388 | 122.6257 | 122.644 | 122.3145 | 122.5708 | 122.5388 | 122.644 | 122.612 | 122.6257 | -0.36163 | -0.33874
1180.625 | 122.6761 | -122.4701 | 0.17853 | 0.16106 | 0.015407 | 0.0073614 | 0.042379 | -0.010848 | -0.0093395 | 0.018175 | 0.050354 | 0.1236 | -0.17395 | 0.064087 | 0.1236 | 0.17853 | -0.16937 | 0.21057 | 0.15106 | -0.14191 | 122.2961 | -0.054932 | 122.5204 | 122.5342 | -0.054932 | 122.3282 | -0.027466 | 0.2243 | 122.3007 | 122.6807 | 122.5937 | 122.5937 | 122.5204 | 122.6212 | 122.6486 | 122.3282 | 122.5937 | 122.5204 | 122.6486 | 122.5937 | 122.6212 | -0.35248 | -0.32044
1182.2969 | 122.6532 | -122.4701 | 0.17395 | 0.19157 | 0.016688 | 0.0062934 | 0.044088 | -0.011275 | -0.0065625 | 0.016039 | 0.050354 | 0.10986 | -0.17395 | 0.068665 | 0.13733 | 0.1831 | -0.17853 | 0.23346 | 0.16022 | -0.1831 | 122.2961 | -0.064087 | 122.5204 | 122.5388 | -0.036621 | 122.287 | -0.013733 | 0.2243 | 122.2916 | 122.7036 | 122.6074 | 122.58 | 122.5204 | 122.6303 | 122.6532 | 122.287 | 122.58 | 122.5204 | 122.6532 | 122.6074 | 122.6303 | -0.3479 | -0.35706
1184.0156 | 122.6944 | -122.4564 | 0.17853 | -0.029679 | 0.016475 | 0.0058662 | 0.046224 | -0.011702 | -0.0089123 | 0.018175 | -0.004578 | 0.11444 | -0.2243 | 0.009155 | 0.045776 | 0.068665 | 0.013733 | 0.1236 | 0.19684 | -0.21057 | 122.2321 | -0.064087 | 122.4518 | 122.4655 | -0.13275 | 122.2458 | 0.01831 | 0.21973 | 122.4701 | 122.58 | 122.5021 | 122.5708 | 122.4518 | 122.6532 | 122.525 | 122.2458 | 122.5708 | 122.4518 | 122.525 | 122.5021 | 122.6532 | -0.40283 | -0.3891
1185.6875 | 122.6807 | -122.5067 | 0.17853 | -0.052567 | 0.017543 | 0.0056524 | 0.045797 | -0.010421 | -0.010621 | 0.018175 | 0.004578 | 0.14191 | -0.21057 | 0.027466 | 0.068665 | 0.10071 | -0.018311 | 0.16479 | 0.17395 | -0.19684 | 122.2961 | -0.036621 | 122.5113 | 122.5342 | -0.10986 | 122.3099 | -0.004578 | 0.21515 | 122.4884 | 122.6715 | 122.5754 | 122.6486 | 122.5113 | 122.6807 | 122.6074 | 122.3099 | 122.6486 | 122.5113 | 122.6074 | 122.5754 | 122.6807 | -0.3891 | -0.37537
1187.375 | 122.7081 | -122.4701 | 0.17853 | 0.13054 | 0.016475 | 0.0073614 | 0.039815 | -0.014052 | -0.0082715 | 0.018175 | 0.045776 | 0.12817 | -0.16022 | 0.045776 | 0.11444 | 0.16022 | -0.11902 | 0.20599 | 0.16937 | -0.17395 | 122.3099 | -0.050354 | 122.5159 | 122.5159 | -0.064087 | 122.2961 | -0.009155 | 0.20599 | 122.3511 | 122.6761 | 122.5845 | 122.5983 | 122.5159 | 122.6395 | 122.6303 | 122.2961 | 122.5983 | 122.5159 | 122.6303 | 122.5845 | 122.6395 | -0.33874 | -0.35248
1189.0469 | 122.7036 | -122.4884 | 0.17853 | -0.13649 | 0.017756 | 0.011634 | 0.046651 | -0.012557 | -0.0089123 | 0.016893 | -0.004578 | 0.14191 | -0.21057 | 0.022888 | 0.07782 | 0.091553 | -0.009155 | 0.16022 | 0.19684 | -0.19226 | 122.2778 | -0.036621 | 122.4838 | 122.5113 | -0.10071 | 122.2961 | 0.01831 | 0.20599 | 122.4792 | 122.6486 | 122.5662 | 122.6303 | 122.4838 | 122.6852 | 122.58 | 122.2961 | 122.6303 | 122.4838 | 122.58 | 122.5662 | 122.6852 | -0.3891 | -0.37079
1190.7188 | 122.8317 | -122.4518 | 0.13733 | -0.19753 | 0.01562 | 0.002021 | 0.04131 | -0.014479 | -0.0072033 | 0.017107 | -0.07782 | 0.14191 | -0.20599 | -0.027466 | 0.013733 | 0.041199 | 0.082397 | 0.10986 | 0.21973 | -0.21057 | 122.2458 | 0.004578 | 122.374 | 122.4243 | -0.1236 | 122.2412 | 0.082398 | 0.12817 | 122.5342 | 122.5616 | 122.4655 | 122.5937 | 122.374 | 122.6715 | 122.493 | 122.2412 | 122.5937 | 122.374 | 122.493 | 122.4655 | 122.6715 | -0.34332 | -0.3479
1192.3906 | 122.699 | -122.5021 | 0.16937 | -0.044937 | 0.014766 | 0.009925 | 0.045797 | -0.010848 | -0.010835 | 0.017534 | 0.004578 | 0.12817 | -0.21973 | 0.022888 | 0.059509 | 0.091553 | -0.027466 | 0.16022 | 0.19226 | -0.19684 | 122.2824 | -0.041199 | 122.5067 | 122.525 | -0.10986 | 122.3053 | 0.022888 | 0.22431 | 122.4747 | 122.6624 | 122.5616 | 122.6303 | 122.5067 | 122.6944 | 122.5937 | 122.3053 | 122.6303 | 122.5067 | 122.5937 | 122.5616 | 122.6944 | -0.3891 | -0.36621
1194.0781 | 122.7219 | -122.4838 | 0.16937 | 0.1458 | 0.017329 | 0.003089 | 0.043019 | -0.010634 | -0.0084851 | 0.018602 | -0.064087 | 0.1236 | -0.22888 | -0.041199 | 0.036621 | 0.059509 | -0.022888 | 0.086975 | 0.19226 | -0.20142 | 122.2549 | -0.045777 | 122.4197 | 122.4426 | -0.13275 | 122.2824 | 0.022888 | 0.16479 | 122.4609 | 122.5708 | 122.5204 | 122.6074 | 122.4197 | 122.6761 | 122.5433 | 122.2824 | 122.6074 | 122.4197 | 122.5433 | 122.5204 | 122.6761 | -0.39826 | -0.37079
1195.75 | 122.7722 | -122.4564 | 0.14191 | -0.12123 | 0.017756 | -0.00075623 | 0.036824 | -0.013625 | -0.0074169 | 0.017107 | 0.041199 | 0.09613 | -0.17853 | 0.086975 | 0.14191 | 0.17395 | -0.11902 | 0.25177 | 0.14648 | -0.17853 | 122.2778 | -0.045777 | 122.4976 | 122.5433 | 0 | 122.2778 | 0.004577 | 0.21973 | 122.3373 | 122.7081 | 122.5983 | 122.5525 | 122.4976 | 122.6028 | 122.6303 | 122.2778 | 122.5525 | 122.4976 | 122.6303 | 122.5983 | 122.6028 | -0.32044 | -0.32044
1197.4219 | 122.7173 | -122.4701 | 0.16022 | 0.13054 | 0.015407 | 0.0060798 | 0.042165 | -0.012984 | -0.0069897 | 0.017534 | 0.022888 | 0.13275 | -0.17853 | 0.041199 | 0.11902 | 0.15564 | -0.13733 | 0.20599 | 0.15564 | -0.17395 | 122.2916 | -0.027466 | 122.493 | 122.5113 | -0.041198 | 122.2961 | -0.004577 | 0.20142 | 122.3328 | 122.6761 | 122.5891 | 122.6028 | 122.493 | 122.6257 | 122.6257 | 122.2961 | 122.6028 | 122.493 | 122.6257 | 122.5891 | 122.6257 | -0.33874 | -0.33417
1199.0938 | 122.6624 | -122.493 | 0.16022 | 0.16106 | 0.016475 | 0.0088568 | 0.044301 | -0.011702 | -0.0067761 | 0.018816 | 0.036621 | 0.10071 | -0.16022 | 0.07782 | 0.11902 | 0.16022 | -0.1831 | 0.21057 | 0.15564 | -0.16022 | 122.3328 | -0.059509 | 122.5296 | 122.5708 | -0.041198 | 122.3328 | -0.004577 | 0.19684 | 122.3099 | 122.7036 | 122.612 | 122.5937 | 122.5296 | 122.6486 | 122.6532 | 122.3328 | 122.5937 | 122.5296 | 122.6532 | 122.612 | 122.6486 | -0.32043 | -0.32043
1200.7656 | 122.7036 | -122.4838 | 0.15564 | 0.15343 | 0.017756 | 0.011634 | 0.045156 | -0.012343 | -0.0095531 | 0.018175 | -0.045776 | 0.12817 | -0.23346 | -0.013733 | 0.013733 | 0.059509 | -0.045776 | 0.086975 | 0.17395 | -0.20599 | 122.2504 | -0.027466 | 122.438 | 122.4701 | -0.14191 | 122.2778 | 0.01831 | 0.18768 | 122.438 | 122.5708 | 122.4976 | 122.612 | 122.438 | 122.6578 | 122.5433 | 122.2778 | 122.612 | 122.438 | 122.5433 | 122.4976 | 122.6578 | -0.3891 | -0.36163
1202.4688 | 122.7127 | -122.4792 | 0.16022 | 0.1458 | 0.016902 | 0.006507 | 0.040242 | -0.011275 | -0.0080579 | 0.018389 | 0.041199 | 0.10529 | -0.18768 | 0.054932 | 0.10986 | 0.14191 | -0.15106 | 0.19226 | 0.15564 | -0.16937 | 122.2916 | -0.054931 | 122.5204 | 122.5342 | -0.050354 | 122.3099 | -0.004577 | 0.22888 | 122.3282 | 122.6715 | 122.5891 | 122.5845 | 122.5204 | 122.6349 | 122.6212 | 122.3099 | 122.5845 | 122.5204 | 122.6212 | 122.5891 | 122.6349 | -0.3479 | -0.32959
1204.1719 | 122.7585 | -122.4747 | 0.16022 | -0.20515 | 0.017116 | 0.0075752 | 0.045797 | -0.01213 | -0.011476 | 0.016253 | -0.018311 | 0.13733 | -0.23804 | 0.009155 | 0.050354 | 0.050354 | 0.013733 | 0.12817 | 0.17853 | -0.19684 | 122.2366 | -0.022888 | 122.4564 | 122.4838 | -0.10986 | 122.2778 | 0.018311 | 0.21973 | 122.4884 | 122.6028 | 122.525 | 122.612 | 122.4564 | 122.6532 | 122.525 | 122.2778 | 122.612 | 122.4564 | 122.525 | 122.525 | 122.6532 | -0.39825 | -0.35706
1205.9375 | 122.7859 | -122.4655 | 0.13733 | -0.098343 | 0.017756 | 0.0035162 | 0.039388 | -0.0097796 | -0.0082715 | 0.016466 | 0.022888 | 0.091553 | -0.19226 | 0.07782 | 0.14648 | 0.16022 | -0.13733 | 0.23804 | 0.16479 | -0.1831 | 122.2733 | -0.045776 | 122.4884 | 122.5433 | 0.009155 | 122.2824 | 0.027466 | 0.21515 | 122.3282 | 122.7036 | 122.612 | 122.5571 | 122.4884 | 122.6303 | 122.6257 | 122.2824 | 122.5571 | 122.4884 | 122.6257 | 122.612 | 122.6303 | -0.32959 | -0.32043
1207.625 | 122.8226 | -122.438 | 0.1236 | 0.00083945 | 0.016261 | 0.0071478 | 0.041097 | -0.014052 | -0.0072033 | 0.017534 | -0.018311 | 0.10071 | -0.21057 | 0.013733 | 0.082397 | 0.10071 | -0.073242 | 0.16937 | 0.13733 | -0.17853 | 122.2275 | -0.022888 | 122.4197 | 122.4518 | -0.041199 | 122.2595 | 0.013733 | 0.19226 | 122.3648 | 122.6074 | 122.5204 | 122.5388 | 122.4197 | 122.5754 | 122.5388 | 122.2595 | 122.5388 | 122.4197 | 122.5388 | 122.5204 | 122.5754 | -0.33417 | -0.30212
1209.3594 | 122.7905 | -122.4747 | 0.13275 | -0.14412 | 0.016688 | 0.0062934 | 0.040456 | -0.014479 | -0.0082715 | 0.016253 | 0.041199 | 0.11444 | -0.1831 | 0.086975 | 0.14648 | 0.17395 | -0.1236 | 0.24719 | 0.14648 | -0.19226 | 122.2916 | -0.01831 | 122.5159 | 122.5616 | 0.013733 | 122.2824 | 0.013733 | 0.2243 | 122.3511 | 122.7219 | 122.6212 | 122.5891 | 122.5159 | 122.6212 | 122.6486 | 122.2824 | 122.5891 | 122.5159 | 122.6486 | 122.6212 | 122.6212 | -0.31586 | -0.32501
1211.1094 | 122.8271 | -122.4472 | 0.14191 | -0.022049 | 0.01562 | 0.0028754 | 0.041951 | -0.011916 | -0.0089123 | 0.017748 | -0.018311 | 0.11444 | -0.19684 | 0.027466 | 0.086975 | 0.11902 | -0.091553 | 0.17395 | 0.16479 | -0.19684 | 122.2504 | -0.027466 | 122.4289 | 122.4747 | -0.054932 | 122.2504 | 0.022888 | 0.17853 | 122.3557 | 122.6212 | 122.5342 | 122.5616 | 122.4289 | 122.612 | 122.5662 | 122.2504 | 122.5616 | 122.4289 | 122.5662 | 122.5342 | 122.612 | -0.33875 | -0.33875
1212.7812 | 122.7768 | -122.4655 | 0.15564 | -0.12886 | 0.017329 | 0.0080024 | 0.043019 | -0.014052 | -0.0082715 | 0.017107 | 0.059509 | 0.082397 | -0.1831 | 0.10529 | 0.15106 | 0.16479 | -0.12817 | 0.27924 | 0.15564 | -0.18768 | 122.2824 | -0.073243 | 122.525 | 122.5708 | -0.004578 | 122.2778 | 0 | 0.24261 | 122.3373 | 122.7448 | 122.6166 | 122.5479 | 122.525 | 122.6212 | 122.6303 | 122.2778 | 122.5479 | 122.525 | 122.6303 | 122.6166 | 122.6212 | -0.33874 | -0.34332
1214.5156 | 122.7356 | -122.4564 | 0.16022 | 0.10765 | 0.017543 | 0.00138 | 0.047078 | -0.011916 | -0.0091259 | 0.017321 | -0.064087 | 0.13275 | -0.24719 | -0.036621 | -0.004578 | 0.009155 | 0 | 0.059509 | 0.19226 | -0.21973 | 122.2092 | -0.027466 | 122.3923 | 122.4197 | -0.16479 | 122.2366 | 0.032044 | 0.1831 | 122.4564 | 122.5159 | 122.4518 | 122.5891 | 122.3923 | 122.6486 | 122.4655 | 122.2366 | 122.5891 | 122.3923 | 122.4655 | 122.4518 | 122.6486 | -0.40741 | -0.37994
1216.2656 | 122.8271 | -122.4701 | 0.11902 | -0.25093 | 0.019038 | 0.0045844 | 0.044942 | -0.012984 | -0.0089123 | 0.016466 | -0.086975 | 0.15564 | -0.24719 | -0.041199 | 0.022888 | 0.018311 | 0.064087 | 0.10071 | 0.19684 | -0.21057 | 122.2229 | 0.036621 | 122.3831 | 122.4289 | -0.096131 | 122.2595 | 0.077819 | 0.16022 | 122.5342 | 122.5708 | 122.493 | 122.6257 | 122.3831 | 122.6669 | 122.4884 | 122.2595 | 122.6257 | 122.3831 | 122.4884 | 122.493 | 122.6669 | -0.36621 | -0.32959
1217.9375 | 122.7997 | -122.4838 | 0.15564 | -0.21278 | 0.016475 | 0.008216 | 0.046437 | -0.011061 | -0.010621 | 0.017107 | -0.032043 | 0.13275 | -0.2243 | 0.009155 | 0.050354 | 0.054932 | 0.022888 | 0.14191 | 0.1831 | -0.20599 | 122.2595 | -0.022889 | 122.4518 | 122.493 | -0.10529 | 122.2778 | 0.027465 | 0.19226 | 122.5067 | 122.6257 | 122.5342 | 122.6166 | 122.4518 | 122.6669 | 122.5388 | 122.2778 | 122.6166 | 122.4518 | 122.5388 | 122.5342 | 122.6669 | -0.37994 | -0.36163
1219.6562 | 122.731 | -122.493 | 0.15564 | 0.10002 | 0.018825 | 0.0060798 | 0.041097 | -0.01277 | -0.0076305 | 0.017321 | 0.032043 | 0.09613 | -0.19684 | 0.054932 | 0.10986 | 0.15564 | -0.14191 | 0.19226 | 0.14648 | -0.19684 | 122.2961 | -0.05951 | 122.525 | 122.5479 | -0.045777 | 122.2961 | -0.009156 | 0.22888 | 122.3511 | 122.6852 | 122.6028 | 122.5891 | 122.525 | 122.6395 | 122.6486 | 122.2961 | 122.5891 | 122.525 | 122.6486 | 122.6028 | 122.6395 | -0.35248 | -0.35248
1221.4062 | 122.85 | -122.4472 | 0.12817 | -0.2433 | 0.017329 | 0.0037298 | 0.044728 | -0.012984 | -0.010194 | 0.01668 | -0.082397 | 0.1236 | -0.24261 | -0.032043 | 0.027466 | 0.032043 | 0.068665 | 0.10986 | 0.20142 | -0.22888 | 122.2046 | -0.004578 | 122.3648 | 122.4152 | -0.10071 | 122.2183 | 0.073242 | 0.16022 | 122.5159 | 122.5571 | 122.4747 | 122.5708 | 122.3648 | 122.6486 | 122.4792 | 122.2183 | 122.5708 | 122.3648 | 122.4792 | 122.4747 | 122.6486 | -0.37079 | -0.35706
1223.0938 | 122.8363 | -122.4609 | 0.10529 | -0.1899 | 0.017116 | 0.003089 | 0.042165 | -0.010421 | -0.0072033 | 0.016893 | -0.073242 | 0.11902 | -0.22888 | -0.013733 | 0.041199 | 0.032043 | 0.064087 | 0.11902 | 0.20142 | -0.21057 | 122.2321 | 0.013733 | 122.3877 | 122.4472 | -0.064087 | 122.2504 | 0.09613 | 0.15564 | 122.525 | 122.58 | 122.5021 | 122.58 | 122.3877 | 122.6624 | 122.493 | 122.2504 | 122.58 | 122.3877 | 122.493 | 122.5021 | 122.6624 | -0.33417 | -0.31586
1224.8438 | 122.7859 | -122.4655 | 0.16022 | -0.1899 | 0.016475 | 0.0028754 | 0.040242 | -0.012557 | -0.0080579 | 0.017321 | 0.054932 | 0.091553 | -0.18768 | 0.10071 | 0.16479 | 0.16022 | -0.10986 | 0.26093 | 0.16022 | -0.17395 | 122.2778 | -0.068664 | 122.5204 | 122.5662 | 0.004578 | 122.2916 | 0 | 0.24261 | 122.3557 | 122.7264 | 122.6303 | 122.5571 | 122.5204 | 122.6257 | 122.6257 | 122.2916 | 122.5571 | 122.5204 | 122.6257 | 122.6303 | 122.6257 | -0.3479 | -0.33417
1226.5781 | 122.8226 | -122.4655 | 0.13733 | 0.084762 | 0.014125 | 0.0050116 | 0.042806 | -0.01512 | -0.0084851 | 0.019243 | -0.004578 | 0.10071 | -0.18768 | 0.027466 | 0.07782 | 0.11902 | -0.10529 | 0.15564 | 0.13733 | -0.17395 | 122.2778 | -0.036621 | 122.4609 | 122.493 | -0.059509 | 122.2916 | 0 | 0.1831 | 122.3602 | 122.6212 | 122.5433 | 122.5662 | 122.4609 | 122.6028 | 122.5845 | 122.2916 | 122.5662 | 122.4609 | 122.5845 | 122.5433 | 122.6028 | -0.32501 | -0.31128
1228.25 | 122.7951 | -122.4609 | 0.16479 | -0.12886 | 0.018611 | 0.0041572 | 0.040883 | -0.013411 | -0.0080579 | 0.017321 | 0.041199 | 0.10986 | -0.18768 | 0.086975 | 0.13275 | 0.16937 | -0.13275 | 0.23804 | 0.15564 | -0.18768 | 122.2733 | -0.054932 | 122.5021 | 122.5479 | -0.032044 | 122.2733 | -0.009155 | 0.22888 | 122.3282 | 122.699 | 122.5937 | 122.5708 | 122.5021 | 122.6166 | 122.6303 | 122.2733 | 122.5708 | 122.5021 | 122.6303 | 122.5937 | 122.6166 | -0.35248 | -0.35248
1229.9844 | 122.8134 | -122.4655 | 0.15106 | -0.25856 | 0.017329 | 0.0052252 | 0.043447 | -0.011275 | -0.0099805 | 0.01668 | 0.045776 | 0.091553 | -0.19226 | 0.050354 | 0.10071 | 0.11902 | -0.032043 | 0.19684 | 0.1831 | -0.19226 | 122.2733 | -0.059509 | 122.5113 | 122.5159 | -0.050354 | 122.2733 | 0.032043 | 0.23804 | 122.4335 | 122.6624 | 122.5662 | 122.5571 | 122.5113 | 122.6486 | 122.5845 | 122.2733 | 122.5571 | 122.5113 | 122.5845 | 122.5662 | 122.6486 | -0.34332 | -0.34332
1231.7344 | 122.7539 | -122.493 | 0.16937 | 0.038986 | 0.016475 | 0.0073614 | 0.049215 | -0.012343 | -0.0082715 | 0.018175 | -0.041199 | 0.13733 | -0.23804 | -0.013733 | -0.004578 | 0.027466 | 0.004578 | 0.073242 | 0.17853 | -0.21057 | 122.2549 | -0.032044 | 122.4518 | 122.4792 | -0.17395 | 122.2824 | 0.009155 | 0.19684 | 122.4976 | 122.5662 | 122.4884 | 122.6303 | 122.4518 | 122.6715 | 122.5204 | 122.2824 | 122.6303 | 122.4518 | 122.5204 | 122.4884 | 122.6715 | -0.40741 | -0.37994
1233.4844 | 122.7722 | -122.4701 | 0.14648 | 0.092392 | 0.016475 | 0.0028754 | 0.042165 | -0.013198 | -0.0067761 | 0.016893 | 0.004578 | 0.086975 | -0.20599 | 0.032043 | 0.082397 | 0.12817 | -0.12817 | 0.17853 | 0.16022 | -0.16937 | 122.2641 | -0.059509 | 122.4747 | 122.5021 | -0.064087 | 122.3007 | 0.013733 | 0.21057 | 122.3419 | 122.6486 | 122.5525 | 122.5571 | 122.4747 | 122.6303 | 122.5983 | 122.3007 | 122.5571 | 122.4747 | 122.5983 | 122.5525 | 122.6303 | -0.35248 | -0.31586
1235.1562 | 122.7127 | -122.5113 | 0.16022 | 0.22209 | 0.016475 | 0.0060798 | 0.04601 | -0.013839 | -0.0072033 | 0.018389 | -0.041199 | 0.11902 | -0.23804 | 0.032043 | 0.073242 | 0.10986 | -0.10986 | 0.15106 | 0.16022 | -0.18768 | 122.2733 | -0.041198 | 122.4701 | 122.5433 | -0.086975 | 122.3236 | 0 | 0.19684 | 122.4014 | 122.6624 | 122.5845 | 122.6303 | 122.4701 | 122.6715 | 122.6212 | 122.3236 | 122.6303 | 122.4701 | 122.6212 | 122.5845 | 122.6715 | -0.39825 | -0.3479
1236.8906 | 122.8363 | -122.4609 | 0.13733 | 0.061874 | 0.016475 | 0.0043708 | 0.039174 | -0.01277 | -0.0061353 | 0.016039 | -0.022888 | 0.11444 | -0.19684 | 0.022888 | 0.082397 | 0.10529 | -0.082397 | 0.17395 | 0.14648 | -0.19684 | 122.2641 | -0.022888 | 122.438 | 122.4838 | -0.054932 | 122.2641 | 0.009155 | 0.17395 | 122.3785 | 122.6349 | 122.5433 | 122.5754 | 122.438 | 122.6074 | 122.5662 | 122.2641 | 122.5754 | 122.438 | 122.5662 | 122.5433 | 122.6074 | -0.33417 | -0.33417
1238.6406 | 122.8409 | -122.4609 | 0.14648 | 0.023727 | 0.017116 | 0.0033026 | 0.043874 | -0.011702 | -0.0072033 | 0.01903 | -0.022888 | 0.10529 | -0.1831 | 0.027466 | 0.082397 | 0.10071 | -0.082397 | 0.16479 | 0.16022 | -0.20142 | 122.2778 | -0.041198 | 122.438 | 122.4884 | -0.064087 | 122.2595 | 0.013733 | 0.16022 | 122.3785 | 122.6257 | 122.5433 | 122.5662 | 122.438 | 122.6212 | 122.5616 | 122.2595 | 122.5662 | 122.438 | 122.5616 | 122.5433 | 122.6212 | -0.32959 | -0.3479
1240.375 | 122.7081 | -122.525 | 0.16479 | 0.1992 | 0.016047 | 0.0060798 | 0.046224 | -0.008498 | -0.0078443 | 0.01668 | 0.064087 | 0.10071 | -0.1831 | 0.09613 | 0.1236 | 0.16479 | -0.19226 | 0.23346 | 0.15106 | -0.16937 | 122.3419 | -0.064087 | 122.5891 | 122.6212 | -0.041199 | 122.3557 | -0.013733 | 0.24719 | 122.3328 | 122.7585 | 122.6486 | 122.6257 | 122.5891 | 122.6761 | 122.6898 | 122.3557 | 122.6257 | 122.5891 | 122.6898 | 122.6486 | 122.6761 | -0.3479 | -0.33417
1242.0625 | 122.8271 | -122.4976 | 0.14648 | -0.25093 | 0.015193 | 0.0071478 | 0.045156 | -0.012984 | -0.011476 | 0.017321 | -0.068665 | 0.13733 | -0.24261 | -0.045776 | 0.018311 | 0.022888 | 0.082397 | 0.10071 | 0.18768 | -0.20599 | 122.2549 | -0.009155 | 122.4289 | 122.4518 | -0.12817 | 122.2916 | 0.041199 | 0.17395 | 122.58 | 122.5983 | 122.5159 | 122.6349 | 122.4289 | 122.6852 | 122.5204 | 122.2916 | 122.6349 | 122.4289 | 122.5204 | 122.5159 | 122.6852 | -0.3891 | -0.35248
1243.8438 | 122.8546 | -122.4747 | 0.14191 | -0.25093 | 0.015193 | 0.0018072 | 0.042592 | -0.012343 | -0.0084851 | 0.017534 | -0.073242 | 0.14191 | -0.25177 | -0.036621 | 0.018311 | 0.036621 | 0.068665 | 0.10986 | 0.19684 | -0.21515 | 122.2229 | 0 | 122.4014 | 122.438 | -0.1236 | 122.2595 | 0.054931 | 0.17853 | 122.5433 | 122.5845 | 122.493 | 122.6166 | 122.4014 | 122.6715 | 122.5113 | 122.2595 | 122.6166 | 122.4014 | 122.5113 | 122.493 | 122.6715 | -0.39368 | -0.35706
1245.625 | 122.8226 | -122.493 | 0.14191 | 0.054245 | 0.014979 | 0.0060798 | 0.040029 | -0.012984 | -0.0082715 | 0.01668 | -0.013733 | 0.10529 | -0.19684 | 0.027466 | 0.073242 | 0.11444 | -0.091553 | 0.15564 | 0.17395 | -0.19226 | 122.2961 | -0.036621 | 122.4792 | 122.5204 | -0.068665 | 122.3007 | 0.032043 | 0.18311 | 122.4014 | 122.6486 | 122.5662 | 122.5983 | 122.4792 | 122.6669 | 122.6074 | 122.3007 | 122.5983 | 122.4792 | 122.6074 | 122.5662 | 122.6669 | -0.33875 | -0.33417
1247.2969 | 122.818 | -122.4747 | 0.13733 | -0.21278 | 0.01562 | 0.0039436 | 0.042379 | -0.01277 | -0.010194 | 0.01903 | 0.032043 | 0.10529 | -0.1831 | 0.068665 | 0.091553 | 0.11902 | -0.032043 | 0.21515 | 0.16937 | -0.19684 | 122.2916 | -0.032043 | 122.5067 | 122.5433 | -0.045776 | 122.2778 | 0.032044 | 0.21515 | 122.4426 | 122.6898 | 122.5662 | 122.58 | 122.5067 | 122.644 | 122.5937 | 122.2778 | 122.58 | 122.5067 | 122.5937 | 122.5662 | 122.644 | -0.32043 | -0.33417
1249.0312 | 122.7264 | -122.5204 | 0.15564 | 0.0084684 | 0.016475 | 0.0077888 | 0.047292 | -0.011916 | -0.01169 | 0.017962 | -0.009155 | 0.13275 | -0.23346 | 0.004578 | 0.036621 | 0.036621 | -0.009155 | 0.10529 | 0.18768 | -0.21973 | 122.287 | -0.022889 | 122.5113 | 122.525 | -0.11902 | 122.3007 | 0.032043 | 0.2243 | 122.5113 | 122.6257 | 122.5571 | 122.6532 | 122.5113 | 122.7081 | 122.5571 | 122.3007 | 122.6532 | 122.5113 | 122.5571 | 122.5571 | 122.7081 | -0.3891 | -0.37537
1250.7188 | 122.7173 | -122.5159 | 0.19226 | 0.15343 | 0.018397 | 0.0058662 | 0.045583 | -0.0089252 | -0.010194 | 0.01967 | 0.032043 | 0.10529 | -0.20142 | 0.059509 | 0.10986 | 0.15564 | -0.14648 | 0.18768 | 0.15106 | -0.1831 | 122.3145 | -0.086975 | 122.5479 | 122.5754 | -0.082398 | 122.3328 | -0.041199 | 0.23346 | 122.3694 | 122.7036 | 122.6257 | 122.6212 | 122.5479 | 122.6669 | 122.6715 | 122.3328 | 122.6212 | 122.5479 | 122.6715 | 122.6257 | 122.6669 | -0.39368 | -0.37537
1252.4531 | 122.8409 | -122.4792 | 0.12817 | 0.031357 | 0.016475 | 0.0060798 | 0.041097 | -0.010848 | -0.0072033 | 0.017534 | -0.022888 | 0.10986 | -0.19684 | 0 | 0.086975 | 0.10529 | -0.07782 | 0.16937 | 0.17395 | -0.20142 | 122.2824 | -0.018311 | 122.4564 | 122.4792 | -0.041199 | 122.2778 | 0.045776 | 0.17395 | 122.4014 | 122.6486 | 122.5662 | 122.5891 | 122.4564 | 122.6532 | 122.5845 | 122.2778 | 122.5891 | 122.4564 | 122.5845 | 122.5662 | 122.6532 | -0.32501 | -0.32959
1254.1875 | 122.7264 | -122.5296 | 0.16937 | 0.15343 | 0.018184 | 0.0075752 | 0.045583 | -0.014479 | -0.0072033 | 0.017534 | 0.045776 | 0.10986 | -0.19684 | 0.082397 | 0.10529 | 0.16022 | -0.16022 | 0.21057 | 0.13275 | -0.16479 | 122.3328 | -0.05951 | 122.5754 | 122.612 | -0.064087 | 122.3648 | -0.036622 | 0.24261 | 122.3694 | 122.7402 | 122.6349 | 122.6395 | 122.5754 | 122.6624 | 122.6898 | 122.3648 | 122.6395 | 122.5754 | 122.6898 | 122.6349 | 122.6624 | -0.36621 | -0.33417
1255.9219 | 122.8409 | -122.4884 | 0.10986 | 0.016098 | 0.017543 | 0.0037298 | 0.04067 | -0.013411 | -0.0084851 | 0.017748 | -0.009155 | 0.10986 | -0.19226 | 0.027466 | 0.07782 | 0.10986 | -0.09613 | 0.16479 | 0.14648 | -0.18768 | 122.2961 | 0 | 122.4792 | 122.5159 | -0.032043 | 122.3007 | 0.036621 | 0.18311 | 122.3923 | 122.6532 | 122.5662 | 122.5983 | 122.4792 | 122.6349 | 122.5983 | 122.3007 | 122.5983 | 122.4792 | 122.5983 | 122.5662 | 122.6349 | -0.30212 | -0.29755
1257.6875 | 122.7264 | -122.5204 | 0.17853 | -0.060196 | 0.017329 | 0.0022346 | 0.04836 | -0.011061 | -0.0097669 | 0.017962 | 0.004578 | 0.1236 | -0.22888 | 0.027466 | 0.054932 | 0.073242 | -0.027466 | 0.13275 | 0.16937 | -0.20599 | 122.2916 | -0.054932 | 122.525 | 122.5479 | -0.1236 | 122.3145 | -0.009155 | 0.23346 | 122.493 | 122.6532 | 122.5754 | 122.644 | 122.525 | 122.6898 | 122.5937 | 122.3145 | 122.644 | 122.525 | 122.5937 | 122.5754 | 122.6898 | -0.40741 | -0.38452
1259.375 | 122.8592 | -122.4655 | 0.13733 | -0.22804 | 0.017543 | 0.0024482 | 0.040242 | -0.012557 | -0.0091259 | 0.015398 | -0.07782 | 0.13733 | -0.22888 | -0.022888 | 0.027466 | 0.036621 | 0.059509 | 0.10986 | 0.20599 | -0.24261 | 122.2366 | 0 | 122.3877 | 122.4426 | -0.10986 | 122.2229 | 0.068665 | 0.15106 | 122.525 | 122.5754 | 122.493 | 122.6028 | 122.3877 | 122.6715 | 122.5021 | 122.2229 | 122.6028 | 122.3877 | 122.5021 | 122.493 | 122.6715 | -0.36621 | -0.37994
1261.0781 | 122.7905 | -122.4884 | 0.14191 | -0.14412 | 0.019679 | 0.004798 | 0.045797 | -0.011061 | -0.0095531 | 0.017748 | -0.022888 | 0.13733 | -0.24261 | 0.027466 | 0.036621 | 0.059509 | 0.009155 | 0.15564 | 0.20142 | -0.20599 | 122.2458 | -0.004578 | 122.4655 | 122.5159 | -0.10529 | 122.2824 | 0.059509 | 0.21973 | 122.4976 | 122.644 | 122.525 | 122.6257 | 122.4655 | 122.6898 | 122.5479 | 122.2824 | 122.6257 | 122.4655 | 122.5479 | 122.525 | 122.6898 | -0.38452 | -0.3479
1262.7656 | 122.818 | -122.4884 | 0.1236 | -0.060196 | 0.014552 | 0.0050116 | 0.040883 | -0.014052 | -0.0048535 | 0.018175 | 0.009155 | 0.10986 | -0.1831 | 0.059509 | 0.11902 | 0.17853 | -0.1236 | 0.22888 | 0.15106 | -0.18768 | 122.3053 | -0.013733 | 122.4976 | 122.5479 | -0.004577 | 122.3007 | 0.027466 | 0.19226 | 122.3648 | 122.7173 | 122.6074 | 122.5983 | 122.4976 | 122.6395 | 122.6669 | 122.3007 | 122.5983 | 122.4976 | 122.6669 | 122.6074 | 122.6395 | -0.3067 | -0.31128
1264.4688 | 122.7173 | -122.5113 | 0.16479 | 0.1992 | 0.016902 | 0.0075752 | 0.044942 | -0.01277 | -0.0069897 | 0.017962 | 0.041199 | 0.07782 | -0.20599 | 0.068665 | 0.11444 | 0.16479 | -0.17853 | 0.22888 | 0.13733 | -0.17853 | 122.3053 | -0.086975 | 122.5525 | 122.58 | -0.050354 | 122.3328 | -0.027466 | 0.24719 | 122.3328 | 122.7402 | 122.6257 | 122.5891 | 122.5525 | 122.6486 | 122.6761 | 122.3328 | 122.5891 | 122.5525 | 122.6761 | 122.6257 | 122.6486 | -0.37079 | -0.34332
1266.2031 | 122.7539 | -122.5113 | 0.16479 | 0.11528 | 0.013057 | 0.0018072 | 0.041951 | -0.011702 | -0.0065625 | 0.01903 | 0.018311 | 0.082397 | -0.1831 | 0.064087 | 0.09613 | 0.15106 | -0.15564 | 0.19226 | 0.15106 | -0.17853 | 122.3282 | -0.082398 | 122.5296 | 122.5754 | -0.068665 | 122.3328 | -0.013733 | 0.20142 | 122.3557 | 122.7036 | 122.6074 | 122.5937 | 122.5296 | 122.6624 | 122.6624 | 122.3328 | 122.5937 | 122.5296 | 122.6624 | 122.6074 | 122.6624 | -0.3479 | -0.34332
1267.9531 | 122.8592 | -122.5113 | 0.13733 | -0.2433 | 0.016688 | 0.010566 | 0.046224 | -0.011702 | -0.011049 | 0.01668 | -0.068665 | 0.15106 | -0.23346 | -0.022888 | -0.004578 | 0.027466 | 0.073242 | 0.09613 | 0.21973 | -0.2243 | 122.2778 | 0.013733 | 122.4426 | 122.4884 | -0.14191 | 122.287 | 0.082398 | 0.16479 | 122.5845 | 122.6074 | 122.5067 | 122.6624 | 122.4426 | 122.731 | 122.5388 | 122.287 | 122.6624 | 122.4426 | 122.5388 | 122.5067 | 122.731 | -0.37079 | -0.36163
1269.625 | 122.7585 | -122.4976 | 0.14648 | 0.054245 | 0.02032 | 0.0084296 | 0.047933 | -0.0097796 | -0.011476 | 0.014971 | -0.036621 | 0.12817 | -0.23804 | -0.032043 | -0.013733 | 0.013733 | 0.041199 | 0.073242 | 0.19684 | -0.21057 | 122.2595 | -0.01831 | 122.4609 | 122.4655 | -0.16022 | 122.287 | 0.050354 | 0.20142 | 122.5388 | 122.5708 | 122.4838 | 122.6257 | 122.4609 | 122.6944 | 122.5113 | 122.287 | 122.6257 | 122.4609 | 122.5113 | 122.4838 | 122.6944 | -0.38452 | -0.35706
1271.3438 | 122.7951 | -122.493 | 0.13733 | -0.12123 | 0.019038 | 0.0069342 | 0.039174 | -0.011489 | -0.010194 | 0.016039 | 0.045776 | 0.10529 | -0.18768 | 0.09613 | 0.15106 | 0.1831 | -0.11444 | 0.25635 | 0.15564 | -0.18768 | 122.3053 | -0.032043 | 122.5388 | 122.5891 | 0.013733 | 122.3053 | 0.018311 | 0.23346 | 122.3785 | 122.7493 | 122.644 | 122.5983 | 122.5388 | 122.6486 | 122.6761 | 122.3053 | 122.5983 | 122.5388 | 122.6761 | 122.644 | 122.6486 | -0.32501 | -0.32501
1273.0156 | 122.7127 | -122.5342 | 0.15106 | 0.1992 | 0.017116 | 0.0071478 | 0.047506 | -0.013198 | -0.0091259 | 0.019243 | 0.050354 | 0.09613 | -0.19226 | 0.07782 | 0.11444 | 0.17853 | -0.17853 | 0.2243 | 0.15106 | -0.17853 | 122.3419 | -0.054932 | 122.5845 | 122.612 | -0.036621 | 122.3557 | 0 | 0.24261 | 122.3557 | 122.7585 | 122.6486 | 122.6303 | 122.5845 | 122.6852 | 122.7127 | 122.3557 | 122.6303 | 122.5845 | 122.7127 | 122.6486 | 122.6852 | -0.34332 | -0.32959
1274.7031 | 122.7722 | -122.5204 | 0.14191 | 0.00083945 | 0.016047 | 0.0043708 | 0.04601 | -0.010207 | -0.0093395 | 0.01668 | -0.07782 | 0.14648 | -0.2243 | -0.045776 | -0.027466 | 0.009155 | 0.018311 | 0.041199 | 0.18768 | -0.2243 | 122.2961 | 0.004577 | 122.4426 | 122.4747 | -0.16937 | 122.2961 | 0.045776 | 0.14648 | 122.5388 | 122.5616 | 122.493 | 122.6669 | 122.4426 | 122.7081 | 122.5296 | 122.2961 | 122.6669 | 122.4426 | 122.5296 | 122.493 | 122.7081 | -0.36621 | -0.36621
1276.375 | 122.7997 | -122.5113 | 0.14191 | -0.12123 | 0.01562 | -0.0016106 | 0.038961 | -0.01213 | -0.0076305 | 0.017321 | 0 | 0.091553 | -0.17853 | 0.022888 | 0.068665 | 0.11902 | -0.09613 | 0.17395 | 0.15106 | -0.17853 | 122.3328 | -0.050354 | 122.5113 | 122.5342 | -0.073242 | 122.3328 | 0.009155 | 0.17853 | 122.4152 | 122.6852 | 122.58 | 122.6028 | 122.5113 | 122.6624 | 122.6303 | 122.3328 | 122.6028 | 122.5113 | 122.6303 | 122.58 | 122.6624 | -0.32044 | -0.32044
1278.0625 | 122.7356 | -122.5296 | 0.15564 | 0.22972 | 0.01797 | 0.0060798 | 0.04366 | -0.011702 | -0.0076305 | 0.018602 | -0.032043 | 0.1236 | -0.21515 | 0.013733 | 0.054932 | 0.10071 | -0.086975 | 0.13733 | 0.16479 | -0.20142 | 122.3145 | -0.032044 | 122.4976 | 122.5433 | -0.10071 | 122.3282 | 0.009155 | 0.18311 | 122.4426 | 122.6669 | 122.5845 | 122.6532 | 122.4976 | 122.6944 | 122.6303 | 122.3282 | 122.6532 | 122.4976 | 122.6303 | 122.5845 | 122.6944 | -0.37079 | -0.35706
1279.7344 | 122.7081 | -122.5204 | 0.16937 | 0.20683 | 0.015834 | 0.0037298 | 0.043233 | -0.011702 | -0.0082715 | 0.018816 | 0.041199 | 0.09613 | -0.19226 | 0.073242 | 0.11444 | 0.17395 | -0.1831 | 0.21515 | 0.14648 | -0.16937 | 122.3282 | -0.073243 | 122.5616 | 122.5937 | -0.054932 | 122.3511 | -0.022889 | 0.23346 | 122.3373 | 122.7356 | 122.6349 | 122.6166 | 122.5616 | 122.6669 | 122.6944 | 122.3511 | 122.6166 | 122.5616 | 122.6944 | 122.6349 | 122.6669 | -0.36163 | -0.33875
1281.4219 | 122.8363 | -122.5159 | 0.13733 | 0.046615 | 0.016902 | 0.0056524 | 0.039601 | -0.013411 | -0.0076305 | 0.017107 | -0.022888 | 0.11902 | -0.20142 | 0.018311 | 0.068665 | 0.09613 | -0.091553 | 0.16937 | 0.16479 | -0.20599 | 122.3145 | -0.01831 | 122.493 | 122.5342 | -0.068664 | 122.3099 | 0.027466 | 0.17853 | 122.4243 | 122.6852 | 122.5845 | 122.6349 | 122.493 | 122.6807 | 122.612 | 122.3099 | 122.6349 | 122.493 | 122.612 | 122.5845 | 122.6807 | -0.33875 | -0.34332
1283.0938 | 122.731 | -122.5159 | 0.16937 | 0.19157 | 0.016902 | 0.0043708 | 0.047719 | -0.012557 | -0.0076305 | 0.016466 | -0.032043 | 0.13275 | -0.2243 | 0.009155 | 0.050354 | 0.09613 | -0.086975 | 0.1236 | 0.17395 | -0.20599 | 122.2916 | -0.036622 | 122.4838 | 122.525 | -0.11902 | 122.3099 | 0.004577 | 0.19226 | 122.4289 | 122.6395 | 122.5662 | 122.6486 | 122.4838 | 122.6898 | 122.612 | 122.3099 | 122.6486 | 122.4838 | 122.612 | 122.5662 | 122.6898 | -0.39368 | -0.37537
1284.7656 | 122.7448 | -122.5113 | 0.17395 | 0.1992 | 0.016261 | 0.003089 | 0.045797 | -0.0097796 | -0.011903 | 0.017534 | -0.041199 | 0.13275 | -0.2243 | 0.022888 | 0.050354 | 0.09613 | -0.086975 | 0.13733 | 0.16479 | -0.1831 | 122.287 | -0.041199 | 122.4701 | 122.5342 | -0.1236 | 122.3282 | -0.009155 | 0.18311 | 122.4243 | 122.6486 | 122.5616 | 122.644 | 122.4701 | 122.6761 | 122.6074 | 122.3282 | 122.644 | 122.4701 | 122.6074 | 122.5616 | 122.6761 | -0.39825 | -0.35706
1286.4375 | 122.7814 | -122.5204 | 0.14191 | 0.11528 | 0.014552 | 0.003089 | 0.041524 | -0.014266 | -0.0072033 | 0.017321 | 0.004578 | 0.10071 | -0.20599 | 0.022888 | 0.068665 | 0.10986 | -0.12817 | 0.1831 | 0.13733 | -0.19226 | 122.3145 | -0.041199 | 122.525 | 122.5433 | -0.073242 | 122.3282 | -0.004578 | 0.21057 | 122.3923 | 122.7036 | 122.5891 | 122.6212 | 122.525 | 122.6578 | 122.6303 | 122.3282 | 122.6212 | 122.525 | 122.6303 | 122.5891 | 122.6578 | -0.3479 | -0.33417
1288.1094 | 122.8271 | -122.493 | 0.14648 | -0.15175 | 0.018397 | 0.0043708 | 0.04131 | -0.013411 | -0.0080579 | 0.016039 | 0.032043 | 0.10529 | -0.19684 | 0.082397 | 0.13275 | 0.16937 | -0.13275 | 0.26093 | 0.16937 | -0.18768 | 122.2961 | -0.041198 | 122.525 | 122.5754 | -0.013733 | 122.3053 | 0.022889 | 0.22888 | 122.3602 | 122.7539 | 122.6257 | 122.5983 | 122.525 | 122.6624 | 122.6624 | 122.3053 | 122.5983 | 122.525 | 122.6624 | 122.6257 | 122.6624 | -0.34332 | -0.33417
1289.7812 | 122.8592 | -122.5067 | 0.13733 | -0.029679 | 0.014979 | 0.0015936 | 0.041097 | -0.014907 | -0.0052807 | 0.017748 | -0.022888 | 0.10986 | -0.20142 | 0.041199 | 0.082397 | 0.13733 | -0.10071 | 0.18768 | 0.15564 | -0.18768 | 122.3053 | -0.027466 | 122.4838 | 122.5479 | -0.054932 | 122.319 | 0.018311 | 0.17853 | 122.406 | 122.6944 | 122.5891 | 122.6166 | 122.4838 | 122.6624 | 122.644 | 122.319 | 122.6166 | 122.4838 | 122.644 | 122.5891 | 122.6624 | -0.33875 | -0.32501
1291.4688 | 122.8409 | -122.5113 | 0.14191 | 0.092392 | 0.016688 | 0.0054388 | 0.042165 | -0.013198 | -0.0095531 | 0.015398 | 0 | 0.10986 | -0.19684 | 0.022888 | 0.068665 | 0.11902 | -0.10071 | 0.16937 | 0.15564 | -0.20142 | 122.3145 | -0.032044 | 122.5113 | 122.5342 | -0.073242 | 122.3099 | 0.013733 | 0.19684 | 122.4106 | 122.6807 | 122.58 | 122.6212 | 122.5113 | 122.6669 | 122.6303 | 122.3099 | 122.6212 | 122.5113 | 122.6303 | 122.58 | 122.6669 | -0.33875 | -0.34332
1293.1406 | 122.7768 | -122.525 | 0.18768 | 0.092392 | 0.018397 | 0.0094978 | 0.049215 | -0.011916 | -0.010408 | 0.019884 | -0.045776 | 0.13733 | -0.23804 | -0.018311 | -0.009155 | 0.022888 | 0.018311 | 0.07782 | 0.1831 | -0.2243 | 122.287 | -0.050354 | 122.4792 | 122.5067 | -0.19684 | 122.3007 | -0.004578 | 0.19226 | 122.5433 | 122.6028 | 122.5159 | 122.6624 | 122.4792 | 122.7081 | 122.5479 | 122.3007 | 122.6624 | 122.4792 | 122.5479 | 122.5159 | 122.7081 | -0.42572 | -0.41199
1294.8438 | 122.8455 | -122.4976 | 0.11902 | -0.12886 | 0.016047 | 0.0077888 | 0.03832 | -0.015548 | -0.0067761 | 0.019243 | 0.022888 | 0.10529 | -0.22888 | 0.086975 | 0.13733 | 0.16937 | -0.13733 | 0.25177 | 0.16479 | -0.1831 | 122.2687 | -0.013733 | 122.5204 | 122.5845 | 0.01831 | 122.3145 | 0.045776 | 0.25177 | 122.3602 | 122.7493 | 122.6349 | 122.6028 | 122.5204 | 122.6624 | 122.6669 | 122.3145 | 122.6028 | 122.5204 | 122.6669 | 122.6349 | 122.6624 | -0.3479 | -0.30212
1296.5156 | 122.85 | -122.4976 | 0.14648 | -0.01442 | 0.017116 | 0.00138 | 0.042806 | -0.013839 | -0.0076305 | 0.015825 | -0.009155 | 0.1236 | -0.20599 | 0.054932 | 0.091553 | 0.1236 | -0.09613 | 0.18768 | 0.16937 | -0.17853 | 122.2916 | -0.022888 | 122.4884 | 122.5525 | -0.054931 | 122.319 | 0.022889 | 0.19684 | 122.4014 | 122.6852 | 122.5891 | 122.6212 | 122.4884 | 122.6669 | 122.6212 | 122.319 | 122.6212 | 122.4884 | 122.6212 | 122.5891 | 122.6669 | -0.35248 | -0.32501
1298.2188 | 122.8958 | -122.4976 | 0.15564 | -0.2433 | 0.016261 | 0.0050116 | 0.045369 | -0.012984 | -0.0086987 | 0.015612 | -0.022888 | 0.11902 | -0.23346 | 0.013733 | 0.036621 | 0.050354 | 0.022888 | 0.13733 | 0.18768 | -0.19684 | 122.2641 | -0.036621 | 122.4747 | 122.5113 | -0.11902 | 122.3007 | 0.032043 | 0.21057 | 122.5204 | 122.6349 | 122.5342 | 122.6166 | 122.4747 | 122.6852 | 122.5479 | 122.3007 | 122.6166 | 122.4747 | 122.5479 | 122.5342 | 122.6852 | -0.3891 | -0.35248
1299.9531 | 122.7493 | -122.5296 | 0.16479 | 0.15343 | 0.016047 | 0.0022346 | 0.045583 | -0.010848 | -0.010194 | 0.017534 | 0.032043 | 0.086975 | -0.20142 | 0.082397 | 0.11444 | 0.16937 | -0.16479 | 0.21515 | 0.14191 | -0.17395 | 122.3282 | -0.07782 | 122.5616 | 122.612 | -0.050354 | 122.3557 | -0.022888 | 0.23346 | 122.3648 | 122.7448 | 122.644 | 122.6166 | 122.5616 | 122.6715 | 122.699 | 122.3557 | 122.6166 | 122.5616 | 122.699 | 122.644 | 122.6715 | -0.36621 | -0.33874
1301.625 | 122.7905 | -122.5113 | 0.16937 | 0.12291 | 0.01562 | 0.0067206 | 0.047933 | -0.012557 | -0.010621 | 0.018816 | -0.07782 | 0.13275 | -0.24719 | -0.022888 | -0.013733 | 0.022888 | -0.004578 | 0.059509 | 0.16937 | -0.21973 | 122.2641 | -0.036622 | 122.4335 | 122.4884 | -0.18311 | 122.2916 | 0 | 0.16937 | 122.5067 | 122.5708 | 122.4976 | 122.644 | 122.4335 | 122.6807 | 122.5342 | 122.2916 | 122.644 | 122.4335 | 122.5342 | 122.4976 | 122.6807 | -0.41656 | -0.3891
1303.3125 | 122.7676 | -122.5159 | 0.15564 | 0.061874 | 0.017329 | 0.0058662 | 0.048574 | -0.012557 | -0.0095531 | 0.017321 | -0.059509 | 0.14648 | -0.23346 | -0.032043 | -0.013733 | 0.022888 | 0.027466 | 0.054932 | 0.19226 | -0.21973 | 122.2824 | -0.009156 | 122.4564 | 122.4838 | -0.16937 | 122.2961 | 0.036621 | 0.17395 | 122.5433 | 122.5708 | 122.5021 | 122.6624 | 122.4564 | 122.7081 | 122.5388 | 122.2961 | 122.6624 | 122.4564 | 122.5388 | 122.5021 | 122.7081 | -0.3891 | -0.37537
1305.0312 | 122.8592 | -122.5021 | 0.1236 | 0.0084684 | 0.016261 | 0.0037298 | 0.036184 | -0.011489 | -0.0072033 | 0.017534 | -0.018311 | 0.1236 | -0.21515 | 0.022888 | 0.10071 | 0.13275 | -0.10071 | 0.17853 | 0.17395 | -0.20599 | 122.287 | 0 | 122.4838 | 122.525 | -0.022888 | 122.2961 | 0.050354 | 0.19684 | 122.4014 | 122.6807 | 122.6028 | 122.6257 | 122.4838 | 122.6761 | 122.6349 | 122.2961 | 122.6257 | 122.4838 | 122.6349 | 122.6028 | 122.6761 | -0.33875 | -0.32959
1306.7188 | 122.8592 | -122.493 | 0.14648 | 0.031357 | 0.015407 | 0.002021 | 0.040883 | -0.013625 | -0.0084851 | 0.015398 | -0.013733 | 0.10529 | -0.21057 | 0.013733 | 0.064087 | 0.09613 | -0.07782 | 0.16479 | 0.1831 | -0.18768 | 122.2824 | -0.041198 | 122.4792 | 122.5067 | -0.082397 | 122.3053 | 0.036621 | 0.19684 | 122.4152 | 122.6578 | 122.5571 | 122.5983 | 122.4792 | 122.6761 | 122.5891 | 122.3053 | 122.5983 | 122.4792 | 122.5891 | 122.5571 | 122.6761 | -0.35706 | -0.33417
1308.3906 | 122.731 | -122.5479 | 0.16937 | 0.21446 | 0.016047 | 0.0090704 | 0.047078 | -0.01213 | -0.0095531 | 0.015184 | 0.050354 | 0.082397 | -0.17853 | 0.091553 | 0.10529 | 0.16937 | -0.18768 | 0.21057 | 0.14191 | -0.16479 | 122.3694 | -0.086976 | 122.5983 | 122.6395 | -0.064087 | 122.3831 | -0.027466 | 0.22888 | 122.3602 | 122.7585 | 122.6532 | 122.6303 | 122.5983 | 122.6898 | 122.7173 | 122.3831 | 122.6303 | 122.5983 | 122.7173 | 122.6532 | 122.6898 | -0.3479 | -0.33417
1310.0625 | 122.7493 | -122.5296 | 0.16479 | 0.18394 | 0.016475 | 0.0075752 | 0.043447 | -0.01213 | -0.0078443 | 0.017321 | 0.059509 | 0.091553 | -0.1831 | 0.086975 | 0.11902 | 0.16479 | -0.1831 | 0.21057 | 0.13733 | -0.19226 | 122.3465 | -0.073242 | 122.5891 | 122.6166 | -0.045776 | 122.3373 | -0.027466 | 0.24261 | 122.3465 | 122.7402 | 122.6486 | 122.6212 | 122.5891 | 122.6669 | 122.6944 | 122.3373 | 122.6212 | 122.5891 | 122.6944 | 122.6486 | 122.6669 | -0.3479 | -0.35706
1311.7344 | 122.7493 | -122.5388 | 0.16937 | 0.15343 | 0.017116 | 0.0073614 | 0.043447 | -0.013839 | -0.0089123 | 0.016253 | 0.045776 | 0.086975 | -0.19684 | 0.086975 | 0.10986 | 0.16937 | -0.15564 | 0.20599 | 0.15564 | -0.16479 | 122.3419 | -0.082398 | 122.5845 | 122.6257 | -0.05951 | 122.374 | -0.013733 | 0.24261 | 122.3831 | 122.7448 | 122.6486 | 122.6257 | 122.5845 | 122.6944 | 122.7081 | 122.374 | 122.6257 | 122.5845 | 122.7081 | 122.6486 | 122.6944 | -0.36621 | -0.33417
1313.4062 | 122.8546 | -122.5067 | 0.13733 | -0.037308 | 0.01562 | 0.0050116 | 0.041097 | -0.013411 | -0.0084851 | 0.016039 | 0.004578 | 0.10529 | -0.19684 | 0.036621 | 0.10986 | 0.15106 | -0.11444 | 0.21515 | 0.17853 | -0.1831 | 122.3099 | -0.032043 | 122.5113 | 122.5433 | -0.027466 | 122.3236 | 0.041199 | 0.20142 | 122.3923 | 122.7219 | 122.6166 | 122.612 | 122.5113 | 122.6852 | 122.6578 | 122.3236 | 122.612 | 122.5113 | 122.6578 | 122.6166 | 122.6852 | -0.33417 | -0.32043
1315.0781 | 122.8409 | -122.525 | 0.14648 | -0.14412 | 0.01562 | 0.003089 | 0.042806 | -0.013625 | -0.011262 | 0.017748 | 0.032043 | 0.10529 | -0.20599 | 0.10071 | 0.11902 | 0.15106 | -0.10529 | 0.22888 | 0.17395 | -0.16479 | 122.319 | -0.041198 | 122.5571 | 122.6257 | -0.027465 | 122.3602 | 0.027466 | 0.23804 | 122.4197 | 122.7539 | 122.644 | 122.6303 | 122.5571 | 122.699 | 122.6761 | 122.3602 | 122.6303 | 122.5571 | 122.6761 | 122.644 | 122.699 | -0.35248 | -0.31128
1316.75 | 122.8134 | -122.5067 | 0.14191 | -0.1899 | 0.014125 | 0.0086432 | 0.042379 | -0.013839 | -0.0095531 | 0.017534 | 0.050354 | 0.10986 | -0.20599 | 0.09613 | 0.13275 | 0.16022 | -0.11902 | 0.23346 | 0.16022 | -0.16937 | 122.3007 | -0.032044 | 122.5571 | 122.6028 | -0.009156 | 122.3373 | 0.01831 | 0.25635 | 122.3877 | 122.7402 | 122.6395 | 122.6166 | 122.5571 | 122.6669 | 122.6669 | 122.3373 | 122.6166 | 122.5571 | 122.6669 | 122.6395 | 122.6669 | -0.3479 | -0.31128
1318.4844 | 122.7219 | -122.5662 | 0.17395 | 0.20683 | 0.014979 | 0.0026618 | 0.045156 | -0.011275 | -0.011262 | 0.018389 | 0.045776 | 0.07782 | -0.21057 | 0.082397 | 0.11902 | 0.17395 | -0.1831 | 0.20142 | 0.14191 | -0.16479 | 122.3557 | -0.09613 | 122.612 | 122.6486 | -0.054931 | 122.4014 | -0.032043 | 0.25635 | 122.3831 | 122.7676 | 122.6852 | 122.644 | 122.612 | 122.7081 | 122.7402 | 122.4014 | 122.644 | 122.612 | 122.7402 | 122.6852 | 122.7081 | -0.38452 | -0.33874
1320.1562 | 122.7768 | -122.5388 | 0.16022 | 0.13054 | 0.016902 | 0.0050116 | 0.04067 | -0.011275 | -0.0089123 | 0.017962 | 0.018311 | 0.086975 | -0.1831 | 0.054932 | 0.082397 | 0.12817 | -0.12817 | 0.16937 | 0.16022 | -0.19226 | 122.3557 | -0.073242 | 122.5571 | 122.5937 | -0.07782 | 122.3465 | 0 | 0.20142 | 122.4106 | 122.7081 | 122.6212 | 122.6257 | 122.5571 | 122.699 | 122.6669 | 122.3465 | 122.6257 | 122.5571 | 122.6669 | 122.6212 | 122.699 | -0.34332 | -0.35248
1321.8438 | 122.731 | -122.5708 | 0.17853 | 0.15343 | 0.014979 | 0.0058662 | 0.045583 | -0.011702 | -0.0067761 | 0.018389 | 0.045776 | 0.10529 | -0.18768 | 0.068665 | 0.10071 | 0.16937 | -0.16937 | 0.19226 | 0.15106 | -0.17853 | 122.3831 | -0.073242 | 122.6166 | 122.6395 | -0.07782 | 122.3923 | -0.027466 | 0.23346 | 122.4014 | 122.7631 | 122.6715 | 122.6761 | 122.6166 | 122.7219 | 122.7402 | 122.3923 | 122.6761 | 122.6166 | 122.7402 | 122.6715 | 122.7219 | -0.36621 | -0.35706
1323.5469 | 122.8271 | -122.5433 | 0.15106 | -0.1899 | 0.015834 | 0.0043708 | 0.041738 | -0.015761 | -0.0084851 | 0.01668 | 0.041199 | 0.10986 | -0.19684 | 0.10529 | 0.14191 | 0.16479 | -0.11902 | 0.25177 | 0.13733 | -0.17853 | 122.3465 | -0.041199 | 122.5845 | 122.6486 | -0.009155 | 122.3648 | -0.013733 | 0.23804 | 122.4243 | 122.7951 | 122.6852 | 122.6532 | 122.5845 | 122.6807 | 122.7081 | 122.3648 | 122.6532 | 122.5845 | 122.7081 | 122.6852 | 122.6807 | -0.3479 | -0.32959
1325.2188 | 122.8134 | -122.4976 | 0.16479 | -0.19753 | 0.015407 | 0.0062934 | 0.040883 | -0.013839 | -0.0089123 | 0.015398 | 0.050354 | 0.09613 | -0.21057 | 0.10529 | 0.12817 | 0.17853 | -0.11902 | 0.27008 | 0.14191 | -0.18768 | 122.287 | -0.068665 | 122.5479 | 122.6028 | -0.036621 | 122.3099 | -0.022888 | 0.26093 | 122.3785 | 122.7676 | 122.6257 | 122.5937 | 122.5479 | 122.6395 | 122.6761 | 122.3099 | 122.5937 | 122.5479 | 122.6761 | 122.6257 | 122.6395 | -0.37537 | -0.35248
1326.8906 | 122.8729 | -122.493 | 0.13733 | 0.069504 | 0.016475 | 0.0026618 | 0.04131 | -0.015334 | -0.0076305 | 0.018389 | -0.013733 | 0.086975 | -0.19684 | 0.050354 | 0.059509 | 0.11902 | -0.09613 | 0.16022 | 0.15106 | -0.20142 | 122.2961 | -0.050354 | 122.4792 | 122.5433 | -0.07782 | 122.2916 | 0.013733 | 0.18311 | 122.3969 | 122.6532 | 122.5525 | 122.58 | 122.4792 | 122.644 | 122.612 | 122.2916 | 122.58 | 122.4792 | 122.612 | 122.5525 | 122.644 | -0.33417 | -0.33875
1328.5781 | 122.7905 | -122.5159 | 0.15564 | 0.11528 | 0.01562 | 0.003089 | 0.049001 | -0.011275 | -0.011049 | 0.017962 | -0.068665 | 0.13733 | -0.24261 | -0.041199 | -0.004578 | 0.022888 | 0.009155 | 0.036621 | 0.19684 | -0.20599 | 122.2733 | -0.018311 | 122.4472 | 122.4747 | -0.16022 | 122.3099 | 0.041198 | 0.17395 | 122.525 | 122.5525 | 122.5113 | 122.6532 | 122.4472 | 122.7127 | 122.5388 | 122.3099 | 122.6532 | 122.4472 | 122.5388 | 122.5113 | 122.7127 | -0.39826 | -0.36163
1330.25 | 122.7768 | -122.5342 | 0.13733 | 0.13817 | 0.015834 | 0.0056524 | 0.042806 | -0.013625 | -0.0091259 | 0.01903 | 0.018311 | 0.086975 | -0.19684 | 0.054932 | 0.09613 | 0.13733 | -0.15106 | 0.18768 | 0.16022 | -0.17395 | 122.3373 | -0.050354 | 122.5525 | 122.5891 | -0.041199 | 122.3602 | 0.022888 | 0.21515 | 122.3831 | 122.7219 | 122.6303 | 122.6212 | 122.5525 | 122.6944 | 122.6715 | 122.3602 | 122.6212 | 122.5525 | 122.6715 | 122.6303 | 122.6944 | -0.33417 | -0.31128
1331.9844 | 122.8729 | -122.4976 | 0.14191 | -0.022049 | 0.016902 | 0.0073614 | 0.040456 | -0.014907 | -0.0074169 | 0.019243 | 0 | 0.11444 | -0.21515 | 0.036621 | 0.07782 | 0.13275 | -0.10071 | 0.21057 | 0.16022 | -0.1831 | 122.2824 | -0.027466 | 122.4976 | 122.5342 | -0.064087 | 122.3145 | 0.01831 | 0.21515 | 122.3969 | 122.7081 | 122.5754 | 122.612 | 122.4976 | 122.6578 | 122.6303 | 122.3145 | 122.612 | 122.4976 | 122.6303 | 122.5754 | 122.6578 | -0.35706 | -0.32501
1333.6562 | 122.8317 | -122.5388 | 0.16479 | -0.20515 | 0.016688 | 0.003089 | 0.042165 | -0.01512 | -0.0093395 | 0.015612 | 0.050354 | 0.09613 | -0.18768 | 0.10071 | 0.13275 | 0.16479 | -0.1236 | 0.24719 | 0.16479 | -0.21515 | 122.3511 | -0.068665 | 122.5891 | 122.6395 | -0.032044 | 122.3236 | 0 | 0.23804 | 122.4152 | 122.7859 | 122.6715 | 122.6349 | 122.5891 | 122.7036 | 122.7036 | 122.3236 | 122.6349 | 122.5891 | 122.7036 | 122.6715 | 122.7036 | -0.35248 | -0.37994
1335.3438 | 122.7631 | -122.5708 | 0.15564 | -0.083084 | 0.01562 | 0.0088568 | 0.04836 | -0.010634 | -0.014039 | 0.018175 | 0.004578 | 0.14191 | -0.2243 | 0.041199 | 0.050354 | 0.086975 | -0.013733 | 0.14648 | 0.1831 | -0.20599 | 122.3465 | -0.013733 | 122.5754 | 122.612 | -0.10529 | 122.3648 | 0.027465 | 0.22888 | 122.5571 | 122.7173 | 122.6212 | 122.7127 | 122.5754 | 122.7539 | 122.6578 | 122.3648 | 122.7127 | 122.5754 | 122.6578 | 122.6212 | 122.7539 | -0.37994 | -0.36163
1337.0156 | 122.7859 | -122.5342 | 0.16479 | 0.13054 | 0.018825 | 0.0054388 | 0.044728 | -0.011489 | -0.0095531 | 0.016253 | -0.068665 | 0.13275 | -0.23346 | -0.041199 | 0.009155 | 0.041199 | -0.009155 | 0.07782 | 0.17853 | -0.23346 | 122.3007 | -0.032044 | 122.4655 | 122.493 | -0.15564 | 122.3007 | 0.013733 | 0.16479 | 122.525 | 122.612 | 122.5433 | 122.6669 | 122.4655 | 122.7127 | 122.5754 | 122.3007 | 122.6669 | 122.4655 | 122.5754 | 122.5433 | 122.7127 | -0.39825 | -0.39825
1338.6875 | 122.7631 | -122.5525 | 0.17853 | -0.029679 | 0.015407 | 0.0077888 | 0.047506 | -0.010634 | -0.0099805 | 0.017321 | -0.022888 | 0.13733 | -0.22888 | 0.022888 | 0.041199 | 0.054932 | -0.027466 | 0.1236 | 0.17395 | -0.21515 | 122.3236 | -0.041199 | 122.5296 | 122.5754 | -0.13733 | 122.3373 | -0.004578 | 0.20599 | 122.525 | 122.6761 | 122.5937 | 122.6898 | 122.5296 | 122.7264 | 122.6074 | 122.3373 | 122.6898 | 122.5296 | 122.6074 | 122.5937 | 122.7264 | -0.40741 | -0.39368
1340.375 | 122.7585 | -122.5662 | 0.17395 | -0.060196 | 0.016688 | 0.0094978 | 0.044728 | -0.010848 | -0.0099805 | 0.016253 | 0 | 0.13275 | -0.25635 | 0.013733 | 0.059509 | 0.082397 | -0.045776 | 0.14648 | 0.19226 | -0.21057 | 122.3099 | -0.041199 | 122.5662 | 122.58 | -0.11444 | 122.3557 | 0.018311 | 0.25635 | 122.5204 | 122.7127 | 122.6257 | 122.699 | 122.5662 | 122.7585 | 122.6486 | 122.3557 | 122.699 | 122.5662 | 122.6486 | 122.6257 | 122.7585 | -0.4303 | -0.38452
1342.0469 | 122.7905 | -122.5479 | 0.16479 | 0.077133 | 0.018397 | 0.009284 | 0.045369 | -0.011702 | -0.0095531 | 0.01903 | -0.059509 | 0.13733 | -0.24719 | -0.050354 | 0.009155 | 0.027466 | 0.032043 | 0.064087 | 0.17853 | -0.21973 | 122.3007 | -0.027466 | 122.4884 | 122.4976 | -0.15564 | 122.3282 | 0.013733 | 0.18768 | 122.58 | 122.612 | 122.5571 | 122.6852 | 122.4884 | 122.7264 | 122.5754 | 122.3282 | 122.6852 | 122.4884 | 122.5754 | 122.5571 | 122.7264 | -0.41199 | -0.38452
1343.75 | 122.8455 | -122.5479 | 0.13733 | -0.18227 | 0.015407 | 0.0069342 | 0.038533 | -0.012984 | -0.0084851 | 0.016466 | 0.036621 | 0.11902 | -0.19226 | 0.082397 | 0.13733 | 0.16937 | -0.086975 | 0.23804 | 0.17395 | -0.1831 | 122.3557 | -0.01831 | 122.5845 | 122.6303 | 0 | 122.3648 | 0.036621 | 0.22888 | 122.4609 | 122.7859 | 122.6852 | 122.6669 | 122.5845 | 122.7219 | 122.7173 | 122.3648 | 122.6669 | 122.5845 | 122.7173 | 122.6852 | 122.7219 | -0.32959 | -0.32043
1345.4375 | 122.818 | -122.5342 | 0.16022 | 0.12291 | 0.018397 | 0.0062934 | 0.044515 | -0.012343 | -0.011262 | 0.018175 | -0.064087 | 0.14191 | -0.23346 | -0.054932 | -0.009155 | 0.022888 | 0.013733 | 0.068665 | 0.19226 | -0.2243 | 122.3007 | -0.01831 | 122.4701 | 122.4792 | -0.16937 | 122.3099 | 0.032044 | 0.16937 | 122.5479 | 122.6028 | 122.525 | 122.6761 | 122.4701 | 122.7264 | 122.5571 | 122.3099 | 122.6761 | 122.4701 | 122.5571 | 122.525 | 122.7264 | -0.39368 | -0.38452
1347.1406 | 122.7905 | -122.5525 | 0.16022 | 0.11528 | 0.014979 | 0.0054388 | 0.045583 | -0.009566 | -0.0072033 | 0.018602 | -0.054932 | 0.14648 | -0.2243 | -0.027466 | 0.013733 | 0.064087 | -0.050354 | 0.091553 | 0.18768 | -0.21973 | 122.3282 | -0.013733 | 122.4976 | 122.525 | -0.14648 | 122.3328 | 0.027466 | 0.16937 | 122.5021 | 122.644 | 122.5662 | 122.699 | 122.4976 | 122.7402 | 122.6166 | 122.3328 | 122.699 | 122.4976 | 122.6166 | 122.5662 | 122.7402 | -0.38452 | -0.37994
1348.8281 | 122.8867 | -122.5159 | 0.13733 | 0.016098 | 0.014979 | 0.010139 | 0.036611 | -0.01277 | -0.0072033 | 0.016253 | -0.032043 | 0.11902 | -0.2243 | -0.004578 | 0.073242 | 0.091553 | -0.073242 | 0.15564 | 0.16479 | -0.21515 | 122.2916 | -0.01831 | 122.4838 | 122.5113 | -0.064087 | 122.3007 | 0.027466 | 0.19226 | 122.4426 | 122.6715 | 122.5891 | 122.6349 | 122.4838 | 122.6807 | 122.6074 | 122.3007 | 122.6349 | 122.4838 | 122.6074 | 122.5891 | 122.6807 | -0.36163 | -0.35248
1350.5 | 122.8912 | -122.5159 | 0.1236 | 0.00083945 | 0.017116 | 0.0041572 | 0.039388 | -0.014693 | -0.010835 | 0.017962 | -0.036621 | 0.10071 | -0.18768 | 0.027466 | 0.059509 | 0.13733 | -0.082397 | 0.17853 | 0.16937 | -0.19684 | 122.3282 | -0.022888 | 122.4792 | 122.5433 | -0.064087 | 122.319 | 0.045777 | 0.15106 | 122.4335 | 122.6944 | 122.5754 | 122.6166 | 122.4792 | 122.6852 | 122.6532 | 122.319 | 122.6166 | 122.4792 | 122.6532 | 122.5754 | 122.6852 | -0.31128 | -0.32043
1352.1875 | 122.8592 | -122.525 | 0.12817 | -0.21278 | 0.014979 | 0.0039436 | 0.04131 | -0.013411 | -0.0078443 | 0.016466 | 0.018311 | 0.12817 | -0.20599 | 0.068665 | 0.09613 | 0.10986 | -0.027466 | 0.20142 | 0.16937 | -0.21973 | 122.319 | 0 | 122.5433 | 122.5937 | -0.032044 | 122.3053 | 0.041199 | 0.22431 | 122.4976 | 122.7264 | 122.6212 | 122.6532 | 122.5433 | 122.6944 | 122.6349 | 122.3053 | 122.6532 | 122.5433 | 122.6349 | 122.6212 | 122.6944 | -0.33417 | -0.3479
1353.8594 | 122.8455 | -122.5159 | 0.13733 | -0.10597 | 0.015193 | 0.0075752 | 0.040883 | -0.013411 | -0.0091259 | 0.017534 | 0.009155 | 0.11444 | -0.19226 | 0.073242 | 0.13733 | 0.16937 | -0.10986 | 0.23804 | 0.16479 | -0.18768 | 122.3236 | -0.022888 | 122.525 | 122.5891 | 0 | 122.3282 | 0.027466 | 0.20142 | 122.406 | 122.7539 | 122.6532 | 122.6303 | 122.525 | 122.6807 | 122.6852 | 122.3282 | 122.6303 | 122.525 | 122.6852 | 122.6532 | 122.6807 | -0.32959 | -0.32501
1355.5469 | 122.8729 | -122.5342 | 0.1236 | -0.029679 | 0.015834 | 0.00138 | 0.041738 | -0.012343 | -0.0067761 | 0.016466 | -0.009155 | 0.11902 | -0.21973 | 0.050354 | 0.086975 | 0.14648 | -0.091553 | 0.19226 | 0.15106 | -0.20599 | 122.3145 | -0.004577 | 122.525 | 122.5845 | -0.036621 | 122.3282 | 0.027466 | 0.21057 | 122.4426 | 122.7264 | 122.6212 | 122.6532 | 122.525 | 122.6852 | 122.6807 | 122.3282 | 122.6532 | 122.525 | 122.6807 | 122.6212 | 122.6852 | -0.34332 | -0.32959
1357.2344 | 122.7905 | -122.5571 | 0.16022 | 0.13054 | 0.016688 | 0.0033026 | 0.042379 | -0.014052 | -0.0076305 | 0.018175 | 0.022888 | 0.073242 | -0.19226 | 0.059509 | 0.086975 | 0.14648 | -0.13733 | 0.18768 | 0.15564 | -0.17853 | 122.3648 | -0.086975 | 122.58 | 122.6166 | -0.073242 | 122.3785 | -0.004577 | 0.21515 | 122.4197 | 122.7448 | 122.644 | 122.6303 | 122.58 | 122.7127 | 122.7036 | 122.3785 | 122.6303 | 122.58 | 122.7036 | 122.644 | 122.7127 | -0.35248 | -0.33874
1358.9688 | 122.9187 | -122.4976 | 0.12817 | -0.17464 | 0.016261 | 0.0062934 | 0.042165 | -0.014266 | -0.0097669 | 0.01668 | -0.068665 | 0.13733 | -0.24719 | -0.032043 | 0.013733 | 0.027466 | 0.050354 | 0.11902 | 0.20599 | -0.23346 | 122.2504 | 0.009155 | 122.4289 | 122.4655 | -0.11444 | 122.2641 | 0.07782 | 0.17853 | 122.5479 | 122.6166 | 122.5113 | 122.6349 | 122.4289 | 122.7036 | 122.525 | 122.2641 | 122.6349 | 122.4289 | 122.525 | 122.5113 | 122.7036 | -0.37537 | -0.36163
1360.6406 | 122.8455 | -122.5571 | 0.15564 | -0.21278 | 0.016902 | 0.009925 | 0.047292 | -0.011275 | -0.010194 | 0.017748 | -0.027466 | 0.13275 | -0.24261 | 0.022888 | 0.032043 | 0.064087 | 0 | 0.14648 | 0.18768 | -0.21973 | 122.3145 | -0.022889 | 122.5296 | 122.58 | -0.1236 | 122.3373 | 0.032043 | 0.21515 | 122.5571 | 122.7036 | 122.5891 | 122.6898 | 122.5296 | 122.7448 | 122.6212 | 122.3373 | 122.6898 | 122.5296 | 122.6212 | 122.5891 | 122.7448 | -0.39826 | -0.37537
1362.3281 | 122.8958 | -122.5342 | 0.13275 | 0.046615 | 0.016261 | 0.0024482 | 0.041097 | -0.011702 | -0.010194 | 0.018389 | -0.013733 | 0.091553 | -0.21057 | 0.018311 | 0.064087 | 0.10986 | -0.091553 | 0.16479 | 0.16937 | -0.17395 | 122.3236 | -0.041198 | 122.5204 | 122.5525 | -0.068664 | 122.3602 | 0.036622 | 0.19684 | 122.4426 | 122.699 | 122.5983 | 122.6257 | 122.5204 | 122.7036 | 122.644 | 122.3602 | 122.6257 | 122.5204 | 122.644 | 122.5983 | 122.7036 | -0.34332 | -0.3067
1364.0312 | 122.7951 | -122.5754 | 0.1831 | 0.16106 | 0.016047 | 0.0086432 | 0.045797 | -0.010848 | -0.0082715 | 0.017962 | -0.064087 | 0.14191 | -0.24261 | -0.036621 | 0.009155 | 0.022888 | 0.004578 | 0.073242 | 0.21515 | -0.20599 | 122.3328 | -0.041198 | 122.5113 | 122.5388 | -0.17395 | 122.3694 | 0.032044 | 0.17853 | 122.58 | 122.6486 | 122.5845 | 122.7173 | 122.5113 | 122.7905 | 122.5983 | 122.3694 | 122.7173 | 122.5113 | 122.5983 | 122.5845 | 122.7905 | -0.42572 | -0.3891
1365.7031 | 122.7997 | -122.5708 | 0.16937 | 0.069504 | 0.017543 | 0.00095277 | 0.046865 | -0.0097796 | -0.0084851 | 0.016253 | -0.054932 | 0.14191 | -0.25635 | -0.032043 | 0.004578 | 0 | 0.022888 | 0.073242 | 0.20142 | -0.21515 | 122.3145 | -0.027466 | 122.5159 | 122.5388 | -0.16479 | 122.3557 | 0.032043 | 0.20142 | 122.5937 | 122.644 | 122.5754 | 122.7127 | 122.5159 | 122.7722 | 122.5708 | 122.3557 | 122.7127 | 122.5159 | 122.5708 | 122.5754 | 122.7722 | -0.42572 | -0.38452
1367.375 | 122.7814 | -122.58 | 0.18768 | -0.022049 | 0.019679 | 0.0052252 | 0.045583 | -0.0089252 | -0.0097669 | 0.018389 | -0.027466 | 0.13275 | -0.23346 | 0.009155 | 0.027466 | 0.045776 | -0.004578 | 0.10529 | 0.17853 | -0.21973 | 122.3465 | -0.054932 | 122.5525 | 122.5891 | -0.16022 | 122.3602 | -0.009155 | 0.20599 | 122.5754 | 122.6852 | 122.6074 | 122.7127 | 122.5525 | 122.7585 | 122.6257 | 122.3602 | 122.7127 | 122.5525 | 122.6257 | 122.6074 | 122.7585 | -0.42114 | -0.40741
1369.0469 | 122.8958 | -122.5159 | 0.14191 | -0.22804 | 0.015407 | -0.00096983 | 0.041097 | -0.011702 | -0.0084851 | 0.018816 | -0.07782 | 0.14191 | -0.26093 | -0.032043 | 0.018311 | 0.032043 | 0.045776 | 0.09613 | 0.18768 | -0.22888 | 122.2549 | 0 | 122.438 | 122.4838 | -0.1236 | 122.287 | 0.045776 | 0.18311 | 122.5616 | 122.612 | 122.5342 | 122.6578 | 122.438 | 122.7036 | 122.5479 | 122.287 | 122.6578 | 122.438 | 122.5479 | 122.5342 | 122.7036 | -0.40283 | -0.37079
1370.7188 | 122.905 | -122.5204 | 0.13275 | -0.25093 | 0.01797 | 0.0018072 | 0.04067 | -0.013411 | -0.0074169 | 0.016253 | -0.082397 | 0.14648 | -0.25177 | -0.036621 | 0.004578 | 0.032043 | 0.073242 | 0.091553 | 0.18768 | -0.21515 | 122.2687 | 0.013733 | 122.4381 | 122.4838 | -0.12817 | 122.3053 | 0.054932 | 0.16937 | 122.5937 | 122.612 | 122.525 | 122.6669 | 122.4381 | 122.7081 | 122.5525 | 122.3053 | 122.6669 | 122.4381 | 122.5525 | 122.525 | 122.7081 | -0.38452 | -0.3479
1372.4219 | 122.8867 | -122.5204 | 0.13733 | -0.27382 | 0.014338 | 0.0058662 | 0.040456 | -0.010848 | -0.010621 | 0.017962 | -0.013733 | 0.12817 | -0.21515 | 0.009155 | 0.059509 | 0.07782 | 0.022888 | 0.14191 | 0.20142 | -0.21973 | 122.3053 | -0.009155 | 122.5067 | 122.5296 | -0.07782 | 122.3007 | 0.064087 | 0.20142 | 122.5433 | 122.6624 | 122.58 | 122.6486 | 122.5067 | 122.7219 | 122.5983 | 122.3007 | 122.6486 | 122.5067 | 122.5983 | 122.58 | 122.7219 | -0.35248 | -0.35706
1374.0938 | 122.7448 | -122.5754 | 0.16022 | 0.19157 | 0.017543 | 0.0045844 | 0.043447 | -0.011916 | -0.0086987 | 0.019457 | 0.041199 | 0.09613 | -0.20599 | 0.07782 | 0.1236 | 0.17395 | -0.1831 | 0.20142 | 0.15106 | -0.16479 | 122.3694 | -0.064087 | 122.6166 | 122.6532 | -0.036621 | 122.4106 | -0.009155 | 0.24719 | 122.3923 | 122.7768 | 122.699 | 122.6715 | 122.6166 | 122.7264 | 122.7493 | 122.4106 | 122.6715 | 122.6166 | 122.7493 | 122.699 | 122.7264 | -0.36621 | -0.32501
1375.7656 | 122.8683 | -122.525 | 0.15106 | 0.069504 | 0.014979 | 0.0071478 | 0.039815 | -0.014693 | -0.0072033 | 0.017534 | -0.018311 | 0.10986 | -0.20599 | 0.013733 | 0.082397 | 0.1236 | -0.086975 | 0.17395 | 0.15106 | -0.18768 | 122.319 | -0.041199 | 122.5067 | 122.5388 | -0.068665 | 122.3373 | 0 | 0.18768 | 122.438 | 122.699 | 122.6074 | 122.6349 | 122.5067 | 122.6761 | 122.6486 | 122.3373 | 122.6349 | 122.5067 | 122.6486 | 122.6074 | 122.6761 | -0.35706 | -0.33874
1377.4375 | 122.8912 | -122.5388 | 0.13733 | 0.0084684 | 0.016475 | 0.002021 | 0.038533 | -0.015548 | -0.0063489 | 0.01668 | -0.027466 | 0.11444 | -0.21515 | 0.027466 | 0.086975 | 0.11444 | -0.10529 | 0.1831 | 0.17395 | -0.20142 | 122.3236 | -0.022888 | 122.5113 | 122.5662 | -0.050354 | 122.3373 | 0.036621 | 0.18768 | 122.4335 | 122.7219 | 122.6257 | 122.6532 | 122.5113 | 122.7127 | 122.6532 | 122.3373 | 122.6532 | 122.5113 | 122.6532 | 122.6257 | 122.7127 | -0.35248 | -0.33875
1379.1094 | 122.7722 | -122.5296 | 0.17395 | 0.17632 | 0.015407 | 0.00073917 | 0.046437 | -0.013198 | -0.0080579 | 0.018175 | -0.013733 | 0.1236 | -0.21057 | 0.064087 | 0.091553 | 0.12817 | -0.13733 | 0.17853 | 0.16022 | -0.18768 | 122.319 | -0.050354 | 122.5159 | 122.5937 | -0.082397 | 122.3419 | -0.013733 | 0.19684 | 122.3923 | 122.7081 | 122.6212 | 122.6532 | 122.5159 | 122.6898 | 122.6578 | 122.3419 | 122.6532 | 122.5159 | 122.6578 | 122.6212 | 122.6898 | -0.38452 | -0.36163
1380.7812 | 122.7585 | -122.5754 | 0.16022 | 0.17632 | 0.017329 | 0.0039436 | 0.043874 | -0.011489 | -0.0082715 | 0.018389 | 0.022888 | 0.10986 | -0.20599 | 0.064087 | 0.091553 | 0.15564 | -0.15106 | 0.19226 | 0.15564 | -0.17853 | 122.3694 | -0.050354 | 122.5983 | 122.6395 | -0.068664 | 122.3969 | -0.004577 | 0.22888 | 122.4243 | 122.7676 | 122.6669 | 122.6852 | 122.5983 | 122.731 | 122.731 | 122.3969 | 122.6852 | 122.5983 | 122.731 | 122.6669 | 122.731 | -0.36621 | -0.33874
1382.5 | 122.9095 | -122.5342 | 0.15564 | -0.23567 | 0.018611 | 0.0035162 | 0.044301 | -0.014907 | -0.0078443 | 0.017534 | -0.082397 | 0.15564 | -0.24719 | -0.032043 | -0.004578 | 0.032043 | 0.082397 | 0.10986 | 0.20599 | -0.23346 | 122.287 | 0 | 122.4518 | 122.5021 | -0.16022 | 122.3007 | 0.050354 | 0.16479 | 122.6166 | 122.644 | 122.5296 | 122.6898 | 122.4518 | 122.7402 | 122.5662 | 122.3007 | 122.6898 | 122.4518 | 122.5662 | 122.5296 | 122.7402 | -0.40283 | -0.3891
1384.1719 | 122.7768 | -122.6074 | 0.16479 | -0.098343 | 0.016475 | 0.0060798 | 0.046651 | -0.0093524 | -0.010194 | 0.018816 | -0.009155 | 0.14648 | -0.23804 | 0.050354 | 0.064087 | 0.091553 | -0.004578 | 0.15564 | 0.19684 | -0.20142 | 122.3694 | -0.018311 | 122.5983 | 122.6578 | -0.10071 | 122.406 | 0.032043 | 0.22888 | 122.6028 | 122.7631 | 122.6715 | 122.7539 | 122.5983 | 122.8043 | 122.699 | 122.406 | 122.7539 | 122.5983 | 122.699 | 122.6715 | 122.8043 | -0.40283 | -0.36621
1385.8438 | 122.8912 | -122.5525 | 0.13733 | -0.28145 | 0.014125 | 0.0056524 | 0.040242 | -0.0099934 | -0.0089123 | 0.017107 | 0.009155 | 0.11444 | -0.21973 | 0.032043 | 0.082397 | 0.091553 | -0.009155 | 0.17853 | 0.17853 | -0.21057 | 122.3328 | -0.022888 | 122.5616 | 122.5845 | -0.054932 | 122.3419 | 0.041199 | 0.22888 | 122.5433 | 122.731 | 122.6349 | 122.6669 | 122.5616 | 122.731 | 122.644 | 122.3419 | 122.6669 | 122.5616 | 122.644 | 122.6349 | 122.731 | -0.35706 | -0.3479
1387.5312 | 122.8592 | -122.5525 | 0.15106 | -0.16701 | 0.016047 | 0.0058662 | 0.040883 | -0.013625 | -0.0099805 | 0.015184 | 0.032043 | 0.10986 | -0.21057 | 0.086975 | 0.11902 | 0.14648 | -0.086975 | 0.22888 | 0.1831 | -0.19684 | 122.3419 | -0.041199 | 122.5845 | 122.6395 | -0.032043 | 122.3557 | 0.032043 | 0.24261 | 122.4655 | 122.7814 | 122.6715 | 122.6624 | 122.5845 | 122.7356 | 122.699 | 122.3557 | 122.6624 | 122.5845 | 122.699 | 122.6715 | 122.7356 | -0.36163 | -0.3479
1389.2344 | 122.7905 | -122.5525 | 0.16022 | 0.1992 | 0.014338 | 0.0071478 | 0.045156 | -0.014052 | -0.010408 | 0.017107 | -0.036621 | 0.14191 | -0.24719 | 0.013733 | 0.032043 | 0.082397 | -0.082397 | 0.13275 | 0.16937 | -0.21973 | 122.3053 | -0.01831 | 122.5159 | 122.5662 | -0.12817 | 122.3328 | 0.009156 | 0.21057 | 122.4701 | 122.6852 | 122.5845 | 122.6944 | 122.5159 | 122.7219 | 122.6349 | 122.3328 | 122.6944 | 122.5159 | 122.6349 | 122.5845 | 122.7219 | -0.40741 | -0.37994
1390.9688 | 122.85 | -122.5342 | 0.14191 | -0.12123 | 0.017116 | 0.0039436 | 0.039174 | -0.015761 | -0.0072033 | 0.017107 | 0.041199 | 0.11444 | -0.19684 | 0.086975 | 0.13733 | 0.17395 | -0.13733 | 0.25635 | 0.16937 | -0.18768 | 122.3373 | -0.027466 | 122.5754 | 122.6212 | -0.004578 | 122.3465 | 0.027466 | 0.23804 | 122.3969 | 122.7905 | 122.6715 | 122.6486 | 122.5754 | 122.7036 | 122.7081 | 122.3465 | 122.6486 | 122.5754 | 122.7081 | 122.6715 | 122.7036 | -0.33875 | -0.32959
1392.6562 | 122.7722 | -122.5845 | 0.16479 | 0.16106 | 0.016475 | 0.008216 | 0.046651 | -0.010207 | -0.0074169 | 0.017107 | 0.054932 | 0.11444 | -0.20599 | 0.082397 | 0.11444 | 0.14648 | -0.16937 | 0.19226 | 0.16937 | -0.17853 | 122.3785 | -0.050354 | 122.6395 | 122.6669 | -0.050354 | 122.406 | 0.004578 | 0.26093 | 122.4152 | 122.7768 | 122.699 | 122.699 | 122.6395 | 122.7539 | 122.731 | 122.406 | 122.699 | 122.6395 | 122.731 | 122.699 | 122.7539 | -0.37079 | -0.34332
1394.3594 | 122.8409 | -122.5616 | 0.15564 | -0.14412 | 0.018184 | 0.0043708 | 0.045583 | -0.01277 | -0.013185 | 0.016893 | -0.027466 | 0.13275 | -0.25177 | 0.027466 | 0.041199 | 0.07782 | 0.013733 | 0.13733 | 0.20142 | -0.22888 | 122.3099 | -0.022889 | 122.5342 | 122.5891 | -0.11444 | 122.3328 | 0.045776 | 0.2243 | 122.5754 | 122.699 | 122.6028 | 122.6944 | 122.5342 | 122.7631 | 122.6395 | 122.3328 | 122.6944 | 122.5342 | 122.6395 | 122.6028 | 122.7631 | -0.40741 | -0.38452
1396.0312 | 122.7951 | -122.58 | 0.17395 | -0.098343 | 0.015407 | 0.006507 | 0.044301 | -0.010421 | -0.0080579 | 0.017748 | -0.004578 | 0.13733 | -0.24261 | 0.041199 | 0.064087 | 0.07782 | -0.018311 | 0.15564 | 0.18768 | -0.20142 | 122.3373 | -0.036621 | 122.5754 | 122.6212 | -0.10986 | 122.3785 | 0.013733 | 0.23804 | 122.5616 | 122.7356 | 122.644 | 122.7173 | 122.5754 | 122.7676 | 122.6578 | 122.3785 | 122.7173 | 122.5754 | 122.6578 | 122.644 | 122.7676 | -0.41656 | -0.37537
1397.7656 | 122.905 | -122.5616 | 0.14191 | -0.25093 | 0.015834 | 0.003089 | 0.040883 | -0.01512 | -0.0080579 | 0.017534 | -0.018311 | 0.13275 | -0.24261 | 0.018311 | 0.082397 | 0.082397 | 0.027466 | 0.16479 | 0.19226 | -0.21973 | 122.319 | -0.009156 | 122.5433 | 122.58 | -0.05951 | 122.3419 | 0.050354 | 0.2243 | 122.5891 | 122.7264 | 122.644 | 122.6944 | 122.5433 | 122.7539 | 122.644 | 122.3419 | 122.6944 | 122.5433 | 122.644 | 122.644 | 122.7539 | -0.38452 | -0.36163
1399.5 | 122.8088 | -122.5708 | 0.15564 | 0.10765 | 0.018184 | 0.0039436 | 0.044515 | -0.011916 | -0.0082715 | 0.018602 | -0.064087 | 0.13733 | -0.25177 | -0.013733 | 0.004578 | 0.064087 | -0.041199 | 0.09613 | 0.1831 | -0.21973 | 122.319 | -0.018311 | 122.5067 | 122.5571 | -0.15106 | 122.3511 | 0.027465 | 0.18768 | 122.5296 | 122.6669 | 122.5754 | 122.7081 | 122.5067 | 122.7539 | 122.6349 | 122.3511 | 122.7081 | 122.5067 | 122.6349 | 122.5754 | 122.7539 | -0.40741 | -0.37537
1401.1875 | 122.8638 | -122.5296 | 0.16479 | -0.1899 | 0.014766 | 0.006507 | 0.044728 | -0.01277 | -0.0072033 | 0.018175 | -0.054932 | 0.15564 | -0.22888 | 0.013733 | 0.027466 | 0.045776 | 0.041199 | 0.11444 | 0.1831 | -0.21515 | 122.3007 | -0.009155 | 122.4747 | 122.5433 | -0.13733 | 122.3145 | 0.01831 | 0.17395 | 122.5708 | 122.644 | 122.5571 | 122.6852 | 122.4747 | 122.7127 | 122.5754 | 122.3145 | 122.6852 | 122.4747 | 122.5754 | 122.5571 | 122.7127 | -0.39368 | -0.37994
1402.9375 | 122.8226 | -122.5571 | 0.16937 | 0.12291 | 0.016261 | 0.0088568 | 0.046437 | -0.011061 | -0.0099805 | 0.017107 | -0.09613 | 0.12817 | -0.24719 | -0.041199 | -0.013733 | 0.013733 | 0.004578 | 0.064087 | 0.20599 | -0.2243 | 122.3099 | -0.041199 | 122.4609 | 122.5159 | -0.18311 | 122.3328 | 0.036621 | 0.15106 | 122.5616 | 122.6212 | 122.5433 | 122.6852 | 122.4609 | 122.7631 | 122.5708 | 122.3328 | 122.6852 | 122.4609 | 122.5708 | 122.5433 | 122.7631 | -0.41656 | -0.39368
1404.6094 | 122.7722 | -122.5845 | 0.16479 | 0.19157 | 0.017329 | 0.0075752 | 0.039174 | -0.012343 | -0.0095531 | 0.018602 | 0.041199 | 0.10986 | -0.17395 | 0.086975 | 0.11444 | 0.17853 | -0.16937 | 0.21973 | 0.15564 | -0.18768 | 122.4106 | -0.054932 | 122.6257 | 122.6715 | -0.050354 | 122.3969 | -0.009155 | 0.21515 | 122.4152 | 122.8043 | 122.699 | 122.6944 | 122.6257 | 122.7402 | 122.7631 | 122.3969 | 122.6944 | 122.6257 | 122.7631 | 122.699 | 122.7402 | -0.33874 | -0.35248
1406.2812 | 122.7859 | -122.6028 | 0.16022 | 0.12291 | 0.016475 | 0.0026618 | 0.039815 | -0.014052 | -0.0076305 | 0.018602 | 0.045776 | 0.086975 | -0.20599 | 0.073242 | 0.09613 | 0.15564 | -0.16022 | 0.20142 | 0.15564 | -0.20599 | 122.3969 | -0.073242 | 122.6486 | 122.6761 | -0.064087 | 122.3969 | -0.004577 | 0.25177 | 122.4426 | 122.8043 | 122.699 | 122.6898 | 122.6486 | 122.7585 | 122.7585 | 122.3969 | 122.6898 | 122.6486 | 122.7585 | 122.699 | 122.7585 | -0.36621 | -0.36621
1407.9844 | 122.9279 | -122.525 | 0.15106 | -0.23567 | 0.016688 | 0.0041572 | 0.040029 | -0.014693 | -0.010194 | 0.015398 | -0.073242 | 0.14191 | -0.23346 | -0.032043 | 0.004578 | 0.018311 | 0.082397 | 0.10986 | 0.19684 | -0.23346 | 122.2916 | -0.009155 | 122.4518 | 122.493 | -0.14648 | 122.2916 | 0.045776 | 0.16022 | 122.6074 | 122.6349 | 122.5296 | 122.6669 | 122.4518 | 122.7219 | 122.5433 | 122.2916 | 122.6669 | 122.4518 | 122.5433 | 122.5296 | 122.7219 | -0.38452 | -0.38452
1409.6562 | 122.8134 | -122.5708 | 0.16022 | -0.14412 | 0.016261 | 0.0022346 | 0.046865 | -0.011916 | -0.010835 | 0.015184 | -0.009155 | 0.13275 | -0.23804 | 0.036621 | 0.064087 | 0.073242 | 0.013733 | 0.14648 | 0.20142 | -0.18768 | 122.3328 | -0.027466 | 122.5616 | 122.6074 | -0.09613 | 122.3831 | 0.041199 | 0.22888 | 122.5845 | 122.7173 | 122.6349 | 122.7036 | 122.5616 | 122.7722 | 122.644 | 122.3831 | 122.7036 | 122.5616 | 122.644 | 122.6349 | 122.7722 | -0.39825 | -0.3479
1411.3281 | 122.7814 | -122.5708 | 0.17395 | -0.044937 | 0.017329 | 0.0054388 | 0.048146 | -0.0097796 | -0.0095531 | 0.01967 | -0.004578 | 0.09613 | -0.23346 | 0.022888 | 0.054932 | 0.064087 | -0.009155 | 0.13733 | 0.20599 | -0.19684 | 122.3373 | -0.07782 | 122.5662 | 122.5937 | -0.11902 | 122.374 | 0.032044 | 0.22888 | 122.5616 | 122.7081 | 122.6257 | 122.6669 | 122.5662 | 122.7768 | 122.6349 | 122.374 | 122.6669 | 122.5662 | 122.6349 | 122.6257 | 122.7768 | -0.40741 | -0.37079
1413.0625 | 122.8226 | -122.5662 | 0.17853 | 0.046615 | 0.016688 | 0.011634 | 0.046865 | -0.0097796 | -0.0086987 | 0.017107 | 0.004578 | 0.14648 | -0.24261 | -0.013733 | 0.018311 | 0.022888 | 0.004578 | 0.07782 | 0.21515 | -0.21057 | 122.3236 | -0.032044 | 122.5708 | 122.5525 | -0.16022 | 122.3557 | 0.036621 | 0.24719 | 122.5708 | 122.644 | 122.5845 | 122.7127 | 122.5708 | 122.7814 | 122.5891 | 122.3557 | 122.7127 | 122.5708 | 122.5891 | 122.5845 | 122.7814 | -0.42114 | -0.3891
1414.7656 | 122.8134 | -122.5891 | 0.16937 | -0.01442 | 0.015193 | 0.0037298 | 0.045156 | -0.009566 | -0.0086987 | 0.019884 | -0.050354 | 0.11902 | -0.26093 | -0.009155 | 0.018311 | 0.045776 | 0.018311 | 0.082397 | 0.18768 | -0.21973 | 122.3282 | -0.050354 | 122.5388 | 122.58 | -0.15106 | 122.3694 | 0.01831 | 0.21057 | 122.6074 | 122.6715 | 122.6074 | 122.7081 | 122.5388 | 122.7768 | 122.6349 | 122.3694 | 122.7081 | 122.5388 | 122.6349 | 122.6074 | 122.7768 | -0.4303 | -0.3891
1416.4375 | 122.7859 | -122.5662 | 0.1831 | 0.17632 | 0.017116 | 0.0073614 | 0.041738 | -0.010634 | -0.0089123 | 0.01668 | -0.004578 | 0.11902 | -0.21515 | 0.045776 | 0.10529 | 0.15106 | -0.14648 | 0.1831 | 0.15106 | -0.17395 | 122.3511 | -0.064086 | 122.5616 | 122.612 | -0.077819 | 122.3923 | -0.032043 | 0.21057 | 122.4197 | 122.7493 | 122.6715 | 122.6852 | 122.5616 | 122.7173 | 122.7173 | 122.3923 | 122.6852 | 122.5616 | 122.7173 | 122.6715 | 122.7173 | -0.39825 | -0.35706
1418.125 | 122.8088 | -122.5891 | 0.17853 | 0.13054 | 0.016261 | 0.0054388 | 0.039601 | -0.012343 | -0.0080579 | 0.018389 | 0.036621 | 0.10986 | -0.1831 | 0.054932 | 0.11444 | 0.16937 | -0.15106 | 0.20142 | 0.16479 | -0.20142 | 122.406 | -0.068665 | 122.6257 | 122.644 | -0.064087 | 122.3877 | -0.013733 | 0.21973 | 122.438 | 122.7905 | 122.7036 | 122.699 | 122.6257 | 122.7539 | 122.7585 | 122.3877 | 122.699 | 122.6257 | 122.7585 | 122.7036 | 122.7539 | -0.36163 | -0.37994
1419.7969 | 122.7997 | -122.5662 | 0.16022 | 0.13817 | 0.017116 | 0.0056524 | 0.03832 | -0.013411 | -0.0059217 | 0.017534 | 0.022888 | 0.11444 | -0.20599 | 0.054932 | 0.09613 | 0.15106 | -0.15106 | 0.1831 | 0.14648 | -0.19684 | 122.3602 | -0.045776 | 122.5891 | 122.6212 | -0.064087 | 122.3694 | -0.013733 | 0.22888 | 122.4152 | 122.7493 | 122.6624 | 122.6807 | 122.5891 | 122.7127 | 122.7173 | 122.3694 | 122.6807 | 122.5891 | 122.7173 | 122.6624 | 122.7127 | -0.36621 | -0.35706
1421.4844 | 122.818 | -122.5937 | 0.17395 | 0.084762 | 0.017329 | 0.0062934 | 0.04836 | -0.0097796 | -0.012117 | 0.017962 | -0.068665 | 0.14648 | -0.24719 | -0.050354 | -0.018311 | 0.018311 | 0.027466 | 0.064087 | 0.20599 | -0.21515 | 122.3465 | -0.027466 | 122.525 | 122.5433 | -0.19226 | 122.3785 | 0.032044 | 0.17853 | 122.6212 | 122.6578 | 122.5754 | 122.7402 | 122.525 | 122.7997 | 122.612 | 122.3785 | 122.7402 | 122.525 | 122.612 | 122.5754 | 122.7997 | -0.42114 | -0.3891
1423.1562 | 122.7997 | -122.5983 | 0.17395 | -0.0067901 | 0.016902 | 0.004798 | 0.043233 | -0.010421 | -0.0091259 | 0.017107 | -0.018311 | 0.1236 | -0.24719 | 0 | 0.032043 | 0.050354 | -0.004578 | 0.10986 | 0.19684 | -0.23346 | 122.3511 | -0.050354 | 122.58 | 122.5983 | -0.14191 | 122.3648 | 0.022888 | 0.22888 | 122.5937 | 122.7081 | 122.6303 | 122.7219 | 122.58 | 122.7951 | 122.6486 | 122.3648 | 122.7219 | 122.58 | 122.6486 | 122.6303 | 122.7951 | -0.42114 | -0.40741
1424.8594 | 122.9233 | -122.5204 | 0.12817 | -0.19753 | 0.018397 | 0.0035162 | 0.039815 | -0.011489 | -0.0084851 | 0.016039 | -0.064087 | 0.12817 | -0.2243 | -0.036621 | 0.032043 | 0.045776 | 0.059509 | 0.13275 | 0.20599 | -0.24261 | 122.2961 | 0 | 122.4564 | 122.4838 | -0.096131 | 122.2778 | 0.07782 | 0.16022 | 122.58 | 122.6532 | 122.5525 | 122.6486 | 122.4564 | 122.7264 | 122.5662 | 122.2778 | 122.6486 | 122.4564 | 122.5662 | 122.5525 | 122.7264 | -0.35248 | -0.37079
1426.5469 | 122.8729 | -122.5479 | 0.13733 | -0.12886 | 0.016047 | 0.0018072 | 0.039388 | -0.013625 | -0.0084851 | 0.016466 | 0.013733 | 0.10529 | -0.20599 | 0.073242 | 0.13733 | 0.17853 | -0.12817 | 0.24261 | 0.15564 | -0.18768 | 122.3419 | -0.032043 | 122.5616 | 122.6212 | 0 | 122.3602 | 0.018311 | 0.21973 | 122.4197 | 122.7905 | 122.6852 | 122.6532 | 122.5616 | 122.7036 | 122.7264 | 122.3602 | 122.6532 | 122.5616 | 122.7264 | 122.6852 | 122.7036 | -0.34332 | -0.32501
1428.2656 | 122.9324 | -122.5616 | 0.14191 | -0.22041 | 0.016688 | 0.0054388 | 0.04366 | -0.013839 | -0.0093395 | 0.017534 | -0.059509 | 0.14648 | -0.24719 | -0.018311 | 0.032043 | 0.018311 | 0.064087 | 0.1236 | 0.21057 | -0.23346 | 122.3145 | 0.004577 | 122.5021 | 122.5433 | -0.10986 | 122.3282 | 0.068664 | 0.18768 | 122.6257 | 122.6852 | 122.5937 | 122.7081 | 122.5021 | 122.7722 | 122.58 | 122.3282 | 122.7081 | 122.5021 | 122.58 | 122.5937 | 122.7722 | -0.3891 | -0.37537
1429.9844 | 122.9187 | -122.5662 | 0.14648 | -0.27382 | 0.016475 | 0.0075752 | 0.036611 | -0.010421 | -0.0086987 | 0.016039 | -0.018311 | 0.11902 | -0.21973 | -0.004578 | 0.032043 | 0.068665 | 0.027466 | 0.14648 | 0.19684 | -0.20599 | 122.3465 | -0.027465 | 122.5479 | 122.5616 | -0.11444 | 122.3602 | 0.050354 | 0.20142 | 122.5937 | 122.7127 | 122.5983 | 122.6852 | 122.5479 | 122.7631 | 122.6349 | 122.3602 | 122.6852 | 122.5479 | 122.6349 | 122.5983 | 122.7631 | -0.36621 | -0.35248
1431.6562 | 122.9187 | -122.5342 | 0.14648 | 0.016098 | 0.017543 | 0.0026618 | 0.037465 | -0.01213 | -0.0057079 | 0.016039 | -0.022888 | 0.10986 | -0.21057 | 0.022888 | 0.07782 | 0.10071 | -0.082397 | 0.16022 | 0.17853 | -0.19684 | 122.3236 | -0.036621 | 122.5113 | 122.5571 | -0.068664 | 122.3373 | 0.032044 | 0.18768 | 122.4518 | 122.6944 | 122.612 | 122.644 | 122.5113 | 122.7127 | 122.6349 | 122.3373 | 122.644 | 122.5113 | 122.6349 | 122.612 | 122.7127 | -0.35706 | -0.34332
1433.3281 | 122.8683 | -122.5708 | 0.14648 | -0.20515 | 0.017329 | 0.0054388 | 0.041951 | -0.013411 | -0.0072033 | 0.017962 | 0.036621 | 0.10986 | -0.20142 | 0.10986 | 0.12817 | 0.17395 | -0.11444 | 0.26093 | 0.16479 | -0.20599 | 122.3694 | -0.036621 | 122.6074 | 122.6807 | -0.01831 | 122.3648 | 0.018311 | 0.23804 | 122.4564 | 122.8317 | 122.699 | 122.6807 | 122.6074 | 122.7356 | 122.7448 | 122.3648 | 122.6807 | 122.6074 | 122.7448 | 122.699 | 122.7356 | -0.3479 | -0.35248
1435.0312 | 122.9279 | -122.5571 | 0.13733 | -0.1899 | 0.018397 | 0.00031197 | 0.043874 | -0.012984 | -0.010408 | 0.016039 | -0.054932 | 0.11902 | -0.24261 | -0.009155 | 0.022888 | 0.041199 | 0.045776 | 0.13733 | 0.20142 | -0.23346 | 122.3145 | -0.01831 | 122.5021 | 122.5479 | -0.11444 | 122.3236 | 0.064087 | 0.18768 | 122.6028 | 122.6944 | 122.58 | 122.6761 | 122.5021 | 122.7585 | 122.5983 | 122.3236 | 122.6761 | 122.5021 | 122.5983 | 122.58 | 122.7585 | -0.37994 | -0.37079
1436.7031 | 122.9233 | -122.5708 | 0.14648 | -0.25093 | 0.014766 | 0.0041572 | 0.043019 | -0.012557 | -0.010408 | 0.015398 | -0.086975 | 0.15106 | -0.25177 | -0.032043 | 0.004578 | 0.022888 | 0.086975 | 0.10529 | 0.20142 | -0.22888 | 122.319 | 0.004578 | 122.4838 | 122.5388 | -0.14191 | 122.3419 | 0.054932 | 0.16479 | 122.6578 | 122.6761 | 122.5754 | 122.7219 | 122.4838 | 122.7722 | 122.5937 | 122.3419 | 122.7219 | 122.4838 | 122.5937 | 122.5754 | 122.7722 | -0.39825 | -0.37537
1438.3906 | 122.9187 | -122.5571 | 0.14191 | -0.1899 | 0.017116 | 0.0075752 | 0.043019 | -0.013839 | -0.010194 | 0.016039 | -0.07782 | 0.14648 | -0.23804 | -0.022888 | 0.009155 | 0.027466 | 0.059509 | 0.10986 | 0.21515 | -0.22888 | 122.319 | 0.004577 | 122.4792 | 122.5342 | -0.13275 | 122.3282 | 0.073242 | 0.16022 | 122.6166 | 122.6669 | 122.5662 | 122.7036 | 122.4792 | 122.7722 | 122.5845 | 122.3282 | 122.7036 | 122.4792 | 122.5845 | 122.5662 | 122.7722 | -0.37994 | -0.37079
1440.0781 | 122.7814 | -122.5754 | 0.16937 | -0.060196 | 0.016047 | 0.0043708 | 0.045583 | -0.010207 | -0.0097669 | 0.017962 | 0.004578 | 0.13733 | -0.26093 | 0.050354 | 0.050354 | 0.064087 | -0.004578 | 0.16022 | 0.19684 | -0.2243 | 122.3145 | -0.032044 | 122.58 | 122.6257 | -0.11902 | 122.3511 | 0.027465 | 0.2655 | 122.5708 | 122.7356 | 122.6257 | 122.7127 | 122.58 | 122.7722 | 122.6395 | 122.3511 | 122.7127 | 122.58 | 122.6395 | 122.6257 | 122.7722 | -0.4303 | -0.39368
1441.7656 | 122.7768 | -122.612 | 0.16937 | 0.15343 | 0.015834 | 0.004798 | 0.044088 | -0.0091388 | -0.010835 | 0.017107 | 0.050354 | 0.10529 | -0.19226 | 0.068665 | 0.11444 | 0.17395 | -0.1831 | 0.19684 | 0.15106 | -0.19226 | 122.4197 | -0.064087 | 122.6624 | 122.6807 | -0.054932 | 122.4197 | -0.018311 | 0.24261 | 122.4289 | 122.8088 | 122.7264 | 122.7173 | 122.6624 | 122.7631 | 122.7859 | 122.4197 | 122.7173 | 122.6624 | 122.7859 | 122.7264 | 122.7631 | -0.36163 | -0.36163
1443.4375 | 122.9141 | -122.5571 | 0.1236 | 0.031357 | 0.017543 | 0.0028754 | 0.038961 | -0.013198 | -0.0078443 | 0.017534 | -0.013733 | 0.1236 | -0.21973 | 0.009155 | 0.064087 | 0.10986 | -0.073242 | 0.16479 | 0.16479 | -0.21515 | 122.3373 | 0 | 122.5433 | 122.5662 | -0.059509 | 122.3419 | 0.041199 | 0.20599 | 122.4838 | 122.7219 | 122.6212 | 122.6807 | 122.5433 | 122.7219 | 122.6669 | 122.3419 | 122.6807 | 122.5433 | 122.6669 | 122.6212 | 122.7219 | -0.34332 | -0.33875
1445.1406 | 122.8638 | -122.5571 | 0.14191 | -0.12123 | 0.01562 | 0.0069342 | 0.04067 | -0.013198 | -0.0080579 | 0.014757 | 0.041199 | 0.10529 | -0.21057 | 0.10071 | 0.13733 | 0.1831 | -0.13275 | 0.24719 | 0.15106 | -0.20599 | 122.3465 | -0.036621 | 122.5983 | 122.6578 | -0.004578 | 122.3511 | 0.009155 | 0.25177 | 122.4243 | 122.8043 | 122.6944 | 122.6624 | 122.5983 | 122.7081 | 122.7402 | 122.3511 | 122.6624 | 122.5983 | 122.7402 | 122.6944 | 122.7081 | -0.35248 | -0.3479
1446.8281 | 122.9233 | -122.5479 | 0.14191 | -0.01442 | 0.016047 | 0.0050116 | 0.040242 | -0.013839 | -0.0082715 | 0.015184 | -0.022888 | 0.11902 | -0.20599 | 0.041199 | 0.068665 | 0.11444 | -0.091553 | 0.17395 | 0.16022 | -0.18768 | 122.3419 | -0.022888 | 122.525 | 122.5891 | -0.073242 | 122.3602 | 0.01831 | 0.18311 | 122.4564 | 122.7219 | 122.6166 | 122.6669 | 122.525 | 122.7081 | 122.6624 | 122.3602 | 122.6669 | 122.525 | 122.6624 | 122.6166 | 122.7081 | -0.3479 | -0.32959
1448.5 | 122.8317 | -122.5937 | 0.1831 | 0.023727 | 0.016475 | 0.0037298 | 0.048146 | -0.012557 | -0.01169 | 0.018389 | -0.045776 | 0.14191 | -0.25635 | -0.013733 | -0.009155 | 0.022888 | 0.022888 | 0.082397 | 0.19684 | -0.21515 | 122.3373 | -0.041198 | 122.5479 | 122.58 | -0.19226 | 122.3785 | 0.013733 | 0.21057 | 122.6166 | 122.6761 | 122.5845 | 122.7356 | 122.5479 | 122.7905 | 122.6166 | 122.3785 | 122.7356 | 122.5479 | 122.6166 | 122.5845 | 122.7905 | -0.43945 | -0.39825
1450.2031 | 122.905 | -122.5708 | 0.14191 | -0.25856 | 0.016047 | 0.0022346 | 0.039815 | -0.011489 | -0.0089123 | 0.017962 | -0.009155 | 0.11444 | -0.21515 | 0.050354 | 0.07782 | 0.091553 | 0.004578 | 0.17395 | 0.19226 | -0.21973 | 122.3557 | -0.027466 | 122.5616 | 122.6212 | -0.064087 | 122.3511 | 0.050354 | 0.20599 | 122.5754 | 122.7448 | 122.6486 | 122.6852 | 122.5616 | 122.7631 | 122.6624 | 122.3511 | 122.6852 | 122.5616 | 122.6624 | 122.6486 | 122.7631 | -0.35706 | -0.36163
1451.875 | 122.9324 | -122.5433 | 0.13733 | -0.25093 | 0.017116 | 0.003089 | 0.043233 | -0.011489 | -0.0082715 | 0.017534 | -0.064087 | 0.14648 | -0.24719 | -0.013733 | 0 | 0.022888 | 0.073242 | 0.10986 | 0.20142 | -0.23804 | 122.2961 | 0.009155 | 122.4792 | 122.5296 | -0.13733 | 122.3053 | 0.064087 | 0.1831 | 122.6166 | 122.6532 | 122.5433 | 122.6898 | 122.4792 | 122.7448 | 122.5662 | 122.3053 | 122.6898 | 122.4792 | 122.5662 | 122.5433 | 122.7448 | -0.38452 | -0.37537
1453.5469 | 122.905 | -122.5479 | 0.14648 | -0.19753 | 0.016475 | 0.0022346 | 0.039174 | -0.0099934 | -0.0091259 | 0.016253 | 0.036621 | 0.10071 | -0.21057 | 0.073242 | 0.10986 | 0.11444 | -0.032043 | 0.21057 | 0.15106 | -0.20599 | 122.3373 | -0.045776 | 122.5845 | 122.6212 | -0.036621 | 122.3419 | 0.004578 | 0.24719 | 122.5159 | 122.7585 | 122.6578 | 122.6486 | 122.5845 | 122.699 | 122.6624 | 122.3419 | 122.6486 | 122.5845 | 122.6624 | 122.6578 | 122.699 | -0.35706 | -0.35248
1455.2188 | 122.8867 | -122.5754 | 0.15564 | -0.16701 | 0.016261 | 0.0058662 | 0.042165 | -0.013839 | -0.0089123 | 0.015612 | 0.050354 | 0.10071 | -0.19226 | 0.086975 | 0.11902 | 0.15106 | -0.073242 | 0.23804 | 0.16479 | -0.21057 | 122.3831 | -0.054932 | 122.6257 | 122.6624 | -0.036621 | 122.3648 | 0.009155 | 0.24261 | 122.5021 | 122.8134 | 122.6944 | 122.6761 | 122.6257 | 122.7402 | 122.7264 | 122.3648 | 122.6761 | 122.6257 | 122.7264 | 122.6944 | 122.7402 | -0.3479 | -0.36621
1456.9062 | 122.7859 | -122.612 | 0.17853 | 0.20683 | 0.015407 | 0.0080024 | 0.042806 | -0.011275 | -0.0093395 | 0.018389 | 0.050354 | 0.086975 | -0.21057 | 0.091553 | 0.10986 | 0.17395 | -0.20142 | 0.21973 | 0.15564 | -0.19226 | 122.4014 | -0.091553 | 122.6624 | 122.7036 | -0.068665 | 122.4197 | -0.022888 | 0.26093 | 122.4106 | 122.8317 | 122.7219 | 122.699 | 122.6624 | 122.7676 | 122.7859 | 122.4197 | 122.699 | 122.6624 | 122.7859 | 122.7219 | 122.7676 | -0.3891 | -0.37079
1458.5938 | 122.9233 | -122.5662 | 0.15564 | -0.26619 | 0.016688 | 0.0069342 | 0.04366 | -0.013839 | -0.0086987 | 0.016893 | 0.013733 | 0.11444 | -0.21973 | 0.045776 | 0.07782 | 0.10071 | -0.018311 | 0.18768 | 0.17395 | -0.2243 | 122.3465 | -0.041199 | 122.58 | 122.612 | -0.07782 | 122.3419 | 0.01831 | 0.23346 | 122.5479 | 122.7539 | 122.644 | 122.6807 | 122.58 | 122.7402 | 122.6669 | 122.3419 | 122.6807 | 122.58 | 122.6669 | 122.644 | 122.7402 | -0.37537 | -0.37994
1460.2656 | 122.7997 | -122.6303 | 0.19226 | -0.067826 | 0.017116 | 0.0026618 | 0.047506 | -0.011061 | -0.01233 | 0.01668 | 0 | 0.1236 | -0.24719 | 0.050354 | 0.059509 | 0.086975 | -0.032043 | 0.16022 | 0.18768 | -0.20142 | 122.3831 | -0.068665 | 122.6303 | 122.6807 | -0.13275 | 122.4289 | -0.004578 | 0.24719 | 122.5983 | 122.7905 | 122.6898 | 122.7539 | 122.6303 | 122.818 | 122.7173 | 122.4289 | 122.7539 | 122.6303 | 122.7173 | 122.6898 | 122.818 | -0.43945 | -0.39368
1461.9375 | 122.7997 | -122.6257 | 0.19684 | -0.029679 | 0.018184 | 0.0052252 | 0.048146 | -0.011702 | -0.011476 | 0.017534 | -0.022888 | 0.13733 | -0.24719 | 0.013733 | 0.054932 | 0.050354 | -0.004578 | 0.13275 | 0.1831 | -0.21973 | 122.3785 | -0.059509 | 122.6028 | 122.6395 | -0.14191 | 122.406 | -0.013733 | 0.2243 | 122.6212 | 122.7585 | 122.6807 | 122.7631 | 122.6028 | 122.8088 | 122.6761 | 122.406 | 122.7631 | 122.6028 | 122.6761 | 122.6807 | 122.8088 | -0.44403 | -0.41657
1463.6406 | 122.8821 | -122.58 | 0.13733 | -0.19753 | 0.016261 | 0.003089 | 0.039815 | -0.012984 | -0.0084851 | 0.01668 | 0.050354 | 0.11444 | -0.20142 | 0.091553 | 0.14648 | 0.16022 | -0.10529 | 0.26093 | 0.16479 | -0.19684 | 122.3785 | -0.022888 | 122.6303 | 122.6715 | 0.009155 | 122.3831 | 0.027466 | 0.25177 | 122.4747 | 122.8409 | 122.7264 | 122.6944 | 122.6303 | 122.7448 | 122.7402 | 122.3831 | 122.6944 | 122.6303 | 122.7402 | 122.7264 | 122.7448 | -0.33875 | -0.33417
1465.3125 | 122.9279 | -122.5525 | 0.15564 | -0.25093 | 0.017116 | 0.0028754 | 0.042379 | -0.012343 | -0.0078443 | 0.016039 | 0.009155 | 0.13275 | -0.21973 | 0.027466 | 0.064087 | 0.07782 | 0 | 0.15564 | 0.1831 | -0.2243 | 122.3328 | -0.022889 | 122.5616 | 122.58 | -0.091553 | 122.3282 | 0.027465 | 0.22888 | 122.5525 | 122.7081 | 122.6166 | 122.6852 | 122.5616 | 122.7356 | 122.6303 | 122.3282 | 122.6852 | 122.5616 | 122.6303 | 122.6166 | 122.7356 | -0.37537 | -0.37994
1466.9688 | 122.8134 | -122.5937 | 0.16937 | 0.13817 | 0.018611 | 0.0045844 | 0.045369 | -0.0099934 | -0.011049 | 0.01668 | -0.036621 | 0.13733 | -0.24719 | 0 | 0.027466 | 0.07782 | -0.073242 | 0.10986 | 0.18768 | -0.21515 | 122.3465 | -0.032044 | 122.5571 | 122.5937 | -0.14191 | 122.3785 | 0.01831 | 0.21057 | 122.5204 | 122.7036 | 122.6212 | 122.731 | 122.5571 | 122.7814 | 122.6715 | 122.3785 | 122.731 | 122.5571 | 122.6715 | 122.6212 | 122.7814 | -0.41656 | -0.38452
1468.6406 | 122.7859 | -122.5662 | 0.17395 | 0.18394 | 0.016902 | 0.003089 | 0.044301 | -0.010634 | -0.0089123 | 0.017748 | -0.018311 | 0.11902 | -0.23804 | 0.064087 | 0.082397 | 0.13733 | -0.12817 | 0.1831 | 0.16479 | -0.21057 | 122.3282 | -0.054931 | 122.5479 | 122.6303 | -0.091553 | 122.3557 | -0.009155 | 0.21973 | 122.438 | 122.7493 | 122.6486 | 122.6852 | 122.5479 | 122.731 | 122.7036 | 122.3557 | 122.6852 | 122.5479 | 122.7036 | 122.6486 | 122.731 | -0.41199 | -0.38452
1470.3438 | 122.905 | -122.5754 | 0.16022 | -0.1899 | 0.015834 | 0.0043708 | 0.040242 | -0.01213 | -0.0097669 | 0.017321 | 0.041199 | 0.11444 | -0.21515 | 0.068665 | 0.11444 | 0.13275 | -0.073242 | 0.22888 | 0.1831 | -0.19684 | 122.3602 | -0.045776 | 122.6166 | 122.644 | -0.045776 | 122.3785 | 0.022888 | 0.25635 | 122.5021 | 122.8043 | 122.6898 | 122.6898 | 122.6166 | 122.7585 | 122.7081 | 122.3785 | 122.6898 | 122.6166 | 122.7081 | 122.6898 | 122.7585 | -0.37537 | -0.35706
1472.0469 | 122.8088 | -122.5845 | 0.17395 | 0.16106 | 0.017543 | 0.0084296 | 0.041097 | -0.011702 | -0.0072033 | 0.017534 | 0.045776 | 0.091553 | -0.19226 | 0.07782 | 0.11444 | 0.16479 | -0.16479 | 0.21515 | 0.16022 | -0.19684 | 122.3923 | -0.082397 | 122.6303 | 122.6624 | -0.059509 | 122.3877 | -0.013733 | 0.23804 | 122.4197 | 122.7997 | 122.699 | 122.6761 | 122.6303 | 122.7448 | 122.7493 | 122.3877 | 122.6761 | 122.6303 | 122.7493 | 122.699 | 122.7448 | -0.36621 | -0.37079
1473.75 | 122.8409 | -122.58 | 0.15564 | 0.13054 | 0.017329 | 0.0077888 | 0.041738 | -0.014052 | -0.0089123 | 0.017748 | 0.013733 | 0.09613 | -0.20142 | 0.073242 | 0.10529 | 0.13275 | -0.13733 | 0.20142 | 0.16022 | -0.21057 | 122.3785 | -0.05951 | 122.5937 | 122.6532 | -0.050354 | 122.3694 | 0.004577 | 0.21515 | 122.4426 | 122.7814 | 122.6852 | 122.6761 | 122.5937 | 122.7402 | 122.7127 | 122.3694 | 122.6761 | 122.5937 | 122.7127 | 122.6852 | 122.7402 | -0.35706 | -0.36621
1475.4219 | 122.9233 | -122.5708 | 0.13275 | 0.016098 | 0.015834 | 0.0026618 | 0.039815 | -0.015761 | -0.0086987 | 0.018816 | -0.032043 | 0.10986 | -0.21973 | 0.027466 | 0.082397 | 0.13275 | -0.09613 | 0.18768 | 0.16937 | -0.21057 | 122.3511 | -0.022888 | 122.5388 | 122.5983 | -0.050354 | 122.3602 | 0.036622 | 0.18768 | 122.4747 | 122.7585 | 122.6532 | 122.6807 | 122.5388 | 122.7402 | 122.7036 | 122.3602 | 122.6807 | 122.5388 | 122.7036 | 122.6532 | 122.7402 | -0.35248 | -0.34332
1477.1094 | 122.8043 | -122.6349 | 0.16479 | 0.1992 | 0.016261 | 0.0094978 | 0.044728 | -0.012557 | -0.0086987 | 0.017962 | 0.050354 | 0.10071 | -0.18768 | 0.09613 | 0.11444 | 0.15564 | -0.17395 | 0.21973 | 0.15106 | -0.20142 | 122.4472 | -0.064087 | 122.6852 | 122.731 | -0.050354 | 122.4335 | -0.013733 | 0.23804 | 122.4609 | 122.8546 | 122.7493 | 122.7356 | 122.6852 | 122.7859 | 122.7905 | 122.4335 | 122.7356 | 122.6852 | 122.7905 | 122.7493 | 122.7859 | -0.35248 | -0.36621
1478.7812 | 122.818 | -122.6074 | 0.16479 | 0.19157 | 0.016902 | 0.0043708 | 0.042592 | -0.014479 | -0.011476 | 0.018816 | 0.041199 | 0.10071 | -0.21515 | 0.082397 | 0.09613 | 0.16937 | -0.17395 | 0.2243 | 0.16022 | -0.19226 | 122.3923 | -0.064087 | 122.6486 | 122.6898 | -0.068665 | 122.4152 | -0.004578 | 0.25635 | 122.4335 | 122.8317 | 122.7036 | 122.7081 | 122.6486 | 122.7676 | 122.7768 | 122.4152 | 122.7081 | 122.6486 | 122.7768 | 122.7036 | 122.7676 | -0.37994 | -0.35706
1480.4531 | 122.9279 | -122.5662 | 0.14648 | 0.023727 | 0.01797 | 0.0028754 | 0.042592 | -0.014693 | -0.0084851 | 0.016253 | -0.036621 | 0.10071 | -0.2243 | 0.018311 | 0.07782 | 0.10986 | -0.082397 | 0.1831 | 0.17853 | -0.19226 | 122.3419 | -0.045776 | 122.5296 | 122.5845 | -0.068664 | 122.374 | 0.032044 | 0.18768 | 122.4838 | 122.7493 | 122.644 | 122.6669 | 122.5296 | 122.7448 | 122.6761 | 122.374 | 122.6669 | 122.5296 | 122.6761 | 122.644 | 122.7448 | -0.37079 | -0.33874
1482.1406 | 122.8409 | -122.6074 | 0.1831 | 0.00083945 | 0.015407 | 0.0062934 | 0.050069 | -0.012557 | -0.010408 | 0.017107 | -0.027466 | 0.14191 | -0.26093 | 0.009155 | 0.013733 | 0.018311 | -0.004578 | 0.09613 | 0.19684 | -0.23804 | 122.3465 | -0.041198 | 122.58 | 122.6166 | -0.16937 | 122.3694 | 0.013733 | 0.23346 | 122.6028 | 122.7036 | 122.6212 | 122.7493 | 122.58 | 122.8043 | 122.6257 | 122.3694 | 122.7493 | 122.58 | 122.6257 | 122.6212 | 122.8043 | -0.44403 | -0.42114
1483.8125 | 122.7951 | -122.6028 | 0.17395 | 0.15343 | 0.014552 | 0.0084296 | 0.044088 | -0.009566 | -0.0072033 | 0.016893 | 0.004578 | 0.11444 | -0.20599 | 0.073242 | 0.10071 | 0.14648 | -0.14648 | 0.20142 | 0.16022 | -0.19684 | 122.3969 | -0.059509 | 122.6074 | 122.6761 | -0.073242 | 122.406 | -0.013733 | 0.21057 | 122.4564 | 122.8043 | 122.7036 | 122.7173 | 122.6074 | 122.7631 | 122.7493 | 122.406 | 122.7173 | 122.6074 | 122.7493 | 122.7036 | 122.7631 | -0.37994 | -0.37079
1485.4844 | 122.8683 | -122.5845 | 0.17395 | 0.084762 | 0.01562 | 0.0054388 | 0.039601 | -0.014266 | -0.0076305 | 0.017321 | 0.004578 | 0.10986 | -0.2243 | 0.041199 | 0.073242 | 0.1236 | -0.13275 | 0.18768 | 0.14648 | -0.20142 | 122.3602 | -0.064087 | 122.5891 | 122.6257 | -0.10071 | 122.3831 | -0.027466 | 0.22888 | 122.4518 | 122.7722 | 122.6578 | 122.6944 | 122.5891 | 122.731 | 122.7081 | 122.3831 | 122.6944 | 122.5891 | 122.7081 | 122.6578 | 122.731 | -0.39825 | -0.37537
1487.1562 | 122.7905 | -122.612 | 0.16937 | 0.1458 | 0.017116 | 0.0062934 | 0.046224 | -0.013198 | -0.0078443 | 0.019243 | 0.054932 | 0.09613 | -0.21973 | 0.086975 | 0.10071 | 0.15564 | -0.16937 | 0.19226 | 0.13733 | -0.20142 | 122.3923 | -0.073243 | 122.6669 | 122.699 | -0.068665 | 122.4106 | -0.032044 | 0.27466 | 122.4426 | 122.8043 | 122.7127 | 122.7081 | 122.6669 | 122.7493 | 122.7676 | 122.4106 | 122.7081 | 122.6669 | 122.7676 | 122.7127 | 122.7493 | -0.3891 | -0.37079
1488.8438 | 122.8088 | -122.6212 | 0.17395 | 0.1458 | 0.016475 | 0.0075752 | 0.041951 | -0.012343 | -0.0076305 | 0.015825 | 0.041199 | 0.10986 | -0.19684 | 0.082397 | 0.11444 | 0.16479 | -0.16937 | 0.19684 | 0.16479 | -0.18768 | 122.4243 | -0.064087 | 122.6624 | 122.7036 | -0.059509 | 122.4335 | -0.009155 | 0.23804 | 122.4518 | 122.818 | 122.7356 | 122.731 | 122.6624 | 122.7859 | 122.7859 | 122.4335 | 122.731 | 122.6624 | 122.7859 | 122.7356 | 122.7859 | -0.37079 | -0.36163
1490.5156 | 122.818 | -122.612 | 0.16022 | 0.13054 | 0.016047 | 0.0050116 | 0.040029 | -0.011275 | -0.010194 | 0.016253 | 0.027466 | 0.10071 | -0.18768 | 0.064087 | 0.086975 | 0.16022 | -0.15564 | 0.20142 | 0.14648 | -0.19684 | 122.4243 | -0.059509 | 122.6395 | 122.6761 | -0.073242 | 122.4152 | -0.013733 | 0.21515 | 122.4564 | 122.8134 | 122.699 | 122.7127 | 122.6395 | 122.7585 | 122.7722 | 122.4152 | 122.7127 | 122.6395 | 122.7722 | 122.699 | 122.7585 | -0.3479 | -0.35706
1492.2031 | 122.9279 | -122.5525 | 0.13733 | 0.054245 | 0.015193 | 0.0033026 | 0.038747 | -0.014693 | -0.0080579 | 0.016039 | -0.036621 | 0.11444 | -0.22888 | 0.027466 | 0.073242 | 0.10986 | -0.082397 | 0.16937 | 0.17395 | -0.21515 | 122.3236 | -0.022888 | 122.5159 | 122.58 | -0.064087 | 122.3373 | 0.036621 | 0.19226 | 122.4701 | 122.7219 | 122.6257 | 122.6669 | 122.5159 | 122.7264 | 122.6624 | 122.3373 | 122.6669 | 122.5159 | 122.6624 | 122.6257 | 122.7264 | -0.36621 | -0.35248
1493.875 | 122.85 | -122.6074 | 0.18768 | 0.084762 | 0.017543 | 0.0024482 | 0.049642 | -0.014266 | -0.010408 | 0.017321 | -0.064087 | 0.15564 | -0.25635 | -0.013733 | -0.004578 | 0.022888 | 0.032043 | 0.07782 | 0.17853 | -0.24261 | 122.3511 | -0.032043 | 122.5433 | 122.5937 | -0.19226 | 122.3648 | -0.009155 | 0.19226 | 122.6395 | 122.6852 | 122.6028 | 122.7631 | 122.5433 | 122.7859 | 122.6303 | 122.3648 | 122.7631 | 122.5433 | 122.6303 | 122.6028 | 122.7859 | -0.44403 | -0.4303
1495.5469 | 122.8363 | -122.6074 | 0.17395 | 0.1992 | 0.016475 | 0.00095277 | 0.042379 | -0.012557 | -0.0099805 | 0.017107 | -0.009155 | 0.11444 | -0.21973 | 0.045776 | 0.082397 | 0.1236 | -0.13275 | 0.17853 | 0.15564 | -0.19684 | 122.3877 | -0.059509 | 122.5983 | 122.6532 | -0.091553 | 122.4106 | -0.01831 | 0.21057 | 122.4747 | 122.7859 | 122.6898 | 122.7219 | 122.5983 | 122.7631 | 122.731 | 122.4106 | 122.7219 | 122.5983 | 122.731 | 122.6898 | 122.7631 | -0.39368 | -0.37079
1497.2188 | 122.9004 | -122.5708 | 0.13733 | -0.12886 | 0.015834 | 0.0056524 | 0.03832 | -0.01512 | -0.0076305 | 0.017534 | 0.009155 | 0.10071 | -0.21515 | 0.10071 | 0.13733 | 0.18768 | -0.12817 | 0.27924 | 0.14648 | -0.19226 | 122.3557 | -0.036621 | 122.58 | 122.6715 | 0 | 122.3785 | 0.009155 | 0.2243 | 122.4426 | 122.85 | 122.7081 | 122.6715 | 122.58 | 122.7173 | 122.7585 | 122.3785 | 122.6715 | 122.58 | 122.7585 | 122.7081 | 122.7173 | -0.35248 | -0.32959
1498.9688 | 122.818 | -122.6074 | 0.17853 | -0.090714 | 0.015193 | 0.0037298 | 0.048146 | -0.012557 | -0.0095531 | 0.018175 | 0.009155 | 0.15106 | -0.25177 | 0.027466 | 0.054932 | 0.082397 | -0.013733 | 0.15564 | 0.18768 | -0.2243 | 122.3557 | -0.027466 | 122.6166 | 122.6349 | -0.1236 | 122.3831 | 0.009155 | 0.26093 | 122.5937 | 122.7631 | 122.6624 | 122.7585 | 122.6166 | 122.7951 | 122.6898 | 122.3831 | 122.7585 | 122.6166 | 122.6898 | 122.6624 | 122.7951 | -0.4303 | -0.40283
1500.6562 | 122.9004 | -122.5571 | 0.15564 | -0.16701 | 0.014125 | 0.00095277 | 0.040029 | -0.012343 | -0.0099805 | 0.017534 | 0.050354 | 0.09613 | -0.20599 | 0.10986 | 0.12817 | 0.18768 | -0.11444 | 0.27008 | 0.15564 | -0.19684 | 122.3511 | -0.05951 | 122.6074 | 122.6669 | -0.027466 | 122.3602 | 0 | 0.25635 | 122.4426 | 122.8271 | 122.6852 | 122.6532 | 122.6074 | 122.7127 | 122.7448 | 122.3602 | 122.6532 | 122.6074 | 122.7448 | 122.6852 | 122.7127 | -0.36163 | -0.35248
1502.3438 | 122.9324 | -122.5662 | 0.13733 | 0.046615 | 0.015193 | 0.0086432 | 0.040242 | -0.012557 | -0.0089123 | 0.016039 | -0.022888 | 0.10071 | -0.21973 | 0.032043 | 0.07782 | 0.1236 | -0.09613 | 0.16937 | 0.16479 | -0.21057 | 122.3465 | -0.036621 | 122.5433 | 122.5983 | -0.059509 | 122.3557 | 0.027466 | 0.19684 | 122.4701 | 122.7356 | 122.644 | 122.6669 | 122.5433 | 122.731 | 122.6898 | 122.3557 | 122.6669 | 122.5433 | 122.6898 | 122.644 | 122.731 | -0.35706 | -0.3479
1504.0156 | 122.8867 | -122.5845 | 0.15106 | -0.22804 | 0.016902 | 0.0028754 | 0.042379 | -0.014266 | -0.0069897 | 0.016253 | 0.036621 | 0.10986 | -0.20599 | 0.091553 | 0.1236 | 0.16479 | -0.11444 | 0.27924 | 0.15564 | -0.19684 | 122.3785 | -0.041199 | 122.6212 | 122.6761 | -0.027466 | 122.3877 | 0.004578 | 0.24262 | 122.4701 | 122.8638 | 122.7081 | 122.6944 | 122.6212 | 122.7402 | 122.7493 | 122.3877 | 122.6944 | 122.6212 | 122.7493 | 122.7081 | 122.7402 | -0.35706 | -0.3479
1505.7188 | 122.8455 | -122.6074 | 0.18768 | 0.054245 | 0.016688 | 0.0088568 | 0.049428 | -0.010848 | -0.0097669 | 0.017107 | -0.050354 | 0.13733 | -0.25635 | -0.009155 | 0 | 0.027466 | 0.018311 | 0.07782 | 0.18768 | -0.2243 | 122.3511 | -0.050354 | 122.5571 | 122.5983 | -0.18768 | 122.3831 | 0 | 0.20599 | 122.6257 | 122.6852 | 122.6074 | 122.7448 | 122.5571 | 122.7951 | 122.6349 | 122.3831 | 122.7448 | 122.5571 | 122.6349 | 122.6074 | 122.7951 | -0.44403 | -0.41199
1507.4062 | 122.8134 | -122.612 | 0.17853 | 0.18394 | 0.016688 | 0.0018072 | 0.044088 | -0.011061 | -0.0097669 | 0.018175 | -0.022888 | 0.12817 | -0.21515 | 0.045776 | 0.073242 | 0.12817 | -0.12817 | 0.17853 | 0.15106 | -0.19226 | 122.3969 | -0.050354 | 122.5891 | 122.6578 | -0.10529 | 122.4197 | -0.027466 | 0.19226 | 122.4838 | 122.7905 | 122.6852 | 122.7402 | 122.5891 | 122.7631 | 122.7402 | 122.4197 | 122.7402 | 122.5891 | 122.7402 | 122.6852 | 122.7631 | -0.39368 | -0.37079
1509.0938 | 122.937 | -122.58 | 0.13275 | 0.054245 | 0.017543 | 0.00031197 | 0.039174 | -0.013411 | -0.0076305 | 0.017321 | -0.022888 | 0.1236 | -0.20599 | 0.018311 | 0.07782 | 0.10529 | -0.068665 | 0.15564 | 0.16479 | -0.22888 | 122.374 | -0.009155 | 122.5571 | 122.5983 | -0.054931 | 122.3511 | 0.032044 | 0.18311 | 122.5113 | 122.7356 | 122.6578 | 122.7036 | 122.5571 | 122.7448 | 122.6852 | 122.3511 | 122.7036 | 122.5571 | 122.6852 | 122.6578 | 122.7448 | -0.33875 | -0.36163
1510.7656 | 122.8867 | -122.612 | 0.17853 | -0.16701 | 0.014979 | 0.0062934 | 0.045797 | -0.012343 | -0.0095531 | 0.017321 | -0.018311 | 0.12817 | -0.25635 | 0.018311 | 0.027466 | 0.054932 | 0.013733 | 0.14648 | 0.18768 | -0.21057 | 122.3557 | -0.050354 | 122.5937 | 122.6303 | -0.15106 | 122.4014 | 0.009155 | 0.23804 | 122.6257 | 122.7585 | 122.6395 | 122.7402 | 122.5937 | 122.7997 | 122.6669 | 122.4014 | 122.7402 | 122.5937 | 122.6669 | 122.6395 | 122.7997 | -0.43488 | -0.3891
1512.4531 | 122.937 | -122.5754 | 0.15106 | 0.00083945 | 0.016475 | 0.00138 | 0.040883 | -0.011489 | -0.0072033 | 0.017107 | -0.032043 | 0.11902 | -0.20599 | 0.022888 | 0.073242 | 0.1236 | -0.086975 | 0.16479 | 0.16479 | -0.21515 | 122.3694 | -0.032043 | 122.5433 | 122.5983 | -0.07782 | 122.3602 | 0.013733 | 0.17395 | 122.4884 | 122.7402 | 122.6486 | 122.6944 | 122.5433 | 122.7402 | 122.699 | 122.3602 | 122.6944 | 122.5433 | 122.699 | 122.6486 | 122.7402 | -0.35706 | -0.36621
1514.1406 | 122.8455 | -122.5937 | 0.15564 | 0.13817 | 0.014766 | 0.0062934 | 0.041097 | -0.012984 | -0.0099805 | 0.017962 | 0.018311 | 0.12817 | -0.20142 | 0.045776 | 0.09613 | 0.14191 | -0.13275 | 0.18768 | 0.16479 | -0.19226 | 122.3923 | -0.027466 | 122.612 | 122.6395 | -0.05951 | 122.4014 | 0.009155 | 0.21973 | 122.4609 | 122.7814 | 122.6898 | 122.7219 | 122.612 | 122.7585 | 122.7356 | 122.4014 | 122.7219 | 122.612 | 122.7356 | 122.6898 | 122.7585 | -0.35706 | -0.3479
1515.8125 | 122.8455 | -122.612 | 0.17853 | 0.10002 | 0.016902 | 0.004798 | 0.047719 | -0.011275 | -0.0093395 | 0.01668 | -0.059509 | 0.15106 | -0.25177 | -0.036621 | -0.009155 | 0.022888 | 0.004578 | 0.073242 | 0.19226 | -0.23346 | 122.3602 | -0.027466 | 122.5525 | 122.5754 | -0.18768 | 122.3785 | 0.013733 | 0.19226 | 122.6166 | 122.6852 | 122.6028 | 122.7631 | 122.5525 | 122.8043 | 122.6349 | 122.3785 | 122.7631 | 122.5525 | 122.6349 | 122.6028 | 122.8043 | -0.4303 | -0.41199
1517.5156 | 122.8363 | -122.6303 | 0.17395 | 0.12291 | 0.013698 | 0.0033026 | 0.042806 | -0.012984 | -0.0084851 | 0.017107 | 0.027466 | 0.09613 | -0.20599 | 0.082397 | 0.10986 | 0.16479 | -0.16022 | 0.21973 | 0.15564 | -0.19684 | 122.4243 | -0.07782 | 122.6578 | 122.7127 | -0.064087 | 122.4335 | -0.01831 | 0.23346 | 122.4701 | 122.85 | 122.7402 | 122.7264 | 122.6578 | 122.7859 | 122.7951 | 122.4335 | 122.7264 | 122.6578 | 122.7951 | 122.7402 | 122.7859 | -0.37994 | -0.37079
1519.2188 | 122.9324 | -122.5708 | 0.14191 | 0.0084684 | 0.015407 | 0.0011664 | 0.042592 | -0.015334 | -0.0078443 | 0.014757 | -0.022888 | 0.11444 | -0.2243 | 0.059509 | 0.086975 | 0.12817 | -0.10071 | 0.20599 | 0.17395 | -0.19226 | 122.3465 | -0.027466 | 122.5479 | 122.6303 | -0.054932 | 122.3785 | 0.032043 | 0.20142 | 122.4701 | 122.7768 | 122.6578 | 122.6852 | 122.5479 | 122.7448 | 122.699 | 122.3785 | 122.6852 | 122.5479 | 122.699 | 122.6578 | 122.7448 | -0.36621 | -0.33417
1521.0156 | 122.8088 | -122.6349 | 0.17853 | -0.083084 | 0.017756 | 0.0071478 | 0.04836 | -0.012557 | -0.010621 | 0.015398 | 0.004578 | 0.12817 | -0.24719 | 0.050354 | 0.045776 | 0.082397 | -0.041199 | 0.16022 | 0.20142 | -0.19684 | 122.3877 | -0.050354 | 122.6395 | 122.6852 | -0.13275 | 122.4381 | 0.022888 | 0.25177 | 122.5937 | 122.7951 | 122.6807 | 122.7631 | 122.6395 | 122.8363 | 122.7173 | 122.4381 | 122.7631 | 122.6395 | 122.7173 | 122.6807 | 122.8363 | -0.42572 | -0.37537
1522.7031 | 122.8043 | -122.6257 | 0.16937 | 0.22972 | 0.016475 | 0.0026618 | 0.041951 | -0.011916 | -0.0082715 | 0.016253 | 0.059509 | 0.10529 | -0.20142 | 0.10529 | 0.13275 | 0.16937 | -0.17395 | 0.23346 | 0.15564 | -0.19226 | 122.4243 | -0.064087 | 122.6852 | 122.731 | -0.036622 | 122.4335 | -0.013733 | 0.26093 | 122.4518 | 122.8592 | 122.7585 | 122.731 | 122.6852 | 122.7814 | 122.7951 | 122.4335 | 122.731 | 122.6852 | 122.7951 | 122.7585 | 122.7814 | -0.37079 | -0.36163
1524.4062 | 122.8088 | -122.612 | 0.15564 | 0.20683 | 0.01797 | 0.0043708 | 0.044301 | -0.010421 | -0.010194 | 0.016893 | 0.045776 | 0.10071 | -0.19684 | 0.086975 | 0.12817 | 0.16937 | -0.19684 | 0.23346 | 0.16937 | -0.18768 | 122.4152 | -0.054932 | 122.6578 | 122.699 | -0.027466 | 122.4243 | 0.013733 | 0.24261 | 122.4152 | 122.8455 | 122.7402 | 122.7127 | 122.6578 | 122.7814 | 122.7814 | 122.4243 | 122.7127 | 122.6578 | 122.7814 | 122.7402 | 122.7814 | -0.35248 | -0.34332
1526.0938 | 122.8363 | -122.612 | 0.1831 | -0.1136 | 0.015407 | 0.0039436 | 0.046865 | -0.013625 | -0.01233 | 0.016039 | -0.018311 | 0.13733 | -0.25635 | 0.027466 | 0.068665 | 0.073242 | -0.013733 | 0.16479 | 0.19684 | -0.21515 | 122.3557 | -0.045776 | 122.5937 | 122.6395 | -0.11444 | 122.3969 | 0.013733 | 0.23804 | 122.5983 | 122.7768 | 122.6807 | 122.7493 | 122.5937 | 122.8088 | 122.6852 | 122.3969 | 122.7493 | 122.5937 | 122.6852 | 122.6807 | 122.8088 | -0.43945 | -0.39825
1527.7812 | 122.9507 | -122.5891 | 0.14191 | -0.25093 | 0.014552 | 0.0018072 | 0.040883 | -0.013198 | -0.010621 | 0.016039 | -0.004578 | 0.11902 | -0.21973 | 0.036621 | 0.082397 | 0.10986 | -0.004578 | 0.19226 | 0.16937 | -0.22888 | 122.3694 | -0.022888 | 122.5845 | 122.6257 | -0.05951 | 122.3602 | 0.027466 | 0.21515 | 122.5845 | 122.7814 | 122.6715 | 122.7081 | 122.5845 | 122.7585 | 122.699 | 122.3602 | 122.7081 | 122.5845 | 122.699 | 122.6715 | 122.7585 | -0.36163 | -0.37079
1529.4844 | 122.8592 | -122.5983 | 0.17395 | 0.061874 | 0.01562 | 0.0041572 | 0.045369 | -0.010848 | -0.0099805 | 0.016893 | -0.050354 | 0.15106 | -0.26093 | -0.022888 | -0.009155 | 0.013733 | 0.036621 | 0.07782 | 0.20599 | -0.2243 | 122.3373 | -0.022888 | 122.5479 | 122.5754 | -0.1831 | 122.374 | 0.032044 | 0.21057 | 122.6349 | 122.6761 | 122.5891 | 122.7493 | 122.5479 | 122.8043 | 122.612 | 122.374 | 122.7493 | 122.5479 | 122.612 | 122.5891 | 122.8043 | -0.43488 | -0.39825
1531.1719 | 122.9187 | -122.58 | 0.16937 | -0.14412 | 0.016902 | -0.0011834 | 0.04131 | -0.014479 | -0.0082715 | 0.016253 | 0.022888 | 0.11902 | -0.21515 | 0.082397 | 0.13733 | 0.13733 | -0.064087 | 0.23804 | 0.15564 | -0.20142 | 122.3648 | -0.050354 | 122.6028 | 122.6624 | -0.032044 | 122.3785 | -0.013733 | 0.23804 | 122.5159 | 122.818 | 122.7173 | 122.699 | 122.6028 | 122.7356 | 122.7173 | 122.3785 | 122.699 | 122.6028 | 122.7173 | 122.7173 | 122.7356 | -0.38452 | -0.37079
1532.8594 | 122.8317 | -122.6166 | 0.16479 | -0.044937 | 0.014766 | 0.0037298 | 0.046437 | -0.011061 | -0.012117 | 0.017107 | -0.009155 | 0.13733 | -0.25177 | 0.036621 | 0.050354 | 0.073242 | -0.009155 | 0.13733 | 0.20142 | -0.22888 | 122.3648 | -0.027466 | 122.6074 | 122.6532 | -0.11444 | 122.3877 | 0.036621 | 0.24261 | 122.6074 | 122.7539 | 122.6669 | 122.7539 | 122.6074 | 122.818 | 122.6898 | 122.3877 | 122.7539 | 122.6074 | 122.6898 | 122.6669 | 122.818 | -0.41656 | -0.39368
1534.5469 | 122.9279 | -122.5891 | 0.13275 | 0.084762 | 0.016688 | 0.00138 | 0.037679 | -0.012343 | -0.0072033 | 0.015184 | -0.022888 | 0.1236 | -0.20599 | 0.022888 | 0.073242 | 0.11902 | -0.082397 | 0.17853 | 0.15564 | -0.20142 | 122.3831 | -0.009155 | 122.5662 | 122.612 | -0.059509 | 122.3877 | 0.022889 | 0.18311 | 122.5067 | 122.7676 | 122.6624 | 122.7127 | 122.5662 | 122.7448 | 122.7081 | 122.3877 | 122.7127 | 122.5662 | 122.7081 | 122.6624 | 122.7448 | -0.33875 | -0.33417
1536.2344 | 122.9233 | -122.5937 | 0.14191 | 0.054245 | 0.016688 | 0.008216 | 0.037465 | -0.014052 | -0.0072033 | 0.018389 | -0.009155 | 0.13275 | -0.21515 | 0.027466 | 0.064087 | 0.12817 | -0.10071 | 0.1831 | 0.16479 | -0.20142 | 122.3785 | -0.009156 | 122.5845 | 122.6212 | -0.07782 | 122.3923 | 0.022888 | 0.20599 | 122.493 | 122.7768 | 122.6578 | 122.7264 | 122.5845 | 122.7585 | 122.7219 | 122.3923 | 122.7264 | 122.5845 | 122.7219 | 122.6578 | 122.7585 | -0.35706 | -0.34332
1537.9844 | 122.9507 | -122.5845 | 0.14191 | 0.061874 | 0.016047 | 0.0062934 | 0.037892 | -0.0097796 | -0.0097669 | 0.015825 | -0.022888 | 0.1236 | -0.21973 | 0.027466 | 0.073242 | 0.10986 | -0.086975 | 0.17395 | 0.18768 | -0.20599 | 122.3648 | -0.018311 | 122.5616 | 122.612 | -0.068665 | 122.3785 | 0.045776 | 0.19684 | 122.4976 | 122.7585 | 122.6578 | 122.7081 | 122.5616 | 122.7722 | 122.6944 | 122.3785 | 122.7081 | 122.5616 | 122.6944 | 122.6578 | 122.7722 | -0.36163 | -0.3479
1539.6719 | 122.8638 | -122.6166 | 0.16022 | 0.15343 | 0.017543 | 0.0039436 | 0.048146 | -0.01277 | -0.010408 | 0.016039 | -0.073242 | 0.13275 | -0.25635 | -0.036621 | -0.032043 | 0.013733 | 0.018311 | 0.068665 | 0.21057 | -0.23804 | 122.3602 | -0.027466 | 122.5433 | 122.58 | -0.19226 | 122.3785 | 0.050354 | 0.18311 | 122.6349 | 122.6852 | 122.5845 | 122.7493 | 122.5433 | 122.8271 | 122.6303 | 122.3785 | 122.7493 | 122.5433 | 122.6303 | 122.5845 | 122.8271 | -0.41657 | -0.39825
1541.375 | 122.8134 | -122.5983 | 0.16937 | 0.1992 | 0.013911 | 0.00052557 | 0.042592 | -0.01277 | -0.0093395 | 0.018602 | -0.027466 | 0.12817 | -0.24719 | 0.036621 | 0.07782 | 0.1236 | -0.12817 | 0.18768 | 0.15564 | -0.20142 | 122.3511 | -0.041199 | 122.5708 | 122.6349 | -0.091553 | 122.3969 | -0.013733 | 0.21973 | 122.4701 | 122.786 | 122.6761 | 122.7264 | 122.5708 | 122.7539 | 122.7219 | 122.3969 | 122.7264 | 122.5708 | 122.7219 | 122.6761 | 122.7539 | -0.41656 | -0.37079
1543.0469 | 122.9324 | -122.5754 | 0.13733 | -0.22041 | 0.018397 | -0.00054263 | 0.042806 | -0.013198 | -0.0091259 | 0.017748 | -0.07782 | 0.15106 | -0.25177 | -0.027466 | 0.009155 | 0.022888 | 0.059509 | 0.11444 | 0.2243 | -0.23346 | 122.3236 | 0.013733 | 122.4976 | 122.5479 | -0.12817 | 122.3419 | 0.086975 | 0.17395 | 122.6349 | 122.6898 | 122.5845 | 122.7264 | 122.4976 | 122.7997 | 122.5983 | 122.3419 | 122.7264 | 122.4976 | 122.5983 | 122.5845 | 122.7997 | -0.3891 | -0.37079
1544.7344 | 122.8912 | -122.6166 | 0.14648 | 0.12291 | 0.016047 | 0.0022346 | 0.037679 | -0.011916 | -0.0086987 | 0.016466 | -0.013733 | 0.12817 | -0.20142 | 0.022888 | 0.082397 | 0.11444 | -0.10986 | 0.1831 | 0.15564 | -0.19226 | 122.4152 | -0.01831 | 122.6028 | 122.6395 | -0.064087 | 122.4243 | 0.009156 | 0.18768 | 122.5067 | 122.7997 | 122.699 | 122.7448 | 122.6028 | 122.7722 | 122.731 | 122.4243 | 122.7448 | 122.6028 | 122.731 | 122.699 | 122.7722 | -0.3479 | -0.33874
1546.4219 | 122.8592 | -122.6028 | 0.17395 | 0.13054 | 0.016902 | 0.0062934 | 0.046224 | -0.01277 | -0.0097669 | 0.017962 | -0.059509 | 0.16022 | -0.25177 | -0.045776 | -0.009155 | 0.018311 | 0.009155 | 0.059509 | 0.21057 | -0.23804 | 122.3511 | -0.013733 | 122.5433 | 122.5571 | -0.1831 | 122.3648 | 0.036621 | 0.19226 | 122.612 | 122.6624 | 122.5937 | 122.7631 | 122.5433 | 122.8134 | 122.6212 | 122.3648 | 122.7631 | 122.5433 | 122.6212 | 122.5937 | 122.8134 | -0.42572 | -0.41199
1548.125 | 122.9507 | -122.5845 | 0.1236 | -0.029679 | 0.014766 | 0.0075752 | 0.038961 | -0.014479 | -0.0082715 | 0.014757 | -0.004578 | 0.11444 | -0.20599 | 0.032043 | 0.10071 | 0.15106 | -0.10529 | 0.21515 | 0.17395 | -0.20599 | 122.3785 | -0.009155 | 122.58 | 122.6166 | -0.022888 | 122.3785 | 0.050354 | 0.20142 | 122.4792 | 122.7997 | 122.6852 | 122.699 | 122.58 | 122.7585 | 122.7356 | 122.3785 | 122.699 | 122.58 | 122.7356 | 122.6852 | 122.7585 | -0.32959 | -0.32959
1549.8125 | 122.9691 | -122.6028 | 0.15106 | -0.2433 | 0.015407 | 0.0043708 | 0.041738 | -0.013839 | -0.0082715 | 0.016893 | -0.027466 | 0.12817 | -0.23804 | 0 | 0.054932 | 0.064087 | 0.032043 | 0.15564 | 0.18768 | -0.22888 | 122.3648 | -0.022888 | 122.5754 | 122.6028 | -0.09613 | 122.374 | 0.036621 | 0.21057 | 122.6349 | 122.7585 | 122.6578 | 122.731 | 122.5754 | 122.7905 | 122.6669 | 122.374 | 122.731 | 122.5754 | 122.6669 | 122.6578 | 122.7905 | -0.3891 | -0.37994
1551.5156 | 122.9095 | -122.6074 | 0.14191 | -0.10597 | 0.014552 | 0.0033026 | 0.03832 | -0.014052 | -0.0089123 | 0.015825 | 0.054932 | 0.11444 | -0.21057 | 0.10986 | 0.14191 | 0.19684 | -0.14648 | 0.27466 | 0.14648 | -0.19684 | 122.3969 | -0.027466 | 122.6624 | 122.7173 | 0 | 122.4106 | 0.004577 | 0.2655 | 122.4609 | 122.8821 | 122.7493 | 122.7219 | 122.6624 | 122.7539 | 122.8043 | 122.4106 | 122.7219 | 122.6624 | 122.8043 | 122.7493 | 122.7539 | -0.35248 | -0.33875
1553.2031 | 122.8729 | -122.6166 | 0.16937 | 0.13817 | 0.016475 | 0.0037298 | 0.046224 | -0.011916 | -0.01233 | 0.016253 | -0.050354 | 0.13733 | -0.25177 | -0.018311 | -0.009155 | 0.041199 | -0.004578 | 0.091553 | 0.20599 | -0.21973 | 122.3648 | -0.032044 | 122.5662 | 122.5983 | -0.17853 | 122.3969 | 0.036621 | 0.20142 | 122.612 | 122.7081 | 122.6074 | 122.7539 | 122.5662 | 122.8226 | 122.6578 | 122.3969 | 122.7539 | 122.5662 | 122.6578 | 122.6074 | 122.8226 | -0.42114 | -0.3891
1554.9375 | 122.8638 | -122.612 | 0.17395 | 0.10765 | 0.015407 | 0.0060798 | 0.046224 | -0.010848 | -0.010835 | 0.017321 | -0.073242 | 0.14191 | -0.25635 | -0.018311 | -0.009155 | 0.013733 | 0.022888 | 0.07782 | 0.20599 | -0.24261 | 122.3557 | -0.032043 | 122.5388 | 122.5937 | -0.1831 | 122.3694 | 0.032044 | 0.18311 | 122.6349 | 122.6898 | 122.6028 | 122.7539 | 122.5388 | 122.818 | 122.6257 | 122.3694 | 122.7539 | 122.5388 | 122.6257 | 122.6028 | 122.818 | -0.4303 | -0.41656
1556.625 | 122.8912 | -122.5983 | 0.15564 | -0.18227 | 0.01562 | 0.004798 | 0.039174 | -0.011275 | -0.0074169 | 0.016466 | 0.027466 | 0.10529 | -0.19684 | 0.10529 | 0.14191 | 0.14648 | -0.10529 | 0.25635 | 0.15564 | -0.20599 | 122.4014 | -0.050354 | 122.6257 | 122.7036 | -0.013733 | 122.3923 | 0 | 0.2243 | 122.493 | 122.8546 | 122.7402 | 122.7036 | 122.6257 | 122.7539 | 122.7448 | 122.3923 | 122.7036 | 122.6257 | 122.7448 | 122.7402 | 122.7539 | -0.35248 | -0.36163
1558.3438 | 122.8409 | -122.6349 | 0.16479 | -0.022049 | 0.015407 | 0.003089 | 0.045369 | -0.011916 | -0.0074169 | 0.017748 | -0.022888 | 0.1236 | -0.23346 | 0.022888 | 0.032043 | 0.059509 | -0.013733 | 0.12817 | 0.20142 | -0.24261 | 122.4014 | -0.041199 | 122.612 | 122.6578 | -0.13275 | 122.3923 | 0.036621 | 0.21057 | 122.6212 | 122.7631 | 122.6669 | 122.7585 | 122.612 | 122.8363 | 122.6944 | 122.3923 | 122.7585 | 122.612 | 122.6944 | 122.6669 | 122.8363 | -0.39825 | -0.40741
1560.0469 | 122.9645 | -122.5983 | 0.14648 | -0.25856 | 0.017116 | 0.0024482 | 0.038533 | -0.014693 | -0.0080579 | 0.01433 | 0.004578 | 0.11444 | -0.20599 | 0.032043 | 0.064087 | 0.091553 | 0 | 0.18768 | 0.17853 | -0.21973 | 122.3923 | -0.032043 | 122.6028 | 122.6303 | -0.082397 | 122.3785 | 0.032044 | 0.21057 | 122.5983 | 122.786 | 122.6624 | 122.7127 | 122.6028 | 122.7768 | 122.6898 | 122.3785 | 122.7127 | 122.6028 | 122.6898 | 122.6624 | 122.7768 | -0.35248 | -0.36621
1561.7344 | 122.8088 | -122.644 | 0.1831 | 0.20683 | 0.016475 | 0.0086432 | 0.044728 | -0.012557 | -0.010835 | 0.016253 | 0.022888 | 0.11902 | -0.21515 | 0.07782 | 0.091553 | 0.14191 | -0.14191 | 0.19684 | 0.15564 | -0.20599 | 122.4289 | -0.064086 | 122.6669 | 122.7219 | -0.091552 | 122.438 | -0.027465 | 0.23804 | 122.5021 | 122.8409 | 122.7356 | 122.7631 | 122.6669 | 122.7997 | 122.7859 | 122.438 | 122.7631 | 122.6669 | 122.7859 | 122.7356 | 122.7997 | -0.39825 | -0.3891
1563.4844 | 122.9279 | -122.5983 | 0.14648 | 0.092392 | 0.015193 | 0.0067206 | 0.039174 | -0.013839 | -0.0078443 | 0.016039 | -0.013733 | 0.13275 | -0.20599 | 0.027466 | 0.064087 | 0.11902 | -0.09613 | 0.18768 | 0.16937 | -0.21973 | 122.3923 | -0.013733 | 122.5845 | 122.6257 | -0.082397 | 122.3785 | 0.022889 | 0.19226 | 122.5021 | 122.786 | 122.6624 | 122.731 | 122.5845 | 122.7676 | 122.7173 | 122.3785 | 122.731 | 122.5845 | 122.7173 | 122.6624 | 122.7676 | -0.35248 | -0.36621
1565.1719 | 122.9095 | -122.5845 | 0.14648 | -0.12123 | 0.014766 | 0.00052557 | 0.039174 | -0.015761 | -0.0059217 | 0.017321 | 0.022888 | 0.10071 | -0.20142 | 0.10071 | 0.13733 | 0.17853 | -0.15106 | 0.28839 | 0.15564 | -0.21057 | 122.3831 | -0.045776 | 122.6074 | 122.6852 | -0.009155 | 122.374 | 0.009156 | 0.2243 | 122.4335 | 122.8729 | 122.7219 | 122.6852 | 122.6074 | 122.7402 | 122.7631 | 122.374 | 122.6852 | 122.6074 | 122.7631 | 122.7219 | 122.7402 | -0.3479 | -0.35706
1566.8906 | 122.9553 | -122.5983 | 0.14648 | -0.26619 | 0.01562 | 0.0050116 | 0.043019 | -0.016402 | -0.0078443 | 0.016253 | -0.073242 | 0.14191 | -0.25635 | -0.018311 | 0.004578 | 0.013733 | 0.086975 | 0.10986 | 0.19684 | -0.23804 | 122.3419 | -0.004577 | 122.525 | 122.58 | -0.14191 | 122.3602 | 0.050354 | 0.18311 | 122.6852 | 122.7081 | 122.6028 | 122.7402 | 122.525 | 122.7951 | 122.612 | 122.3602 | 122.7402 | 122.525 | 122.612 | 122.6028 | 122.7951 | -0.40283 | -0.38452
1568.5781 | 122.905 | -122.6166 | 0.16022 | -0.16701 | 0.013484 | 0.0018072 | 0.040242 | -0.015761 | -0.0084851 | 0.017748 | 0.022888 | 0.10986 | -0.21515 | 0.091553 | 0.13733 | 0.16022 | -0.10071 | 0.25177 | 0.17395 | -0.20142 | 122.4014 | -0.050354 | 122.6395 | 122.7081 | -0.022888 | 122.4152 | 0.013733 | 0.23804 | 122.5159 | 122.8683 | 122.7539 | 122.7264 | 122.6395 | 122.7905 | 122.7768 | 122.4152 | 122.7264 | 122.6395 | 122.7768 | 122.7539 | 122.7905 | -0.37537 | -0.36163
1570.2812 | 122.9233 | -122.5754 | 0.13733 | -0.090714 | 0.015834 | 0.0024482 | 0.041951 | -0.014907 | -0.0078443 | 0.017962 | 0.009155 | 0.11902 | -0.21057 | 0.082397 | 0.11444 | 0.16022 | -0.11902 | 0.25177 | 0.15564 | -0.20599 | 122.3648 | -0.01831 | 122.5845 | 122.6578 | -0.022888 | 122.3694 | 0.018311 | 0.21973 | 122.4564 | 122.8271 | 122.6898 | 122.6944 | 122.5845 | 122.731 | 122.7356 | 122.3694 | 122.6944 | 122.5845 | 122.7356 | 122.6898 | 122.731 | -0.3479 | -0.34332
1571.9531 | 122.8592 | -122.6074 | 0.17853 | 0.13054 | 0.015834 | 0.0071478 | 0.043019 | -0.012984 | -0.0067761 | 0.017962 | 0.041199 | 0.09613 | -0.19226 | 0.064087 | 0.09613 | 0.14191 | -0.16937 | 0.21515 | 0.14648 | -0.19684 | 122.4152 | -0.082398 | 122.6486 | 122.6715 | -0.082398 | 122.4106 | -0.032044 | 0.23346 | 122.438 | 122.8226 | 122.7036 | 122.7036 | 122.6486 | 122.7539 | 122.7493 | 122.4106 | 122.7036 | 122.6486 | 122.7493 | 122.7036 | 122.7539 | -0.37079 | -0.37537
1573.6562 | 122.9187 | -122.6166 | 0.15564 | -0.12123 | 0.014552 | 0.0050116 | 0.042592 | -0.014693 | -0.0069897 | 0.018602 | 0.050354 | 0.10529 | -0.20599 | 0.11902 | 0.11444 | 0.16022 | -0.1236 | 0.27466 | 0.16479 | -0.21515 | 122.4106 | -0.050354 | 122.6669 | 122.7356 | -0.041199 | 122.4014 | 0.009155 | 0.25635 | 122.493 | 122.8912 | 122.731 | 122.7219 | 122.6669 | 122.7814 | 122.7768 | 122.4014 | 122.7219 | 122.6669 | 122.7768 | 122.731 | 122.7814 | -0.36163 | -0.37079
1575.3438 | 122.9645 | -122.5891 | 0.14191 | -0.20515 | 0.016475 | 0.0056524 | 0.045156 | -0.015761 | -0.0082715 | 0.016253 | -0.064087 | 0.14648 | -0.25635 | 0 | 0.022888 | 0.022888 | 0.064087 | 0.11902 | 0.19684 | -0.24719 | 122.3328 | 0.004577 | 122.525 | 122.5891 | -0.11902 | 122.3419 | 0.054931 | 0.19226 | 122.6532 | 122.7081 | 122.612 | 122.7356 | 122.525 | 122.7859 | 122.612 | 122.3419 | 122.7356 | 122.525 | 122.612 | 122.612 | 122.7859 | -0.39826 | -0.3891
1577.0312 | 122.8638 | -122.6395 | 0.16022 | 0.023727 | 0.016902 | 0.0026618 | 0.047292 | -0.010848 | -0.013612 | 0.016039 | -0.041199 | 0.15564 | -0.25177 | -0.004578 | 0.004578 | 0.032043 | -0.004578 | 0.086975 | 0.20142 | -0.2243 | 122.3877 | -0.004577 | 122.5983 | 122.6349 | -0.15564 | 122.4152 | 0.041199 | 0.21057 | 122.6349 | 122.7264 | 122.644 | 122.7951 | 122.5983 | 122.8409 | 122.6715 | 122.4152 | 122.7951 | 122.5983 | 122.6715 | 122.644 | 122.8409 | -0.41199 | -0.38452
1578.75 | 122.9828 | -122.6074 | 0.13733 | -0.17464 | 0.014125 | 0.00138 | 0.04067 | -0.016616 | -0.0097669 | 0.015612 | -0.082397 | 0.13733 | -0.2243 | -0.018311 | 0.027466 | 0.027466 | 0.059509 | 0.14191 | 0.20142 | -0.23346 | 122.3831 | 0 | 122.525 | 122.5891 | -0.10986 | 122.374 | 0.064087 | 0.14191 | 122.6669 | 122.7493 | 122.6349 | 122.7448 | 122.525 | 122.8088 | 122.6349 | 122.374 | 122.7448 | 122.525 | 122.6349 | 122.6349 | 122.8088 | -0.36163 | -0.37079
1580.4219 | 122.905 | -122.5937 | 0.15564 | -0.16701 | 0.017116 | -0.00096983 | 0.038961 | -0.014052 | -0.0074169 | 0.018389 | 0.041199 | 0.10986 | -0.20142 | 0.09613 | 0.13733 | 0.1831 | -0.12817 | 0.28839 | 0.16479 | -0.20142 | 122.3923 | -0.045777 | 122.6349 | 122.6898 | -0.018311 | 122.3923 | 0.009155 | 0.24262 | 122.4655 | 122.8821 | 122.731 | 122.7036 | 122.6349 | 122.7585 | 122.7768 | 122.3923 | 122.7036 | 122.6349 | 122.7768 | 122.731 | 122.7585 | -0.35706 | -0.35706
1582.125 | 122.9324 | -122.6028 | 0.12817 | -0.19753 | 0.013911 | 0.0086432 | 0.047292 | -0.011061 | -0.011476 | 0.01903 | -0.059509 | 0.16022 | -0.23804 | 0.004578 | 0.032043 | 0.045776 | 0.027466 | 0.13275 | 0.20599 | -0.24261 | 122.3648 | 0.032043 | 122.5433 | 122.6074 | -0.096131 | 122.3602 | 0.07782 | 0.17853 | 122.6303 | 122.7356 | 122.6349 | 122.7631 | 122.5433 | 122.8088 | 122.6486 | 122.3602 | 122.7631 | 122.5433 | 122.6486 | 122.6349 | 122.8088 | -0.36621 | -0.37079
1583.8125 | 122.9736 | -122.6074 | 0.15106 | -0.26619 | 0.016688 | 0.00073917 | 0.043874 | -0.01277 | -0.0082715 | 0.017107 | -0.068665 | 0.15564 | -0.27008 | -0.032043 | 0 | 0.027466 | 0.073242 | 0.10529 | 0.21515 | -0.23346 | 122.3373 | 0.004578 | 122.5388 | 122.5754 | -0.15106 | 122.374 | 0.064087 | 0.20142 | 122.6807 | 122.7127 | 122.6074 | 122.7631 | 122.5388 | 122.8226 | 122.6349 | 122.374 | 122.7631 | 122.5388 | 122.6349 | 122.6074 | 122.8226 | -0.42114 | -0.38452
1585.5 | 122.8546 | -122.6349 | 0.17395 | 0.11528 | 0.015407 | 0.0037298 | 0.044515 | -0.01277 | -0.0095531 | 0.017534 | -0.059509 | 0.13275 | -0.24719 | -0.022888 | 0.041199 | 0.082397 | -0.059509 | 0.10986 | 0.20142 | -0.21973 | 122.3877 | -0.041199 | 122.5754 | 122.612 | -0.13275 | 122.4152 | 0.027466 | 0.18768 | 122.5754 | 122.7448 | 122.6761 | 122.7676 | 122.5754 | 122.8363 | 122.7173 | 122.4152 | 122.7676 | 122.5754 | 122.7173 | 122.6761 | 122.8363 | -0.42114 | -0.39368
1587.1875 | 122.85 | -122.6303 | 0.16022 | 0.12291 | 0.012202 | 0.0062934 | 0.03832 | -0.013839 | -0.0072033 | 0.016039 | 0.018311 | 0.10529 | -0.20142 | 0.059509 | 0.11444 | 0.14191 | -0.16022 | 0.20142 | 0.16937 | -0.20142 | 122.4289 | -0.054931 | 122.6486 | 122.6898 | -0.045776 | 122.4289 | 0.009156 | 0.21973 | 122.4701 | 122.8317 | 122.7448 | 122.7356 | 122.6486 | 122.7997 | 122.7722 | 122.4289 | 122.7356 | 122.6486 | 122.7722 | 122.7448 | 122.7997 | -0.36163 | -0.36163
1588.875 | 122.8775 | -122.5937 | 0.17395 | 0.10002 | 0.017116 | 0.0054388 | 0.045797 | -0.0093524 | -0.0084851 | 0.016253 | -0.059509 | 0.1831 | -0.26093 | -0.050354 | -0.009155 | 0.018311 | 0 | 0.064087 | 0.19226 | -0.23346 | 122.3328 | 0.009155 | 122.5342 | 122.5433 | -0.1831 | 122.3602 | 0.018311 | 0.20142 | 122.5937 | 122.6578 | 122.5845 | 122.7768 | 122.5342 | 122.7859 | 122.612 | 122.3602 | 122.7768 | 122.5342 | 122.612 | 122.5845 | 122.7859 | -0.43488 | -0.40741
1590.5625 | 122.85 | -122.6303 | 0.18768 | 0.00083945 | 0.016688 | 0.0041572 | 0.044088 | -0.011916 | -0.0091259 | 0.016253 | -0.036621 | 0.16022 | -0.24261 | -0.004578 | 0.027466 | 0.032043 | -0.004578 | 0.10071 | 0.20599 | -0.21515 | 122.3877 | -0.027466 | 122.5937 | 122.6257 | -0.16022 | 122.4152 | 0.018311 | 0.20599 | 122.6257 | 122.731 | 122.6578 | 122.7905 | 122.5937 | 122.8363 | 122.6624 | 122.4152 | 122.7905 | 122.5937 | 122.6624 | 122.6578 | 122.8363 | -0.4303 | -0.40283
1592.2656 | 122.9004 | -122.6349 | 0.16022 | 0.10002 | 0.014766 | 0.0015936 | 0.04131 | -0.011916 | -0.0076305 | 0.017748 | 0.013733 | 0.13275 | -0.21515 | 0.013733 | 0.07782 | 0.12817 | -0.11902 | 0.17853 | 0.16479 | -0.21515 | 122.4197 | -0.027466 | 122.6486 | 122.6486 | -0.082397 | 122.4197 | 0.004578 | 0.22888 | 122.5159 | 122.8134 | 122.7127 | 122.7676 | 122.6486 | 122.7997 | 122.7631 | 122.4197 | 122.7676 | 122.6486 | 122.7631 | 122.7127 | 122.7997 | -0.37537 | -0.37537
1594 | 122.9095 | -122.6212 | 0.13733 | -0.18227 | 0.014766 | 0.0056524 | 0.038961 | -0.014266 | -0.0067761 | 0.015612 | 0.059509 | 0.10529 | -0.19226 | 0.086975 | 0.13733 | 0.16022 | -0.10529 | 0.27466 | 0.16022 | -0.20599 | 122.4289 | -0.032043 | 122.6807 | 122.7081 | 0 | 122.4152 | 0.022888 | 0.25177 | 122.5159 | 122.8958 | 122.7585 | 122.7264 | 122.6807 | 122.7814 | 122.7814 | 122.4152 | 122.7264 | 122.6807 | 122.7814 | 122.7585 | 122.7814 | -0.32959 | -0.34332
1595.6875 | 122.85 | -122.6212 | 0.16022 | 0.11528 | 0.013911 | 0.0062934 | 0.042592 | -0.011061 | -0.0089123 | 0.017534 | 0.032043 | 0.11444 | -0.21057 | 0.068665 | 0.086975 | 0.15106 | -0.16479 | 0.21515 | 0.16022 | -0.20599 | 122.4106 | -0.045776 | 122.6532 | 122.6898 | -0.073242 | 122.4152 | 0 | 0.24261 | 122.4564 | 122.8363 | 122.7081 | 122.7356 | 122.6532 | 122.7814 | 122.7722 | 122.4152 | 122.7356 | 122.6532 | 122.7722 | 122.7081 | 122.7814 | -0.37079 | -0.36621
1597.375 | 122.8409 | -122.6624 | 0.17853 | -0.075455 | 0.013911 | 0.003089 | 0.047078 | -0.013839 | -0.010621 | 0.017962 | 0 | 0.14191 | -0.24719 | 0.041199 | 0.045776 | 0.073242 | -0.022888 | 0.16022 | 0.16937 | -0.2243 | 122.4152 | -0.036621 | 122.6624 | 122.7036 | -0.13275 | 122.438 | -0.009155 | 0.24719 | 122.6395 | 122.8226 | 122.7081 | 122.8043 | 122.6624 | 122.8317 | 122.7356 | 122.438 | 122.8043 | 122.6624 | 122.7356 | 122.7081 | 122.8317 | -0.42572 | -0.40283
1599.0625 | 123.0011 | -122.5708 | 0.15564 | -0.2433 | 0.014125 | 0.0022346 | 0.04131 | -0.016188 | -0.0080579 | 0.015825 | -0.07782 | 0.16022 | -0.25177 | -0.032043 | -0.004578 | 0.036621 | 0.082397 | 0.1236 | 0.20142 | -0.24719 | 122.319 | 0.004577 | 122.493 | 122.5388 | -0.16022 | 122.3236 | 0.045776 | 0.17395 | 122.6532 | 122.6944 | 122.5662 | 122.731 | 122.493 | 122.7722 | 122.6074 | 122.3236 | 122.731 | 122.493 | 122.6074 | 122.5662 | 122.7722 | -0.40741 | -0.40283
1600.7344 | 122.8455 | -122.6257 | 0.18768 | 0.21446 | 0.014979 | 0.0067206 | 0.04366 | -0.010848 | -0.010408 | 0.018389 | -0.027466 | 0.14191 | -0.22888 | 0.022888 | 0.064087 | 0.10529 | -0.12817 | 0.17853 | 0.17395 | -0.19226 | 122.3969 | -0.045776 | 122.5983 | 122.6486 | -0.1236 | 122.4335 | -0.013733 | 0.20142 | 122.4976 | 122.8043 | 122.6898 | 122.7676 | 122.5983 | 122.7997 | 122.731 | 122.4335 | 122.7676 | 122.5983 | 122.731 | 122.6898 | 122.7997 | -0.41656 | -0.37994
1602.4219 | 122.9645 | -122.5845 | 0.15106 | -0.2433 | 0.017116 | 0.0011664 | 0.042592 | -0.01277 | -0.010194 | 0.016893 | -0.086975 | 0.14648 | -0.28381 | -0.032043 | 0.022888 | 0.022888 | 0.07782 | 0.1236 | 0.20599 | -0.23804 | 122.3007 | -0.004578 | 122.4976 | 122.5525 | -0.12817 | 122.3465 | 0.054932 | 0.19684 | 122.6624 | 122.7081 | 122.6074 | 122.731 | 122.4976 | 122.7905 | 122.6074 | 122.3465 | 122.731 | 122.4976 | 122.6074 | 122.6074 | 122.7905 | -0.43488 | -0.3891
1604.1094 | 122.8729 | -122.644 | 0.15564 | 0.1458 | 0.018184 | 0.0028754 | 0.040029 | -0.011275 | -0.0074169 | 0.016253 | 0.027466 | 0.11902 | -0.2243 | 0.045776 | 0.086975 | 0.1236 | -0.13275 | 0.19684 | 0.15106 | -0.20599 | 122.4197 | -0.036621 | 122.6715 | 122.6898 | -0.068665 | 122.438 | -0.004578 | 0.25177 | 122.5113 | 122.8409 | 122.731 | 122.7631 | 122.6715 | 122.7951 | 122.7676 | 122.438 | 122.7631 | 122.6715 | 122.7676 | 122.731 | 122.7951 | -0.37994 | -0.36163
1605.8125 | 122.8729 | -122.6257 | 0.15564 | 0.15343 | 0.017116 | 0.0073614 | 0.040029 | -0.013411 | -0.0061353 | 0.017962 | 0.027466 | 0.10071 | -0.19226 | 0.041199 | 0.10529 | 0.12817 | -0.13275 | 0.20142 | 0.16937 | -0.20142 | 122.4335 | -0.054932 | 122.6532 | 122.6669 | -0.050354 | 122.4243 | 0.013733 | 0.21973 | 122.493 | 122.8271 | 122.731 | 122.7264 | 122.6532 | 122.7951 | 122.7539 | 122.4243 | 122.7264 | 122.6532 | 122.7539 | 122.731 | 122.7951 | -0.3479 | -0.35706
1607.5 | 122.8821 | -122.6303 | 0.1831 | 0.016098 | 0.015834 | 0.0067206 | 0.048574 | -0.01213 | -0.0095531 | 0.017962 | -0.036621 | 0.12817 | -0.25635 | -0.004578 | -0.004578 | 0.036621 | 0.009155 | 0.09613 | 0.19684 | -0.21057 | 122.374 | -0.054931 | 122.5937 | 122.6257 | -0.18768 | 122.4197 | 0.013733 | 0.21973 | 122.6395 | 122.7264 | 122.6257 | 122.7585 | 122.5937 | 122.8271 | 122.6669 | 122.4197 | 122.7585 | 122.5937 | 122.6669 | 122.6257 | 122.8271 | -0.43945 | -0.39368
1609.1875 | 122.8729 | -122.6257 | 0.16022 | 0.12291 | 0.014338 | 0.00052557 | 0.038533 | -0.01277 | -0.0095531 | 0.017321 | 0 | 0.11444 | -0.21973 | 0.041199 | 0.07782 | 0.12817 | -0.11444 | 0.19684 | 0.17395 | -0.21973 | 122.406 | -0.045776 | 122.6257 | 122.6669 | -0.082397 | 122.406 | 0.013733 | 0.21973 | 122.5113 | 122.8226 | 122.7036 | 122.7402 | 122.6257 | 122.7997 | 122.7539 | 122.406 | 122.7402 | 122.6257 | 122.7539 | 122.7036 | 122.7997 | -0.37994 | -0.37994
1610.875 | 122.9004 | -122.5983 | 0.17395 | 0.15343 | 0.015193 | 0.004798 | 0.045583 | -0.012557 | -0.010621 | 0.016466 | -0.054932 | 0.14648 | -0.25635 | -0.036621 | 0 | 0.018311 | 0.004578 | 0.082397 | 0.19684 | -0.22888 | 122.3419 | -0.027466 | 122.5433 | 122.5616 | -0.17395 | 122.3694 | 0.022888 | 0.20142 | 122.6028 | 122.6807 | 122.5983 | 122.7448 | 122.5433 | 122.7951 | 122.6166 | 122.3694 | 122.7448 | 122.5433 | 122.6166 | 122.5983 | 122.7951 | -0.4303 | -0.40283
1612.5625 | 122.9645 | -122.5891 | 0.13733 | 0.0084684 | 0.014979 | 0.0024482 | 0.035543 | -0.014479 | -0.0067761 | 0.017748 | -0.036621 | 0.13733 | -0.21973 | 0.036621 | 0.068665 | 0.11444 | -0.082397 | 0.1831 | 0.17395 | -0.21515 | 122.3694 | 0 | 122.5525 | 122.6257 | -0.068664 | 122.374 | 0.036621 | 0.18311 | 122.5067 | 122.7722 | 122.6578 | 122.7264 | 122.5525 | 122.7631 | 122.7036 | 122.374 | 122.7264 | 122.5525 | 122.7036 | 122.6578 | 122.7631 | -0.35706 | -0.35248
1614.2656 | 122.8729 | -122.6303 | 0.17853 | -0.12886 | 0.015193 | 0.004798 | 0.046224 | -0.012343 | -0.0091259 | 0.016039 | -0.018311 | 0.15106 | -0.27466 | 0.027466 | 0.041199 | 0.064087 | -0.022888 | 0.16479 | 0.20599 | -0.22888 | 122.3557 | -0.027466 | 122.612 | 122.6578 | -0.13733 | 122.4014 | 0.027466 | 0.25635 | 122.6074 | 122.7951 | 122.6715 | 122.7814 | 122.612 | 122.8363 | 122.6944 | 122.4014 | 122.7814 | 122.612 | 122.6944 | 122.6715 | 122.8363 | -0.45319 | -0.40741
1616 | 122.9553 | -122.6028 | 0.15564 | -0.060196 | 0.013698 | 0.0056524 | 0.037679 | -0.013411 | -0.0074169 | 0.016466 | -0.004578 | 0.10986 | -0.21057 | 0.064087 | 0.10529 | 0.13733 | -0.11444 | 0.22888 | 0.16479 | -0.19226 | 122.3923 | -0.045777 | 122.5983 | 122.6669 | -0.050354 | 122.4106 | 0.009155 | 0.20599 | 122.4884 | 122.8317 | 122.7081 | 122.7127 | 122.5983 | 122.7676 | 122.7402 | 122.4106 | 122.7127 | 122.5983 | 122.7402 | 122.7081 | 122.7676 | -0.36621 | -0.3479
1617.6875 | 122.8821 | -122.6715 | 0.1831 | 0.046615 | 0.015834 | 0.0026618 | 0.045797 | -0.012557 | -0.0078443 | 0.017962 | -0.050354 | 0.14648 | -0.24719 | -0.018311 | 0 | 0.022888 | 0.013733 | 0.09613 | 0.19684 | -0.22888 | 122.4243 | -0.036621 | 122.6212 | 122.6532 | -0.1831 | 122.4426 | 0.013733 | 0.19684 | 122.6852 | 122.7676 | 122.6715 | 122.818 | 122.6212 | 122.8683 | 122.6944 | 122.4426 | 122.818 | 122.6212 | 122.6944 | 122.6715 | 122.8683 | -0.4303 | -0.41199
1619.3906 | 122.9782 | -122.6303 | 0.13275 | -0.21278 | 0.016261 | 0.0075752 | 0.040242 | -0.01747 | -0.0099805 | 0.018175 | -0.068665 | 0.14648 | -0.26093 | -0.009155 | 0.013733 | 0.022888 | 0.068665 | 0.13733 | 0.20142 | -0.24719 | 122.3694 | 0.013733 | 122.5616 | 122.6212 | -0.11902 | 122.3831 | 0.068665 | 0.19226 | 122.699 | 122.7676 | 122.644 | 122.7768 | 122.5616 | 122.8317 | 122.6532 | 122.3831 | 122.7768 | 122.5616 | 122.6532 | 122.644 | 122.8317 | -0.39368 | -0.37994
1621.0938 | 122.8409 | -122.6624 | 0.1831 | -0.10597 | 0.01562 | 0.0052252 | 0.044515 | -0.009566 | -0.011262 | 0.017748 | 0.004578 | 0.13733 | -0.26093 | 0.018311 | 0.054932 | 0.07782 | -0.013733 | 0.16479 | 0.1831 | -0.22888 | 122.4014 | -0.045776 | 122.6669 | 122.6807 | -0.12817 | 122.4335 | 0 | 0.2655 | 122.6486 | 122.8271 | 122.7173 | 122.7997 | 122.6669 | 122.8455 | 122.7402 | 122.4335 | 122.7997 | 122.6669 | 122.7402 | 122.7173 | 122.8455 | -0.44403 | -0.41199
1622.7656 | 122.9736 | -122.6028 | 0.13275 | 0.016098 | 0.01562 | 9.8166e-05 | 0.037679 | -0.013198 | -0.0078443 | 0.016039 | -0.018311 | 0.13733 | -0.21973 | 0.009155 | 0.059509 | 0.11444 | -0.07782 | 0.17395 | 0.16479 | -0.21515 | 122.3831 | 0.004578 | 122.5845 | 122.612 | -0.073242 | 122.3877 | 0.032044 | 0.20142 | 122.525 | 122.7768 | 122.6624 | 122.7402 | 122.5845 | 122.7676 | 122.7173 | 122.3877 | 122.7402 | 122.5845 | 122.7173 | 122.6624 | 122.7676 | -0.35248 | -0.3479
1624.4688 | 122.9416 | -122.6028 | 0.16479 | -0.16701 | 0.014552 | 0.0022346 | 0.040456 | -0.012984 | -0.010621 | 0.017107 | 0.041199 | 0.11444 | -0.21515 | 0.10071 | 0.13275 | 0.15564 | -0.10986 | 0.27924 | 0.15564 | -0.21057 | 122.3877 | -0.050354 | 122.644 | 122.7036 | -0.032044 | 122.3923 | -0.009155 | 0.25635 | 122.493 | 122.8821 | 122.7356 | 122.7173 | 122.644 | 122.7585 | 122.7585 | 122.3923 | 122.7173 | 122.644 | 122.7585 | 122.7356 | 122.7585 | -0.37994 | -0.37537
1626.1719 | 122.8867 | -122.644 | 0.16479 | -0.12123 | 0.017543 | 0.00095277 | 0.046865 | -0.011916 | -0.0095531 | 0.014116 | -0.018311 | 0.14191 | -0.24261 | 0.032043 | 0.045776 | 0.073242 | 0 | 0.16479 | 0.20142 | -0.2243 | 122.4014 | -0.022888 | 122.6257 | 122.6761 | -0.11902 | 122.4197 | 0.036621 | 0.2243 | 122.644 | 122.8088 | 122.6898 | 122.7859 | 122.6257 | 122.8455 | 122.7173 | 122.4197 | 122.7859 | 122.6257 | 122.7173 | 122.6898 | 122.8455 | -0.40741 | -0.3891
1627.8906 | 122.9599 | -122.6028 | 0.15564 | -0.22804 | 0.017329 | 0.002021 | 0.043447 | -0.013198 | -0.0097669 | 0.017962 | -0.073242 | 0.16479 | -0.25177 | -0.004578 | 0.013733 | 0.027466 | 0.054932 | 0.10529 | 0.21057 | -0.24261 | 122.3511 | 0.009155 | 122.5296 | 122.5983 | -0.14191 | 122.3602 | 0.054931 | 0.17853 | 122.6578 | 122.7081 | 122.6166 | 122.7676 | 122.5296 | 122.8134 | 122.6303 | 122.3602 | 122.7676 | 122.5296 | 122.6303 | 122.6166 | 122.8134 | -0.40741 | -0.39826
1629.5625 | 122.85 | -122.6715 | 0.16022 | 0.22972 | 0.016688 | 0.0052252 | 0.042379 | -0.0087116 | -0.0084851 | 0.018389 | 0 | 0.1236 | -0.23346 | 0.045776 | 0.086975 | 0.13733 | -0.14191 | 0.19226 | 0.1831 | -0.19684 | 122.4381 | -0.036621 | 122.6715 | 122.7173 | -0.073242 | 122.4747 | 0.022888 | 0.23346 | 122.5296 | 122.8638 | 122.7585 | 122.7951 | 122.6715 | 122.8546 | 122.8088 | 122.4747 | 122.7951 | 122.6715 | 122.8088 | 122.7585 | 122.8546 | -0.39368 | -0.35706
1631.25 | 122.8455 | -122.6486 | 0.16937 | 0.15343 | 0.014766 | 0.0054388 | 0.043874 | -0.012984 | -0.0097669 | 0.016893 | 0.018311 | 0.10529 | -0.23346 | 0.054932 | 0.09613 | 0.13733 | -0.13733 | 0.20142 | 0.16479 | -0.21057 | 122.4152 | -0.064087 | 122.6669 | 122.7036 | -0.073243 | 122.4381 | -0.004578 | 0.25177 | 122.5113 | 122.85 | 122.7448 | 122.7539 | 122.6669 | 122.8134 | 122.7859 | 122.4381 | 122.7539 | 122.6669 | 122.7859 | 122.7448 | 122.8134 | -0.40283 | -0.37994
1632.9844 | 122.8683 | -122.6669 | 0.18768 | -0.12886 | 0.013698 | 0.0056524 | 0.041951 | -0.014266 | -0.012117 | 0.017748 | -0.013733 | 0.15564 | -0.25635 | 0.027466 | 0.041199 | 0.050354 | -0.013733 | 0.16479 | 0.18768 | -0.21973 | 122.4106 | -0.032043 | 122.6532 | 122.6944 | -0.14648 | 122.4472 | 0 | 0.24262 | 122.6532 | 122.8317 | 122.7081 | 122.8226 | 122.6532 | 122.8546 | 122.7173 | 122.4472 | 122.8226 | 122.6532 | 122.7173 | 122.7081 | 122.8546 | -0.44403 | -0.40741
1634.6719 | 122.9233 | -122.6028 | 0.14648 | -0.18227 | 0.015407 | 0.0026618 | 0.035756 | -0.013411 | -0.0091259 | 0.016253 | 0.036621 | 0.10986 | -0.19684 | 0.086975 | 0.14191 | 0.16022 | -0.11902 | 0.27466 | 0.16479 | -0.19226 | 122.406 | -0.036621 | 122.6395 | 122.6898 | -0.004577 | 122.4106 | 0.018311 | 0.23346 | 122.4838 | 122.8775 | 122.7448 | 122.7127 | 122.6395 | 122.7676 | 122.7631 | 122.4106 | 122.7127 | 122.6395 | 122.7631 | 122.7448 | 122.7676 | -0.34332 | -0.33874
1636.3594 | 122.8821 | -122.644 | 0.16022 | 0.12291 | 0.018397 | 0.00138 | 0.04067 | -0.013625 | -0.0076305 | 0.017534 | 0.041199 | 0.12817 | -0.21057 | 0.059509 | 0.082397 | 0.13733 | -0.13733 | 0.20599 | 0.16479 | -0.20599 | 122.4335 | -0.032043 | 122.6852 | 122.7036 | -0.07782 | 122.438 | 0.004578 | 0.25177 | 122.5067 | 122.85 | 122.7264 | 122.7722 | 122.6852 | 122.8088 | 122.7814 | 122.438 | 122.7722 | 122.6852 | 122.7814 | 122.7264 | 122.8088 | -0.37079 | -0.36621
1638.0625 | 122.8638 | -122.6486 | 0.16937 | 0.12291 | 0.014552 | 0.0022346 | 0.043019 | -0.013411 | -0.010621 | 0.015612 | 0.027466 | 0.10071 | -0.21057 | 0.068665 | 0.09613 | 0.16479 | -0.16479 | 0.21973 | 0.16479 | -0.17395 | 122.4381 | -0.068665 | 122.6761 | 122.7173 | -0.073243 | 122.4747 | -0.004578 | 0.23804 | 122.4838 | 122.8683 | 122.7448 | 122.7493 | 122.6761 | 122.8134 | 122.8134 | 122.4747 | 122.7493 | 122.6761 | 122.8134 | 122.7448 | 122.8134 | -0.37994 | -0.34332
1639.75 | 122.937 | -122.6166 | 0.15106 | -0.16701 | 0.014338 | 9.8166e-05 | 0.042379 | -0.013198 | -0.0091259 | 0.017107 | 0.027466 | 0.11902 | -0.21057 | 0.09613 | 0.11444 | 0.15564 | -0.09613 | 0.2655 | 0.16479 | -0.2243 | 122.406 | -0.032043 | 122.644 | 122.7127 | -0.036621 | 122.3923 | 0.013733 | 0.23804 | 122.5204 | 122.8821 | 122.731 | 122.7356 | 122.644 | 122.7814 | 122.7722 | 122.3923 | 122.7356 | 122.644 | 122.7722 | 122.731 | 122.7814 | -0.36163 | -0.37537
1641.4375 | 122.9645 | -122.6028 | 0.15106 | -0.0067901 | 0.016261 | 0.0024482 | 0.039815 | -0.013839 | -0.0072033 | 0.016039 | -0.022888 | 0.1236 | -0.23804 | 0.041199 | 0.091553 | 0.13275 | -0.09613 | 0.21973 | 0.16937 | -0.21057 | 122.3648 | -0.027466 | 122.58 | 122.644 | -0.059509 | 122.3923 | 0.018311 | 0.21515 | 122.5067 | 122.8226 | 122.6944 | 122.7264 | 122.58 | 122.7722 | 122.7356 | 122.3923 | 122.7264 | 122.58 | 122.7356 | 122.6944 | 122.7722 | -0.3891 | -0.36163
1643.1094 | 122.9599 | -122.6257 | 0.16022 | -0.22041 | 0.016261 | -0.00075623 | 0.041097 | -0.017256 | -0.0091259 | 0.017107 | 0.027466 | 0.10986 | -0.23804 | 0.068665 | 0.073242 | 0.10529 | -0.022888 | 0.21515 | 0.1831 | -0.2243 | 122.3877 | -0.050354 | 122.6532 | 122.6944 | -0.086975 | 122.4014 | 0.022888 | 0.2655 | 122.6028 | 122.8409 | 122.699 | 122.7356 | 122.6532 | 122.8088 | 122.731 | 122.4014 | 122.7356 | 122.6532 | 122.731 | 122.699 | 122.8088 | -0.39825 | -0.38452
1644.7812 | 122.8912 | -122.644 | 0.16479 | 0.15343 | 0.01327 | 0.0018072 | 0.04366 | -0.011916 | -0.010621 | 0.014757 | 0.032043 | 0.11444 | -0.21973 | 0.064087 | 0.082397 | 0.1236 | -0.14191 | 0.20142 | 0.16479 | -0.21057 | 122.4243 | -0.050354 | 122.6761 | 122.7081 | -0.082398 | 122.4335 | 0 | 0.25177 | 122.5021 | 122.8455 | 122.7264 | 122.7585 | 122.6761 | 122.8088 | 122.7676 | 122.4335 | 122.7585 | 122.6761 | 122.7676 | 122.7264 | 122.8088 | -0.38452 | -0.37537
1646.4688 | 122.9599 | -122.6074 | 0.16022 | -0.26619 | 0.014979 | 0.0033026 | 0.044301 | -0.014266 | -0.0089123 | 0.013903 | -0.004578 | 0.11444 | -0.2243 | 0.064087 | 0.073242 | 0.10071 | -0.009155 | 0.21515 | 0.1831 | -0.2243 | 122.3831 | -0.045776 | 122.6028 | 122.6715 | -0.086975 | 122.3831 | 0.022888 | 0.21973 | 122.5983 | 122.8226 | 122.6807 | 122.7219 | 122.6028 | 122.7905 | 122.7081 | 122.3831 | 122.7219 | 122.6028 | 122.7081 | 122.6807 | 122.7905 | -0.38452 | -0.38452
1648.1562 | 122.8226 | -122.6578 | 0.1831 | 0.1992 | 0.016475 | 0.0035162 | 0.042592 | -0.010634 | -0.0084851 | 0.016253 | 0.07782 | 0.10986 | -0.21973 | 0.086975 | 0.10986 | 0.15564 | -0.20142 | 0.21973 | 0.16022 | -0.19226 | 122.438 | -0.073242 | 122.7356 | 122.7448 | -0.073242 | 122.4655 | -0.022888 | 0.29755 | 122.4564 | 122.8775 | 122.7676 | 122.7676 | 122.7356 | 122.818 | 122.8134 | 122.4655 | 122.7676 | 122.7356 | 122.8134 | 122.7676 | 122.818 | -0.40283 | -0.37537
1649.8438 | 122.8683 | -122.644 | 0.18768 | -0.01442 | 0.013911 | 0.0033026 | 0.04601 | -0.010848 | -0.0095531 | 0.017321 | -0.022888 | 0.13733 | -0.24261 | 0.013733 | 0.032043 | 0.036621 | -0.022888 | 0.11444 | 0.20142 | -0.23346 | 122.4014 | -0.050354 | 122.6212 | 122.6578 | -0.15564 | 122.4106 | 0.013733 | 0.21973 | 122.6212 | 122.7585 | 122.6761 | 122.7814 | 122.6212 | 122.8455 | 122.6807 | 122.4106 | 122.7814 | 122.6212 | 122.6807 | 122.6761 | 122.8455 | -0.4303 | -0.42114
1651.5312 | 122.9828 | -122.612 | 0.12817 | 0.0084684 | 0.016902 | 0.0056524 | 0.039601 | -0.010421 | -0.0065625 | 0.015398 | -0.032043 | 0.10986 | -0.21515 | 0.022888 | 0.086975 | 0.10071 | -0.086975 | 0.18768 | 0.16479 | -0.21973 | 122.3969 | -0.018311 | 122.58 | 122.6349 | -0.041199 | 122.3923 | 0.036621 | 0.18311 | 122.525 | 122.7997 | 122.699 | 122.7219 | 122.58 | 122.7768 | 122.7127 | 122.3923 | 122.7219 | 122.58 | 122.7127 | 122.699 | 122.7768 | -0.34332 | -0.3479
1653.2188 | 122.9691 | -122.6074 | 0.14191 | -0.19753 | 0.018184 | -0.00032903 | 0.043874 | -0.013839 | -0.0089123 | 0.016039 | -0.059509 | 0.16479 | -0.26093 | -0.013733 | 0 | 0.027466 | 0.059509 | 0.1236 | 0.21973 | -0.25177 | 122.3465 | 0.022888 | 122.5479 | 122.5937 | -0.14191 | 122.3557 | 0.07782 | 0.20142 | 122.6669 | 122.731 | 122.6074 | 122.7722 | 122.5479 | 122.8271 | 122.6349 | 122.3557 | 122.7722 | 122.5479 | 122.6349 | 122.6074 | 122.8271 | -0.40283 | -0.39368
1654.9688 | 122.9599 | -122.6212 | 0.15106 | 0.046615 | 0.015407 | 0.00138 | 0.038747 | -0.011275 | -0.0082715 | 0.017321 | -0.018311 | 0.10529 | -0.20142 | 0.027466 | 0.068665 | 0.1236 | -0.10071 | 0.16479 | 0.16022 | -0.20599 | 122.4197 | -0.045776 | 122.6028 | 122.6486 | -0.082397 | 122.4152 | 0.009155 | 0.18311 | 122.5204 | 122.7859 | 122.6898 | 122.7264 | 122.6028 | 122.7814 | 122.7448 | 122.4152 | 122.7264 | 122.6028 | 122.7448 | 122.6898 | 122.7814 | -0.35248 | -0.35706
1656.6562 | 122.8638 | -122.6761 | 0.18768 | -0.044937 | 0.017116 | 0.0050116 | 0.046865 | -0.010421 | -0.010621 | 0.017962 | -0.013733 | 0.13275 | -0.25635 | 0.022888 | 0.041199 | 0.059509 | -0.013733 | 0.12817 | 0.20599 | -0.2243 | 122.4197 | -0.054932 | 122.6624 | 122.699 | -0.14648 | 122.4518 | 0.018311 | 0.24262 | 122.6624 | 122.8043 | 122.7173 | 122.8088 | 122.6624 | 122.8821 | 122.7356 | 122.4518 | 122.8088 | 122.6624 | 122.7356 | 122.7173 | 122.8821 | -0.44403 | -0.41199
1658.3594 | 122.8638 | -122.6395 | 0.17853 | 0.16869 | 0.015407 | 0.0041572 | 0.040029 | -0.011489 | -0.0082715 | 0.01668 | 0.041199 | 0.11902 | -0.22888 | 0.086975 | 0.11902 | 0.15106 | -0.16937 | 0.23346 | 0.16937 | -0.20599 | 122.4106 | -0.059509 | 122.6807 | 122.7264 | -0.059509 | 122.4335 | -0.009155 | 0.27008 | 122.4701 | 122.8729 | 122.7585 | 122.7585 | 122.6807 | 122.8088 | 122.7905 | 122.4335 | 122.7585 | 122.6807 | 122.7905 | 122.7585 | 122.8088 | -0.40741 | -0.38452
1660.0469 | 122.8912 | -122.6532 | 0.16479 | 0.069504 | 0.014125 | 0.0045844 | 0.047292 | -0.011275 | -0.010621 | 0.01967 | -0.054932 | 0.16479 | -0.2655 | -0.041199 | -0.009155 | 0.009155 | 0.027466 | 0.082397 | 0.21515 | -0.24719 | 122.3877 | 0 | 122.5983 | 122.612 | -0.17395 | 122.406 | 0.050354 | 0.21057 | 122.6807 | 122.7356 | 122.644 | 122.818 | 122.5983 | 122.8683 | 122.6624 | 122.406 | 122.818 | 122.5983 | 122.6624 | 122.644 | 122.8683 | -0.4303 | -0.41199
1661.7344 | 122.9599 | -122.6303 | 0.16022 | -0.14412 | 0.015407 | 9.8166e-05 | 0.043233 | -0.01213 | -0.0097669 | 0.017748 | -0.07782 | 0.14191 | -0.25635 | -0.009155 | 0.022888 | 0.022888 | 0.045776 | 0.13733 | 0.20599 | -0.24261 | 122.374 | -0.01831 | 122.5525 | 122.6212 | -0.13733 | 122.3877 | 0.045777 | 0.17853 | 122.6761 | 122.7676 | 122.6532 | 122.7722 | 122.5525 | 122.8363 | 122.6532 | 122.3877 | 122.7722 | 122.5525 | 122.6532 | 122.6532 | 122.8363 | -0.41657 | -0.40283
1663.4375 | 122.9324 | -122.6395 | 0.15106 | -0.12886 | 0.014766 | 0.0028754 | 0.036611 | -0.013198 | -0.0082715 | 0.01668 | 0.032043 | 0.10529 | -0.21515 | 0.10986 | 0.13275 | 0.17395 | -0.14191 | 0.25635 | 0.15564 | -0.21973 | 122.4243 | -0.045776 | 122.6715 | 122.7493 | -0.018311 | 122.4197 | 0.004578 | 0.24719 | 122.4976 | 122.8958 | 122.7722 | 122.7448 | 122.6715 | 122.7951 | 122.8134 | 122.4197 | 122.7448 | 122.6715 | 122.8134 | 122.7722 | 122.7951 | -0.36621 | -0.37079
1665.125 | 122.937 | -122.6166 | 0.16479 | 0.084762 | 0.016475 | 0.0045844 | 0.040029 | -0.011489 | -0.0076305 | 0.016253 | 0.013733 | 0.14191 | -0.2243 | 0.036621 | 0.073242 | 0.1236 | -0.10071 | 0.17853 | 0.16937 | -0.19684 | 122.3923 | -0.022888 | 122.6303 | 122.6532 | -0.091553 | 122.4197 | 0.004578 | 0.23804 | 122.5159 | 122.7951 | 122.6898 | 122.7585 | 122.6303 | 122.7859 | 122.7402 | 122.4197 | 122.7585 | 122.6303 | 122.7402 | 122.6898 | 122.7859 | -0.3891 | -0.36163
1666.8281 | 122.8409 | -122.6578 | 0.18768 | 0.18394 | 0.016475 | 0.0022346 | 0.04366 | -0.010634 | -0.0089123 | 0.016039 | 0.045776 | 0.10529 | -0.21515 | 0.082397 | 0.11444 | 0.15564 | -0.19684 | 0.23804 | 0.15106 | -0.19684 | 122.4426 | -0.082397 | 122.7036 | 122.7402 | -0.073242 | 122.4609 | -0.036621 | 0.26093 | 122.4609 | 122.8958 | 122.7722 | 122.7631 | 122.7036 | 122.8088 | 122.8134 | 122.4609 | 122.7631 | 122.7036 | 122.8134 | 122.7722 | 122.8088 | -0.40283 | -0.38452
1668.5156 | 122.8683 | -122.6624 | 0.17853 | -0.075455 | 0.016261 | 0.0037298 | 0.047719 | -0.01213 | -0.0099805 | 0.016039 | -0.009155 | 0.13733 | -0.25177 | 0.027466 | 0.050354 | 0.059509 | -0.018311 | 0.14191 | 0.20599 | -0.23346 | 122.4106 | -0.041199 | 122.6532 | 122.6898 | -0.12817 | 122.4289 | 0.027466 | 0.24261 | 122.644 | 122.8043 | 122.7127 | 122.7997 | 122.6532 | 122.8683 | 122.7219 | 122.4289 | 122.7997 | 122.6532 | 122.7219 | 122.7127 | 122.8683 | -0.4303 | -0.41199
1670.2031 | 122.85 | -122.6669 | 0.19226 | -0.044937 | 0.016261 | 0.0075752 | 0.044728 | -0.012557 | -0.0097669 | 0.019243 | -0.009155 | 0.13275 | -0.24719 | 0.027466 | 0.045776 | 0.086975 | -0.022888 | 0.16479 | 0.20142 | -0.23346 | 122.4197 | -0.05951 | 122.6578 | 122.6944 | -0.14648 | 122.4335 | 0.009155 | 0.23804 | 122.644 | 122.8317 | 122.7127 | 122.7997 | 122.6578 | 122.8683 | 122.7539 | 122.4335 | 122.7997 | 122.6578 | 122.7539 | 122.7127 | 122.8683 | -0.43945 | -0.42572
1671.9531 | 122.8546 | -122.6669 | 0.16937 | 0.19157 | 0.014552 | 0.0028754 | 0.041524 | -0.0097796 | -0.010621 | 0.016893 | -0.009155 | 0.13275 | -0.2243 | 0.059509 | 0.10071 | 0.14648 | -0.15564 | 0.19684 | 0.16479 | -0.20142 | 122.4426 | -0.036622 | 122.6578 | 122.7264 | -0.068665 | 122.4655 | -0.004578 | 0.21515 | 122.5113 | 122.8638 | 122.7676 | 122.7997 | 122.6578 | 122.8317 | 122.8134 | 122.4655 | 122.7997 | 122.6578 | 122.8134 | 122.7676 | 122.8317 | -0.39368 | -0.37079
1673.6406 | 122.8775 | -122.6578 | 0.1831 | -0.12886 | 0.016261 | 0.0018072 | 0.045583 | -0.012343 | -0.0097669 | 0.01668 | -0.027466 | 0.13275 | -0.25635 | 0.032043 | 0.054932 | 0.07782 | -0.013733 | 0.17395 | 0.20599 | -0.2243 | 122.4014 | -0.050354 | 122.6303 | 122.6898 | -0.12817 | 122.4335 | 0.022889 | 0.22888 | 122.644 | 122.8317 | 122.7127 | 122.7905 | 122.6303 | 122.8638 | 122.7356 | 122.4335 | 122.7905 | 122.6303 | 122.7356 | 122.7127 | 122.8638 | -0.43945 | -0.40741
1675.3125 | 122.9553 | -122.6578 | 0.13275 | -0.090714 | 0.016475 | 0.0026618 | 0.03597 | -0.012557 | -0.0080579 | 0.015612 | 0.004578 | 0.1236 | -0.19684 | 0.082397 | 0.14648 | 0.16479 | -0.11444 | 0.25635 | 0.16479 | -0.21515 | 122.4609 | -0.009155 | 122.6624 | 122.7402 | 0.013733 | 122.4426 | 0.032044 | 0.20142 | 122.5433 | 122.9141 | 122.8043 | 122.7814 | 122.6624 | 122.8226 | 122.8226 | 122.4426 | 122.7814 | 122.6624 | 122.8226 | 122.8043 | 122.8226 | -0.32959 | -0.3479
1677 | 122.8867 | -122.6486 | 0.18768 | -0.0067901 | 0.015407 | 9.8166e-05 | 0.046651 | -0.011916 | -0.010835 | 0.017534 | -0.027466 | 0.12817 | -0.2655 | 0.004578 | 0.009155 | 0.032043 | -0.004578 | 0.10071 | 0.21973 | -0.24261 | 122.3831 | -0.059509 | 122.6212 | 122.6532 | -0.17853 | 122.406 | 0.032044 | 0.23804 | 122.644 | 122.7493 | 122.6578 | 122.7768 | 122.6212 | 122.8683 | 122.6807 | 122.406 | 122.7768 | 122.6212 | 122.6807 | 122.6578 | 122.8683 | -0.45319 | -0.4303
1678.6875 | 122.9187 | -122.6624 | 0.17853 | -0.12886 | 0.016475 | 0.0054388 | 0.043447 | -0.01277 | -0.011049 | 0.017962 | -0.032043 | 0.15564 | -0.25635 | 0.022888 | 0.059509 | 0.07782 | 0.009155 | 0.16479 | 0.21057 | -0.21515 | 122.406 | -0.022888 | 122.6303 | 122.6852 | -0.11902 | 122.4472 | 0.032043 | 0.22431 | 122.6715 | 122.8271 | 122.7219 | 122.818 | 122.6303 | 122.8729 | 122.7402 | 122.4472 | 122.818 | 122.6303 | 122.7402 | 122.7219 | 122.8729 | -0.43488 | -0.39368
1680.375 | 122.9416 | -122.6395 | 0.15106 | -0.10597 | 0.01562 | 0.0018072 | 0.036184 | -0.01213 | -0.0074169 | 0.01668 | 0.013733 | 0.12817 | -0.2243 | 0.068665 | 0.1236 | 0.17853 | -0.12817 | 0.25635 | 0.16937 | -0.21057 | 122.4152 | -0.022888 | 122.6532 | 122.7081 | -0.027466 | 122.4289 | 0.018311 | 0.23804 | 122.5113 | 122.8958 | 122.7631 | 122.7676 | 122.6532 | 122.8088 | 122.818 | 122.4289 | 122.7676 | 122.6532 | 122.818 | 122.7631 | 122.8088 | -0.37537 | -0.36163
1682.0781 | 122.9187 | -122.6624 | 0.16479 | 0.15343 | 0.013911 | 0.0011664 | 0.039601 | -0.012984 | -0.0089123 | 0.016893 | 0.004578 | 0.12817 | -0.22888 | 0.022888 | 0.09613 | 0.13275 | -0.11444 | 0.20142 | 0.17853 | -0.20142 | 122.4335 | -0.036621 | 122.6669 | 122.6852 | -0.068665 | 122.4609 | 0.013733 | 0.23346 | 122.5479 | 122.8638 | 122.7585 | 122.7905 | 122.6669 | 122.8409 | 122.7951 | 122.4609 | 122.7905 | 122.6669 | 122.7951 | 122.7585 | 122.8409 | -0.39368 | -0.36621
1683.7969 | 122.8867 | -122.644 | 0.17395 | 0.10765 | 0.014766 | 0.0045844 | 0.044515 | -0.013198 | -0.0080579 | 0.017748 | -0.050354 | 0.14648 | -0.27466 | -0.013733 | 0 | 0.050354 | -0.064087 | 0.11902 | 0.19684 | -0.22888 | 122.3694 | -0.027466 | 122.5937 | 122.6303 | -0.17395 | 122.4152 | 0.022888 | 0.2243 | 122.58 | 122.7631 | 122.644 | 122.7905 | 122.5937 | 122.8409 | 122.6944 | 122.4152 | 122.7905 | 122.5937 | 122.6944 | 122.644 | 122.8409 | -0.44861 | -0.40283
1685.4844 | 123.0057 | -122.6166 | 0.13275 | -0.20515 | 0.016688 | 0.0071478 | 0.041097 | -0.014479 | -0.0080579 | 0.016253 | -0.054932 | 0.15564 | -0.24719 | -0.018311 | 0.018311 | 0.036621 | 0.050354 | 0.14191 | 0.21973 | -0.24719 | 122.3694 | 0.022889 | 122.5616 | 122.5983 | -0.11444 | 122.3694 | 0.086976 | 0.19226 | 122.6669 | 122.7585 | 122.6349 | 122.7722 | 122.5616 | 122.8363 | 122.6532 | 122.3694 | 122.7722 | 122.5616 | 122.6532 | 122.6349 | 122.8363 | -0.37994 | -0.37994
1687.1562 | 122.8867 | -122.6624 | 0.18768 | -0.022049 | 0.013484 | 0.0071478 | 0.047506 | -0.010634 | -0.01169 | 0.016466 | 0 | 0.14191 | -0.24719 | 0.013733 | 0.032043 | 0.059509 | -0.018311 | 0.1236 | 0.20599 | -0.2243 | 122.4152 | -0.045776 | 122.6624 | 122.6761 | -0.15564 | 122.438 | 0.018311 | 0.24719 | 122.644 | 122.7859 | 122.6944 | 122.8043 | 122.6624 | 122.8683 | 122.7219 | 122.438 | 122.8043 | 122.6624 | 122.7219 | 122.6944 | 122.8683 | -0.43488 | -0.41199
1688.8594 | 122.9599 | -122.6212 | 0.14191 | -0.098343 | 0.015407 | -0.00032903 | 0.035543 | -0.013198 | -0.0084851 | 0.018389 | 0.013733 | 0.10986 | -0.21515 | 0.068665 | 0.13275 | 0.16479 | -0.11902 | 0.25177 | 0.16022 | -0.20142 | 122.406 | -0.032044 | 122.6349 | 122.6898 | -0.009156 | 122.4197 | 0.01831 | 0.22888 | 122.5021 | 122.8729 | 122.7539 | 122.731 | 122.6349 | 122.7814 | 122.7859 | 122.4197 | 122.731 | 122.6349 | 122.7859 | 122.7539 | 122.7814 | -0.35706 | -0.34332
1690.5625 | 122.9004 | -122.6624 | 0.18768 | 0.061874 | 0.016902 | 0.0056524 | 0.047719 | -0.01213 | -0.012117 | 0.017534 | -0.045776 | 0.13733 | -0.2655 | -0.041199 | -0.022888 | 0.004578 | 0.032043 | 0.064087 | 0.21057 | -0.23804 | 122.3969 | -0.050354 | 122.6166 | 122.6212 | -0.21057 | 122.4243 | 0.022888 | 0.21973 | 122.6944 | 122.7264 | 122.6395 | 122.7997 | 122.6166 | 122.8729 | 122.6669 | 122.4243 | 122.7997 | 122.6166 | 122.6669 | 122.6395 | 122.8729 | -0.45319 | -0.42572
1692.25 | 122.9874 | -122.644 | 0.15564 | -0.25093 | 0.015407 | 0.003089 | 0.043233 | -0.01277 | -0.0086987 | 0.016253 | -0.082397 | 0.16479 | -0.26093 | -0.036621 | 0.013733 | 0.027466 | 0.068665 | 0.1236 | 0.21973 | -0.25635 | 122.3831 | 0.009155 | 122.5616 | 122.6074 | -0.14191 | 122.3877 | 0.064087 | 0.17853 | 122.7127 | 122.7676 | 122.6578 | 122.8088 | 122.5616 | 122.8638 | 122.6715 | 122.3877 | 122.8088 | 122.5616 | 122.6715 | 122.6578 | 122.8638 | -0.41657 | -0.41199
1693.9844 | 122.9279 | -122.6303 | 0.16479 | 0.13817 | 0.014338 | 0.0052252 | 0.042592 | -0.010421 | -0.0099805 | 0.016253 | -0.073242 | 0.16937 | -0.26093 | -0.059509 | -0.013733 | 0.022888 | 0.009155 | 0.082397 | 0.2243 | -0.23346 | 122.3694 | 0.004578 | 122.5571 | 122.5708 | -0.17853 | 122.3969 | 0.059509 | 0.18768 | 122.6395 | 122.7127 | 122.6166 | 122.7997 | 122.5571 | 122.8546 | 122.6532 | 122.3969 | 122.7997 | 122.5571 | 122.6532 | 122.6166 | 122.8546 | -0.42572 | -0.39825
1695.6719 | 123.0194 | -122.644 | 0.14191 | -0.1899 | 0.015193 | 0.00138 | 0.039174 | -0.014693 | -0.010621 | 0.01668 | -0.082397 | 0.14648 | -0.26093 | -0.036621 | 0.022888 | 0.032043 | 0.07782 | 0.1236 | 0.22888 | -0.25177 | 122.3831 | 0.004577 | 122.5616 | 122.6074 | -0.11902 | 122.3923 | 0.086975 | 0.17853 | 122.7219 | 122.7676 | 122.6669 | 122.7905 | 122.5616 | 122.8729 | 122.6761 | 122.3923 | 122.7905 | 122.5616 | 122.6761 | 122.6669 | 122.8729 | -0.40283 | -0.39368
1697.3594 | 122.9919 | -122.6074 | 0.15106 | 0.023727 | 0.014338 | 0.0035162 | 0.037038 | -0.013411 | -0.0076305 | 0.017107 | -0.027466 | 0.10529 | -0.21973 | 0.027466 | 0.068665 | 0.1236 | -0.091553 | 0.19226 | 0.21057 | -0.2243 | 122.3877 | -0.045776 | 122.58 | 122.6349 | -0.082397 | 122.3831 | 0.059509 | 0.19226 | 122.5159 | 122.7997 | 122.6761 | 122.7127 | 122.58 | 122.818 | 122.731 | 122.3831 | 122.7127 | 122.58 | 122.731 | 122.6761 | 122.818 | -0.37079 | -0.37537
1699.0312 | 122.8592 | -122.6624 | 0.19684 | -0.075455 | 0.015407 | 0.0022346 | 0.045583 | -0.014479 | -0.010408 | 0.017321 | 0 | 0.11902 | -0.25635 | 0.036621 | 0.059509 | 0.073242 | -0.018311 | 0.16937 | 0.19226 | -0.2243 | 122.406 | -0.077819 | 122.6624 | 122.699 | -0.13733 | 122.438 | -0.004577 | 0.25635 | 122.644 | 122.8317 | 122.7219 | 122.7814 | 122.6624 | 122.8546 | 122.7356 | 122.438 | 122.7814 | 122.6624 | 122.7356 | 122.7219 | 122.8546 | -0.45319 | -0.42114
1700.7344 | 122.8912 | -122.6395 | 0.16479 | 0.13054 | 0.016047 | 0.0037298 | 0.044728 | -0.012984 | -0.0099805 | 0.018602 | -0.050354 | 0.12817 | -0.27466 | -0.018311 | 0.009155 | 0.050354 | -0.068665 | 0.11444 | 0.21057 | -0.22888 | 122.3648 | -0.036621 | 122.5891 | 122.6212 | -0.15564 | 122.4106 | 0.045776 | 0.2243 | 122.5708 | 122.7539 | 122.6486 | 122.7676 | 122.5891 | 122.85 | 122.6898 | 122.4106 | 122.7676 | 122.5891 | 122.6898 | 122.6486 | 122.85 | -0.43945 | -0.39368
1702.4219 | 122.9279 | -122.6486 | 0.16022 | 0.092392 | 0.013484 | 0.0050116 | 0.040456 | -0.011275 | -0.0093395 | 0.016466 | 0.004578 | 0.10986 | -0.2243 | 0.027466 | 0.086975 | 0.11902 | -0.10529 | 0.18768 | 0.17853 | -0.20142 | 122.4243 | -0.050354 | 122.6532 | 122.6761 | -0.073242 | 122.4472 | 0.018311 | 0.22888 | 122.5433 | 122.8363 | 122.7356 | 122.7585 | 122.6532 | 122.8271 | 122.7676 | 122.4472 | 122.7585 | 122.6532 | 122.7676 | 122.7356 | 122.8271 | -0.38452 | -0.36163
1704.1094 | 122.9919 | -122.6303 | 0.13733 | -0.21278 | 0.016261 | 0.0033026 | 0.04366 | -0.013411 | -0.010621 | 0.01668 | -0.068665 | 0.15106 | -0.27466 | -0.022888 | -0.004578 | 0.027466 | 0.059509 | 0.11444 | 0.21973 | -0.23346 | 122.3557 | 0.013733 | 122.5616 | 122.6074 | -0.14191 | 122.3969 | 0.082398 | 0.20599 | 122.6898 | 122.7448 | 122.6257 | 122.7814 | 122.5616 | 122.85 | 122.6578 | 122.3969 | 122.7814 | 122.5616 | 122.6578 | 122.6257 | 122.85 | -0.41199 | -0.37079
1705.7969 | 122.9919 | -122.6349 | 0.14191 | 0.031357 | 0.014125 | -0.0011834 | 0.038106 | -0.013625 | -0.0057079 | 0.014971 | -0.013733 | 0.12817 | -0.22888 | 0.013733 | 0.082397 | 0.11902 | -0.086975 | 0.19684 | 0.19226 | -0.21057 | 122.406 | -0.013733 | 122.6212 | 122.6486 | -0.05951 | 122.4243 | 0.050354 | 0.21515 | 122.5479 | 122.8317 | 122.7173 | 122.7631 | 122.6212 | 122.8271 | 122.7539 | 122.4243 | 122.7631 | 122.6212 | 122.7539 | 122.7173 | 122.8271 | -0.37079 | -0.35248
1707.4844 | 122.8592 | -122.6852 | 0.20142 | -0.075455 | 0.016261 | 0.0024482 | 0.045797 | -0.011916 | -0.011262 | 0.017107 | -0.009155 | 0.15106 | -0.2655 | 0.027466 | 0.022888 | 0.064087 | -0.018311 | 0.14648 | 0.19226 | -0.24261 | 122.4197 | -0.050354 | 122.6761 | 122.7127 | -0.17853 | 122.4426 | -0.009155 | 0.25635 | 122.6669 | 122.8317 | 122.7081 | 122.8363 | 122.6761 | 122.8775 | 122.7493 | 122.4426 | 122.8363 | 122.6761 | 122.7493 | 122.7081 | 122.8775 | -0.46692 | -0.44403
1709.1562 | 122.8867 | -122.6624 | 0.17853 | 0.13817 | 0.012416 | 0.00031197 | 0.039174 | -0.012557 | -0.011049 | 0.018602 | 0.022888 | 0.12817 | -0.21973 | 0.045776 | 0.10529 | 0.14191 | -0.13733 | 0.2243 | 0.17395 | -0.21057 | 122.4426 | -0.050354 | 122.6852 | 122.7081 | -0.073242 | 122.4518 | -0.004578 | 0.24261 | 122.525 | 122.8867 | 122.7676 | 122.7905 | 122.6852 | 122.8363 | 122.8043 | 122.4518 | 122.7905 | 122.6852 | 122.8043 | 122.7676 | 122.8363 | -0.39826 | -0.3891
1710.8438 | 122.8638 | -122.6715 | 0.17853 | -0.060196 | 0.017329 | 0.0043708 | 0.047719 | -0.012984 | -0.010408 | 0.017107 | 0.009155 | 0.14191 | -0.24719 | 0.027466 | 0.036621 | 0.07782 | -0.032043 | 0.15564 | 0.18768 | -0.2243 | 122.4243 | -0.036621 | 122.6807 | 122.699 | -0.14191 | 122.4472 | 0.009155 | 0.25635 | 122.6395 | 122.8271 | 122.7081 | 122.8134 | 122.6807 | 122.8592 | 122.7493 | 122.4472 | 122.8134 | 122.6807 | 122.7493 | 122.7081 | 122.8592 | -0.42572 | -0.40283
1712.5312 | 122.9874 | -122.6486 | 0.16479 | -0.25856 | 0.014552 | 0.0056524 | 0.040029 | -0.012557 | -0.0084851 | 0.01668 | -0.018311 | 0.1236 | -0.23346 | 0.009155 | 0.054932 | 0.068665 | 0.009155 | 0.16937 | 0.19226 | -0.22888 | 122.4152 | -0.041199 | 122.6303 | 122.6578 | -0.10986 | 122.4197 | 0.027466 | 0.21515 | 122.6578 | 122.818 | 122.7036 | 122.7722 | 122.6303 | 122.8409 | 122.7173 | 122.4197 | 122.7722 | 122.6303 | 122.7173 | 122.7036 | 122.8409 | -0.39825 | -0.39368
1714.2188 | 122.8683 | -122.6303 | 0.17853 | 0.19157 | 0.014552 | 0.0018072 | 0.044088 | -0.0097796 | -0.0097669 | 0.015825 | 0.045776 | 0.11902 | -0.20599 | 0.086975 | 0.10986 | 0.15564 | -0.19226 | 0.21515 | 0.16937 | -0.19226 | 122.4243 | -0.059509 | 122.6761 | 122.7173 | -0.068665 | 122.438 | -0.009155 | 0.25177 | 122.438 | 122.8455 | 122.7402 | 122.7493 | 122.6761 | 122.7997 | 122.7859 | 122.438 | 122.7493 | 122.6761 | 122.7859 | 122.7402 | 122.7997 | -0.38452 | -0.37079
1715.9062 | 122.9645 | -122.6578 | 0.15564 | -0.19753 | 0.016902 | 9.8166e-05 | 0.043233 | -0.014266 | -0.0091259 | 0.015825 | -0.050354 | 0.16022 | -0.26093 | 0 | 0.032043 | 0.041199 | 0.041199 | 0.13733 | 0.19684 | -0.2243 | 122.3969 | 0.004577 | 122.6074 | 122.6578 | -0.1236 | 122.4335 | 0.041198 | 0.21057 | 122.699 | 122.7951 | 122.6898 | 122.818 | 122.6074 | 122.8546 | 122.699 | 122.4335 | 122.818 | 122.6074 | 122.699 | 122.6898 | 122.8546 | -0.41657 | -0.37994
1717.625 | 122.905 | -122.6624 | 0.15106 | 0.13817 | 0.013911 | 0.0069342 | 0.044088 | -0.011061 | -0.0074169 | 0.016893 | -0.07782 | 0.16022 | -0.26093 | -0.032043 | 0.004578 | 0.045776 | -0.013733 | 0.091553 | 0.18768 | -0.25635 | 122.4014 | 0.009155 | 122.5845 | 122.6303 | -0.14648 | 122.406 | 0.036621 | 0.18311 | 122.6486 | 122.7539 | 122.6669 | 122.8226 | 122.5845 | 122.85 | 122.7081 | 122.406 | 122.8226 | 122.5845 | 122.7081 | 122.6669 | 122.85 | -0.41199 | -0.40741
1719.3125 | 123.0057 | -122.6486 | 0.13733 | -0.044937 | 0.017543 | 0.0024482 | 0.036397 | -0.01213 | -0.0063489 | 0.017748 | -0.027466 | 0.13275 | -0.22888 | 0.018311 | 0.07782 | 0.1236 | -0.091553 | 0.21057 | 0.16937 | -0.22888 | 122.4197 | -0.004578 | 122.6212 | 122.6669 | -0.059509 | 122.4197 | 0.032044 | 0.20142 | 122.5571 | 122.8592 | 122.7264 | 122.7814 | 122.6212 | 122.818 | 122.7722 | 122.4197 | 122.7814 | 122.6212 | 122.7722 | 122.7264 | 122.818 | -0.36621 | -0.36621
1721.0312 | 122.8729 | -122.6715 | 0.19684 | -0.10597 | 0.01562 | 0.0043708 | 0.046437 | -0.011916 | -0.01233 | 0.017107 | 0.004578 | 0.15106 | -0.25177 | 0.036621 | 0.064087 | 0.07782 | -0.018311 | 0.16937 | 0.20599 | -0.21973 | 122.4197 | -0.045776 | 122.6761 | 122.7081 | -0.13275 | 122.4518 | 0.009156 | 0.25635 | 122.6532 | 122.8409 | 122.7356 | 122.8226 | 122.6761 | 122.8775 | 122.7493 | 122.4518 | 122.8226 | 122.6761 | 122.7493 | 122.7356 | 122.8775 | -0.44861 | -0.41657
1722.7188 | 122.8775 | -122.6852 | 0.16479 | 0.13054 | 0.015193 | 0.0056524 | 0.041524 | -0.01277 | -0.0097669 | 0.018389 | 0.036621 | 0.11444 | -0.20599 | 0.073242 | 0.11902 | 0.16022 | -0.16022 | 0.21057 | 0.16479 | -0.19684 | 122.4792 | -0.050354 | 122.7219 | 122.7585 | -0.045776 | 122.4884 | 0 | 0.24262 | 122.525 | 122.8958 | 122.8043 | 122.7997 | 122.7219 | 122.85 | 122.8455 | 122.4884 | 122.7997 | 122.7219 | 122.8455 | 122.8043 | 122.85 | -0.37079 | -0.36163
1724.4531 | 122.9645 | -122.644 | 0.14648 | -0.17464 | 0.015407 | 0.0028754 | 0.039815 | -0.014693 | -0.0074169 | 0.017107 | 0.013733 | 0.10986 | -0.21973 | 0.068665 | 0.11444 | 0.13733 | -0.073242 | 0.23804 | 0.1831 | -0.24261 | 122.4243 | -0.036621 | 122.6578 | 122.7127 | -0.032043 | 122.4014 | 0.036621 | 0.23346 | 122.5708 | 122.8821 | 122.7585 | 122.7539 | 122.6578 | 122.8271 | 122.7814 | 122.4014 | 122.7539 | 122.6578 | 122.7814 | 122.7585 | 122.8271 | -0.36621 | -0.3891
1726.1406 | 122.9782 | -122.6212 | 0.14191 | 0.046615 | 0.016688 | 0.0039436 | 0.038747 | -0.011916 | -0.0084851 | 0.016039 | -0.018311 | 0.12817 | -0.23804 | 0.032043 | 0.054932 | 0.11444 | -0.10529 | 0.19226 | 0.17395 | -0.20142 | 122.3831 | -0.013733 | 122.6028 | 122.6532 | -0.086975 | 122.4197 | 0.032043 | 0.21973 | 122.5159 | 122.8134 | 122.6761 | 122.7493 | 122.6028 | 122.7951 | 122.7356 | 122.4197 | 122.7493 | 122.6028 | 122.7356 | 122.6761 | 122.7951 | -0.37994 | -0.34332
1727.8438 | 122.9187 | -122.6624 | 0.16937 | 0.1458 | 0.01562 | 0.0062934 | 0.047292 | -0.012557 | -0.010621 | 0.015612 | -0.050354 | 0.16022 | -0.25177 | -0.027466 | -0.022888 | 0.009155 | 0.009155 | 0.07782 | 0.20142 | -0.2243 | 122.4106 | -0.009156 | 122.612 | 122.6349 | -0.19226 | 122.438 | 0.032043 | 0.20142 | 122.6715 | 122.7402 | 122.6395 | 122.8226 | 122.612 | 122.8638 | 122.6715 | 122.438 | 122.8226 | 122.612 | 122.6715 | 122.6395 | 122.8638 | -0.42114 | -0.39368
1729.5312 | 122.8638 | -122.7036 | 0.17853 | -0.090714 | 0.012629 | 0.006507 | 0.044088 | -0.011916 | -0.011903 | 0.018389 | 0 | 0.16937 | -0.25635 | 0.041199 | 0.045776 | 0.07782 | -0.022888 | 0.16937 | 0.20599 | -0.21973 | 122.4472 | -0.009155 | 122.7036 | 122.7448 | -0.13275 | 122.4838 | 0.027466 | 0.25635 | 122.6807 | 122.8729 | 122.7493 | 122.8729 | 122.7036 | 122.9095 | 122.7814 | 122.4838 | 122.8729 | 122.7036 | 122.7814 | 122.7493 | 122.9095 | -0.43488 | -0.39826
1731.2031 | 122.9691 | -122.6486 | 0.16479 | -0.19753 | 0.016261 | 0.0011664 | 0.039601 | -0.013625 | -0.0074169 | 0.01668 | 0.013733 | 0.1236 | -0.21973 | 0.07782 | 0.091553 | 0.1236 | -0.032043 | 0.2243 | 0.18768 | -0.22888 | 122.4289 | -0.041199 | 122.6624 | 122.7264 | -0.073242 | 122.4197 | 0.022888 | 0.23346 | 122.6166 | 122.8729 | 122.7402 | 122.7722 | 122.6624 | 122.8363 | 122.7722 | 122.4197 | 122.7722 | 122.6624 | 122.7722 | 122.7402 | 122.8363 | -0.38452 | -0.39368
1732.9375 | 123.0011 | -122.6166 | 0.13733 | 0.023727 | 0.014766 | 0.0045844 | 0.039601 | -0.014266 | -0.0082715 | 0.016039 | -0.018311 | 0.1236 | -0.23804 | 0.013733 | 0.068665 | 0.10986 | -0.086975 | 0.17853 | 0.18768 | -0.21973 | 122.3785 | -0.013733 | 122.5983 | 122.6303 | -0.068664 | 122.3969 | 0.050354 | 0.21973 | 122.5296 | 122.7951 | 122.6852 | 122.7402 | 122.5983 | 122.8043 | 122.7264 | 122.3969 | 122.7402 | 122.5983 | 122.7264 | 122.6852 | 122.8043 | -0.37537 | -0.35706
1734.625 | 122.9324 | -122.6761 | 0.16479 | 0.16106 | 0.01797 | 0.00052557 | 0.045583 | -0.009566 | -0.0074169 | 0.016253 | -0.050354 | 0.15564 | -0.27924 | -0.036621 | -0.004578 | 0.018311 | 0 | 0.10071 | 0.19226 | -0.25635 | 122.3969 | -0.009155 | 122.6257 | 122.6395 | -0.16937 | 122.4197 | 0.027466 | 0.22888 | 122.6761 | 122.7768 | 122.6715 | 122.8317 | 122.6257 | 122.8683 | 122.6944 | 122.4197 | 122.8317 | 122.6257 | 122.6944 | 122.6715 | 122.8683 | -0.44403 | -0.42114
1736.3281 | 122.8867 | -122.6807 | 0.17853 | 0.0084684 | 0.012416 | 0.0037298 | 0.04601 | -0.012984 | -0.0091259 | 0.017748 | -0.032043 | 0.16022 | -0.24719 | -0.004578 | 0.004578 | 0.027466 | 0.009155 | 0.11444 | 0.21515 | -0.2243 | 122.4335 | -0.018311 | 122.6486 | 122.6761 | -0.17395 | 122.4564 | 0.036621 | 0.21515 | 122.6898 | 122.7951 | 122.6852 | 122.8409 | 122.6486 | 122.8958 | 122.7081 | 122.4564 | 122.8409 | 122.6486 | 122.7081 | 122.6852 | 122.8958 | -0.42572 | -0.40283
1738.0469 | 122.9874 | -122.6349 | 0.15106 | -0.25856 | 0.01797 | 0.0041572 | 0.041097 | -0.013411 | -0.0093395 | 0.017107 | -0.068665 | 0.15564 | -0.27924 | -0.041199 | 0.009155 | 0.013733 | 0.064087 | 0.10986 | 0.21057 | -0.25177 | 122.3557 | 0.004578 | 122.5662 | 122.5937 | -0.14191 | 122.3831 | 0.059509 | 0.21057 | 122.699 | 122.7448 | 122.644 | 122.7905 | 122.5662 | 122.8455 | 122.6486 | 122.3831 | 122.7905 | 122.5662 | 122.6486 | 122.644 | 122.8455 | -0.4303 | -0.40283
1739.7188 | 122.8958 | -122.6761 | 0.17853 | 0.18394 | 0.015834 | 0.0050116 | 0.041524 | -0.011275 | -0.0095531 | 0.017962 | -0.041199 | 0.16479 | -0.24719 | 0 | 0.027466 | 0.064087 | -0.07782 | 0.11902 | 0.19226 | -0.21515 | 122.4289 | -0.013733 | 122.6349 | 122.6761 | -0.15106 | 122.4609 | 0.013733 | 0.20599 | 122.5983 | 122.7951 | 122.7036 | 122.8409 | 122.6349 | 122.8683 | 122.7402 | 122.4609 | 122.8409 | 122.6349 | 122.7402 | 122.7036 | 122.8683 | -0.42572 | -0.39368
1741.4062 | 122.8867 | -122.6944 | 0.18768 | -0.052567 | 0.014766 | 0.0039436 | 0.04366 | -0.01213 | -0.010194 | 0.015825 | -0.018311 | 0.14648 | -0.26093 | 0.009155 | 0.050354 | 0.050354 | -0.009155 | 0.13733 | 0.19684 | -0.2243 | 122.4335 | -0.041199 | 122.6761 | 122.7036 | -0.13733 | 122.4701 | 0.009155 | 0.24261 | 122.6852 | 122.8317 | 122.7448 | 122.8409 | 122.6761 | 122.8912 | 122.7448 | 122.4701 | 122.8409 | 122.6761 | 122.7448 | 122.7448 | 122.8912 | -0.44861 | -0.41199
1743.125 | 122.9233 | -122.6669 | 0.16479 | 0.11528 | 0.014552 | 0.0073614 | 0.04131 | -0.011702 | -0.0095531 | 0.017107 | -0.068665 | 0.14648 | -0.2655 | -0.041199 | 0 | 0.027466 | 0.018311 | 0.07782 | 0.21515 | -0.25635 | 122.4014 | -0.018311 | 122.5983 | 122.6257 | -0.16479 | 122.4106 | 0.050354 | 0.19684 | 122.6852 | 122.7448 | 122.6669 | 122.8134 | 122.5983 | 122.8821 | 122.6944 | 122.4106 | 122.8134 | 122.5983 | 122.6944 | 122.6669 | 122.8821 | -0.4303 | -0.42114
1744.8125 | 123.0148 | -122.6349 | 0.14648 | -0.2433 | 0.018397 | 0.0041572 | 0.043019 | -0.013198 | -0.0074169 | 0.01668 | -0.073242 | 0.17395 | -0.27008 | -0.041199 | 0.013733 | 0.027466 | 0.059509 | 0.11902 | 0.21973 | -0.24719 | 122.3648 | 0.027466 | 122.5616 | 122.5937 | -0.13275 | 122.3877 | 0.073243 | 0.19684 | 122.6944 | 122.7539 | 122.6486 | 122.8088 | 122.5616 | 122.8546 | 122.6624 | 122.3877 | 122.8088 | 122.5616 | 122.6624 | 122.6486 | 122.8546 | -0.41657 | -0.39368
1746.5 | 122.8867 | -122.6898 | 0.17395 | 0.13054 | 0.015407 | 0.0052252 | 0.039601 | -0.011275 | -0.0074169 | 0.017962 | 0.045776 | 0.10071 | -0.21515 | 0.054932 | 0.11444 | 0.16937 | -0.16479 | 0.23346 | 0.16479 | -0.20142 | 122.4747 | -0.073242 | 122.7356 | 122.7448 | -0.059509 | 122.4884 | -0.009155 | 0.26093 | 122.525 | 122.9233 | 122.8043 | 122.7905 | 122.7356 | 122.8546 | 122.8592 | 122.4884 | 122.7905 | 122.7356 | 122.8592 | 122.8043 | 122.8546 | -0.3891 | -0.37537
1748.2031 | 123.0057 | -122.6257 | 0.14648 | -0.2433 | 0.01562 | -0.0026788 | 0.042806 | -0.014907 | -0.0084851 | 0.015825 | -0.091553 | 0.16479 | -0.27008 | -0.050354 | 0.013733 | 0.009155 | 0.059509 | 0.10986 | 0.19684 | -0.25177 | 122.3557 | 0.018311 | 122.5342 | 122.5754 | -0.13275 | 122.374 | 0.050354 | 0.17853 | 122.6852 | 122.7356 | 122.6395 | 122.7905 | 122.5342 | 122.8226 | 122.6349 | 122.374 | 122.7905 | 122.5342 | 122.6349 | 122.6395 | 122.8226 | -0.41657 | -0.39825
1749.9375 | 122.9645 | -122.6669 | 0.15564 | -0.17464 | 0.013484 | 0.00052557 | 0.037892 | -0.012984 | -0.0091259 | 0.015184 | 0.059509 | 0.1236 | -0.22888 | 0.091553 | 0.12817 | 0.16937 | -0.11902 | 0.27008 | 0.17853 | -0.20142 | 122.438 | -0.032044 | 122.7264 | 122.7585 | -0.027466 | 122.4655 | 0.022888 | 0.28839 | 122.5479 | 122.937 | 122.7951 | 122.7905 | 122.7264 | 122.8455 | 122.8363 | 122.4655 | 122.7905 | 122.7264 | 122.8363 | 122.7951 | 122.8455 | -0.38452 | -0.35706
1751.625 | 123.0057 | -122.6212 | 0.14648 | 0.016098 | 0.014338 | -0.00075623 | 0.039388 | -0.01512 | -0.0086987 | 0.01967 | -0.013733 | 0.13275 | -0.21515 | 0.013733 | 0.064087 | 0.10529 | -0.082397 | 0.17853 | 0.19684 | -0.23346 | 122.406 | -0.013733 | 122.6074 | 122.6349 | -0.082397 | 122.3877 | 0.050354 | 0.20142 | 122.5388 | 122.7997 | 122.6852 | 122.7539 | 122.6074 | 122.818 | 122.7264 | 122.3877 | 122.7539 | 122.6074 | 122.7264 | 122.6852 | 122.818 | -0.36163 | -0.37994
1753.3281 | 122.8546 | -122.7036 | 0.16479 | 0.1992 | 0.016047 | 0.0018072 | 0.045797 | -0.013411 | -0.0080579 | 0.017534 | 0.013733 | 0.13275 | -0.24719 | 0.054932 | 0.082397 | 0.12817 | -0.14191 | 0.20599 | 0.15564 | -0.21973 | 122.4564 | -0.032044 | 122.7173 | 122.7585 | -0.082398 | 122.4838 | -0.009155 | 0.26093 | 122.5616 | 122.9095 | 122.7859 | 122.8363 | 122.7173 | 122.8592 | 122.8317 | 122.4838 | 122.8363 | 122.7173 | 122.8317 | 122.7859 | 122.8592 | -0.41199 | -0.38452
1755.0312 | 122.9919 | -122.6669 | 0.14648 | -0.25856 | 0.014552 | -0.00011543 | 0.039601 | -0.014266 | -0.0099805 | 0.015398 | 0.004578 | 0.1236 | -0.24261 | 0.050354 | 0.09613 | 0.10071 | -0.027466 | 0.21057 | 0.17853 | -0.20599 | 122.4243 | -0.022888 | 122.6715 | 122.7173 | -0.050354 | 122.4609 | 0.032044 | 0.24719 | 122.6395 | 122.8775 | 122.7631 | 122.7905 | 122.6715 | 122.8455 | 122.7676 | 122.4609 | 122.7905 | 122.6715 | 122.7676 | 122.7631 | 122.8455 | -0.3891 | -0.35248
1756.7188 | 122.9919 | -122.6212 | 0.15564 | 0.031357 | 0.017116 | 0.0018072 | 0.037465 | -0.011916 | -0.0095531 | 0.016466 | -0.009155 | 0.10986 | -0.23346 | 0.022888 | 0.064087 | 0.10071 | -0.091553 | 0.17853 | 0.1831 | -0.21515 | 122.3877 | -0.045777 | 122.612 | 122.644 | -0.091553 | 122.406 | 0.027465 | 0.2243 | 122.5296 | 122.7997 | 122.6852 | 122.731 | 122.612 | 122.8043 | 122.7219 | 122.406 | 122.731 | 122.612 | 122.7219 | 122.6852 | 122.8043 | -0.3891 | -0.37079
1758.4062 | 123.0286 | -122.644 | 0.16022 | -0.17464 | 0.014338 | 0.002021 | 0.042592 | -0.013625 | -0.010408 | 0.018602 | -0.059509 | 0.15564 | -0.2655 | -0.027466 | 0.018311 | 0.018311 | 0.07782 | 0.13733 | 0.23346 | -0.24261 | 122.3785 | -0.004577 | 122.5845 | 122.6166 | -0.14191 | 122.4014 | 0.073242 | 0.20599 | 122.7219 | 122.7814 | 122.6624 | 122.7997 | 122.5845 | 122.8775 | 122.6624 | 122.4014 | 122.7997 | 122.5845 | 122.6624 | 122.6624 | 122.8775 | -0.42572 | -0.40283
1760.1094 | 122.8775 | -122.6898 | 0.19226 | -0.083084 | 0.013698 | 0.0043708 | 0.045156 | -0.01213 | -0.0089123 | 0.017962 | -0.018311 | 0.14648 | -0.27008 | 0.036621 | 0.045776 | 0.07782 | -0.022888 | 0.17853 | 0.18768 | -0.25635 | 122.4197 | -0.045777 | 122.6715 | 122.7264 | -0.14648 | 122.4335 | -0.004578 | 0.25177 | 122.6669 | 122.8683 | 122.7356 | 122.8363 | 122.6715 | 122.8775 | 122.7676 | 122.4335 | 122.8363 | 122.6715 | 122.7676 | 122.7356 | 122.8775 | -0.46234 | -0.44861
1761.7969 | 123.0057 | -122.6532 | 0.14191 | -0.25093 | 0.017543 | 0.0011664 | 0.039388 | -0.012984 | -0.010621 | 0.017107 | -0.073242 | 0.16937 | -0.27924 | -0.041199 | 0.009155 | 0.018311 | 0.064087 | 0.11902 | 0.21515 | -0.25177 | 122.374 | 0.027466 | 122.58 | 122.612 | -0.13275 | 122.4014 | 0.073242 | 0.20599 | 122.7173 | 122.7722 | 122.6624 | 122.8226 | 122.58 | 122.8683 | 122.6715 | 122.4014 | 122.8226 | 122.58 | 122.6715 | 122.6624 | 122.8683 | -0.42114 | -0.39368
1763.4688 | 122.9736 | -122.6166 | 0.14191 | -0.044937 | 0.015407 | 0.0041572 | 0.036397 | -0.013839 | -0.0084851 | 0.016039 | 0.013733 | 0.11444 | -0.21057 | 0.064087 | 0.12817 | 0.14648 | -0.10529 | 0.22888 | 0.18768 | -0.21515 | 122.406 | -0.027466 | 122.6303 | 122.6807 | -0.013733 | 122.4014 | 0.045776 | 0.2243 | 122.5113 | 122.8455 | 122.7448 | 122.731 | 122.6303 | 122.8043 | 122.7631 | 122.4014 | 122.731 | 122.6303 | 122.7631 | 122.7448 | 122.8043 | -0.35248 | -0.35706
1765.1562 | 122.9507 | -122.6715 | 0.15106 | -0.21278 | 0.014766 | 0.00138 | 0.039388 | -0.013625 | -0.0076305 | 0.018389 | 0.036621 | 0.11902 | -0.21973 | 0.10071 | 0.13275 | 0.16937 | -0.1236 | 0.25635 | 0.16937 | -0.21973 | 122.4518 | -0.032043 | 122.7081 | 122.7722 | -0.018311 | 122.4518 | 0.018311 | 0.25635 | 122.5479 | 122.9279 | 122.8043 | 122.7905 | 122.7081 | 122.8409 | 122.8409 | 122.4518 | 122.7905 | 122.7081 | 122.8409 | 122.8043 | 122.8409 | -0.37079 | -0.37079
1766.8438 | 122.9919 | -122.6486 | 0.15564 | 0.084762 | 0.016047 | -0.00011543 | 0.039174 | -0.013625 | -0.0076305 | 0.017107 | -0.004578 | 0.11902 | -0.23804 | 0.032043 | 0.068665 | 0.10986 | -0.09613 | 0.19226 | 0.19226 | -0.20599 | 122.4106 | -0.036621 | 122.644 | 122.6807 | -0.086975 | 122.4426 | 0.036621 | 0.23346 | 122.5525 | 122.8409 | 122.7173 | 122.7676 | 122.644 | 122.8409 | 122.7585 | 122.4426 | 122.7676 | 122.644 | 122.7585 | 122.7173 | 122.8409 | -0.39368 | -0.36163
1768.5469 | 122.905 | -122.6715 | 0.15564 | 0.1458 | 0.014766 | 0.0022346 | 0.043233 | -0.014479 | -0.0097669 | 0.017321 | 0.018311 | 0.10986 | -0.22888 | 0.068665 | 0.09613 | 0.14191 | -0.11902 | 0.19226 | 0.16479 | -0.21515 | 122.4426 | -0.045777 | 122.6898 | 122.7402 | -0.05951 | 122.4564 | 0.009155 | 0.24719 | 122.5525 | 122.8638 | 122.7676 | 122.7814 | 122.6898 | 122.8363 | 122.8134 | 122.4564 | 122.7814 | 122.6898 | 122.8134 | 122.7676 | 122.8363 | -0.38452 | -0.37079
1770.2344 | 122.9965 | -122.6303 | 0.14648 | -0.15175 | 0.016475 | 0.006507 | 0.04601 | -0.012984 | -0.0097669 | 0.018175 | -0.068665 | 0.16479 | -0.27008 | 0.013733 | 0.004578 | 0.032043 | 0.064087 | 0.14648 | 0.21515 | -0.24261 | 122.3602 | 0.018311 | 122.5616 | 122.644 | -0.14191 | 122.3877 | 0.068665 | 0.20142 | 122.6944 | 122.7768 | 122.6349 | 122.7951 | 122.5616 | 122.8455 | 122.6624 | 122.3877 | 122.7951 | 122.5616 | 122.6624 | 122.6349 | 122.8455 | -0.41657 | -0.3891
1771.9375 | 122.9965 | -122.6349 | 0.14191 | 0.061874 | 0.015834 | -0.001397 | 0.035329 | -0.01213 | -0.0067761 | 0.016893 | -0.013733 | 0.13275 | -0.21973 | 0.027466 | 0.07782 | 0.09613 | -0.10071 | 0.1831 | 0.17395 | -0.21515 | 122.4152 | -0.009156 | 122.6212 | 122.6624 | -0.064087 | 122.4197 | 0.032043 | 0.20599 | 122.5342 | 122.818 | 122.7127 | 122.7676 | 122.6212 | 122.8088 | 122.731 | 122.4197 | 122.7676 | 122.6212 | 122.731 | 122.7127 | 122.8088 | -0.36163 | -0.35706
1773.625 | 122.8592 | -122.6578 | 0.16022 | 0.18394 | 0.016475 | 0.0026618 | 0.043874 | -0.010207 | -0.0095531 | 0.017748 | 0.068665 | 0.11444 | -0.21057 | 0.09613 | 0.10986 | 0.15106 | -0.1831 | 0.23804 | 0.17395 | -0.20142 | 122.4472 | -0.045776 | 122.7264 | 122.7539 | -0.050354 | 122.4564 | 0.013733 | 0.27924 | 122.4747 | 122.8958 | 122.7676 | 122.7722 | 122.7264 | 122.8317 | 122.8088 | 122.4564 | 122.7722 | 122.7264 | 122.8088 | 122.7676 | 122.8317 | -0.37079 | -0.36163
1775.3125 | 122.8729 | -122.6944 | 0.18768 | -0.075455 | 0.013911 | 0.0026618 | 0.04836 | -0.01277 | -0.010835 | 0.019243 | 0 | 0.14648 | -0.27466 | 0.041199 | 0.045776 | 0.073242 | -0.036621 | 0.16937 | 0.19684 | -0.21973 | 122.4197 | -0.041199 | 122.6944 | 122.7356 | -0.14191 | 122.4747 | 0.009155 | 0.27466 | 122.6578 | 122.8638 | 122.7402 | 122.8409 | 122.6944 | 122.8912 | 122.7676 | 122.4747 | 122.8409 | 122.6944 | 122.7676 | 122.7402 | 122.8912 | -0.46234 | -0.40741
1776.9844 | 122.905 | -122.6898 | 0.17395 | 0.16106 | 0.015834 | 0.0037298 | 0.039174 | -0.012343 | -0.0099805 | 0.017748 | 0.018311 | 0.11902 | -0.23804 | 0.050354 | 0.018311 | 0.11444 | -0.13275 | 0.19226 | 0.16937 | -0.20142 | 122.4518 | -0.054931 | 122.7081 | 122.7402 | -0.15564 | 122.4884 | -0.004577 | 0.25635 | 122.5571 | 122.8821 | 122.7081 | 122.8088 | 122.7081 | 122.8592 | 122.8043 | 122.4884 | 122.8088 | 122.7081 | 122.8043 | 122.7081 | 122.8592 | -0.41199 | -0.37537
1778.6719 | 122.8775 | -122.7127 | 0.17853 | -0.067826 | 0.013911 | 0.0033026 | 0.04601 | -0.013411 | -0.0097669 | 0.01433 | 0 | 0.13733 | -0.2655 | 0.036621 | 0.054932 | 0.068665 | -0.036621 | 0.16937 | 0.17853 | -0.2243 | 122.4472 | -0.041199 | 122.7127 | 122.7493 | -0.1236 | 122.4884 | 0 | 0.2655 | 122.6761 | 122.8821 | 122.7676 | 122.85 | 122.7127 | 122.8912 | 122.7814 | 122.4884 | 122.85 | 122.7127 | 122.7814 | 122.7676 | 122.8912 | -0.44403 | -0.40283
1780.3594 | 122.9828 | -122.644 | 0.11902 | -0.037308 | 0.017756 | 0.0028754 | 0.036611 | -0.016188 | -0.0082715 | 0.015398 | -0.022888 | 0.1236 | -0.2243 | 0.036621 | 0.10529 | 0.13275 | -0.091553 | 0.21057 | 0.1831 | -0.21973 | 122.4197 | 0.004577 | 122.6212 | 122.6807 | -0.013733 | 122.4243 | 0.064086 | 0.20142 | 122.5525 | 122.8546 | 122.7493 | 122.7676 | 122.6212 | 122.8271 | 122.7768 | 122.4243 | 122.7676 | 122.6212 | 122.7768 | 122.7493 | 122.8271 | -0.34332 | -0.33875
1782.0469 | 122.8821 | -122.6852 | 0.16479 | 0.16869 | 0.013057 | 0.0043708 | 0.042379 | -0.014266 | -0.0078443 | 0.016039 | 0.045776 | 0.10529 | -0.21973 | 0.073242 | 0.11902 | 0.16022 | -0.15564 | 0.22888 | 0.16022 | -0.19684 | 122.4655 | -0.059509 | 122.731 | 122.7585 | -0.045776 | 122.4884 | -0.004578 | 0.2655 | 122.5296 | 122.9141 | 122.8043 | 122.7905 | 122.731 | 122.8455 | 122.8455 | 122.4884 | 122.7905 | 122.731 | 122.8455 | 122.8043 | 122.8455 | -0.38452 | -0.36163
1783.7344 | 122.8638 | -122.699 | 0.19226 | 0.20683 | 0.014979 | -0.00075623 | 0.044088 | -0.011275 | -0.010408 | 0.015825 | 0.054932 | 0.10986 | -0.22888 | 0.09613 | 0.10986 | 0.17395 | -0.20142 | 0.21973 | 0.16479 | -0.19226 | 122.4701 | -0.082398 | 122.7539 | 122.7951 | -0.082398 | 122.5067 | -0.027466 | 0.28381 | 122.4976 | 122.9187 | 122.8088 | 122.8088 | 122.7539 | 122.8638 | 122.8729 | 122.5067 | 122.8088 | 122.7539 | 122.8729 | 122.8088 | 122.8638 | -0.42114 | -0.38452
1785.4375 | 123.0011 | -122.6578 | 0.14191 | -0.22041 | 0.016688 | 0.003089 | 0.043019 | -0.011489 | -0.010621 | 0.015612 | -0.068665 | 0.14648 | -0.26093 | -0.027466 | 0.013733 | 0.013733 | 0.064087 | 0.11444 | 0.2243 | -0.24719 | 122.3969 | 0.004577 | 122.5891 | 122.6303 | -0.12817 | 122.4106 | 0.082397 | 0.19226 | 122.7219 | 122.7722 | 122.6715 | 122.8043 | 122.5891 | 122.8821 | 122.6715 | 122.4106 | 122.8043 | 122.5891 | 122.6715 | 122.6715 | 122.8821 | -0.40283 | -0.3891
1787.1094 | 123.0011 | -122.644 | 0.15106 | -0.25856 | 0.01562 | 0.00031197 | 0.042806 | -0.0099934 | -0.010621 | 0.01668 | -0.086975 | 0.14191 | -0.2655 | -0.027466 | 0.004578 | 0.022888 | 0.064087 | 0.10529 | 0.20599 | -0.24719 | 122.3785 | -0.009155 | 122.5571 | 122.6166 | -0.14648 | 122.3969 | 0.054932 | 0.17853 | 122.7081 | 122.7493 | 122.6486 | 122.7859 | 122.5571 | 122.85 | 122.6669 | 122.3969 | 122.7859 | 122.5571 | 122.6669 | 122.6486 | 122.85 | -0.41656 | -0.39825
1788.7969 | 122.9645 | -122.6578 | 0.15106 | -0.10597 | 0.014979 | 0.0039436 | 0.038106 | -0.012984 | -0.0086987 | 0.016253 | 0.045776 | 0.13275 | -0.20599 | 0.091553 | 0.13733 | 0.17395 | -0.14648 | 0.27008 | 0.16937 | -0.20599 | 122.4518 | -0.018311 | 122.7036 | 122.7493 | -0.013733 | 122.4518 | 0.018311 | 0.25177 | 122.5113 | 122.9279 | 122.7951 | 122.7905 | 122.7036 | 122.8271 | 122.8317 | 122.4518 | 122.7905 | 122.7036 | 122.8317 | 122.7951 | 122.8271 | -0.35706 | -0.35706
1790.4844 | 122.9187 | -122.6715 | 0.16937 | 0.084762 | 0.014338 | 0.0056524 | 0.046224 | -0.0099934 | -0.011903 | 0.01668 | -0.068665 | 0.16022 | -0.26093 | -0.027466 | -0.013733 | 0.013733 | 0.004578 | 0.068665 | 0.20599 | -0.23804 | 122.4106 | -0.009156 | 122.6028 | 122.644 | -0.18311 | 122.4335 | 0.036621 | 0.19226 | 122.6761 | 122.7402 | 122.6578 | 122.8317 | 122.6028 | 122.8775 | 122.6852 | 122.4335 | 122.8317 | 122.6028 | 122.6852 | 122.6578 | 122.8775 | -0.4303 | -0.40741
1792.1875 | 122.9279 | -122.699 | 0.1831 | 0.11528 | 0.016047 | 0.0050116 | 0.046865 | -0.0099934 | -0.0097669 | 0.017962 | -0.086975 | 0.16479 | -0.27924 | -0.050354 | 0 | 0.004578 | 0.013733 | 0.068665 | 0.20142 | -0.24261 | 122.4197 | -0.01831 | 122.612 | 122.6486 | -0.1831 | 122.4564 | 0.018311 | 0.19226 | 122.7127 | 122.7676 | 122.699 | 122.8638 | 122.612 | 122.9004 | 122.7036 | 122.4564 | 122.8638 | 122.612 | 122.7036 | 122.699 | 122.9004 | -0.46234 | -0.42572
1793.875 | 122.9691 | -122.6532 | 0.13733 | -0.12886 | 0.01562 | 0.002021 | 0.036397 | -0.013198 | -0.0065625 | 0.015612 | 0.027466 | 0.1236 | -0.23346 | 0.07782 | 0.14191 | 0.17395 | -0.14191 | 0.27008 | 0.16937 | -0.21515 | 122.4197 | -0.013733 | 122.6807 | 122.731 | 0.004578 | 122.438 | 0.032044 | 0.26093 | 122.5113 | 122.9233 | 122.7951 | 122.7768 | 122.6807 | 122.8226 | 122.8271 | 122.438 | 122.7768 | 122.6807 | 122.8271 | 122.7951 | 122.8226 | -0.37079 | -0.35248
1795.5625 | 122.9233 | -122.699 | 0.16937 | 0.13817 | 0.017329 | 0.0022346 | 0.04601 | -0.010634 | -0.010621 | 0.01668 | -0.059509 | 0.16937 | -0.2655 | -0.027466 | 0 | 0.027466 | -0.009155 | 0.091553 | 0.20599 | -0.22888 | 122.4335 | 0 | 122.6395 | 122.6715 | -0.16937 | 122.4701 | 0.036621 | 0.20599 | 122.6898 | 122.7905 | 122.699 | 122.8683 | 122.6395 | 122.905 | 122.7264 | 122.4701 | 122.8683 | 122.6395 | 122.7264 | 122.699 | 122.905 | -0.43488 | -0.39826
1797.2812 | 122.9691 | -122.6532 | 0.16022 | -0.16701 | 0.015407 | 0.0022346 | 0.038747 | -0.013411 | -0.0078443 | 0.016253 | 0.045776 | 0.11444 | -0.21057 | 0.091553 | 0.15106 | 0.1831 | -0.14648 | 0.27924 | 0.16937 | -0.21057 | 122.4426 | -0.045776 | 122.699 | 122.7448 | -0.009155 | 122.4426 | 0.009156 | 0.25635 | 122.5067 | 122.9324 | 122.8043 | 122.7676 | 122.699 | 122.8226 | 122.8363 | 122.4426 | 122.7676 | 122.699 | 122.8363 | 122.8043 | 122.8226 | -0.37079 | -0.37079
1798.9688 | 122.9004 | -122.6715 | 0.16479 | 0.11528 | 0.014338 | -0.0011834 | 0.040029 | -0.014266 | -0.0091259 | 0.016466 | 0.032043 | 0.1236 | -0.2243 | 0.054932 | 0.11444 | 0.13275 | -0.15564 | 0.21057 | 0.14648 | -0.21057 | 122.4472 | -0.041199 | 122.7036 | 122.7264 | -0.050354 | 122.4609 | -0.018311 | 0.25635 | 122.5159 | 122.8821 | 122.7859 | 122.7951 | 122.7036 | 122.818 | 122.8043 | 122.4609 | 122.7951 | 122.7036 | 122.8043 | 122.7859 | 122.818 | -0.3891 | -0.37537
1800.6719 | 122.9965 | -122.644 | 0.16479 | -0.26619 | 0.013484 | 0.0054388 | 0.043874 | -0.014266 | -0.0095531 | 0.016466 | -0.032043 | 0.1236 | -0.24261 | 0.013733 | 0.041199 | 0.054932 | 0.022888 | 0.15564 | 0.21057 | -0.24719 | 122.4014 | -0.041199 | 122.612 | 122.6578 | -0.1236 | 122.3969 | 0.045776 | 0.21057 | 122.6669 | 122.7997 | 122.6852 | 122.7676 | 122.612 | 122.8546 | 122.699 | 122.3969 | 122.7676 | 122.612 | 122.699 | 122.6852 | 122.8546 | -0.40741 | -0.41199
1802.3906 | 122.9324 | -122.6761 | 0.16937 | 0.1458 | 0.014979 | -0.00096983 | 0.04601 | -0.013839 | -0.011903 | 0.01903 | -0.064087 | 0.14648 | -0.27466 | -0.041199 | -0.013733 | 0.027466 | 0 | 0.091553 | 0.21515 | -0.24261 | 122.4014 | -0.022889 | 122.612 | 122.6349 | -0.18311 | 122.4335 | 0.045776 | 0.21057 | 122.6761 | 122.7676 | 122.6624 | 122.8226 | 122.612 | 122.8912 | 122.7036 | 122.4335 | 122.8226 | 122.612 | 122.7036 | 122.6624 | 122.8912 | -0.44403 | -0.41199
1804.0938 | 122.9965 | -122.6669 | 0.15564 | -0.2433 | 0.012416 | 0.0033026 | 0.038961 | -0.014907 | -0.0093395 | 0.016466 | 0.009155 | 0.12817 | -0.22888 | 0.054932 | 0.082397 | 0.11444 | -0.032043 | 0.21973 | 0.17395 | -0.23804 | 122.438 | -0.027466 | 122.6761 | 122.7219 | -0.073243 | 122.4289 | 0.01831 | 0.23804 | 122.6349 | 122.8867 | 122.7493 | 122.7951 | 122.6761 | 122.8409 | 122.7814 | 122.4289 | 122.7951 | 122.6761 | 122.7814 | 122.7493 | 122.8409 | -0.38452 | -0.39368
1805.7812 | 122.9599 | -122.6532 | 0.14648 | 0.10765 | 0.015193 | 0.0018072 | 0.039815 | -0.012557 | -0.0063489 | 0.016466 | -0.004578 | 0.11902 | -0.21973 | 0.036621 | 0.07782 | 0.11444 | -0.11444 | 0.1831 | 0.1831 | -0.21057 | 122.4335 | -0.027465 | 122.6486 | 122.6898 | -0.068664 | 122.4426 | 0.036621 | 0.21515 | 122.5388 | 122.8363 | 122.731 | 122.7722 | 122.6486 | 122.8363 | 122.7676 | 122.4426 | 122.7722 | 122.6486 | 122.7676 | 122.731 | 122.8363 | -0.36621 | -0.35706
1807.5 | 122.9279 | -122.6578 | 0.1831 | 0.061874 | 0.014766 | -0.0024652 | 0.044942 | -0.012343 | -0.010194 | 0.017107 | -0.068665 | 0.15564 | -0.2655 | -0.036621 | -0.013733 | 0.018311 | 0.027466 | 0.082397 | 0.21057 | -0.24719 | 122.3923 | -0.027465 | 122.5891 | 122.6212 | -0.19684 | 122.4106 | 0.027466 | 0.19684 | 122.6852 | 122.7402 | 122.644 | 122.8134 | 122.5891 | 122.8683 | 122.6761 | 122.4106 | 122.8134 | 122.5891 | 122.6761 | 122.644 | 122.8683 | -0.44861 | -0.4303
1809.1875 | 123.0103 | -122.6486 | 0.13733 | -0.2433 | 0.014979 | 0.0024482 | 0.04366 | -0.01277 | -0.0086987 | 0.017321 | -0.073242 | 0.16479 | -0.31128 | -0.022888 | 0.004578 | 0.009155 | 0.054932 | 0.1236 | 0.21057 | -0.26093 | 122.3373 | 0.027466 | 122.5754 | 122.6257 | -0.13275 | 122.3877 | 0.073242 | 0.23804 | 122.7036 | 122.7722 | 122.6532 | 122.8134 | 122.5754 | 122.8592 | 122.6578 | 122.3877 | 122.8134 | 122.5754 | 122.6578 | 122.6532 | 122.8592 | -0.44861 | -0.39825
1810.9375 | 122.8912 | -122.6944 | 0.16937 | 0.1458 | 0.015407 | -0.0024652 | 0.039388 | -0.012343 | -0.010194 | 0.017748 | 0.036621 | 0.10986 | -0.22888 | 0.064087 | 0.11444 | 0.14648 | -0.15564 | 0.22888 | 0.17853 | -0.20142 | 122.4655 | -0.05951 | 122.731 | 122.7585 | -0.054932 | 122.493 | 0.009155 | 0.2655 | 122.5388 | 122.9233 | 122.8088 | 122.8043 | 122.731 | 122.8729 | 122.8409 | 122.493 | 122.8043 | 122.731 | 122.8409 | 122.8088 | 122.8729 | -0.39826 | -0.37079
1812.625 | 122.8958 | -122.7219 | 0.16937 | -0.067826 | 0.016261 | 0.004798 | 0.046865 | -0.01277 | -0.010621 | 0.014544 | 0.009155 | 0.13733 | -0.24719 | 0.045776 | 0.068665 | 0.086975 | -0.041199 | 0.16937 | 0.20142 | -0.24261 | 122.4747 | -0.032044 | 122.731 | 122.7676 | -0.10071 | 122.4792 | 0.032043 | 0.25635 | 122.6807 | 122.8912 | 122.7905 | 122.8592 | 122.731 | 122.9233 | 122.8088 | 122.4792 | 122.8592 | 122.731 | 122.8088 | 122.7905 | 122.9233 | -0.41656 | -0.41199
1814.3125 | 123.0286 | -122.6532 | 0.14648 | -0.19753 | 0.014979 | -0.003106 | 0.04131 | -0.01277 | -0.0099805 | 0.018389 | -0.073242 | 0.15106 | -0.25177 | -0.027466 | 0.022888 | 0.036621 | 0.082397 | 0.11902 | 0.21973 | -0.2655 | 122.4014 | 0.004578 | 122.58 | 122.6257 | -0.1236 | 122.3877 | 0.073243 | 0.17853 | 122.7356 | 122.7722 | 122.6761 | 122.8043 | 122.58 | 122.8729 | 122.6898 | 122.3877 | 122.8043 | 122.58 | 122.6898 | 122.6761 | 122.8729 | -0.39825 | -0.41199
1816 | 123.0057 | -122.6578 | 0.13733 | -0.037308 | 0.014552 | 0.002021 | 0.038961 | -0.01277 | -0.0080579 | 0.012835 | -0.009155 | 0.11444 | -0.2243 | 0.032043 | 0.10071 | 0.13733 | -0.091553 | 0.2243 | 0.16937 | -0.21515 | 122.4335 | -0.022888 | 122.6486 | 122.6898 | -0.036621 | 122.4426 | 0.032044 | 0.21515 | 122.5662 | 122.8821 | 122.7585 | 122.7722 | 122.6486 | 122.8271 | 122.7951 | 122.4426 | 122.7722 | 122.6486 | 122.7951 | 122.7585 | 122.8271 | -0.36163 | -0.35248
1817.7188 | 122.9736 | -122.644 | 0.16479 | -0.17464 | 0.015834 | 0.0026618 | 0.040029 | -0.013411 | -0.0093395 | 0.015612 | 0.045776 | 0.09613 | -0.23804 | 0.09613 | 0.13733 | 0.16022 | -0.10529 | 0.27008 | 0.16937 | -0.20599 | 122.406 | -0.068665 | 122.6898 | 122.7402 | -0.027466 | 122.438 | 0.004578 | 0.28381 | 122.5388 | 122.9141 | 122.7814 | 122.7402 | 122.6898 | 122.8134 | 122.8043 | 122.438 | 122.7402 | 122.6898 | 122.8043 | 122.7814 | 122.8134 | -0.40283 | -0.37079
1819.4375 | 123.0011 | -122.6395 | 0.13275 | 0.023727 | 0.013911 | 0.0035162 | 0.039815 | -0.013411 | -0.0084851 | 0.015184 | -0.022888 | 0.13733 | -0.23346 | 0.041199 | 0.068665 | 0.09613 | -0.091553 | 0.18768 | 0.18768 | -0.23804 | 122.406 | 0.004578 | 122.6166 | 122.6807 | -0.064086 | 122.4014 | 0.054932 | 0.21057 | 122.5479 | 122.8271 | 122.7081 | 122.7768 | 122.6166 | 122.8271 | 122.7356 | 122.4014 | 122.7768 | 122.6166 | 122.7356 | 122.7081 | 122.8271 | -0.36621 | -0.37079
1821.1406 | 122.9965 | -122.6486 | 0.16479 | -0.2433 | 0.013698 | -0.00032903 | 0.044515 | -0.013625 | -0.010621 | 0.015612 | 0.018311 | 0.09613 | -0.24719 | 0.073242 | 0.073242 | 0.10071 | -0.041199 | 0.2243 | 0.19684 | -0.21973 | 122.4014 | -0.068665 | 122.6669 | 122.7219 | -0.091553 | 122.4289 | 0.032043 | 0.2655 | 122.6074 | 122.8729 | 122.7219 | 122.7448 | 122.6669 | 122.8455 | 122.7493 | 122.4289 | 122.7448 | 122.6669 | 122.7493 | 122.7219 | 122.8455 | -0.41199 | -0.38452
1822.8281 | 122.9782 | -122.6669 | 0.15106 | -0.067826 | 0.014338 | -0.001397 | 0.040456 | -0.013839 | -0.0082715 | 0.013903 | 0.022888 | 0.10071 | -0.24719 | 0.091553 | 0.1236 | 0.14648 | -0.12817 | 0.27008 | 0.17395 | -0.21057 | 122.4197 | -0.050354 | 122.6898 | 122.7585 | -0.027466 | 122.4564 | 0.022888 | 0.27008 | 122.5388 | 122.937 | 122.7905 | 122.7676 | 122.6898 | 122.8409 | 122.8134 | 122.4564 | 122.7676 | 122.6898 | 122.8134 | 122.7905 | 122.8409 | -0.39825 | -0.36163
1824.5156 | 122.9187 | -122.6715 | 0.16022 | 0.084762 | 0.016047 | 0.0022346 | 0.048146 | -0.011275 | -0.013826 | 0.015825 | -0.036621 | 0.16479 | -0.26093 | -0.018311 | -0.009155 | 0.032043 | -0.036621 | 0.09613 | 0.2243 | -0.22888 | 122.4106 | 0.004578 | 122.6349 | 122.6532 | -0.16937 | 122.4426 | 0.064087 | 0.2243 | 122.6349 | 122.7676 | 122.6624 | 122.8363 | 122.6349 | 122.8958 | 122.7036 | 122.4426 | 122.8363 | 122.6349 | 122.7036 | 122.6624 | 122.8958 | -0.42114 | -0.3891
1826.2188 | 123.0148 | -122.6212 | 0.16022 | 0.023727 | 0.016688 | 0.00073917 | 0.039174 | -0.014907 | -0.0072033 | 0.017321 | -0.013733 | 0.13275 | -0.23346 | 0.027466 | 0.064087 | 0.091553 | -0.086975 | 0.17395 | 0.19226 | -0.22888 | 122.3877 | -0.027466 | 122.6074 | 122.6486 | -0.09613 | 122.3923 | 0.032044 | 0.21973 | 122.5342 | 122.7951 | 122.6852 | 122.7539 | 122.6074 | 122.8134 | 122.7127 | 122.3923 | 122.7539 | 122.6074 | 122.7127 | 122.6852 | 122.8134 | -0.39368 | -0.3891
1827.9688 | 123.0103 | -122.6486 | 0.15564 | 0.031357 | 0.013911 | 0.002021 | 0.042165 | -0.014479 | -0.0089123 | 0.016893 | -0.009155 | 0.11902 | -0.2243 | 0.022888 | 0.064087 | 0.10529 | -0.10071 | 0.18768 | 0.17395 | -0.23804 | 122.4243 | -0.036621 | 122.6395 | 122.6715 | -0.091553 | 122.4106 | 0.01831 | 0.21515 | 122.5479 | 122.8363 | 122.7127 | 122.7676 | 122.6395 | 122.8226 | 122.7539 | 122.4106 | 122.7676 | 122.6395 | 122.7539 | 122.7127 | 122.8226 | -0.37994 | -0.39368
1829.6562 | 122.9004 | -122.699 | 0.18768 | 0.16869 | 0.015407 | 0.0039436 | 0.044515 | -0.014479 | -0.010835 | 0.016466 | -0.041199 | 0.16022 | -0.2655 | 0.018311 | 0.027466 | 0.064087 | -0.091553 | 0.13275 | 0.18768 | -0.22888 | 122.4335 | -0.027466 | 122.6578 | 122.7173 | -0.16022 | 122.4701 | 0 | 0.2243 | 122.6074 | 122.8317 | 122.7264 | 122.8592 | 122.6578 | 122.8867 | 122.7631 | 122.4701 | 122.8592 | 122.6578 | 122.7631 | 122.7264 | 122.8867 | -0.45319 | -0.41656
1831.3594 | 123.0011 | -122.6624 | 0.15106 | -0.1899 | 0.013484 | -0.002038 | 0.04366 | -0.015334 | -0.010194 | 0.017107 | -0.073242 | 0.16937 | -0.30212 | -0.013733 | 0.009155 | 0.013733 | 0.054932 | 0.13275 | 0.20599 | -0.24719 | 122.3602 | 0.018311 | 122.5891 | 122.6486 | -0.14191 | 122.4152 | 0.054932 | 0.22888 | 122.7173 | 122.7951 | 122.6715 | 122.8317 | 122.5891 | 122.8683 | 122.6761 | 122.4152 | 122.8317 | 122.5891 | 122.6761 | 122.6715 | 122.8683 | -0.45319 | -0.39825
1833.0469 | 122.9736 | -122.6715 | 0.14648 | -0.17464 | 0.014979 | 0.00138 | 0.037892 | -0.012984 | -0.0080579 | 0.01433 | 0.041199 | 0.10529 | -0.20599 | 0.09613 | 0.15564 | 0.15564 | -0.1236 | 0.27924 | 0.16937 | -0.21973 | 122.4655 | -0.041198 | 122.7127 | 122.7676 | 0.009156 | 122.4518 | 0.022889 | 0.24719 | 122.5479 | 122.9507 | 122.8271 | 122.7768 | 122.7127 | 122.8409 | 122.8271 | 122.4518 | 122.7768 | 122.7127 | 122.8271 | 122.8271 | 122.8409 | -0.35248 | -0.36621
1834.7188 | 122.8912 | -122.6898 | 0.17395 | 0.24498 | 0.016047 | -0.00032903 | 0.045369 | -0.013625 | -0.010835 | 0.015825 | -0.009155 | 0.12817 | -0.25177 | 0.041199 | 0.068665 | 0.10071 | -0.1236 | 0.1831 | 0.18768 | -0.21973 | 122.438 | -0.045776 | 122.6807 | 122.731 | -0.10528 | 122.4701 | 0.013733 | 0.24261 | 122.5662 | 122.8729 | 122.7585 | 122.818 | 122.6807 | 122.8775 | 122.7905 | 122.4701 | 122.818 | 122.6807 | 122.7905 | 122.7585 | 122.8775 | -0.42572 | -0.39368
1836.4219 | 122.8821 | -122.699 | 0.18768 | 0.19157 | 0.016475 | 0.0050116 | 0.042592 | -0.01277 | -0.0084851 | 0.016466 | 0.045776 | 0.10529 | -0.21057 | 0.086975 | 0.11444 | 0.14191 | -0.16937 | 0.22888 | 0.16479 | -0.1831 | 122.4884 | -0.082397 | 122.7448 | 122.7859 | -0.073242 | 122.5159 | -0.022888 | 0.25635 | 122.5296 | 122.9279 | 122.8134 | 122.8043 | 122.7448 | 122.8638 | 122.8409 | 122.5159 | 122.8043 | 122.7448 | 122.8409 | 122.8134 | 122.8638 | -0.39825 | -0.37079
1838.1406 | 122.9095 | -122.6761 | 0.16479 | -0.14412 | 0.016688 | -0.0018244 | 0.044942 | -0.011916 | -0.0099805 | 0.01668 | -0.004578 | 0.13275 | -0.28381 | 0.041199 | 0.068665 | 0.059509 | -0.018311 | 0.16022 | 0.20142 | -0.23804 | 122.3923 | -0.032044 | 122.6715 | 122.7173 | -0.09613 | 122.438 | 0.036621 | 0.27923 | 122.6578 | 122.8363 | 122.7448 | 122.8088 | 122.6715 | 122.8775 | 122.7356 | 122.438 | 122.8088 | 122.6715 | 122.7356 | 122.7448 | 122.8775 | -0.44861 | -0.40283
1839.8281 | 122.9691 | -122.6852 | 0.14191 | -0.1899 | 0.014552 | 0.0022346 | 0.037038 | -0.014266 | -0.0093395 | 0.017748 | 0.041199 | 0.10986 | -0.21973 | 0.09613 | 0.13275 | 0.15564 | -0.10529 | 0.28381 | 0.16937 | -0.21057 | 122.4655 | -0.032044 | 122.7264 | 122.7814 | -0.009156 | 122.4747 | 0.027466 | 0.26093 | 122.58 | 122.9691 | 122.818 | 122.7951 | 122.7264 | 122.8546 | 122.8409 | 122.4747 | 122.7951 | 122.7264 | 122.8409 | 122.818 | 122.8546 | -0.36163 | -0.35248
1841.5312 | 122.9691 | -122.6578 | 0.15564 | -0.12886 | 0.016475 | 0.0026618 | 0.038106 | -0.013625 | -0.010194 | 0.016253 | 0.032043 | 0.1236 | -0.22888 | 0.09613 | 0.12817 | 0.16479 | -0.13275 | 0.27008 | 0.17395 | -0.21973 | 122.4289 | -0.032044 | 122.6898 | 122.7539 | -0.027466 | 122.438 | 0.01831 | 0.26093 | 122.525 | 122.9279 | 122.7859 | 122.7814 | 122.6898 | 122.8317 | 122.8226 | 122.438 | 122.7814 | 122.6898 | 122.8226 | 122.7859 | 122.8317 | -0.38452 | -0.37537
1843.2188 | 122.905 | -122.6898 | 0.18768 | 0.1992 | 0.014979 | 0.0069342 | 0.047506 | -0.013839 | -0.01233 | 0.015825 | 0.009155 | 0.11444 | -0.23804 | 0.068665 | 0.10529 | 0.1236 | -0.15106 | 0.21057 | 0.17853 | -0.20599 | 122.4518 | -0.073242 | 122.699 | 122.7585 | -0.082397 | 122.4838 | -0.009155 | 0.24719 | 122.5388 | 122.9004 | 122.7951 | 122.8043 | 122.699 | 122.8683 | 122.8134 | 122.4838 | 122.8043 | 122.699 | 122.8134 | 122.7951 | 122.8683 | -0.42572 | -0.39368
1844.9531 | 123.0148 | -122.6395 | 0.14191 | -0.029679 | 0.015834 | 0.0060798 | 0.038533 | -0.013411 | -0.0078443 | 0.017748 | -0.013733 | 0.13275 | -0.23346 | 0.032043 | 0.086975 | 0.13275 | -0.10529 | 0.19684 | 0.16937 | -0.21973 | 122.406 | -0.009156 | 122.6257 | 122.6715 | -0.054932 | 122.4197 | 0.027466 | 0.21973 | 122.5342 | 122.8363 | 122.7264 | 122.7722 | 122.6257 | 122.8088 | 122.7722 | 122.4197 | 122.7722 | 122.6257 | 122.7722 | 122.7264 | 122.8088 | -0.37537 | -0.36163
1846.6406 | 122.937 | -122.6852 | 0.17853 | 0.17632 | 0.013911 | 0.0028754 | 0.045369 | -0.013198 | -0.010194 | 0.017534 | -0.073242 | 0.17853 | -0.27466 | -0.027466 | -0.009155 | 0.013733 | 0 | 0.073242 | 0.21973 | -0.25177 | 122.4106 | 0 | 122.612 | 122.6578 | -0.18768 | 122.4335 | 0.041199 | 0.20142 | 122.6852 | 122.7585 | 122.6761 | 122.8638 | 122.612 | 122.905 | 122.699 | 122.4335 | 122.8638 | 122.612 | 122.699 | 122.6761 | 122.905 | -0.45319 | -0.4303
1848.3125 | 123.056 | -122.6486 | 0.15564 | -0.17464 | 0.017543 | -0.00075623 | 0.041951 | -0.013839 | -0.0084851 | 0.013689 | -0.07782 | 0.16022 | -0.28381 | -0.018311 | 0.032043 | 0.022888 | 0.064087 | 0.11444 | 0.21057 | -0.25177 | 122.3648 | 0.004577 | 122.5708 | 122.6303 | -0.1236 | 122.3969 | 0.054931 | 0.20599 | 122.7127 | 122.7631 | 122.6807 | 122.8088 | 122.5708 | 122.8592 | 122.6715 | 122.3969 | 122.8088 | 122.5708 | 122.6715 | 122.6807 | 122.8592 | -0.43945 | -0.40741
1850.0469 | 123.024 | -122.6578 | 0.13733 | 0.0084684 | 0.016261 | 0.003089 | 0.039388 | -0.01277 | -0.0080579 | 0.016039 | -0.032043 | 0.12817 | -0.24261 | 0.022888 | 0.086975 | 0.10986 | -0.09613 | 0.19226 | 0.17395 | -0.22888 | 122.4152 | -0.009155 | 122.6257 | 122.6807 | -0.050354 | 122.4289 | 0.036621 | 0.21057 | 122.5616 | 122.85 | 122.7448 | 122.7859 | 122.6257 | 122.8317 | 122.7676 | 122.4289 | 122.7859 | 122.6257 | 122.7676 | 122.7448 | 122.8317 | -0.37994 | -0.36621
1851.7344 | 122.8912 | -122.699 | 0.18768 | 0.16106 | 0.015834 | 0.009925 | 0.045156 | -0.014693 | -0.0082715 | 0.019457 | 0.032043 | 0.12817 | -0.23346 | 0.064087 | 0.10071 | 0.14648 | -0.17395 | 0.20142 | 0.17395 | -0.21973 | 122.4655 | -0.059509 | 122.731 | 122.7631 | -0.086975 | 122.4792 | -0.013733 | 0.2655 | 122.525 | 122.9004 | 122.7997 | 122.8271 | 122.731 | 122.8729 | 122.8455 | 122.4792 | 122.8271 | 122.731 | 122.8455 | 122.7997 | 122.8729 | -0.42114 | -0.40741
1853.4219 | 122.937 | -122.6852 | 0.15106 | 0.12291 | 0.015834 | -0.0043878 | 0.046651 | -0.012984 | -0.0095531 | 0.017107 | -0.064087 | 0.15564 | -0.28381 | -0.032043 | 0.013733 | 0.032043 | -0.022888 | 0.091553 | 0.20599 | -0.22888 | 122.4014 | 0.004578 | 122.6212 | 122.6532 | -0.13733 | 122.4564 | 0.054932 | 0.21973 | 122.6624 | 122.7768 | 122.699 | 122.8409 | 122.6212 | 122.8912 | 122.7173 | 122.4564 | 122.8409 | 122.6212 | 122.7173 | 122.699 | 122.8912 | -0.43488 | -0.37994
1855.1094 | 122.9965 | -122.6669 | 0.16479 | -0.21278 | 0.015193 | 0.003089 | 0.038747 | -0.014052 | -0.0080579 | 0.016893 | 0 | 0.1236 | -0.22888 | 0.07782 | 0.11444 | 0.13275 | -0.064087 | 0.23346 | 0.17395 | -0.21973 | 122.438 | -0.041199 | 122.6669 | 122.7448 | -0.050354 | 122.4472 | 0.009155 | 0.22888 | 122.6028 | 122.9004 | 122.7814 | 122.7905 | 122.6669 | 122.8409 | 122.7997 | 122.4472 | 122.7905 | 122.6669 | 122.7997 | 122.7814 | 122.8409 | -0.39368 | -0.38452
1856.8281 | 123.0011 | -122.6532 | 0.15106 | -0.022049 | 0.016261 | -0.0026788 | 0.038747 | -0.014052 | -0.0078443 | 0.015825 | -0.009155 | 0.14191 | -0.23804 | 0.054932 | 0.11444 | 0.14191 | -0.11902 | 0.23346 | 0.16479 | -0.21973 | 122.4152 | -0.009155 | 122.644 | 122.7081 | -0.036621 | 122.4335 | 0.013733 | 0.22888 | 122.5342 | 122.8867 | 122.7676 | 122.7951 | 122.644 | 122.818 | 122.7951 | 122.4335 | 122.7951 | 122.644 | 122.7951 | 122.7676 | 122.818 | -0.3891 | -0.37079
1858.5 | 122.905 | -122.6669 | 0.1831 | -0.0067901 | 0.013057 | 0.0018072 | 0.047292 | -0.011916 | -0.012758 | 0.017534 | -0.009155 | 0.13275 | -0.27008 | 0.022888 | 0.018311 | 0.041199 | -0.009155 | 0.10986 | 0.20599 | -0.23346 | 122.3969 | -0.050354 | 122.6578 | 122.6898 | -0.16479 | 122.4335 | 0.022889 | 0.26093 | 122.6578 | 122.7768 | 122.6852 | 122.7997 | 122.6578 | 122.8729 | 122.7081 | 122.4335 | 122.7997 | 122.6578 | 122.7081 | 122.6852 | 122.8729 | -0.45319 | -0.41656
1860.2188 | 123.0148 | -122.6944 | 0.15564 | -0.2433 | 0.015407 | 0.00095277 | 0.039174 | -0.014907 | -0.011262 | 0.016039 | -0.004578 | 0.13275 | -0.24261 | 0.027466 | 0.086975 | 0.082397 | -0.009155 | 0.18768 | 0.19684 | -0.23346 | 122.4518 | -0.022889 | 122.6898 | 122.7219 | -0.068665 | 122.4609 | 0.041198 | 0.23804 | 122.6852 | 122.8821 | 122.7814 | 122.8271 | 122.6898 | 122.8912 | 122.7768 | 122.4609 | 122.8271 | 122.6898 | 122.7768 | 122.7814 | 122.8912 | -0.39826 | -0.3891
1861.9062 | 123.0148 | -122.6715 | 0.15106 | -0.01442 | 0.014338 | 0.0033026 | 0.040242 | -0.01512 | -0.0074169 | 0.014971 | -0.018311 | 0.1236 | -0.24261 | 0.045776 | 0.091553 | 0.1236 | -0.10071 | 0.21515 | 0.17395 | -0.20599 | 122.4289 | -0.027466 | 122.6532 | 122.7173 | -0.059509 | 122.4655 | 0.022888 | 0.2243 | 122.5708 | 122.8867 | 122.7631 | 122.7951 | 122.6532 | 122.8455 | 122.7951 | 122.4655 | 122.7951 | 122.6532 | 122.7951 | 122.7631 | 122.8455 | -0.39368 | -0.35706
1863.6094 | 122.905 | -122.7173 | 0.19684 | -0.083084 | 0.014338 | 0.0094978 | 0.046224 | -0.014479 | -0.0084851 | 0.015612 | -0.009155 | 0.14648 | -0.2655 | 0.022888 | 0.036621 | 0.064087 | -0.009155 | 0.14648 | 0.21973 | -0.24261 | 122.4518 | -0.050354 | 122.7081 | 122.7402 | -0.16022 | 122.4747 | 0.022889 | 0.25635 | 122.7081 | 122.8638 | 122.7539 | 122.8638 | 122.7081 | 122.937 | 122.7814 | 122.4747 | 122.8638 | 122.7081 | 122.7814 | 122.7539 | 122.937 | -0.46234 | -0.43945
1865.3281 | 122.9004 | -122.7036 | 0.17395 | -0.075455 | 0.014125 | 0.0018072 | 0.046865 | -0.011702 | -0.011262 | 0.016466 | 0.004578 | 0.16479 | -0.27466 | 0.032043 | 0.050354 | 0.073242 | -0.036621 | 0.16937 | 0.19226 | -0.2243 | 122.4289 | -0.009155 | 122.7081 | 122.7356 | -0.1236 | 122.4792 | 0.018311 | 0.27924 | 122.6669 | 122.8729 | 122.7539 | 122.8683 | 122.7081 | 122.8958 | 122.7768 | 122.4792 | 122.8683 | 122.7081 | 122.7768 | 122.7539 | 122.8958 | -0.44861 | -0.39825
1867.0156 | 123.0194 | -122.6624 | 0.14648 | 0.031357 | 0.015834 | 0.00073917 | 0.035329 | -0.012984 | -0.0093395 | 0.017748 | -0.027466 | 0.12817 | -0.23346 | 0.027466 | 0.07782 | 0.10529 | -0.086975 | 0.19226 | 0.17395 | -0.2243 | 122.4289 | -0.01831 | 122.6349 | 122.6898 | -0.068664 | 122.438 | 0.027466 | 0.20599 | 122.5754 | 122.8546 | 122.7402 | 122.7905 | 122.6349 | 122.8363 | 122.7676 | 122.438 | 122.7905 | 122.6349 | 122.7676 | 122.7402 | 122.8363 | -0.37994 | -0.37079
1868.7344 | 122.9736 | -122.6715 | 0.16022 | -0.12886 | 0.014979 | 0.00031197 | 0.040456 | -0.016402 | -0.0078443 | 0.01433 | 0.036621 | 0.12817 | -0.21515 | 0.10071 | 0.15564 | 0.16479 | -0.14648 | 0.29755 | 0.16022 | -0.21515 | 122.4564 | -0.032043 | 122.7081 | 122.7722 | -0.004577 | 122.4564 | 0 | 0.25177 | 122.525 | 122.9691 | 122.8271 | 122.7997 | 122.7081 | 122.8317 | 122.8363 | 122.4564 | 122.7997 | 122.7081 | 122.8363 | 122.8271 | 122.8317 | -0.37537 | -0.37537
1870.4531 | 123.0103 | -122.6257 | 0.15564 | -0.0067901 | 0.015834 | -0.0018244 | 0.040883 | -0.014907 | -0.0084851 | 0.017748 | -0.045776 | 0.12817 | -0.24719 | 0.041199 | 0.07782 | 0.10986 | -0.086975 | 0.19684 | 0.1831 | -0.2243 | 122.3785 | -0.027466 | 122.58 | 122.6669 | -0.07782 | 122.4014 | 0.027465 | 0.20142 | 122.5388 | 122.8226 | 122.7036 | 122.7539 | 122.58 | 122.8088 | 122.7356 | 122.4014 | 122.7539 | 122.58 | 122.7356 | 122.7036 | 122.8088 | -0.40283 | -0.37994
1872.1562 | 123.024 | -122.6669 | 0.14191 | -0.25856 | 0.014552 | 0.0033026 | 0.043874 | -0.01512 | -0.0089123 | 0.013262 | -0.082397 | 0.16479 | -0.29297 | -0.018311 | 0.004578 | 0.004578 | 0.059509 | 0.11902 | 0.20599 | -0.25177 | 122.374 | 0.022888 | 122.5845 | 122.6486 | -0.13733 | 122.4152 | 0.064087 | 0.21057 | 122.7264 | 122.7859 | 122.6715 | 122.8317 | 122.5845 | 122.8729 | 122.6715 | 122.4152 | 122.8317 | 122.5845 | 122.6715 | 122.6715 | 122.8729 | -0.43488 | -0.39368
1873.8438 | 122.8867 | -122.6852 | 0.17395 | -0.083084 | 0.014125 | -0.00075623 | 0.045583 | -0.013839 | -0.012117 | 0.018389 | 0.004578 | 0.15106 | -0.27924 | 0.041199 | 0.045776 | 0.07782 | -0.032043 | 0.16937 | 0.20142 | -0.23346 | 122.406 | -0.022888 | 122.6898 | 122.7264 | -0.12817 | 122.4518 | 0.027466 | 0.28381 | 122.6532 | 122.8546 | 122.731 | 122.8363 | 122.6898 | 122.8867 | 122.7631 | 122.4518 | 122.8363 | 122.6898 | 122.7631 | 122.731 | 122.8867 | -0.45319 | -0.40741
1875.5312 | 122.9828 | -122.6807 | 0.15106 | -0.15175 | 0.016475 | 0.0037298 | 0.040456 | -0.014479 | -0.0095531 | 0.016039 | 0.027466 | 0.1236 | -0.23346 | 0.073242 | 0.11902 | 0.14648 | -0.09613 | 0.25177 | 0.18768 | -0.21973 | 122.4472 | -0.027466 | 122.7081 | 122.7539 | -0.032043 | 122.4609 | 0.036621 | 0.26093 | 122.5845 | 122.9324 | 122.7997 | 122.8043 | 122.7081 | 122.8683 | 122.8271 | 122.4609 | 122.8043 | 122.7081 | 122.8271 | 122.7997 | 122.8683 | -0.38452 | -0.37079
1877.2188 | 123.0057 | -122.6578 | 0.14648 | -0.0067901 | 0.014552 | 0.00095277 | 0.039815 | -0.013198 | -0.0086987 | 0.016039 | -0.032043 | 0.1236 | -0.23804 | 0.018311 | 0.068665 | 0.10071 | -0.10529 | 0.18768 | 0.17853 | -0.21057 | 122.4197 | -0.022888 | 122.6257 | 122.6761 | -0.077819 | 122.4472 | 0.032044 | 0.20599 | 122.5525 | 122.8455 | 122.7264 | 122.7814 | 122.6257 | 122.8363 | 122.7585 | 122.4472 | 122.7814 | 122.6257 | 122.7585 | 122.7264 | 122.8363 | -0.38452 | -0.35706
1878.9375 | 122.9965 | -122.6669 | 0.15106 | -0.19753 | 0.016261 | 0.002021 | 0.041951 | -0.016616 | -0.0095531 | 0.014971 | 0.036621 | 0.11902 | -0.23804 | 0.073242 | 0.10071 | 0.11902 | -0.059509 | 0.25635 | 0.17395 | -0.23346 | 122.4289 | -0.032043 | 122.7036 | 122.7402 | -0.050354 | 122.4335 | 0.022888 | 0.27466 | 122.6074 | 122.9233 | 122.7676 | 122.7859 | 122.7036 | 122.8409 | 122.7859 | 122.4335 | 122.7859 | 122.7036 | 122.7859 | 122.7676 | 122.8409 | -0.3891 | -0.38452
1880.625 | 122.9599 | -122.6898 | 0.16479 | 0.12291 | 0.013911 | 0.0052252 | 0.04067 | -0.013625 | -0.0091259 | 0.014544 | -0.004578 | 0.11902 | -0.2243 | 0.032043 | 0.068665 | 0.11444 | -0.11444 | 0.1831 | 0.17395 | -0.21973 | 122.4655 | -0.045776 | 122.6852 | 122.7219 | -0.09613 | 122.4701 | 0.009155 | 0.21973 | 122.5754 | 122.8729 | 122.7585 | 122.8088 | 122.6852 | 122.8638 | 122.8043 | 122.4701 | 122.8088 | 122.6852 | 122.8043 | 122.7585 | 122.8638 | -0.3891 | -0.38452
1882.3125 | 122.9462 | -122.6944 | 0.17395 | 0.061874 | 0.013698 | -0.00075623 | 0.047078 | -0.012557 | -0.012117 | 0.014757 | -0.059509 | 0.13733 | -0.25635 | -0.027466 | -0.013733 | -0.004578 | 0.022888 | 0.09613 | 0.21973 | -0.24261 | 122.438 | -0.036621 | 122.6349 | 122.6669 | -0.18768 | 122.4518 | 0.045777 | 0.19684 | 122.7173 | 122.7905 | 122.6807 | 122.8317 | 122.6349 | 122.9141 | 122.6898 | 122.4518 | 122.8317 | 122.6349 | 122.6898 | 122.6807 | 122.9141 | -0.4303 | -0.41656
1884.0312 | 122.9828 | -122.6898 | 0.16479 | -0.13649 | 0.014338 | -0.00075623 | 0.039815 | -0.014266 | -0.0091259 | 0.016039 | 0.032043 | 0.12817 | -0.24261 | 0.10071 | 0.13733 | 0.16937 | -0.14648 | 0.28381 | 0.16022 | -0.20142 | 122.4472 | -0.036621 | 122.7219 | 122.7905 | -0.027466 | 122.4884 | -0.004578 | 0.27466 | 122.5433 | 122.9736 | 122.8271 | 122.818 | 122.7219 | 122.85 | 122.8592 | 122.4884 | 122.818 | 122.7219 | 122.8592 | 122.8271 | 122.85 | -0.40741 | -0.36621
1885.7188 | 123.024 | -122.6624 | 0.14191 | 0.0084684 | 0.013057 | 0.0018072 | 0.040029 | -0.013625 | -0.0084851 | 0.015612 | -0.009155 | 0.13275 | -0.21515 | 0.027466 | 0.054932 | 0.10529 | -0.10071 | 0.1831 | 0.17395 | -0.21973 | 122.4472 | -0.009156 | 122.6532 | 122.6898 | -0.086975 | 122.4426 | 0.032043 | 0.20599 | 122.5616 | 122.8455 | 122.7173 | 122.7951 | 122.6532 | 122.8363 | 122.7676 | 122.4426 | 122.7951 | 122.6532 | 122.7676 | 122.7173 | 122.8363 | -0.35706 | -0.36163
1887.4219 | 122.9187 | -122.6852 | 0.17395 | 0.20683 | 0.015407 | 0.0058662 | 0.045583 | -0.012984 | -0.0072033 | 0.017107 | -0.022888 | 0.15106 | -0.25635 | 0.018311 | 0.036621 | 0.082397 | -0.09613 | 0.15106 | 0.19226 | -0.22888 | 122.4289 | -0.022888 | 122.6624 | 122.7036 | -0.13733 | 122.4564 | 0.018311 | 0.23346 | 122.5891 | 122.8363 | 122.7219 | 122.8363 | 122.6624 | 122.8775 | 122.7676 | 122.4564 | 122.8363 | 122.6624 | 122.7676 | 122.7219 | 122.8775 | -0.4303 | -0.40283
1889.1094 | 123.0103 | -122.6715 | 0.17853 | -0.18227 | 0.015193 | -0.00075623 | 0.044942 | -0.014266 | -0.010835 | 0.015184 | -0.050354 | 0.15106 | -0.25635 | 0.018311 | 0.032043 | 0.045776 | 0.013733 | 0.14191 | 0.20599 | -0.23804 | 122.4152 | -0.027466 | 122.6212 | 122.6898 | -0.14648 | 122.4335 | 0.027466 | 0.20599 | 122.6852 | 122.8134 | 122.7036 | 122.8226 | 122.6212 | 122.8775 | 122.7173 | 122.4335 | 122.8226 | 122.6212 | 122.7173 | 122.7036 | 122.8775 | -0.43488 | -0.41656
1890.7812 | 122.9919 | -122.6852 | 0.15564 | 0.069504 | 0.016902 | 0.0037298 | 0.04067 | -0.013839 | -0.0091259 | 0.016466 | -0.013733 | 0.11444 | -0.22888 | 0.018311 | 0.068665 | 0.11444 | -0.086975 | 0.18768 | 0.17853 | -0.2243 | 122.4564 | -0.041199 | 122.6715 | 122.7036 | -0.086975 | 122.4609 | 0.022888 | 0.21515 | 122.5983 | 122.8729 | 122.7539 | 122.7997 | 122.6715 | 122.8638 | 122.7997 | 122.4609 | 122.7997 | 122.6715 | 122.7997 | 122.7539 | 122.8638 | -0.38452 | -0.37994
1892.4688 | 123.0331 | -122.6669 | 0.16937 | -0.25856 | 0.016047 | 0.0050116 | 0.042379 | -0.015334 | -0.0084851 | 0.016893 | -0.082397 | 0.16479 | -0.27008 | -0.022888 | 0.018311 | 0.027466 | 0.064087 | 0.1236 | 0.20142 | -0.25177 | 122.3969 | -0.004578 | 122.5845 | 122.644 | -0.15106 | 122.4152 | 0.032043 | 0.18768 | 122.731 | 122.7905 | 122.6852 | 122.8317 | 122.5845 | 122.8683 | 122.6944 | 122.4152 | 122.8317 | 122.5845 | 122.6944 | 122.6852 | 122.8683 | -0.43945 | -0.42114
1894.1875 | 122.905 | -122.731 | 0.19684 | -0.060196 | 0.016047 | 0.0041572 | 0.047933 | -0.013198 | -0.011049 | 0.016039 | 0.004578 | 0.13733 | -0.25635 | 0.045776 | 0.064087 | 0.073242 | -0.027466 | 0.16937 | 0.18768 | -0.24719 | 122.4747 | -0.059509 | 122.7356 | 122.7768 | -0.13275 | 122.4838 | -0.009155 | 0.26093 | 122.7036 | 122.9004 | 122.7951 | 122.8683 | 122.7356 | 122.9187 | 122.8043 | 122.4838 | 122.8683 | 122.7356 | 122.8043 | 122.7951 | 122.9187 | -0.45319 | -0.44403
1895.875 | 122.9965 | -122.6852 | 0.16479 | -0.15175 | 0.014125 | -0.00011543 | 0.038106 | -0.01277 | -0.0078443 | 0.015184 | 0.018311 | 0.13733 | -0.22888 | 0.068665 | 0.11902 | 0.11902 | -0.059509 | 0.24261 | 0.19226 | -0.21973 | 122.4564 | -0.027466 | 122.7036 | 122.7539 | -0.045776 | 122.4655 | 0.027466 | 0.24719 | 122.6257 | 122.9279 | 122.8043 | 122.8226 | 122.7036 | 122.8775 | 122.8043 | 122.4655 | 122.8226 | 122.7036 | 122.8043 | 122.8043 | 122.8775 | -0.39368 | -0.38452
1897.5625 | 122.9553 | -122.6944 | 0.17853 | 0.16106 | 0.015407 | 0.00073917 | 0.039601 | -0.011275 | -0.0080579 | 0.016039 | 0.036621 | 0.15564 | -0.23804 | 0.045776 | 0.10071 | 0.1236 | -0.14191 | 0.19226 | 0.1831 | -0.21973 | 122.4564 | -0.022888 | 122.731 | 122.7402 | -0.07782 | 122.4747 | 0.004577 | 0.27466 | 122.5525 | 122.8867 | 122.7951 | 122.85 | 122.731 | 122.8775 | 122.818 | 122.4747 | 122.85 | 122.731 | 122.818 | 122.7951 | 122.8775 | -0.41656 | -0.39826
1899.25 | 122.9462 | -122.6944 | 0.17853 | 0.16869 | 0.016047 | 0.0043708 | 0.045797 | -0.01277 | -0.0089123 | 0.015398 | -0.068665 | 0.17853 | -0.27924 | -0.032043 | -0.009155 | 0.022888 | 0.013733 | 0.07782 | 0.21515 | -0.26093 | 122.4152 | 0 | 122.6257 | 122.6624 | -0.18768 | 122.4335 | 0.036621 | 0.21057 | 122.7081 | 122.7722 | 122.6852 | 122.8729 | 122.6257 | 122.9095 | 122.7173 | 122.4335 | 122.8729 | 122.6257 | 122.7173 | 122.6852 | 122.9095 | -0.45776 | -0.43945
1900.9844 | 122.9507 | -122.6898 | 0.16937 | 0.10765 | 0.012416 | 0.0035162 | 0.042806 | -0.012557 | -0.0074169 | 0.015398 | -0.073242 | 0.16022 | -0.28381 | -0.032043 | 0 | 0.027466 | -0.022888 | 0.09613 | 0.18768 | -0.24261 | 122.406 | -0.009156 | 122.6166 | 122.6578 | -0.16937 | 122.4472 | 0.01831 | 0.21057 | 122.6669 | 122.7859 | 122.6898 | 122.85 | 122.6166 | 122.8775 | 122.7173 | 122.4472 | 122.85 | 122.6166 | 122.7173 | 122.6898 | 122.8775 | -0.45319 | -0.41199
1902.6562 | 123.024 | -122.6578 | 0.15564 | -0.21278 | 0.016688 | -0.0033196 | 0.044301 | -0.01277 | -0.0093395 | 0.01668 | -0.064087 | 0.16937 | -0.27466 | -0.036621 | 0.009155 | 0.032043 | 0.064087 | 0.12817 | 0.21057 | -0.2655 | 122.3831 | 0.013733 | 122.5937 | 122.6212 | -0.14649 | 122.3923 | 0.054931 | 0.21057 | 122.7219 | 122.7859 | 122.6669 | 122.8271 | 122.5937 | 122.8683 | 122.6898 | 122.3923 | 122.8271 | 122.5937 | 122.6898 | 122.6669 | 122.8683 | -0.4303 | -0.42114
1904.3438 | 123.0194 | -122.6578 | 0.14191 | 0.038986 | 0.01562 | 0.00138 | 0.039815 | -0.012343 | -0.0067761 | 0.017107 | -0.022888 | 0.1236 | -0.2243 | 0.009155 | 0.064087 | 0.10529 | -0.091553 | 0.16937 | 0.19684 | -0.24261 | 122.4335 | -0.018311 | 122.6349 | 122.6669 | -0.07782 | 122.4152 | 0.054931 | 0.20142 | 122.5662 | 122.8271 | 122.7219 | 122.7814 | 122.6349 | 122.8546 | 122.7631 | 122.4152 | 122.7814 | 122.6349 | 122.7631 | 122.7219 | 122.8546 | -0.36621 | -0.38452
1906.0469 | 122.9004 | -122.7219 | 0.17395 | 0.1992 | 0.012843 | 0.0018072 | 0.042165 | -0.013839 | -0.0078443 | 0.017321 | 0.041199 | 0.11444 | -0.21515 | 0.086975 | 0.12817 | 0.16937 | -0.17853 | 0.22888 | 0.16937 | -0.19684 | 122.5067 | -0.059509 | 122.7631 | 122.8088 | -0.045776 | 122.525 | -0.004577 | 0.25635 | 122.5433 | 122.9507 | 122.85 | 122.8363 | 122.7631 | 122.8912 | 122.8912 | 122.525 | 122.8363 | 122.7631 | 122.8912 | 122.85 | 122.8912 | -0.3891 | -0.37079
1907.7344 | 123.0377 | -122.6624 | 0.14191 | -0.25093 | 0.014125 | -0.00011543 | 0.040242 | -0.014479 | -0.0095531 | 0.015398 | -0.086975 | 0.15564 | -0.28381 | -0.027466 | 0 | 0.009155 | 0.073242 | 0.11902 | 0.21515 | -0.24719 | 122.3785 | 0.013733 | 122.5754 | 122.6349 | -0.14191 | 122.4152 | 0.073242 | 0.19684 | 122.7356 | 122.7814 | 122.6624 | 122.818 | 122.5754 | 122.8775 | 122.6715 | 122.4152 | 122.818 | 122.5754 | 122.6715 | 122.6624 | 122.8775 | -0.42572 | -0.3891
1909.4531 | 123.0011 | -122.6898 | 0.16937 | -0.20515 | 0.01562 | -0.003106 | 0.044942 | -0.013839 | -0.011476 | 0.017321 | -0.064087 | 0.16022 | -0.27924 | 0 | 0.032043 | 0.041199 | 0.022888 | 0.15106 | 0.21057 | -0.23346 | 122.4106 | -0.009156 | 122.6257 | 122.6898 | -0.13733 | 122.4564 | 0.041198 | 0.21515 | 122.7127 | 122.8409 | 122.7219 | 122.85 | 122.6257 | 122.9004 | 122.731 | 122.4564 | 122.85 | 122.6257 | 122.731 | 122.7219 | 122.9004 | -0.44861 | -0.40283
1911.1719 | 123.0103 | -122.6669 | 0.16022 | -0.23567 | 0.014125 | 0.0050116 | 0.039815 | -0.013625 | -0.0067761 | 0.015184 | 0.018311 | 0.1236 | -0.2243 | 0.059509 | 0.09613 | 0.10986 | -0.032043 | 0.21973 | 0.20142 | -0.23346 | 122.4426 | -0.036621 | 122.6852 | 122.7264 | -0.064087 | 122.4335 | 0.041199 | 0.24261 | 122.6349 | 122.8867 | 122.7631 | 122.7905 | 122.6852 | 122.8683 | 122.7768 | 122.4335 | 122.7905 | 122.6852 | 122.7768 | 122.7631 | 122.8683 | -0.38452 | -0.39368
1912.8594 | 122.905 | -122.7173 | 0.17853 | 0.15343 | 0.014766 | -0.00011543 | 0.042592 | -0.012984 | -0.0095531 | 0.014544 | 0.050354 | 0.1236 | -0.22888 | 0.086975 | 0.09613 | 0.15106 | -0.17395 | 0.23346 | 0.15564 | -0.19684 | 122.4884 | -0.054932 | 122.7676 | 122.8043 | -0.082398 | 122.5204 | -0.022888 | 0.27924 | 122.5433 | 122.9507 | 122.8134 | 122.8409 | 122.7676 | 122.8729 | 122.8683 | 122.5204 | 122.8409 | 122.7676 | 122.8683 | 122.8134 | 122.8729 | -0.40741 | -0.37537
1914.5625 | 123.0377 | -122.6486 | 0.13275 | -0.0067901 | 0.014338 | 0.002021 | 0.040242 | -0.014052 | -0.0059217 | 0.014757 | -0.022888 | 0.13733 | -0.21515 | 0.022888 | 0.082397 | 0.10529 | -0.09613 | 0.19684 | 0.17853 | -0.23804 | 122.4335 | 0.004578 | 122.6257 | 122.6715 | -0.050354 | 122.4106 | 0.045777 | 0.19226 | 122.5525 | 122.8455 | 122.731 | 122.7859 | 122.6257 | 122.8271 | 122.7539 | 122.4106 | 122.7859 | 122.6257 | 122.7539 | 122.731 | 122.8271 | -0.3479 | -0.37079
1916.2656 | 122.9919 | -122.6715 | 0.13275 | -0.098343 | 0.014552 | -0.001397 | 0.04067 | -0.016188 | -0.0097669 | 0.016893 | 0 | 0.1236 | -0.23346 | 0.091553 | 0.11902 | 0.14648 | -0.13733 | 0.26093 | 0.16479 | -0.21973 | 122.4381 | -0.009155 | 122.6715 | 122.7631 | -0.013732 | 122.4518 | 0.032044 | 0.23346 | 122.5342 | 122.9324 | 122.7905 | 122.7951 | 122.6715 | 122.8363 | 122.818 | 122.4518 | 122.7951 | 122.6715 | 122.818 | 122.7905 | 122.8363 | -0.36621 | -0.35248
1917.9844 | 123.0286 | -122.6624 | 0.13733 | -0.022049 | 0.011775 | 0.0024482 | 0.040242 | -0.012984 | -0.0076305 | 0.015825 | -0.018311 | 0.12817 | -0.24261 | 0.045776 | 0.07782 | 0.11902 | -0.10071 | 0.21515 | 0.17853 | -0.24261 | 122.4197 | -0.009155 | 122.644 | 122.7081 | -0.059509 | 122.4197 | 0.041199 | 0.2243 | 122.5616 | 122.8775 | 122.7402 | 122.7905 | 122.644 | 122.8409 | 122.7814 | 122.4197 | 122.7905 | 122.644 | 122.7814 | 122.7402 | 122.8409 | -0.37994 | -0.37994
1919.6875 | 122.9187 | -122.699 | 0.16022 | 0.16106 | 0.016047 | -0.0024652 | 0.044301 | -0.014052 | -0.011262 | 0.017962 | 0.054932 | 0.11444 | -0.2243 | 0.09613 | 0.10529 | 0.14648 | -0.17395 | 0.22888 | 0.17395 | -0.21515 | 122.4747 | -0.045776 | 122.7539 | 122.7951 | -0.054931 | 122.4838 | 0.013733 | 0.27924 | 122.525 | 122.9279 | 122.8043 | 122.8134 | 122.7539 | 122.8729 | 122.8455 | 122.4838 | 122.8134 | 122.7539 | 122.8455 | 122.8043 | 122.8729 | -0.38452 | -0.37537
1921.3906 | 123.0011 | -122.6761 | 0.15564 | -0.098343 | 0.016475 | 0.0022346 | 0.039601 | -0.016402 | -0.0074169 | 0.017107 | 0.027466 | 0.10986 | -0.22888 | 0.10529 | 0.1236 | 0.15106 | -0.13275 | 0.27466 | 0.17853 | -0.2243 | 122.4472 | -0.045777 | 122.7036 | 122.7814 | -0.032044 | 122.4518 | 0.022888 | 0.25635 | 122.5433 | 122.9507 | 122.7997 | 122.7859 | 122.7036 | 122.8546 | 122.8271 | 122.4518 | 122.7859 | 122.7036 | 122.8271 | 122.7997 | 122.8546 | -0.38452 | -0.37994
1923.0625 | 122.9004 | -122.7127 | 0.19226 | 0.18394 | 0.011989 | 0.0028754 | 0.045369 | -0.013625 | -0.0093395 | 0.014971 | 0.041199 | 0.11902 | -0.23346 | 0.082397 | 0.11902 | 0.15106 | -0.1831 | 0.22888 | 0.14648 | -0.20142 | 122.4792 | -0.073242 | 122.7539 | 122.7951 | -0.073242 | 122.5113 | -0.045777 | 0.27466 | 122.5296 | 122.9416 | 122.8317 | 122.8317 | 122.7539 | 122.8592 | 122.8638 | 122.5113 | 122.8317 | 122.7539 | 122.8638 | 122.8317 | 122.8592 | -0.42572 | -0.39368
1924.75 | 123.0652 | -122.6669 | 0.15106 | -0.23567 | 0.01562 | -0.00054263 | 0.045797 | -0.014479 | -0.0099805 | 0.015398 | -0.086975 | 0.15564 | -0.27466 | -0.027466 | 0 | 0 | 0.068665 | 0.1236 | 0.2243 | -0.26093 | 122.3923 | 0.004578 | 122.58 | 122.6395 | -0.15106 | 122.406 | 0.073242 | 0.18768 | 122.7356 | 122.7905 | 122.6669 | 122.8226 | 122.58 | 122.8912 | 122.6669 | 122.406 | 122.8226 | 122.58 | 122.6669 | 122.6669 | 122.8912 | -0.42572 | -0.41199
1926.4375 | 123.0377 | -122.6669 | 0.16022 | 0.046615 | 0.01327 | 0.0037298 | 0.039601 | -0.014266 | -0.0093395 | 0.015612 | -0.027466 | 0.13275 | -0.22888 | 0.036621 | 0.064087 | 0.10529 | -0.091553 | 0.17853 | 0.17853 | -0.21973 | 122.438 | -0.027466 | 122.6395 | 122.7036 | -0.09613 | 122.4472 | 0.018311 | 0.20142 | 122.5754 | 122.8455 | 122.731 | 122.7997 | 122.6395 | 122.8455 | 122.7722 | 122.4472 | 122.7997 | 122.6395 | 122.7722 | 122.731 | 122.8455 | -0.3891 | -0.37994
1928.125 | 123.0423 | -122.6852 | 0.14648 | -0.22041 | 0.014338 | 9.8166e-05 | 0.044088 | -0.01512 | -0.0086987 | 0.013262 | -0.045776 | 0.15106 | -0.25635 | 0 | 0.027466 | 0.027466 | 0.041199 | 0.13733 | 0.21973 | -0.24719 | 122.4289 | 0.004578 | 122.6395 | 122.6852 | -0.11902 | 122.4381 | 0.073243 | 0.21057 | 122.7264 | 122.8226 | 122.7127 | 122.8363 | 122.6395 | 122.905 | 122.7127 | 122.4381 | 122.8363 | 122.6395 | 122.7127 | 122.7127 | 122.905 | -0.40283 | -0.39368
1929.8438 | 122.9462 | -122.6852 | 0.17853 | 0.10765 | 0.015407 | 0.0058662 | 0.047292 | -0.011916 | -0.012758 | 0.017534 | -0.054932 | 0.14648 | -0.30212 | -0.036621 | 0 | 0.004578 | 0.013733 | 0.068665 | 0.21515 | -0.25635 | 122.3831 | -0.032044 | 122.6303 | 122.6486 | -0.17853 | 122.4289 | 0.036621 | 0.24719 | 122.699 | 122.7539 | 122.6852 | 122.8317 | 122.6303 | 122.9004 | 122.6898 | 122.4289 | 122.8317 | 122.6303 | 122.6898 | 122.6852 | 122.9004 | -0.48065 | -0.43488
1931.5312 | 122.9599 | -122.6807 | 0.16937 | 0.10002 | 0.013057 | 0.00052557 | 0.045797 | -0.0093524 | -0.010621 | 0.017321 | -0.068665 | 0.15564 | -0.29297 | -0.018311 | 0 | 0.009155 | 0.022888 | 0.10071 | 0.19684 | -0.23804 | 122.3877 | -0.013733 | 122.612 | 122.6624 | -0.16937 | 122.4426 | 0.027465 | 0.2243 | 122.7036 | 122.7814 | 122.6807 | 122.8363 | 122.612 | 122.8775 | 122.6898 | 122.4426 | 122.8363 | 122.612 | 122.6898 | 122.6807 | 122.8775 | -0.46234 | -0.40741
1933.2031 | 122.9919 | -122.7081 | 0.15564 | -0.14412 | 0.012843 | -0.00096983 | 0.037892 | -0.013625 | -0.0097669 | 0.013262 | 0.018311 | 0.14648 | -0.20599 | 0.091553 | 0.14648 | 0.16937 | -0.14648 | 0.27466 | 0.15564 | -0.21057 | 122.5021 | -0.009156 | 122.7264 | 122.7997 | -0.009156 | 122.4976 | 0 | 0.22431 | 122.5616 | 122.9828 | 122.8546 | 122.8546 | 122.7264 | 122.8638 | 122.8775 | 122.4976 | 122.8546 | 122.7264 | 122.8775 | 122.8546 | 122.8638 | -0.36163 | -0.36621
1934.9375 | 123.0286 | -122.6669 | 0.16479 | -0.28145 | 0.014979 | 0.00138 | 0.042592 | -0.014266 | -0.010194 | 0.015184 | -0.07782 | 0.15106 | -0.27008 | -0.027466 | 0.013733 | 0.032043 | 0.059509 | 0.11902 | 0.20599 | -0.25177 | 122.3969 | -0.013733 | 122.5891 | 122.6395 | -0.15106 | 122.4152 | 0.041199 | 0.19226 | 122.7264 | 122.7859 | 122.6807 | 122.818 | 122.5891 | 122.8729 | 122.699 | 122.4152 | 122.818 | 122.5891 | 122.699 | 122.6807 | 122.8729 | -0.43488 | -0.41656
1936.625 | 123.0103 | -122.7081 | 0.16022 | -0.098343 | 0.016047 | -0.0039606 | 0.037465 | -0.015334 | -0.0076305 | 0.016253 | 0.004578 | 0.12817 | -0.2243 | 0.082397 | 0.13733 | 0.16937 | -0.1236 | 0.26093 | 0.18768 | -0.2243 | 122.4838 | -0.032043 | 122.7127 | 122.7905 | -0.022888 | 122.4838 | 0.027466 | 0.22888 | 122.5845 | 122.9691 | 122.8455 | 122.8363 | 122.7127 | 122.8958 | 122.8775 | 122.4838 | 122.8363 | 122.7127 | 122.8775 | 122.8455 | 122.8958 | -0.38452 | -0.38452
1938.3125 | 122.9187 | -122.7173 | 0.18768 | 0.19157 | 0.01562 | 0.0024482 | 0.043233 | -0.014266 | -0.010835 | 0.018389 | 0.050354 | 0.11444 | -0.22888 | 0.082397 | 0.11902 | 0.15564 | -0.20599 | 0.22888 | 0.16022 | -0.19684 | 122.4884 | -0.073242 | 122.7676 | 122.7997 | -0.068664 | 122.5204 | -0.027466 | 0.27924 | 122.5113 | 122.9462 | 122.8363 | 122.8317 | 122.7676 | 122.8775 | 122.8729 | 122.5204 | 122.8317 | 122.7676 | 122.8729 | 122.8363 | 122.8775 | -0.41656 | -0.38452
1940 | 123.024 | -122.6669 | 0.16022 | -0.23567 | 0.012843 | 0.0045844 | 0.044301 | -0.012984 | -0.011049 | 0.015612 | -0.082397 | 0.16479 | -0.27466 | -0.018311 | 0.013733 | 0.018311 | 0.07782 | 0.11444 | 0.2243 | -0.24719 | 122.3923 | 0.004578 | 122.5845 | 122.6486 | -0.14648 | 122.4197 | 0.064087 | 0.19226 | 122.7448 | 122.7814 | 122.6807 | 122.8317 | 122.5845 | 122.8912 | 122.6852 | 122.4197 | 122.8317 | 122.5845 | 122.6852 | 122.6807 | 122.8912 | -0.43488 | -0.40741
1941.6875 | 122.9965 | -122.6578 | 0.16022 | 0.10002 | 0.015193 | 0.00073917 | 0.041097 | -0.01277 | -0.0093395 | 0.017748 | -0.009155 | 0.10986 | -0.25177 | 0.041199 | 0.07782 | 0.11902 | -0.10071 | 0.20142 | 0.17853 | -0.20142 | 122.406 | -0.050354 | 122.6486 | 122.699 | -0.082397 | 122.4564 | 0.018311 | 0.24261 | 122.5571 | 122.8592 | 122.7356 | 122.7676 | 122.6486 | 122.8363 | 122.7768 | 122.4564 | 122.7676 | 122.6486 | 122.7768 | 122.7356 | 122.8363 | -0.41199 | -0.36163
1943.3906 | 122.9507 | -122.7081 | 0.17395 | 0.16106 | 0.016688 | 0.00073917 | 0.046651 | -0.01277 | -0.0082715 | 0.016466 | -0.050354 | 0.17395 | -0.27924 | -0.018311 | 0.004578 | 0.032043 | -0.022888 | 0.10071 | 0.21515 | -0.26093 | 122.4289 | 0 | 122.6578 | 122.6898 | -0.16937 | 122.4472 | 0.041199 | 0.22888 | 122.6852 | 122.8088 | 122.7127 | 122.8821 | 122.6578 | 122.9233 | 122.7402 | 122.4472 | 122.8821 | 122.6578 | 122.7402 | 122.7127 | 122.9233 | -0.45319 | -0.43488
1945.0938 | 123.0469 | -122.6852 | 0.16937 | -0.26619 | 0.016261 | 9.8166e-05 | 0.042165 | -0.014693 | -0.0095531 | 0.015612 | -0.004578 | 0.14191 | -0.24719 | 0.036621 | 0.07782 | 0.091553 | -0.004578 | 0.20599 | 0.18768 | -0.24719 | 122.4381 | -0.027466 | 122.6807 | 122.7219 | -0.091553 | 122.4381 | 0.01831 | 0.24261 | 122.6807 | 122.8912 | 122.7631 | 122.8271 | 122.6807 | 122.8729 | 122.7768 | 122.4381 | 122.8271 | 122.6807 | 122.7768 | 122.7631 | 122.8729 | -0.41656 | -0.41656
1946.7812 | 122.9004 | -122.731 | 0.17853 | 0.1992 | 0.014979 | 0.0022346 | 0.04366 | -0.011916 | -0.010194 | 0.016893 | 0.045776 | 0.12817 | -0.22888 | 0.07782 | 0.10986 | 0.16479 | -0.17853 | 0.21973 | 0.1831 | -0.20142 | 122.5021 | -0.050354 | 122.7768 | 122.8088 | -0.068665 | 122.5296 | 0.004577 | 0.27466 | 122.5525 | 122.9507 | 122.8409 | 122.8592 | 122.7768 | 122.9141 | 122.8958 | 122.5296 | 122.8592 | 122.7768 | 122.8958 | 122.8409 | 122.9141 | -0.40741 | -0.37994
1948.5 | 123.0377 | -122.6761 | 0.15564 | -0.19753 | 0.01562 | 0.0043708 | 0.042592 | -0.015975 | -0.011476 | 0.017321 | -0.073242 | 0.17395 | -0.29297 | 0 | 0.022888 | 0.018311 | 0.045776 | 0.1236 | 0.21515 | -0.24261 | 122.3831 | 0.01831 | 122.6028 | 122.6761 | -0.13275 | 122.4335 | 0.059509 | 0.21973 | 122.7219 | 122.7997 | 122.699 | 122.85 | 122.6028 | 122.8912 | 122.6944 | 122.4335 | 122.85 | 122.6028 | 122.6944 | 122.699 | 122.8912 | -0.44861 | -0.39826
1950.1875 | 123.0148 | -122.6761 | 0.15106 | 0.046615 | 0.015407 | 0.00052557 | 0.039174 | -0.01213 | -0.0080579 | 0.014971 | -0.013733 | 0.13275 | -0.23346 | 0.018311 | 0.073242 | 0.10986 | -0.091553 | 0.1831 | 0.1831 | -0.22888 | 122.4426 | -0.018311 | 122.6624 | 122.6944 | -0.07782 | 122.4472 | 0.032043 | 0.21973 | 122.5845 | 122.8592 | 122.7493 | 122.8088 | 122.6624 | 122.8592 | 122.7859 | 122.4472 | 122.8088 | 122.6624 | 122.7859 | 122.7493 | 122.8592 | -0.38452 | -0.37994
1951.8906 | 122.9141 | -122.7081 | 0.1831 | 0.18394 | 0.013484 | 0.0015936 | 0.045156 | -0.014479 | -0.0089123 | 0.018175 | 0.064087 | 0.10986 | -0.21973 | 0.07782 | 0.10986 | 0.16937 | -0.18768 | 0.23804 | 0.15564 | -0.20599 | 122.4884 | -0.073242 | 122.7722 | 122.7859 | -0.073242 | 122.5021 | -0.027465 | 0.28381 | 122.5204 | 122.9462 | 122.818 | 122.818 | 122.7722 | 122.8638 | 122.8775 | 122.5021 | 122.818 | 122.7722 | 122.8775 | 122.818 | 122.8638 | -0.40283 | -0.3891
1953.5781 | 122.9691 | -122.7127 | 0.17395 | -0.16701 | 0.01562 | 0.003089 | 0.045797 | -0.014479 | -0.011262 | 0.016253 | -0.032043 | 0.15564 | -0.27924 | 0.027466 | 0.050354 | 0.059509 | -0.004578 | 0.16479 | 0.19684 | -0.24719 | 122.4335 | -0.01831 | 122.6807 | 122.7402 | -0.1236 | 122.4655 | 0.022888 | 0.24719 | 122.7081 | 122.8775 | 122.7631 | 122.8683 | 122.6807 | 122.9095 | 122.7722 | 122.4655 | 122.8683 | 122.6807 | 122.7722 | 122.7631 | 122.9095 | -0.45319 | -0.42114
1955.2812 | 122.905 | -122.7219 | 0.19684 | -0.060196 | 0.01327 | -0.0026788 | 0.046865 | -0.01277 | -0.012544 | 0.018816 | -0.004578 | 0.15106 | -0.27466 | 0.036621 | 0.068665 | 0.073242 | -0.018311 | 0.15564 | 0.20599 | -0.24719 | 122.4472 | -0.045776 | 122.7173 | 122.7585 | -0.12817 | 122.4747 | 0.009156 | 0.27008 | 122.7036 | 122.8775 | 122.7905 | 122.8729 | 122.7173 | 122.9279 | 122.7951 | 122.4747 | 122.8729 | 122.7173 | 122.7951 | 122.7905 | 122.9279 | -0.4715 | -0.44403
1957.0312 | 122.9462 | -122.7219 | 0.18768 | -0.01442 | 0.016261 | -0.001397 | 0.044728 | -0.013411 | -0.012117 | 0.015612 | -0.013733 | 0.15564 | -0.27008 | -0.013733 | 0.027466 | 0.032043 | -0.009155 | 0.1236 | 0.20599 | -0.23804 | 122.4518 | -0.032043 | 122.7081 | 122.7081 | -0.16022 | 122.4838 | 0.018311 | 0.25635 | 122.7127 | 122.8455 | 122.7493 | 122.8775 | 122.7081 | 122.9279 | 122.7539 | 122.4838 | 122.8775 | 122.7081 | 122.7539 | 122.7493 | 122.9279 | -0.45776 | -0.42572
1958.7188 | 123.0652 | -122.644 | 0.16479 | -0.22041 | 0.01562 | 0.0011664 | 0.039388 | -0.014693 | -0.0091259 | 0.017962 | -0.082397 | 0.17395 | -0.26093 | -0.032043 | 0.018311 | 0.022888 | 0.082397 | 0.13733 | 0.21973 | -0.25635 | 122.3831 | 0.009155 | 122.5616 | 122.612 | -0.14648 | 122.3877 | 0.054932 | 0.17853 | 122.7264 | 122.7814 | 122.6624 | 122.818 | 122.5616 | 122.8638 | 122.6669 | 122.3877 | 122.818 | 122.5616 | 122.6669 | 122.6624 | 122.8638 | -0.42572 | -0.42114
1960.4062 | 123.0011 | -122.6852 | 0.16937 | 0.069504 | 0.014766 | 0.00031197 | 0.039388 | -0.013198 | -0.0091259 | 0.014971 | 0.009155 | 0.12817 | -0.22888 | 0.027466 | 0.073242 | 0.10529 | -0.09613 | 0.1831 | 0.17853 | -0.22888 | 122.4564 | -0.041199 | 122.6944 | 122.7127 | -0.096131 | 122.4564 | 0.009155 | 0.23804 | 122.5891 | 122.8683 | 122.7585 | 122.8134 | 122.6944 | 122.8638 | 122.7905 | 122.4564 | 122.8134 | 122.6944 | 122.7905 | 122.7585 | 122.8638 | -0.39826 | -0.39826
1962.0938 | 123.0057 | -122.6761 | 0.15564 | -0.090714 | 0.015407 | 0.00031197 | 0.040029 | -0.014693 | -0.0091259 | 0.015612 | 0.004578 | 0.11902 | -0.21973 | 0.073242 | 0.11902 | 0.13275 | -0.10071 | 0.26093 | 0.17853 | -0.22888 | 122.4564 | -0.036621 | 122.6807 | 122.7493 | -0.036621 | 122.4472 | 0.022888 | 0.22431 | 122.5754 | 122.937 | 122.7951 | 122.7951 | 122.6807 | 122.8546 | 122.8088 | 122.4472 | 122.7951 | 122.6807 | 122.8088 | 122.7951 | 122.8546 | -0.37537 | -0.38452
1963.7812 | 122.9645 | -122.7127 | 0.17853 | 0.13817 | 0.016475 | 0.0015936 | 0.045369 | -0.014052 | -0.0095531 | 0.017321 | -0.054932 | 0.18768 | -0.27008 | -0.032043 | -0.004578 | 0.032043 | -0.013733 | 0.091553 | 0.21057 | -0.23804 | 122.4426 | 0.009155 | 122.6578 | 122.6807 | -0.18311 | 122.4747 | 0.032043 | 0.21515 | 122.699 | 122.8043 | 122.7081 | 122.9004 | 122.6578 | 122.9233 | 122.7448 | 122.4747 | 122.9004 | 122.6578 | 122.7448 | 122.7081 | 122.9233 | -0.44861 | -0.41656
1965.4688 | 123.0103 | -122.6669 | 0.16022 | -0.17464 | 0.015834 | 0.0037298 | 0.043447 | -0.012557 | -0.012544 | 0.015398 | -0.054932 | 0.15106 | -0.27924 | 0.013733 | 0.032043 | 0.045776 | 0.032043 | 0.14648 | 0.21057 | -0.23346 | 122.3877 | -0.009155 | 122.612 | 122.6807 | -0.12817 | 122.4335 | 0.050354 | 0.2243 | 122.699 | 122.8134 | 122.699 | 122.818 | 122.612 | 122.8775 | 122.7127 | 122.4335 | 122.818 | 122.612 | 122.7127 | 122.699 | 122.8775 | -0.43945 | -0.39368
1967.1406 | 122.8867 | -122.7402 | 0.19226 | 0.17632 | 0.013484 | -0.00054263 | 0.041524 | -0.010207 | -0.010621 | 0.015398 | 0.045776 | 0.10986 | -0.21973 | 0.07782 | 0.10529 | 0.16022 | -0.19226 | 0.2243 | 0.16937 | -0.19684 | 122.5204 | -0.082398 | 122.7859 | 122.818 | -0.086975 | 122.5433 | -0.022888 | 0.2655 | 122.5479 | 122.9645 | 122.8455 | 122.85 | 122.7859 | 122.9095 | 122.9004 | 122.5433 | 122.85 | 122.7859 | 122.9004 | 122.8455 | 122.9095 | -0.41199 | -0.3891
1968.8281 | 122.9416 | -122.7173 | 0.16937 | 0.10765 | 0.01562 | 0.0026618 | 0.045369 | -0.010634 | -0.011262 | 0.015612 | -0.068665 | 0.16022 | -0.2655 | -0.027466 | 0 | 0.036621 | -0.022888 | 0.10986 | 0.21057 | -0.24719 | 122.4518 | -0.009156 | 122.6486 | 122.6898 | -0.16937 | 122.4701 | 0.041198 | 0.19684 | 122.6944 | 122.8271 | 122.7173 | 122.8775 | 122.6486 | 122.9279 | 122.7539 | 122.4701 | 122.8775 | 122.6486 | 122.7539 | 122.7173 | 122.9279 | -0.43488 | -0.41656
1970.5156 | 123.0423 | -122.6807 | 0.16022 | -0.20515 | 0.01327 | 0.0028754 | 0.040029 | -0.015975 | -0.0084851 | 0.01668 | -0.073242 | 0.17853 | -0.27008 | -0.027466 | 0.018311 | 0.018311 | 0.059509 | 0.13275 | 0.2243 | -0.25177 | 122.4106 | 0.018311 | 122.6074 | 122.6532 | -0.14191 | 122.4289 | 0.064087 | 0.19684 | 122.7402 | 122.8134 | 122.699 | 122.8592 | 122.6074 | 122.905 | 122.699 | 122.4289 | 122.8592 | 122.6074 | 122.699 | 122.699 | 122.905 | -0.4303 | -0.41199
1972.2031 | 122.9141 | -122.7219 | 0.16937 | 0.16106 | 0.014766 | 9.8166e-05 | 0.043447 | -0.013411 | -0.0082715 | 0.01668 | 0.041199 | 0.11444 | -0.23346 | 0.068665 | 0.09613 | 0.13733 | -0.16022 | 0.2243 | 0.17853 | -0.19684 | 122.4884 | -0.054932 | 122.7631 | 122.7905 | -0.073243 | 122.525 | 0.009155 | 0.27466 | 122.5616 | 122.9462 | 122.818 | 122.8363 | 122.7631 | 122.9004 | 122.8592 | 122.525 | 122.8363 | 122.7631 | 122.8592 | 122.818 | 122.9004 | -0.40283 | -0.36621
1973.8906 | 122.9279 | -122.7402 | 0.18768 | -0.098343 | 0.016047 | 0.0058662 | 0.043874 | -0.012343 | -0.0097669 | 0.015398 | 0.009155 | 0.15106 | -0.28381 | 0.041199 | 0.064087 | 0.059509 | -0.027466 | 0.16479 | 0.19684 | -0.24261 | 122.4564 | -0.036621 | 122.7493 | 122.7814 | -0.1236 | 122.4976 | 0.009155 | 0.29297 | 122.7127 | 122.905 | 122.8043 | 122.8912 | 122.7493 | 122.937 | 122.7997 | 122.4976 | 122.8912 | 122.7493 | 122.7997 | 122.8043 | 122.937 | -0.4715 | -0.4303
1975.5781 | 123.0011 | -122.6807 | 0.15564 | -0.10597 | 0.015407 | 0.0022346 | 0.037892 | -0.013411 | -0.0089123 | 0.01668 | 0.013733 | 0.13733 | -0.22888 | 0.082397 | 0.12817 | 0.16937 | -0.12817 | 0.25635 | 0.18768 | -0.23346 | 122.4518 | -0.018311 | 122.6944 | 122.7631 | -0.027466 | 122.4472 | 0.032043 | 0.24261 | 122.5525 | 122.937 | 122.8088 | 122.818 | 122.6944 | 122.8683 | 122.85 | 122.4472 | 122.818 | 122.6944 | 122.85 | 122.8088 | 122.8683 | -0.38452 | -0.3891
1977.2656 | 122.9599 | -122.7081 | 0.14191 | 0.15343 | 0.015834 | -0.0026788 | 0.039174 | -0.015761 | -0.0069897 | 0.015184 | 0 | 0.13733 | -0.24261 | 0.022888 | 0.082397 | 0.1236 | -0.11902 | 0.20142 | 0.18768 | -0.2243 | 122.4655 | -0.004578 | 122.7081 | 122.731 | -0.05951 | 122.4838 | 0.045776 | 0.24261 | 122.5891 | 122.9095 | 122.7905 | 122.8455 | 122.7081 | 122.8958 | 122.8317 | 122.4838 | 122.8455 | 122.7081 | 122.8317 | 122.7905 | 122.8958 | -0.38452 | -0.36621
1978.9531 | 123.0469 | -122.7127 | 0.15564 | -0.22804 | 0.014125 | 0.0050116 | 0.040883 | -0.015548 | -0.0095531 | 0.01668 | -0.054932 | 0.15106 | -0.26093 | -0.018311 | 0.013733 | 0.032043 | 0.036621 | 0.16479 | 0.22888 | -0.25635 | 122.4518 | -0.004578 | 122.6578 | 122.6944 | -0.14191 | 122.4564 | 0.073242 | 0.20599 | 122.7493 | 122.8775 | 122.7264 | 122.8638 | 122.6578 | 122.9416 | 122.7448 | 122.4564 | 122.8638 | 122.6578 | 122.7448 | 122.7264 | 122.9416 | -0.41657 | -0.41199
1980.6406 | 123.024 | -122.6807 | 0.15564 | 0.092392 | 0.014125 | 0.00138 | 0.038106 | -0.01213 | -0.0067761 | 0.018389 | -0.027466 | 0.11902 | -0.2243 | 0.027466 | 0.064087 | 0.10986 | -0.10986 | 0.19226 | 0.18768 | -0.21973 | 122.4564 | -0.036621 | 122.6532 | 122.7081 | -0.091553 | 122.4609 | 0.032043 | 0.19684 | 122.5708 | 122.8729 | 122.7448 | 122.7997 | 122.6532 | 122.8683 | 122.7905 | 122.4609 | 122.7997 | 122.6532 | 122.7905 | 122.7448 | 122.8683 | -0.37994 | -0.37537
1982.3438 | 122.9782 | -122.7127 | 0.17395 | 0.16106 | 0.013911 | -0.00032903 | 0.046651 | -0.013839 | -0.0078443 | 0.016253 | -0.073242 | 0.15106 | -0.28381 | -0.036621 | -0.013733 | 0.009155 | -0.009155 | 0.091553 | 0.20599 | -0.24719 | 122.4289 | -0.022888 | 122.6395 | 122.6761 | -0.18768 | 122.4655 | 0.032044 | 0.21057 | 122.7036 | 122.8043 | 122.699 | 122.8638 | 122.6395 | 122.9187 | 122.7219 | 122.4655 | 122.8638 | 122.6395 | 122.7219 | 122.699 | 122.9187 | -0.45776 | -0.42114
1984.0156 | 123.0011 | -122.699 | 0.16022 | -0.13649 | 0.013484 | 0.0011664 | 0.038747 | -0.016616 | -0.0086987 | 0.015398 | 0.036621 | 0.12817 | -0.23346 | 0.086975 | 0.12817 | 0.13733 | -0.09613 | 0.26093 | 0.17853 | -0.22888 | 122.4655 | -0.032043 | 122.7356 | 122.7859 | -0.032043 | 122.4701 | 0.018311 | 0.27008 | 122.6028 | 122.9599 | 122.8271 | 122.8271 | 122.7356 | 122.8775 | 122.8363 | 122.4701 | 122.8271 | 122.7356 | 122.8363 | 122.8271 | 122.8775 | -0.39368 | -0.3891
1985.75 | 122.9736 | -122.6944 | 0.16937 | 0.10765 | 0.015193 | 0.0084296 | 0.047933 | -0.014907 | -0.010835 | 0.014971 | -0.073242 | 0.17853 | -0.29297 | -0.064087 | -0.018311 | -0.004578 | 0.036621 | 0.086975 | 0.20599 | -0.2655 | 122.4014 | 0.009155 | 122.6212 | 122.6303 | -0.18768 | 122.4289 | 0.036621 | 0.21973 | 122.731 | 122.7814 | 122.6761 | 122.8729 | 122.6212 | 122.9004 | 122.6898 | 122.4289 | 122.8729 | 122.6212 | 122.6898 | 122.6761 | 122.9004 | -0.46234 | -0.43488
1987.4375 | 123.0103 | -122.6898 | 0.1236 | -0.1899 | 0.013698 | -0.0026788 | 0.038106 | -0.014052 | -0.0078443 | 0.017748 | 0.022888 | 0.1236 | -0.22888 | 0.059509 | 0.10529 | 0.14191 | -0.068665 | 0.23804 | 0.17853 | -0.21057 | 122.4609 | 0 | 122.7127 | 122.7493 | -0.01831 | 122.4792 | 0.054932 | 0.25177 | 122.6212 | 122.9279 | 122.7951 | 122.8134 | 122.7127 | 122.8683 | 122.8317 | 122.4792 | 122.8134 | 122.7127 | 122.8317 | 122.7951 | 122.8683 | -0.35248 | -0.33417
1989.1094 | 122.9462 | -122.7173 | 0.17853 | -0.15175 | 0.016261 | 0.0011664 | 0.046437 | -0.013198 | -0.011049 | 0.015825 | -0.013733 | 0.14648 | -0.27924 | 0.013733 | 0.041199 | 0.073242 | -0.013733 | 0.17853 | 0.19684 | -0.25177 | 122.438 | -0.032044 | 122.7036 | 122.731 | -0.13733 | 122.4655 | 0.01831 | 0.2655 | 122.7036 | 122.8958 | 122.7585 | 122.8638 | 122.7036 | 122.9141 | 122.7905 | 122.4655 | 122.8638 | 122.7036 | 122.7905 | 122.7585 | 122.9141 | -0.45776 | -0.4303
1990.7812 | 123.0469 | -122.6761 | 0.13275 | 0.016098 | 0.015193 | -0.00075623 | 0.036824 | -0.014479 | -0.0076305 | 0.015184 | -0.041199 | 0.12817 | -0.24261 | 0.032043 | 0.091553 | 0.13275 | -0.091553 | 0.21515 | 0.1831 | -0.21515 | 122.4335 | -0.004577 | 122.6349 | 122.7081 | -0.041198 | 122.4609 | 0.050354 | 0.20142 | 122.5845 | 122.8912 | 122.7676 | 122.8043 | 122.6349 | 122.8592 | 122.8088 | 122.4609 | 122.8043 | 122.6349 | 122.8088 | 122.7676 | 122.8592 | -0.37537 | -0.3479
1992.4688 | 122.9691 | -122.6944 | 0.17853 | 0.15343 | 0.015193 | 0.0035162 | 0.046865 | -0.010421 | -0.01169 | 0.015612 | -0.041199 | 0.16022 | -0.27008 | -0.036621 | -0.009155 | 0.009155 | -0.009155 | 0.091553 | 0.21973 | -0.25635 | 122.4243 | -0.018311 | 122.6532 | 122.6578 | -0.18768 | 122.438 | 0.041199 | 0.22888 | 122.6852 | 122.7859 | 122.6852 | 122.8546 | 122.6532 | 122.9141 | 122.7036 | 122.438 | 122.8546 | 122.6532 | 122.7036 | 122.6852 | 122.9141 | -0.44861 | -0.43488
1994.1562 | 122.9279 | -122.7356 | 0.19226 | -0.098343 | 0.01562 | 0.0037298 | 0.047078 | -0.012557 | -0.010621 | 0.015825 | -0.004578 | 0.14648 | -0.27466 | 0.041199 | 0.064087 | 0.059509 | -0.041199 | 0.16479 | 0.18768 | -0.23804 | 122.4609 | -0.045777 | 122.731 | 122.7768 | -0.12817 | 122.4976 | -0.004578 | 0.27008 | 122.6944 | 122.9004 | 122.7997 | 122.8821 | 122.731 | 122.9233 | 122.7951 | 122.4976 | 122.8821 | 122.731 | 122.7951 | 122.7997 | 122.9233 | -0.46692 | -0.4303
1995.8438 | 123.0652 | -122.6715 | 0.14191 | 0.031357 | 0.014338 | -0.0024652 | 0.036611 | -0.014693 | -0.0076305 | 0.016466 | -0.041199 | 0.13275 | -0.24261 | 0.032043 | 0.068665 | 0.10529 | -0.10071 | 0.21057 | 0.19684 | -0.21973 | 122.4289 | -0.009156 | 122.6303 | 122.7036 | -0.073242 | 122.4518 | 0.054931 | 0.20142 | 122.5708 | 122.8821 | 122.7402 | 122.8043 | 122.6303 | 122.8683 | 122.7768 | 122.4518 | 122.8043 | 122.6303 | 122.7768 | 122.7402 | 122.8683 | -0.38452 | -0.36163
1997.5625 | 122.9095 | -122.7127 | 0.17395 | 0.1458 | 0.015407 | 0.0033026 | 0.044088 | -0.01277 | -0.011903 | 0.017107 | 0.022888 | 0.11902 | -0.23346 | 0.059509 | 0.10986 | 0.15106 | -0.17395 | 0.2243 | 0.1831 | -0.21973 | 122.4792 | -0.054931 | 122.7356 | 122.7722 | -0.064087 | 122.493 | 0.009155 | 0.25635 | 122.5388 | 122.937 | 122.8226 | 122.8317 | 122.7356 | 122.8958 | 122.8638 | 122.493 | 122.8317 | 122.7356 | 122.8638 | 122.8226 | 122.8958 | -0.40741 | -0.39368
1999.25 | 123.0423 | -122.6944 | 0.15564 | -0.1899 | 0.016047 | 0.00138 | 0.043874 | -0.015761 | -0.010621 | 0.014116 | -0.059509 | 0.17395 | -0.28381 | -0.013733 | 0.013733 | 0.032043 | 0.045776 | 0.13275 | 0.22888 | -0.27008 | 122.4106 | 0.01831 | 122.6349 | 122.6807 | -0.14191 | 122.4243 | 0.073242 | 0.2243 | 122.7402 | 122.8271 | 122.7081 | 122.8683 | 122.6349 | 122.9233 | 122.7264 | 122.4243 | 122.8683 | 122.6349 | 122.7264 | 122.7081 | 122.9233 | -0.43945 | -0.42572
2001 | 123.0057 | -122.7219 | 0.15106 | -0.18227 | 0.014766 | -0.0011834 | 0.037679 | -0.015334 | -0.0086987 | 0.015398 | 0.036621 | 0.13275 | -0.2243 | 0.09613 | 0.13275 | 0.14648 | -0.10529 | 0.27466 | 0.1831 | -0.22888 | 122.4976 | -0.018311 | 122.7585 | 122.818 | -0.018311 | 122.493 | 0.032043 | 0.26093 | 122.6166 | 122.9965 | 122.8546 | 122.8546 | 122.7585 | 122.905 | 122.8683 | 122.493 | 122.8546 | 122.7585 | 122.8683 | 122.8546 | 122.905 | -0.37537 | -0.37994
2002.7188 | 122.9324 | -122.7173 | 0.17853 | 0.20683 | 0.016902 | -0.00032903 | 0.045156 | -0.010421 | -0.01169 | 0.016253 | -0.022888 | 0.16479 | -0.26093 | 0.027466 | 0.054932 | 0.086975 | -0.10986 | 0.16022 | 0.18768 | -0.21515 | 122.4564 | -0.013733 | 122.6944 | 122.7448 | -0.1236 | 122.5021 | 0.009155 | 0.23804 | 122.6074 | 122.8775 | 122.7722 | 122.8821 | 122.6944 | 122.905 | 122.8043 | 122.5021 | 122.8821 | 122.6944 | 122.8043 | 122.7722 | 122.905 | -0.43945 | -0.39368
2004.4062 | 123.0469 | -122.6852 | 0.1831 | -0.1899 | 0.016475 | 0.0018072 | 0.043874 | -0.01747 | -0.011049 | 0.016466 | -0.068665 | 0.16937 | -0.27924 | -0.022888 | 0.013733 | 0.027466 | 0.036621 | 0.12817 | 0.24261 | -0.27924 | 122.406 | -0.013732 | 122.6166 | 122.6624 | -0.16937 | 122.406 | 0.05951 | 0.21057 | 122.7219 | 122.8134 | 122.699 | 122.8546 | 122.6166 | 122.9279 | 122.7127 | 122.406 | 122.8546 | 122.6166 | 122.7127 | 122.699 | 122.9279 | -0.46234 | -0.46234
2006.1094 | 122.9004 | -122.7127 | 0.21057 | 0.10765 | 0.014552 | 0.0069342 | 0.042806 | -0.01277 | -0.0097669 | 0.01668 | 0.036621 | 0.10986 | -0.2243 | 0.073242 | 0.11444 | 0.15106 | -0.16937 | 0.2243 | 0.16937 | -0.21057 | 122.4884 | -0.10071 | 122.7493 | 122.7859 | -0.09613 | 122.5021 | -0.041198 | 0.26093 | 122.5433 | 122.937 | 122.8271 | 122.8226 | 122.7493 | 122.8821 | 122.8638 | 122.5021 | 122.8226 | 122.7493 | 122.8638 | 122.8271 | 122.8821 | -0.43488 | -0.42114
2007.7969 | 123.0194 | -122.7036 | 0.15564 | -0.17464 | 0.013057 | -0.0067376 | 0.039174 | -0.01512 | -0.0076305 | 0.015398 | 0.018311 | 0.11902 | -0.23346 | 0.09613 | 0.1236 | 0.13733 | -0.086975 | 0.25177 | 0.17853 | -0.22888 | 122.4701 | -0.036621 | 122.7219 | 122.7997 | -0.032044 | 122.4747 | 0.022888 | 0.25177 | 122.6166 | 122.9553 | 122.8271 | 122.8226 | 122.7219 | 122.8821 | 122.8409 | 122.4747 | 122.8226 | 122.7219 | 122.8409 | 122.8271 | 122.8821 | -0.3891 | -0.38452
2009.4844 | 122.937 | -122.7127 | 0.17853 | 0.1992 | 0.01797 | 0.0022346 | 0.044301 | -0.011916 | -0.0093395 | 0.015398 | -0.032043 | 0.15106 | -0.2655 | 0 | 0.018311 | 0.073242 | -0.091553 | 0.13733 | 0.20599 | -0.24719 | 122.4472 | -0.027466 | 122.6807 | 122.7127 | -0.16022 | 122.4655 | 0.027466 | 0.23346 | 122.6212 | 122.85 | 122.731 | 122.8638 | 122.6807 | 122.9187 | 122.7859 | 122.4655 | 122.8638 | 122.6807 | 122.7859 | 122.731 | 122.9187 | -0.44403 | -0.42572
2011.1875 | 123.0103 | -122.7081 | 0.15564 | 0.10002 | 0.014766 | 0.0033026 | 0.040242 | -0.014266 | -0.0063489 | 0.015825 | -0.009155 | 0.13275 | -0.22888 | 0.032043 | 0.073242 | 0.11444 | -0.10071 | 0.19684 | 0.17853 | -0.21973 | 122.4792 | -0.022889 | 122.699 | 122.7402 | -0.082398 | 122.4884 | 0.022888 | 0.21973 | 122.6074 | 122.905 | 122.7814 | 122.8409 | 122.699 | 122.8867 | 122.8226 | 122.4884 | 122.8409 | 122.699 | 122.8226 | 122.7814 | 122.8867 | -0.38452 | -0.37537
2012.9375 | 122.9416 | -122.7127 | 0.17853 | -0.052567 | 0.015407 | 0.0018072 | 0.046865 | -0.014479 | -0.012544 | 0.014971 | -0.009155 | 0.15564 | -0.27924 | 0.036621 | 0.064087 | 0.068665 | -0.032043 | 0.17395 | 0.21515 | -0.24719 | 122.4335 | -0.022888 | 122.7036 | 122.7493 | -0.11444 | 122.4655 | 0.036621 | 0.27008 | 122.6807 | 122.8867 | 122.7768 | 122.8683 | 122.7036 | 122.9279 | 122.7814 | 122.4655 | 122.8683 | 122.7036 | 122.7814 | 122.7768 | 122.9279 | -0.45776 | -0.42572
2014.625 | 123.0057 | -122.699 | 0.16022 | -0.13649 | 0.012416 | -0.00096983 | 0.037465 | -0.013625 | -0.0078443 | 0.014757 | 0.045776 | 0.12817 | -0.24261 | 0.10071 | 0.14648 | 0.1831 | -0.14191 | 0.29755 | 0.19684 | -0.21057 | 122.4564 | -0.032043 | 122.7448 | 122.7997 | -0.013733 | 122.4884 | 0.036621 | 0.28839 | 122.5571 | 122.9965 | 122.8455 | 122.8271 | 122.7448 | 122.8958 | 122.8821 | 122.4884 | 122.8271 | 122.7448 | 122.8821 | 122.8455 | 122.8958 | -0.40283 | -0.37079
2016.3281 | 122.9507 | -122.7173 | 0.18768 | -0.12123 | 0.013484 | 0.003089 | 0.045156 | -0.01213 | -0.010194 | 0.014116 | -0.036621 | 0.15564 | -0.29297 | 0.041199 | 0.036621 | 0.059509 | -0.022888 | 0.16479 | 0.20142 | -0.25177 | 122.4243 | -0.032043 | 122.6807 | 122.7585 | -0.15106 | 122.4655 | 0.013733 | 0.25635 | 122.6944 | 122.8821 | 122.7539 | 122.8729 | 122.6807 | 122.9187 | 122.7768 | 122.4655 | 122.8729 | 122.6807 | 122.7768 | 122.7539 | 122.9187 | -0.48065 | -0.43945
2018.0156 | 123.0423 | -122.7127 | 0.14191 | -0.26619 | 0.013911 | -0.00032903 | 0.040029 | -0.015548 | -0.0086987 | 0.016039 | 0 | 0.15564 | -0.25635 | 0.027466 | 0.07782 | 0.07782 | 0.013733 | 0.19684 | 0.20142 | -0.23346 | 122.4564 | 0.013733 | 122.7127 | 122.7402 | -0.064087 | 122.4792 | 0.059509 | 0.25635 | 122.7264 | 122.9095 | 122.7905 | 122.8683 | 122.7127 | 122.9141 | 122.7905 | 122.4792 | 122.8683 | 122.7127 | 122.7905 | 122.7905 | 122.9141 | -0.39826 | -0.37537
2019.7031 | 123.0423 | -122.6624 | 0.15106 | 0.061874 | 0.015193 | 0.002021 | 0.039815 | -0.014479 | -0.010621 | 0.016253 | -0.009155 | 0.11902 | -0.22888 | 0.032043 | 0.068665 | 0.10986 | -0.091553 | 0.18768 | 0.1831 | -0.2243 | 122.4335 | -0.032043 | 122.6532 | 122.6944 | -0.082397 | 122.438 | 0.032043 | 0.21973 | 122.5708 | 122.85 | 122.731 | 122.7814 | 122.6532 | 122.8455 | 122.7722 | 122.438 | 122.7814 | 122.6532 | 122.7722 | 122.731 | 122.8455 | -0.37994 | -0.37537
2021.4062 | 123.0103 | -122.6944 | 0.16479 | -0.20515 | 0.015407 | 0.0022346 | 0.041097 | -0.014052 | -0.0095531 | 0.015825 | 0.041199 | 0.12817 | -0.24261 | 0.10529 | 0.12817 | 0.17395 | -0.12817 | 0.29755 | 0.1831 | -0.21515 | 122.4518 | -0.036621 | 122.7356 | 122.7997 | -0.036621 | 122.4792 | 0.01831 | 0.28381 | 122.5662 | 122.9919 | 122.8226 | 122.8226 | 122.7356 | 122.8775 | 122.8683 | 122.4792 | 122.8226 | 122.7356 | 122.8683 | 122.8226 | 122.8775 | -0.40741 | -0.37994
2023.0938 | 122.9141 | -122.731 | 0.18768 | 0.19157 | 0.016475 | 0.0073614 | 0.044301 | -0.012557 | -0.011476 | 0.015184 | 0.036621 | 0.1236 | -0.23346 | 0.091553 | 0.10529 | 0.16022 | -0.20142 | 0.23346 | 0.16937 | -0.21057 | 122.4976 | -0.064087 | 122.7676 | 122.8226 | -0.082397 | 122.5204 | -0.01831 | 0.27008 | 122.5296 | 122.9645 | 122.8363 | 122.8546 | 122.7676 | 122.9004 | 122.8912 | 122.5204 | 122.8546 | 122.7676 | 122.8912 | 122.8363 | 122.9004 | -0.42114 | -0.39825
2024.8125 | 122.9416 | -122.7173 | 0.18768 | -0.12886 | 0.015193 | 0.00073917 | 0.045369 | -0.015334 | -0.010835 | 0.014971 | -0.018311 | 0.16479 | -0.27924 | 0.036621 | 0.041199 | 0.059509 | -0.022888 | 0.17853 | 0.20142 | -0.24719 | 122.438 | -0.022888 | 122.699 | 122.7539 | -0.14648 | 122.4701 | 0.013733 | 0.26092 | 122.6944 | 122.8958 | 122.7585 | 122.8821 | 122.699 | 122.9187 | 122.7768 | 122.4701 | 122.8821 | 122.699 | 122.7768 | 122.7585 | 122.9187 | -0.46692 | -0.43488
2026.5156 | 122.9599 | -122.7173 | 0.19226 | -0.13649 | 0.015834 | 0.0056524 | 0.046651 | -0.011061 | -0.011262 | 0.01668 | -0.027466 | 0.19226 | -0.27466 | 0.032043 | 0.064087 | 0.064087 | -0.009155 | 0.17853 | 0.21057 | -0.24261 | 122.4426 | 0 | 122.6898 | 122.7493 | -0.12817 | 122.4747 | 0.01831 | 0.24719 | 122.7081 | 122.8958 | 122.7814 | 122.9095 | 122.6898 | 122.9279 | 122.7814 | 122.4747 | 122.9095 | 122.6898 | 122.7814 | 122.7814 | 122.9279 | -0.46692 | -0.43488
2028.2031 | 123.0606 | -122.6715 | 0.15564 | 0.00083945 | 0.012416 | 0.00031197 | 0.037465 | -0.012984 | -0.0086987 | 0.014971 | -0.027466 | 0.15106 | -0.24719 | 0.022888 | 0.064087 | 0.09613 | -0.086975 | 0.20142 | 0.16937 | -0.22888 | 122.4243 | -0.004578 | 122.644 | 122.6944 | -0.091553 | 122.4426 | 0.013733 | 0.21973 | 122.5845 | 122.8729 | 122.7356 | 122.8226 | 122.644 | 122.8409 | 122.7676 | 122.4426 | 122.8226 | 122.644 | 122.7676 | 122.7356 | 122.8409 | -0.40283 | -0.38452
2029.8906 | 122.9828 | -122.7127 | 0.17395 | 0.12291 | 0.013911 | 0.003089 | 0.038747 | -0.014266 | -0.0097669 | 0.016466 | -0.004578 | 0.14191 | -0.22888 | 0.032043 | 0.068665 | 0.10071 | -0.13733 | 0.20142 | 0.1831 | -0.21973 | 122.4838 | -0.032043 | 122.7081 | 122.7448 | -0.10528 | 122.493 | 0.009155 | 0.2243 | 122.5754 | 122.9141 | 122.7814 | 122.8546 | 122.7081 | 122.8958 | 122.8134 | 122.493 | 122.8546 | 122.7081 | 122.8134 | 122.7814 | 122.8958 | -0.40283 | -0.39368
2031.5781 | 123.0469 | -122.7036 | 0.16937 | -0.21278 | 0.014979 | 0.003089 | 0.045797 | -0.014907 | -0.0095531 | 0.014544 | -0.073242 | 0.16479 | -0.28839 | -0.009155 | 0.009155 | 0.013733 | 0.054932 | 0.1236 | 0.21515 | -0.25635 | 122.4152 | -0.004578 | 122.6303 | 122.6944 | -0.16022 | 122.4472 | 0.045776 | 0.21515 | 122.7585 | 122.8271 | 122.7127 | 122.8683 | 122.6303 | 122.9187 | 122.7173 | 122.4472 | 122.8683 | 122.6303 | 122.7173 | 122.7127 | 122.9187 | -0.45776 | -0.42572
2033.2656 | 123.0331 | -122.7081 | 0.16479 | -0.20515 | 0.014766 | -0.00032903 | 0.043233 | -0.014907 | -0.0082715 | 0.015398 | 0.018311 | 0.11902 | -0.2655 | 0.064087 | 0.10071 | 0.11902 | -0.054932 | 0.23346 | 0.19226 | -0.21973 | 122.4426 | -0.045776 | 122.7264 | 122.7722 | -0.064087 | 122.4884 | 0.027466 | 0.28381 | 122.6532 | 122.9416 | 122.8088 | 122.8271 | 122.7264 | 122.9004 | 122.8271 | 122.4884 | 122.8271 | 122.7264 | 122.8271 | 122.8088 | 122.9004 | -0.4303 | -0.38452
2035 | 122.9874 | -122.699 | 0.1831 | 0.1458 | 0.015407 | 0.0018072 | 0.039815 | -0.01277 | -0.0095531 | 0.01668 | 0.004578 | 0.1236 | -0.24261 | 0.054932 | 0.059509 | 0.10986 | -0.1236 | 0.19226 | 0.1831 | -0.21973 | 122.4564 | -0.059509 | 122.7036 | 122.7539 | -0.1236 | 122.4792 | 0 | 0.24719 | 122.5754 | 122.8912 | 122.7585 | 122.8226 | 122.7036 | 122.8821 | 122.8088 | 122.4792 | 122.8226 | 122.7036 | 122.8088 | 122.7585 | 122.8821 | -0.42572 | -0.40283
2036.6875 | 122.9874 | -122.7036 | 0.17853 | 0.15343 | 0.017116 | -0.00054263 | 0.046224 | -0.013411 | -0.010621 | 0.016039 | -0.073242 | 0.16479 | -0.28839 | -0.027466 | -0.013733 | 0.004578 | 0.009155 | 0.07782 | 0.21515 | -0.25635 | 122.4152 | -0.013733 | 122.6303 | 122.6761 | -0.19226 | 122.4472 | 0.036621 | 0.21515 | 122.7127 | 122.7814 | 122.6898 | 122.8683 | 122.6303 | 122.9187 | 122.7081 | 122.4472 | 122.8683 | 122.6303 | 122.7081 | 122.6898 | 122.9187 | -0.46692 | -0.43488
2038.375 | 122.9507 | -122.7356 | 0.18768 | -0.10597 | 0.012843 | 0.003089 | 0.045583 | -0.011916 | -0.0097669 | 0.016253 | -0.009155 | 0.14648 | -0.28381 | 0.045776 | 0.041199 | 0.068665 | -0.022888 | 0.17395 | 0.19226 | -0.24719 | 122.4518 | -0.041199 | 122.7264 | 122.7814 | -0.14648 | 122.4884 | 0.004578 | 0.27466 | 122.7127 | 122.9095 | 122.7768 | 122.8821 | 122.7264 | 122.9279 | 122.8043 | 122.4884 | 122.8821 | 122.7264 | 122.8043 | 122.7768 | 122.9279 | -0.4715 | -0.43488
2040.0781 | 123.0606 | -122.6761 | 0.16479 | -0.23567 | 0.016047 | -0.00032903 | 0.042165 | -0.014479 | -0.0097669 | 0.014544 | -0.086975 | 0.16937 | -0.28381 | -0.041199 | 0 | 0.018311 | 0.073242 | 0.12817 | 0.23804 | -0.25635 | 122.3923 | 0.004578 | 122.5891 | 122.6349 | -0.16479 | 122.4197 | 0.073242 | 0.19684 | 122.7493 | 122.8043 | 122.6761 | 122.8455 | 122.5891 | 122.9141 | 122.6944 | 122.4197 | 122.8455 | 122.5891 | 122.6944 | 122.6761 | 122.9141 | -0.44861 | -0.42114
2041.7812 | 122.9874 | -122.731 | 0.16937 | 0.1458 | 0.014338 | 0.0011664 | 0.044515 | -0.011916 | -0.0084851 | 0.015398 | -0.068665 | 0.15564 | -0.27924 | -0.036621 | -0.009155 | 0.018311 | -0.013733 | 0.10529 | 0.23346 | -0.24261 | 122.4518 | -0.013733 | 122.6624 | 122.6944 | -0.17853 | 122.4884 | 0.064086 | 0.21057 | 122.7173 | 122.8363 | 122.7219 | 122.8867 | 122.6624 | 122.9645 | 122.7493 | 122.4884 | 122.8867 | 122.6624 | 122.7493 | 122.7219 | 122.9645 | -0.44861 | -0.41199
2043.4688 | 122.9782 | -122.7356 | 0.16479 | 0.054245 | 0.014552 | 0.0015936 | 0.043874 | -0.011275 | -0.010194 | 0.016039 | -0.050354 | 0.17395 | -0.29297 | -0.036621 | -0.009155 | 0.009155 | 0.022888 | 0.10071 | 0.2243 | -0.24261 | 122.4426 | 0.009155 | 122.6852 | 122.699 | -0.17395 | 122.493 | 0.059509 | 0.24261 | 122.7585 | 122.8363 | 122.7264 | 122.9095 | 122.6852 | 122.9599 | 122.7448 | 122.493 | 122.9095 | 122.6852 | 122.7448 | 122.7264 | 122.9599 | -0.45776 | -0.40741
2045.1562 | 123.0652 | -122.6715 | 0.15106 | -0.22804 | 0.014125 | 0.0052252 | 0.039601 | -0.014266 | -0.0091259 | 0.017107 | -0.073242 | 0.15564 | -0.27924 | -0.032043 | 0.027466 | 0.022888 | 0.054932 | 0.14191 | 0.2243 | -0.25635 | 122.3923 | 0.004578 | 122.5983 | 122.6395 | -0.1236 | 122.4152 | 0.073242 | 0.20599 | 122.7264 | 122.8134 | 122.699 | 122.8271 | 122.5983 | 122.8958 | 122.6944 | 122.4152 | 122.8271 | 122.5983 | 122.6944 | 122.699 | 122.8958 | -0.4303 | -0.40741
2046.8438 | 122.937 | -122.7448 | 0.17853 | -0.044937 | 0.014338 | 0.004798 | 0.046437 | -0.0097796 | -0.011903 | 0.01668 | -0.018311 | 0.15564 | -0.2655 | -0.004578 | 0.009155 | 0.050354 | 0.013733 | 0.13275 | 0.21515 | -0.25177 | 122.4792 | -0.022888 | 122.7264 | 122.7402 | -0.16937 | 122.493 | 0.036621 | 0.24719 | 122.7585 | 122.8775 | 122.7539 | 122.9004 | 122.7264 | 122.9599 | 122.7951 | 122.493 | 122.9004 | 122.7264 | 122.7951 | 122.7539 | 122.9599 | -0.44403 | -0.4303
2048.5781 | 122.9233 | -122.7356 | 0.18768 | -0.075455 | 0.014979 | 0.00073917 | 0.042379 | -0.014052 | -0.011476 | 0.017321 | -0.032043 | 0.14648 | -0.27466 | 0.036621 | 0.059509 | 0.068665 | -0.013733 | 0.1831 | 0.21057 | -0.24261 | 122.4609 | -0.041199 | 122.7036 | 122.7722 | -0.12817 | 122.493 | 0.022888 | 0.24262 | 122.7219 | 122.9187 | 122.7951 | 122.8821 | 122.7036 | 122.9462 | 122.8043 | 122.493 | 122.8821 | 122.7036 | 122.8043 | 122.7951 | 122.9462 | -0.46234 | -0.4303
2050.2656 | 123.056 | -122.6944 | 0.19226 | -0.29671 | 0.013698 | 0.00031197 | 0.040029 | -0.014479 | -0.010408 | 0.016466 | -0.022888 | 0.13275 | -0.24719 | -0.004578 | 0.041199 | 0.054932 | 0.022888 | 0.16022 | 0.19226 | -0.25177 | 122.4472 | -0.05951 | 122.6715 | 122.6898 | -0.15106 | 122.4426 | 0 | 0.2243 | 122.7173 | 122.8546 | 122.7356 | 122.8271 | 122.6715 | 122.8867 | 122.7493 | 122.4426 | 122.8271 | 122.6715 | 122.7493 | 122.7356 | 122.8867 | -0.43945 | -0.44403
2051.9844 | 122.937 | -122.731 | 0.17395 | 0.13054 | 0.011561 | 0.00073917 | 0.038533 | -0.011275 | -0.0078443 | 0.015184 | 0.032043 | 0.11444 | -0.24261 | 0.064087 | 0.10529 | 0.15564 | -0.15564 | 0.24719 | 0.17853 | -0.21515 | 122.4884 | -0.059509 | 122.7631 | 122.7951 | -0.068664 | 122.5159 | 0.004578 | 0.27466 | 122.5754 | 122.9782 | 122.8363 | 122.8455 | 122.7631 | 122.9095 | 122.8867 | 122.5159 | 122.8455 | 122.7631 | 122.8867 | 122.8363 | 122.9095 | -0.41656 | -0.3891
2053.6719 | 122.9691 | -122.7264 | 0.1831 | 0.13054 | 0.014125 | -0.0016106 | 0.042806 | -0.011061 | -0.0091259 | 0.016253 | -0.050354 | 0.14648 | -0.27924 | -0.009155 | 0 | 0.050354 | -0.054932 | 0.12817 | 0.21057 | -0.25177 | 122.4472 | -0.036621 | 122.6761 | 122.7173 | -0.1831 | 122.4747 | 0.027466 | 0.22888 | 122.6715 | 122.8546 | 122.7264 | 122.8729 | 122.6761 | 122.937 | 122.7768 | 122.4747 | 122.8729 | 122.6761 | 122.7768 | 122.7264 | 122.937 | -0.46234 | -0.43488
2055.3594 | 122.9279 | -122.7127 | 0.17395 | -0.052567 | 0.01327 | -0.0028924 | 0.046224 | -0.01213 | -0.011476 | 0.015612 | -0.027466 | 0.15564 | -0.28381 | 0.018311 | 0.032043 | 0.045776 | -0.027466 | 0.15564 | 0.21057 | -0.24719 | 122.4289 | -0.01831 | 122.6852 | 122.731 | -0.14191 | 122.4655 | 0.036621 | 0.25635 | 122.6852 | 122.8683 | 122.7448 | 122.8683 | 122.6852 | 122.9233 | 122.7585 | 122.4655 | 122.8683 | 122.6852 | 122.7585 | 122.7448 | 122.9233 | -0.45776 | -0.42114
2057.0781 | 122.9736 | -122.7356 | 0.17395 | 0.054245 | 0.017756 | 0.003089 | 0.045583 | -0.011916 | -0.010194 | 0.015612 | -0.073242 | 0.16937 | -0.28839 | -0.045776 | -0.013733 | 0 | 0.032043 | 0.086975 | 0.21515 | -0.24261 | 122.4472 | -0.004577 | 122.6624 | 122.6898 | -0.18768 | 122.493 | 0.041199 | 0.21515 | 122.7676 | 122.8226 | 122.7219 | 122.905 | 122.6624 | 122.9507 | 122.7356 | 122.493 | 122.905 | 122.6624 | 122.7356 | 122.7219 | 122.9507 | -0.46234 | -0.41656
2058.7656 | 123.0698 | -122.6898 | 0.16479 | -0.25856 | 0.013911 | 9.8166e-05 | 0.041738 | -0.015334 | -0.0089123 | 0.01433 | -0.082397 | 0.16022 | -0.27466 | -0.036621 | 0.009155 | 0.009155 | 0.064087 | 0.13275 | 0.23346 | -0.2655 | 122.4152 | -0.004578 | 122.6074 | 122.6532 | -0.15564 | 122.4243 | 0.068664 | 0.19226 | 122.7539 | 122.8226 | 122.699 | 122.85 | 122.6074 | 122.9233 | 122.699 | 122.4243 | 122.85 | 122.6074 | 122.699 | 122.699 | 122.9233 | -0.43945 | -0.4303
2060.4688 | 122.937 | -122.7402 | 0.18768 | -0.098343 | 0.014552 | -0.00054263 | 0.044515 | -0.013198 | -0.01233 | 0.015825 | -0.009155 | 0.15564 | -0.28381 | 0.027466 | 0.041199 | 0.068665 | -0.013733 | 0.17853 | 0.20599 | -0.23804 | 122.4564 | -0.032043 | 122.731 | 122.7676 | -0.14648 | 122.5021 | 0.018311 | 0.27466 | 122.7264 | 122.9187 | 122.7814 | 122.8958 | 122.731 | 122.9462 | 122.8088 | 122.5021 | 122.8958 | 122.731 | 122.8088 | 122.7814 | 122.9462 | -0.4715 | -0.42572
2062.1562 | 122.9324 | -122.7676 | 0.1831 | 0.19157 | 0.011989 | 0.0024482 | 0.040029 | -0.013839 | -0.010621 | 0.01668 | 0.041199 | 0.12817 | -0.21515 | 0.073242 | 0.10986 | 0.15564 | -0.16937 | 0.24719 | 0.16479 | -0.2243 | 122.5525 | -0.054931 | 122.8088 | 122.8409 | -0.073242 | 122.5433 | -0.01831 | 0.25635 | 122.5983 | 123.0148 | 122.8775 | 122.8958 | 122.8088 | 122.9324 | 122.9233 | 122.5433 | 122.8958 | 122.8088 | 122.9233 | 122.8775 | 122.9324 | -0.39825 | -0.40741
2063.8281 | 123.0698 | -122.6944 | 0.15106 | -0.25093 | 0.011989 | -0.002038 | 0.041951 | -0.01512 | -0.0089123 | 0.015825 | -0.068665 | 0.18768 | -0.29755 | -0.041199 | -0.009155 | 0.032043 | 0.059509 | 0.12817 | 0.21515 | -0.27466 | 122.3969 | 0.036621 | 122.6257 | 122.6532 | -0.16022 | 122.4197 | 0.064087 | 0.22888 | 122.7539 | 122.8226 | 122.6852 | 122.8821 | 122.6257 | 122.9095 | 122.7264 | 122.4197 | 122.8821 | 122.6257 | 122.7264 | 122.6852 | 122.9095 | -0.44861 | -0.42572
2065.5156 | 123.024 | -122.7081 | 0.15106 | -0.18227 | 0.01562 | 0.0043708 | 0.038533 | -0.013625 | -0.0091259 | 0.013689 | 0.027466 | 0.11444 | -0.23346 | 0.091553 | 0.10071 | 0.14191 | -0.10071 | 0.27008 | 0.17853 | -0.22888 | 122.4747 | -0.036621 | 122.7356 | 122.7997 | -0.050354 | 122.4792 | 0.027466 | 0.26093 | 122.6074 | 122.9782 | 122.8088 | 122.8226 | 122.7356 | 122.8867 | 122.85 | 122.4792 | 122.8226 | 122.7356 | 122.85 | 122.8088 | 122.8867 | -0.38452 | -0.37994
2067.1875 | 122.9462 | -122.7264 | 0.17853 | 0.16106 | 0.014552 | -0.00054263 | 0.040029 | -0.014479 | -0.0086987 | 0.016039 | 0.022888 | 0.10986 | -0.23346 | 0.082397 | 0.10986 | 0.14648 | -0.16022 | 0.23804 | 0.1831 | -0.21515 | 122.493 | -0.068665 | 122.7493 | 122.8088 | -0.068665 | 122.5113 | 0.004577 | 0.25635 | 122.5662 | 122.9645 | 122.8363 | 122.8363 | 122.7493 | 122.9095 | 122.8729 | 122.5113 | 122.8363 | 122.7493 | 122.8729 | 122.8363 | 122.9095 | -0.41199 | -0.39368
2068.9062 | 122.9736 | -122.731 | 0.17853 | 0.054245 | 0.014125 | -0.00011543 | 0.047292 | -0.013411 | -0.010194 | 0.017321 | -0.073242 | 0.17853 | -0.28381 | -0.059509 | -0.032043 | 0.004578 | 0.009155 | 0.091553 | 0.21973 | -0.25177 | 122.4472 | 0 | 122.6578 | 122.6715 | -0.21057 | 122.4792 | 0.041199 | 0.21057 | 122.7402 | 122.8226 | 122.699 | 122.9095 | 122.6578 | 122.9507 | 122.7356 | 122.4792 | 122.9095 | 122.6578 | 122.7356 | 122.699 | 122.9507 | -0.46234 | -0.4303
2070.5938 | 123.0652 | -122.7081 | 0.16022 | -0.17464 | 0.012843 | 0.0037298 | 0.043874 | -0.016188 | -0.011262 | 0.017748 | -0.064087 | 0.17853 | -0.29755 | -0.018311 | -0.009155 | 0.009155 | 0.050354 | 0.13733 | 0.21057 | -0.26093 | 122.4106 | 0.018311 | 122.644 | 122.6898 | -0.16937 | 122.4472 | 0.050354 | 0.23346 | 122.7585 | 122.8455 | 122.699 | 122.8867 | 122.644 | 122.9187 | 122.7173 | 122.4472 | 122.8867 | 122.644 | 122.7173 | 122.699 | 122.9187 | -0.45776 | -0.42114
2072.2812 | 123.0835 | -122.7127 | 0.15106 | -0.22041 | 0.014766 | 0.00073917 | 0.040242 | -0.014693 | -0.0093395 | 0.016039 | -0.064087 | 0.16022 | -0.27008 | -0.018311 | 0.032043 | 0.041199 | 0.036621 | 0.15106 | 0.22888 | -0.25635 | 122.4426 | 0.009155 | 122.6486 | 122.6944 | -0.11902 | 122.4564 | 0.07782 | 0.20599 | 122.7493 | 122.8638 | 122.7448 | 122.8729 | 122.6486 | 122.9416 | 122.7539 | 122.4564 | 122.8729 | 122.6486 | 122.7539 | 122.7448 | 122.9416 | -0.42114 | -0.40741
2074 | 122.9416 | -122.7448 | 0.20599 | -0.067826 | 0.015407 | 0.0037298 | 0.04601 | -0.011702 | -0.010621 | 0.015184 | 0 | 0.15106 | -0.27466 | 0.018311 | 0.036621 | 0.068665 | -0.027466 | 0.16022 | 0.21973 | -0.23804 | 122.4701 | -0.054932 | 122.7448 | 122.7631 | -0.16937 | 122.5067 | 0.013733 | 0.27466 | 122.7173 | 122.905 | 122.7814 | 122.8958 | 122.7448 | 122.9645 | 122.8134 | 122.5067 | 122.8958 | 122.7448 | 122.8134 | 122.7814 | 122.9645 | -0.48065 | -0.44403
2075.6875 | 123.0286 | -122.699 | 0.13733 | -0.15175 | 0.013911 | -0.0033196 | 0.037038 | -0.014266 | -0.0089123 | 0.01433 | 0.013733 | 0.13275 | -0.22888 | 0.064087 | 0.11444 | 0.16479 | -0.14191 | 0.27466 | 0.18768 | -0.21057 | 122.4701 | -0.004578 | 122.7127 | 122.7631 | -0.022888 | 122.4884 | 0.050354 | 0.24261 | 122.5571 | 122.9736 | 122.8134 | 122.8317 | 122.7127 | 122.8867 | 122.8638 | 122.4884 | 122.8317 | 122.7127 | 122.8638 | 122.8134 | 122.8867 | -0.36621 | -0.3479
2077.4375 | 123.024 | -122.6898 | 0.15106 | -0.098343 | 0.012629 | -0.001397 | 0.038961 | -0.013839 | -0.0095531 | 0.014971 | 0.009155 | 0.12817 | -0.24261 | 0.073242 | 0.10986 | 0.16022 | -0.11444 | 0.25177 | 0.19226 | -0.23804 | 122.4472 | -0.022888 | 122.699 | 122.7631 | -0.041199 | 122.4518 | 0.041199 | 0.25177 | 122.5754 | 122.9416 | 122.7997 | 122.818 | 122.699 | 122.8821 | 122.85 | 122.4518 | 122.818 | 122.699 | 122.85 | 122.7997 | 122.8821 | -0.39368 | -0.3891
2079.1875 | 123.0881 | -122.7173 | 0.15564 | -0.27382 | 0.014125 | 0.00073917 | 0.043019 | -0.014479 | -0.010408 | 0.015825 | -0.07782 | 0.16022 | -0.28839 | -0.018311 | -0.004578 | 0.009155 | 0.07782 | 0.13733 | 0.22888 | -0.24719 | 122.4289 | 0.004577 | 122.6395 | 122.699 | -0.16022 | 122.4701 | 0.073242 | 0.21057 | 122.7951 | 122.8546 | 122.7127 | 122.8775 | 122.6395 | 122.9462 | 122.7264 | 122.4701 | 122.8775 | 122.6395 | 122.7264 | 122.7127 | 122.9462 | -0.44403 | -0.40283
2080.9531 | 122.9828 | -122.7219 | 0.19226 | 0.10002 | 0.012202 | 0.0024482 | 0.045797 | -0.011916 | -0.011049 | 0.015612 | -0.059509 | 0.15106 | -0.28839 | -0.022888 | -0.032043 | 0.004578 | 0.018311 | 0.10529 | 0.21973 | -0.27466 | 122.4335 | -0.041199 | 122.6624 | 122.699 | -0.2243 | 122.4472 | 0.027466 | 0.22888 | 122.7402 | 122.8271 | 122.6898 | 122.8729 | 122.6624 | 122.9416 | 122.7264 | 122.4472 | 122.8729 | 122.6624 | 122.7264 | 122.6898 | 122.9416 | -0.48065 | -0.46692
2082.6406 | 123.056 | -122.7036 | 0.15106 | -0.27382 | 0.013911 | 0.0035162 | 0.041524 | -0.01512 | -0.011049 | 0.01433 | -0.082397 | 0.16937 | -0.27008 | -0.027466 | -0.013733 | 0.004578 | 0.068665 | 0.1236 | 0.2243 | -0.25635 | 122.4335 | 0.018311 | 122.6212 | 122.6761 | -0.16479 | 122.4472 | 0.073242 | 0.18768 | 122.7722 | 122.8271 | 122.6898 | 122.8729 | 122.6212 | 122.9279 | 122.7081 | 122.4472 | 122.8729 | 122.6212 | 122.7081 | 122.6898 | 122.9279 | -0.42114 | -0.40741
2084.3438 | 123.0377 | -122.7081 | 0.16479 | -0.17464 | 0.013911 | 0.0018072 | 0.037679 | -0.014052 | -0.0086987 | 0.016039 | 0.036621 | 0.13275 | -0.23804 | 0.064087 | 0.10529 | 0.12817 | -0.07782 | 0.24261 | 0.20142 | -0.2243 | 122.4701 | -0.032044 | 122.7448 | 122.7722 | -0.059509 | 122.4838 | 0.036621 | 0.27466 | 122.6303 | 122.9507 | 122.8134 | 122.8409 | 122.7448 | 122.9095 | 122.8363 | 122.4838 | 122.8409 | 122.7448 | 122.8363 | 122.8134 | 122.9095 | -0.40283 | -0.3891
2086.0938 | 122.9691 | -122.731 | 0.18768 | 0.18394 | 0.014552 | -0.003106 | 0.044088 | -0.013839 | -0.010835 | 0.014971 | -0.036621 | 0.15106 | -0.27466 | 0.004578 | 0.018311 | 0.068665 | -0.09613 | 0.13275 | 0.21515 | -0.21973 | 122.4564 | -0.036621 | 122.6944 | 122.7356 | -0.16937 | 122.5113 | 0.027466 | 0.23804 | 122.6349 | 122.8638 | 122.7493 | 122.8821 | 122.6944 | 122.9462 | 122.7997 | 122.5113 | 122.8821 | 122.6944 | 122.7997 | 122.7493 | 122.9462 | -0.46234 | -0.40741
2087.8594 | 122.9645 | -122.7448 | 0.20142 | -0.0067901 | 0.014552 | 0.0015936 | 0.045583 | -0.010634 | -0.011262 | 0.016893 | -0.027466 | 0.14648 | -0.27466 | 0.009155 | 0.018311 | 0.032043 | -0.004578 | 0.1236 | 0.21973 | -0.25177 | 122.4701 | -0.054932 | 122.7173 | 122.7539 | -0.18311 | 122.493 | 0.018311 | 0.24719 | 122.7402 | 122.8683 | 122.7631 | 122.8912 | 122.7173 | 122.9645 | 122.7768 | 122.493 | 122.8912 | 122.7173 | 122.7768 | 122.7631 | 122.9645 | -0.47607 | -0.45319
2089.5469 | 122.9462 | -122.7173 | 0.19684 | -0.083084 | 0.012843 | 0.00031197 | 0.045369 | -0.012343 | -0.011049 | 0.017748 | -0.009155 | 0.15564 | -0.2655 | 0.041199 | 0.041199 | 0.059509 | -0.022888 | 0.17853 | 0.20599 | -0.23804 | 122.4518 | -0.041198 | 122.7081 | 122.7585 | -0.15564 | 122.4792 | 0.009156 | 0.25635 | 122.6944 | 122.8958 | 122.7585 | 122.8729 | 122.7081 | 122.9233 | 122.7768 | 122.4792 | 122.8729 | 122.7081 | 122.7768 | 122.7585 | 122.9233 | -0.46234 | -0.43488
2091.25 | 122.9187 | -122.731 | 0.17853 | 0.16106 | 0.013057 | 0.002021 | 0.041738 | -0.011061 | -0.0093395 | 0.015184 | 0.022888 | 0.11902 | -0.23804 | 0.073242 | 0.10529 | 0.13733 | -0.18768 | 0.23346 | 0.1831 | -0.21057 | 122.493 | -0.059509 | 122.7539 | 122.8043 | -0.073242 | 122.5204 | 0.004577 | 0.26093 | 122.5433 | 122.9645 | 122.8363 | 122.85 | 122.7539 | 122.9141 | 122.8683 | 122.5204 | 122.85 | 122.7539 | 122.8683 | 122.8363 | 122.9141 | -0.41656 | -0.3891
2093.0156 | 122.9965 | -122.7081 | 0.17395 | 0.12291 | 0.015407 | 0.0018072 | 0.044942 | -0.013198 | -0.0099805 | 0.015184 | -0.073242 | 0.14648 | -0.27466 | -0.041199 | -0.018311 | 0.045776 | -0.013733 | 0.086975 | 0.2243 | -0.2655 | 122.4335 | -0.027466 | 122.6349 | 122.6669 | -0.19226 | 122.4426 | 0.050354 | 0.20142 | 122.6944 | 122.7951 | 122.6898 | 122.8546 | 122.6349 | 122.9324 | 122.7539 | 122.4426 | 122.8546 | 122.6349 | 122.7539 | 122.6898 | 122.9324 | -0.44861 | -0.43945
2094.7031 | 123.056 | -122.6944 | 0.15106 | -0.28145 | 0.01562 | -0.0028924 | 0.042379 | -0.014693 | -0.0069897 | 0.01668 | -0.091553 | 0.17853 | -0.28381 | -0.036621 | 0.004578 | 0.009155 | 0.073242 | 0.12817 | 0.23346 | -0.2655 | 122.4106 | 0.027466 | 122.6028 | 122.6578 | -0.14648 | 122.4289 | 0.082397 | 0.19226 | 122.7676 | 122.8226 | 122.699 | 122.8729 | 122.6028 | 122.9279 | 122.7036 | 122.4289 | 122.8729 | 122.6028 | 122.7036 | 122.699 | 122.9279 | -0.43488 | -0.41656
2096.4062 | 122.9691 | -122.7402 | 0.1831 | 0.17632 | 0.013698 | 0.00031197 | 0.037892 | -0.013839 | -0.0082715 | 0.016039 | 0.022888 | 0.11902 | -0.25177 | 0.041199 | 0.073242 | 0.12817 | -0.12817 | 0.21515 | 0.19226 | -0.21515 | 122.4884 | -0.064086 | 122.7631 | 122.7814 | -0.10986 | 122.525 | 0.009156 | 0.27466 | 122.612 | 122.9553 | 122.8134 | 122.8592 | 122.7631 | 122.9324 | 122.8683 | 122.525 | 122.8592 | 122.7631 | 122.8683 | 122.8134 | 122.9324 | -0.43488 | -0.39825
2098.1562 | 123.024 | -122.7173 | 0.15564 | -0.19753 | 0.014552 | 0.0054388 | 0.04067 | -0.014907 | -0.0063489 | 0.013475 | 0.054932 | 0.13733 | -0.23804 | 0.091553 | 0.11902 | 0.15564 | -0.11444 | 0.28839 | 0.16479 | -0.24261 | 122.4792 | -0.018311 | 122.7722 | 122.8088 | -0.036621 | 122.4747 | 0.009155 | 0.29297 | 122.6028 | 123.0057 | 122.8363 | 122.8546 | 122.7722 | 122.8821 | 122.8729 | 122.4747 | 122.8546 | 122.7722 | 122.8729 | 122.8363 | 122.8821 | -0.39368 | -0.39826
2099.9062 | 122.9645 | -122.7173 | 0.1831 | -0.12123 | 0.014125 | 0.00073917 | 0.046651 | -0.014693 | -0.011262 | 0.015184 | -0.018311 | 0.16022 | -0.30212 | 0.027466 | 0.041199 | 0.059509 | -0.018311 | 0.19226 | 0.20142 | -0.24261 | 122.4152 | -0.022888 | 122.699 | 122.7448 | -0.14191 | 122.4747 | 0.018311 | 0.28381 | 122.699 | 122.9095 | 122.7585 | 122.8775 | 122.699 | 122.9187 | 122.7768 | 122.4747 | 122.8775 | 122.699 | 122.7768 | 122.7585 | 122.9187 | -0.48523 | -0.42572
2101.5938 | 123.0652 | -122.7264 | 0.15106 | -0.18227 | 0.013698 | 0.0011664 | 0.042592 | -0.015548 | -0.010408 | 0.013903 | -0.082397 | 0.16937 | -0.27466 | -0.018311 | 0.009155 | 0.022888 | 0.054932 | 0.14191 | 0.23346 | -0.26093 | 122.4518 | 0.018311 | 122.644 | 122.7081 | -0.14191 | 122.4655 | 0.082397 | 0.19226 | 122.7814 | 122.8683 | 122.7356 | 122.8958 | 122.644 | 122.9599 | 122.7493 | 122.4655 | 122.8958 | 122.644 | 122.7493 | 122.7356 | 122.9599 | -0.42572 | -0.41199
2103.2969 | 122.9233 | -122.7264 | 0.19226 | 0.18394 | 0.014979 | 0.0035162 | 0.041097 | -0.011275 | -0.010194 | 0.017748 | 0.041199 | 0.12817 | -0.23346 | 0.086975 | 0.09613 | 0.16022 | -0.17853 | 0.24719 | 0.16022 | -0.21973 | 122.493 | -0.064087 | 122.7676 | 122.8134 | -0.096131 | 122.5067 | -0.032044 | 0.27466 | 122.5479 | 122.9736 | 122.8226 | 122.8546 | 122.7676 | 122.8867 | 122.8867 | 122.5067 | 122.8546 | 122.7676 | 122.8867 | 122.8226 | 122.8867 | -0.42572 | -0.41199
2105.0469 | 123.0377 | -122.699 | 0.17395 | -0.16701 | 0.015834 | 0.0033026 | 0.042806 | -0.013198 | -0.0099805 | 0.015184 | -0.054932 | 0.16937 | -0.28381 | -0.004578 | 0.004578 | 0.032043 | 0.050354 | 0.15106 | 0.23346 | -0.25177 | 122.4152 | -0.004577 | 122.644 | 122.6944 | -0.16937 | 122.4472 | 0.059509 | 0.22888 | 122.7493 | 122.85 | 122.7036 | 122.8683 | 122.644 | 122.9324 | 122.731 | 122.4472 | 122.8683 | 122.644 | 122.731 | 122.7036 | 122.9324 | -0.45776 | -0.42572
2106.7969 | 123.0377 | -122.6761 | 0.15564 | -0.18227 | 0.016475 | 0.00095277 | 0.044728 | -0.014479 | -0.0099805 | 0.014116 | -0.050354 | 0.17395 | -0.28839 | 0 | 0.022888 | 0.022888 | 0.041199 | 0.14648 | 0.21973 | -0.25635 | 122.3877 | 0.01831 | 122.6257 | 122.6761 | -0.13275 | 122.4197 | 0.064087 | 0.23804 | 122.7173 | 122.8226 | 122.699 | 122.85 | 122.6257 | 122.8958 | 122.699 | 122.4197 | 122.85 | 122.6257 | 122.699 | 122.699 | 122.8958 | -0.44403 | -0.41199
2108.5 | 122.9507 | -122.731 | 0.18768 | 0.13817 | 0.013057 | -0.0046014 | 0.038961 | -0.012557 | -0.0099805 | 0.01668 | 0.022888 | 0.11902 | -0.23804 | 0.073242 | 0.10529 | 0.15106 | -0.16022 | 0.2243 | 0.18768 | -0.23346 | 122.493 | -0.068664 | 122.7539 | 122.8043 | -0.082397 | 122.4976 | 0 | 0.26093 | 122.5708 | 122.9553 | 122.8363 | 122.85 | 122.7539 | 122.9187 | 122.8821 | 122.4976 | 122.85 | 122.7539 | 122.8821 | 122.8363 | 122.9187 | -0.42572 | -0.42114
2110.1875 | 123.0698 | -122.7081 | 0.16022 | -0.22804 | 0.013057 | -0.00032903 | 0.039815 | -0.014693 | -0.0091259 | 0.01668 | -0.068665 | 0.15106 | -0.29297 | -0.027466 | 0.009155 | 0.036621 | 0.045776 | 0.14191 | 0.2243 | -0.25177 | 122.4152 | -0.009155 | 122.6395 | 122.6807 | -0.15106 | 122.4564 | 0.064087 | 0.2243 | 122.7539 | 122.85 | 122.7173 | 122.8592 | 122.6395 | 122.9324 | 122.7448 | 122.4564 | 122.8592 | 122.6395 | 122.7448 | 122.7173 | 122.9324 | -0.45319 | -0.41199
2111.9531 | 123.024 | -122.731 | 0.14191 | -0.12123 | 0.014125 | 0.0035162 | 0.037892 | -0.016402 | -0.0097669 | 0.01433 | 0.032043 | 0.12817 | -0.24719 | 0.09613 | 0.14191 | 0.17853 | -0.14191 | 0.30212 | 0.1831 | -0.22888 | 122.4838 | -0.013733 | 122.7631 | 122.8271 | 0 | 122.5021 | 0.041198 | 0.27924 | 122.5891 | 123.0331 | 122.8729 | 122.8592 | 122.7631 | 122.9141 | 122.9095 | 122.5021 | 122.8592 | 122.7631 | 122.9095 | 122.8729 | 122.9141 | -0.3891 | -0.37079
2113.7031 | 123.0606 | -122.6944 | 0.15106 | -0.01442 | 0.014552 | -0.0033196 | 0.039601 | -0.015548 | -0.0065625 | 0.017107 | -0.032043 | 0.13275 | -0.24261 | 0.009155 | 0.045776 | 0.10071 | -0.09613 | 0.18768 | 0.1831 | -0.23346 | 122.4518 | -0.018311 | 122.6624 | 122.7036 | -0.10529 | 122.4609 | 0.032043 | 0.21057 | 122.5983 | 122.8821 | 122.7402 | 122.8271 | 122.6624 | 122.8775 | 122.7951 | 122.4609 | 122.8271 | 122.6624 | 122.7951 | 122.7402 | 122.8775 | -0.39368 | -0.38452
2115.3906 | 122.9416 | -122.7448 | 0.19226 | -0.083084 | 0.014766 | 0.0043708 | 0.047506 | -0.014479 | -0.010194 | 0.014116 | 0.004578 | 0.14648 | -0.28381 | 0.041199 | 0.036621 | 0.050354 | -0.032043 | 0.17395 | 0.21057 | -0.23346 | 122.4609 | -0.045777 | 122.7493 | 122.7859 | -0.15564 | 122.5113 | 0.01831 | 0.28839 | 122.7127 | 122.9187 | 122.7814 | 122.8912 | 122.7493 | 122.9553 | 122.7951 | 122.5113 | 122.8912 | 122.7493 | 122.7951 | 122.7814 | 122.9553 | -0.47607 | -0.42572
2117.1562 | 122.9462 | -122.7493 | 0.20142 | -0.090714 | 0.014125 | -0.004815 | 0.045583 | -0.013625 | -0.014253 | 0.015825 | -0.013733 | 0.15564 | -0.29297 | 0.041199 | 0.036621 | 0.068665 | -0.009155 | 0.17395 | 0.22888 | -0.23346 | 122.4564 | -0.045776 | 122.7356 | 122.7905 | -0.1648 | 122.5159 | 0.027466 | 0.27924 | 122.7402 | 122.9233 | 122.7859 | 122.905 | 122.7356 | 122.9782 | 122.818 | 122.5159 | 122.905 | 122.7356 | 122.818 | 122.7859 | 122.9782 | -0.49438 | -0.43488
2118.9062 | 123.0789 | -122.7127 | 0.15106 | -0.21278 | 0.01562 | -0.0022516 | 0.040883 | -0.01512 | -0.0082715 | 0.015398 | -0.064087 | 0.16937 | -0.28381 | -0.027466 | 0 | 0.022888 | 0.068665 | 0.14648 | 0.24261 | -0.28381 | 122.4289 | 0.018311 | 122.6486 | 122.6852 | -0.15106 | 122.4289 | 0.091553 | 0.21973 | 122.7814 | 122.8592 | 122.7127 | 122.8821 | 122.6486 | 122.9553 | 122.7356 | 122.4289 | 122.8821 | 122.6486 | 122.7356 | 122.7127 | 122.9553 | -0.43488 | -0.43488
2120.5938 | 123.0377 | -122.699 | 0.15564 | -0.1899 | 0.014552 | -0.00096983 | 0.038961 | -0.014052 | -0.0086987 | 0.013689 | 0.009155 | 0.13275 | -0.23804 | 0.082397 | 0.10071 | 0.1236 | -0.050354 | 0.24261 | 0.19226 | -0.22888 | 122.4609 | -0.022889 | 122.7081 | 122.7814 | -0.054932 | 122.4701 | 0.036621 | 0.24719 | 122.6486 | 122.9416 | 122.7997 | 122.8317 | 122.7081 | 122.8912 | 122.8226 | 122.4701 | 122.8317 | 122.7081 | 122.8226 | 122.7997 | 122.8912 | -0.39368 | -0.38452
2122.2812 | 122.937 | -122.7493 | 0.19684 | 0.22209 | 0.014766 | 0.0028754 | 0.042806 | -0.012984 | -0.011903 | 0.013689 | -0.022888 | 0.14648 | -0.27008 | 0.022888 | 0.036621 | 0.091553 | -0.11444 | 0.16937 | 0.21515 | -0.21973 | 122.4792 | -0.050354 | 122.7264 | 122.7722 | -0.16022 | 122.5296 | 0.018311 | 0.24719 | 122.6349 | 122.9187 | 122.7859 | 122.8958 | 122.7264 | 122.9645 | 122.8409 | 122.5296 | 122.8958 | 122.7264 | 122.8409 | 122.7859 | 122.9645 | -0.46692 | -0.41657
2123.9688 | 122.9736 | -122.7219 | 0.15564 | 0.16106 | 0.013911 | -0.00032903 | 0.038747 | -0.01512 | -0.010408 | 0.016466 | 0.009155 | 0.1236 | -0.23804 | 0.045776 | 0.073242 | 0.11902 | -0.1236 | 0.19684 | 0.16937 | -0.2243 | 122.4838 | -0.032044 | 122.731 | 122.7676 | -0.082398 | 122.4976 | 0.013733 | 0.24719 | 122.5983 | 122.9187 | 122.7951 | 122.8455 | 122.731 | 122.8912 | 122.8409 | 122.4976 | 122.8455 | 122.731 | 122.8409 | 122.7951 | 122.8912 | -0.39368 | -0.37994
2125.7188 | 122.9416 | -122.7448 | 0.20142 | 0.15343 | 0.015407 | 0.0018072 | 0.04131 | -0.014907 | -0.0082715 | 0.015612 | 0.036621 | 0.1236 | -0.24261 | 0.073242 | 0.10529 | 0.14648 | -0.17395 | 0.22888 | 0.17395 | -0.21057 | 122.5021 | -0.07782 | 122.7814 | 122.818 | -0.09613 | 122.5342 | -0.027466 | 0.27924 | 122.5708 | 122.9736 | 122.85 | 122.8683 | 122.7814 | 122.9187 | 122.8912 | 122.5342 | 122.8683 | 122.7814 | 122.8912 | 122.85 | 122.9187 | -0.44403 | -0.41199
2127.4062 | 123.0606 | -122.7173 | 0.16479 | -0.15175 | 0.014552 | -0.001397 | 0.044088 | -0.015761 | -0.011476 | 0.014757 | -0.064087 | 0.17395 | -0.27466 | -0.018311 | 0.018311 | 0.032043 | 0.050354 | 0.14648 | 0.22888 | -0.25635 | 122.4426 | 0.009155 | 122.6532 | 122.699 | -0.14648 | 122.4609 | 0.064087 | 0.21057 | 122.7676 | 122.8638 | 122.7356 | 122.8912 | 122.6532 | 122.9462 | 122.7493 | 122.4609 | 122.8912 | 122.6532 | 122.7493 | 122.7356 | 122.9462 | -0.43945 | -0.42114
2129.1562 | 123.0286 | -122.7448 | 0.15106 | -0.13649 | 0.016047 | -0.001397 | 0.037252 | -0.014266 | -0.0065625 | 0.014757 | 0.009155 | 0.14191 | -0.24719 | 0.086975 | 0.12817 | 0.16022 | -0.14191 | 0.27008 | 0.17853 | -0.2243 | 122.4976 | -0.009155 | 122.7539 | 122.8317 | -0.022888 | 122.5204 | 0.027466 | 0.25635 | 122.6028 | 123.0148 | 122.8729 | 122.8867 | 122.7539 | 122.9233 | 122.905 | 122.5204 | 122.8867 | 122.7539 | 122.905 | 122.8729 | 122.9233 | -0.39825 | -0.37537
2130.9062 | 123.0286 | -122.7036 | 0.15564 | -0.12886 | 0.013484 | 0.00138 | 0.038747 | -0.015975 | -0.0089123 | 0.012621 | 0.022888 | 0.13275 | -0.25177 | 0.082397 | 0.11444 | 0.16022 | -0.14191 | 0.27924 | 0.19226 | -0.21515 | 122.4518 | -0.022889 | 122.7264 | 122.7859 | -0.041199 | 122.4884 | 0.036621 | 0.27466 | 122.5616 | 122.9828 | 122.818 | 122.8363 | 122.7264 | 122.8958 | 122.8638 | 122.4884 | 122.8363 | 122.7264 | 122.8638 | 122.818 | 122.8958 | -0.40741 | -0.37079
2132.6562 | 123.0743 | -122.6852 | 0.15564 | 0.00083945 | 0.013484 | 0.0015936 | 0.040456 | -0.013839 | -0.0089123 | 0.014971 | -0.022888 | 0.12817 | -0.24261 | 0.032043 | 0.082397 | 0.10986 | -0.10529 | 0.20142 | 0.20599 | -0.23804 | 122.4426 | -0.027466 | 122.6624 | 122.7173 | -0.073243 | 122.4472 | 0.050354 | 0.21973 | 122.58 | 122.8867 | 122.7676 | 122.8134 | 122.6624 | 122.8912 | 122.7951 | 122.4472 | 122.8134 | 122.6624 | 122.7951 | 122.7676 | 122.8912 | -0.39826 | -0.39368
2134.3438 | 123.0423 | -122.6807 | 0.16479 | 0.023727 | 0.013057 | 0.0039436 | 0.039601 | -0.012557 | -0.0095531 | 0.016466 | -0.022888 | 0.12817 | -0.24719 | 0.041199 | 0.036621 | 0.10071 | -0.10071 | 0.19684 | 0.19684 | -0.23804 | 122.4335 | -0.036621 | 122.6578 | 122.7219 | -0.12817 | 122.4426 | 0.032043 | 0.2243 | 122.58 | 122.8775 | 122.7173 | 122.8088 | 122.6578 | 122.8775 | 122.7814 | 122.4426 | 122.8088 | 122.6578 | 122.7814 | 122.7173 | 122.8775 | -0.41199 | -0.40283
2136.0938 | 122.9553 | -122.7722 | 0.19684 | -0.060196 | 0.016688 | -0.003106 | 0.049855 | -0.01277 | -0.01233 | 0.016039 | -0.004578 | 0.14648 | -0.29297 | 0.041199 | 0.032043 | 0.064087 | -0.036621 | 0.15564 | 0.21057 | -0.25177 | 122.4792 | -0.050354 | 122.7676 | 122.8134 | -0.1648 | 122.5204 | 0.013733 | 0.28839 | 122.7356 | 122.9279 | 122.8043 | 122.9187 | 122.7676 | 122.9828 | 122.8363 | 122.5204 | 122.9187 | 122.7676 | 122.8363 | 122.8043 | 122.9828 | -0.48981 | -0.44861
2137.8594 | 123.0606 | -122.699 | 0.15564 | 0.023727 | 0.013911 | -0.003106 | 0.041524 | -0.016188 | -0.010194 | 0.016466 | -0.036621 | 0.13275 | -0.2655 | 0.022888 | 0.059509 | 0.091553 | -0.082397 | 0.19226 | 0.21057 | -0.23346 | 122.4335 | -0.022889 | 122.6624 | 122.7219 | -0.096131 | 122.4655 | 0.054931 | 0.22888 | 122.6166 | 122.8912 | 122.7585 | 122.8317 | 122.6624 | 122.9095 | 122.7905 | 122.4655 | 122.8317 | 122.6624 | 122.7905 | 122.7585 | 122.9095 | -0.42114 | -0.3891
2139.5625 | 123.056 | -122.6898 | 0.15564 | 0.038986 | 0.013911 | 0.0035162 | 0.039174 | -0.016402 | -0.0095531 | 0.013475 | -0.013733 | 0.14191 | -0.23804 | 0.013733 | 0.064087 | 0.10529 | -0.10071 | 0.19226 | 0.19226 | -0.23804 | 122.4518 | -0.013733 | 122.6761 | 122.7036 | -0.091553 | 122.4518 | 0.036621 | 0.2243 | 122.5891 | 122.8821 | 122.7539 | 122.8317 | 122.6761 | 122.8821 | 122.7951 | 122.4518 | 122.8317 | 122.6761 | 122.7951 | 122.7539 | 122.8821 | -0.39368 | -0.39368
2141.2656 | 123.0789 | -122.731 | 0.14191 | -0.2433 | 0.012202 | -0.00032903 | 0.043874 | -0.017043 | -0.0089123 | 0.016039 | -0.027466 | 0.15106 | -0.25177 | 0.018311 | 0.032043 | 0.045776 | 0.018311 | 0.15564 | 0.21515 | -0.2655 | 122.4792 | 0.009155 | 122.7036 | 122.7493 | -0.10986 | 122.4655 | 0.073242 | 0.2243 | 122.7493 | 122.8867 | 122.7631 | 122.8821 | 122.7036 | 122.9462 | 122.7768 | 122.4655 | 122.8821 | 122.7036 | 122.7768 | 122.7631 | 122.9462 | -0.39368 | -0.40741
2143.0312 | 123.0469 | -122.7081 | 0.16479 | -0.17464 | 0.012202 | -0.0035332 | 0.041951 | -0.016188 | -0.011262 | 0.015825 | 0.022888 | 0.1236 | -0.26093 | 0.073242 | 0.10071 | 0.10986 | -0.059509 | 0.25177 | 0.21515 | -0.22888 | 122.4472 | -0.041199 | 122.731 | 122.7814 | -0.064087 | 122.4792 | 0.050354 | 0.28381 | 122.6486 | 122.9599 | 122.8088 | 122.8317 | 122.731 | 122.9233 | 122.818 | 122.4792 | 122.8317 | 122.731 | 122.818 | 122.8088 | 122.9233 | -0.42572 | -0.39368
2144.7812 | 123.0743 | -122.7036 | 0.15564 | 0.016098 | 0.012843 | -0.00011543 | 0.039174 | -0.015761 | -0.0076305 | 0.01433 | -0.032043 | 0.12817 | -0.24719 | 0.027466 | 0.068665 | 0.10071 | -0.086975 | 0.1831 | 0.20142 | -0.25177 | 122.4564 | -0.027466 | 122.6715 | 122.731 | -0.086975 | 122.4518 | 0.045776 | 0.21515 | 122.6166 | 122.8867 | 122.7722 | 122.8317 | 122.6715 | 122.905 | 122.8043 | 122.4518 | 122.8317 | 122.6715 | 122.8043 | 122.7722 | 122.905 | -0.40283 | -0.40741
2146.4688 | 123.024 | -122.7127 | 0.13733 | -0.10597 | 0.013484 | 0.00031197 | 0.039174 | -0.012557 | -0.0095531 | 0.014757 | 0.013733 | 0.14191 | -0.24719 | 0.091553 | 0.11902 | 0.14191 | -0.11902 | 0.27008 | 0.19684 | -0.23346 | 122.4655 | 0.004578 | 122.7264 | 122.8043 | -0.01831 | 122.4792 | 0.059509 | 0.26093 | 122.5937 | 122.9828 | 122.8317 | 122.8546 | 122.7264 | 122.9095 | 122.8546 | 122.4792 | 122.8546 | 122.7264 | 122.8546 | 122.8317 | 122.9095 | -0.38452 | -0.37079
2148.1719 | 122.9507 | -122.7539 | 0.19226 | -0.0067901 | 0.014979 | 0.00031197 | 0.048787 | -0.013625 | -0.013826 | 0.014544 | -0.009155 | 0.14648 | -0.2655 | 0.022888 | 0.018311 | 0.036621 | -0.022888 | 0.13275 | 0.24261 | -0.24261 | 122.4884 | -0.045777 | 122.7448 | 122.7768 | -0.17395 | 122.5113 | 0.050354 | 0.25635 | 122.731 | 122.8867 | 122.7722 | 122.9004 | 122.7448 | 122.9965 | 122.7905 | 122.5113 | 122.9004 | 122.7448 | 122.7905 | 122.7722 | 122.9965 | -0.45776 | -0.43488
2149.9219 | 123.024 | -122.7081 | 0.1831 | -0.15175 | 0.013484 | -0.0018244 | 0.040456 | -0.014052 | -0.0097669 | 0.015184 | 0.041199 | 0.14191 | -0.23804 | 0.10986 | 0.15564 | 0.16022 | -0.1236 | 0.28381 | 0.19226 | -0.2243 | 122.4701 | -0.041198 | 122.7493 | 122.818 | -0.027465 | 122.4838 | 0.009156 | 0.27924 | 122.5845 | 122.9919 | 122.8638 | 122.85 | 122.7493 | 122.9004 | 122.8683 | 122.4838 | 122.85 | 122.7493 | 122.8683 | 122.8638 | 122.9004 | -0.42114 | -0.40741
2151.6562 | 122.9828 | -122.7356 | 0.19684 | 0.092392 | 0.014552 | 0.00095277 | 0.04836 | -0.012343 | -0.013399 | 0.015184 | -0.032043 | 0.16022 | -0.28381 | -0.009155 | -0.004578 | 0.013733 | -0.013733 | 0.091553 | 0.21973 | -0.2655 | 122.4518 | -0.036621 | 122.7036 | 122.7264 | -0.20142 | 122.4701 | 0.022889 | 0.25177 | 122.7219 | 122.8271 | 122.731 | 122.8958 | 122.7036 | 122.9553 | 122.7493 | 122.4701 | 122.8958 | 122.7036 | 122.7493 | 122.731 | 122.9553 | -0.48065 | -0.46234
2153.4219 | 122.9782 | -122.7402 | 0.20142 | 0.061874 | 0.016047 | -0.0026788 | 0.045797 | -0.013198 | -0.010408 | 0.016466 | -0.032043 | 0.16479 | -0.26093 | -0.022888 | -0.013733 | 0.004578 | 0.009155 | 0.11444 | 0.23346 | -0.25177 | 122.4792 | -0.036621 | 122.7081 | 122.7173 | -0.21515 | 122.4884 | 0.032043 | 0.22888 | 122.7493 | 122.8546 | 122.7264 | 122.905 | 122.7081 | 122.9736 | 122.7448 | 122.4884 | 122.905 | 122.7081 | 122.7448 | 122.7264 | 122.9736 | -0.46234 | -0.45319
2155.1094 | 122.9736 | -122.7173 | 0.16022 | -0.12123 | 0.01562 | 0.0056524 | 0.044088 | -0.013411 | -0.010194 | 0.015612 | -0.013733 | 0.16022 | -0.29297 | 0.022888 | 0.045776 | 0.059509 | -0.013733 | 0.17853 | 0.2243 | -0.25177 | 122.4243 | 0 | 122.7036 | 122.7402 | -0.11444 | 122.4655 | 0.064087 | 0.27924 | 122.7036 | 122.8958 | 122.7631 | 122.8775 | 122.7036 | 122.9416 | 122.7768 | 122.4655 | 122.8775 | 122.7036 | 122.7768 | 122.7631 | 122.9416 | -0.45319 | -0.41199
2156.8594 | 123.0423 | -122.6944 | 0.14191 | -0.075455 | 0.01327 | -0.00011543 | 0.037679 | -0.014479 | -0.0095531 | 0.016893 | 0.004578 | 0.12817 | -0.23804 | 0.068665 | 0.12817 | 0.15564 | -0.11902 | 0.27466 | 0.20142 | -0.23804 | 122.4564 | -0.013733 | 122.699 | 122.7631 | -0.013733 | 122.4564 | 0.059509 | 0.24261 | 122.5754 | 122.9691 | 122.8226 | 122.8226 | 122.699 | 122.8958 | 122.85 | 122.4564 | 122.8226 | 122.699 | 122.85 | 122.8226 | 122.8958 | -0.37994 | -0.37994
2158.5625 | 122.9553 | -122.7448 | 0.19226 | 0.13054 | 0.014552 | 0.0022346 | 0.041097 | -0.014693 | -0.0095531 | 0.01668 | 0.022888 | 0.12817 | -0.23804 | 0.07782 | 0.09613 | 0.14648 | -0.16479 | 0.2243 | 0.18768 | -0.21515 | 122.5067 | -0.064087 | 122.7676 | 122.8226 | -0.096131 | 122.5296 | -0.004578 | 0.26093 | 122.58 | 122.9691 | 122.8409 | 122.8729 | 122.7676 | 122.9324 | 122.8912 | 122.5296 | 122.8729 | 122.7676 | 122.8912 | 122.8409 | 122.9324 | -0.4303 | -0.40741
2160.25 | 122.9736 | -122.7356 | 0.17853 | 0.13817 | 0.014552 | 0.0018072 | 0.04131 | -0.01512 | -0.0089123 | 0.014971 | 0.022888 | 0.13275 | -0.27008 | 0.050354 | 0.073242 | 0.11902 | -0.13275 | 0.20599 | 0.17853 | -0.2243 | 122.4655 | -0.045777 | 122.7585 | 122.7859 | -0.10529 | 122.5113 | 0 | 0.29297 | 122.6028 | 122.9416 | 122.8088 | 122.8683 | 122.7585 | 122.9141 | 122.8546 | 122.5113 | 122.8683 | 122.7585 | 122.8546 | 122.8088 | 122.9141 | -0.44861 | -0.40283
2162 | 122.9736 | -122.7173 | 0.16937 | 0.12291 | 0.013484 | 0.002021 | 0.042379 | -0.012343 | -0.0086987 | 0.016466 | 0.027466 | 0.11902 | -0.24719 | 0.050354 | 0.086975 | 0.13275 | -0.16022 | 0.23346 | 0.17853 | -0.2243 | 122.4701 | -0.050354 | 122.7448 | 122.7676 | -0.082398 | 122.493 | 0.009155 | 0.27466 | 122.5571 | 122.9507 | 122.8043 | 122.8363 | 122.7448 | 122.8958 | 122.85 | 122.493 | 122.8363 | 122.7448 | 122.85 | 122.8043 | 122.8958 | -0.41656 | -0.39368
2163.75 | 122.9233 | -122.7448 | 0.17395 | 0.18394 | 0.014552 | 0.0050116 | 0.044728 | -0.013625 | -0.012117 | 0.015184 | 0.041199 | 0.1236 | -0.23346 | 0.09613 | 0.10986 | 0.16479 | -0.18768 | 0.25177 | 0.17395 | -0.21973 | 122.5113 | -0.050354 | 122.7859 | 122.8409 | -0.064087 | 122.525 | 0 | 0.27466 | 122.5571 | 122.9965 | 122.8546 | 122.8683 | 122.7859 | 122.9187 | 122.9095 | 122.525 | 122.8683 | 122.7859 | 122.9095 | 122.8546 | 122.9187 | -0.40741 | -0.39368
2165.4375 | 122.9691 | -122.7448 | 0.19226 | -0.029679 | 0.015193 | 0.0043708 | 0.046865 | -0.012984 | -0.010194 | 0.01433 | -0.027466 | 0.16937 | -0.29297 | 0.013733 | 0.013733 | 0.032043 | -0.009155 | 0.12817 | 0.23346 | -0.25177 | 122.4518 | -0.022888 | 122.7173 | 122.7585 | -0.17853 | 122.493 | 0.041198 | 0.2655 | 122.7356 | 122.8729 | 122.7585 | 122.9141 | 122.7173 | 122.9782 | 122.7768 | 122.493 | 122.9141 | 122.7173 | 122.7768 | 122.7585 | 122.9782 | -0.48523 | -0.44403
2167.125 | 123.0469 | -122.7081 | 0.15106 | -0.037308 | 0.012202 | -0.0050286 | 0.037892 | -0.014907 | -0.0095531 | 0.016253 | 0 | 0.12817 | -0.24261 | 0.068665 | 0.10986 | 0.14191 | -0.12817 | 0.27008 | 0.19226 | -0.2243 | 122.4655 | -0.022888 | 122.7081 | 122.7768 | -0.041199 | 122.4838 | 0.041199 | 0.24261 | 122.58 | 122.9782 | 122.818 | 122.8363 | 122.7081 | 122.9004 | 122.85 | 122.4838 | 122.8363 | 122.7081 | 122.85 | 122.818 | 122.9004 | -0.39368 | -0.37537
2168.8906 | 123.0377 | -122.7036 | 0.16479 | -0.083084 | 0.011989 | 0.0028754 | 0.038106 | -0.01512 | -0.0091259 | 0.013689 | 0.009155 | 0.13275 | -0.24719 | 0.082397 | 0.12817 | 0.15564 | -0.1236 | 0.27924 | 0.17853 | -0.2243 | 122.4564 | -0.032044 | 122.7127 | 122.7859 | -0.036621 | 122.4792 | 0.013733 | 0.25635 | 122.58 | 122.9828 | 122.8317 | 122.8363 | 122.7127 | 122.8821 | 122.8592 | 122.4792 | 122.8363 | 122.7127 | 122.8592 | 122.8317 | 122.8821 | -0.41199 | -0.3891
2170.6406 | 122.9507 | -122.7585 | 0.19684 | -0.083084 | 0.014979 | 0.0018072 | 0.047933 | -0.013198 | -0.011476 | 0.014757 | 0 | 0.16022 | -0.27466 | 0.059509 | 0.032043 | 0.068665 | -0.027466 | 0.1831 | 0.20599 | -0.23804 | 122.4838 | -0.036621 | 122.7585 | 122.818 | -0.1648 | 122.5204 | 0.009156 | 0.27466 | 122.731 | 122.9416 | 122.7905 | 122.9187 | 122.7585 | 122.9645 | 122.8271 | 122.5204 | 122.9187 | 122.7585 | 122.8271 | 122.7905 | 122.9645 | -0.4715 | -0.43488
2172.3281 | 122.9462 | -122.7539 | 0.19684 | -0.037308 | 0.013911 | 0.0022346 | 0.045156 | -0.012343 | -0.012117 | 0.015398 | -0.004578 | 0.15564 | -0.28839 | 0.032043 | 0.059509 | 0.068665 | -0.045776 | 0.1831 | 0.21973 | -0.24261 | 122.4655 | -0.041198 | 122.7493 | 122.7859 | -0.13733 | 122.5113 | 0.022889 | 0.28381 | 122.7081 | 122.937 | 122.8134 | 122.9095 | 122.7493 | 122.9736 | 122.8226 | 122.5113 | 122.9095 | 122.7493 | 122.8226 | 122.8134 | 122.9736 | -0.48523 | -0.43945
2174.0781 | 123.0652 | -122.699 | 0.14648 | 0.092392 | 0.014125 | -0.0028924 | 0.038747 | -0.013198 | -0.010408 | 0.01668 | -0.027466 | 0.13733 | -0.24719 | 0.018311 | 0.073242 | 0.10986 | -0.10986 | 0.20142 | 0.1831 | -0.24261 | 122.4518 | -0.009155 | 122.6715 | 122.7173 | -0.073242 | 122.4564 | 0.036621 | 0.21973 | 122.5891 | 122.9004 | 122.7722 | 122.8363 | 122.6715 | 122.8821 | 122.8088 | 122.4564 | 122.8363 | 122.6715 | 122.8088 | 122.7722 | 122.8821 | -0.39368 | -0.3891
2175.8281 | 122.9324 | -122.7356 | 0.1831 | 0.18394 | 0.014766 | 0.0015936 | 0.044515 | -0.013411 | -0.0089123 | 0.016466 | 0.036621 | 0.13275 | -0.2243 | 0.09613 | 0.11902 | 0.15106 | -0.19226 | 0.23804 | 0.19226 | -0.21973 | 122.5113 | -0.050354 | 122.7722 | 122.8317 | -0.064086 | 122.5159 | 0.009156 | 0.26093 | 122.5433 | 122.9736 | 122.8546 | 122.8683 | 122.7722 | 122.9279 | 122.8867 | 122.5159 | 122.8683 | 122.7722 | 122.8867 | 122.8546 | 122.9279 | -0.40741 | -0.40283
2177.5156 | 123.0515 | -122.699 | 0.15564 | -0.052567 | 0.013698 | 0.0069342 | 0.037465 | -0.01512 | -0.0089123 | 0.014544 | -0.009155 | 0.13733 | -0.24719 | 0.073242 | 0.091553 | 0.14191 | -0.11902 | 0.25635 | 0.17853 | -0.24719 | 122.4518 | -0.018311 | 122.6898 | 122.7722 | -0.064087 | 122.4518 | 0.022888 | 0.23804 | 122.58 | 122.9553 | 122.7905 | 122.8363 | 122.6898 | 122.8775 | 122.8409 | 122.4518 | 122.8363 | 122.6898 | 122.8409 | 122.7905 | 122.8775 | -0.40283 | -0.40283
2179.2031 | 123.0469 | -122.7264 | 0.17395 | -0.18227 | 0.011561 | 0.00095277 | 0.041097 | -0.016402 | -0.011262 | 0.015398 | 0.018311 | 0.12817 | -0.23804 | 0.082397 | 0.1236 | 0.14191 | -0.10529 | 0.27466 | 0.19226 | -0.23346 | 122.4884 | -0.045776 | 122.7448 | 122.8088 | -0.050354 | 122.493 | 0.018311 | 0.25635 | 122.6212 | 123.0011 | 122.85 | 122.8546 | 122.7448 | 122.9187 | 122.8683 | 122.493 | 122.8546 | 122.7448 | 122.8683 | 122.85 | 122.9187 | -0.41199 | -0.40741
2180.9531 | 123.0103 | -122.7173 | 0.16479 | 0.12291 | 0.015193 | -0.0033196 | 0.042165 | -0.015975 | -0.0080579 | 0.01433 | 0.004578 | 0.13275 | -0.2655 | 0.032043 | 0.064087 | 0.10986 | -0.11902 | 0.20599 | 0.19684 | -0.21515 | 122.4518 | -0.032044 | 122.7219 | 122.7493 | -0.10071 | 122.5021 | 0.032043 | 0.27008 | 122.5983 | 122.9233 | 122.7814 | 122.85 | 122.7219 | 122.9141 | 122.8271 | 122.5021 | 122.85 | 122.7219 | 122.8271 | 122.7814 | 122.9141 | -0.4303 | -0.37994
2182.7031 | 123.0652 | -122.7127 | 0.16022 | -0.17464 | 0.011561 | -0.00011543 | 0.043874 | -0.014266 | -0.0089123 | 0.014116 | -0.064087 | 0.16937 | -0.28839 | -0.009155 | 0.004578 | 0.027466 | 0.045776 | 0.13733 | 0.23804 | -0.26093 | 122.4243 | 0.009156 | 122.6486 | 122.7036 | -0.15564 | 122.4518 | 0.07782 | 0.2243 | 122.7585 | 122.85 | 122.7173 | 122.8821 | 122.6486 | 122.9507 | 122.7402 | 122.4518 | 122.8821 | 122.6486 | 122.7402 | 122.7173 | 122.9507 | -0.44861 | -0.42114
2184.4062 | 123.0469 | -122.7127 | 0.16022 | -0.15175 | 0.015193 | -0.00032903 | 0.038106 | -0.017043 | -0.0080579 | 0.016893 | 0.013733 | 0.13275 | -0.24261 | 0.10071 | 0.1236 | 0.16022 | -0.15106 | 0.27924 | 0.17853 | -0.22888 | 122.4701 | -0.027466 | 122.7264 | 122.8134 | -0.036621 | 122.4838 | 0.018311 | 0.25635 | 122.5616 | 122.9919 | 122.8363 | 122.8455 | 122.7264 | 122.8912 | 122.8729 | 122.4838 | 122.8455 | 122.7264 | 122.8729 | 122.8363 | 122.8912 | -0.40283 | -0.3891
2186.1562 | 122.9507 | -122.7356 | 0.17853 | -0.022049 | 0.015407 | -0.00054263 | 0.046437 | -0.017256 | -0.011476 | 0.01433 | -0.009155 | 0.17395 | -0.29297 | 0.032043 | 0.018311 | 0.045776 | -0.022888 | 0.13275 | 0.22888 | -0.24261 | 122.4426 | -0.004578 | 122.7264 | 122.7676 | -0.16022 | 122.493 | 0.050354 | 0.28381 | 122.7127 | 122.8683 | 122.7539 | 122.9095 | 122.7264 | 122.9645 | 122.7814 | 122.493 | 122.9095 | 122.7264 | 122.7814 | 122.7539 | 122.9645 | -0.4715 | -0.42114
2187.8438 | 122.9324 | -122.7585 | 0.20142 | -0.090714 | 0.015407 | -0.0022516 | 0.045797 | -0.013625 | -0.010408 | 0.014757 | 0.018311 | 0.16022 | -0.28839 | 0.041199 | 0.050354 | 0.068665 | -0.050354 | 0.1831 | 0.21973 | -0.2655 | 122.4701 | -0.041199 | 122.7768 | 122.7997 | -0.15106 | 122.493 | 0.018311 | 0.3067 | 122.7081 | 122.9416 | 122.8088 | 122.9187 | 122.7768 | 122.9782 | 122.8271 | 122.493 | 122.9187 | 122.7768 | 122.8271 | 122.8088 | 122.9782 | -0.48981 | -0.46692
2189.5312 | 122.9462 | -122.7539 | 0.1831 | 0.13817 | 0.014338 | 0.00052557 | 0.044515 | -0.012343 | -0.012117 | 0.017321 | 0.022888 | 0.12817 | -0.24719 | 0.073242 | 0.10986 | 0.15564 | -0.16937 | 0.23804 | 0.18768 | -0.21515 | 122.5067 | -0.054931 | 122.7768 | 122.8271 | -0.073242 | 122.5388 | 0.004578 | 0.27008 | 122.5845 | 122.9919 | 122.8638 | 122.8821 | 122.7768 | 122.9416 | 122.9095 | 122.5388 | 122.8821 | 122.7768 | 122.9095 | 122.8638 | 122.9416 | -0.4303 | -0.39825
2191.2812 | 122.9599 | -122.7493 | 0.17395 | -0.060196 | 0.013698 | 0.00095277 | 0.04601 | -0.013411 | -0.010194 | 0.017962 | -0.009155 | 0.16022 | -0.29297 | 0.032043 | 0.041199 | 0.064087 | -0.027466 | 0.15564 | 0.21057 | -0.2243 | 122.4564 | -0.013733 | 122.7402 | 122.7814 | -0.13275 | 122.525 | 0.036621 | 0.28381 | 122.7219 | 122.905 | 122.7905 | 122.9095 | 122.7402 | 122.9599 | 122.8134 | 122.525 | 122.9095 | 122.7402 | 122.8134 | 122.7905 | 122.9599 | -0.46692 | -0.39825
2193.0469 | 123.024 | -122.731 | 0.15106 | -0.21278 | 0.013057 | -0.00032903 | 0.038533 | -0.014052 | -0.0093395 | 0.017534 | 0.032043 | 0.12817 | -0.23346 | 0.091553 | 0.1236 | 0.15564 | -0.11902 | 0.27924 | 0.17853 | -0.21973 | 122.4976 | -0.022888 | 122.7631 | 122.8226 | -0.027466 | 122.5113 | 0.027466 | 0.2655 | 122.612 | 123.0103 | 122.8546 | 122.8592 | 122.7631 | 122.9095 | 122.8867 | 122.5113 | 122.8592 | 122.7631 | 122.8867 | 122.8546 | 122.9095 | -0.38452 | -0.37079
2194.7969 | 122.9416 | -122.7768 | 0.18768 | 0.19157 | 0.011561 | 0.0052252 | 0.041738 | -0.01213 | -0.0086987 | 0.012835 | 0.036621 | 0.11444 | -0.2243 | 0.07782 | 0.12817 | 0.14648 | -0.17853 | 0.26093 | 0.19226 | -0.21057 | 122.5525 | -0.073242 | 122.8134 | 122.8546 | -0.059509 | 122.5662 | 0.004578 | 0.26093 | 122.5983 | 123.0377 | 122.905 | 122.8912 | 122.8134 | 122.9691 | 122.9233 | 122.5662 | 122.8912 | 122.8134 | 122.9233 | 122.905 | 122.9691 | -0.41199 | -0.39825
2196.4844 | 122.9462 | -122.7631 | 0.16937 | 0.1458 | 0.01327 | -0.0022516 | 0.043019 | -0.012984 | -0.0084851 | 0.014971 | 0.045776 | 0.11444 | -0.24261 | 0.068665 | 0.10986 | 0.15564 | -0.17853 | 0.23346 | 0.19226 | -0.22888 | 122.5204 | -0.054932 | 122.8088 | 122.8317 | -0.05951 | 122.5342 | 0.022888 | 0.28839 | 122.5845 | 122.9965 | 122.8729 | 122.8775 | 122.8088 | 122.9553 | 122.9187 | 122.5342 | 122.8775 | 122.8088 | 122.9187 | 122.8729 | 122.9553 | -0.41199 | -0.39826
2198.2344 | 123.0789 | -122.7127 | 0.15564 | 0.046615 | 0.014979 | 0.00031197 | 0.039174 | -0.015761 | -0.0095531 | 0.015612 | -0.027466 | 0.12817 | -0.25177 | 0.022888 | 0.059509 | 0.086975 | -0.091553 | 0.19684 | 0.19226 | -0.22888 | 122.4609 | -0.027466 | 122.6852 | 122.7356 | -0.096131 | 122.4838 | 0.036621 | 0.2243 | 122.6212 | 122.9095 | 122.7722 | 122.8409 | 122.6852 | 122.905 | 122.7997 | 122.4838 | 122.8409 | 122.6852 | 122.7997 | 122.7722 | 122.905 | -0.40741 | -0.38452
2199.9844 | 122.9462 | -122.7448 | 0.1831 | -0.090714 | 0.014552 | 0.0041572 | 0.049642 | -0.014266 | -0.011476 | 0.014544 | -0.027466 | 0.15564 | -0.28381 | 0.054932 | 0.045776 | 0.07782 | -0.027466 | 0.17395 | 0.19684 | -0.25177 | 122.4609 | -0.027465 | 122.7173 | 122.7997 | -0.13733 | 122.493 | 0.013733 | 0.25635 | 122.7173 | 122.9187 | 122.7905 | 122.9004 | 122.7173 | 122.9416 | 122.8226 | 122.493 | 122.9004 | 122.7173 | 122.8226 | 122.7905 | 122.9416 | -0.46692 | -0.43488
2201.7344 | 123.0515 | -122.6898 | 0.15564 | -0.044937 | 0.013698 | -0.003747 | 0.036397 | -0.014907 | -0.010408 | 0.014757 | -0.009155 | 0.14648 | -0.24719 | 0.064087 | 0.10529 | 0.15564 | -0.11902 | 0.25635 | 0.19684 | -0.2243 | 122.4426 | -0.009156 | 122.6807 | 122.7539 | -0.050354 | 122.4655 | 0.041198 | 0.23804 | 122.5708 | 122.9462 | 122.7951 | 122.8363 | 122.6807 | 122.8867 | 122.8455 | 122.4655 | 122.8363 | 122.6807 | 122.8455 | 122.7951 | 122.8867 | -0.40283 | -0.37994
2203.4375 | 122.9599 | -122.731 | 0.1831 | 0.11528 | 0.01327 | -0.002038 | 0.041524 | -0.011489 | -0.0086987 | 0.01668 | 0.045776 | 0.12817 | -0.22888 | 0.068665 | 0.10529 | 0.15564 | -0.15564 | 0.22888 | 0.1831 | -0.21515 | 122.5021 | -0.054931 | 122.7768 | 122.7997 | -0.077819 | 122.5159 | 0 | 0.27466 | 122.5754 | 122.9599 | 122.8363 | 122.8592 | 122.7768 | 122.9141 | 122.8867 | 122.5159 | 122.8592 | 122.7768 | 122.8867 | 122.8363 | 122.9141 | -0.41199 | -0.39825
2205.1719 | 123.0881 | -122.7173 | 0.15564 | -0.22041 | 0.016047 | -0.00032903 | 0.042592 | -0.016829 | -0.0080579 | 0.015612 | -0.041199 | 0.15106 | -0.27466 | 0 | 0.027466 | 0.036621 | 0.036621 | 0.16937 | 0.21057 | -0.27008 | 122.4426 | -0.004578 | 122.6761 | 122.7173 | -0.12817 | 122.4472 | 0.054931 | 0.23346 | 122.7539 | 122.8867 | 122.7448 | 122.8683 | 122.6761 | 122.9279 | 122.7539 | 122.4472 | 122.8683 | 122.6761 | 122.7539 | 122.7448 | 122.9279 | -0.4303 | -0.42572
2206.9219 | 123.0469 | -122.7219 | 0.16479 | -0.20515 | 0.014766 | -0.0018244 | 0.041524 | -0.016616 | -0.0089123 | 0.013689 | 0.036621 | 0.1236 | -0.23804 | 0.086975 | 0.11902 | 0.14648 | -0.09613 | 0.27466 | 0.18768 | -0.21057 | 122.4838 | -0.041199 | 122.7585 | 122.8088 | -0.045776 | 122.5113 | 0.022888 | 0.27466 | 122.6257 | 122.9965 | 122.8409 | 122.8455 | 122.7585 | 122.9095 | 122.8683 | 122.5113 | 122.8455 | 122.7585 | 122.8683 | 122.8409 | 122.9095 | -0.40283 | -0.37537
2208.6875 | 123.0835 | -122.7036 | 0.16479 | -0.0067901 | 0.013911 | -0.0033196 | 0.038106 | -0.014479 | -0.0080579 | 0.014544 | -0.018311 | 0.14191 | -0.26093 | 0.036621 | 0.082397 | 0.12817 | -0.10071 | 0.22888 | 0.17853 | -0.23346 | 122.4426 | -0.022888 | 122.6852 | 122.7402 | -0.082398 | 122.4701 | 0.013733 | 0.24261 | 122.6028 | 122.9324 | 122.7859 | 122.8455 | 122.6852 | 122.8821 | 122.8317 | 122.4701 | 122.8455 | 122.6852 | 122.8317 | 122.7859 | 122.8821 | -0.42572 | -0.39825
2210.375 | 123.0606 | -122.7081 | 0.15564 | 0.038986 | 0.015407 | -0.003106 | 0.042379 | -0.014907 | -0.0080579 | 0.014971 | -0.022888 | 0.14191 | -0.24719 | 0.041199 | 0.064087 | 0.11444 | -0.091553 | 0.20599 | 0.19226 | -0.22888 | 122.4609 | -0.013733 | 122.6852 | 122.7493 | -0.091553 | 122.4792 | 0.036621 | 0.2243 | 122.6166 | 122.9141 | 122.7722 | 122.85 | 122.6852 | 122.9004 | 122.8226 | 122.4792 | 122.85 | 122.6852 | 122.8226 | 122.7722 | 122.9004 | -0.40283 | -0.38452
2212.125 | 122.9553 | -122.7722 | 0.20599 | -0.083084 | 0.014766 | 0.0011664 | 0.047292 | -0.013625 | -0.01169 | 0.01433 | -0.004578 | 0.13733 | -0.26093 | 0.027466 | 0.027466 | 0.059509 | -0.032043 | 0.15564 | 0.2243 | -0.22888 | 122.5113 | -0.068665 | 122.7676 | 122.7997 | -0.17853 | 122.5433 | 0.01831 | 0.25635 | 122.7402 | 122.9279 | 122.7997 | 122.9095 | 122.7676 | 122.9965 | 122.8317 | 122.5433 | 122.9095 | 122.7676 | 122.8317 | 122.7997 | 122.9965 | -0.46692 | -0.43488
2213.8906 | 122.9416 | -122.7539 | 0.19226 | 0.17632 | 0.015193 | 0.00052557 | 0.04366 | -0.014693 | -0.0086987 | 0.015825 | 0.022888 | 0.14191 | -0.24719 | 0.068665 | 0.10986 | 0.15106 | -0.17853 | 0.2243 | 0.17853 | -0.21973 | 122.5067 | -0.050354 | 122.7768 | 122.8226 | -0.082398 | 122.5342 | -0.013733 | 0.27008 | 122.5754 | 122.9782 | 122.8638 | 122.8958 | 122.7768 | 122.9324 | 122.905 | 122.5342 | 122.8958 | 122.7768 | 122.905 | 122.8638 | 122.9324 | -0.43945 | -0.41199
2215.5781 | 122.9416 | -122.7768 | 0.18768 | 0.21446 | 0.013484 | 0.00095277 | 0.041524 | -0.01213 | -0.0097669 | 0.015825 | -0.032043 | 0.13275 | -0.26093 | 0.064087 | 0.091553 | 0.11902 | -0.13733 | 0.21515 | 0.19226 | -0.2243 | 122.5159 | -0.054932 | 122.7448 | 122.8409 | -0.09613 | 122.5525 | 0.004578 | 0.22888 | 122.6395 | 122.9919 | 122.8683 | 122.9095 | 122.7448 | 122.9691 | 122.8958 | 122.5525 | 122.9095 | 122.7448 | 122.8958 | 122.8683 | 122.9691 | -0.44861 | -0.41199
2217.2656 | 122.9919 | -122.7402 | 0.19226 | -0.044937 | 0.014979 | -0.00032903 | 0.045797 | -0.015334 | -0.01233 | 0.017748 | -0.07782 | 0.16479 | -0.29755 | -0.050354 | -0.022888 | 0.004578 | 0.018311 | 0.086975 | 0.21057 | -0.26093 | 122.4426 | -0.027466 | 122.6624 | 122.6898 | -0.21515 | 122.4792 | 0.01831 | 0.21973 | 122.7585 | 122.8271 | 122.7173 | 122.905 | 122.6624 | 122.9507 | 122.7448 | 122.4792 | 122.905 | 122.6624 | 122.7448 | 122.7173 | 122.9507 | -0.48981 | -0.45319
2219.0156 | 122.9599 | -122.7356 | 0.16479 | 0.15343 | 0.01327 | -0.0035332 | 0.038106 | -0.013839 | -0.0080579 | 0.016253 | 0.041199 | 0.12817 | -0.24719 | 0.073242 | 0.11444 | 0.15106 | -0.17395 | 0.24261 | 0.19226 | -0.23346 | 122.4884 | -0.036621 | 122.7768 | 122.8088 | -0.050354 | 122.5021 | 0.027466 | 0.28839 | 122.5616 | 122.9782 | 122.85 | 122.8638 | 122.7768 | 122.9279 | 122.8867 | 122.5021 | 122.8638 | 122.7768 | 122.8867 | 122.85 | 122.9279 | -0.41199 | -0.39825
2220.7656 | 122.9553 | -122.7539 | 0.18768 | 0.1992 | 0.012416 | 0.00031197 | 0.041738 | -0.013411 | -0.010621 | 0.016253 | 0.018311 | 0.12817 | -0.24719 | 0.07782 | 0.10529 | 0.15564 | -0.1831 | 0.25177 | 0.17395 | -0.21973 | 122.5067 | -0.059509 | 122.7722 | 122.8317 | -0.082397 | 122.5342 | -0.013733 | 0.2655 | 122.5708 | 123.0057 | 122.8592 | 122.8821 | 122.7722 | 122.9279 | 122.9095 | 122.5342 | 122.8821 | 122.7722 | 122.9095 | 122.8592 | 122.9279 | -0.43488 | -0.40741
2222.5156 | 123.056 | -122.7173 | 0.16937 | -0.16701 | 0.014338 | -0.0060968 | 0.041097 | -0.014907 | -0.0091259 | 0.014757 | 0.018311 | 0.1236 | -0.24719 | 0.07782 | 0.10529 | 0.13275 | -0.07782 | 0.25635 | 0.19684 | -0.25177 | 122.4701 | -0.045777 | 122.7356 | 122.7951 | -0.064087 | 122.4655 | 0.027465 | 0.2655 | 122.6395 | 122.9736 | 122.8226 | 122.8409 | 122.7356 | 122.9141 | 122.85 | 122.4655 | 122.8409 | 122.7356 | 122.85 | 122.8226 | 122.9141 | -0.41656 | -0.42114
2224.2188 | 123.0698 | -122.7219 | 0.16937 | -0.1899 | 0.013484 | 9.8166e-05 | 0.045369 | -0.013839 | -0.010408 | 0.015612 | -0.068665 | 0.16479 | -0.30212 | 0.018311 | 0.013733 | 0.041199 | 0.022888 | 0.15106 | 0.20599 | -0.27466 | 122.4197 | -0.004578 | 122.6532 | 122.7402 | -0.15564 | 122.4472 | 0.036621 | 0.23346 | 122.7448 | 122.8729 | 122.7356 | 122.8867 | 122.6532 | 122.9279 | 122.7631 | 122.4472 | 122.8867 | 122.6532 | 122.7631 | 122.7356 | 122.9279 | -0.4715 | -0.44403
2225.9844 | 122.9736 | -122.7814 | 0.19226 | -0.037308 | 0.014552 | 0.00095277 | 0.045369 | -0.012984 | -0.011476 | 0.012835 | -0.018311 | 0.14191 | -0.27008 | 0.022888 | 0.032043 | 0.050354 | -0.022888 | 0.13733 | 0.2243 | -0.25177 | 122.5113 | -0.050354 | 122.7631 | 122.8043 | -0.16022 | 122.5296 | 0.032043 | 0.25177 | 122.7585 | 122.9187 | 122.8134 | 122.9233 | 122.7631 | 123.0057 | 122.8317 | 122.5296 | 122.9233 | 122.7631 | 122.8317 | 122.8134 | 123.0057 | -0.46234 | -0.44403
2227.7344 | 122.9782 | -122.7585 | 0.16937 | 0.11528 | 0.012202 | 0.0018072 | 0.038747 | -0.013625 | -0.0086987 | 0.014757 | 0.013733 | 0.1236 | -0.23804 | 0.064087 | 0.09613 | 0.14191 | -0.17853 | 0.23346 | 0.16479 | -0.21973 | 122.5204 | -0.045777 | 122.7722 | 122.8226 | -0.073243 | 122.5388 | -0.004578 | 0.25177 | 122.58 | 122.9919 | 122.8546 | 122.8821 | 122.7722 | 122.9233 | 122.9004 | 122.5388 | 122.8821 | 122.7722 | 122.9004 | 122.8546 | 122.9233 | -0.40741 | -0.3891
2229.4219 | 122.9553 | -122.7814 | 0.18768 | -0.098343 | 0.01327 | -0.0022516 | 0.045583 | -0.013411 | -0.011903 | 0.013475 | -0.013733 | 0.15564 | -0.27924 | 0.032043 | 0.059509 | 0.064087 | -0.022888 | 0.19226 | 0.21973 | -0.25635 | 122.5021 | -0.032043 | 122.7676 | 122.8134 | -0.12817 | 122.525 | 0.032044 | 0.2655 | 122.7585 | 122.9736 | 122.8409 | 122.937 | 122.7676 | 123.0011 | 122.8455 | 122.525 | 122.937 | 122.7676 | 122.8455 | 122.8409 | 123.0011 | -0.46692 | -0.44403
2231.1875 | 123.0011 | -122.7493 | 0.17853 | 0.10002 | 0.013484 | 0.0026618 | 0.045156 | -0.011702 | -0.01169 | 0.016466 | -0.086975 | 0.17853 | -0.27466 | -0.041199 | -0.009155 | 0.004578 | -0.004578 | 0.07782 | 0.22888 | -0.24719 | 122.4747 | 0 | 122.6624 | 122.7081 | -0.18768 | 122.5021 | 0.050354 | 0.18768 | 122.7448 | 122.8271 | 122.7402 | 122.9279 | 122.6624 | 122.9782 | 122.7539 | 122.5021 | 122.9279 | 122.6624 | 122.7539 | 122.7402 | 122.9782 | -0.45319 | -0.42572
2232.9375 | 122.937 | -122.7631 | 0.1831 | 0.17632 | 0.013484 | 0.0050116 | 0.042165 | -0.011489 | -0.0086987 | 0.016466 | -0.004578 | 0.15564 | -0.2655 | 0.064087 | 0.082397 | 0.13275 | -0.13275 | 0.21515 | 0.1831 | -0.21973 | 122.4976 | -0.027465 | 122.7585 | 122.8271 | -0.10071 | 122.5433 | 0 | 0.26092 | 122.6303 | 122.9782 | 122.8455 | 122.9187 | 122.7585 | 122.9462 | 122.8958 | 122.5433 | 122.9187 | 122.7585 | 122.8958 | 122.8455 | 122.9462 | -0.44861 | -0.40283
2234.7031 | 122.937 | -122.7539 | 0.19684 | 0.1458 | 0.014979 | -0.0026788 | 0.043233 | -0.014479 | -0.0099805 | 0.01668 | 0.045776 | 0.13275 | -0.24261 | 0.086975 | 0.10071 | 0.15564 | -0.18768 | 0.23346 | 0.17853 | -0.21515 | 122.5113 | -0.064087 | 122.7997 | 122.8409 | -0.09613 | 122.5388 | -0.01831 | 0.28839 | 122.5662 | 122.9874 | 122.8546 | 122.8867 | 122.7997 | 122.9324 | 122.9095 | 122.5388 | 122.8867 | 122.7997 | 122.9095 | 122.8546 | 122.9324 | -0.43945 | -0.41199
2236.4062 | 122.9691 | -122.7722 | 0.18768 | -0.10597 | 0.015407 | -0.0022516 | 0.045156 | -0.011061 | -0.010835 | 0.015184 | -0.018311 | 0.16937 | -0.27924 | 0.036621 | 0.045776 | 0.068665 | -0.027466 | 0.19226 | 0.20599 | -0.23346 | 122.493 | -0.01831 | 122.7539 | 122.8088 | -0.14191 | 122.5388 | 0.018311 | 0.26092 | 122.7448 | 122.9645 | 122.818 | 122.9416 | 122.7539 | 122.9782 | 122.8409 | 122.5388 | 122.9416 | 122.7539 | 122.8409 | 122.818 | 122.9782 | -0.46692 | -0.42114
2238.0938 | 122.9919 | -122.7768 | 0.19226 | -0.0067901 | 0.015834 | -0.00075623 | 0.044728 | -0.011916 | -0.010621 | 0.014544 | -0.036621 | 0.16022 | -0.27466 | -0.004578 | 0.018311 | 0.027466 | -0.013733 | 0.13733 | 0.21973 | -0.2655 | 122.5021 | -0.032044 | 122.7402 | 122.7722 | -0.17395 | 122.5113 | 0.027466 | 0.23804 | 122.7631 | 122.9141 | 122.7951 | 122.937 | 122.7402 | 122.9965 | 122.8043 | 122.5113 | 122.937 | 122.7402 | 122.8043 | 122.7951 | 122.9965 | -0.46692 | -0.45776
2239.8281 | 122.9416 | -122.7676 | 0.17853 | -0.075455 | 0.013484 | -0.0022516 | 0.042806 | -0.010207 | -0.011262 | 0.014757 | 0 | 0.16479 | -0.27008 | 0.018311 | 0.050354 | 0.064087 | -0.022888 | 0.16937 | 0.21515 | -0.23804 | 122.4976 | -0.013733 | 122.7676 | 122.7859 | -0.12817 | 122.5296 | 0.036621 | 0.27008 | 122.7448 | 122.937 | 122.818 | 122.9324 | 122.7676 | 122.9828 | 122.8317 | 122.5296 | 122.9324 | 122.7676 | 122.8317 | 122.818 | 122.9828 | -0.44861 | -0.41656
2241.9219 | 123.0469 | -122.7219 | 0.16937 | -0.22804 | 0.01327 | -0.0035332 | 0.036824 | -0.015548 | -0.0093395 | 0.015398 | 0.036621 | 0.11902 | -0.24261 | 0.091553 | 0.13275 | 0.15106 | -0.10071 | 0.28839 | 0.1831 | -0.24261 | 122.4792 | -0.050354 | 122.7585 | 122.8134 | -0.036622 | 122.4792 | 0.013732 | 0.27924 | 122.6212 | 123.0103 | 122.8546 | 122.8409 | 122.7585 | 122.905 | 122.8729 | 122.4792 | 122.8409 | 122.7585 | 122.8729 | 122.8546 | 122.905 | -0.41199 | -0.41199
2243.8438 | 123.0515 | -122.7356 | 0.15564 | -0.1899 | 0.014125 | -0.00054263 | 0.039388 | -0.012984 | -0.0095531 | 0.014971 | 0.018311 | 0.1236 | -0.23804 | 0.073242 | 0.10986 | 0.13733 | -0.091553 | 0.27008 | 0.19226 | -0.23346 | 122.4976 | -0.032044 | 122.7539 | 122.8088 | -0.045777 | 122.5021 | 0.036621 | 0.25635 | 122.644 | 123.0057 | 122.8455 | 122.8592 | 122.7539 | 122.9279 | 122.8729 | 122.5021 | 122.8592 | 122.7539 | 122.8729 | 122.8455 | 122.9279 | -0.39368 | -0.3891
2245.5781 | 123.0515 | -122.7264 | 0.17395 | -0.22041 | 0.011775 | 0.00095277 | 0.038961 | -0.015334 | -0.0069897 | 0.01433 | 0.022888 | 0.11902 | -0.26093 | 0.082397 | 0.14191 | 0.15564 | -0.1236 | 0.28381 | 0.17853 | -0.2243 | 122.4655 | -0.054931 | 122.7493 | 122.8088 | -0.032043 | 122.5021 | 0.004578 | 0.28381 | 122.6028 | 123.0103 | 122.8683 | 122.8455 | 122.7493 | 122.905 | 122.8821 | 122.5021 | 122.8455 | 122.7493 | 122.8821 | 122.8683 | 122.905 | -0.43488 | -0.39825
2247.3125 | 123.0652 | -122.731 | 0.17853 | -0.19753 | 0.014125 | -0.003747 | 0.044728 | -0.014693 | -0.012117 | 0.014544 | -0.050354 | 0.17853 | -0.28839 | 0 | 0.032043 | 0.059509 | 0.032043 | 0.16937 | 0.21515 | -0.25177 | 122.4426 | 0 | 122.6807 | 122.731 | -0.14648 | 122.4792 | 0.036621 | 0.23804 | 122.7631 | 122.9004 | 122.7631 | 122.9095 | 122.6807 | 122.9462 | 122.7905 | 122.4792 | 122.9095 | 122.6807 | 122.7905 | 122.7631 | 122.9462 | -0.46692 | -0.4303
2249.0781 | 123.056 | -122.7219 | 0.17853 | 0.069504 | 0.012416 | 0.0037298 | 0.037892 | -0.01512 | -0.0095531 | 0.016253 | -0.022888 | 0.13275 | -0.24261 | 0.013733 | 0.064087 | 0.11444 | -0.091553 | 0.20142 | 0.19226 | -0.24261 | 122.4792 | -0.045777 | 122.699 | 122.7356 | -0.11444 | 122.4792 | 0.013733 | 0.21973 | 122.6303 | 122.9233 | 122.7859 | 122.8546 | 122.699 | 122.9141 | 122.8363 | 122.4792 | 122.8546 | 122.699 | 122.8363 | 122.7859 | 122.9141 | -0.42114 | -0.42114
2250.8438 | 123.0743 | -122.7173 | 0.16022 | -0.18227 | 0.014979 | -0.00011543 | 0.045369 | -0.015548 | -0.010408 | 0.016893 | -0.073242 | 0.17853 | -0.29755 | -0.018311 | 0.009155 | 0.032043 | 0.050354 | 0.15106 | 0.21973 | -0.27008 | 122.4197 | 0.018311 | 122.644 | 122.699 | -0.15106 | 122.4472 | 0.05951 | 0.2243 | 122.7676 | 122.8683 | 122.7264 | 122.8958 | 122.644 | 122.937 | 122.7493 | 122.4472 | 122.8958 | 122.644 | 122.7493 | 122.7264 | 122.937 | -0.45776 | -0.4303
2252.5938 | 123.0927 | -122.7356 | 0.16022 | 0.016098 | 0.015407 | -0.0033196 | 0.038961 | -0.014479 | -0.0084851 | 0.015612 | -0.041199 | 0.15106 | -0.25635 | 0.018311 | 0.073242 | 0.082397 | -0.10071 | 0.20599 | 0.20599 | -0.23804 | 122.4792 | -0.009155 | 122.6944 | 122.7539 | -0.086975 | 122.4976 | 0.045777 | 0.21515 | 122.6349 | 122.9416 | 122.8088 | 122.8867 | 122.6944 | 122.9416 | 122.818 | 122.4976 | 122.8867 | 122.6944 | 122.818 | 122.8088 | 122.9416 | -0.41657 | -0.39825
2254.2969 | 122.9599 | -122.7859 | 0.19226 | -0.029679 | 0.01327 | 0.0026618 | 0.046651 | -0.014266 | -0.013399 | 0.015398 | -0.009155 | 0.14648 | -0.28839 | 0.018311 | 0.027466 | 0.041199 | -0.022888 | 0.15106 | 0.23346 | -0.27008 | 122.4976 | -0.045777 | 122.7768 | 122.8043 | -0.16479 | 122.5159 | 0.041198 | 0.27924 | 122.7631 | 122.937 | 122.8134 | 122.9324 | 122.7768 | 123.0194 | 122.8271 | 122.5159 | 122.9324 | 122.7768 | 122.8271 | 122.8134 | 123.0194 | -0.48065 | -0.46234
2256.0469 | 123.0743 | -122.7173 | 0.16479 | -0.22041 | 0.015834 | -0.0016106 | 0.039601 | -0.013411 | -0.0078443 | 0.015612 | 0.013733 | 0.14191 | -0.25177 | 0.068665 | 0.073242 | 0.086975 | -0.027466 | 0.23346 | 0.21515 | -0.25635 | 122.4655 | -0.022888 | 122.731 | 122.7859 | -0.091553 | 122.4609 | 0.050354 | 0.2655 | 122.6898 | 122.9507 | 122.7905 | 122.8592 | 122.731 | 122.9324 | 122.8043 | 122.4609 | 122.8592 | 122.731 | 122.8043 | 122.7905 | 122.9324 | -0.41656 | -0.42114
2257.7969 | 123.0331 | -122.731 | 0.15106 | 0.061874 | 0.015407 | 0.0035162 | 0.039815 | -0.012984 | -0.0082715 | 0.013689 | -0.004578 | 0.1236 | -0.26093 | 0.018311 | 0.059509 | 0.11902 | -0.10986 | 0.21057 | 0.19226 | -0.21973 | 122.4701 | -0.027466 | 122.7264 | 122.7493 | -0.091553 | 122.5113 | 0.041199 | 0.25635 | 122.6212 | 122.9416 | 122.7905 | 122.8546 | 122.7264 | 122.9233 | 122.85 | 122.5113 | 122.8546 | 122.7264 | 122.85 | 122.7905 | 122.9233 | -0.41199 | -0.37079
2259.5469 | 123.0469 | -122.731 | 0.16022 | -0.12886 | 0.014338 | -0.002038 | 0.039388 | -0.015334 | -0.0082715 | 0.014116 | 0.045776 | 0.14648 | -0.23804 | 0.10071 | 0.14191 | 0.15564 | -0.14191 | 0.29297 | 0.1831 | -0.21515 | 122.493 | -0.013733 | 122.7768 | 122.8317 | -0.01831 | 122.5159 | 0.022888 | 0.28381 | 122.5891 | 123.024 | 122.8729 | 122.8775 | 122.7768 | 122.9141 | 122.8867 | 122.5159 | 122.8775 | 122.7768 | 122.8867 | 122.8729 | 122.9141 | -0.39825 | -0.37537
2261.2344 | 123.0835 | -122.7081 | 0.16479 | -0.1899 | 0.016261 | 9.8166e-05 | 0.045797 | -0.014907 | -0.0093395 | 0.013689 | -0.045776 | 0.1831 | -0.28381 | -0.018311 | 0.013733 | 0.022888 | 0.045776 | 0.15106 | 0.21973 | -0.27008 | 122.4243 | 0.01831 | 122.6624 | 122.6898 | -0.15106 | 122.438 | 0.054932 | 0.23804 | 122.7539 | 122.8592 | 122.7219 | 122.8912 | 122.6624 | 122.9279 | 122.731 | 122.438 | 122.8912 | 122.6624 | 122.731 | 122.7219 | 122.9279 | -0.44861 | -0.43488
2262.9688 | 122.9553 | -122.7539 | 0.19684 | 0.17632 | 0.016475 | -0.0018244 | 0.044515 | -0.015761 | -0.0093395 | 0.015184 | 0 | 0.15106 | -0.2655 | 0.068665 | 0.09613 | 0.13733 | -0.16479 | 0.22888 | 0.18768 | -0.20599 | 122.4884 | -0.045776 | 122.7539 | 122.8226 | -0.10071 | 122.5479 | -0.009155 | 0.2655 | 122.5891 | 122.9828 | 122.85 | 122.905 | 122.7539 | 122.9416 | 122.8912 | 122.5479 | 122.905 | 122.7539 | 122.8912 | 122.85 | 122.9416 | -0.46234 | -0.40283
2264.7344 | 123.0057 | -122.7219 | 0.16937 | 0.15343 | 0.014766 | -0.00075623 | 0.045156 | -0.013625 | -0.010621 | 0.016039 | -0.07782 | 0.16022 | -0.28839 | -0.036621 | -0.027466 | 0.009155 | 0 | 0.082397 | 0.21515 | -0.27008 | 122.4335 | -0.009156 | 122.644 | 122.6852 | -0.19684 | 122.4518 | 0.045776 | 0.21057 | 122.7219 | 122.8043 | 122.6944 | 122.8821 | 122.644 | 122.937 | 122.731 | 122.4518 | 122.8821 | 122.644 | 122.731 | 122.6944 | 122.937 | -0.45776 | -0.43945
2266.4375 | 123.0652 | -122.7219 | 0.16479 | -0.098343 | 0.01327 | 0.00138 | 0.039815 | -0.015334 | -0.0082715 | 0.016466 | -0.022888 | 0.15106 | -0.25635 | 0.059509 | 0.1236 | 0.14191 | -0.11444 | 0.26093 | 0.17853 | -0.24261 | 122.4655 | -0.013733 | 122.699 | 122.7814 | -0.041199 | 122.4792 | 0.013733 | 0.23346 | 122.6074 | 122.9828 | 122.8455 | 122.8729 | 122.699 | 122.9004 | 122.8638 | 122.4792 | 122.8729 | 122.699 | 122.8638 | 122.8455 | 122.9004 | -0.42114 | -0.40741
2268.1875 | 122.9828 | -122.7814 | 0.18768 | -0.1136 | 0.014979 | 0.0041572 | 0.046437 | -0.012557 | -0.01169 | 0.013689 | -0.013733 | 0.15106 | -0.28839 | 0.027466 | 0.036621 | 0.050354 | -0.009155 | 0.1831 | 0.22888 | -0.27466 | 122.493 | -0.036621 | 122.7676 | 122.8088 | -0.15106 | 122.5067 | 0.041199 | 0.27466 | 122.7722 | 122.9645 | 122.818 | 122.9324 | 122.7676 | 123.0103 | 122.8317 | 122.5067 | 122.9324 | 122.7676 | 122.8317 | 122.818 | 123.0103 | -0.47607 | -0.46234
2269.9531 | 122.9691 | -122.7402 | 0.20142 | 0.1458 | 0.013057 | 0.002021 | 0.040883 | -0.014479 | -0.0072033 | 0.015825 | 0.041199 | 0.13733 | -0.26093 | 0.073242 | 0.10529 | 0.14648 | -0.17853 | 0.24261 | 0.19226 | -0.23346 | 122.4792 | -0.064087 | 122.7814 | 122.8134 | -0.09613 | 122.5067 | -0.009155 | 0.30212 | 122.5616 | 122.9828 | 122.8455 | 122.8775 | 122.7814 | 122.9324 | 122.8867 | 122.5067 | 122.8775 | 122.7814 | 122.8867 | 122.8455 | 122.9324 | -0.46234 | -0.43488
2271.7031 | 122.9416 | -122.7539 | 0.19684 | 0.16106 | 0.013484 | -0.0028924 | 0.043874 | -0.014693 | -0.011476 | 0.018175 | 0.036621 | 0.1236 | -0.25635 | 0.07782 | 0.086975 | 0.16022 | -0.18768 | 0.23346 | 0.17395 | -0.23346 | 122.4976 | -0.073242 | 122.7905 | 122.8317 | -0.10986 | 122.5204 | -0.022888 | 0.29297 | 122.5662 | 122.9874 | 122.8409 | 122.8775 | 122.7905 | 122.9279 | 122.9141 | 122.5204 | 122.8775 | 122.7905 | 122.9141 | 122.8409 | 122.9279 | -0.45319 | -0.4303
2273.4531 | 122.9691 | -122.7631 | 0.19226 | -0.037308 | 0.015407 | 0.0037298 | 0.047933 | -0.012557 | -0.010408 | 0.015184 | -0.013733 | 0.15564 | -0.28839 | 0.013733 | 0.022888 | 0.041199 | -0.018311 | 0.16022 | 0.21057 | -0.25177 | 122.4747 | -0.036621 | 122.7493 | 122.7768 | -0.16937 | 122.5113 | 0.01831 | 0.27466 | 122.7448 | 122.9233 | 122.7859 | 122.9187 | 122.7493 | 122.9736 | 122.8043 | 122.5113 | 122.9187 | 122.7493 | 122.8043 | 122.7859 | 122.9736 | -0.48065 | -0.44403
2275.1406 | 123.0103 | -122.7539 | 0.18768 | 0.16869 | 0.013911 | -0.002038 | 0.043447 | -0.013839 | -0.0099805 | 0.014971 | -0.050354 | 0.15564 | -0.29755 | -0.004578 | 0.027466 | 0.059509 | -0.086975 | 0.14648 | 0.19226 | -0.23346 | 122.4564 | -0.032043 | 122.7036 | 122.7493 | -0.16022 | 122.5204 | 0.004578 | 0.24719 | 122.6669 | 122.9004 | 122.7814 | 122.9095 | 122.7036 | 122.9462 | 122.8134 | 122.5204 | 122.9095 | 122.7036 | 122.8134 | 122.7814 | 122.9462 | -0.48523 | -0.42114
2276.8906 | 123.0423 | -122.7173 | 0.14191 | -0.098343 | 0.014979 | -0.001397 | 0.036824 | -0.01747 | -0.0093395 | 0.015398 | 0.041199 | 0.14648 | -0.25635 | 0.10529 | 0.16022 | 0.17853 | -0.15106 | 0.28839 | 0.19226 | -0.24719 | 122.4609 | 0.004577 | 122.7585 | 122.8226 | 0.01831 | 122.4701 | 0.050354 | 0.29755 | 122.5662 | 123.0057 | 122.8775 | 122.8638 | 122.7585 | 122.9095 | 122.8958 | 122.4701 | 122.8638 | 122.7585 | 122.8958 | 122.8775 | 122.9095 | -0.39826 | -0.3891
2278.6562 | 123.0972 | -122.7173 | 0.14191 | 0.00083945 | 0.011348 | -0.00032903 | 0.039601 | -0.015975 | -0.0069897 | 0.014116 | -0.032043 | 0.14191 | -0.2655 | 0.009155 | 0.064087 | 0.09613 | -0.073242 | 0.18768 | 0.20599 | -0.25177 | 122.4518 | 0 | 122.6852 | 122.7264 | -0.07782 | 122.4655 | 0.064087 | 0.23346 | 122.644 | 122.905 | 122.7814 | 122.8592 | 122.6852 | 122.9233 | 122.8134 | 122.4655 | 122.8592 | 122.6852 | 122.8134 | 122.7814 | 122.9233 | -0.40741 | -0.39368
2280.3438 | 123.0789 | -122.7127 | 0.14648 | -0.060196 | 0.012202 | 0.00073917 | 0.040456 | -0.015334 | -0.010194 | 0.013262 | 0.009155 | 0.14191 | -0.25635 | 0.064087 | 0.11444 | 0.14191 | -0.11902 | 0.2655 | 0.17853 | -0.21973 | 122.4564 | -0.004577 | 122.7219 | 122.7768 | -0.032043 | 122.493 | 0.032044 | 0.2655 | 122.5937 | 122.9782 | 122.8271 | 122.8546 | 122.7219 | 122.8912 | 122.8546 | 122.493 | 122.8546 | 122.7219 | 122.8546 | 122.8271 | 122.8912 | -0.40283 | -0.36621
2282.0312 | 123.0515 | -122.7356 | 0.16022 | -0.16701 | 0.014979 | 0.0039436 | 0.04131 | -0.014479 | -0.0086987 | 0.015398 | 0.045776 | 0.13275 | -0.26093 | 0.11444 | 0.11444 | 0.16022 | -0.12817 | 0.29297 | 0.19226 | -0.23346 | 122.4747 | -0.027466 | 122.7814 | 122.85 | -0.045776 | 122.5021 | 0.032044 | 0.3067 | 122.6074 | 123.0286 | 122.85 | 122.8683 | 122.7814 | 122.9279 | 122.8958 | 122.5021 | 122.8683 | 122.7814 | 122.8958 | 122.85 | 122.9279 | -0.42114 | -0.39368
2283.7656 | 122.9782 | -122.7722 | 0.17853 | -0.067826 | 0.013698 | -0.00032903 | 0.046437 | -0.012557 | -0.012117 | 0.013689 | -0.004578 | 0.15564 | -0.30212 | 0.041199 | 0.054932 | 0.073242 | -0.036621 | 0.17853 | 0.20599 | -0.24261 | 122.4701 | -0.022888 | 122.7676 | 122.8134 | -0.1236 | 122.5296 | 0.027466 | 0.29755 | 122.7356 | 122.9507 | 122.8271 | 122.9279 | 122.7676 | 122.9782 | 122.8455 | 122.5296 | 122.9279 | 122.7676 | 122.8455 | 122.8271 | 122.9782 | -0.48065 | -0.42114
2285.5312 | 123.0972 | -122.7127 | 0.15564 | -0.2433 | 0.01327 | 0.0026618 | 0.043874 | -0.013839 | -0.01169 | 0.015612 | -0.091553 | 0.17853 | -0.29297 | -0.027466 | 0.009155 | 0.009155 | 0.068665 | 0.13733 | 0.23346 | -0.29297 | 122.4197 | 0.022888 | 122.6212 | 122.6852 | -0.14649 | 122.4197 | 0.077819 | 0.20142 | 122.7814 | 122.85 | 122.7219 | 122.8912 | 122.6212 | 122.9462 | 122.7219 | 122.4197 | 122.8912 | 122.6212 | 122.7219 | 122.7219 | 122.9462 | -0.44861 | -0.44861
2287.2188 | 123.0743 | -122.7768 | 0.14648 | -0.22804 | 0.012843 | 0.0028754 | 0.040242 | -0.015548 | -0.0097669 | 0.015825 | 0 | 0.12817 | -0.27008 | 0.032043 | 0.07782 | 0.09613 | -0.036621 | 0.21973 | 0.21515 | -0.24261 | 122.5067 | -0.01831 | 122.7768 | 122.8088 | -0.068664 | 122.5342 | 0.068665 | 0.27008 | 122.7402 | 122.9965 | 122.8546 | 122.905 | 122.7768 | 122.9919 | 122.8729 | 122.5342 | 122.905 | 122.7768 | 122.8729 | 122.8546 | 122.9919 | -0.41657 | -0.3891
2288.9688 | 123.0789 | -122.731 | 0.16937 | -0.15938 | 0.012843 | -0.0011834 | 0.040883 | -0.015761 | -0.01169 | 0.01433 | 0.027466 | 0.16022 | -0.23346 | 0.086975 | 0.10986 | 0.1236 | -0.07782 | 0.2655 | 0.20599 | -0.25635 | 122.4976 | -0.009156 | 122.7585 | 122.818 | -0.05951 | 122.4747 | 0.036621 | 0.26093 | 122.6532 | 122.9965 | 122.8409 | 122.8912 | 122.7585 | 122.937 | 122.8546 | 122.4747 | 122.8912 | 122.7585 | 122.8546 | 122.8409 | 122.937 | -0.40283 | -0.42572
2290.7188 | 123.0286 | -122.7356 | 0.1831 | -0.15175 | 0.012629 | -0.00011543 | 0.04601 | -0.013198 | -0.0091259 | 0.016039 | -0.018311 | 0.17853 | -0.30212 | 0.027466 | 0.050354 | 0.068665 | -0.013733 | 0.17395 | 0.22888 | -0.26093 | 122.4335 | -0.004577 | 122.7173 | 122.7631 | -0.13275 | 122.4747 | 0.045777 | 0.28381 | 122.7219 | 122.9095 | 122.7859 | 122.9141 | 122.7173 | 122.9645 | 122.8043 | 122.4747 | 122.9141 | 122.7173 | 122.8043 | 122.7859 | 122.9645 | -0.48523 | -0.44403
2292.4062 | 122.9828 | -122.7768 | 0.19226 | 0.21446 | 0.015407 | -0.002038 | 0.045797 | -0.014479 | -0.0080579 | 0.015398 | -0.045776 | 0.15564 | -0.29297 | 0.027466 | 0.050354 | 0.07782 | -0.10986 | 0.16479 | 0.20599 | -0.25177 | 122.4838 | -0.036621 | 122.731 | 122.8043 | -0.14191 | 122.525 | 0.013733 | 0.24719 | 122.6669 | 122.9416 | 122.8271 | 122.9324 | 122.731 | 122.9828 | 122.8546 | 122.525 | 122.9324 | 122.731 | 122.8546 | 122.8271 | 122.9828 | -0.48523 | -0.44403
2294.1562 | 123.0423 | -122.7493 | 0.17853 | -0.20515 | 0.013057 | -0.003106 | 0.040242 | -0.016188 | -0.0076305 | 0.016466 | 0.013733 | 0.1236 | -0.25177 | 0.086975 | 0.11444 | 0.12817 | -0.10071 | 0.2655 | 0.19226 | -0.24719 | 122.4976 | -0.054932 | 122.7631 | 122.8363 | -0.064087 | 122.5021 | 0.013733 | 0.2655 | 122.6486 | 123.0148 | 122.8638 | 122.8729 | 122.7631 | 122.9416 | 122.8775 | 122.5021 | 122.8729 | 122.7631 | 122.8775 | 122.8638 | 122.9416 | -0.4303 | -0.42572
2295.9219 | 122.9645 | -122.7676 | 0.1831 | -0.1136 | 0.013484 | -0.00054263 | 0.04601 | -0.01512 | -0.01468 | 0.014116 | -0.013733 | 0.16022 | -0.28839 | 0.036621 | 0.064087 | 0.082397 | -0.022888 | 0.18768 | 0.2243 | -0.22888 | 122.4792 | -0.022888 | 122.7539 | 122.8043 | -0.11902 | 122.5388 | 0.041199 | 0.27466 | 122.7448 | 122.9553 | 122.8317 | 122.9279 | 122.7539 | 122.9919 | 122.85 | 122.5388 | 122.9279 | 122.7539 | 122.85 | 122.8317 | 122.9919 | -0.4715 | -0.41199
2297.6719 | 123.0286 | -122.7493 | 0.16479 | -0.20515 | 0.013484 | -0.0039606 | 0.039815 | -0.015334 | -0.0095531 | 0.013689 | 0.022888 | 0.14191 | -0.25177 | 0.10071 | 0.13275 | 0.14648 | -0.10986 | 0.27008 | 0.19684 | -0.23346 | 122.4976 | -0.022888 | 122.7722 | 122.85 | -0.032044 | 122.5159 | 0.032043 | 0.27466 | 122.6395 | 123.0194 | 122.8821 | 122.8912 | 122.7722 | 122.9462 | 122.8958 | 122.5159 | 122.8912 | 122.7722 | 122.8958 | 122.8821 | 122.9462 | -0.41656 | -0.39825
2299.375 | 123.0606 | -122.7036 | 0.16022 | -0.16701 | 0.012202 | -0.0022516 | 0.040029 | -0.014907 | -0.010408 | 0.015825 | 0.027466 | 0.15106 | -0.25177 | 0.068665 | 0.11444 | 0.1236 | -0.068665 | 0.2655 | 0.17395 | -0.23804 | 122.4518 | -0.009155 | 122.731 | 122.7722 | -0.045776 | 122.4655 | 0.013733 | 0.27924 | 122.6349 | 122.9691 | 122.818 | 122.8546 | 122.731 | 122.8775 | 122.8271 | 122.4655 | 122.8546 | 122.731 | 122.8271 | 122.818 | 122.8775 | -0.41199 | -0.39825
2301.1406 | 123.0148 | -122.7402 | 0.15564 | 0.11528 | 0.014338 | -0.0022516 | 0.041951 | -0.014479 | -0.0091259 | 0.013903 | 0 | 0.12817 | -0.2655 | 0.036621 | 0.073242 | 0.10529 | -0.12817 | 0.20599 | 0.19684 | -0.25635 | 122.4747 | -0.027466 | 122.7402 | 122.7768 | -0.082398 | 122.4838 | 0.041198 | 0.2655 | 122.612 | 122.9462 | 122.8134 | 122.8683 | 122.7402 | 122.937 | 122.8455 | 122.4838 | 122.8683 | 122.7402 | 122.8455 | 122.8134 | 122.937 | -0.42114 | -0.41199
2302.8906 | 122.9599 | -122.7631 | 0.19226 | 0.1992 | 0.013057 | 0.00138 | 0.043233 | -0.013411 | -0.010194 | 0.013903 | 0.032043 | 0.12817 | -0.23804 | 0.082397 | 0.10986 | 0.16022 | -0.19226 | 0.24719 | 0.16479 | -0.2243 | 122.525 | -0.064087 | 122.7951 | 122.8455 | -0.082398 | 122.5388 | -0.027466 | 0.27008 | 122.5708 | 123.0103 | 122.8729 | 122.8912 | 122.7951 | 122.9279 | 122.9233 | 122.5388 | 122.8912 | 122.7951 | 122.9233 | 122.8729 | 122.9279 | -0.4303 | -0.41656
2304.5781 | 122.9828 | -122.7585 | 0.18768 | 0.1458 | 0.01327 | -0.001397 | 0.043447 | -0.015334 | -0.0091259 | 0.016253 | 0.032043 | 0.13275 | -0.26093 | 0.07782 | 0.086975 | 0.13733 | -0.17853 | 0.23804 | 0.1831 | -0.24719 | 122.4976 | -0.054932 | 122.7905 | 122.8363 | -0.10071 | 122.5113 | -0.004578 | 0.29297 | 122.58 | 122.9965 | 122.8455 | 122.8912 | 122.7905 | 122.9416 | 122.8958 | 122.5113 | 122.8912 | 122.7905 | 122.8958 | 122.8455 | 122.9416 | -0.44861 | -0.43488
2306.2812 | 123.1155 | -122.7356 | 0.16937 | -0.22804 | 0.012416 | 0.00073917 | 0.044088 | -0.016402 | -0.011903 | 0.014971 | -0.07782 | 0.16479 | -0.29297 | -0.013733 | 0 | 0.027466 | 0.054932 | 0.15106 | 0.22888 | -0.2655 | 122.4426 | -0.004578 | 122.6578 | 122.7219 | -0.16937 | 122.4701 | 0.059509 | 0.21515 | 122.7905 | 122.8867 | 122.7356 | 122.9004 | 122.6578 | 122.9645 | 122.7631 | 122.4701 | 122.9004 | 122.6578 | 122.7631 | 122.7356 | 122.9645 | -0.46234 | -0.43488
2308.0469 | 122.9691 | -122.7768 | 0.19684 | -0.12123 | 0.015193 | 0.00138 | 0.046224 | -0.011916 | -0.012758 | 0.014544 | 0 | 0.16479 | -0.28839 | 0.045776 | 0.045776 | 0.073242 | -0.032043 | 0.19226 | 0.22888 | -0.24261 | 122.4884 | -0.032043 | 122.7768 | 122.8226 | -0.15106 | 122.5342 | 0.032044 | 0.28839 | 122.7448 | 122.9691 | 122.8226 | 122.9416 | 122.7768 | 123.0057 | 122.85 | 122.5342 | 122.9416 | 122.7768 | 122.85 | 122.8226 | 123.0057 | -0.48523 | -0.43945
2309.7344 | 123.0652 | -122.7402 | 0.17853 | -0.21278 | 0.014552 | 9.8166e-05 | 0.04366 | -0.010421 | -0.0097669 | 0.013475 | -0.041199 | 0.1831 | -0.3067 | -0.004578 | 0.022888 | 0.050354 | 0.018311 | 0.14648 | 0.24261 | -0.26093 | 122.4335 | 0.004577 | 122.699 | 122.7356 | -0.15564 | 122.4792 | 0.064087 | 0.2655 | 122.7585 | 122.8867 | 122.7631 | 122.9233 | 122.699 | 122.9828 | 122.7905 | 122.4792 | 122.9233 | 122.699 | 122.7905 | 122.7631 | 122.9828 | -0.48523 | -0.43945
2311.4531 | 122.9691 | -122.7631 | 0.19684 | 0.17632 | 0.012416 | -0.00054263 | 0.043874 | -0.014907 | -0.010835 | 0.014971 | 0.041199 | 0.14648 | -0.26093 | 0.07782 | 0.11444 | 0.14648 | -0.1831 | 0.2243 | 0.20142 | -0.23346 | 122.5021 | -0.050354 | 122.8043 | 122.8409 | -0.082397 | 122.5296 | 0.004578 | 0.30212 | 122.58 | 122.9874 | 122.8775 | 122.9095 | 122.8043 | 122.9645 | 122.9095 | 122.5296 | 122.9095 | 122.8043 | 122.9095 | 122.8775 | 122.9645 | -0.45776 | -0.4303
2313.2031 | 122.9462 | -122.7859 | 0.19226 | 0.16106 | 0.012202 | -0.0024652 | 0.041738 | -0.013839 | -0.010408 | 0.013903 | 0.027466 | 0.14191 | -0.26093 | 0.068665 | 0.11444 | 0.14648 | -0.16937 | 0.25177 | 0.19684 | -0.21973 | 122.525 | -0.050354 | 122.8134 | 122.8546 | -0.07782 | 122.5662 | 0.004577 | 0.28839 | 122.6166 | 123.0377 | 122.9004 | 122.9279 | 122.8134 | 122.9828 | 122.9324 | 122.5662 | 122.9279 | 122.8134 | 122.9324 | 122.9004 | 122.9828 | -0.45319 | -0.41199
2314.9688 | 123.0927 | -122.7173 | 0.14648 | 0.054245 | 0.012629 | 0.00138 | 0.038961 | -0.015548 | -0.0072033 | 0.014971 | -0.027466 | 0.16022 | -0.2655 | 0.013733 | 0.073242 | 0.10529 | -0.10071 | 0.19684 | 0.19684 | -0.23804 | 122.4518 | 0.013733 | 122.6898 | 122.731 | -0.073242 | 122.4792 | 0.050354 | 0.23804 | 122.6166 | 122.9141 | 122.7905 | 122.8775 | 122.6898 | 122.9141 | 122.8226 | 122.4792 | 122.8775 | 122.6898 | 122.8226 | 122.7905 | 122.9141 | -0.41199 | -0.38452
2316.7344 | 123.024 | -122.7356 | 0.17853 | 0.17632 | 0.015834 | 0.0035162 | 0.048787 | -0.012984 | -0.011049 | 0.015398 | -0.073242 | 0.17395 | -0.29297 | -0.041199 | -0.027466 | 0.004578 | -0.013733 | 0.07782 | 0.23804 | -0.2655 | 122.4426 | -0.004578 | 122.6624 | 122.6944 | -0.20599 | 122.4701 | 0.059509 | 0.21973 | 122.7219 | 122.8134 | 122.7081 | 122.9095 | 122.6624 | 122.9736 | 122.7402 | 122.4701 | 122.9095 | 122.6624 | 122.7402 | 122.7081 | 122.9736 | -0.4715 | -0.44403
2318.4375 | 123.0743 | -122.7402 | 0.14191 | 0.046615 | 0.014766 | -0.0022516 | 0.039388 | -0.016188 | -0.0093395 | 0.01433 | -0.022888 | 0.14648 | -0.2655 | 0.027466 | 0.068665 | 0.10986 | -0.10986 | 0.20599 | 0.19684 | -0.25635 | 122.4747 | 0.004577 | 122.7173 | 122.7676 | -0.073242 | 122.4838 | 0.054931 | 0.24261 | 122.6303 | 122.9462 | 122.8088 | 122.8867 | 122.7173 | 122.937 | 122.85 | 122.4838 | 122.8867 | 122.7173 | 122.85 | 122.8088 | 122.937 | -0.40741 | -0.39826
2320.2031 | 123.0331 | -122.7402 | 0.16937 | 0.10002 | 0.012629 | 0.00031197 | 0.04067 | -0.016829 | -0.0072033 | 0.013903 | 0 | 0.13275 | -0.25635 | 0.027466 | 0.07782 | 0.10529 | -0.1236 | 0.20599 | 0.19684 | -0.24719 | 122.4838 | -0.036622 | 122.7402 | 122.7676 | -0.091553 | 122.493 | 0.027465 | 0.25635 | 122.6166 | 122.9462 | 122.818 | 122.8729 | 122.7402 | 122.937 | 122.8455 | 122.493 | 122.8729 | 122.7402 | 122.8455 | 122.818 | 122.937 | -0.42572 | -0.41656
2321.8906 | 122.9599 | -122.7905 | 0.19684 | 0.15343 | 0.014552 | -0.0016106 | 0.046865 | -0.014907 | -0.011903 | 0.016893 | 0.018311 | 0.10986 | -0.2655 | 0.07782 | 0.10071 | 0.15106 | -0.17853 | 0.23346 | 0.19226 | -0.22888 | 122.525 | -0.086975 | 122.8088 | 122.8683 | -0.09613 | 122.5616 | -0.004577 | 0.28381 | 122.612 | 123.024 | 122.8912 | 122.9004 | 122.8088 | 122.9828 | 122.9416 | 122.5616 | 122.9004 | 122.8088 | 122.9416 | 122.8912 | 122.9828 | -0.46234 | -0.42572
2323.6406 | 123.0194 | -122.7631 | 0.20599 | 0.10002 | 0.012843 | 0.002021 | 0.045583 | -0.01512 | -0.011262 | 0.013903 | -0.073242 | 0.19226 | -0.28839 | -0.045776 | -0.018311 | 0.009155 | 0.027466 | 0.091553 | 0.24261 | -0.27008 | 122.4747 | -0.013733 | 122.6898 | 122.7173 | -0.22431 | 122.493 | 0.036621 | 0.21515 | 122.7905 | 122.8546 | 122.7448 | 122.9553 | 122.6898 | 123.0057 | 122.7722 | 122.493 | 122.9553 | 122.6898 | 122.7722 | 122.7448 | 123.0057 | -0.49439 | -0.47608
2325.3906 | 123.0881 | -122.7539 | 0.16479 | -0.17464 | 0.011989 | -0.00011543 | 0.044088 | -0.012984 | -0.010835 | 0.018389 | -0.068665 | 0.17395 | -0.29755 | -0.022888 | 0.032043 | 0.041199 | 0.036621 | 0.15106 | 0.22888 | -0.26093 | 122.4564 | 0.009155 | 122.6852 | 122.731 | -0.13275 | 122.493 | 0.064087 | 0.22888 | 122.7905 | 122.905 | 122.7859 | 122.9279 | 122.6852 | 122.9828 | 122.7951 | 122.493 | 122.9279 | 122.6852 | 122.7951 | 122.7859 | 122.9828 | -0.46234 | -0.42572
2327.0781 | 123.0423 | -122.7264 | 0.16022 | -0.12886 | 0.013698 | -0.0035332 | 0.038106 | -0.015334 | -0.0082715 | 0.013903 | 0.032043 | 0.14191 | -0.25635 | 0.10529 | 0.14191 | 0.18768 | -0.14191 | 0.29755 | 0.19226 | -0.23804 | 122.4701 | -0.01831 | 122.7585 | 122.8317 | -0.01831 | 122.4884 | 0.032044 | 0.28839 | 122.5845 | 123.024 | 122.8683 | 122.8683 | 122.7585 | 122.9187 | 122.9141 | 122.4884 | 122.8683 | 122.7585 | 122.9141 | 122.8683 | 122.9187 | -0.41657 | -0.39825
2328.8438 | 123.1201 | -122.7493 | 0.16479 | -0.23567 | 0.013911 | -0.0054558 | 0.041097 | -0.014907 | -0.01233 | 0.015612 | -0.082397 | 0.16022 | -0.3067 | -0.022888 | 0.009155 | 0.018311 | 0.073242 | 0.13733 | 0.23346 | -0.27466 | 122.4426 | -0.004578 | 122.6669 | 122.7264 | -0.15564 | 122.4747 | 0.068664 | 0.2243 | 122.8226 | 122.8867 | 122.7585 | 122.9095 | 122.6669 | 122.9828 | 122.7676 | 122.4747 | 122.9095 | 122.6669 | 122.7676 | 122.7585 | 122.9828 | -0.4715 | -0.43945
2330.5469 | 122.9736 | -122.7768 | 0.18768 | -0.12123 | 0.014552 | -0.00054263 | 0.045797 | -0.012557 | -0.011476 | 0.015612 | -0.027466 | 0.16479 | -0.30212 | 0.032043 | 0.050354 | 0.068665 | -0.036621 | 0.19226 | 0.21515 | -0.24719 | 122.4747 | -0.022888 | 122.7493 | 122.8088 | -0.13733 | 122.5296 | 0.027466 | 0.27466 | 122.7402 | 122.9691 | 122.8271 | 122.9416 | 122.7493 | 122.9919 | 122.8455 | 122.5296 | 122.9416 | 122.7493 | 122.8455 | 122.8271 | 122.9919 | -0.48981 | -0.43488
2332.2344 | 123.0057 | -122.7631 | 0.18768 | 0.046615 | 0.013057 | 0.0039436 | 0.046437 | -0.014907 | -0.0093395 | 0.016039 | -0.041199 | 0.16022 | -0.30212 | -0.036621 | -0.013733 | 0 | 0.013733 | 0.10071 | 0.22888 | -0.25177 | 122.4609 | -0.027466 | 122.7219 | 122.7264 | -0.20142 | 122.5113 | 0.041199 | 0.26093 | 122.7768 | 122.8638 | 122.7493 | 122.9233 | 122.7219 | 122.9919 | 122.7631 | 122.5113 | 122.9233 | 122.7219 | 122.7631 | 122.7493 | 122.9919 | -0.48981 | -0.43945
2333.9844 | 123.0606 | -122.7402 | 0.16937 | -0.22804 | 0.015407 | 0.00073917 | 0.043019 | -0.016402 | -0.010835 | 0.015398 | -0.050354 | 0.16022 | -0.29297 | -0.004578 | 0.032043 | 0.050354 | 0.022888 | 0.17395 | 0.22888 | -0.27008 | 122.4472 | -0.009156 | 122.6898 | 122.7356 | -0.13733 | 122.4701 | 0.059509 | 0.24261 | 122.7631 | 122.9141 | 122.7722 | 122.9004 | 122.6898 | 122.9691 | 122.7905 | 122.4701 | 122.9004 | 122.6898 | 122.7905 | 122.7722 | 122.9691 | -0.46234 | -0.43945
2335.7344 | 123.0148 | -122.7768 | 0.17395 | 0.092392 | 0.015834 | -0.001397 | 0.04366 | -0.013625 | -0.012544 | 0.013475 | -0.068665 | 0.16937 | -0.30212 | -0.032043 | -0.009155 | 0.027466 | -0.004578 | 0.091553 | 0.22888 | -0.2655 | 122.4747 | -0.004577 | 122.7081 | 122.7448 | -0.1831 | 122.5113 | 0.054932 | 0.23346 | 122.7722 | 122.8683 | 122.7676 | 122.9462 | 122.7081 | 123.0057 | 122.8043 | 122.5113 | 122.9462 | 122.7081 | 122.8043 | 122.7676 | 123.0057 | -0.47607 | -0.43945
2337.4844 | 123.056 | -122.7539 | 0.16022 | -0.19753 | 0.011775 | 0.0026618 | 0.039815 | -0.016829 | -0.0095531 | 0.014971 | 0.018311 | 0.12817 | -0.23346 | 0.068665 | 0.12817 | 0.16022 | -0.10986 | 0.26093 | 0.19684 | -0.23346 | 122.5204 | -0.032043 | 122.7722 | 122.8226 | -0.032043 | 122.5204 | 0.036621 | 0.25177 | 122.644 | 123.0148 | 122.8821 | 122.8821 | 122.7722 | 122.9507 | 122.9141 | 122.5204 | 122.8821 | 122.7722 | 122.9141 | 122.8821 | 122.9507 | -0.39368 | -0.39368
2339.1719 | 123.1018 | -122.7036 | 0.14648 | 0.023727 | 0.015193 | -0.003106 | 0.036824 | -0.015548 | -0.0069897 | 0.013903 | -0.027466 | 0.13733 | -0.24719 | 0.018311 | 0.068665 | 0.10986 | -0.10071 | 0.21057 | 0.20599 | -0.23346 | 122.4564 | -0.009155 | 122.6761 | 122.7219 | -0.077819 | 122.4701 | 0.05951 | 0.21973 | 122.6028 | 122.9141 | 122.7722 | 122.8409 | 122.6761 | 122.9095 | 122.8134 | 122.4701 | 122.8409 | 122.6761 | 122.8134 | 122.7722 | 122.9095 | -0.39368 | -0.37994
2340.9375 | 123.0881 | -122.731 | 0.15564 | -0.28145 | 0.013911 | -0.00054263 | 0.04131 | -0.015334 | -0.0089123 | 0.014971 | -0.013733 | 0.13733 | -0.27008 | 0.027466 | 0.059509 | 0.068665 | 0 | 0.20142 | 0.21057 | -0.25177 | 122.4609 | -0.018311 | 122.7173 | 122.7585 | -0.096131 | 122.4792 | 0.054931 | 0.25635 | 122.731 | 122.9324 | 122.7905 | 122.8683 | 122.7173 | 122.9416 | 122.7997 | 122.4792 | 122.8683 | 122.7173 | 122.7997 | 122.7905 | 122.9416 | -0.42572 | -0.40741
2342.6406 | 123.0881 | -122.7219 | 0.13733 | -0.0067901 | 0.012629 | -0.00096983 | 0.038106 | -0.014479 | -0.0097669 | 0.015612 | -0.041199 | 0.15106 | -0.25177 | 0.022888 | 0.059509 | 0.10986 | -0.082397 | 0.20599 | 0.20142 | -0.24261 | 122.4701 | 0.013733 | 122.6807 | 122.7448 | -0.07782 | 122.4792 | 0.064087 | 0.21057 | 122.6395 | 122.9279 | 122.7814 | 122.8729 | 122.6807 | 122.9233 | 122.8317 | 122.4792 | 122.8729 | 122.6807 | 122.8317 | 122.7814 | 122.9233 | -0.3891 | -0.37994
2344.3281 | 123.0789 | -122.7356 | 0.15564 | -0.029679 | 0.012416 | -0.0018244 | 0.041524 | -0.015548 | -0.010194 | 0.013475 | -0.018311 | 0.13733 | -0.26093 | 0.059509 | 0.086975 | 0.1236 | -0.10986 | 0.24261 | 0.20142 | -0.24261 | 122.4747 | -0.018311 | 122.7173 | 122.7951 | -0.068665 | 122.493 | 0.045776 | 0.24261 | 122.6257 | 122.9782 | 122.8226 | 122.8729 | 122.7173 | 122.937 | 122.8592 | 122.493 | 122.8729 | 122.7173 | 122.8592 | 122.8226 | 122.937 | -0.41657 | -0.39826
2346.0625 | 122.9645 | -122.7585 | 0.17853 | 0.17632 | 0.013698 | 0.0022346 | 0.047292 | -0.014266 | -0.010835 | 0.016253 | 0.041199 | 0.1236 | -0.24719 | 0.10071 | 0.11444 | 0.15564 | -0.19226 | 0.23804 | 0.16022 | -0.22888 | 122.5113 | -0.054932 | 122.7997 | 122.8592 | -0.064087 | 122.5296 | -0.018311 | 0.28839 | 122.5662 | 122.9965 | 122.8729 | 122.8821 | 122.7997 | 122.9187 | 122.9141 | 122.5296 | 122.8821 | 122.7997 | 122.9141 | 122.8729 | 122.9187 | -0.42572 | -0.40741
2347.7969 | 123.0469 | -122.7493 | 0.16479 | 0.092392 | 0.01562 | -0.00075623 | 0.040029 | -0.017043 | -0.0069897 | 0.014544 | -0.013733 | 0.15564 | -0.2655 | 0.032043 | 0.064087 | 0.11444 | -0.11444 | 0.20599 | 0.19226 | -0.24719 | 122.4838 | -0.009155 | 122.7356 | 122.7814 | -0.10071 | 122.5021 | 0.027466 | 0.25177 | 122.6349 | 122.9553 | 122.8134 | 122.905 | 122.7356 | 122.9416 | 122.8638 | 122.5021 | 122.905 | 122.7356 | 122.8638 | 122.8134 | 122.9416 | -0.4303 | -0.41199
2349.5156 | 122.9782 | -122.7539 | 0.20142 | -0.060196 | 0.013484 | 0.00052557 | 0.04836 | -0.013839 | -0.014039 | 0.015184 | -0.018311 | 0.14648 | -0.3067 | 0.022888 | 0.022888 | 0.041199 | -0.027466 | 0.16022 | 0.21973 | -0.26093 | 122.4472 | -0.054932 | 122.7356 | 122.7768 | -0.17853 | 122.493 | 0.018311 | 0.28839 | 122.7264 | 122.9141 | 122.7768 | 122.9004 | 122.7356 | 122.9736 | 122.7951 | 122.493 | 122.9004 | 122.7356 | 122.7951 | 122.7768 | 122.9736 | -0.50812 | -0.46234
2351.2188 | 122.9919 | -122.7631 | 0.18768 | 0.1458 | 0.012843 | 0.0041572 | 0.044515 | -0.014479 | -0.01169 | 0.018175 | -0.059509 | 0.15106 | -0.3067 | 0.004578 | 0.013733 | 0.064087 | -0.09613 | 0.15106 | 0.21973 | -0.25177 | 122.4564 | -0.036621 | 122.7036 | 122.7676 | -0.17395 | 122.5113 | 0.032044 | 0.24719 | 122.6669 | 122.9141 | 122.7768 | 122.9141 | 122.7036 | 122.9828 | 122.8271 | 122.5113 | 122.9141 | 122.7036 | 122.8271 | 122.7768 | 122.9828 | -0.49438 | -0.43945
2352.9531 | 123.0835 | -122.7539 | 0.17395 | -0.16701 | 0.015407 | 0.0026618 | 0.044942 | -0.013625 | -0.011262 | 0.013689 | -0.045776 | 0.17853 | -0.3067 | 0 | 0.027466 | 0.018311 | 0.050354 | 0.16479 | 0.24261 | -0.27466 | 122.4472 | 0.004578 | 122.7081 | 122.7539 | -0.14648 | 122.4792 | 0.068665 | 0.26093 | 122.8043 | 122.9187 | 122.7814 | 122.9324 | 122.7081 | 122.9965 | 122.7722 | 122.4792 | 122.9324 | 122.7081 | 122.7722 | 122.7814 | 122.9965 | -0.48065 | -0.44861
2354.6875 | 123.0652 | -122.7219 | 0.17853 | -0.083084 | 0.014766 | -0.0024652 | 0.034688 | -0.013839 | -0.010408 | 0.016039 | -0.013733 | 0.14191 | -0.26093 | 0.086975 | 0.13275 | 0.14648 | -0.1236 | 0.27466 | 0.19684 | -0.25635 | 122.4609 | -0.036621 | 122.7081 | 122.8088 | -0.045777 | 122.4655 | 0.01831 | 0.24719 | 122.5983 | 122.9965 | 122.8546 | 122.8638 | 122.7081 | 122.9187 | 122.8683 | 122.4655 | 122.8638 | 122.7081 | 122.8683 | 122.8546 | 122.9187 | -0.43945 | -0.43488
2356.3906 | 123.056 | -122.7493 | 0.15564 | -0.13649 | 0.012843 | -0.00032903 | 0.038747 | -0.013411 | -0.010408 | 0.015184 | 0.013733 | 0.14191 | -0.25635 | 0.091553 | 0.11902 | 0.15564 | -0.12817 | 0.29297 | 0.19684 | -0.22888 | 122.493 | -0.013733 | 122.7631 | 122.8409 | -0.036621 | 122.5204 | 0.041198 | 0.27008 | 122.6212 | 123.0423 | 122.8683 | 122.8912 | 122.7631 | 122.9462 | 122.905 | 122.5204 | 122.8912 | 122.7631 | 122.905 | 122.8683 | 122.9462 | -0.41199 | -0.38452
2358.1562 | 123.0423 | -122.7081 | 0.17395 | -0.20515 | 0.012202 | 0.0018072 | 0.041738 | -0.014907 | -0.0091259 | 0.01433 | 0.041199 | 0.11902 | -0.26093 | 0.09613 | 0.12817 | 0.13733 | -0.10986 | 0.29297 | 0.19684 | -0.21973 | 122.4472 | -0.054931 | 122.7493 | 122.8043 | -0.045776 | 122.4884 | 0.022888 | 0.30212 | 122.5983 | 123.0011 | 122.8363 | 122.8271 | 122.7493 | 122.905 | 122.8455 | 122.4884 | 122.8271 | 122.7493 | 122.8455 | 122.8363 | 122.905 | -0.43488 | -0.39368
2359.8438 | 123.0881 | -122.7402 | 0.14648 | -0.25093 | 0.014766 | 0.0035162 | 0.043019 | -0.014266 | -0.0084851 | 0.013475 | -0.082397 | 0.1831 | -0.29755 | -0.013733 | -0.004578 | 0.004578 | 0.064087 | 0.14191 | 0.23804 | -0.28381 | 122.4426 | 0.036621 | 122.6578 | 122.7264 | -0.15106 | 122.4564 | 0.091553 | 0.21515 | 122.8043 | 122.8821 | 122.7356 | 122.9233 | 122.6578 | 122.9782 | 122.7448 | 122.4564 | 122.9233 | 122.6578 | 122.7448 | 122.7356 | 122.9782 | -0.44403 | -0.4303
2361.5312 | 123.1018 | -122.731 | 0.13733 | 0.046615 | 0.013911 | -0.00011543 | 0.040242 | -0.014479 | -0.0086987 | 0.015184 | -0.027466 | 0.13733 | -0.26093 | 0.018311 | 0.050354 | 0.07782 | -0.086975 | 0.21057 | 0.21515 | -0.26093 | 122.4701 | 0 | 122.7036 | 122.7493 | -0.086975 | 122.4701 | 0.07782 | 0.23346 | 122.644 | 122.9416 | 122.7814 | 122.8683 | 122.7036 | 122.9462 | 122.8088 | 122.4701 | 122.8683 | 122.7036 | 122.8088 | 122.7814 | 122.9462 | -0.39825 | -0.39825
2363.2188 | 123.024 | -122.7493 | 0.17853 | 0.1458 | 0.012629 | -0.0022516 | 0.041738 | -0.014266 | -0.010194 | 0.016039 | -0.009155 | 0.11902 | -0.27008 | 0.054932 | 0.091553 | 0.11902 | -0.14191 | 0.21515 | 0.18768 | -0.2243 | 122.4792 | -0.059509 | 122.7402 | 122.8043 | -0.086975 | 122.525 | 0.009155 | 0.26093 | 122.6074 | 122.9645 | 122.8409 | 122.8683 | 122.7402 | 122.937 | 122.8683 | 122.525 | 122.8683 | 122.7402 | 122.8683 | 122.8409 | 122.937 | -0.44861 | -0.40283
2364.9688 | 123.0469 | -122.7539 | 0.17395 | -0.15175 | 0.015193 | -0.0058832 | 0.039601 | -0.018538 | -0.0084851 | 0.015612 | 0.059509 | 0.13275 | -0.26093 | 0.10986 | 0.11902 | 0.14191 | -0.12817 | 0.29755 | 0.19684 | -0.21515 | 122.493 | -0.041199 | 122.8134 | 122.8638 | -0.054931 | 122.5388 | 0.022888 | 0.32043 | 122.6257 | 123.0515 | 122.8729 | 122.8867 | 122.8134 | 122.9507 | 122.8958 | 122.5388 | 122.8867 | 122.8134 | 122.8958 | 122.8729 | 122.9507 | -0.43488 | -0.3891
2366.7031 | 123.0515 | -122.7585 | 0.16937 | -0.17464 | 0.01327 | 0.00031197 | 0.045156 | -0.014052 | -0.010835 | 0.01433 | -0.027466 | 0.16022 | -0.31586 | 0.018311 | 0.036621 | 0.054932 | 0.004578 | 0.17853 | 0.24261 | -0.25177 | 122.4426 | -0.009156 | 122.731 | 122.7768 | -0.13275 | 122.5067 | 0.073242 | 0.28839 | 122.7631 | 122.937 | 122.7951 | 122.9187 | 122.731 | 123.0011 | 122.8134 | 122.5067 | 122.9187 | 122.731 | 122.8134 | 122.7951 | 123.0011 | -0.48523 | -0.42114
2368.4219 | 123.1384 | -122.731 | 0.16479 | -0.21278 | 0.014125 | 9.8166e-05 | 0.042592 | -0.015975 | -0.0089123 | 0.014116 | -0.068665 | 0.1831 | -0.29297 | -0.013733 | 0.009155 | 0.004578 | 0.050354 | 0.13275 | 0.23346 | -0.27924 | 122.438 | 0.01831 | 122.6624 | 122.7173 | -0.15564 | 122.4518 | 0.068664 | 0.2243 | 122.7814 | 122.8638 | 122.7402 | 122.9141 | 122.6624 | 122.9645 | 122.7356 | 122.4518 | 122.9141 | 122.6624 | 122.7356 | 122.7402 | 122.9645 | -0.45776 | -0.44403
2370.125 | 123.0194 | -122.7448 | 0.1831 | -0.16701 | 0.015193 | -0.0022516 | 0.047078 | -0.013198 | -0.010835 | 0.015398 | -0.009155 | 0.17395 | -0.29755 | 0.027466 | 0.050354 | 0.064087 | -0.004578 | 0.17853 | 0.23804 | -0.25635 | 122.4472 | -0.009155 | 122.7356 | 122.7722 | -0.13275 | 122.4884 | 0.054932 | 0.28839 | 122.7402 | 122.9233 | 122.7951 | 122.9187 | 122.7356 | 122.9828 | 122.8088 | 122.4884 | 122.9187 | 122.7356 | 122.8088 | 122.7951 | 122.9828 | -0.48065 | -0.43945
2371.9219 | 123.0148 | -122.7402 | 0.16937 | -0.18227 | 0.012202 | 0.0041572 | 0.044728 | -0.014907 | -0.013185 | 0.013689 | -0.036621 | 0.16022 | -0.28839 | 0.022888 | 0.050354 | 0.059509 | -0.004578 | 0.16479 | 0.2243 | -0.2655 | 122.4518 | -0.009156 | 122.7036 | 122.7631 | -0.11902 | 122.4747 | 0.054931 | 0.25177 | 122.7356 | 122.905 | 122.7905 | 122.9004 | 122.7036 | 122.9645 | 122.7997 | 122.4747 | 122.9004 | 122.7036 | 122.7997 | 122.7905 | 122.9645 | -0.45776 | -0.43488
2373.7031 | 123.0606 | -122.7676 | 0.17395 | -0.22804 | 0.012416 | -0.0054558 | 0.045369 | -0.012343 | -0.01169 | 0.015184 | -0.059509 | 0.16937 | -0.30212 | 0.013733 | 0.054932 | 0.059509 | 0.009155 | 0.16937 | 0.21973 | -0.25635 | 122.4655 | -0.004577 | 122.7081 | 122.7814 | -0.11902 | 122.5113 | 0.045777 | 0.24261 | 122.7768 | 122.937 | 122.8226 | 122.937 | 122.7081 | 122.9874 | 122.8271 | 122.5113 | 122.937 | 122.7081 | 122.8271 | 122.8226 | 122.9874 | -0.47607 | -0.4303
2375.3906 | 122.9599 | -122.7997 | 0.19684 | -0.098343 | 0.014125 | 0.00052557 | 0.045583 | -0.01277 | -0.011049 | 0.013475 | -0.004578 | 0.15564 | -0.29755 | 0.032043 | 0.059509 | 0.068665 | -0.027466 | 0.17395 | 0.21973 | -0.25635 | 122.5021 | -0.041198 | 122.7951 | 122.8317 | -0.13733 | 122.5433 | 0.022889 | 0.29297 | 122.7722 | 122.9736 | 122.8592 | 122.9553 | 122.7951 | 123.0194 | 122.8683 | 122.5433 | 122.9553 | 122.7951 | 122.8683 | 122.8592 | 123.0194 | -0.49438 | -0.45319
2377.1406 | 123.0927 | -122.7448 | 0.16479 | 0.061874 | 0.015834 | -0.0022516 | 0.036184 | -0.014266 | -0.0099805 | 0.012835 | -0.032043 | 0.16022 | -0.26093 | 0.009155 | 0.07782 | 0.09613 | -0.068665 | 0.20142 | 0.20599 | -0.23804 | 122.4838 | -0.004578 | 122.7127 | 122.7539 | -0.086975 | 122.5067 | 0.041199 | 0.22888 | 122.6761 | 122.9462 | 122.8226 | 122.905 | 122.7127 | 122.9507 | 122.8409 | 122.5067 | 122.905 | 122.7127 | 122.8409 | 122.8226 | 122.9507 | -0.42572 | -0.40283
2378.9062 | 123.0194 | -122.7768 | 0.16479 | 0.15343 | 0.013484 | -0.0033196 | 0.045369 | -0.012984 | -0.0095531 | 0.015398 | -0.082397 | 0.17853 | -0.28381 | -0.050354 | -0.018311 | 0 | 0.009155 | 0.091553 | 0.2243 | -0.27008 | 122.493 | 0.013733 | 122.6944 | 122.7264 | -0.18311 | 122.5067 | 0.059509 | 0.20142 | 122.7859 | 122.8683 | 122.7585 | 122.9553 | 122.6944 | 123.0011 | 122.7768 | 122.5067 | 122.9553 | 122.6944 | 122.7768 | 122.7585 | 123.0011 | -0.44861 | -0.43488
2380.6562 | 123.0606 | -122.7585 | 0.17853 | -0.21278 | 0.013484 | -0.0063104 | 0.044728 | -0.015334 | -0.01169 | 0.014971 | -0.059509 | 0.17853 | -0.30212 | 0 | 0.041199 | 0.054932 | 0.018311 | 0.16479 | 0.24261 | -0.27924 | 122.4564 | 0 | 122.699 | 122.7585 | -0.13733 | 122.4792 | 0.064087 | 0.24261 | 122.7768 | 122.9233 | 122.7997 | 122.937 | 122.699 | 123.0011 | 122.8134 | 122.4792 | 122.937 | 122.699 | 122.8134 | 122.7997 | 123.0011 | -0.48065 | -0.45776
2382.3438 | 123.0103 | -122.7631 | 0.17395 | 0.15343 | 0.014338 | -0.00032903 | 0.042592 | -0.012984 | -0.010621 | 0.017107 | -0.07782 | 0.17853 | -0.28839 | -0.045776 | -0.018311 | 0.032043 | -0.004578 | 0.09613 | 0.22888 | -0.2655 | 122.4747 | 0.004578 | 122.6852 | 122.7173 | -0.19226 | 122.4976 | 0.054932 | 0.21057 | 122.7585 | 122.8592 | 122.7448 | 122.9416 | 122.6852 | 122.9919 | 122.7951 | 122.4976 | 122.9416 | 122.6852 | 122.7951 | 122.7448 | 122.9919 | -0.46234 | -0.43945
2384.0938 | 123.0927 | -122.7402 | 0.15564 | -0.19753 | 0.014979 | 0.003089 | 0.042379 | -0.015334 | -0.0078443 | 0.013689 | -0.054932 | 0.18768 | -0.29297 | -0.022888 | 0.032043 | 0 | 0.050354 | 0.13275 | 0.23804 | -0.27008 | 122.4472 | 0.032043 | 122.6852 | 122.7173 | -0.1236 | 122.4701 | 0.082397 | 0.23804 | 122.7905 | 122.8729 | 122.7722 | 122.9279 | 122.6852 | 122.9782 | 122.7402 | 122.4701 | 122.9279 | 122.6852 | 122.7402 | 122.7722 | 122.9782 | -0.44861 | -0.42572
2385.8438 | 122.9691 | -122.7631 | 0.21515 | -0.098343 | 0.015834 | 0.0011664 | 0.044942 | -0.012984 | -0.011903 | 0.01433 | -0.004578 | 0.16937 | -0.29755 | 0.045776 | 0.064087 | 0.068665 | -0.018311 | 0.18768 | 0.23804 | -0.24719 | 122.4655 | -0.045776 | 122.7585 | 122.8088 | -0.15106 | 122.5159 | 0.022888 | 0.29297 | 122.7448 | 122.9507 | 122.8271 | 122.9324 | 122.7585 | 123.0011 | 122.8317 | 122.5159 | 122.9324 | 122.7585 | 122.8317 | 122.8271 | 123.0011 | -0.5127 | -0.46234
2387.5938 | 123.0698 | -122.7722 | 0.16937 | -0.19753 | 0.014979 | -0.00075623 | 0.042379 | -0.014479 | -0.0099805 | 0.014116 | -0.045776 | 0.1831 | -0.28839 | 0.018311 | 0.036621 | 0.050354 | 0.004578 | 0.17853 | 0.24261 | -0.25177 | 122.4838 | 0.013732 | 122.7264 | 122.7905 | -0.13275 | 122.5204 | 0.073242 | 0.24262 | 122.7768 | 122.9507 | 122.8088 | 122.9553 | 122.7264 | 123.0148 | 122.8226 | 122.5204 | 122.9553 | 122.7264 | 122.8226 | 122.8088 | 123.0148 | -0.45776 | -0.42114
2389.2812 | 123.0927 | -122.7585 | 0.17395 | -0.22804 | 0.014125 | -0.00075623 | 0.03597 | -0.013411 | -0.0095531 | 0.013048 | -0.009155 | 0.15106 | -0.27466 | 0.036621 | 0.091553 | 0.11444 | -0.036621 | 0.22888 | 0.20142 | -0.25177 | 122.4838 | -0.022888 | 122.7493 | 122.7951 | -0.082397 | 122.5067 | 0.027466 | 0.2655 | 122.7219 | 122.9874 | 122.85 | 122.9095 | 122.7493 | 122.9599 | 122.8729 | 122.5067 | 122.9095 | 122.7493 | 122.8729 | 122.85 | 122.9599 | -0.44861 | -0.42572
2391.0469 | 123.024 | -122.7722 | 0.16937 | 0.10765 | 0.013911 | 0.00052557 | 0.043019 | -0.013198 | -0.011049 | 0.014544 | -0.091553 | 0.1831 | -0.32044 | -0.041199 | -0.018311 | 0.009155 | 0.004578 | 0.091553 | 0.23804 | -0.26093 | 122.4518 | 0.013732 | 122.6807 | 122.731 | -0.18768 | 122.5113 | 0.068664 | 0.22888 | 122.7768 | 122.8638 | 122.7539 | 122.9553 | 122.6807 | 123.0103 | 122.7814 | 122.5113 | 122.9553 | 122.6807 | 122.7814 | 122.7539 | 123.0103 | -0.48981 | -0.4303
2392.7969 | 123.0011 | -122.7768 | 0.19226 | 0.13054 | 0.014552 | 0.0024482 | 0.038961 | -0.014266 | -0.0089123 | 0.014544 | 0.013733 | 0.10986 | -0.25177 | 0.032043 | 0.10529 | 0.14648 | -0.16937 | 0.23804 | 0.19226 | -0.24261 | 122.525 | -0.082398 | 122.7905 | 122.8088 | -0.086975 | 122.5342 | 0 | 0.2655 | 122.6074 | 123.0148 | 122.8821 | 122.8867 | 122.7905 | 122.9691 | 122.9233 | 122.5342 | 122.8867 | 122.7905 | 122.9233 | 122.8821 | 122.9691 | -0.44403 | -0.43488
2394.5469 | 123.056 | -122.7539 | 0.17395 | -0.1899 | 0.014338 | -0.001397 | 0.043874 | -0.014907 | -0.0095531 | 0.015612 | -0.036621 | 0.17395 | -0.31128 | 0.022888 | 0.022888 | 0.041199 | 0.009155 | 0.18768 | 0.23804 | -0.27924 | 122.4426 | 0 | 122.7173 | 122.7768 | -0.15106 | 122.4747 | 0.064087 | 0.27466 | 122.7631 | 122.9416 | 122.7768 | 122.9279 | 122.7173 | 122.9919 | 122.7951 | 122.4747 | 122.9279 | 122.7173 | 122.7951 | 122.7768 | 122.9919 | -0.48523 | -0.45319
2396.25 | 123.0881 | -122.7219 | 0.15106 | -0.037308 | 0.014125 | -0.0016106 | 0.03597 | -0.015334 | -0.0080579 | 0.014757 | -0.018311 | 0.14191 | -0.2655 | 0.050354 | 0.091553 | 0.13275 | -0.11444 | 0.24719 | 0.20142 | -0.25177 | 122.4564 | -0.009155 | 122.7036 | 122.7722 | -0.059509 | 122.4701 | 0.050354 | 0.24719 | 122.6074 | 122.9691 | 122.8134 | 122.8638 | 122.7036 | 122.9233 | 122.8546 | 122.4701 | 122.8638 | 122.7036 | 122.8546 | 122.8134 | 122.9233 | -0.41656 | -0.40283
2398 | 122.9782 | -122.7814 | 0.19226 | -0.090714 | 0.013911 | 0.00138 | 0.046437 | -0.01512 | -0.013185 | 0.01433 | 0 | 0.17395 | -0.29297 | 0.022888 | 0.032043 | 0.050354 | -0.036621 | 0.17395 | 0.21057 | -0.25177 | 122.4884 | -0.018311 | 122.7814 | 122.8043 | -0.16022 | 122.5296 | 0.01831 | 0.29297 | 122.7448 | 122.9553 | 122.8134 | 122.9553 | 122.7814 | 122.9919 | 122.8317 | 122.5296 | 122.9553 | 122.7814 | 122.8317 | 122.8134 | 122.9919 | -0.48523 | -0.44403
2399.75 | 123.024 | -122.7814 | 0.1831 | 0.15343 | 0.012629 | -0.0039606 | 0.044942 | -0.012343 | -0.010194 | 0.014544 | -0.073242 | 0.1831 | -0.29755 | -0.027466 | 0.004578 | 0.027466 | -0.022888 | 0.11444 | 0.22888 | -0.27008 | 122.4838 | 0 | 122.7081 | 122.7539 | -0.17853 | 122.5113 | 0.045777 | 0.2243 | 122.7585 | 122.8958 | 122.7859 | 122.9645 | 122.7081 | 123.0103 | 122.8088 | 122.5113 | 122.9645 | 122.7081 | 122.8088 | 122.7859 | 123.0103 | -0.48065 | -0.45319
2401.5312 | 122.9874 | -122.7631 | 0.19684 | -0.022049 | 0.012629 | -0.0026788 | 0.044728 | -0.013839 | -0.014253 | 0.015398 | -0.022888 | 0.16022 | -0.29755 | 0.013733 | 0.018311 | 0.036621 | -0.022888 | 0.14191 | 0.21515 | -0.27008 | 122.4655 | -0.036621 | 122.7402 | 122.7768 | -0.17853 | 122.493 | 0.018311 | 0.27466 | 122.7402 | 122.905 | 122.7814 | 122.9233 | 122.7402 | 122.9782 | 122.7997 | 122.493 | 122.9233 | 122.7402 | 122.7997 | 122.7814 | 122.9782 | -0.49438 | -0.46692
2403.2188 | 122.9874 | -122.7859 | 0.20599 | -0.060196 | 0.01562 | 0.00138 | 0.044088 | -0.011916 | -0.011049 | 0.015184 | -0.009155 | 0.17853 | -0.28381 | 0.022888 | 0.036621 | 0.059509 | -0.018311 | 0.16479 | 0.23346 | -0.27466 | 122.5021 | -0.027466 | 122.7768 | 122.8088 | -0.16937 | 122.5113 | 0.027465 | 0.27466 | 122.7676 | 122.9507 | 122.8226 | 122.9645 | 122.7768 | 123.0194 | 122.8455 | 122.5113 | 122.9645 | 122.7768 | 122.8455 | 122.8226 | 123.0194 | -0.48981 | -0.48065
2404.9688 | 122.9736 | -122.7722 | 0.19684 | -0.075455 | 0.015407 | 0.00052557 | 0.044301 | -0.014479 | -0.010194 | 0.014971 | -0.013733 | 0.16479 | -0.28839 | 0.018311 | 0.059509 | 0.073242 | -0.032043 | 0.18768 | 0.2243 | -0.2655 | 122.4838 | -0.032043 | 122.7585 | 122.7905 | -0.13733 | 122.5067 | 0.027466 | 0.27466 | 122.7402 | 122.9599 | 122.8317 | 122.937 | 122.7585 | 122.9965 | 122.8455 | 122.5067 | 122.937 | 122.7585 | 122.8455 | 122.8317 | 122.9965 | -0.48523 | -0.46234
2406.6719 | 123.0972 | -122.7264 | 0.15564 | 0.038986 | 0.013698 | -0.0041742 | 0.036611 | -0.016616 | -0.0084851 | 0.016466 | -0.041199 | 0.15106 | -0.24719 | 0 | 0.064087 | 0.10986 | -0.07782 | 0.20142 | 0.21973 | -0.25177 | 122.4792 | -0.004578 | 122.6852 | 122.7264 | -0.091553 | 122.4747 | 0.064087 | 0.20599 | 122.6486 | 122.9279 | 122.7905 | 122.8775 | 122.6852 | 122.9462 | 122.8363 | 122.4747 | 122.8775 | 122.6852 | 122.8363 | 122.7905 | 122.9462 | -0.40283 | -0.40741
2408.375 | 123.0698 | -122.7539 | 0.16479 | -0.1899 | 0.013057 | 0.002021 | 0.039601 | -0.017043 | -0.0093395 | 0.016893 | 0.022888 | 0.14191 | -0.26093 | 0.073242 | 0.11444 | 0.13733 | -0.10529 | 0.28839 | 0.20142 | -0.25177 | 122.493 | -0.022888 | 122.7768 | 122.8271 | -0.050354 | 122.5021 | 0.036621 | 0.28381 | 122.6486 | 123.0423 | 122.8683 | 122.8958 | 122.7768 | 122.9553 | 122.8912 | 122.5021 | 122.8958 | 122.7768 | 122.8912 | 122.8683 | 122.9553 | -0.42572 | -0.41656
2410.125 | 122.9828 | -122.7951 | 0.17853 | -0.067826 | 0.014766 | 0.0022346 | 0.047506 | -0.014693 | -0.010194 | 0.015825 | -0.022888 | 0.16479 | -0.30212 | 0.027466 | 0.027466 | 0.054932 | -0.027466 | 0.17395 | 0.23346 | -0.2655 | 122.493 | -0.013733 | 122.7722 | 122.8226 | -0.15106 | 122.5296 | 0.054931 | 0.27924 | 122.7676 | 122.9691 | 122.8226 | 122.9599 | 122.7722 | 123.0286 | 122.85 | 122.5296 | 122.9599 | 122.7722 | 122.85 | 122.8226 | 123.0286 | -0.48065 | -0.44403
2411.8281 | 123.1293 | -122.7356 | 0.14648 | -0.22041 | 0.012416 | -0.003106 | 0.041097 | -0.015761 | -0.010621 | 0.014116 | -0.082397 | 0.16022 | -0.28839 | -0.032043 | 0.009155 | 0.013733 | 0.07782 | 0.14191 | 0.22888 | -0.28839 | 122.4472 | 0.013733 | 122.6532 | 122.7036 | -0.13733 | 122.4472 | 0.082398 | 0.20599 | 122.8134 | 122.8775 | 122.7448 | 122.8958 | 122.6532 | 122.9645 | 122.7493 | 122.4472 | 122.8958 | 122.6532 | 122.7493 | 122.7448 | 122.9645 | -0.43488 | -0.43488
2413.5312 | 123.1338 | -122.7585 | 0.15564 | -0.21278 | 0.010707 | -0.00075623 | 0.040883 | -0.015334 | -0.011049 | 0.01433 | -0.09613 | 0.16937 | -0.31586 | -0.022888 | 0.009155 | 0.013733 | 0.059509 | 0.14648 | 0.23804 | -0.27008 | 122.4426 | 0.013733 | 122.6624 | 122.7356 | -0.14649 | 122.4884 | 0.082397 | 0.21973 | 122.818 | 122.905 | 122.7676 | 122.9279 | 122.6624 | 122.9965 | 122.7722 | 122.4884 | 122.9279 | 122.6624 | 122.7722 | 122.7676 | 122.9965 | -0.4715 | -0.42572
2415.2812 | 123.0148 | -122.7768 | 0.19684 | 0.069504 | 0.014766 | 0.0026618 | 0.045797 | -0.011702 | -0.011903 | 0.01433 | -0.064087 | 0.16479 | -0.31128 | -0.045776 | -0.027466 | 0.009155 | 0.013733 | 0.091553 | 0.22888 | -0.27008 | 122.4655 | -0.032043 | 122.7127 | 122.731 | -0.2243 | 122.5067 | 0.032044 | 0.24719 | 122.7905 | 122.8683 | 122.7493 | 122.9416 | 122.7127 | 123.0057 | 122.7859 | 122.5067 | 122.9416 | 122.7127 | 122.7859 | 122.7493 | 123.0057 | -0.50812 | -0.46692
2417.0469 | 123.0972 | -122.7356 | 0.16022 | -0.20515 | 0.014979 | -0.00011543 | 0.041524 | -0.015975 | -0.0089123 | 0.01433 | -0.07782 | 0.19226 | -0.30212 | -0.022888 | -0.004578 | 0.022888 | 0.059509 | 0.14648 | 0.25635 | -0.2655 | 122.4335 | 0.032044 | 122.6578 | 122.7127 | -0.16479 | 122.4701 | 0.096131 | 0.2243 | 122.7951 | 122.8821 | 122.731 | 122.9279 | 122.6578 | 122.9919 | 122.7585 | 122.4701 | 122.9279 | 122.6578 | 122.7585 | 122.731 | 122.9919 | -0.46234 | -0.42572
2418.8125 | 123.1018 | -122.7448 | 0.16022 | -0.0067901 | 0.012416 | -0.0041742 | 0.036184 | -0.014266 | -0.0093395 | 0.013689 | -0.050354 | 0.15564 | -0.26093 | 0.022888 | 0.091553 | 0.10071 | -0.091553 | 0.21515 | 0.20142 | -0.2655 | 122.4838 | -0.004577 | 122.6944 | 122.7676 | -0.068664 | 122.4792 | 0.041199 | 0.21057 | 122.6532 | 122.9599 | 122.8363 | 122.9004 | 122.6944 | 122.9462 | 122.8455 | 122.4792 | 122.9004 | 122.6944 | 122.8455 | 122.8363 | 122.9462 | -0.42114 | -0.42572
2420.5 | 123.0377 | -122.7539 | 0.18768 | 0.16106 | 0.013698 | 0.0018072 | 0.047506 | -0.011702 | -0.0095531 | 0.011766 | -0.07782 | 0.1831 | -0.30212 | -0.036621 | -0.018311 | 0 | -0.009155 | 0.09613 | 0.21973 | -0.2655 | 122.4518 | -0.004578 | 122.6761 | 122.7173 | -0.20599 | 122.4884 | 0.032044 | 0.2243 | 122.7448 | 122.85 | 122.7356 | 122.937 | 122.6761 | 122.9736 | 122.7539 | 122.4884 | 122.937 | 122.6761 | 122.7539 | 122.7356 | 122.9736 | -0.48981 | -0.45319
2422.2031 | 122.9645 | -122.7905 | 0.18768 | 0.18394 | 0.01562 | 0.00031197 | 0.045369 | -0.013839 | -0.0091259 | 0.014757 | -0.004578 | 0.13733 | -0.27466 | 0.059509 | 0.091553 | 0.14191 | -0.14648 | 0.21973 | 0.20599 | -0.24719 | 122.5159 | -0.050354 | 122.7859 | 122.85 | -0.09613 | 122.5433 | 0.018311 | 0.27008 | 122.644 | 123.0103 | 122.8821 | 122.9279 | 122.7859 | 122.9965 | 122.9324 | 122.5433 | 122.9279 | 122.7859 | 122.9324 | 122.8821 | 122.9965 | -0.46234 | -0.43488
2423.9531 | 123.0835 | -122.7448 | 0.16479 | -0.17464 | 0.017116 | 0.0060798 | 0.044942 | -0.014907 | -0.010621 | 0.014971 | -0.064087 | 0.1831 | -0.27466 | -0.004578 | 0.022888 | 0.032043 | 0.022888 | 0.16479 | 0.22888 | -0.27466 | 122.4701 | 0.01831 | 122.6807 | 122.7402 | -0.14191 | 122.4701 | 0.064087 | 0.21057 | 122.7676 | 122.9095 | 122.7676 | 122.9279 | 122.6807 | 122.9736 | 122.7768 | 122.4701 | 122.9279 | 122.6807 | 122.7768 | 122.7676 | 122.9736 | -0.43945 | -0.43945
2425.7031 | 122.9599 | -122.7859 | 0.20142 | 0.16869 | 0.012843 | 9.8166e-05 | 0.044942 | -0.013625 | -0.0093395 | 0.01433 | 0.036621 | 0.13275 | -0.24719 | 0.073242 | 0.10986 | 0.15106 | -0.19226 | 0.24261 | 0.17853 | -0.2243 | 122.5388 | -0.068665 | 122.8226 | 122.8592 | -0.091553 | 122.5616 | -0.022888 | 0.28381 | 122.5937 | 123.0286 | 122.8958 | 122.9187 | 122.8226 | 122.9645 | 122.937 | 122.5616 | 122.9187 | 122.8226 | 122.937 | 122.8958 | 122.9645 | -0.44861 | -0.42572
2427.4062 | 123.0927 | -122.7539 | 0.16937 | -0.17464 | 0.015193 | 0.00073917 | 0.044088 | -0.014052 | -0.011262 | 0.013903 | -0.054932 | 0.17853 | -0.3067 | -0.009155 | 0.009155 | 0.013733 | 0.054932 | 0.15564 | 0.22888 | -0.27008 | 122.4472 | 0.009155 | 122.699 | 122.7448 | -0.16022 | 122.4838 | 0.059509 | 0.25177 | 122.8088 | 122.9095 | 122.7631 | 122.9324 | 122.699 | 122.9828 | 122.7676 | 122.4838 | 122.9324 | 122.699 | 122.7676 | 122.7631 | 122.9828 | -0.47607 | -0.43945
2429.1562 | 122.9874 | -122.7814 | 0.18768 | 0.16106 | 0.01327 | -0.003106 | 0.040456 | -0.01277 | -0.011262 | 0.013048 | 0.027466 | 0.13275 | -0.25177 | 0.07782 | 0.10986 | 0.15106 | -0.17395 | 0.23804 | 0.17853 | -0.21973 | 122.5296 | -0.054932 | 122.8088 | 122.8592 | -0.07782 | 122.5616 | -0.009155 | 0.27924 | 122.6074 | 123.0194 | 122.8912 | 122.9141 | 122.8088 | 122.9599 | 122.9324 | 122.5616 | 122.9141 | 122.8088 | 122.9324 | 122.8912 | 122.9599 | -0.43945 | -0.40741
2430.9062 | 122.9828 | -122.7905 | 0.19226 | -0.098343 | 0.012202 | 0.002021 | 0.047078 | -0.013625 | -0.0093395 | 0.013903 | -0.004578 | 0.15564 | -0.3067 | 0.036621 | 0.050354 | 0.054932 | -0.032043 | 0.19684 | 0.20599 | -0.25635 | 122.4838 | -0.036621 | 122.7859 | 122.8271 | -0.14191 | 122.5342 | 0.013733 | 0.30212 | 122.7585 | 122.9874 | 122.8409 | 122.9462 | 122.7859 | 122.9965 | 122.8455 | 122.5342 | 122.9462 | 122.7859 | 122.8455 | 122.8409 | 122.9965 | -0.49896 | -0.44861
2432.5938 | 122.9919 | -122.7585 | 0.18768 | 0.13054 | 0.012629 | 0.00095277 | 0.03832 | -0.01512 | -0.011049 | 0.014971 | -0.004578 | 0.12817 | -0.27008 | 0.059509 | 0.09613 | 0.14648 | -0.15564 | 0.24719 | 0.17853 | -0.26093 | 122.4884 | -0.059509 | 122.7539 | 122.818 | -0.091553 | 122.4976 | -0.009155 | 0.2655 | 122.6028 | 123.0057 | 122.8546 | 122.8867 | 122.7539 | 122.937 | 122.905 | 122.4976 | 122.8867 | 122.7539 | 122.905 | 122.8546 | 122.937 | -0.45776 | -0.44861
2434.2812 | 123.0331 | -122.7585 | 0.1831 | 0.092392 | 0.014766 | 0.00095277 | 0.046437 | -0.013411 | -0.0097669 | 0.014544 | -0.073242 | 0.18768 | -0.31128 | -0.045776 | -0.013733 | 0.009155 | -0.004578 | 0.086975 | 0.23804 | -0.27924 | 122.4472 | 0.004578 | 122.6852 | 122.7127 | -0.19684 | 122.4792 | 0.054932 | 0.23804 | 122.7539 | 122.8455 | 122.7448 | 122.9462 | 122.6852 | 122.9965 | 122.7676 | 122.4792 | 122.9462 | 122.6852 | 122.7676 | 122.7448 | 122.9965 | -0.49438 | -0.46234
2436.0469 | 122.9919 | -122.7631 | 0.18768 | 0.1992 | 0.010921 | 0.003089 | 0.042165 | -0.015334 | -0.012758 | 0.014544 | 0.032043 | 0.14191 | -0.27466 | 0.068665 | 0.10529 | 0.15564 | -0.20599 | 0.25635 | 0.18768 | -0.24261 | 122.4884 | -0.045776 | 122.7951 | 122.8317 | -0.082397 | 122.5204 | 0 | 0.3067 | 122.5571 | 123.0194 | 122.8683 | 122.905 | 122.7951 | 122.9507 | 122.9187 | 122.5204 | 122.905 | 122.7951 | 122.9187 | 122.8683 | 122.9507 | -0.46234 | -0.4303
2437.7969 | 123.0927 | -122.7402 | 0.16937 | 0.069504 | 0.014338 | 0.0024482 | 0.040029 | -0.014052 | -0.0095531 | 0.014544 | -0.013733 | 0.14191 | -0.25635 | 0.022888 | 0.068665 | 0.09613 | -0.10529 | 0.20142 | 0.20599 | -0.24261 | 122.4838 | -0.027466 | 122.7264 | 122.7631 | -0.10071 | 122.4976 | 0.036621 | 0.24262 | 122.6349 | 122.9416 | 122.8088 | 122.8821 | 122.7264 | 122.9462 | 122.8363 | 122.4976 | 122.8821 | 122.7264 | 122.8363 | 122.8088 | 122.9462 | -0.42572 | -0.41199
2439.5469 | 123.0148 | -122.7631 | 0.20599 | 0.10765 | 0.013057 | 0.00095277 | 0.047506 | -0.014693 | -0.010835 | 0.01433 | -0.064087 | 0.16937 | -0.29755 | -0.022888 | -0.009155 | 0 | 0.013733 | 0.10529 | 0.23346 | -0.27466 | 122.4655 | -0.036621 | 122.699 | 122.7402 | -0.21515 | 122.4884 | 0.027465 | 0.23346 | 122.7768 | 122.8683 | 122.7539 | 122.9324 | 122.699 | 122.9965 | 122.7631 | 122.4884 | 122.9324 | 122.699 | 122.7631 | 122.7539 | 122.9965 | -0.50354 | -0.48065
2441.25 | 123.0286 | -122.7814 | 0.1831 | 0.092392 | 0.01327 | 0.0026618 | 0.043233 | -0.012984 | -0.010194 | 0.016253 | -0.073242 | 0.1831 | -0.3067 | -0.027466 | -0.009155 | 0.018311 | -0.027466 | 0.10529 | 0.22888 | -0.27466 | 122.4747 | 0 | 122.7081 | 122.7539 | -0.19226 | 122.5067 | 0.045777 | 0.23346 | 122.7539 | 122.8867 | 122.7722 | 122.9645 | 122.7081 | 123.0103 | 122.7997 | 122.5067 | 122.9645 | 122.7081 | 122.7997 | 122.7722 | 123.0103 | -0.48981 | -0.45776
2443.0156 | 123.0606 | -122.7448 | 0.16937 | -0.14412 | 0.01327 | -0.001397 | 0.037465 | -0.014052 | -0.0089123 | 0.015398 | 0.036621 | 0.13275 | -0.26093 | 0.091553 | 0.13733 | 0.17853 | -0.13275 | 0.31586 | 0.21057 | -0.24261 | 122.4838 | -0.036622 | 122.7814 | 122.8363 | -0.032044 | 122.5021 | 0.041198 | 0.29755 | 122.612 | 123.0606 | 122.8821 | 122.8775 | 122.7814 | 122.9553 | 122.9233 | 122.5021 | 122.8775 | 122.7814 | 122.9233 | 122.8821 | 122.9553 | -0.4303 | -0.41199
2444.7656 | 123.0331 | -122.8088 | 0.20142 | 0.11528 | 0.014552 | -0.002038 | 0.049428 | -0.014907 | -0.011903 | 0.014971 | -0.059509 | 0.17395 | -0.29297 | -0.041199 | -0.022888 | 0 | 0.018311 | 0.10986 | 0.21973 | -0.27008 | 122.5159 | -0.027466 | 122.7493 | 122.7676 | -0.2243 | 122.5388 | 0.018311 | 0.23346 | 122.8271 | 122.9187 | 122.7859 | 122.9828 | 122.7493 | 123.0286 | 122.8088 | 122.5388 | 122.9828 | 122.7493 | 122.8088 | 122.7859 | 123.0286 | -0.49438 | -0.4715
2446.5156 | 123.0698 | -122.7722 | 0.1831 | -0.1899 | 0.013698 | 0.002021 | 0.044515 | -0.013625 | -0.0097669 | 0.01433 | -0.054932 | 0.17395 | -0.31128 | 0.009155 | 0.041199 | 0.050354 | 0.013733 | 0.1831 | 0.22888 | -0.27008 | 122.4609 | -0.009155 | 122.7173 | 122.7814 | -0.14191 | 122.5021 | 0.045777 | 0.25635 | 122.7859 | 122.9553 | 122.8134 | 122.9462 | 122.7173 | 123.0011 | 122.8226 | 122.5021 | 122.9462 | 122.7173 | 122.8226 | 122.8134 | 123.0011 | -0.49438 | -0.45319
2448.2188 | 122.9828 | -122.7814 | 0.16937 | 0.1992 | 0.013698 | 0.0041572 | 0.041524 | -0.011275 | -0.0097669 | 0.012835 | 0.045776 | 0.12817 | -0.26093 | 0.073242 | 0.10529 | 0.14648 | -0.18768 | 0.25177 | 0.17853 | -0.23346 | 122.5204 | -0.041199 | 122.8271 | 122.8546 | -0.064087 | 122.5479 | 0.009155 | 0.3067 | 122.5937 | 123.0331 | 122.8867 | 122.9095 | 122.8271 | 122.9599 | 122.9279 | 122.5479 | 122.9095 | 122.8271 | 122.9279 | 122.8867 | 122.9599 | -0.4303 | -0.40283
2449.9062 | 122.9965 | -122.7859 | 0.19226 | 0.15343 | 0.012202 | -0.002038 | 0.041097 | -0.014907 | -0.011049 | 0.014971 | 0.018311 | 0.1236 | -0.26093 | 0.068665 | 0.10986 | 0.14648 | -0.16479 | 0.24719 | 0.1831 | -0.22888 | 122.525 | -0.068665 | 122.8043 | 122.8546 | -0.082398 | 122.5571 | -0.009156 | 0.27924 | 122.6212 | 123.0331 | 122.8958 | 122.9095 | 122.8043 | 122.9691 | 122.9324 | 122.5571 | 122.9095 | 122.8043 | 122.9324 | 122.8958 | 122.9691 | -0.45319 | -0.42114
2451.5938 | 123.1064 | -122.7173 | 0.14191 | 0.0084684 | 0.012202 | 0.00031197 | 0.03832 | -0.01747 | -0.0069897 | 0.012835 | -0.041199 | 0.16022 | -0.27008 | 0.022888 | 0.073242 | 0.10071 | -0.091553 | 0.21973 | 0.20599 | -0.27924 | 122.4472 | 0.01831 | 122.6761 | 122.7402 | -0.068665 | 122.438 | 0.064087 | 0.22888 | 122.6257 | 122.937 | 122.7905 | 122.8775 | 122.6761 | 122.9233 | 122.818 | 122.438 | 122.8775 | 122.6761 | 122.818 | 122.7905 | 122.9233 | -0.41199 | -0.42114
2453.2969 | 123.0103 | -122.7722 | 0.18768 | -0.15175 | 0.012629 | 0.002021 | 0.046437 | -0.014693 | -0.013185 | 0.013262 | -0.036621 | 0.15106 | -0.32501 | 0.041199 | 0.036621 | 0.050354 | -0.018311 | 0.19684 | 0.24261 | -0.25635 | 122.4472 | -0.036621 | 122.7356 | 122.8134 | -0.15106 | 122.5159 | 0.054932 | 0.28839 | 122.7539 | 122.9691 | 122.8088 | 122.9233 | 122.7356 | 123.0148 | 122.8226 | 122.5159 | 122.9233 | 122.7356 | 122.8226 | 122.8088 | 123.0148 | -0.5127 | -0.44403
2455.0469 | 122.9691 | -122.7997 | 0.21057 | -0.083084 | 0.013484 | 0.0011664 | 0.045797 | -0.013839 | -0.011049 | 0.015184 | -0.022888 | 0.15564 | -0.30212 | 0.027466 | 0.059509 | 0.09613 | -0.027466 | 0.1831 | 0.21515 | -0.26093 | 122.4976 | -0.054931 | 122.7768 | 122.8271 | -0.15106 | 122.5388 | 0.004578 | 0.27924 | 122.7722 | 122.9828 | 122.8592 | 122.9553 | 122.7768 | 123.0148 | 122.8958 | 122.5388 | 122.9553 | 122.7768 | 122.8958 | 122.8592 | 123.0148 | -0.5127 | -0.4715
2456.7969 | 123.0927 | -122.7539 | 0.16479 | -0.17464 | 0.01562 | -0.0011834 | 0.04067 | -0.016829 | -0.0089123 | 0.013903 | 0.027466 | 0.16022 | -0.2655 | 0.07782 | 0.11902 | 0.1236 | -0.064087 | 0.26093 | 0.20142 | -0.25635 | 122.4884 | -0.004578 | 122.7814 | 122.8317 | -0.045776 | 122.4976 | 0.036621 | 0.29297 | 122.6898 | 123.0148 | 122.8729 | 122.9141 | 122.7814 | 122.9553 | 122.8775 | 122.4976 | 122.9141 | 122.7814 | 122.8775 | 122.8729 | 122.9553 | -0.4303 | -0.42114
2458.5625 | 123.0331 | -122.7905 | 0.19226 | 0.061874 | 0.013911 | -0.00075623 | 0.04601 | -0.01512 | -0.0099805 | 0.015398 | -0.064087 | 0.16937 | -0.31128 | -0.041199 | -0.018311 | -0.004578 | 0.022888 | 0.09613 | 0.24261 | -0.28381 | 122.4792 | -0.022888 | 122.7264 | 122.7493 | -0.21057 | 122.5067 | 0.050354 | 0.24719 | 122.8134 | 122.8867 | 122.7722 | 122.9599 | 122.7264 | 123.0331 | 122.7859 | 122.5067 | 122.9599 | 122.7264 | 122.7859 | 122.7722 | 123.0331 | -0.50354 | -0.47607
2460.25 | 122.9782 | -122.8043 | 0.21515 | -0.083084 | 0.013057 | -0.00011543 | 0.047292 | -0.015761 | -0.011262 | 0.014971 | -0.032043 | 0.16479 | -0.28839 | 0.032043 | 0.045776 | 0.059509 | -0.027466 | 0.16022 | 0.22888 | -0.25177 | 122.5159 | -0.050354 | 122.7722 | 122.8363 | -0.16937 | 122.5525 | 0.013733 | 0.25635 | 122.7768 | 122.9645 | 122.85 | 122.9691 | 122.7722 | 123.0331 | 122.8638 | 122.5525 | 122.9691 | 122.7722 | 122.8638 | 122.85 | 123.0331 | -0.50354 | -0.46692
2462 | 123.1155 | -122.7448 | 0.16022 | -0.22804 | 0.013057 | 0.00052557 | 0.041951 | -0.014052 | -0.0095531 | 0.013048 | -0.09613 | 0.19684 | -0.31128 | -0.041199 | 0.009155 | 0.004578 | 0.045776 | 0.14648 | 0.24261 | -0.28839 | 122.4335 | 0.036621 | 122.6486 | 122.7036 | -0.15106 | 122.4564 | 0.082398 | 0.21515 | 122.7905 | 122.8912 | 122.7539 | 122.9416 | 122.6486 | 122.9874 | 122.7493 | 122.4564 | 122.9416 | 122.6486 | 122.7493 | 122.7539 | 122.9874 | -0.4715 | -0.44861
2463.75 | 123.0286 | -122.7722 | 0.19226 | 0.10002 | 0.014338 | 0.003089 | 0.044728 | -0.013411 | -0.011476 | 0.013475 | -0.07782 | 0.16937 | -0.31128 | -0.045776 | 0 | 0.009155 | 0.027466 | 0.10071 | 0.23346 | -0.27466 | 122.4609 | -0.022888 | 122.6944 | 122.7264 | -0.19226 | 122.4976 | 0.041198 | 0.23346 | 122.7997 | 122.8729 | 122.7722 | 122.9416 | 122.6944 | 123.0057 | 122.7814 | 122.4976 | 122.9416 | 122.6944 | 122.7814 | 122.7722 | 123.0057 | -0.50354 | -0.46692
2465.5 | 123.0331 | -122.7631 | 0.17853 | 0.13817 | 0.012202 | 0.00052557 | 0.044301 | -0.014693 | -0.011049 | 0.014971 | -0.086975 | 0.17395 | -0.3067 | -0.045776 | -0.009155 | 0.009155 | -0.009155 | 0.09613 | 0.24719 | -0.27924 | 122.4564 | -0.004578 | 122.6761 | 122.7173 | -0.18768 | 122.4838 | 0.068664 | 0.21973 | 122.7539 | 122.8592 | 122.7539 | 122.937 | 122.6761 | 123.0103 | 122.7722 | 122.4838 | 122.937 | 122.6761 | 122.7722 | 122.7539 | 123.0103 | -0.48523 | -0.45776
2467.1875 | 122.9691 | -122.7814 | 0.19226 | 0.17632 | 0.011348 | -0.0041742 | 0.042806 | -0.015761 | -0.0097669 | 0.013903 | -0.004578 | 0.14191 | -0.27924 | 0.050354 | 0.09613 | 0.13733 | -0.15106 | 0.23346 | 0.18768 | -0.2243 | 122.5021 | -0.050354 | 122.7768 | 122.8317 | -0.096131 | 122.5571 | -0.004578 | 0.27466 | 122.6303 | 123.0148 | 122.8775 | 122.9233 | 122.7768 | 122.9691 | 122.9187 | 122.5571 | 122.9233 | 122.7768 | 122.9187 | 122.8775 | 122.9691 | -0.4715 | -0.41656
2468.9375 | 123.0835 | -122.7493 | 0.16937 | -0.083084 | 0.012202 | -0.0016106 | 0.035543 | -0.018111 | -0.0093395 | 0.013475 | 0.027466 | 0.14648 | -0.24719 | 0.07782 | 0.13733 | 0.16022 | -0.1236 | 0.27008 | 0.19684 | -0.24261 | 122.5021 | -0.022889 | 122.7768 | 122.8271 | -0.032044 | 122.5067 | 0.027465 | 0.27466 | 122.6257 | 123.0194 | 122.8867 | 122.8958 | 122.7768 | 122.9462 | 122.9095 | 122.5067 | 122.8958 | 122.7768 | 122.9095 | 122.8867 | 122.9462 | -0.41656 | -0.41199
2470.7031 | 123.0743 | -122.7722 | 0.16022 | -0.090714 | 0.011134 | 9.8166e-05 | 0.038533 | -0.01512 | -0.010621 | 0.013689 | 0.027466 | 0.14191 | -0.25177 | 0.10071 | 0.10986 | 0.16937 | -0.14648 | 0.30212 | 0.20599 | -0.23804 | 122.5204 | -0.01831 | 122.7997 | 122.8729 | -0.050354 | 122.5342 | 0.045777 | 0.27924 | 122.6257 | 123.0743 | 122.8821 | 122.9141 | 122.7997 | 122.9782 | 122.9416 | 122.5342 | 122.9141 | 122.7997 | 122.9416 | 122.8821 | 122.9782 | -0.41199 | -0.39825
2472.4062 | 123.0743 | -122.7493 | 0.17853 | -0.14412 | 0.013911 | 0.00031197 | 0.041738 | -0.014479 | -0.011049 | 0.013048 | 0.054932 | 0.14191 | -0.2655 | 0.10529 | 0.14648 | 0.17853 | -0.15106 | 0.28839 | 0.19226 | -0.25177 | 122.4838 | -0.036621 | 122.8043 | 122.8546 | -0.032044 | 122.4976 | 0.013733 | 0.32043 | 122.5983 | 123.0377 | 122.8958 | 122.8912 | 122.8043 | 122.9416 | 122.9279 | 122.4976 | 122.8912 | 122.8043 | 122.9279 | 122.8958 | 122.9416 | -0.44403 | -0.4303
2474.1562 | 123.0972 | -122.7493 | 0.15106 | 0.054245 | 0.014766 | -0.001397 | 0.042806 | -0.015975 | -0.0093395 | 0.014116 | -0.041199 | 0.14648 | -0.27466 | 0.022888 | 0.064087 | 0.10071 | -0.10071 | 0.21057 | 0.20599 | -0.23804 | 122.4747 | -0.004578 | 122.7081 | 122.7722 | -0.086975 | 122.5113 | 0.054932 | 0.23346 | 122.6486 | 122.9599 | 122.8134 | 122.8958 | 122.7081 | 122.9553 | 122.85 | 122.5113 | 122.8958 | 122.7081 | 122.85 | 122.8134 | 122.9553 | -0.42572 | -0.3891
2475.9062 | 123.1155 | -122.7356 | 0.14191 | 0.061874 | 0.012629 | -0.0024652 | 0.040883 | -0.015334 | -0.0093395 | 0.015184 | -0.018311 | 0.13275 | -0.27924 | 0.018311 | 0.059509 | 0.091553 | -0.09613 | 0.21057 | 0.20599 | -0.25177 | 122.4564 | -0.009156 | 122.7173 | 122.7539 | -0.082398 | 122.4838 | 0.064087 | 0.26092 | 122.6395 | 122.9462 | 122.7951 | 122.8683 | 122.7173 | 122.9416 | 122.8271 | 122.4838 | 122.8683 | 122.7173 | 122.8271 | 122.7951 | 122.9416 | -0.42114 | -0.39368
2477.6562 | 123.0789 | -122.7493 | 0.17853 | 0.077133 | 0.012202 | -0.00011543 | 0.044515 | -0.016829 | -0.0097669 | 0.015184 | -0.013733 | 0.13275 | -0.27466 | 0.036621 | 0.054932 | 0.10529 | -0.11902 | 0.21515 | 0.19226 | -0.25177 | 122.4747 | -0.045777 | 122.7356 | 122.7859 | -0.1236 | 122.4976 | 0.013733 | 0.26093 | 122.6303 | 122.9645 | 122.8043 | 122.8821 | 122.7356 | 122.9416 | 122.8546 | 122.4976 | 122.8821 | 122.7356 | 122.8546 | 122.8043 | 122.9416 | -0.45319 | -0.4303
2479.3438 | 123.0057 | -122.7859 | 0.20599 | 0.13054 | 0.012629 | 0.0045844 | 0.044942 | -0.013839 | -0.0078443 | 0.015612 | 0.022888 | 0.13733 | -0.27008 | 0.086975 | 0.09613 | 0.13275 | -0.18768 | 0.25177 | 0.17853 | -0.23804 | 122.5159 | -0.068665 | 122.8088 | 122.8729 | -0.10986 | 122.5479 | -0.027466 | 0.29297 | 122.5983 | 123.0377 | 122.8821 | 122.9233 | 122.8088 | 122.9645 | 122.9187 | 122.5479 | 122.9233 | 122.8088 | 122.9187 | 122.8821 | 122.9645 | -0.47608 | -0.44403
2481.0938 | 123.0789 | -122.7631 | 0.15564 | -0.1136 | 0.012202 | -0.0046014 | 0.041097 | -0.015548 | -0.010408 | 0.01433 | 0.022888 | 0.13733 | -0.27466 | 0.11902 | 0.13275 | 0.15106 | -0.14648 | 0.30212 | 0.1831 | -0.2243 | 122.4884 | -0.018311 | 122.7859 | 122.8821 | -0.022889 | 122.5388 | 0.027465 | 0.29755 | 122.6166 | 123.0652 | 122.8958 | 122.9004 | 122.7859 | 122.9462 | 122.9141 | 122.5388 | 122.9004 | 122.7859 | 122.9141 | 122.8958 | 122.9462 | -0.4303 | -0.37994
2482.8438 | 123.1155 | -122.7448 | 0.16022 | -0.22804 | 0.015193 | -0.00075623 | 0.046651 | -0.016616 | -0.010835 | 0.015398 | -0.064087 | 0.1831 | -0.32044 | -0.013733 | 0.004578 | 0.018311 | 0.045776 | 0.15564 | 0.23346 | -0.27924 | 122.4243 | 0.022888 | 122.6807 | 122.731 | -0.15564 | 122.4655 | 0.073242 | 0.25635 | 122.7905 | 122.9004 | 122.7493 | 122.9279 | 122.6807 | 122.9782 | 122.7631 | 122.4655 | 122.9279 | 122.6807 | 122.7631 | 122.7493 | 122.9782 | -0.48065 | -0.43945
2484.5938 | 123.1018 | -122.7493 | 0.16479 | -0.23567 | 0.01562 | 0.0015936 | 0.041097 | -0.015975 | -0.0082715 | 0.014116 | 0.018311 | 0.13733 | -0.29297 | 0.073242 | 0.086975 | 0.10529 | -0.050354 | 0.23804 | 0.20142 | -0.25635 | 122.4564 | -0.027466 | 122.7676 | 122.8226 | -0.07782 | 122.493 | 0.036621 | 0.31128 | 122.699 | 122.9874 | 122.8363 | 122.8867 | 122.7676 | 122.9507 | 122.8546 | 122.493 | 122.8867 | 122.7676 | 122.8546 | 122.8363 | 122.9507 | -0.45776 | -0.42114
2486.2812 | 123.0652 | -122.7585 | 0.15564 | -0.12886 | 0.013057 | -0.00011543 | 0.040242 | -0.015975 | -0.0097669 | 0.013262 | 0.018311 | 0.13275 | -0.27466 | 0.10986 | 0.14191 | 0.16937 | -0.14648 | 0.30212 | 0.19226 | -0.22888 | 122.4838 | -0.022889 | 122.7768 | 122.8683 | -0.013733 | 122.5296 | 0.036621 | 0.29297 | 122.612 | 123.0606 | 122.9004 | 122.8912 | 122.7768 | 122.9507 | 122.9279 | 122.5296 | 122.8912 | 122.7768 | 122.9279 | 122.9004 | 122.9507 | -0.4303 | -0.38452
2488.0469 | 123.0743 | -122.7585 | 0.16479 | -0.20515 | 0.011989 | 0.00052557 | 0.042165 | -0.016616 | -0.0089123 | 0.012835 | 0.022888 | 0.13733 | -0.26093 | 0.10071 | 0.14191 | 0.13733 | -0.1236 | 0.28839 | 0.17853 | -0.21973 | 122.4976 | -0.027466 | 122.7814 | 122.8592 | -0.022888 | 122.5388 | 0.013733 | 0.28381 | 122.6349 | 123.0469 | 122.9004 | 122.8958 | 122.7814 | 122.937 | 122.8958 | 122.5388 | 122.8958 | 122.7814 | 122.8958 | 122.9004 | 122.937 | -0.42572 | -0.38452
2489.8125 | 123.056 | -122.7539 | 0.1831 | -0.14412 | 0.013911 | -0.0067376 | 0.04131 | -0.015334 | -0.011476 | 0.016039 | 0.041199 | 0.1236 | -0.24719 | 0.11902 | 0.1236 | 0.14191 | -0.12817 | 0.30212 | 0.19226 | -0.21973 | 122.5067 | -0.059509 | 122.7951 | 122.8729 | -0.059509 | 122.5342 | 0.009156 | 0.28839 | 122.6257 | 123.056 | 122.8775 | 122.8775 | 122.7951 | 122.9462 | 122.8958 | 122.5342 | 122.8775 | 122.7951 | 122.8958 | 122.8775 | 122.9462 | -0.4303 | -0.40283
2491.5781 | 122.9874 | -122.8088 | 0.19684 | 0.13817 | 0.010921 | 0.0041572 | 0.04366 | -0.01512 | -0.010194 | 0.013475 | 0.041199 | 0.12817 | -0.27008 | 0.09613 | 0.10529 | 0.14648 | -0.1831 | 0.26093 | 0.1831 | -0.22888 | 122.5388 | -0.068664 | 122.85 | 122.905 | -0.091552 | 122.58 | -0.013733 | 0.31128 | 122.6257 | 123.0698 | 122.9141 | 122.937 | 122.85 | 122.9919 | 122.9553 | 122.58 | 122.937 | 122.85 | 122.9553 | 122.9141 | 122.9919 | -0.46692 | -0.42572
2493.3281 | 123.1201 | -122.7539 | 0.17395 | -0.32722 | 0.011775 | -0.0043878 | 0.044728 | -0.015548 | -0.011903 | 0.012835 | -0.013733 | 0.16937 | -0.28839 | 0.050354 | 0.068665 | 0.068665 | 0 | 0.18768 | 0.21515 | -0.27008 | 122.4655 | -0.004577 | 122.7402 | 122.8043 | -0.10528 | 122.4838 | 0.041199 | 0.27466 | 122.7539 | 122.9416 | 122.8226 | 122.9233 | 122.7402 | 122.9691 | 122.8226 | 122.4838 | 122.9233 | 122.7402 | 122.8226 | 122.8226 | 122.9691 | -0.46234 | -0.44403
2495.0156 | 123.0881 | -122.7539 | 0.15106 | 0.077133 | 0.014979 | -0.0046014 | 0.04131 | -0.015975 | -0.0097669 | 0.014116 | -0.022888 | 0.15106 | -0.26093 | 0.045776 | 0.054932 | 0.10529 | -0.10986 | 0.20599 | 0.19226 | -0.25635 | 122.493 | 0 | 122.731 | 122.7997 | -0.09613 | 122.4976 | 0.041199 | 0.23804 | 122.644 | 122.9599 | 122.8088 | 122.905 | 122.731 | 122.9462 | 122.8592 | 122.4976 | 122.905 | 122.731 | 122.8592 | 122.8088 | 122.9462 | -0.41199 | -0.40741
2496.7656 | 122.9919 | -122.8134 | 0.18768 | -0.083084 | 0.013057 | 0.00073917 | 0.047719 | -0.013625 | -0.011262 | 0.013689 | 0.013733 | 0.16479 | -0.3067 | 0.050354 | 0.054932 | 0.059509 | -0.032043 | 0.17853 | 0.21973 | -0.27008 | 122.5067 | -0.022888 | 122.8271 | 122.8638 | -0.13275 | 122.5433 | 0.032044 | 0.32043 | 122.7814 | 122.9919 | 122.8683 | 122.9782 | 122.8271 | 123.0331 | 122.8729 | 122.5433 | 122.9782 | 122.8271 | 122.8729 | 122.8683 | 123.0331 | -0.49438 | -0.45776
2498.5312 | 122.9919 | -122.7814 | 0.19684 | -0.098343 | 0.012843 | -0.0028924 | 0.045797 | -0.01277 | -0.013612 | 0.013689 | -0.013733 | 0.16479 | -0.27924 | 0.054932 | 0.059509 | 0.059509 | -0.027466 | 0.20142 | 0.21515 | -0.24719 | 122.5021 | -0.032043 | 122.7676 | 122.8363 | -0.13733 | 122.5342 | 0.018311 | 0.2655 | 122.7539 | 122.9828 | 122.8409 | 122.9462 | 122.7676 | 122.9965 | 122.8409 | 122.5342 | 122.9462 | 122.7676 | 122.8409 | 122.8409 | 122.9965 | -0.47607 | -0.44403
2500.2188 | 123.1201 | -122.7356 | 0.17853 | -0.26619 | 0.013698 | -0.0024652 | 0.041524 | -0.013625 | -0.01169 | 0.013048 | -0.086975 | 0.19226 | -0.31586 | -0.013733 | 0.009155 | 0.013733 | 0.064087 | 0.14191 | 0.25177 | -0.28381 | 122.4197 | 0.013733 | 122.6486 | 122.7219 | -0.16937 | 122.4518 | 0.073242 | 0.22888 | 122.7997 | 122.8775 | 122.7448 | 122.9279 | 122.6486 | 122.9874 | 122.7493 | 122.4518 | 122.9279 | 122.6486 | 122.7493 | 122.7448 | 122.9874 | -0.49438 | -0.46234
2501.9688 | 123.1064 | -122.7356 | 0.15564 | 0.069504 | 0.011561 | -0.0041742 | 0.039601 | -0.014479 | -0.0086987 | 0.015825 | -0.032043 | 0.12817 | -0.27466 | 0.022888 | 0.073242 | 0.10071 | -0.10986 | 0.21057 | 0.20142 | -0.24719 | 122.4609 | -0.027466 | 122.7036 | 122.7585 | -0.082398 | 122.4884 | 0.045776 | 0.24262 | 122.6257 | 122.9462 | 122.8088 | 122.8638 | 122.7036 | 122.937 | 122.8363 | 122.4884 | 122.8638 | 122.7036 | 122.8363 | 122.8088 | 122.937 | -0.4303 | -0.40283
2503.7188 | 123.0652 | -122.7768 | 0.16479 | -0.17464 | 0.014338 | -0.00032903 | 0.042165 | -0.01747 | -0.011049 | 0.013262 | 0.036621 | 0.13275 | -0.27466 | 0.086975 | 0.1236 | 0.14648 | -0.09613 | 0.27008 | 0.20142 | -0.23804 | 122.5021 | -0.032044 | 122.8134 | 122.8638 | -0.041199 | 122.5388 | 0.036621 | 0.31128 | 122.6807 | 123.0469 | 122.9004 | 122.9095 | 122.8134 | 122.9782 | 122.9233 | 122.5388 | 122.9095 | 122.8134 | 122.9233 | 122.9004 | 122.9782 | -0.43945 | -0.40283
2505.4062 | 123.1064 | -122.7493 | 0.17853 | -0.26619 | 0.012629 | -0.0028924 | 0.042806 | -0.015975 | -0.0099805 | 0.013048 | 0 | 0.13733 | -0.29297 | 0.050354 | 0.073242 | 0.082397 | -0.018311 | 0.21515 | 0.20599 | -0.2655 | 122.4564 | -0.041199 | 122.7493 | 122.7997 | -0.10529 | 122.4838 | 0.027466 | 0.29297 | 122.731 | 122.9645 | 122.8226 | 122.8867 | 122.7493 | 122.9553 | 122.8317 | 122.4838 | 122.8867 | 122.7493 | 122.8317 | 122.8226 | 122.9553 | -0.4715 | -0.44403
2507.1406 | 122.9965 | -122.7768 | 0.19684 | -0.075455 | 0.014552 | -0.00011543 | 0.046865 | -0.016188 | -0.011903 | 0.015612 | -0.022888 | 0.16022 | -0.31128 | 0.036621 | 0.064087 | 0.050354 | -0.018311 | 0.19684 | 0.2243 | -0.27008 | 122.4655 | -0.036621 | 122.7539 | 122.8134 | -0.13275 | 122.5067 | 0.027466 | 0.28839 | 122.7585 | 122.9736 | 122.8409 | 122.937 | 122.7539 | 123.0011 | 122.8271 | 122.5067 | 122.937 | 122.7539 | 122.8271 | 122.8409 | 123.0011 | -0.50812 | -0.46692
2508.9219 | 123.0057 | -122.7997 | 0.17853 | -0.14412 | 0.01327 | 0.0022346 | 0.046651 | -0.011489 | -0.012971 | 0.01668 | -0.032043 | 0.16022 | -0.31586 | 0.027466 | 0.054932 | 0.064087 | -0.018311 | 0.17853 | 0.22888 | -0.27924 | 122.4838 | -0.018311 | 122.7676 | 122.8271 | -0.1236 | 122.5204 | 0.050354 | 0.28381 | 122.7814 | 122.9782 | 122.8546 | 122.9599 | 122.7676 | 123.0286 | 122.8638 | 122.5204 | 122.9599 | 122.7676 | 122.8638 | 122.8546 | 123.0286 | -0.49438 | -0.45776
2510.6719 | 123.056 | -122.7631 | 0.15564 | -0.12123 | 0.012843 | -0.0035332 | 0.039388 | -0.015548 | -0.0099805 | 0.013689 | 0.045776 | 0.13275 | -0.25635 | 0.082397 | 0.13275 | 0.16479 | -0.13275 | 0.29297 | 0.20599 | -0.24719 | 122.5067 | -0.022889 | 122.8088 | 122.8455 | -0.022889 | 122.5159 | 0.050354 | 0.30212 | 122.6303 | 123.056 | 122.8958 | 122.8958 | 122.8088 | 122.9691 | 122.9279 | 122.5159 | 122.8958 | 122.8088 | 122.9279 | 122.8958 | 122.9691 | -0.41199 | -0.40283
2512.3594 | 123.1293 | -122.7493 | 0.15564 | -0.17464 | 0.014552 | -0.003106 | 0.039174 | -0.015761 | -0.010835 | 0.014116 | -0.068665 | 0.17395 | -0.3067 | -0.018311 | 0.009155 | 0.027466 | 0.073242 | 0.16022 | 0.23804 | -0.28839 | 122.4426 | 0.01831 | 122.6807 | 122.731 | -0.14649 | 122.4609 | 0.082397 | 0.23804 | 122.8226 | 122.9095 | 122.7585 | 122.9233 | 122.6807 | 122.9874 | 122.7768 | 122.4609 | 122.9233 | 122.6807 | 122.7768 | 122.7585 | 122.9874 | -0.46234 | -0.44403
2514.1094 | 122.9828 | -122.7951 | 0.19226 | -0.029679 | 0.014338 | 0.0011664 | 0.047078 | -0.014693 | -0.014039 | 0.013475 | -0.004578 | 0.16479 | -0.30212 | 0.022888 | 0.027466 | 0.054932 | -0.018311 | 0.16937 | 0.23346 | -0.2655 | 122.493 | -0.027466 | 122.7905 | 122.818 | -0.16479 | 122.5296 | 0.041198 | 0.29755 | 122.7768 | 122.9645 | 122.8226 | 122.9599 | 122.7905 | 123.0286 | 122.85 | 122.5296 | 122.9599 | 122.7905 | 122.85 | 122.8226 | 123.0286 | -0.49438 | -0.45776
2515.8594 | 122.9828 | -122.7859 | 0.18768 | -0.029679 | 0.013698 | 0.0041572 | 0.047292 | -0.012984 | -0.01169 | 0.014116 | 0 | 0.16479 | -0.28839 | 0.013733 | 0.032043 | 0.036621 | -0.004578 | 0.16022 | 0.23346 | -0.26093 | 122.4976 | -0.022888 | 122.7859 | 122.7997 | -0.15564 | 122.525 | 0.045776 | 0.28839 | 122.7814 | 122.9462 | 122.818 | 122.9507 | 122.7859 | 123.0194 | 122.8226 | 122.525 | 122.9507 | 122.7859 | 122.8226 | 122.818 | 123.0194 | -0.47607 | -0.44861
2517.6094 | 122.9828 | -122.7814 | 0.20142 | -0.052567 | 0.014125 | 0.0058662 | 0.044301 | -0.013198 | -0.01169 | 0.013475 | -0.018311 | 0.13275 | -0.30212 | 0.004578 | 0.027466 | 0.050354 | -0.018311 | 0.16022 | 0.23346 | -0.27466 | 122.4792 | -0.068665 | 122.7631 | 122.7859 | -0.17395 | 122.5067 | 0.032043 | 0.28381 | 122.7631 | 122.9416 | 122.8088 | 122.9141 | 122.7631 | 123.0148 | 122.8317 | 122.5067 | 122.9141 | 122.7631 | 122.8317 | 122.8088 | 123.0148 | -0.50354 | -0.47607
2519.3594 | 122.9919 | -122.7768 | 0.17853 | 0.18394 | 0.013911 | -0.0018244 | 0.043447 | -0.014479 | -0.0084851 | 0.014971 | 0.045776 | 0.12817 | -0.24719 | 0.07782 | 0.11444 | 0.16022 | -0.17853 | 0.2655 | 0.20142 | -0.25635 | 122.5296 | -0.050354 | 122.8226 | 122.8546 | -0.064087 | 122.5204 | 0.022888 | 0.29297 | 122.5983 | 123.0423 | 122.8912 | 122.905 | 122.8226 | 122.9782 | 122.937 | 122.5204 | 122.905 | 122.8226 | 122.937 | 122.8912 | 122.9782 | -0.42572 | -0.43488
2521.0469 | 122.9874 | -122.7905 | 0.19226 | 0.19157 | 0.011989 | 0.0011664 | 0.041951 | -0.015975 | -0.0086987 | 0.014971 | 0.032043 | 0.15106 | -0.25177 | 0.07782 | 0.1236 | 0.15564 | -0.20142 | 0.24261 | 0.17853 | -0.23804 | 122.5388 | -0.041199 | 122.8226 | 122.8683 | -0.068665 | 122.5525 | -0.013733 | 0.28381 | 122.5891 | 123.0331 | 122.9141 | 122.9416 | 122.8226 | 122.9691 | 122.9462 | 122.5525 | 122.9416 | 122.8226 | 122.9462 | 122.9141 | 122.9691 | -0.44403 | -0.4303
2522.7969 | 123.0972 | -122.7768 | 0.15564 | -0.18227 | 0.01327 | -0.0011834 | 0.043019 | -0.014693 | -0.0099805 | 0.014116 | -0.07782 | 0.17853 | -0.31586 | -0.013733 | 0.013733 | 0.032043 | 0.032043 | 0.16022 | 0.22888 | -0.27924 | 122.4609 | 0.022888 | 122.699 | 122.7631 | -0.14191 | 122.4976 | 0.073242 | 0.23804 | 122.8088 | 122.937 | 122.7905 | 122.9553 | 122.699 | 123.0057 | 122.8088 | 122.4976 | 122.9553 | 122.699 | 122.8088 | 122.7905 | 123.0057 | -0.4715 | -0.43488
2524.5625 | 123.0698 | -122.7859 | 0.16479 | -0.090714 | 0.014338 | -0.0073786 | 0.038747 | -0.017684 | -0.0084851 | 0.013475 | 0.018311 | 0.14191 | -0.27008 | 0.10529 | 0.12817 | 0.17853 | -0.14191 | 0.31128 | 0.17853 | -0.24261 | 122.5159 | -0.022888 | 122.8043 | 122.8912 | -0.036621 | 122.5433 | 0.013733 | 0.28839 | 122.644 | 123.0972 | 122.9141 | 122.9279 | 122.8043 | 122.9645 | 122.9645 | 122.5433 | 122.9279 | 122.8043 | 122.9645 | 122.9141 | 122.9645 | -0.43488 | -0.40741
2526.25 | 123.1247 | -122.7585 | 0.15106 | -0.23567 | 0.014979 | -0.00011543 | 0.044942 | -0.014479 | -0.0080579 | 0.013475 | -0.07782 | 0.16937 | -0.32501 | -0.022888 | 0.018311 | 0.009155 | 0.064087 | 0.14648 | 0.23804 | -0.29755 | 122.4335 | 0.018311 | 122.6807 | 122.7356 | -0.13275 | 122.4609 | 0.086975 | 0.24719 | 122.8226 | 122.905 | 122.7768 | 122.9279 | 122.6807 | 122.9965 | 122.7676 | 122.4609 | 122.9279 | 122.6807 | 122.7676 | 122.7768 | 122.9965 | -0.47607 | -0.44861
2528.0156 | 122.9919 | -122.7997 | 0.21057 | -0.098343 | 0.010921 | -0.0022516 | 0.045583 | -0.013839 | -0.010194 | 0.013048 | -0.018311 | 0.16937 | -0.3067 | 0.041199 | 0.041199 | 0.064087 | -0.036621 | 0.19684 | 0.21973 | -0.25177 | 122.493 | -0.041198 | 122.7814 | 122.8409 | -0.16937 | 122.5479 | 0.009156 | 0.28839 | 122.7631 | 122.9965 | 122.8409 | 122.9691 | 122.7814 | 123.0194 | 122.8638 | 122.5479 | 122.9691 | 122.7814 | 122.8638 | 122.8409 | 123.0194 | -0.51727 | -0.46234
2529.7812 | 123.1155 | -122.7585 | 0.16022 | -0.17464 | 0.015193 | -0.0022516 | 0.043233 | -0.015761 | -0.013185 | 0.013689 | -0.07782 | 0.17853 | -0.3067 | -0.022888 | 0.013733 | 0.022888 | 0.059509 | 0.17395 | 0.24261 | -0.28381 | 122.4518 | 0.018311 | 122.6807 | 122.7356 | -0.14648 | 122.4747 | 0.082398 | 0.22888 | 122.818 | 122.9324 | 122.7722 | 122.937 | 122.6807 | 123.0011 | 122.7814 | 122.4747 | 122.937 | 122.6807 | 122.7814 | 122.7722 | 123.0011 | -0.46692 | -0.44403
2531.5469 | 123.0011 | -122.7859 | 0.1831 | 0.18394 | 0.011775 | -0.00075623 | 0.044301 | -0.013625 | -0.01233 | 0.014116 | -0.041199 | 0.15564 | -0.28839 | 0.004578 | 0.032043 | 0.07782 | -0.082397 | 0.16479 | 0.22888 | -0.24719 | 122.4976 | -0.027465 | 122.7448 | 122.7905 | -0.15106 | 122.5388 | 0.045777 | 0.24719 | 122.7036 | 122.9507 | 122.818 | 122.9416 | 122.7448 | 123.0148 | 122.8638 | 122.5388 | 122.9416 | 122.7448 | 122.8638 | 122.818 | 123.0148 | -0.4715 | -0.4303
2533.2344 | 123.0743 | -122.7539 | 0.17395 | -0.098343 | 0.010493 | -0.0080194 | 0.036611 | -0.016188 | -0.0093395 | 0.013475 | -0.022888 | 0.14191 | -0.28381 | 0.068665 | 0.10986 | 0.16937 | -0.12817 | 0.28381 | 0.19684 | -0.24719 | 122.4701 | -0.032043 | 122.731 | 122.8226 | -0.064087 | 122.5067 | 0.022888 | 0.26092 | 122.6257 | 123.0377 | 122.8638 | 122.8958 | 122.731 | 122.9507 | 122.9233 | 122.5067 | 122.8958 | 122.731 | 122.9233 | 122.8638 | 122.9507 | -0.45776 | -0.42114
2534.9844 | 123.0743 | -122.7402 | 0.16937 | -0.12123 | 0.010921 | 0.00095277 | 0.04067 | -0.016188 | -0.0082715 | 0.011553 | 0.009155 | 0.13275 | -0.27466 | 0.091553 | 0.1236 | 0.14648 | -0.12817 | 0.28839 | 0.19684 | -0.22888 | 122.4655 | -0.036622 | 122.7493 | 122.8317 | -0.045777 | 122.5113 | 0.027465 | 0.28381 | 122.612 | 123.0286 | 122.8638 | 122.8729 | 122.7493 | 122.937 | 122.8867 | 122.5113 | 122.8729 | 122.7493 | 122.8867 | 122.8638 | 122.937 | -0.44403 | -0.39826
2536.7344 | 123.0011 | -122.7768 | 0.18768 | 0.12291 | 0.01327 | -0.0033196 | 0.04366 | -0.012984 | -0.0093395 | 0.014544 | 0.027466 | 0.13733 | -0.26093 | 0.07782 | 0.091553 | 0.1236 | -0.17395 | 0.24261 | 0.19684 | -0.23346 | 122.5159 | -0.050354 | 122.8043 | 122.8546 | -0.09613 | 122.5433 | 0.009155 | 0.28839 | 122.6028 | 123.0194 | 122.8683 | 122.9141 | 122.8043 | 122.9736 | 122.9004 | 122.5433 | 122.9141 | 122.8043 | 122.9004 | 122.8683 | 122.9736 | -0.44861 | -0.42114
2538.5312 | 123.1247 | -122.7493 | 0.17395 | -0.25856 | 0.011989 | -0.00032903 | 0.04366 | -0.017684 | -0.0097669 | 0.014544 | -0.07782 | 0.16479 | -0.32044 | -0.018311 | -0.004578 | 0 | 0.050354 | 0.15106 | 0.2655 | -0.27924 | 122.4289 | -0.009155 | 122.6715 | 122.731 | -0.17853 | 122.4701 | 0.091553 | 0.24262 | 122.7997 | 122.9004 | 122.7448 | 122.9141 | 122.6715 | 123.0148 | 122.7493 | 122.4701 | 122.9141 | 122.6715 | 122.7493 | 122.7448 | 123.0148 | -0.49439 | -0.45319
2540.2188 | 122.9965 | -122.7951 | 0.19226 | -0.098343 | 0.014125 | -0.0024652 | 0.04601 | -0.014266 | -0.012758 | 0.012835 | -0.009155 | 0.16022 | -0.31586 | 0.041199 | 0.050354 | 0.068665 | -0.022888 | 0.20599 | 0.23346 | -0.2655 | 122.4792 | -0.032044 | 122.7859 | 122.8363 | -0.14191 | 122.5296 | 0.041198 | 0.3067 | 122.7722 | 123.0011 | 122.8455 | 122.9553 | 122.7859 | 123.0286 | 122.8638 | 122.5296 | 122.9553 | 122.7859 | 122.8638 | 122.8455 | 123.0286 | -0.50812 | -0.45776
2541.9688 | 123.0698 | -122.7539 | 0.17395 | -0.22041 | 0.013911 | -0.002038 | 0.038533 | -0.013625 | -0.011903 | 0.01433 | 0.036621 | 0.1236 | -0.27008 | 0.10071 | 0.11902 | 0.13733 | -0.11902 | 0.28839 | 0.21515 | -0.21973 | 122.4838 | -0.050354 | 122.7905 | 122.8546 | -0.054931 | 122.5342 | 0.041199 | 0.3067 | 122.6349 | 123.0423 | 122.8729 | 122.8775 | 122.7905 | 122.9691 | 122.8912 | 122.5342 | 122.8775 | 122.7905 | 122.8912 | 122.8729 | 122.9691 | -0.44403 | -0.39368
2543.6562 | 123.0194 | -122.7768 | 0.20142 | 0.12291 | 0.013484 | -0.0018244 | 0.040883 | -0.013625 | -0.0093395 | 0.013048 | 0.022888 | 0.1236 | -0.27924 | 0.073242 | 0.09613 | 0.13275 | -0.17395 | 0.24261 | 0.21057 | -0.25635 | 122.4976 | -0.07782 | 122.7997 | 122.85 | -0.10529 | 122.5204 | 0.009155 | 0.30212 | 122.6028 | 123.0194 | 122.8729 | 122.9004 | 122.7997 | 122.9874 | 122.9095 | 122.5204 | 122.9004 | 122.7997 | 122.9095 | 122.8729 | 122.9874 | -0.48065 | -0.45776
2545.3438 | 122.9507 | -122.7997 | 0.20142 | 0.16869 | 0.013484 | -0.00011543 | 0.045583 | -0.01512 | -0.0086987 | 0.016039 | 0.036621 | 0.11902 | -0.2655 | 0.086975 | 0.11444 | 0.14191 | -0.18768 | 0.25177 | 0.1831 | -0.24719 | 122.5342 | -0.082397 | 122.8363 | 122.8867 | -0.086975 | 122.5525 | -0.018311 | 0.30212 | 122.612 | 123.0515 | 122.9141 | 122.9187 | 122.8363 | 122.9828 | 122.9416 | 122.5525 | 122.9187 | 122.8363 | 122.9416 | 122.9141 | 122.9828 | -0.46692 | -0.44861
2547.0781 | 123.1338 | -122.7539 | 0.15106 | -0.19753 | 0.012202 | -0.0063104 | 0.043233 | -0.016402 | -0.012971 | 0.014757 | -0.059509 | 0.15564 | -0.30212 | -0.013733 | 0.013733 | 0.009155 | 0.041199 | 0.16479 | 0.24719 | -0.28381 | 122.4518 | 0.004578 | 122.6944 | 122.7402 | -0.13733 | 122.4701 | 0.09613 | 0.24261 | 122.7951 | 122.9187 | 122.7676 | 122.9095 | 122.6944 | 123.0011 | 122.7631 | 122.4701 | 122.9095 | 122.6944 | 122.7631 | 122.7676 | 123.0011 | -0.45319 | -0.43488
2548.8594 | 123.0011 | -122.818 | 0.17395 | -0.075455 | 0.01327 | -0.00075623 | 0.045797 | -0.014052 | -0.011903 | 0.015612 | -0.013733 | 0.16937 | -0.29755 | 0.041199 | 0.059509 | 0.064087 | -0.018311 | 0.20142 | 0.24261 | -0.27466 | 122.5204 | -0.004577 | 122.8043 | 122.8592 | -0.11444 | 122.5433 | 0.068665 | 0.28381 | 122.7997 | 123.0194 | 122.8775 | 122.9874 | 122.8043 | 123.0606 | 122.8821 | 122.5433 | 122.9874 | 122.8043 | 122.8821 | 122.8775 | 123.0606 | -0.4715 | -0.44861
2550.5469 | 123.1201 | -122.731 | 0.15106 | -0.25856 | 0.013484 | -0.0039606 | 0.043019 | -0.014052 | -0.012117 | 0.012621 | -0.054932 | 0.17853 | -0.31128 | 0 | 0.013733 | 0.022888 | 0.050354 | 0.16937 | 0.22888 | -0.28381 | 122.4197 | 0.027466 | 122.6761 | 122.731 | -0.13733 | 122.4472 | 0.07782 | 0.25635 | 122.7814 | 122.9004 | 122.7448 | 122.9095 | 122.6761 | 122.9599 | 122.7539 | 122.4472 | 122.9095 | 122.6761 | 122.7539 | 122.7448 | 122.9599 | -0.46234 | -0.43488
2552.2344 | 123.143 | -122.7539 | 0.17395 | -0.22041 | 0.01327 | 9.8166e-05 | 0.041524 | -0.015334 | -0.010194 | 0.012407 | -0.064087 | 0.16479 | -0.30212 | -0.013733 | 0.022888 | 0.027466 | 0.036621 | 0.17853 | 0.23804 | -0.29297 | 122.4518 | -0.009155 | 122.6898 | 122.7402 | -0.15106 | 122.4609 | 0.064087 | 0.23804 | 122.7905 | 122.9324 | 122.7768 | 122.9187 | 122.6898 | 122.9919 | 122.7814 | 122.4609 | 122.9187 | 122.6898 | 122.7814 | 122.7768 | 122.9919 | -0.47607 | -0.46692
2554.0156 | 123.0377 | -122.7722 | 0.16937 | 0.13054 | 0.013484 | 0.0011664 | 0.04601 | -0.013198 | -0.010621 | 0.01433 | -0.064087 | 0.1831 | -0.31128 | -0.032043 | -0.013733 | 0.013733 | -0.013733 | 0.11902 | 0.24261 | -0.24719 | 122.4609 | 0.013732 | 122.7081 | 122.7402 | -0.18311 | 122.525 | 0.073242 | 0.24719 | 122.7585 | 122.8912 | 122.7585 | 122.9553 | 122.7081 | 123.0148 | 122.7859 | 122.525 | 122.9553 | 122.7081 | 122.7859 | 122.7585 | 123.0148 | -0.48065 | -0.41656
2555.7656 | 123.0469 | -122.7905 | 0.20599 | 0.13054 | 0.011561 | 0.003089 | 0.04366 | -0.013839 | -0.0099805 | 0.016893 | -0.091553 | 0.16479 | -0.31128 | -0.036621 | -0.013733 | 0.027466 | -0.009155 | 0.11444 | 0.21973 | -0.27466 | 122.4792 | -0.041199 | 122.699 | 122.7539 | -0.21973 | 122.5159 | 0.013733 | 0.21973 | 122.7814 | 122.905 | 122.7768 | 122.9553 | 122.699 | 123.0103 | 122.818 | 122.5159 | 122.9553 | 122.699 | 122.818 | 122.7768 | 123.0103 | -0.51727 | -0.48065
2557.5156 | 123.0423 | -122.7768 | 0.1831 | 0.061874 | 0.013698 | -0.00011543 | 0.043874 | -0.012557 | -0.0093395 | 0.014544 | -0.086975 | 0.1831 | -0.31586 | -0.050354 | -0.004578 | 0.004578 | 0.004578 | 0.10529 | 0.22888 | -0.2655 | 122.4609 | 0 | 122.6898 | 122.7264 | -0.18768 | 122.5113 | 0.045777 | 0.22888 | 122.7814 | 122.8821 | 122.7722 | 122.9599 | 122.6898 | 123.0057 | 122.7814 | 122.5113 | 122.9599 | 122.6898 | 122.7814 | 122.7722 | 123.0057 | -0.49896 | -0.44861
2559.2031 | 123.0789 | -122.7264 | 0.15564 | -0.10597 | 0.015407 | -0.0026788 | 0.03597 | -0.01512 | -0.0086987 | 0.014116 | -0.009155 | 0.14191 | -0.27466 | 0.073242 | 0.13275 | 0.14648 | -0.14191 | 0.29297 | 0.21057 | -0.26093 | 122.4518 | -0.013733 | 122.7173 | 122.7997 | -0.022889 | 122.4655 | 0.054931 | 0.2655 | 122.5845 | 123.0194 | 122.8592 | 122.8683 | 122.7173 | 122.937 | 122.8729 | 122.4655 | 122.8683 | 122.7173 | 122.8729 | 122.8592 | 122.937 | -0.4303 | -0.41657
2560.9688 | 123.0927 | -122.7493 | 0.18768 | -0.18227 | 0.010921 | -0.003747 | 0.041951 | -0.017897 | -0.0086987 | 0.012835 | 0.004578 | 0.13275 | -0.27466 | 0.064087 | 0.09613 | 0.10071 | -0.036621 | 0.27008 | 0.21973 | -0.27924 | 122.4747 | -0.054932 | 122.7539 | 122.8134 | -0.091553 | 122.4701 | 0.032044 | 0.27924 | 122.7127 | 123.0194 | 122.8455 | 122.8821 | 122.7539 | 122.9691 | 122.85 | 122.4701 | 122.8821 | 122.7539 | 122.85 | 122.8455 | 122.9691 | -0.46234 | -0.46692
2562.7344 | 123.111 | -122.7585 | 0.16479 | -0.01442 | 0.012843 | -0.00096983 | 0.040029 | -0.016829 | -0.0097669 | 0.014116 | -0.013733 | 0.14191 | -0.28839 | 0.041199 | 0.10529 | 0.13275 | -0.11444 | 0.2655 | 0.21515 | -0.25177 | 122.4701 | -0.022888 | 122.7448 | 122.7997 | -0.059509 | 122.5067 | 0.050354 | 0.27466 | 122.644 | 123.024 | 122.8638 | 122.9004 | 122.7448 | 122.9736 | 122.8912 | 122.5067 | 122.9004 | 122.7448 | 122.8912 | 122.8638 | 122.9736 | -0.45319 | -0.41656
2564.5 | 122.9919 | -122.7814 | 0.20142 | 0.16869 | 0.015834 | 0.0015936 | 0.046651 | -0.014907 | -0.0091259 | 0.013689 | 0.027466 | 0.14191 | -0.27466 | 0.07782 | 0.09613 | 0.14648 | -0.16937 | 0.24261 | 0.19684 | -0.23804 | 122.5067 | -0.059509 | 122.8088 | 122.8592 | -0.10529 | 122.5433 | -0.004578 | 0.30212 | 122.612 | 123.024 | 122.8775 | 122.9233 | 122.8088 | 122.9782 | 122.9279 | 122.5433 | 122.9233 | 122.8088 | 122.9279 | 122.8775 | 122.9782 | -0.47607 | -0.43945
2566.1875 | 122.9828 | -122.7905 | 0.19226 | 0.1992 | 0.014125 | 0.0041572 | 0.044942 | -0.015975 | -0.0089123 | 0.01198 | 0.032043 | 0.13733 | -0.25635 | 0.10071 | 0.10071 | 0.14191 | -0.20142 | 0.27008 | 0.18768 | -0.23346 | 122.5342 | -0.054932 | 122.8226 | 122.8912 | -0.091553 | 122.5571 | -0.004578 | 0.28839 | 122.5891 | 123.0606 | 122.8912 | 122.9279 | 122.8226 | 122.9782 | 122.9324 | 122.5571 | 122.9279 | 122.8226 | 122.9324 | 122.8912 | 122.9782 | -0.44861 | -0.42572
2567.9375 | 123.0743 | -122.7905 | 0.16022 | -0.22041 | 0.011989 | -0.0022516 | 0.040456 | -0.017043 | -0.010194 | 0.015612 | 0.004578 | 0.12817 | -0.27466 | 0.091553 | 0.10986 | 0.13733 | -0.11444 | 0.29297 | 0.20599 | -0.24261 | 122.5159 | -0.032043 | 122.7951 | 122.8821 | -0.050354 | 122.5479 | 0.045777 | 0.27924 | 122.6761 | 123.0835 | 122.9004 | 122.9187 | 122.7951 | 122.9965 | 122.9279 | 122.5479 | 122.9187 | 122.7951 | 122.9279 | 122.9004 | 122.9965 | -0.43488 | -0.40283
2569.7031 | 123.1293 | -122.7402 | 0.15106 | -0.26619 | 0.01028 | 0.00052557 | 0.042806 | -0.017684 | -0.010194 | 0.012835 | -0.054932 | 0.15564 | -0.30212 | 0.009155 | 0.027466 | 0.027466 | 0.018311 | 0.1831 | 0.24261 | -0.27466 | 122.438 | 0.004578 | 122.6852 | 122.7493 | -0.1236 | 122.4655 | 0.091553 | 0.24719 | 122.7585 | 122.9233 | 122.7676 | 122.8958 | 122.6852 | 122.9828 | 122.7676 | 122.4655 | 122.8958 | 122.6852 | 122.7676 | 122.7676 | 122.9828 | -0.45319 | -0.42572
2571.4062 | 123.0057 | -122.7905 | 0.1831 | 0.21446 | 0.011775 | -0.00011543 | 0.04366 | -0.01512 | -0.011476 | 0.013903 | 0.041199 | 0.1236 | -0.25635 | 0.091553 | 0.10529 | 0.14648 | -0.19684 | 0.27008 | 0.19226 | -0.25177 | 122.5342 | -0.059509 | 122.8317 | 122.8821 | -0.077819 | 122.5388 | 0.009156 | 0.29755 | 122.5937 | 123.0606 | 122.8958 | 122.9141 | 122.8317 | 122.9828 | 122.937 | 122.5388 | 122.9141 | 122.8317 | 122.937 | 122.8958 | 122.9828 | -0.43945 | -0.43488
2573.1406 | 123.1293 | -122.7676 | 0.16937 | -0.25856 | 0.013057 | -0.001397 | 0.044088 | -0.014693 | -0.010621 | 0.012407 | -0.073242 | 0.17853 | -0.32959 | -0.022888 | -0.004578 | 0 | 0.064087 | 0.14648 | 0.25635 | -0.27924 | 122.438 | 0.009155 | 122.6944 | 122.7448 | -0.17395 | 122.4884 | 0.086975 | 0.25635 | 122.8317 | 122.9141 | 122.7631 | 122.9462 | 122.6944 | 123.024 | 122.7676 | 122.4884 | 122.9462 | 122.6944 | 122.7676 | 122.7631 | 123.024 | -0.49896 | -0.44861
2574.9062 | 123.111 | -122.7585 | 0.1831 | 0.054245 | 0.012416 | -0.0028924 | 0.039601 | -0.017256 | -0.0086987 | 0.014116 | -0.032043 | 0.13733 | -0.3067 | 0.036621 | 0.07782 | 0.091553 | -0.11902 | 0.21515 | 0.20599 | -0.26093 | 122.4518 | -0.045776 | 122.7264 | 122.7951 | -0.10528 | 122.4976 | 0.022889 | 0.27466 | 122.6395 | 122.9736 | 122.8363 | 122.8958 | 122.7264 | 122.9645 | 122.85 | 122.4976 | 122.8958 | 122.7264 | 122.85 | 122.8363 | 122.9645 | -0.48981 | -0.44403
2576.6562 | 123.1201 | -122.7539 | 0.16479 | -0.0067901 | 0.011775 | -0.00054263 | 0.041738 | -0.01747 | -0.011262 | 0.013903 | -0.027466 | 0.14648 | -0.27924 | 0.036621 | 0.07782 | 0.09613 | -0.10529 | 0.2243 | 0.22888 | -0.27008 | 122.4747 | -0.018311 | 122.7264 | 122.7905 | -0.086975 | 122.4838 | 0.064087 | 0.25177 | 122.6486 | 122.9782 | 122.8317 | 122.9004 | 122.7264 | 122.9828 | 122.85 | 122.4838 | 122.9004 | 122.7264 | 122.85 | 122.8317 | 122.9828 | -0.44403 | -0.43488
2578.3438 | 123.1018 | -122.7448 | 0.16479 | -0.037308 | 0.011348 | -0.001397 | 0.041951 | -0.016829 | -0.0095531 | 0.014116 | -0.022888 | 0.1236 | -0.28381 | 0.064087 | 0.10071 | 0.12817 | -0.11902 | 0.26093 | 0.19226 | -0.26093 | 122.4609 | -0.041199 | 122.7219 | 122.8088 | -0.064087 | 122.4838 | 0.027466 | 0.26092 | 122.6257 | 123.0057 | 122.8455 | 122.8683 | 122.7219 | 122.937 | 122.8729 | 122.4838 | 122.8683 | 122.7219 | 122.8729 | 122.8455 | 122.937 | -0.44861 | -0.42572
2580.0938 | 122.9965 | -122.7951 | 0.20142 | 0.20683 | 0.014552 | 0.0037298 | 0.048146 | -0.01512 | -0.010621 | 0.012621 | 0.050354 | 0.14191 | -0.24719 | 0.10071 | 0.11902 | 0.14191 | -0.20142 | 0.26093 | 0.1831 | -0.23346 | 122.5479 | -0.059509 | 122.8455 | 122.8958 | -0.082397 | 122.5616 | -0.018311 | 0.29755 | 122.5937 | 123.056 | 122.9141 | 122.937 | 122.8455 | 122.9782 | 122.937 | 122.5616 | 122.937 | 122.8455 | 122.937 | 122.9141 | 122.9782 | -0.44861 | -0.43488
2581.8594 | 123.0881 | -122.7585 | 0.16479 | -0.1136 | 0.01327 | -0.00096983 | 0.039815 | -0.016188 | -0.0082715 | 0.012407 | -0.009155 | 0.14191 | -0.28381 | 0.091553 | 0.13275 | 0.14191 | -0.13275 | 0.27924 | 0.20599 | -0.25177 | 122.4747 | -0.022888 | 122.7493 | 122.85 | -0.032044 | 122.5067 | 0.041199 | 0.27466 | 122.6257 | 123.0377 | 122.8912 | 122.9004 | 122.7493 | 122.9645 | 122.9004 | 122.5067 | 122.9004 | 122.7493 | 122.9004 | 122.8912 | 122.9645 | -0.44861 | -0.41656
2583.5469 | 123.0835 | -122.7539 | 0.16937 | -0.20515 | 0.012416 | 0.00052557 | 0.04131 | -0.016188 | -0.010621 | 0.013475 | 0.036621 | 0.15564 | -0.28381 | 0.10071 | 0.13733 | 0.13275 | -0.13275 | 0.29297 | 0.20142 | -0.26093 | 122.4701 | -0.013733 | 122.7905 | 122.8546 | -0.032044 | 122.493 | 0.032043 | 0.32043 | 122.6212 | 123.0469 | 122.8912 | 122.9095 | 122.7905 | 122.9553 | 122.8867 | 122.493 | 122.9095 | 122.7905 | 122.8867 | 122.8912 | 122.9553 | -0.45319 | -0.4303
2585.25 | 123.1155 | -122.7493 | 0.17853 | -0.28145 | 0.01327 | -0.0054558 | 0.045583 | -0.016616 | -0.012117 | 0.014544 | -0.07782 | 0.15106 | -0.33417 | -0.009155 | 0.004578 | 0.009155 | 0.059509 | 0.14191 | 0.23346 | -0.27008 | 122.4152 | -0.027466 | 122.6715 | 122.7402 | -0.17395 | 122.4792 | 0.054931 | 0.25635 | 122.8088 | 122.8912 | 122.7539 | 122.9004 | 122.6715 | 122.9828 | 122.7585 | 122.4792 | 122.9004 | 122.6715 | 122.7585 | 122.7539 | 122.9828 | -0.5127 | -0.44861
2587 | 123.0103 | -122.7768 | 0.18768 | 0.038986 | 0.015407 | -0.0022516 | 0.049001 | -0.014907 | -0.011476 | 0.012835 | -0.036621 | 0.16479 | -0.32044 | 0.009155 | 0.004578 | 0.018311 | -0.013733 | 0.1236 | 0.21973 | -0.28381 | 122.4564 | -0.022888 | 122.7402 | 122.7859 | -0.1831 | 122.493 | 0.032044 | 0.28381 | 122.7631 | 122.9004 | 122.7814 | 122.9416 | 122.7402 | 122.9965 | 122.7951 | 122.493 | 122.9416 | 122.7402 | 122.7951 | 122.7814 | 122.9965 | -0.50812 | -0.4715
2588.7656 | 123.1567 | -122.7539 | 0.16022 | -0.25093 | 0.016047 | 0.0015936 | 0.042592 | -0.016188 | -0.010194 | 0.013689 | -0.09613 | 0.16937 | -0.32044 | -0.022888 | -0.004578 | 0 | 0.073242 | 0.15106 | 0.25177 | -0.28381 | 122.4335 | 0.009156 | 122.6578 | 122.731 | -0.16479 | 122.4701 | 0.091553 | 0.22431 | 122.8271 | 122.905 | 122.7493 | 122.9233 | 122.6578 | 123.0057 | 122.7539 | 122.4701 | 122.9233 | 122.6578 | 122.7539 | 122.7493 | 123.0057 | -0.48065 | -0.44403
2590.5312 | 122.9919 | -122.8088 | 0.19684 | -0.075455 | 0.012202 | 0.00095277 | 0.044515 | -0.013839 | -0.010835 | 0.014971 | -0.013733 | 0.16479 | -0.29755 | 0.032043 | 0.050354 | 0.059509 | -0.032043 | 0.17395 | 0.23804 | -0.2655 | 122.5113 | -0.032043 | 122.7951 | 122.8409 | -0.14648 | 122.5433 | 0.041199 | 0.28381 | 122.7768 | 122.9828 | 122.8592 | 122.9736 | 122.7951 | 123.0469 | 122.8683 | 122.5433 | 122.9736 | 122.7951 | 122.8683 | 122.8592 | 123.0469 | -0.49438 | -0.46234
2592.2188 | 123.024 | -122.7905 | 0.17853 | 0.054245 | 0.013057 | 9.8166e-05 | 0.048146 | -0.013198 | -0.012117 | 0.015398 | -0.073242 | 0.1831 | -0.32044 | -0.027466 | 0 | 0 | 0.022888 | 0.11444 | 0.23346 | -0.29297 | 122.4701 | 0.004577 | 122.7173 | 122.7631 | -0.17853 | 122.4976 | 0.054931 | 0.24719 | 122.8134 | 122.905 | 122.7905 | 122.9736 | 122.7173 | 123.024 | 122.7905 | 122.4976 | 122.9736 | 122.7173 | 122.7905 | 122.7905 | 123.024 | -0.49896 | -0.4715
2593.9219 | 122.9828 | -122.8043 | 0.20142 | 0.16106 | 0.013484 | -0.00054263 | 0.042379 | -0.011275 | -0.010621 | 0.015612 | 0.004578 | 0.14191 | -0.27008 | 0.073242 | 0.10986 | 0.14648 | -0.18768 | 0.23346 | 0.19684 | -0.22888 | 122.5342 | -0.059509 | 122.8088 | 122.8775 | -0.091553 | 122.5754 | -0.004578 | 0.27466 | 122.6166 | 123.0377 | 122.9141 | 122.9462 | 122.8088 | 123.0011 | 122.9507 | 122.5754 | 122.9462 | 122.8088 | 122.9507 | 122.9141 | 123.0011 | -0.4715 | -0.4303
2595.6875 | 122.9919 | -122.7905 | 0.17853 | 0.22209 | 0.01562 | -0.002038 | 0.044301 | -0.014907 | -0.010194 | 0.01433 | -0.027466 | 0.16479 | -0.27466 | 0.027466 | 0.059509 | 0.11444 | -0.13275 | 0.21057 | 0.19684 | -0.27008 | 122.5159 | -0.013733 | 122.7631 | 122.818 | -0.11902 | 122.5204 | 0.01831 | 0.24719 | 122.6578 | 123.0011 | 122.85 | 122.9553 | 122.7631 | 122.9874 | 122.905 | 122.5204 | 122.9553 | 122.7631 | 122.905 | 122.85 | 122.9874 | -0.45319 | -0.44861
2597.375 | 123.0515 | -122.8043 | 0.16937 | 0.15343 | 0.014125 | 0.0050116 | 0.044301 | -0.014479 | -0.0099805 | 0.015398 | -0.09613 | 0.17395 | -0.30212 | -0.036621 | 0 | 0.018311 | -0.004578 | 0.10986 | 0.21515 | -0.27466 | 122.5021 | 0.004577 | 122.7081 | 122.7676 | -0.16937 | 122.5296 | 0.045776 | 0.20599 | 122.7997 | 122.9141 | 122.8043 | 122.9782 | 122.7081 | 123.0194 | 122.8226 | 122.5296 | 122.9782 | 122.7081 | 122.8226 | 122.8043 | 123.0194 | -0.4715 | -0.44403
2599.0781 | 123.0377 | -122.7722 | 0.19684 | 0.092392 | 0.013698 | 0.00031197 | 0.03832 | -0.01512 | -0.0093395 | 0.01433 | -0.018311 | 0.16022 | -0.27008 | 0.022888 | 0.068665 | 0.11444 | -0.10529 | 0.20142 | 0.20599 | -0.26093 | 122.5021 | -0.036621 | 122.7539 | 122.7951 | -0.12817 | 122.5113 | 0.009156 | 0.25177 | 122.6669 | 122.9736 | 122.8409 | 122.9324 | 122.7539 | 122.9782 | 122.8867 | 122.5113 | 122.9324 | 122.7539 | 122.8867 | 122.8409 | 122.9782 | -0.46692 | -0.45776
2600.7656 | 123.0789 | -122.7859 | 0.1831 | -0.18227 | 0.012202 | -0.0067376 | 0.03832 | -0.015975 | -0.0091259 | 0.014116 | 0.045776 | 0.14191 | -0.25635 | 0.091553 | 0.12817 | 0.15564 | -0.13275 | 0.31128 | 0.21057 | -0.24719 | 122.5296 | -0.041198 | 122.8317 | 122.8775 | -0.054931 | 122.5388 | 0.027466 | 0.30212 | 122.6532 | 123.0972 | 122.9141 | 122.9279 | 122.8317 | 122.9965 | 122.9416 | 122.5388 | 122.9279 | 122.8317 | 122.9416 | 122.9141 | 122.9965 | -0.43945 | -0.4303
2602.5156 | 123.1338 | -122.731 | 0.15106 | 0.016098 | 0.013057 | -0.0039606 | 0.038961 | -0.015761 | -0.0084851 | 0.013689 | -0.045776 | 0.15106 | -0.27924 | 0.041199 | 0.086975 | 0.10071 | -0.091553 | 0.22888 | 0.21515 | -0.26093 | 122.4518 | 0 | 122.6852 | 122.7722 | -0.064087 | 122.4701 | 0.064087 | 0.23346 | 122.6395 | 122.9599 | 122.818 | 122.8821 | 122.6852 | 122.9462 | 122.8317 | 122.4701 | 122.8821 | 122.6852 | 122.8317 | 122.818 | 122.9462 | -0.4303 | -0.41199
2604.2031 | 123.0652 | -122.7768 | 0.1831 | -0.13649 | 0.013484 | -0.003106 | 0.049215 | -0.014693 | -0.011262 | 0.014544 | -0.032043 | 0.1831 | -0.33875 | 0.036621 | 0.027466 | 0.059509 | 0.004578 | 0.19226 | 0.22888 | -0.25635 | 122.438 | 0 | 122.7448 | 122.8134 | -0.15564 | 122.5204 | 0.045777 | 0.3067 | 122.7814 | 122.9691 | 122.8043 | 122.9599 | 122.7448 | 123.0057 | 122.8363 | 122.5204 | 122.9599 | 122.7448 | 122.8363 | 122.8043 | 123.0057 | -0.52185 | -0.43945
2605.9531 | 123.0835 | -122.7676 | 0.17853 | -0.1899 | 0.014338 | 0.004798 | 0.046651 | -0.014052 | -0.013826 | 0.013262 | -0.041199 | 0.16937 | -0.32044 | 0.027466 | 0.045776 | 0.059509 | -0.004578 | 0.20142 | 0.23346 | -0.27466 | 122.4472 | -0.009155 | 122.7264 | 122.7951 | -0.13275 | 122.493 | 0.054931 | 0.27924 | 122.7631 | 122.9691 | 122.8134 | 122.937 | 122.7264 | 123.0011 | 122.8271 | 122.493 | 122.937 | 122.7264 | 122.8271 | 122.8134 | 123.0011 | -0.49896 | -0.45319
2607.7188 | 123.1155 | -122.7402 | 0.1831 | -0.17464 | 0.012629 | -0.0041742 | 0.043233 | -0.015334 | -0.01233 | 0.014757 | -0.07782 | 0.17395 | -0.31586 | -0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.16479 | 0.25635 | -0.28381 | 122.4243 | -0.009155 | 122.6624 | 122.7264 | -0.16479 | 122.4564 | 0.073243 | 0.23804 | 122.7859 | 122.905 | 122.7585 | 122.9141 | 122.6624 | 122.9965 | 122.7631 | 122.4564 | 122.9141 | 122.6624 | 122.7631 | 122.7585 | 122.9965 | -0.49896 | -0.46692
2609.4219 | 123.024 | -122.7859 | 0.17395 | 0.1458 | 0.011561 | -0.0035332 | 0.046224 | -0.011702 | -0.012971 | 0.014757 | -0.064087 | 0.16479 | -0.30212 | -0.004578 | 0.013733 | 0.064087 | -0.082397 | 0.15106 | 0.23804 | -0.26093 | 122.4838 | -0.009155 | 122.7219 | 122.7814 | -0.16022 | 122.525 | 0.064087 | 0.23804 | 122.7036 | 122.937 | 122.7997 | 122.9507 | 122.7219 | 123.024 | 122.85 | 122.525 | 122.9507 | 122.7219 | 122.85 | 122.7997 | 123.024 | -0.47607 | -0.43488
2611.1719 | 123.0652 | -122.7905 | 0.17395 | -0.17464 | 0.011561 | -0.0024652 | 0.045797 | -0.013198 | -0.010194 | 0.014116 | -0.032043 | 0.15564 | -0.31586 | 0.013733 | 0.041199 | 0.059509 | 0.004578 | 0.18768 | 0.23804 | -0.2655 | 122.4747 | -0.01831 | 122.7585 | 122.8043 | -0.13275 | 122.525 | 0.064087 | 0.28381 | 122.7951 | 122.9782 | 122.8317 | 122.9462 | 122.7585 | 123.0286 | 122.85 | 122.525 | 122.9462 | 122.7585 | 122.85 | 122.8317 | 123.0286 | -0.48981 | -0.43945
2612.9219 | 123.0377 | -122.8043 | 0.18768 | 0.084762 | 0.014552 | 0.0015936 | 0.045583 | -0.012984 | -0.01169 | 0.015184 | -0.064087 | 0.18768 | -0.31128 | -0.032043 | -0.013733 | 0.009155 | 0.013733 | 0.10529 | 0.25177 | -0.28381 | 122.493 | 0 | 122.7402 | 122.7722 | -0.20142 | 122.5204 | 0.064087 | 0.24719 | 122.818 | 122.9095 | 122.7905 | 122.9919 | 122.7402 | 123.056 | 122.8134 | 122.5204 | 122.9919 | 122.7402 | 122.8134 | 122.7905 | 123.056 | -0.49896 | -0.4715
2614.6875 | 123.0148 | -122.8088 | 0.20599 | -0.022049 | 0.012202 | -0.0035332 | 0.045156 | -0.013625 | -0.0099805 | 0.016253 | -0.041199 | 0.16937 | -0.31128 | -0.004578 | 0.013733 | 0.041199 | -0.022888 | 0.14648 | 0.21973 | -0.27466 | 122.4976 | -0.036621 | 122.7676 | 122.8043 | -0.19226 | 122.5342 | 0.013733 | 0.27008 | 122.7859 | 122.9553 | 122.8226 | 122.9782 | 122.7676 | 123.0286 | 122.85 | 122.5342 | 122.9782 | 122.7676 | 122.85 | 122.8226 | 123.0286 | -0.51727 | -0.48065
2616.375 | 122.9782 | -122.7997 | 0.20599 | 0.17632 | 0.010707 | -0.0046014 | 0.041524 | -0.014907 | -0.012117 | 0.016039 | -0.004578 | 0.14191 | -0.28381 | 0.054932 | 0.09613 | 0.14648 | -0.14648 | 0.23346 | 0.21515 | -0.2243 | 122.5159 | -0.064087 | 122.7951 | 122.8546 | -0.10986 | 122.5754 | 0.009155 | 0.27923 | 122.6532 | 123.0331 | 122.8958 | 122.9416 | 122.7951 | 123.0148 | 122.9462 | 122.5754 | 122.9416 | 122.7951 | 122.9462 | 122.8958 | 123.0148 | -0.48981 | -0.4303
2618.125 | 123.0743 | -122.7768 | 0.16937 | -0.18227 | 0.014125 | -0.0018244 | 0.042592 | -0.014693 | -0.013185 | 0.013048 | -0.054932 | 0.16937 | -0.32501 | 0.013733 | 0.045776 | 0.041199 | 0.004578 | 0.19684 | 0.21973 | -0.26093 | 122.4518 | 0 | 122.7219 | 122.7905 | -0.1236 | 122.5159 | 0.050354 | 0.27008 | 122.7814 | 122.9736 | 122.8226 | 122.9462 | 122.7219 | 122.9965 | 122.818 | 122.5159 | 122.9462 | 122.7219 | 122.818 | 122.8226 | 122.9965 | -0.49439 | -0.4303
2619.875 | 123.0515 | -122.7859 | 0.19226 | 0.054245 | 0.013911 | 0.0062934 | 0.045156 | -0.013198 | -0.010621 | 0.01433 | -0.068665 | 0.17395 | -0.31128 | -0.032043 | -0.013733 | -0.004578 | 0.027466 | 0.11902 | 0.22888 | -0.28839 | 122.4747 | -0.018311 | 122.7173 | 122.7539 | -0.20599 | 122.4976 | 0.036621 | 0.24261 | 122.8134 | 122.905 | 122.7722 | 122.9599 | 122.7173 | 123.0148 | 122.7814 | 122.4976 | 122.9599 | 122.7173 | 122.7814 | 122.7722 | 123.0148 | -0.50354 | -0.48065
2621.5625 | 123.1293 | -122.7676 | 0.15564 | -0.26619 | 0.012843 | -0.00075623 | 0.041951 | -0.016188 | -0.010835 | 0.017107 | -0.11444 | 0.17853 | -0.31586 | -0.041199 | 0.009155 | 0.022888 | 0.054932 | 0.15106 | 0.25177 | -0.28381 | 122.4518 | 0.022888 | 122.6532 | 122.7264 | -0.14649 | 122.4838 | 0.09613 | 0.20142 | 122.8226 | 122.9187 | 122.7768 | 122.9462 | 122.6532 | 123.0194 | 122.7905 | 122.4838 | 122.9462 | 122.6532 | 122.7905 | 122.7768 | 123.0194 | -0.4715 | -0.43945
2623.25 | 123.1338 | -122.7585 | 0.16937 | -0.25093 | 0.013911 | -0.0052422 | 0.042165 | -0.015334 | -0.0091259 | 0.013903 | -0.091553 | 0.19226 | -0.33417 | -0.045776 | 0 | 0 | 0.073242 | 0.14191 | 0.24719 | -0.28381 | 122.4243 | 0.022888 | 122.6669 | 122.7127 | -0.16937 | 122.4747 | 0.077819 | 0.24261 | 122.8317 | 122.9004 | 122.7585 | 122.9507 | 122.6669 | 123.0057 | 122.7585 | 122.4747 | 122.9507 | 122.6669 | 122.7585 | 122.7585 | 123.0057 | -0.50354 | -0.45319
2625 | 123.0698 | -122.7905 | 0.1831 | -0.23567 | 0.012416 | 0.00073917 | 0.038106 | -0.015975 | -0.0099805 | 0.013475 | 0.022888 | 0.14191 | -0.27924 | 0.082397 | 0.13733 | 0.15564 | -0.11902 | 0.32044 | 0.20142 | -0.23804 | 122.5113 | -0.041198 | 122.8134 | 122.8729 | -0.045776 | 122.5525 | 0.018311 | 0.30212 | 122.6715 | 123.111 | 122.9279 | 122.9324 | 122.8134 | 122.9919 | 122.9462 | 122.5525 | 122.9324 | 122.8134 | 122.9462 | 122.9279 | 122.9919 | -0.46234 | -0.42114
2626.6875 | 123.0515 | -122.7905 | 0.16479 | 0.10002 | 0.011348 | 0.0035162 | 0.041524 | -0.016188 | -0.011049 | 0.012621 | 0.004578 | 0.16479 | -0.29297 | 0.027466 | 0.082397 | 0.09613 | -0.1236 | 0.21973 | 0.22888 | -0.26093 | 122.4976 | 0 | 122.7951 | 122.818 | -0.082398 | 122.5296 | 0.064087 | 0.29755 | 122.6669 | 123.0103 | 122.8729 | 122.9553 | 122.7951 | 123.0194 | 122.8867 | 122.5296 | 122.9553 | 122.7951 | 122.8867 | 122.8729 | 123.0194 | -0.45776 | -0.42572
2628.3906 | 123.1064 | -122.7631 | 0.16022 | -0.037308 | 0.010493 | -0.0016106 | 0.04067 | -0.016829 | -0.0093395 | 0.011339 | -0.027466 | 0.15106 | -0.27466 | 0.041199 | 0.082397 | 0.11902 | -0.11444 | 0.25177 | 0.20142 | -0.27008 | 122.4884 | -0.009155 | 122.7356 | 122.8043 | -0.07782 | 122.493 | 0.041199 | 0.24719 | 122.6486 | 123.0148 | 122.8455 | 122.9141 | 122.7356 | 122.9645 | 122.8821 | 122.493 | 122.9141 | 122.7356 | 122.8821 | 122.8455 | 122.9645 | -0.43488 | -0.4303
2630.1406 | 123.0057 | -122.7951 | 0.17853 | 0.16106 | 0.015193 | -0.0016106 | 0.047078 | -0.016829 | -0.010835 | 0.013475 | -0.018311 | 0.15564 | -0.31586 | 0.022888 | 0.050354 | 0.07782 | -0.13275 | 0.20599 | 0.21057 | -0.25635 | 122.4792 | -0.022888 | 122.7768 | 122.818 | -0.12817 | 122.5388 | 0.032043 | 0.29755 | 122.6624 | 123.0011 | 122.8455 | 122.9507 | 122.7768 | 123.0057 | 122.8729 | 122.5388 | 122.9507 | 122.7768 | 122.8729 | 122.8455 | 123.0057 | -0.49438 | -0.43488
2631.8281 | 122.9782 | -122.8043 | 0.20599 | 0.13054 | 0.014552 | -0.00075623 | 0.042379 | -0.015975 | -0.0091259 | 0.013903 | 0.032043 | 0.1236 | -0.25177 | 0.07782 | 0.10986 | 0.14191 | -0.1831 | 0.25177 | 0.20599 | -0.24261 | 122.5525 | -0.082398 | 122.8363 | 122.8821 | -0.096131 | 122.5616 | 0 | 0.28381 | 122.6212 | 123.056 | 122.9141 | 122.9279 | 122.8363 | 123.0103 | 122.9462 | 122.5616 | 122.9279 | 122.8363 | 122.9462 | 122.9141 | 123.0103 | -0.45776 | -0.44861
2633.5781 | 122.9736 | -122.7859 | 0.17853 | 0.17632 | 0.013698 | -0.0035332 | 0.045797 | -0.015334 | -0.010194 | 0.013262 | 0.022888 | 0.11902 | -0.27466 | 0.07782 | 0.10071 | 0.13733 | -0.20599 | 0.25635 | 0.20142 | -0.23346 | 122.5113 | -0.059509 | 122.8088 | 122.8638 | -0.07782 | 122.5525 | 0.022888 | 0.29755 | 122.58 | 123.0423 | 122.8867 | 122.905 | 122.8088 | 122.9874 | 122.9233 | 122.5525 | 122.905 | 122.8088 | 122.9233 | 122.8867 | 122.9874 | -0.45319 | -0.41199
2635.2656 | 123.0881 | -122.7539 | 0.1831 | -0.18227 | 0.012629 | -0.0016106 | 0.041097 | -0.014693 | -0.0099805 | 0.011766 | 0.022888 | 0.15106 | -0.27924 | 0.086975 | 0.091553 | 0.1236 | -0.064087 | 0.28381 | 0.21515 | -0.26093 | 122.4747 | -0.032043 | 122.7768 | 122.8409 | -0.091552 | 122.493 | 0.032044 | 0.30212 | 122.6898 | 123.0377 | 122.8455 | 122.905 | 122.7768 | 122.9691 | 122.8775 | 122.493 | 122.905 | 122.7768 | 122.8775 | 122.8455 | 122.9691 | -0.46234 | -0.44403
2637.0156 | 123.1384 | -122.7859 | 0.16937 | -0.19753 | 0.014338 | -0.0024652 | 0.043874 | -0.016188 | -0.010835 | 0.014116 | -0.068665 | 0.16937 | -0.30212 | -0.018311 | 0.004578 | 0.013733 | 0.045776 | 0.16937 | 0.24719 | -0.27008 | 122.4838 | 0 | 122.7173 | 122.7676 | -0.16479 | 122.5159 | 0.077819 | 0.23346 | 122.8317 | 122.9553 | 122.7905 | 122.9553 | 122.7173 | 123.0331 | 122.7997 | 122.5159 | 122.9553 | 122.7173 | 122.7997 | 122.7905 | 123.0331 | -0.4715 | -0.43945
2638.7656 | 123.1567 | -122.7585 | 0.16022 | -0.23567 | 0.013484 | 0.00095277 | 0.043233 | -0.014266 | -0.012544 | 0.013689 | -0.091553 | 0.17395 | -0.31128 | -0.018311 | 0.004578 | 0.013733 | 0.050354 | 0.15564 | 0.25635 | -0.29297 | 122.4472 | 0.013733 | 122.6669 | 122.7402 | -0.15564 | 122.4655 | 0.096131 | 0.21973 | 122.8088 | 122.9141 | 122.7631 | 122.9324 | 122.6669 | 123.0148 | 122.7722 | 122.4655 | 122.9324 | 122.6669 | 122.7722 | 122.7631 | 123.0148 | -0.4715 | -0.45319
2640.5156 | 123.0103 | -122.8043 | 0.19684 | -0.044937 | 0.01327 | -0.0022516 | 0.04601 | -0.015975 | -0.012971 | 0.015612 | -0.027466 | 0.15564 | -0.32501 | 0.045776 | 0.022888 | 0.045776 | -0.027466 | 0.16479 | 0.22888 | -0.28381 | 122.4792 | -0.041198 | 122.7768 | 122.85 | -0.17395 | 122.5204 | 0.032044 | 0.29755 | 122.7768 | 122.9691 | 122.8271 | 122.9599 | 122.7768 | 123.0331 | 122.85 | 122.5204 | 122.9599 | 122.7768 | 122.85 | 122.8271 | 123.0331 | -0.52185 | -0.48065
2642.2031 | 123.0469 | -122.7859 | 0.19226 | 0.031357 | 0.012629 | 0.0011664 | 0.045369 | -0.013839 | -0.011262 | 0.013262 | -0.064087 | 0.16937 | -0.31128 | -0.018311 | -0.018311 | 0.004578 | 0 | 0.13733 | 0.25177 | -0.2655 | 122.4747 | -0.022888 | 122.7219 | 122.7676 | -0.21057 | 122.5204 | 0.059509 | 0.24719 | 122.7859 | 122.9233 | 122.7676 | 122.9553 | 122.7219 | 123.0377 | 122.7905 | 122.5204 | 122.9553 | 122.7219 | 122.7905 | 122.7676 | 123.0377 | -0.50354 | -0.45776
2643.9531 | 123.0423 | -122.7997 | 0.18768 | 0.10765 | 0.012843 | -0.0028924 | 0.044301 | -0.013198 | -0.011049 | 0.014971 | -0.10529 | 0.17395 | -0.32501 | -0.022888 | -0.009155 | 0.009155 | -0.004578 | 0.10529 | 0.2243 | -0.28839 | 122.4747 | -0.013733 | 122.6944 | 122.7768 | -0.19684 | 122.5113 | 0.036621 | 0.21973 | 122.7951 | 122.905 | 122.7905 | 122.9736 | 122.6944 | 123.024 | 122.8088 | 122.5113 | 122.9736 | 122.6944 | 122.8088 | 122.7905 | 123.024 | -0.5127 | -0.47607
2645.7031 | 123.0469 | -122.7768 | 0.1831 | 0.077133 | 0.014125 | -0.0026788 | 0.043233 | -0.014052 | -0.011476 | 0.01433 | -0.091553 | 0.17395 | -0.31586 | -0.045776 | -0.018311 | 0.009155 | 0 | 0.10986 | 0.25177 | -0.27008 | 122.4609 | -0.009155 | 122.6852 | 122.731 | -0.20142 | 122.5067 | 0.068665 | 0.2243 | 122.7768 | 122.8867 | 122.7585 | 122.9507 | 122.6852 | 123.0286 | 122.7859 | 122.5067 | 122.9507 | 122.6852 | 122.7859 | 122.7585 | 123.0286 | -0.49896 | -0.45319
2647.3906 | 123.1293 | -122.7448 | 0.14648 | 0.046615 | 0.010921 | -0.0018244 | 0.035329 | -0.016188 | -0.0078443 | 0.01668 | -0.045776 | 0.15564 | -0.25177 | 0.013733 | 0.054932 | 0.086975 | -0.091553 | 0.21515 | 0.21973 | -0.25635 | 122.493 | 0.009156 | 122.699 | 122.7585 | -0.091552 | 122.4884 | 0.073243 | 0.20599 | 122.6532 | 122.9599 | 122.7997 | 122.9004 | 122.699 | 122.9645 | 122.8317 | 122.4884 | 122.9004 | 122.699 | 122.8317 | 122.7997 | 122.9645 | -0.39825 | -0.40283
2649.1406 | 123.0927 | -122.7676 | 0.1831 | -0.18227 | 0.013057 | -0.0028924 | 0.045156 | -0.01512 | -0.013185 | 0.013689 | -0.073242 | 0.17853 | -0.33875 | 0.013733 | 0.032043 | 0.036621 | 0.009155 | 0.19226 | 0.21515 | -0.27924 | 122.4289 | -0.004577 | 122.6944 | 122.7814 | -0.15106 | 122.4884 | 0.032044 | 0.2655 | 122.7768 | 122.9599 | 122.7997 | 122.9462 | 122.6944 | 122.9828 | 122.8043 | 122.4884 | 122.9462 | 122.6944 | 122.8043 | 122.7997 | 122.9828 | -0.52185 | -0.46234
2650.9062 | 123.1155 | -122.7631 | 0.15564 | 0.077133 | 0.016475 | -0.0054558 | 0.038106 | -0.015975 | -0.0076305 | 0.014757 | -0.045776 | 0.15106 | -0.28381 | 0.013733 | 0.082397 | 0.10071 | -0.091553 | 0.21973 | 0.19684 | -0.26093 | 122.4792 | -0.004578 | 122.7173 | 122.7768 | -0.073243 | 122.5021 | 0.041198 | 0.23804 | 122.6715 | 122.9828 | 122.8455 | 122.9141 | 122.7173 | 122.9599 | 122.8638 | 122.5021 | 122.9141 | 122.7173 | 122.8638 | 122.8455 | 122.9599 | -0.43945 | -0.41657
2652.6094 | 123.1522 | -122.7585 | 0.15564 | -0.23567 | 0.012416 | -0.0035332 | 0.043019 | -0.016616 | -0.0099805 | 0.014116 | -0.10071 | 0.16022 | -0.31128 | -0.022888 | 0 | 0.009155 | 0.059509 | 0.16479 | 0.24261 | -0.28381 | 122.4472 | 0.004577 | 122.6578 | 122.7356 | -0.15564 | 122.4747 | 0.086975 | 0.21057 | 122.818 | 122.9233 | 122.7585 | 122.9187 | 122.6578 | 123.0011 | 122.7676 | 122.4747 | 122.9187 | 122.6578 | 122.7676 | 122.7585 | 123.0011 | -0.46692 | -0.43945
2654.2969 | 123.143 | -122.7814 | 0.16022 | -0.27382 | 0.013911 | -0.0043878 | 0.043233 | -0.014907 | -0.0093395 | 0.012621 | -0.082397 | 0.17395 | -0.32044 | -0.027466 | -0.013733 | 0.009155 | 0.073242 | 0.15106 | 0.24261 | -0.28381 | 122.4609 | 0.013733 | 122.699 | 122.7539 | -0.17395 | 122.4976 | 0.082398 | 0.23804 | 122.8546 | 122.9324 | 122.7676 | 122.9553 | 122.699 | 123.024 | 122.7905 | 122.4976 | 122.9553 | 122.699 | 122.7905 | 122.7676 | 123.024 | -0.48065 | -0.44403
2656.0625 | 123.111 | -122.7814 | 0.1831 | -0.25856 | 0.01327 | -0.0043878 | 0.043019 | -0.015334 | -0.012117 | 0.012194 | 0.004578 | 0.15106 | -0.29297 | 0.068665 | 0.073242 | 0.082397 | -0.045776 | 0.25177 | 0.22888 | -0.2655 | 122.4884 | -0.032043 | 122.7859 | 122.85 | -0.10986 | 122.5159 | 0.045777 | 0.29755 | 122.7356 | 123.0331 | 122.8546 | 122.9324 | 122.7859 | 123.0103 | 122.8638 | 122.5159 | 122.9324 | 122.7859 | 122.8638 | 122.8546 | 123.0103 | -0.47607 | -0.44861
2657.8125 | 123.0469 | -122.7905 | 0.20599 | 0.054245 | 0.011989 | 0.0028754 | 0.047078 | -0.014907 | -0.01233 | 0.013903 | -0.045776 | 0.1831 | -0.32501 | -0.027466 | -0.032043 | -0.004578 | 0.004578 | 0.12817 | 0.2655 | -0.27466 | 122.4655 | -0.022889 | 122.7448 | 122.7631 | -0.23804 | 122.5159 | 0.059509 | 0.27924 | 122.7951 | 122.9187 | 122.7585 | 122.9736 | 122.7448 | 123.056 | 122.7859 | 122.5159 | 122.9736 | 122.7448 | 122.7859 | 122.7585 | 123.056 | -0.53101 | -0.48065
2659.5 | 123.0698 | -122.8134 | 0.17853 | 0.038986 | 0.013698 | -0.00011543 | 0.045797 | -0.013625 | -0.0091259 | 0.013262 | -0.091553 | 0.19226 | -0.32044 | -0.050354 | -0.027466 | -0.018311 | 0.032043 | 0.091553 | 0.24261 | -0.27008 | 122.493 | 0.013733 | 122.7219 | 122.7631 | -0.20599 | 122.5433 | 0.064087 | 0.22888 | 122.8455 | 122.905 | 122.7859 | 123.0057 | 122.7219 | 123.056 | 122.7951 | 122.5433 | 123.0057 | 122.7219 | 122.7951 | 122.7859 | 123.056 | -0.49896 | -0.44861
2661.1875 | 123.1155 | -122.7814 | 0.16937 | 0.061874 | 0.012416 | 0.0011664 | 0.039601 | -0.015975 | -0.0074169 | 0.013048 | -0.032043 | 0.13275 | -0.27466 | 0.018311 | 0.073242 | 0.091553 | -0.11902 | 0.21057 | 0.21057 | -0.2655 | 122.5067 | -0.036622 | 122.7493 | 122.7997 | -0.096131 | 122.5159 | 0.041198 | 0.24262 | 122.6624 | 122.9919 | 122.8546 | 122.9141 | 122.7493 | 122.9919 | 122.8729 | 122.5159 | 122.9141 | 122.7493 | 122.8729 | 122.8546 | 122.9919 | -0.44403 | -0.43488
2662.9375 | 123.0515 | -122.8043 | 0.17853 | 0.12291 | 0.011989 | 0.0050116 | 0.044942 | -0.014693 | -0.010621 | 0.013689 | -0.10071 | 0.16479 | -0.32959 | -0.032043 | -0.018311 | 0 | -0.018311 | 0.11902 | 0.23804 | -0.28839 | 122.4747 | -0.013733 | 122.7036 | 122.7722 | -0.19684 | 122.5159 | 0.059509 | 0.22888 | 122.7859 | 122.9233 | 122.7859 | 122.9691 | 122.7036 | 123.0423 | 122.8043 | 122.5159 | 122.9691 | 122.7036 | 122.8043 | 122.7859 | 123.0423 | -0.50812 | -0.46692
2664.625 | 123.0194 | -122.8088 | 0.20599 | 0.11528 | 0.012416 | -0.0067376 | 0.039388 | -0.01512 | -0.0084851 | 0.01433 | 0.009155 | 0.1236 | -0.27008 | 0.054932 | 0.10529 | 0.13733 | -0.16937 | 0.25635 | 0.21057 | -0.25635 | 122.5388 | -0.082398 | 122.818 | 122.8638 | -0.10071 | 122.5525 | 0.004577 | 0.27924 | 122.6395 | 123.0652 | 122.9141 | 122.9324 | 122.818 | 123.0194 | 122.9462 | 122.5525 | 122.9324 | 122.818 | 122.9462 | 122.9141 | 123.0194 | -0.47608 | -0.46234
2666.3125 | 123.1338 | -122.7814 | 0.16937 | -0.2433 | 0.012416 | -0.00032903 | 0.04366 | -0.014052 | -0.012544 | 0.015825 | -0.091553 | 0.16022 | -0.33417 | -0.027466 | 0.013733 | 0.013733 | 0.054932 | 0.15564 | 0.25635 | -0.28381 | 122.4472 | -0.009156 | 122.6898 | 122.7539 | -0.15564 | 122.4976 | 0.086975 | 0.24261 | 122.8363 | 122.937 | 122.7951 | 122.9416 | 122.6898 | 123.0377 | 122.7951 | 122.4976 | 122.9416 | 122.6898 | 122.7951 | 122.7951 | 123.0377 | -0.50354 | -0.45319
2668.0625 | 123.0789 | -122.7722 | 0.16937 | -0.15175 | 0.012202 | -0.0016106 | 0.03832 | -0.018111 | -0.0080579 | 0.012194 | 0.027466 | 0.14191 | -0.27008 | 0.091553 | 0.1236 | 0.17853 | -0.14648 | 0.31586 | 0.18768 | -0.24719 | 122.5021 | -0.027466 | 122.7997 | 122.8638 | -0.045777 | 122.525 | 0.01831 | 0.29755 | 122.6257 | 123.0881 | 122.8958 | 122.9141 | 122.7997 | 122.9599 | 122.9507 | 122.525 | 122.9141 | 122.7997 | 122.9507 | 122.8958 | 122.9599 | -0.43945 | -0.41656
2669.8125 | 122.9965 | -122.8134 | 0.19226 | -0.1136 | 0.013698 | 0.00052557 | 0.047719 | -0.013625 | -0.012758 | 0.013475 | -0.009155 | 0.15564 | -0.32044 | 0.054932 | 0.050354 | 0.054932 | -0.041199 | 0.19226 | 0.23346 | -0.28381 | 122.493 | -0.036621 | 122.8043 | 122.8683 | -0.14191 | 122.5296 | 0.041198 | 0.31128 | 122.7722 | 123.0057 | 122.8638 | 122.9691 | 122.8043 | 123.0469 | 122.8683 | 122.5296 | 122.9691 | 122.8043 | 122.8683 | 122.8638 | 123.0469 | -0.5127 | -0.47607
2671.5 | 123.0515 | -122.8088 | 0.17395 | 0.12291 | 0.014979 | -0.001397 | 0.045156 | -0.014052 | -0.012117 | 0.014971 | -0.11444 | 0.16937 | -0.30212 | -0.018311 | -0.013733 | 0.004578 | -0.018311 | 0.10071 | 0.23804 | -0.27008 | 122.5067 | -0.004577 | 122.6944 | 122.7905 | -0.18768 | 122.5388 | 0.064087 | 0.18768 | 122.7905 | 122.9095 | 122.7951 | 122.9782 | 122.6944 | 123.0469 | 122.8134 | 122.5388 | 122.9782 | 122.6944 | 122.8134 | 122.7951 | 123.0469 | -0.47607 | -0.44403
2673.1875 | 123.0194 | -122.8271 | 0.19684 | -0.14412 | 0.012416 | 0.00095277 | 0.043874 | -0.014907 | -0.011476 | 0.014544 | -0.027466 | 0.15564 | -0.32044 | 0.036621 | 0.059509 | 0.054932 | -0.022888 | 0.19684 | 0.22888 | -0.27466 | 122.5067 | -0.041198 | 122.7997 | 122.8638 | -0.13733 | 122.5525 | 0.032044 | 0.29297 | 122.8043 | 123.024 | 122.8867 | 122.9828 | 122.7997 | 123.056 | 122.8821 | 122.5525 | 122.9828 | 122.7997 | 122.8821 | 122.8867 | 123.056 | -0.51727 | -0.4715
2674.9531 | 123.056 | -122.8043 | 0.18768 | 0.10002 | 0.011134 | 0.0015936 | 0.046865 | -0.011489 | -0.011262 | 0.013475 | -0.10071 | 0.17395 | -0.32044 | -0.041199 | -0.004578 | 0.004578 | 0 | 0.10986 | 0.25635 | -0.27008 | 122.4838 | -0.013733 | 122.7036 | 122.7631 | -0.19226 | 122.5342 | 0.068665 | 0.21973 | 122.8043 | 122.9141 | 122.7997 | 122.9782 | 122.7036 | 123.0606 | 122.8088 | 122.5342 | 122.9782 | 122.7036 | 122.8088 | 122.7997 | 123.0606 | -0.50812 | -0.45776
2676.7031 | 123.0743 | -122.7859 | 0.17395 | -0.21278 | 0.013057 | -0.0011834 | 0.04131 | -0.015548 | -0.013185 | 0.012621 | -0.082397 | 0.17853 | -0.30212 | 0.013733 | 0.032043 | 0.041199 | 0.013733 | 0.16937 | 0.24261 | -0.31128 | 122.4838 | 0.004578 | 122.7036 | 122.7997 | -0.14191 | 122.4747 | 0.068665 | 0.21973 | 122.7997 | 122.9553 | 122.818 | 122.9645 | 122.7036 | 123.0286 | 122.8271 | 122.4747 | 122.9645 | 122.7036 | 122.8271 | 122.818 | 123.0286 | -0.47607 | -0.48523
2678.4219 | 123.0331 | -122.7814 | 0.19226 | 0.13817 | 0.01327 | 0.002021 | 0.03832 | -0.014052 | -0.010835 | 0.013475 | 0 | 0.1236 | -0.27008 | 0.045776 | 0.10986 | 0.1236 | -0.17395 | 0.24261 | 0.20599 | -0.25177 | 122.5113 | -0.068665 | 122.7814 | 122.8271 | -0.082398 | 122.5296 | 0.013733 | 0.27008 | 122.6074 | 123.024 | 122.8912 | 122.905 | 122.7814 | 122.9874 | 122.905 | 122.5296 | 122.905 | 122.7814 | 122.905 | 122.8912 | 122.9874 | -0.46234 | -0.44403
2680.1719 | 123.0698 | -122.7585 | 0.16937 | 0.092392 | 0.012202 | -0.003747 | 0.038747 | -0.017043 | -0.0089123 | 0.014116 | -0.018311 | 0.13275 | -0.27466 | 0.027466 | 0.068665 | 0.10529 | -0.1236 | 0.21973 | 0.20142 | -0.27008 | 122.4838 | -0.036622 | 122.7402 | 122.7859 | -0.10071 | 122.4884 | 0.032043 | 0.25635 | 122.6349 | 122.9782 | 122.8271 | 122.8912 | 122.7402 | 122.9599 | 122.8638 | 122.4884 | 122.8912 | 122.7402 | 122.8638 | 122.8271 | 122.9599 | -0.44403 | -0.43945
2681.9219 | 123.1338 | -122.7539 | 0.16022 | -0.26619 | 0.013484 | -0.0026788 | 0.041738 | -0.015761 | -0.0091259 | 0.012621 | -0.10071 | 0.19684 | -0.3479 | -0.013733 | -0.027466 | 0.004578 | 0.050354 | 0.14648 | 0.25635 | -0.30212 | 122.406 | 0.036621 | 122.6532 | 122.7402 | -0.18768 | 122.4518 | 0.096131 | 0.24719 | 122.8043 | 122.9004 | 122.7264 | 122.9507 | 122.6532 | 123.0103 | 122.7585 | 122.4518 | 122.9507 | 122.6532 | 122.7585 | 122.7264 | 123.0103 | -0.50812 | -0.46234
2683.6875 | 123.0057 | -122.8134 | 0.20599 | -0.052567 | 0.013484 | -0.00054263 | 0.04601 | -0.014693 | -0.011049 | 0.012194 | -0.022888 | 0.15564 | -0.32044 | 0.032043 | 0.036621 | 0.073242 | -0.032043 | 0.20599 | 0.24719 | -0.2655 | 122.493 | -0.050354 | 122.7905 | 122.8455 | -0.16937 | 122.5479 | 0.041198 | 0.29755 | 122.7814 | 123.0194 | 122.85 | 122.9691 | 122.7905 | 123.0606 | 122.8867 | 122.5479 | 122.9691 | 122.7905 | 122.8867 | 122.85 | 123.0606 | -0.52643 | -0.4715
2685.3906 | 123.0652 | -122.7905 | 0.18768 | 0.11528 | 0.013698 | -0.0011834 | 0.040029 | -0.015761 | -0.010408 | 0.015612 | -0.009155 | 0.13733 | -0.27466 | 0.041199 | 0.082397 | 0.09613 | -0.12817 | 0.22888 | 0.21515 | -0.25177 | 122.5159 | -0.050354 | 122.7814 | 122.8317 | -0.10529 | 122.5388 | 0.027466 | 0.2655 | 122.6624 | 123.0194 | 122.8729 | 122.9279 | 122.7814 | 123.0057 | 122.8867 | 122.5388 | 122.9279 | 122.7814 | 122.8867 | 122.8729 | 123.0057 | -0.46234 | -0.43945
2687.125 | 123.0789 | -122.7814 | 0.1831 | -0.15938 | 0.011561 | 0.00031197 | 0.045369 | -0.014693 | -0.012971 | 0.01433 | -0.036621 | 0.16937 | -0.32501 | 0.018311 | 0.054932 | 0.054932 | 0 | 0.1831 | 0.24719 | -0.27008 | 122.4564 | -0.013732 | 122.7448 | 122.7997 | -0.12817 | 122.5113 | 0.064087 | 0.28839 | 122.7814 | 122.9645 | 122.8363 | 122.9507 | 122.7448 | 123.0286 | 122.8363 | 122.5113 | 122.9507 | 122.7448 | 122.8363 | 122.8363 | 123.0286 | -0.50812 | -0.45319
2688.8906 | 123.0011 | -122.7951 | 0.21515 | -0.022049 | 0.011561 | -0.0026788 | 0.048787 | -0.013198 | -0.013826 | 0.013475 | -0.032043 | 0.1831 | -0.30212 | 0.009155 | 0.013733 | 0.032043 | 0.004578 | 0.16022 | 0.24261 | -0.29297 | 122.493 | -0.032044 | 122.7631 | 122.8043 | -0.20142 | 122.5021 | 0.027466 | 0.27008 | 122.7997 | 122.9553 | 122.8088 | 122.9782 | 122.7631 | 123.0377 | 122.8271 | 122.5021 | 122.9782 | 122.7631 | 122.8271 | 122.8088 | 123.0377 | -0.51727 | -0.50812
2690.6562 | 123.0652 | -122.7951 | 0.18768 | 0.15343 | 0.012629 | -0.00075623 | 0.043874 | -0.015548 | -0.0095531 | 0.014757 | -0.07782 | 0.18768 | -0.32044 | -0.041199 | -0.013733 | 0.018311 | -0.022888 | 0.11444 | 0.24261 | -0.29297 | 122.4747 | 0 | 122.7173 | 122.7539 | -0.20142 | 122.5021 | 0.054932 | 0.24262 | 122.7722 | 122.9095 | 122.7814 | 122.9828 | 122.7173 | 123.0377 | 122.8134 | 122.5021 | 122.9828 | 122.7173 | 122.8134 | 122.7814 | 123.0377 | -0.50812 | -0.48065
2692.3594 | 123.0698 | -122.7859 | 0.17395 | -0.17464 | 0.011775 | -0.003106 | 0.042165 | -0.016402 | -0.0099805 | 0.013262 | -0.059509 | 0.17853 | -0.32959 | 0.009155 | 0.050354 | 0.050354 | 0.013733 | 0.17853 | 0.23804 | -0.27924 | 122.4564 | 0.004578 | 122.7264 | 122.7951 | -0.1236 | 122.5067 | 0.064087 | 0.27008 | 122.7997 | 122.9645 | 122.8363 | 122.9645 | 122.7264 | 123.024 | 122.8363 | 122.5067 | 122.9645 | 122.7264 | 122.8363 | 122.8363 | 123.024 | -0.50354 | -0.45319
2694.125 | 123.0743 | -122.7814 | 0.1831 | -0.19753 | 0.012629 | -0.0016106 | 0.044088 | -0.014907 | -0.0093395 | 0.014116 | -0.059509 | 0.17395 | -0.31128 | 0.027466 | 0.036621 | 0.054932 | 0.004578 | 0.20142 | 0.25177 | -0.27008 | 122.4701 | -0.009155 | 122.7219 | 122.8088 | -0.14648 | 122.5113 | 0.068665 | 0.25177 | 122.7859 | 122.9828 | 122.818 | 122.9553 | 122.7219 | 123.0331 | 122.8363 | 122.5113 | 122.9553 | 122.7219 | 122.8363 | 122.818 | 123.0331 | -0.49438 | -0.45319
2695.8906 | 123.0194 | -122.818 | 0.21515 | -0.067826 | 0.011134 | -0.003747 | 0.043874 | -0.014693 | -0.012758 | 0.012621 | -0.022888 | 0.16479 | -0.32959 | 0.032043 | 0.050354 | 0.068665 | -0.027466 | 0.19684 | 0.23346 | -0.27008 | 122.4884 | -0.050354 | 122.7951 | 122.85 | -0.16479 | 122.5479 | 0.01831 | 0.3067 | 122.7905 | 123.0148 | 122.8683 | 122.9828 | 122.7951 | 123.0515 | 122.8867 | 122.5479 | 122.9828 | 122.7951 | 122.8867 | 122.8683 | 123.0515 | -0.54474 | -0.48523
2697.6562 | 123.143 | -122.7356 | 0.16937 | -0.18227 | 0.014552 | -0.0043878 | 0.038961 | -0.017256 | -0.010194 | 0.014971 | -0.082397 | 0.18768 | -0.3067 | -0.032043 | 0.027466 | 0.022888 | 0.050354 | 0.15106 | 0.25635 | -0.29755 | 122.4289 | 0.01831 | 122.6532 | 122.7036 | -0.14191 | 122.4381 | 0.086975 | 0.2243 | 122.7859 | 122.8867 | 122.7631 | 122.9233 | 122.6532 | 122.9919 | 122.7585 | 122.4381 | 122.9233 | 122.6532 | 122.7585 | 122.7631 | 122.9919 | -0.47607 | -0.46692
2699.3594 | 123.0515 | -122.7859 | 0.19226 | 0.12291 | 0.01562 | 0.00138 | 0.044088 | -0.014052 | -0.0093395 | 0.013689 | -0.073242 | 0.18768 | -0.31586 | -0.050354 | -0.018311 | 0.018311 | 0 | 0.11902 | 0.21973 | -0.29755 | 122.4701 | -0.004578 | 122.7127 | 122.7356 | -0.21057 | 122.4884 | 0.027466 | 0.24261 | 122.7859 | 122.905 | 122.7676 | 122.9736 | 122.7127 | 123.0057 | 122.8043 | 122.4884 | 122.9736 | 122.7127 | 122.8043 | 122.7676 | 123.0057 | -0.50812 | -0.48981
2701.0625 | 123.0835 | -122.7768 | 0.1831 | -0.18227 | 0.012416 | -0.00032903 | 0.039174 | -0.015761 | -0.0095531 | 0.013475 | 0.009155 | 0.11444 | -0.24719 | 0.068665 | 0.1236 | 0.15106 | -0.11902 | 0.29755 | 0.1831 | -0.24719 | 122.5296 | -0.068664 | 122.7859 | 122.8455 | -0.059509 | 122.5296 | 0 | 0.25635 | 122.6578 | 123.0743 | 122.9004 | 122.8912 | 122.7859 | 122.9599 | 122.9279 | 122.5296 | 122.8912 | 122.7859 | 122.9279 | 122.9004 | 122.9599 | -0.4303 | -0.4303
2702.8125 | 122.9919 | -122.8088 | 0.1831 | 0.22972 | 0.015407 | 0.0033026 | 0.04601 | -0.013839 | -0.012117 | 0.013903 | -0.036621 | 0.15564 | -0.29755 | 0.050354 | 0.073242 | 0.10986 | -0.13275 | 0.23804 | 0.20599 | -0.25177 | 122.5113 | -0.027465 | 122.7722 | 122.8592 | -0.10986 | 122.5571 | 0.022889 | 0.26092 | 122.6761 | 123.0469 | 122.8821 | 122.9645 | 122.7722 | 123.0148 | 122.9187 | 122.5571 | 122.9645 | 122.7722 | 122.9187 | 122.8821 | 123.0148 | -0.48065 | -0.43488
2704.5781 | 123.024 | -122.7997 | 0.20142 | 0.13054 | 0.012843 | 0.00138 | 0.041097 | -0.014907 | -0.010194 | 0.01198 | 0.027466 | 0.14648 | -0.27466 | 0.073242 | 0.086975 | 0.13733 | -0.17395 | 0.2655 | 0.19684 | -0.24261 | 122.525 | -0.054932 | 122.8271 | 122.8729 | -0.11444 | 122.5571 | -0.004578 | 0.30212 | 122.6257 | 123.0652 | 122.8867 | 122.9462 | 122.8271 | 122.9965 | 122.937 | 122.5571 | 122.9462 | 122.8271 | 122.937 | 122.8867 | 122.9965 | -0.47607 | -0.44403
2706.2812 | 122.9965 | -122.8134 | 0.21057 | -0.10597 | 0.011775 | 0.00073917 | 0.045583 | -0.015761 | -0.01233 | 0.012835 | -0.027466 | 0.15106 | -0.29755 | 0.045776 | 0.045776 | 0.064087 | -0.036621 | 0.21057 | 0.22888 | -0.27008 | 122.5159 | -0.059509 | 122.7859 | 122.8592 | -0.1648 | 122.5433 | 0.018311 | 0.27008 | 122.7768 | 123.024 | 122.8592 | 122.9645 | 122.7859 | 123.0423 | 122.8775 | 122.5433 | 122.9645 | 122.7859 | 122.8775 | 122.8592 | 123.0423 | -0.50812 | -0.48065
2708.0312 | 123.0377 | -122.7997 | 0.18768 | 0.11528 | 0.01028 | 0.0039436 | 0.039815 | -0.015334 | -0.0093395 | 0.011766 | 0.013733 | 0.14191 | -0.28381 | 0.064087 | 0.07782 | 0.13275 | -0.15564 | 0.23804 | 0.21057 | -0.26093 | 122.5159 | -0.045776 | 122.8134 | 122.8638 | -0.10986 | 122.5388 | 0.022888 | 0.29755 | 122.644 | 123.0377 | 122.8775 | 122.9416 | 122.8134 | 123.0103 | 122.9324 | 122.5388 | 122.9416 | 122.8134 | 122.9324 | 122.8775 | 123.0103 | -0.4715 | -0.44861
2709.7812 | 123.1567 | -122.7951 | 0.16937 | -0.23567 | 0.013698 | -0.0028924 | 0.043233 | -0.015548 | -0.01169 | 0.013262 | -0.07782 | 0.16937 | -0.31586 | -0.013733 | 0.018311 | 0.022888 | 0.027466 | 0.1831 | 0.24261 | -0.3067 | 122.4792 | 0 | 122.7173 | 122.7814 | -0.15106 | 122.4884 | 0.073242 | 0.23804 | 122.8226 | 122.9782 | 122.8134 | 122.9645 | 122.7173 | 123.0377 | 122.818 | 122.4884 | 122.9645 | 122.7173 | 122.818 | 122.8134 | 123.0377 | -0.48523 | -0.47607
2711.5312 | 123.1384 | -122.7585 | 0.15106 | -0.28145 | 0.013057 | -0.008233 | 0.044088 | -0.017043 | -0.0086987 | 0.012835 | -0.086975 | 0.1831 | -0.33417 | -0.027466 | -0.013733 | 0.013733 | 0.082397 | 0.15106 | 0.26093 | -0.29297 | 122.4243 | 0.032043 | 122.6715 | 122.731 | -0.16479 | 122.4655 | 0.10986 | 0.24719 | 122.8409 | 122.9095 | 122.7448 | 122.9416 | 122.6715 | 123.0194 | 122.7722 | 122.4655 | 122.9416 | 122.6715 | 122.7722 | 122.7448 | 123.0194 | -0.48523 | -0.44403
2713.2188 | 123.1567 | -122.7676 | 0.16479 | -0.25093 | 0.015193 | -0.0035332 | 0.041951 | -0.017043 | -0.011049 | 0.014116 | -0.09613 | 0.1831 | -0.32959 | -0.018311 | 0 | -0.004578 | 0.068665 | 0.16937 | 0.26093 | -0.28839 | 122.438 | 0.01831 | 122.6715 | 122.7493 | -0.16479 | 122.4792 | 0.09613 | 0.23346 | 122.8363 | 122.937 | 122.7676 | 122.9507 | 122.6715 | 123.0286 | 122.7631 | 122.4792 | 122.9507 | 122.6715 | 122.7631 | 122.7676 | 123.0286 | -0.49438 | -0.45319
2714.9844 | 123.1064 | -122.7585 | 0.16937 | -0.12123 | 0.013698 | -0.0022516 | 0.035756 | -0.014479 | -0.0097669 | 0.013475 | -0.009155 | 0.13733 | -0.29297 | 0.082397 | 0.10986 | 0.15564 | -0.13733 | 0.28381 | 0.21973 | -0.27008 | 122.4655 | -0.032044 | 122.7493 | 122.8409 | -0.05951 | 122.4884 | 0.050354 | 0.28381 | 122.6212 | 123.0423 | 122.8683 | 122.8958 | 122.7493 | 122.9782 | 122.9141 | 122.4884 | 122.8958 | 122.7493 | 122.9141 | 122.8683 | 122.9782 | -0.46234 | -0.43945
2716.75 | 123.1476 | -122.7585 | 0.16479 | 0.046615 | 0.014552 | -0.0039606 | 0.042379 | -0.01277 | -0.0089123 | 0.012407 | -0.045776 | 0.14648 | -0.28381 | 0.013733 | 0.050354 | 0.091553 | -0.09613 | 0.21057 | 0.22888 | -0.2655 | 122.4747 | -0.018311 | 122.7127 | 122.7722 | -0.11444 | 122.493 | 0.064087 | 0.23804 | 122.6624 | 122.9691 | 122.8088 | 122.905 | 122.7127 | 122.9874 | 122.85 | 122.493 | 122.905 | 122.7127 | 122.85 | 122.8088 | 122.9874 | -0.44861 | -0.4303
2718.5156 | 123.0377 | -122.7997 | 0.1831 | 0.11528 | 0.011561 | -0.0039606 | 0.044088 | -0.015761 | -0.0099805 | 0.01198 | 0.022888 | 0.14191 | -0.27008 | 0.068665 | 0.073242 | 0.12817 | -0.18768 | 0.24261 | 0.21515 | -0.26093 | 122.5296 | -0.041198 | 122.8226 | 122.8683 | -0.10986 | 122.5388 | 0.032044 | 0.29297 | 122.612 | 123.0423 | 122.8729 | 122.9416 | 122.8226 | 123.0148 | 122.9279 | 122.5388 | 122.9416 | 122.8226 | 122.9279 | 122.8729 | 123.0148 | -0.45319 | -0.44403
2720.2031 | 123.024 | -122.818 | 0.1831 | 0.13817 | 0.010707 | -0.0011834 | 0.044728 | -0.017043 | -0.0099805 | 0.013689 | 0.027466 | 0.13733 | -0.27008 | 0.086975 | 0.10071 | 0.14191 | -0.1831 | 0.26093 | 0.20142 | -0.25635 | 122.5479 | -0.045776 | 122.8455 | 122.905 | -0.082397 | 122.5616 | 0.018311 | 0.29755 | 122.6349 | 123.0789 | 122.9187 | 122.9553 | 122.8455 | 123.0194 | 122.9599 | 122.5616 | 122.9553 | 122.8455 | 122.9599 | 122.9187 | 123.0194 | -0.45319 | -0.43945
2721.8906 | 123.1338 | -122.7631 | 0.16022 | -0.19753 | 0.013484 | -0.0011834 | 0.04366 | -0.014907 | -0.01169 | 0.01198 | -0.064087 | 0.16937 | -0.32044 | -0.004578 | 0.013733 | 0.022888 | 0.027466 | 0.17853 | 0.24719 | -0.28381 | 122.4426 | 0.009156 | 122.699 | 122.7585 | -0.14648 | 122.4792 | 0.086975 | 0.25635 | 122.7905 | 122.9416 | 122.7768 | 122.9324 | 122.699 | 123.0103 | 122.7859 | 122.4792 | 122.9324 | 122.699 | 122.7859 | 122.7768 | 123.0103 | -0.48065 | -0.44403
2723.5781 | 123.1338 | -122.7539 | 0.15106 | -0.25856 | 0.015193 | 9.8166e-05 | 0.043233 | -0.015548 | -0.0099805 | 0.01198 | -0.032043 | 0.13733 | -0.32501 | 0.009155 | 0.027466 | 0.036621 | 0.022888 | 0.1831 | 0.24261 | -0.28381 | 122.4289 | -0.013733 | 122.7219 | 122.7631 | -0.1236 | 122.4701 | 0.091553 | 0.29297 | 122.7768 | 122.937 | 122.7814 | 122.8912 | 122.7219 | 122.9965 | 122.7905 | 122.4701 | 122.8912 | 122.7219 | 122.7905 | 122.7814 | 122.9965 | -0.47607 | -0.43488
2725.3125 | 123.1384 | -122.7585 | 0.17395 | -0.28908 | 0.010707 | -0.004815 | 0.041738 | -0.015975 | -0.011903 | 0.011126 | -0.022888 | 0.16937 | -0.31128 | 0.013733 | 0.036621 | 0.059509 | 0.004578 | 0.20142 | 0.25177 | -0.27924 | 122.4472 | -0.004577 | 122.7356 | 122.7722 | -0.13733 | 122.4792 | 0.07782 | 0.28839 | 122.7631 | 122.9599 | 122.7951 | 122.9279 | 122.7356 | 123.0103 | 122.818 | 122.4792 | 122.9279 | 122.7356 | 122.818 | 122.7951 | 123.0103 | -0.48523 | -0.45319
2727.0156 | 123.0743 | -122.7539 | 0.18768 | 0.092392 | 0.011775 | -0.00075623 | 0.04067 | -0.01747 | -0.010194 | 0.01433 | -0.018311 | 0.14191 | -0.28839 | 0.036621 | 0.07782 | 0.11444 | -0.13275 | 0.21973 | 0.19684 | -0.27466 | 122.4655 | -0.045776 | 122.7356 | 122.7905 | -0.10986 | 122.4792 | 0.009155 | 0.27008 | 122.6212 | 122.9736 | 122.8317 | 122.8958 | 122.7356 | 122.9507 | 122.8683 | 122.4792 | 122.8958 | 122.7356 | 122.8683 | 122.8317 | 122.9507 | -0.47607 | -0.46234
2728.7656 | 123.0652 | -122.7676 | 0.17853 | 0.11528 | 0.012843 | -0.0035332 | 0.047506 | -0.014052 | -0.0086987 | 0.012194 | -0.091553 | 0.16479 | -0.33875 | -0.032043 | -0.013733 | -0.004578 | 0 | 0.11444 | 0.24261 | -0.3067 | 122.4289 | -0.013733 | 122.6761 | 122.7356 | -0.19226 | 122.4609 | 0.064087 | 0.24719 | 122.7676 | 122.8821 | 122.7539 | 122.9324 | 122.6761 | 123.0103 | 122.7631 | 122.4609 | 122.9324 | 122.6761 | 122.7631 | 122.7539 | 123.0103 | -0.51727 | -0.48523
2730.5156 | 123.0057 | -122.7997 | 0.20599 | -0.060196 | 0.014766 | -0.002038 | 0.046437 | -0.01512 | -0.013612 | 0.012407 | -0.009155 | 0.17853 | -0.3067 | 0.022888 | 0.036621 | 0.059509 | -0.036621 | 0.16937 | 0.22888 | -0.28381 | 122.493 | -0.027466 | 122.7905 | 122.8226 | -0.16937 | 122.5159 | 0.022888 | 0.29755 | 122.7631 | 122.9691 | 122.8363 | 122.9782 | 122.7905 | 123.0286 | 122.8592 | 122.5159 | 122.9782 | 122.7905 | 122.8592 | 122.8363 | 123.0286 | -0.5127 | -0.48981
2732.2031 | 123.1293 | -122.7768 | 0.16937 | -0.01442 | 0.014125 | -0.00054263 | 0.036397 | -0.016402 | -0.010835 | 0.013262 | -0.054932 | 0.16022 | -0.29297 | 0.018311 | 0.064087 | 0.086975 | -0.091553 | 0.20599 | 0.20599 | -0.27008 | 122.4838 | -0.009156 | 122.7219 | 122.7951 | -0.10529 | 122.5067 | 0.036621 | 0.23804 | 122.6852 | 122.9828 | 122.8409 | 122.937 | 122.7219 | 122.9828 | 122.8638 | 122.5067 | 122.937 | 122.7219 | 122.8638 | 122.8409 | 122.9828 | -0.46234 | -0.43945
2733.9531 | 123.111 | -122.7631 | 0.17853 | -0.075455 | 0.012629 | -0.0024652 | 0.040029 | -0.017256 | -0.0069897 | 0.012835 | -0.013733 | 0.14191 | -0.28381 | 0.086975 | 0.1236 | 0.14191 | -0.12817 | 0.30212 | 0.19684 | -0.25635 | 122.4792 | -0.036621 | 122.7493 | 122.85 | -0.054932 | 122.5067 | 0.01831 | 0.27008 | 122.6349 | 123.0652 | 122.8867 | 122.905 | 122.7493 | 122.9599 | 122.905 | 122.5067 | 122.905 | 122.7493 | 122.905 | 122.8867 | 122.9599 | -0.46234 | -0.43488
2735.7188 | 123.1522 | -122.7585 | 0.15564 | 0.023727 | 0.010066 | -0.0035332 | 0.040029 | -0.018538 | -0.0082715 | 0.010912 | -0.054932 | 0.14648 | -0.31586 | 0.022888 | 0.045776 | 0.073242 | -0.09613 | 0.21515 | 0.21515 | -0.2655 | 122.4426 | -0.009156 | 122.7036 | 122.7814 | -0.10986 | 122.493 | 0.059509 | 0.26093 | 122.6624 | 122.9736 | 122.8043 | 122.905 | 122.7036 | 122.9736 | 122.8317 | 122.493 | 122.905 | 122.7036 | 122.8317 | 122.8043 | 122.9736 | -0.4715 | -0.42114
2737.4062 | 123.0927 | -122.7676 | 0.18768 | -0.1899 | 0.011134 | -0.0024652 | 0.041524 | -0.017684 | -0.012117 | 0.01198 | 0.022888 | 0.11902 | -0.29755 | 0.11444 | 0.12817 | 0.13733 | -0.13733 | 0.3067 | 0.20599 | -0.25177 | 122.4701 | -0.068664 | 122.7905 | 122.8821 | -0.059509 | 122.5159 | 0.018311 | 0.32043 | 122.6303 | 123.0743 | 122.8958 | 122.8867 | 122.7905 | 122.9736 | 122.905 | 122.5159 | 122.8867 | 122.7905 | 122.905 | 122.8958 | 122.9736 | -0.48523 | -0.43945
2739.1562 | 123.1338 | -122.7905 | 0.16937 | -0.25856 | 0.012202 | -0.0043878 | 0.043019 | -0.01747 | -0.010835 | 0.013903 | -0.004578 | 0.14191 | -0.3067 | 0.041199 | 0.059509 | 0.073242 | -0.032043 | 0.24261 | 0.23346 | -0.29297 | 122.4838 | -0.027466 | 122.7859 | 122.8317 | -0.10986 | 122.4976 | 0.064086 | 0.30212 | 122.7585 | 123.0331 | 122.85 | 122.9324 | 122.7859 | 123.024 | 122.8638 | 122.4976 | 122.9324 | 122.7859 | 122.8638 | 122.85 | 123.024 | -0.47607 | -0.46234
2740.8438 | 123.0331 | -122.7951 | 0.16937 | 0.13054 | 0.014125 | -0.003106 | 0.048787 | -0.013198 | -0.010408 | 0.014757 | -0.073242 | 0.17395 | -0.32501 | 0.013733 | 0.009155 | 0.022888 | -0.050354 | 0.14191 | 0.25635 | -0.28839 | 122.4701 | 0.004577 | 122.7219 | 122.8088 | -0.16022 | 122.5067 | 0.086975 | 0.25177 | 122.7448 | 122.937 | 122.8043 | 122.9691 | 122.7219 | 123.0515 | 122.818 | 122.5067 | 122.9691 | 122.7219 | 122.818 | 122.8043 | 123.0515 | -0.49439 | -0.45776
2742.5312 | 122.9965 | -122.8088 | 0.18768 | 0.18394 | 0.013484 | -0.0018244 | 0.044728 | -0.015761 | -0.01169 | 0.014116 | 0.027466 | 0.12817 | -0.27008 | 0.091553 | 0.11902 | 0.15564 | -0.21515 | 0.25635 | 0.20599 | -0.24261 | 122.5388 | -0.059509 | 122.8363 | 122.9004 | -0.068664 | 122.5662 | 0.018311 | 0.29755 | 122.5937 | 123.0652 | 122.9279 | 122.937 | 122.8363 | 123.0148 | 122.9645 | 122.5662 | 122.937 | 122.8363 | 122.9645 | 122.9279 | 123.0148 | -0.45776 | -0.4303
2744.2188 | 123.0927 | -122.7768 | 0.16937 | -0.10597 | 0.011989 | -0.0078058 | 0.041738 | -0.018752 | -0.010408 | 0.012407 | 0.018311 | 0.13275 | -0.27924 | 0.09613 | 0.11902 | 0.16937 | -0.16479 | 0.31586 | 0.18768 | -0.25635 | 122.4976 | -0.036622 | 122.7951 | 122.8729 | -0.050354 | 122.5204 | 0.01831 | 0.29755 | 122.612 | 123.0927 | 122.8958 | 122.9095 | 122.7951 | 122.9645 | 122.9462 | 122.5204 | 122.9095 | 122.7951 | 122.9462 | 122.8958 | 122.9645 | -0.44861 | -0.42572
2745.9688 | 123.1522 | -122.7539 | 0.16022 | -0.18227 | 0.014979 | -0.001397 | 0.045369 | -0.017897 | -0.0095531 | 0.012835 | -0.082397 | 0.1831 | -0.32501 | -0.022888 | 0.009155 | 0.013733 | 0.064087 | 0.16937 | 0.25177 | -0.31128 | 122.4289 | 0.022888 | 122.6715 | 122.731 | -0.15106 | 122.4426 | 0.091553 | 0.24262 | 122.818 | 122.9233 | 122.7631 | 122.937 | 122.6715 | 123.0057 | 122.7676 | 122.4426 | 122.937 | 122.6715 | 122.7676 | 122.7631 | 123.0057 | -0.48523 | -0.4715
2747.7188 | 123.111 | -122.7722 | 0.15106 | -0.083084 | 0.013911 | -0.0016106 | 0.041951 | -0.016188 | -0.0076305 | 0.013048 | -0.018311 | 0.14648 | -0.27924 | 0.073242 | 0.10986 | 0.13733 | -0.1236 | 0.28839 | 0.21973 | -0.27008 | 122.493 | -0.004578 | 122.7539 | 122.8455 | -0.041199 | 122.5021 | 0.068665 | 0.26092 | 122.6486 | 123.0606 | 122.8821 | 122.9187 | 122.7539 | 122.9919 | 122.9095 | 122.5021 | 122.9187 | 122.7539 | 122.9095 | 122.8821 | 122.9919 | -0.4303 | -0.42114
2749.4062 | 123.1064 | -122.7676 | 0.16022 | -0.1136 | 0.01028 | 0.00095277 | 0.040029 | -0.017043 | -0.011049 | 0.012835 | -0.018311 | 0.15564 | -0.28839 | 0.091553 | 0.11444 | 0.14648 | -0.13733 | 0.29297 | 0.20599 | -0.24719 | 122.4792 | -0.004577 | 122.7493 | 122.8592 | -0.045776 | 122.5204 | 0.045777 | 0.27008 | 122.6303 | 123.0606 | 122.8821 | 122.9233 | 122.7493 | 122.9736 | 122.9141 | 122.5204 | 122.9233 | 122.7493 | 122.9141 | 122.8821 | 122.9736 | -0.44861 | -0.40741
2751.1719 | 123.0011 | -122.7997 | 0.20142 | -0.083084 | 0.012202 | -0.00075623 | 0.046437 | -0.014907 | -0.011476 | 0.012621 | -0.022888 | 0.15106 | -0.32959 | 0.050354 | 0.041199 | 0.068665 | -0.045776 | 0.1831 | 0.23804 | -0.28381 | 122.4701 | -0.050354 | 122.7768 | 122.85 | -0.16022 | 122.5159 | 0.036621 | 0.3067 | 122.7539 | 122.9828 | 122.8409 | 122.9507 | 122.7768 | 123.0377 | 122.8683 | 122.5159 | 122.9507 | 122.7768 | 122.8683 | 122.8409 | 123.0377 | -0.53101 | -0.48523
2752.8594 | 123.0377 | -122.8317 | 0.20142 | -0.022049 | 0.012843 | -0.0035332 | 0.048146 | -0.013625 | -0.01169 | 0.013903 | -0.041199 | 0.17395 | -0.31586 | 0.013733 | 0.009155 | 0.036621 | -0.018311 | 0.16022 | 0.23804 | -0.29297 | 122.5159 | -0.027466 | 122.7905 | 122.8455 | -0.19226 | 122.5388 | 0.036621 | 0.27466 | 122.8134 | 122.9919 | 122.8409 | 123.0057 | 122.7905 | 123.0698 | 122.8683 | 122.5388 | 123.0057 | 122.7905 | 122.8683 | 122.8409 | 123.0698 | -0.51727 | -0.49438
2754.6094 | 123.0972 | -122.7768 | 0.16479 | -0.12886 | 0.01327 | -0.0026788 | 0.037038 | -0.016402 | -0.011262 | 0.01198 | -0.004578 | 0.13275 | -0.30212 | 0.086975 | 0.12817 | 0.16022 | -0.15106 | 0.29755 | 0.19684 | -0.2655 | 122.4747 | -0.032044 | 122.7722 | 122.8638 | -0.036621 | 122.5113 | 0.032043 | 0.29755 | 122.6257 | 123.0743 | 122.905 | 122.9095 | 122.7722 | 122.9736 | 122.937 | 122.5113 | 122.9095 | 122.7722 | 122.937 | 122.905 | 122.9736 | -0.46692 | -0.4303
2756.3125 | 123.0148 | -122.8088 | 0.20142 | 0.18394 | 0.011989 | -0.0024652 | 0.047719 | -0.014266 | -0.010621 | 0.013689 | -0.050354 | 0.17395 | -0.32501 | 0.022888 | 0.032043 | 0.068665 | -0.11444 | 0.18768 | 0.23804 | -0.25177 | 122.4838 | -0.027466 | 122.7585 | 122.8317 | -0.16937 | 122.5571 | 0.036621 | 0.27466 | 122.6944 | 122.9965 | 122.8409 | 122.9828 | 122.7585 | 123.0469 | 122.8775 | 122.5571 | 122.9828 | 122.7585 | 122.8775 | 122.8409 | 123.0469 | -0.52643 | -0.45319
2758.0625 | 123.024 | -122.8134 | 0.19226 | 0.16106 | 0.012202 | 0.002021 | 0.04366 | -0.016188 | -0.01233 | 0.013903 | 0.032043 | 0.11444 | -0.28839 | 0.082397 | 0.10986 | 0.15564 | -0.1831 | 0.25635 | 0.20142 | -0.24719 | 122.525 | -0.07782 | 122.8455 | 122.8958 | -0.082398 | 122.5662 | 0.009155 | 0.32043 | 122.6303 | 123.0698 | 122.9233 | 122.9279 | 122.8455 | 123.0148 | 122.9691 | 122.5662 | 122.9279 | 122.8455 | 122.9691 | 122.9233 | 123.0148 | -0.48065 | -0.43945
2759.8125 | 123.024 | -122.7814 | 0.1831 | 0.1992 | 0.013057 | -0.00096983 | 0.043874 | -0.015761 | -0.01169 | 0.01433 | 0.027466 | 0.14191 | -0.27008 | 0.086975 | 0.10986 | 0.13733 | -0.1831 | 0.2655 | 0.19684 | -0.26093 | 122.5113 | -0.041198 | 122.8088 | 122.8683 | -0.073242 | 122.5204 | 0.013733 | 0.29755 | 122.5983 | 123.0469 | 122.8912 | 122.9233 | 122.8088 | 122.9782 | 122.9187 | 122.5204 | 122.9233 | 122.8088 | 122.9187 | 122.8912 | 122.9782 | -0.45319 | -0.44403
2761.5156 | 123.0652 | -122.8043 | 0.19684 | -0.14412 | 0.013698 | -0.0011834 | 0.044515 | -0.017043 | -0.011903 | 0.014544 | -0.054932 | 0.16937 | -0.33875 | 0.036621 | 0.036621 | 0.064087 | -0.009155 | 0.20142 | 0.22888 | -0.30212 | 122.4655 | -0.027465 | 122.7493 | 122.8409 | -0.16022 | 122.5021 | 0.032044 | 0.28381 | 122.7951 | 123.0057 | 122.8409 | 122.9736 | 122.7493 | 123.0331 | 122.8683 | 122.5021 | 122.9736 | 122.7493 | 122.8683 | 122.8409 | 123.0331 | -0.53558 | -0.49896
2763.2031 | 123.0469 | -122.7814 | 0.18768 | -0.0067901 | 0.015193 | -0.00054263 | 0.046865 | -0.013411 | -0.013826 | 0.011553 | -0.032043 | 0.1831 | -0.33417 | -0.004578 | 0 | 0.009155 | 0 | 0.13275 | 0.23346 | -0.27924 | 122.4472 | -0.004578 | 122.7493 | 122.7768 | -0.18768 | 122.5021 | 0.045776 | 0.30212 | 122.7814 | 122.9141 | 122.7814 | 122.9645 | 122.7493 | 123.0148 | 122.7905 | 122.5021 | 122.9645 | 122.7493 | 122.7905 | 122.7814 | 123.0148 | -0.52185 | -0.46692
2764.9531 | 123.0286 | -122.8088 | 0.19684 | -0.0067901 | 0.011561 | 0.00073917 | 0.047292 | -0.013839 | -0.012117 | 0.013262 | -0.022888 | 0.15564 | -0.31586 | 0.018311 | 0.018311 | 0.045776 | -0.022888 | 0.15106 | 0.23804 | -0.26093 | 122.493 | -0.041198 | 122.7859 | 122.8271 | -0.17853 | 122.5479 | 0.041199 | 0.29297 | 122.7859 | 122.9599 | 122.8271 | 122.9645 | 122.7859 | 123.0469 | 122.8546 | 122.5479 | 122.9645 | 122.7859 | 122.8546 | 122.8271 | 123.0469 | -0.5127 | -0.45776
2766.7031 | 123.0423 | -122.7905 | 0.1831 | 0.031357 | 0.013911 | -0.0011834 | 0.045583 | -0.013411 | -0.011262 | 0.011553 | -0.068665 | 0.17395 | -0.33875 | -0.013733 | -0.004578 | 0.018311 | 0.009155 | 0.11444 | 0.23346 | -0.29755 | 122.4518 | -0.009155 | 122.7219 | 122.7768 | -0.18768 | 122.493 | 0.050354 | 0.27008 | 122.7997 | 122.905 | 122.7859 | 122.9645 | 122.7219 | 123.024 | 122.8088 | 122.493 | 122.9645 | 122.7219 | 122.8088 | 122.7859 | 123.024 | -0.52185 | -0.48065
2768.3906 | 123.056 | -122.7859 | 0.17853 | 0.13817 | 0.015407 | -0.0046014 | 0.04366 | -0.013411 | -0.0091259 | 0.014116 | -0.091553 | 0.19226 | -0.32044 | -0.027466 | 0 | 0.032043 | -0.036621 | 0.11902 | 0.24261 | -0.27924 | 122.4655 | 0.013733 | 122.6944 | 122.7585 | -0.17853 | 122.5067 | 0.064087 | 0.22888 | 122.7493 | 122.905 | 122.7859 | 122.9782 | 122.6944 | 123.0286 | 122.818 | 122.5067 | 122.9782 | 122.6944 | 122.818 | 122.7859 | 123.0286 | -0.49896 | -0.45776
2770.1406 | 123.0469 | -122.7997 | 0.1831 | -0.14412 | 0.013698 | -0.004815 | 0.042806 | -0.013839 | -0.0095531 | 0.013689 | -0.054932 | 0.17395 | -0.32044 | 0.027466 | 0.054932 | 0.050354 | -0.009155 | 0.19684 | 0.24261 | -0.27008 | 122.4792 | -0.009155 | 122.7448 | 122.8271 | -0.12817 | 122.5296 | 0.05951 | 0.2655 | 122.7905 | 122.9965 | 122.8546 | 122.9736 | 122.7448 | 123.0423 | 122.85 | 122.5296 | 122.9736 | 122.7448 | 122.85 | 122.8546 | 123.0423 | -0.50354 | -0.45319
2771.9062 | 123.0057 | -122.8043 | 0.21515 | 0.18394 | 0.014552 | -0.003747 | 0.041951 | -0.011702 | -0.011049 | 0.014116 | 0 | 0.13733 | -0.29297 | 0.064087 | 0.091553 | 0.15564 | -0.16937 | 0.23804 | 0.19684 | -0.24719 | 122.5113 | -0.07782 | 122.8043 | 122.8683 | -0.1236 | 122.5571 | -0.018311 | 0.29297 | 122.6349 | 123.0423 | 122.8958 | 122.9416 | 122.8043 | 123.0011 | 122.9599 | 122.5571 | 122.9416 | 122.8043 | 122.9599 | 122.8958 | 123.0011 | -0.50812 | -0.46234
2773.6562 | 123.1155 | -122.7951 | 0.16022 | -0.18227 | 0.013057 | 0.00095277 | 0.043447 | -0.015334 | -0.0097669 | 0.012621 | -0.082397 | 0.17395 | -0.35248 | -0.022888 | 0.004578 | 0.036621 | 0.045776 | 0.17853 | 0.23804 | -0.29755 | 122.4426 | 0.013733 | 122.7127 | 122.7722 | -0.15564 | 122.4976 | 0.07782 | 0.27008 | 122.8409 | 122.9736 | 122.7997 | 122.9691 | 122.7127 | 123.0331 | 122.8317 | 122.4976 | 122.9691 | 122.7127 | 122.8317 | 122.7997 | 123.0331 | -0.5127 | -0.45776
2775.3438 | 123.0972 | -122.7768 | 0.1831 | -0.21278 | 0.010707 | -0.002038 | 0.038106 | -0.016616 | -0.01169 | 0.013903 | 0 | 0.13275 | -0.28381 | 0.10071 | 0.11902 | 0.15106 | -0.11444 | 0.32044 | 0.21057 | -0.25635 | 122.493 | -0.050354 | 122.7768 | 122.8775 | -0.064086 | 122.5204 | 0.027466 | 0.28381 | 122.6624 | 123.0972 | 122.8958 | 122.9095 | 122.7768 | 122.9874 | 122.9279 | 122.5204 | 122.9095 | 122.7768 | 122.9279 | 122.8958 | 122.9874 | -0.46692 | -0.43945
2777.0469 | 123.1522 | -122.7631 | 0.16479 | -0.23567 | 0.013911 | -0.0016106 | 0.041951 | -0.016616 | -0.011476 | 0.012621 | -0.10986 | 0.16479 | -0.33417 | -0.027466 | -0.004578 | 0.013733 | 0.073242 | 0.14648 | 0.25177 | -0.3067 | 122.4289 | 0 | 122.6532 | 122.7356 | -0.16937 | 122.4564 | 0.086975 | 0.2243 | 122.8363 | 122.9095 | 122.7585 | 122.9279 | 122.6532 | 123.0148 | 122.7768 | 122.4564 | 122.9279 | 122.6532 | 122.7768 | 122.7585 | 123.0148 | -0.49896 | -0.4715
2778.8125 | 123.1338 | -122.7539 | 0.16937 | -0.25856 | 0.012202 | -0.0026788 | 0.043874 | -0.01512 | -0.012544 | 0.013903 | -0.091553 | 0.19684 | -0.33417 | -0.032043 | -0.004578 | 0.013733 | 0.068665 | 0.16479 | 0.27008 | -0.28839 | 122.4197 | 0.027465 | 122.6624 | 122.7219 | -0.17395 | 122.4655 | 0.10071 | 0.24261 | 122.8226 | 122.9187 | 122.7493 | 122.9507 | 122.6624 | 123.024 | 122.7676 | 122.4655 | 122.9507 | 122.6624 | 122.7676 | 122.7493 | 123.024 | -0.50354 | -0.45776
2780.5781 | 123.1018 | -122.8043 | 0.17853 | -0.20515 | 0.01028 | -0.0024652 | 0.04131 | -0.014693 | -0.011262 | 0.012407 | 0.004578 | 0.13275 | -0.28839 | 0.082397 | 0.091553 | 0.11902 | -0.068665 | 0.29755 | 0.2243 | -0.2655 | 122.5159 | -0.045777 | 122.8088 | 122.8867 | -0.086975 | 122.5388 | 0.045776 | 0.29297 | 122.7356 | 123.1018 | 122.8958 | 122.937 | 122.8088 | 123.0286 | 122.9233 | 122.5388 | 122.937 | 122.8088 | 122.9233 | 122.8958 | 123.0286 | -0.46692 | -0.44403
2782.2812 | 123.0377 | -122.8226 | 0.18768 | 0.13817 | 0.012416 | -0.0080194 | 0.044942 | -0.015334 | -0.013612 | 0.014757 | -0.073242 | 0.16937 | -0.30212 | -0.009155 | 0.004578 | 0.054932 | -0.073242 | 0.16937 | 0.24261 | -0.27008 | 122.5204 | -0.01831 | 122.7493 | 122.8134 | -0.1831 | 122.5525 | 0.054932 | 0.22888 | 122.7493 | 122.9919 | 122.8271 | 122.9919 | 122.7493 | 123.0652 | 122.8775 | 122.5525 | 122.9919 | 122.7493 | 122.8775 | 122.8271 | 123.0652 | -0.48981 | -0.45776
2783.9688 | 122.9965 | -122.8088 | 0.19684 | 0.19157 | 0.012629 | -0.0056696 | 0.044088 | -0.015334 | -0.0078443 | 0.014116 | -0.004578 | 0.12817 | -0.29297 | 0.082397 | 0.10071 | 0.13733 | -0.16937 | 0.24261 | 0.20142 | -0.25177 | 122.5159 | -0.068664 | 122.8043 | 122.8912 | -0.09613 | 122.5571 | 0.004578 | 0.28839 | 122.6395 | 123.0515 | 122.9095 | 122.937 | 122.8043 | 123.0103 | 122.9462 | 122.5571 | 122.937 | 122.8043 | 122.9462 | 122.9095 | 123.0103 | -0.48981 | -0.44861
2785.7344 | 123.0606 | -122.7997 | 0.17853 | 0.16869 | 0.014979 | 9.8166e-05 | 0.045583 | -0.016616 | -0.012117 | 0.013475 | -0.07782 | 0.1831 | -0.32501 | -0.041199 | -0.009155 | 0 | -0.013733 | 0.10986 | 0.22888 | -0.29755 | 122.4747 | 0.004577 | 122.7219 | 122.7585 | -0.18768 | 122.5021 | 0.050354 | 0.24719 | 122.7859 | 122.9095 | 122.7905 | 122.9828 | 122.7219 | 123.0286 | 122.7997 | 122.5021 | 122.9828 | 122.7219 | 122.7997 | 122.7905 | 123.0286 | -0.50354 | -0.47607
2787.5 | 123.0515 | -122.8088 | 0.1831 | 0.16869 | 0.013698 | -0.0022516 | 0.038961 | -0.016402 | -0.0084851 | 0.011766 | -0.004578 | 0.13733 | -0.29297 | 0.041199 | 0.068665 | 0.10986 | -0.14191 | 0.24261 | 0.19684 | -0.27008 | 122.5159 | -0.045776 | 122.8043 | 122.85 | -0.11444 | 122.5388 | 0.013733 | 0.28839 | 122.6669 | 123.0515 | 122.8775 | 122.9462 | 122.8043 | 123.0057 | 122.9187 | 122.5388 | 122.9462 | 122.8043 | 122.9187 | 122.8775 | 123.0057 | -0.47607 | -0.45319
2789.1875 | 123.056 | -122.7951 | 0.19226 | 0.10765 | 0.014979 | 0.00095277 | 0.047933 | -0.017897 | -0.010194 | 0.013903 | -0.086975 | 0.18768 | -0.31586 | -0.022888 | -0.032043 | -0.004578 | 0.018311 | 0.13733 | 0.25177 | -0.27924 | 122.4792 | -0.004578 | 122.7081 | 122.7722 | -0.2243 | 122.5159 | 0.059509 | 0.22888 | 122.8134 | 122.9324 | 122.7631 | 122.9828 | 122.7081 | 123.0469 | 122.7905 | 122.5159 | 122.9828 | 122.7081 | 122.7905 | 122.7631 | 123.0469 | -0.50812 | -0.4715
2790.9375 | 123.1155 | -122.7768 | 0.16937 | -0.21278 | 0.013057 | -0.0011834 | 0.040883 | -0.018325 | -0.0093395 | 0.013048 | -0.013733 | 0.15564 | -0.28381 | 0.054932 | 0.082397 | 0.10071 | -0.027466 | 0.24719 | 0.21057 | -0.27466 | 122.493 | -0.013733 | 122.7631 | 122.8317 | -0.086976 | 122.5021 | 0.041198 | 0.27008 | 122.7493 | 123.024 | 122.8592 | 122.9324 | 122.7631 | 122.9874 | 122.8775 | 122.5021 | 122.9324 | 122.7631 | 122.8775 | 122.8592 | 122.9874 | -0.45319 | -0.44403
2792.625 | 123.0743 | -122.8088 | 0.17395 | 0.10002 | 0.013484 | 0.0024482 | 0.045797 | -0.015548 | -0.0097669 | 0.013262 | -0.10529 | 0.17853 | -0.34332 | -0.045776 | -0.032043 | -0.004578 | -0.004578 | 0.10986 | 0.25635 | -0.29297 | 122.4655 | 0.004578 | 122.7036 | 122.7631 | -0.20599 | 122.5159 | 0.082398 | 0.23804 | 122.8043 | 122.9187 | 122.7768 | 122.9874 | 122.7036 | 123.0652 | 122.8043 | 122.5159 | 122.9874 | 122.7036 | 122.8043 | 122.7768 | 123.0652 | -0.51727 | -0.46692
2794.3125 | 123.0057 | -122.8088 | 0.20142 | -0.067826 | 0.013057 | -0.0052422 | 0.044728 | -0.013411 | -0.011476 | 0.014116 | -0.027466 | 0.16479 | -0.31586 | 0.032043 | 0.036621 | 0.068665 | -0.018311 | 0.19226 | 0.24261 | -0.29297 | 122.493 | -0.036621 | 122.7814 | 122.8409 | -0.1648 | 122.5159 | 0.041199 | 0.28839 | 122.7905 | 123.0011 | 122.8455 | 122.9736 | 122.7814 | 123.0515 | 122.8775 | 122.5159 | 122.9736 | 122.7814 | 122.8775 | 122.8455 | 123.0515 | -0.51727 | -0.49438
2796.0156 | 123.0469 | -122.7997 | 0.19226 | 0.10002 | 0.01327 | 0.0011664 | 0.045797 | -0.01512 | -0.011262 | 0.013475 | -0.09613 | 0.17853 | -0.31586 | -0.036621 | 0 | 0.018311 | -0.013733 | 0.14191 | 0.25177 | -0.28839 | 122.4838 | -0.013733 | 122.7036 | 122.7631 | -0.19226 | 122.5113 | 0.059509 | 0.21973 | 122.7859 | 122.9416 | 122.7997 | 122.9782 | 122.7036 | 123.0515 | 122.818 | 122.5113 | 122.9782 | 122.7036 | 122.818 | 122.7997 | 123.0515 | -0.50812 | -0.48065
2797.7188 | 123.1155 | -122.7859 | 0.17853 | 0.069504 | 0.014979 | -0.003106 | 0.03832 | -0.01512 | -0.0072033 | 0.010698 | -0.027466 | 0.14648 | -0.28839 | 0.032043 | 0.050354 | 0.10529 | -0.10529 | 0.21973 | 0.21515 | -0.27008 | 122.4976 | -0.032044 | 122.7585 | 122.818 | -0.12817 | 122.5159 | 0.036621 | 0.26093 | 122.6807 | 123.0057 | 122.8363 | 122.9324 | 122.7585 | 123.0011 | 122.8912 | 122.5159 | 122.9324 | 122.7585 | 122.8912 | 122.8363 | 123.0011 | -0.46692 | -0.44861
2799.4844 | 123.1247 | -122.7585 | 0.17395 | -0.083084 | 0.013911 | -0.00032903 | 0.038961 | -0.017256 | -0.0080579 | 0.012621 | -0.018311 | 0.16022 | -0.30212 | 0.068665 | 0.10986 | 0.14191 | -0.1236 | 0.29297 | 0.18768 | -0.2655 | 122.4564 | -0.013733 | 122.7402 | 122.8271 | -0.064087 | 122.493 | 0.013733 | 0.28381 | 122.6349 | 123.0515 | 122.8683 | 122.9187 | 122.7402 | 122.9462 | 122.9004 | 122.493 | 122.9187 | 122.7402 | 122.9004 | 122.8683 | 122.9462 | -0.47607 | -0.43945
2801.1719 | 123.1476 | -122.7722 | 0.15564 | -0.19753 | 0.011134 | -0.0022516 | 0.047719 | -0.016188 | -0.0099805 | 0.011766 | -0.086975 | 0.16937 | -0.32501 | 0 | 0.009155 | 0.013733 | 0.041199 | 0.17395 | 0.25635 | -0.28381 | 122.4472 | 0.013733 | 122.6852 | 122.7722 | -0.14649 | 122.4884 | 0.10071 | 0.23804 | 122.8134 | 122.9462 | 122.7814 | 122.9416 | 122.6852 | 123.0286 | 122.7859 | 122.4884 | 122.9416 | 122.6852 | 122.7859 | 122.7814 | 123.0286 | -0.48065 | -0.43945
2802.9219 | 123.1247 | -122.7493 | 0.16937 | -0.18227 | 0.014125 | -0.0039606 | 0.045156 | -0.01512 | -0.010621 | 0.011766 | -0.07782 | 0.17853 | -0.33875 | 0.004578 | 0.009155 | 0.027466 | 0.036621 | 0.18768 | 0.24261 | -0.27466 | 122.4106 | 0.009155 | 122.6715 | 122.7539 | -0.16022 | 122.4747 | 0.073242 | 0.26093 | 122.7859 | 122.937 | 122.7585 | 122.9279 | 122.6715 | 122.9919 | 122.7768 | 122.4747 | 122.9279 | 122.6715 | 122.7768 | 122.7585 | 122.9919 | -0.50812 | -0.44403
2804.6719 | 123.1155 | -122.7768 | 0.17853 | -0.067826 | 0.012202 | -0.00032903 | 0.039601 | -0.016402 | -0.0091259 | 0.013689 | -0.022888 | 0.14648 | -0.29755 | 0.050354 | 0.10071 | 0.1236 | -0.11902 | 0.29755 | 0.2243 | -0.26093 | 122.4792 | -0.032044 | 122.7539 | 122.8271 | -0.07782 | 122.5159 | 0.045776 | 0.27466 | 122.6578 | 123.0743 | 122.8775 | 122.9233 | 122.7539 | 123.0011 | 122.9004 | 122.5159 | 122.9233 | 122.7539 | 122.9004 | 122.8775 | 123.0011 | -0.47607 | -0.43945
2806.375 | 123.0469 | -122.7997 | 0.18768 | 0.11528 | 0.011561 | -0.00032903 | 0.047292 | -0.013198 | -0.01233 | 0.014971 | -0.082397 | 0.17395 | -0.33875 | -0.013733 | 0.004578 | 0.036621 | -0.054932 | 0.14191 | 0.24719 | -0.27008 | 122.4609 | -0.013733 | 122.7173 | 122.7859 | -0.1831 | 122.5296 | 0.059509 | 0.25635 | 122.7448 | 122.9416 | 122.8043 | 122.9736 | 122.7173 | 123.0469 | 122.8363 | 122.5296 | 122.9736 | 122.7173 | 122.8363 | 122.8043 | 123.0469 | -0.52643 | -0.45776
2808.125 | 123.0194 | -122.8363 | 0.20599 | 0.12291 | 0.013698 | -0.00096983 | 0.043874 | -0.014052 | -0.0089123 | 0.013048 | -0.004578 | 0.14191 | -0.31128 | 0.068665 | 0.073242 | 0.11902 | -0.15564 | 0.23804 | 0.19226 | -0.25177 | 122.525 | -0.064087 | 122.8317 | 122.905 | -0.13275 | 122.5845 | -0.013733 | 0.3067 | 122.6807 | 123.0743 | 122.9095 | 122.9782 | 122.8317 | 123.0286 | 122.9553 | 122.5845 | 122.9782 | 122.8317 | 122.9553 | 122.9095 | 123.0286 | -0.51727 | -0.45776
2809.875 | 123.1338 | -122.7402 | 0.15106 | -0.01442 | 0.013698 | -0.0026788 | 0.038106 | -0.017256 | -0.010835 | 0.012835 | -0.059509 | 0.16022 | -0.27924 | 0.022888 | 0.064087 | 0.09613 | -0.091553 | 0.2243 | 0.21057 | -0.27924 | 122.4609 | 0.009155 | 122.6807 | 122.7631 | -0.086975 | 122.4609 | 0.059509 | 0.21973 | 122.6486 | 122.9645 | 122.8043 | 122.9004 | 122.6807 | 122.9507 | 122.8363 | 122.4609 | 122.9004 | 122.6807 | 122.8363 | 122.8043 | 122.9507 | -0.4303 | -0.4303
2811.625 | 123.0194 | -122.8043 | 0.19226 | 0.21446 | 0.011775 | -0.00096983 | 0.045583 | -0.015761 | -0.01169 | 0.013903 | 0.027466 | 0.11902 | -0.29297 | 0.082397 | 0.11444 | 0.14191 | -0.20142 | 0.25635 | 0.19226 | -0.25635 | 122.5113 | -0.073242 | 122.8317 | 122.8867 | -0.07782 | 122.5479 | 0 | 0.32043 | 122.6028 | 123.0606 | 122.9187 | 122.9233 | 122.8317 | 122.9965 | 122.9462 | 122.5479 | 122.9233 | 122.8317 | 122.9462 | 122.9187 | 122.9965 | -0.48523 | -0.44861
2813.3125 | 123.0972 | -122.7905 | 0.16937 | -0.17464 | 0.013911 | -0.0054558 | 0.042165 | -0.017897 | -0.011262 | 0.010912 | 0.013733 | 0.13733 | -0.27924 | 0.082397 | 0.10986 | 0.11902 | -0.091553 | 0.29755 | 0.21515 | -0.27466 | 122.5113 | -0.032044 | 122.8043 | 122.8729 | -0.05951 | 122.5159 | 0.045776 | 0.29297 | 122.699 | 123.0881 | 122.9004 | 122.9279 | 122.8043 | 123.0057 | 122.9095 | 122.5159 | 122.9279 | 122.8043 | 122.9095 | 122.9004 | 123.0057 | -0.44861 | -0.44403
2815.0625 | 123.024 | -122.8317 | 0.19684 | -0.037308 | 0.01327 | 0.0011664 | 0.04836 | -0.015334 | -0.01169 | 0.01198 | -0.041199 | 0.16479 | -0.33417 | 0.004578 | 0.018311 | 0.036621 | -0.004578 | 0.17853 | 0.25177 | -0.28839 | 122.4976 | -0.032043 | 122.7905 | 122.8363 | -0.17853 | 122.5433 | 0.054932 | 0.29297 | 122.8271 | 123.0103 | 122.85 | 122.9965 | 122.7905 | 123.0835 | 122.8683 | 122.5433 | 122.9965 | 122.7905 | 122.8683 | 122.85 | 123.0835 | -0.531 | -0.48523
2816.8125 | 123.0103 | -122.8271 | 0.20142 | -0.083084 | 0.01562 | -0.00054263 | 0.046865 | -0.015975 | -0.010835 | 0.010271 | 0 | 0.16937 | -0.32501 | 0.041199 | 0.027466 | 0.054932 | -0.022888 | 0.19226 | 0.23346 | -0.28381 | 122.5021 | -0.032043 | 122.8271 | 122.8683 | -0.17395 | 122.5433 | 0.032043 | 0.32501 | 122.8043 | 123.0194 | 122.8546 | 122.9965 | 122.8271 | 123.0606 | 122.8821 | 122.5433 | 122.9965 | 122.8271 | 122.8821 | 122.8546 | 123.0606 | -0.52643 | -0.48523
2818.5781 | 123.0469 | -122.8226 | 0.21973 | -0.1136 | 0.014125 | -0.0024652 | 0.04601 | -0.014693 | -0.012117 | 0.013903 | -0.022888 | 0.16479 | -0.32959 | 0.036621 | 0.050354 | 0.07782 | -0.027466 | 0.20599 | 0.23804 | -0.29297 | 122.493 | -0.054932 | 122.7997 | 122.8592 | -0.16937 | 122.5296 | 0.01831 | 0.3067 | 122.7951 | 123.0286 | 122.8729 | 122.9874 | 122.7997 | 123.0606 | 122.9004 | 122.5296 | 122.9874 | 122.7997 | 122.9004 | 122.8729 | 123.0606 | -0.54932 | -0.5127
2820.3281 | 123.1247 | -122.7585 | 0.15106 | 0.061874 | 0.013057 | 0.0011664 | 0.036824 | -0.016616 | -0.01169 | 0.014116 | -0.064087 | 0.12817 | -0.29297 | 0.027466 | 0.054932 | 0.10071 | -0.10529 | 0.21973 | 0.21515 | -0.26093 | 122.4655 | -0.022888 | 122.6944 | 122.7859 | -0.09613 | 122.4976 | 0.064087 | 0.22888 | 122.6532 | 122.9782 | 122.8134 | 122.8867 | 122.6944 | 122.9736 | 122.8592 | 122.4976 | 122.8867 | 122.6944 | 122.8592 | 122.8134 | 122.9736 | -0.44403 | -0.41199
2822.0156 | 123.056 | -122.8043 | 0.19684 | -0.12123 | 0.012629 | -0.003106 | 0.045369 | -0.015334 | -0.011476 | 0.013475 | -0.050354 | 0.16022 | -0.33875 | 0.027466 | 0.036621 | 0.059509 | -0.022888 | 0.1831 | 0.24261 | -0.27008 | 122.4655 | -0.036621 | 122.7539 | 122.8317 | -0.16022 | 122.5342 | 0.045777 | 0.28839 | 122.7814 | 122.9874 | 122.8409 | 122.9645 | 122.7539 | 123.0469 | 122.8638 | 122.5342 | 122.9645 | 122.7539 | 122.8638 | 122.8409 | 123.0469 | -0.53558 | -0.46692
2823.7812 | 123.0194 | -122.8317 | 0.20142 | -0.098343 | 0.013057 | -0.006524 | 0.045369 | -0.013198 | -0.011903 | 0.011766 | -0.032043 | 0.16022 | -0.33875 | 0.032043 | 0.050354 | 0.064087 | -0.045776 | 0.20142 | 0.23346 | -0.2655 | 122.493 | -0.041199 | 122.7997 | 122.8638 | -0.15106 | 122.5662 | 0.032043 | 0.3067 | 122.7859 | 123.0331 | 122.8821 | 122.9919 | 122.7997 | 123.0652 | 122.8958 | 122.5662 | 122.9919 | 122.7997 | 122.8958 | 122.8821 | 123.0652 | -0.54016 | -0.46692
2825.4688 | 123.0469 | -122.7905 | 0.21057 | 0.0084684 | 0.011134 | -0.0033196 | 0.04601 | -0.014693 | -0.012758 | 0.014544 | -0.050354 | 0.16022 | -0.33875 | -0.022888 | -0.004578 | 0.009155 | 0 | 0.12817 | 0.2655 | -0.25635 | 122.4518 | -0.050354 | 122.7402 | 122.7676 | -0.21515 | 122.5342 | 0.054932 | 0.28839 | 122.7905 | 122.9187 | 122.7859 | 122.9507 | 122.7402 | 123.056 | 122.7997 | 122.5342 | 122.9507 | 122.7402 | 122.7997 | 122.7859 | 123.056 | -0.54932 | -0.46692
2827.2188 | 123.0286 | -122.818 | 0.19226 | -0.01442 | 0.014338 | -0.0018244 | 0.045797 | -0.014693 | -0.0086987 | 0.014757 | -0.027466 | 0.16937 | -0.33875 | 0.004578 | 0.022888 | 0.022888 | -0.013733 | 0.16479 | 0.23804 | -0.28381 | 122.4792 | -0.022888 | 122.7905 | 122.8226 | -0.16937 | 122.5342 | 0.045776 | 0.31128 | 122.8043 | 122.9828 | 122.8409 | 122.9874 | 122.7905 | 123.056 | 122.8409 | 122.5342 | 122.9874 | 122.7905 | 122.8409 | 122.8409 | 123.056 | -0.53101 | -0.47607
2828.9844 | 123.0469 | -122.8271 | 0.17853 | 0.17632 | 0.014552 | -0.003106 | 0.042379 | -0.012984 | -0.010621 | 0.013689 | -0.073242 | 0.1831 | -0.31128 | 0.004578 | 0.041199 | 0.064087 | -0.086975 | 0.1831 | 0.2243 | -0.25635 | 122.5159 | 0.004577 | 122.7539 | 122.8317 | -0.13733 | 122.5708 | 0.045776 | 0.23804 | 122.7402 | 123.0103 | 122.8683 | 123.0103 | 122.7539 | 123.0515 | 122.8912 | 122.5708 | 123.0103 | 122.7539 | 122.8912 | 122.8683 | 123.0515 | -0.48981 | -0.43488
2830.6875 | 123.0057 | -122.8226 | 0.19226 | 0.20683 | 0.011134 | -0.0018244 | 0.042806 | -0.014907 | -0.010835 | 0.012621 | -0.009155 | 0.13275 | -0.29755 | 0.068665 | 0.10071 | 0.13733 | -0.15106 | 0.23346 | 0.19226 | -0.2655 | 122.525 | -0.05951 | 122.8134 | 122.8912 | -0.091553 | 122.5571 | 0 | 0.28839 | 122.6715 | 123.056 | 122.9233 | 122.9553 | 122.8134 | 123.0148 | 122.9599 | 122.5571 | 122.9553 | 122.8134 | 122.9599 | 122.9233 | 123.0148 | -0.48981 | -0.45776
2832.4531 | 123.1476 | -122.7814 | 0.14648 | 0.061874 | 0.014979 | -0.0060968 | 0.038106 | -0.016402 | -0.0091259 | 0.013903 | -0.050354 | 0.14191 | -0.30212 | 0.009155 | 0.073242 | 0.10071 | -0.10071 | 0.21973 | 0.2243 | -0.27008 | 122.4792 | -0.004577 | 122.731 | 122.7905 | -0.073242 | 122.5113 | 0.07782 | 0.25177 | 122.6807 | 123.0011 | 122.8546 | 122.9233 | 122.731 | 123.0057 | 122.8821 | 122.5113 | 122.9233 | 122.731 | 122.8821 | 122.8546 | 123.0057 | -0.44861 | -0.41657
2834.1562 | 123.1613 | -122.7814 | 0.16479 | -0.2433 | 0.013698 | 0.00138 | 0.042806 | -0.01512 | -0.012544 | 0.013475 | -0.10986 | 0.18768 | -0.33417 | -0.036621 | 0 | 0 | 0.064087 | 0.16937 | 0.25635 | -0.30212 | 122.4472 | 0.022888 | 122.6715 | 122.7448 | -0.16479 | 122.4792 | 0.091553 | 0.2243 | 122.8455 | 122.9507 | 122.7814 | 122.9691 | 122.6715 | 123.0377 | 122.7814 | 122.4792 | 122.9691 | 122.6715 | 122.7814 | 122.7814 | 123.0377 | -0.49896 | -0.46692
2835.9219 | 123.1338 | -122.7631 | 0.17395 | 0.038986 | 0.014552 | -0.0024652 | 0.038747 | -0.015548 | -0.010621 | 0.011553 | -0.036621 | 0.14648 | -0.3067 | 0.032043 | 0.059509 | 0.10071 | -0.09613 | 0.21973 | 0.21973 | -0.27008 | 122.4564 | -0.027466 | 122.7264 | 122.7951 | -0.11444 | 122.493 | 0.045777 | 0.27008 | 122.6669 | 122.9828 | 122.8226 | 122.9095 | 122.7264 | 122.9828 | 122.8638 | 122.493 | 122.9095 | 122.7264 | 122.8638 | 122.8226 | 122.9828 | -0.48065 | -0.44403
2837.6875 | 123.056 | -122.7814 | 0.1831 | 0.18394 | 0.012202 | -0.00054263 | 0.04366 | -0.014907 | -0.0074169 | 0.011766 | -0.004578 | 0.14648 | -0.28381 | 0.045776 | 0.064087 | 0.12817 | -0.13733 | 0.23804 | 0.19226 | -0.25635 | 122.4976 | -0.036621 | 122.7768 | 122.8271 | -0.11902 | 122.525 | 0.009156 | 0.27923 | 122.644 | 123.0194 | 122.8455 | 122.9279 | 122.7768 | 122.9736 | 122.9095 | 122.525 | 122.9279 | 122.7768 | 122.9095 | 122.8455 | 122.9736 | -0.46692 | -0.43945
2839.3906 | 123.1476 | -122.7631 | 0.16937 | -0.01442 | 0.01327 | -0.0022516 | 0.039388 | -0.017256 | -0.0091259 | 0.013689 | -0.059509 | 0.16937 | -0.29755 | 0.022888 | 0.068665 | 0.10986 | -0.09613 | 0.23804 | 0.23346 | -0.27008 | 122.4655 | 0 | 122.7036 | 122.7859 | -0.10071 | 122.493 | 0.064086 | 0.23804 | 122.6669 | 123.0011 | 122.8317 | 122.9324 | 122.7036 | 122.9965 | 122.8729 | 122.493 | 122.9324 | 122.7036 | 122.8729 | 122.8317 | 122.9965 | -0.46692 | -0.43945
2841.1406 | 123.0606 | -122.7951 | 0.19226 | 0.12291 | 0.013698 | 0.0035162 | 0.047506 | -0.014479 | -0.01169 | 0.012835 | -0.091553 | 0.16022 | -0.33875 | -0.027466 | -0.032043 | -0.004578 | -0.004578 | 0.12817 | 0.24261 | -0.28381 | 122.4564 | -0.032044 | 122.7036 | 122.7676 | -0.2243 | 122.5113 | 0.050354 | 0.24719 | 122.7905 | 122.9233 | 122.7631 | 122.9553 | 122.7036 | 123.0377 | 122.7905 | 122.5113 | 122.9553 | 122.7036 | 122.7905 | 122.7631 | 123.0377 | -0.53101 | -0.47607
2842.9062 | 123.1155 | -122.7859 | 0.18768 | -0.22041 | 0.012416 | -0.0052422 | 0.040456 | -0.014907 | -0.01233 | 0.012407 | -0.004578 | 0.1236 | -0.3067 | 0.09613 | 0.11444 | 0.12817 | -0.10529 | 0.30212 | 0.21057 | -0.2655 | 122.4792 | -0.064087 | 122.7814 | 122.8821 | -0.073242 | 122.5204 | 0.022888 | 0.30212 | 122.6807 | 123.0881 | 122.9004 | 122.9095 | 122.7814 | 122.9965 | 122.9141 | 122.5204 | 122.9095 | 122.7814 | 122.9141 | 122.9004 | 122.9965 | -0.49438 | -0.45319
2844.6719 | 123.0469 | -122.8043 | 0.17395 | 0.1458 | 0.01562 | -0.004815 | 0.042165 | -0.015334 | -0.010194 | 0.011553 | 0.009155 | 0.13275 | -0.28381 | 0.059509 | 0.073242 | 0.12817 | -0.15564 | 0.25177 | 0.21515 | -0.22888 | 122.5204 | -0.041199 | 122.8134 | 122.8638 | -0.10071 | 122.5754 | 0.041199 | 0.29297 | 122.6486 | 123.056 | 122.8775 | 122.937 | 122.8134 | 123.0194 | 122.9324 | 122.5754 | 122.937 | 122.8134 | 122.9324 | 122.8775 | 123.0194 | -0.45776 | -0.40283
2846.375 | 123.0377 | -122.7997 | 0.20599 | 0.054245 | 0.014125 | -0.0033196 | 0.047719 | -0.013411 | -0.012117 | 0.012835 | -0.068665 | 0.16022 | -0.32959 | -0.018311 | -0.022888 | 0.018311 | 0 | 0.11902 | 0.24261 | -0.27466 | 122.4701 | -0.045777 | 122.731 | 122.7814 | -0.22888 | 122.525 | 0.036621 | 0.26092 | 122.7997 | 122.9187 | 122.7768 | 122.9599 | 122.731 | 123.0423 | 122.818 | 122.525 | 122.9599 | 122.731 | 122.818 | 122.7768 | 123.0423 | -0.53558 | -0.48065
2848.125 | 123.1567 | -122.7859 | 0.16937 | -0.25856 | 0.011989 | -0.001397 | 0.042165 | -0.017043 | -0.011049 | 0.012194 | -0.10529 | 0.1831 | -0.35248 | -0.018311 | 0.013733 | 0.004578 | 0.064087 | 0.16479 | 0.23804 | -0.29755 | 122.4335 | 0.013732 | 122.6807 | 122.7676 | -0.15564 | 122.4884 | 0.068664 | 0.24719 | 122.85 | 122.9507 | 122.7997 | 122.9691 | 122.6807 | 123.024 | 122.7905 | 122.4884 | 122.9691 | 122.6807 | 122.7905 | 122.7997 | 123.024 | -0.52185 | -0.46692
2849.8281 | 123.0515 | -122.8088 | 0.19226 | 0.016098 | 0.01327 | -0.0041742 | 0.047719 | -0.016829 | -0.012758 | 0.012407 | -0.050354 | 0.15564 | -0.33875 | -0.004578 | -0.004578 | 0.032043 | -0.027466 | 0.13733 | 0.25177 | -0.28839 | 122.4701 | -0.036621 | 122.7585 | 122.8043 | -0.19684 | 122.5204 | 0.059509 | 0.28839 | 122.7814 | 122.9462 | 122.8043 | 122.9645 | 122.7585 | 123.0606 | 122.8409 | 122.5204 | 122.9645 | 122.7585 | 122.8409 | 122.8043 | 123.0606 | -0.53101 | -0.48065
2851.5938 | 123.024 | -122.8363 | 0.21057 | -0.075455 | 0.013698 | -0.0011834 | 0.043233 | -0.016616 | -0.013826 | 0.014757 | -0.032043 | 0.17395 | -0.33875 | 0.032043 | 0.050354 | 0.059509 | -0.027466 | 0.19684 | 0.24261 | -0.27008 | 122.4976 | -0.036621 | 122.8043 | 122.8683 | -0.16022 | 122.5662 | 0.032044 | 0.3067 | 122.8088 | 123.0331 | 122.8867 | 123.0103 | 122.8043 | 123.0789 | 122.8958 | 122.5662 | 123.0103 | 122.8043 | 122.8958 | 122.8867 | 123.0789 | -0.54932 | -0.48065
2853.2969 | 123.1247 | -122.7631 | 0.16479 | -0.044937 | 0.011134 | 9.8166e-05 | 0.033834 | -0.016188 | -0.0084851 | 0.013475 | -0.041199 | 0.15106 | -0.31128 | 0.045776 | 0.10071 | 0.13275 | -0.11444 | 0.28839 | 0.21057 | -0.26093 | 122.4518 | -0.013733 | 122.7219 | 122.8088 | -0.064087 | 122.5021 | 0.045776 | 0.27008 | 122.6486 | 123.0515 | 122.8638 | 122.9141 | 122.7219 | 122.9736 | 122.8958 | 122.5021 | 122.9141 | 122.7219 | 122.8958 | 122.8638 | 122.9736 | -0.47607 | -0.42572
2855.0469 | 123.0331 | -122.8226 | 0.19226 | -0.060196 | 0.012629 | -0.0026788 | 0.047506 | -0.01512 | -0.010408 | 0.013262 | -0.013733 | 0.16937 | -0.32959 | 0.032043 | 0.036621 | 0.045776 | -0.022888 | 0.19226 | 0.23804 | -0.27924 | 122.493 | -0.022888 | 122.8088 | 122.8546 | -0.15564 | 122.5433 | 0.045776 | 0.31586 | 122.7997 | 123.0148 | 122.8592 | 122.9919 | 122.8088 | 123.0606 | 122.8683 | 122.5433 | 122.9919 | 122.8088 | 122.8683 | 122.8592 | 123.0606 | -0.52185 | -0.4715
2856.8125 | 123.1567 | -122.7768 | 0.15106 | -0.25093 | 0.011775 | -0.0011834 | 0.03832 | -0.016616 | -0.011262 | 0.013689 | -0.07782 | 0.16479 | -0.31586 | -0.013733 | 0.032043 | 0.032043 | 0.022888 | 0.17853 | 0.23346 | -0.29297 | 122.4609 | 0.013733 | 122.699 | 122.7631 | -0.11902 | 122.4838 | 0.082397 | 0.23804 | 122.7997 | 122.9553 | 122.8088 | 122.9416 | 122.699 | 123.0103 | 122.8088 | 122.4838 | 122.9416 | 122.699 | 122.8088 | 122.8088 | 123.0103 | -0.46692 | -0.44403
2858.5781 | 123.1613 | -122.7814 | 0.17395 | -0.30434 | 0.012416 | 0.0018072 | 0.039601 | -0.018111 | -0.011262 | 0.012835 | -0.045776 | 0.15106 | -0.31586 | 0 | 0.045776 | 0.050354 | 0.004578 | 0.19684 | 0.22888 | -0.28381 | 122.4655 | -0.022888 | 122.7356 | 122.7814 | -0.12817 | 122.4976 | 0.054932 | 0.27008 | 122.7859 | 122.9782 | 122.8271 | 122.9324 | 122.7356 | 123.0103 | 122.8317 | 122.4976 | 122.9324 | 122.7356 | 122.8317 | 122.8271 | 123.0103 | -0.48981 | -0.45776
2860.3281 | 123.111 | -122.7814 | 0.16022 | -0.12886 | 0.0092115 | -0.002038 | 0.038106 | -0.016616 | -0.011262 | 0.013903 | -0.013733 | 0.1236 | -0.30212 | 0.082397 | 0.1236 | 0.16937 | -0.15106 | 0.32044 | 0.21515 | -0.24719 | 122.4792 | -0.036621 | 122.7676 | 122.8638 | -0.036621 | 122.5342 | 0.054932 | 0.28839 | 122.6303 | 123.1018 | 122.905 | 122.905 | 122.7676 | 122.9965 | 122.9507 | 122.5342 | 122.905 | 122.7676 | 122.9507 | 122.905 | 122.9965 | -0.46234 | -0.40741
2862.0312 | 123.0606 | -122.7905 | 0.21057 | -0.060196 | 0.012629 | -0.0024652 | 0.045156 | -0.016616 | -0.013399 | 0.011339 | -0.041199 | 0.16022 | -0.3479 | 0.036621 | 0.032043 | 0.054932 | -0.009155 | 0.20599 | 0.27008 | -0.29297 | 122.4426 | -0.050354 | 122.7493 | 122.8271 | -0.17853 | 122.4976 | 0.05951 | 0.3067 | 122.7814 | 122.9965 | 122.8226 | 122.9507 | 122.7493 | 123.0606 | 122.8455 | 122.4976 | 122.9507 | 122.7493 | 122.8455 | 122.8226 | 123.0606 | -0.55847 | -0.50354
2863.7969 | 123.0606 | -122.7951 | 0.19684 | 0.15343 | 0.014125 | -0.00096983 | 0.04601 | -0.014479 | -0.010194 | 0.011126 | -0.082397 | 0.17395 | -0.33875 | -0.032043 | -0.009155 | 0.004578 | -0.009155 | 0.11902 | 0.24719 | -0.28381 | 122.4564 | -0.022888 | 122.7127 | 122.7631 | -0.20599 | 122.5113 | 0.050354 | 0.25635 | 122.7859 | 122.9141 | 122.7859 | 122.9691 | 122.7127 | 123.0423 | 122.7997 | 122.5113 | 122.9691 | 122.7127 | 122.7997 | 122.7859 | 123.0423 | -0.53558 | -0.48065
2865.5625 | 123.1476 | -122.7814 | 0.15564 | -0.28145 | 0.01327 | -0.0043878 | 0.042806 | -0.018111 | -0.01233 | 0.012407 | -0.032043 | 0.16022 | -0.30212 | 0.036621 | 0.036621 | 0.068665 | -0.004578 | 0.21973 | 0.23804 | -0.27924 | 122.4792 | 0.004577 | 122.7493 | 122.818 | -0.11902 | 122.5021 | 0.082397 | 0.27008 | 122.7768 | 123.0011 | 122.818 | 122.9416 | 122.7493 | 123.0194 | 122.85 | 122.5021 | 122.9416 | 122.7493 | 122.85 | 122.818 | 123.0194 | -0.45776 | -0.43488
2867.25 | 123.0423 | -122.8226 | 0.19226 | -0.098343 | 0.012416 | -0.0022516 | 0.04601 | -0.015334 | -0.013399 | 0.011766 | -0.027466 | 0.17853 | -0.32501 | 0.022888 | 0.027466 | 0.045776 | -0.022888 | 0.19684 | 0.25177 | -0.27008 | 122.4976 | -0.013733 | 122.7951 | 122.8455 | -0.16479 | 122.5525 | 0.059509 | 0.29755 | 122.7997 | 123.0194 | 122.85 | 123.0011 | 122.7951 | 123.0743 | 122.8683 | 122.5525 | 123.0011 | 122.7951 | 122.8683 | 122.85 | 123.0743 | -0.51727 | -0.46234
2869.0156 | 123.056 | -122.7997 | 0.17853 | 0.061874 | 0.012202 | -0.0018244 | 0.045369 | -0.014693 | -0.014039 | 0.012835 | -0.10071 | 0.15564 | -0.3479 | -0.036621 | -0.022888 | 0 | -0.018311 | 0.1236 | 0.25177 | -0.29297 | 122.4518 | -0.022888 | 122.699 | 122.7631 | -0.20142 | 122.5067 | 0.073242 | 0.24719 | 122.7814 | 122.9233 | 122.7768 | 122.9553 | 122.699 | 123.0515 | 122.7997 | 122.5067 | 122.9553 | 122.699 | 122.7997 | 122.7768 | 123.0515 | -0.52643 | -0.4715
2870.7812 | 123.024 | -122.7997 | 0.18768 | -0.052567 | 0.012629 | -0.0054558 | 0.047506 | -0.012984 | -0.012117 | 0.013689 | -0.013733 | 0.17395 | -0.32959 | 0.032043 | 0.036621 | 0.064087 | -0.027466 | 0.20142 | 0.23346 | -0.28839 | 122.4701 | -0.013733 | 122.7859 | 122.8317 | -0.15106 | 122.5113 | 0.045776 | 0.31586 | 122.7722 | 123.0011 | 122.8363 | 122.9736 | 122.7859 | 123.0331 | 122.8638 | 122.5113 | 122.9736 | 122.7859 | 122.8638 | 122.8363 | 123.0331 | -0.51727 | -0.47607
2872.5312 | 123.1522 | -122.7905 | 0.16479 | -0.25856 | 0.012202 | -0.003106 | 0.041951 | -0.018325 | -0.0089123 | 0.012194 | -0.10529 | 0.18768 | -0.34332 | -0.032043 | -0.004578 | 0.013733 | 0.073242 | 0.17853 | 0.25177 | -0.31586 | 122.4472 | 0.022888 | 122.6852 | 122.7585 | -0.16937 | 122.4747 | 0.086975 | 0.23804 | 122.8638 | 122.9691 | 122.7859 | 122.9782 | 122.6852 | 123.0423 | 122.8043 | 122.4747 | 122.9782 | 122.6852 | 122.8043 | 122.7859 | 123.0423 | -0.50812 | -0.48065
2874.25 | 123.0377 | -122.7997 | 0.18768 | -0.14412 | 0.011348 | -0.0026788 | 0.045369 | -0.017256 | -0.01169 | 0.01433 | -0.045776 | 0.16937 | -0.34332 | 0.027466 | 0.032043 | 0.045776 | -0.018311 | 0.21057 | 0.25177 | -0.28839 | 122.4564 | -0.01831 | 122.7539 | 122.8271 | -0.15564 | 122.5113 | 0.064087 | 0.29755 | 122.7814 | 123.0103 | 122.8317 | 122.9691 | 122.7539 | 123.0515 | 122.8455 | 122.5113 | 122.9691 | 122.7539 | 122.8455 | 122.8317 | 123.0515 | -0.53101 | -0.47607
2876.0156 | 123.0698 | -122.7997 | 0.16937 | 0.13817 | 0.010493 | -0.0026788 | 0.037679 | -0.015761 | -0.0093395 | 0.013048 | -0.022888 | 0.11902 | -0.3067 | 0.027466 | 0.068665 | 0.10986 | -0.12817 | 0.22888 | 0.20142 | -0.26093 | 122.493 | -0.050354 | 122.7768 | 122.8271 | -0.10071 | 122.5388 | 0.032043 | 0.28381 | 122.6715 | 123.0286 | 122.8683 | 122.9187 | 122.7768 | 123.0011 | 122.9095 | 122.5388 | 122.9187 | 122.7768 | 122.9095 | 122.8683 | 123.0011 | -0.47607 | -0.4303
2877.7656 | 123.0927 | -122.7859 | 0.15106 | -0.1136 | 0.014552 | -0.0016106 | 0.039174 | -0.018325 | -0.0076305 | 0.013475 | -0.018311 | 0.16022 | -0.3067 | 0.07782 | 0.10986 | 0.13733 | -0.13733 | 0.30212 | 0.21057 | -0.25635 | 122.4792 | 0.009155 | 122.7676 | 122.8638 | -0.041199 | 122.5296 | 0.059509 | 0.28839 | 122.6486 | 123.0881 | 122.8958 | 122.9462 | 122.7676 | 122.9965 | 122.9233 | 122.5296 | 122.9462 | 122.7676 | 122.9233 | 122.8958 | 122.9965 | -0.45776 | -0.40741
2879.5156 | 123.0057 | -122.8088 | 0.19226 | 0.15343 | 0.012843 | 0.00073917 | 0.047078 | -0.014693 | -0.012758 | 0.013475 | 0.009155 | 0.13275 | -0.31128 | 0.082397 | 0.09613 | 0.14648 | -0.17853 | 0.24719 | 0.21057 | -0.24719 | 122.4976 | -0.05951 | 122.818 | 122.8912 | -0.096131 | 122.5616 | 0.01831 | 0.32043 | 122.6303 | 123.056 | 122.905 | 122.9416 | 122.818 | 123.0194 | 122.9553 | 122.5616 | 122.9416 | 122.818 | 122.9553 | 122.905 | 123.0194 | -0.50354 | -0.43945
2881.2188 | 123.0927 | -122.7905 | 0.16937 | -0.20515 | 0.013484 | -0.0050286 | 0.039815 | -0.016616 | -0.0084851 | 0.011553 | 0.004578 | 0.13275 | -0.30212 | 0.091553 | 0.11902 | 0.13733 | -0.11902 | 0.3067 | 0.20599 | -0.27466 | 122.4884 | -0.036622 | 122.7951 | 122.8821 | -0.050354 | 122.5159 | 0.036621 | 0.3067 | 122.6715 | 123.0972 | 122.9095 | 122.9233 | 122.7951 | 122.9965 | 122.9279 | 122.5159 | 122.9233 | 122.7951 | 122.9279 | 122.9095 | 122.9965 | -0.4715 | -0.44403
2882.9688 | 123.056 | -122.7951 | 0.18768 | 0.031357 | 0.014338 | -0.003106 | 0.046865 | -0.014907 | -0.013826 | 0.014544 | -0.073242 | 0.16937 | -0.33417 | -0.027466 | -0.009155 | 0.004578 | -0.009155 | 0.11902 | 0.2655 | -0.28839 | 122.4609 | -0.01831 | 122.7219 | 122.7676 | -0.19684 | 122.5067 | 0.07782 | 0.26092 | 122.7859 | 122.9141 | 122.7859 | 122.9645 | 122.7219 | 123.0606 | 122.7997 | 122.5067 | 122.9645 | 122.7219 | 122.7997 | 122.7859 | 123.0606 | -0.52185 | -0.47607
2884.7188 | 123.0057 | -122.818 | 0.1831 | 0.19157 | 0.010707 | 9.8166e-05 | 0.043233 | -0.015334 | -0.010835 | 0.012194 | 0.032043 | 0.13733 | -0.28839 | 0.091553 | 0.10986 | 0.14191 | -0.18768 | 0.2655 | 0.21057 | -0.24719 | 122.5296 | -0.045776 | 122.85 | 122.9095 | -0.073242 | 122.5708 | 0.027466 | 0.32043 | 122.6303 | 123.0835 | 122.9279 | 122.9553 | 122.85 | 123.0286 | 122.9599 | 122.5708 | 122.9553 | 122.85 | 122.9599 | 122.9279 | 123.0286 | -0.4715 | -0.4303
2886.4219 | 123.1247 | -122.7997 | 0.16479 | -0.060196 | 0.013911 | -0.00054263 | 0.039174 | -0.01747 | -0.0097669 | 0.013475 | -0.032043 | 0.13733 | -0.31128 | 0.059509 | 0.10986 | 0.13275 | -0.10529 | 0.30212 | 0.21515 | -0.25635 | 122.4884 | -0.027466 | 122.7676 | 122.8592 | -0.054932 | 122.5433 | 0.050354 | 0.27924 | 122.6944 | 123.1018 | 122.9095 | 122.937 | 122.7676 | 123.0148 | 122.9324 | 122.5433 | 122.937 | 122.7676 | 122.9324 | 122.9095 | 123.0148 | -0.47607 | -0.42114
2888.1875 | 123.0194 | -122.8317 | 0.19226 | 0.1458 | 0.012629 | -0.001397 | 0.045156 | -0.016616 | -0.010194 | 0.013048 | 0.022888 | 0.15106 | -0.30212 | 0.073242 | 0.086975 | 0.14648 | -0.1831 | 0.26093 | 0.20599 | -0.24719 | 122.5296 | -0.041199 | 122.8546 | 122.905 | -0.10529 | 122.5845 | 0.013733 | 0.32501 | 122.6486 | 123.0927 | 122.9187 | 122.9828 | 122.8546 | 123.0377 | 122.9782 | 122.5845 | 122.9828 | 122.8546 | 122.9782 | 122.9187 | 123.0377 | -0.49438 | -0.43945
2889.9531 | 123.1522 | -122.7859 | 0.16022 | -0.2433 | 0.011775 | -0.003106 | 0.045156 | -0.019179 | -0.0065625 | 0.014544 | -0.10071 | 0.17395 | -0.33875 | -0.004578 | -0.004578 | -0.004578 | 0.045776 | 0.15564 | 0.23346 | -0.31128 | 122.4472 | 0.013733 | 122.6852 | 122.7814 | -0.16479 | 122.4747 | 0.073242 | 0.23804 | 122.8317 | 122.9416 | 122.7814 | 122.9599 | 122.6852 | 123.0194 | 122.7814 | 122.4747 | 122.9599 | 122.6852 | 122.7814 | 122.7814 | 123.0194 | -0.49896 | -0.4715
2891.6406 | 123.1705 | -122.7859 | 0.15564 | -0.16701 | 0.0092115 | -0.00096983 | 0.042165 | -0.01512 | -0.010194 | 0.013475 | -0.10986 | 0.16022 | -0.35248 | -0.018311 | 0.009155 | 0.004578 | 0.054932 | 0.19226 | 0.27466 | -0.29755 | 122.4335 | 0.004577 | 122.6761 | 122.7676 | -0.14649 | 122.4884 | 0.11902 | 0.24262 | 122.8409 | 122.9782 | 122.7951 | 122.9462 | 122.6761 | 123.0606 | 122.7905 | 122.4884 | 122.9462 | 122.6761 | 122.7905 | 122.7951 | 123.0606 | -0.50812 | -0.45319
2893.3438 | 123.024 | -122.818 | 0.18768 | 0.1992 | 0.011775 | -0.0046014 | 0.044515 | -0.014052 | -0.0099805 | 0.011553 | 0.009155 | 0.10529 | -0.28381 | 0.082397 | 0.10986 | 0.15106 | -0.19226 | 0.26093 | 0.19684 | -0.24261 | 122.5342 | -0.082397 | 122.8271 | 122.9004 | -0.07782 | 122.5754 | 0.009155 | 0.29297 | 122.6257 | 123.0789 | 122.9279 | 122.9233 | 122.8271 | 123.0148 | 122.9691 | 122.5754 | 122.9233 | 122.8271 | 122.9691 | 122.9279 | 123.0148 | -0.4715 | -0.4303
2895.0938 | 123.0148 | -122.7997 | 0.19684 | 0.16106 | 0.010921 | -0.0075922 | 0.04601 | -0.01512 | -0.011903 | 0.014757 | 0.004578 | 0.12817 | -0.3067 | 0.068665 | 0.086975 | 0.13733 | -0.16479 | 0.25635 | 0.21057 | -0.25177 | 122.493 | -0.068664 | 122.8043 | 122.8683 | -0.10986 | 122.5479 | 0.013733 | 0.31128 | 122.6349 | 123.056 | 122.8867 | 122.9279 | 122.8043 | 123.0103 | 122.937 | 122.5479 | 122.9279 | 122.8043 | 122.937 | 122.8867 | 123.0103 | -0.50354 | -0.44861
2896.8438 | 123.0286 | -122.818 | 0.19684 | 0.20683 | 0.010493 | -0.004815 | 0.043019 | -0.014052 | -0.0097669 | 0.012835 | 0.004578 | 0.12817 | -0.29297 | 0.091553 | 0.10529 | 0.14191 | -0.19684 | 0.2655 | 0.21057 | -0.24719 | 122.525 | -0.068664 | 122.8226 | 122.9095 | -0.091552 | 122.5708 | 0.013733 | 0.29755 | 122.6212 | 123.0835 | 122.9233 | 122.9462 | 122.8226 | 123.0286 | 122.9599 | 122.5708 | 122.9462 | 122.8226 | 122.9599 | 122.9233 | 123.0286 | -0.48981 | -0.44403
2898.6094 | 123.1064 | -122.7997 | 0.16022 | -0.20515 | 0.010066 | -0.0058832 | 0.040456 | -0.018752 | -0.011903 | 0.012407 | 0 | 0.12817 | -0.29297 | 0.10071 | 0.12817 | 0.13733 | -0.13733 | 0.31128 | 0.21515 | -0.2655 | 122.5067 | -0.032043 | 122.7997 | 122.9004 | -0.032043 | 122.5342 | 0.054932 | 0.29297 | 122.6624 | 123.111 | 122.9279 | 122.9279 | 122.7997 | 123.0148 | 122.937 | 122.5342 | 122.9279 | 122.7997 | 122.937 | 122.9279 | 123.0148 | -0.45319 | -0.42572
2900.3125 | 123.0331 | -122.8409 | 0.1831 | -0.037308 | 0.012629 | -0.004815 | 0.048787 | -0.014266 | -0.013612 | 0.013475 | -0.036621 | 0.15564 | -0.32501 | 0.013733 | 0.004578 | 0.050354 | -0.022888 | 0.15564 | 0.24261 | -0.28381 | 122.5159 | -0.027465 | 122.8043 | 122.8546 | -0.17853 | 122.5571 | 0.05951 | 0.28839 | 122.818 | 122.9965 | 122.8455 | 122.9965 | 122.8043 | 123.0835 | 122.8912 | 122.5571 | 122.9965 | 122.8043 | 122.8912 | 122.8455 | 123.0835 | -0.50812 | -0.46692
2902.0781 | 123.0606 | -122.8134 | 0.17853 | 0.1458 | 0.014552 | -0.001397 | 0.045797 | -0.016829 | -0.0099805 | 0.015612 | -0.068665 | 0.17395 | -0.32959 | -0.032043 | -0.013733 | 0.018311 | -0.013733 | 0.1236 | 0.24261 | -0.31128 | 122.4838 | -0.004578 | 122.7448 | 122.7814 | -0.19226 | 122.5021 | 0.064087 | 0.26092 | 122.7997 | 122.937 | 122.7997 | 122.9874 | 122.7448 | 123.056 | 122.8317 | 122.5021 | 122.9874 | 122.7448 | 122.8317 | 122.7997 | 123.056 | -0.50812 | -0.48981
2903.8438 | 123.1705 | -122.7905 | 0.15564 | -0.17464 | 0.011989 | -0.0024652 | 0.042806 | -0.017897 | -0.012117 | 0.01198 | -0.09613 | 0.16937 | -0.34332 | -0.009155 | 0 | 0.018311 | 0.050354 | 0.16937 | 0.27924 | -0.31128 | 122.4472 | 0.013733 | 122.6944 | 122.7814 | -0.15564 | 122.4792 | 0.1236 | 0.24719 | 122.8409 | 122.9599 | 122.7905 | 122.9599 | 122.6944 | 123.0698 | 122.8088 | 122.4792 | 122.9599 | 122.6944 | 122.8088 | 122.7905 | 123.0698 | -0.49896 | -0.46692
2905.5938 | 123.175 | -122.7859 | 0.16479 | -0.25093 | 0.011561 | -0.0026788 | 0.043019 | -0.017684 | -0.0097669 | 0.015612 | -0.09613 | 0.17853 | -0.35706 | -0.018311 | -0.004578 | 0.009155 | 0.068665 | 0.17395 | 0.2655 | -0.29755 | 122.4289 | 0.013733 | 122.6898 | 122.7676 | -0.16937 | 122.4884 | 0.10071 | 0.26093 | 122.8546 | 122.9599 | 122.7814 | 122.9645 | 122.6898 | 123.0515 | 122.7951 | 122.4884 | 122.9645 | 122.6898 | 122.7951 | 122.7814 | 123.0515 | -0.52185 | -0.46234
2907.2812 | 123.0743 | -122.8134 | 0.19684 | 0.13817 | 0.013698 | -0.0075922 | 0.045583 | -0.013198 | -0.012758 | 0.011766 | -0.09613 | 0.17395 | -0.3479 | -0.027466 | -0.013733 | 0.004578 | -0.022888 | 0.11902 | 0.24719 | -0.29755 | 122.4655 | -0.022888 | 122.7173 | 122.7859 | -0.21057 | 122.5159 | 0.050354 | 0.25177 | 122.7905 | 122.9324 | 122.7997 | 122.9874 | 122.7173 | 123.0606 | 122.818 | 122.5159 | 122.9874 | 122.7173 | 122.818 | 122.7997 | 123.0606 | -0.54474 | -0.49438
2909.0469 | 123.1293 | -122.7722 | 0.16479 | -0.16701 | 0.012843 | -0.00075623 | 0.044301 | -0.015334 | -0.010621 | 0.010912 | -0.086975 | 0.17395 | -0.35248 | -0.004578 | 0.018311 | 0.027466 | 0.041199 | 0.16937 | 0.25635 | -0.28381 | 122.4197 | 0.009155 | 122.6852 | 122.7676 | -0.14648 | 122.4884 | 0.091553 | 0.2655 | 122.8134 | 122.9416 | 122.7905 | 122.9462 | 122.6852 | 123.0286 | 122.7997 | 122.4884 | 122.9462 | 122.6852 | 122.7997 | 122.7905 | 123.0286 | -0.51727 | -0.44861
2910.7969 | 123.1018 | -122.7951 | 0.16022 | 0.15343 | 0.012843 | -0.0041742 | 0.039601 | -0.014907 | -0.0091259 | 0.010912 | -0.022888 | 0.13275 | -0.28839 | 0.036621 | 0.064087 | 0.10529 | -0.1236 | 0.22888 | 0.21973 | -0.27008 | 122.5067 | -0.027466 | 122.7722 | 122.8317 | -0.09613 | 122.525 | 0.05951 | 0.2655 | 122.6715 | 123.024 | 122.8592 | 122.9279 | 122.7722 | 123.0148 | 122.9004 | 122.525 | 122.9279 | 122.7722 | 122.9004 | 122.8592 | 123.0148 | -0.44861 | -0.4303
2912.5625 | 123.0789 | -122.8226 | 0.1831 | 0.16106 | 0.012843 | -0.0028924 | 0.046437 | -0.013839 | -0.01233 | 0.01433 | -0.082397 | 0.16937 | -0.33875 | -0.027466 | -0.027466 | 0.009155 | 0.004578 | 0.11444 | 0.27466 | -0.29755 | 122.4838 | -0.013732 | 122.7402 | 122.7951 | -0.21057 | 122.525 | 0.091553 | 0.25635 | 122.8271 | 122.937 | 122.7951 | 122.9919 | 122.7402 | 123.0972 | 122.8317 | 122.525 | 122.9919 | 122.7402 | 122.8317 | 122.7951 | 123.0972 | -0.52185 | -0.48065
2914.2812 | 123.1384 | -122.7631 | 0.15564 | 0.054245 | 0.012843 | -0.0063104 | 0.040029 | -0.016616 | -0.01169 | 0.012194 | -0.059509 | 0.12817 | -0.3067 | 0.018311 | 0.059509 | 0.10071 | -0.10529 | 0.21515 | 0.2243 | -0.27924 | 122.4564 | -0.027466 | 122.7036 | 122.7814 | -0.096131 | 122.4838 | 0.068664 | 0.24719 | 122.6578 | 122.9782 | 122.8226 | 122.8912 | 122.7036 | 122.9874 | 122.8638 | 122.4838 | 122.8912 | 122.7036 | 122.8638 | 122.8226 | 122.9874 | -0.46234 | -0.43488
2915.9844 | 123.1659 | -122.7722 | 0.16022 | -0.25093 | 0.013698 | -0.0028924 | 0.04366 | -0.016402 | -0.012758 | 0.011339 | -0.073242 | 0.16937 | -0.32044 | -0.009155 | 0.018311 | 0.027466 | 0.027466 | 0.19226 | 0.24261 | -0.28381 | 122.4518 | 0.009156 | 122.699 | 122.7631 | -0.14191 | 122.4884 | 0.082398 | 0.24719 | 122.7997 | 122.9645 | 122.7905 | 122.9416 | 122.699 | 123.0148 | 122.7997 | 122.4884 | 122.9416 | 122.699 | 122.7997 | 122.7905 | 123.0148 | -0.48065 | -0.44403
2917.75 | 123.1293 | -122.7814 | 0.16937 | -0.20515 | 0.0085705 | -0.0033196 | 0.040456 | -0.018111 | -0.010835 | 0.011126 | -0.013733 | 0.13275 | -0.29755 | 0.073242 | 0.086975 | 0.10986 | -0.054932 | 0.27924 | 0.21973 | -0.27924 | 122.4838 | -0.036622 | 122.7676 | 122.8546 | -0.082398 | 122.5021 | 0.050354 | 0.28381 | 122.7264 | 123.0606 | 122.8683 | 122.9141 | 122.7676 | 123.0011 | 122.8912 | 122.5021 | 122.9141 | 122.7676 | 122.8912 | 122.8683 | 123.0011 | -0.46692 | -0.44861
2919.5156 | 123.1155 | -122.818 | 0.17395 | -0.1899 | 0.010493 | -0.0056696 | 0.043447 | -0.015975 | -0.011262 | 0.010698 | 0.013733 | 0.11444 | -0.29755 | 0.086975 | 0.11444 | 0.14191 | -0.11444 | 0.32044 | 0.21515 | -0.26093 | 122.5204 | -0.059509 | 122.8317 | 122.905 | -0.059509 | 122.5571 | 0.041199 | 0.31128 | 122.7036 | 123.1384 | 122.9324 | 122.9324 | 122.8317 | 123.0331 | 122.9599 | 122.5571 | 122.9324 | 122.8317 | 122.9599 | 122.9324 | 123.0331 | -0.4715 | -0.43488
2921.2188 | 123.0194 | -122.8088 | 0.21057 | 0.21446 | 0.012202 | -0.003106 | 0.046437 | -0.014266 | -0.011049 | 0.011339 | -0.045776 | 0.16022 | -0.32501 | 0.036621 | 0.050354 | 0.086975 | -0.13733 | 0.21515 | 0.23804 | -0.25177 | 122.4838 | -0.050354 | 122.7631 | 122.8455 | -0.16022 | 122.5571 | 0.027466 | 0.27924 | 122.6715 | 123.024 | 122.8592 | 122.9691 | 122.7631 | 123.0469 | 122.8958 | 122.5571 | 122.9691 | 122.7631 | 122.8958 | 122.8592 | 123.0469 | -0.53558 | -0.46234
2922.9688 | 123.0515 | -122.85 | 0.19226 | 0.00083945 | 0.01327 | -0.0018244 | 0.047506 | -0.015975 | -0.013399 | 0.013903 | -0.032043 | 0.15564 | -0.33417 | 0.004578 | 0.022888 | 0.032043 | -0.004578 | 0.16937 | 0.23804 | -0.30212 | 122.5159 | -0.036621 | 122.818 | 122.8546 | -0.16937 | 122.5479 | 0.045776 | 0.30212 | 122.8455 | 123.0194 | 122.8729 | 123.0057 | 122.818 | 123.0881 | 122.8821 | 122.5479 | 123.0057 | 122.818 | 122.8821 | 122.8729 | 123.0881 | -0.52643 | -0.49438
2924.7188 | 123.0286 | -122.818 | 0.19226 | 0.19157 | 0.0098523 | -0.00011543 | 0.040883 | -0.013839 | -0.011049 | 0.012194 | 0.022888 | 0.13733 | -0.28839 | 0.082397 | 0.091553 | 0.14191 | -0.17853 | 0.27466 | 0.21515 | -0.2655 | 122.5296 | -0.054932 | 122.8409 | 122.9004 | -0.10071 | 122.5525 | 0.022888 | 0.31128 | 122.6395 | 123.0927 | 122.9095 | 122.9553 | 122.8409 | 123.0331 | 122.9599 | 122.5525 | 122.9553 | 122.8409 | 122.9599 | 122.9095 | 123.0331 | -0.48065 | -0.45776
2926.4062 | 123.1247 | -122.7905 | 0.16937 | -0.25093 | 0.010707 | -0.0035332 | 0.041738 | -0.016188 | -0.011049 | 0.011553 | 0.004578 | 0.14191 | -0.28839 | 0.050354 | 0.082397 | 0.091553 | -0.032043 | 0.25635 | 0.2243 | -0.27924 | 122.5021 | -0.027466 | 122.7951 | 122.8409 | -0.086976 | 122.5113 | 0.054931 | 0.29297 | 122.7585 | 123.0469 | 122.8729 | 122.9324 | 122.7951 | 123.0148 | 122.8821 | 122.5113 | 122.9324 | 122.7951 | 122.8821 | 122.8729 | 123.0148 | -0.45776 | -0.44861
2928.1562 | 123.0743 | -122.7905 | 0.1831 | 0.1458 | 0.012416 | -0.0056696 | 0.043233 | -0.015761 | -0.0093395 | 0.013048 | -0.027466 | 0.11902 | -0.31586 | 0.027466 | 0.064087 | 0.11444 | -0.11902 | 0.22888 | 0.21057 | -0.25635 | 122.4747 | -0.064086 | 122.7631 | 122.818 | -0.11902 | 122.5342 | 0.027466 | 0.28839 | 122.6715 | 123.0194 | 122.8546 | 122.9095 | 122.7631 | 123.0011 | 122.905 | 122.5342 | 122.9095 | 122.7631 | 122.905 | 122.8546 | 123.0011 | -0.49896 | -0.43945
2929.8438 | 123.0331 | -122.818 | 0.19226 | -0.044937 | 0.011775 | -0.0016106 | 0.046437 | -0.01512 | -0.014253 | 0.011339 | -0.045776 | 0.17853 | -0.33417 | 0.018311 | 0.009155 | 0.041199 | -0.018311 | 0.17853 | 0.22888 | -0.28839 | 122.4838 | -0.013733 | 122.7722 | 122.8363 | -0.18311 | 122.5296 | 0.036621 | 0.28839 | 122.7997 | 122.9965 | 122.8271 | 122.9965 | 122.7722 | 123.0469 | 122.8592 | 122.5296 | 122.9965 | 122.7722 | 122.8592 | 122.8271 | 123.0469 | -0.52643 | -0.48065
2931.5312 | 123.0789 | -122.8271 | 0.20142 | 0.092392 | 0.011989 | -0.00054263 | 0.047933 | -0.013198 | -0.011903 | 0.013048 | -0.10986 | 0.17395 | -0.34332 | -0.041199 | -0.041199 | -0.027466 | 0.013733 | 0.11902 | 0.2655 | -0.28839 | 122.4838 | -0.027466 | 122.7173 | 122.7859 | -0.24262 | 122.5388 | 0.064087 | 0.23346 | 122.8409 | 122.9462 | 122.7859 | 123.0011 | 122.7173 | 123.0927 | 122.7997 | 122.5388 | 123.0011 | 122.7173 | 122.7997 | 122.7859 | 123.0927 | -0.54474 | -0.48981
2933.2188 | 123.0743 | -122.8088 | 0.17853 | 0.10765 | 0.013057 | -0.00032903 | 0.044515 | -0.013198 | -0.01169 | 0.011126 | -0.07782 | 0.17395 | -0.3479 | -0.050354 | -0.022888 | 0.013733 | 0 | 0.11444 | 0.2655 | -0.29297 | 122.4609 | -0.004578 | 122.731 | 122.7585 | -0.20142 | 122.5159 | 0.086975 | 0.27008 | 122.8088 | 122.9233 | 122.7859 | 122.9828 | 122.731 | 123.0743 | 122.8226 | 122.5159 | 122.9828 | 122.731 | 122.8226 | 122.7859 | 123.0743 | -0.52643 | -0.4715
2934.9688 | 123.0789 | -122.8271 | 0.19684 | 0.15343 | 0.011775 | -0.0026788 | 0.046865 | -0.012984 | -0.012544 | 0.012621 | -0.11444 | 0.16479 | -0.35706 | -0.054932 | -0.009155 | 0.013733 | 0.009155 | 0.11902 | 0.2655 | -0.29755 | 122.4701 | -0.032043 | 122.7127 | 122.7722 | -0.20599 | 122.5296 | 0.068665 | 0.24261 | 122.8363 | 122.9462 | 122.818 | 122.9919 | 122.7127 | 123.0927 | 122.8409 | 122.5296 | 122.9919 | 122.7127 | 122.8409 | 122.818 | 123.0927 | -0.55389 | -0.49438
2936.7188 | 123.0331 | -122.8409 | 0.19684 | -0.01442 | 0.012843 | -0.0039606 | 0.044301 | -0.017043 | -0.011262 | 0.013475 | -0.045776 | 0.16479 | -0.35248 | 0.004578 | 0.022888 | 0.032043 | -0.013733 | 0.17395 | 0.23804 | -0.29297 | 122.4884 | -0.032043 | 122.7951 | 122.8455 | -0.17395 | 122.5479 | 0.041199 | 0.3067 | 122.8271 | 123.0148 | 122.8638 | 123.0057 | 122.7951 | 123.0789 | 122.8729 | 122.5479 | 123.0057 | 122.7951 | 122.8729 | 122.8638 | 123.0789 | -0.54932 | -0.48981
2938.4688 | 123.0698 | -122.7997 | 0.19684 | 0.077133 | 0.013484 | -0.0054558 | 0.044942 | -0.015548 | -0.010835 | 0.013262 | -0.082397 | 0.17395 | -0.35248 | -0.054932 | -0.013733 | 0.004578 | 0.009155 | 0.11902 | 0.25177 | -0.29297 | 122.4472 | -0.022888 | 122.7173 | 122.7448 | -0.21057 | 122.5067 | 0.054932 | 0.27008 | 122.8088 | 122.9187 | 122.7859 | 122.9736 | 122.7173 | 123.0515 | 122.8043 | 122.5067 | 122.9736 | 122.7173 | 122.8043 | 122.7859 | 123.0515 | -0.54932 | -0.48981
2940.1562 | 123.0698 | -122.818 | 0.17853 | 0.12291 | 0.011561 | -0.00011543 | 0.042592 | -0.014907 | -0.01233 | 0.01198 | -0.10986 | 0.17395 | -0.32959 | -0.041199 | -0.013733 | 0.009155 | 0.013733 | 0.11444 | 0.2655 | -0.29297 | 122.4884 | -0.004578 | 122.7081 | 122.7768 | -0.19226 | 122.525 | 0.086975 | 0.21973 | 122.8317 | 122.9324 | 122.8043 | 122.9919 | 122.7081 | 123.0835 | 122.8271 | 122.525 | 122.9919 | 122.7081 | 122.8271 | 122.8043 | 123.0835 | -0.50812 | -0.4715
2941.9375 | 123.1796 | -122.7768 | 0.16937 | -0.26619 | 0.012843 | -0.0016106 | 0.039815 | -0.018538 | -0.0095531 | 0.012835 | -0.11444 | 0.17853 | -0.35706 | -0.027466 | 0.004578 | 0.013733 | 0.068665 | 0.17395 | 0.24719 | -0.29297 | 122.4197 | 0.009155 | 122.6624 | 122.7493 | -0.16479 | 122.4838 | 0.077819 | 0.24261 | 122.8455 | 122.9507 | 122.7814 | 122.9553 | 122.6624 | 123.024 | 122.7905 | 122.4838 | 122.9553 | 122.6624 | 122.7905 | 122.7814 | 123.024 | -0.52643 | -0.46234
2943.7031 | 123.0606 | -122.8363 | 0.20599 | 0.054245 | 0.013057 | -0.0011834 | 0.047933 | -0.013625 | -0.010408 | 0.011553 | -0.086975 | 0.17853 | -0.34332 | -0.050354 | -0.027466 | 0.013733 | 0.022888 | 0.11902 | 0.25635 | -0.29755 | 122.493 | -0.027466 | 122.7493 | 122.7859 | -0.23346 | 122.5388 | 0.050354 | 0.25635 | 122.8592 | 122.9553 | 122.8088 | 123.0148 | 122.7493 | 123.0927 | 122.85 | 122.5388 | 123.0148 | 122.7493 | 122.85 | 122.8088 | 123.0927 | -0.54932 | -0.50354
2945.3906 | 123.0881 | -122.8134 | 0.20142 | 0.077133 | 0.010921 | -0.0052422 | 0.044301 | -0.014479 | -0.013399 | 0.010057 | -0.082397 | 0.16022 | -0.3479 | -0.041199 | -0.032043 | -0.004578 | 0.022888 | 0.13275 | 0.25177 | -0.3067 | 122.4655 | -0.041199 | 122.731 | 122.7722 | -0.23346 | 122.5067 | 0.050354 | 0.2655 | 122.8363 | 122.9462 | 122.7814 | 122.9736 | 122.731 | 123.0652 | 122.8088 | 122.5067 | 122.9736 | 122.731 | 122.8088 | 122.7814 | 123.0652 | -0.54932 | -0.50812
2947.1406 | 123.1201 | -122.7722 | 0.16479 | -0.25093 | 0.010066 | -0.0046014 | 0.040456 | -0.017684 | -0.0095531 | 0.013475 | -0.018311 | 0.13275 | -0.30212 | 0.032043 | 0.091553 | 0.10529 | -0.045776 | 0.25177 | 0.25177 | -0.27466 | 122.4701 | -0.032044 | 122.7539 | 122.8043 | -0.073242 | 122.4976 | 0.086975 | 0.28381 | 122.7264 | 123.024 | 122.8638 | 122.905 | 122.7539 | 123.024 | 122.8775 | 122.4976 | 122.905 | 122.7539 | 122.8775 | 122.8638 | 123.024 | -0.46692 | -0.43945
2948.9062 | 123.0606 | -122.8317 | 0.20142 | 0.084762 | 0.014338 | 0.0026618 | 0.047078 | -0.011702 | -0.011903 | 0.013048 | -0.086975 | 0.1831 | -0.33875 | -0.045776 | -0.027466 | -0.004578 | 0.022888 | 0.11902 | 0.25177 | -0.31586 | 122.493 | -0.018311 | 122.7448 | 122.7859 | -0.22888 | 122.5159 | 0.050354 | 0.25177 | 122.8546 | 122.9507 | 122.8043 | 123.0148 | 122.7448 | 123.0835 | 122.8271 | 122.5159 | 123.0148 | 122.7448 | 122.8271 | 122.8043 | 123.0835 | -0.54016 | -0.51727
2950.6719 | 123.1247 | -122.8088 | 0.17853 | -0.17464 | 0.012416 | -0.0041742 | 0.043019 | -0.017897 | -0.01169 | 0.014544 | -0.086975 | 0.18768 | -0.33417 | -0.022888 | 0.009155 | 0.022888 | 0.036621 | 0.19226 | 0.25635 | -0.28381 | 122.4747 | 0.009155 | 122.7219 | 122.7859 | -0.16937 | 122.525 | 0.07782 | 0.24719 | 122.8455 | 123.0011 | 122.818 | 122.9965 | 122.7219 | 123.0652 | 122.8317 | 122.525 | 122.9965 | 122.7219 | 122.8317 | 122.818 | 123.0652 | -0.5127 | -0.46234
2952.375 | 123.1201 | -122.7676 | 0.16937 | -0.098343 | 0.011134 | -0.0052422 | 0.036184 | -0.014479 | -0.011262 | 0.012621 | -0.009155 | 0.14191 | -0.27924 | 0.064087 | 0.11902 | 0.15564 | -0.13733 | 0.3067 | 0.20599 | -0.27008 | 122.4884 | -0.027466 | 122.7585 | 122.8317 | -0.050354 | 122.4976 | 0.036621 | 0.27008 | 122.6303 | 123.0743 | 122.8867 | 122.9095 | 122.7585 | 122.9736 | 122.9233 | 122.4976 | 122.9095 | 122.7585 | 122.9233 | 122.8867 | 122.9736 | -0.44861 | -0.43945
2954.125 | 123.175 | -122.7722 | 0.17853 | -0.20515 | 0.011561 | -0.0016106 | 0.042165 | -0.016616 | -0.011476 | 0.011126 | -0.054932 | 0.16479 | -0.3479 | 0.009155 | 0.018311 | 0.045776 | 0.022888 | 0.19684 | 0.25635 | -0.29755 | 122.4243 | -0.013733 | 122.7173 | 122.7814 | -0.16022 | 122.4747 | 0.07782 | 0.29297 | 122.7951 | 122.9691 | 122.7905 | 122.937 | 122.7173 | 123.0286 | 122.818 | 122.4747 | 122.937 | 122.7173 | 122.818 | 122.7905 | 123.0286 | -0.52643 | -0.47607
2955.8906 | 123.1567 | -122.7631 | 0.16937 | 0.00083945 | 0.012843 | -0.0054558 | 0.038106 | -0.016616 | -0.0097669 | 0.010485 | -0.059509 | 0.13733 | -0.31586 | 0.018311 | 0.064087 | 0.082397 | -0.09613 | 0.2243 | 0.22888 | -0.29297 | 122.4472 | -0.032044 | 122.7036 | 122.7814 | -0.10529 | 122.4701 | 0.059509 | 0.25635 | 122.6669 | 122.9874 | 122.8271 | 122.9004 | 122.7036 | 122.9919 | 122.8455 | 122.4701 | 122.9004 | 122.7036 | 122.8455 | 122.8271 | 122.9919 | -0.48523 | -0.46234
2957.5781 | 123.1476 | -122.7722 | 0.1831 | 0.031357 | 0.014125 | -0.0033196 | 0.041738 | -0.018538 | -0.0076305 | 0.013475 | -0.050354 | 0.16479 | -0.31128 | 0.018311 | 0.045776 | 0.07782 | -0.091553 | 0.22888 | 0.21515 | -0.28381 | 122.4609 | -0.01831 | 122.7219 | 122.7905 | -0.13733 | 122.4884 | 0.032044 | 0.26092 | 122.6807 | 123.0011 | 122.818 | 122.937 | 122.7219 | 122.9874 | 122.85 | 122.4884 | 122.937 | 122.7219 | 122.85 | 122.818 | 122.9874 | -0.49438 | -0.46692
2959.3438 | 123.0194 | -122.8363 | 0.18768 | -0.083084 | 0.013057 | -0.001397 | 0.047719 | -0.015334 | -0.014039 | 0.015184 | -0.036621 | 0.16022 | -0.34332 | 0.036621 | 0.027466 | 0.041199 | -0.036621 | 0.19684 | 0.25177 | -0.28839 | 122.493 | -0.027466 | 122.7997 | 122.8729 | -0.16022 | 122.5479 | 0.064087 | 0.3067 | 122.7997 | 123.0331 | 122.8638 | 122.9965 | 122.7997 | 123.0881 | 122.8775 | 122.5479 | 122.9965 | 122.7997 | 122.8775 | 122.8638 | 123.0881 | -0.53101 | -0.47607
2961.0938 | 123.1293 | -122.7905 | 0.1831 | -0.21278 | 0.015407 | -0.001397 | 0.040242 | -0.01747 | -0.011903 | 0.012621 | 0 | 0.13733 | -0.32501 | 0.064087 | 0.091553 | 0.10529 | -0.050354 | 0.28381 | 0.23346 | -0.27924 | 122.4655 | -0.045776 | 122.7905 | 122.8546 | -0.091552 | 122.5113 | 0.050354 | 0.32501 | 122.7402 | 123.0743 | 122.8821 | 122.9279 | 122.7905 | 123.024 | 122.8958 | 122.5113 | 122.9279 | 122.7905 | 122.8958 | 122.8821 | 123.024 | -0.50812 | -0.46234
2962.8438 | 123.0606 | -122.8134 | 0.19226 | 0.10765 | 0.012629 | -0.004815 | 0.041738 | -0.015334 | -0.010621 | 0.012621 | 0.009155 | 0.13275 | -0.30212 | 0.068665 | 0.082397 | 0.1236 | -0.17395 | 0.25177 | 0.21515 | -0.24719 | 122.5113 | -0.05951 | 122.8226 | 122.8821 | -0.10986 | 122.5662 | 0.022888 | 0.31128 | 122.6395 | 123.0652 | 122.8958 | 122.9462 | 122.8226 | 123.0286 | 122.937 | 122.5662 | 122.9462 | 122.8226 | 122.937 | 122.8958 | 123.0286 | -0.49438 | -0.43945
2964.6094 | 123.1842 | -122.7722 | 0.17395 | -0.23567 | 0.011989 | -0.003747 | 0.042592 | -0.016829 | -0.012758 | 0.013689 | -0.10071 | 0.1831 | -0.35248 | -0.022888 | 0.004578 | -0.004578 | 0.068665 | 0.16937 | 0.25635 | -0.3067 | 122.4197 | 0.009155 | 122.6715 | 122.7493 | -0.16937 | 122.4655 | 0.082398 | 0.25177 | 122.8409 | 122.9416 | 122.7768 | 122.9553 | 122.6715 | 123.0286 | 122.7676 | 122.4655 | 122.9553 | 122.6715 | 122.7676 | 122.7768 | 123.0286 | -0.52643 | -0.48065
2966.2969 | 123.0743 | -122.8134 | 0.20142 | 0.038986 | 0.011348 | -0.0022516 | 0.047719 | -0.014266 | -0.015535 | 0.01198 | -0.064087 | 0.17395 | -0.35248 | -0.027466 | -0.022888 | 0 | 0.013733 | 0.11902 | 0.2655 | -0.27924 | 122.4609 | -0.027466 | 122.7493 | 122.7859 | -0.2243 | 122.5342 | 0.064087 | 0.28839 | 122.8271 | 122.9324 | 122.7905 | 122.9874 | 122.7493 | 123.0789 | 122.8134 | 122.5342 | 122.9874 | 122.7493 | 122.8134 | 122.7905 | 123.0789 | -0.55389 | -0.48065
2968.0469 | 123.1247 | -122.7951 | 0.17395 | -0.1136 | 0.012843 | -0.003106 | 0.038533 | -0.015761 | -0.0084851 | 0.012407 | -0.032043 | 0.13733 | -0.29755 | 0.082397 | 0.11902 | 0.14191 | -0.11444 | 0.29297 | 0.21973 | -0.26093 | 122.4976 | -0.036621 | 122.7631 | 122.8775 | -0.054931 | 122.5342 | 0.045777 | 0.2655 | 122.6807 | 123.0881 | 122.9141 | 122.9324 | 122.7631 | 123.0148 | 122.937 | 122.5342 | 122.9324 | 122.7631 | 122.937 | 122.9141 | 123.0148 | -0.4715 | -0.43488
2969.8125 | 123.0469 | -122.818 | 0.19684 | -0.029679 | 0.011775 | 0.00095277 | 0.046865 | -0.014052 | -0.013399 | 0.012621 | -0.027466 | 0.16022 | -0.32959 | 0.027466 | 0.009155 | 0.032043 | -0.036621 | 0.1831 | 0.24719 | -0.27924 | 122.4884 | -0.036621 | 122.7905 | 122.8455 | -0.18768 | 122.5388 | 0.050354 | 0.30212 | 122.7814 | 123.0011 | 122.8271 | 122.9782 | 122.7905 | 123.0652 | 122.85 | 122.5388 | 122.9782 | 122.7905 | 122.85 | 122.8271 | 123.0652 | -0.52643 | -0.47607
2971.5 | 123.0743 | -122.8043 | 0.17853 | 0.15343 | 0.012416 | -0.0018244 | 0.045369 | -0.013411 | -0.011262 | 0.01433 | -0.091553 | 0.17395 | -0.34332 | -0.018311 | -0.013733 | 0.009155 | -0.036621 | 0.1236 | 0.25635 | -0.30212 | 122.4609 | -0.004578 | 122.7127 | 122.7859 | -0.19226 | 122.5021 | 0.07782 | 0.25177 | 122.7676 | 122.9279 | 122.7905 | 122.9782 | 122.7127 | 123.0606 | 122.8134 | 122.5021 | 122.9782 | 122.7127 | 122.8134 | 122.7905 | 123.0606 | -0.52185 | -0.48065
2973.1875 | 123.0652 | -122.8043 | 0.20142 | -0.15175 | 0.014125 | 0.00095277 | 0.047292 | -0.016188 | -0.010621 | 0.010485 | -0.050354 | 0.15564 | -0.3479 | 0.018311 | 0.045776 | 0.050354 | -0.013733 | 0.20142 | 0.24261 | -0.3067 | 122.4564 | -0.045776 | 122.7539 | 122.8226 | -0.15564 | 122.4976 | 0.041199 | 0.29755 | 122.7905 | 123.0057 | 122.85 | 122.9599 | 122.7539 | 123.0469 | 122.8546 | 122.4976 | 122.9599 | 122.7539 | 122.8546 | 122.85 | 123.0469 | -0.54932 | -0.50812
2974.9531 | 123.0927 | -122.8043 | 0.1831 | 0.1458 | 0.012629 | -0.004815 | 0.044942 | -0.014052 | -0.010621 | 0.012194 | -0.09613 | 0.18768 | -0.3479 | -0.036621 | -0.009155 | 0.013733 | -0.009155 | 0.1236 | 0.25177 | -0.28839 | 122.4564 | 0.004578 | 122.7081 | 122.7676 | -0.19226 | 122.5159 | 0.068665 | 0.25177 | 122.7951 | 122.9279 | 122.7951 | 122.9919 | 122.7081 | 123.056 | 122.818 | 122.5159 | 122.9919 | 122.7081 | 122.818 | 122.7951 | 123.056 | -0.531 | -0.4715
2976.6562 | 123.0377 | -122.8455 | 0.19226 | -0.098343 | 0.012416 | -0.0022516 | 0.045583 | -0.016829 | -0.013185 | 0.01433 | -0.032043 | 0.17853 | -0.35706 | 0.027466 | 0.045776 | 0.059509 | -0.018311 | 0.1831 | 0.25635 | -0.28381 | 122.4884 | -0.013733 | 122.8134 | 122.8729 | -0.14648 | 122.5616 | 0.064087 | 0.32501 | 122.8271 | 123.0286 | 122.8912 | 123.024 | 122.8134 | 123.1018 | 122.905 | 122.5616 | 123.024 | 122.8134 | 122.905 | 122.8912 | 123.1018 | -0.54932 | -0.47607
2978.4062 | 123.1476 | -122.7905 | 0.16479 | -0.2433 | 0.014338 | -0.0039606 | 0.040029 | -0.015548 | -0.010408 | 0.011126 | -0.054932 | 0.15106 | -0.31128 | -0.004578 | 0.045776 | 0.036621 | 0.009155 | 0.20599 | 0.23804 | -0.29297 | 122.4792 | -0.013733 | 122.7356 | 122.7859 | -0.11902 | 122.4976 | 0.073242 | 0.25635 | 122.7997 | 122.9965 | 122.8363 | 122.9416 | 122.7356 | 123.0286 | 122.8271 | 122.4976 | 122.9416 | 122.7356 | 122.8271 | 122.8363 | 123.0286 | -0.47607 | -0.45776
2980.0938 | 123.0743 | -122.818 | 0.19226 | 0.11528 | 0.014338 | -0.0046014 | 0.044515 | -0.015548 | -0.011903 | 0.014544 | -0.11902 | 0.16022 | -0.35248 | -0.045776 | -0.013733 | 0.018311 | -0.013733 | 0.13275 | 0.23346 | -0.31128 | 122.4655 | -0.032044 | 122.699 | 122.7722 | -0.20599 | 122.5067 | 0.041198 | 0.23346 | 122.8043 | 122.9507 | 122.8043 | 122.9782 | 122.699 | 123.0515 | 122.8363 | 122.5067 | 122.9782 | 122.699 | 122.8363 | 122.8043 | 123.0515 | -0.54474 | -0.50354
2981.8438 | 123.0606 | -122.8043 | 0.1831 | 0.16869 | 0.013057 | -0.0024652 | 0.045583 | -0.014052 | -0.010194 | 0.012621 | -0.10529 | 0.16937 | -0.3479 | -0.050354 | -0.027466 | 0.013733 | 0.004578 | 0.11444 | 0.26093 | -0.29755 | 122.4564 | -0.013732 | 122.699 | 122.7539 | -0.21057 | 122.5067 | 0.07782 | 0.24261 | 122.8088 | 122.9187 | 122.7768 | 122.9736 | 122.699 | 123.0652 | 122.818 | 122.5067 | 122.9736 | 122.699 | 122.818 | 122.7768 | 123.0652 | -0.531 | -0.48065
2983.5938 | 123.1613 | -122.7722 | 0.16937 | -0.22041 | 0.011989 | -0.0028924 | 0.039388 | -0.017256 | -0.0099805 | 0.0089893 | -0.086975 | 0.16937 | -0.33417 | -0.018311 | 0.004578 | 0.018311 | 0.054932 | 0.1831 | 0.24719 | -0.29755 | 122.4381 | 0 | 122.6852 | 122.7539 | -0.16479 | 122.4747 | 0.077819 | 0.24719 | 122.8271 | 122.9553 | 122.7768 | 122.9416 | 122.6852 | 123.0194 | 122.7905 | 122.4747 | 122.9416 | 122.6852 | 122.7905 | 122.7768 | 123.0194 | -0.50354 | -0.46692
2985.2969 | 122.9965 | -122.8134 | 0.19226 | 0.18394 | 0.012416 | -0.0018244 | 0.045156 | -0.015975 | -0.010621 | 0.011339 | 0.009155 | 0.14648 | -0.3067 | 0.073242 | 0.09613 | 0.14648 | -0.18768 | 0.28381 | 0.20142 | -0.25177 | 122.5067 | -0.045777 | 122.8226 | 122.8867 | -0.096131 | 122.5616 | 0.009155 | 0.31586 | 122.6257 | 123.0972 | 122.9095 | 122.9599 | 122.8226 | 123.0148 | 122.9599 | 122.5616 | 122.9599 | 122.8226 | 122.9599 | 122.9095 | 123.0148 | -0.49896 | -0.44403
2987.0469 | 123.111 | -122.8043 | 0.17853 | -0.22041 | 0.011775 | -0.011865 | 0.044515 | -0.018111 | -0.011262 | 0.011766 | -0.082397 | 0.17395 | -0.33417 | 0.022888 | 0.022888 | 0.036621 | 0.018311 | 0.20142 | 0.24719 | -0.31128 | 122.4701 | -0.004578 | 122.7219 | 122.8271 | -0.15564 | 122.493 | 0.068664 | 0.25177 | 122.8226 | 123.0057 | 122.8271 | 122.9782 | 122.7219 | 123.0515 | 122.8409 | 122.493 | 122.9782 | 122.7219 | 122.8409 | 122.8271 | 123.0515 | -0.5127 | -0.48981
2988.7344 | 123.143 | -122.7768 | 0.16022 | -0.18227 | 0.012629 | -0.0058832 | 0.043019 | -0.016402 | -0.0095531 | 0.012407 | -0.10071 | 0.19226 | -0.35248 | -0.004578 | 0.009155 | 0.022888 | 0.032043 | 0.19226 | 0.2655 | -0.28839 | 122.4243 | 0.032044 | 122.6761 | 122.7722 | -0.15106 | 122.4884 | 0.10529 | 0.25177 | 122.8088 | 122.9691 | 122.7859 | 122.9691 | 122.6761 | 123.0423 | 122.7997 | 122.4884 | 122.9691 | 122.6761 | 122.7997 | 122.7859 | 123.0423 | -0.5127 | -0.44861
2990.5 | 123.0286 | -122.8134 | 0.20599 | 0.21446 | 0.012629 | -0.00096983 | 0.04067 | -0.014479 | -0.010408 | 0.012621 | -0.027466 | 0.16022 | -0.31128 | 0.050354 | 0.082397 | 0.13275 | -0.14191 | 0.23804 | 0.2243 | -0.25177 | 122.5021 | -0.045777 | 122.7859 | 122.8638 | -0.1236 | 122.5616 | 0.01831 | 0.28381 | 122.6715 | 123.0515 | 122.8958 | 122.9736 | 122.7859 | 123.0377 | 122.9462 | 122.5616 | 122.9736 | 122.7859 | 122.9462 | 122.8958 | 123.0377 | -0.51727 | -0.45776
2992.1875 | 123.1155 | -122.7905 | 0.16022 | -0.060196 | 0.010707 | -0.0067376 | 0.037465 | -0.017043 | -0.010621 | 0.014971 | -0.018311 | 0.14648 | -0.30212 | 0.082397 | 0.11444 | 0.16022 | -0.1236 | 0.31586 | 0.2243 | -0.28381 | 122.4884 | -0.013733 | 122.7722 | 122.8729 | -0.045776 | 122.5067 | 0.064087 | 0.28381 | 122.6669 | 123.1064 | 122.905 | 122.937 | 122.7722 | 123.0148 | 122.9507 | 122.5067 | 122.937 | 122.7722 | 122.9507 | 122.905 | 123.0148 | -0.46234 | -0.44403
2993.9375 | 123.143 | -122.7722 | 0.16937 | -0.060196 | 0.012202 | -0.0011834 | 0.039388 | -0.019393 | -0.0091259 | 0.011553 | -0.036621 | 0.14191 | -0.29755 | 0.068665 | 0.082397 | 0.1236 | -0.10986 | 0.28381 | 0.21515 | -0.28381 | 122.4747 | -0.027466 | 122.7356 | 122.8409 | -0.086976 | 122.4884 | 0.045776 | 0.26092 | 122.6624 | 123.056 | 122.8546 | 122.9141 | 122.7356 | 122.9874 | 122.8958 | 122.4884 | 122.9141 | 122.7356 | 122.8958 | 122.8546 | 122.9874 | -0.46692 | -0.45319
2995.6875 | 123.1476 | -122.8043 | 0.1831 | -0.037308 | 0.010921 | -0.0052422 | 0.041097 | -0.018111 | -0.0089123 | 0.011126 | -0.054932 | 0.12817 | -0.32044 | 0.050354 | 0.082397 | 0.10529 | -0.10986 | 0.27466 | 0.22888 | -0.27924 | 122.4838 | -0.054931 | 122.7493 | 122.8546 | -0.10071 | 122.525 | 0.045777 | 0.2655 | 122.6944 | 123.0789 | 122.8867 | 122.9324 | 122.7493 | 123.0331 | 122.9095 | 122.525 | 122.9324 | 122.7493 | 122.9095 | 122.8867 | 123.0331 | -0.50354 | -0.46234
2997.375 | 123.0423 | -122.8271 | 0.21515 | -0.1136 | 0.012843 | -0.0033196 | 0.049215 | -0.015334 | -0.013826 | 0.01198 | -0.027466 | 0.15564 | -0.35248 | 0.050354 | 0.036621 | 0.064087 | -0.027466 | 0.2243 | 0.25635 | -0.28381 | 122.4747 | -0.059509 | 122.7997 | 122.8775 | -0.17853 | 122.5433 | 0.041199 | 0.32501 | 122.7997 | 123.0515 | 122.8638 | 122.9828 | 122.7997 | 123.0835 | 122.8912 | 122.5433 | 122.9828 | 122.7997 | 122.8912 | 122.8638 | 123.0835 | -0.56763 | -0.49896
2999.125 | 123.0743 | -122.8088 | 0.20599 | 0.10002 | 0.014766 | -0.001397 | 0.044942 | -0.015761 | -0.0099805 | 0.01433 | -0.073242 | 0.19226 | -0.3479 | -0.022888 | -0.009155 | 0.004578 | -0.045776 | 0.13733 | 0.24261 | -0.30212 | 122.4609 | -0.013733 | 122.7356 | 122.7859 | -0.21515 | 122.5067 | 0.036621 | 0.27466 | 122.7631 | 122.9462 | 122.7997 | 123.0011 | 122.7356 | 123.0515 | 122.8134 | 122.5067 | 123.0011 | 122.7356 | 122.8134 | 122.7997 | 123.0515 | -0.55389 | -0.50812
3000.8281 | 123.1338 | -122.8134 | 0.1831 | -0.17464 | 0.013057 | -0.0041742 | 0.044301 | -0.015761 | -0.010621 | 0.011339 | -0.082397 | 0.1831 | -0.35706 | 0 | 0.009155 | 0.027466 | 0.050354 | 0.18768 | 0.26093 | -0.28381 | 122.4564 | 0 | 122.731 | 122.8134 | -0.17395 | 122.5296 | 0.07782 | 0.27466 | 122.8638 | 123.0011 | 122.8226 | 122.9965 | 122.731 | 123.0743 | 122.8409 | 122.5296 | 122.9965 | 122.731 | 122.8409 | 122.8226 | 123.0743 | -0.54016 | -0.46692
3002.5781 | 123.1476 | -122.7676 | 0.17395 | -0.01442 | 0.0098523 | -0.0063104 | 0.038533 | -0.017684 | -0.0093395 | 0.01198 | -0.041199 | 0.14648 | -0.3067 | 0.045776 | 0.091553 | 0.11444 | -0.10529 | 0.26093 | 0.20599 | -0.27924 | 122.4609 | -0.027466 | 122.7264 | 122.8134 | -0.082397 | 122.4884 | 0.032044 | 0.2655 | 122.6624 | 123.0286 | 122.8592 | 122.9141 | 122.7264 | 122.9736 | 122.8821 | 122.4884 | 122.9141 | 122.7264 | 122.8821 | 122.8592 | 122.9736 | -0.48065 | -0.45319
3004.2812 | 123.0331 | -122.8317 | 0.18768 | 0.22209 | 0.0098523 | -0.0052422 | 0.045369 | -0.017043 | -0.011476 | 0.013048 | -0.064087 | 0.16479 | -0.32044 | 0.013733 | 0.027466 | 0.068665 | -0.09613 | 0.19226 | 0.22888 | -0.27466 | 122.5113 | -0.022888 | 122.7676 | 122.8455 | -0.16022 | 122.5571 | 0.041199 | 0.25635 | 122.7356 | 123.024 | 122.8592 | 122.9965 | 122.7676 | 123.0606 | 122.9004 | 122.5571 | 122.9965 | 122.7676 | 122.9004 | 122.8592 | 123.0606 | -0.50812 | -0.46234
3006.0312 | 123.0881 | -122.818 | 0.19226 | 0.17632 | 0.015193 | -0.0046014 | 0.047078 | -0.014693 | -0.012544 | 0.011766 | -0.10071 | 0.17395 | -0.36163 | -0.018311 | -0.018311 | 0.009155 | -0.013733 | 0.13275 | 0.24719 | -0.30212 | 122.4564 | -0.018311 | 122.7173 | 122.7997 | -0.21057 | 122.5159 | 0.054931 | 0.26092 | 122.8043 | 122.9507 | 122.7997 | 122.9919 | 122.7173 | 123.0652 | 122.8271 | 122.5159 | 122.9919 | 122.7173 | 122.8271 | 122.7997 | 123.0652 | -0.55389 | -0.49438
3007.7812 | 123.0469 | -122.818 | 0.21515 | 0.16106 | 0.011348 | -0.0022516 | 0.040456 | -0.016616 | -0.010408 | 0.012835 | 0.009155 | 0.14191 | -0.3067 | 0.07782 | 0.09613 | 0.14191 | -0.17853 | 0.27924 | 0.20599 | -0.25177 | 122.5113 | -0.073242 | 122.8271 | 122.8958 | -0.11902 | 122.5662 | -0.009155 | 0.31586 | 122.6395 | 123.0972 | 122.9141 | 122.9599 | 122.8271 | 123.024 | 122.9599 | 122.5662 | 122.9599 | 122.8271 | 122.9599 | 122.9141 | 123.024 | -0.52185 | -0.46692
3009.4844 | 123.143 | -122.7905 | 0.19684 | -0.1899 | 0.010707 | -0.0056696 | 0.041951 | -0.019179 | -0.011049 | 0.012621 | -0.004578 | 0.13733 | -0.31586 | 0.064087 | 0.091553 | 0.10529 | -0.059509 | 0.28839 | 0.22888 | -0.27466 | 122.4747 | -0.059509 | 122.7859 | 122.8546 | -0.10529 | 122.5159 | 0.032044 | 0.31128 | 122.731 | 123.0789 | 122.8821 | 122.9279 | 122.7859 | 123.0194 | 122.8958 | 122.5159 | 122.9279 | 122.7859 | 122.8958 | 122.8821 | 123.0194 | -0.5127 | -0.4715
3011.2344 | 123.0469 | -122.8317 | 0.20142 | 0.13054 | 0.010921 | -0.0028924 | 0.043019 | -0.018752 | -0.010835 | 0.013903 | -0.004578 | 0.11444 | -0.31586 | 0.068665 | 0.082397 | 0.12817 | -0.17395 | 0.27924 | 0.20142 | -0.2655 | 122.5159 | -0.086975 | 122.8271 | 122.9004 | -0.11902 | 122.5662 | 0 | 0.31128 | 122.6578 | 123.111 | 122.9141 | 122.9462 | 122.8271 | 123.0331 | 122.9599 | 122.5662 | 122.9462 | 122.8271 | 122.9599 | 122.9141 | 123.0331 | -0.51727 | -0.46692
3012.9844 | 123.1567 | -122.7768 | 0.17395 | 0.016098 | 0.011775 | -0.003106 | 0.040242 | -0.018111 | -0.0099805 | 0.010057 | -0.054932 | 0.13733 | -0.3067 | 0.027466 | 0.050354 | 0.082397 | -0.09613 | 0.22888 | 0.23346 | -0.27008 | 122.4701 | -0.036621 | 122.7219 | 122.8043 | -0.1236 | 122.5067 | 0.059509 | 0.25177 | 122.6807 | 123.0057 | 122.8271 | 122.9141 | 122.7219 | 123.0103 | 122.8592 | 122.5067 | 122.9141 | 122.7219 | 122.8592 | 122.8271 | 123.0103 | -0.48065 | -0.44403
3014.75 | 123.1201 | -122.7997 | 0.19684 | -0.16701 | 0.010707 | -0.003106 | 0.041524 | -0.018111 | -0.0095531 | 0.011553 | 0.018311 | 0.14191 | -0.29297 | 0.11444 | 0.11444 | 0.15106 | -0.13275 | 0.3067 | 0.20142 | -0.27924 | 122.5067 | -0.054931 | 122.818 | 122.9141 | -0.082397 | 122.5204 | 0.004578 | 0.31128 | 122.6669 | 123.1064 | 122.9141 | 122.9416 | 122.818 | 123.0011 | 122.9507 | 122.5204 | 122.9416 | 122.818 | 122.9507 | 122.9141 | 123.0011 | -0.48981 | -0.47607
3016.5156 | 123.0148 | -122.8683 | 0.19684 | 0.18394 | 0.0081433 | -0.0050286 | 0.045583 | -0.014266 | -0.011903 | 0.014116 | 0.022888 | 0.12817 | -0.3067 | 0.10986 | 0.086975 | 0.14648 | -0.19684 | 0.2655 | 0.20142 | -0.24719 | 122.5616 | -0.068664 | 122.8912 | 122.9782 | -0.10986 | 122.6212 | 0.004578 | 0.32959 | 122.6715 | 123.1338 | 122.9553 | 122.9965 | 122.8912 | 123.0698 | 123.0148 | 122.6212 | 122.9965 | 122.8912 | 123.0148 | 122.9553 | 123.0698 | -0.50354 | -0.44403
3018.2031 | 123.0835 | -122.8088 | 0.16937 | 0.1458 | 0.013911 | -0.0043878 | 0.047506 | -0.016616 | -0.010408 | 0.011766 | -0.07782 | 0.19684 | -0.36163 | -0.013733 | -0.027466 | 0.009155 | -0.032043 | 0.14648 | 0.25635 | -0.29297 | 122.4472 | 0.027465 | 122.731 | 122.7951 | -0.19684 | 122.5159 | 0.086975 | 0.28381 | 122.7768 | 122.9553 | 122.7814 | 123.0057 | 122.731 | 123.0652 | 122.818 | 122.5159 | 123.0057 | 122.731 | 122.818 | 122.7814 | 123.0652 | -0.53101 | -0.46234
3019.9688 | 123.1796 | -122.7814 | 0.1831 | -0.2433 | 0.011561 | -0.0095148 | 0.041097 | -0.018965 | -0.010835 | 0.012407 | -0.11444 | 0.18768 | -0.33417 | -0.009155 | -0.013733 | 0.004578 | 0.068665 | 0.17395 | 0.25635 | -0.32501 | 122.4472 | 0.004578 | 122.6669 | 122.7722 | -0.19684 | 122.4564 | 0.073243 | 0.21973 | 122.85 | 122.9553 | 122.7676 | 122.9691 | 122.6669 | 123.0377 | 122.7859 | 122.4564 | 122.9691 | 122.6669 | 122.7859 | 122.7676 | 123.0377 | -0.51727 | -0.50812
3021.7344 | 123.0469 | -122.8226 | 0.20142 | -0.098343 | 0.010921 | -0.0028924 | 0.047078 | -0.015334 | -0.012758 | 0.011766 | -0.036621 | 0.17395 | -0.36163 | 0.050354 | 0.045776 | 0.059509 | -0.027466 | 0.21057 | 0.26093 | -0.27924 | 122.4609 | -0.027466 | 122.7859 | 122.8729 | -0.15564 | 122.5433 | 0.059509 | 0.32501 | 122.7951 | 123.0331 | 122.8683 | 122.9965 | 122.7859 | 123.0835 | 122.8821 | 122.5433 | 122.9965 | 122.7859 | 122.8821 | 122.8683 | 123.0835 | -0.56305 | -0.48065
3023.4375 | 123.0331 | -122.85 | 0.18768 | 0.20683 | 0.012629 | -0.0011834 | 0.04131 | -0.014052 | -0.011049 | 0.013903 | 0.032043 | 0.12817 | -0.32044 | 0.09613 | 0.11444 | 0.13733 | -0.21515 | 0.27008 | 0.21057 | -0.28381 | 122.5296 | -0.059509 | 122.8821 | 122.9462 | -0.073242 | 122.5662 | 0.022888 | 0.35248 | 122.6349 | 123.1201 | 122.9645 | 122.9782 | 122.8821 | 123.0606 | 122.9874 | 122.5662 | 122.9782 | 122.8821 | 122.9874 | 122.9645 | 123.0606 | -0.50812 | -0.4715
3025.2031 | 123.0194 | -122.8043 | 0.21515 | 0.17632 | 0.012416 | -0.0022516 | 0.044728 | -0.014693 | -0.010194 | 0.010485 | 0.013733 | 0.13275 | -0.31586 | 0.082397 | 0.09613 | 0.14648 | -0.19684 | 0.25177 | 0.19684 | -0.25177 | 122.4884 | -0.082398 | 122.818 | 122.8867 | -0.11902 | 122.5525 | -0.018311 | 0.32959 | 122.6074 | 123.056 | 122.9004 | 122.937 | 122.818 | 123.0011 | 122.9507 | 122.5525 | 122.937 | 122.818 | 122.9507 | 122.9004 | 123.0011 | -0.53101 | -0.46692
3026.9688 | 123.1613 | -122.7722 | 0.1831 | 0.016098 | 0.014125 | -0.0058832 | 0.03832 | -0.018538 | -0.011049 | 0.014544 | -0.068665 | 0.14191 | -0.32959 | 0.041199 | 0.064087 | 0.10986 | -0.091553 | 0.24261 | 0.23804 | -0.28839 | 122.4426 | -0.041198 | 122.7036 | 122.8134 | -0.11902 | 122.4838 | 0.054932 | 0.26092 | 122.6807 | 123.0148 | 122.8363 | 122.9141 | 122.7036 | 123.0103 | 122.8821 | 122.4838 | 122.9141 | 122.7036 | 122.8821 | 122.8363 | 123.0103 | -0.5127 | -0.4715
3028.6562 | 123.1522 | -122.7722 | 0.17395 | 0.016098 | 0.01327 | -0.0033196 | 0.039601 | -0.015548 | -0.01169 | 0.010271 | -0.064087 | 0.15564 | -0.31128 | 0.059509 | 0.086975 | 0.10071 | -0.10986 | 0.25635 | 0.21057 | -0.26093 | 122.4609 | -0.01831 | 122.7081 | 122.8317 | -0.086975 | 122.5113 | 0.036621 | 0.24719 | 122.6624 | 123.0286 | 122.8592 | 122.9279 | 122.7081 | 122.9828 | 122.8729 | 122.5113 | 122.9279 | 122.7081 | 122.8729 | 122.8592 | 122.9828 | -0.48523 | -0.43488
3030.375 | 123.1476 | -122.7951 | 0.17395 | -0.26619 | 0.011775 | -0.004815 | 0.044301 | -0.017256 | -0.012544 | 0.0092029 | -0.032043 | 0.14648 | -0.32959 | 0.054932 | 0.059509 | 0.073242 | -0.013733 | 0.23804 | 0.23346 | -0.28839 | 122.4655 | -0.027466 | 122.7631 | 122.85 | -0.11444 | 122.5067 | 0.059509 | 0.29755 | 122.7814 | 123.0331 | 122.8546 | 122.9416 | 122.7631 | 123.0286 | 122.8683 | 122.5067 | 122.9416 | 122.7631 | 122.8683 | 122.8546 | 123.0286 | -0.50354 | -0.46234
3032.125 | 123.0423 | -122.85 | 0.18768 | 0.20683 | 0.011989 | -0.0039606 | 0.045156 | -0.016616 | -0.0097669 | 0.012621 | 0 | 0.13733 | -0.32044 | 0.09613 | 0.10986 | 0.16022 | -0.19226 | 0.27466 | 0.21057 | -0.26093 | 122.5296 | -0.050354 | 122.85 | 122.9462 | -0.07782 | 122.5891 | 0.022888 | 0.32044 | 122.6578 | 123.1247 | 122.9599 | 122.9874 | 122.85 | 123.0606 | 123.0103 | 122.5891 | 122.9874 | 122.85 | 123.0103 | 122.9599 | 123.0606 | -0.50812 | -0.44861
3033.8125 | 123.1384 | -122.8088 | 0.16479 | -0.067826 | 0.0096387 | -0.0041742 | 0.039815 | -0.019606 | -0.0086987 | 0.01198 | -0.027466 | 0.13733 | -0.33417 | 0.09613 | 0.09613 | 0.14191 | -0.13733 | 0.29755 | 0.21515 | -0.28381 | 122.4747 | -0.027466 | 122.7814 | 122.905 | -0.068665 | 122.525 | 0.050354 | 0.3067 | 122.6715 | 123.1064 | 122.905 | 122.9462 | 122.7814 | 123.024 | 122.9507 | 122.525 | 122.9462 | 122.7814 | 122.9507 | 122.905 | 123.024 | -0.49896 | -0.44861
3035.5938 | 123.1201 | -122.7951 | 0.16479 | -0.12886 | 0.011989 | -0.0052422 | 0.042806 | -0.016188 | -0.0089123 | 0.012407 | 0.004578 | 0.1236 | -0.32501 | 0.13275 | 0.14191 | 0.16479 | -0.13275 | 0.32501 | 0.21973 | -0.24719 | 122.4701 | -0.041199 | 122.7997 | 122.9279 | -0.022888 | 122.5479 | 0.054932 | 0.32959 | 122.6624 | 123.1201 | 122.937 | 122.9187 | 122.7997 | 123.0148 | 122.9599 | 122.5479 | 122.9187 | 122.7997 | 122.9599 | 122.937 | 123.0148 | -0.48981 | -0.41199
3037.2812 | 123.1476 | -122.7722 | 0.18768 | -0.2433 | 0.013057 | -0.0086602 | 0.048146 | -0.016402 | -0.013185 | 0.013048 | -0.091553 | 0.18768 | -0.37079 | -0.004578 | -0.004578 | -0.004578 | 0.054932 | 0.17395 | 0.25177 | -0.30212 | 122.4014 | 0 | 122.6807 | 122.7676 | -0.19226 | 122.4701 | 0.064087 | 0.27924 | 122.8271 | 122.9462 | 122.7676 | 122.9599 | 122.6807 | 123.024 | 122.7676 | 122.4701 | 122.9599 | 122.6807 | 122.7676 | 122.7676 | 123.024 | -0.55847 | -0.48981
3039.0469 | 123.143 | -122.8043 | 0.17853 | -0.1899 | 0.010707 | -0.0069512 | 0.046651 | -0.016402 | -0.012544 | 0.013048 | -0.086975 | 0.16022 | -0.36163 | 0.013733 | 0.022888 | 0.009155 | 0.041199 | 0.1831 | 0.25635 | -0.28381 | 122.4426 | -0.018311 | 122.7173 | 122.818 | -0.15564 | 122.5204 | 0.07782 | 0.27466 | 122.8455 | 122.9874 | 122.8271 | 122.9645 | 122.7173 | 123.0606 | 122.8134 | 122.5204 | 122.9645 | 122.7173 | 122.8134 | 122.8271 | 123.0606 | -0.54016 | -0.46234
3040.8125 | 123.0377 | -122.8226 | 0.20142 | -0.067826 | 0.013911 | -0.0069512 | 0.047292 | -0.016616 | -0.012117 | 0.012194 | -0.022888 | 0.16937 | -0.35248 | 0.045776 | 0.041199 | 0.054932 | -0.032043 | 0.20599 | 0.24261 | -0.28839 | 122.4701 | -0.032043 | 122.7997 | 122.8683 | -0.16022 | 122.5342 | 0.041199 | 0.32959 | 122.7905 | 123.0286 | 122.8638 | 122.9919 | 122.7997 | 123.0652 | 122.8775 | 122.5342 | 122.9919 | 122.7997 | 122.8775 | 122.8638 | 123.0652 | -0.55389 | -0.48981
3042.5156 | 123.0698 | -122.818 | 0.1831 | 0.13817 | 0.013057 | -0.0046014 | 0.045797 | -0.017043 | -0.0091259 | 0.012835 | -0.10071 | 0.17395 | -0.3479 | -0.013733 | 0.009155 | 0.022888 | -0.036621 | 0.13733 | 0.23346 | -0.3067 | 122.4701 | -0.009155 | 122.7173 | 122.8043 | -0.17395 | 122.5113 | 0.050354 | 0.24719 | 122.7814 | 122.9553 | 122.8271 | 122.9919 | 122.7173 | 123.0515 | 122.8409 | 122.5113 | 122.9919 | 122.7173 | 122.8409 | 122.8271 | 123.0515 | -0.531 | -0.48981
3044.2812 | 123.0331 | -122.8363 | 0.20142 | 0.1458 | 0.01562 | -0.0035332 | 0.044301 | -0.014479 | -0.0078443 | 0.012835 | -0.004578 | 0.15106 | -0.31128 | 0.082397 | 0.10529 | 0.14191 | -0.17853 | 0.24719 | 0.21973 | -0.27008 | 122.525 | -0.050354 | 122.8317 | 122.9187 | -0.09613 | 122.5662 | 0.018311 | 0.3067 | 122.6578 | 123.0835 | 122.9416 | 122.9874 | 122.8317 | 123.056 | 122.9782 | 122.5662 | 122.9874 | 122.8317 | 122.9782 | 122.9416 | 123.056 | -0.5127 | -0.4715
3046.0469 | 123.0743 | -122.8317 | 0.18768 | 0.092392 | 0.011775 | 0.0024482 | 0.046437 | -0.013625 | -0.010835 | 0.010912 | -0.091553 | 0.17395 | -0.35706 | -0.041199 | -0.022888 | -0.013733 | 0.013733 | 0.09613 | 0.27008 | -0.30212 | 122.4747 | -0.013733 | 122.7402 | 122.7905 | -0.21057 | 122.5296 | 0.082398 | 0.2655 | 122.8455 | 122.9279 | 122.8088 | 123.0057 | 122.7402 | 123.1018 | 122.818 | 122.5296 | 123.0057 | 122.7402 | 122.818 | 122.8088 | 123.1018 | -0.54474 | -0.48981
3047.75 | 123.0469 | -122.7997 | 0.19226 | 0.17632 | 0.011134 | -0.0060968 | 0.044301 | -0.016616 | -0.012971 | 0.012835 | -0.07782 | 0.16479 | -0.34332 | 0.009155 | 0.041199 | 0.059509 | -0.10529 | 0.18768 | 0.24261 | -0.2655 | 122.4564 | -0.027466 | 122.7219 | 122.8088 | -0.15106 | 122.5342 | 0.050354 | 0.2655 | 122.6944 | 122.9874 | 122.8409 | 122.9645 | 122.7219 | 123.0423 | 122.8592 | 122.5342 | 122.9645 | 122.7219 | 122.8592 | 122.8409 | 123.0423 | -0.53558 | -0.45776
3049.5156 | 123.1613 | -122.7997 | 0.17395 | -0.0067901 | 0.011561 | -0.003106 | 0.038747 | -0.017256 | -0.0086987 | 0.012621 | -0.059509 | 0.15106 | -0.32501 | 0.041199 | 0.07782 | 0.10986 | -0.10986 | 0.24719 | 0.21515 | -0.27466 | 122.4747 | -0.022888 | 122.7402 | 122.8409 | -0.09613 | 122.525 | 0.041199 | 0.2655 | 122.6898 | 123.0469 | 122.8775 | 122.9507 | 122.7402 | 123.0148 | 122.9095 | 122.525 | 122.9507 | 122.7402 | 122.9095 | 122.8775 | 123.0148 | -0.49896 | -0.44861
3051.2031 | 123.0835 | -122.8363 | 0.21057 | -0.037308 | 0.011134 | -0.0052422 | 0.046651 | -0.013411 | -0.0093395 | 0.013689 | -0.091553 | 0.1831 | -0.35248 | -0.036621 | -0.018311 | -0.004578 | 0.009155 | 0.1236 | 0.25177 | -0.29755 | 122.4838 | -0.027466 | 122.7448 | 122.7997 | -0.22888 | 122.5388 | 0.041199 | 0.26093 | 122.8455 | 122.9599 | 122.818 | 123.0194 | 122.7448 | 123.0881 | 122.8317 | 122.5388 | 123.0194 | 122.7448 | 122.8317 | 122.818 | 123.0881 | -0.56305 | -0.50812
3052.9531 | 123.1018 | -122.8455 | 0.19226 | 0.10002 | 0.013057 | -0.0039606 | 0.047292 | -0.012984 | -0.014894 | 0.011553 | -0.11444 | 0.1831 | -0.35248 | -0.041199 | -0.022888 | -0.013733 | 0.009155 | 0.11444 | 0.27008 | -0.29755 | 122.493 | -0.009156 | 122.731 | 122.8043 | -0.21515 | 122.5479 | 0.07782 | 0.23804 | 122.8546 | 122.9599 | 122.8226 | 123.0286 | 122.731 | 123.1155 | 122.8317 | 122.5479 | 123.0286 | 122.731 | 122.8317 | 122.8226 | 123.1155 | -0.54474 | -0.48981
3054.6406 | 123.0652 | -122.85 | 0.20142 | 0.13054 | 0.011561 | -0.00075623 | 0.044728 | -0.017256 | -0.01233 | 0.013262 | -0.09613 | 0.16479 | -0.36163 | -0.013733 | 0.004578 | 0.036621 | -0.032043 | 0.14648 | 0.25635 | -0.31128 | 122.4884 | -0.036621 | 122.7539 | 122.8363 | -0.19684 | 122.5388 | 0.054932 | 0.2655 | 122.818 | 122.9965 | 122.8546 | 123.0148 | 122.7539 | 123.1064 | 122.8867 | 122.5388 | 123.0148 | 122.7539 | 122.8867 | 122.8546 | 123.1064 | -0.56305 | -0.5127
3056.3906 | 123.0652 | -122.8134 | 0.1831 | 0.10765 | 0.011134 | -0.011865 | 0.040456 | -0.017897 | -0.0097669 | 0.011553 | -0.018311 | 0.13275 | -0.29755 | 0.054932 | 0.09613 | 0.13733 | -0.17395 | 0.26093 | 0.21515 | -0.27008 | 122.5159 | -0.050354 | 122.7951 | 122.8683 | -0.086975 | 122.5433 | 0.032044 | 0.27923 | 122.6395 | 123.0743 | 122.9095 | 122.9462 | 122.7951 | 123.0286 | 122.9507 | 122.5433 | 122.9462 | 122.7951 | 122.9507 | 122.9095 | 123.0286 | -0.48065 | -0.45319
3058.1406 | 123.0835 | -122.8088 | 0.19226 | 0.12291 | 0.011561 | -0.0075922 | 0.044728 | -0.016402 | -0.011903 | 0.013475 | -0.10529 | 0.17395 | -0.33875 | -0.022888 | -0.004578 | 0.032043 | -0.018311 | 0.14191 | 0.25177 | -0.30212 | 122.4701 | -0.018311 | 122.7036 | 122.7859 | -0.19684 | 122.5067 | 0.059509 | 0.23346 | 122.7905 | 122.9507 | 122.8043 | 122.9828 | 122.7036 | 123.0606 | 122.8409 | 122.5067 | 122.9828 | 122.7036 | 122.8409 | 122.8043 | 123.0606 | -0.53101 | -0.49438
3059.8906 | 123.0789 | -122.8134 | 0.1831 | 0.12291 | 0.012629 | -0.0041742 | 0.044728 | -0.016402 | -0.01169 | 0.01198 | -0.10071 | 0.16937 | -0.36163 | -0.013733 | -0.009155 | 0.022888 | -0.009155 | 0.14191 | 0.24261 | -0.31586 | 122.4518 | -0.013732 | 122.7127 | 122.7997 | -0.19226 | 122.4976 | 0.05951 | 0.26092 | 122.8043 | 122.9553 | 122.8043 | 122.9828 | 122.7127 | 123.056 | 122.8363 | 122.4976 | 122.9828 | 122.7127 | 122.8363 | 122.8043 | 123.056 | -0.54474 | -0.49896
3061.5781 | 123.1659 | -122.7905 | 0.16479 | 0.00083945 | 0.013057 | -0.0024652 | 0.038747 | -0.017684 | -0.0086987 | 0.012621 | -0.073242 | 0.15106 | -0.32959 | 0.027466 | 0.082397 | 0.10986 | -0.10071 | 0.24261 | 0.23346 | -0.28381 | 122.4609 | -0.013733 | 122.7173 | 122.818 | -0.082398 | 122.5067 | 0.068664 | 0.25635 | 122.6898 | 123.0331 | 122.8729 | 122.9416 | 122.7173 | 123.024 | 122.9004 | 122.5067 | 122.9416 | 122.7173 | 122.9004 | 122.8729 | 123.024 | -0.49438 | -0.44861
3063.3438 | 123.1659 | -122.7585 | 0.1831 | -0.25093 | 0.013057 | -0.002038 | 0.046224 | -0.018325 | -0.011476 | 0.012194 | -0.11902 | 0.1831 | -0.35706 | -0.022888 | -0.004578 | -0.004578 | 0.073242 | 0.16937 | 0.2655 | -0.32044 | 122.4014 | 0 | 122.6395 | 122.7356 | -0.18768 | 122.438 | 0.082398 | 0.23804 | 122.8317 | 122.9279 | 122.7539 | 122.9416 | 122.6395 | 123.024 | 122.7539 | 122.438 | 122.9416 | 122.6395 | 122.7539 | 122.7539 | 123.024 | -0.54016 | -0.50354
3065.1094 | 123.1613 | -122.7951 | 0.16479 | -0.25093 | 0.011134 | -0.003747 | 0.043233 | -0.01747 | -0.010194 | 0.0096301 | -0.10529 | 0.1831 | -0.35248 | -0.009155 | 0 | 0.009155 | 0.059509 | 0.17395 | 0.27008 | -0.31586 | 122.4426 | 0.01831 | 122.6898 | 122.7859 | -0.16479 | 122.4792 | 0.10529 | 0.24719 | 122.8546 | 122.9691 | 122.7951 | 122.9782 | 122.6898 | 123.0652 | 122.8043 | 122.4792 | 122.9782 | 122.6898 | 122.8043 | 122.7951 | 123.0652 | -0.51727 | -0.48065
3066.8594 | 123.1476 | -122.818 | 0.17395 | -0.21278 | 0.013057 | -0.0067376 | 0.04131 | -0.016188 | -0.0093395 | 0.011339 | -0.018311 | 0.14648 | -0.32501 | 0.068665 | 0.086975 | 0.11902 | -0.050354 | 0.27924 | 0.23346 | -0.27008 | 122.493 | -0.027466 | 122.7997 | 122.8867 | -0.086975 | 122.5479 | 0.059509 | 0.3067 | 122.7676 | 123.0972 | 122.905 | 122.9645 | 122.7997 | 123.0515 | 122.937 | 122.5479 | 122.9645 | 122.7997 | 122.937 | 122.905 | 123.0515 | -0.49896 | -0.44403
3068.5625 | 123.0377 | -122.8088 | 0.19226 | -0.083084 | 0.012416 | -0.0041742 | 0.048146 | -0.013411 | -0.015107 | 0.011553 | -0.022888 | 0.15106 | -0.3479 | 0.032043 | 0.032043 | 0.054932 | -0.027466 | 0.19684 | 0.27466 | -0.28839 | 122.4609 | -0.041199 | 122.7859 | 122.8409 | -0.16022 | 122.5204 | 0.082397 | 0.32501 | 122.7814 | 123.0057 | 122.8409 | 122.9599 | 122.7859 | 123.0835 | 122.8638 | 122.5204 | 122.9599 | 122.7859 | 122.8638 | 122.8409 | 123.0835 | -0.54016 | -0.48065
3070.3281 | 123.1796 | -122.7814 | 0.17395 | -0.19753 | 0.010921 | -0.0024652 | 0.042379 | -0.014266 | -0.013612 | 0.011553 | -0.082397 | 0.18768 | -0.3479 | -0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.18768 | 0.2655 | -0.31128 | 122.4335 | 0.013733 | 122.699 | 122.7631 | -0.15564 | 122.4701 | 0.091553 | 0.2655 | 122.8271 | 122.9691 | 122.7997 | 122.9691 | 122.699 | 123.0469 | 122.7951 | 122.4701 | 122.9691 | 122.699 | 122.7951 | 122.7997 | 123.0469 | -0.52185 | -0.48523
3072.0781 | 123.1293 | -122.8226 | 0.16937 | -0.20515 | 0.011348 | -0.0033196 | 0.041951 | -0.017897 | -0.0091259 | 0.010271 | 0.004578 | 0.15564 | -0.3067 | 0.068665 | 0.11444 | 0.11902 | -0.086975 | 0.30212 | 0.23346 | -0.28381 | 122.5159 | -0.013733 | 122.8271 | 122.8912 | -0.054932 | 122.5388 | 0.064086 | 0.31128 | 122.7356 | 123.1247 | 122.937 | 122.9782 | 122.8271 | 123.056 | 122.9416 | 122.5388 | 122.9782 | 122.8271 | 122.9416 | 122.937 | 123.056 | -0.47607 | -0.45319
3073.8281 | 123.1338 | -122.7905 | 0.16022 | -0.067826 | 0.012202 | -0.00011543 | 0.038106 | -0.01747 | -0.01169 | 0.011766 | -0.009155 | 0.13733 | -0.32501 | 0.082397 | 0.11444 | 0.14191 | -0.11902 | 0.31586 | 0.23804 | -0.27924 | 122.4655 | -0.022888 | 122.7814 | 122.8729 | -0.045776 | 122.5113 | 0.07782 | 0.31586 | 122.6715 | 123.1064 | 122.905 | 122.9279 | 122.7814 | 123.0286 | 122.9324 | 122.5113 | 122.9279 | 122.7814 | 122.9324 | 122.905 | 123.0286 | -0.48523 | -0.43945
3075.5312 | 123.111 | -122.8134 | 0.18768 | -0.20515 | 0.013057 | -0.0039606 | 0.043447 | -0.017043 | -0.010621 | 0.0096301 | 0.013733 | 0.13733 | -0.31128 | 0.10529 | 0.11444 | 0.13733 | -0.11444 | 0.3067 | 0.21515 | -0.28381 | 122.5021 | -0.050354 | 122.8271 | 122.9187 | -0.073242 | 122.5296 | 0.027466 | 0.32501 | 122.699 | 123.1201 | 122.9279 | 122.9507 | 122.8271 | 123.0286 | 122.9507 | 122.5296 | 122.9507 | 122.8271 | 122.9507 | 122.9279 | 123.0286 | -0.49896 | -0.4715
3077.2812 | 123.0377 | -122.8226 | 0.21515 | -0.075455 | 0.012416 | -0.0050286 | 0.049215 | -0.014907 | -0.014467 | 0.010912 | -0.032043 | 0.16022 | -0.3479 | 0.041199 | 0.004578 | 0.041199 | -0.032043 | 0.21515 | 0.25635 | -0.27008 | 122.4747 | -0.054932 | 122.7905 | 122.8638 | -0.21057 | 122.5525 | 0.041199 | 0.31586 | 122.7905 | 123.0377 | 122.8271 | 122.9828 | 122.7905 | 123.0789 | 122.8638 | 122.5525 | 122.9828 | 122.7905 | 122.8638 | 122.8271 | 123.0789 | -0.56305 | -0.48523
3078.9688 | 123.0881 | -122.8088 | 0.1831 | -0.12886 | 0.013057 | -0.0039606 | 0.045583 | -0.015334 | -0.014467 | 0.013903 | -0.054932 | 0.16937 | -0.3479 | 0.027466 | 0.027466 | 0.036621 | -0.013733 | 0.20142 | 0.25177 | -0.3067 | 122.4609 | -0.013732 | 122.7539 | 122.8363 | -0.15564 | 122.5021 | 0.068665 | 0.29297 | 122.7951 | 123.0103 | 122.8363 | 122.9782 | 122.7539 | 123.0606 | 122.8455 | 122.5021 | 122.9782 | 122.7539 | 122.8455 | 122.8363 | 123.0606 | -0.531 | -0.48981
3080.7188 | 123.0194 | -122.8226 | 0.19684 | 0.20683 | 0.010066 | -0.0097284 | 0.045583 | -0.014479 | -0.01233 | 0.014116 | -0.013733 | 0.14191 | -0.32044 | 0.068665 | 0.086975 | 0.13275 | -0.16479 | 0.25635 | 0.2243 | -0.27008 | 122.5021 | -0.054931 | 122.8088 | 122.8912 | -0.10986 | 122.5525 | 0.027466 | 0.3067 | 122.6578 | 123.0789 | 122.9095 | 122.9645 | 122.8088 | 123.0469 | 122.9553 | 122.5525 | 122.9645 | 122.8088 | 122.9553 | 122.9095 | 123.0469 | -0.51727 | -0.46692
3082.4062 | 123.1567 | -122.7722 | 0.16022 | 0.054245 | 0.012202 | -0.0035332 | 0.037679 | -0.017043 | -0.0084851 | 0.013262 | -0.07782 | 0.16022 | -0.3067 | 0.022888 | 0.068665 | 0.086975 | -0.09613 | 0.22888 | 0.22888 | -0.28839 | 122.4655 | 0 | 122.6944 | 122.7951 | -0.091552 | 122.4838 | 0.068665 | 0.22888 | 122.6761 | 123.0011 | 122.8409 | 122.9324 | 122.6944 | 123.0011 | 122.8592 | 122.4838 | 122.9324 | 122.6944 | 122.8592 | 122.8409 | 123.0011 | -0.46692 | -0.44861
3084.1562 | 123.1613 | -122.7997 | 0.16022 | -0.01442 | 0.011775 | -0.006524 | 0.040883 | -0.019179 | -0.0095531 | 0.010698 | -0.059509 | 0.15106 | -0.31128 | 0.045776 | 0.073242 | 0.10529 | -0.10529 | 0.25177 | 0.22888 | -0.28381 | 122.4884 | -0.009155 | 122.7402 | 122.8455 | -0.086975 | 122.5159 | 0.068665 | 0.25177 | 122.6944 | 123.0515 | 122.8729 | 122.9507 | 122.7402 | 123.0286 | 122.905 | 122.5159 | 122.9507 | 122.7402 | 122.905 | 122.8729 | 123.0286 | -0.4715 | -0.44403
3085.8594 | 123.175 | -122.7722 | 0.16937 | -0.25856 | 0.012843 | -0.0078058 | 0.043019 | -0.017897 | -0.010408 | 0.011553 | -0.054932 | 0.14191 | -0.33875 | 0.013733 | 0.032043 | 0.045776 | 0.013733 | 0.19684 | 0.25177 | -0.29755 | 122.4335 | -0.027466 | 122.7173 | 122.7859 | -0.13733 | 122.4747 | 0.082397 | 0.28381 | 122.7859 | 122.9691 | 122.8043 | 122.9141 | 122.7173 | 123.024 | 122.818 | 122.4747 | 122.9141 | 122.7173 | 122.818 | 122.8043 | 123.024 | -0.50812 | -0.46692
3087.6094 | 123.143 | -122.7951 | 0.16937 | -0.075455 | 0.012416 | -0.0071648 | 0.04067 | -0.018111 | -0.011262 | 0.0096301 | -0.022888 | 0.14191 | -0.33417 | 0.068665 | 0.09613 | 0.1236 | -0.1236 | 0.29755 | 0.21057 | -0.27008 | 122.4609 | -0.027466 | 122.7722 | 122.8638 | -0.073243 | 122.525 | 0.041198 | 0.31128 | 122.6715 | 123.0927 | 122.8912 | 122.937 | 122.7722 | 123.0057 | 122.9187 | 122.525 | 122.937 | 122.7722 | 122.9187 | 122.8912 | 123.0057 | -0.50354 | -0.43945
3089.2969 | 123.1293 | -122.7951 | 0.16937 | -0.16701 | 0.011348 | -0.0084466 | 0.043019 | -0.018325 | -0.010621 | 0.0092029 | -0.009155 | 0.13733 | -0.31586 | 0.10071 | 0.13275 | 0.14191 | -0.14648 | 0.32501 | 0.21057 | -0.27924 | 122.4792 | -0.032044 | 122.7859 | 122.8958 | -0.036622 | 122.5159 | 0.041198 | 0.3067 | 122.6486 | 123.1201 | 122.9279 | 122.9324 | 122.7859 | 123.0057 | 122.937 | 122.5159 | 122.9324 | 122.7859 | 122.937 | 122.9279 | 123.0057 | -0.48523 | -0.44861
3091.0469 | 123.175 | -122.7997 | 0.18768 | -0.25093 | 0.0096387 | -0.0039606 | 0.042806 | -0.017897 | -0.011049 | 0.0096301 | -0.054932 | 0.15564 | -0.34332 | 0.004578 | 0.032043 | 0.032043 | 0.018311 | 0.19684 | 0.25177 | -0.31128 | 122.4564 | -0.032043 | 122.7448 | 122.8043 | -0.15564 | 122.4884 | 0.064087 | 0.28839 | 122.818 | 122.9965 | 122.8317 | 122.9553 | 122.7448 | 123.0515 | 122.8317 | 122.4884 | 122.9553 | 122.7448 | 122.8317 | 122.8317 | 123.0515 | -0.53101 | -0.49896
3092.7969 | 123.1567 | -122.7905 | 0.17853 | -0.18227 | 0.012202 | -0.0018244 | 0.045797 | -0.018325 | -0.010835 | 0.010485 | -0.07782 | 0.18768 | -0.37537 | 0.004578 | 0.004578 | 0.022888 | 0.045776 | 0.19684 | 0.25177 | -0.30212 | 122.4152 | 0.009155 | 122.7127 | 122.7951 | -0.17395 | 122.4884 | 0.073242 | 0.29755 | 122.8363 | 122.9874 | 122.7951 | 122.9782 | 122.7127 | 123.0423 | 122.8134 | 122.4884 | 122.9782 | 122.7127 | 122.8134 | 122.7951 | 123.0423 | -0.55389 | -0.48065
3094.5625 | 123.0469 | -122.8592 | 0.20142 | -0.090714 | 0.01028 | -0.0073786 | 0.047719 | -0.014693 | -0.014894 | 0.013262 | -0.045776 | 0.16022 | -0.3479 | 0.054932 | 0.041199 | 0.068665 | -0.036621 | 0.21515 | 0.25635 | -0.28381 | 122.5113 | -0.041199 | 122.8134 | 122.9141 | -0.16022 | 122.5754 | 0.054932 | 0.30212 | 122.8226 | 123.0743 | 122.9004 | 123.0194 | 122.8134 | 123.1155 | 122.9279 | 122.5754 | 123.0194 | 122.8134 | 122.9279 | 122.9004 | 123.1155 | -0.54932 | -0.48523
3096.2656 | 123.1522 | -122.7539 | 0.16479 | -0.26619 | 0.010921 | -0.0022516 | 0.043019 | -0.017684 | -0.011049 | 0.011766 | -0.054932 | 0.16937 | -0.32501 | 0.027466 | 0.032043 | 0.036621 | 0.009155 | 0.21515 | 0.25635 | -0.28839 | 122.4289 | 0.004578 | 122.699 | 122.7814 | -0.13275 | 122.4655 | 0.091553 | 0.27008 | 122.7631 | 122.9691 | 122.7859 | 122.9233 | 122.699 | 123.0103 | 122.7905 | 122.4655 | 122.9233 | 122.699 | 122.7905 | 122.7859 | 123.0103 | -0.48981 | -0.45319
3098.0156 | 123.0515 | -122.8455 | 0.18768 | -0.10597 | 0.011561 | -0.0035332 | 0.044942 | -0.015975 | -0.01233 | 0.012407 | -0.036621 | 0.15564 | -0.34332 | 0.045776 | 0.045776 | 0.064087 | -0.050354 | 0.21973 | 0.24719 | -0.29755 | 122.5021 | -0.032043 | 122.8088 | 122.8912 | -0.14191 | 122.5479 | 0.059509 | 0.3067 | 122.7951 | 123.0652 | 122.8912 | 123.0011 | 122.8088 | 123.0927 | 122.9095 | 122.5479 | 123.0011 | 122.8088 | 122.9095 | 122.8912 | 123.0927 | -0.53101 | -0.48523
3099.7656 | 123.0835 | -122.818 | 0.20142 | 0.10002 | 0.011775 | -0.003747 | 0.046865 | -0.017897 | -0.013612 | 0.012835 | -0.07782 | 0.16479 | -0.37537 | -0.022888 | -0.022888 | 0.004578 | 0.022888 | 0.13733 | 0.26093 | -0.30212 | 122.4426 | -0.036621 | 122.7402 | 122.7951 | -0.2243 | 122.5159 | 0.059509 | 0.29755 | 122.8409 | 122.9553 | 122.7951 | 122.9828 | 122.7402 | 123.0789 | 122.8226 | 122.5159 | 122.9828 | 122.7402 | 122.8226 | 122.7951 | 123.0789 | -0.57678 | -0.50354
3101.5312 | 123.0881 | -122.8134 | 0.1831 | 0.13817 | 0.012416 | -0.00011543 | 0.046437 | -0.014907 | -0.0084851 | 0.011339 | -0.10071 | 0.17853 | -0.35706 | -0.032043 | -0.009155 | 0.004578 | -0.022888 | 0.1236 | 0.24261 | -0.30212 | 122.4564 | -0.004577 | 122.7127 | 122.7814 | -0.19226 | 122.5113 | 0.05951 | 0.25635 | 122.7905 | 122.937 | 122.8043 | 122.9919 | 122.7127 | 123.056 | 122.818 | 122.5113 | 122.9919 | 122.7127 | 122.818 | 122.8043 | 123.056 | -0.54016 | -0.48523
3103.2188 | 123.1293 | -122.7905 | 0.16022 | -0.075455 | 0.010921 | -0.0063104 | 0.037252 | -0.019179 | -0.011049 | 0.011766 | -0.064087 | 0.14191 | -0.32959 | 0.073242 | 0.11902 | 0.14191 | -0.11444 | 0.28839 | 0.21515 | -0.28381 | 122.4609 | -0.01831 | 122.7264 | 122.8638 | -0.041198 | 122.5067 | 0.054932 | 0.2655 | 122.6761 | 123.0789 | 122.9095 | 122.9324 | 122.7264 | 123.0057 | 122.9324 | 122.5067 | 122.9324 | 122.7264 | 122.9324 | 122.9095 | 123.0057 | -0.48981 | -0.44403
3104.9688 | 123.1476 | -122.7951 | 0.17853 | -0.25856 | 0.01028 | -0.004815 | 0.042806 | -0.020247 | -0.011903 | 0.010271 | -0.045776 | 0.15564 | -0.32501 | 0.027466 | 0.059509 | 0.059509 | 0 | 0.2243 | 0.25177 | -0.27466 | 122.4701 | -0.022888 | 122.7493 | 122.8226 | -0.11902 | 122.5204 | 0.073242 | 0.27924 | 122.7951 | 123.0194 | 122.8546 | 122.9507 | 122.7493 | 123.0469 | 122.8546 | 122.5204 | 122.9507 | 122.7493 | 122.8546 | 122.8546 | 123.0469 | -0.50354 | -0.45319
3106.7344 | 123.1613 | -122.7814 | 0.16022 | -0.022049 | 0.011989 | -0.0035332 | 0.040029 | -0.016829 | -0.010408 | 0.013262 | -0.045776 | 0.15106 | -0.3479 | 0.036621 | 0.07782 | 0.10529 | -0.10986 | 0.2655 | 0.2243 | -0.2655 | 122.4335 | -0.009155 | 122.7356 | 122.818 | -0.082397 | 122.5159 | 0.064087 | 0.30212 | 122.6715 | 123.0469 | 122.8592 | 122.9324 | 122.7356 | 123.0057 | 122.8867 | 122.5159 | 122.9324 | 122.7356 | 122.8867 | 122.8592 | 123.0057 | -0.50812 | -0.42572
3108.5 | 123.0835 | -122.8043 | 0.19684 | 0.13054 | 0.012416 | -0.0035332 | 0.047933 | -0.013839 | -0.011903 | 0.013475 | -0.11444 | 0.16937 | -0.37537 | -0.018311 | -0.022888 | 0.009155 | 0 | 0.1236 | 0.2655 | -0.29297 | 122.4289 | -0.027465 | 122.6898 | 122.7859 | -0.21973 | 122.5113 | 0.068665 | 0.26092 | 122.8043 | 122.9279 | 122.7814 | 122.9736 | 122.6898 | 123.0698 | 122.8134 | 122.5113 | 122.9736 | 122.6898 | 122.8134 | 122.7814 | 123.0698 | -0.5722 | -0.48981
3110.1875 | 123.1064 | -122.8134 | 0.1831 | 0.084762 | 0.012629 | -0.0073786 | 0.042379 | -0.016402 | -0.0099805 | 0.012835 | -0.036621 | 0.14648 | -0.32044 | 0.036621 | 0.07782 | 0.10071 | -0.12817 | 0.24261 | 0.22888 | -0.27466 | 122.493 | -0.036621 | 122.7768 | 122.85 | -0.10528 | 122.5388 | 0.045777 | 0.28381 | 122.6852 | 123.056 | 122.8912 | 122.9599 | 122.7768 | 123.0423 | 122.9141 | 122.5388 | 122.9599 | 122.7768 | 122.9141 | 122.8912 | 123.0423 | -0.50354 | -0.45776
3111.9531 | 123.1567 | -122.7905 | 0.16479 | -0.17464 | 0.013057 | -0.0046014 | 0.046865 | -0.016616 | -0.012758 | 0.011126 | -0.10071 | 0.1831 | -0.37994 | 0.009155 | 0.009155 | 0.013733 | 0.041199 | 0.18768 | 0.26093 | -0.27924 | 122.4106 | 0.01831 | 122.6898 | 122.7997 | -0.15564 | 122.5113 | 0.09613 | 0.27924 | 122.8317 | 122.9782 | 122.7997 | 122.9736 | 122.6898 | 123.0515 | 122.8043 | 122.5113 | 122.9736 | 122.6898 | 122.8043 | 122.7997 | 123.0515 | -0.54474 | -0.44403
3113.7188 | 123.1293 | -122.7997 | 0.16937 | -0.14412 | 0.010493 | -0.0043878 | 0.039174 | -0.017256 | -0.013399 | 0.010057 | 0.004578 | 0.13733 | -0.3067 | 0.09613 | 0.11902 | 0.15106 | -0.16022 | 0.32044 | 0.21515 | -0.2655 | 122.493 | -0.032044 | 122.8043 | 122.8958 | -0.050354 | 122.5342 | 0.045776 | 0.31128 | 122.6395 | 123.1201 | 122.9187 | 122.937 | 122.8043 | 123.0148 | 122.9507 | 122.5342 | 122.937 | 122.8043 | 122.9507 | 122.9187 | 123.0148 | -0.47607 | -0.43488
3115.4219 | 123.1567 | -122.7905 | 0.16479 | 0.023727 | 0.013911 | -0.0056696 | 0.041738 | -0.016829 | -0.010194 | 0.010912 | -0.059509 | 0.15564 | -0.32044 | 0.036621 | 0.064087 | 0.09613 | -0.086975 | 0.22888 | 0.21973 | -0.28839 | 122.4701 | -0.009155 | 122.731 | 122.8271 | -0.10071 | 122.5021 | 0.054932 | 0.26093 | 122.7036 | 123.0194 | 122.8546 | 122.9462 | 122.731 | 123.0103 | 122.8867 | 122.5021 | 122.9462 | 122.731 | 122.8867 | 122.8546 | 123.0103 | -0.48523 | -0.45319
3117.1875 | 123.0469 | -122.8363 | 0.20599 | -0.044937 | 0.011561 | -0.003747 | 0.05071 | -0.014479 | -0.011476 | 0.0096301 | -0.041199 | 0.16022 | -0.36163 | 0.027466 | 0.013733 | 0.022888 | -0.013733 | 0.19226 | 0.27466 | -0.28381 | 122.4747 | -0.045777 | 122.7951 | 122.8638 | -0.19226 | 122.5525 | 0.068664 | 0.32043 | 122.8226 | 123.0286 | 122.85 | 122.9965 | 122.7951 | 123.111 | 122.8592 | 122.5525 | 122.9965 | 122.7951 | 122.8592 | 122.85 | 123.111 | -0.56763 | -0.48981
3118.9531 | 123.0927 | -122.8271 | 0.20142 | 0.16106 | 0.012202 | 0.0011664 | 0.046224 | -0.015975 | -0.012117 | 0.012621 | -0.091553 | 0.17395 | -0.36621 | -0.032043 | -0.022888 | 0.004578 | -0.013733 | 0.13275 | 0.26093 | -0.32044 | 122.4609 | -0.027466 | 122.7356 | 122.7951 | -0.2243 | 122.5067 | 0.059509 | 0.27466 | 122.8134 | 122.9599 | 122.8043 | 123.0011 | 122.7356 | 123.0881 | 122.8317 | 122.5067 | 123.0011 | 122.7356 | 122.8317 | 122.8043 | 123.0881 | -0.56763 | -0.52185
3120.7031 | 123.0469 | -122.8455 | 0.21057 | 0.17632 | 0.014338 | 0.0024482 | 0.040883 | -0.016402 | -0.011903 | 0.011553 | 0 | 0.12817 | -0.30212 | 0.091553 | 0.10986 | 0.14648 | -0.19226 | 0.27924 | 0.21057 | -0.26093 | 122.5433 | -0.082397 | 122.8455 | 122.937 | -0.10071 | 122.5845 | 0 | 0.30212 | 122.6532 | 123.1247 | 122.9553 | 122.9736 | 122.8455 | 123.056 | 122.9919 | 122.5845 | 122.9736 | 122.8455 | 122.9919 | 122.9553 | 123.056 | -0.5127 | -0.4715
3122.4688 | 123.1705 | -122.7951 | 0.17853 | -0.2433 | 0.011561 | -0.0071648 | 0.043447 | -0.017256 | -0.0086987 | 0.011553 | -0.12817 | 0.17395 | -0.37079 | -0.032043 | 0.013733 | -0.009155 | 0.073242 | 0.16022 | 0.27466 | -0.29297 | 122.4243 | -0.004578 | 122.6669 | 122.7631 | -0.16479 | 122.5021 | 0.09613 | 0.24261 | 122.8683 | 122.9553 | 122.8088 | 122.9691 | 122.6669 | 123.0698 | 122.7859 | 122.5021 | 122.9691 | 122.6669 | 122.7859 | 122.8088 | 123.0698 | -0.54932 | -0.4715
3124.1719 | 123.1979 | -122.7768 | 0.17395 | -0.2433 | 0.011134 | -0.0069512 | 0.044301 | -0.016402 | -0.012117 | 0.013048 | -0.1236 | 0.17853 | -0.36163 | -0.032043 | 0 | 0.009155 | 0.073242 | 0.17395 | 0.27008 | -0.3067 | 122.4152 | 0.004578 | 122.6532 | 122.7448 | -0.17395 | 122.4701 | 0.096131 | 0.23804 | 122.85 | 122.9507 | 122.7768 | 122.9553 | 122.6532 | 123.0469 | 122.7859 | 122.4701 | 122.9553 | 122.6532 | 122.7859 | 122.7768 | 123.0469 | -0.53558 | -0.48065
3125.9375 | 123.056 | -122.8455 | 0.19226 | -0.0067901 | 0.013911 | -0.0073786 | 0.048787 | -0.016402 | -0.012544 | 0.010698 | -0.068665 | 0.16937 | -0.36163 | 0.004578 | 0.018311 | 0.013733 | -0.009155 | 0.15564 | 0.25177 | -0.28839 | 122.4838 | -0.022888 | 122.7768 | 122.85 | -0.17395 | 122.5571 | 0.059509 | 0.29297 | 122.8363 | 123.0011 | 122.8638 | 123.0148 | 122.7768 | 123.0972 | 122.8592 | 122.5571 | 123.0148 | 122.7768 | 122.8592 | 122.8638 | 123.0972 | -0.55389 | -0.48065
3127.7031 | 123.0423 | -122.85 | 0.21515 | -0.10597 | 0.013057 | -0.0054558 | 0.047719 | -0.014907 | -0.011476 | 0.012835 | -0.022888 | 0.16022 | -0.34332 | 0.032043 | 0.041199 | 0.064087 | -0.041199 | 0.20599 | 0.26093 | -0.29297 | 122.5067 | -0.054932 | 122.8271 | 122.8821 | -0.17395 | 122.5571 | 0.045776 | 0.32043 | 122.8088 | 123.056 | 122.8912 | 123.0103 | 122.8271 | 123.111 | 122.9141 | 122.5571 | 123.0103 | 122.8271 | 122.9141 | 122.8912 | 123.111 | -0.55847 | -0.50812
3129.4062 | 123.0698 | -122.8363 | 0.20599 | -0.029679 | 0.011561 | -0.003747 | 0.045583 | -0.015334 | -0.012117 | 0.011339 | -0.064087 | 0.15106 | -0.35706 | 0 | 0.013733 | 0.036621 | -0.009155 | 0.15564 | 0.27008 | -0.29755 | 122.4792 | -0.054932 | 122.7722 | 122.8363 | -0.19226 | 122.5388 | 0.064087 | 0.29297 | 122.8271 | 122.9919 | 122.85 | 122.9874 | 122.7722 | 123.1064 | 122.8729 | 122.5388 | 122.9874 | 122.7722 | 122.8729 | 122.85 | 123.1064 | -0.56305 | -0.50354
3131.1719 | 123.1705 | -122.8088 | 0.16937 | -0.23567 | 0.01327 | -0.010156 | 0.03832 | -0.017256 | -0.012758 | 0.011553 | -0.12817 | 0.18768 | -0.36163 | -0.036621 | 0.018311 | 0 | 0.073242 | 0.16479 | 0.2655 | -0.32044 | 122.4472 | 0.01831 | 122.6807 | 122.7722 | -0.15106 | 122.4884 | 0.09613 | 0.23346 | 122.8821 | 122.9736 | 122.8271 | 122.9965 | 122.6807 | 123.0743 | 122.8088 | 122.4884 | 122.9965 | 122.6807 | 122.8088 | 122.8271 | 123.0743 | -0.53101 | -0.48981
3132.9375 | 123.056 | -122.8226 | 0.21973 | 0.16869 | 0.012202 | 0.0011664 | 0.042165 | -0.016402 | -0.0095531 | 0.013048 | -0.009155 | 0.1236 | -0.31586 | 0.086975 | 0.09613 | 0.14648 | -0.18768 | 0.27466 | 0.21057 | -0.27466 | 122.5067 | -0.096131 | 122.8134 | 122.9095 | -0.1236 | 122.5479 | -0.009156 | 0.3067 | 122.6349 | 123.0972 | 122.9187 | 122.9462 | 122.8134 | 123.0331 | 122.9691 | 122.5479 | 122.9462 | 122.8134 | 122.9691 | 122.9187 | 123.0331 | -0.53558 | -0.49439
3134.6875 | 123.0606 | -122.8729 | 0.21515 | -0.10597 | 0.011134 | -0.0026788 | 0.044301 | -0.017256 | -0.01233 | 0.011766 | -0.050354 | 0.15106 | -0.35706 | 0.022888 | 0.041199 | 0.068665 | -0.009155 | 0.22888 | 0.25635 | -0.3067 | 122.5159 | -0.064087 | 122.8226 | 122.8958 | -0.17395 | 122.5662 | 0.041199 | 0.3067 | 122.8638 | 123.1018 | 122.9141 | 123.024 | 122.8226 | 123.1293 | 122.9416 | 122.5662 | 123.024 | 122.8226 | 122.9416 | 122.9141 | 123.1293 | -0.5722 | -0.52185
3136.4531 | 123.1659 | -122.7722 | 0.16479 | -0.01442 | 0.012202 | -0.0084466 | 0.040242 | -0.018752 | -0.0072033 | 0.010912 | -0.068665 | 0.14191 | -0.32044 | 0.041199 | 0.07782 | 0.11444 | -0.11444 | 0.27924 | 0.21515 | -0.28839 | 122.4518 | -0.022888 | 122.7036 | 122.8134 | -0.086975 | 122.4838 | 0.050354 | 0.25177 | 122.6578 | 123.0515 | 122.85 | 122.9141 | 122.7036 | 122.9874 | 122.8867 | 122.4838 | 122.9141 | 122.7036 | 122.8867 | 122.85 | 122.9874 | -0.48523 | -0.45319
3138.1562 | 123.1476 | -122.7814 | 0.16937 | -0.22041 | 0.011561 | -0.0043878 | 0.041524 | -0.018111 | -0.012117 | 0.01198 | -0.013733 | 0.14191 | -0.32959 | 0.073242 | 0.091553 | 0.1236 | -0.073242 | 0.30212 | 0.21973 | -0.27466 | 122.4518 | -0.027466 | 122.7676 | 122.8546 | -0.07782 | 122.5067 | 0.050354 | 0.31586 | 122.7081 | 123.0835 | 122.8729 | 122.9233 | 122.7676 | 123.0011 | 122.905 | 122.5067 | 122.9233 | 122.7676 | 122.905 | 122.8729 | 123.0011 | -0.49896 | -0.44403
3139.9062 | 123.0743 | -122.7997 | 0.20599 | 0.13054 | 0.010493 | -0.0071648 | 0.042379 | -0.016616 | -0.010621 | 0.012835 | -0.045776 | 0.1236 | -0.32501 | 0.045776 | 0.059509 | 0.10986 | -0.14191 | 0.25177 | 0.21515 | -0.26093 | 122.4747 | -0.082398 | 122.7539 | 122.8455 | -0.14649 | 122.5388 | 0.009155 | 0.27924 | 122.6578 | 123.0515 | 122.8592 | 122.9233 | 122.7539 | 123.0148 | 122.9095 | 122.5388 | 122.9233 | 122.7539 | 122.9095 | 122.8592 | 123.0148 | -0.53101 | -0.46692
3141.6562 | 123.0469 | -122.8134 | 0.20142 | 0.1992 | 0.013698 | 0.0035162 | 0.046651 | -0.017897 | -0.013399 | 0.010485 | -0.054932 | 0.17853 | -0.35706 | 0.027466 | 0.032043 | 0.050354 | -0.10529 | 0.19226 | 0.23804 | -0.29297 | 122.4564 | -0.022888 | 122.7585 | 122.8409 | -0.16937 | 122.5204 | 0.036621 | 0.30212 | 122.7081 | 123.0057 | 122.8455 | 122.9919 | 122.7585 | 123.0515 | 122.8638 | 122.5204 | 122.9919 | 122.7585 | 122.8638 | 122.8455 | 123.0515 | -0.55847 | -0.49438
3143.4219 | 123.0881 | -122.818 | 0.1831 | 0.16869 | 0.013911 | -0.0075922 | 0.04836 | -0.016188 | -0.01233 | 0.01198 | -0.086975 | 0.16479 | -0.36621 | -0.018311 | -0.009155 | 0.009155 | 0 | 0.13275 | 0.27466 | -0.31128 | 122.4518 | -0.01831 | 122.731 | 122.7997 | -0.19226 | 122.5067 | 0.091553 | 0.27924 | 122.818 | 122.9507 | 122.8088 | 122.9828 | 122.731 | 123.0927 | 122.8271 | 122.5067 | 122.9828 | 122.731 | 122.8271 | 122.8088 | 123.0927 | -0.54932 | -0.49438
3145.1875 | 123.0835 | -122.8317 | 0.19684 | 0.084762 | 0.010921 | -0.0011834 | 0.044301 | -0.014052 | -0.012544 | 0.010912 | -0.11902 | 0.17395 | -0.3479 | -0.022888 | -0.018311 | 0 | -0.004578 | 0.12817 | 0.25177 | -0.28381 | 122.4838 | -0.022888 | 122.7127 | 122.8088 | -0.21515 | 122.5479 | 0.054932 | 0.22888 | 122.8271 | 122.9599 | 122.8134 | 123.0057 | 122.7127 | 123.0835 | 122.8317 | 122.5479 | 123.0057 | 122.7127 | 122.8317 | 122.8134 | 123.0835 | -0.54474 | -0.48065
3146.8906 | 123.1705 | -122.7951 | 0.16479 | 0.023727 | 0.013057 | -0.0046014 | 0.038106 | -0.015975 | -0.0097669 | 0.010698 | -0.082397 | 0.15106 | -0.31586 | 0.013733 | 0.068665 | 0.07782 | -0.10071 | 0.24719 | 0.24261 | -0.29297 | 122.4792 | -0.013733 | 122.7127 | 122.8088 | -0.09613 | 122.5021 | 0.07782 | 0.23346 | 122.6944 | 123.0423 | 122.8638 | 122.9462 | 122.7127 | 123.0377 | 122.8729 | 122.5021 | 122.9462 | 122.7127 | 122.8729 | 122.8638 | 123.0377 | -0.48065 | -0.45776
3148.6406 | 123.0377 | -122.8455 | 0.21057 | -0.052567 | 0.011989 | -0.003106 | 0.047078 | -0.017043 | -0.012544 | 0.010057 | -0.050354 | 0.15564 | -0.35706 | 0.022888 | 0.013733 | 0.032043 | -0.027466 | 0.1831 | 0.24719 | -0.30212 | 122.4884 | -0.054931 | 122.7951 | 122.8683 | -0.19684 | 122.5433 | 0.036621 | 0.3067 | 122.818 | 123.0286 | 122.8592 | 123.0011 | 122.7951 | 123.0927 | 122.8775 | 122.5433 | 123.0011 | 122.7951 | 122.8775 | 122.8592 | 123.0927 | -0.56763 | -0.5127
3150.4062 | 123.0789 | -122.8317 | 0.19226 | 0.031357 | 0.014338 | -0.0050286 | 0.045369 | -0.015761 | -0.010621 | 0.010912 | -0.10986 | 0.1831 | -0.36163 | -0.041199 | -0.032043 | -0.022888 | 0.018311 | 0.10986 | 0.24719 | -0.3067 | 122.4701 | -0.009156 | 122.7219 | 122.7905 | -0.2243 | 122.525 | 0.054931 | 0.25177 | 122.85 | 122.9416 | 122.7997 | 123.0148 | 122.7219 | 123.0789 | 122.8088 | 122.525 | 123.0148 | 122.7219 | 122.8088 | 122.7997 | 123.0789 | -0.55389 | -0.49896
3152.1094 | 123.0972 | -122.8088 | 0.18768 | -0.14412 | 0.013057 | -0.006524 | 0.045369 | -0.018325 | -0.0095531 | 0.012407 | -0.073242 | 0.16937 | -0.35706 | 0.013733 | 0.041199 | 0.050354 | 0.009155 | 0.21515 | 0.23804 | -0.29755 | 122.4518 | -0.01831 | 122.7356 | 122.8226 | -0.14648 | 122.5113 | 0.050354 | 0.28381 | 122.818 | 123.024 | 122.85 | 122.9782 | 122.7356 | 123.0469 | 122.8592 | 122.5113 | 122.9782 | 122.7356 | 122.8592 | 122.85 | 123.0469 | -0.54474 | -0.48523
3153.8438 | 123.0789 | -122.8088 | 0.21057 | 0.13054 | 0.01327 | -0.0088738 | 0.044728 | -0.016188 | -0.01169 | 0.012835 | -0.11902 | 0.17853 | -0.37537 | -0.045776 | -0.032043 | 0.009155 | -0.009155 | 0.1236 | 0.25635 | -0.31586 | 122.4335 | -0.032043 | 122.6898 | 122.7631 | -0.24261 | 122.493 | 0.045777 | 0.25635 | 122.7997 | 122.9324 | 122.7768 | 122.9874 | 122.6898 | 123.0652 | 122.818 | 122.493 | 122.9874 | 122.6898 | 122.818 | 122.7768 | 123.0652 | -0.58594 | -0.52643
3155.5938 | 123.1247 | -122.8043 | 0.19226 | -0.1899 | 0.010707 | -0.0024652 | 0.043874 | -0.012557 | -0.010835 | 0.011339 | -0.091553 | 0.19684 | -0.35248 | 0.004578 | 0.036621 | 0.045776 | 0.009155 | 0.20142 | 0.26093 | -0.31128 | 122.4518 | 0.004577 | 122.7127 | 122.8088 | -0.15564 | 122.493 | 0.068664 | 0.26093 | 122.8134 | 123.0057 | 122.8409 | 123.0011 | 122.7127 | 123.0652 | 122.85 | 122.493 | 123.0011 | 122.7127 | 122.85 | 122.8409 | 123.0652 | -0.54474 | -0.50354
3157.3438 | 123.0835 | -122.8546 | 0.20599 | 0.084762 | 0.010707 | -0.0060968 | 0.044728 | -0.014907 | -0.014253 | 0.012621 | -0.10986 | 0.17853 | -0.35248 | -0.032043 | -0.013733 | -0.004578 | 0.022888 | 0.13275 | 0.27466 | -0.30212 | 122.5021 | -0.027466 | 122.7448 | 122.8226 | -0.21973 | 122.5525 | 0.068664 | 0.24262 | 122.8775 | 122.9874 | 122.8409 | 123.0331 | 122.7448 | 123.1293 | 122.85 | 122.5525 | 123.0331 | 122.7448 | 122.85 | 122.8409 | 123.1293 | -0.55847 | -0.50812
3159.0938 | 123.0469 | -122.8134 | 0.19226 | 0.18394 | 0.012629 | -0.0024652 | 0.039815 | -0.014907 | -0.0097669 | 0.011126 | 0.004578 | 0.13733 | -0.32044 | 0.07782 | 0.10529 | 0.15564 | -0.19684 | 0.27008 | 0.21057 | -0.26093 | 122.493 | -0.054932 | 122.818 | 122.8912 | -0.086975 | 122.5525 | 0.01831 | 0.32501 | 122.6166 | 123.0835 | 122.9187 | 122.9507 | 122.818 | 123.024 | 122.9691 | 122.5525 | 122.9507 | 122.818 | 122.9691 | 122.9187 | 123.024 | -0.5127 | -0.45319
3160.8438 | 123.1476 | -122.8043 | 0.17395 | -0.20515 | 0.012202 | -0.0028924 | 0.045583 | -0.016829 | -0.011476 | 0.01198 | -0.086975 | 0.1831 | -0.36163 | 0.004578 | 0.022888 | 0.036621 | 0.022888 | 0.21515 | 0.26093 | -0.32044 | 122.4426 | 0.009155 | 122.7173 | 122.8088 | -0.15106 | 122.4838 | 0.086975 | 0.27466 | 122.8271 | 123.0194 | 122.8271 | 122.9874 | 122.7173 | 123.0652 | 122.8409 | 122.4838 | 122.9874 | 122.7173 | 122.8409 | 122.8271 | 123.0652 | -0.53558 | -0.49439
3162.5469 | 123.0927 | -122.818 | 0.20142 | 0.10002 | 0.012843 | -0.0033196 | 0.047292 | -0.017684 | -0.010621 | 0.013262 | -0.14191 | 0.1831 | -0.37994 | -0.032043 | -0.018311 | -0.004578 | 0 | 0.13275 | 0.24719 | -0.31128 | 122.438 | -0.018311 | 122.6761 | 122.7859 | -0.21973 | 122.5067 | 0.045776 | 0.23804 | 122.818 | 122.9507 | 122.7997 | 123.0011 | 122.6761 | 123.0652 | 122.8134 | 122.5067 | 123.0011 | 122.6761 | 122.8134 | 122.7997 | 123.0652 | -0.58136 | -0.5127
3164.2969 | 123.0743 | -122.8455 | 0.19684 | -0.12123 | 0.011348 | -0.0054558 | 0.046651 | -0.013411 | -0.012544 | 0.01198 | -0.064087 | 0.15106 | -0.35706 | 0.022888 | 0.013733 | 0.054932 | -0.027466 | 0.21057 | 0.24261 | -0.2655 | 122.4884 | -0.045776 | 122.7814 | 122.8683 | -0.18311 | 122.58 | 0.045777 | 0.29297 | 122.818 | 123.056 | 122.8592 | 122.9965 | 122.7814 | 123.0881 | 122.9004 | 122.58 | 122.9965 | 122.7814 | 122.9004 | 122.8592 | 123.0881 | -0.55389 | -0.46234
3166.0469 | 123.0423 | -122.8317 | 0.21057 | -0.10597 | 0.0096387 | -0.0078058 | 0.043874 | -0.016616 | -0.013185 | 0.0089893 | -0.059509 | 0.16022 | -0.35248 | 0.022888 | 0.027466 | 0.059509 | -0.013733 | 0.20599 | 0.24261 | -0.3067 | 122.4792 | -0.050354 | 122.7722 | 122.8546 | -0.18311 | 122.525 | 0.032044 | 0.29297 | 122.818 | 123.0377 | 122.8592 | 122.9919 | 122.7722 | 123.0743 | 122.8912 | 122.525 | 122.9919 | 122.7722 | 122.8912 | 122.8592 | 123.0743 | -0.56305 | -0.51727
3167.75 | 123.1842 | -122.7814 | 0.18768 | -0.25856 | 0.010493 | -0.0075922 | 0.037252 | -0.018752 | -0.0095531 | 0.010698 | -0.09613 | 0.14191 | -0.35706 | -0.018311 | 0.022888 | 0.036621 | 0.022888 | 0.20142 | 0.25635 | -0.31586 | 122.4243 | -0.045776 | 122.6852 | 122.7631 | -0.16479 | 122.4655 | 0.068665 | 0.26093 | 122.8043 | 122.9828 | 122.8043 | 122.9233 | 122.6852 | 123.0377 | 122.818 | 122.4655 | 122.9233 | 122.6852 | 122.818 | 122.8043 | 123.0377 | -0.54474 | -0.50354
3169.5 | 123.1567 | -122.8043 | 0.16479 | -0.098343 | 0.012202 | -0.003106 | 0.037465 | -0.020034 | -0.0089123 | 0.01198 | -0.041199 | 0.14648 | -0.33875 | 0.059509 | 0.10986 | 0.14191 | -0.11902 | 0.3067 | 0.23346 | -0.28839 | 122.4655 | -0.018311 | 122.7631 | 122.8638 | -0.054932 | 122.5159 | 0.068664 | 0.29755 | 122.6852 | 123.111 | 122.9141 | 122.9507 | 122.7631 | 123.0377 | 122.9462 | 122.5159 | 122.9507 | 122.7631 | 122.9462 | 122.9141 | 123.0377 | -0.50354 | -0.45319
3171.25 | 123.1476 | -122.7951 | 0.15106 | -0.044937 | 0.010921 | -0.0073786 | 0.039815 | -0.019179 | -0.0089123 | 0.0098437 | -0.041199 | 0.16022 | -0.33417 | 0.054932 | 0.10529 | 0.12817 | -0.10986 | 0.27466 | 0.21057 | -0.27466 | 122.4609 | 0.009155 | 122.7539 | 122.85 | -0.045776 | 122.5204 | 0.059509 | 0.29297 | 122.6852 | 123.0698 | 122.9004 | 122.9553 | 122.7539 | 123.0057 | 122.9233 | 122.5204 | 122.9553 | 122.7539 | 122.9233 | 122.9004 | 123.0057 | -0.48523 | -0.42572
3172.9531 | 123.1796 | -122.7997 | 0.16479 | -0.26619 | 0.012843 | 0.003089 | 0.045583 | -0.018111 | -0.010408 | 0.011766 | -0.11902 | 0.1831 | -0.39825 | 0 | 0 | 0.009155 | 0.059509 | 0.1831 | 0.2655 | -0.31586 | 122.4014 | 0.01831 | 122.6807 | 122.7997 | -0.16479 | 122.4838 | 0.10071 | 0.27924 | 122.8592 | 122.9828 | 122.7997 | 122.9828 | 122.6807 | 123.0652 | 122.8088 | 122.4838 | 122.9828 | 122.6807 | 122.8088 | 122.7997 | 123.0652 | -0.56305 | -0.48065
3174.7031 | 123.1338 | -122.7722 | 0.16937 | -0.1136 | 0.012416 | -0.0097284 | 0.039174 | -0.01982 | -0.0089123 | 0.01198 | -0.032043 | 0.1236 | -0.33875 | 0.10071 | 0.10529 | 0.14648 | -0.13275 | 0.31128 | 0.23346 | -0.27008 | 122.4335 | -0.045777 | 122.7402 | 122.8729 | -0.064087 | 122.5021 | 0.064086 | 0.3067 | 122.6395 | 123.0835 | 122.8775 | 122.8958 | 122.7402 | 123.0057 | 122.9187 | 122.5021 | 122.8958 | 122.7402 | 122.9187 | 122.8775 | 123.0057 | -0.50812 | -0.43945
3176.4688 | 123.0515 | -122.8683 | 0.21515 | -0.067826 | 0.011989 | -0.0035332 | 0.050069 | -0.014907 | -0.013399 | 0.0096301 | -0.045776 | 0.15106 | -0.37537 | 0.036621 | 0.027466 | 0.059509 | -0.027466 | 0.2243 | 0.24719 | -0.27924 | 122.493 | -0.064087 | 122.8226 | 122.905 | -0.18768 | 122.5891 | 0.032043 | 0.32959 | 122.8409 | 123.0927 | 122.8958 | 123.0194 | 122.8226 | 123.1155 | 122.9279 | 122.5891 | 123.0194 | 122.8226 | 122.9279 | 122.8958 | 123.1155 | -0.59052 | -0.49438
3178.2344 | 123.0515 | -122.8455 | 0.20142 | -0.067826 | 0.013484 | -0.0033196 | 0.046651 | -0.015334 | -0.012971 | 0.01198 | -0.036621 | 0.15106 | -0.35706 | 0.032043 | 0.036621 | 0.050354 | -0.018311 | 0.20142 | 0.23346 | -0.32044 | 122.4884 | -0.050354 | 122.8088 | 122.8775 | -0.1648 | 122.525 | 0.032043 | 0.32043 | 122.8271 | 123.0469 | 122.8821 | 122.9965 | 122.8088 | 123.0789 | 122.8958 | 122.525 | 122.9965 | 122.8088 | 122.8958 | 122.8821 | 123.0789 | -0.55847 | -0.52185
3180 | 123.0331 | -122.8455 | 0.20142 | 0.22972 | 0.010707 | -0.0026788 | 0.044515 | -0.016616 | -0.010835 | 0.012407 | -0.073242 | 0.14191 | -0.34332 | 0.045776 | 0.068665 | 0.10986 | -0.14191 | 0.22888 | 0.2243 | -0.29297 | 122.5021 | -0.059509 | 122.7722 | 122.8912 | -0.13275 | 122.5525 | 0.022888 | 0.27008 | 122.7036 | 123.0743 | 122.9141 | 122.9874 | 122.7722 | 123.0698 | 122.9553 | 122.5525 | 122.9874 | 122.7722 | 122.9553 | 122.9141 | 123.0698 | -0.54474 | -0.49438
3181.7031 | 123.175 | -122.7997 | 0.16937 | -0.23567 | 0.011348 | -0.0063104 | 0.04067 | -0.018111 | -0.010194 | 0.010057 | -0.10529 | 0.19684 | -0.36163 | -0.022888 | 0 | 0.009155 | 0.050354 | 0.16479 | 0.27008 | -0.33875 | 122.4381 | 0.027465 | 122.6944 | 122.7768 | -0.16937 | 122.4609 | 0.10071 | 0.25635 | 122.85 | 122.9645 | 122.7997 | 122.9965 | 122.6944 | 123.0698 | 122.8088 | 122.4609 | 122.9965 | 122.6944 | 122.8088 | 122.7997 | 123.0698 | -0.53101 | -0.50812
3183.4531 | 123.175 | -122.7997 | 0.16937 | -0.26619 | 0.014766 | -0.0043878 | 0.045156 | -0.016402 | -0.01233 | 0.01198 | -0.11902 | 0.17395 | -0.37079 | -0.022888 | 0.004578 | 0 | 0.07782 | 0.16937 | 0.27008 | -0.32044 | 122.4289 | 0.004577 | 122.6807 | 122.7768 | -0.16479 | 122.4792 | 0.10071 | 0.25177 | 122.8775 | 122.9691 | 122.8043 | 122.9736 | 122.6807 | 123.0698 | 122.7997 | 122.4792 | 122.9736 | 122.6807 | 122.7997 | 122.8043 | 123.0698 | -0.54016 | -0.48981
3185.2031 | 123.0606 | -122.8363 | 0.21515 | -0.10597 | 0.011989 | -0.00011543 | 0.048146 | -0.014907 | -0.012117 | 0.013048 | -0.045776 | 0.17395 | -0.35248 | 0.041199 | 0.041199 | 0.059509 | -0.032043 | 0.19226 | 0.2655 | -0.29755 | 122.4838 | -0.041199 | 122.7905 | 122.8775 | -0.17395 | 122.5388 | 0.050354 | 0.3067 | 122.8043 | 123.0286 | 122.8775 | 123.0103 | 122.7905 | 123.1018 | 122.8958 | 122.5388 | 123.0103 | 122.7905 | 122.8958 | 122.8775 | 123.1018 | -0.56763 | -0.5127
3186.9062 | 123.1201 | -122.7951 | 0.15564 | -0.12886 | 0.011348 | -0.0050286 | 0.039388 | -0.01512 | -0.0089123 | 0.012407 | -0.027466 | 0.14191 | -0.32959 | 0.082397 | 0.1236 | 0.14191 | -0.14191 | 0.32959 | 0.2243 | -0.27008 | 122.4655 | -0.013733 | 122.7676 | 122.8775 | -0.032044 | 122.525 | 0.068664 | 0.30212 | 122.6532 | 123.1247 | 122.9187 | 122.937 | 122.7676 | 123.0194 | 122.937 | 122.525 | 122.937 | 122.7676 | 122.937 | 122.9187 | 123.0194 | -0.48523 | -0.42572
3188.6562 | 123.056 | -122.8363 | 0.19226 | 0.15343 | 0.011348 | -0.00011543 | 0.047719 | -0.016402 | -0.01169 | 0.012621 | -0.082397 | 0.15564 | -0.36163 | 0.004578 | 0.027466 | 0.073242 | -0.09613 | 0.18768 | 0.24261 | -0.29755 | 122.4747 | -0.036621 | 122.7539 | 122.8409 | -0.16479 | 122.5388 | 0.050354 | 0.27924 | 122.7402 | 123.024 | 122.8638 | 122.9919 | 122.7539 | 123.0789 | 122.9095 | 122.5388 | 122.9919 | 122.7539 | 122.9095 | 122.8638 | 123.0789 | -0.55389 | -0.48981
3190.3594 | 123.0423 | -122.8271 | 0.21973 | -0.10597 | 0.014766 | -0.00054263 | 0.047719 | -0.017256 | -0.012758 | 0.010912 | -0.059509 | 0.17395 | -0.36163 | 0.022888 | 0.036621 | 0.054932 | -0.036621 | 0.21973 | 0.24261 | -0.29297 | 122.4655 | -0.045777 | 122.7676 | 122.85 | -0.18311 | 122.5342 | 0.022888 | 0.30212 | 122.7905 | 123.0469 | 122.8638 | 123.0011 | 122.7676 | 123.0698 | 122.8821 | 122.5342 | 123.0011 | 122.7676 | 122.8821 | 122.8638 | 123.0698 | -0.58136 | -0.5127
3192.125 | 123.143 | -122.8043 | 0.18768 | -0.22041 | 0.01028 | -0.002038 | 0.040029 | -0.018965 | -0.010194 | 0.012194 | -0.018311 | 0.10986 | -0.32959 | 0.09613 | 0.13733 | 0.15564 | -0.11444 | 0.32501 | 0.21973 | -0.27924 | 122.4747 | -0.07782 | 122.7859 | 122.9004 | -0.050354 | 122.525 | 0.032044 | 0.31128 | 122.6898 | 123.1293 | 122.9416 | 122.9141 | 122.7859 | 123.024 | 122.9599 | 122.525 | 122.9141 | 122.7859 | 122.9599 | 122.9416 | 123.024 | -0.51727 | -0.46692
3193.8125 | 123.1293 | -122.7814 | 0.16479 | -0.16701 | 0.0089979 | -0.0043878 | 0.041097 | -0.017684 | -0.010194 | 0.012407 | -0.009155 | 0.13275 | -0.33417 | 0.10071 | 0.11902 | 0.14191 | -0.12817 | 0.33417 | 0.21515 | -0.27924 | 122.4472 | -0.032044 | 122.7722 | 122.8821 | -0.045776 | 122.5021 | 0.050354 | 0.32501 | 122.6532 | 123.1155 | 122.9004 | 122.9141 | 122.7722 | 122.9965 | 122.9233 | 122.5021 | 122.9141 | 122.7722 | 122.9233 | 122.9004 | 122.9965 | -0.49896 | -0.44403
3195.5781 | 123.0927 | -122.8043 | 0.17853 | 0.13817 | 0.013484 | -0.001397 | 0.041951 | -0.017043 | -0.010835 | 0.011126 | -0.027466 | 0.13275 | -0.33875 | 0.050354 | 0.068665 | 0.11444 | -0.13733 | 0.25635 | 0.23346 | -0.27924 | 122.4655 | -0.045777 | 122.7768 | 122.8546 | -0.10986 | 122.525 | 0.054931 | 0.31128 | 122.6669 | 123.0606 | 122.8729 | 122.937 | 122.7768 | 123.0377 | 122.9187 | 122.525 | 122.937 | 122.7768 | 122.9187 | 122.8729 | 123.0377 | -0.51727 | -0.45776
3197.2812 | 123.0423 | -122.8271 | 0.20142 | 0.1458 | 0.013057 | -0.001397 | 0.047506 | -0.015548 | -0.012117 | 0.0094165 | -0.027466 | 0.14191 | -0.34332 | 0.073242 | 0.086975 | 0.13275 | -0.15564 | 0.2655 | 0.2243 | -0.26093 | 122.4838 | -0.059509 | 122.7997 | 122.9004 | -0.11444 | 122.5662 | 0.022888 | 0.31586 | 122.6715 | 123.0927 | 122.9141 | 122.9691 | 122.7997 | 123.0515 | 122.9599 | 122.5662 | 122.9691 | 122.7997 | 122.9599 | 122.9141 | 123.0515 | -0.54474 | -0.46234
3199.0469 | 123.1567 | -122.7859 | 0.16022 | 0.0084684 | 0.013484 | 0.00031197 | 0.040456 | -0.017684 | -0.0069897 | 0.011766 | -0.082397 | 0.12817 | -0.3479 | 0.027466 | 0.064087 | 0.09613 | -0.10986 | 0.22888 | 0.24261 | -0.28381 | 122.4381 | -0.032043 | 122.7036 | 122.8134 | -0.09613 | 122.5021 | 0.082398 | 0.2655 | 122.6761 | 123.0148 | 122.85 | 122.9141 | 122.7036 | 123.0286 | 122.8821 | 122.5021 | 122.9141 | 122.7036 | 122.8821 | 122.85 | 123.0286 | -0.50812 | -0.44403
3200.75 | 123.1293 | -122.8088 | 0.17395 | -0.15938 | 0.0089979 | -0.0060968 | 0.04067 | -0.017684 | -0.011262 | 0.011339 | -0.009155 | 0.1236 | -0.33417 | 0.10986 | 0.11444 | 0.14191 | -0.13733 | 0.33417 | 0.23804 | -0.27466 | 122.4747 | -0.050354 | 122.7997 | 122.9187 | -0.059509 | 122.5342 | 0.064087 | 0.32501 | 122.6715 | 123.143 | 122.9233 | 122.9324 | 122.7997 | 123.0469 | 122.9507 | 122.5342 | 122.9324 | 122.7997 | 122.9507 | 122.9233 | 123.0469 | -0.50812 | -0.44861
3202.5312 | 123.1247 | -122.8226 | 0.1831 | -0.13649 | 0.010707 | -0.0056696 | 0.04067 | -0.017897 | -0.010194 | 0.0098437 | -0.018311 | 0.12817 | -0.35248 | 0.10986 | 0.1236 | 0.15564 | -0.13733 | 0.32501 | 0.2243 | -0.26093 | 122.4701 | -0.054931 | 122.8043 | 122.9324 | -0.059509 | 122.5616 | 0.041199 | 0.33417 | 122.6852 | 123.1476 | 122.9462 | 122.9507 | 122.8043 | 123.0469 | 122.9782 | 122.5616 | 122.9507 | 122.8043 | 122.9782 | 122.9462 | 123.0469 | -0.53558 | -0.44403
3204.2344 | 123.1888 | -122.7951 | 0.16937 | -0.23567 | 0.013484 | -0.0069512 | 0.047292 | -0.016829 | -0.012758 | 0.0098437 | -0.10071 | 0.14191 | -0.36621 | 0.004578 | 0.018311 | 0.009155 | 0.032043 | 0.18768 | 0.28381 | -0.29755 | 122.4289 | -0.027466 | 122.6944 | 122.7997 | -0.15106 | 122.4976 | 0.11444 | 0.2655 | 122.8271 | 122.9828 | 122.8134 | 122.937 | 122.6944 | 123.0789 | 122.8043 | 122.4976 | 122.937 | 122.6944 | 122.8043 | 122.8134 | 123.0789 | -0.53558 | -0.46692
3205.9844 | 123.1247 | -122.8134 | 0.18768 | -0.15938 | 0.010921 | -0.0035332 | 0.043019 | -0.020247 | -0.012544 | 0.011339 | 0.004578 | 0.1236 | -0.3479 | 0.10986 | 0.11444 | 0.13275 | -0.10529 | 0.3067 | 0.21515 | -0.27924 | 122.4655 | -0.064087 | 122.818 | 122.9233 | -0.073242 | 122.5342 | 0.027466 | 0.35248 | 122.7081 | 123.1201 | 122.9279 | 122.937 | 122.818 | 123.0286 | 122.9462 | 122.5342 | 122.937 | 122.818 | 122.9462 | 122.9279 | 123.0286 | -0.53558 | -0.46692
3207.6875 | 123.1796 | -122.7905 | 0.17853 | -0.0067901 | 0.0089979 | -0.0063104 | 0.04131 | -0.018965 | -0.0091259 | 0.010271 | -0.073242 | 0.13733 | -0.33875 | 0.036621 | 0.068665 | 0.09613 | -0.10986 | 0.24719 | 0.23346 | -0.27466 | 122.4518 | -0.041199 | 122.7173 | 122.8271 | -0.10986 | 122.5159 | 0.054931 | 0.2655 | 122.6807 | 123.0377 | 122.8592 | 122.9279 | 122.7173 | 123.024 | 122.8867 | 122.5159 | 122.9279 | 122.7173 | 122.8867 | 122.8592 | 123.024 | -0.51727 | -0.45319
3209.4375 | 123.143 | -122.8317 | 0.16937 | -0.1899 | 0.0098523 | -0.0063104 | 0.041738 | -0.016402 | -0.010835 | 0.010485 | 0.004578 | 0.13275 | -0.32959 | 0.10986 | 0.11902 | 0.12817 | -0.12817 | 0.32501 | 0.21973 | -0.28381 | 122.5021 | -0.036622 | 122.8363 | 122.9416 | -0.050354 | 122.5479 | 0.050354 | 0.33417 | 122.7036 | 123.1567 | 122.9507 | 122.9645 | 122.8363 | 123.0515 | 122.9599 | 122.5479 | 122.9645 | 122.8363 | 122.9599 | 122.9507 | 123.0515 | -0.49896 | -0.45319
3211.1406 | 123.0606 | -122.8455 | 0.19226 | 0.11528 | 0.0098523 | -0.0046014 | 0.044942 | -0.016829 | -0.010194 | 0.010057 | -0.018311 | 0.11444 | -0.33417 | 0.091553 | 0.086975 | 0.11902 | -0.19226 | 0.25635 | 0.23346 | -0.27924 | 122.5113 | -0.07782 | 122.8271 | 122.937 | -0.10529 | 122.5662 | 0.041198 | 0.31586 | 122.6532 | 123.1018 | 122.9324 | 122.9599 | 122.8271 | 123.0789 | 122.9645 | 122.5662 | 122.9599 | 122.8271 | 122.9645 | 122.9324 | 123.0789 | -0.52643 | -0.4715
3212.9062 | 123.0377 | -122.8317 | 0.21057 | 0.16869 | 0.011561 | -0.0052422 | 0.046224 | -0.014907 | -0.010194 | 0.013048 | 0.009155 | 0.10986 | -0.32959 | 0.09613 | 0.11902 | 0.13733 | -0.20599 | 0.27924 | 0.21057 | -0.25177 | 122.5021 | -0.10071 | 122.8409 | 122.9279 | -0.091552 | 122.58 | 0 | 0.33875 | 122.6257 | 123.111 | 122.9507 | 122.9416 | 122.8409 | 123.0423 | 122.9691 | 122.58 | 122.9416 | 122.8409 | 122.9691 | 122.9507 | 123.0423 | -0.54016 | -0.46234
3214.6094 | 123.1659 | -122.818 | 0.17853 | -0.25856 | 0.0098523 | -0.004815 | 0.046651 | -0.01747 | -0.011903 | 0.010485 | -0.11444 | 0.1831 | -0.37537 | 0.004578 | 0.004578 | 0.009155 | 0.064087 | 0.16937 | 0.2655 | -0.32959 | 122.4426 | 0.004577 | 122.7036 | 122.8226 | -0.17395 | 122.4884 | 0.086975 | 0.26092 | 122.8821 | 122.9874 | 122.8226 | 123.0011 | 122.7036 | 123.0835 | 122.8271 | 122.4884 | 123.0011 | 122.7036 | 122.8271 | 122.8226 | 123.0835 | -0.55389 | -0.50812
3216.3594 | 123.0606 | -122.8409 | 0.21057 | -0.044937 | 0.010493 | -0.001397 | 0.049001 | -0.01747 | -0.011903 | 0.012407 | -0.073242 | 0.16479 | -0.37994 | 0.018311 | 0.013733 | 0.013733 | -0.022888 | 0.16937 | 0.26093 | -0.30212 | 122.4609 | -0.045776 | 122.7676 | 122.8592 | -0.19684 | 122.5388 | 0.050354 | 0.3067 | 122.818 | 123.0103 | 122.8546 | 123.0057 | 122.7676 | 123.1018 | 122.8546 | 122.5388 | 123.0057 | 122.7676 | 122.8546 | 122.8546 | 123.1018 | -0.59052 | -0.5127
3218.125 | 123.0927 | -122.818 | 0.19226 | 0.12291 | 0.011348 | -0.0093012 | 0.041097 | -0.017256 | -0.0082715 | 0.013048 | -0.050354 | 0.13275 | -0.34332 | 0.045776 | 0.073242 | 0.10071 | -0.13275 | 0.24719 | 0.21057 | -0.28381 | 122.4747 | -0.05951 | 122.7676 | 122.8638 | -0.11902 | 122.5342 | 0.01831 | 0.29297 | 122.6852 | 123.0652 | 122.8912 | 122.9507 | 122.7676 | 123.0286 | 122.9187 | 122.5342 | 122.9507 | 122.7676 | 122.9187 | 122.8912 | 123.0286 | -0.53558 | -0.47607
3219.8281 | 123.1613 | -122.7859 | 0.16022 | 0.0084684 | 0.011134 | -0.0075922 | 0.039815 | -0.017684 | -0.0093395 | 0.01198 | -0.073242 | 0.14191 | -0.35248 | 0.036621 | 0.068665 | 0.086975 | -0.091553 | 0.24719 | 0.23346 | -0.29297 | 122.4335 | -0.01831 | 122.7127 | 122.8226 | -0.091552 | 122.493 | 0.073242 | 0.27924 | 122.6944 | 123.0331 | 122.8546 | 122.9279 | 122.7127 | 123.0194 | 122.8729 | 122.493 | 122.9279 | 122.7127 | 122.8729 | 122.8546 | 123.0194 | -0.5127 | -0.45319
3221.5781 | 123.0743 | -122.8271 | 0.21515 | 0.046615 | 0.01028 | -0.0026788 | 0.050283 | -0.01747 | -0.01233 | 0.011553 | -0.073242 | 0.15564 | -0.37994 | 0 | -0.004578 | 0.018311 | -0.013733 | 0.14648 | 0.2655 | -0.29755 | 122.4472 | -0.059509 | 122.7539 | 122.8271 | -0.21973 | 122.5296 | 0.050354 | 0.3067 | 122.8134 | 122.9736 | 122.8226 | 122.9828 | 122.7539 | 123.0927 | 122.8455 | 122.5296 | 122.9828 | 122.7539 | 122.8455 | 122.8226 | 123.0927 | -0.59509 | -0.5127
3223.2812 | 123.1201 | -122.818 | 0.18768 | -0.1899 | 0.011134 | -0.0050286 | 0.041524 | -0.01747 | -0.012117 | 0.011339 | -0.018311 | 0.12817 | -0.34332 | 0.10529 | 0.1236 | 0.14648 | -0.1236 | 0.32959 | 0.21057 | -0.28381 | 122.4747 | -0.059509 | 122.7997 | 122.9233 | -0.064087 | 122.5342 | 0.022888 | 0.32501 | 122.6944 | 123.1476 | 122.9416 | 122.9462 | 122.7997 | 123.0286 | 122.9645 | 122.5342 | 122.9462 | 122.7997 | 122.9645 | 122.9416 | 123.0286 | -0.53101 | -0.4715
3225.0469 | 123.1384 | -122.818 | 0.16479 | -0.1136 | 0.011775 | -0.010369 | 0.040456 | -0.020247 | -0.010408 | 0.012194 | -0.050354 | 0.12817 | -0.34332 | 0.11444 | 0.13275 | 0.13733 | -0.13733 | 0.3067 | 0.2243 | -0.29297 | 122.4747 | -0.036621 | 122.7676 | 122.9324 | -0.032044 | 122.525 | 0.059509 | 0.29297 | 122.6807 | 123.1247 | 122.9507 | 122.9462 | 122.7676 | 123.0423 | 122.9553 | 122.525 | 122.9462 | 122.7676 | 122.9553 | 122.9507 | 123.0423 | -0.50812 | -0.45776
3226.75 | 123.1934 | -122.8226 | 0.16022 | -0.21278 | 0.011775 | -0.0078058 | 0.045797 | -0.020034 | -0.010835 | 0.010698 | -0.13275 | 0.16022 | -0.38452 | 0 | 0.004578 | 0.009155 | 0.054932 | 0.1831 | 0.28381 | -0.31586 | 122.438 | 0 | 122.6898 | 122.8226 | -0.15564 | 122.5067 | 0.1236 | 0.25177 | 122.8775 | 123.0057 | 122.8271 | 122.9828 | 122.6898 | 123.1064 | 122.8317 | 122.5067 | 122.9828 | 122.6898 | 122.8317 | 122.8271 | 123.1064 | -0.54474 | -0.47607
3228.5156 | 123.1476 | -122.8043 | 0.16937 | 0.084762 | 0.010921 | -0.0026788 | 0.040242 | -0.018325 | -0.010194 | 0.01198 | -0.054932 | 0.11902 | -0.32501 | 0.050354 | 0.068665 | 0.10071 | -0.1236 | 0.24719 | 0.23346 | -0.28381 | 122.4792 | -0.050354 | 122.7493 | 122.8546 | -0.10071 | 122.5204 | 0.064086 | 0.27008 | 122.6807 | 123.0515 | 122.8729 | 122.9233 | 122.7493 | 123.0377 | 122.905 | 122.5204 | 122.9233 | 122.7493 | 122.905 | 122.8729 | 123.0377 | -0.49439 | -0.45319
3230.2031 | 123.1979 | -122.7859 | 0.17395 | -0.28145 | 0.010493 | -0.0043878 | 0.042592 | -0.018752 | -0.01233 | 0.0077075 | -0.054932 | 0.16022 | -0.36163 | 0.027466 | 0.041199 | 0.041199 | 0 | 0.21515 | 0.25177 | -0.28839 | 122.4243 | -0.013733 | 122.731 | 122.8134 | -0.13275 | 122.4976 | 0.07782 | 0.3067 | 122.7859 | 123.0011 | 122.8271 | 122.9462 | 122.731 | 123.0377 | 122.8271 | 122.4976 | 122.9462 | 122.731 | 122.8271 | 122.8271 | 123.0377 | -0.53558 | -0.46234
3231.9688 | 123.0469 | -122.8592 | 0.21057 | -0.098343 | 0.012416 | -0.0018244 | 0.050496 | -0.01512 | -0.012758 | 0.0096301 | -0.050354 | 0.15564 | -0.36621 | 0.050354 | 0.041199 | 0.07782 | -0.045776 | 0.21973 | 0.24719 | -0.28381 | 122.493 | -0.054931 | 122.8088 | 122.9095 | -0.16937 | 122.5754 | 0.036621 | 0.31586 | 122.8134 | 123.0789 | 122.9004 | 123.0148 | 122.8088 | 123.1064 | 122.937 | 122.5754 | 123.0148 | 122.8088 | 122.937 | 122.9004 | 123.1064 | -0.57678 | -0.49438
3233.7344 | 123.0469 | -122.8317 | 0.21057 | 0.19157 | 0.011561 | -0.0050286 | 0.045369 | -0.017043 | -0.012971 | 0.011126 | -0.045776 | 0.11902 | -0.3479 | 0.068665 | 0.086975 | 0.13275 | -0.16937 | 0.24719 | 0.21515 | -0.2655 | 122.4838 | -0.091552 | 122.7859 | 122.9004 | -0.1236 | 122.5662 | 0.004578 | 0.30212 | 122.6624 | 123.0789 | 122.9187 | 122.9507 | 122.7859 | 123.0469 | 122.9645 | 122.5662 | 122.9507 | 122.7859 | 122.9645 | 122.9187 | 123.0469 | -0.55847 | -0.47607
3235.4375 | 123.0881 | -122.8455 | 0.17395 | 0.16869 | 0.010921 | -0.0078058 | 0.046224 | -0.01747 | -0.010621 | 0.01198 | -0.10986 | 0.16022 | -0.36621 | -0.022888 | -0.018311 | 0.004578 | -0.004578 | 0.13275 | 0.25635 | -0.31586 | 122.4792 | -0.013733 | 122.7356 | 122.8226 | -0.19226 | 122.5296 | 0.082398 | 0.25635 | 122.8409 | 122.9782 | 122.8271 | 123.0057 | 122.7356 | 123.1018 | 122.85 | 122.5296 | 123.0057 | 122.7356 | 122.85 | 122.8271 | 123.1018 | -0.54016 | -0.48981
3237.2031 | 123.1338 | -122.818 | 0.20142 | -0.1899 | 0.010493 | -0.0080194 | 0.044728 | -0.016616 | -0.013826 | 0.012194 | -0.10986 | 0.14191 | -0.3891 | 0.036621 | 0.036621 | 0.059509 | 0.009155 | 0.20599 | 0.2655 | -0.29297 | 122.4289 | -0.059509 | 122.7081 | 122.8546 | -0.1648 | 122.525 | 0.064087 | 0.27924 | 122.8271 | 123.024 | 122.8546 | 122.9599 | 122.7081 | 123.0835 | 122.8775 | 122.525 | 122.9599 | 122.7081 | 122.8775 | 122.8546 | 123.0835 | -0.59052 | -0.49438
3238.9062 | 123.0286 | -122.8409 | 0.19684 | 0.18394 | 0.010921 | -0.003106 | 0.042806 | -0.015761 | -0.0095531 | 0.012407 | -0.018311 | 0.1236 | -0.33875 | 0.07782 | 0.09613 | 0.15564 | -0.18768 | 0.28381 | 0.21973 | -0.27008 | 122.5021 | -0.073242 | 122.8226 | 122.9187 | -0.10071 | 122.5708 | 0.022889 | 0.32043 | 122.6532 | 123.1247 | 122.937 | 122.9645 | 122.8226 | 123.0606 | 122.9965 | 122.5708 | 122.9645 | 122.8226 | 122.9965 | 122.937 | 123.0606 | -0.53558 | -0.46692
3240.6719 | 123.056 | -122.85 | 0.20599 | -0.10597 | 0.011134 | -0.0067376 | 0.047719 | -0.015548 | -0.013399 | 0.011553 | -0.059509 | 0.14191 | -0.3891 | 0.022888 | 0.045776 | 0.073242 | -0.009155 | 0.21515 | 0.24719 | -0.29297 | 122.4609 | -0.064087 | 122.7905 | 122.8729 | -0.16022 | 122.5571 | 0.041198 | 0.32959 | 122.8409 | 123.0652 | 122.8958 | 122.9919 | 122.7905 | 123.0972 | 122.9233 | 122.5571 | 122.9919 | 122.7905 | 122.9233 | 122.8958 | 123.0972 | -0.59509 | -0.49896
3242.4531 | 123.111 | -122.8043 | 0.16937 | -0.13649 | 0.0094251 | -0.003106 | 0.039388 | -0.019393 | -0.01169 | 0.01433 | -0.050354 | 0.10529 | -0.34332 | 0.086975 | 0.13733 | 0.17853 | -0.15106 | 0.32959 | 0.21515 | -0.2655 | 122.4609 | -0.064087 | 122.7539 | 122.8912 | -0.032044 | 122.5388 | 0.045776 | 0.29297 | 122.6532 | 123.1338 | 122.9416 | 122.9095 | 122.7539 | 123.0194 | 122.9828 | 122.5388 | 122.9095 | 122.7539 | 122.9828 | 122.9416 | 123.0194 | -0.5127 | -0.43488
3244.1406 | 123.2025 | -122.7905 | 0.16937 | -0.22804 | 0.011134 | -0.0056696 | 0.043874 | -0.018752 | -0.011262 | 0.0096301 | -0.11444 | 0.17395 | -0.39825 | -0.027466 | -0.009155 | 0.013733 | 0.064087 | 0.16937 | 0.28381 | -0.33417 | 122.3923 | 0.004577 | 122.6761 | 122.7631 | -0.17853 | 122.4564 | 0.11444 | 0.28381 | 122.8546 | 122.9599 | 122.7814 | 122.9645 | 122.6761 | 123.0743 | 122.8043 | 122.4564 | 122.9645 | 122.6761 | 122.8043 | 122.7814 | 123.0743 | -0.56763 | -0.50354
3245.8906 | 123.0515 | -122.8546 | 0.21057 | 0.18394 | 0.011775 | -0.00054263 | 0.046224 | -0.017043 | -0.013185 | 0.010698 | -0.045776 | 0.1236 | -0.35248 | 0.073242 | 0.091553 | 0.13275 | -0.15564 | 0.25635 | 0.24719 | -0.27466 | 122.5021 | -0.086975 | 122.8088 | 122.9279 | -0.11902 | 122.58 | 0.036621 | 0.3067 | 122.699 | 123.111 | 122.9462 | 122.9782 | 122.8088 | 123.1018 | 122.9874 | 122.58 | 122.9782 | 122.8088 | 122.9874 | 122.9462 | 123.1018 | -0.56305 | -0.48523
3247.6719 | 123.0698 | -122.8638 | 0.19684 | 0.16106 | 0.01327 | -0.004815 | 0.047292 | -0.016188 | -0.011049 | 0.012621 | -0.10071 | 0.16022 | -0.38452 | -0.009155 | 0.022888 | 0.041199 | -0.091553 | 0.17853 | 0.23804 | -0.27924 | 122.4792 | -0.036621 | 122.7631 | 122.8546 | -0.17395 | 122.5845 | 0.041199 | 0.28381 | 122.7722 | 123.0423 | 122.8867 | 123.024 | 122.7631 | 123.1018 | 122.905 | 122.5845 | 123.024 | 122.7631 | 122.905 | 122.8867 | 123.1018 | -0.58136 | -0.47607
3249.4531 | 123.0423 | -122.8271 | 0.21973 | 0.16869 | 0.011775 | -0.0039606 | 0.043874 | -0.014266 | -0.015321 | 0.011126 | -0.027466 | 0.11902 | -0.36621 | 0.068665 | 0.091553 | 0.13275 | -0.17853 | 0.27008 | 0.19684 | -0.25635 | 122.4609 | -0.10071 | 122.7997 | 122.8958 | -0.12817 | 122.5708 | -0.022889 | 0.33875 | 122.6486 | 123.0972 | 122.9187 | 122.9462 | 122.7997 | 123.024 | 122.9599 | 122.5708 | 122.9462 | 122.7997 | 122.9599 | 122.9187 | 123.024 | -0.58594 | -0.47608
3251.1406 | 123.0423 | -122.8226 | 0.21057 | 0.22972 | 0.011775 | -0.0058832 | 0.045156 | -0.015548 | -0.0097669 | 0.012194 | -0.050354 | 0.13275 | -0.35248 | 0.073242 | 0.073242 | 0.12817 | -0.15564 | 0.27008 | 0.22888 | -0.27924 | 122.4701 | -0.07782 | 122.7722 | 122.8958 | -0.13733 | 122.5433 | 0.018311 | 0.30212 | 122.6669 | 123.0927 | 122.8958 | 122.9553 | 122.7722 | 123.0515 | 122.9507 | 122.5433 | 122.9553 | 122.7722 | 122.9507 | 122.8958 | 123.0515 | -0.56305 | -0.48981
3252.9062 | 123.1293 | -122.8088 | 0.17395 | -0.16701 | 0.010493 | -0.0071648 | 0.038106 | -0.019606 | -0.0086987 | 0.0094165 | -0.022888 | 0.10986 | -0.33417 | 0.11444 | 0.13275 | 0.15106 | -0.15564 | 0.32501 | 0.20599 | -0.28839 | 122.4747 | -0.064087 | 122.7859 | 122.9233 | -0.041199 | 122.5204 | 0.032044 | 0.31128 | 122.6532 | 123.1338 | 122.9416 | 122.9187 | 122.7859 | 123.0148 | 122.9599 | 122.5204 | 122.9187 | 122.7859 | 122.9599 | 122.9416 | 123.0148 | -0.50812 | -0.46234
3254.5938 | 123.0881 | -122.8592 | 0.20599 | -0.10597 | 0.011348 | -0.0022516 | 0.047933 | -0.018111 | -0.01233 | 0.010912 | -0.086975 | 0.13275 | -0.40741 | 0.045776 | 0.032043 | 0.059509 | -0.013733 | 0.21057 | 0.2655 | -0.30212 | 122.4518 | -0.073243 | 122.7722 | 122.905 | -0.17395 | 122.5571 | 0.059509 | 0.32044 | 122.8455 | 123.0698 | 122.8912 | 122.9919 | 122.7722 | 123.1247 | 122.9187 | 122.5571 | 122.9919 | 122.7722 | 122.9187 | 122.8912 | 123.1247 | -0.6134 | -0.50812
3256.3438 | 123.1201 | -122.8271 | 0.20599 | -0.17464 | 0.012416 | -0.0039606 | 0.047506 | -0.015761 | -0.012971 | 0.01198 | -0.082397 | 0.15106 | -0.37994 | 0.022888 | 0.022888 | 0.045776 | -0.009155 | 0.2243 | 0.24719 | -0.31586 | 122.4472 | -0.054932 | 122.7448 | 122.85 | -0.18311 | 122.5113 | 0.041198 | 0.29755 | 122.818 | 123.0515 | 122.85 | 122.9782 | 122.7448 | 123.0743 | 122.8729 | 122.5113 | 122.9782 | 122.7448 | 122.8729 | 122.85 | 123.0743 | -0.58594 | -0.52185
3258.0469 | 123.1476 | -122.8043 | 0.16479 | 0.054245 | 0.012629 | -0.0041742 | 0.038747 | -0.016402 | -0.010194 | 0.013048 | -0.091553 | 0.1236 | -0.35248 | 0.032043 | 0.082397 | 0.10071 | -0.11444 | 0.23346 | 0.20599 | -0.27924 | 122.4518 | -0.041199 | 122.7127 | 122.8363 | -0.082398 | 122.525 | 0.041199 | 0.26093 | 122.6898 | 123.0377 | 122.8867 | 122.9279 | 122.7127 | 123.0103 | 122.905 | 122.525 | 122.9279 | 122.7127 | 122.905 | 122.8867 | 123.0103 | -0.51727 | -0.44403
3259.7969 | 123.0377 | -122.8363 | 0.19226 | 0.22209 | 0.010921 | 0.00073917 | 0.044088 | -0.015975 | -0.012117 | 0.01198 | -0.022888 | 0.09613 | -0.35248 | 0.086975 | 0.09613 | 0.14191 | -0.19684 | 0.27466 | 0.21973 | -0.27466 | 122.4838 | -0.096131 | 122.8134 | 122.9233 | -0.096131 | 122.5616 | 0.027466 | 0.32959 | 122.6395 | 123.111 | 122.9324 | 122.9324 | 122.8134 | 123.056 | 122.9782 | 122.5616 | 122.9324 | 122.8134 | 122.9782 | 122.9324 | 123.056 | -0.54474 | -0.46692
3261.5469 | 123.0423 | -122.8409 | 0.21515 | -0.1136 | 0.011989 | -0.0052422 | 0.047719 | -0.016616 | -0.011262 | 0.013903 | -0.059509 | 0.13275 | -0.39368 | 0.050354 | 0.022888 | 0.064087 | -0.041199 | 0.21057 | 0.25635 | -0.29755 | 122.4472 | -0.082398 | 122.7814 | 122.8912 | -0.19226 | 122.5433 | 0.041199 | 0.33417 | 122.7997 | 123.0515 | 122.8638 | 122.9736 | 122.7814 | 123.0972 | 122.905 | 122.5433 | 122.9736 | 122.7814 | 122.905 | 122.8638 | 123.0972 | -0.60883 | -0.5127
3263.25 | 123.1476 | -122.8088 | 0.17395 | -0.19753 | 0.01327 | -0.0046014 | 0.04131 | -0.015975 | -0.0097669 | 0.010057 | -0.045776 | 0.11444 | -0.3479 | 0.059509 | 0.091553 | 0.09613 | -0.041199 | 0.27924 | 0.21515 | -0.30212 | 122.4609 | -0.059509 | 122.7631 | 122.8683 | -0.082397 | 122.5067 | 0.041199 | 0.30212 | 122.7676 | 123.0881 | 122.9004 | 122.9233 | 122.7631 | 123.024 | 122.905 | 122.5067 | 122.9233 | 122.7631 | 122.905 | 122.9004 | 123.024 | -0.52185 | -0.47607
3265.0156 | 123.1842 | -122.8043 | 0.17395 | -0.25856 | 0.0085705 | -0.0033196 | 0.040456 | -0.019393 | -0.010408 | 0.010271 | -0.09613 | 0.11902 | -0.37079 | 0.032043 | 0.054932 | 0.082397 | -0.027466 | 0.25635 | 0.25635 | -0.28839 | 122.4335 | -0.054931 | 122.7081 | 122.8363 | -0.11902 | 122.5159 | 0.082398 | 0.27466 | 122.7768 | 123.0606 | 122.8592 | 122.9233 | 122.7081 | 123.0606 | 122.8867 | 122.5159 | 122.9233 | 122.7081 | 122.8867 | 122.8592 | 123.0606 | -0.54474 | -0.46234
3266.7812 | 123.1705 | -122.7905 | 0.15106 | 0.0084684 | 0.013057 | -0.0067376 | 0.039601 | -0.016616 | -0.0099805 | 0.010057 | -0.09613 | 0.1236 | -0.37994 | 0.036621 | 0.07782 | 0.10071 | -0.10529 | 0.25635 | 0.23346 | -0.29755 | 122.4106 | -0.027466 | 122.6944 | 122.8271 | -0.073242 | 122.493 | 0.082397 | 0.28381 | 122.6852 | 123.0469 | 122.8683 | 122.9141 | 122.6944 | 123.024 | 122.8912 | 122.493 | 122.9141 | 122.6944 | 122.8912 | 122.8683 | 123.024 | -0.53101 | -0.44861
3268.5469 | 123.0743 | -122.8546 | 0.19226 | -0.01442 | 0.011989 | -0.0067376 | 0.049215 | -0.017043 | -0.013612 | 0.012194 | -0.09613 | 0.14648 | -0.40741 | 0.004578 | -0.013733 | 0.036621 | -0.013733 | 0.17395 | 0.25177 | -0.28839 | 122.4472 | -0.045777 | 122.7585 | 122.8592 | -0.20599 | 122.5662 | 0.059509 | 0.31128 | 122.8409 | 123.0286 | 122.8409 | 123.0011 | 122.7585 | 123.1064 | 122.8912 | 122.5662 | 123.0011 | 122.7585 | 122.8912 | 122.8409 | 123.1064 | -0.59967 | -0.48065
3270.2344 | 123.1476 | -122.7951 | 0.17853 | -0.18227 | 0.012202 | -0.0090874 | 0.040456 | -0.017684 | -0.0095531 | 0.011553 | -0.036621 | 0.11444 | -0.36163 | 0.10071 | 0.1236 | 0.1236 | -0.10529 | 0.31128 | 0.21973 | -0.27008 | 122.4335 | -0.064087 | 122.7585 | 122.8958 | -0.054932 | 122.525 | 0.041199 | 0.32501 | 122.6898 | 123.1064 | 122.9187 | 122.9095 | 122.7585 | 123.0148 | 122.9187 | 122.525 | 122.9095 | 122.7585 | 122.9187 | 122.9187 | 123.0148 | -0.54016 | -0.44861
3272 | 123.056 | -122.85 | 0.19226 | -0.098343 | 0.01028 | -0.0046014 | 0.047933 | -0.017897 | -0.014039 | 0.011766 | -0.09613 | 0.1236 | -0.40741 | 0.036621 | 0.036621 | 0.050354 | -0.018311 | 0.22888 | 0.25177 | -0.30212 | 122.4426 | -0.068665 | 122.7539 | 122.8867 | -0.15564 | 122.5479 | 0.059509 | 0.31128 | 122.8317 | 123.0789 | 122.8867 | 122.9736 | 122.7539 | 123.1018 | 122.9004 | 122.5479 | 122.9736 | 122.7539 | 122.9004 | 122.8867 | 123.1018 | -0.59967 | -0.49438
3273.7031 | 123.056 | -122.8226 | 0.20142 | 0.19157 | 0.011561 | -0.0011834 | 0.043019 | -0.015548 | -0.011262 | 0.011339 | -0.027466 | 0.10529 | -0.36163 | 0.082397 | 0.11444 | 0.15564 | -0.19226 | 0.27924 | 0.21973 | -0.26093 | 122.4609 | -0.09613 | 122.7951 | 122.905 | -0.086975 | 122.5616 | 0.018311 | 0.33417 | 122.6303 | 123.1018 | 122.937 | 122.9279 | 122.7951 | 123.0423 | 122.9782 | 122.5616 | 122.9279 | 122.7951 | 122.9782 | 122.937 | 123.0423 | -0.56305 | -0.46234
3275.4688 | 123.1384 | -122.8271 | 0.19226 | -0.18227 | 0.011561 | -0.0056696 | 0.040029 | -0.019179 | -0.010835 | 0.010485 | -0.041199 | 0.10529 | -0.35706 | 0.082397 | 0.09613 | 0.1236 | -0.082397 | 0.29297 | 0.23804 | -0.27924 | 122.4701 | -0.086975 | 122.7859 | 122.9095 | -0.096131 | 122.5479 | 0.045776 | 0.31586 | 122.7448 | 123.1201 | 122.9233 | 122.9324 | 122.7859 | 123.0652 | 122.9507 | 122.5479 | 122.9324 | 122.7859 | 122.9507 | 122.9233 | 123.0652 | -0.54932 | -0.4715
3277.1719 | 123.0423 | -122.8729 | 0.21973 | -0.098343 | 0.01028 | -0.003747 | 0.045583 | -0.016402 | -0.01169 | 0.011339 | -0.082397 | 0.12817 | -0.39368 | 0.032043 | 0.041199 | 0.068665 | -0.036621 | 0.20599 | 0.25177 | -0.28839 | 122.4792 | -0.091553 | 122.7905 | 122.905 | -0.17853 | 122.5845 | 0.032043 | 0.31128 | 122.8363 | 123.0789 | 122.9141 | 123.0011 | 122.7905 | 123.1247 | 122.9416 | 122.5845 | 123.0011 | 122.7905 | 122.9416 | 122.9141 | 123.1247 | -0.6134 | -0.50812
3278.9375 | 123.0789 | -122.8317 | 0.19684 | 0.031357 | 0.012629 | -0.003747 | 0.047292 | -0.015761 | -0.012971 | 0.011766 | -0.10071 | 0.13275 | -0.41199 | 0.009155 | 0.009155 | 0.013733 | -0.013733 | 0.14648 | 0.25635 | -0.31586 | 122.4197 | -0.064087 | 122.731 | 122.8409 | -0.18768 | 122.5159 | 0.05951 | 0.31128 | 122.818 | 122.9782 | 122.8409 | 122.9645 | 122.731 | 123.0881 | 122.8455 | 122.5159 | 122.9645 | 122.731 | 122.8455 | 122.8409 | 123.0881 | -0.60882 | -0.5127
3280.6875 | 123.1842 | -122.7905 | 0.17853 | -0.26619 | 0.013911 | -0.0060968 | 0.04131 | -0.016402 | -0.011262 | 0.0092029 | -0.15106 | 0.14648 | -0.42114 | -0.036621 | 0 | 0.004578 | 0.068665 | 0.19684 | 0.26093 | -0.32044 | 122.3694 | -0.032044 | 122.6395 | 122.7539 | -0.17853 | 122.4701 | 0.082397 | 0.27008 | 122.8592 | 122.9874 | 122.7905 | 122.937 | 122.6395 | 123.0515 | 122.7951 | 122.4701 | 122.937 | 122.6395 | 122.7951 | 122.7905 | 123.0515 | -0.59967 | -0.49896
3282.3906 | 123.175 | -122.7951 | 0.15564 | 0.031357 | 0.011561 | -0.001397 | 0.041097 | -0.016188 | -0.0082715 | 0.011339 | -0.082397 | 0.10071 | -0.36163 | 0.022888 | 0.073242 | 0.086975 | -0.09613 | 0.2243 | 0.24261 | -0.28839 | 122.4335 | -0.054932 | 122.7127 | 122.818 | -0.082398 | 122.5067 | 0.086975 | 0.27924 | 122.699 | 123.0194 | 122.8683 | 122.8958 | 122.7127 | 123.0377 | 122.8821 | 122.5067 | 122.8958 | 122.7127 | 122.8821 | 122.8683 | 123.0377 | -0.51727 | -0.44403
3284.1562 | 123.1842 | -122.818 | 0.17395 | -0.23567 | 0.010921 | -0.0067376 | 0.041951 | -0.015548 | -0.01169 | 0.010912 | -0.11902 | 0.13275 | -0.3891 | 0.009155 | 0.027466 | 0.022888 | 0.027466 | 0.19684 | 0.2655 | -0.32501 | 122.4289 | -0.041199 | 122.699 | 122.8271 | -0.14648 | 122.493 | 0.091553 | 0.27008 | 122.8455 | 123.0148 | 122.8455 | 122.9507 | 122.699 | 123.0835 | 122.8409 | 122.493 | 122.9507 | 122.699 | 122.8409 | 122.8455 | 123.0835 | -0.56305 | -0.49896
3285.9062 | 123.1247 | -122.7859 | 0.16479 | -0.10597 | 0.012202 | -0.0095148 | 0.04067 | -0.017684 | -0.010408 | 0.012835 | -0.054932 | 0.10529 | -0.37079 | 0.07782 | 0.11902 | 0.14648 | -0.11444 | 0.31586 | 0.23804 | -0.27924 | 122.4152 | -0.059509 | 122.731 | 122.8638 | -0.045776 | 122.5067 | 0.073242 | 0.31586 | 122.6715 | 123.1018 | 122.905 | 122.8912 | 122.731 | 123.024 | 122.9324 | 122.5067 | 122.8912 | 122.731 | 122.9324 | 122.905 | 123.024 | -0.53558 | -0.44403
3287.6562 | 123.1842 | -122.7997 | 0.17395 | -0.26619 | 0.011134 | -0.004815 | 0.043447 | -0.01747 | -0.011049 | 0.011339 | -0.14648 | 0.13733 | -0.42572 | -0.022888 | 0.004578 | 0.004578 | 0.059509 | 0.19226 | 0.27466 | -0.30212 | 122.374 | -0.036621 | 122.6532 | 122.7768 | -0.16937 | 122.4976 | 0.10071 | 0.27924 | 122.8592 | 122.9919 | 122.8043 | 122.937 | 122.6532 | 123.0743 | 122.8043 | 122.4976 | 122.937 | 122.6532 | 122.8043 | 122.8043 | 123.0743 | -0.59967 | -0.47607
3289.3594 | 123.1934 | -122.7905 | 0.17395 | -0.21278 | 0.015193 | -0.0041742 | 0.041097 | -0.01982 | -0.0099805 | 0.012407 | -0.14648 | 0.13733 | -0.3891 | 0.004578 | 0 | 0.009155 | 0.050354 | 0.20142 | 0.27924 | -0.31586 | 122.4014 | -0.036621 | 122.644 | 122.7951 | -0.17395 | 122.4747 | 0.10529 | 0.24261 | 122.8409 | 122.9919 | 122.7905 | 122.9279 | 122.644 | 123.0698 | 122.7997 | 122.4747 | 122.9279 | 122.644 | 122.7997 | 122.7905 | 123.0698 | -0.56305 | -0.48981
3291.1094 | 123.0515 | -122.8088 | 0.1831 | 0.19157 | 0.013698 | -0.0043878 | 0.043874 | -0.017256 | -0.011903 | 0.011553 | -0.091553 | 0.1236 | -0.38452 | 0.045776 | 0.041199 | 0.09613 | -0.13733 | 0.22888 | 0.22888 | -0.3067 | 122.4243 | -0.059509 | 122.7173 | 122.8546 | -0.14191 | 122.5021 | 0.045777 | 0.29297 | 122.6715 | 123.0377 | 122.85 | 122.9324 | 122.7173 | 123.0377 | 122.905 | 122.5021 | 122.9324 | 122.7173 | 122.905 | 122.85 | 123.0377 | -0.56763 | -0.48981
3292.875 | 123.0377 | -122.85 | 0.21057 | 0.1992 | 0.013911 | -0.0046014 | 0.04601 | -0.014693 | -0.010621 | 0.012407 | -0.032043 | 0.082397 | -0.35706 | 0.082397 | 0.09613 | 0.16022 | -0.18768 | 0.27924 | 0.19684 | -0.2655 | 122.493 | -0.12817 | 122.818 | 122.9324 | -0.11444 | 122.5845 | -0.013733 | 0.32501 | 122.6624 | 123.1293 | 122.9462 | 122.9324 | 122.818 | 123.0469 | 123.0103 | 122.5845 | 122.9324 | 122.818 | 123.0103 | 122.9462 | 123.0469 | -0.56763 | -0.47607
3294.5781 | 123.1201 | -122.8043 | 0.1831 | -0.17464 | 0.011989 | -0.0046014 | 0.038106 | -0.01982 | -0.012117 | 0.010698 | -0.054932 | 0.10529 | -0.3479 | 0.10529 | 0.11444 | 0.13733 | -0.11444 | 0.33417 | 0.2243 | -0.2655 | 122.4564 | -0.077819 | 122.7493 | 122.9095 | -0.068664 | 122.5388 | 0.041199 | 0.29297 | 122.6898 | 123.1384 | 122.9187 | 122.9095 | 122.7493 | 123.0286 | 122.9416 | 122.5388 | 122.9095 | 122.7493 | 122.9416 | 122.9187 | 123.0286 | -0.531 | -0.44861
3296.3438 | 123.111 | -122.8271 | 0.18768 | 0.12291 | 0.012416 | -0.0084466 | 0.04131 | -0.018752 | -0.010194 | 0.013048 | -0.068665 | 0.12817 | -0.35706 | 0.045776 | 0.073242 | 0.10071 | -0.12817 | 0.25177 | 0.22888 | -0.27924 | 122.4701 | -0.059509 | 122.7585 | 122.8729 | -0.11444 | 122.5479 | 0.041199 | 0.28839 | 122.699 | 123.0789 | 122.9004 | 122.9553 | 122.7585 | 123.056 | 122.9279 | 122.5479 | 122.9553 | 122.7585 | 122.9279 | 122.9004 | 123.056 | -0.54474 | -0.46692
3298.1094 | 123.0469 | -122.8363 | 0.20599 | 0.18394 | 0.012843 | -0.0039606 | 0.044728 | -0.018111 | -0.012544 | 0.011766 | -0.013733 | 0.086975 | -0.35706 | 0.086975 | 0.086975 | 0.13275 | -0.17395 | 0.27466 | 0.21057 | -0.27924 | 122.4792 | -0.11902 | 122.8226 | 122.9233 | -0.11902 | 122.5571 | 0.004577 | 0.34332 | 122.6624 | 123.111 | 122.9233 | 122.9233 | 122.8226 | 123.0469 | 122.9691 | 122.5571 | 122.9233 | 122.8226 | 122.9691 | 122.9233 | 123.0469 | -0.56305 | -0.48523
3299.8125 | 123.0469 | -122.8592 | 0.19226 | 0.20683 | 0.0094251 | -0.008233 | 0.046437 | -0.016188 | -0.012544 | 0.012835 | -0.059509 | 0.10529 | -0.36621 | 0.086975 | 0.086975 | 0.13733 | -0.16022 | 0.2655 | 0.21973 | -0.26093 | 122.493 | -0.086975 | 122.7997 | 122.9462 | -0.10529 | 122.5983 | 0.027466 | 0.3067 | 122.699 | 123.1247 | 122.9462 | 122.9645 | 122.7997 | 123.0789 | 122.9965 | 122.5983 | 122.9645 | 122.7997 | 122.9965 | 122.9462 | 123.0789 | -0.55847 | -0.45319
3301.5625 | 123.2025 | -122.7859 | 0.15564 | -0.21278 | 0.012629 | -0.0093012 | 0.042806 | -0.020247 | -0.01169 | 0.011553 | -0.14191 | 0.14191 | -0.39825 | -0.004578 | 0.009155 | 0.018311 | 0.041199 | 0.19226 | 0.27466 | -0.31586 | 122.3877 | -0.013733 | 122.644 | 122.7814 | -0.14649 | 122.4701 | 0.11902 | 0.25635 | 122.8271 | 122.9782 | 122.7951 | 122.9279 | 122.644 | 123.0606 | 122.8043 | 122.4701 | 122.9279 | 122.644 | 122.8043 | 122.7951 | 123.0606 | -0.55389 | -0.4715
3303.2656 | 123.0881 | -122.8455 | 0.19684 | 0.13817 | 0.010921 | -0.0018244 | 0.040456 | -0.015548 | -0.012971 | 0.011553 | -0.064087 | 0.07782 | -0.37079 | 0.041199 | 0.059509 | 0.09613 | -0.14648 | 0.23804 | 0.22888 | -0.24719 | 122.4747 | -0.11902 | 122.7814 | 122.8867 | -0.13733 | 122.5983 | 0.032044 | 0.3067 | 122.699 | 123.0835 | 122.905 | 122.9233 | 122.7814 | 123.0743 | 122.9416 | 122.5983 | 122.9233 | 122.7814 | 122.9416 | 122.905 | 123.0743 | -0.56763 | -0.44403
3305.0156 | 123.1293 | -122.8134 | 0.19226 | -0.15175 | 0.010493 | -0.0041742 | 0.04067 | -0.01747 | -0.010194 | 0.010057 | -0.022888 | 0.10071 | -0.36621 | 0.1236 | 0.12817 | 0.15564 | -0.17853 | 0.32959 | 0.23804 | -0.27008 | 122.4472 | -0.091553 | 122.7905 | 122.937 | -0.064087 | 122.5433 | 0.045776 | 0.34332 | 122.6349 | 123.143 | 122.9416 | 122.9141 | 122.7905 | 123.0515 | 122.9691 | 122.5433 | 122.9141 | 122.7905 | 122.9691 | 122.9416 | 123.0515 | -0.55847 | -0.46234
3306.7812 | 123.1888 | -122.7905 | 0.16937 | -0.1899 | 0.011775 | -0.0052422 | 0.045156 | -0.018538 | -0.013185 | 0.011126 | -0.12817 | 0.13275 | -0.3891 | 0 | -0.004578 | 0.009155 | 0.054932 | 0.16937 | 0.27466 | -0.3067 | 122.4014 | -0.036622 | 122.6624 | 122.7905 | -0.17395 | 122.4838 | 0.10529 | 0.26092 | 122.8455 | 122.9599 | 122.7859 | 122.9233 | 122.6624 | 123.0652 | 122.7997 | 122.4838 | 122.9233 | 122.6624 | 122.7997 | 122.7859 | 123.0652 | -0.55847 | -0.47607
3308.4844 | 123.0652 | -122.8226 | 0.19684 | 0.18394 | 0.012202 | -0.0071648 | 0.045797 | -0.01512 | -0.013612 | 0.011126 | -0.11444 | 0.15106 | -0.39825 | 0.009155 | 0.013733 | 0.054932 | -0.086975 | 0.17853 | 0.24261 | -0.28381 | 122.4243 | -0.045776 | 122.7081 | 122.8317 | -0.18311 | 122.5388 | 0.045777 | 0.28381 | 122.7356 | 123.0011 | 122.8363 | 122.9736 | 122.7081 | 123.0652 | 122.8775 | 122.5388 | 122.9736 | 122.7081 | 122.8775 | 122.8363 | 123.0652 | -0.59509 | -0.48065
3310.2344 | 123.0515 | -122.8226 | 0.21515 | 0.1992 | 0.01028 | -0.003106 | 0.045156 | -0.015761 | -0.012117 | 0.013903 | -0.022888 | 0.10071 | -0.36621 | 0.091553 | 0.10071 | 0.14191 | -0.20142 | 0.27924 | 0.20142 | -0.28381 | 122.4564 | -0.11444 | 122.7997 | 122.9141 | -0.11444 | 122.5388 | -0.013733 | 0.34332 | 122.6212 | 123.1018 | 122.9233 | 122.9233 | 122.7997 | 123.024 | 122.9645 | 122.5388 | 122.9233 | 122.7997 | 122.9645 | 122.9233 | 123.024 | -0.58136 | -0.49896
3311.9844 | 123.0515 | -122.8226 | 0.21973 | 0.1458 | 0.01028 | -0.008233 | 0.044301 | -0.015761 | -0.010194 | 0.010698 | -0.027466 | 0.082397 | -0.36621 | 0.073242 | 0.10071 | 0.15106 | -0.17395 | 0.27924 | 0.20599 | -0.27008 | 122.4564 | -0.13733 | 122.7951 | 122.8958 | -0.11902 | 122.5525 | -0.013733 | 0.33875 | 122.6486 | 123.1018 | 122.9233 | 122.905 | 122.7951 | 123.0286 | 122.9736 | 122.5525 | 122.905 | 122.7951 | 122.9736 | 122.9233 | 123.0286 | -0.58594 | -0.48981
3313.6875 | 123.111 | -122.818 | 0.18768 | 0.13054 | 0.010493 | -0.0026788 | 0.041097 | -0.016616 | -0.011262 | 0.010057 | -0.059509 | 0.086975 | -0.36163 | 0.064087 | 0.073242 | 0.10986 | -0.16022 | 0.25177 | 0.2243 | -0.25635 | 122.4564 | -0.10071 | 122.7585 | 122.8821 | -0.11444 | 122.5616 | 0.036621 | 0.30212 | 122.6578 | 123.0698 | 122.8912 | 122.905 | 122.7585 | 123.0423 | 122.9279 | 122.5616 | 122.905 | 122.7585 | 122.9279 | 122.8912 | 123.0423 | -0.54932 | -0.44403
3315.4531 | 123.1522 | -122.8226 | 0.17853 | -0.19753 | 0.011134 | -0.0039606 | 0.041738 | -0.016829 | -0.012971 | 0.0089893 | -0.041199 | 0.10071 | -0.36163 | 0.086975 | 0.091553 | 0.11444 | -0.086975 | 0.30212 | 0.22888 | -0.27924 | 122.4609 | -0.07782 | 122.7814 | 122.9095 | -0.086975 | 122.5433 | 0.050354 | 0.32043 | 122.7356 | 123.1247 | 122.9141 | 122.9233 | 122.7814 | 123.0515 | 122.937 | 122.5433 | 122.9233 | 122.7814 | 122.937 | 122.9141 | 123.0515 | -0.54016 | -0.45776
3317.2031 | 123.0789 | -122.8455 | 0.21973 | -0.022049 | 0.010921 | -0.0046014 | 0.04836 | -0.014479 | -0.015107 | 0.011553 | -0.059509 | 0.13275 | -0.39825 | 0.032043 | 0.009155 | 0.027466 | -0.027466 | 0.17853 | 0.26093 | -0.30212 | 122.4472 | -0.086976 | 122.7859 | 122.8775 | -0.21057 | 122.5433 | 0.041198 | 0.33875 | 122.818 | 123.024 | 122.8546 | 122.9782 | 122.7859 | 123.1064 | 122.8729 | 122.5433 | 122.9782 | 122.7859 | 122.8729 | 122.8546 | 123.1064 | -0.61798 | -0.52185
3318.9688 | 123.0469 | -122.8409 | 0.19684 | 0.18394 | 0.01028 | -0.0050286 | 0.042592 | -0.015334 | -0.011262 | 0.011553 | -0.045776 | 0.11444 | -0.36621 | 0.082397 | 0.07782 | 0.13275 | -0.1831 | 0.2655 | 0.23804 | -0.27466 | 122.4747 | -0.082397 | 122.7951 | 122.9233 | -0.11902 | 122.5662 | 0.041199 | 0.32044 | 122.6578 | 123.1064 | 122.9187 | 122.9553 | 122.7951 | 123.0789 | 122.9736 | 122.5662 | 122.9553 | 122.7951 | 122.9736 | 122.9187 | 123.0789 | -0.56305 | -0.4715
3320.6562 | 123.1247 | -122.7859 | 0.16479 | -0.1899 | 0.011989 | -0.0084466 | 0.038533 | -0.019393 | -0.010408 | 0.010057 | -0.027466 | 0.10071 | -0.35706 | 0.10529 | 0.12817 | 0.1236 | -0.13733 | 0.32959 | 0.22888 | -0.28381 | 122.4289 | -0.064087 | 122.7585 | 122.8912 | -0.036621 | 122.5021 | 0.064087 | 0.32959 | 122.6486 | 123.1155 | 122.9141 | 122.8867 | 122.7585 | 123.0148 | 122.9095 | 122.5021 | 122.8867 | 122.7585 | 122.9095 | 122.9141 | 123.0148 | -0.52185 | -0.44861
3322.4062 | 123.1476 | -122.8271 | 0.18768 | -0.1899 | 0.011561 | -0.0011834 | 0.046224 | -0.015761 | -0.014253 | 0.010698 | -0.10529 | 0.15106 | -0.3891 | 0.018311 | 0.032043 | 0.045776 | 0.013733 | 0.20142 | 0.27924 | -0.3067 | 122.438 | -0.036621 | 122.7219 | 122.8455 | -0.15564 | 122.5204 | 0.091553 | 0.28381 | 122.8409 | 123.0286 | 122.8592 | 122.9782 | 122.7219 | 123.1064 | 122.8729 | 122.5204 | 122.9782 | 122.7219 | 122.8729 | 122.8592 | 123.1064 | -0.57678 | -0.49438
3324.1719 | 123.1522 | -122.8363 | 0.16937 | -0.14412 | 0.012416 | -0.006524 | 0.040883 | -0.01512 | -0.0086987 | 0.010057 | -0.032043 | 0.09613 | -0.35706 | 0.11444 | 0.14191 | 0.15564 | -0.15106 | 0.32959 | 0.2243 | -0.27924 | 122.4792 | -0.073243 | 122.8043 | 122.9507 | -0.027466 | 122.5571 | 0.054931 | 0.32501 | 122.6852 | 123.1659 | 122.9782 | 122.9324 | 122.8043 | 123.0606 | 122.9919 | 122.5571 | 122.9324 | 122.8043 | 122.9919 | 122.9782 | 123.0606 | -0.52643 | -0.44861
3325.9219 | 123.1064 | -122.8317 | 0.19684 | 0.10765 | 0.012843 | -0.0056696 | 0.047078 | -0.01512 | -0.013399 | 0.0098437 | -0.12817 | 0.13275 | -0.41657 | -0.022888 | -0.009155 | -0.004578 | 0.018311 | 0.14191 | 0.2655 | -0.31586 | 122.4152 | -0.064087 | 122.7036 | 122.8088 | -0.20599 | 122.5159 | 0.068665 | 0.28839 | 122.85 | 122.9736 | 122.8226 | 122.9645 | 122.7036 | 123.0972 | 122.8271 | 122.5159 | 122.9645 | 122.7036 | 122.8271 | 122.8226 | 123.0972 | -0.6134 | -0.5127
3327.625 | 123.1659 | -122.818 | 0.17853 | -0.22041 | 0.010493 | -0.0078058 | 0.042592 | -0.01747 | -0.010835 | 0.012407 | -0.045776 | 0.12817 | -0.36163 | 0.064087 | 0.07782 | 0.086975 | -0.036621 | 0.25635 | 0.23346 | -0.29297 | 122.4564 | -0.050354 | 122.7722 | 122.8821 | -0.10071 | 122.525 | 0.054931 | 0.31586 | 122.7814 | 123.0743 | 122.8958 | 122.9462 | 122.7722 | 123.0515 | 122.905 | 122.525 | 122.9462 | 122.7722 | 122.905 | 122.8958 | 123.0515 | -0.54016 | -0.4715
3329.3906 | 123.1155 | -122.8455 | 0.20142 | 0.16869 | 0.01028 | -0.0052422 | 0.045797 | -0.013625 | -0.014039 | 0.012621 | -0.13275 | 0.14648 | -0.39825 | -0.036621 | -0.022888 | 0.009155 | -0.013733 | 0.13733 | 0.27008 | -0.29297 | 122.4472 | -0.054932 | 122.7127 | 122.8088 | -0.2243 | 122.5525 | 0.068665 | 0.2655 | 122.8317 | 122.9828 | 122.8226 | 122.9919 | 122.7127 | 123.1155 | 122.8546 | 122.5525 | 122.9919 | 122.7127 | 122.8546 | 122.8226 | 123.1155 | -0.59967 | -0.49438
3331.1406 | 123.111 | -122.8317 | 0.20142 | -0.16701 | 0.011775 | -0.0073786 | 0.045797 | -0.01512 | -0.014039 | 0.011339 | -0.10071 | 0.14648 | -0.40741 | 0.032043 | 0.059509 | 0.059509 | 0 | 0.20142 | 0.25635 | -0.32501 | 122.4243 | -0.054932 | 122.731 | 122.8638 | -0.14191 | 122.5067 | 0.054932 | 0.3067 | 122.8317 | 123.0331 | 122.8912 | 122.9782 | 122.731 | 123.0881 | 122.8912 | 122.5067 | 122.9782 | 122.731 | 122.8912 | 122.8912 | 123.0881 | -0.60883 | -0.52643
3332.8906 | 123.056 | -122.8683 | 0.21057 | -0.13649 | 0.012202 | -0.0052422 | 0.045797 | -0.016829 | -0.012758 | 0.012194 | -0.073242 | 0.11902 | -0.40283 | 0.036621 | 0.036621 | 0.073242 | -0.036621 | 0.21973 | 0.25177 | -0.30212 | 122.4655 | -0.091552 | 122.7951 | 122.905 | -0.17395 | 122.5662 | 0.041199 | 0.32959 | 122.8317 | 123.0881 | 122.905 | 122.9874 | 122.7951 | 123.1201 | 122.9416 | 122.5662 | 122.9874 | 122.7951 | 122.9416 | 122.905 | 123.1201 | -0.6134 | -0.5127
3334.5938 | 123.0515 | -122.8821 | 0.21515 | 0.13054 | 0.010066 | -0.0063104 | 0.039174 | -0.016829 | -0.0099805 | 0.010485 | -0.050354 | 0.1236 | -0.3479 | 0.07782 | 0.10529 | 0.14191 | -0.17853 | 0.25635 | 0.21973 | -0.26093 | 122.5342 | -0.091553 | 122.8317 | 122.9599 | -0.10986 | 122.6212 | 0.004578 | 0.29755 | 122.7036 | 123.1384 | 122.9874 | 123.0057 | 122.8317 | 123.1018 | 123.024 | 122.6212 | 123.0057 | 122.8317 | 123.024 | 122.9874 | 123.1018 | -0.56305 | -0.47607
3336.3438 | 123.0698 | -122.8455 | 0.21973 | -0.022049 | 0.013057 | -0.0024652 | 0.048787 | -0.014907 | -0.012971 | 0.0092029 | -0.086975 | 0.12817 | -0.39825 | 0.009155 | 0 | 0.036621 | -0.009155 | 0.16022 | 0.25177 | -0.3067 | 122.4472 | -0.091553 | 122.7585 | 122.8546 | -0.21973 | 122.5388 | 0.032043 | 0.31128 | 122.8363 | 123.0057 | 122.8455 | 122.9736 | 122.7585 | 123.0972 | 122.8821 | 122.5388 | 122.9736 | 122.7585 | 122.8821 | 122.8455 | 123.0972 | -0.61798 | -0.52643
3338.0938 | 123.0515 | -122.8775 | 0.21973 | -0.1136 | 0.014766 | -0.0039606 | 0.047933 | -0.015334 | -0.015107 | 0.010271 | -0.07782 | 0.12817 | -0.40741 | 0.027466 | 0.064087 | 0.068665 | -0.032043 | 0.22888 | 0.25635 | -0.28839 | 122.4701 | -0.091553 | 122.7997 | 122.905 | -0.15564 | 122.5891 | 0.036621 | 0.32959 | 122.8455 | 123.1064 | 122.9416 | 123.0057 | 122.7997 | 123.1339 | 122.9462 | 122.5891 | 123.0057 | 122.7997 | 122.9462 | 122.9416 | 123.1339 | -0.62714 | -0.50812
3339.7969 | 123.0331 | -122.818 | 0.21057 | 0.18394 | 0.010707 | -0.0041742 | 0.041097 | -0.014693 | -0.012117 | 0.013903 | -0.036621 | 0.10071 | -0.3479 | 0.082397 | 0.11444 | 0.17395 | -0.18768 | 0.28381 | 0.2243 | -0.27008 | 122.4701 | -0.10986 | 122.7814 | 122.9004 | -0.09613 | 122.5479 | 0.013733 | 0.31128 | 122.6303 | 123.1018 | 122.9324 | 122.9187 | 122.7814 | 123.0423 | 122.9919 | 122.5479 | 122.9187 | 122.7814 | 122.9919 | 122.9324 | 123.0423 | -0.55847 | -0.48065
3341.5625 | 123.0331 | -122.8455 | 0.21515 | 0.18394 | 0.011348 | -0.0043878 | 0.041951 | -0.016616 | -0.01233 | 0.01198 | -0.027466 | 0.10529 | -0.35706 | 0.086975 | 0.10986 | 0.16479 | -0.18768 | 0.28381 | 0.20599 | -0.26093 | 122.4884 | -0.10986 | 122.818 | 122.9324 | -0.10529 | 122.5845 | -0.009155 | 0.32959 | 122.6578 | 123.1293 | 122.9553 | 122.9507 | 122.818 | 123.0515 | 123.0103 | 122.5845 | 122.9507 | 122.818 | 123.0103 | 122.9553 | 123.0515 | -0.5722 | -0.47607
3343.25 | 123.0698 | -122.8271 | 0.19226 | 0.10765 | 0.0094251 | -0.0024652 | 0.039815 | -0.015975 | -0.011903 | 0.011339 | -0.07782 | 0.10071 | -0.35706 | 0.068665 | 0.091553 | 0.13733 | -0.16479 | 0.27466 | 0.21973 | -0.28381 | 122.4701 | -0.091553 | 122.7493 | 122.8958 | -0.10071 | 122.5433 | 0.027466 | 0.27924 | 122.6624 | 123.1018 | 122.9187 | 122.9279 | 122.7493 | 123.0469 | 122.9645 | 122.5433 | 122.9279 | 122.7493 | 122.9645 | 122.9187 | 123.0469 | -0.54932 | -0.47607
3345 | 123.0469 | -122.8546 | 0.19684 | 0.16106 | 0.011775 | -0.003747 | 0.042806 | -0.017897 | -0.011476 | 0.011339 | -0.036621 | 0.091553 | -0.34332 | 0.059509 | 0.091553 | 0.15106 | -0.17853 | 0.28381 | 0.20599 | -0.28381 | 122.5113 | -0.10529 | 122.818 | 122.9141 | -0.10529 | 122.5708 | 0.009156 | 0.3067 | 122.6761 | 123.1384 | 122.9462 | 122.9462 | 122.818 | 123.0606 | 123.0057 | 122.5708 | 122.9462 | 122.818 | 123.0057 | 122.9462 | 123.0606 | -0.54016 | -0.48065
3346.75 | 123.0377 | -122.818 | 0.19684 | 0.1992 | 0.011561 | -0.00096983 | 0.046224 | -0.015334 | -0.01233 | 0.01198 | -0.082397 | 0.12817 | -0.38452 | 0.045776 | 0.064087 | 0.1236 | -0.15106 | 0.25177 | 0.22888 | -0.27466 | 122.4335 | -0.068664 | 122.7356 | 122.8638 | -0.13275 | 122.5433 | 0.032044 | 0.30212 | 122.6669 | 123.0698 | 122.8821 | 122.9462 | 122.7356 | 123.0469 | 122.9416 | 122.5433 | 122.9462 | 122.7356 | 122.9416 | 122.8821 | 123.0469 | -0.58136 | -0.4715
3348.5156 | 123.1613 | -122.8134 | 0.16479 | -0.060196 | 0.014338 | -0.0093012 | 0.040456 | -0.018538 | -0.01233 | 0.010485 | -0.086975 | 0.11902 | -0.37994 | 0.068665 | 0.09613 | 0.11902 | -0.11902 | 0.27466 | 0.23346 | -0.30212 | 122.4335 | -0.045776 | 122.7264 | 122.8821 | -0.068665 | 122.5113 | 0.068664 | 0.29297 | 122.6944 | 123.0881 | 122.9095 | 122.9324 | 122.7264 | 123.0469 | 122.9324 | 122.5113 | 122.9324 | 122.7264 | 122.9324 | 122.9095 | 123.0469 | -0.54474 | -0.46692
3350.2344 | 123.1201 | -122.8317 | 0.17395 | -0.21278 | 0.010921 | -0.0071648 | 0.041951 | -0.020674 | -0.01233 | 0.0087757 | -0.032043 | 0.10986 | -0.36621 | 0.11444 | 0.11444 | 0.14648 | -0.11902 | 0.32959 | 0.21057 | -0.29755 | 122.4655 | -0.064087 | 122.7997 | 122.9462 | -0.059509 | 122.5342 | 0.036621 | 0.33417 | 122.7127 | 123.1613 | 122.9462 | 122.9416 | 122.7997 | 123.0423 | 122.9782 | 122.5342 | 122.9416 | 122.7997 | 122.9782 | 122.9462 | 123.0423 | -0.54016 | -0.4715
3351.9844 | 123.0972 | -122.7859 | 0.20142 | 0.13054 | 0.011561 | -0.0035332 | 0.047506 | -0.017684 | -0.014253 | 0.01198 | -0.11902 | 0.14191 | -0.39368 | -0.013733 | -0.018311 | 0.022888 | -0.045776 | 0.15564 | 0.25635 | -0.32044 | 122.3923 | -0.059509 | 122.6669 | 122.7722 | -0.21973 | 122.4655 | 0.054932 | 0.27466 | 122.7402 | 122.9416 | 122.7676 | 122.9279 | 122.6669 | 123.0423 | 122.8088 | 122.4655 | 122.9279 | 122.6669 | 122.8088 | 122.7676 | 123.0423 | -0.59509 | -0.52185
3353.7344 | 123.0652 | -122.8271 | 0.21057 | -0.067826 | 0.010921 | -0.0026788 | 0.046865 | -0.017256 | -0.013399 | 0.0094165 | -0.068665 | 0.13275 | -0.39825 | 0.054932 | 0.032043 | 0.050354 | -0.018311 | 0.2243 | 0.2655 | -0.30212 | 122.4289 | -0.07782 | 122.7585 | 122.8821 | -0.17853 | 122.525 | 0.054932 | 0.32959 | 122.8088 | 123.0515 | 122.8592 | 122.9599 | 122.7585 | 123.0927 | 122.8775 | 122.525 | 122.9599 | 122.7585 | 122.8775 | 122.8592 | 123.0927 | -0.60882 | -0.5127
3355.5 | 123.056 | -122.8363 | 0.20142 | 0.1992 | 0.0098523 | -0.001397 | 0.041524 | -0.016188 | -0.010835 | 0.0098437 | -0.013733 | 0.10071 | -0.3479 | 0.086975 | 0.086975 | 0.13733 | -0.19226 | 0.28381 | 0.2243 | -0.28381 | 122.4884 | -0.10071 | 122.8226 | 122.9233 | -0.11444 | 122.5525 | 0.022888 | 0.33417 | 122.644 | 123.1201 | 122.9233 | 122.937 | 122.8226 | 123.0606 | 122.9736 | 122.5525 | 122.937 | 122.8226 | 122.9736 | 122.9233 | 123.0606 | -0.54932 | -0.48523
3357.25 | 123.1064 | -122.8455 | 0.17853 | 0.10002 | 0.012843 | -0.0071648 | 0.045797 | -0.015761 | -0.012971 | 0.011126 | -0.12817 | 0.15106 | -0.40283 | -0.013733 | -0.004578 | 0.009155 | -0.050354 | 0.14648 | 0.27008 | -0.3067 | 122.4426 | -0.027466 | 122.7173 | 122.8317 | -0.18311 | 122.5388 | 0.091553 | 0.27466 | 122.7951 | 122.9919 | 122.8409 | 122.9965 | 122.7173 | 123.1155 | 122.8546 | 122.5388 | 122.9965 | 122.7173 | 122.8546 | 122.8409 | 123.1155 | -0.58136 | -0.48523
3359 | 123.1155 | -122.7951 | 0.18768 | 0.10765 | 0.0085705 | -0.0063104 | 0.039815 | -0.016829 | -0.010194 | 0.010912 | -0.09613 | 0.086975 | -0.38452 | 0.059509 | 0.059509 | 0.09613 | -0.13733 | 0.24261 | 0.23346 | -0.27924 | 122.4106 | -0.10071 | 122.699 | 122.8546 | -0.12817 | 122.5159 | 0.045776 | 0.28839 | 122.6578 | 123.0377 | 122.8546 | 122.8821 | 122.699 | 123.0286 | 122.8912 | 122.5159 | 122.8821 | 122.699 | 122.8912 | 122.8546 | 123.0286 | -0.5722 | -0.46692
3360.6875 | 123.1338 | -122.818 | 0.17395 | -0.1899 | 0.013484 | -0.010369 | 0.042592 | -0.019179 | -0.010621 | 0.011766 | -0.027466 | 0.10529 | -0.35706 | 0.091553 | 0.11444 | 0.15106 | -0.11902 | 0.32501 | 0.22888 | -0.27008 | 122.4609 | -0.068664 | 122.7905 | 122.9095 | -0.059509 | 122.5479 | 0.054932 | 0.32959 | 122.699 | 123.143 | 122.9324 | 122.9233 | 122.7905 | 123.0469 | 122.9691 | 122.5479 | 122.9233 | 122.7905 | 122.9691 | 122.9324 | 123.0469 | -0.53101 | -0.44403
3362.4531 | 123.1384 | -122.8134 | 0.19226 | 0.077133 | 0.0098523 | -0.0054558 | 0.041951 | -0.019606 | -0.0082715 | 0.011553 | -0.082397 | 0.10071 | -0.37537 | 0.041199 | 0.054932 | 0.10529 | -0.1236 | 0.24719 | 0.22888 | -0.28381 | 122.4381 | -0.091553 | 122.731 | 122.8546 | -0.13733 | 122.5296 | 0.036621 | 0.29297 | 122.6898 | 123.0606 | 122.8683 | 122.9141 | 122.731 | 123.0423 | 122.9187 | 122.5296 | 122.9141 | 122.731 | 122.9187 | 122.8683 | 123.0423 | -0.56763 | -0.47607
3364.1562 | 123.1888 | -122.7905 | 0.16937 | -0.27382 | 0.011134 | -0.0052422 | 0.045156 | -0.019393 | -0.014467 | 0.0098437 | -0.15106 | 0.12817 | -0.41199 | -0.022888 | -0.004578 | 0.009155 | 0.064087 | 0.16937 | 0.2655 | -0.31128 | 122.3785 | -0.041199 | 122.6395 | 122.7676 | -0.17395 | 122.4792 | 0.09613 | 0.26092 | 122.8546 | 122.9599 | 122.7859 | 122.9187 | 122.6395 | 123.056 | 122.7997 | 122.4792 | 122.9187 | 122.6395 | 122.7997 | 122.7859 | 123.056 | -0.58136 | -0.48065
3365.9062 | 123.1979 | -122.8043 | 0.16479 | 0.023727 | 0.01028 | -0.012078 | 0.040029 | -0.01982 | -0.01169 | 0.011553 | -0.11444 | 0.13275 | -0.38452 | 0.041199 | 0.059509 | 0.073242 | -0.10071 | 0.24261 | 0.23804 | -0.29755 | 122.4197 | -0.032044 | 122.6898 | 122.8455 | -0.10529 | 122.5067 | 0.073242 | 0.27008 | 122.7036 | 123.0469 | 122.8638 | 122.937 | 122.6898 | 123.0423 | 122.8775 | 122.5067 | 122.937 | 122.6898 | 122.8775 | 122.8638 | 123.0423 | -0.54932 | -0.46234
3367.6562 | 123.0881 | -122.8683 | 0.21973 | 0.023727 | 0.013057 | -0.0028924 | 0.048574 | -0.015975 | -0.012971 | 0.0094165 | -0.10986 | 0.1236 | -0.42114 | -0.009155 | -0.027466 | -0.009155 | -0.013733 | 0.14648 | 0.25635 | -0.29755 | 122.4472 | -0.096131 | 122.7585 | 122.8592 | -0.24719 | 122.5708 | 0.036621 | 0.31128 | 122.8546 | 123.0148 | 122.8409 | 122.9919 | 122.7585 | 123.1247 | 122.8592 | 122.5708 | 122.9919 | 122.7585 | 122.8592 | 122.8409 | 123.1247 | -0.64087 | -0.51727
3369.3594 | 123.1522 | -122.7997 | 0.18768 | -0.17464 | 0.011989 | -0.0056696 | 0.045797 | -0.015761 | -0.014039 | 0.0089893 | -0.11902 | 0.16479 | -0.40283 | 0.013733 | 0.004578 | 0.022888 | 0.036621 | 0.1831 | 0.26093 | -0.32044 | 122.3969 | -0.022888 | 122.6807 | 122.8134 | -0.1831 | 122.4792 | 0.073242 | 0.28381 | 122.8363 | 122.9828 | 122.8043 | 122.9645 | 122.6807 | 123.0606 | 122.8226 | 122.4792 | 122.9645 | 122.6807 | 122.8226 | 122.8043 | 123.0606 | -0.59052 | -0.50812
3371.1094 | 123.0881 | -122.85 | 0.1831 | 0.13054 | 0.011348 | -0.008233 | 0.042165 | -0.016402 | -0.0097669 | 0.011126 | -0.054932 | 0.10986 | -0.37079 | 0.050354 | 0.07782 | 0.11902 | -0.14191 | 0.25635 | 0.21973 | -0.30212 | 122.4792 | -0.073242 | 122.7951 | 122.9004 | -0.10528 | 122.5479 | 0.036622 | 0.31586 | 122.7081 | 123.1064 | 122.9279 | 122.9599 | 122.7951 | 123.0698 | 122.9691 | 122.5479 | 122.9599 | 122.7951 | 122.9691 | 122.9279 | 123.0698 | -0.55389 | -0.48523
3372.8281 | 123.0743 | -122.85 | 0.21057 | -0.037308 | 0.012843 | -0.0043878 | 0.049001 | -0.015548 | -0.012971 | 0.011339 | -0.07782 | 0.13275 | -0.41199 | 0.027466 | 0.009155 | 0.027466 | -0.013733 | 0.1831 | 0.24719 | -0.31586 | 122.4381 | -0.07782 | 122.7722 | 122.8775 | -0.20142 | 122.5342 | 0.036621 | 0.33417 | 122.8363 | 123.0331 | 122.8592 | 122.9828 | 122.7722 | 123.0972 | 122.8775 | 122.5342 | 122.9828 | 122.7722 | 122.8775 | 122.8592 | 123.0972 | -0.62256 | -0.52643
3374.5938 | 123.0606 | -122.8455 | 0.19684 | -0.01442 | 0.011989 | -0.0069512 | 0.047292 | -0.016616 | -0.013612 | 0.013262 | -0.09613 | 0.13275 | -0.41199 | 0.018311 | 0.009155 | 0.022888 | -0.022888 | 0.17853 | 0.27924 | -0.31128 | 122.4335 | -0.064087 | 122.7493 | 122.8638 | -0.18768 | 122.5342 | 0.082398 | 0.31586 | 122.8226 | 123.024 | 122.8546 | 122.9782 | 122.7493 | 123.1247 | 122.8683 | 122.5342 | 122.9782 | 122.7493 | 122.8683 | 122.8546 | 123.1247 | -0.60882 | -0.50812
3376.3438 | 123.1338 | -122.818 | 0.17853 | -0.22804 | 0.011561 | -0.01101 | 0.039388 | -0.017043 | -0.011049 | 0.010912 | -0.032043 | 0.10986 | -0.35248 | 0.091553 | 0.11902 | 0.14191 | -0.11902 | 0.3067 | 0.2243 | -0.29755 | 122.4655 | -0.068665 | 122.7859 | 122.9095 | -0.059509 | 122.5204 | 0.045776 | 0.32044 | 122.699 | 123.1247 | 122.937 | 122.9279 | 122.7859 | 123.0423 | 122.9599 | 122.5204 | 122.9279 | 122.7859 | 122.9599 | 122.937 | 123.0423 | -0.53101 | -0.47607
3378.0938 | 123.1384 | -122.8088 | 0.17853 | 0.077133 | 0.010493 | -0.0086602 | 0.041738 | -0.018752 | -0.010408 | 0.010698 | -0.091553 | 0.11444 | -0.38452 | 0.018311 | 0.059509 | 0.091553 | -0.11444 | 0.25177 | 0.2243 | -0.29297 | 122.4243 | -0.064087 | 122.7173 | 122.8271 | -0.11902 | 122.5159 | 0.045776 | 0.29297 | 122.6944 | 123.0606 | 122.8683 | 122.9233 | 122.7173 | 123.0331 | 122.9004 | 122.5159 | 122.9233 | 122.7173 | 122.9004 | 122.8683 | 123.0331 | -0.56305 | -0.4715
3379.7969 | 123.1979 | -122.7905 | 0.1831 | -0.25093 | 0.010493 | -0.0067376 | 0.044942 | -0.019393 | -0.011476 | 0.010271 | -0.086975 | 0.13275 | -0.41199 | 0.004578 | 0.022888 | 0.027466 | 0.032043 | 0.20142 | 0.24261 | -0.32501 | 122.3785 | -0.050354 | 122.7036 | 122.7951 | -0.16022 | 122.4655 | 0.05951 | 0.32501 | 122.8226 | 122.9919 | 122.8134 | 122.9233 | 122.7036 | 123.0331 | 122.818 | 122.4655 | 122.9233 | 122.7036 | 122.818 | 122.8134 | 123.0331 | -0.59509 | -0.50812
3381.5469 | 123.0606 | -122.8775 | 0.20142 | -0.052567 | 0.010707 | -0.0063104 | 0.047506 | -0.016402 | -0.012758 | 0.012194 | -0.09613 | 0.13275 | -0.40283 | 0.022888 | 0.009155 | 0.045776 | -0.022888 | 0.1831 | 0.27008 | -0.29755 | 122.4747 | -0.068665 | 122.7814 | 122.9004 | -0.19226 | 122.58 | 0.068665 | 0.3067 | 122.8546 | 123.0606 | 122.8867 | 123.0103 | 122.7814 | 123.1476 | 122.9233 | 122.58 | 123.0103 | 122.7814 | 122.9233 | 122.8867 | 123.1476 | -0.60425 | -0.49896
3383.2344 | 123.1247 | -122.8592 | 0.17395 | 0.069504 | 0.010066 | -0.0043878 | 0.040029 | -0.01512 | -0.014253 | 0.011126 | -0.1236 | 0.09613 | -0.37994 | 0.022888 | 0.064087 | 0.09613 | -0.13733 | 0.24261 | 0.23346 | -0.29297 | 122.4792 | -0.07782 | 122.7356 | 122.8821 | -0.10986 | 122.5662 | 0.059509 | 0.25635 | 122.7219 | 123.1018 | 122.9233 | 122.9553 | 122.7356 | 123.0927 | 122.9553 | 122.5662 | 122.9553 | 122.7356 | 122.9553 | 122.9233 | 123.0927 | -0.55389 | -0.46692
3385 | 123.0606 | -122.8546 | 0.20142 | -0.1136 | 0.011989 | -0.0056696 | 0.045369 | -0.018538 | -0.012117 | 0.013048 | -0.10986 | 0.11444 | -0.43488 | 0.050354 | 0.045776 | 0.054932 | -0.027466 | 0.21515 | 0.2655 | -0.31586 | 122.4197 | -0.086975 | 122.7448 | 122.905 | -0.15564 | 122.5388 | 0.064087 | 0.32501 | 122.8271 | 123.0698 | 122.9004 | 122.9691 | 122.7448 | 123.1201 | 122.9095 | 122.5388 | 122.9691 | 122.7448 | 122.9095 | 122.9004 | 123.1201 | -0.63629 | -0.51727
3386.75 | 123.175 | -122.8226 | 0.1831 | -0.0067901 | 0.010493 | -0.0075922 | 0.038106 | -0.018111 | -0.011903 | 0.0098437 | -0.11444 | 0.09613 | -0.39368 | 0.036621 | 0.07782 | 0.11444 | -0.11444 | 0.27466 | 0.23346 | -0.27466 | 122.4289 | -0.086975 | 122.7081 | 122.8592 | -0.10528 | 122.5479 | 0.050354 | 0.27924 | 122.7081 | 123.0972 | 122.9004 | 122.9187 | 122.7081 | 123.056 | 122.937 | 122.5479 | 122.9187 | 122.7081 | 122.937 | 122.9004 | 123.056 | -0.57678 | -0.45776
3388.4531 | 123.1705 | -122.8088 | 0.17853 | -0.1899 | 0.011348 | -0.0060968 | 0.046437 | -0.017043 | -0.013612 | 0.011126 | -0.14191 | 0.13733 | -0.42114 | 0.013733 | 0.004578 | 0.018311 | 0.027466 | 0.18768 | 0.27466 | -0.3067 | 122.3877 | -0.041199 | 122.6669 | 122.8226 | -0.17395 | 122.5021 | 0.09613 | 0.27924 | 122.8363 | 122.9965 | 122.8134 | 122.9462 | 122.6669 | 123.0835 | 122.8271 | 122.5021 | 122.9462 | 122.6669 | 122.8271 | 122.8134 | 123.0835 | -0.59967 | -0.48523
3390.2344 | 123.1796 | -122.7631 | 0.16022 | 0.023727 | 0.011775 | -0.0056696 | 0.039388 | -0.017256 | -0.0091259 | 0.0098437 | -0.09613 | 0.10529 | -0.37994 | 0.032043 | 0.073242 | 0.091553 | -0.10071 | 0.25177 | 0.24719 | -0.29755 | 122.3831 | -0.054931 | 122.6669 | 122.7951 | -0.086975 | 122.4655 | 0.086975 | 0.28381 | 122.6624 | 123.0148 | 122.8363 | 122.8683 | 122.6669 | 123.0103 | 122.8546 | 122.4655 | 122.8683 | 122.6669 | 122.8546 | 122.8363 | 123.0103 | -0.54016 | -0.45776
3391.9844 | 123.1888 | -122.7676 | 0.14648 | 0.046615 | 0.013057 | -0.0054558 | 0.04131 | -0.018325 | -0.010408 | 0.011126 | -0.11444 | 0.091553 | -0.40283 | 0.045776 | 0.064087 | 0.09613 | -0.10986 | 0.24261 | 0.23346 | -0.29755 | 122.3648 | -0.054931 | 122.6532 | 122.8134 | -0.082397 | 122.4701 | 0.086975 | 0.28839 | 122.6578 | 123.0103 | 122.8317 | 122.8592 | 122.6532 | 123.0011 | 122.8638 | 122.4701 | 122.8592 | 122.6532 | 122.8638 | 122.8317 | 123.0011 | -0.54932 | -0.44403
3393.6719 | 123.1247 | -122.8455 | 0.19226 | -0.17464 | 0.0092115 | -0.008233 | 0.044301 | -0.018965 | -0.010408 | 0.011339 | -0.050354 | 0.07782 | -0.37994 | 0.1236 | 0.10529 | 0.15106 | -0.14191 | 0.32501 | 0.24261 | -0.28839 | 122.4655 | -0.11444 | 122.7951 | 122.9691 | -0.086975 | 122.5571 | 0.050354 | 0.32959 | 122.7036 | 123.1705 | 122.9507 | 122.9233 | 122.7951 | 123.0881 | 122.9965 | 122.5571 | 122.9233 | 122.7951 | 122.9965 | 122.9507 | 123.0881 | -0.5722 | -0.48065
3395.4531 | 123.0515 | -122.8546 | 0.2243 | -0.029679 | 0.01028 | -0.003106 | 0.049428 | -0.015975 | -0.015107 | 0.0089893 | -0.091553 | 0.13275 | -0.4303 | 0.041199 | 0.009155 | 0.027466 | -0.018311 | 0.17853 | 0.25177 | -0.29755 | 122.4243 | -0.091553 | 122.7631 | 122.8958 | -0.21515 | 122.5571 | 0.027466 | 0.33875 | 122.8363 | 123.0331 | 122.8638 | 122.9874 | 122.7631 | 123.1064 | 122.8821 | 122.5571 | 122.9874 | 122.7631 | 122.8821 | 122.8638 | 123.1064 | -0.6546 | -0.52185
3397.1562 | 123.1522 | -122.8043 | 0.1831 | -0.022049 | 0.0079297 | -0.009942 | 0.040029 | -0.019393 | -0.010194 | 0.010912 | -0.10529 | 0.082397 | -0.39368 | 0.064087 | 0.091553 | 0.1236 | -0.13275 | 0.29297 | 0.23346 | -0.27466 | 122.4106 | -0.10071 | 122.699 | 122.8683 | -0.091552 | 122.5296 | 0.050354 | 0.28839 | 122.6715 | 123.0972 | 122.8958 | 122.8867 | 122.699 | 123.0377 | 122.9279 | 122.5296 | 122.8867 | 122.699 | 122.9279 | 122.8958 | 123.0377 | -0.57678 | -0.45776
3398.9062 | 123.1064 | -122.8134 | 0.19226 | 0.16106 | 0.012843 | -0.0033196 | 0.048146 | -0.016402 | -0.010835 | 0.010057 | -0.14191 | 0.13733 | -0.40283 | -0.022888 | -0.022888 | -0.013733 | -0.009155 | 0.11902 | 0.2655 | -0.32044 | 122.4106 | -0.054932 | 122.6715 | 122.7905 | -0.21515 | 122.493 | 0.073242 | 0.26093 | 122.8043 | 122.9324 | 122.7905 | 122.9507 | 122.6715 | 123.0789 | 122.7997 | 122.493 | 122.9507 | 122.6715 | 122.7997 | 122.7905 | 123.0789 | -0.59509 | -0.5127
3400.6719 | 123.1064 | -122.8363 | 0.19684 | 0.054245 | 0.011561 | -0.0056696 | 0.049215 | -0.017043 | -0.010835 | 0.010057 | -0.15106 | 0.13733 | -0.43488 | -0.022888 | -0.013733 | -0.013733 | 0.018311 | 0.11444 | 0.29297 | -0.32501 | 122.4014 | -0.059509 | 122.6852 | 122.8134 | -0.21057 | 122.5113 | 0.096131 | 0.28381 | 122.8546 | 122.9507 | 122.8226 | 122.9736 | 122.6852 | 123.1293 | 122.8226 | 122.5113 | 122.9736 | 122.6852 | 122.8226 | 122.8226 | 123.1293 | -0.63171 | -0.52185
3402.4375 | 123.1018 | -122.8729 | 0.1831 | 0.15343 | 0.01028 | -0.0035332 | 0.040029 | -0.018325 | -0.011476 | 0.011339 | -0.082397 | 0.09613 | -0.37994 | 0.050354 | 0.036621 | 0.10529 | -0.13733 | 0.24719 | 0.22888 | -0.27466 | 122.493 | -0.086975 | 122.7905 | 122.9233 | -0.14648 | 122.5983 | 0.045777 | 0.29755 | 122.7356 | 123.1201 | 122.9095 | 122.9691 | 122.7905 | 123.1018 | 122.9782 | 122.5983 | 122.9691 | 122.7905 | 122.9782 | 122.9095 | 123.1018 | -0.56305 | -0.45776
3404.1875 | 123.1613 | -122.7859 | 0.16479 | 0.031357 | 0.01028 | -0.002038 | 0.04067 | -0.01747 | -0.010621 | 0.012621 | -0.1236 | 0.10986 | -0.40283 | 0.032043 | 0.054932 | 0.082397 | -0.10529 | 0.23346 | 0.23346 | -0.29755 | 122.3831 | -0.054932 | 122.6624 | 122.818 | -0.10986 | 122.4884 | 0.068664 | 0.27924 | 122.6807 | 123.0194 | 122.8409 | 122.8958 | 122.6624 | 123.0194 | 122.8683 | 122.4884 | 122.8958 | 122.6624 | 122.8683 | 122.8409 | 123.0194 | -0.56763 | -0.46234
3405.875 | 123.1384 | -122.8455 | 0.18768 | -0.20515 | 0.011775 | -0.0035332 | 0.04067 | -0.017256 | -0.011049 | 0.010485 | -0.068665 | 0.068665 | -0.37079 | 0.10529 | 0.11444 | 0.12817 | -0.13275 | 0.32501 | 0.23804 | -0.28839 | 122.4747 | -0.11902 | 122.7768 | 122.9507 | -0.073242 | 122.5571 | 0.050354 | 0.30212 | 122.7127 | 123.1705 | 122.9599 | 122.9141 | 122.7768 | 123.0835 | 122.9736 | 122.5571 | 122.9141 | 122.7768 | 122.9736 | 122.9599 | 123.0835 | -0.55847 | -0.47607
3407.625 | 123.2071 | -122.7905 | 0.16937 | -0.1899 | 0.013057 | -0.011224 | 0.044942 | -0.01747 | -0.011049 | 0.0094165 | -0.13733 | 0.1236 | -0.44403 | -0.013733 | -0.004578 | 0.004578 | 0.059509 | 0.17853 | 0.28381 | -0.32959 | 122.3465 | -0.045777 | 122.6532 | 122.7768 | -0.17395 | 122.4609 | 0.11444 | 0.3067 | 122.85 | 122.9691 | 122.7859 | 122.9141 | 122.6532 | 123.0743 | 122.7951 | 122.4609 | 122.9141 | 122.6532 | 122.7951 | 122.7859 | 123.0743 | -0.6134 | -0.49896
3409.3125 | 123.0515 | -122.8317 | 0.21515 | 0.22972 | 0.011561 | -0.006524 | 0.04601 | -0.016188 | -0.013612 | 0.0087757 | -0.09613 | 0.10071 | -0.42114 | 0.050354 | 0.073242 | 0.11902 | -0.14191 | 0.23346 | 0.24261 | -0.28381 | 122.4106 | -0.11444 | 122.7356 | 122.8821 | -0.14191 | 122.5479 | 0.027466 | 0.32501 | 122.6898 | 123.0652 | 122.905 | 122.9324 | 122.7356 | 123.0743 | 122.9507 | 122.5479 | 122.9324 | 122.7356 | 122.9507 | 122.905 | 123.0743 | -0.63629 | -0.49896
3411.0781 | 123.0515 | -122.8455 | 0.20599 | 0.1992 | 0.013057 | -0.0069512 | 0.045369 | -0.016402 | -0.0093395 | 0.01198 | -0.054932 | 0.086975 | -0.37537 | 0.086975 | 0.09613 | 0.13275 | -0.20599 | 0.27924 | 0.21973 | -0.27924 | 122.4701 | -0.11902 | 122.7905 | 122.9324 | -0.10986 | 122.5662 | 0.013733 | 0.32043 | 122.6395 | 123.1247 | 122.9416 | 122.9324 | 122.7905 | 123.0652 | 122.9782 | 122.5662 | 122.9324 | 122.7905 | 122.9782 | 122.9416 | 123.0652 | -0.58136 | -0.48523
3412.7812 | 123.0881 | -122.8409 | 0.19226 | 0.13817 | 0.010921 | -0.0022516 | 0.047933 | -0.015761 | -0.011903 | 0.0096301 | -0.16937 | 0.11902 | -0.4303 | -0.018311 | -0.022888 | -0.004578 | -0.027466 | 0.13733 | 0.25635 | -0.3067 | 122.4106 | -0.073242 | 122.6715 | 122.8226 | -0.21515 | 122.5342 | 0.064087 | 0.26093 | 122.8134 | 122.9782 | 122.818 | 122.9599 | 122.6715 | 123.0972 | 122.8363 | 122.5342 | 122.9599 | 122.6715 | 122.8363 | 122.818 | 123.0972 | -0.62256 | -0.49896
3414.5312 | 123.0972 | -122.85 | 0.19684 | 0.038986 | 0.012202 | -0.00075623 | 0.048574 | -0.015761 | -0.013185 | 0.013048 | -0.12817 | 0.11902 | -0.44861 | -0.009155 | -0.032043 | 0.018311 | -0.013733 | 0.13733 | 0.2655 | -0.29755 | 122.4014 | -0.077819 | 122.7219 | 122.8409 | -0.22888 | 122.5525 | 0.068665 | 0.32043 | 122.8363 | 122.9874 | 122.818 | 122.9691 | 122.7219 | 123.1155 | 122.8683 | 122.5525 | 122.9691 | 122.7219 | 122.8683 | 122.818 | 123.1155 | -0.64545 | -0.49438
3416.2969 | 123.1705 | -122.818 | 0.19226 | 0.084762 | 0.012629 | -0.0046014 | 0.03832 | -0.018325 | -0.010194 | 0.011339 | -0.10529 | 0.09613 | -0.3891 | 0.027466 | 0.064087 | 0.10529 | -0.10071 | 0.24261 | 0.23346 | -0.29755 | 122.4289 | -0.096131 | 122.7127 | 122.8455 | -0.12817 | 122.5204 | 0.041198 | 0.28381 | 122.7173 | 123.0606 | 122.8821 | 122.9141 | 122.7127 | 123.0515 | 122.9233 | 122.5204 | 122.9141 | 122.7127 | 122.9233 | 122.8821 | 123.0515 | -0.58136 | -0.48981
3418.0469 | 123.1018 | -122.8409 | 0.19684 | 0.12291 | 0.013484 | -0.0054558 | 0.047506 | -0.015761 | -0.012544 | 0.010912 | -0.15564 | 0.12817 | -0.44403 | -0.032043 | -0.022888 | 0.022888 | -0.009155 | 0.13733 | 0.26093 | -0.32501 | 122.3969 | -0.068664 | 122.6852 | 122.8088 | -0.21973 | 122.5159 | 0.064087 | 0.28839 | 122.8317 | 122.9782 | 122.818 | 122.9691 | 122.6852 | 123.1018 | 122.8638 | 122.5159 | 122.9691 | 122.6852 | 122.8638 | 122.818 | 123.1018 | -0.64087 | -0.52185
3419.7344 | 123.0789 | -122.8729 | 0.20142 | 0.13054 | 0.011348 | -0.0054558 | 0.043233 | -0.01512 | -0.01468 | 0.010912 | -0.068665 | 0.068665 | -0.3891 | 0.073242 | 0.10071 | 0.14191 | -0.15564 | 0.27466 | 0.21057 | -0.27924 | 122.4838 | -0.13275 | 122.8043 | 122.9462 | -0.10071 | 122.5937 | 0.009155 | 0.32043 | 122.7173 | 123.1476 | 122.9736 | 122.9416 | 122.8043 | 123.0835 | 123.0148 | 122.5937 | 122.9416 | 122.8043 | 123.0148 | 122.9736 | 123.0835 | -0.59052 | -0.48065
3421.5 | 123.143 | -122.8134 | 0.17853 | -0.22804 | 0.0094251 | -0.0041742 | 0.040883 | -0.018965 | -0.0091259 | 0.0085619 | -0.073242 | 0.059509 | -0.39825 | 0.10529 | 0.10986 | 0.14191 | -0.12817 | 0.32959 | 0.21973 | -0.27466 | 122.4152 | -0.11902 | 122.7402 | 122.9187 | -0.068665 | 122.5388 | 0.041199 | 0.32501 | 122.6852 | 123.143 | 122.9233 | 122.8729 | 122.7402 | 123.0331 | 122.9553 | 122.5388 | 122.8729 | 122.7402 | 122.9553 | 122.9233 | 123.0331 | -0.57678 | -0.45319
3423.25 | 123.1888 | -122.7905 | 0.17853 | 0.016098 | 0.01028 | -0.0080194 | 0.04067 | -0.019179 | -0.0097669 | 0.010485 | -0.11902 | 0.10071 | -0.3891 | 0.036621 | 0.054932 | 0.086975 | -0.09613 | 0.2655 | 0.23346 | -0.3067 | 122.4014 | -0.07782 | 122.6715 | 122.8271 | -0.1236 | 122.4838 | 0.054931 | 0.27008 | 122.6944 | 123.056 | 122.8455 | 122.8912 | 122.6715 | 123.024 | 122.8775 | 122.4838 | 122.8912 | 122.6715 | 122.8775 | 122.8455 | 123.024 | -0.56763 | -0.48523
3424.9531 | 123.0377 | -122.8271 | 0.21515 | 0.17632 | 0.012843 | -0.0063104 | 0.045797 | -0.017043 | -0.013185 | 0.011339 | -0.045776 | 0.086975 | -0.40283 | 0.10071 | 0.09613 | 0.14648 | -0.20599 | 0.27924 | 0.22888 | -0.27466 | 122.4243 | -0.12817 | 122.7814 | 122.9279 | -0.11902 | 122.5525 | 0.013733 | 0.35706 | 122.6212 | 123.1064 | 122.9233 | 122.9141 | 122.7814 | 123.056 | 122.9736 | 122.5525 | 122.9141 | 122.7814 | 122.9736 | 122.9233 | 123.056 | -0.61798 | -0.48981
3426.7031 | 123.0606 | -122.8409 | 0.21057 | 0.16869 | 0.010493 | -0.0067376 | 0.046437 | -0.015548 | -0.01233 | 0.010057 | -0.059509 | 0.064087 | -0.3891 | 0.09613 | 0.086975 | 0.11902 | -0.17853 | 0.28381 | 0.21515 | -0.28381 | 122.4518 | -0.14648 | 122.7814 | 122.937 | -0.1236 | 122.5571 | 0.004578 | 0.32959 | 122.6624 | 123.1247 | 122.9279 | 122.905 | 122.7814 | 123.056 | 122.9599 | 122.5571 | 122.905 | 122.7814 | 122.9599 | 122.9279 | 123.056 | -0.59967 | -0.49438
3428.4688 | 123.143 | -122.8043 | 0.17853 | -0.18227 | 0.010921 | -0.0063104 | 0.038533 | -0.020674 | -0.01169 | 0.011126 | -0.054932 | 0.082397 | -0.3891 | 0.09613 | 0.11444 | 0.14648 | -0.14648 | 0.31586 | 0.24261 | -0.27466 | 122.4152 | -0.096131 | 122.7493 | 122.9004 | -0.064087 | 122.5296 | 0.064087 | 0.33417 | 122.6578 | 123.1201 | 122.9187 | 122.8867 | 122.7493 | 123.0469 | 122.9507 | 122.5296 | 122.8867 | 122.7493 | 122.9507 | 122.9187 | 123.0469 | -0.56763 | -0.45319
3430.1719 | 123.1476 | -122.8271 | 0.19226 | -0.20515 | 0.0087841 | -0.006524 | 0.042592 | -0.017684 | -0.011049 | 0.0098437 | -0.059509 | 0.082397 | -0.39368 | 0.10529 | 0.1236 | 0.13275 | -0.12817 | 0.32501 | 0.22888 | -0.27466 | 122.4335 | -0.10986 | 122.7676 | 122.9324 | -0.068665 | 122.5525 | 0.036621 | 0.33417 | 122.699 | 123.1522 | 122.9507 | 122.9095 | 122.7676 | 123.056 | 122.9599 | 122.5525 | 122.9095 | 122.7676 | 122.9599 | 122.9507 | 123.056 | -0.58594 | -0.46692
3431.9219 | 123.0881 | -122.8455 | 0.18768 | 0.12291 | 0.0096387 | -0.0046014 | 0.04366 | -0.018325 | -0.012117 | 0.010698 | -0.068665 | 0.086975 | -0.40283 | 0.082397 | 0.07782 | 0.11902 | -0.16022 | 0.27466 | 0.23346 | -0.27924 | 122.4426 | -0.10071 | 122.7768 | 122.9279 | -0.10986 | 122.5662 | 0.045776 | 0.33417 | 122.6852 | 123.1201 | 122.9233 | 122.9324 | 122.7768 | 123.0789 | 122.9645 | 122.5662 | 122.9324 | 122.7768 | 122.9645 | 122.9233 | 123.0789 | -0.59052 | -0.46692
3433.6875 | 123.0652 | -122.8638 | 0.19684 | -0.052567 | 0.010921 | -0.006524 | 0.050283 | -0.016616 | -0.013826 | 0.0087757 | -0.10986 | 0.11902 | -0.43945 | 0.027466 | 0.018311 | 0.027466 | -0.041199 | 0.18768 | 0.26093 | -0.29297 | 122.4243 | -0.077819 | 122.7539 | 122.8912 | -0.17853 | 122.5708 | 0.064087 | 0.32959 | 122.8226 | 123.0515 | 122.8821 | 122.9828 | 122.7539 | 123.1247 | 122.8912 | 122.5708 | 122.9828 | 122.7539 | 122.8912 | 122.8821 | 123.1247 | -0.63629 | -0.48981
3435.4062 | 123.0606 | -122.8363 | 0.20142 | -0.083084 | 0.013484 | -0.004815 | 0.04836 | -0.015334 | -0.015107 | 0.012194 | -0.10986 | 0.10986 | -0.42114 | 0.036621 | 0.045776 | 0.059509 | -0.027466 | 0.21973 | 0.26093 | -0.31128 | 122.4152 | -0.091553 | 122.7264 | 122.8729 | -0.15564 | 122.525 | 0.059509 | 0.31128 | 122.8088 | 123.056 | 122.8821 | 122.9462 | 122.7264 | 123.0972 | 122.8958 | 122.525 | 122.9462 | 122.7264 | 122.8958 | 122.8821 | 123.0972 | -0.62256 | -0.5127
3437.1562 | 123.0927 | -122.818 | 0.19226 | 0.12291 | 0.0092115 | -0.0018244 | 0.039815 | -0.01982 | -0.011262 | 0.011339 | -0.082397 | 0.082397 | -0.3891 | 0.054932 | 0.082397 | 0.11902 | -0.17395 | 0.27466 | 0.22888 | -0.29297 | 122.4289 | -0.10986 | 122.7356 | 122.8729 | -0.10986 | 122.525 | 0.036621 | 0.3067 | 122.644 | 123.0927 | 122.9004 | 122.9004 | 122.7356 | 123.0469 | 122.937 | 122.525 | 122.9004 | 122.7356 | 122.937 | 122.9004 | 123.0469 | -0.58136 | -0.48523
3438.8594 | 123.0606 | -122.8546 | 0.21515 | -0.060196 | 0.011348 | 0.00052557 | 0.049428 | -0.01512 | -0.011476 | 0.010698 | -0.10071 | 0.1236 | -0.4303 | 0.036621 | 0.018311 | 0.050354 | -0.032043 | 0.19684 | 0.2655 | -0.29755 | 122.4243 | -0.091553 | 122.7539 | 122.8912 | -0.19684 | 122.5571 | 0.050354 | 0.32959 | 122.8226 | 123.0515 | 122.8729 | 122.9782 | 122.7539 | 123.1201 | 122.905 | 122.5571 | 122.9782 | 122.7539 | 122.905 | 122.8729 | 123.1201 | -0.64545 | -0.5127
3440.625 | 123.175 | -122.7768 | 0.19684 | 0.0084684 | 0.010921 | -0.014214 | 0.038747 | -0.016616 | -0.013612 | 0.011126 | -0.11902 | 0.09613 | -0.40283 | 0.032043 | 0.064087 | 0.082397 | -0.10071 | 0.23804 | 0.23346 | -0.28839 | 122.374 | -0.10071 | 122.6578 | 122.8088 | -0.13275 | 122.4884 | 0.036621 | 0.28381 | 122.6761 | 123.0148 | 122.8409 | 122.8729 | 122.6578 | 123.0103 | 122.8592 | 122.4884 | 122.8729 | 122.6578 | 122.8592 | 122.8409 | 123.0103 | -0.59967 | -0.48523
3442.3125 | 123.2208 | -122.7859 | 0.17395 | -0.28145 | 0.010066 | -0.0046014 | 0.044301 | -0.018111 | -0.01169 | 0.011339 | -0.16022 | 0.13733 | -0.42114 | -0.022888 | -0.004578 | 0 | 0.054932 | 0.17395 | 0.27466 | -0.31586 | 122.3648 | -0.036621 | 122.6257 | 122.7631 | -0.17853 | 122.4701 | 0.10071 | 0.26093 | 122.8409 | 122.9599 | 122.7814 | 122.9233 | 122.6257 | 123.0606 | 122.7859 | 122.4701 | 122.9233 | 122.6257 | 122.7859 | 122.7814 | 123.0606 | -0.59509 | -0.48981
3444.0625 | 123.1842 | -122.8317 | 0.1831 | -0.20515 | 0.012629 | -0.0043878 | 0.044942 | -0.018325 | -0.011262 | 0.011553 | -0.16022 | 0.14648 | -0.4303 | -0.018311 | 0.004578 | 0.013733 | 0.041199 | 0.18768 | 0.27008 | -0.32501 | 122.4014 | -0.036621 | 122.6715 | 122.8134 | -0.17853 | 122.5067 | 0.086976 | 0.27008 | 122.8729 | 123.0194 | 122.8363 | 122.9782 | 122.6715 | 123.1018 | 122.8455 | 122.5067 | 122.9782 | 122.6715 | 122.8455 | 122.8363 | 123.1018 | -0.6134 | -0.50812
3445.7656 | 123.0881 | -122.8363 | 0.1831 | 0.15343 | 0.010066 | -0.0046014 | 0.038747 | -0.016188 | -0.0095531 | 0.0092029 | -0.07782 | 0.09613 | -0.38452 | 0.068665 | 0.086975 | 0.10529 | -0.15106 | 0.2655 | 0.21515 | -0.27466 | 122.4518 | -0.086975 | 122.7585 | 122.905 | -0.09613 | 122.5616 | 0.032044 | 0.3067 | 122.6852 | 123.1018 | 122.9233 | 122.9324 | 122.7585 | 123.0515 | 122.9416 | 122.5616 | 122.9324 | 122.7585 | 122.9416 | 122.9233 | 123.0515 | -0.56763 | -0.45776
3447.5312 | 123.0927 | -122.818 | 0.21057 | 0.092392 | 0.011561 | -0.0016106 | 0.049642 | -0.015548 | -0.012758 | 0.010698 | -0.17395 | 0.14191 | -0.43945 | -0.041199 | -0.045776 | -0.013733 | 0.018311 | 0.1236 | 0.25635 | -0.30212 | 122.3785 | -0.068664 | 122.644 | 122.7768 | -0.25635 | 122.5159 | 0.045777 | 0.2655 | 122.8363 | 122.9416 | 122.7722 | 122.9599 | 122.644 | 123.0743 | 122.8043 | 122.5159 | 122.9599 | 122.644 | 122.8043 | 122.7722 | 123.0743 | -0.65002 | -0.5127
3449.2344 | 123.1338 | -122.7951 | 0.18768 | -0.2433 | 0.011989 | -0.0071648 | 0.041524 | -0.020247 | -0.012758 | 0.0092029 | -0.059509 | 0.091553 | -0.37537 | 0.11444 | 0.12817 | 0.14191 | -0.12817 | 0.33875 | 0.21973 | -0.28381 | 122.4197 | -0.09613 | 122.7356 | 122.9095 | -0.059509 | 122.5113 | 0.032044 | 0.31586 | 122.6669 | 123.1339 | 122.9233 | 122.8867 | 122.7356 | 123.0148 | 122.937 | 122.5113 | 122.8867 | 122.7356 | 122.937 | 122.9233 | 123.0148 | -0.56305 | -0.4715
3450.9844 | 123.143 | -122.8134 | 0.18768 | 0.092392 | 0.011134 | -0.0084466 | 0.04067 | -0.018752 | -0.010835 | 0.011766 | -0.11902 | 0.09613 | -0.37994 | 0.045776 | 0.068665 | 0.09613 | -0.1236 | 0.25177 | 0.23804 | -0.28839 | 122.4335 | -0.091553 | 122.6944 | 122.8592 | -0.11902 | 122.525 | 0.050354 | 0.26093 | 122.6898 | 123.0652 | 122.8821 | 122.9095 | 122.6944 | 123.0515 | 122.9095 | 122.525 | 122.9095 | 122.6944 | 122.9095 | 122.8821 | 123.0515 | -0.56763 | -0.47607
3452.75 | 123.1888 | -122.8043 | 0.16022 | 0.016098 | 0.013698 | -0.0035332 | 0.041097 | -0.020461 | -0.011262 | 0.010271 | -0.10986 | 0.10986 | -0.3891 | 0.036621 | 0.07782 | 0.10986 | -0.10986 | 0.27466 | 0.22888 | -0.28381 | 122.4152 | -0.050354 | 122.6944 | 122.8409 | -0.082397 | 122.5204 | 0.068665 | 0.27924 | 122.6944 | 123.0789 | 122.8821 | 122.9141 | 122.6944 | 123.0331 | 122.9141 | 122.5204 | 122.9141 | 122.6944 | 122.9141 | 122.8821 | 123.0331 | -0.54932 | -0.44403
3454.5 | 123.1293 | -122.8134 | 0.19226 | 0.10002 | 0.01028 | -0.0022516 | 0.043233 | -0.016829 | -0.010194 | 0.0098437 | -0.068665 | 0.07782 | -0.39825 | 0.054932 | 0.068665 | 0.10986 | -0.14191 | 0.25177 | 0.2243 | -0.28839 | 122.4152 | -0.11444 | 122.7448 | 122.8683 | -0.1236 | 122.525 | 0.032043 | 0.32959 | 122.6715 | 123.0652 | 122.8821 | 122.8912 | 122.7448 | 123.0377 | 122.9233 | 122.525 | 122.8912 | 122.7448 | 122.9233 | 122.8821 | 123.0377 | -0.59052 | -0.48065
3456.2031 | 123.0927 | -122.8638 | 0.19226 | 0.0084684 | 0.011775 | 0.00031197 | 0.050283 | -0.015975 | -0.015321 | 0.0092029 | -0.12817 | 0.10986 | -0.45319 | -0.013733 | -0.027466 | 0.013733 | -0.009155 | 0.12817 | 0.27466 | -0.29755 | 122.4106 | -0.082398 | 122.7356 | 122.85 | -0.21973 | 122.5662 | 0.082397 | 0.32501 | 122.8546 | 122.9919 | 122.8363 | 122.9736 | 122.7356 | 123.1384 | 122.8775 | 122.5662 | 122.9736 | 122.7356 | 122.8775 | 122.8363 | 123.1384 | -0.64545 | -0.48981
3457.9844 | 123.1338 | -122.8226 | 0.18768 | -0.13649 | 0.010707 | -0.011437 | 0.039815 | -0.017684 | -0.012758 | 0.0087757 | -0.045776 | 0.091553 | -0.37537 | 0.10529 | 0.11902 | 0.14648 | -0.11902 | 0.33875 | 0.23346 | -0.28381 | 122.4472 | -0.09613 | 122.7768 | 122.9279 | -0.068664 | 122.5388 | 0.045776 | 0.32959 | 122.7036 | 123.1613 | 122.9416 | 122.9141 | 122.7768 | 123.056 | 122.9691 | 122.5388 | 122.9141 | 122.7768 | 122.9691 | 122.9416 | 123.056 | -0.56305 | -0.4715
3459.7344 | 123.1338 | -122.8088 | 0.19226 | -0.19753 | 0.011134 | -0.0088738 | 0.040456 | -0.021102 | -0.011903 | 0.0098437 | -0.054932 | 0.086975 | -0.3891 | 0.10986 | 0.12817 | 0.13733 | -0.13275 | 0.3479 | 0.22888 | -0.28839 | 122.4197 | -0.10529 | 122.7539 | 122.9187 | -0.064087 | 122.5204 | 0.036621 | 0.33417 | 122.6761 | 123.1567 | 122.937 | 122.8958 | 122.7539 | 123.0377 | 122.9462 | 122.5204 | 122.8958 | 122.7539 | 122.9462 | 122.937 | 123.0377 | -0.58136 | -0.48065
3461.5156 | 123.1705 | -122.8226 | 0.16937 | -0.20515 | 0.0087841 | -0.008233 | 0.046651 | -0.014907 | -0.014039 | 0.010698 | -0.15564 | 0.1236 | -0.44861 | 0.009155 | 0.004578 | 0.009155 | 0.032043 | 0.19684 | 0.27466 | -0.31128 | 122.374 | -0.045777 | 122.6669 | 122.8317 | -0.16479 | 122.5113 | 0.10529 | 0.29297 | 122.8546 | 123.0194 | 122.8271 | 122.9462 | 122.6669 | 123.0972 | 122.8317 | 122.5113 | 122.9462 | 122.6669 | 122.8317 | 122.8271 | 123.0972 | -0.61798 | -0.48065
3463.2188 | 123.0789 | -122.8638 | 0.20142 | -0.029679 | 0.011348 | -0.0052422 | 0.046865 | -0.015334 | -0.012544 | 0.01198 | -0.10071 | 0.10986 | -0.42114 | 0.036621 | 0.009155 | 0.032043 | -0.032043 | 0.17395 | 0.26093 | -0.30212 | 122.4426 | -0.091553 | 122.7631 | 122.9004 | -0.19226 | 122.5616 | 0.059509 | 0.32043 | 122.8317 | 123.0377 | 122.8729 | 122.9736 | 122.7631 | 123.1247 | 122.8958 | 122.5616 | 122.9736 | 122.7631 | 122.8958 | 122.8729 | 123.1247 | -0.62256 | -0.50354
3464.9844 | 123.1064 | -122.8409 | 0.18768 | 0.15343 | 0.010707 | -0.0043878 | 0.039815 | -0.01747 | -0.010835 | 0.010057 | -0.082397 | 0.082397 | -0.37994 | 0.064087 | 0.091553 | 0.10986 | -0.15106 | 0.25635 | 0.2243 | -0.28839 | 122.4609 | -0.10529 | 122.7585 | 122.905 | -0.09613 | 122.5525 | 0.036621 | 0.29755 | 122.6898 | 123.0972 | 122.9324 | 122.9233 | 122.7585 | 123.0652 | 122.9507 | 122.5525 | 122.9233 | 122.7585 | 122.9507 | 122.9324 | 123.0652 | -0.56763 | -0.47607
3466.7344 | 123.1796 | -122.8134 | 0.16479 | 0.0084684 | 0.0085705 | -0.0054558 | 0.041097 | -0.017684 | -0.010835 | 0.0096301 | -0.12817 | 0.086975 | -0.40283 | 0.036621 | 0.073242 | 0.091553 | -0.11444 | 0.25635 | 0.24719 | -0.28381 | 122.4106 | -0.07782 | 122.6852 | 122.85 | -0.091553 | 122.5296 | 0.082397 | 0.27466 | 122.699 | 123.0698 | 122.8867 | 122.9004 | 122.6852 | 123.0606 | 122.905 | 122.5296 | 122.9004 | 122.6852 | 122.905 | 122.8867 | 123.0606 | -0.56763 | -0.44861
3468.5 | 123.1705 | -122.7905 | 0.16937 | 0.016098 | 0.010921 | -0.0071648 | 0.038106 | -0.018965 | -0.01233 | 0.011553 | -0.1236 | 0.10071 | -0.3891 | 0.036621 | 0.064087 | 0.082397 | -0.10529 | 0.24261 | 0.24719 | -0.27924 | 122.4014 | -0.068665 | 122.6669 | 122.8271 | -0.10529 | 122.5113 | 0.077819 | 0.2655 | 122.6852 | 123.0331 | 122.8546 | 122.8912 | 122.6669 | 123.0377 | 122.8729 | 122.5113 | 122.8912 | 122.6669 | 122.8729 | 122.8546 | 123.0377 | -0.55847 | -0.44861
3470.2031 | 123.0927 | -122.8592 | 0.21515 | 0.0084684 | 0.011989 | -0.0054558 | 0.05071 | -0.016616 | -0.014467 | 0.0085619 | -0.13275 | 0.10986 | -0.45319 | -0.004578 | -0.013733 | 0.004578 | -0.013733 | 0.16937 | 0.27008 | -0.32959 | 122.406 | -0.10529 | 122.7264 | 122.8546 | -0.22888 | 122.5296 | 0.054932 | 0.32043 | 122.8455 | 123.0286 | 122.8455 | 122.9691 | 122.7264 | 123.1293 | 122.8638 | 122.5296 | 122.9691 | 122.7264 | 122.8638 | 122.8455 | 123.1293 | -0.66834 | -0.54474
3471.9688 | 123.2025 | -122.7951 | 0.17395 | -0.20515 | 0.013698 | -0.0080194 | 0.043019 | -0.018325 | -0.011903 | 0.010912 | -0.16479 | 0.12817 | -0.43488 | -0.009155 | 0.013733 | 0 | 0.059509 | 0.19226 | 0.29297 | -0.32044 | 122.3602 | -0.045776 | 122.6303 | 122.7859 | -0.16022 | 122.4747 | 0.11902 | 0.27008 | 122.8546 | 122.9874 | 122.8088 | 122.9233 | 122.6303 | 123.0881 | 122.7951 | 122.4747 | 122.9233 | 122.6303 | 122.7951 | 122.8088 | 123.0881 | -0.60882 | -0.49439
3473.6719 | 123.1888 | -122.818 | 0.16937 | -0.25093 | 0.010707 | -0.0071648 | 0.042806 | -0.018111 | -0.011903 | 0.0087757 | -0.1831 | 0.13275 | -0.44861 | -0.013733 | 0.004578 | 0.004578 | 0.054932 | 0.16937 | 0.27924 | -0.32044 | 122.3694 | -0.036622 | 122.6349 | 122.8043 | -0.16479 | 122.4976 | 0.10986 | 0.2655 | 122.8729 | 122.9874 | 122.8226 | 122.9507 | 122.6349 | 123.0972 | 122.8226 | 122.4976 | 122.9507 | 122.6349 | 122.8226 | 122.8226 | 123.0972 | -0.61798 | -0.48981
3475.4375 | 123.0652 | -122.8546 | 0.21515 | 0.21446 | 0.011989 | -0.01101 | 0.04131 | -0.014479 | -0.011903 | 0.01198 | -0.050354 | 0.07782 | -0.37537 | 0.086975 | 0.09613 | 0.15106 | -0.18768 | 0.28839 | 0.21515 | -0.2655 | 122.4792 | -0.13733 | 122.8043 | 122.9416 | -0.11902 | 122.5891 | 0 | 0.32501 | 122.6669 | 123.143 | 122.9507 | 122.9324 | 122.8043 | 123.0698 | 123.0057 | 122.5891 | 122.9324 | 122.8043 | 123.0057 | 122.9507 | 123.0698 | -0.59052 | -0.48065
3477.2031 | 123.0652 | -122.8638 | 0.21515 | -0.083084 | 0.012416 | -0.0056696 | 0.046224 | -0.014266 | -0.014894 | 0.011766 | -0.11444 | 0.10529 | -0.45776 | 0.045776 | 0.050354 | 0.064087 | -0.036621 | 0.21973 | 0.27924 | -0.30212 | 122.406 | -0.10986 | 122.7493 | 122.9095 | -0.16479 | 122.5616 | 0.064087 | 0.34332 | 122.8271 | 123.0835 | 122.9141 | 122.9691 | 122.7493 | 123.143 | 122.9279 | 122.5616 | 122.9691 | 122.7493 | 122.9279 | 122.9141 | 123.143 | -0.67291 | -0.51727
3478.9531 | 123.1293 | -122.8088 | 0.1831 | -0.1899 | 0.010066 | -0.0056696 | 0.040029 | -0.017897 | -0.011903 | 0.0092029 | -0.068665 | 0.086975 | -0.39825 | 0.10071 | 0.13275 | 0.14191 | -0.11902 | 0.32959 | 0.21973 | -0.28381 | 122.4106 | -0.09613 | 122.7402 | 122.9095 | -0.050354 | 122.525 | 0.036622 | 0.32959 | 122.6898 | 123.1384 | 122.9416 | 122.8958 | 122.7402 | 123.0286 | 122.9507 | 122.525 | 122.8958 | 122.7402 | 122.9507 | 122.9416 | 123.0286 | -0.58136 | -0.46692
3480.6562 | 123.0377 | -122.8088 | 0.21057 | 0.18394 | 0.01028 | -0.0050286 | 0.047078 | -0.013625 | -0.012758 | 0.011126 | -0.045776 | 0.086975 | -0.39825 | 0.09613 | 0.10986 | 0.14648 | -0.21057 | 0.29297 | 0.23346 | -0.27466 | 122.4106 | -0.1236 | 122.7631 | 122.905 | -0.10071 | 122.5342 | 0.022888 | 0.35248 | 122.5983 | 123.1018 | 122.9187 | 122.8958 | 122.7631 | 123.0423 | 122.9553 | 122.5342 | 122.8958 | 122.7631 | 122.9553 | 122.9187 | 123.0423 | -0.60882 | -0.48523
3482.4219 | 123.0743 | -122.8455 | 0.19226 | 0.10765 | 0.010493 | -0.006524 | 0.04131 | -0.013198 | -0.01169 | 0.010912 | -0.068665 | 0.059509 | -0.40283 | 0.068665 | 0.10071 | 0.14191 | -0.17853 | 0.27008 | 0.2243 | -0.29755 | 122.4426 | -0.13275 | 122.7768 | 122.9141 | -0.091553 | 122.5479 | 0.032043 | 0.33417 | 122.6669 | 123.1155 | 122.9462 | 122.905 | 122.7768 | 123.0698 | 122.9874 | 122.5479 | 122.905 | 122.7768 | 122.9874 | 122.9462 | 123.0698 | -0.59509 | -0.48981
3484.1875 | 123.0606 | -122.8317 | 0.21057 | -0.060196 | 0.010921 | -0.0039606 | 0.049215 | -0.014479 | -0.013612 | 0.0094165 | -0.09613 | 0.11444 | -0.43945 | 0.027466 | 0.013733 | 0.050354 | -0.013733 | 0.19684 | 0.27008 | -0.31128 | 122.3923 | -0.09613 | 122.7356 | 122.8592 | -0.19684 | 122.5204 | 0.05951 | 0.34332 | 122.818 | 123.0286 | 122.8455 | 122.9462 | 122.7356 | 123.1018 | 122.8821 | 122.5204 | 122.9462 | 122.7356 | 122.8821 | 122.8455 | 123.1018 | -0.65002 | -0.52185
3485.8906 | 123.1613 | -122.8088 | 0.19226 | -0.20515 | 0.010493 | -0.010156 | 0.042592 | -0.017897 | -0.014253 | 0.0092029 | -0.091553 | 0.09613 | -0.40741 | 0.059509 | 0.082397 | 0.10071 | -0.041199 | 0.27466 | 0.24261 | -0.29755 | 122.4014 | -0.096131 | 122.7173 | 122.8683 | -0.10986 | 122.5113 | 0.050354 | 0.31586 | 122.7676 | 123.0835 | 122.8912 | 122.905 | 122.7173 | 123.0515 | 122.9095 | 122.5113 | 122.905 | 122.7173 | 122.9095 | 122.8912 | 123.0515 | -0.59967 | -0.48981
3487.6406 | 123.1842 | -122.8271 | 0.17853 | -0.2433 | 0.01327 | -0.0058832 | 0.04366 | -0.018111 | -0.01233 | 0.0092029 | -0.16479 | 0.13733 | -0.44861 | -0.018311 | 0.013733 | -0.004578 | 0.059509 | 0.1831 | 0.27008 | -0.33417 | 122.3785 | -0.041199 | 122.6624 | 122.8088 | -0.16479 | 122.493 | 0.091553 | 0.28381 | 122.8867 | 123.0103 | 122.8409 | 122.9645 | 122.6624 | 123.0972 | 122.8226 | 122.493 | 122.9645 | 122.6624 | 122.8226 | 122.8409 | 123.0972 | -0.62714 | -0.5127
3489.3906 | 123.1613 | -122.7951 | 0.16937 | -0.037308 | 0.01028 | -0.0084466 | 0.038747 | -0.01747 | -0.011262 | 0.0096301 | -0.1236 | 0.07782 | -0.41199 | 0.073242 | 0.09613 | 0.13733 | -0.11902 | 0.30212 | 0.24261 | -0.29297 | 122.3831 | -0.091553 | 122.6715 | 122.8683 | -0.073243 | 122.5021 | 0.073242 | 0.28839 | 122.6761 | 123.0972 | 122.8912 | 122.8729 | 122.6715 | 123.0377 | 122.9324 | 122.5021 | 122.8729 | 122.6715 | 122.9324 | 122.8912 | 123.0377 | -0.58136 | -0.46234
3491.0938 | 123.0515 | -122.8683 | 0.21973 | -0.075455 | 0.0094251 | -0.0026788 | 0.046651 | -0.016829 | -0.01233 | 0.0092029 | -0.11444 | 0.10986 | -0.44403 | 0.041199 | 0.018311 | 0.059509 | -0.041199 | 0.19226 | 0.25635 | -0.30212 | 122.4243 | -0.10986 | 122.7539 | 122.9095 | -0.20142 | 122.5662 | 0.036621 | 0.32959 | 122.8271 | 123.0606 | 122.8867 | 122.9782 | 122.7539 | 123.1247 | 122.9279 | 122.5662 | 122.9782 | 122.7539 | 122.9279 | 122.8867 | 123.1247 | -0.66376 | -0.52185
3492.8594 | 123.1384 | -122.8043 | 0.19684 | -0.21278 | 0.0096387 | -0.0078058 | 0.047933 | -0.017256 | -0.013399 | 0.011553 | -0.15106 | 0.12817 | -0.44403 | 0.013733 | 0.032043 | 0.050354 | 0.004578 | 0.2243 | 0.2655 | -0.30212 | 122.3602 | -0.068664 | 122.6532 | 122.818 | -0.1648 | 122.5021 | 0.068665 | 0.29297 | 122.8088 | 123.0286 | 122.8363 | 122.9324 | 122.6532 | 123.0698 | 122.8546 | 122.5021 | 122.9324 | 122.6532 | 122.8546 | 122.8363 | 123.0698 | -0.64087 | -0.49896
3494.6094 | 123.1659 | -122.8134 | 0.1831 | -0.052567 | 0.01028 | -0.0056696 | 0.038533 | -0.018538 | -0.0099805 | 0.0085619 | -0.11902 | 0.091553 | -0.42114 | 0.054932 | 0.1236 | 0.13275 | -0.11444 | 0.31128 | 0.23346 | -0.30212 | 122.3923 | -0.091552 | 122.6944 | 122.8683 | -0.059509 | 122.5113 | 0.050354 | 0.30212 | 122.699 | 123.1247 | 122.937 | 122.905 | 122.6944 | 123.0469 | 122.9462 | 122.5113 | 122.905 | 122.6944 | 122.9462 | 122.937 | 123.0469 | -0.60425 | -0.48523
3496.375 | 123.1979 | -122.8317 | 0.16022 | 0.016098 | 0.011134 | -0.0060968 | 0.040456 | -0.01982 | -0.0091259 | 0.010912 | -0.15106 | 0.091553 | -0.41199 | 0.041199 | 0.07782 | 0.11444 | -0.10529 | 0.25635 | 0.23346 | -0.29297 | 122.4197 | -0.068664 | 122.6807 | 122.8729 | -0.082397 | 122.5388 | 0.073242 | 0.26092 | 122.7264 | 123.0881 | 122.9095 | 122.9233 | 122.6807 | 123.0652 | 122.9462 | 122.5388 | 122.9233 | 122.6807 | 122.9462 | 122.9095 | 123.0652 | -0.5722 | -0.45319
3498.125 | 123.0469 | -122.85 | 0.21515 | 0.1992 | 0.01028 | -0.001397 | 0.047292 | -0.019606 | -0.012117 | 0.010057 | -0.10071 | 0.07782 | -0.42572 | 0.09613 | 0.073242 | 0.10529 | -0.16937 | 0.27008 | 0.23346 | -0.27008 | 122.4243 | -0.13733 | 122.7493 | 122.9462 | -0.14191 | 122.58 | 0.01831 | 0.32501 | 122.6807 | 123.1201 | 122.9233 | 122.9279 | 122.7493 | 123.0835 | 122.9553 | 122.58 | 122.9279 | 122.7493 | 122.9553 | 122.9233 | 123.0835 | -0.64087 | -0.48523
3499.875 | 123.111 | -122.85 | 0.18768 | 0.092392 | 0.01327 | -0.0067376 | 0.04601 | -0.016188 | -0.012758 | 0.012621 | -0.17395 | 0.10529 | -0.4303 | -0.013733 | -0.004578 | 0.009155 | -0.036621 | 0.17395 | 0.26093 | -0.31586 | 122.4197 | -0.082397 | 122.6761 | 122.8363 | -0.19226 | 122.5342 | 0.073242 | 0.25635 | 122.8134 | 123.024 | 122.8455 | 122.9553 | 122.6761 | 123.111 | 122.8592 | 122.5342 | 122.9553 | 122.6761 | 122.8592 | 122.8455 | 123.111 | -0.61798 | -0.50354
3501.6406 | 123.1522 | -122.7997 | 0.17395 | -0.083084 | 0.01028 | -0.0056696 | 0.039174 | -0.018538 | -0.010408 | 0.0089893 | -0.10986 | 0.07782 | -0.41199 | 0.091553 | 0.11444 | 0.13733 | -0.12817 | 0.32501 | 0.22888 | -0.31586 | 122.3877 | -0.09613 | 122.6898 | 122.8912 | -0.059509 | 122.4838 | 0.054932 | 0.30212 | 122.6715 | 123.1247 | 122.9141 | 122.8775 | 122.6898 | 123.0286 | 122.937 | 122.4838 | 122.8775 | 122.6898 | 122.937 | 122.9141 | 123.0286 | -0.58594 | -0.48981
3503.3438 | 123.056 | -122.8821 | 0.21057 | -0.037308 | 0.011989 | -0.0071648 | 0.047719 | -0.017897 | -0.012971 | 0.011339 | -0.12817 | 0.086975 | -0.44403 | 0.032043 | 0.022888 | 0.032043 | -0.018311 | 0.20599 | 0.24719 | -0.31128 | 122.438 | -0.1236 | 122.7539 | 122.9141 | -0.18768 | 122.5708 | 0.036621 | 0.31586 | 122.8638 | 123.0881 | 122.905 | 122.9691 | 122.7539 | 123.1293 | 122.9141 | 122.5708 | 122.9691 | 122.7539 | 122.9141 | 122.905 | 123.1293 | -0.6546 | -0.52185
3505.0938 | 123.1934 | -122.7997 | 0.20599 | -0.27382 | 0.0083569 | -0.010369 | 0.04131 | -0.019393 | -0.012971 | 0.010271 | -0.14191 | 0.068665 | -0.4303 | 0.022888 | 0.045776 | 0.041199 | 0.004578 | 0.2243 | 0.25635 | -0.3067 | 122.3694 | -0.13733 | 122.6578 | 122.8226 | -0.16022 | 122.493 | 0.050354 | 0.28839 | 122.8043 | 123.024 | 122.8455 | 122.8683 | 122.6578 | 123.056 | 122.8409 | 122.493 | 122.8683 | 122.6578 | 122.8409 | 122.8455 | 123.056 | -0.63629 | -0.5127
3506.7969 | 123.0606 | -122.8546 | 0.21515 | 0.18394 | 0.010066 | -0.0011834 | 0.042592 | -0.018325 | -0.01169 | 0.011339 | -0.073242 | 0.073242 | -0.40741 | 0.09613 | 0.09613 | 0.14648 | -0.19684 | 0.27466 | 0.21057 | -0.27924 | 122.4472 | -0.14191 | 122.7814 | 122.9507 | -0.11902 | 122.5754 | -0.004578 | 0.33417 | 122.6578 | 123.1293 | 122.9507 | 122.9279 | 122.7814 | 123.0652 | 123.0011 | 122.5754 | 122.9279 | 122.7814 | 123.0011 | 122.9507 | 123.0652 | -0.62256 | -0.49438
3508.5469 | 123.0606 | -122.8455 | 0.19684 | 0.22972 | 0.011775 | -0.0069512 | 0.044728 | -0.016616 | -0.013826 | 0.010912 | -0.12817 | 0.064087 | -0.42572 | 0.064087 | 0.07782 | 0.11902 | -0.14191 | 0.24719 | 0.23346 | -0.27466 | 122.4197 | -0.13275 | 122.7173 | 122.9095 | -0.11902 | 122.5708 | 0.036621 | 0.29755 | 122.7036 | 123.0927 | 122.9233 | 122.9095 | 122.7173 | 123.0789 | 122.9645 | 122.5708 | 122.9095 | 122.7173 | 122.9645 | 122.9233 | 123.0789 | -0.62256 | -0.4715
3510.2969 | 123.0469 | -122.8226 | 0.19684 | 0.1992 | 0.01028 | -0.0067376 | 0.044515 | -0.014907 | -0.011903 | 0.011553 | -0.07782 | 0.045776 | -0.42572 | 0.086975 | 0.10986 | 0.14648 | -0.19684 | 0.28839 | 0.2243 | -0.27924 | 122.3969 | -0.15106 | 122.7448 | 122.9095 | -0.086975 | 122.5433 | 0.027466 | 0.3479 | 122.6257 | 123.111 | 122.9324 | 122.8683 | 122.7448 | 123.0469 | 122.9691 | 122.5433 | 122.8683 | 122.7448 | 122.9691 | 122.9324 | 123.0469 | -0.62256 | -0.47607
3512.0625 | 123.0606 | -122.8729 | 0.20599 | -0.090714 | 0.011348 | -0.003747 | 0.046865 | -0.017897 | -0.01468 | 0.010912 | -0.11444 | 0.09613 | -0.43945 | 0.045776 | 0.022888 | 0.050354 | -0.036621 | 0.21515 | 0.27008 | -0.3067 | 122.4335 | -0.10986 | 122.7585 | 122.9187 | -0.18311 | 122.5662 | 0.064087 | 0.32501 | 122.8363 | 123.0881 | 122.8958 | 122.9691 | 122.7585 | 123.143 | 122.9233 | 122.5662 | 122.9691 | 122.7585 | 122.9233 | 122.8958 | 123.143 | -0.64545 | -0.5127
3513.7656 | 123.1018 | -122.8409 | 0.18768 | 0.16869 | 0.015193 | -0.00011543 | 0.046437 | -0.014693 | -0.014253 | 0.010271 | -0.16479 | 0.10986 | -0.48065 | -0.022888 | -0.022888 | -0.004578 | -0.018311 | 0.12817 | 0.27466 | -0.33417 | 122.3602 | -0.07782 | 122.6761 | 122.818 | -0.21057 | 122.5067 | 0.086975 | 0.31586 | 122.8226 | 122.9691 | 122.818 | 122.9507 | 122.6761 | 123.1155 | 122.8363 | 122.5067 | 122.9507 | 122.6761 | 122.8363 | 122.818 | 123.1155 | -0.66834 | -0.52185
3515.5312 | 123.1796 | -122.8043 | 0.18768 | -0.19753 | 0.010493 | -0.0075922 | 0.042379 | -0.015548 | -0.011262 | 0.0092029 | -0.19226 | 0.10071 | -0.46234 | -0.013733 | 0.004578 | 0 | 0.045776 | 0.17395 | 0.27466 | -0.32044 | 122.3419 | -0.086975 | 122.612 | 122.7905 | -0.1831 | 122.4838 | 0.086975 | 0.27008 | 122.85 | 122.9782 | 122.8088 | 122.905 | 122.612 | 123.0789 | 122.8043 | 122.4838 | 122.905 | 122.612 | 122.8043 | 122.8088 | 123.0789 | -0.65002 | -0.50812
3517.2969 | 123.0743 | -122.8271 | 0.2243 | -0.052567 | 0.011561 | -0.0084466 | 0.045583 | -0.016188 | -0.013826 | 0.010271 | -0.1236 | 0.086975 | -0.44861 | 0.018311 | 0.004578 | 0.036621 | -0.018311 | 0.17853 | 0.27466 | -0.31128 | 122.3785 | -0.13733 | 122.7036 | 122.8455 | -0.21973 | 122.5159 | 0.050354 | 0.32501 | 122.8088 | 123.0057 | 122.8317 | 122.9141 | 122.7036 | 123.1018 | 122.8638 | 122.5159 | 122.9141 | 122.7036 | 122.8638 | 122.8317 | 123.1018 | -0.67291 | -0.53558
3519.0625 | 123.2117 | -122.818 | 0.17395 | -0.2433 | 0.010493 | -0.0058832 | 0.039388 | -0.018538 | -0.01169 | 0.010912 | -0.20142 | 0.11444 | -0.46692 | -0.041199 | 0.013733 | 0.013733 | 0.054932 | 0.18768 | 0.2655 | -0.35248 | 122.3511 | -0.059509 | 122.6166 | 122.7768 | -0.16022 | 122.4655 | 0.091553 | 0.2655 | 122.8729 | 123.0057 | 122.8317 | 122.9324 | 122.6166 | 123.0835 | 122.8317 | 122.4655 | 122.9324 | 122.6166 | 122.8317 | 122.8317 | 123.0835 | -0.64087 | -0.52643
3520.7656 | 123.0972 | -122.8409 | 0.21057 | 0.13817 | 0.010921 | -0.0086602 | 0.046865 | -0.013839 | -0.014039 | 0.010698 | -0.19226 | 0.10986 | -0.43945 | -0.050354 | -0.009155 | 0 | 0 | 0.12817 | 0.27008 | -0.31586 | 122.4014 | -0.10071 | 122.6486 | 122.7905 | -0.21973 | 122.525 | 0.05951 | 0.24719 | 122.8409 | 122.9691 | 122.8317 | 122.9507 | 122.6486 | 123.111 | 122.8409 | 122.525 | 122.9507 | 122.6486 | 122.8409 | 122.8317 | 123.111 | -0.65002 | -0.52643
3522.5312 | 123.1613 | -122.8226 | 0.1831 | -0.15938 | 0.010493 | -0.0063104 | 0.037679 | -0.018538 | -0.011476 | 0.010698 | -0.091553 | 0.059509 | -0.41657 | 0.064087 | 0.10529 | 0.11902 | -0.064087 | 0.30212 | 0.24261 | -0.29755 | 122.406 | -0.1236 | 122.731 | 122.8867 | -0.077819 | 122.525 | 0.05951 | 0.32501 | 122.7585 | 123.1247 | 122.9279 | 122.8821 | 122.731 | 123.0652 | 122.9416 | 122.525 | 122.8821 | 122.731 | 122.9416 | 122.9279 | 123.0652 | -0.59967 | -0.48065
3524.2969 | 123.1979 | -122.8271 | 0.1831 | -0.27382 | 0.010707 | -0.0052422 | 0.04131 | -0.018965 | -0.011476 | 0.011126 | -0.14191 | 0.091553 | -0.43488 | 0.013733 | 0.041199 | 0.054932 | 0.004578 | 0.22888 | 0.2655 | -0.29755 | 122.3923 | -0.091552 | 122.6852 | 122.8409 | -0.14191 | 122.5296 | 0.082398 | 0.29297 | 122.8317 | 123.056 | 122.8683 | 122.9187 | 122.6852 | 123.0927 | 122.8821 | 122.5296 | 122.9187 | 122.6852 | 122.8821 | 122.8683 | 123.0927 | -0.61798 | -0.48065
3526 | 123.0698 | -122.8592 | 0.21057 | -0.083084 | 0.012416 | -0.004815 | 0.047506 | -0.01512 | -0.014467 | 0.011126 | -0.10986 | 0.09613 | -0.44403 | 0.022888 | 0.022888 | 0.050354 | -0.027466 | 0.20599 | 0.2655 | -0.30212 | 122.4152 | -0.11444 | 122.7493 | 122.8821 | -0.18768 | 122.5571 | 0.054932 | 0.33417 | 122.8317 | 123.0652 | 122.8821 | 122.9553 | 122.7493 | 123.1247 | 122.9095 | 122.5571 | 122.9553 | 122.7493 | 122.9095 | 122.8821 | 123.1247 | -0.6546 | -0.5127
3527.7656 | 123.1384 | -122.85 | 0.17853 | -0.16701 | 0.01028 | -0.009942 | 0.038961 | -0.019179 | -0.010621 | 0.0098437 | -0.073242 | 0.073242 | -0.39825 | 0.082397 | 0.1236 | 0.15106 | -0.11444 | 0.33417 | 0.23804 | -0.29297 | 122.4518 | -0.10529 | 122.7768 | 122.9324 | -0.054932 | 122.5571 | 0.059509 | 0.32501 | 122.7356 | 123.1842 | 122.9736 | 122.9233 | 122.7768 | 123.0881 | 123.0011 | 122.5571 | 122.9233 | 122.7768 | 123.0011 | 122.9736 | 123.0881 | -0.57678 | -0.4715
3529.5156 | 123.1842 | -122.8088 | 0.16937 | -0.052567 | 0.0092115 | -0.0056696 | 0.040456 | -0.018111 | -0.011476 | 0.011126 | -0.14191 | 0.082397 | -0.41199 | 0.068665 | 0.091553 | 0.11902 | -0.11902 | 0.27924 | 0.24261 | -0.29755 | 122.3969 | -0.086976 | 122.6669 | 122.8775 | -0.07782 | 122.5113 | 0.073242 | 0.27008 | 122.6898 | 123.0881 | 122.9004 | 122.8912 | 122.6669 | 123.0515 | 122.9279 | 122.5113 | 122.8912 | 122.6669 | 122.9279 | 122.9004 | 123.0515 | -0.58136 | -0.46692
3531.2656 | 123.1567 | -122.8043 | 0.16479 | -0.090714 | 0.0079297 | -0.0067376 | 0.041524 | -0.020674 | -0.010621 | 0.010057 | -0.13733 | 0.073242 | -0.42572 | 0.07782 | 0.10529 | 0.12817 | -0.1236 | 0.31128 | 0.23804 | -0.3067 | 122.3785 | -0.091553 | 122.6669 | 122.8821 | -0.059509 | 122.4976 | 0.073242 | 0.28839 | 122.6807 | 123.1155 | 122.9095 | 122.8775 | 122.6669 | 123.0423 | 122.9324 | 122.4976 | 122.8775 | 122.6669 | 122.9324 | 122.9095 | 123.0423 | -0.59052 | -0.4715
3533.0469 | 123.0469 | -122.8409 | 0.20142 | 0.1458 | 0.011561 | -0.002038 | 0.046651 | -0.015548 | -0.012117 | 0.011553 | -0.10529 | 0.07782 | -0.44403 | 0.07782 | 0.082397 | 0.10986 | -0.16479 | 0.25177 | 0.2243 | -0.2655 | 122.3969 | -0.1236 | 122.7356 | 122.9187 | -0.11902 | 122.5754 | 0.022888 | 0.33875 | 122.6761 | 123.0927 | 122.9233 | 122.9187 | 122.7356 | 123.0652 | 122.9507 | 122.5754 | 122.9187 | 122.7356 | 122.9507 | 122.9233 | 123.0652 | -0.64545 | -0.46692
3534.8125 | 123.0606 | -122.8592 | 0.21057 | 0.12291 | 0.010921 | -0.0035332 | 0.044301 | -0.017256 | -0.013399 | 0.0096301 | -0.091553 | 0.054932 | -0.42572 | 0.091553 | 0.082397 | 0.13733 | -0.1831 | 0.27008 | 0.23346 | -0.27924 | 122.4335 | -0.15564 | 122.7676 | 122.9507 | -0.12817 | 122.58 | 0.022888 | 0.33417 | 122.6761 | 123.1293 | 122.9416 | 122.9141 | 122.7676 | 123.0927 | 122.9965 | 122.58 | 122.9141 | 122.7676 | 122.9965 | 122.9416 | 123.0927 | -0.63629 | -0.48981
3536.5781 | 123.1567 | -122.8134 | 0.19684 | -0.16701 | 0.0096387 | -0.0071648 | 0.044515 | -0.021102 | -0.012544 | 0.0079211 | -0.10529 | 0.054932 | -0.44861 | 0.091553 | 0.09613 | 0.10071 | -0.086975 | 0.3067 | 0.24719 | -0.3067 | 122.3648 | -0.14191 | 122.7081 | 122.905 | -0.10071 | 122.5067 | 0.050354 | 0.34332 | 122.7264 | 123.1201 | 122.9095 | 122.8683 | 122.7081 | 123.0606 | 122.9141 | 122.5067 | 122.8683 | 122.7081 | 122.9141 | 122.9095 | 123.0606 | -0.64545 | -0.50354
3538.2812 | 123.111 | -122.8271 | 0.20599 | 0.077133 | 0.0098523 | -0.0054558 | 0.050283 | -0.016829 | -0.015321 | 0.0098437 | -0.19226 | 0.082397 | -0.46234 | -0.009155 | -0.022888 | 0 | -0.004578 | 0.14191 | 0.2655 | -0.31128 | 122.3648 | -0.1236 | 122.6349 | 122.818 | -0.22888 | 122.5159 | 0.059509 | 0.27008 | 122.8226 | 122.9691 | 122.8043 | 122.9095 | 122.6349 | 123.0927 | 122.8271 | 122.5159 | 122.9095 | 122.6349 | 122.8271 | 122.8043 | 123.0927 | -0.66834 | -0.51727
3540.0312 | 123.0927 | -122.85 | 0.18768 | 0.15343 | 0.0098523 | -0.0067376 | 0.041524 | -0.018538 | -0.011903 | 0.0098437 | -0.11902 | 0.032043 | -0.4303 | 0.054932 | 0.082397 | 0.10986 | -0.16937 | 0.2655 | 0.22888 | -0.28381 | 122.4197 | -0.15564 | 122.731 | 122.905 | -0.10529 | 122.5662 | 0.041199 | 0.31128 | 122.6807 | 123.1155 | 122.9324 | 122.8821 | 122.731 | 123.0789 | 122.9599 | 122.5662 | 122.8821 | 122.731 | 122.9599 | 122.9324 | 123.0789 | -0.61798 | -0.4715
3541.8125 | 123.1522 | -122.8271 | 0.17395 | -0.15175 | 0.0098523 | -0.009942 | 0.042165 | -0.018325 | -0.010621 | 0.010912 | -0.073242 | 0.064087 | -0.42572 | 0.10071 | 0.10986 | 0.14648 | -0.1236 | 0.33417 | 0.2243 | -0.29755 | 122.4014 | -0.10986 | 122.7539 | 122.9279 | -0.064087 | 122.5296 | 0.050354 | 0.35248 | 122.7036 | 123.1613 | 122.937 | 122.8912 | 122.7539 | 123.0515 | 122.9736 | 122.5296 | 122.8912 | 122.7539 | 122.9736 | 122.937 | 123.0515 | -0.59967 | -0.4715
3543.5781 | 123.1476 | -122.8043 | 0.1831 | -0.098343 | 0.0089979 | -0.0093012 | 0.041738 | -0.021529 | -0.010621 | 0.0085619 | -0.073242 | 0.054932 | -0.41657 | 0.11444 | 0.12817 | 0.15564 | -0.15564 | 0.32044 | 0.23346 | -0.29297 | 122.3877 | -0.12817 | 122.731 | 122.9187 | -0.054931 | 122.5113 | 0.050354 | 0.34332 | 122.6486 | 123.1247 | 122.9324 | 122.8592 | 122.731 | 123.0377 | 122.9599 | 122.5113 | 122.8592 | 122.731 | 122.9599 | 122.9324 | 123.0377 | -0.59967 | -0.47607
3545.2812 | 123.0835 | -122.8271 | 0.21515 | 0.1992 | 0.011348 | -0.003106 | 0.04836 | -0.01747 | -0.012758 | 0.011766 | -0.17395 | 0.082397 | -0.46692 | 0.022888 | 0.009155 | 0.059509 | -0.086975 | 0.18768 | 0.25635 | -0.29297 | 122.3602 | -0.13275 | 122.6532 | 122.85 | -0.20599 | 122.5342 | 0.041199 | 0.29297 | 122.7402 | 123.0148 | 122.8363 | 122.9095 | 122.6532 | 123.0835 | 122.8867 | 122.5342 | 122.9095 | 122.6532 | 122.8867 | 122.8363 | 123.0835 | -0.68207 | -0.50812
3546.9844 | 123.1522 | -122.8043 | 0.19684 | -0.20515 | 0.010921 | -0.0058832 | 0.040456 | -0.019179 | -0.01169 | 0.010271 | -0.086975 | 0.068665 | -0.43488 | 0.09613 | 0.11902 | 0.13275 | -0.11444 | 0.3067 | 0.24719 | -0.28381 | 122.3694 | -0.12817 | 122.7173 | 122.9004 | -0.077819 | 122.5204 | 0.050354 | 0.3479 | 122.6898 | 123.111 | 122.9233 | 122.8729 | 122.7173 | 123.0515 | 122.937 | 122.5204 | 122.8729 | 122.7173 | 122.937 | 122.9233 | 123.0515 | -0.63171 | -0.48065
3548.75 | 123.143 | -122.8134 | 0.1831 | -0.19753 | 0.010707 | -0.009942 | 0.048787 | -0.018752 | -0.015107 | 0.0092029 | -0.17395 | 0.10529 | -0.48523 | 0.032043 | 0.022888 | 0.032043 | 0.004578 | 0.21973 | 0.25635 | -0.31128 | 122.3282 | -0.077819 | 122.6395 | 122.8455 | -0.16022 | 122.5021 | 0.073243 | 0.31128 | 122.818 | 123.0331 | 122.8363 | 122.9187 | 122.6395 | 123.0698 | 122.8455 | 122.5021 | 122.9187 | 122.6395 | 122.8455 | 122.8363 | 123.0698 | -0.66833 | -0.49438
3550.5312 | 123.0698 | -122.8683 | 0.20599 | -0.060196 | 0.010707 | -0.0078058 | 0.047933 | -0.016829 | -0.014894 | 0.0096301 | -0.12817 | 0.091553 | -0.4715 | 0.036621 | 0.027466 | 0.041199 | -0.027466 | 0.19684 | 0.25177 | -0.31586 | 122.3969 | -0.11444 | 122.7402 | 122.905 | -0.17853 | 122.5525 | 0.045776 | 0.34332 | 122.8409 | 123.0652 | 122.8958 | 122.9599 | 122.7402 | 123.1201 | 122.9095 | 122.5525 | 122.9599 | 122.7402 | 122.9095 | 122.8958 | 123.1201 | -0.67749 | -0.52185
3552.2344 | 123.1888 | -122.8226 | 0.1831 | -0.28145 | 0.011561 | -0.006524 | 0.043874 | -0.018752 | -0.013399 | 0.0098437 | -0.21515 | 0.11444 | -0.48981 | -0.022888 | 0.004578 | 0 | 0.064087 | 0.17853 | 0.28381 | -0.33417 | 122.3328 | -0.068664 | 122.6074 | 122.7997 | -0.17853 | 122.4884 | 0.10071 | 0.27466 | 122.8867 | 123.0011 | 122.8271 | 122.937 | 122.6074 | 123.1064 | 122.8226 | 122.4884 | 122.937 | 122.6074 | 122.8226 | 122.8271 | 123.1064 | -0.67291 | -0.51727
3554.0156 | 123.175 | -122.7859 | 0.17395 | 0.038986 | 0.013057 | -0.0035332 | 0.038533 | -0.018538 | -0.011476 | 0.010271 | -0.16479 | 0.082397 | -0.42114 | 0.022888 | 0.064087 | 0.073242 | -0.09613 | 0.23346 | 0.24719 | -0.31128 | 122.3648 | -0.091553 | 122.6212 | 122.8088 | -0.10986 | 122.4747 | 0.073242 | 0.25635 | 122.6898 | 123.0194 | 122.85 | 122.8683 | 122.6212 | 123.0331 | 122.8592 | 122.4747 | 122.8683 | 122.6212 | 122.8592 | 122.85 | 123.0331 | -0.59509 | -0.48523
3555.7812 | 123.1842 | -122.7814 | 0.16937 | 0.023727 | 0.01028 | -0.0097284 | 0.038533 | -0.020888 | -0.0097669 | 0.0098437 | -0.16479 | 0.068665 | -0.43488 | 0.032043 | 0.059509 | 0.09613 | -0.086975 | 0.24261 | 0.2243 | -0.30212 | 122.3465 | -0.10071 | 122.6166 | 122.8134 | -0.10986 | 122.4792 | 0.054931 | 0.27008 | 122.6944 | 123.024 | 122.8409 | 122.85 | 122.6166 | 123.0057 | 122.8775 | 122.4792 | 122.85 | 122.6166 | 122.8775 | 122.8409 | 123.0057 | -0.60425 | -0.4715
3557.4844 | 123.1201 | -122.85 | 0.19684 | 0.084762 | 0.011989 | -0.0033196 | 0.049001 | -0.015548 | -0.01233 | 0.0089893 | -0.20142 | 0.091553 | -0.46234 | -0.018311 | -0.032043 | -0.009155 | 0.013733 | 0.12817 | 0.27008 | -0.31128 | 122.3877 | -0.10529 | 122.6486 | 122.8317 | -0.22888 | 122.5388 | 0.073243 | 0.26092 | 122.8638 | 122.9782 | 122.818 | 122.9416 | 122.6486 | 123.1201 | 122.8409 | 122.5388 | 122.9416 | 122.6486 | 122.8409 | 122.818 | 123.1201 | -0.65918 | -0.50812
3559.2344 | 123.1155 | -122.8409 | 0.19226 | 0.1458 | 0.011348 | -0.0050286 | 0.045156 | -0.016188 | -0.014039 | 0.010485 | -0.18768 | 0.09613 | -0.47607 | -0.022888 | -0.018311 | 0.004578 | -0.009155 | 0.13275 | 0.27008 | -0.32044 | 122.3648 | -0.096131 | 122.6532 | 122.818 | -0.21057 | 122.5204 | 0.07782 | 0.28839 | 122.8317 | 122.9736 | 122.8226 | 122.937 | 122.6532 | 123.111 | 122.8455 | 122.5204 | 122.937 | 122.6532 | 122.8455 | 122.8226 | 123.111 | -0.66834 | -0.5127
3560.9844 | 123.0698 | -122.8271 | 0.20142 | 0.17632 | 0.010921 | -0.0039606 | 0.042165 | -0.018538 | -0.012758 | 0.0098437 | -0.091553 | 0.059509 | -0.42572 | 0.086975 | 0.11444 | 0.15106 | -0.19226 | 0.27466 | 0.24261 | -0.27466 | 122.4014 | -0.14191 | 122.7356 | 122.9141 | -0.086975 | 122.5525 | 0.041199 | 0.33417 | 122.6349 | 123.1018 | 122.9416 | 122.8867 | 122.7356 | 123.0698 | 122.9782 | 122.5525 | 122.8867 | 122.7356 | 122.9782 | 122.9416 | 123.0698 | -0.62714 | -0.47607
3562.6875 | 123.0698 | -122.8546 | 0.20142 | -0.029679 | 0.013057 | -0.003106 | 0.044515 | -0.016829 | -0.014894 | 0.010057 | -0.13733 | 0.09613 | -0.46234 | 0.022888 | 0.013733 | 0.027466 | -0.013733 | 0.18768 | 0.28381 | -0.30212 | 122.3923 | -0.10529 | 122.7173 | 122.8775 | -0.18768 | 122.5525 | 0.082397 | 0.32501 | 122.8409 | 123.0423 | 122.8683 | 122.9507 | 122.7173 | 123.1384 | 122.8821 | 122.5525 | 122.9507 | 122.7173 | 122.8821 | 122.8683 | 123.1384 | -0.66376 | -0.50354
3564.4531 | 123.0927 | -122.8775 | 0.19684 | -0.12123 | 0.010921 | -0.0058832 | 0.045156 | -0.017684 | -0.014253 | 0.0092029 | -0.14648 | 0.091553 | -0.48523 | 0.054932 | 0.045776 | 0.050354 | -0.022888 | 0.20599 | 0.26093 | -0.28381 | 122.3923 | -0.10529 | 122.731 | 122.9324 | -0.15106 | 122.5937 | 0.064087 | 0.33875 | 122.8546 | 123.0835 | 122.9233 | 122.9691 | 122.731 | 123.1384 | 122.9279 | 122.5937 | 122.9691 | 122.731 | 122.9279 | 122.9233 | 123.1384 | -0.68207 | -0.48065
3566.2188 | 123.0743 | -122.8546 | 0.2243 | -0.12886 | 0.011775 | -0.0093012 | 0.043874 | -0.014266 | -0.014039 | 0.0096301 | -0.14191 | 0.07782 | -0.47607 | 0.027466 | 0.041199 | 0.054932 | -0.036621 | 0.21973 | 0.27466 | -0.30212 | 122.3785 | -0.14648 | 122.7127 | 122.8821 | -0.18311 | 122.5525 | 0.050354 | 0.33417 | 122.818 | 123.0743 | 122.8958 | 122.9324 | 122.7127 | 123.1293 | 122.9095 | 122.5525 | 122.9324 | 122.7127 | 122.9095 | 122.8958 | 123.1293 | -0.70038 | -0.52643
3568.0156 | 123.0606 | -122.8546 | 0.19226 | -0.12123 | 0.010493 | -0.0088738 | 0.044942 | -0.014693 | -0.01169 | 0.010271 | -0.14191 | 0.091553 | -0.47607 | 0.032043 | 0.045776 | 0.064087 | -0.036621 | 0.2243 | 0.28381 | -0.31586 | 122.3785 | -0.10071 | 122.7127 | 122.8867 | -0.14648 | 122.5388 | 0.091552 | 0.33417 | 122.818 | 123.0789 | 122.9004 | 122.9462 | 122.7127 | 123.1384 | 122.9187 | 122.5388 | 122.9462 | 122.7127 | 122.9187 | 122.9004 | 123.1384 | -0.66834 | -0.50812
3569.7656 | 123.0469 | -122.8546 | 0.20142 | 0.21446 | 0.0094251 | -0.0067376 | 0.04131 | -0.016616 | -0.012117 | 0.0087757 | -0.12817 | 0.073242 | -0.43945 | 0.073242 | 0.10529 | 0.14191 | -0.15106 | 0.25635 | 0.23804 | -0.27008 | 122.4152 | -0.12817 | 122.7264 | 122.9279 | -0.09613 | 122.5845 | 0.036621 | 0.31128 | 122.7036 | 123.111 | 122.9599 | 122.9279 | 122.7264 | 123.0927 | 122.9965 | 122.5845 | 122.9279 | 122.7264 | 122.9965 | 122.9599 | 123.0927 | -0.64087 | -0.4715
3571.5156 | 123.0652 | -122.8592 | 0.20599 | 0.19157 | 0.0089979 | -0.003747 | 0.040456 | -0.015761 | -0.012758 | 0.0098437 | -0.091553 | 0.059509 | -0.42572 | 0.086975 | 0.091553 | 0.15106 | -0.20142 | 0.27924 | 0.20599 | -0.27466 | 122.4335 | -0.14649 | 122.7676 | 122.9462 | -0.11444 | 122.5845 | 0 | 0.33417 | 122.6578 | 123.1384 | 122.9507 | 122.9187 | 122.7676 | 123.0652 | 123.0103 | 122.5845 | 122.9187 | 122.7676 | 123.0103 | 122.9507 | 123.0652 | -0.63171 | -0.48065
3573.2188 | 123.0652 | -122.8455 | 0.21973 | -0.060196 | 0.011775 | -0.001397 | 0.046865 | -0.017256 | -0.012117 | 0.0096301 | -0.1236 | 0.086975 | -0.45776 | 0.041199 | 0.027466 | 0.054932 | -0.032043 | 0.20599 | 0.27008 | -0.31128 | 122.3877 | -0.13275 | 122.7219 | 122.8867 | -0.19226 | 122.5342 | 0.050354 | 0.33417 | 122.8134 | 123.0515 | 122.8729 | 122.9324 | 122.7219 | 123.1155 | 122.9004 | 122.5342 | 122.9324 | 122.7219 | 122.9004 | 122.8729 | 123.1155 | -0.67749 | -0.53101
3574.9844 | 123.143 | -122.8317 | 0.17853 | 0.10765 | 0.0098523 | 0.00031197 | 0.038961 | -0.016829 | -0.011476 | 0.0066393 | -0.13733 | 0.064087 | -0.43488 | 0.022888 | 0.064087 | 0.10986 | -0.1236 | 0.23804 | 0.23346 | -0.29297 | 122.3969 | -0.11444 | 122.6944 | 122.8546 | -0.11444 | 122.5388 | 0.054931 | 0.29755 | 122.7081 | 123.0698 | 122.8958 | 122.8958 | 122.6944 | 123.0652 | 122.9416 | 122.5388 | 122.8958 | 122.6944 | 122.9416 | 122.8958 | 123.0652 | -0.6134 | -0.4715
3576.7344 | 123.1567 | -122.8043 | 0.19226 | -0.13649 | 0.010707 | -0.01101 | 0.041097 | -0.020034 | -0.0093395 | 0.0087757 | -0.12817 | 0.059509 | -0.43945 | 0.082397 | 0.12817 | 0.16022 | -0.13275 | 0.32501 | 0.24261 | -0.27008 | 122.3648 | -0.13275 | 122.6761 | 122.8867 | -0.064087 | 122.5342 | 0.050354 | 0.31128 | 122.6715 | 123.1293 | 122.9324 | 122.8638 | 122.6761 | 123.0469 | 122.9645 | 122.5342 | 122.8638 | 122.6761 | 122.9645 | 122.9324 | 123.0469 | -0.63171 | -0.46234
3578.5 | 123.1888 | -122.8271 | 0.17853 | -0.25856 | 0.011134 | -0.0063104 | 0.044728 | -0.018111 | -0.014894 | 0.0096301 | -0.2243 | 0.086975 | -0.47607 | -0.013733 | 0 | -0.004578 | 0.068665 | 0.19226 | 0.27924 | -0.33417 | 122.3511 | -0.091553 | 122.6028 | 122.8134 | -0.17853 | 122.493 | 0.10071 | 0.25177 | 122.8958 | 123.0194 | 122.8271 | 122.9141 | 122.6028 | 123.1064 | 122.8226 | 122.493 | 122.9141 | 122.6028 | 122.8226 | 122.8271 | 123.1064 | -0.6546 | -0.5127
3580.2656 | 123.1018 | -122.8455 | 0.19684 | 0.15343 | 0.0098523 | -0.0056696 | 0.044942 | -0.017897 | -0.014253 | 0.0096301 | -0.19684 | 0.09613 | -0.48065 | -0.027466 | -0.036621 | 0.004578 | -0.009155 | 0.14191 | 0.25635 | -0.32044 | 122.3648 | -0.10071 | 122.6486 | 122.818 | -0.23346 | 122.525 | 0.05951 | 0.28381 | 122.8363 | 122.9874 | 122.8088 | 122.9416 | 122.6486 | 123.1018 | 122.85 | 122.525 | 122.9416 | 122.6486 | 122.85 | 122.8088 | 123.1018 | -0.67749 | -0.51727
3582.0312 | 123.1155 | -122.85 | 0.21057 | 0.092392 | 0.012416 | -0.0039606 | 0.047078 | -0.015761 | -0.011262 | 0.010485 | -0.16937 | 0.07782 | -0.46692 | -0.036621 | -0.022888 | -0.013733 | 0.022888 | 0.14191 | 0.25635 | -0.33875 | 122.3831 | -0.13275 | 122.6807 | 122.8134 | -0.23346 | 122.5113 | 0.045777 | 0.29755 | 122.8729 | 122.9919 | 122.8271 | 122.9279 | 122.6807 | 123.1064 | 122.8363 | 122.5113 | 122.9279 | 122.6807 | 122.8363 | 122.8271 | 123.1064 | -0.67749 | -0.54932
3583.7969 | 123.1476 | -122.8271 | 0.16937 | -0.20515 | 0.0087841 | -0.009942 | 0.039388 | -0.01747 | -0.010621 | 0.011126 | -0.13275 | 0.054932 | -0.45319 | 0.07782 | 0.10071 | 0.11902 | -0.09613 | 0.3067 | 0.23804 | -0.28839 | 122.374 | -0.11444 | 122.6944 | 122.905 | -0.068665 | 122.5388 | 0.068664 | 0.32043 | 122.731 | 123.1338 | 122.9279 | 122.8821 | 122.6944 | 123.0652 | 122.9462 | 122.5388 | 122.8821 | 122.6944 | 122.9462 | 122.9279 | 123.0652 | -0.62256 | -0.45776
3585.5 | 123.1155 | -122.85 | 0.19684 | 0.069504 | 0.01327 | -0.0095148 | 0.047719 | -0.016829 | -0.014894 | 0.010057 | -0.18768 | 0.073242 | -0.46234 | -0.027466 | -0.027466 | 0.013733 | 0.027466 | 0.14191 | 0.28381 | -0.31128 | 122.3877 | -0.1236 | 122.6624 | 122.8226 | -0.2243 | 122.5388 | 0.086975 | 0.27466 | 122.8775 | 122.9919 | 122.8226 | 122.9233 | 122.6624 | 123.1338 | 122.8638 | 122.5388 | 122.9233 | 122.6624 | 122.8638 | 122.8226 | 123.1338 | -0.65918 | -0.50812
3587.2656 | 123.143 | -122.818 | 0.17853 | -0.15938 | 0.010066 | -0.0028924 | 0.03832 | -0.018111 | -0.012117 | 0.0077075 | -0.068665 | 0.050354 | -0.40741 | 0.091553 | 0.11444 | 0.15106 | -0.12817 | 0.33875 | 0.23804 | -0.28381 | 122.4106 | -0.12817 | 122.7493 | 122.9095 | -0.064087 | 122.5342 | 0.059509 | 0.33874 | 122.6898 | 123.1567 | 122.9324 | 122.8683 | 122.7493 | 123.056 | 122.9691 | 122.5342 | 122.8683 | 122.7493 | 122.9691 | 122.9324 | 123.056 | -0.58594 | -0.46234
3588.9688 | 123.1842 | -122.8271 | 0.16479 | -0.2433 | 0.011561 | -0.0050286 | 0.045583 | -0.017256 | -0.013185 | 0.0096301 | -0.20599 | 0.10071 | -0.4715 | -0.018311 | -0.009155 | 0.018311 | 0.036621 | 0.18768 | 0.28839 | -0.32501 | 122.3557 | -0.064087 | 122.6212 | 122.8088 | -0.17395 | 122.5021 | 0.1236 | 0.2655 | 122.8638 | 123.0148 | 122.818 | 122.9279 | 122.6212 | 123.1155 | 122.8455 | 122.5021 | 122.9279 | 122.6212 | 122.8455 | 122.818 | 123.1155 | -0.63629 | -0.48981
3590.7344 | 123.1888 | -122.818 | 0.18768 | -0.20515 | 0.012843 | -0.0054558 | 0.043447 | -0.017684 | -0.012971 | 0.010057 | -0.20599 | 0.10529 | -0.48065 | -0.009155 | 0.018311 | 0.004578 | 0.045776 | 0.1831 | 0.28839 | -0.32501 | 122.3373 | -0.082397 | 122.612 | 122.8088 | -0.16937 | 122.493 | 0.10071 | 0.27466 | 122.8638 | 123.0011 | 122.8363 | 122.9233 | 122.612 | 123.1064 | 122.8226 | 122.493 | 122.9233 | 122.612 | 122.8226 | 122.8363 | 123.1064 | -0.66834 | -0.5127
3592.5 | 123.0835 | -122.8088 | 0.19684 | 0.10765 | 0.010066 | -0.0046014 | 0.04067 | -0.014907 | -0.011903 | 0.0087757 | -0.10986 | 0.032043 | -0.45776 | 0.050354 | 0.09613 | 0.13275 | -0.16479 | 0.27008 | 0.2243 | -0.28839 | 122.3511 | -0.1648 | 122.699 | 122.8592 | -0.10071 | 122.5204 | 0.027466 | 0.3479 | 122.644 | 123.0789 | 122.905 | 122.8409 | 122.699 | 123.0331 | 122.9416 | 122.5204 | 122.8409 | 122.699 | 122.9416 | 122.905 | 123.0331 | -0.6546 | -0.48523
3594.25 | 123.0743 | -122.8592 | 0.19684 | 0.23735 | 0.01028 | -0.0035332 | 0.044728 | -0.014479 | -0.012117 | 0.010698 | -0.15106 | 0.068665 | -0.47607 | 0.045776 | 0.050354 | 0.091553 | -0.13275 | 0.24261 | 0.24261 | -0.29297 | 122.3831 | -0.12817 | 122.7081 | 122.905 | -0.14648 | 122.5662 | 0.045777 | 0.32501 | 122.7264 | 123.1018 | 122.9095 | 122.9279 | 122.7081 | 123.1018 | 122.9507 | 122.5662 | 122.9279 | 122.7081 | 122.9507 | 122.9095 | 123.1018 | -0.67291 | -0.48981
3596.0156 | 123.1659 | -122.8409 | 0.19684 | 0.2755 | 0.010921 | -0.0058832 | 0.040029 | -0.019179 | -0.011049 | 0.0087757 | -0.16022 | 0.059509 | -0.4303 | 0.022888 | 0.064087 | 0.086975 | -0.11444 | 0.2243 | 0.25635 | -0.30212 | 122.4106 | -0.13733 | 122.6807 | 122.8638 | -0.13275 | 122.5388 | 0.05951 | 0.27008 | 122.7264 | 123.0652 | 122.905 | 122.9004 | 122.6807 | 123.0972 | 122.9279 | 122.5388 | 122.9004 | 122.6807 | 122.9279 | 122.905 | 123.0972 | -0.62714 | -0.49896
3597.7188 | 123.0652 | -122.85 | 0.20599 | 0.17632 | 0.0092115 | -0.0050286 | 0.04366 | -0.017897 | -0.010835 | 0.0092029 | -0.10986 | 0.022888 | -0.4303 | 0.082397 | 0.07782 | 0.12817 | -0.17853 | 0.27466 | 0.20599 | -0.28839 | 122.4197 | -0.18311 | 122.7402 | 122.9324 | -0.12817 | 122.5616 | 0 | 0.32044 | 122.6715 | 123.1247 | 122.9279 | 122.8729 | 122.7402 | 123.056 | 122.9782 | 122.5616 | 122.8729 | 122.7402 | 122.9782 | 122.9279 | 123.056 | -0.63629 | -0.49439
3599.4688 | 123.1064 | -122.8363 | 0.19684 | 0.17632 | 0.011775 | -0.0035332 | 0.043233 | -0.019179 | -0.0093395 | 0.0094165 | -0.11444 | 0.059509 | -0.44403 | 0.045776 | 0.059509 | 0.10071 | -0.14648 | 0.25635 | 0.24719 | -0.28839 | 122.3923 | -0.13733 | 122.7219 | 122.8821 | -0.13733 | 122.5479 | 0.050354 | 0.32959 | 122.6898 | 123.0927 | 122.8958 | 122.8958 | 122.7219 | 123.0835 | 122.937 | 122.5479 | 122.8958 | 122.7219 | 122.937 | 122.8958 | 123.0835 | -0.64087 | -0.48523
3601.2188 | 123.1842 | -122.8134 | 0.1831 | 0.00083945 | 0.0098523 | -0.009942 | 0.039601 | -0.021743 | -0.010835 | 0.0092029 | -0.18768 | 0.045776 | -0.4715 | 0.032043 | 0.045776 | 0.086975 | -0.09613 | 0.27008 | 0.23346 | -0.29755 | 122.3419 | -0.13733 | 122.6257 | 122.8455 | -0.13733 | 122.5159 | 0.050354 | 0.28381 | 122.7173 | 123.0835 | 122.8592 | 122.8592 | 122.6257 | 123.0469 | 122.9004 | 122.5159 | 122.8592 | 122.6257 | 122.9004 | 122.8592 | 123.0469 | -0.6546 | -0.48065
3602.9219 | 123.1659 | -122.7768 | 0.19684 | 0.0084684 | 0.011348 | -0.008233 | 0.042379 | -0.017897 | -0.010194 | 0.0098437 | -0.14648 | 0.045776 | -0.42572 | 0.050354 | 0.068665 | 0.082397 | -0.12817 | 0.24719 | 0.23804 | -0.28839 | 122.3511 | -0.15106 | 122.6303 | 122.8271 | -0.12817 | 122.4884 | 0.041199 | 0.27924 | 122.6486 | 123.024 | 122.8455 | 122.8226 | 122.6303 | 123.0148 | 122.8592 | 122.4884 | 122.8226 | 122.6303 | 122.8592 | 122.8455 | 123.0148 | -0.62256 | -0.48523
3604.6719 | 123.111 | -122.8683 | 0.20599 | 0.092392 | 0.011775 | -0.00096983 | 0.050069 | -0.016188 | -0.011903 | 0.0079211 | -0.18768 | 0.086975 | -0.48981 | -0.022888 | -0.036621 | -0.022888 | 0.013733 | 0.11444 | 0.27008 | -0.32501 | 122.3785 | -0.11902 | 122.6807 | 122.8455 | -0.24262 | 122.5433 | 0.064087 | 0.30212 | 122.8821 | 122.9828 | 122.8317 | 122.9553 | 122.6807 | 123.1384 | 122.8455 | 122.5433 | 122.9553 | 122.6807 | 122.8455 | 122.8317 | 123.1384 | -0.6958 | -0.53101
3606.375 | 123.1796 | -122.8317 | 0.1831 | -0.23567 | 0.012202 | -0.0050286 | 0.043019 | -0.018752 | -0.011049 | 0.0089893 | -0.21057 | 0.09613 | -0.48065 | -0.009155 | 0 | 0 | 0.050354 | 0.18768 | 0.27924 | -0.33875 | 122.3511 | -0.086975 | 122.6212 | 122.8226 | -0.1831 | 122.493 | 0.096131 | 0.27008 | 122.8821 | 123.0194 | 122.8317 | 122.9279 | 122.6212 | 123.111 | 122.8317 | 122.493 | 122.9279 | 122.6212 | 122.8317 | 122.8317 | 123.111 | -0.66376 | -0.52185
3608.1406 | 123.2071 | -122.818 | 0.17853 | 0.069504 | 0.0096387 | -0.0058832 | 0.038533 | -0.018965 | -0.011476 | 0.0081347 | -0.1831 | 0.045776 | -0.43945 | 0.041199 | 0.073242 | 0.10071 | -0.10529 | 0.23804 | 0.25177 | -0.28381 | 122.3785 | -0.13275 | 122.6349 | 122.8592 | -0.10529 | 122.5342 | 0.073242 | 0.25635 | 122.7127 | 123.056 | 122.8912 | 122.8638 | 122.6349 | 123.0698 | 122.9187 | 122.5342 | 122.8638 | 122.6349 | 122.9187 | 122.8912 | 123.0698 | -0.61798 | -0.46234
3609.8438 | 123.1201 | -122.8455 | 0.19684 | 0.13054 | 0.011775 | -0.0056696 | 0.046437 | -0.016616 | -0.01468 | 0.010485 | -0.20142 | 0.10071 | -0.46692 | -0.022888 | -0.027466 | -0.013733 | -0.004578 | 0.12817 | 0.27008 | -0.32959 | 122.3785 | -0.09613 | 122.644 | 122.8226 | -0.2243 | 122.5159 | 0.073243 | 0.2655 | 122.8409 | 122.9736 | 122.818 | 122.9462 | 122.644 | 123.1155 | 122.8317 | 122.5159 | 122.9462 | 122.644 | 122.8317 | 122.818 | 123.1155 | -0.66376 | -0.52643
3611.5938 | 123.2071 | -122.8134 | 0.17853 | -0.27382 | 0.010066 | -0.0063104 | 0.045583 | -0.018538 | -0.012544 | 0.0098437 | -0.21515 | 0.10529 | -0.48065 | -0.018311 | -0.004578 | -0.004578 | 0.050354 | 0.17395 | 0.28839 | -0.32959 | 122.3328 | -0.073242 | 122.5983 | 122.7951 | -0.18311 | 122.4838 | 0.10986 | 0.2655 | 122.8638 | 122.9874 | 122.8088 | 122.9187 | 122.5983 | 123.1018 | 122.8088 | 122.4838 | 122.9187 | 122.5983 | 122.8088 | 122.8088 | 123.1018 | -0.65918 | -0.50812
3613.3594 | 123.1659 | -122.8088 | 0.1831 | 0.069504 | 0.012629 | -0.0086602 | 0.039815 | -0.019179 | -0.011049 | 0.0094165 | -0.16022 | 0.054932 | -0.43488 | 0.027466 | 0.082397 | 0.091553 | -0.11902 | 0.24719 | 0.24719 | -0.3067 | 122.374 | -0.12817 | 122.6486 | 122.8363 | -0.10071 | 122.5021 | 0.064087 | 0.27466 | 122.6898 | 123.056 | 122.8912 | 122.8638 | 122.6486 | 123.056 | 122.9004 | 122.5021 | 122.8638 | 122.6486 | 122.9004 | 122.8912 | 123.056 | -0.61798 | -0.48981
3615.125 | 123.111 | -122.8455 | 0.20142 | 0.10765 | 0.011989 | -0.0067376 | 0.050924 | -0.016829 | -0.013612 | 0.010485 | -0.19684 | 0.091553 | -0.48065 | -0.013733 | -0.018311 | 0.004578 | -0.018311 | 0.11444 | 0.27466 | -0.31128 | 122.3648 | -0.10986 | 122.6486 | 122.8317 | -0.21973 | 122.5342 | 0.073242 | 0.28381 | 122.8271 | 122.9599 | 122.8271 | 122.937 | 122.6486 | 123.1201 | 122.85 | 122.5342 | 122.937 | 122.6486 | 122.85 | 122.8271 | 123.1201 | -0.68207 | -0.5127
3616.8281 | 123.1705 | -122.8271 | 0.1831 | -0.12886 | 0.012202 | -0.0075922 | 0.039174 | -0.018965 | -0.0097669 | 0.0096301 | -0.15564 | 0.086975 | -0.46234 | 0.07782 | 0.10986 | 0.13275 | -0.11444 | 0.29297 | 0.23804 | -0.28839 | 122.3648 | -0.09613 | 122.6715 | 122.905 | -0.073242 | 122.5388 | 0.054932 | 0.3067 | 122.7127 | 123.1201 | 122.937 | 122.9141 | 122.6715 | 123.0652 | 122.9599 | 122.5388 | 122.9141 | 122.6715 | 122.9599 | 122.937 | 123.0652 | -0.64545 | -0.4715
3618.5938 | 123.1613 | -122.8088 | 0.18768 | -0.083084 | 0.011775 | -0.0093012 | 0.040029 | -0.018752 | -0.010408 | 0.011126 | -0.12817 | 0.064087 | -0.43488 | 0.10071 | 0.11444 | 0.14648 | -0.15106 | 0.32044 | 0.23804 | -0.3067 | 122.374 | -0.1236 | 122.6807 | 122.9095 | -0.073242 | 122.5021 | 0.050354 | 0.3067 | 122.6578 | 123.1293 | 122.9233 | 122.8729 | 122.6807 | 123.0469 | 122.9553 | 122.5021 | 122.8729 | 122.6807 | 122.9553 | 122.9233 | 123.0469 | -0.62256 | -0.49438
3620.3594 | 123.111 | -122.8455 | 0.19226 | 0.046615 | 0.01028 | -0.0073786 | 0.04836 | -0.018111 | -0.013399 | 0.010057 | -0.20142 | 0.10071 | -0.48981 | -0.022888 | -0.041199 | -0.013733 | 0.004578 | 0.12817 | 0.27924 | -0.32959 | 122.3557 | -0.091553 | 122.644 | 122.8226 | -0.23346 | 122.5159 | 0.086975 | 0.28839 | 122.85 | 122.9736 | 122.8043 | 122.9462 | 122.644 | 123.1247 | 122.8317 | 122.5159 | 122.9462 | 122.644 | 122.8317 | 122.8043 | 123.1247 | -0.68207 | -0.52185
3622.1094 | 123.0698 | -122.8638 | 0.20599 | -0.10597 | 0.010707 | -0.009942 | 0.046865 | -0.017043 | -0.015535 | 0.010485 | -0.13733 | 0.082397 | -0.48065 | 0.045776 | 0.050354 | 0.059509 | -0.041199 | 0.22888 | 0.27008 | -0.3067 | 122.3831 | -0.1236 | 122.7264 | 122.9095 | -0.15564 | 122.5571 | 0.064087 | 0.34332 | 122.8226 | 123.0927 | 122.9141 | 122.9462 | 122.7264 | 123.1339 | 122.9233 | 122.5571 | 122.9462 | 122.7264 | 122.9233 | 122.9141 | 123.1339 | -0.68665 | -0.5127
3623.8125 | 123.1888 | -122.8043 | 0.1831 | -0.19753 | 0.012202 | -0.0093012 | 0.042165 | -0.016402 | -0.014467 | 0.0089893 | -0.21057 | 0.10071 | -0.49439 | -0.009155 | -0.018311 | 0.018311 | 0.036621 | 0.16937 | 0.28381 | -0.32959 | 122.3099 | -0.082397 | 122.5937 | 122.7951 | -0.20142 | 122.4747 | 0.10071 | 0.28381 | 122.8409 | 122.9736 | 122.7859 | 122.905 | 122.5937 | 123.0881 | 122.8226 | 122.4747 | 122.905 | 122.5937 | 122.8226 | 122.7859 | 123.0881 | -0.67749 | -0.5127
3625.5625 | 123.1796 | -122.7859 | 0.17395 | 0.00083945 | 0.0096387 | -0.010369 | 0.038961 | -0.020247 | -0.0082715 | 0.0072803 | -0.16479 | 0.068665 | -0.43945 | 0.041199 | 0.082397 | 0.09613 | -0.10986 | 0.23804 | 0.25177 | -0.31586 | 122.3465 | -0.10528 | 122.6212 | 122.8271 | -0.091553 | 122.4701 | 0.07782 | 0.27466 | 122.6761 | 123.024 | 122.8683 | 122.8546 | 122.6212 | 123.0377 | 122.8821 | 122.4701 | 122.8546 | 122.6212 | 122.8821 | 122.8683 | 123.0377 | -0.6134 | -0.48981
3627.3125 | 123.111 | -122.8546 | 0.20142 | 0.1458 | 0.010066 | -0.0041742 | 0.047933 | -0.017256 | -0.012544 | 0.011126 | -0.19684 | 0.086975 | -0.48981 | -0.022888 | -0.013733 | 0.018311 | -0.050354 | 0.14191 | 0.28839 | -0.31128 | 122.3648 | -0.11444 | 122.6578 | 122.8317 | -0.21515 | 122.5433 | 0.086975 | 0.29297 | 122.8043 | 122.9965 | 122.8409 | 122.9416 | 122.6578 | 123.143 | 122.8729 | 122.5433 | 122.9416 | 122.6578 | 122.8729 | 122.8409 | 123.143 | -0.69122 | -0.5127
3629.0781 | 123.1842 | -122.818 | 0.17395 | -0.01442 | 0.011775 | -0.008233 | 0.041097 | -0.019393 | -0.0097669 | 0.0077075 | -0.16937 | 0.054932 | -0.43945 | 0.036621 | 0.064087 | 0.10529 | -0.09613 | 0.24261 | 0.24261 | -0.29297 | 122.3785 | -0.11902 | 122.6486 | 122.8546 | -0.10986 | 122.525 | 0.068665 | 0.27008 | 122.7219 | 123.0606 | 122.8821 | 122.8729 | 122.6486 | 123.0606 | 122.9233 | 122.525 | 122.8729 | 122.6486 | 122.9233 | 122.8821 | 123.0606 | -0.6134 | -0.46692
3630.7812 | 123.1888 | -122.8409 | 0.17395 | -0.22041 | 0.011989 | -0.0018244 | 0.045583 | -0.01747 | -0.010835 | 0.0096301 | -0.19226 | 0.091553 | -0.48065 | -0.004578 | 0 | -0.004578 | 0.041199 | 0.19226 | 0.27466 | -0.31586 | 122.3602 | -0.082397 | 122.6486 | 122.8363 | -0.17395 | 122.525 | 0.10071 | 0.28839 | 122.8821 | 123.0331 | 122.8409 | 122.9324 | 122.6486 | 123.1155 | 122.8363 | 122.525 | 122.9324 | 122.6486 | 122.8363 | 122.8409 | 123.1155 | -0.6546 | -0.48981
3632.5469 | 123.0789 | -122.8363 | 0.21057 | 0.16869 | 0.011348 | -0.0056696 | 0.044728 | -0.015334 | -0.013185 | 0.0098437 | -0.09613 | 0.027466 | -0.42572 | 0.086975 | 0.09613 | 0.13275 | -0.20599 | 0.28839 | 0.22888 | -0.27008 | 122.4106 | -0.18311 | 122.7402 | 122.9233 | -0.11444 | 122.5662 | 0.018311 | 0.32959 | 122.6303 | 123.1247 | 122.9324 | 122.8638 | 122.7402 | 123.0652 | 122.9691 | 122.5662 | 122.8638 | 122.7402 | 122.9691 | 122.9324 | 123.0652 | -0.63629 | -0.48065
3634.25 | 123.1842 | -122.8043 | 0.19684 | -0.28145 | 0.011561 | -0.0095148 | 0.043233 | -0.017897 | -0.012544 | 0.0083483 | -0.12817 | 0.054932 | -0.44861 | 0.050354 | 0.054932 | 0.07782 | -0.022888 | 0.25635 | 0.27924 | -0.31128 | 122.3557 | -0.14191 | 122.6761 | 122.8546 | -0.14191 | 122.493 | 0.082398 | 0.32043 | 122.7814 | 123.0606 | 122.8592 | 122.8592 | 122.6761 | 123.0835 | 122.8821 | 122.493 | 122.8592 | 122.6761 | 122.8821 | 122.8592 | 123.0835 | -0.64545 | -0.50812
3636.0156 | 123.111 | -122.8409 | 0.18768 | 0.13817 | 0.010066 | -0.0084466 | 0.049001 | -0.01747 | -0.013399 | 0.012194 | -0.20142 | 0.082397 | -0.48981 | -0.013733 | -0.032043 | -0.009155 | -0.018311 | 0.1236 | 0.28839 | -0.32959 | 122.3511 | -0.10529 | 122.6395 | 122.8271 | -0.21973 | 122.5113 | 0.10071 | 0.28839 | 122.8226 | 122.9645 | 122.8088 | 122.9233 | 122.6395 | 123.1293 | 122.8317 | 122.5113 | 122.9233 | 122.6395 | 122.8317 | 122.8088 | 123.1293 | -0.67749 | -0.51727
3637.7188 | 123.1842 | -122.818 | 0.17395 | -0.26619 | 0.01028 | -0.010156 | 0.041097 | -0.01982 | -0.011262 | 0.010057 | -0.14648 | 0.064087 | -0.45319 | 0.041199 | 0.059509 | 0.091553 | -0.013733 | 0.25635 | 0.25177 | -0.3067 | 122.3648 | -0.10986 | 122.6715 | 122.8592 | -0.11444 | 122.5113 | 0.07782 | 0.3067 | 122.8043 | 123.0743 | 122.8775 | 122.8821 | 122.6715 | 123.0698 | 122.9095 | 122.5113 | 122.8821 | 122.6715 | 122.9095 | 122.8775 | 123.0698 | -0.62714 | -0.48065
3639.4844 | 123.1842 | -122.8043 | 0.16937 | 0.038986 | 0.010066 | -0.013787 | 0.039388 | -0.017897 | -0.010194 | 0.0081347 | -0.15564 | 0.054932 | -0.43945 | 0.018311 | 0.086975 | 0.09613 | -0.10071 | 0.2655 | 0.23804 | -0.30212 | 122.3648 | -0.11444 | 122.6486 | 122.8226 | -0.082398 | 122.5021 | 0.068664 | 0.28381 | 122.7036 | 123.0698 | 122.8912 | 122.8592 | 122.6486 | 123.0423 | 122.9004 | 122.5021 | 122.8592 | 122.6486 | 122.9004 | 122.8912 | 123.0423 | -0.60883 | -0.4715
3641.1719 | 123.1979 | -122.818 | 0.16479 | -0.22804 | 0.0098523 | -0.0035332 | 0.044515 | -0.021529 | -0.010408 | 0.0092029 | -0.1831 | 0.11444 | -0.46234 | -0.004578 | 0.009155 | 0.018311 | 0.032043 | 0.18768 | 0.27008 | -0.32959 | 122.3557 | -0.050354 | 122.6349 | 122.8134 | -0.15564 | 122.4884 | 0.10529 | 0.27924 | 122.85 | 123.0057 | 122.8271 | 122.9324 | 122.6349 | 123.0881 | 122.8363 | 122.4884 | 122.9324 | 122.6349 | 122.8363 | 122.8271 | 123.0881 | -0.62714 | -0.49438
3642.9219 | 123.1934 | -122.7997 | 0.17853 | -0.22804 | 0.0094251 | -0.0073786 | 0.044515 | -0.01982 | -0.011476 | 0.0085619 | -0.20142 | 0.09613 | -0.50354 | -0.018311 | -0.013733 | 0.004578 | 0.050354 | 0.1831 | 0.28839 | -0.3479 | 122.2961 | -0.082398 | 122.5983 | 122.7814 | -0.19226 | 122.4518 | 0.10986 | 0.30212 | 122.85 | 122.9828 | 122.7859 | 122.8958 | 122.5983 | 123.0881 | 122.8043 | 122.4518 | 122.8958 | 122.5983 | 122.8043 | 122.7859 | 123.0881 | -0.68207 | -0.52643
3644.625 | 123.1888 | -122.7997 | 0.18768 | -0.022049 | 0.010066 | -0.0067376 | 0.041524 | -0.01982 | -0.01233 | 0.010912 | -0.17395 | 0.082397 | -0.44861 | 0.059509 | 0.064087 | 0.10986 | -0.10986 | 0.27924 | 0.24261 | -0.29755 | 122.3511 | -0.10529 | 122.6257 | 122.8592 | -0.1236 | 122.5021 | 0.054932 | 0.27466 | 122.6898 | 123.0789 | 122.8638 | 122.8821 | 122.6257 | 123.0423 | 122.9095 | 122.5021 | 122.8821 | 122.6257 | 122.9095 | 122.8638 | 123.0423 | -0.63629 | -0.48523
3646.3906 | 123.1522 | -122.7997 | 0.19226 | -0.15175 | 0.0092115 | -0.0067376 | 0.040029 | -0.021743 | -0.0095531 | 0.0092029 | -0.10071 | 0.059509 | -0.44861 | 0.10071 | 0.12817 | 0.14648 | -0.13733 | 0.32959 | 0.21973 | -0.27924 | 122.3511 | -0.13275 | 122.699 | 122.9004 | -0.064087 | 122.5204 | 0.027466 | 0.3479 | 122.6624 | 123.1293 | 122.9279 | 122.8592 | 122.699 | 123.0194 | 122.9462 | 122.5204 | 122.8592 | 122.699 | 122.9462 | 122.9279 | 123.0194 | -0.64087 | -0.4715
3648.1562 | 123.111 | -122.8683 | 0.20599 | 0.11528 | 0.010921 | -0.006524 | 0.048146 | -0.016402 | -0.012544 | 0.011126 | -0.19684 | 0.09613 | -0.47607 | -0.013733 | -0.009155 | 0.022888 | -0.041199 | 0.16022 | 0.2655 | -0.34332 | 122.3923 | -0.10986 | 122.6715 | 122.8546 | -0.21515 | 122.525 | 0.059509 | 0.27924 | 122.8271 | 123.0286 | 122.8592 | 122.9645 | 122.6715 | 123.1338 | 122.8912 | 122.525 | 122.9645 | 122.6715 | 122.8912 | 122.8592 | 123.1338 | -0.68207 | -0.54932
3649.8594 | 123.1842 | -122.8134 | 0.17395 | -0.044937 | 0.011134 | -0.0058832 | 0.039174 | -0.017897 | -0.011903 | 0.0096301 | -0.14191 | 0.064087 | -0.44861 | 0.059509 | 0.086975 | 0.1236 | -0.13275 | 0.28839 | 0.23804 | -0.3067 | 122.3648 | -0.10986 | 122.6715 | 122.8729 | -0.086975 | 122.5067 | 0.064087 | 0.3067 | 122.6807 | 123.1018 | 122.9004 | 122.8775 | 122.6715 | 123.0515 | 122.937 | 122.5067 | 122.8775 | 122.6715 | 122.937 | 122.9004 | 123.0515 | -0.62256 | -0.48065
3651.625 | 123.0881 | -122.8546 | 0.1831 | 0.13054 | 0.011348 | -0.0071648 | 0.04601 | -0.019393 | -0.010408 | 0.0089893 | -0.10986 | 0.032043 | -0.44403 | 0.068665 | 0.082397 | 0.11902 | -0.16937 | 0.27008 | 0.23804 | -0.29755 | 122.4106 | -0.15106 | 122.7448 | 122.9233 | -0.10071 | 122.5571 | 0.054932 | 0.33417 | 122.6852 | 123.1247 | 122.937 | 122.8867 | 122.7448 | 123.0927 | 122.9736 | 122.5571 | 122.8867 | 122.7448 | 122.9736 | 122.937 | 123.0927 | -0.62714 | -0.48065
3653.3906 | 123.1934 | -122.8088 | 0.1831 | -0.1899 | 0.011348 | -0.0046014 | 0.046651 | -0.015334 | -0.013399 | 0.0096301 | -0.19684 | 0.10986 | -0.48065 | 0.009155 | -0.004578 | -0.004578 | 0.032043 | 0.21057 | 0.28381 | -0.34332 | 122.3282 | -0.073242 | 122.612 | 122.818 | -0.18768 | 122.4655 | 0.10071 | 0.28381 | 122.8409 | 123.0194 | 122.8043 | 122.9187 | 122.612 | 123.0927 | 122.8043 | 122.4655 | 122.9187 | 122.612 | 122.8043 | 122.8043 | 123.0927 | -0.66376 | -0.52643
3655.1406 | 123.0606 | -122.8638 | 0.21973 | -0.1136 | 0.0094251 | -0.0060968 | 0.046437 | -0.017897 | -0.011476 | 0.0089893 | -0.16022 | 0.059509 | -0.4715 | 0.050354 | 0.050354 | 0.064087 | -0.027466 | 0.21057 | 0.2655 | -0.3067 | 122.3923 | -0.16022 | 122.7036 | 122.9141 | -0.16937 | 122.5571 | 0.045776 | 0.31128 | 122.8363 | 123.0743 | 122.9141 | 122.9233 | 122.7036 | 123.1293 | 122.9279 | 122.5571 | 122.9233 | 122.7036 | 122.9279 | 122.9141 | 123.1293 | -0.69122 | -0.52643
3656.8438 | 123.0743 | -122.8638 | 0.20599 | 0.19157 | 0.011775 | -0.0063104 | 0.043019 | -0.016829 | -0.014253 | 0.0083483 | -0.086975 | 0.041199 | -0.43488 | 0.091553 | 0.10529 | 0.13733 | -0.20142 | 0.28839 | 0.24261 | -0.29755 | 122.4289 | -0.1648 | 122.7768 | 122.9553 | -0.10071 | 122.5662 | 0.036621 | 0.3479 | 122.6624 | 123.1522 | 122.9691 | 122.905 | 122.7768 | 123.1064 | 123.0011 | 122.5662 | 122.905 | 122.7768 | 123.0011 | 122.9691 | 123.1064 | -0.64087 | -0.50354
3658.6094 | 123.1155 | -122.8409 | 0.20142 | 0.038986 | 0.01028 | -0.01101 | 0.047719 | -0.01512 | -0.01233 | 0.010912 | -0.21515 | 0.091553 | -0.50354 | -0.036621 | -0.018311 | -0.009155 | 0.022888 | 0.1236 | 0.25635 | -0.31128 | 122.3373 | -0.10986 | 122.6257 | 122.8043 | -0.21973 | 122.5296 | 0.054932 | 0.28839 | 122.8638 | 122.9645 | 122.8226 | 122.9324 | 122.6257 | 123.0972 | 122.8317 | 122.5296 | 122.9324 | 122.6257 | 122.8317 | 122.8226 | 123.0972 | -0.70496 | -0.5127
3660.375 | 123.1842 | -122.8134 | 0.1831 | -0.18227 | 0.011134 | -0.0090874 | 0.044301 | -0.015761 | -0.01169 | 0.0094165 | -0.19684 | 0.10071 | -0.47607 | 0.004578 | 0.018311 | 0.004578 | 0.036621 | 0.19226 | 0.28839 | -0.34332 | 122.3373 | -0.082397 | 122.6166 | 122.818 | -0.16479 | 122.4701 | 0.10529 | 0.27924 | 122.85 | 123.0057 | 122.8317 | 122.9141 | 122.6166 | 123.1018 | 122.818 | 122.4701 | 122.9141 | 122.6166 | 122.818 | 122.8317 | 123.1018 | -0.65918 | -0.52643
3662.125 | 123.0743 | -122.8729 | 0.19684 | 0.15343 | 0.010921 | -0.002038 | 0.042165 | -0.018965 | -0.010194 | 0.0087757 | -0.10986 | 0.050354 | -0.43945 | 0.082397 | 0.10986 | 0.16022 | -0.17395 | 0.28381 | 0.23346 | -0.28839 | 122.4335 | -0.14648 | 122.7631 | 122.9553 | -0.086975 | 122.5845 | 0.036621 | 0.32959 | 122.699 | 123.1567 | 122.9828 | 122.9233 | 122.7631 | 123.1064 | 123.0331 | 122.5845 | 122.9233 | 122.7631 | 123.0331 | 122.9828 | 123.1064 | -0.63629 | -0.48523
3663.8281 | 123.1064 | -122.8455 | 0.21057 | 0.1992 | 0.011561 | -0.0054558 | 0.04601 | -0.017897 | -0.012544 | 0.010698 | -0.20599 | 0.082397 | -0.48981 | 0.004578 | 0.013733 | 0.036621 | -0.086975 | 0.18768 | 0.24261 | -0.32959 | 122.3557 | -0.12817 | 122.6395 | 122.85 | -0.19684 | 122.5159 | 0.032044 | 0.28381 | 122.7585 | 123.0331 | 122.8592 | 122.9279 | 122.6395 | 123.0881 | 122.8821 | 122.5159 | 122.9279 | 122.6395 | 122.8821 | 122.8592 | 123.0881 | -0.70038 | -0.54016
3665.5781 | 123.2162 | -122.818 | 0.1831 | -0.27382 | 0.010707 | -0.0073786 | 0.041524 | -0.021315 | -0.01169 | 0.0085619 | -0.22888 | 0.09613 | -0.48981 | -0.032043 | 0.004578 | 0 | 0.068665 | 0.17395 | 0.29297 | -0.34332 | 122.3282 | -0.086975 | 122.5891 | 122.7859 | -0.17853 | 122.4747 | 0.10986 | 0.26092 | 122.8867 | 122.9919 | 122.8226 | 122.9141 | 122.5891 | 123.111 | 122.818 | 122.4747 | 122.9141 | 122.5891 | 122.818 | 122.8226 | 123.111 | -0.67291 | -0.52643
3667.3438 | 123.0789 | -122.8546 | 0.19226 | -0.037308 | 0.011561 | -0.008233 | 0.047078 | -0.017043 | -0.01169 | 0.0092029 | -0.15564 | 0.068665 | -0.47607 | 0.018311 | 0.018311 | 0.045776 | -0.018311 | 0.19226 | 0.27924 | -0.32044 | 122.3785 | -0.1236 | 122.699 | 122.8729 | -0.17395 | 122.5342 | 0.086975 | 0.32043 | 122.8363 | 123.0469 | 122.8729 | 122.9233 | 122.699 | 123.1338 | 122.9004 | 122.5342 | 122.9233 | 122.699 | 122.9004 | 122.8729 | 123.1338 | -0.66834 | -0.5127
3669.0938 | 123.0743 | -122.85 | 0.20599 | 0.19157 | 0.010493 | -0.0071648 | 0.042806 | -0.018752 | -0.01233 | 0.0092029 | -0.11444 | 0.059509 | -0.43488 | 0.073242 | 0.09613 | 0.15106 | -0.21057 | 0.27466 | 0.21973 | -0.28839 | 122.4152 | -0.14649 | 122.7356 | 122.9233 | -0.10986 | 122.5616 | 0.013733 | 0.32043 | 122.6395 | 123.1247 | 122.9462 | 122.9095 | 122.7356 | 123.0698 | 123.0011 | 122.5616 | 122.9095 | 122.7356 | 123.0011 | 122.9462 | 123.0698 | -0.64087 | -0.49439
3670.7969 | 123.1796 | -122.818 | 0.20142 | -0.029679 | 0.011348 | -0.0060968 | 0.036611 | -0.020888 | -0.0089123 | 0.0087757 | -0.16479 | 0.064087 | -0.42572 | 0.068665 | 0.10986 | 0.12817 | -0.11444 | 0.29297 | 0.22888 | -0.29297 | 122.3923 | -0.13733 | 122.6532 | 122.8867 | -0.091553 | 122.525 | 0.027466 | 0.26092 | 122.7036 | 123.111 | 122.9279 | 122.8821 | 122.6532 | 123.0469 | 122.9462 | 122.525 | 122.8821 | 122.6532 | 122.9462 | 122.9279 | 123.0469 | -0.62714 | -0.49438
3672.5625 | 123.175 | -122.7905 | 0.17395 | 0.077133 | 0.0094251 | -0.0071648 | 0.041097 | -0.018965 | -0.010835 | 0.0081347 | -0.15106 | 0.045776 | -0.44403 | 0.022888 | 0.054932 | 0.082397 | -0.11444 | 0.24261 | 0.24719 | -0.32501 | 122.3465 | -0.12817 | 122.6395 | 122.8134 | -0.11902 | 122.4655 | 0.073242 | 0.29297 | 122.6761 | 123.0331 | 122.8455 | 122.8363 | 122.6395 | 123.0377 | 122.8729 | 122.4655 | 122.8363 | 122.6395 | 122.8729 | 122.8455 | 123.0377 | -0.61798 | -0.49896
3674.3281 | 123.1796 | -122.8043 | 0.1831 | 0.038986 | 0.011134 | -0.0071648 | 0.04131 | -0.020888 | -0.012117 | 0.0079211 | -0.16479 | 0.064087 | -0.44403 | 0.036621 | 0.059509 | 0.09613 | -0.11902 | 0.24719 | 0.2243 | -0.27924 | 122.3602 | -0.11902 | 122.6395 | 122.8409 | -0.1236 | 122.525 | 0.041199 | 0.27924 | 122.6852 | 123.0515 | 122.8638 | 122.8683 | 122.6395 | 123.0286 | 122.9004 | 122.525 | 122.8683 | 122.6395 | 122.9004 | 122.8638 | 123.0286 | -0.62714 | -0.46234
3676.0938 | 123.1613 | -122.7951 | 0.1831 | -0.067826 | 0.013484 | -0.012719 | 0.041738 | -0.018325 | -0.010621 | 0.0094165 | -0.15106 | 0.050354 | -0.45319 | 0.086975 | 0.11444 | 0.14191 | -0.15106 | 0.33875 | 0.22888 | -0.31128 | 122.3419 | -0.13275 | 122.644 | 122.8821 | -0.068664 | 122.4838 | 0.045777 | 0.30212 | 122.644 | 123.1339 | 122.9095 | 122.8455 | 122.644 | 123.024 | 122.937 | 122.4838 | 122.8455 | 122.644 | 122.937 | 122.9095 | 123.024 | -0.63629 | -0.49438
3677.7969 | 123.1293 | -122.8317 | 0.20142 | -0.14412 | 0.010921 | -0.009942 | 0.047933 | -0.018965 | -0.015107 | 0.0070667 | -0.17853 | 0.091553 | -0.48981 | 0.045776 | 0.018311 | 0.032043 | -0.009155 | 0.21057 | 0.25635 | -0.32959 | 122.3419 | -0.10986 | 122.6532 | 122.8775 | -0.18311 | 122.5021 | 0.054932 | 0.31128 | 122.8226 | 123.0423 | 122.85 | 122.9233 | 122.6532 | 123.0881 | 122.8638 | 122.5021 | 122.9233 | 122.6532 | 122.8638 | 122.85 | 123.0881 | -0.69122 | -0.53101
3679.5625 | 123.0743 | -122.8638 | 0.20599 | 0.20683 | 0.011775 | -0.0095148 | 0.044942 | -0.016402 | -0.012117 | 0.0092029 | -0.09613 | 0.032043 | -0.43945 | 0.10071 | 0.09613 | 0.14648 | -0.19226 | 0.29297 | 0.23346 | -0.27466 | 122.4243 | -0.17395 | 122.7676 | 122.9645 | -0.10986 | 122.5891 | 0.027465 | 0.34332 | 122.6715 | 123.1567 | 122.9599 | 122.8958 | 122.7676 | 123.0972 | 123.0103 | 122.5891 | 122.8958 | 122.7676 | 123.0103 | 122.9599 | 123.0972 | -0.64545 | -0.48065
3681.2656 | 123.2117 | -122.8363 | 0.16022 | -0.25093 | 0.010921 | -0.0090874 | 0.041951 | -0.018538 | -0.011476 | 0.0094165 | -0.16937 | 0.073242 | -0.46692 | 0.013733 | 0.036621 | 0.045776 | 0.018311 | 0.21973 | 0.27008 | -0.33417 | 122.3694 | -0.086975 | 122.6669 | 122.85 | -0.1236 | 122.5021 | 0.10986 | 0.29755 | 122.8546 | 123.056 | 122.8729 | 122.9095 | 122.6669 | 123.1064 | 122.8821 | 122.5021 | 122.9095 | 122.6669 | 122.8821 | 122.8729 | 123.1064 | -0.62714 | -0.49438
3683.0469 | 123.1567 | -122.8226 | 0.18768 | 0.038986 | 0.01028 | -0.009942 | 0.040883 | -0.019606 | -0.012544 | 0.0098437 | -0.091553 | 0.050354 | -0.4303 | 0.10529 | 0.11902 | 0.15564 | -0.15564 | 0.34332 | 0.24261 | -0.29755 | 122.3923 | -0.13733 | 122.731 | 122.9279 | -0.068664 | 122.525 | 0.054932 | 0.33875 | 122.6669 | 123.1659 | 122.9416 | 122.8729 | 122.731 | 123.0652 | 122.9782 | 122.525 | 122.8729 | 122.731 | 122.9782 | 122.9416 | 123.0652 | -0.61798 | -0.48523
3684.75 | 123.1796 | -122.8271 | 0.16937 | -0.27382 | 0.010066 | -0.006524 | 0.042806 | -0.021529 | -0.012544 | 0.0098437 | -0.1236 | 0.059509 | -0.44403 | 0.068665 | 0.068665 | 0.091553 | -0.045776 | 0.27466 | 0.25177 | -0.32501 | 122.3831 | -0.10986 | 122.7036 | 122.8958 | -0.10071 | 122.5021 | 0.082397 | 0.32044 | 122.7814 | 123.1018 | 122.8958 | 122.8867 | 122.7036 | 123.0789 | 122.9187 | 122.5021 | 122.8867 | 122.7036 | 122.9187 | 122.8958 | 123.0789 | -0.6134 | -0.49439
3686.5156 | 123.0743 | -122.8546 | 0.20599 | -0.037308 | 0.0085705 | -0.004815 | 0.04836 | -0.016616 | -0.014467 | 0.010485 | -0.14191 | 0.073242 | -0.47607 | 0.036621 | 0.027466 | 0.032043 | -0.009155 | 0.1831 | 0.27008 | -0.33875 | 122.3785 | -0.13275 | 122.7127 | 122.8912 | -0.17853 | 122.5159 | 0.064087 | 0.33417 | 122.8455 | 123.0377 | 122.8821 | 122.9279 | 122.7127 | 123.1247 | 122.8867 | 122.5159 | 122.9279 | 122.7127 | 122.8867 | 122.8821 | 123.1247 | -0.68207 | -0.54474
3688.2188 | 123.1476 | -122.8271 | 0.17853 | -0.2433 | 0.011989 | -0.0058832 | 0.040883 | -0.018538 | -0.01169 | 0.010271 | -0.10986 | 0.036621 | -0.44403 | 0.09613 | 0.11444 | 0.13733 | -0.10986 | 0.32044 | 0.25177 | -0.29297 | 122.3831 | -0.14191 | 122.7173 | 122.9233 | -0.064087 | 122.5342 | 0.073242 | 0.33417 | 122.7173 | 123.1476 | 122.9416 | 122.8638 | 122.7173 | 123.0789 | 122.9645 | 122.5342 | 122.8638 | 122.7173 | 122.9645 | 122.9416 | 123.0789 | -0.62256 | -0.4715
3689.9844 | 123.1567 | -122.8226 | 0.18768 | -0.15938 | 0.012202 | -0.0090874 | 0.040242 | -0.020247 | -0.012117 | 0.0057849 | -0.086975 | 0.059509 | -0.46234 | 0.10529 | 0.12817 | 0.17853 | -0.1236 | 0.3479 | 0.22888 | -0.29297 | 122.3602 | -0.12817 | 122.7356 | 122.9279 | -0.059509 | 122.5296 | 0.041199 | 0.37537 | 122.699 | 123.1705 | 122.9507 | 122.8821 | 122.7356 | 123.0515 | 123.0011 | 122.5296 | 122.8821 | 122.7356 | 123.0011 | 122.9507 | 123.0515 | -0.65002 | -0.48065
3691.6719 | 123.1155 | -122.8363 | 0.20142 | 0.031357 | 0.0098523 | -0.0058832 | 0.049428 | -0.01747 | -0.012544 | 0.010912 | -0.1831 | 0.086975 | -0.48981 | 0.004578 | -0.013733 | -0.004578 | 0.004578 | 0.15106 | 0.2655 | -0.32044 | 122.3465 | -0.11444 | 122.6532 | 122.8409 | -0.21515 | 122.5159 | 0.064087 | 0.3067 | 122.8409 | 122.9874 | 122.8226 | 122.9233 | 122.6532 | 123.1018 | 122.8317 | 122.5159 | 122.9233 | 122.6532 | 122.8317 | 122.8226 | 123.1018 | -0.69122 | -0.52185
3693.4219 | 123.1979 | -122.8226 | 0.17853 | -0.26619 | 0.011989 | -0.0052422 | 0.043019 | -0.019606 | -0.010835 | 0.010485 | -0.23346 | 0.086975 | -0.49896 | -0.013733 | 0.004578 | -0.004578 | 0.054932 | 0.1831 | 0.28381 | -0.32959 | 122.3236 | -0.091553 | 122.5891 | 122.8088 | -0.17395 | 122.493 | 0.10528 | 0.2655 | 122.8775 | 123.0057 | 122.8271 | 122.9095 | 122.5891 | 123.1064 | 122.818 | 122.493 | 122.9095 | 122.5891 | 122.818 | 122.8271 | 123.1064 | -0.67749 | -0.50812
3695.1719 | 123.0972 | -122.8134 | 0.21515 | 0.016098 | 0.01028 | -0.0075922 | 0.047078 | -0.015761 | -0.014894 | 0.0098437 | -0.20599 | 0.086975 | -0.48981 | -0.045776 | -0.018311 | -0.018311 | 0.018311 | 0.1236 | 0.28381 | -0.32044 | 122.3236 | -0.12817 | 122.6074 | 122.7676 | -0.23346 | 122.493 | 0.068664 | 0.28381 | 122.8317 | 122.937 | 122.7951 | 122.9004 | 122.6074 | 123.0972 | 122.7951 | 122.493 | 122.9004 | 122.6074 | 122.7951 | 122.7951 | 123.0972 | -0.70496 | -0.53558
3696.875 | 123.0652 | -122.85 | 0.21057 | 0.21446 | 0.012202 | -0.0071648 | 0.042379 | -0.016829 | -0.011903 | 0.011126 | -0.10529 | 0.045776 | -0.45776 | 0.091553 | 0.10986 | 0.14648 | -0.18768 | 0.27924 | 0.22888 | -0.27008 | 122.3923 | -0.1648 | 122.7448 | 122.9416 | -0.10071 | 122.58 | 0.018311 | 0.35248 | 122.6624 | 123.1293 | 122.9599 | 122.8958 | 122.7448 | 123.0789 | 122.9965 | 122.58 | 122.8958 | 122.7448 | 122.9965 | 122.9599 | 123.0789 | -0.66834 | -0.48065
3698.6406 | 123.0789 | -122.85 | 0.20599 | 0.18394 | 0.014338 | -0.003106 | 0.046224 | -0.015334 | -0.012758 | 0.010912 | -0.18768 | 0.073242 | -0.49439 | 0.009155 | 0.004578 | 0.050354 | -0.10071 | 0.17395 | 0.25635 | -0.31128 | 122.3557 | -0.13275 | 122.6624 | 122.8592 | -0.20142 | 122.5388 | 0.050354 | 0.3067 | 122.7493 | 123.024 | 122.8546 | 122.9233 | 122.6624 | 123.1064 | 122.9004 | 122.5388 | 122.9233 | 122.6624 | 122.9004 | 122.8546 | 123.1064 | -0.70038 | -0.51727
3700.4062 | 123.1155 | -122.8455 | 0.20599 | 0.16106 | 0.010921 | -0.0080194 | 0.047506 | -0.01747 | -0.012544 | 0.0089893 | -0.21973 | 0.07782 | -0.48523 | -0.022888 | -0.027466 | 0.004578 | -0.018311 | 0.13275 | 0.26093 | -0.33417 | 122.3602 | -0.12817 | 122.6257 | 122.8226 | -0.23346 | 122.5113 | 0.054931 | 0.2655 | 122.8271 | 122.9782 | 122.818 | 122.9233 | 122.6257 | 123.1064 | 122.85 | 122.5113 | 122.9233 | 122.6257 | 122.85 | 122.818 | 123.1064 | -0.69122 | -0.54016
3702.1562 | 123.0652 | -122.8867 | 0.2243 | -0.044937 | 0.01028 | -0.0090874 | 0.046865 | -0.015548 | -0.013826 | 0.0085619 | -0.15564 | 0.086975 | -0.48065 | 0.013733 | 0.013733 | 0.032043 | -0.013733 | 0.19684 | 0.28381 | -0.31586 | 122.406 | -0.13733 | 122.731 | 122.9004 | -0.21057 | 122.5708 | 0.059509 | 0.32501 | 122.8729 | 123.0835 | 122.9004 | 122.9736 | 122.731 | 123.1705 | 122.9187 | 122.5708 | 122.9736 | 122.731 | 122.9187 | 122.9004 | 123.1705 | -0.70496 | -0.54016
3703.8438 | 123.0743 | -122.8271 | 0.19684 | 0.23735 | 0.0098523 | -0.0097284 | 0.04366 | -0.01747 | -0.014467 | 0.0085619 | -0.18768 | 0.073242 | -0.4715 | 0.027466 | 0.045776 | 0.086975 | -0.10529 | 0.2243 | 0.27008 | -0.30212 | 122.3557 | -0.1236 | 122.6395 | 122.8546 | -0.15106 | 122.525 | 0.073243 | 0.28381 | 122.7219 | 123.0515 | 122.8729 | 122.9004 | 122.6395 | 123.0972 | 122.9141 | 122.525 | 122.9004 | 122.6395 | 122.9141 | 122.8729 | 123.0972 | -0.66834 | -0.49896
3705.6094 | 123.1155 | -122.85 | 0.21515 | 0.061874 | 0.013484 | -0.0056696 | 0.046865 | -0.016616 | -0.012971 | 0.011339 | -0.23804 | 0.09613 | -0.47607 | -0.064087 | -0.032043 | -0.009155 | 0.009155 | 0.14191 | 0.2655 | -0.31128 | 122.374 | -0.11902 | 122.612 | 122.7859 | -0.24719 | 122.5388 | 0.050354 | 0.23804 | 122.8592 | 122.9919 | 122.818 | 122.9462 | 122.612 | 123.1155 | 122.8409 | 122.5388 | 122.9462 | 122.612 | 122.8409 | 122.818 | 123.1155 | -0.69122 | -0.52643
3707.3594 | 123.0835 | -122.8638 | 0.2243 | -0.044937 | 0.011775 | -0.0093012 | 0.045369 | -0.015334 | -0.013612 | 0.0092029 | -0.16479 | 0.068665 | -0.50354 | -0.004578 | 0.018311 | 0.045776 | -0.009155 | 0.17395 | 0.27008 | -0.3067 | 122.3602 | -0.15564 | 122.699 | 122.8592 | -0.20599 | 122.5571 | 0.045777 | 0.33874 | 122.8546 | 123.0377 | 122.8821 | 122.9324 | 122.699 | 123.1339 | 122.9095 | 122.5571 | 122.9324 | 122.699 | 122.9095 | 122.8821 | 123.1339 | -0.72784 | -0.53101
3709.125 | 123.1293 | -122.85 | 0.19226 | 0.16106 | 0.012416 | -0.0041742 | 0.036611 | -0.016829 | -0.010194 | 0.0098437 | -0.13275 | 0.045776 | -0.44861 | 0.036621 | 0.086975 | 0.10529 | -0.13275 | 0.26093 | 0.23804 | -0.30212 | 122.4014 | -0.14648 | 122.7173 | 122.8867 | -0.10529 | 122.5479 | 0.045776 | 0.31586 | 122.7173 | 123.111 | 122.937 | 122.8958 | 122.7173 | 123.0881 | 122.9553 | 122.5479 | 122.8958 | 122.7173 | 122.9553 | 122.937 | 123.0881 | -0.64087 | -0.49438
3710.8906 | 123.1567 | -122.818 | 0.1831 | -0.1136 | 0.011775 | -0.0097284 | 0.039601 | -0.020034 | -0.012544 | 0.0081347 | -0.11444 | 0.041199 | -0.43945 | 0.091553 | 0.12817 | 0.16937 | -0.13275 | 0.33417 | 0.24719 | -0.30212 | 122.3785 | -0.14191 | 122.7036 | 122.9095 | -0.054931 | 122.5159 | 0.064087 | 0.32501 | 122.6852 | 123.1522 | 122.9462 | 122.8592 | 122.7036 | 123.0652 | 122.9874 | 122.5159 | 122.8592 | 122.7036 | 122.9874 | 122.9462 | 123.0652 | -0.62256 | -0.48523
3712.5938 | 123.0743 | -122.8363 | 0.20599 | -0.022049 | 0.0094251 | -0.0011834 | 0.049001 | -0.01512 | -0.012971 | 0.010271 | -0.16479 | 0.082397 | -0.49439 | 0.009155 | -0.009155 | 0.022888 | -0.013733 | 0.17853 | 0.27008 | -0.3067 | 122.3419 | -0.1236 | 122.6715 | 122.8455 | -0.21515 | 122.5296 | 0.064087 | 0.32959 | 122.8226 | 123.0148 | 122.8271 | 122.9187 | 122.6715 | 123.1064 | 122.8592 | 122.5296 | 122.9187 | 122.6715 | 122.8592 | 122.8271 | 123.1064 | -0.70038 | -0.5127
3714.3438 | 123.0698 | -122.8546 | 0.21515 | 0.22209 | 0.0094251 | -0.0033196 | 0.044301 | -0.015761 | -0.013399 | 0.0081347 | -0.091553 | 0.032043 | -0.44861 | 0.091553 | 0.10529 | 0.14191 | -0.18768 | 0.29297 | 0.23346 | -0.27466 | 122.406 | -0.18311 | 122.7631 | 122.9462 | -0.10986 | 122.58 | 0.01831 | 0.35706 | 122.6669 | 123.1476 | 122.9599 | 122.8867 | 122.7631 | 123.0881 | 122.9965 | 122.58 | 122.8867 | 122.7631 | 122.9965 | 122.9599 | 123.0881 | -0.66376 | -0.48981
3716.0938 | 123.0881 | -122.8317 | 0.21057 | 0.10002 | 0.011134 | -0.011224 | 0.041951 | -0.016616 | -0.0095531 | 0.0092029 | -0.10071 | 0.045776 | -0.43945 | 0.068665 | 0.07782 | 0.13275 | -0.15564 | 0.27466 | 0.2243 | -0.28839 | 122.3923 | -0.1648 | 122.731 | 122.9004 | -0.13275 | 122.5433 | 0.013733 | 0.33874 | 122.6761 | 123.1064 | 122.9095 | 122.8775 | 122.731 | 123.056 | 122.9645 | 122.5433 | 122.8775 | 122.731 | 122.9645 | 122.9095 | 123.056 | -0.65002 | -0.49896
3717.7969 | 123.0743 | -122.85 | 0.20599 | -0.022049 | 0.0083569 | -0.010369 | 0.04836 | -0.016402 | -0.014039 | 0.010912 | -0.15564 | 0.068665 | -0.48981 | 0.009155 | 0.022888 | 0.041199 | -0.027466 | 0.21057 | 0.27924 | -0.30212 | 122.3602 | -0.13733 | 122.6944 | 122.8592 | -0.18311 | 122.5479 | 0.073242 | 0.33417 | 122.8226 | 123.0606 | 122.8729 | 122.9187 | 122.6944 | 123.1293 | 122.8912 | 122.5479 | 122.9187 | 122.6944 | 122.8912 | 122.8729 | 123.1293 | -0.6958 | -0.50812
3719.5625 | 123.0835 | -122.8592 | 0.2243 | 0.21446 | 0.012629 | -0.0054558 | 0.047078 | -0.015975 | -0.014253 | 0.0089893 | -0.18768 | 0.050354 | -0.48065 | 0.018311 | 0.054932 | 0.073242 | -0.12817 | 0.2243 | 0.25635 | -0.28381 | 122.3785 | -0.17395 | 122.6715 | 122.8775 | -0.16937 | 122.5754 | 0.032044 | 0.29297 | 122.731 | 123.0835 | 122.9141 | 122.9095 | 122.6715 | 123.1155 | 122.9324 | 122.5754 | 122.9095 | 122.6715 | 122.9324 | 122.9141 | 123.1155 | -0.70496 | -0.50812
3721.25 | 123.2162 | -122.8043 | 0.17853 | -0.2433 | 0.010921 | -0.0060968 | 0.040029 | -0.019179 | -0.010621 | 0.0094165 | -0.2243 | 0.082397 | -0.49439 | -0.013733 | 0 | 0.013733 | 0.059509 | 0.17853 | 0.29755 | -0.3479 | 122.3099 | -0.096131 | 122.58 | 122.7905 | -0.17853 | 122.4564 | 0.11902 | 0.27008 | 122.8638 | 122.9828 | 122.8043 | 122.8867 | 122.58 | 123.1018 | 122.818 | 122.4564 | 122.8867 | 122.58 | 122.818 | 122.8043 | 123.1018 | -0.67291 | -0.52643
3723 | 123.1567 | -122.8271 | 0.17395 | -0.10597 | 0.0098523 | -0.0093012 | 0.037679 | -0.021102 | -0.011049 | 0.011126 | -0.1236 | 0.041199 | -0.45776 | 0.086975 | 0.12817 | 0.15106 | -0.14648 | 0.32501 | 0.22888 | -0.3067 | 122.3694 | -0.13275 | 122.7036 | 122.9141 | -0.045776 | 122.5204 | 0.054932 | 0.33417 | 122.6807 | 123.1522 | 122.9553 | 122.8683 | 122.7036 | 123.056 | 122.9782 | 122.5204 | 122.8683 | 122.7036 | 122.9782 | 122.9553 | 123.056 | -0.63171 | -0.48065
3724.7656 | 123.1522 | -122.8134 | 0.19226 | -0.083084 | 0.0083569 | -0.003747 | 0.041738 | -0.019179 | -0.010621 | 0.010698 | -0.11902 | 0.041199 | -0.43488 | 0.11902 | 0.12817 | 0.15564 | -0.13733 | 0.3479 | 0.24719 | -0.29755 | 122.3785 | -0.15106 | 122.6944 | 122.9324 | -0.064087 | 122.5159 | 0.054931 | 0.31586 | 122.6761 | 123.1613 | 122.9416 | 122.8546 | 122.6944 | 123.0606 | 122.9691 | 122.5159 | 122.8546 | 122.6944 | 122.9691 | 122.9416 | 123.0606 | -0.62714 | -0.48981
3726.5156 | 123.1842 | -122.7997 | 0.16937 | 0.023727 | 0.010707 | -0.0086602 | 0.040456 | -0.020034 | -0.011476 | 0.0077075 | -0.17395 | 0.050354 | -0.46692 | 0.032043 | 0.059509 | 0.07782 | -0.10071 | 0.24719 | 0.2655 | -0.29755 | 122.3328 | -0.11902 | 122.6257 | 122.8317 | -0.10986 | 122.5021 | 0.09613 | 0.29297 | 122.699 | 123.0469 | 122.8592 | 122.85 | 122.6257 | 123.0652 | 122.8775 | 122.5021 | 122.85 | 122.6257 | 122.8775 | 122.8592 | 123.0652 | -0.63629 | -0.46692
3728.2812 | 123.1888 | -122.8317 | 0.19226 | -0.18227 | 0.011561 | -0.0086602 | 0.048146 | -0.019179 | -0.01233 | 0.0083483 | -0.20599 | 0.10071 | -0.5127 | 0.013733 | 0.004578 | 0.018311 | 0.032043 | 0.19684 | 0.28381 | -0.31128 | 122.319 | -0.091553 | 122.6257 | 122.8455 | -0.18768 | 122.5204 | 0.091552 | 0.3067 | 122.8638 | 123.0286 | 122.8363 | 122.9324 | 122.6257 | 123.1155 | 122.85 | 122.5204 | 122.9324 | 122.6257 | 122.85 | 122.8363 | 123.1155 | -0.70496 | -0.50354
3730.0469 | 123.1934 | -122.8043 | 0.1831 | 0.00083945 | 0.010707 | -0.012505 | 0.038533 | -0.018325 | -0.010194 | 0.0094165 | -0.17395 | 0.041199 | -0.4303 | 0.032043 | 0.059509 | 0.086975 | -0.11444 | 0.23346 | 0.25635 | -0.3067 | 122.374 | -0.14191 | 122.6303 | 122.8363 | -0.1236 | 122.4976 | 0.073243 | 0.25635 | 122.6898 | 123.0377 | 122.8638 | 122.8455 | 122.6303 | 123.0606 | 122.8912 | 122.4976 | 122.8455 | 122.6303 | 122.8912 | 122.8638 | 123.0606 | -0.6134 | -0.48981
3731.7969 | 123.056 | -122.8638 | 0.21973 | 0.1992 | 0.0092115 | -0.0073786 | 0.046437 | -0.019393 | -0.011049 | 0.0081347 | -0.11902 | 0.013733 | -0.45776 | 0.091553 | 0.10529 | 0.13275 | -0.20599 | 0.29297 | 0.23804 | -0.28381 | 122.406 | -0.20599 | 122.7448 | 122.9553 | -0.11444 | 122.58 | 0.01831 | 0.33875 | 122.6578 | 123.1567 | 122.9691 | 122.8775 | 122.7448 | 123.1018 | 122.9965 | 122.58 | 122.8775 | 122.7448 | 122.9965 | 122.9691 | 123.1018 | -0.67749 | -0.50354
3733.5625 | 123.1201 | -122.8409 | 0.20599 | 0.031357 | 0.014766 | -0.003106 | 0.047933 | -0.014693 | -0.013185 | 0.0087757 | -0.19226 | 0.07782 | -0.49896 | -0.013733 | -0.022888 | -0.004578 | 0 | 0.15106 | 0.27924 | -0.32044 | 122.3419 | -0.12817 | 122.6486 | 122.8271 | -0.22888 | 122.5204 | 0.073242 | 0.3067 | 122.8409 | 122.9919 | 122.818 | 122.9187 | 122.6486 | 123.1201 | 122.8363 | 122.5204 | 122.9187 | 122.6486 | 122.8363 | 122.818 | 123.1201 | -0.70496 | -0.52643
3735.25 | 123.1567 | -122.85 | 0.17853 | -0.22041 | 0.010066 | -0.0067376 | 0.040242 | -0.018538 | -0.01169 | 0.0068531 | -0.11902 | 0.059509 | -0.45776 | 0.09613 | 0.1236 | 0.13275 | -0.13733 | 0.31586 | 0.23346 | -0.29297 | 122.3923 | -0.11902 | 122.731 | 122.9462 | -0.054932 | 122.5571 | 0.054931 | 0.33875 | 122.7127 | 123.1659 | 122.9736 | 122.9095 | 122.731 | 123.0835 | 122.9828 | 122.5571 | 122.9095 | 122.731 | 122.9828 | 122.9736 | 123.0835 | -0.63629 | -0.4715
3737 | 123.1567 | -122.8317 | 0.16937 | -0.15938 | 0.0098523 | -0.0088738 | 0.041524 | -0.020247 | -0.010835 | 0.0089893 | -0.10986 | 0.045776 | -0.45776 | 0.11902 | 0.12817 | 0.15106 | -0.13275 | 0.33417 | 0.23804 | -0.29755 | 122.374 | -0.1236 | 122.7219 | 122.9507 | -0.041199 | 122.5342 | 0.068664 | 0.3479 | 122.699 | 123.1659 | 122.9599 | 122.8775 | 122.7219 | 123.0698 | 122.9828 | 122.5342 | 122.8775 | 122.7219 | 122.9828 | 122.9599 | 123.0698 | -0.62714 | -0.46692
3738.7656 | 123.0835 | -122.8592 | 0.21515 | -0.098343 | 0.013698 | -0.004815 | 0.049001 | -0.017897 | -0.014467 | 0.0077075 | -0.15106 | 0.073242 | -0.47607 | 0.050354 | 0.041199 | 0.054932 | -0.045776 | 0.2243 | 0.27008 | -0.30212 | 122.3831 | -0.14191 | 122.7081 | 122.9095 | -0.17395 | 122.5571 | 0.054932 | 0.32501 | 122.8134 | 123.0835 | 122.9004 | 122.9324 | 122.7081 | 123.1293 | 122.9141 | 122.5571 | 122.9324 | 122.7081 | 122.9141 | 122.9004 | 123.1293 | -0.69122 | -0.51727
3740.5469 | 123.1567 | -122.818 | 0.19684 | -0.19753 | 0.01028 | -0.0086602 | 0.039815 | -0.019393 | -0.011903 | 0.0092029 | -0.11444 | 0.041199 | -0.48065 | 0.091553 | 0.10071 | 0.1236 | -0.10071 | 0.29755 | 0.23804 | -0.3067 | 122.3373 | -0.15564 | 122.7036 | 122.9095 | -0.09613 | 122.5113 | 0.041199 | 0.36621 | 122.7173 | 123.1155 | 122.9187 | 122.8592 | 122.7036 | 123.056 | 122.9416 | 122.5113 | 122.8592 | 122.7036 | 122.9416 | 122.9187 | 123.056 | -0.67749 | -0.50354
3742.25 | 123.1705 | -122.8134 | 0.18768 | 0.054245 | 0.010921 | -0.0078058 | 0.04067 | -0.01747 | -0.011903 | 0.0085619 | -0.16022 | 0.064087 | -0.44861 | 0.036621 | 0.059509 | 0.082397 | -0.11444 | 0.24261 | 0.24261 | -0.3067 | 122.3648 | -0.1236 | 122.6532 | 122.85 | -0.12817 | 122.5067 | 0.054932 | 0.28839 | 122.699 | 123.056 | 122.8729 | 122.8775 | 122.6532 | 123.056 | 122.8958 | 122.5067 | 122.8775 | 122.6532 | 122.8958 | 122.8729 | 123.056 | -0.63629 | -0.49438
3744 | 123.1934 | -122.7905 | 0.17395 | 0.038986 | 0.01028 | -0.0078058 | 0.041524 | -0.020034 | -0.012544 | 0.0085619 | -0.17395 | 0.064087 | -0.45319 | 0.059509 | 0.059509 | 0.086975 | -0.09613 | 0.26093 | 0.24261 | -0.31586 | 122.3373 | -0.10986 | 122.6166 | 122.85 | -0.11444 | 122.4747 | 0.068665 | 0.27924 | 122.6944 | 123.0515 | 122.85 | 122.8546 | 122.6166 | 123.0331 | 122.8775 | 122.4747 | 122.8546 | 122.6166 | 122.8775 | 122.85 | 123.0331 | -0.62714 | -0.48981
3745.7656 | 123.1705 | -122.8088 | 0.19226 | -0.17464 | 0.0098523 | -0.011224 | 0.041951 | -0.019393 | -0.012971 | 0.0081347 | -0.11444 | 0.050354 | -0.43488 | 0.082397 | 0.07782 | 0.10529 | -0.073242 | 0.30212 | 0.24261 | -0.30212 | 122.374 | -0.14191 | 122.6944 | 122.8912 | -0.11444 | 122.5067 | 0.050354 | 0.32043 | 122.7356 | 123.111 | 122.8867 | 122.8592 | 122.6944 | 123.0515 | 122.9141 | 122.5067 | 122.8592 | 122.6944 | 122.9141 | 122.8867 | 123.0515 | -0.62714 | -0.49438
3747.5469 | 123.1842 | -122.8271 | 0.17395 | -0.23567 | 0.0072889 | -0.0073786 | 0.04366 | -0.019606 | -0.01468 | 0.0089893 | -0.13733 | 0.041199 | -0.46692 | 0.07782 | 0.07782 | 0.10071 | -0.027466 | 0.28839 | 0.26093 | -0.30212 | 122.3602 | -0.13275 | 122.6898 | 122.905 | -0.09613 | 122.525 | 0.086975 | 0.32959 | 122.7997 | 123.1155 | 122.905 | 122.8683 | 122.6898 | 123.0881 | 122.9279 | 122.525 | 122.8683 | 122.6898 | 122.9279 | 122.905 | 123.0881 | -0.64087 | -0.47607
3749.25 | 123.1842 | -122.8134 | 0.19684 | -0.18227 | 0.010066 | -0.0052422 | 0.049001 | -0.018325 | -0.014039 | 0.010057 | -0.19226 | 0.10529 | -0.49896 | 0.027466 | 0.018311 | 0.013733 | 0.036621 | 0.19226 | 0.28839 | -0.32044 | 122.3145 | -0.091552 | 122.6212 | 122.8409 | -0.17853 | 122.493 | 0.091553 | 0.3067 | 122.85 | 123.0057 | 122.8317 | 122.9187 | 122.6212 | 123.1018 | 122.8271 | 122.493 | 122.9187 | 122.6212 | 122.8271 | 122.8317 | 123.1018 | -0.6958 | -0.51727
3751 | 123.1567 | -122.8409 | 0.19226 | -0.23567 | 0.0098523 | -0.0088738 | 0.043233 | -0.017897 | -0.011049 | 0.0083483 | -0.1236 | 0.041199 | -0.45319 | 0.10986 | 0.12817 | 0.12817 | -0.13275 | 0.31586 | 0.22888 | -0.29755 | 122.3877 | -0.15106 | 122.7173 | 122.9507 | -0.064087 | 122.5433 | 0.036621 | 0.32959 | 122.7081 | 123.1567 | 122.9691 | 122.8821 | 122.7173 | 123.0698 | 122.9691 | 122.5433 | 122.8821 | 122.7173 | 122.9691 | 122.9691 | 123.0698 | -0.64545 | -0.48981
3752.7656 | 123.0789 | -122.8592 | 0.20142 | 0.20683 | 0.011134 | -0.006524 | 0.048574 | -0.017043 | -0.014253 | 0.0068531 | -0.16479 | 0.059509 | -0.47607 | 0.054932 | 0.054932 | 0.091553 | -0.14648 | 0.2243 | 0.26093 | -0.29297 | 122.3831 | -0.14191 | 122.6944 | 122.9141 | -0.14648 | 122.5662 | 0.059509 | 0.31128 | 122.7127 | 123.0835 | 122.9141 | 122.9187 | 122.6944 | 123.1201 | 122.9507 | 122.5662 | 122.9187 | 122.6944 | 122.9507 | 122.9141 | 123.1201 | -0.67749 | -0.49438
3754.4531 | 123.1888 | -122.818 | 0.15564 | -0.25093 | 0.0075025 | -0.008233 | 0.04366 | -0.018111 | -0.010194 | 0.0081347 | -0.15106 | 0.082397 | -0.48065 | 0.045776 | 0.050354 | 0.064087 | -0.027466 | 0.25635 | 0.27008 | -0.30212 | 122.3373 | -0.073243 | 122.6669 | 122.8638 | -0.10529 | 122.5159 | 0.11444 | 0.32959 | 122.7905 | 123.0743 | 122.8683 | 122.9004 | 122.6669 | 123.0881 | 122.8821 | 122.5159 | 122.9004 | 122.6669 | 122.8821 | 122.8683 | 123.0881 | -0.63629 | -0.45776
3756.2188 | 123.0972 | -122.8317 | 0.20142 | 0.15343 | 0.012202 | -0.0067376 | 0.046437 | -0.017684 | -0.010835 | 0.0096301 | -0.20599 | 0.10071 | -0.48065 | 0 | 0.009155 | 0.041199 | -0.059509 | 0.16022 | 0.25635 | -0.31586 | 122.3511 | -0.10071 | 122.6257 | 122.8317 | -0.19226 | 122.5159 | 0.054932 | 0.27466 | 122.7722 | 122.9919 | 122.8409 | 122.9324 | 122.6257 | 123.0881 | 122.8729 | 122.5159 | 122.9324 | 122.6257 | 122.8729 | 122.8409 | 123.0881 | -0.68207 | -0.51727
3758 | 123.1476 | -122.8134 | 0.16022 | -0.20515 | 0.010921 | -0.0075922 | 0.038747 | -0.01982 | -0.010835 | 0.0098437 | -0.10071 | 0.064087 | -0.45776 | 0.09613 | 0.12817 | 0.14648 | -0.12817 | 0.32959 | 0.2243 | -0.29755 | 122.3557 | -0.09613 | 122.7127 | 122.9095 | -0.032043 | 122.5159 | 0.064087 | 0.35706 | 122.6852 | 123.143 | 122.9416 | 122.8775 | 122.7127 | 123.0377 | 122.9599 | 122.5159 | 122.8775 | 122.7127 | 122.9599 | 122.9416 | 123.0377 | -0.61798 | -0.45776
3759.7656 | 123.0606 | -122.8638 | 0.20142 | 0.18394 | 0.010707 | -0.0016106 | 0.046865 | -0.017897 | -0.012971 | 0.0089893 | -0.13275 | 0.064087 | -0.48065 | 0.086975 | 0.09613 | 0.13275 | -0.16937 | 0.2655 | 0.23804 | -0.28381 | 122.3831 | -0.13733 | 122.731 | 122.9507 | -0.10529 | 122.58 | 0.036621 | 0.3479 | 122.6944 | 123.1293 | 122.9599 | 122.9279 | 122.731 | 123.1018 | 122.9965 | 122.58 | 122.9279 | 122.731 | 122.9965 | 122.9599 | 123.1018 | -0.68207 | -0.48523
3761.4531 | 123.1476 | -122.8271 | 0.19226 | -0.17464 | 0.010921 | -0.010369 | 0.039601 | -0.020461 | -0.0084851 | 0.0094165 | -0.11444 | 0.050354 | -0.43488 | 0.10986 | 0.1236 | 0.14191 | -0.13733 | 0.33417 | 0.23804 | -0.27924 | 122.3923 | -0.14191 | 122.7127 | 122.937 | -0.068665 | 122.5479 | 0.045776 | 0.32043 | 122.6898 | 123.1613 | 122.9507 | 122.8775 | 122.7127 | 123.0652 | 122.9691 | 122.5479 | 122.8775 | 122.7127 | 122.9691 | 122.9507 | 123.0652 | -0.62714 | -0.4715
3763.2031 | 123.1201 | -122.818 | 0.21057 | 0.077133 | 0.011134 | -0.0063104 | 0.04836 | -0.018111 | -0.013826 | 0.011126 | -0.21057 | 0.09613 | -0.50354 | -0.050354 | -0.059509 | -0.013733 | -0.004578 | 0.13733 | 0.28839 | -0.35248 | 122.3145 | -0.11444 | 122.6074 | 122.7676 | -0.27008 | 122.4655 | 0.07782 | 0.29297 | 122.8134 | 122.9553 | 122.7585 | 122.9141 | 122.6074 | 123.1064 | 122.8043 | 122.4655 | 122.9141 | 122.6074 | 122.8043 | 122.7585 | 123.1064 | -0.71411 | -0.56305
3764.9688 | 123.2025 | -122.7951 | 0.17853 | -0.20515 | 0.011134 | -0.0095148 | 0.041524 | -0.019606 | -0.012971 | 0.0057849 | -0.18768 | 0.086975 | -0.4715 | 0.009155 | 0.009155 | 0.009155 | 0.022888 | 0.21515 | 0.27466 | -0.33875 | 122.3236 | -0.091553 | 122.6074 | 122.8043 | -0.16937 | 122.4564 | 0.09613 | 0.28381 | 122.818 | 123.0103 | 122.8043 | 122.8821 | 122.6074 | 123.0698 | 122.8043 | 122.4564 | 122.8821 | 122.6074 | 122.8043 | 122.8043 | 123.0698 | -0.65002 | -0.51727
3766.6719 | 123.0835 | -122.8638 | 0.19684 | -0.01442 | 0.012629 | -0.0050286 | 0.047506 | -0.015975 | -0.015107 | 0.010698 | -0.15106 | 0.07782 | -0.48981 | 0 | 0.009155 | 0.022888 | -0.009155 | 0.19226 | 0.28839 | -0.32044 | 122.374 | -0.11902 | 122.7127 | 122.8638 | -0.18768 | 122.5433 | 0.091553 | 0.33874 | 122.8546 | 123.056 | 122.8729 | 122.9416 | 122.7127 | 123.1522 | 122.8867 | 122.5433 | 122.9416 | 122.7127 | 122.8867 | 122.8729 | 123.1522 | -0.68664 | -0.51727
3768.4375 | 123.0789 | -122.8592 | 0.20599 | 0.1992 | 0.012416 | -0.0054558 | 0.04366 | -0.015334 | -0.011049 | 0.0094165 | -0.17853 | 0.073242 | -0.47607 | 0.013733 | 0.036621 | 0.086975 | -0.12817 | 0.21057 | 0.25177 | -0.31128 | 122.3831 | -0.13275 | 122.6807 | 122.8729 | -0.16937 | 122.5479 | 0.045776 | 0.29755 | 122.731 | 123.0698 | 122.8958 | 122.9324 | 122.6807 | 123.111 | 122.9462 | 122.5479 | 122.9324 | 122.6807 | 122.9462 | 122.8958 | 123.111 | -0.68207 | -0.51727
3770.1562 | 123.111 | -122.85 | 0.21515 | 0.13054 | 0.012202 | -0.0073786 | 0.043447 | -0.015548 | -0.012544 | 0.0092029 | -0.2243 | 0.086975 | -0.50812 | -0.022888 | 0 | 0.013733 | -0.018311 | 0.14648 | 0.25635 | -0.33417 | 122.3419 | -0.12817 | 122.6257 | 122.8271 | -0.21515 | 122.5159 | 0.041199 | 0.28381 | 122.8317 | 122.9965 | 122.85 | 122.937 | 122.6257 | 123.1064 | 122.8638 | 122.5159 | 122.937 | 122.6257 | 122.8638 | 122.85 | 123.1064 | -0.72327 | -0.54932
3771.9219 | 123.0652 | -122.8592 | 0.21515 | -0.060196 | 0.010707 | -0.0093012 | 0.043874 | -0.015975 | -0.01233 | 0.0085619 | -0.14648 | 0.091553 | -0.50354 | 0.027466 | 0.027466 | 0.082397 | -0.036621 | 0.21973 | 0.26093 | -0.32959 | 122.3557 | -0.1236 | 122.7127 | 122.8867 | -0.18768 | 122.5296 | 0.045776 | 0.35706 | 122.8226 | 123.0789 | 122.8867 | 122.9507 | 122.7127 | 123.1201 | 122.9416 | 122.5296 | 122.9507 | 122.7127 | 122.9416 | 122.8867 | 123.1201 | -0.71869 | -0.54474
3773.6875 | 123.1064 | -122.8455 | 0.20142 | 0.038986 | 0.01028 | -0.0063104 | 0.04366 | -0.015975 | -0.013612 | 0.010271 | -0.1831 | 0.073242 | -0.48065 | -0.018311 | -0.018311 | 0.009155 | 0.004578 | 0.16479 | 0.27008 | -0.29755 | 122.3648 | -0.12817 | 122.6624 | 122.8271 | -0.21973 | 122.5479 | 0.068665 | 0.29755 | 122.85 | 123.0103 | 122.8271 | 122.9187 | 122.6624 | 123.1155 | 122.8546 | 122.5479 | 122.9187 | 122.6624 | 122.8546 | 122.8271 | 123.1155 | -0.68207 | -0.49896
3775.4688 | 123.0835 | -122.8775 | 0.21515 | -0.083084 | 0.011775 | -0.01101 | 0.046224 | -0.016402 | -0.013612 | 0.010057 | -0.16022 | 0.07782 | -0.48981 | 0.022888 | 0.036621 | 0.064087 | -0.027466 | 0.21973 | 0.28381 | -0.29297 | 122.3877 | -0.13733 | 122.7173 | 122.9004 | -0.17853 | 122.5845 | 0.068664 | 0.32959 | 122.85 | 123.0972 | 122.9141 | 122.9553 | 122.7173 | 123.1613 | 122.9416 | 122.5845 | 122.9553 | 122.7173 | 122.9416 | 122.9141 | 123.1613 | -0.70496 | -0.50812
3777.2188 | 123.1979 | -122.8546 | 0.18768 | -0.25856 | 0.011134 | -0.01101 | 0.039815 | -0.018965 | -0.011262 | 0.0079211 | -0.21515 | 0.10986 | -0.4715 | -0.036621 | 0.013733 | 0.013733 | 0.068665 | 0.18768 | 0.28839 | -0.3479 | 122.3831 | -0.07782 | 122.6395 | 122.818 | -0.17395 | 122.5067 | 0.10071 | 0.25635 | 122.9233 | 123.0423 | 122.8683 | 122.9645 | 122.6395 | 123.143 | 122.8683 | 122.5067 | 122.9645 | 122.6395 | 122.8683 | 122.8683 | 123.143 | -0.65918 | -0.53558
3778.9844 | 123.0743 | -122.8958 | 0.22888 | -0.075455 | 0.011134 | -0.01101 | 0.043019 | -0.016188 | -0.012117 | 0.0092029 | -0.16479 | 0.10071 | -0.47607 | 0.032043 | 0.032043 | 0.068665 | -0.013733 | 0.21973 | 0.27008 | -0.31128 | 122.4197 | -0.12817 | 122.731 | 122.9279 | -0.19684 | 122.5845 | 0.041199 | 0.31128 | 122.8821 | 123.1155 | 122.9279 | 122.9965 | 122.731 | 123.1659 | 122.9645 | 122.5845 | 122.9965 | 122.731 | 122.9645 | 122.9279 | 123.1659 | -0.70496 | -0.54016
3780.75 | 123.056 | -122.8729 | 0.19226 | 0.17632 | 0.012202 | -0.0067376 | 0.042379 | -0.01512 | -0.011903 | 0.0085619 | -0.1236 | 0.050354 | -0.43945 | 0.068665 | 0.10071 | 0.14648 | -0.18768 | 0.2655 | 0.23346 | -0.28839 | 122.4335 | -0.14191 | 122.7493 | 122.9416 | -0.091553 | 122.5845 | 0.041198 | 0.31586 | 122.6852 | 123.1384 | 122.9736 | 122.9233 | 122.7493 | 123.1064 | 123.0194 | 122.5845 | 122.9233 | 122.7493 | 123.0194 | 122.9736 | 123.1064 | -0.63171 | -0.48065
3782.5 | 123.1705 | -122.8271 | 0.17853 | 0.084762 | 0.0094251 | -0.008233 | 0.036397 | -0.019606 | -0.011476 | 0.0066393 | -0.15564 | 0.054932 | -0.45776 | 0.022888 | 0.068665 | 0.091553 | -0.10071 | 0.24261 | 0.24261 | -0.31586 | 122.3694 | -0.1236 | 122.6715 | 122.85 | -0.10986 | 122.5113 | 0.064087 | 0.30212 | 122.7264 | 123.0698 | 122.8958 | 122.8821 | 122.6715 | 123.0698 | 122.9187 | 122.5113 | 122.8821 | 122.6715 | 122.9187 | 122.8958 | 123.0698 | -0.63629 | -0.49438
3784.2031 | 123.0835 | -122.8729 | 0.21057 | -0.090714 | 0.010066 | -0.0097284 | 0.047933 | -0.019606 | -0.010621 | 0.0062121 | -0.15106 | 0.073242 | -0.46692 | 0.027466 | 0.027466 | 0.041199 | -0.022888 | 0.21515 | 0.27008 | -0.31586 | 122.406 | -0.13733 | 122.7219 | 122.9004 | -0.18311 | 122.5571 | 0.05951 | 0.31586 | 122.85 | 123.0881 | 122.9004 | 122.9462 | 122.7219 | 123.143 | 122.9141 | 122.5571 | 122.9462 | 122.7219 | 122.9141 | 122.9004 | 123.143 | -0.67749 | -0.52643
3785.9688 | 123.1155 | -122.8592 | 0.20599 | 0.1458 | 0.011561 | -0.004815 | 0.045156 | -0.017256 | -0.012971 | 0.0094165 | -0.21973 | 0.09613 | -0.48523 | -0.041199 | -0.027466 | -0.004578 | 0 | 0.14191 | 0.28381 | -0.31128 | 122.374 | -0.10986 | 122.6395 | 122.818 | -0.23346 | 122.5479 | 0.077819 | 0.2655 | 122.8592 | 123.0011 | 122.8317 | 122.9553 | 122.6395 | 123.143 | 122.8546 | 122.5479 | 122.9553 | 122.6395 | 122.8546 | 122.8317 | 123.143 | -0.69122 | -0.51727
3787.6719 | 123.1522 | -122.8363 | 0.1831 | -0.17464 | 0.011348 | -0.010583 | 0.039388 | -0.020034 | -0.012117 | 0.0074939 | -0.086975 | 0.054932 | -0.45776 | 0.082397 | 0.1236 | 0.15564 | -0.1236 | 0.33875 | 0.23804 | -0.29755 | 122.3785 | -0.12817 | 122.7493 | 122.9187 | -0.059509 | 122.5388 | 0.054932 | 0.37079 | 122.7127 | 123.175 | 122.9599 | 122.8912 | 122.7493 | 123.0743 | 122.9919 | 122.5388 | 122.8912 | 122.7493 | 122.9919 | 122.9599 | 123.0743 | -0.64087 | -0.48065
3789.4219 | 123.0835 | -122.8729 | 0.21515 | 0.18394 | 0.011775 | -0.011224 | 0.042379 | -0.015548 | -0.012544 | 0.0087757 | -0.10071 | 0.050354 | -0.44861 | 0.082397 | 0.086975 | 0.12817 | -0.18768 | 0.28381 | 0.23804 | -0.29755 | 122.4243 | -0.16479 | 122.7722 | 122.9553 | -0.12817 | 122.5754 | 0.022888 | 0.3479 | 122.6852 | 123.1567 | 122.9599 | 122.9233 | 122.7722 | 123.111 | 123.0011 | 122.5754 | 122.9233 | 122.7722 | 123.0011 | 122.9599 | 123.111 | -0.66376 | -0.5127
3791.1875 | 123.1613 | -122.8043 | 0.18768 | -0.060196 | 0.010066 | -0.0095148 | 0.038533 | -0.018325 | -0.012758 | 0.0081347 | -0.13275 | 0.073242 | -0.44861 | 0.086975 | 0.09613 | 0.14191 | -0.13275 | 0.32044 | 0.23804 | -0.29755 | 122.3557 | -0.11444 | 122.6715 | 122.8912 | -0.091553 | 122.5067 | 0.050354 | 0.31586 | 122.6715 | 123.1247 | 122.9004 | 122.8775 | 122.6715 | 123.0423 | 122.9462 | 122.5067 | 122.8775 | 122.6715 | 122.9462 | 122.9004 | 123.0423 | -0.63629 | -0.48523
3792.8906 | 123.1522 | -122.85 | 0.1831 | -0.14412 | 0.011561 | -0.0095148 | 0.042806 | -0.018325 | -0.013185 | 0.0070667 | -0.082397 | 0.054932 | -0.43488 | 0.09613 | 0.11902 | 0.14648 | -0.12817 | 0.33417 | 0.24261 | -0.29755 | 122.4152 | -0.12817 | 122.7676 | 122.9462 | -0.064086 | 122.5525 | 0.05951 | 0.35248 | 122.7219 | 123.1842 | 122.9691 | 122.905 | 122.7676 | 123.0927 | 122.9965 | 122.5525 | 122.905 | 122.7676 | 122.9965 | 122.9691 | 123.0927 | -0.61798 | -0.48065
3794.6406 | 123.111 | -122.8226 | 0.20599 | 0.1458 | 0.011134 | -0.006524 | 0.044942 | -0.018965 | -0.010194 | 0.0092029 | -0.10986 | 0.054932 | -0.44861 | 0.050354 | 0.064087 | 0.10529 | -0.13733 | 0.26093 | 0.25635 | -0.29755 | 122.374 | -0.15106 | 122.7127 | 122.8729 | -0.14191 | 122.525 | 0.050354 | 0.33875 | 122.6852 | 123.0835 | 122.8867 | 122.8775 | 122.7127 | 123.0789 | 122.9279 | 122.525 | 122.8775 | 122.7127 | 122.9279 | 122.8867 | 123.0789 | -0.6546 | -0.50354
3796.4219 | 123.0743 | -122.8821 | 0.20599 | 0.16869 | 0.011348 | -0.0039606 | 0.046651 | -0.017256 | -0.013826 | 0.0096301 | -0.1236 | 0.064087 | -0.46234 | 0.09613 | 0.082397 | 0.1236 | -0.16479 | 0.28381 | 0.24719 | -0.27466 | 122.4197 | -0.14191 | 122.7585 | 122.9782 | -0.1236 | 122.6074 | 0.041198 | 0.33875 | 122.7173 | 123.1659 | 122.9645 | 122.9462 | 122.7585 | 123.1293 | 123.0057 | 122.6074 | 122.9462 | 122.7585 | 123.0057 | 122.9645 | 123.1293 | -0.66834 | -0.48065
3798.2031 | 123.1705 | -122.8363 | 0.1831 | -0.18227 | 0.0092115 | -0.0067376 | 0.048146 | -0.018538 | -0.015748 | 0.0053577 | -0.17853 | 0.09613 | -0.50354 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.21057 | 0.28381 | -0.34332 | 122.3328 | -0.086975 | 122.6578 | 122.85 | -0.16479 | 122.493 | 0.10071 | 0.32501 | 122.85 | 123.0469 | 122.8546 | 122.9324 | 122.6578 | 123.1201 | 122.85 | 122.493 | 122.9324 | 122.6578 | 122.85 | 122.8546 | 123.1201 | -0.68664 | -0.52643
3799.9062 | 123.1384 | -122.8455 | 0.19226 | -0.22041 | 0.012202 | -0.0097284 | 0.040242 | -0.015975 | -0.010194 | 0.0081347 | -0.09613 | 0.054932 | -0.43945 | 0.10071 | 0.11444 | 0.13733 | -0.13733 | 0.3479 | 0.23804 | -0.28839 | 122.406 | -0.13733 | 122.7493 | 122.9462 | -0.07782 | 122.5571 | 0.045776 | 0.34332 | 122.7081 | 123.1934 | 122.9599 | 122.9004 | 122.7493 | 123.0835 | 122.9828 | 122.5571 | 122.9004 | 122.7493 | 122.9828 | 122.9599 | 123.0835 | -0.63171 | -0.48065
3801.6719 | 123.0927 | -122.8546 | 0.21515 | -0.044937 | 0.010493 | -0.0050286 | 0.047506 | -0.015975 | -0.013826 | 0.010698 | -0.15106 | 0.07782 | -0.48981 | 0.022888 | 0.004578 | 0.022888 | -0.041199 | 0.17853 | 0.27924 | -0.31586 | 122.3648 | -0.13733 | 122.7036 | 122.8775 | -0.21057 | 122.5388 | 0.064087 | 0.33874 | 122.8134 | 123.0331 | 122.8592 | 122.9324 | 122.7036 | 123.1338 | 122.8775 | 122.5388 | 122.9324 | 122.7036 | 122.8775 | 122.8592 | 123.1338 | -0.70496 | -0.53101
3803.4375 | 123.0789 | -122.8775 | 0.21057 | 0.12291 | 0.01028 | -0.010796 | 0.041524 | -0.018111 | -0.011476 | 0.0096301 | -0.086975 | 0.045776 | -0.43945 | 0.082397 | 0.09613 | 0.13733 | -0.16937 | 0.26093 | 0.23804 | -0.28839 | 122.438 | -0.1648 | 122.7905 | 122.9599 | -0.11444 | 122.5891 | 0.027466 | 0.35248 | 122.7081 | 123.1384 | 122.9736 | 122.9233 | 122.7905 | 123.1155 | 123.0148 | 122.5891 | 122.9233 | 122.7905 | 123.0148 | 122.9736 | 123.1155 | -0.65002 | -0.49896
3805.1406 | 123.1705 | -122.8363 | 0.20599 | -0.19753 | 0.011134 | -0.009942 | 0.044301 | -0.018752 | -0.013399 | 0.0089893 | -0.1831 | 0.091553 | -0.49439 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 0.20599 | 0.28381 | -0.32959 | 122.3419 | -0.11444 | 122.6532 | 122.8546 | -0.19226 | 122.5067 | 0.077819 | 0.31128 | 122.85 | 123.0423 | 122.85 | 122.9279 | 122.6532 | 123.1201 | 122.8592 | 122.5067 | 122.9279 | 122.6532 | 122.8592 | 122.85 | 123.1201 | -0.70038 | -0.53558
3806.9062 | 123.0789 | -122.8775 | 0.2243 | 0.18394 | 0.010493 | -0.0078058 | 0.045369 | -0.018111 | -0.011049 | 0.0089893 | -0.091553 | 0.064087 | -0.46692 | 0.086975 | 0.082397 | 0.13733 | -0.19226 | 0.27924 | 0.23346 | -0.29297 | 122.4106 | -0.16022 | 122.7859 | 122.9645 | -0.14191 | 122.5845 | 0.009155 | 0.37537 | 122.6852 | 123.1567 | 122.9599 | 122.9416 | 122.7859 | 123.111 | 123.0148 | 122.5845 | 122.9416 | 122.7859 | 123.0148 | 122.9599 | 123.111 | -0.69122 | -0.51727
3808.6094 | 123.1613 | -122.85 | 0.16937 | -0.22041 | 0.0089979 | -0.0060968 | 0.03832 | -0.021102 | -0.012544 | 0.0077075 | -0.11902 | 0.045776 | -0.43488 | 0.10529 | 0.11444 | 0.14191 | -0.13275 | 0.31586 | 0.23804 | -0.31586 | 122.4152 | -0.1236 | 122.731 | 122.9553 | -0.054932 | 122.5342 | 0.068664 | 0.31586 | 122.7173 | 123.1659 | 122.9645 | 122.8958 | 122.731 | 123.0881 | 122.9919 | 122.5342 | 122.8958 | 122.731 | 122.9919 | 122.9645 | 123.0881 | -0.60425 | -0.48523
3810.375 | 123.1201 | -122.8317 | 0.19226 | 0.069504 | 0.010066 | -0.006524 | 0.045369 | -0.01982 | -0.014253 | 0.010271 | -0.21057 | 0.091553 | -0.48523 | -0.004578 | -0.027466 | 0 | -0.013733 | 0.13733 | 0.29755 | -0.33875 | 122.3465 | -0.10071 | 122.6212 | 122.8271 | -0.21973 | 122.493 | 0.10528 | 0.27466 | 122.818 | 122.9691 | 122.8043 | 122.9233 | 122.6212 | 123.1293 | 122.8317 | 122.493 | 122.9233 | 122.6212 | 122.8317 | 122.8043 | 123.1293 | -0.67749 | -0.53101
3812.1406 | 123.1064 | -122.8546 | 0.18768 | 0.11528 | 0.0085705 | -0.0097284 | 0.040242 | -0.018538 | -0.0086987 | 0.010485 | -0.12817 | 0.059509 | -0.44403 | 0.073242 | 0.091553 | 0.12817 | -0.16937 | 0.27008 | 0.24719 | -0.3067 | 122.4106 | -0.12817 | 122.7264 | 122.9279 | -0.09613 | 122.5479 | 0.059509 | 0.31586 | 122.6852 | 123.1247 | 122.9462 | 122.9141 | 122.7264 | 123.1018 | 122.9828 | 122.5479 | 122.9141 | 122.7264 | 122.9828 | 122.9462 | 123.1018 | -0.63171 | -0.49438
3813.8438 | 123.1522 | -122.8226 | 0.20599 | -0.21278 | 0.0085705 | -0.0052422 | 0.041738 | -0.021102 | -0.011262 | 0.0068531 | -0.10986 | 0.054932 | -0.43488 | 0.10071 | 0.11444 | 0.11902 | -0.1236 | 0.32501 | 0.23346 | -0.31128 | 122.3877 | -0.15106 | 122.7127 | 122.9233 | -0.091553 | 122.5113 | 0.027465 | 0.32501 | 122.699 | 123.1476 | 122.937 | 122.8775 | 122.7127 | 123.056 | 122.9416 | 122.5113 | 122.8775 | 122.7127 | 122.9416 | 122.937 | 123.056 | -0.64087 | -0.51727
3815.625 | 123.0789 | -122.8638 | 0.20599 | 0.15343 | 0.0094251 | -0.0095148 | 0.042592 | -0.017684 | -0.0063489 | 0.010485 | -0.10986 | 0.050354 | -0.44861 | 0.07782 | 0.09613 | 0.13275 | -0.1831 | 0.28381 | 0.2243 | -0.31586 | 122.4152 | -0.15564 | 122.7539 | 122.9416 | -0.10986 | 122.5479 | 0.01831 | 0.33875 | 122.6807 | 123.1476 | 122.9599 | 122.9141 | 122.7539 | 123.0881 | 122.9965 | 122.5479 | 122.9141 | 122.7539 | 122.9965 | 122.9599 | 123.0881 | -0.6546 | -0.52185
3817.3906 | 123.0789 | -122.8592 | 0.22888 | 0.13054 | 0.0096387 | -0.0050286 | 0.043233 | -0.018111 | -0.010835 | 0.0094165 | -0.09613 | 0.045776 | -0.42572 | 0.082397 | 0.091553 | 0.13733 | -0.17853 | 0.28381 | 0.25177 | -0.28381 | 122.4335 | -0.18311 | 122.7631 | 122.9416 | -0.13733 | 122.5754 | 0.022888 | 0.32959 | 122.6807 | 123.143 | 122.9507 | 122.905 | 122.7631 | 123.111 | 122.9965 | 122.5754 | 122.905 | 122.7631 | 122.9965 | 122.9507 | 123.111 | -0.6546 | -0.5127
3819.1562 | 123.1155 | -122.8271 | 0.1831 | 0.1458 | 0.011989 | -0.0035332 | 0.046224 | -0.015548 | -0.014894 | 0.0085619 | -0.19226 | 0.10071 | -0.48981 | 0.004578 | -0.009155 | 0.004578 | -0.036621 | 0.16479 | 0.27924 | -0.31128 | 122.3373 | -0.082397 | 122.6349 | 122.8317 | -0.19226 | 122.5159 | 0.096131 | 0.29755 | 122.7905 | 122.9919 | 122.818 | 122.9279 | 122.6349 | 123.1064 | 122.8317 | 122.5159 | 122.9279 | 122.6349 | 122.8317 | 122.818 | 123.1064 | -0.67291 | -0.49438
3820.8594 | 123.1247 | -122.8409 | 0.19226 | 0.17632 | 0.0092115 | -0.0080194 | 0.047292 | -0.019393 | -0.012758 | 0.0085619 | -0.21057 | 0.07782 | -0.48523 | -0.032043 | -0.022888 | 0.013733 | -0.009155 | 0.14648 | 0.27924 | -0.32959 | 122.3557 | -0.11444 | 122.6303 | 122.8088 | -0.21515 | 122.5113 | 0.086975 | 0.27466 | 122.8317 | 122.9874 | 122.818 | 122.9187 | 122.6303 | 123.1201 | 122.8546 | 122.5113 | 122.9187 | 122.6303 | 122.8546 | 122.818 | 123.1201 | -0.67749 | -0.52185
3822.6094 | 123.0789 | -122.8821 | 0.21973 | 0.15343 | 0.01028 | -0.01101 | 0.041524 | -0.018111 | -0.013826 | 0.010698 | -0.11902 | 0.068665 | -0.44861 | 0.082397 | 0.09613 | 0.13733 | -0.18768 | 0.25177 | 0.25177 | -0.28381 | 122.4335 | -0.15106 | 122.7631 | 122.9645 | -0.1236 | 122.5983 | 0.032043 | 0.32959 | 122.6944 | 123.1338 | 122.9782 | 122.9507 | 122.7631 | 123.1338 | 123.0194 | 122.5983 | 122.9507 | 122.7631 | 123.0194 | 122.9782 | 123.1338 | -0.66834 | -0.50354
3824.375 | 123.0972 | -122.8821 | 0.19226 | 0.13054 | 0.0087841 | -0.012292 | 0.042379 | -0.019393 | -0.010621 | 0.0064257 | -0.11902 | 0.054932 | -0.44403 | 0.064087 | 0.082397 | 0.10986 | -0.15106 | 0.2655 | 0.23804 | -0.31586 | 122.438 | -0.13733 | 122.7631 | 122.9462 | -0.10986 | 122.5662 | 0.045776 | 0.32501 | 122.731 | 123.1476 | 122.9645 | 122.937 | 122.7631 | 123.1201 | 122.9919 | 122.5662 | 122.937 | 122.7631 | 122.9919 | 122.9645 | 123.1201 | -0.63629 | -0.50812
3826.1406 | 123.1934 | -122.8043 | 0.16937 | 0.061874 | 0.010493 | -0.012505 | 0.040883 | -0.020461 | -0.0099805 | 0.0081347 | -0.15106 | 0.068665 | -0.4303 | 0.027466 | 0.064087 | 0.10529 | -0.1236 | 0.24261 | 0.2655 | -0.31128 | 122.374 | -0.10071 | 122.6532 | 122.8317 | -0.10529 | 122.493 | 0.09613 | 0.27924 | 122.6807 | 123.0469 | 122.8683 | 122.8729 | 122.6532 | 123.0698 | 122.9095 | 122.493 | 122.8729 | 122.6532 | 122.9095 | 122.8683 | 123.0698 | -0.59967 | -0.48065
3827.9219 | 123.1155 | -122.8638 | 0.21057 | 0.1458 | 0.012629 | -0.0088738 | 0.045369 | -0.016829 | -0.014253 | 0.0098437 | -0.10529 | 0.064087 | -0.45776 | 0.068665 | 0.073242 | 0.11444 | -0.15564 | 0.25635 | 0.25177 | -0.30212 | 122.406 | -0.14648 | 122.7585 | 122.9324 | -0.13733 | 122.5616 | 0.041199 | 0.35248 | 122.7081 | 123.1201 | 122.937 | 122.9279 | 122.7585 | 123.1155 | 122.9782 | 122.5616 | 122.9279 | 122.7585 | 122.9782 | 122.937 | 123.1155 | -0.66834 | -0.5127
3829.625 | 123.0606 | -122.8638 | 0.21973 | -0.044937 | 0.0096387 | -0.009942 | 0.047719 | -0.018111 | -0.013826 | 0.0089893 | -0.13275 | 0.082397 | -0.48523 | 0.059509 | 0.022888 | 0.032043 | -0.036621 | 0.21515 | 0.26093 | -0.31586 | 122.3785 | -0.13733 | 122.731 | 122.9233 | -0.19684 | 122.5479 | 0.041198 | 0.35248 | 122.8271 | 123.0789 | 122.8867 | 122.9462 | 122.731 | 123.1247 | 122.8958 | 122.5479 | 122.9462 | 122.731 | 122.8958 | 122.8867 | 123.1247 | -0.70496 | -0.53558
3831.3906 | 123.0698 | -122.8592 | 0.21515 | 0.20683 | 0.012843 | -0.0016106 | 0.044728 | -0.018752 | -0.010835 | 0.0092029 | -0.082397 | 0.054932 | -0.42572 | 0.082397 | 0.10071 | 0.14191 | -0.19226 | 0.28381 | 0.24719 | -0.29755 | 122.4335 | -0.16022 | 122.7768 | 122.9416 | -0.11444 | 122.5616 | 0.032043 | 0.34332 | 122.6669 | 123.143 | 122.9599 | 122.9141 | 122.7768 | 123.1064 | 123.0011 | 122.5616 | 122.9141 | 122.7768 | 123.0011 | 122.9599 | 123.1064 | -0.64087 | -0.5127
3833.0938 | 123.1705 | -122.8271 | 0.17853 | -0.17464 | 0.0089979 | -0.0088738 | 0.040883 | -0.020461 | -0.014039 | 0.0096301 | -0.10529 | 0.068665 | -0.44403 | 0.10529 | 0.11902 | 0.1236 | -0.11444 | 0.31586 | 0.25177 | -0.30212 | 122.3831 | -0.10986 | 122.7219 | 122.9324 | -0.059509 | 122.525 | 0.073242 | 0.33875 | 122.7127 | 123.143 | 122.9462 | 122.8958 | 122.7219 | 123.0789 | 122.9507 | 122.525 | 122.8958 | 122.7219 | 122.9507 | 122.9462 | 123.0789 | -0.62256 | -0.48065
3834.8594 | 123.0927 | -122.8821 | 0.20599 | 0.11528 | 0.0098523 | -0.009942 | 0.043019 | -0.019393 | -0.010835 | 0.0087757 | -0.10529 | 0.036621 | -0.44403 | 0.068665 | 0.073242 | 0.1236 | -0.17853 | 0.27008 | 0.24261 | -0.30212 | 122.438 | -0.16937 | 122.7768 | 122.9507 | -0.13275 | 122.58 | 0.036621 | 0.33875 | 122.7036 | 123.1522 | 122.9553 | 122.9187 | 122.7768 | 123.1247 | 123.0057 | 122.58 | 122.9187 | 122.7768 | 123.0057 | 122.9553 | 123.1247 | -0.65003 | -0.50812
3836.625 | 123.1201 | -122.8409 | 0.21973 | 0.1458 | 0.013698 | -0.0056696 | 0.045797 | -0.016402 | -0.012758 | 0.011339 | -0.19684 | 0.10071 | -0.48523 | 0.004578 | -0.009155 | 0.013733 | -0.032043 | 0.15106 | 0.29297 | -0.35248 | 122.3557 | -0.11902 | 122.644 | 122.8455 | -0.22888 | 122.4884 | 0.073242 | 0.28839 | 122.8088 | 122.9919 | 122.8317 | 122.9416 | 122.644 | 123.1338 | 122.8546 | 122.4884 | 122.9416 | 122.644 | 122.8546 | 122.8317 | 123.1338 | -0.70496 | -0.57221
3838.375 | 123.111 | -122.8455 | 0.20599 | 0.16869 | 0.01028 | -0.0058832 | 0.045583 | -0.016829 | -0.01233 | 0.0096301 | -0.18768 | 0.082397 | -0.49439 | 0.013733 | 0.009155 | 0.036621 | -0.07782 | 0.18768 | 0.2655 | -0.29297 | 122.3511 | -0.1236 | 122.6578 | 122.8592 | -0.19684 | 122.5525 | 0.059509 | 0.3067 | 122.7676 | 123.0331 | 122.8546 | 122.9279 | 122.6578 | 123.111 | 122.8821 | 122.5525 | 122.9279 | 122.6578 | 122.8821 | 122.8546 | 123.111 | -0.70038 | -0.49896
3840.125 | 123.0789 | -122.8683 | 0.2243 | -0.083084 | 0.010921 | -0.0046014 | 0.046651 | -0.016188 | -0.015535 | 0.0077075 | -0.1236 | 0.082397 | -0.48981 | 0.032043 | 0.036621 | 0.064087 | -0.036621 | 0.2243 | 0.28839 | -0.31128 | 122.3785 | -0.14191 | 122.7448 | 122.9004 | -0.18768 | 122.5571 | 0.064087 | 0.36621 | 122.8317 | 123.0927 | 122.905 | 122.9507 | 122.7448 | 123.1567 | 122.9324 | 122.5571 | 122.9507 | 122.7448 | 122.9324 | 122.905 | 123.1567 | -0.71411 | -0.53558
3841.8438 | 123.1979 | -122.8271 | 0.1831 | -0.0067901 | 0.013057 | -0.008233 | 0.037465 | -0.01982 | -0.0099805 | 0.0079211 | -0.17853 | 0.07782 | -0.44861 | 0.032043 | 0.091553 | 0.09613 | -0.1236 | 0.27466 | 0.23804 | -0.31586 | 122.3785 | -0.10528 | 122.6486 | 122.8592 | -0.091552 | 122.5113 | 0.054932 | 0.27008 | 122.7036 | 123.1018 | 122.9187 | 122.905 | 122.6486 | 123.0652 | 122.9233 | 122.5113 | 122.905 | 122.6486 | 122.9233 | 122.9187 | 123.0652 | -0.63171 | -0.49896
3843.6094 | 123.1888 | -122.8226 | 0.16479 | 0.054245 | 0.012202 | -0.0043878 | 0.040029 | -0.018111 | -0.010835 | 0.0083483 | -0.14648 | 0.07782 | -0.45776 | 0.045776 | 0.059509 | 0.082397 | -0.091553 | 0.25177 | 0.25177 | -0.31128 | 122.3648 | -0.086975 | 122.6761 | 122.8683 | -0.10529 | 122.5113 | 0.086975 | 0.31128 | 122.731 | 123.0743 | 122.8821 | 122.9004 | 122.6761 | 123.0743 | 122.905 | 122.5113 | 122.9004 | 122.6761 | 122.905 | 122.8821 | 123.0743 | -0.62256 | -0.47607
3845.375 | 123.0835 | -122.8592 | 0.2243 | -0.067826 | 0.012416 | -0.0080194 | 0.04836 | -0.017043 | -0.014039 | 0.0098437 | -0.12817 | 0.082397 | -0.47607 | 0.018311 | 0 | 0.036621 | -0.022888 | 0.19684 | 0.28839 | -0.32501 | 122.3831 | -0.14191 | 122.731 | 122.8775 | -0.2243 | 122.5342 | 0.064087 | 0.3479 | 122.8363 | 123.056 | 122.8592 | 122.9416 | 122.731 | 123.1476 | 122.8958 | 122.5342 | 122.9416 | 122.731 | 122.8958 | 122.8592 | 123.1476 | -0.70038 | -0.54932
3847.125 | 123.0927 | -122.8638 | 0.21057 | -0.15175 | 0.011989 | -0.010369 | 0.046437 | -0.018325 | -0.015321 | 0.010271 | -0.16022 | 0.073242 | -0.48523 | 0.041199 | 0.027466 | 0.050354 | -0.004578 | 0.2243 | 0.28381 | -0.34332 | 122.3785 | -0.13733 | 122.7036 | 122.905 | -0.18311 | 122.5204 | 0.073242 | 0.32501 | 122.8592 | 123.0881 | 122.8912 | 122.937 | 122.7036 | 123.1476 | 122.9141 | 122.5204 | 122.937 | 122.7036 | 122.9141 | 122.8912 | 123.1476 | -0.6958 | -0.55389
3848.8281 | 123.111 | -122.8592 | 0.18768 | 0.1458 | 0.010921 | -0.0050286 | 0.042165 | -0.018538 | -0.010408 | 0.0083483 | -0.1236 | 0.064087 | -0.44403 | 0.041199 | 0.07782 | 0.10986 | -0.13733 | 0.25635 | 0.24719 | -0.30212 | 122.4152 | -0.1236 | 122.7356 | 122.9004 | -0.10986 | 122.5571 | 0.059509 | 0.32044 | 122.7219 | 123.1155 | 122.937 | 122.9233 | 122.7356 | 123.1064 | 122.9691 | 122.5571 | 122.9233 | 122.7356 | 122.9691 | 122.937 | 123.1064 | -0.63171 | -0.48981
3850.5938 | 123.0789 | -122.8821 | 0.21057 | 0.16106 | 0.010707 | -0.0035332 | 0.044728 | -0.017256 | -0.013185 | 0.0098437 | -0.09613 | 0.050354 | -0.4303 | 0.091553 | 0.091553 | 0.14191 | -0.1831 | 0.28381 | 0.2243 | -0.28839 | 122.4518 | -0.16022 | 122.7859 | 122.9736 | -0.11902 | 122.5937 | 0.013733 | 0.33417 | 122.699 | 123.1659 | 122.9736 | 122.9324 | 122.7859 | 123.1064 | 123.024 | 122.5937 | 122.9324 | 122.7859 | 123.024 | 122.9736 | 123.1064 | -0.64087 | -0.49896
3852.3594 | 123.1796 | -122.8134 | 0.19226 | -0.037308 | 0.0087841 | -0.0086602 | 0.037465 | -0.022383 | -0.010194 | 0.0070667 | -0.14648 | 0.091553 | -0.43945 | 0.064087 | 0.10071 | 0.12817 | -0.11902 | 0.29755 | 0.2655 | -0.32044 | 122.374 | -0.10071 | 122.6669 | 122.8775 | -0.091553 | 122.493 | 0.073242 | 0.29297 | 122.6944 | 123.111 | 122.9141 | 122.905 | 122.6669 | 123.0789 | 122.9416 | 122.493 | 122.905 | 122.6669 | 122.9416 | 122.9141 | 123.0789 | -0.63171 | -0.5127
3854.125 | 123.0743 | -122.9004 | 0.20599 | -0.12886 | 0.0089979 | -0.013787 | 0.049855 | -0.018111 | -0.010621 | 0.0085619 | -0.14191 | 0.073242 | -0.48065 | 0.045776 | 0.041199 | 0.054932 | -0.032043 | 0.21973 | 0.2655 | -0.32044 | 122.4197 | -0.13275 | 122.7585 | 122.9462 | -0.1648 | 122.58 | 0.059509 | 0.33875 | 122.8683 | 123.1201 | 122.9416 | 122.9736 | 122.7585 | 123.1659 | 122.9553 | 122.58 | 122.9736 | 122.7585 | 122.9553 | 122.9416 | 123.1659 | -0.68665 | -0.52643
3855.8281 | 123.1888 | -122.8271 | 0.21057 | -0.0067901 | 0.010493 | -0.014214 | 0.039388 | -0.01982 | -0.010835 | 0.0089893 | -0.16479 | 0.082397 | -0.44861 | 0.027466 | 0.059509 | 0.09613 | -0.10986 | 0.2655 | 0.24719 | -0.29755 | 122.3785 | -0.12817 | 122.6624 | 122.8546 | -0.15106 | 122.5296 | 0.036621 | 0.28381 | 122.7173 | 123.0927 | 122.8867 | 122.9095 | 122.6624 | 123.0743 | 122.9233 | 122.5296 | 122.9095 | 122.6624 | 122.9233 | 122.8867 | 123.0743 | -0.65918 | -0.50812
3857.5938 | 123.1155 | -122.8317 | 0.20599 | 0.11528 | 0.012202 | -0.0080194 | 0.049001 | -0.019606 | -0.012971 | 0.0094165 | -0.21057 | 0.09613 | -0.48523 | -0.032043 | -0.027466 | -0.009155 | -0.004578 | 0.13733 | 0.28839 | -0.31128 | 122.3465 | -0.10986 | 122.6212 | 122.7997 | -0.23346 | 122.5204 | 0.082397 | 0.27466 | 122.8271 | 122.9691 | 122.8043 | 122.9279 | 122.6212 | 123.1201 | 122.8226 | 122.5204 | 122.9279 | 122.6212 | 122.8226 | 122.8043 | 123.1201 | -0.69122 | -0.51727
3859.3438 | 123.1293 | -122.8546 | 0.21057 | 0.12291 | 0.010066 | -0.0058832 | 0.043019 | -0.017684 | -0.01468 | 0.010271 | -0.21057 | 0.09613 | -0.49896 | -0.018311 | -0.018311 | 0 | -0.022888 | 0.16479 | 0.29297 | -0.31128 | 122.3557 | -0.11444 | 122.644 | 122.8363 | -0.22888 | 122.5433 | 0.082398 | 0.28839 | 122.8317 | 123.0194 | 122.8363 | 122.9507 | 122.644 | 123.1476 | 122.8546 | 122.5433 | 122.9507 | 122.644 | 122.8546 | 122.8363 | 123.1476 | -0.70953 | -0.52185
3861.1094 | 123.1155 | -122.8455 | 0.19684 | 0.023727 | 0.012843 | -0.0063104 | 0.044515 | -0.016402 | -0.013826 | 0.0098437 | -0.21057 | 0.10986 | -0.50812 | -0.045776 | -0.041199 | -0.018311 | 0.004578 | 0.12817 | 0.29297 | -0.32959 | 122.3373 | -0.086975 | 122.6349 | 122.7997 | -0.23804 | 122.5159 | 0.096131 | 0.29755 | 122.85 | 122.9736 | 122.8043 | 122.9553 | 122.6349 | 123.1384 | 122.8271 | 122.5159 | 122.9553 | 122.6349 | 122.8271 | 122.8043 | 123.1384 | -0.70496 | -0.52643
3862.875 | 123.0835 | -122.8317 | 0.21515 | 0.13817 | 0.011348 | -0.0035332 | 0.042806 | -0.017043 | -0.011262 | 0.0094165 | -0.082397 | 0.064087 | -0.4303 | 0.068665 | 0.091553 | 0.14648 | -0.16479 | 0.28381 | 0.22888 | -0.29755 | 122.4014 | -0.15106 | 122.7493 | 122.9004 | -0.1236 | 122.5342 | 0.013733 | 0.3479 | 122.6669 | 123.1155 | 122.9233 | 122.8958 | 122.7493 | 123.0606 | 122.9782 | 122.5342 | 122.8958 | 122.7493 | 122.9782 | 122.9233 | 123.0606 | -0.64545 | -0.5127
3864.5781 | 123.2025 | -122.7951 | 0.1831 | -0.21278 | 0.011348 | -0.011865 | 0.043447 | -0.020247 | -0.013185 | 0.0081347 | -0.21515 | 0.10529 | -0.46234 | 0 | 0 | 0.027466 | 0.045776 | 0.19684 | 0.28839 | -0.32959 | 122.3328 | -0.077819 | 122.58 | 122.7951 | -0.1831 | 122.4655 | 0.10529 | 0.24719 | 122.8409 | 122.9919 | 122.7951 | 122.9004 | 122.58 | 123.0835 | 122.8226 | 122.4655 | 122.9004 | 122.58 | 122.8226 | 122.7951 | 123.0835 | -0.64545 | -0.5127
3866.3281 | 123.0789 | -122.8821 | 0.21057 | -0.083084 | 0.01028 | -0.01101 | 0.045369 | -0.018752 | -0.013612 | 0.012194 | -0.13275 | 0.10071 | -0.48065 | 0.036621 | 0.036621 | 0.054932 | -0.027466 | 0.2243 | 0.27008 | -0.31586 | 122.4014 | -0.10986 | 122.7493 | 122.9187 | -0.17395 | 122.5662 | 0.05951 | 0.3479 | 122.8546 | 123.1064 | 122.9187 | 122.9828 | 122.7493 | 123.1522 | 122.937 | 122.5662 | 122.9828 | 122.7493 | 122.937 | 122.9187 | 123.1522 | -0.69122 | -0.52643
3868.0938 | 123.1934 | -122.8638 | 0.18768 | -0.22804 | 0.010921 | -0.0046014 | 0.041951 | -0.018965 | -0.012544 | 0.0081347 | -0.10529 | 0.091553 | -0.44403 | 0.050354 | 0.07782 | 0.091553 | -0.032043 | 0.2655 | 0.26093 | -0.32501 | 122.4197 | -0.09613 | 122.7585 | 122.9141 | -0.10986 | 122.5388 | 0.073242 | 0.33875 | 122.8317 | 123.1293 | 122.9416 | 122.9553 | 122.7585 | 123.1247 | 122.9553 | 122.5388 | 122.9553 | 122.7585 | 122.9553 | 122.9416 | 123.1247 | -0.63171 | -0.5127
3869.7812 | 123.0927 | -122.8821 | 0.20142 | 0.16106 | 0.0096387 | -0.010156 | 0.042379 | -0.01747 | -0.012544 | 0.0070667 | -0.10529 | 0.068665 | -0.4303 | 0.07782 | 0.091553 | 0.13275 | -0.17853 | 0.27924 | 0.25177 | -0.30212 | 122.4518 | -0.13275 | 122.7768 | 122.9599 | -0.10986 | 122.58 | 0.050354 | 0.32501 | 122.7036 | 123.1613 | 122.9736 | 122.9507 | 122.7768 | 123.1338 | 123.0148 | 122.58 | 122.9507 | 122.7768 | 123.0148 | 122.9736 | 123.1338 | -0.63171 | -0.50354
3871.5625 | 123.1979 | -122.818 | 0.16022 | 0.00083945 | 0.011348 | -0.010796 | 0.039815 | -0.01982 | -0.010835 | 0.0087757 | -0.15564 | 0.086975 | -0.44403 | 0.041199 | 0.064087 | 0.086975 | -0.09613 | 0.25635 | 0.25177 | -0.32959 | 122.374 | -0.073242 | 122.6624 | 122.8592 | -0.09613 | 122.4884 | 0.091553 | 0.28839 | 122.7219 | 123.0743 | 122.8821 | 122.905 | 122.6624 | 123.0698 | 122.905 | 122.4884 | 122.905 | 122.6624 | 122.905 | 122.8821 | 123.0698 | -0.60425 | -0.48981
3873.2812 | 123.1659 | -122.8363 | 0.17395 | -0.16701 | 0.010066 | -0.0073786 | 0.039388 | -0.019606 | -0.011903 | 0.0055713 | -0.07782 | 0.064087 | -0.43945 | 0.10071 | 0.10529 | 0.13275 | -0.13275 | 0.33875 | 0.23346 | -0.30212 | 122.3969 | -0.10986 | 122.7585 | 122.937 | -0.068664 | 122.5342 | 0.059509 | 0.36163 | 122.7036 | 123.175 | 122.9416 | 122.9004 | 122.7585 | 123.0698 | 122.9691 | 122.5342 | 122.9004 | 122.7585 | 122.9691 | 122.9416 | 123.0698 | -0.6134 | -0.47607
3875.0469 | 123.1979 | -122.818 | 0.17853 | -0.0067901 | 0.0085705 | -0.0060968 | 0.04067 | -0.017684 | -0.011476 | 0.010912 | -0.15106 | 0.07782 | -0.4303 | 0.045776 | 0.073242 | 0.082397 | -0.11444 | 0.28381 | 0.24261 | -0.32044 | 122.3877 | -0.10071 | 122.6669 | 122.8638 | -0.10529 | 122.4976 | 0.064087 | 0.27924 | 122.7036 | 123.1018 | 122.8912 | 122.8958 | 122.6669 | 123.0606 | 122.9004 | 122.4976 | 122.8958 | 122.6669 | 122.9004 | 122.8912 | 123.0606 | -0.60883 | -0.49896
3876.7656 | 123.2025 | -122.8226 | 0.17395 | 0.031357 | 0.010707 | -0.0078058 | 0.042165 | -0.019179 | -0.0099805 | 0.0096301 | -0.13733 | 0.073242 | -0.44403 | 0.064087 | 0.091553 | 0.10071 | -0.11902 | 0.27466 | 0.27008 | -0.30212 | 122.3785 | -0.10071 | 122.6852 | 122.8867 | -0.082397 | 122.5204 | 0.096131 | 0.3067 | 122.7036 | 123.0972 | 122.9141 | 122.8958 | 122.6852 | 123.0927 | 122.9233 | 122.5204 | 122.8958 | 122.6852 | 122.9233 | 122.9141 | 123.0927 | -0.61798 | -0.47607
3878.5312 | 123.175 | -122.8271 | 0.18768 | -0.022049 | 0.0087841 | -0.010369 | 0.040242 | -0.017256 | -0.011476 | 0.0074939 | -0.15106 | 0.073242 | -0.46234 | 0.059509 | 0.07782 | 0.091553 | -0.10986 | 0.27924 | 0.26093 | -0.31128 | 122.3648 | -0.11444 | 122.6761 | 122.8867 | -0.10986 | 122.5159 | 0.073242 | 0.31128 | 122.7173 | 123.1064 | 122.905 | 122.9004 | 122.6761 | 123.0881 | 122.9187 | 122.5159 | 122.9004 | 122.6761 | 122.9187 | 122.905 | 123.0881 | -0.65002 | -0.49896
3880.2969 | 123.1567 | -122.8638 | 0.19226 | -0.15175 | 0.0089979 | -0.0093012 | 0.040883 | -0.020674 | -0.010835 | 0.0081347 | -0.091553 | 0.073242 | -0.43945 | 0.11444 | 0.11902 | 0.13275 | -0.13275 | 0.3479 | 0.25177 | -0.3067 | 122.4243 | -0.11902 | 122.7722 | 122.9782 | -0.073242 | 122.5571 | 0.059509 | 0.3479 | 122.731 | 123.2117 | 122.9828 | 122.937 | 122.7722 | 123.1155 | 122.9965 | 122.5571 | 122.937 | 122.7722 | 122.9965 | 122.9828 | 123.1155 | -0.63171 | -0.49896
3882.0625 | 123.1018 | -122.8546 | 0.19684 | -0.14412 | 0.010066 | -0.0035332 | 0.048787 | -0.01982 | -0.014894 | 0.0079211 | -0.1236 | 0.10529 | -0.48065 | 0.059509 | 0.032043 | 0.036621 | -0.022888 | 0.22888 | 0.28839 | -0.31586 | 122.374 | -0.091552 | 122.731 | 122.9141 | -0.1648 | 122.5388 | 0.091553 | 0.35706 | 122.8317 | 123.0835 | 122.8867 | 122.9599 | 122.731 | 123.143 | 122.8912 | 122.5388 | 122.9599 | 122.731 | 122.8912 | 122.8867 | 123.143 | -0.67749 | -0.5127
3883.7656 | 123.1613 | -122.8683 | 0.16937 | -0.1899 | 0.0089979 | -0.010156 | 0.039174 | -0.01982 | -0.012758 | 0.0094165 | -0.091553 | 0.073242 | -0.45319 | 0.11902 | 0.10986 | 0.13275 | -0.11444 | 0.33417 | 0.24719 | -0.31586 | 122.4152 | -0.096131 | 122.7768 | 122.9874 | -0.05951 | 122.5525 | 0.077819 | 0.36163 | 122.7539 | 123.2025 | 122.9782 | 122.9416 | 122.7768 | 123.1155 | 123.0011 | 122.5525 | 122.9416 | 122.7768 | 123.0011 | 122.9782 | 123.1155 | -0.62256 | -0.48523
3885.5312 | 123.1476 | -122.8317 | 0.18768 | -0.16701 | 0.0098523 | -0.0095148 | 0.04067 | -0.020034 | -0.013185 | 0.0077075 | -0.09613 | 0.059509 | -0.4303 | 0.13275 | 0.13733 | 0.16479 | -0.16022 | 0.35248 | 0.22888 | -0.31128 | 122.4014 | -0.12817 | 122.7356 | 122.9645 | -0.050354 | 122.5204 | 0.041199 | 0.33417 | 122.6715 | 123.1842 | 122.9691 | 122.8912 | 122.7356 | 123.0606 | 122.9965 | 122.5204 | 122.8912 | 122.7356 | 122.9965 | 122.9691 | 123.0606 | -0.61798 | -0.49896
3887.3125 | 123.0927 | -122.8546 | 0.1831 | 0.092392 | 0.011134 | -0.0058832 | 0.047078 | -0.016616 | -0.013185 | 0.0092029 | -0.15106 | 0.09613 | -0.47607 | 0.013733 | 0.004578 | 0.032043 | -0.07782 | 0.17853 | 0.27008 | -0.31586 | 122.3785 | -0.086975 | 122.7036 | 122.8683 | -0.17853 | 122.5388 | 0.086976 | 0.32501 | 122.7768 | 123.0331 | 122.8592 | 122.9507 | 122.7036 | 123.1247 | 122.8867 | 122.5388 | 122.9507 | 122.7036 | 122.8867 | 122.8592 | 123.1247 | -0.65918 | -0.49896
3889.0781 | 123.1247 | -122.8455 | 0.20142 | 0.11528 | 0.013484 | -0.010796 | 0.047292 | -0.016829 | -0.015748 | 0.0083483 | -0.1831 | 0.11444 | -0.47607 | -0.013733 | -0.022888 | 0.004578 | -0.009155 | 0.13275 | 0.28381 | -0.32501 | 122.3694 | -0.086975 | 122.6624 | 122.8317 | -0.2243 | 122.5204 | 0.082397 | 0.29297 | 122.8363 | 122.9782 | 122.8226 | 122.9599 | 122.6624 | 123.1293 | 122.85 | 122.5204 | 122.9599 | 122.6624 | 122.85 | 122.8226 | 123.1293 | -0.67749 | -0.52643
3890.7812 | 123.1659 | -122.8271 | 0.1831 | 0.069504 | 0.010066 | -0.0063104 | 0.038961 | -0.021743 | -0.0099805 | 0.0087757 | -0.15564 | 0.07782 | -0.42572 | 0.041199 | 0.068665 | 0.091553 | -0.13275 | 0.25635 | 0.24719 | -0.3067 | 122.4014 | -0.10528 | 122.6715 | 122.8683 | -0.11444 | 122.5204 | 0.064087 | 0.27008 | 122.6944 | 123.0835 | 122.8958 | 122.905 | 122.6715 | 123.0743 | 122.9187 | 122.5204 | 122.905 | 122.6715 | 122.9187 | 122.8958 | 123.0743 | -0.60882 | -0.48981
3892.5469 | 123.1247 | -122.8409 | 0.19684 | 0.13054 | 0.010066 | -0.0084466 | 0.047078 | -0.016616 | -0.01468 | 0.0079211 | -0.19226 | 0.09613 | -0.46234 | -0.013733 | 0.004578 | 0.018311 | -0.032043 | 0.15564 | 0.27924 | -0.33875 | 122.3785 | -0.10071 | 122.6486 | 122.8271 | -0.19226 | 122.5021 | 0.082398 | 0.27008 | 122.8088 | 122.9965 | 122.8455 | 122.937 | 122.6486 | 123.1201 | 122.8592 | 122.5021 | 122.937 | 122.6486 | 122.8592 | 122.8455 | 123.1201 | -0.65918 | -0.53558
3894.25 | 123.1842 | -122.8271 | 0.18768 | -0.1899 | 0.010921 | -0.0093012 | 0.046224 | -0.018965 | -0.015107 | 0.0096301 | -0.1831 | 0.11444 | -0.49896 | 0.013733 | 0.027466 | 0.032043 | 0.018311 | 0.20142 | 0.30212 | -0.32959 | 122.3282 | -0.073242 | 122.644 | 122.8409 | -0.16022 | 122.4976 | 0.11444 | 0.31586 | 122.8455 | 123.0286 | 122.8546 | 122.9416 | 122.644 | 123.1293 | 122.8592 | 122.4976 | 122.9416 | 122.644 | 122.8592 | 122.8546 | 123.1293 | -0.68664 | -0.51727
3896.0156 | 123.143 | -122.8455 | 0.1831 | 0.11528 | 0.012202 | -0.012078 | 0.038747 | -0.017897 | -0.011049 | 0.0096301 | -0.13275 | 0.086975 | -0.43488 | 0.041199 | 0.073242 | 0.11444 | -0.13733 | 0.23804 | 0.22888 | -0.31128 | 122.4106 | -0.09613 | 122.7127 | 122.8867 | -0.10986 | 122.5342 | 0.045777 | 0.30212 | 122.7081 | 123.0835 | 122.9187 | 122.9324 | 122.7127 | 123.0743 | 122.9599 | 122.5342 | 122.9324 | 122.7127 | 122.9599 | 122.9187 | 123.0743 | -0.61798 | -0.49438
3897.7344 | 123.1201 | -122.8455 | 0.20599 | 0.16869 | 0.010707 | -0.0054558 | 0.044515 | -0.018965 | -0.011476 | 0.0094165 | -0.18768 | 0.11902 | -0.48523 | -0.013733 | -0.022888 | 0.009155 | -0.018311 | 0.15564 | 0.27924 | -0.32501 | 122.3602 | -0.086975 | 122.6578 | 122.8317 | -0.22888 | 122.5204 | 0.073242 | 0.29755 | 122.8271 | 123.0011 | 122.8226 | 122.9645 | 122.6578 | 123.1247 | 122.8546 | 122.5204 | 122.9645 | 122.6578 | 122.8546 | 122.8226 | 123.1247 | -0.69122 | -0.53101
3899.4844 | 123.1247 | -122.8455 | 0.18768 | 0.16869 | 0.010921 | -0.008233 | 0.040242 | -0.018538 | -0.011903 | 0.0096301 | -0.10529 | 0.091553 | -0.4303 | 0.050354 | 0.07782 | 0.10986 | -0.14191 | 0.28381 | 0.24719 | -0.29755 | 122.4152 | -0.09613 | 122.7402 | 122.8958 | -0.10986 | 122.5479 | 0.059509 | 0.32501 | 122.7036 | 123.1293 | 122.9233 | 122.937 | 122.7402 | 123.0927 | 122.9553 | 122.5479 | 122.937 | 122.7402 | 122.9553 | 122.9233 | 123.0927 | -0.61798 | -0.48523
3901.25 | 123.1842 | -122.8134 | 0.1831 | -0.01442 | 0.0089979 | -0.0093012 | 0.037892 | -0.019179 | -0.0097669 | 0.0094165 | -0.14191 | 0.091553 | -0.43488 | 0.050354 | 0.086975 | 0.10529 | -0.11902 | 0.28839 | 0.24261 | -0.3067 | 122.3785 | -0.091552 | 122.6715 | 122.8638 | -0.09613 | 122.5067 | 0.05951 | 0.29297 | 122.6944 | 123.1018 | 122.9004 | 122.905 | 122.6715 | 123.056 | 122.9187 | 122.5067 | 122.905 | 122.6715 | 122.9187 | 122.9004 | 123.056 | -0.61798 | -0.48981
3903.0312 | 123.0881 | -122.8546 | 0.21515 | 0.10002 | 0.0092115 | -0.004815 | 0.043447 | -0.019393 | -0.012544 | 0.0096301 | -0.073242 | 0.082397 | -0.42114 | 0.073242 | 0.091553 | 0.1236 | -0.17853 | 0.27008 | 0.23804 | -0.3067 | 122.4335 | -0.13275 | 122.7814 | 122.9279 | -0.1236 | 122.5479 | 0.022888 | 0.3479 | 122.6761 | 123.1247 | 122.9462 | 122.937 | 122.7814 | 123.0927 | 122.9782 | 122.5479 | 122.937 | 122.7814 | 122.9782 | 122.9462 | 123.0927 | -0.63629 | -0.52185
3904.7344 | 123.1934 | -122.8088 | 0.19684 | -0.2433 | 0.01028 | -0.010369 | 0.046437 | -0.020888 | -0.014039 | 0.0077075 | -0.19226 | 0.12817 | -0.48065 | -0.013733 | -0.004578 | 0.013733 | 0.045776 | 0.19226 | 0.28839 | -0.33875 | 122.3282 | -0.068664 | 122.6166 | 122.7951 | -0.20142 | 122.4701 | 0.091553 | 0.28839 | 122.8546 | 123.0011 | 122.8043 | 122.937 | 122.6166 | 123.0972 | 122.8226 | 122.4701 | 122.937 | 122.6166 | 122.8226 | 122.8043 | 123.0972 | -0.67749 | -0.53558
3906.5 | 123.1842 | -122.8317 | 0.19684 | -0.25093 | 0.0087841 | -0.010583 | 0.042379 | -0.020034 | -0.012117 | 0.0072803 | -0.12817 | 0.086975 | -0.43945 | 0.064087 | 0.068665 | 0.091553 | -0.045776 | 0.26093 | 0.27924 | -0.32044 | 122.3923 | -0.10986 | 122.7036 | 122.8958 | -0.12817 | 122.5113 | 0.082398 | 0.31128 | 122.7859 | 123.0927 | 122.9004 | 122.9187 | 122.7036 | 123.111 | 122.9233 | 122.5113 | 122.9187 | 122.7036 | 122.9233 | 122.9004 | 123.111 | -0.63629 | -0.51727
3908.2812 | 123.1247 | -122.8546 | 0.21973 | 0.054245 | 0.010066 | -0.0067376 | 0.048574 | -0.016188 | -0.013399 | 0.010698 | -0.18768 | 0.11902 | -0.48523 | -0.022888 | -0.041199 | -0.022888 | 0.018311 | 0.12817 | 0.27924 | -0.32501 | 122.3694 | -0.10071 | 122.6669 | 122.8317 | -0.26093 | 122.5296 | 0.059509 | 0.29755 | 122.8729 | 122.9828 | 122.8134 | 122.9736 | 122.6669 | 123.1338 | 122.8317 | 122.5296 | 122.9736 | 122.6669 | 122.8317 | 122.8134 | 123.1338 | -0.70496 | -0.54474
3910.0312 | 123.0881 | -122.8455 | 0.21057 | -0.022049 | 0.010493 | -0.0060968 | 0.046865 | -0.018752 | -0.013612 | 0.0094165 | -0.13733 | 0.09613 | -0.4715 | 0.009155 | 0.009155 | 0.041199 | -0.018311 | 0.20599 | 0.27924 | -0.31128 | 122.374 | -0.11444 | 122.7081 | 122.8546 | -0.20142 | 122.5342 | 0.068665 | 0.33417 | 122.8271 | 123.0515 | 122.8546 | 122.9416 | 122.7081 | 123.1247 | 122.8867 | 122.5342 | 122.9416 | 122.7081 | 122.8867 | 122.8546 | 123.1247 | -0.68207 | -0.52185
3911.7188 | 123.1522 | -122.8134 | 0.19226 | -0.090714 | 0.0079297 | -0.013787 | 0.038106 | -0.019179 | -0.0099805 | 0.0068531 | -0.068665 | 0.082397 | -0.44403 | 0.11902 | 0.13733 | 0.16937 | -0.15564 | 0.35706 | 0.23346 | -0.29297 | 122.3694 | -0.10986 | 122.7448 | 122.9324 | -0.054932 | 122.5204 | 0.041198 | 0.37537 | 122.6578 | 123.1705 | 122.9507 | 122.8958 | 122.7448 | 123.0469 | 122.9828 | 122.5204 | 122.8958 | 122.7448 | 122.9828 | 122.9507 | 123.0469 | -0.63629 | -0.48523
3913.5 | 123.2071 | -122.818 | 0.18768 | -0.25093 | 0.0092115 | -0.0084466 | 0.044942 | -0.019606 | -0.013612 | 0.0081347 | -0.20599 | 0.10529 | -0.47607 | -0.022888 | 0.004578 | 0 | 0.059509 | 0.19684 | 0.28839 | -0.34332 | 122.3419 | -0.082397 | 122.612 | 122.7951 | -0.1831 | 122.4747 | 0.10071 | 0.27008 | 122.8775 | 123.0148 | 122.8226 | 122.9233 | 122.612 | 123.1064 | 122.818 | 122.4747 | 122.9233 | 122.612 | 122.818 | 122.8226 | 123.1064 | -0.66376 | -0.53101
3915.2031 | 123.2162 | -122.8088 | 0.16937 | -0.0067901 | 0.0079297 | -0.0071648 | 0.038747 | -0.018965 | -0.014467 | 0.0074939 | -0.16479 | 0.07782 | -0.44861 | 0.045776 | 0.091553 | 0.10529 | -0.11444 | 0.27924 | 0.27008 | -0.30212 | 122.3602 | -0.091553 | 122.644 | 122.8546 | -0.07782 | 122.5067 | 0.10071 | 0.28381 | 122.6944 | 123.0881 | 122.9004 | 122.8867 | 122.644 | 123.0789 | 122.9141 | 122.5067 | 122.8867 | 122.644 | 122.9141 | 122.9004 | 123.0789 | -0.61798 | -0.4715
3916.9531 | 123.1659 | -122.8363 | 0.17395 | -0.20515 | 0.011134 | -0.013574 | 0.039601 | -0.021315 | -0.012971 | 0.0064257 | -0.082397 | 0.054932 | -0.43945 | 0.10986 | 0.11444 | 0.15564 | -0.13733 | 0.33875 | 0.2243 | -0.3067 | 122.3969 | -0.11902 | 122.7539 | 122.9462 | -0.059509 | 122.5296 | 0.050354 | 0.35706 | 122.699 | 123.175 | 122.9507 | 122.8912 | 122.7539 | 123.0606 | 122.9919 | 122.5296 | 122.8912 | 122.7539 | 122.9919 | 122.9507 | 123.0606 | -0.6134 | -0.48065
3918.7188 | 123.0927 | -122.8729 | 0.20142 | 0.11528 | 0.0092115 | -0.0067376 | 0.044515 | -0.019606 | -0.01169 | 0.0085619 | -0.10529 | 0.045776 | -0.4303 | 0.068665 | 0.091553 | 0.1236 | -0.17853 | 0.27924 | 0.23346 | -0.30212 | 122.4426 | -0.15564 | 122.7676 | 122.9416 | -0.10986 | 122.5708 | 0.032043 | 0.32501 | 122.6944 | 123.1522 | 122.9645 | 122.9187 | 122.7676 | 123.1064 | 122.9965 | 122.5708 | 122.9187 | 122.7676 | 122.9965 | 122.9645 | 123.1064 | -0.63171 | -0.50354
3920.4219 | 123.0743 | -122.85 | 0.2243 | 0.15343 | 0.011348 | -0.0056696 | 0.046651 | -0.01982 | -0.01233 | 0.0068531 | -0.082397 | 0.064087 | -0.43945 | 0.082397 | 0.09613 | 0.13733 | -0.17853 | 0.29755 | 0.23346 | -0.3067 | 122.4106 | -0.16022 | 122.7676 | 122.9324 | -0.12817 | 122.5433 | 0.009155 | 0.35706 | 122.6715 | 123.1476 | 122.9462 | 122.9141 | 122.7676 | 123.0835 | 122.9874 | 122.5433 | 122.9141 | 122.7676 | 122.9874 | 122.9462 | 123.0835 | -0.66376 | -0.53101
3922.1875 | 123.2162 | -122.8134 | 0.1831 | -0.25093 | 0.010707 | -0.01101 | 0.042806 | -0.019393 | -0.012117 | 0.0087757 | -0.15564 | 0.11902 | -0.44403 | 0.004578 | 0.022888 | 0.027466 | 0.022888 | 0.21515 | 0.27466 | -0.34332 | 122.3694 | -0.064086 | 122.6578 | 122.818 | -0.16022 | 122.4701 | 0.091553 | 0.28839 | 122.8363 | 123.0286 | 122.8363 | 122.9324 | 122.6578 | 123.0881 | 122.8409 | 122.4701 | 122.9324 | 122.6578 | 122.8409 | 122.8363 | 123.0881 | -0.62714 | -0.52643
3923.8906 | 123.1201 | -122.8775 | 0.21973 | 0.10765 | 0.0096387 | -0.0050286 | 0.046437 | -0.018538 | -0.012758 | 0.0064257 | -0.21515 | 0.11902 | -0.48981 | -0.018311 | -0.018311 | 0.004578 | -0.018311 | 0.13733 | 0.28839 | -0.33875 | 122.3877 | -0.10071 | 122.6624 | 122.8592 | -0.23804 | 122.5388 | 0.068664 | 0.27466 | 122.8592 | 123.0148 | 122.8592 | 122.9965 | 122.6624 | 123.1659 | 122.8821 | 122.5388 | 122.9965 | 122.6624 | 122.8821 | 122.8592 | 123.1659 | -0.70953 | -0.55847
3925.6562 | 123.1384 | -122.8729 | 0.20142 | 0.10002 | 0.01028 | -0.010796 | 0.046865 | -0.016616 | -0.014467 | 0.0092029 | -0.17853 | 0.11444 | -0.48981 | -0.041199 | -0.022888 | -0.004578 | 0.004578 | 0.13733 | 0.29297 | -0.32501 | 122.3831 | -0.086975 | 122.6944 | 122.8317 | -0.2243 | 122.5479 | 0.091553 | 0.31128 | 122.8775 | 123.0103 | 122.85 | 122.9874 | 122.6944 | 123.1659 | 122.8683 | 122.5479 | 122.9874 | 122.6944 | 122.8683 | 122.85 | 123.1659 | -0.69122 | -0.52643
3927.4219 | 123.2208 | -122.8455 | 0.19226 | -0.28145 | 0.011775 | -0.009942 | 0.04131 | -0.018538 | -0.013399 | 0.0070667 | -0.15106 | 0.10986 | -0.48523 | -0.022888 | 0.013733 | 0.018311 | 0.022888 | 0.21057 | 0.28839 | -0.3479 | 122.3602 | -0.082398 | 122.6944 | 122.8226 | -0.17853 | 122.4976 | 0.09613 | 0.33417 | 122.8683 | 123.056 | 122.8592 | 122.9553 | 122.6944 | 123.1339 | 122.8638 | 122.4976 | 122.9553 | 122.6944 | 122.8638 | 122.8592 | 123.1339 | -0.67749 | -0.54016
3929.1719 | 123.1659 | -122.8455 | 0.16937 | -0.12123 | 0.0083569 | -0.0046014 | 0.037465 | -0.020247 | -0.011262 | 0.0085619 | -0.11444 | 0.073242 | -0.43945 | 0.10071 | 0.12817 | 0.14191 | -0.13733 | 0.32959 | 0.25635 | -0.30212 | 122.406 | -0.096131 | 122.731 | 122.9462 | -0.041199 | 122.5433 | 0.086975 | 0.32501 | 122.7081 | 123.175 | 122.9736 | 122.9187 | 122.731 | 123.1018 | 122.9874 | 122.5433 | 122.9187 | 122.731 | 122.9874 | 122.9736 | 123.1018 | -0.60883 | -0.4715
3930.9219 | 123.0927 | -122.8958 | 0.21515 | 0.17632 | 0.010493 | -0.0071648 | 0.044942 | -0.019179 | -0.013185 | 0.0085619 | -0.07782 | 0.064087 | -0.44403 | 0.073242 | 0.091553 | 0.13733 | -0.17395 | 0.28381 | 0.24261 | -0.29755 | 122.4518 | -0.15106 | 122.818 | 122.9691 | -0.1236 | 122.5983 | 0.027466 | 0.36621 | 122.7219 | 123.1796 | 122.9874 | 122.9599 | 122.818 | 123.1384 | 123.0331 | 122.5983 | 122.9599 | 122.818 | 123.0331 | 122.9874 | 123.1384 | -0.65918 | -0.5127
3932.625 | 123.0927 | -122.8683 | 0.20599 | -0.037308 | 0.01028 | -0.0067376 | 0.048574 | -0.017043 | -0.012971 | 0.0092029 | -0.12817 | 0.10071 | -0.50354 | 0 | -0.009155 | 0.032043 | -0.013733 | 0.18768 | 0.27924 | -0.33417 | 122.3648 | -0.10529 | 122.7402 | 122.8683 | -0.21515 | 122.5342 | 0.073242 | 0.37537 | 122.8546 | 123.056 | 122.8592 | 122.9691 | 122.7402 | 123.1476 | 122.9004 | 122.5342 | 122.9691 | 122.7402 | 122.9004 | 122.8592 | 123.1476 | -0.70953 | -0.54016
3934.3906 | 123.0927 | -122.85 | 0.19684 | 0.20683 | 0.011561 | -0.010369 | 0.044942 | -0.016616 | -0.013399 | 0.0092029 | -0.16022 | 0.10529 | -0.48065 | 0.018311 | 0.036621 | 0.059509 | -0.11902 | 0.20142 | 0.2655 | -0.3067 | 122.3694 | -0.091552 | 122.6898 | 122.8683 | -0.16022 | 122.5433 | 0.068665 | 0.32044 | 122.731 | 123.0515 | 122.8867 | 122.9553 | 122.6898 | 123.1155 | 122.9095 | 122.5433 | 122.9553 | 122.6898 | 122.9095 | 122.8867 | 123.1155 | -0.67749 | -0.50354
3936.1562 | 123.1338 | -122.8363 | 0.20142 | 0.077133 | 0.01028 | -0.011865 | 0.04067 | -0.016188 | -0.011476 | 0.0087757 | -0.1236 | 0.091553 | -0.43945 | 0.045776 | 0.059509 | 0.11444 | -0.12817 | 0.25635 | 0.23804 | -0.29297 | 122.3969 | -0.10986 | 122.7127 | 122.8821 | -0.14191 | 122.5433 | 0.036621 | 0.31586 | 122.7081 | 123.0927 | 122.8958 | 122.9279 | 122.7127 | 123.0743 | 122.9507 | 122.5433 | 122.9279 | 122.7127 | 122.9507 | 122.8958 | 123.0743 | -0.64087 | -0.49438
3937.8594 | 123.1338 | -122.8775 | 0.21973 | 0.069504 | 0.0081433 | -0.0056696 | 0.045369 | -0.016402 | -0.013185 | 0.0081347 | -0.17853 | 0.1236 | -0.48523 | -0.022888 | -0.027466 | 0.004578 | 0.009155 | 0.15106 | 0.28839 | -0.32501 | 122.3923 | -0.096131 | 122.699 | 122.8546 | -0.24719 | 122.5525 | 0.068664 | 0.3067 | 122.8867 | 123.0286 | 122.85 | 123.0011 | 122.699 | 123.1659 | 122.8821 | 122.5525 | 123.0011 | 122.699 | 122.8821 | 122.85 | 123.1659 | -0.70496 | -0.54474
3939.6094 | 123.1064 | -122.8638 | 0.21057 | 0.092392 | 0.011348 | -0.013787 | 0.044942 | -0.015761 | -0.013399 | 0.0070667 | -0.18768 | 0.11902 | -0.4715 | -0.018311 | -0.004578 | 0.018311 | -0.027466 | 0.16022 | 0.27924 | -0.32501 | 122.3923 | -0.091552 | 122.6761 | 122.8455 | -0.21515 | 122.5388 | 0.068665 | 0.28381 | 122.8363 | 123.024 | 122.8592 | 122.9828 | 122.6761 | 123.143 | 122.8821 | 122.5388 | 122.9828 | 122.6761 | 122.8821 | 122.8592 | 123.143 | -0.68207 | -0.53558
3941.3594 | 123.1338 | -122.8638 | 0.21057 | 0.00083945 | 0.011134 | -0.010369 | 0.045583 | -0.01512 | -0.012544 | 0.0094165 | -0.16022 | 0.1236 | -0.4715 | -0.032043 | -0.036621 | -0.004578 | 0.009155 | 0.13733 | 0.28381 | -0.32959 | 122.3923 | -0.086975 | 122.7036 | 122.8317 | -0.24719 | 122.5342 | 0.073242 | 0.31128 | 122.8729 | 123.0011 | 122.8271 | 122.9874 | 122.7036 | 123.1476 | 122.8592 | 122.5342 | 122.9874 | 122.7036 | 122.8592 | 122.8271 | 123.1476 | -0.68207 | -0.54016
3943.0625 | 123.175 | -122.8363 | 0.16479 | -0.098343 | 0.012843 | -0.0080194 | 0.037038 | -0.018965 | -0.012758 | 0.0077075 | -0.13275 | 0.07782 | -0.41199 | 0.082397 | 0.11444 | 0.13275 | -0.1236 | 0.3067 | 0.26093 | -0.31586 | 122.4243 | -0.086975 | 122.7036 | 122.9187 | -0.050354 | 122.5204 | 0.09613 | 0.27924 | 122.7127 | 123.143 | 122.9507 | 122.9141 | 122.7036 | 123.0972 | 122.9691 | 122.5204 | 122.9141 | 122.7036 | 122.9691 | 122.9507 | 123.0972 | -0.57678 | -0.48065
3944.8125 | 123.143 | -122.8455 | 0.1831 | 0.10765 | 0.0068615 | -0.009942 | 0.04131 | -0.018752 | -0.01233 | 0.0081347 | -0.12817 | 0.086975 | -0.43488 | 0.050354 | 0.073242 | 0.086975 | -0.12817 | 0.25635 | 0.24261 | -0.31586 | 122.4106 | -0.09613 | 122.7173 | 122.8958 | -0.10986 | 122.5296 | 0.05951 | 0.3067 | 122.7173 | 123.1018 | 122.9187 | 122.9324 | 122.7173 | 123.0881 | 122.9324 | 122.5296 | 122.9324 | 122.7173 | 122.9324 | 122.9187 | 123.0881 | -0.61798 | -0.49896
3946.5625 | 123.0789 | -122.8409 | 0.21057 | 0.22972 | 0.0098523 | -0.0084466 | 0.045797 | -0.018111 | -0.011476 | 0.0094165 | -0.1236 | 0.07782 | -0.46234 | 0.073242 | 0.091553 | 0.1236 | -0.15564 | 0.2655 | 0.23804 | -0.29755 | 122.3785 | -0.13275 | 122.7173 | 122.9141 | -0.11902 | 122.5433 | 0.027466 | 0.33875 | 122.6852 | 123.1064 | 122.9324 | 122.9187 | 122.7173 | 123.0789 | 122.9645 | 122.5433 | 122.9187 | 122.7173 | 122.9645 | 122.9324 | 123.0789 | -0.67291 | -0.50812
3948.3438 | 123.1842 | -122.8226 | 0.18768 | 0.038986 | 0.011775 | -0.0071648 | 0.038747 | -0.018965 | -0.011049 | 0.0077075 | -0.15106 | 0.086975 | -0.43488 | 0.022888 | 0.073242 | 0.091553 | -0.10986 | 0.2655 | 0.25177 | -0.32501 | 122.3877 | -0.10071 | 122.6715 | 122.8455 | -0.11444 | 122.4976 | 0.064087 | 0.28381 | 122.7127 | 123.0881 | 122.8958 | 122.9095 | 122.6715 | 123.0743 | 122.9141 | 122.4976 | 122.9095 | 122.6715 | 122.9141 | 122.8958 | 123.0743 | -0.62256 | -0.5127
3950.2031 | 123.1613 | -122.8317 | 0.1831 | -0.12123 | 0.010066 | -0.01101 | 0.039174 | -0.020034 | -0.011049 | 0.0079211 | -0.091553 | 0.086975 | -0.43945 | 0.09613 | 0.086975 | 0.13733 | -0.15106 | 0.33417 | 0.25177 | -0.3067 | 122.3923 | -0.09613 | 122.7402 | 122.9279 | -0.09613 | 122.525 | 0.068665 | 0.3479 | 122.6807 | 123.1659 | 122.9187 | 122.9187 | 122.7402 | 123.0835 | 122.9691 | 122.525 | 122.9187 | 122.7402 | 122.9691 | 122.9187 | 123.0835 | -0.62256 | -0.48981
3952.0156 | 123.111 | -122.8592 | 0.21515 | 0.13817 | 0.011561 | -0.0067376 | 0.046651 | -0.016616 | -0.011262 | 0.0094165 | -0.18768 | 0.09613 | -0.46692 | 0.018311 | -0.004578 | 0.036621 | -0.073242 | 0.19226 | 0.2655 | -0.32501 | 122.3923 | -0.11902 | 122.6715 | 122.8775 | -0.21973 | 122.5342 | 0.050354 | 0.27924 | 122.7859 | 123.0515 | 122.8546 | 122.9553 | 122.6715 | 123.1247 | 122.8958 | 122.5342 | 122.9553 | 122.6715 | 122.8958 | 122.8546 | 123.1247 | -0.68207 | -0.54016
3953.7188 | 123.0652 | -122.8638 | 0.21057 | 0.16869 | 0.0094251 | -0.011651 | 0.043447 | -0.017897 | -0.015107 | 0.010271 | -0.07782 | 0.082397 | -0.43945 | 0.09613 | 0.10071 | 0.14648 | -0.20599 | 0.27924 | 0.24719 | -0.29297 | 122.4243 | -0.12817 | 122.7859 | 122.9599 | -0.10986 | 122.5708 | 0.036621 | 0.36163 | 122.6578 | 123.143 | 122.9645 | 122.9462 | 122.7859 | 123.111 | 123.0103 | 122.5708 | 122.9462 | 122.7859 | 123.0103 | 122.9645 | 123.111 | -0.65002 | -0.50354
3955.4375 | 123.2071 | -122.8043 | 0.18768 | 0.046615 | 0.01028 | -0.0090874 | 0.039601 | -0.020461 | -0.011049 | 0.0066393 | -0.15106 | 0.07782 | -0.4303 | 0.036621 | 0.050354 | 0.082397 | -0.10986 | 0.24719 | 0.26093 | -0.3067 | 122.374 | -0.10986 | 122.6532 | 122.8409 | -0.13733 | 122.4976 | 0.073242 | 0.27924 | 122.6944 | 123.0515 | 122.8546 | 122.8821 | 122.6532 | 123.0652 | 122.8867 | 122.4976 | 122.8821 | 122.6532 | 122.8867 | 122.8546 | 123.0652 | -0.61798 | -0.49438
3957.1562 | 123.1659 | -122.8455 | 0.17395 | -0.17464 | 0.0096387 | -0.0084466 | 0.042592 | -0.021315 | -0.0099805 | 0.0059985 | -0.073242 | 0.082397 | -0.43488 | 0.09613 | 0.11902 | 0.16022 | -0.1236 | 0.33417 | 0.2655 | -0.29755 | 122.4106 | -0.091553 | 122.7722 | 122.9416 | -0.054931 | 122.5479 | 0.091553 | 0.36163 | 122.7219 | 123.1796 | 122.9645 | 122.9279 | 122.7722 | 123.111 | 123.0057 | 122.5479 | 122.9279 | 122.7722 | 123.0057 | 122.9645 | 123.111 | -0.60882 | -0.4715
3958.8906 | 123.1384 | -122.8821 | 0.19226 | 0.046615 | 0.010921 | -0.0071648 | 0.049855 | -0.016402 | -0.013826 | 0.0081347 | -0.14191 | 0.091553 | -0.48065 | -0.004578 | -0.027466 | 0 | 0.004578 | 0.15564 | 0.29755 | -0.33417 | 122.4014 | -0.10071 | 122.7402 | 122.8775 | -0.21973 | 122.5479 | 0.10528 | 0.33875 | 122.8867 | 123.0377 | 122.8546 | 122.9736 | 122.7402 | 123.1796 | 122.8821 | 122.5479 | 122.9736 | 122.7402 | 122.8821 | 122.8546 | 123.1796 | -0.67291 | -0.52643
3960.6406 | 123.1338 | -122.8592 | 0.17853 | 0.031357 | 0.0098523 | -0.015283 | 0.04601 | -0.017256 | -0.013612 | 0.0083483 | -0.18768 | 0.12817 | -0.47607 | -0.032043 | -0.032043 | -0.004578 | 0.022888 | 0.11902 | 0.27008 | -0.33875 | 122.3831 | -0.050354 | 122.6715 | 122.8271 | -0.21057 | 122.5204 | 0.091553 | 0.28839 | 122.8821 | 122.9782 | 122.8271 | 122.9874 | 122.6715 | 123.1293 | 122.8546 | 122.5204 | 122.9874 | 122.6715 | 122.8546 | 122.8271 | 123.1293 | -0.6546 | -0.51727
3962.3438 | 123.1384 | -122.8409 | 0.20599 | 0.17632 | 0.010066 | -0.009942 | 0.044942 | -0.017897 | -0.012971 | 0.010271 | -0.1831 | 0.10071 | -0.48523 | -0.022888 | -0.027466 | -0.004578 | -0.013733 | 0.14191 | 0.28381 | -0.32501 | 122.3557 | -0.10529 | 122.6578 | 122.818 | -0.23346 | 122.5159 | 0.077819 | 0.30212 | 122.8271 | 122.9828 | 122.8134 | 122.9416 | 122.6578 | 123.1247 | 122.8363 | 122.5159 | 122.9416 | 122.6578 | 122.8363 | 122.8134 | 123.1247 | -0.69122 | -0.53101
3964.0625 | 123.0835 | -122.8821 | 0.21057 | -0.098343 | 0.0089979 | -0.0078058 | 0.047078 | -0.018538 | -0.014894 | 0.0068531 | -0.13275 | 0.10986 | -0.46234 | 0.036621 | 0.036621 | 0.050354 | -0.036621 | 0.22888 | 0.27466 | -0.33875 | 122.4197 | -0.10071 | 122.7493 | 122.9187 | -0.17395 | 122.5433 | 0.064087 | 0.32959 | 122.8455 | 123.111 | 122.9187 | 122.9919 | 122.7493 | 123.1567 | 122.9324 | 122.5433 | 122.9919 | 122.7493 | 122.9324 | 122.9187 | 123.1567 | -0.67291 | -0.54932
3965.7656 | 123.1247 | -122.8363 | 0.19684 | 0.069504 | 0.011348 | -0.0067376 | 0.044515 | -0.017256 | -0.011049 | 0.0092029 | -0.16937 | 0.11902 | -0.46692 | -0.036621 | -0.022888 | 0.004578 | 0 | 0.14191 | 0.27466 | -0.33875 | 122.3694 | -0.077819 | 122.6669 | 122.7997 | -0.21973 | 122.4976 | 0.07782 | 0.29755 | 122.8363 | 122.9782 | 122.8134 | 122.9553 | 122.6669 | 123.111 | 122.8409 | 122.4976 | 122.9553 | 122.6669 | 122.8409 | 122.8134 | 123.111 | -0.66376 | -0.53558
3967.4688 | 123.0927 | -122.8729 | 0.19226 | 0.11528 | 0.0081433 | -0.0084466 | 0.039388 | -0.020888 | -0.011262 | 0.0096301 | -0.10986 | 0.073242 | -0.41199 | 0.059509 | 0.09613 | 0.12817 | -0.17853 | 0.27924 | 0.23804 | -0.29755 | 122.4609 | -0.11902 | 122.7631 | 122.9324 | -0.096131 | 122.5754 | 0.045776 | 0.30212 | 122.6944 | 123.1522 | 122.9691 | 122.9462 | 122.7631 | 123.111 | 123.0011 | 122.5754 | 122.9462 | 122.7631 | 123.0011 | 122.9691 | 123.111 | -0.60425 | -0.48981
3969.2031 | 123.1888 | -122.8363 | 0.17853 | -0.18227 | 0.010493 | -0.0095148 | 0.04601 | -0.018325 | -0.010621 | 0.0096301 | -0.17395 | 0.1236 | -0.45319 | -0.013733 | 0.013733 | 0.022888 | 0.032043 | 0.20142 | 0.27466 | -0.34332 | 122.3831 | -0.054932 | 122.6624 | 122.8226 | -0.16479 | 122.493 | 0.09613 | 0.27924 | 122.8683 | 123.0377 | 122.85 | 122.9599 | 122.6624 | 123.111 | 122.8592 | 122.493 | 122.9599 | 122.6624 | 122.8592 | 122.85 | 123.111 | -0.63171 | -0.52185
3970.9531 | 123.2117 | -122.8134 | 0.1831 | -0.28145 | 0.0098523 | -0.0078058 | 0.041524 | -0.019179 | -0.010621 | 0.0068531 | -0.12817 | 0.11444 | -0.42572 | 0.032043 | 0.050354 | 0.07782 | -0.009155 | 0.23804 | 0.26093 | -0.33875 | 122.3877 | -0.068664 | 122.6852 | 122.8455 | -0.13275 | 122.4747 | 0.07782 | 0.29755 | 122.8043 | 123.0515 | 122.8638 | 122.9279 | 122.6852 | 123.0743 | 122.8912 | 122.4747 | 122.9279 | 122.6852 | 122.8912 | 122.8638 | 123.0743 | -0.60882 | -0.52185
3972.6719 | 123.1934 | -122.8226 | 0.17853 | 0.069504 | 0.010066 | -0.0095148 | 0.039174 | -0.019179 | -0.011262 | 0.0081347 | -0.15106 | 0.086975 | -0.43488 | 0.036621 | 0.064087 | 0.091553 | -0.10529 | 0.24719 | 0.26093 | -0.29755 | 122.3877 | -0.091553 | 122.6715 | 122.8592 | -0.11444 | 122.525 | 0.082397 | 0.28381 | 122.7173 | 123.0698 | 122.8867 | 122.9095 | 122.6715 | 123.0835 | 122.9141 | 122.525 | 122.9095 | 122.6715 | 122.9141 | 122.8867 | 123.0835 | -0.6134 | -0.47607
3974.3906 | 123.1979 | -122.8134 | 0.17853 | 0.046615 | 0.012202 | -0.011224 | 0.04067 | -0.020034 | -0.012117 | 0.0074939 | -0.15564 | 0.10071 | -0.44861 | 0.032043 | 0.082397 | 0.086975 | -0.11444 | 0.27008 | 0.27924 | -0.31586 | 122.3648 | -0.07782 | 122.6578 | 122.8455 | -0.096131 | 122.4976 | 0.10071 | 0.29297 | 122.699 | 123.0835 | 122.8958 | 122.9141 | 122.6578 | 123.0927 | 122.9004 | 122.4976 | 122.9141 | 122.6578 | 122.9004 | 122.8958 | 123.0927 | -0.62714 | -0.49438
3976.0938 | 123.1247 | -122.8409 | 0.21057 | 0.17632 | 0.010921 | -0.010583 | 0.046651 | -0.017897 | -0.014467 | 0.0096301 | -0.16479 | 0.11444 | -0.48065 | -0.018311 | -0.027466 | -0.009155 | -0.018311 | 0.16479 | 0.28839 | -0.3479 | 122.3602 | -0.09613 | 122.6761 | 122.8226 | -0.23804 | 122.493 | 0.07782 | 0.31586 | 122.8226 | 123.0057 | 122.8134 | 122.9553 | 122.6761 | 123.1293 | 122.8317 | 122.493 | 122.9553 | 122.6761 | 122.8317 | 122.8134 | 123.1293 | -0.69122 | -0.55847
3977.8125 | 123.1476 | -122.8271 | 0.19684 | 0.092392 | 0.011561 | -0.012505 | 0.040242 | -0.01747 | -0.01233 | 0.0085619 | -0.10986 | 0.086975 | -0.43945 | 0.045776 | 0.059509 | 0.10529 | -0.13275 | 0.27466 | 0.25177 | -0.3067 | 122.3877 | -0.10986 | 122.7173 | 122.8729 | -0.13733 | 122.5204 | 0.054932 | 0.32959 | 122.6944 | 123.1018 | 122.8867 | 122.9141 | 122.7173 | 123.0789 | 122.9324 | 122.5204 | 122.9141 | 122.7173 | 122.9324 | 122.8867 | 123.0789 | -0.63629 | -0.50354
3979.5156 | 123.2117 | -122.8317 | 0.18768 | -0.25856 | 0.0089979 | -0.008233 | 0.045156 | -0.021315 | -0.01169 | 0.0074939 | -0.19684 | 0.12817 | -0.48981 | -0.009155 | -0.013733 | -0.009155 | 0.054932 | 0.18768 | 0.3067 | -0.32501 | 122.3419 | -0.059509 | 122.6349 | 122.8226 | -0.20142 | 122.5067 | 0.11902 | 0.29297 | 122.8867 | 123.0194 | 122.818 | 122.9599 | 122.6349 | 123.1384 | 122.8226 | 122.5067 | 122.9599 | 122.6349 | 122.8226 | 122.818 | 123.1384 | -0.67749 | -0.5127
3981.2344 | 123.2162 | -122.818 | 0.18768 | -0.21278 | 0.011561 | -0.013787 | 0.044088 | -0.019606 | -0.013185 | 0.0077075 | -0.1831 | 0.1236 | -0.47607 | -0.013733 | 0.004578 | 0 | 0.054932 | 0.20142 | 0.30212 | -0.3479 | 122.3419 | -0.064087 | 122.6349 | 122.8043 | -0.1831 | 122.4701 | 0.11444 | 0.29297 | 122.8729 | 123.0194 | 122.8226 | 122.9416 | 122.6349 | 123.1201 | 122.818 | 122.4701 | 122.9416 | 122.6349 | 122.818 | 122.8226 | 123.1201 | -0.66376 | -0.53558
3982.9375 | 123.2346 | -122.7859 | 0.18768 | -0.25093 | 0.0089979 | -0.011437 | 0.041951 | -0.020461 | -0.012758 | 0.0070667 | -0.19684 | 0.12817 | -0.46692 | -0.018311 | -0.013733 | -0.004578 | 0.059509 | 0.20599 | 0.28839 | -0.34332 | 122.319 | -0.059509 | 122.5891 | 122.7676 | -0.20142 | 122.4426 | 0.10071 | 0.27008 | 122.8455 | 122.9919 | 122.7722 | 122.9141 | 122.5891 | 123.0743 | 122.7814 | 122.4426 | 122.9141 | 122.5891 | 122.7814 | 122.7722 | 123.0743 | -0.6546 | -0.53101
3984.7031 | 123.1293 | -122.8317 | 0.20599 | 0.069504 | 0.01028 | -0.0097284 | 0.046437 | -0.019179 | -0.013185 | 0.0079211 | -0.17853 | 0.14191 | -0.47607 | -0.018311 | -0.013733 | -0.004578 | -0.022888 | 0.14648 | 0.28381 | -0.34332 | 122.3557 | -0.064087 | 122.6532 | 122.8134 | -0.21973 | 122.4884 | 0.077819 | 0.29755 | 122.8088 | 122.9782 | 122.818 | 122.9736 | 122.6532 | 123.1155 | 122.8271 | 122.4884 | 122.9736 | 122.6532 | 122.8271 | 122.818 | 123.1155 | -0.68207 | -0.54932
3986.4062 | 123.2025 | -122.8363 | 0.18768 | -0.25093 | 0.010921 | -0.0090874 | 0.043233 | -0.01982 | -0.012758 | 0.0081347 | -0.20599 | 0.13275 | -0.48523 | -0.013733 | 0.018311 | 0 | 0.068665 | 0.19226 | 0.29297 | -0.36163 | 122.3511 | -0.054932 | 122.6303 | 122.8226 | -0.16937 | 122.4747 | 0.10529 | 0.27924 | 122.905 | 123.0286 | 122.8546 | 122.9691 | 122.6303 | 123.1293 | 122.8363 | 122.4747 | 122.9691 | 122.6303 | 122.8363 | 122.8546 | 123.1293 | -0.67291 | -0.54932
3988.0938 | 123.1659 | -122.8592 | 0.18768 | -0.20515 | 0.0089979 | -0.010583 | 0.038961 | -0.018965 | -0.013185 | 0.0062121 | -0.07782 | 0.086975 | -0.43488 | 0.086975 | 0.11444 | 0.13275 | -0.11902 | 0.32501 | 0.23804 | -0.31128 | 122.4243 | -0.10071 | 122.7814 | 122.9462 | -0.073242 | 122.5479 | 0.050354 | 0.35706 | 122.7402 | 123.1842 | 122.9736 | 122.9462 | 122.7814 | 123.0972 | 122.9919 | 122.5479 | 122.9462 | 122.7814 | 122.9919 | 122.9736 | 123.0972 | -0.62256 | -0.49896
3989.7812 | 123.1613 | -122.8317 | 0.17853 | -0.12886 | 0.011134 | -0.01101 | 0.037252 | -0.018752 | -0.0097669 | 0.0089893 | -0.07782 | 0.082397 | -0.42114 | 0.10071 | 0.13275 | 0.15106 | -0.16022 | 0.34332 | 0.25177 | -0.30212 | 122.4106 | -0.096131 | 122.7539 | 122.9324 | -0.045777 | 122.5296 | 0.073242 | 0.34332 | 122.6715 | 123.175 | 122.9645 | 122.9141 | 122.7539 | 123.0835 | 122.9828 | 122.5296 | 122.9141 | 122.7539 | 122.9828 | 122.9645 | 123.0835 | -0.59967 | -0.48065
3991.5312 | 123.0789 | -122.8409 | 0.21057 | 0.20683 | 0.011561 | -0.006524 | 0.046651 | -0.018325 | -0.013612 | 0.0092029 | -0.13275 | 0.091553 | -0.45776 | 0.064087 | 0.068665 | 0.10529 | -0.15106 | 0.24719 | 0.27008 | -0.31128 | 122.3831 | -0.11902 | 122.7081 | 122.905 | -0.14191 | 122.5296 | 0.05951 | 0.32501 | 122.6898 | 123.0881 | 122.9095 | 122.9324 | 122.7081 | 123.111 | 122.9462 | 122.5296 | 122.9324 | 122.7081 | 122.9462 | 122.9095 | 123.111 | -0.66834 | -0.52185
3993.2031 | 123.1796 | -122.8409 | 0.18768 | -0.17464 | 0.010921 | -0.0093012 | 0.045583 | -0.020247 | -0.010621 | 0.0085619 | -0.15106 | 0.14648 | -0.46234 | 0.013733 | 0.018311 | 0.013733 | 0.027466 | 0.20599 | 0.28381 | -0.35248 | 122.3785 | -0.041199 | 122.6898 | 122.8546 | -0.16937 | 122.4884 | 0.09613 | 0.31128 | 122.8683 | 123.0469 | 122.8592 | 122.9874 | 122.6898 | 123.1247 | 122.8546 | 122.4884 | 122.9874 | 122.6898 | 122.8546 | 122.8592 | 123.1247 | -0.65002 | -0.54016
3994.9219 | 123.0789 | -122.8592 | 0.2243 | 0.15343 | 0.011561 | -0.0052422 | 0.045369 | -0.016616 | -0.013399 | 0.0083483 | -0.082397 | 0.10529 | -0.40741 | 0.091553 | 0.07782 | 0.13275 | -0.17853 | 0.27924 | 0.25177 | -0.28839 | 122.4518 | -0.11902 | 122.7768 | 122.9507 | -0.14648 | 122.5708 | 0.027466 | 0.32501 | 122.6807 | 123.1384 | 122.937 | 122.9645 | 122.7768 | 123.111 | 122.9919 | 122.5708 | 122.9645 | 122.7768 | 122.9919 | 122.937 | 123.111 | -0.63171 | -0.5127
3996.6094 | 123.1247 | -122.8363 | 0.21057 | 0.13054 | 0.0098523 | -0.0071648 | 0.048787 | -0.018111 | -0.012544 | 0.0092029 | -0.18768 | 0.11902 | -0.48065 | -0.022888 | -0.036621 | 0.013733 | -0.013733 | 0.14191 | 0.28839 | -0.34332 | 122.3557 | -0.091552 | 122.6486 | 122.8134 | -0.24719 | 122.493 | 0.07782 | 0.29297 | 122.8226 | 122.9782 | 122.7997 | 122.9553 | 122.6486 | 123.1247 | 122.85 | 122.493 | 122.9553 | 122.6486 | 122.85 | 122.7997 | 123.1247 | -0.69122 | -0.55389
3998.2969 | 123.0835 | -122.85 | 0.21515 | -0.090714 | 0.010493 | -0.011651 | 0.046224 | -0.019179 | -0.01233 | 0.0083483 | -0.1236 | 0.12817 | -0.48065 | 0.027466 | 0.032043 | 0.054932 | -0.050354 | 0.21973 | 0.28381 | -0.31586 | 122.3694 | -0.086975 | 122.7264 | 122.8775 | -0.18311 | 122.5342 | 0.068664 | 0.35706 | 122.7997 | 123.0698 | 122.8821 | 122.9782 | 122.7264 | 123.1338 | 122.905 | 122.5342 | 122.9782 | 122.7264 | 122.905 | 122.8821 | 123.1338 | -0.6958 | -0.53101
4000 | 123.0972 | -122.8592 | 0.20142 | 0.1992 | 0.013057 | -0.0071648 | 0.043874 | -0.01747 | -0.010408 | 0.0064257 | -0.15106 | 0.11444 | -0.45319 | 0.013733 | 0.032043 | 0.068665 | -0.11444 | 0.21057 | 0.25635 | -0.32044 | 122.406 | -0.086975 | 122.7081 | 122.8729 | -0.16937 | 122.5388 | 0.054932 | 0.30212 | 122.7448 | 123.0698 | 122.8912 | 122.9736 | 122.7081 | 123.1155 | 122.9279 | 122.5388 | 122.9736 | 122.7081 | 122.9279 | 122.8912 | 123.1155 | -0.6546 | -0.52185
4001.6875 | 123.0927 | -122.905 | 0.21057 | -0.037308 | 0.011989 | -0.006524 | 0.04601 | -0.016616 | -0.012971 | 0.0098437 | -0.13275 | 0.11902 | -0.46234 | 0.013733 | 0 | 0.022888 | -0.022888 | 0.20142 | 0.28839 | -0.33417 | 122.4426 | -0.091552 | 122.7722 | 122.9187 | -0.21057 | 122.5708 | 0.07782 | 0.32959 | 122.8821 | 123.1064 | 122.905 | 123.024 | 122.7722 | 123.1934 | 122.9279 | 122.5708 | 123.024 | 122.7722 | 122.9279 | 122.905 | 123.1934 | -0.67291 | -0.54474
4003.375 | 123.111 | -122.8546 | 0.21057 | 0.077133 | 0.011989 | -0.009942 | 0.046865 | -0.01747 | -0.015107 | 0.0072803 | -0.17395 | 0.12817 | -0.47607 | -0.032043 | -0.009155 | 0.013733 | 0.004578 | 0.15106 | 0.28839 | -0.32959 | 122.3785 | -0.082397 | 122.6807 | 122.8226 | -0.21973 | 122.525 | 0.07782 | 0.30212 | 122.8592 | 123.0057 | 122.8455 | 122.9828 | 122.6807 | 123.143 | 122.8683 | 122.525 | 122.9828 | 122.6807 | 122.8683 | 122.8455 | 123.143 | -0.68664 | -0.54016
4005.0625 | 123.1705 | -122.8638 | 0.19684 | -0.2433 | 0.010493 | -0.013146 | 0.036184 | -0.018325 | -0.0099805 | 0.0055713 | -0.082397 | 0.09613 | -0.4303 | 0.07782 | 0.1236 | 0.14648 | -0.1236 | 0.32501 | 0.26093 | -0.29755 | 122.4335 | -0.10071 | 122.7814 | 122.9416 | -0.073242 | 122.5662 | 0.064087 | 0.3479 | 122.7402 | 123.1888 | 122.9874 | 122.9599 | 122.7814 | 123.1247 | 123.0103 | 122.5662 | 122.9599 | 122.7814 | 123.0103 | 122.9874 | 123.1247 | -0.62714 | -0.49438
4006.7656 | 123.0835 | -122.8592 | 0.22888 | 0.13054 | 0.0085705 | -0.0073786 | 0.041097 | -0.016829 | -0.013185 | 0.0064257 | -0.073242 | 0.086975 | -0.42114 | 0.064087 | 0.086975 | 0.12817 | -0.17395 | 0.27924 | 0.23346 | -0.29755 | 122.438 | -0.14191 | 122.7859 | 122.9233 | -0.14191 | 122.5616 | 0.004577 | 0.3479 | 122.6852 | 123.1384 | 122.9462 | 122.9462 | 122.7859 | 123.0927 | 122.9874 | 122.5616 | 122.9462 | 122.7859 | 122.9874 | 122.9462 | 123.0927 | -0.65002 | -0.52643
4008.4531 | 123.1293 | -122.8409 | 0.1831 | 0.092392 | 0.01028 | -0.008233 | 0.047078 | -0.018325 | -0.013185 | 0.0079211 | -0.17395 | 0.13275 | -0.48065 | -0.013733 | -0.009155 | 0.018311 | -0.036621 | 0.16937 | 0.27924 | -0.33875 | 122.3602 | -0.050354 | 122.6669 | 122.8271 | -0.19226 | 122.5021 | 0.096131 | 0.3067 | 122.8043 | 123.0103 | 122.8317 | 122.9736 | 122.6669 | 123.1201 | 122.8592 | 122.5021 | 122.9736 | 122.6669 | 122.8592 | 122.8317 | 123.1201 | -0.66376 | -0.52185
4010.1406 | 123.1018 | -122.8821 | 0.20599 | -0.0067901 | 0.010921 | -0.0075922 | 0.045156 | -0.018965 | -0.013399 | 0.0087757 | -0.15106 | 0.11902 | -0.46234 | -0.009155 | -0.013733 | 0.013733 | -0.018311 | 0.16022 | 0.28839 | -0.33417 | 122.4197 | -0.086975 | 122.731 | 122.8729 | -0.21973 | 122.5479 | 0.082397 | 0.31128 | 122.8638 | 123.0423 | 122.8683 | 123.0011 | 122.731 | 123.1705 | 122.8958 | 122.5479 | 123.0011 | 122.731 | 122.8958 | 122.8683 | 123.1705 | -0.66834 | -0.54016
4011.8281 | 123.1888 | -122.8409 | 0.19226 | -0.17464 | 0.0096387 | -0.01101 | 0.043019 | -0.01982 | -0.015107 | 0.010912 | -0.17853 | 0.14191 | -0.46692 | -0.009155 | 0.004578 | 0.022888 | 0.032043 | 0.21057 | 0.30212 | -0.33875 | 122.374 | -0.050354 | 122.6624 | 122.8317 | -0.18768 | 122.5021 | 0.10986 | 0.28839 | 122.8729 | 123.0515 | 122.8455 | 122.9828 | 122.6624 | 123.143 | 122.8638 | 122.5021 | 122.9828 | 122.6624 | 122.8638 | 122.8455 | 123.143 | -0.65918 | -0.53101
4013.5156 | 123.1934 | -122.8317 | 0.17853 | -0.1899 | 0.0085705 | -0.0073786 | 0.041951 | -0.018111 | -0.01233 | 0.0089893 | -0.17853 | 0.13275 | -0.48523 | -0.022888 | -0.004578 | 0.013733 | 0.045776 | 0.21057 | 0.29297 | -0.33417 | 122.3465 | -0.045777 | 122.6532 | 122.8088 | -0.18311 | 122.4976 | 0.11444 | 0.3067 | 122.8775 | 123.0423 | 122.8271 | 122.9645 | 122.6532 | 123.1247 | 122.8455 | 122.4976 | 122.9645 | 122.6532 | 122.8455 | 122.8271 | 123.1247 | -0.66376 | -0.5127
4015.2031 | 123.1842 | -122.8317 | 0.1831 | 0.084762 | 0.011348 | -0.0084466 | 0.038747 | -0.018111 | -0.0099805 | 0.0081347 | -0.12817 | 0.10071 | -0.4303 | 0.036621 | 0.068665 | 0.082397 | -0.11444 | 0.23804 | 0.27008 | -0.31586 | 122.4014 | -0.082397 | 122.7036 | 122.8683 | -0.11444 | 122.5159 | 0.086976 | 0.30212 | 122.7173 | 123.0698 | 122.9004 | 122.9324 | 122.7036 | 123.1018 | 122.9141 | 122.5159 | 122.9324 | 122.7036 | 122.9141 | 122.9004 | 123.1018 | -0.6134 | -0.49896
4016.9375 | 123.1338 | -122.8409 | 0.21057 | 0.13817 | 0.012202 | -0.011865 | 0.046224 | -0.01982 | -0.013399 | 0.0098437 | -0.17395 | 0.11444 | -0.4715 | -0.022888 | -0.009155 | 0.013733 | -0.018311 | 0.14648 | 0.29297 | -0.32959 | 122.3694 | -0.09613 | 122.6669 | 122.818 | -0.21973 | 122.5113 | 0.082398 | 0.29755 | 122.8226 | 122.9874 | 122.8317 | 122.9553 | 122.6669 | 123.1338 | 122.8546 | 122.5113 | 122.9553 | 122.6669 | 122.8546 | 122.8317 | 123.1338 | -0.68207 | -0.54016
4018.625 | 123.1293 | -122.8821 | 0.21515 | 0.061874 | 0.010707 | -0.0084466 | 0.046437 | -0.016616 | -0.013612 | 0.0096301 | -0.17395 | 0.14191 | -0.46692 | -0.041199 | -0.018311 | -0.004578 | 0.022888 | 0.14191 | 0.28839 | -0.35248 | 122.4152 | -0.073242 | 122.7081 | 122.8409 | -0.23346 | 122.5296 | 0.073242 | 0.29297 | 122.905 | 123.024 | 122.8638 | 123.024 | 122.7081 | 123.1705 | 122.8775 | 122.5296 | 123.024 | 122.7081 | 122.8775 | 122.8638 | 123.1705 | -0.68207 | -0.56763
4020.3125 | 123.2162 | -122.818 | 0.18768 | -0.2433 | 0.0094251 | -0.0060968 | 0.042165 | -0.018965 | -0.0082715 | 0.0068531 | -0.20599 | 0.15106 | -0.47607 | -0.027466 | -0.009155 | -0.013733 | 0.059509 | 0.18768 | 0.28381 | -0.34332 | 122.3419 | -0.036621 | 122.612 | 122.7905 | -0.19684 | 122.4747 | 0.09613 | 0.27008 | 122.8775 | 123.0057 | 122.8088 | 122.9691 | 122.612 | 123.1018 | 122.8043 | 122.4747 | 122.9691 | 122.612 | 122.8043 | 122.8088 | 123.1018 | -0.66376 | -0.53101
4022 | 123.2071 | -122.8363 | 0.17395 | -0.28145 | 0.010921 | -0.0046014 | 0.038961 | -0.019179 | -0.012117 | 0.0081347 | -0.11902 | 0.10986 | -0.44403 | 0.022888 | 0.041199 | 0.054932 | 0.013733 | 0.23804 | 0.27466 | -0.34332 | 122.3923 | -0.064087 | 122.7173 | 122.8592 | -0.13275 | 122.493 | 0.10071 | 0.32501 | 122.85 | 123.0743 | 122.8775 | 122.9462 | 122.7173 | 123.111 | 122.8912 | 122.493 | 122.9462 | 122.7173 | 122.8912 | 122.8775 | 123.111 | -0.61798 | -0.51727
4023.6875 | 123.1613 | -122.8088 | 0.1831 | -0.15175 | 0.011134 | -0.012505 | 0.039815 | -0.01982 | -0.012544 | 0.0077075 | -0.064087 | 0.10529 | -0.42572 | 0.09613 | 0.1236 | 0.16937 | -0.14648 | 0.34332 | 0.24261 | -0.29297 | 122.3831 | -0.077819 | 122.7448 | 122.905 | -0.059509 | 122.5159 | 0.05951 | 0.36163 | 122.6624 | 123.1522 | 122.9324 | 122.9141 | 122.7448 | 123.0515 | 122.9782 | 122.5159 | 122.9141 | 122.7448 | 122.9782 | 122.9324 | 123.0515 | -0.60882 | -0.47607
4025.4531 | 123.0972 | -122.8638 | 0.19684 | 0.12291 | 0.0077161 | -0.012505 | 0.041951 | -0.019606 | -0.012117 | 0.0089893 | -0.068665 | 0.086975 | -0.40741 | 0.07782 | 0.09613 | 0.13733 | -0.17853 | 0.29297 | 0.25177 | -0.31128 | 122.4564 | -0.10986 | 122.7951 | 122.9416 | -0.10071 | 122.5525 | 0.054932 | 0.33874 | 122.6852 | 123.1567 | 122.9599 | 122.9507 | 122.7951 | 123.1155 | 123.0011 | 122.5525 | 122.9507 | 122.7951 | 123.0011 | 122.9599 | 123.1155 | -0.60425 | -0.50812
4027.1406 | 123.1064 | -122.8592 | 0.19684 | 0.10765 | 0.0094251 | -0.009942 | 0.045156 | -0.020034 | -0.013826 | 0.011339 | -0.17395 | 0.11444 | -0.47607 | -0.009155 | -0.004578 | 0.036621 | -0.054932 | 0.16937 | 0.27466 | -0.33875 | 122.3831 | -0.082397 | 122.6852 | 122.85 | -0.20142 | 122.5204 | 0.07782 | 0.30212 | 122.8043 | 123.0286 | 122.8546 | 122.9736 | 122.6852 | 123.1338 | 122.8958 | 122.5204 | 122.9736 | 122.6852 | 122.8958 | 122.8546 | 123.1338 | -0.67291 | -0.53558
4028.8438 | 123.175 | -122.8729 | 0.20142 | -0.1899 | 0.0092115 | -0.008233 | 0.038533 | -0.01982 | -0.013399 | 0.0066393 | -0.07782 | 0.086975 | -0.42572 | 0.09613 | 0.11902 | 0.14191 | -0.13275 | 0.34332 | 0.22888 | -0.3067 | 122.4472 | -0.11444 | 122.7951 | 122.9691 | -0.082397 | 122.5662 | 0.027466 | 0.3479 | 122.7402 | 123.2162 | 122.9919 | 122.9599 | 122.7951 | 123.1018 | 123.0148 | 122.5662 | 122.9599 | 122.7951 | 123.0148 | 122.9919 | 123.1018 | -0.62714 | -0.50812
4030.5312 | 123.2208 | -122.8043 | 0.16937 | 0.054245 | 0.0089979 | -0.0086602 | 0.041524 | -0.019179 | -0.01169 | 0.0072803 | -0.13733 | 0.10986 | -0.42572 | 0.036621 | 0.068665 | 0.07782 | -0.10529 | 0.26093 | 0.25635 | -0.32044 | 122.3785 | -0.05951 | 122.6669 | 122.8409 | -0.10071 | 122.4838 | 0.086975 | 0.28839 | 122.699 | 123.0652 | 122.8729 | 122.9141 | 122.6669 | 123.0606 | 122.8821 | 122.4838 | 122.9141 | 122.6669 | 122.8821 | 122.8729 | 123.0606 | -0.59509 | -0.48981
4032.2188 | 123.1979 | -122.7997 | 0.1831 | -0.16701 | 0.010707 | -0.0080194 | 0.047719 | -0.018965 | -0.012117 | 0.0074939 | -0.16937 | 0.1236 | -0.4715 | 0.013733 | 0.004578 | 0.004578 | 0.036621 | 0.20142 | 0.31128 | -0.34332 | 122.3282 | -0.059509 | 122.6303 | 122.8134 | -0.17853 | 122.4564 | 0.12817 | 0.30212 | 122.8363 | 123.0011 | 122.8043 | 122.9233 | 122.6303 | 123.111 | 122.8043 | 122.4564 | 122.9233 | 122.6303 | 122.8043 | 122.8043 | 123.111 | -0.6546 | -0.52643
4033.9688 | 123.111 | -122.85 | 0.20142 | 0.1458 | 0.011561 | -0.0063104 | 0.047078 | -0.017684 | -0.012758 | 0.0092029 | -0.16479 | 0.13275 | -0.45776 | 0.022888 | 0 | 0.032043 | -0.082397 | 0.17853 | 0.28381 | -0.34332 | 122.3923 | -0.068665 | 122.6852 | 122.8729 | -0.20142 | 122.5067 | 0.082397 | 0.29297 | 122.7676 | 123.0286 | 122.85 | 122.9828 | 122.6852 | 123.1338 | 122.8821 | 122.5067 | 122.9828 | 122.6852 | 122.8821 | 122.85 | 123.1338 | -0.65918 | -0.54474
4035.6719 | 123.056 | -122.8546 | 0.20599 | 0.22209 | 0.011134 | -0.0054558 | 0.041951 | -0.017684 | -0.011476 | 0.0081347 | -0.045776 | 0.09613 | -0.42114 | 0.082397 | 0.10071 | 0.13733 | -0.19226 | 0.30212 | 0.25177 | -0.3067 | 122.4335 | -0.10986 | 122.8088 | 122.937 | -0.10529 | 122.5479 | 0.045776 | 0.37537 | 122.6624 | 123.1567 | 122.9553 | 122.9507 | 122.8088 | 123.1064 | 122.9919 | 122.5479 | 122.9507 | 122.8088 | 122.9919 | 122.9553 | 123.1064 | -0.62714 | -0.5127
4037.3594 | 123.2117 | -122.8134 | 0.1831 | -0.2433 | 0.0092115 | -0.01101 | 0.043447 | -0.021743 | -0.011476 | 0.0087757 | -0.18768 | 0.13733 | -0.48065 | -0.013733 | 0.004578 | -0.004578 | 0.059509 | 0.1831 | 0.28839 | -0.34332 | 122.3328 | -0.045776 | 122.6257 | 122.7997 | -0.17853 | 122.4701 | 0.10529 | 0.29297 | 122.8729 | 122.9965 | 122.818 | 122.9507 | 122.6257 | 123.1018 | 122.8088 | 122.4701 | 122.9507 | 122.6257 | 122.8088 | 122.818 | 123.1018 | -0.66376 | -0.52643
4039.0625 | 123.2117 | -122.8271 | 0.17853 | -0.25093 | 0.0085705 | -0.0093012 | 0.041097 | -0.020247 | -0.013612 | 0.0098437 | -0.20599 | 0.11444 | -0.47607 | -0.022888 | 0 | -0.004578 | 0.059509 | 0.18768 | 0.30212 | -0.35248 | 122.3511 | -0.064087 | 122.6212 | 122.8043 | -0.17853 | 122.4747 | 0.1236 | 0.27008 | 122.8867 | 123.0148 | 122.8271 | 122.9416 | 122.6212 | 123.1293 | 122.8226 | 122.4747 | 122.9416 | 122.6212 | 122.8226 | 122.8271 | 123.1293 | -0.6546 | -0.53101
4040.75 | 123.1705 | -122.818 | 0.1831 | -0.15938 | 0.010066 | -0.012719 | 0.04131 | -0.020461 | -0.011262 | 0.0059985 | -0.086975 | 0.086975 | -0.42114 | 0.073242 | 0.10071 | 0.11444 | -0.10986 | 0.32044 | 0.2655 | -0.31586 | 122.3969 | -0.09613 | 122.731 | 122.8912 | -0.082397 | 122.5021 | 0.082398 | 0.33417 | 122.7081 | 123.1384 | 122.9187 | 122.905 | 122.731 | 123.0835 | 122.9324 | 122.5021 | 122.905 | 122.731 | 122.9324 | 122.9187 | 123.0835 | -0.60425 | -0.49896
4042.4375 | 123.2162 | -122.8271 | 0.1831 | 0.023727 | 0.0092115 | -0.011224 | 0.038961 | -0.018111 | -0.010408 | 0.0085619 | -0.15106 | 0.10986 | -0.41657 | 0.036621 | 0.068665 | 0.082397 | -0.10529 | 0.25635 | 0.2655 | -0.28839 | 122.4106 | -0.073242 | 122.6761 | 122.8638 | -0.11444 | 122.5388 | 0.082398 | 0.2655 | 122.7219 | 123.0835 | 122.8958 | 122.937 | 122.6761 | 123.0927 | 122.9095 | 122.5388 | 122.937 | 122.6761 | 122.9095 | 122.8958 | 123.0927 | -0.59967 | -0.4715
4044.125 | 123.2071 | -122.8226 | 0.16022 | 0.031357 | 0.0083569 | -0.0095148 | 0.041738 | -0.01747 | -0.012758 | 0.0074939 | -0.12817 | 0.091553 | -0.44861 | 0.027466 | 0.054932 | 0.086975 | -0.11444 | 0.25635 | 0.24719 | -0.32044 | 122.374 | -0.068664 | 122.6944 | 122.85 | -0.10528 | 122.5021 | 0.086975 | 0.32043 | 122.7081 | 123.0789 | 122.8775 | 122.9141 | 122.6944 | 123.0698 | 122.9095 | 122.5021 | 122.9141 | 122.6944 | 122.9095 | 122.8775 | 123.0698 | -0.60882 | -0.48065
4045.8125 | 123.0652 | -122.8683 | 0.19684 | 0.18394 | 0.0098523 | -0.0075922 | 0.045583 | -0.017256 | -0.0099805 | 0.0077075 | -0.059509 | 0.091553 | -0.43488 | 0.09613 | 0.10071 | 0.14648 | -0.19684 | 0.28381 | 0.24261 | -0.29297 | 122.4335 | -0.10529 | 122.8088 | 122.9645 | -0.09613 | 122.5754 | 0.045777 | 0.37537 | 122.6715 | 123.1522 | 122.9691 | 122.9599 | 122.8088 | 123.111 | 123.0148 | 122.5754 | 122.9599 | 122.8088 | 123.0148 | 122.9691 | 123.111 | -0.63171 | -0.48981
4047.5312 | 123.1613 | -122.8638 | 0.21057 | -0.23567 | 0.0081433 | -0.010796 | 0.040883 | -0.023238 | -0.01233 | 0.0096301 | -0.073242 | 0.091553 | -0.4303 | 0.10986 | 0.09613 | 0.12817 | -0.1236 | 0.33417 | 0.24719 | -0.31128 | 122.4335 | -0.11902 | 122.7905 | 122.9736 | -0.11444 | 122.5525 | 0.036621 | 0.35706 | 122.7402 | 123.1979 | 122.9599 | 122.9553 | 122.7905 | 123.111 | 122.9919 | 122.5525 | 122.9553 | 122.7905 | 122.9919 | 122.9599 | 123.111 | -0.64087 | -0.52185
4049.2188 | 123.2071 | -122.8271 | 0.16937 | 0.0084684 | 0.0092115 | -0.012719 | 0.039388 | -0.021102 | -0.012117 | 0.0074939 | -0.14191 | 0.10529 | -0.43945 | 0.036621 | 0.068665 | 0.091553 | -0.10529 | 0.25177 | 0.26093 | -0.3067 | 122.3877 | -0.064087 | 122.6852 | 122.8638 | -0.10071 | 122.5204 | 0.091552 | 0.29755 | 122.7219 | 123.0789 | 122.8958 | 122.9324 | 122.6852 | 123.0881 | 122.9187 | 122.5204 | 122.9324 | 122.6852 | 122.9187 | 122.8958 | 123.0881 | -0.60883 | -0.47607
4050.9062 | 123.1247 | -122.8546 | 0.20599 | 0.077133 | 0.011348 | -0.0050286 | 0.046865 | -0.019606 | -0.013399 | 0.0074939 | -0.17395 | 0.13733 | -0.48523 | -0.018311 | -0.018311 | -0.027466 | -0.022888 | 0.14648 | 0.28381 | -0.33417 | 122.3694 | -0.068665 | 122.6807 | 122.8363 | -0.22431 | 122.5204 | 0.077819 | 0.31128 | 122.8317 | 123.0011 | 122.8363 | 122.9919 | 122.6807 | 123.1384 | 122.8271 | 122.5204 | 122.9919 | 122.6807 | 122.8271 | 122.8363 | 123.1384 | -0.69122 | -0.54016
4052.5781 | 123.2025 | -122.818 | 0.1831 | -0.029679 | 0.0098523 | -0.010796 | 0.040883 | -0.021102 | -0.010408 | 0.0072803 | -0.1236 | 0.11444 | -0.43488 | 0.073242 | 0.091553 | 0.11902 | -0.13733 | 0.30212 | 0.24719 | -0.31586 | 122.3831 | -0.068664 | 122.6944 | 122.8912 | -0.091552 | 122.5021 | 0.064087 | 0.31128 | 122.6807 | 123.1201 | 122.9095 | 122.9324 | 122.6944 | 123.0652 | 122.937 | 122.5021 | 122.9324 | 122.6944 | 122.937 | 122.9095 | 123.0652 | -0.61798 | -0.49896
4054.2656 | 123.143 | -122.8592 | 0.19684 | 0.16869 | 0.011561 | -0.0078058 | 0.048146 | -0.019179 | -0.013185 | 0.0068531 | -0.16479 | 0.13275 | -0.49896 | -0.022888 | -0.022888 | -0.004578 | -0.013733 | 0.15106 | 0.31586 | -0.33417 | 122.3602 | -0.064087 | 122.6944 | 122.8363 | -0.21973 | 122.525 | 0.11902 | 0.33417 | 122.8455 | 123.0103 | 122.8363 | 122.9919 | 122.6944 | 123.175 | 122.8546 | 122.525 | 122.9919 | 122.6944 | 122.8546 | 122.8363 | 123.175 | -0.6958 | -0.531
4056 | 123.2483 | -122.8363 | 0.18768 | -0.22041 | 0.011775 | -0.011224 | 0.043874 | -0.020674 | -0.012758 | 0.0064257 | -0.19226 | 0.14648 | -0.46234 | -0.013733 | 0.004578 | -0.004578 | 0.059509 | 0.20142 | 0.28839 | -0.36163 | 122.374 | -0.041199 | 122.644 | 122.8226 | -0.1831 | 122.4747 | 0.10071 | 0.27008 | 122.8958 | 123.0377 | 122.8409 | 122.9828 | 122.644 | 123.1247 | 122.8317 | 122.4747 | 122.9828 | 122.644 | 122.8317 | 122.8409 | 123.1247 | -0.65002 | -0.54932
4057.6875 | 123.175 | -122.8271 | 0.1831 | -0.15938 | 0.0096387 | -0.0080194 | 0.039601 | -0.020247 | -0.010835 | 0.0074939 | -0.07782 | 0.10986 | -0.41199 | 0.10986 | 0.10071 | 0.13275 | -0.10529 | 0.31586 | 0.25177 | -0.29755 | 122.4152 | -0.073242 | 122.7493 | 122.937 | -0.082397 | 122.5296 | 0.068665 | 0.33417 | 122.7219 | 123.143 | 122.9279 | 122.937 | 122.7493 | 123.0789 | 122.9599 | 122.5296 | 122.937 | 122.7493 | 122.9599 | 122.9279 | 123.0789 | -0.59509 | -0.48065
4059.375 | 123.1247 | -122.8775 | 0.21057 | 0.077133 | 0.013484 | -0.003106 | 0.049001 | -0.016829 | -0.014039 | 0.0087757 | -0.14191 | 0.14648 | -0.46692 | -0.018311 | -0.045776 | -0.004578 | -0.009155 | 0.14191 | 0.29755 | -0.33417 | 122.4106 | -0.064087 | 122.7356 | 122.8592 | -0.25635 | 122.5433 | 0.086975 | 0.32501 | 122.8683 | 123.0194 | 122.8317 | 123.024 | 122.7356 | 123.175 | 122.8729 | 122.5433 | 123.024 | 122.7356 | 122.8729 | 122.8317 | 123.175 | -0.67749 | -0.54474
4061.0781 | 123.1201 | -122.8271 | 0.20142 | 0.054245 | 0.012416 | -0.0078058 | 0.047506 | -0.017043 | -0.014039 | 0.0074939 | -0.1831 | 0.13275 | -0.46234 | -0.022888 | -0.027466 | -0.013733 | 0.009155 | 0.12817 | 0.27924 | -0.33417 | 122.3648 | -0.068665 | 122.644 | 122.8043 | -0.22888 | 122.493 | 0.07782 | 0.27924 | 122.8363 | 122.9553 | 122.7997 | 122.9599 | 122.644 | 123.1064 | 122.8134 | 122.493 | 122.9599 | 122.644 | 122.8134 | 122.7997 | 123.1064 | -0.66376 | -0.53558
4062.7969 | 123.1064 | -122.8775 | 0.21515 | -0.14412 | 0.0070751 | -0.0088738 | 0.047078 | -0.017256 | -0.014467 | 0.0089893 | -0.12817 | 0.12817 | -0.45776 | 0.022888 | 0.041199 | 0.050354 | -0.009155 | 0.2243 | 0.28839 | -0.32501 | 122.4197 | -0.086975 | 122.7493 | 122.9004 | -0.17395 | 122.5525 | 0.073242 | 0.32959 | 122.8683 | 123.1018 | 122.9187 | 123.0057 | 122.7493 | 123.1659 | 122.9279 | 122.5525 | 123.0057 | 122.7493 | 122.9279 | 122.9187 | 123.1659 | -0.67291 | -0.54016
4064.5 | 123.1567 | -122.8546 | 0.21057 | -0.16701 | 0.012629 | -0.008233 | 0.04131 | -0.019393 | -0.012758 | 0.0094165 | -0.13733 | 0.11444 | -0.47607 | 0.018311 | 0.064087 | 0.045776 | -0.009155 | 0.22888 | 0.28839 | -0.32044 | 122.3785 | -0.09613 | 122.7173 | 122.8729 | -0.14648 | 122.5342 | 0.07782 | 0.33874 | 122.8455 | 123.0835 | 122.9187 | 122.9691 | 122.7173 | 123.143 | 122.9004 | 122.5342 | 122.9691 | 122.7173 | 122.9004 | 122.9187 | 123.143 | -0.68664 | -0.53101
4066.2031 | 123.1613 | -122.8455 | 0.17395 | -0.12886 | 0.010707 | -0.011651 | 0.036824 | -0.018965 | -0.010621 | 0.0081347 | -0.082397 | 0.10529 | -0.43945 | 0.082397 | 0.13275 | 0.15106 | -0.15564 | 0.3479 | 0.26093 | -0.28839 | 122.406 | -0.068664 | 122.7631 | 122.9279 | -0.041199 | 122.5571 | 0.086975 | 0.35706 | 122.6898 | 123.1934 | 122.9782 | 122.9507 | 122.7631 | 123.1064 | 122.9965 | 122.5571 | 122.9507 | 122.7631 | 122.9965 | 122.9782 | 123.1064 | -0.6134 | -0.46234
4067.9375 | 123.0835 | -122.8867 | 0.21057 | -0.075455 | 0.01028 | -0.0084466 | 0.046865 | -0.018752 | -0.013826 | 0.0057849 | -0.10986 | 0.12817 | -0.4715 | 0.027466 | 0.059509 | 0.064087 | -0.045776 | 0.23804 | 0.28839 | -0.3067 | 122.4152 | -0.082397 | 122.7768 | 122.9141 | -0.15106 | 122.58 | 0.07782 | 0.36163 | 122.8409 | 123.1247 | 122.9462 | 123.0148 | 122.7768 | 123.175 | 122.9507 | 122.58 | 123.0148 | 122.7768 | 122.9507 | 122.9462 | 123.175 | -0.68207 | -0.51727
4069.6406 | 123.1705 | -122.8317 | 0.17395 | -0.090714 | 0.0079297 | -0.0097284 | 0.039815 | -0.018325 | -0.010194 | 0.0064257 | -0.10986 | 0.11444 | -0.42114 | 0.07782 | 0.11902 | 0.15564 | -0.13733 | 0.32959 | 0.25635 | -0.31586 | 122.4106 | -0.059509 | 122.7219 | 122.9095 | -0.054931 | 122.5159 | 0.082398 | 0.31128 | 122.6944 | 123.1613 | 122.9507 | 122.9462 | 122.7219 | 123.0881 | 122.9874 | 122.5159 | 122.9462 | 122.7219 | 122.9874 | 122.9507 | 123.0881 | -0.59509 | -0.48981
4071.3281 | 123.1613 | -122.8363 | 0.19226 | 0.069504 | 0.0087841 | -0.011651 | 0.041524 | -0.018538 | -0.011476 | 0.0081347 | -0.10529 | 0.10529 | -0.4303 | 0.041199 | 0.07782 | 0.10529 | -0.10986 | 0.2655 | 0.2655 | -0.32044 | 122.406 | -0.086975 | 122.731 | 122.8775 | -0.11444 | 122.5159 | 0.073242 | 0.32501 | 122.7264 | 123.1018 | 122.9141 | 122.9416 | 122.731 | 123.1018 | 122.9416 | 122.5159 | 122.9416 | 122.731 | 122.9416 | 122.9141 | 123.1018 | -0.62256 | -0.5127
4073.0469 | 123.1888 | -122.8088 | 0.19684 | 0.077133 | 0.01028 | -0.015283 | 0.041524 | -0.017256 | -0.013399 | 0.0070667 | -0.1236 | 0.091553 | -0.43488 | 0.041199 | 0.082397 | 0.10071 | -0.11444 | 0.27008 | 0.24261 | -0.30212 | 122.374 | -0.10529 | 122.6852 | 122.85 | -0.11444 | 122.5067 | 0.045777 | 0.31128 | 122.6944 | 123.0789 | 122.8912 | 122.9004 | 122.6852 | 123.0515 | 122.9095 | 122.5067 | 122.9004 | 122.6852 | 122.9095 | 122.8912 | 123.0515 | -0.63171 | -0.49896
4074.7344 | 123.1613 | -122.8271 | 0.19226 | -0.19753 | 0.0077161 | -0.010369 | 0.043019 | -0.02217 | -0.012117 | 0.0070667 | -0.064087 | 0.091553 | -0.43488 | 0.10986 | 0.10529 | 0.14648 | -0.12817 | 0.3479 | 0.24261 | -0.31586 | 122.3923 | -0.10071 | 122.7631 | 122.937 | -0.086975 | 122.5113 | 0.050354 | 0.37079 | 122.699 | 123.175 | 122.9324 | 122.9187 | 122.7631 | 123.0698 | 122.9736 | 122.5113 | 122.9187 | 122.7631 | 122.9736 | 122.9324 | 123.0698 | -0.62714 | -0.50812
4076.4219 | 123.1247 | -122.85 | 0.19684 | 0.069504 | 0.012843 | -0.0073786 | 0.048146 | -0.018965 | -0.01468 | 0.0066393 | -0.14648 | 0.11902 | -0.48523 | -0.018311 | -0.032043 | 0 | -0.009155 | 0.13733 | 0.28381 | -0.32501 | 122.3648 | -0.077819 | 122.7036 | 122.8317 | -0.22888 | 122.525 | 0.086975 | 0.33875 | 122.8409 | 122.9874 | 122.818 | 122.9691 | 122.7036 | 123.1338 | 122.85 | 122.525 | 122.9691 | 122.7036 | 122.85 | 122.818 | 123.1338 | -0.68207 | -0.52185
4078.1094 | 123.1934 | -122.818 | 0.19684 | -0.22041 | 0.0089979 | -0.010583 | 0.042806 | -0.018111 | -0.014039 | 0.0074939 | -0.1831 | 0.16022 | -0.4715 | -0.004578 | 0.009155 | -0.004578 | 0.036621 | 0.19226 | 0.29297 | -0.34332 | 122.3465 | -0.036621 | 122.6349 | 122.8134 | -0.18768 | 122.4747 | 0.096131 | 0.28839 | 122.8546 | 123.0103 | 122.8271 | 122.9782 | 122.6349 | 123.111 | 122.8134 | 122.4747 | 122.9782 | 122.6349 | 122.8134 | 122.8271 | 123.111 | -0.66834 | -0.54016
4079.8281 | 123.2117 | -122.8271 | 0.1831 | -0.27382 | 0.0098523 | -0.0056696 | 0.040242 | -0.018752 | -0.012117 | 0.0077075 | -0.13275 | 0.11444 | -0.44403 | 0.027466 | 0.054932 | 0.036621 | 0.004578 | 0.2243 | 0.29297 | -0.33417 | 122.3831 | -0.068664 | 122.6944 | 122.8546 | -0.12817 | 122.493 | 0.10986 | 0.31128 | 122.8317 | 123.0515 | 122.8821 | 122.9416 | 122.6944 | 123.1201 | 122.8638 | 122.493 | 122.9416 | 122.6944 | 122.8638 | 122.8821 | 123.1201 | -0.62714 | -0.51727
4081.5156 | 123.1979 | -122.85 | 0.1831 | -0.20515 | 0.0083569 | -0.010369 | 0.042592 | -0.018752 | -0.011903 | 0.0070667 | -0.082397 | 0.10529 | -0.42572 | 0.064087 | 0.07782 | 0.09613 | -0.045776 | 0.29297 | 0.26093 | -0.32959 | 122.4243 | -0.077819 | 122.7676 | 122.9141 | -0.10528 | 122.5204 | 0.07782 | 0.34332 | 122.8043 | 123.143 | 122.9279 | 122.9553 | 122.7676 | 123.111 | 122.9462 | 122.5204 | 122.9553 | 122.7676 | 122.9462 | 122.9279 | 123.111 | -0.60882 | -0.5127
4083.2031 | 123.1476 | -122.8409 | 0.19684 | 0.10002 | 0.012843 | -0.0095148 | 0.041738 | -0.016188 | -0.013612 | 0.010057 | -0.10071 | 0.10529 | -0.41657 | 0.054932 | 0.073242 | 0.10986 | -0.12817 | 0.27008 | 0.26093 | -0.32044 | 122.4243 | -0.091552 | 122.7402 | 122.8958 | -0.1236 | 122.5204 | 0.064087 | 0.31586 | 122.7127 | 123.111 | 122.9141 | 122.9462 | 122.7402 | 123.1018 | 122.9507 | 122.5204 | 122.9462 | 122.7402 | 122.9507 | 122.9141 | 123.1018 | -0.6134 | -0.51727
4084.9375 | 123.1522 | -122.8683 | 0.20142 | -0.22804 | 0.011775 | -0.0056696 | 0.045369 | -0.018325 | -0.012117 | 0.0074939 | -0.12817 | 0.13733 | -0.4715 | 0.022888 | 0.036621 | 0.050354 | -0.004578 | 0.21973 | 0.27924 | -0.32959 | 122.3969 | -0.064087 | 122.7402 | 122.8912 | -0.1648 | 122.5388 | 0.07782 | 0.34332 | 122.8638 | 123.0881 | 122.905 | 123.0057 | 122.7402 | 123.1476 | 122.9187 | 122.5388 | 123.0057 | 122.7402 | 122.9187 | 122.905 | 123.1476 | -0.67291 | -0.53101
4086.625 | 123.23 | -122.8226 | 0.17853 | -0.1899 | 0.011348 | -0.011865 | 0.043019 | -0.018111 | -0.011476 | 0.0081347 | -0.16479 | 0.14191 | -0.46692 | -0.009155 | -0.004578 | 0.004578 | 0.036621 | 0.20599 | 0.30212 | -0.35248 | 122.3557 | -0.036621 | 122.6578 | 122.8134 | -0.18311 | 122.4701 | 0.1236 | 0.30212 | 122.8592 | 123.0286 | 122.818 | 122.9645 | 122.6578 | 123.1247 | 122.8271 | 122.4701 | 122.9645 | 122.6578 | 122.8271 | 122.818 | 123.1247 | -0.64545 | -0.53101
4088.3281 | 123.1888 | -122.85 | 0.1831 | -0.25856 | 0.011989 | -0.0088738 | 0.045156 | -0.018111 | -0.011049 | 0.0085619 | -0.15106 | 0.15564 | -0.46234 | -0.018311 | 0.009155 | 0 | 0.041199 | 0.19684 | 0.3067 | -0.36163 | 122.3877 | -0.027465 | 122.699 | 122.8317 | -0.17395 | 122.4884 | 0.1236 | 0.31128 | 122.8912 | 123.0469 | 122.8592 | 123.0057 | 122.699 | 123.1567 | 122.85 | 122.4884 | 123.0057 | 122.699 | 122.85 | 122.8592 | 123.1567 | -0.64545 | -0.54474
4090.0156 | 123.1842 | -122.8455 | 0.19684 | -0.1899 | 0.010493 | -0.014214 | 0.040883 | -0.020461 | -0.014467 | 0.0070667 | -0.082397 | 0.091553 | -0.42572 | 0.10529 | 0.11444 | 0.13733 | -0.10529 | 0.32501 | 0.25635 | -0.30212 | 122.4197 | -0.10529 | 122.7631 | 122.9507 | -0.082397 | 122.5433 | 0.05951 | 0.34332 | 122.7402 | 123.1705 | 122.9599 | 122.937 | 122.7631 | 123.1018 | 122.9828 | 122.5433 | 122.937 | 122.7631 | 122.9828 | 122.9599 | 123.1018 | -0.62256 | -0.49896
4091.7188 | 123.2208 | -122.8271 | 0.18768 | -0.28145 | 0.011989 | -0.011224 | 0.044088 | -0.017897 | -0.012971 | 0.0064257 | -0.17853 | 0.14648 | -0.46692 | -0.013733 | -0.004578 | 0 | 0.068665 | 0.20599 | 0.29297 | -0.33417 | 122.3602 | -0.041199 | 122.6486 | 122.8134 | -0.19226 | 122.493 | 0.10529 | 0.28839 | 122.8958 | 123.0331 | 122.8226 | 122.9736 | 122.6486 | 123.1201 | 122.8271 | 122.493 | 122.9736 | 122.6486 | 122.8271 | 122.8226 | 123.1201 | -0.6546 | -0.52185
4093.4062 | 123.2071 | -122.8226 | 0.17853 | 0.0084684 | 0.011134 | -0.01101 | 0.039174 | -0.017684 | -0.014253 | 0.0085619 | -0.11902 | 0.13275 | -0.43488 | 0.050354 | 0.07782 | 0.10986 | -0.10071 | 0.27466 | 0.26093 | -0.32501 | 122.3877 | -0.045777 | 122.7036 | 122.8729 | -0.10071 | 122.4976 | 0.082397 | 0.31586 | 122.7219 | 123.0972 | 122.9004 | 122.9553 | 122.7036 | 123.0835 | 122.9324 | 122.4976 | 122.9553 | 122.7036 | 122.9324 | 122.9004 | 123.0835 | -0.6134 | -0.50354
4095.1094 | 123.2117 | -122.8317 | 0.16937 | 0.00083945 | 0.010707 | -0.0095148 | 0.04067 | -0.020034 | -0.010835 | 0.0089893 | -0.11444 | 0.10071 | -0.43945 | 0.041199 | 0.068665 | 0.082397 | -0.10986 | 0.25635 | 0.23804 | -0.3067 | 122.3923 | -0.068665 | 122.7173 | 122.8729 | -0.10071 | 122.525 | 0.068664 | 0.32501 | 122.7219 | 123.0881 | 122.9004 | 122.9324 | 122.7173 | 123.0698 | 122.9141 | 122.525 | 122.9324 | 122.7173 | 122.9141 | 122.9004 | 123.0698 | -0.60883 | -0.47607
4096.7969 | 123.1888 | -122.818 | 0.18768 | 0.038986 | 0.012416 | -0.008233 | 0.04067 | -0.020461 | -0.011903 | 0.0064257 | -0.1236 | 0.10071 | -0.43945 | 0.050354 | 0.054932 | 0.09613 | -0.11444 | 0.2655 | 0.2655 | -0.31128 | 122.3785 | -0.086975 | 122.6944 | 122.8683 | -0.13275 | 122.5067 | 0.07782 | 0.31586 | 122.7036 | 123.0835 | 122.8729 | 122.9187 | 122.6944 | 123.0835 | 122.9141 | 122.5067 | 122.9187 | 122.6944 | 122.9141 | 122.8729 | 123.0835 | -0.62714 | -0.49896
4098.4844 | 123.0698 | -122.8638 | 0.20142 | 0.18394 | 0.010066 | -0.012933 | 0.045583 | -0.016829 | -0.011049 | 0.0072803 | -0.054932 | 0.091553 | -0.42572 | 0.09613 | 0.091553 | 0.14648 | -0.20599 | 0.30212 | 0.24719 | -0.3067 | 122.4381 | -0.10986 | 122.8088 | 122.9599 | -0.10986 | 122.5571 | 0.045776 | 0.37079 | 122.6578 | 123.1659 | 122.9553 | 122.9553 | 122.8088 | 123.111 | 123.0103 | 122.5571 | 122.9553 | 122.8088 | 123.0103 | 122.9553 | 123.111 | -0.62714 | -0.50812
4100.1719 | 123.0743 | -122.85 | 0.19226 | 0.17632 | 0.01028 | -0.009942 | 0.044515 | -0.01982 | -0.014253 | 0.0072803 | -0.050354 | 0.09613 | -0.41199 | 0.10071 | 0.09613 | 0.13733 | -0.20142 | 0.28839 | 0.24261 | -0.29755 | 122.4381 | -0.096131 | 122.7997 | 122.9507 | -0.096131 | 122.5525 | 0.050354 | 0.36163 | 122.6486 | 123.1384 | 122.9462 | 122.9462 | 122.7997 | 123.0927 | 122.9874 | 122.5525 | 122.9462 | 122.7997 | 122.9874 | 122.9462 | 123.0927 | -0.60425 | -0.48981
4101.8594 | 123.2162 | -122.8409 | 0.17853 | -0.25856 | 0.0083569 | -0.013146 | 0.044301 | -0.022811 | -0.014253 | 0.0062121 | -0.19226 | 0.15106 | -0.46234 | -0.018311 | 0 | -0.009155 | 0.032043 | 0.18768 | 0.31586 | -0.33875 | 122.3785 | -0.027466 | 122.6486 | 122.8226 | -0.17853 | 122.5021 | 0.13733 | 0.27008 | 122.8729 | 123.0286 | 122.8409 | 122.9919 | 122.6486 | 123.1567 | 122.8317 | 122.5021 | 122.9919 | 122.6486 | 122.8317 | 122.8409 | 123.1567 | -0.64087 | -0.51727
4103.5625 | 123.2117 | -122.8088 | 0.1831 | -0.26619 | 0.012843 | -0.0095148 | 0.042592 | -0.01747 | -0.013399 | 0.0079211 | -0.17395 | 0.15106 | -0.46692 | 0 | -0.004578 | -0.009155 | 0.059509 | 0.19226 | 0.3067 | -0.35248 | 122.3419 | -0.032043 | 122.6349 | 122.8088 | -0.18768 | 122.4564 | 0.1236 | 0.29297 | 122.8683 | 123.0011 | 122.8043 | 122.9599 | 122.6349 | 123.1155 | 122.7997 | 122.4564 | 122.9599 | 122.6349 | 122.7997 | 122.8043 | 123.1155 | -0.65002 | -0.53558
4105.25 | 123.2346 | -122.818 | 0.20599 | -0.25093 | 0.0096387 | -0.0071648 | 0.044301 | -0.017043 | -0.012758 | 0.0079211 | -0.16479 | 0.15564 | -0.4715 | 0.004578 | 0.009155 | 0 | 0.054932 | 0.20142 | 0.28839 | -0.35706 | 122.3465 | -0.050354 | 122.6532 | 122.8226 | -0.19684 | 122.4609 | 0.082397 | 0.3067 | 122.8729 | 123.0194 | 122.8271 | 122.9736 | 122.6532 | 123.1064 | 122.818 | 122.4609 | 122.9736 | 122.6532 | 122.818 | 122.8271 | 123.1064 | -0.67749 | -0.56305
4106.9375 | 123.2117 | -122.8088 | 0.18768 | -0.01442 | 0.0096387 | -0.01101 | 0.04067 | -0.01747 | -0.01169 | 0.0066393 | -0.1236 | 0.09613 | -0.44403 | 0.041199 | 0.073242 | 0.086975 | -0.1236 | 0.25177 | 0.24719 | -0.30212 | 122.3648 | -0.091553 | 122.6852 | 122.85 | -0.11444 | 122.5067 | 0.059509 | 0.32044 | 122.6852 | 123.0606 | 122.8821 | 122.905 | 122.6852 | 123.056 | 122.8958 | 122.5067 | 122.905 | 122.6852 | 122.8958 | 122.8821 | 123.056 | -0.63171 | -0.48981
4108.625 | 123.1201 | -122.8638 | 0.19684 | 0.1458 | 0.0085705 | -0.0097284 | 0.042592 | -0.019606 | -0.0099805 | 0.0081347 | -0.086975 | 0.10071 | -0.43945 | 0.068665 | 0.10071 | 0.11444 | -0.16022 | 0.27466 | 0.22888 | -0.30212 | 122.4243 | -0.09613 | 122.7768 | 122.9324 | -0.09613 | 122.5616 | 0.032044 | 0.35248 | 122.7036 | 123.1384 | 122.9645 | 122.9645 | 122.7768 | 123.0927 | 122.9782 | 122.5616 | 122.9645 | 122.7768 | 122.9782 | 122.9645 | 123.0927 | -0.63629 | -0.49896
4110.3125 | 123.1201 | -122.8546 | 0.21973 | 0.10765 | 0.01028 | -0.006524 | 0.047719 | -0.018325 | -0.013399 | 0.010057 | -0.16479 | 0.14648 | -0.48523 | -0.013733 | 0.009155 | 0.022888 | -0.064087 | 0.16479 | 0.28381 | -0.33875 | 122.3694 | -0.073243 | 122.6898 | 122.8409 | -0.21057 | 122.5159 | 0.064086 | 0.32043 | 122.7905 | 123.0194 | 122.8638 | 123.0011 | 122.6898 | 123.1384 | 122.8775 | 122.5159 | 123.0011 | 122.6898 | 122.8775 | 122.8638 | 123.1384 | -0.70496 | -0.55847
4112.0469 | 123.1613 | -122.8363 | 0.18768 | -0.15175 | 0.0083569 | -0.010369 | 0.039601 | -0.018325 | -0.011903 | 0.0074939 | -0.059509 | 0.10529 | -0.41199 | 0.10529 | 0.11902 | 0.15564 | -0.14191 | 0.33417 | 0.26093 | -0.31128 | 122.4243 | -0.082397 | 122.7768 | 122.9416 | -0.068664 | 122.525 | 0.073242 | 0.35248 | 122.6944 | 123.1705 | 122.9553 | 122.9416 | 122.7768 | 123.0972 | 122.9919 | 122.525 | 122.9416 | 122.7768 | 122.9919 | 122.9553 | 123.0972 | -0.59967 | -0.49896
4113.7344 | 123.1796 | -122.8363 | 0.16937 | 0.077133 | 0.0098523 | -0.0060968 | 0.04067 | -0.020034 | -0.012544 | 0.0072803 | -0.10071 | 0.10529 | -0.41657 | 0.045776 | 0.054932 | 0.09613 | -0.11902 | 0.25635 | 0.25635 | -0.33875 | 122.4197 | -0.064087 | 122.7356 | 122.8821 | -0.11444 | 122.4976 | 0.086975 | 0.31586 | 122.7173 | 123.0927 | 122.8912 | 122.9416 | 122.7356 | 123.0927 | 122.9324 | 122.4976 | 122.9416 | 122.7356 | 122.9324 | 122.8912 | 123.0927 | -0.58594 | -0.50812
4115.4375 | 123.111 | -122.8638 | 0.19226 | 0.031357 | 0.0094251 | -0.0095148 | 0.049642 | -0.016188 | -0.012971 | 0.0068531 | -0.11902 | 0.14191 | -0.48065 | -0.004578 | 0.009155 | 0.009155 | -0.013733 | 0.16479 | 0.32044 | -0.33417 | 122.3831 | -0.050354 | 122.7448 | 122.8592 | -0.18311 | 122.5296 | 0.12817 | 0.36163 | 122.85 | 123.0286 | 122.8729 | 123.0057 | 122.7448 | 123.1842 | 122.8729 | 122.5296 | 123.0057 | 122.7448 | 122.8729 | 122.8729 | 123.1842 | -0.67291 | -0.52643
4117.1562 | 123.1659 | -122.8455 | 0.17853 | -0.13649 | 0.0098523 | -0.014642 | 0.036824 | -0.018752 | -0.010621 | 0.0085619 | -0.068665 | 0.10529 | -0.42114 | 0.1236 | 0.14648 | 0.16479 | -0.15106 | 0.36163 | 0.23346 | -0.30212 | 122.4243 | -0.073242 | 122.7768 | 122.9691 | -0.032044 | 122.5433 | 0.054931 | 0.35248 | 122.6944 | 123.2071 | 122.9919 | 122.9507 | 122.7768 | 123.0789 | 123.0103 | 122.5433 | 122.9507 | 122.7768 | 123.0103 | 122.9919 | 123.0789 | -0.59967 | -0.48065
4118.8438 | 123.1613 | -122.8271 | 0.17395 | -0.13649 | 0.0089979 | -0.0097284 | 0.039815 | -0.020461 | -0.012758 | 0.0062121 | -0.068665 | 0.10986 | -0.41199 | 0.10529 | 0.13275 | 0.14648 | -0.14648 | 0.33417 | 0.24719 | -0.30212 | 122.4152 | -0.064087 | 122.7585 | 122.9324 | -0.041199 | 122.525 | 0.073242 | 0.34332 | 122.6807 | 123.1613 | 122.9599 | 122.937 | 122.7585 | 123.0743 | 122.9736 | 122.525 | 122.937 | 122.7585 | 122.9736 | 122.9599 | 123.0743 | -0.58594 | -0.47607
4120.5312 | 123.1476 | -122.85 | 0.1831 | 0.11528 | 0.011348 | -0.015496 | 0.043447 | -0.017256 | -0.011476 | 0.0066393 | -0.07782 | 0.10071 | -0.42114 | 0.073242 | 0.086975 | 0.10529 | -0.14191 | 0.26093 | 0.2655 | -0.32044 | 122.4289 | -0.082397 | 122.7722 | 122.9233 | -0.09613 | 122.5296 | 0.082398 | 0.34332 | 122.7081 | 123.111 | 122.937 | 122.9507 | 122.7722 | 123.1155 | 122.9553 | 122.5296 | 122.9507 | 122.7722 | 122.9553 | 122.937 | 123.1155 | -0.60425 | -0.50354
4122.2188 | 123.1201 | -122.8638 | 0.21515 | 0.11528 | 0.011134 | -0.0067376 | 0.047719 | -0.017897 | -0.013399 | 0.0087757 | -0.15564 | 0.13733 | -0.47607 | 0.004578 | 0.004578 | 0.041199 | -0.073242 | 0.17395 | 0.2655 | -0.34332 | 122.3877 | -0.07782 | 122.7081 | 122.8683 | -0.21057 | 122.5204 | 0.050354 | 0.32043 | 122.7905 | 123.0377 | 122.8683 | 123.0011 | 122.7081 | 123.1293 | 122.905 | 122.5204 | 123.0011 | 122.7081 | 122.905 | 122.8683 | 123.1293 | -0.69122 | -0.55847
4123.9688 | 123.1979 | -122.8271 | 0.19226 | -0.098343 | 0.0094251 | -0.0088738 | 0.040456 | -0.019393 | -0.0099805 | 0.0077075 | -0.09613 | 0.09613 | -0.4303 | 0.091553 | 0.11902 | 0.14648 | -0.13275 | 0.32959 | 0.25177 | -0.31128 | 122.3969 | -0.096131 | 122.731 | 122.9187 | -0.073242 | 122.5159 | 0.059509 | 0.33417 | 122.6944 | 123.1567 | 122.9462 | 122.9233 | 122.731 | 123.0789 | 122.9736 | 122.5159 | 122.9233 | 122.731 | 122.9736 | 122.9462 | 123.0789 | -0.62256 | -0.50354
4125.7031 | 123.2117 | -122.8409 | 0.16937 | -0.0067901 | 0.010921 | -0.01101 | 0.040883 | -0.021102 | -0.0095531 | 0.0070667 | -0.1236 | 0.1236 | -0.43945 | 0.041199 | 0.068665 | 0.086975 | -0.11444 | 0.25635 | 0.25635 | -0.33417 | 122.4014 | -0.045777 | 122.7173 | 122.8821 | -0.10071 | 122.5067 | 0.086975 | 0.31586 | 122.7264 | 123.0972 | 122.9095 | 122.9645 | 122.7173 | 123.0972 | 122.9279 | 122.5067 | 122.9645 | 122.7173 | 122.9279 | 122.9095 | 123.0972 | -0.60883 | -0.50354
4127.3906 | 123.2117 | -122.818 | 0.18768 | -0.029679 | 0.010707 | -0.0084466 | 0.042379 | -0.020461 | -0.011476 | 0.0087757 | -0.10986 | 0.11444 | -0.4303 | 0.064087 | 0.082397 | 0.10986 | -0.11444 | 0.28381 | 0.25177 | -0.31586 | 122.3877 | -0.073242 | 122.7081 | 122.8821 | -0.10529 | 122.5021 | 0.064087 | 0.32044 | 122.7036 | 123.1018 | 122.9004 | 122.9324 | 122.7081 | 123.0698 | 122.9279 | 122.5021 | 122.9324 | 122.7081 | 122.9279 | 122.9004 | 123.0698 | -0.61798 | -0.50354
4129.0938 | 123.1888 | -122.85 | 0.20142 | -0.16701 | 0.010493 | -0.011437 | 0.044515 | -0.021529 | -0.01233 | 0.0047167 | -0.07782 | 0.10986 | -0.42572 | 0.091553 | 0.082397 | 0.10529 | -0.082397 | 0.31586 | 0.24719 | -0.32044 | 122.4243 | -0.091553 | 122.7722 | 122.9416 | -0.11902 | 122.5296 | 0.045776 | 0.3479 | 122.7676 | 123.1659 | 122.9324 | 122.9599 | 122.7722 | 123.0972 | 122.9553 | 122.5296 | 122.9599 | 122.7722 | 122.9553 | 122.9324 | 123.0972 | -0.62714 | -0.52185
4130.7812 | 123.1338 | -122.8729 | 0.20142 | 0.084762 | 0.0070751 | -0.010156 | 0.042379 | -0.017043 | -0.014894 | 0.0083483 | -0.09613 | 0.11444 | -0.43488 | 0.068665 | 0.068665 | 0.091553 | -0.14648 | 0.27466 | 0.23804 | -0.3067 | 122.438 | -0.086975 | 122.7768 | 122.9416 | -0.13275 | 122.5662 | 0.036621 | 0.33875 | 122.7264 | 123.1476 | 122.9416 | 122.9874 | 122.7768 | 123.111 | 122.9645 | 122.5662 | 122.9874 | 122.7768 | 122.9645 | 122.9416 | 123.111 | -0.63629 | -0.50812
4132.4688 | 123.0743 | -122.8867 | 0.20142 | 0.16106 | 0.010493 | -0.0097284 | 0.045583 | -0.01747 | -0.013612 | 0.0077075 | -0.073242 | 0.10071 | -0.43488 | 0.086975 | 0.09613 | 0.14191 | -0.19226 | 0.29755 | 0.2655 | -0.29297 | 122.4518 | -0.10071 | 122.8134 | 122.9736 | -0.10529 | 122.5937 | 0.064087 | 0.36163 | 122.6944 | 123.1842 | 122.9828 | 122.9874 | 122.8134 | 123.1522 | 123.0286 | 122.5937 | 122.9874 | 122.8134 | 123.0286 | 122.9828 | 123.1522 | -0.63629 | -0.49438
4134.1562 | 123.111 | -122.8683 | 0.20142 | 0.13817 | 0.011775 | -0.0097284 | 0.047933 | -0.017256 | -0.014894 | 0.0085619 | -0.15106 | 0.1236 | -0.48065 | 0.004578 | 0.009155 | 0.032043 | -0.086975 | 0.17853 | 0.27466 | -0.31586 | 122.3877 | -0.07782 | 122.7173 | 122.8729 | -0.19226 | 122.5525 | 0.073242 | 0.32959 | 122.7814 | 123.0469 | 122.8775 | 122.9919 | 122.7173 | 123.143 | 122.9004 | 122.5525 | 122.9919 | 122.7173 | 122.9004 | 122.8775 | 123.143 | -0.68207 | -0.51727
4135.8438 | 123.0835 | -122.8775 | 0.22888 | -0.083084 | 0.0089979 | -0.010796 | 0.044301 | -0.019606 | -0.016176 | 0.0059985 | -0.091553 | 0.13275 | -0.48065 | 0.032043 | 0.045776 | 0.054932 | -0.036621 | 0.24719 | 0.27466 | -0.32044 | 122.3969 | -0.096131 | 122.7859 | 122.9095 | -0.18311 | 122.5571 | 0.045776 | 0.3891 | 122.8409 | 123.1247 | 122.9233 | 123.0103 | 122.7859 | 123.1522 | 122.9324 | 122.5571 | 123.0103 | 122.7859 | 122.9324 | 122.9233 | 123.1522 | -0.70953 | -0.54932
4137.5312 | 123.1064 | -122.8867 | 0.22888 | -0.037308 | 0.01028 | -0.0071648 | 0.047078 | -0.018325 | -0.010835 | 0.0066393 | -0.11902 | 0.12817 | -0.45319 | 0.027466 | 0.009155 | 0.045776 | -0.032043 | 0.19226 | 0.28381 | -0.33417 | 122.4335 | -0.10071 | 122.7676 | 122.9141 | -0.21973 | 122.5525 | 0.054931 | 0.33417 | 122.8546 | 123.0789 | 122.8958 | 123.0148 | 122.7676 | 123.1705 | 122.9324 | 122.5525 | 123.0148 | 122.7676 | 122.9324 | 122.8958 | 123.1705 | -0.68207 | -0.56305
4139.25 | 123.1064 | -122.8683 | 0.21973 | 0.0084684 | 0.010707 | -0.0011834 | 0.045797 | -0.015761 | -0.01233 | 0.0096301 | -0.10986 | 0.15106 | -0.46692 | 0 | 0.004578 | 0.009155 | -0.018311 | 0.16022 | 0.28381 | -0.35248 | 122.4014 | -0.068665 | 122.7585 | 122.8683 | -0.21515 | 122.5159 | 0.064086 | 0.35706 | 122.85 | 123.0286 | 122.8729 | 123.0194 | 122.7585 | 123.1522 | 122.8775 | 122.5159 | 123.0194 | 122.7585 | 122.8775 | 122.8729 | 123.1522 | -0.68665 | -0.57221
4140.9375 | 123.1796 | -122.85 | 0.17395 | -0.17464 | 0.0087841 | -0.01336 | 0.038747 | -0.018538 | -0.011903 | 0.0085619 | -0.082397 | 0.09613 | -0.43945 | 0.082397 | 0.10986 | 0.12817 | -0.09613 | 0.32044 | 0.25635 | -0.31128 | 122.4106 | -0.07782 | 122.7676 | 122.9324 | -0.064087 | 122.5388 | 0.082398 | 0.35706 | 122.7539 | 123.1705 | 122.9599 | 122.9462 | 122.7676 | 123.1064 | 122.9782 | 122.5388 | 122.9462 | 122.7676 | 122.9782 | 122.9599 | 123.1064 | -0.6134 | -0.48523
4142.6562 | 123.1659 | -122.8592 | 0.18768 | 0.077133 | 0.0096387 | -0.009942 | 0.040242 | -0.018325 | -0.012544 | 0.0079211 | -0.10071 | 0.10071 | -0.42572 | 0.041199 | 0.07782 | 0.10071 | -0.12817 | 0.27008 | 0.25635 | -0.29297 | 122.4335 | -0.086975 | 122.7585 | 122.9004 | -0.10986 | 122.5662 | 0.068665 | 0.32501 | 122.731 | 123.1293 | 122.937 | 122.9599 | 122.7585 | 123.1155 | 122.9599 | 122.5662 | 122.9599 | 122.7585 | 122.9599 | 122.937 | 123.1155 | -0.6134 | -0.48065
4144.3594 | 123.1979 | -122.8409 | 0.1831 | -0.25856 | 0.012202 | -0.014642 | 0.04366 | -0.018752 | -0.012544 | 0.0077075 | -0.16479 | 0.15564 | -0.48065 | -0.013733 | -0.013733 | -0.004578 | 0.054932 | 0.18768 | 0.3067 | -0.3479 | 122.3602 | -0.027465 | 122.6761 | 122.8271 | -0.19684 | 122.493 | 0.1236 | 0.31586 | 122.8958 | 123.0286 | 122.8271 | 122.9965 | 122.6761 | 123.1476 | 122.8363 | 122.493 | 122.9965 | 122.6761 | 122.8363 | 122.8271 | 123.1476 | -0.66376 | -0.531
4146.0625 | 123.111 | -122.8592 | 0.21515 | 0.10765 | 0.0079297 | -0.0093012 | 0.041524 | -0.01982 | -0.011049 | 0.0047167 | -0.073242 | 0.073242 | -0.43488 | 0.068665 | 0.091553 | 0.14191 | -0.17853 | 0.28381 | 0.23346 | -0.28381 | 122.4243 | -0.14191 | 122.7859 | 122.9279 | -0.1236 | 122.5754 | 0.01831 | 0.36163 | 122.6807 | 123.143 | 122.9507 | 122.9324 | 122.7859 | 123.0927 | 123.0011 | 122.5754 | 122.9324 | 122.7859 | 123.0011 | 122.9507 | 123.0927 | -0.65002 | -0.49896
4147.75 | 123.1018 | -122.8775 | 0.21057 | 0.1458 | 0.0087841 | -0.013146 | 0.042379 | -0.020461 | -0.011049 | 0.0074939 | -0.073242 | 0.082397 | -0.42572 | 0.086975 | 0.10071 | 0.13733 | -0.1831 | 0.29755 | 0.23346 | -0.30212 | 122.4518 | -0.12817 | 122.8043 | 122.9645 | -0.10986 | 122.5754 | 0.022888 | 0.35248 | 122.6944 | 123.175 | 122.9782 | 122.9599 | 122.8043 | 123.111 | 123.0148 | 122.5754 | 122.9599 | 122.8043 | 123.0148 | 122.9782 | 123.111 | -0.63629 | -0.5127
4149.4375 | 123.1247 | -122.8638 | 0.19684 | 0.10002 | 0.0098523 | -0.010583 | 0.047933 | -0.020674 | -0.011262 | 0.0083483 | -0.16937 | 0.15564 | -0.46234 | -0.018311 | 0 | 0.009155 | -0.059509 | 0.17395 | 0.28839 | -0.3479 | 122.4014 | -0.041198 | 122.6944 | 122.8455 | -0.19684 | 122.5159 | 0.091553 | 0.29297 | 122.8043 | 123.0377 | 122.8638 | 123.0194 | 122.6944 | 123.1522 | 122.8729 | 122.5159 | 123.0194 | 122.6944 | 122.8729 | 122.8638 | 123.1522 | -0.65918 | -0.54474
4151.1094 | 123.1888 | -122.7997 | 0.1831 | -0.17464 | 0.0089979 | -0.011865 | 0.044088 | -0.018965 | -0.014039 | 0.0077075 | -0.17395 | 0.16479 | -0.48523 | 0 | 0.004578 | 0.018311 | 0.041199 | 0.20142 | 0.29297 | -0.35248 | 122.3145 | -0.01831 | 122.6257 | 122.7997 | -0.17853 | 122.4472 | 0.10986 | 0.31128 | 122.8409 | 123.0011 | 122.8043 | 122.9645 | 122.6257 | 123.0927 | 122.818 | 122.4472 | 122.9645 | 122.6257 | 122.818 | 122.8043 | 123.0927 | -0.66833 | -0.53558
4152.7969 | 123.2162 | -122.8134 | 0.17395 | -0.23567 | 0.0089979 | -0.014428 | 0.041951 | -0.020034 | -0.011262 | 0.0081347 | -0.16022 | 0.14191 | -0.46692 | -0.013733 | -0.009155 | 0.013733 | 0.045776 | 0.20142 | 0.3067 | -0.35248 | 122.3465 | -0.032043 | 122.6532 | 122.7997 | -0.1831 | 122.4609 | 0.13275 | 0.3067 | 122.8592 | 123.0148 | 122.8043 | 122.9553 | 122.6532 | 123.1201 | 122.8271 | 122.4609 | 122.9553 | 122.6532 | 122.8271 | 122.8043 | 123.1201 | -0.64087 | -0.52643
4154.4844 | 123.1705 | -122.8592 | 0.19684 | -0.13649 | 0.0083569 | -0.010583 | 0.038533 | -0.021529 | -0.0099805 | 0.0089893 | -0.086975 | 0.11444 | -0.42572 | 0.091553 | 0.1236 | 0.15106 | -0.15106 | 0.34332 | 0.26093 | -0.33417 | 122.4335 | -0.082397 | 122.7722 | 122.9507 | -0.073242 | 122.525 | 0.064087 | 0.33874 | 122.7081 | 123.2025 | 122.9828 | 122.9736 | 122.7722 | 123.1201 | 123.0103 | 122.525 | 122.9736 | 122.7722 | 123.0103 | 122.9828 | 123.1201 | -0.62256 | -0.531
4156.2031 | 123.175 | -122.8317 | 0.19684 | -0.22041 | 0.011775 | -0.0043878 | 0.046865 | -0.017684 | -0.013185 | 0.0062121 | -0.15564 | 0.13733 | -0.46692 | 0.013733 | 0.013733 | 0.032043 | 0 | 0.22888 | 0.29755 | -0.33417 | 122.3648 | -0.059509 | 122.6761 | 122.8455 | -0.18311 | 122.4976 | 0.10071 | 0.31128 | 122.8317 | 123.0606 | 122.8455 | 122.9691 | 122.6761 | 123.1293 | 122.8638 | 122.4976 | 122.9691 | 122.6761 | 122.8638 | 122.8455 | 123.1293 | -0.66376 | -0.531
4157.9531 | 123.2346 | -122.8409 | 0.18768 | -0.25856 | 0.0085705 | -0.0093012 | 0.041951 | -0.018752 | -0.014467 | 0.0077075 | -0.14648 | 0.14648 | -0.44403 | 0.004578 | 0.013733 | 0.032043 | 0.022888 | 0.2243 | 0.28839 | -0.33875 | 122.3969 | -0.041199 | 122.6944 | 122.8455 | -0.17395 | 122.5021 | 0.10071 | 0.29755 | 122.8638 | 123.0652 | 122.8546 | 122.9874 | 122.6944 | 123.1293 | 122.8729 | 122.5021 | 122.9874 | 122.6944 | 122.8729 | 122.8546 | 123.1293 | -0.63171 | -0.52643
4159.6562 | 123.2117 | -122.8363 | 0.20599 | -0.18227 | 0.011348 | -0.010156 | 0.044942 | -0.018538 | -0.013399 | 0.0079211 | -0.16479 | 0.15564 | -0.48065 | -0.013733 | 0.009155 | 0.013733 | 0.022888 | 0.20599 | 0.30212 | -0.34332 | 122.3557 | -0.050354 | 122.6715 | 122.8226 | -0.19684 | 122.493 | 0.09613 | 0.31586 | 122.8592 | 123.0423 | 122.8455 | 122.9919 | 122.6715 | 123.1384 | 122.85 | 122.493 | 122.9919 | 122.6715 | 122.85 | 122.8455 | 123.1384 | -0.68665 | -0.54932
4161.3438 | 123.23 | -122.8226 | 0.1831 | -0.27382 | 0.010493 | -0.010796 | 0.04366 | -0.018325 | -0.014894 | 0.0059985 | -0.16937 | 0.16479 | -0.47607 | -0.022888 | 0.013733 | 0 | 0.050354 | 0.18768 | 0.3067 | -0.34332 | 122.3465 | -0.01831 | 122.6532 | 122.7997 | -0.16937 | 122.4792 | 0.1236 | 0.3067 | 122.8729 | 123.0103 | 122.8363 | 122.9874 | 122.6532 | 123.1293 | 122.8226 | 122.4792 | 122.9874 | 122.6532 | 122.8226 | 122.8363 | 123.1293 | -0.65918 | -0.52643
4163.0312 | 123.1247 | -122.8729 | 0.1831 | 0.10765 | 0.010493 | -0.013787 | 0.045797 | -0.019179 | -0.015321 | 0.0089893 | -0.16022 | 0.15106 | -0.46234 | -0.013733 | 0.013733 | 0.027466 | -0.064087 | 0.17395 | 0.28839 | -0.33417 | 122.4106 | -0.032043 | 122.7127 | 122.8592 | -0.16937 | 122.5388 | 0.10529 | 0.30212 | 122.8088 | 123.0469 | 122.8867 | 123.024 | 122.7127 | 123.1613 | 122.9004 | 122.5388 | 123.024 | 122.7127 | 122.9004 | 122.8867 | 123.1613 | -0.64545 | -0.51727
4164.7188 | 123.1293 | -122.905 | 0.19684 | 0.13054 | 0.0085705 | -0.01101 | 0.045369 | -0.018325 | -0.013185 | 0.0077075 | -0.16479 | 0.14191 | -0.48523 | -0.032043 | -0.004578 | 0.004578 | -0.018311 | 0.15106 | 0.29755 | -0.34332 | 122.4197 | -0.054931 | 122.7402 | 122.8729 | -0.20142 | 122.5616 | 0.10071 | 0.32043 | 122.8867 | 123.056 | 122.9004 | 123.0469 | 122.7402 | 123.2025 | 122.9095 | 122.5616 | 123.0469 | 122.7402 | 122.9095 | 122.9004 | 123.2025 | -0.68207 | -0.54016
4166.4219 | 123.23 | -122.8317 | 0.18768 | -0.2433 | 0.0087841 | -0.010369 | 0.042165 | -0.020461 | -0.011903 | 0.0064257 | -0.19226 | 0.14648 | -0.48065 | -0.036621 | 0.009155 | 0.009155 | 0.064087 | 0.20599 | 0.29755 | -0.36163 | 122.3511 | -0.041199 | 122.6395 | 122.7951 | -0.17853 | 122.4701 | 0.10986 | 0.28839 | 122.8958 | 123.0377 | 122.8409 | 122.9782 | 122.6395 | 123.1293 | 122.8409 | 122.4701 | 122.9782 | 122.6395 | 122.8409 | 122.8409 | 123.1293 | -0.66834 | -0.54932
4168.1094 | 123.1796 | -122.8455 | 0.19226 | -0.20515 | 0.0089979 | -0.011437 | 0.038747 | -0.020247 | -0.015321 | 0.0068531 | -0.068665 | 0.10986 | -0.41199 | 0.07782 | 0.10071 | 0.11902 | -0.068665 | 0.32959 | 0.27008 | -0.31586 | 122.4335 | -0.082398 | 122.7768 | 122.9233 | -0.091553 | 122.5296 | 0.07782 | 0.34332 | 122.7768 | 123.175 | 122.9462 | 122.9553 | 122.7768 | 123.1155 | 122.9645 | 122.5296 | 122.9553 | 122.7768 | 122.9645 | 122.9462 | 123.1155 | -0.60425 | -0.50812
4169.7969 | 123.1613 | -122.8638 | 0.20599 | -0.19753 | 0.010493 | -0.0097284 | 0.038961 | -0.019606 | -0.014039 | 0.0077075 | -0.054932 | 0.09613 | -0.4303 | 0.082397 | 0.1236 | 0.15106 | -0.14648 | 0.3479 | 0.27008 | -0.33417 | 122.4335 | -0.10986 | 122.8088 | 122.9462 | -0.082398 | 122.5296 | 0.064087 | 0.37537 | 122.7173 | 123.2117 | 122.9874 | 122.9599 | 122.8088 | 123.1339 | 123.0148 | 122.5296 | 122.9599 | 122.8088 | 123.0148 | 122.9874 | 123.1339 | -0.63629 | -0.54016
4171.5156 | 123.1705 | -122.8409 | 0.16022 | -0.12886 | 0.0083569 | -0.014001 | 0.039601 | -0.018752 | -0.011903 | 0.0072803 | -0.086975 | 0.11902 | -0.42572 | 0.10986 | 0.12817 | 0.16479 | -0.12817 | 0.32959 | 0.25635 | -0.3067 | 122.4152 | -0.041198 | 122.7539 | 122.9507 | -0.032043 | 122.5342 | 0.096131 | 0.33874 | 122.7127 | 123.1705 | 122.9691 | 122.9599 | 122.7539 | 123.0972 | 123.0057 | 122.5342 | 122.9599 | 122.7539 | 123.0057 | 122.9691 | 123.0972 | -0.58594 | -0.46692
4173.2188 | 123.2162 | -122.8317 | 0.17395 | 0.016098 | 0.0092115 | -0.013146 | 0.04067 | -0.021529 | -0.01233 | 0.0051441 | -0.12817 | 0.10529 | -0.45319 | 0.032043 | 0.068665 | 0.082397 | -0.10986 | 0.2655 | 0.27008 | -0.31586 | 122.3785 | -0.068664 | 122.7036 | 122.8638 | -0.10528 | 122.5159 | 0.096131 | 0.32501 | 122.7219 | 123.0972 | 122.9004 | 122.937 | 122.7036 | 123.1018 | 122.9141 | 122.5159 | 122.937 | 122.7036 | 122.9141 | 122.9004 | 123.1018 | -0.62714 | -0.48981
4174.9688 | 123.1705 | -122.8363 | 0.17853 | -0.067826 | 0.010707 | -0.011437 | 0.041951 | -0.021956 | -0.011476 | 0.0081347 | -0.10986 | 0.10529 | -0.44403 | 0.091553 | 0.10529 | 0.11902 | -0.1236 | 0.31586 | 0.24719 | -0.32501 | 122.3923 | -0.073242 | 122.7264 | 122.9279 | -0.073242 | 122.5113 | 0.068664 | 0.33417 | 122.7127 | 123.1522 | 122.9416 | 122.9416 | 122.7264 | 123.0835 | 122.9553 | 122.5113 | 122.9416 | 122.7264 | 122.9553 | 122.9416 | 123.0835 | -0.62256 | -0.50354
4176.6562 | 123.175 | -122.8317 | 0.19226 | -0.12123 | 0.0092115 | -0.01101 | 0.04131 | -0.020461 | -0.012117 | 0.0072803 | -0.064087 | 0.10529 | -0.4303 | 0.11444 | 0.11902 | 0.14191 | -0.16479 | 0.34332 | 0.25635 | -0.3067 | 122.4014 | -0.086975 | 122.7676 | 122.9462 | -0.073242 | 122.525 | 0.064087 | 0.36621 | 122.6669 | 123.175 | 122.9507 | 122.937 | 122.7676 | 123.0881 | 122.9736 | 122.525 | 122.937 | 122.7676 | 122.9736 | 122.9507 | 123.0881 | -0.62256 | -0.49896
4178.3438 | 123.1888 | -122.8043 | 0.17853 | 0.016098 | 0.01028 | -0.012078 | 0.040883 | -0.020461 | -0.011903 | 0.0055713 | -0.10071 | 0.10986 | -0.43488 | 0.068665 | 0.059509 | 0.091553 | -0.10986 | 0.24719 | 0.26093 | -0.32044 | 122.3694 | -0.068665 | 122.7036 | 122.8729 | -0.11902 | 122.4838 | 0.082397 | 0.33417 | 122.6944 | 123.0515 | 122.8638 | 122.9141 | 122.7036 | 123.0652 | 122.8958 | 122.4838 | 122.9141 | 122.7036 | 122.8958 | 122.8638 | 123.0652 | -0.6134 | -0.49896
4180.0625 | 123.0972 | -122.8821 | 0.21515 | 0.18394 | 0.0075025 | -0.012292 | 0.047078 | -0.017684 | -0.011903 | 0.0077075 | -0.045776 | 0.086975 | -0.4303 | 0.10986 | 0.10071 | 0.13733 | -0.18768 | 0.29755 | 0.23804 | -0.28839 | 122.4518 | -0.12817 | 122.8363 | 122.9919 | -0.11444 | 122.5937 | 0.022888 | 0.38452 | 122.6944 | 123.1796 | 122.9828 | 122.9691 | 122.8363 | 123.1201 | 123.0194 | 122.5937 | 122.9691 | 122.8363 | 123.0194 | 122.9828 | 123.1201 | -0.64545 | -0.50354
4181.75 | 123.0743 | -122.8775 | 0.21973 | 0.20683 | 0.0077161 | -0.0054558 | 0.047506 | -0.019179 | -0.015962 | 0.0074939 | -0.059509 | 0.082397 | -0.42572 | 0.10529 | 0.10071 | 0.14648 | -0.21973 | 0.29297 | 0.23804 | -0.31586 | 122.4518 | -0.13733 | 122.818 | 122.9828 | -0.11902 | 122.5616 | 0.01831 | 0.36621 | 122.6578 | 123.1705 | 122.9782 | 122.9599 | 122.818 | 123.1155 | 123.024 | 122.5616 | 122.9599 | 122.818 | 123.024 | 122.9782 | 123.1155 | -0.64545 | -0.53558
4183.5 | 123.2071 | -122.8683 | 0.1831 | -0.25093 | 0.0092115 | -0.01101 | 0.042592 | -0.021315 | -0.01169 | 0.0057849 | -0.10529 | 0.10071 | -0.46234 | 0.07782 | 0.07782 | 0.07782 | -0.054932 | 0.28381 | 0.27924 | -0.32501 | 122.406 | -0.082397 | 122.7631 | 122.9462 | -0.10528 | 122.5433 | 0.096131 | 0.35706 | 122.8134 | 123.1522 | 122.9462 | 122.9691 | 122.7631 | 123.1476 | 122.9462 | 122.5433 | 122.9691 | 122.7631 | 122.9462 | 122.9462 | 123.1476 | -0.64545 | -0.50812
4185.1875 | 123.1293 | -122.8455 | 0.21057 | 0.13054 | 0.011348 | -0.0088738 | 0.043233 | -0.01982 | -0.012971 | 0.0074939 | -0.086975 | 0.091553 | -0.43488 | 0.064087 | 0.073242 | 0.10529 | -0.13733 | 0.27466 | 0.25177 | -0.3067 | 122.4106 | -0.11902 | 122.7585 | 122.9095 | -0.13733 | 122.5388 | 0.041199 | 0.3479 | 122.7081 | 123.1201 | 122.9187 | 122.937 | 122.7585 | 123.0972 | 122.9507 | 122.5388 | 122.937 | 122.7585 | 122.9507 | 122.9187 | 123.0972 | -0.64545 | -0.51727
4186.8906 | 123.111 | -122.8867 | 0.21057 | -0.14412 | 0.0089979 | -0.0088738 | 0.047933 | -0.018538 | -0.012117 | 0.0053577 | -0.11902 | 0.13733 | -0.48065 | 0.041199 | 0.050354 | 0.041199 | -0.041199 | 0.22888 | 0.28381 | -0.33417 | 122.406 | -0.073242 | 122.7676 | 122.9279 | -0.16022 | 122.5525 | 0.073242 | 0.36163 | 122.8455 | 123.1155 | 122.937 | 123.024 | 122.7676 | 123.1705 | 122.9279 | 122.5525 | 123.024 | 122.7676 | 122.9279 | 122.937 | 123.1705 | -0.69122 | -0.54474
4188.5938 | 123.1384 | -122.8775 | 0.17395 | 0.0084684 | 0.012202 | -0.0058832 | 0.047719 | -0.018325 | -0.014467 | 0.0074939 | -0.16937 | 0.14648 | -0.49439 | -0.032043 | -0.032043 | -0.013733 | -0.022888 | 0.14648 | 0.28381 | -0.3479 | 122.3831 | -0.027466 | 122.7081 | 122.8455 | -0.20599 | 122.5296 | 0.10986 | 0.32501 | 122.8546 | 123.024 | 122.8455 | 123.024 | 122.7081 | 123.1613 | 122.8638 | 122.5296 | 123.024 | 122.7081 | 122.8638 | 122.8455 | 123.1613 | -0.66834 | -0.52185
4190.2812 | 123.1064 | -122.8409 | 0.21057 | 0.16106 | 0.0098523 | -0.0039606 | 0.046224 | -0.019606 | -0.012117 | 0.0081347 | -0.17853 | 0.13275 | -0.48523 | 0.004578 | 0.027466 | 0.041199 | -0.091553 | 0.19684 | 0.27924 | -0.32959 | 122.3557 | -0.07782 | 122.6624 | 122.8455 | -0.18311 | 122.5113 | 0.068665 | 0.3067 | 122.7493 | 123.0377 | 122.8683 | 122.9736 | 122.6624 | 123.1201 | 122.8821 | 122.5113 | 122.9736 | 122.6624 | 122.8821 | 122.8683 | 123.1201 | -0.6958 | -0.54016
4192.0469 | 123.1064 | -122.8821 | 0.20599 | 0.12291 | 0.0096387 | -0.0075922 | 0.042165 | -0.021956 | -0.0089123 | 0.0083483 | -0.086975 | 0.086975 | -0.42572 | 0.082397 | 0.086975 | 0.11444 | -0.1831 | 0.28839 | 0.23346 | -0.31128 | 122.4564 | -0.11902 | 122.7951 | 122.9645 | -0.11902 | 122.5708 | 0.027465 | 0.33874 | 122.699 | 123.1705 | 122.9691 | 122.9691 | 122.7951 | 123.1155 | 122.9965 | 122.5708 | 122.9691 | 122.7951 | 122.9965 | 122.9691 | 123.1155 | -0.63171 | -0.51727
4193.7344 | 123.0881 | -122.8821 | 0.22888 | 0.12291 | 0.011561 | -0.011651 | 0.043874 | -0.019606 | -0.010835 | 0.0094165 | -0.082397 | 0.086975 | -0.42572 | 0.064087 | 0.091553 | 0.13733 | -0.17395 | 0.28381 | 0.23804 | -0.30212 | 122.4564 | -0.14191 | 122.7997 | 122.9462 | -0.13733 | 122.58 | 0.009155 | 0.34332 | 122.7081 | 123.1659 | 122.9736 | 122.9691 | 122.7997 | 123.1201 | 123.0194 | 122.58 | 122.9691 | 122.7997 | 123.0194 | 122.9736 | 123.1201 | -0.6546 | -0.53101
4195.4219 | 123.1384 | -122.8455 | 0.18768 | 0.12291 | 0.0087841 | -0.0073786 | 0.046651 | -0.018538 | -0.01169 | 0.0070667 | -0.17395 | 0.13275 | -0.46692 | -0.004578 | -0.004578 | 0.022888 | -0.036621 | 0.16022 | 0.3067 | -0.36163 | 122.3785 | -0.054932 | 122.6715 | 122.8409 | -0.19226 | 122.4838 | 0.11902 | 0.29297 | 122.8088 | 123.0057 | 122.8409 | 122.9782 | 122.6715 | 123.1522 | 122.8683 | 122.4838 | 122.9782 | 122.6715 | 122.8683 | 122.8409 | 123.1522 | -0.6546 | -0.54932
4197.1094 | 123.1064 | -122.8821 | 0.21515 | -0.1136 | 0.0098523 | -0.0084466 | 0.04601 | -0.021315 | -0.013826 | 0.0066393 | -0.1236 | 0.13275 | -0.47607 | 0.036621 | 0.045776 | 0.054932 | -0.022888 | 0.23346 | 0.28839 | -0.32959 | 122.406 | -0.082398 | 122.7585 | 122.9187 | -0.16937 | 122.5525 | 0.073242 | 0.35248 | 122.8592 | 123.1155 | 122.9279 | 123.0148 | 122.7585 | 123.1705 | 122.937 | 122.5525 | 123.0148 | 122.7585 | 122.937 | 122.9279 | 123.1705 | -0.69122 | -0.54474
4198.7969 | 123.2391 | -122.8546 | 0.1831 | -0.20515 | 0.011989 | -0.012933 | 0.037465 | -0.018965 | -0.010835 | 0.0085619 | -0.1831 | 0.12817 | -0.4715 | -0.013733 | 0.009155 | 0 | 0.054932 | 0.21057 | 0.29297 | -0.3479 | 122.3831 | -0.054931 | 122.6715 | 122.8409 | -0.17395 | 122.5067 | 0.10986 | 0.28839 | 122.9095 | 123.0652 | 122.8638 | 122.9828 | 122.6715 | 123.1476 | 122.8546 | 122.5067 | 122.9828 | 122.6715 | 122.8546 | 122.8638 | 123.1476 | -0.6546 | -0.531
4200.5312 | 123.1567 | -122.8363 | 0.19684 | -0.15938 | 0.011348 | -0.010583 | 0.047292 | -0.018111 | -0.014039 | 0.0070667 | -0.14648 | 0.13733 | -0.47607 | 0.027466 | 0.022888 | 0.050354 | 0 | 0.21973 | 0.27924 | -0.33417 | 122.3602 | -0.059509 | 122.6898 | 122.8638 | -0.17395 | 122.5021 | 0.082398 | 0.32959 | 122.8363 | 123.056 | 122.8592 | 122.9736 | 122.6898 | 123.1155 | 122.8867 | 122.5021 | 122.9736 | 122.6898 | 122.8867 | 122.8592 | 123.1155 | -0.67291 | -0.531
4202.2188 | 123.2162 | -122.8226 | 0.18768 | -0.22804 | 0.011775 | -0.011224 | 0.040242 | -0.020674 | -0.013612 | 0.0070667 | -0.16479 | 0.14648 | -0.48523 | -0.022888 | 0 | 0.009155 | 0.050354 | 0.19684 | 0.32044 | -0.33875 | 122.3373 | -0.041199 | 122.6578 | 122.7997 | -0.18768 | 122.4838 | 0.13275 | 0.32043 | 122.8729 | 123.0194 | 122.8226 | 122.9691 | 122.6578 | 123.143 | 122.8317 | 122.4838 | 122.9691 | 122.6578 | 122.8317 | 122.8226 | 123.143 | -0.67291 | -0.52643
4203.9688 | 123.1338 | -122.8638 | 0.20142 | 0.084762 | 0.01028 | -0.0084466 | 0.044301 | -0.016402 | -0.013826 | 0.0057849 | -0.16479 | 0.14191 | -0.47607 | -0.032043 | -0.027466 | -0.009155 | 0.022888 | 0.14191 | 0.29755 | -0.32959 | 122.3877 | -0.059509 | 122.699 | 122.8317 | -0.22888 | 122.5342 | 0.09613 | 0.31128 | 122.8867 | 123.0057 | 122.8363 | 123.0057 | 122.699 | 123.1613 | 122.8546 | 122.5342 | 123.0057 | 122.699 | 122.8546 | 122.8363 | 123.1613 | -0.67749 | -0.53101
4205.6719 | 123.1155 | -122.8592 | 0.20142 | 0.061874 | 0.0092115 | -0.0056696 | 0.045156 | -0.016402 | -0.012758 | 0.0083483 | -0.1831 | 0.13733 | -0.48065 | -0.036621 | -0.022888 | 0 | -0.009155 | 0.15106 | 0.30212 | -0.32959 | 122.3785 | -0.064087 | 122.6761 | 122.8226 | -0.2243 | 122.5296 | 0.10071 | 0.29755 | 122.85 | 123.0103 | 122.8363 | 122.9965 | 122.6761 | 123.1613 | 122.8592 | 122.5296 | 122.9965 | 122.6761 | 122.8592 | 122.8363 | 123.1613 | -0.68207 | -0.53101
4207.3594 | 123.111 | -122.8912 | 0.22888 | 0.016098 | 0.0098523 | -0.011224 | 0.044301 | -0.018325 | -0.013826 | 0.0083483 | -0.13733 | 0.12817 | -0.46234 | -0.009155 | 0.013733 | 0.022888 | -0.004578 | 0.1831 | 0.29755 | -0.32959 | 122.4289 | -0.10071 | 122.7539 | 122.8821 | -0.21515 | 122.5616 | 0.068664 | 0.32501 | 122.8867 | 123.0743 | 122.905 | 123.0194 | 122.7539 | 123.1888 | 122.9141 | 122.5616 | 123.0194 | 122.7539 | 122.9141 | 122.905 | 123.1888 | -0.69122 | -0.55847
4209.0469 | 123.1338 | -122.8363 | 0.1831 | 0.11528 | 0.0083569 | -0.0090874 | 0.038533 | -0.01747 | -0.012971 | 0.0072803 | -0.1236 | 0.10986 | -0.42572 | 0.018311 | 0.07782 | 0.09613 | -0.13733 | 0.26093 | 0.26093 | -0.31128 | 122.4106 | -0.073242 | 122.7127 | 122.8546 | -0.10528 | 122.525 | 0.07782 | 0.30212 | 122.699 | 123.0972 | 122.9141 | 122.9462 | 122.7127 | 123.0972 | 122.9324 | 122.525 | 122.9462 | 122.7127 | 122.9324 | 122.9141 | 123.0972 | -0.60882 | -0.49438
4210.7344 | 123.0743 | -122.8821 | 0.22888 | 0.22209 | 0.010707 | -0.010796 | 0.04366 | -0.020674 | -0.013826 | 0.0070667 | -0.10986 | 0.10986 | -0.43488 | 0.064087 | 0.064087 | 0.11902 | -0.14191 | 0.27008 | 0.26093 | -0.32044 | 122.4472 | -0.11902 | 122.7722 | 122.9462 | -0.16479 | 122.5616 | 0.032043 | 0.32501 | 122.7402 | 123.1522 | 122.9462 | 122.9919 | 122.7722 | 123.143 | 123.0011 | 122.5616 | 122.9919 | 122.7722 | 123.0011 | 122.9462 | 123.143 | -0.66376 | -0.54932
4212.4531 | 123.1384 | -122.8455 | 0.19684 | 0.12291 | 0.011134 | -0.0071648 | 0.045583 | -0.018325 | -0.014039 | 0.0077075 | -0.16937 | 0.13733 | -0.48065 | -0.032043 | -0.018311 | 0.022888 | -0.032043 | 0.16022 | 0.3067 | -0.34332 | 122.3648 | -0.059509 | 122.6761 | 122.8134 | -0.21515 | 122.5021 | 0.10986 | 0.31128 | 122.8134 | 123.0057 | 122.8271 | 122.9828 | 122.6761 | 123.1522 | 122.8683 | 122.5021 | 122.9828 | 122.6761 | 122.8683 | 122.8271 | 123.1522 | -0.67749 | -0.54016
4214.1562 | 123.175 | -122.8546 | 0.20599 | -0.17464 | 0.0085705 | -0.01571 | 0.038533 | -0.020247 | -0.013185 | 0.0066393 | -0.086975 | 0.10071 | -0.42572 | 0.082397 | 0.10986 | 0.13733 | -0.10071 | 0.32959 | 0.25177 | -0.31128 | 122.4289 | -0.10529 | 122.7676 | 122.937 | -0.096131 | 122.5433 | 0.045776 | 0.33874 | 122.7539 | 123.1842 | 122.9645 | 122.9553 | 122.7676 | 123.1064 | 122.9919 | 122.5433 | 122.9553 | 122.7676 | 122.9919 | 122.9645 | 123.1064 | -0.63171 | -0.51727
4215.8906 | 123.2162 | -122.8455 | 0.17395 | -0.25856 | 0.0079297 | -0.01101 | 0.040883 | -0.021529 | -0.01468 | 0.0064257 | -0.11444 | 0.12817 | -0.44861 | 0.009155 | 0.027466 | 0.022888 | 0.009155 | 0.24261 | 0.29755 | -0.33417 | 122.3969 | -0.045776 | 122.731 | 122.8546 | -0.14648 | 122.5113 | 0.1236 | 0.33417 | 122.8546 | 123.0881 | 122.8729 | 122.9736 | 122.731 | 123.143 | 122.8683 | 122.5113 | 122.9736 | 122.731 | 122.8683 | 122.8729 | 123.143 | -0.62256 | -0.50812
4217.5938 | 123.1934 | -122.8271 | 0.19226 | -0.18227 | 0.0094251 | -0.0080194 | 0.040883 | -0.018965 | -0.014467 | 0.0070667 | -0.091553 | 0.10071 | -0.42572 | 0.068665 | 0.09613 | 0.10071 | -0.041199 | 0.29297 | 0.25635 | -0.31128 | 122.4014 | -0.091553 | 122.7356 | 122.8958 | -0.096131 | 122.5159 | 0.064087 | 0.33417 | 122.7859 | 123.1201 | 122.9233 | 122.9279 | 122.7356 | 123.0835 | 122.9279 | 122.5159 | 122.9279 | 122.7356 | 122.9279 | 122.9233 | 123.0835 | -0.61798 | -0.50354
4219.2969 | 123.2071 | -122.8363 | 0.16479 | 0.031357 | 0.0075025 | -0.012505 | 0.040029 | -0.020461 | -0.012117 | 0.0079211 | -0.13275 | 0.09613 | -0.4303 | 0.045776 | 0.068665 | 0.086975 | -0.10071 | 0.27924 | 0.25177 | -0.32959 | 122.406 | -0.068665 | 122.7036 | 122.8821 | -0.09613 | 122.5067 | 0.086975 | 0.29755 | 122.7356 | 123.1155 | 122.905 | 122.9324 | 122.7036 | 123.0881 | 122.9233 | 122.5067 | 122.9324 | 122.7036 | 122.9233 | 122.905 | 123.0881 | -0.59509 | -0.49438
4221.0312 | 123.1018 | -122.8592 | 0.19684 | 0.1992 | 0.011348 | -0.011651 | 0.044301 | -0.018111 | -0.010194 | 0.0055713 | -0.036621 | 0.09613 | -0.41199 | 0.091553 | 0.09613 | 0.13733 | -0.18768 | 0.29297 | 0.25635 | -0.31586 | 122.4472 | -0.10071 | 122.8226 | 122.9507 | -0.10071 | 122.5433 | 0.05951 | 0.37537 | 122.6715 | 123.1522 | 122.9553 | 122.9553 | 122.8226 | 123.1155 | 122.9965 | 122.5433 | 122.9553 | 122.8226 | 122.9965 | 122.9553 | 123.1155 | -0.60882 | -0.5127
4222.7188 | 123.1293 | -122.8821 | 0.21515 | 0.13054 | 0.011989 | -0.008233 | 0.047719 | -0.017256 | -0.012544 | 0.0066393 | -0.16937 | 0.14191 | -0.48523 | 0 | -0.018311 | 0.022888 | -0.059509 | 0.17395 | 0.29297 | -0.32501 | 122.3969 | -0.073242 | 122.7127 | 122.8821 | -0.23346 | 122.5571 | 0.07782 | 0.31586 | 122.8226 | 123.056 | 122.8638 | 123.024 | 122.7127 | 123.175 | 122.905 | 122.5571 | 123.024 | 122.7127 | 122.905 | 122.8638 | 123.175 | -0.70038 | -0.54016
4224.4375 | 123.0927 | -122.8638 | 0.20599 | 0.15343 | 0.0092115 | -0.0090874 | 0.041738 | -0.018538 | -0.01169 | 0.0066393 | -0.059509 | 0.10071 | -0.42114 | 0.086975 | 0.091553 | 0.12817 | -0.17395 | 0.29297 | 0.25177 | -0.30212 | 122.4426 | -0.10529 | 122.8043 | 122.9507 | -0.11444 | 122.5616 | 0.045776 | 0.36163 | 122.6898 | 123.1567 | 122.9553 | 122.9645 | 122.8043 | 123.1155 | 122.9919 | 122.5616 | 122.9645 | 122.8043 | 122.9919 | 122.9553 | 123.1155 | -0.62714 | -0.50812
4226.1562 | 123.2162 | -122.8455 | 0.1831 | 0.023727 | 0.0096387 | -0.014642 | 0.040883 | -0.018965 | -0.011903 | 0.0072803 | -0.12817 | 0.10529 | -0.43945 | 0.041199 | 0.068665 | 0.091553 | -0.10986 | 0.28381 | 0.27466 | -0.31586 | 122.406 | -0.077819 | 122.7173 | 122.8867 | -0.11444 | 122.5296 | 0.091553 | 0.31128 | 122.7356 | 123.1293 | 122.9141 | 122.9507 | 122.7173 | 123.1201 | 122.937 | 122.5296 | 122.9507 | 122.7173 | 122.937 | 122.9141 | 123.1201 | -0.62256 | -0.49896
4227.8438 | 123.1201 | -122.8546 | 0.19684 | 0.1458 | 0.011348 | -0.011865 | 0.04601 | -0.01982 | -0.012971 | 0.0087757 | -0.14648 | 0.13733 | -0.4715 | 0 | 0 | 0.018311 | -0.073242 | 0.1831 | 0.27008 | -0.35248 | 122.3831 | -0.059509 | 122.7081 | 122.8546 | -0.19684 | 122.5021 | 0.073243 | 0.32501 | 122.7814 | 123.0377 | 122.8546 | 122.9919 | 122.7081 | 123.1247 | 122.8729 | 122.5021 | 122.9919 | 122.7081 | 122.8729 | 122.8546 | 123.1247 | -0.66834 | -0.54932
4229.5469 | 123.1018 | -122.8821 | 0.20599 | -0.037308 | 0.011561 | -0.004815 | 0.047292 | -0.018111 | -0.013612 | 0.0068531 | -0.11444 | 0.16479 | -0.45776 | 0.041199 | 0.036621 | 0.041199 | -0.022888 | 0.21515 | 0.28839 | -0.34332 | 122.4243 | -0.041199 | 122.7676 | 122.9233 | -0.16937 | 122.5388 | 0.082397 | 0.34332 | 122.8592 | 123.0972 | 122.9187 | 123.0469 | 122.7676 | 123.1705 | 122.9233 | 122.5388 | 123.0469 | 122.7676 | 122.9233 | 122.9187 | 123.1705 | -0.66376 | -0.54932
4231.2344 | 123.175 | -122.85 | 0.1831 | -0.22041 | 0.01028 | -0.0071648 | 0.039388 | -0.01982 | -0.011903 | 0.0055713 | -0.054932 | 0.1236 | -0.41657 | 0.09613 | 0.11902 | 0.13733 | -0.1236 | 0.32959 | 0.25635 | -0.31586 | 122.4335 | -0.059509 | 122.7951 | 122.9462 | -0.064086 | 122.5342 | 0.073243 | 0.36163 | 122.7264 | 123.1796 | 122.9691 | 122.9736 | 122.7951 | 123.1064 | 122.9874 | 122.5342 | 122.9736 | 122.7951 | 122.9874 | 122.9691 | 123.1064 | -0.59967 | -0.49896
4232.9531 | 123.1842 | -122.85 | 0.17853 | -0.22041 | 0.0083569 | -0.0071648 | 0.04131 | -0.020034 | -0.012758 | 0.0068531 | -0.073242 | 0.10071 | -0.4303 | 0.10071 | 0.10529 | 0.13733 | -0.11444 | 0.32959 | 0.25177 | -0.29297 | 122.4197 | -0.07782 | 122.7768 | 122.9507 | -0.073242 | 122.5571 | 0.073242 | 0.35706 | 122.7356 | 123.1796 | 122.9553 | 122.9507 | 122.7768 | 123.1018 | 122.9874 | 122.5571 | 122.9507 | 122.7768 | 122.9874 | 122.9553 | 123.1018 | -0.60883 | -0.4715
4234.6562 | 123.1979 | -122.8363 | 0.20142 | -0.26619 | 0.0083569 | -0.006524 | 0.04131 | -0.020034 | -0.014253 | 0.0066393 | -0.09613 | 0.11902 | -0.44403 | 0.059509 | 0.064087 | 0.082397 | -0.027466 | 0.27466 | 0.28381 | -0.33875 | 122.3923 | -0.082397 | 122.7402 | 122.8958 | -0.13733 | 122.4976 | 0.082397 | 0.3479 | 122.8088 | 123.111 | 122.9004 | 122.9553 | 122.7402 | 123.1201 | 122.9187 | 122.4976 | 122.9553 | 122.7402 | 122.9187 | 122.9004 | 123.1201 | -0.64545 | -0.54016
4236.3594 | 123.23 | -122.8271 | 0.17853 | -0.20515 | 0.010493 | -0.014001 | 0.041524 | -0.018752 | -0.012758 | 0.0055713 | -0.14191 | 0.15106 | -0.45319 | -0.004578 | 0.013733 | 0.004578 | 0.027466 | 0.21515 | 0.30212 | -0.36163 | 122.374 | -0.027466 | 122.6852 | 122.8226 | -0.16479 | 122.4655 | 0.1236 | 0.31128 | 122.8546 | 123.0423 | 122.8409 | 122.9782 | 122.6852 | 123.1293 | 122.8317 | 122.4655 | 122.9782 | 122.6852 | 122.8317 | 122.8409 | 123.1293 | -0.63171 | -0.54016
4238.0625 | 123.1796 | -122.8271 | 0.17395 | -0.17464 | 0.010921 | -0.012719 | 0.038961 | -0.019179 | -0.012117 | 0.0077075 | -0.07782 | 0.11444 | -0.4303 | 0.10071 | 0.14191 | 0.14648 | -0.15106 | 0.35248 | 0.24261 | -0.31586 | 122.3969 | -0.059509 | 122.7493 | 122.9279 | -0.032043 | 122.5113 | 0.068665 | 0.35248 | 122.6761 | 123.1796 | 122.9691 | 122.9416 | 122.7493 | 123.0698 | 122.9736 | 122.5113 | 122.9416 | 122.7493 | 122.9736 | 122.9691 | 123.0698 | -0.60425 | -0.48981
4239.75 | 123.1934 | -122.85 | 0.16937 | -0.10597 | 0.0098523 | -0.011437 | 0.040883 | -0.020888 | -0.013185 | 0.0077075 | -0.086975 | 0.14191 | -0.41657 | 0.10529 | 0.12817 | 0.16479 | -0.15106 | 0.33417 | 0.25177 | -0.32501 | 122.4335 | -0.027466 | 122.7631 | 122.9553 | -0.041199 | 122.525 | 0.082397 | 0.32959 | 122.699 | 123.1842 | 122.9782 | 122.9919 | 122.7631 | 123.1018 | 123.0148 | 122.525 | 122.9919 | 122.7631 | 123.0148 | 122.9782 | 123.1018 | -0.58594 | -0.49439
4241.4531 | 123.0881 | -122.8729 | 0.19684 | 0.20683 | 0.011348 | -0.0033196 | 0.045369 | -0.018965 | -0.01233 | 0.0092029 | -0.054932 | 0.082397 | -0.41199 | 0.10071 | 0.09613 | 0.13275 | -0.19226 | 0.30212 | 0.24261 | -0.3067 | 122.4609 | -0.11444 | 122.818 | 122.9736 | -0.10071 | 122.5662 | 0.045777 | 0.35706 | 122.6807 | 123.175 | 122.9691 | 122.9553 | 122.818 | 123.1155 | 123.0057 | 122.5662 | 122.9553 | 122.818 | 123.0057 | 122.9691 | 123.1155 | -0.60882 | -0.50354
4243.1406 | 123.1842 | -122.85 | 0.19226 | -0.20515 | 0.010493 | -0.0095148 | 0.044301 | -0.020888 | -0.014894 | 0.0070667 | -0.15564 | 0.14648 | -0.47607 | 0.022888 | 0.013733 | 0.027466 | 0 | 0.2243 | 0.28381 | -0.32044 | 122.374 | -0.045777 | 122.6944 | 122.8729 | -0.17853 | 122.5296 | 0.091552 | 0.32043 | 122.85 | 123.0743 | 122.8638 | 122.9965 | 122.6944 | 123.1338 | 122.8775 | 122.5296 | 122.9965 | 122.6944 | 122.8775 | 122.8638 | 123.1338 | -0.66834 | -0.5127
4244.8594 | 123.143 | -122.8592 | 0.21515 | 0.046615 | 0.010707 | -0.012292 | 0.046651 | -0.019179 | -0.012971 | 0.0087757 | -0.14191 | 0.13275 | -0.47607 | -0.032043 | -0.032043 | -0.004578 | -0.009155 | 0.15106 | 0.27008 | -0.34332 | 122.3831 | -0.082398 | 122.7173 | 122.8271 | -0.24719 | 122.5159 | 0.054932 | 0.33417 | 122.85 | 123.0103 | 122.8271 | 122.9919 | 122.7173 | 123.1293 | 122.8546 | 122.5159 | 122.9919 | 122.7173 | 122.8546 | 122.8271 | 123.1293 | -0.69122 | -0.55847
4246.5469 | 123.0927 | -122.8775 | 0.20142 | -0.083084 | 0.012629 | -0.009942 | 0.045369 | -0.019179 | -0.013826 | 0.0068531 | -0.10529 | 0.13733 | -0.4715 | 0.050354 | 0.036621 | 0.045776 | -0.032043 | 0.2243 | 0.27008 | -0.33417 | 122.406 | -0.064087 | 122.7722 | 122.9279 | -0.1648 | 122.5433 | 0.068665 | 0.36621 | 122.8455 | 123.1018 | 122.9141 | 123.0148 | 122.7722 | 123.1476 | 122.9233 | 122.5433 | 123.0148 | 122.7722 | 122.9233 | 122.9141 | 123.1476 | -0.67291 | -0.53558
4248.2344 | 123.1705 | -122.8409 | 0.21515 | -0.1899 | 0.011134 | -0.010583 | 0.043233 | -0.019179 | -0.013826 | 0.0074939 | -0.16937 | 0.16479 | -0.4715 | 0.013733 | 0.018311 | 0.041199 | 0.022888 | 0.2243 | 0.28381 | -0.33417 | 122.3694 | -0.050354 | 122.6715 | 122.8546 | -0.19684 | 122.5067 | 0.068664 | 0.30212 | 122.8638 | 123.0652 | 122.8592 | 123.0057 | 122.6715 | 123.1247 | 122.8821 | 122.5067 | 123.0057 | 122.6715 | 122.8821 | 122.8592 | 123.1247 | -0.68665 | -0.54932
4249.9219 | 123.2071 | -122.8088 | 0.20142 | 0.054245 | 0.010707 | -0.012078 | 0.038747 | -0.020034 | -0.013185 | 0.0089893 | -0.13733 | 0.1236 | -0.43488 | 0.032043 | 0.073242 | 0.10071 | -0.11444 | 0.25177 | 0.27924 | -0.31586 | 122.374 | -0.07782 | 122.6715 | 122.8409 | -0.12817 | 122.493 | 0.07782 | 0.29755 | 122.6944 | 123.0606 | 122.8821 | 122.9324 | 122.6715 | 123.0881 | 122.9095 | 122.493 | 122.9324 | 122.6715 | 122.9095 | 122.8821 | 123.0881 | -0.63629 | -0.51727
4251.6094 | 123.111 | -122.8821 | 0.21515 | 0.11528 | 0.0085705 | -0.01336 | 0.039601 | -0.021529 | -0.010835 | 0.0081347 | -0.091553 | 0.10071 | -0.41657 | 0.068665 | 0.086975 | 0.11444 | -0.16479 | 0.27924 | 0.26093 | -0.32959 | 122.4655 | -0.11444 | 122.7905 | 122.9507 | -0.12817 | 122.5525 | 0.045776 | 0.32501 | 122.7173 | 123.1613 | 122.9691 | 122.9828 | 122.7905 | 123.143 | 122.9965 | 122.5525 | 122.9828 | 122.7905 | 122.9965 | 122.9691 | 123.143 | -0.63171 | -0.54474
4253.2969 | 123.0743 | -122.8638 | 0.21515 | 0.20683 | 0.010707 | -0.0086602 | 0.046651 | -0.019393 | -0.012758 | 0.0074939 | -0.086975 | 0.09613 | -0.44403 | 0.07782 | 0.068665 | 0.1236 | -0.15564 | 0.27008 | 0.26093 | -0.29297 | 122.4197 | -0.11902 | 122.7768 | 122.9416 | -0.14648 | 122.5708 | 0.045776 | 0.35706 | 122.7081 | 123.1339 | 122.9324 | 122.9599 | 122.7768 | 123.1247 | 122.9874 | 122.5708 | 122.9599 | 122.7768 | 122.9874 | 122.9324 | 123.1247 | -0.65918 | -0.50812
4254.9844 | 123.1934 | -122.8409 | 0.17853 | -0.25856 | 0.0066479 | -0.012292 | 0.039815 | -0.020888 | -0.012544 | 0.0074939 | -0.09613 | 0.11902 | -0.43945 | 0.050354 | 0.082397 | 0.086975 | -0.054932 | 0.3067 | 0.28381 | -0.33417 | 122.4014 | -0.059509 | 122.7448 | 122.8912 | -0.096131 | 122.5067 | 0.10528 | 0.34332 | 122.7859 | 123.1476 | 122.9233 | 122.9599 | 122.7448 | 123.1247 | 122.9279 | 122.5067 | 122.9599 | 122.7448 | 122.9279 | 122.9233 | 123.1247 | -0.61798 | -0.5127
4256.7188 | 123.1064 | -122.8683 | 0.20599 | 0.16106 | 0.0092115 | -0.0088738 | 0.046651 | -0.017897 | -0.013612 | 0.0066393 | -0.16022 | 0.1236 | -0.47607 | 0.018311 | 0.036621 | 0.050354 | -0.10529 | 0.21057 | 0.27008 | -0.31128 | 122.3923 | -0.082398 | 122.7081 | 122.8867 | -0.16937 | 122.5571 | 0.064087 | 0.31586 | 122.7631 | 123.0789 | 122.905 | 122.9919 | 122.7081 | 123.1384 | 122.9187 | 122.5571 | 122.9919 | 122.7081 | 122.9187 | 122.905 | 123.1384 | -0.68207 | -0.51727
4258.4062 | 123.1201 | -122.8775 | 0.20142 | 0.13817 | 0.010707 | -0.013146 | 0.041738 | -0.018325 | -0.011262 | 0.0077075 | -0.082397 | 0.11902 | -0.43488 | 0.073242 | 0.10071 | 0.11444 | -0.16479 | 0.27466 | 0.26093 | -0.31586 | 122.4426 | -0.082397 | 122.7951 | 122.9507 | -0.10071 | 122.5616 | 0.059509 | 0.35248 | 122.7127 | 123.1522 | 122.9782 | 122.9965 | 122.7951 | 123.1384 | 122.9919 | 122.5616 | 122.9965 | 122.7951 | 122.9919 | 122.9782 | 123.1384 | -0.63629 | -0.51727
4260.125 | 123.1018 | -122.8821 | 0.21515 | -0.13649 | 0.010707 | -0.0078058 | 0.046651 | -0.019606 | -0.014253 | 0.0053577 | -0.11444 | 0.12817 | -0.4715 | 0.036621 | 0.041199 | 0.050354 | -0.027466 | 0.21515 | 0.29297 | -0.32044 | 122.4106 | -0.086975 | 122.7676 | 122.9187 | -0.17395 | 122.5616 | 0.07782 | 0.35706 | 122.8546 | 123.0972 | 122.9233 | 123.0103 | 122.7676 | 123.175 | 122.9324 | 122.5616 | 123.0103 | 122.7676 | 122.9324 | 122.9233 | 123.175 | -0.68665 | -0.53558
4261.8125 | 123.1842 | -122.8455 | 0.18768 | -0.18227 | 0.010921 | -0.013787 | 0.043447 | -0.019179 | -0.011262 | 0.0066393 | -0.15106 | 0.15106 | -0.48065 | -0.004578 | 0.018311 | 0.004578 | 0.036621 | 0.21973 | 0.30212 | -0.33417 | 122.3648 | -0.036621 | 122.6944 | 122.8409 | -0.16937 | 122.5113 | 0.11444 | 0.32959 | 122.8821 | 123.0652 | 122.8638 | 122.9965 | 122.6944 | 123.1476 | 122.85 | 122.5113 | 122.9965 | 122.6944 | 122.85 | 122.8638 | 123.1476 | -0.66834 | -0.52185
4263.5 | 123.0881 | -122.9004 | 0.19684 | 0.13054 | 0.011561 | -0.0080194 | 0.042806 | -0.018538 | -0.015107 | 0.0094165 | -0.064087 | 0.086975 | -0.4303 | 0.086975 | 0.091553 | 0.13733 | -0.19226 | 0.28381 | 0.26093 | -0.29755 | 122.4701 | -0.10986 | 122.8363 | 122.9874 | -0.10529 | 122.6028 | 0.064087 | 0.36621 | 122.7081 | 123.1842 | 122.9919 | 122.9874 | 122.8363 | 123.1613 | 123.0377 | 122.6028 | 122.9874 | 122.8363 | 123.0377 | 122.9919 | 123.1613 | -0.62714 | -0.49438
4265.1875 | 123.0972 | -122.8821 | 0.2243 | -0.029679 | 0.011134 | -0.011224 | 0.047292 | -0.016616 | -0.013612 | 0.0085619 | -0.11902 | 0.11444 | -0.46692 | 0.004578 | 0.027466 | 0.027466 | -0.009155 | 0.19226 | 0.27008 | -0.35248 | 122.4152 | -0.10986 | 122.7631 | 122.8867 | -0.19684 | 122.5296 | 0.045777 | 0.3479 | 122.8729 | 123.0743 | 122.9095 | 122.9965 | 122.7631 | 123.1522 | 122.9095 | 122.5296 | 122.9965 | 122.7631 | 122.9095 | 122.9095 | 123.1522 | -0.69122 | -0.57678
4266.9375 | 123.1934 | -122.8546 | 0.18768 | 0.077133 | 0.010493 | -0.01336 | 0.038961 | -0.018965 | -0.012117 | 0.0059985 | -0.13733 | 0.1236 | -0.43945 | 0.018311 | 0.073242 | 0.09613 | -0.11902 | 0.25635 | 0.26093 | -0.31586 | 122.4152 | -0.064087 | 122.7173 | 122.8729 | -0.11444 | 122.5388 | 0.073242 | 0.30212 | 122.7356 | 123.111 | 122.9279 | 122.9782 | 122.7173 | 123.1155 | 122.9507 | 122.5388 | 122.9782 | 122.7173 | 122.9507 | 122.9279 | 123.1155 | -0.62714 | -0.50354
4268.625 | 123.2162 | -122.8271 | 0.16937 | 0.038986 | 0.0096387 | -0.015069 | 0.04067 | -0.020674 | -0.01169 | 0.0092029 | -0.13275 | 0.13275 | -0.42114 | 0.036621 | 0.059509 | 0.086975 | -0.10986 | 0.26093 | 0.2655 | -0.32959 | 122.406 | -0.036622 | 122.6944 | 122.8638 | -0.10986 | 122.4976 | 0.09613 | 0.28839 | 122.7173 | 123.0881 | 122.8867 | 122.9599 | 122.6944 | 123.0927 | 122.9141 | 122.4976 | 122.9599 | 122.6944 | 122.9141 | 122.8867 | 123.0927 | -0.59052 | -0.49896
4270.3125 | 123.1796 | -122.8455 | 0.18768 | 0.069504 | 0.0085705 | -0.016778 | 0.040029 | -0.01982 | -0.012971 | 0.0068531 | -0.10986 | 0.11902 | -0.41199 | 0.045776 | 0.068665 | 0.091553 | -0.13275 | 0.27466 | 0.25177 | -0.3067 | 122.4335 | -0.068664 | 122.7356 | 122.8912 | -0.11902 | 122.5388 | 0.064087 | 0.30212 | 122.7127 | 123.1201 | 122.9141 | 122.9645 | 122.7356 | 123.0972 | 122.937 | 122.5388 | 122.9645 | 122.7356 | 122.937 | 122.9141 | 123.0972 | -0.59967 | -0.49438
4272 | 123.111 | -122.8821 | 0.21057 | 0.16106 | 0.0096387 | -0.0073786 | 0.043233 | -0.018752 | -0.012971 | 0.0079211 | -0.068665 | 0.091553 | -0.42114 | 0.09613 | 0.091553 | 0.12817 | -0.18768 | 0.30212 | 0.24261 | -0.31586 | 122.4609 | -0.11902 | 122.8134 | 122.9782 | -0.11902 | 122.5662 | 0.032044 | 0.35248 | 122.6944 | 123.1842 | 122.9736 | 122.9736 | 122.8134 | 123.1247 | 123.0103 | 122.5662 | 122.9736 | 122.8134 | 123.0103 | 122.9736 | 123.1247 | -0.63171 | -0.52643
4273.7031 | 123.0881 | -122.8683 | 0.20142 | 0.21446 | 0.010921 | -0.012933 | 0.045369 | -0.017684 | -0.015107 | 0.0066393 | -0.11902 | 0.12817 | -0.45776 | 0.054932 | 0.064087 | 0.09613 | -0.14191 | 0.24719 | 0.2655 | -0.32044 | 122.4106 | -0.073242 | 122.7493 | 122.9233 | -0.13733 | 122.5479 | 0.064087 | 0.33875 | 122.7264 | 123.1155 | 122.9324 | 122.9965 | 122.7493 | 123.1338 | 122.9645 | 122.5479 | 122.9965 | 122.7493 | 122.9645 | 122.9324 | 123.1338 | -0.65918 | -0.52185
4275.3906 | 123.1338 | -122.8592 | 0.19684 | 0.13054 | 0.011348 | -0.011651 | 0.046651 | -0.01982 | -0.014039 | 0.0072803 | -0.16937 | 0.14648 | -0.48065 | -0.013733 | -0.004578 | 0.027466 | -0.068665 | 0.17395 | 0.27924 | -0.35706 | 122.3785 | -0.050354 | 122.6898 | 122.8455 | -0.20142 | 122.5021 | 0.082398 | 0.31128 | 122.7905 | 123.0331 | 122.8546 | 123.0057 | 122.6898 | 123.1384 | 122.8867 | 122.5021 | 123.0057 | 122.6898 | 122.8867 | 122.8546 | 123.1384 | -0.67749 | -0.55389
4277.0938 | 123.0881 | -122.8592 | 0.2243 | 0.1992 | 0.011348 | -0.0069512 | 0.041738 | -0.019179 | -0.012544 | 0.0077075 | -0.054932 | 0.10071 | -0.41657 | 0.082397 | 0.091553 | 0.12817 | -0.17853 | 0.27924 | 0.26093 | -0.30212 | 122.4426 | -0.1236 | 122.8043 | 122.9416 | -0.13275 | 122.5571 | 0.036621 | 0.36163 | 122.6807 | 123.1384 | 122.9507 | 122.9599 | 122.8043 | 123.1201 | 122.9874 | 122.5571 | 122.9599 | 122.8043 | 122.9874 | 122.9507 | 123.1201 | -0.64087 | -0.52643
4278.7812 | 123.0698 | -122.8775 | 0.21515 | 0.17632 | 0.0083569 | -0.0046014 | 0.043447 | -0.018752 | -0.011049 | 0.0083483 | -0.07782 | 0.12817 | -0.44403 | 0.064087 | 0.082397 | 0.1236 | -0.16022 | 0.27008 | 0.26093 | -0.3067 | 122.4335 | -0.086975 | 122.7997 | 122.9416 | -0.13275 | 122.5708 | 0.045776 | 0.36621 | 122.7173 | 123.1476 | 122.9599 | 123.0057 | 122.7997 | 123.1384 | 123.0011 | 122.5708 | 123.0057 | 122.7997 | 123.0011 | 122.9599 | 123.1384 | -0.65918 | -0.52185
4280.4688 | 123.0835 | -122.8683 | 0.22888 | 0.19157 | 0.0098523 | -0.0093012 | 0.04366 | -0.019393 | -0.012971 | 0.0053577 | -0.064087 | 0.091553 | -0.41657 | 0.091553 | 0.10529 | 0.15106 | -0.20599 | 0.29755 | 0.24719 | -0.30212 | 122.4518 | -0.13733 | 122.8043 | 122.9599 | -0.1236 | 122.5662 | 0.01831 | 0.35248 | 122.6624 | 123.1659 | 122.9736 | 122.9599 | 122.8043 | 123.1155 | 123.0194 | 122.5662 | 122.9599 | 122.8043 | 123.0194 | 122.9736 | 123.1155 | -0.64545 | -0.53101
4282.1562 | 123.1018 | -122.8912 | 0.2243 | -0.10597 | 0.0087841 | -0.0090874 | 0.046651 | -0.020888 | -0.014894 | 0.0066393 | -0.10529 | 0.14648 | -0.46234 | 0.036621 | 0.032043 | 0.054932 | -0.022888 | 0.22888 | 0.29755 | -0.33875 | 122.4289 | -0.07782 | 122.7859 | 122.9279 | -0.19226 | 122.5525 | 0.073242 | 0.35706 | 122.8683 | 123.1201 | 122.9233 | 123.0377 | 122.7859 | 123.1888 | 122.9462 | 122.5525 | 123.0377 | 122.7859 | 122.9462 | 122.9233 | 123.1888 | -0.68664 | -0.56305
4283.8438 | 123.0789 | -122.8867 | 0.21057 | 0.18394 | 0.010493 | -0.0033196 | 0.044301 | -0.019179 | -0.012971 | 0.0066393 | -0.064087 | 0.10529 | -0.41199 | 0.07782 | 0.10986 | 0.15106 | -0.20599 | 0.29297 | 0.2655 | -0.29755 | 122.4747 | -0.10529 | 122.8226 | 122.9645 | -0.10071 | 122.5891 | 0.054932 | 0.3479 | 122.6807 | 123.1796 | 122.9965 | 122.9919 | 122.8226 | 123.1522 | 123.0377 | 122.5891 | 122.9919 | 122.8226 | 123.0377 | 122.9965 | 123.1522 | -0.62256 | -0.50812
4285.7188 | 123.1384 | -122.8409 | 0.20142 | 0.069504 | 0.010066 | -0.0095148 | 0.045156 | -0.020247 | -0.014894 | 0.0059985 | -0.17395 | 0.16479 | -0.46692 | -0.045776 | -0.041199 | -0.018311 | 0 | 0.13733 | 0.29297 | -0.3479 | 122.374 | -0.036621 | 122.6669 | 122.7951 | -0.24262 | 122.493 | 0.091553 | 0.29297 | 122.8409 | 122.9782 | 122.7997 | 123.0057 | 122.6669 | 123.1338 | 122.8226 | 122.493 | 123.0057 | 122.6669 | 122.8226 | 122.7997 | 123.1338 | -0.66834 | -0.54932
4287.6562 | 123.2117 | -122.8363 | 0.17853 | -0.25856 | 0.0092115 | -0.0090874 | 0.03832 | -0.021529 | -0.013612 | 0.0057849 | -0.086975 | 0.13733 | -0.42572 | 0.036621 | 0.073242 | 0.068665 | -0.032043 | 0.28839 | 0.27466 | -0.33417 | 122.4106 | -0.041199 | 122.7493 | 122.8729 | -0.10529 | 122.5021 | 0.09613 | 0.33874 | 122.8043 | 123.1247 | 122.9095 | 122.9736 | 122.7493 | 123.111 | 122.905 | 122.5021 | 122.9736 | 122.7493 | 122.905 | 122.9095 | 123.111 | -0.60425 | -0.5127
4289.625 | 123.1247 | -122.8821 | 0.20142 | -0.1136 | 0.0098523 | -0.01101 | 0.046224 | -0.018752 | -0.013399 | 0.0062121 | -0.09613 | 0.15564 | -0.4715 | 0.041199 | 0.036621 | 0.045776 | -0.022888 | 0.23346 | 0.3067 | -0.33417 | 122.4106 | -0.045776 | 122.7859 | 122.9233 | -0.1648 | 122.5479 | 0.10529 | 0.37537 | 122.8592 | 123.1155 | 122.9187 | 123.0377 | 122.7859 | 123.1888 | 122.9279 | 122.5479 | 123.0377 | 122.7859 | 122.9279 | 122.9187 | 123.1888 | -0.67291 | -0.53558
4291.75 | 123.2346 | -122.8409 | 0.1831 | -0.22804 | 0.011348 | -0.012078 | 0.04366 | -0.01982 | -0.011262 | 0.0057849 | -0.17853 | 0.17395 | -0.4715 | -0.027466 | 0.013733 | 0 | 0.045776 | 0.19684 | 0.30212 | -0.3479 | 122.3694 | -0.009155 | 122.6624 | 122.8134 | -0.16937 | 122.493 | 0.11902 | 0.29297 | 122.8867 | 123.0377 | 122.8546 | 123.0148 | 122.6624 | 123.143 | 122.8409 | 122.493 | 123.0148 | 122.6624 | 122.8409 | 122.8546 | 123.143 | -0.6546 | -0.531
4293.5781 | 123.0835 | -122.8867 | 0.20599 | -0.075455 | 0.011134 | -0.0054558 | 0.044515 | -0.019393 | -0.014253 | 0.0081347 | -0.086975 | 0.15564 | -0.44861 | 0.036621 | 0.032043 | 0.064087 | -0.041199 | 0.2243 | 0.27008 | -0.3479 | 122.4381 | -0.050354 | 122.7997 | 122.9233 | -0.17395 | 122.5388 | 0.064087 | 0.36163 | 122.8455 | 123.111 | 122.9187 | 123.0423 | 122.7997 | 123.1567 | 122.9507 | 122.5388 | 123.0423 | 122.7997 | 122.9507 | 122.9187 | 123.1567 | -0.6546 | -0.55389
4296.4688 | 123.1842 | -122.8409 | 0.18768 | -0.13649 | 0.0079297 | -0.011865 | 0.038747 | -0.021956 | -0.013185 | 0.0079211 | -0.059509 | 0.11902 | -0.41199 | 0.091553 | 0.13275 | 0.13275 | -0.1236 | 0.33875 | 0.25177 | -0.3067 | 122.4289 | -0.068664 | 122.7814 | 122.9324 | -0.054932 | 122.5342 | 0.064087 | 0.35248 | 122.7173 | 123.1796 | 122.9736 | 122.9599 | 122.7814 | 123.0927 | 122.9736 | 122.5342 | 122.9599 | 122.7814 | 122.9736 | 122.9736 | 123.0927 | -0.59967 | -0.49438
4298.5781 | 123.1384 | -122.8775 | 0.20599 | 0.12291 | 0.010066 | -0.0088738 | 0.039601 | -0.021956 | -0.012544 | 0.0079211 | -0.082397 | 0.1236 | -0.43488 | 0.032043 | 0.073242 | 0.10071 | -0.13733 | 0.27924 | 0.27924 | -0.3067 | 122.4426 | -0.082398 | 122.7951 | 122.9095 | -0.13275 | 122.5708 | 0.073242 | 0.35248 | 122.7402 | 123.1567 | 122.9507 | 123.0011 | 122.7951 | 123.1567 | 122.9782 | 122.5708 | 123.0011 | 122.7951 | 122.9782 | 122.9507 | 123.1567 | -0.64087 | -0.5127
4300.2656 | 123.2346 | -122.8317 | 0.1831 | -0.0067901 | 0.0089979 | -0.0093012 | 0.038961 | -0.021315 | -0.010408 | 0.0092029 | -0.11902 | 0.11902 | -0.43488 | 0.027466 | 0.064087 | 0.086975 | -0.11444 | 0.27008 | 0.26093 | -0.31128 | 122.3969 | -0.064086 | 122.7127 | 122.8592 | -0.11902 | 122.5204 | 0.07782 | 0.31586 | 122.7173 | 123.1018 | 122.8958 | 122.9507 | 122.7127 | 123.0927 | 122.9187 | 122.5204 | 122.9507 | 122.7127 | 122.9187 | 122.8958 | 123.0927 | -0.61798 | -0.49438
4301.9531 | 123.2162 | -122.7951 | 0.1831 | -0.029679 | 0.01028 | -0.010583 | 0.041524 | -0.01982 | -0.010835 | 0.0072803 | -0.11902 | 0.11902 | -0.4303 | 0.054932 | 0.082397 | 0.10986 | -0.1236 | 0.31128 | 0.25635 | -0.33875 | 122.3648 | -0.064086 | 122.6761 | 122.85 | -0.10071 | 122.4564 | 0.073243 | 0.31128 | 122.6715 | 123.1064 | 122.8775 | 122.9141 | 122.6761 | 123.0515 | 122.905 | 122.4564 | 122.9141 | 122.6761 | 122.905 | 122.8775 | 123.0515 | -0.6134 | -0.52185
4303.6406 | 123.2071 | -122.8409 | 0.17853 | 0.023727 | 0.010707 | -0.012292 | 0.042806 | -0.020247 | -0.010835 | 0.0079211 | -0.10986 | 0.12817 | -0.41657 | 0.050354 | 0.059509 | 0.09613 | -0.11444 | 0.25635 | 0.25635 | -0.32501 | 122.4243 | -0.050354 | 122.731 | 122.8912 | -0.11902 | 122.5159 | 0.07782 | 0.3067 | 122.7264 | 123.0972 | 122.9004 | 122.9691 | 122.731 | 123.0972 | 122.937 | 122.5159 | 122.9691 | 122.731 | 122.937 | 122.9004 | 123.0972 | -0.59509 | -0.50354
4305.3281 | 123.1247 | -122.8592 | 0.21515 | 0.13817 | 0.011561 | -0.0093012 | 0.043447 | -0.021529 | -0.010835 | 0.0077075 | -0.082397 | 0.1236 | -0.43488 | 0.07782 | 0.073242 | 0.10986 | -0.15564 | 0.28381 | 0.25177 | -0.30212 | 122.4243 | -0.091553 | 122.7768 | 122.937 | -0.14191 | 122.5571 | 0.036621 | 0.35248 | 122.7036 | 123.143 | 122.9324 | 122.9828 | 122.7768 | 123.111 | 122.9691 | 122.5571 | 122.9828 | 122.7768 | 122.9691 | 122.9324 | 123.111 | -0.65002 | -0.51727
4307.0312 | 123.1338 | -122.8638 | 0.21973 | -0.15175 | 0.0098523 | -0.0088738 | 0.047933 | -0.020247 | -0.015321 | 0.0072803 | -0.1236 | 0.16479 | -0.46692 | 0.045776 | 0.027466 | 0.036621 | -0.018311 | 0.22888 | 0.29755 | -0.33417 | 122.3969 | -0.054932 | 122.7402 | 122.9095 | -0.19226 | 122.5296 | 0.077819 | 0.34332 | 122.8455 | 123.0927 | 122.8912 | 123.0286 | 122.7402 | 123.1613 | 122.9004 | 122.5296 | 123.0286 | 122.7402 | 122.9004 | 122.8912 | 123.1613 | -0.68665 | -0.55389
4308.7188 | 123.1064 | -122.8729 | 0.21973 | -0.12123 | 0.011348 | -0.0090874 | 0.04601 | -0.018538 | -0.015535 | 0.0062121 | -0.09613 | 0.14648 | -0.45319 | 0.036621 | 0.050354 | 0.054932 | -0.045776 | 0.23804 | 0.30212 | -0.34332 | 122.4197 | -0.073243 | 122.7768 | 122.9095 | -0.16937 | 122.5296 | 0.082397 | 0.35706 | 122.8271 | 123.111 | 122.9233 | 123.0194 | 122.7768 | 123.175 | 122.9279 | 122.5296 | 123.0194 | 122.7768 | 122.9279 | 122.9233 | 123.175 | -0.67291 | -0.56305
4310.4219 | 123.0881 | -122.8775 | 0.18768 | 0.17632 | 0.010707 | -0.0095148 | 0.044515 | -0.019393 | -0.011903 | 0.0077075 | -0.064087 | 0.13275 | -0.43945 | 0.082397 | 0.086975 | 0.13275 | -0.16937 | 0.27924 | 0.23804 | -0.31586 | 122.438 | -0.054932 | 122.8134 | 122.9599 | -0.10071 | 122.5616 | 0.050354 | 0.37537 | 122.7081 | 123.1567 | 122.9645 | 123.0103 | 122.8134 | 123.1155 | 123.0103 | 122.5616 | 123.0103 | 122.8134 | 123.0103 | 122.9645 | 123.1155 | -0.62714 | -0.50354
4312.125 | 123.1522 | -122.8683 | 0.21057 | 0.16869 | 0.01028 | -0.010796 | 0.043233 | -0.018538 | -0.014467 | 0.0098437 | -0.17853 | 0.15564 | -0.46692 | -0.041199 | -0.018311 | 0.004578 | -0.013733 | 0.15564 | 0.28839 | -0.37079 | 122.4014 | -0.054931 | 122.6898 | 122.8271 | -0.22888 | 122.4976 | 0.07782 | 0.28839 | 122.8546 | 123.024 | 122.85 | 123.024 | 122.6898 | 123.1567 | 122.8729 | 122.4976 | 123.024 | 122.6898 | 122.8729 | 122.85 | 123.1567 | -0.67749 | -0.58136
4313.8125 | 123.1064 | -122.8821 | 0.21515 | -0.022049 | 0.010493 | -0.0067376 | 0.044301 | -0.018111 | -0.014039 | 0.0070667 | -0.11444 | 0.13733 | -0.44403 | 0.004578 | 0.018311 | 0.027466 | -0.022888 | 0.20142 | 0.28839 | -0.33875 | 122.438 | -0.07782 | 122.7676 | 122.8867 | -0.19684 | 122.5433 | 0.073242 | 0.32959 | 122.8592 | 123.0835 | 122.9004 | 123.0194 | 122.7676 | 123.1705 | 122.9095 | 122.5433 | 123.0194 | 122.7676 | 122.9095 | 122.9004 | 123.1705 | -0.65918 | -0.55389
4315.5156 | 123.1201 | -122.8775 | 0.2243 | -0.0067901 | 0.0098523 | -0.0039606 | 0.045156 | -0.018538 | -0.013826 | 0.0089893 | -0.11444 | 0.17395 | -0.44861 | -0.013733 | 0.013733 | 0.018311 | -0.009155 | 0.1831 | 0.28839 | -0.33417 | 122.4289 | -0.050354 | 122.7631 | 122.8638 | -0.21057 | 122.5433 | 0.064087 | 0.33417 | 122.8683 | 123.0606 | 122.8912 | 123.0515 | 122.7631 | 123.1659 | 122.8958 | 122.5433 | 123.0515 | 122.7631 | 122.8958 | 122.8912 | 123.1659 | -0.67291 | -0.55847
4317.2031 | 123.0927 | -122.8821 | 0.19684 | -0.0067901 | 0.011348 | -0.01101 | 0.044515 | -0.018111 | -0.01233 | 0.0070667 | -0.091553 | 0.16022 | -0.43945 | 0 | 0.013733 | 0.036621 | -0.009155 | 0.1831 | 0.30212 | -0.32501 | 122.4426 | -0.036621 | 122.7905 | 122.8821 | -0.18311 | 122.5571 | 0.10529 | 0.3479 | 122.8729 | 123.0652 | 122.8958 | 123.0423 | 122.7905 | 123.1842 | 122.9187 | 122.5571 | 123.0423 | 122.7905 | 122.9187 | 122.8958 | 123.1842 | -0.63629 | -0.52185
4318.8906 | 123.0835 | -122.8683 | 0.2243 | 0.18394 | 0.0087841 | -0.010583 | 0.038961 | -0.016188 | -0.011476 | 0.0074939 | -0.064087 | 0.11444 | -0.41199 | 0.068665 | 0.10986 | 0.14648 | -0.1831 | 0.29755 | 0.26093 | -0.3067 | 122.4564 | -0.10986 | 122.8043 | 122.937 | -0.11444 | 122.5616 | 0.036621 | 0.3479 | 122.6852 | 123.1659 | 122.9782 | 122.9828 | 122.8043 | 123.1293 | 123.0148 | 122.5616 | 122.9828 | 122.8043 | 123.0148 | 122.9782 | 123.1293 | -0.63629 | -0.53101
4320.5781 | 123.1201 | -122.8638 | 0.21515 | 0.13054 | 0.0092115 | -0.0088738 | 0.037252 | -0.018965 | -0.010621 | 0.0079211 | -0.082397 | 0.13275 | -0.42114 | 0.068665 | 0.11902 | 0.11902 | -0.15564 | 0.27924 | 0.25177 | -0.32959 | 122.4426 | -0.082398 | 122.7814 | 122.9324 | -0.09613 | 122.5342 | 0.036621 | 0.33875 | 122.7081 | 123.143 | 122.9828 | 122.9965 | 122.7814 | 123.1155 | 122.9828 | 122.5342 | 122.9965 | 122.7814 | 122.9828 | 122.9828 | 123.1155 | -0.63629 | -0.54474
4322.2656 | 123.111 | -122.8867 | 0.20599 | 0.13054 | 0.011561 | -0.0090874 | 0.045583 | -0.017256 | -0.014039 | 0.0077075 | -0.12817 | 0.15106 | -0.46234 | 0 | 0.018311 | 0.059509 | -0.082397 | 0.18768 | 0.27008 | -0.34332 | 122.4243 | -0.054932 | 122.7585 | 122.8867 | -0.18768 | 122.5433 | 0.064087 | 0.33417 | 122.8043 | 123.0743 | 122.905 | 123.0377 | 122.7585 | 123.1567 | 122.9462 | 122.5433 | 123.0377 | 122.7585 | 122.9462 | 122.905 | 123.1567 | -0.66834 | -0.54932
4323.9688 | 123.1842 | -122.8271 | 0.18768 | -0.12886 | 0.0077161 | -0.013146 | 0.038106 | -0.01982 | -0.012544 | 0.0066393 | -0.064087 | 0.13275 | -0.42114 | 0.091553 | 0.11444 | 0.14648 | -0.12817 | 0.33417 | 0.2655 | -0.30212 | 122.406 | -0.054932 | 122.7631 | 122.9187 | -0.073242 | 122.525 | 0.07782 | 0.35706 | 122.699 | 123.1613 | 122.9416 | 122.9599 | 122.7631 | 123.0927 | 122.9736 | 122.525 | 122.9599 | 122.7631 | 122.9736 | 122.9416 | 123.0927 | -0.60883 | -0.48981
4325.6719 | 123.1979 | -122.8317 | 0.20599 | -0.22804 | 0.0072889 | -0.013574 | 0.039388 | -0.018111 | -0.013612 | 0.0064257 | -0.073242 | 0.12817 | -0.42114 | 0.064087 | 0.082397 | 0.10529 | -0.064087 | 0.31586 | 0.25635 | -0.31128 | 122.4106 | -0.07782 | 122.7585 | 122.8958 | -0.1236 | 122.5204 | 0.050354 | 0.3479 | 122.7676 | 123.1476 | 122.9141 | 122.9599 | 122.7585 | 123.0881 | 122.937 | 122.5204 | 122.9599 | 122.7585 | 122.937 | 122.9141 | 123.0881 | -0.62714 | -0.51727
4327.375 | 123.1705 | -122.85 | 0.18768 | -0.21278 | 0.010066 | -0.016137 | 0.039815 | -0.021743 | -0.014039 | 0.0064257 | -0.045776 | 0.10529 | -0.40283 | 0.091553 | 0.11444 | 0.13275 | -0.12817 | 0.34332 | 0.2655 | -0.31128 | 122.4472 | -0.082397 | 122.8043 | 122.9416 | -0.073242 | 122.5388 | 0.07782 | 0.35706 | 122.7219 | 123.1934 | 122.9645 | 122.9553 | 122.8043 | 123.1155 | 122.9828 | 122.5388 | 122.9553 | 122.8043 | 122.9828 | 122.9645 | 123.1155 | -0.59052 | -0.49896
4329.0625 | 123.1293 | -122.8912 | 0.21515 | 0.023727 | 0.011989 | -0.0033196 | 0.048574 | -0.018538 | -0.015748 | 0.0083483 | -0.10529 | 0.14191 | -0.44403 | -0.004578 | -0.009155 | 0 | -0.022888 | 0.16479 | 0.29755 | -0.34332 | 122.4472 | -0.073242 | 122.7859 | 122.8867 | -0.2243 | 122.5479 | 0.082397 | 0.33875 | 122.8683 | 123.056 | 122.8821 | 123.0331 | 122.7859 | 123.1888 | 122.8912 | 122.5479 | 123.0331 | 122.7859 | 122.8912 | 122.8821 | 123.1888 | -0.65918 | -0.55847
4330.7812 | 123.0927 | -122.8867 | 0.2243 | -0.083084 | 0.0092115 | -0.008233 | 0.04601 | -0.020461 | -0.014039 | 0.0092029 | -0.09613 | 0.16022 | -0.46234 | 0.027466 | 0.041199 | 0.059509 | -0.041199 | 0.26093 | 0.28381 | -0.31586 | 122.4243 | -0.064087 | 122.7905 | 122.9141 | -0.18311 | 122.5708 | 0.059509 | 0.36621 | 122.8455 | 123.1476 | 122.9279 | 123.0469 | 122.7905 | 123.1705 | 122.9462 | 122.5708 | 123.0469 | 122.7905 | 122.9462 | 122.9279 | 123.1705 | -0.68664 | -0.54016
4332.5312 | 123.0972 | -122.8821 | 0.21057 | 0.20683 | 0.01028 | -0.010369 | 0.042806 | -0.018111 | -0.013612 | 0.0057849 | -0.045776 | 0.13275 | -0.40283 | 0.073242 | 0.10986 | 0.13275 | -0.20599 | 0.28839 | 0.24719 | -0.3067 | 122.4792 | -0.07782 | 122.8363 | 122.9553 | -0.10071 | 122.5754 | 0.036621 | 0.35706 | 122.6761 | 123.1705 | 122.9919 | 123.0148 | 122.8363 | 123.1293 | 123.0148 | 122.5754 | 123.0148 | 122.8363 | 123.0148 | 122.9919 | 123.1293 | -0.6134 | -0.51727
4334.2188 | 123.1018 | -122.8867 | 0.19684 | 0.16106 | 0.0094251 | -0.012933 | 0.043233 | -0.019606 | -0.013826 | 0.0087757 | -0.10986 | 0.15106 | -0.43945 | 0.041199 | 0.064087 | 0.10071 | -0.13733 | 0.2655 | 0.27924 | -0.32959 | 122.4472 | -0.045776 | 122.7768 | 122.9279 | -0.13275 | 122.5571 | 0.082398 | 0.32959 | 122.7493 | 123.1522 | 122.9507 | 123.0377 | 122.7768 | 123.1659 | 122.9874 | 122.5571 | 123.0377 | 122.7768 | 122.9874 | 122.9507 | 123.1659 | -0.63629 | -0.52643
4335.9688 | 123.111 | -122.9095 | 0.23804 | -0.1136 | 0.011775 | -0.0097284 | 0.047078 | -0.018325 | -0.014039 | 0.0077075 | -0.10071 | 0.15106 | -0.44861 | 0.022888 | 0.045776 | 0.050354 | -0.027466 | 0.23346 | 0.28839 | -0.34332 | 122.4609 | -0.086975 | 122.8088 | 122.9324 | -0.19226 | 122.5662 | 0.050354 | 0.3479 | 122.8821 | 123.143 | 122.9553 | 123.0606 | 122.8088 | 123.1979 | 122.9599 | 122.5662 | 123.0606 | 122.8088 | 122.9599 | 122.9553 | 123.1979 | -0.68664 | -0.58136
4337.6562 | 123.2391 | -122.8409 | 0.16937 | -0.25093 | 0.0070751 | -0.013574 | 0.038961 | -0.021102 | -0.014467 | 0.0062121 | -0.13733 | 0.14648 | -0.4303 | -0.009155 | 0.018311 | 0.018311 | 0.027466 | 0.2243 | 0.3067 | -0.36621 | 122.4106 | -0.022889 | 122.7036 | 122.8317 | -0.15106 | 122.4747 | 0.13733 | 0.29297 | 122.8683 | 123.0652 | 122.8592 | 122.9874 | 122.7036 | 123.1476 | 122.8592 | 122.4747 | 122.9874 | 122.7036 | 122.8592 | 122.8592 | 123.1476 | -0.59967 | -0.53558
4339.375 | 123.0927 | -122.8912 | 0.22888 | -0.083084 | 0.010707 | -0.013574 | 0.044301 | -0.020247 | -0.016389 | 0.0068531 | -0.086975 | 0.14648 | -0.43488 | 0.022888 | 0.041199 | 0.045776 | -0.032043 | 0.23346 | 0.27924 | -0.32501 | 122.4564 | -0.082398 | 122.8043 | 122.9141 | -0.18768 | 122.5662 | 0.050354 | 0.3479 | 122.8592 | 123.1247 | 122.9324 | 123.0377 | 122.8043 | 123.1705 | 122.937 | 122.5662 | 123.0377 | 122.8043 | 122.937 | 122.9324 | 123.1705 | -0.66376 | -0.55389
4341.0781 | 123.2254 | -122.8317 | 0.1831 | -0.27382 | 0.01028 | -0.010369 | 0.038533 | -0.01982 | -0.01468 | 0.0055713 | -0.068665 | 0.16022 | -0.42114 | 0.041199 | 0.064087 | 0.082397 | -0.022888 | 0.26093 | 0.28839 | -0.34332 | 122.4106 | -0.022888 | 122.7631 | 122.8729 | -0.11902 | 122.4884 | 0.10529 | 0.35248 | 122.8088 | 123.0927 | 122.8958 | 122.9919 | 122.7631 | 123.1201 | 122.9141 | 122.4884 | 122.9919 | 122.7631 | 122.9141 | 122.8958 | 123.1201 | -0.60425 | -0.52643
4342.7656 | 123.1842 | -122.8363 | 0.19226 | 0.069504 | 0.0096387 | -0.01101 | 0.03832 | -0.018111 | -0.012971 | 0.0062121 | -0.07782 | 0.15106 | -0.40283 | 0.032043 | 0.073242 | 0.07782 | -0.1236 | 0.27008 | 0.27924 | -0.32501 | 122.4335 | -0.041199 | 122.7585 | 122.8683 | -0.11902 | 122.5113 | 0.086975 | 0.32501 | 122.7127 | 123.1064 | 122.9095 | 122.9874 | 122.7585 | 123.1155 | 122.9141 | 122.5113 | 122.9874 | 122.7585 | 122.9141 | 122.9095 | 123.1155 | -0.59509 | -0.51727
4344.4688 | 123.1842 | -122.8592 | 0.16479 | 0.069504 | 0.01028 | -0.010796 | 0.041951 | -0.019179 | -0.013612 | 0.0085619 | -0.091553 | 0.12817 | -0.41657 | 0.050354 | 0.068665 | 0.09613 | -0.1236 | 0.27008 | 0.25177 | -0.32501 | 122.4426 | -0.036621 | 122.7676 | 122.9095 | -0.09613 | 122.5342 | 0.086975 | 0.32501 | 122.7356 | 123.1293 | 122.9279 | 122.9874 | 122.7676 | 123.111 | 122.9553 | 122.5342 | 122.9874 | 122.7676 | 122.9553 | 122.9279 | 123.111 | -0.58136 | -0.48981
4346.1719 | 123.2071 | -122.8271 | 0.17395 | -0.22804 | 0.0096387 | -0.012078 | 0.045369 | -0.019393 | -0.015107 | 0.0064257 | -0.15106 | 0.1831 | -0.46692 | -0.004578 | 0.009155 | -0.004578 | 0.054932 | 0.20599 | 0.3067 | -0.35248 | 122.3602 | 0.009155 | 122.6761 | 122.8226 | -0.16479 | 122.4747 | 0.13275 | 0.31586 | 122.8821 | 123.0331 | 122.8363 | 123.0103 | 122.6761 | 123.1338 | 122.8226 | 122.4747 | 123.0103 | 122.6761 | 122.8226 | 122.8363 | 123.1338 | -0.64087 | -0.52643
4347.8594 | 123.1659 | -122.818 | 0.17395 | -0.13649 | 0.0077161 | -0.016992 | 0.041524 | -0.019606 | -0.013612 | 0.0081347 | -0.041199 | 0.13275 | -0.38452 | 0.091553 | 0.11444 | 0.14191 | -0.15564 | 0.32959 | 0.24719 | -0.29755 | 122.4335 | -0.041199 | 122.7768 | 122.9095 | -0.059509 | 122.5204 | 0.073242 | 0.34332 | 122.6624 | 123.1476 | 122.9324 | 122.9507 | 122.7768 | 123.0652 | 122.9599 | 122.5204 | 122.9507 | 122.7768 | 122.9599 | 122.9324 | 123.0652 | -0.55847 | -0.4715
4349.5469 | 123.23 | -122.8363 | 0.19684 | 0.00083945 | 0.0098523 | -0.015069 | 0.043019 | -0.020674 | -0.01169 | 0.0074939 | -0.086975 | 0.14648 | -0.42572 | 0.032043 | 0.07782 | 0.09613 | -0.11444 | 0.27008 | 0.2655 | -0.33417 | 122.4106 | -0.050354 | 122.7493 | 122.8683 | -0.11902 | 122.5021 | 0.068665 | 0.33874 | 122.7219 | 123.1064 | 122.9141 | 122.9828 | 122.7493 | 123.1018 | 122.9324 | 122.5021 | 122.9828 | 122.7493 | 122.9324 | 122.9141 | 123.1018 | -0.62256 | -0.531
4351.25 | 123.2025 | -122.8592 | 0.19226 | -0.22041 | 0.01028 | -0.010156 | 0.045156 | -0.020247 | -0.013399 | 0.0051441 | -0.036621 | 0.13733 | -0.41657 | 0.082397 | 0.07782 | 0.10529 | -0.054932 | 0.29755 | 0.2655 | -0.32501 | 122.4426 | -0.054932 | 122.8226 | 122.9416 | -0.11444 | 122.5342 | 0.073242 | 0.37994 | 122.8043 | 123.1567 | 122.937 | 122.9965 | 122.8226 | 123.1247 | 122.9645 | 122.5342 | 122.9965 | 122.8226 | 122.9645 | 122.937 | 123.1247 | -0.60883 | -0.51727
4352.9375 | 123.0972 | -122.8775 | 0.2243 | -0.083084 | 0.0094251 | -0.0071648 | 0.047933 | -0.018752 | -0.014894 | 0.0051441 | -0.073242 | 0.16937 | -0.45319 | 0.041199 | 0.036621 | 0.041199 | -0.036621 | 0.23346 | 0.27008 | -0.3479 | 122.4243 | -0.054931 | 122.8043 | 122.9187 | -0.18768 | 122.5296 | 0.045777 | 0.37994 | 122.8409 | 123.111 | 122.9141 | 123.0469 | 122.8043 | 123.1476 | 122.9187 | 122.5296 | 123.0469 | 122.8043 | 122.9187 | 122.9141 | 123.1476 | -0.67749 | -0.5722
4354.6406 | 123.2025 | -122.8317 | 0.19226 | -0.01442 | 0.0064343 | -0.010796 | 0.039601 | -0.019179 | -0.011476 | 0.0077075 | -0.10529 | 0.15564 | -0.41199 | 0.041199 | 0.091553 | 0.10071 | -0.1236 | 0.28381 | 0.28381 | -0.32501 | 122.4197 | -0.036621 | 122.7264 | 122.8729 | -0.10071 | 122.5067 | 0.091552 | 0.3067 | 122.7081 | 123.1155 | 122.9233 | 122.9874 | 122.7264 | 123.1155 | 122.9324 | 122.5067 | 122.9874 | 122.7264 | 122.9324 | 122.9233 | 123.1155 | -0.60425 | -0.51727
4356.3281 | 123.143 | -122.8638 | 0.21057 | 0.13054 | 0.0089979 | -0.011651 | 0.041951 | -0.020461 | -0.01169 | 0.0077075 | -0.050354 | 0.15106 | -0.41657 | 0.064087 | 0.073242 | 0.11444 | -0.16022 | 0.2655 | 0.26093 | -0.32044 | 122.4472 | -0.059509 | 122.8134 | 122.9279 | -0.13733 | 122.5433 | 0.050354 | 0.36621 | 122.7036 | 123.1293 | 122.937 | 123.0148 | 122.8134 | 123.1247 | 122.9782 | 122.5433 | 123.0148 | 122.8134 | 122.9782 | 122.937 | 123.1247 | -0.62714 | -0.53101
4358.0625 | 123.2025 | -122.8409 | 0.16022 | 0.023727 | 0.010493 | -0.012078 | 0.041097 | -0.018325 | -0.012758 | 0.0074939 | -0.073242 | 0.13733 | -0.39368 | 0.036621 | 0.059509 | 0.09613 | -0.1236 | 0.27466 | 0.2655 | -0.32501 | 122.4472 | -0.022888 | 122.7676 | 122.8775 | -0.10071 | 122.5159 | 0.10529 | 0.32044 | 122.7173 | 123.1155 | 122.9004 | 122.9782 | 122.7676 | 123.1064 | 122.937 | 122.5159 | 122.9782 | 122.7676 | 122.937 | 122.9004 | 123.1064 | -0.55389 | -0.48523
4359.75 | 123.1842 | -122.8363 | 0.19684 | 0.069504 | 0.010066 | -0.0093012 | 0.040883 | -0.020247 | -0.01233 | 0.0077075 | -0.07782 | 0.16937 | -0.41199 | 0.054932 | 0.07782 | 0.082397 | -0.13275 | 0.26093 | 0.26093 | -0.32959 | 122.4243 | -0.027465 | 122.7585 | 122.8912 | -0.11902 | 122.5067 | 0.064087 | 0.33417 | 122.7036 | 123.0972 | 122.9141 | 123.0057 | 122.7585 | 123.0972 | 122.9187 | 122.5067 | 123.0057 | 122.7585 | 122.9187 | 122.9141 | 123.0972 | -0.60882 | -0.52643
4361.4375 | 123.1842 | -122.8729 | 0.18768 | -0.1136 | 0.01028 | -0.011865 | 0.040029 | -0.021102 | -0.01233 | 0.0077075 | -0.041199 | 0.12817 | -0.3891 | 0.13275 | 0.13275 | 0.14191 | -0.15106 | 0.33875 | 0.26093 | -0.31128 | 122.4838 | -0.059509 | 122.8317 | 123.0057 | -0.054932 | 122.5616 | 0.073242 | 0.3479 | 122.7219 | 123.2117 | 123.0057 | 123.0011 | 122.8317 | 123.1338 | 123.0148 | 122.5616 | 123.0011 | 122.8317 | 123.0148 | 123.0057 | 123.1338 | -0.57678 | -0.49896
4363.125 | 123.1842 | -122.8409 | 0.1831 | -0.19753 | 0.0096387 | -0.011651 | 0.047292 | -0.018111 | -0.015748 | 0.0066393 | -0.11444 | 0.1831 | -0.43945 | 0.022888 | 0.022888 | 0.032043 | -0.004578 | 0.22888 | 0.3067 | -0.3479 | 122.4014 | 0 | 122.7264 | 122.8638 | -0.16022 | 122.493 | 0.1236 | 0.32501 | 122.8363 | 123.0698 | 122.8638 | 123.024 | 122.7264 | 123.1476 | 122.8729 | 122.493 | 123.024 | 122.7264 | 122.8729 | 122.8638 | 123.1476 | -0.62256 | -0.531
4364.8594 | 123.0698 | -122.8729 | 0.2243 | 0.21446 | 0.0087841 | -0.011865 | 0.044088 | -0.018965 | -0.01468 | 0.0096301 | -0.018311 | 0.1236 | -0.40283 | 0.09613 | 0.09613 | 0.13275 | -0.20142 | 0.31128 | 0.25635 | -0.30212 | 122.4701 | -0.10071 | 122.8546 | 122.9691 | -0.12817 | 122.5708 | 0.032044 | 0.38452 | 122.6715 | 123.1842 | 122.9691 | 122.9965 | 122.8546 | 123.1293 | 123.0057 | 122.5708 | 122.9965 | 122.8546 | 123.0057 | 122.9691 | 123.1293 | -0.62714 | -0.52643
4366.5469 | 123.0606 | -122.8683 | 0.20599 | 0.18394 | 0.0081433 | -0.0093012 | 0.044942 | -0.017897 | -0.013185 | 0.0064257 | -0.032043 | 0.13275 | -0.41199 | 0.091553 | 0.10529 | 0.15106 | -0.18768 | 0.3067 | 0.24261 | -0.3067 | 122.4564 | -0.073243 | 122.8363 | 122.9599 | -0.10071 | 122.5616 | 0.036621 | 0.37994 | 122.6807 | 123.175 | 122.9736 | 123.0011 | 122.8363 | 123.111 | 123.0194 | 122.5616 | 123.0011 | 122.8363 | 123.0194 | 122.9736 | 123.111 | -0.61798 | -0.5127
4368.2344 | 123.1064 | -122.8912 | 0.21515 | -0.075455 | 0.0098523 | -0.01101 | 0.046437 | -0.01747 | -0.013399 | 0.0059985 | -0.064087 | 0.16937 | -0.45776 | 0.032043 | 0.018311 | 0.045776 | -0.032043 | 0.2243 | 0.27924 | -0.3479 | 122.4335 | -0.045776 | 122.8271 | 122.9233 | -0.19684 | 122.5433 | 0.064087 | 0.39368 | 122.8592 | 123.1155 | 122.9095 | 123.0606 | 122.8271 | 123.1705 | 122.937 | 122.5433 | 123.0606 | 122.8271 | 122.937 | 122.9095 | 123.1705 | -0.67291 | -0.56305
4369.9844 | 123.1476 | -122.8821 | 0.21057 | 0.069504 | 0.0096387 | -0.009942 | 0.039174 | -0.020888 | -0.012758 | 0.0092029 | -0.12817 | 0.16022 | -0.40741 | 0.032043 | 0.064087 | 0.10529 | -0.13275 | 0.27008 | 0.27008 | -0.32044 | 122.4747 | -0.050354 | 122.7539 | 122.9141 | -0.14648 | 122.5616 | 0.05951 | 0.27924 | 122.7493 | 123.1522 | 122.9462 | 123.0423 | 122.7539 | 123.1522 | 122.9874 | 122.5616 | 123.0423 | 122.7539 | 122.9874 | 122.9462 | 123.1522 | -0.61798 | -0.53101
4371.6719 | 123.0743 | -122.8729 | 0.21515 | 0.18394 | 0.011989 | -0.0093012 | 0.043447 | -0.01982 | -0.012971 | 0.0070667 | -0.022888 | 0.14191 | -0.39368 | 0.09613 | 0.09613 | 0.14191 | -0.19684 | 0.31128 | 0.24719 | -0.31128 | 122.4792 | -0.073242 | 122.85 | 122.9691 | -0.11902 | 122.5616 | 0.032043 | 0.37079 | 122.6761 | 123.1842 | 122.9691 | 123.0148 | 122.85 | 123.1201 | 123.0148 | 122.5616 | 123.0148 | 122.85 | 123.0148 | 122.9691 | 123.1201 | -0.60883 | -0.52643
4373.4062 | 123.1018 | -122.8638 | 0.23346 | -0.022049 | 0.0075025 | -0.014428 | 0.047292 | -0.019179 | -0.014894 | 0.0070667 | -0.086975 | 0.18768 | -0.44861 | 0.032043 | 0.022888 | 0.036621 | -0.009155 | 0.18768 | 0.29755 | -0.32959 | 122.4152 | -0.045776 | 122.7768 | 122.8958 | -0.21057 | 122.5342 | 0.064087 | 0.36163 | 122.8546 | 123.0515 | 122.8867 | 123.0515 | 122.7768 | 123.1613 | 122.9004 | 122.5342 | 123.0515 | 122.7768 | 122.9004 | 122.8867 | 123.1613 | -0.68207 | -0.56305
4375.0938 | 123.2162 | -122.8363 | 0.18768 | -0.25093 | 0.01028 | -0.012719 | 0.042806 | -0.018752 | -0.013399 | 0.0068531 | -0.13275 | 0.18768 | -0.44861 | -0.013733 | 0.018311 | 0 | 0.041199 | 0.20142 | 0.31128 | -0.3479 | 122.3877 | 0 | 122.7036 | 122.8226 | -0.16937 | 122.4884 | 0.1236 | 0.31586 | 122.8775 | 123.0377 | 122.8546 | 123.024 | 122.7036 | 123.1476 | 122.8363 | 122.4884 | 123.024 | 122.7036 | 122.8363 | 122.8546 | 123.1476 | -0.63629 | -0.53558
4376.7812 | 123.1979 | -122.85 | 0.1831 | -0.022049 | 0.0094251 | -0.009942 | 0.036397 | -0.021315 | -0.012544 | 0.0053577 | -0.07782 | 0.13733 | -0.41199 | 0.064087 | 0.10529 | 0.11902 | -0.1236 | 0.32044 | 0.2655 | -0.33417 | 122.4381 | -0.045776 | 122.7722 | 122.9141 | -0.077819 | 122.5159 | 0.082398 | 0.33417 | 122.7264 | 123.1705 | 122.9553 | 122.9874 | 122.7722 | 123.1155 | 122.9691 | 122.5159 | 122.9874 | 122.7722 | 122.9691 | 122.9553 | 123.1155 | -0.59509 | -0.51727
4378.4844 | 123.0881 | -122.8683 | 0.21057 | 0.1992 | 0.011561 | -0.010369 | 0.045797 | -0.017684 | -0.012758 | 0.0074939 | -0.086975 | 0.16479 | -0.43945 | 0.050354 | 0.054932 | 0.10529 | -0.14191 | 0.25177 | 0.2655 | -0.31586 | 122.4289 | -0.045776 | 122.7814 | 122.9187 | -0.15564 | 122.5525 | 0.054932 | 0.35248 | 122.7264 | 123.1201 | 122.9233 | 123.0331 | 122.7814 | 123.1338 | 122.9736 | 122.5525 | 123.0331 | 122.7814 | 122.9736 | 122.9233 | 123.1338 | -0.65002 | -0.52643
4380.1719 | 123.1201 | -122.8638 | 0.21515 | 0.054245 | 0.010066 | -0.01101 | 0.047292 | -0.020034 | -0.014467 | 0.0081347 | -0.10071 | 0.16022 | -0.43488 | -0.032043 | -0.004578 | 0.004578 | 0 | 0.16479 | 0.28381 | -0.35706 | 122.4289 | -0.054932 | 122.7631 | 122.8317 | -0.21973 | 122.5067 | 0.068664 | 0.33417 | 122.8638 | 123.0286 | 122.8592 | 123.024 | 122.7631 | 123.1476 | 122.8683 | 122.5067 | 123.024 | 122.7631 | 122.8683 | 122.8592 | 123.1476 | -0.65002 | -0.5722
4381.9062 | 123.1064 | -122.8638 | 0.20599 | 0.11528 | 0.010066 | -0.0093012 | 0.040456 | -0.017256 | -0.010835 | 0.0083483 | -0.036621 | 0.14191 | -0.40283 | 0.068665 | 0.082397 | 0.12817 | -0.19226 | 0.29297 | 0.26093 | -0.32044 | 122.4609 | -0.064087 | 122.8271 | 122.9324 | -0.1236 | 122.5433 | 0.054931 | 0.36621 | 122.6715 | 123.1567 | 122.9462 | 123.0057 | 122.8271 | 123.1247 | 122.9919 | 122.5433 | 123.0057 | 122.8271 | 122.9919 | 122.9462 | 123.1247 | -0.60883 | -0.52643
4383.5938 | 123.0972 | -122.8775 | 0.21973 | -0.067826 | 0.010921 | -0.012719 | 0.046651 | -0.020674 | -0.01468 | 0.0053577 | -0.07782 | 0.17395 | -0.44403 | 0.032043 | 0.027466 | 0.059509 | -0.041199 | 0.21973 | 0.29297 | -0.32959 | 122.4335 | -0.045777 | 122.7997 | 122.9095 | -0.19226 | 122.5479 | 0.073242 | 0.36621 | 122.8363 | 123.0972 | 122.905 | 123.0515 | 122.7997 | 123.1705 | 122.937 | 122.5479 | 123.0515 | 122.7997 | 122.937 | 122.905 | 123.1705 | -0.66376 | -0.54932
4385.2969 | 123.1888 | -122.8271 | 0.19226 | -0.060196 | 0.010921 | -0.012719 | 0.037252 | -0.021529 | -0.010621 | 0.0074939 | -0.082397 | 0.15564 | -0.40741 | 0.068665 | 0.086975 | 0.12817 | -0.13275 | 0.31586 | 0.27466 | -0.3479 | 122.4197 | -0.036621 | 122.7448 | 122.8958 | -0.10529 | 122.4792 | 0.082397 | 0.32501 | 122.6944 | 123.143 | 122.9141 | 122.9828 | 122.7448 | 123.1018 | 122.9553 | 122.4792 | 122.9828 | 122.7448 | 122.9553 | 122.9141 | 123.1018 | -0.59967 | -0.54016
4387.0312 | 123.0972 | -122.8638 | 0.21973 | 0.16869 | 0.012202 | -0.012078 | 0.045156 | -0.020247 | -0.012971 | 0.0066393 | -0.10986 | 0.15106 | -0.43488 | 0.041199 | 0.064087 | 0.09613 | -0.14191 | 0.25177 | 0.25177 | -0.31128 | 122.4289 | -0.068665 | 122.7539 | 122.905 | -0.15564 | 122.5525 | 0.032043 | 0.32501 | 122.7219 | 123.1155 | 122.9279 | 123.0148 | 122.7539 | 123.1155 | 122.9599 | 122.5525 | 123.0148 | 122.7539 | 122.9599 | 122.9279 | 123.1155 | -0.6546 | -0.53101
4388.7188 | 123.1338 | -122.8912 | 0.19684 | 0.13817 | 0.010493 | -0.010583 | 0.046224 | -0.019606 | -0.013185 | 0.0081347 | -0.13733 | 0.19684 | -0.44403 | -0.036621 | -0.018311 | -0.009155 | -0.004578 | 0.16022 | 0.30212 | -0.33875 | 122.4472 | 0 | 122.7539 | 122.8546 | -0.21515 | 122.5525 | 0.10529 | 0.3067 | 122.8867 | 123.0515 | 122.8729 | 123.0881 | 122.7539 | 123.1934 | 122.8821 | 122.5525 | 123.0881 | 122.7539 | 122.8821 | 122.8729 | 123.1934 | -0.64087 | -0.53558
4390.4219 | 123.2071 | -122.8317 | 0.17853 | 0.023727 | 0.010493 | -0.0090874 | 0.037038 | -0.01982 | -0.013612 | 0.0059985 | -0.10071 | 0.16937 | -0.41657 | 0.018311 | 0.07782 | 0.068665 | -0.11902 | 0.26093 | 0.2655 | -0.33417 | 122.4152 | -0.009155 | 122.731 | 122.85 | -0.10071 | 122.4976 | 0.086975 | 0.31586 | 122.7127 | 123.0927 | 122.9095 | 123.0011 | 122.731 | 123.0972 | 122.9004 | 122.4976 | 123.0011 | 122.731 | 122.9004 | 122.9095 | 123.0972 | -0.59509 | -0.5127
4392.1406 | 123.0881 | -122.8638 | 0.21973 | 0.20683 | 0.0094251 | -0.011437 | 0.04366 | -0.020674 | -0.013185 | 0.0079211 | -0.091553 | 0.17395 | -0.41657 | 0.059509 | 0.059509 | 0.10529 | -0.15564 | 0.2655 | 0.24261 | -0.32044 | 122.4472 | -0.045777 | 122.7722 | 122.9233 | -0.16022 | 122.5433 | 0.022888 | 0.32501 | 122.7081 | 123.1293 | 122.9233 | 123.0377 | 122.7722 | 123.1064 | 122.9691 | 122.5433 | 123.0377 | 122.7722 | 122.9691 | 122.9233 | 123.1064 | -0.63629 | -0.54016
4393.8281 | 123.0835 | -122.8683 | 0.20142 | 0.1992 | 0.010066 | -0.010796 | 0.043019 | -0.018325 | -0.012544 | 0.0068531 | -0.041199 | 0.14191 | -0.37994 | 0.082397 | 0.09613 | 0.13733 | -0.20599 | 0.3067 | 0.2243 | -0.29297 | 122.4884 | -0.059509 | 122.8271 | 122.9507 | -0.10529 | 122.5754 | 0.022888 | 0.33875 | 122.6624 | 123.175 | 122.9645 | 123.0103 | 122.8271 | 123.0927 | 123.0057 | 122.5754 | 123.0103 | 122.8271 | 123.0057 | 122.9645 | 123.0927 | -0.58136 | -0.49438
4395.5469 | 123.1018 | -122.8821 | 0.21057 | -0.090714 | 0.0077161 | -0.0078058 | 0.047719 | -0.018538 | -0.015535 | 0.0068531 | -0.059509 | 0.1831 | -0.42114 | 0.032043 | 0.027466 | 0.059509 | -0.054932 | 0.22888 | 0.29755 | -0.35248 | 122.4609 | -0.027466 | 122.8226 | 122.9141 | -0.18311 | 122.5296 | 0.086975 | 0.36163 | 122.8271 | 123.111 | 122.9095 | 123.0652 | 122.8226 | 123.1796 | 122.9416 | 122.5296 | 123.0652 | 122.8226 | 122.9416 | 122.9095 | 123.1796 | -0.63171 | -0.56305
4397.2344 | 123.1018 | -122.8821 | 0.21515 | -0.067826 | 0.010707 | -0.012505 | 0.047506 | -0.018965 | -0.015321 | 0.0045031 | -0.050354 | 0.20142 | -0.41657 | 0.032043 | 0.027466 | 0.041199 | -0.027466 | 0.2243 | 0.29297 | -0.33417 | 122.4655 | -0.013733 | 122.8317 | 122.9141 | -0.18768 | 122.5479 | 0.07782 | 0.36621 | 122.8546 | 123.1064 | 122.9095 | 123.0835 | 122.8317 | 123.175 | 122.9233 | 122.5479 | 123.0835 | 122.8317 | 122.9233 | 122.9095 | 123.175 | -0.63171 | -0.54932
4398.9844 | 123.1476 | -122.8729 | 0.20142 | 0.038986 | 0.011348 | -0.0086602 | 0.044728 | -0.01512 | -0.012971 | 0.0094165 | -0.10071 | 0.16937 | -0.43488 | -0.018311 | -0.022888 | 0.004578 | -0.004578 | 0.16022 | 0.29755 | -0.36163 | 122.438 | -0.032043 | 122.7722 | 122.8546 | -0.2243 | 122.5113 | 0.09613 | 0.33417 | 122.8683 | 123.0331 | 122.85 | 123.0423 | 122.7722 | 123.1705 | 122.8775 | 122.5113 | 123.0423 | 122.7722 | 122.8775 | 122.85 | 123.1705 | -0.63629 | -0.56305
4400.6719 | 123.1293 | -122.8592 | 0.21057 | 0.069504 | 0.0094251 | -0.008233 | 0.045369 | -0.01747 | -0.015748 | 0.0083483 | -0.15106 | 0.1831 | -0.46692 | -0.041199 | -0.013733 | 0 | -0.009155 | 0.16022 | 0.3067 | -0.36163 | 122.3923 | -0.027466 | 122.7081 | 122.818 | -0.2243 | 122.4976 | 0.096131 | 0.31586 | 122.85 | 123.0194 | 122.8455 | 123.0423 | 122.7081 | 123.1659 | 122.8592 | 122.4976 | 123.0423 | 122.7081 | 122.8592 | 122.8455 | 123.1659 | -0.67749 | -0.5722
4402.3594 | 123.0835 | -122.8912 | 0.2243 | -0.067826 | 0.010066 | -0.011865 | 0.044728 | -0.018325 | -0.013185 | 0.0072803 | -0.068665 | 0.16937 | -0.41199 | 0 | 0.018311 | 0.054932 | -0.027466 | 0.21515 | 0.27924 | -0.36621 | 122.4792 | -0.054931 | 122.8226 | 122.8912 | -0.20599 | 122.525 | 0.054932 | 0.34332 | 122.8638 | 123.1064 | 122.9095 | 123.0606 | 122.8226 | 123.1705 | 122.9462 | 122.525 | 123.0606 | 122.8226 | 122.9462 | 122.9095 | 123.1705 | -0.63629 | -0.59052
4404.0625 | 123.0972 | -122.8821 | 0.20599 | -0.060196 | 0.0081433 | -0.0093012 | 0.045156 | -0.018538 | -0.014467 | 0.0079211 | -0.091553 | 0.20142 | -0.42572 | 0.004578 | 0.032043 | 0.045776 | -0.027466 | 0.20142 | 0.27924 | -0.33875 | 122.4564 | -0.004578 | 122.7905 | 122.8867 | -0.17395 | 122.5433 | 0.073242 | 0.33417 | 122.8546 | 123.0835 | 122.9141 | 123.0835 | 122.7905 | 123.1613 | 122.9279 | 122.5433 | 123.0835 | 122.7905 | 122.9279 | 122.9141 | 123.1613 | -0.63171 | -0.54474
4405.7656 | 123.1338 | -122.8867 | 0.21057 | 0.10002 | 0.0096387 | -0.011865 | 0.044301 | -0.017897 | -0.014467 | 0.0072803 | -0.13733 | 0.1831 | -0.43488 | -0.041199 | -0.018311 | -0.004578 | -0.004578 | 0.15106 | 0.29297 | -0.35248 | 122.4518 | -0.027466 | 122.7493 | 122.8455 | -0.22888 | 122.5342 | 0.082398 | 0.29755 | 122.8821 | 123.0377 | 122.8683 | 123.0698 | 122.7493 | 123.1796 | 122.8821 | 122.5342 | 123.0698 | 122.7493 | 122.8821 | 122.8683 | 123.1796 | -0.64545 | -0.56305
4407.4531 | 123.1338 | -122.85 | 0.20142 | 0.12291 | 0.0081433 | -0.012292 | 0.046437 | -0.017684 | -0.015107 | 0.0085619 | -0.15564 | 0.17853 | -0.43945 | -0.050354 | -0.009155 | -0.004578 | -0.013733 | 0.15564 | 0.30212 | -0.36163 | 122.4106 | -0.022888 | 122.6944 | 122.7997 | -0.21057 | 122.4884 | 0.10071 | 0.28381 | 122.8363 | 123.0057 | 122.8409 | 123.0286 | 122.6944 | 123.1522 | 122.8455 | 122.4884 | 123.0286 | 122.6944 | 122.8455 | 122.8409 | 123.1522 | -0.64087 | -0.56305
4409.1406 | 123.23 | -122.8683 | 0.17853 | -0.22041 | 0.0085705 | -0.01336 | 0.040456 | -0.018111 | -0.01468 | 0.0077075 | -0.13733 | 0.19684 | -0.43945 | -0.045776 | 0.004578 | 0.013733 | 0.054932 | 0.20599 | 0.28839 | -0.35248 | 122.4289 | 0.01831 | 122.731 | 122.8226 | -0.17395 | 122.5159 | 0.10986 | 0.30212 | 122.9233 | 123.0743 | 122.8729 | 123.0652 | 122.731 | 123.1567 | 122.8821 | 122.5159 | 123.0652 | 122.731 | 122.8821 | 122.8729 | 123.1567 | -0.61798 | -0.53101
4410.8281 | 123.1796 | -122.85 | 0.17853 | -0.15938 | 0.0089979 | -0.010583 | 0.03832 | -0.019393 | -0.013612 | 0.0072803 | -0.027466 | 0.15106 | -0.39368 | 0.059509 | 0.10071 | 0.1236 | -0.086975 | 0.31586 | 0.2655 | -0.32501 | 122.4564 | -0.027466 | 122.8226 | 122.9095 | -0.07782 | 122.525 | 0.086975 | 0.36621 | 122.7631 | 123.1659 | 122.9507 | 123.0011 | 122.8226 | 123.1155 | 122.9736 | 122.525 | 123.0011 | 122.8226 | 122.9736 | 122.9507 | 123.1155 | -0.5722 | -0.50354
4412.5156 | 123.2483 | -122.8363 | 0.20142 | -0.25856 | 0.0094251 | -0.012719 | 0.042165 | -0.020247 | -0.014253 | 0.0049303 | -0.11902 | 0.21057 | -0.44861 | -0.027466 | 0.009155 | 0 | 0.045776 | 0.20599 | 0.31586 | -0.35248 | 122.3877 | 0.009155 | 122.7173 | 122.8088 | -0.19226 | 122.4838 | 0.11444 | 0.32959 | 122.8821 | 123.0423 | 122.8455 | 123.0469 | 122.7173 | 123.1522 | 122.8363 | 122.4838 | 123.0469 | 122.7173 | 122.8363 | 122.8455 | 123.1522 | -0.65002 | -0.55389
4414.2031 | 123.2025 | -122.85 | 0.18768 | -0.28908 | 0.0083569 | -0.012933 | 0.039815 | -0.018965 | -0.014253 | 0.0055713 | -0.050354 | 0.15564 | -0.39825 | 0.027466 | 0.064087 | 0.054932 | -0.032043 | 0.27008 | 0.28839 | -0.32501 | 122.4518 | -0.032043 | 122.7997 | 122.8775 | -0.1236 | 122.525 | 0.10071 | 0.3479 | 122.818 | 123.1201 | 122.9141 | 123.0057 | 122.7997 | 123.1384 | 122.905 | 122.525 | 123.0057 | 122.7997 | 122.905 | 122.9141 | 123.1384 | -0.58594 | -0.5127
4415.9219 | 123.0789 | -122.8821 | 0.21973 | 0.1992 | 0.0087841 | -0.0097284 | 0.042165 | -0.018965 | -0.014039 | 0.0053577 | -0.018311 | 0.14191 | -0.39825 | 0.086975 | 0.10529 | 0.14191 | -0.18768 | 0.30212 | 0.27924 | -0.32044 | 122.4838 | -0.07782 | 122.8638 | 122.9691 | -0.11444 | 122.5616 | 0.059509 | 0.37994 | 122.6944 | 123.1842 | 122.9874 | 123.024 | 122.8638 | 123.1613 | 123.024 | 122.5616 | 123.024 | 122.8638 | 123.024 | 122.9874 | 123.1613 | -0.61798 | -0.54016
4417.6094 | 123.1247 | -122.8775 | 0.21973 | 0.016098 | 0.011775 | -0.0097284 | 0.047719 | -0.018965 | -0.016389 | 0.0072803 | -0.09613 | 0.16022 | -0.4303 | -0.032043 | -0.032043 | 0.009155 | -0.009155 | 0.15564 | 0.29755 | -0.34332 | 122.4472 | -0.05951 | 122.7814 | 122.8455 | -0.25177 | 122.5342 | 0.077819 | 0.33417 | 122.8683 | 123.0331 | 122.8455 | 123.0377 | 122.7814 | 123.175 | 122.8867 | 122.5342 | 123.0377 | 122.7814 | 122.8867 | 122.8455 | 123.175 | -0.65003 | -0.56305
4419.3125 | 123.1979 | -122.8363 | 0.18768 | -0.19753 | 0.0094251 | -0.0073786 | 0.042379 | -0.018111 | -0.015107 | 0.0059985 | -0.13275 | 0.19226 | -0.44861 | -0.013733 | 0.027466 | 0.004578 | 0.036621 | 0.21973 | 0.3067 | -0.3479 | 122.3877 | 0.004578 | 122.7036 | 122.8226 | -0.16022 | 122.4884 | 0.11902 | 0.31586 | 122.8729 | 123.056 | 122.8638 | 123.0286 | 122.7036 | 123.143 | 122.8409 | 122.4884 | 123.0286 | 122.7036 | 122.8409 | 122.8638 | 123.143 | -0.63629 | -0.53558
4421.0312 | 123.1018 | -122.8638 | 0.21973 | -0.075455 | 0.0096387 | -0.013574 | 0.045156 | -0.020034 | -0.015321 | 0.0077075 | -0.050354 | 0.17395 | -0.41657 | 0.027466 | 0.027466 | 0.041199 | -0.032043 | 0.21057 | 0.27466 | -0.3479 | 122.4472 | -0.045777 | 122.8134 | 122.8912 | -0.19226 | 122.5159 | 0.054931 | 0.36621 | 122.8317 | 123.0743 | 122.8912 | 123.0377 | 122.8134 | 123.1384 | 122.905 | 122.5159 | 123.0377 | 122.8134 | 122.905 | 122.8912 | 123.1384 | -0.63629 | -0.56763
4422.7188 | 123.1567 | -122.8546 | 0.21515 | 0.16106 | 0.01028 | -0.0086602 | 0.044088 | -0.018538 | -0.015107 | 0.0074939 | -0.13275 | 0.19226 | -0.43488 | -0.045776 | -0.018311 | -0.004578 | -0.009155 | 0.15564 | 0.32501 | -0.36163 | 122.4197 | -0.022888 | 122.7219 | 122.8088 | -0.23346 | 122.493 | 0.10986 | 0.30212 | 122.8455 | 123.0103 | 122.8363 | 123.0469 | 122.7219 | 123.1796 | 122.85 | 122.493 | 123.0469 | 122.7219 | 122.85 | 122.8363 | 123.1796 | -0.65002 | -0.57678
4424.4688 | 123.175 | -122.8592 | 0.19226 | -0.13649 | 0.0092115 | -0.012505 | 0.03362 | -0.020674 | -0.01169 | 0.0074939 | -0.073242 | 0.17395 | -0.37079 | 0.07782 | 0.12817 | 0.15106 | -0.13733 | 0.32959 | 0.26093 | -0.31586 | 122.4884 | -0.018311 | 122.7859 | 122.937 | -0.064087 | 122.5433 | 0.068664 | 0.29755 | 122.7219 | 123.1888 | 122.9874 | 123.0331 | 122.7859 | 123.1201 | 123.0103 | 122.5433 | 123.0331 | 122.7859 | 123.0103 | 122.9874 | 123.1201 | -0.56305 | -0.50812
4426.1875 | 123.2162 | -122.8409 | 0.17853 | 0.00083945 | 0.0085705 | -0.010583 | 0.037465 | -0.01982 | -0.012544 | 0.0072803 | -0.068665 | 0.16479 | -0.39825 | 0.013733 | 0.059509 | 0.07782 | -0.09613 | 0.26093 | 0.27008 | -0.32959 | 122.4426 | -0.013733 | 122.7722 | 122.8546 | -0.11902 | 122.5113 | 0.091553 | 0.32959 | 122.7448 | 123.1018 | 122.9004 | 123.0057 | 122.7722 | 123.111 | 122.9187 | 122.5113 | 123.0057 | 122.7722 | 122.9187 | 122.9004 | 123.111 | -0.57678 | -0.50812
4427.875 | 123.0972 | -122.8729 | 0.21973 | 0.19157 | 0.0070751 | -0.01336 | 0.043874 | -0.018538 | -0.013826 | 0.0068531 | -0.018311 | 0.14648 | -0.3891 | 0.091553 | 0.10071 | 0.13733 | -0.20599 | 0.29755 | 0.24719 | -0.3067 | 122.4838 | -0.073243 | 122.8546 | 122.9645 | -0.11902 | 122.5662 | 0.027465 | 0.37079 | 122.6669 | 123.1705 | 122.9736 | 123.0194 | 122.8546 | 123.1201 | 123.0103 | 122.5662 | 123.0194 | 122.8546 | 123.0103 | 122.9736 | 123.1201 | -0.60883 | -0.52643
4429.5781 | 123.23 | -122.8455 | 0.19226 | -0.28145 | 0.0096387 | -0.010796 | 0.042592 | -0.022383 | -0.01233 | 0.0057849 | -0.068665 | 0.16479 | -0.40283 | 0.022888 | 0.045776 | 0.050354 | -0.004578 | 0.25635 | 0.27924 | -0.35248 | 122.4426 | -0.027466 | 122.7768 | 122.8683 | -0.14648 | 122.493 | 0.086975 | 0.33417 | 122.8409 | 123.1018 | 122.8912 | 123.0103 | 122.7768 | 123.1247 | 122.8958 | 122.493 | 123.0103 | 122.7768 | 122.8958 | 122.8912 | 123.1247 | -0.59509 | -0.54474
4431.2656 | 123.1155 | -122.8683 | 0.21973 | -0.090714 | 0.0096387 | -0.015923 | 0.045583 | -0.020461 | -0.01468 | 0.0072803 | -0.082397 | 0.19226 | -0.44861 | 0.045776 | 0.036621 | 0.045776 | -0.022888 | 0.24261 | 0.29755 | -0.35248 | 122.4197 | -0.027466 | 122.7859 | 122.9141 | -0.18311 | 122.5159 | 0.077819 | 0.36621 | 122.8455 | 123.111 | 122.905 | 123.0606 | 122.7859 | 123.1659 | 122.9141 | 122.5159 | 123.0606 | 122.7859 | 122.9141 | 122.905 | 123.1659 | -0.66834 | -0.57221
4432.9688 | 123.0927 | -122.8683 | 0.2243 | -0.067826 | 0.0096387 | -0.0093012 | 0.047292 | -0.019393 | -0.013399 | 0.0064257 | -0.059509 | 0.17395 | -0.4303 | 0.018311 | 0.022888 | 0.036621 | -0.032043 | 0.2243 | 0.29297 | -0.33875 | 122.438 | -0.050354 | 122.8088 | 122.8867 | -0.20142 | 122.5296 | 0.068665 | 0.37079 | 122.8363 | 123.0927 | 122.8912 | 123.0423 | 122.8088 | 123.1613 | 122.905 | 122.5296 | 123.0423 | 122.8088 | 122.905 | 122.8912 | 123.1613 | -0.6546 | -0.56305
4434.6562 | 123.1796 | -122.8455 | 0.21057 | -0.1899 | 0.0077161 | -0.012292 | 0.038533 | -0.020674 | -0.011476 | 0.0074939 | -0.050354 | 0.16022 | -0.39368 | 0.086975 | 0.09613 | 0.10529 | -0.082397 | 0.32044 | 0.2655 | -0.32501 | 122.4518 | -0.050354 | 122.7951 | 122.9324 | -0.11444 | 122.5204 | 0.054932 | 0.34332 | 122.7631 | 123.1659 | 122.9416 | 123.0057 | 122.7951 | 123.111 | 122.9507 | 122.5204 | 123.0057 | 122.7951 | 122.9507 | 122.9416 | 123.111 | -0.60425 | -0.53558
4436.375 | 123.1567 | -122.85 | 0.19684 | 0.13054 | 0.010493 | -0.01336 | 0.040029 | -0.021743 | -0.013826 | 0.0079211 | -0.07782 | 0.16022 | -0.40283 | 0.045776 | 0.073242 | 0.086975 | -0.13733 | 0.2655 | 0.26093 | -0.32044 | 122.4472 | -0.036621 | 122.7722 | 122.8958 | -0.1236 | 122.5296 | 0.064087 | 0.32501 | 122.7127 | 123.1155 | 122.9233 | 123.0103 | 122.7722 | 123.111 | 122.937 | 122.5296 | 123.0103 | 122.7722 | 122.937 | 122.9233 | 123.111 | -0.59967 | -0.51727
4438.0625 | 123.1476 | -122.85 | 0.21973 | 0.11528 | 0.0092115 | -0.013146 | 0.041097 | -0.020461 | -0.011903 | 0.0032215 | -0.059509 | 0.15564 | -0.38452 | 0.032043 | 0.068665 | 0.091553 | -0.15106 | 0.26093 | 0.2655 | -0.31586 | 122.4655 | -0.064087 | 122.7905 | 122.8821 | -0.15106 | 122.5342 | 0.045776 | 0.32501 | 122.699 | 123.111 | 122.9187 | 123.0057 | 122.7905 | 123.1155 | 122.9416 | 122.5342 | 123.0057 | 122.7905 | 122.9416 | 122.9187 | 123.1155 | -0.60425 | -0.53558
4439.7656 | 123.0789 | -122.8729 | 0.21057 | 0.11528 | 0.0089979 | -0.0050286 | 0.047292 | -0.018111 | -0.01233 | 0.0064257 | -0.004578 | 0.15564 | -0.40283 | 0.10071 | 0.07782 | 0.12817 | -0.21515 | 0.28839 | 0.24261 | -0.33875 | 122.4701 | -0.054931 | 122.8683 | 122.9736 | -0.13275 | 122.5342 | 0.032044 | 0.39825 | 122.6578 | 123.1613 | 122.9507 | 123.0286 | 122.8683 | 123.1155 | 123.0011 | 122.5342 | 123.0286 | 122.8683 | 123.0011 | 122.9507 | 123.1155 | -0.6134 | -0.54932
4441.4844 | 123.23 | -122.85 | 0.1831 | 0.023727 | 0.0096387 | -0.013574 | 0.037892 | -0.021102 | -0.010408 | 0.0064257 | -0.091553 | 0.18768 | -0.41199 | 0.041199 | 0.050354 | 0.082397 | -0.10986 | 0.25177 | 0.27008 | -0.34332 | 122.4381 | 0.004578 | 122.7585 | 122.8912 | -0.13275 | 122.5067 | 0.086976 | 0.32043 | 122.7402 | 123.1018 | 122.9004 | 123.0377 | 122.7585 | 123.1201 | 122.9324 | 122.5067 | 123.0377 | 122.7585 | 122.9324 | 122.9004 | 123.1201 | -0.59509 | -0.52643
4443.2188 | 123.2162 | -122.85 | 0.17395 | -0.22804 | 0.011348 | -0.011224 | 0.045156 | -0.021743 | -0.011262 | 0.0089893 | -0.10986 | 0.21057 | -0.42572 | 0 | 0.013733 | 0.004578 | 0.032043 | 0.23804 | 0.30212 | -0.37994 | 122.4243 | 0.036621 | 122.7402 | 122.85 | -0.16022 | 122.4701 | 0.12817 | 0.31586 | 122.8821 | 123.0881 | 122.8638 | 123.0606 | 122.7402 | 123.1522 | 122.8546 | 122.4701 | 123.0606 | 122.7402 | 122.8546 | 122.8638 | 123.1522 | -0.59967 | -0.55389
4444.9062 | 123.1842 | -122.85 | 0.19226 | -0.1899 | 0.0083569 | -0.0095148 | 0.039815 | -0.020461 | -0.013399 | 0.0053577 | -0.018311 | 0.16022 | -0.41199 | 0.09613 | 0.10071 | 0.11902 | -0.09613 | 0.33417 | 0.2655 | -0.32501 | 122.4381 | -0.032044 | 122.8317 | 122.9462 | -0.091553 | 122.525 | 0.073242 | 0.39368 | 122.7539 | 123.1842 | 122.9507 | 123.0103 | 122.8317 | 123.1155 | 122.9691 | 122.525 | 123.0103 | 122.8317 | 122.9691 | 122.9507 | 123.1155 | -0.60425 | -0.51727
4446.6094 | 123.1934 | -122.8409 | 0.18768 | -0.18227 | 0.0085705 | -0.009942 | 0.046865 | -0.01982 | -0.018098 | 0.0083483 | -0.12817 | 0.20142 | -0.46234 | 0 | 0.022888 | 0.004578 | 0.018311 | 0.21973 | 0.30212 | -0.37079 | 122.3785 | 0.013733 | 122.7127 | 122.8409 | -0.16479 | 122.4701 | 0.11444 | 0.33417 | 122.8592 | 123.0606 | 122.8638 | 123.0423 | 122.7127 | 123.143 | 122.8455 | 122.4701 | 123.0423 | 122.7127 | 122.8455 | 122.8638 | 123.143 | -0.65002 | -0.55847
4448.2969 | 123.1522 | -122.8638 | 0.21515 | -0.15175 | 0.0094251 | -0.009942 | 0.044942 | -0.018538 | -0.014467 | 0.0079211 | -0.082397 | 0.20142 | -0.44403 | 0.050354 | 0.027466 | 0.045776 | -0.018311 | 0.2243 | 0.30212 | -0.33417 | 122.4197 | -0.013733 | 122.7814 | 122.9141 | -0.18768 | 122.5296 | 0.086975 | 0.36163 | 122.8455 | 123.0881 | 122.8912 | 123.0652 | 122.7814 | 123.1659 | 122.9095 | 122.5296 | 123.0652 | 122.7814 | 122.9095 | 122.8912 | 123.1659 | -0.65918 | -0.54932
4449.9844 | 123.1796 | -122.8409 | 0.19226 | -0.075455 | 0.011134 | -0.019128 | 0.037892 | -0.020461 | -0.013612 | 0.0068531 | -0.07782 | 0.14648 | -0.40741 | 0.064087 | 0.11444 | 0.13275 | -0.12817 | 0.31586 | 0.26093 | -0.31586 | 122.4335 | -0.045777 | 122.7631 | 122.905 | -0.07782 | 122.525 | 0.068664 | 0.32959 | 122.7127 | 123.1567 | 122.9553 | 122.9874 | 122.7631 | 123.1018 | 122.9736 | 122.525 | 122.9874 | 122.7631 | 122.9736 | 122.9553 | 123.1018 | -0.59967 | -0.50812
4451.7031 | 123.2117 | -122.818 | 0.18768 | 0.00083945 | 0.011989 | -0.0086602 | 0.038533 | -0.018538 | -0.013185 | 0.0070667 | -0.082397 | 0.16937 | -0.40283 | 0.050354 | 0.07782 | 0.091553 | -0.1236 | 0.27008 | 0.27924 | -0.33875 | 122.4152 | -0.01831 | 122.7356 | 122.8683 | -0.10986 | 122.4792 | 0.091553 | 0.32044 | 122.6944 | 123.0881 | 122.8958 | 122.9874 | 122.7356 | 123.0972 | 122.9095 | 122.4792 | 122.9874 | 122.7356 | 122.9095 | 122.8958 | 123.0972 | -0.59052 | -0.52643
4453.4219 | 123.0927 | -122.8958 | 0.21973 | -0.067826 | 0.010066 | -0.0071648 | 0.047719 | -0.018752 | -0.015321 | 0.0053577 | -0.054932 | 0.16479 | -0.43945 | 0.045776 | 0.027466 | 0.054932 | -0.036621 | 0.22888 | 0.28839 | -0.33875 | 122.4564 | -0.054932 | 122.8409 | 122.9416 | -0.19226 | 122.5571 | 0.068664 | 0.38452 | 122.8592 | 123.1247 | 122.9233 | 123.0606 | 122.8409 | 123.1842 | 122.9507 | 122.5571 | 123.0606 | 122.8409 | 122.9507 | 122.9233 | 123.1842 | -0.65918 | -0.55847
4455.125 | 123.1064 | -122.8775 | 0.2243 | 0.1992 | 0.011134 | -0.008233 | 0.043447 | -0.018965 | -0.010835 | 0.0085619 | -0.07782 | 0.18768 | -0.43488 | 0.041199 | 0.050354 | 0.073242 | -0.14191 | 0.25177 | 0.27924 | -0.33875 | 122.4426 | -0.036621 | 122.7997 | 122.9187 | -0.17395 | 122.5388 | 0.054932 | 0.35706 | 122.7356 | 123.1293 | 122.9279 | 123.0652 | 122.7997 | 123.1567 | 122.9507 | 122.5388 | 123.0652 | 122.7997 | 122.9507 | 122.9279 | 123.1567 | -0.65918 | -0.56305
4456.8281 | 123.2117 | -122.8546 | 0.16937 | 0.023727 | 0.0075025 | -0.0086602 | 0.041097 | -0.018538 | -0.011049 | 0.0066393 | -0.07782 | 0.15564 | -0.40741 | 0.032043 | 0.064087 | 0.073242 | -0.11902 | 0.26093 | 0.2655 | -0.32044 | 122.4472 | -0.013733 | 122.7768 | 122.8867 | -0.10529 | 122.5342 | 0.09613 | 0.32959 | 122.7356 | 123.1155 | 122.9187 | 123.0103 | 122.7768 | 123.1201 | 122.9279 | 122.5342 | 123.0103 | 122.7768 | 122.9279 | 122.9187 | 123.1201 | -0.57678 | -0.48981
4458.5469 | 123.1384 | -122.8912 | 0.1831 | 0.12291 | 0.011134 | -0.009942 | 0.046651 | -0.017256 | -0.013399 | 0.0077075 | -0.1236 | 0.18768 | -0.45319 | -0.032043 | -0.004578 | -0.004578 | -0.022888 | 0.17395 | 0.28839 | -0.35706 | 122.438 | 0.004578 | 122.7676 | 122.8592 | -0.18768 | 122.5342 | 0.10529 | 0.32959 | 122.8683 | 123.0652 | 122.8867 | 123.0789 | 122.7676 | 123.1796 | 122.8867 | 122.5342 | 123.0789 | 122.7676 | 122.8867 | 122.8867 | 123.1796 | -0.63629 | -0.54016
4460.2344 | 123.1338 | -122.8592 | 0.20599 | 0.1458 | 0.010707 | -0.014001 | 0.044942 | -0.018538 | -0.014253 | 0.0094165 | -0.13275 | 0.20599 | -0.44861 | -0.027466 | -0.004578 | 0.009155 | -0.018311 | 0.15564 | 0.29297 | -0.34332 | 122.4106 | 0 | 122.7264 | 122.8317 | -0.21057 | 122.5159 | 0.086975 | 0.31586 | 122.8409 | 123.0148 | 122.8546 | 123.0652 | 122.7264 | 123.1522 | 122.8683 | 122.5159 | 123.0652 | 122.7264 | 122.8683 | 122.8546 | 123.1522 | -0.6546 | -0.54932
4461.9844 | 123.2162 | -122.8592 | 0.18768 | -0.28908 | 0.0062207 | -0.012505 | 0.038747 | -0.021315 | -0.011049 | 0.0077075 | -0.10071 | 0.17395 | -0.42572 | 0.009155 | 0.054932 | 0.050354 | 0 | 0.25177 | 0.29755 | -0.36163 | 122.4335 | -0.013733 | 122.7585 | 122.8683 | -0.13275 | 122.4976 | 0.10986 | 0.32501 | 122.8592 | 123.111 | 122.9141 | 123.0331 | 122.7585 | 123.1567 | 122.9095 | 122.4976 | 123.0331 | 122.7585 | 122.9095 | 122.9141 | 123.1567 | -0.6134 | -0.54932
4463.6719 | 123.175 | -122.8592 | 0.17853 | -0.19753 | 0.01028 | -0.0088738 | 0.041524 | -0.020888 | -0.013185 | 0.0064257 | -0.013733 | 0.16937 | -0.39825 | 0.10071 | 0.11444 | 0.1236 | -0.1236 | 0.34332 | 0.25635 | -0.31586 | 122.4609 | -0.009155 | 122.8455 | 122.9599 | -0.064087 | 122.5433 | 0.07782 | 0.38452 | 122.7356 | 123.2025 | 122.9736 | 123.0286 | 122.8455 | 123.1155 | 122.9828 | 122.5433 | 123.0286 | 122.8455 | 122.9828 | 122.9736 | 123.1155 | -0.57678 | -0.49438
4465.375 | 123.0972 | -122.8821 | 0.22888 | 0.18394 | 0.0092115 | -0.011865 | 0.043874 | -0.018111 | -0.012544 | 0.0049303 | -0.054932 | 0.16022 | -0.41199 | 0.064087 | 0.07782 | 0.10529 | -0.15564 | 0.27924 | 0.25635 | -0.3067 | 122.4701 | -0.068665 | 122.8271 | 122.9462 | -0.15106 | 122.5754 | 0.027466 | 0.35706 | 122.7264 | 123.1613 | 122.9599 | 123.0423 | 122.8271 | 123.1384 | 122.9874 | 122.5754 | 123.0423 | 122.8271 | 122.9874 | 122.9599 | 123.1384 | -0.64087 | -0.53558
4467.0781 | 123.1155 | -122.8683 | 0.20599 | 0.11528 | 0.010066 | -0.0078058 | 0.041951 | -0.019179 | -0.01169 | 0.0066393 | -0.032043 | 0.16022 | -0.38452 | 0.068665 | 0.10529 | 0.12817 | -0.1831 | 0.29755 | 0.27008 | -0.31128 | 122.4838 | -0.045777 | 122.8363 | 122.937 | -0.10071 | 122.5571 | 0.064087 | 0.35248 | 122.6852 | 123.1659 | 122.9736 | 123.0286 | 122.8363 | 123.1384 | 122.9965 | 122.5571 | 123.0286 | 122.8363 | 122.9965 | 122.9736 | 123.1384 | -0.59052 | -0.51727
4468.7656 | 123.0927 | -122.8821 | 0.23346 | -0.098343 | 0.01028 | -0.0090874 | 0.046224 | -0.020034 | -0.014039 | 0.0085619 | -0.059509 | 0.1831 | -0.43488 | 0.041199 | 0.027466 | 0.059509 | -0.036621 | 0.24261 | 0.29297 | -0.3479 | 122.4472 | -0.050354 | 122.8226 | 122.9233 | -0.20599 | 122.5342 | 0.05951 | 0.37537 | 122.8455 | 123.1247 | 122.9095 | 123.0652 | 122.8226 | 123.175 | 122.9416 | 122.5342 | 123.0652 | 122.8226 | 122.9416 | 122.9095 | 123.175 | -0.66833 | -0.58136
4470.4531 | 123.2208 | -122.8409 | 0.20142 | -0.16701 | 0.0081433 | -0.011865 | 0.045583 | -0.019393 | -0.014894 | 0.0066393 | -0.14648 | 0.18768 | -0.43945 | -0.013733 | 0.018311 | 0.009155 | 0.054932 | 0.21515 | 0.29755 | -0.3479 | 122.4014 | -0.013733 | 122.6944 | 122.8271 | -0.18311 | 122.493 | 0.09613 | 0.29297 | 122.8958 | 123.056 | 122.8592 | 123.0286 | 122.6944 | 123.1384 | 122.85 | 122.493 | 123.0286 | 122.6944 | 122.85 | 122.8592 | 123.1384 | -0.64087 | -0.54932
4472.1719 | 123.2117 | -122.8546 | 0.20142 | -0.19753 | 0.011989 | -0.010156 | 0.043874 | -0.018965 | -0.015535 | 0.0066393 | -0.12817 | 0.19226 | -0.42572 | 0 | 0.022888 | 0.022888 | 0.013733 | 0.21973 | 0.3067 | -0.3479 | 122.4289 | -0.009155 | 122.7264 | 122.8546 | -0.17853 | 122.5067 | 0.10529 | 0.29755 | 122.8683 | 123.0743 | 122.8775 | 123.0469 | 122.7264 | 123.1613 | 122.8775 | 122.5067 | 123.0469 | 122.7264 | 122.8775 | 122.8775 | 123.1613 | -0.62714 | -0.54932
4473.8594 | 123.1522 | -122.8638 | 0.18768 | 0.16869 | 0.010066 | -0.010796 | 0.039601 | -0.019393 | -0.011262 | 0.0070667 | -0.050354 | 0.15564 | -0.40741 | 0.050354 | 0.073242 | 0.10071 | -0.13733 | 0.26093 | 0.2655 | -0.32044 | 122.4564 | -0.032043 | 122.8134 | 122.9141 | -0.11444 | 122.5433 | 0.07782 | 0.35706 | 122.7264 | 123.1247 | 122.937 | 123.0194 | 122.8134 | 123.1293 | 122.9645 | 122.5433 | 123.0194 | 122.8134 | 122.9645 | 122.937 | 123.1293 | -0.59509 | -0.50812
4475.5625 | 123.0972 | -122.8729 | 0.21057 | 0.17632 | 0.0075025 | -0.0097284 | 0.042165 | -0.020888 | -0.012117 | 0.0077075 | -0.022888 | 0.15564 | -0.39368 | 0.091553 | 0.11444 | 0.13733 | -0.17853 | 0.30212 | 0.24719 | -0.3067 | 122.4792 | -0.054931 | 122.85 | 122.9645 | -0.09613 | 122.5662 | 0.036621 | 0.37079 | 122.6944 | 123.175 | 122.9874 | 123.0286 | 122.85 | 123.1201 | 123.0103 | 122.5662 | 123.0286 | 122.85 | 123.0103 | 122.9874 | 123.1201 | -0.60425 | -0.51727
4477.2656 | 123.23 | -122.8638 | 0.1831 | -0.23567 | 0.010921 | -0.014855 | 0.044088 | -0.018752 | -0.010835 | 0.0068531 | -0.12817 | 0.18768 | -0.45319 | -0.032043 | -0.018311 | 0.004578 | 0.068665 | 0.19226 | 0.3067 | -0.36163 | 122.4106 | 0.004578 | 122.7356 | 122.8317 | -0.20142 | 122.5021 | 0.1236 | 0.32501 | 122.9324 | 123.056 | 122.8455 | 123.0515 | 122.7356 | 123.1705 | 122.8683 | 122.5021 | 123.0515 | 122.7356 | 122.8683 | 122.8455 | 123.1705 | -0.63629 | -0.54474
4478.9688 | 123.1796 | -122.8546 | 0.19684 | -0.19753 | 0.0089979 | -0.010369 | 0.038747 | -0.020247 | -0.013612 | 0.0049303 | -0.032043 | 0.15564 | -0.39825 | 0.10529 | 0.1236 | 0.15106 | -0.14191 | 0.35248 | 0.2655 | -0.32044 | 122.4564 | -0.041198 | 122.8226 | 122.9599 | -0.073242 | 122.5342 | 0.068665 | 0.36621 | 122.7127 | 123.2071 | 122.9782 | 123.0103 | 122.8226 | 123.1201 | 123.0057 | 122.5342 | 123.0103 | 122.8226 | 123.0057 | 122.9782 | 123.1201 | -0.59509 | -0.51727
4480.6719 | 123.1934 | -122.8638 | 0.19226 | -0.16701 | 0.0098523 | -0.01571 | 0.041738 | -0.018111 | -0.014467 | 0.0062121 | -0.027466 | 0.15106 | -0.3891 | 0.086975 | 0.10071 | 0.1236 | -0.082397 | 0.32959 | 0.28381 | -0.32501 | 122.4747 | -0.041199 | 122.8363 | 122.9507 | -0.091553 | 122.5388 | 0.091552 | 0.36163 | 122.7814 | 123.1934 | 122.9645 | 123.0148 | 122.8363 | 123.1476 | 122.9874 | 122.5388 | 123.0148 | 122.8363 | 122.9874 | 122.9645 | 123.1476 | -0.58136 | -0.51727
4482.375 | 123.0972 | -122.8683 | 0.21973 | -0.075455 | 0.0096387 | -0.011651 | 0.046865 | -0.017043 | -0.013826 | 0.0064257 | -0.054932 | 0.18768 | -0.42572 | 0.045776 | 0.022888 | 0.050354 | -0.036621 | 0.23346 | 0.29755 | -0.3479 | 122.4426 | -0.032044 | 122.8134 | 122.9141 | -0.19684 | 122.5204 | 0.077819 | 0.37079 | 122.8317 | 123.1018 | 122.8912 | 123.056 | 122.8134 | 123.1659 | 122.9187 | 122.5204 | 123.056 | 122.8134 | 122.9187 | 122.8912 | 123.1659 | -0.64545 | -0.56763
4484.0781 | 123.2025 | -122.8271 | 0.1831 | -0.022049 | 0.0077161 | -0.014428 | 0.038961 | -0.020034 | -0.012544 | 0.0057849 | -0.068665 | 0.16937 | -0.3891 | 0.045776 | 0.073242 | 0.11902 | -0.1236 | 0.3067 | 0.29297 | -0.3479 | 122.438 | -0.013732 | 122.7585 | 122.8729 | -0.10986 | 122.4792 | 0.10986 | 0.32043 | 122.7036 | 123.1338 | 122.9004 | 122.9965 | 122.7585 | 123.1201 | 122.9462 | 122.4792 | 122.9965 | 122.7585 | 122.9462 | 122.9004 | 123.1201 | -0.5722 | -0.531
4485.7969 | 123.1155 | -122.8638 | 0.21515 | 0.13054 | 0.010066 | -0.010583 | 0.043233 | -0.020247 | -0.012544 | 0.0064257 | -0.036621 | 0.13733 | -0.40283 | 0.064087 | 0.10529 | 0.14191 | -0.19684 | 0.27924 | 0.24719 | -0.31128 | 122.4609 | -0.07782 | 122.8271 | 122.9279 | -0.10986 | 122.5525 | 0.032043 | 0.36621 | 122.6669 | 123.143 | 122.9691 | 123.0011 | 122.8271 | 123.111 | 123.0057 | 122.5525 | 123.0011 | 122.8271 | 123.0057 | 122.9691 | 123.111 | -0.61798 | -0.52643
4487.4844 | 123.1476 | -122.8455 | 0.18768 | 0.13054 | 0.010921 | -0.012292 | 0.041097 | -0.020247 | -0.010408 | 0.0087757 | -0.050354 | 0.13275 | -0.3891 | 0.045776 | 0.073242 | 0.09613 | -0.13733 | 0.27924 | 0.27008 | -0.32501 | 122.4564 | -0.054932 | 122.7951 | 122.8912 | -0.11444 | 122.5204 | 0.082398 | 0.33874 | 122.7081 | 123.1247 | 122.9187 | 122.9782 | 122.7951 | 123.1155 | 122.9416 | 122.5204 | 122.9782 | 122.7951 | 122.9416 | 122.9187 | 123.1155 | -0.57678 | -0.5127
4489.1719 | 123.1476 | -122.8683 | 0.21057 | 0.077133 | 0.0089979 | -0.0097284 | 0.048146 | -0.01982 | -0.014253 | 0.0072803 | -0.11902 | 0.18768 | -0.44403 | -0.018311 | -0.027466 | -0.013733 | 0.013733 | 0.15106 | 0.3067 | -0.35706 | 122.4243 | -0.022888 | 122.7493 | 122.85 | -0.23804 | 122.5113 | 0.096131 | 0.32501 | 122.8821 | 123.0194 | 122.8409 | 123.056 | 122.7493 | 123.175 | 122.8546 | 122.5113 | 123.056 | 122.7493 | 122.8546 | 122.8409 | 123.175 | -0.6546 | -0.56763
4490.8594 | 123.1338 | -122.8775 | 0.24261 | 0.016098 | 0.0098523 | -0.012292 | 0.046224 | -0.018965 | -0.01468 | 0.0057849 | -0.11444 | 0.20142 | -0.44861 | -0.009155 | -0.013733 | 0.009155 | -0.018311 | 0.16937 | 0.30212 | -0.35706 | 122.4289 | -0.041199 | 122.7631 | 122.8683 | -0.25635 | 122.5204 | 0.059509 | 0.33417 | 122.8592 | 123.0469 | 122.8638 | 123.0789 | 122.7631 | 123.1796 | 122.8867 | 122.5204 | 123.0789 | 122.7631 | 122.8867 | 122.8638 | 123.1796 | -0.69122 | -0.59967
4492.5469 | 123.1293 | -122.85 | 0.21973 | 0.077133 | 0.0085705 | -0.0080194 | 0.04366 | -0.020247 | -0.013612 | 0.0074939 | -0.13733 | 0.19684 | -0.43945 | -0.036621 | -0.022888 | -0.009155 | 0.013733 | 0.15106 | 0.30212 | -0.36621 | 122.4106 | -0.022889 | 122.7127 | 122.8134 | -0.24261 | 122.4838 | 0.082397 | 0.30212 | 122.8638 | 123.0011 | 122.8271 | 123.0469 | 122.7127 | 123.1522 | 122.8409 | 122.4838 | 123.0469 | 122.7127 | 122.8409 | 122.8271 | 123.1522 | -0.65918 | -0.58594
4494.2344 | 123.0789 | -122.8821 | 0.21057 | -0.13649 | 0.0098523 | -0.0078058 | 0.044301 | -0.019179 | -0.014039 | 0.0087757 | -0.082397 | 0.1831 | -0.42114 | 0.032043 | 0.041199 | 0.045776 | -0.027466 | 0.23346 | 0.29297 | -0.33875 | 122.4609 | -0.027466 | 122.7997 | 122.9141 | -0.16937 | 122.5433 | 0.082398 | 0.33875 | 122.8546 | 123.1155 | 122.9233 | 123.0652 | 122.7997 | 123.175 | 122.9279 | 122.5433 | 123.0652 | 122.7997 | 122.9279 | 122.9233 | 123.175 | -0.63171 | -0.54932
4495.9375 | 123.2025 | -122.8592 | 0.21057 | -0.20515 | 0.0072889 | -0.0095148 | 0.041951 | -0.020034 | -0.011903 | 0.0057849 | -0.11444 | 0.18768 | -0.44861 | 0 | 0.022888 | 0.027466 | 0.013733 | 0.22888 | 0.3067 | -0.35706 | 122.4106 | -0.022888 | 122.7448 | 122.8592 | -0.18768 | 122.5021 | 0.096131 | 0.33417 | 122.8729 | 123.0881 | 122.8821 | 123.0469 | 122.7448 | 123.1659 | 122.8867 | 122.5021 | 123.0469 | 122.7448 | 122.8867 | 122.8821 | 123.1659 | -0.65918 | -0.56763
4497.625 | 123.1567 | -122.8729 | 0.21057 | -0.17464 | 0.0096387 | -0.0097284 | 0.043233 | -0.019606 | -0.013185 | 0.0068531 | -0.086975 | 0.20142 | -0.42114 | 0.018311 | 0.059509 | 0.050354 | -0.022888 | 0.23804 | 0.30212 | -0.35248 | 122.4518 | -0.009155 | 122.7859 | 122.8912 | -0.15106 | 122.5204 | 0.091553 | 0.33417 | 122.85 | 123.111 | 122.9324 | 123.0743 | 122.7859 | 123.175 | 122.9233 | 122.5204 | 123.0743 | 122.7859 | 122.9233 | 122.9324 | 123.175 | -0.63171 | -0.56305
4499.3125 | 123.1338 | -122.8638 | 0.21515 | -0.15938 | 0.0098523 | -0.012078 | 0.044515 | -0.018965 | -0.015107 | 0.0057849 | -0.07782 | 0.17853 | -0.43488 | 0.013733 | 0.045776 | 0.050354 | -0.022888 | 0.23804 | 0.29755 | -0.33875 | 122.4289 | -0.036621 | 122.7859 | 122.8775 | -0.16937 | 122.525 | 0.082397 | 0.35706 | 122.8409 | 123.1018 | 122.9095 | 123.0423 | 122.7859 | 123.1613 | 122.9141 | 122.525 | 123.0423 | 122.7859 | 122.9141 | 122.9095 | 123.1613 | -0.65002 | -0.55389
4501.0156 | 123.1842 | -122.8409 | 0.1831 | -0.12886 | 0.0070751 | -0.014642 | 0.034688 | -0.021956 | -0.012971 | 0.0081347 | -0.054932 | 0.16937 | -0.39825 | 0.064087 | 0.12817 | 0.14648 | -0.12817 | 0.33417 | 0.2655 | -0.33417 | 122.4426 | -0.013732 | 122.7859 | 122.905 | -0.054931 | 122.5067 | 0.082398 | 0.34332 | 122.7127 | 123.175 | 122.9691 | 123.0103 | 122.7859 | 123.1064 | 122.9874 | 122.5067 | 123.0103 | 122.7859 | 122.9874 | 122.9691 | 123.1064 | -0.58136 | -0.51727
4502.7031 | 123.2391 | -122.85 | 0.17395 | 0.031357 | 0.0094251 | -0.011224 | 0.03597 | -0.019179 | -0.013399 | 0.0047167 | -0.07782 | 0.17853 | -0.41657 | 0.045776 | 0.07782 | 0.10529 | -0.1236 | 0.29297 | 0.24719 | -0.32501 | 122.4335 | 0.004578 | 122.7722 | 122.8958 | -0.09613 | 122.525 | 0.073242 | 0.33875 | 122.7264 | 123.143 | 122.9279 | 123.0286 | 122.7722 | 123.0972 | 122.9553 | 122.525 | 123.0286 | 122.7722 | 122.9553 | 122.9279 | 123.0972 | -0.59052 | -0.49896
4504.4531 | 123.1476 | -122.8775 | 0.20599 | -0.12886 | 0.0085705 | -0.01336 | 0.047933 | -0.020034 | -0.014894 | 0.0081347 | -0.073242 | 0.19684 | -0.4303 | 0.027466 | 0.027466 | 0.045776 | -0.018311 | 0.24261 | 0.29755 | -0.34332 | 122.4472 | -0.009156 | 122.8043 | 122.905 | -0.17853 | 122.5342 | 0.091552 | 0.35706 | 122.8592 | 123.1201 | 122.905 | 123.0743 | 122.8043 | 123.175 | 122.9233 | 122.5342 | 123.0743 | 122.8043 | 122.9233 | 122.905 | 123.175 | -0.63629 | -0.54932
4506.1406 | 123.175 | -122.8546 | 0.19226 | -0.17464 | 0.0077161 | -0.012292 | 0.039388 | -0.019606 | -0.013612 | 0.0077075 | -0.013733 | 0.16479 | -0.39825 | 0.082397 | 0.10071 | 0.11444 | -0.086975 | 0.32044 | 0.28381 | -0.32959 | 122.4564 | -0.027466 | 122.8409 | 122.937 | -0.091553 | 122.525 | 0.091552 | 0.38452 | 122.7676 | 123.175 | 122.9553 | 123.0194 | 122.8409 | 123.1384 | 122.9691 | 122.525 | 123.0194 | 122.8409 | 122.9691 | 122.9553 | 123.1384 | -0.59052 | -0.52185
4507.8281 | 123.1842 | -122.85 | 0.18768 | -0.044937 | 0.0094251 | -0.0073786 | 0.037252 | -0.020247 | -0.013399 | 0.0032215 | -0.064087 | 0.17395 | -0.39368 | 0.064087 | 0.091553 | 0.11444 | -0.12817 | 0.32044 | 0.27924 | -0.32959 | 122.4564 | -0.013733 | 122.7859 | 122.9141 | -0.09613 | 122.5204 | 0.091553 | 0.32959 | 122.7219 | 123.1705 | 122.9416 | 123.024 | 122.7859 | 123.1293 | 122.9645 | 122.5204 | 123.024 | 122.7859 | 122.9645 | 122.9416 | 123.1293 | -0.58136 | -0.51727
4509.5312 | 123.1888 | -122.8546 | 0.21515 | -0.17464 | 0.0077161 | -0.01101 | 0.04067 | -0.020674 | -0.015962 | 0.0053577 | -0.009155 | 0.16022 | -0.37994 | 0.10986 | 0.12817 | 0.12817 | -0.1236 | 0.35248 | 0.26093 | -0.29755 | 122.4747 | -0.054932 | 122.8455 | 122.9645 | -0.086975 | 122.5571 | 0.045776 | 0.37079 | 122.731 | 123.2071 | 122.9828 | 123.0148 | 122.8455 | 123.1155 | 122.9828 | 122.5571 | 123.0148 | 122.8455 | 122.9828 | 122.9828 | 123.1155 | -0.59509 | -0.5127
4511.2188 | 123.1842 | -122.8409 | 0.19684 | -0.22804 | 0.010707 | -0.011437 | 0.041524 | -0.021315 | -0.012544 | 0.0051441 | -0.022888 | 0.16479 | -0.39368 | 0.10986 | 0.10986 | 0.13733 | -0.1236 | 0.3479 | 0.26093 | -0.32959 | 122.4472 | -0.032043 | 122.818 | 122.9507 | -0.086975 | 122.5113 | 0.064087 | 0.37079 | 122.7173 | 123.1888 | 122.9507 | 123.0057 | 122.818 | 123.1018 | 122.9782 | 122.5113 | 123.0057 | 122.818 | 122.9782 | 122.9507 | 123.1018 | -0.59052 | -0.52643
4512.9062 | 123.1934 | -122.8363 | 0.17853 | -0.13649 | 0.0096387 | -0.010369 | 0.039815 | -0.022597 | -0.013612 | 0.0062121 | -0.032043 | 0.1831 | -0.38452 | 0.10529 | 0.13275 | 0.13733 | -0.17395 | 0.32501 | 0.27466 | -0.32959 | 122.4518 | 0.004577 | 122.8043 | 122.9416 | -0.045777 | 122.5067 | 0.09613 | 0.35248 | 122.6624 | 123.1613 | 122.9691 | 123.0194 | 122.8043 | 123.111 | 122.9736 | 122.5067 | 123.0194 | 122.8043 | 122.9736 | 122.9691 | 123.111 | -0.56305 | -0.50812
4514.5938 | 123.1476 | -122.8729 | 0.19684 | 0.11528 | 0.010921 | -0.0086602 | 0.045369 | -0.019606 | -0.014039 | 0.0072803 | -0.10986 | 0.19684 | -0.43488 | -0.004578 | -0.027466 | -0.004578 | -0.027466 | 0.15564 | 0.29755 | -0.35706 | 122.438 | 0 | 122.7631 | 122.8683 | -0.2243 | 122.5159 | 0.10071 | 0.32501 | 122.8455 | 123.0286 | 122.8455 | 123.0698 | 122.7631 | 123.1705 | 122.8683 | 122.5159 | 123.0698 | 122.7631 | 122.8683 | 122.8455 | 123.1705 | -0.63171 | -0.55389
4516.2812 | 123.1338 | -122.8729 | 0.19684 | 0.16869 | 0.012629 | -0.0093012 | 0.043874 | -0.020034 | -0.01233 | 0.0059985 | -0.12817 | 0.21515 | -0.42572 | -0.013733 | -0.009155 | -0.004578 | -0.027466 | 0.16022 | 0.29297 | -0.35706 | 122.4472 | 0.018311 | 122.7448 | 122.8592 | -0.20599 | 122.5159 | 0.096131 | 0.29755 | 122.8455 | 123.0331 | 122.8638 | 123.0881 | 122.7448 | 123.1659 | 122.8683 | 122.5159 | 123.0881 | 122.7448 | 122.8683 | 122.8638 | 123.1659 | -0.62256 | -0.55389
4518.0312 | 123.1384 | -122.8912 | 0.21973 | 0.12291 | 0.01028 | -0.011865 | 0.04366 | -0.017897 | -0.014253 | 0.0072803 | -0.10986 | 0.19226 | -0.43488 | -0.009155 | 0.009155 | 0.027466 | -0.07782 | 0.1831 | 0.30212 | -0.35706 | 122.4564 | -0.027466 | 122.7814 | 122.8821 | -0.21057 | 122.5342 | 0.082397 | 0.32501 | 122.8134 | 123.0743 | 122.9004 | 123.0835 | 122.7814 | 123.1934 | 122.9187 | 122.5342 | 123.0835 | 122.7814 | 122.9187 | 122.9004 | 123.1934 | -0.6546 | -0.57678
4519.7188 | 123.1293 | -122.9004 | 0.21515 | 0.00083945 | 0.0094251 | -0.008233 | 0.044942 | -0.019179 | -0.014039 | 0.0072803 | -0.086975 | 0.19684 | -0.42572 | -0.009155 | -0.013733 | 0.004578 | -0.018311 | 0.16937 | 0.3067 | -0.36163 | 122.4747 | -0.018311 | 122.8134 | 122.8912 | -0.22888 | 122.5388 | 0.091553 | 0.33874 | 122.8821 | 123.0698 | 122.8867 | 123.0972 | 122.8134 | 123.2071 | 122.905 | 122.5388 | 123.0972 | 122.8134 | 122.905 | 122.8867 | 123.2071 | -0.64087 | -0.57678
4521.4688 | 123.1934 | -122.8683 | 0.18768 | -0.21278 | 0.0087841 | -0.014642 | 0.036397 | -0.020888 | -0.012544 | 0.0062121 | -0.027466 | 0.16479 | -0.37537 | 0.082397 | 0.11902 | 0.13275 | -0.11444 | 0.33875 | 0.26093 | -0.32959 | 122.493 | -0.022888 | 122.8409 | 122.9507 | -0.068664 | 122.5388 | 0.073242 | 0.3479 | 122.7539 | 123.2071 | 122.9874 | 123.0331 | 122.8409 | 123.1293 | 123.0011 | 122.5388 | 123.0331 | 122.8409 | 123.0011 | 122.9874 | 123.1293 | -0.56305 | -0.51727
4523.1562 | 123.2208 | -122.8455 | 0.18768 | 0.061874 | 0.010493 | -0.0050286 | 0.040029 | -0.022597 | -0.011476 | 0.0066393 | -0.086975 | 0.18768 | -0.39825 | 0.032043 | 0.073242 | 0.082397 | -0.10529 | 0.26093 | 0.27466 | -0.32501 | 122.4472 | 0 | 122.7585 | 122.8775 | -0.11444 | 122.5204 | 0.086975 | 0.31128 | 122.7402 | 123.1064 | 122.9187 | 123.0331 | 122.7585 | 123.1201 | 122.9279 | 122.5204 | 123.0331 | 122.7585 | 122.9279 | 122.9187 | 123.1201 | -0.58594 | -0.5127
4524.8438 | 123.1201 | -122.8638 | 0.21057 | 0.13054 | 0.0087841 | -0.012719 | 0.04131 | -0.018325 | -0.012544 | 0.0066393 | -0.032043 | 0.16479 | -0.40283 | 0.073242 | 0.10071 | 0.10529 | -0.17853 | 0.29297 | 0.25635 | -0.3479 | 122.4609 | -0.045776 | 122.8317 | 122.937 | -0.10986 | 122.5159 | 0.045777 | 0.37079 | 122.6852 | 123.1567 | 122.9645 | 123.0286 | 122.8317 | 123.1201 | 122.9691 | 122.5159 | 123.0286 | 122.8317 | 122.9691 | 122.9645 | 123.1201 | -0.6134 | -0.55847
4526.5469 | 123.0698 | -122.8546 | 0.21973 | 0.19157 | 0.010921 | -0.0095148 | 0.045156 | -0.01747 | -0.013612 | 0.0057849 | -0.022888 | 0.16937 | -0.38452 | 0.086975 | 0.091553 | 0.15106 | -0.19684 | 0.28381 | 0.24261 | -0.31128 | 122.4701 | -0.050354 | 122.8317 | 122.9416 | -0.12817 | 122.5433 | 0.022888 | 0.36163 | 122.6578 | 123.1384 | 122.9462 | 123.024 | 122.8317 | 123.0972 | 123.0057 | 122.5433 | 123.024 | 122.8317 | 123.0057 | 122.9462 | 123.0972 | -0.60425 | -0.53101
4528.2656 | 123.1613 | -122.8317 | 0.18768 | -0.16701 | 0.0064343 | -0.014428 | 0.039174 | -0.019179 | -0.012758 | 0.0051441 | -0.032043 | 0.16479 | -0.3891 | 0.10071 | 0.13275 | 0.13733 | -0.15564 | 0.35248 | 0.2655 | -0.34332 | 122.4426 | -0.022888 | 122.7997 | 122.9324 | -0.054932 | 122.4884 | 0.07782 | 0.35706 | 122.6761 | 123.1842 | 122.9645 | 122.9965 | 122.7997 | 123.0972 | 122.9691 | 122.4884 | 122.9965 | 122.7997 | 122.9691 | 122.9645 | 123.0972 | -0.57678 | -0.53101
4530 | 123.2254 | -122.8546 | 0.1831 | 0.023727 | 0.010493 | -0.012933 | 0.039388 | -0.020674 | -0.012758 | 0.0042895 | -0.07782 | 0.16479 | -0.39825 | 0.050354 | 0.059509 | 0.086975 | -0.11444 | 0.27466 | 0.27924 | -0.33875 | 122.4564 | -0.01831 | 122.7768 | 122.905 | -0.1236 | 122.5159 | 0.096131 | 0.32043 | 122.7402 | 123.1293 | 122.9141 | 123.0194 | 122.7768 | 123.1338 | 122.9416 | 122.5159 | 123.0194 | 122.7768 | 122.9416 | 122.9141 | 123.1338 | -0.58136 | -0.52185
4531.6875 | 123.2117 | -122.8409 | 0.18768 | 0.069504 | 0.011989 | -0.0093012 | 0.04131 | -0.021102 | -0.01233 | 0.0077075 | -0.054932 | 0.16022 | -0.39825 | 0.059509 | 0.073242 | 0.082397 | -0.13733 | 0.2655 | 0.28381 | -0.34332 | 122.4426 | -0.027466 | 122.7859 | 122.9004 | -0.11444 | 122.4976 | 0.09613 | 0.34332 | 122.7036 | 123.1064 | 122.9141 | 123.0011 | 122.7859 | 123.1247 | 122.9233 | 122.4976 | 123.0011 | 122.7859 | 122.9233 | 122.9141 | 123.1247 | -0.58594 | -0.53101
4533.3906 | 123.2254 | -122.8317 | 0.20142 | -0.022049 | 0.0098523 | -0.006524 | 0.040456 | -0.021102 | -0.012971 | 0.0038623 | -0.068665 | 0.16937 | -0.42114 | 0.059509 | 0.07782 | 0.10529 | -0.13275 | 0.31586 | 0.27466 | -0.34332 | 122.4106 | -0.032043 | 122.7631 | 122.8912 | -0.1236 | 122.4884 | 0.073242 | 0.35248 | 122.699 | 123.1476 | 122.9095 | 123.0011 | 122.7631 | 123.1064 | 122.937 | 122.4884 | 123.0011 | 122.7631 | 122.937 | 122.9095 | 123.1064 | -0.62256 | -0.54474
4535.0781 | 123.2162 | -122.85 | 0.17853 | 0.00083945 | 0.0094251 | -0.012505 | 0.041524 | -0.023879 | -0.011049 | 0.0053577 | -0.082397 | 0.1831 | -0.39825 | 0.059509 | 0.082397 | 0.09613 | -0.12817 | 0.30212 | 0.26093 | -0.34332 | 122.4518 | 0.004577 | 122.7676 | 122.9095 | -0.096131 | 122.5067 | 0.082397 | 0.31586 | 122.7219 | 123.1522 | 122.9324 | 123.0331 | 122.7676 | 123.111 | 122.9462 | 122.5067 | 123.0331 | 122.7676 | 122.9462 | 122.9324 | 123.111 | -0.57678 | -0.52185
4536.7656 | 123.0972 | -122.8775 | 0.20142 | 0.1992 | 0.0081433 | -0.010796 | 0.043874 | -0.020461 | -0.013399 | 0.0064257 | 0 | 0.14648 | -0.3891 | 0.09613 | 0.09613 | 0.13733 | -0.21973 | 0.28839 | 0.26093 | -0.3067 | 122.4884 | -0.054932 | 122.8775 | 122.9736 | -0.10529 | 122.5708 | 0.059509 | 0.3891 | 122.6578 | 123.1659 | 122.9736 | 123.024 | 122.8775 | 123.1384 | 123.0148 | 122.5708 | 123.024 | 122.8775 | 123.0148 | 122.9736 | 123.1384 | -0.59052 | -0.50812
4538.5 | 123.0743 | -122.8867 | 0.2243 | 0.17632 | 0.0092115 | -0.014214 | 0.043233 | -0.018752 | -0.012758 | 0.0068531 | -0.013733 | 0.17395 | -0.41199 | 0.091553 | 0.086975 | 0.12817 | -0.19684 | 0.29755 | 0.25635 | -0.30212 | 122.4747 | -0.050354 | 122.8729 | 122.9782 | -0.13733 | 122.5845 | 0.032044 | 0.39825 | 122.6898 | 123.1842 | 122.9736 | 123.0606 | 122.8729 | 123.143 | 123.0148 | 122.5845 | 123.0606 | 122.8729 | 123.0148 | 122.9736 | 123.143 | -0.63629 | -0.52643
4540.1875 | 123.0927 | -122.8821 | 0.23346 | -0.1136 | 0.0087841 | -0.010156 | 0.047506 | -0.01982 | -0.017244 | 0.0083483 | -0.059509 | 0.20599 | -0.42572 | 0.050354 | 0.041199 | 0.054932 | -0.045776 | 0.23804 | 0.27924 | -0.34332 | 122.4564 | -0.027465 | 122.8226 | 122.9324 | -0.19226 | 122.5388 | 0.045777 | 0.36621 | 122.8363 | 123.1201 | 122.9233 | 123.0881 | 122.8226 | 123.1613 | 122.937 | 122.5388 | 123.0881 | 122.8226 | 122.937 | 122.9233 | 123.1613 | -0.65918 | -0.57678
4541.9375 | 123.23 | -122.8363 | 0.18768 | 0.031357 | 0.0096387 | -0.01101 | 0.036397 | -0.021315 | -0.01169 | 0.0066393 | -0.073242 | 0.17853 | -0.38452 | 0.032043 | 0.07782 | 0.086975 | -0.12817 | 0.27008 | 0.27008 | -0.33417 | 122.4518 | -0.009155 | 122.7631 | 122.8683 | -0.10986 | 122.5021 | 0.082398 | 0.31128 | 122.7081 | 123.1064 | 122.9141 | 123.0148 | 122.7631 | 123.1064 | 122.9233 | 122.5021 | 123.0148 | 122.7631 | 122.9233 | 122.9141 | 123.1064 | -0.5722 | -0.52185
4543.625 | 123.1796 | -122.8638 | 0.19684 | -0.16701 | 0.0096387 | -0.010583 | 0.040456 | -0.021956 | -0.01233 | 0.0045031 | -0.013733 | 0.16937 | -0.39368 | 0.10529 | 0.1236 | 0.12817 | -0.13275 | 0.3479 | 0.25635 | -0.32501 | 122.4701 | -0.027465 | 122.85 | 122.9691 | -0.073242 | 122.5388 | 0.05951 | 0.37994 | 122.731 | 123.2117 | 122.9874 | 123.0331 | 122.85 | 123.1201 | 122.9919 | 122.5388 | 123.0331 | 122.85 | 122.9919 | 122.9874 | 123.1201 | -0.59052 | -0.52185
4545.3438 | 123.2483 | -122.8455 | 0.17395 | -0.23567 | 0.011561 | -0.010156 | 0.043874 | -0.020247 | -0.01233 | 0.0064257 | -0.10071 | 0.22888 | -0.41657 | -0.004578 | 0.013733 | 0.009155 | 0.032043 | 0.21515 | 0.30212 | -0.37994 | 122.4289 | 0.054932 | 122.7448 | 122.8409 | -0.16022 | 122.4655 | 0.12817 | 0.31586 | 122.8775 | 123.0606 | 122.8592 | 123.0743 | 122.7448 | 123.1476 | 122.8546 | 122.4655 | 123.0743 | 122.7448 | 122.8546 | 122.8592 | 123.1476 | -0.59052 | -0.55389
4547.0312 | 123.2208 | -122.8455 | 0.18768 | -0.022049 | 0.0062207 | -0.015923 | 0.038747 | -0.021102 | -0.012758 | 0.0066393 | -0.068665 | 0.18768 | -0.38452 | 0.059509 | 0.09613 | 0.091553 | -0.1236 | 0.3067 | 0.27466 | -0.32501 | 122.4609 | 0 | 122.7768 | 122.905 | -0.091553 | 122.5204 | 0.086975 | 0.31586 | 122.7219 | 123.1522 | 122.9416 | 123.0331 | 122.7768 | 123.1201 | 122.937 | 122.5204 | 123.0331 | 122.7768 | 122.937 | 122.9416 | 123.1201 | -0.5722 | -0.5127
4548.7188 | 123.2346 | -122.8134 | 0.19226 | 0.00083945 | 0.0085705 | -0.013146 | 0.04131 | -0.019179 | -0.013185 | 0.0064257 | -0.082397 | 0.15106 | -0.39368 | 0.041199 | 0.068665 | 0.09613 | -0.11444 | 0.29755 | 0.27924 | -0.32044 | 122.4197 | -0.041199 | 122.731 | 122.8546 | -0.1236 | 122.493 | 0.086975 | 0.31128 | 122.699 | 123.111 | 122.8821 | 122.9645 | 122.731 | 123.0927 | 122.9095 | 122.493 | 122.9645 | 122.731 | 122.9095 | 122.8821 | 123.0927 | -0.58594 | -0.5127
4550.4062 | 123.2483 | -122.8134 | 0.17853 | -0.26619 | 0.012416 | -0.011437 | 0.04366 | -0.019606 | -0.013399 | 0.0057849 | -0.11444 | 0.21973 | -0.43945 | -0.004578 | 0 | 0 | 0.054932 | 0.20599 | 0.31128 | -0.36621 | 122.374 | 0.041199 | 122.699 | 122.8088 | -0.17853 | 122.4472 | 0.13275 | 0.32501 | 122.8683 | 123.0194 | 122.8134 | 123.0331 | 122.699 | 123.1247 | 122.8134 | 122.4472 | 123.0331 | 122.699 | 122.8134 | 122.8134 | 123.1247 | -0.61798 | -0.54474
4552.125 | 123.23 | -122.8317 | 0.17395 | 0.061874 | 0.0094251 | -0.013787 | 0.040456 | -0.018965 | -0.012544 | 0.0085619 | -0.068665 | 0.1831 | -0.41657 | 0.045776 | 0.073242 | 0.091553 | -0.11444 | 0.25635 | 0.27008 | -0.32501 | 122.4152 | 0.009155 | 122.7631 | 122.8775 | -0.10071 | 122.5067 | 0.096131 | 0.3479 | 122.7173 | 123.0881 | 122.905 | 123.0148 | 122.7631 | 123.1018 | 122.9233 | 122.5067 | 123.0148 | 122.7631 | 122.9233 | 122.905 | 123.1018 | -0.59052 | -0.49896
4553.8125 | 123.111 | -122.8867 | 0.2243 | 0.20683 | 0.0085705 | -0.010796 | 0.044728 | -0.019606 | -0.013826 | 0.0066393 | -0.013733 | 0.16479 | -0.39825 | 0.10529 | 0.10529 | 0.13733 | -0.18768 | 0.31586 | 0.24261 | -0.32044 | 122.4884 | -0.059509 | 122.8729 | 122.9919 | -0.11902 | 122.5662 | 0.018311 | 0.38452 | 122.699 | 123.2025 | 122.9919 | 123.0515 | 122.8729 | 123.1293 | 123.024 | 122.5662 | 123.0515 | 122.8729 | 123.024 | 122.9919 | 123.1293 | -0.62256 | -0.54474
4555.5312 | 123.23 | -122.8409 | 0.16937 | -0.029679 | 0.01028 | -0.011651 | 0.04131 | -0.021743 | -0.010621 | 0.0062121 | -0.064087 | 0.1831 | -0.41657 | 0.064087 | 0.09613 | 0.11902 | -0.13275 | 0.29755 | 0.25177 | -0.33417 | 122.4243 | 0.013732 | 122.7768 | 122.905 | -0.073243 | 122.5067 | 0.082397 | 0.35248 | 122.7081 | 123.1384 | 122.937 | 123.024 | 122.7768 | 123.0927 | 122.9599 | 122.5067 | 123.024 | 122.7768 | 122.9599 | 122.937 | 123.0927 | -0.58594 | -0.50354
4557.2188 | 123.1888 | -122.8271 | 0.19684 | -0.1136 | 0.0070751 | -0.014428 | 0.039174 | -0.021743 | -0.014467 | 0.0066393 | -0.064087 | 0.16479 | -0.38452 | 0.09613 | 0.1236 | 0.13275 | -0.14191 | 0.35248 | 0.27466 | -0.32959 | 122.4426 | -0.032043 | 122.7631 | 122.9233 | -0.073242 | 122.4976 | 0.07782 | 0.32043 | 122.6852 | 123.1796 | 122.9507 | 122.9919 | 122.7631 | 123.1018 | 122.9599 | 122.4976 | 122.9919 | 122.7631 | 122.9599 | 122.9507 | 123.1018 | -0.58136 | -0.52643
4558.9062 | 123.1384 | -122.8683 | 0.21515 | 0.13054 | 0.010921 | -0.0095148 | 0.048787 | -0.018111 | -0.015321 | 0.0055713 | -0.10071 | 0.21057 | -0.42572 | 0.018311 | -0.004578 | 0.018311 | -0.068665 | 0.19684 | 0.29755 | -0.3479 | 122.4426 | -0.004578 | 122.7676 | 122.8867 | -0.21973 | 122.5204 | 0.082397 | 0.32501 | 122.7997 | 123.0652 | 122.8638 | 123.0789 | 122.7676 | 123.1659 | 122.8867 | 122.5204 | 123.0789 | 122.7676 | 122.8867 | 122.8638 | 123.1659 | -0.64087 | -0.56305
4560.6094 | 123.2208 | -122.85 | 0.20599 | -0.23567 | 0.01028 | -0.012292 | 0.043874 | -0.020888 | -0.013185 | 0.0085619 | -0.12817 | 0.21057 | -0.42114 | 0.004578 | 0.018311 | -0.009155 | 0.041199 | 0.19684 | 0.3067 | -0.37079 | 122.4289 | 0.004577 | 122.7219 | 122.8546 | -0.18768 | 122.4792 | 0.10071 | 0.29297 | 122.8912 | 123.0469 | 122.8683 | 123.0606 | 122.7219 | 123.1567 | 122.8409 | 122.4792 | 123.0606 | 122.7219 | 122.8409 | 122.8683 | 123.1567 | -0.62714 | -0.57678
4562.2969 | 123.2162 | -122.8409 | 0.19684 | -0.20515 | 0.0072889 | -0.014001 | 0.040242 | -0.020674 | -0.015321 | 0.0059985 | -0.036621 | 0.17395 | -0.39825 | 0.068665 | 0.091553 | 0.09613 | -0.050354 | 0.29755 | 0.28381 | -0.33417 | 122.4426 | -0.022888 | 122.8043 | 122.9095 | -0.10529 | 122.5067 | 0.086975 | 0.36163 | 122.7905 | 123.1384 | 122.9324 | 123.0148 | 122.8043 | 123.1247 | 122.937 | 122.5067 | 123.0148 | 122.8043 | 122.937 | 122.9324 | 123.1247 | -0.59509 | -0.531
4564 | 123.111 | -122.8867 | 0.24719 | -0.075455 | 0.011561 | -0.015069 | 0.045797 | -0.019393 | -0.016176 | 0.0057849 | -0.050354 | 0.19684 | -0.43488 | 0.045776 | 0.045776 | 0.059509 | -0.022888 | 0.24719 | 0.30212 | -0.35248 | 122.4518 | -0.050354 | 122.8363 | 122.9324 | -0.20142 | 122.5342 | 0.054932 | 0.38452 | 122.8638 | 123.1338 | 122.9324 | 123.0835 | 122.8363 | 123.1888 | 122.9462 | 122.5342 | 123.0835 | 122.8363 | 122.9462 | 122.9324 | 123.1888 | -0.68207 | -0.59967
4565.6875 | 123.2437 | -122.8546 | 0.18768 | -0.26619 | 0.011134 | -0.0073786 | 0.040456 | -0.021315 | -0.014894 | 0.0064257 | -0.11902 | 0.20599 | -0.4303 | -0.013733 | 0.009155 | 0 | 0.059509 | 0.21057 | 0.31586 | -0.35706 | 122.4243 | 0.018311 | 122.7356 | 122.8409 | -0.17853 | 122.4976 | 0.12817 | 0.31128 | 122.9141 | 123.0652 | 122.8638 | 123.0606 | 122.7356 | 123.1705 | 122.8546 | 122.4976 | 123.0606 | 122.7356 | 122.8546 | 122.8638 | 123.1705 | -0.61798 | -0.54474
4567.375 | 123.2208 | -122.8592 | 0.17853 | -0.23567 | 0.0098523 | -0.015283 | 0.042592 | -0.01982 | -0.014467 | 0.0057849 | -0.10529 | 0.20599 | -0.41657 | -0.004578 | 0.009155 | 0.013733 | 0.041199 | 0.20599 | 0.31586 | -0.35706 | 122.4426 | 0.027466 | 122.7539 | 122.8546 | -0.16937 | 122.5021 | 0.13733 | 0.31128 | 122.9004 | 123.0652 | 122.8683 | 123.0652 | 122.7539 | 123.175 | 122.8729 | 122.5021 | 123.0652 | 122.7539 | 122.8729 | 122.8683 | 123.175 | -0.59509 | -0.53558
4569.0625 | 123.1934 | -122.8455 | 0.18768 | -0.060196 | 0.0064343 | -0.011224 | 0.038533 | -0.018752 | -0.013399 | 0.0070667 | -0.050354 | 0.16479 | -0.3891 | 0.086975 | 0.11444 | 0.10986 | -0.13733 | 0.31586 | 0.2655 | -0.32501 | 122.4564 | -0.022888 | 122.7951 | 122.9324 | -0.073242 | 122.5204 | 0.07782 | 0.33874 | 122.7081 | 123.1613 | 122.9599 | 123.0103 | 122.7951 | 123.111 | 122.9553 | 122.5204 | 123.0103 | 122.7951 | 122.9553 | 122.9599 | 123.111 | -0.57678 | -0.5127
4570.7812 | 123.1338 | -122.8867 | 0.21057 | 0.13054 | 0.0068615 | -0.0078058 | 0.047078 | -0.019606 | -0.014253 | 0.0072803 | -0.10986 | 0.19684 | -0.4303 | 0.009155 | 0.018311 | 0.036621 | -0.091553 | 0.21515 | 0.29755 | -0.35248 | 122.4564 | -0.013733 | 122.7768 | 122.8958 | -0.19226 | 122.5342 | 0.086975 | 0.32044 | 122.7951 | 123.1018 | 122.905 | 123.0835 | 122.7768 | 123.1842 | 122.9233 | 122.5342 | 123.0835 | 122.7768 | 122.9233 | 122.905 | 123.1842 | -0.64087 | -0.56305
4572.5156 | 123.2529 | -122.8271 | 0.17853 | -0.26619 | 0.0092115 | -0.014214 | 0.039388 | -0.023238 | -0.01233 | 0.0047167 | -0.13733 | 0.20599 | -0.43945 | -0.013733 | 0.004578 | 0.004578 | 0.064087 | 0.21057 | 0.30212 | -0.35706 | 122.3877 | 0.027466 | 122.6898 | 122.8134 | -0.17395 | 122.4701 | 0.1236 | 0.30212 | 122.8912 | 123.0377 | 122.8317 | 123.0331 | 122.6898 | 123.1293 | 122.8317 | 122.4701 | 123.0331 | 122.6898 | 122.8317 | 122.8317 | 123.1293 | -0.61798 | -0.53558
4574.2031 | 123.2208 | -122.8546 | 0.1831 | -0.25856 | 0.0081433 | -0.009942 | 0.043447 | -0.018965 | -0.01233 | 0.0059985 | -0.1236 | 0.21515 | -0.43488 | -0.009155 | 0.009155 | 0.009155 | 0.041199 | 0.19684 | 0.32959 | -0.35248 | 122.4197 | 0.032044 | 122.731 | 122.8455 | -0.17395 | 122.5021 | 0.14649 | 0.31128 | 122.8958 | 123.0515 | 122.8638 | 123.0698 | 122.731 | 123.1842 | 122.8638 | 122.5021 | 123.0698 | 122.731 | 122.8638 | 122.8638 | 123.1842 | -0.61798 | -0.53558
4575.9375 | 123.1064 | -122.9233 | 0.21057 | -0.10597 | 0.010493 | -0.013574 | 0.047078 | -0.01982 | -0.015748 | 0.0072803 | -0.054932 | 0.19684 | -0.4303 | 0.032043 | 0.036621 | 0.054932 | -0.032043 | 0.22888 | 0.3067 | -0.33417 | 122.493 | -0.013733 | 122.8683 | 122.9553 | -0.17395 | 122.5891 | 0.096131 | 0.37537 | 122.8912 | 123.1522 | 122.9599 | 123.1201 | 122.8683 | 123.23 | 122.9782 | 122.5891 | 123.1201 | 122.8683 | 122.9782 | 122.9599 | 123.23 | -0.64087 | -0.54474
4577.625 | 123.111 | -122.9004 | 0.2243 | -0.098343 | 0.010707 | -0.010796 | 0.04601 | -0.017684 | -0.015535 | 0.0053577 | -0.050354 | 0.20142 | -0.41657 | 0.022888 | 0.041199 | 0.059509 | -0.022888 | 0.2243 | 0.30212 | -0.33417 | 122.4838 | -0.022888 | 122.85 | 122.9233 | -0.18311 | 122.5662 | 0.07782 | 0.36621 | 122.8775 | 123.1247 | 122.9416 | 123.1018 | 122.85 | 123.2025 | 122.9599 | 122.5662 | 123.1018 | 122.85 | 122.9599 | 122.9416 | 123.2025 | -0.64087 | -0.55847
4579.3125 | 123.143 | -122.8455 | 0.21515 | 0.12291 | 0.0087841 | -0.01101 | 0.043233 | -0.018965 | -0.015962 | 0.0068531 | -0.1236 | 0.20142 | -0.41199 | -0.032043 | -0.013733 | 0.004578 | -0.022888 | 0.16022 | 0.29297 | -0.37079 | 122.4335 | -0.013733 | 122.7219 | 122.8134 | -0.22888 | 122.4747 | 0.07782 | 0.28839 | 122.8226 | 123.0057 | 122.8317 | 123.0469 | 122.7219 | 123.1384 | 122.85 | 122.4747 | 123.0469 | 122.7219 | 122.85 | 122.8317 | 123.1384 | -0.62714 | -0.58594
4581.0312 | 123.111 | -122.9004 | 0.20599 | 0.16106 | 0.0085705 | -0.011224 | 0.03832 | -0.020034 | -0.013185 | 0.0068531 | -0.036621 | 0.14648 | -0.38452 | 0.064087 | 0.10986 | 0.14191 | -0.17395 | 0.30212 | 0.27008 | -0.29755 | 122.5159 | -0.05951 | 122.8638 | 122.9645 | -0.096131 | 122.6028 | 0.064087 | 0.3479 | 122.7264 | 123.2025 | 123.0103 | 123.0469 | 122.8638 | 123.1705 | 123.0423 | 122.6028 | 123.0469 | 122.8638 | 123.0423 | 123.0103 | 123.1705 | -0.59052 | -0.50354
4582.7188 | 123.0789 | -122.8683 | 0.21057 | 0.13817 | 0.0098523 | -0.010156 | 0.043874 | -0.01747 | -0.012971 | 0.0066393 | -0.009155 | 0.16479 | -0.37537 | 0.07782 | 0.09613 | 0.14191 | -0.17853 | 0.28381 | 0.25177 | -0.31128 | 122.493 | -0.045776 | 122.8592 | 122.9462 | -0.11444 | 122.5571 | 0.041199 | 0.36621 | 122.6898 | 123.1522 | 122.9645 | 123.0331 | 122.8592 | 123.1201 | 123.0103 | 122.5571 | 123.0331 | 122.8592 | 123.0103 | 122.9645 | 123.1201 | -0.58594 | -0.52185
4584.4219 | 123.1384 | -122.8638 | 0.21515 | 0.16869 | 0.0085705 | -0.01101 | 0.046224 | -0.018752 | -0.014253 | 0.0066393 | -0.11902 | 0.21057 | -0.4303 | -0.032043 | -0.013733 | -0.009155 | -0.013733 | 0.16479 | 0.29755 | -0.36163 | 122.4335 | -0.004578 | 122.7448 | 122.8317 | -0.22888 | 122.5021 | 0.082397 | 0.31128 | 122.85 | 123.0286 | 122.85 | 123.0743 | 122.7448 | 123.1613 | 122.8546 | 122.5021 | 123.0743 | 122.7448 | 122.8546 | 122.85 | 123.1613 | -0.64545 | -0.57678
4586.1562 | 123.2254 | -122.818 | 0.17853 | 0.023727 | 0.0077161 | -0.015496 | 0.037892 | -0.022597 | -0.012544 | 0.0059985 | -0.082397 | 0.17853 | -0.37079 | 0.027466 | 0.073242 | 0.091553 | -0.091553 | 0.2655 | 0.26093 | -0.33875 | 122.4472 | 0 | 122.7356 | 122.8455 | -0.10529 | 122.4792 | 0.082397 | 0.28839 | 122.7264 | 123.0835 | 122.8912 | 122.9965 | 122.7356 | 123.0789 | 122.9095 | 122.4792 | 122.9965 | 122.7356 | 122.9095 | 122.8912 | 123.0789 | -0.54932 | -0.51727
4587.8438 | 123.0927 | -122.8683 | 0.21973 | 0.12291 | 0.01028 | -0.0088738 | 0.042379 | -0.021102 | -0.013399 | 0.0072803 | -0.027466 | 0.16937 | -0.3891 | 0.07782 | 0.086975 | 0.14191 | -0.17853 | 0.29297 | 0.26093 | -0.32044 | 122.4792 | -0.050354 | 122.8409 | 122.9462 | -0.13275 | 122.5479 | 0.041198 | 0.36163 | 122.6898 | 123.1613 | 122.9553 | 123.0377 | 122.8409 | 123.1293 | 123.0103 | 122.5479 | 123.0377 | 122.8409 | 123.0103 | 122.9553 | 123.1293 | -0.60883 | -0.54016
4589.5312 | 123.1842 | -122.8455 | 0.18768 | -0.16701 | 0.012416 | -0.0056696 | 0.039601 | -0.023665 | -0.011903 | 0.0064257 | -0.009155 | 0.16937 | -0.37537 | 0.11444 | 0.13733 | 0.16022 | -0.12817 | 0.3479 | 0.27008 | -0.34332 | 122.4701 | -0.01831 | 122.8363 | 122.9599 | -0.050354 | 122.5021 | 0.082398 | 0.36621 | 122.7173 | 123.1934 | 122.9828 | 123.0148 | 122.8363 | 123.1155 | 123.0057 | 122.5021 | 123.0148 | 122.8363 | 123.0057 | 122.9828 | 123.1155 | -0.56305 | -0.53101
4591.2188 | 123.1796 | -122.8409 | 0.20599 | -0.1899 | 0.01028 | -0.014642 | 0.039174 | -0.022383 | -0.010835 | 0.0064257 | -0.009155 | 0.16022 | -0.37537 | 0.10071 | 0.10986 | 0.13733 | -0.13733 | 0.3479 | 0.27008 | -0.32501 | 122.4655 | -0.045777 | 122.8317 | 122.9416 | -0.096131 | 122.5159 | 0.064087 | 0.36621 | 122.7036 | 123.1888 | 122.9507 | 123.0011 | 122.8317 | 123.111 | 122.9782 | 122.5159 | 123.0011 | 122.8317 | 122.9782 | 122.9507 | 123.111 | -0.58136 | -0.53101
4592.8906 | 123.0835 | -122.8683 | 0.2243 | 0.16869 | 0.0096387 | -0.0071648 | 0.044728 | -0.020247 | -0.01233 | 0.0055713 | -0.036621 | 0.15564 | -0.41199 | 0.086975 | 0.073242 | 0.11444 | -0.16937 | 0.29755 | 0.25177 | -0.32501 | 122.4564 | -0.068664 | 122.8317 | 122.9553 | -0.15106 | 122.5433 | 0.027466 | 0.37537 | 122.699 | 123.1659 | 122.9416 | 123.024 | 122.8317 | 123.1201 | 122.9828 | 122.5433 | 123.024 | 122.8317 | 122.9828 | 122.9416 | 123.1201 | -0.63629 | -0.54932
4594.5781 | 123.111 | -122.8729 | 0.2243 | 0.13817 | 0.0072889 | -0.018273 | 0.043447 | -0.019606 | -0.012117 | 0.0064257 | -0.027466 | 0.16479 | -0.39368 | 0.068665 | 0.091553 | 0.13733 | -0.1831 | 0.30212 | 0.24719 | -0.33875 | 122.4792 | -0.059509 | 122.8455 | 122.9416 | -0.13275 | 122.5342 | 0.022888 | 0.36621 | 122.6898 | 123.175 | 122.9645 | 123.0377 | 122.8455 | 123.1201 | 123.0103 | 122.5342 | 123.0377 | 122.8455 | 123.0103 | 122.9645 | 123.1201 | -0.61798 | -0.56305
4596.2656 | 123.1476 | -122.8638 | 0.20599 | 0.16106 | 0.0094251 | -0.011865 | 0.038533 | -0.020888 | -0.013185 | 0.0068531 | -0.032043 | 0.15106 | -0.39368 | 0.073242 | 0.064087 | 0.10071 | -0.15564 | 0.27466 | 0.26093 | -0.32044 | 122.4701 | -0.054932 | 122.8317 | 122.937 | -0.14191 | 122.5433 | 0.054931 | 0.36163 | 122.7081 | 123.1384 | 122.9279 | 123.0148 | 122.8317 | 123.1247 | 122.9645 | 122.5433 | 123.0148 | 122.8317 | 122.9645 | 122.9279 | 123.1247 | -0.59967 | -0.52643
4598 | 123.2254 | -122.8455 | 0.19226 | -0.20515 | 0.012843 | -0.014855 | 0.04366 | -0.022383 | -0.015748 | 0.0066393 | -0.10529 | 0.2243 | -0.43945 | 0.009155 | 0.004578 | 0.009155 | 0.036621 | 0.21973 | 0.3067 | -0.35706 | 122.406 | 0.032043 | 122.7402 | 122.8546 | -0.18768 | 122.4884 | 0.11444 | 0.33417 | 122.8821 | 123.0652 | 122.85 | 123.0698 | 122.7402 | 123.1522 | 122.8546 | 122.4884 | 123.0698 | 122.7402 | 122.8546 | 122.85 | 123.1522 | -0.63171 | -0.54932
4599.7344 | 123.1705 | -122.8729 | 0.19684 | -0.21278 | 0.01028 | -0.014855 | 0.04131 | -0.021102 | -0.0099805 | 0.0053577 | -0.013733 | 0.1831 | -0.37537 | 0.10071 | 0.11444 | 0.13733 | -0.1236 | 0.3479 | 0.27008 | -0.32959 | 122.4976 | -0.013733 | 122.8592 | 122.9736 | -0.082397 | 122.5433 | 0.073243 | 0.36163 | 122.7493 | 123.2208 | 122.9874 | 123.056 | 122.8592 | 123.143 | 123.0103 | 122.5433 | 123.056 | 122.8592 | 123.0103 | 122.9874 | 123.143 | -0.5722 | -0.52643
4601.4219 | 123.2437 | -122.8363 | 0.19684 | -0.28145 | 0.010921 | -0.010583 | 0.04366 | -0.020461 | -0.014253 | 0.0077075 | -0.10986 | 0.23346 | -0.43488 | -0.013733 | -0.009155 | -0.004578 | 0.064087 | 0.21515 | 0.31128 | -0.36621 | 122.4014 | 0.036621 | 122.7264 | 122.8226 | -0.20599 | 122.4701 | 0.11444 | 0.32501 | 122.9004 | 123.0515 | 122.8271 | 123.0698 | 122.7264 | 123.1476 | 122.8317 | 122.4701 | 123.0698 | 122.7264 | 122.8317 | 122.8271 | 123.1476 | -0.63171 | -0.56305
4603.125 | 123.23 | -122.818 | 0.19226 | 0.046615 | 0.010066 | -0.012719 | 0.039174 | -0.022383 | -0.01233 | 0.0066393 | -0.07782 | 0.1831 | -0.39368 | 0.022888 | 0.059509 | 0.09613 | -0.10529 | 0.2655 | 0.27008 | -0.34332 | 122.4243 | -0.009156 | 122.7402 | 122.8409 | -0.13275 | 122.4747 | 0.07782 | 0.31586 | 122.7127 | 123.0835 | 122.8775 | 123.0011 | 122.7402 | 123.0881 | 122.9141 | 122.4747 | 123.0011 | 122.7402 | 122.9141 | 122.8775 | 123.0881 | -0.58594 | -0.53558
4604.8125 | 123.1018 | -122.8821 | 0.21515 | 0.19157 | 0.010066 | -0.010156 | 0.043019 | -0.018752 | -0.015321 | 0.0057849 | -0.009155 | 0.16479 | -0.38452 | 0.073242 | 0.10071 | 0.13733 | -0.21973 | 0.3067 | 0.25635 | -0.31128 | 122.4976 | -0.050354 | 122.8729 | 122.9553 | -0.11444 | 122.5708 | 0.041199 | 0.37537 | 122.6624 | 123.1888 | 122.9828 | 123.0469 | 122.8729 | 123.1384 | 123.0194 | 122.5708 | 123.0469 | 122.8729 | 123.0194 | 122.9828 | 123.1384 | -0.59967 | -0.52643
4606.5 | 123.0789 | -122.8958 | 0.21973 | 0.1992 | 0.0083569 | -0.0073786 | 0.044942 | -0.019606 | -0.014039 | 0.0055713 | -0.013733 | 0.15564 | -0.3891 | 0.10071 | 0.09613 | 0.12817 | -0.21515 | 0.28839 | 0.25177 | -0.31586 | 122.5067 | -0.064087 | 122.8821 | 122.9965 | -0.1236 | 122.58 | 0.032043 | 0.37537 | 122.6807 | 123.1842 | 122.9919 | 123.0515 | 122.8821 | 123.1476 | 123.024 | 122.58 | 123.0515 | 122.8821 | 123.024 | 122.9919 | 123.1476 | -0.60883 | -0.53558
4608.2031 | 123.2025 | -122.8409 | 0.19684 | -0.18227 | 0.01028 | -0.013574 | 0.040456 | -0.021956 | -0.013612 | 0.0074939 | -0.032043 | 0.18768 | -0.37079 | 0.082397 | 0.10529 | 0.15106 | -0.11902 | 0.32959 | 0.26093 | -0.33417 | 122.4701 | -0.009155 | 122.8088 | 122.9233 | -0.091552 | 122.5067 | 0.064087 | 0.33875 | 122.7219 | 123.1705 | 122.9462 | 123.0286 | 122.8088 | 123.1018 | 122.9919 | 122.5067 | 123.0286 | 122.8088 | 122.9919 | 122.9462 | 123.1018 | -0.56763 | -0.531
4609.8906 | 123.175 | -122.8409 | 0.19684 | -0.18227 | 0.010707 | -0.015283 | 0.037892 | -0.021529 | -0.013826 | 0.0059985 | -0.004578 | 0.15564 | -0.37079 | 0.1236 | 0.13733 | 0.16022 | -0.17395 | 0.37079 | 0.27008 | -0.34332 | 122.4701 | -0.041198 | 122.8363 | 122.9645 | -0.059509 | 122.4976 | 0.073243 | 0.36621 | 122.6669 | 123.2117 | 122.9782 | 122.9965 | 122.8363 | 123.111 | 123.0011 | 122.4976 | 122.9965 | 122.8363 | 123.0011 | 122.9782 | 123.111 | -0.56763 | -0.54016
4611.6094 | 123.1934 | -122.8592 | 0.19684 | -0.1899 | 0.0089979 | -0.0075922 | 0.04131 | -0.022597 | -0.015962 | 0.0049303 | -0.018311 | 0.16479 | -0.37994 | 0.091553 | 0.1236 | 0.12817 | -0.1236 | 0.33875 | 0.24719 | -0.33417 | 122.4792 | -0.032043 | 122.8409 | 122.9507 | -0.073242 | 122.525 | 0.050354 | 0.36163 | 122.7356 | 123.1979 | 122.9828 | 123.024 | 122.8409 | 123.1064 | 122.9874 | 122.525 | 123.024 | 122.8409 | 122.9874 | 122.9828 | 123.1064 | -0.57678 | -0.531
4613.3438 | 123.1567 | -122.8821 | 0.18768 | 0.10765 | 0.010493 | -0.010796 | 0.044301 | -0.020247 | -0.014894 | 0.0040759 | -0.027466 | 0.16479 | -0.3891 | 0.059509 | 0.068665 | 0.10529 | -0.14191 | 0.27924 | 0.25635 | -0.32501 | 122.493 | -0.022888 | 122.8546 | 122.9416 | -0.11902 | 122.5571 | 0.068665 | 0.36163 | 122.7402 | 123.1613 | 122.9507 | 123.0469 | 122.8546 | 123.1384 | 122.9874 | 122.5571 | 123.0469 | 122.8546 | 122.9874 | 122.9507 | 123.1384 | -0.57678 | -0.5127
4615.0312 | 123.23 | -122.8317 | 0.20142 | -0.22041 | 0.0096387 | -0.0086602 | 0.04601 | -0.021743 | -0.01468 | 0.0068531 | -0.10986 | 0.21057 | -0.4303 | 0.013733 | 0 | -0.013733 | 0.032043 | 0.21515 | 0.29755 | -0.36163 | 122.4014 | 0.009155 | 122.7219 | 122.8455 | -0.20142 | 122.4701 | 0.09613 | 0.32044 | 122.8638 | 123.0469 | 122.8317 | 123.0423 | 122.7219 | 123.1293 | 122.818 | 122.4701 | 123.0423 | 122.7219 | 122.818 | 122.8317 | 123.1293 | -0.63171 | -0.56305
4616.75 | 123.1155 | -122.8775 | 0.22888 | -0.037308 | 0.010707 | -0.014855 | 0.045583 | -0.01747 | -0.015107 | 0.0077075 | -0.054932 | 0.20599 | -0.4303 | 0.013733 | 0.004578 | 0.027466 | -0.032043 | 0.19684 | 0.31128 | -0.36163 | 122.4472 | -0.022888 | 122.8226 | 122.8912 | -0.2243 | 122.5159 | 0.082397 | 0.37537 | 122.8455 | 123.0743 | 122.8821 | 123.0835 | 122.8226 | 123.1888 | 122.905 | 122.5159 | 123.0835 | 122.8226 | 122.905 | 122.8821 | 123.1888 | -0.65918 | -0.59052
4618.5 | 123.2254 | -122.8409 | 0.19684 | -0.28908 | 0.010493 | -0.0088738 | 0.040456 | -0.022597 | -0.011049 | 0.0055713 | -0.045776 | 0.16479 | -0.39368 | 0.054932 | 0.086975 | 0.082397 | -0.027466 | 0.29297 | 0.27924 | -0.35248 | 122.4472 | -0.032043 | 122.7951 | 122.8958 | -0.10986 | 122.4884 | 0.082398 | 0.3479 | 122.8134 | 123.1338 | 122.9279 | 123.0057 | 122.7951 | 123.1201 | 122.9233 | 122.4884 | 123.0057 | 122.7951 | 122.9233 | 122.9279 | 123.1201 | -0.59052 | -0.54932
4620.1875 | 123.2025 | -122.8546 | 0.20599 | -0.1899 | 0.0083569 | -0.010369 | 0.044942 | -0.016829 | -0.015107 | 0.0077075 | -0.10529 | 0.21057 | -0.41657 | 0.004578 | 0.004578 | 0.018311 | 0.027466 | 0.21973 | 0.30212 | -0.35248 | 122.438 | 0.004577 | 122.7493 | 122.8592 | -0.20142 | 122.5021 | 0.09613 | 0.31128 | 122.8821 | 123.0743 | 122.8592 | 123.0652 | 122.7493 | 123.1567 | 122.8729 | 122.5021 | 123.0652 | 122.7493 | 122.8729 | 122.8592 | 123.1567 | -0.62256 | -0.55847
4621.875 | 123.1934 | -122.8638 | 0.19226 | -0.16701 | 0.0072889 | -0.015283 | 0.039601 | -0.019179 | -0.014253 | 0.0045031 | -0.022888 | 0.17395 | -0.38452 | 0.086975 | 0.10986 | 0.1236 | -0.10071 | 0.32959 | 0.2655 | -0.33875 | 122.4792 | -0.018311 | 122.8409 | 122.9507 | -0.082398 | 122.525 | 0.073242 | 0.36163 | 122.7631 | 123.1934 | 122.9736 | 123.0377 | 122.8409 | 123.1293 | 122.9874 | 122.525 | 123.0377 | 122.8409 | 122.9874 | 122.9736 | 123.1293 | -0.57678 | -0.53101
4623.5625 | 123.1888 | -122.8638 | 0.20142 | -0.10597 | 0.011134 | -0.01336 | 0.038533 | -0.018111 | -0.011903 | 0.0074939 | 0 | 0.16479 | -0.39368 | 0.11902 | 0.13733 | 0.15564 | -0.16022 | 0.35706 | 0.27008 | -0.32501 | 122.4701 | -0.036621 | 122.8638 | 122.9828 | -0.064087 | 122.5388 | 0.068665 | 0.39368 | 122.7036 | 123.2208 | 123.0011 | 123.0286 | 122.8638 | 123.1339 | 123.0194 | 122.5388 | 123.0286 | 122.8638 | 123.0194 | 123.0011 | 123.1339 | -0.59509 | -0.52643
4625.25 | 123.2391 | -122.85 | 0.19226 | -0.2433 | 0.011561 | -0.014001 | 0.043019 | -0.021102 | -0.014253 | 0.0055713 | -0.068665 | 0.21973 | -0.40741 | 0.004578 | 0.022888 | 0.018311 | 0.013733 | 0.23346 | 0.3067 | -0.37079 | 122.4426 | 0.027466 | 122.7814 | 122.8546 | -0.16937 | 122.4792 | 0.11444 | 0.33874 | 122.8638 | 123.0835 | 122.8729 | 123.0698 | 122.7814 | 123.1567 | 122.8683 | 122.4792 | 123.0698 | 122.7814 | 122.8683 | 122.8729 | 123.1567 | -0.59967 | -0.56305
4626.9375 | 123.2071 | -122.8455 | 0.1831 | -0.090714 | 0.0089979 | -0.014214 | 0.040242 | -0.021102 | -0.01233 | 0.0059985 | -0.032043 | 0.17853 | -0.39825 | 0.10071 | 0.11902 | 0.12817 | -0.13275 | 0.33875 | 0.2655 | -0.32501 | 122.4472 | -0.004577 | 122.8134 | 122.9462 | -0.064086 | 122.5204 | 0.082398 | 0.36621 | 122.7127 | 123.1842 | 122.9645 | 123.024 | 122.8134 | 123.111 | 122.9736 | 122.5204 | 123.024 | 122.8134 | 122.9736 | 122.9645 | 123.111 | -0.58136 | -0.50812
4628.6406 | 123.1888 | -122.8363 | 0.19226 | -0.15938 | 0.0085705 | -0.011651 | 0.041951 | -0.020247 | -0.012971 | 0.0034351 | 0 | 0.16937 | -0.38452 | 0.10986 | 0.13275 | 0.14648 | -0.1236 | 0.36163 | 0.26093 | -0.32044 | 122.4518 | -0.022888 | 122.8363 | 122.9462 | -0.05951 | 122.5159 | 0.068664 | 0.38452 | 122.7127 | 123.1979 | 122.9691 | 123.0057 | 122.8363 | 123.0972 | 122.9828 | 122.5159 | 123.0057 | 122.8363 | 122.9828 | 122.9691 | 123.0972 | -0.57678 | -0.5127
4630.4375 | 123.1934 | -122.8363 | 0.18768 | 0.069504 | 0.010493 | -0.012505 | 0.041524 | -0.021102 | -0.013185 | 0.0062121 | -0.050354 | 0.16937 | -0.3891 | 0.054932 | 0.068665 | 0.10071 | -0.12817 | 0.27924 | 0.28381 | -0.32044 | 122.4472 | -0.01831 | 122.7859 | 122.8912 | -0.11902 | 122.5159 | 0.09613 | 0.33874 | 122.7081 | 123.1155 | 122.905 | 123.0057 | 122.7859 | 123.1201 | 122.937 | 122.5159 | 123.0057 | 122.7859 | 122.937 | 122.905 | 123.1201 | -0.57678 | -0.50812
4632.1406 | 123.0881 | -122.8958 | 0.21515 | 0.18394 | 0.0094251 | -0.0075922 | 0.045156 | -0.020461 | -0.012544 | 0.0049303 | 0 | 0.16937 | -0.38452 | 0.10529 | 0.09613 | 0.15106 | -0.21057 | 0.3067 | 0.25177 | -0.3067 | 122.5113 | -0.045776 | 122.8958 | 123.0011 | -0.11902 | 122.5891 | 0.036621 | 0.38452 | 122.6852 | 123.2025 | 122.9919 | 123.0652 | 122.8958 | 123.1476 | 123.0469 | 122.5891 | 123.0652 | 122.8958 | 123.0469 | 122.9919 | 123.1476 | -0.59967 | -0.52185
4633.8281 | 123.1705 | -122.8729 | 0.19684 | -0.20515 | 0.0081433 | -0.013574 | 0.040456 | -0.020888 | -0.012758 | 0.0066393 | -0.004578 | 0.17395 | -0.39368 | 0.10529 | 0.11902 | 0.1236 | -0.13733 | 0.34332 | 0.26093 | -0.33417 | 122.4792 | -0.022888 | 122.8683 | 122.9782 | -0.077819 | 122.5388 | 0.064087 | 0.3891 | 122.7356 | 123.2162 | 122.9919 | 123.0469 | 122.8683 | 123.1338 | 122.9965 | 122.5388 | 123.0469 | 122.8683 | 122.9965 | 122.9919 | 123.1338 | -0.59052 | -0.531
4635.5312 | 123.1018 | -122.9187 | 0.23804 | -0.098343 | 0.010493 | -0.013146 | 0.047506 | -0.017897 | -0.015748 | 0.0038623 | -0.050354 | 0.21057 | -0.41199 | 0.050354 | 0.032043 | 0.036621 | -0.032043 | 0.25635 | 0.31128 | -0.35248 | 122.5067 | -0.027466 | 122.8683 | 122.9691 | -0.20599 | 122.5662 | 0.073242 | 0.36163 | 122.8867 | 123.175 | 122.9507 | 123.1293 | 122.8683 | 123.23 | 122.9553 | 122.5662 | 123.1293 | 122.8683 | 122.9553 | 122.9507 | 123.23 | -0.65002 | -0.59052
4637.25 | 123.1979 | -122.8226 | 0.19684 | -0.19753 | 0.0092115 | -0.017205 | 0.043874 | -0.020034 | -0.014467 | 0.0045031 | -0.12817 | 0.21515 | -0.43945 | 0 | 0.022888 | 0.004578 | 0.022888 | 0.21057 | 0.32044 | -0.35248 | 122.3831 | 0.018311 | 122.6944 | 122.8226 | -0.17395 | 122.4701 | 0.1236 | 0.31128 | 122.8455 | 123.0331 | 122.8455 | 123.0377 | 122.6944 | 123.143 | 122.8271 | 122.4701 | 123.0377 | 122.6944 | 122.8271 | 122.8455 | 123.143 | -0.63629 | -0.54932
4639.0156 | 123.0789 | -122.8729 | 0.21515 | 0.16106 | 0.0066479 | -0.0086602 | 0.042592 | -0.018111 | -0.014253 | 0.0070667 | -0.009155 | 0.17395 | -0.39825 | 0.091553 | 0.10986 | 0.14648 | -0.20599 | 0.31128 | 0.25177 | -0.31128 | 122.4747 | -0.041199 | 122.8638 | 122.9645 | -0.10529 | 122.5616 | 0.036621 | 0.3891 | 122.6669 | 123.1842 | 122.9828 | 123.0469 | 122.8638 | 123.1247 | 123.0194 | 122.5616 | 123.0469 | 122.8638 | 123.0194 | 122.9828 | 123.1247 | -0.6134 | -0.52643
4640.7188 | 123.143 | -122.8821 | 0.20599 | 0.12291 | 0.011348 | -0.0090874 | 0.043447 | -0.018965 | -0.014894 | 0.0053577 | -0.11444 | 0.20142 | -0.44861 | -0.018311 | 0.009155 | 0.018311 | -0.036621 | 0.17395 | 0.30212 | -0.37079 | 122.4335 | -0.004578 | 122.7676 | 122.8638 | -0.19684 | 122.5113 | 0.09613 | 0.33417 | 122.8455 | 123.056 | 122.8912 | 123.0835 | 122.7676 | 123.1842 | 122.9004 | 122.5113 | 123.0835 | 122.7676 | 122.9004 | 122.8912 | 123.1842 | -0.6546 | -0.57678
4642.4375 | 123.1155 | -122.8638 | 0.21515 | 0.16106 | 0.010493 | -0.010796 | 0.044301 | -0.019179 | -0.014467 | 0.0051441 | -0.11902 | 0.20599 | -0.42572 | 0.009155 | 0.027466 | 0.041199 | -0.082397 | 0.18768 | 0.28839 | -0.33417 | 122.4381 | -0.009155 | 122.7448 | 122.8729 | -0.18768 | 122.5296 | 0.073242 | 0.3067 | 122.7814 | 123.0515 | 122.8912 | 123.0698 | 122.7448 | 123.1522 | 122.905 | 122.5296 | 123.0698 | 122.7448 | 122.905 | 122.8912 | 123.1522 | -0.64087 | -0.54932
4644.125 | 123.1018 | -122.8821 | 0.21515 | 0.1992 | 0.0089979 | -0.0088738 | 0.041524 | -0.019179 | -0.012544 | 0.0070667 | -0.018311 | 0.15106 | -0.3891 | 0.07782 | 0.11902 | 0.16022 | -0.20142 | 0.30212 | 0.27466 | -0.32959 | 122.493 | -0.064087 | 122.8638 | 122.9599 | -0.09613 | 122.5525 | 0.059509 | 0.37079 | 122.6807 | 123.1842 | 123.0011 | 123.0331 | 122.8638 | 123.1567 | 123.0423 | 122.5525 | 123.0331 | 122.8638 | 123.0423 | 123.0011 | 123.1567 | -0.60425 | -0.54474
4645.8594 | 123.1018 | -122.8821 | 0.21057 | -0.090714 | 0.0075025 | -0.018914 | 0.043874 | -0.018538 | -0.017244 | 0.0053577 | -0.059509 | 0.21057 | -0.42572 | 0.032043 | 0.045776 | 0.050354 | -0.027466 | 0.23804 | 0.29297 | -0.32959 | 122.4564 | 0 | 122.8226 | 122.9141 | -0.1648 | 122.5525 | 0.082398 | 0.36621 | 122.8546 | 123.1201 | 122.9279 | 123.0927 | 122.8226 | 123.175 | 122.9324 | 122.5525 | 123.0927 | 122.8226 | 122.9324 | 122.9279 | 123.175 | -0.63629 | -0.54016
4647.5469 | 123.2437 | -122.8317 | 0.17853 | -0.23567 | 0.01028 | -0.012078 | 0.04067 | -0.020034 | -0.01468 | 0.0070667 | -0.10529 | 0.20142 | -0.42114 | -0.018311 | 0.022888 | 0.009155 | 0.054932 | 0.21515 | 0.32044 | -0.36621 | 122.4106 | 0.022888 | 122.7264 | 122.8134 | -0.15564 | 122.4655 | 0.14191 | 0.31586 | 122.8867 | 123.0469 | 122.8546 | 123.0331 | 122.7264 | 123.1522 | 122.8409 | 122.4655 | 123.0331 | 122.7264 | 122.8409 | 122.8546 | 123.1522 | -0.59967 | -0.54474
4649.25 | 123.1659 | -122.8546 | 0.19684 | -0.1899 | 0.012416 | -0.014642 | 0.044515 | -0.018325 | -0.012971 | 0.0057849 | -0.068665 | 0.2243 | -0.41657 | 0.013733 | 0.045776 | 0.045776 | -0.004578 | 0.23804 | 0.3067 | -0.36621 | 122.438 | 0.027466 | 122.7859 | 122.8683 | -0.15106 | 122.4884 | 0.10986 | 0.3479 | 122.85 | 123.0927 | 122.9004 | 123.0789 | 122.7859 | 123.1613 | 122.9004 | 122.4884 | 123.0789 | 122.7859 | 122.9004 | 122.9004 | 123.1613 | -0.6134 | -0.56305
4650.9844 | 123.143 | -122.9004 | 0.19684 | 0.11528 | 0.0070751 | -0.0090874 | 0.045369 | -0.016616 | -0.015962 | 0.0070667 | -0.10529 | 0.19684 | -0.46234 | -0.045776 | -0.032043 | -0.013733 | 0.004578 | 0.16022 | 0.31128 | -0.3479 | 122.4381 | 0 | 122.7951 | 122.8546 | -0.22888 | 122.5525 | 0.11444 | 0.35706 | 122.905 | 123.0606 | 122.8683 | 123.0972 | 122.7951 | 123.2117 | 122.8867 | 122.5525 | 123.0972 | 122.7951 | 122.8867 | 122.8683 | 123.2117 | -0.65918 | -0.54474
4652.6719 | 123.2437 | -122.8409 | 0.17853 | -0.25856 | 0.0089979 | -0.01336 | 0.038533 | -0.020888 | -0.018312 | 0.0066393 | -0.14191 | 0.20599 | -0.42114 | -0.022888 | 0.009155 | 0.009155 | 0.054932 | 0.19684 | 0.29755 | -0.36163 | 122.4197 | 0.027466 | 122.699 | 122.818 | -0.16937 | 122.4792 | 0.11902 | 0.27924 | 122.8958 | 123.0377 | 122.85 | 123.0469 | 122.699 | 123.1384 | 122.85 | 122.4792 | 123.0469 | 122.699 | 122.85 | 122.85 | 123.1384 | -0.59967 | -0.54016
4654.3906 | 123.1293 | -122.8867 | 0.21973 | 0.10765 | 0.0079297 | -0.0095148 | 0.043447 | -0.020034 | -0.014039 | 0.0083483 | -0.11444 | 0.21973 | -0.48065 | -0.018311 | 0.004578 | 0.022888 | -0.054932 | 0.17853 | 0.31128 | -0.36163 | 122.406 | 0 | 122.7722 | 122.8683 | -0.21515 | 122.525 | 0.091552 | 0.36621 | 122.8317 | 123.0652 | 122.8912 | 123.1064 | 122.7722 | 123.1979 | 122.9095 | 122.525 | 123.1064 | 122.7722 | 122.9095 | 122.8912 | 123.1979 | -0.70038 | -0.58136
4656.0938 | 123.1659 | -122.8683 | 0.19684 | 0.084762 | 0.011134 | -0.0075922 | 0.038747 | -0.020034 | -0.012544 | 0.0077075 | -0.068665 | 0.16022 | -0.39368 | 0.032043 | 0.073242 | 0.10986 | -0.13733 | 0.27466 | 0.27466 | -0.33875 | 122.4747 | -0.036621 | 122.7997 | 122.9004 | -0.1236 | 122.5296 | 0.07782 | 0.32501 | 122.731 | 123.143 | 122.9416 | 123.0286 | 122.7997 | 123.143 | 122.9782 | 122.5296 | 123.0286 | 122.7997 | 122.9782 | 122.9416 | 123.143 | -0.59052 | -0.53558
4657.7812 | 123.0927 | -122.8729 | 0.20599 | 0.18394 | 0.011775 | -0.0088738 | 0.042379 | -0.019179 | -0.01169 | 0.0038623 | -0.032043 | 0.16937 | -0.3891 | 0.082397 | 0.10071 | 0.1236 | -0.16937 | 0.28839 | 0.25635 | -0.32959 | 122.4838 | -0.036621 | 122.8409 | 122.9553 | -0.10529 | 122.5433 | 0.050354 | 0.35706 | 122.7036 | 123.1613 | 122.9736 | 123.0423 | 122.8409 | 123.1293 | 122.9965 | 122.5433 | 123.0423 | 122.8409 | 122.9965 | 122.9736 | 123.1293 | -0.59509 | -0.53558
4659.4844 | 123.1018 | -122.9004 | 0.21057 | 0.21446 | 0.010707 | -0.012292 | 0.043019 | -0.020674 | -0.012971 | 0.0053577 | -0.082397 | 0.20599 | -0.40741 | 0.018311 | 0.054932 | 0.073242 | -0.11902 | 0.26093 | 0.2655 | -0.3479 | 122.493 | -0.004577 | 122.818 | 122.9187 | -0.15564 | 122.5525 | 0.054932 | 0.32501 | 122.7814 | 123.1613 | 122.9553 | 123.1064 | 122.818 | 123.1659 | 122.9736 | 122.5525 | 123.1064 | 122.818 | 122.9736 | 122.9553 | 123.1659 | -0.61798 | -0.55847
4661.1875 | 123.1888 | -122.8455 | 0.19684 | -0.1899 | 0.0068615 | -0.014001 | 0.039388 | -0.021315 | -0.012544 | 0.0068531 | -0.050354 | 0.17853 | -0.37079 | 0.09613 | 0.11444 | 0.13275 | -0.10986 | 0.33875 | 0.27466 | -0.32959 | 122.4747 | -0.01831 | 122.7951 | 122.9416 | -0.082397 | 122.5159 | 0.07782 | 0.32043 | 122.7356 | 123.1842 | 122.9599 | 123.024 | 122.7951 | 123.1201 | 122.9782 | 122.5159 | 123.024 | 122.7951 | 122.9782 | 122.9599 | 123.1201 | -0.56763 | -0.52643
4662.9375 | 123.111 | -122.8958 | 0.21057 | 0.19157 | 0.0098523 | -0.015923 | 0.044515 | -0.018752 | -0.013612 | 0.0072803 | -0.086975 | 0.19226 | -0.41657 | 0.013733 | 0.036621 | 0.041199 | -0.10529 | 0.21515 | 0.29297 | -0.32959 | 122.4792 | -0.01831 | 122.8088 | 122.9095 | -0.17395 | 122.5662 | 0.082398 | 0.32959 | 122.7905 | 123.111 | 122.9324 | 123.0881 | 122.8088 | 123.1888 | 122.937 | 122.5662 | 123.0881 | 122.8088 | 122.937 | 122.9324 | 123.1888 | -0.62714 | -0.54016
4664.625 | 123.1567 | -122.8683 | 0.21057 | 0.16106 | 0.0092115 | -0.015923 | 0.046651 | -0.018538 | -0.01468 | 0.0045031 | -0.1236 | 0.20142 | -0.44403 | -0.045776 | -0.004578 | 0.009155 | -0.027466 | 0.16937 | 0.30212 | -0.36621 | 122.4243 | -0.009155 | 122.7448 | 122.8226 | -0.21515 | 122.5021 | 0.091553 | 0.32044 | 122.8409 | 123.0377 | 122.8638 | 123.0698 | 122.7448 | 123.1705 | 122.8775 | 122.5021 | 123.0698 | 122.7448 | 122.8775 | 122.8638 | 123.1705 | -0.6546 | -0.57678
4666.3125 | 123.1934 | -122.8775 | 0.19226 | -0.17464 | 0.011775 | -0.010156 | 0.044728 | -0.019393 | -0.013826 | 0.0062121 | -0.10529 | 0.21057 | -0.42572 | 0.004578 | 0.041199 | 0.036621 | -0.004578 | 0.23804 | 0.30212 | -0.36163 | 122.4518 | 0.01831 | 122.7722 | 122.8821 | -0.15106 | 122.5159 | 0.10986 | 0.32043 | 122.8729 | 123.1155 | 122.9187 | 123.0881 | 122.7722 | 123.1796 | 122.9141 | 122.5159 | 123.0881 | 122.7722 | 122.9141 | 122.9187 | 123.1796 | -0.61798 | -0.55389
4668.0625 | 123.2117 | -122.8729 | 0.19226 | -0.15938 | 0.0072889 | -0.013787 | 0.04366 | -0.020247 | -0.013399 | 0.0045031 | -0.11902 | 0.24719 | -0.41657 | -0.013733 | 0.013733 | 0.004578 | 0.036621 | 0.21515 | 0.3067 | -0.34332 | 122.4564 | 0.054931 | 122.7539 | 122.8592 | -0.17853 | 122.5296 | 0.11444 | 0.29755 | 122.9095 | 123.0881 | 122.8867 | 123.1201 | 122.7539 | 123.1796 | 122.8775 | 122.5296 | 123.1201 | 122.7539 | 122.8775 | 122.8867 | 123.1796 | -0.60883 | -0.53558
4669.7656 | 123.0927 | -122.9004 | 0.2243 | -0.075455 | 0.0072889 | -0.011651 | 0.043447 | -0.017043 | -0.014253 | 0.0068531 | -0.041199 | 0.20599 | -0.42114 | 0.018311 | 0.032043 | 0.041199 | -0.041199 | 0.21515 | 0.29755 | -0.34332 | 122.4792 | -0.01831 | 122.8592 | 122.9187 | -0.19226 | 122.5571 | 0.073242 | 0.37994 | 122.8592 | 123.1155 | 122.9324 | 123.1064 | 122.8592 | 123.1979 | 122.9416 | 122.5571 | 123.1064 | 122.8592 | 122.9416 | 122.9324 | 123.1979 | -0.64545 | -0.56763
4671.4688 | 123.23 | -122.8271 | 0.1831 | -0.0067901 | 0.0096387 | -0.012505 | 0.037679 | -0.019393 | -0.012117 | 0.0059985 | -0.059509 | 0.18768 | -0.39825 | 0.032043 | 0.09613 | 0.10529 | -0.12817 | 0.3067 | 0.27924 | -0.34332 | 122.4289 | 0.004578 | 122.7676 | 122.8592 | -0.086975 | 122.4838 | 0.096131 | 0.33875 | 122.699 | 123.1338 | 122.9233 | 123.0148 | 122.7676 | 123.1064 | 122.9324 | 122.4838 | 123.0148 | 122.7676 | 122.9324 | 122.9233 | 123.1064 | -0.58136 | -0.52643
4673.1719 | 123.2117 | -122.8455 | 0.18768 | 0.061874 | 0.0087841 | -0.013574 | 0.040456 | -0.017897 | -0.012544 | 0.0079211 | -0.059509 | 0.1831 | -0.38452 | 0.045776 | 0.07782 | 0.086975 | -0.13275 | 0.27008 | 0.28381 | -0.33417 | 122.4609 | -0.004578 | 122.7859 | 122.8912 | -0.10986 | 122.5113 | 0.09613 | 0.32501 | 122.7127 | 123.1155 | 122.9233 | 123.0286 | 122.7859 | 123.1293 | 122.9324 | 122.5113 | 123.0286 | 122.7859 | 122.9324 | 122.9233 | 123.1293 | -0.5722 | -0.52185
4674.8594 | 123.1384 | -122.8912 | 0.19226 | 0.13817 | 0.0089979 | -0.010583 | 0.041524 | -0.021102 | -0.012971 | 0.0049303 | -0.018311 | 0.16479 | -0.37994 | 0.050354 | 0.07782 | 0.091553 | -0.14191 | 0.27008 | 0.2655 | -0.31128 | 122.5113 | -0.027466 | 122.8729 | 122.9416 | -0.11444 | 122.58 | 0.073242 | 0.36163 | 122.7493 | 123.1613 | 122.9691 | 123.056 | 122.8729 | 123.1567 | 122.9828 | 122.58 | 123.056 | 122.8729 | 122.9828 | 122.9691 | 123.1567 | -0.5722 | -0.50354
4676.5469 | 123.0972 | -122.8912 | 0.21515 | 0.13817 | 0.0079297 | -0.011865 | 0.042379 | -0.018965 | -0.013612 | 0.0066393 | -0.018311 | 0.14648 | -0.37537 | 0.082397 | 0.10986 | 0.1236 | -0.19226 | 0.28839 | 0.27466 | -0.33417 | 122.5159 | -0.068665 | 122.8729 | 122.9736 | -0.10529 | 122.5571 | 0.059509 | 0.35705 | 122.699 | 123.1796 | 123.0011 | 123.0377 | 122.8729 | 123.1659 | 123.0148 | 122.5571 | 123.0377 | 122.8729 | 123.0148 | 123.0011 | 123.1659 | -0.59052 | -0.54932
4678.25 | 123.111 | -122.8912 | 0.21515 | 0.21446 | 0.011989 | -0.0058832 | 0.044728 | -0.020034 | -0.012758 | 0.0066393 | -0.050354 | 0.20599 | -0.41657 | 0.045776 | 0.041199 | 0.086975 | -0.13733 | 0.25635 | 0.28839 | -0.32959 | 122.4747 | -0.009155 | 122.8409 | 122.937 | -0.17395 | 122.5616 | 0.073242 | 0.36621 | 122.7539 | 123.1476 | 122.9324 | 123.0972 | 122.8409 | 123.1796 | 122.9782 | 122.5616 | 123.0972 | 122.8409 | 122.9782 | 122.9324 | 123.1796 | -0.63171 | -0.54474
4680.0156 | 123.1064 | -122.8775 | 0.20599 | 0.18394 | 0.0098523 | -0.0095148 | 0.044088 | -0.020034 | -0.013826 | 0.0070667 | -0.07782 | 0.20599 | -0.41657 | 0.036621 | 0.045776 | 0.07782 | -0.14191 | 0.25177 | 0.27924 | -0.35248 | 122.4609 | 0 | 122.7997 | 122.9141 | -0.16022 | 122.525 | 0.073242 | 0.33875 | 122.7356 | 123.1293 | 122.9233 | 123.0835 | 122.7997 | 123.1567 | 122.9553 | 122.525 | 123.0835 | 122.7997 | 122.9553 | 122.9233 | 123.1567 | -0.62256 | -0.55847
4681.7031 | 123.143 | -122.8867 | 0.21515 | 0.084762 | 0.0089979 | -0.010156 | 0.046651 | -0.020247 | -0.014467 | 0.0066393 | -0.09613 | 0.20142 | -0.42114 | -0.036621 | -0.013733 | -0.004578 | 0.009155 | 0.16937 | 0.31586 | -0.35248 | 122.4655 | -0.013733 | 122.7905 | 122.85 | -0.22888 | 122.5342 | 0.10071 | 0.32501 | 122.8958 | 123.056 | 122.8729 | 123.0881 | 122.7905 | 123.2025 | 122.8821 | 122.5342 | 123.0881 | 122.7905 | 122.8821 | 122.8729 | 123.2025 | -0.63629 | -0.56763
4683.4219 | 123.1293 | -122.8638 | 0.21515 | 0.12291 | 0.0085705 | -0.01336 | 0.039601 | -0.020461 | -0.011476 | 0.0079211 | -0.013733 | 0.1831 | -0.37079 | 0.064087 | 0.10529 | 0.11902 | -0.1831 | 0.28381 | 0.2655 | -0.34332 | 122.493 | -0.032044 | 122.85 | 122.9279 | -0.10986 | 122.5204 | 0.050354 | 0.35706 | 122.6807 | 123.1476 | 122.9691 | 123.0469 | 122.85 | 123.1293 | 122.9828 | 122.5204 | 123.0469 | 122.85 | 122.9828 | 122.9691 | 123.1293 | -0.58594 | -0.55847
4685.125 | 123.143 | -122.8867 | 0.21057 | 0.084762 | 0.010493 | -0.013574 | 0.046224 | -0.019606 | -0.01468 | 0.0064257 | -0.12817 | 0.2243 | -0.44861 | -0.009155 | -0.004578 | -0.004578 | -0.022888 | 0.14191 | 0.32044 | -0.35706 | 122.4381 | 0.013733 | 122.7585 | 122.8775 | -0.21515 | 122.5296 | 0.10986 | 0.32043 | 122.8638 | 123.0286 | 122.8821 | 123.111 | 122.7585 | 123.2071 | 122.8821 | 122.5296 | 123.111 | 122.7585 | 122.8821 | 122.8821 | 123.2071 | -0.65918 | -0.56763
4686.8125 | 123.0972 | -122.8867 | 0.21515 | -0.090714 | 0.011134 | -0.011651 | 0.04366 | -0.020888 | -0.014039 | 0.0057849 | -0.059509 | 0.19226 | -0.42114 | 0.018311 | 0.027466 | 0.054932 | -0.032043 | 0.24261 | 0.30212 | -0.33875 | 122.4655 | -0.022888 | 122.8271 | 122.905 | -0.18768 | 122.5479 | 0.086975 | 0.36163 | 122.8546 | 123.1293 | 122.9141 | 123.0789 | 122.8271 | 123.1888 | 122.9416 | 122.5479 | 123.0789 | 122.8271 | 122.9416 | 122.9141 | 123.1888 | -0.63629 | -0.55389
4688.5156 | 123.143 | -122.8409 | 0.21515 | -0.16701 | 0.011989 | -0.015283 | 0.044088 | -0.020888 | -0.015535 | 0.0062121 | -0.07782 | 0.20599 | -0.40283 | 0.022888 | 0.045776 | 0.050354 | -0.027466 | 0.23804 | 0.31586 | -0.35248 | 122.438 | -0.009155 | 122.7631 | 122.8638 | -0.16937 | 122.4884 | 0.10071 | 0.32501 | 122.8134 | 123.0789 | 122.8867 | 123.0469 | 122.7631 | 123.1567 | 122.8912 | 122.4884 | 123.0469 | 122.7631 | 122.8912 | 122.8867 | 123.1567 | -0.61798 | -0.56763
4690.2031 | 123.2529 | -122.8638 | 0.18768 | -0.23567 | 0.01028 | -0.014855 | 0.038747 | -0.02217 | -0.014467 | 0.0057849 | -0.09613 | 0.21057 | -0.40283 | -0.009155 | 0.022888 | 0.018311 | 0.032043 | 0.21515 | 0.29755 | -0.36621 | 122.4609 | 0.022888 | 122.7676 | 122.8546 | -0.16479 | 122.4976 | 0.10986 | 0.3067 | 122.8958 | 123.0789 | 122.8867 | 123.0743 | 122.7676 | 123.1613 | 122.8821 | 122.4976 | 123.0743 | 122.7676 | 122.8821 | 122.8867 | 123.1613 | -0.59052 | -0.55389
4691.875 | 123.1338 | -122.8867 | 0.21515 | 0.1458 | 0.010066 | -0.013787 | 0.043874 | -0.018752 | -0.01468 | 0.0059985 | -0.10071 | 0.20599 | -0.41199 | -0.027466 | -0.018311 | 0 | -0.027466 | 0.17395 | 0.31128 | -0.38452 | 122.4747 | -0.009155 | 122.7859 | 122.8592 | -0.23346 | 122.5021 | 0.09613 | 0.31128 | 122.8592 | 123.0606 | 122.8683 | 123.0927 | 122.7859 | 123.1979 | 122.8867 | 122.5021 | 123.0927 | 122.7859 | 122.8867 | 122.8683 | 123.1979 | -0.62714 | -0.59967
4693.5625 | 123.1979 | -122.8683 | 0.19684 | -0.20515 | 0.0089979 | -0.016564 | 0.043874 | -0.019606 | -0.014467 | 0.0066393 | -0.10529 | 0.23804 | -0.41199 | -0.004578 | 0.013733 | 0.027466 | 0.009155 | 0.21973 | 0.31128 | -0.37079 | 122.4564 | 0.041199 | 122.7631 | 122.8638 | -0.18311 | 122.4976 | 0.11444 | 0.3067 | 122.8775 | 123.0881 | 122.8821 | 123.1064 | 122.7631 | 123.1796 | 122.8958 | 122.4976 | 123.1064 | 122.7631 | 122.8958 | 122.8821 | 123.1796 | -0.60882 | -0.56763
4695.25 | 123.1476 | -122.8546 | 0.20599 | -0.15938 | 0.012629 | -0.016778 | 0.042592 | -0.018325 | -0.015107 | 0.0062121 | -0.064087 | 0.2243 | -0.40741 | 0.022888 | 0.036621 | 0.059509 | -0.009155 | 0.23804 | 0.3067 | -0.3479 | 122.4472 | 0.01831 | 122.7905 | 122.8775 | -0.16937 | 122.5067 | 0.10071 | 0.34332 | 122.8455 | 123.0927 | 122.8912 | 123.0789 | 122.7905 | 123.1613 | 122.9141 | 122.5067 | 123.0789 | 122.7905 | 122.9141 | 122.8912 | 123.1613 | -0.6134 | -0.55389
4696.9844 | 123.1064 | -122.9004 | 0.21515 | -0.10597 | 0.0098523 | -0.011865 | 0.044088 | -0.017684 | -0.014467 | 0.0074939 | -0.032043 | 0.21057 | -0.42572 | 0.018311 | 0.036621 | 0.050354 | -0.022888 | 0.24261 | 0.29297 | -0.36163 | 122.4747 | -0.004578 | 122.8683 | 122.9187 | -0.17853 | 122.5388 | 0.07782 | 0.39368 | 122.8775 | 123.143 | 122.937 | 123.111 | 122.8683 | 123.1934 | 122.9507 | 122.5388 | 123.111 | 122.8683 | 122.9507 | 122.937 | 123.1934 | -0.64087 | -0.57678
4698.6719 | 123.0972 | -122.8821 | 0.20599 | -0.1136 | 0.0094251 | -0.010369 | 0.042592 | -0.019393 | -0.01468 | 0.0051441 | -0.050354 | 0.21973 | -0.42572 | 0.022888 | 0.045776 | 0.054932 | -0.032043 | 0.23804 | 0.3067 | -0.35706 | 122.4564 | 0.013733 | 122.8317 | 122.905 | -0.16022 | 122.525 | 0.10071 | 0.37537 | 122.85 | 123.1201 | 122.9279 | 123.1018 | 122.8317 | 123.1888 | 122.937 | 122.525 | 123.1018 | 122.8317 | 122.937 | 122.9279 | 123.1888 | -0.63171 | -0.56305
4700.3594 | 123.2346 | -122.8638 | 0.20599 | -0.25856 | 0.0087841 | -0.011224 | 0.039174 | -0.020888 | -0.01468 | 0.0072803 | -0.13275 | 0.23346 | -0.41657 | -0.032043 | 0.009155 | 0.009155 | 0.050354 | 0.21057 | 0.32044 | -0.37079 | 122.4472 | 0.027465 | 122.731 | 122.8317 | -0.19684 | 122.493 | 0.11444 | 0.28381 | 122.9141 | 123.0743 | 122.8729 | 123.0972 | 122.731 | 123.1842 | 122.8729 | 122.493 | 123.0972 | 122.731 | 122.8729 | 122.8729 | 123.1842 | -0.62256 | -0.57678
4702.0625 | 123.1888 | -122.85 | 0.17853 | -0.075455 | 0.0092115 | -0.0063104 | 0.033834 | -0.018752 | -0.012758 | 0.0049303 | -0.050354 | 0.21057 | -0.37537 | 0.059509 | 0.1236 | 0.13733 | -0.13733 | 0.32044 | 0.27466 | -0.33875 | 122.4747 | 0.032043 | 122.7997 | 122.9095 | -0.054932 | 122.5113 | 0.09613 | 0.32501 | 122.7127 | 123.1705 | 122.9736 | 123.0606 | 122.7997 | 123.1247 | 122.9874 | 122.5113 | 123.0606 | 122.7997 | 122.9874 | 122.9736 | 123.1247 | -0.55389 | -0.51727
4703.75 | 123.111 | -122.8729 | 0.20599 | 0.13817 | 0.0066479 | -0.011224 | 0.042165 | -0.020674 | -0.01169 | 0.0062121 | 0 | 0.16937 | -0.37994 | 0.064087 | 0.10529 | 0.12817 | -0.16937 | 0.28839 | 0.25177 | -0.32501 | 122.493 | -0.036621 | 122.8729 | 122.937 | -0.10071 | 122.5479 | 0.045776 | 0.37994 | 122.7036 | 123.1613 | 122.9782 | 123.0423 | 122.8729 | 123.1247 | 123.0011 | 122.5479 | 123.0423 | 122.8729 | 123.0011 | 122.9782 | 123.1247 | -0.58594 | -0.53101
4705.4531 | 123.1293 | -122.8821 | 0.20142 | 0.13817 | 0.0089979 | -0.0046014 | 0.047506 | -0.018965 | -0.014467 | 0.0059985 | -0.086975 | 0.22888 | -0.42114 | -0.009155 | 0.009155 | 0.036621 | -0.086975 | 0.18768 | 0.3067 | -0.36163 | 122.4609 | 0.027466 | 122.7951 | 122.8729 | -0.19226 | 122.5204 | 0.10529 | 0.33417 | 122.7951 | 123.0698 | 122.8912 | 123.111 | 122.7951 | 123.1888 | 122.9187 | 122.5204 | 123.111 | 122.7951 | 122.9187 | 122.8912 | 123.1888 | -0.62256 | -0.56305
4707.1406 | 123.1476 | -122.8912 | 0.21515 | 0.023727 | 0.011134 | -0.0093012 | 0.045583 | -0.019393 | -0.015748 | 0.0066393 | -0.11902 | 0.2243 | -0.41657 | -0.050354 | -0.027466 | 0.004578 | 0 | 0.15564 | 0.29755 | -0.36621 | 122.4747 | 0.009155 | 122.7722 | 122.8409 | -0.24261 | 122.525 | 0.082397 | 0.29755 | 122.8912 | 123.0469 | 122.8638 | 123.1155 | 122.7722 | 123.1888 | 122.8958 | 122.525 | 123.1155 | 122.7722 | 122.8958 | 122.8638 | 123.1888 | -0.63171 | -0.58136
4708.8594 | 123.1247 | -122.8729 | 0.19684 | 0.15343 | 0.0079297 | -0.014001 | 0.044942 | -0.020034 | -0.01468 | 0.0070667 | -0.10986 | 0.20142 | -0.40741 | -0.009155 | 0.018311 | 0.036621 | -0.10071 | 0.20142 | 0.28381 | -0.34332 | 122.4655 | 0.004578 | 122.7631 | 122.8638 | -0.17853 | 122.5296 | 0.086975 | 0.29755 | 122.7722 | 123.0743 | 122.8912 | 123.0743 | 122.7631 | 123.1567 | 122.9095 | 122.5296 | 123.0743 | 122.7631 | 122.9095 | 122.8912 | 123.1567 | -0.60425 | -0.54016
4710.5469 | 123.0972 | -122.8821 | 0.20599 | -0.1136 | 0.010493 | -0.0080194 | 0.04366 | -0.022811 | -0.013826 | 0.0062121 | -0.032043 | 0.20142 | -0.41657 | 0.027466 | 0.032043 | 0.054932 | -0.027466 | 0.23346 | 0.3067 | -0.3479 | 122.4655 | -0.004578 | 122.85 | 122.9095 | -0.17395 | 122.5342 | 0.10071 | 0.38452 | 122.8546 | 123.1155 | 122.9141 | 123.0835 | 122.85 | 123.1888 | 122.937 | 122.5342 | 123.0835 | 122.85 | 122.937 | 122.9141 | 123.1888 | -0.62256 | -0.55389
4712.25 | 123.1842 | -122.8683 | 0.20599 | -0.15175 | 0.0089979 | -0.013574 | 0.041097 | -0.018752 | -0.013185 | 0.0042895 | -0.068665 | 0.21515 | -0.41657 | 0 | 0.054932 | 0.050354 | -0.018311 | 0.24261 | 0.3067 | -0.35248 | 122.4518 | 0.009155 | 122.7997 | 122.8683 | -0.15106 | 122.5159 | 0.10071 | 0.3479 | 122.85 | 123.111 | 122.9233 | 123.0835 | 122.7997 | 123.175 | 122.9187 | 122.5159 | 123.0835 | 122.7997 | 122.9187 | 122.9233 | 123.175 | -0.62256 | -0.55847
4713.9375 | 123.2483 | -122.8592 | 0.19226 | -0.26619 | 0.0075025 | -0.01101 | 0.039815 | -0.021102 | -0.012758 | 0.0051441 | -0.10986 | 0.26093 | -0.41657 | -0.032043 | 0.018311 | -0.004578 | 0.059509 | 0.20599 | 0.32044 | -0.37079 | 122.4426 | 0.068664 | 122.7493 | 122.8271 | -0.17395 | 122.4884 | 0.12817 | 0.3067 | 122.9187 | 123.0652 | 122.8775 | 123.1201 | 122.7493 | 123.1796 | 122.8546 | 122.4884 | 123.1201 | 122.7493 | 122.8546 | 122.8775 | 123.1796 | -0.60883 | -0.56305
4715.625 | 123.2071 | -122.8271 | 0.19684 | -0.12886 | 0.010066 | -0.016564 | 0.036824 | -0.020247 | -0.01233 | 0.0059985 | -0.032043 | 0.19226 | -0.36163 | 0.091553 | 0.11902 | 0.1236 | -0.16479 | 0.3479 | 0.27008 | -0.33417 | 122.4655 | -0.004577 | 122.7951 | 122.9187 | -0.077819 | 122.493 | 0.073243 | 0.32959 | 122.6624 | 123.175 | 122.9462 | 123.0194 | 122.7951 | 123.0972 | 122.9507 | 122.493 | 123.0194 | 122.7951 | 122.9507 | 122.9462 | 123.0972 | -0.55847 | -0.531
4717.3125 | 123.1384 | -122.8546 | 0.20142 | 0.16106 | 0.0092115 | -0.011437 | 0.041524 | -0.020888 | -0.011903 | 0.0079211 | -0.022888 | 0.1831 | -0.3891 | 0.036621 | 0.082397 | 0.086975 | -0.16022 | 0.27466 | 0.27008 | -0.31128 | 122.4655 | -0.018311 | 122.8317 | 122.8912 | -0.11902 | 122.5433 | 0.068665 | 0.36621 | 122.6944 | 123.1293 | 122.937 | 123.0377 | 122.8317 | 123.1247 | 122.9416 | 122.5433 | 123.0377 | 122.8317 | 122.9416 | 122.937 | 123.1247 | -0.59052 | -0.5127
4719.0312 | 123.0972 | -122.8867 | 0.22888 | 0.16869 | 0.0089979 | -0.013787 | 0.043019 | -0.018325 | -0.015321 | 0.0038623 | -0.036621 | 0.19684 | -0.39825 | 0.073242 | 0.091553 | 0.12817 | -0.17853 | 0.28839 | 0.25635 | -0.3067 | 122.4884 | -0.032044 | 122.85 | 122.9599 | -0.13733 | 122.58 | 0.027466 | 0.36163 | 122.7081 | 123.175 | 122.9782 | 123.0835 | 122.85 | 123.143 | 123.0148 | 122.58 | 123.0835 | 122.85 | 123.0148 | 122.9782 | 123.143 | -0.62714 | -0.53558
4720.7188 | 123.143 | -122.8821 | 0.21515 | -0.01442 | 0.010921 | -0.006524 | 0.046224 | -0.021529 | -0.013612 | 0.0070667 | -0.068665 | 0.23346 | -0.40741 | 0.009155 | 0.018311 | 0.018311 | -0.013733 | 0.19684 | 0.30212 | -0.36163 | 122.4747 | 0.01831 | 122.8134 | 122.8912 | -0.19684 | 122.5204 | 0.086975 | 0.33874 | 122.8683 | 123.0789 | 122.9004 | 123.1155 | 122.8134 | 123.1842 | 122.9004 | 122.5204 | 123.1155 | 122.8134 | 122.9004 | 122.9004 | 123.1842 | -0.62256 | -0.57678
4722.4062 | 123.1247 | -122.8821 | 0.21057 | -0.13649 | 0.010066 | -0.011437 | 0.044301 | -0.020674 | -0.012758 | 0.0049303 | -0.054932 | 0.22888 | -0.40741 | 0.027466 | 0.045776 | 0.041199 | -0.032043 | 0.23804 | 0.3067 | -0.3479 | 122.4747 | 0.018311 | 122.8271 | 122.9095 | -0.1648 | 122.5342 | 0.096131 | 0.35248 | 122.85 | 123.1201 | 122.9279 | 123.111 | 122.8271 | 123.1888 | 122.9233 | 122.5342 | 123.111 | 122.8271 | 122.9233 | 122.9279 | 123.1888 | -0.61798 | -0.55847
4724.1094 | 123.2254 | -122.8409 | 0.18768 | -0.26619 | 0.0094251 | -0.01101 | 0.043447 | -0.018965 | -0.015107 | 0.0057849 | -0.10529 | 0.25177 | -0.41657 | -0.018311 | 0.009155 | -0.018311 | 0.036621 | 0.20599 | 0.30212 | -0.37079 | 122.4243 | 0.064087 | 122.7356 | 122.8226 | -0.17853 | 122.4701 | 0.11444 | 0.31128 | 122.8775 | 123.0469 | 122.85 | 123.0927 | 122.7356 | 123.143 | 122.8226 | 122.4701 | 123.0927 | 122.7356 | 122.8226 | 122.85 | 123.143 | -0.60425 | -0.55847
4725.7969 | 123.1338 | -122.8821 | 0.20599 | -0.13649 | 0.0085705 | -0.015069 | 0.043447 | -0.01982 | -0.012544 | 0.0057849 | -0.054932 | 0.2243 | -0.41657 | 0.027466 | 0.041199 | 0.050354 | -0.022888 | 0.22888 | 0.31128 | -0.35248 | 122.4655 | 0.01831 | 122.8271 | 122.9095 | -0.1648 | 122.5296 | 0.10528 | 0.36163 | 122.8592 | 123.111 | 122.9233 | 123.1064 | 122.8271 | 123.1934 | 122.9324 | 122.5296 | 123.1064 | 122.8271 | 122.9324 | 122.9233 | 123.1934 | -0.62256 | -0.55847
4727.5 | 123.2071 | -122.8592 | 0.21057 | -0.23567 | 0.0087841 | -0.012078 | 0.038747 | -0.021743 | -0.01169 | 0.0034351 | -0.022888 | 0.19684 | -0.38452 | 0.054932 | 0.073242 | 0.082397 | -0.059509 | 0.3067 | 0.30212 | -0.3479 | 122.4747 | -0.013733 | 122.8363 | 122.9141 | -0.13733 | 122.5113 | 0.091553 | 0.36163 | 122.7997 | 123.1659 | 122.9324 | 123.056 | 122.8363 | 123.1613 | 122.9416 | 122.5113 | 123.056 | 122.8363 | 122.9416 | 122.9324 | 123.1613 | -0.59509 | -0.55847
4729.1875 | 123.0789 | -122.9095 | 0.22888 | 0.16106 | 0.011348 | -0.0075922 | 0.04366 | -0.01982 | -0.013612 | 0.0062121 | 0.009155 | 0.19684 | -0.37994 | 0.073242 | 0.09613 | 0.14191 | -0.1831 | 0.29297 | 0.26093 | -0.32044 | 122.5296 | -0.032044 | 122.9187 | 122.9828 | -0.13275 | 122.5891 | 0.032043 | 0.3891 | 122.7264 | 123.2025 | 123.0057 | 123.1064 | 122.9187 | 123.1705 | 123.0515 | 122.5891 | 123.1064 | 122.9187 | 123.0515 | 123.0057 | 123.1705 | -0.60883 | -0.54932
4730.8906 | 123.1064 | -122.9095 | 0.20599 | 0.13817 | 0.0094251 | -0.012933 | 0.041097 | -0.020674 | -0.014039 | 0.0049303 | 0.009155 | 0.16937 | -0.37537 | 0.068665 | 0.09613 | 0.11902 | -0.1831 | 0.3067 | 0.24719 | -0.32959 | 122.5342 | -0.036621 | 122.9187 | 122.9782 | -0.10986 | 122.58 | 0.041198 | 0.38452 | 122.7264 | 123.2162 | 123.0057 | 123.0789 | 122.9187 | 123.1567 | 123.0286 | 122.58 | 123.0789 | 122.9187 | 123.0286 | 123.0057 | 123.1567 | -0.58136 | -0.53558
4732.5781 | 123.1064 | -122.8912 | 0.21057 | 0.16106 | 0.010066 | -0.0071648 | 0.045583 | -0.018538 | -0.013185 | 0.0040759 | -0.054932 | 0.21057 | -0.40283 | 0.068665 | 0.07782 | 0.10529 | -0.15106 | 0.27924 | 0.28381 | -0.32501 | 122.4884 | 0 | 122.8363 | 122.9599 | -0.13275 | 122.5662 | 0.073242 | 0.3479 | 122.7402 | 123.1705 | 122.9691 | 123.1018 | 122.8363 | 123.175 | 122.9965 | 122.5662 | 123.1018 | 122.8363 | 122.9965 | 122.9691 | 123.175 | -0.6134 | -0.53558
4734.2812 | 123.1476 | -122.8683 | 0.20142 | 0.17632 | 0.011775 | -0.012292 | 0.039815 | -0.018538 | -0.012117 | 0.0064257 | -0.036621 | 0.18768 | -0.37537 | 0.045776 | 0.073242 | 0.10071 | -0.15106 | 0.27466 | 0.25635 | -0.32501 | 122.493 | -0.013733 | 122.8317 | 122.9141 | -0.12817 | 122.5433 | 0.054932 | 0.33874 | 122.7173 | 123.143 | 122.9416 | 123.056 | 122.8317 | 123.1247 | 122.9691 | 122.5433 | 123.056 | 122.8317 | 122.9691 | 122.9416 | 123.1247 | -0.57678 | -0.52643
4736.0156 | 123.1888 | -122.8683 | 0.20142 | -0.15175 | 0.0089979 | -0.014428 | 0.040242 | -0.023024 | -0.010194 | 0.0049303 | 0.004578 | 0.21057 | -0.36621 | 0.10529 | 0.13733 | 0.14191 | -0.16479 | 0.35706 | 0.2655 | -0.31586 | 122.5021 | 0.009155 | 122.8729 | 122.9736 | -0.064087 | 122.5525 | 0.064087 | 0.37079 | 122.7036 | 123.2254 | 123.0057 | 123.0789 | 122.8729 | 123.1338 | 123.0103 | 122.5525 | 123.0789 | 122.8729 | 123.0103 | 123.0057 | 123.1338 | -0.56763 | -0.51727
4737.7031 | 123.2391 | -122.85 | 0.18768 | 0.023727 | 0.0051525 | -0.010156 | 0.039601 | -0.021956 | -0.012117 | 0.0049303 | -0.059509 | 0.20599 | -0.36163 | 0.041199 | 0.064087 | 0.082397 | -0.13733 | 0.27008 | 0.27008 | -0.33875 | 122.4884 | 0.018311 | 122.7905 | 122.8912 | -0.1236 | 122.5113 | 0.082398 | 0.30212 | 122.7127 | 123.1201 | 122.9141 | 123.056 | 122.7905 | 123.1201 | 122.9324 | 122.5113 | 123.056 | 122.7905 | 122.9324 | 122.9141 | 123.1201 | -0.54932 | -0.52643
4739.4062 | 123.1705 | -122.8729 | 0.21515 | 0.13054 | 0.0089979 | -0.010369 | 0.047292 | -0.021102 | -0.012758 | 0.0053577 | -0.091553 | 0.23804 | -0.42114 | -0.027466 | -0.009155 | 0 | -0.032043 | 0.15564 | 0.31586 | -0.35706 | 122.4518 | 0.022888 | 122.7814 | 122.8455 | -0.2243 | 122.5159 | 0.10071 | 0.32959 | 122.8409 | 123.0286 | 122.8638 | 123.111 | 122.7814 | 123.1888 | 122.8729 | 122.5159 | 123.111 | 122.7814 | 122.8729 | 122.8638 | 123.1888 | -0.63629 | -0.5722
4741.1094 | 123.1247 | -122.9187 | 0.21973 | -0.052567 | 0.010921 | -0.012505 | 0.04601 | -0.021315 | -0.015748 | 0.0047167 | -0.041199 | 0.2243 | -0.40741 | 0.027466 | 0.045776 | 0.050354 | -0.041199 | 0.22888 | 0.30212 | -0.33875 | 122.5113 | 0.004577 | 122.8775 | 122.9462 | -0.17395 | 122.58 | 0.082397 | 0.36621 | 122.8775 | 123.1476 | 122.9645 | 123.143 | 122.8775 | 123.2208 | 122.9691 | 122.58 | 123.143 | 122.8775 | 122.9691 | 122.9645 | 123.2208 | -0.62714 | -0.55847
4742.7969 | 123.2254 | -122.8271 | 0.20599 | -0.28145 | 0.0075025 | -0.0093012 | 0.040242 | -0.021529 | -0.013826 | 0.0064257 | -0.054932 | 0.21057 | -0.41199 | 0.027466 | 0.054932 | 0.064087 | -0.013733 | 0.25635 | 0.30212 | -0.35706 | 122.4152 | 0.004577 | 122.7722 | 122.8546 | -0.15106 | 122.4701 | 0.09613 | 0.35706 | 122.8134 | 123.0835 | 122.8821 | 123.0377 | 122.7722 | 123.1293 | 122.8912 | 122.4701 | 123.0377 | 122.7722 | 122.8912 | 122.8821 | 123.1293 | -0.61798 | -0.56305
4744.5 | 123.2208 | -122.8363 | 0.17853 | -0.21278 | 0.0066479 | -0.01571 | 0.039174 | -0.021529 | -0.013826 | 0.0040759 | -0.032043 | 0.19684 | -0.36621 | 0.064087 | 0.086975 | 0.091553 | -0.045776 | 0.31128 | 0.28839 | -0.3479 | 122.4701 | 0.01831 | 122.8043 | 122.9004 | -0.091553 | 122.4884 | 0.10986 | 0.33417 | 122.7905 | 123.1476 | 122.9233 | 123.0331 | 122.8043 | 123.1247 | 122.9279 | 122.4884 | 123.0331 | 122.8043 | 122.9279 | 122.9233 | 123.1247 | -0.54474 | -0.52643
4746.2031 | 123.2071 | -122.8546 | 0.21515 | -0.1899 | 0.0077161 | -0.01336 | 0.045156 | -0.020674 | -0.014253 | 0.0072803 | -0.09613 | 0.2243 | -0.41199 | 0.013733 | 0.036621 | 0.009155 | 0.013733 | 0.21515 | 0.31128 | -0.35706 | 122.4426 | 0.009155 | 122.7585 | 122.8683 | -0.17853 | 122.4976 | 0.09613 | 0.31586 | 122.8683 | 123.0698 | 122.8912 | 123.0789 | 122.7585 | 123.1659 | 122.8638 | 122.4976 | 123.0789 | 122.7585 | 122.8638 | 122.8912 | 123.1659 | -0.62714 | -0.5722
4747.9375 | 123.2483 | -122.85 | 0.16479 | -0.18227 | 0.0096387 | -0.013574 | 0.043233 | -0.020888 | -0.012971 | 0.0045031 | -0.10529 | 0.23346 | -0.42572 | -0.013733 | 0.018311 | 0.009155 | 0.050354 | 0.21973 | 0.3067 | -0.37537 | 122.4243 | 0.068664 | 122.7448 | 122.8363 | -0.14648 | 122.4747 | 0.14191 | 0.32043 | 122.9004 | 123.0698 | 122.8683 | 123.0835 | 122.7448 | 123.1567 | 122.8592 | 122.4747 | 123.0835 | 122.7448 | 122.8592 | 122.8683 | 123.1567 | -0.59052 | -0.54016
4749.625 | 123.1979 | -122.8729 | 0.19684 | -0.1899 | 0.0096387 | -0.013787 | 0.04067 | -0.021315 | -0.011903 | 0.0049303 | 0.004578 | 0.19226 | -0.37994 | 0.07782 | 0.10529 | 0.1236 | -0.13275 | 0.32959 | 0.27008 | -0.33875 | 122.493 | -0.004577 | 122.8775 | 122.9507 | -0.091552 | 122.5342 | 0.073243 | 0.38452 | 122.7402 | 123.2025 | 122.9782 | 123.0652 | 122.8775 | 123.143 | 122.9965 | 122.5342 | 123.0652 | 122.8775 | 122.9965 | 122.9782 | 123.143 | -0.57678 | -0.53558
4751.3125 | 123.1888 | -122.8409 | 0.17853 | -0.14412 | 0.0087841 | -0.014642 | 0.038106 | -0.018752 | -0.011262 | 0.0042895 | 0.018311 | 0.19226 | -0.37537 | 0.13275 | 0.13275 | 0.15564 | -0.16022 | 0.36163 | 0.27466 | -0.33417 | 122.4655 | 0.013733 | 122.8592 | 122.9736 | -0.045777 | 122.5067 | 0.09613 | 0.39368 | 122.6807 | 123.2025 | 122.9736 | 123.0331 | 122.8592 | 123.1155 | 122.9965 | 122.5067 | 123.0331 | 122.8592 | 122.9965 | 122.9736 | 123.1155 | -0.55389 | -0.5127
4753 | 123.0972 | -122.9004 | 0.21515 | 0.13054 | 0.0083569 | -0.012719 | 0.044728 | -0.018965 | -0.01169 | 0.0066393 | 0 | 0.1831 | -0.39368 | 0.086975 | 0.10071 | 0.13275 | -0.20599 | 0.29297 | 0.2655 | -0.31586 | 122.5067 | -0.032044 | 122.9004 | 122.9874 | -0.11444 | 122.5845 | 0.050354 | 0.39368 | 122.6944 | 123.1934 | 123.0011 | 123.0835 | 122.9004 | 123.1659 | 123.0331 | 122.5845 | 123.0835 | 122.9004 | 123.0331 | 123.0011 | 123.1659 | -0.60883 | -0.53101
4754.6875 | 123.0881 | -122.8775 | 0.21057 | 0.15343 | 0.010066 | -0.011224 | 0.044301 | -0.01982 | -0.013399 | 0.0045031 | -0.013733 | 0.17853 | -0.39825 | 0.091553 | 0.10529 | 0.14191 | -0.19226 | 0.30212 | 0.25635 | -0.32501 | 122.4792 | -0.032043 | 122.8638 | 122.9691 | -0.10529 | 122.5525 | 0.045777 | 0.38452 | 122.6852 | 123.1796 | 122.9828 | 123.056 | 122.8638 | 123.1339 | 123.0194 | 122.5525 | 123.056 | 122.8638 | 123.0194 | 122.9828 | 123.1339 | -0.60882 | -0.53558
4756.4062 | 123.1201 | -122.8821 | 0.22888 | -0.029679 | 0.012843 | -0.011224 | 0.045156 | -0.020461 | -0.015107 | 0.0064257 | -0.059509 | 0.21515 | -0.40741 | 0.009155 | 0.004578 | 0.018311 | -0.013733 | 0.19684 | 0.30212 | -0.37079 | 122.4747 | -0.013733 | 122.8226 | 122.8912 | -0.2243 | 122.5113 | 0.073242 | 0.3479 | 122.8683 | 123.0789 | 122.8867 | 123.0972 | 122.8226 | 123.1842 | 122.9004 | 122.5113 | 123.0972 | 122.8226 | 122.9004 | 122.8867 | 123.1842 | -0.63629 | -0.59967
4758.0938 | 123.1018 | -122.8958 | 0.21057 | -0.090714 | 0.0085705 | -0.012292 | 0.044728 | -0.020034 | -0.014039 | 0.0057849 | -0.050354 | 0.2243 | -0.39825 | 0.036621 | 0.036621 | 0.054932 | -0.027466 | 0.24261 | 0.3067 | -0.36163 | 122.4976 | 0.013733 | 122.8455 | 122.9324 | -0.17395 | 122.5342 | 0.096131 | 0.3479 | 122.8683 | 123.1384 | 122.9324 | 123.1201 | 122.8455 | 123.2025 | 122.9507 | 122.5342 | 123.1201 | 122.8455 | 122.9507 | 122.9324 | 123.2025 | -0.60882 | -0.5722
4759.7812 | 123.2346 | -122.8363 | 0.17853 | -0.25093 | 0.0089979 | -0.011865 | 0.040242 | -0.020674 | -0.013185 | 0.0042895 | -0.09613 | 0.21057 | -0.39825 | -0.013733 | 0.022888 | 0.036621 | 0.013733 | 0.23346 | 0.31128 | -0.36163 | 122.4381 | 0.032043 | 122.7402 | 122.8226 | -0.15564 | 122.4747 | 0.13275 | 0.30212 | 122.85 | 123.0698 | 122.8592 | 123.0469 | 122.7402 | 123.1476 | 122.8729 | 122.4747 | 123.0469 | 122.7402 | 122.8729 | 122.8592 | 123.1476 | -0.57678 | -0.54016
4761.4844 | 123.2162 | -122.8683 | 0.19226 | -0.28908 | 0.0079297 | -0.016351 | 0.039388 | -0.020247 | -0.012758 | 0.0042895 | -0.050354 | 0.19684 | -0.3891 | 0.022888 | 0.054932 | 0.064087 | 0 | 0.25177 | 0.3067 | -0.34332 | 122.4792 | 0.004577 | 122.818 | 122.8912 | -0.13733 | 122.525 | 0.11444 | 0.33874 | 122.8683 | 123.1201 | 122.9233 | 123.0652 | 122.818 | 123.175 | 122.9324 | 122.525 | 123.0652 | 122.818 | 122.9324 | 122.9233 | 123.175 | -0.58136 | -0.53558
4763.1719 | 123.1705 | -122.85 | 0.21057 | -0.1899 | 0.010493 | -0.01336 | 0.038106 | -0.022383 | -0.010835 | 0.0045031 | 0.009155 | 0.17853 | -0.37079 | 0.086975 | 0.13275 | 0.14191 | -0.13733 | 0.35706 | 0.26093 | -0.33417 | 122.4792 | -0.032043 | 122.8592 | 122.937 | -0.07782 | 122.5159 | 0.050354 | 0.37994 | 122.7127 | 123.2071 | 122.9828 | 123.0286 | 122.8592 | 123.111 | 122.9919 | 122.5159 | 123.0286 | 122.8592 | 122.9919 | 122.9828 | 123.111 | -0.58136 | -0.54474
4764.8594 | 123.0972 | -122.9004 | 0.19226 | 0.21446 | 0.011348 | -0.010369 | 0.046437 | -0.01982 | -0.013826 | 0.0047167 | -0.004578 | 0.19684 | -0.3891 | 0.07782 | 0.091553 | 0.11902 | -0.17395 | 0.28381 | 0.28839 | -0.32501 | 122.5113 | 0.004577 | 122.8958 | 122.9782 | -0.10071 | 122.5754 | 0.09613 | 0.38452 | 122.7264 | 123.1842 | 122.9919 | 123.0972 | 122.8958 | 123.1888 | 123.0194 | 122.5754 | 123.0972 | 122.8958 | 123.0194 | 122.9919 | 123.1888 | -0.58136 | -0.51727
4766.5625 | 123.1842 | -122.8455 | 0.20599 | -0.1136 | 0.0092115 | -0.015283 | 0.03832 | -0.020888 | -0.012117 | 0.0072803 | -0.004578 | 0.19684 | -0.37994 | 0.10071 | 0.14648 | 0.13733 | -0.15564 | 0.35248 | 0.27008 | -0.31586 | 122.4655 | -0.009156 | 122.8409 | 122.9462 | -0.05951 | 122.5296 | 0.064087 | 0.37537 | 122.6898 | 123.1979 | 122.9919 | 123.0423 | 122.8409 | 123.1155 | 122.9828 | 122.5296 | 123.0423 | 122.8409 | 122.9828 | 122.9919 | 123.1155 | -0.58594 | -0.52185
4768.25 | 123.2162 | -122.8546 | 0.17395 | 0.00083945 | 0.0094251 | -0.012078 | 0.037892 | -0.021956 | -0.012758 | 0.0047167 | -0.073242 | 0.19226 | -0.39825 | 0.045776 | 0.082397 | 0.09613 | -0.10986 | 0.27466 | 0.29297 | -0.34332 | 122.4564 | 0.018311 | 122.7814 | 122.9004 | -0.091553 | 122.5113 | 0.11902 | 0.32501 | 122.7448 | 123.1293 | 122.937 | 123.0469 | 122.7814 | 123.1476 | 122.9507 | 122.5113 | 123.0469 | 122.7814 | 122.9507 | 122.937 | 123.1476 | -0.5722 | -0.51727
4769.9531 | 123.0972 | -122.8912 | 0.23346 | -0.098343 | 0.0087841 | -0.010796 | 0.049642 | -0.019393 | -0.016603 | 0.0047167 | -0.032043 | 0.2243 | -0.41199 | 0.050354 | 0.041199 | 0.050354 | -0.050354 | 0.23804 | 0.30212 | -0.36621 | 122.4792 | -0.009155 | 122.8592 | 122.9416 | -0.19226 | 122.525 | 0.068665 | 0.37994 | 122.8409 | 123.1293 | 122.9324 | 123.1155 | 122.8592 | 123.1934 | 122.9416 | 122.525 | 123.1155 | 122.8592 | 122.9416 | 122.9324 | 123.1934 | -0.64545 | -0.59967
4771.6719 | 123.1247 | -122.8912 | 0.21057 | 0.12291 | 0.012202 | -0.015923 | 0.043447 | -0.018325 | -0.01233 | 0.0055713 | -0.086975 | 0.23346 | -0.42572 | -0.009155 | 0.004578 | 0.022888 | -0.073242 | 0.17853 | 0.3067 | -0.37537 | 122.4655 | 0.022888 | 122.8043 | 122.8821 | -0.20599 | 122.5159 | 0.096131 | 0.33874 | 122.818 | 123.0698 | 122.8958 | 123.1247 | 122.8043 | 123.1979 | 122.9141 | 122.5159 | 123.1247 | 122.8043 | 122.9141 | 122.8958 | 123.1979 | -0.63629 | -0.58594
4773.375 | 123.0789 | -122.8958 | 0.20142 | 0.19157 | 0.010707 | -0.012505 | 0.043874 | -0.018965 | -0.012971 | 0.0068531 | 0.018311 | 0.19226 | -0.37079 | 0.082397 | 0.10986 | 0.12817 | -0.21057 | 0.30212 | 0.24719 | -0.32501 | 122.525 | -0.009155 | 122.9141 | 122.9782 | -0.091553 | 122.5708 | 0.045776 | 0.3891 | 122.6852 | 123.1979 | 123.0057 | 123.0881 | 122.9141 | 123.143 | 123.024 | 122.5708 | 123.0881 | 122.9141 | 123.024 | 123.0057 | 123.143 | -0.5722 | -0.52643
4775.0938 | 123.1018 | -122.9141 | 0.19684 | 0.22972 | 0.0098523 | -0.011651 | 0.043447 | -0.01982 | -0.010621 | 0.0045031 | -0.045776 | 0.21973 | -0.40283 | 0.059509 | 0.068665 | 0.09613 | -0.15564 | 0.2655 | 0.27466 | -0.32959 | 122.5113 | 0.022889 | 122.8683 | 122.9736 | -0.12817 | 122.5845 | 0.07782 | 0.35706 | 122.7585 | 123.1796 | 122.9828 | 123.1339 | 122.8683 | 123.1888 | 123.0103 | 122.5845 | 123.1339 | 122.8683 | 123.0103 | 122.9828 | 123.1888 | -0.59967 | -0.52643
4776.7812 | 123.0881 | -122.9141 | 0.21973 | 0.19157 | 0.0098523 | -0.016564 | 0.041738 | -0.020247 | -0.012971 | 0.0051441 | -0.018311 | 0.20599 | -0.39368 | 0.059509 | 0.091553 | 0.11902 | -0.16937 | 0.27008 | 0.27008 | -0.31128 | 122.5204 | -0.013733 | 122.8958 | 122.9736 | -0.12817 | 122.6028 | 0.050354 | 0.37537 | 122.7448 | 123.1842 | 123.0057 | 123.1201 | 122.8958 | 123.1842 | 123.0331 | 122.6028 | 123.1201 | 122.8958 | 123.0331 | 123.0057 | 123.1842 | -0.6134 | -0.53101
4778.5312 | 123.1934 | -122.8638 | 0.19684 | 0.16106 | 0.010921 | -0.0075922 | 0.040242 | -0.021102 | -0.010835 | 0.0079211 | -0.059509 | 0.18768 | -0.3891 | 0.041199 | 0.082397 | 0.09613 | -0.12817 | 0.27008 | 0.27466 | -0.32044 | 122.4747 | -0.009155 | 122.8043 | 122.905 | -0.11444 | 122.5433 | 0.07782 | 0.32959 | 122.7356 | 123.1339 | 122.9462 | 123.0515 | 122.8043 | 123.1384 | 122.9599 | 122.5433 | 123.0515 | 122.8043 | 122.9599 | 122.9462 | 123.1384 | -0.58594 | -0.51727
4780.2188 | 123.0927 | -122.9187 | 0.21515 | 0.17632 | 0.010707 | -0.0052422 | 0.044515 | -0.01982 | -0.011262 | 0.0059985 | 0.004578 | 0.19684 | -0.39368 | 0.073242 | 0.11444 | 0.14648 | -0.20599 | 0.32044 | 0.25177 | -0.32501 | 122.525 | -0.018311 | 122.9233 | 122.9919 | -0.10071 | 122.5937 | 0.036621 | 0.39826 | 122.7127 | 123.2391 | 123.0331 | 123.1155 | 122.9233 | 123.1705 | 123.0652 | 122.5937 | 123.1155 | 122.9233 | 123.0652 | 123.0331 | 123.1705 | -0.60883 | -0.54016
4781.9688 | 123.1796 | -122.85 | 0.20599 | -0.19753 | 0.0087841 | -0.010796 | 0.044942 | -0.020461 | -0.013826 | 0.0066393 | -0.082397 | 0.23804 | -0.40741 | 0.018311 | 0.032043 | 0.041199 | -0.013733 | 0.26093 | 0.29755 | -0.36621 | 122.4426 | 0.032043 | 122.7676 | 122.8683 | -0.17395 | 122.4838 | 0.091552 | 0.32501 | 122.8363 | 123.111 | 122.8821 | 123.0881 | 122.7676 | 123.1476 | 122.8912 | 122.4838 | 123.0881 | 122.7676 | 122.8912 | 122.8821 | 123.1476 | -0.6134 | -0.57221
4783.7031 | 123.1064 | -122.9141 | 0.21057 | 0.22209 | 0.0064343 | -0.0086602 | 0.041738 | -0.021315 | -0.012544 | 0.0059985 | -0.004578 | 0.19684 | -0.37079 | 0.091553 | 0.10529 | 0.14648 | -0.20599 | 0.32044 | 0.2655 | -0.32501 | 122.5433 | -0.013733 | 122.9095 | 123.0057 | -0.10529 | 122.5891 | 0.054932 | 0.36621 | 122.7081 | 123.2346 | 123.0194 | 123.111 | 122.9095 | 123.1796 | 123.0606 | 122.5891 | 123.111 | 122.9095 | 123.0606 | 123.0194 | 123.1796 | -0.58136 | -0.53558
4785.3906 | 123.1476 | -122.8592 | 0.19684 | 0.11528 | 0.010493 | -0.0078058 | 0.046865 | -0.01982 | -0.014039 | 0.0042895 | -0.082397 | 0.23346 | -0.41657 | -0.004578 | 0 | 0.013733 | -0.041199 | 0.1831 | 0.29755 | -0.36163 | 122.4426 | 0.036621 | 122.7768 | 122.8546 | -0.19684 | 122.4976 | 0.10071 | 0.33417 | 122.818 | 123.0423 | 122.8592 | 123.0927 | 122.7768 | 123.1567 | 122.8729 | 122.4976 | 123.0927 | 122.7768 | 122.8729 | 122.8592 | 123.1567 | -0.6134 | -0.55847
4787.1094 | 123.1476 | -122.8455 | 0.21515 | 0.1458 | 0.0094251 | -0.012292 | 0.044088 | -0.01747 | -0.013399 | 0.0062121 | -0.1236 | 0.22888 | -0.42572 | -0.022888 | -0.004578 | 0 | -0.013733 | 0.16022 | 0.3067 | -0.35248 | 122.4197 | 0.013733 | 122.7219 | 122.8226 | -0.21973 | 122.493 | 0.091553 | 0.30212 | 122.8317 | 123.0057 | 122.8409 | 123.0743 | 122.7219 | 123.1522 | 122.8455 | 122.493 | 123.0743 | 122.7219 | 122.8455 | 122.8409 | 123.1522 | -0.64087 | -0.56763
4788.7969 | 123.1567 | -122.8912 | 0.21057 | 0.077133 | 0.010707 | -0.0080194 | 0.044515 | -0.018752 | -0.013826 | 0.0072803 | -0.1236 | 0.2243 | -0.42114 | -0.041199 | -0.013733 | -0.009155 | 0.004578 | 0.16479 | 0.31128 | -0.36621 | 122.4701 | 0.013733 | 122.7676 | 122.85 | -0.2243 | 122.525 | 0.10071 | 0.29755 | 122.8958 | 123.056 | 122.8775 | 123.1155 | 122.7676 | 123.2025 | 122.8821 | 122.525 | 123.1155 | 122.7676 | 122.8821 | 122.8775 | 123.2025 | -0.63171 | -0.57678
4790.5 | 123.1888 | -122.85 | 0.19684 | -0.17464 | 0.0092115 | -0.016564 | 0.039174 | -0.021529 | -0.013826 | 0.0036487 | -0.013733 | 0.18768 | -0.36621 | 0.073242 | 0.10986 | 0.13275 | -0.1236 | 0.33417 | 0.28381 | -0.3479 | 122.4838 | -0.009155 | 122.8363 | 122.9233 | -0.086975 | 122.5021 | 0.086975 | 0.35248 | 122.7264 | 123.1842 | 122.9599 | 123.0377 | 122.8363 | 123.1338 | 122.9828 | 122.5021 | 123.0377 | 122.8363 | 122.9828 | 122.9599 | 123.1338 | -0.56305 | -0.54474
4792.2031 | 123.1613 | -122.8867 | 0.2243 | 0.13054 | 0.013057 | -0.010369 | 0.045583 | -0.01982 | -0.011049 | 0.0066393 | -0.10071 | 0.21973 | -0.41657 | -0.027466 | 0.009155 | -0.013733 | -0.018311 | 0.15106 | 0.32044 | -0.36163 | 122.4701 | -0.004577 | 122.7859 | 122.8592 | -0.21515 | 122.525 | 0.096131 | 0.31586 | 122.8683 | 123.0377 | 122.8958 | 123.1064 | 122.7859 | 123.2071 | 122.8729 | 122.525 | 123.1064 | 122.7859 | 122.8729 | 122.8958 | 123.2071 | -0.64087 | -0.58594
4793.9375 | 123.2529 | -122.85 | 0.19226 | -0.25093 | 0.010493 | -0.012505 | 0.040456 | -0.021315 | -0.012117 | 0.0049303 | -0.10071 | 0.24261 | -0.42572 | -0.032043 | -0.004578 | 0 | 0.054932 | 0.19684 | 0.31586 | -0.37537 | 122.4243 | 0.050354 | 122.7493 | 122.818 | -0.19684 | 122.4747 | 0.1236 | 0.32501 | 122.905 | 123.0469 | 122.8455 | 123.0927 | 122.7493 | 123.1659 | 122.85 | 122.4747 | 123.0927 | 122.7493 | 122.85 | 122.8455 | 123.1659 | -0.61798 | -0.56763
4795.625 | 123.23 | -122.85 | 0.18768 | -0.27382 | 0.0094251 | -0.019982 | 0.041738 | -0.020888 | -0.014253 | 0.0049303 | -0.10986 | 0.24261 | -0.43945 | -0.018311 | 0.004578 | -0.009155 | 0.050354 | 0.20599 | 0.32044 | -0.37079 | 122.4106 | 0.054932 | 122.7402 | 122.8317 | -0.1831 | 122.4792 | 0.13275 | 0.32959 | 122.9004 | 123.056 | 122.8546 | 123.0927 | 122.7402 | 123.1705 | 122.8409 | 122.4792 | 123.0927 | 122.7402 | 122.8409 | 122.8546 | 123.1705 | -0.62714 | -0.55847
4797.3438 | 123.2025 | -122.8546 | 0.18768 | -0.1899 | 0.0089979 | -0.011437 | 0.041097 | -0.020888 | -0.014253 | 0.0055713 | -0.018311 | 0.19684 | -0.37537 | 0.064087 | 0.10071 | 0.10071 | -0.059509 | 0.32044 | 0.28381 | -0.3479 | 122.4792 | 0.009155 | 122.8363 | 122.9187 | -0.086975 | 122.5067 | 0.09613 | 0.35705 | 122.7951 | 123.175 | 122.9553 | 123.0515 | 122.8363 | 123.1384 | 122.9553 | 122.5067 | 123.0515 | 122.8363 | 122.9553 | 122.9553 | 123.1384 | -0.56305 | -0.53558
4799.0312 | 123.2254 | -122.8271 | 0.19226 | 0.023727 | 0.011134 | -0.015496 | 0.040029 | -0.021102 | -0.01233 | 0.0053577 | -0.045776 | 0.20599 | -0.3891 | 0.041199 | 0.07782 | 0.10071 | -0.1236 | 0.27008 | 0.29755 | -0.3479 | 122.438 | 0.013733 | 122.7814 | 122.8683 | -0.11444 | 122.4792 | 0.10528 | 0.34332 | 122.7036 | 123.0972 | 122.905 | 123.0331 | 122.7814 | 123.1247 | 122.9279 | 122.4792 | 123.0331 | 122.7814 | 122.9279 | 122.905 | 123.1247 | -0.58136 | -0.54016
4800.7188 | 123.1796 | -122.8775 | 0.19226 | 0.10765 | 0.0096387 | -0.012719 | 0.039815 | -0.019606 | -0.012117 | 0.0049303 | -0.045776 | 0.18768 | -0.38452 | 0.045776 | 0.068665 | 0.091553 | -0.12817 | 0.27008 | 0.27924 | -0.33417 | 122.493 | -0.004578 | 122.8317 | 122.9233 | -0.1236 | 122.5433 | 0.086975 | 0.33875 | 122.7493 | 123.1476 | 122.9462 | 123.0652 | 122.8317 | 123.1567 | 122.9691 | 122.5433 | 123.0652 | 122.8317 | 122.9691 | 122.9462 | 123.1567 | -0.57678 | -0.52643
4802.4062 | 123.1888 | -122.8592 | 0.17395 | -0.10597 | 0.0083569 | -0.012078 | 0.040883 | -0.021529 | -0.011476 | 0.0055713 | 0.022888 | 0.1831 | -0.36163 | 0.11444 | 0.12817 | 0.16937 | -0.17853 | 0.37994 | 0.27924 | -0.32044 | 122.4976 | 0.009155 | 122.8821 | 122.9736 | -0.045776 | 122.5388 | 0.10529 | 0.38452 | 122.6807 | 123.2391 | 122.9874 | 123.0423 | 122.8821 | 123.1384 | 123.0286 | 122.5388 | 123.0423 | 122.8821 | 123.0286 | 122.9874 | 123.1384 | -0.53558 | -0.49439
4804.125 | 123.1384 | -122.8546 | 0.21515 | 0.16106 | 0.0094251 | -0.010369 | 0.048787 | -0.019393 | -0.015535 | 0.0059985 | -0.086975 | 0.22888 | -0.40283 | -0.018311 | -0.027466 | -0.018311 | -0.032043 | 0.16022 | 0.3067 | -0.36621 | 122.4518 | 0.013733 | 122.7676 | 122.8363 | -0.24261 | 122.4884 | 0.091553 | 0.31586 | 122.8226 | 123.0148 | 122.8271 | 123.0835 | 122.7676 | 123.1613 | 122.8363 | 122.4884 | 123.0835 | 122.7676 | 122.8363 | 122.8271 | 123.1613 | -0.61798 | -0.58136
4805.8125 | 123.1384 | -122.8729 | 0.21973 | 0.084762 | 0.0072889 | -0.0078058 | 0.047292 | -0.018325 | -0.013826 | 0.0051441 | -0.10986 | 0.2243 | -0.42572 | -0.032043 | -0.013733 | -0.022888 | 0.009155 | 0.15106 | 0.30212 | -0.37537 | 122.4472 | 0.004577 | 122.7631 | 122.8409 | -0.23346 | 122.4976 | 0.082397 | 0.31586 | 122.8821 | 123.024 | 122.8592 | 123.0972 | 122.7631 | 123.175 | 122.85 | 122.4976 | 123.0972 | 122.7631 | 122.85 | 122.8592 | 123.175 | -0.64545 | -0.59509
4807.5469 | 123.1796 | -122.85 | 0.19226 | -0.15175 | 0.010707 | -0.014428 | 0.036397 | -0.021529 | -0.012758 | 0.0068531 | 0.004578 | 0.19684 | -0.36621 | 0.11444 | 0.13733 | 0.15106 | -0.15106 | 0.35706 | 0.27008 | -0.32044 | 122.4838 | 0.004577 | 122.8546 | 122.9645 | -0.054932 | 122.5296 | 0.07782 | 0.37079 | 122.699 | 123.2071 | 122.9874 | 123.0469 | 122.8546 | 123.1201 | 123.0011 | 122.5296 | 123.0469 | 122.8546 | 123.0011 | 122.9874 | 123.1201 | -0.55847 | -0.5127
4809.2344 | 123.1979 | -122.8638 | 0.17853 | -0.029679 | 0.0057935 | -0.014428 | 0.038106 | -0.02217 | -0.012117 | 0.0077075 | -0.045776 | 0.19684 | -0.37994 | 0.064087 | 0.10986 | 0.11444 | -0.11444 | 0.31586 | 0.27466 | -0.32044 | 122.4838 | 0.01831 | 122.818 | 122.9279 | -0.068665 | 122.5433 | 0.09613 | 0.33417 | 122.7493 | 123.1796 | 122.9736 | 123.0606 | 122.818 | 123.1384 | 122.9782 | 122.5433 | 123.0606 | 122.818 | 122.9782 | 122.9736 | 123.1384 | -0.55847 | -0.49896
4810.9688 | 123.1888 | -122.8592 | 0.19226 | -0.12123 | 0.0075025 | -0.011437 | 0.041738 | -0.023879 | -0.010194 | 0.0045031 | 0.018311 | 0.18768 | -0.37537 | 0.10529 | 0.13275 | 0.14191 | -0.14191 | 0.3479 | 0.27008 | -0.32044 | 122.4838 | -0.004578 | 122.8775 | 122.9645 | -0.05951 | 122.5388 | 0.07782 | 0.39368 | 122.7173 | 123.2071 | 122.9919 | 123.0469 | 122.8775 | 123.1293 | 123.0011 | 122.5388 | 123.0469 | 122.8775 | 123.0011 | 122.9919 | 123.1293 | -0.56763 | -0.5127
4812.6562 | 123.1888 | -122.8729 | 0.20599 | -0.1899 | 0.0085705 | -0.013787 | 0.04067 | -0.021956 | -0.010835 | 0.0062121 | 0.013733 | 0.17853 | -0.36163 | 0.091553 | 0.11444 | 0.1236 | -0.11444 | 0.3479 | 0.27008 | -0.32959 | 122.5113 | -0.027466 | 122.8867 | 122.9645 | -0.091553 | 122.5433 | 0.064087 | 0.37537 | 122.7585 | 123.2208 | 122.9874 | 123.0515 | 122.8867 | 123.143 | 122.9965 | 122.5433 | 123.0515 | 122.8867 | 122.9965 | 122.9874 | 123.143 | -0.56763 | -0.53558
4814.3438 | 123.2391 | -122.8546 | 0.18768 | -0.22041 | 0.0098523 | -0.016351 | 0.044728 | -0.020461 | -0.01468 | 0.0053577 | -0.050354 | 0.2243 | -0.39825 | 0.009155 | 0.045776 | 0.013733 | 0.009155 | 0.23804 | 0.31586 | -0.36621 | 122.4564 | 0.036621 | 122.8043 | 122.8638 | -0.14191 | 122.4884 | 0.12817 | 0.3479 | 122.8638 | 123.0927 | 122.9004 | 123.0789 | 122.8043 | 123.1705 | 122.8683 | 122.4884 | 123.0789 | 122.8043 | 122.8683 | 122.9004 | 123.1705 | -0.58594 | -0.55389
4816.0312 | 123.1796 | -122.8455 | 0.19226 | -0.13649 | 0.0087841 | -0.014642 | 0.040242 | -0.019393 | -0.01233 | 0.0045031 | -0.004578 | 0.20599 | -0.36621 | 0.11444 | 0.14191 | 0.14648 | -0.16022 | 0.35706 | 0.27924 | -0.32959 | 122.4792 | 0.013733 | 122.8409 | 122.9599 | -0.050354 | 122.5159 | 0.086975 | 0.36163 | 122.6852 | 123.2025 | 122.9874 | 123.0515 | 122.8409 | 123.1247 | 122.9919 | 122.5159 | 123.0515 | 122.8409 | 122.9919 | 122.9874 | 123.1247 | -0.55847 | -0.52185
4817.7188 | 123.2391 | -122.85 | 0.17395 | 0.046615 | 0.0089979 | -0.014642 | 0.040029 | -0.021956 | -0.010621 | 0.0059985 | -0.050354 | 0.21057 | -0.38452 | 0.036621 | 0.068665 | 0.07782 | -0.11444 | 0.27924 | 0.28839 | -0.34332 | 122.4655 | 0.036621 | 122.7997 | 122.8867 | -0.10528 | 122.5067 | 0.11444 | 0.33417 | 122.7356 | 123.1293 | 122.9187 | 123.0606 | 122.7997 | 123.1384 | 122.9279 | 122.5067 | 123.0606 | 122.7997 | 122.9279 | 122.9187 | 123.1384 | -0.55847 | -0.51727
4819.4062 | 123.175 | -122.8271 | 0.19684 | -0.20515 | 0.0092115 | -0.017419 | 0.041951 | -0.022383 | -0.014467 | 0.0021533 | 0.018311 | 0.1831 | -0.37994 | 0.11444 | 0.12817 | 0.1236 | -0.14191 | 0.34332 | 0.27924 | -0.33417 | 122.4472 | -0.013733 | 122.8455 | 122.9416 | -0.068664 | 122.493 | 0.082398 | 0.39826 | 122.6852 | 123.1705 | 122.9553 | 123.0103 | 122.8455 | 123.1064 | 122.9507 | 122.493 | 123.0103 | 122.8455 | 122.9507 | 122.9553 | 123.1064 | -0.57678 | -0.531
4821.0938 | 123.0881 | -122.8775 | 0.21515 | 0.16106 | 0.010707 | -0.010369 | 0.045369 | -0.020888 | -0.01233 | 0.0053577 | -0.004578 | 0.19684 | -0.38452 | 0.10529 | 0.091553 | 0.12817 | -0.19226 | 0.27924 | 0.2655 | -0.33417 | 122.493 | -0.018311 | 122.8729 | 122.9828 | -0.1236 | 122.5433 | 0.050354 | 0.37994 | 122.6852 | 123.1567 | 122.9691 | 123.0743 | 122.8729 | 123.143 | 123.0057 | 122.5433 | 123.0743 | 122.8729 | 123.0057 | 122.9691 | 123.143 | -0.59967 | -0.54932
4822.7969 | 123.1018 | -122.8821 | 0.21973 | 0.1992 | 0.010921 | -0.010583 | 0.045583 | -0.020247 | -0.01233 | 0.0051441 | -0.059509 | 0.21973 | -0.40283 | 0.045776 | 0.073242 | 0.082397 | -0.15106 | 0.25635 | 0.30212 | -0.34332 | 122.4792 | 0 | 122.8226 | 122.9279 | -0.14649 | 122.5388 | 0.082397 | 0.34332 | 122.731 | 123.1384 | 122.9553 | 123.1018 | 122.8226 | 123.1842 | 122.9645 | 122.5388 | 123.1018 | 122.8226 | 122.9645 | 122.9553 | 123.1842 | -0.62256 | -0.56305
4824.5156 | 123.0927 | -122.8775 | 0.23346 | 0.15343 | 0.010493 | -0.012719 | 0.046865 | -0.019606 | -0.012117 | 0.0057849 | 0.013733 | 0.16479 | -0.37994 | 0.10071 | 0.10986 | 0.14648 | -0.20599 | 0.28839 | 0.26093 | -0.31586 | 122.4976 | -0.068664 | 122.8912 | 122.9782 | -0.1236 | 122.5616 | 0.027466 | 0.39368 | 122.6715 | 123.1659 | 122.9874 | 123.0423 | 122.8912 | 123.1384 | 123.024 | 122.5616 | 123.0423 | 122.8912 | 123.024 | 122.9874 | 123.1384 | -0.6134 | -0.54932
4826.2031 | 123.1796 | -122.8363 | 0.17853 | 0.25261 | 0.0075025 | -0.012933 | 0.040456 | -0.021743 | -0.01233 | 0.0062121 | -0.050354 | 0.20142 | -0.36621 | 0.059509 | 0.086975 | 0.09613 | -0.14191 | 0.27924 | 0.27466 | -0.33417 | 122.4701 | 0.022888 | 122.7859 | 122.8958 | -0.091553 | 122.5021 | 0.09613 | 0.31586 | 122.6944 | 123.1155 | 122.9233 | 123.0377 | 122.7859 | 123.111 | 122.9324 | 122.5021 | 123.0377 | 122.7859 | 122.9324 | 122.9233 | 123.111 | -0.54474 | -0.5127
4827.9375 | 123.1338 | -122.8729 | 0.21057 | 0.13054 | 0.0094251 | -0.011437 | 0.041524 | -0.021529 | -0.013185 | 0.0081347 | -0.018311 | 0.20142 | -0.37537 | 0.068665 | 0.10529 | 0.13733 | -0.19226 | 0.29755 | 0.25177 | -0.32501 | 122.4976 | -0.009155 | 122.8546 | 122.9416 | -0.10529 | 122.5479 | 0.041199 | 0.35705 | 122.6807 | 123.1705 | 122.9782 | 123.0743 | 122.8546 | 123.1247 | 123.0103 | 122.5479 | 123.0743 | 122.8546 | 123.0103 | 122.9782 | 123.1247 | -0.58594 | -0.53558
4829.625 | 123.1476 | -122.8775 | 0.20142 | 0.13054 | 0.011348 | -0.016564 | 0.04836 | -0.020247 | -0.01169 | 0.0053577 | -0.10071 | 0.23804 | -0.41657 | -0.027466 | -0.013733 | 0 | -0.027466 | 0.17853 | 0.30212 | -0.36621 | 122.4609 | 0.036621 | 122.7768 | 122.85 | -0.21515 | 122.5113 | 0.10071 | 0.31586 | 122.85 | 123.056 | 122.8638 | 123.1155 | 122.7768 | 123.1796 | 122.8775 | 122.5113 | 123.1155 | 122.7768 | 122.8775 | 122.8638 | 123.1796 | -0.61798 | -0.56763
4831.3281 | 123.1338 | -122.8912 | 0.20599 | 0.10002 | 0.010707 | -0.012078 | 0.044942 | -0.019179 | -0.012758 | 0.0047167 | -0.082397 | 0.23346 | -0.42114 | 0 | 0.027466 | 0.022888 | -0.10529 | 0.21057 | 0.31128 | -0.35706 | 122.4701 | 0.027465 | 122.8088 | 122.8912 | -0.17853 | 122.5342 | 0.10528 | 0.33875 | 122.7859 | 123.1018 | 122.9187 | 123.1247 | 122.8088 | 123.2025 | 122.9141 | 122.5342 | 123.1247 | 122.8088 | 122.9141 | 122.9187 | 123.2025 | -0.62714 | -0.56305
4833.0156 | 123.1201 | -122.8775 | 0.21515 | -0.13649 | 0.0098523 | -0.013574 | 0.045156 | -0.020461 | -0.014467 | 0.0040759 | -0.032043 | 0.24261 | -0.39825 | 0.027466 | 0.054932 | 0.036621 | -0.027466 | 0.24261 | 0.32501 | -0.35248 | 122.4792 | 0.027466 | 122.8455 | 122.905 | -0.16022 | 122.525 | 0.10986 | 0.36621 | 122.85 | 123.1201 | 122.9324 | 123.1201 | 122.8455 | 123.2025 | 122.9141 | 122.525 | 123.1201 | 122.8455 | 122.9141 | 122.9324 | 123.2025 | -0.6134 | -0.56763
4834.7031 | 123.2391 | -122.85 | 0.19226 | -0.22804 | 0.0092115 | -0.014214 | 0.040029 | -0.021102 | -0.014039 | 0.0051441 | -0.10986 | 0.23804 | -0.40741 | -0.027466 | 0.013733 | 0.004578 | 0.050354 | 0.20142 | 0.32959 | -0.37537 | 122.4426 | 0.045776 | 122.7402 | 122.8226 | -0.17853 | 122.4747 | 0.13733 | 0.29755 | 122.9004 | 123.0515 | 122.8638 | 123.0881 | 122.7402 | 123.1796 | 122.8546 | 122.4747 | 123.0881 | 122.7402 | 122.8546 | 122.8638 | 123.1796 | -0.59967 | -0.56763
4836.4219 | 123.23 | -122.8134 | 0.17395 | 0.0084684 | 0.0075025 | -0.010583 | 0.037892 | -0.01982 | -0.011049 | 0.0062121 | -0.050354 | 0.20599 | -0.37079 | 0.032043 | 0.091553 | 0.09613 | -0.12817 | 0.28839 | 0.27924 | -0.35248 | 122.4426 | 0.032044 | 122.7631 | 122.8455 | -0.082397 | 122.4609 | 0.10529 | 0.32043 | 122.6852 | 123.1018 | 122.905 | 123.0194 | 122.7631 | 123.0927 | 122.9095 | 122.4609 | 123.0194 | 122.7631 | 122.9095 | 122.905 | 123.0927 | -0.54474 | -0.52643
4838.1094 | 123.2254 | -122.8363 | 0.17853 | 0.054245 | 0.0083569 | -0.010369 | 0.039601 | -0.021315 | -0.013612 | 0.0068531 | -0.068665 | 0.20142 | -0.38452 | 0.036621 | 0.07782 | 0.086975 | -0.11444 | 0.27466 | 0.28381 | -0.33417 | 122.4518 | 0.022888 | 122.7676 | 122.8729 | -0.10071 | 122.5021 | 0.10528 | 0.31586 | 122.7219 | 123.111 | 122.9141 | 123.0377 | 122.7676 | 123.1201 | 122.9233 | 122.5021 | 123.0377 | 122.7676 | 122.9233 | 122.9141 | 123.1201 | -0.56305 | -0.5127
4839.7969 | 123.1888 | -122.8775 | 0.19226 | 0.084762 | 0.01028 | -0.013146 | 0.040456 | -0.021529 | -0.0089123 | 0.0059985 | -0.027466 | 0.19684 | -0.36621 | 0.059509 | 0.07782 | 0.10529 | -0.12817 | 0.27466 | 0.27924 | -0.3479 | 122.5113 | 0.004577 | 122.85 | 122.937 | -0.11444 | 122.5296 | 0.086975 | 0.33875 | 122.7493 | 123.1522 | 122.9553 | 123.0743 | 122.85 | 123.1567 | 122.9828 | 122.5296 | 123.0743 | 122.85 | 122.9828 | 122.9553 | 123.1567 | -0.55847 | -0.54016
4841.4844 | 123.1567 | -122.8729 | 0.20142 | 0.16106 | 0.0096387 | -0.014001 | 0.043233 | -0.021315 | -0.01233 | 0.0049303 | -0.018311 | 0.17395 | -0.3891 | 0.041199 | 0.082397 | 0.10071 | -0.15564 | 0.27924 | 0.27008 | -0.32959 | 122.4838 | -0.027466 | 122.8546 | 122.9141 | -0.11902 | 122.5433 | 0.068665 | 0.37079 | 122.7173 | 123.1522 | 122.9553 | 123.0469 | 122.8546 | 123.143 | 122.9736 | 122.5433 | 123.0469 | 122.8546 | 122.9736 | 122.9553 | 123.143 | -0.59052 | -0.53101
4843.1719 | 123.143 | -122.8638 | 0.21515 | 0.1458 | 0.0092115 | -0.0097284 | 0.046437 | -0.020247 | -0.014467 | 0.0057849 | -0.09613 | 0.24261 | -0.40741 | 0.013733 | 0 | 0.022888 | -0.054932 | 0.1831 | 0.3067 | -0.37079 | 122.4564 | 0.027466 | 122.7676 | 122.8775 | -0.21515 | 122.493 | 0.091553 | 0.31128 | 122.8088 | 123.0469 | 122.8638 | 123.1064 | 122.7676 | 123.1705 | 122.8867 | 122.493 | 123.1064 | 122.7676 | 122.8867 | 122.8638 | 123.1705 | -0.62256 | -0.58594
4844.8594 | 123.1476 | -122.8546 | 0.21515 | 0.069504 | 0.010066 | -0.010583 | 0.049855 | -0.020247 | -0.012758 | 0.0070667 | -0.082397 | 0.23346 | -0.42572 | -0.013733 | -0.018311 | -0.022888 | -0.004578 | 0.15564 | 0.31128 | -0.37079 | 122.4289 | 0.01831 | 122.7722 | 122.8409 | -0.23346 | 122.4838 | 0.09613 | 0.34332 | 122.85 | 123.0103 | 122.8363 | 123.0881 | 122.7722 | 123.1659 | 122.8317 | 122.4838 | 123.0881 | 122.7722 | 122.8317 | 122.8363 | 123.1659 | -0.64087 | -0.58594
4846.5469 | 123.1293 | -122.8638 | 0.21515 | 0.1458 | 0.010066 | -0.01336 | 0.043874 | -0.020674 | -0.0097669 | 0.0066393 | -0.09613 | 0.25177 | -0.39825 | -0.022888 | 0.004578 | 0.018311 | -0.032043 | 0.17395 | 0.29755 | -0.38452 | 122.4655 | 0.036621 | 122.7676 | 122.8409 | -0.21057 | 122.4792 | 0.082397 | 0.30212 | 122.8317 | 123.0377 | 122.8683 | 123.1155 | 122.7676 | 123.1613 | 122.8821 | 122.4792 | 123.1155 | 122.7676 | 122.8821 | 122.8683 | 123.1613 | -0.6134 | -0.59967
4848.2344 | 123.111 | -122.8958 | 0.21515 | 0.16869 | 0.0075025 | -0.012933 | 0.040029 | -0.018325 | -0.010835 | 0.0047167 | 0 | 0.20142 | -0.35248 | 0.068665 | 0.11444 | 0.13275 | -0.1831 | 0.29755 | 0.25635 | -0.33417 | 122.5433 | -0.013733 | 122.8958 | 122.9645 | -0.10071 | 122.5616 | 0.041199 | 0.35248 | 122.7127 | 123.1934 | 123.0103 | 123.0972 | 122.8958 | 123.1522 | 123.0286 | 122.5616 | 123.0972 | 122.8958 | 123.0286 | 123.0103 | 123.1522 | -0.56763 | -0.54932
4849.9844 | 123.1979 | -122.8455 | 0.20599 | -0.19753 | 0.0079297 | -0.010583 | 0.039601 | -0.02217 | -0.012971 | 0.0064257 | 0 | 0.19684 | -0.3479 | 0.07782 | 0.14191 | 0.13275 | -0.14191 | 0.3479 | 0.26093 | -0.33417 | 122.4976 | -0.009156 | 122.8455 | 122.9233 | -0.064087 | 122.5113 | 0.054931 | 0.3479 | 122.7036 | 123.1934 | 122.9874 | 123.0423 | 122.8455 | 123.1064 | 122.9782 | 122.5113 | 123.0423 | 122.8455 | 122.9782 | 122.9874 | 123.1064 | -0.55389 | -0.54016
4851.6719 | 123.1796 | -122.8546 | 0.19684 | -0.20515 | 0.010921 | -0.010796 | 0.038961 | -0.020888 | -0.012544 | 0.0047167 | 0.009155 | 0.21057 | -0.36621 | 0.10071 | 0.12817 | 0.13733 | -0.14191 | 0.34332 | 0.27008 | -0.32959 | 122.4884 | 0.013733 | 122.8638 | 122.9553 | -0.068664 | 122.525 | 0.073243 | 0.37537 | 122.7127 | 123.1979 | 122.9828 | 123.0652 | 122.8638 | 123.1247 | 122.9919 | 122.525 | 123.0652 | 122.8638 | 122.9919 | 122.9828 | 123.1247 | -0.56305 | -0.52643
4853.3906 | 123.1018 | -122.8867 | 0.21515 | -0.10597 | 0.0075025 | -0.011651 | 0.047292 | -0.020888 | -0.015321 | 0.0049303 | -0.045776 | 0.25635 | -0.41199 | 0.045776 | 0.036621 | 0.054932 | -0.027466 | 0.24261 | 0.30212 | -0.36163 | 122.4747 | 0.041199 | 122.8409 | 122.9324 | -0.17853 | 122.525 | 0.086975 | 0.36621 | 122.8592 | 123.1293 | 122.9233 | 123.143 | 122.8409 | 123.1888 | 122.9416 | 122.525 | 123.143 | 122.8409 | 122.9416 | 122.9233 | 123.1888 | -0.62714 | -0.57678
4855.0938 | 123.1522 | -122.9004 | 0.20142 | 0.1458 | 0.011134 | -0.0088738 | 0.045797 | -0.019179 | -0.012971 | 0.0053577 | -0.082397 | 0.24261 | -0.39825 | -0.009155 | 0.013733 | 0.027466 | -0.068665 | 0.18768 | 0.29755 | -0.36621 | 122.5021 | 0.041199 | 122.818 | 122.8912 | -0.18768 | 122.5342 | 0.09613 | 0.31586 | 122.8317 | 123.0881 | 122.9141 | 123.143 | 122.818 | 123.1979 | 122.9279 | 122.5342 | 123.143 | 122.818 | 122.9279 | 122.9141 | 123.1979 | -0.59967 | -0.56763
4856.7812 | 123.1476 | -122.8775 | 0.20142 | 0.13054 | 0.0089979 | -0.012292 | 0.044728 | -0.020888 | -0.014253 | 0.0062121 | -0.10986 | 0.24261 | -0.41657 | -0.041199 | -0.009155 | -0.009155 | -0.004578 | 0.16479 | 0.31586 | -0.37079 | 122.4609 | 0.041199 | 122.7676 | 122.8363 | -0.21057 | 122.5067 | 0.11444 | 0.3067 | 122.8729 | 123.0423 | 122.8683 | 123.1201 | 122.7676 | 123.1934 | 122.8683 | 122.5067 | 123.1201 | 122.7676 | 122.8683 | 122.8683 | 123.1934 | -0.61798 | -0.5722
4858.4688 | 123.1979 | -122.8546 | 0.19684 | -0.13649 | 0.010066 | -0.015496 | 0.037465 | -0.019606 | -0.011262 | 0.0049303 | -0.004578 | 0.21515 | -0.37079 | 0.09613 | 0.12817 | 0.13275 | -0.14191 | 0.34332 | 0.26093 | -0.32959 | 122.4838 | 0.018311 | 122.85 | 122.9507 | -0.068664 | 122.525 | 0.064087 | 0.36621 | 122.7127 | 123.1979 | 122.9828 | 123.0698 | 122.85 | 123.1155 | 122.9874 | 122.525 | 123.0698 | 122.85 | 122.9874 | 122.9828 | 123.1155 | -0.56763 | -0.52643
4860.1719 | 123.1934 | -122.8363 | 0.20142 | -0.16701 | 0.0089979 | -0.011224 | 0.04067 | -0.021102 | -0.011476 | 0.0040759 | -0.004578 | 0.20599 | -0.37079 | 0.082397 | 0.12817 | 0.11902 | -0.10529 | 0.32959 | 0.27924 | -0.32501 | 122.4655 | 0.004578 | 122.8317 | 122.9187 | -0.073242 | 122.5113 | 0.07782 | 0.36621 | 122.731 | 123.1659 | 122.9645 | 123.0423 | 122.8317 | 123.1155 | 122.9553 | 122.5113 | 123.0423 | 122.8317 | 122.9553 | 122.9645 | 123.1155 | -0.5722 | -0.52643
4861.8438 | 123.1613 | -122.8958 | 0.2243 | 0.0084684 | 0.0087841 | -0.0097284 | 0.047292 | -0.018752 | -0.015535 | 0.0040759 | -0.064087 | 0.24261 | -0.41199 | -0.022888 | -0.022888 | -0.004578 | -0.009155 | 0.17395 | 0.28839 | -0.37079 | 122.4838 | 0.018311 | 122.8317 | 122.8729 | -0.24719 | 122.525 | 0.064087 | 0.3479 | 122.8867 | 123.0698 | 122.8729 | 123.1384 | 122.8317 | 123.1842 | 122.8912 | 122.525 | 123.1384 | 122.8317 | 122.8912 | 122.8729 | 123.1842 | -0.63629 | -0.59509
4863.5312 | 123.1613 | -122.8867 | 0.20599 | 0.1458 | 0.0085705 | -0.008233 | 0.044301 | -0.015975 | -0.014039 | 0.0072803 | -0.11444 | 0.23346 | -0.42572 | -0.022888 | 0 | 0 | -0.018311 | 0.16937 | 0.32501 | -0.3479 | 122.4609 | 0.027465 | 122.7722 | 122.8638 | -0.20599 | 122.5388 | 0.11902 | 0.31128 | 122.8683 | 123.056 | 122.8867 | 123.1201 | 122.7722 | 123.2117 | 122.8867 | 122.5388 | 123.1201 | 122.7722 | 122.8867 | 122.8867 | 123.2117 | -0.63171 | -0.55389
4865.2188 | 123.2483 | -122.8546 | 0.17853 | -0.20515 | 0.0083569 | -0.01336 | 0.040242 | -0.020674 | -0.01233 | 0.0047167 | -0.091553 | 0.25177 | -0.40283 | -0.018311 | 0.027466 | 0 | 0.036621 | 0.20599 | 0.31128 | -0.37537 | 122.4518 | 0.073242 | 122.7631 | 122.8363 | -0.15106 | 122.4792 | 0.13275 | 0.31128 | 122.8912 | 123.0606 | 122.8821 | 123.1064 | 122.7631 | 123.1659 | 122.8546 | 122.4792 | 123.1064 | 122.7631 | 122.8546 | 122.8821 | 123.1659 | -0.58136 | -0.55389
4866.9688 | 123.2529 | -122.8455 | 0.18768 | -0.22041 | 0.0068615 | -0.012292 | 0.041097 | -0.020674 | -0.010835 | 0.0045031 | -0.09613 | 0.24719 | -0.41199 | -0.022888 | 0.013733 | 0.004578 | 0.032043 | 0.23346 | 0.3067 | -0.37079 | 122.4335 | 0.059509 | 122.7493 | 122.8226 | -0.17395 | 122.4747 | 0.11902 | 0.31586 | 122.8775 | 123.0789 | 122.8592 | 123.0927 | 122.7493 | 123.1522 | 122.85 | 122.4747 | 123.0927 | 122.7493 | 122.85 | 122.8592 | 123.1522 | -0.59967 | -0.55847
4868.6562 | 123.23 | -122.8455 | 0.19226 | -0.28145 | 0.0089979 | -0.014428 | 0.039388 | -0.01982 | -0.010194 | 0.0045031 | -0.022888 | 0.22888 | -0.38452 | 0.027466 | 0.068665 | 0.059509 | -0.009155 | 0.27924 | 0.30212 | -0.37079 | 122.4609 | 0.036621 | 122.8226 | 122.8729 | -0.1236 | 122.4747 | 0.10986 | 0.36163 | 122.8363 | 123.1247 | 122.9141 | 123.0743 | 122.8226 | 123.1476 | 122.905 | 122.4747 | 123.0743 | 122.8226 | 122.905 | 122.9141 | 123.1476 | -0.57678 | -0.56305
4870.375 | 123.111 | -122.8867 | 0.21515 | 0.18394 | 0.0098523 | -0.010796 | 0.044301 | -0.019179 | -0.012758 | 0.0038623 | 0.018311 | 0.18768 | -0.37079 | 0.07782 | 0.09613 | 0.14648 | -0.1831 | 0.32501 | 0.27466 | -0.3067 | 122.5159 | -0.027466 | 122.905 | 122.9645 | -0.11902 | 122.58 | 0.059509 | 0.3891 | 122.7036 | 123.2117 | 122.9828 | 123.0743 | 122.905 | 123.1613 | 123.0331 | 122.58 | 123.0743 | 122.905 | 123.0331 | 122.9828 | 123.1613 | -0.58594 | -0.52185
4872.0625 | 123.0927 | -122.8546 | 0.20142 | 0.18394 | 0.0085705 | -0.011865 | 0.045583 | -0.020034 | -0.015107 | 0.0059985 | -0.059509 | 0.20599 | -0.41199 | 0.036621 | 0.054932 | 0.068665 | -0.12817 | 0.25635 | 0.28839 | -0.35248 | 122.4426 | 0.004578 | 122.7951 | 122.8912 | -0.14648 | 122.5021 | 0.086975 | 0.35248 | 122.7264 | 123.111 | 122.9095 | 123.0606 | 122.7951 | 123.143 | 122.9233 | 122.5021 | 123.0606 | 122.7951 | 122.9233 | 122.9095 | 123.143 | -0.6134 | -0.55389
4873.7656 | 123.1522 | -122.8867 | 0.19684 | 0.16106 | 0.0081433 | -0.01101 | 0.044728 | -0.020247 | -0.014253 | 0.0068531 | -0.10529 | 0.23346 | -0.41657 | -0.027466 | -0.009155 | 0.004578 | -0.022888 | 0.16937 | 0.32501 | -0.35706 | 122.4701 | 0.036621 | 122.7814 | 122.8592 | -0.20599 | 122.5296 | 0.12817 | 0.31128 | 122.8638 | 123.056 | 122.8775 | 123.1201 | 122.7814 | 123.2117 | 122.8912 | 122.5296 | 123.1201 | 122.7814 | 122.8912 | 122.8775 | 123.2117 | -0.6134 | -0.55389
4875.4688 | 123.1476 | -122.8867 | 0.21973 | -0.14412 | 0.0081433 | -0.014428 | 0.042592 | -0.019393 | -0.015107 | 0.0047167 | -0.050354 | 0.21973 | -0.41657 | 0.022888 | 0.059509 | 0.045776 | -0.009155 | 0.24719 | 0.32044 | -0.35706 | 122.4701 | 0 | 122.8363 | 122.9095 | -0.16022 | 122.5296 | 0.10071 | 0.36621 | 122.8775 | 123.1338 | 122.9462 | 123.1064 | 122.8363 | 123.2071 | 122.9324 | 122.5296 | 123.1064 | 122.8363 | 122.9324 | 122.9462 | 123.2071 | -0.63629 | -0.57678
4877.1875 | 123.2666 | -122.8546 | 0.1831 | -0.23567 | 0.0089979 | -0.013574 | 0.040456 | -0.021529 | -0.01169 | 0.0038623 | -0.11902 | 0.25635 | -0.41657 | -0.027466 | 0.018311 | 0.009155 | 0.059509 | 0.21515 | 0.34332 | -0.36621 | 122.438 | 0.073243 | 122.7356 | 122.8271 | -0.16479 | 122.4884 | 0.16022 | 0.29755 | 122.9141 | 123.0698 | 122.8729 | 123.111 | 122.7356 | 123.1979 | 122.8638 | 122.4884 | 123.111 | 122.7356 | 122.8638 | 122.8729 | 123.1979 | -0.59967 | -0.54932
4878.9375 | 123.2071 | -122.8363 | 0.16022 | -0.060196 | 0.0060071 | -0.01571 | 0.036397 | -0.018325 | -0.011049 | 0.0053577 | -0.032043 | 0.21515 | -0.36621 | 0.059509 | 0.10986 | 0.12817 | -0.12817 | 0.32044 | 0.26093 | -0.32044 | 122.4701 | 0.054932 | 122.8043 | 122.8958 | -0.050354 | 122.5159 | 0.10071 | 0.33417 | 122.7081 | 123.1567 | 122.9462 | 123.0515 | 122.8043 | 123.0972 | 122.9645 | 122.5159 | 123.0515 | 122.8043 | 122.9645 | 122.9462 | 123.0972 | -0.52643 | -0.48065
4880.625 | 123.1155 | -122.8821 | 0.20599 | 0.13054 | 0.010921 | -0.012505 | 0.043019 | -0.018111 | -0.0093395 | 0.0038623 | 0.022888 | 0.19226 | -0.37537 | 0.073242 | 0.10986 | 0.1236 | -0.17853 | 0.30212 | 0.27924 | -0.33417 | 122.5067 | -0.013733 | 122.905 | 122.9553 | -0.096131 | 122.5479 | 0.073242 | 0.39825 | 122.7036 | 123.1842 | 122.9919 | 123.0743 | 122.905 | 123.1613 | 123.0057 | 122.5479 | 123.0743 | 122.905 | 123.0057 | 122.9919 | 123.1613 | -0.58136 | -0.54016
4882.3438 | 123.0835 | -122.8958 | 0.2243 | 0.19157 | 0.010493 | -0.01336 | 0.042806 | -0.018752 | -0.012117 | 0.0057849 | 0.027466 | 0.19226 | -0.39368 | 0.09613 | 0.10986 | 0.13733 | -0.20599 | 0.31128 | 0.25177 | -0.32044 | 122.5021 | -0.032043 | 122.9233 | 122.9919 | -0.11444 | 122.5754 | 0.027466 | 0.42114 | 122.6898 | 123.2071 | 123.0057 | 123.0881 | 122.9233 | 123.1476 | 123.0331 | 122.5754 | 123.0881 | 122.9233 | 123.0331 | 123.0057 | 123.1476 | -0.61798 | -0.54474
4884.0625 | 123.2117 | -122.8638 | 0.18768 | 0.069504 | 0.010921 | -0.01336 | 0.039174 | -0.020461 | -0.011476 | 0.0027941 | -0.022888 | 0.21515 | -0.37537 | 0.032043 | 0.064087 | 0.10071 | -0.12817 | 0.2655 | 0.28839 | -0.32959 | 122.4884 | 0.027466 | 122.8409 | 122.8958 | -0.1236 | 122.5342 | 0.10071 | 0.35248 | 122.7356 | 123.1293 | 122.9279 | 123.0789 | 122.8409 | 123.1522 | 122.9645 | 122.5342 | 123.0789 | 122.8409 | 122.9645 | 122.9279 | 123.1522 | -0.56305 | -0.51727
4885.75 | 123.143 | -122.8821 | 0.17853 | 0.12291 | 0.010707 | -0.018914 | 0.041097 | -0.020461 | -0.01169 | 0.0064257 | -0.018311 | 0.20599 | -0.37994 | 0.045776 | 0.068665 | 0.10529 | -0.14648 | 0.27924 | 0.27466 | -0.32959 | 122.5021 | 0.027466 | 122.8638 | 122.9279 | -0.10986 | 122.5525 | 0.09613 | 0.36163 | 122.7356 | 123.1613 | 122.9507 | 123.0881 | 122.8638 | 123.1567 | 122.9874 | 122.5525 | 123.0881 | 122.8638 | 122.9874 | 122.9507 | 123.1567 | -0.55847 | -0.50812
4887.4375 | 123.0881 | -122.8821 | 0.21057 | 0.1992 | 0.0085705 | -0.0086602 | 0.043233 | -0.020888 | -0.010835 | 0.0042895 | 0.018311 | 0.20142 | -0.35706 | 0.10071 | 0.09613 | 0.14648 | -0.20599 | 0.32044 | 0.26093 | -0.32501 | 122.525 | -0.009155 | 122.9004 | 122.9828 | -0.11444 | 122.5571 | 0.050354 | 0.37537 | 122.6761 | 123.2025 | 122.9782 | 123.0835 | 122.9004 | 123.143 | 123.0286 | 122.5571 | 123.0835 | 122.9004 | 123.0286 | 122.9782 | 123.143 | -0.56763 | -0.53558
4889.1094 | 123.143 | -122.8775 | 0.23346 | -0.01442 | 0.0092115 | -0.011224 | 0.046224 | -0.020461 | -0.015321 | 0.0051441 | -0.041199 | 0.21057 | -0.40283 | -0.004578 | -0.009155 | -0.013733 | -0.018311 | 0.18768 | 0.30212 | -0.37079 | 122.4747 | -0.022888 | 122.8363 | 122.8729 | -0.24261 | 122.5067 | 0.068665 | 0.36163 | 122.8592 | 123.0652 | 122.8683 | 123.0881 | 122.8363 | 123.1796 | 122.8638 | 122.5067 | 123.0881 | 122.8363 | 122.8638 | 122.8683 | 123.1796 | -0.63629 | -0.60425
4890.8281 | 123.2071 | -122.8546 | 0.20599 | 0.046615 | 0.0085705 | -0.013787 | 0.038747 | -0.020247 | -0.014253 | 0.0057849 | -0.045776 | 0.21057 | -0.37537 | 0.036621 | 0.07782 | 0.10529 | -0.11902 | 0.27924 | 0.28381 | -0.33417 | 122.4792 | 0.004577 | 122.8088 | 122.8912 | -0.12817 | 122.5204 | 0.077819 | 0.32959 | 122.7356 | 123.1338 | 122.9324 | 123.0652 | 122.8088 | 123.1384 | 122.9599 | 122.5204 | 123.0652 | 122.8088 | 122.9599 | 122.9324 | 123.1384 | -0.58136 | -0.54016
4892.5312 | 123.23 | -122.8317 | 0.17395 | 0.0084684 | 0.0075025 | -0.014214 | 0.039174 | -0.020034 | -0.01169 | 0.0047167 | -0.054932 | 0.21515 | -0.38452 | 0.036621 | 0.068665 | 0.082397 | -0.1236 | 0.28839 | 0.27924 | -0.35706 | 122.4472 | 0.041199 | 122.7768 | 122.8683 | -0.10528 | 122.4747 | 0.10529 | 0.32959 | 122.7081 | 123.1201 | 122.9004 | 123.0469 | 122.7768 | 123.111 | 122.9141 | 122.4747 | 123.0469 | 122.7768 | 122.9141 | 122.9004 | 123.111 | -0.55847 | -0.53101
4894.2188 | 123.175 | -122.8638 | 0.20142 | 0.077133 | 0.010493 | -0.013146 | 0.040883 | -0.021102 | -0.01233 | 0.0032215 | -0.041199 | 0.20142 | -0.3891 | 0.045776 | 0.073242 | 0.10529 | -0.13275 | 0.27924 | 0.28381 | -0.35248 | 122.4747 | 0 | 122.8226 | 122.9095 | -0.12817 | 122.5113 | 0.082397 | 0.3479 | 122.731 | 123.143 | 122.937 | 123.0652 | 122.8226 | 123.1476 | 122.9691 | 122.5113 | 123.0652 | 122.8226 | 122.9691 | 122.937 | 123.1476 | -0.59052 | -0.55389
4895.9688 | 123.2437 | -122.8317 | 0.16937 | -0.19753 | 0.0087841 | -0.013787 | 0.043233 | -0.023452 | -0.01233 | 0.0040759 | -0.086975 | 0.23804 | -0.42114 | -0.013733 | 0.018311 | 0.004578 | 0.036621 | 0.23346 | 0.29755 | -0.37537 | 122.4106 | 0.068664 | 122.7448 | 122.818 | -0.15106 | 122.4564 | 0.12817 | 0.33417 | 122.8683 | 123.0652 | 122.85 | 123.0698 | 122.7448 | 123.1293 | 122.8363 | 122.4564 | 123.0698 | 122.7448 | 122.8363 | 122.85 | 123.1293 | -0.59052 | -0.54474
4897.6562 | 123.2483 | -122.8546 | 0.1831 | -0.25856 | 0.011134 | -0.015069 | 0.043019 | -0.023238 | -0.01468 | 0.0036487 | -0.10071 | 0.27008 | -0.41657 | 0 | 0.009155 | -0.004578 | 0.054932 | 0.20142 | 0.3067 | -0.37994 | 122.438 | 0.086976 | 122.7539 | 122.8546 | -0.17395 | 122.4747 | 0.1236 | 0.31586 | 122.9095 | 123.056 | 122.8638 | 123.1247 | 122.7539 | 123.1613 | 122.85 | 122.4747 | 123.1247 | 122.7539 | 122.85 | 122.8638 | 123.1613 | -0.59967 | -0.56305
4899.3906 | 123.1293 | -122.9004 | 0.21057 | 0.16106 | 0.01028 | -0.010583 | 0.046224 | -0.018538 | -0.013185 | 0.0053577 | -0.064087 | 0.23804 | -0.40741 | 0.018311 | 0.027466 | 0.045776 | -0.10529 | 0.2243 | 0.3067 | -0.3479 | 122.493 | 0.027466 | 122.8363 | 122.9187 | -0.18311 | 122.5525 | 0.096131 | 0.34332 | 122.7951 | 123.1247 | 122.9279 | 123.1384 | 122.8363 | 123.2071 | 122.9462 | 122.5525 | 123.1384 | 122.8363 | 122.9462 | 122.9279 | 123.2071 | -0.61798 | -0.55847
4901.0781 | 123.111 | -122.8912 | 0.21515 | -0.10597 | 0.011775 | -0.0088738 | 0.04601 | -0.019393 | -0.013185 | 0.0062121 | -0.027466 | 0.23346 | -0.3891 | 0.045776 | 0.045776 | 0.045776 | -0.027466 | 0.25635 | 0.31586 | -0.35706 | 122.5021 | 0.01831 | 122.8638 | 122.937 | -0.16937 | 122.5342 | 0.10071 | 0.36163 | 122.8638 | 123.1476 | 122.937 | 123.1247 | 122.8638 | 123.2071 | 122.937 | 122.5342 | 123.1247 | 122.8638 | 122.937 | 122.937 | 123.2071 | -0.60425 | -0.5722
4902.7812 | 123.1842 | -122.8546 | 0.19684 | -0.22804 | 0.0062207 | -0.012505 | 0.039388 | -0.020247 | -0.014039 | 0.0045031 | 0.009155 | 0.21973 | -0.36163 | 0.086975 | 0.11902 | 0.11902 | -0.11444 | 0.33417 | 0.28381 | -0.34332 | 122.493 | 0.022889 | 122.8638 | 122.9416 | -0.077819 | 122.5113 | 0.086975 | 0.37079 | 122.7402 | 123.1888 | 122.9736 | 123.0743 | 122.8638 | 123.1384 | 122.9736 | 122.5113 | 123.0743 | 122.8638 | 122.9736 | 122.9736 | 123.1384 | -0.55847 | -0.54016
4904.4844 | 123.2254 | -122.8317 | 0.17395 | -0.0067901 | 0.010707 | -0.011651 | 0.037252 | -0.021315 | -0.011476 | 0.0055713 | -0.059509 | 0.2243 | -0.37994 | 0.045776 | 0.091553 | 0.091553 | -0.11444 | 0.29297 | 0.28381 | -0.32959 | 122.4518 | 0.050354 | 122.7722 | 122.8775 | -0.082397 | 122.5021 | 0.10986 | 0.32044 | 122.7173 | 123.1247 | 122.9233 | 123.056 | 122.7722 | 123.1155 | 122.9233 | 122.5021 | 123.056 | 122.7722 | 122.9233 | 122.9233 | 123.1155 | -0.55389 | -0.50354
4906.1719 | 123.2391 | -122.8409 | 0.1831 | -0.22804 | 0.0094251 | -0.010583 | 0.042379 | -0.021743 | -0.012117 | 0.0042895 | -0.07782 | 0.24719 | -0.40283 | -0.018311 | 0.009155 | 0.013733 | 0.041199 | 0.2243 | 0.32501 | -0.37994 | 122.438 | 0.064087 | 122.7631 | 122.8226 | -0.17395 | 122.4609 | 0.14191 | 0.32501 | 122.8821 | 123.0652 | 122.85 | 123.0881 | 122.7631 | 123.1659 | 122.8546 | 122.4609 | 123.0881 | 122.7631 | 122.8546 | 122.85 | 123.1659 | -0.58594 | -0.56305
4907.8594 | 123.1613 | -122.8409 | 0.19684 | 0.13054 | 0.011134 | -0.012078 | 0.039601 | -0.01982 | -0.011476 | 0.0064257 | -0.027466 | 0.19684 | -0.36621 | 0.054932 | 0.086975 | 0.091553 | -0.14648 | 0.28839 | 0.28381 | -0.33417 | 122.4747 | 0 | 122.8134 | 122.8958 | -0.10986 | 122.5067 | 0.086975 | 0.33875 | 122.6944 | 123.1293 | 122.9279 | 123.0377 | 122.8134 | 123.1247 | 122.9324 | 122.5067 | 123.0377 | 122.8134 | 122.9324 | 122.9279 | 123.1247 | -0.56305 | -0.531
4909.5625 | 123.2346 | -122.8226 | 0.17395 | 0.00083945 | 0.011561 | -0.014001 | 0.039174 | -0.020461 | -0.01233 | 0.0051441 | -0.064087 | 0.23804 | -0.37079 | 0.050354 | 0.10071 | 0.091553 | -0.13733 | 0.29755 | 0.28839 | -0.35706 | 122.4518 | 0.064087 | 122.7585 | 122.8729 | -0.073242 | 122.4655 | 0.11444 | 0.3067 | 122.6852 | 123.1201 | 122.9233 | 123.0606 | 122.7585 | 123.111 | 122.9141 | 122.4655 | 123.0606 | 122.7585 | 122.9141 | 122.9233 | 123.111 | -0.54474 | -0.53101
4911.25 | 123.2254 | -122.8592 | 0.17853 | -0.029679 | 0.0094251 | -0.014855 | 0.039174 | -0.022811 | -0.010835 | 0.0064257 | -0.036621 | 0.2243 | -0.37994 | 0.054932 | 0.07782 | 0.10986 | -0.13275 | 0.31586 | 0.26093 | -0.34332 | 122.4792 | 0.045776 | 122.8226 | 122.9141 | -0.10071 | 122.5159 | 0.082397 | 0.34332 | 122.7264 | 123.175 | 122.937 | 123.0835 | 122.8226 | 123.1201 | 122.9691 | 122.5159 | 123.0835 | 122.8226 | 122.9691 | 122.937 | 123.1201 | -0.55847 | -0.52185
4912.9844 | 123.1842 | -122.85 | 0.21515 | -0.18227 | 0.0085705 | -0.011865 | 0.042806 | -0.022811 | -0.012758 | 0.0040759 | -0.004578 | 0.20142 | -0.37079 | 0.10986 | 0.10986 | 0.13733 | -0.12817 | 0.3479 | 0.2655 | -0.32044 | 122.4792 | -0.013733 | 122.8455 | 122.9599 | -0.10529 | 122.5296 | 0.050354 | 0.36621 | 122.7219 | 123.1979 | 122.9599 | 123.0515 | 122.8455 | 123.1155 | 122.9874 | 122.5296 | 123.0515 | 122.8455 | 122.9874 | 122.9599 | 123.1155 | -0.58594 | -0.53558
4914.6719 | 123.1155 | -122.9004 | 0.20142 | 0.10765 | 0.0089979 | -0.013146 | 0.042806 | -0.01982 | -0.012544 | 0.0055713 | 0.009155 | 0.1831 | -0.37079 | 0.086975 | 0.091553 | 0.13733 | -0.1831 | 0.29755 | 0.27924 | -0.34332 | 122.5296 | -0.018311 | 122.9095 | 122.9874 | -0.10986 | 122.5571 | 0.07782 | 0.37994 | 122.7173 | 123.1979 | 122.9919 | 123.0835 | 122.9095 | 123.1796 | 123.0377 | 122.5571 | 123.0835 | 122.9095 | 123.0377 | 122.9919 | 123.1796 | -0.5722 | -0.54474
4916.3906 | 123.0972 | -122.9004 | 0.21973 | 0.1992 | 0.010066 | -0.009942 | 0.046651 | -0.019393 | -0.014467 | 0.0062121 | 0.032043 | 0.19684 | -0.37994 | 0.10986 | 0.10986 | 0.12817 | -0.21973 | 0.31586 | 0.25635 | -0.32501 | 122.5204 | -0.022889 | 122.9324 | 123.0103 | -0.10986 | 122.5754 | 0.036621 | 0.41199 | 122.6807 | 123.2162 | 123.0103 | 123.0972 | 122.9324 | 123.1567 | 123.0286 | 122.5754 | 123.0972 | 122.9324 | 123.0286 | 123.0103 | 123.1567 | -0.59967 | -0.54474
4918.0938 | 123.2346 | -122.8271 | 0.18768 | 0.00083945 | 0.0092115 | -0.015496 | 0.04067 | -0.021956 | -0.011049 | 0.0051441 | -0.041199 | 0.22888 | -0.3891 | 0.045776 | 0.07782 | 0.086975 | -0.10986 | 0.27466 | 0.2655 | -0.33875 | 122.438 | 0.041199 | 122.7859 | 122.8729 | -0.10986 | 122.4884 | 0.07782 | 0.3479 | 122.7173 | 123.1018 | 122.905 | 123.056 | 122.7859 | 123.0927 | 122.9141 | 122.4884 | 123.056 | 122.7859 | 122.9141 | 122.905 | 123.0927 | -0.57678 | -0.52643
4919.7969 | 123.2391 | -122.8226 | 0.17395 | -0.022049 | 0.010066 | -0.015496 | 0.039174 | -0.022383 | -0.011903 | 0.0062121 | -0.036621 | 0.23346 | -0.38452 | 0.054932 | 0.091553 | 0.091553 | -0.11444 | 0.29755 | 0.27008 | -0.33875 | 122.438 | 0.059509 | 122.7859 | 122.8775 | -0.082397 | 122.4838 | 0.096131 | 0.3479 | 122.7081 | 123.1201 | 122.9141 | 123.056 | 122.7859 | 123.0927 | 122.9141 | 122.4838 | 123.056 | 122.7859 | 122.9141 | 122.9141 | 123.0927 | -0.55847 | -0.5127
4921.5312 | 123.2208 | -122.8317 | 0.1831 | 0.046615 | 0.0096387 | -0.011865 | 0.039815 | -0.023238 | -0.011049 | 0.0047167 | -0.059509 | 0.22888 | -0.37537 | 0.050354 | 0.068665 | 0.07782 | -0.12817 | 0.27008 | 0.27924 | -0.37537 | 122.4564 | 0.045777 | 122.7722 | 122.8821 | -0.11444 | 122.4564 | 0.096131 | 0.31586 | 122.7036 | 123.1018 | 122.9004 | 123.0606 | 122.7722 | 123.111 | 122.9095 | 122.4564 | 123.0606 | 122.7722 | 122.9095 | 122.9004 | 123.111 | -0.55847 | -0.55847
4923.2188 | 123.2254 | -122.85 | 0.18768 | -0.01442 | 0.0062207 | -0.01571 | 0.040456 | -0.023452 | -0.012544 | 0.0064257 | -0.082397 | 0.21057 | -0.39368 | 0.054932 | 0.086975 | 0.086975 | -0.13275 | 0.29297 | 0.27466 | -0.33875 | 122.4564 | 0.022888 | 122.7676 | 122.905 | -0.10071 | 122.5113 | 0.086975 | 0.31128 | 122.7173 | 123.143 | 122.937 | 123.0606 | 122.7676 | 123.1247 | 122.937 | 122.5113 | 123.0606 | 122.7676 | 122.937 | 122.937 | 123.1247 | -0.58136 | -0.52643
4924.8906 | 123.1522 | -122.8867 | 0.20142 | 0.077133 | 0.0072889 | -0.0073786 | 0.047292 | -0.019393 | -0.011262 | 0.0049303 | -0.091553 | 0.23804 | -0.4303 | -0.022888 | -0.022888 | -0.032043 | -0.009155 | 0.16479 | 0.30212 | -0.36621 | 122.4564 | 0.036621 | 122.7951 | 122.8638 | -0.2243 | 122.5204 | 0.10071 | 0.33875 | 122.8775 | 123.0515 | 122.8638 | 123.1247 | 122.7951 | 123.1888 | 122.8546 | 122.5204 | 123.1247 | 122.7951 | 122.8546 | 122.8638 | 123.1888 | -0.63171 | -0.56763
4926.5781 | 123.1567 | -122.8546 | 0.21515 | 0.10765 | 0.0083569 | -0.01101 | 0.044515 | -0.021529 | -0.012971 | 0.0068531 | -0.10071 | 0.23346 | -0.41657 | -0.009155 | 0 | 0.018311 | -0.064087 | 0.19226 | 0.30212 | -0.36163 | 122.438 | 0.01831 | 122.7539 | 122.8455 | -0.21515 | 122.493 | 0.086975 | 0.31586 | 122.7905 | 123.0469 | 122.8546 | 123.0881 | 122.7539 | 123.1567 | 122.8729 | 122.493 | 123.0881 | 122.7539 | 122.8729 | 122.8546 | 123.1567 | -0.63171 | -0.57678
4928.2656 | 123.1293 | -122.8729 | 0.22888 | 0.15343 | 0.012202 | -0.015069 | 0.042165 | -0.020461 | -0.012758 | 0.0064257 | -0.073242 | 0.24261 | -0.40283 | 0.022888 | 0.027466 | 0.045776 | -0.091553 | 0.20599 | 0.29297 | -0.37079 | 122.4701 | 0.013733 | 122.7997 | 122.8958 | -0.20142 | 122.5021 | 0.064087 | 0.32959 | 122.7814 | 123.0789 | 122.9004 | 123.1155 | 122.7997 | 123.1659 | 122.9187 | 122.5021 | 123.1155 | 122.7997 | 122.9187 | 122.9004 | 123.1659 | -0.63171 | -0.59967
4929.9688 | 123.175 | -122.8592 | 0.21973 | -0.16701 | 0.0092115 | -0.012505 | 0.041738 | -0.021956 | -0.013612 | 0.0059985 | -0.073242 | 0.25177 | -0.41657 | 0.022888 | 0.045776 | 0.054932 | 0 | 0.24261 | 0.3067 | -0.37079 | 122.4426 | 0.032043 | 122.7859 | 122.8821 | -0.17395 | 122.4884 | 0.086975 | 0.34332 | 122.8592 | 123.1018 | 122.905 | 123.111 | 122.7859 | 123.1659 | 122.9141 | 122.4884 | 123.111 | 122.7859 | 122.9141 | 122.905 | 123.1659 | -0.63629 | -0.59052
4931.6719 | 123.1613 | -122.8867 | 0.21057 | 0.15343 | 0.0089979 | -0.015283 | 0.045369 | -0.020034 | -0.010621 | 0.0057849 | -0.10071 | 0.25177 | -0.41199 | -0.022888 | 0.004578 | 0.013733 | -0.013733 | 0.17395 | 0.32501 | -0.37079 | 122.4747 | 0.041199 | 122.7859 | 122.8638 | -0.20599 | 122.5159 | 0.11444 | 0.31128 | 122.8729 | 123.0606 | 122.8912 | 123.1384 | 122.7859 | 123.2117 | 122.9004 | 122.5159 | 123.1384 | 122.7859 | 122.9004 | 122.8912 | 123.2117 | -0.62256 | -0.58136
4933.375 | 123.2346 | -122.8317 | 0.18768 | -0.0067901 | 0.01028 | -0.012505 | 0.037038 | -0.020888 | -0.011476 | 0.0038623 | -0.064087 | 0.22888 | -0.37537 | 0.027466 | 0.091553 | 0.10986 | -0.10986 | 0.29297 | 0.27466 | -0.36163 | 122.4564 | 0.041199 | 122.7676 | 122.8592 | -0.09613 | 122.4701 | 0.086975 | 0.31128 | 122.7219 | 123.1247 | 122.9233 | 123.0606 | 122.7676 | 123.1064 | 122.9416 | 122.4701 | 123.0606 | 122.7676 | 122.9416 | 122.9233 | 123.1064 | -0.56305 | -0.54932
4935.0781 | 123.2254 | -122.8271 | 0.19226 | 0.016098 | 0.01028 | -0.010156 | 0.039388 | -0.020461 | -0.0093395 | 0.0051441 | -0.050354 | 0.21973 | -0.37537 | 0.041199 | 0.07782 | 0.09613 | -0.11902 | 0.27466 | 0.27924 | -0.36163 | 122.4518 | 0.027466 | 122.7768 | 122.8683 | -0.11444 | 122.4655 | 0.086975 | 0.32501 | 122.7081 | 123.1018 | 122.905 | 123.0469 | 122.7768 | 123.1064 | 122.9233 | 122.4655 | 123.0469 | 122.7768 | 122.9233 | 122.905 | 123.1064 | -0.56763 | -0.55389
4936.7656 | 123.1293 | -122.8912 | 0.20599 | 0.18394 | 0.010493 | -0.013574 | 0.04601 | -0.018752 | -0.011476 | 0.0059985 | -0.064087 | 0.24261 | -0.39825 | 0.027466 | 0.041199 | 0.054932 | -0.11444 | 0.23804 | 0.28839 | -0.32959 | 122.493 | 0.036621 | 122.8271 | 122.9187 | -0.1648 | 122.5616 | 0.082397 | 0.33417 | 122.7768 | 123.1293 | 122.9324 | 123.1338 | 122.8271 | 123.1796 | 122.9462 | 122.5616 | 123.1338 | 122.8271 | 122.9462 | 122.9324 | 123.1796 | -0.60425 | -0.53558
4938.4688 | 123.1934 | -122.8546 | 0.18768 | -0.037308 | 0.0083569 | -0.016992 | 0.03832 | -0.023024 | -0.0091259 | 0.0034351 | -0.036621 | 0.23346 | -0.35706 | 0.068665 | 0.10529 | 0.1236 | -0.14191 | 0.31586 | 0.27008 | -0.32501 | 122.4976 | 0.045776 | 122.818 | 122.9233 | -0.082397 | 122.5296 | 0.082398 | 0.32043 | 122.7127 | 123.1705 | 122.9599 | 123.0881 | 122.818 | 123.1247 | 122.9782 | 122.5296 | 123.0881 | 122.818 | 122.9782 | 122.9599 | 123.1247 | -0.54474 | -0.5127
4940.1562 | 123.2346 | -122.8271 | 0.16479 | -0.0067901 | 0.0081433 | -0.015069 | 0.038106 | -0.01982 | -0.011262 | 0.0042895 | -0.054932 | 0.21057 | -0.37994 | 0.050354 | 0.07782 | 0.091553 | -0.11902 | 0.28839 | 0.29755 | -0.35248 | 122.4472 | 0.045776 | 122.7722 | 122.8775 | -0.086975 | 122.4747 | 0.13275 | 0.32501 | 122.7081 | 123.1155 | 122.905 | 123.0377 | 122.7722 | 123.1247 | 122.9187 | 122.4747 | 123.0377 | 122.7722 | 122.9187 | 122.905 | 123.1247 | -0.54474 | -0.51727
4941.8438 | 123.1567 | -122.8638 | 0.20142 | 0.16106 | 0.0098523 | -0.012933 | 0.04836 | -0.01982 | -0.013399 | 0.0059985 | -0.07782 | 0.24719 | -0.42572 | -0.018311 | -0.009155 | -0.018311 | -0.018311 | 0.16937 | 0.32044 | -0.37537 | 122.4381 | 0.045776 | 122.7859 | 122.8455 | -0.21057 | 122.4884 | 0.11902 | 0.3479 | 122.8455 | 123.0331 | 122.8546 | 123.111 | 122.7859 | 123.1842 | 122.8455 | 122.4884 | 123.111 | 122.7859 | 122.8455 | 122.8546 | 123.1842 | -0.62714 | -0.57678
4943.5469 | 123.1888 | -122.8775 | 0.19684 | -0.15175 | 0.010493 | -0.020196 | 0.039174 | -0.018325 | -0.012117 | 0.0036487 | 0.013733 | 0.21515 | -0.37079 | 0.10071 | 0.14191 | 0.13733 | -0.16022 | 0.37079 | 0.27466 | -0.32959 | 122.5067 | 0.018311 | 122.8912 | 122.9782 | -0.054931 | 122.5479 | 0.07782 | 0.38452 | 122.7173 | 123.2483 | 123.0194 | 123.0927 | 122.8912 | 123.1522 | 123.0148 | 122.5479 | 123.0927 | 122.8912 | 123.0148 | 123.0194 | 123.1522 | -0.56763 | -0.52643
4945.2812 | 123.2117 | -122.8775 | 0.19226 | -0.23567 | 0.0079297 | -0.011865 | 0.042806 | -0.021102 | -0.013612 | 0.0042895 | -0.004578 | 0.21973 | -0.36163 | 0.073242 | 0.09613 | 0.091553 | -0.041199 | 0.3067 | 0.28381 | -0.3479 | 122.5159 | 0.027466 | 122.8729 | 122.9507 | -0.096131 | 122.5296 | 0.091552 | 0.35705 | 122.8363 | 123.1842 | 122.9736 | 123.0972 | 122.8729 | 123.1613 | 122.9691 | 122.5296 | 123.0972 | 122.8729 | 122.9691 | 122.9736 | 123.1613 | -0.55389 | -0.54016
4946.9688 | 123.1934 | -122.8592 | 0.1831 | 0.077133 | 0.0085705 | -0.013574 | 0.042592 | -0.021529 | -0.011903 | 0.0059985 | -0.050354 | 0.21057 | -0.37994 | 0.045776 | 0.07782 | 0.091553 | -0.13733 | 0.27466 | 0.27924 | -0.34332 | 122.4792 | 0.027466 | 122.8088 | 122.905 | -0.10528 | 122.5159 | 0.096131 | 0.32959 | 122.7219 | 123.1338 | 122.937 | 123.0698 | 122.8088 | 123.1384 | 122.9507 | 122.5159 | 123.0698 | 122.8088 | 122.9507 | 122.937 | 123.1384 | -0.56305 | -0.52643
4948.6875 | 123.1155 | -122.8683 | 0.2243 | 0.16106 | 0.010707 | -0.011224 | 0.042379 | -0.02217 | -0.012758 | 0.0042895 | 0.022888 | 0.20142 | -0.39368 | 0.09613 | 0.10529 | 0.12817 | -0.1831 | 0.3067 | 0.27466 | -0.32501 | 122.4747 | -0.022888 | 122.8912 | 122.9645 | -0.11902 | 122.5433 | 0.050354 | 0.41657 | 122.6852 | 123.175 | 122.9736 | 123.0698 | 122.8912 | 123.143 | 122.9965 | 122.5433 | 123.0698 | 122.8912 | 122.9965 | 122.9736 | 123.143 | -0.61798 | -0.54932
4950.3906 | 123.111 | -122.8912 | 0.21973 | -0.1136 | 0.0081433 | -0.009942 | 0.04836 | -0.018965 | -0.015321 | 0.0057849 | -0.022888 | 0.21515 | -0.40283 | 0.032043 | 0.036621 | 0.041199 | -0.045776 | 0.23804 | 0.3067 | -0.37079 | 122.4884 | -0.004578 | 122.8683 | 122.9233 | -0.18311 | 122.5204 | 0.086975 | 0.37994 | 122.8455 | 123.1293 | 122.9279 | 123.1064 | 122.8683 | 123.1979 | 122.9324 | 122.5204 | 123.1064 | 122.8683 | 122.9324 | 122.9279 | 123.1979 | -0.62256 | -0.59052
4952.1094 | 123.1705 | -122.8638 | 0.21057 | -0.19753 | 0.010066 | -0.011865 | 0.043233 | -0.020034 | -0.013826 | 0.0040759 | -0.064087 | 0.23804 | -0.41657 | 0.032043 | 0.045776 | 0.036621 | -0.004578 | 0.24261 | 0.31586 | -0.36621 | 122.4472 | 0.027466 | 122.7997 | 122.8958 | -0.1648 | 122.4976 | 0.10529 | 0.35248 | 122.8592 | 123.1064 | 122.9095 | 123.1018 | 122.7997 | 123.1796 | 122.9004 | 122.4976 | 123.1018 | 122.7997 | 122.9004 | 122.9095 | 123.1796 | -0.62714 | -0.57678
4953.7969 | 123.2071 | -122.8821 | 0.1831 | -0.19753 | 0.0098523 | -0.017846 | 0.043019 | -0.019179 | -0.01233 | 0.0062121 | -0.082397 | 0.25635 | -0.41657 | -0.009155 | 0.004578 | 0.004578 | 0.041199 | 0.21973 | 0.3067 | -0.37994 | 122.4655 | 0.073243 | 122.7997 | 122.8729 | -0.17853 | 122.5021 | 0.1236 | 0.33417 | 122.9233 | 123.1018 | 122.8867 | 123.1384 | 122.7997 | 123.1888 | 122.8867 | 122.5021 | 123.1384 | 122.7997 | 122.8867 | 122.8867 | 123.1888 | -0.59967 | -0.56305
4955.5469 | 123.143 | -122.8775 | 0.2243 | 0.12291 | 0.010921 | -0.010796 | 0.047078 | -0.020034 | -0.013612 | 0.0055713 | -0.082397 | 0.23804 | -0.41657 | -0.027466 | 0.004578 | 0.009155 | -0.013733 | 0.16937 | 0.32501 | -0.37537 | 122.4609 | 0.013733 | 122.7951 | 122.85 | -0.21973 | 122.5021 | 0.10071 | 0.33417 | 122.8638 | 123.0469 | 122.8821 | 123.1155 | 122.7951 | 123.2025 | 122.8867 | 122.5021 | 123.1155 | 122.7951 | 122.8867 | 122.8821 | 123.2025 | -0.64087 | -0.59967
4957.2344 | 123.1384 | -122.8958 | 0.20142 | 0.084762 | 0.011989 | -0.014214 | 0.044515 | -0.018538 | -0.01468 | 0.0055713 | -0.07782 | 0.25177 | -0.40283 | -0.045776 | -0.009155 | -0.009155 | 0.018311 | 0.16479 | 0.3067 | -0.36163 | 122.493 | 0.050354 | 122.818 | 122.85 | -0.21057 | 122.5342 | 0.10529 | 0.32501 | 122.9141 | 123.0606 | 122.8867 | 123.1476 | 122.818 | 123.2025 | 122.8867 | 122.5342 | 123.1476 | 122.818 | 122.8867 | 122.8867 | 123.2025 | -0.60425 | -0.56305
4958.9219 | 123.2208 | -122.85 | 0.17853 | -0.26619 | 0.010066 | -0.015283 | 0.039601 | -0.020247 | -0.014467 | 0.0055713 | -0.10529 | 0.26093 | -0.41199 | -0.013733 | 0 | 0.004578 | 0.050354 | 0.20142 | 0.31128 | -0.37994 | 122.4381 | 0.082397 | 122.7448 | 122.8363 | -0.17853 | 122.4701 | 0.13275 | 0.3067 | 122.9004 | 123.0515 | 122.85 | 123.111 | 122.7448 | 123.1613 | 122.8546 | 122.4701 | 123.111 | 122.7448 | 122.8546 | 122.85 | 123.1613 | -0.59052 | -0.55847
4960.625 | 123.1522 | -122.8592 | 0.21057 | 0.15343 | 0.0083569 | -0.012505 | 0.042165 | -0.017256 | -0.012758 | 0.0053577 | -0.10071 | 0.23804 | -0.41199 | -0.036621 | 0.022888 | 0.013733 | -0.009155 | 0.17395 | 0.31128 | -0.37079 | 122.4472 | 0.027466 | 122.7585 | 122.8226 | -0.18768 | 122.4884 | 0.10071 | 0.31128 | 122.85 | 123.0331 | 122.8821 | 123.0972 | 122.7585 | 123.1705 | 122.8729 | 122.4884 | 123.0972 | 122.7585 | 122.8729 | 122.8821 | 123.1705 | -0.62256 | -0.58136
4962.3281 | 123.1522 | -122.8775 | 0.22888 | 0.031357 | 0.0094251 | -0.01101 | 0.045156 | -0.01982 | -0.01468 | 0.0042895 | -0.082397 | 0.25635 | -0.39825 | -0.041199 | -0.009155 | 0.009155 | 0.009155 | 0.17395 | 0.31586 | -0.38452 | 122.4792 | 0.027466 | 122.7951 | 122.8363 | -0.23804 | 122.493 | 0.086975 | 0.31586 | 122.8867 | 123.0515 | 122.8683 | 123.1339 | 122.7951 | 123.1934 | 122.8867 | 122.493 | 123.1339 | 122.7951 | 122.8867 | 122.8683 | 123.1934 | -0.62714 | -0.6134
4964.0469 | 123.0789 | -122.8958 | 0.21057 | 0.19157 | 0.0079297 | -0.01336 | 0.039601 | -0.019606 | -0.010408 | 0.0040759 | 0.009155 | 0.19684 | -0.37994 | 0.07782 | 0.11444 | 0.14648 | -0.20142 | 0.30212 | 0.27008 | -0.32959 | 122.5159 | -0.013733 | 122.905 | 122.9736 | -0.09613 | 122.5662 | 0.05951 | 0.3891 | 122.6944 | 123.1979 | 123.0103 | 123.0927 | 122.905 | 123.1659 | 123.0423 | 122.5662 | 123.0927 | 122.905 | 123.0423 | 123.0103 | 123.1659 | -0.59052 | -0.54016
4965.7344 | 123.1476 | -122.8775 | 0.21973 | 0.054245 | 0.0094251 | -0.01101 | 0.042592 | -0.020461 | -0.012971 | 0.0051441 | -0.082397 | 0.24261 | -0.40741 | -0.036621 | -0.032043 | 0.009155 | 0 | 0.16937 | 0.30212 | -0.37079 | 122.4701 | 0.022888 | 122.7951 | 122.8409 | -0.25177 | 122.5067 | 0.082397 | 0.32501 | 122.8775 | 123.0469 | 122.8455 | 123.1201 | 122.7951 | 123.1796 | 122.8867 | 122.5067 | 123.1201 | 122.7951 | 122.8867 | 122.8455 | 123.1796 | -0.62714 | -0.59052
4967.4219 | 123.1522 | -122.8638 | 0.21973 | -0.1136 | 0.0092115 | -0.011865 | 0.044515 | -0.021743 | -0.015535 | 0.0049303 | -0.054932 | 0.24261 | -0.40741 | 0.018311 | 0.041199 | 0.059509 | 0.004578 | 0.24261 | 0.30212 | -0.35706 | 122.4564 | 0.022888 | 122.8088 | 122.8821 | -0.17853 | 122.5067 | 0.082397 | 0.35248 | 122.8683 | 123.1064 | 122.905 | 123.1064 | 122.8088 | 123.1659 | 122.9233 | 122.5067 | 123.1064 | 122.8088 | 122.9233 | 122.905 | 123.1659 | -0.62714 | -0.57678
4969.1406 | 123.2391 | -122.8638 | 0.20142 | -0.21278 | 0.0094251 | -0.013146 | 0.038961 | -0.01982 | -0.010194 | 0.0051441 | -0.10071 | 0.25635 | -0.39825 | -0.045776 | 0.009155 | 0.009155 | 0.064087 | 0.2243 | 0.33875 | -0.37079 | 122.4655 | 0.054932 | 122.7631 | 122.818 | -0.19226 | 122.493 | 0.13733 | 0.29755 | 122.9279 | 123.0881 | 122.8729 | 123.1201 | 122.7631 | 123.2025 | 122.8729 | 122.493 | 123.1201 | 122.7631 | 122.8729 | 122.8729 | 123.2025 | -0.59967 | -0.5722
4970.8281 | 123.2529 | -122.85 | 0.17853 | -0.28145 | 0.0089979 | -0.013574 | 0.041097 | -0.021102 | -0.012758 | 0.0062121 | -0.09613 | 0.27008 | -0.39825 | -0.041199 | 0.013733 | 0 | 0.059509 | 0.20599 | 0.32501 | -0.37537 | 122.4518 | 0.091553 | 122.7539 | 122.8088 | -0.16479 | 122.4747 | 0.14648 | 0.30212 | 122.9095 | 123.056 | 122.8638 | 123.1201 | 122.7539 | 123.175 | 122.85 | 122.4747 | 123.1201 | 122.7539 | 122.85 | 122.8638 | 123.175 | -0.57678 | -0.55389
4972.5156 | 123.2483 | -122.8592 | 0.19226 | -0.25856 | 0.010921 | -0.016778 | 0.04067 | -0.019606 | -0.014253 | 0.0038623 | -0.10986 | 0.27466 | -0.40283 | -0.018311 | 0.013733 | 0 | 0.054932 | 0.2243 | 0.32959 | -0.36621 | 122.4564 | 0.082397 | 122.7493 | 122.8409 | -0.17853 | 122.493 | 0.13733 | 0.29297 | 122.9141 | 123.0835 | 122.8729 | 123.1338 | 122.7493 | 123.1888 | 122.8592 | 122.493 | 123.1338 | 122.7493 | 122.8592 | 122.8729 | 123.1888 | -0.59509 | -0.55847
4974.2031 | 123.1796 | -122.8546 | 0.18768 | -0.22041 | 0.0077161 | -0.016137 | 0.03597 | -0.019179 | -0.012117 | 0.0038623 | 0.018311 | 0.20142 | -0.35706 | 0.086975 | 0.12817 | 0.13275 | -0.13275 | 0.37537 | 0.28839 | -0.31586 | 122.4976 | 0.013733 | 122.8729 | 122.9416 | -0.059509 | 122.5388 | 0.10071 | 0.37537 | 122.7219 | 123.23 | 122.9828 | 123.056 | 122.8729 | 123.143 | 122.9874 | 122.5388 | 123.056 | 122.8729 | 122.9874 | 122.9828 | 123.143 | -0.54474 | -0.50354
4975.8906 | 123.1842 | -122.8363 | 0.20599 | -0.098343 | 0.0092115 | -0.014642 | 0.037465 | -0.021529 | -0.011903 | 0.0051441 | 0.032043 | 0.22888 | -0.35248 | 0.10986 | 0.14191 | 0.16022 | -0.16479 | 0.37537 | 0.25635 | -0.34332 | 122.4838 | 0.022888 | 122.8683 | 122.9462 | -0.064087 | 122.493 | 0.050354 | 0.38452 | 122.6715 | 123.2117 | 122.9782 | 123.0652 | 122.8683 | 123.0927 | 122.9965 | 122.493 | 123.0652 | 122.8683 | 122.9965 | 122.9782 | 123.0927 | -0.55847 | -0.54932
4977.5938 | 123.1064 | -122.8867 | 0.21057 | 0.18394 | 0.0087841 | -0.01101 | 0.042379 | -0.021102 | -0.012971 | 0.0038623 | 0.018311 | 0.20599 | -0.37079 | 0.07782 | 0.091553 | 0.13275 | -0.19684 | 0.31128 | 0.27008 | -0.32959 | 122.5159 | -0.004577 | 122.905 | 122.9645 | -0.11902 | 122.5571 | 0.05951 | 0.3891 | 122.6898 | 123.1979 | 122.9782 | 123.0927 | 122.905 | 123.1567 | 123.0194 | 122.5571 | 123.0927 | 122.905 | 123.0194 | 122.9782 | 123.1567 | -0.58136 | -0.54016
4979.2812 | 123.2346 | -122.85 | 0.17853 | -0.18227 | 0.0075025 | -0.013574 | 0.04366 | -0.021102 | -0.013399 | 0.0049303 | -0.082397 | 0.25177 | -0.40741 | -0.009155 | 0.004578 | 0 | 0.041199 | 0.22888 | 0.32044 | -0.3891 | 122.4426 | 0.073242 | 122.7676 | 122.8409 | -0.17395 | 122.4609 | 0.14191 | 0.32501 | 122.8912 | 123.0789 | 122.8546 | 123.1018 | 122.7676 | 123.1705 | 122.85 | 122.4609 | 123.1018 | 122.7676 | 122.85 | 122.8546 | 123.1705 | -0.58594 | -0.56763
4981.0312 | 123.1613 | -122.8775 | 0.17395 | 0.10002 | 0.01028 | -0.008233 | 0.040029 | -0.017043 | -0.01169 | 0.0051441 | 0 | 0.2243 | -0.36163 | 0.054932 | 0.064087 | 0.10529 | -0.13733 | 0.27924 | 0.29297 | -0.32044 | 122.5159 | 0.050354 | 122.8775 | 122.9324 | -0.10986 | 122.5571 | 0.11902 | 0.36163 | 122.7402 | 123.1567 | 122.9416 | 123.1018 | 122.8775 | 123.1705 | 122.9828 | 122.5571 | 123.1018 | 122.8775 | 122.9828 | 122.9416 | 123.1705 | -0.53558 | -0.49439
4982.7344 | 123.0972 | -122.8455 | 0.21057 | 0.18394 | 0.0072889 | -0.0080194 | 0.046224 | -0.018752 | -0.01233 | 0.0032215 | 0.045776 | 0.21057 | -0.38452 | 0.10986 | 0.11444 | 0.14648 | -0.21057 | 0.31128 | 0.2655 | -0.32501 | 122.4609 | 0 | 122.8912 | 122.9553 | -0.09613 | 122.5204 | 0.054932 | 0.4303 | 122.6349 | 123.1567 | 122.9599 | 123.056 | 122.8912 | 123.111 | 122.9919 | 122.5204 | 123.056 | 122.8912 | 122.9919 | 122.9599 | 123.111 | -0.59509 | -0.53558
4984.4844 | 123.2529 | -122.85 | 0.17395 | -0.22804 | 0.0096387 | -0.012933 | 0.042806 | -0.023238 | -0.01169 | 0.0047167 | -0.086975 | 0.27008 | -0.39825 | -0.013733 | 0.018311 | -0.018311 | 0.054932 | 0.21515 | 0.31586 | -0.3891 | 122.4518 | 0.096131 | 122.7631 | 122.8363 | -0.15564 | 122.4609 | 0.14191 | 0.31128 | 122.905 | 123.0652 | 122.8683 | 123.1201 | 122.7631 | 123.1659 | 122.8317 | 122.4609 | 123.1201 | 122.7631 | 122.8317 | 122.8683 | 123.1659 | -0.5722 | -0.56305
4986.1719 | 123.2254 | -122.8226 | 0.19226 | -0.26619 | 0.0085705 | -0.015283 | 0.042379 | -0.021529 | -0.013826 | 0.0059985 | -0.07782 | 0.24719 | -0.42114 | -0.009155 | 0.022888 | -0.004578 | 0.045776 | 0.19226 | 0.31586 | -0.35706 | 122.4014 | 0.054931 | 122.7448 | 122.8134 | -0.16937 | 122.4655 | 0.1236 | 0.34332 | 122.8683 | 123.0148 | 122.8455 | 123.0698 | 122.7448 | 123.1384 | 122.818 | 122.4655 | 123.0698 | 122.7448 | 122.818 | 122.8455 | 123.1384 | -0.6134 | -0.54932
4987.875 | 123.1338 | -122.8775 | 0.20599 | 0.10002 | 0.010493 | -0.012505 | 0.04366 | -0.019606 | -0.013612 | 0.0068531 | -0.068665 | 0.24719 | -0.41199 | -0.013733 | 0.004578 | 0 | -0.045776 | 0.1831 | 0.31128 | -0.37994 | 122.4655 | 0.041198 | 122.8088 | 122.8638 | -0.20142 | 122.4976 | 0.10528 | 0.34332 | 122.8317 | 123.0606 | 122.8821 | 123.1247 | 122.8088 | 123.1888 | 122.8775 | 122.4976 | 123.1247 | 122.8088 | 122.8775 | 122.8821 | 123.1888 | -0.61798 | -0.58594
4989.5781 | 123.2391 | -122.8455 | 0.19684 | -0.23567 | 0.0089979 | -0.008233 | 0.039388 | -0.020034 | -0.012544 | 0.0027941 | -0.045776 | 0.2655 | -0.37994 | -0.009155 | 0.027466 | 0.022888 | 0.036621 | 0.22888 | 0.32501 | -0.37079 | 122.4655 | 0.068665 | 122.7997 | 122.8363 | -0.16937 | 122.4747 | 0.12817 | 0.33417 | 122.8821 | 123.0743 | 122.8729 | 123.111 | 122.7997 | 123.1705 | 122.8683 | 122.4747 | 123.111 | 122.7997 | 122.8683 | 122.8729 | 123.1705 | -0.57678 | -0.56763
4991.2812 | 123.0972 | -122.8867 | 0.21515 | 0.16869 | 0.01028 | -0.014001 | 0.044088 | -0.021102 | -0.01233 | 0.0047167 | 0.018311 | 0.2243 | -0.36163 | 0.073242 | 0.10986 | 0.13275 | -0.1831 | 0.28381 | 0.27008 | -0.33417 | 122.525 | 0.009155 | 122.905 | 122.9599 | -0.10529 | 122.5525 | 0.054932 | 0.37994 | 122.7036 | 123.1705 | 122.9965 | 123.111 | 122.905 | 123.1567 | 123.0194 | 122.5525 | 123.111 | 122.905 | 123.0194 | 122.9965 | 123.1567 | -0.57678 | -0.54932
4993.0312 | 123.2208 | -122.8271 | 0.18768 | -0.01442 | 0.0087841 | -0.011437 | 0.037038 | -0.020888 | -0.011262 | 0.0034351 | -0.041199 | 0.24719 | -0.37537 | 0.059509 | 0.091553 | 0.10071 | -0.11902 | 0.29297 | 0.30212 | -0.33875 | 122.4518 | 0.059509 | 122.7859 | 122.8867 | -0.09613 | 122.4884 | 0.11444 | 0.33417 | 122.7081 | 123.1201 | 122.9187 | 123.0743 | 122.7859 | 123.1293 | 122.9279 | 122.4884 | 123.0743 | 122.7859 | 122.9279 | 122.9187 | 123.1293 | -0.56305 | -0.52643
4994.7188 | 123.143 | -122.8867 | 0.21057 | 0.11528 | 0.0085705 | -0.014855 | 0.041738 | -0.01982 | -0.013612 | 0.0027941 | 0.013733 | 0.20599 | -0.36621 | 0.068665 | 0.10071 | 0.10986 | -0.1831 | 0.28839 | 0.27924 | -0.32959 | 122.5204 | -0.004577 | 122.9004 | 122.9553 | -0.10986 | 122.5571 | 0.068665 | 0.37994 | 122.7036 | 123.175 | 122.9874 | 123.0927 | 122.9004 | 123.1659 | 122.9965 | 122.5571 | 123.0927 | 122.9004 | 122.9965 | 122.9874 | 123.1659 | -0.57678 | -0.54016
4996.4219 | 123.23 | -122.8546 | 0.19684 | -0.0067901 | 0.01028 | -0.011865 | 0.037679 | -0.021956 | -0.013185 | 0.0051441 | -0.032043 | 0.23346 | -0.37537 | 0.036621 | 0.068665 | 0.07782 | -0.11444 | 0.27924 | 0.28381 | -0.33417 | 122.4792 | 0.036621 | 122.8226 | 122.8912 | -0.12817 | 122.5204 | 0.086975 | 0.34332 | 122.7402 | 123.1338 | 122.9233 | 123.0881 | 122.8226 | 123.1384 | 122.9324 | 122.5204 | 123.0881 | 122.8226 | 122.9324 | 122.9233 | 123.1384 | -0.5722 | -0.531
4998.125 | 123.0881 | -122.8821 | 0.2243 | 0.18394 | 0.0089979 | -0.010156 | 0.046224 | -0.020674 | -0.011049 | 0.0059985 | 0.027466 | 0.21057 | -0.3891 | 0.10071 | 0.11444 | 0.14648 | -0.20599 | 0.30212 | 0.27924 | -0.32959 | 122.493 | -0.013733 | 122.9095 | 122.9828 | -0.10986 | 122.5525 | 0.054932 | 0.41656 | 122.6761 | 123.1842 | 122.9965 | 123.0927 | 122.9095 | 123.1613 | 123.0286 | 122.5525 | 123.0927 | 122.9095 | 123.0286 | 122.9965 | 123.1613 | -0.6134 | -0.55389
4999.8125 | 123.0835 | -122.8867 | 0.19684 | 0.17632 | 0.0089979 | -0.013574 | 0.044301 | -0.020461 | -0.012971 | 0.0059985 | 0.027466 | 0.21057 | -0.36163 | 0.09613 | 0.10529 | 0.14648 | -0.21973 | 0.3067 | 0.27466 | -0.33875 | 122.525 | 0.013733 | 122.9141 | 122.9828 | -0.091552 | 122.5479 | 0.07782 | 0.3891 | 122.6669 | 123.1934 | 122.9919 | 123.0972 | 122.9141 | 123.1613 | 123.0331 | 122.5479 | 123.0972 | 122.9141 | 123.0331 | 122.9919 | 123.1613 | -0.55847 | -0.53558
5001.5 | 123.1155 | -122.8775 | 0.21057 | 0.18394 | 0.0081433 | -0.01101 | 0.043447 | -0.019606 | -0.013185 | 0.0027941 | -0.009155 | 0.21973 | -0.3891 | 0.07782 | 0.082397 | 0.11444 | -0.16937 | 0.28381 | 0.27924 | -0.34332 | 122.4884 | 0.009156 | 122.8683 | 122.9553 | -0.12817 | 122.5342 | 0.068665 | 0.37994 | 122.7081 | 123.1613 | 122.9599 | 123.0972 | 122.8683 | 123.1567 | 122.9919 | 122.5342 | 123.0972 | 122.8683 | 122.9919 | 122.9599 | 123.1567 | -0.59967 | -0.55389
5003.2188 | 123.2071 | -122.8409 | 0.1831 | 0.031357 | 0.0062207 | -0.010583 | 0.038533 | -0.023024 | -0.013399 | 0.0047167 | -0.050354 | 0.21515 | -0.34332 | 0.032043 | 0.073242 | 0.082397 | -0.1236 | 0.26093 | 0.29297 | -0.3479 | 122.4976 | 0.032044 | 122.7905 | 122.8729 | -0.10986 | 122.493 | 0.10986 | 0.29297 | 122.7173 | 123.1018 | 122.9141 | 123.056 | 122.7905 | 123.1338 | 122.9233 | 122.493 | 123.056 | 122.7905 | 122.9233 | 122.9141 | 123.1338 | -0.52643 | -0.531
5004.9688 | 123.2483 | -122.85 | 0.19684 | -0.19753 | 0.0092115 | -0.010796 | 0.041097 | -0.021529 | -0.013185 | 0.0040759 | -0.068665 | 0.2655 | -0.3891 | -0.013733 | 0.013733 | -0.004578 | 0.041199 | 0.23346 | 0.31128 | -0.37537 | 122.4609 | 0.068665 | 122.7814 | 122.8363 | -0.18311 | 122.4747 | 0.11444 | 0.32043 | 122.8912 | 123.0835 | 122.8638 | 123.1155 | 122.7814 | 123.1613 | 122.8455 | 122.4747 | 123.1155 | 122.7814 | 122.8455 | 122.8638 | 123.1613 | -0.58594 | -0.5722
5006.7031 | 123.1796 | -122.8409 | 0.19684 | -0.23567 | 0.0087841 | -0.013787 | 0.039815 | -0.020461 | -0.011476 | 0.0034351 | 0.036621 | 0.21515 | -0.34332 | 0.09613 | 0.12817 | 0.13275 | -0.1236 | 0.35248 | 0.27008 | -0.3479 | 122.4976 | 0.018311 | 122.8775 | 122.937 | -0.068664 | 122.493 | 0.073243 | 0.37994 | 122.7173 | 123.1934 | 122.9691 | 123.056 | 122.8775 | 123.111 | 122.9736 | 122.493 | 123.056 | 122.8775 | 122.9736 | 122.9691 | 123.111 | -0.54016 | -0.54474
5008.4844 | 123.1018 | -122.9004 | 0.22888 | 0.18394 | 0.011775 | -0.015923 | 0.046224 | -0.019606 | -0.011049 | 0.0049303 | 0.032043 | 0.2243 | -0.37537 | 0.086975 | 0.10071 | 0.1236 | -0.1831 | 0.27924 | 0.27008 | -0.31586 | 122.525 | -0.004578 | 122.9324 | 122.9874 | -0.12817 | 122.5845 | 0.041199 | 0.40741 | 122.7173 | 123.1796 | 123.0011 | 123.1247 | 122.9324 | 123.1705 | 123.024 | 122.5845 | 123.1247 | 122.9324 | 123.024 | 123.0011 | 123.1705 | -0.60425 | -0.54474
5010.25 | 123.1384 | -122.8867 | 0.19226 | 0.17632 | 0.0096387 | -0.012719 | 0.044728 | -0.021743 | -0.012758 | 0.0049303 | -0.045776 | 0.23804 | -0.3891 | 0.022888 | 0.022888 | 0.045776 | -0.10071 | 0.22888 | 0.29755 | -0.3479 | 122.4976 | 0.045776 | 122.8409 | 122.9095 | -0.16937 | 122.5388 | 0.10528 | 0.34332 | 122.7859 | 123.1155 | 122.9095 | 123.1247 | 122.8409 | 123.1842 | 122.9324 | 122.5388 | 123.1247 | 122.8409 | 122.9324 | 122.9095 | 123.1842 | -0.58136 | -0.54016
5012.0156 | 123.1613 | -122.8867 | 0.20142 | 0.13817 | 0.0092115 | -0.01336 | 0.045797 | -0.019179 | -0.014467 | 0.0047167 | -0.086975 | 0.25177 | -0.39368 | -0.013733 | 0.009155 | 0.009155 | -0.022888 | 0.17853 | 0.3067 | -0.36163 | 122.493 | 0.050354 | 122.7997 | 122.8729 | -0.19226 | 122.525 | 0.10529 | 0.3067 | 122.8638 | 123.0652 | 122.8958 | 123.1384 | 122.7997 | 123.1934 | 122.8958 | 122.525 | 123.1384 | 122.7997 | 122.8958 | 122.8958 | 123.1934 | -0.59509 | -0.56305
5013.7812 | 123.1979 | -122.8775 | 0.17395 | -0.15938 | 0.0085705 | -0.017846 | 0.035543 | -0.02217 | -0.010194 | 0.0051441 | 0.013733 | 0.23346 | -0.36163 | 0.09613 | 0.14191 | 0.15106 | -0.16022 | 0.35706 | 0.27008 | -0.32959 | 122.5159 | 0.059509 | 122.8912 | 122.9736 | -0.032043 | 122.5479 | 0.096131 | 0.37537 | 122.7173 | 123.2346 | 123.0194 | 123.111 | 122.8912 | 123.1476 | 123.0286 | 122.5479 | 123.111 | 122.8912 | 123.0286 | 123.0194 | 123.1476 | -0.53558 | -0.50354
5015.5312 | 123.2437 | -122.8867 | 0.20142 | -0.25093 | 0.0094251 | -0.012292 | 0.041524 | -0.020461 | -0.012117 | 0.0040759 | -0.050354 | 0.2655 | -0.39368 | -0.009155 | 0.032043 | 0.013733 | 0.018311 | 0.21973 | 0.31586 | -0.35706 | 122.493 | 0.064087 | 122.8363 | 122.8775 | -0.16937 | 122.5296 | 0.11444 | 0.34332 | 122.905 | 123.1064 | 122.9187 | 123.1522 | 122.8363 | 123.2025 | 122.9004 | 122.5296 | 123.1522 | 122.8363 | 122.9004 | 122.9187 | 123.2025 | -0.59509 | -0.55847
5017.2188 | 123.1064 | -122.9095 | 0.23346 | -0.075455 | 0.0096387 | -0.013146 | 0.04836 | -0.018538 | -0.013612 | 0.0057849 | 0.004578 | 0.24719 | -0.40283 | 0.045776 | 0.032043 | 0.059509 | -0.050354 | 0.23804 | 0.31128 | -0.36163 | 122.5067 | 0.013733 | 122.9141 | 122.9553 | -0.20142 | 122.5479 | 0.07782 | 0.40741 | 122.8592 | 123.1476 | 122.9416 | 123.1567 | 122.9141 | 123.2208 | 122.9691 | 122.5479 | 123.1567 | 122.9141 | 122.9691 | 122.9416 | 123.2208 | -0.63629 | -0.59509
5018.9531 | 123.1064 | -122.8821 | 0.19684 | 0.19157 | 0.0077161 | -0.010583 | 0.040242 | -0.020461 | -0.01169 | 0.0081347 | 0.013733 | 0.21515 | -0.35248 | 0.09613 | 0.10986 | 0.14191 | -0.18768 | 0.3067 | 0.2655 | -0.33417 | 122.5296 | 0.018311 | 122.8958 | 122.9782 | -0.086975 | 122.5479 | 0.068665 | 0.36621 | 122.6944 | 123.1888 | 122.9919 | 123.0972 | 122.8958 | 123.1476 | 123.024 | 122.5479 | 123.0972 | 122.8958 | 123.024 | 122.9919 | 123.1476 | -0.54932 | -0.531
5020.7031 | 123.0881 | -122.8867 | 0.21515 | 0.17632 | 0.010066 | -0.010796 | 0.043233 | -0.018538 | -0.014467 | 0.0062121 | 0.004578 | 0.21973 | -0.36621 | 0.073242 | 0.10986 | 0.13275 | -0.17395 | 0.29297 | 0.28381 | -0.33875 | 122.5204 | 0.004578 | 122.8912 | 122.9599 | -0.10529 | 122.5479 | 0.068664 | 0.37079 | 122.7127 | 123.1796 | 122.9965 | 123.1064 | 122.8912 | 123.1705 | 123.0194 | 122.5479 | 123.1064 | 122.8912 | 123.0194 | 122.9965 | 123.1705 | -0.58136 | -0.55389
5022.4062 | 123.2346 | -122.85 | 0.17853 | 0.023727 | 0.0094251 | -0.016351 | 0.039174 | -0.020034 | -0.010621 | 0.0051441 | -0.045776 | 0.23346 | -0.37079 | 0.054932 | 0.091553 | 0.10986 | -0.11444 | 0.3067 | 0.28381 | -0.35706 | 122.4792 | 0.054931 | 122.8043 | 122.905 | -0.086975 | 122.493 | 0.10528 | 0.32501 | 122.7356 | 123.1567 | 122.9416 | 123.0835 | 122.8043 | 123.1338 | 122.9599 | 122.493 | 123.0835 | 122.8043 | 122.9599 | 122.9416 | 123.1338 | -0.54932 | -0.53558
5024.1562 | 123.1338 | -122.8775 | 0.21973 | -0.12886 | 0.010921 | -0.012078 | 0.045583 | -0.018965 | -0.01468 | 0.0047167 | -0.027466 | 0.24719 | -0.40741 | 0.027466 | 0.054932 | 0.045776 | -0.036621 | 0.24261 | 0.30212 | -0.36621 | 122.4701 | 0.027465 | 122.85 | 122.905 | -0.16479 | 122.5113 | 0.082397 | 0.37994 | 122.8409 | 123.1201 | 122.9324 | 123.1247 | 122.85 | 123.1796 | 122.9233 | 122.5113 | 123.1247 | 122.85 | 122.9233 | 122.9324 | 123.1796 | -0.62714 | -0.58594
5025.8594 | 123.1247 | -122.8775 | 0.21515 | -0.0067901 | 0.0098523 | -0.014855 | 0.047078 | -0.019393 | -0.015535 | 0.0053577 | -0.022888 | 0.24719 | -0.40283 | -0.004578 | 0.009155 | 0.018311 | -0.018311 | 0.19684 | 0.32044 | -0.35248 | 122.4747 | 0.032043 | 122.8546 | 122.8729 | -0.20599 | 122.525 | 0.10529 | 0.37994 | 122.8592 | 123.0743 | 122.8867 | 123.1247 | 122.8546 | 123.1979 | 122.8958 | 122.525 | 123.1247 | 122.8546 | 122.8958 | 122.8867 | 123.1979 | -0.61798 | -0.56763
5027.625 | 123.2162 | -122.8592 | 0.18768 | -0.20515 | 0.0089979 | -0.0093012 | 0.041951 | -0.018752 | -0.013612 | 0.0045031 | -0.064087 | 0.27466 | -0.39368 | 0.004578 | 0.032043 | 0.022888 | 0.018311 | 0.22888 | 0.32501 | -0.35248 | 122.4655 | 0.086975 | 122.7951 | 122.8638 | -0.15564 | 122.5067 | 0.13733 | 0.32959 | 122.8775 | 123.0881 | 122.8912 | 123.1338 | 122.7951 | 123.1842 | 122.8821 | 122.5067 | 123.1338 | 122.7951 | 122.8821 | 122.8912 | 123.1842 | -0.58136 | -0.54016
5029.3281 | 123.2254 | -122.818 | 0.17853 | 0.031357 | 0.0087841 | -0.01336 | 0.039174 | -0.021315 | -0.015107 | 0.0042895 | -0.032043 | 0.24261 | -0.36163 | 0.032043 | 0.09613 | 0.09613 | -0.13275 | 0.29297 | 0.28381 | -0.35248 | 122.4564 | 0.064087 | 122.7859 | 122.85 | -0.082398 | 122.4655 | 0.10528 | 0.32959 | 122.6852 | 123.111 | 122.9141 | 123.0606 | 122.7859 | 123.1018 | 122.9141 | 122.4655 | 123.0606 | 122.7859 | 122.9141 | 122.9141 | 123.1018 | -0.54016 | -0.53101
5031.0156 | 123.23 | -122.8455 | 0.1831 | 0.023727 | 0.0083569 | -0.014214 | 0.039174 | -0.02217 | -0.0086987 | 0.0036487 | -0.032043 | 0.24719 | -0.36163 | 0.054932 | 0.073242 | 0.091553 | -0.11444 | 0.27924 | 0.28381 | -0.35706 | 122.4838 | 0.064087 | 122.8134 | 122.9004 | -0.10986 | 122.4884 | 0.10071 | 0.32959 | 122.731 | 123.1247 | 122.9187 | 123.0927 | 122.8134 | 123.1293 | 122.937 | 122.4884 | 123.0927 | 122.8134 | 122.937 | 122.9187 | 123.1293 | -0.54474 | -0.54016
5032.7188 | 123.1888 | -122.8546 | 0.20142 | -0.19753 | 0.0057935 | -0.014642 | 0.039815 | -0.020461 | -0.01233 | 0.0032215 | 0.009155 | 0.2243 | -0.3479 | 0.091553 | 0.11444 | 0.11902 | -0.10986 | 0.3479 | 0.28381 | -0.32501 | 122.5067 | 0.022888 | 122.8638 | 122.9462 | -0.086975 | 122.5296 | 0.082397 | 0.35706 | 122.7448 | 123.2025 | 122.9691 | 123.0789 | 122.8638 | 123.1384 | 122.9736 | 122.5296 | 123.0789 | 122.8638 | 122.9736 | 122.9691 | 123.1384 | -0.54932 | -0.52643
5034.4219 | 123.1293 | -122.8912 | 0.21515 | 0.12291 | 0.0070751 | -0.0067376 | 0.043233 | -0.021529 | -0.013185 | 0.0057849 | 0.027466 | 0.19684 | -0.34332 | 0.064087 | 0.09613 | 0.11444 | -0.18768 | 0.30212 | 0.27466 | -0.32959 | 122.5479 | -0.018311 | 122.9187 | 122.9553 | -0.11902 | 122.5616 | 0.059509 | 0.37079 | 122.7036 | 123.1934 | 122.9874 | 123.0881 | 122.9187 | 123.1659 | 123.0057 | 122.5616 | 123.0881 | 122.9187 | 123.0057 | 122.9874 | 123.1659 | -0.55847 | -0.54474
5036.1719 | 123.23 | -122.8409 | 0.16937 | -0.022049 | 0.010707 | -0.012505 | 0.03832 | -0.020674 | -0.011049 | 0.0059985 | -0.009155 | 0.24261 | -0.36163 | 0.082397 | 0.10529 | 0.11444 | -0.1236 | 0.32501 | 0.28381 | -0.35248 | 122.4792 | 0.073242 | 122.8317 | 122.9233 | -0.064087 | 122.4884 | 0.11444 | 0.35248 | 122.7173 | 123.1659 | 122.9462 | 123.0835 | 122.8317 | 123.1247 | 122.9553 | 122.4884 | 123.0835 | 122.8317 | 122.9553 | 122.9462 | 123.1247 | -0.53101 | -0.52185
5037.8594 | 123.1064 | -122.9004 | 0.2243 | -0.067826 | 0.010707 | -0.014855 | 0.046224 | -0.01982 | -0.013612 | 0.0036487 | -0.004578 | 0.24261 | -0.40283 | 0.036621 | 0.027466 | 0.059509 | -0.036621 | 0.24719 | 0.31128 | -0.35706 | 122.4976 | 0.018311 | 122.8958 | 122.937 | -0.19684 | 122.5433 | 0.086975 | 0.39825 | 122.8638 | 123.1476 | 122.9279 | 123.143 | 122.8958 | 123.2117 | 122.9599 | 122.5433 | 123.143 | 122.8958 | 122.9599 | 122.9279 | 123.2117 | -0.62714 | -0.58136
5039.625 | 123.2437 | -122.8592 | 0.19226 | -0.27382 | 0.0077161 | -0.014855 | 0.043447 | -0.019606 | -0.013399 | 0.0055713 | -0.086975 | 0.28381 | -0.41199 | -0.004578 | 0.018311 | -0.004578 | 0.054932 | 0.21057 | 0.32959 | -0.3891 | 122.4472 | 0.091552 | 122.7722 | 122.8546 | -0.17395 | 122.4701 | 0.13733 | 0.32501 | 122.9141 | 123.0698 | 122.8775 | 123.143 | 122.7722 | 123.1888 | 122.8546 | 122.4701 | 123.143 | 122.7722 | 122.8546 | 122.8775 | 123.1888 | -0.60425 | -0.58136
5041.3906 | 123.2437 | -122.8409 | 0.17853 | -0.22804 | 0.0089979 | -0.017632 | 0.040883 | -0.023665 | -0.012758 | 0.0066393 | -0.068665 | 0.27466 | -0.39825 | -0.009155 | 0.018311 | 0.009155 | 0.027466 | 0.22888 | 0.32501 | -0.37537 | 122.4426 | 0.09613 | 122.7722 | 122.8317 | -0.16022 | 122.4655 | 0.14648 | 0.32959 | 122.8683 | 123.0698 | 122.8592 | 123.1155 | 122.7722 | 123.1659 | 122.85 | 122.4655 | 123.1155 | 122.7722 | 122.85 | 122.8592 | 123.1659 | -0.57678 | -0.55389
5043.1562 | 123.0972 | -122.9141 | 0.21515 | -0.052567 | 0.0085705 | -0.0084466 | 0.045797 | -0.019606 | -0.01233 | 0.0047167 | -0.013733 | 0.24261 | -0.38452 | 0.018311 | 0.027466 | 0.050354 | -0.013733 | 0.21057 | 0.3067 | -0.37537 | 122.5296 | 0.027466 | 122.9004 | 122.9324 | -0.18768 | 122.5388 | 0.091553 | 0.37079 | 122.9004 | 123.1247 | 122.9416 | 123.1567 | 122.9004 | 123.2208 | 122.9645 | 122.5388 | 123.1567 | 122.9004 | 122.9645 | 122.9416 | 123.2208 | -0.59967 | -0.59052
5044.8594 | 123.1796 | -122.8775 | 0.16937 | 0.10002 | 0.0085705 | -0.016778 | 0.037892 | -0.020888 | -0.011476 | 0.0042895 | -0.018311 | 0.21973 | -0.34332 | 0.054932 | 0.086975 | 0.091553 | -0.13275 | 0.28381 | 0.29297 | -0.35248 | 122.5342 | 0.050354 | 122.8592 | 122.9324 | -0.082398 | 122.525 | 0.1236 | 0.32501 | 122.7448 | 123.1613 | 122.9645 | 123.0972 | 122.8592 | 123.1705 | 122.9691 | 122.525 | 123.0972 | 122.8592 | 122.9691 | 122.9645 | 123.1705 | -0.5127 | -0.52185
5046.6094 | 123.1522 | -122.8271 | 0.19684 | 0.17632 | 0.0094251 | -0.018487 | 0.04131 | -0.02217 | -0.011262 | 0.0051441 | -0.009155 | 0.21973 | -0.37994 | 0.059509 | 0.07782 | 0.10071 | -0.15564 | 0.28839 | 0.27924 | -0.34332 | 122.4472 | 0.022889 | 122.818 | 122.8867 | -0.11902 | 122.4838 | 0.082398 | 0.37079 | 122.6715 | 123.1155 | 122.905 | 123.0469 | 122.818 | 123.1064 | 122.9279 | 122.4838 | 123.0469 | 122.818 | 122.9279 | 122.905 | 123.1064 | -0.57678 | -0.54016
5048.2969 | 123.2437 | -122.8134 | 0.18768 | 0.031357 | 0.0085705 | -0.017632 | 0.039174 | -0.021529 | -0.010621 | 0.0032215 | -0.041199 | 0.25177 | -0.36163 | 0.045776 | 0.07782 | 0.10071 | -0.11902 | 0.29297 | 0.30212 | -0.3479 | 122.4518 | 0.064087 | 122.7722 | 122.8592 | -0.10986 | 122.4655 | 0.11444 | 0.32043 | 122.6944 | 123.1064 | 122.8912 | 123.0652 | 122.7722 | 123.1155 | 122.9141 | 122.4655 | 123.0652 | 122.7722 | 122.9141 | 122.8912 | 123.1155 | -0.54932 | -0.53558
5050.0625 | 123.2346 | -122.85 | 0.1831 | -0.27382 | 0.011561 | -0.014214 | 0.044088 | -0.022811 | -0.012758 | 0.0027941 | -0.086975 | 0.27924 | -0.3891 | 0 | 0.009155 | -0.009155 | 0.054932 | 0.21515 | 0.32044 | -0.39368 | 122.4609 | 0.096131 | 122.7631 | 122.85 | -0.17395 | 122.4564 | 0.13733 | 0.30212 | 122.905 | 123.0652 | 122.8592 | 123.1293 | 122.7631 | 123.1705 | 122.8409 | 122.4564 | 123.1293 | 122.7631 | 122.8409 | 122.8592 | 123.1705 | -0.5722 | -0.57678
5051.8125 | 123.1613 | -122.8775 | 0.20599 | -0.14412 | 0.0096387 | -0.012292 | 0.04601 | -0.01982 | -0.015321 | 0.0051441 | -0.018311 | 0.26093 | -0.41199 | 0.045776 | 0.032043 | 0.041199 | -0.022888 | 0.24261 | 0.3067 | -0.36621 | 122.4655 | 0.054931 | 122.8592 | 122.9233 | -0.17395 | 122.5113 | 0.10071 | 0.39368 | 122.8546 | 123.1201 | 122.9095 | 123.1384 | 122.8592 | 123.1842 | 122.9187 | 122.5113 | 123.1384 | 122.8592 | 122.9187 | 122.9095 | 123.1842 | -0.61798 | -0.57221
5053.5156 | 123.2254 | -122.8363 | 0.16937 | 0.023727 | 0.0085705 | -0.012505 | 0.038106 | -0.020674 | -0.012544 | 0.0040759 | -0.027466 | 0.23346 | -0.37079 | 0.036621 | 0.073242 | 0.086975 | -0.11902 | 0.27466 | 0.28839 | -0.3479 | 122.4655 | 0.064086 | 122.8088 | 122.8729 | -0.096131 | 122.4884 | 0.11902 | 0.34332 | 122.7173 | 123.111 | 122.9095 | 123.0698 | 122.8088 | 123.1247 | 122.9233 | 122.4884 | 123.0698 | 122.8088 | 122.9233 | 122.9095 | 123.1247 | -0.54016 | -0.51727
5055.2812 | 123.1476 | -122.8683 | 0.20599 | 0.13054 | 0.0085705 | -0.014214 | 0.046437 | -0.020888 | -0.015107 | 0.0051441 | -0.054932 | 0.25635 | -0.39825 | -0.022888 | 0.004578 | 0.009155 | -0.050354 | 0.1831 | 0.32501 | -0.35248 | 122.4701 | 0.050354 | 122.8134 | 122.8455 | -0.20142 | 122.5159 | 0.11902 | 0.34332 | 122.818 | 123.0515 | 122.8729 | 123.1247 | 122.8134 | 123.1934 | 122.8775 | 122.5159 | 123.1247 | 122.8134 | 122.8775 | 122.8729 | 123.1934 | -0.60425 | -0.55847
5057.0312 | 123.0972 | -122.8729 | 0.2243 | 0.20683 | 0.0089979 | -0.013787 | 0.042806 | -0.020461 | -0.0097669 | 0.0064257 | -0.009155 | 0.24261 | -0.37079 | 0.064087 | 0.091553 | 0.09613 | -0.16022 | 0.27924 | 0.28381 | -0.33875 | 122.5021 | 0.018311 | 122.8638 | 122.937 | -0.13275 | 122.5342 | 0.059509 | 0.36163 | 122.7127 | 123.1522 | 122.9645 | 123.1155 | 122.8638 | 123.1567 | 122.9691 | 122.5342 | 123.1155 | 122.8638 | 122.9691 | 122.9645 | 123.1567 | -0.59509 | -0.56305
5058.7969 | 123.1888 | -122.8546 | 0.18768 | -0.10597 | 0.0094251 | -0.014428 | 0.039174 | -0.021529 | -0.011049 | 0.0055713 | 0 | 0.23804 | -0.36621 | 0.086975 | 0.13275 | 0.14648 | -0.15106 | 0.32959 | 0.27466 | -0.34332 | 122.4884 | 0.050354 | 122.8546 | 122.9416 | -0.054932 | 122.5113 | 0.086975 | 0.36621 | 122.7036 | 123.1842 | 122.9874 | 123.0927 | 122.8546 | 123.1293 | 123.0011 | 122.5113 | 123.0927 | 122.8546 | 123.0011 | 122.9874 | 123.1293 | -0.55389 | -0.53101
5060.5625 | 123.2117 | -122.8455 | 0.19226 | -0.19753 | 0.0077161 | -0.0090874 | 0.045156 | -0.018965 | -0.012117 | 0.0040759 | -0.064087 | 0.29297 | -0.37994 | 0.004578 | 0.022888 | 0.013733 | 0.027466 | 0.21973 | 0.32959 | -0.3891 | 122.4655 | 0.10071 | 122.7814 | 122.85 | -0.16937 | 122.4564 | 0.13733 | 0.31586 | 122.8729 | 123.0652 | 122.8683 | 123.1384 | 122.7814 | 123.175 | 122.8592 | 122.4564 | 123.1384 | 122.7814 | 122.8592 | 122.8683 | 123.175 | -0.5722 | -0.58136
5062.25 | 123.1155 | -122.8912 | 0.22888 | -0.12123 | 0.010707 | -0.016351 | 0.044515 | -0.018538 | -0.014894 | 0.0053577 | -0.032043 | 0.27466 | -0.3891 | 0.032043 | 0.041199 | 0.045776 | -0.032043 | 0.25177 | 0.3067 | -0.35706 | 122.5021 | 0.045776 | 122.8592 | 122.9233 | -0.18768 | 122.5342 | 0.07782 | 0.35706 | 122.8592 | 123.143 | 122.9324 | 123.1659 | 122.8592 | 123.1979 | 122.937 | 122.5342 | 123.1659 | 122.8592 | 122.937 | 122.9324 | 123.1979 | -0.61798 | -0.58594
5064 | 123.1018 | -122.8592 | 0.21515 | -0.052567 | 0.0072889 | -0.013574 | 0.044301 | -0.019606 | -0.012758 | 0.0066393 | -0.009155 | 0.27008 | -0.3891 | 0.013733 | 0.041199 | 0.036621 | -0.036621 | 0.22888 | 0.28839 | -0.3479 | 122.4701 | 0.054932 | 122.85 | 122.8729 | -0.17395 | 122.5113 | 0.073242 | 0.37994 | 122.8226 | 123.0881 | 122.9004 | 123.1293 | 122.85 | 123.1476 | 122.8958 | 122.5113 | 123.1293 | 122.85 | 122.8958 | 122.9004 | 123.1476 | -0.60425 | -0.56305
5065.75 | 123.143 | -122.8729 | 0.21973 | 0.15343 | 0.010493 | -0.01336 | 0.044728 | -0.021743 | -0.013612 | 0.0070667 | -0.082397 | 0.24719 | -0.37537 | -0.022888 | -0.004578 | 0.013733 | -0.022888 | 0.1831 | 0.3067 | -0.37079 | 122.4976 | 0.027465 | 122.7905 | 122.85 | -0.22431 | 122.5021 | 0.086975 | 0.29297 | 122.85 | 123.056 | 122.8683 | 123.1201 | 122.7905 | 123.1796 | 122.8867 | 122.5021 | 123.1201 | 122.7905 | 122.8867 | 122.8683 | 123.1796 | -0.59509 | -0.59052
5067.5 | 123.1567 | -122.8729 | 0.21515 | 0.16106 | 0.0092115 | -0.010796 | 0.044301 | -0.018111 | -0.011262 | 0.0049303 | -0.07782 | 0.27466 | -0.39825 | -0.027466 | 0.009155 | 0.004578 | -0.018311 | 0.20142 | 0.31586 | -0.37994 | 122.4747 | 0.059509 | 122.7951 | 122.8455 | -0.20599 | 122.493 | 0.10071 | 0.32043 | 122.8546 | 123.0743 | 122.8821 | 123.1476 | 122.7951 | 123.1888 | 122.8775 | 122.493 | 123.1476 | 122.7951 | 122.8775 | 122.8821 | 123.1888 | -0.6134 | -0.59509
5069.1875 | 123.1338 | -122.8867 | 0.21973 | 0.046615 | 0.0096387 | -0.014642 | 0.043233 | -0.020888 | -0.012971 | 0.0053577 | -0.036621 | 0.27924 | -0.37994 | -0.022888 | 0.018311 | 0 | -0.009155 | 0.17853 | 0.32501 | -0.36163 | 122.5067 | 0.059509 | 122.85 | 122.8638 | -0.20142 | 122.525 | 0.10529 | 0.34332 | 122.8775 | 123.0652 | 122.905 | 123.1659 | 122.85 | 123.2117 | 122.8867 | 122.525 | 123.1659 | 122.85 | 122.8867 | 122.905 | 123.2117 | -0.59967 | -0.58136
5070.9531 | 123.2025 | -122.8546 | 0.19684 | -0.21278 | 0.0096387 | -0.016137 | 0.043874 | -0.018752 | -0.015748 | 0.0055713 | -0.054932 | 0.28381 | -0.3891 | 0 | 0.036621 | 0.032043 | 0.022888 | 0.22888 | 0.32044 | -0.37079 | 122.4655 | 0.086975 | 122.7997 | 122.8546 | -0.16022 | 122.4838 | 0.1236 | 0.33417 | 122.8775 | 123.0835 | 122.8912 | 123.1384 | 122.7997 | 123.175 | 122.8867 | 122.4838 | 123.1384 | 122.7997 | 122.8867 | 122.8912 | 123.175 | -0.58594 | -0.56763
5072.7031 | 123.2346 | -122.8363 | 0.18768 | 0.00083945 | 0.011134 | -0.010156 | 0.034047 | -0.01982 | -0.010194 | 0.0059985 | -0.022888 | 0.24261 | -0.34332 | 0.036621 | 0.091553 | 0.10071 | -0.1236 | 0.3067 | 0.27924 | -0.35248 | 122.493 | 0.054932 | 122.8134 | 122.8729 | -0.09613 | 122.4838 | 0.091553 | 0.32043 | 122.7127 | 123.143 | 122.9279 | 123.0789 | 122.8134 | 123.1155 | 122.937 | 122.4838 | 123.0789 | 122.8134 | 122.937 | 122.9279 | 123.1155 | -0.53101 | -0.54016
5074.4531 | 123.2346 | -122.8409 | 0.19226 | -0.01442 | 0.0098523 | -0.016137 | 0.03832 | -0.020461 | -0.010835 | 0.0064257 | -0.032043 | 0.24719 | -0.35706 | 0.045776 | 0.07782 | 0.091553 | -0.13275 | 0.3067 | 0.28839 | -0.35248 | 122.4838 | 0.054931 | 122.8088 | 122.8867 | -0.11444 | 122.4884 | 0.09613 | 0.32501 | 122.7081 | 123.1476 | 122.9187 | 123.0881 | 122.8088 | 123.1293 | 122.9324 | 122.4884 | 123.0881 | 122.8088 | 122.9324 | 122.9187 | 123.1293 | -0.54932 | -0.54474
5076.1562 | 123.111 | -122.8821 | 0.2243 | 0.19157 | 0.0085705 | -0.014855 | 0.047506 | -0.017256 | -0.014253 | 0.0049303 | -0.036621 | 0.2655 | -0.38452 | 0.018311 | 0.018311 | 0.045776 | -0.10071 | 0.21973 | 0.31128 | -0.37079 | 122.4976 | 0.041199 | 122.8455 | 122.9004 | -0.20599 | 122.5113 | 0.086975 | 0.3479 | 122.7814 | 123.1018 | 122.9004 | 123.1476 | 122.8455 | 123.1934 | 122.9279 | 122.5113 | 123.1476 | 122.8455 | 122.9279 | 122.9004 | 123.1934 | -0.60882 | -0.59509
5077.9219 | 123.2437 | -122.8455 | 0.18768 | -0.27382 | 0.01028 | -0.018914 | 0.043019 | -0.020888 | -0.015107 | 0.0032215 | -0.059509 | 0.27924 | -0.3891 | -0.022888 | 0.009155 | 0.004578 | 0.073242 | 0.21515 | 0.33417 | -0.36163 | 122.4564 | 0.091553 | 122.7859 | 122.8226 | -0.17853 | 122.4838 | 0.14648 | 0.32959 | 122.9187 | 123.0606 | 122.8546 | 123.1247 | 122.7859 | 123.1796 | 122.85 | 122.4838 | 123.1247 | 122.7859 | 122.85 | 122.8546 | 123.1796 | -0.57678 | -0.54932
5079.6719 | 123.2574 | -122.8455 | 0.19226 | -0.25856 | 0.0098523 | -0.014001 | 0.041097 | -0.020888 | -0.01468 | 0.0049303 | -0.059509 | 0.27466 | -0.40283 | -0.009155 | 0.013733 | 0.004578 | 0.064087 | 0.21515 | 0.31586 | -0.38452 | 122.4426 | 0.082397 | 122.7859 | 122.8363 | -0.17853 | 122.4609 | 0.1236 | 0.34332 | 122.9095 | 123.0606 | 122.8592 | 123.1201 | 122.7859 | 123.1613 | 122.85 | 122.4609 | 123.1201 | 122.7859 | 122.85 | 122.8592 | 123.1613 | -0.59509 | -0.57678
5081.4375 | 123.1247 | -122.9187 | 0.19684 | 0.12291 | 0.0081433 | -0.01571 | 0.042165 | -0.020461 | -0.012758 | 0.0045031 | 0.027466 | 0.23804 | -0.34332 | 0.064087 | 0.091553 | 0.11902 | -0.15564 | 0.29755 | 0.27008 | -0.31586 | 122.5754 | 0.041199 | 122.9462 | 122.9828 | -0.10529 | 122.6028 | 0.073243 | 0.37079 | 122.7631 | 123.2162 | 123.0103 | 123.1567 | 122.9462 | 123.1888 | 123.0377 | 122.6028 | 123.1567 | 122.9462 | 123.0377 | 123.0103 | 123.1888 | -0.54016 | -0.5127
5083.125 | 123.1018 | -122.8958 | 0.2243 | 0.21446 | 0.0077161 | -0.0097284 | 0.043233 | -0.020888 | -0.01468 | 0.0064257 | 0.027466 | 0.21973 | -0.34332 | 0.09613 | 0.09613 | 0.13733 | -0.20599 | 0.30212 | 0.2655 | -0.31128 | 122.5525 | -0.004577 | 122.9233 | 122.9919 | -0.12817 | 122.5845 | 0.041199 | 0.37079 | 122.6898 | 123.1979 | 122.9919 | 123.1155 | 122.9233 | 123.1613 | 123.0331 | 122.5845 | 123.1155 | 122.9233 | 123.0331 | 122.9919 | 123.1613 | -0.56763 | -0.53558
5084.875 | 123.2071 | -122.85 | 0.1831 | -0.19753 | 0.010707 | -0.013146 | 0.044515 | -0.019606 | -0.013185 | 0.0042895 | -0.050354 | 0.2655 | -0.39368 | 0 | 0.013733 | 0.032043 | 0.013733 | 0.25177 | 0.32501 | -0.37079 | 122.4564 | 0.082398 | 122.7997 | 122.85 | -0.16937 | 122.4792 | 0.14191 | 0.34332 | 122.8638 | 123.1018 | 122.8638 | 123.1155 | 122.7997 | 123.175 | 122.8821 | 122.4792 | 123.1155 | 122.7997 | 122.8821 | 122.8638 | 123.175 | -0.57678 | -0.55389
5086.6406 | 123.1384 | -122.8775 | 0.21973 | 0.13817 | 0.010493 | -0.0095148 | 0.042592 | -0.01982 | -0.010835 | 0.0066393 | -0.054932 | 0.25635 | -0.3891 | -0.018311 | 0.009155 | 0.018311 | -0.064087 | 0.1831 | 0.31128 | -0.37537 | 122.4884 | 0.036621 | 122.8226 | 122.8592 | -0.21057 | 122.5021 | 0.091552 | 0.33417 | 122.8134 | 123.0606 | 122.8867 | 123.1339 | 122.8226 | 123.1888 | 122.8958 | 122.5021 | 123.1339 | 122.8226 | 122.8958 | 122.8867 | 123.1888 | -0.60883 | -0.59509
5088.4062 | 123.1018 | -122.8683 | 0.23804 | 0.15343 | 0.0087841 | -0.013787 | 0.044301 | -0.020034 | -0.012758 | 0.0072803 | 0.032043 | 0.24261 | -0.35706 | 0.07782 | 0.09613 | 0.13275 | -0.16479 | 0.29297 | 0.27924 | -0.34332 | 122.5113 | 0.004578 | 122.9004 | 122.9462 | -0.14191 | 122.525 | 0.041199 | 0.3891 | 122.7036 | 123.1613 | 122.9645 | 123.111 | 122.9004 | 123.1476 | 123.0011 | 122.525 | 123.111 | 122.9004 | 123.0011 | 122.9645 | 123.1476 | -0.59509 | -0.58136
5090.1094 | 123.1613 | -122.8867 | 0.2243 | 0.061874 | 0.011989 | -0.011865 | 0.045797 | -0.02217 | -0.011903 | 0.0049303 | -0.064087 | 0.27924 | -0.40283 | -0.041199 | -0.013733 | -0.013733 | 0.018311 | 0.17395 | 0.31586 | -0.37537 | 122.4838 | 0.054932 | 122.8226 | 122.8455 | -0.23804 | 122.5113 | 0.091553 | 0.33875 | 122.905 | 123.0606 | 122.8729 | 123.1659 | 122.8226 | 123.2025 | 122.8729 | 122.5113 | 123.1659 | 122.8226 | 122.8729 | 122.8729 | 123.2025 | -0.62714 | -0.59967
5091.8594 | 123.1247 | -122.8867 | 0.21515 | 0.10765 | 0.0070751 | -0.013787 | 0.040029 | -0.01982 | -0.01169 | 0.0042895 | 0.036621 | 0.25177 | -0.3479 | 0.054932 | 0.09613 | 0.1236 | -0.18768 | 0.29297 | 0.27008 | -0.33417 | 122.5388 | 0.036621 | 122.9233 | 122.9416 | -0.11902 | 122.5525 | 0.054932 | 0.38452 | 122.699 | 123.1796 | 122.9828 | 123.1384 | 122.9233 | 123.1567 | 123.0103 | 122.5525 | 123.1384 | 122.9233 | 123.0103 | 122.9828 | 123.1567 | -0.56305 | -0.54932
5093.625 | 123.1064 | -122.9004 | 0.2243 | -0.060196 | 0.0087841 | -0.014855 | 0.04601 | -0.020461 | -0.014039 | 0.0045031 | -0.013733 | 0.26093 | -0.39368 | 0.027466 | 0.036621 | 0.054932 | -0.022888 | 0.25177 | 0.3067 | -0.33417 | 122.5067 | 0.036621 | 122.8867 | 122.9279 | -0.18768 | 122.5662 | 0.082398 | 0.37994 | 122.8775 | 123.1522 | 122.937 | 123.1613 | 122.8867 | 123.2071 | 122.9553 | 122.5662 | 123.1613 | 122.8867 | 122.9553 | 122.937 | 123.2071 | -0.61798 | -0.55847
5095.3281 | 123.1888 | -122.8592 | 0.19226 | 0.092392 | 0.0081433 | -0.017632 | 0.037038 | -0.018965 | -0.011049 | 0.0064257 | -0.018311 | 0.24261 | -0.35706 | 0.032043 | 0.073242 | 0.10529 | -0.11902 | 0.27924 | 0.29755 | -0.3479 | 122.5021 | 0.050354 | 122.8409 | 122.8912 | -0.11902 | 122.5113 | 0.10528 | 0.33874 | 122.7402 | 123.1384 | 122.9324 | 123.1018 | 122.8409 | 123.1567 | 122.9645 | 122.5113 | 123.1018 | 122.8409 | 122.9645 | 122.9324 | 123.1567 | -0.54932 | -0.54016
5097.0781 | 123.2254 | -122.8455 | 0.1831 | 0.038986 | 0.0083569 | -0.016992 | 0.038106 | -0.020247 | -0.011262 | 0.0047167 | -0.018311 | 0.26093 | -0.33875 | 0.045776 | 0.082397 | 0.082397 | -0.1236 | 0.27008 | 0.29297 | -0.35706 | 122.5067 | 0.07782 | 122.8271 | 122.8912 | -0.10071 | 122.4884 | 0.10986 | 0.32043 | 122.7219 | 123.1155 | 122.9279 | 123.1064 | 122.8271 | 123.1384 | 122.9279 | 122.4884 | 123.1064 | 122.8271 | 122.9279 | 122.9279 | 123.1384 | -0.52185 | -0.54016
5098.8438 | 123.23 | -122.8592 | 0.20142 | -0.17464 | 0.010921 | -0.011437 | 0.043874 | -0.01982 | -0.012544 | 0.0042895 | -0.036621 | 0.28839 | -0.37994 | -0.004578 | 0 | 0.018311 | 0.045776 | 0.23804 | 0.33417 | -0.37994 | 122.4792 | 0.086975 | 122.8226 | 122.8546 | -0.20142 | 122.4792 | 0.13275 | 0.34332 | 122.905 | 123.0972 | 122.8592 | 123.1476 | 122.8226 | 123.1934 | 122.8775 | 122.4792 | 123.1476 | 122.8226 | 122.8775 | 122.8592 | 123.1934 | -0.58136 | -0.58136
5100.5312 | 123.1293 | -122.8683 | 0.21515 | 0.12291 | 0.0083569 | -0.01101 | 0.043233 | -0.018538 | -0.01169 | 0.0051441 | 0.036621 | 0.2243 | -0.35248 | 0.07782 | 0.10071 | 0.1236 | -0.1831 | 0.29297 | 0.27924 | -0.33417 | 122.5159 | 0.009155 | 122.905 | 122.9462 | -0.11444 | 122.5342 | 0.064087 | 0.3891 | 122.6852 | 123.1613 | 122.9691 | 123.0927 | 122.905 | 123.1476 | 122.9919 | 122.5342 | 123.0927 | 122.905 | 122.9919 | 122.9691 | 123.1476 | -0.56763 | -0.54932

## Thermal Data
Fire Time | north top
-0.9333 | 19.0292
0.0667 | 18.9892
1.0667 | 19.0217
2.0667 | 19.0325
3.0667 | 19.026
4.0667 | 19.0755
5.0667 | 28.1058
6.0667 | 90.6331
7.0667 | 192.5715
8.0667 | 261.3808
9.0823 | 303.8788
10.0667 | 315.5811
11.0667 | 301.2283
12.0667 | 308.962
13.0667 | 347.394
14.0667 | 359.8569
15.0667 | 353.648
16.0667 | 359.2039
17.0667 | 354.9435
18.0667 | 352.5192
19.0667 | 348.6091
20.0667 | 350.6534
21.0667 | 344.6222
22.0667 | 339.8203
23.0823 | 330.9001
24.0823 | 318.9239
25.0667 | 312.1344
26.0667 | 302.2408
27.0667 | 288.5765
28.0667 | 273.8368
29.0667 | 264.5222
30.0667 | 257.4478
31.0667 | 251.0043
32.0667 | 248.5653
33.0667 | 243.2552
34.0667 | 236.7547
35.0667 | 228.9306
36.0667 | 223.9944
37.0667 | 215.923
38.0667 | 211.0749
39.0667 | 206.2751
40.0667 | 199.1454
41.0667 | 192.1093
42.0667 | 186.3943
43.0823 | 180.3197
44.0667 | 175.9352
45.0667 | 171.829
46.0667 | 168.0797
47.0667 | 165.3898
48.0667 | 163.5571
49.0667 | 160.4258
50.0667 | 159.9461
51.0823 | 159.8351
52.0667 | 158.381
53.0823 | 157.2138
54.0667 | 157.3873
55.0667 | 160.9316
56.0667 | 159.0819
57.0667 | 158.7272
58.0667 | 157.9869
59.0667 | 158.8999
60.0667 | 159.8574
61.0667 | 159.8824
62.0667 | 160.1552
63.0667 | 161.1363
64.0823 | 161.4593
65.0667 | 160.4763
66.0667 | 159.1635
67.0667 | 159.4656
68.0667 | 158.8767
69.0667 | 157.8357
70.0667 | 160.16
71.0667 | 161.5076
72.0667 | 161.4696
73.0667 | 162.2752
74.0667 | 161.1124
75.0667 | 163.0666
76.0667 | 164.4509
77.0667 | 164.6431
78.0667 | 163.0263
79.0667 | 166.0722
80.0667 | 170.7661
81.0667 | 170.4887
82.0667 | 170.5151
83.0667 | 171.6567
84.0667 | 172.8295
85.0667 | 175.2436
86.0667 | 174.2967
87.0667 | 173.6149
88.0667 | 172.9545
89.0667 | 172.4873
90.0667 | 173.2303
91.0667 | 173.9455
92.0667 | 175.6099
93.0667 | 177.154
94.0667 | 178.7437
95.0667 | 178.398
96.0667 | 178.8117
97.0667 | 180.7175
98.0667 | 180.4393
99.0667 | 180.3999
100.0667 | 183.9643
101.0667 | 183.7569
102.0667 | 185.6378
103.0667 | 187.0291
104.0667 | 187.4275
105.0667 | 188.1959
106.0667 | 187.5663
107.0667 | 186.9163
108.0667 | 184.2679
109.0667 | 184.6128
110.0667 | 183.2697
111.0667 | 180.5053
112.0667 | 177.9802
113.0667 | 178.2204
114.0667 | 178.7434
115.0667 | 177.8667
116.0667 | 177.4547
117.0667 | 181.8535
118.0667 | 184.1155
119.0667 | 182.8507
120.0667 | 183.9025
121.0667 | 183.9442
122.0667 | 187.685
123.0667 | 191.4909
124.0667 | 190.9639
125.0667 | 190.3539
126.0667 | 188.5344
127.0667 | 187.9033
128.0667 | 188.5955
129.0667 | 190.0361
130.0667 | 189.8139
131.0667 | 189.1527
132.0667 | 188.0425
133.0667 | 185.6182
134.0667 | 189.6127
135.0667 | 190.9688
136.0667 | 192.3681
137.0667 | 195.0941
138.0667 | 194.3045
139.0667 | 196.6387
140.0667 | 196.7477
141.0667 | 197.9635
142.0667 | 198.0059
143.0667 | 200.276
144.0823 | 204.7353
145.0667 | 208.3974
146.0667 | 213.7495
147.0667 | 211.4318
148.0667 | 215.2036
149.0667 | 215.9569
150.0667 | 219.4559
151.0667 | 216.4466
152.0667 | 214.3459
153.0667 | 214.1355
154.0667 | 211.5185
155.0667 | 211.2929
156.0667 | 214.8295
157.0667 | 211.8328
158.0667 | 217.294
159.0823 | 215.5486
160.0667 | 218.7971
161.0667 | 220.7543
162.0667 | 220.2735
163.0667 | 223.1968
164.0667 | 221.1076
165.0667 | 220.626
166.0667 | 217.6465
167.0667 | 214.7462
168.0667 | 214.2018
169.0667 | 213.9291
170.0667 | 212.9392
171.0667 | 213.3056
172.0667 | 213.2861
173.0667 | 212.2489
174.0667 | 211.1011
175.0667 | 211.8233
176.0667 | 210.9467
177.0667 | 211.3332
178.0667 | 212.3476
179.0667 | 212.439
180.0667 | 209.3651
181.0667 | 208.0818
182.0667 | 204.6895
183.0667 | 203.9242
184.0823 | 204.8283
185.0667 | 205.8657
186.0667 | 205.7912
187.0667 | 204.4791
188.0667 | 204.2177
189.0667 | 207.6435
190.0667 | 209.848
191.0667 | 214.2169
192.0667 | 218.2442
193.0667 | 221.9809
194.0667 | 225.3582
195.0667 | 230.4363
196.0667 | 231.6521
197.0667 | 230.173
198.0667 | 230.343
199.0667 | 231.9228
200.0667 | 230.3127
201.0667 | 226.7046
202.0667 | 224.5256
203.0667 | 224.0043
204.0667 | 224.3312
205.0667 | 221.2158
206.0667 | 220.4227
207.0667 | 221.8161
208.0667 | 225.0764
209.0667 | 224.5719
210.0667 | 229.0089
211.0667 | 229.4736
212.0667 | 231.8946
213.0667 | 231.9174
214.0667 | 230.0061
215.0667 | 230.4411
216.0667 | 230.3676
217.0667 | 230.8241
218.0667 | 229.2734
219.0667 | 231.6575
220.0667 | 231.492
221.0667 | 236.5535
222.0667 | 238.2061
223.0667 | 239.5005
224.0667 | 237.5923
225.0667 | 237.0787
226.0667 | 240.1208
227.0667 | 238.7899
228.0667 | 237.7507
229.0823 | 236.3915
230.0667 | 236.1145
231.0667 | 239.8829
232.0667 | 248.21
233.0667 | 257.7759
234.0667 | 264.8473
235.0667 | 268.5349
236.0667 | 271.9763
237.0667 | 276.5053
238.0667 | 279.2336
239.0667 | 276.1777
240.0667 | 273.2064
241.0667 | 278.0754
242.0667 | 280.4578
243.0667 | 273.9879
244.0823 | 271.7659
245.0667 | 276.4725
246.0667 | 276.4335
247.0667 | 281.7215
248.0667 | 279.11
249.0667 | 282.7838
250.0667 | 297.0909
251.0667 | 306.0723
252.0667 | 319.0306
253.0667 | 326.4936
254.0667 | 338.0191
255.0667 | 342.6304
256.0667 | 343.9383
257.0667 | 348.2541
258.0667 | 356.2719
259.0667 | 354.0605
260.0667 | 356.9884
261.0667 | 352.8227
262.0667 | 362.4842
263.0667 | 360.9561
264.0667 | 368.1158
265.0667 | 374.7285
266.0667 | 380.8334
267.0667 | 389.8344
268.0667 | 391.7949
269.0667 | 394.4184
270.0667 | 407.0314
271.0667 | 408.3791
272.0667 | 409.3831
273.0823 | 408.5613
274.0667 | 407.5021
275.0667 | 408.228
276.0667 | 398.6535
277.0667 | 406.748
278.0667 | 405.1994
279.0667 | 409.888
280.0667 | 419.3401
281.0667 | 415.9762
282.0667 | 418.0509
283.0667 | 426.1331
284.0667 | 428.2111
285.0667 | 424.29
286.0667 | 429.993
287.0667 | 436.1108
288.0667 | 443.8826
289.0667 | 448.9519
290.0667 | 453.0784
291.0667 | 453.5812
292.0667 | 455.4312
293.0667 | 456.8227
294.0667 | 450.4155
295.0667 | 454.6272
296.0667 | 454.3967
297.0667 | 464.0358
298.0667 | 464.0761
299.0667 | 470.9334
300.0667 | 478.2716
301.0667 | 488.3285
302.0667 | 486.9319
303.0667 | 483.4894
304.0667 | 482.0638
305.0667 | 483.617
306.0667 | 484.8615
307.0667 | 482.3577
308.0667 | 485.1963
309.0667 | 491.5247
310.0667 | 500.4566
311.0667 | 501.9893
312.0667 | 504.9363
313.0667 | 507.9759
314.0667 | 507.8981
315.0667 | 521.6074
316.0667 | 522.1594
317.0667 | 522.7126
318.0667 | 516.9944
319.0667 | 511.2559
320.0667 | 511.5874
321.0667 | 511.3532
322.0667 | 523.5449
323.0667 | 523.0607
324.0667 | 521.1837
325.0667 | 515.9505
326.0667 | 511.0549
327.0667 | 517.1101
328.0667 | 517.0169
329.0667 | 516.0153
330.0667 | 515.4496
331.0667 | 523.4341
332.0667 | 524.6786
333.0667 | 532.5343
334.0667 | 532.4314
335.0667 | 537.6658
336.0667 | 539.9928
337.0667 | 543.1144
338.0667 | 548.3759
339.0667 | 547.7302
340.0667 | 550.4376
341.0667 | 549.0408
342.0667 | 548.4661
343.0667 | 547.3093
344.0667 | 549.1041
345.0667 | 547.0558
346.0667 | 548.5593
347.0667 | 549.4679
348.0667 | 543.5692
349.0667 | 543.6945
350.0667 | 543.4289
351.0667 | 544.4033
352.0667 | 536.6537
353.0667 | 540.1084
354.0667 | 528.276
355.0667 | 532.0901
356.0667 | 535.9904
357.0667 | 536.5869
358.0667 | 546.8846
359.0667 | 556.1314
360.0667 | 557.5643
361.0667 | 561.3056
362.0667 | 565.536
363.0667 | 570.5846
364.0823 | 569.5779
365.0667 | 574.3894
366.0667 | 571.1244
367.0667 | 577.2006
368.0667 | 584.341
369.0667 | 577.9348
370.0667 | 575.9275
371.0667 | 579.33
372.0667 | 573.3926
373.0667 | 567.8074
374.0667 | 567.3862
375.0667 | 569.7214
376.0667 | 572.8145
377.0667 | 565.5087
378.0667 | 568.6897
379.0823 | 565.6551
380.0667 | 573.7683
381.0667 | 572.0778
382.0667 | 561.1974
383.0667 | 558.1717
384.0667 | 557.0407
385.0667 | 561.9376
386.0667 | 565.1164
387.0667 | 572.1029
388.0667 | 571.8933
389.0667 | 563.1478
390.0667 | 562.3114
391.0667 | 551.6098
392.0667 | 548.5261
393.0667 | 557.5815
394.0667 | 554.6783
395.0667 | 566.9298
396.0667 | 565.133
397.0667 | 559.0199
398.0667 | 558.3078
399.0667 | 557.6028
400.0667 | 560.2684
401.0667 | 571.6069
402.0667 | 583.2743
403.0667 | 583.7995
404.0823 | 592.5078
405.0667 | 603.8548
406.0667 | 610.8899
407.0667 | 617.5985
408.0667 | 624.2755
409.0667 | 610.2195
410.0667 | 607.7404
411.0667 | 607.1066
412.0667 | 607.5536
413.0667 | 598.0071
414.0667 | 589.9259
415.0667 | 580.5005
416.0667 | 580.3035
417.0667 | 588.76
418.0667 | 585.5556
419.0667 | 587.5964
420.0667 | 593.7745
421.0667 | 590.8019
422.0667 | 583.3909
423.0667 | 590.8925
424.0667 | 596.4298
425.0667 | 593.6946
426.0667 | 593.954
427.0667 | 585.237
428.0667 | 583.9716
429.0667 | 562.5738
430.0667 | 567.4134
431.0667 | 558.5551
432.0667 | 555.8525
433.0667 | 551.2726
434.0667 | 558.0844
435.0667 | 546.612
436.0667 | 552.4015
437.0667 | 561.9248
438.0667 | 566.6489
439.0667 | 560.6134
440.0667 | 567.3269
441.0667 | 572.6448
442.0667 | 576.8392
443.0667 | 573.5137
444.0667 | 570.6724
445.0667 | 580.2968
446.0667 | 590.0567
447.0667 | 597.8519
448.0667 | 591.5877
449.0667 | 599.1699
450.0823 | 606.2561
451.0667 | 615.4706
452.0667 | 623.7528
453.0667 | 625.0623
454.0667 | 626.8944
455.0667 | 627.3961
456.0667 | 630.4321
457.0667 | 627.4456
458.0667 | 628.5417
459.0667 | 621.4861
460.0667 | 626.5012
461.0667 | 621.2115
462.0667 | 626.9706
463.0667 | 632.3494
464.0823 | 630.0019
465.0667 | 624.659
466.0667 | 630.3152
467.0823 | 635.7459
468.0667 | 617.8612
469.0667 | 607.1974
470.0667 | 602.1437
471.0667 | 603.0868
472.0667 | 608.8835
473.0667 | 600.2984
474.0667 | 593.1061
475.0667 | 601.0822
476.0667 | 601.7093
477.0667 | 593.6173
478.0667 | 598.1004
479.0667 | 594.9804
480.0667 | 607.7544
481.0667 | 603.9619
482.0667 | 604.674
483.0667 | 611.8349
484.0667 | 621.1842
485.0667 | 641.6881
486.0667 | 637.5372
487.0667 | 632.5526
488.0667 | 634.6404
489.0667 | 643.2423
490.0667 | 639.3991
491.0667 | 645.1839
492.0667 | 651.7845
493.0667 | 639.8396
494.0667 | 646.1353
495.0667 | 646.842
496.0667 | 661.7009
497.0667 | 654.3717
498.0667 | 666.4506
499.0667 | 664.9645
500.0667 | 679.521
501.0667 | 685.8281
502.0667 | 677.0241
503.0667 | 678.0145
504.0823 | 690.1092
505.0667 | 695.205
506.0667 | 686.1864
507.0667 | 698.5685
508.0667 | 706.2001
509.0667 | 701.5839
510.0667 | 720.0075
511.0667 | 724.707
512.0667 | 727.7584
513.0667 | 728.6599
514.0667 | 743.0204
515.0667 | 733.9036
516.0667 | 734.7627
517.0667 | 746.8215
518.0667 | 756.4035
519.0667 | 756.7855
520.0667 | 758.2252
521.0667 | 766.4514
522.0667 | 760.9143
523.0667 | 751.9357
524.0667 | 744.3329
525.0667 | 746.1838
526.0667 | 731.3967
527.0667 | 722.1717
528.0667 | 718.1176
529.0667 | 719.0817
530.0667 | 706.7091
531.0667 | 699.681
532.0667 | 687.96
533.0667 | 680.3665
534.0667 | 680.6571
535.0667 | 690.5143
536.0667 | 670.6069
537.0667 | 693.5855
538.0667 | 694.395
539.0667 | 701.2503
540.0667 | 686.0655
541.0667 | 680.4043
542.0667 | 668.9979
543.0667 | 659.0351
544.0667 | 659.0569
545.0667 | 663.6925
546.0667 | 665.3709
547.0667 | 653.8407
548.0667 | 652.6591
549.0667 | 656.4117
550.0667 | 659.5603
551.0667 | 661.4119
552.0667 | 658.9832
553.0667 | 654.712
554.0667 | 649.2132
555.0667 | 645.4129
556.0667 | 646.0927
557.0667 | 631.261
558.0667 | 633.8334
559.0667 | 640.2682
560.0667 | 640.6379
561.0667 | 640.915
562.0667 | 646.5571
563.0667 | 640.0161
564.0667 | 632.6432
565.0667 | 640.4869
566.0667 | 633.3626
567.0667 | 638.7149
568.0667 | 638.6355
569.0667 | 654.9604
570.0667 | 657.923
571.0667 | 652.2256
572.0667 | 645.4291
573.0667 | 638.369
574.0667 | 631.0371
575.0667 | 635.4831
576.0667 | 634.6669
577.0667 | 634.1504
578.0667 | 632.41
579.0667 | 627.5784
580.0667 | 628.1202
581.0667 | 630.2783
582.0667 | 625.6807
583.0667 | 630.9279
584.0667 | 629.4704
585.0667 | 640.9227
586.0667 | 634.8937
587.0667 | 631.8305
588.0667 | 632.886
589.0667 | 631.0555
590.0667 | 624.2428
591.0667 | 624.7125
592.0667 | 629.2753
593.0667 | 632.4095
594.0667 | 633.5278
595.0667 | 628.8219
596.0667 | 623.7136
597.0667 | 624.7541
598.0667 | 632.5471
599.0667 | 636.0251
600.0667 | 637.0644
601.0667 | 635.5591
602.0667 | 645.2579
603.0667 | 648.22
604.0667 | 641.0177
605.0667 | 646.5621
606.0667 | 649.2621
607.0667 | 652.2352
608.0667 | 648.7644
609.0667 | 649.3646
610.0667 | 645.6791
611.0667 | 626.8847
612.0667 | 632.2604
613.0667 | 636.9204
614.0667 | 640.4613
615.0667 | 655.1244
616.0667 | 654.5425
617.0667 | 660.5795
618.0667 | 650.5596
619.0667 | 655.9286
620.0667 | 655.9584
621.0667 | 654.6807
622.0667 | 647.0333
623.0667 | 647.4099
624.0667 | 643.1435
625.0667 | 649.5039
626.0667 | 644.9333
627.0667 | 630.5076
628.0667 | 629.5929
629.0667 | 635.3989
630.0667 | 643.5704
631.0667 | 644.951
632.0667 | 640.0681
633.0667 | 640.9922
634.0667 | 644.6729
635.0667 | 641.0174
636.0667 | 636.0972
637.0667 | 628.25
638.0667 | 631.1283
639.0823 | 627.7572
640.0667 | 633.2531
641.0667 | 638.926
642.0667 | 644.94
643.0667 | 645.7614
644.0667 | 643.9539
645.0667 | 647.8699
646.0667 | 647.4833
647.0667 | 645.8354
648.0667 | 639.3546
649.0667 | 646.1563
650.0667 | 651.8761
651.0667 | 650.8489
652.0667 | 647.0487
653.0667 | 644.9175
654.0823 | 639.5947
655.0667 | 637.2092
656.0667 | 636.4432
657.0667 | 632.742
658.0667 | 614.1732
659.0667 | 597.7723
660.0667 | 591.6926
661.0667 | 586.2664
662.0667 | 591.0965
663.0667 | 580.3354
664.0667 | 571.6824
665.0667 | 558.1706
666.0667 | 551.206
667.0667 | 543.178
668.0667 | 536.4635
669.0667 | 522.922
670.0667 | 526.912
671.0667 | 516.8392
672.0667 | 510.8183
673.0667 | 510.2987
674.0667 | 503.3903
675.0667 | 493.2483
676.0667 | 491.7194
677.0667 | 483.6006
678.0667 | 484.6297
679.0823 | 482.1282
680.0667 | 493.95
681.0667 | 505.5787
682.0667 | 509.6181
683.0667 | 529.2593
684.0667 | 543.3794
685.0667 | 560.8936
686.0667 | 564.3949
687.0667 | 570.8916
688.0667 | 578.7622
689.0667 | 591.4163
690.0667 | 599.0625
691.0667 | 593.8086
692.0667 | 585.1698
693.0667 | 571.6098
694.0667 | 557.3854
695.0667 | 550.7158
696.0667 | 550.1344
697.0667 | 552.6911
698.0667 | 563.8258
699.0667 | 566.615
700.0667 | 570.7059
701.0667 | 565.625
702.0667 | 566.4655
703.0667 | 556.1841
704.0667 | 555.9269
705.0667 | 559.8007
706.0667 | 557.2433
707.0667 | 550.6081
708.0667 | 553.073
709.0667 | 551.9233
710.0667 | 546.4459
711.0667 | 544.0957
712.0667 | 538.9045
713.0667 | 541.3054
714.0667 | 537.8867
715.0667 | 529.02
716.0667 | 534.0711
717.0667 | 539.1487
718.0667 | 539.2529
719.0667 | 525.7187
720.0667 | 517.3607
721.0667 | 515.6511
722.0667 | 513.5311
723.0667 | 516.098
724.0667 | 523.7258
725.0667 | 527.1557
726.0667 | 525.9329
727.0667 | 523.9038
728.0667 | 520.2716
729.0667 | 513.3605
730.0823 | 514.2177
731.0823 | 502.9649
732.0667 | 499.2795
733.0667 | 501.4908
734.0667 | 510.5848
735.0667 | 507.7003
736.0667 | 512.9027
737.0667 | 512.0848
738.0667 | 514.3018
739.0823 | 517.3226
740.0667 | 520.3135
741.0667 | 524.369
742.0667 | 533.7585
743.0667 | 531.1699
744.0667 | 531.4387
745.0667 | 524.4714
746.0667 | 528.5101
747.0667 | 522.501
748.0667 | 530.6422
749.0667 | 530.1362
750.0667 | 533.5074
751.0667 | 526.6556
752.0667 | 522.5676
753.0667 | 524.1949
754.0667 | 510.8926
755.0667 | 503.3105
756.0667 | 496.5977
757.0667 | 491.6019
758.0667 | 502.7273
759.0667 | 506.247
760.0667 | 504.7616
761.0667 | 497.6572
762.0667 | 493.052
763.0667 | 492.064
764.0667 | 490.3535
765.0667 | 487.2177
766.0667 | 483.9275
767.0667 | 482.0538
768.0667 | 481.5607
769.0667 | 477.7472
770.0667 | 474.224
771.0667 | 468.3148
772.0667 | 468.5106
773.0667 | 470.5313
774.0667 | 464.3489
775.0667 | 459.8998
776.0667 | 460.5456
777.0667 | 454.8168
778.0667 | 457.9983
779.0823 | 461.195
780.0667 | 453.5149
781.0667 | 450.6647
782.0667 | 447.7465
783.0667 | 442.067
784.0667 | 442.4525
785.0667 | 443.7684
786.0667 | 438.6004
787.0667 | 441.9612
788.0667 | 441.3115
789.0667 | 440.7939
790.0667 | 442.9299
791.0667 | 444.8004
792.0667 | 448.7503
793.0667 | 448.4227
794.0823 | 445.0686
795.0667 | 445.1345
796.0667 | 442.3773
797.0667 | 441.898
798.0667 | 440.0166
799.0667 | 443.1751
800.0667 | 438.3335
801.0667 | 436.9287
802.0667 | 434.2002
803.0667 | 437.9658
804.0667 | 435.5049
805.0667 | 433.9001
806.0667 | 435.8584
807.0667 | 432.3595
808.0667 | 427.8998
809.0667 | 429.5573
810.0667 | 435.7681
811.0667 | 438.4543
812.0667 | 444.9588
813.0667 | 445.3627
814.0667 | 443.3553
815.0667 | 439.116
816.0667 | 437.7124
817.0667 | 433.122
818.0667 | 428.3695
819.0667 | 432.9156
820.0667 | 429.1001
821.0667 | 428.1874
822.0667 | 428.2868
823.0667 | 422.3743
824.0667 | 422.2504
825.0667 | 433.65
826.0667 | 438.5272
827.0667 | 439.6563
828.0667 | 444.0071
829.0667 | 439.9207
830.0667 | 435.8075
831.0667 | 440.5708
832.0667 | 439.5052
833.0667 | 440.878
834.0667 | 435.3023
835.0667 | 428.9572
836.0667 | 426.8147
837.0667 | 426.8982
838.0667 | 430.0495
839.0667 | 429.4084
840.0667 | 431.1133
841.0667 | 433.6953
842.0667 | 435.6027
843.0667 | 434.7271
844.0667 | 428.9077
845.0667 | 435.7661
846.0667 | 437.7107
847.0667 | 438.1372
848.0667 | 441.471
849.0667 | 444.1437
850.0667 | 453.5026
851.0667 | 466.5631
852.0667 | 477.8982
853.0667 | 483.0554
854.0667 | 481.9756
855.0667 | 480.3938
856.0667 | 477.818
857.0667 | 478.0777
858.0667 | 468.5286
859.0667 | 463.8648
860.0667 | 460.3173
861.0667 | 465.5181
862.0823 | 463.9313
863.0667 | 463.7558
864.0667 | 461.3079
865.0667 | 458.3059
866.0667 | 457.7214
867.0667 | 456.3063
868.0667 | 457.1294
869.0667 | 453.3764
870.0667 | 447.8976
871.0667 | 449.0773
872.0667 | 447.2347
873.0667 | 446.2548
874.0667 | 453.9796
875.0667 | 454.6345
876.0667 | 462.2972
877.0667 | 457.0343
878.0667 | 465.5555
879.0667 | 464.9581
880.0667 | 468.4819
881.0667 | 469.1566
882.0667 | 471.0845
883.0667 | 472.2668
884.0667 | 469.9248
885.0667 | 472.6008
886.0667 | 470.3326
887.0667 | 477.0473
888.0667 | 478.6286
889.0667 | 489.5608
890.0667 | 481.9199
891.0667 | 478.2827
892.0667 | 477.8193
893.0667 | 476.2948
894.0667 | 474.8753
895.0667 | 468.6933
896.0667 | 466.0342
897.0667 | 467.8051
898.0667 | 479.4818
899.0667 | 487.6399
900.0667 | 480.753
901.0667 | 481.1028
902.0667 | 474.0354
903.0667 | 475.15
904.0667 | 474.469
905.0667 | 469.4991
906.0667 | 470.8348
907.0667 | 471.7205
908.0667 | 467.4364
909.0667 | 467.1793
910.0667 | 466.8238
911.0667 | 470.6443
912.0667 | 476.9813
913.0667 | 478.0466
914.0823 | 472.9933
915.0667 | 471.9689
916.0667 | 471.5473
917.0667 | 473.9583
918.0667 | 471.9221
919.0667 | 464.9745
920.0667 | 471.7439
921.0667 | 476.95
922.0667 | 485.568
923.0667 | 488.3358
924.0823 | 495.7268
925.0667 | 501.2187
926.0667 | 494.2188
927.0667 | 490.6516
928.0667 | 492.3044
929.0823 | 499.0091
930.0667 | 499.5891
931.0667 | 495.2255
932.0667 | 489.143
933.0667 | 484.7885
934.0667 | 476.9776
935.0667 | 474.2325
936.0667 | 477.6572
937.0667 | 489.1891
938.0667 | 500.0068
939.0667 | 513.5307
940.0667 | 504.6783
941.0667 | 501.7761
942.0667 | 498.5807
943.0667 | 507.8649
944.0667 | 508.8366
945.0823 | 511.5038
946.0667 | 510.5439
947.0667 | 531.6732
948.0667 | 523.7393
949.0667 | 520.4021
950.0667 | 514.8716
951.0667 | 513.9356
952.0667 | 512.854
953.0667 | 506.0346
954.0823 | 510.6887
955.0667 | 512.6646
956.0667 | 515.9375
957.0667 | 537.8287
958.0667 | 574.4851
959.0667 | 601.4505
960.0667 | 629.2317
961.0667 | 635.8496
962.0667 | 645.8063
963.0667 | 652.924
964.0667 | 640.1084
965.0667 | 646.0703
966.0667 | 649.525
967.0667 | 651.7624
968.0667 | 663.9734
969.0823 | 675.3679
970.0667 | 683.1676
971.0667 | 683.957
972.0667 | 696.5503
973.0667 | 698.9387
974.0667 | 704.2661
975.0667 | 700.1887
976.0667 | 712.7334
977.0667 | 724.6136
978.0667 | 725.247
979.0667 | 728.6059
980.0667 | 728.7702
981.0667 | 711.0336
982.0667 | 710.3501
983.0667 | 721.9339
984.0823 | 730.644
985.0667 | 737.9582
986.0667 | 745.4012
987.0667 | 746.2733
988.0667 | 741.6339
989.0667 | 737.5096
990.0667 | 737.8801
991.0667 | 744.5696
992.0667 | 729.9111
993.0667 | 726.6076
994.0667 | 731.8459
995.0667 | 729.945
996.0667 | 743.749
997.0667 | 753.1939
998.0667 | 763.9034
999.0667 | 759.6739
1000.0667 | 761.9098
1001.0667 | 750.872
1002.0667 | 748.6108
1003.0667 | 755.1962
1004.0667 | 750.6725
1005.0667 | 748.1302
1006.0667 | 741.1792
1007.0667 | 747.8597
1008.0667 | 740.2482
1009.0823 | 743.6282
1010.0667 | 751.5146
1011.0667 | 757.3845
1012.0667 | 770.3692
1013.0667 | 777.2396
1014.0823 | 774.0645
1015.0667 | 770.8191
1016.0667 | 774.0517
1017.0667 | 770.3953
1018.0667 | 761.1647
1019.0667 | 745.1232
1020.0667 | 753.9281
1021.0667 | 762.4599
1022.0667 | 765.5104
1023.0667 | 769.1411
1024.0667 | 761.8286
1025.0667 | 756.0947
1026.0667 | 748.2392
1027.0667 | 747.7671
1028.0667 | 754.4781
1029.0667 | 751.4086
1030.0667 | 746.3903
1031.0667 | 738.513
1032.0667 | 748.8613
1033.0667 | 742.822
1034.0667 | 747.0558
1035.0667 | 747.9731
1036.0667 | 747.5358
1037.0667 | 754.1471
1038.0667 | 756.2449
1039.0667 | 754.3634
1040.0667 | 758.4659
1041.0667 | 768.165
1042.0667 | 763.7264
1043.0667 | 762.8144
1044.0823 | 754.2816
1045.0667 | 743.5228
1046.0667 | 751.1
1047.0667 | 748.4006
1048.0667 | 753.1351
1049.0667 | 757.9046
1050.0667 | 769.8852
1051.0667 | 770.6085
1052.0667 | 772.3339
1053.0667 | 765.552
1054.0667 | 779.0008
1055.0667 | 787.0739
1056.0667 | 779.0715
1057.0667 | 783.6473
1058.0667 | 772.5806
1059.0667 | 774.7227
1060.0667 | 772.6135
1061.0667 | 772.2353
1062.0667 | 753.1177
1063.0667 | 752.0468
1064.0667 | 752.8218
1065.0667 | 749.9771
1066.0667 | 752.85
1067.0667 | 750.2964
1068.0667 | 760.958
1069.0823 | 770.5515
1070.0667 | 751.1863
1071.0667 | 745.4057
1072.0667 | 741.2829
1073.0667 | 732.2192
1074.0823 | 741.9926
1075.0667 | 741.7717
1076.0667 | 749.0392
1077.0667 | 758.2838
1078.0667 | 759.6747
1079.0667 | 759.3022
1080.0667 | 759.7311
1081.0667 | 743.0892
1082.0667 | 743.9513
1083.0667 | 749.4037
1084.0667 | 753.2855
1085.0667 | 757.2216
1086.0667 | 749.0561
1087.0667 | 759.1669
1088.0667 | 755.2688
1089.0667 | 757.4509
1090.0667 | 757.634
1091.0667 | 764.0644
1092.0667 | 772.9437
1093.0667 | 769.46
1094.0667 | 769.9784
1095.0667 | 757.6099
1096.0667 | 738.3131
1097.0667 | 736.0191
1098.0667 | 738.7477
1099.0667 | 747.7555
1100.0667 | 743.7556
1101.0667 | 742.3742
1102.0667 | 742.4063
1103.0667 | 743.409
1104.0667 | 736.4806
1105.0667 | 739.7974
1106.0667 | 741.7227
1107.0823 | 741.4434
1108.0823 | 742.4232
1109.0823 | 744.5024
1110.0667 | 750.0319
1111.0823 | 749.5361
1112.0823 | 752.7936
1113.0823 | 751.1942
1114.0823 | 741.3394
1115.0667 | 740.7564
1116.0667 | 746.6866
1117.0667 | 755.0013
1118.0667 | 756.9523
1119.0667 | 759.5393
1120.0667 | 750.5325
1121.0667 | 743.4342
1122.0667 | 745.1883
1123.0667 | 757.7095
1124.0823 | 758.8963
1125.0667 | 771.7401
1126.0667 | 776.6421
1127.0667 | 779.6749
1128.0667 | 771.929
1129.0667 | 777.6764
1130.0667 | 773.0728
1131.0667 | 774.516
1132.0667 | 773.2282
1133.0667 | 774.5295
1134.0667 | 784.6192
1135.0667 | 792.1952
1136.0667 | 799.8475
1137.0667 | 793.8411
1138.0667 | 790.9531
1139.0667 | 797.5245
1140.0667 | 808.7242
1141.0667 | 810.9404
1142.0667 | 796.1266
1143.0667 | 792.7996
1144.0667 | 786.4187
1145.0667 | 772.0702
1146.0667 | 768.456
1147.0667 | 764.6753
1148.0667 | 757.339
1149.0667 | 747.8916
1150.0667 | 756.6162
1151.0667 | 757.4839
1152.0667 | 764.3742
1153.0667 | 769.8353
1154.0667 | 766.2912
1155.0667 | 752.4958
1156.0667 | 762.6842
1157.0667 | 763.8194
1158.0667 | 749.7002
1159.0667 | 742.0973
1160.0667 | 750.6135
1161.0667 | 765.7022
1162.0667 | 776.7079
1163.0667 | 781.8014
1164.0667 | 775.3939
1165.0667 | 760.6599
1166.0667 | 748.6518
1167.0667 | 749.8837
1168.0667 | 762.456
1169.0667 | 767.5073
1170.0667 | 773.0803
1171.0667 | 767.626
1172.0667 | 756.0677
1173.0667 | 741.6706
1174.0667 | 735.5749
1175.0667 | 740.224
1176.0667 | 747.3688
1177.0667 | 753.5611
1178.0667 | 765.5543
1179.0667 | 759.2563
1180.0667 | 760.2271
1181.0667 | 771.256
1182.0667 | 781.8583
1183.0667 | 781.3938
1184.0667 | 788.3738
1185.0667 | 798.0243
1186.0667 | 798.3924
1187.0667 | 788.5321
1188.0667 | 780.1219
1189.0667 | 772.439
1190.0667 | 765.9153
1191.0667 | 758.9133
1192.0667 | 764.4453
1193.0667 | 767.2217
1194.0667 | 769.6625
1195.0667 | 758.2648
1196.0667 | 760.6463
1197.0667 | 754.7358
1198.0667 | 758.7324
1199.0667 | 756.8581
1200.0667 | 749.6751
1201.0667 | 754.9107
1202.0667 | 775.2027
1203.0667 | 771.7603
1204.0667 | 779.0299
1205.0667 | 784.0747
1206.0667 | 790.0192
1207.0667 | 797.1713
1208.0667 | 804.3893
1209.0667 | 800.058
1210.0667 | 794.5643
1211.0667 | 804.0649
1212.0667 | 788.9201
1213.0667 | 793.9892
1214.0667 | 775.8972
1215.0667 | 777.6897
1216.0667 | 773.4907
1217.0667 | 775.4991
1218.0667 | 776.8082
1219.0667 | 781.8139
1220.0667 | 778.2442
1221.0667 | 763.1471
1222.0667 | 757.8568
1223.0667 | 754.9418
1224.0667 | 752.4989
1225.0667 | 744.5243
1226.0667 | 754.4299
1227.0667 | 751.7583
1228.0667 | 760.3064
1229.0667 | 772.7972
1230.0667 | 788.8294
1231.0667 | 796.4673
1232.0667 | 787.4006
1233.0667 | 782.4674
1234.0667 | 791.7298
1235.0667 | 796.376
1236.0667 | 797.3781
1237.0667 | 785.7078
1238.0667 | 795.821
1239.0667 | 792.6293
1240.0667 | 794.1136
1241.0667 | 789.0161
1242.0667 | 774.1801
1243.0667 | 782.3356
1244.0823 | 778.9918
1245.0667 | 792.0982
1246.0667 | 783.1121
1247.0667 | 779.561
1248.0667 | 770.1545
1249.0667 | 776.812
1250.0667 | 779.9951
1251.0667 | 788.537
1252.0667 | 775.754
1253.0667 | 770.7394
1254.0667 | 759.3953
1255.0667 | 762.7894
1256.0667 | 761.2145
1257.0667 | 766.8318
1258.0667 | 760.4672
1259.0823 | 750.2055
1260.0667 | 756.9052
1261.0667 | 760.1484
1262.0667 | 749.9056
1263.0667 | 744.3548
1264.0667 | 759.8496
1265.0667 | 778.4387
1266.0667 | 787.5072
1267.0667 | 769.4282
1268.0667 | 772.3905
1269.0667 | 765.48
1270.0667 | 780.8335
1271.0667 | 791.6802
1272.0667 | 799.8194
1273.0667 | 788.5115
1274.0667 | 779.9309
1275.0667 | 778.3859
1276.0667 | 779.0911
1277.0667 | 779.0645
1278.0667 | 786.4482
1279.0667 | 775.4282
1280.0667 | 774.6573
1281.0667 | 769.1584
1282.0667 | 773.3033
1283.0667 | 781.2962
1284.0823 | 787.376
1285.0667 | 784.9037
1286.0667 | 772.7946
1287.0667 | 764.9983
1288.0667 | 754.2111
1289.0667 | 768.4709
1290.0667 | 772.8511
1291.0667 | 780.2087
1292.0667 | 782.3693
1293.0667 | 773.8502
1294.0667 | 783.4442
1295.0667 | 791.8115
1296.0667 | 805.3283
1297.0667 | 797.8093
1298.0667 | 791.1579
1299.0823 | 789.6039
1300.0667 | 803.512
1301.0667 | 814.4517
1302.0667 | 817.2834
1303.0667 | 827.0882
1304.0667 | 822.6016
1305.0667 | 816.8853
1306.0667 | 805.4193
1307.0667 | 799.8879
1308.0667 | 805.6251
1309.0667 | 806.74
1310.0667 | 790.9517
1311.0667 | 793.2578
1312.0667 | 802.0922
1313.0667 | 807.9884
1314.0667 | 816.0539
1315.0667 | 805.1131
1316.0667 | 800.5292
1317.0667 | 797.3783
1318.0667 | 795.6961
1319.0667 | 797.1117
1320.0667 | 803.1466
1321.0667 | 805.4758
1322.0667 | 816.3371
1323.0667 | 808.3208
1324.0667 | 814.1653
1325.0667 | 815.629
1326.0667 | 829.1606
1327.0667 | 824.9423
1328.0667 | 818.4508
1329.0667 | 810.5763
1330.0667 | 809.4778
1331.0667 | 801.645
1332.0667 | 802.0139
1333.0667 | 815.1279
1334.0667 | 823.3091
1335.0667 | 823.1027
1336.0667 | 824.3691
1337.0667 | 827.8092
1338.0667 | 835.886
1339.0823 | 832.8673
1340.0667 | 833.2489
1341.0667 | 813.3098
1342.0667 | 811.3522
1343.0667 | 801.1578
1344.0823 | 787.597
1345.0667 | 771.3376
1346.0667 | 775.5428
1347.0667 | 759.4355
1348.0667 | 764.4631
1349.0667 | 768.473
1350.0667 | 767.725
1351.0667 | 766.5803
1352.0667 | 771.1745
1353.0667 | 768.6599
1354.0667 | 771.0907
1355.0667 | 759.278
1356.0667 | 769.4814
1357.0667 | 779.4288
1358.0667 | 781.8679
1359.0667 | 786.1826
1360.0667 | 770.9121
1361.0667 | 766.5222
1362.0667 | 761.9254
1363.0667 | 774.1675
1364.0667 | 760.1693
1365.0667 | 770.2416
1366.0667 | 751.4141
1367.0667 | 743.1495
1368.0667 | 733.9363
1369.0667 | 732.8832
1370.0667 | 753.3599
1371.0667 | 763.8229
1372.0667 | 764.2729
1373.0667 | 748.1673
1374.0667 | 760.3568
1375.0667 | 757.2623
1376.0667 | 767.9579
1377.0667 | 763.3391
1378.0667 | 752.9952
1379.0667 | 751.0741
1380.0667 | 748.5002
1381.0667 | 753.0756
1382.0667 | 769.1554
1383.0667 | 780.4763
1384.0823 | 772.1877
1385.0667 | 764.2278
1386.0667 | 756.7753
1387.0667 | 754.061
1388.0667 | 771.9599
1389.0823 | 778.1929
1390.0667 | 775.4573
1391.0667 | 778.904
1392.0667 | 783.0632
1393.0823 | 781.3081
1394.0667 | 788.7216
1395.0667 | 787.8606
1396.0667 | 783.8244
1397.0667 | 804.1906
1398.0667 | 815.6213
1399.0823 | 821.0788
1400.0667 | 828.6206
1401.0823 | 809.9832
1402.0667 | 804.3269
1403.0667 | 780.2525
1404.0667 | 772.1251
1405.0823 | 790.8049
1406.0667 | 806.6706
1407.0667 | 812.746
1408.0667 | 825.0167
1409.0667 | 819.5615
1410.0667 | 791.418
1411.0667 | 799.5512
1412.0667 | 801.1335
1413.0667 | 804.7365
1414.0667 | 795.2772
1415.0667 | 785.4218
1416.0667 | 774.1063
1417.0667 | 789.5543
1418.0667 | 796.1435
1419.0667 | 788.4771
1420.0667 | 774.3078
1421.0667 | 766.815
1422.0667 | 764.0644
1423.0667 | 761.4627
1424.0667 | 772.0694
1425.0667 | 784.0179
1426.0667 | 777.9154
1427.0667 | 780.0886
1428.0667 | 781.0557
1429.0667 | 770.6713
1430.0667 | 782.8256
1431.0667 | 775.7928
1432.0667 | 760.4636
1433.0667 | 737.6244
1434.0667 | 741.4861
1435.0667 | 751.2096
1436.0667 | 778.1823
1437.0667 | 778.399
1438.0667 | 776.6794
1439.0823 | 765.5906
1440.0667 | 777.0101
1441.0823 | 787.8877
1442.0667 | 797.3644
1443.0667 | 801.7171
1444.0823 | 805.4084
1445.0667 | 796.2518
1446.0667 | 806.809
1447.0667 | 811.6385
1448.0667 | 821.355
1449.0667 | 814.4143
1450.0667 | 813.765
1451.0667 | 810.6427
1452.0667 | 811.6699
1453.0667 | 820.216
1454.0823 | 818.0066
1455.0667 | 817.5651
1456.0667 | 815.2416
1457.0667 | 798.1856
1458.0667 | 786.1367
1459.0667 | 787.6928
1460.0667 | 800.7243
1461.0667 | 808.8093
1462.0667 | 815.3416
1463.0667 | 791.1022
1464.0667 | 767.285
1465.0667 | 773.6536
1466.0667 | 788.9387
1467.0667 | 779.6759
1468.0667 | 781.1919
1469.0667 | 784.8657
1470.0667 | 783.8032
1471.0667 | 789.1663
1472.0667 | 787.1027
1473.0667 | 780.7789
1474.0667 | 794.6272
1475.0667 | 776.0363
1476.0667 | 776.864
1477.0667 | 786.9514
1478.0667 | 797.1621
1479.0667 | 805.6259
1480.0667 | 777.805
1481.0667 | 754.6007
1482.0667 | 746.4553
1483.0667 | 764.061
1484.0667 | 774.0216
1485.0667 | 782.3632
1486.0667 | 787.0829
1487.0667 | 781.2032
1488.0667 | 780.2874
1489.0667 | 770.5767
1490.0667 | 762.9256
1491.0667 | 780.2739
1492.0667 | 789.0255
1493.0667 | 781.6527
1494.0667 | 786.9245
1495.0667 | 776.0013
1496.0667 | 790.947
1497.0667 | 797.1499
1498.0667 | 794.7087
1499.0667 | 782.8316
1500.0667 | 789.4886
1501.0667 | 805.5312
1502.0667 | 793.5432
1503.0667 | 782.3791
1504.0667 | 781.8743
1505.0667 | 777.9804
1506.0667 | 776.3945
1507.0667 | 769.6519
1508.0667 | 766.2824
1509.0667 | 769.2643
1510.0667 | 774.0759
1511.0667 | 760.8493
1512.0667 | 749.26
1513.0667 | 750.6107
1514.0667 | 755.1366
1515.0667 | 759.3098
1516.0667 | 752.9588
1517.0667 | 765.4756
1518.0667 | 761.1436
1519.0667 | 753.0601
1520.0667 | 775.2458
1521.0667 | 795.6748
1522.0667 | 790.495
1523.0667 | 790.362
1524.0667 | 779.6244
1525.0667 | 778.3646
1526.0667 | 790.2214
1527.0667 | 786.3959
1528.0667 | 784.5308
1529.0667 | 800.2207
1530.0667 | 807.1077
1531.0667 | 819.1274
1532.0667 | 823.0932
1533.0667 | 829.9562
1534.0667 | 825.7403
1535.0667 | 818.7971
1536.0667 | 800.6622
1537.0667 | 783.0024
1538.0667 | 772.5298
1539.0667 | 752.5303
1540.0667 | 754.9626
1541.0667 | 764.0101
1542.0667 | 767.939
1543.0667 | 765.0783
1544.0667 | 763.815
1545.0667 | 767.9982
1546.0667 | 765.2652
1547.0667 | 766.0459
1548.0667 | 774.758
1549.0667 | 777.6877
1550.0667 | 776.5323
1551.0667 | 756.2371
1552.0667 | 753.9189
1553.0667 | 752.7217
1554.0667 | 757.1256
1555.0667 | 767.4925
1556.0667 | 783.1305
1557.0667 | 784.5229
1558.0667 | 789.9508
1559.0667 | 776.6411
1560.0667 | 771.3193
1561.0667 | 785.6479
1562.0667 | 788.8172
1563.0667 | 770.8213
1564.0667 | 770.8039
1565.0667 | 767.6131
1566.0667 | 750.7501
1567.0667 | 747.1646
1568.0667 | 745.436
1569.0667 | 770.7277
1570.0667 | 780.9215
1571.0667 | 778.1601
1572.0667 | 789.7423
1573.0667 | 783.4177
1574.0667 | 786.1364
1575.0667 | 775.3693
1576.0667 | 749.7619
1577.0667 | 739.5805
1578.0667 | 740.2297
1579.0667 | 747.7137
1580.0667 | 758.9926
1581.0667 | 746.4904
1582.0667 | 731.6094
1583.0667 | 738.4554
1584.0667 | 747.8575
1585.0667 | 742.4438
1586.0667 | 739.8642
1587.0667 | 740.1858
1588.0667 | 746.8981
1589.0667 | 744.159
1590.0667 | 729.2744
1591.0667 | 726.8531
1592.0667 | 718.5103
1593.0667 | 719.6778
1594.0667 | 705.9997
1595.0667 | 704.7083
1596.0667 | 702.9855
1597.0667 | 718.404
1598.0667 | 727.9136
1599.0667 | 737.742
1600.0667 | 737.1322
1601.0667 | 733.4801
1602.0667 | 747.6463
1603.0667 | 769.2999
1604.0667 | 782.3282
1605.0667 | 781.5187
1606.0667 | 786.098
1607.0667 | 784.9961
1608.0667 | 784.8163
1609.0667 | 796.9435
1610.0667 | 799.0601
1611.0667 | 791.6061
1612.0667 | 810.5326
1613.0667 | 810.5851
1614.0667 | 823.9974
1615.0667 | 822.8915
1616.0667 | 818.3347
1617.0667 | 803.1945
1618.0667 | 817.7453
1619.0667 | 821.758
1620.0667 | 829.094
1621.0667 | 831.1237
1622.0667 | 816.348
1623.0667 | 819.8755
1624.0667 | 831.3473
1625.0667 | 831.5599
1626.0667 | 828.8664
1627.0667 | 815.1728
1628.0667 | 802.3045
1629.0823 | 790.258
1630.0667 | 794.4692
1631.0667 | 796.2781
1632.0667 | 808.9075
1633.0667 | 811.1148
1634.0667 | 803.0822
1635.0667 | 786.8561
1636.0667 | 778.4949
1637.0667 | 776.0004
1638.0667 | 781.0678
1639.0667 | 784.8232
1640.0667 | 776.2736
1641.0667 | 780.4794
1642.0667 | 790.7264
1643.0667 | 795.2321
1644.0823 | 784.5261
1645.0667 | 775.1039
1646.0667 | 775.222
1647.0667 | 786.3579
1648.0667 | 794.0928
1649.0667 | 791.5204
1650.0667 | 790.8922
1651.0667 | 798.2401
1652.0667 | 781.4521
1653.0667 | 781.5899
1654.0667 | 795.0409
1655.0667 | 796.58
1656.0667 | 784.1893
1657.0667 | 762.8048
1658.0667 | 740.595
1659.0667 | 720.9976
1660.0667 | 726.0067
1661.0667 | 742.9351
1662.0667 | 757.3715
1663.0667 | 784.0028
1664.0667 | 796.9536
1665.0667 | 781.7236
1666.0667 | 774.7618
1667.0667 | 769.7562
1668.0667 | 780.026
1669.0823 | 772.8141
1670.0667 | 755.0963
1671.0667 | 760.4862
1672.0667 | 772.572
1673.0667 | 774.7552
1674.0667 | 784.4679
1675.0667 | 770.0066
1676.0667 | 748.6968
1677.0667 | 722.7633
1678.0667 | 738.3547
1679.0667 | 745.6077
1680.0667 | 756.9355
1681.0667 | 750.9708
1682.0667 | 735.7758
1683.0667 | 733.8513
1684.0667 | 736.2767
1685.0667 | 756.3378
1686.0667 | 762.5077
1687.0667 | 774.5052
1688.0667 | 764.6302
1689.0667 | 773.1156
1690.0667 | 774.5106
1691.0667 | 780.0836
1692.0667 | 768.0678
1693.0667 | 759.3692
1694.0667 | 764.7669
1695.0667 | 776.2749
1696.0667 | 780.3429
1697.0667 | 788.7894
1698.0667 | 783.939
1699.0667 | 769.5744
1700.0667 | 764.1168
1701.0667 | 771.7218
1702.0667 | 766.2207
1703.0667 | 743.5993
1704.0667 | 742.5479
1705.0667 | 738.1806
1706.0667 | 764.1557
1707.0667 | 779.3218
1708.0667 | 768.1349
1709.0667 | 765.5093
1710.0667 | 753.1649
1711.0667 | 740.0229
1712.0667 | 731.7513
1713.0667 | 748.3942
1714.0667 | 750.0951
1715.0667 | 745.3612
1716.0667 | 744.7256
1717.0667 | 760.7809
1718.0667 | 766.497
1719.0667 | 774.9699
1720.0667 | 759.4173
1721.0667 | 754.3534
1722.0667 | 769.7422
1723.0667 | 779.7606
1724.0667 | 770.8437
1725.0667 | 767.7736
1726.0667 | 756.4737
1727.0667 | 745.1548
1728.0667 | 749.5736
1729.0823 | 750.5171
1730.0667 | 760.9819
1731.0667 | 771.9874
1732.0667 | 766.1389
1733.0667 | 739.2434
1734.0667 | 726.887
1735.0667 | 732.6434
1736.0667 | 717.6469
1737.0667 | 728.8476
1738.0667 | 727.7158
1739.0667 | 723.438
1740.0667 | 747.1054
1741.0667 | 746.1899
1742.0667 | 736.1615
1743.0667 | 750.1229
1744.0667 | 758.6226
1745.0667 | 759.8806
1746.0667 | 746.2057
1747.0667 | 746.0798
1748.0667 | 755.2964
1749.0667 | 736.7665
1750.0667 | 743.7056
1751.0667 | 742.1849
1752.0667 | 754.0216
1753.0667 | 755.3263
1754.0667 | 778.9892
1755.0667 | 777.4199
1756.0667 | 778.1401
1757.0667 | 786.1108
1758.0667 | 774.4218
1759.0667 | 769.2863
1760.0667 | 758.8796
1761.0667 | 774.6896
1762.0667 | 765.8492
1763.0667 | 766.3617
1764.0667 | 743.1527
1765.0667 | 723.0016
1766.0667 | 709.9937
1767.0667 | 722.6922
1768.0667 | 709.3769
1769.0823 | 728.8167
1770.0667 | 741.726
1771.0667 | 733.7852
1772.0667 | 732.9795
1773.0667 | 745.8875
1774.0667 | 757.5964
1775.0667 | 775.235
1776.0667 | 771.239
1777.0667 | 762.323
1778.0667 | 756.1341
1779.0667 | 754.8931
1780.0667 | 763.26
1781.0667 | 761.5652
1782.0667 | 766.1733
1783.0667 | 759.9748
1784.0823 | 756.3577
1785.0667 | 780.4775
1786.0667 | 779.0578
1787.0667 | 784.1573
1788.0667 | 784.1116
1789.0667 | 785.8309
1790.0667 | 770.4926
1791.0667 | 774.3224
1792.0667 | 780.8003
1793.0667 | 768.9596
1794.0667 | 776.7979
1795.0667 | 778.244
1796.0667 | 768.1497
1797.0667 | 758.2565
1798.0667 | 748.9665
1799.0667 | 729.9952
1800.0823 | 720.5245
1801.0667 | 723.2938
1802.0667 | 735.878
1803.0667 | 740.012
1804.0667 | 747.265
1805.0667 | 758.5378
1806.0667 | 752.2222
1807.0667 | 739.0036
1808.0667 | 749.4259
1809.0667 | 739.9828
1810.0667 | 741.6845
1811.0667 | 760.5298
1812.0667 | 776.443
1813.0667 | 784.6785
1814.0667 | 766.8889
1815.0667 | 766.3531
1816.0667 | 763.9435
1817.0667 | 768.3415
1818.0667 | 759.6389
1819.0667 | 750.0443
1820.0667 | 754.1045
1821.0667 | 772.0657
1822.0667 | 781.2265
1823.0667 | 779.1584
1824.0667 | 771.4438
1825.0667 | 757.7954
1826.0667 | 748.0174
1827.0667 | 724.6021
1828.0667 | 732.2349
1829.0667 | 724.3028
1830.0667 | 729.2186
1831.0667 | 740.9607
1832.0667 | 749.782
1833.0667 | 767.7786
1834.0667 | 786.6322
1835.0667 | 796.5877
1836.0667 | 802.0113
1837.0667 | 808.5068
1838.0667 | 791.823
1839.0667 | 779.5587
1840.0667 | 790.3683
1841.0667 | 803.8085
1842.0667 | 802.8527
1843.0667 | 804.6188
1844.0667 | 801.2684
1845.0667 | 796.8039
1846.0667 | 788.5348
1847.0667 | 780.1965
1848.0667 | 779.209
1849.0667 | 788.1457
1850.0667 | 787.4981
1851.0667 | 778.2253
1852.0667 | 775.9778
1853.0667 | 757.7412
1854.0667 | 760.0802
1855.0667 | 764.3807
1856.0667 | 766.7104
1857.0667 | 773.4305
1858.0667 | 780.2124
1859.0667 | 760.1336
1860.0667 | 771.6959
1861.0667 | 779.268
1862.0667 | 783.8992
1863.0667 | 792.0353
1864.0667 | 804.6107
1865.0667 | 810.1266
1866.0667 | 816.5276
1867.0667 | 826.2757
1868.0667 | 833.455
1869.0667 | 828.8945
1870.0667 | 817.124
1871.0667 | 820.4751
1872.0667 | 823.5547
1873.0667 | 828.5198
1874.0667 | 830.4874
1875.0667 | 831.162
1876.0667 | 833.5723
1877.0667 | 831.7662
1878.0667 | 817.7124
1879.0667 | 805.2838
1880.0667 | 798.8509
1881.0667 | 807.8198
1882.0667 | 805.1533
1883.0667 | 792.6298
1884.0667 | 774.5695
1885.0667 | 760.8185
1886.0667 | 747.5256
1887.0667 | 754.6222
1888.0667 | 736.661
1889.0667 | 737.1824
1890.0667 | 755.9223
1891.0667 | 747.6701
1892.0667 | 730.56
1893.0667 | 737.9727
1894.0667 | 727.2357
1895.0667 | 726.8447
1896.0667 | 755.7784
1897.0667 | 763.4323
1898.0667 | 782.8378
1899.0667 | 777.306
1900.0667 | 783.0518
1901.0667 | 797.9618
1902.0667 | 805.3335
1903.0667 | 805.4069
1904.0667 | 805.7067
1905.0667 | 809.0564
1906.0667 | 815.9407
1907.0667 | 813.7158
1908.0667 | 795.5922
1909.0667 | 808.9863
1910.0667 | 815.6426
1911.0667 | 812.9008
1912.0667 | 795.2659
1913.0667 | 780.9665
1914.0667 | 775.4834
1915.0667 | 784.4727
1916.0667 | 789.6808
1917.0667 | 789.1555
1918.0667 | 789.3522
1919.0667 | 787.9795
1920.0667 | 797.8505
1921.0667 | 798.8082
1922.0667 | 816.6537
1923.0667 | 826.1879
1924.0667 | 835.8988
1925.0667 | 836.3349
1926.0667 | 840.8366
1927.0667 | 849.449
1928.0667 | 848.3482
1929.0667 | 840.8092
1930.0667 | 835.4941
1931.0667 | 830.7347
1932.0667 | 829.0801
1933.0667 | 819.4527
1934.0667 | 818.3109
1935.0667 | 827.1344
1936.0667 | 823.7565
1937.0667 | 814.2954
1938.0667 | 820.9718
1939.0667 | 824.9231
1940.0667 | 829.0316
1941.0667 | 828.1143
1942.0667 | 833.7767
1943.0667 | 833.8004
1944.0667 | 818.544
1945.0823 | 834.3297
1946.0667 | 841.3711
1947.0667 | 832.7103
1948.0667 | 813.8862
1949.0667 | 809.9603
1950.0667 | 802.2412
1951.0667 | 814.3017
1952.0667 | 807.5523
1953.0667 | 794.9192
1954.0667 | 774.0954
1955.0667 | 766.2259
1956.0667 | 747.232
1957.0667 | 756.5001
1958.0667 | 754.8988
1959.0823 | 764.2561
1960.0667 | 766.3999
1961.0667 | 762.8199
1962.0667 | 768.5963
1963.0667 | 750.3271
1964.0667 | 733.6827
1965.0667 | 742.1397
1966.0667 | 733.7894
1967.0667 | 723.6584
1968.0667 | 734.1556
1969.0667 | 741.8767
1970.0667 | 755.6635
1971.0667 | 766.9819
1972.0667 | 752.0224
1973.0667 | 734.1017
1974.0823 | 723.0592
1975.0823 | 720.7968
1976.0667 | 716.2382
1977.0667 | 710.7859
1978.0667 | 721.1002
1979.0667 | 731.2226
1980.0667 | 756.6528
1981.0667 | 757.2848
1982.0667 | 760.6622
1983.0667 | 761.5123
1984.0667 | 765.4076
1985.0667 | 758.9344
1986.0667 | 768.6129
1987.0667 | 761.5382
1988.0667 | 763.0574
1989.0667 | 770.1382
1990.0667 | 783.7157
1991.0667 | 780.6508
1992.0667 | 786.6209
1993.0667 | 795.0951
1994.0667 | 808.7606
1995.0667 | 802.3993
1996.0667 | 797.8575
1997.0667 | 771.1673
1998.0667 | 781.0027
1999.0667 | 783.9955
2000.0667 | 781.5215
2001.0667 | 787.9951
2002.0667 | 800.5175
2003.0667 | 804.0766
2004.0667 | 793.6715
2005.0667 | 787.9614
2006.0667 | 785.1456
2007.0667 | 798.2116
2008.0667 | 796.4071
2009.0667 | 784.4807
2010.0667 | 772.5326
2011.0667 | 794.3999
2012.0667 | 794.4141
2013.0667 | 779.312
2014.0823 | 749.4641
2015.0667 | 752.2824
2016.0667 | 739.9954
2017.0667 | 721.045
2018.0667 | 730.5935
2019.0667 | 750.752
2020.0667 | 764.9291
2021.0667 | 784.3431
2022.0667 | 788.6105
2023.0667 | 805.0108
2024.0667 | 798.8472
2025.0667 | 795.3431
2026.0667 | 778.5403
2027.0667 | 769.2483
2028.0667 | 773.1496
2029.0667 | 767.8243
2030.0667 | 771.8815
2031.0667 | 757.5745
2032.0667 | 764.9607
2033.0667 | 773.3194
2034.0667 | 772.5104
2035.0667 | 776.1007
2036.0667 | 794.9654
2037.0667 | 816.3332
2038.0667 | 833.3941
2039.0667 | 836.7235
2040.0667 | 844.1947
2041.0667 | 847.0551
2042.0667 | 853.065
2043.0667 | 848.4082
2044.0667 | 843.8208
2045.0667 | 837.9961
2046.0667 | 816.8787
2047.0667 | 809.004
2048.0667 | 818.9114
2049.0667 | 823.7518
2050.0667 | 819.1555
2051.0667 | 820.2104
2052.0667 | 820.7204
2053.0667 | 816.5057
2054.0667 | 801.2227
2055.0667 | 784.7261
2056.0667 | 792.8437
2057.0667 | 791.5551
2058.0667 | 784.2378
2059.0667 | 798.167
2060.0667 | 800.4349
2061.0667 | 795.4509
2062.0667 | 786.0718
2063.0667 | 779.8853
2064.0667 | 781.2858
2065.0823 | 775.0271
2066.0667 | 785.4995
2067.0667 | 800.8401
2068.0667 | 813.6524
2069.0667 | 818.694
2070.0667 | 805.0002
2071.0667 | 803.887
2072.0667 | 788.3388
2073.0667 | 788.0636
2074.0667 | 804.0039
2075.0667 | 796.1104
2076.0667 | 800.3352
2077.0667 | 792.2339
2078.0667 | 789.538
2079.0667 | 793.2399
2080.0667 | 803.3536
2081.0667 | 819.8352
2082.0667 | 814.2809
2083.0667 | 804.53
2084.0667 | 792.8453
2085.0667 | 791.2212
2086.0667 | 794.0449
2087.0667 | 776.8342
2088.0667 | 763.3919
2089.0667 | 764.5083
2090.0667 | 752.8484
2091.0667 | 746.0108
2092.0667 | 764.0444
2093.0667 | 787.6886
2094.0667 | 795.9768
2095.0667 | 785.7095
2096.0667 | 795.4699
2097.0667 | 778.2853
2098.0667 | 774.1633
2099.0823 | 772.0704
2100.0667 | 749.6325
2101.0667 | 742.4367
2102.0667 | 743.6004
2103.0667 | 755.4078
2104.0667 | 753.6708
2105.0667 | 756.9443
2106.0667 | 760.5172
2107.0667 | 760.6036
2108.0667 | 755.7791
2109.0667 | 736.1051
2110.0667 | 724.835
2111.0667 | 714.4721
2112.0667 | 699.2224
2113.0667 | 701.1522
2114.0823 | 697.0649
2115.0667 | 710.7692
2116.0667 | 707.8034
2117.0667 | 705.6057
2118.0667 | 722.3011
2119.0667 | 735.2095
2120.0667 | 747.5239
2121.0667 | 746.0242
2122.0667 | 757.7136
2123.0667 | 751.1565
2124.0667 | 754.6723
2125.0667 | 774.4145
2126.0667 | 791.1921
2127.0667 | 805.0775
2128.0667 | 805.341
2129.0667 | 821.4873
2130.0667 | 827.9057
2131.0667 | 816.4803
2132.0667 | 821.8687
2133.0667 | 828.5302
2134.0667 | 817.1456
2135.0667 | 820.9622
2136.0667 | 805.8943
2137.0823 | 799.9831
2138.0823 | 792.8753
2139.0667 | 798.9361
2140.0667 | 803.1789
2141.0667 | 794.6054
2142.0667 | 783.1642
2143.0667 | 769.5461
2144.0667 | 768.3461
2145.0667 | 787.0306
2146.0667 | 788.5747
2147.0667 | 790.1334
2148.0667 | 795.5362
2149.0667 | 778.6681
2150.0667 | 778.3657
2151.0667 | 780.788
2152.0667 | 779.8225
2153.0667 | 782.4347
2154.0667 | 772.4853
2155.0667 | 765.6884
2156.0667 | 778.0003
2157.0667 | 784.9776
2158.0667 | 775.3492
2159.0667 | 777.2987
2160.0667 | 793.8385
2161.0667 | 798.3596
2162.0667 | 802.3009
2163.0667 | 801.9125
2164.0667 | 793.713
2165.0667 | 804.7563
2166.0667 | 792.1716
2167.0667 | 793.712
2168.0667 | 794.8218
2169.0667 | 788.0393
2170.0667 | 787.575
2171.0667 | 786.4837
2172.0667 | 789.1539
2173.0667 | 803.8368
2174.0667 | 807.5416
2175.0667 | 798.0584
2176.0667 | 789.1319
2177.0667 | 769.1359
2178.0667 | 751.282
2179.0667 | 751.1242
2180.0667 | 744.2113
2181.0667 | 736.6182
2182.0667 | 742.7634
2183.0667 | 723.8281
2184.0667 | 725.099
2185.0667 | 725.8449
2186.0667 | 726.2558
2187.0667 | 743.5194
2188.0667 | 754.4881
2189.0667 | 761.6756
2190.0667 | 768.5543
2191.0667 | 762.9829
2192.0667 | 756.6875
2193.0667 | 760.6548
2194.0667 | 784.5445
2195.0667 | 796.0406
2196.0667 | 801.6553
2197.0667 | 788.574
2198.0667 | 787.411
2199.0667 | 766.2865
2200.0667 | 769.0045
2201.0667 | 762.7948
2202.0667 | 751.4462
2203.0667 | 734.9029
2204.0667 | 729.9237
2205.0667 | 739.1822
2206.0667 | 740.0732
2207.0667 | 728.056
2208.0667 | 743.1075
2209.0667 | 758.0726
2210.0667 | 760.4687
2211.0667 | 776.8448
2212.0667 | 767.6218
2213.0667 | 768.9705
2214.0667 | 783.6789
2215.0667 | 795.5366
2216.0667 | 805.8914
2217.0667 | 790.2048
2218.0667 | 801.4154
2219.0667 | 819.6805
2220.0667 | 812.2531
2221.0667 | 807.4651
2222.0667 | 801.087
2223.0667 | 808.1743
2224.0667 | 819.1725
2225.0667 | 830.8485
2226.0667 | 827.3145
2227.0667 | 827.5243
2228.0667 | 829.2217
2229.0667 | 816.4626
2230.0667 | 801.196
2231.0667 | 779.3474
2232.0667 | 761.6942
2233.0667 | 757.3655
2234.0667 | 734.4341
2235.0667 | 733.376
2236.0667 | 733.8562
2237.0667 | 712.9779
2238.0667 | 713.7042
2239.0667 | 735.078
2240.0667 | 764.5709
2241.0667 | 783.3458
2242.0667 | 794.4716
2243.0667 | 793.5601
2244.0667 | 786.7884
2245.0667 | 780.1683
2246.0667 | 780.7761
2247.0667 | 802.1632
2248.0667 | 804.3881
2249.0667 | 808.4833
2250.0667 | 813.3087
2251.0667 | 826.0638
2252.0667 | 825.834
2253.0667 | 828.1642
2254.0667 | 820.6297
2255.0667 | 815.7195
2256.0667 | 820.845
2257.0667 | 822.447
2258.0667 | 788.9729
2259.0667 | 769.7494
2260.0667 | 775.0549
2261.0667 | 775.3737
2262.0667 | 765.6244
2263.0667 | 760.481
2264.0667 | 751.0098
2265.0667 | 753.1723
2266.0667 | 751.8345
2267.0667 | 746.619
2268.0667 | 750.1965
2269.0667 | 774.3948
2270.0667 | 765.5735
2271.0667 | 763.7549
2272.0667 | 741.5584
2273.0667 | 731.9752
2274.0823 | 726.4504
2275.0667 | 738.3824
2276.0667 | 759.0825
2277.0667 | 773.9897
2278.0667 | 771.6931
2279.0667 | 768.7318
2280.0667 | 758.7259
2281.0667 | 761.4095
2282.0667 | 745.8254
2283.0667 | 724.7006
2284.0667 | 733.4551
2285.0667 | 755.0821
2286.0667 | 769.2746
2287.0667 | 758.4201
2288.0667 | 742.1644
2289.0823 | 749.8975
2290.0667 | 754.7661
2291.0667 | 739.8725
2292.0667 | 726.4819
2293.0667 | 744.8594
2294.0667 | 760.2088
2295.0667 | 765.1298
2296.0667 | 782.3919
2297.0667 | 790.2577
2298.0667 | 798.2942
2299.0667 | 806.0112
2300.0667 | 821.8326
2301.0667 | 834.4054
2302.0667 | 823.0799
2303.0667 | 813.6072
2304.0667 | 821.1773
2305.0667 | 812.7767
2306.0667 | 814.2045
2307.0667 | 824.5923
2308.0667 | 827.4287
2309.0667 | 832.0459
2310.0667 | 844.8697
2311.0667 | 844.5807
2312.0667 | 834.1296
2313.0667 | 824.6795
2314.0667 | 831.9471
2315.0667 | 826.217
2316.0667 | 841.6012
2317.0667 | 845.2267
2318.0667 | 835.3872
2319.0667 | 838.4239
2320.0667 | 816.1369
2321.0667 | 799.669
2322.0667 | 814.9512
2323.0667 | 831.4404
2324.0667 | 840.3343
2325.0667 | 850.9196
2326.0667 | 845.8846
2327.0667 | 827.738
2328.0667 | 821.2436
2329.0667 | 804.4688
2330.0667 | 799.3632
2331.0667 | 804.8322
2332.0667 | 819.9089
2333.0667 | 829.4563
2334.0823 | 815.1371
2335.0667 | 802.4805
2336.0667 | 794.3255
2337.0667 | 795.7154
2338.0667 | 809.3416
2339.0667 | 817.7519
2340.0667 | 829.3326
2341.0667 | 829.3093
2342.0667 | 835.6995
2343.0667 | 843.9693
2344.0667 | 846.1626
2345.0667 | 840.5593
2346.0667 | 846.5994
2347.0667 | 846.8848
2348.0667 | 847.4514
2349.0667 | 846.2624
2350.0667 | 847.8707
2351.0667 | 850.8203
2352.0667 | 839.9815
2353.0667 | 845.4086
2354.0667 | 842.566
2355.0667 | 821.6867
2356.0667 | 798.7868
2357.0667 | 772.8491
2358.0667 | 780.6077
2359.0667 | 786.3282
2360.0667 | 768.2036
2361.0667 | 742.6691
2362.0667 | 758.1679
2363.0667 | 761.9064
2364.0667 | 755.2027
2365.0667 | 757.4
2366.0667 | 759.0446
2367.0667 | 753.6278
2368.0667 | 742.6669
2369.0667 | 742.8978
2370.0667 | 749.9005
2371.0667 | 767.075
2372.0667 | 778.8456
2373.0667 | 779.421
2374.0823 | 781.205
2375.0667 | 787.7879
2376.0667 | 780.3429
2377.0667 | 784.401
2378.0667 | 793.755
2379.0667 | 804.2241
2380.0667 | 802.3897
2381.0667 | 802.823
2382.0667 | 808.7656
2383.0667 | 808.453
2384.0667 | 819.3777
2385.0667 | 820.7154
2386.0667 | 831.4703
2387.0667 | 831.3106
2388.0667 | 833.38
2389.0823 | 838.5425
2390.0667 | 838.3713
2391.0667 | 824.2516
2392.0667 | 811.3217
2393.0667 | 809.1605
2394.0667 | 809.4597
2395.0667 | 823.8392
2396.0667 | 815.1716
2397.0667 | 792.6322
2398.0667 | 782.9603
2399.0667 | 798.469
2400.0667 | 799.6209
2401.0667 | 796.9633
2402.0667 | 817.6686
2403.0667 | 823.3962
2404.0667 | 807.8995
2405.0667 | 793.7617
2406.0667 | 774.1068
2407.0667 | 782.2946
2408.0667 | 773.0954
2409.0667 | 775.8225
2410.0667 | 792.8363
2411.0667 | 803.6879
2412.0667 | 810.8231
2413.0667 | 824.3606
2414.0667 | 828.5692
2415.0667 | 833.3945
2416.0667 | 838.6366
2417.0667 | 846.5286
2418.0667 | 851.5895
2419.0667 | 834.0371
2420.0667 | 806.9786
2421.0667 | 783.4733
2422.0667 | 792.5296
2423.0667 | 788.9592
2424.0667 | 790.505
2425.0667 | 804.2451
2426.0667 | 804.9175
2427.0667 | 802.1729
2428.0667 | 768.8672
2429.0667 | 743.9058
2430.0667 | 753.5513
2431.0667 | 760.1055
2432.0667 | 785.4177
2433.0667 | 786.2434
2434.0667 | 789.4705
2435.0667 | 798.1122
2436.0667 | 803.4311
2437.0667 | 805.1709
2438.0667 | 799.0978
2439.0667 | 781.283
2440.0667 | 788.3355
2441.0667 | 787.5968
2442.0667 | 783.8747
2443.0667 | 795.6909
2444.0667 | 790.0602
2445.0667 | 802.865
2446.0667 | 806.0098
2447.0667 | 819.2331
2448.0667 | 821.131
2449.0667 | 821.3935
2450.0667 | 812.8432
2451.0667 | 818.4776
2452.0667 | 801.9238
2453.0667 | 812.3843
2454.0667 | 818.449
2455.0667 | 820.236
2456.0667 | 801.7261
2457.0667 | 792.5792
2458.0667 | 789.6181
2459.0667 | 796.7497
2460.0667 | 791.3977
2461.0667 | 788.7249
2462.0667 | 773.6211
2463.0667 | 761.8659
2464.0667 | 765.8568
2465.0667 | 771.5974
2466.0667 | 775.5599
2467.0667 | 765.2908
2468.0667 | 767.0824
2469.0667 | 752.0433
2470.0667 | 759.7034
2471.0667 | 765.925
2472.0667 | 772.1437
2473.0667 | 776.2364
2474.0667 | 747.4679
2475.0667 | 749.364
2476.0667 | 774.7313
2477.0667 | 790.268
2478.0667 | 801.3239
2479.0667 | 796.0368
2480.0667 | 811.9579
2481.0667 | 815.012
2482.0667 | 820.1423
2483.0667 | 826.8752
2484.0667 | 830.4431
2485.0667 | 821.1514
2486.0667 | 831.1625
2487.0667 | 833.5819
2488.0667 | 826.4904
2489.0667 | 816.7242
2490.0667 | 824.646
2491.0667 | 831.2512
2492.0667 | 815.8494
2493.0667 | 819.4113
2494.0667 | 818.832
2495.0667 | 781.184
2496.0667 | 766.0158
2497.0667 | 763.098
2498.0667 | 785.6695
2499.0667 | 793.1982
2500.0667 | 811.1793
2501.0667 | 815.1555
2502.0667 | 821.5879
2503.0667 | 822.6564
2504.0667 | 831.6251
2505.0667 | 837.5336
2506.0667 | 836.3195
2507.0667 | 833.363
2508.0667 | 831.0939
2509.0823 | 840.9761
2510.0667 | 840.9151
2511.0667 | 834.656
2512.0667 | 826.676
2513.0667 | 834.3463
2514.0667 | 839.9567
2515.0667 | 840.746
2516.0667 | 824.491
2517.0667 | 826.626
2518.0667 | 831.8183
2519.0667 | 846.9926
2520.0667 | 850.8041
2521.0667 | 851.9383
2522.0667 | 847.771
2523.0667 | 839.9852
2524.0667 | 836.8852
2525.0667 | 836.4761
2526.0667 | 807.2112
2527.0667 | 784.3814
2528.0667 | 780.2052
2529.0667 | 769.9466
2530.0667 | 782.0919
2531.0667 | 797.4892
2532.0667 | 788.0927
2533.0667 | 772.9115
2534.0667 | 795.4299
2535.0667 | 803.8264
2536.0667 | 803.2645
2537.0667 | 802.2964
2538.0667 | 817.81
2539.0667 | 821.0297
2540.0667 | 818.2243
2541.0667 | 807.2454
2542.0667 | 822.3905
2543.0667 | 821.7721
2544.0667 | 824.2105
2545.0667 | 812.9295
2546.0667 | 816.4276
2547.0667 | 812.5437
2548.0667 | 814.3509
2549.0667 | 826.9672
2550.0667 | 822.6506
2551.0667 | 824.735
2552.0667 | 827.9683
2553.0667 | 823.4523
2554.0667 | 822.5077
2555.0667 | 810.215
2556.0667 | 780.387
2557.0667 | 774.9092
2558.0667 | 799.7723
2559.0667 | 805.8491
2560.0667 | 810.4049
2561.0667 | 823.1547
2562.0667 | 833.1645
2563.0667 | 826.4618
2564.0667 | 829.4709
2565.0667 | 824.2427
2566.0667 | 820.8671
2567.0667 | 793.0728
2568.0667 | 783.3487
2569.0667 | 794.2138
2570.0667 | 810.6782
2571.0667 | 816.0295
2572.0667 | 820.11
2573.0667 | 819.0213
2574.0667 | 802.948
2575.0667 | 812.3832
2576.0667 | 820.9569
2577.0667 | 835.6903
2578.0667 | 833.2004
2579.0667 | 842.7627
2580.0667 | 844.4858
2581.0667 | 832.8401
2582.0667 | 840.8142
2583.0667 | 840.5336
2584.0667 | 834.9527
2585.0667 | 817.0704
2586.0667 | 822.2562
2587.0667 | 806.7276
2588.0667 | 801.079
2589.0667 | 799.0989
2590.0667 | 797.9093
2591.0667 | 770.4404
2592.0667 | 755.7411
2593.0667 | 762.1623
2594.0823 | 786.7984
2595.0667 | 795.7545
2596.0667 | 807.1639
2597.0667 | 807.4572
2598.0667 | 818.438
2599.0667 | 832.9652
2600.0667 | 837.2989
2601.0667 | 842.0299
2602.0667 | 844.1092
2603.0667 | 823.4189
2604.0667 | 797.6055
2605.0667 | 789.1378
2606.0667 | 777.3343
2607.0667 | 779.37
2608.0667 | 768.7797
2609.0823 | 764.1973
2610.0667 | 750.1091
2611.0667 | 751.8477
2612.0667 | 765.2528
2613.0667 | 790.1044
2614.0667 | 795.9831
2615.0667 | 796.294
2616.0667 | 802.6817
2617.0667 | 815.7361
2618.0667 | 822.3906
2619.0667 | 816.0502
2620.0667 | 811.2376
2621.0667 | 824.2744
2622.0667 | 828.6649
2623.0667 | 830.2792
2624.0667 | 835.7772
2625.0667 | 825.8638
2626.0667 | 806.5788
2627.0667 | 809.6655
2628.0667 | 808.123
2629.0667 | 813.1314
2630.0667 | 813.2656
2631.0667 | 810.2992
2632.0667 | 809.0004
2633.0667 | 813.9375
2634.0667 | 807.6555
2635.0667 | 822.173
2636.0667 | 824.7764
2637.0667 | 827.4238
2638.0667 | 817.2236
2639.0667 | 824.5475
2640.0667 | 838.98
2641.0667 | 847.1664
2642.0667 | 845.994
2643.0667 | 839.6144
2644.0667 | 828.7012
2645.0667 | 825.9414
2646.0667 | 827.2246
2647.0667 | 801.8915
2648.0667 | 777.5452
2649.0667 | 770.5501
2650.0667 | 746.7982
2651.0667 | 743.6453
2652.0667 | 734.3031
2653.0667 | 714.9969
2654.0667 | 708.3824
2655.0667 | 708.6509
2656.0667 | 723.4968
2657.0667 | 757.3102
2658.0667 | 762.3574
2659.0667 | 779.6815
2660.0667 | 774.2238
2661.0667 | 758.7984
2662.0667 | 741.3118
2663.0667 | 756.8441
2664.0667 | 736.0315
2665.0667 | 725.0494
2666.0667 | 717.8764
2667.0667 | 716.0917
2668.0667 | 727.8954
2669.0667 | 723.0927
2670.0667 | 723.5116
2671.0667 | 728.7764
2672.0667 | 711.3339
2673.0667 | 695.4203
2674.0667 | 694.3574
2675.0667 | 687.0356
2676.0667 | 677.5613
2677.0667 | 674.6883
2678.0667 | 678.5372
2679.0667 | 676.5522
2680.0667 | 673.5526
2681.0667 | 685.0128
2682.0667 | 685.1435
2683.0667 | 682.5091
2684.0667 | 707.3996
2685.0667 | 715.043
2686.0667 | 730.4153
2687.0667 | 745.8561
2688.0667 | 751.2404
2689.0667 | 757.4215
2690.0667 | 753.3304
2691.0667 | 743.464
2692.0667 | 745.3652
2693.0667 | 734.865
2694.0667 | 719.5884
2695.0667 | 707.0811
2696.0667 | 724.4796
2697.0667 | 737.213
2698.0667 | 742.2437
2699.0667 | 740.2095
2700.0667 | 721.1399
2701.0667 | 704.4748
2702.0667 | 699.6598
2703.0667 | 702.8149
2704.0823 | 718.1771
2705.0667 | 719.2989
2706.0667 | 708.0262
2707.0667 | 702.8777
2708.0667 | 696.933
2709.0667 | 710.9639
2710.0667 | 692.3143
2711.0667 | 691.7855
2712.0667 | 696.4532
2713.0667 | 691.6388
2714.0667 | 679.9775
2715.0667 | 687.4881
2716.0667 | 690.8907
2717.0667 | 686.0101
2718.0667 | 700.9043
2719.0667 | 718.9234
2720.0667 | 737.4932
2721.0667 | 735.8568
2722.0667 | 734.117
2723.0667 | 755.7694
2724.0667 | 754.9089
2725.0667 | 756.3066
2726.0667 | 778.262
2727.0667 | 789.529
2728.0667 | 800.5246
2729.0667 | 802.3426
2730.0667 | 799.3124
2731.0667 | 799.386
2732.0667 | 782.0161
2733.0667 | 778.3223
2734.0667 | 786.5257
2735.0667 | 809.4676
2736.0667 | 821.7645
2737.0667 | 832.2501
2738.0667 | 825.9678
2739.0667 | 805.2974
2740.0667 | 812.1718
2741.0667 | 822.1003
2742.0667 | 819.8055
2743.0667 | 824.2646
2744.0667 | 826.2729
2745.0667 | 816.7625
2746.0667 | 809.7918
2747.0667 | 823.0081
2748.0667 | 803.3297
2749.0667 | 811.4081
2750.0667 | 798.052
2751.0667 | 793.6464
2752.0667 | 800.4894
2753.0667 | 806.8916
2754.0667 | 813.8425
2755.0667 | 803.4499
2756.0667 | 805.4009
2757.0667 | 813.589
2758.0667 | 805.8668
2759.0667 | 793.9301
2760.0667 | 757.0358
2761.0667 | 759.3128
2762.0667 | 764.6297
2763.0667 | 770.7456
2764.0667 | 771.0476
2765.0667 | 766.225
2766.0667 | 749.3793
2767.0667 | 756.8924
2768.0667 | 752.6645
2769.0823 | 755.7879
2770.0667 | 757.4456
2771.0667 | 757.0681
2772.0667 | 745.9039
2773.0667 | 717.2986
2774.0667 | 692.0201
2775.0667 | 691.2496
2776.0667 | 716.424
2777.0667 | 714.9327
2778.0823 | 700.508
2779.0667 | 709.4422
2780.0667 | 720.1576
2781.0823 | 725.9176
2782.0667 | 759.2639
2783.0667 | 760.8687
2784.0667 | 755.6481
2785.0667 | 767.831
2786.0667 | 777.7612
2787.0667 | 784.4653
2788.0667 | 801.961
2789.0667 | 794.521
2790.0667 | 768.9153
2791.0667 | 768.4043
2792.0667 | 754.8764
2793.0667 | 754.3474
2794.0667 | 745.9612
2795.0667 | 726.7197
2796.0667 | 720.1037
2797.0667 | 729.5984
2798.0667 | 748.117
2799.0667 | 755.2589
2800.0667 | 764.5339
2801.0667 | 781.3817
2802.0667 | 785.4992
2803.0823 | 782.4167
2804.0823 | 765.9637
2805.0667 | 780.8661
2806.0667 | 797.668
2807.0667 | 811.5029
2808.0667 | 811.6522
2809.0667 | 799.9974
2810.0667 | 797.0511
2811.0667 | 807.2348
2812.0667 | 814.5928
2813.0667 | 828.091
2814.0823 | 825.8401
2815.0667 | 805.4628
2816.0667 | 785.1158
2817.0667 | 778.5621
2818.0667 | 753.5182
2819.0667 | 742.1575
2820.0667 | 742.4548
2821.0667 | 744.0605
2822.0667 | 759.3925
2823.0667 | 761.0749
2824.0667 | 738.3378
2825.0667 | 722.0873
2826.0667 | 729.5996
2827.0667 | 753.9194
2828.0667 | 747.0508
2829.0823 | 730.563
2830.0667 | 744.0627
2831.0667 | 763.8183
2832.0667 | 784.3035
2833.0667 | 781.6963
2834.0667 | 770.7778
2835.0667 | 774.8399
2836.0667 | 788.5195
2837.0667 | 785.403
2838.0667 | 768.7621
2839.0667 | 761.1896
2840.0667 | 739.2135
2841.0667 | 719.9724
2842.0667 | 708.106
2843.0667 | 683.7205
2844.0667 | 675.7018
2845.0667 | 675.0152
2846.0667 | 662.7958
2847.0667 | 686.3737
2848.0667 | 695.8634
2849.0667 | 696.384
2850.0667 | 712.1831
2851.0667 | 726.8722
2852.0667 | 741.8882
2853.0667 | 732.4195
2854.0667 | 717.2088
2855.0667 | 697.5729
2856.0667 | 718.797
2857.0667 | 714.5941
2858.0667 | 700.5798
2859.0667 | 694.4324
2860.0667 | 697.5626
2861.0667 | 691.5336
2862.0667 | 687.8474
2863.0667 | 682.6729
2864.0667 | 678.4161
2865.0667 | 672.918
2866.0667 | 673.0757
2867.0667 | 669.3932
2868.0667 | 669.1502
2869.0667 | 671.0951
2870.0667 | 674.4492
2871.0667 | 686.3776
2872.0667 | 694.2216
2873.0667 | 714.1227
2874.0667 | 709.9706
2875.0667 | 707.4816
2876.0667 | 693.0459
2877.0667 | 693.1419
2878.0667 | 708.991
2879.0667 | 714.9984
2880.0667 | 721.5045
2881.0667 | 732.6528
2882.0667 | 731.2385
2883.0667 | 714.0967
2884.0667 | 711.4225
2885.0823 | 719.7361
2886.0667 | 744.9039
2887.0667 | 757.2487
2888.0667 | 753.9595
2889.0667 | 733.9488
2890.0667 | 750.9475
2891.0667 | 742.146
2892.0667 | 754.7943
2893.0667 | 765.8043
2894.0667 | 755.4093
2895.0667 | 741.7137
2896.0667 | 719.3307
2897.0667 | 704.0178
2898.0667 | 696.5987
2899.0667 | 713.7685
2900.0667 | 725.7007
2901.0667 | 738.418
2902.0667 | 716.935
2903.0667 | 692.6244
2904.0667 | 678.5471
2905.0667 | 674.1129
2906.0667 | 678.2319
2907.0667 | 691.3485
2908.0667 | 701.8689
2909.0823 | 697.9235
2910.0667 | 711.5737
2911.0667 | 717.3616
2912.0667 | 708.8474
2913.0667 | 717.6797
2914.0667 | 720.1419
2915.0667 | 715.1941
2916.0667 | 714.2976
2917.0667 | 717.4048
2918.0667 | 700.5952
2919.0667 | 696.1698
2920.0667 | 691.681
2921.0667 | 703.3684
2922.0667 | 722.7339
2923.0667 | 740.6483
2924.0667 | 749.1416
2925.0667 | 747.7055
2926.0667 | 755.0758
2927.0667 | 751.2961
2928.0667 | 748.1968
2929.0667 | 736.3256
2930.0667 | 728.6266
2931.0667 | 738.83
2932.0667 | 735.7204
2933.0667 | 728.4728
2934.0823 | 717.974
2935.0667 | 716.4455
2936.0667 | 731.8658
2937.0667 | 741.7292
2938.0667 | 735.0529
2939.0667 | 754.5944
2940.0667 | 722.7215
2941.0667 | 704.6771
2942.0667 | 689.9384
2943.0667 | 688.5206
2944.0667 | 701.259
2945.0823 | 721.2185
2946.0667 | 730.6442
2947.0667 | 763.1576
2948.0667 | 762.1286
2949.0667 | 769.4503
2950.0667 | 779.4081
2951.0667 | 761.6751
2952.0667 | 750.8974
2953.0667 | 738.8241
2954.0667 | 747.1567
2955.0667 | 759.2742
2956.0667 | 749.3323
2957.0667 | 728.1673
2958.0667 | 725.3882
2959.0667 | 711.6556
2960.0667 | 719.3338
2961.0667 | 713.6406
2962.0667 | 703.1251
2963.0667 | 698.6544
2964.0667 | 716.5352
2965.0667 | 733.2616
2966.0667 | 743.9299
2967.0667 | 751.7472
2968.0667 | 758.6723
2969.0667 | 749.8957
2970.0667 | 741.2787
2971.0667 | 725.9789
2972.0667 | 732.1716
2973.0667 | 743.5267
2974.0667 | 742.6236
2975.0667 | 745.8025
2976.0667 | 735.5009
2977.0667 | 735.7477
2978.0667 | 735.1557
2979.0823 | 743.0163
2980.0667 | 722.3264
2981.0667 | 730.1638
2982.0667 | 737.2397
2983.0667 | 747.8151
2984.0667 | 751.9814
2985.0667 | 724.91
2986.0667 | 717.7542
2987.0667 | 694.1023
2988.0667 | 695.6952
2989.0667 | 698.744
2990.0667 | 717.4635
2991.0667 | 711.9405
2992.0667 | 701.4983
2993.0667 | 672.3311
2994.0823 | 664.2456
2995.0667 | 683.6162
2996.0823 | 667.5842
2997.0667 | 668.4147
2998.0667 | 666.6597
2999.0667 | 653.6927
3000.0667 | 666.4205
3001.0667 | 662.9239
3002.0667 | 657.5386
3003.0667 | 664.2212
3004.0667 | 670.7364
3005.0823 | 677.2478
3006.0667 | 677.3302
3007.0667 | 669.4154
3008.0667 | 660.6983
3009.0667 | 693.8219
3010.0667 | 702.3656
3011.0667 | 711.1088
3012.0667 | 722.4237
3013.0667 | 746.4755
3014.0667 | 756.8201
3015.0667 | 765.787
3016.0667 | 756.495
3017.0667 | 750.5243
3018.0667 | 738.125
3019.0667 | 741.0045
3020.0667 | 732.6132
3021.0667 | 728.3983
3022.0667 | 728.5781
3023.0667 | 732.6306
3024.0667 | 745.2386
3025.0667 | 756.1956
3026.0823 | 762.9014
3027.0667 | 756.969
3028.0667 | 725.151
3029.0667 | 722.9854
3030.0667 | 722.5679
3031.0667 | 716.4357
3032.0667 | 703.7685
3033.0667 | 696.0554
3034.0667 | 672.2571
3035.0667 | 679.8162
3036.0667 | 668.4831
3037.0667 | 667.1722
3038.0667 | 689.6743
3039.0667 | 679.6446
3040.0667 | 693.2591
3041.0667 | 689.6619
3042.0667 | 700.1037
3043.0667 | 691.9627
3044.0667 | 687.3928
3045.0667 | 671.3503
3046.0667 | 653.7272
3047.0667 | 639.1481
3048.0667 | 627.7655
3049.0667 | 627.6815
3050.0667 | 649.8071
3051.0667 | 641.337
3052.0667 | 642.0378
3053.0667 | 651.0409
3054.0667 | 663.9721
3055.0667 | 657.5308
3056.0667 | 662.8886
3057.0667 | 646.7518
3058.0667 | 633.3357
3059.0667 | 613.8245
3060.0667 | 599.1565
3061.0667 | 599.0143
3062.0667 | 617.3323
3063.0667 | 659.0162
3064.0667 | 649.6559
3065.0823 | 639.4733
3066.0667 | 635.2995
3067.0667 | 645.0884
3068.0667 | 662.4084
3069.0667 | 662.6573
3070.0667 | 685.102
3071.0667 | 687.7332
3072.0667 | 709.6363
3073.0667 | 713.0205
3074.0823 | 715.2246
3075.0667 | 715.7178
3076.0667 | 702.449
3077.0667 | 695.6993
3078.0667 | 729.7837
3079.0667 | 732.1421
3080.0667 | 721.5858
3081.0667 | 734.28
3082.0667 | 758.5123
3083.0667 | 758.7145
3084.0667 | 778.8209
3085.0667 | 752.3412
3086.0667 | 751.513
3087.0667 | 735.4812
3088.0667 | 712.8275
3089.0667 | 711.5667
3090.0667 | 744.9964
3091.0667 | 741.9795
3092.0667 | 724.2216
3093.0667 | 735.2249
3094.0667 | 729.2841
3095.0667 | 749.7812
3096.0667 | 761.4988
3097.0667 | 766.1474
3098.0667 | 788.076
3099.0823 | 802.1457
3100.0667 | 816.101
3101.0667 | 801.0456
3102.0823 | 778.3886
3103.0667 | 777.0961
3104.0667 | 774.4314
3105.0667 | 764.3865
3106.0667 | 762.3208
3107.0667 | 770.258
3108.0667 | 746.014
3109.0667 | 733.6928
3110.0667 | 724.0181
3111.0667 | 711.9284
3112.0667 | 697.0195
3113.0667 | 696.2719
3114.0823 | 720.3105
3115.0667 | 730.3667
3116.0823 | 712.2418
3117.0667 | 682.2367
3118.0667 | 668.6324
3119.0667 | 661.9959
3120.0667 | 657.6022
3121.0667 | 649.4123
3122.0667 | 655.4728
3123.0667 | 663.9974
3124.0667 | 699.7163
3125.0667 | 706.1758
3126.0667 | 747.0176
3127.0667 | 756.2761
3128.0667 | 737.6819
3129.0667 | 753.9986
3130.0667 | 756.9507
3131.0667 | 735.7531
3132.0667 | 746.3626
3133.0667 | 751.3374
3134.0667 | 762.5658
3135.0667 | 747.1009
3136.0667 | 748.5053
3137.0667 | 739.5012
3138.0667 | 742.189
3139.0667 | 722.2736
3140.0667 | 728.5205
3141.0667 | 726.285
3142.0667 | 730.6374
3143.0667 | 726.5101
3144.0667 | 708.8971
3145.0667 | 713.683
3146.0667 | 717.0619
3147.0667 | 731.1107
3148.0667 | 719.3377
3149.0667 | 713.0281
3150.0667 | 698.683
3151.0667 | 686.8376
3152.0667 | 684.0736
3153.0667 | 668.161
3154.0667 | 672.7821
3155.0667 | 682.1777
3156.0667 | 677.0576
3157.0667 | 668.1089
3158.0667 | 658.5972
3159.0823 | 643.29
3160.0667 | 664.1004
3161.0667 | 691.9115
3162.0667 | 692.5392
3163.0667 | 672.1426
3164.0667 | 666.6448
3165.0667 | 670.0157
3166.0667 | 683.3818
3167.0667 | 666.9153
3168.0667 | 657.4779
3169.0667 | 637.0046
3170.0667 | 638.8494
3171.0667 | 637.9674
3172.0667 | 624.9452
3173.0667 | 610.9578
3174.0667 | 611.4993
3175.0667 | 624.2882
3176.0823 | 625.8619
3177.0667 | 617.7061
3178.0667 | 626.2422
3179.0667 | 623.1268
3180.0667 | 616.8392
3181.0667 | 602.7123
3182.0667 | 596.4525
3183.0667 | 594.1398
3184.0667 | 606.3821
3185.0823 | 604.8036
3186.0667 | 618.657
3187.0667 | 630.1448
3188.0667 | 619.6588
3189.0667 | 631.2768
3190.0667 | 672.1217
3191.0667 | 673.0137
3192.0667 | 663.5622
3193.0667 | 672.2695
3194.0667 | 676.481
3195.0667 | 667.9737
3196.0667 | 656.6749
3197.0667 | 653.6488
3198.0667 | 652.6392
3199.0667 | 670.5234
3200.0667 | 674.7182
3201.0667 | 687.4636
3202.0667 | 682.3804
3203.0667 | 673.2269
3204.0667 | 664.5299
3205.0667 | 662.8992
3206.0667 | 656.6897
3207.0667 | 671.3549
3208.0667 | 676.0819
3209.0667 | 665.4816
3210.0667 | 690.4789
3211.0667 | 677.3848
3212.0667 | 668.902
3213.0667 | 706.073
3214.0667 | 721.1077
3215.0667 | 722.5317
3216.0667 | 743.5432
3217.0667 | 748.1465
3218.0667 | 767.5746
3219.0667 | 764.7796
3220.0667 | 741.3015
3221.0667 | 728.8364
3222.0667 | 737.3951
3223.0667 | 730.367
3224.0667 | 725.7344
3225.0667 | 703.818
3226.0667 | 695.2251
3227.0667 | 696.9418
3228.0667 | 713.5189
3229.0667 | 726.6138
3230.0667 | 729.321
3231.0667 | 727.5697
3232.0667 | 712.3212
3233.0667 | 702.571
3234.0667 | 707.8714
3235.0667 | 699.1053
3236.0667 | 684.0491
3237.0667 | 684.1865
3238.0667 | 701.5076
3239.0667 | 699.9774
3240.0667 | 683.117
3241.0667 | 687.5147
3242.0667 | 684.375
3243.0667 | 671.7508
3244.0667 | 662.5575
3245.0667 | 681.7059
3246.0667 | 691.6793
3247.0667 | 693.358
3248.0667 | 673.2271
3249.0667 | 679.3384
3250.0667 | 692.7564
3251.0667 | 699.538
3252.0667 | 687.3374
3253.0667 | 685.2976
3254.0667 | 688.0935
3255.0667 | 688.1786
3256.0667 | 692.0799
3257.0667 | 700.9159
3258.0667 | 674.9332
3259.0667 | 668.0443
3260.0667 | 659.9343
3261.0667 | 653.3926
3262.0667 | 647.1406
3263.0667 | 648.3504
3264.0667 | 641.6219
3265.0667 | 639.1591
3266.0823 | 645.5665
3267.0667 | 654.4596
3268.0667 | 649.3394
3269.0667 | 633.4517
3270.0667 | 638.232
3271.0667 | 650.9343
3272.0667 | 665.7825
3273.0667 | 646.7676
3274.0667 | 647.5674
3275.0667 | 625.5113
3276.0667 | 605.5563
3277.0667 | 614.2287
3278.0667 | 627.9872
3279.0667 | 618.0487
3280.0667 | 632.4593
3281.0667 | 658.9032
3282.0667 | 698.2063
3283.0667 | 734.1792
3284.0667 | 727.0424
3285.0667 | 710.8377
3286.0667 | 697.8041
3287.0667 | 709.4024
3288.0667 | 718.0665
3289.0667 | 721.4212
3290.0667 | 717.8138
3291.0667 | 715.1073
3292.0667 | 692.6298
3293.0667 | 678.7443
3294.0823 | 690.6657
3295.0667 | 668.3315
3296.0667 | 669.5428
3297.0667 | 662.8611
3298.0667 | 657.0158
3299.0667 | 654.8166
3300.0667 | 644.5461
3301.0667 | 628.5146
3302.0667 | 610.992
3303.0667 | 603.7313
3304.0667 | 606.2053
3305.0823 | 618.0906
3306.0667 | 617.9142
3307.0667 | 602.6553
3308.0667 | 623.783
3309.0667 | 643.6928
3310.0667 | 656.7256
3311.0667 | 661.9611
3312.0667 | 697.4132
3313.0667 | 706.4733
3314.0667 | 686.7637
3315.0667 | 682.2007
3316.0667 | 676.8545
3317.0667 | 696.6421
3318.0667 | 701.6049
3319.0823 | 697.616
3320.0667 | 697.4206
3321.0667 | 684.4867
3322.0667 | 676.1192
3323.0667 | 670.8582
3324.0667 | 655.346
3325.0667 | 638.7969
3326.0667 | 627.0239
3327.0667 | 629.2211
3328.0667 | 635.8722
3329.0667 | 621.6734
3330.0667 | 627.0995
3331.0667 | 660.0359
3332.0667 | 692.3318
3333.0667 | 676.9107
3334.0667 | 663.7651
3335.0667 | 655.2705
3336.0667 | 659.3772
3337.0667 | 654.0302
3338.0667 | 661.1291
3339.0667 | 673.0524
3340.0667 | 659.3141
3341.0667 | 660.0366
3342.0667 | 658.8346
3343.0667 | 661.4891
3344.0667 | 670.9229
3345.0667 | 665.5986
3346.0667 | 667.2981
3347.0667 | 664.7541
3348.0667 | 669.6571
3349.0667 | 678.0684
3350.0667 | 676.0746
3351.0667 | 673.9291
3352.0667 | 670.7651
3353.0667 | 659.4024
3354.0667 | 664.5765
3355.0667 | 698.2996
3356.0667 | 694.8675
3357.0667 | 683.6195
3358.0667 | 697.7164
3359.0667 | 722.1073
3360.0667 | 742.1082
3361.0667 | 745.8102
3362.0667 | 743.7423
3363.0667 | 722.6129
3364.0823 | 718.5764
3365.0823 | 746.4431
3366.0667 | 749.3126
3367.0667 | 726.6352
3368.0667 | 708.7269
3369.0667 | 691.33
3370.0667 | 686.7546
3371.0667 | 699.8849
3372.0667 | 690.6806
3373.0667 | 687.9916
3374.0667 | 681.7656
3375.0667 | 670.4222
3376.0667 | 667.2547
3377.0667 | 677.3738
3378.0667 | 690.2847
3379.0823 | 699.752
3380.0667 | 693.8794
3381.0667 | 699.5476
3382.0667 | 691.4372
3383.0667 | 694.8136
3384.0667 | 685.4977
3385.0667 | 691.5386
3386.0667 | 687.9617
3387.0667 | 682.8513
3388.0667 | 665.736
3389.0667 | 652.3503
3390.0667 | 672.7312
3391.0667 | 658.6594
3392.0667 | 636.9288
3393.0667 | 638.9497
3394.0667 | 649.8596
3395.0667 | 644.8992
3396.0667 | 652.9312
3397.0667 | 659.0753
3398.0667 | 654.3123
3399.0667 | 639.9377
3400.0667 | 630.309
3401.0667 | 630.013
3402.0667 | 625.9219
3403.0667 | 622.5625
3404.0667 | 621.9582
3405.0667 | 611.8761
3406.0667 | 608.9472
3407.0667 | 602.0689
3408.0667 | 612.7294
3409.0667 | 617.3498
3410.0667 | 625.7818
3411.0667 | 626.4558
3412.0667 | 621.2957
3413.0667 | 608.3359
3414.0667 | 601.9464
3415.0667 | 601.457
3416.0667 | 599.3945
3417.0667 | 597.0946
3418.0667 | 586.8327
3419.0667 | 573.6411
3420.0667 | 570.6751
3421.0667 | 574.0278
3422.0667 | 606.1442
3423.0667 | 639.6644
3424.0667 | 663.3158
3425.0667 | 688.2037
3426.0667 | 699.8717
3427.0667 | 730.103
3428.0667 | 749.5274
3429.0667 | 732.0438
3430.0667 | 736.6411
3431.0667 | 759.1604
3432.0667 | 744.2759
3433.0667 | 724.8509
3434.0667 | 727.1371
3435.0667 | 733.1332
3436.0667 | 730.2301
3437.0667 | 722.2363
3438.0667 | 713.9531
3439.0667 | 704.8564
3440.0667 | 697.4172
3441.0667 | 700.0991
3442.0667 | 697.1437
3443.0667 | 703.457
3444.0667 | 706.2726
3445.0667 | 702.4161
3446.0667 | 697.6055
3447.0667 | 706.4126
3448.0667 | 733.7689
3449.0667 | 747.5377
3450.0667 | 750.9574
3451.0667 | 732.2121
3452.0667 | 736.2053
3453.0667 | 739.0634
3454.0667 | 733.154
3455.0667 | 719.2806
3456.0667 | 711.0793
3457.0667 | 704.9073
3458.0667 | 697.7845
3459.0667 | 727.7503
3460.0667 | 727.6491
3461.0667 | 705.6915
3462.0667 | 690.668
3463.0667 | 674.2009
3464.0667 | 655.3453
3465.0667 | 655.3295
3466.0667 | 659.3563
3467.0667 | 658.9212
3468.0667 | 674.4235
3469.0667 | 682.012
3470.0667 | 688.0666
3471.0667 | 688.0042
3472.0667 | 689.6131
3473.0667 | 678.8952
3474.0667 | 664.8775
3475.0667 | 654.5713
3476.0667 | 664.0289
3477.0667 | 661.8418
3478.0667 | 668.7785
3479.0667 | 715.7175
3480.0667 | 709.8866
3481.0667 | 712.8507
3482.0667 | 702.8275
3483.0667 | 700.4296
3484.0823 | 700.4171
3485.0667 | 679.0139
3486.0667 | 661.4539
3487.0667 | 649.8559
3488.0667 | 640.8943
3489.0667 | 654.6569
3490.0667 | 669.8107
3491.0667 | 692.6051
3492.0667 | 688.3779
3493.0667 | 705.4432
3494.0667 | 714.7335
3495.0667 | 749.0735
3496.0667 | 769.0447
3497.0667 | 764.3498
3498.0667 | 755.3062
3499.0823 | 757.5897
3500.0667 | 727.2796
3501.0667 | 700.9657
3502.0667 | 718.6166
3503.0667 | 715.0804
3504.0667 | 710.7674
3505.0667 | 718.8442
3506.0667 | 729.1436
3507.0667 | 722.9913
3508.0667 | 733.005
3509.0667 | 751.096
3510.0667 | 751.5723
3511.0667 | 753.4663
3512.0667 | 740.9861
3513.0667 | 751.7082
3514.0667 | 738.844
3515.0667 | 711.5259
3516.0667 | 701.554
3517.0667 | 695.1984
3518.0667 | 693.4285
3519.0667 | 686.9148
3520.0667 | 694.6367
3521.0667 | 688.6215
3522.0667 | 664.5971
3523.0667 | 647.54
3524.0667 | 646.4903
3525.0667 | 651.9435
3526.0667 | 666.3692
3527.0667 | 690.4961
3528.0667 | 717.9997
3529.0667 | 733.5587
3530.0667 | 742.073
3531.0667 | 738.2636
3532.0667 | 754.889
3533.0667 | 740.0971
3534.0667 | 739.7396
3535.0667 | 725.1511
3536.0667 | 717.2932
3537.0667 | 737.0385
3538.0667 | 740.0567
3539.0667 | 721.459
3540.0667 | 697.3283
3541.0667 | 683.2958
3542.0667 | 682.546
3543.0667 | 674.3097
3544.0823 | 663.9459
3545.0667 | 677.4988
3546.0667 | 670.5728
3547.0823 | 658.7109
3548.0667 | 636.6804
3549.0667 | 626.9189
3550.0823 | 639.3295
3551.0823 | 664.8125
3552.0667 | 666.1915
3553.0667 | 653.6648
3554.0667 | 660.9614
3555.0667 | 688.3286
3556.0667 | 722.3249
3557.0667 | 735.6104
3558.0667 | 736.1742
3559.0667 | 703.3979
3560.0667 | 691.785
3561.0667 | 694.0672
3562.0667 | 691.2792
3563.0667 | 675.2125
3564.0667 | 669.136
3565.0667 | 697.7749
3566.0667 | 718.4928
3567.0667 | 727.0622
3568.0667 | 707.8368
3569.0667 | 692.3023
3570.0667 | 680.2158
3571.0667 | 667.2511
3572.0667 | 670.4128
3573.0667 | 657.7096
3574.0667 | 648.2314
3575.0667 | 646.1011
3576.0667 | 662.0631
3577.0667 | 659.9849
3578.0667 | 644.4281
3579.0667 | 658.5837
3580.0667 | 672.8796
3581.0667 | 656.2081
3582.0667 | 638.1332
3583.0667 | 633.065
3584.0823 | 641.7182
3585.0667 | 631.1897
3586.0667 | 629.1407
3587.0667 | 643.8044
3588.0667 | 660.064
3589.0667 | 688.6768
3590.0667 | 702.0069
3591.0667 | 716.1584
3592.0667 | 710.3444
3593.0667 | 708.5434
3594.0667 | 716.5597
3595.0667 | 725.0668
3596.0667 | 703.8624
3597.0667 | 688.6785
3598.0667 | 670.0187
3599.0667 | 662.4929
3600.0667 | 685.8239
3601.0667 | 679.8621
3602.0667 | 679.6184
3603.0667 | 683.1162
3604.0667 | 686.1611
3605.0667 | 699.6161
3606.0667 | 679.9042
3607.0667 | 691.8172
3608.0667 | 702.6426
3609.0667 | 685.9921
3610.0667 | 663.1907
3611.0667 | 706.4759
3612.0667 | 730.6035
3613.0667 | 730.6668
3614.0667 | 740.5778
3615.0667 | 761.5901
3616.0667 | 768.7208
3617.0667 | 780.4307
3618.0667 | 769.8077
3619.0667 | 756.0361
3620.0667 | 740.9481
3621.0667 | 708.0811
3622.0667 | 717.0526
3623.0667 | 736.7673
3624.0667 | 712.1825
3625.0667 | 700.6053
3626.0667 | 711.4433
3627.0667 | 733.2302
3628.0667 | 759.5703
3629.0667 | 757.8368
3630.0667 | 752.8107
3631.0667 | 732.2813
3632.0667 | 730.947
3633.0667 | 706.1185
3634.0667 | 687.4246
3635.0667 | 677.6587
3636.0667 | 665.594
3637.0667 | 673.7202
3638.0667 | 694.006
3639.0667 | 703.3268
3640.0667 | 690.4544
3641.0667 | 682.7193
3642.0667 | 669.5344
3643.0667 | 662.7361
3644.0667 | 651.4893
3645.0667 | 651.6857
3646.0667 | 652.1014
3647.0667 | 645.3996
3648.0667 | 655.5272
3649.0667 | 652.7358
3650.0667 | 636.8105
3651.0667 | 629.2756
3652.0667 | 617.5388
3653.0667 | 636.8426
3654.0667 | 630.3823
3655.0667 | 621.6144
3656.0667 | 640.3822
3657.0667 | 652.8424
3658.0667 | 658.4856
3659.0667 | 657.5542
3660.0667 | 667.0193
3661.0667 | 677.456
3662.0667 | 676.8591
3663.0667 | 668.66
3664.0823 | 640.1318
3665.0667 | 640.5959
3666.0667 | 665.5256
3667.0667 | 668.6927
3668.0667 | 670.3673
3669.0667 | 671.4185
3670.0667 | 666.0852
3671.0667 | 664.2094
3672.0667 | 661.1569
3673.0667 | 657.4156
3674.0667 | 641.2713
3675.0667 | 646.4721
3676.0667 | 655.1503
3677.0667 | 682.9724
3678.0667 | 700.2591
3679.0823 | 717.1095
3680.0667 | 719.0163
3681.0667 | 706.5141
3682.0667 | 695.7189
3683.0667 | 666.1763
3684.0667 | 646.9891
3685.0667 | 629.0588
3686.0667 | 625.9206
3687.0667 | 623.4659
3688.0667 | 611.3426
3689.0667 | 598.9667
3690.0667 | 589.5217
3691.0667 | 609.6183
3692.0667 | 649.8217
3693.0667 | 646.8977
3694.0667 | 647.7914
3695.0667 | 657.8158
3696.0667 | 666.6316
3697.0667 | 675.6063
3698.0667 | 694.2829
3699.0667 | 676.387
3700.0667 | 683.8166
3701.0667 | 710.3805
3702.0823 | 720.0843
3703.0667 | 719.6058
3704.0823 | 706.2178
3705.0667 | 708.0137
3706.0667 | 727.6592
3707.0667 | 707.7158
3708.0667 | 695.6937
3709.0667 | 723.6062
3710.0667 | 744.7978
3711.0667 | 729.5342
3712.0667 | 729.8714
3713.0667 | 736.1747
3714.0667 | 747.8507
3715.0667 | 738.2143
3716.0667 | 739.7459
3717.0667 | 719.6726
3718.0667 | 693.7445
3719.0823 | 674.0739
3720.0667 | 663.0082
3721.0667 | 658.4264
3722.0667 | 679.3229
3723.0667 | 716.9389
3724.0667 | 731.2553
3725.0667 | 751.4462
3726.0667 | 771.6951
3727.0667 | 784.5299
3728.0667 | 762.3768
3729.0667 | 744.6126
3730.0667 | 749.1263
3731.0667 | 746.0499
3732.0667 | 757.7583
3733.0667 | 772.4584
3734.0667 | 777.3813
3735.0667 | 801.9542
3736.0667 | 803.6883
3737.0667 | 805.9258
3738.0667 | 780.5924
3739.0667 | 764.8438
3740.0667 | 744.3121
3741.0667 | 733.9622
3742.0667 | 720.8866
3743.0667 | 737.9764
3744.0667 | 743.6849
3745.0667 | 756.1936
3746.0667 | 749.5927
3747.0667 | 739.0918
3748.0667 | 751.4142
3749.0667 | 725.9556
3750.0667 | 705.3835
3751.0667 | 698.5068
3752.0667 | 714.1521
3753.0667 | 713.1183
3754.0667 | 693.3376
3755.0667 | 681.9705
3756.0667 | 676.6246
3757.0667 | 677.4384
3758.0667 | 671.1917
3759.0667 | 675.7873
3760.0667 | 670.0417
3761.0667 | 666.9654
3762.0667 | 671.3779
3763.0667 | 671.9225
3764.0823 | 659.4598
3765.0667 | 656.1044
3766.0667 | 670.617
3767.0667 | 684.936
3768.0667 | 690.6321
3769.0667 | 686.5725
3770.0667 | 693.7173
3771.0667 | 681.0322
3772.0667 | 670.2462
3773.0667 | 666.6254
3774.0667 | 683.2483
3775.0667 | 677.5052
3776.0667 | 675.4545
3777.0667 | 674.3238
3778.0667 | 661.9001
3779.0667 | 651.7279
3780.0823 | 628.805
3781.0823 | 627.0227
3782.0667 | 630.9464
3783.0667 | 653.9972
3784.0823 | 666.7381
3785.0667 | 664.0115
3786.0823 | 654.6526
3787.0823 | 673.2702
3788.0667 | 699.8335
3789.0667 | 682.0562
3790.0667 | 682.5003
3791.0667 | 675.3856
3792.0667 | 681.9575
3793.0667 | 683.2782
3794.0667 | 663.9407
3795.0667 | 677.4719
3796.0667 | 678.5573
3797.0667 | 669.6398
3798.0667 | 672.934
3799.0667 | 680.4314
3800.0667 | 695.4952
3801.0823 | 679.3177
3802.0667 | 661.0231
3803.0667 | 675.8349
3804.0823 | 698.861
3805.0667 | 695.8118
3806.0667 | 680.445
3807.0667 | 673.6604
3808.0667 | 658.2949
3809.0667 | 658.1357
3810.0667 | 657.6866
3811.0667 | 653.0517
3812.0667 | 644.2813
3813.0667 | 645.7143
3814.0667 | 635.5322
3815.0667 | 618.9593
3816.0667 | 632.2328
3817.0667 | 637.4491
3818.0667 | 650.0183
3819.0667 | 642.9272
3820.0667 | 627.7837
3821.0667 | 636.4064
3822.0667 | 637.6018
3823.0667 | 624.1181
3824.0667 | 624.6918
3825.0667 | 649.9813
3826.0667 | 661.2687
3827.0667 | 648.1121
3828.0667 | 659.2794
3829.0667 | 696.5582
3830.0667 | 704.7646
3831.0667 | 684.3572
3832.0667 | 663.0102
3833.0667 | 655.7438
3834.0667 | 647.2977
3835.0667 | 674.4469
3836.0667 | 695.2762
3837.0667 | 705.5926
3838.0667 | 717.8319
3839.0667 | 729.6082
3840.0667 | 707.9474
3841.0667 | 703.0871
3842.0667 | 711.6316
3843.0667 | 688.7191
3844.0667 | 678.5786
3845.0667 | 698.5866
3846.0667 | 708.8857
3847.0667 | 732.4937
3848.0667 | 754.007
3849.0667 | 729.4905
3850.0667 | 739.0087
3851.0667 | 766.5365
3852.0667 | 776.2944
3853.0667 | 783.2558
3854.0667 | 779.4739
3855.0667 | 764.3262
3856.0667 | 763.9193
3857.0667 | 775.454
3858.0667 | 768.3953
3859.0667 | 758.003
3860.0667 | 771.7025
3861.0667 | 753.6793
3862.0667 | 758.2571
3863.0667 | 741.0633
3864.0667 | 725.7764
3865.0667 | 739.0623
3866.0667 | 751.7605
3867.0667 | 753.0106
3868.0667 | 740.7763
3869.0667 | 740.3007
3870.0667 | 730.9057
3871.0667 | 736.8787
3872.0667 | 740.0161
3873.0667 | 733.418
3874.0667 | 712.6133
3875.0667 | 697.2861
3876.0667 | 676.0024
3877.0667 | 664.3648
3878.0667 | 676.4704
3879.0667 | 709.4774
3880.0667 | 713.3116
3881.0667 | 709.4712
3882.0667 | 699.3188
3883.0667 | 713.9221
3884.0823 | 702.4283
3885.0667 | 685.3402
3886.0667 | 709.0622
3887.0667 | 723.4108
3888.0667 | 722.5098
3889.0667 | 721.3884
3890.0667 | 718.4725
3891.0667 | 740.0289
3892.0667 | 749.0318
3893.0667 | 746.9106
3894.0823 | 735.368
3895.0667 | 734.9297
3896.0667 | 734.4989
3897.0667 | 724.4826
3898.0667 | 701.0987
3899.0823 | 689.18
3900.0667 | 709.4145
3901.0667 | 729.6103
3902.0667 | 761.3582
3903.0667 | 755.3382
3904.0667 | 734.1385
3905.0667 | 732.1137
3906.0667 | 730.7411
3907.0667 | 719.2091
3908.0667 | 714.037
3909.0667 | 704.007
3910.0667 | 705.9675
3911.0667 | 724.0845
3912.0667 | 739.6813
3913.0667 | 743.0911
3914.0667 | 733.1055
3915.0667 | 747.9294
3916.0667 | 744.1434
3917.0667 | 756.6352
3918.0667 | 763.7132
3919.0667 | 768.8379
3920.0667 | 757.0899
3921.0667 | 744.2929
3922.0667 | 727.2497
3923.0667 | 704.6822
3924.0823 | 690.0313
3925.0667 | 679.3548
3926.0667 | 675.9424
3927.0667 | 671.6994
3928.0667 | 660.941
3929.0667 | 661.9829
3930.0667 | 666.9784
3931.0667 | 656.574
3932.0667 | 651.2136
3933.0667 | 656.5862
3934.0823 | 671.8326
3935.0667 | 682.334
3936.0667 | 658.0628
3937.0667 | 641.1319
3938.0667 | 646.7101
3939.0823 | 660.7713
3940.0667 | 677.6977
3941.0667 | 694.5223
3942.0667 | 695.1614
3943.0667 | 675.1315
3944.0667 | 681.8622
3945.0667 | 688.851
3946.0667 | 709.9471
3947.0667 | 706.2882
3948.0667 | 685.3284
3949.0667 | 680.3352
3950.0667 | 672.0947
3951.0667 | 682.709
3952.0667 | 664.632
3953.0667 | 648.8342
3954.0667 | 639.6469
3955.0667 | 654.12
3956.0667 | 655.0175
3957.0667 | 647.9039
3958.0667 | 631.7556
3959.0667 | 613.6828
3960.0667 | 596.9746
3961.0667 | 602.9383
3962.0667 | 631.5368
3963.0667 | 661.4589
3964.0667 | 679.4356
3965.0823 | 661.7892
3966.0667 | 651.0202
3967.0667 | 652.2277
3968.0667 | 648.9684
3969.0667 | 657.8421
3970.0667 | 666.389
3971.0667 | 691.1755
3972.0667 | 674.6475
3973.0667 | 660.2972
3974.0667 | 651.9372
3975.0667 | 646.9072
3976.0667 | 664.7592
3977.0667 | 676.0539
3978.0667 | 667.7026
3979.0667 | 668.1717
3980.0667 | 665.2949
3981.0667 | 691.0375
3982.0667 | 710.8239
3983.0667 | 719.0016
3984.0823 | 724.1869
3985.0667 | 706.383
3986.0667 | 684.6787
3987.0667 | 665.9736
3988.0667 | 661.0486
3989.0667 | 640.7748
3990.0667 | 637.6297
3991.0667 | 623.2821
3992.0667 | 616.3321
3993.0667 | 612.1672
3994.0667 | 616.7624
3995.0667 | 617.7927
3996.0667 | 622.5581
3997.0667 | 657.0274
3998.0667 | 675.9934
3999.0667 | 687.8273
4000.0667 | 692.4718
4001.0667 | 716.6842
4002.0667 | 727.0498
4003.0667 | 711.183
4004.0667 | 720.6156
4005.0667 | 719.9619
4006.0667 | 727.4944
4007.0667 | 704.2424
4008.0667 | 714.2441
4009.0667 | 726.6628
4010.0667 | 749.355
4011.0667 | 772.629
4012.0667 | 764.6184
4013.0667 | 757.4406
4014.0667 | 739.9149
4015.0667 | 736.5095
4016.0667 | 731.0557
4017.0667 | 740.0962
4018.0667 | 737.9272
4019.0667 | 744.8336
4020.0667 | 756.0881
4021.0667 | 764.4699
4022.0667 | 762.3792
4023.0823 | 747.9518
4024.0823 | 739.4198
4025.0667 | 741.6408
4026.0667 | 731.6016
4027.0667 | 704.9549
4028.0667 | 699.9516
4029.0667 | 689.0333
4030.0667 | 685.9506
4031.0667 | 686.5089
4032.0667 | 703.093
4033.0667 | 714.0899
4034.0667 | 718.1059
4035.0667 | 711.6655
4036.0667 | 692.2096
4037.0667 | 679.0511
4038.0667 | 680.0606
4039.0667 | 695.9533
4040.0667 | 694.8727
4041.0667 | 673.4798
4042.0667 | 653.4117
4043.0667 | 680.8818
4044.0667 | 698.3469
4045.0667 | 707.1595
4046.0667 | 705.6655
4047.0667 | 687.381
4048.0667 | 669.0819
4049.0667 | 662.0743
4050.0667 | 649.5925
4051.0667 | 699.9442
4052.0667 | 723.7427
4053.0667 | 738.9667
4054.0667 | 754.7758
4055.0667 | 759.032
4056.0667 | 736.6121
4057.0667 | 733.9446
4058.0667 | 734.9957
4059.0667 | 748.8021
4060.0667 | 756.1471
4061.0667 | 762.8474
4062.0667 | 767.4837
4063.0667 | 745.4085
4064.0667 | 754.302
4065.0667 | 735.3387
4066.0667 | 729.3088
4067.0667 | 731.5162
4068.0667 | 736.0571
4069.0667 | 761.508
4070.0667 | 777.5864
4071.0667 | 770.3266
4072.0667 | 766.6164
4073.0667 | 773.5025
4074.0667 | 748.0259
4075.0667 | 720.7522
4076.0667 | 695.7934
4077.0667 | 691.8917
4078.0667 | 685.8535
4079.0667 | 706.7367
4080.0667 | 723.896
4081.0667 | 736.1734
4082.0667 | 733.2407
4083.0667 | 737.023
4084.0667 | 730.1469
4085.0667 | 736.1936
4086.0667 | 728.6515
4087.0667 | 704.1383
4088.0667 | 699.2295
4089.0667 | 698.0524
4090.0667 | 686.0806
4091.0667 | 677.0843
4092.0667 | 683.3489
4093.0667 | 663.5802
4094.0667 | 655.2892
4095.0667 | 662.8024
4096.0667 | 668.3228
4097.0667 | 660.372
4098.0667 | 660.8305
4099.0667 | 665.1152
4100.0667 | 663.116
4101.0667 | 664.3653
4102.0667 | 656.1503
4103.0667 | 666.2128
4104.0667 | 668.9356
4105.0667 | 686.258
4106.0667 | 724.5169
4107.0667 | 742.3537
4108.0667 | 739.3971
4109.0667 | 723.7697
4110.0667 | 708.582
4111.0667 | 684.4951
4112.0667 | 679.7271
4113.0667 | 671.0817
4114.0667 | 675.6223
4115.0667 | 676.1304
4116.0667 | 670.6975
4117.0667 | 669.2535
4118.0667 | 652.5333
4119.0667 | 662.1573
4120.0667 | 665.1945
4121.0667 | 664.0707
4122.0667 | 681.3583
4123.0667 | 703.7736
4124.0667 | 715.1162
4125.0667 | 699.3722
4126.0667 | 717.4415
4127.0667 | 702.4864
4128.0667 | 691.9105
4129.0667 | 695.266
4130.0667 | 707.3391
4131.0667 | 702.516
4132.0667 | 695.3518
4133.0667 | 695.4544
4134.0667 | 686.7843
4135.0667 | 662.6084
4136.0667 | 686.6183
4137.0667 | 706.864
4138.0667 | 742.0267
4139.0667 | 743.2921
4140.0667 | 752.0003
4141.0667 | 730.5921
4142.0667 | 765.083
4143.0667 | 772.3657
4144.0667 | 765.4982
4145.0667 | 745.2021
4146.0667 | 719.4662
4147.0667 | 710.757
4148.0667 | 700.7596
4149.0667 | 707.5711
4150.0667 | 719.0494
4151.0667 | 709.0549
4152.0667 | 695.5137
4153.0667 | 719.5192
4154.0667 | 733.0051
4155.0667 | 741.6232
4156.0667 | 741.7731
4157.0667 | 739.772
4158.0667 | 744.0724
4159.0823 | 751.9787
4160.0667 | 761.1587
4161.0667 | 760.0281
4162.0667 | 748.8515
4163.0667 | 754.3709
4164.0667 | 737.7001
4165.0667 | 749.9878
4166.0667 | 755.9628
4167.0667 | 743.1691
4168.0667 | 722.8361
4169.0667 | 726.4654
4170.0667 | 700.7434
4171.0667 | 688.5148
4172.0667 | 683.4886
4173.0667 | 682.2042
4174.0667 | 688.3788
4175.0667 | 694.2669
4176.0667 | 687.6742
4177.0667 | 675.9531
4178.0667 | 679.0034
4179.0667 | 723.2635
4180.0667 | 753.2275
4181.0667 | 732.5923
4182.0667 | 740.0705
4183.0667 | 735.1705
4184.0667 | 756.6
4185.0667 | 757.1503
4186.0667 | 739.9956
4187.0667 | 736.921
4188.0667 | 723.2875
4189.0667 | 713.7286
4190.0667 | 707.7349
4191.0667 | 730.6887
4192.0667 | 730.7024
4193.0667 | 736.4419
4194.0667 | 723.4533
4195.0667 | 714.7917
4196.0667 | 721.7374
4197.0823 | 718.6112
4198.0667 | 704.5706
4199.0823 | 689.7008
4200.0667 | 685.7197
4201.0667 | 675.4236
4202.0667 | 692.7034
4203.0667 | 703.9591
4204.0667 | 734.6887
4205.0667 | 757.7603
4206.0667 | 757.6001
4207.0667 | 746.3534
4208.0667 | 753.5859
4209.0667 | 768.6661
4210.0667 | 760.5266
4211.0667 | 749.0094
4212.0667 | 733.8839
4213.0667 | 735.569
4214.0667 | 736.6264
4215.0667 | 737.232
4216.0667 | 758.799
4217.0667 | 763.5216
4218.0667 | 752.2863
4219.0667 | 747.3141
4220.0667 | 727.1037
4221.0667 | 710.8706
4222.0667 | 728.7204
4223.0667 | 727.8205
4224.0667 | 746.7211
4225.0667 | 751.1469
4226.0667 | 734.7909
4227.0823 | 714.1857
4228.0667 | 730.2902
4229.0667 | 729.2541
4230.0667 | 714.5949
4231.0667 | 720.9367
4232.0667 | 701.9973
4233.0667 | 686.3511
4234.0667 | 686.0194
4235.0667 | 697.1391
4236.0667 | 697.4958
4237.0667 | 693.2338
4238.0667 | 695.5276
4239.0667 | 699.6223
4240.0667 | 710.1195
4241.0667 | 683.8237
4242.0667 | 682.4428
4243.0667 | 698.3696
4244.0823 | 687.8987
4245.0667 | 691.6051
4246.0667 | 673.5373
4247.0667 | 675.0852
4248.0667 | 683.9123
4249.0667 | 673.7552
4250.0667 | 679.1857
4251.0667 | 682.0561
4252.0667 | 688.3277
4253.0667 | 682.4411
4254.0667 | 692.8601
4255.0667 | 691.2179
4256.0667 | 666.7078
4257.0823 | 660.4644
4258.0667 | 648.5013
4259.0823 | 671.2068
4260.0667 | 677.8717
4261.0667 | 688.4681
4262.0667 | 679.763
4263.0667 | 687.4571
4264.0667 | 689.9151
4265.0667 | 673.4937
4266.0667 | 665.3698
4267.0667 | 675.6077
4268.0823 | 694.7916
4269.0667 | 686.8393
4270.0667 | 704.9831
4271.0823 | 719.2682
4272.0823 | 715.5798
4273.0667 | 696.2453
4274.0823 | 727.0837
4275.0667 | 720.1333
4276.0667 | 719.5833
4277.0823 | 724.6814
4278.0667 | 717.2154
4279.0667 | 745.3648
4280.0667 | 750.9486
4281.0667 | 749.7521
4282.0667 | 746.4149
4283.0667 | 767.1178
4284.0667 | 768.2325
4285.0667 | 763.886
4286.0667 | 754.8629
4287.0667 | 725.6906
4288.0667 | 715.3163
4289.0667 | 742.6433
4290.0667 | 757.6773
4291.0667 | 761.0424
4292.0667 | 737.1832
4293.0667 | 744.6359
4294.0667 | 758.6646
4295.0667 | 770.3891
4296.0667 | 779.8848
4297.0667 | 786.5421
4298.0667 | 794.1306
4299.0667 | 800.9859
4300.0667 | 815.6691
4301.0667 | 800.3507
4302.0979 | 801.5322
4303.0667 | 791.117
4304.0667 | 799.5734
4305.0667 | 792.2065
4306.0667 | 787.8834
4307.0667 | 804.5428
4308.0667 | 818.7415
4309.0667 | 809.4977
4310.0667 | 788.6393
4311.0667 | 793.3317
4312.0667 | 781.1927
4313.0667 | 781.2572
4314.0667 | 768.4694
4315.0667 | 778.2973
4316.0667 | 775.2019
4317.0823 | 788.4145
4318.0667 | 785.2727
4319.0667 | 788.8457
4320.0667 | 807.0042
4321.0667 | 817.7148
4322.0667 | 804.2007
4323.0667 | 810.6293
4324.0667 | 813.2359
4325.0667 | 792.1549
4326.0667 | 788.1929
4327.0667 | 790.0357
4328.0667 | 804.8287
4329.0667 | 800.1155
4330.0667 | 780.6851
4331.0667 | 785.0124
4332.0667 | 790.6434
4333.0667 | 780.5581
4334.0667 | 787.7955
4335.0667 | 809.8151
4336.0667 | 787.3556
4337.0667 | 775.0055
4338.0667 | 768.1208
4339.0667 | 766.9018
4340.0667 | 783.4151
4341.0667 | 787.3776
4342.0667 | 779.3403
4343.0667 | 786.3642
4344.0667 | 796.997
4345.0667 | 797.9446
4346.0667 | 796.1136
4347.0667 | 819.7846
4348.0667 | 834.9401
4349.0667 | 832.4501
4350.0667 | 841.7402
4351.0667 | 846.5391
4352.0667 | 849.0864
4353.0667 | 855.0807
4354.0667 | 851.0398
4355.0667 | 854.2672
4356.0667 | 866.5334
4357.0667 | 867.3156
4358.0667 | 874.6661
4359.0667 | 858.4047
4360.0667 | 837.3183
4361.0667 | 839.4676
4362.0667 | 839.845
4363.0667 | 850.3191
4364.0667 | 836.6806
4365.0667 | 814.2173
4366.0667 | 821.5454
4367.0667 | 835.6716
4368.0667 | 847.4038
4369.0667 | 850.3008
4370.0667 | 849.4435
4371.0667 | 858.1944
4372.0667 | 852.2611
4373.0667 | 846.071
4374.0667 | 831.7753
4375.0667 | 819.3894
4376.0667 | 807.6849
4377.0667 | 791.9759
4378.0667 | 782.8482
4379.0667 | 785.6903
4380.0667 | 796.4279
4381.0667 | 808.5073
4382.0667 | 796.3294
4383.0667 | 777.2334
4384.0667 | 755.4529
4385.0667 | 729.1325
4386.0667 | 742.3178
4387.0667 | 742.54
4388.0667 | 756.7692
4389.0667 | 780.5384
4390.0667 | 798.1145
4391.0667 | 779.6557
4392.0667 | 762.7828
4393.0667 | 762.8081
4394.0667 | 791.3537
4395.0667 | 779.2707
4396.0667 | 792.0434
4397.0667 | 812.2871
4398.0667 | 826.4999
4399.0667 | 825.3126
4400.0667 | 830.0759
4401.0667 | 812.2672
4402.0667 | 816.2645
4403.0667 | 806.9443
4404.0667 | 787.2265
4405.0667 | 788.0324
4406.0667 | 812.4315
4407.0823 | 830.3204
4408.0667 | 829.7348
4409.0667 | 806.5375
4410.0667 | 771.4167
4411.0667 | 768.6821
4412.0667 | 778.9819
4413.0667 | 784.5751
4414.0667 | 789.9245
4415.0667 | 801.9122
4416.0667 | 806.853
4417.0667 | 819.0882
4418.0667 | 823.341
4419.0823 | 823.1746
4420.0667 | 828.5191
4421.0667 | 847.4701
4422.0667 | 853.3761
4423.0667 | 845.2594
4424.0667 | 843.7701
4425.0667 | 830.0983
4426.0667 | 842.3026
4427.0667 | 845.6195
4428.0667 | 840.2521
4429.0667 | 852.3594
4430.0667 | 851.6511
4431.0667 | 840.0694
4432.0667 | 829.2227
4433.0667 | 802.1637
4434.0667 | 785.1272
4435.0667 | 778.9428
4436.0667 | 802.6303
4437.0823 | 813.5329
4438.0667 | 811.4253
4439.0667 | 800.687
4440.0667 | 797.6004
4441.0667 | 782.9296
4442.0667 | 753.9994
4443.0667 | 762.1318
4444.0667 | 772.7321
4445.0667 | 789.1178
4446.0667 | 783.9776
4447.0667 | 786.8306
4448.0667 | 793.2003
4449.0667 | 782.9213
4450.0667 | 761.6806
4451.0667 | 756.7424
4452.0667 | 755.471
4453.0667 | 750.5093
4454.0667 | 767.9217
4455.0667 | 777.1385
4456.0667 | 779.8921
4457.0667 | 783.9251
4458.0667 | 800.628
4459.0667 | 793.7137
4460.0667 | 796.687
4461.0667 | 790.696
4462.0667 | 777.5409
4463.0667 | 789.8715
4464.0667 | 800.16
4465.0667 | 775.5742
4466.0667 | 769.3297
4467.0667 | 790.1252
4468.0667 | 792.0421
4469.0667 | 806.8478
4470.0667 | 794.7584
4471.0667 | 765.2102
4472.0667 | 750.1655
4473.0667 | 729.8985
4474.0823 | 741.1445
4475.0667 | 766.8669
4476.0667 | 772.277
4477.0667 | 739.0579
4478.0667 | 722.1213
4479.0667 | 724.1507
4480.0667 | 748.6732
4481.0667 | 777.015
4482.0667 | 792.39
4483.0667 | 805.2301
4484.0667 | 811.5004
4485.0667 | 816.0884
4486.0667 | 825.6218
4487.0667 | 812.1298
4488.0667 | 810.1358
4489.0667 | 805.8578
4490.0667 | 779.701
4491.0667 | 761.13
4492.0667 | 745.6091
4493.0667 | 736.0484
4494.0667 | 738.0967
4495.0667 | 745.4433
4496.0667 | 731.1801
4497.0667 | 752.4476
4498.0667 | 769.0724
4499.0667 | 781.5979
4500.0667 | 768.7645
4501.0667 | 779.8019
4502.0667 | 782.7206
4503.0823 | 790.9067
4504.0823 | 790.2162
4505.0667 | 772.3395
4506.0667 | 767.0025
4507.0823 | 739.3279
4508.0823 | 728.4947
4509.0823 | 751.5985
4510.0667 | 744.1422
4511.0667 | 743.9157
4512.0667 | 761.8912
4513.0667 | 781.2948
4514.0667 | 805.5357
4515.0667 | 801.2144
4516.0667 | 775.7277
4517.0667 | 766.5132
4518.0667 | 771.6365
4519.0823 | 781.9858
4520.0667 | 761.937
4521.0667 | 759.9944
4522.0667 | 775.3972
4523.0667 | 773.6314
4524.0667 | 787.5343
4525.0667 | 791.8033
4526.0667 | 774.0759
4527.0667 | 769.7679
4528.0667 | 759.17
4529.0667 | 737.0158
4530.0667 | 749.635
4531.0667 | 748.0511
4532.0667 | 729.9659
4533.0667 | 738.5807
4534.0823 | 765.1291
4535.0667 | 773.8471
4536.0667 | 765.7621
4537.0667 | 759.2135
4538.0667 | 770.4876
4539.0667 | 772.5311
4540.0667 | 780.8802
4541.0667 | 781.1427
4542.0667 | 789.2352
4543.0667 | 785.6257
4544.0667 | 758.2244
4545.0667 | 758.721
4546.0667 | 757.7706
4547.0667 | 756.5386
4548.0667 | 769.3033
4549.0667 | 777.6041
4550.0667 | 755.6311
4551.0823 | 731.022
4552.0667 | 756.818
4553.0667 | 783.4079
4554.0667 | 783.4882
4555.0667 | 779.1431
4556.0667 | 746.0415
4557.0667 | 744.7935
4558.0667 | 735.9815
4559.0667 | 722.9736
4560.0667 | 708.5825
4561.0667 | 713.1601
4562.0667 | 723.3113
4563.0667 | 745.3287
4564.0667 | 772.829
4565.0667 | 803.1414
4566.0667 | 816.7103
4567.0667 | 815.333
4568.0667 | 811.491
4569.0667 | 806.1607
4570.0667 | 792.5866
4571.0667 | 783.4496
4572.0667 | 790.9819
4573.0667 | 776.3428
4574.0667 | 754.4054
4575.0667 | 724.8489
4576.0667 | 726.2138
4577.0667 | 730.5013
4578.0667 | 735.5638
4579.0667 | 738.3604
4580.0667 | 746.7603
4581.0667 | 745.5402
4582.0667 | 731.149
4583.0667 | 729.1395
4584.0667 | 721.7063
4585.0667 | 710.6838
4586.0667 | 734.4729
4587.0667 | 759.0535
4588.0667 | 785.5389
4589.0667 | 796.5808
4590.0667 | 805.1972
4591.0667 | 769.2009
4592.0667 | 759.1141
4593.0667 | 732.9505
4594.0667 | 711.5338
4595.0667 | 708.4179
4596.0667 | 694.4787
4597.0667 | 691.8891
4598.0667 | 691.572
4599.0667 | 680.1201
4600.0667 | 668.1746
4601.0667 | 687.3867
4602.0667 | 675.4592
4603.0667 | 680.0043
4604.0667 | 684.2209
4605.0667 | 683.1739
4606.0667 | 684.7742
4607.0667 | 688.8307
4608.0667 | 700.4177
4609.0667 | 719.3423
4610.0667 | 716.5127
4611.0667 | 702.5521
4612.0667 | 711.5503
4613.0667 | 725.1215
4614.0667 | 714.1715
4615.0667 | 711.1304
4616.0667 | 710.3165
4617.0667 | 706.6672
4618.0667 | 695.1338
4619.0667 | 725.2069
4620.0667 | 753.7997
4621.0667 | 766.0797
4622.0667 | 762.1482
4623.0667 | 775.6653
4624.0667 | 787.0474
4625.0667 | 780.967
4626.0667 | 784.2696
4627.0667 | 788.343
4628.0667 | 785.5567
4629.0667 | 807.5308
4630.0667 | 816.486
4631.0667 | 822.601
4632.0667 | 820.8457
4633.0667 | 815.9876
4634.0667 | 802.6137
4635.0667 | 781.6807
4636.0667 | 786.2165
4637.0667 | 774.1526
4638.0667 | 778.8067
4639.0667 | 792.0316
4640.0667 | 777.192
4641.0667 | 797.1552
4642.0667 | 804.0069
4643.0667 | 805.6502
4644.0667 | 807.2042
4645.0667 | 816.3475
4646.0667 | 818.1346
4647.0667 | 832.6759
4648.0667 | 843.9994
4649.0667 | 826.8014
4650.0667 | 809.7909
4651.0667 | 790.0282
4652.0667 | 791.4906
4653.0667 | 781.6231
4654.0667 | 765.0584
4655.0667 | 745.9767
4656.0667 | 735.3038
4657.0667 | 732.0138
4658.0667 | 744.4536
4659.0667 | 748.8427
4660.0667 | 750.9356
4661.0667 | 740.0295
4662.0667 | 714.022
4663.0667 | 730.1209
4664.0667 | 749.4521
4665.0667 | 746.9569
4666.0667 | 749.4841
4667.0667 | 764.9177
4668.0667 | 747.7335
4669.0823 | 721.5624
4670.0667 | 708.1483
4671.0667 | 696.674
4672.0667 | 693.7709
4673.0667 | 688.1398
4674.0667 | 686.8581
4675.0667 | 688.8149
4676.0667 | 696.5238
4677.0667 | 723.1022
4678.0667 | 745.8937
4679.0667 | 744.3748
4680.0667 | 749.5737
4681.0667 | 741.3429
4682.0667 | 746.43
4683.0667 | 755.6238
4684.0667 | 744.002
4685.0667 | 757.7627
4686.0667 | 743.0338
4687.0667 | 731.7857
4688.0667 | 713.287
4689.0667 | 705.5978
4690.0667 | 692.831
4691.0667 | 710.1635
4692.0667 | 746.6546
4693.0667 | 748.3028
4694.0667 | 739.5275
4695.0667 | 752.1588
4696.0667 | 754.3963
4697.0667 | 763.0769
4698.0667 | 746.6837
4699.0667 | 739.9547
4700.0667 | 708.1278
4701.0667 | 683.1383
4702.0667 | 684.6482
4703.0667 | 708.1995
4704.0667 | 711.069
4705.0667 | 703.1483
4706.0667 | 720.6994
4707.0667 | 713.7896
4708.0667 | 699.6829
4709.0823 | 686.9734
4710.0667 | 709.294
4711.0667 | 735.5316
4712.0667 | 745.6452
4713.0667 | 738.8841
4714.0667 | 740.5
4715.0667 | 745.3469
4716.0667 | 733.9516
4717.0667 | 725.6639
4718.0667 | 705.9346
4719.0667 | 682.4428
4720.0667 | 668.6272
4721.0667 | 688.3849
4722.0667 | 723.8051
4723.0667 | 732.4519
4724.0667 | 747.0889
4725.0667 | 763.6766
4726.0667 | 777.0091
4727.0667 | 777.784
4728.0667 | 777.3051
4729.0667 | 776.6609
4730.0667 | 771.1531
4731.0667 | 759.2027
4732.0667 | 732.3537
4733.0667 | 736.4227
4734.0667 | 728.6911
4735.0667 | 720.4287
4736.0667 | 707.1602
4737.0667 | 704.6983
4738.0667 | 708.2141
4739.0667 | 701.7946
4740.0667 | 698.2903
4741.0667 | 686.798
4742.0667 | 690.6978
4743.0667 | 687.2739
4744.0667 | 678.9314
4745.0667 | 674.5667
4746.0667 | 664.6113
4747.0667 | 687.6574
4748.0667 | 712.284
4749.0823 | 711.4805
4750.0667 | 735.2784
4751.0667 | 745.7239
4752.0667 | 748.8629
4753.0667 | 767.9854
4754.0667 | 751.9233
4755.0667 | 781.3012
4756.0667 | 786.1518
4757.0667 | 787.3074
4758.0667 | 782.1144
4759.0667 | 766.6943
4760.0667 | 750.9932
4761.0667 | 736.6725
4762.0667 | 751.2841
4763.0667 | 771.8725
4764.0667 | 778.5379
4765.0667 | 793.6228
4766.0667 | 800.8013
4767.0667 | 793.7555
4768.0667 | 786.0743
4769.0667 | 793.8986
4770.0667 | 804.8597
4771.0667 | 773.7719
4772.0667 | 749.1196
4773.0667 | 759.4337
4774.0667 | 747.98
4775.0667 | 741.2071
4776.0667 | 741.3216
4777.0667 | 730.0327
4778.0667 | 734.1512
4779.0667 | 727.1372
4780.0667 | 723.7909
4781.0667 | 743.6185
4782.0667 | 760.8435
4783.0667 | 754.0293
4784.0667 | 721.2459
4785.0667 | 719.5739
4786.0667 | 735.1542
4787.0667 | 727.0715
4788.0667 | 738.5417
4789.0667 | 731.0695
4790.0667 | 739.6801
4791.0667 | 761.2935
4792.0667 | 780.7803
4793.0667 | 779.4092
4794.0823 | 785.057
4795.0667 | 799.1807
4796.0667 | 812.7548
4797.0667 | 821.6769
4798.0667 | 805.7348
4799.0667 | 789.7856
4800.0667 | 796.2018
4801.0667 | 785.7093
4802.0667 | 776.3172
4803.0667 | 766.3357
4804.0667 | 768.9119
4805.0667 | 758.9847
4806.0667 | 735.3508
4807.0667 | 702.9129
4808.0667 | 726.8687
4809.0823 | 764.9483
4810.0667 | 793.6576
4811.0667 | 815.5334
4812.0667 | 813.0687
4813.0667 | 822.2032
4814.0667 | 820.1493
4815.0667 | 805.5144
4816.0667 | 790.4931
4817.0667 | 787.1643
4818.0667 | 798.5622
4819.0667 | 817.3673
4820.0667 | 824.7499
4821.0667 | 838.2078
4822.0667 | 842.064
4823.0667 | 822.0125
4824.0667 | 815.8216
4825.0667 | 818.5729
4826.0667 | 819.8396
4827.0667 | 817.684
4828.0667 | 809.064
4829.0667 | 810.9833
4830.0667 | 832.0206
4831.0667 | 845.6954
4832.0667 | 852.3044
4833.0667 | 857.9612
4834.0667 | 857.3316
4835.0667 | 845.3312
4836.0667 | 841.1199
4837.0667 | 832.9303
4838.0667 | 837.4674
4839.0667 | 843.8206
4840.0667 | 842.9677
4841.0667 | 841.0457
4842.0667 | 847.2066
4843.0667 | 846.467
4844.0667 | 853.7127
4845.0667 | 857.5958
4846.0667 | 859.0964
4847.0667 | 839.844
4848.0667 | 823.3702
4849.0823 | 828.7823
4850.0667 | 844.4058
4851.0667 | 834.3055
4852.0667 | 830.5377
4853.0667 | 843.5347
4854.0667 | 850.0443
4855.0667 | 839.3168
4856.0667 | 821.3367
4857.0667 | 815.3038
4858.0667 | 836.2526
4859.0667 | 835.5428
4860.0667 | 853.4263
4861.0667 | 861.2072
4862.0667 | 868.7966
4863.0667 | 871.1608
4864.0667 | 847.5471
4865.0667 | 833.6194
4866.0667 | 830.9905
4867.0667 | 836.415
4868.0667 | 832.1336
4869.0667 | 838.9681
4870.0667 | 847.6732
4871.0667 | 850.7185
4872.0667 | 849.0525
4873.0667 | 839.5344
4874.0667 | 814.5959
4875.0667 | 800.2411
4876.0667 | 770.6826
4877.0667 | 777.1175
4878.0667 | 790.5817
4879.0667 | 773.7798
4880.0667 | 788.7304
4881.0667 | 802.6594
4882.0667 | 808.7697
4883.0667 | 828.8148
4884.0667 | 842.7539
4885.0667 | 815.5836
4886.0667 | 813.5489
4887.0667 | 797.4113
4888.0667 | 801.8144
4889.0667 | 813.3143
4890.0667 | 805.8485
4891.0667 | 788.6906
4892.0667 | 809.3803
4893.0667 | 808.8618
4894.0667 | 831.0259
4895.0667 | 843.082
4896.0667 | 835.0636
4897.0667 | 844.3521
4898.0667 | 816.8755
4899.0667 | 815.993
4900.0667 | 824.5182
4901.0667 | 834.5215
4902.0667 | 823.0814
4903.0667 | 791.8446
4904.0667 | 799.8785
4905.0667 | 823.8707
4906.0667 | 839.4857
4907.0667 | 834.4424
4908.0667 | 826.1856
4909.0667 | 825.4449
4910.0667 | 833.2443
4911.0667 | 849.6582
4912.0667 | 860.4355
4913.0667 | 868.2103
4914.0667 | 872.3188
4915.0667 | 870.1677
4916.0667 | 873.4633
4917.0667 | 860.4716
4918.0667 | 861.4914
4919.0667 | 841.2665
4920.0667 | 813.7971
4921.0667 | 792.8884
4922.0667 | 812.3622
4923.0667 | 827.7262
4924.0667 | 813.709
4925.0667 | 814.9153
4926.0667 | 820.3562
4927.0667 | 838.2061
4928.0667 | 826.8292
4929.0667 | 810.3974
4930.0667 | 804.829
4931.0667 | 789.2595
4932.0667 | 784.5365
4933.0667 | 800.7771
4934.0667 | 813.9188
4935.0667 | 804.8208
4936.0667 | 799.7082
4937.0667 | 814.4098
4938.0667 | 829.5528
4939.0667 | 808.5388
4940.0667 | 826.3441
4941.0667 | 835.1123
4942.0667 | 836.5234
4943.0667 | 847.7543
4944.0667 | 856.3256
4945.0667 | 847.793
4946.0667 | 856.9294
4947.0667 | 862.5107
4948.0667 | 867.1989
4949.0667 | 875.1126
4950.0667 | 874.0111
4951.0667 | 875.9822
4952.0667 | 883.801
4953.0667 | 883.1725
4954.0667 | 880.5154
4955.0667 | 875.6263
4956.0667 | 870.8694
4957.0667 | 874.1576
4958.0667 | 861.9431
4959.0667 | 843.5943
4960.0667 | 819.3841
4961.0667 | 819.7667
4962.0667 | 818.0249
4963.0667 | 829.9946
4964.0667 | 830.9866
4965.0667 | 828.6452
4966.0667 | 832.681
4967.0667 | 839.908
4968.0667 | 834.0292
4969.0667 | 842.6068
4970.0667 | 851.5534
4971.0667 | 847.452
4972.0667 | 862.2267
4973.0667 | 866.2781
4974.0667 | 873.2086
4975.0667 | 863.6672
4976.0667 | 844.5553
4977.0667 | 848.4195
4978.0667 | 829.3756
4979.0667 | 845.5791
4980.0667 | 854.0333
4981.0667 | 849.5839
4982.0667 | 848.2825
4983.0667 | 800.8739
4984.0823 | 787.4869
4985.0667 | 794.9466
4986.0667 | 805.1885
4987.0667 | 806.4317
4988.0667 | 789.2225
4989.0667 | 814.1545
4990.0667 | 809.7184
4991.0667 | 802.8996
4992.0667 | 815.5167
4993.0667 | 815.5184
4994.0667 | 827.0659
4995.0667 | 833.0001
4996.0667 | 827.3763
4997.0667 | 840.1697
4998.0667 | 847.3812
4999.0823 | 856.9479
5000.0667 | 863.9158
5001.0667 | 874.0567
5002.0667 | 871.1766
5003.0667 | 873.7186
5004.0667 | 840.0071
5005.0667 | 838.1393
5006.0667 | 839.5476
5007.0667 | 854.0721
5008.0667 | 861.1512
5009.0667 | 867.4887
5010.0667 | 855.5654
5011.0667 | 850.2808
5012.0667 | 857.7823
5013.0667 | 869.0218
5014.0667 | 868.7386
5015.0667 | 875.3194
5016.0667 | 873.2014
5017.0667 | 876.7097
5018.0667 | 878.6177
5019.0667 | 868.8764
5020.0667 | 849.666
5021.0667 | 854.7622
5022.0667 | 841.2997
5023.0667 | 826.2976
5024.0823 | 826.6923
5025.0667 | 846.0321
5026.0667 | 855.6031
5027.0667 | 858.6962
5028.0667 | 859.6214
5029.0667 | 861.7575
5030.0667 | 855.9726
5031.0667 | 864.5713
5032.0667 | 862.1259
5033.0667 | 867.7124
5034.0667 | 867.9761
5035.0667 | 860.2525
5036.0667 | 865.2306
5037.0667 | 847.7073
5038.0667 | 835.2564
5039.0823 | 834.8282
5040.0667 | 816.2195
5041.0667 | 816.0842
5042.0667 | 825.5334
5043.0667 | 831.3884
5044.0667 | 824.5991
5045.0667 | 836.3833
5046.0667 | 848.3346
5047.0667 | 855.0554
5048.0667 | 854.8982
5049.0667 | 855.0211
5050.0667 | 857.2645
5051.0667 | 839.3968
5052.0667 | 841.1843
5053.0667 | 845.6733
5054.0667 | 851.4417
5055.0667 | 853.7133
5056.0667 | 850.9168
5057.0667 | 825.6418
5058.0667 | 809.1867
5059.0667 | 813.4826
5060.0667 | 832.8815
5061.0667 | 812.3488
5062.0667 | 781.5688
5063.0667 | 772.1872
5064.0667 | 756.7321
5065.0667 | 749.9391
5066.0667 | 737.5165
5067.0667 | 759.1854
5068.0667 | 767.9648
5069.0667 | 766.1589
5070.0667 | 781.8984
5071.0667 | 791.982
5072.0667 | 784.4225
5073.0667 | 784.5233
5074.0667 | 778.6369
5075.0667 | 763.1434
5076.0667 | 763.6826
5077.0667 | 758.1158
5078.0667 | 773.3134
5079.0823 | 786.1303
5080.0667 | 792.8836
5081.0667 | 778.0916
5082.0667 | 750.4657
5083.0667 | 735.0079
5084.0667 | 751.1129
5085.0667 | 783.8143
5086.0667 | 797.426
5087.0667 | 823.2451
5088.0667 | 838.9532
5089.0667 | 836.9129
5090.0667 | 828.6936
5091.0667 | 825.5774
5092.0667 | 824.9676
5093.0667 | 830.1962
5094.0667 | 822.6381
5095.0667 | 792.7335
5096.0667 | 753.6468
5097.0667 | 742.9206
5098.0667 | 741.4451
5099.0667 | 769.6552
5100.0667 | 779.4607