## Test Conditions
DESIREE-FIRE Intermediate Scale Test Preliminary 1 - Circuit Data Only
Test Date: | 2009-11-06
DCSim DAQ Start Time | 13:36
DCSim Time for Synchronization | 13:37
Heat Source Synchronization | 0:02 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:35
Fire Time | 14:12
Offset | 0:36 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2160 | seconds
Heat Source Offset | 0:37 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2192 | seconds
Heat Source Stop Time | 15:37
Test Duration | 1:25 | hours:minutes:seconds
| 5100 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 7, 8, 9 represents the middle of the tray located in E Position. It is labeled as "south mid", "south bottom", and "burner" in the raw temperature file. The TC nomenclature was not changed after Preliminary Test 2
Large Coil | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 7, 8, 9 represents the middle of the tray located in E Position. It is labeled as "south mid", "south bottom", and "burner" in the raw temperature file. The TC nomenclature was not changed after Preliminary Test 2
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.65625 | 122.818 | -60.7452 | 61.7432 | -0.27527 | 0.012924 | 0.0023072 | 0.0066137 | -0.0017752 | -0.0014164 | -0.0043793 | -0.16502 | -0.0040097 | -0.003262 | -0.00048061 | 4.9132e-05 | -0.0069578 | 0.13275 | 0.12817 | 0.16022 | 0.10529 | 0.15106 | 0.11902 | 0.004578 | 0.082397 | 0.17853 | -0.022888 | 0.10986 | 0.10529 | 0.041199 | -0.018311 | 60.8643 | 60.7498 | -61.5921 | 60.8734 | 60.8505 | 0.10071 | -61.6104 | 60.7864 | 60.7269 | -61.6333 | 60.8276 | 60.7224 | -0.004577 | -61.6379 | 60.8963 | 60.878 | 60.9055 | -61.7386 | 60.8551 | 60.8505 | 60.9238 | -61.7615
1.0156 | 122.7219 | -60.8322 | 61.7889 | 0.12146 | 0.010788 | 0.0031616 | -0.00086308 | -0.002416 | -0.0039798 | -0.0039521 | 0.14778 | -0.0059323 | -0.0019802 | 0.0018692 | 0.0017581 | -0.005035 | 0.013733 | 0.013733 | 0.027466 | -0.018311 | -0.036621 | -0.027466 | -0.12817 | 0.10986 | 0.064087 | -0.018311 | -0.013733 | -0.045776 | -0.027466 | -0.091553 | 60.8047 | 60.704 | -61.8256 | 60.8459 | 60.8139 | 0.10986 | -61.7752 | 60.8047 | 60.7407 | -61.8027 | 60.9421 | 60.8139 | 0.073242 | -61.8347 | 60.7956 | 60.8459 | 60.8597 | -61.9171 | 60.8185 | 60.7864 | 60.8963 | -61.8805
2.7656 | 122.731 | -60.8139 | 61.8027 | 0.037537 | 0.012283 | 0.0010254 | -0.00064948 | -0.004125 | 0.0020016 | -0.0020295 | 0.03334 | 4.9068e-05 | -0.0047574 | 0.0012284 | 0.0053897 | -0.005676 | -0.059509 | -0.14648 | -0.11902 | -0.09613 | 0.022888 | -0.045776 | -0.16479 | -0.022888 | -0.11902 | -0.19226 | 0.027466 | -0.009155 | -0.064087 | -0.13275 | 60.7681 | 60.6491 | -61.7798 | 60.6674 | 60.7178 | 0.068665 | -61.8622 | 60.7498 | 60.6812 | -61.7752 | 60.791 | 60.6216 | -0.05951 | -61.8118 | 60.8368 | 60.7544 | 60.6949 | -61.9675 | 60.8414 | 60.8047 | 60.6949 | -61.9354
4.4375 | 122.8363 | -60.7773 | 61.7661 | -0.17609 | 0.012711 | 0.0018798 | 0.0072547 | -0.00092065 | -0.0014164 | -0.0018159 | -0.24895 | -0.0042233 | -0.0030484 | -5.3406e-05 | 4.9132e-05 | -0.0041806 | 0.068665 | 0.050354 | 0.041199 | 0.036621 | 0.13733 | 0.07782 | -0.041199 | 0.073242 | 0.10529 | -0.036621 | 0.11444 | 0.10529 | 0.018311 | -0.027466 | 60.8551 | 60.7361 | -61.6287 | 60.8276 | 60.8139 | 0.07782 | -61.6974 | 60.7956 | 60.7498 | -61.6516 | 60.8505 | 60.7407 | -0.009155 | -61.6608 | 60.9146 | 60.8459 | 60.8185 | -61.8073 | 60.8917 | 60.8826 | 60.8826 | -61.7935
6.1875 | 122.8455 | -60.759 | 61.7569 | -0.11505 | 0.010574 | 0.0027344 | 0.0057593 | -0.0034842 | -0.0031254 | -0.0048065 | -0.096359 | -0.0072141 | -0.0041164 | 0.00058739 | -0.0010191 | -0.0058896 | 0.16022 | 0.16937 | 0.17395 | 0.10986 | 0.082397 | 0.10529 | -0.032043 | 0.18768 | 0.28381 | 0.10529 | 0.036621 | 0.036621 | 0.068665 | -0.018311 | 60.8643 | 60.7269 | -61.6745 | 60.9283 | 60.8688 | 0.14191 | -61.5967 | 60.8276 | 60.7407 | -61.7203 | 60.9467 | 60.8643 | 0.1236 | -61.7203 | 60.8414 | 60.9192 | 60.9329 | -61.7889 | 60.7956 | 60.7956 | 61.0428 | -61.7752
7.9219 | 122.8088 | -60.8002 | 61.7935 | -0.22186 | 0.011643 | 0.0031616 | 0.0046911 | -0.0017752 | -0.00013458 | -0.0030975 | -0.18791 | -0.0035825 | -0.0039028 | -0.0021896 | 0.0011173 | -0.0037534 | 0.10986 | 0.082397 | 0.10071 | 0.073242 | 0.15564 | 0.086975 | -0.009155 | 0.073242 | 0.13733 | -0.022888 | 0.12817 | 0.091553 | 0.013733 | -0.027466 | 60.8871 | 60.791 | -61.6379 | 60.8826 | 60.8734 | 0.082397 | -61.6837 | 60.8139 | 60.7727 | -61.6653 | 60.8734 | 60.7773 | 0.004578 | -61.702 | 60.9558 | 60.91 | 60.9009 | -61.8027 | 60.9283 | 60.8917 | 60.9375 | -61.821
9.5938 | 122.8638 | -60.7407 | 61.7569 | -0.13794 | 0.0086517 | 0.004657 | 0.0029821 | -0.0019888 | -0.0054752 | -0.0016021 | -0.058212 | -0.0070003 | -0.00048483 | -0.0021896 | -0.00016447 | -0.0048214 | 0.14648 | 0.13733 | 0.15106 | 0.09613 | 0.091553 | 0.10529 | -0.013733 | 0.18768 | 0.28381 | 0.11902 | 0.050354 | 0.032043 | 0.045776 | -0.018311 | 60.8459 | 60.7269 | -61.6653 | 60.878 | 60.8368 | 0.10986 | -61.6104 | 60.7864 | 60.7224 | -61.7065 | 60.9283 | 60.8597 | 0.13733 | -61.7249 | 60.8322 | 60.8871 | 60.8917 | -61.7706 | 60.791 | 60.7727 | 61.0245 | -61.7752
11.3281 | 122.8043 | -60.7727 | 61.7752 | 0.1825 | 0.011429 | 0.0023072 | 0.0019141 | -0.0026296 | -0.0014164 | -0.0011749 | 0.094375 | -0.0035825 | -0.0043302 | 0.00058739 | 0.0056033 | -0.0063168 | 0.018311 | -0.018311 | -0.004578 | -0.032043 | -0.032043 | -0.004578 | -0.15564 | 0.082397 | 0.032043 | -0.036621 | -0.027466 | -0.054932 | -0.054932 | -0.082397 | 60.7681 | 60.6171 | -61.8073 | 60.7544 | 60.7407 | 0.1236 | -61.7569 | 60.7178 | 60.6903 | -61.8027 | 60.8551 | 60.7361 | 0.045776 | -61.8301 | 60.7407 | 60.791 | 60.7681 | -61.9308 | 60.7452 | 60.7178 | 60.8047 | -61.8576
13.0625 | 122.8775 | -60.759 | 61.7432 | -0.11505 | 0.011002 | 0.0010254 | 0.0023413 | -0.0034842 | 0.0015744 | -0.0013885 | -0.20317 | -0.0031551 | -0.004971 | -0.00026701 | 0.0045351 | -0.0043942 | 0.064087 | 0.009155 | 0.027466 | 0.027466 | 0.11444 | 0.045776 | -0.073242 | 0.068665 | 0.054932 | -0.068665 | 0.054932 | 0.018311 | -0.018311 | -0.09613 | 60.8047 | 60.6857 | -61.6287 | 60.7681 | 60.7864 | 0.10071 | -61.6791 | 60.7407 | 60.6628 | -61.6882 | 60.8276 | 60.6903 | 0.027465 | -61.7249 | 60.8734 | 60.8231 | 60.7864 | -61.8164 | 60.8139 | 60.7773 | 60.8139 | -61.8393
14.7969 | 122.818 | -60.7819 | 61.7935 | -0.069275 | 0.012711 | 0.0018798 | 0.0031957 | -0.00027985 | 0.001788 | -0.0022431 | -0.13451 | -0.0035825 | -0.0053982 | 0.00016019 | 0.0026125 | -0.0071714 | 0.064087 | 0.027466 | 0.036621 | 0 | 0.041199 | 0.022888 | -0.10071 | 0.050354 | 0.022888 | -0.059509 | 0.022888 | 0.004578 | -0.027466 | -0.10529 | 60.8047 | 60.6812 | -61.7523 | 60.8093 | 60.7819 | 0.10071 | -61.7294 | 60.7544 | 60.6766 | -61.7706 | 60.8322 | 60.7224 | 0.045777 | -61.7889 | 60.8231 | 60.8459 | 60.8185 | -61.8942 | 60.8047 | 60.7864 | 60.8047 | -61.8988
16.4688 | 122.8592 | -60.759 | 61.7615 | -0.12268 | 0.013565 | 0.0018798 | 0.0053321 | -0.001348 | 0.00093342 | -0.00074767 | -0.14977 | -0.0037961 | -0.0019802 | 0.0022964 | 0.0017581 | -0.005676 | 0.054932 | 0.018311 | 0.027466 | 0.027466 | 0.073242 | 0.027466 | -0.091553 | 0.041199 | 0.059509 | -0.064087 | 0.045776 | 0.032043 | -0.013733 | -0.10071 | 60.7864 | 60.6674 | -61.6882 | 60.7773 | 60.7864 | 0.11902 | -61.7065 | 60.7452 | 60.6583 | -61.7157 | 60.8002 | 60.6949 | 0.036621 | -61.7294 | 60.8322 | 60.8139 | 60.7864 | -61.853 | 60.8047 | 60.791 | 60.8185 | -61.8622
18.1875 | 122.7264 | -60.8047 | 61.7798 | 0.19775 | 0.010788 | -4.2814e-05 | 0.0019141 | -0.0043386 | -0.0031254 | -0.0026703 | 0.1783 | -0.0042233 | -0.0019802 | 0.00058739 | 0.0013309 | -0.005676 | 0.009155 | 0.004578 | 0.041199 | -0.022888 | -0.054932 | -0.009155 | -0.15106 | 0.10529 | 0.09613 | -0.009155 | -0.045776 | -0.050354 | -0.050354 | -0.082397 | 60.7956 | 60.6537 | -61.8347 | 60.8093 | 60.7819 | 0.12817 | -61.7706 | 60.7544 | 60.7224 | -61.8256 | 60.91 | 60.7956 | 0.073242 | -61.8301 | 60.7498 | 60.8139 | 60.8459 | -61.9308 | 60.759 | 60.7544 | 60.9009 | -61.8622
19.9219 | 122.7539 | -60.8047 | 61.7889 | 0.029907 | 0.013565 | 0.0031616 | 0.0083227 | -0.0022024 | -0.005048 | -0.0035249 | 0.086746 | -0.0052915 | -0.0039028 | 0.00016019 | -0.0037961 | -0.005676 | 0.041199 | 0.022888 | 0.054932 | 0.009155 | 0.050354 | 0.059509 | -0.082397 | 0.082397 | 0.1236 | 0.004578 | 0.045776 | 0.013733 | 0 | -0.054932 | 60.8643 | 60.7224 | -61.7386 | 60.8276 | 60.8139 | 0.091552 | -61.7477 | 60.8047 | 60.7498 | -61.7432 | 60.8871 | 60.8093 | 0.05951 | -61.7752 | 60.8551 | 60.8459 | 60.8597 | -61.8713 | 60.8505 | 60.8185 | 60.9283 | -61.8439
21.5938 | 122.7264 | -60.8276 | 61.7706 | 0.12909 | 0.0092925 | 0.0027344 | 0.0012731 | -0.0034842 | -0.0041934 | -0.0028839 | 0.13252 | -0.0035825 | -0.0039028 | 0.0010148 | 0.0021853 | -0.0065304 | 0.027466 | 0.004578 | 0.050354 | -0.027466 | -0.022888 | 0.004578 | -0.13733 | 0.10986 | 0.11444 | -0.013733 | 0 | -0.004578 | -0.013733 | -0.054932 | 60.8322 | 60.6903 | -61.7935 | 60.8322 | 60.8002 | 0.10986 | -61.7432 | 60.8139 | 60.7727 | -61.7706 | 60.9375 | 60.8139 | 0.041199 | -61.7752 | 60.8047 | 60.8551 | 60.878 | -61.908 | 60.8276 | 60.8231 | 60.9421 | -61.8256
23.3125 | 122.8683 | -60.7864 | 61.7523 | -0.14557 | 0.0095063 | 0.0018798 | 0.0061865 | -0.0015616 | -0.0046206 | -0.0039521 | -0.13451 | -0.0072141 | -0.0036892 | 0.00058739 | -0.00059167 | -0.0058896 | 0.16479 | 0.16022 | 0.17853 | 0.10529 | 0.07782 | 0.09613 | -0.027466 | 0.18768 | 0.30212 | 0.091553 | 0.059509 | 0.059509 | 0.068665 | 0.013733 | 60.8826 | 60.759 | -61.6745 | 60.9467 | 60.8917 | 0.13275 | -61.5875 | 60.8551 | 60.8002 | -61.6928 | 60.9741 | 60.878 | 0.07782 | -61.6928 | 60.8643 | 60.9512 | 60.965 | -61.7798 | 60.8459 | 60.8459 | 61.0886 | -61.7386
24.9688 | 122.7631 | -60.8185 | 61.8164 | -0.092163 | 0.012497 | 0.00038459 | 0.00020512 | -0.0017752 | 0.0056332 | -0.00074767 | -0.13451 | -0.0025143 | -0.0034756 | 0.003151 | 0.0041079 | -0.008453 | 0.07782 | 0.009155 | 0.009155 | 0.004578 | 0.059509 | 0.013733 | -0.09613 | 0.054932 | -0.013733 | -0.10986 | 0.032043 | 0.022888 | -0.045776 | -0.10071 | 60.8322 | 60.7224 | -61.7569 | 60.8276 | 60.8231 | 0.10071 | -61.7386 | 60.7727 | 60.7178 | -61.7844 | 60.8734 | 60.7086 | -0.009155 | -61.7935 | 60.878 | 60.8963 | 60.8276 | -61.9125 | 60.8505 | 60.8414 | 60.8047 | -61.9171
26.7031 | 122.7585 | -60.8139 | 61.8027 | -0.031128 | 0.012711 | 0.00017099 | 0.0019141 | -0.0028432 | 0.0037106 | -0.0011749 | -0.096359 | -0.0020871 | -0.004971 | 0.00080099 | 0.0036807 | -0.0061032 | 0.050354 | -0.004578 | 0 | -0.018311 | 0.064087 | 0.004578 | -0.1236 | 0.013733 | -0.041199 | -0.11444 | 0.032043 | 0.018311 | -0.032043 | -0.11444 | 60.8185 | 60.6903 | -61.7386 | 60.8093 | 60.7956 | 0.10528 | -61.7523 | 60.7819 | 60.6995 | -61.7706 | 60.8276 | 60.6995 | 0 | -61.7844 | 60.878 | 60.8643 | 60.8139 | -61.9263 | 60.8459 | 60.8322 | 60.7727 | -61.9171
28.4219 | 122.7585 | -60.7681 | 61.8073 | -0.069275 | 0.012497 | -0.00047001 | 0.0023413 | -0.0011342 | 0.00071982 | 0.0018157 | -0.073471 | -0.0037961 | 0.00015597 | 0.001442 | 0.0043215 | -0.0046078 | 0.054932 | -0.009155 | 0.004578 | -0.004578 | 0.036621 | 0.027466 | -0.09613 | 0.036621 | -0.013733 | -0.10071 | 0.022888 | 0.032043 | -0.036621 | -0.086975 | 60.7956 | 60.672 | -61.7706 | 60.759 | 60.7635 | 0.091552 | -61.7523 | 60.7315 | 60.6812 | -61.7844 | 60.8047 | 60.6674 | -0.013733 | -61.7752 | 60.8047 | 60.8231 | 60.7727 | -61.9034 | 60.791 | 60.8002 | 60.7544 | -61.8942
30.1406 | 122.8363 | -60.759 | 61.7935 | -0.22949 | 0.013565 | 0.0016662 | 0.0059729 | 0.001002 | -0.0037662 | -0.0030975 | -0.21843 | -0.0044369 | -0.001553 | 0.0018692 | 0.00026273 | -0.0020444 | 0.07782 | 0.032043 | 0.045776 | 0.032043 | 0.15564 | 0.07782 | -0.041199 | 0.073242 | 0.15106 | -0.022888 | 0.11902 | 0.11444 | 0.027466 | -0.022888 | 60.8368 | 60.7178 | -61.6379 | 60.791 | 60.791 | 0.073242 | -61.7157 | 60.7864 | 60.7361 | -61.6745 | 60.8322 | 60.7361 | 0 | -61.6791 | 60.9146 | 60.8368 | 60.8047 | -61.8347 | 60.878 | 60.8734 | 60.91 | -61.8164
31.8906 | 122.8683 | -60.7864 | 61.7294 | -0.084534 | 0.013565 | 0.004657 | 0.0042639 | -0.0032706 | -0.0069706 | -0.0039521 | -0.050583 | -0.0070003 | -0.004971 | -0.0015488 | -0.00080527 | -0.0035398 | 0.10529 | 0.11902 | 0.12817 | 0.09613 | 0.07782 | 0.091553 | -0.022888 | 0.17853 | 0.27924 | 0.086975 | 0.064087 | 0.041199 | 0.050354 | 0 | 60.878 | 60.7635 | -61.6516 | 60.9055 | 60.8826 | 0.11902 | -61.6241 | 60.8368 | 60.7864 | -61.6653 | 60.965 | 60.8734 | 0.086975 | -61.6882 | 60.8643 | 60.8917 | 60.9146 | -61.7523 | 60.8505 | 60.8276 | 61.0657 | -61.7294
33.625 | 122.7448 | -60.8139 | 61.7981 | -0.031128 | 0.013352 | 0.00059819 | 0.00084592 | 0.00014735 | 0.0043514 | -0.00096127 | -0.096359 | -0.0027279 | -0.0036892 | 0.001442 | 0.0038943 | -0.0082394 | 0.054932 | -0.013733 | 0 | -0.013733 | 0.054932 | 0.013733 | -0.10986 | 0.013733 | -0.027466 | -0.12817 | 0.036621 | 0.013733 | -0.045776 | -0.10071 | 60.8276 | 60.704 | -61.7432 | 60.8002 | 60.8002 | 0.09613 | -61.7432 | 60.7681 | 60.7132 | -61.7615 | 60.8276 | 60.6857 | -0.027466 | -61.7844 | 60.8688 | 60.8688 | 60.8139 | -61.908 | 60.8505 | 60.8276 | 60.7864 | -61.8988
35.3438 | 122.8226 | -60.7636 | 61.7523 | -0.19135 | 0.010147 | 0.0038024 | 0.0078955 | -0.0045522 | -0.0046206 | -0.0026703 | -0.11925 | -0.0059323 | -0.0026212 | -0.00090781 | 0.00047633 | -0.0046078 | 0.13733 | 0.14648 | 0.16937 | 0.10986 | 0.09613 | 0.1236 | -0.022888 | 0.16022 | 0.28839 | 0.07782 | 0.064087 | 0.045776 | 0.050354 | 0 | 60.8871 | 60.7407 | -61.6562 | 60.91 | 60.8734 | 0.13275 | -61.615 | 60.8139 | 60.7636 | -61.6882 | 60.9238 | 60.8414 | 0.07782 | -61.7065 | 60.8597 | 60.9009 | 60.9329 | -61.7752 | 60.8276 | 60.8093 | 61.0519 | -61.7523
37.0156 | 122.7859 | -60.791 | 61.8073 | 0.098572 | 0.011002 | 0.0020936 | 0.0017005 | -0.0045522 | 0.00029262 | -0.0033111 | 0.12489 | -0.0048641 | -0.0021938 | 0.00037379 | 0.0047489 | -0.0063168 | -0.036621 | -0.10986 | -0.09613 | -0.082397 | 0.032043 | -0.041199 | -0.15106 | 0 | -0.091553 | -0.10986 | 0.018311 | -0.009155 | -0.050354 | -0.11902 | 60.7498 | 60.64 | -61.7752 | 60.6812 | 60.7086 | 0.068665 | -61.8439 | 60.7407 | 60.672 | -61.7889 | 60.791 | 60.6812 | 0.009156 | -61.8164 | 60.8231 | 60.7544 | 60.6949 | -61.9583 | 60.8093 | 60.7819 | 60.6995 | -61.9263
38.75 | 122.7814 | -60.7956 | 61.7706 | 0.15961 | 0.0084381 | 0.0025208 | -0.0015039 | -0.0034842 | -0.0014164 | -0.0016021 | 0.15541 | -0.0048641 | -0.0068936 | 0.00037379 | 0.0038943 | -0.005035 | 0.018311 | 0.004578 | -0.009155 | -0.027466 | -0.022888 | -0.022888 | -0.14648 | 0.07782 | 0.018311 | -0.036621 | -0.041199 | -0.041199 | -0.064087 | -0.086975 | 60.7727 | 60.6491 | -61.7935 | 60.8002 | 60.7681 | 0.11902 | -61.7523 | 60.7315 | 60.7086 | -61.8118 | 60.8734 | 60.759 | 0.050354 | -61.8118 | 60.7727 | 60.8139 | 60.7864 | -61.9171 | 60.7544 | 60.7544 | 60.8139 | -61.8576
40.4375 | 122.7768 | -60.8185 | 61.7844 | 0.16724 | 0.012283 | 0.001239 | 0.0027685 | -0.0026296 | 0.00050622 | -0.0018159 | 0.11726 | -0.0059323 | -0.0034756 | 0.00037379 | 0.0036807 | -0.0052488 | -0.054932 | -0.15106 | -0.11444 | -0.11444 | 0.013733 | -0.054932 | -0.16937 | -0.032043 | -0.12817 | -0.15564 | 0.009155 | -0.013733 | -0.064087 | -0.13275 | 60.7635 | 60.6491 | -61.7706 | 60.6674 | 60.704 | 0.054932 | -61.8393 | 60.7544 | 60.6857 | -61.7752 | 60.7864 | 60.6628 | -0.022889 | -61.7981 | 60.8322 | 60.7635 | 60.704 | -61.9537 | 60.8276 | 60.8047 | 60.6903 | -61.9171
42.1562 | 122.7722 | -60.7956 | 61.7981 | 0.1062 | 0.0099335 | 0.00081179 | 0.0044775 | -0.0026296 | 0.0013608 | -0.0013885 | 0.11726 | -0.0027279 | -0.0041164 | 0.001442 | 0.0034671 | -0.0048214 | -0.045776 | -0.10986 | -0.082397 | -0.082397 | 0.022888 | -0.036621 | -0.16022 | -0.009155 | -0.091553 | -0.13733 | 0.018311 | 0.004578 | -0.068665 | -0.12817 | 60.759 | 60.6354 | -61.7752 | 60.6857 | 60.7132 | 0.07782 | -61.8439 | 60.7269 | 60.6674 | -61.7798 | 60.7864 | 60.6583 | -0.009155 | -61.7935 | 60.8185 | 60.7498 | 60.7132 | -61.9583 | 60.8139 | 60.8002 | 60.704 | -61.9263
43.8281 | 122.8317 | -60.7498 | 61.7661 | -0.16846 | 0.010147 | 0.0027344 | 0.0083227 | -0.00070705 | -0.005048 | -0.0020295 | -0.065842 | -0.0057187 | -0.0021938 | 0.0012284 | 0.0015445 | -0.005676 | 0.16022 | 0.16022 | 0.17853 | 0.10986 | 0.091553 | 0.13275 | 0.004578 | 0.15564 | 0.3067 | 0.07782 | 0.073242 | 0.064087 | 0.064087 | -0.013733 | 60.8826 | 60.7544 | -61.6745 | 60.91 | 60.8597 | 0.10529 | -61.6058 | 60.8139 | 60.7361 | -61.6928 | 60.9055 | 60.8276 | 0.091553 | -61.702 | 60.8414 | 60.91 | 60.9283 | -61.7615 | 60.8231 | 60.8139 | 61.0565 | -61.7798
45.5625 | 122.8729 | -60.7864 | 61.7615 | -0.031128 | 0.0069427 | 0.0023072 | 0.0023413 | -0.0039114 | -0.0056888 | -0.0022431 | 0.018082 | -0.0055051 | -0.0026212 | 0.001442 | -0.00080527 | -0.005676 | 0.07782 | 0.07782 | 0.09613 | 0.064087 | 0.059509 | 0.073242 | -0.059509 | 0.15564 | 0.25635 | 0.064087 | 0.059509 | 0.045776 | 0.045776 | -0.018311 | 60.8597 | 60.7269 | -61.702 | 60.8643 | 60.8505 | 0.1236 | -61.6837 | 60.8322 | 60.7681 | -61.702 | 60.9421 | 60.8505 | 0.082398 | -61.7157 | 60.8459 | 60.8643 | 60.8826 | -61.821 | 60.8459 | 60.8322 | 61.0428 | -61.7798
47.25 | 122.8638 | -60.7498 | 61.7889 | -0.13031 | 0.013138 | 0.0016662 | 0.0027685 | -0.00070705 | 0.0013608 | -0.0016021 | -0.17265 | -0.0033687 | -0.0051846 | 0.00080099 | 0.0032535 | -0.0082394 | 0.086975 | 0.004578 | 0.013733 | 0.027466 | 0.1236 | 0.059509 | -0.068665 | 0.041199 | 0.059509 | -0.068665 | 0.050354 | 0.045776 | -0.036621 | -0.082397 | 60.8093 | 60.6812 | -61.6653 | 60.7544 | 60.7773 | 0.096131 | -61.702 | 60.7132 | 60.6674 | -61.7386 | 60.791 | 60.6812 | 0.013732 | -61.7432 | 60.8734 | 60.8368 | 60.7636 | -61.8576 | 60.8002 | 60.7956 | 60.8093 | -61.8713
49.0156 | 122.7859 | -60.7956 | 61.7706 | 0.045166 | 0.012283 | 0.0031616 | 0.0066137 | -0.002416 | -0.0046206 | -0.0033111 | 0.102 | -0.0067867 | -0.0034756 | 0.00080099 | -0.0014463 | -0.0058896 | 0.036621 | 0.018311 | 0.054932 | 0.027466 | 0.045776 | 0.041199 | -0.07782 | 0.086975 | 0.14191 | -0.004578 | 0.045776 | 0.018311 | 0.009155 | -0.027466 | 60.8368 | 60.7178 | -61.7249 | 60.8139 | 60.8231 | 0.10529 | -61.734 | 60.8047 | 60.7681 | -61.7249 | 60.8826 | 60.791 | 0.022888 | -61.7523 | 60.8414 | 60.8322 | 60.8505 | -61.8484 | 60.8414 | 60.8139 | 60.9375 | -61.7981
50.7031 | 122.8317 | -60.7819 | 61.7523 | -0.16083 | 0.011002 | 0.0040162 | 0.0017005 | -0.0017752 | -0.003339 | -0.0033111 | -0.13451 | -0.0057187 | -0.0019802 | -0.0011216 | 0.0028263 | -0.0063168 | 0.15564 | 0.15106 | 0.16022 | 0.11444 | 0.086975 | 0.10071 | -0.022888 | 0.16479 | 0.27924 | 0.073242 | 0.07782 | 0.036621 | 0.027466 | -0.009155 | 60.8826 | 60.759 | -61.6653 | 60.9329 | 60.8963 | 0.13733 | -61.5967 | 60.8093 | 60.7727 | -61.6745 | 60.9467 | 60.8551 | 0.082397 | -61.7157 | 60.8688 | 60.9375 | 60.9421 | -61.7752 | 60.8597 | 60.8185 | 61.0611 | -61.7615
52.375 | 122.7402 | -60.8139 | 61.7706 | 0.1825 | 0.011002 | 0.00059819 | -8.476e-06 | -0.004125 | 0.00050622 | -0.0022431 | 0.16304 | -0.0057187 | -0.00091223 | -0.00048061 | 0.0030399 | -0.006744 | 0.036621 | 0.022888 | 0.032043 | -0.032043 | -0.064087 | -0.013733 | -0.15564 | 0.10986 | 0.082397 | -0.009155 | -0.041199 | -0.068665 | -0.041199 | -0.10071 | 60.8002 | 60.6583 | -61.8347 | 60.8368 | 60.7819 | 0.1236 | -61.734 | 60.7727 | 60.7132 | -61.8118 | 60.9238 | 60.8047 | 0.091553 | -61.8393 | 60.7498 | 60.8505 | 60.8459 | -61.9263 | 60.7727 | 60.7452 | 60.8963 | -61.8713
54.0469 | 122.7402 | -60.8185 | 61.7889 | 0.052795 | 0.010361 | 0.0031616 | 0.0021277 | -0.0022024 | -0.0041934 | -0.0028839 | 0.102 | -0.0055051 | -0.003262 | -0.0021896 | 0.0026125 | -0.0048214 | 0.032043 | 0.036621 | 0.064087 | -0.004578 | 0.036621 | 0.064087 | -0.09613 | 0.09613 | 0.10529 | -0.009155 | 0.036621 | 0.009155 | 0 | -0.045776 | 60.8826 | 60.7224 | -61.7523 | 60.8551 | 60.8139 | 0.091552 | -61.7569 | 60.8185 | 60.7727 | -61.7523 | 60.9146 | 60.8093 | 0.036621 | -61.7798 | 60.8551 | 60.8505 | 60.8826 | -61.8851 | 60.8551 | 60.8276 | 60.9238 | -61.8347
55.7656 | 122.818 | -60.7864 | 61.7798 | -0.16083 | 0.011429 | 0.0020936 | 0.0081091 | -0.00070705 | -0.0022708 | -0.0022431 | -0.14977 | -0.0055051 | -0.00091223 | 0.00016019 | 0.0015445 | -0.0069578 | 0.15564 | 0.14648 | 0.15106 | 0.10529 | 0.086975 | 0.10986 | -0.022888 | 0.15106 | 0.2655 | 0.050354 | 0.054932 | 0.032043 | 0.045776 | -0.022888 | 60.8963 | 60.7635 | -61.6928 | 60.9329 | 60.8917 | 0.12817 | -61.6241 | 60.8322 | 60.7635 | -61.7249 | 60.9375 | 60.8368 | 0.073242 | -61.7477 | 60.8734 | 60.9421 | 60.9375 | -61.8027 | 60.8414 | 60.8185 | 61.0519 | -61.8027
57.4375 | 122.7768 | -60.7864 | 61.7935 | 0.12909 | 0.010788 | 0.0018798 | 0.00084592 | -0.004125 | 0.003497 | -0.0016021 | 0.048599 | -0.0035825 | -0.0039028 | 0.00251 | 0.0030399 | -0.0046078 | -0.041199 | -0.1236 | -0.11902 | -0.086975 | 0.009155 | -0.054932 | -0.14648 | 0.009155 | -0.11444 | -0.13275 | 0.018311 | 0 | -0.068665 | -0.12817 | 60.7315 | 60.64 | -61.7844 | 60.6628 | 60.6995 | 0.059509 | -61.8347 | 60.7178 | 60.6583 | -61.7752 | 60.7956 | 60.6537 | -0.004577 | -61.7935 | 60.7956 | 60.7452 | 60.6674 | -61.94 | 60.8047 | 60.7864 | 60.672 | -61.9217
59.125 | 122.6944 | -60.8047 | 61.7706 | 0.19775 | 0.010147 | 0.0031616 | 0.0014867 | -0.0028432 | -0.00163 | -0.00032047 | 0.14778 | -0.0050777 | -0.0039028 | -0.0011216 | 0.0036807 | -0.0075986 | 0.022888 | 0.013733 | 0.045776 | -0.036621 | -0.027466 | -0.022888 | -0.14648 | 0.10071 | 0.054932 | -0.018311 | -0.050354 | -0.07782 | -0.054932 | -0.09613 | 60.7819 | 60.6583 | -61.7981 | 60.8185 | 60.7681 | 0.10986 | -61.7477 | 60.7498 | 60.7086 | -61.821 | 60.9055 | 60.7864 | 0.077819 | -61.8484 | 60.7773 | 60.8276 | 60.8505 | -61.9171 | 60.7544 | 60.7269 | 60.8597 | -61.8668
60.7969 | 122.8775 | -60.7544 | 61.7661 | -0.16083 | 0.011215 | 0.0020936 | 0.0017005 | -0.0030568 | 0.0022152 | -0.00096127 | -0.26421 | -0.0031551 | -0.0030484 | 0.00016019 | 0.0038943 | -0.0058896 | 0.082397 | 0.018311 | 0.009155 | 0.032043 | 0.14191 | 0.073242 | -0.059509 | 0.045776 | 0.086975 | -0.068665 | 0.09613 | 0.059509 | 0.018311 | -0.064087 | 60.8276 | 60.6949 | -61.6241 | 60.7727 | 60.7864 | 0.091552 | -61.6837 | 60.7727 | 60.6903 | -61.6699 | 60.8002 | 60.6857 | -0.004578 | -61.7065 | 60.8963 | 60.8368 | 60.7636 | -61.8256 | 60.8505 | 60.8139 | 60.8414 | -61.8301
62.4844 | 122.8775 | -60.7636 | 61.7798 | -0.2066 | 0.010788 | 0.0027344 | 0.0036231 | -0.0017752 | 0.00071982 | -0.0013885 | -0.20317 | -0.0031551 | -0.0019802 | 0.00080099 | 0.0019717 | -0.007385 | 0.068665 | 0.022888 | 0.022888 | 0.041199 | 0.14648 | 0.09613 | -0.041199 | 0.050354 | 0.07782 | -0.059509 | 0.10529 | 0.082397 | 0 | -0.068665 | 60.8597 | 60.7224 | -61.6333 | 60.7864 | 60.8047 | 0.082398 | -61.7111 | 60.7636 | 60.6949 | -61.6745 | 60.8139 | 60.704 | 0.009156 | -61.6974 | 60.91 | 60.8322 | 60.7864 | -61.821 | 60.8688 | 60.8459 | 60.8414 | -61.8484
64.1719 | 122.8592 | -60.7864 | 61.7615 | -0.11505 | 0.014206 | 0.0014526 | 0.0046911 | -0.0022024 | 0.003497 | -0.0018159 | -0.17265 | -0.0044369 | -0.0043302 | 0.00058739 | 0.0011173 | -0.0058896 | 0.073242 | 0.032043 | 0.036621 | 0.032043 | 0.082397 | 0.036621 | -0.09613 | 0.064087 | 0.064087 | -0.054932 | 0.045776 | 0.036621 | -0.018311 | -0.086975 | 60.8231 | 60.6903 | -61.6791 | 60.8185 | 60.8185 | 0.12817 | -61.6882 | 60.7681 | 60.6995 | -61.7157 | 60.8505 | 60.7315 | 0.032043 | -61.7249 | 60.8688 | 60.8597 | 60.8231 | -61.8576 | 60.8322 | 60.8231 | 60.8505 | -61.8484
65.8438 | 122.8363 | -60.7727 | 61.7569 | -0.19897 | 0.011429 | 0.0025208 | 0.0059729 | -0.0019888 | -0.0035526 | -0.0026703 | -0.17265 | -0.0044369 | -0.0028348 | 0.0029374 | -0.0014463 | -0.003967 | 0.1236 | 0.13733 | 0.1236 | 0.10529 | 0.11902 | 0.10529 | -0.018311 | 0.11444 | 0.21515 | 0.018311 | 0.091553 | 0.10529 | 0.041199 | -0.018311 | 60.878 | 60.7544 | -61.6379 | 60.91 | 60.878 | 0.1236 | -61.6333 | 60.8139 | 60.7544 | -61.6653 | 60.8871 | 60.791 | 0.036622 | -61.6516 | 60.8917 | 60.8963 | 60.8963 | -61.7752 | 60.8643 | 60.878 | 60.9879 | -61.7752
67.5625 | 122.7539 | -60.8002 | 61.8027 | 0.11383 | 0.011429 | 0.001239 | 0.0010595 | -0.0022024 | 0.00093342 | -0.00053407 | 0.03334 | -0.0027279 | -0.0028348 | 0.00080099 | 0.0021853 | -0.0048214 | -0.064087 | -0.12817 | -0.11444 | -0.086975 | 0.018311 | -0.054932 | -0.16022 | -0.027466 | -0.13275 | -0.1831 | 0.022888 | -0.004578 | -0.07782 | -0.12817 | 60.7452 | 60.64 | -61.7844 | 60.672 | 60.7132 | 0.073242 | -61.8668 | 60.7224 | 60.672 | -61.7798 | 60.7727 | 60.6171 | -0.054931 | -61.8073 | 60.8185 | 60.7361 | 60.6857 | -61.9629 | 60.8231 | 60.7956 | 60.6674 | -61.9308
69.2344 | 122.7493 | -60.8276 | 61.7981 | -0.023499 | 0.011856 | 0.00059819 | 0.0046911 | -0.002416 | 0.001788 | -0.0018159 | -0.065842 | -0.0031551 | -0.0034756 | 0.0020828 | 0.0032535 | -0.0052488 | 0.027466 | -0.027466 | -0.004578 | -0.013733 | 0.059509 | 0.022888 | -0.11444 | 0.004578 | -0.045776 | -0.12817 | 0.032043 | 0.009155 | -0.050354 | -0.12817 | 60.8505 | 60.7132 | -61.7386 | 60.8002 | 60.8139 | 0.10071 | -61.7706 | 60.7773 | 60.6995 | -61.7661 | 60.8322 | 60.6995 | 0 | -61.7889 | 60.8871 | 60.8551 | 60.8231 | -61.9125 | 60.8597 | 60.8368 | 60.7819 | -61.9263
70.9219 | 122.7997 | -60.7819 | 61.7706 | -0.054016 | 0.014633 | 0.002948 | 0.0044775 | -0.0028432 | 0.0022152 | -0.00053407 | -0.10399 | -0.0040097 | -0.0024076 | 0.00058739 | 0.0034671 | -0.0054624 | 0.059509 | 0.022888 | 0.036621 | -0.004578 | 0.082397 | 0.009155 | -0.10986 | 0.050354 | 0.032043 | -0.068665 | 0.027466 | 0.022888 | -0.041199 | -0.09613 | 60.791 | 60.672 | -61.6882 | 60.8047 | 60.7773 | 0.10529 | -61.7111 | 60.7407 | 60.6857 | -61.7432 | 60.8322 | 60.7132 | 0.027465 | -61.7477 | 60.8643 | 60.8414 | 60.8185 | -61.8805 | 60.8093 | 60.8047 | 60.8139 | -61.8668
72.625 | 122.7402 | -60.8322 | 61.821 | 0.083313 | 0.012283 | 0.00017099 | 0.0034093 | -0.0017752 | 0.001788 | 0.00053413 | 0.03334 | -0.0023007 | -0.0030484 | 0.0012284 | 0.0013309 | -0.005676 | -0.064087 | -0.10986 | -0.086975 | -0.082397 | 0.027466 | -0.013733 | -0.16022 | -0.050354 | -0.10986 | -0.16479 | 0.018311 | 0.013733 | -0.064087 | -0.11902 | 60.8185 | 60.672 | -61.7935 | 60.7224 | 60.7498 | 0.07782 | -61.8851 | 60.7681 | 60.7132 | -61.8027 | 60.7819 | 60.6674 | -0.045776 | -61.8073 | 60.8597 | 60.7681 | 60.7452 | -61.9812 | 60.8505 | 60.8459 | 60.7224 | -61.94
74.2969 | 122.7402 | -60.8047 | 61.7935 | 0.1825 | 0.010788 | 0.0010254 | 0.0044775 | -0.00092065 | -0.0065434 | -0.0020295 | 0.20119 | -0.0050777 | -0.0045438 | -5.3406e-05 | 0.00068993 | -0.0031124 | 0 | 0.027466 | 0.045776 | -0.018311 | -0.050354 | -0.013733 | -0.13275 | 0.091553 | 0.086975 | -0.004578 | -0.022888 | -0.064087 | -0.027466 | -0.082397 | 60.791 | 60.672 | -61.8439 | 60.8322 | 60.7864 | 0.11444 | -61.7935 | 60.7773 | 60.7224 | -61.8164 | 60.8963 | 60.8002 | 0.077819 | -61.8576 | 60.7544 | 60.8047 | 60.8505 | -61.9263 | 60.7819 | 60.7407 | 60.8917 | -61.8759
76.0469 | 122.8683 | -60.7727 | 61.7523 | -0.069275 | 0.010574 | 0.001239 | 0.0031957 | -0.001348 | -0.0076114 | -0.0024567 | -0.035324 | -0.0057187 | -0.0019802 | -0.00048061 | -0.0016599 | -0.0052488 | 0.10986 | 0.12817 | 0.12817 | 0.10071 | 0.086975 | 0.10071 | -0.059509 | 0.17395 | 0.27008 | 0.091553 | 0.064087 | 0.050354 | 0.032043 | -0.018311 | 60.8734 | 60.7132 | -61.6653 | 60.9009 | 60.8734 | 0.16022 | -61.6425 | 60.8047 | 60.7544 | -61.6882 | 60.9467 | 60.8643 | 0.10986 | -61.702 | 60.8597 | 60.8826 | 60.9009 | -61.8118 | 60.8368 | 60.8231 | 61.0428 | -61.7706
77.7188 | 122.7448 | -60.8002 | 61.8256 | 0.0070193 | 0.012497 | 0.00059819 | 0.00063232 | -0.0051932 | 0.0013608 | -0.0026703 | 0.025711 | -0.0027279 | -0.00091223 | 0.0010148 | 0.0036807 | -0.0075986 | 0.009155 | -0.07782 | -0.068665 | -0.064087 | 0.036621 | -0.009155 | -0.13733 | -0.041199 | -0.10071 | -0.15106 | 0.013733 | 0.004578 | -0.073242 | -0.1236 | 60.791 | 60.6628 | -61.7889 | 60.7224 | 60.7361 | 0.073242 | -61.8164 | 60.7269 | 60.6766 | -61.8118 | 60.759 | 60.6491 | -0.027466 | -61.821 | 60.8368 | 60.8093 | 60.7315 | -61.9629 | 60.8139 | 60.8047 | 60.6995 | -61.9492
79.4531 | 122.8226 | -60.759 | 61.7661 | -0.16083 | 0.015488 | 0.0033752 | 0.0044775 | -0.0039114 | -0.0037662 | -0.0039521 | -0.10399 | -0.0097775 | -0.001553 | -0.0024032 | 0.00068993 | -0.0052488 | 0.13733 | 0.15106 | 0.16479 | 0.10986 | 0.09613 | 0.11444 | -0.032043 | 0.14648 | 0.27008 | 0.068665 | 0.064087 | 0.054932 | 0.041199 | -0.018311 | 60.8734 | 60.7269 | -61.6699 | 60.91 | 60.8688 | 0.14191 | -61.6287 | 60.8002 | 60.7407 | -61.702 | 60.9055 | 60.8276 | 0.086976 | -61.7111 | 60.8551 | 60.8963 | 60.9238 | -61.7981 | 60.8231 | 60.8139 | 61.0291 | -61.7844
81.1094 | 122.7493 | -60.8139 | 61.8347 | 0.090942 | 0.011856 | 0.0014526 | -8.476e-06 | -0.0022024 | 7.902e-05 | -0.00096127 | -0.0048066 | -0.0046505 | -0.0013394 | -5.3406e-05 | 0.0051761 | -0.0058896 | -0.050354 | -0.13275 | -0.091553 | -0.068665 | 0.064087 | -0.036621 | -0.16022 | -0.059509 | -0.13275 | -0.17395 | 0.013733 | 0.027466 | -0.073242 | -0.1236 | 60.7773 | 60.6537 | -61.7706 | 60.6812 | 60.7452 | 0.091552 | -61.8851 | 60.7407 | 60.6903 | -61.821 | 60.7544 | 60.64 | -0.050354 | -61.8073 | 60.878 | 60.7636 | 60.7224 | -61.9949 | 60.8276 | 60.8414 | 60.6812 | -61.9583
82.7656 | 122.7493 | -60.8322 | 61.7615 | 0.022278 | 0.0069427 | 0.0042298 | 0.0042639 | -0.0028432 | -0.0059024 | -0.0037385 | 0.102 | -0.0057187 | -0.0028348 | -0.0015488 | -0.0012327 | -0.0046078 | 0.022888 | 0.027466 | 0.050354 | 0.018311 | 0.050354 | 0.032043 | -0.07782 | 0.07782 | 0.13275 | -0.004578 | 0.032043 | 0.022888 | 0.022888 | -0.045776 | 60.8643 | 60.7544 | -61.7111 | 60.8597 | 60.8505 | 0.096131 | -61.7386 | 60.8551 | 60.7864 | -61.7294 | 60.91 | 60.8276 | 0.041198 | -61.7386 | 60.8826 | 60.8551 | 60.8826 | -61.8393 | 60.8643 | 60.8551 | 60.965 | -61.8073
84.4844 | 122.7814 | -60.8047 | 61.7844 | 0.022278 | 0.0088653 | 0.0044434 | 0.0036231 | -0.0026296 | -0.0054752 | -0.0050201 | 0.094375 | -0.0063595 | -0.003262 | -0.00069421 | 0.0011173 | -0.0078122 | 0.036621 | 0.022888 | 0.050354 | 0.018311 | 0.050354 | 0.050354 | -0.07782 | 0.068665 | 0.12817 | 0.004578 | 0.036621 | 0.041199 | 0.004578 | -0.036621 | 60.8551 | 60.7269 | -61.734 | 60.8276 | 60.8231 | 0.096131 | -61.7477 | 60.8093 | 60.7681 | -61.7477 | 60.8734 | 60.8093 | 0.041199 | -61.7432 | 60.8551 | 60.8414 | 60.8551 | -61.8622 | 60.8414 | 60.8459 | 60.9329 | -61.821
86.1406 | 122.8683 | -60.8002 | 61.7798 | -0.19897 | 0.013779 | 0.00017099 | 0.0051183 | -6.6248e-05 | 0.0013608 | -0.0020295 | -0.20317 | -0.0046505 | -0.0017666 | 0.0012284 | 0.0041079 | -0.0086666 | 0.09613 | 0.022888 | 0.036621 | 0.054932 | 0.13275 | 0.091553 | -0.036621 | 0.032043 | 0.045776 | -0.054932 | 0.07782 | 0.050354 | -0.027466 | -0.09613 | 60.8917 | 60.7636 | -61.647 | 60.8231 | 60.8551 | 0.091553 | -61.6837 | 60.7727 | 60.704 | -61.702 | 60.8322 | 60.7452 | 0.041198 | -61.7294 | 60.9329 | 60.8963 | 60.8368 | -61.8164 | 60.878 | 60.8505 | 60.8459 | -61.8759
87.8438 | 122.7356 | -60.7956 | 61.8027 | 0.068054 | 0.012711 | 0.0031616 | 0.0027685 | -0.0043386 | -0.0052616 | -0.0037385 | 0.094375 | -0.0057187 | -0.0019802 | 0.0027236 | 0.00090353 | -0.005035 | 0.045776 | 0.018311 | 0.054932 | -0.009155 | 0.050354 | 0.022888 | -0.09613 | 0.10071 | 0.13275 | -0.009155 | 0.032043 | 0.013733 | 0.009155 | -0.036621 | 60.8185 | 60.6995 | -61.7523 | 60.8139 | 60.7864 | 0.086975 | -61.7569 | 60.8047 | 60.759 | -61.7706 | 60.8963 | 60.7864 | 0.027466 | -61.7889 | 60.8459 | 60.8414 | 60.8505 | -61.8988 | 60.8276 | 60.8093 | 60.9283 | -61.8393
89.5156 | 122.8683 | -60.7636 | 61.7798 | -0.25238 | 0.011429 | 0.0018798 | 0.0053321 | -0.0062612 | -0.0018436 | -0.0022431 | -0.24895 | -0.0040097 | -0.0024076 | 0.0012284 | 0.0019717 | -0.0080258 | 0.09613 | 0.041199 | 0.027466 | 0.059509 | 0.17395 | 0.09613 | -0.027466 | 0.059509 | 0.091553 | -0.045776 | 0.11444 | 0.10071 | -0.004578 | -0.032043 | 60.8597 | 60.7361 | -61.6058 | 60.8047 | 60.8231 | 0.086975 | -61.6837 | 60.759 | 60.7315 | -61.6653 | 60.8231 | 60.7178 | -0.013733 | -61.6791 | 60.9375 | 60.8597 | 60.791 | -61.8073 | 60.878 | 60.8643 | 60.8551 | -61.8118
91.1719 | 122.7722 | -60.8002 | 61.8073 | 0.15961 | 0.011215 | 0.002948 | 0.0010595 | -0.0043386 | 0.0022152 | -0.0018159 | 0.079117 | -0.0033687 | -0.0034756 | 0.00016019 | 0.0030399 | -0.0052488 | -0.036621 | -0.10986 | -0.10071 | -0.091553 | 0.018311 | -0.036621 | -0.17853 | 0.004578 | -0.09613 | -0.13733 | 0.022888 | 0.004578 | -0.07782 | -0.11902 | 60.7636 | 60.6216 | -61.7889 | 60.6903 | 60.7086 | 0.086975 | -61.8439 | 60.7224 | 60.6812 | -61.7844 | 60.8047 | 60.6628 | -0.01831 | -61.8027 | 60.8185 | 60.7636 | 60.6995 | -61.9858 | 60.8231 | 60.8047 | 60.704 | -61.9263
92.8438 | 122.8134 | -60.7727 | 61.7523 | -0.18372 | 0.011856 | 0.0031616 | 0.0076819 | -0.00049345 | -0.0054752 | -0.0020295 | -0.11925 | -0.0061459 | -0.0021938 | -0.0011216 | -0.0014463 | -0.0054624 | 0.14648 | 0.14191 | 0.16479 | 0.10529 | 0.091553 | 0.10529 | -0.032043 | 0.15106 | 0.27008 | 0.059509 | 0.064087 | 0.022888 | 0.036621 | -0.027466 | 60.878 | 60.7407 | -61.6608 | 60.9146 | 60.878 | 0.13733 | -61.6058 | 60.8093 | 60.7452 | -61.6882 | 60.9238 | 60.8322 | 0.086975 | -61.7294 | 60.8643 | 60.9192 | 60.9375 | -61.7844 | 60.8368 | 60.7956 | 61.0428 | -61.7798
94.5156 | 122.7859 | -60.7864 | 61.7752 | 0.1062 | 0.010574 | 0.0010254 | -0.00022208 | -0.00070705 | 0.0013608 | -0.0039521 | 0.063858 | -0.0037961 | -0.0051846 | -0.0021896 | 0.0043215 | -0.0054624 | -0.041199 | -0.10071 | -0.086975 | -0.07782 | 0.013733 | -0.045776 | -0.16937 | 0 | -0.09613 | -0.13275 | 0.022888 | 0.004578 | -0.064087 | -0.11444 | 60.7407 | 60.6171 | -61.7615 | 60.6857 | 60.7086 | 0.091553 | -61.8164 | 60.7224 | 60.672 | -61.7523 | 60.7864 | 60.6537 | -0.01831 | -61.7706 | 60.8002 | 60.7452 | 60.6995 | -61.9446 | 60.8093 | 60.791 | 60.6903 | -61.8896
96.1875 | 122.7264 | -60.791 | 61.8164 | 0.16724 | 0.012283 | 0.00017099 | 0.0031957 | -0.0039114 | -0.0031254 | -0.0018159 | 0.18593 | -0.0029415 | -0.0045438 | 0.001442 | -0.00037807 | -0.0069578 | 0.022888 | 0 | 0.041199 | -0.022888 | -0.054932 | -0.022888 | -0.15106 | 0.09613 | 0.07782 | 0 | -0.041199 | -0.054932 | -0.032043 | -0.091553 | 60.7681 | 60.64 | -61.8713 | 60.791 | 60.7681 | 0.12817 | -61.7935 | 60.759 | 60.6995 | -61.8576 | 60.8871 | 60.791 | 0.091553 | -61.8713 | 60.7361 | 60.8139 | 60.8322 | -61.9675 | 60.7498 | 60.7361 | 60.8688 | -61.908
97.8438 | 122.8683 | -60.7727 | 61.7065 | -0.11505 | 0.0097199 | 0.0035888 | 0.0046911 | -0.0032706 | -0.0052616 | -0.0033111 | -0.058212 | -0.0059323 | -0.001553 | 0.0010148 | 4.9132e-05 | -0.005676 | 0.16022 | 0.14191 | 0.15564 | 0.10071 | 0.10529 | 0.10071 | -0.018311 | 0.19226 | 0.28381 | 0.10986 | 0.064087 | 0.050354 | 0.041199 | -0.018311 | 60.8734 | 60.7544 | -61.6013 | 60.9146 | 60.8734 | 0.11902 | -61.5463 | 60.8139 | 60.7544 | -61.6425 | 60.965 | 60.8826 | 0.12817 | -61.6562 | 60.878 | 60.9329 | 60.9283 | -61.7249 | 60.8368 | 60.8231 | 61.0565 | -61.7249
99.5156 | 122.7814 | -60.791 | 61.7798 | 0.045166 | 0.0075835 | 0.0035888 | 0.0010595 | -0.0049796 | -0.0037662 | -0.0043793 | 0.079117 | -0.0070003 | -0.003262 | -0.00048061 | 0.0015445 | -0.0061032 | 0.054932 | 0.013733 | 0.036621 | 0.018311 | 0.050354 | 0.045776 | -0.073242 | 0.10529 | 0.13275 | 0.009155 | 0.045776 | 0.032043 | 0.009155 | -0.027466 | 60.8368 | 60.7178 | -61.7294 | 60.8047 | 60.8093 | 0.091553 | -61.7249 | 60.8002 | 60.7636 | -61.734 | 60.8963 | 60.8002 | 0.036621 | -61.7477 | 60.8414 | 60.8459 | 60.8276 | -61.853 | 60.8368 | 60.8231 | 60.9238 | -61.8073
101.1719 | 122.7905 | -60.8047 | 61.7935 | 0.13672 | 0.011215 | 0.0027344 | -0.0012903 | -0.0026296 | 0.0024288 | -0.0024567 | 0.13252 | -0.0050777 | -0.00668 | -0.00069421 | 0.0062441 | -0.0048214 | -0.018311 | -0.09613 | -0.086975 | -0.086975 | 0.018311 | -0.022888 | -0.17395 | 0.013733 | -0.10071 | -0.1236 | 0.004578 | -0.013733 | -0.054932 | -0.11902 | 60.7819 | 60.6308 | -61.7752 | 60.7086 | 60.7178 | 0.086975 | -61.8118 | 60.7498 | 60.6857 | -61.7889 | 60.8185 | 60.6812 | -0.004577 | -61.8073 | 60.8231 | 60.7864 | 60.7178 | -61.9675 | 60.8093 | 60.791 | 60.704 | -61.9125
102.8438 | 122.8638 | -60.7681 | 61.7752 | -0.23712 | 0.011215 | 0.0033752 | 0.0038367 | -0.0039114 | -0.00098918 | -0.0026703 | -0.24132 | -0.0059323 | -0.0030484 | 0.001442 | 0.0017581 | -0.0033262 | 0.086975 | 0.032043 | 0.050354 | 0.045776 | 0.18768 | 0.082397 | -0.041199 | 0.064087 | 0.086975 | -0.059509 | 0.10529 | 0.10071 | 0.018311 | -0.041199 | 60.8505 | 60.7269 | -61.5875 | 60.8002 | 60.8139 | 0.086975 | -61.6882 | 60.7864 | 60.7269 | -61.6699 | 60.8322 | 60.7086 | -0.01831 | -61.6745 | 60.9558 | 60.8551 | 60.8185 | -61.8164 | 60.8734 | 60.8688 | 60.8551 | -61.8164
104.5156 | 122.7402 | -60.8322 | 61.7889 | 0.19012 | 0.011429 | 0.0010254 | 0.00084592 | -0.00070705 | 7.902e-05 | -0.0018159 | 0.1783 | -0.0063595 | -0.0053982 | -0.00026701 | 0.0019717 | -0.0052488 | 0.022888 | 0.009155 | 0.027466 | -0.022888 | -0.068665 | -0.022888 | -0.15106 | 0.082397 | 0.073242 | -0.022888 | -0.032043 | -0.041199 | -0.059509 | -0.10986 | 60.8093 | 60.6812 | -61.8576 | 60.8414 | 60.8093 | 0.12817 | -61.7661 | 60.7727 | 60.7224 | -61.821 | 60.9146 | 60.8093 | 0.086975 | -61.8301 | 60.7635 | 60.8551 | 60.8597 | -61.94 | 60.8002 | 60.791 | 60.9055 | -61.8988
106.1875 | 122.7448 | -60.8368 | 61.8073 | 0.068054 | 0.011215 | 0.0031616 | 0.0023413 | -0.0034842 | 0.001788 | 0.0011749 | 0.0028229 | -0.0052915 | -0.0026212 | 0.00080099 | 0.0032535 | -0.007385 | -0.036621 | -0.10529 | -0.086975 | -0.07782 | 0.050354 | -0.032043 | -0.15564 | -0.036621 | -0.13275 | -0.16022 | 0.027466 | 0.004578 | -0.07782 | -0.11902 | 60.8047 | 60.6812 | -61.7569 | 60.7315 | 60.759 | 0.07782 | -61.8439 | 60.759 | 60.7178 | -61.7798 | 60.8002 | 60.6766 | -0.041198 | -61.8027 | 60.8871 | 60.8002 | 60.7498 | -61.9629 | 60.8643 | 60.8414 | 60.704 | -61.9263
107.8438 | 122.7127 | -60.8093 | 61.7798 | 0.1825 | 0.010788 | 0.0010254 | -8.476e-06 | -0.0011342 | -0.0029118 | -0.0026703 | 0.17067 | -0.0099911 | -0.004971 | -0.0026168 | 0.0023989 | -0.0061032 | 0.027466 | 0.013733 | 0.064087 | -0.022888 | -0.050354 | -0.013733 | -0.15106 | 0.09613 | 0.082397 | -0.004578 | -0.032043 | -0.064087 | -0.041199 | -0.091553 | 60.7956 | 60.6583 | -61.8301 | 60.8231 | 60.7864 | 0.12817 | -61.7523 | 60.7681 | 60.7178 | -61.8118 | 60.9055 | 60.8047 | 0.086975 | -61.8439 | 60.759 | 60.8368 | 60.8734 | -61.9308 | 60.7773 | 60.7452 | 60.8917 | -61.8713
109.5156 | 122.8363 | -60.7498 | 61.7706 | -0.19897 | 0.014847 | 0.0057252 | 0.0066137 | -0.004125 | -0.003339 | -0.0026703 | -0.22606 | -0.0037961 | -0.0030484 | 0.0016556 | 0.00047633 | -0.0058896 | 0.082397 | 0.036621 | 0.041199 | 0.032043 | 0.14648 | 0.091553 | -0.050354 | 0.068665 | 0.13733 | -0.027466 | 0.1236 | 0.10071 | 0.032043 | -0.027466 | 60.8414 | 60.6995 | -61.6241 | 60.7864 | 60.7819 | 0.082397 | -61.6882 | 60.7819 | 60.7224 | -61.647 | 60.8185 | 60.7224 | 0 | -61.6699 | 60.8963 | 60.8322 | 60.791 | -61.821 | 60.8734 | 60.8505 | 60.8871 | -61.7981
111.1875 | 122.818 | -60.7819 | 61.7661 | -0.16083 | 0.012711 | 0.0020936 | 0.0061865 | -0.0022024 | -0.0020572 | -0.0039521 | -0.18791 | -0.0059323 | -0.00048483 | 0.0010148 | -0.0010191 | -0.005035 | 0.14191 | 0.13275 | 0.15106 | 0.09613 | 0.11444 | 0.11902 | -0.045776 | 0.14648 | 0.26093 | 0.064087 | 0.082397 | 0.086975 | 0.041199 | -0.009155 | 60.9009 | 60.7361 | -61.6516 | 60.9146 | 60.878 | 0.14191 | -61.6241 | 60.8231 | 60.7727 | -61.6837 | 60.9283 | 60.8459 | 0.073242 | -61.6791 | 60.8963 | 60.9238 | 60.9329 | -61.8118 | 60.8643 | 60.8688 | 61.0428 | -61.7752
112.8594 | 122.8317 | -60.7498 | 61.7752 | -0.2066 | 0.012924 | 0.0035888 | 0.0053321 | -0.0032706 | -0.00163 | -0.0033111 | -0.23369 | -0.0042233 | -0.0019802 | -0.00026701 | 0.00090353 | -0.0065304 | 0.082397 | 0.050354 | 0.054932 | 0.045776 | 0.15564 | 0.073242 | -0.045776 | 0.082397 | 0.13733 | -0.022888 | 0.13275 | 0.11444 | 0.009155 | -0.027466 | 60.8231 | 60.704 | -61.6196 | 60.8002 | 60.7956 | 0.091552 | -61.6928 | 60.759 | 60.7224 | -61.6425 | 60.8322 | 60.7269 | 0.004578 | -61.6608 | 60.9055 | 60.8322 | 60.8047 | -61.821 | 60.8826 | 60.8643 | 60.8871 | -61.8027
114.5312 | 122.7631 | -60.8093 | 61.7706 | 0.13672 | 0.010574 | 0.0020936 | -8.476e-06 | -0.0043386 | 0.0013608 | -0.0020295 | 0.1783 | -0.0076413 | -0.003262 | -0.00069421 | 0.0043215 | -0.005035 | 0.022888 | 0.013733 | 0.004578 | -0.013733 | -0.022888 | -0.009155 | -0.14191 | 0.091553 | 0.050354 | -0.036621 | -0.059509 | -0.068665 | -0.064087 | -0.10986 | 60.8002 | 60.6674 | -61.7935 | 60.8231 | 60.7956 | 0.12817 | -61.7477 | 60.7452 | 60.6995 | -61.8301 | 60.9009 | 60.7727 | 0.073242 | -61.8393 | 60.7864 | 60.8322 | 60.8139 | -61.9125 | 60.7498 | 60.7407 | 60.8597 | -61.8805
116.2031 | 122.7768 | -60.7773 | 61.7798 | 0.1825 | 0.0097199 | 0.0038024 | -0.0015039 | -0.0032706 | 0.00029262 | -0.00053407 | 0.10963 | -0.0031551 | -0.0056118 | -0.0015488 | 0.0045351 | -0.003967 | -0.004578 | -0.032043 | -0.018311 | -0.050354 | 0 | -0.032043 | -0.16022 | 0.086975 | 0.013733 | -0.045776 | -0.022888 | -0.036621 | -0.036621 | -0.086975 | 60.7452 | 60.6171 | -61.7798 | 60.7452 | 60.7269 | 0.10986 | -61.7844 | 60.7407 | 60.6903 | -61.8027 | 60.8643 | 60.7315 | 0.041199 | -61.8164 | 60.7773 | 60.7727 | 60.759 | -61.94 | 60.7544 | 60.7407 | 60.791 | -61.8668
117.875 | 122.8592 | -60.791 | 61.7523 | -0.24475 | 0.011856 | 0.0033752 | 0.0066137 | -0.0028432 | -0.0014164 | -0.0028839 | -0.24895 | -0.0046505 | -0.0026212 | 0.00037379 | 0.00090353 | -0.0043942 | 0.068665 | 0.045776 | 0.045776 | 0.054932 | 0.1831 | 0.091553 | -0.064087 | 0.073242 | 0.10529 | -0.050354 | 0.1236 | 0.082397 | 0.022888 | -0.045776 | 60.8826 | 60.7269 | -61.5692 | 60.8368 | 60.8459 | 0.11902 | -61.6837 | 60.8139 | 60.7452 | -61.6287 | 60.8643 | 60.7407 | -0.004578 | -61.6699 | 60.9741 | 60.8597 | 60.8368 | -61.8164 | 60.9146 | 60.8734 | 60.8963 | -61.7981
119.5938 | 122.8455 | -60.7636 | 61.7477 | 0.0070193 | 0.011002 | 0.0033752 | 0.0031957 | -0.0047658 | -0.0037662 | -0.0043793 | 0.018082 | -0.0074277 | -0.0036892 | -0.00048061 | 0.00090353 | -0.0043942 | 0.064087 | 0.068665 | 0.068665 | 0.045776 | 0.068665 | 0.054932 | -0.064087 | 0.14191 | 0.21057 | 0.059509 | 0.045776 | 0.032043 | 0.018311 | -0.018311 | 60.8185 | 60.6995 | -61.6791 | 60.8322 | 60.8093 | 0.10986 | -61.6837 | 60.7819 | 60.7452 | -61.702 | 60.9055 | 60.8231 | 0.07782 | -61.7157 | 60.8322 | 60.8276 | 60.8322 | -61.8118 | 60.8093 | 60.7956 | 60.9741 | -61.7661
121.25 | 122.7585 | -60.7956 | 61.7981 | 0.11383 | 0.012711 | 0.0035888 | 0.00041872 | -0.0034842 | 0.003497 | -0.0011749 | 0.102 | -0.0029415 | -0.0051846 | 0.0016556 | 0.0049625 | -0.0061032 | -0.027466 | -0.12817 | -0.10529 | -0.091553 | 0.036621 | -0.032043 | -0.16022 | -0.018311 | -0.14648 | -0.16479 | 0.041199 | -0.013733 | -0.068665 | -0.14191 | 60.7635 | 60.6354 | -61.7615 | 60.6674 | 60.704 | 0.068664 | -61.8256 | 60.7269 | 60.6537 | -61.7569 | 60.7773 | 60.6308 | -0.022888 | -61.8118 | 60.8322 | 60.7681 | 60.6903 | -61.9583 | 60.8368 | 60.7819 | 60.6491 | -61.94
122.9844 | 122.7127 | -60.8047 | 61.7981 | 0.15198 | 0.011643 | 0.0018798 | 0.0014867 | -0.00049345 | -0.0031254 | -0.00096127 | 0.14778 | -0.0074277 | -0.0028348 | -0.00090781 | 0.00026273 | -0.0054624 | 0.045776 | 0.032043 | 0.050354 | -0.018311 | -0.013733 | -0.004578 | -0.12817 | 0.10071 | 0.082397 | -0.013733 | -0.018311 | -0.022888 | -0.045776 | -0.091553 | 60.8002 | 60.6766 | -61.8118 | 60.8368 | 60.7864 | 0.10986 | -61.7523 | 60.759 | 60.7132 | -61.8164 | 60.9055 | 60.791 | 0.07782 | -61.821 | 60.791 | 60.8505 | 60.8551 | -61.9263 | 60.7864 | 60.7819 | 60.8871 | -61.8896
124.6562 | 122.8867 | -60.7773 | 61.7615 | -0.19135 | 0.011643 | 0.0033752 | 0.0057593 | -0.00027985 | -0.00098918 | -0.0011749 | -0.20317 | -0.0042233 | -0.0034756 | 0.0022964 | 0.0015445 | -0.006744 | 0.07782 | 0.018311 | 0.027466 | 0.041199 | 0.15564 | 0.073242 | -0.059509 | 0.045776 | 0.082397 | -0.064087 | 0.091553 | 0.091553 | -0.009155 | -0.050354 | 60.8505 | 60.7178 | -61.6058 | 60.7956 | 60.8185 | 0.10071 | -61.6837 | 60.7681 | 60.7269 | -61.6699 | 60.8231 | 60.7132 | -0.013733 | -61.6699 | 60.9329 | 60.8551 | 60.8047 | -61.821 | 60.8688 | 60.8688 | 60.8597 | -61.8118
126.3438 | 122.7448 | -60.8414 | 61.7752 | 0.098572 | 0.0088653 | 0.0016662 | 0.0021277 | -0.0047658 | -0.0039798 | -0.0022431 | 0.11726 | -0.0055051 | -0.0036892 | 0.001442 | 0.0019717 | -0.0058896 | 0.032043 | 0.032043 | 0.059509 | -0.004578 | 0.013733 | 0.022888 | -0.10529 | 0.09613 | 0.1236 | -0.009155 | 0.032043 | 0.013733 | -0.009155 | -0.050354 | 60.8643 | 60.7361 | -61.7615 | 60.8734 | 60.8368 | 0.10071 | -61.7432 | 60.8322 | 60.791 | -61.7432 | 60.9375 | 60.8322 | 0.041199 | -61.7615 | 60.8551 | 60.8734 | 60.9009 | -61.8805 | 60.8734 | 60.8551 | 60.965 | -61.8256
128.0156 | 122.8226 | -60.7819 | 61.7706 | -0.24475 | 0.012924 | 0.0025208 | 0.0042639 | -0.0028432 | -0.0024844 | -0.0013885 | -0.22606 | -0.0061459 | -0.0028348 | 0.00058739 | 0.0015445 | -0.005676 | 0.12817 | 0.13275 | 0.12817 | 0.09613 | 0.1236 | 0.10529 | -0.036621 | 0.10529 | 0.1831 | 0.004578 | 0.10529 | 0.07782 | 0.022888 | -0.022888 | 60.8871 | 60.7452 | -61.647 | 60.9146 | 60.878 | 0.13275 | -61.6425 | 60.8047 | 60.759 | -61.6653 | 60.8871 | 60.7864 | 0.027466 | -61.6928 | 60.9055 | 60.91 | 60.91 | -61.8073 | 60.8871 | 60.8597 | 60.965 | -61.7935
129.6719 | 122.731 | -60.8047 | 61.7661 | 0.12146 | 0.0073699 | 0.0040162 | 0.0029821 | -0.0032706 | -0.003339 | -0.0041657 | 0.14015 | -0.0067867 | -0.003262 | -0.00026701 | 0.0021853 | -0.0063168 | 0.022888 | 0.041199 | 0.041199 | -0.022888 | 0 | 0 | -0.12817 | 0.10529 | 0.10071 | -0.004578 | 0 | 0 | -0.013733 | -0.068665 | 60.8047 | 60.6766 | -61.7661 | 60.8459 | 60.7819 | 0.10529 | -61.7432 | 60.791 | 60.7361 | -61.7661 | 60.91 | 60.8002 | 0.064087 | -61.7661 | 60.8047 | 60.8276 | 60.8459 | -61.8942 | 60.8047 | 60.8047 | 60.9055 | -61.8347
131.3438 | 122.7631 | -60.8002 | 61.7615 | 0.052795 | 0.0095063 | 0.0044434 | 0.0021277 | -0.0015616 | -0.0035526 | -0.0037385 | 0.056228 | -0.0070003 | -0.0051846 | -0.00048061 | -0.00037807 | -0.0048214 | 0.036621 | 0.041199 | 0.054932 | 0.027466 | 0.036621 | 0.045776 | -0.073242 | 0.091553 | 0.1236 | -0.013733 | 0.059509 | 0.022888 | 0.013733 | -0.054932 | 60.8459 | 60.7269 | -61.7249 | 60.8414 | 60.8276 | 0.10071 | -61.7249 | 60.8139 | 60.7452 | -61.702 | 60.8917 | 60.7864 | 0.041199 | -61.7386 | 60.8368 | 60.8368 | 60.8551 | -61.8347 | 60.8597 | 60.8231 | 60.9238 | -61.8164
133.0312 | 122.8592 | -60.7636 | 61.7706 | -0.099793 | 0.013992 | 0.0023072 | 0.0042639 | -0.0026296 | 0.0043514 | -0.00096127 | -0.20317 | -0.0042233 | -0.0034756 | 0.0018692 | 0.0049625 | -0.007385 | 0.082397 | 0.013733 | 0.027466 | 0.027466 | 0.09613 | 0.036621 | -0.091553 | 0.064087 | 0.050354 | -0.054932 | 0.045776 | 0.022888 | -0.027466 | -0.086975 | 60.8002 | 60.672 | -61.6745 | 60.7773 | 60.791 | 0.11902 | -61.6882 | 60.7361 | 60.6766 | -61.7249 | 60.8276 | 60.7086 | 0.032043 | -61.7477 | 60.8597 | 60.8459 | 60.791 | -61.8622 | 60.8093 | 60.7864 | 60.8139 | -61.8576
134.6875 | 122.8455 | -60.7773 | 61.7615 | 0.014648 | 0.0090789 | 0.0020936 | 0.0044775 | -0.0028432 | -0.0041934 | -0.0022431 | 0.018082 | -0.0089229 | -0.0034756 | 0.0016556 | -0.00059167 | -0.0065304 | 0.054932 | 0.045776 | 0.07782 | 0.032043 | 0.050354 | 0.059509 | -0.086975 | 0.1236 | 0.18768 | 0.041199 | 0.054932 | 0.022888 | 0.013733 | -0.032043 | 60.8368 | 60.6903 | -61.7111 | 60.8231 | 60.8093 | 0.11902 | -61.7065 | 60.791 | 60.7452 | -61.7065 | 60.9009 | 60.8185 | 0.073242 | -61.7386 | 60.8276 | 60.8322 | 60.8551 | -61.8484 | 60.8322 | 60.8002 | 60.965 | -61.7935
136.375 | 122.7493 | -60.8276 | 61.7706 | 0.060425 | 0.0077973 | 0.0042298 | 0.0014867 | -0.0022024 | -0.0014164 | -0.0028839 | 0.079117 | -0.0070003 | -0.0062528 | -0.0017624 | 4.9132e-05 | -0.0052488 | 0.041199 | 0.041199 | 0.054932 | 0.009155 | 0.050354 | 0.027466 | -0.073242 | 0.10071 | 0.1236 | -0.004578 | 0.050354 | 0.009155 | 0 | -0.054932 | 60.8551 | 60.7544 | -61.7203 | 60.8688 | 60.8368 | 0.082397 | -61.7294 | 60.8276 | 60.7727 | -61.7203 | 60.9283 | 60.8231 | 0.050354 | -61.7615 | 60.878 | 60.8688 | 60.8826 | -61.8439 | 60.878 | 60.8368 | 60.9512 | -61.8256
138.0312 | 122.7402 | -60.8231 | 61.8164 | 0.090942 | 0.013138 | 0.0023072 | -0.00022208 | -0.0019888 | 0.004565 | -0.00074767 | -0.065842 | -0.0046505 | -0.0036892 | 0.00058739 | 0.0062441 | -0.006744 | -0.050354 | -0.10071 | -0.086975 | -0.073242 | 0.059509 | -0.032043 | -0.16937 | -0.032043 | -0.11902 | -0.17395 | 0.036621 | 0.013733 | -0.059509 | -0.13275 | 60.791 | 60.6537 | -61.7569 | 60.7224 | 60.7498 | 0.096131 | -61.8668 | 60.7636 | 60.6903 | -61.7798 | 60.791 | 60.6491 | -0.041199 | -61.8027 | 60.8826 | 60.7727 | 60.7361 | -61.9858 | 60.8597 | 60.8368 | 60.704 | -61.9492
139.7031 | 122.85 | -60.7681 | 61.7661 | 0.0070193 | 0.010788 | 0.0050842 | 0.0034093 | -0.0043386 | -0.0052616 | -0.0035249 | 0.025711 | -0.0074277 | -0.0026212 | 0.00016019 | -0.00016447 | -0.0063168 | 0.036621 | 0.050354 | 0.068665 | 0.027466 | 0.073242 | 0.045776 | -0.09613 | 0.12817 | 0.19226 | 0.027466 | 0.050354 | 0.036621 | 0.022888 | -0.050354 | 60.8139 | 60.672 | -61.6928 | 60.8185 | 60.7956 | 0.1236 | -61.7294 | 60.791 | 60.7178 | -61.7157 | 60.8963 | 60.7956 | 0.07782 | -61.7294 | 60.8414 | 60.8047 | 60.8368 | -61.8622 | 60.8185 | 60.8047 | 60.9604 | -61.8164
141.375 | 122.8592 | -60.7681 | 61.7889 | -0.18372 | 0.013138 | 0.0033752 | 0.0019141 | -0.0022024 | 0.0024288 | -0.0030975 | -0.24132 | -0.0059323 | -0.0043302 | 0.00251 | 0.0032535 | -0.007385 | 0.091553 | 0.041199 | 0.022888 | 0.045776 | 0.15106 | 0.073242 | -0.045776 | 0.050354 | 0.050354 | -0.068665 | 0.10071 | 0.045776 | -0.009155 | -0.082397 | 60.8414 | 60.7224 | -61.6379 | 60.8093 | 60.8139 | 0.091552 | -61.6974 | 60.759 | 60.6857 | -61.6882 | 60.8185 | 60.6995 | 0.013732 | -61.7432 | 60.9192 | 60.8597 | 60.791 | -61.8347 | 60.8688 | 60.8139 | 60.8185 | -61.8713
143.0469 | 122.7448 | -60.8139 | 61.7615 | 0.19012 | 0.013138 | 0.0023072 | 0.0025549 | -0.0054068 | -0.00163 | 0.00032053 | 0.20119 | -0.0067867 | -0.0028348 | -0.0015488 | 0.0028263 | -0.0048214 | 0.018311 | 0 | 0.032043 | -0.013733 | -0.036621 | -0.036621 | -0.15106 | 0.086975 | 0.054932 | -0.032043 | -0.050354 | -0.064087 | -0.054932 | -0.1236 | 60.7773 | 60.6628 | -61.7981 | 60.8139 | 60.8002 | 0.13733 | -61.7432 | 60.759 | 60.6903 | -61.8118 | 60.9009 | 60.7819 | 0.091553 | -61.8256 | 60.7773 | 60.8322 | 60.8459 | -61.9125 | 60.7636 | 60.7498 | 60.8688 | -61.8851
144.7188 | 122.8271 | -60.7773 | 61.7889 | -0.25238 | 0.011643 | 0.00038459 | 0.0044775 | -0.0028432 | -0.00034818 | -0.0013885 | -0.23369 | -0.0050777 | -0.0051846 | 0.0022964 | 0.0021853 | -0.0078122 | 0.1236 | 0.11444 | 0.11444 | 0.091553 | 0.13733 | 0.11444 | -0.022888 | 0.10529 | 0.16937 | -0.013733 | 0.12817 | 0.10986 | 0.022888 | -0.018311 | 60.8917 | 60.7544 | -61.6516 | 60.8917 | 60.8688 | 0.11444 | -61.6653 | 60.8002 | 60.759 | -61.6608 | 60.8826 | 60.7635 | 0.004578 | -61.6791 | 60.9146 | 60.9009 | 60.8917 | -61.8118 | 60.9055 | 60.8871 | 60.9467 | -61.8073
146.3906 | 122.8043 | -60.7498 | 61.7798 | -0.099793 | 0.013352 | 0.0020936 | 0.0010595 | -0.0028432 | 0.003497 | -0.0028839 | -0.14214 | -0.0033687 | -0.0056118 | 0.0012284 | 0.0034671 | -0.0082394 | 0.07782 | 0.036621 | 0.013733 | -0.004578 | 0.068665 | 0.027466 | -0.13275 | 0.068665 | 0.022888 | -0.059509 | 0.045776 | 0.032043 | -0.045776 | -0.10986 | 60.7773 | 60.6171 | -61.7111 | 60.7864 | 60.7452 | 0.12817 | -61.702 | 60.704 | 60.64 | -61.734 | 60.8185 | 60.6903 | 0.050354 | -61.7477 | 60.8185 | 60.8276 | 60.7636 | -61.9125 | 60.7956 | 60.7819 | 60.7727 | -61.8896
148.0625 | 122.7676 | -60.791 | 61.7844 | 0.12909 | 0.011643 | 0.0018798 | 0.0025549 | -0.0051932 | -0.002698 | -0.0020295 | 0.21645 | -0.0050777 | -0.0045438 | -0.00048061 | 0.0023989 | -0.0065304 | 0 | 0.013733 | 0.027466 | -0.013733 | -0.018311 | -0.032043 | -0.15564 | 0.091553 | 0.041199 | -0.027466 | -0.032043 | -0.068665 | -0.050354 | -0.09613 | 60.759 | 60.6354 | -61.8027 | 60.8047 | 60.7773 | 0.14191 | -61.7844 | 60.7407 | 60.6949 | -61.8164 | 60.8826 | 60.7636 | 0.068664 | -61.853 | 60.7727 | 60.791 | 60.8185 | -61.94 | 60.759 | 60.7224 | 60.8322 | -61.8805
149.7344 | 122.8683 | -60.7544 | 61.7432 | -0.015869 | 0.014633 | 0.0035888 | 0.0068273 | -0.0039114 | -0.005048 | -0.0035249 | -0.012436 | -0.0065731 | -0.0047574 | -0.0011216 | -0.00016447 | -0.0063168 | 0.054932 | 0.07782 | 0.086975 | 0.050354 | 0.07782 | 0.064087 | -0.073242 | 0.13733 | 0.23804 | 0.073242 | 0.054932 | 0.041199 | 0.027466 | -0.022888 | 60.8185 | 60.6812 | -61.6653 | 60.8322 | 60.8047 | 0.1236 | -61.6882 | 60.7819 | 60.7315 | -61.6882 | 60.8917 | 60.8276 | 0.09613 | -61.702 | 60.8322 | 60.8093 | 60.8414 | -61.8164 | 60.8093 | 60.7956 | 60.9924 | -61.7661
151.4531 | 122.8134 | -60.7636 | 61.7432 | -0.19897 | 0.013779 | 0.0044434 | 0.0051183 | -0.0017752 | -0.0014164 | -0.0024567 | -0.18791 | -0.0048641 | -0.0017666 | -0.0013352 | -0.0010191 | -0.0065304 | 0.14648 | 0.14191 | 0.12817 | 0.10529 | 0.12817 | 0.10071 | -0.036621 | 0.10529 | 0.21515 | 0.018311 | 0.10529 | 0.086975 | 0.027466 | -0.009155 | 60.8643 | 60.7269 | -61.615 | 60.9055 | 60.8688 | 0.14191 | -61.5967 | 60.791 | 60.7544 | -61.6379 | 60.8688 | 60.7819 | 0.027466 | -61.6562 | 60.8917 | 60.91 | 60.8917 | -61.7798 | 60.8688 | 60.8505 | 60.9787 | -61.7523
153.125 | 122.8271 | -60.7773 | 61.7615 | -0.061646 | 0.012711 | 0.00059819 | 0.00084592 | 0.00057455 | 0.0030698 | -0.00053407 | -0.14214 | -0.0059323 | -0.0064664 | 0.0022964 | 0.0045351 | -0.007385 | 0.082397 | 0.036621 | 0.027466 | 0.009155 | 0.07782 | 0.018311 | -0.11444 | 0.054932 | 0.018311 | -0.064087 | 0.022888 | 0.022888 | -0.045776 | -0.086975 | 60.7956 | 60.6628 | -61.6837 | 60.8139 | 60.7864 | 0.1236 | -61.6791 | 60.7315 | 60.6903 | -61.7386 | 60.8322 | 60.7132 | 0.022888 | -61.7386 | 60.8551 | 60.8597 | 60.8047 | -61.8759 | 60.8002 | 60.8002 | 60.7956 | -61.8484
154.8281 | 122.7722 | -60.7956 | 61.7706 | 0.16724 | 0.012711 | 0.0042298 | 0.0019141 | -0.0064748 | 0.00029262 | -0.0013885 | 0.16304 | -0.0052915 | -0.0036892 | -0.0034714 | 0.0021853 | -0.0061032 | 0.027466 | 0.009155 | 0.013733 | -0.013733 | -0.013733 | -0.013733 | -0.16022 | 0.09613 | 0.036621 | -0.036621 | -0.009155 | -0.064087 | -0.041199 | -0.10071 | 60.7819 | 60.6354 | -61.7844 | 60.8047 | 60.7819 | 0.14648 | -61.7432 | 60.7544 | 60.6949 | -61.7798 | 60.8917 | 60.759 | 0.064087 | -61.8347 | 60.7819 | 60.8231 | 60.8093 | -61.9308 | 60.7864 | 60.7315 | 60.8322 | -61.8713
156.5 | 122.8409 | -60.7819 | 61.7523 | -0.0082397 | 0.012711 | 0.004657 | 0.0046911 | -0.0022024 | -0.003339 | -0.0060883 | 0.03334 | -0.0044369 | -0.003262 | 0.00037379 | -0.00016447 | -0.0063168 | 0.041199 | 0.073242 | 0.086975 | 0.032043 | 0.07782 | 0.045776 | -0.073242 | 0.14191 | 0.20142 | 0.054932 | 0.036621 | 0.041199 | 0.004578 | -0.041199 | 60.8276 | 60.7086 | -61.6745 | 60.8551 | 60.8139 | 0.10529 | -61.7111 | 60.7864 | 60.7407 | -61.7157 | 60.9238 | 60.8368 | 0.096131 | -61.7111 | 60.8597 | 60.8231 | 60.8688 | -61.8256 | 60.8185 | 60.8231 | 60.9833 | -61.7935
158.1719 | 122.7859 | -60.7819 | 61.7889 | 0.19775 | 0.010361 | 0.00059819 | 0.0019141 | -0.0034842 | 0.0015744 | -0.0045929 | 0.12489 | -0.0046505 | -0.004971 | 0.00058739 | 0.0056033 | -0.0075986 | -0.018311 | -0.045776 | -0.041199 | -0.059509 | -0.009155 | -0.022888 | -0.16022 | 0.07782 | 0 | -0.045776 | -0.022888 | -0.045776 | -0.032043 | -0.10986 | 60.759 | 60.6216 | -61.7981 | 60.7361 | 60.7224 | 0.10071 | -61.8073 | 60.7498 | 60.672 | -61.8118 | 60.8597 | 60.7361 | 0.064087 | -61.8347 | 60.7727 | 60.7635 | 60.7407 | -61.9492 | 60.759 | 60.7361 | 60.7819 | -61.8988
159.8438 | 122.8455 | -60.7498 | 61.7477 | -0.23712 | 0.01442 | 0.0027344 | 0.0051183 | -0.0028432 | -0.00163 | -0.0033111 | -0.21843 | -0.0052915 | -0.00069863 | -0.00026701 | 0.00047633 | -0.0063168 | 0.07782 | 0.050354 | 0.059509 | 0.045776 | 0.16937 | 0.082397 | -0.054932 | 0.064087 | 0.11444 | -0.036621 | 0.13275 | 0.10071 | 0.004578 | -0.036621 | 60.8322 | 60.6949 | -61.5784 | 60.8002 | 60.7956 | 0.10071 | -61.6699 | 60.7544 | 60.7132 | -61.615 | 60.8139 | 60.7132 | 0 | -61.647 | 60.9192 | 60.8276 | 60.8093 | -61.8027 | 60.8826 | 60.8505 | 60.8643 | -61.7844
161.5156 | 122.7356 | -60.8139 | 61.8118 | 0.15198 | 0.011856 | 0.0016662 | 0.00063232 | -0.0036978 | -0.0029118 | -0.0033111 | 0.14015 | -0.0084957 | -0.0051846 | 0.00016019 | 0.0013309 | -0.0048214 | 0.036621 | 0.027466 | 0.068665 | -0.009155 | -0.018311 | -0.018311 | -0.14191 | 0.09613 | 0.07782 | -0.013733 | -0.018311 | -0.022888 | -0.036621 | -0.086975 | 60.7956 | 60.672 | -61.8301 | 60.8414 | 60.8047 | 0.13275 | -61.7752 | 60.7773 | 60.7269 | -61.8301 | 60.91 | 60.8002 | 0.073242 | -61.8347 | 60.7956 | 60.8505 | 60.8826 | -61.9537 | 60.7956 | 60.791 | 60.8917 | -61.8988
163.1875 | 122.8271 | -60.7681 | 61.7844 | -0.22949 | 0.012711 | 0.0018798 | 0.0064001 | -0.0022024 | -0.0022708 | -0.0045929 | -0.20317 | -0.0033687 | -0.0045438 | 0.0029374 | 4.9132e-05 | -0.0075986 | 0.13733 | 0.13275 | 0.14648 | 0.10529 | 0.14648 | 0.091553 | -0.027466 | 0.1236 | 0.19684 | 0.013733 | 0.10071 | 0.091553 | 0.027466 | -0.018311 | 60.8597 | 60.7407 | -61.6379 | 60.9009 | 60.8734 | 0.13275 | -61.647 | 60.7956 | 60.7498 | -61.6837 | 60.8917 | 60.7819 | 0.032044 | -61.6928 | 60.9146 | 60.9055 | 60.9146 | -61.8118 | 60.8688 | 60.8597 | 60.965 | -61.8027
164.8594 | 122.7402 | -60.8139 | 61.8164 | -0.031128 | 0.012711 | 0.0033752 | 0.00084592 | -0.0015616 | 0.0032834 | -0.0033111 | -0.065842 | -0.0046505 | -0.0058254 | -0.00026701 | 0.0053897 | -0.006744 | 0.032043 | -0.013733 | -0.032043 | -0.032043 | 0.068665 | 0 | -0.11902 | 0 | -0.082397 | -0.14648 | 0.032043 | -0.004578 | -0.064087 | -0.13275 | 60.8139 | 60.6949 | -61.7477 | 60.8002 | 60.7819 | 0.086976 | -61.7844 | 60.7498 | 60.6812 | -61.7844 | 60.8139 | 60.6674 | -0.013733 | -61.821 | 60.8826 | 60.8459 | 60.7819 | -61.9354 | 60.8459 | 60.8093 | 60.7315 | -61.9492
166.5312 | 122.8683 | -60.7498 | 61.734 | -0.031128 | 0.010574 | 0.0023072 | 0.0070409 | -0.002416 | -0.0052616 | -0.0045929 | -0.020065 | -0.0050777 | -0.0026212 | 0.00037379 | -0.0033689 | -0.005035 | 0.064087 | 0.086975 | 0.09613 | 0.054932 | 0.07782 | 0.054932 | -0.073242 | 0.15106 | 0.21973 | 0.07782 | 0.059509 | 0.032043 | 0.018311 | -0.027466 | 60.8047 | 60.6766 | -61.6562 | 60.8368 | 60.8047 | 0.12817 | -61.6699 | 60.7681 | 60.7224 | -61.6745 | 60.9009 | 60.8276 | 0.10529 | -61.702 | 60.8276 | 60.8139 | 60.8459 | -61.8073 | 60.8093 | 60.7819 | 60.9695 | -61.7615
168.2031 | 122.7631 | -60.8047 | 61.8073 | 0.098572 | 0.012497 | 0.0014526 | 0.0017005 | -0.0045522 | 0.0037106 | -0.0013885 | 0.102 | -0.0040097 | -0.0058254 | -0.0015488 | 0.0051761 | -0.0058896 | -0.045776 | -0.1236 | -0.11444 | -0.10071 | 0.027466 | -0.045776 | -0.1831 | -0.018311 | -0.15106 | -0.16022 | 0.018311 | 0.009155 | -0.07782 | -0.14191 | 60.759 | 60.6216 | -61.7798 | 60.6812 | 60.704 | 0.082397 | -61.853 | 60.7269 | 60.6628 | -61.7889 | 60.7864 | 60.6445 | -0.01831 | -61.7981 | 60.8322 | 60.759 | 60.6903 | -61.9904 | 60.8231 | 60.8139 | 60.6537 | -61.9492
169.8594 | 122.8363 | -60.7452 | 61.7569 | -0.18372 | 0.014206 | 0.0048706 | 0.0061865 | -0.002416 | -0.00034818 | -0.0033111 | -0.24895 | -0.0052915 | -0.0019802 | -0.0041122 | 4.9132e-05 | -0.0018308 | 0.068665 | 0.045776 | 0.059509 | 0.036621 | 0.16022 | 0.086975 | -0.027466 | 0.07782 | 0.10529 | -0.050354 | 0.11902 | 0.091553 | 0 | -0.059509 | 60.8322 | 60.7178 | -61.5967 | 60.791 | 60.7819 | 0.064087 | -61.6882 | 60.7452 | 60.6857 | -61.6379 | 60.8231 | 60.6949 | 0.009155 | -61.6653 | 60.9055 | 60.8139 | 60.8047 | -61.7844 | 60.8643 | 60.8368 | 60.8505 | -61.8164
171.5156 | 122.7356 | -60.7773 | 61.8073 | -0.038757 | 0.014206 | 0.0027344 | 0.0042639 | -0.004125 | 0.0026424 | -0.0030975 | -0.081101 | -0.0065731 | -0.0026212 | 0.0029374 | 0.0023989 | -0.0069578 | 0.059509 | 0.018311 | 0.009155 | 0.004578 | 0.082397 | 0.013733 | -0.12817 | 0.041199 | -0.018311 | -0.10071 | 0.036621 | 0.027466 | -0.064087 | -0.1236 | 60.791 | 60.6491 | -61.7249 | 60.7956 | 60.7819 | 0.13275 | -61.7477 | 60.7132 | 60.6537 | -61.7706 | 60.8185 | 60.6766 | 0.022888 | -61.7798 | 60.8597 | 60.8368 | 60.7864 | -61.9354 | 60.8139 | 60.8047 | 60.759 | -61.9308
173.1875 | 122.8683 | -60.7727 | 61.7386 | -0.10742 | 0.01207 | 0.0050842 | 0.0049047 | -0.0036978 | -0.005048 | -0.0037385 | -0.042954 | -0.0044369 | -0.0026212 | 0.00080099 | -0.0014463 | -0.005676 | 0.11444 | 0.16022 | 0.15106 | 0.091553 | 0.09613 | 0.086975 | -0.022888 | 0.1831 | 0.27924 | 0.10986 | 0.054932 | 0.032043 | 0.036621 | -0.009155 | 60.8597 | 60.7498 | -61.6425 | 60.9329 | 60.8643 | 0.11444 | -61.6241 | 60.8093 | 60.7636 | -61.6837 | 60.9558 | 60.8826 | 0.11902 | -61.7065 | 60.8688 | 60.8871 | 60.9238 | -61.7615 | 60.8276 | 60.8047 | 61.0519 | -61.7477
174.8438 | 122.8134 | -60.7773 | 61.7798 | -0.084534 | 0.014206 | 0.0027344 | 0.0036231 | -0.0022024 | 0.0030698 | -0.0016021 | -0.12688 | -0.0025143 | -0.0017666 | 0.0012284 | 0.0034671 | -0.0080258 | 0.059509 | 0.032043 | 0.027466 | 0.018311 | 0.073242 | 0.009155 | -0.12817 | 0.068665 | 0.022888 | -0.059509 | 0.045776 | 0.027466 | -0.036621 | -0.091553 | 60.7864 | 60.6491 | -61.7065 | 60.8093 | 60.7956 | 0.14649 | -61.7203 | 60.7407 | 60.6857 | -61.734 | 60.8459 | 60.7178 | 0.032044 | -61.7523 | 60.8505 | 60.8368 | 60.8047 | -61.908 | 60.8231 | 60.8047 | 60.8002 | -61.8713
176.5156 | 122.7722 | -60.8047 | 61.7661 | 0.052795 | 0.011002 | 0.0033752 | 0.0064001 | -0.0045522 | -0.0052616 | -0.0048065 | 0.094375 | -0.0063595 | -0.003262 | -5.3406e-05 | 0.00047633 | -0.0058896 | 0.013733 | 0.027466 | 0.054932 | 0.018311 | 0.054932 | 0.045776 | -0.07782 | 0.09613 | 0.14191 | 0 | 0.054932 | 0.036621 | -0.004578 | -0.045776 | 60.8505 | 60.7269 | -61.7111 | 60.8322 | 60.8231 | 0.096131 | -61.7523 | 60.8002 | 60.759 | -61.7111 | 60.9009 | 60.8047 | 0.045776 | -61.7294 | 60.8597 | 60.8185 | 60.8597 | -61.8439 | 60.8597 | 60.8414 | 60.9467 | -61.8118
178.1875 | 122.8088 | -60.7819 | 61.7752 | -0.22949 | 0.013352 | 0.0044434 | 0.0042639 | -0.0028432 | -0.0020572 | -0.0041657 | -0.22606 | -0.0082821 | -0.0026212 | -5.3406e-05 | 0.00068993 | -0.0071714 | 0.13733 | 0.15106 | 0.13733 | 0.10529 | 0.10986 | 0.09613 | 0 | 0.11902 | 0.21515 | 0.022888 | 0.09613 | 0.086975 | 0.036621 | -0.018311 | 60.878 | 60.7819 | -61.6653 | 60.9329 | 60.8871 | 0.10529 | -61.6379 | 60.8185 | 60.7635 | -61.6791 | 60.9009 | 60.8047 | 0.041199 | -61.6882 | 60.8917 | 60.9192 | 60.9192 | -61.7752 | 60.878 | 60.8688 | 60.997 | -61.7935
179.8438 | 122.85 | -60.7681 | 61.7661 | -0.25238 | 0.013565 | 0.0050842 | 0.0059729 | -0.0022024 | -0.002698 | -0.0035249 | -0.22606 | -0.0035825 | -0.0045438 | 0.00251 | 0.0013309 | -0.0078122 | 0.091553 | 0.045776 | 0.041199 | 0.050354 | 0.1831 | 0.086975 | -0.045776 | 0.054932 | 0.073242 | -0.045776 | 0.11444 | 0.091553 | 0.013733 | -0.045776 | 60.8551 | 60.7224 | -61.5829 | 60.8139 | 60.8185 | 0.09613 | -61.6745 | 60.7819 | 60.7224 | -61.6516 | 60.8231 | 60.7224 | 0 | -61.6745 | 60.9512 | 60.8597 | 60.8093 | -61.8118 | 60.8826 | 60.8597 | 60.8414 | -61.8118
181.5312 | 122.8409 | -60.7727 | 61.7798 | -0.084534 | 0.015061 | 0.0014526 | 0.0042639 | -0.00027985 | 0.0049924 | -0.0026703 | -0.13451 | -0.0027279 | -0.0017666 | 0.003151 | 0.0034671 | -0.0052488 | 0.073242 | 0.018311 | 0.027466 | 0.018311 | 0.068665 | 0.022888 | -0.11902 | 0.082397 | 0.036621 | -0.068665 | 0.036621 | 0.018311 | -0.045776 | -0.09613 | 60.7956 | 60.6537 | -61.7111 | 60.791 | 60.791 | 0.13733 | -61.7065 | 60.7269 | 60.6766 | -61.7432 | 60.8551 | 60.704 | 0.027465 | -61.7615 | 60.8414 | 60.8459 | 60.8002 | -61.8988 | 60.8093 | 60.791 | 60.8093 | -61.8759
183.1875 | 122.7539 | -60.8093 | 61.7844 | 0.083313 | 0.013992 | 0.0025208 | -8.476e-06 | -0.0022024 | -0.00034818 | -0.00053407 | -0.0048066 | -0.0029415 | -0.0039028 | -0.0015488 | 0.0053897 | -0.0063168 | -0.054932 | -0.091553 | -0.09613 | -0.064087 | 0.054932 | -0.045776 | -0.16479 | -0.054932 | -0.1236 | -0.17853 | 0.027466 | 0.009155 | -0.073242 | -0.13275 | 60.7636 | 60.6445 | -61.7294 | 60.7178 | 60.7452 | 0.10071 | -61.8393 | 60.7361 | 60.6766 | -61.7569 | 60.7544 | 60.6308 | -0.045777 | -61.7752 | 60.8643 | 60.7544 | 60.7132 | -61.9492 | 60.8368 | 60.8185 | 60.6857 | -61.9171
184.8594 | 122.7264 | -60.8231 | 61.7661 | 0.12909 | 0.010788 | 0.0057252 | 0.0036231 | -0.0043386 | -0.0039798 | -0.0041657 | 0.1783 | -0.0070003 | -0.0036892 | -0.00090781 | 4.9132e-05 | -0.0033262 | 0.004578 | 0.032043 | 0.050354 | -0.022888 | -0.009155 | -0.009155 | -0.13733 | 0.09613 | 0.11444 | 0.013733 | 0.018311 | -0.013733 | -0.009155 | -0.07782 | 60.8139 | 60.6857 | -61.7752 | 60.8551 | 60.8002 | 0.11444 | -61.7615 | 60.8139 | 60.7452 | -61.7477 | 60.9192 | 60.8368 | 0.091553 | -61.7798 | 60.8139 | 60.8276 | 60.8734 | -61.9034 | 60.8414 | 60.8093 | 60.9375 | -61.8439
186.5312 | 122.7905 | -60.7956 | 61.7798 | 0.12146 | 0.011215 | 0.002948 | 0.0031957 | -0.001348 | 0.00050622 | -0.0026703 | 0.15541 | -0.0055051 | -0.004971 | -0.00090781 | 0.0041079 | -0.0041806 | -0.045776 | -0.073242 | -0.082397 | -0.091553 | 0.050354 | -0.041199 | -0.17853 | 0.018311 | -0.073242 | -0.10986 | 0 | -0.018311 | -0.068665 | -0.12817 | 60.7544 | 60.6171 | -61.7294 | 60.7224 | 60.704 | 0.086975 | -61.8256 | 60.7269 | 60.6674 | -61.7798 | 60.8139 | 60.6857 | 0.018311 | -61.7981 | 60.8459 | 60.7498 | 60.7132 | -61.9583 | 60.7956 | 60.7773 | 60.7224 | -61.908
188.2031 | 122.8088 | -60.7956 | 61.7844 | -0.23712 | 0.012924 | 0.0044434 | 0.0083227 | -0.0043386 | -0.0037662 | -0.0037385 | -0.17265 | -0.0046505 | -0.0011258 | -0.0021896 | -0.0018735 | -0.003967 | 0.082397 | 0.10529 | 0.10529 | 0.064087 | 0.12817 | 0.073242 | -0.036621 | 0.07782 | 0.14648 | -0.018311 | 0.13275 | 0.091553 | 0.018311 | -0.036621 | 60.8688 | 60.759 | -61.6562 | 60.9009 | 60.8597 | 0.10071 | -61.702 | 60.8139 | 60.759 | -61.6516 | 60.8734 | 60.7773 | 0.01831 | -61.6928 | 60.9238 | 60.878 | 60.9009 | -61.821 | 60.9283 | 60.8871 | 60.9421 | -61.821
189.875 | 122.7905 | -60.8047 | 61.7706 | 0.19012 | 0.012497 | 0.0027344 | 0.0042639 | -0.0047658 | -0.00013458 | -0.0016021 | 0.14778 | -0.0061459 | -0.0043302 | 0.00080099 | 0.0034671 | -0.0061032 | -0.045776 | -0.082397 | -0.068665 | -0.073242 | 0.009155 | -0.027466 | -0.17395 | 0.059509 | -0.036621 | -0.054932 | -0.013733 | -0.022888 | -0.054932 | -0.1236 | 60.7773 | 60.6308 | -61.7615 | 60.7224 | 60.7315 | 0.10071 | -61.8164 | 60.7498 | 60.6812 | -61.7844 | 60.8643 | 60.7498 | 0.068664 | -61.7935 | 60.8139 | 60.759 | 60.7361 | -61.9446 | 60.791 | 60.7819 | 60.7681 | -61.8942
191.5469 | 122.8546 | -60.7773 | 61.7615 | -0.22949 | 0.013565 | 0.0050842 | 0.0072547 | -0.00070705 | -0.0020572 | -0.0039521 | -0.24895 | -0.0048641 | 0.0010104 | 0.001442 | 0.00026273 | -0.0058896 | 0.073242 | 0.045776 | 0.054932 | 0.050354 | 0.1831 | 0.09613 | -0.050354 | 0.059509 | 0.11444 | -0.045776 | 0.14191 | 0.10071 | 0.018311 | -0.036621 | 60.8734 | 60.7269 | -61.5784 | 60.8231 | 60.8276 | 0.10071 | -61.6882 | 60.7956 | 60.7407 | -61.6196 | 60.8368 | 60.7315 | -0.009155 | -61.6608 | 60.9604 | 60.8505 | 60.8322 | -61.8118 | 60.9192 | 60.878 | 60.8917 | -61.7981
193.2031 | 122.7585 | -60.8093 | 61.7798 | 0.075684 | 0.0080109 | 0.0035888 | 0.00020512 | -0.0030568 | -0.0037662 | -0.0039521 | 0.102 | -0.0063595 | -0.00668 | -0.00048061 | 0.0015445 | -0.0048214 | 0.032043 | 0.041199 | 0.054932 | 0.009155 | 0.045776 | 0.041199 | -0.086975 | 0.086975 | 0.10986 | 0.004578 | 0.045776 | 0.018311 | 0.004578 | -0.086975 | 60.8505 | 60.7224 | -61.734 | 60.8505 | 60.8185 | 0.09613 | -61.7477 | 60.8139 | 60.7224 | -61.734 | 60.8963 | 60.8139 | 0.091553 | -61.7615 | 60.8551 | 60.8414 | 60.8643 | -61.8668 | 60.8551 | 60.8276 | 60.9192 | -61.8668
194.8594 | 122.85 | -60.7452 | 61.7752 | -0.25238 | 0.013352 | 0.004657 | 0.0078955 | -0.0032706 | 0.0015744 | -0.0039521 | -0.21843 | -0.0055051 | -0.0028348 | 0.00080099 | -0.00016447 | -0.0052488 | 0.07782 | 0.032043 | 0.027466 | 0.045776 | 0.1831 | 0.086975 | -0.059509 | 0.036621 | 0.086975 | -0.045776 | 0.10986 | 0.10071 | 0.027466 | -0.050354 | 60.8322 | 60.6857 | -61.5921 | 60.7773 | 60.791 | 0.10528 | -61.6974 | 60.7727 | 60.6949 | -61.6653 | 60.7819 | 60.6995 | 0.004578 | -61.6745 | 60.9283 | 60.8231 | 60.7727 | -61.8347 | 60.8551 | 60.8459 | 60.8322 | -61.8256
196.5312 | 122.7219 | -60.7956 | 61.7981 | 0.12146 | 0.011429 | 0.0023072 | 0.0025549 | -0.0032706 | -0.002698 | -0.0028839 | 0.15541 | -0.0074277 | -0.0030484 | -0.00026701 | 0.00068993 | -0.0043942 | 0.036621 | 0.041199 | 0.054932 | -0.013733 | -0.013733 | -0.009155 | -0.13275 | 0.10529 | 0.073242 | -0.027466 | -0.013733 | -0.041199 | -0.050354 | -0.10986 | 60.7864 | 60.6628 | -61.8118 | 60.8368 | 60.7819 | 0.11902 | -61.7615 | 60.7452 | 60.6857 | -61.8118 | 60.9009 | 60.7681 | 0.082397 | -61.8393 | 60.7819 | 60.8322 | 60.8505 | -61.9308 | 60.7819 | 60.7544 | 60.8688 | -61.908
198.2031 | 122.7448 | -60.7956 | 61.8073 | 0.029907 | 0.012497 | 0.0033752 | 0.0021277 | -0.0047658 | 0.0039242 | -0.0028839 | 0.018082 | -0.0046505 | -0.0041164 | -5.3406e-05 | 0.0049625 | -0.006744 | -0.050354 | -0.10986 | -0.10529 | -0.091553 | 0.059509 | -0.022888 | -0.16022 | -0.013733 | -0.13733 | -0.16937 | 0.027466 | -0.013733 | -0.068665 | -0.15564 | 60.7727 | 60.6354 | -61.7477 | 60.6857 | 60.704 | 0.068664 | -61.8576 | 60.7269 | 60.64 | -61.7798 | 60.7819 | 60.6262 | -0.013733 | -61.821 | 60.8551 | 60.7452 | 60.6903 | -61.9675 | 60.8231 | 60.7819 | 60.6583 | -61.9629
199.8594 | 122.8043 | -60.7773 | 61.7615 | -0.22186 | 0.014847 | 0.0050842 | 0.0087499 | -0.001348 | -0.0020572 | -0.0035249 | -0.15739 | -0.0070003 | -0.0013394 | 0.00058739 | -0.00059167 | -0.005035 | 0.10071 | 0.10986 | 0.11902 | 0.091553 | 0.14191 | 0.10071 | -0.022888 | 0.09613 | 0.15564 | -0.009155 | 0.11902 | 0.091553 | 0.022888 | -0.036621 | 60.878 | 60.7544 | -61.6196 | 60.8871 | 60.8688 | 0.11444 | -61.6608 | 60.8002 | 60.7407 | -61.6425 | 60.8734 | 60.7681 | 0.027466 | -61.6699 | 60.9192 | 60.878 | 60.8963 | -61.7844 | 60.8963 | 60.8688 | 60.9329 | -61.7981
201.5156 | 122.7585 | -60.8047 | 61.7935 | 0.12146 | 0.012283 | 0.00017099 | 0.0012731 | -0.0030568 | 0.0013608 | -0.0013885 | 0.094375 | -0.0048641 | -0.0045438 | 0.001442 | 0.0026125 | -0.0078122 | -0.068665 | -0.12817 | -0.10986 | -0.07782 | 0.041199 | -0.036621 | -0.16937 | -0.027466 | -0.12817 | -0.17395 | 0.036621 | 0.009155 | -0.086975 | -0.13733 | 60.7681 | 60.6354 | -61.7523 | 60.6766 | 60.7269 | 0.091553 | -61.8622 | 60.7178 | 60.6674 | -61.7569 | 60.7773 | 60.6308 | -0.036621 | -61.7844 | 60.8459 | 60.7361 | 60.6949 | -61.9629 | 60.8414 | 60.8139 | 60.6766 | -61.9308
203.1719 | 122.7493 | -60.8139 | 61.7752 | 0.037537 | 0.0099335 | 0.002948 | 0.0046911 | -0.0017752 | -0.0056888 | -0.0011749 | 0.12489 | -0.0082821 | -0.0028348 | 0.0010148 | 0.00026273 | -0.0058896 | 0.022888 | 0.050354 | 0.041199 | 0.013733 | 0.064087 | 0.036621 | -0.07782 | 0.073242 | 0.13733 | 0 | 0.045776 | 0.041199 | -0.013733 | -0.064087 | 60.8505 | 60.7361 | -61.7111 | 60.8643 | 60.8276 | 0.091553 | -61.7523 | 60.8002 | 60.7498 | -61.7294 | 60.8871 | 60.8139 | 0.064087 | -61.734 | 60.878 | 60.8368 | 60.8551 | -61.853 | 60.8597 | 60.8551 | 60.9512 | -61.8393
204.8438 | 122.7905 | -60.791 | 61.7844 | -0.054016 | 0.013138 | 0.00017099 | 0.0031957 | -0.0036978 | 0.0013608 | -0.0018159 | -0.13451 | -0.0020871 | -0.0058254 | 0.00080099 | 0.0049625 | -0.0058896 | 0.064087 | 0.036621 | 0.018311 | 0 | 0.086975 | 0.004578 | -0.11444 | 0.050354 | -0.009155 | -0.082397 | 0.022888 | 0.032043 | -0.045776 | -0.091553 | 60.7956 | 60.6766 | -61.6974 | 60.8276 | 60.791 | 0.11444 | -61.7203 | 60.7452 | 60.6995 | -61.7615 | 60.8414 | 60.7086 | 0.009156 | -61.7523 | 60.878 | 60.8551 | 60.8093 | -61.8988 | 60.8139 | 60.8231 | 60.7819 | -61.8759
206.5156 | 122.7219 | -60.8505 | 61.7706 | 0.090942 | 0.013352 | 0.0048706 | 0.0068273 | -0.0064748 | -0.0052616 | -0.0033111 | 0.14015 | -0.0070003 | -0.0021938 | 0.00058739 | -0.0012327 | -0.0041806 | 0.032043 | 0.050354 | 0.054932 | 0 | 0.041199 | 0.027466 | -0.10529 | 0.086975 | 0.11902 | 0 | 0.041199 | 0.009155 | -0.013733 | -0.059509 | 60.878 | 60.7452 | -61.7294 | 60.9009 | 60.8505 | 0.10529 | -61.7386 | 60.8368 | 60.791 | -61.7294 | 60.9375 | 60.8505 | 0.059509 | -61.7615 | 60.8917 | 60.8826 | 60.9055 | -61.8759 | 60.8917 | 60.8597 | 60.9695 | -61.8301
208.1875 | 122.8638 | -60.7727 | 61.7432 | -0.12268 | 0.012711 | 0.0038024 | 0.0051183 | -0.0028432 | -0.0059024 | -0.0022431 | -0.081101 | -0.0070003 | -0.0043302 | -0.00090781 | -0.00080527 | -0.0058896 | 0.14648 | 0.18768 | 0.16937 | 0.09613 | 0.11902 | 0.091553 | -0.050354 | 0.21057 | 0.29755 | 0.10986 | 0.059509 | 0.050354 | 0.068665 | -0.018311 | 60.8643 | 60.7224 | -61.6241 | 60.9604 | 60.8688 | 0.14648 | -61.5967 | 60.8414 | 60.7544 | -61.6837 | 60.9833 | 60.8826 | 0.12817 | -61.6928 | 60.8917 | 60.9192 | 60.9421 | -61.7935 | 60.8322 | 60.8231 | 61.0703 | -61.7615
209.8594 | 122.7814 | -60.7864 | 61.7798 | 0.045166 | 0.011215 | 0.0048706 | 0.0031957 | -0.0015616 | -0.0048344 | -0.0039521 | 0.094375 | -0.0072141 | -0.0017666 | -0.0011216 | 0.00090353 | -0.0071714 | 0.036621 | 0.032043 | 0.045776 | 0.022888 | 0.068665 | 0.036621 | -0.07782 | 0.091553 | 0.12817 | -0.018311 | 0.054932 | 0.027466 | 0.004578 | -0.059509 | 60.8231 | 60.7086 | -61.7111 | 60.8185 | 60.8093 | 0.10071 | -61.7432 | 60.791 | 60.7269 | -61.7249 | 60.878 | 60.7681 | 0.041198 | -61.7523 | 60.8551 | 60.8231 | 60.8322 | -61.8576 | 60.8414 | 60.8139 | 60.9146 | -61.8393
211.5469 | 122.7722 | -60.7956 | 61.7935 | 0.17487 | 0.013779 | 0.0027344 | -0.00086308 | -0.0028432 | 0.0024288 | -0.0018159 | 0.14015 | -0.0076413 | -0.0019802 | -0.0032578 | 0.0045351 | -0.0065304 | 0.036621 | 0.013733 | 0.009155 | -0.009155 | -0.004578 | -0.013733 | -0.15106 | 0.082397 | 0.036621 | -0.036621 | -0.032043 | -0.073242 | -0.068665 | -0.11444 | 60.7819 | 60.6445 | -61.7981 | 60.8093 | 60.7864 | 0.14191 | -61.7569 | 60.7269 | 60.6812 | -61.8256 | 60.878 | 60.759 | 0.07782 | -61.8668 | 60.791 | 60.8322 | 60.8047 | -61.9446 | 60.7635 | 60.7224 | 60.8322 | -61.908
213.2188 | 122.8226 | -60.7727 | 61.7752 | -0.1532 | 0.011856 | 0.0020936 | 0.0061865 | -0.0015616 | -0.0041934 | -0.0028839 | -0.18791 | -0.0050777 | -0.0026212 | -0.00090781 | 0.0015445 | -0.0086666 | 0.15564 | 0.15564 | 0.16479 | 0.10986 | 0.086975 | 0.09613 | -0.027466 | 0.16479 | 0.25177 | 0.054932 | 0.082397 | 0.068665 | 0.018311 | -0.027466 | 60.8688 | 60.7452 | -61.6882 | 60.9283 | 60.8826 | 0.13733 | -61.6196 | 60.791 | 60.7452 | -61.6928 | 60.9375 | 60.8276 | 0.082398 | -61.7065 | 60.8597 | 60.9283 | 60.9375 | -61.8027 | 60.8551 | 60.8414 | 61.0245 | -61.8027
214.9375 | 122.7768 | -60.8002 | 61.7889 | 0.1062 | 0.010147 | 0.002948 | -0.00043588 | -0.0047658 | 0.00093342 | -0.0037385 | 0.14778 | -0.0061459 | -0.0071072 | -0.00090781 | 0.0053897 | -0.005676 | 0.041199 | 0.013733 | 0.036621 | -0.009155 | -0.022888 | -0.018311 | -0.15106 | 0.09613 | 0.022888 | -0.032043 | -0.032043 | -0.059509 | -0.059509 | -0.11444 | 60.7819 | 60.6491 | -61.8118 | 60.8139 | 60.791 | 0.14191 | -61.7477 | 60.7407 | 60.6857 | -61.821 | 60.8963 | 60.7681 | 0.082398 | -61.8484 | 60.7773 | 60.8414 | 60.8368 | -61.94 | 60.7681 | 60.7407 | 60.8231 | -61.9034
216.6094 | 122.7448 | -60.8185 | 61.8164 | 0.075684 | 0.016129 | 0.0023072 | 0.0010595 | -0.0039114 | 0.0024288 | -0.0016021 | 0.071487 | -0.0025143 | -0.0036892 | 0.00058739 | 0.0053897 | -0.0061032 | -0.054932 | -0.13275 | -0.1236 | -0.091553 | 0.064087 | -0.027466 | -0.17395 | -0.032043 | -0.12817 | -0.17853 | 0.009155 | -0.009155 | -0.082397 | -0.14648 | 60.791 | 60.6445 | -61.7523 | 60.6857 | 60.7269 | 0.082397 | -61.8713 | 60.7361 | 60.672 | -61.8073 | 60.7864 | 60.64 | -0.032044 | -61.8256 | 60.8826 | 60.7635 | 60.6949 | -61.9904 | 60.8276 | 60.8093 | 60.6903 | -61.9629
218.2969 | 122.8546 | -60.7681 | 61.7798 | -0.22186 | 0.013992 | 0.0040162 | 0.0076819 | -0.0045522 | -0.0018436 | -0.0033111 | -0.24132 | -0.0044369 | -0.0019802 | 0.00037379 | -0.00059167 | -0.0063168 | 0.073242 | 0.045776 | 0.068665 | 0.041199 | 0.16479 | 0.064087 | -0.068665 | 0.073242 | 0.11902 | -0.045776 | 0.14648 | 0.1236 | 0.009155 | -0.036621 | 60.8322 | 60.6995 | -61.615 | 60.8139 | 60.8093 | 0.10986 | -61.7065 | 60.7773 | 60.7315 | -61.6333 | 60.8414 | 60.7224 | -0.009155 | -61.6562 | 60.9329 | 60.8414 | 60.8368 | -61.8484 | 60.9146 | 60.8917 | 60.8871 | -61.8164
220.0156 | 122.7814 | -60.7681 | 61.7798 | 0.090942 | 0.012497 | 0.0027344 | 0.0017005 | -0.0043386 | -0.00056178 | -0.0030975 | 0.1783 | -0.0055051 | -0.0034756 | 0.00080099 | 0.0026125 | -0.006744 | -0.041199 | -0.07782 | -0.07782 | -0.082397 | 0.068665 | -0.027466 | -0.17395 | 0.027466 | -0.068665 | -0.10071 | 0.004578 | -0.036621 | -0.07782 | -0.13275 | 60.7407 | 60.5942 | -61.7111 | 60.6903 | 60.6857 | 0.091553 | -61.821 | 60.6903 | 60.6354 | -61.7752 | 60.7956 | 60.6674 | 0.032043 | -61.8164 | 60.8368 | 60.7269 | 60.6903 | -61.9537 | 60.7727 | 60.7315 | 60.6995 | -61.9125
221.6875 | 122.8409 | -60.7681 | 61.7432 | -0.18372 | 0.013138 | 0.0052978 | 0.0061865 | -0.002416 | -0.0056888 | -0.0013885 | -0.14977 | -0.0065731 | -0.0019802 | 0.00037379 | 0.0011173 | -0.0052488 | 0.15564 | 0.17853 | 0.18768 | 0.12817 | 0.11902 | 0.10529 | -0.036621 | 0.17853 | 0.29297 | 0.10986 | 0.07782 | 0.059509 | 0.032043 | -0.013733 | 60.8734 | 60.7315 | -61.6241 | 60.9467 | 60.8963 | 0.1648 | -61.5875 | 60.8002 | 60.7544 | -61.6653 | 60.9467 | 60.878 | 0.1236 | -61.6837 | 60.8871 | 60.9238 | 60.9558 | -61.7798 | 60.8459 | 60.8276 | 61.0611 | -61.7569
223.3594 | 122.8683 | -60.7681 | 61.7798 | -0.11505 | 0.014206 | -0.00089721 | 0.0034093 | -0.002416 | 0.0028562 | -0.00096127 | -0.17265 | -0.0040097 | -0.0039028 | 0.00037379 | 0.0030399 | -0.0063168 | 0.068665 | 0.018311 | 0.022888 | 0.009155 | 0.10529 | 0.041199 | -0.10529 | 0.068665 | 0.045776 | -0.064087 | 0.054932 | 0.018311 | -0.032043 | -0.10529 | 60.8093 | 60.6628 | -61.6745 | 60.7864 | 60.7773 | 0.11444 | -61.7111 | 60.7361 | 60.6628 | -61.7249 | 60.8368 | 60.704 | 0.041199 | -61.7615 | 60.8734 | 60.8368 | 60.791 | -61.8851 | 60.8231 | 60.7864 | 60.8139 | -61.8851
225.0312 | 122.818 | -60.7773 | 61.7798 | -0.21423 | 0.015274 | 0.0042298 | 0.0085363 | -0.0028432 | -0.0024844 | -0.0033111 | -0.20317 | -0.0042233 | -0.0028348 | -5.3406e-05 | 0.00047633 | -0.0054624 | 0.07782 | 0.045776 | 0.064087 | 0.041199 | 0.16022 | 0.086975 | -0.054932 | 0.09613 | 0.13733 | -0.022888 | 0.13275 | 0.10986 | 0.004578 | -0.032043 | 60.8643 | 60.7224 | -61.6196 | 60.8231 | 60.8185 | 0.096131 | -61.702 | 60.7819 | 60.7452 | -61.647 | 60.8734 | 60.7544 | 0.009155 | -61.6699 | 60.9375 | 60.8551 | 60.8414 | -61.8347 | 60.91 | 60.8871 | 60.9146 | -61.8118
226.6875 | 122.7448 | -60.8002 | 61.7981 | 0.1825 | 0.0097199 | 0.002948 | 0.00063232 | -0.001348 | -0.00098918 | -0.0016021 | 0.18593 | -0.0050777 | -0.0051846 | 0.00058739 | 0.0041079 | -0.0080258 | 0.013733 | 0.009155 | 0.022888 | -0.022888 | -0.032043 | -0.013733 | -0.14191 | 0.082397 | 0.045776 | -0.041199 | -0.045776 | -0.064087 | -0.07782 | -0.1236 | 60.7864 | 60.6583 | -61.8301 | 60.8093 | 60.7773 | 0.11902 | -61.7844 | 60.7224 | 60.6766 | -61.8439 | 60.8826 | 60.759 | 0.082397 | -61.8622 | 60.7681 | 60.8139 | 60.8231 | -61.94 | 60.7544 | 60.7361 | 60.8459 | -61.9217
228.3438 | 122.8775 | -60.7636 | 61.7706 | -0.24475 | 0.013352 | 0.0033752 | 0.0059729 | -0.0011342 | -0.00077538 | -0.0033111 | -0.23369 | -0.0050777 | -0.0021938 | -5.3406e-05 | 0.00047633 | -0.0065304 | 0.073242 | 0.041199 | 0.036621 | 0.050354 | 0.17395 | 0.07782 | -0.045776 | 0.054932 | 0.07782 | -0.064087 | 0.12817 | 0.091553 | -0.013733 | -0.064087 | 60.8414 | 60.7178 | -61.5967 | 60.8047 | 60.8139 | 0.09613 | -61.6974 | 60.7498 | 60.6995 | -61.6425 | 60.8185 | 60.6995 | 0 | -61.6791 | 60.9375 | 60.8368 | 60.8002 | -61.8164 | 60.8917 | 60.8551 | 60.8414 | -61.8347
230.0312 | 122.7493 | -60.8093 | 61.7706 | 0.1825 | 0.014633 | 0.0014526 | 0.0029821 | -0.0056204 | -0.0024844 | -0.00096127 | 0.17067 | -0.0067867 | -0.0028348 | -0.00048061 | 0.0032535 | -0.0071714 | 0.004578 | 0.009155 | 0.045776 | -0.013733 | -0.036621 | -0.009155 | -0.17395 | 0.10071 | 0.07782 | -0.013733 | -0.027466 | -0.041199 | -0.064087 | -0.10529 | 60.8002 | 60.6354 | -61.8073 | 60.8185 | 60.7956 | 0.16022 | -61.7661 | 60.7452 | 60.704 | -61.7981 | 60.91 | 60.7956 | 0.091553 | -61.8118 | 60.7727 | 60.8139 | 60.8551 | -61.9446 | 60.7819 | 60.7681 | 60.8871 | -61.8759
231.7031 | 122.818 | -60.7864 | 61.7798 | -0.21423 | 0.011643 | 0.0020936 | 0.0038367 | -0.0026296 | -0.0022708 | -0.0050201 | -0.16502 | -0.0057187 | -0.0021938 | -0.00069421 | -0.00059167 | -0.0063168 | 0.09613 | 0.10071 | 0.09613 | 0.07782 | 0.16022 | 0.091553 | -0.036621 | 0.07782 | 0.13733 | -0.018311 | 0.12817 | 0.091553 | 0.004578 | -0.050354 | 60.878 | 60.7498 | -61.6196 | 60.8871 | 60.8643 | 0.11444 | -61.6837 | 60.791 | 60.7361 | -61.6516 | 60.8643 | 60.7681 | 0.032043 | -61.6882 | 60.9467 | 60.8826 | 60.8826 | -61.8164 | 60.9146 | 60.878 | 60.9238 | -61.8301
233.4062 | 122.7814 | -60.8139 | 61.8073 | 0.11383 | 0.01207 | 0.0027344 | 0.0025549 | -0.0011342 | 0.00029262 | -0.0039521 | 0.094375 | -0.0046505 | -0.0041164 | 0.0016556 | 0.0041079 | -0.0065304 | -0.036621 | -0.10071 | -0.091553 | -0.10071 | 0.041199 | -0.036621 | -0.16022 | 0.018311 | -0.10529 | -0.13275 | 0.036621 | -0.004578 | -0.073242 | -0.13733 | 60.7773 | 60.6537 | -61.7661 | 60.7132 | 60.7132 | 0.059509 | -61.8439 | 60.7407 | 60.6766 | -61.7706 | 60.8322 | 60.6812 | 0.004578 | -61.8118 | 60.8551 | 60.7773 | 60.7224 | -61.9675 | 60.8505 | 60.8093 | 60.7086 | -61.9446
235.0781 | 122.7814 | -60.8093 | 61.7752 | 0.022278 | 0.011215 | 0.0040162 | 0.0038367 | -0.0039114 | -0.0059024 | -0.0045929 | 0.086746 | -0.0070003 | -0.0019802 | -0.0013352 | -0.0012327 | -0.0035398 | 0.027466 | 0.041199 | 0.050354 | 0.013733 | 0.073242 | 0.054932 | -0.10986 | 0.086975 | 0.14648 | -0.018311 | 0.059509 | 0.041199 | 0.013733 | -0.068665 | 60.8643 | 60.6995 | -61.702 | 60.8505 | 60.8231 | 0.1236 | -61.7477 | 60.8231 | 60.7407 | -61.7157 | 60.8963 | 60.791 | 0.050354 | -61.734 | 60.8826 | 60.8368 | 60.8597 | -61.8851 | 60.8688 | 60.8505 | 60.9558 | -61.8439
236.7344 | 122.7264 | -60.8047 | 61.8073 | -0.031128 | 0.013779 | 0.0014526 | 0.00084592 | -0.0019888 | 0.0020016 | -0.0013885 | -0.050583 | -0.0048641 | -0.0051846 | 0.00016019 | 0.0053897 | -0.0071714 | 0.009155 | -0.032043 | -0.018311 | -0.027466 | 0.054932 | -0.004578 | -0.14191 | -0.013733 | -0.086975 | -0.15564 | 0.013733 | 0.018311 | -0.07782 | -0.14191 | 60.8002 | 60.6628 | -61.7523 | 60.7727 | 60.7773 | 0.11444 | -61.7981 | 60.7269 | 60.6628 | -61.7935 | 60.791 | 60.6491 | -0.013733 | -61.7889 | 60.8597 | 60.8139 | 60.7864 | -61.9492 | 60.8185 | 60.8231 | 60.7178 | -61.9492
238.4688 | 122.7219 | -60.8047 | 61.7798 | 0.098572 | 0.012283 | 0.002948 | 0.0046911 | -0.0064748 | -0.004407 | -0.0041657 | 0.14778 | -0.0065731 | -0.003262 | 0.0010148 | -0.0010191 | -0.0065304 | 0.036621 | 0.050354 | 0.059509 | 0 | 0.013733 | 0.009155 | -0.11444 | 0.10071 | 0.10529 | -0.013733 | 0.013733 | 0.013733 | -0.004578 | -0.068665 | 60.8139 | 60.6903 | -61.7661 | 60.8551 | 60.8047 | 0.11444 | -61.7432 | 60.8002 | 60.7361 | -61.7661 | 60.9055 | 60.791 | 0.054932 | -61.7661 | 60.8185 | 60.8414 | 60.8643 | -61.8942 | 60.8185 | 60.8185 | 60.91 | -61.8484
240.1406 | 122.8912 | -60.7452 | 61.7706 | -0.16083 | 0.012711 | 0.002948 | 0.0034093 | -0.0032706 | 0.0015744 | -0.0033111 | -0.25658 | -0.0042233 | -0.0039028 | 0.0016556 | 0.0028263 | -0.0065304 | 0.068665 | 0.018311 | 0.009155 | 0.050354 | 0.14648 | 0.068665 | -0.068665 | 0.064087 | 0.07782 | -0.059509 | 0.09613 | 0.073242 | -0.013733 | -0.064087 | 60.8139 | 60.6766 | -61.6241 | 60.7635 | 60.7956 | 0.11902 | -61.702 | 60.7315 | 60.6812 | -61.6745 | 60.8093 | 60.6857 | 0.004578 | -61.6974 | 60.8917 | 60.8139 | 60.7544 | -61.8393 | 60.8414 | 60.8185 | 60.8231 | -61.8347
241.8125 | 122.818 | -60.7773 | 61.7844 | -0.24475 | 0.013352 | 0.0038024 | 0.0057593 | -0.0026296 | -0.002698 | -0.0028839 | -0.18791 | -0.0065731 | -0.0045438 | -0.00048061 | -0.00080527 | -0.0071714 | 0.1236 | 0.10529 | 0.11902 | 0.086975 | 0.15106 | 0.10071 | -0.032043 | 0.091553 | 0.16479 | -0.013733 | 0.11902 | 0.091553 | 0.027466 | -0.036621 | 60.878 | 60.7452 | -61.6333 | 60.8826 | 60.8643 | 0.11902 | -61.6608 | 60.8047 | 60.7407 | -61.6653 | 60.8688 | 60.7635 | 0.022888 | -61.6928 | 60.9283 | 60.9009 | 60.8963 | -61.8164 | 60.8963 | 60.8688 | 60.9421 | -61.821
243.5156 | 122.7356 | -60.8276 | 61.7889 | 0.14435 | 0.012497 | 0.0023072 | 0.0010595 | -0.001348 | -0.0046206 | -0.0022431 | 0.14015 | -0.0063595 | -0.0045438 | -0.00026701 | 0.0043215 | -0.005035 | 0.018311 | 0.050354 | 0.050354 | -0.004578 | -0.027466 | -0.018311 | -0.15106 | 0.091553 | 0.068665 | -0.027466 | -0.013733 | -0.022888 | -0.054932 | -0.09613 | 60.8093 | 60.6766 | -61.8164 | 60.878 | 60.8231 | 0.14648 | -61.7706 | 60.7727 | 60.7315 | -61.8027 | 60.9192 | 60.8002 | 0.068664 | -61.8118 | 60.8002 | 60.8459 | 60.878 | -61.94 | 60.8139 | 60.8047 | 60.8963 | -61.8851
245.1875 | 122.8088 | -60.759 | 61.7798 | -0.24475 | 0.013565 | 0.0038024 | 0.0051183 | -0.0022024 | -0.0012028 | -0.0054475 | -0.17265 | -0.0046505 | -0.0021938 | 0.001442 | 0.0019717 | -0.0058896 | 0.10071 | 0.09613 | 0.10071 | 0.082397 | 0.15564 | 0.10986 | -0.041199 | 0.07782 | 0.14648 | -0.032043 | 0.12817 | 0.10986 | 0.013733 | -0.045776 | 60.8688 | 60.7178 | -61.6241 | 60.8551 | 60.8414 | 0.1236 | -61.6791 | 60.7727 | 60.7132 | -61.6516 | 60.8368 | 60.7269 | 0.013733 | -61.6699 | 60.9146 | 60.8597 | 60.8597 | -61.821 | 60.8871 | 60.8688 | 60.9055 | -61.8256
246.8594 | 122.8546 | -60.7544 | 61.7569 | -0.084534 | 0.01442 | 0.0020936 | 0.0023413 | -0.0045522 | 0.0028562 | 0.00053413 | -0.15739 | -0.0046505 | -0.0034756 | 0.00058739 | 0.0045351 | -0.0058896 | 0.064087 | 0.032043 | 0.022888 | 0.018311 | 0.09613 | 0.018311 | -0.11444 | 0.068665 | 0.032043 | -0.054932 | 0.045776 | 0.027466 | -0.041199 | -0.086975 | 60.7727 | 60.64 | -61.6608 | 60.7864 | 60.7727 | 0.13275 | -61.6928 | 60.7132 | 60.6674 | -61.7111 | 60.8231 | 60.6995 | 0.032043 | -61.7294 | 60.8505 | 60.8185 | 60.7773 | -61.8713 | 60.8002 | 60.7819 | 60.7864 | -61.8439
248.5469 | 122.8958 | -60.7498 | 61.7798 | -0.16846 | 0.011856 | 0.00017099 | 0.0019141 | -0.0039114 | 7.902e-05 | -0.00032047 | -0.22606 | -0.0046505 | -0.0030484 | 0.00037379 | 0.0032535 | -0.005035 | 0.068665 | 0.027466 | 0.018311 | 0.041199 | 0.14191 | 0.059509 | -0.086975 | 0.068665 | 0.07782 | -0.064087 | 0.10071 | 0.068665 | 0 | -0.036621 | 60.8093 | 60.6628 | -61.6379 | 60.7773 | 60.791 | 0.12817 | -61.7111 | 60.7498 | 60.7132 | -61.6791 | 60.8185 | 60.6857 | -0.027466 | -61.7111 | 60.8917 | 60.8185 | 60.7681 | -61.8668 | 60.8505 | 60.8185 | 60.8276 | -61.8164
250.2188 | 122.7539 | -60.8093 | 61.7798 | 0.037537 | 0.011215 | 0.0033752 | 0.0046911 | -0.001348 | -0.006116 | -0.0022431 | 0.094375 | -0.0063595 | -0.0034756 | -0.00048061 | -0.00016447 | -0.0043942 | 0.041199 | 0.022888 | 0.054932 | 0.009155 | 0.027466 | 0.050354 | -0.091553 | 0.091553 | 0.12817 | 0 | 0.041199 | 0.027466 | -0.004578 | -0.086975 | 60.8597 | 60.7178 | -61.7523 | 60.8322 | 60.8185 | 0.10071 | -61.7386 | 60.8047 | 60.7224 | -61.7386 | 60.9009 | 60.8093 | 0.086975 | -61.7523 | 60.8368 | 60.8505 | 60.8643 | -61.8713 | 60.8505 | 60.8368 | 60.9375 | -61.8668
251.9062 | 122.7585 | -60.8322 | 61.7798 | -0.046387 | 0.013565 | 0.0023072 | 0.0019141 | -0.0032706 | 0.0026424 | -0.0024567 | -0.042954 | -0.0040097 | -0.0041164 | 0.0020828 | 0.0036807 | -0.0071714 | 0.022888 | -0.032043 | -0.041199 | -0.045776 | 0.064087 | 0.009155 | -0.13275 | -0.018311 | -0.091553 | -0.15106 | 0.022888 | 0.022888 | -0.059509 | -0.12817 | 60.8414 | 60.6995 | -61.7157 | 60.8002 | 60.7864 | 0.086975 | -61.7569 | 60.7727 | 60.704 | -61.7569 | 60.8139 | 60.6812 | -0.022888 | -61.7569 | 60.8963 | 60.8551 | 60.791 | -61.9125 | 60.8551 | 60.8551 | 60.7407 | -61.908
253.5781 | 122.8638 | -60.7773 | 61.7477 | -0.10742 | 0.011856 | 0.0055114 | 0.0055457 | -0.0034842 | -0.0046206 | -0.0033111 | -0.073471 | -0.0078549 | -0.0047574 | 0.00016019 | -0.0027279 | -0.0046078 | 0.14191 | 0.17853 | 0.15564 | 0.10071 | 0.07782 | 0.082397 | -0.041199 | 0.21057 | 0.29297 | 0.12817 | 0.086975 | 0.022888 | 0.045776 | -0.013733 | 60.8597 | 60.7361 | -61.6699 | 60.9558 | 60.878 | 0.14191 | -61.6058 | 60.8231 | 60.7635 | -61.6608 | 60.9879 | 60.9055 | 0.14191 | -61.7249 | 60.8551 | 60.9192 | 60.9329 | -61.7889 | 60.8643 | 60.8002 | 61.0703 | -61.7615
255.25 | 122.8317 | -60.7819 | 61.7981 | -0.092163 | 0.015274 | 0.0025208 | 0.0031957 | -0.00092065 | 0.00071982 | -0.0018159 | -0.14977 | -0.0042233 | -0.0041164 | 0.0018692 | 0.0036807 | -0.0075986 | 0.07782 | 0.036621 | 0.013733 | 0.004578 | 0.09613 | 0.027466 | -0.10529 | 0.068665 | 0.027466 | -0.059509 | 0.041199 | 0.045776 | -0.059509 | -0.11444 | 60.8093 | 60.6766 | -61.702 | 60.8185 | 60.7864 | 0.10986 | -61.7203 | 60.7224 | 60.6674 | -61.7569 | 60.8505 | 60.7224 | 0.054932 | -61.7523 | 60.878 | 60.8597 | 60.7956 | -61.9034 | 60.8231 | 60.8276 | 60.8093 | -61.9125
256.9688 | 122.85 | -60.7636 | 61.7661 | -0.16083 | 0.012711 | 0.0035888 | 0.0091773 | -0.0030568 | -0.0052616 | -0.0039521 | -0.11162 | -0.0063595 | -0.001553 | -0.0021896 | 0.00047633 | -0.0071714 | 0.13733 | 0.17395 | 0.17395 | 0.12817 | 0.091553 | 0.086975 | -0.036621 | 0.18768 | 0.31128 | 0.10071 | 0.086975 | 0.068665 | 0.036621 | 0 | 60.8505 | 60.7269 | -61.6745 | 60.9375 | 60.8917 | 0.1648 | -61.6287 | 60.8002 | 60.7636 | -61.6791 | 60.9512 | 60.8643 | 0.10071 | -61.6974 | 60.8551 | 60.9009 | 60.9375 | -61.8027 | 60.8505 | 60.8322 | 61.0748 | -61.7661
258.625 | 122.7722 | -60.8139 | 61.7798 | 0.15961 | 0.013565 | 0.0023072 | 0.00063232 | -0.0043386 | 0.0013608 | -0.0013885 | 0.056228 | -0.0052915 | -0.0026212 | 0.00080099 | 0.0034671 | -0.0069578 | -0.073242 | -0.1236 | -0.10071 | -0.091553 | 0.022888 | -0.050354 | -0.17395 | 0 | -0.11902 | -0.14648 | 0.027466 | 0.013733 | -0.082397 | -0.12817 | 60.7636 | 60.64 | -61.7569 | 60.6903 | 60.7224 | 0.082397 | -61.853 | 60.7315 | 60.6857 | -61.7523 | 60.8139 | 60.6674 | -0.01831 | -61.7661 | 60.8368 | 60.7407 | 60.7132 | -61.9537 | 60.8414 | 60.8276 | 60.6949 | -61.908
260.3125 | 122.7448 | -60.8139 | 61.7935 | 0.022278 | 0.010361 | 0.0033752 | 0.0053321 | -6.6248e-05 | -0.006116 | -0.0054475 | 0.10963 | -0.0093503 | -0.0034756 | -0.00090781 | 0.00090353 | -0.0028988 | 0.009155 | 0.045776 | 0.054932 | 0.004578 | 0.059509 | 0.050354 | -0.10986 | 0.086975 | 0.12817 | 0 | 0.041199 | 0.036621 | 0.009155 | -0.073242 | 60.8643 | 60.704 | -61.734 | 60.8597 | 60.8185 | 0.11444 | -61.7844 | 60.8231 | 60.7407 | -61.7523 | 60.9009 | 60.8139 | 0.073242 | -61.7569 | 60.8734 | 60.8231 | 60.8688 | -61.9034 | 60.8551 | 60.8505 | 60.9421 | -61.8668
262.0312 | 122.8271 | -60.7636 | 61.7752 | -0.18372 | 0.014206 | 0.0023072 | 0.0040503 | -0.0022024 | -0.0012028 | -0.0043793 | -0.20317 | -0.0057187 | -0.0056118 | 0.00058739 | 0.0017581 | -0.0065304 | 0.07782 | 0.050354 | 0.045776 | 0.050354 | 0.16479 | 0.068665 | -0.068665 | 0.064087 | 0.13275 | -0.036621 | 0.13733 | 0.10986 | 0.013733 | -0.059509 | 60.8322 | 60.6949 | -61.6104 | 60.8139 | 60.8139 | 0.11902 | -61.6974 | 60.7773 | 60.704 | -61.6379 | 60.8276 | 60.7269 | 0.022888 | -61.6653 | 60.9283 | 60.8414 | 60.8093 | -61.8439 | 60.9009 | 60.8734 | 60.8963 | -61.8347
263.7031 | 122.7356 | -60.8139 | 61.7981 | 0.19012 | 0.011429 | 0.001239 | 0.0017005 | -0.004125 | -0.00013458 | -0.0018159 | 0.19356 | -0.0063595 | -0.0036892 | -5.3406e-05 | 0.0056033 | -0.0058896 | 0.022888 | 0.004578 | 0.022888 | -0.022888 | -0.041199 | -0.041199 | -0.15564 | 0.086975 | 0.068665 | -0.027466 | -0.041199 | -0.045776 | -0.054932 | -0.10529 | 60.7727 | 60.6583 | -61.8393 | 60.8185 | 60.791 | 0.13275 | -61.7752 | 60.759 | 60.7086 | -61.8393 | 60.9009 | 60.7864 | 0.07782 | -61.8439 | 60.7727 | 60.8368 | 60.8368 | -61.9537 | 60.7727 | 60.7681 | 60.8826 | -61.9034
265.3594 | 122.7448 | -60.8139 | 61.7981 | -0.061646 | 0.014633 | 0.0014526 | 0.0021277 | -0.0045522 | 0.0032834 | -0.0024567 | -0.081101 | -0.0023007 | -0.0011258 | 0.0018692 | 0.0043215 | -0.0082394 | 0.036621 | -0.022888 | -0.009155 | -0.032043 | 0.091553 | 0.004578 | -0.13275 | 0 | -0.041199 | -0.1236 | 0.013733 | 0.022888 | -0.064087 | -0.12817 | 60.8185 | 60.6812 | -61.7065 | 60.791 | 60.7819 | 0.10071 | -61.7615 | 60.7498 | 60.6857 | -61.7844 | 60.8139 | 60.6903 | 0.004578 | -61.7752 | 60.9055 | 60.8505 | 60.8047 | -61.9308 | 60.8276 | 60.8368 | 60.7727 | -61.9263
267.0312 | 122.7402 | -60.8139 | 61.7935 | -0.0082397 | 0.015274 | 0.0033752 | 0.0021277 | -0.0039114 | 0.0032834 | -0.00074767 | 0.018082 | -0.0050777 | -0.0043302 | 0.0033646 | 0.0036807 | -0.0063168 | -0.013733 | -0.054932 | -0.045776 | -0.054932 | 0.054932 | -0.018311 | -0.13733 | -0.041199 | -0.086975 | -0.16022 | 0.018311 | 0.022888 | -0.09613 | -0.12817 | 60.7956 | 60.6766 | -61.7386 | 60.759 | 60.759 | 0.082397 | -61.8073 | 60.7178 | 60.6857 | -61.7752 | 60.7727 | 60.6537 | -0.032043 | -61.7706 | 60.8688 | 60.8002 | 60.7681 | -61.9308 | 60.8322 | 60.8368 | 60.7269 | -61.9217
268.6875 | 122.8592 | -60.7636 | 61.7386 | -0.12268 | 0.0097199 | 0.0035888 | 0.0091773 | -0.0017752 | -0.0069706 | -0.0024567 | -0.050583 | -0.0059323 | -0.0019802 | -0.00069421 | -0.0020871 | -0.0052488 | 0.1236 | 0.18768 | 0.1831 | 0.091553 | 0.10071 | 0.082397 | -0.050354 | 0.1831 | 0.30212 | 0.091553 | 0.068665 | 0.059509 | 0.041199 | -0.022888 | 60.8459 | 60.7132 | -61.6379 | 60.9512 | 60.8551 | 0.14191 | -61.615 | 60.8047 | 60.7407 | -61.6699 | 60.9467 | 60.8551 | 0.11444 | -61.6791 | 60.8643 | 60.8871 | 60.9467 | -61.7889 | 60.8322 | 60.8231 | 61.0657 | -61.7615
270.375 | 122.85 | -60.7727 | 61.7569 | -0.015869 | 0.012283 | 0.0040162 | 0.0059729 | -0.0039114 | -0.0054752 | -0.0045929 | 0.04097 | -0.0067867 | -0.0034756 | -0.00090781 | 0.0013309 | -0.005035 | 0.036621 | 0.054932 | 0.07782 | 0.041199 | 0.082397 | 0.059509 | -0.082397 | 0.13733 | 0.21515 | 0.050354 | 0.054932 | 0.032043 | 0.004578 | -0.036621 | 60.8322 | 60.6903 | -61.6745 | 60.8276 | 60.8139 | 0.1236 | -61.7203 | 60.7773 | 60.7361 | -61.702 | 60.91 | 60.8231 | 0.086975 | -61.7249 | 60.8551 | 60.8093 | 60.8505 | -61.8393 | 60.8276 | 60.8047 | 60.9879 | -61.7935
272.0469 | 122.8134 | -60.7773 | 61.7798 | -0.084534 | 0.013992 | 0.0018798 | 0.0027685 | -0.0051932 | 0.0032834 | -0.0030975 | -0.11925 | -0.0037961 | -0.0043302 | -0.00026701 | 0.0045351 | -0.0082394 | 0.086975 | 0.013733 | 0.022888 | 0.004578 | 0.082397 | 0.009155 | -0.10986 | 0.059509 | 0.004578 | -0.073242 | 0.064087 | 0.022888 | -0.054932 | -0.10071 | 60.7864 | 60.6674 | -61.6974 | 60.791 | 60.7819 | 0.11444 | -61.6928 | 60.7224 | 60.6766 | -61.7157 | 60.8368 | 60.704 | 0.027466 | -61.7569 | 60.8597 | 60.8643 | 60.8002 | -61.8896 | 60.8414 | 60.8002 | 60.7819 | -61.8805
273.7031 | 122.7631 | -60.791 | 61.7569 | 0.037537 | 0.010147 | 0.0055114 | 0.00063232 | -0.0022024 | -0.006116 | -0.0058747 | 0.086746 | -0.0067867 | -0.0047574 | -5.3406e-05 | 0.0015445 | -0.005676 | 0.018311 | 0.032043 | 0.059509 | 0.013733 | 0.054932 | 0.041199 | -0.091553 | 0.082397 | 0.14191 | -0.004578 | 0.054932 | 0.045776 | -0.018311 | -0.068665 | 60.8322 | 60.6995 | -61.702 | 60.8231 | 60.8047 | 0.10529 | -61.7386 | 60.7727 | 60.7224 | -61.702 | 60.8734 | 60.7864 | 0.064087 | -61.7111 | 60.8459 | 60.8093 | 60.8505 | -61.8484 | 60.8459 | 60.8368 | 60.9329 | -61.8256
275.3906 | 122.8226 | -60.7864 | 61.7615 | -0.19135 | 0.011643 | 0.0044434 | 0.0064001 | -0.0034842 | -0.0018436 | -0.0048065 | -0.24132 | -0.0074277 | -0.0051846 | -0.00069421 | 4.9132e-05 | -0.0061032 | 0.13275 | 0.13733 | 0.13733 | 0.11444 | 0.12817 | 0.09613 | -0.054932 | 0.1236 | 0.21973 | 0.027466 | 0.10071 | 0.091553 | 0.032043 | -0.041199 | 60.8826 | 60.7315 | -61.6333 | 60.9238 | 60.9009 | 0.16937 | -61.6287 | 60.8185 | 60.7452 | -61.6608 | 60.91 | 60.8139 | 0.068665 | -61.6699 | 60.9146 | 60.9192 | 60.9238 | -61.8164 | 60.8871 | 60.878 | 61.0062 | -61.8027
277.0625 | 122.7264 | -60.8231 | 61.7935 | 0.0070193 | 0.016342 | 0.002948 | 0.0023413 | -0.0011342 | 0.0028562 | -0.0030975 | 0.0028229 | -0.0048641 | -0.0056118 | 0.00037379 | 0.0066715 | -0.0082394 | -0.018311 | -0.059509 | -0.054932 | -0.064087 | 0.068665 | -0.022888 | -0.16937 | -0.027466 | -0.10071 | -0.15564 | 0.041199 | 0.009155 | -0.09613 | -0.13275 | 60.8002 | 60.6537 | -61.7249 | 60.7636 | 60.759 | 0.10529 | -61.8118 | 60.7269 | 60.6903 | -61.7523 | 60.7956 | 60.6674 | -0.022889 | -61.7844 | 60.8917 | 60.8047 | 60.7681 | -61.9629 | 60.8643 | 60.8322 | 60.7224 | -61.9263
278.7344 | 122.7402 | -60.8002 | 61.7706 | 0.11383 | 0.012497 | 0.0033752 | 0.0038367 | -0.0071158 | -0.0048344 | -0.0013885 | 0.12489 | -0.0061459 | -0.003262 | 0.00016019 | -0.0012327 | -0.0031124 | 0.036621 | 0.036621 | 0.045776 | -0.013733 | 0.013733 | 0.018311 | -0.10529 | 0.09613 | 0.09613 | -0.009155 | 0.027466 | 0.027466 | -0.009155 | -0.054932 | 60.8185 | 60.6949 | -61.7569 | 60.8368 | 60.7864 | 0.091553 | -61.734 | 60.791 | 60.7452 | -61.7432 | 60.8963 | 60.791 | 0.045777 | -61.7432 | 60.8139 | 60.8368 | 60.8459 | -61.8759 | 60.8276 | 60.8276 | 60.8963 | -61.8256
280.4531 | 122.7768 | -60.8093 | 61.7706 | 0.11383 | 0.011215 | 0.0035888 | -0.00064948 | -0.0017752 | -0.00056178 | -0.0039521 | 0.20119 | -0.0063595 | -0.0053982 | 0.0010148 | 0.0045351 | -0.0078122 | 0.036621 | -0.009155 | 0.013733 | -0.004578 | -0.009155 | -0.027466 | -0.14648 | 0.068665 | 0.027466 | -0.036621 | -0.036621 | -0.050354 | -0.064087 | -0.11902 | 60.7819 | 60.6628 | -61.7798 | 60.8002 | 60.8047 | 0.14191 | -61.734 | 60.7452 | 60.6903 | -61.8073 | 60.878 | 60.7727 | 0.082398 | -61.821 | 60.8002 | 60.8459 | 60.8231 | -61.9171 | 60.7727 | 60.759 | 60.8368 | -61.8896
282.125 | 122.7493 | -60.7864 | 61.8256 | 0.037537 | 0.013565 | 0.0040162 | 0.0021277 | -0.0026296 | 0.0037106 | -0.0018159 | -0.0048066 | -0.0040097 | -0.0047574 | 0.0016556 | 0.0043215 | -0.0054624 | -0.009155 | -0.07782 | -0.068665 | -0.073242 | 0.07782 | -0.009155 | -0.16937 | -0.022888 | -0.10529 | -0.15564 | 0.041199 | 0.018311 | -0.082397 | -0.14191 | 60.7773 | 60.6171 | -61.7477 | 60.7086 | 60.7132 | 0.096131 | -61.8347 | 60.704 | 60.6445 | -61.7844 | 60.7635 | 60.6308 | -0.013733 | -61.8073 | 60.8643 | 60.7773 | 60.7178 | -61.9949 | 60.8276 | 60.8047 | 60.6812 | -61.9675
283.7969 | 122.8409 | -60.7636 | 61.7569 | -0.19897 | 0.011429 | 0.0027344 | 0.0074683 | -0.0028432 | -0.004407 | -0.0039521 | -0.11925 | -0.0084957 | -0.0030484 | -0.001976 | -0.00080527 | -0.006744 | 0.14191 | 0.18768 | 0.18768 | 0.1236 | 0.1236 | 0.10071 | -0.022888 | 0.16937 | 0.30212 | 0.09613 | 0.068665 | 0.064087 | 0.036621 | -0.013733 | 60.8643 | 60.7407 | -61.6333 | 60.9512 | 60.8871 | 0.14648 | -61.615 | 60.8002 | 60.7498 | -61.6882 | 60.9329 | 60.8597 | 0.10986 | -61.6928 | 60.8871 | 60.9055 | 60.9512 | -61.7798 | 60.8322 | 60.8276 | 61.0657 | -61.7706
285.5 | 122.7264 | -60.8231 | 61.8073 | 0.15961 | 0.012924 | 0.002948 | 0.0012731 | -6.6248e-05 | -0.0014164 | -0.0037385 | 0.14015 | -0.0067867 | -0.0056118 | -0.0011216 | 0.0026125 | -0.0058896 | 0.045776 | 0.036621 | 0.054932 | -0.009155 | -0.004578 | -0.009155 | -0.14648 | 0.10071 | 0.082397 | -0.013733 | -0.009155 | -0.032043 | -0.050354 | -0.10071 | 60.8139 | 60.6766 | -61.8118 | 60.8597 | 60.8139 | 0.13733 | -61.7615 | 60.7727 | 60.7224 | -61.8164 | 60.9238 | 60.8093 | 0.086975 | -61.8393 | 60.8185 | 60.8688 | 60.878 | -61.9537 | 60.8139 | 60.791 | 60.9055 | -61.908
287.1719 | 122.8592 | -60.7773 | 61.7477 | 0.0070193 | 0.012497 | 0.0025208 | 0.011314 | -0.0032706 | -0.004407 | -0.0037385 | -0.0048066 | -0.0070003 | -0.0041164 | -0.0013352 | -0.0014463 | -0.005676 | 0.050354 | 0.041199 | 0.050354 | 0.041199 | 0.073242 | 0.059509 | -0.07782 | 0.1236 | 0.19226 | 0.041199 | 0.054932 | 0.041199 | 0.013733 | -0.045776 | 60.8368 | 60.6995 | -61.6745 | 60.8185 | 60.8185 | 0.11902 | -61.6974 | 60.791 | 60.7315 | -61.6928 | 60.9009 | 60.8185 | 0.086975 | -61.7065 | 60.8505 | 60.8276 | 60.8276 | -61.8256 | 60.8322 | 60.8185 | 60.9695 | -61.7935
288.8438 | 122.8546 | -60.759 | 61.7706 | -0.13031 | 0.01442 | 0.0033752 | 0.00063232 | -0.0028432 | 0.0013608 | -0.0035249 | -0.18028 | -0.0027279 | -0.0047574 | 0.00058739 | 0.0053897 | -0.0095212 | 0.073242 | 0.027466 | 0.018311 | 0.013733 | 0.1236 | 0.022888 | -0.11902 | 0.073242 | 0.045776 | -0.045776 | 0.054932 | 0.036621 | -0.032043 | -0.10529 | 60.7819 | 60.64 | -61.647 | 60.7864 | 60.7727 | 0.13275 | -61.6974 | 60.7269 | 60.6537 | -61.7157 | 60.8322 | 60.7132 | 0.05951 | -61.734 | 60.8826 | 60.8322 | 60.7773 | -61.8896 | 60.8139 | 60.7956 | 60.8047 | -61.8759
290.5156 | 122.7402 | -60.8047 | 61.7661 | 0.090942 | 0.011002 | 0.0023072 | 0.0034093 | -0.0030568 | -0.0039798 | -0.0054475 | 0.11726 | -0.0067867 | -0.0026212 | -0.0017624 | -0.00016447 | -0.0052488 | 0.041199 | 0.045776 | 0.059509 | 0 | 0.032043 | 0.004578 | -0.11902 | 0.091553 | 0.11902 | -0.018311 | 0.036621 | 0.018311 | -0.018311 | -0.068665 | 60.8093 | 60.6857 | -61.734 | 60.8505 | 60.8047 | 0.11902 | -61.7249 | 60.7864 | 60.7361 | -61.7294 | 60.8963 | 60.7864 | 0.050354 | -61.7477 | 60.8368 | 60.8459 | 60.8643 | -61.8851 | 60.8414 | 60.8231 | 60.9238 | -61.8347
292.2031 | 122.7264 | -60.791 | 61.7889 | 0.12909 | 0.011002 | 0.0010254 | 0.0049047 | -0.001348 | -0.0014164 | -0.0041657 | 0.17067 | -0.0076413 | -0.003262 | -0.0011216 | 0.0028263 | -0.005035 | 0.032043 | 0.036621 | 0.07782 | -0.013733 | 0 | -0.032043 | -0.13733 | 0.091553 | 0.064087 | -0.027466 | 0.009155 | -0.036621 | -0.068665 | -0.09613 | 60.759 | 60.6537 | -61.7889 | 60.8276 | 60.7773 | 0.1236 | -61.7569 | 60.7224 | 60.6949 | -61.7798 | 60.8826 | 60.7636 | 0.068664 | -61.8256 | 60.791 | 60.8231 | 60.8688 | -61.9263 | 60.8002 | 60.7544 | 60.8551 | -61.8851
293.875 | 122.8592 | -60.759 | 61.7432 | -0.19135 | 0.012924 | 0.0023072 | 0.0010595 | -0.00092065 | 0.0032834 | -0.0022431 | -0.20317 | -0.0042233 | -0.0041164 | -0.00090781 | 0.0041079 | -0.0063168 | 0.073242 | 0.036621 | 0.041199 | 0.054932 | 0.15564 | 0.07782 | -0.07782 | 0.045776 | 0.064087 | -0.064087 | 0.09613 | 0.045776 | -0.018311 | -0.09613 | 60.8368 | 60.6812 | -61.5875 | 60.7956 | 60.8139 | 0.13275 | -61.6699 | 60.7407 | 60.6628 | -61.647 | 60.8047 | 60.6949 | 0.032043 | -61.6974 | 60.9146 | 60.8322 | 60.8002 | -61.821 | 60.8551 | 60.8047 | 60.8231 | -61.8393
295.5469 | 122.7539 | -60.8231 | 61.7752 | 0.15961 | 0.013779 | 0.0023072 | 0.0021277 | -0.0043386 | -0.00077538 | -0.0018159 | 0.19356 | -0.0063595 | -0.0047574 | 0.00037379 | 0.0043215 | -0.0054624 | 0.022888 | 0.022888 | 0.027466 | -0.032043 | -0.027466 | -0.027466 | -0.15564 | 0.086975 | 0.045776 | -0.041199 | -0.036621 | -0.064087 | -0.073242 | -0.1236 | 60.7956 | 60.6674 | -61.8027 | 60.8459 | 60.791 | 0.1236 | -61.7523 | 60.7498 | 60.6995 | -61.8118 | 60.91 | 60.7819 | 0.082397 | -61.8393 | 60.7956 | 60.8459 | 60.8505 | -61.9308 | 60.7864 | 60.759 | 60.8688 | -61.8988
297.2344 | 122.85 | -60.7727 | 61.7981 | -0.061646 | 0.017197 | 0.0023072 | 0.0070409 | -0.0032706 | 0.003497 | -0.0011749 | -0.15739 | -0.0050777 | -0.0011258 | -0.0013352 | 0.0032535 | -0.0082394 | 0.068665 | 0.027466 | 0.036621 | 0.009155 | 0.10071 | 0.009155 | -0.12817 | 0.073242 | 0.041199 | -0.068665 | 0.059509 | 0.036621 | -0.050354 | -0.11444 | 60.7819 | 60.6445 | -61.6974 | 60.8002 | 60.7819 | 0.13733 | -61.7294 | 60.7224 | 60.6583 | -61.7386 | 60.8459 | 60.704 | 0.045776 | -61.7615 | 60.8734 | 60.8414 | 60.8093 | -61.9263 | 60.8322 | 60.8093 | 60.8139 | -61.9125
298.9375 | 122.7631 | -60.8047 | 61.7889 | 0.12146 | 0.014206 | 0.001239 | 0.0023413 | -0.004125 | 0.0026424 | -0.0018159 | 0.063858 | -0.0048641 | -0.0039028 | 0.0010148 | 0.0032535 | -0.0065304 | -0.059509 | -0.11444 | -0.10986 | -0.091553 | 0.013733 | -0.064087 | -0.18768 | -0.009155 | -0.10986 | -0.15564 | 0.041199 | -0.004578 | -0.10071 | -0.12817 | 60.7407 | 60.6171 | -61.7752 | 60.6903 | 60.7132 | 0.09613 | -61.8484 | 60.704 | 60.6766 | -61.7477 | 60.7956 | 60.6491 | -0.027466 | -61.7935 | 60.8185 | 60.7452 | 60.6949 | -61.9766 | 60.8459 | 60.8002 | 60.6949 | -61.9171
300.5938 | 122.8592 | -60.7498 | 61.7477 | -0.12268 | 0.013138 | 0.0010254 | 0.0078955 | -0.0034842 | -0.0069706 | -0.0028839 | -0.081101 | -0.0059323 | -0.0030484 | -0.00048061 | -0.00080527 | -0.0048214 | 0.14191 | 0.18768 | 0.16479 | 0.11444 | 0.10071 | 0.09613 | -0.041199 | 0.19684 | 0.29755 | 0.11444 | 0.07782 | 0.054932 | 0.032043 | -0.022888 | 60.8459 | 60.7086 | -61.647 | 60.9375 | 60.8643 | 0.15564 | -61.6058 | 60.7819 | 60.7269 | -61.6699 | 60.9467 | 60.8643 | 0.13733 | -61.6928 | 60.8505 | 60.8917 | 60.9146 | -61.7889 | 60.8276 | 60.8047 | 61.0474 | -61.7706
302.2656 | 122.8683 | -60.7681 | 61.7706 | -0.23712 | 0.014633 | 0.0020936 | 0.0055457 | -0.001348 | 0.00071982 | -0.0067291 | -0.20317 | -0.0040097 | -0.0019802 | 0.0020828 | 0.0019717 | -0.0078122 | 0.068665 | 0.036621 | 0.032043 | 0.054932 | 0.1831 | 0.073242 | -0.054932 | 0.050354 | 0.082397 | -0.082397 | 0.1236 | 0.082397 | -0.009155 | -0.068665 | 60.8414 | 60.7132 | -61.5875 | 60.8047 | 60.8231 | 0.10986 | -61.702 | 60.759 | 60.6995 | -61.647 | 60.8185 | 60.6857 | -0.013732 | -61.6882 | 60.9512 | 60.8368 | 60.8002 | -61.8256 | 60.8917 | 60.8505 | 60.8505 | -61.8393
303.9844 | 122.8592 | -60.759 | 61.7798 | -0.099793 | 0.016769 | 0.00081179 | 0.0029821 | -0.0049796 | 0.003497 | -0.0030975 | -0.14214 | -0.0048641 | -0.0039028 | 0.00037379 | 0.0028263 | -0.006744 | 0.068665 | 0.013733 | 0.009155 | 0.032043 | 0.10986 | 0.018311 | -0.11902 | 0.064087 | 0.050354 | -0.059509 | 0.045776 | 0.041199 | -0.050354 | -0.10529 | 60.7773 | 60.64 | -61.6699 | 60.7727 | 60.791 | 0.15106 | -61.7111 | 60.7086 | 60.6537 | -61.734 | 60.8231 | 60.6995 | 0.045777 | -61.7386 | 60.8688 | 60.8276 | 60.7681 | -61.8988 | 60.8047 | 60.8002 | 60.8093 | -61.8851
305.6562 | 122.7264 | -60.8139 | 61.7844 | 0.068054 | 0.012924 | 0.0033752 | 0.0046911 | -0.0039114 | -0.005048 | -0.0033111 | 0.14015 | -0.0070003 | -0.0028348 | -0.001976 | 0.0019717 | -0.005035 | 0.009155 | 0.041199 | 0.059509 | -0.018311 | 0.050354 | 0.013733 | -0.11902 | 0.07782 | 0.11902 | -0.018311 | 0.022888 | 0.022888 | -0.027466 | -0.059509 | 60.8276 | 60.6949 | -61.734 | 60.8551 | 60.7956 | 0.10071 | -61.7752 | 60.7864 | 60.7544 | -61.7615 | 60.8917 | 60.7956 | 0.041198 | -61.7615 | 60.8643 | 60.8231 | 60.8734 | -61.9034 | 60.8368 | 60.8368 | 60.9329 | -61.8439
307.3438 | 122.8638 | -60.7361 | 61.7432 | -0.092163 | 0.015915 | 0.0052978 | 0.0034093 | -0.0019888 | -0.003339 | -0.0056611 | -0.065842 | -0.0057187 | -0.0021938 | 0.00016019 | -0.0014463 | -0.006744 | 0.13733 | 0.19684 | 0.16022 | 0.11444 | 0.10529 | 0.09613 | -0.027466 | 0.18768 | 0.29755 | 0.10071 | 0.082397 | 0.059509 | 0.022888 | -0.027466 | 60.8322 | 60.7086 | -61.6379 | 60.9329 | 60.8505 | 0.14191 | -61.6058 | 60.759 | 60.7086 | -61.6608 | 60.9238 | 60.8368 | 0.12817 | -61.6837 | 60.8414 | 60.8734 | 60.8963 | -61.7706 | 60.8185 | 60.7956 | 61.0336 | -61.7706
309.0469 | 122.7493 | -60.7773 | 61.8027 | 0.075684 | 0.013352 | 0.0038024 | 0.0012731 | -0.0032706 | 0.0043514 | -0.0024567 | 0.025711 | -0.0037961 | -0.0043302 | 0.00080099 | 0.0070987 | -0.0065304 | -0.054932 | -0.11902 | -0.10986 | -0.091553 | 0.068665 | -0.036621 | -0.16937 | -0.036621 | -0.1236 | -0.16479 | 0.036621 | 0.013733 | -0.10071 | -0.16479 | 60.7407 | 60.6079 | -61.734 | 60.6583 | 60.6857 | 0.07782 | -61.8576 | 60.6766 | 60.6125 | -61.7661 | 60.7407 | 60.6125 | 0 | -61.7889 | 60.8459 | 60.7224 | 60.6674 | -61.972 | 60.8139 | 60.791 | 60.6537 | -61.9675
310.7188 | 122.8546 | -60.759 | 61.7523 | -0.0082397 | 0.01207 | 0.0027344 | 0.0096045 | -0.0028432 | -0.0048344 | -0.0052337 | 0.03334 | -0.0067867 | -0.0011258 | 0.00058739 | -0.0016599 | -0.0061032 | 0.041199 | 0.073242 | 0.073242 | 0.027466 | 0.086975 | 0.032043 | -0.091553 | 0.1236 | 0.19226 | 0.036621 | 0.050354 | 0.032043 | 0.009155 | -0.059509 | 60.791 | 60.6674 | -61.6653 | 60.8322 | 60.7864 | 0.11902 | -61.7111 | 60.7681 | 60.6995 | -61.702 | 60.8826 | 60.7956 | 0.09613 | -61.7203 | 60.8459 | 60.8002 | 60.8322 | -61.8439 | 60.8093 | 60.791 | 60.9512 | -61.8118
312.4219 | 122.8226 | -60.7819 | 61.7615 | -0.19135 | 0.013779 | 0.0031616 | 0.0051183 | -0.0066884 | -0.0029118 | -0.0041657 | -0.11925 | -0.0067867 | -0.0019802 | 0.00080099 | 0.0023989 | -0.0071714 | 0.14191 | 0.16937 | 0.16937 | 0.11444 | 0.11444 | 0.09613 | -0.045776 | 0.16479 | 0.27924 | 0.068665 | 0.068665 | 0.050354 | 0.027466 | -0.045776 | 60.878 | 60.7361 | -61.647 | 60.9512 | 60.8963 | 0.16022 | -61.6196 | 60.8093 | 60.7361 | -61.6928 | 60.9467 | 60.8505 | 0.11444 | -61.7111 | 60.8963 | 60.9238 | 60.9512 | -61.8073 | 60.8505 | 60.8322 | 61.0611 | -61.8073
314.1094 | 122.7997 | -60.8047 | 61.7798 | 0.17487 | 0.012283 | 0.0038024 | -0.0012903 | -0.0017752 | 0.0024288 | -0.0020295 | 0.13252 | -0.0050777 | -0.004971 | -0.00026701 | 0.0060305 | -0.0071714 | 0.027466 | 0.013733 | 0 | -0.013733 | -0.004578 | 0 | -0.15106 | 0.082397 | 0.032043 | -0.036621 | -0.018311 | -0.032043 | -0.054932 | -0.11444 | 60.8047 | 60.6537 | -61.7844 | 60.8185 | 60.791 | 0.13733 | -61.7523 | 60.7498 | 60.6903 | -61.7981 | 60.8871 | 60.7681 | 0.07782 | -61.8118 | 60.8002 | 60.8322 | 60.8047 | -61.9308 | 60.7864 | 60.7727 | 60.8368 | -61.8942
315.7656 | 122.8683 | -60.7498 | 61.7661 | -0.23712 | 0.01442 | 0.0027344 | 0.0044775 | -0.0043386 | 0.0022152 | -0.0030975 | -0.19554 | -0.0050777 | -0.0024076 | 0.00080099 | 0.0026125 | -0.010162 | 0.091553 | 0.050354 | 0.036621 | 0.064087 | 0.14191 | 0.064087 | -0.073242 | 0.050354 | 0.050354 | -0.068665 | 0.068665 | 0.059509 | -0.050354 | -0.10986 | 60.8139 | 60.6766 | -61.6241 | 60.8002 | 60.8139 | 0.13733 | -61.6745 | 60.6995 | 60.64 | -61.6974 | 60.8002 | 60.6812 | 0.041198 | -61.7065 | 60.8917 | 60.8414 | 60.7864 | -61.8393 | 60.8185 | 60.8093 | 60.8002 | -61.8759
317.4375 | 122.8271 | -60.7819 | 61.7569 | -0.23712 | 0.013138 | 0.0025208 | 0.0083227 | -0.001348 | -0.00163 | -0.0037385 | -0.19554 | -0.0059323 | -0.00069863 | 0.001442 | 0.00026273 | -0.0061032 | 0.064087 | 0.07782 | 0.064087 | 0.054932 | 0.15564 | 0.07782 | -0.068665 | 0.068665 | 0.13275 | -0.013733 | 0.12817 | 0.1236 | 0.009155 | -0.068665 | 60.8597 | 60.7132 | -61.6013 | 60.8597 | 60.8368 | 0.1236 | -61.6928 | 60.791 | 60.7132 | -61.6287 | 60.8505 | 60.7681 | 0.054932 | -61.6333 | 60.9375 | 60.8459 | 60.8459 | -61.8256 | 60.91 | 60.9055 | 60.9146 | -61.8256
319.1094 | 122.8638 | -60.7636 | 61.7523 | -0.023499 | 0.013352 | 0.0016662 | 0.0057593 | -0.004125 | -0.0063296 | -0.0054475 | -0.0048066 | -0.0052915 | -0.0021938 | -5.3406e-05 | -0.0010191 | -0.0078122 | 0.059509 | 0.082397 | 0.091553 | 0.064087 | 0.082397 | 0.050354 | -0.073242 | 0.15106 | 0.23804 | 0.07782 | 0.068665 | 0.045776 | 0.032043 | -0.054932 | 60.8139 | 60.6903 | -61.6699 | 60.8459 | 60.8276 | 0.13733 | -61.6928 | 60.7956 | 60.7086 | -61.6837 | 60.9146 | 60.8414 | 0.13275 | -61.7065 | 60.8459 | 60.8231 | 60.8551 | -61.8256 | 60.8322 | 60.8093 | 61.0016 | -61.8073
320.7812 | 122.7631 | -60.7819 | 61.7935 | -0.061646 | 0.015701 | 0.002948 | -0.00086308 | -0.0028432 | 0.0032834 | -0.0039521 | -0.11162 | -0.0046505 | -0.0053982 | -0.00026701 | 0.0060305 | -0.008453 | 0.068665 | 0.018311 | 0.004578 | 0.004578 | 0.07782 | 0.013733 | -0.11444 | 0.045776 | -0.013733 | -0.086975 | 0.050354 | 0.027466 | -0.064087 | -0.1236 | 60.7956 | 60.6674 | -61.7157 | 60.8002 | 60.7864 | 0.11902 | -61.7249 | 60.7178 | 60.6583 | -61.7432 | 60.8276 | 60.6949 | 0.036621 | -61.7661 | 60.8597 | 60.8505 | 60.7864 | -61.908 | 60.8322 | 60.8093 | 60.7681 | -61.9171
322.4531 | 122.7722 | -60.7681 | 61.7935 | 0.037537 | 0.011643 | 0.0038024 | 0.0059729 | -0.0045522 | -0.006116 | -0.0033111 | 0.086746 | -0.0061459 | -0.0034756 | 0.00080099 | -0.00059167 | -0.0048214 | 0.009155 | 0.036621 | 0.054932 | 0.022888 | 0.082397 | 0.050354 | -0.068665 | 0.086975 | 0.14191 | 0 | 0.054932 | 0.018311 | -0.018311 | -0.091553 | 60.8185 | 60.6995 | -61.7111 | 60.8047 | 60.791 | 0.091553 | -61.7844 | 60.7498 | 60.6766 | -61.7386 | 60.8551 | 60.7681 | 0.091553 | -61.7752 | 60.8505 | 60.7773 | 60.8231 | -61.8622 | 60.8231 | 60.7864 | 60.91 | -61.8851
324.125 | 122.7768 | -60.7819 | 61.7752 | 0.12909 | 0.012924 | 0.0040162 | 0.0012731 | -0.0036978 | 0.0028562 | -0.0041657 | 0.063858 | -0.0029415 | -0.0053982 | -0.0013352 | 0.0053897 | -0.0054624 | -0.054932 | -0.09613 | -0.10529 | -0.073242 | 0.036621 | -0.036621 | -0.19684 | -0.013733 | -0.10986 | -0.13733 | 0.041199 | 0.022888 | -0.091553 | -0.16022 | 60.7452 | 60.585 | -61.7386 | 60.6857 | 60.7086 | 0.1236 | -61.8301 | 60.6903 | 60.6216 | -61.734 | 60.7681 | 60.6445 | 0.022888 | -61.7523 | 60.8185 | 60.7269 | 60.6766 | -61.972 | 60.8231 | 60.8047 | 60.672 | -61.9354
325.7812 | 122.8546 | -60.7498 | 61.7798 | -0.25238 | 0.017838 | 0.002948 | 0.0068273 | -0.0017752 | -0.0014164 | -0.0045929 | -0.21843 | -0.0046505 | -0.0013394 | 0.00080099 | 0.0011173 | -0.0065304 | 0.064087 | 0.064087 | 0.045776 | 0.059509 | 0.19226 | 0.07782 | -0.036621 | 0.059509 | 0.091553 | -0.045776 | 0.13275 | 0.10071 | 0 | -0.059509 | 60.8276 | 60.7132 | -61.5875 | 60.8139 | 60.8093 | 0.09613 | -61.7157 | 60.7498 | 60.6903 | -61.647 | 60.8093 | 60.704 | 0.013733 | -61.6791 | 60.9421 | 60.8139 | 60.7956 | -61.8164 | 60.8826 | 60.8505 | 60.8414 | -61.8393
327.4531 | 122.7768 | -60.8231 | 61.7706 | 0.12909 | 0.01442 | 0.0020936 | 0.0023413 | -0.0047658 | -0.00163 | -0.0024567 | 0.19356 | -0.0065731 | -0.0051846 | -0.0017624 | 0.0043215 | -0.0075986 | 0.022888 | 0.032043 | 0.009155 | -0.009155 | -0.009155 | -0.022888 | -0.16937 | 0.082397 | 0.041199 | -0.036621 | -0.009155 | -0.036621 | -0.059509 | -0.1236 | 60.8002 | 60.6537 | -61.7798 | 60.8551 | 60.8139 | 0.16022 | -61.7477 | 60.7636 | 60.6995 | -61.7798 | 60.9055 | 60.7864 | 0.086975 | -61.8073 | 60.8139 | 60.8459 | 60.8322 | -61.94 | 60.8139 | 60.7864 | 60.8643 | -61.8942
329.125 | 122.85 | -60.7636 | 61.7386 | 0.0070193 | 0.013352 | 0.0038024 | 0.0074683 | -0.0030568 | -0.0056888 | -0.0058747 | 0.03334 | -0.0067867 | -0.001553 | -5.3406e-05 | -0.0031553 | -0.0071714 | 0.022888 | 0.054932 | 0.064087 | 0.036621 | 0.086975 | 0.041199 | -0.086975 | 0.10986 | 0.18768 | 0.032043 | 0.059509 | 0.041199 | 0.004578 | -0.10071 | 60.8047 | 60.6766 | -61.6516 | 60.8185 | 60.8002 | 0.1236 | -61.7157 | 60.7681 | 60.6628 | -61.6791 | 60.8734 | 60.7956 | 0.13275 | -61.6974 | 60.8505 | 60.7864 | 60.8276 | -61.8256 | 60.8231 | 60.8047 | 60.9512 | -61.8393
330.7969 | 122.7402 | -60.7956 | 61.8027 | 0.060425 | 0.014206 | 0.0042298 | -0.00086308 | -0.0032706 | 0.0049924 | -0.00053407 | -0.0048066 | -0.0040097 | -0.0058254 | 0.00251 | 0.0053897 | -0.0063168 | -0.004578 | -0.054932 | -0.041199 | -0.050354 | 0.068665 | -0.022888 | -0.15106 | -0.045776 | -0.09613 | -0.14648 | 0.032043 | 0.004578 | -0.082397 | -0.14648 | 60.7727 | 60.6445 | -61.734 | 60.7407 | 60.7452 | 0.10071 | -61.8073 | 60.7132 | 60.6491 | -61.7706 | 60.7498 | 60.6491 | 0 | -61.7981 | 60.8643 | 60.791 | 60.7544 | -61.9537 | 60.8276 | 60.8002 | 60.6995 | -61.9492
332.4688 | 122.818 | -60.7773 | 61.7706 | -0.18372 | 0.015274 | 0.0025208 | 0.0076819 | -0.002416 | -0.0039798 | -0.0043793 | -0.18791 | -0.0072141 | -0.003262 | -0.00090781 | -0.00059167 | -0.0061032 | 0.12817 | 0.15106 | 0.13733 | 0.11444 | 0.10071 | 0.10529 | -0.050354 | 0.13275 | 0.24261 | 0.050354 | 0.11902 | 0.082397 | 0.022888 | -0.050354 | 60.8826 | 60.7269 | -61.6699 | 60.9283 | 60.8917 | 0.16479 | -61.6425 | 60.8002 | 60.7269 | -61.6516 | 60.91 | 60.8276 | 0.10071 | -61.6882 | 60.878 | 60.9055 | 60.9146 | -61.821 | 60.8963 | 60.8597 | 61.0199 | -61.821
334.1406 | 122.8638 | -60.7727 | 61.7752 | -0.17609 | 0.016129 | 0.0010254 | 0.0061865 | -0.0062612 | 0.0013608 | -0.0033111 | -0.21843 | -0.0035825 | -0.003262 | 0.0018692 | 0.0011173 | -0.0065304 | 0.073242 | 0.032043 | 0.032043 | 0.054932 | 0.15564 | 0.068665 | -0.07782 | 0.041199 | 0.054932 | -0.064087 | 0.091553 | 0.064087 | -0.041199 | -0.11902 | 60.8414 | 60.6949 | -61.6196 | 60.8047 | 60.8276 | 0.13275 | -61.702 | 60.7315 | 60.6537 | -61.6837 | 60.8139 | 60.7086 | 0.054932 | -61.7111 | 60.9283 | 60.8459 | 60.8047 | -61.853 | 60.8643 | 60.8368 | 60.8276 | -61.8942
335.7969 | 122.8821 | -60.759 | 61.7386 | -0.031128 | 0.01207 | 0.0027344 | 0.0034093 | -0.0017752 | -0.0080386 | -0.0050201 | 0.0028229 | -0.0082821 | -0.0047574 | -0.00069421 | 0.00047633 | -0.0048214 | 0.036621 | 0.07782 | 0.086975 | 0.054932 | 0.086975 | 0.054932 | -0.073242 | 0.15106 | 0.2243 | 0.068665 | 0.068665 | 0.059509 | 0.009155 | -0.07782 | 60.8139 | 60.6857 | -61.6516 | 60.8368 | 60.8139 | 0.12817 | -61.702 | 60.7681 | 60.6812 | -61.6699 | 60.91 | 60.8276 | 0.14649 | -61.6791 | 60.8459 | 60.7956 | 60.8459 | -61.8118 | 60.8276 | 60.8185 | 60.9833 | -61.8164
337.4688 | 122.8455 | -60.7636 | 61.7798 | -0.084534 | 0.015488 | 0.0023072 | -0.00022208 | -0.0043386 | 0.003497 | -0.0035249 | -0.12688 | -0.0018735 | -0.0021938 | 0.001442 | 0.0036807 | -0.0075986 | 0.07782 | 0.018311 | 0.018311 | 0.036621 | 0.10529 | 0.022888 | -0.11444 | 0.054932 | 0.036621 | -0.059509 | 0.064087 | 0.022888 | -0.059509 | -0.12817 | 60.7864 | 60.6491 | -61.6745 | 60.7819 | 60.8002 | 0.15106 | -61.702 | 60.704 | 60.6354 | -61.7157 | 60.8185 | 60.704 | 0.068665 | -61.7569 | 60.8688 | 60.8414 | 60.7819 | -61.8942 | 60.8276 | 60.7864 | 60.8002 | -61.908
339.1406 | 122.7036 | -60.8368 | 61.8027 | 0.11383 | 0.013565 | 0.0020936 | 0.0023413 | -0.005834 | -0.005048 | -0.0035249 | 0.21645 | -0.0074277 | -0.003262 | 0.00037379 | 0.0019717 | -0.0058896 | 0.022888 | 0.022888 | 0.041199 | -0.032043 | 0 | -0.004578 | -0.13733 | 0.091553 | 0.10529 | -0.018311 | -0.004578 | 0 | -0.068665 | -0.11444 | 60.8322 | 60.6995 | -61.8027 | 60.8597 | 60.8047 | 0.10529 | -61.7798 | 60.7681 | 60.7224 | -61.8073 | 60.9283 | 60.8185 | 0.09613 | -61.8027 | 60.8368 | 60.8597 | 60.878 | -61.94 | 60.8322 | 60.8368 | 60.9421 | -61.9171
340.8125 | 122.818 | -60.7773 | 61.7706 | -0.16083 | 0.013779 | 0.0020936 | 0.0061865 | -0.00027985 | -0.003339 | -0.0045929 | -0.12688 | -0.0070003 | -0.0024076 | 0.0012284 | 0.00068993 | -0.0063168 | 0.14191 | 0.13733 | 0.15106 | 0.091553 | 0.13733 | 0.10071 | -0.050354 | 0.15106 | 0.27008 | 0.064087 | 0.091553 | 0.064087 | 0.013733 | -0.036621 | 60.878 | 60.7269 | -61.6333 | 60.9146 | 60.8688 | 0.14191 | -61.6287 | 60.791 | 60.7407 | -61.6791 | 60.9283 | 60.8414 | 0.10071 | -61.7065 | 60.9146 | 60.9192 | 60.9283 | -61.821 | 60.8688 | 60.8414 | 61.0474 | -61.8073
342.4844 | 122.7859 | -60.791 | 61.7844 | 0.19012 | 0.012497 | 0.0018798 | -8.476e-06 | -0.0032706 | 0.00029262 | -0.0018159 | 0.10963 | -0.0059323 | -0.0036892 | -5.3406e-05 | 0.0049625 | -0.0054624 | -0.050354 | -0.091553 | -0.073242 | -0.091553 | 0.018311 | -0.045776 | -0.1831 | 0.045776 | -0.022888 | -0.07782 | -0.018311 | -0.041199 | -0.064087 | -0.13275 | 60.7452 | 60.6079 | -61.7661 | 60.6995 | 60.6995 | 0.091552 | -61.8347 | 60.7269 | 60.6583 | -61.8027 | 60.8368 | 60.7132 | 0.054931 | -61.8256 | 60.8093 | 60.7407 | 60.7178 | -61.9675 | 60.7727 | 60.7498 | 60.7681 | -61.9171
344.1562 | 122.818 | -60.791 | 61.7798 | -0.076904 | 0.014206 | 0.00059819 | 0.0059729 | -0.0051932 | 0.001788 | -0.00096127 | -0.096359 | -0.0044369 | -0.004971 | -0.00048061 | 0.0032535 | -0.007385 | 0.068665 | 0.022888 | 0.032043 | 0.004578 | 0.086975 | 0.009155 | -0.13275 | 0.059509 | 0.018311 | -0.068665 | 0.041199 | 0.032043 | -0.050354 | -0.12817 | 60.8002 | 60.6583 | -61.6928 | 60.8139 | 60.7956 | 0.13733 | -61.7111 | 60.7407 | 60.6628 | -61.7386 | 60.8505 | 60.7224 | 0.059509 | -61.7477 | 60.878 | 60.8597 | 60.8231 | -61.9125 | 60.8322 | 60.8231 | 60.8093 | -61.908
345.8281 | 122.818 | -60.7819 | 61.7798 | -0.16846 | 0.013992 | 0.0031616 | 0.0046911 | -0.00092065 | -0.0039798 | -0.0035249 | -0.21843 | -0.0067867 | -0.0036892 | 0.00058739 | 0.00026273 | -0.006744 | 0.11444 | 0.15106 | 0.15106 | 0.11444 | 0.1236 | 0.068665 | -0.041199 | 0.12817 | 0.23346 | 0.041199 | 0.10071 | 0.091553 | 0.018311 | -0.050354 | 60.8505 | 60.7407 | -61.6562 | 60.9329 | 60.8963 | 0.15564 | -61.6653 | 60.8002 | 60.7315 | -61.6791 | 60.91 | 60.8231 | 0.091553 | -61.6882 | 60.9055 | 60.8963 | 60.9329 | -61.821 | 60.8826 | 60.8734 | 61.0153 | -61.8301
347.5 | 122.7676 | -60.8047 | 61.7844 | 0.060425 | 0.010574 | 0.0033752 | 0.0014867 | -0.0030568 | -0.0065434 | -0.0063019 | 0.048599 | -0.0074277 | -0.0043302 | 0.00080099 | 0.00047633 | -0.0071714 | 0.032043 | 0.041199 | 0.059509 | 0.027466 | 0.073242 | 0.032043 | -0.10529 | 0.086975 | 0.13733 | 0 | 0.068665 | 0.036621 | -0.022888 | -0.082397 | 60.8368 | 60.6995 | -61.7111 | 60.8459 | 60.8322 | 0.13275 | -61.7523 | 60.7819 | 60.7224 | -61.7157 | 60.8917 | 60.8047 | 0.082397 | -61.7477 | 60.878 | 60.8368 | 60.8643 | -61.8896 | 60.8734 | 60.8414 | 60.9421 | -61.8668
349.1562 | 122.9004 | -60.7452 | 61.7752 | -0.16083 | 0.01741 | 0.0018798 | 0.0055457 | -0.0047658 | 0.001788 | -0.0043793 | -0.24895 | -0.0042233 | -0.0028348 | 0.0010148 | 0.0021853 | -0.006744 | 0.07782 | 0.018311 | 0.018311 | 0.045776 | 0.14648 | 0.054932 | -0.091553 | 0.064087 | 0.073242 | -0.073242 | 0.09613 | 0.082397 | -0.022888 | -0.09613 | 60.8002 | 60.6537 | -61.6287 | 60.7635 | 60.791 | 0.13733 | -61.6974 | 60.7224 | 60.6491 | -61.6791 | 60.8093 | 60.672 | 0.022888 | -61.6928 | 60.8917 | 60.8231 | 60.7635 | -61.8668 | 60.8414 | 60.8276 | 60.8185 | -61.8713
350.8125 | 122.8592 | -60.759 | 61.7615 | -0.015869 | 0.011856 | 0.0035888 | 0.0023413 | -0.0062612 | -0.003339 | -0.0039521 | 0.04097 | -0.0046505 | -0.0028348 | 0.00058739 | 0.00068993 | -0.0063168 | 0.041199 | 0.050354 | 0.068665 | 0.050354 | 0.082397 | 0.036621 | -0.086975 | 0.11444 | 0.21515 | 0.041199 | 0.082397 | 0.059509 | 0.009155 | -0.064087 | 60.7956 | 60.672 | -61.6791 | 60.8093 | 60.8093 | 0.13733 | -61.7203 | 60.7681 | 60.6949 | -61.6791 | 60.8734 | 60.8002 | 0.10529 | -61.702 | 60.8414 | 60.8002 | 60.8276 | -61.8484 | 60.8414 | 60.8185 | 60.9741 | -61.8256
352.4844 | 122.7448 | -60.791 | 61.8347 | 0.037537 | 0.016769 | 0.0018798 | 0.00063232 | -0.0017752 | 0.0049924 | -0.0024567 | -0.012436 | -0.0027279 | -0.0051846 | 0.00037379 | 0.0062441 | -0.0065304 | -0.018311 | -0.086975 | -0.068665 | -0.068665 | 0.054932 | -0.018311 | -0.15564 | -0.022888 | -0.10529 | -0.16937 | 0.045776 | 0.041199 | -0.086975 | -0.17395 | 60.7727 | 60.6354 | -61.7798 | 60.704 | 60.7224 | 0.086975 | -61.853 | 60.704 | 60.6171 | -61.7889 | 60.7681 | 60.6216 | 0.004577 | -61.7935 | 60.8459 | 60.7727 | 60.7224 | -61.9904 | 60.8368 | 60.8322 | 60.6857 | -62.0087
354.1562 | 122.8638 | -60.7498 | 61.7752 | -0.13794 | 0.014633 | 0.0035888 | 0.0049047 | -0.0051932 | -0.0056888 | -0.0035249 | -0.096359 | -0.0074277 | -0.0041164 | -0.00048061 | -0.0014463 | -0.0069578 | 0.16479 | 0.19684 | 0.17853 | 0.1236 | 0.10986 | 0.091553 | -0.059509 | 0.16937 | 0.29297 | 0.10986 | 0.082397 | 0.068665 | 0.036621 | -0.032043 | 60.8414 | 60.6903 | -61.6653 | 60.9467 | 60.8734 | 0.1831 | -61.6104 | 60.7864 | 60.7178 | -61.6928 | 60.9192 | 60.8597 | 0.14191 | -61.7065 | 60.8597 | 60.9146 | 60.9283 | -61.8347 | 60.8322 | 60.8185 | 61.0428 | -61.8073
355.8281 | 122.7859 | -60.7819 | 61.7981 | 0.17487 | 0.013992 | 0.0027344 | 0.00020512 | -0.0039114 | -0.00034818 | -0.0018159 | 0.102 | -0.0031551 | -0.0053982 | -0.0015488 | 0.0047489 | -0.0078122 | 0.032043 | 0 | -0.004578 | -0.027466 | 0 | -0.018311 | -0.16937 | 0.07782 | 0.013733 | -0.036621 | -0.013733 | -0.032043 | -0.054932 | -0.13733 | 60.7635 | 60.6125 | -61.7981 | 60.7819 | 60.7544 | 0.14191 | -61.7661 | 60.7269 | 60.6445 | -61.8118 | 60.8597 | 60.7452 | 0.10071 | -61.8301 | 60.7819 | 60.8139 | 60.7773 | -61.9675 | 60.7681 | 60.7498 | 60.7956 | -61.9354
357.5156 | 122.7631 | -60.7544 | 61.8256 | -0.061646 | 0.015488 | 0.0016662 | 0.0027685 | -0.004125 | 0.0049924 | -0.0035249 | -0.11162 | -0.0035825 | -0.00668 | 0.0029374 | 0.0051761 | -0.0061032 | 0.082397 | 0.013733 | 0.004578 | 0 | 0.086975 | 0.013733 | -0.1236 | 0.041199 | 0.018311 | -0.07782 | 0.054932 | 0.027466 | -0.041199 | -0.13275 | 60.7681 | 60.6308 | -61.7386 | 60.7681 | 60.7544 | 0.1236 | -61.7432 | 60.7132 | 60.6216 | -61.7706 | 60.7956 | 60.6766 | 0.054931 | -61.7981 | 60.8414 | 60.8368 | 60.759 | -61.9492 | 60.8093 | 60.7819 | 60.7727 | -61.9583
359.1875 | 122.7585 | -60.7819 | 61.8347 | 0.060425 | 0.013352 | 0.0031616 | 0.0029821 | -0.004125 | -0.0056888 | -0.0037385 | 0.094375 | -0.0072141 | -0.001553 | -0.00090781 | -0.00016447 | -0.0037534 | 0.018311 | 0.041199 | 0.045776 | 0 | 0.054932 | 0.027466 | -0.10529 | 0.07782 | 0.12817 | -0.004578 | 0.041199 | 0.032043 | -0.013733 | -0.086975 | 60.8093 | 60.6766 | -61.7798 | 60.8231 | 60.7819 | 0.10529 | -61.8164 | 60.7681 | 60.6949 | -61.7935 | 60.8597 | 60.7773 | 0.082397 | -61.8027 | 60.8368 | 60.8002 | 60.8276 | -61.94 | 60.8231 | 60.8139 | 60.91 | -61.9217
360.8594 | 122.9004 | -60.7224 | 61.7889 | -0.2066 | 0.012497 | 0.00081179 | 0.0055457 | -0.004125 | 0.0026424 | -0.0041657 | -0.19554 | -0.0046505 | -0.0024076 | 0.0020828 | 0.0011173 | -0.0075986 | 0.068665 | 0.018311 | 0.013733 | 0.045776 | 0.17853 | 0.064087 | -0.068665 | 0.036621 | 0.082397 | -0.054932 | 0.13733 | 0.082397 | -0.018311 | -0.10071 | 60.7864 | 60.6537 | -61.6104 | 60.7407 | 60.7681 | 0.11444 | -61.7203 | 60.704 | 60.6216 | -61.6516 | 60.759 | 60.6674 | 0.045776 | -61.7065 | 60.9009 | 60.791 | 60.7361 | -61.8576 | 60.8597 | 60.8047 | 60.8047 | -61.8896
362.5625 | 122.85 | -60.7132 | 61.8164 | -0.092163 | 0.015915 | 0.0038024 | 0.0019141 | -0.0028432 | 0.0024288 | -0.0037385 | -0.16502 | -0.0055051 | -0.0030484 | -0.0013352 | 0.0066715 | -0.0054624 | 0.059509 | 0.027466 | 0.013733 | 0.022888 | 0.11902 | 0.027466 | -0.1236 | 0.054932 | 0.036621 | -0.059509 | 0.068665 | 0.054932 | -0.045776 | -0.1236 | 60.7407 | 60.5896 | -61.6974 | 60.7407 | 60.7361 | 0.14648 | -61.7569 | 60.6674 | 60.5896 | -61.7477 | 60.7681 | 60.6537 | 0.064087 | -61.7615 | 60.8322 | 60.7727 | 60.7269 | -61.94 | 60.7819 | 60.7681 | 60.7498 | -61.94
364.2344 | 122.8271 | -60.6857 | 61.8256 | -0.1532 | 0.015701 | 0.0023072 | 0.0051183 | -0.0030568 | -0.0048344 | -0.0011749 | -0.11925 | -0.0067867 | -0.0024076 | -0.0024032 | 4.9132e-05 | -0.0058896 | 0.14191 | 0.1831 | 0.17853 | 0.11444 | 0.14648 | 0.11444 | -0.032043 | 0.16937 | 0.29297 | 0.091553 | 0.10529 | 0.059509 | 0.027466 | -0.041199 | 60.8002 | 60.6537 | -61.6791 | 60.8688 | 60.8002 | 0.14648 | -61.6837 | 60.7132 | 60.6445 | -61.7203 | 60.8551 | 60.7773 | 0.13275 | -61.7661 | 60.8322 | 60.8276 | 60.8643 | -61.8576 | 60.791 | 60.7452 | 60.9787 | -61.8668
365.9062 | 122.7905 | -60.7132 | 61.8622 | 0.17487 | 0.012497 | 0.0033752 | 0.0014867 | -0.002416 | 0.00029262 | -0.00096127 | 0.11726 | -0.0046505 | -0.0041164 | -5.3406e-05 | 0.0036807 | -0.0048214 | -0.032043 | -0.059509 | -0.045776 | -0.068665 | 0.018311 | -0.041199 | -0.17395 | 0.068665 | 0.022888 | -0.050354 | -0.004578 | -0.018311 | -0.059509 | -0.12817 | 60.672 | 60.5392 | -61.8439 | 60.6537 | 60.6445 | 0.10528 | -61.8942 | 60.6537 | 60.585 | -61.8668 | 60.7819 | 60.6628 | 0.07782 | -61.8805 | 60.7315 | 60.6812 | 60.6674 | -62.0361 | 60.7086 | 60.6949 | 60.7361 | -61.9904
367.5781 | 122.7905 | -60.6857 | 61.8805 | 0.052795 | 0.0092925 | 0.0018798 | 0.0027685 | -0.0028432 | -0.0071842 | -0.0039521 | 0.079117 | -0.0061459 | -0.0051846 | -0.0030442 | 0.0013309 | -0.0028988 | 0.027466 | 0.036621 | 0.045776 | 0.018311 | 0.082397 | 0.041199 | -0.09613 | 0.073242 | 0.13275 | 0 | 0.050354 | 0.022888 | 0 | -0.082397 | 60.7269 | 60.5896 | -61.7981 | 60.7224 | 60.704 | 0.11444 | -61.853 | 60.6857 | 60.6033 | -61.8301 | 60.759 | 60.6857 | 0.082397 | -61.8576 | 60.7681 | 60.7132 | 60.7315 | -61.9766 | 60.7361 | 60.7086 | 60.8185 | -61.9629
369.25 | 122.8729 | -60.6537 | 61.853 | -0.11505 | 0.011643 | 0.0048706 | 0.0044775 | -0.0026296 | -0.006116 | -0.0043793 | -0.081101 | -0.0061459 | -0.0045438 | -0.00069421 | 0.00068993 | -0.0061032 | 0.14648 | 0.17395 | 0.14648 | 0.09613 | 0.11902 | 0.07782 | -0.045776 | 0.20599 | 0.28381 | 0.10529 | 0.068665 | 0.041199 | 0.027466 | -0.045776 | 60.7315 | 60.6079 | -61.734 | 60.8276 | 60.7498 | 0.14191 | -61.7065 | 60.6812 | 60.6079 | -61.7844 | 60.8597 | 60.759 | 0.15106 | -61.8118 | 60.7727 | 60.8002 | 60.8002 | -61.8988 | 60.7224 | 60.6949 | 60.9375 | -61.8988
370.9062 | 122.7219 | -60.6766 | 61.9583 | -0.00061023 | 0.015061 | 0.0031616 | 0.0036231 | 0.00057455 | 0.0054196 | -0.0037385 | -0.050583 | -0.0059323 | -0.0068936 | -0.00026701 | 0.0058169 | -0.0088804 | 0.041199 | -0.054932 | -0.045776 | -0.041199 | 0.068665 | -0.018311 | -0.14648 | -0.004578 | -0.073242 | -0.15106 | 0.036621 | 0.018311 | -0.07782 | -0.15106 | 60.6583 | 60.5301 | -61.8896 | 60.6216 | 60.6354 | 0.10529 | -61.9171 | 60.5988 | 60.5255 | -61.9217 | 60.672 | 60.5255 | 0 | -61.94 | 60.7452 | 60.7178 | 60.6308 | -62.1048 | 60.7132 | 60.6949 | 60.6033 | -62.1094
372.5938 | 122.7859 | -60.6308 | 61.9354 | 0.11383 | 0.013992 | 0.0040162 | 0.0012731 | -0.0054068 | 0.001788 | -0.0037385 | 0.086746 | -0.0037961 | -0.0043302 | 0.0012284 | 0.0041079 | -0.005676 | -0.027466 | -0.10071 | -0.082397 | -0.082397 | 0.050354 | -0.045776 | -0.17395 | 0.013733 | -0.10986 | -0.13275 | 0.045776 | 0 | -0.082397 | -0.16937 | 60.585 | 60.4568 | -61.8851 | 60.5301 | 60.5484 | 0.091553 | -61.9629 | 60.5484 | 60.4614 | -61.8896 | 60.6445 | 60.498 | 0.036622 | -61.9354 | 60.6812 | 60.6033 | 60.5484 | -62.1094 | 60.6766 | 60.6308 | 60.5209 | -62.1048
374.25 | 122.8775 | -60.585 | 61.9263 | -0.22186 | 0.016556 | 0.0052978 | 0.0093909 | -0.0017752 | -0.00013458 | -0.0035249 | -0.21843 | -0.0052915 | -0.0045438 | 0.00058739 | -0.00037807 | -0.0054624 | 0.07782 | 0.032043 | 0.032043 | 0.054932 | 0.19684 | 0.068665 | -0.068665 | 0.054932 | 0.07782 | -0.068665 | 0.11444 | 0.10986 | -0.018311 | -0.082397 | 60.6537 | 60.5164 | -61.7294 | 60.6171 | 60.64 | 0.1236 | -61.8484 | 60.5667 | 60.5026 | -61.8118 | 60.64 | 60.5164 | 0.013732 | -61.8164 | 60.7819 | 60.6628 | 60.6171 | -61.9949 | 60.6995 | 60.6949 | 60.6628 | -62.0087
375.9844 | 122.8912 | -60.5484 | 61.9675 | -0.19897 | 0.012711 | 0.0044434 | 0.0068273 | -0.0011342 | 0.0011472 | -0.0039521 | -0.19554 | -0.0057187 | -0.0043302 | 0.0012284 | 0.0023989 | -0.0078122 | 0.059509 | 0.027466 | 0.009155 | 0.041199 | 0.16937 | 0.064087 | -0.068665 | 0.045776 | 0.07782 | -0.068665 | 0.10986 | 0.09613 | -0.022888 | -0.086975 | 60.6125 | 60.4797 | -61.7981 | 60.5759 | 60.5896 | 0.10986 | -61.908 | 60.5255 | 60.4614 | -61.8576 | 60.5942 | 60.4797 | 0.01831 | -61.8713 | 60.7178 | 60.6079 | 60.5576 | -62.0361 | 60.6583 | 60.6445 | 60.6262 | -62.0544
377.6562 | 122.731 | -60.5713 | 62.0224 | 0.13672 | 0.013138 | 0.0059388 | 0.0025549 | -0.0017752 | -0.0046206 | -0.0037385 | 0.13252 | -0.0065731 | -0.0030484 | -0.00026701 | 0.00047633 | -0.0041806 | 0 | 0.041199 | 0.059509 | -0.022888 | 0.013733 | 0.013733 | -0.12817 | 0.082397 | 0.10986 | 0.009155 | 0.036621 | 0.004578 | -0.032043 | -0.10071 | 60.585 | 60.4431 | -62.0087 | 60.6125 | 60.5484 | 0.10529 | -62.0224 | 60.5392 | 60.4706 | -61.9858 | 60.6537 | 60.5804 | 0.10986 | -62.0178 | 60.585 | 60.5713 | 60.6308 | -62.1506 | 60.6079 | 60.5759 | 60.6812 | -62.1231
379.3438 | 122.7631 | -60.5301 | 62.0636 | -0.054016 | 0.016769 | 0.00017099 | 0.0040503 | -0.0026296 | 0.0022152 | -0.0028839 | -0.12688 | -0.0057187 | -0.0019802 | 0.0033646 | 0.0036807 | -0.008453 | 0.073242 | 0.004578 | 0.022888 | -0.009155 | 0.09613 | -0.004578 | -0.14191 | 0.054932 | -0.009155 | -0.091553 | 0.054932 | 0.022888 | -0.054932 | -0.12817 | 60.5255 | 60.3882 | -61.9675 | 60.5347 | 60.5209 | 0.13275 | -61.9904 | 60.4752 | 60.4019 | -62.0087 | 60.585 | 60.4385 | 0.036621 | -62.0407 | 60.6262 | 60.6033 | 60.553 | -62.2055 | 60.585 | 60.553 | 60.5209 | -62.1918
381.0156 | 122.7402 | -60.5209 | 62.0911 | 0.083313 | 0.011002 | 0.0033752 | 0.0044775 | -0.0045522 | -0.004407 | -0.0041657 | 0.10963 | -0.0080685 | -0.003262 | -0.0013352 | 0.00068993 | -0.005035 | 0.013733 | 0.027466 | 0.041199 | 0.018311 | 0.073242 | 0.032043 | -0.10529 | 0.07782 | 0.12817 | -0.009155 | 0.054932 | 0.036621 | 0 | -0.082397 | 60.553 | 60.4156 | -62.0178 | 60.5484 | 60.5392 | 0.1236 | -62.0773 | 60.5209 | 60.4385 | -62.0361 | 60.5988 | 60.5118 | 0.073242 | -62.0544 | 60.5942 | 60.5347 | 60.5621 | -62.1964 | 60.5759 | 60.5576 | 60.6491 | -62.1735
382.6719 | 122.7402 | -60.4385 | 62.1826 | 0.083313 | 0.015061 | 0.0018798 | -0.0010767 | -0.0017752 | 0.0028562 | -0.0018159 | -0.035324 | -0.0033687 | -0.0030484 | 0.0018692 | 0.0066715 | -0.0080258 | -0.050354 | -0.10529 | -0.082397 | -0.068665 | 0.050354 | -0.041199 | -0.17853 | -0.036621 | -0.11444 | -0.16937 | 0.045776 | 0.009155 | -0.09613 | -0.14648 | 60.3973 | 60.26 | -62.1323 | 60.3333 | 60.3699 | 0.10986 | -62.233 | 60.3424 | 60.2921 | -62.1368 | 60.4019 | 60.2692 | -0.022889 | -62.1735 | 60.4889 | 60.3882 | 60.3561 | -62.3611 | 60.4843 | 60.4477 | 60.3241 | -62.3291
384.3438 | 122.8271 | -60.3333 | 62.2101 | -0.22186 | 0.015915 | 0.0050842 | 0.0057593 | -0.004125 | -0.003339 | -0.0043793 | -0.17265 | -0.0067867 | -0.0034756 | 0.00037379 | -0.00059167 | -0.0052488 | 0.07782 | 0.068665 | 0.059509 | 0.059509 | 0.18768 | 0.082397 | -0.059509 | 0.073242 | 0.15106 | -0.022888 | 0.14191 | 0.10529 | -0.013733 | -0.068665 | 60.4156 | 60.2737 | -62.0224 | 60.4019 | 60.3928 | 0.11902 | -62.1323 | 60.3195 | 60.2646 | -62.0682 | 60.4065 | 60.3104 | 0.045777 | -62.1048 | 60.5209 | 60.4111 | 60.3928 | -62.2696 | 60.4752 | 60.4385 | 60.4843 | -62.2787
386.0469 | 122.8958 | -60.3561 | 62.178 | -0.1532 | 0.014633 | 0.0025208 | 0.0046911 | -0.0011342 | 0.0013608 | -0.0037385 | -0.24132 | -0.0067867 | -0.001553 | -0.00048061 | 0.0034671 | -0.0082394 | 0.064087 | 0.013733 | 0.013733 | 0.041199 | 0.16479 | 0.050354 | -0.10071 | 0.064087 | 0.091553 | -0.050354 | 0.11444 | 0.10529 | -0.004578 | -0.086975 | 60.4065 | 60.2554 | -62.0132 | 60.3699 | 60.3973 | 0.14191 | -62.114 | 60.3516 | 60.2692 | -62.0636 | 60.4202 | 60.3058 | 0.036621 | -62.0728 | 60.5209 | 60.4202 | 60.3699 | -62.2787 | 60.4706 | 60.4614 | 60.4477 | -62.265
387.7188 | 122.8592 | -60.3104 | 62.233 | -0.0082397 | 0.0086517 | 0.0059388 | 0.0031957 | -0.0032706 | -0.0073978 | -0.0071563 | 0.048599 | -0.0074277 | -0.0039028 | -0.001976 | 4.9132e-05 | -0.0052488 | 0.036621 | 0.045776 | 0.07782 | 0.045776 | 0.10071 | 0.036621 | -0.10071 | 0.13275 | 0.21515 | 0.050354 | 0.068665 | 0.041199 | -0.027466 | -0.068665 | 60.347 | 60.2097 | -62.1323 | 60.3561 | 60.3561 | 0.14648 | -62.1964 | 60.2829 | 60.2417 | -62.1643 | 60.4431 | 60.3607 | 0.11902 | -62.1918 | 60.4111 | 60.347 | 60.3882 | -62.3337 | 60.379 | 60.3516 | 60.5255 | -62.3016
389.375 | 122.7951 | -60.2966 | 62.3062 | 0.15198 | 0.014206 | 0.0014526 | 0.0038367 | -0.0019888 | 0.001788 | -0.0052337 | 0.079117 | -0.0050777 | -0.0036892 | -5.3406e-05 | 0.0026125 | -0.006744 | -0.041199 | -0.10986 | -0.09613 | -0.082397 | 0.054932 | -0.045776 | -0.19684 | 0.009155 | -0.10986 | -0.12817 | 0.045776 | 0.018311 | -0.082397 | -0.17395 | 60.2509 | 60.0998 | -62.2513 | 60.1868 | 60.2142 | 0.11444 | -62.3474 | 60.2142 | 60.1227 | -62.2604 | 60.3058 | 60.1685 | 0.045776 | -62.2879 | 60.3516 | 60.2554 | 60.2005 | -62.5031 | 60.3424 | 60.3149 | 60.1868 | -62.4802
391.0312 | 122.8683 | -60.2188 | 62.2879 | -0.14557 | 0.015061 | 0.0044434 | 0.0074683 | -0.0036978 | -0.006116 | -0.0043793 | -0.012436 | -0.0076413 | -0.0036892 | 0.00016019 | 0.0013309 | -0.0058896 | 0.15564 | 0.16022 | 0.14191 | 0.10986 | 0.10986 | 0.07782 | -0.068665 | 0.18768 | 0.29297 | 0.12817 | 0.059509 | 0.064087 | 0.032043 | -0.041199 | 60.2966 | 60.1501 | -62.178 | 60.379 | 60.3287 | 0.17853 | -62.1323 | 60.2509 | 60.1776 | -62.2284 | 60.4065 | 60.347 | 0.16937 | -62.2238 | 60.3287 | 60.3745 | 60.3607 | -62.3566 | 60.2783 | 60.2829 | 60.5118 | -62.3291
392.7031 | 122.8729 | -60.0769 | 62.4527 | -0.14557 | 0.013992 | 0.0048706 | 0.0061865 | -0.0045522 | -0.0052616 | -0.0067291 | -0.11925 | -0.0072141 | -0.0019802 | -0.0013352 | -0.00037807 | -0.0075986 | 0.15106 | 0.18768 | 0.16479 | 0.10529 | 0.10986 | 0.09613 | -0.054932 | 0.19226 | 0.29755 | 0.091553 | 0.07782 | 0.054932 | 0.022888 | -0.041199 | 60.173 | 60.022 | -62.3428 | 60.2646 | 60.1822 | 0.16022 | -62.3016 | 60.0998 | 60.0357 | -62.3749 | 60.2692 | 60.1685 | 0.13275 | -62.3978 | 60.1868 | 60.228 | 60.2417 | -62.5076 | 60.1547 | 60.1318 | 60.3744 | -62.4939
394.3594 | 122.7905 | -60.1273 | 62.4344 | 0.083313 | 0.014206 | 0.0031616 | 0.00084592 | -0.0030568 | 0.0020016 | -0.0024567 | 0.10963 | -0.0035825 | -0.0053982 | -0.00069421 | 0.0051761 | -0.0065304 | -0.036621 | -0.082397 | -0.091553 | -0.091553 | 0.050354 | -0.032043 | -0.17853 | 0.018311 | -0.09613 | -0.12817 | 0.022888 | 0 | -0.073242 | -0.14648 | 60.0952 | 59.9487 | -62.384 | 60.0449 | 60.0357 | 0.086975 | -62.471 | 60.054 | 59.9808 | -62.4115 | 60.1456 | 59.9991 | 0.01831 | -62.4344 | 60.1776 | 60.0906 | 60.0357 | -62.6129 | 60.1501 | 60.1273 | 60.0311 | -62.5809
396.0312 | 122.8226 | -60.0357 | 62.5259 | -0.22949 | 0.013565 | 0.002948 | 0.0055457 | -0.00092065 | -0.0018436 | -0.0035249 | -0.15739 | -0.0055051 | -0.0019802 | -0.0011216 | 0.00090353 | -0.0069578 | 0.11902 | 0.09613 | 0.086975 | 0.068665 | 0.16022 | 0.07782 | -0.050354 | 0.073242 | 0.15106 | -0.022888 | 0.14648 | 0.10986 | -0.009155 | -0.073242 | 60.1135 | 59.9854 | -62.3657 | 60.1318 | 60.1044 | 0.11902 | -62.4069 | 60.0266 | 59.9625 | -62.3795 | 60.1089 | 60.0128 | 0.050354 | -62.4161 | 60.1959 | 60.1547 | 60.1227 | -62.5763 | 60.1822 | 60.1456 | 60.1868 | -62.5992
397.7031 | 122.7905 | -59.9762 | 62.6358 | 0.19012 | 0.01442 | 0.001239 | 0.0010595 | -0.0049796 | 0.00050622 | -0.0026703 | 0.102 | -0.0048641 | -0.0036892 | 0.0020828 | 0.0026125 | -0.0058896 | -0.004578 | -0.050354 | -0.036621 | -0.045776 | 0.004578 | -0.036621 | -0.17853 | 0.086975 | 0 | -0.036621 | -0.009155 | -0.036621 | -0.054932 | -0.1236 | 59.9396 | 59.7977 | -62.6312 | 59.9258 | 59.9304 | 0.13275 | -62.6404 | 59.9213 | 59.8526 | -62.645 | 60.0632 | 59.9396 | 0.086975 | -62.6724 | 59.9808 | 59.9716 | 59.9396 | -62.8143 | 59.967 | 59.9396 | 59.9762 | -62.7594
399.3906 | 122.7859 | -59.8068 | 62.764 | 0.13672 | 0.014847 | 0.0027344 | 0.0017005 | -0.0019888 | -0.00163 | -0.0030975 | 0.17067 | -0.0080685 | -0.0019802 | 0.0012284 | 0.0034671 | -0.008453 | -0.027466 | -0.086975 | -0.09613 | -0.086975 | 0.041199 | -0.032043 | -0.17853 | 0.036621 | -0.045776 | -0.086975 | 0.009155 | -0.004578 | -0.082397 | -0.14191 | 59.7748 | 59.6283 | -62.7228 | 59.7198 | 59.7198 | 0.091553 | -62.7914 | 59.7244 | 59.6649 | -62.7548 | 59.8434 | 59.7198 | 0.054932 | -62.7686 | 59.848 | 59.7794 | 59.7107 | -62.9425 | 59.816 | 59.8022 | 59.761 | -62.9059
401.1406 | 122.7448 | -59.697 | 62.915 | 0.13672 | 0.012924 | 0.0027344 | 0.0053321 | -0.0054068 | -0.0041934 | -0.0037385 | 0.1783 | -0.0074277 | -0.0036892 | -0.00048061 | 0.0026125 | -0.0058896 | 0.022888 | 0.009155 | 0.036621 | -0.036621 | 0.018311 | -0.022888 | -0.14191 | 0.10986 | 0.10071 | 0.004578 | 0.027466 | 0.009155 | -0.027466 | -0.086975 | 59.6741 | 59.5551 | -62.8967 | 59.7061 | 59.6603 | 0.10529 | -62.8922 | 59.6695 | 59.61 | -62.8876 | 59.8068 | 59.7015 | 0.091553 | -62.9059 | 59.7153 | 59.7198 | 59.7336 | -63.0569 | 59.7244 | 59.7061 | 59.7977 | -63.002
402.8906 | 122.8409 | -59.3948 | 63.1165 | -0.054016 | 0.011856 | 0.006366 | 0.0072547 | -0.002416 | -0.006116 | -0.0022431 | -0.096359 | -0.0095639 | -0.0058254 | -0.00048061 | 4.9132e-05 | -0.0065304 | 0.1236 | 0.13275 | 0.12817 | 0.09613 | 0.12817 | 0.073242 | -0.054932 | 0.1831 | 0.2655 | 0.086975 | 0.086975 | 0.054932 | 0.018311 | -0.059509 | 59.4681 | 59.3399 | -62.9883 | 59.5276 | 59.491 | 0.15106 | -62.9929 | 59.4131 | 59.3353 | -63.0295 | 59.5779 | 59.4818 | 0.14648 | -63.0615 | 59.523 | 59.5184 | 59.523 | -63.1714 | 59.4818 | 59.4498 | 59.6603 | -63.176
404.5781 | 122.8683 | -59.1293 | 63.3728 | -0.14557 | 0.013992 | 0.0055114 | 0.0059729 | -0.0026296 | -0.0039798 | -0.0043793 | -0.096359 | -0.0067867 | -0.0028348 | -0.0017624 | -0.00080527 | -0.007385 | 0.16479 | 0.15106 | 0.14191 | 0.10986 | 0.11444 | 0.07782 | -0.045776 | 0.21057 | 0.29755 | 0.10529 | 0.09613 | 0.050354 | 0.022888 | -0.045776 | 59.2072 | 59.0836 | -63.2584 | 59.2804 | 59.2392 | 0.15564 | -63.208 | 59.1522 | 59.0836 | -63.2767 | 59.3399 | 59.2346 | 0.15106 | -63.3224 | 59.2438 | 59.2941 | 59.2712 | -63.4186 | 59.2255 | 59.1797 | 59.4269 | -63.4186
406.3125 | 122.8363 | -58.905 | 63.6703 | -0.24475 | 0.011215 | 0.0052978 | 0.0040503 | -0.0028432 | 0.00071982 | -0.0050201 | -0.24132 | -0.0072141 | -0.003262 | -0.00069421 | 0.0030399 | -0.0065304 | 0.082397 | 0.054932 | 0.045776 | 0.045776 | 0.19226 | 0.082397 | -0.050354 | 0.091553 | 0.10529 | -0.050354 | 0.14191 | 0.10071 | -0.027466 | -0.073242 | 58.9874 | 58.8547 | -63.4781 | 58.96 | 58.9508 | 0.09613 | -63.588 | 58.8776 | 58.8318 | -63.5284 | 58.9966 | 58.8547 | 0.022888 | -63.5696 | 59.0973 | 58.9874 | 58.9508 | -63.7207 | 59.0469 | 59.0057 | 59.0103 | -63.7436
408.0469 | 122.7127 | -58.5754 | 64.0228 | 0.12909 | 0.011002 | 0.0040162 | -0.00022208 | -0.0026296 | -0.0012028 | -0.0035249 | 0.15541 | -0.0061459 | -0.004971 | -0.00090781 | 0.0034671 | -0.005035 | 0.045776 | 0.050354 | 0.045776 | -0.013733 | 0.004578 | -0.009155 | -0.13733 | 0.09613 | 0.073242 | -0.032043 | -0.013733 | -0.041199 | -0.07782 | -0.13733 | 58.5663 | 58.4381 | -64.0182 | 58.6258 | 58.5617 | 0.1236 | -63.9771 | 58.4976 | 58.4381 | -64.0366 | 58.6716 | 58.5434 | 0.10529 | -64.064 | 58.58 | 58.6212 | 58.6212 | -64.1602 | 58.5617 | 58.5342 | 58.6487 | -64.1602
409.7188 | 122.7676 | -58.1406 | 64.476 | 0.11383 | 0.013352 | 0.00038459 | 0.0034093 | -0.0034842 | 0.0022152 | -0.0028839 | 0.056228 | -0.0057187 | -0.00091223 | 0.0016556 | 0.0036807 | -0.0061032 | -0.041199 | -0.13733 | -0.11444 | -0.091553 | 0.054932 | -0.073242 | -0.19226 | -0.004578 | -0.1236 | -0.15106 | 0.036621 | 0.004578 | -0.091553 | -0.16937 | 58.0673 | 57.9483 | -64.4211 | 58.0032 | 58.049 | 0.10071 | -64.5172 | 58.049 | 57.9712 | -64.4394 | 58.136 | 57.9895 | 0.018311 | -64.4714 | 58.1955 | 58.0994 | 58.0261 | -64.6683 | 58.1772 | 58.1451 | 58.017 | -64.6454
411.4531 | 122.8592 | -57.4768 | 65.062 | -0.12268 | 0.018051 | 0.002948 | 0.0053321 | -0.0028432 | 0.0015744 | -0.0013885 | -0.14977 | -0.0059323 | -0.0036892 | 0.00251 | 0.0028263 | -0.0095212 | 0.07782 | 0.032043 | 0.022888 | 0.018311 | 0.10986 | 0.018311 | -0.11444 | 0.059509 | 0.045776 | -0.064087 | 0.059509 | 0.041199 | -0.073242 | -0.11902 | 57.4951 | 57.3624 | -64.9521 | 57.5089 | 57.4951 | 0.13275 | -64.9841 | 57.4036 | 57.3578 | -65.0024 | 57.5363 | 57.4127 | 0.054932 | -65.0208 | 57.5867 | 57.5546 | 57.4997 | -65.1764 | 57.5363 | 57.518 | 57.5226 | -65.181
413.125 | 122.8455 | -56.7032 | 65.8356 | -0.099793 | 0.014206 | 0.0057252 | 0.0049047 | -0.0032706 | -0.0065434 | -0.0020295 | -0.13451 | -0.0074277 | -0.0019802 | -0.0017624 | -0.0010191 | -0.0054624 | 0.15564 | 0.19684 | 0.18768 | 0.11902 | 0.10071 | 0.091553 | -0.050354 | 0.17853 | 0.31586 | 0.10529 | 0.073242 | 0.082397 | 0.022888 | -0.041199 | 56.7947 | 56.6528 | -65.7349 | 56.9 | 56.8222 | 0.16937 | -65.6799 | 56.7261 | 56.662 | -65.7623 | 56.8817 | 56.8085 | 0.14649 | -65.7532 | 56.8039 | 56.8588 | 56.8909 | -65.8859 | 56.7764 | 56.7856 | 57.019 | -65.8768
414.8594 | 122.7585 | -56.0669 | 66.5451 | 0.13672 | 0.015061 | 0.0020936 | 0.0031957 | -0.0039114 | 0.0030698 | -0.0041657 | 0.048599 | -0.0059323 | -0.0021938 | 0.0012284 | 0.0045351 | -0.0071714 | -0.045776 | -0.11902 | -0.10986 | -0.082397 | 0.045776 | -0.050354 | -0.1831 | -0.004578 | -0.10071 | -0.14191 | 0.054932 | 0.013733 | -0.086975 | -0.17853 | 56.0165 | 55.8838 | -66.4993 | 55.9479 | 55.9845 | 0.10071 | -66.5909 | 55.9799 | 55.8884 | -66.4902 | 56.0623 | 55.925 | 0.036621 | -66.5314 | 56.1127 | 56.0211 | 55.957 | -66.7282 | 56.1218 | 56.0806 | 55.9662 | -66.7236
416.5781 | 122.8638 | -55.0369 | 67.4927 | -0.076904 | 0.015061 | 0.002948 | 0.0057593 | -0.0032706 | -0.005048 | -0.0026703 | -0.08873 | -0.0063595 | -0.0030484 | 0.00080099 | -0.0016599 | -0.0063168 | 0.13733 | 0.1831 | 0.16479 | 0.11902 | 0.10071 | 0.07782 | -0.064087 | 0.18768 | 0.30212 | 0.10071 | 0.086975 | 0.073242 | 0.041199 | -0.041199 | 55.1147 | 54.9728 | -67.392 | 55.22 | 55.1559 | 0.18311 | -67.3553 | 55.0781 | 54.9957 | -67.4057 | 55.2246 | 55.1376 | 0.14191 | -67.4194 | 55.1376 | 55.1743 | 55.2017 | -67.5568 | 55.1239 | 55.1102 | 55.3391 | -67.5339
418.3125 | 122.7448 | -53.5812 | 69.0399 | 0.083313 | 0.015061 | -4.2814e-05 | 0.0019141 | -0.0022024 | 0.0026424 | -0.0016021 | 0.056228 | -0.0042233 | -0.003262 | 0.0029374 | 0.0043215 | -0.0071714 | -0.059509 | -0.13275 | -0.10529 | -0.086975 | 0.059509 | -0.045776 | -0.18768 | -0.036621 | -0.13275 | -0.17395 | 0.022888 | 0.018311 | -0.10986 | -0.17853 | 53.5355 | 53.3936 | -68.9804 | 53.4485 | 53.4943 | 0.10071 | -69.0994 | 53.4714 | 53.4027 | -69.017 | 53.5446 | 53.4073 | 0.004578 | -69.0216 | 53.6407 | 53.5217 | 53.476 | -69.2276 | 53.6041 | 53.5995 | 53.4485 | -69.2184
420.0625 | 122.7264 | -52.684 | 69.96 | 0.1825 | 0.013992 | 0.0020936 | 0.0034093 | -0.004125 | 0.00029262 | -0.0030975 | 0.18593 | -0.0078549 | -0.003262 | -5.3406e-05 | 0.0015445 | -0.0061032 | 0.018311 | 0.032043 | 0.050354 | -0.004578 | -0.022888 | -0.018311 | -0.16479 | 0.10071 | 0.082397 | -0.009155 | -0.009155 | -0.032043 | -0.064087 | -0.14191 | 52.6657 | 52.5192 | -69.9829 | 52.7161 | 52.6794 | 0.16022 | -69.9417 | 52.6199 | 52.5421 | -69.9692 | 52.7847 | 52.6749 | 0.13275 | -69.9921 | 52.6611 | 52.7023 | 52.7344 | -70.1248 | 52.6749 | 52.652 | 52.7664 | -70.1019
421.7188 | 122.7356 | -52.2629 | 70.3629 | 0.075684 | 0.013992 | 0.0020936 | 0.0040503 | -0.002416 | 0.0039242 | -0.00096127 | 0.048599 | -0.0035825 | -0.0028348 | 0.0018692 | 0.0053897 | -0.0065304 | -0.045776 | -0.13275 | -0.10529 | -0.082397 | 0.073242 | -0.050354 | -0.17853 | -0.032043 | -0.13733 | -0.16479 | 0.032043 | 0.013733 | -0.10986 | -0.18768 | 52.2125 | 52.0844 | -70.2896 | 52.1301 | 52.1805 | 0.096131 | -70.4086 | 52.153 | 52.0752 | -70.3308 | 52.2308 | 52.0981 | 0.022888 | -70.3491 | 52.3361 | 52.2171 | 52.1576 | -70.5414 | 52.2949 | 52.2766 | 52.1255 | -70.5505
423.4531 | 122.85 | -50.8209 | 71.6995 | -0.092163 | 0.013565 | 0.0044434 | 0.0042639 | -0.0015616 | -0.0046206 | -0.0033111 | -0.081101 | -0.0089229 | -0.0013394 | -0.0011216 | 0.0023989 | -0.0069578 | 0.082397 | 0.13733 | 0.12817 | 0.073242 | 0.09613 | 0.068665 | -0.07782 | 0.17853 | 0.2655 | 0.086975 | 0.07782 | 0.07782 | 0.018311 | -0.064087 | 50.8896 | 50.7431 | -71.6034 | 50.9583 | 50.8942 | 0.15106 | -71.6171 | 50.8392 | 50.7568 | -71.6217 | 50.9995 | 50.9079 | 0.15106 | -71.6217 | 50.9171 | 50.9033 | 50.9491 | -71.7773 | 50.8987 | 50.8987 | 51.0864 | -71.7636
425.2031 | 122.7448 | -50.1068 | 72.5281 | 0.075684 | 0.013565 | 0.0014526 | 0.0046911 | -0.001348 | -0.0029118 | -0.0039521 | 0.094375 | -0.0063595 | -0.0053982 | -0.00026701 | 0.0011173 | -0.0061032 | 0.041199 | 0.036621 | 0.054932 | 0.013733 | 0.064087 | 0.045776 | -0.10529 | 0.091553 | 0.10071 | 0.004578 | 0.050354 | 0.027466 | -0.022888 | -0.09613 | 50.1526 | 50.0015 | -72.464 | 50.1434 | 50.1205 | 0.11902 | -72.4869 | 50.0839 | 50.0107 | -72.4777 | 50.1984 | 50.1114 | 0.10071 | -72.5006 | 50.1709 | 50.148 | 50.1617 | -72.6334 | 50.1572 | 50.1343 | 50.2075 | -72.6242
426.9375 | 122.8043 | -48.2391 | 74.3317 | -0.16083 | 0.013352 | 0.0038024 | 0.0044775 | -0.0039114 | -0.00163 | -0.0033111 | -0.18028 | -0.0084957 | -0.004971 | -0.00090781 | 0.00068993 | -0.0080258 | 0.14648 | 0.13275 | 0.15106 | 0.10529 | 0.13275 | 0.082397 | -0.064087 | 0.16022 | 0.25635 | 0.064087 | 0.1236 | 0.10071 | 0.013733 | -0.045776 | 48.3215 | 48.175 | -74.1989 | 48.3719 | 48.3444 | 0.16937 | -74.1852 | 48.2529 | 48.1934 | -74.2081 | 48.3994 | 48.3032 | 0.10986 | -74.231 | 48.3719 | 48.3856 | 48.3902 | -74.3958 | 48.3627 | 48.3398 | 48.4955 | -74.3774
428.6094 | 122.7539 | -46.3943 | 76.2039 | 0.060425 | 0.011429 | 0.0031616 | 0.0014867 | -0.0030568 | -0.0046206 | -0.0045929 | 0.04097 | -0.0082821 | -0.0043302 | -0.001976 | 0.0032535 | -0.005676 | 0.022888 | 0.036621 | 0.041199 | 0.009155 | 0.082397 | 0.041199 | -0.10071 | 0.10071 | 0.14648 | -0.004578 | 0.07782 | 0.045776 | -0.004578 | -0.091553 | 46.4355 | 46.2936 | -76.1215 | 46.431 | 46.4035 | 0.10986 | -76.181 | 46.3898 | 46.3028 | -76.1261 | 46.4951 | 46.3898 | 0.086975 | -76.1581 | 46.4767 | 46.4172 | 46.4355 | -76.3046 | 46.4722 | 46.4401 | 46.5408 | -76.2955
430.3594 | 122.8043 | -45.3186 | 77.211 | -0.16846 | 0.015061 | 0.0059388 | 0.0051183 | -0.0030568 | -0.0018436 | -0.0041657 | -0.16502 | -0.0084957 | -0.003262 | -0.0021896 | 0.0023989 | -0.0071714 | 0.16022 | 0.18768 | 0.17395 | 0.10986 | 0.15564 | 0.091553 | -0.041199 | 0.18768 | 0.3067 | 0.082397 | 0.091553 | 0.068665 | 0.022888 | -0.041199 | 45.4102 | 45.2774 | -77.0554 | 45.5063 | 45.4285 | 0.15106 | -77.0508 | 45.3415 | 45.2774 | -77.1194 | 45.5063 | 45.401 | 0.1236 | -77.1423 | 45.4742 | 45.4788 | 45.4926 | -77.2522 | 45.4102 | 45.3873 | 45.6253 | -77.2522
432.0938 | 122.7402 | -43.1122 | 79.5593 | -0.069275 | 0.014847 | 0.0023072 | 0.00084592 | -0.0043386 | 0.006274 | -0.0011749 | -0.14214 | -0.0048641 | -0.0043302 | 0.0016556 | 0.0058169 | -0.0099484 | 0.068665 | 0.013733 | -0.009155 | -0.013733 | 0.09613 | 0.013733 | -0.15106 | 0.018311 | -0.050354 | -0.11444 | 0.054932 | 0.022888 | -0.068665 | -0.15106 | 43.1259 | 42.9611 | -79.4632 | 43.1259 | 43.0984 | 0.13733 | -79.4907 | 43.0435 | 42.9611 | -79.5044 | 43.1305 | 42.9977 | 0.036621 | -79.5364 | 43.2083 | 43.1808 | 43.103 | -79.7104 | 43.1671 | 43.1351 | 43.0618 | -79.7104
433.7656 | 122.7905 | -39.6881 | 82.8964 | -0.18372 | 0.019333 | 0.002948 | 0.0044775 | -0.0026296 | -0.0020572 | -0.0026703 | -0.14977 | -0.0093503 | -0.0021938 | -0.0017624 | 0.0019717 | -0.0065304 | 0.13733 | 0.16022 | 0.16022 | 0.10529 | 0.11444 | 0.091553 | -0.054932 | 0.16479 | 0.27008 | 0.086975 | 0.082397 | 0.068665 | 0.009155 | -0.068665 | 39.7797 | 39.6332 | -82.782 | 39.8483 | 39.7934 | 0.16022 | -82.7591 | 39.6973 | 39.6194 | -82.814 | 39.8529 | 39.7751 | 0.15564 | -82.8278 | 39.8026 | 39.8254 | 39.8483 | -82.9514 | 39.7705 | 39.7568 | 39.9582 | -82.9651
435.5 | 122.85 | -38.1088 | 84.4666 | -0.17609 | 0.015915 | 0.0020936 | 0.0036231 | -0.001348 | 0.0022152 | -0.0039521 | -0.24132 | -0.0046505 | -0.0019802 | 0.00037379 | 0.0041079 | -0.0099484 | 0.082397 | 0.036621 | 0.027466 | 0.050354 | 0.17395 | 0.064087 | -0.082397 | 0.045776 | 0.073242 | -0.059509 | 0.10071 | 0.050354 | -0.036621 | -0.12817 | 38.1729 | 38.0264 | -84.2926 | 38.1454 | 38.1592 | 0.13275 | -84.3842 | 38.0722 | 37.9807 | -84.3658 | 38.1546 | 38.0493 | 0.068665 | -84.4162 | 38.2828 | 38.1912 | 38.1363 | -84.549 | 38.2095 | 38.1592 | 38.1821 | -84.5947
437.2344 | 122.7539 | -36.8866 | 85.7391 | 0.15961 | 0.013352 | 0.0027344 | 0.0017005 | -0.0022024 | -0.0014164 | 0.00096133 | 0.14778 | -0.0061459 | -0.0053982 | -0.0013352 | 0.0064577 | -0.0052488 | 0.054932 | 0.018311 | 0.013733 | -0.013733 | 0.009155 | -0.022888 | -0.16022 | 0.073242 | 0.036621 | -0.032043 | -0.027466 | -0.045776 | -0.073242 | -0.13733 | 36.8637 | 36.7264 | -85.73 | 36.9049 | 36.8729 | 0.14648 | -85.6842 | 36.8134 | 36.7493 | -85.7666 | 36.9598 | 36.8546 | 0.10529 | -85.7849 | 36.8958 | 36.9415 | 36.9003 | -85.8994 | 36.8591 | 36.8408 | 36.9232 | -85.8765
438.9688 | 122.7173 | -36.3693 | 86.2839 | 0.20538 | 0.012497 | 0.0038024 | 0.0014867 | -0.0030568 | -0.002698 | -0.0028839 | 0.19356 | -0.0057187 | -0.0071072 | -0.00090781 | 0.0036807 | -0.0063168 | 0.032043 | 0.009155 | 0.027466 | -0.022888 | -0.018311 | -0.018311 | -0.17853 | 0.086975 | 0.068665 | -0.027466 | -0.036621 | -0.050354 | -0.07782 | -0.1236 | 36.351 | 36.1908 | -86.3022 | 36.3785 | 36.3464 | 0.15564 | -86.2518 | 36.2915 | 36.2457 | -86.3205 | 36.4563 | 36.3419 | 0.09613 | -86.3342 | 36.351 | 36.4014 | 36.3968 | -86.4624 | 36.3327 | 36.319 | 36.438 | -86.4075
440.7188 | 122.7127 | -35.1196 | 87.5244 | -0.0082397 | 0.01207 | 0.0016662 | 0.0023413 | -0.0032706 | 0.001788 | -0.0016021 | -0.020065 | -0.0035825 | -0.0036892 | -0.0011216 | 0.0060305 | -0.008453 | -0.013733 | -0.054932 | -0.064087 | -0.054932 | 0.068665 | -0.036621 | -0.15564 | -0.022888 | -0.10529 | -0.17395 | 0.032043 | 0.018311 | -0.10071 | -0.16937 | 35.083 | 34.964 | -87.4557 | 35.0647 | 35.0647 | 0.10071 | -87.5381 | 35.0189 | 34.9503 | -87.4924 | 35.0967 | 34.9457 | -0.004577 | -87.5061 | 35.1883 | 35.1059 | 35.0555 | -87.6801 | 35.1517 | 35.1379 | 35.0143 | -87.6938
442.3906 | 122.7081 | -33.3939 | 89.2319 | 0.060425 | 0.013138 | 0.001239 | 0.0051183 | -0.001348 | 0.0020016 | 0.00032053 | -0.065842 | -0.0065731 | -0.0043302 | -0.00090781 | 0.0049625 | -0.0069578 | -0.041199 | -0.07782 | -0.064087 | -0.054932 | 0.059509 | -0.022888 | -0.16479 | -0.054932 | -0.09613 | -0.16022 | 0.068665 | 0.032043 | -0.091553 | -0.16479 | 33.371 | 33.2291 | -89.1724 | 33.316 | 33.3389 | 0.10986 | -89.2731 | 33.3023 | 33.2291 | -89.1632 | 33.3389 | 33.2336 | 0.004578 | -89.1998 | 33.4534 | 33.3527 | 33.3298 | -89.3967 | 33.4625 | 33.4259 | 33.2977 | -89.3967
444.1094 | 122.7264 | -34.4604 | 88.1332 | 0.045166 | 0.010574 | 0.0042298 | 0.0038367 | -0.0039114 | -0.0082522 | -0.0056611 | 0.11726 | -0.0078549 | -0.0051846 | -0.00048061 | -0.0010191 | -0.0046078 | 0.004578 | 0.041199 | 0.045776 | 0.022888 | 0.082397 | 0.036621 | -0.10986 | 0.091553 | 0.13275 | -0.004578 | 0.07782 | 0.032043 | -0.018311 | -0.082397 | 34.4971 | 34.3506 | -88.0508 | 34.5016 | 34.4833 | 0.13275 | -88.1287 | 34.4421 | 34.3781 | -88.0554 | 34.552 | 34.4559 | 0.077819 | -88.1012 | 34.5428 | 34.465 | 34.5062 | -88.2431 | 34.5383 | 34.4925 | 34.5932 | -88.2156
445.8438 | 122.7997 | -38.4384 | 84.0958 | -0.015869 | 0.014206 | 0.0044434 | 0.0053321 | -0.0045522 | -0.005048 | -0.0065155 | 0.079117 | -0.0080685 | -0.0041164 | -0.0028306 | -0.0023007 | -0.0078122 | 0.027466 | 0.032043 | 0.059509 | 0.022888 | 0.10071 | 0.041199 | -0.10529 | 0.10071 | 0.16937 | 0.013733 | 0.068665 | 0.036621 | -0.004578 | -0.082397 | 38.4796 | 38.3331 | -83.9951 | 38.4705 | 38.4613 | 0.12817 | -84.0683 | 38.4338 | 38.356 | -84.0271 | 38.5391 | 38.4521 | 0.09613 | -84.0591 | 38.5391 | 38.4659 | 38.4979 | -84.2011 | 38.5071 | 38.475 | 38.6078 | -84.1782
447.5156 | 122.7219 | -38.1271 | 84.5215 | 0.1062 | 0.014206 | 0.0014526 | 0.0029821 | -0.001348 | 0.0032834 | -0.0054475 | 0.056228 | -0.0023007 | -0.0041164 | 0.0012284 | 0.0045351 | -0.0071714 | -0.036621 | -0.12817 | -0.10529 | -0.082397 | 0.059509 | -0.041199 | -0.20599 | -0.032043 | -0.15106 | -0.16937 | 0.032043 | 0.009155 | -0.10529 | -0.18768 | 38.0859 | 37.9211 | -84.462 | 37.999 | 38.0447 | 0.1236 | -84.5581 | 38.0219 | 37.9395 | -84.4894 | 38.0951 | 37.9578 | 0.01831 | -84.5123 | 38.1866 | 38.0905 | 38.0219 | -84.7275 | 38.1592 | 38.1363 | 37.9761 | -84.7092
449.25 | 122.8226 | -36.85 | 85.6842 | -0.0082397 | 0.012924 | 0.0035888 | 0.0070409 | -0.0026296 | -0.0046206 | -0.0028839 | 0.010452 | -0.0084957 | -0.0017666 | -0.0017624 | 0.0011173 | -0.0069578 | 0.059509 | 0.068665 | 0.082397 | 0.054932 | 0.091553 | 0.027466 | -0.091553 | 0.15106 | 0.2243 | 0.050354 | 0.059509 | 0.050354 | 0.004578 | -0.064087 | 36.8774 | 36.7584 | -85.5927 | 36.9186 | 36.9049 | 0.14649 | -85.6247 | 36.8546 | 36.7859 | -85.6247 | 37.001 | 36.9003 | 0.11444 | -85.6338 | 36.9415 | 36.9095 | 36.9324 | -85.7758 | 36.9095 | 36.9003 | 37.0743 | -85.7483
451 | 122.6624 | -31.279 | 91.3605 | 0.12146 | 0.011002 | 0.0048706 | 0.0019141 | -0.0056204 | -0.00056178 | -0.0022431 | 0.14778 | -0.0059323 | -0.0034756 | 0.001442 | 0.0030399 | -0.0088804 | 0.036621 | 0.036621 | 0.059509 | -0.018311 | 0.022888 | -0.004578 | -0.13733 | 0.10071 | 0.054932 | -0.022888 | 0.004578 | -0.027466 | -0.064087 | -0.12817 | 31.2744 | 31.1417 | -91.3376 | 31.3156 | 31.2607 | 0.11902 | -91.3239 | 31.2149 | 31.1508 | -91.3559 | 31.3797 | 31.2561 | 0.10529 | -91.3879 | 31.3019 | 31.3156 | 31.3385 | -91.4978 | 31.2836 | 31.2515 | 31.3339 | -91.4886
452.6719 | 122.7448 | -29.3152 | 93.3151 | 0.12146 | 0.015488 | 0.0020936 | -8.476e-06 | -0.0030568 | 0.003497 | -0.0041657 | 0.12489 | -0.0067867 | -0.0034756 | 0.001442 | 0.0056033 | -0.0075986 | -0.013733 | -0.082397 | -0.082397 | -0.086975 | 0.059509 | -0.041199 | -0.18768 | 0.032043 | -0.073242 | -0.10986 | 0.032043 | 0.004578 | -0.09613 | -0.15564 | 29.274 | 29.1275 | -93.2556 | 29.2328 | 29.2282 | 0.10071 | -93.3289 | 29.2191 | 29.1595 | -93.2831 | 29.3472 | 29.2053 | 0.045777 | -93.3105 | 29.3747 | 29.3015 | 29.2328 | -93.5028 | 29.3472 | 29.3198 | 29.2419 | -93.4708
454.3906 | 122.7173 | -29.8691 | 92.7292 | 0.022278 | 0.011215 | 0.0033752 | 0.0038367 | -0.0030568 | -0.005048 | -0.0037385 | 0.102 | -0.0080685 | -0.0034756 | 0.00037379 | -0.00037807 | -0.0061032 | 0.032043 | 0.036621 | 0.045776 | 0.009155 | 0.073242 | 0.036621 | -0.11444 | 0.091553 | 0.14648 | -0.004578 | 0.073242 | 0.041199 | -0.009155 | -0.091553 | 29.9057 | 29.7546 | -92.6559 | 29.9057 | 29.8782 | 0.1236 | -92.6971 | 29.8599 | 29.7775 | -92.6559 | 29.9606 | 29.8645 | 0.086975 | -92.688 | 29.9423 | 29.9011 | 29.9149 | -92.8436 | 29.9423 | 29.9103 | 30.0156 | -92.8207
456.125 | 122.6898 | -24.8978 | 97.7646 | 0.045166 | 0.010574 | 0.0052978 | 0.0014867 | -0.0051932 | -0.0031254 | -0.0030975 | 0.079117 | -0.0063595 | -0.0045438 | -0.00069421 | 0.0026125 | -0.0069578 | 0.045776 | 0.050354 | 0.059509 | 0.018311 | 0.07782 | 0.036621 | -0.11444 | 0.10071 | 0.1236 | -0.009155 | 0.059509 | 0.036621 | -0.022888 | -0.091553 | 24.9344 | 24.7833 | -97.6868 | 24.9481 | 24.9161 | 0.13275 | -97.7188 | 24.8749 | 24.8062 | -97.7051 | 24.9985 | 24.8886 | 0.082398 | -97.728 | 24.9756 | 24.9435 | 24.9573 | -97.879 | 24.9573 | 24.9344 | 25.0214 | -97.8561
457.8438 | 122.7905 | -36.7996 | 85.7208 | -0.22949 | 0.013779 | 0.0042298 | 0.0074683 | -0.0051932 | -0.00098918 | -0.0030975 | -0.23369 | -0.0070003 | -0.0036892 | 0.00037379 | 0.00047633 | -0.0078122 | 0.11902 | 0.086975 | 0.10529 | 0.082397 | 0.16479 | 0.07782 | -0.064087 | 0.073242 | 0.13275 | -0.027466 | 0.15564 | 0.1236 | 0 | -0.086975 | 36.8774 | 36.7355 | -85.556 | 36.8866 | 36.882 | 0.14648 | -85.6018 | 36.7996 | 36.7126 | -85.5652 | 36.8729 | 36.7722 | 0.059509 | -85.5972 | 36.9644 | 36.9186 | 36.9049 | -85.7849 | 36.9553 | 36.9232 | 36.9324 | -85.8078
459.5156 | 122.7036 | -35.7147 | 86.9293 | 0.083313 | 0.011215 | 0.0025208 | 0.0053321 | -0.0049796 | -0.0020572 | -0.0033111 | 0.086746 | -0.0076413 | -0.0039028 | -0.0011216 | 0.0032535 | -0.0063168 | 0.045776 | 0.050354 | 0.054932 | 0 | 0.045776 | 0.009155 | -0.14191 | 0.10986 | 0.11902 | -0.009155 | 0.059509 | 0.022888 | -0.013733 | -0.10529 | 35.7239 | 35.5728 | -86.8835 | 35.7651 | 35.7147 | 0.14191 | -86.8835 | 35.701 | 35.6094 | -86.8698 | 35.8246 | 35.7056 | 0.096131 | -86.9064 | 35.7605 | 35.7605 | 35.7697 | -87.0712 | 35.7742 | 35.7376 | 35.8337 | -87.0346
461.25 | 122.7402 | -34.0759 | 88.5315 | 0.13672 | 0.015274 | 0.0027344 | 0.0023413 | -0.001348 | 0.0041378 | -0.0026703 | 0.12489 | -0.0029415 | -0.0064664 | 0.00080099 | 0.0043215 | -0.009094 | -0.004578 | -0.07782 | -0.086975 | -0.073242 | 0.054932 | -0.059509 | -0.20142 | 0.022888 | -0.082397 | -0.11902 | 0.018311 | 0.004578 | -0.091553 | -0.14648 | 34.0164 | 33.8745 | -88.4766 | 33.9981 | 34.0027 | 0.12817 | -88.5361 | 33.9844 | 33.9294 | -88.5132 | 34.0988 | 33.9569 | 0.027465 | -88.5269 | 34.1309 | 34.0713 | 33.989 | -88.7329 | 34.0942 | 34.0805 | 33.9935 | -88.678
462.9844 | 122.818 | -34.8129 | 87.7121 | -0.21423 | 0.014847 | 0.0020936 | 0.0083227 | -0.0051932 | -0.00034818 | -0.0033111 | -0.24895 | -0.0048641 | -0.0013394 | 0.0012284 | 0.00047633 | -0.007385 | 0.10529 | 0.041199 | 0.045776 | 0.045776 | 0.19684 | 0.082397 | -0.059509 | 0.073242 | 0.11444 | -0.045776 | 0.15106 | 0.11444 | -0.018311 | -0.07782 | 34.8953 | 34.7534 | -87.5153 | 34.8541 | 34.8587 | 0.10528 | -87.6068 | 34.7946 | 34.7351 | -87.561 | 34.8862 | 34.7672 | 0.032044 | -87.5977 | 35.0098 | 34.9182 | 34.8587 | -87.7716 | 34.964 | 34.9274 | 34.9274 | -87.7899
464.7031 | 122.699 | -32.0892 | 90.5136 | 0.15961 | 0.011429 | 0.0031616 | 0.0046911 | -0.00092065 | -0.0020572 | -0.0018159 | 0.12489 | -0.0080685 | -0.0030484 | 0.00037379 | 0.00090353 | -0.0063168 | 0.027466 | 0.027466 | 0.073242 | -0.004578 | 0.009155 | -0.009155 | -0.13733 | 0.11444 | 0.10986 | -0.004578 | 0.050354 | 0.022888 | -0.022888 | -0.10529 | 32.0801 | 31.9519 | -90.5045 | 32.1167 | 32.0847 | 0.13275 | -90.4861 | 32.0663 | 31.9839 | -90.4633 | 32.2037 | 32.0847 | 0.10071 | -90.4907 | 32.0984 | 32.1167 | 32.1625 | -90.6509 | 32.1396 | 32.1121 | 32.1991 | -90.6189
466.375 | 122.7356 | -30.0797 | 92.45 | -0.14557 | 0.015915 | 0.0055114 | 0.0085363 | -0.0028432 | -0.0012028 | -0.0024567 | -0.18791 | -0.0063595 | -0.001553 | -0.0013352 | 0.00047633 | -0.0071714 | 0.37994 | 0.35248 | 0.27008 | 0.21057 | 0.13733 | 0.11902 | -0.018311 | 0.15106 | 0.27924 | 0.073242 | 0.10986 | 0.09613 | 0.018311 | -0.041199 | 30.1987 | 30.0613 | -92.3126 | 30.4321 | 30.2902 | 0.22888 | -92.07 | 30.098 | 30.0385 | -92.3401 | 30.2307 | 30.1529 | 0.11444 | -92.3538 | 30.217 | 30.4596 | 30.3497 | -92.4683 | 30.1895 | 30.1758 | 30.3589 | -92.4912
468.1094 | 122.4747 | -54.3823 | 67.662 | -0.21423 | 0.015274 | 0.0016662 | 0.0061865 | -0.0032706 | 0.001788 | -0.0035249 | -0.2108 | -0.0046505 | -0.0036892 | 0.00080099 | 0.0023989 | -0.006744 | 0.091553 | 0.064087 | 0.027466 | 0.050354 | 0.16937 | 0.050354 | -0.073242 | 0.054932 | 0.068665 | -0.059509 | 0.091553 | 0.045776 | -0.050354 | -0.10071 | 54.4327 | 54.3091 | -67.4927 | 54.4464 | 54.4327 | 0.1236 | -67.5705 | 54.332 | 54.2816 | -67.5705 | 54.4373 | 54.3228 | 0.041199 | -67.6163 | 54.5517 | 54.4739 | 54.4098 | -67.7353 | 54.4739 | 54.4281 | 54.451 | -67.7628
469.8438 | 122.5525 | -55.7556 | 66.4261 | -0.069275 | 0.013992 | 0.0055114 | 0.0031957 | -0.0051932 | -0.0054752 | -0.0033111 | -0.12688 | -0.0067867 | -0.0036892 | -0.00069421 | -0.00016447 | -0.0078122 | 0.15564 | 0.19684 | 0.17853 | 0.13275 | 0.12817 | 0.073242 | -0.050354 | 0.16022 | 0.28839 | 0.082397 | 0.10071 | 0.064087 | 0.004578 | -0.041199 | 55.8289 | 55.7053 | -66.2979 | 55.9525 | 55.8884 | 0.18311 | -66.2704 | 55.7602 | 55.7144 | -66.3254 | 55.9158 | 55.838 | 0.1236 | -66.362 | 55.8838 | 55.9113 | 55.9341 | -66.4764 | 55.8563 | 55.8197 | 56.044 | -66.4673
471.5156 | 122.6212 | -58.5342 | 63.6429 | -0.13031 | 0.016769 | 0.0016662 | 0.0021277 | -0.0026296 | 0.003497 | -0.0013885 | -0.22606 | -0.0078549 | -0.003262 | 0.0010148 | 0.0038943 | -0.010162 | 0.054932 | 0.022888 | 0.009155 | 0.036621 | 0.15564 | 0.018311 | -0.10529 | 0.064087 | 0.059509 | -0.045776 | 0.082397 | 0.045776 | -0.036621 | -0.10986 | 58.5526 | 58.429 | -63.4872 | 58.5571 | 58.5709 | 0.14191 | -63.588 | 58.4976 | 58.4244 | -63.5605 | 58.5983 | 58.4885 | 0.064087 | -63.5971 | 58.6899 | 58.5892 | 58.5434 | -63.7482 | 58.6166 | 58.58 | 58.5938 | -63.7527
473.25 | 122.58 | -55.5496 | 66.6962 | -0.13794 | 0.016983 | 0.0023072 | 0.0038367 | -0.0026296 | 0.0013608 | -0.0011749 | -0.16502 | -0.0074277 | -0.0034756 | -0.00048061 | 0.0041079 | -0.007385 | 0.045776 | 0.054932 | 0.018311 | 0.027466 | 0.10986 | -0.004578 | -0.12817 | 0.064087 | 0.059509 | -0.064087 | 0.068665 | 0.036621 | -0.064087 | -0.12817 | 55.545 | 55.4214 | -66.5863 | 55.6046 | 55.5771 | 0.15564 | -66.6504 | 55.4855 | 55.4214 | -66.6275 | 55.6137 | 55.4855 | 0.064087 | -66.6595 | 55.6595 | 55.5954 | 55.5679 | -66.8243 | 55.6183 | 55.5862 | 55.6091 | -66.8243
474.9688 | 122.5571 | -60.91 | 61.3953 | 0.16724 | 0.01207 | 0.0040162 | 0.0012731 | -0.0039114 | -0.00163 | -0.0020295 | 0.15541 | -0.0046505 | -0.0047574 | -0.0011216 | 0.0030399 | -0.003967 | -0.045776 | -0.009155 | -0.045776 | -0.045776 | 0.018311 | -0.045776 | -0.17395 | 0.086975 | 0.013733 | -0.036621 | -0.004578 | -0.018311 | -0.082397 | -0.1236 | 60.8643 | 60.7361 | -61.377 | 60.9009 | 60.8643 | 0.12817 | -61.441 | 60.8276 | 60.7864 | -61.3998 | 60.997 | 60.8734 | 0.086975 | -61.4136 | 60.9283 | 60.8643 | 60.8643 | -61.5692 | 60.9055 | 60.8917 | 60.9238 | -61.5189
476.7188 | 122.5204 | -64.4943 | 57.9254 | 0.12909 | 0.014206 | 0.0033752 | 0.0040503 | -0.0030568 | -0.0020572 | -0.0030975 | 0.17067 | -0.0082821 | -0.006039 | -0.0011216 | 0.0019717 | -0.0052488 | 0.004578 | 0.068665 | 0.068665 | 0.009155 | 0.018311 | 0.004578 | -0.14648 | 0.07782 | 0.059509 | -0.018311 | 0.013733 | -0.013733 | -0.068665 | -0.13275 | 64.4989 | 64.3478 | -57.9071 | 64.563 | 64.5035 | 0.15564 | -57.9208 | 64.4257 | 64.3616 | -57.9117 | 64.5721 | 64.476 | 0.11444 | -57.9391 | 64.5126 | 64.4989 | 64.563 | -58.0719 | 64.5081 | 64.4806 | 64.5538 | -58.0582
478.4688 | 121.1517 | -33.316 | 87.5427 | -0.14557 | 0.013992 | 0.0027344 | 0.0070409 | -0.0062612 | -0.0046206 | -0.0048065 | -0.020065 | -0.0076413 | -0.0013394 | -0.0015488 | -0.0020871 | -0.0075986 | 0.13275 | 0.16937 | 0.17395 | 0.10986 | 0.11902 | 0.082397 | -0.041199 | 0.1831 | 0.3067 | 0.12817 | 0.091553 | 0.068665 | 0.022888 | -0.036621 | 33.3984 | 33.2748 | -87.4237 | 33.4854 | 33.4259 | 0.15106 | -87.41 | 33.3389 | 33.2794 | -87.4512 | 33.4991 | 33.4442 | 0.1648 | -87.4741 | 33.4351 | 33.4488 | 33.49 | -87.5839 | 33.4076 | 33.3847 | 33.6227 | -87.5793
480.1406 | 121.7102 | -30.0842 | 91.4566 | 0.0070193 | 0.011856 | 0.0016662 | 0.0038367 | -0.0011342 | -0.005048 | -0.0030975 | 0.048599 | -0.0078549 | -0.0073208 | -0.00026701 | 0.0013309 | -0.0058896 | 0 | -0.022888 | -0.022888 | -0.059509 | 0.068665 | 0.004578 | -0.13275 | 0.068665 | 0.11902 | -0.027466 | 0.041199 | 0.018311 | -0.054932 | -0.11444 | 30.0888 | 29.9515 | -91.3879 | 30.0613 | 30.0247 | 0.073242 | -91.4566 | 30.0293 | 29.9698 | -91.4154 | 30.1529 | 30.0568 | 0.086975 | -91.4383 | 30.1529 | 30.0842 | 30.0613 | -91.5894 | 30.1254 | 30.1025 | 30.2032 | -91.571
481.875 | 121.8201 | -35.2386 | 86.2793 | -0.11505 | 0.014847 | 0.0025208 | 0.0017005 | -0.0054068 | -0.0041934 | -0.0041657 | -0.042954 | -0.0076413 | -0.0039028 | -0.00026701 | 0.00068993 | -0.0097348 | 0.16479 | 0.16022 | 0.14648 | 0.1236 | 0.12817 | 0.082397 | -0.059509 | 0.19684 | 0.31128 | 0.10986 | 0.10071 | 0.050354 | 0.036621 | -0.032043 | 35.321 | 35.1791 | -86.1511 | 35.3989 | 35.3622 | 0.1831 | -86.1145 | 35.2753 | 35.2066 | -86.1786 | 35.4355 | 35.3485 | 0.14191 | -86.2289 | 35.3668 | 35.4034 | 35.3851 | -86.3388 | 35.3394 | 35.289 | 35.5499 | -86.3113
483.5469 | 121.6141 | -46.2387 | 75.1923 | 0.12909 | 0.01442 | 0.0025208 | 0.0010595 | -0.0028432 | 0.0015744 | -0.0026703 | 0.14778 | -0.0057187 | -0.006039 | 0.0020828 | 0.0070987 | -0.009094 | 0.045776 | 0.013733 | 0.018311 | -0.013733 | 0 | -0.041199 | -0.17853 | 0.07782 | 0.032043 | -0.032043 | -0.032043 | -0.059509 | -0.07782 | -0.14648 | 46.1975 | 46.0602 | -75.1923 | 46.2524 | 46.225 | 0.16479 | -75.1465 | 46.1609 | 46.0922 | -75.2243 | 46.3165 | 46.2067 | 0.11444 | -75.2518 | 46.2387 | 46.2845 | 46.257 | -75.3708 | 46.2067 | 46.1792 | 46.2708 | -75.3387
485.2969 | 121.5729 | -44.8929 | 76.5564 | 0.1825 | 0.013992 | 0.0023072 | 0.00084592 | -0.0049796 | 0.0020016 | -0.0028839 | 0.1783 | -0.0076413 | -0.0036892 | 0.0033646 | 0.0053897 | -0.0063168 | 0.045776 | 0 | 0.018311 | -0.004578 | -0.022888 | -0.036621 | -0.16479 | 0.082397 | 0.045776 | -0.045776 | -0.032043 | -0.054932 | -0.086975 | -0.14191 | 44.8563 | 44.7281 | -76.5793 | 44.8929 | 44.8883 | 0.16022 | -76.5106 | 44.8059 | 44.751 | -76.5884 | 44.9753 | 44.8471 | 0.096131 | -76.6113 | 44.87 | 44.9387 | 44.9112 | -76.7212 | 44.8608 | 44.838 | 44.9387 | -76.6983
487.0312 | 121.7514 | -45.9595 | 75.5402 | -0.22186 | 0.014847 | 0.002948 | 0.0074683 | -0.0028432 | -0.00056178 | -0.0043793 | -0.18791 | -0.0087093 | -0.0017666 | -0.00048061 | -0.00016447 | -0.0078122 | 0.10071 | 0.10071 | 0.086975 | 0.086975 | 0.17853 | 0.086975 | -0.054932 | 0.082397 | 0.15106 | -0.027466 | 0.14191 | 0.10529 | -0.013733 | -0.073242 | 46.0464 | 45.9045 | -75.3616 | 46.0602 | 46.0464 | 0.14191 | -75.4395 | 45.9457 | 45.8862 | -75.3983 | 46.0419 | 45.932 | 0.045776 | -75.4349 | 46.138 | 46.0602 | 46.0464 | -75.5951 | 46.1014 | 46.0648 | 46.1105 | -75.6134
488.7031 | 121.9482 | -73.526 | 47.905 | -0.061646 | 0.014206 | 0.0042298 | 0.0057593 | -0.0032706 | -0.0037662 | -0.0050201 | -0.08873 | -0.0074277 | -0.0041164 | -0.0015488 | -0.00037807 | -0.0080258 | 0.10986 | 0.14191 | 0.12817 | 0.10071 | 0.11444 | 0.064087 | -0.045776 | 0.18768 | 0.25635 | 0.082397 | 0.091553 | 0.050354 | 0.022888 | -0.041199 | 73.5901 | 73.4802 | -47.7905 | 73.6679 | 73.6267 | 0.14648 | -47.7951 | 73.5489 | 73.4848 | -47.8134 | 73.7137 | 73.6084 | 0.1236 | -47.8546 | 73.6404 | 73.6359 | 73.6542 | -47.9507 | 73.6176 | 73.5764 | 73.7823 | -47.9462
490.4688 | 121.8292 | -89.7354 | 31.8054 | 0.029907 | 0.013352 | 0.002948 | 0.0031957 | -0.004125 | -0.0031254 | -0.0033111 | 0.063858 | -0.0087093 | -0.0043302 | 0.00037379 | 0.0015445 | -0.0078122 | 0.050354 | 0.045776 | 0.073242 | 0.041199 | 0.09613 | 0.054932 | -0.10529 | 0.091553 | 0.14648 | -0.004578 | 0.073242 | 0.064087 | -0.018311 | -0.09613 | 89.7903 | 89.6301 | -31.7093 | 89.7812 | 89.7766 | 0.14649 | -31.7551 | 89.7171 | 89.6393 | -31.7322 | 89.827 | 89.7308 | 0.091552 | -31.7413 | 89.8315 | 89.7858 | 89.8087 | -31.9107 | 89.8087 | 89.7995 | 89.8819 | -31.9016
492.2031 | 120.8496 | -60.704 | 60.0082 | 0.14435 | 0.013779 | 0.0038024 | -0.00064948 | -0.0032706 | 0.00093342 | -0.0037385 | 0.13252 | -0.0059323 | -0.0073208 | -0.0011216 | 0.0049625 | -0.0082394 | -0.004578 | -0.064087 | -0.073242 | -0.073242 | 0.045776 | -0.050354 | -0.19226 | 0.050354 | -0.050354 | -0.10071 | 0.022888 | -0.032043 | -0.086975 | -0.16479 | 60.6537 | 60.5118 | -59.9625 | 60.64 | 60.6308 | 0.11902 | -60.0128 | 60.6171 | 60.5392 | -59.9854 | 60.7544 | 60.6033 | 0.064087 | -60.0403 | 60.7498 | 60.6995 | 60.6308 | -60.2005 | 60.7269 | 60.672 | 60.6537 | -60.173
493.9375 | 121.8109 | -91.0172 | 30.4504 | -0.24475 | 0.015274 | 0.002948 | 0.0031957 | -0.0017752 | -0.0014164 | -0.0033111 | -0.18791 | -0.0082821 | -0.006039 | -5.3406e-05 | 0.0017581 | -0.0058896 | 0.13275 | 0.1236 | 0.10529 | 0.07782 | 0.17395 | 0.068665 | -0.054932 | 0.091553 | 0.16937 | -0.004578 | 0.14191 | 0.10071 | -0.004578 | -0.073242 | 91.0858 | 90.9622 | -30.2765 | 91.1407 | 91.095 | 0.13275 | -30.3177 | 91.0126 | 90.9439 | -30.3085 | 91.1087 | 91.0126 | 0.068664 | -30.3497 | 91.1911 | 91.1499 | 91.1224 | -30.5054 | 91.1591 | 91.1179 | 91.1865 | -30.5237
495.6875 | 121.8201 | -93.5623 | 27.9877 | -0.046387 | 0.016769 | 0.004657 | -0.00043588 | -0.0026296 | 0.0024288 | -0.00096127 | -0.14214 | -0.0035825 | -0.0075344 | -0.00026701 | 0.0060305 | -0.0058896 | -0.022888 | -0.018311 | 0.19684 | 0.050354 | 0.12817 | 0.032043 | -0.10071 | -0.054932 | -0.082397 | -0.036621 | 0.064087 | 0.018311 | -0.059509 | -0.1236 | 93.5944 | 93.4616 | -27.8595 | 93.544 | 93.6127 | 0.15106 | -28.0106 | 93.5028 | 93.4387 | -27.9236 | 93.5074 | 93.5257 | 0.086975 | -27.9694 | 93.6905 | 93.5394 | 93.7592 | -28.0884 | 93.6264 | 93.5806 | 93.4799 | -28.1113
497.3594 | 121.8887 | -115.2054 | 6.3538 | -0.19135 | 0.016129 | 0.0040162 | 0.0070409 | -0.0028432 | 0.00029262 | -0.0024567 | -0.23369 | -0.0057187 | -0.0017666 | -0.00048061 | 0.0036807 | -0.0063168 | 0.07782 | 0.045776 | 0.022888 | 0.064087 | 0.16937 | 0.054932 | -0.086975 | 0.036621 | 0.054932 | -0.054932 | 0.091553 | 0.054932 | -0.050354 | -0.13275 | 115.2603 | 115.1184 | -6.1844 | 115.2512 | 115.2695 | 0.15106 | -6.2759 | 115.155 | 115.0726 | -6.2622 | 115.242 | 115.1505 | 0.077819 | -6.2988 | 115.3748 | 115.2832 | 115.2283 | -6.4407 | 115.2969 | 115.2603 | 115.2603 | -6.4865
499.0312 | 121.8658 | -114.6378 | 7.077 | -0.16083 | 0.018906 | 0.0031616 | 0.0085363 | -0.0022024 | 0.00050622 | -0.0018159 | -0.19554 | -0.0061459 | 0.00036957 | 0.00016019 | 0.0021853 | -0.0043942 | 0.045776 | 0.032043 | 0.032043 | 0.032043 | 0.14191 | 0.032043 | -0.10529 | 0.032043 | 0.064087 | -0.054932 | 0.068665 | 0.045776 | -0.054932 | -0.11902 | 114.6698 | 114.5325 | -6.9351 | 114.6698 | 114.6698 | 0.13733 | -7.0312 | 114.5828 | 114.5187 | -7.0084 | 114.6698 | 114.5828 | 0.064087 | -7.0312 | 114.7797 | 114.6835 | 114.6698 | -7.1823 | 114.7064 | 114.6835 | 114.7018 | -7.196
500.7656 | 121.7651 | -118.6798 | 2.9709 | -0.26764 | 0.013138 | 0.0038024 | 0.0040503 | -0.0043386 | -0.005048 | -0.0039521 | -0.18791 | -0.0065731 | -0.0026212 | -0.00048061 | 0.00047633 | -0.0052488 | 0.10071 | 0.15564 | 0.13275 | 0.11444 | 0.14191 | 0.064087 | -0.059509 | 0.10071 | 0.19226 | 0.018311 | 0.14191 | 0.11444 | 0.022888 | -0.036621 | 118.7439 | 118.6203 | -2.829 | 118.8355 | 118.7943 | 0.17395 | -2.8702 | 118.7027 | 118.6432 | -2.829 | 118.7805 | 118.6981 | 0.054932 | -2.8564 | 118.8217 | 118.7805 | 118.8126 | -3.0304 | 118.8217 | 118.7943 | 118.8721 | -3.0075
502.5 | 121.6919 | -119.2841 | 2.1973 | 0.098572 | 0.018051 | 0.0031616 | -0.0012903 | -0.0047658 | 0.00029262 | -0.0024567 | 0.071487 | -0.0037961 | -0.0058254 | 0.0016556 | 0.0058169 | -0.0071714 | -0.17395 | -0.21973 | -0.15564 | -0.17395 | -0.068665 | -0.16937 | -0.31586 | -0.09613 | -0.16479 | -0.24261 | -0.073242 | -0.09613 | -0.21515 | -0.28839 | 119.1147 | 118.9682 | -2.2659 | 119.0643 | 119.1101 | 0.14191 | -2.3712 | 119.0689 | 118.9957 | -2.2705 | 119.1879 | 119.0414 | 0.045776 | -2.2934 | 119.2154 | 119.1101 | 119.1284 | -2.5131 | 119.2108 | 119.1879 | 119.1193 | -2.4857
504.1719 | 121.7102 | -114.798 | 6.7795 | 0.022278 | 0.016129 | 0.0031616 | 0.00084592 | -0.0032706 | 0.0030698 | -0.00074767 | 0.0028229 | -0.00080533 | -0.0041164 | -0.001976 | 0.0045351 | -0.0065304 | -0.19226 | -0.20599 | -0.17395 | -0.15564 | -0.022888 | -0.12817 | -0.2655 | -0.050354 | -0.050354 | -0.16022 | 0 | 0.004578 | -0.10529 | -0.18768 | 114.6698 | 114.5325 | -6.8024 | 114.592 | 114.6423 | 0.10986 | -6.9717 | 114.6927 | 114.6103 | -6.7795 | 114.7476 | 114.6378 | 0.027466 | -6.7749 | 114.7751 | 114.6057 | 114.624 | -7.045 | 114.798 | 114.8026 | 114.7476 | -6.9672
505.9062 | 121.5637 | -3.4607 | 117.9703 | -0.092163 | 0.013138 | 0.0059388 | 0.0061865 | -0.004125 | -0.007825 | -0.0054475 | -0.042954 | -0.0076413 | -0.0041164 | 0.00058739 | -0.0016599 | -0.003967 | 0.1236 | 0.17395 | 0.16479 | 0.11444 | 0.16022 | 0.11902 | -0.041199 | 0.15106 | 0.2655 | 0.082397 | 0.036621 | 0.013733 | -0.036621 | -0.091553 | 3.5797 | 3.4195 | -117.8101 | 3.6346 | 3.5751 | 0.15564 | -117.8467 | 3.4241 | 3.3691 | -117.9337 | 3.6118 | 3.5431 | 0.17395 | -117.9565 | 3.6209 | 3.5843 | 3.6255 | -118.0115 | 3.4973 | 3.4744 | 3.7262 | -118.0618
507.6406 | 121.3623 | -0.3067 | 121.1105 | 0.11383 | 0.013779 | 0.0025208 | 0.00041872 | -0.0043386 | 0.00071982 | -0.0024567 | 0.12489 | -0.0052915 | -0.003262 | -0.00048061 | 0.0047489 | -0.0086666 | -0.036621 | -0.09613 | -0.086975 | -0.073242 | 0.059509 | -0.050354 | -0.18768 | -0.009155 | -0.09613 | -0.10986 | 0.032043 | -0.009155 | -0.073242 | -0.16022 | 0.25635 | 0.11902 | -121.051 | 0.21057 | 0.23346 | 0.11444 | -121.1472 | 0.23346 | 0.14648 | -121.0785 | 0.29755 | 0.19684 | 0.050354 | -121.1197 | 0.36621 | 0.27008 | 0.21973 | -121.2982 | 0.33874 | 0.29755 | 0.21057 | -121.2708
509.3125 | 121.3074 | -0.073242 | 121.0785 | -0.19897 | 0.016556 | 0.0027344 | 0.0076819 | -0.0017752 | 7.902e-05 | -0.0045929 | -0.18791 | -0.0067867 | -0.0021938 | 0.0016556 | 0.0011173 | -0.010589 | 0.059509 | 0.022888 | 0.022888 | 0.041199 | 0.16937 | 0.050354 | -0.10529 | 0.013733 | 0.068665 | -0.064087 | 0.13275 | 0.091553 | -0.041199 | -0.10529 | 0.1236 | -0.032044 | -120.9091 | 0.09613 | 0.11444 | 0.14649 | -121.019 | 0.032043 | -0.032044 | -120.9457 | 0.086975 | 0.009155 | 0.041199 | -120.9869 | 0.24261 | 0.13275 | 0.09613 | -121.1838 | 0.20599 | 0.16479 | 0.14191 | -121.1838
511.0469 | 121.6003 | -0.09613 | 121.3852 | -0.19135 | 0.018265 | 0.0025208 | 0.0057593 | -0.0019888 | 0.0020016 | -0.00096127 | -0.16502 | -0.0050777 | -0.00069863 | 0.0016556 | 0.0015445 | -0.0093076 | 0.064087 | 0.041199 | 0.027466 | 0.059509 | 0.16022 | 0.059509 | -0.068665 | 0.022888 | 0.068665 | -0.064087 | 0.11444 | 0.073242 | -0.050354 | -0.11444 | 0.15564 | 0.027465 | -121.225 | 0.13733 | 0.15564 | 0.12817 | -121.3211 | 0.045776 | -0.018311 | -121.2708 | 0.11902 | 0.032043 | 0.050354 | -121.312 | 0.25635 | 0.16022 | 0.1236 | -121.4539 | 0.21057 | 0.16937 | 0.16479 | -121.4996
512.7812 | 117.5034 | -36.7859 | 80.8182 | -0.061646 | 0.012924 | 0.0018798 | 0.0072547 | -0.0028432 | -0.0073978 | -0.0050201 | -0.0048066 | -0.0099911 | -0.0017666 | -5.3406e-05 | -0.0035825 | -0.005676 | 0.25635 | 0.36163 | 0.44403 | 0.48523 | 0.25635 | 0.25635 | 0.13733 | 0.14648 | 0.26093 | 0.064087 | 0.10529 | 0.068665 | 0.013733 | -0.059509 | 37.0422 | 36.9232 | -80.5618 | 37.1475 | 37.2711 | 0.3479 | -80.5618 | 36.7996 | 36.7264 | -80.7129 | 36.9324 | 36.85 | 0.1236 | -80.7495 | 37.0422 | 37.0422 | 37.2299 | -80.6808 | 36.8912 | 36.8546 | 37.0468 | -80.8777
514.5156 | 116.4688 | -43.0618 | 73.0911 | -0.054016 | 0.016769 | -4.2814e-05 | 0.0051183 | -0.0017752 | 0.0028562 | -0.00010687 | -0.10399 | -0.0065731 | -0.0036892 | 0.0018692 | 0.0049625 | -0.0080258 | -0.33875 | -0.25177 | -0.23346 | -0.27008 | 0.082397 | -0.091553 | -0.25635 | 0.07782 | 0.022888 | -0.054932 | -0.045776 | -0.045776 | -0.12817 | -0.18768 | 42.9703 | 42.8055 | -73.0087 | 42.8101 | 42.7917 | -0.013733 | -73.4299 | 42.9337 | 42.8741 | -73.1369 | 43.1396 | 43.0069 | 0.13275 | -73.1369 | 43.1442 | 42.7231 | 42.8284 | -73.3475 | 43.0161 | 43.0161 | 43.0847 | -73.2788
516.1875 | 121.0373 | -16.5024 | 104.6127 | 0.13672 | 0.012283 | 0.0023072 | 0.0019141 | -0.0039114 | -0.0056888 | -0.0045929 | 0.19356 | -0.0080685 | -0.0041164 | -0.0013352 | 0.0032535 | -0.0058896 | 0.027466 | 0.041199 | 0.059509 | -0.009155 | 0.004578 | -0.009155 | -0.14191 | 0.082397 | 0.073242 | -0.009155 | 0.018311 | 0 | -0.073242 | -0.13733 | 16.4932 | 16.3605 | -104.6082 | 16.5436 | 16.4932 | 0.13275 | -104.5853 | 16.4291 | 16.3651 | -104.5944 | 16.5848 | 16.4932 | 0.12817 | -104.6127 | 16.507 | 16.5298 | 16.5619 | -104.7546 | 16.5207 | 16.5024 | 16.5756 | -104.7501
517.9219 | 121.2982 | -21.8079 | 99.2889 | -0.14557 | 0.015488 | 0.0010254 | 0.0068273 | -0.00092065 | 0.0011472 | -0.0028839 | -0.17265 | -0.0055051 | -0.0034756 | 0.0020828 | 0.0028263 | -0.008453 | 0.064087 | 0.027466 | 0 | 0.041199 | 0.15564 | 0.027466 | -0.11902 | 0.059509 | 0.054932 | -0.054932 | 0.073242 | 0.068665 | -0.054932 | -0.13733 | 21.8353 | 21.6888 | -99.1333 | 21.8353 | 21.8491 | 0.16022 | -99.2249 | 21.7529 | 21.6705 | -99.2157 | 21.8674 | 21.7529 | 0.082397 | -99.2203 | 21.9635 | 21.8719 | 21.8079 | -99.408 | 21.8811 | 21.8765 | 21.8628 | -99.4263
519.5938 | 121.3028 | -19.1345 | 102.0172 | -0.21423 | 0.01442 | 0.0035888 | 0.0066137 | -0.004125 | -0.0059024 | -0.0026703 | -0.18028 | -0.0087093 | -0.0028348 | -0.001976 | -0.0010191 | -0.0063168 | 0.13275 | 0.14648 | 0.13733 | 0.10986 | 0.15564 | 0.073242 | -0.032043 | 0.10529 | 0.22888 | 0.027466 | 0.13275 | 0.091553 | 0.004578 | -0.064087 | 19.2078 | 19.1025 | -101.8616 | 19.281 | 19.2444 | 0.14191 | -101.8845 | 19.1391 | 19.0704 | -101.8845 | 19.2398 | 19.162 | 0.091553 | -101.9257 | 19.2902 | 19.2673 | 19.2719 | -102.0493 | 19.2673 | 19.2261 | 19.3634 | -102.0813
521.3281 | 121.2845 | -63.8947 | 57.2479 | 0.1062 | 0.011643 | 0.004657 | 0.0029821 | -0.0032706 | -0.0031254 | -0.0035249 | 0.17067 | -0.0076413 | -0.003262 | -0.0017624 | 0.0043215 | -0.007385 | 0.009155 | 0.036621 | 0.036621 | -0.032043 | 0.018311 | -0.022888 | -0.14191 | 0.09613 | 0.086975 | -0.013733 | 0.018311 | 0.004578 | -0.041199 | -0.11444 | 63.8718 | 63.7527 | -57.2296 | 63.9313 | 63.8626 | 0.10986 | -57.2388 | 63.8535 | 63.7802 | -57.2296 | 63.9908 | 63.8809 | 0.10071 | -57.2433 | 63.913 | 63.9038 | 63.9313 | -57.3898 | 63.913 | 63.8992 | 63.9816 | -57.3624
523 | 121.3852 | -61.8027 | 59.3674 | 0.1825 | 0.013992 | 0.0031616 | 0.0036231 | -0.0045522 | 0.00093342 | -0.0016021 | 0.14015 | -0.0059323 | -0.0039028 | 0.00016019 | 0.0060305 | -0.0071714 | -0.17853 | -0.18768 | -0.09613 | -0.13733 | -0.20142 | -0.25177 | -0.36621 | 0.073242 | 0.022888 | -0.054932 | -0.018311 | -0.036621 | -0.082397 | -0.15106 | 61.5509 | 61.4365 | -59.5688 | 61.615 | 61.6653 | 0.22888 | -59.5459 | 61.7203 | 61.6516 | -59.3857 | 61.8759 | 61.7477 | 0.09613 | -59.404 | 61.6013 | 61.6241 | 61.7065 | -59.7336 | 61.7844 | 61.7661 | 61.8256 | -59.5184
524.7344 | 121.2891 | -85.4736 | 35.4858 | -0.076904 | 0.014206 | 0.0027344 | 0.0081091 | -0.0064748 | -0.0041934 | -0.0048065 | -0.035324 | -0.0084957 | -0.001553 | -0.0011216 | -0.0012327 | -0.0065304 | 0.37537 | 0.70038 | 0.14648 | -0.19684 | 0.15106 | 0.091553 | -0.050354 | 0.050354 | 0.050354 | -0.07782 | 0.068665 | 0.050354 | -0.013733 | -0.082397 | 85.5652 | 85.4233 | -35.3348 | 86.174 | 85.2768 | -0.14648 | -35.1105 | 85.4599 | 85.3912 | -35.4172 | 85.524 | 85.3958 | 0.004577 | -35.4355 | 85.6247 | 85.849 | 85.6201 | -35.5362 | 85.5423 | 85.524 | 85.524 | -35.5682
526.4688 | 120.8313 | -60.2646 | 61.0062 | 0.14435 | 0.016129 | 0.002948 | 0.0036231 | -0.0043386 | 0.0043514 | -0.0035249 | 0.04097 | -0.0037961 | -0.0030484 | 0.001442 | 0.0015445 | -0.008453 | -0.018311 | -0.091553 | -0.091553 | -0.082397 | 0.073242 | -0.045776 | -0.20142 | 0.004578 | -0.11902 | -0.12817 | 0.050354 | 0.041199 | -0.11444 | -0.16479 | 60.2188 | 60.0632 | -60.9329 | 60.173 | 60.1822 | 0.11902 | -61.0245 | 60.1501 | 60.0998 | -60.9558 | 60.2692 | 60.1364 | 0.036621 | -60.965 | 60.3378 | 60.2463 | 60.173 | -61.2076 | 60.3149 | 60.3058 | 60.1456 | -61.171
528.25 | 121.4172 | -112.7747 | 8.4 | 0.16724 | 0.012497 | 0.0044434 | 0.0012731 | -0.0054068 | -0.0029118 | -0.0016021 | 0.17067 | -0.0072141 | -0.00668 | 0.001442 | 0.0053897 | -0.005676 | 0.032043 | 0.013733 | -0.022888 | -0.032043 | 0 | -0.036621 | -0.16022 | 0.068665 | 0.054932 | -0.045776 | -0.022888 | -0.041199 | -0.07782 | -0.16479 | 112.738 | 112.6144 | -8.4 | 112.7884 | 112.7426 | 0.12817 | -8.3679 | 112.6968 | 112.6099 | -8.4229 | 112.8433 | 112.7289 | 0.11902 | -8.4412 | 112.7747 | 112.8067 | 112.7518 | -8.5602 | 112.7518 | 112.7335 | 112.8296 | -8.5648
529.9844 | 121.4676 | -114.8346 | 6.3675 | -0.18372 | 0.015701 | 0.0042298 | 0.0072547 | -0.0062612 | -0.0031254 | -0.0054475 | -0.18028 | -0.0059323 | -0.0028348 | -0.0024032 | -0.00037807 | -0.0071714 | 0.10071 | 0.073242 | 0.054932 | 0.054932 | 0.25635 | 0.13275 | -0.036621 | 0.10071 | 0.15106 | -0.018311 | 0.15106 | 0.11902 | -0.013733 | -0.073242 | 114.9673 | 114.798 | -6.1111 | 114.9078 | 114.8895 | 0.091553 | -6.2668 | 114.8209 | 114.7614 | -6.2164 | 114.9353 | 114.8163 | 0.054931 | -6.2485 | 115.0909 | 114.9353 | 114.8895 | -6.4041 | 114.9857 | 114.9536 | 114.9857 | -6.4407
531.7656 | 121.3257 | -98.9456 | 22.3068 | 0.14435 | 0.016983 | 0.002948 | 0.0017005 | -0.0047658 | 0.0024288 | -0.00053407 | 0.14015 | -0.0063595 | -0.003262 | 0.00037379 | 0.0038943 | -0.0080258 | -0.054932 | -0.036621 | -0.036621 | -0.10529 | 0.036621 | -0.064087 | -0.19226 | 0.068665 | -0.036621 | -0.068665 | 0.018311 | -0.018311 | -0.086975 | -0.16479 | 98.8815 | 98.7534 | -22.2702 | 98.909 | 98.8403 | 0.086975 | -22.3618 | 98.8586 | 98.7808 | -22.2885 | 99.0143 | 98.877 | 0.09613 | -22.3251 | 98.9822 | 98.8907 | 98.909 | -22.4991 | 98.9639 | 98.9273 | 98.909 | -22.4716
533.4531 | 121.2936 | -6.134 | 115.1001 | -0.17609 | 0.015488 | 0.0044434 | 0.0057593 | -0.0028432 | -0.0039798 | -0.0054475 | -0.15739 | -0.0078549 | -0.0021938 | -0.00069421 | 0.00090353 | -0.010376 | 0.14648 | 0.19226 | 0.17395 | 0.1236 | 0.14648 | 0.091553 | -0.032043 | 0.1831 | 0.29755 | 0.09613 | 0.10071 | 0.068665 | 0.022888 | -0.050354 | 6.2256 | 6.102 | -114.9536 | 6.3263 | 6.2576 | 0.15564 | -114.9536 | 6.1569 | 6.0837 | -114.9994 | 6.3171 | 6.2302 | 0.14648 | -115.0314 | 6.2805 | 6.2805 | 6.308 | -115.1321 | 6.2347 | 6.2027 | 6.4316 | -115.1505
535.125 | 121.312 | -4.7836 | 116.6016 | -0.061646 | 0.015701 | 0.0033752 | 0.0014867 | -0.0034842 | 0.0041378 | -0.0026703 | -0.15739 | -0.0029415 | -0.0068936 | -0.00048061 | 0.0047489 | -0.0093076 | 0.082397 | 0.027466 | 0.018311 | 0 | 0.11444 | -0.004578 | -0.13275 | 0.054932 | 0.013733 | -0.086975 | 0.068665 | 0.054932 | -0.068665 | -0.13733 | 4.7791 | 4.6509 | -116.4871 | 4.8111 | 4.7836 | 0.13275 | -116.5192 | 4.715 | 4.6463 | -116.5329 | 4.8386 | 4.6967 | 0.050354 | -116.5466 | 4.8981 | 4.866 | 4.8019 | -116.7343 | 4.8523 | 4.8386 | 4.7974 | -116.7389
536.8594 | 121.3211 | -4.8248 | 116.629 | -0.0082397 | 0.017197 | 0.0038024 | 0.00084592 | -0.002416 | 0.003497 | -0.0024567 | -0.020065 | -0.0059323 | -0.0036892 | 0.00058739 | 0.0045351 | -0.0078122 | -0.045776 | -0.082397 | -0.073242 | -0.068665 | 0.082397 | -0.041199 | -0.17853 | -0.041199 | -0.10071 | -0.16479 | 0.054932 | 0.036621 | -0.10529 | -0.17395 | 4.7836 | 4.6463 | -116.5466 | 4.7424 | 4.7562 | 0.10986 | -116.6748 | 4.7195 | 4.6509 | -116.5741 | 4.7836 | 4.66 | 0.009155 | -116.5924 | 4.9072 | 4.7791 | 4.7516 | -116.8076 | 4.8798 | 4.8615 | 4.7241 | -116.803
538.5781 | 121.3715 | -4.6692 | 116.7938 | 0.022278 | 0.014633 | 0.001239 | 0.0029821 | -0.0043386 | 0.001788 | -0.0011749 | 0.048599 | -0.0048641 | -0.0028348 | 0.00058739 | 0.0047489 | -0.0052488 | -0.032043 | -0.086975 | -0.07782 | -0.068665 | 0.073242 | -0.032043 | -0.1831 | -0.032043 | -0.09613 | -0.16479 | 0.050354 | 0.041199 | -0.091553 | -0.17395 | 4.6371 | 4.4861 | -116.7206 | 4.5822 | 4.6005 | 0.11444 | -116.8259 | 4.5776 | 4.4952 | -116.7435 | 4.6371 | 4.5044 | 0.009155 | -116.7526 | 4.7424 | 4.6371 | 4.5914 | -116.9769 | 4.7195 | 4.7104 | 4.5731 | -116.9678
540.2812 | 120.6802 | -90.5869 | 29.7638 | 0.17487 | 0.015701 | 0.0023072 | 0.0027685 | -0.0043386 | 0.00050622 | -0.0026703 | 0.071487 | -0.0046505 | -0.0043302 | 0.0012284 | 0.0036807 | -0.0086666 | -0.086975 | -0.10986 | -0.09613 | -0.082397 | 0.054932 | -0.041199 | -0.19684 | 0.004578 | -0.09613 | -0.091553 | 0.045776 | 0.032043 | -0.086975 | -0.14648 | 90.5457 | 90.39 | -29.7089 | 90.477 | 90.5045 | 0.11444 | -29.8508 | 90.4999 | 90.4404 | -29.718 | 90.5914 | 90.4953 | 0.054931 | -29.7318 | 90.6418 | 90.4999 | 90.4907 | -29.9606 | 90.6326 | 90.6189 | 90.4907 | -29.9103
542.0312 | 120.8862 | -109.7305 | 10.9177 | 0.083313 | 0.016769 | 0.0042298 | 0.0019141 | -0.002416 | 0.00050622 | -0.0016021 | 0.025711 | -0.0035825 | -0.0045438 | -0.00026701 | 0.0047489 | -0.0078122 | -0.064087 | -0.12817 | -0.10986 | -0.068665 | 0.082397 | -0.041199 | -0.17853 | -0.073242 | -0.11444 | -0.18768 | 0.041199 | 0.036621 | -0.09613 | -0.16937 | 109.6893 | 109.552 | -10.8353 | 109.6024 | 109.6619 | 0.10986 | -10.9818 | 109.6344 | 109.5612 | -10.8765 | 109.6573 | 109.5428 | -0.01831 | -10.881 | 109.8129 | 109.6664 | 109.6207 | -11.0962 | 109.7717 | 109.7672 | 109.6161 | -11.087
543.7344 | 120.9824 | -109.8999 | 10.8948 | 0.052795 | 0.012711 | 0.0035888 | 0.0055457 | -0.0028432 | -0.0052616 | -0.0024567 | 0.14015 | -0.0076413 | -0.006039 | 0.00037379 | 0.00068993 | -0.0048214 | 0.009155 | 0.027466 | 0.064087 | 0.018311 | 0.07782 | 0.027466 | -0.11444 | 0.07782 | 0.1236 | -0.004578 | 0.068665 | 0.032043 | -0.013733 | -0.09613 | 109.9274 | 109.7855 | -10.817 | 109.9274 | 109.9182 | 0.13275 | -10.8856 | 109.8862 | 109.8038 | -10.8261 | 109.9777 | 109.8953 | 0.091552 | -10.8627 | 109.9777 | 109.9091 | 109.964 | -11.0092 | 109.9686 | 109.9319 | 110.0235 | -10.9909
545.5 | 121.0373 | -119.3939 | 1.5015 | 0.098572 | 0.014206 | 0.0040162 | 0.0040503 | -0.0047658 | -0.0037662 | -0.0043793 | 0.20119 | -0.0070003 | -0.0026212 | 0.00058739 | 0.0011173 | -0.005676 | 0.022888 | 0.027466 | 0.027466 | -0.004578 | 0.027466 | -0.018311 | -0.14648 | 0.07782 | 0.086975 | -0.009155 | 0.018311 | 0 | -0.050354 | -0.10529 | 119.3756 | 119.2474 | -1.474 | 119.4214 | 119.3893 | 0.14191 | -1.4786 | 119.3436 | 119.2886 | -1.4832 | 119.4717 | 119.3848 | 0.096131 | -1.5015 | 119.4214 | 119.4168 | 119.4214 | -1.6479 | 119.4122 | 119.3939 | 119.4809 | -1.6068
547.1875 | 121.1014 | -119.9524 | 1.03 | -0.031128 | 0.019119 | 0.00081179 | 0.0025549 | -0.0039114 | 0.0028562 | -0.0016021 | -0.042954 | -0.0031551 | -0.0056118 | 0.00037379 | 0.0051761 | -0.0097348 | 0.041199 | -0.041199 | -0.022888 | -0.018311 | 0.10071 | -0.009155 | -0.16479 | -0.013733 | -0.082397 | -0.12817 | 0.041199 | 0.032043 | -0.07782 | -0.16937 | 119.9432 | 119.7876 | -0.92926 | 119.9112 | 119.9341 | 0.14648 | -0.98877 | 119.8746 | 119.783 | -0.98877 | 119.9387 | 119.8242 | 0.041199 | -0.99792 | 120.0531 | 119.9936 | 119.9295 | -1.1948 | 119.9936 | 119.9844 | 119.87 | -1.1993
548.8906 | 121.1517 | -119.9295 | 1.1353 | 0.037537 | 0.010147 | 0.0057252 | 0.0036231 | -0.004125 | -0.0071842 | -0.0028839 | 0.11726 | -0.0080685 | -0.0064664 | 0.0012284 | 0.00090353 | -0.0082394 | 0.032043 | 0.018311 | 0.050354 | 0.022888 | 0.086975 | 0.018311 | -0.10529 | 0.082397 | 0.1236 | -0.018311 | 0.064087 | 0.050354 | -0.041199 | -0.091553 | 119.9478 | 119.8242 | -1.0483 | 119.9478 | 119.9524 | 0.12817 | -1.1032 | 119.8883 | 119.838 | -1.0712 | 120.0119 | 119.9112 | 0.073242 | -1.0849 | 120.0165 | 119.9615 | 119.9799 | -1.2405 | 119.9936 | 119.9799 | 120.0531 | -1.2268
550.5625 | 121.17 | -119.9661 | 1.1398 | 0.022278 | 0.015701 | 0.0040162 | 0.00063232 | -0.0026296 | 0.003497 | -0.0020295 | 0.04097 | -0.0050777 | -0.004971 | -0.00069421 | 0.0049625 | -0.010162 | -0.045776 | -0.15564 | -0.10986 | -0.086975 | 0.07782 | -0.050354 | -0.17853 | -0.041199 | -0.12817 | -0.17853 | 0.041199 | 0.009155 | -0.10071 | -0.16479 | 119.9158 | 119.7876 | -1.062 | 119.8105 | 119.8792 | 0.091553 | -1.1856 | 119.8654 | 119.8013 | -1.0986 | 119.9249 | 119.7876 | -0.013733 | -1.1307 | 120.0439 | 119.9203 | 119.8563 | -1.3184 | 120.0073 | 119.9753 | 119.838 | -1.3046
552.2344 | 121.3303 | -120.1401 | 0.90179 | -0.12268 | 0.017624 | 0.0031616 | 0.0061865 | -0.0039114 | 0.00050622 | -0.0026703 | -0.16502 | -0.0046505 | -0.003262 | 0.00080099 | 0.0015445 | -0.0086666 | 0.086975 | 0.013733 | 0.013733 | 0.013733 | 0.12817 | -0.004578 | -0.13275 | 0.054932 | 0.054932 | -0.064087 | 0.073242 | 0.054932 | -0.073242 | -0.12817 | 120.1355 | 120.0073 | -0.77362 | 120.1538 | 120.1538 | 0.14648 | -0.81482 | 120.0668 | 120.0119 | -0.82855 | 120.195 | 120.076 | 0.064087 | -0.84686 | 120.2682 | 120.2271 | 120.1538 | -1.0345 | 120.2133 | 120.195 | 120.195 | -1.03
553.9219 | 121.257 | -120.5887 | 0.54016 | 0.15198 | 0.013352 | 0.0040162 | -0.0015039 | -0.0036978 | -0.0020572 | -0.0043793 | 0.20119 | -0.0061459 | -0.0034756 | 0.0010148 | 0.0051761 | -0.0065304 | 0.032043 | 0 | 0.018311 | 0 | 0.013733 | -0.032043 | -0.17853 | 0.07782 | 0.032043 | -0.022888 | -0.018311 | -0.022888 | -0.07782 | -0.14648 | 120.5566 | 120.4102 | -0.52643 | 120.5887 | 120.5887 | 0.17853 | -0.50812 | 120.5109 | 120.4422 | -0.55847 | 120.6665 | 120.5658 | 0.1236 | -0.56305 | 120.6024 | 120.6207 | 120.607 | -0.71869 | 120.5704 | 120.5658 | 120.6207 | -0.68664
555.6094 | 121.3898 | -120.6985 | 0.4303 | -0.2066 | 0.013565 | 0.001239 | 0.0057593 | -0.0032706 | 0.0015744 | -0.0045929 | -0.058212 | -0.0048641 | -0.00091223 | 0.00037379 | 0.0036807 | -0.008453 | 0.07782 | 0.041199 | 0.032043 | 0.045776 | 0.17395 | 0.068665 | -0.09613 | 0.045776 | 0.045776 | -0.054932 | 0.07782 | 0.064087 | -0.068665 | -0.1236 | 120.7672 | 120.6024 | -0.25635 | 120.7397 | 120.7443 | 0.14191 | -0.35248 | 120.6299 | 120.575 | -0.35248 | 120.7443 | 120.6436 | 0.068664 | -0.36621 | 120.8725 | 120.7764 | 120.7306 | -0.52643 | 120.7764 | 120.7626 | 120.7443 | -0.55389
557.2812 | 121.3531 | -120.6619 | 0.51727 | -0.17609 | 0.014633 | 0.0042298 | 0.0055457 | -0.004125 | -0.0056888 | -0.0037385 | -0.073471 | -0.0076413 | -0.0024076 | 0.00080099 | -0.00016447 | -0.0080258 | 0.14191 | 0.16479 | 0.16937 | 0.11902 | 0.14648 | 0.086975 | -0.054932 | 0.14191 | 0.29297 | 0.068665 | 0.082397 | 0.073242 | 0 | -0.045776 | 120.7489 | 120.607 | -0.37079 | 120.8267 | 120.7809 | 0.17395 | -0.37537 | 120.6619 | 120.6161 | -0.43488 | 120.8038 | 120.7306 | 0.11444 | -0.44403 | 120.8084 | 120.8038 | 120.8313 | -0.5722 | 120.7443 | 120.7352 | 120.9549 | -0.56305
558.9375 | 121.3348 | -120.7855 | 0.39825 | 0.1062 | 0.014206 | 0.0042298 | 0.0014867 | -0.0017752 | 0.0013608 | -0.0028839 | 0.14778 | -0.0050777 | -0.0047574 | 0.0020828 | 0.0056033 | -0.0061032 | -0.036621 | -0.091553 | -0.07782 | -0.073242 | 0.064087 | -0.064087 | -0.16937 | 0.018311 | -0.086975 | -0.09613 | 0.022888 | 0 | -0.09613 | -0.16022 | 120.7214 | 120.6161 | -0.33417 | 120.694 | 120.7123 | 0.096131 | -0.43488 | 120.6894 | 120.6253 | -0.37537 | 120.8038 | 120.6894 | 0.064087 | -0.39825 | 120.8496 | 120.7489 | 120.7077 | -0.56763 | 120.8084 | 120.7855 | 120.6985 | -0.55847
560.625 | 121.344 | -120.845 | 0.39825 | 0.075684 | 0.016129 | 0.0040162 | 0.0012731 | -0.0039114 | 0.0022152 | -0.0028839 | 0.10963 | -0.0037961 | -0.0045438 | 0.001442 | 0.0032535 | -0.0058896 | -0.050354 | -0.1236 | -0.11902 | -0.09613 | 0.082397 | -0.073242 | -0.19684 | -0.032043 | -0.13275 | -0.16937 | 0.022888 | 0.027466 | -0.10071 | -0.16937 | 120.7718 | 120.6482 | -0.31586 | 120.7214 | 120.7489 | 0.10071 | -0.44861 | 120.7443 | 120.6757 | -0.37537 | 120.813 | 120.6757 | 0 | -0.37079 | 120.9274 | 120.7947 | 120.726 | -0.59509 | 120.8679 | 120.8725 | 120.7123 | -0.56763
562.2969 | 121.4813 | -120.8405 | 0.37537 | -0.19897 | 0.01741 | 0.002948 | 0.0091773 | -0.0032706 | -0.00034818 | -0.0024567 | -0.17265 | -0.0076413 | -0.0041164 | 0.00037379 | 0.00068993 | -0.0065304 | 0.073242 | 0 | 0.022888 | 0.045776 | 0.1831 | 0.050354 | -0.07782 | 0.036621 | 0.07782 | -0.064087 | 0.10986 | 0.086975 | -0.050354 | -0.09613 | 120.8908 | 120.7626 | -0.19226 | 120.8405 | 120.8862 | 0.1236 | -0.30212 | 120.7901 | 120.7443 | -0.2655 | 120.8771 | 120.7764 | 0.032043 | -0.28839 | 121.0236 | 120.9137 | 120.8633 | -0.45319 | 120.9503 | 120.9274 | 120.9183 | -0.4715
564.0156 | 121.3898 | -120.4559 | 0.8194 | 0.12909 | 0.014847 | 0.0023072 | 0.00063232 | -0.0045522 | -0.0041934 | -0.0037385 | 0.20882 | -0.0078549 | -0.004971 | -5.3406e-05 | 0.0023989 | -0.009094 | 0.009155 | 0 | 0.018311 | -0.013733 | 0.009155 | -0.045776 | -0.1831 | 0.073242 | 0.050354 | -0.027466 | -0.027466 | -0.041199 | -0.09613 | -0.16022 | 120.4102 | 120.2728 | -0.81024 | 120.4559 | 120.4422 | 0.16937 | -0.81024 | 120.3598 | 120.2957 | -0.84686 | 120.5292 | 120.4285 | 0.13275 | -0.8606 | 120.4651 | 120.4651 | 120.4742 | -1.0025 | 120.4285 | 120.4147 | 120.5063 | -0.97961
565.6875 | 121.3531 | -120.5292 | 0.79651 | 0.029907 | 0.014633 | 0.0010254 | 0.0053321 | -0.0047658 | 0.00050622 | -0.0018159 | 0.0028229 | -0.0084957 | -0.0051846 | 0.0012284 | 0.0038943 | -0.0063168 | -0.041199 | -0.10071 | -0.073242 | -0.054932 | 0.068665 | -0.027466 | -0.1831 | -0.045776 | -0.086975 | -0.16479 | 0.050354 | 0.027466 | -0.09613 | -0.17853 | 120.5017 | 120.3461 | -0.72784 | 120.4285 | 120.4742 | 0.12817 | -0.83771 | 120.433 | 120.3506 | -0.74616 | 120.4834 | 120.3644 | 0.013733 | -0.76904 | 120.5978 | 120.488 | 120.4559 | -0.97961 | 120.5795 | 120.5566 | 120.4422 | -0.97504
567.3594 | 121.3989 | -120.5978 | 0.76904 | -0.015869 | 0.015488 | -0.00025641 | 0.0034093 | -0.002416 | 0.00029262 | -0.0037385 | -0.012436 | -0.0057187 | -0.0039028 | 0.0027236 | 0.0032535 | -0.0080258 | -0.004578 | -0.036621 | -0.027466 | -0.045776 | 0.086975 | -0.032043 | -0.16022 | -0.027466 | -0.091553 | -0.16022 | 0.054932 | 0.045776 | -0.09613 | -0.15106 | 120.5658 | 120.4376 | -0.68207 | 120.5612 | 120.5521 | 0.11444 | -0.77362 | 120.5017 | 120.4468 | -0.71411 | 120.5704 | 120.4376 | -0.009155 | -0.72327 | 120.6848 | 120.5933 | 120.5704 | -0.92926 | 120.6528 | 120.6436 | 120.5063 | -0.92011
569.0469 | 121.4539 | -120.5978 | 0.75073 | 0.12146 | 0.015915 | 0.0050842 | 0.0014867 | -0.0051932 | -0.00056178 | -0.0030975 | 0.11726 | -0.0057187 | -0.0028348 | 0.0029374 | 0.0030399 | -0.0065304 | -0.082397 | -0.1236 | -0.1236 | -0.09613 | 0.050354 | -0.054932 | -0.19684 | -0.022888 | -0.10986 | -0.15106 | 0.059509 | 0.022888 | -0.11902 | -0.14648 | 120.5429 | 120.401 | -0.70038 | 120.4742 | 120.5017 | 0.10071 | -0.83313 | 120.4788 | 120.4514 | -0.69122 | 120.575 | 120.4468 | -0.004578 | -0.72784 | 120.6482 | 120.5154 | 120.4742 | -0.94757 | 120.6573 | 120.6207 | 120.488 | -0.89722
570.7188 | 121.4539 | -120.6482 | 0.70496 | 0.13672 | 0.014847 | 0.0027344 | 0.0023413 | -0.0060476 | -0.0018436 | -0.0030975 | 0.102 | -0.0057187 | -0.0051846 | 0.0035782 | 0.0013309 | -0.0048214 | -0.073242 | -0.11902 | -0.11902 | -0.07782 | 0.059509 | -0.064087 | -0.19684 | -0.027466 | -0.11902 | -0.14191 | 0.059509 | 0.022888 | -0.10529 | -0.16022 | 120.5841 | 120.4514 | -0.64545 | 120.5292 | 120.5704 | 0.11902 | -0.7782 | 120.5429 | 120.488 | -0.64545 | 120.6207 | 120.5063 | 0.01831 | -0.68207 | 120.7077 | 120.575 | 120.5292 | -0.90179 | 120.7077 | 120.6711 | 120.5292 | -0.86517
572.3906 | 121.431 | -120.6482 | 0.76904 | 0.068054 | 0.010147 | 0.0061524 | 0.0046911 | -0.0017752 | -0.0048344 | -0.0054475 | 0.14015 | -0.0072141 | -0.0053982 | -5.3406e-05 | 0.00026273 | -0.0052488 | 0.018311 | 0.027466 | 0.041199 | 0.004578 | 0.054932 | 0.027466 | -0.10986 | 0.07782 | 0.12817 | -0.009155 | 0.050354 | 0.050354 | -0.022888 | -0.10529 | 120.6757 | 120.5383 | -0.71411 | 120.6757 | 120.6528 | 0.11444 | -0.75073 | 120.6253 | 120.5429 | -0.71869 | 120.726 | 120.639 | 0.096131 | -0.71869 | 120.7031 | 120.6665 | 120.6894 | -0.87891 | 120.6985 | 120.6985 | 120.7764 | -0.87433
574.0625 | 121.4951 | -120.7352 | 0.65918 | 0.13672 | 0.014633 | 0.0025208 | 0.0012731 | -0.0034842 | 0.00050622 | -0.0039521 | 0.071487 | -0.0046505 | -0.0068936 | 0.00058739 | 0.0038943 | -0.006744 | -0.036621 | -0.14191 | -0.10986 | -0.10071 | 0.054932 | -0.045776 | -0.19684 | -0.013733 | -0.13275 | -0.14648 | 0.07782 | 0.041199 | -0.11444 | -0.16937 | 120.6894 | 120.5383 | -0.60425 | 120.5933 | 120.6345 | 0.09613 | -0.6958 | 120.6207 | 120.5658 | -0.58136 | 120.7214 | 120.5887 | 0.022889 | -0.61798 | 120.7901 | 120.6985 | 120.6253 | -0.85602 | 120.813 | 120.7764 | 120.6024 | -0.82855
575.7344 | 121.5042 | -120.7947 | 0.57678 | -0.054016 | 0.016983 | 0.0023072 | 0.0068273 | -0.0022024 | 0.00050622 | -0.0035249 | -0.08873 | -0.0070003 | -0.0017666 | -5.3406e-05 | 0.0045351 | -0.009094 | 0.059509 | 0.009155 | 0.022888 | 0.009155 | 0.11444 | -0.013733 | -0.13275 | 0.041199 | -0.009155 | -0.082397 | 0.064087 | 0.059509 | -0.068665 | -0.13733 | 120.7809 | 120.6619 | -0.46234 | 120.8038 | 120.8038 | 0.14191 | -0.51727 | 120.726 | 120.6573 | -0.5127 | 120.8359 | 120.7123 | 0.054932 | -0.51727 | 120.9091 | 120.8542 | 120.8176 | -0.70953 | 120.8588 | 120.8542 | 120.7855 | -0.71411
577.4062 | 121.6187 | -120.8908 | 0.4715 | -0.12268 | 0.01741 | 0.0027344 | 0.0042639 | -0.0019888 | -0.0018436 | -0.0043793 | -0.16502 | -0.0063595 | -0.0034756 | -0.00069421 | 0.0028263 | -0.0078122 | 0.045776 | 0.022888 | 0.022888 | 0.041199 | 0.13275 | 0.004578 | -0.11902 | 0.036621 | 0.054932 | -0.054932 | 0.068665 | 0.059509 | -0.059509 | -0.1236 | 120.8954 | 120.7718 | -0.33875 | 120.9137 | 120.932 | 0.16022 | -0.42572 | 120.8313 | 120.7672 | -0.40283 | 120.9274 | 120.8359 | 0.068664 | -0.41199 | 121.0236 | 120.9366 | 120.9137 | -0.59052 | 120.9595 | 120.9503 | 120.9457 | -0.59509
579.0781 | 121.5317 | -121.0144 | 0.43488 | 0.16724 | 0.014633 | 0.0042298 | 0.0023413 | -0.004125 | -0.0039798 | -0.0043793 | 0.19356 | -0.0067867 | -0.0021938 | -0.0013352 | 0.0036807 | -0.0069578 | 0 | 0.004578 | 0.045776 | -0.013733 | 0.009155 | -0.050354 | -0.16937 | 0.07782 | 0.041199 | -0.032043 | -0.004578 | -0.032043 | -0.10071 | -0.15106 | 120.9641 | 120.845 | -0.42572 | 121.019 | 121.0007 | 0.15564 | -0.43488 | 120.9137 | 120.8633 | -0.43945 | 121.0922 | 120.9824 | 0.11902 | -0.46692 | 121.0236 | 121.0144 | 121.0602 | -0.60425 | 121.0098 | 120.9824 | 121.0556 | -0.58594
580.7812 | 121.5042 | -121.019 | 0.42572 | 0.17487 | 0.015488 | 0.0035888 | 0.0053321 | -0.0030568 | -0.0031254 | -0.0050201 | 0.18593 | -0.0082821 | -0.003262 | -0.0011216 | 0.00068993 | -0.007385 | 0.013733 | 0.013733 | 0.054932 | -0.022888 | 0 | -0.032043 | -0.16937 | 0.091553 | 0.073242 | -0.013733 | 0 | -0.032043 | -0.068665 | -0.13733 | 120.9869 | 120.8496 | -0.42572 | 121.0327 | 120.9961 | 0.14649 | -0.41199 | 120.9503 | 120.8817 | -0.42572 | 121.1105 | 121.0052 | 0.1236 | -0.45776 | 121.019 | 121.0327 | 121.0739 | -0.59509 | 121.019 | 120.9869 | 121.0922 | -0.56305
582.4531 | 121.6415 | -121.0236 | 0.42572 | -0.099793 | 0.017197 | 0.0031616 | 0.0034093 | -0.0022024 | 0.0011472 | -0.0024567 | -0.13451 | -0.0052915 | -0.0047574 | 0.00016019 | 0.0047489 | -0.0095212 | 0.068665 | 0.022888 | 0.018311 | 0.027466 | 0.12817 | 0.013733 | -0.13733 | 0.059509 | 0.041199 | -0.068665 | 0.050354 | 0.045776 | -0.064087 | -0.12817 | 121.0373 | 120.8862 | -0.29755 | 121.0464 | 121.051 | 0.16479 | -0.35706 | 120.9595 | 120.8954 | -0.37537 | 121.0831 | 120.9549 | 0.059509 | -0.37994 | 121.1517 | 121.0922 | 121.0419 | -0.56305 | 121.0739 | 121.0693 | 121.0648 | -0.55389
584.125 | 121.6782 | -121.0419 | 0.37537 | -0.22186 | 0.019119 | 0.0033752 | 0.0066137 | -0.0043386 | -0.0018436 | -0.0045929 | -0.18791 | -0.0074277 | -0.0021938 | -0.001976 | -0.00037807 | -0.005676 | 0.068665 | 0.018311 | 0.032043 | 0.054932 | 0.19684 | 0.054932 | -0.064087 | 0.045776 | 0.082397 | -0.054932 | 0.13275 | 0.11444 | -0.032043 | -0.10071 | 121.0968 | 120.9778 | -0.17853 | 121.0602 | 121.0968 | 0.11902 | -0.3067 | 121.0098 | 120.9412 | -0.24261 | 121.0876 | 120.9869 | 0.045776 | -0.26092 | 121.2387 | 121.1105 | 121.0739 | -0.43945 | 121.1746 | 121.1563 | 121.1243 | -0.47607
585.7969 | 121.6461 | -121.1334 | 0.30212 | -0.17609 | 0.017197 | 0.002948 | 0.0085363 | -0.004125 | -0.0024844 | -0.0026703 | -0.2108 | -0.0050777 | -0.003262 | 0.0020828 | -0.00037807 | -0.0065304 | 0.050354 | 0.050354 | 0.050354 | 0.054932 | 0.20142 | 0.068665 | -0.073242 | 0.059509 | 0.11444 | -0.027466 | 0.15106 | 0.13275 | -0.022888 | -0.068665 | 121.2021 | 121.0602 | -0.10071 | 121.1838 | 121.1884 | 0.12817 | -0.25177 | 121.1105 | 121.0648 | -0.15106 | 121.1929 | 121.106 | 0.041199 | -0.16937 | 121.3348 | 121.1838 | 121.1838 | -0.37537 | 121.2845 | 121.2662 | 121.2479 | -0.37079
587.5156 | 121.701 | -121.1563 | 0.32044 | -0.13031 | 0.017838 | 0.0025208 | 0.0051183 | -0.0028432 | 0.00071982 | -0.0024567 | -0.19554 | -0.0050777 | -0.0026212 | 0.00016019 | 0.0019717 | -0.0095212 | 0.059509 | 0.013733 | 0.018311 | 0.032043 | 0.16022 | 0.022888 | -0.10986 | 0.045776 | 0.050354 | -0.059509 | 0.068665 | 0.041199 | -0.068665 | -0.1236 | 121.1792 | 121.0464 | -0.16022 | 121.17 | 121.1884 | 0.14191 | -0.26093 | 121.0876 | 121.0327 | -0.25177 | 121.2021 | 121.0968 | 0.064087 | -0.27924 | 121.3165 | 121.2158 | 121.1746 | -0.4303 | 121.225 | 121.1975 | 121.2067 | -0.44403
589.1719 | 121.5591 | -121.1838 | 0.32044 | 0.12146 | 0.015061 | 0.0031616 | 0.0019141 | -0.0051932 | -0.0041934 | -0.0045929 | 0.20119 | -0.0084957 | -0.0047574 | 0.00058739 | 0.0021853 | -0.005676 | 0.009155 | 0.036621 | 0.032043 | -0.022888 | 0.022888 | -0.013733 | -0.16479 | 0.10529 | 0.10529 | -0.009155 | 0.013733 | 0.009155 | -0.068665 | -0.1236 | 121.17 | 121.019 | -0.29755 | 121.2204 | 121.1609 | 0.14191 | -0.31128 | 121.1151 | 121.0602 | -0.3067 | 121.2891 | 121.1746 | 0.11444 | -0.31128 | 121.2067 | 121.1929 | 121.2158 | -0.48523 | 121.1975 | 121.1929 | 121.2891 | -0.44403
590.8438 | 121.6095 | -121.225 | 0.30212 | 0.045166 | 0.017197 | 0.0018798 | 0.00041872 | -0.0039114 | 0.0022152 | -0.0037385 | 0.048599 | -0.0065731 | -0.0036892 | 0.00016019 | 0.0051761 | -0.0078122 | -0.059509 | -0.13275 | -0.10071 | -0.073242 | 0.10071 | -0.041199 | -0.18768 | -0.050354 | -0.1236 | -0.17395 | 0.045776 | 0.032043 | -0.12817 | -0.1831 | 121.1838 | 121.0373 | -0.20142 | 121.0922 | 121.1517 | 0.11444 | -0.36163 | 121.0968 | 121.0419 | -0.25635 | 121.1746 | 121.051 | 0.009155 | -0.27008 | 121.3257 | 121.1655 | 121.1243 | -0.48981 | 121.2708 | 121.257 | 121.1014 | -0.48523
592.5156 | 121.7514 | -121.2158 | 0.27466 | -0.16846 | 0.01741 | 0.0027344 | 0.0051183 | -0.0034842 | 7.902e-05 | -0.0030975 | -0.21843 | -0.0037961 | -0.0028348 | 0.00016019 | 0.0034671 | -0.0080258 | 0.041199 | 0.027466 | 0.018311 | 0.050354 | 0.18768 | 0.041199 | -0.1236 | 0.059509 | 0.064087 | -0.059509 | 0.12817 | 0.086975 | -0.041199 | -0.10071 | 121.257 | 121.0922 | -0.086975 | 121.2433 | 121.2662 | 0.17395 | -0.23346 | 121.1746 | 121.1151 | -0.14648 | 121.2753 | 121.1563 | 0.041199 | -0.18768 | 121.4035 | 121.257 | 121.2341 | -0.39825 | 121.344 | 121.3028 | 121.2799 | -0.37537
594.1719 | 121.7468 | -121.2387 | 0.26093 | 0.014648 | 0.013352 | 0.0052978 | 0.0057593 | -0.004125 | -0.006757 | -0.0035249 | 0.04097 | -0.0097775 | -0.0028348 | 0.00016019 | -0.00037807 | -0.0069578 | 0.032043 | 0.064087 | 0.086975 | 0.050354 | 0.11444 | 0.032043 | -0.086975 | 0.12817 | 0.19684 | 0.036621 | 0.07782 | 0.073242 | -0.004578 | -0.082397 | 121.2708 | 121.1517 | -0.14648 | 121.3028 | 121.2891 | 0.13733 | -0.22888 | 121.2341 | 121.1563 | -0.18311 | 121.3669 | 121.2753 | 0.11902 | -0.18768 | 121.3531 | 121.2708 | 121.3257 | -0.3479 | 121.3165 | 121.3119 | 121.4355 | -0.34332
595.8438 | 121.669 | -121.3074 | 0.27008 | 0.075684 | 0.015488 | 0.0040162 | 0.00084592 | -0.0056204 | 0.0024288 | -0.0037385 | 0.102 | -0.0052915 | -0.006039 | -0.00048061 | 0.0049625 | -0.0086666 | -0.045776 | -0.086975 | -0.086975 | -0.068665 | 0.07782 | -0.050354 | -0.1831 | 0.009155 | -0.11444 | -0.1236 | 0.041199 | 0.013733 | -0.086975 | -0.17395 | 121.257 | 121.1243 | -0.19226 | 121.2204 | 121.2387 | 0.11444 | -0.31586 | 121.2204 | 121.1334 | -0.22888 | 121.3165 | 121.1838 | 0.050354 | -0.25635 | 121.3852 | 121.2616 | 121.2204 | -0.45319 | 121.3486 | 121.3211 | 121.1929 | -0.44403
597.5469 | 121.6599 | -121.3348 | 0.29297 | 0.11383 | 0.01442 | 0.00038459 | 0.0031957 | -0.0032706 | 0.0011472 | -0.0030975 | 0.048599 | -0.0042233 | -0.0026212 | 0.00058739 | 0.0030399 | -0.0078122 | -0.07782 | -0.14648 | -0.11444 | -0.09613 | 0.059509 | -0.054932 | -0.18768 | -0.027466 | -0.16022 | -0.16937 | 0.050354 | 0.032043 | -0.11444 | -0.18768 | 121.2799 | 121.1472 | -0.23346 | 121.1884 | 121.2387 | 0.091553 | -0.37079 | 121.2204 | 121.1472 | -0.24261 | 121.3074 | 121.1655 | 0.01831 | -0.26093 | 121.3943 | 121.257 | 121.2204 | -0.48065 | 121.3852 | 121.3669 | 121.1746 | -0.48065
599.2188 | 121.8063 | -121.2799 | 0.21057 | -0.19135 | 0.018692 | 0.00059819 | 0.010459 | -0.0045522 | -0.00034818 | -0.0028839 | -0.18028 | -0.0050777 | -0.0011258 | 0.0022964 | 0.00047633 | -0.007385 | 0.054932 | 0.027466 | 0.027466 | 0.036621 | 0.19684 | 0.068665 | -0.091553 | 0.045776 | 0.07782 | -0.050354 | 0.13733 | 0.11444 | -0.022888 | -0.1236 | 121.3486 | 121.1884 | -0.013733 | 121.3074 | 121.3165 | 0.12817 | -0.15564 | 121.257 | 121.1563 | -0.073242 | 121.3257 | 121.2296 | 0.073242 | -0.09613 | 121.4767 | 121.3348 | 121.3074 | -0.30212 | 121.4172 | 121.3943 | 121.3577 | -0.33417
600.9688 | 121.6919 | -121.3486 | 0.2655 | 0.060425 | 0.017197 | 0.0014526 | 0.0023413 | -0.00027985 | -0.0012028 | -0.0037385 | 0.079117 | -0.0065731 | -0.0024076 | 0.0020828 | 0.0034671 | -0.0054624 | -0.10071 | -0.13733 | -0.13275 | -0.091553 | 0.09613 | -0.041199 | -0.20142 | -0.027466 | -0.13733 | -0.17395 | 0.036621 | 0.018311 | -0.10986 | -0.1831 | 121.3074 | 121.1472 | -0.16937 | 121.2112 | 121.257 | 0.10986 | -0.36621 | 121.2387 | 121.1655 | -0.22888 | 121.3211 | 121.1746 | 0.009155 | -0.24719 | 121.4447 | 121.2479 | 121.2158 | -0.46692 | 121.3852 | 121.3669 | 121.2112 | -0.44861
602.7344 | 121.7606 | -121.3348 | 0.21515 | -0.17609 | 0.013138 | 0.0052978 | 0.0081091 | -0.0022024 | -0.0059024 | -0.0052337 | -0.073471 | -0.0091367 | -0.0019802 | 0.00058739 | -0.0023007 | -0.0075986 | 0.1236 | 0.16479 | 0.16479 | 0.1236 | 0.14648 | 0.082397 | -0.032043 | 0.15106 | 0.27924 | 0.091553 | 0.09613 | 0.064087 | 0.018311 | -0.059509 | 121.4172 | 121.3028 | -0.068665 | 121.4996 | 121.4584 | 0.15564 | -0.091553 | 121.3531 | 121.2753 | -0.11902 | 121.4859 | 121.4264 | 0.15106 | -0.15106 | 121.4813 | 121.4584 | 121.4996 | -0.24719 | 121.431 | 121.3989 | 121.6141 | -0.27466
604.4844 | 121.7331 | -121.4127 | 0.21973 | 0.15198 | 0.01741 | 0.0020936 | 0.0019141 | -0.0049796 | 0.0022152 | -0.0033111 | 0.086746 | -0.0059323 | -0.0047574 | 0.0016556 | 0.0038943 | -0.0095212 | -0.054932 | -0.10071 | -0.10071 | -0.07782 | 0.064087 | -0.054932 | -0.19226 | -0.009155 | -0.10529 | -0.14191 | 0.059509 | 0.050354 | -0.10529 | -0.16479 | 121.3577 | 121.2204 | -0.15564 | 121.312 | 121.3348 | 0.11444 | -0.27466 | 121.3074 | 121.2479 | -0.16022 | 121.4035 | 121.2708 | 0.022888 | -0.16937 | 121.4767 | 121.3577 | 121.312 | -0.41199 | 121.4722 | 121.463 | 121.3074 | -0.38452
606.1719 | 121.7743 | -121.3898 | 0.21057 | -0.26764 | 0.015061 | 0.0025208 | 0.0064001 | -0.0039114 | -0.005048 | -0.0045929 | -0.14977 | -0.0065731 | -0.0021938 | 0.00080099 | -0.00016447 | -0.0082394 | 0.11902 | 0.11902 | 0.1236 | 0.09613 | 0.18768 | 0.086975 | -0.050354 | 0.086975 | 0.1831 | -0.009155 | 0.15106 | 0.12817 | -0.009155 | -0.073242 | 121.4767 | 121.3394 | -0.022888 | 121.5088 | 121.4859 | 0.14648 | -0.091552 | 121.3806 | 121.3165 | -0.059509 | 121.4767 | 121.3806 | 0.064087 | -0.082397 | 121.5775 | 121.5088 | 121.5134 | -0.26093 | 121.5408 | 121.5179 | 121.5729 | -0.28381
607.9062 | 121.8521 | -121.3806 | 0.17395 | -0.13031 | 0.013565 | 0.0050842 | 0.0053321 | -0.0043386 | -0.0054752 | -0.0045929 | -0.042954 | -0.0080685 | -0.0056118 | -0.00048061 | 0.0011173 | -0.0063168 | 0.13275 | 0.15106 | 0.14191 | 0.10529 | 0.12817 | 0.086975 | -0.050354 | 0.17853 | 0.27466 | 0.11444 | 0.082397 | 0.054932 | 0 | -0.059509 | 121.4676 | 121.3303 | -0.045776 | 121.5317 | 121.4859 | 0.15564 | -0.041199 | 121.3806 | 121.3211 | -0.091553 | 121.5591 | 121.4951 | 0.17395 | -0.11902 | 121.5088 | 121.5134 | 121.5225 | -0.2243 | 121.463 | 121.4355 | 121.6553 | -0.23346
609.6406 | 121.7697 | -121.4539 | 0.20599 | 0.029907 | 0.013565 | 0.0025208 | 0.0044775 | -0.0051932 | -0.0076114 | -0.0056611 | 0.048599 | -0.0087093 | -0.0034756 | 0.00080099 | -0.00016447 | -0.007385 | 0.022888 | 0.027466 | 0.054932 | 0.027466 | 0.10071 | 0.027466 | -0.09613 | 0.086975 | 0.13275 | -0.004578 | 0.082397 | 0.059509 | -0.036621 | -0.09613 | 121.4813 | 121.3577 | -0.10529 | 121.4813 | 121.4813 | 0.1236 | -0.18311 | 121.4172 | 121.3577 | -0.1236 | 121.5408 | 121.4493 | 0.091552 | -0.14649 | 121.5546 | 121.4767 | 121.5088 | -0.30212 | 121.5363 | 121.5134 | 121.5866 | -0.30212
611.375 | 121.875 | -121.4493 | 0.17853 | -0.19897 | 0.01442 | 0.0050842 | 0.0023413 | -0.0036978 | 0.0022152 | -0.0037385 | -0.24132 | -0.0076413 | -0.0039028 | 0.001442 | 0.0085941 | -0.0093076 | 0.07782 | 0.004578 | 0.004578 | 0.045776 | 0.18768 | 0.045776 | -0.082397 | 0.059509 | 0.07782 | -0.054932 | 0.14191 | 0.09613 | -0.032043 | -0.09613 | 121.4951 | 121.3669 | 0.009155 | 121.4539 | 121.4951 | 0.12817 | -0.10071 | 121.4172 | 121.3531 | -0.036621 | 121.5088 | 121.3943 | 0.041198 | -0.082398 | 121.637 | 121.5271 | 121.4539 | -0.26092 | 121.5912 | 121.5454 | 121.5271 | -0.27466
613.1094 | 121.7606 | -121.4584 | 0.20599 | -0.061646 | 0.017838 | 0.0052978 | 0.00084592 | -0.0036978 | 0.0013608 | -0.0026703 | -0.13451 | -0.0050777 | -0.0053982 | 0.00016019 | 0.0073123 | -0.0071714 | 0.073242 | 0.022888 | 0.009155 | 0.013733 | 0.086975 | -0.004578 | -0.14648 | 0.050354 | 0.004578 | -0.07782 | 0.073242 | 0.045776 | -0.064087 | -0.12817 | 121.4539 | 121.312 | -0.11902 | 121.4813 | 121.4722 | 0.16022 | -0.13275 | 121.3943 | 121.3303 | -0.13275 | 121.5088 | 121.3806 | 0.050354 | -0.16022 | 121.5454 | 121.5317 | 121.4676 | -0.35248 | 121.5317 | 121.5042 | 121.463 | -0.33417
614.8438 | 121.8887 | -121.4539 | 0.17853 | -0.21423 | 0.016983 | 0.0014526 | 0.0061865 | -0.0054068 | -0.00013458 | -0.0026703 | -0.18791 | -0.0061459 | -0.0028348 | 0.001442 | 0.00047633 | -0.0082394 | 0.064087 | 0.018311 | 0.022888 | 0.054932 | 0.20142 | 0.059509 | -0.082397 | 0.036621 | 0.07782 | -0.064087 | 0.13275 | 0.10529 | -0.050354 | -0.10986 | 121.5134 | 121.3715 | 0.022888 | 121.4722 | 121.5088 | 0.13733 | -0.11444 | 121.4035 | 121.344 | -0.045777 | 121.4905 | 121.3898 | 0.045776 | -0.073242 | 121.6553 | 121.5179 | 121.4767 | -0.26092 | 121.5866 | 121.5591 | 121.5317 | -0.28839
616.5156 | 121.7789 | -121.4722 | 0.20142 | 0.045166 | 0.013565 | 0.0027344 | 0.0053321 | -0.0066884 | -0.0065434 | -0.0026703 | 0.13252 | -0.0074277 | -0.0021938 | 0.00016019 | -0.0014463 | -0.0075986 | 0.022888 | 0.045776 | 0.054932 | 0.013733 | 0.10986 | 0.045776 | -0.10071 | 0.07782 | 0.12817 | 0.009155 | 0.07782 | 0.032043 | -0.022888 | -0.10529 | 121.5179 | 121.3715 | -0.091553 | 121.5179 | 121.4859 | 0.11444 | -0.17853 | 121.4493 | 121.3669 | -0.1236 | 121.55 | 121.4813 | 0.11444 | -0.16937 | 121.582 | 121.4951 | 121.5271 | -0.30212 | 121.55 | 121.5042 | 121.6003 | -0.3067
618.2656 | 121.8979 | -121.4584 | 0.18768 | -0.12268 | 0.016556 | 0.0038024 | 0.0070409 | -0.0047658 | -0.004407 | -0.0035249 | -0.10399 | -0.0087093 | -0.0013394 | -0.0021896 | 0.00047633 | -0.0078122 | 0.15106 | 0.1831 | 0.17395 | 0.11902 | 0.14191 | 0.086975 | -0.050354 | 0.18768 | 0.28839 | 0.10529 | 0.10529 | 0.073242 | 0.013733 | -0.045776 | 121.5454 | 121.4081 | -0.045776 | 121.6415 | 121.5775 | 0.16937 | -0.036621 | 121.4722 | 121.4127 | -0.082397 | 121.6461 | 121.5637 | 0.15106 | -0.11444 | 121.6003 | 121.6095 | 121.6324 | -0.23804 | 121.5637 | 121.5317 | 121.7468 | -0.23346
619.9375 | 121.7468 | -121.4859 | 0.21973 | 0.083313 | 0.013992 | 0.0050842 | -0.0012903 | -0.0045522 | -0.0035526 | -0.0052337 | 0.18593 | -0.0076413 | -0.0075344 | -0.0011216 | 0.0036807 | -0.0078122 | 0.032043 | 0.041199 | 0.045776 | -0.013733 | 0.018311 | -0.018311 | -0.14648 | 0.086975 | 0.068665 | -0.013733 | 0.032043 | -0.009155 | -0.07782 | -0.14191 | 121.4676 | 121.3394 | -0.20142 | 121.5271 | 121.4722 | 0.13275 | -0.18768 | 121.4081 | 121.344 | -0.18768 | 121.5729 | 121.4722 | 0.12817 | -0.22888 | 121.5042 | 121.5179 | 121.5317 | -0.36621 | 121.5179 | 121.4767 | 121.5546 | -0.36163
621.6719 | 121.8613 | -121.4722 | 0.17853 | -0.23712 | 0.016983 | 0.0052978 | 0.0076819 | -0.0026296 | -0.00034818 | -0.0048065 | -0.19554 | -0.0067867 | -0.0021938 | 0.0012284 | 0.00090353 | -0.0058896 | 0.086975 | 0.086975 | 0.07782 | 0.07782 | 0.18768 | 0.073242 | -0.059509 | 0.082397 | 0.14648 | -0.013733 | 0.13275 | 0.1236 | -0.027466 | -0.091553 | 121.5454 | 121.4127 | 0.009155 | 121.5591 | 121.55 | 0.13733 | -0.091553 | 121.4447 | 121.3806 | -0.045777 | 121.5546 | 121.4584 | 0.07782 | -0.054932 | 121.6599 | 121.5591 | 121.55 | -0.23804 | 121.6049 | 121.5958 | 121.6187 | -0.27008
623.4219 | 121.8018 | -121.4584 | 0.29297 | 0.16724 | 0.013992 | 0.0040162 | -0.0017175 | -0.0043386 | 0.00029262 | -0.0026703 | 0.1783 | -0.0072141 | -0.0039028 | -0.00026701 | 0.0041079 | -0.0069578 | 0.013733 | 0.036621 | 0.027466 | -0.013733 | 0 | -0.032043 | -0.16937 | 0.082397 | 0.059509 | -0.018311 | -0.013733 | -0.032043 | -0.10071 | -0.15106 | 121.4264 | 121.2891 | -0.29297 | 121.4951 | 121.4447 | 0.15564 | -0.27924 | 121.3577 | 121.3074 | -0.3067 | 121.5408 | 121.4401 | 0.13275 | -0.32501 | 121.4584 | 121.4722 | 121.4859 | -0.46234 | 121.4447 | 121.4264 | 121.5179 | -0.44403
625.1406 | 121.9208 | -120.8908 | 0.77362 | -0.12268 | 0.015488 | 0.0025208 | 0.0078955 | -0.0045522 | -0.0054752 | -0.0039521 | -0.15739 | -0.0078549 | -0.0043302 | -0.0013352 | -0.0016599 | -0.0075986 | 0.16479 | 0.21515 | 0.19684 | 0.1236 | 0.14648 | 0.09613 | -0.054932 | 0.18768 | 0.29755 | 0.10071 | 0.09613 | 0.07782 | 0.018311 | -0.050354 | 120.9869 | 120.8359 | -0.62714 | 121.106 | 121.0144 | 0.17853 | -0.60883 | 120.9091 | 120.8405 | -0.67749 | 121.0785 | 120.9915 | 0.15106 | -0.6958 | 121.0373 | 121.0556 | 121.0876 | -0.82855 | 120.9869 | 120.9686 | 121.1884 | -0.82398
626.8125 | 121.9254 | -120.9412 | 0.75073 | -0.10742 | 0.018265 | 0.0044434 | 0.0038367 | -0.0051932 | 0.0026424 | -0.0024567 | -0.20317 | -0.0052915 | -0.003262 | 0.0040054 | 0.0032535 | -0.0097348 | 0.068665 | 0.045776 | 0.032043 | 0.050354 | 0.15106 | 0.027466 | -0.1236 | 0.068665 | 0.041199 | -0.059509 | 0.073242 | 0.050354 | -0.050354 | -0.12817 | 120.9686 | 120.8176 | -0.59967 | 120.9869 | 120.9915 | 0.17395 | -0.68207 | 120.8908 | 120.813 | -0.67749 | 121.0098 | 120.8817 | 0.068665 | -0.70038 | 121.0922 | 121.0098 | 120.9732 | -0.87433 | 121.0144 | 120.9915 | 120.9824 | -0.87891
628.5469 | 121.8246 | -121.0327 | 0.73242 | 0.17487 | 0.014847 | 0.0044434 | 0.0014867 | -0.0049796 | -0.0024844 | -0.0045929 | 0.20119 | -0.0076413 | -0.0058254 | -0.00069421 | 0.0047489 | -0.0078122 | 0.004578 | 0.036621 | 0.018311 | -0.018311 | 0.009155 | -0.045776 | -0.17853 | 0.09613 | 0.050354 | -0.027466 | -0.032043 | -0.045776 | -0.10071 | -0.16937 | 120.9869 | 120.8542 | -0.72327 | 121.0693 | 121.0144 | 0.16022 | -0.72784 | 120.932 | 120.8633 | -0.76447 | 121.1288 | 121.0052 | 0.14191 | -0.7782 | 121.0419 | 121.0373 | 121.051 | -0.91095 | 121.0007 | 120.9869 | 121.0831 | -0.9018
630.2188 | 121.8246 | -121.1014 | 0.65918 | 0.060425 | 0.010788 | 0.0057252 | 0.0017005 | -0.0028432 | -0.0037662 | -0.0043793 | 0.094375 | -0.0078549 | -0.00668 | 0.00080099 | 0.0032535 | -0.006744 | 0.041199 | 0.041199 | 0.036621 | 0 | 0.07782 | 0.022888 | -0.13275 | 0.07782 | 0.11444 | 0.013733 | 0.059509 | 0.036621 | -0.036621 | -0.09613 | 121.1243 | 120.9686 | -0.58136 | 121.1426 | 121.1014 | 0.13275 | -0.61798 | 121.0648 | 121.0052 | -0.59967 | 121.1792 | 121.1151 | 0.10986 | -0.62256 | 121.1792 | 121.1426 | 121.138 | -0.79193 | 121.1609 | 121.138 | 121.2158 | -0.75531
631.9375 | 121.9666 | -121.1197 | 0.59967 | -0.11505 | 0.013779 | 0.0057252 | 0.0070409 | -0.0019888 | -0.0039798 | -0.0022431 | -0.096359 | -0.0087093 | -0.003262 | -0.0024032 | 0.00026273 | -0.0069578 | 0.16479 | 0.20599 | 0.1831 | 0.11902 | 0.1236 | 0.082397 | -0.054932 | 0.19226 | 0.30212 | 0.10529 | 0.086975 | 0.086975 | 0.018311 | -0.050354 | 121.2021 | 121.0648 | -0.47607 | 121.3257 | 121.2387 | 0.17395 | -0.43488 | 121.138 | 121.0693 | -0.5127 | 121.312 | 121.225 | 0.15564 | -0.5127 | 121.2433 | 121.2845 | 121.3028 | -0.6546 | 121.2067 | 121.2067 | 121.4218 | -0.65002
633.6719 | 121.8658 | -121.1884 | 0.60425 | 0.029907 | 0.011429 | 0.0025208 | 0.0023413 | -0.0054068 | -0.003339 | -0.0043793 | 0.079117 | -0.0070003 | -0.0043302 | -0.00026701 | 0.0011173 | -0.0071714 | 0.036621 | 0.045776 | 0.041199 | 0.027466 | 0.10071 | 0.018311 | -0.10529 | 0.09613 | 0.11902 | 0.004578 | 0.091553 | 0.059509 | -0.045776 | -0.10529 | 121.2067 | 121.0831 | -0.50354 | 121.2341 | 121.2158 | 0.13275 | -0.56763 | 121.1426 | 121.0831 | -0.5127 | 121.2845 | 121.1929 | 0.10986 | -0.54474 | 121.2891 | 121.225 | 121.2296 | -0.70953 | 121.2799 | 121.2479 | 121.3074 | -0.70953
635.3438 | 121.907 | -121.2158 | 0.57678 | 0.21301 | 0.015701 | 0.00059819 | 0.0036231 | -0.0060476 | 0.0030698 | -0.0050201 | 0.14778 | -0.0072141 | -0.0047574 | -5.3406e-05 | 0.0026125 | -0.0088804 | 0 | -0.054932 | -0.054932 | -0.059509 | 0.032043 | -0.064087 | -0.19684 | 0.086975 | 0.009155 | -0.050354 | -0.009155 | -0.004578 | -0.07782 | -0.14648 | 121.1517 | 121.019 | -0.54474 | 121.1609 | 121.1563 | 0.13733 | -0.57678 | 121.138 | 121.0693 | -0.58594 | 121.3028 | 121.1655 | 0.09613 | -0.58136 | 121.2479 | 121.2158 | 121.1609 | -0.77362 | 121.2067 | 121.2112 | 121.225 | -0.72327
637.0781 | 121.8979 | -121.1975 | 0.58594 | 0.12146 | 0.01442 | 0.0040162 | 0.0017005 | -0.002416 | 0.0032834 | -0.0052337 | 0.13252 | -0.0044369 | -0.0045438 | 0.001442 | 0.0062441 | -0.0086666 | -0.018311 | -0.07782 | -0.07782 | -0.091553 | 0.09613 | -0.059509 | -0.19226 | 0.022888 | -0.09613 | -0.11444 | 0.032043 | 0 | -0.10529 | -0.16479 | 121.138 | 121.0052 | -0.48981 | 121.1197 | 121.106 | 0.10071 | -0.60425 | 121.0922 | 121.0327 | -0.55389 | 121.2204 | 121.0831 | 0.050354 | -0.58594 | 121.2936 | 121.1792 | 121.1197 | -0.7782 | 121.2296 | 121.1975 | 121.1014 | -0.75073
638.75 | 121.8338 | -121.2341 | 0.55389 | 0.11383 | 0.011429 | 0.0033752 | 0.00041872 | -0.0064748 | -0.0039798 | -0.0045929 | 0.19356 | -0.0082821 | -0.006039 | -0.0034714 | 0.0032535 | -0.0058896 | 0.032043 | 0.032043 | 0.041199 | -0.018311 | 0.013733 | -0.027466 | -0.15564 | 0.10071 | 0.091553 | 0 | 0.027466 | 0.004578 | -0.059509 | -0.1236 | 121.2067 | 121.0785 | -0.54016 | 121.2662 | 121.2158 | 0.13733 | -0.52185 | 121.1746 | 121.1105 | -0.52643 | 121.3348 | 121.2341 | 0.1236 | -0.54932 | 121.2479 | 121.2662 | 121.2753 | -0.70953 | 121.2616 | 121.2387 | 121.3257 | -0.67749
640.4844 | 121.8887 | -121.2982 | 0.53101 | 0.068054 | 0.016129 | 0.0038024 | 0.0014867 | -0.0030568 | 0.0041378 | -0.0020295 | -0.012436 | -0.0065731 | -0.0053982 | 0.0018692 | 0.0051761 | -0.0088804 | -0.032043 | -0.1236 | -0.10529 | -0.073242 | 0.091553 | -0.068665 | -0.18768 | -0.022888 | -0.1236 | -0.16937 | 0.073242 | 0.032043 | -0.10529 | -0.16937 | 121.2296 | 121.1105 | -0.43945 | 121.1746 | 121.225 | 0.11444 | -0.56305 | 121.1929 | 121.1288 | -0.45776 | 121.2753 | 121.1288 | 0 | -0.49896 | 121.3898 | 121.2662 | 121.1929 | -0.71869 | 121.3715 | 121.3303 | 121.1746 | -0.70038
642.1562 | 121.9666 | -121.4172 | 0.32959 | -0.24475 | 0.015701 | 0.0027344 | 0.0087499 | -0.0032706 | -0.00056178 | -0.0028839 | -0.18028 | -0.0084957 | -0.0030484 | -0.00069421 | 0.0011173 | -0.008453 | 0.082397 | 0.068665 | 0.064087 | 0.045776 | 0.19684 | 0.082397 | -0.068665 | 0.082397 | 0.14191 | -0.027466 | 0.15106 | 0.13275 | -0.018311 | -0.07782 | 121.4996 | 121.3486 | -0.13275 | 121.4859 | 121.463 | 0.11444 | -0.24719 | 121.3989 | 121.3394 | -0.17853 | 121.4996 | 121.3898 | 0.050354 | -0.19684 | 121.6141 | 121.4996 | 121.4813 | -0.39826 | 121.5683 | 121.55 | 121.5591 | -0.40741
643.8906 | 121.8842 | -121.4905 | 0.35248 | 0.11383 | 0.012497 | 0.0048706 | 0.0031957 | -0.0030568 | -0.0046206 | -0.0045929 | 0.20882 | -0.0065731 | -0.0034756 | -0.00048061 | 0.0028263 | -0.005676 | 0.054932 | 0.027466 | 0.054932 | -0.013733 | 0.027466 | -0.018311 | -0.16022 | 0.082397 | 0.073242 | -0.022888 | 0.013733 | 0 | -0.082397 | -0.12817 | 121.4722 | 121.3303 | -0.32501 | 121.5179 | 121.4767 | 0.14648 | -0.29755 | 121.4081 | 121.3623 | -0.33875 | 121.5729 | 121.4676 | 0.10529 | -0.35248 | 121.5179 | 121.5454 | 121.5454 | -0.5127 | 121.5042 | 121.4905 | 121.5637 | -0.48065
645.625 | 122.0169 | -121.4722 | 0.31128 | -0.00061023 | 0.013352 | 0.0038024 | 0.0044775 | -0.0039114 | -0.0018436 | -0.0060883 | 0.010452 | -0.0080685 | -0.0036892 | 0.0012284 | 0.00026273 | -0.0052488 | 0.064087 | 0.064087 | 0.059509 | 0.032043 | 0.09613 | 0.032043 | -0.10986 | 0.10986 | 0.1831 | 0.032043 | 0.07782 | 0.064087 | -0.027466 | -0.09613 | 121.5042 | 121.3623 | -0.21515 | 121.5363 | 121.5042 | 0.14191 | -0.24719 | 121.4447 | 121.376 | -0.23346 | 121.582 | 121.5042 | 0.12817 | -0.24719 | 121.5683 | 121.5363 | 121.5317 | -0.42114 | 121.55 | 121.5363 | 121.6553 | -0.40741
647.3438 | 122.049 | -121.5134 | 0.29297 | -0.19897 | 0.017838 | 0.0040162 | 0.0040503 | -0.0022024 | 0.0028562 | -0.0026703 | -0.23369 | -0.0050777 | -0.0051846 | -0.00069421 | 0.0034671 | -0.010589 | 0.10986 | 0.027466 | 0.018311 | 0.059509 | 0.17395 | 0.068665 | -0.086975 | 0.073242 | 0.050354 | -0.059509 | 0.10071 | 0.068665 | -0.064087 | -0.1236 | 121.582 | 121.4264 | -0.11902 | 121.5408 | 121.5729 | 0.14648 | -0.18311 | 121.4493 | 121.3898 | -0.19226 | 121.5866 | 121.4539 | 0.064087 | -0.2243 | 121.6873 | 121.6232 | 121.5317 | -0.37994 | 121.6141 | 121.582 | 121.5637 | -0.41656
649.0312 | 121.9482 | -121.5454 | 0.3067 | 0.13672 | 0.013779 | 0.0035888 | -0.00043588 | -0.002416 | 0.001788 | -0.00053407 | 0.16304 | -0.0063595 | -0.0058254 | 0.00037379 | 0.0041079 | -0.008453 | 0.045776 | 0.013733 | 0.027466 | -0.013733 | 0.018311 | -0.018311 | -0.17853 | 0.07782 | 0.032043 | -0.036621 | -0.013733 | -0.027466 | -0.07782 | -0.15106 | 121.5271 | 121.3669 | -0.28839 | 121.5591 | 121.5317 | 0.16479 | -0.26093 | 121.4676 | 121.3943 | -0.32043 | 121.6232 | 121.5088 | 0.11444 | -0.33417 | 121.5637 | 121.5912 | 121.5729 | -0.48523 | 121.5317 | 121.5179 | 121.5775 | -0.45776
650.7656 | 122.0444 | -121.5134 | 0.27924 | -0.12268 | 0.019119 | 0.0014526 | 0.0040503 | -0.0026296 | 0.0015744 | -0.00010687 | -0.14214 | -0.0065731 | -0.0043302 | 0.00016019 | 0.0036807 | -0.0093076 | 0.059509 | 0.036621 | 0.018311 | 0.022888 | 0.14191 | 0 | -0.14191 | 0.068665 | 0.050354 | -0.064087 | 0.064087 | 0.041199 | -0.068665 | -0.13733 | 121.5134 | 121.3715 | -0.13733 | 121.55 | 121.5363 | 0.16479 | -0.21973 | 121.4447 | 121.376 | -0.21515 | 121.582 | 121.4493 | 0.073242 | -0.23804 | 121.6553 | 121.5729 | 121.5317 | -0.42114 | 121.5775 | 121.5546 | 121.5637 | -0.41656
652.4375 | 122.0169 | -121.5591 | 0.27924 | -0.26001 | 0.016556 | 0.0033752 | 0.0083227 | -0.0022024 | -0.0035526 | -0.0050201 | -0.16502 | -0.0074277 | -0.00069863 | -0.0013352 | -0.00080527 | -0.0088804 | 0.1236 | 0.14191 | 0.11444 | 0.09613 | 0.16022 | 0.068665 | -0.068665 | 0.09613 | 0.18768 | -0.004578 | 0.13733 | 0.11444 | -0.009155 | -0.068665 | 121.6278 | 121.4905 | -0.11902 | 121.7011 | 121.6553 | 0.16479 | -0.15564 | 121.55 | 121.4905 | -0.14191 | 121.6553 | 121.5546 | 0.064087 | -0.16479 | 121.7194 | 121.6827 | 121.6736 | -0.3479 | 121.6965 | 121.6736 | 121.7468 | -0.3479
654.1719 | 122.049 | -121.5683 | 0.2655 | -0.0082397 | 0.014206 | 0.0033752 | 0.0036231 | -0.0051932 | -0.0041934 | -0.0039521 | 0.025711 | -0.0067867 | -0.003262 | -0.0013352 | 4.9132e-05 | -0.0095212 | 0.041199 | 0.064087 | 0.064087 | 0.027466 | 0.11444 | 0.027466 | -0.11444 | 0.11444 | 0.18768 | 0.032043 | 0.09613 | 0.050354 | -0.027466 | -0.09613 | 121.5958 | 121.4539 | -0.15106 | 121.6324 | 121.5958 | 0.14191 | -0.2243 | 121.5408 | 121.4722 | -0.16937 | 121.6827 | 121.6003 | 0.12817 | -0.21515 | 121.6827 | 121.6095 | 121.6324 | -0.37994 | 121.6644 | 121.6187 | 121.756 | -0.36163
655.9062 | 122.0306 | -121.6507 | 0.20142 | -0.22949 | 0.015701 | 0.0031616 | 0.0049047 | -0.0017752 | -0.0022708 | -0.0063019 | -0.21843 | -0.0074277 | -0.0041164 | -0.0015488 | 0.0030399 | -0.006744 | 0.14191 | 0.1236 | 0.14648 | 0.10529 | 0.15564 | 0.082397 | -0.073242 | 0.10529 | 0.18768 | 0.013733 | 0.13733 | 0.11902 | 0.009155 | -0.059509 | 121.7331 | 121.5775 | -0.045776 | 121.7743 | 121.756 | 0.17853 | -0.059509 | 121.6599 | 121.5912 | -0.064087 | 121.756 | 121.6644 | 0.073242 | -0.082397 | 121.8063 | 121.7926 | 121.7972 | -0.27466 | 121.788 | 121.7697 | 121.8384 | -0.26093
657.5781 | 122.0215 | -121.6415 | 0.20599 | -0.076904 | 0.021469 | 0.0035888 | 0.0044775 | -0.005834 | 0.001788 | -0.0043793 | -0.18791 | -0.0057187 | -0.0041164 | 0.0016556 | 0.0062441 | -0.0097348 | 0.086975 | 0.032043 | 0.004578 | 0.009155 | 0.10986 | 0 | -0.14191 | 0.073242 | 0.032043 | -0.068665 | 0.068665 | 0.041199 | -0.082397 | -0.14191 | 121.6415 | 121.4996 | -0.096131 | 121.6736 | 121.6507 | 0.15106 | -0.11902 | 121.5591 | 121.4996 | -0.13733 | 121.7148 | 121.5729 | 0.073242 | -0.1648 | 121.7514 | 121.7285 | 121.6461 | -0.3479 | 121.7102 | 121.6827 | 121.6736 | -0.3479
659.3125 | 121.9528 | -121.7285 | 0.17395 | 0.052795 | 0.015915 | 0.0050842 | 0.0049047 | -0.0039114 | -0.0054752 | -0.0054475 | 0.086746 | -0.0074277 | -0.003262 | -0.0015488 | 4.9132e-05 | -0.0048214 | 0.027466 | 0.054932 | 0.041199 | 0.027466 | 0.091553 | 0.013733 | -0.1236 | 0.091553 | 0.1236 | -0.009155 | 0.045776 | 0.045776 | -0.036621 | -0.11444 | 121.7422 | 121.6049 | -0.082397 | 121.7834 | 121.756 | 0.15106 | -0.14648 | 121.6919 | 121.6141 | -0.12817 | 121.8201 | 121.7194 | 0.10529 | -0.12817 | 121.8201 | 121.756 | 121.7697 | -0.29755 | 121.7743 | 121.7743 | 121.8521 | -0.28839
661.0469 | 122.0993 | -121.637 | 0.16479 | -0.13031 | 0.015061 | 0.0020936 | 0.0068273 | -0.0036978 | -0.0031254 | -0.0045929 | -0.035324 | -0.0082821 | -0.0024076 | 0.00016019 | -0.0010191 | -0.0080258 | 0.13733 | 0.17853 | 0.16022 | 0.091553 | 0.13275 | 0.07782 | -0.054932 | 0.20142 | 0.30212 | 0.11902 | 0.09613 | 0.064087 | 0.013733 | -0.050354 | 121.7148 | 121.582 | -0.032044 | 121.8155 | 121.7285 | 0.14649 | -0.027466 | 121.6507 | 121.5866 | -0.068665 | 121.8384 | 121.756 | 0.16937 | -0.10071 | 121.7697 | 121.7743 | 121.7972 | -0.21973 | 121.7331 | 121.701 | 121.9391 | -0.21515
662.7969 | 121.9574 | -121.7239 | 0.18768 | 0.1062 | 0.017197 | 0.0038024 | 0.0038367 | -0.0045522 | -0.0018436 | -0.0024567 | 0.14015 | -0.0087093 | -0.0053982 | 0.00058739 | 0.0028263 | -0.006744 | 0.018311 | 0.045776 | 0.045776 | -0.004578 | 0.045776 | 0.009155 | -0.12817 | 0.10986 | 0.10529 | -0.013733 | 0.064087 | 0.032043 | -0.041199 | -0.09613 | 121.7331 | 121.5958 | -0.14191 | 121.7697 | 121.7194 | 0.1236 | -0.16937 | 121.6827 | 121.6278 | -0.1236 | 121.8338 | 121.7102 | 0.082397 | -0.15564 | 121.7697 | 121.7422 | 121.7697 | -0.31586 | 121.788 | 121.756 | 121.8292 | -0.28381
664.4688 | 122.0718 | -121.7148 | 0.16937 | -0.092163 | 0.017197 | 0.002948 | -0.00022208 | -0.002416 | 0.0030698 | -0.0030975 | -0.16502 | -0.0061459 | -0.0062528 | 0.00037379 | 0.0064577 | -0.009094 | 0.09613 | 0.045776 | 0.018311 | 0.018311 | 0.10986 | -0.004578 | -0.13733 | 0.064087 | 0.027466 | -0.064087 | 0.07782 | 0.032043 | -0.073242 | -0.13275 | 121.7102 | 121.5775 | -0.05951 | 121.7606 | 121.7331 | 0.15564 | -0.073243 | 121.6415 | 121.582 | -0.091553 | 121.7789 | 121.6507 | 0.068664 | -0.13733 | 121.8246 | 121.8109 | 121.7331 | -0.3067 | 121.7926 | 121.7468 | 121.7422 | -0.30212
666.2031 | 122.0718 | -121.7148 | 0.16022 | -0.18372 | 0.016556 | 0.002948 | 0.0049047 | -0.0039114 | -0.00163 | -0.0026703 | -0.12688 | -0.0078549 | -0.0036892 | 0.00037379 | 0.0019717 | -0.006744 | 0.16022 | 0.18768 | 0.16479 | 0.1236 | 0.16937 | 0.091553 | -0.059509 | 0.16022 | 0.27466 | 0.086975 | 0.1236 | 0.07782 | 0.004578 | -0.050354 | 121.8063 | 121.6553 | 0.009156 | 121.9025 | 121.8384 | 0.1831 | 0 | 121.7194 | 121.6644 | -0.036621 | 121.875 | 121.8018 | 0.13733 | -0.082397 | 121.8842 | 121.875 | 121.8796 | -0.21973 | 121.8384 | 121.7926 | 121.9894 | -0.21057
667.9531 | 122.0901 | -121.7285 | 0.1831 | -0.22186 | 0.014847 | 0.0025208 | 0.0064001 | -0.0056204 | -0.0014164 | -0.0033111 | -0.26421 | -0.0040097 | -0.0036892 | -0.00069421 | 0.0041079 | -0.0088804 | 0.07782 | 0.059509 | 0.050354 | 0.050354 | 0.20142 | 0.059509 | -0.068665 | 0.073242 | 0.1236 | -0.009155 | 0.16479 | 0.13733 | -0.022888 | -0.091553 | 121.788 | 121.6599 | 0.018311 | 121.788 | 121.7789 | 0.11902 | -0.10528 | 121.7056 | 121.637 | -0.01831 | 121.8018 | 121.7194 | 0.082398 | -0.045776 | 121.9299 | 121.8063 | 121.7789 | -0.25177 | 121.8933 | 121.8658 | 121.8521 | -0.27466
669.625 | 122.1268 | -121.7194 | 0.14648 | -0.19135 | 0.01741 | 0.0031616 | 0.0049047 | -0.0077566 | 0.0028562 | -0.0026703 | -0.22606 | -0.0048641 | -0.0039028 | -0.00090781 | 0.0034671 | -0.0082394 | 0.07782 | 0.059509 | 0.027466 | 0.068665 | 0.18768 | 0.041199 | -0.091553 | 0.068665 | 0.064087 | -0.059509 | 0.09613 | 0.086975 | -0.041199 | -0.1236 | 121.7606 | 121.6278 | 0.041199 | 121.7789 | 121.788 | 0.16022 | -0.068664 | 121.6782 | 121.5958 | -0.050354 | 121.788 | 121.6599 | 0.064087 | -0.059509 | 121.907 | 121.7972 | 121.7468 | -0.23804 | 121.8155 | 121.8063 | 121.7834 | -0.27008
671.3594 | 122.0627 | -121.756 | 0.1831 | 0.20538 | 0.015488 | -0.0011108 | 0.0017005 | -0.0030568 | 7.902e-05 | -0.0013885 | 0.10963 | -0.0072141 | -0.0056118 | 0.0029374 | 0.0049625 | -0.0078122 | -0.032043 | -0.027466 | -0.036621 | -0.050354 | 0.045776 | -0.036621 | -0.20142 | 0.086975 | 0.004578 | -0.036621 | 0.013733 | -0.004578 | -0.086975 | -0.1236 | 121.7194 | 121.5546 | -0.13733 | 121.7285 | 121.7056 | 0.15106 | -0.21515 | 121.669 | 121.6324 | -0.16937 | 121.843 | 121.7194 | 0.086975 | -0.18768 | 121.8018 | 121.7239 | 121.7194 | -0.38452 | 121.7697 | 121.7514 | 121.7606 | -0.3067
673.0938 | 121.9986 | -121.756 | 0.19226 | 0.037537 | 0.016556 | 0.0033752 | 0.0021277 | -0.0051932 | 0.0020016 | -0.0037385 | 0.063858 | -0.0065731 | -0.0045438 | -0.00048061 | 0.0043215 | -0.006744 | -0.059509 | -0.10529 | -0.09613 | -0.086975 | 0.09613 | -0.036621 | -0.1831 | -0.032043 | -0.1236 | -0.16479 | 0.050354 | 0.032043 | -0.1236 | -0.19226 | 121.7194 | 121.5729 | -0.096131 | 121.6507 | 121.669 | 0.09613 | -0.25177 | 121.6324 | 121.5637 | -0.14191 | 121.7239 | 121.5912 | 0.027466 | -0.16022 | 121.8521 | 121.6965 | 121.6599 | -0.37537 | 121.8063 | 121.788 | 121.6324 | -0.38452
674.8281 | 121.9986 | -121.7926 | 0.18768 | 0.15198 | 0.01442 | 0.0031616 | 0.0068273 | -0.0028432 | -0.005048 | -0.0033111 | 0.19356 | -0.0055051 | -0.004971 | -5.3406e-05 | -0.0012327 | -0.0069578 | 0.013733 | 0.027466 | 0.027466 | -0.013733 | 0.022888 | -0.027466 | -0.16022 | 0.09613 | 0.10986 | 0.004578 | 0.059509 | 0.027466 | -0.041199 | -0.10071 | 121.7651 | 121.6324 | -0.16479 | 121.8201 | 121.7789 | 0.14648 | -0.17395 | 121.7514 | 121.6919 | -0.12817 | 121.8887 | 121.7972 | 0.10529 | -0.16022 | 121.8155 | 121.8063 | 121.8201 | -0.3479 | 121.8521 | 121.8201 | 121.9025 | -0.28839
676.5625 | 122.1405 | -121.7239 | 0.17395 | -0.19897 | 0.018906 | 0.0038024 | 0.0027685 | -0.005834 | 0.003497 | -0.0028839 | -0.16502 | -0.0050777 | -0.0041164 | 0.00037379 | 0.0053897 | -0.0093076 | 0.082397 | 0.036621 | 0.018311 | 0.068665 | 0.17853 | 0.041199 | -0.10529 | 0.045776 | 0.068665 | -0.054932 | 0.086975 | 0.082397 | -0.059509 | -0.11444 | 121.7651 | 121.6187 | 0.004578 | 121.7606 | 121.7926 | 0.17395 | -0.091553 | 121.6644 | 121.6095 | -0.086975 | 121.7697 | 121.669 | 0.059509 | -0.091553 | 121.9025 | 121.8063 | 121.7422 | -0.27924 | 121.8109 | 121.8063 | 121.7926 | -0.28839
678.2344 | 122.0398 | -121.669 | 0.29755 | 0.022278 | 0.012283 | 0.0010254 | 0.0029821 | -0.0039114 | -0.0048344 | -0.0039521 | 0.094375 | -0.0089229 | -0.0043302 | -5.3406e-05 | 0.00047633 | -0.0054624 | 0.018311 | 0.045776 | 0.050354 | 0.022888 | 0.07782 | 0.013733 | -0.10071 | 0.091553 | 0.1236 | 0.004578 | 0.068665 | 0.045776 | -0.036621 | -0.09613 | 121.6827 | 121.5683 | -0.21973 | 121.7148 | 121.6919 | 0.1236 | -0.27923 | 121.6324 | 121.5729 | -0.22888 | 121.7606 | 121.6736 | 0.10071 | -0.25177 | 121.7468 | 121.6873 | 121.7194 | -0.39825 | 121.7377 | 121.7148 | 121.7926 | -0.39368
679.9688 | 122.1359 | -121.6415 | 0.28381 | -0.076904 | 0.016983 | 0.0031616 | 0.0049047 | -0.0022024 | 0.0020016 | -0.0045929 | -0.12688 | -0.0059323 | -0.0058254 | -5.3406e-05 | 0.0068851 | -0.010376 | 0.07782 | 0.032043 | 0.013733 | 0.013733 | 0.13275 | 0.004578 | -0.15564 | 0.073242 | 0.027466 | -0.064087 | 0.082397 | 0.054932 | -0.073242 | -0.15564 | 121.6461 | 121.4859 | -0.15106 | 121.6736 | 121.6553 | 0.16937 | -0.20599 | 121.5683 | 121.4859 | -0.20142 | 121.7148 | 121.5775 | 0.091553 | -0.22888 | 121.7743 | 121.7194 | 121.6553 | -0.43945 | 121.7239 | 121.6965 | 121.669 | -0.43945
681.7031 | 122.1313 | -121.6232 | 0.29297 | -0.18372 | 0.016129 | 0.0044434 | 0.0072547 | -0.0039114 | -0.0065434 | -0.0039521 | -0.13451 | -0.0091367 | -0.0062528 | -5.3406e-05 | -0.00059167 | -0.006744 | 0.13733 | 0.19226 | 0.1831 | 0.11444 | 0.14191 | 0.068665 | -0.059509 | 0.19226 | 0.28839 | 0.11444 | 0.10071 | 0.07782 | 0.027466 | -0.050354 | 121.6919 | 121.5637 | -0.15106 | 121.8155 | 121.7377 | 0.17395 | -0.15564 | 121.6507 | 121.5729 | -0.19226 | 121.8155 | 121.7377 | 0.16479 | -0.21515 | 121.7651 | 121.7606 | 121.8063 | -0.35248 | 121.7239 | 121.7011 | 121.9116 | -0.34332
683.3906 | 122.0993 | -121.6553 | 0.31586 | 0.20538 | 0.016769 | 0.0035888 | 0.0027685 | -0.0051932 | 7.902e-05 | -0.0041657 | 0.10963 | -0.0059323 | -0.0056118 | 0.0027236 | 0.0047489 | -0.0097348 | 0.018311 | -0.018311 | -0.018311 | -0.032043 | 0.032043 | -0.036621 | -0.17853 | 0.10071 | 0.018311 | -0.041199 | 0 | -0.022888 | -0.082397 | -0.15564 | 121.6187 | 121.4767 | -0.28381 | 121.637 | 121.6232 | 0.14648 | -0.29755 | 121.5729 | 121.4996 | -0.31586 | 121.756 | 121.6141 | 0.11444 | -0.33875 | 121.6873 | 121.6736 | 121.637 | -0.49438 | 121.6553 | 121.6324 | 121.6736 | -0.4715
685.2344 | 122.1039 | -121.6644 | 0.30212 | -0.092163 | 0.018051 | 0.0014526 | 0.0053321 | -0.001348 | 0.0030698 | -0.0018159 | -0.14214 | -0.0046505 | -0.0045438 | 0.00058739 | 0.0030399 | -0.0086666 | 0.073242 | 0.027466 | 0.027466 | 0.018311 | 0.1236 | 0 | -0.12817 | 0.064087 | 0.022888 | -0.064087 | 0.064087 | 0.036621 | -0.086975 | -0.16022 | 121.6644 | 121.5363 | -0.17853 | 121.6919 | 121.6827 | 0.14649 | -0.22888 | 121.5775 | 121.5042 | -0.23804 | 121.7285 | 121.6003 | 0.09613 | -0.2655 | 121.788 | 121.7377 | 121.6919 | -0.4303 | 121.7285 | 121.701 | 121.6873 | -0.46234
687.0156 | 122.1039 | -121.701 | 0.29755 | 0.029907 | 0.012497 | 0.0038024 | 0.0021277 | -0.004125 | -0.0080386 | -0.0043793 | 0.10963 | -0.0074277 | -0.006039 | -0.0021896 | 0.00026273 | -0.0061032 | 0.013733 | 0.027466 | 0.041199 | 0.027466 | 0.09613 | 0.018311 | -0.09613 | 0.086975 | 0.14191 | 0 | 0.09613 | 0.054932 | -0.027466 | -0.10071 | 121.7194 | 121.6049 | -0.20142 | 121.7285 | 121.7285 | 0.1236 | -0.28381 | 121.6736 | 121.6003 | -0.20142 | 121.788 | 121.701 | 0.10071 | -0.24261 | 121.7972 | 121.7148 | 121.7422 | -0.39368 | 121.7972 | 121.756 | 121.843 | -0.39825
688.9219 | 122.1039 | -121.6736 | 0.32044 | 0.13672 | 0.019547 | 0.002948 | 0.0049047 | -0.0034842 | -0.00163 | -0.0041657 | 0.16304 | -0.0065731 | -0.0028348 | -0.0011216 | 0.0036807 | -0.008453 | 0.032043 | 0.009155 | 0.018311 | -0.009155 | 0.022888 | -0.050354 | -0.15564 | 0.064087 | 0.045776 | -0.036621 | -0.013733 | -0.032043 | -0.082397 | -0.15564 | 121.6232 | 121.5179 | -0.29755 | 121.6827 | 121.6644 | 0.14649 | -0.28839 | 121.5912 | 121.5179 | -0.33417 | 121.7377 | 121.637 | 0.11902 | -0.35248 | 121.6965 | 121.7056 | 121.6919 | -0.47608 | 121.6599 | 121.6415 | 121.7194 | -0.47608
692.25 | 122.1954 | -121.6599 | 0.31128 | -0.25238 | 0.016129 | 0.0018798 | 0.0040503 | -0.0045522 | 0.00093342 | -0.0045929 | -0.20317 | -0.0055051 | -0.0045438 | 0.00080099 | 0.0013309 | -0.009094 | 0.07782 | 0.045776 | 0.018311 | 0.045776 | 0.20142 | 0.07782 | -0.068665 | 0.059509 | 0.086975 | -0.073242 | 0.15106 | 0.11902 | -0.050354 | -0.10071 | 121.7377 | 121.5912 | -0.10986 | 121.7056 | 121.7056 | 0.11444 | -0.23346 | 121.6095 | 121.5591 | -0.16022 | 121.7194 | 121.5866 | 0.027466 | -0.19226 | 121.8613 | 121.7377 | 121.6782 | -0.37994 | 121.8109 | 121.7789 | 121.7468 | -0.41199
695.4375 | 122.2183 | -121.6415 | 0.28839 | -0.046387 | 0.015061 | 0.0048706 | 0.0057593 | -0.0034842 | -0.006757 | -0.0033111 | -0.058212 | -0.0087093 | -0.004971 | -0.00069421 | 0.00026273 | -0.006744 | 0.091553 | 0.11902 | 0.11444 | 0.07782 | 0.13275 | 0.064087 | -0.091553 | 0.18768 | 0.2655 | 0.10986 | 0.10529 | 0.073242 | 0.009155 | -0.059509 | 121.7056 | 121.55 | -0.15564 | 121.7606 | 121.7194 | 0.16937 | -0.19684 | 121.6507 | 121.582 | -0.18311 | 121.8292 | 121.7514 | 0.16937 | -0.21515 | 121.7743 | 121.7331 | 121.756 | -0.37994 | 121.7468 | 121.7148 | 121.907 | -0.3479
697.5 | 122.0947 | -121.843 | 0.13275 | 0.022278 | 0.011856 | 0.0018798 | 0.0038367 | -0.0036978 | -0.003339 | -0.0058747 | 0.086746 | -0.0067867 | -0.004971 | 0.00058739 | 0.00068993 | -0.006744 | 0.045776 | 0.045776 | 0.054932 | 0.022888 | 0.11444 | 0.027466 | -0.1236 | 0.09613 | 0.13275 | 0.004578 | 0.07782 | 0.050354 | -0.018311 | -0.10986 | 121.8704 | 121.7194 | -0.01831 | 121.8887 | 121.8658 | 0.14648 | -0.086975 | 121.8246 | 121.7331 | -0.054931 | 121.9391 | 121.8475 | 0.11444 | -0.082397 | 121.9574 | 121.8887 | 121.8979 | -0.25635 | 121.9208 | 121.8933 | 121.9757 | -0.24261
699.25 | 122.1085 | -121.8704 | 0.15564 | 0.19012 | 0.01442 | 0.0020936 | 0.0027685 | -0.0064748 | 7.902e-05 | -0.0041657 | 0.17067 | -0.0080685 | -0.0047574 | -0.00048061 | 0.0028263 | -0.0082394 | 0.032043 | 0.013733 | 0.018311 | -0.009155 | -0.004578 | -0.050354 | -0.19226 | 0.082397 | 0.045776 | -0.032043 | 0.004578 | -0.041199 | -0.10986 | -0.16937 | 121.8201 | 121.6782 | -0.16022 | 121.8842 | 121.8613 | 0.18311 | -0.1236 | 121.7606 | 121.701 | -0.15106 | 121.9528 | 121.8384 | 0.13733 | -0.19684 | 121.8658 | 121.9025 | 121.8887 | -0.3479 | 121.875 | 121.8292 | 121.9162 | -0.32501
701.125 | 122.1176 | -121.8933 | 0.15106 | 0.090942 | 0.019333 | 0.0020936 | 0.0029821 | -6.6248e-05 | 0.0037106 | -0.0011749 | 0.03334 | -0.0050777 | -0.0028348 | 0.0018692 | 0.0056033 | -0.0093076 | -0.054932 | -0.13733 | -0.12817 | -0.10071 | 0.086975 | -0.068665 | -0.19684 | -0.009155 | -0.14191 | -0.16479 | 0.050354 | 0.027466 | -0.11902 | -0.1831 | 121.8246 | 121.6965 | -0.064087 | 121.756 | 121.7926 | 0.09613 | -0.20599 | 121.7743 | 121.7102 | -0.10071 | 121.8842 | 121.7285 | 0.01831 | -0.1236 | 121.9803 | 121.8384 | 121.7651 | -0.3479 | 121.9437 | 121.9208 | 121.7514 | -0.33417
706.3438 | 122.2275 | -121.8521 | 0.13275 | -0.14557 | 0.014847 | 0.007434 | 0.0057593 | -0.0069022 | -0.0031254 | -0.0054475 | -0.11925 | -0.0076413 | -0.0030484 | 0.00016019 | -0.0016599 | -0.0088804 | 0.15106 | 0.21057 | 0.16937 | 0.10529 | 0.1236 | 0.07782 | -0.068665 | 0.19226 | 0.29755 | 0.10986 | 0.10529 | 0.082397 | 0 | -0.064087 | 121.9299 | 121.7834 | -0.009155 | 122.0627 | 121.9574 | 0.17395 | 0.018311 | 121.8521 | 121.788 | -0.027465 | 122.0444 | 121.962 | 0.17395 | -0.050354 | 121.9757 | 122.0032 | 122.0215 | -0.20142 | 121.9574 | 121.9345 | 122.1497 | -0.19684
708.1562 | 122.2321 | -121.8658 | 0.14191 | -0.076904 | 0.016342 | 0.0025208 | 0.00063232 | -0.0034842 | 0.0022152 | -0.0026703 | -0.20317 | -0.0050777 | -0.0071072 | 0.0022964 | 0.0058169 | -0.0099484 | 0.086975 | 0.027466 | 0.018311 | 0.027466 | 0.13275 | -0.013733 | -0.13733 | 0.068665 | 0.036621 | -0.059509 | 0.082397 | 0.054932 | -0.073242 | -0.13275 | 121.8521 | 121.7285 | -0.009156 | 121.8933 | 121.8933 | 0.16479 | -0.054932 | 121.7926 | 121.7331 | -0.05951 | 121.9345 | 121.8063 | 0.073242 | -0.086975 | 121.9986 | 121.9528 | 121.8842 | -0.27924 | 121.9482 | 121.9208 | 121.9025 | -0.27466
709.8438 | 122.2504 | -121.8842 | 0.13733 | -0.17609 | 0.014633 | 0.0016662 | 0.0044775 | -0.0032706 | 0.0028562 | -0.0026703 | -0.18028 | -0.0080685 | -0.0064664 | 0.00080099 | 0.0030399 | -0.0088804 | 0.073242 | 0.036621 | 0.018311 | 0.041199 | 0.20142 | 0.027466 | -0.10071 | 0.050354 | 0.068665 | -0.054932 | 0.082397 | 0.068665 | -0.068665 | -0.13733 | 121.9116 | 121.7834 | 0.064087 | 121.9208 | 121.9254 | 0.14191 | -0.064087 | 121.8155 | 121.7468 | -0.054932 | 121.9345 | 121.8292 | 0.082397 | -0.068664 | 122.0856 | 121.9574 | 121.9025 | -0.23804 | 121.9666 | 121.9528 | 121.9528 | -0.27466
711.5781 | 122.1771 | -121.8979 | 0.14648 | 0.14435 | 0.019974 | 0.0035888 | 0.0046911 | -0.0043386 | -0.00056178 | 0.00010673 | 0.1783 | -0.0046505 | -0.0043302 | 0.00058739 | 0.0034671 | -0.0065304 | -0.041199 | -0.082397 | -0.073242 | -0.07782 | 0.064087 | -0.045776 | -0.21057 | 0.041199 | -0.036621 | -0.10071 | 0.032043 | -0.013733 | -0.091553 | -0.15106 | 121.8521 | 121.6873 | -0.082397 | 121.8155 | 121.8201 | 0.13275 | -0.18768 | 121.8063 | 121.7468 | -0.11444 | 121.9391 | 121.7972 | 0.050354 | -0.16022 | 121.962 | 121.8567 | 121.8246 | -0.35706 | 121.9299 | 121.8842 | 121.8613 | -0.29755
713.25 | 122.1542 | -121.9254 | 0.15106 | 0.14435 | 0.01442 | 0.0025208 | 0.0014867 | -0.0036978 | -0.0012028 | -0.0013885 | 0.1783 | -0.0087093 | -0.006039 | 0.0010148 | 0.0032535 | -0.0086666 | 0.013733 | 0.022888 | 0.022888 | -0.018311 | 0 | -0.022888 | -0.18768 | 0.064087 | 0.032043 | -0.004578 | -0.004578 | -0.027466 | -0.086975 | -0.16022 | 121.9025 | 121.7377 | -0.15106 | 121.9482 | 121.907 | 0.16937 | -0.13733 | 121.8384 | 121.7651 | -0.15564 | 121.9894 | 121.9208 | 0.15564 | -0.17853 | 121.9254 | 121.9391 | 121.9482 | -0.33874 | 121.9208 | 121.8979 | 121.9574 | -0.31128
715 | 122.2275 | -121.8979 | 0.14648 | 0.0070193 | 0.013352 | 0.0048706 | 0.0044775 | -0.002416 | -0.006757 | -0.0037385 | 0.071487 | -0.0078549 | -0.004971 | -0.0011216 | -0.00080527 | -0.0063168 | 0.022888 | 0.045776 | 0.041199 | 0.036621 | 0.12817 | 0.022888 | -0.11902 | 0.10529 | 0.17853 | 0.022888 | 0.10071 | 0.050354 | -0.027466 | -0.11444 | 121.9208 | 121.7789 | -0.01831 | 121.9437 | 121.9345 | 0.15564 | -0.1236 | 121.8704 | 121.7834 | -0.045776 | 122.0032 | 121.9208 | 0.13733 | -0.09613 | 122.0261 | 121.9208 | 121.9391 | -0.2655 | 121.9986 | 121.9482 | 122.0764 | -0.26093
716.7344 | 122.1909 | -121.9162 | 0.15564 | -0.076904 | 0.015274 | 0.0033752 | 0.0027685 | -0.0054068 | 0.0030698 | -0.0030975 | -0.10399 | -0.0044369 | -0.0030484 | -0.0015488 | 0.0062441 | -0.009094 | 0.073242 | 0.032043 | 0.013733 | 0.013733 | 0.11902 | -0.004578 | -0.13275 | 0.054932 | 0.018311 | -0.07782 | 0.082397 | 0.054932 | -0.082397 | -0.12817 | 121.9116 | 121.7834 | -0.036621 | 121.9482 | 121.9299 | 0.14648 | -0.082398 | 121.8338 | 121.788 | -0.073243 | 121.9711 | 121.8384 | 0.050354 | -0.10071 | 122.0352 | 121.9894 | 121.9299 | -0.28839 | 121.9986 | 121.9711 | 121.9345 | -0.28381
718.4062 | 122.2549 | -121.9025 | 0.13733 | -0.25238 | 0.018906 | 0.0033752 | 0.0072547 | -0.0047658 | -0.0029118 | -0.0035249 | -0.24895 | -0.0059323 | -0.0036892 | -0.00090781 | 0.0030399 | -0.0086666 | 0.068665 | 0.050354 | 0.050354 | 0.041199 | 0.21057 | 0.054932 | -0.059509 | 0.054932 | 0.11444 | -0.036621 | 0.15564 | 0.13275 | -0.013733 | -0.086975 | 121.9574 | 121.843 | 0.073242 | 121.9528 | 121.9437 | 0.10071 | -0.068664 | 121.8887 | 121.8155 | 0.018311 | 121.9574 | 121.8658 | 0.050354 | -0.004578 | 122.113 | 121.9711 | 121.9528 | -0.19684 | 122.0581 | 122.0352 | 122.0169 | -0.2243
720.1406 | 122.1542 | -121.9208 | 0.16937 | 0.12909 | 0.015701 | 0.0033752 | 0.0014867 | -0.0026296 | -0.005048 | -0.0018159 | 0.15541 | -0.0080685 | -0.0053982 | 0.00058739 | 0.0021853 | -0.0063168 | 0.009155 | 0.050354 | 0.059509 | -0.004578 | 0.027466 | -0.027466 | -0.14648 | 0.09613 | 0.068665 | -0.018311 | 0.013733 | -0.013733 | -0.09613 | -0.14648 | 121.8933 | 121.7743 | -0.14191 | 121.9711 | 121.9162 | 0.14191 | -0.16022 | 121.8246 | 121.7743 | -0.15564 | 122.0169 | 121.9025 | 0.12817 | -0.18311 | 121.9482 | 121.9299 | 121.9803 | -0.31586 | 121.9345 | 121.907 | 121.9894 | -0.31586
721.875 | 122.3007 | -121.9116 | 0.1236 | -0.17609 | 0.018051 | 0.0048706 | 0.0059729 | -0.0045522 | 0.0032834 | -0.0011749 | -0.24132 | -0.0070003 | -0.0051846 | 0.00016019 | 0.0021853 | -0.0099484 | 0.068665 | 0.041199 | 0.022888 | 0.068665 | 0.1831 | 0.041199 | -0.09613 | 0.036621 | 0.059509 | -0.068665 | 0.12817 | 0.09613 | -0.059509 | -0.10986 | 121.9528 | 121.8155 | 0.059509 | 121.9528 | 121.9803 | 0.16479 | -0.054931 | 121.8521 | 121.8018 | 0.004578 | 121.9482 | 121.843 | 0.041198 | -0.027466 | 122.0947 | 121.9803 | 121.9345 | -0.21973 | 122.0398 | 122.0078 | 121.9711 | -0.23346
723.5469 | 122.287 | -121.907 | 0.1236 | -0.061646 | 0.017624 | 0.0059388 | 0.0040503 | -0.0011342 | -0.0063296 | -0.0037385 | -0.020065 | -0.0091367 | -0.0024076 | -0.00048061 | -0.0012327 | -0.0086666 | 0.11444 | 0.15106 | 0.13733 | 0.10986 | 0.12817 | 0.054932 | -0.09613 | 0.1831 | 0.26093 | 0.10529 | 0.091553 | 0.07782 | 0.004578 | -0.086975 | 121.962 | 121.8109 | 0.004578 | 122.0581 | 122.0169 | 0.20599 | -0.009155 | 121.9116 | 121.8201 | -0.032043 | 122.0901 | 122.0123 | 0.19226 | -0.045776 | 122.0352 | 122.0215 | 122.0444 | -0.21973 | 121.9986 | 121.9849 | 122.168 | -0.21057
725.2969 | 122.2778 | -121.9254 | 0.13733 | -0.22186 | 0.018906 | 0.0040162 | 0.0061865 | -0.0039114 | 0.00029262 | -0.0050201 | -0.25658 | -0.0059323 | -0.0030484 | 0.00037379 | 0.0017581 | -0.0088804 | 0.064087 | 0.059509 | 0.045776 | 0.059509 | 0.22888 | 0.050354 | -0.064087 | 0.059509 | 0.11444 | -0.022888 | 0.16937 | 0.13275 | -0.022888 | -0.073242 | 121.9757 | 121.8613 | 0.091553 | 121.9849 | 121.9849 | 0.1236 | -0.073242 | 121.9025 | 121.8521 | 0.032044 | 121.9849 | 121.9025 | 0.050354 | -0.004578 | 122.1542 | 121.9894 | 121.9711 | -0.20142 | 122.0947 | 122.0581 | 122.0398 | -0.21057
726.9531 | 122.1863 | -121.9528 | 0.15564 | 0.052795 | 0.013352 | 0.006366 | 0.0025549 | -0.0054068 | -0.003339 | -0.0045929 | 0.086746 | -0.0067867 | -0.0045438 | -0.0013352 | 0.0017581 | -0.0061032 | 0.018311 | 0.050354 | 0.041199 | 0.032043 | 0.10529 | 0.027466 | -0.11444 | 0.086975 | 0.13275 | 0 | 0.082397 | 0.073242 | -0.045776 | -0.10071 | 121.9803 | 121.8384 | -0.050354 | 122.0032 | 121.9849 | 0.14648 | -0.13733 | 121.907 | 121.8521 | -0.073243 | 122.0398 | 121.9528 | 0.10071 | -0.082398 | 122.0581 | 121.9711 | 121.994 | -0.27008 | 122.0352 | 122.0261 | 122.0856 | -0.25635
728.6875 | 122.1954 | -121.962 | 0.15106 | 0.037537 | 0.013138 | 0.0040162 | 0.0014867 | -0.0043386 | -0.0035526 | -0.0060883 | 0.094375 | -0.0089229 | -0.0064664 | -0.0021896 | 0.0032535 | -0.0063168 | 0.041199 | 0.050354 | 0.032043 | 0.022888 | 0.091553 | 0.013733 | -0.09613 | 0.082397 | 0.12817 | -0.018311 | 0.091553 | 0.054932 | -0.027466 | -0.09613 | 121.9757 | 121.8658 | -0.059509 | 122.0123 | 121.9849 | 0.11902 | -0.10986 | 121.9345 | 121.8658 | -0.059509 | 122.0444 | 121.9437 | 0.077819 | -0.09613 | 122.0535 | 122.0032 | 121.994 | -0.24719 | 122.0535 | 122.0169 | 122.0901 | -0.24719
730.4375 | 122.1954 | -121.9711 | 0.15564 | 0.090942 | 0.017624 | 0.004657 | 0.0010595 | -0.0036978 | 0.0043514 | -0.0020295 | 0.018082 | -0.0059323 | -0.0053982 | -0.0013352 | 0.0077395 | -0.009094 | -0.022888 | -0.11902 | -0.10529 | -0.068665 | 0.10071 | -0.059509 | -0.2243 | -0.013733 | -0.14191 | -0.17395 | 0.045776 | 0.032043 | -0.11902 | -0.19684 | 121.9116 | 121.7468 | -0.054932 | 121.8521 | 121.9025 | 0.15564 | -0.17853 | 121.8521 | 121.7743 | -0.10986 | 121.9574 | 121.7972 | 0.022888 | -0.1236 | 122.0718 | 121.9482 | 121.8658 | -0.37994 | 122.0169 | 122.0032 | 121.8292 | -0.35248
732.1719 | 122.1725 | -121.962 | 0.15564 | 0.13672 | 0.01442 | 0.0031616 | 0.0021277 | -0.0071158 | -0.0029118 | -0.0048065 | 0.079117 | -0.0076413 | -0.0026212 | -0.0017624 | 0.0015445 | -0.0063168 | 0.018311 | 0.050354 | 0.045776 | -0.013733 | 0.018311 | -0.045776 | -0.15106 | 0.091553 | 0.09613 | 0 | 0.054932 | 0.045776 | -0.041199 | -0.10071 | 121.9162 | 121.8109 | -0.13733 | 122.0123 | 121.9482 | 0.13733 | -0.13733 | 121.9208 | 121.8613 | -0.10071 | 122.0535 | 121.962 | 0.10071 | -0.10986 | 121.9803 | 121.9803 | 122.0078 | -0.3067 | 122.0169 | 122.0078 | 122.0581 | -0.25635
733.8281 | 122.2275 | -121.9666 | 0.14191 | 0.1825 | 0.014206 | 0.0016662 | 0.0017005 | -0.0047658 | 0.00093342 | -0.00096127 | 0.13252 | -0.0074277 | -0.0071072 | 0.00016019 | 0.0049625 | -0.0086666 | 0 | -0.018311 | -0.022888 | -0.032043 | 0.032043 | -0.050354 | -0.19226 | 0.07782 | 0.018311 | -0.045776 | 0.013733 | 0 | -0.068665 | -0.12817 | 121.9162 | 121.7743 | -0.10986 | 121.9482 | 121.9345 | 0.16022 | -0.14191 | 121.8979 | 121.8384 | -0.12817 | 122.0444 | 121.9208 | 0.082398 | -0.14191 | 121.9986 | 121.9666 | 121.9437 | -0.33417 | 121.9803 | 121.9666 | 121.9849 | -0.27008
735.5625 | 122.1954 | -121.9849 | 0.15564 | 0.17487 | 0.014206 | 0.0027344 | 0.00084592 | -0.0062612 | -0.00098918 | -0.0037385 | 0.19356 | -0.0057187 | -0.0073208 | -0.00026701 | 0.0034671 | -0.0063168 | 0.045776 | 0.013733 | 0.013733 | -0.018311 | -0.004578 | -0.041199 | -0.18768 | 0.091553 | 0.050354 | -0.045776 | -0.018311 | -0.022888 | -0.10529 | -0.16937 | 121.9437 | 121.7972 | -0.16022 | 121.9986 | 121.9666 | 0.16937 | -0.10986 | 121.8796 | 121.8155 | -0.17395 | 122.0764 | 121.9391 | 0.1236 | -0.17853 | 121.9803 | 122.0306 | 121.9986 | -0.34332 | 121.9666 | 121.962 | 122.0352 | -0.32501
737.2344 | 122.1954 | -121.9894 | 0.15564 | -0.023499 | 0.019119 | 0.0031616 | 0.0068273 | -0.0054068 | 0.0049924 | -0.0041657 | -0.020065 | -0.0063595 | -0.0034756 | 0.0012284 | 0.0036807 | -0.0082394 | 0.041199 | -0.041199 | -0.041199 | -0.036621 | 0.10071 | -0.027466 | -0.16937 | -0.022888 | -0.082397 | -0.15564 | 0.045776 | 0.036621 | -0.11444 | -0.18768 | 121.962 | 121.8201 | -0.054932 | 121.9482 | 121.9528 | 0.13275 | -0.11444 | 121.875 | 121.8018 | -0.10986 | 121.9666 | 121.8338 | 0.032043 | -0.11902 | 122.0901 | 122.0306 | 121.9482 | -0.32501 | 122.0352 | 122.0261 | 121.907 | -0.34332
738.9688 | 122.3145 | -121.9482 | 0.13733 | -0.12268 | 0.016129 | 0.0048706 | 0.0064001 | -0.0047658 | -0.0056888 | -0.0033111 | -0.11162 | -0.0097775 | -0.0030484 | -0.0028306 | -0.0018735 | -0.0063168 | 0.16937 | 0.19226 | 0.17395 | 0.12817 | 0.14648 | 0.07782 | -0.068665 | 0.1831 | 0.31586 | 0.11444 | 0.10529 | 0.10071 | 0.009155 | -0.050354 | 122.0261 | 121.8796 | 0.009155 | 122.1405 | 122.0764 | 0.19684 | 0.032044 | 121.9574 | 121.8979 | -0.032043 | 122.1313 | 122.0627 | 0.16479 | -0.036621 | 122.0947 | 122.1176 | 122.1222 | -0.20599 | 122.0535 | 122.0489 | 122.2641 | -0.18768
740.6406 | 122.3373 | -121.9757 | 0.1236 | -0.19897 | 0.018478 | 0.0035888 | 0.0068273 | -0.0026296 | 0.00029262 | -0.0050201 | -0.19554 | -0.0063595 | -0.0024076 | 0.00251 | 0.0047489 | -0.0093076 | 0.082397 | 0.045776 | 0.036621 | 0.068665 | 0.18768 | 0.041199 | -0.09613 | 0.059509 | 0.059509 | -0.068665 | 0.10071 | 0.07782 | -0.064087 | -0.12817 | 122.0169 | 121.8796 | 0.064087 | 122.0215 | 122.0444 | 0.16479 | -0.041199 | 121.9116 | 121.8475 | -0.022888 | 122.0352 | 121.907 | 0.059509 | -0.045776 | 122.1634 | 122.0581 | 122.0123 | -0.21973 | 122.0764 | 122.0535 | 122.0352 | -0.25177
742.375 | 122.2046 | -121.9849 | 0.16479 | 0.13672 | 0.015274 | 0.0038024 | 0.0010595 | -0.0017752 | -0.0024844 | -0.0030975 | 0.16304 | -0.0084957 | -0.0039028 | -0.0013352 | 0.00068993 | -0.0078122 | 0.027466 | 0.050354 | 0.059509 | -0.004578 | 0.032043 | -0.013733 | -0.16479 | 0.086975 | 0.07782 | -0.027466 | 0.009155 | -0.009155 | -0.082397 | -0.14191 | 121.9711 | 121.8201 | -0.13275 | 122.0352 | 121.9803 | 0.16022 | -0.13733 | 121.9025 | 121.843 | -0.15564 | 122.0718 | 121.9574 | 0.11444 | -0.17395 | 122.0169 | 122.0123 | 122.0444 | -0.32959 | 121.994 | 121.9757 | 122.0627 | -0.3067
744.1094 | 122.3373 | -121.962 | 0.1236 | -0.10742 | 0.018265 | 0.0035888 | 0.0044775 | -0.004125 | 0.0011472 | -0.00074767 | -0.15739 | -0.0059323 | -0.0045438 | -5.3406e-05 | 0.0036807 | -0.0097348 | 0.082397 | 0.022888 | 0.022888 | 0.036621 | 0.14648 | 0 | -0.13733 | 0.068665 | 0.054932 | -0.073242 | 0.086975 | 0.059509 | -0.07782 | -0.13733 | 121.962 | 121.8246 | 0.022888 | 121.9849 | 121.9986 | 0.17395 | -0.041199 | 121.8842 | 121.8246 | -0.036621 | 122.0306 | 121.8887 | 0.064087 | -0.064087 | 122.1085 | 122.0444 | 121.9849 | -0.26093 | 122.0489 | 122.0215 | 122.0169 | -0.26093
745.7812 | 122.2595 | -122.0032 | 0.15106 | 0.1825 | 0.015701 | 0.00017099 | 0.0031957 | -0.0022024 | -0.00013458 | -0.0011749 | 0.14015 | -0.0052915 | -0.0045438 | 0.001442 | 0.0045351 | -0.0088804 | 0.004578 | -0.036621 | -0.018311 | -0.032043 | 0.032043 | -0.050354 | -0.19684 | 0.086975 | 0.036621 | -0.036621 | 0 | -0.004578 | -0.07782 | -0.14648 | 121.9528 | 121.8063 | -0.11902 | 121.9666 | 121.9711 | 0.1648 | -0.14648 | 121.9254 | 121.8567 | -0.15106 | 122.0901 | 121.9666 | 0.10986 | -0.15564 | 122.0352 | 122.0078 | 121.9849 | -0.3479 | 122.0032 | 121.9986 | 122.0398 | -0.29755
747.5156 | 122.3511 | -121.9666 | 0.11444 | -0.23712 | 0.015061 | 0.0033752 | 0.0042639 | -0.002416 | -0.0018436 | -0.0037385 | -0.18791 | -0.0035825 | -0.0045438 | -0.0015488 | 0.0019717 | -0.007385 | 0.064087 | 0.064087 | 0.013733 | 0.064087 | 0.23346 | 0.050354 | -0.068665 | 0.041199 | 0.07782 | -0.064087 | 0.14648 | 0.11444 | -0.032043 | -0.10986 | 122.0169 | 121.8979 | 0.11902 | 122.0306 | 122.0306 | 0.13275 | -0.050354 | 121.9345 | 121.8567 | 0.032043 | 122.0078 | 121.9025 | 0.045776 | 0 | 122.2 | 122.0306 | 121.9803 | -0.18311 | 122.113 | 122.081 | 122.0444 | -0.2243
749.25 | 122.2549 | -122.0261 | 0.14648 | 0.037537 | 0.013138 | 0.0033752 | 0.0036231 | -0.0036978 | -0.0048344 | -0.0039521 | 0.102 | -0.0084957 | -0.0019802 | -0.0017624 | 0.0011173 | -0.005035 | 0.009155 | 0.041199 | 0.050354 | 0.027466 | 0.10529 | 0.022888 | -0.14191 | 0.082397 | 0.14191 | 0.013733 | 0.07782 | 0.059509 | -0.036621 | -0.09613 | 122.0489 | 121.8842 | -0.041198 | 122.0673 | 122.0535 | 0.16937 | -0.13733 | 121.9894 | 121.9299 | -0.068664 | 122.1085 | 122.0398 | 0.10986 | -0.086975 | 122.1313 | 122.0352 | 122.0764 | -0.28839 | 122.1039 | 122.0856 | 122.168 | -0.24261
750.9844 | 122.2366 | -122.0032 | 0.16479 | 0.037537 | 0.012711 | 0.004657 | 0.0023413 | -0.0049796 | -0.0041934 | -0.0048065 | 0.102 | -0.0074277 | -0.0041164 | -0.0028306 | 0.0023989 | -0.0080258 | 0.013733 | 0.041199 | 0.045776 | 0.022888 | 0.10986 | 0.022888 | -0.11902 | 0.082397 | 0.12817 | 0 | 0.068665 | 0.050354 | -0.045776 | -0.11444 | 122.0261 | 121.8842 | -0.054932 | 122.0444 | 122.0261 | 0.14191 | -0.15106 | 121.9574 | 121.8887 | -0.09613 | 122.0856 | 122.0032 | 0.11444 | -0.11444 | 122.113 | 122.0169 | 122.049 | -0.28381 | 122.0718 | 122.0535 | 122.1313 | -0.27924
752.7188 | 122.3145 | -121.994 | 0.14648 | -0.24475 | 0.016769 | 0.0067932 | 0.0031957 | -0.0028432 | -0.00056178 | -0.0054475 | -0.21843 | -0.0065731 | -0.004971 | -0.0017624 | 0.0015445 | -0.0086666 | 0.13275 | 0.11902 | 0.09613 | 0.086975 | 0.21057 | 0.064087 | -0.073242 | 0.09613 | 0.15106 | -0.022888 | 0.16022 | 0.11902 | -0.004578 | -0.068665 | 122.0581 | 121.9208 | 0.064087 | 122.113 | 122.081 | 0.16022 | -0.013733 | 121.9894 | 121.9254 | 0.013733 | 122.0901 | 121.9711 | 0.045777 | -0.027465 | 122.2046 | 122.1268 | 122.0901 | -0.21973 | 122.1542 | 122.113 | 122.1451 | -0.21515
754.3906 | 122.3465 | -121.9666 | 0.13275 | -0.11505 | 0.016769 | 0.0038024 | 0.0061865 | -0.0034842 | -0.0052616 | -0.0043793 | -0.14214 | -0.0087093 | -0.0026212 | 0.00058739 | 4.9132e-05 | -0.0093076 | 0.15106 | 0.21515 | 0.19684 | 0.1236 | 0.13275 | 0.059509 | -0.059509 | 0.19226 | 0.3067 | 0.1236 | 0.12817 | 0.082397 | 0.018311 | -0.045776 | 122.0261 | 121.907 | 0 | 122.1817 | 122.0901 | 0.1831 | 0.018311 | 121.9849 | 121.9208 | -0.004577 | 122.1588 | 122.0901 | 0.16937 | -0.050354 | 122.0993 | 122.1176 | 122.1634 | -0.19226 | 122.0947 | 122.049 | 122.2733 | -0.17853
756.1406 | 122.3831 | -121.9803 | 0.12817 | -0.19135 | 0.019974 | 0.0031616 | 0.0042639 | -0.0017752 | 0.0022152 | -0.0048065 | -0.22606 | -0.0061459 | -0.0024076 | -5.3406e-05 | 0.0034671 | -0.0097348 | 0.082397 | 0.041199 | 0.022888 | 0.064087 | 0.21515 | 0.054932 | -0.10529 | 0.059509 | 0.086975 | -0.059509 | 0.13733 | 0.10529 | -0.045776 | -0.11444 | 122.0352 | 121.875 | 0.086975 | 122.0215 | 122.0444 | 0.16937 | -0.045777 | 121.9345 | 121.8658 | 0.009155 | 122.0398 | 121.9208 | 0.054932 | -0.022888 | 122.1954 | 122.0627 | 122.0032 | -0.23346 | 122.1176 | 122.0856 | 122.0673 | -0.24262
757.8125 | 122.3785 | -122.0169 | 0.11444 | -0.17609 | 0.01741 | 0.0038024 | 0.00041872 | -0.0054068 | 0.0024288 | -0.0026703 | -0.2108 | -0.0063595 | -0.0028348 | -0.00069421 | 0.0051761 | -0.0097348 | 0.073242 | -0.027466 | 0 | 0.054932 | 0.1831 | 0.022888 | -0.11444 | 0.07782 | 0.054932 | -0.059509 | 0.10529 | 0.064087 | -0.086975 | -0.1236 | 122.0398 | 121.9025 | 0.068664 | 121.9894 | 122.0718 | 0.16937 | -0.041199 | 121.9299 | 121.8933 | -0.009155 | 122.0947 | 121.9574 | 0.064087 | -0.050354 | 122.2 | 122.0901 | 122.0169 | -0.22888 | 122.1222 | 122.081 | 122.0718 | -0.23804
759.5469 | 122.3648 | -121.9894 | 0.12817 | -0.015869 | 0.014847 | 0.0061524 | 0.0034093 | -0.0036978 | -0.006757 | -0.0028839 | -0.0048066 | -0.0095639 | -0.006039 | -0.001976 | -0.0014463 | -0.007385 | 0.082397 | 0.10986 | 0.09613 | 0.07782 | 0.13275 | 0.059509 | -0.10986 | 0.16022 | 0.23804 | 0.082397 | 0.082397 | 0.068665 | -0.018311 | -0.064087 | 122.049 | 121.8796 | 0.004577 | 122.0993 | 122.0673 | 0.18768 | -0.045777 | 121.9711 | 121.9254 | -0.045777 | 122.1497 | 122.0718 | 0.14648 | -0.059509 | 122.1222 | 122.0718 | 122.0856 | -0.23804 | 122.0718 | 122.0581 | 122.2275 | -0.19226
761.2812 | 122.3648 | -121.9849 | 0.12817 | -0.0082397 | 0.013779 | 0.0055114 | 0.0042639 | -0.004125 | -0.0035526 | -0.0048065 | 0.0028229 | -0.0065731 | -0.0030484 | -0.0017624 | 0.0011173 | -0.008453 | 0.054932 | 0.091553 | 0.07782 | 0.059509 | 0.10529 | 0.032043 | -0.10529 | 0.14648 | 0.23346 | 0.073242 | 0.10529 | 0.073242 | -0.013733 | -0.082397 | 122.0169 | 121.8796 | -0.022888 | 122.0764 | 122.0444 | 0.16479 | -0.073242 | 121.9711 | 121.9025 | -0.022888 | 122.1313 | 122.0581 | 0.15564 | -0.054932 | 122.0901 | 122.0398 | 122.0627 | -0.23346 | 122.0901 | 122.0581 | 122.2183 | -0.21057
762.9531 | 122.374 | -122.0032 | 0.13275 | -0.11505 | 0.017838 | 0.0020936 | 0.0044775 | -0.0047658 | 0.0056332 | -0.0024567 | -0.15739 | -0.0050777 | -0.0021938 | 0.0012284 | 0.0030399 | -0.013794 | 0.07782 | 0.032043 | 0.018311 | 0.036621 | 0.13733 | 0.004578 | -0.12817 | 0.07782 | 0.050354 | -0.064087 | 0.082397 | 0.036621 | -0.059509 | -0.12817 | 122.0078 | 121.875 | 0.004578 | 122.0352 | 122.0398 | 0.1648 | -0.054931 | 121.9437 | 121.875 | -0.050354 | 122.081 | 121.9391 | 0.064087 | -0.09613 | 122.1405 | 122.081 | 122.0215 | -0.26093 | 122.0856 | 122.0398 | 122.0535 | -0.26093
764.6875 | 122.2549 | -122.0535 | 0.16022 | 0.11383 | 0.013992 | 0.0040162 | 0.0040503 | -0.0064748 | -0.0046206 | -0.0011749 | 0.13252 | -0.0072141 | -0.0036892 | 0.00016019 | 0.00026273 | -0.0080258 | 0.018311 | 0.054932 | 0.068665 | 0 | 0.045776 | -0.009155 | -0.14648 | 0.10529 | 0.10529 | 0 | 0.059509 | 0.059509 | -0.041199 | -0.1236 | 122.0444 | 121.907 | -0.11444 | 122.1085 | 122.0535 | 0.14648 | -0.14191 | 122.0123 | 121.9299 | -0.10071 | 122.1588 | 122.0535 | 0.1236 | -0.10071 | 122.0993 | 122.0718 | 122.1222 | -0.3067 | 122.113 | 122.113 | 122.1588 | -0.28381
766.4375 | 122.2458 | -122.0718 | 0.15564 | 0.12146 | 0.016983 | 0.0050842 | 0.0031957 | -0.0028432 | -0.0024844 | -0.0043793 | 0.15541 | -0.0070003 | -0.0019802 | -0.00090781 | 0.0038943 | -0.009094 | 0.045776 | 0.050354 | 0.059509 | 0 | 0.041199 | -0.027466 | -0.16937 | 0.10529 | 0.07782 | -0.004578 | 0.009155 | -0.018311 | -0.082397 | -0.15106 | 122.0444 | 121.9025 | -0.11444 | 122.1222 | 122.0718 | 0.16937 | -0.10986 | 121.9894 | 121.9208 | -0.14649 | 122.1771 | 122.0673 | 0.14648 | -0.17395 | 122.113 | 122.1176 | 122.1313 | -0.32501 | 122.081 | 122.0535 | 122.1497 | -0.3067
768.1094 | 122.2961 | -122.049 | 0.15564 | 0.098572 | 0.018906 | 0.0050842 | -8.476e-06 | -0.0049796 | 0.00093342 | -0.0041657 | 0.13252 | -0.0063595 | -0.0041164 | 0.0016556 | 0.0066715 | -0.0086666 | -0.027466 | -0.073242 | -0.086975 | -0.07782 | 0.073242 | -0.059509 | -0.21057 | 0.036621 | -0.073242 | -0.091553 | 0.022888 | 0.027466 | -0.10986 | -0.16479 | 121.9894 | 121.8384 | -0.082398 | 121.9757 | 121.9711 | 0.13275 | -0.18311 | 121.9391 | 121.8842 | -0.13275 | 122.0856 | 121.9574 | 0.073242 | -0.12817 | 122.1222 | 122.0215 | 121.962 | -0.36621 | 122.0718 | 122.0764 | 121.9757 | -0.32044
769.8281 | 122.319 | -122.0398 | 0.14648 | -0.2066 | 0.015701 | 0.0055114 | 0.0055457 | -0.0028432 | -0.0022708 | -0.0037385 | -0.21843 | -0.0076413 | -0.0013394 | -0.0015488 | 0.00090353 | -0.0080258 | 0.13733 | 0.15564 | 0.13275 | 0.13275 | 0.16479 | 0.07782 | -0.07782 | 0.11444 | 0.2243 | 0.032043 | 0.13275 | 0.13733 | 0 | -0.064087 | 122.1176 | 121.962 | 0.018311 | 122.1954 | 122.1725 | 0.21057 | -0.009155 | 122.0398 | 121.9757 | -0.013733 | 122.1542 | 122.0718 | 0.09613 | -0.009155 | 122.2046 | 122.1771 | 122.1725 | -0.2243 | 122.1725 | 122.1771 | 122.2641 | -0.21057
771.5 | 122.3785 | -122.0078 | 0.1236 | -0.099793 | 0.018692 | 0.0031616 | 0.0059729 | -0.0049796 | 0.0026424 | -0.0024567 | -0.18028 | -0.0063595 | -0.0021938 | -0.00090781 | 0.0036807 | -0.01123 | 0.054932 | 0.050354 | 0.027466 | 0.032043 | 0.14191 | 0.004578 | -0.13275 | 0.086975 | 0.054932 | -0.050354 | 0.091553 | 0.068665 | -0.07782 | -0.14648 | 122.0123 | 121.875 | 0.018311 | 122.0581 | 122.0398 | 0.16479 | -0.068664 | 121.9299 | 121.8613 | -0.032043 | 122.0947 | 121.9574 | 0.09613 | -0.054931 | 122.1497 | 122.0627 | 122.0352 | -0.25635 | 122.0993 | 122.0764 | 122.0627 | -0.27008
773.2344 | 122.3969 | -122.0306 | 0.10986 | -0.11505 | 0.013779 | 0.0048706 | 0.0057593 | -0.0034842 | -0.0037662 | -0.0033111 | -0.042954 | -0.0074277 | -0.0041164 | 0.00037379 | -0.00016447 | -0.0069578 | 0.1236 | 0.18768 | 0.15106 | 0.10986 | 0.13733 | 0.07782 | -0.082397 | 0.21057 | 0.29755 | 0.11444 | 0.082397 | 0.054932 | 0.004578 | -0.045776 | 122.1085 | 121.9482 | 0.027466 | 122.2183 | 122.1405 | 0.19226 | 0.013733 | 122.0352 | 121.9849 | -0.027466 | 122.2412 | 122.1451 | 0.16022 | -0.054931 | 122.168 | 122.1542 | 122.1817 | -0.19226 | 122.113 | 122.0856 | 122.3282 | -0.15564
774.9844 | 122.3831 | -122.0261 | 0.12817 | -0.12268 | 0.016342 | 0.001239 | 0.0010595 | -0.0034842 | 0.0030698 | -0.0020295 | -0.15739 | -0.0055051 | -0.0047574 | -0.00069421 | 0.0060305 | -0.0093076 | 0.07782 | 0.050354 | 0.022888 | 0.036621 | 0.15106 | 0 | -0.13733 | 0.073242 | 0.041199 | -0.059509 | 0.086975 | 0.059509 | -0.07782 | -0.14648 | 122.0261 | 121.8887 | 0.022888 | 122.0764 | 122.0627 | 0.17395 | -0.050354 | 121.9482 | 121.8796 | -0.041199 | 122.0993 | 121.9666 | 0.086975 | -0.068665 | 122.1771 | 122.1039 | 122.0489 | -0.2655 | 122.113 | 122.0856 | 122.0673 | -0.27466
776.7188 | 122.4014 | -122.0261 | 0.11902 | -0.14557 | 0.016342 | 0.0042298 | 0.0081091 | -0.0060476 | -0.0041934 | -0.0024567 | -0.058212 | -0.0095639 | -0.003262 | 0.0012284 | -0.00059167 | -0.0071714 | 0.10071 | 0.18768 | 0.16022 | 0.10986 | 0.13275 | 0.073242 | -0.064087 | 0.19226 | 0.27924 | 0.10071 | 0.086975 | 0.059509 | -0.004578 | -0.064087 | 122.0993 | 121.962 | 0.013732 | 122.2137 | 122.1359 | 0.17395 | -0.018311 | 122.0215 | 121.962 | -0.032044 | 122.2183 | 122.1268 | 0.1648 | -0.05951 | 122.1588 | 122.1268 | 122.1863 | -0.18311 | 122.113 | 122.0856 | 122.3053 | -0.18311
778.3906 | 122.3511 | -122.0856 | 0.13275 | 0.045166 | 0.012711 | 0.0057252 | 0.0023413 | -0.002416 | -0.0018436 | -0.0058747 | 0.048599 | -0.0091367 | -0.0056118 | -0.0011216 | 0.0028263 | -0.0075986 | 0.004578 | 0.064087 | 0.050354 | 0.027466 | 0.09613 | 0.022888 | -0.10071 | 0.10986 | 0.14191 | 0.018311 | 0.073242 | 0.059509 | -0.032043 | -0.091553 | 122.1085 | 121.9849 | -0.036621 | 122.1497 | 122.113 | 0.12817 | -0.12817 | 122.0535 | 121.994 | -0.059509 | 122.1954 | 122.1039 | 0.10986 | -0.073242 | 122.1817 | 122.0901 | 122.1359 | -0.23346 | 122.1588 | 122.1451 | 122.2275 | -0.2243
780.125 | 122.4106 | -122.049 | 0.13275 | -0.023499 | 0.016556 | 0.0042298 | 0.0044775 | -0.0066884 | -0.0052616 | -0.0065155 | -0.020065 | -0.0078549 | -0.0051846 | -0.00069421 | 0.0011173 | -0.0095212 | 0.054932 | 0.082397 | 0.073242 | 0.059509 | 0.13733 | 0.013733 | -0.10529 | 0.15106 | 0.21515 | 0.07782 | 0.10529 | 0.07782 | 0.004578 | -0.064087 | 122.0627 | 121.9437 | 0.004578 | 122.1313 | 122.1085 | 0.16479 | -0.077819 | 122.0535 | 121.9849 | -0.027465 | 122.2 | 122.1268 | 0.14191 | -0.054931 | 122.1863 | 122.1039 | 122.1222 | -0.23804 | 122.1542 | 122.1268 | 122.2641 | -0.19684
781.8594 | 122.3373 | -122.0901 | 0.16937 | 0.12909 | 0.016342 | 0.004657 | 0.0012731 | -0.0047658 | 0.0024288 | -0.0030975 | 0.04097 | -0.0067867 | -0.007748 | -5.3406e-05 | 0.0062441 | -0.009094 | -0.022888 | -0.09613 | -0.10529 | -0.082397 | 0.086975 | -0.07782 | -0.20599 | 0.018311 | -0.10529 | -0.12817 | 0.068665 | 0.027466 | -0.10071 | -0.16937 | 122.0123 | 121.8842 | -0.082398 | 121.994 | 122.0078 | 0.1236 | -0.19226 | 121.9894 | 121.9208 | -0.10071 | 122.1085 | 121.962 | 0.041199 | -0.14191 | 122.1771 | 122.0673 | 121.9849 | -0.37537 | 122.1588 | 122.1176 | 121.9849 | -0.33875
783.5312 | 122.2916 | -122.1039 | 0.16479 | -0.076904 | 0.019333 | 0.0031616 | 0.0061865 | -0.0049796 | 0.0047788 | -0.0011749 | -0.10399 | -0.0055051 | -0.0043302 | 0.00016019 | 0.0034671 | -0.0095212 | 0.068665 | 0.032043 | 0.009155 | 0 | 0.11902 | -0.009155 | -0.15106 | 0.050354 | -0.018311 | -0.09613 | 0.050354 | 0.050354 | -0.091553 | -0.16022 | 122.0947 | 121.9528 | -0.045776 | 122.1359 | 122.1039 | 0.15106 | -0.09613 | 122.0123 | 121.9437 | -0.11444 | 122.1542 | 122.0078 | 0.064087 | -0.11444 | 122.2229 | 122.1725 | 122.113 | -0.31586 | 122.1542 | 122.1542 | 122.0856 | -0.32501
785.3906 | 122.3007 | -122.0627 | 0.16479 | 0.19012 | 0.016769 | 0.0050842 | 0.00063232 | -0.0043386 | -0.002698 | -0.0024567 | 0.19356 | -0.0074277 | -0.0075344 | -0.00069421 | 0.0053897 | -0.0086666 | 0.013733 | 0.018311 | 0.027466 | -0.013733 | 0.004578 | -0.041199 | -0.1831 | 0.07782 | 0.054932 | -0.027466 | -0.027466 | -0.045776 | -0.10071 | -0.16022 | 122.0215 | 121.8796 | -0.16022 | 122.081 | 122.049 | 0.16937 | -0.15106 | 121.962 | 121.9025 | -0.19226 | 122.1405 | 122.0352 | 0.13275 | -0.21057 | 122.0673 | 122.0764 | 122.0901 | -0.3479 | 122.0352 | 122.0169 | 122.1176 | -0.32501
787.1406 | 122.2961 | -122.1313 | 0.15106 | 0.045166 | 0.012711 | 0.0014526 | 0.0025549 | -0.0032706 | -0.0048344 | -0.0037385 | 0.11726 | -0.0082821 | -0.0039028 | -0.00048061 | 0.0021853 | -0.007385 | 0.022888 | 0.045776 | 0.054932 | 0.022888 | 0.09613 | 0.004578 | -0.12817 | 0.086975 | 0.1236 | -0.004578 | 0.082397 | 0.041199 | -0.041199 | -0.10071 | 122.1359 | 122.0032 | -0.054932 | 122.1771 | 122.1542 | 0.15106 | -0.12817 | 122.0901 | 122.0306 | -0.068665 | 122.2183 | 122.1268 | 0.09613 | -0.10986 | 122.2275 | 122.1542 | 122.1863 | -0.27924 | 122.2137 | 122.1725 | 122.2549 | -0.25177
788.875 | 122.287 | -122.1039 | 0.16479 | 0.14435 | 0.017197 | 0.0035888 | 0.0019141 | -0.0049796 | -0.0029118 | -0.0026703 | 0.15541 | -0.0076413 | -0.004971 | -0.001976 | 0.0056033 | -0.008453 | 0.027466 | 0.041199 | 0.041199 | -0.013733 | 0.022888 | -0.050354 | -0.17395 | 0.09613 | 0.073242 | -0.013733 | 0.004578 | 0 | -0.086975 | -0.13733 | 122.0535 | 121.9299 | -0.14191 | 122.1451 | 122.0901 | 0.16022 | -0.13733 | 122.0169 | 121.9666 | -0.16022 | 122.2 | 122.0901 | 0.1236 | -0.16479 | 122.1268 | 122.1313 | 122.1451 | -0.33874 | 122.1085 | 122.1039 | 122.1771 | -0.30212
790.625 | 122.3969 | -122.0627 | 0.13275 | 0.037537 | 0.012283 | 0.0050842 | 0.0068273 | -0.005834 | -0.0039798 | -0.0084381 | 0.018082 | -0.0067867 | -0.0064664 | -0.0017624 | 0.0015445 | -0.007385 | 0.064087 | 0.045776 | 0.064087 | 0.041199 | 0.11444 | 0.009155 | -0.1236 | 0.10986 | 0.1831 | 0.032043 | 0.091553 | 0.082397 | -0.036621 | -0.086975 | 122.0718 | 121.9391 | -0.01831 | 122.1085 | 122.1039 | 0.16479 | -0.068664 | 122.0261 | 121.9757 | -0.041198 | 122.1725 | 122.0947 | 0.11902 | -0.050354 | 122.1771 | 122.1268 | 122.1268 | -0.25635 | 122.1542 | 122.1451 | 122.2458 | -0.21973
792.2969 | 122.3007 | -122.0627 | 0.13733 | 0.060425 | 0.015701 | 0.004657 | 0.0038367 | -0.0069022 | -0.0024844 | -0.0063019 | 0.063858 | -0.0059323 | -0.0051846 | -5.3406e-05 | 0.00047633 | -0.0078122 | 0.054932 | 0.041199 | 0.059509 | 0.004578 | 0.10529 | 0.013733 | -0.12817 | 0.10986 | 0.10986 | -0.004578 | 0.07782 | 0.068665 | -0.032043 | -0.1236 | 122.0764 | 121.9345 | -0.032043 | 122.1039 | 122.0673 | 0.13275 | -0.082397 | 122.0306 | 121.9391 | -0.059509 | 122.1725 | 122.0581 | 0.11902 | -0.068664 | 122.168 | 122.1176 | 122.1222 | -0.2655 | 122.1405 | 122.1313 | 122.1725 | -0.26093
793.9844 | 122.4106 | -122.0581 | 0.13275 | -0.00061023 | 0.014633 | 0.002948 | 0.0057593 | -0.0071158 | -0.0031254 | -0.0045929 | 0.0028229 | -0.0074277 | -0.0047574 | -0.0013352 | 0.00026273 | -0.0082394 | 0.059509 | 0.059509 | 0.059509 | 0.036621 | 0.13733 | 0.032043 | -0.13275 | 0.13275 | 0.16937 | 0.036621 | 0.10071 | 0.045776 | -0.045776 | -0.086975 | 122.0901 | 121.9254 | 0.004578 | 122.1176 | 122.0947 | 0.16937 | -0.073242 | 122.0123 | 121.9711 | -0.032043 | 122.1909 | 122.0947 | 0.1236 | -0.086975 | 122.1954 | 122.1176 | 122.1176 | -0.2655 | 122.1588 | 122.1039 | 122.2275 | -0.21973
795.6875 | 122.3007 | -122.113 | 0.16022 | 0.068054 | 0.019119 | 0.0025208 | 0.0031957 | -0.0049796 | 0.0043514 | -0.0039521 | -0.027695 | -0.0059323 | -0.0036892 | 0.00037379 | 0.0058169 | -0.0099484 | 0 | -0.10986 | -0.086975 | -0.07782 | 0.09613 | -0.059509 | -0.18768 | -0.032043 | -0.11444 | -0.16937 | 0.073242 | 0.050354 | -0.10529 | -0.19226 | 122.0535 | 121.9254 | -0.064087 | 122.0032 | 122.0352 | 0.10986 | -0.16022 | 122.0078 | 121.9208 | -0.086975 | 122.081 | 121.9437 | 0.022888 | -0.10986 | 122.2092 | 122.113 | 122.0261 | -0.3479 | 122.1863 | 122.1634 | 121.9986 | -0.35248
797.3594 | 122.3602 | -122.1039 | 0.16479 | 0.1825 | 0.016129 | 0.0027344 | 0.0034093 | -0.0036978 | 0.0026424 | -0.0011749 | 0.102 | -0.0063595 | -0.0030484 | 0.0010148 | 0.0045351 | -0.0080258 | -0.027466 | -0.082397 | -0.07782 | -0.068665 | 0.050354 | -0.068665 | -0.20142 | 0.068665 | -0.036621 | -0.073242 | 0.041199 | 0.009155 | -0.11444 | -0.17395 | 122.0352 | 121.9025 | -0.11444 | 122.0215 | 122.0352 | 0.13275 | -0.19226 | 121.9894 | 121.9299 | -0.1236 | 122.1725 | 122.0306 | 0.10071 | -0.15564 | 122.1542 | 122.0764 | 122.0261 | -0.36621 | 122.1451 | 122.113 | 122.0673 | -0.33874
799.0625 | 122.3282 | -122.0718 | 0.15564 | 0.052795 | 0.011429 | 0.0057252 | 0.0036231 | -0.0051932 | -0.0054752 | -0.0043793 | 0.063858 | -0.0072141 | -0.0058254 | 0.0027236 | 0.0028263 | -0.0061032 | 0.036621 | 0.059509 | 0.050354 | 0.013733 | 0.10986 | 0.013733 | -0.13733 | 0.086975 | 0.11902 | 0.009155 | 0.073242 | 0.045776 | -0.045776 | -0.10071 | 122.0856 | 121.9345 | -0.045777 | 122.1313 | 122.0856 | 0.15106 | -0.11902 | 122.0261 | 121.9711 | -0.082398 | 122.1588 | 122.081 | 0.10986 | -0.10986 | 122.1817 | 122.1085 | 122.1222 | -0.29297 | 122.1451 | 122.1176 | 122.1909 | -0.25635
800.75 | 122.3602 | -122.0718 | 0.16937 | 0.14435 | 0.015274 | 0.0033752 | 0.0019141 | -0.0030568 | -0.0014164 | -0.0022431 | 0.1783 | -0.0063595 | -0.004971 | -0.00026701 | 0.0047489 | -0.010589 | 0.050354 | 0.022888 | 0.018311 | 0 | 0.013733 | -0.041199 | -0.17395 | 0.073242 | 0.032043 | -0.050354 | -0.018311 | -0.022888 | -0.086975 | -0.15564 | 122.0306 | 121.8979 | -0.15564 | 122.0947 | 122.0718 | 0.17395 | -0.11902 | 121.9849 | 121.9162 | -0.18768 | 122.1451 | 122.0215 | 0.10529 | -0.19226 | 122.0856 | 122.1222 | 122.0901 | -0.34332 | 122.0535 | 122.049 | 122.1039 | -0.32501
802.4531 | 122.4609 | -122.0856 | 0.11902 | -0.16083 | 0.015915 | 0.0023072 | 0.0064001 | -0.0056204 | 0.0011472 | -0.0024567 | -0.24132 | -0.0074277 | -0.0030484 | 0.003151 | 0.0041079 | -0.0095212 | 0.059509 | 0.032043 | 0.032043 | 0.045776 | 0.20142 | 0.036621 | -0.11902 | 0.054932 | 0.082397 | -0.054932 | 0.13733 | 0.091553 | -0.041199 | -0.10529 | 122.1222 | 121.9666 | 0.082397 | 122.1176 | 122.1313 | 0.16479 | -0.05951 | 122.0444 | 121.9803 | 0.01831 | 122.1405 | 122.0306 | 0.050354 | -0.027466 | 122.287 | 122.1451 | 122.1176 | -0.23804 | 122.2229 | 122.1771 | 122.168 | -0.22431
804.1562 | 122.4014 | -122.0993 | 0.15106 | 0.029907 | 0.015274 | 0.0050842 | 0.0061865 | -0.0045522 | -0.0031254 | -0.0052337 | 0.071487 | -0.0070003 | -0.007748 | -0.0021896 | 0.0011173 | -0.0078122 | 0.041199 | 0.045776 | 0.045776 | 0.041199 | 0.11444 | 0.013733 | -0.11444 | 0.11444 | 0.15106 | 0.004578 | 0.091553 | 0.064087 | -0.036621 | -0.10529 | 122.113 | 121.9849 | -0.036621 | 122.1451 | 122.1405 | 0.15564 | -0.10986 | 122.0627 | 121.994 | -0.059509 | 122.2137 | 122.1039 | 0.10986 | -0.086975 | 122.2137 | 122.1405 | 122.1451 | -0.2655 | 122.1909 | 122.1634 | 122.2504 | -0.25635
805.8281 | 122.3557 | -122.1176 | 0.16479 | 0.090942 | 0.018051 | 0.0025208 | 0.0021277 | -0.00049345 | -0.00056178 | -0.00010687 | 0.19356 | -0.0059323 | -0.0058254 | -0.00069421 | 0.0053897 | -0.007385 | 0.045776 | -0.004578 | 0.009155 | -0.004578 | 0.022888 | -0.041199 | -0.17853 | 0.091553 | 0.036621 | -0.032043 | -0.009155 | -0.032043 | -0.09613 | -0.16479 | 122.0764 | 121.9391 | -0.14191 | 122.113 | 122.113 | 0.17395 | -0.11902 | 122.0215 | 121.9528 | -0.17395 | 122.2092 | 122.0856 | 0.13275 | -0.19684 | 122.1405 | 122.1634 | 122.1268 | -0.34332 | 122.1085 | 122.0856 | 122.1542 | -0.32959
807.5312 | 122.3648 | -122.1222 | 0.16937 | 0.14435 | 0.018265 | 0.0027344 | 0.0014867 | -0.0056204 | 0.00093342 | -0.0039521 | 0.17067 | -0.0063595 | -0.0034756 | 0.00037379 | 0.0041079 | -0.0093076 | 0.045776 | 0.009155 | 0.004578 | -0.004578 | 0.032043 | -0.041199 | -0.19226 | 0.082397 | 0.022888 | -0.022888 | -0.009155 | -0.027466 | -0.10071 | -0.16937 | 122.081 | 121.9299 | -0.13733 | 122.1313 | 122.1176 | 0.18768 | -0.1236 | 122.0215 | 121.9528 | -0.17853 | 122.2046 | 122.0993 | 0.14649 | -0.19684 | 122.1542 | 122.168 | 122.1268 | -0.36163 | 122.113 | 122.0947 | 122.1451 | -0.33875
809.2344 | 122.3328 | -122.1588 | 0.17395 | 0.068054 | 0.020401 | 0.00038459 | 0.0046911 | -0.0022024 | 0.0039242 | -0.00053407 | 0.010452 | -0.0059323 | -0.0024076 | 0.0035782 | 0.0032535 | -0.0097348 | -0.027466 | -0.086975 | -0.09613 | -0.073242 | 0.10071 | -0.054932 | -0.21057 | -0.036621 | -0.14191 | -0.16937 | 0.064087 | 0.041199 | -0.10529 | -0.16937 | 122.1039 | 121.9482 | -0.073242 | 122.0718 | 122.0856 | 0.13733 | -0.20142 | 122.0535 | 121.9894 | -0.10986 | 122.1222 | 121.9894 | 0 | -0.13275 | 122.2595 | 122.1313 | 122.0627 | -0.38452 | 122.2229 | 122.2 | 122.0169 | -0.34332
810.9688 | 122.3648 | -122.1405 | 0.16937 | 0.1062 | 0.018051 | 0.0014526 | 0.0025549 | -0.0066884 | 0.003497 | -0.0041657 | 0.094375 | -0.0065731 | -0.0064664 | 0.00016019 | 0.0045351 | -0.007385 | -0.036621 | -0.10986 | -0.10986 | -0.068665 | 0.09613 | -0.064087 | -0.19684 | -0.027466 | -0.15564 | -0.17395 | 0.050354 | 0.032043 | -0.11902 | -0.18768 | 122.0764 | 121.9437 | -0.073243 | 122.0306 | 122.0718 | 0.12817 | -0.20599 | 122.0215 | 121.9528 | -0.11902 | 122.113 | 121.9666 | 0.013733 | -0.13733 | 122.2366 | 122.1039 | 122.0306 | -0.36621 | 122.1909 | 122.1725 | 121.9849 | -0.35706
812.6719 | 122.3465 | -122.1268 | 0.16937 | -0.061646 | 0.016983 | 0.0042298 | 0.0031957 | -0.00027985 | 0.0024288 | -0.0037385 | -0.073471 | -0.0050777 | -0.0030484 | -0.0011216 | 0.0056033 | -0.007385 | 0.045776 | 0.009155 | -0.013733 | 0 | 0.11902 | -0.013733 | -0.16479 | 0.018311 | -0.032043 | -0.1236 | 0.068665 | 0.045776 | -0.086975 | -0.16022 | 122.113 | 121.962 | -0.050354 | 122.1359 | 122.1268 | 0.16479 | -0.1236 | 122.0398 | 121.9666 | -0.10071 | 122.1451 | 122.0032 | 0.036621 | -0.1236 | 122.2458 | 122.1725 | 122.113 | -0.33417 | 122.1954 | 122.1725 | 122.0947 | -0.32959
814.3594 | 122.3328 | -122.1405 | 0.19684 | 0.0070193 | 0.018478 | 0.0014526 | 0.0049047 | -0.005834 | 0.00071982 | -0.00074767 | 0.04097 | -0.0055051 | -0.0045438 | 0.0010148 | 0.0049625 | -0.0071714 | -0.013733 | -0.050354 | -0.064087 | -0.041199 | 0.10529 | -0.050354 | -0.18768 | -0.018311 | -0.09613 | -0.15106 | 0.059509 | 0.036621 | -0.1236 | -0.17853 | 122.0901 | 121.9528 | -0.091552 | 122.0901 | 122.0993 | 0.14648 | -0.21057 | 122.0169 | 121.962 | -0.13733 | 122.1222 | 121.9894 | 0.027466 | -0.16022 | 122.2458 | 122.1268 | 122.0764 | -0.38452 | 122.2 | 122.1771 | 122.0444 | -0.37537
816.1094 | 122.4014 | -122.1176 | 0.15106 | 0.1825 | 0.016556 | 0.002948 | 0.0029821 | -0.0049796 | -0.00098918 | -0.0033111 | 0.14015 | -0.0059323 | -0.0056118 | -0.00090781 | 0.0043215 | -0.0078122 | -0.027466 | -0.073242 | -0.064087 | -0.064087 | 0.050354 | -0.064087 | -0.21057 | 0.054932 | -0.018311 | -0.054932 | 0.027466 | 0.009155 | -0.10529 | -0.15106 | 122.0535 | 121.907 | -0.10071 | 122.0444 | 122.0535 | 0.14648 | -0.17853 | 122.0123 | 121.9666 | -0.1236 | 122.1725 | 122.0627 | 0.09613 | -0.14191 | 122.168 | 122.0901 | 122.0535 | -0.36163 | 122.1451 | 122.1268 | 122.0993 | -0.30212
817.7812 | 122.4014 | -122.113 | 0.14648 | 0.17487 | 0.014206 | 0.0025208 | 0.0064001 | -0.0054068 | -0.00077538 | -0.00074767 | 0.16304 | -0.0082821 | -0.0053982 | 0.00058739 | 0.0028263 | -0.008453 | -0.022888 | -0.054932 | -0.050354 | -0.050354 | 0.050354 | -0.073242 | -0.19684 | 0.059509 | 0.009155 | -0.032043 | 0.018311 | -0.018311 | -0.09613 | -0.15106 | 122.0398 | 121.9162 | -0.09613 | 122.0581 | 122.0627 | 0.14648 | -0.16937 | 122.0169 | 121.962 | -0.12817 | 122.1725 | 122.081 | 0.11902 | -0.16479 | 122.1634 | 122.0901 | 122.0627 | -0.34332 | 122.1313 | 122.0947 | 122.1222 | -0.29755
819.4844 | 122.3511 | -122.1359 | 0.16479 | 0.12146 | 0.015701 | 0.004657 | 0.0036231 | -0.0056204 | -0.0048344 | -0.0056611 | 0.1783 | -0.0097775 | -0.0041164 | 0.0010148 | 0.0015445 | -0.006744 | 0.022888 | 0.036621 | 0.054932 | 0.009155 | 0.064087 | -0.009155 | -0.13275 | 0.07782 | 0.10071 | -0.009155 | 0.068665 | 0.041199 | -0.041199 | -0.11444 | 122.1268 | 122.0032 | -0.10071 | 122.1725 | 122.1451 | 0.14191 | -0.14191 | 122.0947 | 122.0215 | -0.09613 | 122.2137 | 122.1268 | 0.10529 | -0.1236 | 122.2 | 122.1588 | 122.1909 | -0.29755 | 122.2046 | 122.1771 | 122.2366 | -0.27924
821.1719 | 122.4426 | -122.0947 | 0.12817 | -0.18372 | 0.017624 | 0.0050842 | 0.0074683 | -0.0047658 | -0.0035526 | -0.0056611 | -0.08873 | -0.0097775 | -0.004971 | -0.00048061 | -0.00059167 | -0.0082394 | 0.15106 | 0.15564 | 0.16479 | 0.13275 | 0.17395 | 0.073242 | -0.059509 | 0.14191 | 0.26093 | 0.086975 | 0.11444 | 0.086975 | -0.004578 | -0.082397 | 122.168 | 122.0352 | 0.045776 | 122.2504 | 122.2275 | 0.19226 | 0.022888 | 122.0901 | 122.0123 | -0.013733 | 122.2366 | 122.1817 | 0.16937 | -0.041199 | 122.2687 | 122.2458 | 122.2595 | -0.18768 | 122.2092 | 122.1817 | 122.3557 | -0.21057
822.875 | 122.3877 | -122.1085 | 0.15106 | 0.17487 | 0.015701 | 0.0023072 | 0.0027685 | -0.0043386 | 0.0011472 | -0.0033111 | 0.12489 | -0.0080685 | -0.0056118 | 0.00016019 | 0.0036807 | -0.009094 | 0.032043 | -0.009155 | 0 | -0.013733 | 0.032043 | -0.022888 | -0.17395 | 0.086975 | 0.013733 | -0.032043 | 0.004578 | -0.013733 | -0.086975 | -0.15106 | 122.0856 | 121.9345 | -0.11902 | 122.0993 | 122.0947 | 0.16022 | -0.11902 | 122.0215 | 121.9574 | -0.14648 | 122.1954 | 122.0764 | 0.11902 | -0.16479 | 122.1405 | 122.1405 | 122.1085 | -0.32501 | 122.113 | 122.0947 | 122.1222 | -0.30212
824.5938 | 122.4152 | -122.1222 | 0.15106 | -0.22186 | 0.01741 | 0.0050842 | 0.0066137 | -0.00049345 | -0.0041934 | -0.0054475 | -0.22606 | -0.0076413 | -0.00091223 | -0.0013352 | -0.00037807 | -0.0080258 | 0.13275 | 0.12817 | 0.14648 | 0.10986 | 0.18768 | 0.064087 | -0.086975 | 0.091553 | 0.18768 | 0.018311 | 0.13733 | 0.11444 | -0.018311 | -0.059509 | 122.1863 | 122.0352 | 0.036621 | 122.2504 | 122.2321 | 0.19684 | -0.018311 | 122.1039 | 122.0627 | -0.013733 | 122.2137 | 122.1405 | 0.07782 | -0.036621 | 122.3099 | 122.2549 | 122.2687 | -0.23804 | 122.2595 | 122.2366 | 122.3099 | -0.21057
826.2812 | 122.4197 | -122.1313 | 0.15564 | -0.069275 | 0.018265 | 0.0040162 | 0.0029821 | -0.0056204 | 0.0013608 | -0.0020295 | -0.17265 | -0.0046505 | -0.0039028 | 0.0018692 | 0.0053897 | -0.010589 | 0.091553 | 0.036621 | 0.004578 | 0.013733 | 0.13733 | -0.004578 | -0.15564 | 0.059509 | 0.013733 | -0.068665 | 0.07782 | 0.041199 | -0.068665 | -0.16937 | 122.1268 | 121.9757 | -0.018311 | 122.168 | 122.1451 | 0.16937 | -0.064087 | 122.0627 | 121.962 | -0.07782 | 122.1909 | 122.0627 | 0.10071 | -0.11444 | 122.2687 | 122.2229 | 122.1359 | -0.31128 | 122.2092 | 122.1725 | 122.1451 | -0.32501
828.0156 | 122.3648 | -122.1634 | 0.16479 | 0.16724 | 0.01442 | 0.0020936 | 0.00041872 | -0.0034842 | -0.0018436 | -0.0039521 | 0.1783 | -0.0074277 | -0.0062528 | 0.00037379 | 0.0051761 | -0.0069578 | 0 | 0.013733 | 0.018311 | -0.013733 | 0.009155 | -0.050354 | -0.20142 | 0.10071 | 0.041199 | -0.018311 | -0.009155 | -0.032043 | -0.1236 | -0.16937 | 122.113 | 121.962 | -0.15564 | 122.1771 | 122.1497 | 0.18768 | -0.16479 | 122.0398 | 121.994 | -0.17395 | 122.2641 | 122.1451 | 0.15106 | -0.19684 | 122.1725 | 122.1634 | 122.1817 | -0.36621 | 122.1542 | 122.1313 | 122.2046 | -0.33417
829.6875 | 122.406 | -122.1359 | 0.16479 | 0.1825 | 0.017197 | 0.0025208 | 0.0023413 | -0.0034842 | -0.0018436 | -0.0033111 | 0.14778 | -0.0070003 | -0.0045438 | 0.00058739 | 0.0049625 | -0.0071714 | 0.022888 | 0.009155 | -0.009155 | -0.009155 | 0.032043 | -0.054932 | -0.20599 | 0.10071 | -0.004578 | -0.036621 | 0.018311 | -0.018311 | -0.082397 | -0.14191 | 122.081 | 121.9299 | -0.13275 | 122.1451 | 122.1268 | 0.19684 | -0.14191 | 122.0535 | 121.994 | -0.14648 | 122.2366 | 122.0993 | 0.10529 | -0.18311 | 122.168 | 122.1588 | 122.1268 | -0.37079 | 122.1542 | 122.1176 | 122.1313 | -0.3067
831.3906 | 122.3785 | -122.1497 | 0.1831 | -0.076904 | 0.01741 | 0.0052978 | 0.0034093 | -0.0036978 | 0.0024288 | -0.0030975 | -0.035324 | -0.0057187 | -0.0062528 | -0.00026701 | 0.0060305 | -0.0099484 | 0.050354 | 0.009155 | -0.004578 | 0 | 0.1236 | -0.004578 | -0.13275 | 0.018311 | -0.045776 | -0.11902 | 0.073242 | 0.064087 | -0.091553 | -0.16937 | 122.1451 | 122.0169 | -0.059509 | 122.1588 | 122.1497 | 0.13275 | -0.13275 | 122.0581 | 121.9803 | -0.10986 | 122.168 | 122.0306 | 0.050354 | -0.11902 | 122.2733 | 122.2 | 122.1451 | -0.31586 | 122.2229 | 122.2137 | 122.1039 | -0.35248
833.1094 | 122.4792 | -122.1634 | 0.14191 | -0.22186 | 0.018906 | 0.0044434 | 0.0083227 | -0.0054068 | -0.0035526 | -0.0058747 | -0.22606 | -0.0084957 | -0.0017666 | -0.0013352 | -0.0010191 | -0.0080258 | 0.059509 | 0.059509 | 0.045776 | 0.050354 | 0.22888 | 0.059509 | -0.068665 | 0.064087 | 0.10529 | -0.045776 | 0.16937 | 0.13275 | -0.018311 | -0.09613 | 122.2229 | 122.0947 | 0.086975 | 122.2229 | 122.2137 | 0.11902 | -0.082398 | 122.1451 | 122.0673 | 0.027466 | 122.2275 | 122.1176 | 0.050354 | -0.009156 | 122.3923 | 122.2229 | 122.2092 | -0.21057 | 122.3328 | 122.2961 | 122.2687 | -0.23804
834.7812 | 122.5204 | -122.1222 | 0.1236 | -0.16083 | 0.01976 | 0.0044434 | 0.0076819 | -0.002416 | -0.00034818 | -0.0024567 | -0.22606 | -0.0052915 | -0.0034756 | 0.00080099 | 4.9132e-05 | -0.0099484 | 0.045776 | 0.027466 | 0.013733 | 0.054932 | 0.20599 | 0.050354 | -0.10529 | 0.059509 | 0.082397 | -0.050354 | 0.14191 | 0.11444 | -0.045776 | -0.11444 | 122.1725 | 122.0169 | 0.082398 | 122.1497 | 122.1771 | 0.16022 | -0.07782 | 122.0764 | 122.0078 | 0.018311 | 122.1817 | 122.0718 | 0.064087 | -0.009155 | 122.3282 | 122.168 | 122.1359 | -0.22888 | 122.2641 | 122.2366 | 122.2046 | -0.23804
836.4688 | 122.3602 | -122.168 | 0.16937 | 0.11383 | 0.011429 | 0.0035888 | 0.00084592 | -0.0047658 | -0.0022708 | -0.0045929 | 0.19356 | -0.0093503 | -0.0073208 | -5.3406e-05 | 0.0019717 | -0.009094 | 0.013733 | 0.045776 | 0.036621 | -0.004578 | 0.050354 | -0.036621 | -0.17395 | 0.086975 | 0.091553 | -0.018311 | 0.022888 | 0 | -0.07782 | -0.15564 | 122.1313 | 121.994 | -0.11902 | 122.2137 | 122.1634 | 0.16937 | -0.15564 | 122.0901 | 122.0123 | -0.14649 | 122.2549 | 122.1497 | 0.13733 | -0.16937 | 122.2183 | 122.1817 | 122.2046 | -0.34332 | 122.1909 | 122.168 | 122.2595 | -0.32501
838.1719 | 122.3694 | -122.2046 | 0.17395 | 0.090942 | 0.016556 | 0.0035888 | 0.0014867 | -0.0049796 | 0.0030698 | -0.0028839 | -0.0048066 | -0.0067867 | -0.0056118 | -0.00048061 | 0.0060305 | -0.010162 | -0.041199 | -0.09613 | -0.091553 | -0.064087 | 0.09613 | -0.054932 | -0.19226 | -0.073242 | -0.10986 | -0.16937 | 0.064087 | 0.050354 | -0.11902 | -0.17395 | 122.1497 | 122.0123 | -0.07782 | 122.1085 | 122.1405 | 0.12817 | -0.21515 | 122.0856 | 122.0306 | -0.10986 | 122.1313 | 122.0352 | 0.004577 | -0.1236 | 122.3007 | 122.1634 | 122.113 | -0.36621 | 122.2687 | 122.2549 | 122.0947 | -0.3479
839.8594 | 122.3923 | -122.1405 | 0.15564 | 0.16724 | 0.017197 | 0.0040162 | 0.0014867 | -0.0022024 | -0.0039798 | -0.0050201 | 0.22408 | -0.0055051 | -0.0075344 | 0.00016019 | 0.0028263 | -0.0071714 | 0.032043 | 0 | 0.013733 | 0 | 0.022888 | -0.045776 | -0.1831 | 0.07782 | 0.032043 | -0.027466 | -0.004578 | -0.032043 | -0.1236 | -0.16022 | 122.0947 | 121.9574 | -0.13275 | 122.1405 | 122.1405 | 0.1831 | -0.1236 | 122.0169 | 121.9803 | -0.16022 | 122.2183 | 122.113 | 0.13275 | -0.18768 | 122.1634 | 122.1725 | 122.1542 | -0.33874 | 122.1359 | 122.1085 | 122.1725 | -0.31586
841.5625 | 122.4014 | -122.2 | 0.13275 | 0.14435 | 0.017838 | 0.0040162 | 0.0025549 | -0.0028432 | -0.0014164 | -0.0033111 | 0.21645 | -0.0078549 | -0.0064664 | -0.0015488 | 0.0028263 | -0.0069578 | 0.041199 | -0.004578 | 0.018311 | -0.018311 | 0.018311 | -0.041199 | -0.17395 | 0.068665 | 0.022888 | -0.032043 | -0.018311 | -0.013733 | -0.11444 | -0.16937 | 122.1588 | 122.0261 | -0.11444 | 122.1954 | 122.1817 | 0.15564 | -0.091552 | 122.0856 | 122.0306 | -0.15106 | 122.2687 | 122.168 | 0.13733 | -0.14648 | 122.2183 | 122.2412 | 122.2183 | -0.3067 | 122.1817 | 122.1863 | 122.2229 | -0.30212
843.2656 | 122.5067 | -122.1405 | 0.1236 | -0.092163 | 0.016556 | 0.0057252 | 0.0066137 | -0.004125 | -0.0063296 | -0.0045929 | -0.027695 | -0.0093503 | -0.00668 | -0.0015488 | -0.00080527 | -0.0078122 | 0.16479 | 0.14648 | 0.15106 | 0.11902 | 0.16479 | 0.064087 | -0.07782 | 0.19684 | 0.28381 | 0.091553 | 0.10986 | 0.073242 | 0.009155 | -0.068665 | 122.2046 | 122.0627 | 0.041199 | 122.287 | 122.2595 | 0.19684 | 0.041199 | 122.1497 | 122.0718 | -0.013733 | 122.3373 | 122.2321 | 0.16022 | -0.050354 | 122.3053 | 122.3053 | 122.2916 | -0.20142 | 122.2504 | 122.2137 | 122.4243 | -0.19226
845 | 122.4655 | -122.1451 | 0.14191 | -0.25238 | 0.018906 | 0.0031616 | 0.0044775 | -0.005834 | -0.0014164 | -0.0058747 | -0.2108 | -0.0089229 | -0.0019802 | -0.0021896 | 0.0026125 | -0.0099484 | 0.15106 | 0.13733 | 0.1236 | 0.10986 | 0.17395 | 0.086975 | -0.059509 | 0.10529 | 0.19226 | 0 | 0.15106 | 0.14648 | -0.036621 | -0.082397 | 122.2321 | 122.0856 | 0.032043 | 122.2824 | 122.2549 | 0.16937 | 0.009155 | 122.1085 | 122.0627 | 0.009155 | 122.2504 | 122.1451 | 0.082397 | 0.004577 | 122.319 | 122.2961 | 122.2687 | -0.20142 | 122.2961 | 122.2916 | 122.3373 | -0.2243
846.7031 | 122.5204 | -122.1176 | 0.1236 | -0.10742 | 0.016129 | 0.0042298 | 0.0066137 | -0.0054068 | -0.0029118 | -0.0054475 | -0.050583 | -0.0076413 | -0.0047574 | -0.00090781 | -0.00080527 | -0.010589 | 0.16479 | 0.19226 | 0.15106 | 0.1236 | 0.16022 | 0.059509 | -0.073242 | 0.20599 | 0.28839 | 0.1236 | 0.11444 | 0.082397 | -0.004578 | -0.068665 | 122.1771 | 122.0444 | 0.036621 | 122.3099 | 122.2412 | 0.19684 | 0.041199 | 122.113 | 122.049 | -0.009155 | 122.3236 | 122.2412 | 0.19226 | -0.041199 | 122.2778 | 122.2824 | 122.2687 | -0.19684 | 122.2321 | 122.2 | 122.406 | -0.19226
848.4062 | 122.4014 | -122.2046 | 0.17395 | 0.14435 | 0.016556 | 0.0025208 | -0.00022208 | -0.0069022 | 0.0030698 | -0.0028839 | 0.071487 | -0.0063595 | -0.0036892 | 0.00080099 | 0.0075259 | -0.0095212 | -0.036621 | -0.11444 | -0.11444 | -0.068665 | 0.10986 | -0.068665 | -0.20142 | -0.027466 | -0.14191 | -0.16022 | 0.059509 | 0.045776 | -0.10986 | -0.1831 | 122.1359 | 122.0032 | -0.064087 | 122.0901 | 122.1359 | 0.13275 | -0.21057 | 122.0947 | 122.0215 | -0.11444 | 122.1771 | 122.0444 | 0.022888 | -0.12817 | 122.3145 | 122.168 | 122.0901 | -0.37537 | 122.2641 | 122.2504 | 122.0627 | -0.35706
850.1094 | 122.4747 | -122.1497 | 0.11902 | -0.16083 | 0.018692 | 0.0055114 | 0.0066137 | -0.0039114 | -0.005048 | -0.0058747 | -0.11925 | -0.0082821 | -0.0039028 | -0.0015488 | -0.00016447 | -0.008453 | 0.16479 | 0.17395 | 0.16479 | 0.1236 | 0.15106 | 0.073242 | -0.054932 | 0.18768 | 0.30212 | 0.11444 | 0.10529 | 0.082397 | 0.013733 | -0.050354 | 122.2229 | 122.0947 | 0.032043 | 122.3236 | 122.2733 | 0.17853 | 0.045776 | 122.1634 | 122.0993 | -0.013733 | 122.3373 | 122.2641 | 0.16479 | -0.036622 | 122.3007 | 122.3145 | 122.3145 | -0.17395 | 122.2549 | 122.2321 | 122.4518 | -0.16937
851.7812 | 122.5204 | -122.1405 | 0.14648 | -0.13794 | 0.016556 | 0.0031616 | 0.0053321 | -0.0045522 | -0.004407 | -0.0054475 | -0.081101 | -0.0089229 | -0.0043302 | -0.0013352 | -0.0010191 | -0.0082394 | 0.19226 | 0.18768 | 0.17853 | 0.12817 | 0.14648 | 0.054932 | -0.073242 | 0.19684 | 0.28381 | 0.10986 | 0.10986 | 0.09613 | 0.004578 | -0.073242 | 122.1954 | 122.0673 | 0 | 122.3282 | 122.2687 | 0.20142 | 0.045777 | 122.1451 | 122.0673 | -0.036621 | 122.3373 | 122.2504 | 0.18311 | -0.050354 | 122.287 | 122.3328 | 122.319 | -0.21973 | 122.2504 | 122.2366 | 122.4243 | -0.21973
853.4844 | 122.493 | -122.1634 | 0.1236 | -0.18372 | 0.01741 | 0.0048706 | 0.0064001 | -0.00027985 | -0.0029118 | -0.0060883 | -0.13451 | -0.0084957 | -0.0034756 | -0.0015488 | 0.0026125 | -0.0093076 | 0.17395 | 0.17395 | 0.17853 | 0.11902 | 0.16479 | 0.09613 | -0.050354 | 0.17395 | 0.28839 | 0.091553 | 0.091553 | 0.09613 | -0.009155 | -0.07782 | 122.2595 | 122.113 | 0.041199 | 122.3373 | 122.2824 | 0.16937 | 0.050354 | 122.1542 | 122.0856 | -0.032043 | 122.3373 | 122.2549 | 0.16937 | -0.027466 | 122.3282 | 122.3373 | 122.3419 | -0.17395 | 122.2549 | 122.2595 | 122.4518 | -0.20142
855.1875 | 122.4564 | -122.1817 | 0.16022 | 0.19775 | 0.015701 | 0.0033752 | -0.0010767 | -0.0056204 | 0.0015744 | -0.0043793 | 0.11726 | -0.0067867 | -0.007748 | -0.0011216 | 0.0064577 | -0.010803 | 0.018311 | -0.07782 | -0.059509 | -0.064087 | 0.064087 | -0.082397 | -0.1831 | 0.086975 | -0.018311 | -0.050354 | 0.009155 | 0.004578 | -0.10071 | -0.16937 | 122.0993 | 121.9986 | -0.09613 | 122.1039 | 122.1176 | 0.11902 | -0.14191 | 122.081 | 122.0123 | -0.15106 | 122.2687 | 122.1313 | 0.11902 | -0.15564 | 122.2458 | 122.2 | 122.1222 | -0.34332 | 122.1909 | 122.1863 | 122.1634 | -0.32959
856.8906 | 122.5296 | -122.2 | 0.1236 | -0.25238 | 0.014847 | 0.004657 | 0.0070409 | -0.0036978 | 0.00071982 | -0.0028839 | -0.23369 | -0.0065731 | -0.0030484 | -0.00026701 | 0.0030399 | -0.010162 | 0.10071 | 0.050354 | 0.036621 | 0.059509 | 0.23346 | 0.059509 | -0.082397 | 0.054932 | 0.082397 | -0.068665 | 0.15106 | 0.13733 | -0.050354 | -0.11902 | 122.2595 | 122.1176 | 0.10986 | 122.2504 | 122.2595 | 0.14191 | -0.022888 | 122.1497 | 122.081 | 0.027466 | 122.2549 | 122.1313 | 0.050354 | 0.013733 | 122.4335 | 122.3007 | 122.2366 | -0.20599 | 122.3511 | 122.3373 | 122.2824 | -0.24261
858.5625 | 122.5433 | -122.1725 | 0.11902 | -0.22186 | 0.020401 | 0.0025208 | 0.0078955 | -0.0030568 | 0.0026424 | -0.0035249 | -0.20317 | -0.0080685 | -0.0019802 | 0.00016019 | 0.0038943 | -0.0099484 | 0.073242 | 0.059509 | 0.036621 | 0.050354 | 0.18768 | 0.045776 | -0.12817 | 0.054932 | 0.068665 | -0.054932 | 0.11902 | 0.082397 | -0.073242 | -0.15564 | 122.2183 | 122.0444 | 0.068664 | 122.2321 | 122.2229 | 0.17853 | -0.045777 | 122.0993 | 122.0169 | 0 | 122.2275 | 122.1176 | 0.10071 | -0.036622 | 122.3602 | 122.2458 | 122.2092 | -0.24719 | 122.2916 | 122.2549 | 122.2412 | -0.27466
860.2656 | 122.4976 | -122.1634 | 0.14191 | -0.17609 | 0.019333 | 0.0035888 | 0.0057593 | -0.0047658 | -0.003339 | -0.0039521 | -0.10399 | -0.0084957 | -0.0047574 | -0.0026168 | -0.0027279 | -0.007385 | 0.13733 | 0.19684 | 0.16937 | 0.12817 | 0.14648 | 0.082397 | -0.068665 | 0.15106 | 0.27924 | 0.091553 | 0.09613 | 0.082397 | -0.018311 | -0.073242 | 122.2458 | 122.0947 | 0.004577 | 122.3602 | 122.2916 | 0.19684 | -0.004578 | 122.1451 | 122.0901 | -0.045777 | 122.3145 | 122.2549 | 0.16479 | -0.05951 | 122.3099 | 122.3007 | 122.3328 | -0.21057 | 122.2595 | 122.2458 | 122.4426 | -0.21515
861.9844 | 122.406 | -122.1909 | 0.17395 | 0.090942 | 0.018692 | 0.0016662 | 0.0012731 | -0.0047658 | 0.004565 | -0.0030975 | -0.0048066 | -0.0052915 | -0.0056118 | 0.0016556 | 0.0060305 | -0.0097348 | -0.045776 | -0.082397 | -0.07782 | -0.064087 | 0.086975 | -0.054932 | -0.20599 | -0.054932 | -0.12817 | -0.16479 | 0.068665 | 0.041199 | -0.1236 | -0.18768 | 122.1359 | 121.9849 | -0.086975 | 122.1085 | 122.1268 | 0.14191 | -0.21973 | 122.0673 | 122.0032 | -0.10528 | 122.1359 | 122.0261 | 0.022888 | -0.13275 | 122.2778 | 122.1451 | 122.113 | -0.37994 | 122.2595 | 122.2321 | 122.0627 | -0.36163
863.6719 | 122.438 | -122.2183 | 0.14191 | -0.069275 | 0.016556 | 0.002948 | 0.0025549 | -0.0039114 | 0.0022152 | -0.0033111 | -0.073471 | -0.0072141 | -0.0039028 | 0.00080099 | 0.0058169 | -0.0080258 | 0.050354 | 0.036621 | 0.009155 | 0.009155 | 0.11444 | -0.004578 | -0.16022 | 0.045776 | 0 | -0.091553 | 0.07782 | 0.059509 | -0.09613 | -0.15106 | 122.2137 | 122.0581 | -0.027466 | 122.2549 | 122.2275 | 0.16937 | -0.091553 | 122.1222 | 122.0673 | -0.064087 | 122.2641 | 122.1268 | 0.059509 | -0.082398 | 122.3328 | 122.2687 | 122.2275 | -0.30212 | 122.2961 | 122.2778 | 122.2183 | -0.29297
865.3594 | 122.3969 | -122.2229 | 0.17395 | -0.031128 | 0.018265 | 0.0027344 | 0.0040503 | -0.0028432 | 0.00093342 | -0.0035249 | 0.010452 | -0.0044369 | -0.0041164 | 0.0022964 | 0.0053897 | -0.0082394 | 0.009155 | -0.009155 | -0.041199 | -0.027466 | 0.10529 | -0.032043 | -0.16937 | -0.004578 | -0.07782 | -0.14648 | 0.059509 | 0.045776 | -0.11444 | -0.19684 | 122.1909 | 122.0535 | -0.068664 | 122.2137 | 122.1954 | 0.14191 | -0.16479 | 122.1085 | 122.0261 | -0.11444 | 122.2183 | 122.0764 | 0.050354 | -0.12817 | 122.3282 | 122.2321 | 122.1817 | -0.34332 | 122.2824 | 122.2687 | 122.1451 | -0.37079
867.0781 | 122.493 | -122.1954 | 0.11902 | -0.16083 | 0.017197 | 0.0018798 | 0.0061865 | -0.0030568 | -0.0063296 | -0.0033111 | -0.11162 | -0.0087093 | -0.0045438 | -0.00090781 | -0.0012327 | -0.0065304 | 0.10986 | 0.17395 | 0.14191 | 0.11902 | 0.16022 | 0.068665 | -0.073242 | 0.1236 | 0.27008 | 0.064087 | 0.10986 | 0.10529 | 0 | -0.068665 | 122.2641 | 122.1222 | 0.041198 | 122.3694 | 122.3145 | 0.19226 | -0.009156 | 122.1954 | 122.1268 | -0.009156 | 122.319 | 122.2595 | 0.13275 | -0.013733 | 122.3557 | 122.3053 | 122.3373 | -0.19226 | 122.3053 | 122.3007 | 122.4655 | -0.18768
868.7812 | 122.4197 | -122.2183 | 0.14648 | 0.14435 | 0.016129 | 0.002948 | 0.0040503 | -0.004125 | -0.0052616 | -0.0035249 | 0.13252 | -0.0093503 | -0.00069863 | -0.00090781 | 0.00090353 | -0.010376 | 0.004578 | 0.032043 | 0.036621 | -0.009155 | 0.054932 | -0.022888 | -0.17853 | 0.091553 | 0.10529 | 0.009155 | 0.059509 | 0.041199 | -0.054932 | -0.091553 | 122.1954 | 122.0398 | -0.091552 | 122.2504 | 122.2092 | 0.16937 | -0.14191 | 122.1634 | 122.1268 | -0.086975 | 122.3099 | 122.2275 | 0.10071 | -0.10529 | 122.2733 | 122.2229 | 122.2549 | -0.32501 | 122.2778 | 122.2595 | 122.3236 | -0.23804
870.4531 | 122.4106 | -122.2137 | 0.16479 | 0.12909 | 0.012497 | 0.0065796 | 0.0017005 | -0.0064748 | -0.0048344 | -0.0065155 | 0.14015 | -0.0087093 | -0.0062528 | 0.00016019 | 0.00068993 | -0.0080258 | 0.018311 | 0.045776 | 0.036621 | -0.004578 | 0.064087 | -0.036621 | -0.16022 | 0.11444 | 0.09613 | 0.009155 | 0.073242 | 0.054932 | -0.041199 | -0.10986 | 122.1771 | 122.0535 | -0.10071 | 122.2595 | 122.2092 | 0.15564 | -0.14648 | 122.1725 | 122.1039 | -0.091553 | 122.3282 | 122.2229 | 0.11902 | -0.10986 | 122.2778 | 122.2321 | 122.2504 | -0.32501 | 122.287 | 122.2687 | 122.3099 | -0.27466
872.125 | 122.5113 | -122.2092 | 0.13275 | -0.19135 | 0.019333 | 0.0023072 | 0.0081091 | -0.0045522 | -0.00034818 | -0.0067291 | -0.24132 | -0.0072141 | -0.0024076 | -5.3406e-05 | 0.0015445 | -0.0093076 | 0.082397 | 0.064087 | 0.050354 | 0.045776 | 0.21515 | 0.059509 | -0.10071 | 0.073242 | 0.14191 | -0.027466 | 0.19684 | 0.14191 | -0.041199 | -0.09613 | 122.2687 | 122.1085 | 0.082398 | 122.2733 | 122.2549 | 0.14648 | -0.050354 | 122.168 | 122.113 | 0.064087 | 122.2824 | 122.1817 | 0.068664 | 0.009156 | 122.4243 | 122.2916 | 122.2595 | -0.23346 | 122.406 | 122.3511 | 122.3511 | -0.22888
873.7969 | 122.4884 | -122.1909 | 0.14191 | 0.0070193 | 0.015274 | 0.0057252 | 0.0049047 | -0.0034842 | -0.0071842 | -0.0054475 | 0.071487 | -0.0097775 | -0.004971 | -0.0024032 | 0.0019717 | -0.006744 | 0.027466 | 0.045776 | 0.041199 | 0.045776 | 0.11902 | 0.032043 | -0.1236 | 0.09613 | 0.15564 | 0.013733 | 0.091553 | 0.068665 | -0.041199 | -0.11444 | 122.2229 | 122.0673 | -0.022888 | 122.2366 | 122.2366 | 0.16937 | -0.11444 | 122.1497 | 122.0764 | -0.050354 | 122.287 | 122.2046 | 0.12817 | -0.073242 | 122.3099 | 122.2183 | 122.2321 | -0.2655 | 122.2824 | 122.2595 | 122.3465 | -0.25635
875.4688 | 122.438 | -122.2137 | 0.15564 | 0.037537 | 0.014206 | 0.004657 | 0.00084592 | -0.0032706 | -0.0041934 | -0.0037385 | 0.086746 | -0.0061459 | -0.0043302 | -0.0013352 | 0.0041079 | -0.007385 | 0.054932 | 0.059509 | 0.041199 | 0.022888 | 0.11902 | 0.004578 | -0.12817 | 0.09613 | 0.11444 | -0.009155 | 0.086975 | 0.07782 | -0.032043 | -0.11444 | 122.2183 | 122.0856 | -0.036621 | 122.2733 | 122.2366 | 0.15106 | -0.10071 | 122.1817 | 122.0993 | -0.068665 | 122.3099 | 122.2046 | 0.10529 | -0.07782 | 122.3328 | 122.2687 | 122.2549 | -0.28381 | 122.3007 | 122.2916 | 122.3282 | -0.27008
877.1406 | 122.4884 | -122.1909 | 0.16479 | 0.14435 | 0.015061 | 0.0052978 | 0.0012731 | -0.0051932 | 0.0041378 | -0.0022431 | 0.03334 | -0.0065731 | -0.004971 | 0.00058739 | 0.0070987 | -0.01123 | -0.013733 | -0.11444 | -0.10529 | -0.07782 | 0.091553 | -0.07782 | -0.21057 | 0.018311 | -0.1236 | -0.13275 | 0.059509 | 0.032043 | -0.10986 | -0.16937 | 122.113 | 121.9803 | -0.073242 | 122.0764 | 122.113 | 0.13275 | -0.17853 | 122.081 | 122.0215 | -0.10529 | 122.2092 | 122.0581 | 0.036622 | -0.13275 | 122.2824 | 122.1771 | 122.0856 | -0.37537 | 122.2504 | 122.2229 | 122.0673 | -0.33417
878.8594 | 122.438 | -122.2092 | 0.15106 | 0.17487 | 0.015061 | 0.0035888 | 0.0023413 | -0.0039114 | 0.00050622 | -0.0016021 | 0.19356 | -0.0072141 | -0.0073208 | -0.00069421 | 0.0058169 | -0.008453 | 0.027466 | 0.018311 | 0.022888 | -0.013733 | 0.036621 | -0.068665 | -0.1831 | 0.10071 | 0.054932 | -0.027466 | -0.009155 | -0.018311 | -0.11902 | -0.17853 | 122.1405 | 122.0261 | -0.11444 | 122.2275 | 122.1954 | 0.16937 | -0.1236 | 122.0901 | 122.0306 | -0.16022 | 122.3099 | 122.1817 | 0.15106 | -0.16937 | 122.2458 | 122.2366 | 122.2321 | -0.33417 | 122.2 | 122.1909 | 122.2641 | -0.32959
880.5625 | 122.4701 | -122.2137 | 0.16022 | 0.098572 | 0.016556 | 0.0038024 | 0.0017005 | -0.004125 | 0.0032834 | -0.0013885 | 0.048599 | -0.0057187 | -0.006039 | 0.00016019 | 0.0038943 | -0.0082394 | -0.013733 | -0.09613 | -0.09613 | -0.086975 | 0.10071 | -0.050354 | -0.20599 | 0 | -0.10529 | -0.14648 | 0.07782 | 0.032043 | -0.10529 | -0.19226 | 122.1634 | 122.0078 | -0.059509 | 122.1176 | 122.1268 | 0.11902 | -0.17395 | 122.1085 | 122.0215 | -0.082397 | 122.2137 | 122.0673 | 0.045777 | -0.12817 | 122.3145 | 122.2 | 122.1176 | -0.36621 | 122.2916 | 122.2458 | 122.1085 | -0.35248
882.2344 | 122.4564 | -122.2275 | 0.17395 | 0.090942 | 0.021256 | 0.0052978 | 0.0040503 | -0.0049796 | 0.0024288 | -0.0030975 | 0.071487 | -0.0046505 | -0.0041164 | -0.00026701 | 0.0038943 | -0.0078122 | -0.045776 | -0.14648 | -0.10986 | -0.082397 | 0.086975 | -0.054932 | -0.21515 | -0.018311 | -0.14191 | -0.17395 | 0.054932 | 0.027466 | -0.12817 | -0.17853 | 122.1725 | 122.0123 | -0.086975 | 122.081 | 122.1451 | 0.13275 | -0.21973 | 122.0993 | 122.049 | -0.11902 | 122.2092 | 122.0535 | 0.004578 | -0.14648 | 122.3145 | 122.1817 | 122.1176 | -0.3891 | 122.2824 | 122.2549 | 122.0856 | -0.35248
883.9688 | 122.5662 | -122.2 | 0.11444 | -0.092163 | 0.015701 | 0.002948 | 0.0096045 | -0.004125 | -0.0054752 | -0.0050201 | -0.073471 | -0.010418 | -0.0026212 | -0.0021896 | -0.00037807 | -0.0078122 | 0.15564 | 0.16022 | 0.14191 | 0.11444 | 0.15564 | 0.064087 | -0.073242 | 0.19226 | 0.26093 | 0.10529 | 0.10071 | 0.091553 | -0.009155 | -0.050354 | 122.2641 | 122.1268 | 0.041199 | 122.3602 | 122.3145 | 0.18768 | 0.041199 | 122.1909 | 122.1497 | -0.013733 | 122.3923 | 122.3053 | 0.15564 | -0.022888 | 122.3557 | 122.3557 | 122.3419 | -0.18768 | 122.3007 | 122.2916 | 122.4609 | -0.16479
885.6406 | 122.5479 | -122.2 | 0.14191 | -0.16083 | 0.015915 | 0.0067932 | 0.0061865 | -0.0043386 | -0.0039798 | -0.0041657 | -0.12688 | -0.0087093 | -0.0043302 | -0.0021896 | 4.9132e-05 | -0.0095212 | 0.18768 | 0.1831 | 0.16479 | 0.13275 | 0.16022 | 0.086975 | -0.07782 | 0.17853 | 0.3067 | 0.10071 | 0.11902 | 0.10529 | 0.009155 | -0.068665 | 122.287 | 122.1222 | 0.01831 | 122.3831 | 122.3328 | 0.21057 | 0.045776 | 122.2092 | 122.1313 | -0.022888 | 122.3785 | 122.3007 | 0.16937 | -0.036621 | 122.3602 | 122.3877 | 122.3648 | -0.21973 | 122.319 | 122.3053 | 122.5067 | -0.21057
887.3281 | 122.5845 | -122.2046 | 0.13275 | -0.092163 | 0.014633 | 0.0033752 | 0.0042639 | -0.0045522 | -0.0029118 | -0.0033111 | -0.073471 | -0.0084957 | -0.0039028 | 0.001442 | 4.9132e-05 | -0.0071714 | 0.16022 | 0.13733 | 0.13733 | 0.10529 | 0.13275 | 0.059509 | -0.07782 | 0.1831 | 0.27008 | 0.09613 | 0.10071 | 0.09613 | -0.013733 | -0.082397 | 122.2641 | 122.1268 | 0 | 122.3419 | 122.3099 | 0.18311 | 0.027466 | 122.1909 | 122.1222 | -0.032043 | 122.3877 | 122.3007 | 0.17853 | -0.036621 | 122.3373 | 122.3648 | 122.3419 | -0.21057 | 122.3053 | 122.3007 | 122.4747 | -0.21515
889 | 122.438 | -122.2229 | 0.16479 | 0.12909 | 0.015274 | 0.0031616 | 0.0014867 | -0.0034842 | -0.00098918 | -0.0067291 | 0.086746 | -0.0072141 | -0.0088162 | 0.0010148 | 0.0030399 | -0.0086666 | 0.059509 | 0.018311 | 0.041199 | -0.013733 | 0.068665 | -0.041199 | -0.16479 | 0.09613 | 0.09613 | -0.013733 | 0.068665 | 0.041199 | -0.050354 | -0.10986 | 122.1817 | 122.0581 | -0.09613 | 122.2412 | 122.2092 | 0.15106 | -0.10529 | 122.1725 | 122.113 | -0.09613 | 122.319 | 122.2092 | 0.09613 | -0.1236 | 122.2916 | 122.2824 | 122.2641 | -0.32959 | 122.2916 | 122.2641 | 122.319 | -0.27466
890.6719 | 122.4655 | -122.2183 | 0.16937 | 0.083313 | 0.014633 | 0.0044434 | 0.0031957 | -0.0051932 | -0.0020572 | -0.0048065 | 0.102 | -0.0070003 | -0.0071072 | -0.0038986 | 0.0038943 | -0.0078122 | 0.068665 | 0.032043 | 0.045776 | 0.004578 | 0.059509 | -0.027466 | -0.15564 | 0.11444 | 0.09613 | -0.013733 | 0.059509 | 0.059509 | -0.054932 | -0.11902 | 122.1909 | 122.0627 | -0.10986 | 122.2504 | 122.2229 | 0.16022 | -0.10071 | 122.1634 | 122.0993 | -0.10986 | 122.3328 | 122.2046 | 0.10529 | -0.10986 | 122.2778 | 122.287 | 122.2641 | -0.32501 | 122.2778 | 122.2778 | 122.3145 | -0.28839
892.4062 | 122.5296 | -122.2046 | 0.15106 | -0.17609 | 0.016983 | 0.0033752 | 0.0066137 | -0.0060476 | -0.00098918 | -0.0022431 | -0.16502 | -0.0087093 | -0.0036892 | -0.0017624 | 0.0032535 | -0.012085 | 0.19684 | 0.15564 | 0.15564 | 0.11444 | 0.15106 | 0.054932 | -0.082397 | 0.14648 | 0.26093 | 0.073242 | 0.10986 | 0.10071 | -0.004578 | -0.059509 | 122.2595 | 122.1222 | 0 | 122.3602 | 122.319 | 0.19684 | 0.045776 | 122.2 | 122.1451 | -0.041199 | 122.3511 | 122.2778 | 0.13275 | -0.050354 | 122.3557 | 122.4014 | 122.3602 | -0.23346 | 122.3145 | 122.3053 | 122.4655 | -0.21057
894.0938 | 122.5891 | -122.2 | 0.15106 | -0.22186 | 0.019547 | 0.0023072 | 0.0055457 | -0.0036978 | 0.0011472 | -0.0054475 | -0.24895 | -0.0059323 | -0.0017666 | -0.00069421 | 0.0026125 | -0.011444 | 0.10986 | 0.036621 | 0.009155 | 0.059509 | 0.2243 | 0.050354 | -0.09613 | 0.064087 | 0.068665 | -0.073242 | 0.14191 | 0.12817 | -0.045776 | -0.1236 | 122.2504 | 122.1039 | 0.073242 | 122.2366 | 122.2595 | 0.15564 | -0.041199 | 122.1542 | 122.0764 | -0.009155 | 122.2641 | 122.1268 | 0.050354 | -0.022888 | 122.4243 | 122.3099 | 122.2092 | -0.24719 | 122.3419 | 122.3282 | 122.2687 | -0.27466
895.7812 | 122.4884 | -122.2229 | 0.17853 | -0.031128 | 0.020401 | 0.001239 | 0.0040503 | -0.0043386 | 0.0049924 | -0.0026703 | -0.17265 | -0.0065731 | -0.0028348 | 0.00251 | 0.0053897 | -0.011871 | 0.086975 | 0.018311 | 0.009155 | 0.013733 | 0.1236 | -0.009155 | -0.16022 | 0.064087 | 0.009155 | -0.086975 | 0.082397 | 0.059509 | -0.082397 | -0.16022 | 122.2137 | 122.0627 | -0.054932 | 122.2412 | 122.2366 | 0.17395 | -0.091553 | 122.1405 | 122.0627 | -0.096131 | 122.287 | 122.1359 | 0.073242 | -0.11902 | 122.3465 | 122.3099 | 122.2321 | -0.33874 | 122.3053 | 122.2824 | 122.2321 | -0.33874
897.4844 | 122.5845 | -122.1725 | 0.16022 | -0.16083 | 0.019333 | 0.0040162 | 0.0059729 | -0.0062612 | 0.003497 | -0.0028839 | -0.24895 | -0.0061459 | -0.0030484 | 0.0016556 | 0.0026125 | -0.0082394 | 0.082397 | 0.045776 | 0.013733 | 0.050354 | 0.19684 | 0.022888 | -0.1236 | 0.07782 | 0.073242 | -0.059509 | 0.091553 | 0.059509 | -0.086975 | -0.14191 | 122.1954 | 122.0489 | 0.036621 | 122.2183 | 122.2229 | 0.17395 | -0.07782 | 122.0856 | 122.0306 | -0.068664 | 122.2504 | 122.113 | 0.082398 | -0.10071 | 122.3694 | 122.2549 | 122.1863 | -0.28381 | 122.2641 | 122.2321 | 122.2458 | -0.30212
899.2031 | 122.6212 | -122.1771 | 0.16937 | -0.1532 | 0.017624 | 0.0023072 | 0.0061865 | -0.0043386 | 0.0026424 | -0.0041657 | -0.25658 | -0.0063595 | -0.0041164 | 0.0037918 | 0.0017581 | -0.0088804 | 0.045776 | 0.050354 | 0.004578 | 0.041199 | 0.19684 | 0.027466 | -0.10071 | 0.050354 | 0.10071 | -0.045776 | 0.13733 | 0.1236 | -0.064087 | -0.10529 | 122.2046 | 122.0764 | 0.027465 | 122.2275 | 122.2183 | 0.14191 | -0.1236 | 122.113 | 122.0718 | -0.032044 | 122.2275 | 122.1313 | 0.05951 | -0.045777 | 122.374 | 122.2229 | 122.1817 | -0.27008 | 122.3145 | 122.3007 | 122.2778 | -0.27466
900.8906 | 122.5708 | -122.1909 | 0.16022 | -0.2066 | 0.019119 | 0.002948 | 0.0091773 | -0.0030568 | -0.0031254 | -0.0026703 | -0.23369 | -0.0055051 | -0.0021938 | 0.0018692 | 0.00026273 | -0.0080258 | 0.050354 | 0.064087 | 0.041199 | 0.059509 | 0.2243 | 0.059509 | -0.086975 | 0.064087 | 0.12817 | -0.018311 | 0.1831 | 0.1236 | -0.027466 | -0.09613 | 122.2504 | 122.1039 | 0.064087 | 122.2549 | 122.2504 | 0.14648 | -0.10986 | 122.1634 | 122.0947 | 0.022888 | 122.2549 | 122.1725 | 0.077819 | -0.036621 | 122.4152 | 122.2412 | 122.2321 | -0.24719 | 122.374 | 122.3145 | 122.319 | -0.25635
902.625 | 122.58 | -122.1954 | 0.16937 | -0.061646 | 0.018906 | 0.0040162 | 0.0061865 | -0.002416 | -0.00013458 | -0.0013885 | -0.18028 | -0.0067867 | -0.003262 | -0.0013352 | 0.0043215 | -0.0086666 | 0.050354 | 0.059509 | 0.004578 | 0.022888 | 0.15106 | 0.004578 | -0.14648 | 0.059509 | 0.041199 | -0.064087 | 0.086975 | 0.054932 | -0.068665 | -0.15564 | 122.2 | 122.049 | -0.018311 | 122.2549 | 122.2183 | 0.16937 | -0.11902 | 122.1268 | 122.0398 | -0.082398 | 122.2549 | 122.1313 | 0.091553 | -0.11444 | 122.3465 | 122.2458 | 122.2 | -0.31586 | 122.2824 | 122.2504 | 122.2366 | -0.32501
904.3281 | 122.4976 | -122.2046 | 0.18768 | 0.14435 | 0.017838 | 0.0035888 | 0.0042639 | -0.0032706 | -0.00098918 | -0.0016021 | 0.14778 | -0.0080685 | -0.004971 | -0.0013352 | 0.0026125 | -0.0075986 | -0.059509 | -0.054932 | -0.09613 | -0.073242 | 0.086975 | -0.064087 | -0.21973 | 0.009155 | -0.091553 | -0.10986 | 0.068665 | 0.018311 | -0.1236 | -0.17853 | 122.1405 | 121.9849 | -0.10071 | 122.1497 | 122.1313 | 0.14649 | -0.24719 | 122.081 | 122.0261 | -0.11902 | 122.2137 | 122.0947 | 0.068665 | -0.16937 | 122.2916 | 122.1451 | 122.1085 | -0.40741 | 122.2733 | 122.2229 | 122.113 | -0.36621
906.0312 | 122.5433 | -122.1954 | 0.15564 | 0.029907 | 0.015488 | 0.0023072 | 0.0044775 | -0.0047658 | -0.0076114 | -0.0048065 | 0.12489 | -0.0084957 | -0.0073208 | 0.00037379 | 0.00026273 | -0.007385 | -0.009155 | 0.045776 | 0.045776 | 0.036621 | 0.1236 | 0.027466 | -0.11902 | 0.068665 | 0.16479 | 0.018311 | 0.09613 | 0.064087 | -0.036621 | -0.09613 | 122.2229 | 122.0764 | -0.032044 | 122.2412 | 122.2321 | 0.15564 | -0.16479 | 122.1588 | 122.0993 | -0.05951 | 122.2641 | 122.2137 | 0.11444 | -0.091553 | 122.319 | 122.1863 | 122.2412 | -0.27466 | 122.2916 | 122.2595 | 122.3602 | -0.25177
907.7344 | 122.5845 | -122.1817 | 0.16937 | -0.099793 | 0.017838 | 0.0040162 | 0.0053321 | -0.005834 | -0.0039798 | -0.0045929 | -0.13451 | -0.0082821 | -0.0043302 | -0.0015488 | 0.0015445 | -0.0086666 | 0.16479 | 0.20142 | 0.1831 | 0.13275 | 0.15106 | 0.073242 | -0.073242 | 0.19226 | 0.29755 | 0.11444 | 0.11444 | 0.086975 | 0.013733 | -0.041199 | 122.2549 | 122.1085 | -0.018311 | 122.3831 | 122.3145 | 0.20599 | -0.004578 | 122.1954 | 122.1405 | -0.054932 | 122.374 | 122.2961 | 0.15564 | -0.082398 | 122.3328 | 122.3465 | 122.3648 | -0.24261 | 122.2961 | 122.2687 | 122.4792 | -0.21057
909.4688 | 122.5159 | -122.2504 | 0.1831 | 0.090942 | 0.018478 | 0.001239 | 0.0042639 | -0.0047658 | 0.001788 | -0.0041657 | 0.13252 | -0.0080685 | -0.0043302 | 0.0016556 | 0.0047489 | -0.0095212 | -0.032043 | -0.07782 | -0.09613 | -0.082397 | 0.1236 | -0.064087 | -0.20142 | 0.004578 | -0.09613 | -0.11902 | 0.068665 | 0.036621 | -0.13275 | -0.1831 | 122.1863 | 122.049 | -0.059509 | 122.1725 | 122.168 | 0.11902 | -0.21515 | 122.1176 | 122.0673 | -0.11444 | 122.2549 | 122.1313 | 0.064086 | -0.14648 | 122.374 | 122.2183 | 122.1542 | -0.38452 | 122.319 | 122.287 | 122.1542 | -0.36621
911.1719 | 122.5479 | -122.2137 | 0.16479 | -0.25238 | 0.01741 | 0.0035888 | 0.0074683 | -0.0039114 | -0.002698 | -0.0035249 | -0.21843 | -0.0099911 | -0.0030484 | -0.00069421 | 0.00090353 | -0.008453 | 0.068665 | 0.064087 | 0.041199 | 0.050354 | 0.21057 | 0.086975 | -0.091553 | 0.082397 | 0.13733 | -0.027466 | 0.14191 | 0.15564 | -0.041199 | -0.11444 | 122.3007 | 122.1222 | 0.045776 | 122.2778 | 122.2641 | 0.14191 | -0.09613 | 122.1725 | 122.0993 | -0.022888 | 122.2961 | 122.1863 | 0.086975 | -0.009155 | 122.4243 | 122.2824 | 122.2549 | -0.25635 | 122.3557 | 122.3694 | 122.3511 | -0.27924
912.8594 | 122.5891 | -122.1863 | 0.15564 | -0.13031 | 0.013992 | 0.0033752 | 0.0068273 | -0.005834 | -0.0052616 | -0.0058747 | 0.0028229 | -0.0078549 | -0.0056118 | 0.00016019 | -0.00059167 | -0.0088804 | 0.15106 | 0.19226 | 0.15564 | 0.10071 | 0.17853 | 0.064087 | -0.068665 | 0.20599 | 0.28381 | 0.11902 | 0.09613 | 0.07782 | -0.013733 | -0.073242 | 122.2504 | 122.1176 | 0.022888 | 122.3785 | 122.287 | 0.16937 | -0.004578 | 122.1725 | 122.113 | -0.05951 | 122.3923 | 122.3053 | 0.19226 | -0.07782 | 122.3648 | 122.3373 | 122.3419 | -0.22431 | 122.2824 | 122.2641 | 122.4701 | -0.22888
914.5312 | 122.5937 | -122.2137 | 0.15564 | -0.13794 | 0.017624 | 0.0023072 | 0.0051183 | -0.004125 | -0.003339 | -0.0054475 | -0.073471 | -0.010205 | -0.0041164 | -5.3406e-05 | 0.0013309 | -0.0095212 | 0.13275 | 0.18768 | 0.14191 | 0.1236 | 0.16937 | 0.07782 | -0.086975 | 0.20142 | 0.29755 | 0.13275 | 0.10071 | 0.068665 | -0.004578 | -0.068665 | 122.2916 | 122.1268 | 0.013733 | 122.4014 | 122.3373 | 0.21057 | -0.022889 | 122.2092 | 122.1451 | -0.054932 | 122.4152 | 122.3465 | 0.20142 | -0.086975 | 122.3831 | 122.3465 | 122.3557 | -0.24261 | 122.3145 | 122.2824 | 122.5113 | -0.22431
916.2031 | 122.5296 | -122.2458 | 0.17395 | 0.0070193 | 0.015915 | 0.006366 | 0.0029821 | -0.0056204 | -0.004407 | -0.0054475 | 0.025711 | -0.0093503 | -0.0036892 | -0.0011216 | 0.0028263 | -0.010589 | 0.027466 | 0.050354 | 0.041199 | 0.032043 | 0.12817 | 0.009155 | -0.11902 | 0.10071 | 0.14191 | 0.009155 | 0.091553 | 0.064087 | -0.045776 | -0.10986 | 122.2549 | 122.1268 | -0.045776 | 122.2961 | 122.2778 | 0.15106 | -0.14648 | 122.2 | 122.1359 | -0.082397 | 122.3465 | 122.2549 | 0.11902 | -0.10986 | 122.374 | 122.2733 | 122.287 | -0.29297 | 122.3373 | 122.3099 | 122.3877 | -0.28381
917.875 | 122.4655 | -122.2641 | 0.17853 | 0.15961 | 0.018265 | 0.0042298 | 0.0044775 | -0.0034842 | 0.00071982 | -0.0077973 | 0.12489 | -0.0084957 | -0.0062528 | -0.00069421 | 0.0028263 | -0.010162 | 0.050354 | 0.027466 | 0.032043 | -0.004578 | 0.004578 | -0.068665 | -0.21057 | 0.10071 | 0.050354 | -0.013733 | 0.018311 | -0.004578 | -0.10071 | -0.15106 | 122.1954 | 122.0535 | -0.17395 | 122.2916 | 122.2595 | 0.20599 | -0.12817 | 122.1634 | 122.113 | -0.16022 | 122.3648 | 122.2504 | 0.13733 | -0.18311 | 122.2687 | 122.3145 | 122.2961 | -0.3891 | 122.2824 | 122.2595 | 122.3145 | -0.32959
919.5469 | 122.4747 | -122.2504 | 0.20599 | 0.15961 | 0.015488 | 0.0020936 | -0.00064948 | -0.0030568 | 0.00093342 | -0.00096127 | 0.12489 | -0.0072141 | -0.0071072 | -0.0028306 | 0.0049625 | -0.0095212 | 0.032043 | 0.041199 | 0.032043 | -0.004578 | 0.032043 | -0.045776 | -0.17395 | 0.11902 | 0.082397 | 0 | 0.036621 | 0.009155 | -0.09613 | -0.16479 | 122.2046 | 122.0764 | -0.17395 | 122.2916 | 122.2458 | 0.16937 | -0.17395 | 122.1542 | 122.0856 | -0.16937 | 122.3694 | 122.2504 | 0.16479 | -0.19684 | 122.2824 | 122.2824 | 122.2824 | -0.37994 | 122.287 | 122.2595 | 122.3328 | -0.37079
921.2188 | 122.5204 | -122.2458 | 0.17853 | 0.11383 | 0.018906 | 0.0035888 | 0.0012731 | -0.005834 | 0.001788 | -0.0045929 | 0.086746 | -0.0065731 | -0.0056118 | 0.0012284 | 0.0075259 | -0.01123 | -0.022888 | -0.07782 | -0.086975 | -0.07782 | 0.10071 | -0.050354 | -0.19684 | 0.013733 | -0.10529 | -0.13275 | 0.045776 | 0.050354 | -0.11902 | -0.17853 | 122.1954 | 122.049 | -0.07782 | 122.168 | 122.168 | 0.11902 | -0.20142 | 122.1268 | 122.0673 | -0.13275 | 122.2595 | 122.113 | 0.045777 | -0.12817 | 122.3465 | 122.2229 | 122.1588 | -0.37537 | 122.2916 | 122.2961 | 122.1405 | -0.35706
922.9375 | 122.5754 | -122.2275 | 0.17853 | -0.099793 | 0.019119 | 0.00081179 | 0.0042639 | -0.0047658 | 0.0022152 | -0.0028839 | -0.14977 | -0.0070003 | -0.0026212 | -5.3406e-05 | 0.0036807 | -0.011017 | 0.086975 | 0.045776 | 0.009155 | 0.027466 | 0.15106 | -0.004578 | -0.14191 | 0.082397 | 0.036621 | -0.068665 | 0.068665 | 0.064087 | -0.10529 | -0.16022 | 122.2229 | 122.0856 | -0.027466 | 122.2733 | 122.2549 | 0.16937 | -0.091553 | 122.1222 | 122.0673 | -0.10986 | 122.3099 | 122.1588 | 0.091552 | -0.11444 | 122.3785 | 122.3145 | 122.2366 | -0.32044 | 122.2961 | 122.2916 | 122.2641 | -0.33874
924.6094 | 122.5571 | -122.2458 | 0.16022 | -0.084534 | 0.019119 | 0.0014526 | 0.0059729 | -0.0032706 | 0.0013608 | -0.0022431 | -0.11162 | -0.0042233 | -0.0071072 | 0.00016019 | 0.0066715 | -0.008453 | 0.068665 | 0.050354 | 0.018311 | 0.009155 | 0.14191 | -0.004578 | -0.16022 | 0.086975 | 0.022888 | -0.068665 | 0.07782 | 0.045776 | -0.09613 | -0.14191 | 122.2412 | 122.0856 | -0.01831 | 122.2961 | 122.2549 | 0.16937 | -0.091552 | 122.1497 | 122.1039 | -0.082397 | 122.3328 | 122.1771 | 0.073242 | -0.11444 | 122.3877 | 122.3145 | 122.2641 | -0.32043 | 122.3236 | 122.2916 | 122.2687 | -0.30212
926.2812 | 122.6532 | -122.2092 | 0.17395 | -0.16083 | 0.018265 | 0.0025208 | 0.0034093 | -0.0049796 | 0.00050622 | -0.0020295 | -0.21843 | -0.0063595 | -0.0028348 | -0.0015488 | 0.0032535 | -0.0088804 | 0.045776 | 0.050354 | -0.004578 | 0.050354 | 0.18768 | 0.032043 | -0.10529 | 0.050354 | 0.082397 | -0.036621 | 0.15564 | 0.11902 | -0.059509 | -0.11444 | 122.2412 | 122.1039 | 0.013733 | 122.2595 | 122.2595 | 0.15564 | -0.12817 | 122.1497 | 122.0947 | -0.01831 | 122.2595 | 122.1725 | 0.07782 | -0.054931 | 122.3969 | 122.2549 | 122.2046 | -0.27924 | 122.3648 | 122.3282 | 122.2916 | -0.28839
927.9531 | 122.6395 | -122.2046 | 0.17395 | -0.17609 | 0.017197 | 0.0042298 | 0.0074683 | -0.0039114 | -0.00013458 | -0.0033111 | -0.23369 | -0.0082821 | -0.003262 | -0.00090781 | 0.0021853 | -0.0088804 | 0.032043 | 0.050354 | 0.018311 | 0.059509 | 0.20599 | 0.027466 | -0.12817 | 0.045776 | 0.082397 | -0.036621 | 0.14648 | 0.12817 | -0.050354 | -0.13275 | 122.2321 | 122.0764 | 0.032044 | 122.2549 | 122.2641 | 0.18768 | -0.14191 | 122.1542 | 122.0718 | -0.027466 | 122.2504 | 122.168 | 0.09613 | -0.045776 | 122.4106 | 122.2366 | 122.2229 | -0.30212 | 122.3511 | 122.3328 | 122.287 | -0.3067
929.625 | 122.6166 | -122.2275 | 0.17395 | -0.24475 | 0.018906 | 0.0059388 | 0.0066137 | -0.0036978 | -0.0018436 | -0.0037385 | -0.23369 | -0.0072141 | -0.0030484 | 0.0012284 | -0.00016447 | -0.0082394 | 0.059509 | 0.059509 | 0.041199 | 0.064087 | 0.23346 | 0.068665 | -0.091553 | 0.032043 | 0.09613 | -0.045776 | 0.16022 | 0.15106 | -0.022888 | -0.10986 | 122.2961 | 122.1359 | 0.059509 | 122.287 | 122.2916 | 0.15564 | -0.11444 | 122.2046 | 122.1176 | -0.013733 | 122.2595 | 122.1817 | 0.064087 | -0.022888 | 122.4609 | 122.287 | 122.2687 | -0.2655 | 122.3877 | 122.3785 | 122.3236 | -0.28381
931.2969 | 122.5845 | -122.2549 | 0.16479 | -0.2066 | 0.017624 | 0.0033752 | 0.0044775 | -0.0069022 | -0.0048344 | -0.0054475 | -0.073471 | -0.0089229 | -0.0039028 | -0.0015488 | 0.00026273 | -0.0078122 | 0.13733 | 0.20142 | 0.17853 | 0.15106 | 0.16479 | 0.07782 | -0.059509 | 0.16022 | 0.29297 | 0.10986 | 0.13275 | 0.086975 | 0.018311 | -0.068665 | 122.3328 | 122.1954 | 0 | 122.4564 | 122.406 | 0.21057 | -0.027466 | 122.2733 | 122.1863 | -0.032044 | 122.4152 | 122.3648 | 0.17853 | -0.07782 | 122.4197 | 122.3923 | 122.4335 | -0.2243 | 122.3877 | 122.3419 | 122.5479 | -0.23346
933.0156 | 122.6349 | -122.2092 | 0.17853 | -0.14557 | 0.017838 | 0.0027344 | 0.0044775 | -0.0054068 | 0.00093342 | -0.0067291 | -0.22606 | -0.0074277 | -0.0039028 | -0.0011216 | 0.0034671 | -0.0095212 | 0.059509 | 0.050354 | 0.013733 | 0.068665 | 0.20599 | 0.032043 | -0.10986 | 0.032043 | 0.073242 | -0.059509 | 0.13275 | 0.086975 | -0.073242 | -0.10986 | 122.2412 | 122.0993 | 0.027466 | 122.2595 | 122.2778 | 0.17853 | -0.11902 | 122.1359 | 122.0993 | -0.045777 | 122.2412 | 122.1497 | 0.050354 | -0.091553 | 122.4152 | 122.2687 | 122.2229 | -0.28839 | 122.3419 | 122.2961 | 122.2824 | -0.28839
934.6875 | 122.6166 | -122.2 | 0.16937 | -0.13031 | 0.017838 | 0.0023072 | 0.0051183 | -0.00049345 | 0.0020016 | -0.0054475 | -0.15739 | -0.0050777 | -0.0011258 | 0.0027236 | 0.0038943 | -0.009094 | 0.054932 | 0.045776 | 0.018311 | 0.032043 | 0.16937 | -0.018311 | -0.16022 | 0.050354 | 0.050354 | -0.054932 | 0.082397 | 0.059509 | -0.091553 | -0.16022 | 122.1817 | 122.0398 | 0 | 122.2458 | 122.2321 | 0.19226 | -0.11444 | 122.1085 | 122.0398 | -0.086976 | 122.2504 | 122.1451 | 0.10528 | -0.10986 | 122.3694 | 122.2549 | 122.2183 | -0.32959 | 122.2824 | 122.2595 | 122.2504 | -0.32959
936.3594 | 122.644 | -122.2275 | 0.16937 | -0.1532 | 0.021896 | 0.0035888 | 0.0061865 | -0.0047658 | 0.0013608 | -0.0028839 | -0.23369 | -0.0065731 | -0.0026212 | 0.00080099 | 0.00047633 | -0.008453 | 0.032043 | 0.050354 | 0.027466 | 0.045776 | 0.19684 | 0.018311 | -0.10071 | 0.045776 | 0.064087 | -0.054932 | 0.13733 | 0.10529 | -0.064087 | -0.1236 | 122.2458 | 122.1268 | 0.027465 | 122.2778 | 122.2733 | 0.14648 | -0.13733 | 122.1634 | 122.1039 | -0.032044 | 122.2733 | 122.1725 | 0.068664 | -0.064087 | 122.4243 | 122.2595 | 122.2549 | -0.27008 | 122.3648 | 122.3328 | 122.2916 | -0.29297
938.0469 | 122.5754 | -122.2321 | 0.16937 | -0.17609 | 0.019119 | 0.0042298 | 0.0066137 | -0.0047658 | -0.0063296 | -0.0022431 | -0.096359 | -0.0093503 | -0.0039028 | 0.00058739 | -0.00016447 | -0.007385 | 0.10529 | 0.18768 | 0.16022 | 0.11902 | 0.17395 | 0.082397 | -0.054932 | 0.13733 | 0.27466 | 0.07782 | 0.10529 | 0.086975 | -0.013733 | -0.082397 | 122.3145 | 122.1771 | 0.004577 | 122.4197 | 122.3511 | 0.17395 | -0.064087 | 122.2183 | 122.1497 | -0.064087 | 122.3694 | 122.3099 | 0.16022 | -0.082398 | 122.406 | 122.3373 | 122.3923 | -0.22431 | 122.3373 | 122.319 | 122.5067 | -0.25177
939.7188 | 122.6074 | -122.2092 | 0.14191 | -0.099793 | 0.017197 | 0.0055114 | 0.0055457 | -0.0026296 | -0.006116 | -0.0069427 | -0.081101 | -0.010846 | -0.0053982 | -0.00090781 | 0.00068993 | -0.0069578 | 0.14648 | 0.19684 | 0.16022 | 0.13275 | 0.16479 | 0.068665 | -0.068665 | 0.16937 | 0.30212 | 0.11444 | 0.1236 | 0.09613 | -0.004578 | -0.064087 | 122.2778 | 122.1405 | 0.022888 | 122.406 | 122.3419 | 0.20142 | 0.004577 | 122.2046 | 122.1451 | -0.018311 | 122.3785 | 122.3236 | 0.17853 | -0.045777 | 122.374 | 122.3557 | 122.3694 | -0.21057 | 122.3328 | 122.3053 | 122.5113 | -0.20599
941.4062 | 122.5021 | -122.2778 | 0.21057 | 0.029907 | 0.016556 | 0.0050842 | 0.0025549 | -0.0079702 | -0.0035526 | -0.0056611 | 0.086746 | -0.010205 | -0.0028348 | 0.0012284 | 0.0021853 | -0.0078122 | 0.041199 | 0.041199 | 0.022888 | 0.004578 | 0.11902 | 0 | -0.13733 | 0.086975 | 0.10986 | 0.004578 | 0.082397 | 0.059509 | -0.059509 | -0.12817 | 122.2778 | 122.1405 | -0.091552 | 122.319 | 122.2824 | 0.14191 | -0.16937 | 122.2183 | 122.1497 | -0.12817 | 122.3648 | 122.2824 | 0.13275 | -0.15106 | 122.3969 | 122.319 | 122.3007 | -0.3479 | 122.3602 | 122.3373 | 122.3877 | -0.33875
943.0781 | 122.5479 | -122.2458 | 0.20599 | 0.098572 | 0.018051 | 0.0016662 | 0.0034093 | -0.0047658 | 0.0030698 | -0.0018159 | 0.13252 | -0.0059323 | -0.006039 | 0.00058739 | 0.0073123 | -0.0097348 | -0.027466 | -0.086975 | -0.09613 | -0.07782 | 0.09613 | -0.091553 | -0.21515 | 0.022888 | -0.086975 | -0.11444 | 0.050354 | 0.018311 | -0.11902 | -0.17853 | 122.1542 | 122.0306 | -0.10986 | 122.1588 | 122.168 | 0.13733 | -0.23346 | 122.1268 | 122.0673 | -0.15564 | 122.2687 | 122.1313 | 0.064087 | -0.18768 | 122.3419 | 122.2183 | 122.1497 | -0.42114 | 122.2961 | 122.2641 | 122.1588 | -0.38452
944.75 | 122.5204 | -122.2458 | 0.18768 | 0.037537 | 0.013138 | 0.0035888 | 0.0014867 | -0.004125 | -0.005048 | -0.0043793 | 0.086746 | -0.0084957 | -0.0062528 | -5.3406e-05 | 0.0036807 | -0.0071714 | 0.045776 | 0.036621 | 0.041199 | 0.036621 | 0.10071 | 0.022888 | -0.13275 | 0.068665 | 0.12817 | -0.013733 | 0.09613 | 0.082397 | -0.050354 | -0.10986 | 122.2687 | 122.113 | -0.086975 | 122.2824 | 122.2824 | 0.16937 | -0.14191 | 122.1954 | 122.1359 | -0.091553 | 122.3145 | 122.2321 | 0.09613 | -0.10529 | 122.3465 | 122.2916 | 122.287 | -0.32043 | 122.3419 | 122.3282 | 122.374 | -0.29755
946.4844 | 122.5754 | -122.2549 | 0.19684 | -0.099793 | 0.018692 | 0.0018798 | 0.0029821 | -0.0030568 | 0.0024288 | -0.0033111 | -0.17265 | -0.0050777 | -0.0043302 | -0.00069421 | 0.0049625 | -0.0097348 | 0.086975 | 0.027466 | 0.004578 | 0.022888 | 0.14648 | -0.022888 | -0.14648 | 0.054932 | 0.004578 | -0.073242 | 0.082397 | 0.054932 | -0.09613 | -0.16937 | 122.2321 | 122.1085 | -0.050354 | 122.2824 | 122.2778 | 0.16937 | -0.10986 | 122.1588 | 122.0856 | -0.11444 | 122.3099 | 122.1817 | 0.096131 | -0.14191 | 122.4014 | 122.3419 | 122.2595 | -0.34332 | 122.3373 | 122.3099 | 122.2595 | -0.36621
948.1719 | 122.5479 | -122.2549 | 0.21057 | 0.11383 | 0.019547 | 0.0052978 | 0.0044775 | -0.0036978 | 0.0020016 | -0.0016021 | 0.063858 | -0.0078549 | -0.004971 | -0.00090781 | 0.0036807 | -0.008453 | -0.036621 | -0.10529 | -0.12817 | -0.086975 | 0.086975 | -0.073242 | -0.21973 | -0.018311 | -0.13275 | -0.16022 | 0.068665 | 0.032043 | -0.13733 | -0.19226 | 122.1817 | 122.0352 | -0.1236 | 122.1497 | 122.168 | 0.13275 | -0.24719 | 122.1176 | 122.0627 | -0.14191 | 122.2366 | 122.0947 | 0.032044 | -0.17853 | 122.3419 | 122.2183 | 122.1268 | -0.4303 | 122.3236 | 122.287 | 122.1222 | -0.40283
949.875 | 122.6028 | -122.2458 | 0.17853 | -0.099793 | 0.020828 | 0.0016662 | 0.0083227 | -0.0073294 | 0.00029262 | -0.0022431 | -0.11162 | -0.0089229 | -0.0019802 | 0.0018692 | 0.0043215 | -0.011017 | 0.068665 | 0.022888 | 0.027466 | 0.022888 | 0.14191 | 0.009155 | -0.16022 | 0.050354 | 0.027466 | -0.059509 | 0.068665 | 0.059509 | -0.082397 | -0.15106 | 122.2549 | 122.0856 | -0.036621 | 122.2687 | 122.2687 | 0.1831 | -0.10986 | 122.1634 | 122.0947 | -0.10986 | 122.2961 | 122.1863 | 0.091553 | -0.11902 | 122.3877 | 122.3145 | 122.2733 | -0.33874 | 122.3145 | 122.3053 | 122.2733 | -0.32959
951.5625 | 122.5845 | -122.2549 | 0.17395 | -0.26001 | 0.015701 | 0.0050842 | 0.0072547 | -0.0030568 | -0.004407 | -0.0052337 | -0.18791 | -0.0076413 | -0.0024076 | -0.0017624 | -0.00080527 | -0.010589 | 0.11444 | 0.16022 | 0.13733 | 0.11902 | 0.1831 | 0.059509 | -0.059509 | 0.07782 | 0.18768 | 0.013733 | 0.16479 | 0.1236 | -0.022888 | -0.082397 | 122.3145 | 122.1954 | 0.009155 | 122.4152 | 122.374 | 0.17853 | -0.059509 | 122.2321 | 122.1725 | -0.009155 | 122.3328 | 122.2687 | 0.09613 | -0.050354 | 122.438 | 122.3694 | 122.3923 | -0.23346 | 122.4197 | 122.3785 | 122.4426 | -0.25635
953.25 | 122.6578 | -122.2412 | 0.16022 | -0.16846 | 0.019547 | 0.00081179 | 0.0083227 | -0.0043386 | 0.0015744 | -0.0026703 | -0.2108 | -0.0089229 | -0.0047574 | 0.00080099 | 0.0041079 | -0.0086666 | 0.068665 | 0.059509 | 0.018311 | 0.064087 | 0.19684 | 0.022888 | -0.10986 | 0.036621 | 0.059509 | -0.050354 | 0.11902 | 0.091553 | -0.07782 | -0.13275 | 122.2641 | 122.1313 | 0.036621 | 122.3007 | 122.3053 | 0.17395 | -0.091552 | 122.1634 | 122.1085 | -0.041198 | 122.2778 | 122.1909 | 0.082397 | -0.068664 | 122.438 | 122.3099 | 122.2595 | -0.27008 | 122.3602 | 122.3328 | 122.3007 | -0.29297
954.9844 | 122.6578 | -122.2458 | 0.15564 | -0.16846 | 0.017838 | 0.0052978 | 0.0070409 | -0.0043386 | -0.00098918 | -0.0028839 | -0.23369 | -0.0089229 | -0.0019802 | -0.0011216 | 0.0019717 | -0.0097348 | 0.050354 | 0.032043 | -0.009155 | 0.054932 | 0.20599 | 0.027466 | -0.11902 | 0.059509 | 0.086975 | -0.041199 | 0.1236 | 0.11902 | -0.073242 | -0.13275 | 122.2733 | 122.1268 | 0.050354 | 122.2778 | 122.3007 | 0.17395 | -0.10529 | 122.1725 | 122.113 | -0.032044 | 122.3053 | 122.2046 | 0.091552 | -0.036621 | 122.4518 | 122.2961 | 122.2366 | -0.27466 | 122.3694 | 122.3648 | 122.3328 | -0.28839
956.6562 | 122.612 | -122.2641 | 0.17395 | -0.22186 | 0.019547 | 0.0038024 | 0.0072547 | -0.0056204 | -0.0024844 | -0.0060883 | -0.18028 | -0.0072141 | -0.00069863 | -0.0021896 | 0.00047633 | -0.009094 | 0.041199 | 0.064087 | 0.045776 | 0.059509 | 0.2243 | 0.073242 | -0.086975 | 0.059509 | 0.11902 | -0.022888 | 0.18768 | 0.13275 | -0.045776 | -0.10529 | 122.3373 | 122.1771 | 0.050354 | 122.3282 | 122.3236 | 0.14648 | -0.13275 | 122.2183 | 122.1588 | 0.013733 | 122.3236 | 122.2412 | 0.082398 | -0.041199 | 122.4884 | 122.3053 | 122.3099 | -0.26092 | 122.4518 | 122.3969 | 122.3831 | -0.27924
958.3438 | 122.5937 | -122.2458 | 0.17853 | -0.2066 | 0.019119 | 0.0020936 | 0.0068273 | -0.0034842 | -0.0037662 | -0.0058747 | -0.2108 | -0.0089229 | -0.0026212 | -0.00090781 | 0.00090353 | -0.009094 | 0.10529 | 0.15564 | 0.12817 | 0.10986 | 0.17853 | 0.064087 | -0.068665 | 0.091553 | 0.21057 | 0.013733 | 0.16479 | 0.13733 | -0.018311 | -0.082397 | 122.3099 | 122.1771 | 0 | 122.4014 | 122.3557 | 0.17853 | -0.073242 | 122.2275 | 122.1634 | -0.013733 | 122.3373 | 122.2595 | 0.09613 | -0.041199 | 122.4243 | 122.3511 | 122.374 | -0.24719 | 122.4106 | 122.3831 | 122.4564 | -0.26092
960.0469 | 122.5662 | -122.2504 | 0.20142 | 0.15961 | 0.016129 | 0.0031616 | -0.00022208 | -0.0028432 | -0.00013458 | -0.0045929 | 0.13252 | -0.0059323 | -0.0068936 | 0.00037379 | 0.0038943 | -0.0088804 | 0.013733 | 0.013733 | -0.013733 | -0.027466 | 0.050354 | -0.045776 | -0.17853 | 0.07782 | 0.018311 | -0.045776 | 0.027466 | 0.004578 | -0.10986 | -0.15106 | 122.2046 | 122.0718 | -0.15106 | 122.2641 | 122.2229 | 0.15106 | -0.18768 | 122.1405 | 122.0993 | -0.17395 | 122.3282 | 122.2046 | 0.10529 | -0.19684 | 122.3007 | 122.2641 | 122.2366 | -0.37994 | 122.2778 | 122.2549 | 122.2687 | -0.35248
961.7188 | 122.5433 | -122.2824 | 0.20142 | 0.13672 | 0.019547 | 0.0040162 | 0.0021277 | -0.005834 | 0.00029262 | -0.0045929 | 0.071487 | -0.0063595 | -0.0034756 | -0.00090781 | 0.0049625 | -0.0080258 | -0.064087 | -0.10986 | -0.11902 | -0.091553 | 0.09613 | -0.086975 | -0.20142 | -0.032043 | -0.12817 | -0.15106 | 0.059509 | 0.045776 | -0.13275 | -0.20599 | 122.1954 | 122.081 | -0.10529 | 122.1725 | 122.1909 | 0.10986 | -0.2655 | 122.1497 | 122.0764 | -0.14191 | 122.2504 | 122.1313 | 0.054932 | -0.15564 | 122.3785 | 122.2183 | 122.1634 | -0.40283 | 122.3419 | 122.3282 | 122.1542 | -0.40741
963.3906 | 122.525 | -122.2733 | 0.19684 | 0.20538 | 0.017838 | 0.0033752 | 0.0025549 | -0.0069022 | -0.004407 | -0.0030975 | 0.21645 | -0.0076413 | -0.0058254 | -0.0030442 | 0.0017581 | -0.0078122 | 0.018311 | 0.004578 | 0.009155 | -0.013733 | 0.013733 | -0.064087 | -0.20142 | 0.059509 | 0.059509 | -0.018311 | -0.009155 | -0.022888 | -0.11902 | -0.17853 | 122.2092 | 122.0718 | -0.18311 | 122.2778 | 122.2595 | 0.18768 | -0.17853 | 122.1542 | 122.0947 | -0.20599 | 122.3328 | 122.2549 | 0.16022 | -0.21973 | 122.287 | 122.2916 | 122.2824 | -0.39825 | 122.2641 | 122.2504 | 122.3328 | -0.37537
965.0781 | 122.5983 | -122.3007 | 0.17395 | -0.27527 | 0.019974 | 0.0048706 | 0.0074683 | -0.0026296 | -0.0037662 | -0.0054475 | -0.18028 | -0.0070003 | -0.0034756 | -0.00090781 | 0.0011173 | -0.0075986 | 0.10529 | 0.13733 | 0.1236 | 0.10071 | 0.19684 | 0.07782 | -0.082397 | 0.07782 | 0.16937 | 0.009155 | 0.15564 | 0.1236 | -0.027466 | -0.082397 | 122.3785 | 122.2183 | 0.022888 | 122.438 | 122.4014 | 0.18311 | -0.068664 | 122.2733 | 122.2183 | -0.01831 | 122.3785 | 122.3099 | 0.091552 | -0.050354 | 122.4976 | 122.406 | 122.4243 | -0.25635 | 122.4564 | 122.4243 | 122.4701 | -0.25635
966.75 | 122.6212 | -122.2824 | 0.15106 | -0.22186 | 0.019119 | 0.0020936 | 0.0078955 | -0.005834 | -0.00077538 | -0.0052337 | -0.20317 | -0.0067867 | -0.0017666 | 0.0012284 | 0.0013309 | -0.010803 | 0.041199 | 0.064087 | 0.045776 | 0.054932 | 0.21515 | 0.050354 | -0.086975 | 0.068665 | 0.11444 | -0.036621 | 0.17395 | 0.15106 | -0.032043 | -0.082397 | 122.3328 | 122.1954 | 0.064087 | 122.3465 | 122.3373 | 0.14191 | -0.10986 | 122.2504 | 122.2 | 0.022888 | 122.3511 | 122.2458 | 0.045776 | 0 | 122.4976 | 122.3236 | 122.3282 | -0.23804 | 122.4564 | 122.4335 | 122.3969 | -0.23346
968.4375 | 122.5754 | -122.3007 | 0.19226 | 0.12146 | 0.018478 | 0.0027344 | 0.0025549 | -0.0056204 | -0.00098918 | -0.0037385 | 0.13252 | -0.0074277 | -0.006039 | -0.0026168 | 0.0066715 | -0.009094 | 0.013733 | 0.004578 | -0.009155 | 0 | 0.068665 | -0.045776 | -0.18768 | 0.064087 | 0.022888 | -0.027466 | 0.032043 | -0.013733 | -0.086975 | -0.17395 | 122.2549 | 122.113 | -0.1236 | 122.3053 | 122.3007 | 0.18768 | -0.17853 | 122.2137 | 122.1268 | -0.16022 | 122.3648 | 122.2733 | 0.14648 | -0.20599 | 122.3694 | 122.3145 | 122.2916 | -0.37994 | 122.3328 | 122.287 | 122.3236 | -0.36621
970.1406 | 122.6578 | -122.3007 | 0.15106 | -0.25238 | 0.016342 | 0.0027344 | 0.0049047 | -0.0051932 | -0.0018436 | -0.0041657 | -0.23369 | -0.0074277 | -0.0041164 | -0.00069421 | 0.0017581 | -0.009094 | 0.064087 | 0.064087 | 0.022888 | 0.059509 | 0.23346 | 0.059509 | -0.082397 | 0.045776 | 0.073242 | -0.054932 | 0.15564 | 0.13275 | -0.054932 | -0.1236 | 122.3602 | 122.2183 | 0.082397 | 122.3648 | 122.3602 | 0.14191 | -0.086975 | 122.2458 | 122.1771 | 0.004578 | 122.3465 | 122.2458 | 0.068664 | -0.018311 | 122.5342 | 122.3648 | 122.3236 | -0.23346 | 122.4564 | 122.4335 | 122.374 | -0.27466
971.8594 | 122.5479 | -122.2916 | 0.20142 | 0.014648 | 0.014633 | 0.001239 | 0.0027685 | -0.0054068 | -0.0041934 | -0.0054475 | 0.094375 | -0.0097775 | -0.0047574 | -0.0011216 | 0.00068993 | -0.0075986 | 0.041199 | 0.059509 | 0.050354 | 0.032043 | 0.1236 | 0.009155 | -0.12817 | 0.086975 | 0.1236 | 0.009155 | 0.07782 | 0.045776 | -0.041199 | -0.1236 | 122.3007 | 122.1634 | -0.07782 | 122.3511 | 122.3236 | 0.16022 | -0.16022 | 122.2504 | 122.168 | -0.1236 | 122.3785 | 122.3007 | 0.13275 | -0.15564 | 122.4152 | 122.3328 | 122.3419 | -0.32959 | 122.3694 | 122.3373 | 122.4152 | -0.32501
973.5312 | 122.5067 | -122.3145 | 0.20599 | 0.1062 | 0.015488 | 0.0052978 | 0.0023413 | -0.0056204 | -0.0035526 | -0.0050201 | 0.1783 | -0.0080685 | -0.0064664 | -5.3406e-05 | 0.0043215 | -0.0063168 | 0.027466 | 0.041199 | 0.022888 | -0.013733 | 0.045776 | -0.027466 | -0.16022 | 0.09613 | 0.082397 | 0 | 0.045776 | 0.018311 | -0.082397 | -0.14648 | 122.287 | 122.1542 | -0.16022 | 122.3557 | 122.3007 | 0.14648 | -0.17853 | 122.2321 | 122.168 | -0.16022 | 122.4106 | 122.3145 | 0.14648 | -0.18768 | 122.3602 | 122.3419 | 122.3373 | -0.36621 | 122.3602 | 122.3328 | 122.3969 | -0.35248
975.2344 | 122.5204 | -122.3007 | 0.18768 | 0.13672 | 0.013992 | 0.0048706 | 0.00063232 | -0.0047658 | -0.0039798 | -0.0058747 | 0.14015 | -0.0078549 | -0.0041164 | -0.00048061 | 0.0026125 | -0.007385 | 0.036621 | 0.027466 | 0.032043 | -0.022888 | 0.054932 | -0.050354 | -0.16937 | 0.10071 | 0.10071 | -0.009155 | 0.073242 | 0.045776 | -0.068665 | -0.13275 | 122.2504 | 122.1313 | -0.13275 | 122.3282 | 122.2778 | 0.14649 | -0.15106 | 122.2321 | 122.168 | -0.11444 | 122.4014 | 122.2916 | 0.1236 | -0.14191 | 122.3557 | 122.3373 | 122.3328 | -0.35706 | 122.374 | 122.3465 | 122.4014 | -0.32043
976.9688 | 122.612 | -122.2961 | 0.16479 | -0.26001 | 0.016769 | 0.0025208 | 0.0078955 | -0.0036978 | 0.0011472 | -0.0058747 | -0.17265 | -0.0061459 | -0.0039028 | -0.0017624 | 0.0026125 | -0.0095212 | 0.14191 | 0.1236 | 0.10071 | 0.086975 | 0.21515 | 0.050354 | -0.068665 | 0.086975 | 0.15106 | -0.027466 | 0.16022 | 0.14191 | -0.013733 | -0.082397 | 122.3465 | 122.2275 | 0.050354 | 122.4197 | 122.3831 | 0.15564 | -0.022888 | 122.2824 | 122.2137 | -0.004578 | 122.3831 | 122.2687 | 0.054931 | -0.022888 | 122.5113 | 122.4381 | 122.3969 | -0.23346 | 122.4564 | 122.4381 | 122.4472 | -0.24719
978.6562 | 122.6212 | -122.287 | 0.16022 | -0.19897 | 0.019333 | 0.0033752 | 0.0057593 | -0.0060476 | -0.0022708 | -0.0063019 | -0.12688 | -0.0076413 | -0.0026212 | -0.0013352 | 0.0015445 | -0.010803 | 0.16022 | 0.19684 | 0.17853 | 0.11902 | 0.16937 | 0.082397 | -0.045776 | 0.16022 | 0.27924 | 0.082397 | 0.09613 | 0.09613 | -0.022888 | -0.064087 | 122.3694 | 122.2412 | 0.009156 | 122.4838 | 122.406 | 0.16479 | 0 | 122.2641 | 122.2229 | -0.064087 | 122.4472 | 122.3694 | 0.14648 | -0.064087 | 122.4564 | 122.4472 | 122.4655 | -0.20599 | 122.3831 | 122.3831 | 122.5662 | -0.2243
980.3281 | 122.6212 | -122.3007 | 0.15106 | -0.17609 | 0.016129 | 0.0044434 | 0.0068273 | -0.0032706 | -0.0020572 | -0.0028839 | -0.14977 | -0.0089229 | -0.0041164 | -0.00026701 | 0.0021853 | -0.010162 | 0.14648 | 0.16479 | 0.15564 | 0.12817 | 0.16022 | 0.059509 | -0.045776 | 0.14648 | 0.26093 | 0.073242 | 0.12817 | 0.07782 | -0.022888 | -0.073242 | 122.3602 | 122.2549 | 0.009155 | 122.4655 | 122.4289 | 0.17395 | -0.004578 | 122.2778 | 122.2275 | -0.022888 | 122.4472 | 122.374 | 0.14648 | -0.073242 | 122.4609 | 122.4472 | 122.4564 | -0.19684 | 122.4289 | 122.3785 | 122.5616 | -0.2243
982.0156 | 122.5479 | -122.3373 | 0.21057 | 0.075684 | 0.018692 | 0.0031616 | 0.0017005 | -0.0060476 | 0.005206 | -0.0037385 | -0.050583 | -0.0046505 | -0.0047574 | -0.0030442 | 0.0056033 | -0.011017 | -0.032043 | -0.09613 | -0.10529 | -0.054932 | 0.11444 | -0.068665 | -0.20142 | -0.045776 | -0.13275 | -0.1831 | 0.068665 | 0.050354 | -0.12817 | -0.21515 | 122.2687 | 122.1359 | -0.09613 | 122.2412 | 122.2824 | 0.14648 | -0.24261 | 122.2092 | 122.1222 | -0.14191 | 122.2916 | 122.1542 | 0.032044 | -0.16022 | 122.4518 | 122.3053 | 122.2321 | -0.41199 | 122.406 | 122.3877 | 122.2046 | -0.42572
983.6875 | 122.5388 | -122.3236 | 0.16479 | 0.052795 | 0.017624 | 0.0025208 | 0.0014867 | -0.0039114 | 0.0041378 | -0.0045929 | -0.012436 | -0.0065731 | -0.0039028 | 0.0010148 | 0.0056033 | -0.0093076 | -0.045776 | -0.086975 | -0.10529 | -0.059509 | 0.10986 | -0.07782 | -0.20599 | -0.032043 | -0.13733 | -0.16937 | 0.068665 | 0.045776 | -0.12817 | -0.21057 | 122.2458 | 122.1176 | -0.054932 | 122.2366 | 122.2641 | 0.14649 | -0.21057 | 122.1954 | 122.113 | -0.09613 | 122.2916 | 122.1542 | 0.041198 | -0.11902 | 122.4335 | 122.2778 | 122.2183 | -0.37079 | 122.3923 | 122.3694 | 122.1863 | -0.37537
985.3594 | 122.5433 | -122.3099 | 0.16022 | 0.068054 | 0.016129 | 0.0040162 | 0.0021277 | -0.0056204 | -0.0035526 | -0.0052337 | 0.13252 | -0.0087093 | -0.004971 | -0.0021896 | 0.00090353 | -0.0080258 | 0.009155 | 0.07782 | 0.050354 | 0.018311 | 0.091553 | -0.004578 | -0.15564 | 0.10071 | 0.10986 | -0.013733 | 0.073242 | 0.045776 | -0.059509 | -0.11902 | 122.3053 | 122.1542 | -0.068664 | 122.3877 | 122.3282 | 0.17395 | -0.15106 | 122.2504 | 122.1909 | -0.086975 | 122.4106 | 122.2961 | 0.10529 | -0.11444 | 122.4014 | 122.319 | 122.3602 | -0.31586 | 122.3831 | 122.3557 | 122.4197 | -0.27924
987.0469 | 122.5571 | -122.3511 | 0.20142 | -0.023499 | 0.020615 | 0.0044434 | 0.0025549 | -0.0060476 | 0.003497 | -0.0041657 | -0.020065 | -0.0059323 | -0.0068936 | -0.00069421 | 0.0058169 | -0.0097348 | 0.013733 | -0.004578 | -0.032043 | -0.027466 | 0.10529 | -0.041199 | -0.17395 | -0.027466 | -0.082397 | -0.15564 | 0.054932 | 0.064087 | -0.11902 | -0.20142 | 122.3099 | 122.1771 | -0.09613 | 122.3465 | 122.3236 | 0.14648 | -0.18768 | 122.2321 | 122.1497 | -0.14648 | 122.3236 | 122.1954 | 0.045776 | -0.13733 | 122.4564 | 122.3648 | 122.319 | -0.37537 | 122.406 | 122.4152 | 122.2687 | -0.40283
988.7188 | 122.5845 | -122.319 | 0.16937 | -0.046387 | 0.020401 | 0.0027344 | 0.0029821 | -0.0060476 | 0.0011472 | -0.0026703 | -0.12688 | -0.0061459 | -0.0056118 | -0.001976 | 0.0047489 | -0.009094 | 0.068665 | 0.045776 | 0.004578 | 0.018311 | 0.14191 | 0.004578 | -0.14648 | 0.059509 | 0.013733 | -0.086975 | 0.068665 | 0.082397 | -0.09613 | -0.15106 | 122.3236 | 122.1725 | -0.027466 | 122.3648 | 122.3373 | 0.16479 | -0.10071 | 122.2229 | 122.168 | -0.10071 | 122.3785 | 122.2321 | 0.064087 | -0.086976 | 122.4609 | 122.3877 | 122.3236 | -0.31586 | 122.3877 | 122.4014 | 122.3328 | -0.32044
990.3906 | 122.6669 | -122.2595 | 0.12817 | -0.084534 | 0.016769 | 0.0044434 | 0.0064001 | -0.0066884 | -0.0071842 | -0.0028839 | -0.012436 | -0.010632 | -0.0034756 | -5.3406e-05 | -0.0012327 | -0.0086666 | 0.086975 | 0.13275 | 0.1236 | 0.091553 | 0.15106 | 0.041199 | -0.10071 | 0.16022 | 0.26093 | 0.09613 | 0.1236 | 0.086975 | -0.036621 | -0.068665 | 122.3007 | 122.1588 | 0.022888 | 122.3923 | 122.3511 | 0.19226 | -0.041199 | 122.2229 | 122.1909 | -0.004578 | 122.4197 | 122.3557 | 0.16479 | -0.041199 | 122.4106 | 122.3465 | 122.3831 | -0.22888 | 122.3831 | 122.3465 | 122.5204 | -0.19684
992.0625 | 122.5479 | -122.3557 | 0.19684 | 0.0070193 | 0.018692 | 0.0027344 | 0.0029821 | -0.004125 | 0.0028562 | -0.0028839 | 0.03334 | -0.0070003 | -0.0036892 | -0.00069421 | 0.0066715 | -0.0082394 | 0.004578 | -0.032043 | -0.054932 | -0.032043 | 0.11444 | -0.032043 | -0.17853 | -0.036621 | -0.082397 | -0.15564 | 0.07782 | 0.050354 | -0.12817 | -0.19226 | 122.3236 | 122.1771 | -0.082397 | 122.3236 | 122.3236 | 0.14648 | -0.19226 | 122.2275 | 122.1634 | -0.11902 | 122.319 | 122.2 | 0.036621 | -0.14648 | 122.4701 | 122.3602 | 122.3007 | -0.37537 | 122.4335 | 122.406 | 122.2733 | -0.3891
993.75 | 122.5433 | -122.3282 | 0.16937 | 0.15198 | 0.017838 | 0.0033752 | 0.0040503 | -0.0034842 | -0.0041934 | -0.0043793 | 0.1783 | -0.0097775 | -0.0047574 | -0.001976 | 0.0017581 | -0.0080258 | 0.022888 | 0.032043 | 0.018311 | -0.018311 | 0.059509 | -0.045776 | -0.1831 | 0.09613 | 0.10071 | -0.004578 | 0.036621 | 0.041199 | -0.054932 | -0.14648 | 122.2824 | 122.1451 | -0.10986 | 122.3602 | 122.3099 | 0.16479 | -0.14649 | 122.2733 | 122.1817 | -0.13275 | 122.4243 | 122.3236 | 0.14191 | -0.12817 | 122.3877 | 122.3511 | 122.3465 | -0.35248 | 122.3648 | 122.3694 | 122.4289 | -0.31586
995.4219 | 122.6395 | -122.2916 | 0.12817 | -0.1532 | 0.017838 | 0.0044434 | 0.0059729 | -0.0047658 | -0.0029118 | -0.0065155 | -0.14977 | -0.0080685 | -0.0064664 | -0.0041122 | 0.0011173 | -0.008453 | 0.16937 | 0.17395 | 0.16022 | 0.12817 | 0.16022 | 0.068665 | -0.054932 | 0.16479 | 0.3067 | 0.10529 | 0.1236 | 0.10071 | 0 | -0.068665 | 122.3602 | 122.2366 | 0.032043 | 122.4655 | 122.4197 | 0.18311 | 0.041199 | 122.2916 | 122.2229 | -0.004578 | 122.4564 | 122.3969 | 0.17395 | -0.027466 | 122.4518 | 122.4609 | 122.4518 | -0.18311 | 122.4152 | 122.3923 | 122.5983 | -0.19684
997.1094 | 122.5983 | -122.319 | 0.16022 | 0.15961 | 0.015915 | 0.0035888 | 0.0040503 | -0.0030568 | -0.00013458 | -0.0039521 | 0.1783 | -0.0061459 | -0.0058254 | -0.0017624 | 0.0053897 | -0.0095212 | 0.054932 | -0.013733 | -0.004578 | 0.009155 | 0.045776 | -0.050354 | -0.18768 | 0.073242 | 0.027466 | -0.027466 | 0.027466 | -0.009155 | -0.10071 | -0.17395 | 122.2687 | 122.1313 | -0.11444 | 122.3053 | 122.3282 | 0.19684 | -0.10528 | 122.2183 | 122.1451 | -0.13275 | 122.3923 | 122.2916 | 0.14648 | -0.16937 | 122.3648 | 122.374 | 122.3145 | -0.3479 | 122.3465 | 122.3099 | 122.3465 | -0.33417
998.7812 | 122.6074 | -122.3145 | 0.17853 | 0.16724 | 0.017197 | 0.0070068 | 0.0025549 | -0.0054068 | 0.0015744 | -0.0026703 | 0.15541 | -0.0057187 | -0.006039 | 0.0027236 | 0.0045351 | -0.0078122 | -0.013733 | -0.086975 | -0.086975 | -0.082397 | 0.082397 | -0.064087 | -0.21057 | 0.018311 | -0.059509 | -0.086975 | 0.032043 | 0.022888 | -0.1236 | -0.17853 | 122.2504 | 122.1039 | -0.096131 | 122.2275 | 122.2321 | 0.12817 | -0.19226 | 122.1909 | 122.1359 | -0.14648 | 122.3328 | 122.2275 | 0.091553 | -0.15564 | 122.3969 | 122.3007 | 122.2275 | -0.3891 | 122.3465 | 122.3373 | 122.2549 | -0.35706
1000.4531 | 122.612 | -122.3419 | 0.17853 | 0.15198 | 0.016983 | 0.0027344 | 0.0027685 | -0.0056204 | 0.00050622 | -0.0020295 | 0.14015 | -0.0076413 | -0.0075344 | -0.001976 | 0.0056033 | -0.008453 | -0.004578 | -0.086975 | -0.09613 | -0.086975 | 0.073242 | -0.068665 | -0.22888 | 0.036621 | -0.050354 | -0.091553 | 0.022888 | 0.004578 | -0.10529 | -0.16937 | 122.2733 | 122.113 | -0.10529 | 122.2549 | 122.2549 | 0.14191 | -0.18311 | 122.2366 | 122.1725 | -0.15564 | 122.3785 | 122.2504 | 0.07782 | -0.17395 | 122.4152 | 122.3373 | 122.2458 | -0.40741 | 122.3648 | 122.3465 | 122.2916 | -0.3479
1002.1406 | 122.5479 | -122.3511 | 0.17395 | 0.12909 | 0.018051 | 0.0027344 | 0.0017005 | -0.0047658 | -0.0031254 | -0.0048065 | 0.16304 | -0.0097775 | -0.0045438 | 0.00080099 | 0.0032535 | -0.0082394 | 0.027466 | 0.045776 | 0.045776 | -0.009155 | 0.027466 | -0.032043 | -0.17395 | 0.082397 | 0.073242 | -0.013733 | 0.013733 | -0.004578 | -0.086975 | -0.14648 | 122.319 | 122.1771 | -0.14648 | 122.3969 | 122.3419 | 0.16479 | -0.14648 | 122.2641 | 122.2046 | -0.16022 | 122.4335 | 122.3373 | 0.13275 | -0.17853 | 122.3785 | 122.3785 | 122.3969 | -0.3479 | 122.3648 | 122.3465 | 122.4243 | -0.32043
1003.8906 | 122.6074 | -122.3511 | 0.17395 | -0.076904 | 0.019333 | 0.0038024 | 0.0059729 | -0.0049796 | 0.0032834 | -0.0026703 | -0.11925 | -0.0065731 | -0.0053982 | -0.0028306 | 0.0056033 | -0.010376 | 0.073242 | 0.027466 | 0.013733 | 0.013733 | 0.15106 | -0.022888 | -0.16022 | 0.045776 | 0.018311 | -0.07782 | 0.07782 | 0.059509 | -0.10986 | -0.16479 | 122.3282 | 122.1909 | -0.022888 | 122.3785 | 122.3648 | 0.17395 | -0.10071 | 122.2412 | 122.1863 | -0.09613 | 122.3969 | 122.2733 | 0.086975 | -0.11444 | 122.5021 | 122.4243 | 122.3648 | -0.33417 | 122.4289 | 122.4106 | 122.3694 | -0.33874
1005.625 | 122.6944 | -122.287 | 0.14648 | -0.22949 | 0.019119 | 0.0048706 | 0.0051183 | -0.0043386 | 0.00071982 | -0.0043793 | -0.19554 | -0.0078549 | -0.0045438 | -0.001976 | 0.0028263 | -0.0061032 | 0.09613 | 0.050354 | 0.032043 | 0.068665 | 0.25635 | 0.050354 | -0.10071 | 0.054932 | 0.073242 | -0.054932 | 0.16479 | 0.13733 | -0.045776 | -0.11902 | 122.3373 | 122.1863 | 0.10986 | 122.3373 | 122.3557 | 0.16937 | -0.050354 | 122.2412 | 122.168 | 0.018311 | 122.3419 | 122.2321 | 0.064087 | -0.009155 | 122.5433 | 122.3831 | 122.319 | -0.24719 | 122.4518 | 122.4243 | 122.3602 | -0.2655
1007.375 | 122.6715 | -122.3053 | 0.15106 | -0.25238 | 0.016342 | 0.0038024 | 0.0064001 | -0.0049796 | -0.0012028 | -0.0018159 | -0.24895 | -0.0076413 | -0.0017666 | 0.0010148 | 0.0011173 | -0.0086666 | 0.068665 | 0.059509 | 0.032043 | 0.064087 | 0.24719 | 0.045776 | -0.082397 | 0.041199 | 0.091553 | -0.050354 | 0.18768 | 0.14648 | -0.022888 | -0.11902 | 122.3511 | 122.2229 | 0.09613 | 122.3648 | 122.3694 | 0.14648 | -0.082397 | 122.2824 | 122.1863 | 0.036621 | 122.3465 | 122.2549 | 0.068665 | -0.004578 | 122.5525 | 122.374 | 122.3373 | -0.23346 | 122.493 | 122.4518 | 122.3969 | -0.27008
1009.125 | 122.6166 | -122.3465 | 0.17395 | 0.12909 | 0.019974 | 0.0038024 | 0.0021277 | -0.0039114 | 0.00071982 | -0.0039521 | 0.17067 | -0.0061459 | -0.0043302 | 0.00037379 | 0.0043215 | -0.0088804 | -0.032043 | -0.09613 | -0.086975 | -0.082397 | 0.09613 | -0.073242 | -0.21057 | 0.013733 | -0.086975 | -0.10986 | 0.050354 | 0.022888 | -0.12817 | -0.18768 | 122.2733 | 122.1359 | -0.07782 | 122.2504 | 122.2641 | 0.12817 | -0.20599 | 122.2183 | 122.1588 | -0.1236 | 122.3602 | 122.2366 | 0.07782 | -0.15106 | 122.4426 | 122.3145 | 122.2595 | -0.38452 | 122.3969 | 122.3694 | 122.2595 | -0.36163
1010.875 | 122.6074 | -122.3373 | 0.1831 | -0.069275 | 0.019547 | 0.0033752 | 0.0023413 | -0.0056204 | 0.0013608 | -0.0026703 | -0.10399 | -0.0067867 | -0.0051846 | 0.00037379 | 0.0049625 | -0.010589 | 0.086975 | 0.032043 | 0.004578 | 0.022888 | 0.13733 | -0.022888 | -0.16479 | 0.018311 | 0.004578 | -0.091553 | 0.091553 | 0.050354 | -0.07782 | -0.13275 | 122.3145 | 122.1725 | -0.045776 | 122.3694 | 122.3602 | 0.18768 | -0.09613 | 122.2595 | 122.2046 | -0.091552 | 122.3557 | 122.2458 | 0.041198 | -0.13275 | 122.4747 | 122.4243 | 122.3419 | -0.3479 | 122.4289 | 122.3877 | 122.3419 | -0.31586
1012.5469 | 122.5662 | -122.3648 | 0.18768 | -0.0082397 | 0.021042 | 0.0027344 | 0.0027685 | -0.0054068 | 0.0043514 | -0.0033111 | 0.04097 | -0.0046505 | -0.0028348 | -0.00048061 | 0.0038943 | -0.0080258 | -0.013733 | -0.068665 | -0.068665 | -0.050354 | 0.10986 | -0.054932 | -0.20599 | -0.045776 | -0.091553 | -0.15564 | 0.059509 | 0.054932 | -0.11444 | -0.19684 | 122.3099 | 122.1588 | -0.07782 | 122.2961 | 122.3145 | 0.15564 | -0.20142 | 122.2504 | 122.168 | -0.12817 | 122.319 | 122.2092 | 0.041198 | -0.13275 | 122.4747 | 122.3511 | 122.2961 | -0.39368 | 122.4243 | 122.4197 | 122.2733 | -0.38452
1014.2969 | 122.5983 | -122.3557 | 0.16479 | 0.045166 | 0.016556 | 0.0023072 | 0.0070409 | -0.0039114 | -0.007825 | -0.0028839 | 0.10963 | -0.0080685 | -0.006039 | -0.00090781 | -0.0035825 | -0.006744 | 0.022888 | 0.032043 | 0.054932 | 0.027466 | 0.10986 | 0.009155 | -0.1236 | 0.073242 | 0.13733 | 0.018311 | 0.10071 | 0.050354 | -0.045776 | -0.10986 | 122.3648 | 122.2321 | -0.054932 | 122.3877 | 122.3831 | 0.15106 | -0.14191 | 122.3099 | 122.2458 | -0.064087 | 122.4289 | 122.374 | 0.12817 | -0.11444 | 122.4655 | 122.3785 | 122.4106 | -0.28839 | 122.4564 | 122.406 | 122.493 | -0.27466
1016.0312 | 122.6761 | -122.3282 | 0.14191 | -0.13031 | 0.019333 | 0.0035888 | 0.0042639 | -0.0019888 | 0.0015744 | -0.0026703 | -0.16502 | -0.0070003 | -0.0051846 | 0.00058739 | 0.0049625 | -0.01123 | 0.054932 | 0.027466 | 0.018311 | 0.036621 | 0.16937 | -0.009155 | -0.14648 | 0.032043 | 0.036621 | -0.059509 | 0.09613 | 0.073242 | -0.091553 | -0.16022 | 122.319 | 122.1817 | 0.027466 | 122.3557 | 122.3648 | 0.18311 | -0.086975 | 122.2366 | 122.168 | -0.045777 | 122.3602 | 122.2687 | 0.10071 | -0.068665 | 122.4976 | 122.3831 | 122.3465 | -0.28839 | 122.4243 | 122.4014 | 122.3648 | -0.30212
1017.7656 | 122.58 | -122.3282 | 0.17395 | 0.16724 | 0.020615 | 0.00017099 | 0.0034093 | -0.0064748 | -0.0035526 | -0.0024567 | 0.22408 | -0.0093503 | -0.0047574 | 0.00037379 | 0.0023989 | -0.0080258 | 0 | 0.009155 | 0.027466 | -0.013733 | 0.018311 | -0.045776 | -0.21515 | 0.068665 | 0.045776 | -0.022888 | 0.004578 | -0.018311 | -0.11902 | -0.15106 | 122.2824 | 122.113 | -0.15564 | 122.3373 | 122.3145 | 0.20142 | -0.17395 | 122.2092 | 122.1771 | -0.16937 | 122.3969 | 122.3053 | 0.12817 | -0.19226 | 122.3465 | 122.3282 | 122.3557 | -0.3891 | 122.3328 | 122.3099 | 122.374 | -0.32501
1019.5 | 122.6715 | -122.319 | 0.12817 | -0.19135 | 0.018051 | 0.0052978 | 0.0068273 | -0.0045522 | -0.005048 | -0.0045929 | -0.14214 | -0.0099911 | -0.0036892 | -0.00090781 | -0.00059167 | -0.0078122 | 0.13733 | 0.21973 | 0.17853 | 0.1236 | 0.16479 | 0.059509 | -0.07782 | 0.17395 | 0.3067 | 0.1236 | 0.10071 | 0.09613 | 0.018311 | -0.059509 | 122.3785 | 122.2412 | 0.036621 | 122.5388 | 122.4426 | 0.20142 | 0.009155 | 122.3373 | 122.2595 | -0.027466 | 122.493 | 122.4426 | 0.1831 | -0.032044 | 122.4838 | 122.4564 | 122.4976 | -0.20599 | 122.4197 | 122.4152 | 122.6257 | -0.18768
1021.1719 | 122.7036 | -122.3145 | 0.14191 | -0.084534 | 0.01976 | 0.0052978 | 0.0044775 | -0.0047658 | -0.0041934 | -0.0073701 | -0.073471 | -0.0093503 | -0.0062528 | -0.00048061 | -0.00059167 | -0.0088804 | 0.12817 | 0.16022 | 0.13275 | 0.09613 | 0.15106 | 0.054932 | -0.073242 | 0.18768 | 0.2655 | 0.086975 | 0.10529 | 0.086975 | 0.004578 | -0.068665 | 122.3694 | 122.2412 | 0.009155 | 122.4747 | 122.4106 | 0.16937 | -0.013733 | 122.319 | 122.2458 | -0.036621 | 122.5021 | 122.4014 | 0.15564 | -0.054932 | 122.4655 | 122.4426 | 122.4472 | -0.21515 | 122.4197 | 122.4014 | 122.58 | -0.21057
1022.9219 | 122.7036 | -122.319 | 0.14191 | -0.12268 | 0.017838 | 0.0061524 | 0.0057593 | -0.0019888 | -0.004407 | -0.0048065 | -0.096359 | -0.0076413 | -0.006039 | -0.0030442 | 0.00090353 | -0.010162 | 0.17395 | 0.19226 | 0.16479 | 0.1236 | 0.16022 | 0.064087 | -0.064087 | 0.17853 | 0.29297 | 0.10529 | 0.1236 | 0.09613 | -0.004578 | -0.050354 | 122.3831 | 122.2549 | 0.01831 | 122.5113 | 122.4426 | 0.18768 | 0.032043 | 122.3145 | 122.2687 | -0.018311 | 122.4976 | 122.4243 | 0.15564 | -0.045777 | 122.4792 | 122.493 | 122.4838 | -0.20599 | 122.4426 | 122.4152 | 122.612 | -0.19226
1024.6562 | 122.6715 | -122.3282 | 0.15564 | -0.092163 | 0.01976 | 0.0025208 | 0.0010595 | -0.0043386 | 0.0037106 | -0.0028839 | -0.12688 | -0.0065731 | -0.0053982 | 0.00058739 | 0.0064577 | -0.011017 | 0.09613 | 0.032043 | 0.009155 | 0.022888 | 0.13733 | -0.004578 | -0.15106 | 0.064087 | 0.018311 | -0.059509 | 0.07782 | 0.068665 | -0.10071 | -0.15106 | 122.3236 | 122.1771 | -0.018311 | 122.3602 | 122.3511 | 0.17395 | -0.05951 | 122.2275 | 122.1771 | -0.07782 | 122.3923 | 122.2687 | 0.091553 | -0.086975 | 122.4655 | 122.4243 | 122.3373 | -0.3067 | 122.406 | 122.3969 | 122.3465 | -0.3067
1026.3438 | 122.731 | -122.3511 | 0.13733 | -0.17609 | 0.018906 | 0.0038024 | 0.0023413 | -0.0051932 | 0.0015744 | -0.0022431 | -0.24132 | -0.0063595 | -0.0043302 | -5.3406e-05 | 0.0047489 | -0.0093076 | 0.073242 | 0.050354 | 0 | 0.064087 | 0.21057 | 0.032043 | -0.10986 | 0.073242 | 0.073242 | -0.073242 | 0.13733 | 0.10071 | -0.064087 | -0.13733 | 122.3831 | 122.2412 | 0.073242 | 122.4014 | 122.4152 | 0.17395 | -0.064087 | 122.287 | 122.2137 | 0 | 122.4243 | 122.2778 | 0.064087 | -0.036621 | 122.5616 | 122.4243 | 122.3511 | -0.24719 | 122.4884 | 122.4518 | 122.4243 | -0.27466
1028.0781 | 122.6578 | -122.3511 | 0.16937 | -0.21423 | 0.019974 | 0.0023072 | 0.0068273 | -0.005834 | 0.00029262 | -0.0039521 | -0.22606 | -0.0076413 | -0.0024076 | 0.00058739 | 0.00090353 | -0.008453 | 0.064087 | 0.064087 | 0.050354 | 0.054932 | 0.22888 | 0.045776 | -0.11902 | 0.059509 | 0.12817 | -0.032043 | 0.18768 | 0.15106 | -0.041199 | -0.10529 | 122.3969 | 122.2321 | 0.059509 | 122.4152 | 122.406 | 0.17395 | -0.10529 | 122.3099 | 122.2458 | 0.01831 | 122.4106 | 122.319 | 0.073243 | -0.018311 | 122.58 | 122.4152 | 122.4014 | -0.28839 | 122.5388 | 122.5021 | 122.4792 | -0.27466
1029.8125 | 122.7127 | -122.3373 | 0.13733 | -0.17609 | 0.019333 | 0.0038024 | 0.0038367 | -0.0066884 | -0.00056178 | -0.0039521 | -0.19554 | -0.0072141 | -0.0034756 | 0.0016556 | 0.0051761 | -0.0097348 | 0.059509 | 0.036621 | 0.009155 | 0.054932 | 0.21057 | 0.036621 | -0.11444 | 0.036621 | 0.091553 | -0.041199 | 0.14191 | 0.11444 | -0.07782 | -0.10986 | 122.374 | 122.2229 | 0.073242 | 122.374 | 122.3923 | 0.16937 | -0.07782 | 122.2595 | 122.2275 | 0.004578 | 122.374 | 122.2961 | 0.068664 | -0.022888 | 122.5479 | 122.3969 | 122.3465 | -0.25177 | 122.4792 | 122.4518 | 122.4289 | -0.24719
1031.4844 | 122.7264 | -122.3145 | 0.16479 | -0.19135 | 0.019974 | 0.0027344 | 0.0083227 | -0.0051932 | 0.00093342 | -0.0024567 | -0.23369 | -0.0076413 | -0.0045438 | 0.00058739 | 0.0017581 | -0.010162 | 0.059509 | 0.036621 | 0.009155 | 0.050354 | 0.20599 | 0.032043 | -0.1236 | 0.059509 | 0.09613 | -0.054932 | 0.14191 | 0.1236 | -0.054932 | -0.11902 | 122.3465 | 122.1909 | 0.041199 | 122.3511 | 122.3648 | 0.17395 | -0.10529 | 122.2595 | 122.1954 | -0.022888 | 122.374 | 122.2595 | 0.064087 | -0.041199 | 122.5204 | 122.374 | 122.3236 | -0.28839 | 122.4564 | 122.438 | 122.4106 | -0.28381
1033.2188 | 122.6486 | -122.3648 | 0.17853 | 0.022278 | 0.013779 | 0.0052978 | 0.0036231 | -0.005834 | -0.0080386 | -0.0050201 | 0.10963 | -0.010205 | -0.0051846 | -0.00026701 | 0.0017581 | -0.009094 | 0.004578 | 0.068665 | 0.032043 | 0.036621 | 0.14648 | 0.018311 | -0.14191 | 0.07782 | 0.13733 | 0.009155 | 0.10071 | 0.07782 | -0.068665 | -0.10986 | 122.3831 | 122.2229 | -0.032044 | 122.4335 | 122.4014 | 0.17853 | -0.17395 | 122.2961 | 122.2549 | -0.07782 | 122.4426 | 122.374 | 0.11902 | -0.10071 | 122.5113 | 122.3694 | 122.3969 | -0.32044 | 122.4655 | 122.4426 | 122.5021 | -0.28839
1034.9688 | 122.5708 | -122.3648 | 0.1831 | 0.13672 | 0.017197 | 0.0018798 | 0.0036231 | -0.0043386 | -0.003339 | -0.0052337 | 0.16304 | -0.0070003 | -0.004971 | -0.00026701 | 0.0023989 | -0.010162 | 0.032043 | 0.059509 | 0.045776 | 0 | 0.050354 | -0.041199 | -0.19226 | 0.086975 | 0.064087 | 0 | 0.041199 | 0.009155 | -0.086975 | -0.16479 | 122.3236 | 122.1725 | -0.13275 | 122.4243 | 122.3648 | 0.19226 | -0.15106 | 122.2778 | 122.2 | -0.14191 | 122.4518 | 122.3648 | 0.16479 | -0.17395 | 122.4152 | 122.3969 | 122.4106 | -0.37537 | 122.406 | 122.374 | 122.4289 | -0.3479
1036.6406 | 122.5616 | -122.3969 | 0.16937 | 0.12909 | 0.016769 | 0.0050842 | 0.0021277 | -0.0062612 | -0.004407 | -0.0048065 | 0.20119 | -0.0080685 | -0.00668 | 0.00080099 | 0.0030399 | -0.009094 | 0.050354 | 0.050354 | 0.045776 | 0 | 0.054932 | -0.027466 | -0.17853 | 0.07782 | 0.068665 | -0.018311 | 0.027466 | 0 | -0.10986 | -0.16479 | 122.3694 | 122.2183 | -0.11444 | 122.4472 | 122.3969 | 0.17853 | -0.11902 | 122.287 | 122.2321 | -0.14191 | 122.4747 | 122.3785 | 0.14648 | -0.16937 | 122.4518 | 122.4472 | 122.4426 | -0.3479 | 122.4243 | 122.3969 | 122.4655 | -0.33417
1038.375 | 122.58 | -122.3511 | 0.18768 | 0.15961 | 0.016556 | 0.004657 | 0.0014867 | -0.0051932 | -0.0018436 | -0.0035249 | 0.14015 | -0.0076413 | -0.0073208 | -0.00048061 | 0.0030399 | -0.010589 | 0.032043 | 0.036621 | 0.041199 | -0.009155 | 0.027466 | -0.050354 | -0.20142 | 0.10071 | 0.07782 | 0 | 0.018311 | -0.013733 | -0.10529 | -0.15564 | 122.3007 | 122.1497 | -0.16022 | 122.3877 | 122.3419 | 0.19226 | -0.15564 | 122.2458 | 122.1954 | -0.16937 | 122.4518 | 122.3511 | 0.15564 | -0.20142 | 122.3785 | 122.3831 | 122.3923 | -0.3891 | 122.3694 | 122.3373 | 122.4289 | -0.34332
1040.1094 | 122.6624 | -122.3602 | 0.15106 | -0.084534 | 0.019974 | 0.0035888 | 0.0057593 | -0.0051932 | 0.0041378 | -0.0026703 | -0.13451 | -0.0059323 | -0.0030484 | -5.3406e-05 | 0.0073123 | -0.01123 | 0.086975 | 0.045776 | 0.018311 | 0.009155 | 0.15106 | -0.018311 | -0.14648 | 0.064087 | 0.018311 | -0.073242 | 0.086975 | 0.054932 | -0.10071 | -0.15564 | 122.3419 | 122.2137 | 0 | 122.406 | 122.3694 | 0.15564 | -0.064087 | 122.2595 | 122.2046 | -0.064087 | 122.4243 | 122.287 | 0.082398 | -0.09613 | 122.5113 | 122.4472 | 122.3785 | -0.29755 | 122.4472 | 122.4152 | 122.3785 | -0.3067
1041.7812 | 122.5937 | -122.3831 | 0.16022 | 0.12146 | 0.01976 | 0.0018798 | 0.0049047 | -0.0039114 | 0.0028562 | -0.00010687 | 0.086746 | -0.0040097 | -0.0041164 | 0.0012284 | 0.0043215 | -0.009094 | -0.068665 | -0.10529 | -0.10986 | -0.082397 | 0.11444 | -0.059509 | -0.21973 | -0.032043 | -0.11444 | -0.15564 | 0.068665 | 0.045776 | -0.14648 | -0.19684 | 122.3236 | 122.1634 | -0.045776 | 122.2778 | 122.3007 | 0.13733 | -0.22888 | 122.2366 | 122.1863 | -0.091552 | 122.3511 | 122.2275 | 0.041198 | -0.11444 | 122.4976 | 122.3145 | 122.2733 | -0.37994 | 122.4518 | 122.4289 | 122.2687 | -0.35706
1043.5156 | 122.5845 | -122.3923 | 0.18768 | -0.054016 | 0.019547 | 0.0038024 | 0.0051183 | -0.002416 | 0.0043514 | -0.0048065 | -0.08873 | -0.0055051 | -0.0036892 | -0.00048061 | 0.0070987 | -0.008453 | 0.022888 | 0.009155 | -0.004578 | -0.009155 | 0.12817 | -0.018311 | -0.17395 | -0.009155 | -0.054932 | -0.1236 | 0.073242 | 0.054932 | -0.11902 | -0.1831 | 122.374 | 122.2183 | -0.059509 | 122.4014 | 122.3831 | 0.16479 | -0.16479 | 122.2733 | 122.2092 | -0.11444 | 122.3831 | 122.2687 | 0.059509 | -0.13275 | 122.5204 | 122.4152 | 122.3877 | -0.36163 | 122.4655 | 122.4472 | 122.3373 | -0.37079
1045.2656 | 122.6349 | -122.3877 | 0.16937 | 0.12909 | 0.018265 | 0.0044434 | 0.0057593 | -0.0056204 | -0.0029118 | -0.0033111 | 0.15541 | -0.0084957 | -0.0019802 | -0.0013352 | 0.0019717 | -0.0086666 | 0.004578 | 0.032043 | 0.004578 | -0.004578 | 0.059509 | -0.036621 | -0.19226 | 0.064087 | 0.027466 | -0.018311 | 0.013733 | -0.027466 | -0.10986 | -0.17853 | 122.3511 | 122.1954 | -0.10986 | 122.4197 | 122.3831 | 0.18768 | -0.16479 | 122.2778 | 122.2092 | -0.15564 | 122.4518 | 122.3694 | 0.16022 | -0.19684 | 122.4472 | 122.3923 | 122.3923 | -0.36163 | 122.4014 | 122.3602 | 122.4152 | -0.3479
1046.9375 | 122.699 | -122.3419 | 0.12817 | -0.11505 | 0.018692 | 0.0016662 | 0.0031957 | -0.0066884 | 0.0013608 | -0.0039521 | -0.096359 | -0.0072141 | -0.0039028 | -5.3406e-05 | 0.0051761 | -0.0093076 | 0.054932 | 0.050354 | 0.004578 | 0.018311 | 0.16479 | 0.004578 | -0.16937 | 0.059509 | 0.054932 | -0.059509 | 0.091553 | 0.07782 | -0.07782 | -0.16937 | 122.3465 | 122.1725 | 0.036621 | 122.3923 | 122.3602 | 0.18768 | -0.073242 | 122.2641 | 122.1725 | -0.036621 | 122.4014 | 122.2824 | 0.10986 | -0.050354 | 122.5067 | 122.3969 | 122.3465 | -0.29755 | 122.4335 | 122.4197 | 122.3969 | -0.29755
1048.6875 | 122.6669 | -122.3648 | 0.14648 | -0.2066 | 0.017838 | 0.0055114 | 0.0046911 | -0.0064748 | -0.002698 | -0.0052337 | -0.19554 | -0.0072141 | -0.0058254 | 0.00037379 | 0.00026273 | -0.0095212 | 0.068665 | 0.086975 | 0.068665 | 0.086975 | 0.23346 | 0.07782 | -0.091553 | 0.054932 | 0.14648 | -0.018311 | 0.19684 | 0.15106 | -0.036621 | -0.10529 | 122.4426 | 122.2733 | 0.086975 | 122.4518 | 122.4518 | 0.17853 | -0.077819 | 122.3282 | 122.2595 | 0.050354 | 122.4197 | 122.3465 | 0.086975 | 0.004578 | 122.5983 | 122.4335 | 122.4335 | -0.23804 | 122.5616 | 122.5159 | 122.5113 | -0.25177
1050.375 | 122.7127 | -122.3557 | 0.13733 | -0.0082397 | 0.017624 | 0.0044434 | 0.0031957 | -0.0069022 | -0.0063296 | -0.0071563 | -0.050583 | -0.010632 | -0.00668 | -0.0024032 | 0.00026273 | -0.0082394 | 0.068665 | 0.14191 | 0.11444 | 0.082397 | 0.13733 | 0.027466 | -0.09613 | 0.16479 | 0.25177 | 0.10071 | 0.11444 | 0.086975 | -0.004578 | -0.082397 | 122.3831 | 122.2595 | 0 | 122.4976 | 122.438 | 0.17853 | -0.068664 | 122.3511 | 122.2733 | -0.022888 | 122.5204 | 122.4564 | 0.18311 | -0.050354 | 122.493 | 122.4243 | 122.4701 | -0.23346 | 122.4701 | 122.4426 | 122.6074 | -0.21973
1052.1094 | 122.5845 | -122.3923 | 0.16937 | 0.14435 | 0.015061 | 0.0035888 | 0.0031957 | -0.0036978 | -0.0029118 | -0.0039521 | 0.13252 | -0.0095639 | -0.0081754 | -0.0017624 | 0.0030399 | -0.0080258 | 0.041199 | 0.032043 | 0.045776 | 0.009155 | 0.068665 | -0.032043 | -0.16937 | 0.082397 | 0.10529 | 0.009155 | 0.059509 | 0.068665 | -0.054932 | -0.1236 | 122.3602 | 122.2229 | -0.10071 | 122.4243 | 122.4014 | 0.17853 | -0.12817 | 122.3373 | 122.2687 | -0.10986 | 122.4747 | 122.4014 | 0.13275 | -0.10071 | 122.4609 | 122.4335 | 122.438 | -0.33875 | 122.4518 | 122.4609 | 122.4976 | -0.29297
1053.8438 | 122.6898 | -122.3648 | 0.15106 | 0.045166 | 0.015274 | 0.0042298 | 0.0027685 | -0.0062612 | -0.0037662 | -0.0048065 | 0.079117 | -0.0087093 | -0.0068936 | -0.00069421 | 0.0036807 | -0.0082394 | 0.045776 | 0.022888 | 0.041199 | 0.045776 | 0.13733 | 0.004578 | -0.11444 | 0.091553 | 0.14648 | 0.022888 | 0.082397 | 0.07782 | -0.064087 | -0.10986 | 122.3694 | 122.2504 | -0.013733 | 122.3877 | 122.4106 | 0.16022 | -0.10529 | 122.3007 | 122.2549 | -0.068665 | 122.4564 | 122.3877 | 0.13275 | -0.073242 | 122.5021 | 122.4106 | 122.406 | -0.2655 | 122.4472 | 122.4426 | 122.5113 | -0.26093
1055.5156 | 122.7173 | -122.3328 | 0.14191 | -0.00061023 | 0.017624 | 0.0044434 | 0.0057593 | -0.0051932 | -0.004407 | -0.0069427 | 0.010452 | -0.0097775 | -0.0041164 | -0.00090781 | 0.00047633 | -0.010803 | 0.082397 | 0.054932 | 0.059509 | 0.059509 | 0.14648 | 0.032043 | -0.13275 | 0.12817 | 0.20142 | 0.059509 | 0.10986 | 0.07782 | -0.022888 | -0.091553 | 122.3648 | 122.2 | 0.004577 | 122.3877 | 122.3923 | 0.19226 | -0.05951 | 122.3099 | 122.2412 | -0.032044 | 122.4609 | 122.3923 | 0.15106 | -0.064087 | 122.4792 | 122.4152 | 122.3923 | -0.27466 | 122.4426 | 122.4106 | 122.5342 | -0.23346
1057.2656 | 122.7356 | -122.3602 | 0.14648 | -0.12268 | 0.018051 | 0.004657 | 0.0049047 | -0.0049796 | -0.0018436 | -0.0069427 | -0.11925 | -0.0089229 | -0.0045438 | -0.00090781 | -0.00080527 | -0.011444 | 0.16937 | 0.16479 | 0.15564 | 0.11444 | 0.17395 | 0.073242 | -0.091553 | 0.20142 | 0.28839 | 0.10986 | 0.11444 | 0.086975 | -0.013733 | -0.073242 | 122.4335 | 122.2687 | 0.027466 | 122.525 | 122.4747 | 0.20599 | 0.022889 | 122.3465 | 122.287 | -0.032043 | 122.5616 | 122.4701 | 0.18311 | -0.059509 | 122.5342 | 122.5296 | 122.5159 | -0.23804 | 122.4747 | 122.4472 | 122.6486 | -0.21973
1059.0156 | 122.6578 | -122.4106 | 0.1831 | 0.14435 | 0.020401 | 0.0020936 | 0.0023413 | -0.0036978 | 0.0043514 | -0.0050201 | 0.063858 | -0.0040097 | -0.0043302 | -0.00090781 | 0.0068851 | -0.0093076 | -0.018311 | -0.11444 | -0.1236 | -0.086975 | 0.09613 | -0.086975 | -0.23804 | 0.004578 | -0.13275 | -0.14191 | 0.07782 | 0.036621 | -0.13275 | -0.1831 | 122.3236 | 122.1725 | -0.086975 | 122.2961 | 122.3236 | 0.15106 | -0.20142 | 122.2778 | 122.2275 | -0.10528 | 122.4152 | 122.2687 | 0.041198 | -0.14648 | 122.5067 | 122.3923 | 122.287 | -0.42114 | 122.4884 | 122.4472 | 122.2778 | -0.36621
1060.6875 | 122.6349 | -122.374 | 0.14648 | 0.14435 | 0.018478 | 0.0044434 | -0.0015039 | -0.0030568 | 0.00029262 | -0.0018159 | 0.18593 | -0.0089229 | -0.0062528 | -0.0011216 | 0.0051761 | -0.0080258 | 0.054932 | 0.009155 | 0.009155 | 0.009155 | 0.041199 | -0.050354 | -0.21515 | 0.07782 | 0.041199 | -0.032043 | 0.013733 | 0.004578 | -0.10071 | -0.16937 | 122.3236 | 122.1588 | -0.10529 | 122.3831 | 122.3831 | 0.2243 | -0.091552 | 122.2733 | 122.2046 | -0.13275 | 122.4518 | 122.3419 | 0.13733 | -0.14191 | 122.4152 | 122.4289 | 122.3831 | -0.36163 | 122.3877 | 122.3785 | 122.4152 | -0.31586
1062.4219 | 122.6852 | -122.3785 | 0.15106 | -0.25238 | 0.015488 | 0.0061524 | 0.0074683 | -0.0036978 | -0.0018436 | -0.0060883 | -0.24895 | -0.0089229 | -0.0011258 | -0.0028306 | 0.0017581 | -0.0099484 | 0.14648 | 0.13275 | 0.13275 | 0.10986 | 0.21515 | 0.054932 | -0.07782 | 0.10529 | 0.17395 | -0.004578 | 0.14648 | 0.15106 | -0.027466 | -0.10529 | 122.4335 | 122.3007 | 0.064087 | 122.5113 | 122.4884 | 0.18768 | -0.004578 | 122.3511 | 122.2733 | -0.004578 | 122.4838 | 122.374 | 0.10071 | 0 | 122.5937 | 122.525 | 122.5113 | -0.22888 | 122.525 | 122.5296 | 122.5525 | -0.25635
1064.1719 | 122.6944 | -122.3648 | 0.15106 | -0.2066 | 0.020401 | 0.0020936 | 0.0074683 | -0.002416 | -0.0012028 | -0.0039521 | -0.18791 | -0.0097775 | -0.0045438 | 0.0012284 | 0.0019717 | -0.0086666 | 0.14648 | 0.15564 | 0.14191 | 0.13275 | 0.19226 | 0.068665 | -0.091553 | 0.11444 | 0.20599 | 0.022888 | 0.16479 | 0.12817 | -0.027466 | -0.073242 | 122.4335 | 122.2733 | 0.041199 | 122.5204 | 122.4976 | 0.2243 | -0.004578 | 122.3373 | 122.2916 | 0.013733 | 122.4792 | 122.3877 | 0.09613 | -0.022888 | 122.5571 | 122.5113 | 122.5067 | -0.24261 | 122.5296 | 122.493 | 122.5708 | -0.2243
1065.8438 | 122.6807 | -122.374 | 0.16022 | -0.26001 | 0.017624 | 0.0020936 | 0.0089635 | -0.0047658 | -0.00034818 | -0.0024567 | -0.23369 | -0.0078549 | -0.0017666 | -0.0013352 | 0.0041079 | -0.0086666 | 0.12817 | 0.15106 | 0.10529 | 0.10529 | 0.21973 | 0.059509 | -0.07782 | 0.086975 | 0.17853 | 0.009155 | 0.16937 | 0.13733 | -0.036621 | -0.10529 | 122.4335 | 122.2961 | 0.05951 | 122.525 | 122.4792 | 0.18311 | -0.032043 | 122.3373 | 122.2687 | 0.009156 | 122.4609 | 122.3831 | 0.11444 | -0.022888 | 122.5937 | 122.5021 | 122.4792 | -0.23804 | 122.5433 | 122.5113 | 122.5525 | -0.2655
1067.625 | 122.7264 | -122.3602 | 0.14191 | -0.092163 | 0.021469 | 0.0023072 | 0.0042639 | -0.0045522 | 0.0041378 | -0.0024567 | -0.18791 | -0.0078549 | -0.0053982 | -0.00026701 | 0.0038943 | -0.012726 | 0.059509 | 0.050354 | -0.004578 | 0.032043 | 0.15564 | -0.004578 | -0.16937 | 0.07782 | 0.045776 | -0.064087 | 0.082397 | 0.07782 | -0.091553 | -0.16937 | 122.3557 | 122.1909 | 0.013733 | 122.4106 | 122.3923 | 0.20142 | -0.082398 | 122.2687 | 122.1909 | -0.05951 | 122.438 | 122.2961 | 0.10529 | -0.064087 | 122.5159 | 122.4197 | 122.3557 | -0.31128 | 122.4426 | 122.438 | 122.406 | -0.31128
1069.375 | 122.699 | -122.3831 | 0.13275 | -0.18372 | 0.019974 | 0.0023072 | 0.0046911 | -0.0071158 | -0.003339 | -0.0058747 | -0.20317 | -0.0097775 | -0.006039 | -5.3406e-05 | -0.00037807 | -0.0099484 | 0.13275 | 0.16479 | 0.13733 | 0.13275 | 0.16479 | 0.050354 | -0.073242 | 0.13733 | 0.25635 | 0.073242 | 0.1236 | 0.091553 | -0.022888 | -0.082397 | 122.4335 | 122.3099 | 0.032044 | 122.5479 | 122.5159 | 0.20599 | 0 | 122.3602 | 122.3007 | -0.009155 | 122.5204 | 122.4564 | 0.15564 | -0.041198 | 122.5479 | 122.5159 | 122.5204 | -0.20599 | 122.5067 | 122.4747 | 122.6395 | -0.21515
1071.0781 | 122.6166 | -122.4243 | 0.17395 | 0.060425 | 0.01976 | 0.0042298 | 0.0034093 | -0.0062612 | 0.0020016 | -0.0033111 | 0.048599 | -0.0037961 | -0.0041164 | -0.00090781 | 0.0077395 | -0.0088804 | -0.054932 | -0.09613 | -0.10986 | -0.068665 | 0.1236 | -0.073242 | -0.22888 | -0.027466 | -0.10986 | -0.16937 | 0.064087 | 0.041199 | -0.15564 | -0.19684 | 122.3511 | 122.1954 | -0.050354 | 122.3282 | 122.3557 | 0.16022 | -0.22888 | 122.2687 | 122.2275 | -0.10986 | 122.3969 | 122.2549 | 0.027465 | -0.13275 | 122.5479 | 122.3694 | 122.3145 | -0.40283 | 122.4884 | 122.4655 | 122.3145 | -0.37079
1072.75 | 122.6028 | -122.406 | 0.18768 | 0.13672 | 0.015061 | 0.0048706 | 0.0010595 | -0.0045522 | -0.0046206 | -0.0041657 | 0.14015 | -0.0093503 | -0.0081754 | -0.0015488 | 0.0038943 | -0.010376 | 0.018311 | 0.054932 | 0.050354 | -0.018311 | 0.045776 | -0.041199 | -0.20142 | 0.09613 | 0.082397 | -0.013733 | 0.036621 | 0.004578 | -0.10529 | -0.16022 | 122.3648 | 122.2046 | -0.14191 | 122.4609 | 122.3877 | 0.18311 | -0.16937 | 122.3007 | 122.2458 | -0.15106 | 122.5021 | 122.3923 | 0.14648 | -0.1831 | 122.4518 | 122.4243 | 122.4564 | -0.3891 | 122.4426 | 122.4106 | 122.4884 | -0.3479
1074.4375 | 122.7402 | -122.374 | 0.14648 | -0.24475 | 0.018906 | 0.0038024 | 0.0078955 | -0.0047658 | 0.00093342 | -0.0024567 | -0.25658 | -0.0042233 | -0.0028348 | -0.0011216 | 0.0011173 | -0.0093076 | 0.07782 | 0.064087 | 0.054932 | 0.068665 | 0.26093 | 0.054932 | -0.086975 | 0.068665 | 0.10529 | -0.032043 | 0.16479 | 0.14648 | -0.059509 | -0.10529 | 122.4289 | 122.287 | 0.11444 | 122.438 | 122.4426 | 0.15564 | -0.068664 | 122.3145 | 122.2687 | 0.018311 | 122.4426 | 122.3419 | 0.073243 | 0 | 122.6349 | 122.4518 | 122.4289 | -0.23346 | 122.5388 | 122.5204 | 122.4792 | -0.25177
1076.1406 | 122.5891 | -122.4152 | 0.16937 | 0.098572 | 0.015274 | 0.0027344 | 0.00063232 | -0.0043386 | -0.0018436 | -0.0048065 | 0.20119 | -0.0084957 | -0.0062528 | -0.0015488 | 0.0030399 | -0.0063168 | 0.027466 | 0.059509 | 0.027466 | 0 | 0.059509 | -0.027466 | -0.16937 | 0.07782 | 0.10071 | 0 | 0.027466 | 0.027466 | -0.091553 | -0.16479 | 122.3877 | 122.2458 | -0.10986 | 122.4747 | 122.4152 | 0.16937 | -0.14191 | 122.3236 | 122.2504 | -0.14191 | 122.493 | 122.4152 | 0.16479 | -0.14191 | 122.4747 | 122.4426 | 122.4426 | -0.33875 | 122.4426 | 122.4426 | 122.5159 | -0.33417
1077.8281 | 122.7402 | -122.3694 | 0.12817 | -0.22949 | 0.018478 | 0.0052978 | 0.0074683 | -0.0049796 | -0.00056178 | -0.0030975 | -0.24895 | -0.0055051 | -0.0034756 | -0.0017624 | 0.0028263 | -0.0088804 | 0.10529 | 0.059509 | 0.027466 | 0.059509 | 0.25635 | 0.045776 | -0.068665 | 0.059509 | 0.086975 | -0.059509 | 0.15564 | 0.14191 | -0.059509 | -0.10071 | 122.4152 | 122.3007 | 0.12817 | 122.4289 | 122.4289 | 0.12817 | -0.022888 | 122.3099 | 122.2687 | 0.027466 | 122.4289 | 122.3099 | 0.041199 | 0.013733 | 122.6257 | 122.4747 | 122.3969 | -0.19684 | 122.525 | 122.5113 | 122.4564 | -0.22888
1079.5 | 122.7264 | -122.3831 | 0.15564 | -0.22186 | 0.017624 | 0.0042298 | 0.0085363 | -0.0039114 | -0.0014164 | -0.0052337 | -0.27184 | -0.0063595 | -0.0053982 | -0.0015488 | 0.00090353 | -0.010162 | 0.07782 | 0.054932 | 0.036621 | 0.059509 | 0.23346 | 0.059509 | -0.082397 | 0.054932 | 0.09613 | -0.032043 | 0.17395 | 0.16479 | -0.054932 | -0.10986 | 122.4426 | 122.3007 | 0.077819 | 122.438 | 122.4426 | 0.14191 | -0.07782 | 122.3282 | 122.2733 | 0.01831 | 122.438 | 122.3511 | 0.07782 | 0.009155 | 122.6166 | 122.4609 | 122.4197 | -0.23804 | 122.5571 | 122.5479 | 122.4792 | -0.2655
1081.1719 | 122.7127 | -122.3557 | 0.15106 | -0.13794 | 0.017197 | 0.0072204 | 0.0066137 | -0.0069022 | -0.006116 | -0.0045929 | -0.12688 | -0.010632 | -0.0047574 | -0.00069421 | 0.0019717 | -0.008453 | 0.15106 | 0.20142 | 0.15564 | 0.1236 | 0.1831 | 0.054932 | -0.082397 | 0.18768 | 0.31586 | 0.11444 | 0.1236 | 0.10071 | 0 | -0.068665 | 122.4106 | 122.2733 | 0.032043 | 122.5571 | 122.4792 | 0.20599 | 0 | 122.3557 | 122.287 | -0.027466 | 122.5433 | 122.4701 | 0.18311 | -0.050354 | 122.5388 | 122.5067 | 122.5113 | -0.23346 | 122.4792 | 122.4564 | 122.6715 | -0.21973
1082.8594 | 122.7539 | -122.3969 | 0.14191 | -0.099793 | 0.016556 | 0.0023072 | 0.0074683 | -0.0062612 | -0.0022708 | -0.0060883 | -0.081101 | -0.0087093 | -0.0036892 | -0.0013352 | 0.00090353 | -0.010803 | 0.14191 | 0.17853 | 0.14648 | 0.11902 | 0.17395 | 0.041199 | -0.09613 | 0.19684 | 0.28381 | 0.11444 | 0.10986 | 0.064087 | -0.022888 | -0.086975 | 122.4381 | 122.3007 | 0.032043 | 122.5754 | 122.5159 | 0.21515 | 0 | 122.374 | 122.3099 | -0.032044 | 122.5937 | 122.5113 | 0.20142 | -0.07782 | 122.5708 | 122.5388 | 122.5433 | -0.23804 | 122.5067 | 122.4609 | 122.6807 | -0.22888
1084.5469 | 122.5983 | -122.4152 | 0.16479 | 0.098572 | 0.020615 | 0.0042298 | 0.0038367 | -0.0039114 | -0.00163 | -0.0045929 | 0.16304 | -0.010205 | -0.0051846 | -0.0011216 | 0.0047489 | -0.009094 | 0.027466 | 0.059509 | 0.032043 | -0.013733 | 0.059509 | -0.050354 | -0.1831 | 0.086975 | 0.09613 | 0.004578 | 0.041199 | 0.032043 | -0.09613 | -0.15564 | 122.3648 | 122.2321 | -0.10529 | 122.4747 | 122.4014 | 0.16937 | -0.13733 | 122.319 | 122.2595 | -0.1236 | 122.5021 | 122.4197 | 0.16022 | -0.13275 | 122.4747 | 122.4426 | 122.4472 | -0.3479 | 122.4564 | 122.4472 | 122.5113 | -0.32044
1086.2344 | 122.6074 | -122.4289 | 0.19226 | -0.038757 | 0.019333 | 0.0031616 | 0.0017005 | -0.0062612 | 0.0049924 | -0.0041657 | -0.081101 | -0.0087093 | -0.0062528 | -0.00048061 | 0.0058169 | -0.012085 | 0.045776 | -0.009155 | -0.018311 | -0.009155 | 0.13275 | -0.045776 | -0.1831 | 0.022888 | -0.059509 | -0.12817 | 0.086975 | 0.054932 | -0.11902 | -0.18768 | 122.3831 | 122.2458 | -0.05951 | 122.4197 | 122.4197 | 0.17395 | -0.14648 | 122.3099 | 122.2412 | -0.10529 | 122.4518 | 122.3007 | 0.059509 | -0.13733 | 122.5616 | 122.4747 | 122.4106 | -0.37537 | 122.5159 | 122.4838 | 122.3694 | -0.37994
1087.9688 | 122.7631 | -122.3785 | 0.13733 | -0.22949 | 0.018692 | 0.0059388 | 0.0053321 | -0.0032706 | -0.00013458 | -0.0030975 | -0.22606 | -0.0065731 | -0.0058254 | -0.001976 | 0.0058169 | -0.0078122 | 0.082397 | 0.050354 | 0.027466 | 0.054932 | 0.24719 | 0.041199 | -0.082397 | 0.054932 | 0.09613 | -0.064087 | 0.16937 | 0.13733 | -0.050354 | -0.11902 | 122.4197 | 122.2961 | 0.10986 | 122.4289 | 122.4335 | 0.13733 | -0.054932 | 122.3282 | 122.2595 | 0.032044 | 122.4335 | 122.3145 | 0.054932 | 0 | 122.6257 | 122.4609 | 122.406 | -0.21973 | 122.5479 | 122.5159 | 122.4747 | -0.25635
1089.6719 | 122.6166 | -122.4106 | 0.17853 | 0.19012 | 0.01741 | 0.0055114 | 0.0021277 | -0.0039114 | -0.002698 | -0.0013885 | 0.1783 | -0.0070003 | -0.0071072 | -0.00069421 | 0.0028263 | -0.0080258 | 0.009155 | 0.036621 | 0.027466 | -0.004578 | 0.045776 | -0.064087 | -0.20142 | 0.082397 | 0.09613 | -0.009155 | 0.018311 | -0.004578 | -0.11902 | -0.16022 | 122.3465 | 122.2092 | -0.13275 | 122.4472 | 122.406 | 0.19684 | -0.16937 | 122.2916 | 122.2504 | -0.16022 | 122.493 | 122.4014 | 0.15106 | -0.18311 | 122.4564 | 122.4197 | 122.438 | -0.37994 | 122.4289 | 122.406 | 122.5067 | -0.33874
1091.4531 | 122.6944 | -122.4106 | 0.15106 | -0.18372 | 0.019333 | 0.004657 | 0.0051183 | -0.0036978 | -0.0031254 | -0.0058747 | -0.2108 | -0.0089229 | -0.0056118 | -0.00069421 | 0.00090353 | -0.009094 | 0.1236 | 0.16479 | 0.14191 | 0.11902 | 0.16479 | 0.041199 | -0.10071 | 0.13275 | 0.25635 | 0.073242 | 0.14648 | 0.1236 | -0.018311 | -0.07782 | 122.4518 | 122.3099 | 0.013733 | 122.5754 | 122.5296 | 0.21973 | -0.027466 | 122.3923 | 122.3328 | -0.004578 | 122.5433 | 122.4838 | 0.15106 | -0.027466 | 122.5754 | 122.5342 | 122.5525 | -0.25177 | 122.5571 | 122.5342 | 122.6669 | -0.22888
1093.1406 | 122.7539 | -122.3602 | 0.13275 | -0.22949 | 0.017838 | 0.0035888 | 0.0046911 | -0.0047658 | -0.00013458 | -0.0039521 | -0.22606 | -0.0061459 | -0.004971 | 0.00037379 | 0.0041079 | -0.0099484 | 0.086975 | 0.032043 | 0.004578 | 0.059509 | 0.25177 | 0.054932 | -0.086975 | 0.041199 | 0.086975 | -0.059509 | 0.15106 | 0.13275 | -0.045776 | -0.12817 | 122.4152 | 122.2733 | 0.11902 | 122.3923 | 122.4197 | 0.14648 | -0.045776 | 122.3145 | 122.2321 | 0.018311 | 122.4014 | 122.3007 | 0.068665 | 0 | 122.612 | 122.4472 | 122.3648 | -0.21973 | 122.5113 | 122.493 | 122.4472 | -0.26093
1094.8281 | 122.7585 | -122.3694 | 0.14191 | -0.19897 | 0.023819 | 0.0042298 | 0.0066137 | -0.0039114 | 0.00029262 | -0.0050201 | -0.18791 | -0.0059323 | -0.003262 | 0.001442 | 0.0051761 | -0.007385 | 0.050354 | 0.041199 | 0.004578 | 0.054932 | 0.23804 | 0.027466 | -0.11902 | 0.041199 | 0.09613 | -0.045776 | 0.16937 | 0.13275 | -0.073242 | -0.13733 | 122.3969 | 122.2504 | 0.09613 | 122.4106 | 122.4243 | 0.17395 | -0.091553 | 122.2961 | 122.2321 | 0.027466 | 122.4106 | 122.3236 | 0.091553 | -0.009156 | 122.6074 | 122.4197 | 122.374 | -0.26093 | 122.5388 | 122.5021 | 122.4655 | -0.27924
1096.5 | 122.7722 | -122.3923 | 0.12817 | -0.2066 | 0.019119 | 0.0031616 | 0.0072547 | -0.0034842 | 0.00029262 | -0.0026703 | -0.20317 | -0.0076413 | -0.0039028 | -5.3406e-05 | 0.0026125 | -0.010376 | 0.050354 | 0.050354 | 0.009155 | 0.064087 | 0.23346 | 0.036621 | -0.1236 | 0.054932 | 0.09613 | -0.045776 | 0.15106 | 0.13275 | -0.059509 | -0.14191 | 122.4289 | 122.2687 | 0.10528 | 122.4426 | 122.4564 | 0.18768 | -0.07782 | 122.3328 | 122.2504 | 0.022888 | 122.4472 | 122.3465 | 0.096131 | 0.004577 | 122.6257 | 122.4426 | 122.4014 | -0.25177 | 122.5433 | 122.525 | 122.4884 | -0.27008
1098.1875 | 122.7585 | -122.3877 | 0.13275 | -0.12268 | 0.018692 | 0.0042298 | 0.0042639 | -0.0062612 | -0.0063296 | -0.0041657 | -0.096359 | -0.0087093 | -0.00668 | -0.00026701 | 0.0013309 | -0.0080258 | 0.10986 | 0.19226 | 0.17395 | 0.13733 | 0.16022 | 0.045776 | -0.082397 | 0.16937 | 0.29755 | 0.11902 | 0.11902 | 0.09613 | -0.004578 | -0.07782 | 122.4335 | 122.3053 | 0.027466 | 122.58 | 122.525 | 0.21973 | -0.022888 | 122.3831 | 122.3099 | -0.013732 | 122.5571 | 122.5067 | 0.19684 | -0.036621 | 122.5479 | 122.4976 | 122.5616 | -0.21515 | 122.5067 | 122.4838 | 122.6852 | -0.21057
1099.8594 | 122.7676 | -122.4014 | 0.1236 | -0.17609 | 0.021683 | 0.0018798 | 0.0064001 | -0.002416 | 0.0022152 | -0.0030975 | -0.18791 | -0.0065731 | -0.0028348 | -0.00026701 | 0.0041079 | -0.012298 | 0.050354 | 0.064087 | 0.009155 | 0.050354 | 0.20599 | 0.009155 | -0.14648 | 0.050354 | 0.068665 | -0.045776 | 0.10986 | 0.082397 | -0.09613 | -0.14191 | 122.4106 | 122.2549 | 0.082398 | 122.4655 | 122.4518 | 0.19684 | -0.073242 | 122.3053 | 122.2595 | -0.013733 | 122.4518 | 122.3557 | 0.096131 | -0.041199 | 122.6074 | 122.4518 | 122.4106 | -0.27008 | 122.5113 | 122.4838 | 122.4701 | -0.2655
1101.5312 | 122.7081 | -122.3831 | 0.13733 | -0.099793 | 0.021683 | 0.0023072 | 0.0061865 | -0.0039114 | 0.0013608 | -0.0030975 | -0.11162 | -0.0087093 | -0.0036892 | 0.0010148 | 0.0038943 | -0.011444 | 0.045776 | 0.050354 | 0.004578 | 0.027466 | 0.15106 | -0.013733 | -0.16022 | 0.059509 | 0.041199 | -0.064087 | 0.082397 | 0.054932 | -0.09613 | -0.16937 | 122.3694 | 122.2229 | 0.013733 | 122.4335 | 122.4106 | 0.18768 | -0.091553 | 122.287 | 122.2137 | -0.054932 | 122.4426 | 122.319 | 0.10529 | -0.082397 | 122.5342 | 122.4289 | 122.3877 | -0.29755 | 122.4655 | 122.438 | 122.4243 | -0.3067
1103.2188 | 122.7448 | -122.3694 | 0.14191 | -0.038757 | 0.01442 | 0.0085022 | 0.0017005 | -0.0051932 | -0.0065434 | -0.0043793 | -0.012436 | -0.0087093 | -0.0090298 | 0.00037379 | 0.0028263 | -0.0095212 | 0.054932 | 0.11444 | 0.09613 | 0.07782 | 0.15106 | 0.036621 | -0.11444 | 0.16022 | 0.25635 | 0.086975 | 0.11902 | 0.10071 | -0.032043 | -0.073242 | 122.406 | 122.2549 | 0.009155 | 122.4838 | 122.4472 | 0.19226 | -0.086975 | 122.3373 | 122.2961 | -0.022888 | 122.5296 | 122.4564 | 0.16022 | -0.041199 | 122.5204 | 122.4243 | 122.4655 | -0.25635 | 122.4884 | 122.4701 | 122.6257 | -0.21515
1104.9375 | 122.7448 | -122.3648 | 0.14191 | -0.10742 | 0.018265 | 0.0050842 | 0.0051183 | -0.0069022 | -0.0035526 | -0.0073701 | -0.11162 | -0.0084957 | -0.0047574 | -0.0030442 | 0.0017581 | -0.007385 | 0.15564 | 0.20142 | 0.17853 | 0.11444 | 0.16937 | 0.064087 | -0.073242 | 0.17853 | 0.3067 | 0.1236 | 0.1236 | 0.10071 | -0.009155 | -0.07782 | 122.4289 | 122.2916 | 0.027466 | 122.5662 | 122.4792 | 0.18768 | 0.013733 | 122.3557 | 122.287 | -0.018311 | 122.5433 | 122.4884 | 0.20142 | -0.041199 | 122.5342 | 122.5204 | 122.5433 | -0.21515 | 122.4884 | 122.4655 | 122.6715 | -0.21973
1106.6094 | 122.7356 | -122.3969 | 0.13733 | -0.1532 | 0.017197 | 0.002948 | 0.0083227 | -0.0069022 | -0.0054752 | -0.0058747 | -0.14977 | -0.0080685 | -0.0028348 | -0.00069421 | 0.0021853 | -0.0097348 | 0.15106 | 0.19226 | 0.16937 | 0.13275 | 0.18768 | 0.054932 | -0.068665 | 0.1831 | 0.31586 | 0.10986 | 0.11902 | 0.10071 | -0.004578 | -0.07782 | 122.4518 | 122.3282 | 0.050354 | 122.5891 | 122.5296 | 0.20142 | 0.013733 | 122.3923 | 122.319 | -0.01831 | 122.58 | 122.5067 | 0.18768 | -0.036621 | 122.5845 | 122.5479 | 122.5662 | -0.20599 | 122.5159 | 122.4976 | 122.7127 | -0.21515
1108.2812 | 122.7676 | -122.3831 | 0.14191 | -0.25238 | 0.022324 | 0.0050842 | 0.0072547 | -0.0060476 | 0.00029262 | -0.0041657 | -0.23369 | -0.0082821 | -0.0039028 | 0.00080099 | 0.0026125 | -0.010376 | 0.09613 | 0.073242 | 0.027466 | 0.07782 | 0.23804 | 0.032043 | -0.091553 | 0.050354 | 0.082397 | -0.059509 | 0.16479 | 0.14191 | -0.059509 | -0.1236 | 122.4152 | 122.2916 | 0.09613 | 122.4564 | 122.4609 | 0.16937 | -0.045777 | 122.3236 | 122.2595 | 0.022888 | 122.4335 | 122.3236 | 0.064087 | 0 | 122.6212 | 122.4792 | 122.4106 | -0.23346 | 122.5479 | 122.525 | 122.4655 | -0.2655
1109.9844 | 122.6715 | -122.4197 | 0.16479 | 0.11383 | 0.017838 | 0.0038024 | 0.0010595 | -0.0045522 | 7.902e-05 | -0.0052337 | 0.079117 | -0.0074277 | -0.0043302 | 0.001442 | 0.0041079 | -0.010589 | -0.054932 | -0.068665 | -0.10986 | -0.073242 | 0.09613 | -0.091553 | -0.21973 | 0.009155 | -0.12817 | -0.12817 | 0.064087 | 0.041199 | -0.12817 | -0.19226 | 122.3282 | 122.2 | -0.068665 | 122.3511 | 122.3465 | 0.14649 | -0.21973 | 122.2916 | 122.2275 | -0.10071 | 122.4289 | 122.2916 | 0.064087 | -0.1236 | 122.5159 | 122.3648 | 122.3099 | -0.38452 | 122.4838 | 122.4609 | 122.2916 | -0.35706
1111.6562 | 122.6349 | -122.438 | 0.16937 | 0.090942 | 0.018478 | 0.0035888 | -0.00022208 | -0.0045522 | 0.005206 | -0.0016021 | -0.027695 | -0.0061459 | -0.004971 | -5.3406e-05 | 0.0049625 | -0.009094 | -0.054932 | -0.07782 | -0.12817 | -0.064087 | 0.11902 | -0.068665 | -0.21057 | -0.050354 | -0.13275 | -0.17853 | 0.073242 | 0.054932 | -0.14648 | -0.20599 | 122.3694 | 122.2275 | -0.050354 | 122.3602 | 122.374 | 0.14648 | -0.22431 | 122.2916 | 122.2321 | -0.096131 | 122.3877 | 122.2595 | 0.027466 | -0.11444 | 122.5571 | 122.3831 | 122.3099 | -0.37994 | 122.5113 | 122.493 | 122.3053 | -0.37537
1113.3438 | 122.6349 | -122.438 | 0.19226 | -0.00061023 | 0.021256 | 0.0020936 | 0.0034093 | -0.0056204 | 0.0028562 | -0.0016021 | 0.010452 | -0.0061459 | -0.003262 | 0.00037379 | 0.0060305 | -0.0080258 | -0.059509 | -0.054932 | -0.091553 | -0.050354 | 0.11902 | -0.054932 | -0.19226 | -0.032043 | -0.086975 | -0.16937 | 0.082397 | 0.050354 | -0.13275 | -0.21515 | 122.3831 | 122.2458 | -0.073242 | 122.3831 | 122.3877 | 0.14191 | -0.25177 | 122.3053 | 122.2229 | -0.10986 | 122.406 | 122.2687 | 0.045776 | -0.14191 | 122.5571 | 122.3785 | 122.3465 | -0.38452 | 122.5204 | 122.4884 | 122.3511 | -0.40741
1115.0312 | 122.6715 | -122.406 | 0.17395 | 0.1062 | 0.019547 | 0.0042298 | 0.0029821 | -0.0043386 | 0.00071982 | -0.0013885 | 0.094375 | -0.0080685 | -0.0062528 | -0.00090781 | 0.0032535 | -0.0075986 | -0.068665 | -0.086975 | -0.11902 | -0.082397 | 0.09613 | -0.091553 | -0.22888 | -0.022888 | -0.10986 | -0.13275 | 0.073242 | 0.054932 | -0.12817 | -0.1831 | 122.3145 | 122.1771 | -0.07782 | 122.319 | 122.3236 | 0.14649 | -0.24261 | 122.2778 | 122.2229 | -0.10071 | 122.3831 | 122.2733 | 0.050354 | -0.11902 | 122.5021 | 122.3373 | 122.287 | -0.40283 | 122.4792 | 122.4609 | 122.2961 | -0.35706
1116.7031 | 122.7448 | -122.3923 | 0.15106 | -0.092163 | 0.018692 | 0.0033752 | 0.0051183 | -0.001348 | 0.00050622 | -0.0041657 | -0.081101 | -0.0040097 | -0.0021938 | 0.00058739 | 0.0030399 | -0.0078122 | 0.068665 | 0.050354 | 0.004578 | 0.022888 | 0.16479 | -0.013733 | -0.15564 | 0.054932 | 0.045776 | -0.054932 | 0.091553 | 0.064087 | -0.09613 | -0.15564 | 122.3785 | 122.2366 | 0.013733 | 122.4426 | 122.4152 | 0.17853 | -0.082397 | 122.2961 | 122.2366 | -0.059509 | 122.4472 | 122.3373 | 0.10071 | -0.086975 | 122.5571 | 122.4609 | 122.3969 | -0.3067 | 122.4838 | 122.4564 | 122.438 | -0.3067
1118.3906 | 122.7219 | -122.4106 | 0.13733 | -0.19897 | 0.020187 | 0.0059388 | 0.010032 | -0.0030568 | -0.005048 | -0.0050201 | -0.14214 | -0.0080685 | -0.0041164 | -0.0013352 | -0.0012327 | -0.0080258 | 0.10529 | 0.16022 | 0.14191 | 0.12817 | 0.16937 | 0.07782 | -0.064087 | 0.1236 | 0.27924 | 0.068665 | 0.10529 | 0.09613 | -0.027466 | -0.086975 | 122.4884 | 122.3465 | 0.032044 | 122.5708 | 122.5388 | 0.19226 | -0.032043 | 122.3831 | 122.3236 | -0.032043 | 122.5342 | 122.4792 | 0.15564 | -0.041199 | 122.58 | 122.5159 | 122.5525 | -0.20142 | 122.5159 | 122.5067 | 122.6898 | -0.2243
1120.0781 | 122.6212 | -122.4472 | 0.18768 | 0.1062 | 0.018478 | 0.0040162 | 0.0040503 | -0.0064748 | -0.0035526 | -0.0052337 | 0.21645 | -0.0070003 | -0.004971 | -0.0013352 | -0.00016447 | -0.0088804 | 0.018311 | 0.050354 | 0.032043 | 0.004578 | 0.059509 | -0.036621 | -0.17853 | 0.07782 | 0.086975 | -0.013733 | 0.032043 | 0.041199 | -0.086975 | -0.15564 | 122.4106 | 122.2687 | -0.12817 | 122.4976 | 122.4518 | 0.18311 | -0.16937 | 122.3602 | 122.2916 | -0.15564 | 122.525 | 122.4335 | 0.14191 | -0.14648 | 122.5067 | 122.4655 | 122.4792 | -0.36621 | 122.4792 | 122.4884 | 122.5342 | -0.34332
1121.75 | 122.6166 | -122.4335 | 0.16937 | 0.1062 | 0.015701 | 0.0018798 | 0.0012731 | -0.0047658 | -0.004407 | -0.0050201 | 0.17067 | -0.0099911 | -0.0051846 | -0.0034714 | 0.0045351 | -0.0088804 | 0.036621 | 0.045776 | 0.027466 | -0.013733 | 0.068665 | -0.041199 | -0.17853 | 0.073242 | 0.10071 | -0.004578 | 0.041199 | 0.022888 | -0.07782 | -0.14648 | 122.3923 | 122.2549 | -0.10071 | 122.4792 | 122.4197 | 0.16479 | -0.13275 | 122.3557 | 122.287 | -0.12817 | 122.5067 | 122.4289 | 0.14191 | -0.14649 | 122.5021 | 122.4701 | 122.4609 | -0.3479 | 122.4747 | 122.4564 | 122.5342 | -0.31586
1123.4219 | 122.7127 | -122.3923 | 0.15564 | -0.24475 | 0.021683 | 0.0023072 | 0.0066137 | -0.0054068 | -0.0024844 | -0.0067291 | -0.17265 | -0.0070003 | -0.0039028 | 0.00016019 | 0.0021853 | -0.01123 | 0.12817 | 0.10529 | 0.086975 | 0.086975 | 0.2243 | 0.054932 | -0.086975 | 0.059509 | 0.13733 | -0.032043 | 0.17853 | 0.14648 | -0.045776 | -0.11444 | 122.4472 | 122.3053 | 0.068664 | 122.4976 | 122.4792 | 0.17395 | -0.027466 | 122.3465 | 122.2778 | 0.022888 | 122.4518 | 122.3602 | 0.082398 | -0.009156 | 122.6166 | 122.5204 | 122.4792 | -0.24261 | 122.5708 | 122.5388 | 122.5296 | -0.27008
1125.1094 | 122.6532 | -122.4289 | 0.18768 | 0.19012 | 0.016769 | 0.0027344 | 0.00084592 | -0.0034842 | -0.0037662 | -0.0041657 | 0.18593 | -0.0093503 | -0.0073208 | -0.0030442 | 0.0023989 | -0.0097348 | 0.036621 | -0.013733 | 0.009155 | -0.022888 | 0.027466 | -0.054932 | -0.21057 | 0.091553 | 0.059509 | -0.009155 | 0.018311 | -0.013733 | -0.13275 | -0.18768 | 122.374 | 122.2183 | -0.16022 | 122.4152 | 122.406 | 0.18768 | -0.15106 | 122.2961 | 122.2412 | -0.16937 | 122.5204 | 122.4197 | 0.17853 | -0.20142 | 122.4564 | 122.4655 | 122.438 | -0.39825 | 122.4472 | 122.4152 | 122.4884 | -0.37537
1126.7969 | 122.7493 | -122.3694 | 0.14648 | -0.00061023 | 0.018051 | 0.0050842 | 0.0040503 | -0.0049796 | -0.0065434 | -0.0058747 | 0.03334 | -0.0080685 | -0.0041164 | -0.0024032 | 0.0015445 | -0.0088804 | 0.07782 | 0.054932 | 0.073242 | 0.045776 | 0.15106 | 0.009155 | -0.13275 | 0.1236 | 0.18768 | 0.064087 | 0.09613 | 0.086975 | -0.054932 | -0.09613 | 122.3785 | 122.2366 | 0.004578 | 122.4243 | 122.4152 | 0.17853 | -0.068664 | 122.3145 | 122.2733 | -0.050354 | 122.493 | 122.4335 | 0.16022 | -0.059509 | 122.5204 | 122.4472 | 122.4426 | -0.27924 | 122.4655 | 122.4564 | 122.5571 | -0.24261
1128.4688 | 122.644 | -122.4197 | 0.17853 | 0.052795 | 0.015488 | 0.0048706 | 0.0040503 | -0.0056204 | -0.0035526 | -0.0054475 | 0.071487 | -0.0089229 | -0.006039 | -0.00026701 | 0.0015445 | -0.01123 | 0.059509 | 0.036621 | 0.032043 | 0.013733 | 0.10071 | -0.018311 | -0.16022 | 0.09613 | 0.10071 | 0 | 0.07782 | 0.059509 | -0.064087 | -0.12817 | 122.4014 | 122.2595 | -0.07782 | 122.4564 | 122.4335 | 0.17395 | -0.11902 | 122.3557 | 122.2916 | -0.10071 | 122.5159 | 122.4197 | 0.12817 | -0.11902 | 122.5204 | 122.4792 | 122.4518 | -0.33874 | 122.4976 | 122.4792 | 122.5204 | -0.3067
1130.1562 | 122.7859 | -122.3648 | 0.15564 | -0.13031 | 0.018692 | 0.0018798 | 0.0025549 | -0.0064748 | 0.003497 | -0.0041657 | -0.17265 | -0.0089229 | -0.006039 | -0.0015488 | 0.0075259 | -0.011444 | 0.091553 | 0.032043 | 0.004578 | 0.041199 | 0.17853 | 0 | -0.15564 | 0.064087 | 0.036621 | -0.068665 | 0.10071 | 0.091553 | -0.091553 | -0.15564 | 122.3648 | 122.2092 | 0.022888 | 122.3969 | 122.406 | 0.19684 | -0.064087 | 122.2733 | 122.2092 | -0.054932 | 122.4289 | 122.2961 | 0.086975 | -0.064087 | 122.5433 | 122.4564 | 122.3694 | -0.31128 | 122.4655 | 122.4564 | 122.4014 | -0.31128
1131.8281 | 122.6532 | -122.4472 | 0.17395 | 0.12146 | 0.018692 | 0.0033752 | 0.0057593 | -0.0056204 | -0.0014164 | -0.0030975 | 0.16304 | -0.0074277 | -0.0030484 | 0.00016019 | 0.0015445 | -0.007385 | 0.050354 | 0.045776 | 0.059509 | 0.013733 | 0.073242 | -0.054932 | -0.17853 | 0.086975 | 0.068665 | -0.022888 | 0.036621 | 0.013733 | -0.10529 | -0.16022 | 122.3923 | 122.2687 | -0.10071 | 122.493 | 122.4609 | 0.19226 | -0.1236 | 122.3419 | 122.287 | -0.13733 | 122.5342 | 122.4243 | 0.13733 | -0.16022 | 122.5204 | 122.4976 | 122.5067 | -0.35248 | 122.4838 | 122.4609 | 122.5159 | -0.33417
1133.5 | 122.6944 | -122.4289 | 0.17853 | 0.20538 | 0.018051 | 0.0014526 | 0.0040503 | -0.0045522 | -0.00034818 | -0.0033111 | 0.102 | -0.0078549 | -0.006039 | -0.00048061 | 0.0045351 | -0.009094 | 0.032043 | 0 | -0.022888 | -0.004578 | 0.041199 | -0.045776 | -0.21973 | 0.091553 | 0.013733 | -0.041199 | 0.032043 | -0.004578 | -0.09613 | -0.15564 | 122.3831 | 122.2092 | -0.13733 | 122.4289 | 122.4243 | 0.21515 | -0.14648 | 122.3328 | 122.2733 | -0.14648 | 122.5204 | 122.3877 | 0.11444 | -0.18311 | 122.4701 | 122.4609 | 122.406 | -0.39826 | 122.4609 | 122.4243 | 122.4426 | -0.33417
1135.1719 | 122.7219 | -122.406 | 0.16937 | -0.076904 | 0.018478 | 0.0018798 | 0.0053321 | -0.0049796 | 0.0032834 | -0.0024567 | -0.11925 | -0.0072141 | -0.0030484 | -0.00026701 | 0.0051761 | -0.0093076 | 0.07782 | 0.054932 | 0 | 0.018311 | 0.16479 | -0.022888 | -0.16479 | 0.059509 | 0.022888 | -0.073242 | 0.086975 | 0.059509 | -0.10529 | -0.16937 | 122.3831 | 122.2412 | -0.004578 | 122.4609 | 122.4243 | 0.18311 | -0.091553 | 122.3007 | 122.2366 | -0.082398 | 122.4655 | 122.3328 | 0.096131 | -0.10986 | 122.5708 | 122.4838 | 122.406 | -0.33417 | 122.493 | 122.4655 | 122.4289 | -0.33875
1136.8438 | 122.731 | -122.406 | 0.16937 | -0.22949 | 0.020187 | 0.0027344 | 0.010245 | -0.0045522 | -0.003339 | -0.0048065 | -0.13451 | -0.0097775 | -0.0030484 | -5.3406e-05 | 0.00090353 | -0.0093076 | 0.07782 | 0.091553 | 0.073242 | 0.064087 | 0.24261 | 0.059509 | -0.091553 | 0.073242 | 0.14648 | -0.027466 | 0.17853 | 0.13733 | -0.045776 | -0.10986 | 122.4655 | 122.3145 | 0.073242 | 122.4976 | 122.4701 | 0.15564 | -0.091553 | 122.3602 | 122.2961 | 0.009155 | 122.4792 | 122.3785 | 0.082397 | -0.032044 | 122.6486 | 122.4838 | 122.4792 | -0.26093 | 122.5845 | 122.5433 | 122.5525 | -0.27924
1138.5312 | 122.7585 | -122.406 | 0.17853 | -0.099793 | 0.021896 | 0.0033752 | 0.0044775 | -0.0034842 | 0.0041378 | -0.0041657 | -0.15739 | -0.0055051 | 0.00036957 | 0.001442 | 0.0045351 | -0.0099484 | 0.064087 | 0.050354 | -0.009155 | 0.018311 | 0.15564 | -0.027466 | -0.16022 | 0.059509 | 0.018311 | -0.073242 | 0.086975 | 0.068665 | -0.091553 | -0.15106 | 122.3785 | 122.2458 | -0.022888 | 122.4564 | 122.4243 | 0.17853 | -0.11444 | 122.3145 | 122.2549 | -0.091553 | 122.4655 | 122.3328 | 0.07782 | -0.10986 | 122.5616 | 122.4701 | 122.3969 | -0.33874 | 122.493 | 122.4747 | 122.4243 | -0.32959
1140.2031 | 122.7585 | -122.4106 | 0.15564 | -0.11505 | 0.019119 | 0.0027344 | 0.0029821 | -0.005834 | 0.0037106 | -0.0028839 | -0.15739 | -0.0082821 | -0.0051846 | 0.00037379 | 0.0049625 | -0.010803 | 0.041199 | 0.041199 | -0.004578 | 0.022888 | 0.16022 | -0.013733 | -0.15564 | 0.064087 | 0.064087 | -0.064087 | 0.11444 | 0.07782 | -0.086975 | -0.15106 | 122.3969 | 122.2549 | 0.004577 | 122.4518 | 122.4335 | 0.17853 | -0.11444 | 122.3236 | 122.2595 | -0.041199 | 122.4747 | 122.3465 | 0.086975 | -0.07782 | 122.5708 | 122.4518 | 122.406 | -0.31128 | 122.525 | 122.4884 | 122.4747 | -0.3067
1141.8906 | 122.7768 | -122.4243 | 0.14648 | -0.24475 | 0.019333 | 0.0035888 | 0.0096045 | -0.0060476 | -0.0029118 | -0.0041657 | -0.24132 | -0.0072141 | -0.00091223 | 0.00016019 | -0.00037807 | -0.009094 | 0.050354 | 0.064087 | 0.036621 | 0.059509 | 0.25177 | 0.032043 | -0.10071 | 0.059509 | 0.11902 | -0.032043 | 0.18768 | 0.15106 | -0.054932 | -0.10071 | 122.4564 | 122.3236 | 0.10529 | 122.4884 | 122.4838 | 0.16022 | -0.09613 | 122.3694 | 122.3236 | 0.041199 | 122.4838 | 122.3923 | 0.068665 | 0.004578 | 122.6761 | 122.4747 | 122.4609 | -0.24719 | 122.612 | 122.5754 | 122.5433 | -0.24719
1143.5625 | 122.7264 | -122.3877 | 0.14648 | -0.2066 | 0.017838 | 0.0044434 | 0.0059729 | -0.0045522 | -0.0059024 | -0.0075837 | -0.11925 | -0.0084957 | -0.0062528 | -0.0017624 | -0.00059167 | -0.008453 | 0.13733 | 0.20599 | 0.16937 | 0.13275 | 0.16937 | 0.064087 | -0.07782 | 0.15106 | 0.28381 | 0.091553 | 0.1236 | 0.091553 | -0.022888 | -0.086975 | 122.4518 | 122.3099 | 0.022889 | 122.5937 | 122.5204 | 0.21057 | -0.009155 | 122.3648 | 122.3007 | -0.022888 | 122.5388 | 122.4792 | 0.17853 | -0.054931 | 122.5571 | 122.525 | 122.5571 | -0.2243 | 122.5113 | 122.4792 | 122.6715 | -0.23346
1145.2344 | 122.7814 | -122.374 | 0.14648 | -0.031128 | 0.016769 | 0.0050842 | 0.0040503 | -0.0051932 | -0.006116 | -0.0052337 | -0.042954 | -0.0087093 | -0.0047574 | -0.0021896 | 0.0028263 | -0.0069578 | 0.091553 | 0.1236 | 0.10071 | 0.082397 | 0.16479 | 0.041199 | -0.09613 | 0.16937 | 0.25635 | 0.10986 | 0.13733 | 0.10986 | -0.041199 | -0.07782 | 122.4152 | 122.2778 | 0.018311 | 122.4976 | 122.4564 | 0.17853 | -0.054931 | 122.3328 | 122.2961 | -0.009155 | 122.5433 | 122.4838 | 0.18768 | -0.036621 | 122.5388 | 122.4655 | 122.4747 | -0.24261 | 122.5113 | 122.4838 | 122.6303 | -0.2243
1146.9219 | 122.7356 | -122.406 | 0.15564 | -0.16846 | 0.01976 | 0.0065796 | 0.0049047 | -0.001348 | -0.004407 | -0.0060883 | -0.13451 | -0.0091367 | -0.0030484 | -0.0017624 | 0.00068993 | -0.011017 | 0.16022 | 0.20599 | 0.1831 | 0.13733 | 0.18768 | 0.054932 | -0.059509 | 0.16022 | 0.28381 | 0.09613 | 0.12817 | 0.11444 | -0.013733 | -0.082397 | 122.4609 | 122.3465 | 0.032043 | 122.612 | 122.5433 | 0.19684 | 0.004577 | 122.3923 | 122.3236 | -0.027466 | 122.5662 | 122.5021 | 0.17853 | -0.041199 | 122.5937 | 122.5662 | 122.5891 | -0.21515 | 122.5342 | 122.5204 | 122.6898 | -0.23804
1148.5938 | 122.7585 | -122.3831 | 0.16479 | -0.00061023 | 0.020401 | 0.0052978 | 0.0057593 | -0.0028432 | -0.0046206 | -0.0073701 | 0.010452 | -0.0093503 | -0.0030484 | -0.00069421 | 0.00068993 | -0.010376 | 0.027466 | 0.054932 | 0.059509 | 0.050354 | 0.17395 | 0.022888 | -0.14191 | 0.10986 | 0.17395 | 0.036621 | 0.11444 | 0.064087 | -0.050354 | -0.11902 | 122.406 | 122.2412 | 0.009155 | 122.438 | 122.4335 | 0.19226 | -0.13733 | 122.3328 | 122.2641 | -0.050354 | 122.493 | 122.4197 | 0.15564 | -0.10071 | 122.5571 | 122.4106 | 122.4426 | -0.3067 | 122.4976 | 122.4472 | 122.5571 | -0.28381
1150.2969 | 122.6761 | -122.438 | 0.19684 | -0.046387 | 0.020615 | 0.0020936 | -0.00043588 | -0.0022024 | 0.005206 | -0.0043793 | -0.10399 | -0.0055051 | -0.0051846 | 0.001442 | 0.0068851 | -0.01123 | 0.050354 | 0.004578 | -0.022888 | 0.004578 | 0.15106 | -0.013733 | -0.17853 | 0.004578 | -0.059509 | -0.11902 | 0.082397 | 0.050354 | -0.12817 | -0.1831 | 122.4243 | 122.2595 | -0.045776 | 122.4426 | 122.4426 | 0.18311 | -0.14648 | 122.3099 | 122.2549 | -0.11444 | 122.4426 | 122.319 | 0.064086 | -0.14648 | 122.5891 | 122.4884 | 122.4152 | -0.37537 | 122.5204 | 122.4884 | 122.3785 | -0.37994
1152.0156 | 122.7036 | -122.4335 | 0.17853 | 0.12909 | 0.020615 | 0.0033752 | 0.00041872 | -0.0043386 | 0.0022152 | -0.0024567 | 0.094375 | -0.0063595 | -0.0053982 | 0.00058739 | 0.0066715 | -0.009094 | -0.054932 | -0.086975 | -0.10529 | -0.082397 | 0.10986 | -0.091553 | -0.23346 | 0.004578 | -0.10986 | -0.12817 | 0.082397 | 0.041199 | -0.14191 | -0.17395 | 122.3419 | 122.2 | -0.068665 | 122.3465 | 122.3511 | 0.15106 | -0.23346 | 122.2916 | 122.2595 | -0.096131 | 122.438 | 122.3053 | 0.045776 | -0.13733 | 122.5433 | 122.3785 | 122.3282 | -0.41199 | 122.5159 | 122.4747 | 122.3236 | -0.35248
1153.6875 | 122.6852 | -122.4335 | 0.17853 | 0.11383 | 0.019119 | 0.0040162 | 0.0025549 | -0.0032706 | 0.0022152 | -0.0037385 | 0.056228 | -0.0055051 | -0.0047574 | -0.00026701 | 0.0038943 | -0.010589 | -0.054932 | -0.10071 | -0.11444 | -0.082397 | 0.10986 | -0.07782 | -0.22888 | -0.013733 | -0.11902 | -0.15106 | 0.091553 | 0.041199 | -0.16022 | -0.19684 | 122.3557 | 122.2046 | -0.068665 | 122.3328 | 122.3511 | 0.14649 | -0.23346 | 122.2733 | 122.2366 | -0.086975 | 122.4197 | 122.2824 | 0.045776 | -0.13733 | 122.5433 | 122.3785 | 122.319 | -0.40741 | 122.525 | 122.4747 | 122.3145 | -0.37537
1155.375 | 122.644 | -122.4518 | 0.18768 | 0.098572 | 0.016342 | 0.006366 | 0.0040503 | -0.0081838 | -0.0031254 | -0.0052337 | 0.20119 | -0.0084957 | -0.0047574 | -0.0015488 | 0.0021853 | -0.0075986 | 0.013733 | 0.050354 | 0.045776 | 0 | 0.059509 | -0.041199 | -0.17853 | 0.073242 | 0.073242 | -0.027466 | 0.041199 | 0.013733 | -0.10529 | -0.16479 | 122.4106 | 122.2733 | -0.12817 | 122.5021 | 122.4518 | 0.17853 | -0.17395 | 122.3465 | 122.287 | -0.14648 | 122.525 | 122.4243 | 0.13733 | -0.17395 | 122.5113 | 122.4655 | 122.4976 | -0.36621 | 122.493 | 122.4655 | 122.525 | -0.35248
1157.0469 | 122.7036 | -122.438 | 0.1831 | 0.15198 | 0.018051 | 0.0059388 | 0.00084592 | -0.0043386 | 0.0022152 | -0.0037385 | 0.18593 | -0.0042233 | -0.0062528 | 0.00080099 | 0.0060305 | -0.0071714 | -0.036621 | -0.086975 | -0.091553 | -0.082397 | 0.09613 | -0.068665 | -0.21057 | 0.018311 | -0.050354 | -0.086975 | 0.054932 | 0.027466 | -0.13275 | -0.19226 | 122.3694 | 122.2275 | -0.086975 | 122.3511 | 122.3557 | 0.12817 | -0.21973 | 122.3053 | 122.2458 | -0.12817 | 122.4564 | 122.3511 | 0.10529 | -0.15564 | 122.5342 | 122.4014 | 122.3465 | -0.39368 | 122.493 | 122.4655 | 122.3877 | -0.37537
1158.7188 | 122.6532 | -122.4609 | 0.18768 | 0.052795 | 0.021469 | 0.0038024 | 0.0031957 | -0.0047658 | 0.0032834 | -0.0013885 | -0.0048066 | -0.0059323 | -0.0073208 | 0.00080099 | 0.0079531 | -0.0080258 | -0.022888 | -0.086975 | -0.086975 | -0.054932 | 0.1236 | -0.059509 | -0.21973 | -0.041199 | -0.091553 | -0.15564 | 0.073242 | 0.045776 | -0.12817 | -0.20142 | 122.4014 | 122.2412 | -0.064087 | 122.374 | 122.406 | 0.16479 | -0.21057 | 122.3328 | 122.2595 | -0.11444 | 122.4197 | 122.3053 | 0.045776 | -0.14191 | 122.5845 | 122.438 | 122.374 | -0.40741 | 122.5342 | 122.5067 | 122.3694 | -0.3891
1160.4062 | 122.7997 | -122.438 | 0.14191 | -0.23712 | 0.020401 | 0.0035888 | 0.0096045 | -0.0049796 | -0.0029118 | -0.0041657 | -0.22606 | -0.0080685 | -0.0058254 | -5.3406e-05 | 0.00026273 | -0.0078122 | 0.064087 | 0.073242 | 0.045776 | 0.054932 | 0.27008 | 0.050354 | -0.10529 | 0.041199 | 0.10986 | -0.041199 | 0.17395 | 0.16022 | -0.045776 | -0.10529 | 122.4884 | 122.3328 | 0.12817 | 122.5113 | 122.493 | 0.16022 | -0.07782 | 122.3923 | 122.3328 | 0.032043 | 122.4792 | 122.3969 | 0.064087 | 0.01831 | 122.7081 | 122.5021 | 122.4838 | -0.24719 | 122.612 | 122.5983 | 122.5479 | -0.24719
1162.0938 | 122.7127 | -122.4335 | 0.18768 | 0.19012 | 0.018478 | 0.0031616 | 0.0040503 | -0.0056204 | -0.00098918 | -0.0043793 | 0.16304 | -0.0052915 | -0.0047574 | 0.0012284 | 0.0053897 | -0.0088804 | 0.041199 | 0.009155 | 0.004578 | 0 | 0.054932 | -0.07782 | -0.20142 | 0.068665 | 0.036621 | -0.032043 | 0.009155 | -0.018311 | -0.10529 | -0.16937 | 122.3557 | 122.2321 | -0.13275 | 122.4426 | 122.4335 | 0.20142 | -0.14648 | 122.3282 | 122.2641 | -0.17853 | 122.5021 | 122.4014 | 0.13733 | -0.20599 | 122.4884 | 122.4747 | 122.438 | -0.3891 | 122.4426 | 122.4152 | 122.4701 | -0.35706
1163.7656 | 122.6944 | -122.4518 | 0.17395 | 0.14435 | 0.017838 | 0.0052978 | 0.0029821 | -0.0056204 | -0.00098918 | -0.0033111 | 0.19356 | -0.0076413 | -0.0058254 | -0.00090781 | 0.0056033 | -0.008453 | 0.027466 | 0.004578 | 0.009155 | -0.013733 | 0.036621 | -0.064087 | -0.20599 | 0.050354 | 0.032043 | -0.032043 | 0.009155 | -0.009155 | -0.11902 | -0.17395 | 122.3877 | 122.2458 | -0.13733 | 122.4564 | 122.438 | 0.19226 | -0.14648 | 122.3328 | 122.2778 | -0.16479 | 122.5021 | 122.4197 | 0.14191 | -0.1831 | 122.4884 | 122.4792 | 122.4609 | -0.37994 | 122.4609 | 122.4426 | 122.4838 | -0.3479
1165.5 | 122.7448 | -122.4426 | 0.14648 | -0.17609 | 0.019547 | 0.0044434 | 0.0081091 | -0.0047658 | -0.003339 | -0.0054475 | -0.14977 | -0.0097775 | -0.0047574 | -0.00090781 | -0.0012327 | -0.010376 | 0.13275 | 0.15564 | 0.15564 | 0.11902 | 0.16479 | 0.073242 | -0.091553 | 0.14648 | 0.27008 | 0.073242 | 0.13275 | 0.10071 | -0.009155 | -0.082397 | 122.5159 | 122.3511 | 0.018311 | 122.5983 | 122.5616 | 0.21057 | -0.013733 | 122.4335 | 122.3602 | -0.013733 | 122.5891 | 122.5159 | 0.15564 | -0.045776 | 122.6074 | 122.5754 | 122.5983 | -0.23804 | 122.5754 | 122.5433 | 122.7127 | -0.22888
1167.1719 | 122.699 | -122.4747 | 0.19226 | 0.098572 | 0.021896 | 0.0048706 | 0.00063232 | -0.0051932 | 0.001788 | -0.0026703 | 0.063858 | -0.0072141 | -0.0047574 | -0.00048061 | 0.0053897 | -0.010803 | -0.050354 | -0.1236 | -0.12817 | -0.07782 | 0.10529 | -0.082397 | -0.24719 | -0.036621 | -0.13733 | -0.15106 | 0.064087 | 0.054932 | -0.15564 | -0.21057 | 122.3923 | 122.2275 | -0.086975 | 122.3511 | 122.3969 | 0.16937 | -0.24261 | 122.319 | 122.2641 | -0.12817 | 122.438 | 122.3236 | 0.059509 | -0.13733 | 122.58 | 122.4243 | 122.3465 | -0.43945 | 122.5388 | 122.5296 | 122.3373 | -0.40283
1168.8438 | 122.7219 | -122.4609 | 0.15564 | 0.15198 | 0.019547 | 0.0020936 | 0.0038367 | -0.0047658 | 0.0011472 | -0.0013885 | 0.15541 | -0.0072141 | -0.0053982 | -0.0015488 | 0.0053897 | -0.009094 | -0.022888 | -0.07782 | -0.082397 | -0.068665 | 0.073242 | -0.073242 | -0.2243 | 0.045776 | -0.027466 | -0.068665 | 0.041199 | 0.004578 | -0.11902 | -0.16479 | 122.3877 | 122.2366 | -0.082398 | 122.3831 | 122.3923 | 0.15564 | -0.17853 | 122.3419 | 122.2961 | -0.11444 | 122.5067 | 122.3923 | 0.09613 | -0.15106 | 122.5342 | 122.438 | 122.3785 | -0.37994 | 122.5021 | 122.4655 | 122.4335 | -0.32044
1170.5156 | 122.6761 | -122.4747 | 0.18768 | -0.061646 | 0.020401 | 0.0044434 | 0.0046911 | -0.0073294 | 0.0013608 | -0.0041657 | -0.050583 | -0.0052915 | -0.0045438 | -0.0013352 | 0.0049625 | -0.010162 | 0.068665 | 0 | -0.022888 | -0.009155 | 0.13275 | -0.036621 | -0.1831 | 0.009155 | -0.050354 | -0.11902 | 0.082397 | 0.068665 | -0.11902 | -0.18768 | 122.438 | 122.2916 | -0.054932 | 122.4747 | 122.4655 | 0.17395 | -0.11902 | 122.3557 | 122.287 | -0.10529 | 122.4838 | 122.3557 | 0.068664 | -0.11902 | 122.6074 | 122.5433 | 122.4518 | -0.37079 | 122.5571 | 122.5433 | 122.4243 | -0.37537
1172.2031 | 122.8088 | -122.4609 | 0.13275 | -0.19135 | 0.020401 | 0.0050842 | 0.0051183 | -0.0056204 | 0.00050622 | -0.0013885 | -0.16502 | -0.0089229 | -0.0039028 | -0.00069421 | 0.0060305 | -0.010162 | 0.07782 | 0.050354 | 0.009155 | 0.068665 | 0.21515 | 0.032043 | -0.10986 | 0.032043 | 0.054932 | -0.045776 | 0.13733 | 0.10529 | -0.11444 | -0.15106 | 122.493 | 122.3511 | 0.082398 | 122.5113 | 122.5296 | 0.17853 | -0.054931 | 122.3465 | 122.3099 | 0.004578 | 122.493 | 122.4152 | 0.10529 | -0.027465 | 122.6761 | 122.5388 | 122.4701 | -0.24261 | 122.5983 | 122.5662 | 122.5159 | -0.28381
1173.8906 | 122.6852 | -122.4884 | 0.1831 | 0.022278 | 0.019119 | 0.0038024 | 0.0027685 | -0.0064748 | 0.0028562 | -0.0026703 | 0.071487 | -0.0057187 | -0.0053982 | -0.0011216 | 0.0045351 | -0.0086666 | -0.013733 | -0.054932 | -0.068665 | -0.045776 | 0.13275 | -0.050354 | -0.19684 | -0.054932 | -0.082397 | -0.15564 | 0.082397 | 0.064087 | -0.14191 | -0.20142 | 122.438 | 122.2916 | -0.050354 | 122.4335 | 122.4426 | 0.15106 | -0.19684 | 122.3465 | 122.287 | -0.10071 | 122.4335 | 122.3328 | 0.045776 | -0.11902 | 122.6212 | 122.4747 | 122.4197 | -0.37994 | 122.5708 | 122.5525 | 122.406 | -0.38452
1175.5625 | 122.7219 | -122.4564 | 0.16022 | 0.11383 | 0.017197 | 0.0040162 | 0.0055457 | -0.0056204 | -0.0035526 | -0.0039521 | 0.17067 | -0.0080685 | -0.0058254 | 0.00037379 | 0.0066715 | -0.0071714 | -0.059509 | -0.07782 | -0.10071 | -0.07782 | 0.086975 | -0.082397 | -0.23804 | 0.009155 | -0.07782 | -0.11444 | 0.054932 | 0.009155 | -0.13733 | -0.19684 | 122.374 | 122.2183 | -0.073242 | 122.3785 | 122.3785 | 0.16022 | -0.21973 | 122.319 | 122.2595 | -0.10528 | 122.4655 | 122.3419 | 0.082397 | -0.15106 | 122.5433 | 122.3969 | 122.3557 | -0.39825 | 122.5113 | 122.4655 | 122.3785 | -0.35706
1177.2344 | 122.7173 | -122.4609 | 0.16937 | 0.12146 | 0.019547 | 0.0048706 | 0.0046911 | -0.0045522 | -0.00034818 | -0.0039521 | 0.14015 | -0.0089229 | -0.003262 | -0.00026701 | 0.0038943 | -0.0075986 | -0.054932 | -0.091553 | -0.082397 | -0.068665 | 0.09613 | -0.07782 | -0.2243 | 0.009155 | -0.11444 | -0.1236 | 0.045776 | 0.018311 | -0.13275 | -0.19226 | 122.3831 | 122.2366 | -0.073243 | 122.3694 | 122.3923 | 0.15564 | -0.22431 | 122.3282 | 122.2687 | -0.1236 | 122.4701 | 122.3373 | 0.068665 | -0.15106 | 122.5571 | 122.406 | 122.3785 | -0.39368 | 122.5067 | 122.4792 | 122.3465 | -0.36163
1178.9375 | 122.6532 | -122.4747 | 0.17853 | 0.1062 | 0.016342 | 0.0035888 | 0.0027685 | -0.0045522 | -0.006116 | -0.0060883 | 0.23933 | -0.0095639 | -0.0058254 | -5.3406e-05 | 0.0011173 | -0.0097348 | 0.032043 | 0.041199 | 0.041199 | -0.009155 | 0.050354 | -0.059509 | -0.17395 | 0.073242 | 0.082397 | 0 | 0.045776 | 0.009155 | -0.10071 | -0.16937 | 122.4152 | 122.3007 | -0.12817 | 122.5159 | 122.4655 | 0.16479 | -0.14648 | 122.374 | 122.3053 | -0.13275 | 122.5479 | 122.4747 | 0.16937 | -0.16937 | 122.525 | 122.5067 | 122.5159 | -0.35248 | 122.5204 | 122.4838 | 122.5571 | -0.3479
1180.625 | 122.6761 | -122.4701 | 0.17853 | 0.13672 | 0.019333 | 0.0044434 | 0.0040503 | -0.0049796 | -0.0046206 | -0.0056611 | 0.1783 | -0.0074277 | -0.003262 | -0.00048061 | 4.9132e-05 | -0.009094 | 0.018311 | 0.045776 | 0.041199 | -0.009155 | 0.059509 | -0.050354 | -0.17395 | 0.07782 | 0.082397 | -0.013733 | 0.059509 | 0.022888 | -0.10071 | -0.16022 | 122.4197 | 122.2961 | -0.11902 | 122.5159 | 122.4609 | 0.16479 | -0.16022 | 122.3694 | 122.3099 | -0.11902 | 122.5479 | 122.4564 | 0.14648 | -0.15564 | 122.5296 | 122.4884 | 122.5113 | -0.35248 | 122.5296 | 122.493 | 122.5525 | -0.33874
1182.2969 | 122.6532 | -122.4701 | 0.17395 | 0.090942 | 0.015915 | 0.0044434 | 0.0021277 | -0.007543 | -0.0037662 | -0.0054475 | 0.2317 | -0.0080685 | -0.00668 | -0.00026701 | 0.0032535 | -0.0088804 | 0.045776 | 0.041199 | 0.027466 | -0.018311 | 0.082397 | -0.041199 | -0.17853 | 0.068665 | 0.082397 | -0.018311 | 0.045776 | 0.027466 | -0.09613 | -0.16479 | 122.4289 | 122.2916 | -0.091553 | 122.5113 | 122.4518 | 0.16022 | -0.12817 | 122.374 | 122.3053 | -0.12817 | 122.5388 | 122.4518 | 0.14648 | -0.14648 | 122.5525 | 122.5159 | 122.4976 | -0.35248 | 122.5159 | 122.4976 | 122.5525 | -0.33874
1184.0156 | 122.6944 | -122.4564 | 0.17853 | 0.1062 | 0.019974 | 0.0042298 | 0.0017005 | -0.0062612 | 0.0024288 | -0.0030975 | 0.094375 | -0.0065731 | -0.006039 | -5.3406e-05 | 0.0056033 | -0.0099484 | -0.041199 | -0.13733 | -0.12817 | -0.082397 | 0.13275 | -0.073242 | -0.21057 | -0.036621 | -0.1236 | -0.17853 | 0.054932 | 0.045776 | -0.13275 | -0.21973 | 122.3831 | 122.2458 | -0.045777 | 122.319 | 122.374 | 0.12817 | -0.21973 | 122.3236 | 122.2366 | -0.1236 | 122.4197 | 122.2778 | 0.041199 | -0.13275 | 122.5891 | 122.4152 | 122.3282 | -0.3891 | 122.5113 | 122.5021 | 122.3328 | -0.39826
1185.6875 | 122.6807 | -122.5067 | 0.17853 | 0.037537 | 0.02211 | 0.0023072 | 0.0019141 | -0.0054068 | 0.0032834 | -0.0033111 | -0.035324 | -0.0070003 | -0.0047574 | 0.00080099 | 0.0064577 | -0.011444 | -0.018311 | -0.086975 | -0.082397 | -0.054932 | 0.1236 | -0.059509 | -0.21057 | -0.054932 | -0.13733 | -0.15564 | 0.07782 | 0.050354 | -0.14191 | -0.20599 | 122.4472 | 122.2961 | -0.054932 | 122.4197 | 122.4518 | 0.15564 | -0.19684 | 122.3648 | 122.3007 | -0.10071 | 122.4518 | 122.3511 | 0.050354 | -0.12817 | 122.6303 | 122.4884 | 122.4243 | -0.3891 | 122.5845 | 122.5571 | 122.3694 | -0.38452
1187.375 | 122.7081 | -122.4701 | 0.17853 | 0.029907 | 0.019119 | 0.0061524 | 0.0055457 | -0.0047658 | -0.0071842 | -0.0045929 | 0.086746 | -0.0089229 | -0.0045438 | -0.00048061 | -0.0012327 | -0.0086666 | 0.022888 | 0.041199 | 0.054932 | 0.036621 | 0.1236 | -0.013733 | -0.15564 | 0.068665 | 0.13275 | -0.009155 | 0.10986 | 0.082397 | -0.032043 | -0.11444 | 122.4564 | 122.3145 | -0.054932 | 122.5113 | 122.5067 | 0.19226 | -0.15564 | 122.4381 | 122.3557 | -0.068665 | 122.5388 | 122.4609 | 0.10529 | -0.096131 | 122.5937 | 122.493 | 122.525 | -0.33417 | 122.58 | 122.5525 | 122.6028 | -0.29297
1189.0469 | 122.7036 | -122.4884 | 0.17853 | -0.054016 | 0.021896 | 0.0031616 | 0.0042639 | -0.0060476 | 0.0032834 | -0.0026703 | -0.058212 | -0.0061459 | -0.0043302 | 0.0010148 | 0.0053897 | -0.013153 | 0.068665 | -0.013733 | -0.022888 | 0 | 0.13733 | -0.018311 | -0.19226 | 0.009155 | -0.041199 | -0.12817 | 0.091553 | 0.068665 | -0.11902 | -0.1831 | 122.4701 | 122.2961 | -0.041199 | 122.4747 | 122.4884 | 0.19226 | -0.10986 | 122.3694 | 122.3053 | -0.086975 | 122.4976 | 122.3602 | 0.054931 | -0.10986 | 122.6257 | 122.5571 | 122.4655 | -0.37079 | 122.58 | 122.5571 | 122.4472 | -0.36163
1190.7188 | 122.8317 | -122.4518 | 0.13733 | -0.18372 | 0.021256 | 0.0025208 | 0.0089635 | -0.0073294 | -0.00056178 | -0.0033111 | -0.22606 | -0.0070003 | -0.0011258 | 0.00058739 | 0.0030399 | -0.010589 | 0.064087 | 0.027466 | 0.018311 | 0.059509 | 0.21515 | 0.036621 | -0.1236 | 0.036621 | 0.07782 | -0.045776 | 0.15564 | 0.14648 | -0.054932 | -0.1236 | 122.4884 | 122.3282 | 0.07782 | 122.4792 | 122.5113 | 0.1831 | -0.073242 | 122.3969 | 122.3282 | 0.018311 | 122.4884 | 122.406 | 0.07782 | 0.009155 | 122.6669 | 122.5159 | 122.4701 | -0.26093 | 122.6074 | 122.5983 | 122.5296 | -0.26093
1192.3906 | 122.699 | -122.5021 | 0.16937 | 0.022278 | 0.019547 | 0.0023072 | 0.0051183 | -0.0062612 | 0.00093342 | -0.0045929 | 0.010452 | -0.0072141 | -0.0026212 | 0.00016019 | 0.0056033 | -0.011657 | -0.018311 | -0.050354 | -0.068665 | -0.041199 | 0.11902 | -0.064087 | -0.21515 | -0.032043 | -0.10529 | -0.15106 | 0.07782 | 0.064087 | -0.15106 | -0.1831 | 122.438 | 122.287 | -0.050354 | 122.4518 | 122.4609 | 0.17395 | -0.18768 | 122.3511 | 122.319 | -0.091553 | 122.4701 | 122.3511 | 0.032043 | -0.10529 | 122.6212 | 122.4838 | 122.4335 | -0.38452 | 122.58 | 122.5662 | 122.3968 | -0.35248
1194.0781 | 122.7219 | -122.4838 | 0.16937 | 0.15961 | 0.020828 | 0.004657 | 0.0012731 | -0.0039114 | -0.00163 | -0.0024567 | 0.18593 | -0.0093503 | -0.0056118 | 0.0010148 | 0.0045351 | -0.0078122 | 0.018311 | 0.022888 | -0.004578 | -0.018311 | 0.064087 | -0.059509 | -0.18768 | 0.054932 | 0.022888 | -0.018311 | 0.009155 | -0.004578 | -0.10986 | -0.17853 | 122.4243 | 122.2961 | -0.10529 | 122.5067 | 122.4655 | 0.16937 | -0.15106 | 122.374 | 122.3053 | -0.16022 | 122.5388 | 122.4655 | 0.16022 | -0.17395 | 122.5479 | 122.5021 | 122.4792 | -0.35706 | 122.493 | 122.4792 | 122.5067 | -0.3479
1195.75 | 122.7722 | -122.4564 | 0.14191 | -0.18372 | 0.016556 | 0.0040162 | 0.0074683 | -0.0043386 | -0.005048 | -0.0052337 | -0.058212 | -0.0076413 | -0.0036892 | -0.0021896 | 0.00047633 | -0.0099484 | 0.14191 | 0.17395 | 0.16022 | 0.14191 | 0.20142 | 0.082397 | -0.068665 | 0.14648 | 0.27466 | 0.091553 | 0.1236 | 0.10529 | -0.013733 | -0.09613 | 122.5388 | 122.3877 | 0.059509 | 122.6303 | 122.5983 | 0.21057 | 0 | 122.4426 | 122.3602 | -0.018311 | 122.6028 | 122.5479 | 0.18768 | -0.036621 | 122.6578 | 122.5983 | 122.6166 | -0.21057 | 122.58 | 122.5616 | 122.731 | -0.23804
1197.4219 | 122.7173 | -122.4701 | 0.16022 | 0.029907 | 0.017838 | 0.0052978 | 0.0046911 | -0.005834 | -0.0065434 | -0.0067291 | 0.10963 | -0.0089229 | -0.0030484 | -0.0011216 | 0.00068993 | -0.011017 | 0.032043 | 0.027466 | 0.045776 | 0.027466 | 0.1236 | 0.013733 | -0.13275 | 0.07782 | 0.11902 | 0.004578 | 0.11902 | 0.09613 | -0.068665 | -0.11444 | 122.4838 | 122.3373 | -0.036621 | 122.4976 | 122.4976 | 0.16022 | -0.12817 | 122.4014 | 122.3557 | -0.041198 | 122.5479 | 122.4747 | 0.11902 | -0.064087 | 122.5937 | 122.5021 | 122.5159 | -0.29297 | 122.5891 | 122.5662 | 122.5891 | -0.27466
1199.0938 | 122.6624 | -122.493 | 0.16022 | 0.12146 | 0.016556 | 0.0044434 | -0.00022208 | -0.0043386 | -0.0029118 | -0.0069427 | 0.1783 | -0.0074277 | -0.006039 | -0.00048061 | 0.0028263 | -0.010376 | 0.050354 | 0.054932 | 0.045776 | 0 | 0.064087 | -0.027466 | -0.1831 | 0.064087 | 0.064087 | -0.022888 | 0.045776 | 0.013733 | -0.12817 | -0.17853 | 122.4655 | 122.3099 | -0.09613 | 122.5479 | 122.493 | 0.1831 | -0.10986 | 122.3648 | 122.3145 | -0.11444 | 122.5571 | 122.4701 | 0.15564 | -0.14648 | 122.5571 | 122.5433 | 122.5388 | -0.34332 | 122.5388 | 122.5067 | 122.5571 | -0.33874
1200.7656 | 122.7036 | -122.4838 | 0.15564 | 0.15961 | 0.018051 | 0.0038024 | 0.0029821 | -0.0039114 | 0.00029262 | -0.0035249 | 0.20882 | -0.0042233 | -0.0056118 | 0.00058739 | 0.0032535 | -0.010589 | 0.050354 | 0.009155 | -0.009155 | 0.009155 | 0.045776 | -0.054932 | -0.19226 | 0.073242 | 0.027466 | -0.018311 | 0.004578 | -0.013733 | -0.12817 | -0.18768 | 122.4289 | 122.2916 | -0.10986 | 122.493 | 122.493 | 0.20142 | -0.10529 | 122.3557 | 122.2961 | -0.15106 | 122.5571 | 122.4655 | 0.16937 | -0.16937 | 122.5296 | 122.5342 | 122.4747 | -0.3479 | 122.4884 | 122.4701 | 122.5113 | -0.34332
1202.4688 | 122.7127 | -122.4792 | 0.16022 | 0.060425 | 0.019547 | 0.0050842 | 0.0059729 | -0.004125 | -0.0031254 | -0.0067291 | 0.079117 | -0.010846 | -0.0030484 | -0.0026168 | 0.00068993 | -0.0099484 | 0.041199 | 0.018311 | 0.036621 | 0.022888 | 0.13275 | -0.004578 | -0.15106 | 0.082397 | 0.11902 | 0.009155 | 0.09613 | 0.073242 | -0.050354 | -0.11444 | 122.4747 | 122.3282 | -0.027466 | 122.4976 | 122.5021 | 0.17395 | -0.11902 | 122.4289 | 122.3648 | -0.064087 | 122.5616 | 122.4884 | 0.1236 | -0.086975 | 122.612 | 122.5204 | 122.5159 | -0.31128 | 122.5754 | 122.5525 | 122.5983 | -0.27466
1204.1719 | 122.7585 | -122.4747 | 0.16022 | -0.069275 | 0.020187 | 0.0027344 | 0.0040503 | -0.0043386 | 0.003497 | -0.0026703 | -0.14214 | -0.0074277 | -0.003262 | -0.00048061 | 0.0068851 | -0.01123 | 0.10071 | 0.027466 | 0.018311 | 0.027466 | 0.13733 | -0.027466 | -0.16937 | 0.064087 | 0.022888 | -0.073242 | 0.082397 | 0.07782 | -0.11444 | -0.16022 | 122.4472 | 122.3053 | -0.022888 | 122.5021 | 122.5021 | 0.19684 | -0.059509 | 122.3602 | 122.3145 | -0.07782 | 122.5388 | 122.4014 | 0.086975 | -0.082397 | 122.612 | 122.5754 | 122.493 | -0.32959 | 122.5571 | 122.5525 | 122.4976 | -0.32043
1205.9375 | 122.7859 | -122.4655 | 0.13733 | -0.17609 | 0.017197 | 0.0052978 | 0.0089635 | -0.0060476 | -0.0039798 | -0.0037385 | -0.14214 | -0.010632 | -0.0051846 | -0.001976 | 0.0023989 | -0.0097348 | 0.14648 | 0.21057 | 0.17853 | 0.1236 | 0.18768 | 0.050354 | -0.068665 | 0.15564 | 0.28839 | 0.086975 | 0.13733 | 0.091553 | -0.018311 | -0.091553 | 122.5159 | 122.3969 | 0.050354 | 122.6761 | 122.5891 | 0.19226 | 0.009155 | 122.4472 | 122.374 | 0 | 122.6212 | 122.5525 | 0.17853 | -0.045776 | 122.6532 | 122.612 | 122.644 | -0.20599 | 122.6028 | 122.5571 | 122.7539 | -0.22888
1207.625 | 122.8226 | -122.438 | 0.1236 | -0.076904 | 0.017838 | 0.0040162 | 0.0038367 | -0.005834 | -0.0037662 | -0.0045929 | -0.058212 | -0.0084957 | -0.0064664 | 0.00037379 | 0.0026125 | -0.0099484 | 0.13275 | 0.13733 | 0.12817 | 0.10071 | 0.19226 | 0.036621 | -0.091553 | 0.17853 | 0.27008 | 0.10071 | 0.12817 | 0.10986 | -0.013733 | -0.07782 | 122.4747 | 122.3465 | 0.068665 | 122.5754 | 122.5388 | 0.19226 | 0.009155 | 122.4243 | 122.3602 | 0.004578 | 122.6166 | 122.5388 | 0.17853 | -0.013733 | 122.6303 | 122.5708 | 122.5662 | -0.21515 | 122.5662 | 122.5479 | 122.7081 | -0.20142
1209.3594 | 122.7905 | -122.4747 | 0.13275 | -0.17609 | 0.016769 | 0.0059388 | 0.0055457 | -0.0047658 | -0.0018436 | -0.0065155 | -0.14977 | -0.0087093 | -0.0045438 | -0.001976 | 0.0023989 | -0.010162 | 0.16022 | 0.18768 | 0.17395 | 0.14191 | 0.18768 | 0.073242 | -0.073242 | 0.16937 | 0.28381 | 0.07782 | 0.13733 | 0.10071 | -0.022888 | -0.073242 | 122.5479 | 122.4014 | 0.054932 | 122.6624 | 122.6166 | 0.21515 | 0.027466 | 122.4518 | 122.4014 | 0.004578 | 122.644 | 122.5525 | 0.15106 | -0.032043 | 122.6624 | 122.6349 | 122.6486 | -0.20599 | 122.612 | 122.5754 | 122.7585 | -0.20599
1211.1094 | 122.8271 | -122.4472 | 0.14191 | -0.16846 | 0.016769 | 0.004657 | 0.0038367 | -0.0077566 | -0.0037662 | -0.0056611 | -0.11162 | -0.0093503 | -0.0039028 | -0.0015488 | 0.00047633 | -0.012298 | 0.16022 | 0.1831 | 0.14648 | 0.1236 | 0.1831 | 0.041199 | -0.10071 | 0.19226 | 0.26093 | 0.11444 | 0.11444 | 0.068665 | -0.013733 | -0.068665 | 122.4884 | 122.3465 | 0.041198 | 122.6303 | 122.5708 | 0.2243 | 0.01831 | 122.4335 | 122.3785 | -0.027466 | 122.6395 | 122.5616 | 0.18311 | -0.073242 | 122.6303 | 122.6074 | 122.5937 | -0.24262 | 122.5616 | 122.5159 | 122.7081 | -0.21057
1212.7812 | 122.7768 | -122.4655 | 0.15564 | -0.18372 | 0.018478 | 0.0042298 | 0.0081091 | -0.0060476 | -0.0029118 | -0.0030975 | -0.25658 | -0.010632 | -0.001553 | 0.0016556 | 0.0038943 | -0.011444 | 0.15106 | 0.16479 | 0.14191 | 0.13733 | 0.20142 | 0.054932 | -0.068665 | 0.11444 | 0.22888 | 0.041199 | 0.14648 | 0.12817 | -0.032043 | -0.09613 | 122.5204 | 122.3969 | 0.045776 | 122.6303 | 122.6028 | 0.20599 | -0.004578 | 122.4335 | 122.3694 | -0.009156 | 122.58 | 122.5067 | 0.13733 | -0.027466 | 122.6669 | 122.6166 | 122.6074 | -0.22431 | 122.612 | 122.5937 | 122.6944 | -0.25177
1214.5156 | 122.7356 | -122.4564 | 0.16022 | 0.13672 | 0.018265 | 0.0050842 | 0.0014867 | -0.0051932 | 0.0037106 | -0.0033111 | 0.086746 | -0.0048641 | -0.0058254 | 0.00037379 | 0.0066715 | -0.0088804 | -0.004578 | -0.068665 | -0.09613 | -0.064087 | 0.091553 | -0.082397 | -0.2243 | 0.059509 | -0.045776 | -0.086975 | 0.050354 | 0.013733 | -0.12817 | -0.1831 | 122.374 | 122.2321 | -0.068664 | 122.3877 | 122.3923 | 0.16022 | -0.16479 | 122.3282 | 122.2733 | -0.10986 | 122.5159 | 122.3694 | 0.09613 | -0.14648 | 122.5479 | 122.4518 | 122.3602 | -0.38452 | 122.5067 | 122.4701 | 122.4106 | -0.34332
1216.2656 | 122.8271 | -122.4701 | 0.11902 | -0.16846 | 0.022965 | 0.0035888 | 0.0049047 | -0.0064748 | 0.0022152 | -0.0013885 | -0.2108 | -0.0076413 | -0.0047574 | -0.0013352 | 0.0053897 | -0.010162 | 0.091553 | 0.041199 | 0.004578 | 0.045776 | 0.21515 | 0.009155 | -0.12817 | 0.064087 | 0.064087 | -0.059509 | 0.11902 | 0.073242 | -0.091553 | -0.17853 | 122.4792 | 122.3419 | 0.09613 | 122.5113 | 122.5159 | 0.17395 | -0.027466 | 122.3785 | 122.2916 | 0 | 122.5342 | 122.4106 | 0.11902 | -0.045777 | 122.6852 | 122.5616 | 122.4747 | -0.24719 | 122.5891 | 122.5433 | 122.5342 | -0.29755
1217.9375 | 122.7997 | -122.4838 | 0.15564 | -0.092163 | 0.018906 | 0.0016662 | 0.0068273 | -0.0039114 | 0.0032834 | -0.0028839 | -0.16502 | -0.0074277 | -0.0041164 | 0.0018692 | 0.0034671 | -0.011017 | 0.059509 | 0.036621 | 0.004578 | 0.018311 | 0.13733 | -0.022888 | -0.17395 | 0.059509 | 0.036621 | -0.064087 | 0.091553 | 0.068665 | -0.10529 | -0.17395 | 122.4609 | 122.3099 | -0.018311 | 122.5204 | 122.5021 | 0.19226 | -0.096131 | 122.3785 | 122.3099 | -0.064087 | 122.5433 | 122.4197 | 0.10986 | -0.086975 | 122.6212 | 122.5433 | 122.4884 | -0.32959 | 122.5754 | 122.5525 | 122.5204 | -0.32959
1219.6562 | 122.731 | -122.493 | 0.15564 | 0.014648 | 0.016556 | 0.0057252 | 0.0027685 | -0.0043386 | -0.0065434 | -0.0045929 | 0.102 | -0.0076413 | -0.0026212 | -0.00069421 | 0.0019717 | -0.0071714 | 0.022888 | 0.059509 | 0.036621 | 0.027466 | 0.12817 | -0.004578 | -0.13275 | 0.073242 | 0.12817 | 0.009155 | 0.086975 | 0.086975 | -0.059509 | -0.13275 | 122.4884 | 122.3602 | -0.027466 | 122.5525 | 122.5204 | 0.16022 | -0.13275 | 122.4335 | 122.3602 | -0.068665 | 122.5662 | 122.5021 | 0.14191 | -0.068665 | 122.6212 | 122.5159 | 122.5296 | -0.28839 | 122.58 | 122.58 | 122.6212 | -0.28839
1221.4062 | 122.85 | -122.4472 | 0.12817 | -0.16083 | 0.020828 | 0.0023072 | 0.0070409 | -0.0060476 | 0.0011472 | -0.0028839 | -0.23369 | -0.0084957 | -0.0045438 | -0.00048061 | 0.0045351 | -0.011871 | 0.068665 | 0.050354 | 0.018311 | 0.064087 | 0.22888 | 0.036621 | -0.12817 | 0.054932 | 0.07782 | -0.054932 | 0.15106 | 0.10986 | -0.073242 | -0.12817 | 122.4838 | 122.319 | 0.10071 | 122.4976 | 122.5113 | 0.19226 | -0.059509 | 122.374 | 122.319 | 0.022888 | 122.5021 | 122.3923 | 0.073242 | -0.018311 | 122.6761 | 122.5159 | 122.4655 | -0.25635 | 122.5983 | 122.5571 | 122.525 | -0.25635
1223.0938 | 122.8363 | -122.4609 | 0.10529 | -0.19135 | 0.016556 | 0.0052978 | 0.0021277 | -0.0051932 | -0.00056178 | -0.0039521 | -0.19554 | -0.0080685 | -0.0041164 | 0.0012284 | 0.0053897 | -0.011444 | 0.036621 | 0.064087 | 0.009155 | 0.054932 | 0.24261 | 0.032043 | -0.1236 | 0.041199 | 0.082397 | -0.050354 | 0.14648 | 0.11444 | -0.064087 | -0.13275 | 122.493 | 122.3373 | 0.13733 | 122.525 | 122.5159 | 0.17853 | -0.068665 | 122.3969 | 122.3282 | 0.041198 | 122.5021 | 122.4106 | 0.082397 | 0.009155 | 122.7036 | 122.4976 | 122.4701 | -0.22888 | 122.6074 | 122.5754 | 122.5433 | -0.23804
1224.8438 | 122.7859 | -122.4655 | 0.16022 | -0.21423 | 0.01976 | 0.0035888 | 0.0074683 | -0.0054068 | -0.0031254 | -0.0043793 | -0.18028 | -0.0087093 | -0.0039028 | 0.00080099 | 0.00068993 | -0.0075986 | 0.10986 | 0.17853 | 0.11902 | 0.11902 | 0.21973 | 0.07782 | -0.086975 | 0.086975 | 0.19684 | 0.009155 | 0.16479 | 0.15564 | -0.059509 | -0.09613 | 122.5433 | 122.3785 | 0.05951 | 122.644 | 122.5845 | 0.20599 | -0.050354 | 122.406 | 122.3694 | 0.004578 | 122.5525 | 122.4747 | 0.10528 | -0.004577 | 122.6852 | 122.5754 | 122.5845 | -0.24719 | 122.6303 | 122.6212 | 122.6624 | -0.25635
1226.5781 | 122.8226 | -122.4655 | 0.13733 | 0.0070193 | 0.014633 | 0.0040162 | 0.0051183 | -0.0054068 | -0.006757 | -0.0060883 | 0.03334 | -0.0091367 | -0.00668 | -0.0026168 | 0.0015445 | -0.0075986 | 0.032043 | 0.073242 | 0.059509 | 0.059509 | 0.15106 | 0.009155 | -0.15106 | 0.11444 | 0.20142 | 0.059509 | 0.10071 | 0.09613 | -0.054932 | -0.11444 | 122.4747 | 122.3145 | 0.013733 | 122.5388 | 122.525 | 0.21057 | -0.10529 | 122.4106 | 122.3511 | -0.036621 | 122.58 | 122.525 | 0.17395 | -0.041199 | 122.6166 | 122.4976 | 122.525 | -0.28839 | 122.5662 | 122.5616 | 122.6669 | -0.25177
1228.25 | 122.7951 | -122.4609 | 0.16479 | -0.1532 | 0.019547 | 0.0059388 | 0.0061865 | -0.0043386 | -0.0039798 | -0.0063019 | -0.13451 | -0.0087093 | -0.0058254 | -0.0021896 | 0.0021853 | -0.009094 | 0.15106 | 0.21057 | 0.16022 | 0.15106 | 0.17395 | 0.064087 | -0.073242 | 0.15106 | 0.27924 | 0.10071 | 0.12817 | 0.09613 | -0.013733 | -0.068665 | 122.525 | 122.3877 | 0.009155 | 122.6715 | 122.612 | 0.2243 | -0.013733 | 122.4472 | 122.3923 | -0.036621 | 122.612 | 122.5616 | 0.16937 | -0.068665 | 122.6349 | 122.612 | 122.6212 | -0.23804 | 122.5891 | 122.5571 | 122.7402 | -0.23346
1229.9844 | 122.8134 | -122.4655 | 0.15106 | -0.2066 | 0.024246 | 0.002948 | 0.0066137 | -0.0071158 | 0.00029262 | -0.0045929 | -0.25658 | -0.0089229 | -0.0036892 | -0.00069421 | 0.0021853 | -0.0097348 | 0.073242 | 0.073242 | 0.018311 | 0.073242 | 0.26093 | 0.032043 | -0.10071 | 0.068665 | 0.10529 | -0.032043 | 0.19226 | 0.15564 | -0.054932 | -0.10071 | 122.4976 | 122.3648 | 0.10986 | 122.5388 | 122.5388 | 0.17395 | -0.07782 | 122.4106 | 122.3648 | 0.041199 | 122.5342 | 122.4335 | 0.068665 | 0.004578 | 122.7264 | 122.5388 | 122.4838 | -0.25177 | 122.6578 | 122.6212 | 122.5708 | -0.25177
1231.7344 | 122.7539 | -122.493 | 0.16937 | 0.13672 | 0.020187 | 0.002948 | -0.00064948 | -0.0066884 | 0.003497 | -0.0026703 | 0.086746 | -0.0048641 | -0.0047574 | 0.00058739 | 0.0066715 | -0.0093076 | -0.059509 | -0.10529 | -0.13733 | -0.082397 | 0.10986 | -0.10071 | -0.23346 | -0.022888 | -0.12817 | -0.15106 | 0.082397 | 0.041199 | -0.14191 | -0.19226 | 122.3923 | 122.2595 | -0.05951 | 122.3877 | 122.4106 | 0.15106 | -0.22888 | 122.3511 | 122.3007 | -0.086976 | 122.4701 | 122.3419 | 0.041199 | -0.12817 | 122.6028 | 122.4335 | 122.3557 | -0.40283 | 122.5754 | 122.5342 | 122.3648 | -0.36163
1233.4844 | 122.7722 | -122.4701 | 0.14648 | 0.029907 | 0.018265 | 0.0027344 | 0.0059729 | -0.0043386 | -0.0052616 | -0.0030975 | 0.079117 | -0.0093503 | -0.0043302 | -0.0024032 | -0.0010191 | -0.0093076 | 0.013733 | 0.068665 | 0.036621 | 0.050354 | 0.14191 | 0.004578 | -0.14648 | 0.07782 | 0.14648 | 0.009155 | 0.10986 | 0.082397 | -0.064087 | -0.13275 | 122.4747 | 122.3236 | -0.004577 | 122.5388 | 122.5204 | 0.19684 | -0.13275 | 122.406 | 122.3373 | -0.036621 | 122.5479 | 122.4792 | 0.14191 | -0.064087 | 122.612 | 122.4838 | 122.5067 | -0.29297 | 122.58 | 122.5525 | 122.6166 | -0.27924
1235.1562 | 122.7127 | -122.5113 | 0.16022 | 0.17487 | 0.016129 | 0.0044434 | 0.0010595 | -0.0032706 | -0.00034818 | -0.0045929 | 0.18593 | -0.0080685 | -0.0053982 | -0.0017624 | 0.0066715 | -0.010162 | 0.018311 | 0.027466 | 0.018311 | -0.022888 | 0.050354 | -0.059509 | -0.21973 | 0.086975 | 0.064087 | -0.009155 | 0.018311 | -0.004578 | -0.1236 | -0.19226 | 122.4518 | 122.2916 | -0.10986 | 122.5388 | 122.4884 | 0.19684 | -0.14191 | 122.3877 | 122.319 | -0.14191 | 122.5983 | 122.5021 | 0.18311 | -0.16479 | 122.5616 | 122.5296 | 122.5296 | -0.37994 | 122.5296 | 122.5067 | 122.5754 | -0.35248
1236.8906 | 122.8363 | -122.4609 | 0.13733 | -0.10742 | 0.018692 | 0.004657 | 0.0046911 | -0.0079702 | -0.006116 | -0.0063019 | -0.050583 | -0.0089229 | -0.0039028 | 0.0012284 | -0.0010191 | -0.0078122 | 0.15106 | 0.17853 | 0.11902 | 0.10529 | 0.1831 | 0.041199 | -0.09613 | 0.19684 | 0.28839 | 0.1236 | 0.10529 | 0.086975 | -0.009155 | -0.073242 | 122.5021 | 122.3648 | 0.045776 | 122.6395 | 122.5662 | 0.20142 | 0.013733 | 122.4518 | 122.3877 | -0.032043 | 122.6578 | 122.5845 | 0.19684 | -0.050354 | 122.644 | 122.612 | 122.58 | -0.23346 | 122.5662 | 122.5479 | 122.7493 | -0.21057
1238.6406 | 122.8409 | -122.4609 | 0.14648 | -0.046387 | 0.018692 | 0.0055114 | 0.0085363 | -0.0049796 | -0.005048 | -0.0063019 | -0.081101 | -0.0087093 | -0.0030484 | -0.0011216 | 4.9132e-05 | -0.011017 | 0.10986 | 0.14648 | 0.11902 | 0.09613 | 0.1831 | 0.036621 | -0.091553 | 0.18768 | 0.26093 | 0.10071 | 0.11902 | 0.091553 | -0.032043 | -0.086975 | 122.4976 | 122.3694 | 0.036621 | 122.6074 | 122.5571 | 0.18768 | -0.036621 | 122.4289 | 122.374 | -0.027465 | 122.6486 | 122.5616 | 0.18768 | -0.054931 | 122.644 | 122.5708 | 122.58 | -0.23804 | 122.58 | 122.5525 | 122.7219 | -0.23346
1240.375 | 122.7081 | -122.525 | 0.16479 | 0.090942 | 0.015915 | 0.0035888 | 0.0010595 | -0.0090384 | -0.00163 | -0.0054475 | 0.094375 | -0.0095639 | -0.008389 | 0.0016556 | 0.0038943 | -0.010162 | 0.041199 | 0.041199 | 0.032043 | 0.004578 | 0.082397 | -0.032043 | -0.16937 | 0.09613 | 0.09613 | -0.004578 | 0.086975 | 0.050354 | -0.073242 | -0.13275 | 122.493 | 122.3557 | -0.082398 | 122.5662 | 122.5296 | 0.17395 | -0.1236 | 122.4518 | 122.3923 | -0.07782 | 122.6212 | 122.5204 | 0.12817 | -0.11444 | 122.6074 | 122.5662 | 122.5571 | -0.33417 | 122.612 | 122.5754 | 122.6212 | -0.29755
1242.0625 | 122.8271 | -122.4976 | 0.14648 | -0.13794 | 0.020828 | 0.0027344 | 0.0055457 | -0.0066884 | 0.0037106 | -0.0065155 | -0.23369 | -0.0072141 | -0.0043302 | 0.00080099 | 0.0070987 | -0.014221 | 0.068665 | 0.045776 | 0.004578 | 0.045776 | 0.20142 | 0 | -0.16479 | 0.059509 | 0.045776 | -0.050354 | 0.11444 | 0.082397 | -0.10529 | -0.16479 | 122.4976 | 122.3328 | 0.054932 | 122.5433 | 122.5433 | 0.21057 | -0.077819 | 122.3923 | 122.3328 | -0.032043 | 122.5571 | 122.4472 | 0.11444 | -0.064087 | 122.699 | 122.5662 | 122.5021 | -0.31128 | 122.612 | 122.58 | 122.5433 | -0.31128
1243.8438 | 122.8546 | -122.4747 | 0.14191 | -0.16846 | 0.019974 | 0.0038024 | 0.0010595 | -0.008611 | 0.0020016 | -0.0060883 | -0.24895 | -0.0089229 | -0.0039028 | -0.0017624 | 0.0047489 | -0.011444 | 0.059509 | 0.059509 | 0.022888 | 0.064087 | 0.21057 | 0.004578 | -0.15564 | 0.059509 | 0.07782 | -0.050354 | 0.15564 | 0.11444 | -0.064087 | -0.13275 | 122.4792 | 122.319 | 0.068664 | 122.5342 | 122.5388 | 0.21973 | -0.082398 | 122.4106 | 122.3419 | 0.013733 | 122.5342 | 122.4243 | 0.082397 | -0.027466 | 122.6852 | 122.5342 | 122.4976 | -0.29755 | 122.6303 | 122.5891 | 122.5525 | -0.27466
1245.625 | 122.8226 | -122.493 | 0.14191 | -0.023499 | 0.018478 | 0.0044434 | 0.0066137 | -0.0060476 | -0.0071842 | -0.0056611 | -0.012436 | -0.0078549 | -0.0036892 | -0.0021896 | 4.9132e-05 | -0.0088804 | 0.045776 | 0.10529 | 0.091553 | 0.073242 | 0.14648 | 0.009155 | -0.1236 | 0.14648 | 0.24719 | 0.091553 | 0.11444 | 0.086975 | -0.027466 | -0.07782 | 122.5021 | 122.3694 | 0.004577 | 122.5983 | 122.5662 | 0.19684 | -0.096131 | 122.4655 | 122.4152 | -0.027466 | 122.6395 | 122.5845 | 0.16937 | -0.054932 | 122.6395 | 122.5388 | 122.5845 | -0.2655 | 122.6074 | 122.58 | 122.7402 | -0.21973
1247.2969 | 122.818 | -122.4747 | 0.13733 | -0.23712 | 0.019333 | 0.006366 | 0.0070409 | -0.0066884 | 7.902e-05 | -0.0069427 | -0.21843 | -0.0074277 | -0.0043302 | -0.0013352 | 0.00026273 | -0.013366 | 0.082397 | 0.082397 | 0.022888 | 0.059509 | 0.23804 | 0.050354 | -0.09613 | 0.050354 | 0.11444 | -0.032043 | 0.19226 | 0.15106 | -0.045776 | -0.10986 | 122.525 | 122.3785 | 0.10071 | 122.5571 | 122.5342 | 0.15564 | -0.054932 | 122.4289 | 122.3648 | 0.054932 | 122.525 | 122.4426 | 0.07782 | 0.013733 | 122.7127 | 122.5571 | 122.4976 | -0.23346 | 122.6669 | 122.6257 | 122.5891 | -0.24719
1249.0312 | 122.7264 | -122.5204 | 0.15564 | 0.075684 | 0.02211 | 0.0050842 | 0.0021277 | -0.0036978 | 0.0041378 | -0.0030975 | 0.056228 | -0.0046505 | -0.0056118 | -0.0011216 | 0.0070987 | -0.010162 | -0.054932 | -0.10986 | -0.1236 | -0.068665 | 0.14648 | -0.07782 | -0.21973 | -0.032043 | -0.12817 | -0.17395 | 0.082397 | 0.036621 | -0.13733 | -0.21057 | 122.4426 | 122.3007 | -0.009156 | 122.4106 | 122.4518 | 0.15106 | -0.21057 | 122.3831 | 122.3099 | -0.073243 | 122.4884 | 122.3465 | 0.036621 | -0.11902 | 122.6669 | 122.4655 | 122.3969 | -0.37537 | 122.6028 | 122.5571 | 122.3923 | -0.36621
1250.7188 | 122.7173 | -122.5159 | 0.19226 | 0.1825 | 0.019333 | 0.0065796 | 0.0031957 | -0.0054068 | -0.0024844 | -0.0050201 | 0.15541 | -0.0084957 | -0.004971 | -0.0017624 | 0.0026125 | -0.0093076 | 0.018311 | 0.054932 | 0.036621 | -0.009155 | 0.041199 | -0.068665 | -0.20599 | 0.09613 | 0.07782 | 0.004578 | 0.050354 | 0.004578 | -0.10986 | -0.16479 | 122.4472 | 122.3099 | -0.15106 | 122.5708 | 122.5067 | 0.19684 | -0.17395 | 122.406 | 122.3511 | -0.14191 | 122.612 | 122.5204 | 0.16937 | -0.18768 | 122.5571 | 122.5342 | 122.5525 | -0.39826 | 122.5662 | 122.5204 | 122.5937 | -0.35706
1252.4531 | 122.8409 | -122.4792 | 0.12817 | -0.061646 | 0.020615 | 0.0040162 | 0.0064001 | -0.0079702 | -0.0059024 | -0.0050201 | -0.08873 | -0.0097775 | -0.0017666 | -0.00069421 | -0.00016447 | -0.0097348 | 0.10986 | 0.16479 | 0.1236 | 0.11902 | 0.16022 | 0.045776 | -0.10986 | 0.17853 | 0.25177 | 0.086975 | 0.10986 | 0.09613 | -0.036621 | -0.086975 | 122.525 | 122.3694 | 0.032043 | 122.644 | 122.5983 | 0.22888 | -0.018311 | 122.4426 | 122.3923 | -0.018311 | 122.6578 | 122.5662 | 0.17395 | -0.032044 | 122.6395 | 122.5891 | 122.6028 | -0.23804 | 122.5891 | 122.5754 | 122.731 | -0.21515
1254.1875 | 122.7264 | -122.5296 | 0.16937 | 0.052795 | 0.014633 | 0.0042298 | 0.0040503 | -0.0062612 | -0.0056888 | -0.0045929 | 0.063858 | -0.010205 | -0.0062528 | -0.0011216 | 0.0049625 | -0.0093076 | 0.050354 | 0.045776 | 0.041199 | 0.022888 | 0.11902 | -0.009155 | -0.17853 | 0.086975 | 0.10986 | 0 | 0.091553 | 0.07782 | -0.054932 | -0.13275 | 122.5204 | 122.3511 | -0.050354 | 122.5754 | 122.5525 | 0.20142 | -0.11902 | 122.4747 | 122.3969 | -0.07782 | 122.6166 | 122.5296 | 0.13275 | -0.091553 | 122.6486 | 122.58 | 122.5708 | -0.3479 | 122.6212 | 122.6074 | 122.6395 | -0.30212
1255.9219 | 122.8409 | -122.4884 | 0.10986 | -0.031128 | 0.018265 | 0.0038024 | 0.0038367 | -0.0064748 | -0.0039798 | -0.0054475 | -0.027695 | -0.0082821 | -0.0064664 | -0.0021896 | -0.0012327 | -0.010803 | 0.082397 | 0.091553 | 0.073242 | 0.054932 | 0.16479 | 0.032043 | -0.13733 | 0.15564 | 0.21057 | 0.064087 | 0.09613 | 0.09613 | -0.036621 | -0.073242 | 122.5204 | 122.3511 | 0.054932 | 122.58 | 122.5433 | 0.19226 | -0.027466 | 122.4518 | 122.4152 | -0.013733 | 122.644 | 122.5525 | 0.13733 | -0.013733 | 122.6532 | 122.5708 | 122.5616 | -0.24719 | 122.5845 | 122.5845 | 122.699 | -0.18311
1257.6875 | 122.7264 | -122.5204 | 0.17853 | 0.090942 | 0.019974 | 0.0016662 | 0.0051183 | -0.0045522 | 0.0060604 | -0.0048065 | -0.035324 | -0.0048641 | -0.004971 | -5.3406e-05 | 0.0070987 | -0.012939 | 0 | -0.09613 | -0.10071 | -0.054932 | 0.13275 | -0.07782 | -0.21057 | -0.032043 | -0.12817 | -0.17853 | 0.082397 | 0.059509 | -0.12817 | -0.21973 | 122.4426 | 122.3099 | -0.045777 | 122.4243 | 122.4655 | 0.15564 | -0.17853 | 122.3923 | 122.3007 | -0.096131 | 122.4884 | 122.3419 | 0.041199 | -0.11902 | 122.6532 | 122.5204 | 122.4197 | -0.3891 | 122.6028 | 122.58 | 122.3923 | -0.39826
1259.375 | 122.8592 | -122.4655 | 0.13733 | -0.19135 | 0.019333 | 0.0055114 | 0.0051183 | -0.0032706 | 0.00071982 | -0.0060883 | -0.22606 | -0.0067867 | -0.0058254 | -0.00026701 | 0.0038943 | -0.012298 | 0.09613 | 0.032043 | -0.004578 | 0.064087 | 0.22888 | 0.027466 | -0.11902 | 0.054932 | 0.082397 | -0.050354 | 0.16479 | 0.12817 | -0.054932 | -0.11902 | 122.493 | 122.3465 | 0.091553 | 122.4976 | 122.5296 | 0.18311 | -0.041199 | 122.4106 | 122.3465 | 0.027466 | 122.5204 | 122.4152 | 0.068665 | -0.009155 | 122.6944 | 122.5616 | 122.4609 | -0.25635 | 122.6303 | 122.5937 | 122.5479 | -0.25635
1261.0781 | 122.7905 | -122.4884 | 0.14191 | -0.099793 | 0.02211 | 0.0033752 | 0.0064001 | -0.005834 | 0.003497 | -0.0028839 | -0.13451 | -0.0063595 | -0.0051846 | 0.0012284 | 0.0062441 | -0.012085 | 0.07782 | 0.036621 | 0.013733 | 0.027466 | 0.16937 | -0.027466 | -0.18768 | 0.054932 | 0.022888 | -0.073242 | 0.10986 | 0.064087 | -0.12817 | -0.1831 | 122.4609 | 122.3007 | 0.027466 | 122.525 | 122.5159 | 0.21515 | -0.064087 | 122.3602 | 122.3053 | -0.032044 | 122.5433 | 122.4152 | 0.10986 | -0.07782 | 122.6578 | 122.5662 | 122.5021 | -0.32959 | 122.5983 | 122.5525 | 122.5113 | -0.32501
1262.7656 | 122.818 | -122.4884 | 0.1236 | -0.2066 | 0.021042 | 0.0059388 | 0.0040503 | -0.0039114 | -0.0063296 | -0.0043793 | -0.11925 | -0.0093503 | -0.00668 | -0.0024032 | 0.0015445 | -0.006744 | 0.16479 | 0.20142 | 0.16022 | 0.13275 | 0.17853 | 0.07782 | -0.082397 | 0.16479 | 0.30212 | 0.10986 | 0.13275 | 0.10529 | -0.009155 | -0.064087 | 122.5662 | 122.406 | 0.054932 | 122.6898 | 122.6212 | 0.21515 | 0.041199 | 122.4792 | 122.4243 | 0.009155 | 122.6532 | 122.5983 | 0.17395 | -0.01831 | 122.6669 | 122.6532 | 122.6486 | -0.20599 | 122.6212 | 122.5937 | 122.7905 | -0.18768
1264.4688 | 122.7173 | -122.5113 | 0.16479 | 0.075684 | 0.015274 | 0.004657 | 0.0014867 | -0.005834 | -0.0039798 | -0.0052337 | 0.13252 | -0.0076413 | -0.0058254 | -5.3406e-05 | 0.0023989 | -0.010162 | 0.045776 | 0.045776 | 0.032043 | 0 | 0.09613 | -0.022888 | -0.17395 | 0.07782 | 0.10529 | -0.004578 | 0.07782 | 0.054932 | -0.059509 | -0.12817 | 122.4884 | 122.3373 | -0.068665 | 122.5571 | 122.5113 | 0.17395 | -0.11902 | 122.4518 | 122.3831 | -0.086975 | 122.5891 | 122.5067 | 0.1236 | -0.10986 | 122.6074 | 122.5571 | 122.5433 | -0.33874 | 122.5891 | 122.5662 | 122.6166 | -0.29297
1266.2031 | 122.7539 | -122.5113 | 0.16479 | 0.037537 | 0.015701 | 0.0055114 | 0.0049047 | -0.0064748 | -0.0048344 | -0.0067291 | 0.071487 | -0.0084957 | -0.0045438 | -0.0028306 | 0.0026125 | -0.0082394 | 0.036621 | 0.050354 | 0.032043 | 0.027466 | 0.14191 | -0.009155 | -0.15106 | 0.082397 | 0.12817 | 0.013733 | 0.10529 | 0.073242 | -0.086975 | -0.14191 | 122.5021 | 122.3602 | -0.022888 | 122.5616 | 122.5388 | 0.17853 | -0.12817 | 122.4243 | 122.3694 | -0.059509 | 122.5937 | 122.525 | 0.15564 | -0.091553 | 122.6532 | 122.5479 | 122.5433 | -0.31586 | 122.6166 | 122.5845 | 122.6395 | -0.3067
1267.9531 | 122.8592 | -122.5113 | 0.13733 | -0.19135 | 0.018051 | 0.0035888 | 0.0036231 | -0.0043386 | 0.004565 | -0.0060883 | -0.25658 | -0.0095639 | -0.0058254 | -0.00048061 | 0.0075259 | -0.010162 | 0.086975 | 0.064087 | 0.013733 | 0.07782 | 0.22888 | 0.027466 | -0.11444 | 0.054932 | 0.045776 | -0.050354 | 0.14191 | 0.082397 | -0.10071 | -0.14191 | 122.5388 | 122.3969 | 0.091553 | 122.5754 | 122.5891 | 0.19226 | -0.050354 | 122.4106 | 122.3694 | 0.004578 | 122.5662 | 122.4609 | 0.091553 | -0.054932 | 122.7402 | 122.5983 | 122.525 | -0.25177 | 122.6532 | 122.5937 | 122.5571 | -0.27924
1269.625 | 122.7585 | -122.4976 | 0.14648 | 0.098572 | 0.022751 | 0.0031616 | 0.0074683 | -0.0051932 | 0.0020016 | -0.0037385 | 0.063858 | -0.0084957 | -0.0036892 | -0.0011216 | 0.0049625 | -0.010803 | -0.073242 | -0.10529 | -0.1236 | -0.073242 | 0.11444 | -0.09613 | -0.23346 | -0.032043 | -0.11902 | -0.11902 | 0.073242 | 0.041199 | -0.13275 | -0.20599 | 122.4014 | 122.2641 | -0.032043 | 122.3923 | 122.4243 | 0.16022 | -0.21973 | 122.3648 | 122.2916 | -0.073242 | 122.4655 | 122.3785 | 0.086975 | -0.10529 | 122.612 | 122.4243 | 122.374 | -0.37994 | 122.5708 | 122.5388 | 122.3785 | -0.35248
1271.3438 | 122.7951 | -122.493 | 0.13733 | -0.17609 | 0.019119 | 0.0057252 | 0.0057593 | -0.0054068 | -0.0022708 | -0.0037385 | -0.18791 | -0.010418 | -0.0051846 | -0.0028306 | 0.0015445 | -0.0082394 | 0.10529 | 0.17395 | 0.14191 | 0.13275 | 0.19226 | 0.068665 | -0.10071 | 0.12817 | 0.24261 | 0.054932 | 0.14191 | 0.12817 | -0.032043 | -0.07782 | 122.5616 | 122.3923 | 0.054932 | 122.6669 | 122.6257 | 0.23346 | -0.032043 | 122.4609 | 122.4152 | 0.004578 | 122.6212 | 122.5479 | 0.13275 | -0.009155 | 122.6852 | 122.5983 | 122.6349 | -0.23804 | 122.6349 | 122.6212 | 122.7356 | -0.21515
1273.0156 | 122.7127 | -122.5342 | 0.15106 | 0.098572 | 0.016983 | 0.0040162 | 0.0023413 | -0.005834 | -0.0037662 | -0.0045929 | 0.15541 | -0.0065731 | -0.0073208 | -0.00048061 | 0.0043215 | -0.0099484 | 0.032043 | 0.032043 | 0.018311 | 0 | 0.059509 | -0.068665 | -0.17853 | 0.091553 | 0.10071 | 0.018311 | 0.064087 | 0.041199 | -0.09613 | -0.15106 | 122.4655 | 122.3557 | -0.091553 | 122.5662 | 122.5342 | 0.17853 | -0.11902 | 122.4381 | 122.3831 | -0.086975 | 122.6257 | 122.5525 | 0.16937 | -0.10986 | 122.5937 | 122.5662 | 122.5525 | -0.32959 | 122.5983 | 122.5754 | 122.6349 | -0.30212
1274.7031 | 122.7722 | -122.5204 | 0.14191 | 0.12146 | 0.020828 | 0.004657 | 0.0017005 | -0.0056204 | 0.0020016 | -0.0050201 | 0.063858 | -0.0063595 | -0.0051846 | 0.0010148 | 0.0077395 | -0.011871 | -0.018311 | -0.086975 | -0.11444 | -0.086975 | 0.11902 | -0.082397 | -0.2243 | -0.013733 | -0.10529 | -0.13733 | 0.068665 | 0.041199 | -0.13733 | -0.21515 | 122.4381 | 122.2961 | -0.022888 | 122.4335 | 122.4335 | 0.13733 | -0.16022 | 122.3831 | 122.3053 | -0.073242 | 122.5067 | 122.3831 | 0.07782 | -0.10071 | 122.6395 | 122.5021 | 122.406 | -0.36621 | 122.5891 | 122.5616 | 122.4152 | -0.35706
1276.375 | 122.7997 | -122.5113 | 0.14191 | 0.029907 | 0.016342 | 0.004657 | 0.0029821 | -0.0056204 | -0.0063296 | -0.0071563 | 0.03334 | -0.0091367 | -0.0034756 | -0.0013352 | 0.0013309 | -0.0086666 | 0.036621 | 0.045776 | 0.036621 | 0.027466 | 0.15106 | 0.013733 | -0.15564 | 0.10071 | 0.15106 | 0.032043 | 0.091553 | 0.064087 | -0.054932 | -0.13733 | 122.525 | 122.3557 | 0.009155 | 122.5571 | 122.5388 | 0.18311 | -0.10529 | 122.4564 | 122.374 | -0.050354 | 122.612 | 122.5433 | 0.16937 | -0.07782 | 122.6624 | 122.5479 | 122.5479 | -0.29755 | 122.6028 | 122.5754 | 122.6624 | -0.27924
1278.0625 | 122.7356 | -122.5296 | 0.15564 | 0.19012 | 0.019333 | 0.0035888 | 0.0027685 | -0.0030568 | 0.00093342 | -0.0037385 | 0.20119 | -0.0067867 | -0.00668 | -0.0015488 | 0.0041079 | -0.009094 | 0.050354 | 0.013733 | 0 | -0.009155 | 0.027466 | -0.082397 | -0.21057 | 0.073242 | 0.050354 | -0.022888 | 0.013733 | -0.022888 | -0.12817 | -0.17853 | 122.4472 | 122.319 | -0.12817 | 122.5433 | 122.5204 | 0.20142 | -0.10529 | 122.4014 | 122.3511 | -0.14191 | 122.6028 | 122.5067 | 0.15564 | -0.17853 | 122.5571 | 122.58 | 122.5296 | -0.36621 | 122.5433 | 122.5067 | 122.58 | -0.33417
1279.7344 | 122.7081 | -122.5204 | 0.16937 | 0.098572 | 0.017838 | 0.0052978 | 0.00063232 | -0.0043386 | -0.0041934 | -0.0041657 | 0.19356 | -0.0091367 | -0.0071072 | -0.0011216 | 0.0043215 | -0.0097348 | 0.064087 | 0.032043 | 0.036621 | -0.018311 | 0.073242 | -0.059509 | -0.16479 | 0.07782 | 0.07782 | -0.009155 | 0.050354 | 0.032043 | -0.10986 | -0.16937 | 122.4609 | 122.3557 | -0.096131 | 122.5525 | 122.5021 | 0.14648 | -0.10529 | 122.4106 | 122.3511 | -0.11902 | 122.5983 | 122.5113 | 0.16022 | -0.13733 | 122.5937 | 122.5845 | 122.5571 | -0.33417 | 122.5708 | 122.5525 | 122.5983 | -0.33875
1281.4219 | 122.8363 | -122.5159 | 0.13733 | -0.015869 | 0.01741 | 0.006366 | 0.0044775 | -0.0064748 | -0.0054752 | -0.0039521 | -0.020065 | -0.0084957 | -0.00668 | -0.001976 | 0.0023989 | -0.0095212 | 0.07782 | 0.059509 | 0.059509 | 0.059509 | 0.15106 | 0.022888 | -0.12817 | 0.11902 | 0.20142 | 0.045776 | 0.1236 | 0.086975 | -0.050354 | -0.10529 | 122.5388 | 122.3877 | 0.013733 | 122.5754 | 122.5754 | 0.18768 | -0.059509 | 122.4655 | 122.4106 | -0.013733 | 122.6349 | 122.5616 | 0.15106 | -0.050354 | 122.6669 | 122.5937 | 122.5754 | -0.2655 | 122.6395 | 122.6028 | 122.7173 | -0.24262
1283.0938 | 122.731 | -122.5159 | 0.16937 | 0.15961 | 0.020828 | 0.0018798 | 0.0038367 | -0.0049796 | 0.0011472 | -0.0058747 | 0.15541 | -0.0087093 | -0.0056118 | -0.00048061 | 0.0058169 | -0.014435 | 0.068665 | 0 | 0.013733 | 0 | 0.050354 | -0.082397 | -0.19684 | 0.082397 | 0.036621 | -0.032043 | 0.013733 | -0.013733 | -0.1236 | -0.19684 | 122.4335 | 122.319 | -0.11902 | 122.5159 | 122.5159 | 0.19684 | -0.10071 | 122.3923 | 122.319 | -0.15564 | 122.5983 | 122.4838 | 0.1648 | -0.18311 | 122.5662 | 122.5845 | 122.5296 | -0.36621 | 122.5296 | 122.5021 | 122.5525 | -0.36621
1284.7656 | 122.7448 | -122.5113 | 0.17395 | 0.19775 | 0.019547 | 0.0033752 | 0.0019141 | -0.0032706 | 0.00029262 | -0.0035249 | 0.18593 | -0.0070003 | -0.009457 | -0.0013352 | 0.0053897 | -0.011017 | 0.068665 | 0.009155 | 0.018311 | -0.009155 | 0.032043 | -0.07782 | -0.22888 | 0.082397 | 0.032043 | -0.018311 | 0.027466 | -0.013733 | -0.1236 | -0.18768 | 122.4335 | 122.2824 | -0.14191 | 122.5204 | 122.5021 | 0.21973 | -0.10528 | 122.3877 | 122.3236 | -0.14648 | 122.5937 | 122.493 | 0.16937 | -0.18768 | 122.5433 | 122.58 | 122.5296 | -0.40283 | 122.5388 | 122.4976 | 122.5433 | -0.36163
1286.4375 | 122.7814 | -122.5204 | 0.14191 | 0.045166 | 0.015488 | 0.0020936 | 0.0064001 | -0.0047658 | -0.0048344 | -0.0056611 | 0.025711 | -0.010205 | -0.0053982 | -0.0017624 | 0.00068993 | -0.010162 | 0.068665 | 0.013733 | 0.027466 | 0.041199 | 0.12817 | 0.004578 | -0.13275 | 0.086975 | 0.13733 | 0.009155 | 0.11444 | 0.07782 | -0.068665 | -0.12817 | 122.525 | 122.3877 | -0.013733 | 122.5342 | 122.5616 | 0.17395 | -0.073242 | 122.4518 | 122.3923 | -0.027466 | 122.6074 | 122.5296 | 0.13733 | -0.064087 | 122.6486 | 122.5891 | 122.5479 | -0.27466 | 122.6349 | 122.5983 | 122.6578 | -0.27008
1288.1094 | 122.8271 | -122.493 | 0.14648 | -0.23712 | 0.019333 | 0.0035888 | 0.0087499 | -0.002416 | -0.00013458 | -0.0071563 | -0.18028 | -0.011487 | -0.0024076 | 0.001442 | 0.00047633 | -0.012298 | 0.1831 | 0.17395 | 0.16937 | 0.13275 | 0.19684 | 0.059509 | -0.068665 | 0.17395 | 0.25635 | 0.082397 | 0.13275 | 0.10986 | -0.018311 | -0.10986 | 122.5525 | 122.4243 | 0.050354 | 122.6669 | 122.6257 | 0.20142 | 0.036621 | 122.4747 | 122.3831 | -0.013733 | 122.6669 | 122.5754 | 0.19226 | -0.036621 | 122.6898 | 122.6761 | 122.6624 | -0.21515 | 122.6257 | 122.6028 | 122.7493 | -0.25635
1289.7812 | 122.8592 | -122.5067 | 0.13733 | -0.12268 | 0.017624 | 0.0042298 | 0.0051183 | -0.0019888 | -0.0037662 | -0.0056611 | -0.16502 | -0.0093503 | -0.0034756 | -0.0026168 | 0.0017581 | -0.012512 | 0.1831 | 0.1831 | 0.16937 | 0.1236 | 0.1831 | 0.054932 | -0.086975 | 0.17853 | 0.27466 | 0.10529 | 0.13275 | 0.10986 | -0.022888 | -0.082397 | 122.5616 | 122.4197 | 0.045776 | 122.6898 | 122.6303 | 0.21057 | 0.045776 | 122.4838 | 122.4243 | -0.004578 | 122.6852 | 122.612 | 0.18768 | -0.027466 | 122.6898 | 122.6898 | 122.6761 | -0.2243 | 122.6395 | 122.6166 | 122.7814 | -0.21973
1291.4688 | 122.8409 | -122.5113 | 0.14191 | 0.029907 | 0.021256 | 0.0057252 | 0.0064001 | -0.0039114 | -0.0024844 | -0.0052337 | 0.018082 | -0.0093503 | -0.007748 | -0.00090781 | 0.0013309 | -0.011444 | 0.073242 | 0.032043 | 0.045776 | 0.041199 | 0.15564 | 0 | -0.13733 | 0.10529 | 0.15564 | 0.009155 | 0.10986 | 0.086975 | -0.064087 | -0.13275 | 122.5113 | 122.374 | 0.013733 | 122.5433 | 122.5525 | 0.17853 | -0.068665 | 122.4472 | 122.3785 | -0.032044 | 122.6166 | 122.5204 | 0.14191 | -0.054932 | 122.6669 | 122.5845 | 122.5571 | -0.27924 | 122.6212 | 122.5983 | 122.6669 | -0.27466
1293.1406 | 122.7768 | -122.525 | 0.18768 | 0.11383 | 0.022965 | 0.0031616 | 0.0029821 | -0.0045522 | 0.0043514 | -0.0043793 | 0.025711 | -0.0061459 | -0.0064664 | 0.00080099 | 0.0081667 | -0.012726 | 0.004578 | -0.11444 | -0.15106 | -0.07782 | 0.10986 | -0.091553 | -0.22888 | -0.009155 | -0.12817 | -0.14648 | 0.091553 | 0.045776 | -0.15106 | -0.20142 | 122.4335 | 122.2961 | -0.07782 | 122.4106 | 122.4472 | 0.15106 | -0.1831 | 122.374 | 122.3236 | -0.09613 | 122.5159 | 122.3785 | 0.054932 | -0.14191 | 122.6349 | 122.5296 | 122.374 | -0.41656 | 122.6166 | 122.5708 | 122.3969 | -0.3891
1294.8438 | 122.8455 | -122.4976 | 0.11902 | -0.2066 | 0.019333 | 0.0057252 | 0.0046911 | -0.004125 | -0.0031254 | -0.0045929 | -0.16502 | -0.0074277 | -0.0073208 | -0.0026168 | 0.0028263 | -0.0099484 | 0.1831 | 0.1831 | 0.16022 | 0.13275 | 0.21057 | 0.068665 | -0.073242 | 0.16937 | 0.27924 | 0.086975 | 0.11902 | 0.09613 | -0.022888 | -0.07782 | 122.5662 | 122.4243 | 0.091552 | 122.6807 | 122.6303 | 0.20599 | 0.064086 | 122.4747 | 122.4197 | 0 | 122.6669 | 122.5845 | 0.16479 | -0.022889 | 122.7081 | 122.6807 | 122.6578 | -0.19226 | 122.6166 | 122.5937 | 122.7768 | -0.19684
1296.5156 | 122.85 | -122.4976 | 0.14648 | -0.12268 | 0.019119 | 0.0020936 | 0.0064001 | -0.004125 | -0.0035526 | -0.0056611 | -0.11925 | -0.010632 | -0.0051846 | 0.00037379 | 0.0023989 | -0.011871 | 0.1831 | 0.19226 | 0.16479 | 0.12817 | 0.17395 | 0.036621 | -0.082397 | 0.19226 | 0.29297 | 0.082397 | 0.12817 | 0.10529 | -0.018311 | -0.059509 | 122.5342 | 122.4152 | 0.027466 | 122.6898 | 122.6257 | 0.21057 | 0.036621 | 122.4792 | 122.438 | -0.01831 | 122.6898 | 122.58 | 0.14191 | -0.041198 | 122.6715 | 122.6807 | 122.6624 | -0.22888 | 122.6257 | 122.6028 | 122.7905 | -0.20599
1298.2188 | 122.8958 | -122.4976 | 0.15564 | -0.22949 | 0.019974 | 0.0031616 | 0.0055457 | -0.0045522 | 0.0024288 | -0.0045929 | -0.26421 | -0.0061459 | -0.0058254 | -0.00069421 | 0.0038943 | -0.012939 | 0.091553 | 0.064087 | 0.027466 | 0.073242 | 0.2655 | 0.036621 | -0.10071 | 0.064087 | 0.073242 | -0.045776 | 0.16022 | 0.13733 | -0.064087 | -0.13733 | 122.5342 | 122.3969 | 0.10986 | 122.5616 | 122.5708 | 0.17395 | -0.064087 | 122.4335 | 122.3602 | 0.004577 | 122.5616 | 122.4518 | 0.091553 | -0.018311 | 122.7631 | 122.5891 | 122.525 | -0.25635 | 122.6578 | 122.6349 | 122.5708 | -0.29297
1299.9531 | 122.7493 | -122.5296 | 0.16479 | 0.068054 | 0.017838 | 0.0050842 | 0.0025549 | -0.0071158 | -0.003339 | -0.0075837 | 0.079117 | -0.010846 | -0.0043302 | -0.00090781 | 0.0019717 | -0.007385 | 0.032043 | 0.064087 | 0.045776 | 0.022888 | 0.1236 | 0 | -0.14648 | 0.10529 | 0.10071 | 0.004578 | 0.10071 | 0.064087 | -0.07782 | -0.13275 | 122.5296 | 122.3831 | -0.041199 | 122.5937 | 122.5525 | 0.16937 | -0.13275 | 122.4518 | 122.3969 | -0.064087 | 122.6349 | 122.5342 | 0.13733 | -0.10071 | 122.6532 | 122.5616 | 122.5754 | -0.31128 | 122.6303 | 122.5937 | 122.6303 | -0.29755
1301.625 | 122.7905 | -122.5113 | 0.16937 | 0.12909 | 0.019974 | 0.004657 | 0.0040503 | -0.0066884 | 0.0011472 | -0.0016021 | 0.11726 | -0.0057187 | -0.0053982 | 0.00016019 | 0.0066715 | -0.012298 | -0.022888 | -0.068665 | -0.082397 | -0.068665 | 0.10071 | -0.07782 | -0.21515 | 0.032043 | -0.073242 | -0.091553 | 0.064087 | 0.036621 | -0.15106 | -0.20599 | 122.4335 | 122.2961 | -0.068665 | 122.4426 | 122.4426 | 0.14648 | -0.19226 | 122.3602 | 122.3053 | -0.10529 | 122.5433 | 122.4197 | 0.11444 | -0.13275 | 122.612 | 122.4884 | 122.4289 | -0.38452 | 122.5754 | 122.5479 | 122.4381 | -0.37537
1303.3125 | 122.7676 | -122.5159 | 0.15564 | 0.13672 | 0.020615 | 0.0027344 | 0.0025549 | -0.0054068 | 0.00050622 | -0.0037385 | 0.018082 | -0.0065731 | -0.0058254 | -0.00026701 | 0.0060305 | -0.0093076 | -0.036621 | -0.086975 | -0.11444 | -0.07782 | 0.09613 | -0.091553 | -0.22888 | 0 | -0.10529 | -0.13275 | 0.086975 | 0.045776 | -0.12817 | -0.21515 | 122.4243 | 122.287 | -0.05951 | 122.4289 | 122.438 | 0.15106 | -0.19226 | 122.3877 | 122.3007 | -0.068665 | 122.5159 | 122.3831 | 0.082398 | -0.10986 | 122.612 | 122.4792 | 122.4014 | -0.38452 | 122.6028 | 122.5616 | 122.4106 | -0.37079
1305.0312 | 122.8592 | -122.5021 | 0.1236 | -0.092163 | 0.019547 | 0.0035888 | 0.0098181 | -0.0071158 | -0.0039798 | -0.0048065 | -0.042954 | -0.0095639 | -0.0047574 | -0.0024032 | -0.0012327 | -0.009094 | 0.13733 | 0.19684 | 0.13733 | 0.10986 | 0.17395 | 0.041199 | -0.10071 | 0.1831 | 0.28839 | 0.13275 | 0.10529 | 0.082397 | -0.032043 | -0.091553 | 122.5433 | 122.4014 | 0.050354 | 122.699 | 122.612 | 0.21057 | 0.013733 | 122.4701 | 122.4106 | -0.01831 | 122.6852 | 122.6349 | 0.2243 | -0.041199 | 122.6761 | 122.6395 | 122.6395 | -0.2243 | 122.6074 | 122.5845 | 122.7905 | -0.21515
1306.7188 | 122.8592 | -122.493 | 0.14648 | -0.084534 | 0.019974 | 0.0031616 | 0.0078955 | -0.0043386 | -0.0059024 | -0.0033111 | -0.10399 | -0.010632 | -0.0051846 | -0.00090781 | -0.0016599 | -0.0097348 | 0.09613 | 0.15564 | 0.1236 | 0.11444 | 0.16022 | 0.041199 | -0.11902 | 0.16479 | 0.25177 | 0.10529 | 0.1236 | 0.10071 | -0.036621 | -0.091553 | 122.5342 | 122.374 | 0.013733 | 122.6486 | 122.6074 | 0.23346 | -0.050354 | 122.4564 | 122.4014 | -0.022888 | 122.6578 | 122.5983 | 0.19684 | -0.045776 | 122.6532 | 122.5891 | 122.6166 | -0.2655 | 122.6166 | 122.5937 | 122.7448 | -0.23804
1308.3906 | 122.731 | -122.5479 | 0.16937 | 0.12146 | 0.016983 | 0.0035888 | 0.0029821 | -0.0036978 | -0.0012028 | -0.0058747 | 0.12489 | -0.0087093 | -0.0064664 | 0.00016019 | 0.0036807 | -0.0095212 | 0.032043 | 0.045776 | 0.004578 | -0.013733 | 0.045776 | -0.054932 | -0.20599 | 0.09613 | 0.10529 | -0.004578 | 0.082397 | 0.045776 | -0.068665 | -0.14648 | 122.493 | 122.3419 | -0.1236 | 122.5937 | 122.5342 | 0.19226 | -0.13733 | 122.4792 | 122.4014 | -0.086976 | 122.644 | 122.5433 | 0.14191 | -0.1236 | 122.5937 | 122.58 | 122.5525 | -0.37537 | 122.6303 | 122.5937 | 122.6532 | -0.31586
1310.0625 | 122.7493 | -122.5296 | 0.16479 | 0.060425 | 0.018692 | 0.0048706 | 0.0023413 | -0.0069022 | -0.0020572 | -0.0048065 | 0.071487 | -0.010846 | -0.0053982 | -0.0047532 | 0.0041079 | -0.010803 | 0.050354 | 0.032043 | 0.045776 | 0.018311 | 0.12817 | -0.009155 | -0.16022 | 0.091553 | 0.11444 | 0.009155 | 0.086975 | 0.068665 | -0.064087 | -0.14191 | 122.5204 | 122.3694 | -0.036621 | 122.5616 | 122.5479 | 0.17853 | -0.11444 | 122.4655 | 122.3877 | -0.07782 | 122.6212 | 122.5388 | 0.15106 | -0.09613 | 122.6578 | 122.58 | 122.5754 | -0.32501 | 122.6166 | 122.5983 | 122.644 | -0.3067
1311.7344 | 122.7493 | -122.5388 | 0.16937 | 0.068054 | 0.016769 | 0.0038024 | 0.0014867 | -0.007543 | -0.002698 | -0.0056611 | 0.063858 | -0.0065731 | -0.0068936 | -0.00090781 | 0.0026125 | -0.0097348 | 0.054932 | 0.041199 | 0.032043 | 0.013733 | 0.1236 | -0.009155 | -0.16022 | 0.091553 | 0.11902 | 0.013733 | 0.091553 | 0.07782 | -0.073242 | -0.10986 | 122.5296 | 122.3785 | -0.045777 | 122.58 | 122.5525 | 0.17395 | -0.11444 | 122.4655 | 122.4289 | -0.07782 | 122.6303 | 122.5525 | 0.1236 | -0.091553 | 122.6624 | 122.5937 | 122.5708 | -0.32959 | 122.6303 | 122.6166 | 122.6578 | -0.27924
1313.4062 | 122.8546 | -122.5067 | 0.13733 | -0.16083 | 0.018692 | 0.0042298 | 0.0042639 | -0.0045522 | 0.00093342 | -0.0039521 | -0.19554 | -0.0089229 | -0.0068936 | -0.0021896 | 0.0019717 | -0.011444 | 0.19226 | 0.17395 | 0.15106 | 0.12817 | 0.18768 | 0.054932 | -0.073242 | 0.17853 | 0.28839 | 0.09613 | 0.13275 | 0.10071 | -0.009155 | -0.068665 | 122.5616 | 122.4335 | 0.050354 | 122.6807 | 122.6349 | 0.20142 | 0.054932 | 122.4976 | 122.438 | -0.004578 | 122.6852 | 122.6028 | 0.16479 | -0.036621 | 122.6944 | 122.699 | 122.6578 | -0.21057 | 122.6395 | 122.6074 | 122.7951 | -0.20599
1315.0781 | 122.8409 | -122.525 | 0.14648 | -0.22949 | 0.020401 | 0.0042298 | 0.0074683 | -0.0071158 | 7.902e-05 | -0.0067291 | -0.28709 | -0.0093503 | -0.0034756 | 0.00080099 | 0.0032535 | -0.011017 | 0.10529 | 0.059509 | 0.036621 | 0.064087 | 0.25177 | 0.036621 | -0.09613 | 0.073242 | 0.1236 | -0.022888 | 0.19226 | 0.15106 | -0.068665 | -0.11444 | 122.5616 | 122.4289 | 0.10529 | 122.5845 | 122.5891 | 0.16022 | -0.041198 | 122.4564 | 122.4106 | 0.045777 | 122.5983 | 122.5021 | 0.091553 | 0.004578 | 122.7768 | 122.6303 | 122.5616 | -0.24261 | 122.7173 | 122.6761 | 122.6486 | -0.26093
1316.75 | 122.8134 | -122.5067 | 0.14191 | -0.22186 | 0.020401 | 0.002948 | 0.0078955 | -0.0028432 | 7.902e-05 | -0.0050201 | -0.24132 | -0.0080685 | -0.0041164 | 0.00016019 | 4.9132e-05 | -0.010162 | 0.09613 | 0.10986 | 0.068665 | 0.086975 | 0.24719 | 0.045776 | -0.10529 | 0.07782 | 0.13275 | -0.022888 | 0.17853 | 0.13733 | -0.07782 | -0.14191 | 122.5525 | 122.4014 | 0.10528 | 122.6166 | 122.5937 | 0.19226 | -0.045777 | 122.4289 | 122.3648 | 0.036621 | 122.5845 | 122.4838 | 0.11902 | -0.004578 | 122.7539 | 122.6028 | 122.5754 | -0.24719 | 122.6852 | 122.644 | 122.6395 | -0.28381
1318.4844 | 122.7219 | -122.5662 | 0.17395 | 0.1062 | 0.016769 | 0.0055114 | 0.0012731 | -0.0066884 | 0.00093342 | -0.0048065 | 0.14015 | -0.0093503 | -0.004971 | -0.00048061 | 0.0023989 | -0.0086666 | 0.036621 | 0.07782 | 0.022888 | 0 | 0.073242 | -0.054932 | -0.20142 | 0.09613 | 0.09613 | 0.009155 | 0.068665 | 0.018311 | -0.09613 | -0.15564 | 122.5113 | 122.3648 | -0.10071 | 122.644 | 122.5662 | 0.20142 | -0.13733 | 122.4701 | 122.4106 | -0.10528 | 122.6624 | 122.5754 | 0.16479 | -0.15564 | 122.6395 | 122.6028 | 122.5891 | -0.37537 | 122.6349 | 122.5845 | 122.6624 | -0.32959
1320.1562 | 122.7768 | -122.5388 | 0.16022 | 0.029907 | 0.017838 | 0.0048706 | 0.0029821 | -0.0049796 | -0.0039798 | -0.0054475 | 0.048599 | -0.0097775 | -0.0073208 | -0.00048061 | 0.0028263 | -0.0097348 | 0.041199 | 0.041199 | 0.041199 | 0.022888 | 0.14191 | 0.009155 | -0.15106 | 0.091553 | 0.13275 | 0.009155 | 0.10986 | 0.07782 | -0.068665 | -0.1236 | 122.5479 | 122.3877 | -0.01831 | 122.58 | 122.5616 | 0.17395 | -0.11902 | 122.4701 | 122.4152 | -0.050354 | 122.6303 | 122.5479 | 0.13275 | -0.082397 | 122.6807 | 122.58 | 122.58 | -0.31128 | 122.6486 | 122.6166 | 122.6715 | -0.28381
1321.8438 | 122.731 | -122.5708 | 0.17853 | 0.14435 | 0.01976 | 0.0035888 | 0.0031957 | -0.0043386 | 0.00050622 | -0.0041657 | 0.10963 | -0.0084957 | -0.0053982 | -0.0015488 | 0.0043215 | -0.010589 | 0.054932 | 0.050354 | 0.036621 | -0.004578 | 0.064087 | -0.050354 | -0.20142 | 0.10529 | 0.073242 | -0.027466 | 0.041199 | 0.018311 | -0.10529 | -0.19684 | 122.5204 | 122.3694 | -0.11444 | 122.6212 | 122.5662 | 0.19684 | -0.1236 | 122.4655 | 122.374 | -0.13733 | 122.6761 | 122.5433 | 0.16937 | -0.16022 | 122.6349 | 122.6257 | 122.6074 | -0.37994 | 122.612 | 122.5891 | 122.644 | -0.37537
1323.5469 | 122.8271 | -122.5433 | 0.15106 | -0.18372 | 0.018906 | 0.0050842 | 0.0042639 | -0.0073294 | 7.902e-05 | -0.0045929 | -0.23369 | -0.0089229 | -0.0047574 | -0.0024032 | 0.0038943 | -0.012298 | 0.17395 | 0.16479 | 0.1236 | 0.1236 | 0.20142 | 0.041199 | -0.10071 | 0.1236 | 0.21057 | 0.027466 | 0.16937 | 0.13275 | -0.032043 | -0.086975 | 122.5845 | 122.4426 | 0.050354 | 122.7081 | 122.6669 | 0.2243 | 0.022888 | 122.5113 | 122.4564 | 0.018311 | 122.6669 | 122.5708 | 0.11444 | -0.018311 | 122.7448 | 122.7173 | 122.6669 | -0.25177 | 122.7127 | 122.6761 | 122.7539 | -0.23804
1325.2188 | 122.8134 | -122.4976 | 0.16479 | -0.2829 | 0.018478 | 0.0059388 | 0.0061865 | -0.0073294 | 0.00029262 | -0.0033111 | -0.23369 | -0.0095639 | -0.0047574 | -0.0021896 | 0.0038943 | -0.010162 | 0.16022 | 0.13275 | 0.10071 | 0.09613 | 0.23346 | 0.050354 | -0.086975 | 0.086975 | 0.15564 | 0.004578 | 0.17395 | 0.14648 | -0.041199 | -0.10529 | 122.5479 | 122.4106 | 0.068664 | 122.6303 | 122.5937 | 0.1831 | -0.004578 | 122.4564 | 122.3923 | 0.009155 | 122.5845 | 122.5021 | 0.10986 | -0.018311 | 122.731 | 122.6578 | 122.5983 | -0.25177 | 122.6715 | 122.644 | 122.6532 | -0.27008
1326.8906 | 122.8729 | -122.493 | 0.13733 | -0.00061023 | 0.01741 | 0.0052978 | 0.0027685 | -0.0047658 | -0.0037662 | -0.0048065 | -0.020065 | -0.0097775 | -0.0041164 | 0.00016019 | 0.0023989 | -0.0093076 | 0.050354 | 0.064087 | 0.054932 | 0.045776 | 0.15106 | -0.009155 | -0.13733 | 0.10986 | 0.17853 | 0.050354 | 0.10986 | 0.091553 | -0.045776 | -0.11444 | 122.4838 | 122.3557 | 0.013733 | 122.5571 | 122.5388 | 0.18311 | -0.086975 | 122.4472 | 122.3785 | -0.027466 | 122.6028 | 122.5433 | 0.16479 | -0.045776 | 122.644 | 122.5433 | 122.5479 | -0.27466 | 122.6028 | 122.5845 | 122.6715 | -0.25177
1328.5781 | 122.7905 | -122.5159 | 0.15564 | 0.12909 | 0.019119 | 0.0027344 | 0.0014867 | -0.0071158 | 0.0032834 | -0.0030975 | 0.12489 | -0.0074277 | -0.0073208 | -5.3406e-05 | 0.0058169 | -0.011017 | -0.009155 | -0.068665 | -0.10071 | -0.073242 | 0.10986 | -0.082397 | -0.23346 | 0.027466 | -0.064087 | -0.082397 | 0.050354 | 0.022888 | -0.13733 | -0.1831 | 122.4335 | 122.2824 | -0.045777 | 122.4472 | 122.4426 | 0.16022 | -0.16479 | 122.3785 | 122.3328 | -0.10529 | 122.5433 | 122.4335 | 0.10071 | -0.13275 | 122.6257 | 122.5067 | 122.4152 | -0.3891 | 122.5662 | 122.5388 | 122.4518 | -0.33874
1330.25 | 122.7768 | -122.5342 | 0.13733 | 0.052795 | 0.018051 | 0.0052978 | 0.0023413 | -0.0060476 | -0.004407 | -0.0054475 | 0.086746 | -0.0093503 | -0.0068936 | -0.0011216 | 0.0026125 | -0.0080258 | 0.045776 | 0.050354 | 0.045776 | 0.027466 | 0.14648 | 0 | -0.14191 | 0.10071 | 0.1236 | 0.009155 | 0.10071 | 0.064087 | -0.068665 | -0.12817 | 122.5342 | 122.3923 | 0.009155 | 122.5845 | 122.5616 | 0.16937 | -0.091553 | 122.4655 | 122.406 | -0.036621 | 122.6349 | 122.5433 | 0.13733 | -0.073242 | 122.6807 | 122.58 | 122.58 | -0.27924 | 122.6349 | 122.5983 | 122.6578 | -0.2655
1331.9844 | 122.8729 | -122.4976 | 0.14191 | -0.10742 | 0.016983 | 0.0031616 | 0.0061865 | -0.0036978 | -0.0041934 | -0.0041657 | -0.14214 | -0.0084957 | -0.006039 | -0.0013352 | 0.0038943 | -0.012512 | 0.17395 | 0.21515 | 0.16022 | 0.14191 | 0.18768 | 0.059509 | -0.09613 | 0.16937 | 0.27924 | 0.11444 | 0.12817 | 0.10071 | -0.027466 | -0.082397 | 122.5571 | 122.4014 | 0.045776 | 122.7127 | 122.6395 | 0.23804 | 0.032043 | 122.4701 | 122.4152 | -0.013733 | 122.6669 | 122.612 | 0.19684 | -0.041199 | 122.6852 | 122.6715 | 122.6578 | -0.23804 | 122.6257 | 122.5983 | 122.7768 | -0.2243
1333.6562 | 122.8317 | -122.5388 | 0.16479 | -0.23712 | 0.020187 | 0.0050842 | 0.0066137 | -0.002416 | -0.00034818 | -0.0024567 | -0.23369 | -0.0093503 | -0.003262 | -0.001976 | 0.0015445 | -0.012085 | 0.13275 | 0.1236 | 0.082397 | 0.09613 | 0.23804 | 0.045776 | -0.09613 | 0.064087 | 0.13275 | -0.022888 | 0.16479 | 0.14648 | -0.054932 | -0.11444 | 122.5845 | 122.4426 | 0.073242 | 122.6624 | 122.6349 | 0.19226 | -0.032044 | 122.4838 | 122.4243 | 0 | 122.6028 | 122.5159 | 0.091553 | -0.018311 | 122.7768 | 122.6715 | 122.6212 | -0.26092 | 122.7036 | 122.6852 | 122.6715 | -0.27924
1335.3438 | 122.7631 | -122.5708 | 0.15564 | 0.022278 | 0.022324 | 0.0031616 | 0.0034093 | -0.0054068 | 0.003497 | -0.0037385 | -0.08873 | -0.0050777 | -0.0043302 | 0.001442 | 0.0068851 | -0.010803 | -0.009155 | -0.050354 | -0.082397 | -0.054932 | 0.12817 | -0.059509 | -0.21973 | -0.032043 | -0.12817 | -0.16479 | 0.10529 | 0.059509 | -0.13275 | -0.21515 | 122.5113 | 122.3511 | -0.027466 | 122.5204 | 122.5159 | 0.16479 | -0.16479 | 122.4381 | 122.3557 | -0.050354 | 122.5388 | 122.406 | 0.050354 | -0.096131 | 122.699 | 122.5616 | 122.4884 | -0.37537 | 122.6761 | 122.6303 | 122.4426 | -0.37079
1337.0156 | 122.7859 | -122.5342 | 0.16479 | 0.16724 | 0.020401 | 0.004657 | 0.0012731 | -0.0056204 | 0.0015744 | -0.00074767 | 0.094375 | -0.0084957 | -0.0053982 | 0.0012284 | 0.0079531 | -0.0099484 | 0.032043 | 0.013733 | -0.009155 | -0.009155 | 0.073242 | -0.064087 | -0.2243 | 0.073242 | 0.013733 | -0.041199 | 0.041199 | 0.004578 | -0.11444 | -0.17395 | 122.4701 | 122.3099 | -0.091553 | 122.5479 | 122.525 | 0.21515 | -0.13275 | 122.4197 | 122.3602 | -0.1236 | 122.6074 | 122.493 | 0.13275 | -0.16022 | 122.6074 | 122.5662 | 122.525 | -0.3891 | 122.5754 | 122.5388 | 122.5479 | -0.33874
1338.6875 | 122.7631 | -122.5525 | 0.17853 | 0.045166 | 0.022537 | 0.0014526 | 0.0027685 | -0.0079702 | 0.003497 | -0.0028839 | 0.048599 | -0.0055051 | -0.0068936 | -0.00069421 | 0.0058169 | -0.009094 | -0.027466 | -0.11444 | -0.10986 | -0.073242 | 0.11902 | -0.082397 | -0.21057 | -0.054932 | -0.12817 | -0.16937 | 0.10071 | 0.059509 | -0.14648 | -0.21057 | 122.4701 | 122.3419 | -0.059509 | 122.438 | 122.4792 | 0.13733 | -0.20599 | 122.406 | 122.3419 | -0.07782 | 122.4976 | 122.3831 | 0.041198 | -0.11902 | 122.6715 | 122.525 | 122.4426 | -0.3891 | 122.6532 | 122.612 | 122.4243 | -0.3891
1340.375 | 122.7585 | -122.5662 | 0.17395 | 0.052795 | 0.02211 | 0.0040162 | 0.0019141 | -0.005834 | 0.0026424 | -0.0020295 | 0.0028229 | -0.0059323 | -0.0062528 | 0.00080099 | 0.0049625 | -0.010589 | -0.018311 | -0.10986 | -0.10071 | -0.064087 | 0.11444 | -0.07782 | -0.23804 | -0.059509 | -0.13275 | -0.16937 | 0.091553 | 0.07782 | -0.15106 | -0.21057 | 122.4884 | 122.3282 | -0.059509 | 122.4564 | 122.5021 | 0.17395 | -0.19226 | 122.4152 | 122.3557 | -0.082397 | 122.5067 | 122.3969 | 0.041198 | -0.09613 | 122.6807 | 122.5479 | 122.4655 | -0.41199 | 122.6578 | 122.644 | 122.4335 | -0.38452
1342.0469 | 122.7905 | -122.5479 | 0.16479 | 0.13672 | 0.022324 | 0.002948 | 0.0044775 | -0.0047658 | 0.00050622 | -0.0024567 | 0.079117 | -0.0074277 | -0.0051846 | -0.0013352 | 0.0053897 | -0.009094 | -0.050354 | -0.10071 | -0.12817 | -0.091553 | 0.10986 | -0.09613 | -0.25177 | -0.036621 | -0.11444 | -0.13275 | 0.091553 | 0.064087 | -0.13733 | -0.2243 | 122.4518 | 122.2961 | -0.054932 | 122.4472 | 122.4564 | 0.16022 | -0.21515 | 122.4106 | 122.3236 | -0.073242 | 122.5113 | 122.4152 | 0.091553 | -0.10071 | 122.6578 | 122.4976 | 122.4197 | -0.41656 | 122.6395 | 122.612 | 122.4335 | -0.3891
1343.75 | 122.8455 | -122.5479 | 0.13733 | -0.24475 | 0.020401 | 0.0018798 | 0.0091773 | -0.0032706 | -0.0039798 | -0.0056611 | -0.15739 | -0.0089229 | -0.0019802 | -0.001976 | -0.0010191 | -0.011017 | 0.073242 | 0.082397 | 0.073242 | 0.059509 | 0.24261 | 0.041199 | -0.091553 | 0.045776 | 0.13733 | -0.009155 | 0.1831 | 0.15106 | -0.054932 | -0.11902 | 122.5891 | 122.4564 | 0.10529 | 122.6303 | 122.6074 | 0.15106 | -0.064087 | 122.493 | 122.4289 | 0.045776 | 122.5937 | 122.5388 | 0.10986 | 0.013733 | 122.7905 | 122.6212 | 122.6212 | -0.22888 | 122.731 | 122.699 | 122.6852 | -0.25635
1345.4375 | 122.818 | -122.5342 | 0.16022 | 0.13672 | 0.019547 | 0.0038024 | 0.0042639 | -0.0073294 | 0.00071982 | -0.0037385 | 0.14015 | -0.0089229 | -0.006039 | -0.00069421 | 0.0041079 | -0.0086666 | -0.041199 | -0.064087 | -0.082397 | -0.073242 | 0.10071 | -0.082397 | -0.23346 | 0.032043 | -0.045776 | -0.054932 | 0.059509 | 0.009155 | -0.12817 | -0.19226 | 122.4518 | 122.3007 | -0.059509 | 122.4701 | 122.4609 | 0.16022 | -0.20142 | 122.406 | 122.3419 | -0.10071 | 122.5662 | 122.4792 | 0.13733 | -0.15106 | 122.6349 | 122.493 | 122.4518 | -0.39368 | 122.5937 | 122.5433 | 122.4884 | -0.35248
1347.1406 | 122.7905 | -122.5525 | 0.16022 | 0.15961 | 0.019547 | 0.0048706 | 0.0017005 | -0.0056204 | -0.0018436 | -0.0035249 | 0.19356 | -0.0076413 | -0.0071072 | -0.001976 | 0.0041079 | -0.0097348 | 0.027466 | 0.004578 | 0 | -0.009155 | 0.050354 | -0.054932 | -0.20599 | 0.059509 | 0.027466 | -0.022888 | 0.013733 | -0.004578 | -0.13733 | -0.1831 | 122.4976 | 122.3465 | -0.10986 | 122.5571 | 122.5433 | 0.19684 | -0.13275 | 122.4152 | 122.3694 | -0.14648 | 122.612 | 122.5296 | 0.16022 | -0.16479 | 122.6028 | 122.58 | 122.5525 | -0.36621 | 122.5662 | 122.5479 | 122.58 | -0.34332
1348.8281 | 122.8867 | -122.5159 | 0.13733 | -0.084534 | 0.019119 | 0.0067932 | 0.0053321 | -0.0079702 | -0.0054752 | -0.0054475 | -0.042954 | -0.010205 | -0.006039 | -0.0021896 | -0.0012327 | -0.0088804 | 0.13275 | 0.1236 | 0.11902 | 0.10071 | 0.16937 | 0.032043 | -0.11902 | 0.16022 | 0.24261 | 0.11902 | 0.11902 | 0.10071 | -0.041199 | -0.09613 | 122.5479 | 122.3969 | 0.032044 | 122.6395 | 122.6166 | 0.21973 | -0.004578 | 122.4747 | 122.4197 | -0.01831 | 122.6761 | 122.6349 | 0.21515 | -0.036621 | 122.6852 | 122.6486 | 122.6349 | -0.25635 | 122.6349 | 122.6166 | 122.7585 | -0.23346
1350.5 | 122.8912 | -122.5159 | 0.1236 | -0.13794 | 0.018906 | 0.0061524 | 0.010245 | -0.0060476 | -0.0052616 | -0.0056611 | -0.065842 | -0.0099911 | -0.0039028 | 0.00080099 | -0.00037807 | -0.0093076 | 0.16479 | 0.15106 | 0.14191 | 0.11444 | 0.19226 | 0.050354 | -0.10071 | 0.18768 | 0.27008 | 0.10529 | 0.13275 | 0.10529 | -0.045776 | -0.073242 | 122.5662 | 122.4152 | 0.068665 | 122.6669 | 122.6303 | 0.21515 | 0.041199 | 122.4701 | 122.4426 | 0.009155 | 122.7036 | 122.6212 | 0.17853 | -0.01831 | 122.7081 | 122.6807 | 122.6578 | -0.2243 | 122.6486 | 122.6212 | 122.7859 | -0.19684
1352.1875 | 122.8592 | -122.525 | 0.12817 | -0.24475 | 0.02211 | 0.0042298 | 0.0096045 | -0.0060476 | 7.902e-05 | -0.0050201 | -0.26421 | -0.0089229 | -0.0019802 | 0.00058739 | 0.0032535 | -0.012726 | 0.086975 | 0.054932 | 0.041199 | 0.054932 | 0.2655 | 0.045776 | -0.11902 | 0.054932 | 0.086975 | -0.027466 | 0.1831 | 0.16479 | -0.073242 | -0.12817 | 122.5708 | 122.406 | 0.13733 | 122.58 | 122.58 | 0.17395 | -0.041199 | 122.4518 | 122.3969 | 0.054931 | 122.58 | 122.4976 | 0.10071 | 0.036621 | 122.7905 | 122.612 | 122.5662 | -0.24719 | 122.7081 | 122.6898 | 122.612 | -0.25635
1353.8594 | 122.8455 | -122.5159 | 0.13733 | -0.16846 | 0.020615 | 0.0055114 | 0.0085363 | -0.0022024 | -0.0039798 | -0.0060883 | -0.16502 | -0.011487 | -0.0030484 | 0.00016019 | 0.00047633 | -0.011871 | 0.16479 | 0.19684 | 0.17853 | 0.13275 | 0.19684 | 0.054932 | -0.068665 | 0.15564 | 0.26093 | 0.10529 | 0.13733 | 0.11444 | -0.027466 | -0.086975 | 122.5708 | 122.4472 | 0.059509 | 122.7127 | 122.6486 | 0.20142 | 0.027466 | 122.4884 | 122.4289 | 0 | 122.6715 | 122.6212 | 0.19226 | -0.022888 | 122.7127 | 122.6807 | 122.6944 | -0.20599 | 122.6532 | 122.6303 | 122.7768 | -0.2243
1355.5469 | 122.8729 | -122.5342 | 0.1236 | -0.10742 | 0.020187 | 0.0048706 | 0.0068273 | -0.0056204 | -0.0041934 | -0.0058747 | -0.14214 | -0.0078549 | -0.0030484 | -0.0011216 | 0.00047633 | -0.011444 | 0.17853 | 0.19684 | 0.16022 | 0.14191 | 0.17853 | 0.068665 | -0.086975 | 0.16022 | 0.27466 | 0.10071 | 0.12817 | 0.11444 | -0.018311 | -0.091553 | 122.6028 | 122.4472 | 0.054932 | 122.731 | 122.6761 | 0.22888 | 0.054932 | 122.5159 | 122.4426 | 0.004578 | 122.6944 | 122.6349 | 0.19226 | -0.009155 | 122.7127 | 122.7127 | 122.6944 | -0.21057 | 122.6624 | 122.6486 | 122.8088 | -0.21515
1357.2344 | 122.7905 | -122.5571 | 0.16022 | 0.052795 | 0.016556 | 0.0057252 | 0.0012731 | -0.004125 | -0.0031254 | -0.0052337 | 0.071487 | -0.0078549 | -0.0053982 | -0.00069421 | 0.0058169 | -0.0093076 | 0.064087 | 0.054932 | 0.032043 | 0.022888 | 0.14648 | -0.004578 | -0.15564 | 0.082397 | 0.10986 | 0.004578 | 0.10071 | 0.082397 | -0.064087 | -0.1236 | 122.5525 | 122.4014 | -0.013733 | 122.612 | 122.58 | 0.17853 | -0.09613 | 122.493 | 122.4335 | -0.059509 | 122.6395 | 122.5616 | 0.12817 | -0.07782 | 122.7036 | 122.6212 | 122.5891 | -0.31586 | 122.6578 | 122.6395 | 122.6669 | -0.28381
1358.9688 | 122.9187 | -122.4976 | 0.12817 | -0.19135 | 0.022324 | 0.0042298 | 0.0055457 | -0.0064748 | 0.0039242 | -0.0065155 | -0.23369 | -0.0070003 | -0.0034756 | -0.00048061 | 0.0051761 | -0.014435 | 0.10071 | 0.041199 | 0 | 0.059509 | 0.25635 | 0.013733 | -0.14191 | 0.059509 | 0.064087 | -0.064087 | 0.16479 | 0.12817 | -0.07782 | -0.14648 | 122.5113 | 122.3557 | 0.12817 | 122.5388 | 122.5571 | 0.20142 | -0.027466 | 122.4197 | 122.3511 | 0.036621 | 122.5571 | 122.4335 | 0.082397 | 0 | 122.7539 | 122.5983 | 122.4976 | -0.27008 | 122.6624 | 122.6257 | 122.5616 | -0.27466
1360.6406 | 122.8455 | -122.5571 | 0.15564 | -0.084534 | 0.021256 | 0.0031616 | 0.0038367 | -0.005834 | 0.0043514 | -0.0035249 | -0.14977 | -0.0070003 | -0.0043302 | -0.00026701 | 0.0068851 | -0.011657 | 0.09613 | 0.032043 | -0.013733 | 0.022888 | 0.16022 | -0.036621 | -0.17395 | 0.068665 | 0.018311 | -0.059509 | 0.086975 | 0.082397 | -0.13275 | -0.17853 | 122.5204 | 122.3831 | 0.004577 | 122.5891 | 122.58 | 0.19684 | -0.05951 | 122.4243 | 122.3785 | -0.068665 | 122.6257 | 122.4976 | 0.11902 | -0.073243 | 122.7173 | 122.6532 | 122.5433 | -0.32959 | 122.644 | 122.6395 | 122.5754 | -0.33417
1362.3281 | 122.8958 | -122.5342 | 0.13275 | -0.084534 | 0.018051 | 0.0044434 | 0.0049047 | -0.0064748 | -0.0059024 | -0.0054475 | -0.073471 | -0.0095639 | -0.004971 | -0.0015488 | -0.00059167 | -0.008453 | 0.082397 | 0.12817 | 0.11444 | 0.082397 | 0.16479 | 0.018311 | -0.12817 | 0.16022 | 0.24261 | 0.09613 | 0.13733 | 0.10529 | -0.032043 | -0.10071 | 122.5525 | 122.406 | 0.032044 | 122.6624 | 122.6166 | 0.21057 | -0.050354 | 122.5021 | 122.4335 | 0.004578 | 122.6944 | 122.6303 | 0.19684 | -0.027465 | 122.699 | 122.6166 | 122.6486 | -0.26093 | 122.6715 | 122.6395 | 122.7768 | -0.23346
1364.0312 | 122.7951 | -122.5754 | 0.1831 | 0.17487 | 0.021683 | 0.0016662 | 0.0021277 | -0.0054068 | 0.00093342 | -0.0037385 | 0.13252 | -0.0055051 | -0.0073208 | -0.00090781 | 0.0075259 | -0.013366 | -0.004578 | -0.036621 | -0.045776 | -0.032043 | 0.059509 | -0.082397 | -0.22888 | 0.07782 | 0.027466 | -0.027466 | 0.036621 | 0 | -0.10986 | -0.16022 | 122.493 | 122.3465 | -0.1236 | 122.5388 | 122.5433 | 0.19684 | -0.18768 | 122.4655 | 122.4152 | -0.14648 | 122.6532 | 122.5479 | 0.13275 | -0.1831 | 122.6349 | 122.5708 | 122.5296 | -0.41199 | 122.612 | 122.5754 | 122.6028 | -0.34332
1365.7031 | 122.7997 | -122.5708 | 0.16937 | 0.12909 | 0.021469 | 0.0050842 | 0.0021277 | -0.0022024 | 0.0028562 | -0.0020295 | 0.063858 | -0.0070003 | -0.004971 | -0.0015488 | 0.0060305 | -0.0099484 | -0.041199 | -0.10529 | -0.11902 | -0.082397 | 0.11902 | -0.10529 | -0.25635 | -0.004578 | -0.1236 | -0.12817 | 0.082397 | 0.045776 | -0.14648 | -0.19226 | 122.4655 | 122.3145 | -0.050354 | 122.4655 | 122.4884 | 0.17395 | -0.21057 | 122.4243 | 122.3785 | -0.086976 | 122.5662 | 122.4426 | 0.064087 | -0.1236 | 122.6898 | 122.5296 | 122.4518 | -0.42572 | 122.6532 | 122.6166 | 122.4472 | -0.36163
1367.375 | 122.7814 | -122.58 | 0.18768 | 0.068054 | 0.020828 | 0.0035888 | 0.0051183 | -0.0032706 | 0.0015744 | -0.0026703 | 0.071487 | -0.0072141 | -0.006039 | -0.0011216 | 0.0053897 | -0.012512 | -0.07782 | -0.11444 | -0.10986 | -0.082397 | 0.1236 | -0.086975 | -0.21973 | -0.036621 | -0.13733 | -0.16022 | 0.086975 | 0.045776 | -0.15564 | -0.2243 | 122.493 | 122.3602 | -0.064087 | 122.4655 | 122.4976 | 0.13733 | -0.2655 | 122.4243 | 122.3557 | -0.10071 | 122.5433 | 122.4197 | 0.064087 | -0.14191 | 122.7036 | 122.5021 | 122.4701 | -0.40741 | 122.6669 | 122.6257 | 122.4426 | -0.41199
1369.0469 | 122.8958 | -122.5159 | 0.14191 | -0.12268 | 0.021896 | 0.002948 | 0.0031957 | -0.0015616 | 0.0011472 | -0.0045929 | -0.14977 | -0.0076413 | -0.0045438 | -0.0013352 | 0.0038943 | -0.011444 | 0.068665 | 0.041199 | 0 | 0.054932 | 0.20142 | -0.013733 | -0.16479 | 0.059509 | 0.059509 | -0.050354 | 0.11902 | 0.10071 | -0.091553 | -0.16937 | 122.5021 | 122.3511 | 0.059509 | 122.5571 | 122.5708 | 0.21973 | -0.073242 | 122.4243 | 122.3465 | -0.022888 | 122.5754 | 122.4655 | 0.11902 | -0.041199 | 122.7173 | 122.5845 | 122.5159 | -0.3067 | 122.6349 | 122.6166 | 122.5754 | -0.31128
1370.7188 | 122.905 | -122.5204 | 0.13275 | -0.16846 | 0.023605 | 0.0035888 | 0.010245 | -0.0039114 | -0.00056178 | -0.0033111 | -0.19554 | -0.0072141 | -0.0024076 | -0.0015488 | 0.0038943 | -0.010376 | 0.059509 | 0.054932 | 0.018311 | 0.086975 | 0.21515 | 0.022888 | -0.11902 | 0.018311 | 0.064087 | -0.050354 | 0.14648 | 0.10986 | -0.086975 | -0.14191 | 122.5433 | 122.4014 | 0.082398 | 122.5754 | 122.6074 | 0.20599 | -0.073242 | 122.4335 | 122.3785 | 0.013733 | 122.5388 | 122.4701 | 0.091553 | -0.022888 | 122.7356 | 122.58 | 122.5388 | -0.25177 | 122.6669 | 122.6303 | 122.5845 | -0.27466
1372.4219 | 122.8867 | -122.5204 | 0.13733 | -0.26001 | 0.021683 | 0.0038024 | 0.0091773 | -0.0043386 | 0.00029262 | -0.0063019 | -0.18791 | -0.0072141 | -0.0051846 | -5.3406e-05 | 0.0019717 | -0.010162 | 0.068665 | 0.07782 | 0.032043 | 0.068665 | 0.27008 | 0.022888 | -0.11444 | 0.022888 | 0.086975 | -0.045776 | 0.18768 | 0.16022 | -0.064087 | -0.10529 | 122.5433 | 122.406 | 0.13275 | 122.5983 | 122.5891 | 0.18311 | -0.068664 | 122.4564 | 122.4152 | 0.050354 | 122.5433 | 122.4747 | 0.05951 | 0.022888 | 122.7905 | 122.5891 | 122.5525 | -0.25177 | 122.7081 | 122.6807 | 122.6074 | -0.24262
1374.0938 | 122.7448 | -122.5754 | 0.16022 | 0.11383 | 0.016983 | 0.0057252 | 0.00084592 | -0.0094656 | -0.006757 | -0.0033111 | 0.20882 | -0.0078549 | -0.0086026 | 0.00037379 | 0.0026125 | -0.0088804 | 0.018311 | 0.054932 | 0.027466 | 0 | 0.07782 | -0.054932 | -0.19684 | 0.073242 | 0.10071 | 0.004578 | 0.059509 | 0.032043 | -0.09613 | -0.14648 | 122.5204 | 122.3785 | -0.082397 | 122.6303 | 122.5754 | 0.19684 | -0.14191 | 122.4792 | 122.4289 | -0.10071 | 122.6486 | 122.58 | 0.15106 | -0.12817 | 122.6532 | 122.5937 | 122.6028 | -0.35706 | 122.6349 | 122.6074 | 122.6761 | -0.3067
1375.7656 | 122.8683 | -122.525 | 0.15106 | 0.014648 | 0.017624 | 0.0050842 | 0.0053321 | -0.0051932 | -0.0076114 | -0.0067291 | 0.056228 | -0.0084957 | -0.0071072 | -0.00069421 | 0.00068993 | -0.013366 | 0.032043 | 0.064087 | 0.041199 | 0.050354 | 0.15106 | -0.004578 | -0.14191 | 0.086975 | 0.16022 | 0.054932 | 0.10071 | 0.091553 | -0.054932 | -0.11902 | 122.5204 | 122.3831 | 0 | 122.5891 | 122.5754 | 0.19226 | -0.11902 | 122.4701 | 122.406 | -0.050354 | 122.612 | 122.58 | 0.17395 | -0.059509 | 122.6761 | 122.5571 | 122.5662 | -0.29297 | 122.6257 | 122.6166 | 122.6852 | -0.27008
1377.4375 | 122.8912 | -122.5388 | 0.13733 | -0.13794 | 0.019333 | 0.0061524 | 0.0040503 | -0.0060476 | -0.0052616 | -0.0058747 | -0.073471 | -0.010205 | -0.0086026 | -0.0017624 | 0.0013309 | -0.010162 | 0.16022 | 0.16937 | 0.14648 | 0.11902 | 0.19226 | 0.050354 | -0.10071 | 0.19226 | 0.28381 | 0.1236 | 0.12817 | 0.10986 | -0.036621 | -0.091553 | 122.5891 | 122.438 | 0.054932 | 122.7081 | 122.6578 | 0.21973 | 0.022888 | 122.5021 | 122.4472 | -0.009155 | 122.731 | 122.6624 | 0.21515 | -0.027466 | 122.731 | 122.699 | 122.6852 | -0.23804 | 122.6669 | 122.6486 | 122.8226 | -0.22888
1379.1094 | 122.7722 | -122.5296 | 0.17395 | 0.1825 | 0.019547 | 0.0048706 | -0.00064948 | -0.0045522 | -0.00077538 | -0.0058747 | 0.15541 | -0.0072141 | -0.0058254 | -0.001976 | 0.0043215 | -0.01123 | 0.041199 | 0.027466 | 0.013733 | -0.022888 | 0.027466 | -0.073242 | -0.21515 | 0.073242 | 0.059509 | 0 | 0.032043 | -0.004578 | -0.1236 | -0.17853 | 122.4564 | 122.3145 | -0.14648 | 122.5571 | 122.5067 | 0.19226 | -0.13275 | 122.406 | 122.3511 | -0.14191 | 122.6028 | 122.5296 | 0.17853 | -0.17853 | 122.5571 | 122.5708 | 122.5433 | -0.3891 | 122.5616 | 122.525 | 122.5891 | -0.35248
1380.7812 | 122.7585 | -122.5754 | 0.16022 | 0.16724 | 0.016556 | 0.002948 | 0.0025549 | -0.0032706 | -0.00056178 | -0.0039521 | 0.14015 | -0.0084957 | -0.0075344 | 0.00080099 | 0.0045351 | -0.01123 | 0.064087 | 0.032043 | 0.018311 | -0.022888 | 0.07782 | -0.059509 | -0.21515 | 0.091553 | 0.059509 | 0.004578 | 0.064087 | 0.018311 | -0.10071 | -0.18768 | 122.5159 | 122.3602 | -0.082397 | 122.6074 | 122.5525 | 0.19226 | -0.09613 | 122.4747 | 122.3877 | -0.09613 | 122.6669 | 122.58 | 0.19226 | -0.14191 | 122.6532 | 122.6395 | 122.5937 | -0.37537 | 122.6395 | 122.5937 | 122.6349 | -0.3479
1382.5 | 122.9095 | -122.5342 | 0.15564 | -0.18372 | 0.021469 | 0.0050842 | 0.0066137 | -0.0034842 | 0.0024288 | -0.0016021 | -0.24132 | -0.0076413 | -0.0041164 | -0.0013352 | 0.0047489 | -0.011017 | 0.09613 | 0.041199 | 0.022888 | 0.073242 | 0.23346 | 0.009155 | -0.14191 | 0.050354 | 0.059509 | -0.041199 | 0.15106 | 0.10986 | -0.09613 | -0.16937 | 122.5433 | 122.3923 | 0.077819 | 122.5754 | 122.6074 | 0.21515 | -0.05951 | 122.4381 | 122.3648 | -0.004578 | 122.5845 | 122.493 | 0.12817 | -0.045777 | 122.7676 | 122.6303 | 122.5571 | -0.29755 | 122.6852 | 122.644 | 122.5937 | -0.32501
1384.1719 | 122.7768 | -122.6074 | 0.16479 | -0.054016 | 0.024674 | 0.0020936 | 0.0051183 | -0.0062612 | 0.0028562 | -0.0033111 | -0.10399 | -0.0063595 | -0.0039028 | 0.0010148 | 0.0070987 | -0.0095212 | 0.068665 | 0.013733 | 0.004578 | 0 | 0.15564 | -0.045776 | -0.19226 | 0 | -0.027466 | -0.11444 | 0.10071 | 0.068665 | -0.13733 | -0.20142 | 122.5616 | 122.4152 | -0.009155 | 122.6212 | 122.6074 | 0.19226 | -0.09613 | 122.4701 | 122.406 | -0.064087 | 122.6074 | 122.493 | 0.086975 | -0.09613 | 122.7631 | 122.6761 | 122.612 | -0.35706 | 122.7081 | 122.6761 | 122.58 | -0.36621
1385.8438 | 122.8912 | -122.5525 | 0.13733 | -0.26001 | 0.01976 | 0.0040162 | 0.0072547 | -0.0060476 | -0.0024844 | -0.0048065 | -0.24895 | -0.011487 | -0.0041164 | -5.3406e-05 | 0.0026125 | -0.0093076 | 0.073242 | 0.082397 | 0.041199 | 0.073242 | 0.25635 | 0.045776 | -0.11444 | 0.050354 | 0.091553 | -0.041199 | 0.20599 | 0.14648 | -0.07782 | -0.13733 | 122.5983 | 122.438 | 0.11902 | 122.6349 | 122.6257 | 0.18768 | -0.064087 | 122.4747 | 122.4152 | 0.068665 | 122.6028 | 122.5113 | 0.09613 | 0.009155 | 122.8088 | 122.6257 | 122.5937 | -0.25177 | 122.7585 | 122.699 | 122.644 | -0.27466
1387.5312 | 122.8592 | -122.5525 | 0.15106 | -0.2066 | 0.022324 | 0.0059388 | 0.0059729 | -0.0039114 | -0.0035526 | -0.0041657 | -0.23369 | -0.0080685 | -0.0034756 | 0.00058739 | 0.0023989 | -0.010589 | 0.059509 | 0.059509 | 0.036621 | 0.041199 | 0.24261 | 0.036621 | -0.12817 | 0.054932 | 0.10986 | -0.022888 | 0.19684 | 0.15564 | -0.068665 | -0.11444 | 122.5891 | 122.4243 | 0.091553 | 122.612 | 122.5937 | 0.16937 | -0.091553 | 122.4838 | 122.438 | 0.045776 | 122.6074 | 122.5296 | 0.091553 | 0.004578 | 122.7951 | 122.612 | 122.5891 | -0.27924 | 122.7493 | 122.7081 | 122.6624 | -0.2655
1389.2344 | 122.7905 | -122.5525 | 0.16022 | 0.17487 | 0.019547 | 0.0052978 | 0.0014867 | -0.0045522 | -0.0029118 | -0.0067291 | 0.18593 | -0.0072141 | -0.00668 | -0.001976 | 0.0021853 | -0.011017 | 0.018311 | 0.045776 | 0.009155 | -0.009155 | 0.041199 | -0.064087 | -0.20599 | 0.050354 | 0.027466 | -0.018311 | 0.004578 | -0.022888 | -0.13733 | -0.19684 | 122.4884 | 122.3465 | -0.11902 | 122.5983 | 122.5433 | 0.19684 | -0.14191 | 122.4152 | 122.3557 | -0.15564 | 122.6028 | 122.5342 | 0.17853 | -0.1831 | 122.5937 | 122.5708 | 122.5616 | -0.36621 | 122.5571 | 122.5296 | 122.58 | -0.35706
1390.9688 | 122.85 | -122.5342 | 0.14191 | -0.19135 | 0.017624 | 0.0033752 | 0.0070409 | -0.0064748 | -0.005048 | -0.0052337 | -0.12688 | -0.0074277 | -0.0028348 | -0.00069421 | 0.00026273 | -0.011657 | 0.16022 | 0.17853 | 0.15564 | 0.14191 | 0.20142 | 0.068665 | -0.086975 | 0.13275 | 0.26093 | 0.09613 | 0.12817 | 0.1236 | -0.032043 | -0.10986 | 122.6028 | 122.4472 | 0.059509 | 122.7127 | 122.6761 | 0.22888 | 0.01831 | 122.5021 | 122.4243 | -0.013733 | 122.6669 | 122.6303 | 0.20599 | -0.018311 | 122.7356 | 122.6944 | 122.6898 | -0.22888 | 122.6624 | 122.6578 | 122.7951 | -0.25177
1392.6562 | 122.7722 | -122.5845 | 0.16479 | 0.13672 | 0.021896 | 0.0038024 | 0.0070409 | -0.0066884 | -0.00163 | -0.0043793 | 0.14778 | -0.0080685 | -0.0030484 | 0.00080099 | 0.0015445 | -0.0095212 | 0.032043 | 0.045776 | 0.041199 | 0 | 0.054932 | -0.059509 | -0.18768 | 0.082397 | 0.064087 | -0.009155 | 0.050354 | 0.013733 | -0.1236 | -0.17853 | 122.525 | 122.3969 | -0.10986 | 122.6303 | 122.5845 | 0.18768 | -0.13275 | 122.4609 | 122.406 | -0.11444 | 122.6669 | 122.5754 | 0.16937 | -0.15106 | 122.6395 | 122.6166 | 122.6257 | -0.35248 | 122.6349 | 122.5983 | 122.6486 | -0.34332
1394.3594 | 122.8409 | -122.5616 | 0.15564 | -0.076904 | 0.023392 | 0.002948 | 0.0042639 | -0.0045522 | 0.0024288 | -0.0030975 | -0.16502 | -0.0059323 | -0.0028348 | 0.0010148 | 0.0058169 | -0.013153 | 0.086975 | 0.050354 | 0 | 0.032043 | 0.16937 | -0.009155 | -0.18768 | 0.045776 | 0.009155 | -0.07782 | 0.10986 | 0.073242 | -0.11902 | -0.17853 | 122.5525 | 122.374 | 0.013733 | 122.612 | 122.5937 | 0.21973 | -0.068665 | 122.4426 | 122.3831 | -0.045777 | 122.6074 | 122.4838 | 0.10071 | -0.082398 | 122.731 | 122.6486 | 122.5616 | -0.34332 | 122.6715 | 122.6349 | 122.5708 | -0.33417
1396.0312 | 122.7951 | -122.58 | 0.17395 | -0.054016 | 0.022965 | 0.0038024 | 0.0029821 | -0.004125 | 0.0024288 | -0.0033111 | -0.081101 | -0.0065731 | -0.0045438 | -0.0017624 | 0.0062441 | -0.010376 | 0.045776 | 0.009155 | -0.036621 | 0.013733 | 0.16022 | -0.036621 | -0.17853 | 0.004578 | -0.032043 | -0.10071 | 0.10071 | 0.07782 | -0.12817 | -0.19684 | 122.5433 | 122.4014 | -0.013733 | 122.5891 | 122.5937 | 0.19226 | -0.12817 | 122.4518 | 122.3831 | -0.073242 | 122.5845 | 122.4792 | 0.09613 | -0.09613 | 122.7402 | 122.6257 | 122.5433 | -0.35248 | 122.6807 | 122.6578 | 122.5479 | -0.37079
1397.7656 | 122.905 | -122.5616 | 0.14191 | -0.23712 | 0.018478 | 0.0044434 | 0.0042639 | -0.0077566 | -0.002698 | -0.0041657 | -0.23369 | -0.0072141 | -0.00668 | -0.00090781 | 0.0036807 | -0.011017 | 0.073242 | 0.073242 | 0.036621 | 0.073242 | 0.27008 | 0.032043 | -0.09613 | 0.036621 | 0.086975 | -0.050354 | 0.1831 | 0.16937 | -0.068665 | -0.11902 | 122.5937 | 122.4655 | 0.12817 | 122.6349 | 122.6349 | 0.16937 | -0.068665 | 122.493 | 122.4426 | 0.041198 | 122.5983 | 122.5113 | 0.068665 | 0.027466 | 122.8317 | 122.6349 | 122.5983 | -0.23804 | 122.7448 | 122.731 | 122.6486 | -0.26093
1399.5 | 122.8088 | -122.5708 | 0.15564 | 0.17487 | 0.020401 | 0.0033752 | 0.0010595 | -0.0064748 | -0.0012028 | -0.0028839 | 0.15541 | -0.0082821 | -0.0058254 | -0.00090781 | 0.0058169 | -0.0097348 | 0.018311 | 0.032043 | 0 | 0.009155 | 0.068665 | -0.054932 | -0.20599 | 0.068665 | 0.027466 | -0.027466 | 0.009155 | 0.009155 | -0.12817 | -0.19226 | 122.5159 | 122.3648 | -0.086975 | 122.6028 | 122.58 | 0.21515 | -0.13733 | 122.4426 | 122.3785 | -0.14649 | 122.6395 | 122.5433 | 0.16479 | -0.14649 | 122.6395 | 122.5891 | 122.5708 | -0.36163 | 122.58 | 122.58 | 122.5983 | -0.3479
1401.1875 | 122.8638 | -122.5296 | 0.16479 | -0.076904 | 0.022537 | 0.0010254 | 0.0042639 | -0.0047658 | 0.0022152 | -0.0018159 | -0.14214 | -0.0061459 | -0.0028348 | -0.00090781 | 0.0045351 | -0.012298 | 0.082397 | 0.045776 | 0.018311 | 0.027466 | 0.17395 | -0.009155 | -0.17395 | 0.054932 | 0.041199 | -0.050354 | 0.10071 | 0.064087 | -0.1236 | -0.17395 | 122.5204 | 122.3557 | 0.009155 | 122.5754 | 122.5571 | 0.20142 | -0.082398 | 122.406 | 122.3557 | -0.064087 | 122.5845 | 122.4792 | 0.1236 | -0.10071 | 122.7036 | 122.612 | 122.5479 | -0.33874 | 122.6303 | 122.5937 | 122.5708 | -0.33874
1402.9375 | 122.8226 | -122.5571 | 0.16937 | 0.1062 | 0.020401 | 0.0048706 | 0.0027685 | -0.0047658 | -0.00034818 | -0.0041657 | 0.1783 | -0.0091367 | -0.0039028 | -5.3406e-05 | 0.0034671 | -0.010589 | -0.050354 | -0.091553 | -0.09613 | -0.059509 | 0.10071 | -0.091553 | -0.22888 | 0.004578 | -0.064087 | -0.073242 | 0.041199 | 0.022888 | -0.12817 | -0.19684 | 122.4655 | 122.3282 | -0.068665 | 122.4655 | 122.4976 | 0.16937 | -0.21973 | 122.4289 | 122.3602 | -0.12817 | 122.5616 | 122.4838 | 0.1236 | -0.14649 | 122.6578 | 122.5067 | 122.4609 | -0.39826 | 122.5983 | 122.58 | 122.493 | -0.36621
1404.6094 | 122.7722 | -122.5845 | 0.16479 | 0.26642 | 0.015701 | 0.006366 | 0.0053321 | -0.0064748 | -0.0065434 | -0.0026703 | 0.14778 | -0.0076413 | -0.0075344 | -0.00026701 | 0.0013309 | -0.0082394 | 0.018311 | 0.036621 | 0.022888 | 0.027466 | 0.11902 | -0.032043 | -0.16937 | 0.054932 | 0.09613 | 0.004578 | 0.09613 | 0.054932 | -0.073242 | -0.14191 | 122.5525 | 122.4152 | -0.045776 | 122.6212 | 122.612 | 0.19684 | -0.14648 | 122.5113 | 122.4426 | -0.068665 | 122.6395 | 122.5891 | 0.14649 | -0.10986 | 122.7036 | 122.6028 | 122.6074 | -0.33417 | 122.6807 | 122.6395 | 122.6807 | -0.3067
1406.2812 | 122.7859 | -122.6028 | 0.16022 | 0.045166 | 0.017624 | 0.0040162 | 0.0031957 | -0.0062612 | -0.0059024 | -0.0058747 | 0.094375 | -0.010418 | -0.004971 | -0.00026701 | 0.0021853 | -0.0095212 | 0.027466 | 0.027466 | 0.032043 | 0.032043 | 0.12817 | -0.004578 | -0.15106 | 0.054932 | 0.10071 | 0 | 0.10071 | 0.082397 | -0.073242 | -0.13733 | 122.5983 | 122.4518 | -0.032043 | 122.6303 | 122.6349 | 0.18311 | -0.13275 | 122.5296 | 122.4655 | -0.059509 | 122.6578 | 122.6028 | 0.13733 | -0.07782 | 122.731 | 122.6303 | 122.6349 | -0.31128 | 122.7036 | 122.6852 | 122.7036 | -0.29755
1407.9844 | 122.9279 | -122.525 | 0.15106 | -0.1532 | 0.022537 | 0.0050842 | 0.0074683 | -0.0062612 | 0.0024288 | -0.0050201 | -0.24132 | -0.0082821 | -0.003262 | -5.3406e-05 | 0.0038943 | -0.012085 | 0.07782 | 0.027466 | 0.009155 | 0.054932 | 0.24719 | 0.022888 | -0.11444 | 0.050354 | 0.059509 | -0.054932 | 0.15106 | 0.13275 | -0.07782 | -0.13275 | 122.5479 | 122.4106 | 0.09613 | 122.5525 | 122.58 | 0.16937 | -0.073242 | 122.4472 | 122.3923 | 0 | 122.5754 | 122.4701 | 0.077819 | -0.018311 | 122.7722 | 122.6028 | 122.5342 | -0.2655 | 122.6761 | 122.6578 | 122.5845 | -0.28381
1409.6562 | 122.8134 | -122.5708 | 0.16022 | -0.061646 | 0.025101 | 0.0031616 | 0.0053321 | -0.0081838 | 0.0037106 | -0.0056611 | -0.13451 | -0.0074277 | -0.0024076 | -0.00026701 | 0.0068851 | -0.010589 | 0.082397 | 0.027466 | 0.009155 | 0.022888 | 0.16937 | -0.013733 | -0.17395 | 0.041199 | -0.032043 | -0.082397 | 0.10986 | 0.064087 | -0.11444 | -0.16937 | 122.5571 | 122.3969 | 0.009156 | 122.5983 | 122.5937 | 0.19684 | -0.07782 | 122.4564 | 122.4014 | -0.050354 | 122.612 | 122.4884 | 0.086976 | -0.09613 | 122.7402 | 122.6532 | 122.58 | -0.33417 | 122.6807 | 122.6349 | 122.5388 | -0.32959
1411.3281 | 122.7814 | -122.5708 | 0.17395 | 0.068054 | 0.023178 | 0.001239 | 0.0036231 | -0.0056204 | 0.0024288 | -0.0035249 | 0.048599 | -0.0055051 | -0.0030484 | 0.001442 | 0.0056033 | -0.010803 | -0.07782 | -0.10986 | -0.11444 | -0.068665 | 0.14191 | -0.07782 | -0.23346 | -0.045776 | -0.11444 | -0.16022 | 0.07782 | 0.064087 | -0.15564 | -0.21057 | 122.493 | 122.3373 | -0.032043 | 122.4609 | 122.5021 | 0.16479 | -0.25177 | 122.4152 | 122.3602 | -0.09613 | 122.525 | 122.4106 | 0.050354 | -0.10986 | 122.7127 | 122.493 | 122.4564 | -0.40741 | 122.6486 | 122.6349 | 122.4564 | -0.38452
1413.0625 | 122.8226 | -122.5662 | 0.17853 | 0.12909 | 0.022751 | 0.004657 | 0.0027685 | -0.0054068 | -0.00013458 | -0.0028839 | 0.079117 | -0.0074277 | -0.0043302 | 0.00058739 | 0.0062441 | -0.010803 | -0.086975 | -0.10529 | -0.12817 | -0.082397 | 0.11902 | -0.082397 | -0.25177 | -0.050354 | -0.12817 | -0.15106 | 0.086975 | 0.032043 | -0.16937 | -0.20599 | 122.4838 | 122.3145 | -0.059509 | 122.4609 | 122.4838 | 0.16937 | -0.2655 | 122.3969 | 122.3602 | -0.091553 | 122.5159 | 122.4152 | 0.054932 | -0.14648 | 122.6852 | 122.4792 | 122.438 | -0.4303 | 122.6532 | 122.5983 | 122.438 | -0.38452
1414.7656 | 122.8134 | -122.5891 | 0.16937 | 0.098572 | 0.023605 | 0.0027344 | 0.0029821 | -0.0062612 | -0.00098918 | -0.0050201 | 0.094375 | -0.0067867 | -0.0028348 | -0.00090781 | 0.0036807 | -0.0097348 | -0.082397 | -0.09613 | -0.12817 | -0.082397 | 0.1236 | -0.07782 | -0.24719 | -0.045776 | -0.11902 | -0.15106 | 0.086975 | 0.054932 | -0.14648 | -0.21973 | 122.5113 | 122.3419 | -0.045777 | 122.493 | 122.5067 | 0.16479 | -0.25177 | 122.4426 | 122.3694 | -0.082398 | 122.5433 | 122.438 | 0.068665 | -0.11444 | 122.7127 | 122.5067 | 122.4609 | -0.41656 | 122.6761 | 122.644 | 122.4701 | -0.3891
1416.4375 | 122.7859 | -122.5662 | 0.1831 | 0.19012 | 0.020401 | 0.0070068 | 0.0023413 | -0.0088248 | -0.0048344 | -0.0045929 | 0.18593 | -0.0087093 | -0.0056118 | 0.00037379 | 0.0038943 | -0.0097348 | 0.004578 | 0.041199 | 0.027466 | -0.013733 | 0.059509 | -0.082397 | -0.21973 | 0.07782 | 0.073242 | 0 | 0.050354 | 0.027466 | -0.11444 | -0.1831 | 122.4838 | 122.3465 | -0.1236 | 122.6074 | 122.5525 | 0.20599 | -0.17853 | 122.4518 | 122.3831 | -0.13275 | 122.644 | 122.5662 | 0.1831 | -0.15564 | 122.6257 | 122.5708 | 122.5937 | -0.40283 | 122.6166 | 122.5937 | 122.6395 | -0.36621
1418.125 | 122.8088 | -122.5891 | 0.17853 | 0.060425 | 0.015701 | 0.0057252 | 0.0053321 | -0.0062612 | -0.0054752 | -0.0077973 | 0.16304 | -0.0080685 | -0.0068936 | -0.0017624 | 0.0013309 | -0.0093076 | 0.018311 | 0.018311 | 0.045776 | 0.013733 | 0.10986 | -0.013733 | -0.16479 | 0.059509 | 0.10071 | 0 | 0.10529 | 0.09613 | -0.07782 | -0.12817 | 122.5754 | 122.4243 | -0.068665 | 122.6074 | 122.6028 | 0.17853 | -0.16022 | 122.5113 | 122.4609 | -0.073242 | 122.6486 | 122.5891 | 0.12817 | -0.082398 | 122.699 | 122.6074 | 122.6349 | -0.34332 | 122.6944 | 122.6852 | 122.6898 | -0.3067
1419.7969 | 122.7997 | -122.5662 | 0.16022 | 0.052795 | 0.016556 | 0.0044434 | 0.0053321 | -0.0071158 | -0.0063296 | -0.0056611 | 0.071487 | -0.0095639 | -0.0081754 | -0.0017624 | 0.00090353 | -0.0095212 | 0.050354 | 0.027466 | 0.027466 | 0.027466 | 0.14648 | -0.009155 | -0.14648 | 0.07782 | 0.10071 | 0 | 0.10071 | 0.082397 | -0.068665 | -0.13733 | 122.5571 | 122.4197 | -0.013733 | 122.5937 | 122.5937 | 0.17395 | -0.10986 | 122.4976 | 122.4289 | -0.059509 | 122.644 | 122.5662 | 0.13733 | -0.07782 | 122.7127 | 122.6166 | 122.5937 | -0.3067 | 122.6669 | 122.6486 | 122.6669 | -0.29755
1421.4844 | 122.818 | -122.5937 | 0.17395 | 0.12909 | 0.021683 | 0.0044434 | 0.0040503 | -0.004125 | 0.0032834 | -0.0073701 | 0.056228 | -0.0061459 | -0.0041164 | 0.0012284 | 0.0036807 | -0.010376 | -0.027466 | -0.12817 | -0.1236 | -0.07782 | 0.10986 | -0.09613 | -0.25635 | -0.022888 | -0.12817 | -0.14191 | 0.10529 | 0.050354 | -0.14648 | -0.19226 | 122.4976 | 122.3373 | -0.064087 | 122.4655 | 122.5159 | 0.17853 | -0.20142 | 122.4472 | 122.4014 | -0.068664 | 122.5708 | 122.4518 | 0.050354 | -0.1236 | 122.7036 | 122.5662 | 122.4701 | -0.4303 | 122.699 | 122.644 | 122.4655 | -0.36621
1423.1562 | 122.7997 | -122.5983 | 0.17395 | 0.090942 | 0.020828 | 0.0055114 | 0.0038367 | -0.0069022 | 7.902e-05 | -0.0052337 | 0.086746 | -0.0074277 | -0.0036892 | -0.0028306 | 0.0043215 | -0.010376 | -0.045776 | -0.11902 | -0.11902 | -0.064087 | 0.14191 | -0.091553 | -0.25177 | -0.050354 | -0.13733 | -0.15564 | 0.073242 | 0.050354 | -0.14191 | -0.21515 | 122.5067 | 122.3465 | -0.032043 | 122.4792 | 122.5342 | 0.18768 | -0.21973 | 122.4564 | 122.3831 | -0.10071 | 122.5479 | 122.4426 | 0.059509 | -0.1236 | 122.7402 | 122.5525 | 122.4792 | -0.42572 | 122.6715 | 122.6486 | 122.4609 | -0.3891
1424.8594 | 122.9233 | -122.5204 | 0.12817 | -0.22949 | 0.024246 | 0.0052978 | 0.0096045 | -0.0036978 | -0.00098918 | -0.0048065 | -0.18791 | -0.0084957 | -0.0019802 | -0.0017624 | 0.0026125 | -0.0099484 | 0.07782 | 0.036621 | 0.013733 | 0.064087 | 0.25635 | 0.027466 | -0.1236 | 0.022888 | 0.073242 | -0.054932 | 0.16479 | 0.12817 | -0.068665 | -0.13275 | 122.5479 | 122.3969 | 0.12817 | 122.5571 | 122.5845 | 0.18768 | -0.050354 | 122.4518 | 122.3877 | 0.036621 | 122.5433 | 122.4655 | 0.077819 | 0 | 122.7768 | 122.5983 | 122.5342 | -0.25177 | 122.6852 | 122.6486 | 122.5937 | -0.26093
1426.5469 | 122.8729 | -122.5479 | 0.13733 | -0.19897 | 0.021256 | 0.0033752 | 0.0059729 | -0.0049796 | -0.0029118 | -0.0037385 | -0.14214 | -0.010846 | -0.0039028 | -0.0030442 | -0.00016447 | -0.010589 | 0.15106 | 0.17395 | 0.16479 | 0.11902 | 0.18768 | 0.073242 | -0.068665 | 0.14191 | 0.27008 | 0.091553 | 0.13733 | 0.11902 | -0.041199 | -0.082397 | 122.6212 | 122.4792 | 0.050354 | 122.7219 | 122.6669 | 0.18768 | 0.013733 | 122.5067 | 122.4655 | 0 | 122.6898 | 122.6395 | 0.17395 | -0.01831 | 122.7356 | 122.699 | 122.7127 | -0.20599 | 122.6852 | 122.6669 | 122.818 | -0.21973
1428.2656 | 122.9324 | -122.5616 | 0.14191 | -0.19135 | 0.021683 | 0.0040162 | 0.0068273 | -0.007543 | 0.0013608 | -0.0030975 | -0.20317 | -0.0046505 | -0.0019802 | 0.0010148 | 0.0041079 | -0.012726 | 0.068665 | 0.036621 | 0.009155 | 0.054932 | 0.24719 | 0.022888 | -0.11902 | 0.036621 | 0.086975 | -0.045776 | 0.16937 | 0.15106 | -0.07782 | -0.13275 | 122.5845 | 122.4426 | 0.10528 | 122.5983 | 122.6166 | 0.17395 | -0.073242 | 122.4838 | 122.4289 | 0.027466 | 122.5983 | 122.5159 | 0.086975 | 0.009155 | 122.8088 | 122.6303 | 122.5708 | -0.26093 | 122.731 | 122.7127 | 122.6486 | -0.27466
1429.9844 | 122.9187 | -122.5662 | 0.14648 | -0.26001 | 0.021683 | 0.0014526 | 0.010245 | -0.0051932 | 0.00093342 | -0.0071563 | -0.23369 | -0.0089229 | -0.0026212 | -5.3406e-05 | 0.0017581 | -0.010376 | 0.073242 | 0.054932 | 0.032043 | 0.068665 | 0.27924 | 0.045776 | -0.10986 | 0.050354 | 0.054932 | -0.050354 | 0.17395 | 0.16022 | -0.064087 | -0.11902 | 122.612 | 122.4564 | 0.13275 | 122.6212 | 122.6349 | 0.17853 | -0.073242 | 122.5021 | 122.4472 | 0.027466 | 122.6166 | 122.5159 | 0.068665 | 0.013733 | 122.8455 | 122.6395 | 122.5983 | -0.25635 | 122.7402 | 122.7264 | 122.6212 | -0.2655
1431.6562 | 122.9187 | -122.5342 | 0.14648 | -0.11505 | 0.018906 | 0.002948 | 0.0066137 | -0.0077566 | -0.004407 | -0.0043793 | -0.042954 | -0.0093503 | -0.0051846 | -0.0015488 | -0.00037807 | -0.0095212 | 0.10071 | 0.17395 | 0.12817 | 0.11444 | 0.1831 | 0.041199 | -0.10986 | 0.17395 | 0.24719 | 0.10071 | 0.11902 | 0.10986 | -0.013733 | -0.09613 | 122.5754 | 122.4243 | 0.036621 | 122.7081 | 122.6486 | 0.2243 | -0.045776 | 122.5204 | 122.4381 | -0.027465 | 122.7081 | 122.6349 | 0.19684 | -0.036621 | 122.7173 | 122.6349 | 122.6624 | -0.25635 | 122.6532 | 122.644 | 122.7814 | -0.24261
1433.3281 | 122.8683 | -122.5708 | 0.14648 | -0.21423 | 0.022324 | 0.0040162 | 0.0061865 | -0.0039114 | -0.0054752 | -0.0056611 | -0.21843 | -0.010205 | -0.0036892 | -0.0028306 | 0.0021853 | -0.010162 | 0.1236 | 0.15564 | 0.13275 | 0.1236 | 0.21973 | 0.045776 | -0.086975 | 0.10529 | 0.19684 | 0.032043 | 0.16937 | 0.15564 | -0.027466 | -0.10529 | 122.6166 | 122.4838 | 0.073243 | 122.7264 | 122.6944 | 0.21057 | -0.022888 | 122.5433 | 122.4655 | 0.022889 | 122.6761 | 122.6028 | 0.13733 | 0.009156 | 122.7905 | 122.6944 | 122.7036 | -0.23346 | 122.7402 | 122.7264 | 122.7676 | -0.25177
1435.0312 | 122.9279 | -122.5571 | 0.13733 | -0.2066 | 0.023819 | 0.0042298 | 0.0046911 | -0.004125 | 0.0022152 | -0.0037385 | -0.2108 | -0.0067867 | -0.0047574 | -0.00026701 | 0.0047489 | -0.012298 | 0.068665 | 0.045776 | 0 | 0.068665 | 0.2655 | 0.032043 | -0.1236 | 0.032043 | 0.068665 | -0.050354 | 0.16022 | 0.15564 | -0.082397 | -0.13275 | 122.5891 | 122.4335 | 0.12817 | 122.6028 | 122.6257 | 0.19226 | -0.068664 | 122.4747 | 122.4243 | 0.022888 | 122.5891 | 122.5067 | 0.082397 | 0.018311 | 122.8226 | 122.6257 | 122.5571 | -0.26093 | 122.7173 | 122.7127 | 122.6257 | -0.27008
1436.7031 | 122.9233 | -122.5708 | 0.14648 | -0.19135 | 0.023819 | 0.0027344 | 0.0051183 | -0.0043386 | 0.0032834 | -0.0028839 | -0.19554 | -0.0087093 | -0.0053982 | -0.00026701 | 0.0041079 | -0.012298 | 0.068665 | 0.082397 | 0.022888 | 0.068665 | 0.23346 | 0.013733 | -0.13275 | 0.036621 | 0.050354 | -0.036621 | 0.13275 | 0.09613 | -0.10071 | -0.16022 | 122.5845 | 122.4381 | 0.086975 | 122.6532 | 122.6395 | 0.20142 | -0.077819 | 122.4701 | 122.4106 | -0.013733 | 122.6074 | 122.5342 | 0.1236 | -0.050354 | 122.8043 | 122.6395 | 122.5937 | -0.27924 | 122.7036 | 122.6669 | 122.6212 | -0.3067
1438.3906 | 122.9187 | -122.5571 | 0.14191 | -0.1532 | 0.020828 | 0.0038024 | 0.0038367 | -0.0056204 | 0.0020016 | -0.0028839 | -0.15739 | -0.0078549 | -0.0053982 | -0.00048061 | 0.0075259 | -0.010376 | 0.045776 | 0.059509 | 0.004578 | 0.045776 | 0.20599 | -0.018311 | -0.15106 | 0.045776 | 0.041199 | -0.050354 | 0.11902 | 0.086975 | -0.11444 | -0.17395 | 122.5388 | 122.406 | 0.064087 | 122.6166 | 122.6028 | 0.19684 | -0.096131 | 122.4426 | 122.3831 | -0.022888 | 122.6028 | 122.5067 | 0.1236 | -0.054932 | 122.7631 | 122.6028 | 122.5616 | -0.29297 | 122.6761 | 122.644 | 122.5983 | -0.31586
1440.0781 | 122.7814 | -122.5754 | 0.16937 | -0.038757 | 0.022537 | 0.0031616 | 0.0044775 | -0.0049796 | 0.0037106 | -0.0024567 | -0.050583 | -0.0082821 | -0.0028348 | 0.0012284 | 0.0056033 | -0.011017 | 0.036621 | 0.027466 | -0.009155 | 0.009155 | 0.16022 | -0.041199 | -0.20142 | 0 | -0.045776 | -0.11444 | 0.09613 | 0.059509 | -0.12817 | -0.19226 | 122.5342 | 122.374 | -0.009156 | 122.6028 | 122.5845 | 0.21057 | -0.13275 | 122.4472 | 122.3831 | -0.073243 | 122.5754 | 122.4609 | 0.07782 | -0.10986 | 122.7356 | 122.612 | 122.5662 | -0.37079 | 122.6715 | 122.6349 | 122.5296 | -0.36163
1441.7656 | 122.7768 | -122.612 | 0.16937 | 0.11383 | 0.020615 | 0.0042298 | 0.0044775 | -0.0077566 | -0.006116 | -0.0041657 | 0.21645 | -0.0095639 | -0.0036892 | -0.001976 | 0.0026125 | -0.007385 | 0 | 0.073242 | 0.032043 | 0 | 0.073242 | -0.059509 | -0.19684 | 0.059509 | 0.064087 | -0.013733 | 0.036621 | 0.004578 | -0.13275 | -0.19684 | 122.5525 | 122.4152 | -0.096131 | 122.6852 | 122.612 | 0.19684 | -0.16937 | 122.4792 | 122.4152 | -0.13275 | 122.6715 | 122.5983 | 0.18311 | -0.16479 | 122.6852 | 122.612 | 122.644 | -0.36621 | 122.6486 | 122.6166 | 122.6761 | -0.36621
1443.4375 | 122.9141 | -122.5571 | 0.1236 | -0.092163 | 0.017838 | 0.0059388 | 0.0053321 | -0.0030568 | -0.006757 | -0.0065155 | -0.020065 | -0.0099911 | -0.0056118 | -0.0030442 | 0.00090353 | -0.0075986 | 0.073242 | 0.13275 | 0.10986 | 0.086975 | 0.16937 | 0.036621 | -0.10986 | 0.16022 | 0.24719 | 0.10529 | 0.12817 | 0.10071 | -0.032043 | -0.09613 | 122.5937 | 122.4472 | 0.045777 | 122.6898 | 122.644 | 0.19684 | -0.050354 | 122.525 | 122.4609 | 0.004578 | 122.7173 | 122.6624 | 0.20142 | -0.022888 | 122.7264 | 122.6303 | 122.6669 | -0.23346 | 122.6852 | 122.6578 | 122.8043 | -0.21973
1445.1406 | 122.8638 | -122.5571 | 0.14191 | -0.19897 | 0.022537 | 0.0042298 | 0.0049047 | -0.0051932 | -0.004407 | -0.0048065 | -0.096359 | -0.0087093 | -0.0068936 | -0.0015488 | 0.00047633 | -0.010162 | 0.14648 | 0.17395 | 0.16479 | 0.13733 | 0.19684 | 0.073242 | -0.07782 | 0.12817 | 0.25635 | 0.086975 | 0.1236 | 0.11444 | -0.036621 | -0.086975 | 122.6303 | 122.4792 | 0.054931 | 122.731 | 122.6944 | 0.21515 | 0.004577 | 122.5204 | 122.4701 | -0.018311 | 122.6852 | 122.644 | 0.17395 | -0.027466 | 122.7539 | 122.7036 | 122.7219 | -0.21973 | 122.6807 | 122.6715 | 122.8134 | -0.22888
1446.8281 | 122.9233 | -122.5479 | 0.14191 | -0.13031 | 0.01741 | 0.0042298 | 0.0057593 | -0.0064748 | -0.0039798 | -0.0069427 | -0.027695 | -0.0089229 | -0.004971 | -0.0024032 | 0.0013309 | -0.012085 | 0.12817 | 0.16022 | 0.13733 | 0.11902 | 0.17853 | 0.032043 | -0.091553 | 0.18768 | 0.27008 | 0.13275 | 0.12817 | 0.091553 | -0.032043 | -0.082397 | 122.58 | 122.4564 | 0.036621 | 122.7081 | 122.6669 | 0.21057 | -0.013733 | 122.5159 | 122.4655 | -0.013733 | 122.7356 | 122.6807 | 0.21515 | -0.050354 | 122.7264 | 122.6761 | 122.6852 | -0.23346 | 122.6761 | 122.6395 | 122.818 | -0.2243
1448.5 | 122.8317 | -122.5937 | 0.1831 | 0.12146 | 0.020828 | 0.0025208 | 0.0025549 | -0.0069022 | 0.0022152 | -0.0043793 | 0.056228 | -0.0074277 | -0.0081754 | -0.00026701 | 0.0070987 | -0.011017 | -0.027466 | -0.09613 | -0.11902 | -0.082397 | 0.11902 | -0.10986 | -0.23804 | -0.027466 | -0.12817 | -0.14191 | 0.091553 | 0.059509 | -0.15564 | -0.21973 | 122.4838 | 122.3557 | -0.064086 | 122.4976 | 122.5113 | 0.15564 | -0.21057 | 122.438 | 122.374 | -0.091552 | 122.5662 | 122.4518 | 0.07782 | -0.1236 | 122.7127 | 122.5662 | 122.4747 | -0.42114 | 122.6852 | 122.6532 | 122.4655 | -0.40283
1450.2031 | 122.905 | -122.5708 | 0.14191 | -0.23712 | 0.020828 | 0.004657 | 0.0078955 | -0.0069022 | 0.00093342 | -0.0054475 | -0.25658 | -0.0078549 | -0.0041164 | -0.00048061 | 0.0015445 | -0.0099484 | 0.086975 | 0.073242 | 0.013733 | 0.064087 | 0.28839 | 0.036621 | -0.10986 | 0.045776 | 0.07782 | -0.050354 | 0.19226 | 0.15564 | -0.068665 | -0.11444 | 122.6074 | 122.4609 | 0.14648 | 122.644 | 122.6349 | 0.17395 | -0.054932 | 122.5021 | 122.4564 | 0.050354 | 122.6166 | 122.5204 | 0.064087 | 0.013733 | 122.8592 | 122.6578 | 122.5845 | -0.25177 | 122.7631 | 122.7264 | 122.6486 | -0.25635
1451.875 | 122.9324 | -122.5433 | 0.13733 | -0.19135 | 0.022537 | 0.0031616 | 0.0061865 | -0.0022024 | 0.0015744 | -0.0026703 | -0.18028 | -0.0061459 | -0.0021938 | -0.0013352 | 0.0028263 | -0.013153 | 0.068665 | 0.064087 | 0.022888 | 0.073242 | 0.23804 | 0.013733 | -0.13733 | 0.036621 | 0.036621 | -0.050354 | 0.14648 | 0.10529 | -0.11444 | -0.15564 | 122.5571 | 122.406 | 0.10071 | 122.6074 | 122.6166 | 0.21057 | -0.068664 | 122.4289 | 122.3877 | 0.009155 | 122.58 | 122.493 | 0.10529 | -0.032043 | 122.7814 | 122.612 | 122.5662 | -0.27466 | 122.6898 | 122.6486 | 122.58 | -0.29297
1453.5469 | 122.905 | -122.5479 | 0.14648 | -0.24475 | 0.022965 | 0.0059388 | 0.0074683 | -0.0030568 | -0.00013458 | -0.0060883 | -0.23369 | -0.0072141 | -0.0021938 | -0.0015488 | 0.0013309 | -0.0097348 | 0.064087 | 0.07782 | 0.041199 | 0.064087 | 0.2655 | 0.027466 | -0.10529 | 0.054932 | 0.09613 | -0.018311 | 0.19684 | 0.16022 | -0.064087 | -0.11902 | 122.5754 | 122.4426 | 0.11902 | 122.6257 | 122.612 | 0.16937 | -0.082397 | 122.4838 | 122.4289 | 0.050354 | 122.6028 | 122.5296 | 0.10071 | 0.013733 | 122.8134 | 122.612 | 122.5891 | -0.25177 | 122.7448 | 122.7081 | 122.644 | -0.2655
1455.2188 | 122.8867 | -122.5754 | 0.15564 | -0.23712 | 0.020828 | 0.0031616 | 0.0061865 | -0.0032706 | -0.002698 | -0.0050201 | -0.21843 | -0.0059323 | -0.003262 | -0.0011216 | 0.0023989 | -0.011017 | 0.041199 | 0.07782 | 0.036621 | 0.068665 | 0.26093 | 0.022888 | -0.11444 | 0.050354 | 0.11444 | -0.032043 | 0.19226 | 0.15564 | -0.050354 | -0.12817 | 122.5983 | 122.4609 | 0.10529 | 122.6532 | 122.644 | 0.18311 | -0.11444 | 122.525 | 122.4472 | 0.036621 | 122.6257 | 122.5433 | 0.096131 | 0 | 122.8363 | 122.6166 | 122.612 | -0.27008 | 122.7676 | 122.731 | 122.6898 | -0.28381
1456.9062 | 122.7859 | -122.612 | 0.17853 | 0.12909 | 0.015915 | 0.0035888 | 0.0017005 | -0.0060476 | -0.0039798 | -0.0065155 | 0.14778 | -0.0082821 | -0.0062528 | 0.00016019 | 0.0034671 | -0.010589 | 0.009155 | 0.045776 | 0.032043 | -0.004578 | 0.10529 | -0.041199 | -0.17853 | 0.07782 | 0.091553 | -0.018311 | 0.091553 | 0.068665 | -0.07782 | -0.13275 | 122.5708 | 122.4335 | -0.073242 | 122.6578 | 122.6074 | 0.17395 | -0.16937 | 122.5342 | 122.4792 | -0.086975 | 122.6898 | 122.5937 | 0.11444 | -0.10986 | 122.7173 | 122.6212 | 122.644 | -0.35706 | 122.7036 | 122.6807 | 122.7036 | -0.31128
1458.5938 | 122.9233 | -122.5662 | 0.15564 | -0.27527 | 0.02211 | 0.004657 | 0.0059729 | -0.005834 | -0.00056178 | -0.0045929 | -0.27184 | -0.0076413 | -0.0058254 | 0.00058739 | 0.0036807 | -0.011871 | 0.068665 | 0.068665 | 0.027466 | 0.059509 | 0.2655 | 0.059509 | -0.09613 | 0.050354 | 0.07782 | -0.045776 | 0.19684 | 0.16022 | -0.073242 | -0.1236 | 122.6257 | 122.4701 | 0.10986 | 122.6349 | 122.6257 | 0.15564 | -0.086975 | 122.493 | 122.4426 | 0.041198 | 122.6166 | 122.5204 | 0.07782 | 0.004577 | 122.8317 | 122.6349 | 122.5937 | -0.25177 | 122.7631 | 122.7264 | 122.644 | -0.27924
1460.2656 | 122.7997 | -122.6303 | 0.19226 | 0.037537 | 0.023392 | 0.0018798 | 0.0036231 | -0.0056204 | 0.0020016 | -0.0037385 | -0.050583 | -0.0076413 | -0.0053982 | 0.0010148 | 0.0077395 | -0.012298 | -0.036621 | -0.064087 | -0.07782 | -0.059509 | 0.14191 | -0.07782 | -0.22888 | -0.045776 | -0.10986 | -0.15106 | 0.091553 | 0.054932 | -0.14648 | -0.22888 | 122.5525 | 122.4014 | -0.050354 | 122.5662 | 122.5708 | 0.16937 | -0.22888 | 122.4838 | 122.4014 | -0.10071 | 122.5845 | 122.4792 | 0.07782 | -0.13733 | 122.7722 | 122.5937 | 122.5525 | -0.42114 | 122.7219 | 122.6852 | 122.5204 | -0.42114
1461.9375 | 122.7997 | -122.6257 | 0.19684 | 0.068054 | 0.023605 | 0.002948 | 0.0027685 | -0.0064748 | 7.902e-05 | -0.0035249 | 0.048599 | -0.0087093 | -0.0075344 | 0.003151 | 0.0053897 | -0.008453 | -0.045776 | -0.091553 | -0.11444 | -0.054932 | 0.15106 | -0.091553 | -0.24261 | -0.050354 | -0.1236 | -0.16479 | 0.07782 | 0.064087 | -0.16022 | -0.21515 | 122.5342 | 122.3831 | -0.045776 | 122.5342 | 122.5708 | 0.18768 | -0.24261 | 122.4655 | 122.4106 | -0.11902 | 122.5754 | 122.4609 | 0.050354 | -0.13275 | 122.7768 | 122.58 | 122.5113 | -0.43945 | 122.7036 | 122.6898 | 122.5021 | -0.41199
1463.6406 | 122.8821 | -122.58 | 0.13733 | -0.25238 | 0.022965 | 0.0048706 | 0.0074683 | -0.0051932 | -0.0024844 | -0.0035249 | -0.18791 | -0.0089229 | -0.0011258 | -0.0030442 | 0.0013309 | -0.0095212 | 0.091553 | 0.11902 | 0.082397 | 0.10529 | 0.24261 | 0.041199 | -0.09613 | 0.064087 | 0.13733 | -0.018311 | 0.17395 | 0.16022 | -0.068665 | -0.10986 | 122.6212 | 122.4838 | 0.10529 | 122.699 | 122.6852 | 0.20142 | -0.045776 | 122.5113 | 122.4701 | 0.036621 | 122.644 | 122.5616 | 0.091552 | 0.022888 | 122.8226 | 122.6715 | 122.6624 | -0.23346 | 122.7539 | 122.7402 | 122.7173 | -0.24719
1465.3125 | 122.9279 | -122.5525 | 0.15564 | -0.22949 | 0.021896 | 0.0055114 | 0.0098181 | -0.0069022 | -0.0014164 | -0.0050201 | -0.21843 | -0.0070003 | -0.0028348 | -5.3406e-05 | 0.0030399 | -0.0093076 | 0.050354 | 0.059509 | 0.013733 | 0.07782 | 0.27466 | 0.041199 | -0.11444 | 0.032043 | 0.073242 | -0.032043 | 0.19226 | 0.15564 | -0.054932 | -0.13275 | 122.5937 | 122.438 | 0.11902 | 122.612 | 122.6303 | 0.19226 | -0.10529 | 122.4976 | 122.4197 | 0.036621 | 122.5845 | 122.5204 | 0.10071 | 0 | 122.8271 | 122.6028 | 122.5662 | -0.27008 | 122.7448 | 122.7081 | 122.6257 | -0.28839
1466.9688 | 122.8134 | -122.5937 | 0.16937 | 0.1825 | 0.016129 | 0.0031616 | -8.476e-06 | -0.0051932 | 0.00050622 | -0.0041657 | 0.20882 | -0.010418 | -0.0075344 | -0.0011216 | 0.0045351 | -0.010162 | 0.009155 | 0.018311 | 0 | -0.009155 | 0.041199 | -0.064087 | -0.21057 | 0.059509 | 0.036621 | -0.027466 | 0.022888 | -0.004578 | -0.12817 | -0.19684 | 122.5296 | 122.3831 | -0.12817 | 122.612 | 122.5845 | 0.20142 | -0.16022 | 122.4655 | 122.3969 | -0.14649 | 122.6532 | 122.5662 | 0.16937 | -0.17395 | 122.6349 | 122.6028 | 122.5937 | -0.37994 | 122.6166 | 122.5891 | 122.6303 | -0.36621
1468.6406 | 122.7859 | -122.5662 | 0.17395 | 0.19012 | 0.020187 | 0.0040162 | 0.00020512 | -0.0043386 | -0.0012028 | -0.0054475 | 0.17067 | -0.0078549 | -0.007748 | -0.0015488 | 0.0043215 | -0.0099484 | 0.009155 | 0.036621 | 0.032043 | -0.018311 | 0.032043 | -0.064087 | -0.21515 | 0.07782 | 0.059509 | -0.009155 | 0.018311 | -0.004578 | -0.11902 | -0.19684 | 122.5021 | 122.3511 | -0.14191 | 122.6028 | 122.5479 | 0.19684 | -0.16479 | 122.4472 | 122.3694 | -0.15564 | 122.644 | 122.5571 | 0.18768 | -0.17853 | 122.5983 | 122.5754 | 122.5983 | -0.3891 | 122.5845 | 122.5616 | 122.6257 | -0.37079
1470.3438 | 122.905 | -122.5754 | 0.16022 | -0.21423 | 0.022324 | 0.006366 | 0.0076819 | -0.0028432 | -0.00034818 | -0.0054475 | -0.21843 | -0.0099911 | -0.0030484 | -0.0024032 | 0.0017581 | -0.0099484 | 0.054932 | 0.064087 | 0.032043 | 0.059509 | 0.2655 | 0.050354 | -0.11902 | 0.050354 | 0.086975 | -0.032043 | 0.20142 | 0.16022 | -0.07782 | -0.1236 | 122.6257 | 122.4564 | 0.10529 | 122.6395 | 122.6349 | 0.17853 | -0.10528 | 122.4976 | 122.4518 | 0.041199 | 122.6257 | 122.5433 | 0.091553 | 0 | 122.8409 | 122.6303 | 122.6074 | -0.27924 | 122.7768 | 122.7356 | 122.6624 | -0.28381
1472.0469 | 122.8088 | -122.5845 | 0.17395 | 0.068054 | 0.01976 | 0.0050842 | 0.0059729 | -0.0039114 | -0.005048 | -0.0065155 | 0.11726 | -0.0084957 | -0.0034756 | 0.0018692 | -0.0010191 | -0.011444 | 0.018311 | 0.032043 | 0.027466 | 0.004578 | 0.13733 | -0.022888 | -0.16937 | 0.068665 | 0.10986 | 0 | 0.091553 | 0.068665 | -0.082397 | -0.13275 | 122.5616 | 122.4152 | -0.036621 | 122.6166 | 122.5891 | 0.17395 | -0.15564 | 122.5021 | 122.4518 | -0.082397 | 122.6532 | 122.5845 | 0.13275 | -0.10528 | 122.7219 | 122.6028 | 122.612 | -0.34332 | 122.6761 | 122.6532 | 122.6944 | -0.3067
1473.75 | 122.8409 | -122.58 | 0.15564 | 0.0070193 | 0.017624 | 0.0044434 | 0.0031957 | -0.0054068 | -0.0035526 | -0.0052337 | 0.063858 | -0.0065731 | -0.0071072 | 0.00058739 | 0.0032535 | -0.010803 | 0.041199 | 0.032043 | 0.036621 | 0.022888 | 0.15106 | -0.004578 | -0.14648 | 0.059509 | 0.12817 | 0.009155 | 0.11902 | 0.086975 | -0.064087 | -0.1236 | 122.5754 | 122.4335 | -0.004578 | 122.612 | 122.6028 | 0.16937 | -0.11444 | 122.5159 | 122.4564 | -0.036621 | 122.6395 | 122.5891 | 0.13275 | -0.068665 | 122.731 | 122.6212 | 122.6166 | -0.30212 | 122.699 | 122.6669 | 122.7081 | -0.27924
1475.4219 | 122.9233 | -122.5708 | 0.13275 | -0.099793 | 0.019333 | 0.0057252 | 0.0044775 | -0.0066884 | -0.0037662 | -0.0063019 | -0.096359 | -0.010632 | -0.0064664 | -0.00069421 | 0.0026125 | -0.01123 | 0.1831 | 0.16479 | 0.11902 | 0.11902 | 0.19226 | 0.041199 | -0.082397 | 0.17853 | 0.27466 | 0.11902 | 0.13275 | 0.09613 | -0.050354 | -0.10071 | 122.612 | 122.4884 | 0.05951 | 122.7356 | 122.6898 | 0.20142 | 0.050354 | 122.5204 | 122.4701 | 0 | 122.7493 | 122.6898 | 0.21973 | -0.036621 | 122.7631 | 122.7539 | 122.6898 | -0.21515 | 122.7036 | 122.6669 | 122.8455 | -0.23346
1477.1094 | 122.8043 | -122.6349 | 0.16479 | 0.098572 | 0.018051 | 0.008075 | 0.0046911 | -0.0077566 | -0.002698 | -0.0045929 | 0.079117 | -0.0076413 | -0.00668 | -0.0049668 | 0.0047489 | -0.010589 | 0.064087 | 0.018311 | 0.041199 | 0.004578 | 0.09613 | -0.050354 | -0.17853 | 0.073242 | 0.086975 | -0.013733 | 0.09613 | 0.086975 | -0.086975 | -0.14191 | 122.5845 | 122.4564 | -0.068665 | 122.6532 | 122.6395 | 0.18311 | -0.10071 | 122.5479 | 122.493 | -0.068665 | 122.7081 | 122.6212 | 0.12817 | -0.07782 | 122.731 | 122.699 | 122.6761 | -0.34332 | 122.731 | 122.7219 | 122.7219 | -0.3067
1478.7812 | 122.818 | -122.6074 | 0.16479 | -0.11505 | 0.016556 | 0.0061524 | 0.0034093 | -0.0051932 | -0.00056178 | -0.0052337 | 0.079117 | -0.011059 | -0.0092434 | -0.0011216 | 0.0030399 | -0.0093076 | 0.07782 | 0.032043 | 0.022888 | 0 | 0.12817 | -0.032043 | -0.16937 | 0.082397 | 0.091553 | -0.018311 | 0.09613 | 0.082397 | -0.10071 | -0.14648 | 122.5754 | 122.438 | -0.036621 | 122.6395 | 122.6074 | 0.16937 | -0.086975 | 122.5067 | 122.4609 | -0.068665 | 122.6898 | 122.5891 | 0.12817 | -0.082398 | 122.7356 | 122.6852 | 122.6303 | -0.33417 | 122.7036 | 122.6898 | 122.699 | -0.31128
1480.4531 | 122.9279 | -122.5662 | 0.14648 | -0.054016 | 0.018051 | 0.0040162 | 0.0066137 | -0.0054068 | -0.0037662 | -0.0037385 | -0.081101 | -0.010205 | -0.0051846 | -0.0011216 | 0.0019717 | -0.009094 | 0.15564 | 0.1236 | 0.09613 | 0.086975 | 0.1831 | 0.027466 | -0.12817 | 0.17395 | 0.23346 | 0.086975 | 0.13733 | 0.10529 | -0.022888 | -0.09613 | 122.5937 | 122.438 | 0.036621 | 122.6898 | 122.6532 | 0.21515 | 0.009156 | 122.5433 | 122.4701 | -0.009155 | 122.7402 | 122.6532 | 0.1831 | -0.041198 | 122.7493 | 122.7219 | 122.6624 | -0.27466 | 122.7036 | 122.6715 | 122.7997 | -0.24261
1482.1406 | 122.8409 | -122.6074 | 0.1831 | 0.11383 | 0.021256 | 0.0057252 | 0.0029821 | -0.0056204 | 0.0058468 | -0.0030975 | 0.0028229 | -0.0078549 | -0.0062528 | -0.0017624 | 0.0079531 | -0.012512 | 0 | -0.11902 | -0.11444 | -0.07782 | 0.11902 | -0.07782 | -0.23346 | -0.032043 | -0.13733 | -0.1831 | 0.09613 | 0.054932 | -0.15106 | -0.21973 | 122.5296 | 122.374 | -0.064086 | 122.4884 | 122.5296 | 0.15564 | -0.1831 | 122.4564 | 122.3877 | -0.086975 | 122.5754 | 122.4243 | 0.036622 | -0.12817 | 122.7264 | 122.6074 | 122.493 | -0.41656 | 122.7036 | 122.6624 | 122.4701 | -0.40283
1483.8125 | 122.7951 | -122.6028 | 0.17395 | 0.1825 | 0.019333 | 0.0031616 | 0.0010595 | -0.0045522 | -0.0014164 | -0.0041657 | 0.12489 | -0.011487 | -0.0075344 | -0.0028306 | 0.0041079 | -0.011657 | 0.054932 | 0.045776 | 0.032043 | -0.004578 | 0.054932 | -0.054932 | -0.20142 | 0.086975 | 0.059509 | -0.009155 | 0.041199 | -0.004578 | -0.11902 | -0.16022 | 122.5479 | 122.4014 | -0.11902 | 122.6486 | 122.5983 | 0.19684 | -0.11902 | 122.4838 | 122.4426 | -0.13275 | 122.6898 | 122.5937 | 0.15106 | -0.17853 | 122.6578 | 122.6578 | 122.6349 | -0.37537 | 122.644 | 122.5983 | 122.6624 | -0.33417
1485.4844 | 122.8683 | -122.5845 | 0.17395 | 0.022278 | 0.017624 | 0.0035888 | 0.0025549 | -0.0064748 | -0.0052616 | -0.0071563 | 0.03334 | -0.010418 | -0.00668 | -0.0021896 | 0.0030399 | -0.010376 | 0.041199 | 0.027466 | 0.022888 | 0.041199 | 0.16479 | 0 | -0.14648 | 0.082397 | 0.12817 | 0.013733 | 0.11444 | 0.086975 | -0.086975 | -0.13733 | 122.5845 | 122.4381 | -0.009155 | 122.612 | 122.6257 | 0.18768 | -0.13275 | 122.4976 | 122.4472 | -0.059509 | 122.6669 | 122.5983 | 0.15106 | -0.086975 | 122.7493 | 122.6257 | 122.6074 | -0.32043 | 122.699 | 122.6715 | 122.7127 | -0.31128
1487.1562 | 122.7905 | -122.612 | 0.16937 | 0.12146 | 0.020401 | 0.0048706 | 0.0017005 | -0.0039114 | -0.00098918 | -0.0035249 | 0.14778 | -0.0099911 | -0.0088162 | -0.003685 | 0.0038943 | -0.0099484 | 0.073242 | 0.050354 | 0.032043 | 0.013733 | 0.073242 | -0.064087 | -0.21057 | 0.073242 | 0.050354 | -0.041199 | 0.045776 | 0.013733 | -0.1236 | -0.17395 | 122.5479 | 122.4014 | -0.096131 | 122.6624 | 122.6257 | 0.2243 | -0.096131 | 122.4884 | 122.438 | -0.1236 | 122.6852 | 122.5708 | 0.13275 | -0.15564 | 122.6852 | 122.6852 | 122.644 | -0.37994 | 122.6578 | 122.6257 | 122.6624 | -0.34332
1488.8438 | 122.8088 | -122.6212 | 0.17395 | 0.12909 | 0.019333 | 0.0038024 | 0.0040503 | -0.0069022 | 0.00029262 | -0.0050201 | 0.10963 | -0.0082821 | -0.0071072 | 0.00016019 | 0.0034671 | -0.010589 | 0.073242 | 0.036621 | 0.045776 | 0.004578 | 0.082397 | -0.064087 | -0.21057 | 0.09613 | 0.059509 | -0.013733 | 0.054932 | 0.027466 | -0.11444 | -0.1831 | 122.5571 | 122.4106 | -0.091553 | 122.6578 | 122.6257 | 0.21515 | -0.10071 | 122.5067 | 122.4381 | -0.11902 | 122.7173 | 122.6074 | 0.16937 | -0.14648 | 122.7036 | 122.6944 | 122.6669 | -0.38452 | 122.6761 | 122.6486 | 122.6807 | -0.35706
1490.5156 | 122.818 | -122.612 | 0.16022 | -0.0082397 | 0.015701 | 0.0065796 | 0.0044775 | -0.004125 | -0.0018436 | -0.0052337 | 0.079117 | -0.0084957 | -0.0051846 | 0.00037379 | 0.0036807 | -0.010589 | 0.073242 | 0.018311 | 0.041199 | 0.032043 | 0.14648 | -0.018311 | -0.15564 | 0.082397 | 0.09613 | -0.009155 | 0.10986 | 0.10071 | -0.073242 | -0.14191 | 122.5937 | 122.4564 | -0.013733 | 122.6303 | 122.644 | 0.18768 | -0.086975 | 122.5388 | 122.4701 | -0.050354 | 122.6944 | 122.6028 | 0.13275 | -0.059509 | 122.7585 | 122.6852 | 122.6532 | -0.31586 | 122.7219 | 122.7127 | 122.7081 | -0.30212
1492.2031 | 122.9279 | -122.5525 | 0.13733 | -0.11505 | 0.019547 | 0.0044434 | 0.0068273 | -0.0047658 | -0.005048 | -0.0077973 | -0.08873 | -0.010205 | -0.0051846 | -0.00090781 | 0.0028263 | -0.014007 | 0.1831 | 0.16022 | 0.1236 | 0.11902 | 0.19226 | 0.054932 | -0.10529 | 0.17395 | 0.25635 | 0.11902 | 0.13275 | 0.091553 | -0.045776 | -0.082397 | 122.6074 | 122.4472 | 0.054932 | 122.7127 | 122.6715 | 0.22431 | 0.045776 | 122.5067 | 122.4701 | -0.004578 | 122.7264 | 122.6715 | 0.20142 | -0.045776 | 122.7448 | 122.7356 | 122.6761 | -0.24262 | 122.6852 | 122.644 | 122.8088 | -0.21973
1493.875 | 122.85 | -122.6074 | 0.18768 | 0.1825 | 0.020187 | 0.0025208 | 0.0070409 | -0.005834 | 0.004565 | -0.0065155 | 0.03334 | -0.0089229 | -0.004971 | -0.00090781 | 0.0056033 | -0.011657 | 0.004578 | -0.11902 | -0.11902 | -0.073242 | 0.11902 | -0.10071 | -0.23346 | 0 | -0.1236 | -0.12817 | 0.086975 | 0.068665 | -0.15564 | -0.21057 | 122.5067 | 122.374 | -0.068664 | 122.4884 | 122.5342 | 0.16022 | -0.1831 | 122.4518 | 122.3969 | -0.10071 | 122.6074 | 122.4792 | 0.082397 | -0.11902 | 122.7264 | 122.612 | 122.4884 | -0.42114 | 122.6944 | 122.6761 | 122.4838 | -0.39825
1495.5469 | 122.8363 | -122.6074 | 0.17395 | 0.19775 | 0.020187 | 0.0055114 | 0.0025549 | -0.0054068 | -0.00077538 | -0.0041657 | 0.15541 | -0.0093503 | -0.0071072 | 0.00058739 | 0.0049625 | -0.011444 | 0.054932 | 0.027466 | 0.018311 | -0.013733 | 0.059509 | -0.086975 | -0.21515 | 0.086975 | 0.073242 | -0.022888 | 0.032043 | 0 | -0.1236 | -0.17853 | 122.5204 | 122.3923 | -0.11444 | 122.6349 | 122.5937 | 0.20142 | -0.11902 | 122.4838 | 122.4289 | -0.14191 | 122.6944 | 122.5845 | 0.15564 | -0.17395 | 122.6669 | 122.6624 | 122.6257 | -0.3891 | 122.6395 | 122.6074 | 122.6807 | -0.35248
1497.2188 | 122.9004 | -122.5708 | 0.13733 | -0.17609 | 0.01741 | 0.0065796 | 0.0031957 | -0.0064748 | -0.0029118 | -0.0052337 | -0.14977 | -0.0095639 | -0.0088162 | -0.0013352 | 0.0038943 | -0.0099484 | 0.17395 | 0.18768 | 0.16479 | 0.15106 | 0.19684 | 0.064087 | -0.082397 | 0.15106 | 0.2655 | 0.082397 | 0.1236 | 0.091553 | -0.032043 | -0.082397 | 122.6349 | 122.4884 | 0.059509 | 122.7585 | 122.7219 | 0.23346 | 0.036621 | 122.5388 | 122.4884 | -0.013733 | 122.7219 | 122.6532 | 0.16479 | -0.045776 | 122.7676 | 122.7448 | 122.7356 | -0.21973 | 122.6944 | 122.6624 | 122.8363 | -0.21973
1498.9688 | 122.818 | -122.6074 | 0.17853 | -0.00061023 | 0.022537 | 0.00038459 | 0.0036231 | -0.0081838 | 0.0020016 | -0.0024567 | -0.065842 | -0.0072141 | -0.00668 | -0.0011216 | 0.0077395 | -0.01123 | 0.050354 | -0.032043 | -0.045776 | -0.018311 | 0.16479 | -0.054932 | -0.23804 | -0.018311 | -0.086975 | -0.16022 | 0.09613 | 0.059509 | -0.15106 | -0.21973 | 122.5525 | 122.3694 | -0.013733 | 122.5754 | 122.5891 | 0.21973 | -0.12817 | 122.4564 | 122.3877 | -0.082398 | 122.5891 | 122.4472 | 0.05951 | -0.11902 | 122.7722 | 122.6578 | 122.5616 | -0.41656 | 122.7036 | 122.6669 | 122.5204 | -0.39826
1500.6562 | 122.9004 | -122.5571 | 0.15564 | -0.19135 | 0.022965 | 0.0035888 | 0.0066137 | -0.0069022 | -0.0039798 | -0.0056611 | -0.24895 | -0.0078549 | -0.006039 | -0.00090781 | 4.9132e-05 | -0.008453 | 0.13733 | 0.16022 | 0.13733 | 0.13275 | 0.21057 | 0.050354 | -0.1236 | 0.1236 | 0.21057 | 0.041199 | 0.15106 | 0.13275 | -0.045776 | -0.10529 | 122.6074 | 122.4335 | 0.054931 | 122.7173 | 122.6898 | 0.25635 | -0.018311 | 122.5113 | 122.4518 | -0.004578 | 122.6807 | 122.5983 | 0.14649 | -0.022889 | 122.7676 | 122.6944 | 122.6944 | -0.27924 | 122.7081 | 122.6898 | 122.7676 | -0.26093
1502.3438 | 122.9324 | -122.5662 | 0.13733 | -0.015869 | 0.016769 | 0.0065796 | 0.0036231 | -0.0083974 | -0.0056888 | -0.0037385 | 0.010452 | -0.010205 | -0.0071072 | -0.0028306 | 0.00090353 | -0.0099484 | 0.068665 | 0.073242 | 0.068665 | 0.064087 | 0.16479 | 0.004578 | -0.14191 | 0.10986 | 0.1831 | 0.050354 | 0.11444 | 0.091553 | -0.054932 | -0.11444 | 122.5708 | 122.4243 | 0.027466 | 122.6395 | 122.6303 | 0.20599 | -0.068664 | 122.5113 | 122.4518 | -0.022888 | 122.6761 | 122.6166 | 0.16479 | -0.045776 | 122.731 | 122.6349 | 122.6349 | -0.27924 | 122.6807 | 122.6578 | 122.7493 | -0.25177
1504.0156 | 122.8867 | -122.5845 | 0.15106 | -0.25238 | 0.023605 | 0.0042298 | 0.0085363 | -0.0049796 | -0.0020572 | -0.0037385 | -0.19554 | -0.0089229 | -0.0047574 | -0.00026701 | 0.0015445 | -0.012298 | 0.12817 | 0.12817 | 0.11902 | 0.11444 | 0.23804 | 0.050354 | -0.10529 | 0.09613 | 0.16479 | 0.009155 | 0.19684 | 0.14191 | -0.064087 | -0.11902 | 122.6349 | 122.4792 | 0.086975 | 122.7127 | 122.699 | 0.21973 | -0.022888 | 122.5204 | 122.4655 | 0.045776 | 122.6807 | 122.5937 | 0.12817 | -0.009155 | 122.8226 | 122.7127 | 122.7036 | -0.25635 | 122.7814 | 122.7264 | 122.7493 | -0.27008
1505.7188 | 122.8455 | -122.6074 | 0.18768 | 0.11383 | 0.02211 | 0.0057252 | 0.0017005 | -0.0032706 | 0.0028562 | -0.0048065 | 0.03334 | -0.0059323 | -0.0021938 | 0.00251 | 0.0068851 | -0.011017 | -0.045776 | -0.10071 | -0.10529 | -0.068665 | 0.1236 | -0.10071 | -0.23804 | -0.018311 | -0.11902 | -0.16022 | 0.086975 | 0.073242 | -0.16479 | -0.19684 | 122.5067 | 122.3694 | -0.064087 | 122.5067 | 122.5388 | 0.16937 | -0.23346 | 122.4426 | 122.4106 | -0.10071 | 122.5891 | 122.4472 | 0.036621 | -0.11444 | 122.731 | 122.5616 | 122.5021 | -0.42572 | 122.6944 | 122.6807 | 122.4884 | -0.38452
1507.4062 | 122.8134 | -122.612 | 0.17853 | 0.17487 | 0.01741 | 0.0035888 | 0.0017005 | -0.0069022 | -0.00077538 | -0.0020295 | 0.17067 | -0.012341 | -0.0073208 | 0.0016556 | 0.0058169 | -0.010589 | 0.027466 | 0.050354 | 0.022888 | -0.013733 | 0.054932 | -0.073242 | -0.21057 | 0.068665 | 0.064087 | 0.004578 | 0.018311 | 0.004578 | -0.13275 | -0.20142 | 122.5388 | 122.4014 | -0.1236 | 122.6624 | 122.5983 | 0.19684 | -0.15106 | 122.4792 | 122.4106 | -0.16022 | 122.6807 | 122.6166 | 0.20599 | -0.17395 | 122.6669 | 122.6395 | 122.6349 | -0.3891 | 122.6303 | 122.6166 | 122.6761 | -0.37994
1509.0938 | 122.937 | -122.58 | 0.13275 | -0.023499 | 0.019974 | 0.004657 | 0.0072547 | -0.0064748 | -0.0065434 | -0.0060883 | -0.035324 | -0.0095639 | -0.0056118 | -0.0011216 | 0.0011173 | -0.0097348 | 0.07782 | 0.10071 | 0.086975 | 0.073242 | 0.19226 | 0.022888 | -0.13275 | 0.14191 | 0.2243 | 0.091553 | 0.14648 | 0.09613 | -0.045776 | -0.10986 | 122.6028 | 122.4472 | 0.05951 | 122.6807 | 122.6532 | 0.20599 | -0.054931 | 122.5342 | 122.4701 | 0.013733 | 122.7219 | 122.6715 | 0.20142 | -0.036621 | 122.7722 | 122.6578 | 122.6669 | -0.2655 | 122.7264 | 122.6761 | 122.8043 | -0.24261
1510.7656 | 122.8867 | -122.612 | 0.17853 | -0.084534 | 0.02446 | 0.0033752 | 0.0036231 | -0.004125 | 0.0054196 | -0.0033111 | -0.16502 | -0.0065731 | -0.0043302 | 0.0012284 | 0.0053897 | -0.011871 | 0.10986 | 0.036621 | 0.009155 | 0.022888 | 0.17395 | -0.036621 | -0.21057 | 0.059509 | 0.009155 | -0.068665 | 0.1236 | 0.09613 | -0.11902 | -0.1831 | 122.5754 | 122.4014 | -0.004578 | 122.6486 | 122.6349 | 0.23346 | -0.068665 | 122.493 | 122.4289 | -0.054932 | 122.6715 | 122.5433 | 0.11444 | -0.082398 | 122.7859 | 122.7219 | 122.6212 | -0.3891 | 122.7356 | 122.7081 | 122.6212 | -0.36163
1512.4531 | 122.937 | -122.5754 | 0.15106 | -0.069275 | 0.019974 | 0.0031616 | 0.0068273 | -0.0088248 | -0.0059024 | -0.0039521 | -0.081101 | -0.011273 | -0.0047574 | -0.0015488 | 0.00068993 | -0.010589 | 0.09613 | 0.14191 | 0.1236 | 0.10529 | 0.17395 | 0.013733 | -0.14191 | 0.17853 | 0.23346 | 0.09613 | 0.13275 | 0.10071 | -0.045776 | -0.09613 | 122.5891 | 122.4335 | 0.022888 | 122.7173 | 122.6807 | 0.24719 | -0.054932 | 122.5296 | 122.4792 | -0.018311 | 122.7539 | 122.6715 | 0.19226 | -0.050354 | 122.7493 | 122.6715 | 122.699 | -0.29297 | 122.7081 | 122.6761 | 122.8088 | -0.24719
1514.1406 | 122.8455 | -122.5937 | 0.15564 | 0.045166 | 0.020615 | 0.0033752 | 0.0057593 | -0.0056204 | -0.0041934 | -0.0043793 | 0.04097 | -0.0095639 | -0.004971 | -5.3406e-05 | 0.0026125 | -0.0097348 | 0.027466 | 0.045776 | 0.041199 | 0.050354 | 0.15564 | -0.013733 | -0.14648 | 0.082397 | 0.13275 | 0.013733 | 0.11444 | 0.073242 | -0.086975 | -0.13275 | 122.58 | 122.4472 | 0 | 122.6395 | 122.644 | 0.19684 | -0.12817 | 122.5067 | 122.4609 | -0.041199 | 122.6761 | 122.6074 | 0.14648 | -0.082398 | 122.7493 | 122.6212 | 122.6349 | -0.30212 | 122.7081 | 122.6669 | 122.7264 | -0.28839
1515.8125 | 122.8455 | -122.612 | 0.17853 | 0.1062 | 0.022751 | 0.0031616 | 0.0010595 | -0.005834 | 0.0026424 | -0.0024567 | 0.10963 | -0.0080685 | -0.0051846 | -5.3406e-05 | 0.0085941 | -0.011871 | -0.027466 | -0.059509 | -0.086975 | -0.073242 | 0.13733 | -0.091553 | -0.23804 | 0.022888 | -0.068665 | -0.09613 | 0.059509 | 0.041199 | -0.15106 | -0.20599 | 122.5204 | 122.374 | -0.041199 | 122.5525 | 122.5388 | 0.16479 | -0.20599 | 122.4609 | 122.406 | -0.11902 | 122.6349 | 122.5159 | 0.10986 | -0.13733 | 122.7493 | 122.5845 | 122.525 | -0.41656 | 122.6715 | 122.6532 | 122.5433 | -0.38452
1517.5156 | 122.8363 | -122.6303 | 0.17395 | 0.090942 | 0.020615 | 0.0048706 | 0.0057593 | -0.0060476 | -0.003339 | -0.0060883 | 0.094375 | -0.0067867 | -0.0062528 | -0.0013352 | 0.0013309 | -0.0097348 | 0.045776 | 0.054932 | 0.041199 | 0.032043 | 0.13275 | -0.032043 | -0.15106 | 0.07782 | 0.10986 | -0.004578 | 0.11444 | 0.091553 | -0.082397 | -0.13275 | 122.5983 | 122.4792 | -0.041199 | 122.6852 | 122.6624 | 0.18311 | -0.12817 | 122.5479 | 122.4976 | -0.059509 | 122.7081 | 122.6257 | 0.12817 | -0.082397 | 122.7631 | 122.6761 | 122.6715 | -0.32501 | 122.7448 | 122.7219 | 122.7402 | -0.3067
1519.2188 | 122.9324 | -122.5708 | 0.14191 | -0.099793 | 0.020401 | 0.0048706 | 0.0072547 | -0.0051932 | -0.0035526 | -0.0043793 | -0.12688 | -0.0099911 | -0.0051846 | -0.0013352 | 4.9132e-05 | -0.010803 | 0.16937 | 0.20142 | 0.16022 | 0.13733 | 0.18768 | 0.032043 | -0.10986 | 0.17395 | 0.28381 | 0.10986 | 0.14191 | 0.091553 | -0.018311 | -0.091553 | 122.6028 | 122.4609 | 0.045776 | 122.7722 | 122.7081 | 0.24719 | 0.027466 | 122.5525 | 122.4792 | 0 | 122.7448 | 122.6807 | 0.20142 | -0.050354 | 122.7585 | 122.7402 | 122.731 | -0.25177 | 122.7127 | 122.6624 | 122.8546 | -0.23346
1521.0156 | 122.8088 | -122.6349 | 0.17853 | 0.022278 | 0.022965 | 0.004657 | 0.0014867 | -0.002416 | 0.0043514 | -0.0033111 | -0.020065 | -0.0052915 | -0.006039 | 0.00016019 | 0.0092349 | -0.009094 | -0.004578 | -0.07782 | -0.07782 | -0.032043 | 0.15564 | -0.050354 | -0.21515 | -0.032043 | -0.10071 | -0.17395 | 0.10071 | 0.068665 | -0.13733 | -0.21057 | 122.5845 | 122.4197 | -0.022888 | 122.5571 | 122.6028 | 0.18311 | -0.18311 | 122.4976 | 122.4243 | -0.07782 | 122.6028 | 122.4609 | 0.036621 | -0.10986 | 122.7905 | 122.6303 | 122.5571 | -0.39368 | 122.7356 | 122.7036 | 122.5342 | -0.3891
1522.7031 | 122.8043 | -122.6257 | 0.16937 | 0.1062 | 0.021256 | 0.004657 | 0.0057593 | -0.0039114 | -0.003339 | -0.0054475 | 0.14015 | -0.0078549 | -0.0073208 | -0.0011216 | 0.0032535 | -0.010162 | 0.041199 | 0.041199 | 0.054932 | 0.009155 | 0.10071 | -0.032043 | -0.17853 | 0.073242 | 0.09613 | -0.013733 | 0.09613 | 0.064087 | -0.11444 | -0.14191 | 122.5937 | 122.4472 | -0.068665 | 122.6669 | 122.6349 | 0.18768 | -0.12817 | 122.5113 | 122.4838 | -0.073243 | 122.699 | 122.612 | 0.12817 | -0.10529 | 122.7264 | 122.6669 | 122.6807 | -0.3479 | 122.7219 | 122.6898 | 122.7219 | -0.31128
1524.4062 | 122.8088 | -122.612 | 0.15564 | 0.12146 | 0.018265 | 0.0038024 | 0.0021277 | -0.0064748 | -0.002698 | -0.0050201 | 0.13252 | -0.0097775 | -0.0081754 | -0.0011216 | 0.0030399 | -0.0097348 | 0.032043 | 0.041199 | 0.045776 | 0 | 0.086975 | -0.045776 | -0.18768 | 0.09613 | 0.091553 | -0.009155 | 0.082397 | 0.054932 | -0.09613 | -0.13733 | 122.5662 | 122.4243 | -0.068665 | 122.6532 | 122.612 | 0.18768 | -0.1236 | 122.5159 | 122.4747 | -0.073243 | 122.7081 | 122.6028 | 0.12817 | -0.10071 | 122.699 | 122.644 | 122.6578 | -0.34332 | 122.6944 | 122.6669 | 122.7036 | -0.29297
1526.0938 | 122.8363 | -122.612 | 0.1831 | -0.076904 | 0.021896 | 0.0050842 | 0.0027685 | -0.0019888 | 0.0047788 | -0.0020295 | -0.08873 | -0.0080685 | -0.00668 | 0.0010148 | 0.0081667 | -0.01358 | 0.068665 | 0.027466 | 0 | 0.009155 | 0.17853 | -0.045776 | -0.17853 | 0.022888 | -0.045776 | -0.11902 | 0.11444 | 0.09613 | -0.14191 | -0.18768 | 122.5662 | 122.4335 | -0.004577 | 122.6395 | 122.6212 | 0.18768 | -0.11444 | 122.4701 | 122.4243 | -0.068664 | 122.6349 | 122.493 | 0.068664 | -0.086975 | 122.7905 | 122.6807 | 122.612 | -0.36163 | 122.7264 | 122.7081 | 122.5662 | -0.37079
1527.7812 | 122.9507 | -122.5891 | 0.14191 | -0.23712 | 0.021469 | 0.0035888 | 0.0068273 | -0.0069022 | -0.0012028 | -0.0030975 | -0.26421 | -0.0087093 | -0.0039028 | -0.00048061 | 0.00090353 | -0.0086666 | 0.07782 | 0.07782 | 0.027466 | 0.073242 | 0.27008 | 0.018311 | -0.10071 | 0.027466 | 0.073242 | -0.059509 | 0.19684 | 0.16479 | -0.082397 | -0.11902 | 122.6074 | 122.4884 | 0.12817 | 122.6669 | 122.6624 | 0.17395 | -0.064087 | 122.5067 | 122.4701 | 0.054931 | 122.6166 | 122.5296 | 0.05951 | 0.022888 | 122.8592 | 122.6669 | 122.6166 | -0.24262 | 122.7859 | 122.7539 | 122.6624 | -0.26093
1529.4844 | 122.8592 | -122.5983 | 0.17395 | 0.13672 | 0.020401 | 0.0027344 | 0.0049047 | -0.007543 | 0.003497 | -0.0043793 | 0.018082 | -0.0082821 | -0.0034756 | 0.00058739 | 0.0036807 | -0.010376 | -0.032043 | -0.091553 | -0.10071 | -0.082397 | 0.12817 | -0.091553 | -0.24719 | -0.027466 | -0.086975 | -0.13733 | 0.091553 | 0.050354 | -0.15106 | -0.21057 | 122.5067 | 122.3511 | -0.045776 | 122.5067 | 122.5159 | 0.16479 | -0.20599 | 122.4472 | 122.3877 | -0.082397 | 122.5708 | 122.4609 | 0.073242 | -0.1236 | 122.7264 | 122.5662 | 122.4976 | -0.42114 | 122.6898 | 122.6486 | 122.5113 | -0.38452
1531.1719 | 122.9187 | -122.58 | 0.16937 | -0.19897 | 0.021042 | 0.0055114 | 0.0070409 | -0.0069022 | -0.00163 | -0.0067291 | -0.23369 | -0.0099911 | -0.0045438 | -0.001976 | 0.00047633 | -0.010162 | 0.050354 | 0.086975 | 0.027466 | 0.068665 | 0.26093 | 0.018311 | -0.10986 | 0.041199 | 0.091553 | -0.018311 | 0.20599 | 0.14191 | -0.07782 | -0.12817 | 122.5983 | 122.4701 | 0.091552 | 122.6669 | 122.6486 | 0.17853 | -0.11902 | 122.5021 | 122.4518 | 0.036621 | 122.6212 | 122.5616 | 0.10986 | -0.027466 | 122.8409 | 122.6303 | 122.6074 | -0.27924 | 122.7859 | 122.7219 | 122.6715 | -0.29755
1532.8594 | 122.8317 | -122.6166 | 0.16479 | 0.068054 | 0.022324 | 0.0042298 | 0.0036231 | -0.0047658 | 0.0024288 | -0.0030975 | 0.048599 | -0.0080685 | -0.0051846 | -5.3406e-05 | 0.0070987 | -0.0093076 | -0.064087 | -0.073242 | -0.09613 | -0.050354 | 0.15106 | -0.091553 | -0.21973 | -0.041199 | -0.10071 | -0.14191 | 0.10529 | 0.064087 | -0.15564 | -0.21057 | 122.525 | 122.3969 | -0.013733 | 122.5433 | 122.5662 | 0.16937 | -0.22888 | 122.4609 | 122.406 | -0.059509 | 122.5754 | 122.4747 | 0.068664 | -0.10071 | 122.7676 | 122.5525 | 122.5204 | -0.38452 | 122.7219 | 122.6807 | 122.5159 | -0.37537
1534.5469 | 122.9279 | -122.5891 | 0.13275 | -0.00061023 | 0.018051 | 0.0038024 | 0.0051183 | -0.0062612 | -0.006757 | -0.0048065 | 0.056228 | -0.010205 | -0.0062528 | 0.00016019 | -0.0012327 | -0.0075986 | 0.036621 | 0.086975 | 0.059509 | 0.050354 | 0.16937 | -0.009155 | -0.13733 | 0.10529 | 0.17853 | 0.054932 | 0.1236 | 0.09613 | -0.068665 | -0.10529 | 122.58 | 122.4518 | 0.036622 | 122.6761 | 122.6395 | 0.18768 | -0.09613 | 122.5204 | 122.4838 | -0.009155 | 122.6944 | 122.644 | 0.16022 | -0.036621 | 122.7585 | 122.6257 | 122.6486 | -0.27008 | 122.7127 | 122.6852 | 122.7676 | -0.23804
1536.2344 | 122.9233 | -122.5937 | 0.14191 | -0.023499 | 0.018051 | 0.0025208 | 0.0068273 | -0.007543 | -0.0046206 | -0.0073701 | 0.071487 | -0.0091367 | -0.0030484 | 0.00016019 | -0.00037807 | -0.009094 | 0.022888 | 0.059509 | 0.073242 | 0.064087 | 0.16937 | -0.004578 | -0.14648 | 0.082397 | 0.14648 | 0.036621 | 0.1236 | 0.09613 | -0.068665 | -0.1236 | 122.5891 | 122.4472 | 0.027466 | 122.6532 | 122.6578 | 0.21057 | -0.11902 | 122.525 | 122.4701 | -0.018311 | 122.6761 | 122.6303 | 0.16022 | -0.045777 | 122.7631 | 122.6166 | 122.6669 | -0.28839 | 122.7173 | 122.6898 | 122.7402 | -0.2655
1537.9844 | 122.9507 | -122.5845 | 0.14191 | -0.046387 | 0.017624 | 0.0052978 | 0.0066137 | -0.0049796 | -0.004407 | -0.0065155 | -0.073471 | -0.0072141 | -0.0024076 | -0.001976 | -0.00037807 | -0.011017 | 0.11444 | 0.11444 | 0.10071 | 0.082397 | 0.1831 | 0.027466 | -0.12817 | 0.15564 | 0.21973 | 0.10071 | 0.12817 | 0.09613 | -0.027466 | -0.10071 | 122.612 | 122.4564 | 0.041198 | 122.699 | 122.6669 | 0.21057 | -0.027466 | 122.5571 | 122.4838 | -0.013733 | 122.7402 | 122.6852 | 0.20142 | -0.045777 | 122.7676 | 122.699 | 122.6852 | -0.27008 | 122.7127 | 122.6807 | 122.8043 | -0.24262
1539.6719 | 122.8638 | -122.6166 | 0.16022 | 0.17487 | 0.021256 | 0.0033752 | -0.00022208 | -0.0047658 | 0.0020016 | -0.0039521 | 0.15541 | -0.0070003 | -0.0062528 | 0.0022964 | 0.0075259 | -0.01358 | 0.004578 | -0.064087 | -0.059509 | -0.050354 | 0.13733 | -0.073242 | -0.2243 | 0.054932 | -0.032043 | -0.086975 | 0.064087 | 0.032043 | -0.12817 | -0.18768 | 122.5433 | 122.3923 | -0.022888 | 122.5525 | 122.5662 | 0.17395 | -0.15564 | 122.4884 | 122.4289 | -0.09613 | 122.6715 | 122.5296 | 0.10071 | -0.12817 | 122.7539 | 122.6212 | 122.5571 | -0.38452 | 122.6807 | 122.6486 | 122.5845 | -0.3479
1541.375 | 122.8134 | -122.5983 | 0.16937 | 0.19012 | 0.01976 | 0.0057252 | 0.00020512 | -0.0051932 | -0.00098918 | -0.0048065 | 0.17067 | -0.010205 | -0.00668 | -0.0021896 | 0.0066715 | -0.011017 | 0.054932 | 0.045776 | 0.059509 | 0.018311 | 0.07782 | -0.054932 | -0.21057 | 0.082397 | 0.07782 | -0.004578 | 0.022888 | 0.022888 | -0.13733 | -0.1831 | 122.5433 | 122.3877 | -0.091553 | 122.644 | 122.6166 | 0.22888 | -0.11444 | 122.4609 | 122.4152 | -0.14649 | 122.6807 | 122.5937 | 0.17853 | -0.14649 | 122.6761 | 122.6532 | 122.6578 | -0.37994 | 122.6212 | 122.6212 | 122.6761 | -0.35248
1543.0469 | 122.9324 | -122.5754 | 0.13733 | -0.13794 | 0.026383 | 0.0018798 | 0.0051183 | -0.0051932 | 0.0028562 | -0.0048065 | -0.14214 | -0.0074277 | -0.0047574 | 0.00080099 | 0.0049625 | -0.01123 | 0.11444 | 0.045776 | 0.022888 | 0.059509 | 0.20599 | -0.013733 | -0.15564 | 0.050354 | 0.032043 | -0.059509 | 0.12817 | 0.10071 | -0.10986 | -0.15564 | 122.5616 | 122.4197 | 0.068665 | 122.6212 | 122.6349 | 0.21515 | -0.022888 | 122.4655 | 122.4197 | -0.009155 | 122.6257 | 122.5159 | 0.096131 | -0.036621 | 122.7814 | 122.6898 | 122.5983 | -0.29297 | 122.7036 | 122.6761 | 122.6074 | -0.29297
1544.7344 | 122.8912 | -122.6166 | 0.14648 | 0.022278 | 0.021256 | 0.0067932 | 0.0061865 | -0.0066884 | -0.0048344 | -0.0037385 | 0.079117 | -0.0091367 | -0.0053982 | -0.00026701 | -0.00080527 | -0.011871 | 0.032043 | 0.054932 | 0.064087 | 0.050354 | 0.16479 | 0.004578 | -0.14648 | 0.082397 | 0.13275 | 0.009155 | 0.1236 | 0.073242 | -0.086975 | -0.12817 | 122.6212 | 122.4701 | 0.018311 | 122.6715 | 122.6669 | 0.19684 | -0.11444 | 122.5296 | 122.4884 | -0.022888 | 122.699 | 122.6257 | 0.13733 | -0.073242 | 122.7814 | 122.6486 | 122.6807 | -0.29297 | 122.7402 | 122.6898 | 122.7493 | -0.27466
1546.4219 | 122.8592 | -122.6028 | 0.17395 | 0.098572 | 0.019974 | 0.0038024 | 0.0012731 | -0.0069022 | 0.0015744 | -0.0024567 | 0.14015 | -0.0082821 | -0.0047574 | -0.0013352 | 0.0058169 | -0.011444 | 0.004578 | -0.059509 | -0.059509 | -0.032043 | 0.16022 | -0.073242 | -0.22888 | 0.032043 | -0.036621 | -0.073242 | 0.07782 | 0.013733 | -0.15564 | -0.20599 | 122.5296 | 122.374 | -0.013733 | 122.5433 | 122.5708 | 0.19684 | -0.16937 | 122.4472 | 122.3969 | -0.09613 | 122.6349 | 122.5296 | 0.13275 | -0.16022 | 122.7631 | 122.6074 | 122.5433 | -0.40283 | 122.6807 | 122.6166 | 122.5662 | -0.37994
1548.125 | 122.9507 | -122.5845 | 0.1236 | -0.12268 | 0.020615 | 0.0055114 | 0.0066137 | -0.007543 | -0.0014164 | -0.0067291 | -0.13451 | -0.0084957 | -0.0030484 | -0.0017624 | -0.00037807 | -0.0099484 | 0.16937 | 0.19684 | 0.19226 | 0.14648 | 0.19226 | 0.050354 | -0.10529 | 0.16022 | 0.2655 | 0.10986 | 0.13733 | 0.11444 | -0.041199 | -0.091553 | 122.6349 | 122.4792 | 0.068665 | 122.7814 | 122.731 | 0.25177 | 0.045777 | 122.5433 | 122.493 | 0.013733 | 122.7448 | 122.6944 | 0.20142 | -0.009155 | 122.7768 | 122.7539 | 122.7768 | -0.22888 | 122.7219 | 122.699 | 122.85 | -0.21515
1549.8125 | 122.9691 | -122.6028 | 0.15106 | -0.25238 | 0.020828 | 0.0044434 | 0.0061865 | -0.002416 | 0.0011472 | -0.0060883 | -0.23369 | -0.0082821 | -0.0064664 | -0.00026701 | 0.0030399 | -0.012726 | 0.11444 | 0.059509 | 0.027466 | 0.07782 | 0.28381 | 0.041199 | -0.1236 | 0.045776 | 0.045776 | -0.064087 | 0.20599 | 0.17853 | -0.091553 | -0.13275 | 122.644 | 122.4792 | 0.13275 | 122.6624 | 122.6807 | 0.20142 | -0.036621 | 122.5113 | 122.4701 | 0.054932 | 122.6486 | 122.5388 | 0.068664 | 0.027466 | 122.8867 | 122.7173 | 122.6303 | -0.27466 | 122.8088 | 122.7814 | 122.6486 | -0.28381
1551.5156 | 122.9095 | -122.6074 | 0.14191 | -0.1532 | 0.023178 | 0.0076478 | 0.0055457 | -0.0071158 | -0.0029118 | -0.0058747 | -0.14214 | -0.010205 | -0.0028348 | -0.001976 | 0.0030399 | -0.01123 | 0.13275 | 0.16937 | 0.15106 | 0.13733 | 0.20142 | 0.064087 | -0.10071 | 0.14191 | 0.22888 | 0.068665 | 0.15106 | 0.10986 | -0.041199 | -0.11902 | 122.6715 | 122.5067 | 0.059509 | 122.7768 | 122.7448 | 0.23804 | -0.009156 | 122.5662 | 122.4884 | 0.009155 | 122.7493 | 122.6761 | 0.18768 | -0.032044 | 122.8088 | 122.7402 | 122.7585 | -0.24262 | 122.7585 | 122.7173 | 122.8363 | -0.26093
1553.2031 | 122.8729 | -122.6166 | 0.16937 | 0.14435 | 0.020615 | 0.0042298 | 0.0014867 | -0.0049796 | 0.00050622 | -0.0043793 | 0.086746 | -0.0089229 | -0.0068936 | -5.3406e-05 | 0.0060305 | -0.010589 | 0.041199 | 0.050354 | 0.032043 | 0.013733 | 0.11902 | -0.045776 | -0.19226 | 0.07782 | 0.054932 | -0.013733 | 0.059509 | 0.004578 | -0.11902 | -0.16479 | 122.5708 | 122.4243 | -0.050354 | 122.6669 | 122.6303 | 0.20599 | -0.12817 | 122.4976 | 122.4518 | -0.10986 | 122.6944 | 122.6028 | 0.15106 | -0.16479 | 122.7356 | 122.6578 | 122.6486 | -0.36163 | 122.6761 | 122.6212 | 122.6715 | -0.33417
1554.9375 | 122.8638 | -122.612 | 0.17395 | 0.11383 | 0.020401 | 0.0042298 | 0.0029821 | -0.0051932 | 0.0028562 | -0.0041657 | 0.056228 | -0.0093503 | -0.0058254 | -0.00048061 | 0.0064577 | -0.0082394 | -0.022888 | -0.073242 | -0.064087 | -0.054932 | 0.13733 | -0.07782 | -0.24261 | 0.013733 | -0.068665 | -0.1236 | 0.10529 | 0.059509 | -0.16022 | -0.21057 | 122.5342 | 122.3694 | -0.036621 | 122.5388 | 122.5571 | 0.18768 | -0.19684 | 122.4518 | 122.4014 | -0.068664 | 122.6257 | 122.4884 | 0.086975 | -0.11444 | 122.7493 | 122.5891 | 122.5479 | -0.41656 | 122.7173 | 122.6715 | 122.5433 | -0.38452
1556.625 | 122.8912 | -122.5983 | 0.15564 | -0.27527 | 0.021042 | 0.002948 | 0.0087499 | -0.004125 | -0.002698 | -0.0056611 | -0.19554 | -0.0076413 | -0.0043302 | -0.00090781 | 0.00047633 | -0.010589 | 0.10986 | 0.13733 | 0.10529 | 0.1236 | 0.26093 | 0.059509 | -0.091553 | 0.064087 | 0.11902 | -0.018311 | 0.19226 | 0.14191 | -0.068665 | -0.1236 | 122.6578 | 122.5067 | 0.10529 | 122.7356 | 122.7219 | 0.21515 | -0.045777 | 122.5296 | 122.4747 | 0.036621 | 122.6624 | 122.58 | 0.10528 | -0.013733 | 122.8592 | 122.7081 | 122.7036 | -0.24719 | 122.7905 | 122.7402 | 122.7173 | -0.27924
1558.3438 | 122.8409 | -122.6349 | 0.16479 | 0.014648 | 0.022537 | 0.0048706 | 0.0012731 | -0.0064748 | 0.001788 | -0.0033111 | 0.04097 | -0.0042233 | -0.006039 | 0.0022964 | 0.0066715 | -0.01123 | -0.027466 | -0.09613 | -0.07782 | -0.054932 | 0.16022 | -0.073242 | -0.21057 | -0.027466 | -0.091553 | -0.16479 | 0.10529 | 0.068665 | -0.16022 | -0.21057 | 122.5616 | 122.4243 | -0.004578 | 122.5388 | 122.58 | 0.15564 | -0.19226 | 122.4747 | 122.4243 | -0.059509 | 122.6074 | 122.4701 | 0.045776 | -0.09613 | 122.7951 | 122.6074 | 122.5571 | -0.37537 | 122.7402 | 122.7036 | 122.5433 | -0.37537
1560.0469 | 122.9645 | -122.5983 | 0.14648 | -0.23712 | 0.023605 | 0.0059388 | 0.010673 | -0.0071158 | -0.0022708 | -0.0048065 | -0.24895 | -0.0061459 | -0.003262 | 0.0020828 | 0.0015445 | -0.012726 | 0.091553 | 0.068665 | 0.059509 | 0.068665 | 0.27466 | 0.050354 | -0.11902 | 0.027466 | 0.068665 | -0.036621 | 0.17853 | 0.16937 | -0.068665 | -0.12817 | 122.6486 | 122.4792 | 0.12817 | 122.6669 | 122.6669 | 0.18768 | -0.054931 | 122.5296 | 122.4701 | 0.032044 | 122.6257 | 122.5616 | 0.091553 | 0.022889 | 122.8729 | 122.6898 | 122.6578 | -0.2655 | 122.7768 | 122.7676 | 122.6669 | -0.27466
1561.7344 | 122.8088 | -122.644 | 0.1831 | 0.1825 | 0.018906 | 0.004657 | 0.00020512 | -0.0081838 | -0.0031254 | -0.0050201 | 0.15541 | -0.0082821 | -0.0051846 | -0.0038986 | 0.0041079 | -0.0099484 | 0.045776 | 0.068665 | 0.07782 | 0.022888 | 0.09613 | -0.054932 | -0.18768 | 0.086975 | 0.12817 | 0.004578 | 0.045776 | 0.027466 | -0.10986 | -0.17395 | 122.5891 | 122.4564 | -0.086975 | 122.7127 | 122.6669 | 0.21057 | -0.13733 | 122.5342 | 122.4701 | -0.13733 | 122.731 | 122.6486 | 0.17853 | -0.15564 | 122.7402 | 122.6898 | 122.7219 | -0.37079 | 122.6898 | 122.6715 | 122.7722 | -0.35706
1563.4844 | 122.9279 | -122.5983 | 0.14648 | 0.0070193 | 0.019974 | 0.0048706 | 0.0044775 | -0.0051932 | -0.0059024 | -0.0050201 | 0.03334 | -0.010205 | -0.0056118 | -0.0026168 | 0.00026273 | -0.008453 | 0.059509 | 0.091553 | 0.10071 | 0.073242 | 0.18768 | 0.009155 | -0.11902 | 0.11444 | 0.16937 | 0.045776 | 0.13733 | 0.10529 | -0.068665 | -0.12817 | 122.6074 | 122.4792 | 0.041199 | 122.6898 | 122.6715 | 0.19226 | -0.086975 | 122.5296 | 122.4701 | -0.009155 | 122.7127 | 122.644 | 0.17395 | -0.041198 | 122.786 | 122.6578 | 122.699 | -0.2655 | 122.7356 | 122.7036 | 122.7676 | -0.27466
1565.1719 | 122.9095 | -122.5845 | 0.14648 | -0.17609 | 0.021256 | 0.0040162 | 0.0096045 | -0.0051932 | -0.0046206 | -0.0026703 | -0.14977 | -0.010205 | -0.0034756 | -5.3406e-05 | 0.0013309 | -0.013366 | 0.17395 | 0.16937 | 0.17395 | 0.14648 | 0.23346 | 0.050354 | -0.086975 | 0.13275 | 0.23346 | 0.073242 | 0.13275 | 0.13275 | -0.054932 | -0.10986 | 122.6349 | 122.4976 | 0.086975 | 122.7539 | 122.731 | 0.23346 | 0.027466 | 122.5296 | 122.4747 | -0.013733 | 122.7173 | 122.6578 | 0.18311 | -0.013733 | 122.818 | 122.7585 | 122.7585 | -0.23346 | 122.7173 | 122.7173 | 122.818 | -0.25635
1566.8906 | 122.9553 | -122.5983 | 0.14648 | -0.19897 | 0.02211 | 0.0050842 | 0.0036231 | -0.005834 | 0.00093342 | -0.0045929 | -0.21843 | -0.0065731 | -0.0041164 | -0.00026701 | 0.0051761 | -0.012298 | 0.12817 | 0.059509 | 0.036621 | 0.091553 | 0.24261 | 0.018311 | -0.11444 | 0.041199 | 0.059509 | -0.050354 | 0.14648 | 0.1236 | -0.09613 | -0.17395 | 122.6166 | 122.4838 | 0.096131 | 122.6578 | 122.6898 | 0.20599 | -0.01831 | 122.5021 | 122.4243 | 0 | 122.6395 | 122.5479 | 0.1236 | -0.022888 | 122.8409 | 122.7264 | 122.6349 | -0.26093 | 122.7448 | 122.7219 | 122.6578 | -0.32043
1568.5781 | 122.905 | -122.6166 | 0.16022 | -0.19897 | 0.021256 | 0.002948 | 0.0078955 | -0.0073294 | -0.0012028 | -0.0063019 | -0.18028 | -0.0078549 | -0.0024076 | -5.3406e-05 | 0.00090353 | -0.01123 | 0.12817 | 0.086975 | 0.09613 | 0.09613 | 0.26093 | 0.045776 | -0.10529 | 0.036621 | 0.10986 | -0.009155 | 0.19226 | 0.16022 | -0.082397 | -0.1236 | 122.6624 | 122.5113 | 0.10071 | 122.7036 | 122.7127 | 0.20142 | -0.032043 | 122.5342 | 122.493 | 0.032044 | 122.6532 | 122.6074 | 0.11444 | 0 | 122.8775 | 122.7448 | 122.7127 | -0.2655 | 122.8088 | 122.7768 | 122.7264 | -0.28381
1570.2812 | 122.9233 | -122.5754 | 0.13733 | -0.22186 | 0.016983 | 0.0055114 | 0.0059729 | -0.0066884 | -0.004407 | -0.0039521 | -0.16502 | -0.011487 | -0.0047574 | -0.0030442 | 0.0032535 | -0.010376 | 0.16479 | 0.21515 | 0.19226 | 0.14648 | 0.23346 | 0.068665 | -0.082397 | 0.16022 | 0.27466 | 0.09613 | 0.14648 | 0.11444 | -0.032043 | -0.07782 | 122.644 | 122.493 | 0.09613 | 122.7905 | 122.7219 | 0.22888 | 0.027466 | 122.5433 | 122.4976 | 0.009155 | 122.7356 | 122.6715 | 0.17395 | -0.022888 | 122.8088 | 122.7402 | 122.7676 | -0.21973 | 122.7219 | 122.6898 | 122.85 | -0.21515
1571.9531 | 122.8592 | -122.6074 | 0.17853 | 0.052795 | 0.01741 | 0.0055114 | 0.0051183 | -0.004125 | -0.0052616 | -0.0054475 | 0.048599 | -0.011487 | -0.0058254 | -0.00069421 | 0.0036807 | -0.0097348 | 0.059509 | 0.07782 | 0.091553 | 0.045776 | 0.15564 | 0.009155 | -0.13733 | 0.082397 | 0.1236 | 0.009155 | 0.11902 | 0.086975 | -0.068665 | -0.13733 | 122.6166 | 122.4701 | -0.022888 | 122.6852 | 122.6532 | 0.18311 | -0.11902 | 122.5388 | 122.4701 | -0.059509 | 122.6898 | 122.6166 | 0.14648 | -0.091553 | 122.7631 | 122.6669 | 122.699 | -0.31586 | 122.7264 | 122.6944 | 122.731 | -0.31586
1573.6562 | 122.9187 | -122.6166 | 0.15564 | -0.19135 | 0.022324 | 0.0035888 | 0.0059729 | -0.0039114 | -0.00077538 | -0.0067291 | -0.20317 | -0.0099911 | -0.0075344 | -0.00069421 | 0.0017581 | -0.012298 | 0.16022 | 0.19226 | 0.16479 | 0.14648 | 0.2243 | 0.050354 | -0.086975 | 0.13275 | 0.21973 | 0.050354 | 0.15564 | 0.13275 | -0.027466 | -0.09613 | 122.6669 | 122.5296 | 0.068664 | 122.8088 | 122.7631 | 0.23346 | 0.004577 | 122.5891 | 122.5204 | 0 | 122.7493 | 122.6669 | 0.14648 | -0.022889 | 122.8409 | 122.7768 | 122.7814 | -0.24261 | 122.7722 | 122.7493 | 122.8363 | -0.25177
1575.3438 | 122.9645 | -122.5891 | 0.14191 | -0.19135 | 0.025314 | 0.0048706 | 0.0081091 | -0.0060476 | 0.0020016 | -0.0056611 | -0.24895 | -0.0076413 | -0.0036892 | 0.00058739 | 0.0043215 | -0.012298 | 0.10529 | 0.054932 | 0.045776 | 0.07782 | 0.27924 | 0.032043 | -0.1236 | 0.050354 | 0.068665 | -0.050354 | 0.18768 | 0.14191 | -0.068665 | -0.11902 | 122.6212 | 122.4655 | 0.13733 | 122.644 | 122.6669 | 0.20142 | -0.036621 | 122.5204 | 122.4701 | 0.045776 | 122.6395 | 122.5388 | 0.068665 | 0 | 122.8683 | 122.6944 | 122.6349 | -0.2655 | 122.7768 | 122.731 | 122.6578 | -0.26093
1577.0312 | 122.8638 | -122.6395 | 0.16022 | 0.1062 | 0.021683 | 0.0035888 | 0.0027685 | -0.0051932 | 0.0028562 | -0.0037385 | 0.071487 | -0.0072141 | -0.0073208 | -0.00069421 | 0.0075259 | -0.0095212 | -0.013733 | -0.068665 | -0.032043 | -0.027466 | 0.17853 | -0.064087 | -0.21515 | -0.009155 | -0.064087 | -0.14191 | 0.10071 | 0.091553 | -0.15564 | -0.19684 | 122.5754 | 122.4243 | 0.018311 | 122.5708 | 122.612 | 0.18768 | -0.17395 | 122.4838 | 122.4426 | -0.059509 | 122.6303 | 122.4976 | 0.054931 | -0.068664 | 122.818 | 122.6257 | 122.6074 | -0.37537 | 122.7402 | 122.731 | 122.5754 | -0.35706
1578.75 | 122.9828 | -122.6074 | 0.13733 | -0.17609 | 0.020828 | 0.0048706 | 0.0057593 | -0.0047658 | -0.00013458 | -0.0035249 | -0.23369 | -0.0084957 | -0.0036892 | -0.0017624 | 0.0030399 | -0.010162 | 0.082397 | 0.064087 | 0.059509 | 0.073242 | 0.26093 | 0.027466 | -0.11902 | 0.050354 | 0.082397 | -0.041199 | 0.16937 | 0.15564 | -0.064087 | -0.14191 | 122.6349 | 122.4884 | 0.1236 | 122.6715 | 122.6807 | 0.19226 | -0.054932 | 122.5433 | 122.4655 | 0.032044 | 122.6578 | 122.5662 | 0.10071 | 0.018311 | 122.8683 | 122.6898 | 122.6669 | -0.25635 | 122.7768 | 122.7631 | 122.6898 | -0.27924
1580.4219 | 122.905 | -122.5937 | 0.15564 | -0.24475 | 0.024033 | 0.0044434 | 0.0078955 | -0.0047658 | -0.004407 | -0.0058747 | -0.20317 | -0.0093503 | -0.0041164 | 0.00058739 | 0.00090353 | -0.010376 | 0.13275 | 0.16479 | 0.16022 | 0.14191 | 0.24261 | 0.054932 | -0.09613 | 0.09613 | 0.1831 | 0.018311 | 0.19684 | 0.16479 | -0.036621 | -0.086975 | 122.6486 | 122.4976 | 0.086975 | 122.7585 | 122.7356 | 0.23804 | -0.022889 | 122.5571 | 122.5067 | 0.041198 | 122.6898 | 122.612 | 0.10529 | 0.009155 | 122.8363 | 122.7264 | 122.7539 | -0.25177 | 122.7905 | 122.7585 | 122.7768 | -0.24261
1582.125 | 122.9324 | -122.6028 | 0.12817 | -0.084534 | 0.023392 | 0.0023072 | 0.0029821 | -0.0066884 | 0.00029262 | -0.0048065 | -0.18028 | -0.0070003 | -0.0075344 | 0.00037379 | 0.0079531 | -0.011657 | 0.10529 | 0.086975 | 0.068665 | 0.059509 | 0.21057 | -0.013733 | -0.14191 | 0.059509 | 0.064087 | -0.059509 | 0.10529 | 0.091553 | -0.1236 | -0.17395 | 122.5891 | 122.4609 | 0.082397 | 122.6898 | 122.6624 | 0.20142 | -0.022888 | 122.4792 | 122.4289 | -0.022888 | 122.6624 | 122.5433 | 0.11444 | -0.036621 | 122.8134 | 122.7081 | 122.6715 | -0.27008 | 122.7081 | 122.6944 | 122.6669 | -0.30212
1583.8125 | 122.9736 | -122.6074 | 0.15106 | -0.19897 | 0.023392 | 0.0044434 | 0.0053321 | -0.0060476 | 0.00093342 | -0.0045929 | -0.20317 | -0.0067867 | -0.0045438 | -0.0017624 | 0.0026125 | -0.011017 | 0.091553 | 0.059509 | 0.059509 | 0.091553 | 0.25177 | 0.041199 | -0.12817 | 0.041199 | 0.082397 | -0.036621 | 0.17853 | 0.15106 | -0.091553 | -0.16022 | 122.6486 | 122.4792 | 0.10071 | 122.6669 | 122.699 | 0.21973 | -0.059509 | 122.5159 | 122.4472 | 0.027466 | 122.6486 | 122.5708 | 0.1236 | 0 | 122.8592 | 122.699 | 122.6669 | -0.27924 | 122.7859 | 122.7585 | 122.6898 | -0.31128
1585.5 | 122.8546 | -122.6349 | 0.17395 | 0.11383 | 0.01976 | 0.0040162 | 0.0025549 | -0.004125 | -0.0024844 | -0.0035249 | 0.20119 | -0.0080685 | -0.004971 | -0.00026701 | 0.0036807 | -0.0099484 | 0.054932 | 0.07782 | 0.10529 | 0.045776 | 0.1236 | -0.032043 | -0.1831 | 0.086975 | 0.1236 | -0.004578 | 0.045776 | 0.022888 | -0.11902 | -0.17395 | 122.6028 | 122.4518 | -0.050354 | 122.7127 | 122.6807 | 0.22888 | -0.11902 | 122.5159 | 122.4609 | -0.12817 | 122.7219 | 122.6303 | 0.16937 | -0.15106 | 122.7585 | 122.6898 | 122.7402 | -0.35706 | 122.6807 | 122.6578 | 122.7585 | -0.3479
1587.1875 | 122.85 | -122.6303 | 0.16022 | 0.022278 | 0.019119 | 0.0078614 | 0.0023413 | -0.0034842 | -0.0054752 | -0.0067291 | 0.12489 | -0.0093503 | -0.0056118 | -0.001976 | 0.0028263 | -0.009094 | 0.054932 | 0.082397 | 0.11444 | 0.054932 | 0.18768 | 0.009155 | -0.11444 | 0.073242 | 0.14648 | 0.013733 | 0.11444 | 0.11902 | -0.059509 | -0.12817 | 122.6395 | 122.5159 | 0.027466 | 122.7127 | 122.6852 | 0.16937 | -0.10528 | 122.5708 | 122.5021 | -0.045776 | 122.7036 | 122.644 | 0.14191 | -0.041198 | 122.818 | 122.6852 | 122.7448 | -0.27466 | 122.7448 | 122.7493 | 122.7768 | -0.28839
1588.875 | 122.8775 | -122.5937 | 0.17395 | 0.12909 | 0.021469 | 0.0050842 | 0.0023413 | -0.0071158 | 0.0015744 | -0.0039521 | 0.16304 | -0.0063595 | -0.0075344 | -0.0011216 | 0.0066715 | -0.012512 | 0.013733 | -0.041199 | 0.013733 | -0.022888 | 0.17395 | -0.050354 | -0.21515 | 0.036621 | 0.027466 | -0.064087 | 0.09613 | 0.064087 | -0.11444 | -0.1831 | 122.5433 | 122.3785 | 0 | 122.5525 | 122.5708 | 0.19226 | -0.16022 | 122.4792 | 122.4106 | -0.07782 | 122.6303 | 122.5296 | 0.11902 | -0.10986 | 122.7676 | 122.6074 | 122.6074 | -0.3891 | 122.6898 | 122.6578 | 122.6212 | -0.35706
1590.5625 | 122.85 | -122.6303 | 0.18768 | 0.11383 | 0.023392 | 0.0020936 | 0.0038367 | -0.0049796 | 0.0024288 | -0.0022431 | 0.094375 | -0.0082821 | -0.0051846 | -0.00026701 | 0.0058169 | -0.011871 | 0.004578 | -0.064087 | -0.022888 | -0.022888 | 0.16022 | -0.050354 | -0.21057 | -0.018311 | -0.054932 | -0.13733 | 0.11902 | 0.091553 | -0.13733 | -0.20599 | 122.58 | 122.4197 | -0.027466 | 122.5662 | 122.6074 | 0.18768 | -0.1831 | 122.493 | 122.4243 | -0.068664 | 122.612 | 122.493 | 0.068665 | -0.09613 | 122.7905 | 122.6349 | 122.6074 | -0.39825 | 122.7493 | 122.7219 | 122.5754 | -0.39368
1592.2656 | 122.9004 | -122.6349 | 0.16022 | 0.029907 | 0.022751 | 0.0048706 | 0.0059729 | -0.0073294 | -0.0065434 | -0.0056611 | 0.086746 | -0.0095639 | -0.0051846 | -0.001976 | -0.0012327 | -0.010803 | 0.050354 | 0.086975 | 0.10529 | 0.068665 | 0.20599 | 0.032043 | -0.1236 | 0.091553 | 0.16022 | 0.022888 | 0.13275 | 0.10529 | -0.050354 | -0.1236 | 122.6669 | 122.5113 | 0.045777 | 122.7219 | 122.7036 | 0.19226 | -0.10986 | 122.5845 | 122.5113 | -0.027466 | 122.7264 | 122.6578 | 0.14648 | -0.054931 | 122.8409 | 122.6852 | 122.7402 | -0.28381 | 122.7676 | 122.7402 | 122.7951 | -0.28381
1594 | 122.9095 | -122.6212 | 0.13733 | -0.17609 | 0.023178 | 0.0061524 | 0.0076819 | -0.0036978 | -0.0024844 | -0.0052337 | -0.20317 | -0.010418 | -0.0053982 | -0.0015488 | 4.9132e-05 | -0.013153 | 0.16479 | 0.17395 | 0.18768 | 0.16479 | 0.2243 | 0.059509 | -0.082397 | 0.10986 | 0.21515 | 0.054932 | 0.1831 | 0.16022 | -0.045776 | -0.09613 | 122.6807 | 122.5388 | 0.086975 | 122.7951 | 122.7859 | 0.24719 | 0.027466 | 122.5754 | 122.525 | 0.045776 | 122.731 | 122.6761 | 0.15106 | 0.022888 | 122.8455 | 122.7859 | 122.8088 | -0.21973 | 122.8043 | 122.7814 | 122.8363 | -0.23346
1595.6875 | 122.85 | -122.6212 | 0.16022 | 0.060425 | 0.020828 | 0.0067932 | 0.0034093 | -0.0049796 | -0.002698 | -0.0063019 | 0.086746 | -0.0082821 | -0.0062528 | -0.0017624 | 0.0028263 | -0.010589 | 0.091553 | 0.082397 | 0.1236 | 0.064087 | 0.18768 | 0.032043 | -0.13733 | 0.07782 | 0.15106 | 0.018311 | 0.13275 | 0.10071 | -0.059509 | -0.13275 | 122.6532 | 122.4838 | 0.027466 | 122.7036 | 122.6852 | 0.20142 | -0.068664 | 122.5616 | 122.4884 | -0.027466 | 122.699 | 122.6395 | 0.15106 | -0.059509 | 122.8088 | 122.7127 | 122.7448 | -0.29755 | 122.7539 | 122.7219 | 122.7722 | -0.29297
1597.375 | 122.8409 | -122.6624 | 0.17853 | 0.090942 | 0.024033 | 0.0035888 | 0.0019141 | -0.0064748 | 0.004565 | -0.0024567 | -0.050583 | -0.0057187 | -0.0047574 | 0.0010148 | 0.0056033 | -0.015503 | 0.036621 | -0.050354 | -0.009155 | -0.009155 | 0.18768 | -0.027466 | -0.20142 | -0.022888 | -0.018311 | -0.13733 | 0.12817 | 0.091553 | -0.16022 | -0.17853 | 122.6349 | 122.4609 | 0.009155 | 122.612 | 122.6532 | 0.19226 | -0.14191 | 122.5021 | 122.4838 | -0.050354 | 122.6395 | 122.525 | 0.041199 | -0.086975 | 122.85 | 122.699 | 122.6532 | -0.37994 | 122.7905 | 122.7539 | 122.644 | -0.35706
1599.0625 | 123.0011 | -122.5708 | 0.15564 | -0.16083 | 0.020615 | 0.0055114 | 0.0049047 | -0.0056204 | -0.00034818 | -0.0063019 | -0.23369 | -0.0082821 | -0.0056118 | 0.00037379 | 0.0045351 | -0.012512 | 0.10986 | 0.059509 | 0.068665 | 0.10529 | 0.27466 | 0.050354 | -0.10071 | 0.054932 | 0.09613 | -0.050354 | 0.16937 | 0.15106 | -0.068665 | -0.12817 | 122.6212 | 122.4701 | 0.11902 | 122.6303 | 122.6761 | 0.20599 | -0.045777 | 122.5021 | 122.4426 | 0.013733 | 122.6257 | 122.5204 | 0.07782 | -0.004578 | 122.8455 | 122.6807 | 122.6395 | -0.25635 | 122.7402 | 122.7219 | 122.6669 | -0.28381
1600.7344 | 122.8455 | -122.6257 | 0.18768 | 0.15198 | 0.021256 | 0.0052978 | -0.00043588 | -0.0051932 | -0.0029118 | -0.0020295 | 0.1783 | -0.0080685 | -0.00668 | -0.0015488 | 0.0032535 | -0.010589 | 0.082397 | 0.086975 | 0.12817 | 0.032043 | 0.10986 | -0.036621 | -0.16937 | 0.091553 | 0.15564 | 0.013733 | 0.054932 | 0.036621 | -0.10529 | -0.17395 | 122.5891 | 122.4564 | -0.07782 | 122.7127 | 122.6578 | 0.20142 | -0.10529 | 122.5204 | 122.4518 | -0.13275 | 122.7173 | 122.6395 | 0.18768 | -0.15106 | 122.7356 | 122.7081 | 122.7539 | -0.35706 | 122.6807 | 122.6624 | 122.7814 | -0.36163
1602.4219 | 122.9645 | -122.5845 | 0.15106 | -0.19897 | 0.021256 | 0.0027344 | 0.0042639 | -0.0043386 | 0.0028562 | -0.0052337 | -0.20317 | -0.0080685 | -0.0056118 | -0.00026701 | 0.0068851 | -0.010376 | 0.11902 | 0.086975 | 0.091553 | 0.09613 | 0.27466 | 0.050354 | -0.091553 | 0.059509 | 0.09613 | -0.041199 | 0.16479 | 0.13275 | -0.091553 | -0.13275 | 122.6349 | 122.493 | 0.1236 | 122.6715 | 122.6807 | 0.18768 | -0.032043 | 122.493 | 122.4518 | 0.013733 | 122.644 | 122.5433 | 0.091552 | -0.018311 | 122.8592 | 122.7036 | 122.6761 | -0.24261 | 122.7493 | 122.7173 | 122.6807 | -0.28381
1604.1094 | 122.8729 | -122.644 | 0.15564 | 0.045166 | 0.019333 | 0.0082886 | 0.0081091 | -0.0064748 | -0.004407 | -0.0065155 | 0.10963 | -0.0097775 | -0.0030484 | -0.0030442 | 0.00047633 | -0.0088804 | 0.064087 | 0.082397 | 0.13275 | 0.07782 | 0.19684 | 0.027466 | -0.1236 | 0.082397 | 0.16479 | 0.041199 | 0.13733 | 0.11444 | -0.064087 | -0.10529 | 122.6715 | 122.5204 | 0.041198 | 122.7264 | 122.7219 | 0.20142 | -0.091553 | 122.58 | 122.5388 | -0.018311 | 122.7264 | 122.6852 | 0.14649 | -0.041199 | 122.8409 | 122.7081 | 122.7768 | -0.27924 | 122.7814 | 122.7585 | 122.8088 | -0.26093
1605.8125 | 122.8729 | -122.6257 | 0.15564 | 0.029907 | 0.019119 | 0.004657 | 0.0064001 | -0.0054068 | -0.0039798 | -0.0045929 | 0.086746 | -0.0097775 | -0.0062528 | -0.0015488 | 0.00068993 | -0.011017 | 0.068665 | 0.082397 | 0.12817 | 0.07782 | 0.20142 | 0.041199 | -0.12817 | 0.082397 | 0.16479 | 0.032043 | 0.15106 | 0.11444 | -0.059509 | -0.11902 | 122.6669 | 122.4976 | 0.045776 | 122.7081 | 122.7036 | 0.20599 | -0.086975 | 122.5662 | 122.5067 | -0.004578 | 122.7081 | 122.6578 | 0.15106 | -0.041199 | 122.8271 | 122.6944 | 122.7539 | -0.28381 | 122.7768 | 122.7402 | 122.7905 | -0.27466
1607.5 | 122.8821 | -122.6303 | 0.1831 | 0.12909 | 0.023819 | 0.0031616 | 0.0031957 | -0.005834 | 0.0043514 | -0.0043793 | 0.071487 | -0.0078549 | -0.0053982 | 0.0010148 | 0.0068851 | -0.014221 | 0.032043 | -0.054932 | -0.009155 | -0.022888 | 0.18768 | -0.050354 | -0.19226 | 0.004578 | -0.022888 | -0.1236 | 0.11902 | 0.086975 | -0.14191 | -0.17853 | 122.58 | 122.438 | 0.004578 | 122.5754 | 122.6074 | 0.16937 | -0.15106 | 122.4884 | 122.4518 | -0.064086 | 122.6349 | 122.5067 | 0.054932 | -0.09613 | 122.818 | 122.6624 | 122.6212 | -0.37537 | 122.7493 | 122.7173 | 122.6074 | -0.36163
1609.1875 | 122.8729 | -122.6257 | 0.16022 | 0.029907 | 0.018692 | 0.0040162 | 0.0057593 | -0.0049796 | -0.0056888 | -0.0088653 | 0.056228 | -0.0093503 | -0.0039028 | 0.00016019 | 0.00068993 | -0.010803 | 0.082397 | 0.091553 | 0.12817 | 0.09613 | 0.21057 | 0.032043 | -0.1236 | 0.10529 | 0.17853 | 0.045776 | 0.16479 | 0.10986 | -0.045776 | -0.10986 | 122.6578 | 122.5021 | 0.050354 | 122.7173 | 122.7219 | 0.21973 | -0.07782 | 122.58 | 122.5159 | 0.004578 | 122.731 | 122.6715 | 0.15564 | -0.050354 | 122.8363 | 122.7081 | 122.7539 | -0.28381 | 122.7905 | 122.7356 | 122.8043 | -0.27008
1610.875 | 122.9004 | -122.5983 | 0.17395 | 0.21301 | 0.021469 | 0.0042298 | 0.00041872 | -0.0051932 | 0.00093342 | -0.0052337 | 0.11726 | -0.0080685 | -0.0053982 | -0.00069421 | 0.0049625 | -0.012512 | 0.059509 | 0.013733 | 0.068665 | 0.032043 | 0.15106 | -0.022888 | -0.17853 | 0.09613 | 0.13275 | -0.009155 | 0.068665 | 0.054932 | -0.064087 | -0.15106 | 122.5754 | 122.4197 | -0.022888 | 122.612 | 122.6303 | 0.21057 | -0.11444 | 122.5342 | 122.4472 | -0.10528 | 122.6944 | 122.5891 | 0.14191 | -0.11902 | 122.7493 | 122.6578 | 122.6669 | -0.35248 | 122.6669 | 122.6532 | 122.731 | -0.32501
1612.5625 | 122.9645 | -122.5891 | 0.13733 | -0.10742 | 0.018906 | 0.0042298 | 0.0081091 | -0.0088248 | -0.003339 | -0.0077973 | 0.010452 | -0.0091367 | -0.0045438 | -0.0015488 | -0.00016447 | -0.011657 | 0.21057 | 0.20599 | 0.21973 | 0.16022 | 0.2243 | 0.10071 | -0.059509 | 0.2243 | 0.29297 | 0.14648 | 0.14648 | 0.12817 | -0.022888 | -0.054932 | 122.6898 | 122.5296 | 0.086975 | 122.7951 | 122.7493 | 0.21973 | 0.073242 | 122.5662 | 122.5342 | 0.009155 | 122.8134 | 122.7356 | 0.20142 | -0.009155 | 122.8134 | 122.7997 | 122.8088 | -0.19684 | 122.7356 | 122.7173 | 122.8821 | -0.19226
1614.2656 | 122.8729 | -122.6303 | 0.17853 | -0.061646 | 0.023392 | 0.0018798 | 0.00084592 | -0.0062612 | 0.0049924 | -0.0035249 | -0.11162 | -0.0067867 | -0.004971 | 0.00080099 | 0.0068851 | -0.012939 | 0.15564 | 0.07782 | 0.082397 | 0.054932 | 0.20599 | 0.022888 | -0.1236 | 0.068665 | 0.086975 | -0.054932 | 0.14648 | 0.10986 | -0.10529 | -0.15564 | 122.6532 | 122.5067 | 0.027466 | 122.7081 | 122.6852 | 0.17853 | -0.022888 | 122.525 | 122.4747 | -0.032044 | 122.699 | 122.5754 | 0.10071 | -0.068665 | 122.8363 | 122.7859 | 122.7127 | -0.30212 | 122.7768 | 122.7402 | 122.7173 | -0.33417
1616 | 122.9553 | -122.6028 | 0.15564 | -0.19135 | 0.020615 | 0.0065796 | 0.0087499 | -0.0066884 | -0.0046206 | -0.0054475 | -0.14214 | -0.0097775 | -0.003262 | -0.0015488 | 0.0011173 | -0.011017 | 0.19226 | 0.23346 | 0.24719 | 0.17395 | 0.25177 | 0.082397 | -0.059509 | 0.19684 | 0.32501 | 0.12817 | 0.16479 | 0.14191 | 0.009155 | -0.073242 | 122.6852 | 122.5433 | 0.09613 | 122.8363 | 122.7768 | 0.23346 | 0.036621 | 122.612 | 122.5296 | 0.009155 | 122.7997 | 122.731 | 0.20142 | -0.013733 | 122.8546 | 122.7951 | 122.85 | -0.21515 | 122.7676 | 122.7448 | 122.9279 | -0.22888
1617.6875 | 122.8821 | -122.6715 | 0.1831 | 0.11383 | 0.023605 | 0.0038024 | 0.0036231 | -0.0049796 | 0.004565 | -0.0037385 | 0.056228 | -0.0084957 | -0.004971 | 0.00016019 | 0.0060305 | -0.012939 | 0.027466 | -0.041199 | 0 | -0.009155 | 0.18768 | -0.050354 | -0.20142 | 0.013733 | 0.004578 | -0.10529 | 0.11444 | 0.10986 | -0.13733 | -0.17395 | 122.6212 | 122.4701 | 0.004578 | 122.6303 | 122.6624 | 0.19226 | -0.15564 | 122.5342 | 122.4976 | -0.068664 | 122.6852 | 122.5662 | 0.068664 | -0.073242 | 122.8592 | 122.699 | 122.6715 | -0.38452 | 122.7859 | 122.7814 | 122.6761 | -0.35706
1619.3906 | 122.9782 | -122.6303 | 0.13275 | -0.21423 | 0.02446 | 0.0031616 | 0.0091773 | -0.0054068 | 0.00029262 | -0.0058747 | -0.20317 | -0.0080685 | -0.0058254 | 0.00080099 | 0.0034671 | -0.011444 | 0.10529 | 0.07782 | 0.082397 | 0.10071 | 0.28381 | 0.054932 | -0.10071 | 0.073242 | 0.1236 | -0.027466 | 0.20142 | 0.17853 | -0.045776 | -0.1236 | 122.6852 | 122.5296 | 0.15106 | 122.7081 | 122.731 | 0.20142 | -0.027465 | 122.5845 | 122.5067 | 0.068665 | 122.7036 | 122.6028 | 0.09613 | 0.045777 | 122.9141 | 122.7356 | 122.7127 | -0.23346 | 122.8317 | 122.8088 | 122.7539 | -0.25635
1621.0938 | 122.8409 | -122.6624 | 0.1831 | -0.054016 | 0.023392 | 0.0031616 | 0.0044775 | -0.0056204 | 0.0024288 | -0.0054475 | -0.065842 | -0.0070003 | -0.0056118 | -0.00048061 | 0.0066715 | -0.011657 | 0.086975 | 0.091553 | 0.086975 | 0.045776 | 0.23804 | 0.013733 | -0.13275 | 0.050354 | 0.064087 | -0.073242 | 0.13275 | 0.11444 | -0.11444 | -0.16022 | 122.6761 | 122.5296 | 0.054932 | 122.7539 | 122.7081 | 0.17853 | -0.09613 | 122.5479 | 122.5021 | -0.050354 | 122.7127 | 122.5891 | 0.086975 | -0.068664 | 122.9004 | 122.7493 | 122.7493 | -0.31586 | 122.7951 | 122.7768 | 122.7264 | -0.34332
1622.7656 | 122.9736 | -122.6028 | 0.13275 | -0.092163 | 0.020401 | 0.0038024 | 0.0085363 | -0.0071158 | -0.0082522 | -0.0052337 | -0.058212 | -0.0097775 | -0.0056118 | -0.0013352 | 0.00047633 | -0.009094 | 0.14191 | 0.21515 | 0.21973 | 0.16937 | 0.24261 | 0.07782 | -0.073242 | 0.1831 | 0.28839 | 0.15106 | 0.16479 | 0.12817 | -0.009155 | -0.073242 | 122.6807 | 122.5296 | 0.10986 | 122.818 | 122.7722 | 0.24261 | 0.009156 | 122.5937 | 122.5296 | 0.032044 | 122.7859 | 122.7539 | 0.2243 | -0.004577 | 122.8455 | 122.7448 | 122.8226 | -0.20599 | 122.7676 | 122.731 | 122.8912 | -0.20599
1624.4688 | 122.9416 | -122.6028 | 0.16479 | -0.2066 | 0.020615 | 0.0038024 | 0.0081091 | -0.0043386 | -0.0037662 | -0.0058747 | -0.21843 | -0.0089229 | -0.0036892 | -0.00069421 | 0.0013309 | -0.011657 | 0.17395 | 0.16937 | 0.19226 | 0.16022 | 0.24719 | 0.091553 | -0.068665 | 0.11444 | 0.21515 | 0.050354 | 0.19684 | 0.1831 | -0.041199 | -0.09613 | 122.6944 | 122.5342 | 0.082397 | 122.7722 | 122.7631 | 0.22888 | 0.009155 | 122.5616 | 122.5067 | 0.032043 | 122.7173 | 122.6532 | 0.14648 | 0.01831 | 122.85 | 122.7768 | 122.7951 | -0.23346 | 122.7997 | 122.7859 | 122.818 | -0.26092
1626.1719 | 122.8867 | -122.644 | 0.16479 | -0.084534 | 0.022751 | 0.0033752 | 0.0040503 | -0.005834 | 0.004565 | -0.0018159 | -0.12688 | -0.0080685 | -0.0028348 | -0.00069421 | 0.0066715 | -0.014007 | 0.13275 | 0.10986 | 0.10986 | 0.064087 | 0.23346 | 0.009155 | -0.12817 | 0.09613 | 0.10986 | -0.041199 | 0.15564 | 0.11444 | -0.091553 | -0.14648 | 122.6532 | 122.5159 | 0.068664 | 122.7539 | 122.7081 | 0.19226 | -0.032044 | 122.5525 | 122.4976 | -0.009155 | 122.7402 | 122.6028 | 0.10529 | -0.050354 | 122.8775 | 122.7768 | 122.7539 | -0.29297 | 122.7997 | 122.7585 | 122.7539 | -0.31128
1627.8906 | 122.9599 | -122.6028 | 0.15564 | -0.17609 | 0.025314 | 0.0048706 | 0.0049047 | -0.0064748 | 0.0015744 | -0.0050201 | -0.16502 | -0.0093503 | -0.0017666 | 0.0016556 | 0.0053897 | -0.01123 | 0.10071 | 0.11902 | 0.11902 | 0.082397 | 0.26093 | 0.041199 | -0.13275 | 0.07782 | 0.12817 | -0.009155 | 0.15106 | 0.1236 | -0.091553 | -0.13275 | 122.644 | 122.4701 | 0.10529 | 122.7219 | 122.6852 | 0.21515 | -0.054932 | 122.5113 | 122.4701 | -0.004578 | 122.6807 | 122.5937 | 0.1236 | -0.032044 | 122.8638 | 122.7036 | 122.7219 | -0.28839 | 122.7539 | 122.7264 | 122.731 | -0.28839
1629.5625 | 122.85 | -122.6715 | 0.16022 | 0.17487 | 0.01976 | 0.0052978 | 0.0010595 | -0.0060476 | -0.0022708 | -0.0035249 | 0.17067 | -0.0097775 | -0.006039 | -0.0015488 | 0.0041079 | -0.010803 | 0.064087 | 0.12817 | 0.14648 | 0.059509 | 0.14191 | -0.009155 | -0.13733 | 0.10986 | 0.19226 | 0.045776 | 0.091553 | 0.050354 | -0.10071 | -0.12817 | 122.6624 | 122.5342 | -0.01831 | 122.7997 | 122.731 | 0.19684 | -0.09613 | 122.5708 | 122.5433 | -0.068664 | 122.7814 | 122.7173 | 0.17395 | -0.10986 | 122.8134 | 122.7356 | 122.818 | -0.29755 | 122.7631 | 122.7219 | 122.8638 | -0.28839
1631.25 | 122.8455 | -122.6486 | 0.16937 | 0.16724 | 0.020401 | 0.0035888 | 0.0021277 | -0.0043386 | -0.0041934 | -0.0052337 | 0.1783 | -0.0084957 | -0.0051846 | 0.00058739 | 0.0038943 | -0.010803 | 0.09613 | 0.11902 | 0.15564 | 0.07782 | 0.14191 | -0.009155 | -0.13733 | 0.10986 | 0.20142 | 0.041199 | 0.09613 | 0.059509 | -0.073242 | -0.12817 | 122.6395 | 122.5113 | -0.027466 | 122.7676 | 122.7264 | 0.21515 | -0.073243 | 122.5754 | 122.5204 | -0.073243 | 122.7585 | 122.6898 | 0.16937 | -0.10986 | 122.7905 | 122.7448 | 122.8043 | -0.3067 | 122.7448 | 122.7081 | 122.85 | -0.29755
1632.9844 | 122.8683 | -122.6669 | 0.18768 | -0.061646 | 0.023819 | 0.0048706 | 0.0051183 | -0.0051932 | 0.0028562 | -0.0035249 | -0.08873 | -0.0067867 | -0.0088162 | -0.0047532 | 0.0066715 | -0.011444 | 0.13275 | 0.082397 | 0.10071 | 0.086975 | 0.24261 | 0.013733 | -0.12817 | 0.054932 | 0.10529 | -0.059509 | 0.16022 | 0.12817 | -0.091553 | -0.14191 | 122.6807 | 122.5388 | 0.054932 | 122.7493 | 122.7539 | 0.21515 | -0.054932 | 122.5754 | 122.525 | -0.027466 | 122.7219 | 122.6074 | 0.082398 | -0.059509 | 122.9095 | 122.7997 | 122.7676 | -0.31586 | 122.8271 | 122.7951 | 122.7722 | -0.32959
1634.6719 | 122.9233 | -122.6028 | 0.14648 | -0.22949 | 0.021042 | 0.0052978 | 0.0091773 | -0.0034842 | -0.0048344 | -0.0054475 | -0.20317 | -0.0072141 | -0.0013394 | -0.00026701 | 0.00047633 | -0.0095212 | 0.15106 | 0.17853 | 0.19684 | 0.15564 | 0.27924 | 0.068665 | -0.050354 | 0.10529 | 0.20599 | 0.050354 | 0.22888 | 0.19684 | -0.013733 | -0.07782 | 122.6715 | 122.5525 | 0.13275 | 122.7814 | 122.7585 | 0.20599 | 0.004578 | 122.5891 | 122.525 | 0.082398 | 122.7081 | 122.6532 | 0.12817 | 0.050354 | 122.8821 | 122.7539 | 122.7997 | -0.19684 | 122.8317 | 122.7997 | 122.8088 | -0.2243
1636.3594 | 122.8821 | -122.644 | 0.16022 | 0.037537 | 0.020828 | 0.0052978 | 0.0036231 | -0.0043386 | -0.003339 | -0.0058747 | 0.086746 | -0.011487 | -0.0047574 | -0.0030442 | 0.0021853 | -0.0097348 | 0.082397 | 0.10986 | 0.13733 | 0.086975 | 0.22888 | 0.032043 | -0.086975 | 0.09613 | 0.19226 | 0.036621 | 0.17395 | 0.1236 | -0.032043 | -0.11444 | 122.6761 | 122.5571 | 0.068665 | 122.7539 | 122.731 | 0.17395 | -0.07782 | 122.612 | 122.5296 | 0.013733 | 122.7402 | 122.6807 | 0.15106 | -0.036621 | 122.8729 | 122.7264 | 122.7814 | -0.24719 | 122.818 | 122.7676 | 122.8363 | -0.27466
1638.0625 | 122.8638 | -122.6486 | 0.16937 | 0.045166 | 0.019547 | 0.0040162 | 0.0064001 | -0.0094656 | -0.0031254 | -0.0060883 | 0.063858 | -0.0091367 | -0.0026212 | -0.0028306 | 0.0017581 | -0.011871 | 0.091553 | 0.11902 | 0.14191 | 0.091553 | 0.21515 | 0.045776 | -0.10071 | 0.10529 | 0.18768 | 0.041199 | 0.15564 | 0.12817 | -0.054932 | -0.11444 | 122.6944 | 122.5479 | 0.045776 | 122.7676 | 122.7402 | 0.19226 | -0.07782 | 122.5937 | 122.5342 | -0.013733 | 122.7539 | 122.6898 | 0.15564 | -0.041199 | 122.8638 | 122.7402 | 122.7905 | -0.27008 | 122.8043 | 122.7768 | 122.8363 | -0.28381
1639.75 | 122.937 | -122.6166 | 0.15106 | -0.19897 | 0.02211 | 0.0055114 | 0.0068273 | -0.0039114 | -0.00034818 | -0.0063019 | -0.24132 | -0.0070003 | -0.0058254 | -0.00069421 | 0.0026125 | -0.012512 | 0.13733 | 0.12817 | 0.12817 | 0.11444 | 0.30212 | 0.073242 | -0.073242 | 0.086975 | 0.15106 | -0.004578 | 0.24261 | 0.21057 | -0.045776 | -0.10071 | 122.6898 | 122.5433 | 0.15106 | 122.7448 | 122.731 | 0.18768 | -0.013733 | 122.5708 | 122.5159 | 0.091553 | 122.7036 | 122.612 | 0.09613 | 0.059509 | 122.9187 | 122.7539 | 122.7448 | -0.2243 | 122.8592 | 122.8271 | 122.7676 | -0.25177
1641.4375 | 122.9645 | -122.6028 | 0.15106 | -0.10742 | 0.021469 | 0.006366 | 0.0053321 | -0.0045522 | -0.004407 | -0.0063019 | -0.11925 | -0.010205 | -0.0045438 | -0.0026168 | 0.0021853 | -0.010376 | 0.20599 | 0.26093 | 0.24719 | 0.1831 | 0.25177 | 0.10986 | -0.041199 | 0.21057 | 0.32959 | 0.14191 | 0.16479 | 0.14191 | 0.013733 | -0.073242 | 122.7127 | 122.5616 | 0.10071 | 122.8638 | 122.7859 | 0.2243 | 0.054932 | 122.6166 | 122.5296 | 0.013733 | 122.8134 | 122.7448 | 0.21515 | -0.009155 | 122.8546 | 122.8088 | 122.85 | -0.19226 | 122.7676 | 122.7448 | 122.9324 | -0.2243
1643.1094 | 122.9599 | -122.6257 | 0.16022 | -0.22949 | 0.024674 | 0.0031616 | 0.0064001 | -0.007543 | -0.00077538 | -0.0073701 | -0.27946 | -0.0082821 | -0.0053982 | 0.00080099 | 0.0011173 | -0.011871 | 0.14648 | 0.10529 | 0.1236 | 0.11444 | 0.32044 | 0.068665 | -0.086975 | 0.091553 | 0.14648 | -0.009155 | 0.2243 | 0.19684 | -0.041199 | -0.086975 | 122.6944 | 122.5388 | 0.16022 | 122.731 | 122.7402 | 0.20142 | -0.013733 | 122.5845 | 122.5388 | 0.064087 | 122.7173 | 122.6166 | 0.07782 | 0.036621 | 122.9462 | 122.7722 | 122.7493 | -0.24719 | 122.85 | 122.8226 | 122.7722 | -0.24719
1644.7812 | 122.8912 | -122.644 | 0.16479 | 0.022278 | 0.017624 | 0.008075 | 0.0019141 | -0.0056204 | -0.0037662 | -0.0084381 | 0.071487 | -0.011059 | -0.0056118 | -0.0038986 | 0.0021853 | -0.0099484 | 0.10529 | 0.13733 | 0.15106 | 0.11444 | 0.22888 | 0.041199 | -0.073242 | 0.10986 | 0.19226 | 0.054932 | 0.16479 | 0.15106 | -0.054932 | -0.11444 | 122.6852 | 122.5708 | 0.064087 | 122.7814 | 122.7585 | 0.18768 | -0.059509 | 122.5891 | 122.5296 | 0 | 122.7539 | 122.699 | 0.16937 | -0.013733 | 122.8729 | 122.7493 | 122.7951 | -0.23804 | 122.8088 | 122.7951 | 122.8363 | -0.27924
1646.4688 | 122.9599 | -122.6074 | 0.16022 | -0.22186 | 0.021256 | 0.0055114 | 0.0066137 | -0.0069022 | -0.0012028 | -0.0035249 | -0.27184 | -0.0074277 | -0.0041164 | -0.0013352 | 0.0049625 | -0.011444 | 0.14648 | 0.12817 | 0.11902 | 0.10986 | 0.33417 | 0.064087 | -0.068665 | 0.086975 | 0.14648 | -0.013733 | 0.24719 | 0.20599 | -0.054932 | -0.11444 | 122.6715 | 122.5388 | 0.17395 | 122.7356 | 122.7173 | 0.17853 | -0.013733 | 122.5525 | 122.493 | 0.086975 | 122.6944 | 122.5937 | 0.10071 | 0.045777 | 122.9416 | 122.7539 | 122.7264 | -0.22888 | 122.8546 | 122.8134 | 122.7539 | -0.27466
1648.1562 | 122.8226 | -122.6578 | 0.1831 | 0.11383 | 0.019333 | 0.0038024 | 0.0031957 | -0.0071158 | -0.0031254 | -0.0067291 | 0.14778 | -0.0095639 | -0.003262 | -0.0013352 | 0.0030399 | -0.010589 | 0.10529 | 0.14648 | 0.15564 | 0.086975 | 0.17853 | 0.022888 | -0.11444 | 0.14648 | 0.18768 | 0.045776 | 0.12817 | 0.068665 | -0.050354 | -0.11902 | 122.6807 | 122.5433 | -0.004577 | 122.8043 | 122.7448 | 0.20142 | -0.077819 | 122.6074 | 122.5388 | -0.054931 | 122.8043 | 122.7036 | 0.16479 | -0.11444 | 122.8363 | 122.7631 | 122.8134 | -0.29755 | 122.7859 | 122.7264 | 122.8455 | -0.30212
1649.8438 | 122.8683 | -122.644 | 0.18768 | 0.060425 | 0.02211 | 0.0010254 | 0.0027685 | -0.0073294 | 0.003497 | -0.0037385 | 0.048599 | -0.0070003 | -0.0086026 | -0.00048061 | 0.0051761 | -0.010803 | 0.050354 | -0.004578 | 0.004578 | 0.009155 | 0.22888 | -0.018311 | -0.15564 | 0.022888 | 0.013733 | -0.11444 | 0.14191 | 0.10986 | -0.10986 | -0.17853 | 122.6257 | 122.4884 | 0.041199 | 122.6395 | 122.6532 | 0.16479 | -0.13733 | 122.5342 | 122.4655 | -0.045776 | 122.6669 | 122.5296 | 0.064087 | -0.07782 | 122.8729 | 122.6944 | 122.6486 | -0.34332 | 122.7859 | 122.7539 | 122.6578 | -0.36621
1651.5312 | 122.9828 | -122.612 | 0.12817 | -0.16083 | 0.018692 | 0.0042298 | 0.0049047 | -0.0083974 | -0.0052616 | -0.0069427 | -0.10399 | -0.012982 | -0.003262 | -0.0030442 | 0.00026273 | -0.0097348 | 0.19226 | 0.25635 | 0.23346 | 0.16937 | 0.27008 | 0.09613 | -0.036621 | 0.21973 | 0.32959 | 0.16022 | 0.17853 | 0.13275 | 0.009155 | -0.050354 | 122.7081 | 122.5754 | 0.14191 | 122.8683 | 122.7814 | 0.20599 | 0.064087 | 122.6212 | 122.5616 | 0.050354 | 122.8317 | 122.7722 | 0.21057 | 0.004577 | 122.8821 | 122.8043 | 122.8455 | -0.1648 | 122.7905 | 122.7448 | 122.9416 | -0.17853
1653.2188 | 122.9691 | -122.6074 | 0.14191 | -0.11505 | 0.025101 | 0.002948 | 0.0068273 | -0.0047658 | 0.0056332 | -0.0028839 | -0.18028 | -0.0057187 | -0.0041164 | -5.3406e-05 | 0.0045351 | -0.012085 | 0.15106 | 0.10986 | 0.11444 | 0.11902 | 0.25635 | 0.041199 | -0.11444 | 0.086975 | 0.15106 | -0.009155 | 0.16937 | 0.13275 | -0.064087 | -0.12817 | 122.6486 | 122.493 | 0.11444 | 122.7173 | 122.7264 | 0.23346 | 0.009155 | 122.5433 | 122.4792 | 0.027466 | 122.6944 | 122.5983 | 0.11902 | -0.009156 | 122.8638 | 122.7585 | 122.7219 | -0.25635 | 122.7768 | 122.7402 | 122.7585 | -0.27008
1654.9688 | 122.9599 | -122.6212 | 0.15106 | 0.0070193 | 0.021042 | 0.0031616 | 0.0038367 | -0.0030568 | -0.0065434 | -0.0077973 | 0.025711 | -0.011487 | -0.0053982 | -0.0011216 | 0.00026273 | -0.0097348 | 0.09613 | 0.14648 | 0.16022 | 0.10986 | 0.25177 | 0.068665 | -0.09613 | 0.15106 | 0.25635 | 0.09613 | 0.15106 | 0.16022 | -0.018311 | -0.07782 | 122.6898 | 122.525 | 0.10071 | 122.7676 | 122.731 | 0.20599 | -0.054932 | 122.6028 | 122.5433 | 0 | 122.7722 | 122.7173 | 0.17395 | 0.009155 | 122.8729 | 122.7173 | 122.7814 | -0.24719 | 122.7722 | 122.7814 | 122.8775 | -0.22888
1656.6562 | 122.8638 | -122.6761 | 0.18768 | 0.022278 | 0.024674 | 0.0052978 | 0.0025549 | -0.0071158 | 0.0039242 | -0.0039521 | 0.025711 | -0.0067867 | -0.007748 | -0.001976 | 0.0085941 | -0.011017 | 0.045776 | -0.018311 | 0 | 0.013733 | 0.2243 | -0.013733 | -0.15564 | 0.022888 | 0.009155 | -0.11444 | 0.15106 | 0.13733 | -0.11902 | -0.16937 | 122.6624 | 122.5204 | 0.036621 | 122.6578 | 122.6898 | 0.16937 | -0.14191 | 122.5571 | 122.5067 | -0.036621 | 122.699 | 122.5616 | 0.054932 | -0.050354 | 122.9004 | 122.7219 | 122.6761 | -0.34332 | 122.8271 | 122.8134 | 122.6852 | -0.35706
1658.3594 | 122.8638 | -122.6395 | 0.17853 | 0.083313 | 0.019119 | 0.0050842 | 0.0046911 | -0.0056204 | -0.0048344 | -0.0060883 | 0.11726 | -0.012341 | -0.0039028 | -0.0021896 | 0.0036807 | -0.0082394 | 0.10529 | 0.14191 | 0.15106 | 0.09613 | 0.20599 | 0.050354 | -0.09613 | 0.1236 | 0.2243 | 0.064087 | 0.15564 | 0.11444 | -0.036621 | -0.09613 | 122.6898 | 122.5433 | 0.027466 | 122.7814 | 122.7356 | 0.19226 | -0.073242 | 122.6028 | 122.5433 | -0.022888 | 122.7631 | 122.7036 | 0.16022 | -0.064087 | 122.8455 | 122.7448 | 122.7905 | -0.27466 | 122.7951 | 122.7539 | 122.8638 | -0.27466
1660.0469 | 122.8912 | -122.6532 | 0.16479 | 0.14435 | 0.023819 | 0.004657 | 0.0017005 | -0.0064748 | 0.0043514 | -0.0037385 | 0.063858 | -0.0072141 | -0.0064664 | 0.0010148 | 0.0053897 | -0.011871 | 0.041199 | 0.004578 | 0.032043 | 0.004578 | 0.2243 | -0.009155 | -0.15106 | 0.054932 | 0.045776 | -0.073242 | 0.15564 | 0.1236 | -0.091553 | -0.16022 | 122.644 | 122.5021 | 0.059509 | 122.6578 | 122.6578 | 0.15564 | -0.1236 | 122.5616 | 122.493 | -0.009155 | 122.7081 | 122.58 | 0.086975 | -0.041199 | 122.8775 | 122.6944 | 122.6852 | -0.31586 | 122.8088 | 122.7768 | 122.699 | -0.32501
1661.7344 | 122.9599 | -122.6303 | 0.16022 | -0.092163 | 0.021256 | 0.0010254 | 0.0051183 | -0.0079702 | 0.0022152 | -0.0028839 | -0.18791 | -0.0065731 | -0.006039 | 0.00037379 | 0.0075259 | -0.012726 | 0.14648 | 0.11902 | 0.11902 | 0.11902 | 0.25635 | 0.059509 | -0.1236 | 0.10071 | 0.14191 | -0.004578 | 0.16937 | 0.14191 | -0.07782 | -0.13275 | 122.6898 | 122.5067 | 0.096131 | 122.7493 | 122.7493 | 0.24261 | -0.013733 | 122.5525 | 122.4976 | 0.009156 | 122.731 | 122.6257 | 0.12817 | -0.01831 | 122.8867 | 122.7768 | 122.7493 | -0.28381 | 122.7997 | 122.7722 | 122.7722 | -0.29297
1663.4375 | 122.9324 | -122.6395 | 0.15106 | -0.18372 | 0.021042 | 0.0065796 | 0.0081091 | -0.0077566 | -0.0039798 | -0.0063019 | -0.096359 | -0.010846 | -0.003262 | -0.0026168 | 0.00068993 | -0.009094 | 0.20599 | 0.26093 | 0.26093 | 0.21515 | 0.2655 | 0.10986 | -0.027466 | 0.1831 | 0.30212 | 0.11444 | 0.19226 | 0.16022 | -0.004578 | -0.054932 | 122.7493 | 122.612 | 0.11444 | 122.9004 | 122.8546 | 0.24261 | 0.054932 | 122.6349 | 122.5845 | 0.041199 | 122.8226 | 122.7539 | 0.16937 | 0.009155 | 122.905 | 122.8455 | 122.9004 | -0.17853 | 122.8317 | 122.7997 | 122.9416 | -0.20599
1665.125 | 122.937 | -122.6166 | 0.16479 | 0.014648 | 0.019333 | 0.0023072 | 0.0070409 | -0.0071158 | -0.0035526 | -0.0054475 | 0.071487 | -0.0084957 | -0.0039028 | -0.0015488 | -0.00080527 | -0.0099484 | 0.09613 | 0.12817 | 0.16479 | 0.10071 | 0.24261 | 0.064087 | -0.073242 | 0.12817 | 0.2243 | 0.068665 | 0.16937 | 0.12817 | -0.013733 | -0.086975 | 122.6807 | 122.5433 | 0.07782 | 122.7448 | 122.7173 | 0.17395 | -0.068665 | 122.6028 | 122.5296 | 0.004578 | 122.7448 | 122.6852 | 0.15564 | -0.036621 | 122.8592 | 122.7127 | 122.7814 | -0.23804 | 122.7859 | 122.7448 | 122.8409 | -0.25177
1666.8281 | 122.8409 | -122.6578 | 0.18768 | 0.12146 | 0.018265 | 0.0040162 | 0.0010595 | -0.0047658 | -0.003339 | -0.0073701 | 0.11726 | -0.0084957 | -0.0068936 | -0.0030442 | 0.0041079 | -0.012298 | 0.11902 | 0.13733 | 0.14648 | 0.082397 | 0.18768 | 0.032043 | -0.11902 | 0.13275 | 0.1831 | 0.045776 | 0.12817 | 0.10529 | -0.064087 | -0.1236 | 122.6898 | 122.5388 | 0 | 122.7951 | 122.7402 | 0.20142 | -0.068664 | 122.5937 | 122.5342 | -0.059509 | 122.7905 | 122.7036 | 0.16937 | -0.082397 | 122.8455 | 122.7768 | 122.8043 | -0.3067 | 122.7859 | 122.7631 | 122.8409 | -0.31128
1668.5156 | 122.8683 | -122.6624 | 0.17853 | 0.052795 | 0.022965 | 0.0055114 | 0.0025549 | -0.0073294 | 0.003497 | -0.0041657 | -0.042954 | -0.0059323 | -0.0062528 | 0.0016556 | 0.0081667 | -0.014221 | 0.064087 | -0.018311 | 0.013733 | 0.045776 | 0.2243 | -0.018311 | -0.15564 | -0.004578 | 0.018311 | -0.13733 | 0.16937 | 0.14648 | -0.10529 | -0.14191 | 122.644 | 122.5067 | 0.045776 | 122.644 | 122.7081 | 0.20142 | -0.11444 | 122.5571 | 122.5204 | -0.009155 | 122.6578 | 122.525 | 0.004578 | -0.032044 | 122.8867 | 122.7264 | 122.6761 | -0.33417 | 122.8317 | 122.8088 | 122.6807 | -0.32044
1670.2031 | 122.85 | -122.6669 | 0.19226 | 0.060425 | 0.024033 | 0.0033752 | 0.0029821 | -0.0051932 | -0.00013458 | -0.0022431 | -0.012436 | -0.0078549 | -0.0062528 | -0.00026701 | 0.0064577 | -0.012298 | 0.059509 | 0.004578 | 0.032043 | 0.027466 | 0.23346 | 0.018311 | -0.14191 | -0.004578 | 0.018311 | -0.10986 | 0.14648 | 0.14191 | -0.082397 | -0.15564 | 122.6852 | 122.525 | 0.041198 | 122.6715 | 122.6944 | 0.16937 | -0.13275 | 122.5845 | 122.5113 | -0.045777 | 122.6624 | 122.5571 | 0.045777 | -0.050354 | 122.9004 | 122.7264 | 122.699 | -0.33417 | 122.8134 | 122.8088 | 122.6852 | -0.3479
1671.9531 | 122.8546 | -122.6669 | 0.16937 | 0.1825 | 0.01976 | 0.0023072 | 0.0042639 | -0.0069022 | -0.00163 | -0.0024567 | 0.15541 | -0.0087093 | -0.0036892 | -0.00048061 | 0.0036807 | -0.0099484 | 0.10986 | 0.13733 | 0.16937 | 0.091553 | 0.17395 | 0.018311 | -0.13275 | 0.15564 | 0.20599 | 0.073242 | 0.11444 | 0.082397 | -0.068665 | -0.11444 | 122.6852 | 122.5342 | 0.004577 | 122.8043 | 122.7585 | 0.2243 | -0.05951 | 122.5983 | 122.5525 | -0.054932 | 122.8226 | 122.7402 | 0.18768 | -0.086976 | 122.8409 | 122.7768 | 122.8363 | -0.30212 | 122.7814 | 122.7493 | 122.8729 | -0.28381
1673.6406 | 122.8775 | -122.6578 | 0.1831 | -0.046387 | 0.022324 | 0.0033752 | 0.0081091 | -0.008611 | 0.003497 | -0.0035249 | -0.065842 | -0.0074277 | -0.0036892 | -0.00026701 | 0.0066715 | -0.012085 | 0.13275 | 0.091553 | 0.091553 | 0.086975 | 0.24719 | 0.022888 | -0.11902 | 0.059509 | 0.09613 | -0.050354 | 0.15564 | 0.1236 | -0.073242 | -0.14191 | 122.6807 | 122.5388 | 0.064087 | 122.7493 | 122.7448 | 0.20599 | -0.050354 | 122.5845 | 122.5159 | -0.027465 | 122.7173 | 122.6074 | 0.091553 | -0.059509 | 122.905 | 122.7905 | 122.7493 | -0.30212 | 122.8134 | 122.7814 | 122.7539 | -0.32501
1675.3125 | 122.9553 | -122.6578 | 0.13275 | -0.2066 | 0.021469 | 0.0055114 | 0.0061865 | -0.0034842 | -0.0054752 | -0.0058747 | -0.08873 | -0.010205 | -0.0058254 | -0.0028306 | 0.0034671 | -0.0099484 | 0.20142 | 0.26093 | 0.26093 | 0.20142 | 0.28381 | 0.10529 | -0.022888 | 0.19684 | 0.30212 | 0.13733 | 0.1831 | 0.16479 | -0.009155 | -0.036621 | 122.7631 | 122.6349 | 0.15106 | 122.9187 | 122.8592 | 0.2243 | 0.068665 | 122.6486 | 122.6212 | 0.050354 | 122.8546 | 122.7951 | 0.17395 | 0.032044 | 122.9416 | 122.8592 | 122.9187 | -0.15564 | 122.8409 | 122.8226 | 122.9599 | -0.16937
1677 | 122.8867 | -122.6486 | 0.18768 | 0.083313 | 0.023392 | 0.0035888 | 0.0040503 | -0.004125 | 0.001788 | -0.0035249 | 0.063858 | -0.0078549 | -0.0075344 | 0.00037379 | 0.0062441 | -0.012726 | 0.041199 | -0.013733 | 0.009155 | 0.009155 | 0.23346 | 0.004578 | -0.16479 | 0.018311 | 0.022888 | -0.10529 | 0.17395 | 0.1236 | -0.12817 | -0.17395 | 122.6532 | 122.4838 | 0.045776 | 122.6349 | 122.6578 | 0.17395 | -0.14648 | 122.5204 | 122.4747 | -0.013733 | 122.6669 | 122.5433 | 0.068664 | -0.064087 | 122.8821 | 122.6898 | 122.6578 | -0.35248 | 122.8226 | 122.7722 | 122.6715 | -0.36163
1678.6875 | 122.9187 | -122.6624 | 0.17853 | -0.10742 | 0.022537 | 0.00081179 | 0.0036231 | -0.0051932 | 0.0028562 | -0.0058747 | -0.11162 | -0.0072141 | -0.0045438 | -0.00090781 | 0.0047489 | -0.012085 | 0.14648 | 0.10071 | 0.10529 | 0.09613 | 0.23804 | 0.041199 | -0.10986 | 0.073242 | 0.13733 | -0.027466 | 0.16479 | 0.15564 | -0.059509 | -0.13733 | 122.7036 | 122.5525 | 0.059509 | 122.7631 | 122.7585 | 0.20599 | -0.032044 | 122.6028 | 122.525 | -0.013733 | 122.7356 | 122.6349 | 0.10986 | -0.022888 | 122.9004 | 122.8088 | 122.7676 | -0.28839 | 122.8271 | 122.818 | 122.7997 | -0.31586
1680.375 | 122.9416 | -122.6395 | 0.15106 | -0.2066 | 0.021683 | 0.0050842 | 0.010032 | -0.007543 | -0.007825 | -0.0052337 | -0.12688 | -0.010205 | -0.0043302 | -0.00069421 | -0.00016447 | -0.010162 | 0.20599 | 0.25635 | 0.26093 | 0.21515 | 0.27924 | 0.11444 | -0.027466 | 0.18768 | 0.31586 | 0.15106 | 0.18768 | 0.16937 | 0.009155 | -0.045776 | 122.7539 | 122.612 | 0.12817 | 122.8958 | 122.8546 | 0.24261 | 0.054932 | 122.6486 | 122.5937 | 0.036621 | 122.8271 | 122.7905 | 0.19684 | 0.018311 | 122.9187 | 122.8455 | 122.9004 | -0.17853 | 122.8271 | 122.8088 | 122.9553 | -0.19684
1682.0781 | 122.9187 | -122.6624 | 0.16479 | 0.037537 | 0.018051 | 0.0052978 | 0.0044775 | -0.0066884 | -0.004407 | -0.0058747 | 0.056228 | -0.011487 | -0.0051846 | -0.0015488 | 0.0013309 | -0.010376 | 0.10071 | 0.1236 | 0.15106 | 0.11902 | 0.25177 | 0.082397 | -0.091553 | 0.1236 | 0.20599 | 0.07782 | 0.16937 | 0.15564 | -0.018311 | -0.10071 | 122.7448 | 122.5708 | 0.086975 | 122.7859 | 122.7814 | 0.21057 | -0.064087 | 122.644 | 122.5616 | 0.004578 | 122.7859 | 122.7402 | 0.17853 | -0.009155 | 122.9141 | 122.7631 | 122.8134 | -0.25635 | 122.8317 | 122.818 | 122.8683 | -0.2655
1683.7969 | 122.8867 | -122.644 | 0.17395 | 0.14435 | 0.01976 | 0.001239 | 0.0029821 | -0.0064748 | 0.00050622 | -0.0035249 | 0.18593 | -0.0091367 | -0.0051846 | 0.001442 | 0.0053897 | -0.011871 | 0.14191 | 0.11444 | 0.14648 | 0.10071 | 0.17395 | 0.018311 | -0.10986 | 0.13733 | 0.1831 | 0.036621 | 0.10071 | 0.086975 | -0.054932 | -0.12817 | 122.6624 | 122.5342 | 0 | 122.7585 | 122.7448 | 0.21057 | -0.032043 | 122.5891 | 122.5159 | -0.073242 | 122.7814 | 122.6807 | 0.1648 | -0.086975 | 122.818 | 122.7859 | 122.7905 | -0.28381 | 122.7448 | 122.731 | 122.8271 | -0.30212
1685.4844 | 123.0057 | -122.6166 | 0.13275 | -0.19135 | 0.023178 | 0.0040162 | 0.0085363 | -0.007543 | -0.00034818 | -0.0050201 | -0.2108 | -0.0057187 | -0.0045438 | 0.0018692 | 0.0036807 | -0.01593 | 0.14191 | 0.091553 | 0.10986 | 0.11444 | 0.33875 | 0.10071 | -0.07782 | 0.10071 | 0.15106 | 0.009155 | 0.23804 | 0.19226 | -0.045776 | -0.10071 | 122.7173 | 122.5388 | 0.20599 | 122.7081 | 122.731 | 0.19226 | 0.009156 | 122.5708 | 122.5159 | 0.10529 | 122.7173 | 122.6257 | 0.10986 | 0.05951 | 122.9553 | 122.7585 | 122.7264 | -0.21057 | 122.8546 | 122.8088 | 122.7676 | -0.23346
1687.1562 | 122.8867 | -122.6624 | 0.18768 | 0.060425 | 0.022537 | 0.0052978 | 0.0036231 | -0.0066884 | 0.00093342 | -0.0024567 | 0.04097 | -0.0082821 | -0.0041164 | 0.0027236 | 0.0068851 | -0.012512 | 0.041199 | -0.013733 | 0.018311 | 0.032043 | 0.25177 | -0.004578 | -0.16022 | 0.027466 | 0.027466 | -0.07782 | 0.15564 | 0.14191 | -0.091553 | -0.14648 | 122.6578 | 122.5021 | 0.064087 | 122.6486 | 122.6944 | 0.19226 | -0.14648 | 122.5708 | 122.5159 | -0.032043 | 122.6898 | 122.5845 | 0.068664 | -0.045776 | 122.9141 | 122.7036 | 122.6807 | -0.3479 | 122.818 | 122.8043 | 122.6898 | -0.33417
1688.8594 | 122.9599 | -122.6212 | 0.14191 | -0.16846 | 0.019547 | 0.0038024 | 0.0053321 | -0.0066884 | -0.0082522 | -0.0037385 | -0.13451 | -0.011059 | -0.0045438 | -0.0015488 | 0.00047633 | -0.010162 | 0.20142 | 0.27924 | 0.27466 | 0.20142 | 0.2655 | 0.13275 | -0.041199 | 0.19684 | 0.32044 | 0.15564 | 0.21515 | 0.16937 | 0.018311 | -0.045776 | 122.7539 | 122.58 | 0.1236 | 122.9004 | 122.8226 | 0.24262 | 0.059509 | 122.6395 | 122.5754 | 0.073242 | 122.818 | 122.7768 | 0.20142 | 0.027466 | 122.8867 | 122.8226 | 122.8958 | -0.18311 | 122.8363 | 122.7905 | 122.9416 | -0.18768
1690.5625 | 122.9004 | -122.6624 | 0.18768 | 0.15961 | 0.023178 | 0.0040162 | 0.0021277 | -0.0056204 | 0.0020016 | -0.0052337 | 0.04097 | -0.0078549 | -0.0071072 | -0.0013352 | 0.0062441 | -0.010589 | 0.032043 | 0.036621 | 0.041199 | 0.027466 | 0.21057 | 0 | -0.15564 | 0.054932 | 0.059509 | -0.064087 | 0.16937 | 0.14191 | -0.10071 | -0.14191 | 122.6624 | 122.5067 | 0.022888 | 122.699 | 122.6898 | 0.18311 | -0.15564 | 122.5616 | 122.5204 | -0.01831 | 122.7173 | 122.5983 | 0.07782 | -0.045776 | 122.8729 | 122.6944 | 122.7036 | -0.34332 | 122.8317 | 122.8043 | 122.7219 | -0.32959
1692.25 | 122.9874 | -122.644 | 0.15564 | -0.18372 | 0.025528 | 0.002948 | 0.0087499 | -0.005834 | 0.0015744 | -0.0041657 | -0.16502 | -0.0095639 | -0.0026212 | 0.0012284 | 0.0051761 | -0.014007 | 0.14648 | 0.11902 | 0.11444 | 0.12817 | 0.28381 | 0.07782 | -0.086975 | 0.10071 | 0.17395 | -0.004578 | 0.19684 | 0.16479 | -0.036621 | -0.10071 | 122.7219 | 122.5571 | 0.12817 | 122.7631 | 122.7722 | 0.21515 | -0.009156 | 122.6074 | 122.5433 | 0.041198 | 122.7448 | 122.6395 | 0.09613 | 0.009155 | 122.9279 | 122.7905 | 122.7585 | -0.24261 | 122.8409 | 122.8088 | 122.818 | -0.25635
1693.9844 | 122.9279 | -122.6303 | 0.16479 | 0.15198 | 0.022324 | 0.0023072 | 0.00084592 | -0.0064748 | -0.0020572 | -0.0045929 | 0.15541 | -0.0080685 | -0.0075344 | -0.00069421 | 0.0062441 | -0.010162 | 0.054932 | 0.064087 | 0.073242 | 0.064087 | 0.19684 | 0.009155 | -0.14648 | 0.11902 | 0.16479 | 0.041199 | 0.11902 | 0.10071 | -0.059509 | -0.11444 | 122.6395 | 122.4838 | 0.032043 | 122.6944 | 122.6944 | 0.21057 | -0.10986 | 122.5708 | 122.5159 | -0.045776 | 122.7493 | 122.6715 | 0.15564 | -0.064087 | 122.8271 | 122.6852 | 122.7036 | -0.31128 | 122.7493 | 122.731 | 122.7951 | -0.27924
1695.6719 | 123.0194 | -122.644 | 0.14191 | -0.19135 | 0.024674 | 0.0020936 | 0.0059729 | -0.0054068 | -0.00034818 | -0.0052337 | -0.19554 | -0.0078549 | -0.0043302 | 0.0016556 | 0.0017581 | -0.011444 | 0.10986 | 0.12817 | 0.10986 | 0.11444 | 0.32959 | 0.073242 | -0.09613 | 0.082397 | 0.16937 | 0.018311 | 0.23346 | 0.20142 | -0.045776 | -0.10071 | 122.7173 | 122.5479 | 0.18768 | 122.7722 | 122.7585 | 0.21057 | -0.032044 | 122.5983 | 122.5433 | 0.091552 | 122.7264 | 122.6624 | 0.11902 | 0.059509 | 122.9736 | 122.7539 | 122.7539 | -0.23804 | 122.8775 | 122.8455 | 122.8134 | -0.24262
1697.3594 | 122.9919 | -122.6074 | 0.15106 | -0.13794 | 0.018692 | 0.0067932 | 0.0036231 | -0.0060476 | -0.0076114 | -0.0058747 | 0.010452 | -0.0117 | -0.006039 | -0.0021896 | -0.00016447 | -0.011017 | 0.18768 | 0.25177 | 0.27008 | 0.20142 | 0.27466 | 0.12817 | -0.054932 | 0.21973 | 0.32501 | 0.16479 | 0.1831 | 0.15564 | 0.027466 | -0.041199 | 122.7356 | 122.5525 | 0.1236 | 122.8592 | 122.8088 | 0.25635 | 0.036621 | 122.6349 | 122.5662 | 0.032043 | 122.8271 | 122.7722 | 0.20599 | 0.004578 | 122.8821 | 122.7951 | 122.8775 | -0.20599 | 122.7905 | 122.7631 | 122.9324 | -0.19226
1699.0312 | 122.8592 | -122.6624 | 0.19684 | 0.022278 | 0.021469 | 0.00059819 | 0.0044775 | -0.007543 | 0.0041378 | -0.0033111 | -0.027695 | -0.0078549 | -0.0056118 | 0.00016019 | 0.0073123 | -0.014007 | 0.086975 | 0.027466 | 0.045776 | 0.045776 | 0.26093 | -0.004578 | -0.13733 | 0.018311 | 0.027466 | -0.082397 | 0.17395 | 0.15106 | -0.09613 | -0.15106 | 122.6578 | 122.525 | 0.064087 | 122.6898 | 122.7081 | 0.18311 | -0.10986 | 122.5662 | 122.5113 | -0.022888 | 122.6807 | 122.58 | 0.068665 | -0.045776 | 122.9233 | 122.7493 | 122.7081 | -0.33417 | 122.8363 | 122.8134 | 122.6898 | -0.3479
1700.7344 | 122.8912 | -122.6395 | 0.16479 | 0.14435 | 0.021896 | 0.0038024 | 0.0055457 | -0.0062612 | -0.00098918 | -0.0048065 | 0.20119 | -0.0099911 | -0.0068936 | -0.0030442 | 0.0045351 | -0.010162 | 0.10071 | 0.12817 | 0.15106 | 0.09613 | 0.17853 | 0.036621 | -0.12817 | 0.12817 | 0.1831 | 0.032043 | 0.11902 | 0.086975 | -0.064087 | -0.10071 | 122.6761 | 122.5113 | 0.013733 | 122.7676 | 122.7356 | 0.2243 | -0.064087 | 122.5754 | 122.5388 | -0.045776 | 122.7676 | 122.6715 | 0.13275 | -0.07782 | 122.818 | 122.7402 | 122.7905 | -0.29297 | 122.7585 | 122.7264 | 122.8226 | -0.2655
1702.4219 | 122.9279 | -122.6486 | 0.16022 | 0.0070193 | 0.017624 | 0.007434 | 0.0059729 | -0.005834 | -0.0059024 | -0.0063019 | 0.056228 | -0.011487 | -0.0071072 | -0.0026168 | 4.9132e-05 | -0.0093076 | 0.09613 | 0.12817 | 0.17395 | 0.1236 | 0.24261 | 0.082397 | -0.082397 | 0.12817 | 0.20599 | 0.07782 | 0.17853 | 0.15106 | -0.022888 | -0.082397 | 122.731 | 122.5662 | 0.082398 | 122.7768 | 122.7722 | 0.20599 | -0.064087 | 122.6257 | 122.5662 | 0.018311 | 122.7768 | 122.7264 | 0.16022 | -0.009155 | 122.8912 | 122.7448 | 122.8226 | -0.24261 | 122.8271 | 122.7997 | 122.8546 | -0.24261
1704.1094 | 122.9919 | -122.6303 | 0.13733 | -0.13794 | 0.021256 | 0.0050842 | 0.0034093 | -0.0056204 | 0.0039242 | -0.0043793 | -0.18028 | -0.0067867 | -0.0051846 | 0.00016019 | 0.0060305 | -0.013366 | 0.15106 | 0.13275 | 0.11902 | 0.1236 | 0.29297 | 0.050354 | -0.10071 | 0.10986 | 0.14191 | -0.004578 | 0.19226 | 0.16479 | -0.036621 | -0.11902 | 122.6807 | 122.5296 | 0.15564 | 122.7631 | 122.7539 | 0.2243 | 0.013733 | 122.5937 | 122.5113 | 0.054932 | 122.7402 | 122.6257 | 0.11444 | 0.027466 | 122.9233 | 122.7814 | 122.7493 | -0.23804 | 122.8226 | 122.7951 | 122.7722 | -0.25635
1705.7969 | 122.9919 | -122.6349 | 0.14191 | -0.11505 | 0.019974 | 0.006366 | 0.0055457 | -0.0077566 | -0.0046206 | -0.0039521 | -0.08873 | -0.010418 | -0.0053982 | -0.0011216 | -0.0014463 | -0.011017 | 0.19226 | 0.25635 | 0.24719 | 0.19684 | 0.27008 | 0.10986 | -0.032043 | 0.22888 | 0.31586 | 0.16937 | 0.19684 | 0.16479 | 0.018311 | -0.027466 | 122.7448 | 122.6028 | 0.12817 | 122.8912 | 122.8317 | 0.22888 | 0.050354 | 122.6532 | 122.6074 | 0.054931 | 122.8638 | 122.8043 | 0.19684 | 0.022888 | 122.905 | 122.8271 | 122.8821 | -0.17395 | 122.8317 | 122.7997 | 122.9507 | -0.16937
1707.4844 | 122.8592 | -122.6852 | 0.20142 | 0.075684 | 0.025314 | 0.0016662 | 0.0044775 | -0.0064748 | 0.0043514 | -0.0033111 | 0.04097 | -0.0070003 | -0.0041164 | -0.00048061 | 0.0070987 | -0.01358 | 0.064087 | -0.013733 | 0.004578 | 0.036621 | 0.24719 | 0.009155 | -0.14648 | 0.013733 | 0.018311 | -0.11444 | 0.17853 | 0.15564 | -0.09613 | -0.13275 | 122.6944 | 122.5388 | 0.045776 | 122.6715 | 122.7219 | 0.18311 | -0.13733 | 122.5891 | 122.5525 | -0.022888 | 122.699 | 122.5708 | 0.01831 | -0.045776 | 122.9324 | 122.7493 | 122.6898 | -0.3479 | 122.8638 | 122.8409 | 122.7036 | -0.33417
1709.1562 | 122.8867 | -122.6624 | 0.17853 | 0.052795 | 0.021469 | 0.0059388 | 0.0040503 | -0.0071158 | -0.0071842 | -0.0060883 | 0.102 | -0.0093503 | -0.0045438 | -0.0028306 | 0.0021853 | -0.010162 | 0.12817 | 0.13733 | 0.15106 | 0.10071 | 0.23804 | 0.068665 | -0.086975 | 0.1236 | 0.1831 | 0.068665 | 0.1831 | 0.16022 | -0.027466 | -0.07782 | 122.731 | 122.5754 | 0.059509 | 122.7997 | 122.7631 | 0.18768 | -0.050354 | 122.6349 | 122.5845 | 0.004577 | 122.7859 | 122.731 | 0.14649 | -0.018311 | 122.9004 | 122.7905 | 122.8134 | -0.2655 | 122.8455 | 122.8226 | 122.8455 | -0.25635
1710.8438 | 122.8638 | -122.6715 | 0.17853 | 0.083313 | 0.024887 | 0.0057252 | 0.0046911 | -0.0077566 | 0.0039242 | -0.0043793 | -0.058212 | -0.0055051 | -0.0081754 | -0.00069421 | 0.0058169 | -0.012512 | 0.064087 | 0 | 0.036621 | 0.032043 | 0.23804 | 0.018311 | -0.14648 | 0.022888 | 0.022888 | -0.11902 | 0.17395 | 0.14191 | -0.082397 | -0.15564 | 122.6898 | 122.525 | 0.059509 | 122.6715 | 122.7036 | 0.17853 | -0.11444 | 122.5891 | 122.5159 | -0.004578 | 122.6944 | 122.5525 | 0.036621 | -0.036621 | 122.9095 | 122.7356 | 122.7081 | -0.32501 | 122.8455 | 122.8134 | 122.6944 | -0.33417
1712.5312 | 122.9874 | -122.6486 | 0.16479 | -0.23712 | 0.024674 | 0.0048706 | 0.0081091 | -0.0032706 | -0.00077538 | -0.0054475 | -0.23369 | -0.0087093 | -0.0021938 | -5.3406e-05 | 0.00090353 | -0.012726 | 0.13733 | 0.12817 | 0.11444 | 0.14191 | 0.34332 | 0.10071 | -0.050354 | 0.09613 | 0.14191 | 0 | 0.25177 | 0.21973 | -0.004578 | -0.082397 | 122.7493 | 122.5983 | 0.17853 | 122.7768 | 122.7905 | 0.19226 | -0.027466 | 122.644 | 122.5662 | 0.086975 | 122.7448 | 122.6486 | 0.082397 | 0.054932 | 122.9919 | 122.7859 | 122.7631 | -0.21515 | 122.9004 | 122.8683 | 122.7905 | -0.24719
1714.2188 | 122.8683 | -122.6303 | 0.17853 | 0.13672 | 0.020615 | 0.0038024 | 0.0066137 | -0.005834 | -0.0037662 | -0.0077973 | 0.14015 | -0.0097775 | -0.0030484 | -0.00069421 | 0.00068993 | -0.010162 | 0.10529 | 0.13275 | 0.16022 | 0.091553 | 0.20142 | 0.036621 | -0.10986 | 0.16022 | 0.21057 | 0.086975 | 0.17395 | 0.13275 | -0.041199 | -0.082397 | 122.6669 | 122.5204 | 0.022888 | 122.7631 | 122.7219 | 0.20142 | -0.073242 | 122.5891 | 122.5479 | -0.004578 | 122.7905 | 122.7173 | 0.16937 | -0.045777 | 122.8317 | 122.7356 | 122.7905 | -0.28839 | 122.8043 | 122.7631 | 122.8409 | -0.26092
1715.9062 | 122.9645 | -122.6578 | 0.15564 | -0.076904 | 0.023178 | 0.0027344 | 0.0023413 | -0.0049796 | 0.0026424 | -0.0050201 | -0.15739 | -0.0080685 | -0.0051846 | -0.00090781 | 0.0064577 | -0.013153 | 0.17395 | 0.13275 | 0.11902 | 0.10071 | 0.2655 | 0.041199 | -0.09613 | 0.12817 | 0.16937 | -0.013733 | 0.20142 | 0.14648 | -0.045776 | -0.11902 | 122.699 | 122.5616 | 0.10986 | 122.7905 | 122.7585 | 0.19684 | 0.01831 | 122.612 | 122.5388 | 0.045776 | 122.7859 | 122.644 | 0.10529 | -0.009156 | 122.9233 | 122.8317 | 122.7768 | -0.25177 | 122.8592 | 122.8043 | 122.8271 | -0.27466
1717.625 | 122.905 | -122.6624 | 0.15106 | 0.14435 | 0.021896 | 0.0040162 | 0.0040503 | -0.0079702 | 0.00029262 | -0.0037385 | 0.12489 | -0.0082821 | -0.0075344 | 0.00037379 | 0.0043215 | -0.01123 | 0.12817 | 0.10529 | 0.1236 | 0.10529 | 0.1831 | 0.036621 | -0.10986 | 0.14648 | 0.17395 | 0.041199 | 0.11444 | 0.09613 | -0.050354 | -0.10986 | 122.699 | 122.5525 | 0.032043 | 122.7676 | 122.7676 | 0.21515 | -0.022888 | 122.612 | 122.5525 | -0.036621 | 122.8088 | 122.7036 | 0.15106 | -0.054932 | 122.8455 | 122.7905 | 122.7859 | -0.26093 | 122.7768 | 122.7585 | 122.8363 | -0.26093
1719.3125 | 123.0057 | -122.6486 | 0.13733 | -0.12268 | 0.020401 | 0.0078614 | 0.0061865 | -0.0064748 | -0.0065434 | -0.0082245 | -0.08873 | -0.012127 | -0.0051846 | -0.001976 | 0.0021853 | -0.011871 | 0.20599 | 0.25635 | 0.24719 | 0.20599 | 0.2655 | 0.10071 | -0.054932 | 0.21973 | 0.34332 | 0.16479 | 0.19226 | 0.17853 | 0.013733 | -0.045776 | 122.7493 | 122.5937 | 0.12817 | 122.905 | 122.8546 | 0.26093 | 0.068665 | 122.6624 | 122.6028 | 0.054932 | 122.8683 | 122.8134 | 0.21057 | 0.041199 | 122.9141 | 122.8546 | 122.8958 | -0.19226 | 122.8409 | 122.8271 | 122.9919 | -0.18311
1721.0312 | 122.8729 | -122.6715 | 0.19684 | -0.046387 | 0.024033 | 0.0061524 | 0.0061865 | -0.0083974 | 0.0039242 | -0.0041657 | -0.035324 | -0.0076413 | -0.0045438 | 0.0010148 | 0.0070987 | -0.012512 | 0.13733 | 0.07782 | 0.064087 | 0.07782 | 0.25635 | 0.032043 | -0.11902 | 0.059509 | 0.082397 | -0.068665 | 0.17853 | 0.16022 | -0.073242 | -0.14648 | 122.7036 | 122.5525 | 0.05951 | 122.7493 | 122.7493 | 0.19684 | -0.059509 | 122.5983 | 122.525 | -0.01831 | 122.731 | 122.6028 | 0.077819 | -0.036621 | 122.9279 | 122.8088 | 122.7356 | -0.31586 | 122.85 | 122.8317 | 122.7539 | -0.34332
1722.7188 | 122.8775 | -122.6852 | 0.16479 | 0.045166 | 0.022965 | 0.0055114 | 0.0057593 | -0.008611 | -0.0052616 | -0.0082245 | 0.102 | -0.012555 | -0.004971 | -0.0015488 | -0.00059167 | -0.0097348 | 0.1236 | 0.12817 | 0.16022 | 0.091553 | 0.21973 | 0.059509 | -0.068665 | 0.14191 | 0.21515 | 0.064087 | 0.19684 | 0.15564 | -0.022888 | -0.068665 | 122.7448 | 122.6166 | 0.054932 | 122.8134 | 122.7768 | 0.16022 | -0.041199 | 122.6624 | 122.6166 | 0.032043 | 122.8271 | 122.7493 | 0.13275 | -0.009155 | 122.905 | 122.8088 | 122.8455 | -0.23346 | 122.8821 | 122.8409 | 122.9004 | -0.23346
1724.4531 | 122.9645 | -122.644 | 0.14648 | -0.21423 | 0.021683 | 0.004657 | 0.0087499 | -0.0056204 | -0.0012028 | -0.0065155 | -0.25658 | -0.0074277 | -0.003262 | -0.0013352 | 0.0028263 | -0.010162 | 0.15106 | 0.13275 | 0.13275 | 0.15564 | 0.35248 | 0.09613 | -0.068665 | 0.10071 | 0.16937 | 0.027466 | 0.25635 | 0.2243 | -0.009155 | -0.064087 | 122.7402 | 122.5754 | 0.20599 | 122.7768 | 122.7997 | 0.22431 | 0.004578 | 122.6349 | 122.58 | 0.10986 | 122.7448 | 122.6715 | 0.091553 | 0.07782 | 122.9965 | 122.7951 | 122.7768 | -0.21515 | 122.9004 | 122.8683 | 122.8134 | -0.21057
1726.1406 | 122.9782 | -122.6212 | 0.14191 | 0.014648 | 0.018692 | 0.0040162 | 0.0055457 | -0.0066884 | -0.0046206 | -0.0073701 | 0.018082 | -0.012982 | -0.0053982 | -0.0015488 | 0.00090353 | -0.01123 | 0.13733 | 0.16479 | 0.17853 | 0.14648 | 0.25635 | 0.068665 | -0.064087 | 0.17853 | 0.25177 | 0.10986 | 0.17395 | 0.1831 | -0.013733 | -0.050354 | 122.6898 | 122.5571 | 0.11444 | 122.7859 | 122.7676 | 0.21057 | -0.004578 | 122.6074 | 122.5708 | 0.032043 | 122.7997 | 122.731 | 0.16022 | 0.041198 | 122.8775 | 122.7585 | 122.7997 | -0.20599 | 122.7951 | 122.8043 | 122.8729 | -0.19226
1727.8438 | 122.9187 | -122.6624 | 0.16937 | 0.19775 | 0.023605 | 0.0027344 | 0.0038367 | -0.005834 | 0.00093342 | -0.0045929 | 0.12489 | -0.0097775 | -0.0068936 | 0.00058739 | 0.0051761 | -0.012939 | 0.11902 | 0.064087 | 0.086975 | 0.064087 | 0.19684 | 0.022888 | -0.12817 | 0.15106 | 0.16479 | 0.027466 | 0.14191 | 0.10986 | -0.050354 | -0.11444 | 122.6852 | 122.5342 | 0.027465 | 122.7264 | 122.7264 | 0.19226 | -0.050354 | 122.612 | 122.5479 | -0.027466 | 122.8134 | 122.6898 | 0.14191 | -0.05951 | 122.8592 | 122.7814 | 122.7493 | -0.29755 | 122.8043 | 122.7722 | 122.8271 | -0.28381
1729.5312 | 122.8638 | -122.7036 | 0.17853 | -0.054016 | 0.023819 | 0.0035888 | 0.0066137 | -0.0066884 | 0.0058468 | -0.0045929 | -0.050583 | -0.0063595 | -0.0030484 | 0.00058739 | 0.0058169 | -0.013366 | 0.12817 | 0.045776 | 0.07782 | 0.059509 | 0.25177 | 0.036621 | -0.12817 | 0.050354 | 0.045776 | -0.091553 | 0.16937 | 0.15564 | -0.068665 | -0.15106 | 122.7402 | 122.5754 | 0.073242 | 122.7493 | 122.7631 | 0.18768 | -0.050354 | 122.6349 | 122.5525 | -0.009155 | 122.7539 | 122.612 | 0.059509 | -0.022888 | 122.9553 | 122.8317 | 122.7814 | -0.3067 | 122.8729 | 122.8592 | 122.7493 | -0.32959
1731.2031 | 122.9691 | -122.6486 | 0.16479 | -0.21423 | 0.022751 | 0.0067932 | 0.0089635 | -0.0049796 | -0.00077538 | -0.0056611 | -0.24895 | -0.0074277 | -0.0036892 | 0.00016019 | 0.0011173 | -0.011657 | 0.14648 | 0.14191 | 0.12817 | 0.13275 | 0.3479 | 0.086975 | -0.064087 | 0.11444 | 0.16479 | 0.018311 | 0.27008 | 0.2243 | -0.013733 | -0.054932 | 122.7356 | 122.5845 | 0.1831 | 122.7905 | 122.7814 | 0.19684 | -0.018311 | 122.6349 | 122.5937 | 0.10529 | 122.7631 | 122.6669 | 0.073243 | 0.059509 | 122.9965 | 122.7951 | 122.7768 | -0.22888 | 122.9187 | 122.8729 | 122.8134 | -0.21973
1732.9375 | 123.0011 | -122.6166 | 0.13733 | -0.023499 | 0.020187 | 0.0065796 | 0.0040503 | -0.008611 | -0.0056888 | -0.0071563 | -0.027695 | -0.011059 | -0.0056118 | -0.0026168 | 0.0013309 | -0.0093076 | 0.15106 | 0.18768 | 0.18768 | 0.16937 | 0.27466 | 0.073242 | -0.050354 | 0.19684 | 0.29755 | 0.14191 | 0.18768 | 0.16022 | 0.009155 | -0.050354 | 122.6898 | 122.5662 | 0.13733 | 122.8043 | 122.7859 | 0.21973 | 0.013733 | 122.6257 | 122.5662 | 0.050354 | 122.8134 | 122.7585 | 0.19226 | 0.022888 | 122.8912 | 122.7676 | 122.8043 | -0.18768 | 122.8043 | 122.7768 | 122.9141 | -0.18768
1734.625 | 122.9324 | -122.6761 | 0.16479 | 0.19775 | 0.019974 | 0.0027344 | 0.0046911 | -0.007543 | 0.00093342 | -0.0026703 | 0.10963 | -0.0091367 | -0.0075344 | -0.0028306 | 0.0053897 | -0.012939 | 0.13275 | 0.091553 | 0.10529 | 0.073242 | 0.18768 | 0.032043 | -0.1236 | 0.13733 | 0.17853 | 0.045776 | 0.13275 | 0.10986 | -0.045776 | -0.11444 | 122.7081 | 122.5525 | 0.022888 | 122.7676 | 122.7493 | 0.19684 | -0.032044 | 122.6303 | 122.5616 | -0.032044 | 122.8134 | 122.7219 | 0.16022 | -0.054932 | 122.8638 | 122.8088 | 122.7814 | -0.28839 | 122.8088 | 122.7859 | 122.8546 | -0.27924
1736.3281 | 122.8867 | -122.6807 | 0.17853 | 0.068054 | 0.024033 | 0.0027344 | 0.0049047 | -0.0039114 | 0.001788 | -0.0039521 | 0.048599 | -0.0061459 | -0.00668 | 0.00037379 | 0.0090213 | -0.012085 | 0.054932 | 0.009155 | 0.022888 | 0.032043 | 0.24719 | 0.013733 | -0.15564 | 0.045776 | 0.027466 | -0.082397 | 0.17395 | 0.14191 | -0.09613 | -0.16022 | 122.6944 | 122.525 | 0.068664 | 122.6898 | 122.7127 | 0.18768 | -0.1236 | 122.5845 | 122.5204 | -0.004578 | 122.7264 | 122.5983 | 0.07782 | -0.036621 | 122.9279 | 122.7356 | 122.7036 | -0.33417 | 122.8546 | 122.8226 | 122.7081 | -0.33874
1738.0469 | 122.9874 | -122.6349 | 0.15106 | -0.1532 | 0.025742 | 0.0016662 | 0.0064001 | -0.0051932 | 0.00093342 | -0.0048065 | -0.18791 | -0.0074277 | -0.0056118 | -0.00069421 | 0.0056033 | -0.011657 | 0.16479 | 0.15564 | 0.11902 | 0.13275 | 0.28839 | 0.054932 | -0.082397 | 0.10071 | 0.16022 | 0.022888 | 0.19226 | 0.17395 | -0.041199 | -0.13275 | 122.6898 | 122.5525 | 0.13733 | 122.7905 | 122.7676 | 0.21515 | 0.013733 | 122.5937 | 122.5021 | 0.041199 | 122.7356 | 122.6578 | 0.15564 | 0.022888 | 122.9233 | 122.7997 | 122.7539 | -0.23346 | 122.8271 | 122.8088 | 122.7951 | -0.28381
1739.7188 | 122.8958 | -122.6761 | 0.17853 | 0.1825 | 0.021469 | 0.004657 | 0.0014867 | -0.0047658 | -0.00034818 | -0.0037385 | 0.18593 | -0.010418 | -0.00668 | -0.0013352 | 0.0036807 | -0.011657 | 0.12817 | 0.15564 | 0.15106 | 0.10986 | 0.17853 | 0.032043 | -0.1236 | 0.13733 | 0.19226 | 0.050354 | 0.10986 | 0.086975 | -0.059509 | -0.10986 | 122.7081 | 122.5525 | 0 | 122.8317 | 122.7859 | 0.23346 | -0.050354 | 122.6166 | 122.5662 | -0.068665 | 122.8134 | 122.7264 | 0.16022 | -0.091553 | 122.8546 | 122.8043 | 122.8271 | -0.30212 | 122.7859 | 122.7631 | 122.8683 | -0.28839
1741.4062 | 122.8867 | -122.6944 | 0.18768 | 0.068054 | 0.022965 | 0.0031616 | 0.0057593 | -0.0060476 | 0.00050622 | -0.0045929 | 0.04097 | -0.0067867 | -0.0053982 | -5.3406e-05 | 0.0049625 | -0.0095212 | 0.054932 | 0.009155 | 0.027466 | 0.041199 | 0.27924 | 0.022888 | -0.1236 | 0.027466 | 0.027466 | -0.082397 | 0.1831 | 0.16022 | -0.068665 | -0.13733 | 122.7173 | 122.5708 | 0.091553 | 122.7036 | 122.7356 | 0.16479 | -0.13275 | 122.6257 | 122.5571 | -0.004578 | 122.7219 | 122.612 | 0.054932 | -0.027466 | 122.9736 | 122.7493 | 122.7219 | -0.31128 | 122.8775 | 122.8546 | 122.7219 | -0.32501
1743.125 | 122.9233 | -122.6669 | 0.16479 | 0.17487 | 0.022751 | 0.0048706 | 0.0021277 | -0.0066884 | -0.003339 | -0.0050201 | 0.1783 | -0.0091367 | -0.0058254 | -0.00069421 | 0.0045351 | -0.0099484 | 0.086975 | 0.07782 | 0.10529 | 0.059509 | 0.20599 | 0.013733 | -0.11902 | 0.14191 | 0.17395 | 0.045776 | 0.12817 | 0.10071 | -0.045776 | -0.10529 | 122.6807 | 122.5479 | 0.041199 | 122.7448 | 122.7264 | 0.17853 | -0.07782 | 122.6212 | 122.5616 | -0.036621 | 122.8088 | 122.7127 | 0.15106 | -0.064087 | 122.8729 | 122.7539 | 122.7722 | -0.28381 | 122.7951 | 122.7676 | 122.8409 | -0.27008
1744.8125 | 123.0148 | -122.6349 | 0.14648 | -0.13031 | 0.022537 | 0.0035888 | 0.0081091 | -0.008611 | -0.00098918 | -0.0056611 | -0.18028 | -0.0072141 | -0.004971 | 0.00080099 | 0.0034671 | -0.012298 | 0.16022 | 0.1236 | 0.11444 | 0.13733 | 0.29297 | 0.064087 | -0.07782 | 0.11902 | 0.15564 | 0.004578 | 0.21515 | 0.18768 | -0.041199 | -0.10071 | 122.699 | 122.5571 | 0.14648 | 122.7585 | 122.7722 | 0.21515 | 0.013733 | 122.5937 | 122.5342 | 0.068665 | 122.7539 | 122.6395 | 0.10529 | 0.041199 | 122.9279 | 122.7951 | 122.7493 | -0.2243 | 122.85 | 122.8226 | 122.7905 | -0.24719
1746.5 | 122.8867 | -122.6898 | 0.17395 | 0.068054 | 0.023605 | 0.0038024 | 0.0093909 | -0.0060476 | -0.0071842 | -0.0058747 | 0.13252 | -0.0093503 | -0.0013394 | -0.0017624 | -0.00037807 | -0.0078122 | 0.10071 | 0.1236 | 0.13733 | 0.1236 | 0.23804 | 0.068665 | -0.054932 | 0.13733 | 0.20142 | 0.064087 | 0.18768 | 0.15564 | -0.027466 | -0.07782 | 122.7585 | 122.6349 | 0.064087 | 122.8134 | 122.8134 | 0.17853 | -0.073242 | 122.6624 | 122.612 | 0.013733 | 122.8271 | 122.7539 | 0.14191 | -0.01831 | 122.9279 | 122.7905 | 122.8271 | -0.22888 | 122.8775 | 122.8455 | 122.8912 | -0.25177
1748.2031 | 123.0057 | -122.6257 | 0.14648 | -0.16846 | 0.024033 | 0.0050842 | 0.0061865 | -0.0062612 | 7.902e-05 | -0.0037385 | -0.18791 | -0.0070003 | -0.0064664 | 0.0020828 | 0.0023989 | -0.013366 | 0.17395 | 0.1236 | 0.1236 | 0.1236 | 0.29755 | 0.082397 | -0.073242 | 0.10986 | 0.16479 | 0 | 0.20599 | 0.19684 | -0.027466 | -0.091553 | 122.7081 | 122.5525 | 0.15106 | 122.7493 | 122.7493 | 0.19684 | 0.027466 | 122.5983 | 122.5342 | 0.05951 | 122.7356 | 122.6257 | 0.091553 | 0.050354 | 122.9233 | 122.7997 | 122.7493 | -0.21973 | 122.8317 | 122.8226 | 122.7905 | -0.23804
1749.9375 | 122.9645 | -122.6669 | 0.15564 | -0.19135 | 0.02446 | 0.0044434 | 0.0096045 | -0.0032706 | -0.0031254 | -0.0077973 | -0.18028 | -0.011487 | -0.003262 | -0.0038986 | 0.00090353 | -0.011444 | 0.20599 | 0.23346 | 0.2243 | 0.21515 | 0.28381 | 0.11902 | -0.045776 | 0.17853 | 0.28839 | 0.10529 | 0.23804 | 0.20142 | 0.013733 | -0.041199 | 122.7859 | 122.6212 | 0.12817 | 122.9004 | 122.8821 | 0.26093 | 0.050354 | 122.6807 | 122.6257 | 0.082397 | 122.8455 | 122.7722 | 0.14649 | 0.045776 | 122.9507 | 122.8729 | 122.8912 | -0.20142 | 122.905 | 122.8683 | 122.9553 | -0.19684
1751.625 | 123.0057 | -122.6212 | 0.14648 | -0.076904 | 0.019119 | 0.0052978 | 0.0053321 | -0.0064748 | -0.0059024 | -0.0075837 | -0.050583 | -0.011273 | -0.0047574 | -0.00069421 | 0.0017581 | -0.010376 | 0.17853 | 0.2243 | 0.21057 | 0.1831 | 0.27924 | 0.10529 | -0.041199 | 0.21515 | 0.29755 | 0.16937 | 0.20599 | 0.16479 | 0.022888 | -0.036621 | 122.7264 | 122.58 | 0.13275 | 122.8455 | 122.8043 | 0.2243 | 0.032044 | 122.644 | 122.5845 | 0.05951 | 122.8363 | 122.7905 | 0.20599 | 0.018311 | 122.9004 | 122.7997 | 122.8317 | -0.18768 | 122.8271 | 122.7859 | 122.9187 | -0.18311
1753.3281 | 122.8546 | -122.7036 | 0.16479 | 0.19775 | 0.021896 | 0.0033752 | 0.0014867 | -0.007543 | -0.00077538 | -0.0050201 | 0.16304 | -0.0080685 | -0.0045438 | -0.0015488 | 0.0032535 | -0.011657 | 0.14648 | 0.14191 | 0.17853 | 0.10071 | 0.17395 | 0.054932 | -0.11902 | 0.16479 | 0.19684 | 0.07782 | 0.13275 | 0.10071 | -0.054932 | -0.11902 | 122.7585 | 122.5845 | 0.009155 | 122.8455 | 122.8043 | 0.21973 | -0.018311 | 122.6486 | 122.5845 | -0.032044 | 122.8683 | 122.7814 | 0.19684 | -0.064087 | 122.8775 | 122.85 | 122.8821 | -0.28381 | 122.8363 | 122.8043 | 122.9004 | -0.28381
1755.0312 | 122.9919 | -122.6669 | 0.14648 | -0.24475 | 0.022751 | 0.0035888 | 0.0055457 | -0.0047658 | 0.00071982 | -0.0033111 | -0.27184 | -0.0076413 | -0.0039028 | -0.0021896 | 0.0028263 | -0.010803 | 0.16937 | 0.13733 | 0.11444 | 0.13733 | 0.37079 | 0.10529 | -0.064087 | 0.11902 | 0.15106 | 0.022888 | 0.2655 | 0.23804 | -0.009155 | -0.064087 | 122.7722 | 122.6028 | 0.2243 | 122.8043 | 122.8043 | 0.20142 | 0.022889 | 122.6578 | 122.6028 | 0.11902 | 122.7859 | 122.6898 | 0.086975 | 0.091553 | 123.0377 | 122.8363 | 122.7814 | -0.21057 | 122.9324 | 122.905 | 122.818 | -0.21057
1756.7188 | 122.9919 | -122.6212 | 0.15564 | -0.015869 | 0.020187 | 0.006366 | 0.0057593 | -0.005834 | -0.004407 | -0.0063019 | 0.010452 | -0.010846 | -0.0041164 | -0.00048061 | -0.00016447 | -0.010803 | 0.15564 | 0.17853 | 0.19226 | 0.14648 | 0.28839 | 0.10529 | -0.068665 | 0.1831 | 0.27008 | 0.12817 | 0.1831 | 0.17395 | 0.013733 | -0.036621 | 122.7264 | 122.5525 | 0.13275 | 122.7997 | 122.7676 | 0.21515 | 0 | 122.6349 | 122.5845 | 0.027465 | 122.8043 | 122.7493 | 0.1648 | 0.01831 | 122.9095 | 122.7768 | 122.8134 | -0.22431 | 122.8043 | 122.7951 | 122.8912 | -0.19226
1758.4062 | 123.0286 | -122.644 | 0.16022 | -0.17609 | 0.023819 | 0.0040162 | 0.0078955 | -0.0039114 | 0.001788 | -0.0063019 | -0.22606 | -0.0089229 | -0.0039028 | 0.00058739 | 0.0047489 | -0.012726 | 0.16479 | 0.11444 | 0.11902 | 0.13733 | 0.33875 | 0.09613 | -0.064087 | 0.11902 | 0.15106 | 0.013733 | 0.23346 | 0.21515 | -0.027466 | -0.082397 | 122.7402 | 122.58 | 0.17853 | 122.7585 | 122.7814 | 0.20142 | 0.004578 | 122.6166 | 122.5616 | 0.073242 | 122.7631 | 122.6578 | 0.09613 | 0.054932 | 122.9828 | 122.8088 | 122.7631 | -0.2243 | 122.8775 | 122.8592 | 122.7951 | -0.24261
1760.1094 | 122.8775 | -122.6898 | 0.19226 | -0.038757 | 0.023392 | 0.0010254 | 0.0038367 | -0.0064748 | 0.0020016 | -0.0028839 | -0.065842 | -0.0074277 | -0.003262 | 0.0010148 | 0.0077395 | -0.011871 | 0.15564 | 0.10986 | 0.086975 | 0.10071 | 0.27008 | 0.041199 | -0.11444 | 0.073242 | 0.09613 | -0.059509 | 0.17853 | 0.15564 | -0.073242 | -0.13733 | 122.731 | 122.5754 | 0.07782 | 122.7997 | 122.7905 | 0.21515 | -0.036621 | 122.6166 | 122.5525 | -0.013733 | 122.7631 | 122.6303 | 0.07782 | -0.036621 | 122.9599 | 122.8455 | 122.7768 | -0.3067 | 122.8683 | 122.8455 | 122.7859 | -0.32959
1761.7969 | 123.0057 | -122.6532 | 0.14191 | -0.18372 | 0.02681 | 0.0023072 | 0.0059729 | -0.0066884 | -0.00098918 | -0.0024567 | -0.19554 | -0.0078549 | -0.0047574 | 0.00080099 | 0.0049625 | -0.012512 | 0.15564 | 0.14648 | 0.11902 | 0.14191 | 0.32044 | 0.091553 | -0.059509 | 0.09613 | 0.15564 | 0.018311 | 0.22888 | 0.19226 | -0.050354 | -0.10071 | 122.7448 | 122.5937 | 0.17853 | 122.7997 | 122.7951 | 0.20142 | 0.013733 | 122.6028 | 122.5525 | 0.086975 | 122.7493 | 122.6715 | 0.11902 | 0.050354 | 122.9736 | 122.8088 | 122.7722 | -0.20142 | 122.8821 | 122.8455 | 122.8088 | -0.24262
1763.4688 | 122.9736 | -122.6166 | 0.14191 | -0.16083 | 0.021896 | 0.0038024 | 0.0046911 | -0.0064748 | -0.0063296 | -0.0060883 | -0.12688 | -0.012127 | -0.0045438 | -0.00069421 | 4.9132e-05 | -0.012726 | 0.21057 | 0.29297 | 0.25177 | 0.23346 | 0.3067 | 0.1236 | -0.018311 | 0.21515 | 0.32959 | 0.17395 | 0.20599 | 0.17395 | 0.041199 | -0.041199 | 122.7402 | 122.5983 | 0.16479 | 122.9095 | 122.85 | 0.25177 | 0.068664 | 122.6578 | 122.5754 | 0.064087 | 122.8317 | 122.7905 | 0.21515 | 0.032043 | 122.9233 | 122.8271 | 122.8683 | -0.16022 | 122.8226 | 122.7905 | 122.9462 | -0.18311
1765.1562 | 122.9507 | -122.6715 | 0.15106 | -0.24475 | 0.023178 | 0.0048706 | 0.0083227 | -0.0051932 | -0.0020572 | -0.0063019 | -0.20317 | -0.0082821 | -0.0036892 | 0.0010148 | 0.00068993 | -0.012298 | 0.17395 | 0.20599 | 0.16937 | 0.1831 | 0.33875 | 0.10986 | -0.041199 | 0.13275 | 0.20142 | 0.050354 | 0.27924 | 0.21973 | -0.004578 | -0.059509 | 122.7814 | 122.6303 | 0.18768 | 122.8775 | 122.8546 | 0.2243 | 0.022888 | 122.6669 | 122.612 | 0.12817 | 122.8043 | 122.7219 | 0.10986 | 0.068665 | 123.0103 | 122.8455 | 122.8409 | -0.19226 | 122.9507 | 122.8912 | 122.8729 | -0.21057
1766.8438 | 122.9919 | -122.6486 | 0.15564 | 0.0070193 | 0.022965 | 0.0057252 | 0.0070409 | -0.0026296 | -0.0052616 | -0.0067291 | 0.04097 | -0.010418 | -0.0053982 | -0.0013352 | 0.0015445 | -0.010589 | 0.10986 | 0.16479 | 0.16479 | 0.13733 | 0.27466 | 0.073242 | -0.073242 | 0.16937 | 0.24719 | 0.10986 | 0.20142 | 0.16479 | 0.004578 | -0.073242 | 122.7219 | 122.5754 | 0.11902 | 122.8134 | 122.7859 | 0.21057 | -0.045777 | 122.6532 | 122.5754 | 0.045776 | 122.818 | 122.7585 | 0.18311 | 0.009155 | 122.9233 | 122.7585 | 122.8134 | -0.22888 | 122.85 | 122.8134 | 122.8958 | -0.22888
1768.5469 | 122.905 | -122.6715 | 0.15564 | 0.014648 | 0.022537 | 0.0031616 | 0.0049047 | -0.0056204 | -0.0014164 | -0.0058747 | 0.071487 | -0.011059 | -0.0041164 | -0.00026701 | 0.0026125 | -0.01123 | 0.12817 | 0.14191 | 0.15564 | 0.12817 | 0.25635 | 0.09613 | -0.082397 | 0.15564 | 0.20599 | 0.09613 | 0.20599 | 0.16479 | -0.022888 | -0.073242 | 122.7676 | 122.5891 | 0.10071 | 122.8134 | 122.7997 | 0.21057 | -0.027466 | 122.6486 | 122.5983 | 0.050354 | 122.8271 | 122.7676 | 0.16937 | 0.009155 | 122.9279 | 122.7997 | 122.8271 | -0.23804 | 122.8775 | 122.8363 | 122.8775 | -0.22888
1770.2344 | 122.9965 | -122.6303 | 0.14648 | -0.13031 | 0.023392 | 0.002948 | 0.0034093 | -0.0056204 | 0.0030698 | -0.0054475 | -0.19554 | -0.0080685 | -0.0071072 | -0.0024032 | 0.0077395 | -0.013153 | 0.1831 | 0.13733 | 0.11444 | 0.1236 | 0.27924 | 0.054932 | -0.10529 | 0.13733 | 0.16937 | 0.004578 | 0.19684 | 0.16937 | -0.050354 | -0.11902 | 122.6852 | 122.525 | 0.13275 | 122.7676 | 122.7539 | 0.22888 | 0.036621 | 122.58 | 122.5113 | 0.050354 | 122.7676 | 122.6349 | 0.1236 | 0.022889 | 122.9095 | 122.8134 | 122.7448 | -0.25177 | 122.8271 | 122.7997 | 122.7997 | -0.2655
1771.9375 | 122.9965 | -122.6349 | 0.14191 | -0.031128 | 0.017838 | 0.0055114 | 0.0053321 | -0.0071158 | -0.0048344 | -0.0069427 | -0.042954 | -0.011059 | -0.004971 | -0.00048061 | 0.00068993 | -0.012085 | 0.16022 | 0.20599 | 0.19684 | 0.16937 | 0.25635 | 0.09613 | -0.045776 | 0.21057 | 0.28839 | 0.15106 | 0.19684 | 0.16937 | 0.018311 | -0.045776 | 122.731 | 122.5891 | 0.11444 | 122.8409 | 122.8043 | 0.21515 | 0.01831 | 122.6532 | 122.5891 | 0.054931 | 122.8455 | 122.7859 | 0.19684 | 0.027466 | 122.8912 | 122.7951 | 122.8317 | -0.18768 | 122.8317 | 122.8043 | 122.9233 | -0.18768
1773.625 | 122.8592 | -122.6578 | 0.16022 | 0.1062 | 0.02211 | 0.0044434 | 0.0027685 | -0.0062612 | -0.0018436 | -0.0063019 | 0.16304 | -0.0087093 | -0.006039 | -0.00048061 | 0.0023989 | -0.010803 | 0.14648 | 0.16479 | 0.15106 | 0.10986 | 0.21057 | 0.045776 | -0.091553 | 0.16022 | 0.21057 | 0.064087 | 0.16479 | 0.13733 | -0.036621 | -0.09613 | 122.7036 | 122.5662 | 0.050354 | 122.8226 | 122.7676 | 0.20142 | -0.013733 | 122.6212 | 122.5616 | 0.004578 | 122.818 | 122.7219 | 0.16022 | -0.022888 | 122.8683 | 122.8043 | 122.8088 | -0.25177 | 122.8226 | 122.7951 | 122.8683 | -0.25635
1775.3125 | 122.8729 | -122.6944 | 0.18768 | 0.083313 | 0.025314 | 0.0044434 | 0.0049047 | -0.0043386 | 0.0039242 | -0.0041657 | -0.035324 | -0.0078549 | -0.0062528 | -0.00069421 | 0.0053897 | -0.014221 | 0.091553 | 0.027466 | 0.045776 | 0.041199 | 0.25635 | 0.022888 | -0.13275 | 0.027466 | 0.050354 | -0.09613 | 0.1831 | 0.16937 | -0.082397 | -0.15106 | 122.7173 | 122.5616 | 0.068665 | 122.7219 | 122.7356 | 0.17395 | -0.09613 | 122.612 | 122.5433 | -0.004578 | 122.7219 | 122.5983 | 0.054932 | -0.01831 | 122.9507 | 122.7859 | 122.7402 | -0.32043 | 122.8775 | 122.8638 | 122.7448 | -0.33874
1776.9844 | 122.905 | -122.6898 | 0.17395 | 0.045166 | 0.019119 | 0.0061524 | 0.0038367 | -0.0071158 | -0.0059024 | -0.0052337 | 0.086746 | -0.010632 | -0.0073208 | -0.001976 | 0.0038943 | -0.0075986 | 0.1236 | 0.16937 | 0.15564 | 0.13733 | 0.27008 | 0.07782 | -0.064087 | 0.16022 | 0.21515 | 0.082397 | 0.19684 | 0.17853 | -0.009155 | -0.073242 | 122.7676 | 122.6257 | 0.096131 | 122.8592 | 122.8271 | 0.20142 | -0.050354 | 122.6807 | 122.6166 | 0.022888 | 122.85 | 122.7722 | 0.15564 | 0.004578 | 122.9599 | 122.8134 | 122.8455 | -0.23804 | 122.8867 | 122.8683 | 122.905 | -0.24719
1778.6719 | 122.8775 | -122.7127 | 0.17853 | 0.029907 | 0.024674 | 0.0033752 | 0.0017005 | -0.0051932 | 0.0043514 | -0.0020295 | 0.0028229 | -0.0057187 | -0.0071072 | -0.00090781 | 0.0070987 | -0.013794 | 0.086975 | 0.018311 | 0.027466 | 0.059509 | 0.27008 | 0.022888 | -0.13733 | 0.032043 | 0.054932 | -0.07782 | 0.18768 | 0.16479 | -0.086975 | -0.13275 | 122.7356 | 122.5754 | 0.091553 | 122.731 | 122.7722 | 0.19684 | -0.091553 | 122.6257 | 122.58 | 0.009155 | 122.7448 | 122.6349 | 0.054931 | -0.013733 | 122.9828 | 122.7997 | 122.7402 | -0.31586 | 122.9004 | 122.8775 | 122.7676 | -0.31128
1780.3594 | 122.9828 | -122.644 | 0.11902 | -0.14557 | 0.021042 | 0.0035888 | 0.0070409 | -0.0062612 | -0.0046206 | -0.0077973 | -0.11162 | -0.012982 | -0.0062528 | -0.001976 | 0.00068993 | -0.011444 | 0.26093 | 0.27466 | 0.27008 | 0.21057 | 0.27924 | 0.13275 | -0.018311 | 0.22888 | 0.34332 | 0.16937 | 0.20599 | 0.1831 | 0.032043 | -0.032043 | 122.7768 | 122.6257 | 0.16022 | 122.9187 | 122.8546 | 0.22888 | 0.14191 | 122.6761 | 122.612 | 0.086975 | 122.8729 | 122.8134 | 0.20142 | 0.064086 | 122.9233 | 122.905 | 122.9141 | -0.13733 | 122.85 | 122.8271 | 122.9874 | -0.15106
1782.0469 | 122.8821 | -122.6852 | 0.16479 | 0.060425 | 0.016556 | 0.0038024 | 0.0044775 | -0.008611 | -0.0056888 | -0.0050201 | 0.048599 | -0.011059 | -0.0086026 | -0.0045394 | 0.0032535 | -0.0099484 | 0.15106 | 0.16022 | 0.15564 | 0.11902 | 0.23804 | 0.07782 | -0.07782 | 0.15564 | 0.19684 | 0.07782 | 0.1831 | 0.15106 | -0.018311 | -0.068665 | 122.7631 | 122.6074 | 0.073242 | 122.8455 | 122.8043 | 0.19684 | -0.013733 | 122.6669 | 122.6166 | 0.01831 | 122.8409 | 122.7631 | 0.14649 | -0.013733 | 122.9233 | 122.8363 | 122.8409 | -0.24261 | 122.8683 | 122.8363 | 122.8821 | -0.23346
1783.7344 | 122.8638 | -122.699 | 0.19226 | 0.15198 | 0.019974 | 0.0076478 | 0.0042639 | -0.0071158 | -0.0012028 | -0.0050201 | 0.12489 | -0.011059 | -0.0051846 | -0.0011216 | 0.0045351 | -0.010803 | 0.14191 | 0.15106 | 0.16022 | 0.11902 | 0.21057 | 0.050354 | -0.09613 | 0.17395 | 0.20142 | 0.064087 | 0.15564 | 0.15106 | -0.036621 | -0.07782 | 122.7493 | 122.6028 | 0.01831 | 122.85 | 122.818 | 0.21515 | -0.050354 | 122.6624 | 122.6212 | -0.036621 | 122.8729 | 122.7631 | 0.14191 | -0.041199 | 122.9095 | 122.8409 | 122.8592 | -0.28839 | 122.8546 | 122.85 | 122.9004 | -0.27008
1785.4375 | 123.0011 | -122.6578 | 0.14191 | -0.14557 | 0.025314 | 0.0040162 | 0.0055457 | -0.0062612 | 0.003497 | -0.0041657 | -0.19554 | -0.0072141 | -0.0053982 | 0.00058739 | 0.0056033 | -0.01358 | 0.19684 | 0.14191 | 0.10986 | 0.14191 | 0.29297 | 0.045776 | -0.09613 | 0.13733 | 0.16937 | 0.009155 | 0.20599 | 0.16022 | -0.041199 | -0.10071 | 122.7036 | 122.5616 | 0.15106 | 122.7997 | 122.7997 | 0.23804 | 0.054931 | 122.6166 | 122.5571 | 0.064087 | 122.7951 | 122.6669 | 0.10986 | 0.01831 | 122.9507 | 122.8546 | 122.7676 | -0.23804 | 122.8638 | 122.818 | 122.8271 | -0.24262
1787.1094 | 123.0011 | -122.644 | 0.15106 | -0.13794 | 0.023178 | 0.0050842 | 0.0044775 | -0.0083974 | 0.0026424 | -0.0041657 | -0.18791 | -0.0078549 | -0.0043302 | -0.00026701 | 0.0060305 | -0.011871 | 0.15564 | 0.14648 | 0.10529 | 0.13733 | 0.31128 | 0.064087 | -0.091553 | 0.11902 | 0.16022 | 0.004578 | 0.20599 | 0.16022 | -0.045776 | -0.09613 | 122.7081 | 122.5525 | 0.16022 | 122.7905 | 122.7814 | 0.22888 | 0.004578 | 122.5983 | 122.5479 | 0.054932 | 122.7631 | 122.6486 | 0.10071 | 0.009155 | 122.9553 | 122.7997 | 122.7493 | -0.24261 | 122.85 | 122.8043 | 122.8043 | -0.24719
1788.7969 | 122.9645 | -122.6578 | 0.15106 | -0.21423 | 0.022324 | 0.0061524 | 0.0096045 | -0.0069022 | -0.0039798 | -0.0056611 | -0.11925 | -0.0097775 | -0.0034756 | -0.0021896 | 0.0013309 | -0.011657 | 0.21515 | 0.28839 | 0.25635 | 0.21515 | 0.29755 | 0.1236 | -0.027466 | 0.20599 | 0.31128 | 0.14648 | 0.21057 | 0.16937 | 0.022888 | -0.041199 | 122.7814 | 122.6303 | 0.14648 | 122.9462 | 122.8729 | 0.24261 | 0.064087 | 122.6807 | 122.6166 | 0.059509 | 122.8638 | 122.8043 | 0.18768 | 0.018311 | 122.9553 | 122.8729 | 122.9141 | -0.17853 | 122.8683 | 122.8271 | 122.9691 | -0.19226
1790.4844 | 122.9187 | -122.6715 | 0.16937 | 0.11383 | 0.02211 | 0.0055114 | 0.0012731 | -0.0079702 | 0.0015744 | -0.0039521 | 0.10963 | -0.0084957 | -0.0034756 | 0.0010148 | 0.0058169 | -0.011444 | 0.068665 | 0.045776 | 0.036621 | 0.054932 | 0.2655 | 0.004578 | -0.12817 | 0.086975 | 0.07782 | -0.027466 | 0.16479 | 0.14648 | -0.082397 | -0.14191 | 122.6761 | 122.5433 | 0.09613 | 122.7173 | 122.7264 | 0.18311 | -0.10071 | 122.5891 | 122.5296 | -0.004578 | 122.7585 | 122.644 | 0.11444 | -0.022889 | 122.937 | 122.7402 | 122.7081 | -0.29755 | 122.8363 | 122.818 | 122.7493 | -0.31128
1792.1875 | 122.9279 | -122.699 | 0.1831 | 0.1062 | 0.025101 | 0.0031616 | 0.0017005 | -0.0071158 | 0.0013608 | -0.0030975 | 0.15541 | -0.0093503 | -0.007748 | -0.0011216 | 0.0053897 | -0.010803 | 0.082397 | 0.068665 | 0.032043 | 0.050354 | 0.24261 | -0.009155 | -0.14191 | 0.07782 | 0.10071 | -0.032043 | 0.16479 | 0.14191 | -0.07782 | -0.10986 | 122.6898 | 122.5571 | 0.05951 | 122.7676 | 122.7493 | 0.19226 | -0.10071 | 122.6212 | 122.5891 | -0.01831 | 122.7768 | 122.6669 | 0.07782 | -0.041198 | 122.9416 | 122.7814 | 122.731 | -0.32501 | 122.8638 | 122.8409 | 122.7997 | -0.29297
1793.875 | 122.9691 | -122.6532 | 0.13733 | -0.21423 | 0.022751 | 0.0055114 | 0.010673 | -0.0066884 | -0.0052616 | -0.0058747 | -0.08873 | -0.011914 | -0.0045438 | -0.00026701 | -0.00037807 | -0.010803 | 0.21515 | 0.27924 | 0.27008 | 0.21515 | 0.3067 | 0.14191 | -0.004578 | 0.20142 | 0.30212 | 0.13733 | 0.21515 | 0.19226 | 0.018311 | -0.050354 | 122.7951 | 122.6486 | 0.16937 | 122.9324 | 122.8683 | 0.21973 | 0.07782 | 122.6715 | 122.6028 | 0.07782 | 122.8546 | 122.7905 | 0.18768 | 0.054932 | 122.9599 | 122.8683 | 122.9233 | -0.14191 | 122.8683 | 122.8455 | 122.9553 | -0.18768
1795.5625 | 122.9233 | -122.699 | 0.16937 | 0.16724 | 0.021896 | 0.0042298 | 0.0046911 | -0.0047658 | -0.00056178 | -0.0056611 | 0.14778 | -0.0067867 | -0.007748 | 0.00080099 | 0.0058169 | -0.011657 | 0.14648 | 0.1236 | 0.11902 | 0.09613 | 0.21515 | 0.036621 | -0.13733 | 0.15564 | 0.18768 | 0.050354 | 0.13275 | 0.11444 | -0.050354 | -0.09613 | 122.7356 | 122.5616 | 0.045776 | 122.8226 | 122.7951 | 0.23346 | -0.022889 | 122.6486 | 122.6028 | -0.036622 | 122.8546 | 122.7493 | 0.14648 | -0.054932 | 122.9141 | 122.8455 | 122.818 | -0.3067 | 122.8317 | 122.8134 | 122.8867 | -0.2655
1797.2812 | 122.9691 | -122.6532 | 0.16022 | -0.17609 | 0.020828 | 0.0038024 | 0.0072547 | -0.0069022 | -0.004407 | -0.0065155 | -0.14214 | -0.0074277 | -0.004971 | -0.0028306 | 0.00068993 | -0.012085 | 0.21057 | 0.26093 | 0.23804 | 0.21515 | 0.29755 | 0.13733 | -0.027466 | 0.19684 | 0.30212 | 0.12817 | 0.22888 | 0.19226 | 0.018311 | -0.050354 | 122.7905 | 122.6257 | 0.13733 | 122.9141 | 122.8683 | 0.24261 | 0.050354 | 122.6715 | 122.6028 | 0.068665 | 122.85 | 122.7814 | 0.17853 | 0.032044 | 122.9507 | 122.8638 | 122.8912 | -0.18768 | 122.8821 | 122.8455 | 122.9553 | -0.21057
1798.9688 | 122.9004 | -122.6715 | 0.16479 | 0.029907 | 0.02211 | 0.0052978 | 0.0066137 | -0.005834 | -0.0039798 | -0.0045929 | 0.063858 | -0.0095639 | -0.0043302 | -0.00048061 | 0.0028263 | -0.012726 | 0.11902 | 0.16022 | 0.16479 | 0.1236 | 0.25177 | 0.082397 | -0.064087 | 0.15106 | 0.18768 | 0.07782 | 0.19684 | 0.16937 | -0.013733 | -0.059509 | 122.7539 | 122.6074 | 0.086975 | 122.8317 | 122.7951 | 0.18768 | -0.045776 | 122.6578 | 122.612 | 0.032043 | 122.8226 | 122.7493 | 0.13733 | 0.004578 | 122.9233 | 122.7905 | 122.8363 | -0.22888 | 122.8683 | 122.8409 | 122.8592 | -0.2243
1800.6719 | 122.9965 | -122.644 | 0.16479 | -0.25238 | 0.023392 | 0.0040162 | 0.0070409 | -0.0069022 | 0.00050622 | -0.0071563 | -0.26421 | -0.0080685 | -0.0021938 | 0.00058739 | 0.0038943 | -0.013794 | 0.16022 | 0.16022 | 0.13275 | 0.15106 | 0.3891 | 0.10986 | -0.045776 | 0.11902 | 0.15564 | 0.013733 | 0.27466 | 0.2243 | -0.022888 | -0.073242 | 122.7539 | 122.5983 | 0.2243 | 122.8043 | 122.7951 | 0.19684 | -0.004578 | 122.6212 | 122.5708 | 0.10986 | 122.7631 | 122.6578 | 0.086975 | 0.059509 | 123.0331 | 122.8043 | 122.7768 | -0.21057 | 122.9187 | 122.8683 | 122.7997 | -0.23804
1802.3906 | 122.9324 | -122.6761 | 0.16937 | 0.19012 | 0.022324 | 0.0050842 | 0.0017005 | -0.0079702 | 0.00029262 | -0.0043793 | 0.102 | -0.0076413 | -0.0075344 | -0.00048061 | 0.0075259 | -0.011017 | 0.11444 | 0.09613 | 0.11902 | 0.091553 | 0.20599 | 0.032043 | -0.11902 | 0.16022 | 0.20142 | 0.059509 | 0.14191 | 0.11902 | -0.054932 | -0.11444 | 122.7081 | 122.5571 | 0.036621 | 122.7722 | 122.7676 | 0.21057 | -0.054932 | 122.6212 | 122.5616 | -0.027466 | 122.8363 | 122.7356 | 0.17395 | -0.050354 | 122.8821 | 122.7905 | 122.7951 | -0.28839 | 122.818 | 122.7951 | 122.8775 | -0.28381
1804.0938 | 122.9965 | -122.6669 | 0.15564 | -0.22949 | 0.021896 | 0.0038024 | 0.0057593 | -0.005834 | 0.00029262 | -0.0041657 | -0.24132 | -0.0089229 | -0.0039028 | -0.0024032 | 0.0045351 | -0.010803 | 0.17853 | 0.16022 | 0.12817 | 0.13733 | 0.37537 | 0.11444 | -0.036621 | 0.1236 | 0.17395 | 0.022888 | 0.27924 | 0.23346 | -0.013733 | -0.059509 | 122.7814 | 122.6303 | 0.21973 | 122.8271 | 122.8043 | 0.17395 | 0.022888 | 122.6532 | 122.6074 | 0.1236 | 122.7905 | 122.6898 | 0.082397 | 0.077819 | 123.0423 | 122.8455 | 122.7951 | -0.19226 | 122.9462 | 122.9004 | 122.8409 | -0.21515
1805.7812 | 122.9599 | -122.6532 | 0.14648 | -0.015869 | 0.023178 | 0.0040162 | 0.0078955 | -0.0073294 | -0.0056888 | -0.0058747 | 0.063858 | -0.0093503 | -0.0030484 | -0.0013352 | 0.0011173 | -0.0099484 | 0.11902 | 0.16022 | 0.16022 | 0.14191 | 0.27008 | 0.09613 | -0.054932 | 0.16479 | 0.24261 | 0.10529 | 0.20142 | 0.1831 | -0.022888 | -0.054932 | 122.7493 | 122.5983 | 0.1236 | 122.8134 | 122.7951 | 0.19684 | -0.027465 | 122.6303 | 122.5983 | 0.054932 | 122.818 | 122.7585 | 0.16022 | 0.036621 | 122.9233 | 122.7722 | 122.8134 | -0.20142 | 122.8546 | 122.8363 | 122.8958 | -0.20142
1807.5 | 122.9279 | -122.6578 | 0.1831 | 0.1062 | 0.023178 | 0.0035888 | 0.0049047 | -0.0077566 | 0.0022152 | -0.0035249 | 0.04097 | -0.0072141 | -0.0062528 | -0.0015488 | 0.0062441 | -0.013153 | 0.07782 | 0.009155 | 0.018311 | 0.032043 | 0.27466 | 0.018311 | -0.13733 | 0.073242 | 0.059509 | -0.068665 | 0.17853 | 0.14191 | -0.091553 | -0.1236 | 122.6761 | 122.5204 | 0.091553 | 122.6669 | 122.6898 | 0.16937 | -0.10528 | 122.5662 | 122.5342 | -0.004577 | 122.731 | 122.5891 | 0.054931 | -0.041198 | 122.9324 | 122.7356 | 122.6761 | -0.32043 | 122.8363 | 122.7997 | 122.7173 | -0.3067
1809.1875 | 123.0103 | -122.6486 | 0.13733 | -0.13031 | 0.023819 | 0.002948 | 0.0046911 | -0.0049796 | 0.003497 | -0.0050201 | -0.18791 | -0.0095639 | -0.004971 | 0.00058739 | 0.0051761 | -0.011871 | 0.18768 | 0.14191 | 0.1236 | 0.13733 | 0.32959 | 0.059509 | -0.073242 | 0.1236 | 0.16479 | 0.009155 | 0.21515 | 0.17853 | -0.041199 | -0.10986 | 122.7081 | 122.5754 | 0.19226 | 122.7905 | 122.7859 | 0.21057 | 0.050354 | 122.6074 | 122.5388 | 0.07782 | 122.7722 | 122.6578 | 0.11902 | 0.041199 | 122.9782 | 122.8363 | 122.7722 | -0.21057 | 122.8638 | 122.8271 | 122.8134 | -0.24719
1810.9375 | 122.8912 | -122.6944 | 0.16937 | 0.075684 | 0.01976 | 0.0055114 | 0.0034093 | -0.0062612 | -0.0041934 | -0.0067291 | 0.11726 | -0.0087093 | -0.0064664 | 0.00037379 | 0.0017581 | -0.0086666 | 0.13733 | 0.14648 | 0.16022 | 0.12817 | 0.27466 | 0.064087 | -0.07782 | 0.15564 | 0.21057 | 0.091553 | 0.21057 | 0.16479 | -0.027466 | -0.073242 | 122.7585 | 122.6166 | 0.10529 | 122.8409 | 122.8226 | 0.20599 | -0.032044 | 122.6669 | 122.6212 | 0.041198 | 122.85 | 122.7859 | 0.16479 | -0.004578 | 122.9691 | 122.8317 | 122.8546 | -0.24719 | 122.905 | 122.8592 | 122.905 | -0.24261
1812.625 | 122.8958 | -122.7219 | 0.16937 | 0.0070193 | 0.024246 | 0.0033752 | 0.0029821 | -0.0064748 | 0.0047788 | -0.0050201 | -0.027695 | -0.0055051 | -0.0062528 | 0.0016556 | 0.0047489 | -0.011657 | 0.11444 | 0.045776 | 0.032043 | 0.041199 | 0.26093 | 0.045776 | -0.10986 | 0.050354 | 0.059509 | -0.073242 | 0.16479 | 0.16479 | -0.082397 | -0.12817 | 122.7676 | 122.612 | 0.091552 | 122.7676 | 122.7631 | 0.15106 | -0.054932 | 122.6395 | 122.5937 | -0.004578 | 122.7722 | 122.6486 | 0.054932 | -0.004578 | 122.9828 | 122.8363 | 122.7539 | -0.27924 | 122.8867 | 122.8867 | 122.7814 | -0.29755
1814.3125 | 123.0286 | -122.6532 | 0.14648 | -0.18372 | 0.025742 | 0.0042298 | 0.0055457 | -0.0088248 | -0.00056178 | -0.0056611 | -0.22606 | -0.0097775 | -0.0039028 | -0.00069421 | 0.0019717 | -0.013794 | 0.14648 | 0.11444 | 0.1236 | 0.13733 | 0.33875 | 0.091553 | -0.054932 | 0.11444 | 0.1831 | 0.013733 | 0.23804 | 0.22888 | -0.027466 | -0.064087 | 122.7448 | 122.5983 | 0.19226 | 122.7676 | 122.7905 | 0.19226 | 0 | 122.6257 | 122.5891 | 0.091553 | 122.7676 | 122.6669 | 0.07782 | 0.082398 | 122.9919 | 122.7997 | 122.7768 | -0.20142 | 122.8912 | 122.8821 | 122.8363 | -0.21057
1816 | 123.0057 | -122.6578 | 0.13733 | -0.10742 | 0.019333 | 0.0048706 | 0.0078955 | -0.0054068 | -0.0054752 | -0.0054475 | -0.081101 | -0.012127 | -0.0019802 | -0.0026168 | -0.00059167 | -0.0095212 | 0.24719 | 0.3067 | 0.28381 | 0.23804 | 0.29297 | 0.12817 | -0.027466 | 0.24261 | 0.3479 | 0.1831 | 0.2243 | 0.20142 | 0.036621 | -0.022888 | 122.7859 | 122.6303 | 0.15564 | 122.9645 | 122.8958 | 0.2655 | 0.10986 | 122.6944 | 122.6349 | 0.086975 | 122.9004 | 122.8409 | 0.20599 | 0.064087 | 122.9507 | 122.905 | 122.9416 | -0.16479 | 122.8821 | 122.8592 | 123.0057 | -0.16022
1817.7188 | 122.9736 | -122.644 | 0.16479 | -0.22186 | 0.024674 | 0.002948 | 0.0072547 | -0.0056204 | -0.00163 | -0.0056611 | -0.18028 | -0.0099911 | -0.0034756 | -0.0021896 | 0.00047633 | -0.010803 | 0.19684 | 0.21973 | 0.17853 | 0.1831 | 0.36621 | 0.1236 | -0.018311 | 0.13275 | 0.19226 | 0.045776 | 0.25635 | 0.23804 | 0.004578 | -0.059509 | 122.7676 | 122.6257 | 0.20142 | 122.8638 | 122.8271 | 0.20142 | 0.032043 | 122.6486 | 122.5845 | 0.091553 | 122.7768 | 122.6898 | 0.10528 | 0.073242 | 123.0103 | 122.8409 | 122.8226 | -0.18311 | 122.9004 | 122.8821 | 122.8363 | -0.2243
1819.4375 | 123.0011 | -122.6395 | 0.13275 | -0.092163 | 0.021896 | 0.0052978 | 0.0091773 | -0.007543 | -0.0071842 | -0.0067291 | -0.065842 | -0.012127 | -0.0053982 | -0.00090781 | 4.9132e-05 | -0.011017 | 0.19684 | 0.26093 | 0.22888 | 0.20142 | 0.3067 | 0.1236 | -0.018311 | 0.26093 | 0.3067 | 0.17395 | 0.2243 | 0.1831 | 0.018311 | -0.018311 | 122.7631 | 122.6212 | 0.17395 | 122.9004 | 122.8409 | 0.21973 | 0.064087 | 122.6578 | 122.6212 | 0.091553 | 122.9004 | 122.8134 | 0.19226 | 0.050354 | 122.9462 | 122.8363 | 122.8683 | -0.15106 | 122.8638 | 122.8226 | 122.9462 | -0.15106
1821.1406 | 122.9965 | -122.6486 | 0.16479 | -0.19897 | 0.026383 | 0.002948 | 0.0081091 | -0.0060476 | 7.902e-05 | -0.0069427 | -0.27946 | -0.0074277 | -0.0047574 | 0.00016019 | 0.0034671 | -0.012512 | 0.13733 | 0.16937 | 0.13275 | 0.14648 | 0.36163 | 0.10071 | -0.032043 | 0.14191 | 0.16479 | 0.032043 | 0.27008 | 0.24261 | -0.004578 | -0.059509 | 122.7493 | 122.6166 | 0.19684 | 122.818 | 122.7951 | 0.17853 | -0.027466 | 122.644 | 122.5891 | 0.10529 | 122.7905 | 122.6807 | 0.091552 | 0.07782 | 123.0103 | 122.7859 | 122.7814 | -0.19684 | 122.9187 | 122.8912 | 122.8134 | -0.2243
1822.8281 | 122.9782 | -122.6669 | 0.15106 | -0.16083 | 0.020828 | 0.0065796 | 0.0040503 | -0.0051932 | -0.0054752 | -0.0058747 | -0.15739 | -0.011273 | -0.0062528 | -0.0026168 | 0.0017581 | -0.01358 | 0.21973 | 0.3067 | 0.27008 | 0.21515 | 0.31586 | 0.15564 | 0.004578 | 0.23804 | 0.32959 | 0.17853 | 0.20142 | 0.20142 | 0.041199 | -0.032043 | 122.8226 | 122.6715 | 0.16479 | 122.9736 | 122.8821 | 0.21057 | 0.068665 | 122.7081 | 122.6349 | 0.050354 | 122.905 | 122.8455 | 0.21057 | 0.050354 | 122.9828 | 122.8867 | 122.937 | -0.14648 | 122.8683 | 122.8683 | 122.9965 | -0.18311
1824.5156 | 122.9187 | -122.6715 | 0.16022 | 0.15961 | 0.020187 | 0.0048706 | 0.0010595 | -0.004125 | 0.00093342 | -0.0045929 | 0.14015 | -0.010632 | -0.007748 | -0.0021896 | 0.0066715 | -0.013366 | 0.13733 | 0.17395 | 0.12817 | 0.12817 | 0.20599 | 0.050354 | -0.10986 | 0.16022 | 0.18768 | 0.073242 | 0.14191 | 0.10529 | -0.059509 | -0.11902 | 122.7219 | 122.5616 | 0.045777 | 122.8455 | 122.7997 | 0.23804 | -0.022888 | 122.612 | 122.5525 | -0.01831 | 122.8317 | 122.7448 | 0.19226 | -0.054931 | 122.8775 | 122.8088 | 122.7997 | -0.27008 | 122.8134 | 122.7768 | 122.8592 | -0.27924
1826.2188 | 123.0148 | -122.6212 | 0.16022 | -0.061646 | 0.023178 | 0.0050842 | 0.0059729 | -0.002416 | -0.0037662 | -0.0065155 | -0.042954 | -0.0089229 | -0.0039028 | 0.00037379 | 0.0013309 | -0.010162 | 0.16479 | 0.21515 | 0.20142 | 0.17395 | 0.29755 | 0.09613 | -0.041199 | 0.22888 | 0.29755 | 0.16022 | 0.22888 | 0.19226 | 0.013733 | -0.036621 | 122.7173 | 122.58 | 0.13733 | 122.8363 | 122.7951 | 0.21515 | 0.004578 | 122.6349 | 122.5845 | 0.068665 | 122.85 | 122.7814 | 0.19684 | 0.032044 | 122.9187 | 122.7859 | 122.8226 | -0.20142 | 122.85 | 122.8134 | 122.9187 | -0.19684
1827.9688 | 123.0103 | -122.6486 | 0.15564 | -0.023499 | 0.02211 | 0.0057252 | 0.0057593 | -0.0062612 | -0.0037662 | -0.0080109 | -0.020065 | -0.0084957 | -0.0062528 | -0.00090781 | 4.9132e-05 | -0.012298 | 0.15564 | 0.1831 | 0.18768 | 0.16479 | 0.28839 | 0.086975 | -0.059509 | 0.19684 | 0.2655 | 0.1236 | 0.21973 | 0.19226 | 0.004578 | -0.059509 | 122.7356 | 122.5891 | 0.13275 | 122.8317 | 122.8134 | 0.2243 | 0 | 122.6532 | 122.5891 | 0.064087 | 122.8455 | 122.7722 | 0.1831 | 0.036621 | 122.937 | 122.8043 | 122.8363 | -0.21515 | 122.8683 | 122.8409 | 122.9141 | -0.21515
1829.6562 | 122.9004 | -122.699 | 0.18768 | 0.16724 | 0.023178 | 0.0035888 | 0.0023413 | -0.0047658 | 0.00029262 | -0.0054475 | 0.17067 | -0.0063595 | -0.0079618 | -0.00026701 | 0.0075259 | -0.012085 | 0.17853 | 0.14648 | 0.15106 | 0.12817 | 0.20142 | 0.050354 | -0.11902 | 0.17395 | 0.19226 | 0.054932 | 0.12817 | 0.10071 | -0.068665 | -0.10071 | 122.7493 | 122.58 | 0.013733 | 122.8455 | 122.8271 | 0.24719 | -0.009155 | 122.6303 | 122.5983 | -0.059509 | 122.8729 | 122.7539 | 0.15564 | -0.086975 | 122.9004 | 122.8775 | 122.85 | -0.3067 | 122.8271 | 122.7997 | 122.8912 | -0.28839
1831.3594 | 123.0011 | -122.6624 | 0.15106 | -0.13031 | 0.02446 | 0.0018798 | 0.0046911 | -0.009252 | 0.0037106 | -0.0033111 | -0.20317 | -0.0091367 | -0.0075344 | 0.00016019 | 0.0073123 | -0.013794 | 0.19684 | 0.13275 | 0.11444 | 0.13733 | 0.3067 | 0.07782 | -0.07782 | 0.14648 | 0.16479 | 0.018311 | 0.21515 | 0.20142 | -0.041199 | -0.10529 | 122.7402 | 122.5845 | 0.15564 | 122.7951 | 122.7997 | 0.21515 | 0.045776 | 122.6212 | 122.5571 | 0.064087 | 122.8088 | 122.6807 | 0.1236 | 0.050354 | 122.9691 | 122.8592 | 122.7768 | -0.22888 | 122.8775 | 122.8638 | 122.8271 | -0.25635
1833.0469 | 122.9736 | -122.6715 | 0.14648 | -0.22186 | 0.02446 | 0.0038024 | 0.0070409 | -0.0079702 | -0.0014164 | -0.0058747 | -0.23369 | -0.011487 | -0.0039028 | -0.0021896 | 0.0017581 | -0.0099484 | 0.21973 | 0.26093 | 0.22888 | 0.20142 | 0.32959 | 0.11902 | -0.013733 | 0.19226 | 0.2655 | 0.10529 | 0.23804 | 0.24261 | 0.004578 | -0.041199 | 122.7905 | 122.6578 | 0.18311 | 122.9324 | 122.8729 | 0.21515 | 0.073243 | 122.6761 | 122.6303 | 0.091553 | 122.8638 | 122.7768 | 0.14649 | 0.096131 | 123.0011 | 122.8912 | 122.9004 | -0.16022 | 122.9095 | 122.9141 | 122.937 | -0.18768
1834.7188 | 122.8912 | -122.6898 | 0.17395 | 0.17487 | 0.019974 | 0.0038024 | 0.0025549 | -0.0049796 | 0.00050622 | -0.0013885 | 0.1783 | -0.0099911 | -0.004971 | -0.0017624 | 0.0060305 | -0.01123 | 0.14191 | 0.16479 | 0.16479 | 0.10986 | 0.20142 | 0.041199 | -0.1236 | 0.16937 | 0.20142 | 0.073242 | 0.12817 | 0.10529 | -0.054932 | -0.10529 | 122.731 | 122.5662 | 0.027466 | 122.8546 | 122.7997 | 0.23346 | -0.032043 | 122.6349 | 122.5845 | -0.045776 | 122.8592 | 122.7631 | 0.17853 | -0.068664 | 122.8912 | 122.8317 | 122.8546 | -0.29755 | 122.818 | 122.7951 | 122.8912 | -0.27924
1836.4219 | 122.8821 | -122.699 | 0.18768 | 0.075684 | 0.019547 | 0.0061524 | 0.0023413 | -0.0081838 | -0.0031254 | -0.0054475 | 0.094375 | -0.010418 | -0.007748 | -0.0024032 | 0.0017581 | -0.011017 | 0.15106 | 0.17395 | 0.15564 | 0.12817 | 0.26093 | 0.068665 | -0.07782 | 0.16022 | 0.20599 | 0.091553 | 0.18768 | 0.17395 | -0.004578 | -0.086975 | 122.7676 | 122.6212 | 0.073242 | 122.8729 | 122.8271 | 0.20599 | -0.036621 | 122.6944 | 122.612 | 0 | 122.8592 | 122.7905 | 0.17853 | -0.013733 | 122.9599 | 122.85 | 122.8546 | -0.2655 | 122.8867 | 122.8729 | 122.905 | -0.27466
1838.1406 | 122.9095 | -122.6761 | 0.16479 | -0.038757 | 0.02446 | 0.0044434 | 0.0031957 | -0.0062612 | 0.007983 | -0.0048065 | -0.10399 | -0.0074277 | -0.0071072 | -0.00069421 | 0.0081667 | -0.012512 | 0.1831 | 0.1236 | 0.09613 | 0.11902 | 0.3067 | 0.059509 | -0.091553 | 0.1236 | 0.11902 | -0.032043 | 0.21057 | 0.16937 | -0.064087 | -0.11444 | 122.7356 | 122.5845 | 0.14191 | 122.7997 | 122.7951 | 0.21057 | 0.01831 | 122.612 | 122.5616 | 0.045776 | 122.7997 | 122.644 | 0.082398 | 0.004578 | 122.9828 | 122.8592 | 122.7722 | -0.25635 | 122.8867 | 122.8455 | 122.7951 | -0.27924
1839.8281 | 122.9691 | -122.6852 | 0.14191 | -0.23712 | 0.02446 | 0.0038024 | 0.0083227 | -0.0049796 | -0.0012028 | -0.0069427 | -0.24132 | -0.010846 | -0.0041164 | -0.0015488 | 0.0013309 | -0.0097348 | 0.19226 | 0.2243 | 0.20142 | 0.19684 | 0.3479 | 0.1236 | -0.036621 | 0.15564 | 0.21515 | 0.073242 | 0.27466 | 0.22888 | 0 | -0.064087 | 122.8088 | 122.6486 | 0.20599 | 122.9095 | 122.8821 | 0.23346 | 0.050354 | 122.6852 | 122.6212 | 0.13275 | 122.8409 | 122.7585 | 0.13733 | 0.086975 | 123.0331 | 122.8775 | 122.8867 | -0.17853 | 122.9599 | 122.9141 | 122.9004 | -0.20599
1841.5312 | 122.9691 | -122.6578 | 0.15564 | -0.17609 | 0.020401 | 0.0052978 | 0.0087499 | -0.0066884 | -0.0046206 | -0.0056611 | -0.16502 | -0.010205 | -0.004971 | -0.0015488 | 0.0023989 | -0.011444 | 0.23804 | 0.31586 | 0.27008 | 0.2243 | 0.31586 | 0.12817 | -0.018311 | 0.21973 | 0.31586 | 0.16022 | 0.21515 | 0.19226 | 0.032043 | -0.032043 | 122.7859 | 122.6395 | 0.16022 | 122.9736 | 122.8821 | 0.24261 | 0.082397 | 122.6898 | 122.6257 | 0.059509 | 122.8775 | 122.818 | 0.19226 | 0.036621 | 122.9736 | 122.8958 | 122.9279 | -0.17395 | 122.8729 | 122.85 | 122.9736 | -0.18768
1843.2188 | 122.905 | -122.6898 | 0.18768 | 0.17487 | 0.022537 | 0.0040162 | 0.0027685 | -0.0064748 | -0.0012028 | -0.0045929 | 0.13252 | -0.0076413 | -0.0071072 | -0.0011216 | 0.0047489 | -0.011657 | 0.14648 | 0.1831 | 0.17395 | 0.11902 | 0.19684 | 0.036621 | -0.12817 | 0.16479 | 0.19684 | 0.086975 | 0.16022 | 0.11444 | -0.045776 | -0.086975 | 122.7264 | 122.5616 | 0.009155 | 122.8729 | 122.8088 | 0.24719 | -0.041199 | 122.644 | 122.6028 | -0.027466 | 122.8546 | 122.7768 | 0.17395 | -0.073242 | 122.8867 | 122.8363 | 122.8638 | -0.31586 | 122.85 | 122.8043 | 122.8867 | -0.27466
1844.9531 | 123.0148 | -122.6395 | 0.14191 | -0.099793 | 0.022537 | 0.008075 | 0.0091773 | -0.0047658 | -0.0052616 | -0.0063019 | -0.073471 | -0.010846 | -0.0043302 | -0.0032578 | 0.0034671 | -0.011017 | 0.23346 | 0.28839 | 0.27008 | 0.21973 | 0.29755 | 0.13733 | -0.018311 | 0.24719 | 0.34332 | 0.17395 | 0.25635 | 0.19226 | 0.022888 | -0.013733 | 122.7768 | 122.6212 | 0.15564 | 122.9279 | 122.8592 | 0.23804 | 0.091552 | 122.6624 | 122.6257 | 0.11444 | 122.8867 | 122.8134 | 0.18768 | 0.050354 | 122.937 | 122.8729 | 122.9095 | -0.16022 | 122.8958 | 122.8317 | 122.9828 | -0.15564
1846.6406 | 122.937 | -122.6852 | 0.17853 | 0.098572 | 0.021896 | 0.0042298 | 0.0038367 | -0.0054068 | 0.0028562 | -0.0058747 | 0.094375 | -0.0070003 | -0.0073208 | -0.0011216 | 0.0075259 | -0.013794 | 0.09613 | 0.054932 | 0.022888 | 0.054932 | 0.27008 | 0.022888 | -0.1236 | 0.10071 | 0.082397 | -0.027466 | 0.17853 | 0.14648 | -0.068665 | -0.11444 | 122.7081 | 122.5616 | 0.091553 | 122.7402 | 122.7402 | 0.17853 | -0.082398 | 122.6166 | 122.5708 | 0 | 122.7859 | 122.6578 | 0.086975 | -0.032044 | 122.9553 | 122.7814 | 122.7081 | -0.30212 | 122.8638 | 122.8317 | 122.7676 | -0.29297
1848.3125 | 123.056 | -122.6486 | 0.15564 | -0.16083 | 0.024887 | 0.0027344 | 0.0072547 | -0.0079702 | 0.0028562 | -0.0045929 | -0.25658 | -0.0067867 | -0.0051846 | -0.00026701 | 0.0041079 | -0.012298 | 0.1831 | 0.13275 | 0.1236 | 0.14191 | 0.35248 | 0.091553 | -0.064087 | 0.13275 | 0.16937 | 0.022888 | 0.26093 | 0.23346 | -0.027466 | -0.07782 | 122.7402 | 122.5845 | 0.19684 | 122.7814 | 122.7905 | 0.20599 | 0.027465 | 122.6212 | 122.5708 | 0.10529 | 122.7814 | 122.6715 | 0.10071 | 0.077819 | 123.0011 | 122.8317 | 122.7722 | -0.21973 | 122.9095 | 122.8821 | 122.818 | -0.23346
1850.0469 | 123.024 | -122.6578 | 0.13733 | -0.14557 | 0.021683 | 0.0025208 | 0.0081091 | -0.0049796 | -0.005048 | -0.0071563 | -0.027695 | -0.01405 | -0.0041164 | -0.0011216 | 4.9132e-05 | -0.0086666 | 0.24261 | 0.31128 | 0.25635 | 0.21515 | 0.30212 | 0.13275 | 0.004578 | 0.27008 | 0.35706 | 0.21057 | 0.23346 | 0.18768 | 0.027466 | -0.032043 | 122.7905 | 122.6624 | 0.16479 | 122.9691 | 122.8729 | 0.21057 | 0.10529 | 122.6852 | 122.6257 | 0.09613 | 122.9279 | 122.8683 | 0.24261 | 0.050354 | 122.9599 | 122.9004 | 122.9141 | -0.13275 | 122.8912 | 122.8455 | 123.0148 | -0.16937
1851.7344 | 122.8912 | -122.699 | 0.18768 | 0.12909 | 0.020828 | 0.004657 | 0.0042639 | -0.007543 | -0.00056178 | -0.0048065 | 0.11726 | -0.0084957 | -0.0073208 | -0.0015488 | 0.0053897 | -0.01123 | 0.17853 | 0.16937 | 0.16022 | 0.11902 | 0.21515 | 0.041199 | -0.09613 | 0.17395 | 0.18768 | 0.07782 | 0.15106 | 0.12817 | -0.018311 | -0.10986 | 122.7402 | 122.6028 | 0.027466 | 122.8683 | 122.818 | 0.21515 | -0.009155 | 122.6807 | 122.5891 | -0.036621 | 122.8729 | 122.7768 | 0.18768 | -0.059509 | 122.9141 | 122.8775 | 122.8592 | -0.28381 | 122.85 | 122.8271 | 122.8867 | -0.29755
1853.4219 | 122.937 | -122.6852 | 0.15106 | 0.16724 | 0.026169 | 0.0025208 | 0.0019141 | -0.005834 | 0.00093342 | -0.0048065 | 0.10963 | -0.0082821 | -0.007748 | 0.0010148 | 0.0056033 | -0.014007 | 0.17395 | 0.15106 | 0.13275 | 0.11902 | 0.21973 | 0.059509 | -0.09613 | 0.16937 | 0.19226 | 0.068665 | 0.13733 | 0.10986 | -0.064087 | -0.10986 | 122.7448 | 122.5891 | 0.068665 | 122.8363 | 122.8043 | 0.21515 | 0.022888 | 122.6212 | 122.5754 | -0.013733 | 122.8546 | 122.7539 | 0.17853 | -0.041199 | 122.905 | 122.8592 | 122.818 | -0.24719 | 122.8226 | 122.7951 | 122.8775 | -0.26093
1855.1094 | 122.9965 | -122.6669 | 0.16479 | -0.19897 | 0.021896 | 0.0044434 | 0.0055457 | -0.0066884 | -0.0012028 | -0.0054475 | -0.24132 | -0.0091367 | -0.0051846 | 0.0029374 | 0.0013309 | -0.010376 | 0.17395 | 0.16022 | 0.14191 | 0.13733 | 0.35248 | 0.10986 | -0.050354 | 0.14191 | 0.17853 | 0.041199 | 0.27924 | 0.26093 | -0.022888 | -0.059509 | 122.7768 | 122.6166 | 0.18768 | 122.8271 | 122.8043 | 0.18768 | 0.009155 | 122.644 | 122.6074 | 0.11444 | 122.8088 | 122.7081 | 0.10071 | 0.09613 | 123.0194 | 122.8409 | 122.8088 | -0.21515 | 122.9462 | 122.9279 | 122.8455 | -0.2243
1856.8281 | 123.0011 | -122.6532 | 0.15106 | -0.13794 | 0.021256 | 0.0050842 | 0.0089635 | -0.007543 | -0.0024844 | -0.0067291 | -0.12688 | -0.011059 | -0.0041164 | -0.0015488 | 0.0021853 | -0.012298 | 0.26093 | 0.31586 | 0.25635 | 0.24719 | 0.32501 | 0.13275 | -0.022888 | 0.25177 | 0.3479 | 0.18768 | 0.21973 | 0.21057 | 0.027466 | -0.018311 | 122.7859 | 122.6303 | 0.17395 | 122.9691 | 122.9004 | 0.27008 | 0.10986 | 122.6807 | 122.6349 | 0.068665 | 122.905 | 122.8409 | 0.20599 | 0.059509 | 122.9782 | 122.9141 | 122.9095 | -0.17395 | 122.8729 | 122.8638 | 123.0011 | -0.16937
1858.5 | 122.905 | -122.6669 | 0.1831 | 0.098572 | 0.023178 | 0.0059388 | 0.0038367 | -0.0090384 | 0.0043514 | -0.0048065 | 0.048599 | -0.0070003 | -0.00668 | -0.00026701 | 0.0073123 | -0.011871 | 0.07782 | 0.009155 | 0.027466 | 0.045776 | 0.27008 | 0.045776 | -0.1236 | 0.064087 | 0.032043 | -0.064087 | 0.19226 | 0.15564 | -0.073242 | -0.14648 | 122.7127 | 122.5433 | 0.086976 | 122.6761 | 122.7127 | 0.16937 | -0.10528 | 122.5937 | 122.5204 | 0.009156 | 122.731 | 122.6028 | 0.082397 | -0.027465 | 122.937 | 122.7448 | 122.6944 | -0.3067 | 122.8592 | 122.8226 | 122.699 | -0.32959
1860.2188 | 123.0148 | -122.6944 | 0.15564 | -0.26001 | 0.020615 | 0.0061524 | 0.0059729 | -0.004125 | -0.00034818 | -0.0033111 | -0.24895 | -0.0067867 | -0.0062528 | -0.0024032 | 0.0058169 | -0.012512 | 0.1831 | 0.16937 | 0.12817 | 0.16022 | 0.38452 | 0.1236 | -0.041199 | 0.13733 | 0.16022 | 0.036621 | 0.28839 | 0.24719 | -0.004578 | -0.059509 | 122.818 | 122.6532 | 0.22888 | 122.8638 | 122.8546 | 0.20142 | 0.027465 | 122.6898 | 122.6349 | 0.13275 | 122.8317 | 122.731 | 0.09613 | 0.091552 | 123.0789 | 122.8775 | 122.8226 | -0.19684 | 122.9828 | 122.9416 | 122.8546 | -0.21515
1861.9062 | 123.0148 | -122.6715 | 0.15106 | -0.099793 | 0.023819 | 0.0050842 | 0.0076819 | -0.0066884 | -0.0041934 | -0.0037385 | -0.14977 | -0.011273 | -0.003262 | -0.0030442 | 0.00026273 | -0.013794 | 0.23804 | 0.31586 | 0.2655 | 0.23804 | 0.29755 | 0.14648 | -0.009155 | 0.24719 | 0.33875 | 0.17395 | 0.22888 | 0.19226 | 0.041199 | -0.004578 | 122.818 | 122.6624 | 0.14648 | 122.9874 | 122.9095 | 0.24719 | 0.086975 | 122.7127 | 122.6669 | 0.07782 | 122.9187 | 122.8455 | 0.17853 | 0.041199 | 122.9691 | 122.9095 | 122.937 | -0.16022 | 122.9004 | 122.8638 | 123.0103 | -0.15564
1863.6094 | 122.905 | -122.7173 | 0.19684 | 0.083313 | 0.025101 | 0.002948 | 0.0031957 | -0.004125 | 0.0037106 | -0.0043793 | 0.010452 | -0.0082821 | -0.0068936 | 0.00037379 | 0.0047489 | -0.014007 | 0.091553 | 0.018311 | 0.018311 | 0.050354 | 0.27008 | 0.018311 | -0.1236 | 0.059509 | 0.054932 | -0.064087 | 0.20599 | 0.15106 | -0.068665 | -0.14648 | 122.7356 | 122.5937 | 0.073243 | 122.7356 | 122.7676 | 0.17395 | -0.10529 | 122.6486 | 122.5708 | 0.009156 | 122.7768 | 122.6532 | 0.082397 | -0.045776 | 122.9874 | 122.8088 | 122.7356 | -0.32043 | 122.9233 | 122.8683 | 122.7722 | -0.34332
1865.3281 | 122.9004 | -122.7036 | 0.17395 | 0.0070193 | 0.024887 | 0.0033752 | 0.0040503 | -0.0060476 | 0.0037106 | -0.0022431 | 0.025711 | -0.0082821 | -0.0039028 | -0.00090781 | 0.0064577 | -0.012085 | 0.086975 | 0.068665 | 0.050354 | 0.064087 | 0.2655 | 0.041199 | -0.13275 | 0.045776 | 0.073242 | -0.07782 | 0.20142 | 0.18768 | -0.073242 | -0.13275 | 122.7448 | 122.5708 | 0.091553 | 122.7722 | 122.7676 | 0.19684 | -0.086975 | 122.6303 | 122.5708 | 0.027466 | 122.7493 | 122.6257 | 0.054931 | 0.013733 | 122.9691 | 122.7905 | 122.7539 | -0.3067 | 122.905 | 122.8912 | 122.7768 | -0.3067
1867.0156 | 123.0194 | -122.6624 | 0.14648 | -0.13794 | 0.023605 | 0.0044434 | 0.0072547 | -0.0064748 | -0.0076114 | -0.0060883 | -0.020065 | -0.012768 | -0.0030484 | 0.0012284 | -0.0014463 | -0.0086666 | 0.20599 | 0.29755 | 0.26093 | 0.21973 | 0.3067 | 0.13733 | -0.004578 | 0.2655 | 0.32959 | 0.21515 | 0.2243 | 0.1831 | 0.041199 | -0.022888 | 122.7997 | 122.6578 | 0.16022 | 122.9599 | 122.8821 | 0.22431 | 0.05951 | 122.7036 | 122.6395 | 0.07782 | 122.9279 | 122.8775 | 0.23804 | 0.036621 | 122.9691 | 122.8683 | 122.9233 | -0.15106 | 122.8867 | 122.8455 | 122.9919 | -0.16937
1868.7344 | 122.9736 | -122.6715 | 0.16022 | -0.17609 | 0.022965 | 0.004657 | 0.0072547 | -0.0054068 | -0.0022708 | -0.0052337 | -0.13451 | -0.010846 | -0.0053982 | -5.3406e-05 | 0.00090353 | -0.01358 | 0.23346 | 0.27008 | 0.23804 | 0.21057 | 0.31586 | 0.14648 | -0.022888 | 0.21515 | 0.30212 | 0.15106 | 0.24261 | 0.17853 | 0.009155 | -0.036621 | 122.818 | 122.6486 | 0.15564 | 122.9416 | 122.8821 | 0.23346 | 0.073242 | 122.6807 | 122.6349 | 0.082398 | 122.8867 | 122.8226 | 0.18768 | 0.018311 | 122.9874 | 122.905 | 122.9095 | -0.1831 | 122.9141 | 122.85 | 122.9736 | -0.19684
1870.4531 | 123.0103 | -122.6257 | 0.15564 | -0.16083 | 0.021042 | 0.0038024 | 0.0081091 | -0.0066884 | -0.0031254 | -0.0063019 | -0.027695 | -0.010846 | -0.0056118 | -0.00026701 | 0.00047633 | -0.011871 | 0.24261 | 0.29297 | 0.25635 | 0.22888 | 0.31128 | 0.1236 | -0.009155 | 0.26093 | 0.32044 | 0.20599 | 0.2243 | 0.19226 | 0.032043 | -0.032043 | 122.7493 | 122.6166 | 0.15564 | 122.9187 | 122.8546 | 0.23804 | 0.086975 | 122.6578 | 122.5937 | 0.068664 | 122.8867 | 122.8317 | 0.23804 | 0.036621 | 122.937 | 122.8683 | 122.8821 | -0.16479 | 122.85 | 122.818 | 122.9462 | -0.18768
1872.1562 | 123.024 | -122.6669 | 0.14191 | -0.19897 | 0.024887 | 0.0040162 | 0.0040503 | -0.005834 | 0.0041378 | -0.0016021 | -0.22606 | -0.0087093 | -0.008389 | 0.0027236 | 0.0062441 | -0.015289 | 0.20142 | 0.14648 | 0.12817 | 0.15564 | 0.33875 | 0.10071 | -0.082397 | 0.13275 | 0.16937 | 0.027466 | 0.23346 | 0.20599 | -0.018311 | -0.091553 | 122.7676 | 122.5845 | 0.19684 | 122.8134 | 122.8226 | 0.23804 | 0.059509 | 122.6486 | 122.5754 | 0.091552 | 122.7997 | 122.6944 | 0.11902 | 0.064087 | 123.0057 | 122.8683 | 122.7951 | -0.2243 | 122.9004 | 122.8729 | 122.8363 | -0.23346
1873.8438 | 122.8867 | -122.6852 | 0.17395 | 0.029907 | 0.023819 | 0.0050842 | 0.0025549 | -0.0047658 | 0.0032834 | -0.0054475 | 0.018082 | -0.0063595 | -0.0062528 | -0.0017624 | 0.0077395 | -0.011871 | 0.09613 | 0.068665 | 0.041199 | 0.07782 | 0.26093 | 0.041199 | -0.10986 | 0.045776 | 0.068665 | -0.073242 | 0.19684 | 0.17395 | -0.073242 | -0.13733 | 122.7264 | 122.5754 | 0.086975 | 122.7539 | 122.7631 | 0.18768 | -0.07782 | 122.612 | 122.5479 | 0.022888 | 122.731 | 122.612 | 0.064087 | 0 | 122.9462 | 122.7814 | 122.7264 | -0.28381 | 122.8821 | 122.8592 | 122.7539 | -0.31128
1875.5312 | 122.9828 | -122.6807 | 0.15106 | -0.21423 | 0.023819 | 0.0038024 | 0.0076819 | -0.0036978 | -0.0024844 | -0.0052337 | -0.21843 | -0.0087093 | -0.0030484 | -0.0017624 | 0.0011173 | -0.009094 | 0.14191 | 0.16937 | 0.14191 | 0.16022 | 0.35706 | 0.11444 | -0.041199 | 0.12817 | 0.1831 | 0.041199 | 0.28839 | 0.24261 | -0.022888 | -0.059509 | 122.7951 | 122.6395 | 0.20599 | 122.85 | 122.8409 | 0.20142 | -0.009155 | 122.6578 | 122.6212 | 0.13733 | 122.8088 | 122.7219 | 0.10071 | 0.091553 | 123.0377 | 122.8226 | 122.8226 | -0.19226 | 122.9691 | 122.9233 | 122.8638 | -0.21057
1877.2188 | 123.0057 | -122.6578 | 0.14648 | -0.17609 | 0.018265 | -0.0028198 | 0.0038367 | -0.0066884 | -0.0071842 | -0.0073701 | -0.012436 | -0.010205 | -0.008389 | -0.0024032 | 0.0026125 | -0.0097348 | 0.22888 | 0.29755 | 0.23346 | 0.21515 | 0.31128 | 0.10986 | -0.009155 | 0.24719 | 0.31586 | 0.20142 | 0.23346 | 0.19226 | 0.032043 | -0.032043 | 122.7676 | 122.6486 | 0.16479 | 122.9553 | 122.8729 | 0.2243 | 0.082398 | 122.6898 | 122.6257 | 0.086975 | 122.905 | 122.8592 | 0.23346 | 0.045777 | 122.9691 | 122.8867 | 122.8912 | -0.15564 | 122.8912 | 122.85 | 122.9736 | -0.17853
1878.9375 | 122.9965 | -122.6669 | 0.15106 | -0.16083 | 0.023819 | 0.002948 | 0.0076819 | -0.0077566 | -0.00098918 | -0.0086517 | -0.26421 | -0.0072141 | -0.0036892 | 0.0010148 | 0.0021853 | -0.010803 | 0.16479 | 0.17853 | 0.13733 | 0.16479 | 0.37079 | 0.10986 | -0.032043 | 0.11902 | 0.16479 | 0.050354 | 0.28839 | 0.25177 | 0 | -0.068665 | 122.7768 | 122.6349 | 0.21973 | 122.8455 | 122.8317 | 0.19684 | 0.013733 | 122.6669 | 122.5983 | 0.13733 | 122.7859 | 122.7173 | 0.11902 | 0.10071 | 123.0377 | 122.8317 | 122.8043 | -0.18311 | 122.9553 | 122.9187 | 122.8317 | -0.21973
1880.625 | 122.9599 | -122.6898 | 0.16479 | 0.014648 | 0.023392 | 0.0055114 | 0.0068273 | -0.0051932 | -0.0031254 | -0.0058747 | 0.063858 | -0.010205 | -0.003262 | -5.3406e-05 | 0.0030399 | -0.010376 | 0.12817 | 0.16022 | 0.16937 | 0.15564 | 0.27924 | 0.091553 | -0.059509 | 0.16479 | 0.21057 | 0.10529 | 0.20599 | 0.1831 | -0.013733 | -0.064087 | 122.7814 | 122.6303 | 0.11444 | 122.85 | 122.8455 | 0.21515 | -0.036621 | 122.6761 | 122.6257 | 0.041199 | 122.8546 | 122.7951 | 0.16937 | 0.01831 | 122.9691 | 122.818 | 122.8592 | -0.2243 | 122.8958 | 122.8729 | 122.9004 | -0.22888
1882.3125 | 122.9462 | -122.6944 | 0.17395 | 0.15198 | 0.02446 | 0.0040162 | 0.0017005 | -0.0054068 | 0.0049924 | -0.0054475 | 0.056228 | -0.0099911 | -0.0056118 | -0.0017624 | 0.0064577 | -0.011444 | 0.09613 | 0.041199 | 0.027466 | 0.054932 | 0.27924 | 0.013733 | -0.11902 | 0.082397 | 0.054932 | -0.036621 | 0.21057 | 0.17395 | -0.064087 | -0.1236 | 122.7081 | 122.5754 | 0.10529 | 122.7356 | 122.7493 | 0.17395 | -0.07782 | 122.6303 | 122.5708 | 0.036621 | 122.7768 | 122.6578 | 0.086975 | 0 | 122.9736 | 122.7905 | 122.7219 | -0.29297 | 122.905 | 122.8683 | 122.7493 | -0.29755
1884.0312 | 122.9828 | -122.6898 | 0.16479 | -0.17609 | 0.022751 | 0.004657 | 0.0081091 | -0.0064748 | -0.0048344 | -0.0056611 | -0.13451 | -0.0097775 | -0.0053982 | 0.00037379 | 0.0021853 | -0.011657 | 0.25177 | 0.27924 | 0.24719 | 0.22888 | 0.32044 | 0.15106 | -0.018311 | 0.22888 | 0.29297 | 0.14648 | 0.21515 | 0.19684 | 0.022888 | -0.045776 | 122.8409 | 122.6715 | 0.15564 | 122.9691 | 122.9187 | 0.24719 | 0.086975 | 122.7127 | 122.644 | 0.050354 | 122.9187 | 122.8363 | 0.19226 | 0.032043 | 123.0103 | 122.9416 | 122.937 | -0.18311 | 122.905 | 122.8867 | 122.9828 | -0.21057
1885.7188 | 123.024 | -122.6624 | 0.14191 | -0.0082397 | 0.018906 | 0.0048706 | 0.0055457 | -0.0051932 | -0.0059024 | -0.0054475 | 0.0028229 | -0.010418 | -0.0058254 | -0.0026168 | 0.0015445 | -0.011444 | 0.17395 | 0.19226 | 0.18768 | 0.18768 | 0.30212 | 0.11444 | -0.045776 | 0.21057 | 0.26093 | 0.15564 | 0.21515 | 0.20142 | 0.027466 | -0.022888 | 122.7768 | 122.6166 | 0.16022 | 122.8546 | 122.85 | 0.23346 | 0.032043 | 122.6898 | 122.6395 | 0.073242 | 122.8729 | 122.818 | 0.17853 | 0.059509 | 122.9645 | 122.8363 | 122.85 | -0.18768 | 122.8775 | 122.8638 | 122.9233 | -0.16479
1887.4219 | 122.9187 | -122.6852 | 0.17395 | 0.16724 | 0.023605 | 0.0044434 | 0.0036231 | -0.0069022 | 0.00050622 | -0.0058747 | 0.1783 | -0.0097775 | -0.00668 | -0.001976 | 0.0056033 | -0.014221 | 0.16022 | 0.16479 | 0.16022 | 0.11902 | 0.19684 | 0.045776 | -0.10529 | 0.16022 | 0.17853 | 0.050354 | 0.13733 | 0.09613 | -0.064087 | -0.10529 | 122.731 | 122.58 | 0.022888 | 122.85 | 122.8043 | 0.22431 | -0.013733 | 122.6212 | 122.58 | -0.036621 | 122.8455 | 122.7356 | 0.15564 | -0.07782 | 122.8821 | 122.8455 | 122.8455 | -0.27924 | 122.8226 | 122.7814 | 122.8638 | -0.27924
1889.1094 | 123.0103 | -122.6715 | 0.17853 | -0.076904 | 0.023819 | 0.00081179 | 0.0055457 | -0.0060476 | 0.0049924 | -0.0039521 | -0.16502 | -0.0087093 | -0.0064664 | 0.0010148 | 0.0058169 | -0.013366 | 0.2243 | 0.15564 | 0.11444 | 0.13733 | 0.30212 | 0.073242 | -0.082397 | 0.15106 | 0.15564 | 0.027466 | 0.21057 | 0.17853 | -0.041199 | -0.10071 | 122.7448 | 122.5891 | 0.1236 | 122.8271 | 122.8088 | 0.21973 | 0.045776 | 122.6303 | 122.5708 | 0.032043 | 122.8226 | 122.699 | 0.12817 | 0 | 122.9736 | 122.8958 | 122.7859 | -0.26092 | 122.8821 | 122.85 | 122.8271 | -0.27924
1890.7812 | 122.9919 | -122.6852 | 0.15564 | 0.014648 | 0.018265 | 0.0050842 | 0.0057593 | -0.0069022 | -0.005048 | -0.0069427 | 0.048599 | -0.0095639 | -0.0039028 | -0.00048061 | 0.0017581 | -0.009094 | 0.14191 | 0.16022 | 0.17853 | 0.16022 | 0.28839 | 0.09613 | -0.064087 | 0.19684 | 0.21973 | 0.12817 | 0.21057 | 0.18768 | 0.004578 | -0.064087 | 122.7814 | 122.6212 | 0.13275 | 122.8455 | 122.8455 | 0.2243 | -0.013733 | 122.6898 | 122.6212 | 0.054931 | 122.8821 | 122.8134 | 0.19226 | 0.032043 | 122.9736 | 122.8271 | 122.8638 | -0.21973 | 122.8958 | 122.8729 | 122.905 | -0.21973
1892.4688 | 123.0331 | -122.6669 | 0.16937 | -0.19135 | 0.022324 | 0.0042298 | 0.0046911 | -0.0034842 | 0.0026424 | -0.0039521 | -0.2108 | -0.0078549 | -0.0047574 | -0.0017624 | 0.0060305 | -0.01358 | 0.20142 | 0.16479 | 0.13275 | 0.14648 | 0.38452 | 0.082397 | -0.036621 | 0.13733 | 0.13733 | 0.013733 | 0.27466 | 0.20599 | -0.041199 | -0.082397 | 122.7493 | 122.6303 | 0.21515 | 122.8317 | 122.8134 | 0.18311 | 0.032043 | 122.6257 | 122.5845 | 0.10529 | 122.8043 | 122.6807 | 0.09613 | 0.036621 | 123.0515 | 122.8683 | 122.7997 | -0.20599 | 122.9416 | 122.8729 | 122.8043 | -0.25177
1894.1875 | 122.905 | -122.731 | 0.19684 | -0.0082397 | 0.024887 | 0.0050842 | 0.0023413 | -0.0071158 | 0.0041378 | -0.0035249 | 0.018082 | -0.0089229 | -0.0045438 | -0.0026168 | 0.0079531 | -0.014648 | 0.11902 | 0.064087 | 0.054932 | 0.068665 | 0.28381 | 0.032043 | -0.11902 | 0.059509 | 0.068665 | -0.064087 | 0.20142 | 0.16937 | -0.064087 | -0.13275 | 122.7631 | 122.612 | 0.086975 | 122.7951 | 122.7997 | 0.18768 | -0.077819 | 122.6669 | 122.5983 | 0.004578 | 122.7905 | 122.6669 | 0.068664 | -0.027465 | 123.0148 | 122.85 | 122.7859 | -0.31586 | 122.9324 | 122.9004 | 122.7997 | -0.32959
1895.875 | 122.9965 | -122.6852 | 0.16479 | -0.18372 | 0.027237 | 0.0044434 | 0.010459 | -0.0069022 | -0.00056178 | -0.0071563 | -0.22606 | -0.010205 | -0.0056118 | -0.00048061 | 0.0019717 | -0.010803 | 0.16479 | 0.16022 | 0.15106 | 0.15564 | 0.36621 | 0.10071 | -0.041199 | 0.11902 | 0.16479 | 0.054932 | 0.29297 | 0.24719 | -0.013733 | -0.041199 | 122.7859 | 122.644 | 0.20142 | 122.8455 | 122.8409 | 0.19684 | 0 | 122.6715 | 122.644 | 0.12817 | 122.8043 | 122.7402 | 0.096131 | 0.082397 | 123.0515 | 122.85 | 122.8363 | -0.20599 | 122.9782 | 122.9324 | 122.85 | -0.20599
1897.5625 | 122.9553 | -122.6944 | 0.17853 | 0.045166 | 0.021896 | 0.0055114 | 0.0027685 | -0.007543 | -0.0031254 | -0.0065155 | 0.086746 | -0.0087093 | -0.003262 | -0.0013352 | 0.0032535 | -0.0097348 | 0.14191 | 0.16479 | 0.15564 | 0.14648 | 0.29297 | 0.082397 | -0.068665 | 0.13733 | 0.20142 | 0.10529 | 0.21973 | 0.19684 | -0.022888 | -0.064087 | 122.7768 | 122.6257 | 0.11444 | 122.8592 | 122.8409 | 0.21515 | -0.036621 | 122.6715 | 122.6303 | 0.041199 | 122.8317 | 122.7997 | 0.16937 | 0.01831 | 122.9874 | 122.8363 | 122.85 | -0.24719 | 122.9141 | 122.8912 | 122.8958 | -0.24261
1899.25 | 122.9462 | -122.6944 | 0.17853 | 0.17487 | 0.02446 | 0.0031616 | 0.0036231 | -0.0062612 | 0.0013608 | -0.0056611 | 0.102 | -0.0093503 | -0.007748 | -0.00048061 | 0.0062441 | -0.014221 | 0.13733 | 0.10071 | 0.091553 | 0.09613 | 0.23804 | 0.032043 | -0.11902 | 0.16937 | 0.1831 | 0.064087 | 0.15106 | 0.1236 | -0.018311 | -0.086975 | 122.7264 | 122.5754 | 0.059509 | 122.7951 | 122.7905 | 0.21515 | -0.041199 | 122.6761 | 122.6074 | -0.027466 | 122.8638 | 122.7585 | 0.15106 | -0.054932 | 122.9324 | 122.8317 | 122.7859 | -0.29755 | 122.8455 | 122.818 | 122.8775 | -0.2655
1900.9844 | 122.9507 | -122.6898 | 0.16937 | 0.13672 | 0.022751 | 0.0033752 | 0.0012731 | -0.007543 | 0.0015744 | -0.0054475 | 0.1783 | -0.0082821 | -0.0053982 | -0.0030442 | 0.0064577 | -0.012085 | 0.15564 | 0.15106 | 0.14191 | 0.14191 | 0.22888 | 0.050354 | -0.10986 | 0.16937 | 0.17395 | 0.064087 | 0.14191 | 0.12817 | -0.036621 | -0.10071 | 122.7402 | 122.58 | 0.059509 | 122.8409 | 122.8317 | 0.25177 | -0.013733 | 122.6532 | 122.5891 | -0.027466 | 122.8592 | 122.7539 | 0.1648 | -0.041199 | 122.9187 | 122.8455 | 122.8317 | -0.27924 | 122.8317 | 122.818 | 122.8638 | -0.27008
1902.6562 | 123.024 | -122.6578 | 0.15564 | -0.13794 | 0.025742 | 0.0035888 | 0.0070409 | -0.0047658 | 0.0020016 | -0.0045929 | -0.11925 | -0.0074277 | -0.004971 | 0.00058739 | 0.0045351 | -0.013153 | 0.20142 | 0.13275 | 0.11902 | 0.16022 | 0.32959 | 0.068665 | -0.07782 | 0.13275 | 0.15564 | 0.018311 | 0.23804 | 0.21057 | -0.032043 | -0.10986 | 122.7264 | 122.58 | 0.17395 | 122.7905 | 122.818 | 0.23804 | 0.045776 | 122.6257 | 122.5479 | 0.082397 | 122.7905 | 122.6761 | 0.12817 | 0.054931 | 122.9874 | 122.8592 | 122.7768 | -0.23346 | 122.8958 | 122.8683 | 122.8134 | -0.2655
1904.3438 | 123.0194 | -122.6578 | 0.14191 | -0.061646 | 0.02211 | 0.0055114 | 0.0078955 | -0.0064748 | -0.0059024 | -0.0058747 | 0.03334 | -0.0117 | -0.0028348 | 0.00037379 | 0.00068993 | -0.014007 | 0.1831 | 0.21057 | 0.20599 | 0.18768 | 0.30212 | 0.11444 | -0.054932 | 0.23346 | 0.28839 | 0.17853 | 0.2243 | 0.19684 | 0.022888 | -0.032043 | 122.7722 | 122.6028 | 0.16022 | 122.8683 | 122.8455 | 0.24261 | 0.041198 | 122.6807 | 122.6257 | 0.082397 | 122.8912 | 122.8363 | 0.21057 | 0.054931 | 122.9599 | 122.8409 | 122.8638 | -0.19684 | 122.8821 | 122.8546 | 122.9462 | -0.17395
1906.0469 | 122.9004 | -122.7219 | 0.17395 | 0.11383 | 0.018265 | 0.0048706 | 0.0046911 | -0.0062612 | -0.0039798 | -0.0073701 | 0.13252 | -0.011059 | -0.0086026 | -0.001976 | 0.0023989 | -0.013794 | 0.16022 | 0.16937 | 0.16937 | 0.1236 | 0.25635 | 0.064087 | -0.068665 | 0.16022 | 0.17395 | 0.086975 | 0.20599 | 0.16937 | 0.009155 | -0.073242 | 122.7859 | 122.6532 | 0.082398 | 122.8912 | 122.8455 | 0.19226 | -0.013733 | 122.731 | 122.6486 | 0.032044 | 122.8821 | 122.8088 | 0.16022 | -0.004577 | 122.9782 | 122.8821 | 122.8912 | -0.24261 | 122.9279 | 122.8912 | 122.8958 | -0.24719
1907.7344 | 123.0377 | -122.6624 | 0.14191 | -0.16846 | 0.021469 | 0.0023072 | 0.0057593 | -0.0073294 | 0.0049924 | -0.0095063 | -0.20317 | -0.0074277 | -0.004971 | 0.0012284 | 0.0047489 | -0.014862 | 0.20142 | 0.14191 | 0.10986 | 0.15106 | 0.35248 | 0.10071 | -0.059509 | 0.13275 | 0.15106 | 0.032043 | 0.24261 | 0.20142 | -0.041199 | -0.10071 | 122.7631 | 122.6028 | 0.21057 | 122.8043 | 122.8134 | 0.21057 | 0.059509 | 122.6212 | 122.5616 | 0.10071 | 122.7951 | 122.6944 | 0.13275 | 0.059509 | 123.0148 | 122.8638 | 122.7722 | -0.20142 | 122.905 | 122.8638 | 122.8134 | -0.24262
1909.4531 | 123.0011 | -122.6898 | 0.16937 | -0.092163 | 0.02211 | 0.001239 | 0.0061865 | -0.009252 | 0.0043514 | -0.0030975 | -0.16502 | -0.0078549 | -0.0064664 | 0.001442 | 0.0058169 | -0.012939 | 0.19226 | 0.15106 | 0.10529 | 0.14648 | 0.30212 | 0.07782 | -0.086975 | 0.15564 | 0.15564 | 0.013733 | 0.21973 | 0.19226 | -0.032043 | -0.10071 | 122.7676 | 122.6028 | 0.13275 | 122.8409 | 122.8363 | 0.23346 | 0.022888 | 122.6578 | 122.5891 | 0.050354 | 122.8455 | 122.7036 | 0.11444 | 0.022888 | 122.9919 | 122.8821 | 122.7951 | -0.25635 | 122.9095 | 122.8821 | 122.8455 | -0.27008
1911.1719 | 123.0103 | -122.6669 | 0.16022 | -0.22186 | 0.022537 | 0.0033752 | 0.0061865 | -0.008611 | -0.0029118 | -0.0054475 | -0.24132 | -0.0091367 | -0.0047574 | 0.0016556 | 0.0028263 | -0.010589 | 0.16479 | 0.15564 | 0.13733 | 0.16022 | 0.36621 | 0.10529 | -0.032043 | 0.1236 | 0.16479 | 0.036621 | 0.30212 | 0.2655 | -0.013733 | -0.064087 | 122.7722 | 122.6349 | 0.20599 | 122.8226 | 122.8271 | 0.19226 | 0.004578 | 122.6532 | 122.6028 | 0.14191 | 122.7905 | 122.7036 | 0.10071 | 0.10529 | 123.0331 | 122.8317 | 122.8043 | -0.19226 | 122.9691 | 122.9324 | 122.8317 | -0.2243
1912.8594 | 122.905 | -122.7173 | 0.17853 | 0.13672 | 0.02446 | 0.0040162 | 0.0019141 | -0.0049796 | -0.005048 | -0.0058747 | 0.19356 | -0.012555 | -0.0053982 | -0.0015488 | 0.0045351 | -0.0097348 | 0.14191 | 0.18768 | 0.16479 | 0.13733 | 0.21973 | 0.082397 | -0.10529 | 0.16937 | 0.17853 | 0.082397 | 0.17395 | 0.13733 | -0.041199 | -0.10529 | 122.7997 | 122.612 | 0.041199 | 122.905 | 122.8546 | 0.24262 | -0.036621 | 122.6761 | 122.612 | -0.004578 | 122.8867 | 122.7997 | 0.18768 | -0.041199 | 122.937 | 122.8592 | 122.8821 | -0.28381 | 122.8912 | 122.8546 | 122.8958 | -0.28381
1914.5625 | 123.0377 | -122.6486 | 0.13275 | -0.11505 | 0.020615 | 0.0055114 | 0.0093909 | -0.0051932 | -0.0056888 | -0.0065155 | -0.073471 | -0.010846 | -0.004971 | 0.00016019 | 0.00047633 | -0.012726 | 0.21973 | 0.27924 | 0.26093 | 0.21515 | 0.31586 | 0.13733 | -0.018311 | 0.28381 | 0.32959 | 0.21057 | 0.22888 | 0.19226 | 0.032043 | -0.018311 | 122.7859 | 122.6303 | 0.18311 | 122.9279 | 122.8638 | 0.23346 | 0.086976 | 122.6807 | 122.6303 | 0.096131 | 122.9324 | 122.8592 | 0.22888 | 0.05951 | 122.9645 | 122.8683 | 122.9095 | -0.15106 | 122.8775 | 122.8409 | 122.9782 | -0.15106
1916.2656 | 122.9919 | -122.6715 | 0.13275 | -0.2066 | 0.023392 | 0.0038024 | 0.0074683 | -0.0062612 | -0.0046206 | -0.0080109 | -0.16502 | -0.012127 | -0.0056118 | -0.00069421 | 0.0013309 | -0.013153 | 0.25177 | 0.29297 | 0.27008 | 0.24261 | 0.32044 | 0.13275 | 0.013733 | 0.23346 | 0.32044 | 0.17853 | 0.24261 | 0.2243 | 0.045776 | -0.032043 | 122.8043 | 122.6852 | 0.18768 | 122.9645 | 122.9141 | 0.22888 | 0.11902 | 122.7173 | 122.6395 | 0.10986 | 122.905 | 122.85 | 0.21057 | 0.091553 | 122.9919 | 122.9233 | 122.9416 | -0.11902 | 122.9141 | 122.8958 | 122.9919 | -0.16479
1917.9844 | 123.0286 | -122.6624 | 0.13733 | -0.16083 | 0.023178 | 0.0040162 | 0.0059729 | -0.0060476 | -0.0039798 | -0.0077973 | -0.12688 | -0.0099911 | -0.0019802 | 0.00016019 | 0.0028263 | -0.013366 | 0.25635 | 0.32044 | 0.25635 | 0.23346 | 0.33875 | 0.12817 | -0.013733 | 0.26093 | 0.31586 | 0.19684 | 0.22888 | 0.21057 | 0.036621 | -0.018311 | 122.7905 | 122.6486 | 0.20142 | 122.9828 | 122.8958 | 0.24719 | 0.11902 | 122.699 | 122.644 | 0.091553 | 122.9233 | 122.8592 | 0.21515 | 0.073242 | 123.0011 | 122.9187 | 122.9187 | -0.15106 | 122.8912 | 122.8729 | 122.9782 | -0.15564
1919.6875 | 122.9187 | -122.699 | 0.16022 | 0.090942 | 0.020187 | 0.0044434 | 0.0010595 | -0.0066884 | -0.0039798 | -0.0071563 | 0.048599 | -0.010418 | -0.0053982 | -0.00026701 | 0.0036807 | -0.012726 | 0.15564 | 0.16937 | 0.13733 | 0.14648 | 0.25635 | 0.086975 | -0.045776 | 0.1831 | 0.1831 | 0.09613 | 0.20599 | 0.16479 | -0.018311 | -0.050354 | 122.7859 | 122.6532 | 0.096131 | 122.8683 | 122.8455 | 0.19226 | -0.004577 | 122.6807 | 122.6486 | 0.045777 | 122.8821 | 122.7951 | 0.14648 | 0.004578 | 122.9553 | 122.8546 | 122.8363 | -0.20599 | 122.905 | 122.8638 | 122.8821 | -0.21057
1921.3906 | 123.0011 | -122.6761 | 0.15564 | -0.18372 | 0.022324 | 0.006366 | 0.0059729 | -0.0026296 | -0.0029118 | -0.0084381 | -0.17265 | -0.0095639 | -0.0064664 | -0.0011216 | 0.0041079 | -0.011657 | 0.28839 | 0.30212 | 0.25635 | 0.2243 | 0.32959 | 0.16022 | 0.013733 | 0.23346 | 0.29297 | 0.16479 | 0.21973 | 0.19684 | 0.032043 | -0.032043 | 122.8363 | 122.6898 | 0.17395 | 122.9782 | 122.9004 | 0.21057 | 0.13275 | 122.7081 | 122.644 | 0.064087 | 122.9095 | 122.8409 | 0.19684 | 0.041198 | 123.0057 | 122.9645 | 122.9324 | -0.14191 | 122.8958 | 122.8729 | 122.9691 | -0.18768
1923.0625 | 122.9004 | -122.7127 | 0.19226 | 0.11383 | 0.019547 | 0.0044434 | 0.0010595 | -0.0066884 | -0.00098918 | -0.0075837 | 0.094375 | -0.011487 | -0.0068936 | -0.00048061 | 0.0032535 | -0.010589 | 0.1831 | 0.17395 | 0.15564 | 0.13275 | 0.25177 | 0.073242 | -0.073242 | 0.18768 | 0.18768 | 0.091553 | 0.20142 | 0.16937 | -0.009155 | -0.050354 | 122.7859 | 122.6395 | 0.059509 | 122.8867 | 122.8455 | 0.20599 | -0.009156 | 122.7036 | 122.6624 | 0.009155 | 122.9004 | 122.8043 | 0.14191 | -0.022888 | 122.9645 | 122.8958 | 122.8683 | -0.2655 | 122.9141 | 122.8821 | 122.9004 | -0.24261
1924.75 | 123.0652 | -122.6669 | 0.15106 | -0.14557 | 0.021896 | 0.0048706 | 0.0031957 | -0.0071158 | 0.0030698 | -0.0048065 | -0.28709 | -0.0078549 | -0.006039 | -0.00048061 | 0.0053897 | -0.015075 | 0.20599 | 0.1236 | 0.10071 | 0.17395 | 0.36621 | 0.091553 | -0.045776 | 0.13733 | 0.16022 | 0.032043 | 0.27466 | 0.21515 | -0.032043 | -0.059509 | 122.7585 | 122.6212 | 0.21515 | 122.7905 | 122.8409 | 0.21973 | 0.054932 | 122.6349 | 122.6074 | 0.1236 | 122.8043 | 122.699 | 0.091552 | 0.064087 | 123.0331 | 122.8729 | 122.7676 | -0.19684 | 122.9416 | 122.8821 | 122.8271 | -0.21057
1926.4375 | 123.0377 | -122.6669 | 0.16022 | -0.092163 | 0.020828 | 0.0050842 | 0.0066137 | -0.0083974 | -0.0063296 | -0.0043793 | -0.11162 | -0.010632 | -0.0062528 | -0.0026168 | 0.0011173 | -0.010589 | 0.21057 | 0.23346 | 0.20599 | 0.18768 | 0.29297 | 0.11444 | -0.022888 | 0.25635 | 0.28839 | 0.1831 | 0.23346 | 0.20142 | 0.045776 | -0.027466 | 122.7814 | 122.644 | 0.13275 | 122.9004 | 122.8546 | 0.21057 | 0.050354 | 122.7127 | 122.6395 | 0.073242 | 122.9233 | 122.85 | 0.21057 | 0.041199 | 122.9599 | 122.8775 | 122.8729 | -0.1831 | 122.9004 | 122.8683 | 122.9553 | -0.18768
1928.125 | 123.0423 | -122.6852 | 0.14648 | -0.25238 | 0.022965 | 0.0035888 | 0.0093909 | -0.0049796 | 0.0030698 | -0.0065155 | -0.21843 | -0.0067867 | -0.0041164 | -0.0013352 | 0.0030399 | -0.01358 | 0.19684 | 0.14648 | 0.11444 | 0.16479 | 0.36621 | 0.1236 | -0.050354 | 0.13275 | 0.14191 | 0.018311 | 0.27924 | 0.22888 | -0.018311 | -0.059509 | 122.8088 | 122.6349 | 0.21973 | 122.8317 | 122.85 | 0.21515 | 0.050354 | 122.6669 | 122.6257 | 0.13275 | 122.818 | 122.7036 | 0.07782 | 0.082398 | 123.0515 | 122.8821 | 122.7997 | -0.19684 | 122.9645 | 122.9141 | 122.8271 | -0.20599
1929.8438 | 122.9462 | -122.6852 | 0.17853 | 0.15961 | 0.024033 | 0.0048706 | 0.0042639 | -0.0071158 | 0.0026424 | -0.0048065 | 0.03334 | -0.0089229 | -0.006039 | -0.00026701 | 0.0053897 | -0.01358 | 0.10071 | 0.036621 | 0 | 0.059509 | 0.27466 | 0.022888 | -0.13733 | 0.09613 | 0.050354 | -0.018311 | 0.20599 | 0.16022 | -0.064087 | -0.12817 | 122.7081 | 122.5479 | 0.09613 | 122.7219 | 122.7448 | 0.19684 | -0.07782 | 122.6212 | 122.5571 | 0.027466 | 122.7814 | 122.6669 | 0.10986 | -0.018311 | 122.9599 | 122.7859 | 122.6852 | -0.31586 | 122.8912 | 122.8455 | 122.7356 | -0.3067
1931.5312 | 122.9599 | -122.6807 | 0.16937 | 0.13672 | 0.024033 | 0.0059388 | 0.0038367 | -0.005834 | 0.0037106 | -0.0039521 | 0.063858 | -0.0082821 | -0.0047574 | 0.00037379 | 0.0041079 | -0.011657 | 0.07782 | 0.022888 | 0.009155 | 0.032043 | 0.25635 | 0.009155 | -0.1236 | 0.073242 | 0.050354 | -0.041199 | 0.21515 | 0.17395 | -0.082397 | -0.12817 | 122.6898 | 122.5571 | 0.086975 | 122.7036 | 122.7127 | 0.15564 | -0.091553 | 122.5983 | 122.5525 | 0.045776 | 122.7539 | 122.6395 | 0.086975 | 0.004577 | 122.937 | 122.7585 | 122.6898 | -0.29297 | 122.8958 | 122.8546 | 122.731 | -0.29755
1933.2031 | 122.9919 | -122.7081 | 0.15564 | -0.19135 | 0.021042 | 0.0035888 | 0.0040503 | -0.0073294 | -0.0054752 | -0.0054475 | -0.096359 | -0.011487 | -0.0047574 | -0.0015488 | 0.0028263 | -0.0097348 | 0.23804 | 0.3067 | 0.2655 | 0.23804 | 0.31128 | 0.14648 | 0 | 0.23346 | 0.32044 | 0.16022 | 0.23346 | 0.21515 | 0.027466 | -0.022888 | 122.8546 | 122.7081 | 0.15564 | 123.0148 | 122.9462 | 0.23804 | 0.082397 | 122.7356 | 122.6852 | 0.077819 | 122.9416 | 122.8683 | 0.1831 | 0.059509 | 123.0194 | 122.9462 | 122.9736 | -0.15564 | 122.9416 | 122.9233 | 123.0286 | -0.17853
1934.9375 | 123.0286 | -122.6669 | 0.16479 | -0.19897 | 0.025101 | 0.002948 | 0.0046911 | -0.0054068 | 0.0015744 | -0.0052337 | -0.17265 | -0.0082821 | -0.0062528 | -0.0013352 | 0.0045351 | -0.013153 | 0.16937 | 0.16022 | 0.11902 | 0.18768 | 0.35706 | 0.10986 | -0.032043 | 0.13733 | 0.15106 | 0.041199 | 0.23346 | 0.20142 | -0.032043 | -0.091553 | 122.7768 | 122.6349 | 0.19226 | 122.8271 | 122.8546 | 0.21973 | 0.004578 | 122.6349 | 122.5754 | 0.068664 | 122.8043 | 122.7081 | 0.13275 | 0.036621 | 123.024 | 122.8363 | 122.7859 | -0.19684 | 122.9004 | 122.8683 | 122.818 | -0.25635
1936.625 | 123.0103 | -122.7081 | 0.16022 | -0.19135 | 0.021042 | 0.0038024 | 0.0070409 | -0.0049796 | -0.006116 | -0.0045929 | -0.14214 | -0.011914 | -0.0053982 | -5.3406e-05 | 0.0017581 | -0.010803 | 0.24261 | 0.3067 | 0.2655 | 0.24719 | 0.32044 | 0.15106 | -0.027466 | 0.23804 | 0.32044 | 0.17395 | 0.24261 | 0.21515 | 0.032043 | -0.032043 | 122.8592 | 122.6807 | 0.16022 | 123.0148 | 122.9553 | 0.27466 | 0.082398 | 122.7402 | 122.6761 | 0.082398 | 122.9462 | 122.8821 | 0.20599 | 0.054932 | 123.0286 | 122.9507 | 122.9736 | -0.18768 | 122.9507 | 122.9233 | 123.0286 | -0.19226
1938.3125 | 122.9187 | -122.7173 | 0.18768 | 0.14435 | 0.020187 | 0.0076478 | 0.0010595 | -0.0094656 | -0.0029118 | -0.0056611 | 0.12489 | -0.0117 | -0.0064664 | -0.001976 | 0.0017581 | -0.010803 | 0.14191 | 0.17853 | 0.16479 | 0.11902 | 0.23346 | 0.064087 | -0.091553 | 0.1831 | 0.17853 | 0.09613 | 0.19684 | 0.15106 | -0.018311 | -0.073242 | 122.7814 | 122.6257 | 0.045776 | 122.8958 | 122.8363 | 0.21057 | -0.045776 | 122.699 | 122.644 | 0.009155 | 122.9004 | 122.8134 | 0.16937 | -0.036621 | 122.9507 | 122.8592 | 122.8821 | -0.27924 | 122.9141 | 122.8683 | 122.8958 | -0.26092
1940 | 123.024 | -122.6669 | 0.16022 | -0.12268 | 0.023605 | 0.0035888 | 0.0031957 | -0.0064748 | 0.004565 | -0.0065155 | -0.18791 | -0.011059 | -0.00668 | -5.3406e-05 | 0.0060305 | -0.013366 | 0.19684 | 0.15564 | 0.10986 | 0.15106 | 0.34332 | 0.082397 | -0.07782 | 0.15106 | 0.14648 | 0.036621 | 0.2243 | 0.21515 | -0.041199 | -0.10529 | 122.7493 | 122.5891 | 0.18311 | 122.8226 | 122.818 | 0.22888 | 0.036621 | 122.6257 | 122.5616 | 0.064087 | 122.818 | 122.7036 | 0.14191 | 0.054932 | 123.0103 | 122.8638 | 122.7768 | -0.23804 | 122.8912 | 122.8821 | 122.8134 | -0.2655
1941.6875 | 122.9965 | -122.6578 | 0.16022 | -0.015869 | 0.02211 | 0.0061524 | 0.0066137 | -0.0071158 | -0.0041934 | -0.0067291 | 0.025711 | -0.011487 | -0.0073208 | -0.00048061 | -0.00016447 | -0.010376 | 0.13733 | 0.17853 | 0.15564 | 0.16022 | 0.31128 | 0.091553 | -0.050354 | 0.17853 | 0.21515 | 0.13275 | 0.21515 | 0.1831 | 0.004578 | -0.041199 | 122.7493 | 122.6074 | 0.15106 | 122.8363 | 122.818 | 0.21057 | -0.022888 | 122.6624 | 122.6166 | 0.054932 | 122.8363 | 122.7905 | 0.17395 | 0.022888 | 122.9691 | 122.7951 | 122.8134 | -0.21057 | 122.8729 | 122.8409 | 122.8729 | -0.20142
1943.3906 | 122.9507 | -122.7081 | 0.17395 | 0.15198 | 0.025955 | 0.0025208 | 0.0040503 | -0.0060476 | 0.00071982 | -0.0050201 | 0.15541 | -0.0070003 | -0.004971 | -0.0015488 | 0.0064577 | -0.014648 | 0.17395 | 0.15106 | 0.1236 | 0.13275 | 0.22888 | 0.041199 | -0.10071 | 0.16937 | 0.16479 | 0.073242 | 0.16479 | 0.11902 | -0.059509 | -0.10529 | 122.7493 | 122.6074 | 0.054932 | 122.8592 | 122.8409 | 0.23346 | 0 | 122.6486 | 122.6028 | -0.009155 | 122.8775 | 122.7814 | 0.17853 | -0.054931 | 122.937 | 122.8821 | 122.8317 | -0.27466 | 122.8729 | 122.8271 | 122.8729 | -0.27924
1945.0938 | 123.0469 | -122.6852 | 0.16937 | -0.25238 | 0.023819 | 0.0050842 | 0.0085363 | -0.0062612 | -0.0014164 | -0.0048065 | -0.25658 | -0.010418 | -0.0045438 | -0.00048061 | 0.0053897 | -0.012512 | 0.1831 | 0.16479 | 0.11902 | 0.16479 | 0.3891 | 0.10529 | -0.041199 | 0.14648 | 0.15564 | 0.045776 | 0.27924 | 0.25177 | 0.009155 | -0.054932 | 122.7905 | 122.644 | 0.21973 | 122.85 | 122.85 | 0.20599 | 0.013732 | 122.6944 | 122.6303 | 0.10986 | 122.8317 | 122.731 | 0.10071 | 0.082397 | 123.0743 | 122.8683 | 122.8043 | -0.21057 | 122.9645 | 122.937 | 122.8409 | -0.22431
1946.7812 | 122.9004 | -122.731 | 0.17853 | 0.1062 | 0.020187 | 0.0035888 | 0.0031957 | -0.0071158 | -0.0039798 | -0.0048065 | 0.15541 | -0.012127 | -0.006039 | -0.00069421 | 0.0045351 | -0.010803 | 0.14648 | 0.1831 | 0.15106 | 0.10986 | 0.21973 | 0.054932 | -0.091553 | 0.16022 | 0.1831 | 0.09613 | 0.17395 | 0.14191 | -0.041199 | -0.082397 | 122.7859 | 122.6395 | 0.041199 | 122.9141 | 122.8409 | 0.20142 | -0.032044 | 122.6898 | 122.6486 | -0.004578 | 122.8912 | 122.8271 | 0.17853 | -0.036621 | 122.9507 | 122.8775 | 122.8821 | -0.27008 | 122.905 | 122.8729 | 122.9141 | -0.26092
1948.5 | 123.0377 | -122.6761 | 0.15564 | -0.13031 | 0.026169 | 0.004657 | 0.0031957 | -0.0079702 | 0.0026424 | -0.0043793 | -0.16502 | -0.0091367 | -0.0062528 | 0.00016019 | 0.0062441 | -0.012939 | 0.21057 | 0.17395 | 0.10529 | 0.15564 | 0.33417 | 0.068665 | -0.086975 | 0.13275 | 0.14191 | 0.032043 | 0.23804 | 0.1831 | -0.032043 | -0.082397 | 122.7448 | 122.5891 | 0.17853 | 122.85 | 122.8317 | 0.24261 | 0.054931 | 122.644 | 122.5937 | 0.082397 | 122.8088 | 122.7081 | 0.11444 | 0.027465 | 123.0103 | 122.8867 | 122.7814 | -0.24261 | 122.9141 | 122.8592 | 122.818 | -0.23804
1950.1875 | 123.0148 | -122.6761 | 0.15106 | -0.038757 | 0.022537 | 0.006366 | 0.0057593 | -0.0064748 | -0.006757 | -0.0067291 | 0.010452 | -0.011059 | -0.0056118 | -0.00026701 | 0.00047633 | -0.010162 | 0.15106 | 0.18768 | 0.16937 | 0.16022 | 0.28839 | 0.086975 | -0.045776 | 0.19226 | 0.22888 | 0.15564 | 0.21973 | 0.18768 | 0.004578 | -0.050354 | 122.7631 | 122.6303 | 0.13733 | 122.8638 | 122.8363 | 0.20599 | 0 | 122.6807 | 122.6257 | 0.068665 | 122.8683 | 122.8317 | 0.20599 | 0.036621 | 122.9645 | 122.8271 | 122.8455 | -0.19684 | 122.8958 | 122.8638 | 122.905 | -0.20142
1951.8906 | 122.9141 | -122.7081 | 0.1831 | 0.083313 | 0.021896 | 0.0057252 | 0.0042639 | -0.007543 | -0.0048344 | -0.0084381 | 0.102 | -0.010205 | -0.0056118 | 0.00016019 | 0.0036807 | -0.012726 | 0.16022 | 0.20142 | 0.14648 | 0.12817 | 0.25177 | 0.064087 | -0.082397 | 0.1831 | 0.18768 | 0.086975 | 0.20599 | 0.1831 | -0.018311 | -0.059509 | 122.7722 | 122.6257 | 0.068665 | 122.9095 | 122.8363 | 0.21057 | -0.022888 | 122.6898 | 122.6486 | 0.022889 | 122.8912 | 122.7951 | 0.14648 | 0 | 122.9599 | 122.8683 | 122.8546 | -0.2655 | 122.9141 | 122.8912 | 122.8958 | -0.24261
1953.5781 | 122.9691 | -122.7127 | 0.17395 | -0.084534 | 0.025101 | 0.0023072 | 0.0036231 | -0.0064748 | 0.0011472 | -0.0035249 | -0.17265 | -0.0078549 | -0.0056118 | -5.3406e-05 | 0.0060305 | -0.015075 | 0.21973 | 0.14191 | 0.10071 | 0.13733 | 0.30212 | 0.054932 | -0.073242 | 0.12817 | 0.14191 | 0.004578 | 0.21515 | 0.1831 | -0.027466 | -0.10071 | 122.7676 | 122.6395 | 0.12817 | 122.8546 | 122.85 | 0.21057 | 0.045777 | 122.6852 | 122.612 | 0.041199 | 122.8409 | 122.7173 | 0.10529 | 0.009155 | 123.0148 | 122.9324 | 122.8134 | -0.24719 | 122.9279 | 122.8958 | 122.8546 | -0.27466
1955.2812 | 122.905 | -122.7219 | 0.19684 | 0.0070193 | 0.024246 | 0.0050842 | 0.0044775 | -0.005834 | 0.001788 | -0.0028839 | 0.0028229 | -0.0065731 | -0.0047574 | -0.00090781 | 0.0064577 | -0.013153 | 0.10986 | 0.07782 | 0.032043 | 0.086975 | 0.28839 | 0.036621 | -0.13733 | 0.068665 | 0.050354 | -0.068665 | 0.2243 | 0.16479 | -0.082397 | -0.13733 | 122.7585 | 122.5845 | 0.091553 | 122.7997 | 122.8088 | 0.2243 | -0.086975 | 122.6395 | 122.5845 | 0.027466 | 122.7905 | 122.6532 | 0.068664 | -0.032043 | 123.0103 | 122.8317 | 122.7539 | -0.33417 | 122.9462 | 122.8867 | 122.7722 | -0.33417
1957.0312 | 122.9462 | -122.7219 | 0.18768 | 0.098572 | 0.02681 | 0.0055114 | 0.0029821 | -0.009252 | 0.00029262 | -0.0016021 | 0.086746 | -0.0095639 | -0.006039 | -0.0013352 | 0.0064577 | -0.012085 | 0.050354 | 0.027466 | -0.009155 | 0.050354 | 0.25177 | 0 | -0.14648 | 0.054932 | 0.022888 | -0.050354 | 0.20142 | 0.16937 | -0.091553 | -0.14648 | 122.7219 | 122.5754 | 0.064087 | 122.7493 | 122.7722 | 0.19684 | -0.13733 | 122.6303 | 122.5754 | 0.013733 | 122.7768 | 122.6715 | 0.09613 | -0.01831 | 122.9736 | 122.7722 | 122.7127 | -0.33417 | 122.9233 | 122.8912 | 122.7448 | -0.33417
1958.7188 | 123.0652 | -122.644 | 0.16479 | -0.17609 | 0.02681 | 0.0027344 | 0.0081091 | -0.0066884 | 0.00071982 | -0.0052337 | -0.22606 | -0.0074277 | -0.0034756 | -0.0017624 | 0.0034671 | -0.011017 | 0.15564 | 0.13275 | 0.11902 | 0.15564 | 0.3479 | 0.11444 | -0.054932 | 0.13275 | 0.17853 | 0.050354 | 0.28381 | 0.22888 | -0.009155 | -0.059509 | 122.7585 | 122.5891 | 0.1831 | 122.7768 | 122.7997 | 0.21057 | -0.009155 | 122.6349 | 122.5845 | 0.11902 | 122.7768 | 122.6944 | 0.10986 | 0.064087 | 122.9919 | 122.7997 | 122.7631 | -0.21973 | 122.9279 | 122.8729 | 122.8226 | -0.2243
1960.4062 | 123.0011 | -122.6852 | 0.16937 | 0.014648 | 0.02446 | 0.0035888 | 0.0072547 | -0.0066884 | -0.0063296 | -0.0052337 | 0.094375 | -0.010632 | -0.0036892 | -0.0013352 | -0.0014463 | -0.011017 | 0.10529 | 0.16937 | 0.15564 | 0.15564 | 0.30212 | 0.10986 | -0.041199 | 0.16937 | 0.21515 | 0.12817 | 0.23346 | 0.19226 | -0.004578 | -0.059509 | 122.7951 | 122.644 | 0.13275 | 122.8546 | 122.8409 | 0.19684 | -0.064087 | 122.6807 | 122.6257 | 0.064086 | 122.8546 | 122.8134 | 0.18768 | 0.022888 | 122.9874 | 122.7905 | 122.8409 | -0.21057 | 122.9187 | 122.8775 | 122.9004 | -0.22888
1962.0938 | 123.0057 | -122.6761 | 0.15564 | -0.19897 | 0.021256 | 0.0057252 | 0.0070409 | -0.0049796 | -0.0059024 | -0.0058747 | -0.16502 | -0.012341 | -0.0053982 | -0.0030442 | 4.9132e-05 | -0.011871 | 0.22888 | 0.3067 | 0.26093 | 0.23804 | 0.31586 | 0.11902 | -0.027466 | 0.23804 | 0.31586 | 0.19226 | 0.26093 | 0.21057 | 0.050354 | -0.009155 | 122.7951 | 122.6486 | 0.16022 | 122.9828 | 122.9141 | 0.2655 | 0.073242 | 122.7264 | 122.6669 | 0.10529 | 122.9141 | 122.8683 | 0.20142 | 0.054931 | 122.9919 | 122.905 | 122.937 | -0.18311 | 122.937 | 122.8867 | 122.9919 | -0.16479
1963.7812 | 122.9645 | -122.7127 | 0.17853 | 0.15198 | 0.023178 | 0.0038024 | 0.00084592 | -0.0071158 | 0.0011472 | -0.0056611 | 0.14015 | -0.0082821 | -0.00668 | -0.00069421 | 0.0051761 | -0.01358 | 0.13733 | 0.11902 | 0.11902 | 0.10529 | 0.21973 | 0.041199 | -0.10529 | 0.16937 | 0.16479 | 0.073242 | 0.15106 | 0.12817 | -0.022888 | -0.086975 | 122.7539 | 122.6074 | 0.041199 | 122.8317 | 122.818 | 0.21057 | -0.041199 | 122.6898 | 122.6257 | -0.027466 | 122.8821 | 122.7859 | 0.16022 | -0.050354 | 122.9324 | 122.85 | 122.8317 | -0.28381 | 122.8638 | 122.8409 | 122.8775 | -0.2655
1965.4688 | 123.0103 | -122.6669 | 0.16022 | -0.099793 | 0.027451 | 0.0025208 | 0.0074683 | -0.0062612 | 0.0026424 | -0.0041657 | -0.17265 | -0.0076413 | -0.0026212 | 0.00037379 | 0.0056033 | -0.015289 | 0.16937 | 0.16937 | 0.10071 | 0.14648 | 0.32501 | 0.064087 | -0.086975 | 0.16022 | 0.15106 | 0.027466 | 0.21515 | 0.1831 | -0.041199 | -0.091553 | 122.731 | 122.58 | 0.1648 | 122.8363 | 122.8134 | 0.23346 | 0.009156 | 122.6257 | 122.5754 | 0.054932 | 122.8271 | 122.6944 | 0.11902 | 0.022888 | 122.9919 | 122.8363 | 122.7676 | -0.24719 | 122.8821 | 122.85 | 122.818 | -0.25177
1967.1406 | 122.8867 | -122.7402 | 0.19226 | 0.083313 | 0.02211 | 0.0067932 | 0.0042639 | -0.0079702 | -0.0052616 | -0.0058747 | 0.18593 | -0.012341 | -0.0081754 | -0.00026701 | 0.0047489 | -0.010376 | 0.12817 | 0.19226 | 0.14191 | 0.1236 | 0.23346 | 0.054932 | -0.10529 | 0.16937 | 0.1831 | 0.10071 | 0.16479 | 0.14648 | -0.050354 | -0.086975 | 122.7951 | 122.6349 | 0.041198 | 122.9324 | 122.8638 | 0.22888 | -0.064087 | 122.6898 | 122.6532 | -0.027466 | 122.9095 | 122.8409 | 0.18768 | -0.045777 | 122.9736 | 122.8683 | 122.8821 | -0.29755 | 122.905 | 122.8867 | 122.9233 | -0.27924
1968.8281 | 122.9416 | -122.7173 | 0.16937 | 0.15961 | 0.024674 | 0.0038024 | 0.0014867 | -0.0069022 | 0.0015744 | -0.0054475 | 0.13252 | -0.0099911 | -0.0075344 | -0.0026168 | 0.0060305 | -0.011017 | 0.15106 | 0.14648 | 0.11902 | 0.1236 | 0.24261 | 0.050354 | -0.1236 | 0.16479 | 0.15564 | 0.07782 | 0.14648 | 0.13733 | -0.036621 | -0.09613 | 122.7676 | 122.5937 | 0.073242 | 122.8638 | 122.8409 | 0.24719 | -0.018311 | 122.6807 | 122.6212 | -0.022889 | 122.8821 | 122.7951 | 0.17395 | -0.032044 | 122.9599 | 122.8683 | 122.8363 | -0.29297 | 122.8638 | 122.8546 | 122.8729 | -0.2655
1970.5156 | 123.0423 | -122.6807 | 0.16022 | -0.12268 | 0.023392 | 0.0061524 | 0.0025549 | -0.0060476 | 0.0015744 | -0.0039521 | -0.15739 | -0.0080685 | -0.0064664 | -5.3406e-05 | 0.0062441 | -0.012512 | 0.19684 | 0.13275 | 0.10071 | 0.15564 | 0.31586 | 0.073242 | -0.07782 | 0.13733 | 0.13733 | 0.032043 | 0.22888 | 0.1831 | -0.027466 | -0.10071 | 122.7539 | 122.6028 | 0.15564 | 122.8134 | 122.8363 | 0.23346 | 0.036621 | 122.6532 | 122.58 | 0.068665 | 122.818 | 122.7127 | 0.13275 | 0.022888 | 122.9965 | 122.8775 | 122.7814 | -0.23804 | 122.9095 | 122.8638 | 122.818 | -0.26093
1972.2031 | 122.9141 | -122.7219 | 0.16937 | 0.12909 | 0.022751 | 0.0038024 | 0.0046911 | -0.0073294 | -0.00163 | -0.0035249 | 0.16304 | -0.0093503 | -0.0047574 | -0.0013352 | 0.0032535 | -0.010162 | 0.14648 | 0.18768 | 0.14648 | 0.14191 | 0.21515 | 0.045776 | -0.10529 | 0.16937 | 0.16479 | 0.10529 | 0.1831 | 0.13275 | -0.032043 | -0.082397 | 122.7676 | 122.6166 | 0.045776 | 122.9095 | 122.8638 | 0.24719 | -0.022889 | 122.6898 | 122.6395 | 0.013732 | 122.8912 | 122.8271 | 0.18768 | -0.036622 | 122.937 | 122.8683 | 122.8683 | -0.27466 | 122.905 | 122.8546 | 122.8867 | -0.25177
1973.8906 | 122.9279 | -122.7402 | 0.18768 | -0.0082397 | 0.026383 | 0.0027344 | 0.0053321 | -0.0073294 | 0.0032834 | -0.0041657 | -0.0048066 | -0.0059323 | -0.0051846 | -0.0015488 | 0.0075259 | -0.014435 | 0.1236 | 0.068665 | 0.045776 | 0.064087 | 0.29297 | 0.045776 | -0.11902 | 0.045776 | 0.027466 | -0.059509 | 0.21515 | 0.18768 | -0.086975 | -0.10986 | 122.7859 | 122.6212 | 0.10529 | 122.8088 | 122.8043 | 0.18311 | -0.064087 | 122.6532 | 122.6303 | 0.027466 | 122.7859 | 122.6807 | 0.050354 | 0 | 123.0331 | 122.8638 | 122.7859 | -0.3067 | 122.9553 | 122.9279 | 122.7676 | -0.29755
1975.5781 | 123.0011 | -122.6807 | 0.15564 | -0.2066 | 0.020615 | 0.0061524 | 0.0096045 | -0.0060476 | -0.0052616 | -0.0065155 | -0.11162 | -0.011914 | -0.0024076 | -0.0024032 | -0.00037807 | -0.0088804 | 0.23804 | 0.29297 | 0.25635 | 0.24719 | 0.31586 | 0.14648 | 0 | 0.23346 | 0.30212 | 0.16479 | 0.2243 | 0.20599 | 0.050354 | -0.027466 | 122.8271 | 122.6807 | 0.16022 | 122.9736 | 122.9279 | 0.24719 | 0.082397 | 122.731 | 122.6532 | 0.068664 | 122.9141 | 122.8455 | 0.19226 | 0.050354 | 122.9965 | 122.9187 | 122.937 | -0.15564 | 122.905 | 122.8867 | 122.9828 | -0.18311
1977.2656 | 122.9599 | -122.7081 | 0.14191 | 0.029907 | 0.020187 | 0.0057252 | 0.0044775 | -0.0073294 | -0.0063296 | -0.0069427 | 0.079117 | -0.0089229 | -0.006039 | -0.00069421 | 0.0028263 | -0.011871 | 0.15564 | 0.15564 | 0.14191 | 0.15564 | 0.31128 | 0.07782 | -0.041199 | 0.16479 | 0.1831 | 0.10986 | 0.2243 | 0.20142 | 0.013733 | -0.064087 | 122.7859 | 122.6669 | 0.16937 | 122.8638 | 122.8638 | 0.19684 | 0.013733 | 122.7219 | 122.644 | 0.082397 | 122.8729 | 122.818 | 0.17395 | 0.059509 | 123.0194 | 122.8638 | 122.85 | -0.18311 | 122.9324 | 122.9095 | 122.8912 | -0.20599
1978.9531 | 123.0469 | -122.7127 | 0.15564 | -0.18372 | 0.025742 | 0.0018798 | 0.0091773 | -0.007543 | 0.0022152 | -0.0054475 | -0.23369 | -0.0076413 | -0.0041164 | -5.3406e-05 | 0.0028263 | -0.014648 | 0.1831 | 0.11902 | 0.09613 | 0.17395 | 0.37537 | 0.10529 | -0.036621 | 0.12817 | 0.13275 | 0.032043 | 0.27008 | 0.25177 | -0.004578 | -0.059509 | 122.818 | 122.6761 | 0.21973 | 122.8317 | 122.8867 | 0.21057 | 0.027465 | 122.7081 | 122.6532 | 0.11444 | 122.8409 | 122.7448 | 0.091552 | 0.09613 | 123.0881 | 122.8958 | 122.8088 | -0.19226 | 122.9828 | 122.9645 | 122.8455 | -0.21515
1980.6406 | 123.024 | -122.6807 | 0.15564 | -0.015869 | 0.022751 | 0.0050842 | 0.0085363 | -0.008611 | -0.0065434 | -0.0039521 | 0.03334 | -0.012127 | -0.0026212 | -0.0021896 | -0.0010191 | -0.010589 | 0.14191 | 0.16937 | 0.14648 | 0.16479 | 0.31128 | 0.09613 | -0.054932 | 0.18768 | 0.20142 | 0.11444 | 0.21515 | 0.20142 | 0.004578 | -0.036621 | 122.7768 | 122.6257 | 0.15564 | 122.85 | 122.8455 | 0.21973 | -0.013733 | 122.6852 | 122.644 | 0.059509 | 122.8683 | 122.7951 | 0.15106 | 0.045776 | 122.9919 | 122.8226 | 122.8271 | -0.21057 | 122.8958 | 122.8821 | 122.8821 | -0.19226
1982.3438 | 122.9782 | -122.7127 | 0.17395 | 0.20538 | 0.023392 | 0.0070068 | 0.0027685 | -0.0051932 | 0.0030698 | -0.0050201 | 0.13252 | -0.0091367 | -0.0058254 | -0.0011216 | 0.0060305 | -0.014007 | 0.11902 | 0.068665 | 0.059509 | 0.068665 | 0.22888 | 0.045776 | -0.15106 | 0.15106 | 0.1236 | 0.064087 | 0.15106 | 0.14191 | -0.045776 | -0.09613 | 122.7585 | 122.5616 | 0.054932 | 122.7814 | 122.7814 | 0.21973 | -0.054931 | 122.6669 | 122.6166 | -0.022888 | 122.8638 | 122.7768 | 0.16022 | -0.032043 | 122.9416 | 122.8317 | 122.7722 | -0.32501 | 122.8638 | 122.8546 | 122.8363 | -0.27008
1984.0156 | 123.0011 | -122.699 | 0.16022 | -0.23712 | 0.022965 | 0.006366 | 0.0083227 | -0.0060476 | -0.00034818 | -0.0052337 | -0.18028 | -0.0099911 | -0.0036892 | -5.3406e-05 | 0.0023989 | -0.011657 | 0.19684 | 0.16479 | 0.15106 | 0.16937 | 0.37079 | 0.1236 | -0.022888 | 0.14648 | 0.16022 | 0.054932 | 0.27924 | 0.27008 | -0.004578 | -0.064087 | 122.8226 | 122.6761 | 0.21057 | 122.8638 | 122.8683 | 0.19226 | 0.036621 | 122.6944 | 122.6349 | 0.11902 | 122.8455 | 122.7539 | 0.11902 | 0.10986 | 123.0698 | 122.8958 | 122.85 | -0.1831 | 122.9782 | 122.9691 | 122.8592 | -0.2243
1985.75 | 122.9736 | -122.6944 | 0.16937 | 0.098572 | 0.025101 | 0.002948 | 0.0017005 | -0.0045522 | 0.0015744 | -0.0050201 | 0.094375 | -0.0093503 | -0.0039028 | -0.00069421 | 0.0060305 | -0.013153 | 0.11444 | 0.036621 | 0.032043 | 0.059509 | 0.27924 | 0.027466 | -0.12817 | 0.11444 | 0.050354 | -0.022888 | 0.19684 | 0.15564 | -0.059509 | -0.11902 | 122.7219 | 122.5662 | 0.10986 | 122.731 | 122.7539 | 0.18768 | -0.054932 | 122.6349 | 122.5754 | 0.027465 | 122.8088 | 122.6715 | 0.096131 | -0.013733 | 122.9736 | 122.8088 | 122.7264 | -0.29755 | 122.8912 | 122.85 | 122.7448 | -0.28839
1987.4375 | 123.0103 | -122.6898 | 0.1236 | -0.22186 | 0.025742 | 0.004657 | 0.0087499 | -0.0045522 | -0.0022708 | -0.0063019 | -0.24132 | -0.0076413 | -0.0019802 | -0.00090781 | 0.0019717 | -0.010803 | 0.16479 | 0.15564 | 0.1236 | 0.16479 | 0.37537 | 0.11444 | -0.045776 | 0.14191 | 0.14648 | 0.050354 | 0.29755 | 0.2655 | 0.004578 | -0.064087 | 122.8043 | 122.644 | 0.25177 | 122.8455 | 122.8546 | 0.21057 | 0.041199 | 122.6944 | 122.6257 | 0.17395 | 122.8317 | 122.7402 | 0.11444 | 0.14191 | 123.0652 | 122.8546 | 122.8134 | -0.16937 | 122.9874 | 122.9553 | 122.8363 | -0.18768
1989.1094 | 122.9462 | -122.7173 | 0.17853 | -0.061646 | 0.025955 | 0.0035888 | 0.0061865 | -0.0051932 | 0.003497 | -0.0067291 | -0.096359 | -0.0074277 | -0.0036892 | 0.001442 | 0.0051761 | -0.012726 | 0.16937 | 0.14191 | 0.091553 | 0.1236 | 0.30212 | 0.059509 | -0.10986 | 0.11444 | 0.11444 | -0.004578 | 0.21973 | 0.17853 | -0.045776 | -0.11902 | 122.7768 | 122.6074 | 0.1236 | 122.8592 | 122.8409 | 0.23346 | -0.009155 | 122.6715 | 122.5983 | 0.041199 | 122.8317 | 122.7127 | 0.11444 | 0 | 123.0194 | 122.8867 | 122.8088 | -0.28839 | 122.937 | 122.8958 | 122.8317 | -0.29755
1990.7812 | 123.0469 | -122.6761 | 0.13275 | -0.084534 | 0.022324 | 0.0082886 | 0.0074683 | -0.0071158 | -0.0076114 | -0.0058747 | -0.10399 | -0.012982 | -0.0075344 | -0.00048061 | -0.00016447 | -0.011017 | 0.22888 | 0.32044 | 0.26093 | 0.23804 | 0.31586 | 0.13275 | -0.027466 | 0.24719 | 0.31128 | 0.21057 | 0.24719 | 0.19684 | 0.036621 | 0 | 122.8088 | 122.6486 | 0.18311 | 122.9965 | 122.9141 | 0.2655 | 0.096131 | 122.7127 | 122.6761 | 0.11444 | 122.9233 | 122.8867 | 0.21057 | 0.064087 | 122.9919 | 122.905 | 122.937 | -0.16022 | 122.9233 | 122.8729 | 122.9874 | -0.13275
1992.4688 | 122.9691 | -122.6944 | 0.17853 | 0.1825 | 0.022751 | 0.0057252 | 0.0021277 | -0.0051932 | 0.0020016 | -0.0013885 | 0.14778 | -0.0067867 | -0.0053982 | -0.0013352 | 0.0058169 | -0.01123 | 0.09613 | 0.059509 | 0.036621 | 0.068665 | 0.25635 | 0.022888 | -0.13733 | 0.15106 | 0.13275 | 0.068665 | 0.15106 | 0.12817 | -0.050354 | -0.086975 | 122.7173 | 122.5571 | 0.07782 | 122.7539 | 122.7631 | 0.20599 | -0.082398 | 122.644 | 122.6074 | -0.027466 | 122.8455 | 122.7631 | 0.15564 | -0.050354 | 122.9507 | 122.7905 | 122.731 | -0.31586 | 122.8455 | 122.8226 | 122.8271 | -0.2655
1994.1562 | 122.9279 | -122.7356 | 0.19226 | 0.022278 | 0.026169 | 0.0040162 | 0.0044775 | -0.0047658 | 0.0024288 | -0.0048065 | -0.0048066 | -0.0074277 | -0.0075344 | -0.0011216 | 0.0079531 | -0.011657 | 0.10071 | 0.032043 | 0.013733 | 0.064087 | 0.27008 | 0.036621 | -0.12817 | 0.036621 | 0.045776 | -0.059509 | 0.18768 | 0.19226 | -0.073242 | -0.15106 | 122.7722 | 122.6074 | 0.07782 | 122.7676 | 122.7997 | 0.19226 | -0.091553 | 122.6624 | 122.5845 | -0.004578 | 122.7722 | 122.6761 | 0.091553 | 0 | 123.0057 | 122.8363 | 122.7493 | -0.32044 | 122.9233 | 122.9279 | 122.7814 | -0.34332
1995.8438 | 123.0652 | -122.6715 | 0.14191 | -0.11505 | 0.024246 | 0.0040162 | 0.0070409 | -0.007543 | -0.0080386 | -0.0075837 | -0.073471 | -0.010418 | -0.0043302 | -0.0017624 | -0.0016599 | -0.011871 | 0.21515 | 0.27466 | 0.23804 | 0.20599 | 0.32501 | 0.13733 | -0.036621 | 0.27466 | 0.29297 | 0.20599 | 0.23346 | 0.21057 | 0.032043 | -0.022888 | 122.8088 | 122.6349 | 0.18311 | 122.9462 | 122.8775 | 0.24262 | 0.073242 | 122.7036 | 122.6486 | 0.091552 | 122.9462 | 122.8775 | 0.22888 | 0.068664 | 122.9965 | 122.8867 | 122.9095 | -0.17853 | 122.905 | 122.8821 | 122.9645 | -0.16479
1997.5625 | 122.9095 | -122.7127 | 0.17395 | 0.13672 | 0.020828 | 0.0055114 | 0.0029821 | -0.0045522 | -0.0029118 | -0.0058747 | 0.16304 | -0.010418 | -0.0071072 | -0.00048061 | 0.0060305 | -0.012085 | 0.16022 | 0.16937 | 0.14648 | 0.11902 | 0.21973 | 0.036621 | -0.09613 | 0.16937 | 0.17395 | 0.086975 | 0.16937 | 0.13733 | -0.041199 | -0.09613 | 122.7493 | 122.6166 | 0.045777 | 122.8821 | 122.8317 | 0.21515 | -0.013733 | 122.6715 | 122.6166 | -0.004577 | 122.8821 | 122.7997 | 0.1831 | -0.036621 | 122.9324 | 122.8729 | 122.8592 | -0.27008 | 122.8821 | 122.85 | 122.8867 | -0.27008
1999.25 | 123.0423 | -122.6944 | 0.15564 | -0.12268 | 0.024674 | 0.0044434 | 0.0074683 | -0.0051932 | 0.0028562 | -0.0060883 | -0.18028 | -0.0076413 | -0.0056118 | 0.001442 | 0.0062441 | -0.016998 | 0.19226 | 0.13733 | 0.10986 | 0.15564 | 0.31128 | 0.064087 | -0.091553 | 0.13275 | 0.14648 | 0.022888 | 0.23346 | 0.19684 | -0.027466 | -0.10529 | 122.7585 | 122.6028 | 0.15564 | 122.8317 | 122.85 | 0.24719 | 0.036621 | 122.6669 | 122.5891 | 0.077819 | 122.8271 | 122.7173 | 0.12817 | 0.041198 | 123.0057 | 122.8867 | 122.8043 | -0.24719 | 122.9279 | 122.8912 | 122.8409 | -0.26093
2001 | 123.0057 | -122.7219 | 0.15106 | -0.25238 | 0.024246 | 0.0042298 | 0.0089635 | -0.0049796 | -0.0014164 | -0.0058747 | -0.18791 | -0.012768 | -0.0024076 | -0.001976 | 0.0028263 | -0.011657 | 0.20599 | 0.19226 | 0.16937 | 0.18768 | 0.37079 | 0.13275 | -0.041199 | 0.14648 | 0.15564 | 0.082397 | 0.28381 | 0.26093 | -0.009155 | -0.068665 | 122.8546 | 122.6807 | 0.21973 | 122.9141 | 122.9095 | 0.22888 | 0.054932 | 122.7127 | 122.6532 | 0.13275 | 122.8683 | 122.8043 | 0.15106 | 0.10986 | 123.0927 | 122.9279 | 122.8912 | -0.19226 | 123.0057 | 122.9828 | 122.8775 | -0.21973
2002.7188 | 122.9324 | -122.7173 | 0.17853 | 0.19012 | 0.02211 | 0.004657 | 0.0027685 | -0.0054068 | -0.0020572 | -0.0028839 | 0.18593 | -0.010632 | -0.0043302 | -0.0024032 | 0.0041079 | -0.012512 | 0.13275 | 0.16022 | 0.13275 | 0.12817 | 0.2243 | 0.032043 | -0.13275 | 0.17853 | 0.17853 | 0.086975 | 0.15106 | 0.11902 | -0.059509 | -0.10071 | 122.7493 | 122.5845 | 0.045776 | 122.8775 | 122.8455 | 0.26093 | -0.045777 | 122.6578 | 122.6166 | -0.027466 | 122.8958 | 122.8043 | 0.18768 | -0.059509 | 122.9416 | 122.85 | 122.85 | -0.31128 | 122.8683 | 122.8363 | 122.8958 | -0.27924
2004.4062 | 123.0469 | -122.6852 | 0.1831 | -0.10742 | 0.025101 | 0.004657 | 0.0057593 | -0.0045522 | 0.0013608 | -0.0043793 | -0.18791 | -0.0099911 | -0.0039028 | -0.00048061 | 0.0051761 | -0.015289 | 0.16937 | 0.15106 | 0.09613 | 0.14648 | 0.33417 | 0.068665 | -0.086975 | 0.15564 | 0.14648 | 0.036621 | 0.22888 | 0.19684 | -0.041199 | -0.10071 | 122.7539 | 122.5983 | 0.15106 | 122.8363 | 122.8317 | 0.23346 | -0.013732 | 122.644 | 122.5845 | 0.045777 | 122.8409 | 122.7219 | 0.13733 | 0.013733 | 123.0194 | 122.8546 | 122.7814 | -0.27008 | 122.9141 | 122.8821 | 122.8317 | -0.28381
2006.1094 | 122.9004 | -122.7127 | 0.21057 | 0.13672 | 0.020828 | 0.0059388 | 0.0031957 | -0.0083974 | -0.004407 | -0.0054475 | 0.1783 | -0.011487 | -0.0062528 | -0.0024032 | 0.0049625 | -0.011017 | 0.16022 | 0.17395 | 0.14648 | 0.1236 | 0.20599 | 0.059509 | -0.086975 | 0.16022 | 0.16022 | 0.091553 | 0.15564 | 0.12817 | -0.045776 | -0.082397 | 122.7722 | 122.6257 | -0.004577 | 122.8867 | 122.8363 | 0.21057 | -0.050354 | 122.6669 | 122.6303 | -0.054931 | 122.8729 | 122.8043 | 0.17395 | -0.082397 | 122.9187 | 122.8729 | 122.8592 | -0.29755 | 122.8683 | 122.8409 | 122.8729 | -0.29297
2007.7969 | 123.0194 | -122.7036 | 0.15564 | -0.19897 | 0.023178 | 0.0057252 | 0.0083227 | -0.0064748 | -0.002698 | -0.0075837 | -0.24132 | -0.0091367 | -0.0043302 | -0.0013352 | 0.0021853 | -0.011657 | 0.15564 | 0.16022 | 0.13275 | 0.15564 | 0.3891 | 0.10529 | -0.041199 | 0.11902 | 0.15564 | 0.073242 | 0.28839 | 0.2655 | -0.018311 | -0.032043 | 122.8088 | 122.6624 | 0.23346 | 122.8638 | 122.8592 | 0.19684 | 0 | 122.6852 | 122.6715 | 0.13275 | 122.8226 | 122.7768 | 0.10529 | 0.10986 | 123.0927 | 122.8592 | 122.8363 | -0.19684 | 122.9919 | 122.9691 | 122.8592 | -0.18768
2009.4844 | 122.937 | -122.7127 | 0.17853 | 0.15198 | 0.022965 | 0.0044434 | 0.0034093 | -0.0062612 | -0.00163 | -0.0041657 | 0.19356 | -0.011059 | -0.0071072 | -0.0015488 | 0.0068851 | -0.012085 | 0.15564 | 0.15564 | 0.12817 | 0.11902 | 0.21057 | 0.032043 | -0.10529 | 0.16937 | 0.15106 | 0.073242 | 0.15564 | 0.11444 | -0.064087 | -0.091553 | 122.7448 | 122.6074 | 0.032043 | 122.8683 | 122.8317 | 0.22431 | -0.022888 | 122.6486 | 122.6212 | -0.022888 | 122.8821 | 122.7859 | 0.16479 | -0.064087 | 122.9233 | 122.8683 | 122.8409 | -0.28381 | 122.8683 | 122.8271 | 122.8638 | -0.27008
2011.1875 | 123.0103 | -122.7081 | 0.15564 | 0.022278 | 0.024033 | 0.0048706 | 0.0072547 | -0.0045522 | -0.0037662 | -0.0063019 | 0.056228 | -0.0099911 | -0.0039028 | -0.0026168 | 4.9132e-05 | -0.012726 | 0.13733 | 0.15106 | 0.14191 | 0.14648 | 0.29755 | 0.10071 | -0.068665 | 0.16022 | 0.18768 | 0.12817 | 0.23346 | 0.1831 | 0 | -0.032043 | 122.8088 | 122.6395 | 0.14191 | 122.8592 | 122.8546 | 0.21515 | -0.018311 | 122.7081 | 122.6761 | 0.077819 | 122.8683 | 122.8363 | 0.16022 | 0.027465 | 123.0057 | 122.8455 | 122.85 | -0.22431 | 122.9416 | 122.8912 | 122.8958 | -0.18768
2012.9375 | 122.9416 | -122.7127 | 0.17853 | -0.046387 | 0.024887 | 0.0055114 | 0.0012731 | -0.0056204 | 0.0039242 | -0.0054475 | -0.065842 | -0.0065731 | -0.0075344 | -0.00048061 | 0.0085941 | -0.016571 | 0.1831 | 0.09613 | 0.054932 | 0.10529 | 0.27924 | 0.059509 | -0.09613 | 0.091553 | 0.064087 | -0.041199 | 0.20142 | 0.16479 | -0.073242 | -0.11902 | 122.7722 | 122.6166 | 0.10071 | 122.8088 | 122.818 | 0.20142 | 0.004577 | 122.6395 | 122.5937 | 0.022888 | 122.8043 | 122.6715 | 0.07782 | -0.013733 | 122.9919 | 122.8958 | 122.7676 | -0.27466 | 122.9141 | 122.8775 | 122.7768 | -0.29755
2014.625 | 123.0057 | -122.699 | 0.16022 | -0.16083 | 0.023178 | 0.0035888 | 0.0074683 | -0.0062612 | -0.0039798 | -0.0058747 | -0.14977 | -0.0117 | -0.0045438 | -0.001976 | 0.0013309 | -0.013794 | 0.22888 | 0.27466 | 0.2243 | 0.22888 | 0.33417 | 0.13733 | -0.009155 | 0.2243 | 0.28381 | 0.16022 | 0.25177 | 0.21515 | 0.032043 | -0.036621 | 122.8363 | 122.6898 | 0.17395 | 122.9736 | 122.9279 | 0.23804 | 0.068665 | 122.731 | 122.6624 | 0.091553 | 122.9233 | 122.8592 | 0.19684 | 0.054932 | 123.0331 | 122.9279 | 122.9233 | -0.16937 | 122.9507 | 122.9141 | 122.9828 | -0.19684
2016.3281 | 122.9507 | -122.7173 | 0.18768 | -0.069275 | 0.025955 | 0.0057252 | 0.0029821 | -0.0062612 | 0.0058468 | -0.0037385 | -0.13451 | -0.0078549 | -0.0045438 | -0.0017624 | 0.0079531 | -0.014007 | 0.18768 | 0.12817 | 0.073242 | 0.11902 | 0.29297 | 0.073242 | -0.10071 | 0.13275 | 0.1236 | 0.009155 | 0.21515 | 0.19226 | -0.050354 | -0.1236 | 122.7905 | 122.6166 | 0.10529 | 122.8455 | 122.8363 | 0.21973 | 0 | 122.6669 | 122.5937 | 0.027466 | 122.85 | 122.7264 | 0.13275 | 0.004578 | 123.0103 | 122.905 | 122.7905 | -0.28839 | 122.9324 | 122.9095 | 122.8409 | -0.31128
2018.0156 | 123.0423 | -122.7127 | 0.14191 | -0.25238 | 0.025101 | 0.0048706 | 0.0098181 | -0.0094656 | -0.00034818 | -0.0039521 | -0.25658 | -0.0093503 | -0.0041164 | 0.00080099 | 0.00090353 | -0.010162 | 0.16937 | 0.17853 | 0.10986 | 0.16937 | 0.3891 | 0.11444 | -0.045776 | 0.12817 | 0.14191 | 0.054932 | 0.29297 | 0.27008 | 0 | -0.064087 | 122.8271 | 122.6669 | 0.24719 | 122.8912 | 122.8821 | 0.21515 | 0.027466 | 122.7127 | 122.6486 | 0.15106 | 122.8409 | 122.7676 | 0.11902 | 0.12817 | 123.1018 | 122.8821 | 122.8226 | -0.18768 | 123.0057 | 122.9828 | 122.8546 | -0.20599
2019.7031 | 123.0423 | -122.6624 | 0.15106 | -0.023499 | 0.021256 | 0.0067932 | 0.0059729 | -0.0062612 | -0.0052616 | -0.0065155 | 0.025711 | -0.010418 | -0.003262 | -0.00090781 | 0.00047633 | -0.010803 | 0.11902 | 0.1831 | 0.16479 | 0.16022 | 0.28839 | 0.09613 | -0.050354 | 0.19684 | 0.22888 | 0.17395 | 0.21973 | 0.20599 | 0.004578 | -0.041199 | 122.7585 | 122.612 | 0.13733 | 122.8455 | 122.8226 | 0.21057 | -0.032043 | 122.6669 | 122.6212 | 0.068665 | 122.8592 | 122.8363 | 0.21515 | 0.054932 | 122.9507 | 122.7814 | 122.8271 | -0.20142 | 122.8821 | 122.8683 | 122.8912 | -0.19226
2021.4062 | 123.0103 | -122.6944 | 0.16479 | -0.18372 | 0.02211 | 0.0044434 | 0.0083227 | -0.0051932 | -0.0037662 | -0.0063019 | -0.2108 | -0.011059 | -0.0045438 | -0.001976 | 0.0030399 | -0.013153 | 0.2243 | 0.25177 | 0.21057 | 0.22888 | 0.32044 | 0.13275 | -0.022888 | 0.20599 | 0.24719 | 0.14648 | 0.27008 | 0.24719 | 0.041199 | -0.032043 | 122.8271 | 122.6715 | 0.15564 | 122.9462 | 122.9233 | 0.25177 | 0.059509 | 122.7356 | 122.6624 | 0.10529 | 122.9004 | 122.8409 | 0.17853 | 0.082397 | 123.0148 | 122.9187 | 122.905 | -0.18768 | 122.9645 | 122.9416 | 122.9416 | -0.19684
2023.0938 | 122.9141 | -122.731 | 0.18768 | 0.11383 | 0.021042 | 0.0040162 | 0.0017005 | -0.0051932 | -0.0041934 | -0.0065155 | 0.102 | -0.010205 | -0.0062528 | 0.00016019 | 0.0045351 | -0.011017 | 0.14191 | 0.16022 | 0.13275 | 0.11902 | 0.23346 | 0.041199 | -0.09613 | 0.16937 | 0.17395 | 0.091553 | 0.18768 | 0.15564 | -0.013733 | -0.082397 | 122.7722 | 122.6349 | 0.045776 | 122.8912 | 122.85 | 0.21515 | -0.045776 | 122.7173 | 122.6486 | 0 | 122.9004 | 122.8226 | 0.17395 | -0.032043 | 122.9645 | 122.8729 | 122.8638 | -0.28381 | 122.9187 | 122.8867 | 122.905 | -0.27008
2024.8125 | 122.9416 | -122.7173 | 0.18768 | -0.069275 | 0.024674 | 0.0065796 | 0.0046911 | -0.0073294 | 0.0041378 | -0.0054475 | -0.13451 | -0.0074277 | -0.0056118 | 0.00016019 | 0.0085941 | -0.014435 | 0.18768 | 0.14191 | 0.082397 | 0.14191 | 0.28839 | 0.059509 | -0.10071 | 0.1236 | 0.11444 | 0.004578 | 0.21973 | 0.19226 | -0.041199 | -0.10986 | 122.7768 | 122.6166 | 0.10071 | 122.8592 | 122.8592 | 0.24262 | 0 | 122.6761 | 122.6074 | 0.032044 | 122.8409 | 122.7219 | 0.11444 | 0.004578 | 123.0057 | 122.905 | 122.7997 | -0.28839 | 122.937 | 122.9095 | 122.8317 | -0.29755
2026.5156 | 122.9599 | -122.7173 | 0.19226 | -0.099793 | 0.027878 | 0.004657 | 0.0027685 | -0.0079702 | 0.001788 | -0.0033111 | -0.14977 | -0.0082821 | -0.0071072 | -0.0017624 | 0.0081667 | -0.011871 | 0.19684 | 0.13275 | 0.09613 | 0.13275 | 0.29755 | 0.054932 | -0.09613 | 0.13275 | 0.12817 | 0.009155 | 0.21515 | 0.17853 | -0.054932 | -0.10986 | 122.7722 | 122.6212 | 0.10528 | 122.85 | 122.85 | 0.22888 | 0.004577 | 122.6624 | 122.6074 | 0.022888 | 122.85 | 122.7264 | 0.11902 | -0.013733 | 123.0148 | 122.9141 | 122.8134 | -0.28839 | 122.9324 | 122.8958 | 122.8455 | -0.30212
2028.2031 | 123.0606 | -122.6715 | 0.15564 | -0.11505 | 0.023178 | 0.0059388 | 0.0096045 | -0.0062612 | -0.0065434 | -0.0052337 | -0.058212 | -0.010632 | -0.0053982 | -0.001976 | -0.0020871 | -0.01123 | 0.21973 | 0.26093 | 0.23346 | 0.2243 | 0.32501 | 0.13733 | -0.018311 | 0.26093 | 0.30212 | 0.20599 | 0.25177 | 0.20599 | 0.027466 | -0.032043 | 122.8088 | 122.6532 | 0.16937 | 122.9324 | 122.8958 | 0.24261 | 0.064087 | 122.699 | 122.6395 | 0.09613 | 122.9324 | 122.8775 | 0.23804 | 0.050354 | 122.9965 | 122.8912 | 122.905 | -0.17395 | 122.9233 | 122.8775 | 122.9736 | -0.18768
2029.8906 | 122.9828 | -122.7127 | 0.17395 | -0.00061023 | 0.022751 | 0.007434 | 0.0066137 | -0.0049796 | -0.0059024 | -0.0056611 | 0.056228 | -0.010846 | -0.006039 | -0.0028306 | 0.0023989 | -0.011657 | 0.14648 | 0.14648 | 0.13275 | 0.15106 | 0.29755 | 0.082397 | -0.064087 | 0.14648 | 0.17395 | 0.10986 | 0.24719 | 0.21057 | -0.018311 | -0.045776 | 122.7951 | 122.6486 | 0.1236 | 122.8592 | 122.8638 | 0.21515 | -0.027466 | 122.6944 | 122.6669 | 0.073242 | 122.8592 | 122.8226 | 0.15564 | 0.036621 | 123.0103 | 122.8592 | 122.8455 | -0.23804 | 122.9599 | 122.9233 | 122.8867 | -0.21973
2031.5781 | 123.0469 | -122.7036 | 0.16937 | -0.14557 | 0.02681 | 0.0035888 | 0.0061865 | -0.0051932 | 0.0039242 | -0.0035249 | -0.18028 | -0.0082821 | -0.0071072 | 0.00037379 | 0.0062441 | -0.014435 | 0.20142 | 0.14648 | 0.10986 | 0.15106 | 0.32501 | 0.050354 | -0.091553 | 0.14191 | 0.14648 | 0.032043 | 0.24261 | 0.19684 | -0.050354 | -0.09613 | 122.7539 | 122.612 | 0.15564 | 122.85 | 122.8546 | 0.24261 | 0.032043 | 122.6532 | 122.6074 | 0.073242 | 122.8455 | 122.7356 | 0.12817 | 0.027465 | 123.0286 | 122.905 | 122.8134 | -0.26093 | 122.9462 | 122.9004 | 122.85 | -0.2655
2033.2656 | 123.0331 | -122.7081 | 0.16479 | -0.22186 | 0.026169 | 0.0050842 | 0.0066137 | -0.0049796 | 0.00029262 | -0.0037385 | -0.23369 | -0.010205 | -0.0028348 | -0.0013352 | 0.0017581 | -0.011871 | 0.16937 | 0.15106 | 0.10529 | 0.15564 | 0.37994 | 0.12817 | -0.064087 | 0.13733 | 0.16479 | 0.050354 | 0.31128 | 0.26093 | -0.009155 | -0.068665 | 122.8363 | 122.644 | 0.21515 | 122.8592 | 122.8638 | 0.21973 | 0.004578 | 122.699 | 122.6395 | 0.14648 | 122.8455 | 122.7585 | 0.11902 | 0.09613 | 123.0881 | 122.8775 | 122.8134 | -0.22888 | 123.0194 | 122.9691 | 122.8729 | -0.23346
2035 | 122.9874 | -122.699 | 0.1831 | 0.052795 | 0.021896 | 0.0038024 | 0.0083227 | -0.0054068 | -0.005048 | -0.0073701 | 0.086746 | -0.011273 | -0.003262 | 0.00016019 | -0.00080527 | -0.012939 | 0.14648 | 0.15564 | 0.15106 | 0.15106 | 0.31128 | 0.073242 | -0.059509 | 0.16022 | 0.18768 | 0.11444 | 0.21973 | 0.19226 | -0.009155 | -0.07782 | 122.7722 | 122.6395 | 0.12817 | 122.8546 | 122.85 | 0.21057 | -0.036621 | 122.6898 | 122.6212 | 0.036622 | 122.8592 | 122.8134 | 0.19226 | 0.009156 | 123.0103 | 122.8455 | 122.85 | -0.24261 | 122.9187 | 122.8912 | 122.8867 | -0.26092
2036.6875 | 122.9874 | -122.7036 | 0.17853 | 0.12909 | 0.024033 | 0.004657 | 0.0019141 | -0.0064748 | 0.0032834 | -0.0045929 | 0.18593 | -0.0082821 | -0.0062528 | 0.00037379 | 0.0083805 | -0.013366 | 0.10529 | 0.036621 | 0.027466 | 0.036621 | 0.27008 | 0.009155 | -0.13275 | 0.13275 | 0.091553 | 0.013733 | 0.1831 | 0.15564 | -0.064087 | -0.13275 | 122.7127 | 122.5708 | 0.091553 | 122.7402 | 122.7402 | 0.16937 | -0.073242 | 122.6395 | 122.5708 | 0.004577 | 122.8363 | 122.7173 | 0.14648 | -0.022888 | 122.9736 | 122.8088 | 122.731 | -0.31128 | 122.8867 | 122.8592 | 122.7951 | -0.31128
2038.375 | 122.9507 | -122.7356 | 0.18768 | -0.023499 | 0.023819 | 0.0038024 | 0.0019141 | -0.005834 | 0.0030698 | -0.0060883 | -0.065842 | -0.0087093 | -0.008389 | -0.00048061 | 0.0062441 | -0.014007 | 0.16022 | 0.11444 | 0.073242 | 0.11902 | 0.29297 | 0.045776 | -0.086975 | 0.10529 | 0.086975 | -0.027466 | 0.20599 | 0.17853 | -0.054932 | -0.11444 | 122.7814 | 122.6486 | 0.10529 | 122.85 | 122.8546 | 0.20599 | -0.027466 | 122.6807 | 122.6212 | 0.018311 | 122.8409 | 122.7081 | 0.086975 | -0.009155 | 123.0286 | 122.8958 | 122.8088 | -0.27466 | 122.9416 | 122.9141 | 122.8226 | -0.30212
2040.0781 | 123.0606 | -122.6761 | 0.16479 | -0.19135 | 0.023392 | 0.0048706 | 0.0061865 | -0.0069022 | 0.00093342 | -0.0033111 | -0.10399 | -0.0059323 | -0.0053982 | -0.00069421 | 0.0058169 | -0.011871 | 0.1831 | 0.14191 | 0.091553 | 0.15106 | 0.3479 | 0.10071 | -0.07782 | 0.1236 | 0.14648 | 0.032043 | 0.24261 | 0.21973 | -0.027466 | -0.10529 | 122.7768 | 122.5983 | 0.1831 | 122.818 | 122.8271 | 0.22888 | 0.01831 | 122.6486 | 122.5708 | 0.07782 | 122.7997 | 122.7081 | 0.13733 | 0.054932 | 123.024 | 122.8592 | 122.7676 | -0.24261 | 122.9187 | 122.8958 | 122.8226 | -0.27008
2041.7812 | 122.9874 | -122.731 | 0.16937 | 0.1825 | 0.024674 | 0.0055114 | 0.0034093 | -0.005834 | -0.00056178 | -0.0060883 | 0.15541 | -0.010418 | -0.0058254 | -0.0015488 | 0.0038943 | -0.011017 | 0.11444 | 0.11444 | 0.091553 | 0.086975 | 0.21973 | 0.022888 | -0.11444 | 0.14648 | 0.16479 | 0.07782 | 0.17395 | 0.14191 | -0.036621 | -0.086975 | 122.7539 | 122.6166 | 0.050354 | 122.8455 | 122.818 | 0.20142 | -0.054932 | 122.6944 | 122.644 | 0.004577 | 122.8775 | 122.8088 | 0.16479 | -0.027466 | 122.9507 | 122.8455 | 122.8226 | -0.28381 | 122.905 | 122.8729 | 122.8958 | -0.25635
2043.4688 | 122.9782 | -122.7356 | 0.16479 | 0.11383 | 0.024246 | 0.0033752 | 0.0044775 | -0.0079702 | -0.00013458 | -0.0039521 | 0.063858 | -0.0097775 | -0.0030484 | -0.00048061 | 0.0049625 | -0.012298 | 0.054932 | 0 | -0.004578 | 0.041199 | 0.25635 | 0 | -0.14191 | 0.068665 | 0.036621 | -0.036621 | 0.19226 | 0.1831 | -0.054932 | -0.12817 | 122.7356 | 122.5937 | 0.091553 | 122.7356 | 122.7768 | 0.18311 | -0.10986 | 122.6807 | 122.6074 | 0.027466 | 122.8043 | 122.699 | 0.091553 | 0.01831 | 122.9919 | 122.7905 | 122.731 | -0.3067 | 122.9279 | 122.9187 | 122.7722 | -0.29297
2045.1562 | 123.0652 | -122.6715 | 0.15106 | -0.2066 | 0.021683 | 0.0059388 | 0.0078955 | -0.0062612 | 0.00029262 | -0.0052337 | -0.18791 | -0.0089229 | -0.0068936 | -0.00069421 | 0.0028263 | -0.010803 | 0.15564 | 0.14648 | 0.086975 | 0.15106 | 0.37994 | 0.09613 | -0.050354 | 0.11902 | 0.15564 | 0.041199 | 0.27924 | 0.24261 | -0.022888 | -0.086975 | 122.7676 | 122.6212 | 0.22888 | 122.818 | 122.8226 | 0.20142 | 0.004578 | 122.6486 | 122.5845 | 0.12817 | 122.7905 | 122.7127 | 0.12817 | 0.091553 | 123.0515 | 122.8271 | 122.7585 | -0.20142 | 122.9507 | 122.9141 | 122.8271 | -0.23804
2046.8438 | 122.937 | -122.7448 | 0.17853 | 0.075684 | 0.02446 | 0.002948 | 0.0042639 | -0.007543 | 0.00029262 | -0.0058747 | 0.063858 | -0.0091367 | -0.0053982 | -0.00026701 | 0.0060305 | -0.011444 | 0.027466 | 0.013733 | 0 | 0.041199 | 0.27466 | 0.013733 | -0.15106 | 0.036621 | 0.004578 | -0.050354 | 0.21057 | 0.17395 | -0.10071 | -0.13275 | 122.7585 | 122.5937 | 0.09613 | 122.7585 | 122.7859 | 0.19226 | -0.15106 | 122.644 | 122.612 | 0.032043 | 122.7814 | 122.6944 | 0.082397 | -0.004578 | 123.0194 | 122.7722 | 122.7448 | -0.32959 | 122.9553 | 122.9187 | 122.7493 | -0.31128
2048.5781 | 122.9233 | -122.7356 | 0.18768 | -0.046387 | 0.025528 | 0.0050842 | 0.0046911 | -0.0081838 | -0.00013458 | -0.0060883 | -0.035324 | -0.0082821 | -0.0028348 | -0.00090781 | 0.0036807 | -0.011657 | 0.11444 | 0.10986 | 0.059509 | 0.10071 | 0.29297 | 0.064087 | -0.11444 | 0.07782 | 0.073242 | -0.032043 | 0.20142 | 0.17395 | -0.073242 | -0.13275 | 122.7997 | 122.6212 | 0.10529 | 122.8455 | 122.8363 | 0.21515 | -0.073242 | 122.6624 | 122.6028 | 0.013733 | 122.8134 | 122.7036 | 0.10071 | -0.013733 | 123.0286 | 122.85 | 122.7951 | -0.30212 | 122.937 | 122.9095 | 122.8088 | -0.32043
2050.2656 | 123.056 | -122.6944 | 0.19226 | -0.26001 | 0.023178 | 0.0042298 | 0.0087499 | -0.0069022 | -0.002698 | -0.0058747 | -0.20317 | -0.0087093 | -0.0034756 | -0.00048061 | 0.0026125 | -0.012085 | 0.15106 | 0.14648 | 0.10529 | 0.15564 | 0.38452 | 0.10986 | -0.036621 | 0.11444 | 0.14648 | 0.041199 | 0.27924 | 0.25177 | -0.004578 | -0.054932 | 122.8043 | 122.6578 | 0.19226 | 122.8409 | 122.85 | 0.19226 | -0.041199 | 122.6898 | 122.6395 | 0.086975 | 122.8088 | 122.7356 | 0.096131 | 0.059509 | 123.0789 | 122.8455 | 122.7997 | -0.22888 | 122.9736 | 122.9462 | 122.8409 | -0.24719
2051.9844 | 122.937 | -122.731 | 0.17395 | 0.037537 | 0.022751 | 0.0044434 | 0.0068273 | -0.0069022 | -0.006757 | -0.0095063 | 0.16304 | -0.010632 | -0.0030484 | 0.00016019 | 0.00068993 | -0.010376 | 0.11444 | 0.15106 | 0.13733 | 0.14191 | 0.27466 | 0.086975 | -0.064087 | 0.15564 | 0.18768 | 0.09613 | 0.21515 | 0.18768 | 0.013733 | -0.045776 | 122.818 | 122.6669 | 0.10071 | 122.8821 | 122.8729 | 0.20599 | -0.059509 | 122.7448 | 122.6852 | 0.041199 | 122.8867 | 122.8271 | 0.14191 | 0.013733 | 123.0057 | 122.8455 | 122.8683 | -0.23804 | 122.9462 | 122.9187 | 122.9187 | -0.21973
2053.6719 | 122.9691 | -122.7264 | 0.1831 | 0.12146 | 0.024033 | 0.0040162 | 0.0027685 | -0.0064748 | -0.0012028 | -0.0071563 | 0.19356 | -0.010205 | -0.0075344 | 0.0022964 | 0.0045351 | -0.012939 | 0.12817 | 0.14191 | 0.11444 | 0.11444 | 0.21515 | 0.045776 | -0.11902 | 0.16479 | 0.16479 | 0.086975 | 0.16022 | 0.12817 | -0.073242 | -0.11902 | 122.7722 | 122.6074 | 0.032044 | 122.8683 | 122.8409 | 0.23346 | -0.054931 | 122.6532 | 122.6074 | -0.022888 | 122.8912 | 122.8134 | 0.20599 | -0.054931 | 122.9416 | 122.8546 | 122.8409 | -0.30212 | 122.8867 | 122.8546 | 122.8912 | -0.30212
2055.3594 | 122.9279 | -122.7127 | 0.17395 | 0.029907 | 0.025742 | 0.0035888 | 0.0027685 | -0.0060476 | 0.0032834 | -0.0054475 | -0.0048066 | -0.010205 | -0.004971 | -0.00048061 | 0.0075259 | -0.012939 | 0.059509 | 0.004578 | -0.022888 | 0.045776 | 0.29297 | 0.013733 | -0.14191 | 0.027466 | 0 | -0.054932 | 0.21057 | 0.17853 | -0.086975 | -0.14191 | 122.7264 | 122.5708 | 0.11902 | 122.7173 | 122.7585 | 0.18768 | -0.11444 | 122.6257 | 122.5708 | 0.036621 | 122.7402 | 122.6578 | 0.086975 | 0.004578 | 123.0057 | 122.7722 | 122.6898 | -0.31586 | 122.9233 | 122.8912 | 122.7127 | -0.31586
2057.0781 | 122.9736 | -122.7356 | 0.17395 | 0.12146 | 0.025742 | 0.0059388 | 0.0014867 | -0.0054068 | -0.00056178 | -0.0073701 | 0.079117 | -0.0080685 | -0.0041164 | -0.00026701 | 0.0060305 | -0.011871 | 0.045776 | 0.013733 | -0.018311 | 0.050354 | 0.2655 | 0 | -0.15564 | 0.073242 | 0.032043 | -0.022888 | 0.21057 | 0.17853 | -0.073242 | -0.11444 | 122.7356 | 122.58 | 0.091553 | 122.7493 | 122.7859 | 0.20599 | -0.12817 | 122.6624 | 122.6212 | 0.036621 | 122.8088 | 122.7127 | 0.091553 | 0.004578 | 123.0011 | 122.7814 | 122.7173 | -0.32959 | 122.9462 | 122.9141 | 122.7676 | -0.28839
2058.7656 | 123.0698 | -122.6898 | 0.16479 | -0.16846 | 0.025955 | 0.0027344 | 0.0072547 | -0.0062612 | -0.00098918 | -0.0041657 | -0.14977 | -0.0065731 | -0.0034756 | 0.0010148 | 0.0038943 | -0.013153 | 0.16022 | 0.14648 | 0.09613 | 0.16022 | 0.3479 | 0.07782 | -0.07782 | 0.11444 | 0.15564 | 0.041199 | 0.21973 | 0.20599 | -0.032043 | -0.10071 | 122.7676 | 122.612 | 0.1831 | 122.8363 | 122.85 | 0.23804 | -0.004578 | 122.6578 | 122.5891 | 0.054932 | 122.8043 | 122.731 | 0.14191 | 0.041199 | 123.0377 | 122.85 | 122.7859 | -0.24261 | 122.9095 | 122.8958 | 122.8455 | -0.2655
2060.4688 | 122.937 | -122.7402 | 0.18768 | -0.054016 | 0.028305 | 0.0055114 | 0.0046911 | -0.0064748 | 0.001788 | -0.0043793 | -0.073471 | -0.0087093 | -0.00668 | -0.0011216 | 0.0058169 | -0.013153 | 0.13733 | 0.1236 | 0.073242 | 0.11444 | 0.30212 | 0.059509 | -0.09613 | 0.086975 | 0.091553 | -0.009155 | 0.22888 | 0.18768 | -0.054932 | -0.10529 | 122.7997 | 122.644 | 0.11444 | 122.8638 | 122.8546 | 0.21057 | -0.050354 | 122.6852 | 122.6349 | 0.041199 | 122.8271 | 122.731 | 0.096131 | 0 | 123.0423 | 122.8775 | 122.8134 | -0.28381 | 122.9691 | 122.9279 | 122.8317 | -0.29297
2062.1562 | 122.9324 | -122.7676 | 0.1831 | 0.1062 | 0.020401 | 0.0050842 | 0.0038367 | -0.0069022 | -0.0080386 | -0.0069427 | 0.17067 | -0.0095639 | -0.0073208 | -0.0038986 | 0.0026125 | -0.010162 | 0.11902 | 0.16479 | 0.12817 | 0.13275 | 0.2655 | 0.07782 | -0.07782 | 0.15106 | 0.17395 | 0.10071 | 0.21973 | 0.1831 | 0 | -0.068665 | 122.8455 | 122.6898 | 0.082398 | 122.9324 | 122.9004 | 0.21057 | -0.064086 | 122.7676 | 122.699 | 0.036622 | 122.9187 | 122.8683 | 0.16937 | 0 | 123.0331 | 122.8867 | 122.8958 | -0.26092 | 122.9874 | 122.9507 | 122.9416 | -0.25177
2063.8281 | 123.0698 | -122.6944 | 0.15106 | -0.14557 | 0.028305 | 0.0020936 | 0.0074683 | -0.0060476 | 0.001788 | -0.0054475 | -0.15739 | -0.0078549 | -0.0047574 | -0.0011216 | 0.0041079 | -0.014435 | 0.18768 | 0.1236 | 0.091553 | 0.15106 | 0.35706 | 0.07782 | -0.10529 | 0.13733 | 0.14191 | 0.032043 | 0.24719 | 0.21515 | -0.045776 | -0.086975 | 122.7722 | 122.5891 | 0.20599 | 122.818 | 122.8455 | 0.25635 | 0.036621 | 122.6486 | 122.6074 | 0.09613 | 122.8317 | 122.7264 | 0.11902 | 0.064087 | 123.0515 | 122.8821 | 122.7859 | -0.25635 | 122.9416 | 122.9095 | 122.8363 | -0.23804
2065.5156 | 123.024 | -122.7081 | 0.15106 | -0.22949 | 0.026169 | 0.006366 | 0.0053321 | -0.0043386 | -0.0037662 | -0.0063019 | -0.15739 | -0.0093503 | -0.0047574 | -0.001976 | 0.0011173 | -0.012085 | 0.15564 | 0.16479 | 0.13275 | 0.16937 | 0.36621 | 0.10529 | -0.050354 | 0.12817 | 0.16022 | 0.064087 | 0.29755 | 0.2655 | -0.022888 | -0.059509 | 122.8134 | 122.6578 | 0.21515 | 122.8729 | 122.8775 | 0.21973 | 0.004578 | 122.6852 | 122.6486 | 0.14648 | 122.8363 | 122.7722 | 0.1236 | 0.11444 | 123.0743 | 122.8638 | 122.8409 | -0.20142 | 123.0057 | 122.9736 | 122.8683 | -0.21057
2067.1875 | 122.9462 | -122.7264 | 0.17853 | 0.060425 | 0.021469 | 0.004657 | 0.0055457 | -0.0090384 | -0.0076114 | -0.0073701 | 0.102 | -0.011059 | -0.0088162 | -0.0024032 | 0.0023989 | -0.0097348 | 0.12817 | 0.16022 | 0.12817 | 0.13733 | 0.27008 | 0.086975 | -0.068665 | 0.16022 | 0.17853 | 0.11444 | 0.21515 | 0.19226 | -0.013733 | -0.064087 | 122.8134 | 122.6578 | 0.091553 | 122.8867 | 122.8638 | 0.20599 | -0.050354 | 122.7127 | 122.6624 | 0.036621 | 122.8867 | 122.8409 | 0.17853 | 0.013733 | 122.9965 | 122.8546 | 122.8546 | -0.24719 | 122.9416 | 122.9187 | 122.905 | -0.24261
2068.9062 | 122.9736 | -122.731 | 0.17853 | 0.075684 | 0.025314 | 0.0052978 | 0.0029821 | -0.0071158 | -0.00013458 | -0.0069427 | 0.11726 | -0.0097775 | -0.00668 | 0.00080099 | 0.0049625 | -0.012512 | 0.10529 | 0.027466 | -0.013733 | 0.054932 | 0.27924 | 0.018311 | -0.15564 | 0.10071 | 0.045776 | -0.022888 | 0.1831 | 0.16937 | -0.068665 | -0.13733 | 122.7493 | 122.5754 | 0.10071 | 122.7585 | 122.7859 | 0.21057 | -0.073242 | 122.6624 | 122.5937 | 0.004577 | 122.8317 | 122.7081 | 0.11444 | -0.009155 | 123.0103 | 122.8363 | 122.7173 | -0.33417 | 122.9141 | 122.9004 | 122.7768 | -0.31586
2070.5938 | 123.0652 | -122.7081 | 0.16022 | -0.076904 | 0.025528 | 0.0048706 | 0.0038367 | -0.005834 | 0.0011472 | -0.0050201 | -0.14977 | -0.0089229 | -0.0041164 | -0.00090781 | 0.0058169 | -0.014435 | 0.18768 | 0.13733 | 0.10071 | 0.14191 | 0.31586 | 0.064087 | -0.086975 | 0.13275 | 0.14648 | 0.041199 | 0.21973 | 0.21515 | -0.045776 | -0.086975 | 122.7722 | 122.6212 | 0.15564 | 122.8455 | 122.85 | 0.22888 | 0.027466 | 122.6624 | 122.6212 | 0.05951 | 122.8409 | 122.7493 | 0.12817 | 0.054932 | 123.024 | 122.8958 | 122.8088 | -0.24719 | 122.9279 | 122.9233 | 122.8546 | -0.24719
2072.2812 | 123.0835 | -122.7127 | 0.15106 | -0.22186 | 0.025955 | 0.0055114 | 0.0068273 | -0.0066884 | 7.902e-05 | -0.0058747 | -0.18028 | -0.0097775 | -0.0039028 | -5.3406e-05 | 0.0030399 | -0.012298 | 0.1831 | 0.11902 | 0.086975 | 0.16022 | 0.36163 | 0.10529 | -0.054932 | 0.11444 | 0.14648 | 0.036621 | 0.2655 | 0.24261 | -0.018311 | -0.059509 | 122.818 | 122.6578 | 0.21057 | 122.8317 | 122.8729 | 0.21515 | 0.032043 | 122.6944 | 122.6532 | 0.11444 | 122.8271 | 122.7493 | 0.09613 | 0.091553 | 123.0743 | 122.8958 | 122.7997 | -0.20599 | 122.9782 | 122.9553 | 122.8592 | -0.21057
2074 | 122.9416 | -122.7448 | 0.20599 | 0.068054 | 0.025101 | 0.004657 | 0.0036231 | -0.0060476 | 0.003497 | -0.0054475 | 0.018082 | -0.0097775 | -0.004971 | -0.0024032 | 0.0060305 | -0.013794 | 0.064087 | 0.018311 | -0.004578 | 0.041199 | 0.27924 | 0.027466 | -0.15106 | 0.041199 | 0.018311 | -0.054932 | 0.20599 | 0.20142 | -0.068665 | -0.14648 | 122.7722 | 122.5937 | 0.073242 | 122.7631 | 122.7859 | 0.19226 | -0.14191 | 122.6761 | 122.5983 | 0 | 122.7859 | 122.6898 | 0.091552 | -0.004578 | 123.024 | 122.8088 | 122.7402 | -0.35706 | 122.9507 | 122.9462 | 122.7631 | -0.35248
2075.6875 | 123.0286 | -122.699 | 0.13733 | -0.2066 | 0.022965 | 0.0048706 | 0.010673 | -0.0064748 | -0.006116 | -0.0065155 | -0.096359 | -0.010846 | -0.003262 | -0.003685 | 0.00026273 | -0.011871 | 0.2243 | 0.28839 | 0.25635 | 0.23346 | 0.32959 | 0.14191 | -0.004578 | 0.21973 | 0.29755 | 0.19226 | 0.25177 | 0.2243 | 0.027466 | -0.032043 | 122.8409 | 122.6944 | 0.19226 | 122.9874 | 122.9324 | 0.23804 | 0.086975 | 122.7264 | 122.6669 | 0.11444 | 122.9187 | 122.8912 | 0.2243 | 0.086975 | 123.0286 | 122.9233 | 122.9553 | -0.14191 | 122.9507 | 122.9233 | 122.9965 | -0.16937
2077.4375 | 123.024 | -122.6898 | 0.15106 | -0.21423 | 0.024246 | 0.0055114 | 0.0072547 | -0.0069022 | -0.0041934 | -0.0069427 | -0.12688 | -0.014264 | -0.0053982 | 0.00037379 | 0.00026273 | -0.0097348 | 0.22888 | 0.29755 | 0.25177 | 0.22888 | 0.32959 | 0.12817 | -0.009155 | 0.22888 | 0.29755 | 0.1831 | 0.24719 | 0.21515 | 0.041199 | -0.036621 | 122.818 | 122.6807 | 0.17853 | 122.9874 | 122.9187 | 0.23804 | 0.07782 | 122.731 | 122.6532 | 0.09613 | 122.9187 | 122.8729 | 0.21973 | 0.064087 | 123.0194 | 122.9187 | 122.9416 | -0.16022 | 122.937 | 122.905 | 122.9874 | -0.18768
2079.1875 | 123.0881 | -122.7173 | 0.15564 | -0.16083 | 0.025101 | 0.0050842 | 0.0076819 | -0.005834 | 0.00029262 | -0.0056611 | -0.22606 | -0.0097775 | -0.0034756 | 0.00058739 | 0.0043215 | -0.012939 | 0.16937 | 0.1236 | 0.09613 | 0.16479 | 0.35248 | 0.086975 | -0.064087 | 0.11902 | 0.14191 | 0.036621 | 0.26093 | 0.24261 | -0.022888 | -0.068665 | 122.8043 | 122.6532 | 0.19684 | 122.8409 | 122.8821 | 0.22888 | 0.013733 | 122.6944 | 122.6486 | 0.10529 | 122.8363 | 122.7539 | 0.10529 | 0.086975 | 123.0698 | 122.8867 | 122.8134 | -0.21973 | 122.9782 | 122.9599 | 122.8592 | -0.22431
2080.9531 | 122.9828 | -122.7219 | 0.19226 | 0.12909 | 0.024887 | 0.0042298 | 0.0038367 | -0.0047658 | 0.0015744 | -0.0045929 | 0.025711 | -0.0078549 | -0.0043302 | -0.00026701 | 0.0060305 | -0.01358 | 0.059509 | 0.004578 | -0.018311 | 0.032043 | 0.27008 | 0 | -0.15564 | 0.073242 | 0.027466 | -0.027466 | 0.20599 | 0.16479 | -0.07782 | -0.13733 | 122.7219 | 122.5662 | 0.07782 | 122.7264 | 122.7539 | 0.18768 | -0.13275 | 122.644 | 122.5845 | 0.013733 | 122.7951 | 122.6944 | 0.10986 | -0.027466 | 122.9919 | 122.7814 | 122.7036 | -0.3479 | 122.9279 | 122.8867 | 122.7493 | -0.32959
2082.6406 | 123.056 | -122.7036 | 0.15106 | -0.16083 | 0.025314 | 0.0050842 | 0.0040503 | -0.0098928 | 0.0015744 | -0.0037385 | -0.19554 | -0.0089229 | -0.006039 | -0.00069421 | 0.0060305 | -0.01123 | 0.17395 | 0.13275 | 0.07782 | 0.14191 | 0.32959 | 0.073242 | -0.10071 | 0.13733 | 0.15564 | 0.045776 | 0.22888 | 0.20599 | -0.032043 | -0.10071 | 122.7768 | 122.6028 | 0.17853 | 122.8363 | 122.8455 | 0.24262 | 0.022888 | 122.6715 | 122.6028 | 0.07782 | 122.8409 | 122.7493 | 0.14648 | 0.054932 | 123.0331 | 122.8775 | 122.7814 | -0.25177 | 122.9324 | 122.9095 | 122.8592 | -0.25177
2084.3438 | 123.0377 | -122.7081 | 0.16479 | -0.19897 | 0.026383 | 0.0055114 | 0.0087499 | -0.0060476 | -0.0031254 | -0.0052337 | -0.19554 | -0.0084957 | -0.0030484 | -0.00069421 | 0.00068993 | -0.012085 | 0.14648 | 0.16022 | 0.13275 | 0.15106 | 0.35706 | 0.091553 | -0.041199 | 0.1236 | 0.15564 | 0.064087 | 0.29755 | 0.25635 | 0.004578 | -0.059509 | 122.7997 | 122.6669 | 0.19226 | 122.8683 | 122.8592 | 0.19226 | -0.018311 | 122.7127 | 122.6486 | 0.13275 | 122.8317 | 122.7722 | 0.1236 | 0.091553 | 123.0652 | 122.8546 | 122.8409 | -0.20599 | 123.0057 | 122.9645 | 122.8638 | -0.2243
2086.0938 | 122.9691 | -122.731 | 0.18768 | 0.14435 | 0.020401 | 0.0044434 | 0.0017005 | -0.007543 | -0.0037662 | -0.0052337 | 0.2317 | -0.011059 | -0.00668 | -0.00090781 | 0.0051761 | -0.012726 | 0.13275 | 0.14648 | 0.11902 | 0.12817 | 0.19684 | 0.018311 | -0.13275 | 0.14648 | 0.15564 | 0.068665 | 0.13733 | 0.10529 | -0.054932 | -0.11902 | 122.7493 | 122.5983 | 0.009155 | 122.8775 | 122.8592 | 0.26093 | -0.054932 | 122.6761 | 122.612 | -0.050354 | 122.8775 | 122.7997 | 0.18768 | -0.082397 | 122.9279 | 122.8638 | 122.85 | -0.32043 | 122.8683 | 122.8363 | 122.8867 | -0.3067
2087.8594 | 122.9645 | -122.7448 | 0.20142 | 0.083313 | 0.026596 | 0.0040162 | 0.0044775 | -0.01032 | 0.0013608 | -0.0060883 | 0.102 | -0.0070003 | -0.0039028 | -0.0017624 | 0.0062441 | -0.01123 | 0.064087 | 0 | -0.027466 | 0.045776 | 0.27008 | 0 | -0.16022 | 0.059509 | 0.018311 | -0.054932 | 0.21057 | 0.16937 | -0.082397 | -0.13733 | 122.7448 | 122.5845 | 0.068665 | 122.7448 | 122.7905 | 0.20599 | -0.13733 | 122.6624 | 122.6074 | 0.009155 | 122.8043 | 122.6898 | 0.082397 | -0.032043 | 123.0148 | 122.8088 | 122.7173 | -0.36163 | 122.9553 | 122.9141 | 122.7631 | -0.33875
2089.5469 | 122.9462 | -122.7173 | 0.19684 | -0.061646 | 0.027237 | 0.0044434 | 0.0066137 | -0.0054068 | 0.00029262 | -0.0028839 | -0.058212 | -0.0082821 | -0.0028348 | 0.00080099 | 0.0068851 | -0.013794 | 0.13275 | 0.10529 | 0.073242 | 0.10986 | 0.28839 | 0.045776 | -0.1236 | 0.10986 | 0.07782 | -0.027466 | 0.20599 | 0.17853 | -0.059509 | -0.13275 | 122.7631 | 122.5937 | 0.091553 | 122.8226 | 122.8271 | 0.23346 | -0.064087 | 122.6578 | 122.5845 | 0.009156 | 122.8271 | 122.6898 | 0.10529 | -0.01831 | 123.0057 | 122.85 | 122.7905 | -0.32043 | 122.9233 | 122.8958 | 122.7951 | -0.32959
2091.25 | 122.9187 | -122.731 | 0.17853 | 0.098572 | 0.023178 | 0.0044434 | 0.0053321 | -0.0064748 | -0.005048 | -0.0052337 | 0.20882 | -0.010418 | -0.0051846 | 0.00037379 | 0.0021853 | -0.010803 | 0.1236 | 0.1831 | 0.11902 | 0.12817 | 0.2243 | 0.045776 | -0.10071 | 0.14191 | 0.16479 | 0.086975 | 0.1831 | 0.13275 | -0.050354 | -0.091553 | 122.7768 | 122.6303 | 0.045776 | 122.9141 | 122.8592 | 0.22888 | -0.054932 | 122.6807 | 122.6395 | 0.004577 | 122.8729 | 122.818 | 0.17853 | -0.045777 | 122.9553 | 122.8546 | 122.85 | -0.27924 | 122.9141 | 122.8638 | 122.8958 | -0.27008
2093.0156 | 122.9965 | -122.7081 | 0.17395 | 0.17487 | 0.024246 | 0.0050842 | 0.0055457 | -0.0056204 | 7.902e-05 | -0.0052337 | 0.11726 | -0.0117 | -0.0058254 | -0.0015488 | 0.0047489 | -0.015075 | 0.1236 | 0.10529 | 0.082397 | 0.10071 | 0.21057 | 0.013733 | -0.13275 | 0.16022 | 0.14648 | 0.064087 | 0.16479 | 0.1236 | -0.032043 | -0.09613 | 122.7219 | 122.5754 | 0.036621 | 122.8134 | 122.8088 | 0.23346 | -0.050354 | 122.6761 | 122.612 | -0.009155 | 122.8683 | 122.7722 | 0.16022 | -0.050354 | 122.9187 | 122.8317 | 122.7905 | -0.3067 | 122.8729 | 122.8317 | 122.8546 | -0.27008
2094.7031 | 123.056 | -122.6944 | 0.15106 | -0.19135 | 0.025101 | 0.0040162 | 0.0053321 | -0.0056204 | 0.0024288 | -0.0077973 | -0.18791 | -0.0076413 | -0.004971 | -0.00048061 | 0.0051761 | -0.012085 | 0.17395 | 0.13733 | 0.091553 | 0.15106 | 0.37079 | 0.082397 | -0.045776 | 0.10986 | 0.13733 | 0.050354 | 0.25635 | 0.24261 | -0.018311 | -0.09613 | 122.7768 | 122.6486 | 0.21973 | 122.8317 | 122.8455 | 0.19684 | 0.022888 | 122.6761 | 122.5983 | 0.10529 | 122.8043 | 122.7448 | 0.14648 | 0.091553 | 123.0652 | 122.8683 | 122.7859 | -0.19684 | 122.9507 | 122.937 | 122.8317 | -0.24719
2096.4062 | 122.9691 | -122.7402 | 0.1831 | 0.052795 | 0.020187 | 0.0050842 | 0.0057593 | -0.0098928 | -0.0080386 | -0.0054475 | 0.086746 | -0.012555 | -0.0068936 | -0.00048061 | 0.00047633 | -0.0099484 | 0.1236 | 0.14648 | 0.14191 | 0.13733 | 0.28381 | 0.064087 | -0.073242 | 0.15106 | 0.16937 | 0.11444 | 0.24261 | 0.19226 | -0.009155 | -0.064087 | 122.8043 | 122.6669 | 0.10071 | 122.8867 | 122.8775 | 0.21057 | -0.059509 | 122.731 | 122.6761 | 0.05951 | 122.8912 | 122.8546 | 0.17853 | 0.009156 | 123.024 | 122.8638 | 122.8821 | -0.25635 | 122.9828 | 122.9324 | 122.9095 | -0.24719
2098.1562 | 123.024 | -122.7173 | 0.15564 | -0.19135 | 0.023819 | 0.0044434 | 0.0059729 | -0.0049796 | -0.004407 | -0.0084381 | -0.22606 | -0.0099911 | -0.0064664 | -0.0028306 | 0.0028263 | -0.012085 | 0.24719 | 0.24719 | 0.20599 | 0.22888 | 0.32501 | 0.11444 | -0.027466 | 0.19684 | 0.23346 | 0.12817 | 0.2655 | 0.25177 | 0.009155 | -0.041199 | 122.8317 | 122.6898 | 0.16937 | 122.9645 | 122.9462 | 0.25635 | 0.091552 | 122.7264 | 122.6761 | 0.10986 | 122.9141 | 122.8455 | 0.16937 | 0.09613 | 123.0423 | 122.9645 | 122.9233 | -0.18311 | 122.9828 | 122.9691 | 122.9507 | -0.19684
2099.9062 | 122.9645 | -122.7173 | 0.1831 | -0.092163 | 0.025101 | 0.0027344 | 0.0034093 | -0.0077566 | 0.0026424 | -0.0043793 | -0.08873 | -0.0087093 | -0.0068936 | -0.0013352 | 0.0062441 | -0.01593 | 0.17853 | 0.11444 | 0.073242 | 0.11444 | 0.3067 | 0.045776 | -0.13275 | 0.10071 | 0.10071 | -0.013733 | 0.21515 | 0.17853 | -0.073242 | -0.11902 | 122.7631 | 122.5845 | 0.1236 | 122.8317 | 122.8317 | 0.24719 | -0.004577 | 122.644 | 122.5983 | 0.032044 | 122.818 | 122.7036 | 0.10529 | -0.004577 | 123.024 | 122.8958 | 122.7905 | -0.31586 | 122.9324 | 122.8958 | 122.818 | -0.30212
2101.5938 | 123.0652 | -122.7264 | 0.15106 | -0.099793 | 0.025742 | 0.0020936 | 0.0053321 | -0.0047658 | 0.0015744 | -0.0063019 | -0.15739 | -0.0087093 | -0.0034756 | -0.003685 | 0.0032535 | -0.013153 | 0.16479 | 0.13275 | 0.086975 | 0.14191 | 0.3067 | 0.068665 | -0.11902 | 0.14191 | 0.14191 | 0.027466 | 0.2243 | 0.19226 | -0.050354 | -0.09613 | 122.7951 | 122.6074 | 0.15564 | 122.8592 | 122.8683 | 0.26093 | 0.013733 | 122.6761 | 122.6303 | 0.073242 | 122.8683 | 122.7539 | 0.1236 | 0.041199 | 123.0331 | 122.8912 | 122.8134 | -0.27008 | 122.9507 | 122.9187 | 122.8683 | -0.24719
2103.2969 | 122.9233 | -122.7264 | 0.19226 | 0.090942 | 0.021469 | 0.0033752 | 0.0066137 | -0.0071158 | -0.0046206 | -0.0077973 | 0.18593 | -0.010632 | -0.0034756 | -0.0026168 | 0.0017581 | -0.01123 | 0.14648 | 0.15106 | 0.1236 | 0.10986 | 0.2243 | 0.059509 | -0.10071 | 0.17853 | 0.16479 | 0.086975 | 0.17853 | 0.16022 | -0.059509 | -0.10071 | 122.7859 | 122.6257 | 0.032043 | 122.8775 | 122.8363 | 0.21057 | -0.045777 | 122.6669 | 122.6257 | -0.013733 | 122.905 | 122.8134 | 0.18768 | -0.032044 | 122.9507 | 122.8729 | 122.85 | -0.29297 | 122.905 | 122.8867 | 122.8912 | -0.29297
2105.0469 | 123.0377 | -122.699 | 0.17395 | -0.054016 | 0.027023 | 0.0050842 | 0.0064001 | -0.0077566 | 0.001788 | -0.0043793 | -0.12688 | -0.0089229 | -0.0053982 | -0.001976 | 0.0060305 | -0.013794 | 0.17853 | 0.13733 | 0.091553 | 0.14191 | 0.31586 | 0.054932 | -0.09613 | 0.14191 | 0.13733 | 0.032043 | 0.2243 | 0.20599 | -0.050354 | -0.082397 | 122.7539 | 122.6028 | 0.14191 | 122.8363 | 122.8409 | 0.23804 | 0.004578 | 122.6486 | 122.6166 | 0.050354 | 122.8409 | 122.731 | 0.11444 | 0.032044 | 123.0148 | 122.8775 | 122.7905 | -0.27008 | 122.9233 | 122.905 | 122.8363 | -0.25635
2106.7969 | 123.0377 | -122.6761 | 0.15564 | -0.12268 | 0.030014 | 0.002948 | 0.0085363 | -0.0069022 | 0.00029262 | -0.0050201 | -0.096359 | -0.0082821 | -0.0026212 | 0.0010148 | 0.0034671 | -0.014007 | 0.15564 | 0.13733 | 0.082397 | 0.12817 | 0.32044 | 0.041199 | -0.10986 | 0.13275 | 0.14648 | 0.032043 | 0.21057 | 0.20142 | -0.064087 | -0.10986 | 122.7173 | 122.5662 | 0.1648 | 122.8134 | 122.8043 | 0.23804 | 0 | 122.612 | 122.5662 | 0.054931 | 122.8088 | 122.7081 | 0.14191 | 0.045776 | 122.9965 | 122.8317 | 122.7585 | -0.2655 | 122.8867 | 122.8775 | 122.8226 | -0.2655
2108.5 | 122.9507 | -122.731 | 0.18768 | 0.022278 | 0.022751 | 0.0061524 | 0.0076819 | -0.007543 | -0.0076114 | -0.0088653 | 0.11726 | -0.012768 | -0.0036892 | -0.00069421 | 0.00047633 | -0.0099484 | 0.11902 | 0.17395 | 0.13733 | 0.12817 | 0.27466 | 0.086975 | -0.082397 | 0.16022 | 0.16022 | 0.10529 | 0.23346 | 0.17853 | -0.013733 | -0.064087 | 122.818 | 122.6486 | 0.086975 | 122.905 | 122.8592 | 0.21057 | -0.068664 | 122.7173 | 122.6669 | 0.045776 | 122.8912 | 122.8363 | 0.16937 | -0.009155 | 123.0057 | 122.85 | 122.8683 | -0.27008 | 122.9645 | 122.9095 | 122.8912 | -0.25177
2110.1875 | 123.0698 | -122.7081 | 0.16022 | -0.22186 | 0.024674 | 0.0035888 | 0.0038367 | -0.0062612 | -0.00013458 | -0.0054475 | -0.19554 | -0.0091367 | -0.0047574 | 0.00037379 | 0.0043215 | -0.012726 | 0.16479 | 0.1236 | 0.082397 | 0.15106 | 0.37994 | 0.091553 | -0.059509 | 0.12817 | 0.13733 | 0.041199 | 0.28839 | 0.25177 | -0.013733 | -0.064087 | 122.7997 | 122.6486 | 0.21973 | 122.8317 | 122.8592 | 0.21057 | 0.004578 | 122.6944 | 122.644 | 0.12817 | 122.8363 | 122.7493 | 0.10529 | 0.091553 | 123.0881 | 122.8729 | 122.7905 | -0.21973 | 122.9965 | 122.9599 | 122.8455 | -0.2243
2111.9531 | 123.024 | -122.731 | 0.14191 | -0.17609 | 0.023819 | 0.0048706 | 0.0081091 | -0.0056204 | -0.0039798 | -0.0065155 | -0.13451 | -0.013196 | -0.0053982 | -0.0021896 | 0.0013309 | -0.013366 | 0.2243 | 0.26093 | 0.21973 | 0.22888 | 0.31128 | 0.11444 | -0.036621 | 0.21515 | 0.27466 | 0.17395 | 0.25635 | 0.23346 | 0.032043 | -0.036621 | 122.8455 | 122.6944 | 0.16937 | 122.9919 | 122.9599 | 0.2655 | 0.082397 | 122.7631 | 122.6944 | 0.11444 | 122.9462 | 122.905 | 0.21057 | 0.091552 | 123.0423 | 122.9553 | 122.9507 | -0.17853 | 122.9874 | 122.9645 | 123.0057 | -0.17853
2113.7031 | 123.0606 | -122.6944 | 0.15106 | -0.054016 | 0.022965 | 0.0055114 | 0.0046911 | -0.007543 | -0.0076114 | -0.0067291 | -0.050583 | -0.0097775 | -0.0043302 | -0.00069421 | 0.0028263 | -0.011444 | 0.21057 | 0.23804 | 0.20142 | 0.20599 | 0.32959 | 0.10071 | -0.041199 | 0.25635 | 0.2655 | 0.20142 | 0.23804 | 0.2243 | 0.045776 | -0.022888 | 122.7951 | 122.6532 | 0.17853 | 122.9324 | 122.9004 | 0.24719 | 0.059509 | 122.7402 | 122.6715 | 0.086975 | 122.9507 | 122.8958 | 0.2243 | 0.073242 | 123.024 | 122.905 | 122.8958 | -0.19226 | 122.9324 | 122.9187 | 122.9599 | -0.17395
2115.3906 | 122.9416 | -122.7448 | 0.19226 | 0.068054 | 0.024887 | 0.0067932 | 0.0017005 | -0.0094656 | 0.0047788 | -0.0048065 | -0.0048066 | -0.0080685 | -0.0062528 | 0.00080099 | 0.0079531 | -0.013153 | 0.086975 | 0.027466 | -0.018311 | 0.045776 | 0.28381 | 0 | -0.16022 | 0.032043 | 0.022888 | -0.068665 | 0.21973 | 0.19226 | -0.07782 | -0.13275 | 122.7448 | 122.5845 | 0.091552 | 122.7722 | 122.7905 | 0.20599 | -0.10529 | 122.6669 | 122.612 | 0.027466 | 122.7768 | 122.6761 | 0.064086 | 0 | 123.0286 | 122.8317 | 122.7264 | -0.35248 | 122.9645 | 122.937 | 122.7676 | -0.32501
2117.1562 | 122.9462 | -122.7493 | 0.20142 | -0.038757 | 0.023392 | 0.0059388 | 0.0025549 | -0.0062612 | 0.0028562 | -0.0060883 | -0.073471 | -0.0089229 | -0.0036892 | -0.0013352 | 0.0090213 | -0.014221 | 0.11902 | 0.086975 | 0.032043 | 0.10529 | 0.2655 | 0.045776 | -0.11444 | 0.07782 | 0.045776 | -0.045776 | 0.21057 | 0.17853 | -0.068665 | -0.13275 | 122.7951 | 122.6349 | 0.064087 | 122.8363 | 122.8546 | 0.21973 | -0.082397 | 122.6807 | 122.6166 | 0.009155 | 122.8271 | 122.7036 | 0.086975 | -0.022888 | 123.0148 | 122.8683 | 122.7814 | -0.31586 | 122.9599 | 122.9279 | 122.7951 | -0.33417
2118.9062 | 123.0789 | -122.7127 | 0.15106 | -0.16846 | 0.024887 | 0.0044434 | 0.0070409 | -0.0047658 | -0.00163 | -0.0063019 | -0.23369 | -0.0093503 | -0.0041164 | -0.00069421 | 0.0034671 | -0.013794 | 0.14191 | 0.13733 | 0.07782 | 0.14648 | 0.35248 | 0.073242 | -0.073242 | 0.10529 | 0.15106 | 0.050354 | 0.27466 | 0.25635 | -0.004578 | -0.068665 | 122.7859 | 122.6395 | 0.20142 | 122.85 | 122.8592 | 0.21973 | -0.009155 | 122.7081 | 122.644 | 0.1236 | 122.818 | 122.7631 | 0.11902 | 0.10529 | 123.0652 | 122.8546 | 122.7905 | -0.2243 | 122.9874 | 122.9691 | 122.8638 | -0.21973
2120.5938 | 123.0377 | -122.699 | 0.15564 | -0.19897 | 0.023605 | 0.0042298 | 0.0078955 | -0.0062612 | -0.003339 | -0.0056611 | -0.21843 | -0.0099911 | -0.0019802 | -0.00026701 | 0.0011173 | -0.010589 | 0.13733 | 0.16479 | 0.10986 | 0.14648 | 0.36163 | 0.10071 | -0.059509 | 0.13733 | 0.15106 | 0.064087 | 0.3067 | 0.25635 | -0.009155 | -0.050354 | 122.7997 | 122.6395 | 0.20599 | 122.8638 | 122.8455 | 0.20599 | -0.018311 | 122.6898 | 122.6486 | 0.15106 | 122.8363 | 122.7631 | 0.11444 | 0.10071 | 123.0606 | 122.8363 | 122.8088 | -0.21515 | 123.0057 | 122.9553 | 122.85 | -0.20599
2122.2812 | 122.937 | -122.7493 | 0.19684 | 0.17487 | 0.024033 | 0.0061524 | 0.0029821 | -0.0077566 | -0.0031254 | -0.0039521 | 0.2317 | -0.011273 | -0.0058254 | -0.001976 | 0.0043215 | -0.012085 | 0.1236 | 0.16022 | 0.1236 | 0.11902 | 0.19226 | 0.013733 | -0.10529 | 0.16479 | 0.15564 | 0.07782 | 0.14648 | 0.09613 | -0.054932 | -0.11902 | 122.7631 | 122.644 | -0.004577 | 122.9095 | 122.8683 | 0.22431 | -0.073242 | 122.6944 | 122.6303 | -0.050354 | 122.9141 | 122.8271 | 0.19684 | -0.10071 | 122.9416 | 122.8729 | 122.8729 | -0.30212 | 122.8958 | 122.8455 | 122.905 | -0.31586
2123.9688 | 122.9736 | -122.7219 | 0.15564 | 0.052795 | 0.019333 | 0.0059388 | 0.0057593 | -0.0073294 | -0.0054752 | -0.0075837 | 0.063858 | -0.010418 | -0.0058254 | -0.0013352 | 0.0021853 | -0.011017 | 0.13275 | 0.15564 | 0.1236 | 0.14648 | 0.29755 | 0.086975 | -0.064087 | 0.16022 | 0.1831 | 0.11902 | 0.24719 | 0.21057 | -0.018311 | -0.050354 | 122.8088 | 122.6578 | 0.14191 | 122.8775 | 122.8683 | 0.21057 | -0.022889 | 122.7036 | 122.6715 | 0.091552 | 122.8821 | 122.8409 | 0.16937 | 0.054931 | 123.0194 | 122.8546 | 122.8455 | -0.21973 | 122.9691 | 122.9324 | 122.905 | -0.20599
2125.7188 | 122.9416 | -122.7448 | 0.20142 | 0.075684 | 0.019119 | 0.0050842 | 0.0042639 | -0.0083974 | -0.0031254 | -0.0073701 | 0.10963 | -0.010846 | -0.0075344 | -0.0011216 | 0.0028263 | -0.013153 | 0.15106 | 0.14648 | 0.11444 | 0.11902 | 0.26093 | 0.064087 | -0.064087 | 0.16479 | 0.16937 | 0.10529 | 0.22888 | 0.19684 | -0.013733 | -0.050354 | 122.8088 | 122.6807 | 0.059509 | 122.8912 | 122.8638 | 0.18311 | -0.050354 | 122.731 | 122.6944 | 0.027466 | 122.9095 | 122.85 | 0.15564 | -0.004578 | 123.0057 | 122.8958 | 122.8592 | -0.2655 | 122.9736 | 122.9416 | 122.9141 | -0.25177
2127.4062 | 123.0606 | -122.7173 | 0.16479 | -0.13031 | 0.025742 | 0.0059388 | 0.0051183 | -0.004125 | 0.0028562 | -0.0048065 | -0.16502 | -0.0063595 | -0.0051846 | -0.0024032 | 0.0068851 | -0.012085 | 0.19226 | 0.11902 | 0.082397 | 0.14191 | 0.32044 | 0.054932 | -0.086975 | 0.13733 | 0.13275 | 0.013733 | 0.22888 | 0.19684 | -0.059509 | -0.091553 | 122.7722 | 122.6303 | 0.15564 | 122.8363 | 122.8592 | 0.22888 | 0.027466 | 122.6578 | 122.6257 | 0.064087 | 122.8546 | 122.731 | 0.10529 | 0.032043 | 123.0377 | 122.9095 | 122.7997 | -0.25177 | 122.9462 | 122.9141 | 122.85 | -0.25635
2129.1562 | 123.0286 | -122.7448 | 0.15106 | -0.19135 | 0.023605 | 0.0042298 | 0.0098181 | -0.009252 | -0.0046206 | -0.0075837 | -0.14977 | -0.010846 | -0.0034756 | -0.0024032 | 0.0021853 | -0.012085 | 0.26093 | 0.28839 | 0.23804 | 0.2243 | 0.33417 | 0.14648 | -0.018311 | 0.23804 | 0.29297 | 0.18768 | 0.2655 | 0.23346 | 0.050354 | -0.045776 | 122.8912 | 122.7264 | 0.1831 | 123.0331 | 122.9691 | 0.24261 | 0.10986 | 122.7951 | 122.699 | 0.11444 | 122.9828 | 122.9324 | 0.23346 | 0.082397 | 123.0789 | 123.0057 | 122.9828 | -0.16937 | 123.0103 | 122.9782 | 123.0377 | -0.19684
2130.9062 | 123.0286 | -122.7036 | 0.15564 | -0.19897 | 0.022751 | 0.0059388 | 0.0078955 | -0.0051932 | -0.0037662 | -0.0063019 | -0.13451 | -0.012127 | -0.0034756 | -0.0026168 | 0.0036807 | -0.011017 | 0.24719 | 0.29755 | 0.23346 | 0.24261 | 0.32044 | 0.13275 | -0.022888 | 0.24719 | 0.29297 | 0.17395 | 0.24261 | 0.21057 | 0.032043 | -0.022888 | 122.8363 | 122.6807 | 0.1648 | 123.0011 | 122.9462 | 0.2655 | 0.091552 | 122.7356 | 122.6807 | 0.086975 | 122.9507 | 122.8775 | 0.19684 | 0.054931 | 123.024 | 122.9507 | 122.937 | -0.17853 | 122.9462 | 122.9141 | 122.9965 | -0.17853
2132.6562 | 123.0743 | -122.6852 | 0.15564 | -0.12268 | 0.023819 | 0.0055114 | 0.0081091 | -0.0077566 | -0.0039798 | -0.0065155 | -0.042954 | -0.010846 | -0.0041164 | -0.00069421 | 0.0023989 | -0.01358 | 0.23804 | 0.28839 | 0.23346 | 0.20599 | 0.32959 | 0.11444 | -0.018311 | 0.29297 | 0.32959 | 0.21973 | 0.24719 | 0.21973 | 0.036621 | -0.018311 | 122.7997 | 122.6669 | 0.17395 | 122.9736 | 122.8912 | 0.22431 | 0.082397 | 122.7219 | 122.6669 | 0.091552 | 122.9782 | 122.905 | 0.23804 | 0.064087 | 123.0148 | 122.9233 | 122.9187 | -0.17395 | 122.9324 | 122.905 | 123.0148 | -0.17395
2134.3438 | 123.0423 | -122.6807 | 0.16479 | 0.0070193 | 0.022324 | 0.0050842 | 0.0040503 | -0.0090384 | -0.003339 | -0.0077973 | -0.050583 | -0.012982 | -0.0036892 | -0.00090781 | 0.0028263 | -0.012085 | 0.17395 | 0.1831 | 0.16022 | 0.16937 | 0.3067 | 0.082397 | -0.050354 | 0.21515 | 0.22888 | 0.16022 | 0.23346 | 0.20142 | 0.009155 | -0.027466 | 122.7631 | 122.6303 | 0.14191 | 122.8638 | 122.85 | 0.21973 | 0.009155 | 122.6898 | 122.6532 | 0.068664 | 122.8958 | 122.8409 | 0.18768 | 0.036621 | 122.9874 | 122.8546 | 122.8409 | -0.21515 | 122.9141 | 122.8821 | 122.9095 | -0.19226
2136.0938 | 122.9553 | -122.7722 | 0.19684 | 0.045166 | 0.02681 | 0.0031616 | 0.0031957 | -0.0088248 | 0.0054196 | -0.0063019 | -0.0048066 | -0.0078549 | -0.0088162 | 0.0016556 | 0.0079531 | -0.013366 | 0.082397 | 0.004578 | -0.022888 | 0.036621 | 0.28381 | 0.004578 | -0.14191 | 0.073242 | 0.018311 | -0.059509 | 0.21057 | 0.19226 | -0.10529 | -0.13733 | 122.7768 | 122.6303 | 0.086975 | 122.7768 | 122.8088 | 0.17853 | -0.11444 | 122.6669 | 122.6349 | 0.013733 | 122.8455 | 122.7127 | 0.07782 | -0.004577 | 123.056 | 122.8546 | 122.7493 | -0.33875 | 122.9828 | 122.9645 | 122.7905 | -0.33417
2137.8594 | 123.0606 | -122.699 | 0.15564 | -0.054016 | 0.019974 | 0.0082886 | 0.0044775 | -0.0081838 | -0.0054752 | -0.0058747 | -0.035324 | -0.011059 | -0.0071072 | -0.0013352 | 0.0015445 | -0.0099484 | 0.16022 | 0.19226 | 0.16022 | 0.16479 | 0.28839 | 0.086975 | -0.068665 | 0.21973 | 0.23346 | 0.16937 | 0.24719 | 0.21973 | 0.018311 | -0.036621 | 122.7859 | 122.6303 | 0.13275 | 122.8912 | 122.8638 | 0.23346 | 0.004577 | 122.7173 | 122.6624 | 0.091552 | 122.9187 | 122.8683 | 0.20599 | 0.064087 | 122.9874 | 122.8592 | 122.8592 | -0.22431 | 122.9462 | 122.9187 | 122.9324 | -0.19226
2139.5625 | 123.056 | -122.6898 | 0.15564 | -0.046387 | 0.021469 | 0.0055114 | 0.0057593 | -0.0047658 | -0.006116 | -0.0077973 | 0.010452 | -0.010632 | -0.007748 | -0.0013352 | 0.00068993 | -0.014435 | 0.17395 | 0.1831 | 0.16937 | 0.17853 | 0.29755 | 0.10071 | -0.054932 | 0.2243 | 0.23346 | 0.15106 | 0.25635 | 0.21515 | 0.013733 | -0.045776 | 122.7905 | 122.6349 | 0.14191 | 122.8729 | 122.8683 | 0.23346 | 0.01831 | 122.7036 | 122.644 | 0.10071 | 122.9141 | 122.8409 | 0.19684 | 0.059509 | 122.9874 | 122.8638 | 122.8592 | -0.21057 | 122.9462 | 122.905 | 122.9233 | -0.20142
2141.2656 | 123.0789 | -122.731 | 0.14191 | -0.24475 | 0.023605 | 0.0027344 | 0.0053321 | -0.0064748 | 0.00093342 | -0.0067291 | -0.27184 | -0.0091367 | -0.0036892 | -0.00026701 | 0.0060305 | -0.015075 | 0.20599 | 0.16022 | 0.09613 | 0.16022 | 0.3891 | 0.10529 | -0.064087 | 0.1236 | 0.14191 | 0.027466 | 0.30212 | 0.26093 | -0.018311 | -0.068665 | 122.8363 | 122.6669 | 0.24719 | 122.8912 | 122.8912 | 0.2243 | 0.064087 | 122.7127 | 122.6624 | 0.16022 | 122.8546 | 122.7585 | 0.096131 | 0.11902 | 123.1201 | 122.937 | 122.8271 | -0.20599 | 123.0331 | 122.9919 | 122.8729 | -0.21057
2143.0312 | 123.0469 | -122.7081 | 0.16479 | -0.17609 | 0.024674 | 0.0040162 | 0.0074683 | -0.0081838 | 0.00029262 | -0.0077973 | -0.24895 | -0.010418 | -0.0030484 | -0.001976 | 0.0015445 | -0.011871 | 0.18768 | 0.16479 | 0.11902 | 0.15106 | 0.37537 | 0.11444 | -0.068665 | 0.14191 | 0.16022 | 0.059509 | 0.3067 | 0.2655 | -0.009155 | -0.054932 | 122.8226 | 122.6395 | 0.21057 | 122.8729 | 122.8592 | 0.21973 | 0.022888 | 122.699 | 122.6532 | 0.14191 | 122.85 | 122.7676 | 0.11444 | 0.10071 | 123.0835 | 122.8958 | 122.8271 | -0.23346 | 123.0148 | 122.9736 | 122.8683 | -0.21973
2144.7812 | 123.0743 | -122.7036 | 0.15564 | -0.054016 | 0.023392 | 0.006366 | 0.0068273 | -0.0045522 | -0.0059024 | -0.0086517 | -0.058212 | -0.01405 | -0.0047574 | -0.00048061 | 0.00047633 | -0.012085 | 0.18768 | 0.2243 | 0.19226 | 0.20142 | 0.31586 | 0.10071 | -0.036621 | 0.24261 | 0.27466 | 0.19226 | 0.24261 | 0.21973 | 0.027466 | -0.027466 | 122.8043 | 122.6669 | 0.16022 | 122.9279 | 122.905 | 0.23804 | 0.032043 | 122.731 | 122.6761 | 0.086975 | 122.9462 | 122.8958 | 0.21973 | 0.064087 | 123.0194 | 122.8912 | 122.8958 | -0.19226 | 122.9462 | 122.9233 | 122.9782 | -0.18311
2146.4688 | 123.024 | -122.7127 | 0.13733 | -0.19897 | 0.024246 | 0.0042298 | 0.0068273 | -0.0045522 | -0.0029118 | -0.0067291 | -0.14214 | -0.012127 | -0.0041164 | -0.0013352 | 0.0011173 | -0.014648 | 0.2655 | 0.31128 | 0.25177 | 0.24719 | 0.32959 | 0.13275 | -0.022888 | 0.26093 | 0.31128 | 0.19226 | 0.25635 | 0.21973 | 0.041199 | -0.027466 | 122.8455 | 122.6898 | 0.19226 | 123.024 | 122.9599 | 0.27008 | 0.12817 | 122.7539 | 122.6852 | 0.11902 | 122.9736 | 122.905 | 0.21973 | 0.082398 | 123.0423 | 122.9782 | 122.9645 | -0.16022 | 122.9691 | 122.9324 | 123.024 | -0.16479
2148.1719 | 122.9507 | -122.7539 | 0.19226 | 0.060425 | 0.025314 | 0.0050842 | 0.0036231 | -0.0081838 | 0.0049924 | -0.0043793 | 0.04097 | -0.0087093 | -0.0045438 | -0.0011216 | 0.0081667 | -0.014221 | 0.059509 | -0.009155 | -0.032043 | 0.027466 | 0.26093 | 0.004578 | -0.14648 | 0.091553 | 0.022888 | -0.068665 | 0.20599 | 0.17395 | -0.086975 | -0.16937 | 122.7585 | 122.6074 | 0.068664 | 122.7448 | 122.7814 | 0.17395 | -0.13275 | 122.6669 | 122.5845 | 0.013733 | 122.8455 | 122.6852 | 0.10071 | -0.018311 | 123.0148 | 122.8134 | 122.7219 | -0.33874 | 122.9599 | 122.9279 | 122.7768 | -0.36163
2149.9219 | 123.024 | -122.7081 | 0.1831 | -0.1532 | 0.022537 | 0.0057252 | 0.0093909 | -0.0081838 | -0.0029118 | -0.0065155 | -0.20317 | -0.0117 | -0.0041164 | -0.001976 | 0.0019717 | -0.011444 | 0.20599 | 0.27924 | 0.21057 | 0.22888 | 0.31586 | 0.11902 | -0.027466 | 0.22888 | 0.29297 | 0.16479 | 0.28381 | 0.23346 | 0.041199 | -0.018311 | 122.8271 | 122.6807 | 0.13275 | 122.9874 | 122.937 | 0.25635 | 0.022889 | 122.7493 | 122.6898 | 0.10071 | 122.937 | 122.8729 | 0.18311 | 0.050354 | 123.024 | 122.9141 | 122.9187 | -0.21057 | 122.9919 | 122.9416 | 123.0011 | -0.20142
2151.6562 | 122.9828 | -122.7356 | 0.19684 | 0.11383 | 0.025955 | 0.0059388 | 0.0019141 | -0.0060476 | 0.0030698 | -0.0054475 | 0.063858 | -0.0091367 | -0.0041164 | -0.00090781 | 0.0066715 | -0.013153 | 0.064087 | 0.018311 | -0.041199 | 0.041199 | 0.2655 | 0 | -0.15106 | 0.07782 | 0.013733 | -0.036621 | 0.21057 | 0.16479 | -0.068665 | -0.14648 | 122.7356 | 122.5845 | 0.068665 | 122.7539 | 122.7768 | 0.19226 | -0.13275 | 122.6669 | 122.5891 | 0.013733 | 122.8134 | 122.699 | 0.10986 | -0.032043 | 123.0011 | 122.7997 | 122.6944 | -0.3479 | 122.9462 | 122.9004 | 122.7493 | -0.34332
2153.4219 | 122.9782 | -122.7402 | 0.20142 | 0.14435 | 0.026169 | 0.0027344 | 0.0021277 | -0.0064748 | 0.0028562 | -0.0026703 | 0.063858 | -0.0072141 | -0.0071072 | -0.00069421 | 0.0098757 | -0.013153 | 0.041199 | 0.018311 | -0.027466 | 0.036621 | 0.2655 | -0.009155 | -0.15564 | 0.059509 | 0.022888 | -0.041199 | 0.20599 | 0.17853 | -0.086975 | -0.14648 | 122.731 | 122.5845 | 0.064087 | 122.7585 | 122.7768 | 0.19226 | -0.16022 | 122.6532 | 122.5937 | 0.004578 | 122.7997 | 122.699 | 0.10529 | -0.022888 | 123.0057 | 122.7814 | 122.7127 | -0.35706 | 122.9462 | 122.9187 | 122.7631 | -0.3479
2155.1094 | 122.9736 | -122.7173 | 0.16022 | -0.061646 | 0.025314 | 0.0016662 | 0.0066137 | -0.0077566 | 0.0011472 | -0.0018159 | -0.10399 | -0.0078549 | -0.0026212 | -0.0028306 | 0.0051761 | -0.014221 | 0.17853 | 0.14648 | 0.091553 | 0.11902 | 0.29755 | 0.032043 | -0.10529 | 0.13733 | 0.14648 | 0.009155 | 0.21973 | 0.18768 | -0.050354 | -0.10986 | 122.7493 | 122.612 | 0.13733 | 122.8638 | 122.8363 | 0.22431 | 0.018311 | 122.6669 | 122.6074 | 0.05951 | 122.8546 | 122.7264 | 0.11902 | 0.027466 | 123.0148 | 122.8958 | 122.8088 | -0.2655 | 122.937 | 122.905 | 122.8638 | -0.27008
2156.8594 | 123.0423 | -122.6944 | 0.14191 | -0.18372 | 0.022965 | 0.0057252 | 0.0068273 | -0.0083974 | -0.006116 | -0.0050201 | -0.11925 | -0.012127 | -0.0039028 | -0.0030442 | 0.00026273 | -0.012939 | 0.21515 | 0.31586 | 0.24261 | 0.23346 | 0.32044 | 0.14191 | -0.018311 | 0.24261 | 0.32501 | 0.19226 | 0.25177 | 0.20142 | 0.027466 | -0.004578 | 122.8363 | 122.6761 | 0.17853 | 123.0103 | 122.9279 | 0.25177 | 0.073242 | 122.7219 | 122.6898 | 0.10986 | 122.937 | 122.8867 | 0.19684 | 0.059509 | 123.0148 | 122.9095 | 122.937 | -0.16022 | 122.9462 | 122.8958 | 123.0194 | -0.14649
2158.5625 | 122.9553 | -122.7448 | 0.19226 | 0.029907 | 0.018692 | 0.0059388 | 0.0029821 | -0.0071158 | -0.0056888 | -0.0043793 | 0.10963 | -0.011914 | -0.0053982 | -0.00090781 | 0.0023989 | -0.0097348 | 0.13275 | 0.14648 | 0.12817 | 0.13733 | 0.27008 | 0.073242 | -0.073242 | 0.15106 | 0.17853 | 0.11902 | 0.2243 | 0.20599 | -0.004578 | -0.054932 | 122.818 | 122.6715 | 0.07782 | 122.8912 | 122.8821 | 0.21057 | -0.05951 | 122.7402 | 122.6898 | 0.032043 | 122.8958 | 122.8638 | 0.17395 | 0.013733 | 123.0148 | 122.8775 | 122.8729 | -0.2655 | 122.9691 | 122.9507 | 122.9233 | -0.24719
2160.25 | 122.9736 | -122.7356 | 0.17853 | 0.029907 | 0.022537 | 0.0055114 | 0.0027685 | -0.009252 | -0.005048 | -0.0058747 | 0.056228 | -0.010846 | -0.0064664 | 0.00016019 | 0.0036807 | -0.012939 | 0.13733 | 0.15564 | 0.11902 | 0.14191 | 0.29297 | 0.07782 | -0.086975 | 0.16479 | 0.17395 | 0.12817 | 0.21057 | 0.19684 | 0.004578 | -0.059509 | 122.8134 | 122.6486 | 0.11444 | 122.8912 | 122.8775 | 0.22888 | -0.041199 | 122.7402 | 122.6761 | 0.032043 | 122.9004 | 122.8638 | 0.18768 | 0.01831 | 123.0286 | 122.8729 | 122.8546 | -0.2655 | 122.9462 | 122.9324 | 122.9095 | -0.23804
2162 | 122.9736 | -122.7173 | 0.16937 | 0.014648 | 0.021896 | 0.0070068 | 0.0025549 | -0.0077566 | -0.002698 | -0.0075837 | 0.071487 | -0.012127 | -0.0079618 | -0.0024032 | 0.0045351 | -0.012298 | 0.14648 | 0.14648 | 0.12817 | 0.13275 | 0.28839 | 0.086975 | -0.059509 | 0.16479 | 0.16479 | 0.11444 | 0.21973 | 0.1831 | -0.018311 | -0.068665 | 122.8043 | 122.6578 | 0.11902 | 122.8638 | 122.85 | 0.19226 | -0.022889 | 122.699 | 122.6486 | 0.050354 | 122.8821 | 122.8317 | 0.18311 | 0.013732 | 123.0057 | 122.8638 | 122.8455 | -0.22888 | 122.937 | 122.9004 | 122.8821 | -0.23804
2163.75 | 122.9233 | -122.7448 | 0.17395 | 0.12146 | 0.022537 | 0.0035888 | 0.0036231 | -0.0088248 | -0.0024844 | -0.0054475 | 0.15541 | -0.0099911 | -0.0064664 | -0.0013352 | 0.0041079 | -0.014648 | 0.15564 | 0.15564 | 0.11902 | 0.11444 | 0.23346 | 0.027466 | -0.13275 | 0.18768 | 0.16479 | 0.09613 | 0.18768 | 0.16022 | -0.027466 | -0.073242 | 122.7722 | 122.612 | 0.059509 | 122.9004 | 122.8592 | 0.24719 | -0.01831 | 122.7173 | 122.6715 | 0.013733 | 122.9324 | 122.8409 | 0.16937 | -0.013733 | 122.9782 | 122.9004 | 122.8638 | -0.3067 | 122.9324 | 122.905 | 122.9095 | -0.24719
2165.4375 | 122.9691 | -122.7448 | 0.19226 | 0.098572 | 0.025314 | 0.0048706 | 0.0053321 | -0.0077566 | 0.005206 | -0.0067291 | 0.056228 | -0.0082821 | -0.0064664 | -0.0013352 | 0.0058169 | -0.012298 | 0.086975 | -0.009155 | -0.036621 | 0.032043 | 0.27466 | 0.009155 | -0.16022 | 0.073242 | 0.009155 | -0.064087 | 0.20599 | 0.16479 | -0.091553 | -0.13733 | 122.7539 | 122.5845 | 0.082397 | 122.7356 | 122.7768 | 0.19226 | -0.10529 | 122.6532 | 122.6074 | 0.013733 | 122.818 | 122.6807 | 0.073242 | -0.027466 | 123.0194 | 122.8317 | 122.7081 | -0.35248 | 122.9507 | 122.9095 | 122.7539 | -0.32959
2167.125 | 123.0469 | -122.7081 | 0.15106 | -0.16083 | 0.024674 | 0.004657 | 0.0096045 | -0.005834 | -0.0041934 | -0.0075837 | -0.14977 | -0.011273 | -0.004971 | -0.001976 | 0.00068993 | -0.013366 | 0.26093 | 0.29755 | 0.23804 | 0.22888 | 0.33875 | 0.12817 | -0.018311 | 0.2655 | 0.30212 | 0.18768 | 0.24719 | 0.22888 | 0.045776 | -0.009155 | 122.8363 | 122.6898 | 0.18768 | 123.0057 | 122.937 | 0.24719 | 0.10986 | 122.7539 | 122.699 | 0.09613 | 122.9736 | 122.8958 | 0.19684 | 0.07782 | 123.0469 | 122.9691 | 122.9462 | -0.16937 | 122.9553 | 122.937 | 123.0103 | -0.16022
2168.8906 | 123.0377 | -122.7036 | 0.16479 | -0.2066 | 0.02446 | 0.0057252 | 0.0081091 | -0.0049796 | -0.0024844 | -0.0084381 | -0.19554 | -0.011273 | -0.0053982 | -0.00090781 | 0.0030399 | -0.012939 | 0.26093 | 0.29755 | 0.25177 | 0.23346 | 0.32501 | 0.11902 | -0.013733 | 0.25635 | 0.28839 | 0.19226 | 0.24719 | 0.2243 | 0.045776 | -0.018311 | 122.8226 | 122.6898 | 0.16022 | 123.0011 | 122.937 | 0.24719 | 0.09613 | 122.7493 | 122.6852 | 0.082397 | 122.9599 | 122.8958 | 0.21057 | 0.059509 | 123.0286 | 122.9645 | 122.9553 | -0.17853 | 122.9507 | 122.9279 | 122.9919 | -0.18311
2170.6406 | 122.9507 | -122.7585 | 0.19684 | -0.023499 | 0.022324 | 0.0052978 | 0.0021277 | -0.005834 | 0.0058468 | -0.0060883 | -0.073471 | -0.0099911 | -0.0056118 | -0.0011216 | 0.0085941 | -0.015716 | 0.15106 | 0.1236 | 0.041199 | 0.086975 | 0.29297 | 0.045776 | -0.1236 | 0.10071 | 0.068665 | -0.041199 | 0.2243 | 0.17853 | -0.07782 | -0.12817 | 122.8043 | 122.6349 | 0.096131 | 122.8821 | 122.8455 | 0.21057 | -0.045776 | 122.6807 | 122.6303 | 0.027466 | 122.8592 | 122.7173 | 0.086975 | -0.01831 | 123.0515 | 122.9095 | 122.7997 | -0.32043 | 122.9828 | 122.937 | 122.8271 | -0.32501
2172.3281 | 122.9462 | -122.7539 | 0.19684 | 0.045166 | 0.027023 | 0.0050842 | 0.0019141 | -0.0066884 | 0.0030698 | -0.0022431 | -0.012436 | -0.0089229 | -0.0058254 | -0.00090781 | 0.0075259 | -0.01358 | 0.10986 | 0.068665 | 0.009155 | 0.059509 | 0.27466 | 0.013733 | -0.14191 | 0.059509 | 0.050354 | -0.064087 | 0.20599 | 0.17853 | -0.09613 | -0.13275 | 122.7676 | 122.612 | 0.07782 | 122.8226 | 122.8134 | 0.20142 | -0.086975 | 122.6578 | 122.6212 | 0.009156 | 122.8134 | 122.6898 | 0.068664 | -0.01831 | 123.0286 | 122.8638 | 122.7631 | -0.33875 | 122.9599 | 122.9324 | 122.8043 | -0.32959
2174.0781 | 123.0652 | -122.699 | 0.14648 | 0.014648 | 0.022751 | 0.0048706 | 0.0087499 | -0.0047658 | -0.0086796 | -0.0069427 | 0.03334 | -0.0117 | -0.0058254 | -0.0017624 | 0.00090353 | -0.011657 | 0.14191 | 0.19226 | 0.16022 | 0.16022 | 0.29755 | 0.082397 | -0.068665 | 0.20142 | 0.23346 | 0.16937 | 0.25177 | 0.20599 | 0.013733 | -0.054932 | 122.7814 | 122.6303 | 0.15106 | 122.8912 | 122.8592 | 0.22888 | -0.004577 | 122.7127 | 122.644 | 0.10529 | 122.9004 | 122.8683 | 0.22431 | 0.05951 | 122.9965 | 122.8409 | 122.8592 | -0.21515 | 122.9507 | 122.905 | 122.9324 | -0.20142
2175.8281 | 122.9324 | -122.7356 | 0.1831 | 0.1062 | 0.022751 | 0.0050842 | 0.0036231 | -0.0051932 | -0.0024844 | -0.0060883 | 0.13252 | -0.011487 | -0.0090298 | -0.0011216 | 0.0045351 | -0.012939 | 0.14648 | 0.15564 | 0.1236 | 0.10529 | 0.2243 | 0.018311 | -0.10986 | 0.16937 | 0.17395 | 0.10529 | 0.19226 | 0.16022 | -0.036621 | -0.09613 | 122.7539 | 122.6257 | 0.041199 | 122.8912 | 122.8409 | 0.21515 | -0.036621 | 122.699 | 122.6395 | 0.009156 | 122.905 | 122.8409 | 0.20142 | -0.022888 | 122.9599 | 122.8821 | 122.8592 | -0.29297 | 122.9279 | 122.8958 | 122.9095 | -0.27924
2177.5156 | 123.0515 | -122.699 | 0.15564 | -0.16846 | 0.022965 | 0.004657 | 0.0055457 | -0.0056204 | -0.0037662 | -0.0071563 | -0.14977 | -0.0097775 | -0.0062528 | -0.0024032 | 0.0023989 | -0.014648 | 0.27008 | 0.27466 | 0.23804 | 0.22888 | 0.32501 | 0.11902 | -0.018311 | 0.25177 | 0.3067 | 0.21515 | 0.26093 | 0.23804 | 0.041199 | -0.004578 | 122.818 | 122.6807 | 0.16937 | 122.9736 | 122.9279 | 0.24719 | 0.11444 | 122.7402 | 122.6944 | 0.10529 | 122.9507 | 122.9141 | 0.21973 | 0.082397 | 123.024 | 122.9691 | 122.937 | -0.17395 | 122.9599 | 122.937 | 123.0057 | -0.16022
2179.2031 | 123.0469 | -122.7264 | 0.17395 | -0.23712 | 0.023605 | 0.0048706 | 0.0085363 | -0.0049796 | -0.00056178 | -0.0069427 | -0.18028 | -0.010418 | -0.0043302 | -0.0021896 | 0.0047489 | -0.012298 | 0.19684 | 0.18768 | 0.14191 | 0.17395 | 0.36621 | 0.10529 | -0.054932 | 0.16022 | 0.15564 | 0.059509 | 0.29297 | 0.25635 | 0.013733 | -0.041199 | 122.8317 | 122.6715 | 0.19226 | 122.9141 | 122.9004 | 0.22888 | 0.022888 | 122.7402 | 122.6852 | 0.11902 | 122.8867 | 122.7859 | 0.10071 | 0.082398 | 123.0927 | 122.9233 | 122.8683 | -0.22888 | 123.0194 | 122.9828 | 122.8821 | -0.21515
2180.9531 | 123.0103 | -122.7173 | 0.16479 | -0.015869 | 0.021683 | 0.0055114 | 0.0078955 | -0.0064748 | -0.003339 | -0.0056611 | 0.063858 | -0.0117 | -0.0045438 | -0.00090781 | 0.0013309 | -0.010589 | 0.12817 | 0.15106 | 0.13275 | 0.13733 | 0.27924 | 0.064087 | -0.091553 | 0.17395 | 0.17853 | 0.11902 | 0.23804 | 0.20142 | -0.009155 | -0.059509 | 122.7814 | 122.6257 | 0.11444 | 122.8683 | 122.8546 | 0.22888 | -0.036621 | 122.7081 | 122.6578 | 0.073242 | 122.8912 | 122.8363 | 0.17853 | 0.036621 | 122.9965 | 122.8455 | 122.85 | -0.25635 | 122.9553 | 122.9187 | 122.8958 | -0.2243
2182.7031 | 123.0652 | -122.7127 | 0.16022 | -0.13794 | 0.025742 | 0.0033752 | 0.0029821 | -0.0051932 | 0.0056332 | -0.0043793 | -0.19554 | -0.0082821 | -0.00668 | -0.0013352 | 0.0075259 | -0.014648 | 0.1831 | 0.14191 | 0.068665 | 0.14648 | 0.31128 | 0.041199 | -0.11444 | 0.16022 | 0.13275 | 0.036621 | 0.2243 | 0.20599 | -0.045776 | -0.086975 | 122.7539 | 122.5983 | 0.15106 | 122.8546 | 122.8592 | 0.26093 | 0.022888 | 122.6669 | 122.6257 | 0.064087 | 122.8729 | 122.7493 | 0.1236 | 0.045777 | 123.024 | 122.8958 | 122.7814 | -0.27466 | 122.937 | 122.9187 | 122.8455 | -0.24719
2184.4062 | 123.0469 | -122.7127 | 0.16022 | -0.21423 | 0.025314 | 0.0035888 | 0.0081091 | -0.0069022 | -0.0035526 | -0.0084381 | -0.14214 | -0.011273 | -0.004971 | -0.0015488 | 0.0019717 | -0.011871 | 0.25177 | 0.30212 | 0.23346 | 0.22888 | 0.32959 | 0.15106 | -0.036621 | 0.21973 | 0.30212 | 0.18768 | 0.27008 | 0.21515 | 0.022888 | -0.041199 | 122.8638 | 122.6761 | 0.16937 | 123.0148 | 122.9416 | 0.2655 | 0.091553 | 122.7356 | 122.6715 | 0.10986 | 122.9324 | 122.9004 | 0.22888 | 0.054932 | 123.0423 | 122.9645 | 122.9462 | -0.19684 | 122.9828 | 122.9279 | 123.0148 | -0.20142
2186.1562 | 122.9507 | -122.7356 | 0.17853 | 0.1062 | 0.026383 | 0.0042298 | 0.0046911 | -0.0062612 | 0.0030698 | -0.0058747 | 0.04097 | -0.0076413 | -0.0079618 | 0.0022964 | 0.0077395 | -0.013153 | 0.073242 | 0.004578 | -0.027466 | 0.050354 | 0.28381 | 0.009155 | -0.13275 | 0.059509 | 0.009155 | -0.045776 | 0.19684 | 0.17853 | -0.082397 | -0.13733 | 122.7448 | 122.6028 | 0.10528 | 122.7402 | 122.7859 | 0.18311 | -0.10529 | 122.6532 | 122.5983 | 0.01831 | 122.7951 | 122.6898 | 0.091553 | 0 | 123.0194 | 122.8088 | 122.7081 | -0.31128 | 122.9324 | 122.9141 | 122.7448 | -0.31586
2187.8438 | 122.9324 | -122.7585 | 0.20142 | 0.0070193 | 0.025955 | 0.0033752 | 0.0055457 | -0.0073294 | 0.0032834 | -0.0039521 | 0.010452 | -0.0063595 | -0.003262 | 0.001442 | 0.0056033 | -0.012939 | 0.10071 | 0.07782 | 0.032043 | 0.064087 | 0.29297 | 0.013733 | -0.14648 | 0.068665 | 0.041199 | -0.050354 | 0.21973 | 0.16937 | -0.073242 | -0.13733 | 122.7722 | 122.612 | 0.091553 | 122.8363 | 122.8226 | 0.21057 | -0.10071 | 122.6852 | 122.6212 | 0.018311 | 122.8271 | 122.7081 | 0.086975 | -0.032043 | 123.0515 | 122.8592 | 122.7905 | -0.3479 | 122.9782 | 122.9279 | 122.7997 | -0.33875
2189.5312 | 122.9462 | -122.7539 | 0.1831 | 0.12909 | 0.023392 | 0.0044434 | 0.0027685 | -0.0079702 | -0.005048 | -0.0060883 | 0.1783 | -0.0093503 | -0.0056118 | -0.0024032 | 0.0034671 | -0.012085 | 0.14191 | 0.17395 | 0.13733 | 0.11902 | 0.21057 | 0.032043 | -0.091553 | 0.17853 | 0.17395 | 0.10071 | 0.16479 | 0.15106 | -0.059509 | -0.10986 | 122.7859 | 122.6624 | 0.027466 | 122.9279 | 122.8729 | 0.21057 | -0.041198 | 122.6944 | 122.644 | -0.01831 | 122.9324 | 122.8546 | 0.21057 | -0.032043 | 122.9645 | 122.8958 | 122.8912 | -0.27466 | 122.9187 | 122.905 | 122.9279 | -0.29297
2191.2812 | 122.9599 | -122.7493 | 0.17395 | 0.075684 | 0.027451 | 0.0035888 | 0.0066137 | -0.0066884 | 0.0030698 | -0.0039521 | -0.0048066 | -0.0080685 | -0.0058254 | -0.00090781 | 0.0058169 | -0.014007 | 0.082397 | 0.009155 | -0.013733 | 0.032043 | 0.25635 | 0.004578 | -0.15106 | 0.045776 | 0.027466 | -0.059509 | 0.20599 | 0.16937 | -0.10071 | -0.12817 | 122.7539 | 122.5983 | 0.082398 | 122.7585 | 122.7814 | 0.18311 | -0.091553 | 122.6486 | 122.6212 | 0.032044 | 122.7951 | 122.6898 | 0.068665 | -0.004577 | 123.0057 | 122.8317 | 122.7356 | -0.32501 | 122.9553 | 122.9187 | 122.7768 | -0.30212
2193.0469 | 123.024 | -122.731 | 0.15106 | -0.25238 | 0.02446 | 0.004657 | 0.0087499 | -0.010106 | -0.005048 | -0.0065155 | -0.2108 | -0.010418 | -0.0041164 | -0.0032578 | 0.0019717 | -0.01123 | 0.21057 | 0.23804 | 0.17395 | 0.19684 | 0.36621 | 0.11902 | -0.036621 | 0.15106 | 0.19226 | 0.09613 | 0.32044 | 0.25177 | 0.018311 | -0.050354 | 122.85 | 122.6944 | 0.21515 | 122.9691 | 122.9279 | 0.23346 | 0.059509 | 122.7493 | 122.6807 | 0.16937 | 122.8821 | 122.8271 | 0.14648 | 0.10071 | 123.0972 | 122.9416 | 122.905 | -0.18768 | 123.0515 | 122.9828 | 122.9233 | -0.20142
2194.7969 | 122.9416 | -122.7768 | 0.18768 | 0.1062 | 0.021256 | 0.0048706 | 0.0031957 | -0.0060476 | -0.0054752 | -0.0071563 | 0.10963 | -0.0097775 | -0.0071072 | 0.0010148 | 0.0036807 | -0.009094 | 0.12817 | 0.17853 | 0.13733 | 0.11902 | 0.27466 | 0.050354 | -0.082397 | 0.16022 | 0.16937 | 0.10071 | 0.21515 | 0.16937 | -0.013733 | -0.073242 | 122.8271 | 122.6944 | 0.086975 | 122.9553 | 122.8958 | 0.20142 | -0.059509 | 122.7631 | 122.7036 | 0.027466 | 122.937 | 122.8775 | 0.17395 | -0.01831 | 123.0515 | 122.905 | 122.9141 | -0.27008 | 122.9919 | 122.9462 | 122.9462 | -0.26092
2196.4844 | 122.9462 | -122.7631 | 0.16937 | 0.068054 | 0.021896 | 0.0070068 | 0.0040503 | -0.0090384 | -0.0054752 | -0.0065155 | 0.056228 | -0.010418 | -0.0073208 | -0.0028306 | 0.0043215 | -0.011871 | 0.12817 | 0.16022 | 0.12817 | 0.11902 | 0.27924 | 0.073242 | -0.082397 | 0.17395 | 0.16022 | 0.11444 | 0.21973 | 0.20142 | -0.013733 | -0.07782 | 122.8363 | 122.6807 | 0.10986 | 122.9233 | 122.8821 | 0.20142 | -0.041199 | 122.7493 | 122.6852 | 0.050354 | 122.937 | 122.8775 | 0.19226 | 0.032043 | 123.0423 | 122.8912 | 122.8912 | -0.25177 | 122.9828 | 122.9645 | 122.9233 | -0.24719
2198.2344 | 123.0789 | -122.7127 | 0.15564 | -0.015869 | 0.020828 | 0.0072204 | 0.0074683 | -0.0069022 | -0.0037662 | -0.0071563 | -0.035324 | -0.010846 | -0.0075344 | -0.0028306 | 0.00047633 | -0.012939 | 0.16937 | 0.17853 | 0.16022 | 0.17395 | 0.31586 | 0.07782 | -0.059509 | 0.21515 | 0.23804 | 0.16479 | 0.24261 | 0.20599 | 0.032043 | -0.041199 | 122.7905 | 122.6532 | 0.16022 | 122.8912 | 122.8867 | 0.23346 | 0.013733 | 122.7448 | 122.6715 | 0.086975 | 122.9279 | 122.8775 | 0.20599 | 0.050354 | 123.0286 | 122.8821 | 122.8729 | -0.21515 | 122.9553 | 122.9187 | 122.9507 | -0.19684
2199.9844 | 122.9462 | -122.7448 | 0.1831 | 0.029907 | 0.027664 | 0.001239 | 0.0010595 | -0.0069022 | 0.0049924 | -0.0048065 | -0.050583 | -0.0074277 | -0.0075344 | -0.0011216 | 0.0090213 | -0.015075 | 0.13275 | 0.050354 | 0.004578 | 0.054932 | 0.28839 | 0.004578 | -0.13733 | 0.064087 | 0.041199 | -0.059509 | 0.20599 | 0.16937 | -0.068665 | -0.15106 | 122.7493 | 122.6074 | 0.10529 | 122.7951 | 122.7997 | 0.19226 | -0.050354 | 122.6761 | 122.5937 | 0.022889 | 122.8088 | 122.6852 | 0.091553 | -0.013732 | 123.0331 | 122.8775 | 122.7493 | -0.32043 | 122.9507 | 122.9141 | 122.7859 | -0.33417
2201.7344 | 123.0515 | -122.6898 | 0.15564 | -0.1532 | 0.024033 | 0.006366 | 0.0098181 | -0.0049796 | -0.003339 | -0.0071563 | -0.16502 | -0.0091367 | -0.0047574 | -0.0015488 | 0.00026273 | -0.01123 | 0.24719 | 0.29297 | 0.23346 | 0.23804 | 0.31586 | 0.13275 | -0.013733 | 0.26093 | 0.31586 | 0.19226 | 0.25635 | 0.22888 | 0.050354 | -0.018311 | 122.8226 | 122.6761 | 0.16022 | 122.9828 | 122.9279 | 0.25177 | 0.091552 | 122.7402 | 122.6715 | 0.10071 | 122.9507 | 122.8821 | 0.21057 | 0.073242 | 123.0057 | 122.937 | 122.9233 | -0.16937 | 122.9462 | 122.9187 | 123.0057 | -0.17395
2203.4375 | 122.9599 | -122.731 | 0.1831 | 0.037537 | 0.020828 | 0.004657 | 0.0046911 | -0.0073294 | -0.0041934 | -0.0063019 | 0.086746 | -0.011487 | -0.0071072 | -0.0024032 | 0.0041079 | -0.012726 | 0.14648 | 0.16022 | 0.13733 | 0.13275 | 0.30212 | 0.082397 | -0.068665 | 0.16937 | 0.17853 | 0.10986 | 0.21973 | 0.20142 | -0.013733 | -0.050354 | 122.8134 | 122.6624 | 0.11902 | 122.8912 | 122.8638 | 0.20142 | -0.036621 | 122.7173 | 122.6807 | 0.036622 | 122.9004 | 122.8409 | 0.16022 | 0.018311 | 123.0331 | 122.8775 | 122.8683 | -0.25177 | 122.9507 | 122.9324 | 122.9095 | -0.23346
2205.1719 | 123.0881 | -122.7173 | 0.15564 | -0.24475 | 0.025528 | 0.0048706 | 0.0089635 | -0.004125 | 0.0020016 | -0.0069427 | -0.24895 | -0.010418 | -0.0039028 | -0.00048061 | 0.0028263 | -0.014648 | 0.19684 | 0.13275 | 0.068665 | 0.15106 | 0.40283 | 0.10071 | -0.068665 | 0.1236 | 0.12817 | 0.032043 | 0.29755 | 0.23804 | -0.013733 | -0.064087 | 122.818 | 122.6486 | 0.24719 | 122.85 | 122.8683 | 0.21973 | 0.041198 | 122.7036 | 122.6532 | 0.14191 | 122.8409 | 122.7493 | 0.09613 | 0.082397 | 123.1201 | 122.9141 | 122.7859 | -0.22431 | 123.0148 | 122.9553 | 122.8455 | -0.21973
2206.9219 | 123.0469 | -122.7219 | 0.16479 | -0.19897 | 0.025528 | 0.0040162 | 0.0098181 | -0.0047658 | 0.00093342 | -0.0073701 | -0.24895 | -0.0095639 | -0.0045438 | -0.0017624 | 0.0028263 | -0.013366 | 0.17395 | 0.16937 | 0.12817 | 0.16479 | 0.3891 | 0.12817 | -0.059509 | 0.17395 | 0.14648 | 0.054932 | 0.27924 | 0.26093 | -0.018311 | -0.068665 | 122.85 | 122.6624 | 0.2243 | 122.8912 | 122.8867 | 0.2243 | 0.009155 | 122.7036 | 122.6532 | 0.11444 | 122.8958 | 122.7768 | 0.1236 | 0.09613 | 123.111 | 122.8958 | 122.85 | -0.2243 | 123.0011 | 122.9828 | 122.8683 | -0.23346
2208.6875 | 123.0835 | -122.7036 | 0.16479 | -0.13031 | 0.022751 | 0.0040162 | 0.0046911 | -0.0071158 | -0.0039798 | -0.0084381 | -0.14214 | -0.012341 | -0.0039028 | -0.0021896 | 0.0021853 | -0.011657 | 0.25635 | 0.3067 | 0.23804 | 0.23804 | 0.32044 | 0.12817 | -0.036621 | 0.27924 | 0.31128 | 0.19226 | 0.23346 | 0.21057 | 0.018311 | -0.027466 | 122.8317 | 122.6669 | 0.15564 | 123.0103 | 122.9416 | 0.27466 | 0.091553 | 122.7219 | 122.6761 | 0.068664 | 122.9828 | 122.8958 | 0.21973 | 0.045776 | 123.024 | 122.9599 | 122.9416 | -0.20142 | 122.937 | 122.9141 | 123.0148 | -0.19226
2210.375 | 123.0606 | -122.7081 | 0.15564 | -0.00061023 | 0.023819 | 0.0042298 | 0.0076819 | -0.0051932 | -0.0037662 | -0.0065155 | -0.020065 | -0.012127 | -0.0034756 | 0.00016019 | 0.00026273 | -0.012512 | 0.16479 | 0.19226 | 0.17395 | 0.17853 | 0.31128 | 0.10529 | -0.068665 | 0.22888 | 0.23804 | 0.15564 | 0.2243 | 0.21973 | 0.018311 | -0.041199 | 122.8134 | 122.6395 | 0.15564 | 122.9004 | 122.8867 | 0.24719 | 0.009155 | 122.7264 | 122.6669 | 0.068664 | 122.937 | 122.8638 | 0.19684 | 0.064087 | 123.0194 | 122.8729 | 122.8821 | -0.22431 | 122.9324 | 122.9279 | 122.9462 | -0.19684
2212.125 | 122.9553 | -122.7722 | 0.20599 | 0.037537 | 0.026169 | 0.0044434 | 0.0027685 | -0.0054068 | 0.0058468 | -0.0035249 | -0.020065 | -0.0072141 | -0.0056118 | -0.0015488 | 0.0079531 | -0.01593 | 0.073242 | 0.018311 | -0.036621 | 0.054932 | 0.26093 | 0.013733 | -0.15564 | 0.064087 | 0.018311 | -0.059509 | 0.20599 | 0.19226 | -0.10071 | -0.14191 | 122.7859 | 122.6166 | 0.054931 | 122.7905 | 122.8271 | 0.21057 | -0.13275 | 122.6715 | 122.6303 | 0 | 122.8363 | 122.7127 | 0.082398 | -0.013733 | 123.0331 | 122.8455 | 122.7356 | -0.36163 | 122.9782 | 122.9645 | 122.7905 | -0.3479
2213.8906 | 122.9416 | -122.7539 | 0.19226 | 0.12909 | 0.022537 | 0.0040162 | 0.0029821 | -0.0064748 | -0.0022708 | -0.0041657 | 0.12489 | -0.010418 | -0.0062528 | -0.0026168 | 0.0049625 | -0.010803 | 0.14648 | 0.17395 | 0.13733 | 0.11902 | 0.21057 | 0.004578 | -0.1236 | 0.19226 | 0.1831 | 0.086975 | 0.15564 | 0.14191 | -0.045776 | -0.10986 | 122.7585 | 122.6303 | 0.01831 | 122.9279 | 122.8729 | 0.24261 | -0.045777 | 122.7081 | 122.644 | -0.036621 | 122.9462 | 122.8409 | 0.19684 | -0.050354 | 122.9645 | 122.9004 | 122.8912 | -0.31586 | 122.9095 | 122.8958 | 122.937 | -0.30212
2215.5781 | 122.9416 | -122.7768 | 0.18768 | 0.1825 | 0.021896 | 0.0065796 | 0.0025549 | -0.008611 | -0.00013458 | -0.0056611 | 0.14778 | -0.0091367 | -0.0068936 | -0.0026168 | 0.0038943 | -0.013153 | 0.14648 | 0.15564 | 0.10071 | 0.10529 | 0.20142 | 0.022888 | -0.11902 | 0.17853 | 0.18768 | 0.09613 | 0.16022 | 0.1236 | -0.045776 | -0.10529 | 122.7997 | 122.6578 | 0.013733 | 122.9324 | 122.8821 | 0.22431 | -0.041199 | 122.731 | 122.6715 | -0.027466 | 122.9553 | 122.8729 | 0.20142 | -0.064087 | 122.9782 | 122.9233 | 122.8775 | -0.3067 | 122.937 | 122.9004 | 122.9645 | -0.29297
2217.2656 | 122.9919 | -122.7402 | 0.19226 | 0.11383 | 0.024033 | 0.002948 | 0.0046911 | -0.0071158 | -0.00034818 | -0.0071563 | 0.04097 | -0.0080685 | -0.0068936 | -0.00048061 | 0.0056033 | -0.012085 | 0.086975 | 0.018311 | -0.004578 | 0.032043 | 0.27466 | -0.013733 | -0.16937 | 0.091553 | 0.041199 | -0.009155 | 0.19684 | 0.16479 | -0.064087 | -0.14191 | 122.7264 | 122.5708 | 0.082397 | 122.7585 | 122.7722 | 0.20142 | -0.10529 | 122.6761 | 122.5983 | 0.004577 | 122.8317 | 122.731 | 0.13275 | -0.027466 | 123.0148 | 122.8271 | 122.7356 | -0.36163 | 122.937 | 122.905 | 122.7814 | -0.33417
2219.0156 | 122.9599 | -122.7356 | 0.16479 | 0.090942 | 0.020828 | 0.0067932 | 0.0049047 | -0.0071158 | -0.0041934 | -0.0063019 | 0.13252 | -0.011487 | -0.006039 | -0.0021896 | 0.0023989 | -0.010589 | 0.13275 | 0.16022 | 0.12817 | 0.13733 | 0.27466 | 0.045776 | -0.09613 | 0.19226 | 0.1831 | 0.10529 | 0.24261 | 0.19226 | -0.018311 | -0.073242 | 122.7814 | 122.6395 | 0.10986 | 122.8958 | 122.8729 | 0.23346 | -0.032044 | 122.7173 | 122.6624 | 0.07782 | 122.9279 | 122.8409 | 0.17853 | 0.027466 | 123.0103 | 122.8683 | 122.8638 | -0.26092 | 122.9782 | 122.9279 | 122.9187 | -0.23804
2220.7656 | 122.9553 | -122.7539 | 0.18768 | 0.037537 | 0.021256 | 0.0052978 | 0.0040503 | -0.0081838 | -0.0035526 | -0.0050201 | 0.079117 | -0.0093503 | -0.0090298 | -0.0013352 | 0.0026125 | -0.009094 | 0.14648 | 0.16937 | 0.13275 | 0.11444 | 0.25635 | 0.059509 | -0.07782 | 0.19684 | 0.16022 | 0.10986 | 0.22888 | 0.1831 | -0.009155 | -0.082397 | 122.8134 | 122.6761 | 0.068665 | 122.9233 | 122.8683 | 0.19226 | -0.041199 | 122.7448 | 122.6715 | 0.041199 | 122.9507 | 122.8638 | 0.19226 | -0.004578 | 123.0103 | 122.9004 | 122.8867 | -0.2655 | 122.9828 | 122.937 | 122.9141 | -0.27008
2222.5156 | 123.056 | -122.7173 | 0.16937 | -0.18372 | 0.024674 | 0.0070068 | 0.0078955 | -0.0073294 | 0.00093342 | -0.0060883 | -0.26421 | -0.0089229 | -0.0053982 | 0.00016019 | 0.0030399 | -0.014221 | 0.1831 | 0.15564 | 0.1236 | 0.12817 | 0.39368 | 0.082397 | -0.073242 | 0.15564 | 0.15106 | 0.068665 | 0.29297 | 0.27466 | -0.004578 | -0.068665 | 122.7997 | 122.644 | 0.2243 | 122.8729 | 122.8455 | 0.20142 | 0.013732 | 122.7127 | 122.6486 | 0.1236 | 122.8729 | 122.7859 | 0.13733 | 0.10529 | 123.111 | 122.9004 | 122.8409 | -0.24261 | 123.0103 | 122.9919 | 122.8683 | -0.23804
2224.2188 | 123.0698 | -122.7219 | 0.16937 | -0.12268 | 0.024887 | 0.004657 | 0.0042639 | -0.0081838 | 0.0020016 | -0.0033111 | -0.14977 | -0.0091367 | -0.0064664 | 0.00016019 | 0.0064577 | -0.014435 | 0.19684 | 0.13275 | 0.082397 | 0.11444 | 0.30212 | 0.054932 | -0.10529 | 0.15106 | 0.13275 | 0.009155 | 0.21515 | 0.17853 | -0.054932 | -0.09613 | 122.7768 | 122.6166 | 0.13275 | 122.8546 | 122.8363 | 0.21973 | 0.027465 | 122.6669 | 122.6257 | 0.045776 | 122.8729 | 122.731 | 0.10528 | 0.009155 | 123.024 | 122.9187 | 122.8043 | -0.27466 | 122.937 | 122.9004 | 122.8546 | -0.2655
2225.9844 | 122.9736 | -122.7814 | 0.19226 | 0.052795 | 0.025528 | 0.0048706 | 0.0059729 | -0.0054068 | 0.0030698 | -0.0048065 | 0.03334 | -0.010632 | -0.003262 | -5.3406e-05 | 0.0058169 | -0.012298 | 0.068665 | -0.009155 | -0.032043 | 0.045776 | 0.29297 | -0.004578 | -0.13733 | 0.064087 | 0.027466 | -0.07782 | 0.20142 | 0.17853 | -0.091553 | -0.15564 | 122.7768 | 122.644 | 0.10071 | 122.7722 | 122.8271 | 0.18311 | -0.1236 | 122.6898 | 122.6257 | 0.009155 | 122.8455 | 122.7036 | 0.07782 | -0.013733 | 123.0743 | 122.85 | 122.7493 | -0.32959 | 122.9828 | 122.9599 | 122.8088 | -0.3479
2227.7344 | 122.9782 | -122.7585 | 0.16937 | -0.015869 | 0.020828 | 0.0055114 | 0.0061865 | -0.0056204 | -0.0052616 | -0.0045929 | 0.079117 | -0.011487 | -0.0036892 | -0.003685 | 0.0019717 | -0.010589 | 0.1236 | 0.16479 | 0.14191 | 0.13275 | 0.27466 | 0.064087 | -0.09613 | 0.17853 | 0.19226 | 0.11902 | 0.21973 | 0.1831 | 0.004578 | -0.064087 | 122.8226 | 122.6624 | 0.10529 | 122.9233 | 122.8912 | 0.22888 | -0.045777 | 122.7631 | 122.6944 | 0.050354 | 122.937 | 122.8775 | 0.18311 | 0.013732 | 123.0331 | 122.8821 | 122.9004 | -0.2655 | 122.9782 | 122.9416 | 122.9507 | -0.23346
2229.4219 | 122.9553 | -122.7814 | 0.18768 | -0.023499 | 0.026169 | 0.0031616 | 0.0059729 | -0.0062612 | 0.0037106 | -0.0039521 | -0.065842 | -0.0082821 | -0.0039028 | 0.0012284 | 0.0083805 | -0.012726 | 0.10986 | 0.10529 | 0.036621 | 0.086975 | 0.28381 | 0.009155 | -0.12817 | 0.082397 | 0.064087 | -0.054932 | 0.21515 | 0.17395 | -0.086975 | -0.12817 | 122.7905 | 122.6532 | 0.09613 | 122.8867 | 122.8683 | 0.21515 | -0.07782 | 122.6944 | 122.6532 | 0.027466 | 122.8638 | 122.7264 | 0.073242 | -0.013733 | 123.0652 | 122.8912 | 122.818 | -0.31586 | 122.9965 | 122.9553 | 122.8455 | -0.31586
2231.1875 | 123.0011 | -122.7493 | 0.17853 | 0.12909 | 0.026596 | 0.0042298 | 0.0057593 | -0.0081838 | 0.00071982 | -0.0043793 | 0.13252 | -0.0082821 | -0.001553 | 0.0016556 | 0.0064577 | -0.011444 | 0.054932 | 0.036621 | 0 | 0.036621 | 0.26093 | 0.009155 | -0.15106 | 0.10529 | 0.054932 | -0.009155 | 0.19684 | 0.16479 | -0.07782 | -0.12817 | 122.7585 | 122.5983 | 0.082397 | 122.7859 | 122.7859 | 0.18768 | -0.1236 | 122.6715 | 122.6212 | 0.01831 | 122.8546 | 122.7402 | 0.11902 | -0.013733 | 123.0103 | 122.8043 | 122.7493 | -0.32959 | 122.9462 | 122.9141 | 122.8043 | -0.3067
2232.9375 | 122.937 | -122.7631 | 0.1831 | 0.1825 | 0.023819 | 0.0038024 | 0.0068273 | -0.005834 | -0.0039798 | -0.0039521 | 0.17067 | -0.010632 | -0.0073208 | -0.0021896 | 0.0081667 | -0.011871 | 0.1236 | 0.15564 | 0.1236 | 0.10071 | 0.19226 | 0.018311 | -0.14191 | 0.16937 | 0.19226 | 0.091553 | 0.16479 | 0.13733 | -0.032043 | -0.091553 | 122.7814 | 122.6212 | 0.009156 | 122.9187 | 122.8638 | 0.24262 | -0.059509 | 122.731 | 122.6715 | -0.01831 | 122.9324 | 122.8546 | 0.18311 | -0.045776 | 122.9553 | 122.8867 | 122.8867 | -0.32501 | 122.9279 | 122.9004 | 122.9553 | -0.27466
2234.7031 | 122.937 | -122.7539 | 0.19684 | 0.11383 | 0.023178 | 0.0052978 | 0.0068273 | -0.0096792 | -0.004407 | -0.0073701 | 0.20882 | -0.010846 | -0.0064664 | 0.00037379 | 0.0026125 | -0.01123 | 0.14191 | 0.16937 | 0.14648 | 0.10529 | 0.21973 | 0.050354 | -0.10986 | 0.16937 | 0.16022 | 0.068665 | 0.17395 | 0.14648 | -0.050354 | -0.10071 | 122.8043 | 122.644 | 0.022889 | 122.9233 | 122.8592 | 0.21515 | -0.054931 | 122.7036 | 122.6532 | -0.022888 | 122.9233 | 122.8226 | 0.16937 | -0.050354 | 122.9736 | 122.8958 | 122.9004 | -0.3067 | 122.9279 | 122.9004 | 122.9141 | -0.29755
2236.4062 | 122.9691 | -122.7722 | 0.18768 | -0.054016 | 0.027878 | 0.0044434 | 0.0038367 | -0.0071158 | 0.0047788 | -0.0054475 | -0.096359 | -0.0089229 | -0.0030484 | -0.0013352 | 0.0062441 | -0.01358 | 0.14191 | 0.12817 | 0.064087 | 0.10071 | 0.31586 | 0.027466 | -0.11444 | 0.12817 | 0.091553 | -0.018311 | 0.2243 | 0.17853 | -0.082397 | -0.11902 | 122.7997 | 122.6578 | 0.12817 | 122.9004 | 122.8729 | 0.21515 | -0.045776 | 122.6898 | 122.6532 | 0.036621 | 122.9004 | 122.7539 | 0.10071 | -0.009155 | 123.0881 | 122.9141 | 122.8363 | -0.30212 | 122.9965 | 122.9507 | 122.8638 | -0.3067
2238.0938 | 122.9919 | -122.7768 | 0.19226 | 0.12909 | 0.02681 | 0.0052978 | 0.0038367 | -0.0054068 | 0.00093342 | -0.0052337 | 0.102 | -0.0082821 | -0.0075344 | -0.0015488 | 0.0060305 | -0.011871 | 0.054932 | 0.009155 | -0.022888 | 0.018311 | 0.2655 | -0.013733 | -0.17395 | 0.059509 | 0.009155 | -0.064087 | 0.20142 | 0.15564 | -0.082397 | -0.16479 | 122.7631 | 122.6028 | 0.073242 | 122.7859 | 122.7951 | 0.19226 | -0.13733 | 122.6944 | 122.612 | 0.009155 | 122.8363 | 122.7127 | 0.10071 | -0.036621 | 123.0423 | 122.8317 | 122.7539 | -0.36621 | 122.9782 | 122.9324 | 122.7859 | -0.35706
2239.8281 | 122.9416 | -122.7676 | 0.17853 | 0.068054 | 0.027237 | 0.0035888 | 0.0091773 | -0.0081838 | 0.003497 | -0.0033111 | 0.0028229 | -0.011273 | -0.0062528 | -0.0013352 | 0.0062441 | -0.013153 | 0.036621 | 0.018311 | -0.018311 | 0.050354 | 0.27008 | -0.004578 | -0.14648 | 0.041199 | 0.027466 | -0.050354 | 0.21973 | 0.17853 | -0.086975 | -0.13733 | 122.7631 | 122.6212 | 0.091553 | 122.7859 | 122.818 | 0.19684 | -0.14191 | 122.6807 | 122.6303 | 0.041199 | 122.8088 | 122.7173 | 0.086975 | 0 | 123.0377 | 122.8043 | 122.7493 | -0.32501 | 122.9874 | 122.9462 | 122.7951 | -0.31586
2241.9219 | 123.0469 | -122.7219 | 0.16937 | -0.26764 | 0.025101 | 0.0033752 | 0.0087499 | -0.0039114 | -0.006116 | -0.0048065 | -0.19554 | -0.010418 | -0.0047574 | -0.0011216 | -0.0010191 | -0.012085 | 0.17395 | 0.23346 | 0.17853 | 0.20142 | 0.36621 | 0.11902 | -0.050354 | 0.14648 | 0.20599 | 0.086975 | 0.31586 | 0.27466 | 0.013733 | -0.059509 | 122.8409 | 122.6715 | 0.19684 | 122.9553 | 122.9233 | 0.25177 | 0.004577 | 122.7356 | 122.6624 | 0.14648 | 122.8683 | 122.8088 | 0.14648 | 0.10529 | 123.0881 | 122.8958 | 122.9004 | -0.21973 | 123.0377 | 122.9965 | 122.9279 | -0.22888
2243.8438 | 123.0515 | -122.7356 | 0.15564 | -0.22949 | 0.022537 | 0.0052978 | 0.0091773 | -0.0062612 | -0.003339 | -0.0071563 | -0.18791 | -0.011059 | -0.0039028 | -0.0013352 | 0.0023989 | -0.014221 | 0.14648 | 0.18768 | 0.1236 | 0.15564 | 0.37537 | 0.09613 | -0.050354 | 0.13733 | 0.16022 | 0.068665 | 0.3067 | 0.27466 | 0.004578 | -0.054932 | 122.8317 | 122.6852 | 0.21973 | 122.9233 | 122.8912 | 0.20599 | -0.009156 | 122.7402 | 122.6807 | 0.15106 | 122.8729 | 122.8043 | 0.1236 | 0.11902 | 123.111 | 122.8821 | 122.8592 | -0.20599 | 123.0423 | 123.0103 | 122.8958 | -0.21057
2245.5781 | 123.0515 | -122.7264 | 0.17395 | -0.27527 | 0.02446 | 0.0042298 | 0.0074683 | -0.004125 | -0.0020572 | -0.0088653 | -0.19554 | -0.0080685 | -0.0039028 | -5.3406e-05 | 0.00090353 | -0.012298 | 0.17853 | 0.19226 | 0.15106 | 0.17853 | 0.37537 | 0.10986 | -0.050354 | 0.15106 | 0.17395 | 0.064087 | 0.29755 | 0.27924 | 0.004578 | -0.059509 | 122.8363 | 122.6761 | 0.20142 | 122.9187 | 122.905 | 0.22888 | 0.004578 | 122.731 | 122.6669 | 0.1236 | 122.8775 | 122.7905 | 0.1236 | 0.10529 | 123.1018 | 122.905 | 122.8775 | -0.2243 | 123.024 | 123.0057 | 122.9004 | -0.23346
2247.3125 | 123.0652 | -122.731 | 0.17853 | -0.092163 | 0.027023 | 0.0023072 | 0.0057593 | -0.005834 | 0.0026424 | -0.0043793 | -0.11162 | -0.0097775 | -0.0034756 | -5.3406e-05 | 0.0056033 | -0.014007 | 0.15564 | 0.12817 | 0.064087 | 0.10071 | 0.28839 | 0.041199 | -0.10071 | 0.14191 | 0.15106 | 0.036621 | 0.21973 | 0.1831 | -0.07782 | -0.11902 | 122.7722 | 122.6303 | 0.10986 | 122.8592 | 122.8317 | 0.20142 | -0.022888 | 122.6532 | 122.612 | 0.041199 | 122.8729 | 122.7676 | 0.15564 | 0.004577 | 123.0194 | 122.8867 | 122.7951 | -0.27924 | 122.9507 | 122.9141 | 122.8821 | -0.29755
2249.0781 | 123.056 | -122.7219 | 0.17853 | 0.014648 | 0.02211 | 0.006366 | 0.0053321 | -0.0039114 | -0.0080386 | -0.0082245 | 0.071487 | -0.010205 | -0.0056118 | -0.0013352 | -0.00080527 | -0.012939 | 0.12817 | 0.16937 | 0.14191 | 0.14191 | 0.27924 | 0.064087 | -0.068665 | 0.1831 | 0.21973 | 0.16022 | 0.25177 | 0.20599 | 0.013733 | -0.045776 | 122.7859 | 122.6532 | 0.10071 | 122.8912 | 122.8638 | 0.21057 | -0.050354 | 122.7356 | 122.6761 | 0.073242 | 122.905 | 122.8821 | 0.20599 | 0.027466 | 123.0011 | 122.85 | 122.8638 | -0.24719 | 122.9736 | 122.9279 | 122.9416 | -0.2243
2250.8438 | 123.0743 | -122.7173 | 0.16022 | -0.099793 | 0.02681 | 0.002948 | 0.0040503 | -0.0060476 | 0.0026424 | -0.0054475 | -0.16502 | -0.0091367 | -0.00668 | -0.00026701 | 0.0051761 | -0.016571 | 0.16479 | 0.14191 | 0.07782 | 0.13275 | 0.31128 | 0.027466 | -0.10986 | 0.13733 | 0.15106 | 0.036621 | 0.23346 | 0.19226 | -0.064087 | -0.10529 | 122.7448 | 122.6074 | 0.15106 | 122.8592 | 122.85 | 0.24261 | 0.004578 | 122.6532 | 122.612 | 0.073242 | 122.8546 | 122.7539 | 0.14191 | 0.032044 | 123.0286 | 122.8821 | 122.7951 | -0.27008 | 122.9507 | 122.9095 | 122.8683 | -0.2655
2252.5938 | 123.0927 | -122.7356 | 0.16022 | -0.14557 | 0.022537 | 0.0061524 | 0.0081091 | -0.0062612 | -0.0054752 | -0.0086517 | -0.050583 | -0.012127 | -0.0056118 | -0.001976 | 0.0013309 | -0.012298 | 0.21057 | 0.27466 | 0.2243 | 0.2243 | 0.32044 | 0.11902 | -0.032043 | 0.2655 | 0.31128 | 0.24261 | 0.25635 | 0.2243 | 0.036621 | -0.032043 | 122.8546 | 122.7036 | 0.16022 | 123.0103 | 122.9599 | 0.25635 | 0.050354 | 122.7722 | 122.7036 | 0.096131 | 123.0011 | 122.9782 | 0.27466 | 0.064087 | 123.056 | 122.9462 | 122.9599 | -0.19226 | 122.9919 | 122.9599 | 123.0469 | -0.19226
2254.2969 | 122.9599 | -122.7859 | 0.19226 | 0.045166 | 0.025955 | 0.0048706 | 0.0046911 | -0.0047658 | 0.0041378 | -0.0048065 | 0.03334 | -0.0089229 | -0.0047574 | 0.0010148 | 0.0051761 | -0.014435 | 0.045776 | 0.009155 | -0.027466 | 0.027466 | 0.25635 | 0.009155 | -0.14648 | 0.054932 | 0.013733 | -0.064087 | 0.20599 | 0.17853 | -0.10071 | -0.13733 | 122.7951 | 122.6395 | 0.064087 | 122.7951 | 122.8134 | 0.17395 | -0.14648 | 122.6852 | 122.6486 | 0.013733 | 122.8409 | 122.7219 | 0.073242 | -0.013733 | 123.0423 | 122.8317 | 122.7585 | -0.33874 | 122.9919 | 122.9645 | 122.7997 | -0.32959
2256.0469 | 123.0743 | -122.7173 | 0.16479 | -0.22949 | 0.023605 | 0.0038024 | 0.0085363 | -0.0081838 | -0.0018436 | -0.0063019 | -0.24895 | -0.011914 | -0.0030484 | 0.00016019 | 0.0021853 | -0.011871 | 0.14191 | 0.16022 | 0.10071 | 0.14191 | 0.3891 | 0.09613 | -0.054932 | 0.13275 | 0.15106 | 0.068665 | 0.31586 | 0.27466 | -0.022888 | -0.045776 | 122.8134 | 122.6624 | 0.2243 | 122.8775 | 122.8592 | 0.19684 | -0.022888 | 122.6944 | 122.6715 | 0.15106 | 122.85 | 122.7859 | 0.11444 | 0.10986 | 123.1064 | 122.8592 | 122.818 | -0.21973 | 123.0331 | 122.9919 | 122.8683 | -0.21057
2257.7969 | 123.0331 | -122.731 | 0.15106 | 0.037537 | 0.019547 | 0.0059388 | 0.0044775 | -0.005834 | -0.0056888 | -0.0080109 | 0.071487 | -0.010632 | -0.0041164 | -0.0026168 | 0.0030399 | -0.010803 | 0.10071 | 0.16022 | 0.14648 | 0.14191 | 0.32044 | 0.07782 | -0.073242 | 0.17853 | 0.17853 | 0.12817 | 0.2243 | 0.19684 | 0 | -0.082397 | 122.8088 | 122.6578 | 0.16937 | 122.8912 | 122.8729 | 0.21515 | -0.050354 | 122.731 | 122.6486 | 0.073242 | 122.9095 | 122.8592 | 0.21057 | 0.045776 | 123.0515 | 122.8317 | 122.8775 | -0.2243 | 122.9553 | 122.9279 | 122.9095 | -0.23346
2259.5469 | 123.0469 | -122.731 | 0.16022 | -0.17609 | 0.024674 | 0.0055114 | 0.0049047 | -0.0073294 | -0.0031254 | -0.0065155 | -0.096359 | -0.011914 | -0.00668 | -0.0026168 | 0.00068993 | -0.012298 | 0.23804 | 0.27924 | 0.23804 | 0.2243 | 0.3479 | 0.13275 | -0.027466 | 0.23804 | 0.28839 | 0.18768 | 0.2655 | 0.2243 | 0.045776 | -0.032043 | 122.8638 | 122.7036 | 0.18768 | 123.0103 | 122.9553 | 0.25177 | 0.07782 | 122.7768 | 122.699 | 0.10529 | 122.9691 | 122.9187 | 0.21973 | 0.064087 | 123.0789 | 122.9691 | 122.9691 | -0.18768 | 122.9965 | 122.9553 | 123.0194 | -0.19226
2261.2344 | 123.0835 | -122.7081 | 0.16479 | -0.084534 | 0.02681 | 0.0027344 | 0.0046911 | -0.0047658 | 0.0026424 | -0.0058747 | -0.18028 | -0.0089229 | -0.0056118 | -0.0013352 | 0.0068851 | -0.014648 | 0.17395 | 0.13275 | 0.07782 | 0.13733 | 0.3067 | 0.059509 | -0.11444 | 0.15106 | 0.14648 | 0.032043 | 0.2243 | 0.19226 | -0.054932 | -0.10071 | 122.7676 | 122.5937 | 0.14191 | 122.8409 | 122.8455 | 0.25177 | 0.009155 | 122.6532 | 122.6074 | 0.059509 | 122.8592 | 122.7402 | 0.13275 | 0.027466 | 123.0148 | 122.8821 | 122.7859 | -0.27924 | 122.9324 | 122.9004 | 122.8546 | -0.2655
2262.9688 | 122.9553 | -122.7539 | 0.19684 | 0.1825 | 0.024246 | 0.0061524 | 0.0019141 | -0.0081838 | -0.00056178 | -0.0069427 | 0.15541 | -0.012127 | -0.0088162 | -0.0021896 | 0.0056033 | -0.013794 | 0.12817 | 0.14648 | 0.10071 | 0.11902 | 0.19684 | 0.018311 | -0.14648 | 0.16479 | 0.18768 | 0.10529 | 0.17853 | 0.13275 | -0.050354 | -0.10071 | 122.7722 | 122.6074 | 0 | 122.9004 | 122.8729 | 0.2655 | -0.068664 | 122.7036 | 122.6532 | -0.01831 | 122.9187 | 122.8592 | 0.20599 | -0.064087 | 122.9507 | 122.8821 | 122.8546 | -0.34332 | 122.9324 | 122.8867 | 122.9416 | -0.29755
2264.7344 | 123.0057 | -122.7219 | 0.16937 | 0.14435 | 0.026169 | 0.0040162 | 0.0038367 | -0.0066884 | 0.0022152 | -0.0056611 | 0.16304 | -0.0089229 | -0.0071072 | -5.3406e-05 | 0.0060305 | -0.012726 | 0.10529 | 0.027466 | 0.013733 | 0.054932 | 0.24261 | -0.013733 | -0.18768 | 0.13275 | 0.12817 | 0.045776 | 0.16479 | 0.15106 | -0.059509 | -0.10529 | 122.7081 | 122.5342 | 0.073242 | 122.7493 | 122.7768 | 0.24261 | -0.064087 | 122.6624 | 122.6166 | -0.004578 | 122.8546 | 122.7676 | 0.15106 | -0.018311 | 122.9645 | 122.8271 | 122.7356 | -0.35706 | 122.8867 | 122.8729 | 122.85 | -0.27466
2266.4375 | 123.0652 | -122.7219 | 0.16479 | -0.2066 | 0.022751 | 0.0055114 | 0.010032 | -0.0088248 | -0.0037662 | -0.0037385 | -0.16502 | -0.010846 | -0.0068936 | -0.0026168 | -0.00037807 | -0.012726 | 0.26093 | 0.2655 | 0.24261 | 0.23346 | 0.34332 | 0.1236 | -0.027466 | 0.25177 | 0.32501 | 0.20599 | 0.25635 | 0.24261 | 0.027466 | -0.032043 | 122.8455 | 122.6944 | 0.17853 | 122.9874 | 122.9553 | 0.26093 | 0.09613 | 122.7493 | 122.6898 | 0.091553 | 122.9736 | 122.9279 | 0.23804 | 0.07782 | 123.0652 | 122.9828 | 122.9645 | -0.19226 | 122.9782 | 122.9645 | 123.0469 | -0.19684
2268.1875 | 122.9828 | -122.7814 | 0.18768 | -0.031128 | 0.028092 | 0.0023072 | 0.0055457 | -0.0088248 | 0.0032834 | -0.0048065 | -0.065842 | -0.0063595 | -0.006039 | -0.00048061 | 0.0064577 | -0.016143 | 0.17853 | 0.086975 | 0.050354 | 0.10071 | 0.28839 | 0.032043 | -0.1236 | 0.11902 | 0.10071 | -0.018311 | 0.23346 | 0.18768 | -0.054932 | -0.13275 | 122.8134 | 122.6578 | 0.10071 | 122.8683 | 122.8821 | 0.2243 | -0.009155 | 122.7264 | 122.6486 | 0.045776 | 122.9004 | 122.7631 | 0.11444 | 0 | 123.0698 | 122.9599 | 122.8317 | -0.31128 | 123.0148 | 122.9691 | 122.8821 | -0.32043
2269.9531 | 122.9691 | -122.7402 | 0.20142 | 0.052795 | 0.02211 | 0.0055114 | 0.0055457 | -0.0073294 | -0.006757 | -0.0067291 | 0.12489 | -0.013623 | -0.0045438 | -0.0026168 | 0.0017581 | -0.012512 | 0.13275 | 0.16937 | 0.1236 | 0.13275 | 0.29297 | 0.064087 | -0.07782 | 0.17395 | 0.17853 | 0.11444 | 0.21057 | 0.19684 | -0.032043 | -0.050354 | 122.8043 | 122.6624 | 0.091553 | 122.9095 | 122.8729 | 0.21057 | -0.068665 | 122.7081 | 122.6898 | 0.009155 | 122.9141 | 122.8546 | 0.16479 | -0.004578 | 123.0331 | 122.8729 | 122.8638 | -0.27924 | 122.9507 | 122.937 | 122.9187 | -0.25177
2271.7031 | 122.9416 | -122.7539 | 0.19684 | 0.1062 | 0.021896 | 0.006366 | 0.0027685 | -0.0077566 | -0.0018436 | -0.0043793 | 0.17067 | -0.010846 | -0.0056118 | -0.0011216 | 0.0036807 | -0.01358 | 0.16479 | 0.16937 | 0.13733 | 0.10986 | 0.22888 | 0.036621 | -0.11902 | 0.1831 | 0.1831 | 0.09613 | 0.1831 | 0.15564 | -0.045776 | -0.10529 | 122.7905 | 122.6349 | 0.032044 | 122.9233 | 122.8638 | 0.22888 | -0.032043 | 122.7081 | 122.6486 | -0.013733 | 122.937 | 122.85 | 0.20142 | -0.041198 | 122.9828 | 122.9187 | 122.8912 | -0.31586 | 122.937 | 122.9095 | 122.937 | -0.30212
2273.4531 | 122.9691 | -122.7631 | 0.19226 | 0.083313 | 0.028305 | 0.0044434 | 0.0023413 | -0.0066884 | 0.0026424 | -0.0033111 | 0.03334 | -0.0095639 | -0.0036892 | -0.001976 | 0.0064577 | -0.014007 | 0.091553 | -0.009155 | -0.036621 | 0.036621 | 0.27008 | -0.009155 | -0.17395 | 0.050354 | 0.018311 | -0.064087 | 0.22888 | 0.16937 | -0.07782 | -0.15564 | 122.7539 | 122.5891 | 0.07782 | 122.7539 | 122.7997 | 0.21057 | -0.10071 | 122.6852 | 122.6074 | 0.036621 | 122.8134 | 122.699 | 0.091553 | -0.022888 | 123.0331 | 122.8546 | 122.7264 | -0.36621 | 122.9919 | 122.9324 | 122.7814 | -0.3479
2275.1406 | 123.0103 | -122.7539 | 0.18768 | 0.16724 | 0.025528 | 0.0057252 | 0.0029821 | -0.0077566 | -0.00098918 | -0.0054475 | 0.19356 | -0.0095639 | -0.008389 | -0.0013352 | 0.0062441 | -0.011657 | 0.15564 | 0.1236 | 0.10071 | 0.10529 | 0.20142 | 0.009155 | -0.14648 | 0.16022 | 0.16937 | 0.082397 | 0.13733 | 0.1236 | -0.068665 | -0.11444 | 122.7631 | 122.6074 | 0.013733 | 122.8775 | 122.8592 | 0.25177 | -0.032043 | 122.6852 | 122.6395 | -0.050354 | 122.9141 | 122.8363 | 0.19684 | -0.064087 | 122.9553 | 122.9095 | 122.8546 | -0.33417 | 122.8912 | 122.8775 | 122.9233 | -0.30212
2276.8906 | 123.0423 | -122.7173 | 0.14191 | -0.16846 | 0.02446 | 0.006366 | 0.0068273 | -0.0054068 | -0.0041934 | -0.0075837 | -0.13451 | -0.010418 | -0.0068936 | -0.0026168 | 0.0015445 | -0.015075 | 0.25635 | 0.26093 | 0.2243 | 0.21973 | 0.32501 | 0.11902 | -0.032043 | 0.23804 | 0.28381 | 0.16937 | 0.25635 | 0.24261 | 0.027466 | -0.036621 | 122.8363 | 122.6852 | 0.18311 | 122.9782 | 122.937 | 0.25177 | 0.11444 | 122.7448 | 122.6807 | 0.11444 | 122.9553 | 122.8867 | 0.20599 | 0.10071 | 123.0423 | 122.9736 | 122.9416 | -0.17395 | 122.9736 | 122.9599 | 123.0011 | -0.17853
2278.6562 | 123.0972 | -122.7173 | 0.14191 | -0.099793 | 0.02446 | 0.0070068 | 0.0076819 | -0.0088248 | -0.0039798 | -0.0077973 | -0.042954 | -0.0117 | -0.0024076 | -0.0024032 | -0.0012327 | -0.012512 | 0.21515 | 0.24719 | 0.23346 | 0.20599 | 0.32959 | 0.11902 | -0.041199 | 0.26093 | 0.27924 | 0.18768 | 0.25177 | 0.21057 | 0.027466 | -0.027466 | 122.8363 | 122.6761 | 0.18768 | 122.9645 | 122.9233 | 0.24719 | 0.073242 | 122.7448 | 122.6898 | 0.10986 | 122.9782 | 122.905 | 0.21515 | 0.068664 | 123.0469 | 122.9324 | 122.9507 | -0.18311 | 122.9691 | 122.9279 | 122.9965 | -0.16937
2280.3438 | 123.0789 | -122.7127 | 0.14648 | -0.14557 | 0.023392 | 0.0038024 | 0.0087499 | -0.0081838 | -0.002698 | -0.0082245 | -0.16502 | -0.012982 | -0.0036892 | -0.0013352 | 0.0021853 | -0.013794 | 0.25177 | 0.3067 | 0.24719 | 0.23804 | 0.32501 | 0.12817 | -0.013733 | 0.27008 | 0.31586 | 0.20142 | 0.2655 | 0.2243 | 0.036621 | -0.022888 | 122.8409 | 122.699 | 0.17853 | 123.0194 | 122.9507 | 0.25177 | 0.10529 | 122.7493 | 122.6898 | 0.11902 | 122.9828 | 122.9141 | 0.2243 | 0.07782 | 123.0377 | 122.9645 | 122.9599 | -0.16022 | 122.9782 | 122.937 | 123.0286 | -0.16937
2282.0312 | 123.0515 | -122.7356 | 0.16022 | -0.22186 | 0.026169 | 0.0042298 | 0.0078955 | -0.0069022 | -0.00013458 | -0.0060883 | -0.27184 | -0.01405 | -0.0028348 | -0.0013352 | 0.0030399 | -0.014435 | 0.23804 | 0.2655 | 0.20142 | 0.2243 | 0.33417 | 0.10986 | -0.027466 | 0.20142 | 0.23804 | 0.11444 | 0.3067 | 0.23346 | 0.004578 | -0.032043 | 122.8455 | 122.7081 | 0.17395 | 123.0011 | 122.9599 | 0.25177 | 0.07782 | 122.7402 | 122.7036 | 0.14648 | 122.937 | 122.85 | 0.14648 | 0.073242 | 123.0698 | 122.9736 | 122.937 | -0.18768 | 123.0423 | 122.9691 | 122.9736 | -0.19226
2283.7656 | 122.9782 | -122.7722 | 0.17853 | -0.046387 | 0.025742 | 0.0023072 | 0.0038367 | -0.0079702 | 0.0028562 | -0.0043793 | -0.11162 | -0.0070003 | -0.003262 | -0.00048061 | 0.0073123 | -0.016571 | 0.14648 | 0.12817 | 0.054932 | 0.091553 | 0.29755 | 0.032043 | -0.1236 | 0.10071 | 0.064087 | -0.036621 | 0.22888 | 0.16937 | -0.091553 | -0.12817 | 122.8043 | 122.6486 | 0.11902 | 122.9004 | 122.8638 | 0.21515 | -0.032044 | 122.6807 | 122.644 | 0.050354 | 122.8729 | 122.7356 | 0.091553 | -0.009155 | 123.0698 | 122.9187 | 122.8271 | -0.30212 | 123.0011 | 122.9416 | 122.8363 | -0.3067
2285.5312 | 123.0972 | -122.7127 | 0.15564 | -0.16846 | 0.026596 | 0.004657 | 0.0055457 | -0.0066884 | 0.0022152 | -0.0065155 | -0.2108 | -0.0084957 | -0.0075344 | -5.3406e-05 | 0.0068851 | -0.011657 | 0.15106 | 0.13733 | 0.068665 | 0.13275 | 0.33417 | 0.059509 | -0.10071 | 0.14191 | 0.16022 | 0.036621 | 0.24719 | 0.2243 | -0.036621 | -0.10529 | 122.7722 | 122.612 | 0.17853 | 122.85 | 122.8455 | 0.23346 | -0.004578 | 122.6761 | 122.6074 | 0.091552 | 122.8546 | 122.7493 | 0.14191 | 0.068664 | 123.0469 | 122.8638 | 122.7814 | -0.25635 | 122.9599 | 122.937 | 122.8729 | -0.26093
2287.2188 | 123.0743 | -122.7768 | 0.14648 | -0.22186 | 0.02446 | 0.006366 | 0.0087499 | -0.0073294 | -0.0020572 | -0.0052337 | -0.25658 | -0.0093503 | -0.0047574 | 0.0016556 | 0.0045351 | -0.011017 | 0.14191 | 0.17395 | 0.10529 | 0.16937 | 0.39825 | 0.09613 | -0.059509 | 0.12817 | 0.16022 | 0.050354 | 0.31586 | 0.27466 | -0.004578 | -0.054932 | 122.8729 | 122.7173 | 0.25177 | 122.9507 | 122.9462 | 0.22888 | -0.004577 | 122.7722 | 122.7219 | 0.16937 | 122.905 | 122.8271 | 0.10529 | 0.12817 | 123.175 | 122.9187 | 122.8821 | -0.20599 | 123.0927 | 123.0515 | 122.937 | -0.20142
2288.9688 | 123.0789 | -122.731 | 0.16937 | -0.19135 | 0.028092 | 0.004657 | 0.0098181 | -0.0073294 | -0.0018436 | -0.0063019 | -0.22606 | -0.010632 | -0.003262 | -0.0024032 | 0.0023989 | -0.01358 | 0.1236 | 0.17395 | 0.10986 | 0.16479 | 0.39368 | 0.091553 | -0.068665 | 0.14191 | 0.17853 | 0.064087 | 0.31128 | 0.26093 | 0.004578 | -0.068665 | 122.8226 | 122.6624 | 0.2243 | 122.905 | 122.8958 | 0.23346 | -0.045777 | 122.7356 | 122.6624 | 0.14191 | 122.8729 | 122.7951 | 0.13275 | 0.091552 | 123.1247 | 122.8546 | 122.8409 | -0.23804 | 123.0423 | 122.9919 | 122.9095 | -0.23804
2290.7188 | 123.0286 | -122.7356 | 0.1831 | -0.069275 | 0.028305 | 0.0048706 | 0.0042639 | -0.0043386 | 0.003497 | -0.0073701 | -0.10399 | -0.0093503 | -0.0064664 | 0.00037379 | 0.0079531 | -0.014007 | 0.15564 | 0.14648 | 0.064087 | 0.11902 | 0.29755 | 0.032043 | -0.11902 | 0.1236 | 0.12817 | 0.018311 | 0.23346 | 0.19226 | -0.050354 | -0.09613 | 122.7676 | 122.6166 | 0.11444 | 122.8821 | 122.8546 | 0.23804 | -0.027465 | 122.6852 | 122.6395 | 0.050354 | 122.8592 | 122.7539 | 0.11444 | 0.009156 | 123.0331 | 122.8912 | 122.7997 | -0.30212 | 122.9691 | 122.9279 | 122.8638 | -0.27924
2292.4062 | 122.9828 | -122.7768 | 0.19226 | 0.17487 | 0.025101 | 0.0055114 | 0.0027685 | -0.005834 | -0.00098918 | -0.0045929 | 0.20882 | -0.011273 | -0.0075344 | -0.0015488 | 0.0066715 | -0.012298 | 0.11444 | 0.14191 | 0.10071 | 0.10529 | 0.21057 | 0.004578 | -0.15564 | 0.16479 | 0.17395 | 0.07782 | 0.17395 | 0.11444 | -0.054932 | -0.11902 | 122.7814 | 122.6212 | 0.01831 | 122.9187 | 122.8821 | 0.26093 | -0.07782 | 122.7219 | 122.6578 | -0.018311 | 122.9416 | 122.8546 | 0.19684 | -0.07782 | 122.9874 | 122.8912 | 122.8775 | -0.3479 | 122.9507 | 122.8912 | 122.9507 | -0.31128
2294.1562 | 123.0423 | -122.7493 | 0.17853 | -0.24475 | 0.025314 | 0.0061524 | 0.0083227 | -0.0051932 | 0.00029262 | -0.0086517 | -0.19554 | -0.0097775 | -0.0045438 | -0.00026701 | 0.0032535 | -0.012726 | 0.17395 | 0.16022 | 0.1236 | 0.15564 | 0.37079 | 0.11444 | -0.045776 | 0.1236 | 0.16022 | 0.068665 | 0.30212 | 0.27008 | -0.004578 | -0.059509 | 122.8638 | 122.7036 | 0.19226 | 122.9095 | 122.905 | 0.20142 | -0.004578 | 122.7448 | 122.6898 | 0.1236 | 122.8729 | 122.818 | 0.12817 | 0.091553 | 123.1201 | 122.9233 | 122.8729 | -0.2243 | 123.0515 | 123.0194 | 122.9095 | -0.23804
2295.9219 | 122.9645 | -122.7676 | 0.1831 | -0.038757 | 0.027023 | 0.0014526 | 0.0074683 | -0.0064748 | 0.0049924 | -0.0050201 | -0.020065 | -0.0074277 | -0.0064664 | 0.00016019 | 0.0056033 | -0.012085 | 0.11444 | 0.064087 | 0.018311 | 0.07782 | 0.28839 | 0.013733 | -0.14191 | 0.059509 | 0.064087 | -0.050354 | 0.21515 | 0.16479 | -0.086975 | -0.14191 | 122.7814 | 122.6257 | 0.10529 | 122.8317 | 122.8455 | 0.21973 | -0.068664 | 122.6807 | 122.6257 | 0.032044 | 122.8271 | 122.7173 | 0.091553 | -0.01831 | 123.056 | 122.8821 | 122.7859 | -0.32501 | 122.9828 | 122.9324 | 122.8317 | -0.32501
2297.6719 | 123.0286 | -122.7493 | 0.16479 | -0.27527 | 0.025101 | 0.0052978 | 0.010245 | -0.0062612 | -0.0046206 | -0.0067291 | -0.19554 | -0.011914 | -0.0053982 | -0.0021896 | 0.0015445 | -0.011657 | 0.1831 | 0.21973 | 0.1831 | 0.19226 | 0.36621 | 0.10071 | -0.041199 | 0.15106 | 0.20142 | 0.082397 | 0.31586 | 0.27008 | 0.013733 | -0.059509 | 122.85 | 122.7081 | 0.20142 | 122.9691 | 122.9416 | 0.23346 | 0.01831 | 122.7631 | 122.6898 | 0.15106 | 122.9004 | 122.8317 | 0.14191 | 0.10529 | 123.1155 | 122.9324 | 122.9324 | -0.20599 | 123.0652 | 123.0194 | 122.9507 | -0.2243
2299.375 | 123.0606 | -122.7036 | 0.16022 | -0.18372 | 0.025101 | 0.0048706 | 0.0076819 | -0.0077566 | -0.0029118 | -0.0060883 | -0.25658 | -0.0074277 | -0.004971 | 0.00016019 | 0.0034671 | -0.012512 | 0.14191 | 0.17395 | 0.10986 | 0.15564 | 0.36163 | 0.10986 | -0.041199 | 0.12817 | 0.15564 | 0.064087 | 0.3067 | 0.28839 | -0.004578 | -0.050354 | 122.8134 | 122.6624 | 0.20142 | 122.8775 | 122.8592 | 0.19684 | -0.01831 | 122.699 | 122.6532 | 0.14648 | 122.8317 | 122.7676 | 0.11444 | 0.12817 | 123.0652 | 122.8455 | 122.8134 | -0.20142 | 123.0103 | 122.9919 | 122.8592 | -0.21057
2301.1406 | 123.0148 | -122.7402 | 0.15564 | -0.0082397 | 0.025955 | 0.0085022 | 0.0051183 | -0.0096792 | -0.006757 | -0.0090791 | 0.071487 | -0.011914 | -0.0045438 | -0.00069421 | 0.0036807 | -0.012512 | 0.10529 | 0.16937 | 0.13275 | 0.13275 | 0.29755 | 0.068665 | -0.07782 | 0.15564 | 0.19684 | 0.13275 | 0.23346 | 0.21515 | 0.004578 | -0.07782 | 122.8088 | 122.6624 | 0.14191 | 122.9095 | 122.8729 | 0.21057 | -0.050354 | 122.7448 | 122.6624 | 0.077819 | 122.8958 | 122.8729 | 0.21057 | 0.059509 | 123.0377 | 122.8455 | 122.8729 | -0.23346 | 122.9736 | 122.9553 | 122.937 | -0.23346
2302.8906 | 122.9599 | -122.7631 | 0.19226 | 0.083313 | 0.021256 | 0.0038024 | 0.0012731 | -0.0071158 | -0.0054752 | -0.0071563 | 0.102 | -0.0117 | -0.0064664 | -0.0011216 | 0.0036807 | -0.012939 | 0.13275 | 0.17395 | 0.11902 | 0.1236 | 0.25635 | 0.059509 | -0.09613 | 0.17853 | 0.17853 | 0.11444 | 0.2243 | 0.17853 | -0.004578 | -0.054932 | 122.8226 | 122.6669 | 0.064087 | 122.937 | 122.8867 | 0.21973 | -0.05951 | 122.7585 | 122.7081 | 0.032043 | 122.9416 | 122.8775 | 0.16937 | -0.013733 | 123.0194 | 122.8958 | 122.8821 | -0.28839 | 122.9874 | 122.9416 | 122.9416 | -0.24719
2304.5781 | 122.9828 | -122.7585 | 0.18768 | 0.037537 | 0.021256 | 0.0040162 | 0.0031957 | -0.0056204 | -0.0039798 | -0.0092927 | 0.079117 | -0.010632 | -0.0068936 | -0.0017624 | 0.0021853 | -0.012298 | 0.15564 | 0.16937 | 0.12817 | 0.14648 | 0.29755 | 0.07782 | -0.068665 | 0.16937 | 0.16479 | 0.11902 | 0.24261 | 0.18768 | 0 | -0.068665 | 122.8363 | 122.6898 | 0.10986 | 122.9279 | 122.905 | 0.21515 | -0.032043 | 122.7585 | 122.6898 | 0.054932 | 122.9279 | 122.8775 | 0.18768 | 0 | 123.056 | 122.9141 | 122.8867 | -0.25635 | 123.0011 | 122.9462 | 122.9233 | -0.25635
2306.2812 | 123.1155 | -122.7356 | 0.16937 | -0.16846 | 0.026169 | 0.0020936 | 0.0055457 | -0.0034842 | 0.00050622 | -0.0063019 | -0.25658 | -0.010846 | -0.0064664 | -0.00048061 | 0.0053897 | -0.015289 | 0.17853 | 0.11902 | 0.091553 | 0.14648 | 0.36621 | 0.086975 | -0.073242 | 0.13275 | 0.16022 | 0.041199 | 0.32501 | 0.25177 | -0.036621 | -0.07782 | 122.8226 | 122.6624 | 0.19684 | 122.8546 | 122.8821 | 0.21973 | 0.009155 | 122.699 | 122.6578 | 0.15564 | 122.8683 | 122.7768 | 0.11902 | 0.082397 | 123.1018 | 122.9141 | 122.8271 | -0.24261 | 123.0606 | 122.9874 | 122.8958 | -0.24719
2308.0469 | 122.9691 | -122.7768 | 0.19684 | 0.029907 | 0.028732 | 0.0033752 | 0.0049047 | -0.0062612 | 0.0026424 | -0.0050201 | -0.027695 | -0.0093503 | -0.0041164 | -0.00026701 | 0.0075259 | -0.012726 | 0.10071 | 0.059509 | 0.013733 | 0.059509 | 0.29755 | 0.027466 | -0.16022 | 0.064087 | 0.041199 | -0.073242 | 0.21057 | 0.15106 | -0.10986 | -0.1236 | 122.8043 | 122.6166 | 0.10071 | 122.8363 | 122.8363 | 0.21973 | -0.09613 | 122.6669 | 122.6532 | 0.013733 | 122.8409 | 122.7036 | 0.050354 | -0.045776 | 123.0743 | 122.8775 | 122.7905 | -0.35706 | 122.9874 | 122.9279 | 122.818 | -0.32043
2309.7344 | 123.0652 | -122.7402 | 0.17853 | -0.084534 | 0.027451 | 0.0038024 | 0.0049047 | -0.005834 | 0.0020016 | -0.0056611 | -0.10399 | -0.0084957 | -0.0047574 | 0.00037379 | 0.0053897 | -0.012726 | 0.14648 | 0.15564 | 0.09613 | 0.1236 | 0.3067 | 0.050354 | -0.11902 | 0.14648 | 0.16022 | 0.022888 | 0.23346 | 0.1831 | -0.041199 | -0.10071 | 122.7905 | 122.6212 | 0.12817 | 122.8958 | 122.8638 | 0.24261 | -0.032044 | 122.699 | 122.6395 | 0.054931 | 122.8867 | 122.7631 | 0.1236 | 0.004577 | 123.0469 | 122.8867 | 122.8363 | -0.29755 | 122.9736 | 122.9233 | 122.9004 | -0.27924
2311.4531 | 122.9691 | -122.7631 | 0.19684 | 0.12909 | 0.024246 | 0.0067932 | 0.0059729 | -0.0069022 | -0.0035526 | -0.0048065 | 0.14015 | -0.010632 | -0.00668 | -0.0017624 | 0.0043215 | -0.010589 | 0.11444 | 0.16937 | 0.1236 | 0.10986 | 0.21057 | 0.027466 | -0.12817 | 0.17853 | 0.1831 | 0.086975 | 0.1831 | 0.15106 | -0.050354 | -0.10529 | 122.7905 | 122.6349 | 0.013733 | 122.9324 | 122.8729 | 0.23804 | -0.082397 | 122.7127 | 122.6578 | -0.013733 | 122.9416 | 122.85 | 0.19226 | -0.045776 | 122.9736 | 122.8775 | 122.8867 | -0.32501 | 122.9462 | 122.9141 | 122.9462 | -0.30212
2313.2031 | 122.9462 | -122.7859 | 0.19226 | 0.12909 | 0.023392 | 0.0052978 | 0.0049047 | -0.0079702 | -0.002698 | -0.0043793 | 0.14778 | -0.011914 | -0.0073208 | -0.0011216 | 0.0030399 | -0.012298 | 0.11902 | 0.17853 | 0.1236 | 0.10529 | 0.21057 | 0.032043 | -0.1236 | 0.17395 | 0.16937 | 0.091553 | 0.1831 | 0.14191 | -0.036621 | -0.10071 | 122.818 | 122.6624 | 0.01831 | 122.9645 | 122.8912 | 0.22888 | -0.073242 | 122.7493 | 122.6852 | -0.009156 | 122.9599 | 122.8775 | 0.19226 | -0.050354 | 122.9965 | 122.905 | 122.9095 | -0.31586 | 122.9691 | 122.9279 | 122.9553 | -0.29297
2314.9688 | 123.0927 | -122.7173 | 0.14648 | -0.069275 | 0.025528 | 0.0048706 | 0.0061865 | -0.0062612 | -0.0056888 | -0.0082245 | -0.10399 | -0.012341 | -0.0058254 | -0.003685 | -0.00080527 | -0.012298 | 0.2243 | 0.23346 | 0.19684 | 0.21057 | 0.32501 | 0.10071 | -0.054932 | 0.27008 | 0.29297 | 0.21973 | 0.25635 | 0.2243 | 0.036621 | -0.022888 | 122.818 | 122.6624 | 0.17853 | 122.9507 | 122.9279 | 0.2655 | 0.07782 | 122.7539 | 122.6944 | 0.10986 | 122.9874 | 122.937 | 0.24261 | 0.07782 | 123.0423 | 122.9416 | 122.9141 | -0.20142 | 122.9736 | 122.9416 | 123.0103 | -0.16937
2316.7344 | 123.024 | -122.7356 | 0.17853 | 0.17487 | 0.026383 | 0.0048706 | 0.0044775 | -0.0090384 | 0.0024288 | -0.0052337 | 0.1783 | -0.0093503 | -0.00668 | 0.00037379 | 0.0062441 | -0.014007 | 0.07782 | 0.045776 | 0.018311 | 0.041199 | 0.25177 | -0.009155 | -0.15564 | 0.14191 | 0.1236 | 0.027466 | 0.16479 | 0.14191 | -0.064087 | -0.13275 | 122.7264 | 122.58 | 0.073242 | 122.7814 | 122.7768 | 0.19684 | -0.10071 | 122.6715 | 122.6028 | -0.013733 | 122.8775 | 122.7631 | 0.16022 | -0.036621 | 122.9874 | 122.8134 | 122.7539 | -0.33417 | 122.9004 | 122.8775 | 122.8592 | -0.31128
2318.4375 | 123.0743 | -122.7402 | 0.14191 | -0.0082397 | 0.025742 | 0.0050842 | 0.0078955 | -0.0051932 | -0.0054752 | -0.0058747 | 0.03334 | -0.010632 | -0.0064664 | -0.0015488 | 0.00026273 | -0.012726 | 0.15106 | 0.16937 | 0.15106 | 0.15564 | 0.3067 | 0.082397 | -0.07782 | 0.21515 | 0.25177 | 0.16937 | 0.24261 | 0.21973 | 0.013733 | -0.054932 | 122.8226 | 122.6624 | 0.16479 | 122.9095 | 122.8958 | 0.23346 | 0.009155 | 122.7539 | 122.6852 | 0.10071 | 122.9553 | 122.9095 | 0.22431 | 0.07782 | 123.0469 | 122.8912 | 122.8912 | -0.21973 | 122.9828 | 122.9599 | 122.9919 | -0.19684
2320.2031 | 123.0331 | -122.7402 | 0.16937 | 0.045166 | 0.02446 | 0.0065796 | 0.0059729 | -0.0069022 | -0.0048344 | -0.0090791 | 0.025711 | -0.010205 | -0.0071072 | -0.0028306 | 0.0015445 | -0.011017 | 0.15106 | 0.14191 | 0.13275 | 0.15106 | 0.3067 | 0.068665 | -0.068665 | 0.19226 | 0.20142 | 0.1236 | 0.24719 | 0.22888 | -0.022888 | -0.068665 | 122.8088 | 122.6715 | 0.13733 | 122.8821 | 122.8912 | 0.21973 | -0.018311 | 122.7173 | 122.6715 | 0.077819 | 122.9324 | 122.8638 | 0.19226 | 0.059509 | 123.0469 | 122.8912 | 122.8729 | -0.23804 | 122.9874 | 122.9691 | 122.9416 | -0.23804
2321.8906 | 122.9599 | -122.7905 | 0.19684 | 0.13672 | 0.021469 | 0.0055114 | 0.0021277 | -0.0054068 | -0.0020572 | -0.0063019 | 0.12489 | -0.0089229 | -0.0079618 | -0.00069421 | 0.0034671 | -0.015503 | 0.19684 | 0.13733 | 0.11902 | 0.11444 | 0.21057 | 0.027466 | -0.13275 | 0.20142 | 0.17853 | 0.082397 | 0.1831 | 0.15564 | -0.050354 | -0.09613 | 122.818 | 122.6578 | 0.013733 | 122.9279 | 122.905 | 0.24719 | 0 | 122.7402 | 122.6944 | -0.013733 | 122.9919 | 122.8729 | 0.17853 | -0.041198 | 123.0011 | 122.9874 | 122.9095 | -0.32959 | 122.9736 | 122.9462 | 122.9691 | -0.29297
2323.6406 | 123.0194 | -122.7631 | 0.20599 | 0.12146 | 0.025955 | 0.0042298 | 0.0036231 | -0.0062612 | 0.0024288 | -0.0069427 | 0.0028229 | -0.011914 | -0.0073208 | -0.0011216 | 0.0070987 | -0.014862 | 0.086975 | 0 | -0.036621 | 0.027466 | 0.26093 | -0.013733 | -0.18768 | 0.086975 | 0.036621 | -0.045776 | 0.2243 | 0.17853 | -0.09613 | -0.14648 | 122.7493 | 122.5754 | 0.054931 | 122.7631 | 122.7905 | 0.21515 | -0.11902 | 122.6669 | 122.6166 | 0.01831 | 122.85 | 122.7173 | 0.10071 | -0.027466 | 123.024 | 122.85 | 122.7264 | -0.39368 | 122.9874 | 122.9416 | 122.7997 | -0.35248
2325.3906 | 123.0881 | -122.7539 | 0.16479 | -0.084534 | 0.025101 | 0.0044434 | 0.0042639 | -0.0079702 | 0.0037106 | -0.0030975 | -0.18028 | -0.010846 | -0.004971 | -0.00069421 | 0.0058169 | -0.012726 | 0.17395 | 0.1236 | 0.07782 | 0.1236 | 0.29755 | 0.027466 | -0.11902 | 0.16479 | 0.15564 | 0.022888 | 0.21057 | 0.20142 | -0.064087 | -0.10529 | 122.7814 | 122.6349 | 0.13275 | 122.8775 | 122.8775 | 0.24261 | 0.009155 | 122.6898 | 122.6486 | 0.045776 | 122.9187 | 122.7768 | 0.12817 | 0.036621 | 123.0515 | 122.9279 | 122.8317 | -0.28381 | 122.9645 | 122.9553 | 122.9095 | -0.27008
2327.0781 | 123.0423 | -122.7264 | 0.16022 | -0.18372 | 0.024033 | 0.0035888 | 0.010032 | -0.0081838 | -0.0046206 | -0.0075837 | -0.14977 | -0.0117 | -0.003262 | -0.0011216 | 0.0023989 | -0.012512 | 0.2243 | 0.27008 | 0.23346 | 0.23346 | 0.32501 | 0.11902 | -0.054932 | 0.23804 | 0.27924 | 0.17853 | 0.25635 | 0.23346 | 0.022888 | -0.041199 | 122.8455 | 122.6715 | 0.1648 | 122.9965 | 122.9599 | 0.28839 | 0.064087 | 122.7493 | 122.6852 | 0.096131 | 122.9645 | 122.905 | 0.21973 | 0.073242 | 123.0515 | 122.9507 | 122.9599 | -0.21515 | 122.9828 | 122.9599 | 123.0057 | -0.20142
2328.8438 | 123.1201 | -122.7493 | 0.16479 | -0.19135 | 0.027237 | 0.0038024 | 0.0042639 | -0.007543 | 7.902e-05 | -0.0050201 | -0.24132 | -0.0063595 | -0.004971 | 0.00058739 | 0.0051761 | -0.015716 | 0.17395 | 0.14191 | 0.086975 | 0.14191 | 0.36163 | 0.082397 | -0.091553 | 0.13275 | 0.16479 | 0.036621 | 0.26093 | 0.21973 | -0.045776 | -0.09613 | 122.8317 | 122.6578 | 0.19684 | 122.8912 | 122.8912 | 0.23346 | 0.009155 | 122.7036 | 122.6532 | 0.09613 | 122.8821 | 122.7859 | 0.13275 | 0.054932 | 123.111 | 122.9233 | 122.8363 | -0.25635 | 123.0103 | 122.9691 | 122.9141 | -0.26092
2330.5469 | 122.9736 | -122.7768 | 0.18768 | -0.0082397 | 0.026383 | 0.0035888 | 0.0055457 | -0.007543 | 0.0026424 | -0.0052337 | 0.010452 | -0.0078549 | -0.0047574 | -0.00090781 | 0.0070987 | -0.013366 | 0.082397 | 0.050354 | 0.022888 | 0.059509 | 0.27008 | 0 | -0.16022 | 0.050354 | 0.045776 | -0.054932 | 0.21515 | 0.17853 | -0.10529 | -0.15564 | 122.7768 | 122.6166 | 0.082398 | 122.8271 | 122.8363 | 0.21973 | -0.10529 | 122.6715 | 122.6212 | 0.027466 | 122.8271 | 122.7219 | 0.10071 | -0.009155 | 123.0469 | 122.8592 | 122.7997 | -0.3479 | 122.9919 | 122.9553 | 122.8226 | -0.34332
2332.2344 | 123.0057 | -122.7631 | 0.18768 | 0.12146 | 0.025955 | 0.0044434 | 0.0040503 | -0.0079702 | 0.0013608 | -0.0028839 | 0.086746 | -0.0082821 | -0.0071072 | -0.0017624 | 0.0068851 | -0.011871 | 0.022888 | 0 | -0.027466 | 0.018311 | 0.24719 | -0.032043 | -0.17395 | 0.050354 | 0.050354 | -0.041199 | 0.20142 | 0.18768 | -0.09613 | -0.14648 | 122.731 | 122.5891 | 0.059509 | 122.7631 | 122.7814 | 0.19226 | -0.16479 | 122.6669 | 122.6166 | 0.013733 | 122.8134 | 122.7219 | 0.10529 | 0 | 123.0103 | 122.7859 | 122.7356 | -0.36163 | 122.9645 | 122.9507 | 122.8134 | -0.33417
2333.9844 | 123.0606 | -122.7402 | 0.16937 | -0.092163 | 0.029373 | 0.0031616 | 0.0055457 | -0.0081838 | 0.00029262 | -0.0058747 | -0.14214 | -0.0072141 | -0.0043302 | 0.00080099 | 0.0047489 | -0.013366 | 0.16479 | 0.1236 | 0.07782 | 0.11902 | 0.30212 | 0.027466 | -0.1236 | 0.12817 | 0.16937 | 0.022888 | 0.21515 | 0.20142 | -0.050354 | -0.11902 | 122.7676 | 122.6166 | 0.13275 | 122.8638 | 122.8592 | 0.24261 | -0.004578 | 122.6898 | 122.6212 | 0.045776 | 122.8683 | 122.7631 | 0.14191 | 0.032043 | 123.0423 | 122.905 | 122.818 | -0.29297 | 122.9553 | 122.9416 | 122.9095 | -0.28839
2335.7344 | 123.0148 | -122.7768 | 0.17395 | 0.12146 | 0.027451 | 0.0044434 | 0.0057593 | -0.0051932 | 0.00029262 | -0.0050201 | 0.086746 | -0.0076413 | -0.004971 | 0.00037379 | 0.0045351 | -0.010803 | 0.018311 | -0.013733 | -0.045776 | 0.036621 | 0.25177 | -0.041199 | -0.17395 | 0.068665 | 0.041199 | -0.022888 | 0.21057 | 0.16479 | -0.09613 | -0.15564 | 122.7356 | 122.6028 | 0.07782 | 122.7631 | 122.8134 | 0.21057 | -0.15564 | 122.6807 | 122.6212 | 0.036621 | 122.8455 | 122.7539 | 0.13275 | -0.009155 | 123.0286 | 122.7951 | 122.731 | -0.3479 | 122.9874 | 122.9416 | 122.818 | -0.32959
2337.4844 | 123.056 | -122.7539 | 0.16022 | -0.24475 | 0.025742 | 0.0044434 | 0.010245 | -0.0083974 | -0.0039798 | -0.0084381 | -0.19554 | -0.0087093 | -0.0028348 | -0.0017624 | 0.0034671 | -0.011017 | 0.13733 | 0.17853 | 0.13733 | 0.16937 | 0.37537 | 0.10986 | -0.050354 | 0.12817 | 0.1831 | 0.07782 | 0.31128 | 0.2655 | -0.009155 | -0.050354 | 122.8638 | 122.7036 | 0.21515 | 122.9324 | 122.9233 | 0.21973 | -0.022888 | 122.7448 | 122.7036 | 0.15106 | 122.8821 | 122.8317 | 0.12817 | 0.10529 | 123.1293 | 122.8912 | 122.8912 | -0.21057 | 123.0652 | 123.0194 | 122.937 | -0.21057
2339.1719 | 123.1018 | -122.7036 | 0.14648 | -0.069275 | 0.025528 | 0.0055114 | 0.0070409 | -0.0083974 | -0.0088932 | -0.0075837 | -0.042954 | -0.013196 | -0.0047574 | -0.0034714 | 0.0011173 | -0.010803 | 0.17395 | 0.22888 | 0.20599 | 0.20142 | 0.31586 | 0.10529 | -0.050354 | 0.23804 | 0.31586 | 0.21057 | 0.25177 | 0.22888 | 0.018311 | -0.036621 | 122.8088 | 122.6532 | 0.16937 | 122.9324 | 122.905 | 0.25177 | 0.027466 | 122.7219 | 122.6669 | 0.10529 | 122.9416 | 122.9141 | 0.24719 | 0.082398 | 123.0194 | 122.8775 | 122.9095 | -0.19684 | 122.9553 | 122.9324 | 123.0194 | -0.18311
2340.9375 | 123.0881 | -122.731 | 0.15564 | -0.24475 | 0.025955 | 0.0055114 | 0.0085363 | -0.0081838 | -0.00077538 | -0.0063019 | -0.25658 | -0.0076413 | -0.006039 | -0.00069421 | 0.0056033 | -0.012512 | 0.17853 | 0.14648 | 0.11444 | 0.16022 | 0.39368 | 0.10986 | -0.064087 | 0.1236 | 0.14648 | 0.041199 | 0.3067 | 0.27466 | -0.022888 | -0.064087 | 122.8409 | 122.6669 | 0.23804 | 122.8775 | 122.8912 | 0.2243 | 0.022888 | 122.7081 | 122.6669 | 0.15106 | 122.8546 | 122.7722 | 0.10529 | 0.11902 | 123.1247 | 122.9095 | 122.8455 | -0.21973 | 123.0377 | 123.0057 | 122.8775 | -0.21973
2342.6406 | 123.0881 | -122.7219 | 0.13733 | -0.10742 | 0.022537 | 0.0065796 | 0.0064001 | -0.0079702 | -0.0035526 | -0.0063019 | -0.058212 | -0.012341 | -0.0051846 | -0.0028306 | 4.9132e-05 | -0.01358 | 0.2243 | 0.26093 | 0.23804 | 0.21973 | 0.32959 | 0.10529 | -0.050354 | 0.27008 | 0.30212 | 0.20142 | 0.25177 | 0.2243 | 0.027466 | -0.032043 | 122.8271 | 122.6715 | 0.19226 | 122.9828 | 122.9416 | 0.27008 | 0.086975 | 122.7493 | 122.6898 | 0.11444 | 122.9919 | 122.9233 | 0.23346 | 0.086975 | 123.0515 | 122.9462 | 122.9599 | -0.18768 | 122.9736 | 122.9462 | 123.024 | -0.16937
2344.3281 | 123.0789 | -122.7356 | 0.15564 | -0.1532 | 0.025314 | 0.004657 | 0.0078955 | -0.0069022 | -0.0041934 | -0.0073701 | -0.14977 | -0.012341 | -0.0056118 | -0.00048061 | 0.00068993 | -0.014007 | 0.24261 | 0.29755 | 0.25177 | 0.23804 | 0.32044 | 0.1236 | -0.013733 | 0.2655 | 0.32044 | 0.21515 | 0.26093 | 0.24719 | 0.036621 | -0.018311 | 122.8592 | 122.7219 | 0.1648 | 123.0331 | 122.9736 | 0.25177 | 0.086975 | 122.7722 | 122.7173 | 0.10529 | 123.0011 | 122.9507 | 0.23346 | 0.091552 | 123.056 | 122.9782 | 122.9874 | -0.16937 | 122.9965 | 122.9828 | 123.056 | -0.17395
2346.0625 | 122.9645 | -122.7585 | 0.17853 | 0.1062 | 0.025528 | 0.0059388 | 0.0029821 | -0.0090384 | -0.002698 | -0.0058747 | 0.15541 | -0.011487 | -0.0081754 | 0.00080099 | 0.0034671 | -0.013794 | 0.16022 | 0.14648 | 0.1236 | 0.11444 | 0.23804 | 0.032043 | -0.11444 | 0.17395 | 0.17395 | 0.10529 | 0.17395 | 0.17395 | -0.041199 | -0.082397 | 122.7905 | 122.644 | 0.059509 | 122.905 | 122.8729 | 0.22888 | -0.018311 | 122.7173 | 122.6761 | -0.004578 | 122.9324 | 122.8638 | 0.18768 | -0.004578 | 122.9965 | 122.9187 | 122.8821 | -0.29297 | 122.9324 | 122.9324 | 122.9324 | -0.26092
2347.7969 | 123.0469 | -122.7493 | 0.16479 | 0.052795 | 0.024674 | 0.0040162 | 0.0061865 | -0.0066884 | -0.003339 | -0.0071563 | 0.048599 | -0.011487 | -0.0045438 | -0.0041122 | 0.0013309 | -0.013366 | 0.15564 | 0.13275 | 0.15106 | 0.13733 | 0.29297 | 0.086975 | -0.09613 | 0.1831 | 0.20142 | 0.13275 | 0.25177 | 0.20599 | 0 | -0.059509 | 122.8363 | 122.6532 | 0.12817 | 122.8821 | 122.8867 | 0.23346 | -0.009155 | 122.7493 | 122.6898 | 0.086975 | 122.9324 | 122.8821 | 0.19226 | 0.041199 | 123.0423 | 122.905 | 122.9004 | -0.26092 | 123.0011 | 122.9553 | 122.9507 | -0.2243
2349.5156 | 122.9782 | -122.7539 | 0.20142 | 0.045166 | 0.026383 | 0.0033752 | 0.0021277 | -0.0064748 | 0.0054196 | -0.0050201 | -0.0048066 | -0.0089229 | -0.0064664 | -0.00048061 | 0.0070987 | -0.016998 | 0.082397 | 0.009155 | -0.027466 | 0.036621 | 0.29297 | -0.022888 | -0.16022 | 0.059509 | 0.018311 | -0.07782 | 0.21973 | 0.16937 | -0.091553 | -0.15564 | 122.731 | 122.5937 | 0.091553 | 122.7631 | 122.7905 | 0.19684 | -0.11902 | 122.6624 | 122.5983 | 0.018311 | 122.8134 | 122.6761 | 0.07782 | -0.032043 | 123.0469 | 122.8363 | 122.7264 | -0.36163 | 122.9736 | 122.9233 | 122.7722 | -0.35706
2351.2188 | 122.9919 | -122.7631 | 0.18768 | 0.17487 | 0.024033 | 0.0040162 | 0.0012731 | -0.0064748 | -0.00163 | -0.0033111 | 0.18593 | -0.010205 | -0.0056118 | -0.00048061 | 0.0053897 | -0.014435 | 0.16022 | 0.13733 | 0.091553 | 0.10071 | 0.21973 | 0.013733 | -0.16479 | 0.16937 | 0.17395 | 0.064087 | 0.13733 | 0.12817 | -0.073242 | -0.10529 | 122.7768 | 122.5983 | 0.032044 | 122.9004 | 122.8638 | 0.2655 | -0.027466 | 122.6898 | 122.6578 | -0.050354 | 122.9324 | 122.8271 | 0.16937 | -0.059509 | 122.9828 | 122.9233 | 122.8546 | -0.35248 | 122.9004 | 122.8912 | 122.937 | -0.29297
2352.9531 | 123.0835 | -122.7539 | 0.17395 | -0.13031 | 0.030655 | 0.0042298 | 0.0072547 | -0.0088248 | 0.0043514 | -0.0052337 | -0.18028 | -0.0095639 | -0.0053982 | -0.0026168 | 0.0047489 | -0.014435 | 0.16022 | 0.14191 | 0.091553 | 0.13275 | 0.32044 | 0.050354 | -0.13275 | 0.15106 | 0.15106 | 0.027466 | 0.21515 | 0.21515 | -0.073242 | -0.091553 | 122.8043 | 122.6212 | 0.14649 | 122.8958 | 122.8867 | 0.2655 | -0.013733 | 122.6807 | 122.6624 | 0.041199 | 122.905 | 122.7814 | 0.11902 | 0.041199 | 123.0743 | 122.9141 | 122.8455 | -0.3067 | 122.9691 | 122.9691 | 122.905 | -0.2655
2354.6875 | 123.0652 | -122.7219 | 0.17853 | -0.19135 | 0.025955 | 0.006366 | 0.0085363 | -0.008611 | -0.0037662 | -0.0054475 | -0.11925 | -0.012555 | -0.0034756 | -0.0017624 | 0.0021853 | -0.010803 | 0.23346 | 0.3067 | 0.26093 | 0.25177 | 0.3479 | 0.1236 | -0.022888 | 0.23804 | 0.32959 | 0.19226 | 0.26093 | 0.25177 | 0.054932 | -0.013733 | 122.8455 | 122.699 | 0.16937 | 123.0286 | 122.9736 | 0.27466 | 0.054931 | 122.7768 | 122.7081 | 0.082397 | 122.9599 | 122.9141 | 0.20599 | 0.073242 | 123.0698 | 122.9553 | 122.9828 | -0.20142 | 122.9828 | 122.9736 | 123.0515 | -0.19226
2356.3906 | 123.056 | -122.7493 | 0.15564 | -0.2066 | 0.023819 | 0.006366 | 0.0091773 | -0.0081838 | -0.0039798 | -0.0075837 | -0.14977 | -0.011059 | -0.0056118 | -0.0021896 | 0.0017581 | -0.014221 | 0.23346 | 0.29297 | 0.25177 | 0.24261 | 0.35706 | 0.14191 | -0.018311 | 0.2655 | 0.32959 | 0.17853 | 0.24261 | 0.23346 | 0.027466 | -0.018311 | 122.8912 | 122.731 | 0.20142 | 123.0423 | 122.9919 | 0.26093 | 0.077819 | 122.7768 | 122.731 | 0.086975 | 123.0148 | 122.9279 | 0.19684 | 0.077819 | 123.1064 | 122.9828 | 123.0011 | -0.17395 | 122.9919 | 122.9828 | 123.0789 | -0.17395
2358.1562 | 123.0423 | -122.7081 | 0.17395 | -0.26764 | 0.023819 | 0.0057252 | 0.010673 | -0.007543 | -0.0020572 | -0.0080109 | -0.18791 | -0.0099911 | -0.0053982 | -0.0021896 | 0.0032535 | -0.014007 | 0.1831 | 0.21515 | 0.16479 | 0.1831 | 0.37079 | 0.10986 | -0.045776 | 0.15106 | 0.20142 | 0.082397 | 0.31128 | 0.25635 | -0.013733 | -0.059509 | 122.818 | 122.6624 | 0.19684 | 122.9233 | 122.8912 | 0.22888 | 0.009155 | 122.6944 | 122.6486 | 0.13733 | 122.8592 | 122.7905 | 0.14191 | 0.082398 | 123.0789 | 122.8912 | 122.8729 | -0.21973 | 123.0194 | 122.9645 | 122.9095 | -0.23346
2359.8438 | 123.0881 | -122.7402 | 0.14648 | -0.17609 | 0.028946 | 0.0042298 | 0.0078955 | -0.0083974 | 0.0013608 | -0.0039521 | -0.21843 | -0.010846 | -0.0051846 | -0.0011216 | 0.0051761 | -0.016784 | 0.15564 | 0.15106 | 0.10071 | 0.14191 | 0.3479 | 0.045776 | -0.10071 | 0.15106 | 0.16479 | 0.036621 | 0.23346 | 0.2243 | -0.045776 | -0.10529 | 122.7859 | 122.6395 | 0.20142 | 122.8912 | 122.8821 | 0.24262 | 0.009156 | 122.6944 | 122.6349 | 0.086975 | 122.8912 | 122.7768 | 0.14191 | 0.07782 | 123.0881 | 122.8958 | 122.8409 | -0.24719 | 122.9736 | 122.9645 | 122.905 | -0.25177
2361.5312 | 123.1018 | -122.731 | 0.13733 | -0.046387 | 0.025101 | 0.0059388 | 0.0044775 | -0.0066884 | -0.0046206 | -0.0069427 | -0.042954 | -0.011059 | -0.0045438 | -0.0034714 | 0.00026273 | -0.012939 | 0.16479 | 0.24719 | 0.20142 | 0.18768 | 0.32959 | 0.10986 | -0.068665 | 0.27008 | 0.29755 | 0.20599 | 0.2655 | 0.21057 | 0.018311 | -0.041199 | 122.8409 | 122.6624 | 0.19226 | 122.9782 | 122.9187 | 0.25635 | 0.027466 | 122.7493 | 122.6898 | 0.12817 | 123.0011 | 122.937 | 0.24719 | 0.073242 | 123.0606 | 122.8958 | 122.9324 | -0.20599 | 122.9965 | 122.9416 | 123.0286 | -0.17853
2363.2188 | 123.024 | -122.7493 | 0.17853 | -0.0082397 | 0.021256 | 0.0072204 | 0.0029821 | -0.0064748 | -0.0041934 | -0.0075837 | 0.079117 | -0.011914 | -0.0073208 | -0.0017624 | 0.0049625 | -0.01123 | 0.14191 | 0.17853 | 0.1236 | 0.13733 | 0.32501 | 0.07782 | -0.068665 | 0.17395 | 0.20599 | 0.1236 | 0.24261 | 0.21057 | -0.022888 | -0.059509 | 122.8271 | 122.6807 | 0.14648 | 122.9279 | 122.8867 | 0.20599 | -0.036621 | 122.7264 | 122.6898 | 0.064087 | 122.9233 | 122.8729 | 0.1831 | 0.032043 | 123.0743 | 122.8912 | 122.8729 | -0.24719 | 122.9919 | 122.9599 | 122.9553 | -0.23804
2364.9688 | 123.0469 | -122.7539 | 0.17395 | -0.17609 | 0.025314 | 0.0038024 | 0.0078955 | -0.0073294 | -0.00034818 | -0.0080109 | -0.24132 | -0.010418 | -0.0062528 | -0.0011216 | 0.0045351 | -0.014862 | 0.24261 | 0.25635 | 0.21973 | 0.21973 | 0.34332 | 0.10071 | -0.036621 | 0.21973 | 0.27466 | 0.13733 | 0.26093 | 0.27008 | 0.013733 | -0.022888 | 122.8546 | 122.7173 | 0.16937 | 123.0103 | 122.9736 | 0.25635 | 0.068665 | 122.7676 | 122.731 | 0.086975 | 122.9736 | 122.8912 | 0.16022 | 0.096131 | 123.0972 | 122.9965 | 122.9736 | -0.21057 | 123.0148 | 123.024 | 123.0286 | -0.19684
2366.7031 | 123.0515 | -122.7585 | 0.16937 | -0.076904 | 0.026596 | 0.0038024 | 0.0038367 | -0.0069022 | 0.003497 | -0.0037385 | -0.16502 | -0.0074277 | -0.0075344 | -0.0013352 | 0.0073123 | -0.015075 | 0.16479 | 0.12817 | 0.064087 | 0.10986 | 0.3067 | 0.022888 | -0.14191 | 0.14648 | 0.14191 | 0.009155 | 0.2243 | 0.18768 | -0.086975 | -0.11902 | 122.7814 | 122.6166 | 0.13733 | 122.8867 | 122.8683 | 0.25177 | -0.004578 | 122.6715 | 122.6395 | 0.054931 | 122.905 | 122.7676 | 0.12817 | 0.01831 | 123.0652 | 122.9233 | 122.8226 | -0.31128 | 122.9828 | 122.9462 | 122.9004 | -0.28839
2368.4219 | 123.1384 | -122.731 | 0.16479 | -0.17609 | 0.027023 | 0.0033752 | 0.0085363 | -0.0083974 | 0.0030698 | -0.0050201 | -0.27184 | -0.0089229 | -0.0043302 | -0.001976 | 0.0041079 | -0.011444 | 0.16937 | 0.13275 | 0.10071 | 0.15106 | 0.37079 | 0.07782 | -0.086975 | 0.13275 | 0.17395 | 0.022888 | 0.28839 | 0.22888 | -0.036621 | -0.09613 | 122.8088 | 122.644 | 0.20599 | 122.8638 | 122.8821 | 0.23804 | 0.004578 | 122.6944 | 122.6349 | 0.1236 | 122.8638 | 122.7539 | 0.11902 | 0.064087 | 123.1018 | 122.9004 | 122.8317 | -0.25177 | 123.0194 | 122.9599 | 122.905 | -0.26092
2370.125 | 123.0194 | -122.7448 | 0.1831 | -0.031128 | 0.027878 | 0.0038024 | 0.0040503 | -0.0081838 | 0.0028562 | -0.0039521 | -0.11162 | -0.0084957 | -0.0073208 | -0.00048061 | 0.0053897 | -0.013153 | 0.14648 | 0.15106 | 0.068665 | 0.10529 | 0.3067 | 0.022888 | -0.12817 | 0.12817 | 0.14648 | 0.013733 | 0.23346 | 0.19684 | -0.059509 | -0.11902 | 122.7676 | 122.6166 | 0.1236 | 122.8958 | 122.85 | 0.23346 | -0.036621 | 122.6852 | 122.6257 | 0.050354 | 122.8729 | 122.7585 | 0.13275 | 0.013733 | 123.0515 | 122.8912 | 122.8134 | -0.31128 | 122.9782 | 122.9416 | 122.8912 | -0.30212
2371.9219 | 123.0148 | -122.7402 | 0.16937 | -0.092163 | 0.027237 | 0.0025208 | 0.0046911 | -0.008611 | 0.004565 | -0.0050201 | -0.096359 | -0.0082821 | -0.0041164 | 0.0018692 | 0.0056033 | -0.01358 | 0.14648 | 0.14191 | 0.073242 | 0.10986 | 0.29297 | 0.027466 | -0.13275 | 0.1236 | 0.15106 | 0.022888 | 0.21973 | 0.18768 | -0.068665 | -0.1236 | 122.7676 | 122.6074 | 0.1236 | 122.8821 | 122.85 | 0.24261 | -0.022889 | 122.6715 | 122.6166 | 0.050354 | 122.8638 | 122.7631 | 0.14648 | 0.01831 | 123.0331 | 122.8867 | 122.8134 | -0.30212 | 122.9599 | 122.9279 | 122.8912 | -0.29297
2373.7031 | 123.0606 | -122.7676 | 0.17395 | -0.13031 | 0.026596 | 0.0048706 | 0.0074683 | -0.0083974 | 0.0011472 | -0.0033111 | -0.10399 | -0.010418 | -0.0058254 | 0.00058739 | 0.0068851 | -0.014862 | 0.13733 | 0.16479 | 0.086975 | 0.11444 | 0.32044 | 0.036621 | -0.10986 | 0.13275 | 0.15106 | 0.022888 | 0.20142 | 0.19684 | -0.059509 | -0.10986 | 122.8043 | 122.6578 | 0.14649 | 122.9324 | 122.8821 | 0.2243 | -0.036621 | 122.7081 | 122.6578 | 0.027466 | 122.9004 | 122.7905 | 0.13275 | 0.022888 | 123.0881 | 122.905 | 122.8546 | -0.28381 | 122.9691 | 122.9645 | 122.9187 | -0.28381
2375.3906 | 122.9599 | -122.7997 | 0.19684 | 0.090942 | 0.027451 | 0.0044434 | 0.0057593 | -0.0073294 | 0.0015744 | -0.0063019 | 0.025711 | -0.0089229 | -0.0047574 | 0.0022964 | 0.0051761 | -0.01123 | 0.018311 | 0.032043 | -0.004578 | 0.041199 | 0.26093 | -0.004578 | -0.17395 | 0.027466 | 0.032043 | -0.068665 | 0.21973 | 0.17853 | -0.091553 | -0.15564 | 122.7951 | 122.6257 | 0.064087 | 122.8317 | 122.8409 | 0.21515 | -0.17853 | 122.7081 | 122.644 | 0.022889 | 122.8271 | 122.731 | 0.086975 | -0.01831 | 123.0606 | 122.818 | 122.7951 | -0.37079 | 123.0194 | 122.9782 | 122.8317 | -0.35248
2377.1406 | 123.0927 | -122.7448 | 0.16479 | -0.046387 | 0.025314 | 0.0070068 | 0.0059729 | -0.0096792 | -0.0069706 | -0.0082245 | -0.050583 | -0.012127 | -0.004971 | -0.0015488 | -0.0016599 | -0.009094 | 0.17395 | 0.25635 | 0.21515 | 0.21057 | 0.32501 | 0.10986 | -0.045776 | 0.25177 | 0.3067 | 0.21515 | 0.27008 | 0.24719 | 0.032043 | -0.022888 | 122.8546 | 122.699 | 0.16022 | 123.0011 | 122.9553 | 0.25635 | 0.009155 | 122.7768 | 122.7219 | 0.10529 | 122.9965 | 122.9599 | 0.23804 | 0.082397 | 123.0698 | 122.9187 | 122.9599 | -0.21057 | 123.0148 | 122.9919 | 123.0515 | -0.18768
2378.9062 | 123.0194 | -122.7768 | 0.16479 | 0.12146 | 0.024887 | 0.0048706 | 0.0055457 | -0.0094656 | -0.00034818 | -0.0077973 | 0.1783 | -0.0084957 | -0.0053982 | 0.00058739 | 0.0051761 | -0.013794 | 0.045776 | 0.032043 | -0.009155 | 0.032043 | 0.23804 | -0.009155 | -0.17853 | 0.10986 | 0.11444 | 0.032043 | 0.18768 | 0.14648 | -0.07782 | -0.1236 | 122.7676 | 122.5983 | 0.073242 | 122.8088 | 122.8088 | 0.21057 | -0.11902 | 122.699 | 122.6532 | 0.022888 | 122.8867 | 122.8088 | 0.15564 | -0.018311 | 123.0148 | 122.8226 | 122.7676 | -0.34332 | 122.9645 | 122.9233 | 122.8912 | -0.28839
2380.6562 | 123.0606 | -122.7585 | 0.17853 | -0.076904 | 0.028946 | 0.006366 | 0.0055457 | -0.0064748 | 0.0043514 | -0.0037385 | -0.11925 | -0.0093503 | -0.006039 | -0.0011216 | 0.0070987 | -0.013794 | 0.16937 | 0.13733 | 0.073242 | 0.11902 | 0.31128 | 0.036621 | -0.11902 | 0.14191 | 0.13733 | 0.027466 | 0.2243 | 0.18768 | -0.050354 | -0.10986 | 122.7951 | 122.6395 | 0.13275 | 122.8958 | 122.8775 | 0.23804 | -0.009155 | 122.7081 | 122.6486 | 0.045776 | 122.9004 | 122.7859 | 0.13733 | 0.009155 | 123.0698 | 122.9279 | 122.8317 | -0.29755 | 122.9828 | 122.9462 | 122.8958 | -0.28839
2382.3438 | 123.0103 | -122.7631 | 0.17395 | 0.16724 | 0.027664 | 0.0048706 | 0.0012731 | -0.0081838 | -0.0020572 | -0.0069427 | 0.16304 | -0.0097775 | -0.008389 | -0.0038986 | 0.0053897 | -0.011444 | 0.073242 | 0.054932 | 0.032043 | 0.054932 | 0.2243 | -0.004578 | -0.1831 | 0.14191 | 0.16479 | 0.068665 | 0.17395 | 0.14191 | -0.059509 | -0.10986 | 122.7585 | 122.58 | 0.050354 | 122.818 | 122.818 | 0.23804 | -0.10071 | 122.7036 | 122.6532 | 0 | 122.905 | 122.8317 | 0.17853 | -0.032043 | 122.9874 | 122.8363 | 122.7951 | -0.35706 | 122.937 | 122.905 | 122.9279 | -0.28381
2384.0938 | 123.0927 | -122.7402 | 0.15564 | -0.14557 | 0.029587 | 0.0027344 | 0.0093909 | -0.0066884 | 0.00071982 | -0.0065155 | -0.13451 | -0.0078549 | -0.0043302 | -0.0030442 | 0.0062441 | -0.014435 | 0.15564 | 0.13275 | 0.082397 | 0.13275 | 0.32044 | 0.036621 | -0.1236 | 0.13275 | 0.15106 | 0.041199 | 0.24719 | 0.19684 | -0.068665 | -0.10986 | 122.7768 | 122.6166 | 0.1648 | 122.8729 | 122.8729 | 0.25635 | 0 | 122.6715 | 122.6303 | 0.091552 | 122.8729 | 122.7814 | 0.15106 | 0.041198 | 123.0606 | 122.8958 | 122.8226 | -0.27924 | 122.9874 | 122.937 | 122.8912 | -0.2655
2385.8438 | 122.9691 | -122.7631 | 0.21515 | -0.015869 | 0.028519 | 0.0038024 | 0.0078955 | -0.0032706 | 0.0028562 | -0.0048065 | -0.027695 | -0.0074277 | -0.0043302 | -0.00026701 | 0.0051761 | -0.014007 | 0.09613 | 0.064087 | 0.027466 | 0.068665 | 0.28381 | 0.013733 | -0.15564 | 0.041199 | 0.059509 | -0.050354 | 0.23346 | 0.16937 | -0.09613 | -0.14648 | 122.7768 | 122.6074 | 0.068664 | 122.8271 | 122.8317 | 0.22431 | -0.11902 | 122.6669 | 122.6166 | 0.01831 | 122.8043 | 122.7127 | 0.09613 | -0.045776 | 123.0469 | 122.8592 | 122.7905 | -0.37079 | 122.9965 | 122.9324 | 122.8226 | -0.36163
2387.5938 | 123.0698 | -122.7722 | 0.16937 | -0.076904 | 0.027664 | 0.0035888 | 0.0072547 | -0.0056204 | 0.0026424 | -0.0056611 | -0.10399 | -0.0082821 | -0.0043302 | 0.00080099 | 0.0058169 | -0.012939 | 0.13733 | 0.1236 | 0.073242 | 0.11444 | 0.30212 | 0.032043 | -0.12817 | 0.1236 | 0.13733 | 0.018311 | 0.20599 | 0.20142 | -0.073242 | -0.11902 | 122.8043 | 122.644 | 0.13275 | 122.8958 | 122.8867 | 0.24262 | -0.032044 | 122.699 | 122.6532 | 0.036621 | 122.8958 | 122.7905 | 0.13733 | 0.032043 | 123.0743 | 122.9095 | 122.8455 | -0.29755 | 122.9782 | 122.9736 | 122.9095 | -0.28839
2389.2812 | 123.0927 | -122.7585 | 0.17395 | -0.23712 | 0.026169 | 0.0055114 | 0.0057593 | -0.0077566 | -0.0035526 | -0.0080109 | -0.21843 | -0.010846 | -0.0053982 | -0.0013352 | 0.0030399 | -0.011871 | 0.13275 | 0.17853 | 0.13275 | 0.16937 | 0.39368 | 0.10071 | -0.059509 | 0.10986 | 0.17853 | 0.073242 | 0.3067 | 0.27924 | 0 | -0.059509 | 122.8592 | 122.699 | 0.21973 | 122.937 | 122.9279 | 0.22888 | -0.041199 | 122.7585 | 122.699 | 0.13275 | 122.8683 | 122.8317 | 0.13275 | 0.10529 | 123.1522 | 122.8912 | 122.8912 | -0.23346 | 123.0652 | 123.0377 | 122.937 | -0.23346
2391.0469 | 123.024 | -122.7722 | 0.16937 | 0.13672 | 0.025955 | 0.0044434 | 0.0044775 | -0.007543 | 0.0015744 | -0.0054475 | 0.21645 | -0.010205 | -0.0056118 | 0.00016019 | 0.0045351 | -0.011444 | 0.022888 | 0.041199 | 0 | 0.027466 | 0.25635 | -0.018311 | -0.1831 | 0.10071 | 0.09613 | 0.009155 | 0.19226 | 0.15106 | -0.07782 | -0.1236 | 122.7539 | 122.5891 | 0.086975 | 122.8134 | 122.7997 | 0.21057 | -0.14649 | 122.6944 | 122.6486 | 0.022888 | 122.8729 | 122.7814 | 0.13275 | -0.018311 | 123.0286 | 122.7951 | 122.7722 | -0.35248 | 122.9645 | 122.9233 | 122.8683 | -0.29297
2392.7969 | 123.0011 | -122.7768 | 0.19226 | 0.075684 | 0.024246 | 0.0048706 | 0.0055457 | -0.0077566 | -0.0041934 | -0.0058747 | 0.10963 | -0.012555 | -0.0075344 | -0.0017624 | 0.0021853 | -0.012085 | 0.11444 | 0.16022 | 0.13275 | 0.14191 | 0.3067 | 0.068665 | -0.09613 | 0.15106 | 0.16937 | 0.12817 | 0.23804 | 0.21973 | -0.013733 | -0.054932 | 122.8455 | 122.6807 | 0.11444 | 122.937 | 122.9187 | 0.23804 | -0.07782 | 122.7631 | 122.7219 | 0.045776 | 122.9279 | 122.905 | 0.18311 | 0.027466 | 123.0835 | 122.8912 | 122.9095 | -0.28839 | 123.0148 | 122.9965 | 122.9462 | -0.24719
2394.5469 | 123.056 | -122.7539 | 0.17395 | -0.076904 | 0.028305 | 0.0031616 | 0.0025549 | -0.0088248 | 0.0022152 | -0.0060883 | -0.12688 | -0.010846 | -0.0062528 | 0.00058739 | 0.0068851 | -0.013153 | 0.16022 | 0.1236 | 0.073242 | 0.10071 | 0.29755 | 0.018311 | -0.11444 | 0.13275 | 0.16022 | 0.013733 | 0.22888 | 0.19226 | -0.059509 | -0.11444 | 122.7722 | 122.6395 | 0.1236 | 122.8775 | 122.8546 | 0.21515 | -0.013733 | 122.6944 | 122.6395 | 0.054932 | 122.8867 | 122.7676 | 0.12817 | 0.018311 | 123.0515 | 122.9141 | 122.8271 | -0.28839 | 122.9828 | 122.9462 | 122.9141 | -0.28839
2396.25 | 123.0881 | -122.7219 | 0.15106 | -0.14557 | 0.02446 | 0.0072204 | 0.0072547 | -0.0079702 | -0.0076114 | -0.0084381 | -0.12688 | -0.012982 | -0.003262 | -0.0017624 | -0.00016447 | -0.011444 | 0.25635 | 0.3067 | 0.27466 | 0.23346 | 0.32044 | 0.11444 | -0.036621 | 0.25177 | 0.32044 | 0.20599 | 0.27466 | 0.27008 | 0.050354 | 0.004578 | 122.8363 | 122.6852 | 0.16937 | 123.0286 | 122.9553 | 0.27008 | 0.10529 | 122.7722 | 122.7264 | 0.1236 | 122.9736 | 122.9279 | 0.20142 | 0.11902 | 123.0423 | 122.9782 | 122.9965 | -0.18768 | 122.9965 | 122.9919 | 123.0423 | -0.14648
2398 | 122.9782 | -122.7814 | 0.19226 | 0.083313 | 0.027237 | 0.0050842 | 0.0038367 | -0.004125 | 0.0032834 | -0.0067291 | 0.04097 | -0.0080685 | -0.0062528 | 0.00037379 | 0.0092349 | -0.016357 | 0.068665 | -0.009155 | -0.036621 | 0.032043 | 0.25177 | -0.004578 | -0.16937 | 0.004578 | 0.036621 | -0.091553 | 0.21057 | 0.19226 | -0.091553 | -0.15564 | 122.7768 | 122.612 | 0.059509 | 122.7722 | 122.8134 | 0.20142 | -0.1236 | 122.6898 | 122.6257 | 0.01831 | 122.7859 | 122.6898 | 0.064087 | 0 | 123.0331 | 122.85 | 122.7448 | -0.36163 | 122.9919 | 122.9736 | 122.818 | -0.3479
2399.75 | 123.024 | -122.7814 | 0.1831 | 0.13672 | 0.024887 | 0.004657 | 0.0031957 | -0.0079702 | -0.0024844 | -0.0073701 | 0.13252 | -0.010205 | -0.006039 | 0.0012284 | 0.0051761 | -0.014435 | 0.12817 | 0.12817 | 0.10071 | 0.09613 | 0.22888 | 0.009155 | -0.15106 | 0.14648 | 0.16937 | 0.059509 | 0.16022 | 0.12817 | -0.050354 | -0.11444 | 122.7905 | 122.6303 | 0.045777 | 122.9095 | 122.8775 | 0.24719 | -0.054931 | 122.731 | 122.6669 | -0.022888 | 122.9279 | 122.8409 | 0.17395 | -0.054931 | 123.0103 | 122.9095 | 122.8821 | -0.33417 | 122.9416 | 122.9095 | 122.9507 | -0.29755
2401.5312 | 122.9874 | -122.7631 | 0.19684 | 0.075684 | 0.027023 | 0.007434 | 0.0046911 | -0.0071158 | 0.0032834 | -0.0052337 | 0.071487 | -0.0089229 | -0.0047574 | 0.00016019 | 0.0043215 | -0.013153 | 0.032043 | -0.036621 | -0.041199 | 0.013733 | 0.27924 | -0.009155 | -0.17395 | 0.018311 | 0.018311 | -0.07782 | 0.20142 | 0.1831 | -0.10071 | -0.15564 | 122.7539 | 122.5891 | 0.082398 | 122.7264 | 122.7768 | 0.18768 | -0.1648 | 122.6624 | 122.6074 | 0.004578 | 122.7814 | 122.6852 | 0.07782 | -0.013733 | 123.0423 | 122.7951 | 122.7219 | -0.37079 | 122.9645 | 122.9462 | 122.7814 | -0.35248
2403.2188 | 122.9874 | -122.7859 | 0.20599 | 0.075684 | 0.0345 | 0.0023072 | 0.0093909 | -0.0088248 | 0.0013608 | -0.0052337 | 0.010452 | -0.0072141 | -0.0017666 | 0.0012284 | 0.0026125 | -0.011444 | 0.036621 | 0.004578 | -0.018311 | 0.036621 | 0.27466 | -0.027466 | -0.15106 | 0.036621 | 0.050354 | -0.086975 | 0.21973 | 0.17853 | -0.10529 | -0.15106 | 122.7585 | 122.6349 | 0.068664 | 122.7905 | 122.8226 | 0.18768 | -0.16937 | 122.6807 | 122.6349 | 0.013733 | 122.8226 | 122.699 | 0.064087 | -0.027466 | 123.0606 | 122.8226 | 122.7676 | -0.35706 | 123.0057 | 122.9645 | 122.8363 | -0.35706
2404.9688 | 122.9736 | -122.7722 | 0.19684 | 0.0070193 | 0.028092 | 0.0044434 | 0.0036231 | -0.0069022 | 0.0028562 | -0.0054475 | 0.04097 | -0.0082821 | -0.0039028 | -0.0013352 | 0.0073123 | -0.013153 | 0.041199 | 0.022888 | -0.009155 | 0.036621 | 0.27008 | -0.027466 | -0.16937 | 0.036621 | 0.050354 | -0.064087 | 0.21057 | 0.1831 | -0.10986 | -0.15106 | 122.7448 | 122.6028 | 0.073243 | 122.7951 | 122.8088 | 0.20599 | -0.15564 | 122.6624 | 122.6212 | 0.013733 | 122.8088 | 122.7081 | 0.086975 | -0.013733 | 123.0423 | 122.8134 | 122.7631 | -0.36621 | 122.9828 | 122.9553 | 122.8226 | -0.3479
2406.6719 | 123.0972 | -122.7264 | 0.15564 | -0.054016 | 0.026383 | 0.0059388 | 0.0061865 | -0.011175 | -0.008466 | -0.0077973 | 0.0028229 | -0.0117 | -0.0064664 | -0.00048061 | -0.00016447 | -0.011657 | 0.14648 | 0.20599 | 0.17395 | 0.18768 | 0.31586 | 0.073242 | -0.050354 | 0.19684 | 0.27008 | 0.1831 | 0.25635 | 0.2243 | 0.013733 | -0.027466 | 122.7997 | 122.6761 | 0.16022 | 122.9324 | 122.9141 | 0.23804 | -0.009156 | 122.7402 | 122.699 | 0.10071 | 122.9233 | 122.9095 | 0.21057 | 0.068664 | 123.0423 | 122.8729 | 122.9004 | -0.20599 | 122.9828 | 122.9507 | 122.9965 | -0.18311
2408.375 | 123.0698 | -122.7539 | 0.16479 | -0.22949 | 0.026596 | 0.0048706 | 0.0042639 | -0.0064748 | -0.00098918 | -0.0058747 | -0.20317 | -0.0091367 | -0.004971 | -0.0021896 | 0.0030399 | -0.014221 | 0.15106 | 0.15106 | 0.1236 | 0.14191 | 0.38452 | 0.086975 | -0.07782 | 0.11902 | 0.17395 | 0.064087 | 0.31128 | 0.29755 | -0.009155 | -0.054932 | 122.8409 | 122.6761 | 0.21973 | 122.905 | 122.8958 | 0.21973 | -0.013733 | 122.7448 | 122.699 | 0.14648 | 122.8729 | 122.818 | 0.11902 | 0.13275 | 123.1384 | 122.905 | 122.8775 | -0.24261 | 123.0652 | 123.0515 | 122.9279 | -0.21973
2410.125 | 122.9828 | -122.7951 | 0.17853 | 0.037537 | 0.027878 | 0.0070068 | 0.0040503 | -0.0079702 | 0.0037106 | -0.0041657 | 0.094375 | -0.0082821 | -0.0043302 | 0.00080099 | 0.0051761 | -0.014648 | 0.064087 | -0.022888 | -0.018311 | 0.027466 | 0.29755 | 0 | -0.16937 | 0 | 0.004578 | -0.059509 | 0.19684 | 0.17853 | -0.10071 | -0.16022 | 122.7951 | 122.6257 | 0.11902 | 122.7722 | 122.8226 | 0.19684 | -0.11444 | 122.6944 | 122.6349 | 0.01831 | 122.7951 | 122.7356 | 0.10071 | 0 | 123.0927 | 122.8592 | 122.7768 | -0.3479 | 122.9919 | 122.9736 | 122.7997 | -0.33874
2411.8281 | 123.1293 | -122.7356 | 0.14648 | -0.18372 | 0.026169 | 0.0057252 | 0.0085363 | -0.0079702 | 7.902e-05 | -0.0041657 | -0.24895 | -0.0097775 | -0.004971 | -0.0013352 | 0.0036807 | -0.014221 | 0.14648 | 0.13733 | 0.086975 | 0.15564 | 0.37079 | 0.082397 | -0.082397 | 0.1236 | 0.16479 | 0.059509 | 0.29755 | 0.25177 | -0.022888 | -0.082397 | 122.818 | 122.6532 | 0.2243 | 122.8729 | 122.8912 | 0.23804 | 0 | 122.7127 | 122.6532 | 0.15106 | 122.8592 | 122.7951 | 0.14191 | 0.10529 | 123.1064 | 122.8821 | 122.8226 | -0.22888 | 123.0331 | 122.9874 | 122.9004 | -0.22888
2413.5312 | 123.1338 | -122.7585 | 0.15564 | -0.19135 | 0.026169 | 0.0044434 | 0.010245 | -0.0090384 | -0.00163 | -0.0067291 | -0.20317 | -0.012768 | -0.0056118 | -0.00048061 | 0.0026125 | -0.014221 | 0.13733 | 0.13733 | 0.086975 | 0.14191 | 0.37537 | 0.073242 | -0.082397 | 0.10986 | 0.17395 | 0.027466 | 0.29755 | 0.23804 | -0.050354 | -0.09613 | 122.8317 | 122.6761 | 0.21973 | 122.8958 | 122.9004 | 0.2243 | -0.018311 | 122.7081 | 122.6624 | 0.14191 | 122.8683 | 122.7859 | 0.1236 | 0.082397 | 123.1338 | 122.8958 | 122.8455 | -0.23804 | 123.056 | 122.9965 | 122.9324 | -0.25177
2415.2812 | 123.0148 | -122.7768 | 0.19684 | 0.15198 | 0.025528 | 0.0040162 | 0.0049047 | -0.0060476 | -0.00013458 | -0.0045929 | 0.12489 | -0.0095639 | -0.0064664 | 0.0010148 | 0.0045351 | -0.013366 | 0.032043 | -0.013733 | -0.027466 | 0.032043 | 0.25635 | -0.013733 | -0.1831 | 0.054932 | 0.064087 | -0.050354 | 0.21515 | 0.18768 | -0.086975 | -0.14648 | 122.7631 | 122.5937 | 0.05951 | 122.7631 | 122.8088 | 0.21515 | -0.1648 | 122.6898 | 122.6303 | 0.018311 | 122.8317 | 122.7264 | 0.09613 | -0.009155 | 123.0331 | 122.8088 | 122.7493 | -0.37994 | 122.9919 | 122.9645 | 122.8409 | -0.34332
2417.0469 | 123.0972 | -122.7356 | 0.16022 | -0.13031 | 0.027664 | 0.0055114 | 0.0061865 | -0.0062612 | 0.0020016 | -0.0048065 | -0.13451 | -0.0084957 | -0.0068936 | -0.00026701 | 0.0043215 | -0.012512 | 0.13733 | 0.13733 | 0.07782 | 0.14648 | 0.33417 | 0.041199 | -0.10986 | 0.10529 | 0.16022 | 0.027466 | 0.2243 | 0.21057 | -0.054932 | -0.11902 | 122.7768 | 122.6257 | 0.17395 | 122.8729 | 122.8821 | 0.25635 | -0.022888 | 122.6807 | 122.6166 | 0.064087 | 122.8409 | 122.7631 | 0.14649 | 0.050354 | 123.0698 | 122.8729 | 122.8134 | -0.27008 | 122.9599 | 122.9462 | 122.8958 | -0.27924
2418.8125 | 123.1018 | -122.7448 | 0.16022 | -0.14557 | 0.023819 | 0.0061524 | 0.0074683 | -0.0079702 | -0.0063296 | -0.0073701 | 0.025711 | -0.013623 | -0.0039028 | -0.0030442 | 0.0011173 | -0.012939 | 0.21515 | 0.28839 | 0.22888 | 0.22888 | 0.32959 | 0.1236 | -0.032043 | 0.24719 | 0.32044 | 0.21515 | 0.26093 | 0.22888 | 0.013733 | -0.027466 | 122.8683 | 122.7127 | 0.16937 | 123.0331 | 122.9736 | 0.26093 | 0.054932 | 122.7585 | 122.7173 | 0.10071 | 122.9919 | 122.9599 | 0.24261 | 0.068665 | 123.0743 | 122.9599 | 122.9736 | -0.19226 | 123.0057 | 122.9736 | 123.0652 | -0.18768
2420.5 | 123.0377 | -122.7539 | 0.18768 | 0.19012 | 0.02446 | 0.0050842 | 0.0051183 | -0.005834 | -0.00077538 | -0.0071563 | 0.1783 | -0.0093503 | -0.0086026 | 0.00037379 | 0.0045351 | -0.014221 | 0.064087 | 0.027466 | 0.018311 | 0.041199 | 0.26093 | -0.018311 | -0.17853 | 0.10986 | 0.11902 | 0.027466 | 0.19226 | 0.16479 | -0.10071 | -0.11902 | 122.7356 | 122.5754 | 0.073242 | 122.7814 | 122.7951 | 0.21973 | -0.1236 | 122.6532 | 122.6349 | 0.004578 | 122.8638 | 122.7814 | 0.14649 | -0.022888 | 123.0148 | 122.818 | 122.7722 | -0.36621 | 122.9462 | 122.9187 | 122.8729 | -0.3067
2422.2031 | 122.9645 | -122.7905 | 0.18768 | 0.19775 | 0.02446 | 0.004657 | 0.0029821 | -0.010106 | -0.0020572 | -0.0073701 | 0.1783 | -0.0117 | -0.00668 | -0.0026168 | 0.0036807 | -0.012298 | 0.12817 | 0.13275 | 0.10986 | 0.11902 | 0.20599 | 0.018311 | -0.14191 | 0.16937 | 0.1831 | 0.091553 | 0.16937 | 0.15106 | -0.054932 | -0.09613 | 122.8088 | 122.6486 | 0.018311 | 122.9233 | 122.9095 | 0.26093 | -0.059509 | 122.7356 | 122.6944 | -0.01831 | 122.9599 | 122.8821 | 0.18768 | -0.036621 | 122.9965 | 122.9187 | 122.9004 | -0.32959 | 122.9599 | 122.9416 | 122.9736 | -0.28381
2423.9531 | 123.0835 | -122.7448 | 0.16479 | -0.10742 | 0.028946 | 0.0044434 | 0.0059729 | -0.0094656 | 0.0032834 | -0.0056611 | -0.14214 | -0.010205 | -0.0021938 | -0.0017624 | 0.0053897 | -0.016998 | 0.17853 | 0.10986 | 0.07782 | 0.11902 | 0.32044 | 0.027466 | -0.11902 | 0.1236 | 0.15106 | 0.018311 | 0.23346 | 0.20142 | -0.073242 | -0.12817 | 122.7722 | 122.6257 | 0.15564 | 122.8546 | 122.8638 | 0.23804 | 0.013733 | 122.6715 | 122.6166 | 0.068664 | 122.8683 | 122.7631 | 0.14649 | 0.036621 | 123.0652 | 122.9233 | 122.8226 | -0.28381 | 122.9782 | 122.9462 | 122.8958 | -0.29297
2425.7031 | 122.9599 | -122.7859 | 0.20142 | 0.098572 | 0.025314 | 0.0035888 | 0.0059729 | -0.0094656 | -0.0048344 | -0.0065155 | 0.20119 | -0.011914 | -0.0041164 | -0.0013352 | 0.00068993 | -0.012298 | 0.11444 | 0.14191 | 0.12817 | 0.09613 | 0.22888 | 0.032043 | -0.14191 | 0.15106 | 0.17853 | 0.07782 | 0.19684 | 0.16479 | -0.050354 | -0.086975 | 122.818 | 122.644 | 0.027466 | 122.9279 | 122.8821 | 0.23804 | -0.086975 | 122.7356 | 122.699 | -0.004578 | 122.937 | 122.8638 | 0.16479 | -0.036621 | 123.0148 | 122.9004 | 122.9141 | -0.34332 | 122.9828 | 122.9507 | 122.9645 | -0.28839
2427.4062 | 123.0927 | -122.7539 | 0.16937 | -0.069275 | 0.027451 | 0.0044434 | 0.0074683 | -0.007543 | 0.0039242 | -0.0065155 | -0.15739 | -0.0093503 | -0.0034756 | 0.00080099 | 0.0062441 | -0.015503 | 0.15564 | 0.13275 | 0.09613 | 0.11902 | 0.32044 | 0.032043 | -0.12817 | 0.13733 | 0.14191 | 0.013733 | 0.23346 | 0.19684 | -0.064087 | -0.12817 | 122.7859 | 122.6257 | 0.15106 | 122.8867 | 122.8729 | 0.24719 | -0.013733 | 122.6898 | 122.6257 | 0.064086 | 122.8912 | 122.7676 | 0.14191 | 0.027465 | 123.0743 | 122.9095 | 122.85 | -0.29755 | 122.9874 | 122.9507 | 122.8958 | -0.29755
2429.1562 | 122.9874 | -122.7814 | 0.18768 | 0.052795 | 0.022751 | 0.0055114 | 0.0040503 | -0.0071158 | -0.0054752 | -0.0052337 | 0.12489 | -0.0117 | -0.006039 | -5.3406e-05 | 0.0023989 | -0.012085 | 0.10071 | 0.14191 | 0.13275 | 0.13275 | 0.27008 | 0.068665 | -0.09613 | 0.16937 | 0.19226 | 0.10529 | 0.25635 | 0.20142 | -0.041199 | -0.054932 | 122.85 | 122.6852 | 0.082398 | 122.9233 | 122.9141 | 0.22888 | -0.086975 | 122.7402 | 122.7264 | 0.068665 | 122.9507 | 122.8867 | 0.16022 | 0.013733 | 123.0515 | 122.8821 | 122.9141 | -0.28381 | 123.0377 | 122.9828 | 122.9736 | -0.24261
2430.9062 | 122.9828 | -122.7905 | 0.19226 | -0.00061023 | 0.027878 | 0.0050842 | 0.0023413 | -0.0049796 | 0.0028562 | -0.0054475 | 0.010452 | -0.0065731 | -0.0081754 | -0.0013352 | 0.0085941 | -0.014007 | 0.11444 | 0.036621 | 0.004578 | 0.050354 | 0.28381 | -0.018311 | -0.16937 | 0.041199 | 0.045776 | -0.059509 | 0.20142 | 0.17853 | -0.09613 | -0.16479 | 122.7722 | 122.6212 | 0.091552 | 122.8271 | 122.8409 | 0.21973 | -0.07782 | 122.6944 | 122.6257 | 0.009155 | 122.8317 | 122.731 | 0.10529 | -0.013733 | 123.0743 | 122.905 | 122.7951 | -0.36163 | 122.9919 | 122.9691 | 122.8363 | -0.35706
2432.5938 | 122.9919 | -122.7585 | 0.18768 | 0.022278 | 0.023819 | 0.0067932 | 0.0046911 | -0.0081838 | -0.0073978 | -0.0071563 | 0.086746 | -0.012555 | -0.0068936 | -0.0026168 | 0.0023989 | -0.011444 | 0.13733 | 0.13275 | 0.13275 | 0.12817 | 0.29755 | 0.059509 | -0.10071 | 0.15106 | 0.19226 | 0.11902 | 0.23346 | 0.21515 | -0.018311 | -0.064087 | 122.818 | 122.6578 | 0.10986 | 122.8912 | 122.8867 | 0.22888 | -0.050354 | 122.7402 | 122.6944 | 0.045776 | 122.9095 | 122.8775 | 0.18311 | 0.027466 | 123.056 | 122.8958 | 122.8912 | -0.28839 | 122.9919 | 122.9736 | 122.9507 | -0.25177
2434.2812 | 123.0331 | -122.7585 | 0.1831 | 0.11383 | 0.024246 | 0.004657 | 0.0042639 | -0.005834 | 0.0020016 | -0.0058747 | 0.13252 | -0.0091367 | -0.0081754 | -0.00090781 | 0.0053897 | -0.01358 | 0.07782 | 0.009155 | -0.004578 | 0.018311 | 0.25177 | -0.027466 | -0.16479 | 0.09613 | 0.10529 | 0 | 0.19226 | 0.16479 | -0.086975 | -0.13733 | 122.731 | 122.5937 | 0.068665 | 122.7676 | 122.7768 | 0.18311 | -0.10528 | 122.6715 | 122.6212 | 0.009156 | 122.8546 | 122.7585 | 0.13733 | -0.01831 | 123.0103 | 122.8363 | 122.7539 | -0.3479 | 122.9507 | 122.9233 | 122.8638 | -0.32043
2436.0469 | 122.9919 | -122.7631 | 0.18768 | 0.15198 | 0.023178 | 0.0057252 | 0.0040503 | -0.0098928 | -0.003339 | -0.0077973 | 0.14015 | -0.010846 | -0.0075344 | -0.0011216 | 0.0036807 | -0.013366 | 0.16022 | 0.12817 | 0.10071 | 0.10986 | 0.23804 | 0.032043 | -0.12817 | 0.16479 | 0.19226 | 0.09613 | 0.22888 | 0.18768 | -0.022888 | -0.086975 | 122.7951 | 122.6349 | 0.050354 | 122.8912 | 122.8729 | 0.23804 | -0.027466 | 122.7402 | 122.6761 | 0.041199 | 122.9279 | 122.8592 | 0.1831 | 0 | 123.0011 | 122.9233 | 122.8638 | -0.31586 | 122.9919 | 122.9507 | 122.9553 | -0.27466
2437.7969 | 123.0927 | -122.7402 | 0.16937 | 0.037537 | 0.022751 | 0.006366 | 0.0036231 | -0.0094656 | -0.006116 | -0.0067291 | 0.04097 | -0.012341 | -0.0053982 | -0.0026168 | 0.0019717 | -0.011657 | 0.14191 | 0.14191 | 0.14191 | 0.15106 | 0.28839 | 0.073242 | -0.07782 | 0.17853 | 0.21515 | 0.13275 | 0.24719 | 0.21973 | -0.013733 | -0.059509 | 122.8134 | 122.6624 | 0.11902 | 122.8821 | 122.8912 | 0.22888 | -0.027466 | 122.7264 | 122.6807 | 0.077819 | 122.9187 | 122.8729 | 0.19226 | 0.050354 | 123.0286 | 122.8821 | 122.8821 | -0.24719 | 122.9874 | 122.9599 | 122.9553 | -0.22888
2439.5469 | 123.0148 | -122.7631 | 0.20599 | 0.14435 | 0.028305 | 0.0025208 | 0.0038367 | -0.0051932 | 0.0041378 | -0.0048065 | 0.063858 | -0.0059323 | -0.0051846 | 0.00037379 | 0.0068851 | -0.013794 | 0.082397 | -0.027466 | -0.036621 | 0.018311 | 0.24261 | -0.054932 | -0.1831 | 0.059509 | 0.027466 | -0.054932 | 0.21973 | 0.17853 | -0.11902 | -0.16479 | 122.7081 | 122.58 | 0.036621 | 122.7356 | 122.7814 | 0.20142 | -0.1236 | 122.644 | 122.5983 | 0.013733 | 122.8226 | 122.7081 | 0.10986 | -0.027466 | 123.0057 | 122.8455 | 122.7264 | -0.3891 | 122.9828 | 122.9416 | 122.7905 | -0.37079
2441.25 | 123.0286 | -122.7814 | 0.1831 | 0.12146 | 0.026383 | 0.0050842 | 0.0068273 | -0.0071158 | -0.00034818 | -0.0052337 | 0.14778 | -0.0097775 | -0.00668 | -0.00026701 | 0.0041079 | -0.014221 | 0.16479 | 0.11444 | 0.11444 | 0.1236 | 0.21973 | 0.004578 | -0.14191 | 0.15564 | 0.15564 | 0.068665 | 0.16937 | 0.13275 | -0.073242 | -0.12817 | 122.7859 | 122.6395 | 0.036622 | 122.8958 | 122.905 | 0.2655 | -0.01831 | 122.7081 | 122.6532 | -0.013732 | 122.937 | 122.85 | 0.19684 | -0.050354 | 123.0011 | 122.9462 | 122.8958 | -0.32501 | 122.9507 | 122.9141 | 122.937 | -0.31128
2443.0156 | 123.0606 | -122.7448 | 0.16937 | -0.19897 | 0.02446 | 0.0050842 | 0.0093909 | -0.0051932 | -0.0035526 | -0.0056611 | -0.13451 | -0.013623 | -0.0047574 | -0.00048061 | 0.0013309 | -0.015716 | 0.23804 | 0.2655 | 0.2243 | 0.22888 | 0.35248 | 0.10986 | -0.032043 | 0.21515 | 0.28839 | 0.14191 | 0.26093 | 0.24261 | 0.004578 | -0.059509 | 122.8546 | 122.7127 | 0.18311 | 123.0103 | 122.9736 | 0.26093 | 0.068664 | 122.7493 | 122.6852 | 0.091552 | 122.9599 | 122.8867 | 0.20142 | 0.073242 | 123.0972 | 122.9828 | 122.9691 | -0.20142 | 123.0057 | 122.9874 | 123.0331 | -0.22888
2444.7656 | 123.0331 | -122.8088 | 0.20142 | 0.12146 | 0.026169 | 0.004657 | 0.0029821 | -0.0077566 | 0.0037106 | -0.0054475 | 0.048599 | -0.0093503 | -0.008389 | -0.00090781 | 0.0058169 | -0.014007 | 0.059509 | -0.018311 | -0.050354 | 0.013733 | 0.2655 | -0.041199 | -0.16937 | 0.073242 | 0.054932 | -0.045776 | 0.20599 | 0.21057 | -0.091553 | -0.14648 | 122.7676 | 122.6395 | 0.064087 | 122.7905 | 122.8226 | 0.18311 | -0.14191 | 122.7173 | 122.6624 | 0.004578 | 122.8821 | 122.7631 | 0.10071 | 0.009155 | 123.0743 | 122.8683 | 122.7585 | -0.37079 | 123.0148 | 123.0194 | 122.8638 | -0.3479
2446.5156 | 123.0698 | -122.7722 | 0.1831 | -0.061646 | 0.028092 | 0.0025208 | 0.0078955 | -0.0051932 | 0.0024288 | -0.0045929 | -0.13451 | -0.0099911 | -0.0041164 | -0.00069421 | 0.0049625 | -0.016143 | 0.17395 | 0.11444 | 0.073242 | 0.10986 | 0.30212 | 0.009155 | -0.11444 | 0.1236 | 0.16937 | 0.009155 | 0.23804 | 0.18768 | -0.064087 | -0.11902 | 122.7814 | 122.6578 | 0.11902 | 122.8867 | 122.8821 | 0.2243 | -0.009155 | 122.7081 | 122.6532 | 0.054932 | 122.8958 | 122.7814 | 0.12817 | 0.004578 | 123.0743 | 122.9462 | 122.8455 | -0.29755 | 123.0103 | 122.9599 | 122.9416 | -0.30212
2448.2188 | 122.9828 | -122.7814 | 0.16937 | 0.13672 | 0.025101 | 0.007434 | 0.0023413 | -0.0081838 | -0.0056888 | -0.0060883 | 0.16304 | -0.010205 | -0.0043302 | -0.0026168 | 0.0023989 | -0.01358 | 0.10986 | 0.15106 | 0.10529 | 0.11902 | 0.23804 | 0.018311 | -0.11444 | 0.16479 | 0.19226 | 0.10529 | 0.21515 | 0.18768 | -0.022888 | -0.073242 | 122.7997 | 122.6669 | 0.068664 | 122.9324 | 122.9004 | 0.23346 | -0.05951 | 122.7585 | 122.7081 | 0.045776 | 122.9462 | 122.8867 | 0.17853 | 0.01831 | 123.0194 | 122.8912 | 122.8867 | -0.28381 | 122.9965 | 122.9691 | 122.9736 | -0.24261
2449.9062 | 122.9965 | -122.7859 | 0.19226 | 0.037537 | 0.023819 | 0.0072204 | 0.0055457 | -0.0079702 | -0.0048344 | -0.0065155 | 0.018082 | -0.011487 | -0.0071072 | 0.00037379 | 0.0032535 | -0.011657 | 0.13733 | 0.14648 | 0.13275 | 0.10986 | 0.28381 | 0.064087 | -0.10071 | 0.16479 | 0.1831 | 0.086975 | 0.24719 | 0.22888 | -0.013733 | -0.059509 | 122.85 | 122.6852 | 0.091552 | 122.9324 | 122.8958 | 0.21057 | -0.054932 | 122.7722 | 122.7264 | 0.054931 | 122.9507 | 122.8729 | 0.14648 | 0.036621 | 123.0698 | 122.9233 | 122.9187 | -0.29297 | 123.0331 | 123.0148 | 122.9691 | -0.25177
2451.5938 | 123.1064 | -122.7173 | 0.14191 | -0.13031 | 0.022537 | 0.0061524 | 0.0066137 | -0.0051932 | -0.0046206 | -0.0073701 | -0.11925 | -0.012127 | -0.0056118 | -0.0030442 | 0.0021853 | -0.01358 | 0.25635 | 0.24261 | 0.23804 | 0.23804 | 0.32501 | 0.10529 | -0.050354 | 0.2655 | 0.33875 | 0.23346 | 0.25177 | 0.21973 | 0.032043 | -0.009155 | 122.8226 | 122.6669 | 0.18311 | 122.9599 | 122.9553 | 0.28839 | 0.11444 | 122.7493 | 122.7081 | 0.10986 | 122.9828 | 122.9507 | 0.24261 | 0.07782 | 123.0423 | 122.9736 | 122.9553 | -0.19226 | 122.9691 | 122.937 | 123.056 | -0.15106
2453.2969 | 123.0103 | -122.7722 | 0.18768 | -0.099793 | 0.028732 | 0.0040162 | 0.0053321 | -0.008611 | 0.0054196 | -0.0048065 | -0.11925 | -0.011059 | -0.0034756 | 0.00251 | 0.0066715 | -0.015716 | 0.17853 | 0.10986 | 0.054932 | 0.10529 | 0.30212 | 0.027466 | -0.13733 | 0.10529 | 0.10986 | -0.022888 | 0.2243 | 0.19684 | -0.086975 | -0.13733 | 122.7997 | 122.6349 | 0.11444 | 122.8821 | 122.8775 | 0.24262 | -0.009155 | 122.6852 | 122.6349 | 0.036621 | 122.8775 | 122.7493 | 0.11444 | 0.009155 | 123.0743 | 122.9507 | 122.8271 | -0.32501 | 122.9965 | 122.9691 | 122.8821 | -0.32501
2455.0469 | 122.9691 | -122.7997 | 0.21057 | 0.045166 | 0.030441 | 0.0052978 | 0.0038367 | -0.0088248 | 0.0039242 | -0.0030975 | -0.0048066 | -0.0093503 | -0.0062528 | -0.0013352 | 0.0075259 | -0.014648 | 0.064087 | 0 | -0.027466 | 0.036621 | 0.27008 | 0 | -0.16937 | 0.041199 | 0.041199 | -0.10071 | 0.2243 | 0.19226 | -0.086975 | -0.17395 | 122.7997 | 122.6303 | 0.05951 | 122.7997 | 122.8363 | 0.20599 | -0.14648 | 122.7127 | 122.6257 | 0.013733 | 122.8409 | 122.699 | 0.073242 | -0.01831 | 123.0698 | 122.8638 | 122.7722 | -0.37994 | 123.024 | 122.9919 | 122.8409 | -0.38452
2456.7969 | 123.0927 | -122.7539 | 0.16479 | -0.17609 | 0.025742 | 0.0059388 | 0.0085363 | -0.0064748 | -0.0012028 | -0.0067291 | -0.24895 | -0.010846 | -0.0053982 | -0.00069421 | 0.0023989 | -0.012298 | 0.14648 | 0.13275 | 0.13275 | 0.14648 | 0.37994 | 0.086975 | -0.073242 | 0.12817 | 0.17853 | 0.045776 | 0.3067 | 0.27924 | -0.018311 | -0.073242 | 122.8409 | 122.6807 | 0.21515 | 122.8867 | 122.9004 | 0.21973 | -0.018311 | 122.7356 | 122.6807 | 0.14191 | 122.8821 | 122.7997 | 0.11902 | 0.11444 | 123.1338 | 122.9004 | 122.8867 | -0.23804 | 123.0606 | 123.0331 | 122.9324 | -0.23804
2458.5625 | 123.0331 | -122.7905 | 0.19226 | 0.11383 | 0.02916 | 0.0038024 | 0.0057593 | -0.0073294 | 0.00029262 | -0.0039521 | 0.048599 | -0.0057187 | -0.007748 | 0.00058739 | 0.0064577 | -0.011871 | 0.045776 | -0.013733 | -0.032043 | 0.032043 | 0.2655 | -0.045776 | -0.20142 | 0.059509 | 0.054932 | -0.041199 | 0.21057 | 0.19684 | -0.10986 | -0.15106 | 122.7448 | 122.5891 | 0.073242 | 122.7768 | 122.8226 | 0.23346 | -0.14648 | 122.6807 | 122.6395 | 0.01831 | 122.85 | 122.7493 | 0.10986 | 0.004577 | 123.056 | 122.8363 | 122.7585 | -0.39368 | 123.0011 | 122.9874 | 122.8455 | -0.34332
2460.25 | 122.9782 | -122.8043 | 0.21515 | 0.045166 | 0.0298 | 0.0033752 | 0.0027685 | -0.007543 | 0.001788 | -0.0063019 | 0.048599 | -0.012555 | -0.0051846 | -0.00026701 | 0.0066715 | -0.013153 | 0.054932 | -0.018311 | -0.027466 | 0.027466 | 0.27924 | -0.018311 | -0.18768 | 0 | 0.032043 | -0.082397 | 0.21973 | 0.1831 | -0.10529 | -0.16479 | 122.7859 | 122.6166 | 0.064087 | 122.7859 | 122.8317 | 0.21515 | -0.16022 | 122.699 | 122.6395 | 0.004578 | 122.8043 | 122.7219 | 0.082398 | -0.032044 | 123.0835 | 122.8592 | 122.7768 | -0.40283 | 123.024 | 122.9874 | 122.8363 | -0.37994
2462 | 123.1155 | -122.7448 | 0.16022 | -0.13031 | 0.028946 | 0.0042298 | 0.0087499 | -0.0049796 | 0.0011472 | -0.0043793 | -0.15739 | -0.0082821 | -0.0036892 | -0.00048061 | 0.0041079 | -0.014648 | 0.14191 | 0.1236 | 0.086975 | 0.12817 | 0.32501 | 0.041199 | -0.11902 | 0.11902 | 0.17395 | 0.013733 | 0.24261 | 0.2243 | -0.068665 | -0.11902 | 122.7859 | 122.6257 | 0.1648 | 122.8683 | 122.8729 | 0.24719 | -0.01831 | 122.6761 | 122.6257 | 0.082398 | 122.8638 | 122.7585 | 0.13275 | 0.064087 | 123.0698 | 122.8867 | 122.8317 | -0.27924 | 122.9874 | 122.9691 | 122.9187 | -0.27924
2463.75 | 123.0286 | -122.7722 | 0.19226 | 0.13672 | 0.02681 | 0.0055114 | 0.0042639 | -0.0079702 | 7.902e-05 | -0.0048065 | 0.12489 | -0.010846 | -0.0045438 | 0.00037379 | 0.0038943 | -0.011871 | 0.018311 | 0.004578 | -0.036621 | 0.022888 | 0.26093 | -0.036621 | -0.1831 | 0.054932 | 0.054932 | -0.041199 | 0.21973 | 0.16479 | -0.10071 | -0.14648 | 122.7356 | 122.5891 | 0.068664 | 122.7768 | 122.7951 | 0.20599 | -0.17395 | 122.6715 | 122.6257 | 0.027466 | 122.8271 | 122.731 | 0.10529 | -0.027466 | 123.0331 | 122.7905 | 122.7356 | -0.37537 | 122.9919 | 122.937 | 122.8271 | -0.33874
2465.5 | 123.0331 | -122.7631 | 0.17853 | 0.1825 | 0.026169 | 0.004657 | 0.0055457 | -0.0094656 | 0.00050622 | -0.0037385 | 0.19356 | -0.010418 | -0.0051846 | 0.00016019 | 0.0053897 | -0.012085 | 0.054932 | 0.064087 | 0.032043 | 0.059509 | 0.24261 | -0.027466 | -0.17853 | 0.13733 | 0.14191 | 0.054932 | 0.17853 | 0.14648 | -0.086975 | -0.13275 | 122.7356 | 122.5845 | 0.064087 | 122.8271 | 122.8226 | 0.23804 | -0.1236 | 122.6761 | 122.6303 | 0 | 122.9004 | 122.818 | 0.18768 | -0.032044 | 123.0057 | 122.818 | 122.7951 | -0.35706 | 122.9416 | 122.9095 | 122.905 | -0.31128
2467.1875 | 122.9691 | -122.7814 | 0.19226 | 0.17487 | 0.023392 | 0.006366 | 0.0053321 | -0.009252 | -0.0052616 | -0.0045929 | 0.17067 | -0.0117 | -0.006039 | -0.0030442 | 0.0015445 | -0.011444 | 0.10529 | 0.13275 | 0.12817 | 0.086975 | 0.20599 | 0.022888 | -0.15564 | 0.17853 | 0.18768 | 0.09613 | 0.17853 | 0.14648 | -0.054932 | -0.11444 | 122.8043 | 122.6257 | 0.013733 | 122.9141 | 122.8683 | 0.24261 | -0.086975 | 122.7264 | 122.6669 | -0.013733 | 122.9599 | 122.8775 | 0.21057 | -0.045777 | 122.9874 | 122.8867 | 122.9095 | -0.3479 | 122.9599 | 122.9279 | 122.9691 | -0.3067
2468.9375 | 123.0835 | -122.7493 | 0.16937 | -0.17609 | 0.02681 | 0.004657 | 0.0068273 | -0.0047658 | -0.0041934 | -0.0080109 | -0.11925 | -0.010632 | -0.0045438 | -0.00090781 | 4.9132e-05 | -0.013153 | 0.24261 | 0.28381 | 0.24719 | 0.23346 | 0.32959 | 0.11902 | -0.022888 | 0.23346 | 0.33417 | 0.19226 | 0.27008 | 0.22888 | 0.022888 | -0.032043 | 122.8683 | 122.7264 | 0.16022 | 123.0331 | 122.9828 | 0.25635 | 0.073242 | 122.7722 | 122.7173 | 0.10071 | 122.9828 | 122.9416 | 0.2243 | 0.059509 | 123.0789 | 122.9919 | 122.9965 | -0.19226 | 123.0194 | 122.9782 | 123.0835 | -0.20142
2470.7031 | 123.0743 | -122.7722 | 0.16022 | -0.1532 | 0.024887 | 0.0020936 | 0.0087499 | -0.007543 | -0.002698 | -0.0086517 | -0.12688 | -0.012555 | -0.0051846 | -0.0028306 | 0.0021853 | -0.013366 | 0.2243 | 0.2655 | 0.22888 | 0.2243 | 0.34332 | 0.11444 | -0.022888 | 0.21057 | 0.30212 | 0.16937 | 0.24261 | 0.2243 | 0 | -0.050354 | 122.8867 | 122.7493 | 0.18311 | 123.0377 | 122.9965 | 0.24719 | 0.064087 | 122.7722 | 122.7219 | 0.082398 | 122.9828 | 122.9416 | 0.21973 | 0.064087 | 123.1155 | 122.9965 | 123.0011 | -0.1831 | 123.0148 | 122.9965 | 123.0743 | -0.21057
2472.4062 | 123.0743 | -122.7493 | 0.17853 | -0.16083 | 0.025742 | 0.0082886 | 0.0081091 | -0.0056204 | -0.0020572 | -0.0092927 | -0.18791 | -0.011487 | -0.0058254 | -0.0030442 | 0.0032535 | -0.013794 | 0.20142 | 0.26093 | 0.2243 | 0.2243 | 0.32044 | 0.10986 | -0.045776 | 0.21515 | 0.29755 | 0.14191 | 0.28381 | 0.24261 | 0.013733 | -0.050354 | 122.8592 | 122.7036 | 0.14191 | 123.0103 | 122.9736 | 0.27008 | 0.022888 | 122.7631 | 122.699 | 0.10528 | 122.9645 | 122.8912 | 0.19226 | 0.064087 | 123.0698 | 122.9507 | 122.9736 | -0.2243 | 123.0331 | 122.9919 | 123.0469 | -0.22888
2474.1562 | 123.0972 | -122.7493 | 0.15106 | -0.0082397 | 0.024033 | 0.0055114 | 0.0051183 | -0.0062612 | -0.0041934 | -0.0065155 | 0.0028229 | -0.012555 | -0.0064664 | -0.001976 | 0.0017581 | -0.013794 | 0.15106 | 0.17395 | 0.15564 | 0.15564 | 0.3067 | 0.07782 | -0.068665 | 0.21973 | 0.26093 | 0.16479 | 0.25635 | 0.2243 | 0.004578 | -0.045776 | 122.8271 | 122.6807 | 0.15564 | 122.9233 | 122.905 | 0.22431 | 0 | 122.7539 | 122.7036 | 0.10529 | 122.9691 | 122.9141 | 0.21057 | 0.073242 | 123.056 | 122.9004 | 122.905 | -0.21973 | 123.0057 | 122.9736 | 123.0103 | -0.19684
2475.9062 | 123.1155 | -122.7356 | 0.14191 | -0.038757 | 0.024246 | 0.0048706 | 0.0055457 | -0.0062612 | -0.003339 | -0.0067291 | -0.073471 | -0.012768 | -0.0086026 | -0.0015488 | 0.0032535 | -0.012939 | 0.19684 | 0.20599 | 0.1831 | 0.18768 | 0.3067 | 0.082397 | -0.073242 | 0.23804 | 0.27008 | 0.19684 | 0.25635 | 0.23804 | -0.004578 | -0.036621 | 122.818 | 122.6624 | 0.16479 | 122.9416 | 122.9233 | 0.26092 | 0.054931 | 122.731 | 122.699 | 0.11444 | 122.9736 | 122.9324 | 0.23346 | 0.09613 | 123.0423 | 122.9324 | 122.9187 | -0.21515 | 122.9919 | 122.9736 | 123.0057 | -0.17853
2477.6562 | 123.0789 | -122.7493 | 0.17853 | 0.0070193 | 0.024674 | 0.0040162 | 0.0014867 | -0.005834 | -0.002698 | -0.0099335 | 0.025711 | -0.0117 | -0.0081754 | -0.0028306 | 0.0030399 | -0.013153 | 0.16479 | 0.13733 | 0.1236 | 0.13733 | 0.29755 | 0.091553 | -0.082397 | 0.1831 | 0.20599 | 0.13275 | 0.25177 | 0.21973 | -0.004578 | -0.064087 | 122.8409 | 122.6669 | 0.11902 | 122.8867 | 122.8867 | 0.21973 | -0.013733 | 122.7448 | 122.6852 | 0.073242 | 122.9324 | 122.8821 | 0.19684 | 0.041199 | 123.0469 | 122.9141 | 122.8729 | -0.26092 | 123.0011 | 122.9691 | 122.9553 | -0.24261
2479.3438 | 123.0057 | -122.7859 | 0.20599 | 0.037537 | 0.024246 | 0.0061524 | 0.0040503 | -0.0060476 | -0.0024844 | -0.0067291 | 0.048599 | -0.0089229 | -0.0051846 | -0.001976 | 0.0032535 | -0.015503 | 0.18768 | 0.1236 | 0.1236 | 0.12817 | 0.28839 | 0.082397 | -0.082397 | 0.1831 | 0.17853 | 0.10986 | 0.2243 | 0.21973 | -0.022888 | -0.091553 | 122.8683 | 122.7036 | 0.082397 | 122.9095 | 122.9141 | 0.21057 | -0.018311 | 122.7631 | 122.6944 | 0.01831 | 122.9691 | 122.8958 | 0.20142 | 0.013733 | 123.0743 | 122.9736 | 122.9095 | -0.28839 | 123.0103 | 123.0057 | 122.9645 | -0.29755
2481.0938 | 123.0789 | -122.7631 | 0.15564 | -0.19897 | 0.025528 | 0.002948 | 0.0061865 | -0.0064748 | -0.00056178 | -0.0075837 | -0.14977 | -0.0117 | -0.0039028 | -0.0028306 | 0.0034671 | -0.015716 | 0.27924 | 0.27924 | 0.23346 | 0.23346 | 0.32044 | 0.1236 | -0.022888 | 0.23804 | 0.30212 | 0.14648 | 0.26093 | 0.23804 | 0.018311 | -0.050354 | 122.8867 | 122.7402 | 0.1648 | 123.0423 | 122.9965 | 0.25635 | 0.1236 | 122.7814 | 122.7127 | 0.10529 | 123.0011 | 122.9095 | 0.19684 | 0.082397 | 123.0835 | 123.0423 | 122.9965 | -0.17853 | 123.024 | 123.0011 | 123.0652 | -0.20599
2482.8438 | 123.1155 | -122.7448 | 0.16022 | -0.13794 | 0.028092 | 0.004657 | 0.0061865 | -0.0077566 | 0.0039242 | -0.0056611 | -0.21843 | -0.0091367 | -0.0062528 | 0.00058739 | 0.0056033 | -0.016571 | 0.1831 | 0.13733 | 0.091553 | 0.13733 | 0.34332 | 0.032043 | -0.10986 | 0.14191 | 0.15564 | 0.009155 | 0.25177 | 0.20142 | -0.068665 | -0.11902 | 122.7768 | 122.6349 | 0.18311 | 122.8821 | 122.8821 | 0.24719 | 0.022888 | 122.6761 | 122.6257 | 0.091553 | 122.8867 | 122.7539 | 0.12817 | 0.041199 | 123.0881 | 122.9279 | 122.8363 | -0.27008 | 122.9965 | 122.9462 | 122.9004 | -0.27924
2484.5938 | 123.1018 | -122.7493 | 0.16479 | -0.24475 | 0.027451 | 0.006366 | 0.0064001 | -0.0073294 | 0.0011472 | -0.0069427 | -0.27184 | -0.0095639 | -0.006039 | 0.00037379 | 0.0017581 | -0.012512 | 0.17853 | 0.14648 | 0.1236 | 0.14191 | 0.40283 | 0.082397 | -0.082397 | 0.14191 | 0.18768 | 0.036621 | 0.32044 | 0.28381 | -0.018311 | -0.059509 | 122.8317 | 122.6669 | 0.23804 | 122.8958 | 122.8912 | 0.2243 | 0.013733 | 122.731 | 122.6898 | 0.15564 | 122.8912 | 122.7859 | 0.09613 | 0.11902 | 123.1522 | 122.9279 | 122.8729 | -0.24719 | 123.0698 | 123.0331 | 122.937 | -0.2243
2486.2812 | 123.0652 | -122.7585 | 0.15564 | -0.22186 | 0.027878 | 0.0050842 | 0.0061865 | -0.0064748 | -0.0056888 | -0.0077973 | -0.12688 | -0.013409 | -0.004971 | -0.0015488 | 0.00068993 | -0.012939 | 0.21973 | 0.28381 | 0.23346 | 0.22888 | 0.33875 | 0.10529 | -0.036621 | 0.23346 | 0.30212 | 0.16937 | 0.24719 | 0.22888 | -0.004578 | -0.054932 | 122.8638 | 122.7219 | 0.18311 | 123.0423 | 122.9874 | 0.2655 | 0.064087 | 122.7539 | 122.7036 | 0.091552 | 122.9919 | 122.9279 | 0.22431 | 0.073242 | 123.0972 | 122.9782 | 122.9919 | -0.19226 | 123.0057 | 122.9874 | 123.0606 | -0.21057
2488.0469 | 123.0743 | -122.7585 | 0.16479 | -0.19897 | 0.027878 | 0.0042298 | 0.0068273 | -0.0081838 | -0.0018436 | -0.0069427 | -0.18791 | -0.011487 | -0.0036892 | 0.00037379 | 0.0026125 | -0.015075 | 0.17853 | 0.21057 | 0.15106 | 0.17395 | 0.36163 | 0.10529 | -0.064087 | 0.14191 | 0.16937 | 0.050354 | 0.30212 | 0.26093 | -0.018311 | -0.073242 | 122.8638 | 122.6944 | 0.19684 | 122.9691 | 122.9324 | 0.23804 | 0.013733 | 122.7402 | 122.6852 | 0.13733 | 122.9004 | 122.8088 | 0.1236 | 0.09613 | 123.1201 | 122.937 | 122.9095 | -0.22888 | 123.0606 | 123.0194 | 122.9279 | -0.23804
2489.8125 | 123.056 | -122.7539 | 0.1831 | -0.17609 | 0.027237 | 0.0072204 | 0.0089635 | -0.0069022 | -0.00098918 | -0.0080109 | -0.21843 | -0.0093503 | -0.0056118 | -0.0015488 | 0.0017581 | -0.013794 | 0.21057 | 0.27008 | 0.21973 | 0.2243 | 0.36163 | 0.10986 | -0.054932 | 0.21515 | 0.27008 | 0.13275 | 0.28381 | 0.22888 | -0.004578 | -0.032043 | 122.8638 | 122.699 | 0.17853 | 123.024 | 122.9782 | 0.27924 | 0.027466 | 122.7493 | 122.7219 | 0.10071 | 122.9691 | 122.8867 | 0.16479 | 0.045777 | 123.1155 | 122.9645 | 122.9736 | -0.23804 | 123.0377 | 122.9828 | 123.024 | -0.21515
2491.5781 | 122.9874 | -122.8088 | 0.19684 | 0.037537 | 0.024246 | 0.0048706 | 0.0055457 | -0.0083974 | -0.0024844 | -0.0050201 | 0.079117 | -0.011059 | -0.0073208 | -0.001976 | 0.0036807 | -0.013366 | 0.11902 | 0.16937 | 0.1236 | 0.11902 | 0.27924 | 0.050354 | -0.10986 | 0.1831 | 0.20142 | 0.11444 | 0.23804 | 0.19684 | -0.032043 | -0.09613 | 122.8592 | 122.699 | 0.082398 | 122.9782 | 122.9279 | 0.22888 | -0.077819 | 122.7768 | 122.7127 | 0.041199 | 122.9919 | 122.9233 | 0.21057 | 0 | 123.0881 | 122.9279 | 122.9324 | -0.3067 | 123.0469 | 123.0057 | 123.0103 | -0.29297
2493.3281 | 123.1201 | -122.7539 | 0.17395 | -0.25238 | 0.023178 | 0.0040162 | 0.0040503 | -0.0060476 | -0.00034818 | -0.0071563 | -0.26421 | -0.0091367 | -0.0041164 | -0.0015488 | 0.0060305 | -0.015503 | 0.16937 | 0.16022 | 0.10986 | 0.15564 | 0.39368 | 0.082397 | -0.086975 | 0.12817 | 0.14191 | 0.036621 | 0.32501 | 0.26093 | -0.032043 | -0.073242 | 122.8363 | 122.6669 | 0.21973 | 122.9141 | 122.9095 | 0.24261 | -0.004577 | 122.7219 | 122.6807 | 0.15106 | 122.8821 | 122.7905 | 0.10986 | 0.086975 | 123.1476 | 122.9233 | 122.8638 | -0.26092 | 123.0789 | 123.0148 | 122.8958 | -0.24719
2495.0156 | 123.0881 | -122.7539 | 0.15106 | -0.0082397 | 0.01976 | 0.0076478 | 0.0076819 | -0.01032 | -0.0054752 | -0.0060883 | 0.025711 | -0.010205 | -0.0073208 | -0.00069421 | 0.0021853 | -0.011871 | 0.11444 | 0.1831 | 0.15564 | 0.14648 | 0.31128 | 0.054932 | -0.07782 | 0.19684 | 0.22888 | 0.12817 | 0.24719 | 0.21973 | -0.004578 | -0.07782 | 122.8088 | 122.6761 | 0.16022 | 122.937 | 122.9004 | 0.2243 | -0.036621 | 122.7493 | 122.6761 | 0.09613 | 122.9507 | 122.8821 | 0.20599 | 0.068665 | 123.0652 | 122.8683 | 122.9095 | -0.22888 | 123.0011 | 122.9736 | 122.9828 | -0.22888
2496.7656 | 122.9919 | -122.8134 | 0.18768 | 0.083313 | 0.029587 | 0.0059388 | 0.0049047 | -0.0066884 | 0.0037106 | -0.0041657 | -0.050583 | -0.0089229 | -0.0068936 | -0.001976 | 0.0096621 | -0.015075 | 0.050354 | 0.004578 | -0.041199 | 0.027466 | 0.26093 | -0.022888 | -0.18768 | 0.045776 | 0.045776 | -0.07782 | 0.2243 | 0.16022 | -0.10529 | -0.16479 | 122.7905 | 122.6257 | 0.073242 | 122.818 | 122.8409 | 0.21515 | -0.13733 | 122.7081 | 122.6486 | 0.036621 | 122.8592 | 122.7356 | 0.086975 | -0.027466 | 123.0743 | 122.8638 | 122.7722 | -0.37537 | 123.0377 | 122.9736 | 122.8592 | -0.35248
2498.5312 | 122.9919 | -122.7814 | 0.19684 | -0.076904 | 0.027237 | 0.0025208 | 0.0046911 | -0.0049796 | 0.004565 | -0.0037385 | -0.10399 | -0.0082821 | -0.0034756 | 0.0012284 | 0.0062441 | -0.014221 | 0.13275 | 0.10529 | 0.045776 | 0.086975 | 0.30212 | 0.018311 | -0.15106 | 0.091553 | 0.10071 | -0.027466 | 0.21057 | 0.17853 | -0.091553 | -0.14191 | 122.7997 | 122.6303 | 0.10529 | 122.8867 | 122.8683 | 0.23804 | -0.064087 | 122.6898 | 122.6395 | 0.013733 | 122.8729 | 122.7539 | 0.11444 | -0.01831 | 123.0835 | 122.9141 | 122.8271 | -0.3479 | 122.9919 | 122.9599 | 122.8821 | -0.33875
2500.2188 | 123.1201 | -122.7356 | 0.17853 | -0.18372 | 0.02681 | 0.0055114 | 0.0049047 | -0.0077566 | -0.00056178 | -0.0048065 | -0.20317 | -0.0099911 | -0.00668 | -0.0015488 | 0.0038943 | -0.014435 | 0.14191 | 0.14648 | 0.091553 | 0.14648 | 0.35706 | 0.059509 | -0.10986 | 0.11902 | 0.18768 | 0.009155 | 0.2655 | 0.20142 | -0.059509 | -0.1236 | 122.7951 | 122.6257 | 0.17853 | 122.8821 | 122.8821 | 0.25635 | -0.036621 | 122.6761 | 122.612 | 0.086975 | 122.8546 | 122.7448 | 0.13275 | 0.022888 | 123.0927 | 122.8775 | 122.8271 | -0.28839 | 123.0011 | 122.937 | 122.9233 | -0.30212
2501.9688 | 123.1064 | -122.7356 | 0.15564 | -0.00061023 | 0.022965 | 0.0065796 | 0.0070409 | -0.0079702 | -0.0073978 | -0.0080109 | 0.018082 | -0.0099911 | -0.0058254 | -0.00090781 | 0.00068993 | -0.012512 | 0.1236 | 0.19226 | 0.16022 | 0.17395 | 0.31128 | 0.086975 | -0.07782 | 0.19684 | 0.26093 | 0.16937 | 0.24719 | 0.23804 | 0 | -0.041199 | 122.8226 | 122.6578 | 0.15564 | 122.9279 | 122.9095 | 0.25177 | -0.032044 | 122.7356 | 122.6944 | 0.091552 | 122.9324 | 122.905 | 0.21057 | 0.082397 | 123.0469 | 122.8592 | 122.8958 | -0.23346 | 122.9828 | 122.9736 | 122.9965 | -0.19684
2503.7188 | 123.0652 | -122.7768 | 0.16479 | -0.19897 | 0.027237 | 0.009143 | 0.0057593 | -0.0079702 | -0.0012028 | -0.0056611 | -0.18791 | -0.0093503 | -0.0053982 | -0.0021896 | 0.0032535 | -0.013153 | 0.15564 | 0.16022 | 0.13275 | 0.14648 | 0.37079 | 0.10071 | -0.064087 | 0.13733 | 0.1831 | 0.054932 | 0.31586 | 0.27466 | -0.032043 | -0.068665 | 122.8775 | 122.7127 | 0.20599 | 122.937 | 122.9233 | 0.21057 | -0.009155 | 122.7448 | 122.7081 | 0.15106 | 122.9141 | 122.8317 | 0.1236 | 0.10986 | 123.1476 | 122.9324 | 122.9095 | -0.22888 | 123.0927 | 123.0515 | 122.9599 | -0.23346
2505.4062 | 123.1064 | -122.7493 | 0.17853 | -0.26001 | 0.027237 | 0.0050842 | 0.0070409 | -0.0083974 | -0.00056178 | -0.0058747 | -0.27946 | -0.0099911 | -0.0047574 | -0.0013352 | 0.0028263 | -0.015289 | 0.16479 | 0.14191 | 0.10071 | 0.16937 | 0.37537 | 0.086975 | -0.082397 | 0.11444 | 0.16937 | 0.045776 | 0.31128 | 0.27008 | -0.027466 | -0.07782 | 122.8363 | 122.6669 | 0.19684 | 122.8912 | 122.9187 | 0.25177 | -0.013733 | 122.7219 | 122.6715 | 0.13275 | 122.8638 | 122.7951 | 0.1236 | 0.091553 | 123.1247 | 122.9141 | 122.85 | -0.26092 | 123.0606 | 123.0194 | 122.9187 | -0.25635
2507.1406 | 122.9965 | -122.7768 | 0.19684 | -0.054016 | 0.027237 | 0.0035888 | 0.0036231 | -0.0081838 | 0.0026424 | -0.0030975 | -0.073471 | -0.0084957 | -0.0062528 | -5.3406e-05 | 0.0081667 | -0.012939 | 0.13733 | 0.10071 | 0.064087 | 0.091553 | 0.29297 | 0.032043 | -0.14648 | 0.082397 | 0.10529 | -0.018311 | 0.21973 | 0.19684 | -0.086975 | -0.13733 | 122.8088 | 122.6303 | 0.096131 | 122.8775 | 122.8683 | 0.23804 | -0.059509 | 122.6898 | 122.6395 | 0.022889 | 122.8592 | 122.7585 | 0.11902 | 0 | 123.0698 | 122.9141 | 122.8409 | -0.34332 | 122.9965 | 122.9736 | 122.8821 | -0.33417
2508.9219 | 123.0057 | -122.7997 | 0.17853 | -0.084534 | 0.026596 | 0.0038024 | 0.0034093 | -0.007543 | 0.0024288 | -0.0050201 | -0.08873 | -0.0091367 | -0.00668 | 0.00058739 | 0.0060305 | -0.013366 | 0.13733 | 0.11902 | 0.064087 | 0.09613 | 0.3067 | 0.013733 | -0.12817 | 0.10986 | 0.13275 | -0.009155 | 0.23804 | 0.17395 | -0.082397 | -0.13275 | 122.8134 | 122.6715 | 0.12817 | 122.9187 | 122.8958 | 0.2243 | -0.041199 | 122.7173 | 122.6669 | 0.059509 | 122.9095 | 122.7905 | 0.1236 | -0.004578 | 123.1064 | 122.937 | 122.8638 | -0.3067 | 123.0377 | 122.9736 | 122.9324 | -0.31128
2510.6719 | 123.056 | -122.7631 | 0.15564 | -0.19135 | 0.025314 | 0.0050842 | 0.0070409 | -0.0045522 | -0.0054752 | -0.0052337 | -0.20317 | -0.0099911 | -0.0056118 | -0.0024032 | 0.00026273 | -0.011871 | 0.19684 | 0.24719 | 0.21973 | 0.22888 | 0.33875 | 0.09613 | -0.059509 | 0.19226 | 0.28381 | 0.14191 | 0.28839 | 0.24719 | 0.013733 | -0.041199 | 122.8592 | 122.7036 | 0.18311 | 123.0103 | 122.9919 | 0.28839 | 0.041198 | 122.7768 | 122.7219 | 0.13275 | 122.9553 | 122.905 | 0.18311 | 0.091552 | 123.1018 | 122.9599 | 122.9828 | -0.21515 | 123.0515 | 123.0103 | 123.0469 | -0.19684
2512.3594 | 123.1293 | -122.7493 | 0.15564 | -0.19135 | 0.028305 | 0.0076478 | 0.010459 | -0.0079702 | 0.00093342 | -0.0060883 | -0.21843 | -0.0089229 | -0.0021938 | 0.00016019 | 0.0034671 | -0.015503 | 0.12817 | 0.12817 | 0.07782 | 0.13733 | 0.36621 | 0.059509 | -0.11444 | 0.11444 | 0.16479 | 0.032043 | 0.28381 | 0.23804 | -0.022888 | -0.086975 | 122.8088 | 122.6349 | 0.21057 | 122.8775 | 122.8867 | 0.25177 | -0.027466 | 122.7264 | 122.6624 | 0.12817 | 122.8638 | 122.7814 | 0.11902 | 0.082397 | 123.1155 | 122.8775 | 122.8271 | -0.27008 | 123.0331 | 122.9874 | 122.9141 | -0.24261
2514.1094 | 122.9828 | -122.7951 | 0.19226 | 0.060425 | 0.027878 | 0.004657 | 0.0044775 | -0.0064748 | -0.00034818 | -0.0045929 | 0.048599 | -0.0076413 | -0.0041164 | -0.0017624 | 0.0053897 | -0.012939 | 0.022888 | -0.009155 | -0.041199 | 0.027466 | 0.29297 | -0.022888 | -0.1831 | 0.027466 | 0.041199 | -0.073242 | 0.20142 | 0.1831 | -0.09613 | -0.17853 | 122.7722 | 122.612 | 0.10071 | 122.7859 | 122.8226 | 0.21057 | -0.16937 | 122.699 | 122.6166 | 0.009155 | 122.8226 | 122.7219 | 0.10529 | -0.009156 | 123.0881 | 122.818 | 122.7539 | -0.37537 | 122.9965 | 122.9782 | 122.8363 | -0.37079
2515.8594 | 122.9828 | -122.7859 | 0.18768 | 0.045166 | 0.02681 | 0.0052978 | 0.0040503 | -0.0064748 | 0.0026424 | -0.0071563 | 0.056228 | -0.0076413 | -0.0058254 | -0.0011216 | 0.0060305 | -0.013794 | 0.013733 | -0.018311 | -0.036621 | 0.032043 | 0.27008 | -0.018311 | -0.1831 | 0.032043 | 0.050354 | -0.091553 | 0.22888 | 0.15564 | -0.10529 | -0.16479 | 122.7676 | 122.6028 | 0.082398 | 122.7676 | 122.818 | 0.21515 | -0.17395 | 122.6807 | 122.6212 | 0.041199 | 122.818 | 122.6944 | 0.073242 | -0.032043 | 123.056 | 122.7997 | 122.7493 | -0.37079 | 123.0148 | 122.9416 | 122.8363 | -0.35248
2517.6094 | 122.9828 | -122.7814 | 0.20142 | 0.045166 | 0.028519 | 0.0040162 | 0.0051183 | -0.0071158 | 0.001788 | -0.0080109 | 0.102 | -0.0093503 | -0.0047574 | -0.00048061 | 0.0088077 | -0.011657 | 0 | -0.009155 | -0.041199 | 0.018311 | 0.27008 | 0 | -0.19226 | 0.027466 | 0.036621 | -0.068665 | 0.20599 | 0.16479 | -0.10071 | -0.17853 | 122.7814 | 122.5891 | 0.068665 | 122.7722 | 122.7997 | 0.21057 | -0.20142 | 122.6807 | 122.6028 | 0.004578 | 122.8088 | 122.7127 | 0.10986 | -0.036621 | 123.0515 | 122.7814 | 122.7402 | -0.39368 | 122.9874 | 122.9462 | 122.818 | -0.37994
2519.3594 | 122.9919 | -122.7768 | 0.17853 | 0.060425 | 0.027023 | 0.0065796 | 0.0078955 | -0.0088248 | -0.006757 | -0.0075837 | 0.17067 | -0.0117 | -0.006039 | -0.0024032 | 0.0011173 | -0.01123 | 0.09613 | 0.14648 | 0.11444 | 0.11444 | 0.24719 | 0.054932 | -0.10986 | 0.1236 | 0.19226 | 0.1236 | 0.22888 | 0.19684 | -0.013733 | -0.086975 | 122.8317 | 122.6669 | 0.068664 | 122.9233 | 122.8912 | 0.2243 | -0.082398 | 122.7631 | 122.6898 | 0.050354 | 122.9004 | 122.9004 | 0.21057 | 0.01831 | 123.024 | 122.8729 | 122.8912 | -0.28839 | 123.0057 | 122.9736 | 122.9691 | -0.2655
2521.0469 | 122.9874 | -122.7905 | 0.19226 | 0.11383 | 0.023605 | 0.0059388 | 0.0046911 | -0.0056204 | -0.005048 | -0.0075837 | 0.14015 | -0.0097775 | -0.0073208 | -0.0041122 | 0.0049625 | -0.0082394 | 0.1236 | 0.13275 | 0.11444 | 0.10986 | 0.25177 | 0.036621 | -0.14191 | 0.14648 | 0.19684 | 0.11902 | 0.23346 | 0.21515 | -0.036621 | -0.091553 | 122.8271 | 122.6486 | 0.059509 | 122.9233 | 122.9004 | 0.25177 | -0.068665 | 122.7539 | 122.699 | 0.041198 | 122.937 | 122.9095 | 0.21057 | 0.022888 | 123.0423 | 122.9141 | 122.905 | -0.33417 | 123.024 | 123.0057 | 122.9874 | -0.28381
2522.7969 | 123.0972 | -122.7768 | 0.15564 | -0.11505 | 0.027451 | 0.004657 | 0.0053321 | -0.0060476 | 0.00071982 | -0.0050201 | -0.13451 | -0.0078549 | -0.007748 | -0.00090781 | 0.0056033 | -0.014007 | 0.17395 | 0.11902 | 0.07782 | 0.11902 | 0.32959 | 0.027466 | -0.14191 | 0.10529 | 0.16022 | 0.018311 | 0.23346 | 0.21057 | -0.07782 | -0.11902 | 122.8043 | 122.6349 | 0.17395 | 122.8958 | 122.8958 | 0.26093 | 0.01831 | 122.699 | 122.6578 | 0.077819 | 122.8821 | 122.7951 | 0.13733 | 0.054931 | 123.1064 | 122.9507 | 122.8546 | -0.29755 | 123.0103 | 122.9874 | 122.937 | -0.27466
2524.5625 | 123.0698 | -122.7859 | 0.16479 | -0.18372 | 0.027664 | 0.0055114 | 0.0057593 | -0.0077566 | -0.005048 | -0.0071563 | -0.13451 | -0.013623 | -0.0043302 | -0.0034714 | 0.0023989 | -0.012939 | 0.23346 | 0.25177 | 0.21057 | 0.21973 | 0.33875 | 0.11902 | -0.045776 | 0.19684 | 0.29755 | 0.17853 | 0.26093 | 0.23804 | 0.013733 | -0.036621 | 122.905 | 122.7402 | 0.17395 | 123.0377 | 123.0057 | 0.2655 | 0.068664 | 122.7997 | 122.7493 | 0.09613 | 122.9828 | 122.9645 | 0.21515 | 0.073242 | 123.1247 | 123.0194 | 122.9965 | -0.21057 | 123.0469 | 123.024 | 123.0835 | -0.20142
2526.25 | 123.1247 | -122.7585 | 0.15106 | -0.19135 | 0.0298 | 0.0059388 | 0.0098181 | -0.0069022 | 0.003497 | -0.0052337 | -0.19554 | -0.010418 | -0.0041164 | -0.0011216 | 0.0038943 | -0.01593 | 0.16022 | 0.10529 | 0.091553 | 0.11902 | 0.32959 | 0.059509 | -0.10071 | 0.11902 | 0.16937 | 0.041199 | 0.25177 | 0.21973 | -0.059509 | -0.1236 | 122.818 | 122.6578 | 0.17853 | 122.8638 | 122.8775 | 0.21973 | 0.009155 | 122.699 | 122.6349 | 0.10071 | 122.8775 | 122.7997 | 0.16479 | 0.068665 | 123.0881 | 122.9187 | 122.85 | -0.25177 | 123.0103 | 122.9782 | 122.9279 | -0.27466
2528.0156 | 122.9919 | -122.7997 | 0.21057 | -0.046387 | 0.028946 | 0.0023072 | 0.0057593 | -0.0073294 | 0.0026424 | -0.0041657 | -0.050583 | -0.0095639 | -0.0030484 | 0.0016556 | 0.0056033 | -0.015075 | 0.09613 | 0.054932 | 0.022888 | 0.050354 | 0.28839 | 0 | -0.16479 | 0.032043 | 0.050354 | -0.054932 | 0.20599 | 0.1831 | -0.10986 | -0.16937 | 122.7997 | 122.6349 | 0.07782 | 122.8546 | 122.85 | 0.21515 | -0.11444 | 122.6898 | 122.6303 | -0.004577 | 122.8317 | 122.7448 | 0.11444 | -0.027466 | 123.0881 | 122.8958 | 122.8226 | -0.37537 | 123.0057 | 122.9828 | 122.85 | -0.37994
2529.7812 | 123.1155 | -122.7585 | 0.16022 | -0.10742 | 0.028305 | 0.0065796 | 0.0044775 | -0.0069022 | -0.00077538 | -0.0050201 | -0.10399 | -0.0084957 | -0.0041164 | 0.0010148 | 0.0047489 | -0.016143 | 0.13733 | 0.1236 | 0.07782 | 0.10986 | 0.32959 | 0.027466 | -0.13733 | 0.1236 | 0.15564 | 0.022888 | 0.24261 | 0.20142 | -0.073242 | -0.12817 | 122.7859 | 122.6212 | 0.16937 | 122.8821 | 122.8683 | 0.24719 | -0.022888 | 122.6852 | 122.6303 | 0.082398 | 122.8821 | 122.7814 | 0.15106 | 0.041199 | 123.0881 | 122.8958 | 122.8363 | -0.29755 | 123.0011 | 122.9599 | 122.9141 | -0.28839
2531.5469 | 123.0011 | -122.7859 | 0.1831 | 0.15198 | 0.024674 | 0.0038024 | 0.0038367 | -0.0083974 | -0.0022708 | -0.0052337 | 0.20882 | -0.011487 | -0.0058254 | 0.00037379 | 0.0045351 | -0.012726 | 0.09613 | 0.14648 | 0.09613 | 0.09613 | 0.18768 | -0.009155 | -0.15564 | 0.16479 | 0.17853 | 0.082397 | 0.15106 | 0.12817 | -0.082397 | -0.13275 | 122.7768 | 122.6303 | 0.004578 | 122.9324 | 122.8821 | 0.25177 | -0.086975 | 122.7036 | 122.6532 | -0.032043 | 122.9507 | 122.8683 | 0.21515 | -0.054931 | 122.9736 | 122.8821 | 122.8821 | -0.33874 | 122.937 | 122.9141 | 122.9645 | -0.31586
2533.2344 | 123.0743 | -122.7539 | 0.17395 | -0.2066 | 0.020401 | 0.008075 | 0.0064001 | -0.0069022 | -0.0071842 | -0.0080109 | -0.12688 | -0.012555 | -0.0073208 | -0.0030442 | 0.0026125 | -0.014435 | 0.22888 | 0.28839 | 0.24261 | 0.23346 | 0.33417 | 0.11902 | -0.027466 | 0.2243 | 0.32044 | 0.19684 | 0.27008 | 0.25635 | 0.018311 | -0.032043 | 122.8729 | 122.7264 | 0.16022 | 123.0423 | 122.9874 | 0.26093 | 0.054932 | 122.7722 | 122.7219 | 0.096131 | 122.9782 | 122.9507 | 0.22888 | 0.082398 | 123.0881 | 122.9828 | 122.9965 | -0.20142 | 123.024 | 123.0103 | 123.0743 | -0.20599
2534.9844 | 123.0743 | -122.7402 | 0.16937 | -0.16846 | 0.025101 | 0.0065796 | 0.010886 | -0.005834 | -0.0056888 | -0.0077973 | -0.12688 | -0.012768 | -0.0047574 | -0.0021896 | 0.0026125 | -0.012512 | 0.25177 | 0.28381 | 0.23346 | 0.23346 | 0.3479 | 0.11902 | -0.022888 | 0.22888 | 0.31586 | 0.18768 | 0.24261 | 0.23346 | 0.018311 | -0.022888 | 122.8592 | 122.7173 | 0.17853 | 123.024 | 122.9736 | 0.25635 | 0.082397 | 122.7585 | 122.7173 | 0.073242 | 122.9691 | 122.9279 | 0.21057 | 0.064086 | 123.0881 | 122.9919 | 122.9736 | -0.19226 | 122.9828 | 122.9736 | 123.056 | -0.19226
2536.7344 | 123.0011 | -122.7768 | 0.18768 | 0.037537 | 0.025314 | 0.0044434 | 0.0076819 | -0.007543 | -0.0048344 | -0.0084381 | 0.071487 | -0.013196 | -0.0068936 | -0.00069421 | 0.0021853 | -0.013366 | 0.12817 | 0.14648 | 0.12817 | 0.1236 | 0.29755 | 0.059509 | -0.07782 | 0.15106 | 0.1831 | 0.10529 | 0.23804 | 0.20599 | -0.018311 | -0.07782 | 122.8363 | 122.699 | 0.10986 | 122.9233 | 122.9004 | 0.20142 | -0.059509 | 122.7585 | 122.699 | 0.050354 | 122.9279 | 122.8821 | 0.18311 | 0.018311 | 123.0743 | 122.905 | 122.905 | -0.2655 | 123.0148 | 122.9828 | 122.9599 | -0.2655
2538.5312 | 123.1247 | -122.7493 | 0.17395 | -0.16846 | 0.027237 | 0.0057252 | 0.0055457 | -0.01032 | 0.001788 | -0.0050201 | -0.22606 | -0.0099911 | -0.0051846 | 0.00016019 | 0.0056033 | -0.015716 | 0.16479 | 0.12817 | 0.082397 | 0.14191 | 0.32959 | 0.022888 | -0.12817 | 0.11902 | 0.16022 | 0.018311 | 0.25635 | 0.2243 | -0.059509 | -0.1236 | 122.7722 | 122.6212 | 0.15564 | 122.8775 | 122.8912 | 0.27008 | -0.009155 | 122.6898 | 122.6257 | 0.082398 | 122.8683 | 122.7676 | 0.14191 | 0.050354 | 123.0789 | 122.9141 | 122.8317 | -0.30212 | 123.0057 | 122.9736 | 122.9095 | -0.29755
2540.2188 | 122.9965 | -122.7951 | 0.19226 | -0.069275 | 0.031296 | 0.0027344 | 0.0046911 | -0.0054068 | 0.0028562 | -0.0067291 | -0.08873 | -0.0076413 | -0.0045438 | -0.00026701 | 0.0051761 | -0.014435 | 0.1236 | 0.12817 | 0.050354 | 0.10529 | 0.29297 | 0.022888 | -0.13275 | 0.091553 | 0.09613 | -0.045776 | 0.21973 | 0.17395 | -0.10071 | -0.14191 | 122.818 | 122.6624 | 0.10071 | 122.9233 | 122.9004 | 0.23804 | -0.068665 | 122.6944 | 122.6532 | 0.027466 | 122.8867 | 122.7493 | 0.096131 | -0.018311 | 123.0881 | 122.9187 | 122.8455 | -0.32501 | 123.0148 | 122.9691 | 122.8912 | -0.33417
2541.9688 | 123.0698 | -122.7539 | 0.17395 | -0.25238 | 0.027878 | 0.004657 | 0.0087499 | -0.0049796 | -0.004407 | -0.0067291 | -0.15739 | -0.012127 | -0.0034756 | -0.00048061 | 0.00090353 | -0.013794 | 0.1831 | 0.24719 | 0.17853 | 0.20142 | 0.36163 | 0.10529 | -0.064087 | 0.14648 | 0.23346 | 0.07782 | 0.31128 | 0.2655 | -0.004578 | -0.068665 | 122.8592 | 122.6898 | 0.18768 | 123.0011 | 122.9553 | 0.2655 | 0.009155 | 122.7493 | 122.6852 | 0.13733 | 122.9004 | 122.8317 | 0.14649 | 0.091553 | 123.1155 | 122.937 | 122.9324 | -0.23804 | 123.0652 | 123.0194 | 122.9874 | -0.24261
2543.6562 | 123.0194 | -122.7768 | 0.20142 | 0.068054 | 0.022751 | 0.006366 | 0.0093909 | -0.0062612 | -0.0071842 | -0.0073701 | 0.094375 | -0.014691 | -0.0024076 | -0.0032578 | 0.0030399 | -0.01123 | 0.09613 | 0.15564 | 0.11902 | 0.13275 | 0.30212 | 0.059509 | -0.10071 | 0.16022 | 0.18768 | 0.12817 | 0.24261 | 0.20599 | -0.032043 | -0.07782 | 122.8363 | 122.6761 | 0.10071 | 122.9324 | 122.9095 | 0.23346 | -0.10529 | 122.7448 | 122.699 | 0.041199 | 122.937 | 122.905 | 0.20599 | 0.004578 | 123.0789 | 122.8729 | 122.8958 | -0.30212 | 123.0194 | 122.9828 | 122.9645 | -0.27924
2545.3438 | 122.9507 | -122.7997 | 0.20142 | 0.1062 | 0.022965 | 0.0052978 | 0.0049047 | -0.0064748 | -0.0035526 | -0.0063019 | 0.1783 | -0.011059 | -0.0088162 | -0.0024032 | 0.0034671 | -0.011657 | 0.1236 | 0.15106 | 0.10986 | 0.10986 | 0.2243 | 0.018311 | -0.13275 | 0.16479 | 0.19226 | 0.082397 | 0.20142 | 0.16937 | -0.036621 | -0.11444 | 122.818 | 122.6669 | 0.022888 | 122.9507 | 122.9095 | 0.24261 | -0.07782 | 122.7631 | 122.6852 | 0 | 122.9645 | 122.8821 | 0.19684 | -0.032043 | 123.024 | 122.9233 | 122.9095 | -0.33417 | 123.0011 | 122.9691 | 122.9919 | -0.31586
2547.0781 | 123.1338 | -122.7539 | 0.15106 | -0.18372 | 0.029587 | 0.0055114 | 0.0089635 | -0.008611 | 0.0020016 | -0.0075837 | -0.23369 | -0.0091367 | -0.0034756 | -0.0017624 | 0.0045351 | -0.014435 | 0.14191 | 0.11444 | 0.086975 | 0.14191 | 0.3891 | 0.054932 | -0.086975 | 0.1236 | 0.16022 | 0.036621 | 0.29297 | 0.24719 | -0.032043 | -0.10071 | 122.8088 | 122.6669 | 0.23804 | 122.8683 | 122.8958 | 0.22888 | -0.009155 | 122.7219 | 122.6532 | 0.14191 | 122.8775 | 122.7905 | 0.13733 | 0.09613 | 123.143 | 122.8958 | 122.8409 | -0.23804 | 123.0469 | 123.0011 | 122.9141 | -0.25177
2548.8594 | 123.0011 | -122.818 | 0.17395 | -0.023499 | 0.028519 | 0.0035888 | 0.0014867 | -0.0062612 | 0.0030698 | -0.0058747 | -0.042954 | -0.0080685 | -0.00668 | 0.0012284 | 0.0075259 | -0.012939 | 0.1236 | 0.09613 | 0.036621 | 0.086975 | 0.28839 | 0.022888 | -0.14648 | 0.07782 | 0.086975 | -0.041199 | 0.22888 | 0.1831 | -0.09613 | -0.16479 | 122.8409 | 122.6715 | 0.11444 | 122.9141 | 122.905 | 0.23346 | -0.050354 | 122.7219 | 122.6532 | 0.054932 | 122.8958 | 122.7768 | 0.1236 | 0.009155 | 123.1064 | 122.9416 | 122.8546 | -0.32043 | 123.0469 | 123.0011 | 122.905 | -0.33874
2550.5469 | 123.1201 | -122.731 | 0.15106 | -0.21423 | 0.027237 | 0.0042298 | 0.0091773 | -0.0079702 | -0.00056178 | -0.0069427 | -0.20317 | -0.0089229 | -0.0024076 | -0.00090781 | 0.0045351 | -0.012726 | 0.12817 | 0.1236 | 0.086975 | 0.14648 | 0.37994 | 0.068665 | -0.086975 | 0.12817 | 0.16937 | 0.027466 | 0.28381 | 0.25635 | -0.032043 | -0.10071 | 122.7997 | 122.644 | 0.22888 | 122.8546 | 122.8775 | 0.23346 | -0.022888 | 122.699 | 122.6303 | 0.13275 | 122.8592 | 122.7585 | 0.12817 | 0.10529 | 123.111 | 122.8592 | 122.818 | -0.23804 | 123.0148 | 122.9874 | 122.9004 | -0.25177
2552.2344 | 123.143 | -122.7539 | 0.17395 | -0.23712 | 0.028946 | 0.0059388 | 0.0093909 | -0.008611 | -0.00163 | -0.0056611 | -0.19554 | -0.010632 | -0.0039028 | 0.0010148 | 0.0034671 | -0.01358 | 0.11444 | 0.15106 | 0.082397 | 0.15106 | 0.38452 | 0.07782 | -0.09613 | 0.10529 | 0.16022 | 0.036621 | 0.28839 | 0.2655 | -0.045776 | -0.091553 | 122.8317 | 122.6578 | 0.21057 | 122.905 | 122.905 | 0.24719 | -0.059509 | 122.7081 | 122.6624 | 0.11444 | 122.8592 | 122.7905 | 0.12817 | 0.091553 | 123.1384 | 122.8683 | 122.8363 | -0.27008 | 123.0423 | 123.0194 | 122.9141 | -0.2655
2554.0156 | 123.0377 | -122.7722 | 0.16937 | 0.19775 | 0.028305 | 0.002948 | 0.0044775 | -0.0083974 | 0.00071982 | -0.0058747 | 0.11726 | -0.011487 | -0.0062528 | 0.00080099 | 0.0049625 | -0.014435 | 0.068665 | 0.10071 | 0.068665 | 0.07782 | 0.20599 | -0.009155 | -0.17395 | 0.15106 | 0.17395 | 0.07782 | 0.16937 | 0.16479 | -0.068665 | -0.1236 | 122.7631 | 122.5983 | 0.036621 | 122.8729 | 122.85 | 0.25177 | -0.10071 | 122.7036 | 122.6486 | 0 | 122.9233 | 122.85 | 0.20142 | -0.004578 | 122.9782 | 122.8409 | 122.8409 | -0.34332 | 122.9416 | 122.937 | 122.9462 | -0.29297
2555.7656 | 123.0469 | -122.7905 | 0.20599 | 0.15961 | 0.025101 | 0.0027344 | 0.0025549 | -0.0077566 | 0.0013608 | -0.0063019 | 0.16304 | -0.010846 | -0.0081754 | -0.0017624 | 0.0058169 | -0.015289 | 0.07782 | 0.10529 | 0.068665 | 0.09613 | 0.21515 | -0.004578 | -0.17395 | 0.15106 | 0.1831 | 0.064087 | 0.16479 | 0.14648 | -0.068665 | -0.10986 | 122.7859 | 122.6166 | 0.009155 | 122.8958 | 122.8867 | 0.27008 | -0.12817 | 122.7219 | 122.6807 | -0.041199 | 122.9416 | 122.8546 | 0.17395 | -0.05951 | 123.0057 | 122.8683 | 122.8592 | -0.37994 | 122.9553 | 122.937 | 122.9736 | -0.31586
2557.5156 | 123.0423 | -122.7768 | 0.1831 | 0.090942 | 0.027237 | 0.0065796 | 0.0036231 | -0.0064748 | 0.0013608 | -0.0056611 | 0.12489 | -0.0082821 | -0.0056118 | -0.001976 | 0.0070987 | -0.01358 | 0.027466 | 0.032043 | -0.013733 | 0.022888 | 0.27466 | -0.013733 | -0.17853 | 0.07782 | 0.068665 | -0.013733 | 0.19226 | 0.16022 | -0.11444 | -0.15106 | 122.7631 | 122.5983 | 0.091553 | 122.8088 | 122.7997 | 0.20142 | -0.15564 | 122.6624 | 122.6257 | 0.009156 | 122.8546 | 122.7631 | 0.13733 | -0.022888 | 123.0515 | 122.8043 | 122.7631 | -0.36163 | 122.9691 | 122.937 | 122.8455 | -0.33417
2559.2031 | 123.0789 | -122.7264 | 0.15564 | -0.2066 | 0.02211 | 0.0072204 | 0.0031957 | -0.008611 | -0.0071842 | -0.0071563 | -0.11925 | -0.01405 | -0.0064664 | -0.0021896 | 0.0023989 | -0.012085 | 0.21973 | 0.29755 | 0.24719 | 0.23804 | 0.33417 | 0.10529 | -0.027466 | 0.2243 | 0.32501 | 0.17853 | 0.2655 | 0.24261 | 0.013733 | -0.045776 | 122.8317 | 122.699 | 0.17853 | 123.024 | 122.9645 | 0.2655 | 0.064087 | 122.7402 | 122.6807 | 0.10986 | 122.9507 | 122.905 | 0.2243 | 0.086975 | 123.0606 | 122.9462 | 122.9736 | -0.18311 | 122.9919 | 122.9691 | 123.0515 | -0.20142
2560.9688 | 123.0927 | -122.7493 | 0.18768 | -0.17609 | 0.026169 | 0.0067932 | 0.0076819 | -0.0079702 | -0.0031254 | -0.0060883 | -0.22606 | -0.0091367 | -0.00668 | 0.00016019 | 0.0049625 | -0.013366 | 0.16022 | 0.14191 | 0.09613 | 0.13733 | 0.37994 | 0.07782 | -0.073242 | 0.12817 | 0.1831 | 0.045776 | 0.31128 | 0.27924 | -0.013733 | -0.064087 | 122.8271 | 122.6761 | 0.19226 | 122.8912 | 122.8867 | 0.21057 | -0.027466 | 122.7356 | 122.6852 | 0.1236 | 122.8775 | 122.7951 | 0.10986 | 0.091553 | 123.1293 | 122.9095 | 122.8455 | -0.26092 | 123.0606 | 123.0286 | 122.9324 | -0.25177
2562.7344 | 123.111 | -122.7585 | 0.16479 | -0.16083 | 0.025742 | 0.006366 | 0.0074683 | -0.0081838 | -0.0065434 | -0.0075837 | -0.10399 | -0.013196 | -0.004971 | -0.0021896 | 0.00047633 | -0.013153 | 0.23804 | 0.28839 | 0.24261 | 0.23804 | 0.33875 | 0.10529 | -0.050354 | 0.24261 | 0.34332 | 0.21057 | 0.27008 | 0.2243 | 0.009155 | -0.027466 | 122.8638 | 122.7081 | 0.17395 | 123.0469 | 122.9965 | 0.28839 | 0.073242 | 122.7676 | 122.731 | 0.10529 | 123.0011 | 122.9691 | 0.23804 | 0.059509 | 123.0972 | 122.9965 | 123.0011 | -0.21515 | 123.0286 | 122.9828 | 123.1018 | -0.19226
2564.5 | 122.9919 | -122.7814 | 0.20142 | 0.15961 | 0.026169 | 0.0059388 | 0.0025549 | -0.0062612 | -0.00163 | -0.0071563 | 0.12489 | -0.010846 | -0.0079618 | -0.0026168 | 0.0049625 | -0.012512 | 0.13275 | 0.13733 | 0.11444 | 0.091553 | 0.19684 | 0 | -0.14191 | 0.17853 | 0.18768 | 0.091553 | 0.19226 | 0.16022 | -0.054932 | -0.1236 | 122.7814 | 122.6395 | -0.004578 | 122.9187 | 122.8729 | 0.23346 | -0.068665 | 122.7264 | 122.6578 | -0.009155 | 122.9599 | 122.8729 | 0.21515 | -0.041199 | 122.9782 | 122.9141 | 122.8958 | -0.34332 | 122.9736 | 122.9416 | 122.9691 | -0.32501
2566.1875 | 122.9828 | -122.7905 | 0.19226 | 0.12146 | 0.024887 | 0.0087158 | 0.0038367 | -0.0073294 | -0.0037662 | -0.0080109 | 0.11726 | -0.011487 | -0.007748 | -0.00069421 | 0.0036807 | -0.013794 | 0.13275 | 0.14191 | 0.11902 | 0.091553 | 0.24261 | 0.013733 | -0.13275 | 0.16937 | 0.19226 | 0.10071 | 0.21973 | 0.19684 | -0.027466 | -0.091553 | 122.8043 | 122.6578 | 0.050354 | 122.9324 | 122.8821 | 0.2243 | -0.05951 | 122.7631 | 122.699 | 0.027466 | 122.9599 | 122.8912 | 0.19226 | 0.004577 | 123.0331 | 122.9233 | 122.9095 | -0.32501 | 123.0103 | 122.9874 | 122.9828 | -0.28381
2567.9375 | 123.0743 | -122.7905 | 0.16022 | -0.22186 | 0.027237 | 0.0065796 | 0.0074683 | -0.0071158 | -0.00056178 | -0.0080109 | -0.21843 | -0.010205 | -0.0051846 | -0.0015488 | 0.0023989 | -0.01358 | 0.2243 | 0.17853 | 0.14191 | 0.17853 | 0.37994 | 0.10529 | -0.050354 | 0.1236 | 0.1831 | 0.059509 | 0.31586 | 0.27924 | -0.018311 | -0.054932 | 122.8958 | 122.7402 | 0.21973 | 122.9691 | 122.9691 | 0.22888 | 0.064087 | 122.7722 | 122.7356 | 0.15564 | 122.9141 | 122.85 | 0.11444 | 0.11902 | 123.1705 | 123.0148 | 122.9324 | -0.21057 | 123.1064 | 123.0698 | 122.9736 | -0.21515
2569.7031 | 123.1293 | -122.7402 | 0.15106 | -0.22949 | 0.025742 | 0.004657 | 0.0091773 | -0.0060476 | 0.00093342 | -0.0056611 | -0.24132 | -0.0091367 | -0.0053982 | -0.00090781 | 0.0062441 | -0.015503 | 0.17853 | 0.1236 | 0.086975 | 0.13733 | 0.39368 | 0.073242 | -0.091553 | 0.10071 | 0.16022 | 0.022888 | 0.28381 | 0.26093 | -0.041199 | -0.09613 | 122.8134 | 122.6486 | 0.24261 | 122.8638 | 122.8775 | 0.22888 | 0.027466 | 122.699 | 122.644 | 0.13275 | 122.8409 | 122.7631 | 0.11902 | 0.10986 | 123.1338 | 122.9187 | 122.8271 | -0.24261 | 123.024 | 123.0011 | 122.9004 | -0.24719
2571.4062 | 123.0057 | -122.7905 | 0.1831 | 0.068054 | 0.022751 | 0.0059388 | 0.0049047 | -0.007543 | -0.0046206 | -0.0084381 | 0.11726 | -0.011487 | -0.0047574 | -0.0038986 | 0.0041079 | -0.010803 | 0.15106 | 0.17395 | 0.11902 | 0.10986 | 0.2655 | 0.050354 | -0.1236 | 0.16022 | 0.20599 | 0.091553 | 0.19684 | 0.18768 | -0.041199 | -0.091553 | 122.8409 | 122.6669 | 0.082398 | 122.9645 | 122.9004 | 0.23346 | -0.032043 | 122.7493 | 122.699 | 0.013733 | 122.9507 | 122.8821 | 0.18311 | 0.004578 | 123.056 | 122.9416 | 122.9095 | -0.3067 | 122.9874 | 122.9782 | 122.9965 | -0.27466
2573.1406 | 123.1293 | -122.7676 | 0.16937 | -0.17609 | 0.030655 | 0.0050842 | 0.0093909 | -0.0083974 | 0.0028562 | -0.0056611 | -0.27184 | -0.010418 | -0.0017666 | -5.3406e-05 | 0.0015445 | -0.015716 | 0.16479 | 0.11902 | 0.073242 | 0.15564 | 0.36163 | 0.068665 | -0.10071 | 0.13275 | 0.15564 | 0.032043 | 0.28381 | 0.2243 | -0.050354 | -0.091553 | 122.8363 | 122.6669 | 0.19226 | 122.8867 | 122.9233 | 0.25635 | -0.004578 | 122.7173 | 122.6761 | 0.11444 | 122.9004 | 122.7997 | 0.1236 | 0.054931 | 123.1293 | 122.9324 | 122.8409 | -0.27008 | 123.0515 | 122.9919 | 122.9233 | -0.26093
2574.9062 | 123.111 | -122.7585 | 0.1831 | -0.031128 | 0.021683 | 0.0089294 | 0.0046911 | -0.008611 | -0.0037662 | -0.0073701 | -0.020065 | -0.012341 | -0.0071072 | 0.00037379 | 0.0011173 | -0.012298 | 0.15564 | 0.18768 | 0.15106 | 0.15106 | 0.29755 | 0.068665 | -0.082397 | 0.20599 | 0.26093 | 0.16937 | 0.25635 | 0.23804 | -0.009155 | -0.054932 | 122.8271 | 122.6761 | 0.11444 | 122.9462 | 122.9095 | 0.23346 | -0.027465 | 122.7493 | 122.7036 | 0.073243 | 122.9645 | 122.9279 | 0.22431 | 0.054932 | 123.056 | 122.9141 | 122.9095 | -0.2655 | 123.0148 | 122.9965 | 123.0194 | -0.23804
2576.6562 | 123.1201 | -122.7539 | 0.16479 | -0.16846 | 0.025314 | 0.0052978 | 0.0074683 | -0.0060476 | -0.0056888 | -0.0086517 | -0.042954 | -0.011487 | -0.0073208 | -0.0028306 | 0.0013309 | -0.014221 | 0.23346 | 0.27466 | 0.24261 | 0.21515 | 0.32959 | 0.10986 | -0.036621 | 0.25177 | 0.31586 | 0.20142 | 0.25177 | 0.2243 | 0.004578 | -0.032043 | 122.8638 | 122.7173 | 0.16479 | 123.0286 | 122.9691 | 0.25177 | 0.068664 | 122.7585 | 122.7219 | 0.086975 | 123.0057 | 122.9553 | 0.23346 | 0.059509 | 123.0835 | 122.9874 | 122.9965 | -0.20142 | 123.0057 | 122.9782 | 123.0698 | -0.19684
2578.3438 | 123.1018 | -122.7448 | 0.16479 | -0.099793 | 0.023819 | 0.0059388 | 0.0044775 | -0.0066884 | -0.0018436 | -0.0069427 | -0.16502 | -0.012555 | -0.0098844 | -0.0028306 | 0.0015445 | -0.015289 | 0.2655 | 0.27466 | 0.24719 | 0.22888 | 0.32044 | 0.10986 | -0.059509 | 0.27008 | 0.32959 | 0.20599 | 0.2655 | 0.25177 | 0.027466 | -0.022888 | 122.8546 | 122.6852 | 0.15564 | 123.0194 | 122.9736 | 0.28839 | 0.10071 | 122.7722 | 122.7219 | 0.10071 | 123.0148 | 122.9507 | 0.22888 | 0.086975 | 123.0652 | 123.0103 | 122.9919 | -0.2243 | 123.0103 | 122.9965 | 123.0743 | -0.18768
2580.0938 | 122.9965 | -122.7951 | 0.20142 | 0.14435 | 0.027237 | 0.0078614 | 0.0072547 | -0.0047658 | -0.0029118 | -0.0067291 | 0.102 | -0.010846 | -0.0051846 | -0.0013352 | 0.0038943 | -0.014007 | 0.14648 | 0.14191 | 0.12817 | 0.15564 | 0.23346 | 0.022888 | -0.11902 | 0.16022 | 0.16479 | 0.086975 | 0.21973 | 0.19684 | -0.032043 | -0.10071 | 122.818 | 122.6761 | 0.032043 | 122.937 | 122.9507 | 0.27466 | -0.054932 | 122.7631 | 122.6944 | 0.018311 | 122.9553 | 122.8821 | 0.18768 | -0.004578 | 123.0286 | 122.9416 | 122.9233 | -0.32044 | 123.0148 | 122.9919 | 122.9599 | -0.30212
2581.8594 | 123.0881 | -122.7585 | 0.16479 | -0.17609 | 0.025955 | 0.0065796 | 0.0061865 | -0.0062612 | -0.00077538 | -0.0071563 | -0.18791 | -0.010846 | -0.0073208 | -0.0021896 | 0.0011173 | -0.01593 | 0.2655 | 0.29755 | 0.25635 | 0.24261 | 0.35248 | 0.1236 | -0.027466 | 0.2655 | 0.31586 | 0.18768 | 0.27008 | 0.23346 | 0.032043 | -0.036621 | 122.8821 | 122.731 | 0.18768 | 123.056 | 123.0011 | 0.27008 | 0.10071 | 122.7905 | 122.7219 | 0.10529 | 123.024 | 122.9462 | 0.2243 | 0.068664 | 123.111 | 123.024 | 123.0148 | -0.19226 | 123.0286 | 122.9919 | 123.0743 | -0.20142
2583.5469 | 123.0835 | -122.7539 | 0.16937 | -0.16083 | 0.027664 | 0.0061524 | 0.0059729 | -0.0056204 | -0.00034818 | -0.0084381 | -0.24132 | -0.0117 | -0.0068936 | -0.0021896 | 0.0058169 | -0.016143 | 0.24719 | 0.23346 | 0.21057 | 0.22888 | 0.3479 | 0.086975 | -0.050354 | 0.20599 | 0.26093 | 0.10986 | 0.27466 | 0.2655 | 0.018311 | -0.041199 | 122.8409 | 122.7036 | 0.17853 | 122.9874 | 122.9828 | 0.27924 | 0.077819 | 122.7722 | 122.7127 | 0.10529 | 122.9599 | 122.8638 | 0.15106 | 0.09613 | 123.1018 | 123.0011 | 122.9645 | -0.21973 | 123.0286 | 123.0194 | 123.0148 | -0.21057
2585.25 | 123.1155 | -122.7493 | 0.17853 | -0.19135 | 0.028946 | 0.0042298 | 0.0051183 | -0.005834 | 0.003497 | -0.0065155 | -0.21843 | -0.0084957 | -0.0071072 | -0.0015488 | 0.0075259 | -0.014862 | 0.1831 | 0.1236 | 0.07782 | 0.12817 | 0.35706 | 0.054932 | -0.10986 | 0.12817 | 0.16479 | 0.022888 | 0.23804 | 0.20599 | -0.082397 | -0.12817 | 122.8043 | 122.6395 | 0.17853 | 122.8729 | 122.8775 | 0.23804 | 0.004577 | 122.6669 | 122.6212 | 0.059509 | 122.8775 | 122.7722 | 0.15106 | 0.027466 | 123.1064 | 122.9324 | 122.8271 | -0.28839 | 122.9874 | 122.9553 | 122.9141 | -0.3067
2587 | 123.0103 | -122.7768 | 0.18768 | 0.1062 | 0.028305 | 0.0061524 | 0.0029821 | -0.0069022 | 0.0020016 | -0.0056611 | 0.063858 | -0.0080685 | -0.008389 | -0.001976 | 0.0081667 | -0.014435 | 0.036621 | -0.013733 | -0.041199 | 0 | 0.25635 | -0.045776 | -0.19226 | 0.041199 | 0.045776 | -0.07782 | 0.20599 | 0.16479 | -0.11444 | -0.16022 | 122.731 | 122.5845 | 0.068665 | 122.7631 | 122.7768 | 0.19226 | -0.15106 | 122.6624 | 122.6166 | 0.018311 | 122.818 | 122.699 | 0.082397 | -0.022888 | 123.0331 | 122.8134 | 122.7356 | -0.37994 | 122.9828 | 122.9416 | 122.8226 | -0.3479
2588.7656 | 123.1567 | -122.7539 | 0.16022 | -0.21423 | 0.026596 | 0.0050842 | 0.0059729 | -0.009252 | 0.00093342 | -0.0037385 | -0.2108 | -0.010418 | -0.0073208 | 0.00080099 | 0.0070987 | -0.013794 | 0.16937 | 0.13275 | 0.082397 | 0.14191 | 0.36621 | 0.045776 | -0.11902 | 0.11444 | 0.16022 | 0.032043 | 0.25635 | 0.21515 | -0.064087 | -0.10986 | 122.7997 | 122.6349 | 0.20599 | 122.8867 | 122.8958 | 0.26093 | 0.009156 | 122.6898 | 122.644 | 0.096131 | 122.8683 | 122.7859 | 0.14191 | 0.054932 | 123.1201 | 122.9233 | 122.8363 | -0.27924 | 123.0103 | 122.9691 | 122.9141 | -0.27008
2590.5312 | 122.9919 | -122.8088 | 0.19684 | 0.075684 | 0.028092 | 0.0048706 | 0.0053321 | -0.005834 | 0.0024288 | -0.0043793 | 0.018082 | -0.0097775 | -0.0043302 | 0.00016019 | 0.0066715 | -0.015289 | 0.050354 | 0.004578 | -0.027466 | 0.032043 | 0.27008 | -0.041199 | -0.1831 | 0.032043 | 0.045776 | -0.07782 | 0.20599 | 0.18768 | -0.11902 | -0.16479 | 122.7676 | 122.6257 | 0.073243 | 122.8134 | 122.8409 | 0.21515 | -0.14648 | 122.6898 | 122.644 | 0.009156 | 122.8409 | 122.731 | 0.086975 | -0.009155 | 123.0789 | 122.8592 | 122.7814 | -0.37994 | 123.0148 | 122.9965 | 122.8546 | -0.36163
2592.2188 | 123.024 | -122.7905 | 0.17853 | 0.14435 | 0.031723 | 0.0035888 | 0.0051183 | -0.009252 | 0.0032834 | -0.0056611 | 0.102 | -0.0070003 | -0.006039 | -0.0024032 | 0.0068851 | -0.012085 | 0.018311 | -0.027466 | -0.041199 | 0.009155 | 0.23346 | -0.064087 | -0.21057 | 0.054932 | 0.064087 | -0.027466 | 0.21973 | 0.18768 | -0.082397 | -0.16937 | 122.7264 | 122.58 | 0.054931 | 122.7631 | 122.7997 | 0.21973 | -0.16022 | 122.7081 | 122.6212 | 0.041199 | 122.8455 | 122.7631 | 0.14191 | 0.009155 | 123.024 | 122.8088 | 122.7493 | -0.3891 | 123.0103 | 122.9782 | 122.8546 | -0.3479
2593.9219 | 122.9828 | -122.8043 | 0.20142 | 0.13672 | 0.02446 | 0.0035888 | 0.0055457 | -0.0098928 | -0.003339 | -0.0048065 | 0.17067 | -0.011059 | -0.0081754 | -0.0015488 | 0.00068993 | -0.011871 | 0.11902 | 0.14648 | 0.11444 | 0.10071 | 0.21057 | 0 | -0.14191 | 0.16022 | 0.18768 | 0.091553 | 0.17853 | 0.14191 | -0.064087 | -0.11444 | 122.8043 | 122.6624 | 0.009155 | 122.9507 | 122.905 | 0.24262 | -0.082397 | 122.7402 | 122.6898 | -0.022888 | 122.9645 | 122.8958 | 0.20599 | -0.059509 | 123.0148 | 122.9233 | 122.9187 | -0.34332 | 122.9828 | 122.9462 | 122.9919 | -0.31586
2595.6875 | 122.9919 | -122.7905 | 0.17853 | 0.17487 | 0.027451 | 0.0050842 | 0.0057593 | -0.0043386 | -0.0022708 | -0.0045929 | 0.20882 | -0.011273 | -0.0058254 | -0.001976 | 0.0034671 | -0.013153 | 0.10986 | 0.10986 | 0.086975 | 0.091553 | 0.19684 | -0.009155 | -0.13733 | 0.14191 | 0.19684 | 0.07782 | 0.16479 | 0.12817 | -0.082397 | -0.13275 | 122.7814 | 122.6532 | 0.01831 | 122.9004 | 122.8821 | 0.22888 | -0.068665 | 122.7081 | 122.6578 | -0.013733 | 122.9324 | 122.8683 | 0.21057 | -0.050354 | 122.9874 | 122.9004 | 122.8775 | -0.31586 | 122.9553 | 122.9187 | 122.9874 | -0.31128
2597.375 | 123.0515 | -122.8043 | 0.16937 | 0.1825 | 0.027878 | 0.0057252 | 0.0051183 | -0.0043386 | 0.00093342 | -0.0065155 | 0.14015 | -0.010846 | -0.0043302 | -0.00048061 | 0.0056033 | -0.013366 | 0.09613 | 0.054932 | 0.036621 | 0.064087 | 0.2243 | -0.004578 | -0.18768 | 0.14648 | 0.16937 | 0.068665 | 0.17395 | 0.12817 | -0.064087 | -0.10986 | 122.7997 | 122.6166 | 0.054931 | 122.8592 | 122.8683 | 0.25177 | -0.073243 | 122.7402 | 122.6944 | 0.004577 | 122.9507 | 122.8729 | 0.17853 | -0.041199 | 123.0286 | 122.9004 | 122.8409 | -0.35706 | 122.9782 | 122.9324 | 122.9736 | -0.27924
2599.0781 | 123.0377 | -122.7722 | 0.19684 | 0.014648 | 0.023605 | 0.0070068 | 0.0085363 | -0.0077566 | -0.0056888 | -0.0069427 | 0.102 | -0.0089229 | -0.0051846 | -0.00048061 | 0.00026273 | -0.012726 | 0.12817 | 0.13275 | 0.13733 | 0.14191 | 0.30212 | 0.059509 | -0.10986 | 0.15564 | 0.20142 | 0.11444 | 0.23346 | 0.21973 | -0.032043 | -0.068665 | 122.8317 | 122.6624 | 0.10529 | 122.905 | 122.9141 | 0.25177 | -0.068664 | 122.7402 | 122.7036 | 0.036621 | 122.9279 | 122.8867 | 0.18311 | 0.022889 | 123.0743 | 122.9004 | 122.9095 | -0.3067 | 123.0057 | 122.9919 | 122.9736 | -0.2655
2600.7656 | 123.0789 | -122.7859 | 0.1831 | -0.22186 | 0.024246 | 0.007434 | 0.0066137 | -0.0077566 | -0.002698 | -0.0069427 | -0.21843 | -0.013836 | -0.0053982 | -0.0030442 | 0.0036807 | -0.015503 | 0.22888 | 0.23346 | 0.20599 | 0.22888 | 0.33417 | 0.091553 | -0.064087 | 0.19226 | 0.26093 | 0.15106 | 0.29297 | 0.24719 | 0.009155 | -0.054932 | 122.8775 | 122.7219 | 0.15106 | 123.0194 | 123.0148 | 0.29297 | 0.045777 | 122.7951 | 122.731 | 0.10986 | 122.9782 | 122.937 | 0.20599 | 0.064087 | 123.1201 | 123.0148 | 122.9919 | -0.24719 | 123.0789 | 123.0331 | 123.0469 | -0.23804
2602.5156 | 123.1338 | -122.731 | 0.15106 | -0.11505 | 0.023392 | 0.008075 | 0.0089635 | -0.0056204 | -0.0037662 | -0.0067291 | -0.13451 | -0.012341 | -0.0043302 | -0.0026168 | 0.0011173 | -0.013153 | 0.23804 | 0.25177 | 0.21973 | 0.22888 | 0.34332 | 0.10986 | -0.050354 | 0.26093 | 0.34332 | 0.21973 | 0.25635 | 0.23346 | 0.022888 | -0.027466 | 122.8409 | 122.6807 | 0.19226 | 122.9828 | 122.9599 | 0.27924 | 0.086975 | 122.7539 | 122.7036 | 0.10529 | 122.9919 | 122.9507 | 0.24719 | 0.082397 | 123.0743 | 122.9691 | 122.9507 | -0.20142 | 122.9874 | 122.9645 | 123.0743 | -0.17853
2604.2031 | 123.0652 | -122.7768 | 0.1831 | -0.061646 | 0.028732 | 0.0070068 | 0.0040503 | -0.0083974 | 0.0039242 | -0.0048065 | -0.14214 | -0.010205 | -0.0039028 | -0.00090781 | 0.0066715 | -0.016998 | 0.18768 | 0.1236 | 0.073242 | 0.11444 | 0.30212 | 0.009155 | -0.14191 | 0.13733 | 0.15106 | 0.009155 | 0.22888 | 0.19226 | -0.073242 | -0.13275 | 122.7859 | 122.6349 | 0.11902 | 122.9004 | 122.8912 | 0.25635 | 0.004578 | 122.7036 | 122.644 | 0.045777 | 122.9141 | 122.7859 | 0.14191 | 0.009156 | 123.0789 | 122.9645 | 122.85 | -0.32501 | 123.0057 | 122.9691 | 122.9279 | -0.31586
2605.9531 | 123.0835 | -122.7676 | 0.17853 | -0.10742 | 0.029373 | 0.0050842 | 0.0061865 | -0.0062612 | 0.0013608 | -0.0045929 | -0.13451 | -0.010632 | -0.0053982 | 0.00037379 | 0.0056033 | -0.014007 | 0.15106 | 0.11902 | 0.07782 | 0.10529 | 0.3067 | 0.013733 | -0.15564 | 0.1236 | 0.15564 | 0 | 0.21515 | 0.1831 | -0.082397 | -0.13733 | 122.7814 | 122.612 | 0.12817 | 122.8867 | 122.8729 | 0.26093 | -0.027466 | 122.6852 | 122.6303 | 0.036621 | 122.8912 | 122.7676 | 0.13733 | 0.004577 | 123.0743 | 122.9187 | 122.8455 | -0.33417 | 122.9828 | 122.9507 | 122.9233 | -0.31586
2607.7188 | 123.1155 | -122.7402 | 0.1831 | -0.13031 | 0.027664 | 0.0050842 | 0.0074683 | -0.0073294 | 0.0011472 | -0.0035249 | -0.13451 | -0.0099911 | -0.0056118 | -0.0015488 | 0.0062441 | -0.013794 | 0.1236 | 0.14648 | 0.082397 | 0.10986 | 0.3067 | 0.045776 | -0.12817 | 0.12817 | 0.17395 | 0.022888 | 0.23346 | 0.19226 | -0.064087 | -0.11902 | 122.7859 | 122.612 | 0.1236 | 122.8867 | 122.85 | 0.23804 | -0.059509 | 122.6761 | 122.6212 | 0.050354 | 122.8683 | 122.7631 | 0.14191 | 0.009156 | 123.0469 | 122.8638 | 122.8226 | -0.31128 | 122.9736 | 122.9324 | 122.9141 | -0.30212
2609.4219 | 123.024 | -122.7859 | 0.17395 | 0.11383 | 0.024887 | 0.0035888 | 0.0029821 | -0.0066884 | -0.0024844 | -0.0067291 | 0.20882 | -0.010632 | -0.0028348 | -0.0015488 | 0.0047489 | -0.013153 | 0.091553 | 0.14648 | 0.10529 | 0.086975 | 0.21515 | -0.004578 | -0.16479 | 0.13733 | 0.17395 | 0.059509 | 0.13733 | 0.086975 | -0.068665 | -0.15106 | 122.7814 | 122.6212 | 0.041199 | 122.9324 | 122.8729 | 0.25177 | -0.082397 | 122.7173 | 122.6349 | -0.036621 | 122.9233 | 122.8455 | 0.21057 | -0.086975 | 123.0011 | 122.8775 | 122.8912 | -0.33874 | 122.9233 | 122.8729 | 122.9599 | -0.32501
2611.1719 | 123.0652 | -122.7905 | 0.17395 | -0.054016 | 0.02916 | 0.0040162 | 0.0098181 | -0.008611 | 0.00071982 | -0.0077973 | -0.10399 | -0.0093503 | -0.0024076 | 0.0020828 | 0.0051761 | -0.014648 | 0.11902 | 0.13733 | 0.082397 | 0.10986 | 0.30212 | 0.004578 | -0.14191 | 0.1236 | 0.15106 | 0 | 0.20599 | 0.19684 | -0.059509 | -0.14191 | 122.7951 | 122.6486 | 0.12817 | 122.9279 | 122.9004 | 0.25177 | -0.054931 | 122.731 | 122.6486 | 0.032044 | 122.9141 | 122.7905 | 0.14191 | 0.022888 | 123.0927 | 122.9095 | 122.8729 | -0.31586 | 122.9965 | 122.9874 | 122.9416 | -0.31586
2612.9219 | 123.0377 | -122.8043 | 0.18768 | 0.13672 | 0.027664 | 0.0050842 | 0.0025549 | -0.0060476 | -0.00056178 | -0.0063019 | 0.10963 | -0.0076413 | -0.0043302 | -5.3406e-05 | 0.0038943 | -0.013794 | 0.004578 | 0.009155 | -0.054932 | 0.004578 | 0.24719 | -0.045776 | -0.21057 | 0.054932 | 0.054932 | -0.041199 | 0.20599 | 0.16479 | -0.10071 | -0.17853 | 122.7585 | 122.5937 | 0.059509 | 122.8134 | 122.8088 | 0.21515 | -0.1831 | 122.7036 | 122.6257 | 0.018311 | 122.8592 | 122.7631 | 0.13733 | -0.022888 | 123.0515 | 122.8088 | 122.7493 | -0.39825 | 123.0103 | 122.9691 | 122.8592 | -0.36621
2614.6875 | 123.0148 | -122.8088 | 0.20599 | 0.068054 | 0.030441 | 0.0067932 | 0.0040503 | -0.0054068 | 0.0030698 | -0.0052337 | 0.094375 | -0.0097775 | -0.0056118 | 0.00037379 | 0.0051761 | -0.01123 | 0.004578 | -0.050354 | -0.050354 | -0.009155 | 0.27466 | -0.027466 | -0.19684 | 0.018311 | 0.027466 | -0.064087 | 0.21515 | 0.17853 | -0.11902 | -0.16937 | 122.7814 | 122.612 | 0.068664 | 122.7585 | 122.7997 | 0.18768 | -0.20142 | 122.6898 | 122.6395 | 0.009155 | 122.8271 | 122.7448 | 0.10529 | -0.027466 | 123.0835 | 122.8134 | 122.7585 | -0.40283 | 123.024 | 122.9874 | 122.8363 | -0.37537
2616.375 | 122.9782 | -122.7997 | 0.20599 | 0.1825 | 0.025955 | 0.0035888 | 0.0051183 | -0.0083974 | -0.0059024 | -0.0063019 | 0.18593 | -0.0117 | -0.0064664 | -0.003685 | 0.0045351 | -0.011871 | 0.10986 | 0.14648 | 0.11902 | 0.091553 | 0.19226 | 0.004578 | -0.16479 | 0.16479 | 0.20599 | 0.091553 | 0.18768 | 0.12817 | -0.082397 | -0.12817 | 122.8043 | 122.6349 | -0.013733 | 122.9462 | 122.8912 | 0.25635 | -0.096131 | 122.7173 | 122.6715 | -0.018311 | 122.9645 | 122.8912 | 0.21973 | -0.07782 | 122.9919 | 122.9095 | 122.9187 | -0.37079 | 122.9874 | 122.9279 | 123.0057 | -0.33417
2618.125 | 123.0743 | -122.7768 | 0.16937 | -0.084534 | 0.030014 | 0.0070068 | 0.0070409 | -0.0077566 | 0.0039242 | -0.0071563 | -0.11162 | -0.0078549 | -0.0073208 | -0.0026168 | 0.0066715 | -0.013366 | 0.13733 | 0.11444 | 0.068665 | 0.09613 | 0.3067 | 0.027466 | -0.15106 | 0.11444 | 0.16022 | -0.004578 | 0.2243 | 0.20142 | -0.054932 | -0.13733 | 122.8043 | 122.6257 | 0.13733 | 122.8912 | 122.8729 | 0.24719 | -0.032044 | 122.7219 | 122.6395 | 0.054931 | 122.8912 | 122.7722 | 0.13275 | 0.032043 | 123.0835 | 122.9141 | 122.8455 | -0.32044 | 123.0011 | 122.9782 | 122.937 | -0.3067
2619.875 | 123.0515 | -122.7859 | 0.19226 | 0.12146 | 0.029373 | 0.0057252 | 0.0064001 | -0.007543 | -0.00056178 | -0.0075837 | 0.079117 | -0.0087093 | -0.0071072 | -0.00048061 | 0.0051761 | -0.011871 | 0.013733 | -0.027466 | -0.036621 | 0 | 0.26093 | -0.041199 | -0.19226 | 0.041199 | 0.054932 | -0.045776 | 0.21057 | 0.17395 | -0.10529 | -0.16022 | 122.7448 | 122.5937 | 0.068664 | 122.7585 | 122.7859 | 0.19226 | -0.17853 | 122.6807 | 122.6257 | 0.01831 | 122.8271 | 122.7402 | 0.11444 | -0.018311 | 123.0469 | 122.7997 | 122.7493 | -0.38452 | 122.9965 | 122.9599 | 122.8409 | -0.35248
2621.5625 | 123.1293 | -122.7676 | 0.15564 | -0.13031 | 0.02916 | 0.006366 | 0.0076819 | -0.0051932 | 0.001788 | -0.0060883 | -0.12688 | -0.0080685 | -0.0030484 | -0.00048061 | 0.0064577 | -0.013366 | 0.1236 | 0.12817 | 0.07782 | 0.14648 | 0.33417 | 0.027466 | -0.12817 | 0.11444 | 0.16022 | 0.022888 | 0.2243 | 0.20142 | -0.054932 | -0.12817 | 122.7951 | 122.6395 | 0.17853 | 122.8958 | 122.9141 | 0.27466 | -0.032044 | 122.7127 | 122.6395 | 0.068664 | 122.8821 | 122.7905 | 0.15106 | 0.045776 | 123.1018 | 122.8912 | 122.8455 | -0.28381 | 122.9919 | 122.9691 | 122.9279 | -0.28381
2623.25 | 123.1338 | -122.7585 | 0.16937 | -0.17609 | 0.030869 | 0.0048706 | 0.0096045 | -0.005834 | -0.00056178 | -0.0075837 | -0.17265 | -0.012127 | -0.0030484 | 0.00037379 | 0.0026125 | -0.014221 | 0.1236 | 0.14191 | 0.091553 | 0.13733 | 0.35706 | 0.064087 | -0.10529 | 0.09613 | 0.16022 | 0.027466 | 0.25177 | 0.21515 | -0.073242 | -0.1236 | 122.8226 | 122.6532 | 0.18768 | 122.9004 | 122.8958 | 0.24262 | -0.045777 | 122.6852 | 122.6349 | 0.082397 | 122.8546 | 122.7859 | 0.15106 | 0.045776 | 123.1155 | 122.8821 | 122.85 | -0.27466 | 123.0103 | 122.9736 | 122.9187 | -0.29297
2625 | 123.0698 | -122.7905 | 0.1831 | -0.23712 | 0.028305 | 0.0067932 | 0.0089635 | -0.0079702 | -0.0037662 | -0.0075837 | -0.18028 | -0.0117 | -0.0043302 | -0.00026701 | -0.00080527 | -0.01358 | 0.19226 | 0.24261 | 0.20142 | 0.21057 | 0.33417 | 0.091553 | -0.050354 | 0.15564 | 0.24719 | 0.11902 | 0.28381 | 0.25635 | 0.013733 | -0.054932 | 122.8821 | 122.7402 | 0.15106 | 123.0331 | 123.0011 | 0.26093 | 0.009156 | 122.8043 | 122.7356 | 0.10071 | 122.9462 | 122.9095 | 0.17395 | 0.073243 | 123.1247 | 122.9828 | 122.9919 | -0.23346 | 123.0743 | 123.0469 | 123.0377 | -0.23804
2626.6875 | 123.0515 | -122.7905 | 0.16479 | 0.029907 | 0.024033 | 0.0061524 | 0.0085363 | -0.0066884 | -0.0076114 | -0.0067291 | 0.086746 | -0.014477 | -0.0028348 | -0.0011216 | 0.00047633 | -0.011871 | 0.086975 | 0.15564 | 0.13275 | 0.14648 | 0.31586 | 0.068665 | -0.09613 | 0.13733 | 0.21057 | 0.12817 | 0.24719 | 0.21973 | -0.018311 | -0.082397 | 122.8592 | 122.6944 | 0.15106 | 122.9462 | 122.937 | 0.24261 | -0.07782 | 122.7722 | 122.7081 | 0.082397 | 122.9279 | 122.9187 | 0.21057 | 0.054932 | 123.1064 | 122.8775 | 122.9233 | -0.26092 | 123.0377 | 123.0103 | 123.0011 | -0.24719
2628.3906 | 123.1064 | -122.7631 | 0.16022 | -0.14557 | 0.024033 | 0.0061524 | 0.0081091 | -0.007543 | -0.0039798 | -0.0099335 | -0.081101 | -0.012768 | -0.0056118 | -0.0015488 | 0.00090353 | -0.014648 | 0.21057 | 0.28381 | 0.23346 | 0.21057 | 0.32501 | 0.10071 | -0.064087 | 0.23804 | 0.32959 | 0.19684 | 0.25635 | 0.23804 | 0.022888 | -0.041199 | 122.8638 | 122.699 | 0.1648 | 123.0469 | 122.9736 | 0.27466 | 0.050354 | 122.7859 | 122.7219 | 0.096131 | 123.0011 | 122.9599 | 0.23804 | 0.07782 | 123.0881 | 122.9736 | 122.9965 | -0.2243 | 123.0194 | 123.0011 | 123.0927 | -0.20142
2630.1406 | 123.0057 | -122.7951 | 0.17853 | 0.15961 | 0.025101 | 0.0055114 | 0.0012731 | -0.0039114 | 0.00093342 | -0.0080109 | 0.18593 | -0.010846 | -0.0071072 | -0.0013352 | 0.0062441 | -0.013794 | 0.10986 | 0.11902 | 0.086975 | 0.082397 | 0.19226 | -0.004578 | -0.14191 | 0.14648 | 0.17395 | 0.054932 | 0.15564 | 0.13275 | -0.091553 | -0.15106 | 122.7905 | 122.6532 | 0.013733 | 122.9141 | 122.8775 | 0.2243 | -0.068665 | 122.7036 | 122.644 | -0.022888 | 122.9416 | 122.85 | 0.20599 | -0.045777 | 122.9874 | 122.905 | 122.8821 | -0.32044 | 122.9507 | 122.9279 | 122.9691 | -0.32959
2631.8281 | 122.9782 | -122.8043 | 0.20599 | 0.11383 | 0.027023 | 0.004657 | 0.0029821 | -0.0062612 | -0.0012028 | -0.0067291 | 0.1783 | -0.011059 | -0.0068936 | -0.0024032 | 0.0058169 | -0.011017 | 0.14191 | 0.14648 | 0.1236 | 0.09613 | 0.21973 | 0.004578 | -0.14191 | 0.15106 | 0.16937 | 0.073242 | 0.1831 | 0.14648 | -0.068665 | -0.1236 | 122.8088 | 122.6624 | 0.013733 | 122.9507 | 122.9004 | 0.23804 | -0.064087 | 122.7356 | 122.6807 | -0.022889 | 122.9553 | 122.8775 | 0.19684 | -0.05951 | 123.024 | 122.9462 | 122.9279 | -0.3479 | 122.9874 | 122.9507 | 122.9736 | -0.32959
2633.5781 | 122.9736 | -122.7859 | 0.17853 | 0.1062 | 0.025101 | 0.0050842 | 0.0070409 | -0.0071158 | -0.0022708 | -0.0065155 | 0.1783 | -0.011059 | -0.0086026 | -0.00026701 | 0.0051761 | -0.014648 | 0.13275 | 0.12817 | 0.11444 | 0.10071 | 0.24261 | 0.018311 | -0.15564 | 0.17395 | 0.16937 | 0.073242 | 0.1831 | 0.14648 | -0.064087 | -0.11444 | 122.8043 | 122.6303 | 0.064087 | 122.9141 | 122.8867 | 0.25635 | -0.045777 | 122.7219 | 122.6715 | 0.004577 | 122.9599 | 122.8592 | 0.18768 | -0.032044 | 123.0286 | 122.9187 | 122.9004 | -0.33417 | 122.9691 | 122.9324 | 122.9553 | -0.29297
2635.2656 | 123.0881 | -122.7539 | 0.1831 | -0.2066 | 0.028092 | 0.0050842 | 0.0096045 | -0.008611 | 7.902e-05 | -0.0075837 | -0.26421 | -0.012127 | -0.0028348 | -0.0028306 | 0.0041079 | -0.013153 | 0.17395 | 0.14648 | 0.11902 | 0.15106 | 0.39368 | 0.082397 | -0.086975 | 0.12817 | 0.17395 | 0.032043 | 0.32501 | 0.28381 | -0.041199 | -0.091553 | 122.8363 | 122.6669 | 0.21057 | 122.9004 | 122.905 | 0.23804 | -0.009155 | 122.7127 | 122.6624 | 0.14191 | 122.8821 | 122.7859 | 0.1236 | 0.10071 | 123.1476 | 122.9279 | 122.8729 | -0.27008 | 123.0789 | 123.0377 | 122.9279 | -0.27466
2637.0156 | 123.1384 | -122.7859 | 0.16937 | -0.2066 | 0.027451 | 0.0044434 | 0.0091773 | -0.0096792 | 0.00050622 | -0.0065155 | -0.23369 | -0.0117 | -0.0028348 | -0.0011216 | 0.0038943 | -0.015503 | 0.16022 | 0.10986 | 0.07782 | 0.13733 | 0.38452 | 0.064087 | -0.09613 | 0.11902 | 0.16022 | 0.022888 | 0.27924 | 0.24719 | -0.054932 | -0.10529 | 122.85 | 122.6898 | 0.21515 | 122.8958 | 122.9233 | 0.23346 | -0.009156 | 122.731 | 122.6807 | 0.10986 | 122.905 | 122.8088 | 0.12817 | 0.077819 | 123.1705 | 122.9462 | 122.8638 | -0.2655 | 123.0652 | 123.0331 | 122.9462 | -0.27466
2638.7656 | 123.1567 | -122.7585 | 0.16022 | -0.19135 | 0.0298 | 0.0050842 | 0.010032 | -0.0051932 | 0.00050622 | -0.0069427 | -0.23369 | -0.010205 | -0.0045438 | -0.00026701 | 0.0032535 | -0.016143 | 0.14191 | 0.1236 | 0.09613 | 0.12817 | 0.36621 | 0.054932 | -0.091553 | 0.11444 | 0.18768 | 0.041199 | 0.28381 | 0.24261 | -0.045776 | -0.09613 | 122.8134 | 122.6669 | 0.20599 | 122.8821 | 122.8867 | 0.21973 | -0.01831 | 122.7127 | 122.6624 | 0.1236 | 122.8729 | 122.7997 | 0.13733 | 0.082398 | 123.1247 | 122.9004 | 122.8546 | -0.25177 | 123.0423 | 123.0011 | 122.9462 | -0.25635
2640.5156 | 123.0103 | -122.8043 | 0.19684 | 0.068054 | 0.028519 | 0.0059388 | 0.0025549 | -0.0071158 | 0.0028562 | -0.0056611 | 0.010452 | -0.0089229 | -0.0058254 | -0.00069421 | 0.0070987 | -0.013366 | 0.027466 | 0 | -0.041199 | 0.009155 | 0.27466 | -0.041199 | -0.19226 | 0.036621 | 0.041199 | -0.07782 | 0.21973 | 0.16479 | -0.1236 | -0.15564 | 122.7631 | 122.612 | 0.07782 | 122.8043 | 122.8134 | 0.20142 | -0.16937 | 122.6807 | 122.6486 | 0.022889 | 122.8409 | 122.7264 | 0.07782 | -0.032043 | 123.0789 | 122.8317 | 122.7631 | -0.3891 | 123.024 | 122.9691 | 122.8455 | -0.35248
2642.2031 | 123.0469 | -122.7859 | 0.19226 | 0.12909 | 0.030228 | 0.0038024 | 0.0031957 | -0.0083974 | 0.00029262 | -0.0043793 | 0.11726 | -0.0089229 | -0.0058254 | -0.001976 | 0.0077395 | -0.011871 | 0.022888 | -0.009155 | -0.045776 | 0.009155 | 0.26093 | -0.032043 | -0.20142 | 0.032043 | 0.027466 | -0.064087 | 0.20599 | 0.17853 | -0.11444 | -0.1831 | 122.7539 | 122.5845 | 0.068664 | 122.7768 | 122.7951 | 0.21057 | -0.16937 | 122.6715 | 122.6028 | 0.013733 | 122.818 | 122.7219 | 0.11902 | -0.013733 | 123.0469 | 122.8088 | 122.7402 | -0.39368 | 122.9919 | 122.9645 | 122.8134 | -0.37537
2643.9531 | 123.0423 | -122.7997 | 0.18768 | 0.083313 | 0.026596 | 0.0065796 | 0.0021277 | -0.0060476 | 0.00050622 | -0.0052337 | 0.1783 | -0.010846 | -0.0045438 | -0.0030442 | 0.0045351 | -0.012939 | 0.013733 | 0.018311 | -0.018311 | 0.022888 | 0.23346 | -0.041199 | -0.20142 | 0.082397 | 0.091553 | -0.009155 | 0.16937 | 0.14191 | -0.09613 | -0.14648 | 122.7585 | 122.5983 | 0.045776 | 122.818 | 122.8226 | 0.2243 | -0.17395 | 122.7036 | 122.6532 | -0.01831 | 122.8821 | 122.7905 | 0.13733 | -0.045776 | 123.0331 | 122.8134 | 122.7814 | -0.3891 | 122.9691 | 122.9416 | 122.8912 | -0.33417
2645.7031 | 123.0469 | -122.7768 | 0.1831 | 0.12909 | 0.028732 | 0.0055114 | 0.0036231 | -0.0066884 | -0.00013458 | -0.0077973 | 0.1783 | -0.0093503 | -0.007748 | -0.0024032 | 0.0058169 | -0.015075 | 0.032043 | 0.018311 | -0.013733 | 0.009155 | 0.24719 | -0.050354 | -0.19226 | 0.086975 | 0.10071 | 0.009155 | 0.17395 | 0.16022 | -0.10529 | -0.16479 | 122.7264 | 122.5845 | 0.064087 | 122.7951 | 122.7859 | 0.20142 | -0.15106 | 122.6715 | 122.612 | -0.009155 | 122.8638 | 122.7859 | 0.17395 | -0.022888 | 123.024 | 122.8088 | 122.7631 | -0.37537 | 122.9507 | 122.937 | 122.8775 | -0.3479
2647.3906 | 123.1293 | -122.7448 | 0.14648 | -0.099793 | 0.022324 | 0.006366 | 0.0042639 | -0.0069022 | -0.0080386 | -0.0077973 | -0.050583 | -0.010632 | -0.0079618 | -0.0028306 | 0.00090353 | -0.01123 | 0.16937 | 0.2243 | 0.20142 | 0.1831 | 0.33417 | 0.091553 | -0.068665 | 0.23346 | 0.31128 | 0.19684 | 0.24719 | 0.22888 | 0.018311 | -0.041199 | 122.8363 | 122.6761 | 0.18768 | 122.9691 | 122.9279 | 0.25177 | 0.022889 | 122.7631 | 122.7036 | 0.10071 | 122.9782 | 122.9416 | 0.23804 | 0.082398 | 123.0789 | 122.9141 | 122.9462 | -0.21515 | 122.9919 | 122.9736 | 123.056 | -0.18768
2649.1406 | 123.0927 | -122.7676 | 0.1831 | -0.12268 | 0.028305 | 0.0059388 | 0.0051183 | -0.0066884 | 0.0028562 | -0.0048065 | -0.14214 | -0.0074277 | -0.007748 | -0.00090781 | 0.0077395 | -0.012512 | 0.16937 | 0.10529 | 0.059509 | 0.10529 | 0.29297 | 0.004578 | -0.13275 | 0.12817 | 0.15106 | 0.004578 | 0.21057 | 0.19226 | -0.082397 | -0.12817 | 122.7722 | 122.6349 | 0.10986 | 122.8729 | 122.8729 | 0.23804 | -0.013732 | 122.6852 | 122.6395 | 0.027466 | 122.8958 | 122.7722 | 0.13275 | 0.009156 | 123.0606 | 122.937 | 122.8271 | -0.31586 | 122.9782 | 122.9599 | 122.9187 | -0.31128
2650.9062 | 123.1155 | -122.7631 | 0.15564 | 0.0070193 | 0.02446 | 0.0082886 | 0.0068273 | -0.008611 | -0.0080386 | -0.0095063 | 0.03334 | -0.012127 | -0.0068936 | -0.0024032 | -0.00037807 | -0.012939 | 0.12817 | 0.13733 | 0.15106 | 0.13275 | 0.29755 | 0.050354 | -0.09613 | 0.16937 | 0.24719 | 0.14648 | 0.24719 | 0.21057 | -0.013733 | -0.086975 | 122.8134 | 122.6669 | 0.14191 | 122.9004 | 122.8958 | 0.22888 | -0.027466 | 122.7493 | 122.6761 | 0.091552 | 122.9324 | 122.9095 | 0.23346 | 0.054931 | 123.0606 | 122.8912 | 122.9141 | -0.25177 | 123.0103 | 122.9736 | 123.0103 | -0.24261
2652.6094 | 123.1522 | -122.7585 | 0.15564 | -0.1532 | 0.027237 | 0.006366 | 0.0087499 | -0.0064748 | 0.0024288 | -0.0054475 | -0.22606 | -0.0089229 | -0.0053982 | -0.0030442 | 0.0068851 | -0.014221 | 0.13733 | 0.091553 | 0.068665 | 0.13733 | 0.37079 | 0.059509 | -0.09613 | 0.11902 | 0.16937 | 0.018311 | 0.26093 | 0.24719 | -0.045776 | -0.086975 | 122.818 | 122.6624 | 0.21515 | 122.85 | 122.8958 | 0.23346 | -0.018311 | 122.7127 | 122.6715 | 0.10529 | 122.8775 | 122.7768 | 0.10529 | 0.091552 | 123.1293 | 122.8958 | 122.8271 | -0.25177 | 123.0194 | 123.0057 | 122.9279 | -0.24261
2654.2969 | 123.143 | -122.7814 | 0.16022 | -0.18372 | 0.031082 | 0.0048706 | 0.0078955 | -0.007543 | 0.0020016 | -0.0067291 | -0.11925 | -0.0099911 | -0.0034756 | -0.001976 | 0.0053897 | -0.016143 | 0.15564 | 0.11902 | 0.086975 | 0.12817 | 0.34332 | 0.036621 | -0.11902 | 0.10529 | 0.16479 | 0.009155 | 0.23804 | 0.2243 | -0.07782 | -0.1236 | 122.818 | 122.6624 | 0.18311 | 122.9004 | 122.9095 | 0.24719 | -0.004577 | 122.7036 | 122.6578 | 0.07782 | 122.8867 | 122.7905 | 0.13275 | 0.064087 | 123.1247 | 122.937 | 122.8683 | -0.27924 | 123.0194 | 123.0057 | 122.9462 | -0.28381
2656.0625 | 123.111 | -122.7814 | 0.1831 | -0.24475 | 0.027878 | 0.0059388 | 0.010032 | -0.0077566 | -0.0037662 | -0.0058747 | -0.22606 | -0.011273 | -0.0026212 | -0.0013352 | 0.0013309 | -0.012298 | 0.14648 | 0.12817 | 0.10529 | 0.13275 | 0.39368 | 0.059509 | -0.09613 | 0.10986 | 0.17853 | 0.059509 | 0.29755 | 0.2655 | -0.041199 | -0.073242 | 122.8409 | 122.6852 | 0.21057 | 122.9095 | 122.9141 | 0.22888 | -0.036621 | 122.7402 | 122.7081 | 0.11444 | 122.8912 | 122.8409 | 0.13275 | 0.082398 | 123.175 | 122.9279 | 122.8867 | -0.27924 | 123.0789 | 123.0469 | 122.9599 | -0.25635
2657.8125 | 123.0469 | -122.7905 | 0.20599 | 0.12146 | 0.027664 | 0.0055114 | 0.0042639 | -0.0081838 | 0.001788 | -0.0065155 | 0.079117 | -0.0087093 | -0.0056118 | -0.00026701 | 0.0064577 | -0.014862 | 0.022888 | -0.018311 | -0.050354 | 0.004578 | 0.26093 | -0.050354 | -0.20599 | 0.045776 | 0.036621 | -0.064087 | 0.19226 | 0.16479 | -0.1236 | -0.15564 | 122.7402 | 122.5845 | 0.054931 | 122.7722 | 122.7951 | 0.21057 | -0.18311 | 122.6669 | 122.6349 | -0.013733 | 122.8363 | 122.7264 | 0.091553 | -0.041199 | 123.0515 | 122.8134 | 122.7402 | -0.41199 | 122.9828 | 122.9553 | 122.8271 | -0.36163
2659.5 | 123.0698 | -122.8134 | 0.17853 | 0.083313 | 0.028519 | 0.0052978 | 0.0055457 | -0.0098928 | -0.00034818 | -0.0073701 | 0.10963 | -0.012768 | -0.0056118 | -0.00069421 | 0.0058169 | -0.014007 | 0.027466 | 0.009155 | -0.022888 | 0.018311 | 0.27008 | -0.050354 | -0.20599 | 0.07782 | 0.059509 | -0.045776 | 0.21515 | 0.16022 | -0.09613 | -0.15106 | 122.7631 | 122.6074 | 0.091553 | 122.8226 | 122.8317 | 0.22431 | -0.15106 | 122.7173 | 122.6624 | 0.036621 | 122.8912 | 122.7676 | 0.10529 | -0.018311 | 123.0835 | 122.8409 | 122.7905 | -0.38452 | 123.0286 | 122.9736 | 122.8729 | -0.32959
2661.1875 | 123.1155 | -122.7814 | 0.16937 | -0.023499 | 0.025314 | 0.0076478 | 0.0051183 | -0.0060476 | -0.0088932 | -0.0082245 | 0.071487 | -0.013409 | -0.0068936 | -0.0024032 | 0.0021853 | -0.010376 | 0.1236 | 0.17395 | 0.16937 | 0.15106 | 0.32044 | 0.054932 | -0.091553 | 0.17395 | 0.24261 | 0.15564 | 0.25177 | 0.21973 | -0.004578 | -0.059509 | 122.8363 | 122.6898 | 0.15106 | 122.9553 | 122.9324 | 0.24261 | -0.045777 | 122.7768 | 122.7219 | 0.082397 | 122.9553 | 122.937 | 0.21515 | 0.050354 | 123.1018 | 122.905 | 122.9507 | -0.26093 | 123.0331 | 123.0011 | 123.024 | -0.22888
2662.9375 | 123.0515 | -122.8043 | 0.17853 | 0.16724 | 0.02681 | 0.004657 | 0.0036231 | -0.0096792 | 0.00029262 | -0.0073701 | 0.16304 | -0.0084957 | -0.00668 | -0.0015488 | 0.0060305 | -0.014221 | 0.064087 | 0.013733 | -0.013733 | 0.027466 | 0.23346 | -0.041199 | -0.17853 | 0.11902 | 0.1236 | 0.018311 | 0.17853 | 0.15106 | -0.09613 | -0.13733 | 122.7631 | 122.6257 | 0.054931 | 122.818 | 122.8317 | 0.20599 | -0.11444 | 122.7081 | 122.6669 | 0 | 122.9233 | 122.8226 | 0.15564 | -0.027466 | 123.0377 | 122.8683 | 122.7905 | -0.35706 | 122.9828 | 122.9553 | 122.9279 | -0.31586
2664.625 | 123.0194 | -122.8088 | 0.20599 | 0.052795 | 0.022751 | 0.007434 | 0.0038367 | -0.0069022 | -0.0046206 | -0.0069427 | 0.086746 | -0.012127 | -0.0092434 | -0.0017624 | 0.0047489 | -0.011017 | 0.13275 | 0.1236 | 0.12817 | 0.11902 | 0.29755 | 0.050354 | -0.11444 | 0.14648 | 0.17395 | 0.09613 | 0.21515 | 0.20599 | -0.018311 | -0.073242 | 122.8592 | 122.6944 | 0.091552 | 122.9324 | 122.9279 | 0.23346 | -0.073243 | 122.7905 | 122.7356 | 0.009155 | 122.9553 | 122.905 | 0.16937 | 0 | 123.1064 | 122.9416 | 122.937 | -0.32044 | 123.024 | 123.0148 | 122.9828 | -0.27924
2666.3125 | 123.1338 | -122.7814 | 0.16937 | -0.13794 | 0.030655 | 0.0042298 | 0.0096045 | -0.0069022 | 0.0020016 | -0.0060883 | -0.17265 | -0.0093503 | -0.0056118 | 0.00016019 | 0.0047489 | -0.015716 | 0.15564 | 0.11902 | 0.07782 | 0.13275 | 0.33417 | 0.032043 | -0.13733 | 0.11444 | 0.15106 | 0 | 0.25177 | 0.19226 | -0.059509 | -0.1236 | 122.8134 | 122.644 | 0.16479 | 122.9004 | 122.9141 | 0.27008 | -0.013733 | 122.7219 | 122.6578 | 0.082397 | 122.8958 | 122.7814 | 0.1236 | 0.022888 | 123.1155 | 122.937 | 122.8592 | -0.3067 | 123.0331 | 122.9736 | 122.9324 | -0.29297
2668.0625 | 123.0789 | -122.7722 | 0.16937 | -0.19135 | 0.028519 | 0.0059388 | 0.010245 | -0.0071158 | -0.0046206 | -0.0069427 | -0.11162 | -0.013409 | -0.0041164 | -0.001976 | 0.0019717 | -0.011871 | 0.21057 | 0.24719 | 0.23346 | 0.22888 | 0.35706 | 0.10071 | -0.059509 | 0.20599 | 0.29755 | 0.14648 | 0.27466 | 0.21515 | 0.018311 | -0.041199 | 122.8729 | 122.7127 | 0.18768 | 123.0194 | 123.0011 | 0.28839 | 0.041198 | 122.7905 | 122.731 | 0.10529 | 122.9782 | 122.9187 | 0.18768 | 0.045776 | 123.1293 | 122.9828 | 123.0057 | -0.22888 | 123.0469 | 122.9874 | 123.0698 | -0.21057
2669.8125 | 122.9965 | -122.8134 | 0.19226 | -0.054016 | 0.027023 | 0.002948 | 0.0049047 | -0.0064748 | 0.0024288 | -0.0048065 | -0.020065 | -0.010846 | -0.0051846 | -0.00048061 | 0.0058169 | -0.017425 | 0.09613 | 0.045776 | 0.009155 | 0.041199 | 0.27924 | -0.013733 | -0.16479 | 0.045776 | 0.064087 | -0.082397 | 0.20142 | 0.16022 | -0.11902 | -0.15564 | 122.7997 | 122.6486 | 0.086975 | 122.8592 | 122.8546 | 0.20599 | -0.096131 | 122.6944 | 122.6578 | 0.009155 | 122.8592 | 122.731 | 0.073243 | -0.032044 | 123.0927 | 122.9095 | 122.8226 | -0.35706 | 123.0148 | 122.9736 | 122.8775 | -0.3479
2671.5 | 123.0515 | -122.8088 | 0.17395 | 0.15198 | 0.027664 | 0.0038024 | 0.0044775 | -0.0051932 | 0.0015744 | -0.0050201 | 0.14015 | -0.0097775 | -0.0056118 | -0.00026701 | 0.0066715 | -0.013153 | 0.036621 | 0.013733 | -0.009155 | 0.004578 | 0.25177 | -0.045776 | -0.19684 | 0.07782 | 0.09613 | -0.018311 | 0.18768 | 0.15564 | -0.11444 | -0.16479 | 122.7631 | 122.612 | 0.07782 | 122.8226 | 122.8134 | 0.20142 | -0.13733 | 122.6944 | 122.644 | 0.013733 | 122.8867 | 122.7905 | 0.14648 | -0.01831 | 123.0606 | 122.8455 | 122.7997 | -0.37079 | 122.9965 | 122.9645 | 122.905 | -0.33874
2673.1875 | 123.0194 | -122.8271 | 0.19684 | -0.054016 | 0.027237 | 0.004657 | 0.0066137 | -0.005834 | 0.0015744 | -0.0037385 | -0.065842 | -0.010846 | -0.006039 | -0.0038986 | 0.0073123 | -0.015075 | 0.10071 | 0.082397 | 0.045776 | 0.073242 | 0.28381 | 0.004578 | -0.14191 | 0.068665 | 0.091553 | -0.050354 | 0.21973 | 0.16937 | -0.091553 | -0.15106 | 122.8317 | 122.6852 | 0.086975 | 122.9095 | 122.9004 | 0.21515 | -0.09613 | 122.7356 | 122.6761 | 0.022889 | 122.8958 | 122.7768 | 0.10071 | -0.027465 | 123.111 | 122.9279 | 122.8729 | -0.33875 | 123.0469 | 122.9965 | 122.9187 | -0.3479
2674.9531 | 123.056 | -122.8043 | 0.18768 | 0.13672 | 0.029373 | 0.0059388 | 0.0046911 | -0.0094656 | -0.00098918 | -0.0058747 | 0.17067 | -0.0117 | -0.0045438 | 0.00058739 | 0.0056033 | -0.012726 | 0.018311 | 0.018311 | -0.013733 | 0.013733 | 0.26093 | -0.022888 | -0.19226 | 0.054932 | 0.059509 | -0.045776 | 0.19226 | 0.15564 | -0.1236 | -0.15564 | 122.7814 | 122.612 | 0.073242 | 122.8226 | 122.818 | 0.20599 | -0.16937 | 122.6807 | 122.6486 | 0.004578 | 122.8592 | 122.7585 | 0.10986 | -0.032043 | 123.0652 | 122.8226 | 122.7905 | -0.37994 | 122.9965 | 122.9599 | 122.8638 | -0.34332
2676.7031 | 123.0743 | -122.7859 | 0.17395 | -0.11505 | 0.030014 | 0.0035888 | 0.0072547 | -0.0045522 | -0.00013458 | -0.0060883 | -0.081101 | -0.0078549 | -0.009457 | -0.0024032 | 0.0066715 | -0.013794 | 0.12817 | 0.12817 | 0.073242 | 0.10529 | 0.29297 | 0.013733 | -0.15106 | 0.11444 | 0.16937 | 0.013733 | 0.21515 | 0.1831 | -0.082397 | -0.12817 | 122.7997 | 122.6349 | 0.11902 | 122.9141 | 122.8912 | 0.25635 | -0.045776 | 122.7036 | 122.6578 | 0.041199 | 122.9004 | 122.7997 | 0.14191 | 0.009155 | 123.0789 | 122.9141 | 122.8592 | -0.32501 | 123.0011 | 122.9691 | 122.9553 | -0.30212
2678.4219 | 123.0331 | -122.7814 | 0.19226 | 0.0070193 | 0.02446 | 0.0067932 | 0.0049047 | -0.0066884 | -0.0071842 | -0.0080109 | 0.10963 | -0.013409 | -0.004971 | -0.00090781 | 0.0011173 | -0.01358 | 0.091553 | 0.14191 | 0.1236 | 0.13275 | 0.28839 | 0.054932 | -0.11444 | 0.13733 | 0.20599 | 0.091553 | 0.22888 | 0.19226 | -0.045776 | -0.064087 | 122.8363 | 122.6669 | 0.09613 | 122.9233 | 122.9141 | 0.24719 | -0.10071 | 122.7356 | 122.7173 | 0.036621 | 122.9187 | 122.8729 | 0.15564 | 0 | 123.0698 | 122.8729 | 122.905 | -0.3067 | 123.0103 | 122.9736 | 122.9874 | -0.25635
2680.1719 | 123.0698 | -122.7585 | 0.16937 | 0.022278 | 0.024246 | 0.0057252 | 0.0046911 | -0.005834 | -0.0063296 | -0.0099335 | 0.094375 | -0.011487 | -0.0079618 | -0.0015488 | 0.0028263 | -0.010376 | 0.10986 | 0.14191 | 0.13275 | 0.1236 | 0.30212 | 0.068665 | -0.10071 | 0.14191 | 0.20142 | 0.12817 | 0.23804 | 0.21515 | -0.041199 | -0.073242 | 122.8271 | 122.6578 | 0.13275 | 122.9004 | 122.8821 | 0.2243 | -0.05951 | 122.7173 | 122.6852 | 0.068664 | 122.9004 | 122.8867 | 0.20142 | 0.045776 | 123.0606 | 122.8683 | 122.8912 | -0.27008 | 122.9965 | 122.9736 | 122.9599 | -0.24261
2681.9219 | 123.1338 | -122.7539 | 0.16022 | -0.16846 | 0.028946 | 0.0048706 | 0.0031957 | -0.0079702 | 0.0030698 | -0.0077973 | -0.24132 | -0.0080685 | -0.0096706 | -0.00048061 | 0.0070987 | -0.01593 | 0.15106 | 0.10071 | 0.073242 | 0.13275 | 0.32959 | 0.018311 | -0.1236 | 0.10529 | 0.15564 | 0.022888 | 0.23804 | 0.2243 | -0.064087 | -0.13733 | 122.7722 | 122.6303 | 0.16937 | 122.8546 | 122.8867 | 0.25635 | -0.009155 | 122.6898 | 122.6166 | 0.07782 | 122.8592 | 122.7768 | 0.16022 | 0.064087 | 123.0835 | 122.905 | 122.8271 | -0.28381 | 122.9919 | 122.9782 | 122.9095 | -0.29755
2683.6875 | 123.0057 | -122.8134 | 0.20599 | -0.038757 | 0.029587 | 0.0048706 | 0.0057593 | -0.0064748 | 0.0015744 | -0.0065155 | -0.042954 | -0.010205 | -0.0045438 | -0.001976 | 0.0053897 | -0.016143 | 0.12817 | 0.073242 | 0.032043 | 0.068665 | 0.29297 | -0.018311 | -0.15106 | 0.064087 | 0.082397 | -0.059509 | 0.21515 | 0.17853 | -0.10986 | -0.16479 | 122.7951 | 122.6624 | 0.086975 | 122.8867 | 122.8821 | 0.21973 | -0.07782 | 122.7036 | 122.6486 | 0.009155 | 122.8775 | 122.7539 | 0.10529 | -0.027466 | 123.1064 | 122.9416 | 122.8455 | -0.35706 | 123.0286 | 122.9919 | 122.8958 | -0.37079
2685.3906 | 123.0652 | -122.7905 | 0.18768 | 0.0070193 | 0.023605 | 0.0067932 | 0.0066137 | -0.0079702 | -0.0069706 | -0.0077973 | 0.102 | -0.011059 | -0.0062528 | -0.0032578 | 0.0021853 | -0.012726 | 0.09613 | 0.15106 | 0.14191 | 0.13275 | 0.31128 | 0.064087 | -0.091553 | 0.1236 | 0.19684 | 0.11902 | 0.23804 | 0.19684 | -0.027466 | -0.07782 | 122.8546 | 122.699 | 0.1236 | 122.9416 | 122.9233 | 0.2243 | -0.091553 | 122.7631 | 122.7127 | 0.050354 | 122.9141 | 122.9095 | 0.19684 | 0.009155 | 123.1018 | 122.8867 | 122.9324 | -0.27924 | 123.0286 | 122.9874 | 122.9874 | -0.2655
2687.125 | 123.0789 | -122.7814 | 0.1831 | -0.099793 | 0.029587 | 0.0048706 | 0.0089635 | -0.0071158 | 0.0032834 | -0.0035249 | -0.14214 | -0.0076413 | -0.003262 | -0.0015488 | 0.0051761 | -0.015716 | 0.14191 | 0.12817 | 0.07782 | 0.091553 | 0.30212 | -0.004578 | -0.15106 | 0.11444 | 0.13275 | -0.009155 | 0.22888 | 0.1831 | -0.086975 | -0.12817 | 122.7768 | 122.6303 | 0.11902 | 122.9095 | 122.8729 | 0.24261 | -0.041198 | 122.6944 | 122.6532 | 0.045777 | 122.8958 | 122.7722 | 0.11902 | 0 | 123.0835 | 122.9233 | 122.8592 | -0.33417 | 123.0103 | 122.9645 | 122.9141 | -0.31128
2688.8906 | 123.0011 | -122.7951 | 0.21515 | 0.083313 | 0.027664 | 0.0065796 | 0.0040503 | -0.0077566 | 0.00071982 | -0.0063019 | 0.071487 | -0.0078549 | -0.0058254 | -0.0015488 | 0.0049625 | -0.014007 | 0.013733 | -0.032043 | -0.064087 | 0.009155 | 0.27924 | -0.041199 | -0.19226 | 0.018311 | 0.027466 | -0.086975 | 0.19226 | 0.16479 | -0.12817 | -0.16937 | 122.7539 | 122.6028 | 0.064087 | 122.7631 | 122.8043 | 0.20142 | -0.20142 | 122.6669 | 122.6257 | -0.022888 | 122.8134 | 122.7081 | 0.082398 | -0.050354 | 123.0743 | 122.8088 | 122.731 | -0.40741 | 122.9874 | 122.9599 | 122.8226 | -0.38452
2690.6562 | 123.0652 | -122.7951 | 0.18768 | 0.22064 | 0.027023 | 0.0042298 | 0.0055457 | -0.0083974 | -0.002698 | -0.0067291 | 0.16304 | -0.010632 | -0.0051846 | -0.0011216 | 0.0060305 | -0.015075 | 0.059509 | 0.045776 | 0.027466 | 0.041199 | 0.23346 | -0.004578 | -0.17395 | 0.12817 | 0.15564 | 0.045776 | 0.15564 | 0.1236 | -0.068665 | -0.14191 | 122.7905 | 122.6212 | 0.045776 | 122.8409 | 122.8363 | 0.21515 | -0.12817 | 122.7264 | 122.6532 | -0.032043 | 122.9233 | 122.8409 | 0.18768 | -0.064087 | 123.0286 | 122.8546 | 122.8226 | -0.36163 | 122.9507 | 122.9187 | 122.9507 | -0.32959
2692.3594 | 123.0698 | -122.7859 | 0.17395 | -0.099793 | 0.029587 | 0.0055114 | 0.0061865 | -0.0047658 | 0.0015744 | -0.0067291 | -0.10399 | -0.0089229 | -0.0075344 | -0.003685 | 0.0068851 | -0.01593 | 0.15106 | 0.11444 | 0.064087 | 0.10529 | 0.3067 | 0.009155 | -0.14648 | 0.10071 | 0.14648 | -0.004578 | 0.23346 | 0.21057 | -0.091553 | -0.12817 | 122.7951 | 122.6395 | 0.13275 | 122.9004 | 122.8912 | 0.25177 | -0.022888 | 122.6944 | 122.6578 | 0.059509 | 122.8867 | 122.7814 | 0.1236 | 0.036621 | 123.0927 | 122.937 | 122.85 | -0.32043 | 123.0194 | 122.9965 | 122.9324 | -0.30212
2694.125 | 123.0743 | -122.7814 | 0.1831 | -0.11505 | 0.030228 | 0.0052978 | 0.0070409 | -0.010106 | 0.0013608 | -0.0030975 | -0.08873 | -0.0087093 | -0.0071072 | -0.0024032 | 0.0060305 | -0.015289 | 0.14191 | 0.10986 | 0.059509 | 0.10529 | 0.29297 | 0 | -0.16479 | 0.10986 | 0.15106 | -0.013733 | 0.21973 | 0.20142 | -0.082397 | -0.1236 | 122.7814 | 122.6166 | 0.10986 | 122.8912 | 122.8867 | 0.27008 | -0.041198 | 122.699 | 122.6578 | 0.036622 | 122.8912 | 122.7676 | 0.10986 | 0.018311 | 123.0743 | 122.9233 | 122.8409 | -0.3479 | 123.0011 | 122.9828 | 122.9324 | -0.3067
2695.8906 | 123.0194 | -122.818 | 0.21515 | -0.038757 | 0.029587 | 0.0052978 | 0.0051183 | -0.008611 | -0.00077538 | -0.0048065 | 0.018082 | -0.0076413 | -0.0062528 | -0.0013352 | 0.0068851 | -0.011871 | 0.086975 | 0.036621 | 0.018311 | 0.064087 | 0.3067 | -0.009155 | -0.16937 | 0.022888 | 0.054932 | -0.064087 | 0.20142 | 0.1831 | -0.1236 | -0.16937 | 122.8088 | 122.6486 | 0.091553 | 122.8546 | 122.8821 | 0.23346 | -0.12817 | 122.6944 | 122.6486 | -0.013733 | 122.8409 | 122.7539 | 0.10529 | -0.032044 | 123.1247 | 122.905 | 122.8363 | -0.38452 | 123.0194 | 123.0011 | 122.8729 | -0.38452
2697.6562 | 123.143 | -122.7356 | 0.16937 | -0.17609 | 0.028519 | 0.0050842 | 0.0083227 | -0.0062612 | -0.00013458 | -0.0056611 | -0.18791 | -0.010418 | -0.0041164 | -0.0017624 | 0.0028263 | -0.014862 | 0.11444 | 0.11902 | 0.091553 | 0.1236 | 0.36163 | 0.064087 | -0.10071 | 0.09613 | 0.17853 | 0.018311 | 0.28381 | 0.26093 | -0.045776 | -0.086975 | 122.7997 | 122.6349 | 0.19226 | 122.8546 | 122.8592 | 0.2243 | -0.054932 | 122.6898 | 122.6486 | 0.11444 | 122.8317 | 122.7539 | 0.10529 | 0.091552 | 123.0972 | 122.85 | 122.8271 | -0.27008 | 123.0194 | 122.9965 | 122.9141 | -0.25635
2699.3594 | 123.0515 | -122.7859 | 0.19226 | 0.12909 | 0.028092 | 0.0057252 | 0.0055457 | -0.007543 | -0.0029118 | -0.0058747 | 0.14778 | -0.011487 | -0.0053982 | 0.00058739 | 0.0049625 | -0.013153 | 0.082397 | 0.07782 | 0.07782 | 0.064087 | 0.2243 | -0.032043 | -0.17853 | 0.13733 | 0.17395 | 0.068665 | 0.16022 | 0.13275 | -0.07782 | -0.1236 | 122.7539 | 122.6074 | 0.032043 | 122.8638 | 122.85 | 0.24261 | -0.10986 | 122.7081 | 122.6624 | -0.032044 | 122.9233 | 122.8546 | 0.19226 | -0.05951 | 123.0103 | 122.8683 | 122.8638 | -0.37079 | 122.9462 | 122.9187 | 122.9599 | -0.31586
2701.0625 | 123.0835 | -122.7768 | 0.1831 | -0.24475 | 0.028092 | 0.0048706 | 0.010673 | -0.0045522 | -0.0048344 | -0.010147 | -0.13451 | -0.0099911 | -0.0036892 | -0.0015488 | 0.0023989 | -0.012726 | 0.17395 | 0.16479 | 0.14191 | 0.17853 | 0.38452 | 0.073242 | -0.064087 | 0.11902 | 0.17853 | 0.064087 | 0.31128 | 0.27008 | -0.027466 | -0.086975 | 122.85 | 122.7127 | 0.20142 | 122.9416 | 122.9553 | 0.24261 | -0.009155 | 122.7493 | 122.6898 | 0.12817 | 122.8958 | 122.8409 | 0.15106 | 0.086976 | 123.1613 | 122.9507 | 122.9187 | -0.24719 | 123.0881 | 123.0469 | 122.9553 | -0.27008
2702.8125 | 122.9919 | -122.8088 | 0.1831 | 0.19012 | 0.028092 | 0.0042298 | 0.0087499 | -0.0077566 | -0.0035526 | -0.0067291 | 0.18593 | -0.012982 | -0.0026212 | -0.0011216 | 0.0021853 | -0.012512 | 0.086975 | 0.11902 | 0.09613 | 0.07782 | 0.20142 | -0.018311 | -0.16937 | 0.13733 | 0.18768 | 0.068665 | 0.15106 | 0.1236 | -0.091553 | -0.13275 | 122.7905 | 122.6395 | 0.018311 | 122.9279 | 122.8867 | 0.24719 | -0.09613 | 122.7173 | 122.6761 | -0.032043 | 122.9462 | 122.8775 | 0.20142 | -0.059509 | 123.0103 | 122.8958 | 122.905 | -0.35248 | 122.9599 | 122.9324 | 122.9965 | -0.31586
2704.5781 | 123.024 | -122.7997 | 0.20142 | 0.068054 | 0.02681 | 0.0042298 | 0.0091773 | -0.0051932 | -0.0065434 | -0.0077973 | 0.063858 | -0.012127 | -0.0058254 | -0.00090781 | 0.0019717 | -0.012085 | 0.10529 | 0.13275 | 0.11902 | 0.13275 | 0.28381 | 0.054932 | -0.11444 | 0.14191 | 0.19226 | 0.09613 | 0.2243 | 0.19684 | -0.045776 | -0.091553 | 122.8546 | 122.6852 | 0.082397 | 122.9324 | 122.9324 | 0.24719 | -0.09613 | 122.7539 | 122.7081 | 0.022888 | 122.9416 | 122.8958 | 0.18768 | -0.004578 | 123.0835 | 122.905 | 122.9187 | -0.31586 | 123.024 | 122.9965 | 122.9919 | -0.29297
2706.2812 | 122.9965 | -122.8134 | 0.21057 | -0.0082397 | 0.030869 | 0.0044434 | 0.0057593 | -0.0062612 | 0.0028562 | -0.0067291 | -0.012436 | -0.010846 | -0.003262 | 0.0018692 | 0.0062441 | -0.015289 | 0.07782 | 0.041199 | 0 | 0.045776 | 0.27008 | -0.036621 | -0.19226 | 0.032043 | 0.045776 | -0.09613 | 0.21515 | 0.17395 | -0.13275 | -0.16479 | 122.7768 | 122.6212 | 0.05951 | 122.8546 | 122.8592 | 0.23804 | -0.13275 | 122.6807 | 122.6486 | 0.004578 | 122.8455 | 122.7173 | 0.068665 | -0.036621 | 123.0835 | 122.8912 | 122.8134 | -0.40283 | 123.0286 | 122.9874 | 122.8592 | -0.37537
2708.0312 | 123.0377 | -122.7997 | 0.18768 | 0.029907 | 0.025314 | 0.0057252 | 0.0083227 | -0.0081838 | -0.0041934 | -0.0069427 | 0.079117 | -0.013196 | -0.0041164 | -5.3406e-05 | -0.00037807 | -0.015075 | 0.10071 | 0.14191 | 0.12817 | 0.10986 | 0.28839 | 0.045776 | -0.11902 | 0.13733 | 0.20142 | 0.11444 | 0.24261 | 0.21057 | -0.036621 | -0.091553 | 122.8455 | 122.6807 | 0.10071 | 122.9416 | 122.9095 | 0.22888 | -0.086975 | 122.7631 | 122.7081 | 0.054932 | 122.937 | 122.9141 | 0.20599 | 0.022888 | 123.0881 | 122.9004 | 122.9279 | -0.3067 | 123.0423 | 123.0103 | 123.0011 | -0.27924
2709.7812 | 123.1567 | -122.7951 | 0.16937 | -0.23712 | 0.027664 | 0.0087158 | 0.0074683 | -0.007543 | 0.00071982 | -0.0082245 | -0.20317 | -0.0084957 | -0.0043302 | -0.0021896 | 0.0051761 | -0.015075 | 0.15564 | 0.11902 | 0.09613 | 0.14191 | 0.39368 | 0.068665 | -0.10986 | 0.10529 | 0.14648 | 0.018311 | 0.29297 | 0.27008 | -0.064087 | -0.10529 | 122.8638 | 122.6852 | 0.2243 | 122.9141 | 122.937 | 0.25177 | -0.013733 | 122.731 | 122.6898 | 0.1236 | 122.9004 | 122.8134 | 0.1236 | 0.10071 | 123.1888 | 122.9507 | 122.8912 | -0.27924 | 123.0881 | 123.0652 | 122.9416 | -0.27466
2711.5312 | 123.1384 | -122.7585 | 0.15106 | -0.19135 | 0.028732 | 0.0048706 | 0.0083227 | -0.0073294 | 0.00050622 | -0.0048065 | -0.18791 | -0.0097775 | -0.004971 | 0.001442 | 0.0073123 | -0.016357 | 0.14648 | 0.1236 | 0.07782 | 0.13275 | 0.36163 | 0.059509 | -0.10986 | 0.10986 | 0.13733 | 0.009155 | 0.24261 | 0.22888 | -0.068665 | -0.10529 | 122.818 | 122.6486 | 0.21057 | 122.8821 | 122.8912 | 0.24261 | -0.004578 | 122.6898 | 122.6532 | 0.091553 | 122.8683 | 122.7676 | 0.11444 | 0.07782 | 123.1201 | 122.905 | 122.8363 | -0.26093 | 123.0011 | 122.9874 | 122.8958 | -0.25635
2713.2188 | 123.1567 | -122.7676 | 0.16479 | -0.17609 | 0.031296 | 0.0044434 | 0.0087499 | -0.0060476 | 0.0024288 | -0.0065155 | -0.19554 | -0.011487 | -0.003262 | -0.0011216 | 0.0043215 | -0.014648 | 0.11444 | 0.13275 | 0.09613 | 0.15106 | 0.3479 | 0.045776 | -0.11902 | 0.10071 | 0.16022 | 0.009155 | 0.2655 | 0.24261 | -0.054932 | -0.10986 | 122.8134 | 122.6486 | 0.1831 | 122.9004 | 122.9187 | 0.27008 | -0.050354 | 122.7127 | 122.6578 | 0.10071 | 122.8683 | 122.7768 | 0.11902 | 0.07782 | 123.1155 | 122.8821 | 122.8638 | -0.28381 | 123.0331 | 123.0103 | 122.9279 | -0.27466
2714.9844 | 123.1064 | -122.7585 | 0.16937 | -0.23712 | 0.026596 | 0.0048706 | 0.0089635 | -0.0071158 | -0.0054752 | -0.0069427 | -0.11162 | -0.011914 | -0.0041164 | -0.00069421 | 0.0017581 | -0.014007 | 0.21057 | 0.29755 | 0.25177 | 0.23346 | 0.35706 | 0.13733 | -0.045776 | 0.23346 | 0.31586 | 0.16937 | 0.27466 | 0.23346 | 0.009155 | -0.032043 | 122.8958 | 122.7127 | 0.18768 | 123.056 | 122.9919 | 0.27924 | 0.041198 | 122.7676 | 122.7264 | 0.10529 | 122.9919 | 122.9279 | 0.20142 | 0.064086 | 123.1155 | 122.9691 | 123.0103 | -0.21515 | 123.0331 | 122.9919 | 123.0743 | -0.20142
2716.75 | 123.1476 | -122.7585 | 0.16479 | -0.038757 | 0.023178 | 0.0055114 | 0.0070409 | -0.0096792 | -0.006116 | -0.0080109 | 0.0028229 | -0.011273 | -0.0047574 | -5.3406e-05 | -0.00059167 | -0.012939 | 0.13733 | 0.2243 | 0.19226 | 0.1831 | 0.32959 | 0.07782 | -0.086975 | 0.22888 | 0.29297 | 0.19226 | 0.25177 | 0.22888 | -0.009155 | -0.068665 | 122.8363 | 122.6715 | 0.16479 | 122.9828 | 122.9416 | 0.27008 | -0.027466 | 122.7493 | 122.6898 | 0.086975 | 122.9874 | 122.9507 | 0.26093 | 0.064087 | 123.0881 | 122.8958 | 122.9507 | -0.25177 | 123.0103 | 122.9874 | 123.0515 | -0.23346
2718.5156 | 123.0377 | -122.7997 | 0.1831 | 0.045166 | 0.027237 | 0.0052978 | 0.0059729 | -0.0069022 | -0.0048344 | -0.0084381 | 0.086746 | -0.012555 | -0.0043302 | -0.00090781 | 0.0015445 | -0.012726 | 0.1236 | 0.13733 | 0.12817 | 0.10071 | 0.28839 | 0.059509 | -0.10071 | 0.15106 | 0.18768 | 0.11444 | 0.24261 | 0.19684 | -0.032043 | -0.09613 | 122.8592 | 122.699 | 0.10529 | 122.937 | 122.9004 | 0.20142 | -0.059509 | 122.7676 | 122.7036 | 0.05951 | 122.9507 | 122.9141 | 0.21057 | 0.013733 | 123.0881 | 122.9233 | 122.9279 | -0.28381 | 123.0423 | 122.9965 | 122.9874 | -0.27924
2720.2031 | 123.024 | -122.818 | 0.1831 | 0.068054 | 0.024033 | 0.0065796 | 0.0064001 | -0.005834 | -0.0022708 | -0.0092927 | 0.063858 | -0.012768 | -0.004971 | 0.00016019 | 0.0036807 | -0.014648 | 0.1236 | 0.13275 | 0.11902 | 0.11902 | 0.27924 | 0.059509 | -0.10529 | 0.15564 | 0.19226 | 0.09613 | 0.22888 | 0.19226 | -0.041199 | -0.082397 | 122.8775 | 122.7127 | 0.096131 | 122.9507 | 122.937 | 0.22431 | -0.059509 | 122.7768 | 122.7356 | 0.045777 | 122.9736 | 122.9141 | 0.17853 | 0.009156 | 123.0972 | 122.9416 | 122.937 | -0.28839 | 123.0469 | 123.0103 | 123.0103 | -0.2655
2721.8906 | 123.1338 | -122.7631 | 0.16022 | -0.22949 | 0.029587 | 0.0052978 | 0.0064001 | -0.0079702 | 0.0015744 | -0.0052337 | -0.22606 | -0.010205 | -0.0028348 | -0.0013352 | 0.0060305 | -0.01593 | 0.15564 | 0.11444 | 0.091553 | 0.13275 | 0.38452 | 0.07782 | -0.09613 | 0.11902 | 0.15106 | 0.027466 | 0.28839 | 0.26093 | -0.050354 | -0.10529 | 122.8409 | 122.6669 | 0.2243 | 122.8775 | 122.8958 | 0.22888 | -0.004577 | 122.7127 | 122.6578 | 0.12817 | 122.8821 | 122.7905 | 0.13275 | 0.10071 | 123.1476 | 122.9187 | 122.8546 | -0.25635 | 123.0515 | 123.024 | 122.9141 | -0.2655
2723.5781 | 123.1338 | -122.7539 | 0.15106 | -0.25238 | 0.027237 | 0.0052978 | 0.0087499 | -0.008611 | -0.00056178 | -0.0067291 | -0.23369 | -0.0097775 | -0.006039 | -0.00090781 | 0.0045351 | -0.017639 | 0.16022 | 0.15106 | 0.09613 | 0.13733 | 0.39368 | 0.064087 | -0.091553 | 0.10986 | 0.16937 | 0.004578 | 0.28839 | 0.24719 | -0.041199 | -0.07782 | 122.818 | 122.6624 | 0.24261 | 122.905 | 122.8912 | 0.22888 | 0.009155 | 122.7127 | 122.6761 | 0.13733 | 122.8638 | 122.7585 | 0.082398 | 0.09613 | 123.1476 | 122.9141 | 122.85 | -0.24261 | 123.0423 | 123.0011 | 122.9233 | -0.22888
2725.3125 | 123.1384 | -122.7585 | 0.17395 | -0.25238 | 0.027237 | 0.0048706 | 0.0072547 | -0.0073294 | 0.00071982 | -0.0065155 | -0.24132 | -0.0097775 | -0.0045438 | -0.0021896 | 0.0043215 | -0.015075 | 0.14191 | 0.16937 | 0.11902 | 0.16022 | 0.39825 | 0.091553 | -0.086975 | 0.10986 | 0.16479 | 0.027466 | 0.3067 | 0.26093 | -0.036621 | -0.086975 | 122.85 | 122.6715 | 0.2243 | 122.9279 | 122.9187 | 0.24719 | -0.032043 | 122.7219 | 122.6715 | 0.13275 | 122.8683 | 122.7859 | 0.11444 | 0.086975 | 123.1567 | 122.9004 | 122.8775 | -0.26092 | 123.0652 | 123.0194 | 122.9233 | -0.26092
2727.0156 | 123.0743 | -122.7539 | 0.18768 | 0.014648 | 0.025955 | 0.0070068 | 0.0040503 | -0.0090384 | -0.0048344 | -0.0084381 | 0.04097 | -0.010846 | -0.0090298 | -0.0015488 | 0.0015445 | -0.011657 | 0.10071 | 0.15564 | 0.12817 | 0.13733 | 0.29755 | 0.068665 | -0.11444 | 0.14191 | 0.19226 | 0.10986 | 0.25635 | 0.20142 | -0.022888 | -0.086975 | 122.8226 | 122.6395 | 0.10986 | 122.9095 | 122.8912 | 0.25177 | -0.086975 | 122.731 | 122.6669 | 0.068665 | 122.8958 | 122.8638 | 0.19684 | 0.013733 | 123.0515 | 122.8546 | 122.8821 | -0.30212 | 123.0103 | 122.9553 | 122.9462 | -0.27466
2728.7656 | 123.0652 | -122.7676 | 0.17853 | 0.12146 | 0.029587 | 0.0065796 | 0.0027685 | -0.0071158 | 0.0015744 | -0.0069427 | 0.14015 | -0.0097775 | -0.004971 | 0.0010148 | 0.0083805 | -0.01358 | 0.059509 | 0.009155 | -0.022888 | 0.013733 | 0.25635 | -0.027466 | -0.18768 | 0.073242 | 0.054932 | -0.013733 | 0.1831 | 0.14191 | -0.1236 | -0.17853 | 122.7402 | 122.58 | 0.07782 | 122.7768 | 122.7814 | 0.20142 | -0.11902 | 122.644 | 122.5891 | 0.004577 | 122.8409 | 122.7539 | 0.16479 | -0.036621 | 123.024 | 122.8271 | 122.7448 | -0.36621 | 122.9507 | 122.9095 | 122.8226 | -0.35706
2730.5156 | 123.0057 | -122.7997 | 0.20599 | 0.075684 | 0.030869 | 0.0057252 | 0.0019141 | -0.0088248 | 0.0032834 | -0.0063019 | 0.010452 | -0.0078549 | -0.0073208 | 0.00037379 | 0.0070987 | -0.012726 | 0.054932 | -0.018311 | -0.027466 | 0.009155 | 0.2655 | -0.032043 | -0.19226 | 0 | 0.027466 | -0.10529 | 0.1831 | 0.17395 | -0.11444 | -0.16937 | 122.7676 | 122.6074 | 0.059509 | 122.7814 | 122.8088 | 0.20142 | -0.15106 | 122.6852 | 122.6303 | -0.022889 | 122.7997 | 122.6944 | 0.064087 | -0.032044 | 123.0652 | 122.8546 | 122.7722 | -0.39826 | 122.9828 | 122.9736 | 122.8271 | -0.37537
2732.2031 | 123.1293 | -122.7768 | 0.16937 | -0.11505 | 0.027451 | 0.0057252 | 0.0049047 | -0.0071158 | -0.0076114 | -0.0063019 | -0.073471 | -0.013623 | -0.0051846 | -0.0028306 | 0.0017581 | -0.011871 | 0.18768 | 0.25635 | 0.2243 | 0.20142 | 0.33875 | 0.082397 | -0.054932 | 0.22888 | 0.29297 | 0.18768 | 0.25177 | 0.23346 | -0.009155 | -0.045776 | 122.8592 | 122.7219 | 0.16937 | 123.0331 | 122.9782 | 0.25635 | 0.01831 | 122.7676 | 122.731 | 0.082397 | 123.0057 | 122.9645 | 0.23346 | 0.064086 | 123.1155 | 122.9645 | 123.0011 | -0.22431 | 123.0286 | 123.0103 | 123.0698 | -0.21515
2733.9531 | 123.111 | -122.7631 | 0.17853 | -0.22186 | 0.026169 | 0.0044434 | 0.0081091 | -0.009252 | -0.0035526 | -0.0077973 | -0.15739 | -0.010846 | -0.0073208 | -0.0026168 | 0.0013309 | -0.014221 | 0.23804 | 0.27466 | 0.25177 | 0.22888 | 0.35248 | 0.12817 | -0.054932 | 0.23804 | 0.31586 | 0.19226 | 0.24719 | 0.24719 | 0.018311 | -0.041199 | 122.8912 | 122.7081 | 0.17395 | 123.0377 | 122.9919 | 0.28381 | 0.059509 | 122.7814 | 122.7219 | 0.068664 | 123.0011 | 122.9553 | 0.23346 | 0.068664 | 123.1155 | 123.0011 | 123.0148 | -0.23346 | 123.0103 | 123.0103 | 123.0789 | -0.21973
2735.7188 | 123.1522 | -122.7585 | 0.15564 | -0.046387 | 0.022965 | 0.0085022 | 0.0044775 | -0.007543 | -0.0052616 | -0.0082245 | -0.065842 | -0.0117 | -0.007748 | -0.0015488 | 0.0023989 | -0.013153 | 0.20599 | 0.21057 | 0.20142 | 0.19684 | 0.33417 | 0.091553 | -0.07782 | 0.24261 | 0.29297 | 0.1831 | 0.27008 | 0.21973 | 0.004578 | -0.050354 | 122.85 | 122.6807 | 0.17853 | 122.9691 | 122.9553 | 0.27466 | 0.050354 | 122.7631 | 122.7081 | 0.11444 | 123.0011 | 122.9416 | 0.23346 | 0.064087 | 123.0927 | 122.9645 | 122.9599 | -0.23346 | 123.0286 | 122.9782 | 123.0515 | -0.20599
2737.4062 | 123.0927 | -122.7676 | 0.18768 | -0.25238 | 0.027237 | 0.0061524 | 0.0057593 | -0.007543 | 0.00050622 | -0.0088653 | -0.27184 | -0.012768 | -0.0051846 | -0.0026168 | 0.0019717 | -0.01358 | 0.22888 | 0.19226 | 0.16479 | 0.18768 | 0.36621 | 0.091553 | -0.07782 | 0.15564 | 0.21515 | 0.068665 | 0.28839 | 0.27924 | -0.009155 | -0.07782 | 122.8592 | 122.6898 | 0.17853 | 122.9599 | 122.9553 | 0.2655 | 0.041199 | 122.7585 | 122.6898 | 0.10071 | 122.9233 | 122.8363 | 0.14649 | 0.091553 | 123.1339 | 122.9965 | 122.9324 | -0.2655 | 123.056 | 123.0469 | 122.9828 | -0.2655
2739.1562 | 123.1338 | -122.7905 | 0.16937 | -0.26001 | 0.025955 | 0.0050842 | 0.0078955 | -0.0071158 | 0.00093342 | -0.0084381 | -0.26421 | -0.0093503 | -0.0036892 | 0.0018692 | 0.0058169 | -0.014007 | 0.16479 | 0.13733 | 0.10071 | 0.14648 | 0.41199 | 0.059509 | -0.073242 | 0.10986 | 0.15106 | 0.036621 | 0.3067 | 0.29297 | -0.032043 | -0.082397 | 122.85 | 122.7173 | 0.24261 | 122.9279 | 122.937 | 0.21973 | -0.004578 | 122.7585 | 122.7081 | 0.13733 | 122.9004 | 122.8271 | 0.11902 | 0.1236 | 123.2025 | 122.9553 | 122.8912 | -0.24261 | 123.0972 | 123.0835 | 122.9416 | -0.25177
2740.8438 | 123.0331 | -122.7951 | 0.16937 | 0.15198 | 0.028092 | 0.0027344 | 0.0034093 | -0.0098928 | 0.0013608 | -0.0058747 | 0.11726 | -0.013196 | -0.0041164 | -0.0017624 | 0.0051761 | -0.014221 | 0.13733 | 0.13733 | 0.09613 | 0.10071 | 0.21515 | -0.013733 | -0.16479 | 0.14191 | 0.16022 | 0.050354 | 0.15106 | 0.1236 | -0.09613 | -0.15106 | 122.7814 | 122.6303 | 0.045776 | 122.9324 | 122.8958 | 0.2655 | -0.032044 | 122.699 | 122.644 | -0.018311 | 122.937 | 122.8455 | 0.20142 | -0.045777 | 123.0103 | 122.9324 | 122.8912 | -0.33417 | 122.9462 | 122.9187 | 122.9553 | -0.32044
2742.5312 | 122.9965 | -122.8088 | 0.18768 | 0.13672 | 0.023819 | 0.0052978 | 0.0023413 | -0.0051932 | -0.005048 | -0.0065155 | 0.14778 | -0.0117 | -0.0071072 | -0.00090781 | 0.0051761 | -0.011871 | 0.09613 | 0.13275 | 0.10529 | 0.09613 | 0.21973 | 0 | -0.14191 | 0.16479 | 0.18768 | 0.073242 | 0.18768 | 0.1831 | -0.050354 | -0.11902 | 122.8088 | 122.6669 | 0.032044 | 122.9416 | 122.905 | 0.23804 | -0.091553 | 122.7585 | 122.6898 | 0 | 122.9736 | 122.8821 | 0.19226 | -0.004578 | 123.0286 | 122.905 | 122.9141 | -0.32959 | 122.9965 | 122.9919 | 122.9965 | -0.3067
2744.2188 | 123.0927 | -122.7768 | 0.16937 | -0.19135 | 0.02681 | 0.004657 | 0.0074683 | -0.0047658 | -0.0024844 | -0.0084381 | -0.16502 | -0.010632 | -0.0041164 | -0.0038986 | 0.0011173 | -0.014007 | 0.22888 | 0.27924 | 0.25177 | 0.21515 | 0.34332 | 0.11444 | -0.045776 | 0.21515 | 0.30212 | 0.15564 | 0.25635 | 0.22888 | -0.004578 | -0.045776 | 122.8912 | 122.731 | 0.17395 | 123.056 | 122.9919 | 0.26093 | 0.059509 | 122.7722 | 122.731 | 0.086975 | 122.9919 | 122.9324 | 0.20142 | 0.059509 | 123.1201 | 123.0057 | 123.0286 | -0.21515 | 123.0331 | 123.0057 | 123.0789 | -0.21515
2745.9688 | 123.1522 | -122.7539 | 0.16022 | -0.16846 | 0.028519 | 0.0044434 | 0.0061865 | -0.0088248 | 0.0022152 | -0.0084381 | -0.27946 | -0.0080685 | -0.007748 | -0.0011216 | 0.0047489 | -0.015075 | 0.14648 | 0.10529 | 0.073242 | 0.1236 | 0.37537 | 0.045776 | -0.10071 | 0.11444 | 0.16937 | 0.022888 | 0.28381 | 0.21973 | -0.045776 | -0.11902 | 122.7997 | 122.6532 | 0.21515 | 122.8592 | 122.8775 | 0.2243 | -0.013733 | 122.7081 | 122.6349 | 0.1236 | 122.8683 | 122.7768 | 0.14191 | 0.05951 | 123.1293 | 122.9004 | 122.8271 | -0.26093 | 123.0377 | 122.9736 | 122.9233 | -0.27924
2747.7188 | 123.111 | -122.7722 | 0.15106 | -0.17609 | 0.02681 | 0.0040162 | 0.0072547 | -0.0054068 | -0.0024844 | -0.0058747 | -0.18028 | -0.012768 | -0.0058254 | 0.00037379 | 0.0028263 | -0.012939 | 0.23346 | 0.29297 | 0.23804 | 0.2243 | 0.33417 | 0.11444 | -0.032043 | 0.23346 | 0.32501 | 0.1831 | 0.26093 | 0.23804 | 0 | -0.022888 | 122.8867 | 122.7402 | 0.1831 | 123.0652 | 122.9965 | 0.25635 | 0.082397 | 122.7722 | 122.7493 | 0.10986 | 123.0057 | 122.9553 | 0.20599 | 0.086975 | 123.1064 | 123.0057 | 123.0103 | -0.18311 | 123.0331 | 123.0103 | 123.0972 | -0.17395
2749.4062 | 123.1064 | -122.7676 | 0.16022 | -0.19135 | 0.025742 | 0.0057252 | 0.0081091 | -0.0062612 | -0.0018436 | -0.0058747 | -0.14977 | -0.013196 | -0.0058254 | -0.0017624 | 0.0023989 | -0.01358 | 0.23804 | 0.28839 | 0.24261 | 0.21515 | 0.34332 | 0.10071 | -0.050354 | 0.23346 | 0.32959 | 0.17853 | 0.27008 | 0.23346 | 0.018311 | -0.041199 | 122.8683 | 122.7173 | 0.18311 | 123.056 | 122.9828 | 0.2655 | 0.07782 | 122.7859 | 122.7264 | 0.10986 | 123.0011 | 122.9462 | 0.21973 | 0.073242 | 123.111 | 123.0057 | 123.0103 | -0.21057 | 123.0377 | 123.0011 | 123.0972 | -0.20142
2751.1719 | 123.0011 | -122.7997 | 0.20142 | 0.037537 | 0.0298 | 0.0065796 | 0.0025549 | -0.0077566 | 0.003497 | -0.0041657 | -0.035324 | -0.0099911 | -0.0043302 | 0.00080099 | 0.0079531 | -0.015716 | 0.059509 | 0 | -0.027466 | 0.009155 | 0.25635 | -0.032043 | -0.19226 | 0.022888 | 0.045776 | -0.07782 | 0.19684 | 0.17853 | -0.12817 | -0.1831 | 122.7676 | 122.6074 | 0.054932 | 122.7997 | 122.8088 | 0.20142 | -0.14191 | 122.6715 | 122.6166 | -0.004578 | 122.8226 | 122.7219 | 0.10528 | -0.022888 | 123.056 | 122.8592 | 122.7722 | -0.39368 | 122.9965 | 122.9782 | 122.8455 | -0.38452
2752.8594 | 123.0377 | -122.8317 | 0.20142 | 0.12146 | 0.0298 | 0.006366 | 0.0042639 | -0.010106 | 0.0032834 | -0.0067291 | 0.04097 | -0.0084957 | -0.0062528 | -0.00090781 | 0.0088077 | -0.01358 | 0.009155 | -0.018311 | -0.045776 | 0 | 0.27008 | -0.050354 | -0.17853 | 0.027466 | 0.022888 | -0.073242 | 0.20599 | 0.15564 | -0.12817 | -0.1831 | 122.7814 | 122.6532 | 0.068665 | 122.8134 | 122.8317 | 0.17853 | -0.19226 | 122.7036 | 122.6486 | 0.004578 | 122.8592 | 122.7585 | 0.10986 | -0.045776 | 123.1018 | 122.8409 | 122.7859 | -0.37994 | 123.0377 | 122.9874 | 122.8546 | -0.38452
2754.6094 | 123.0972 | -122.7768 | 0.16479 | -0.22186 | 0.028092 | 0.0057252 | 0.0074683 | -0.009252 | -0.0065434 | -0.0054475 | -0.11925 | -0.010846 | -0.0058254 | -0.0024032 | 0.00068993 | -0.013153 | 0.20599 | 0.28839 | 0.25177 | 0.22888 | 0.32959 | 0.10529 | -0.045776 | 0.21515 | 0.28381 | 0.16937 | 0.24261 | 0.21973 | 0.013733 | -0.050354 | 122.8821 | 122.731 | 0.16479 | 123.0652 | 123.0057 | 0.27466 | 0.041199 | 122.7905 | 122.7264 | 0.07782 | 122.9919 | 122.9462 | 0.21973 | 0.054932 | 123.1064 | 122.9828 | 123.0286 | -0.21057 | 123.0194 | 122.9965 | 123.0606 | -0.21515
2756.3125 | 123.0148 | -122.8088 | 0.20142 | 0.19775 | 0.02681 | 0.0076478 | 0.0017005 | -0.0066884 | -0.002698 | -0.0050201 | 0.1783 | -0.011487 | -0.006039 | -0.00069421 | 0.0056033 | -0.015503 | 0.10071 | 0.12817 | 0.09613 | 0.091553 | 0.19226 | -0.022888 | -0.17395 | 0.13275 | 0.17395 | 0.059509 | 0.13275 | 0.10071 | -0.09613 | -0.16022 | 122.7859 | 122.6349 | -0.009155 | 122.937 | 122.9004 | 0.2655 | -0.10071 | 122.7127 | 122.6486 | -0.068665 | 122.9416 | 122.8683 | 0.21973 | -0.10071 | 123.0011 | 122.9095 | 122.905 | -0.37537 | 122.9416 | 122.9095 | 122.9828 | -0.36163
2758.0625 | 123.024 | -122.8134 | 0.19226 | 0.060425 | 0.023392 | 0.0055114 | 0.0040503 | -0.010534 | -0.0039798 | -0.0071563 | 0.10963 | -0.011059 | -0.0098844 | -0.003685 | 0.0034671 | -0.012726 | 0.10986 | 0.16022 | 0.11902 | 0.11444 | 0.27008 | 0.041199 | -0.1236 | 0.16022 | 0.19684 | 0.09613 | 0.21057 | 0.19226 | -0.027466 | -0.082397 | 122.8546 | 122.6898 | 0.07782 | 122.9736 | 122.9279 | 0.23804 | -0.082398 | 122.7859 | 122.731 | 0.01831 | 122.9736 | 122.9095 | 0.17853 | 0 | 123.0835 | 122.9233 | 122.9324 | -0.31586 | 123.024 | 123.0057 | 123.0103 | -0.27466
2759.8125 | 123.024 | -122.7814 | 0.1831 | 0.090942 | 0.024246 | 0.006366 | 0.0044775 | -0.0079702 | -0.0052616 | -0.0073701 | 0.10963 | -0.0076413 | -0.0086026 | -0.0026168 | 0.0045351 | -0.012726 | 0.13275 | 0.14648 | 0.1236 | 0.10529 | 0.26093 | 0.032043 | -0.13275 | 0.15106 | 0.1831 | 0.091553 | 0.21057 | 0.18768 | -0.032043 | -0.10529 | 122.8134 | 122.6486 | 0.07782 | 122.9279 | 122.8867 | 0.23804 | -0.050354 | 122.7493 | 122.6761 | 0.027466 | 122.9324 | 122.8729 | 0.19684 | 0.004578 | 123.0423 | 122.9141 | 122.905 | -0.31586 | 122.9919 | 122.9691 | 122.9645 | -0.28839
2761.5156 | 123.0652 | -122.8043 | 0.19684 | -0.092163 | 0.0298 | 0.0052978 | 0.0036231 | -0.0079702 | 0.0028562 | -0.0043793 | -0.15739 | -0.0082821 | -0.0073208 | -0.0015488 | 0.0068851 | -0.014648 | 0.1831 | 0.10071 | 0.064087 | 0.09613 | 0.28839 | 0.013733 | -0.13733 | 0.11444 | 0.13733 | -0.018311 | 0.20599 | 0.19684 | -0.082397 | -0.13733 | 122.818 | 122.6669 | 0.091553 | 122.905 | 122.9004 | 0.23346 | -0.013733 | 122.7219 | 122.6669 | 0.009156 | 122.9187 | 122.7859 | 0.11902 | 0 | 123.0927 | 122.9874 | 122.8683 | -0.33417 | 123.0103 | 123.0011 | 122.9416 | -0.33417
2763.2031 | 123.0469 | -122.7814 | 0.18768 | 0.098572 | 0.033859 | 0.002948 | 0.0083227 | -0.0064748 | 0.0030698 | -0.0048065 | 0.079117 | -0.010846 | -0.0047574 | -0.0011216 | 0.0036807 | -0.014862 | 0.013733 | -0.036621 | -0.032043 | 0 | 0.27466 | -0.036621 | -0.21057 | 0.032043 | 0.013733 | -0.07782 | 0.21057 | 0.16937 | -0.12817 | -0.18768 | 122.7448 | 122.5708 | 0.086975 | 122.7448 | 122.7814 | 0.21057 | -0.17395 | 122.6532 | 122.5937 | 0.022888 | 122.8134 | 122.7036 | 0.10986 | -0.01831 | 123.056 | 122.7951 | 122.7493 | -0.39825 | 122.9919 | 122.9507 | 122.7951 | -0.37537
2764.9531 | 123.0286 | -122.8088 | 0.19684 | 0.045166 | 0.030441 | 0.0042298 | 0.0046911 | -0.005834 | 0.0026424 | -0.0030975 | 0.04097 | -0.0095639 | -0.008389 | -0.0026168 | 0.0058169 | -0.014862 | 0.018311 | -0.032043 | -0.054932 | 0 | 0.28381 | -0.041199 | -0.19684 | 0.022888 | 0.036621 | -0.082397 | 0.19226 | 0.16937 | -0.12817 | -0.19226 | 122.7676 | 122.612 | 0.086975 | 122.7768 | 122.8088 | 0.19684 | -0.17853 | 122.6807 | 122.6166 | -0.004577 | 122.8317 | 122.7264 | 0.10986 | -0.027465 | 123.0927 | 122.8271 | 122.7539 | -0.39368 | 123.0011 | 122.9782 | 122.8455 | -0.3891
2766.7031 | 123.0423 | -122.7905 | 0.1831 | 0.13672 | 0.027664 | 0.0050842 | 0.0040503 | -0.0064748 | 0.0011472 | -0.0058747 | 0.086746 | -0.010418 | -0.00668 | 0.00037379 | 0.0060305 | -0.013794 | 0.013733 | -0.027466 | -0.050354 | 0.004578 | 0.26093 | -0.045776 | -0.21057 | 0.027466 | 0.036621 | -0.082397 | 0.20599 | 0.15564 | -0.14191 | -0.16022 | 122.7448 | 122.58 | 0.07782 | 122.7631 | 122.7951 | 0.21515 | -0.16937 | 122.6486 | 122.6303 | 0.022889 | 122.818 | 122.7081 | 0.07782 | -0.027465 | 123.0515 | 122.8043 | 122.7402 | -0.39368 | 122.9965 | 122.9462 | 122.8271 | -0.34332
2768.3906 | 123.056 | -122.7859 | 0.17853 | 0.13672 | 0.027237 | 0.0027344 | 0.0053321 | -0.0079702 | -0.0018436 | -0.0052337 | 0.14778 | -0.011914 | -0.0092434 | -0.001976 | 0.0060305 | -0.012726 | 0.12817 | 0.10986 | 0.082397 | 0.10529 | 0.21057 | 0.004578 | -0.1831 | 0.1236 | 0.16937 | 0.050354 | 0.14648 | 0.1236 | -0.091553 | -0.14648 | 122.7905 | 122.6028 | 0.032043 | 122.8958 | 122.8912 | 0.28839 | -0.050354 | 122.6944 | 122.6395 | -0.032044 | 122.9095 | 122.8363 | 0.19684 | -0.054932 | 122.9965 | 122.9141 | 122.8683 | -0.36163 | 122.9324 | 122.9095 | 122.9553 | -0.32501
2770.1406 | 123.0469 | -122.7997 | 0.1831 | -0.092163 | 0.030228 | 0.0065796 | 0.0066137 | -0.0066884 | 0.0011472 | -0.0045929 | -0.11925 | -0.0099911 | -0.004971 | -0.0026168 | 0.0064577 | -0.013153 | 0.12817 | 0.10986 | 0.07782 | 0.10071 | 0.30212 | 0.013733 | -0.14648 | 0.082397 | 0.13733 | -0.018311 | 0.21973 | 0.18768 | -0.086975 | -0.15106 | 122.8134 | 122.6532 | 0.11902 | 122.9095 | 122.9004 | 0.24719 | -0.054931 | 122.7127 | 122.6486 | 0.036622 | 122.8821 | 122.7814 | 0.13275 | 0.004578 | 123.1018 | 122.9279 | 122.8775 | -0.32959 | 123.0194 | 122.9874 | 122.937 | -0.33417
2771.9062 | 123.0057 | -122.8043 | 0.21515 | 0.12146 | 0.025742 | 0.0055114 | 0.0057593 | -0.0071158 | -0.0052616 | -0.0069427 | 0.1783 | -0.011487 | -0.0068936 | -0.0032578 | 0.0047489 | -0.01358 | 0.073242 | 0.13733 | 0.10986 | 0.091553 | 0.20142 | -0.018311 | -0.15564 | 0.15106 | 0.19226 | 0.091553 | 0.17395 | 0.13733 | -0.064087 | -0.1236 | 122.7859 | 122.6486 | -0.013733 | 122.9416 | 122.8958 | 0.24719 | -0.14191 | 122.7402 | 122.6807 | -0.041199 | 122.9553 | 122.8958 | 0.21515 | -0.07782 | 123.0057 | 122.8775 | 122.9141 | -0.37079 | 122.9782 | 122.9416 | 122.9965 | -0.33875
2773.6562 | 123.1155 | -122.7951 | 0.16022 | -0.084534 | 0.028305 | 0.0055114 | 0.0059729 | -0.0060476 | 0.0022152 | -0.0067291 | -0.13451 | -0.010632 | -0.0028348 | -0.00069421 | 0.0056033 | -0.014221 | 0.14648 | 0.10529 | 0.068665 | 0.10071 | 0.31586 | 0.009155 | -0.14191 | 0.11444 | 0.15564 | 0.009155 | 0.21973 | 0.19226 | -0.091553 | -0.15106 | 122.8043 | 122.6532 | 0.15564 | 122.9004 | 122.8958 | 0.24262 | -0.013733 | 122.7036 | 122.644 | 0.05951 | 122.9095 | 122.8043 | 0.16022 | 0.032044 | 123.111 | 122.9416 | 122.8638 | -0.30212 | 123.0148 | 122.9874 | 122.9507 | -0.31128
2775.3438 | 123.0972 | -122.7768 | 0.1831 | -0.22186 | 0.027664 | 0.0072204 | 0.010459 | -0.0062612 | -0.0039798 | -0.0080109 | -0.17265 | -0.010205 | -0.0030484 | -0.0024032 | 0.0013309 | -0.013153 | 0.16022 | 0.20599 | 0.16479 | 0.1831 | 0.37079 | 0.09613 | -0.073242 | 0.12817 | 0.20142 | 0.073242 | 0.31586 | 0.26093 | -0.022888 | -0.073242 | 122.8729 | 122.7036 | 0.18768 | 122.9828 | 122.9599 | 0.25635 | -0.022888 | 122.7539 | 122.7036 | 0.13275 | 122.905 | 122.85 | 0.14648 | 0.07782 | 123.1476 | 122.937 | 122.9416 | -0.25635 | 123.0927 | 123.0377 | 122.9782 | -0.25635
2777.0469 | 123.1522 | -122.7631 | 0.16479 | -0.2066 | 0.030228 | 0.0072204 | 0.0061865 | -0.0049796 | 0.0015744 | -0.0080109 | -0.18791 | -0.0091367 | -0.0045438 | -0.00048061 | 0.0032535 | -0.014435 | 0.13275 | 0.11902 | 0.073242 | 0.11902 | 0.36163 | 0.041199 | -0.11902 | 0.10529 | 0.16479 | 0.018311 | 0.24719 | 0.19684 | -0.07782 | -0.14191 | 122.8043 | 122.644 | 0.19684 | 122.8821 | 122.8821 | 0.23804 | -0.032044 | 122.6852 | 122.6212 | 0.082397 | 122.8683 | 122.7814 | 0.16022 | 0.032043 | 123.1247 | 122.8958 | 122.8363 | -0.28381 | 123.0103 | 122.9599 | 122.9279 | -0.3067
2778.8125 | 123.1338 | -122.7539 | 0.16937 | -0.19135 | 0.028732 | 0.0076478 | 0.0072547 | -0.0060476 | -0.0012028 | -0.0050201 | -0.16502 | -0.012341 | -0.0051846 | -0.00069421 | 0.0088077 | -0.015075 | 0.12817 | 0.13733 | 0.082397 | 0.11902 | 0.36621 | 0.041199 | -0.10529 | 0.091553 | 0.16022 | 0.022888 | 0.23804 | 0.21515 | -0.082397 | -0.1236 | 122.7951 | 122.6486 | 0.19684 | 122.8912 | 122.8729 | 0.22431 | -0.041199 | 122.6715 | 122.6303 | 0.068664 | 122.8455 | 122.7768 | 0.14648 | 0.045776 | 123.1201 | 122.8821 | 122.8363 | -0.27466 | 122.9919 | 122.9691 | 122.9141 | -0.29297
2780.5781 | 123.1018 | -122.8043 | 0.17853 | -0.19897 | 0.027878 | 0.0065796 | 0.0066137 | -0.0073294 | -0.0029118 | -0.0073701 | -0.24895 | -0.010205 | -0.004971 | -0.0015488 | 0.0034671 | -0.012085 | 0.10071 | 0.15106 | 0.11902 | 0.12817 | 0.37994 | 0.086975 | -0.09613 | 0.10529 | 0.16479 | 0.059509 | 0.31128 | 0.27924 | -0.041199 | -0.09613 | 122.8912 | 122.7081 | 0.20142 | 122.9553 | 122.9324 | 0.2243 | -0.07782 | 122.7631 | 122.7081 | 0.13275 | 122.9095 | 122.8638 | 0.15564 | 0.10071 | 123.1842 | 122.905 | 122.9233 | -0.27466 | 123.1155 | 123.0835 | 122.9691 | -0.27466
2782.2812 | 123.0377 | -122.8226 | 0.18768 | 0.15961 | 0.028092 | 0.0038024 | 0.0034093 | -0.007543 | -0.0012028 | -0.0080109 | 0.20119 | -0.0091367 | -0.0079618 | -0.00069421 | 0.0051761 | -0.013794 | 0.091553 | 0.1236 | 0.082397 | 0.091553 | 0.20599 | -0.018311 | -0.17853 | 0.10986 | 0.14648 | 0.050354 | 0.14191 | 0.091553 | -0.086975 | -0.14648 | 122.8043 | 122.644 | 0.018311 | 122.9462 | 122.9141 | 0.27008 | -0.09613 | 122.7356 | 122.6761 | -0.045776 | 122.9324 | 122.8729 | 0.19684 | -0.09613 | 123.0286 | 122.9141 | 122.905 | -0.36621 | 122.9645 | 122.9141 | 122.9691 | -0.33417
2783.9688 | 122.9965 | -122.8088 | 0.19684 | 0.15961 | 0.026596 | 0.0052978 | 0.0027685 | -0.007543 | -0.0031254 | -0.0073701 | 0.1783 | -0.010632 | -0.0079618 | -0.0021896 | 0.0034671 | -0.013366 | 0.10529 | 0.1236 | 0.11444 | 0.09613 | 0.20142 | -0.009155 | -0.19684 | 0.15106 | 0.16937 | 0.082397 | 0.15564 | 0.13733 | -0.07782 | -0.13275 | 122.7997 | 122.612 | 0.004578 | 122.9324 | 122.905 | 0.29297 | -0.091552 | 122.731 | 122.6761 | -0.041198 | 122.9599 | 122.8912 | 0.21515 | -0.059509 | 123.0103 | 122.9141 | 122.9233 | -0.39368 | 122.9645 | 122.9462 | 122.9782 | -0.32959
2785.7344 | 123.0606 | -122.7997 | 0.17853 | 0.19775 | 0.028092 | 0.0072204 | 0.0036231 | -0.007543 | 7.902e-05 | -0.0065155 | 0.16304 | -0.012127 | -0.0075344 | -5.3406e-05 | 0.0064577 | -0.015289 | 0.07782 | 0.036621 | 0.032043 | 0.032043 | 0.23804 | -0.041199 | -0.19684 | 0.11444 | 0.13275 | 0.032043 | 0.16479 | 0.15106 | -0.09613 | -0.14648 | 122.7585 | 122.6028 | 0.059509 | 122.8363 | 122.8317 | 0.22888 | -0.10071 | 122.7036 | 122.6532 | -0.013733 | 122.9141 | 122.8317 | 0.17853 | -0.027466 | 123.0377 | 122.8775 | 122.8317 | -0.37537 | 122.9645 | 122.9507 | 122.9324 | -0.32501
2787.5 | 123.0515 | -122.8088 | 0.1831 | 0.0070193 | 0.023178 | 0.0070068 | 0.0057593 | -0.0090384 | -0.0076114 | -0.0084381 | 0.079117 | -0.011059 | -0.0068936 | -0.0034714 | 0.00026273 | -0.013366 | 0.13275 | 0.10986 | 0.14191 | 0.1236 | 0.31586 | 0.059509 | -0.10986 | 0.13733 | 0.19684 | 0.10071 | 0.24261 | 0.21057 | -0.022888 | -0.07782 | 122.8683 | 122.699 | 0.13275 | 122.9187 | 122.9324 | 0.23346 | -0.050354 | 122.7859 | 122.731 | 0.05951 | 122.9462 | 122.9095 | 0.17853 | 0.027466 | 123.1247 | 122.9416 | 122.9507 | -0.29297 | 123.0515 | 123.0194 | 123.0057 | -0.26092
2789.1875 | 123.056 | -122.7951 | 0.19226 | 0.12909 | 0.026383 | 0.007434 | 0.0053321 | -0.0062612 | 0.0013608 | -0.0086517 | 0.071487 | -0.0078549 | -0.0098844 | -0.00048061 | 0.0075259 | -0.016571 | 0.068665 | -0.050354 | -0.036621 | 0.004578 | 0.24719 | -0.050354 | -0.21057 | 0.032043 | 0.032043 | -0.059509 | 0.20142 | 0.1831 | -0.10529 | -0.17853 | 122.7448 | 122.5845 | 0.054931 | 122.7448 | 122.7997 | 0.21515 | -0.1236 | 122.6898 | 122.6166 | 0.009155 | 122.8271 | 122.7356 | 0.11902 | -0.009156 | 123.0423 | 122.8638 | 122.7585 | -0.40283 | 122.9965 | 122.9782 | 122.8271 | -0.37079
2790.9375 | 123.1155 | -122.7768 | 0.16937 | -0.22949 | 0.027023 | 0.0040162 | 0.0091773 | -0.0051932 | -0.0020572 | -0.0090791 | -0.24132 | -0.011273 | -0.0056118 | -0.0011216 | 0.0034671 | -0.01358 | 0.16479 | 0.12817 | 0.10986 | 0.1236 | 0.37994 | 0.082397 | -0.091553 | 0.10986 | 0.16937 | 0.050354 | 0.3067 | 0.27466 | -0.041199 | -0.082397 | 122.8592 | 122.6852 | 0.21057 | 122.905 | 122.9004 | 0.21515 | -0.004578 | 122.7356 | 122.6944 | 0.13733 | 122.8867 | 122.8271 | 0.13275 | 0.10529 | 123.1567 | 122.9416 | 122.8867 | -0.26093 | 123.0835 | 123.0515 | 122.9462 | -0.25177
2792.625 | 123.0743 | -122.8088 | 0.17395 | 0.13672 | 0.027451 | 0.0070068 | 0.0046911 | -0.0060476 | 0.0020016 | -0.0065155 | 0.11726 | -0.010418 | -0.0090298 | -0.001976 | 0.0060305 | -0.012726 | 0.073242 | -0.013733 | -0.018311 | 0.013733 | 0.29755 | -0.041199 | -0.19684 | 0.073242 | 0.064087 | -0.041199 | 0.18768 | 0.16022 | -0.10529 | -0.16937 | 122.7676 | 122.612 | 0.1236 | 122.7951 | 122.8226 | 0.21057 | -0.10071 | 122.7036 | 122.6395 | 0.013733 | 122.8821 | 122.7676 | 0.12817 | -0.013733 | 123.1064 | 122.8821 | 122.7905 | -0.37079 | 122.9965 | 122.9691 | 122.8729 | -0.34332
2794.3125 | 123.0057 | -122.8088 | 0.20142 | 0.068054 | 0.029373 | 0.0048706 | 0.0049047 | -0.0056204 | 0.003497 | -0.0045929 | -0.035324 | -0.0097775 | -0.0056118 | -0.0013352 | 0.0090213 | -0.014007 | 0.032043 | -0.027466 | -0.041199 | 0.004578 | 0.2655 | -0.045776 | -0.20142 | -0.009155 | 0.018311 | -0.10529 | 0.19684 | 0.16937 | -0.14191 | -0.1831 | 122.7631 | 122.6074 | 0.064087 | 122.7814 | 122.8134 | 0.20599 | -0.16937 | 122.6669 | 122.6257 | -0.004578 | 122.7997 | 122.7036 | 0.077819 | -0.032043 | 123.0743 | 122.8409 | 122.7676 | -0.40283 | 123.0057 | 122.9782 | 122.8271 | -0.38452
2796.0156 | 123.0469 | -122.7997 | 0.19226 | 0.16724 | 0.028092 | 0.0035888 | 0.0036231 | -0.0077566 | 0.0011472 | -0.0075837 | 0.13252 | -0.012555 | -0.008389 | -0.001976 | 0.0053897 | -0.013794 | 0.10529 | 0.091553 | 0.086975 | 0.082397 | 0.21515 | -0.022888 | -0.18768 | 0.11902 | 0.16022 | 0.045776 | 0.15106 | 0.12817 | -0.091553 | -0.14648 | 122.7768 | 122.612 | 0.022888 | 122.8912 | 122.8821 | 0.27008 | -0.086975 | 122.7081 | 122.6532 | -0.041199 | 122.9187 | 122.8455 | 0.19226 | -0.064087 | 123.0148 | 122.905 | 122.8867 | -0.37994 | 122.9507 | 122.9279 | 122.9599 | -0.33874
2797.7188 | 123.1155 | -122.7859 | 0.17853 | -0.0082397 | 0.027664 | 0.004657 | 0.0078955 | -0.010106 | -0.0063296 | -0.0088653 | 0.071487 | -0.012982 | -0.0062528 | -0.0026168 | -0.00016447 | -0.014221 | 0.12817 | 0.14648 | 0.14191 | 0.12817 | 0.31128 | 0.064087 | -0.086975 | 0.16022 | 0.24261 | 0.1236 | 0.22888 | 0.21515 | -0.032043 | -0.064087 | 122.85 | 122.699 | 0.13275 | 122.9324 | 122.9141 | 0.21515 | -0.050354 | 122.7539 | 122.7219 | 0.050354 | 122.9462 | 122.9095 | 0.18768 | 0.036621 | 123.0972 | 122.9141 | 122.9279 | -0.2655 | 123.0148 | 123.0011 | 123.0286 | -0.24261
2799.4844 | 123.1247 | -122.7585 | 0.17395 | -0.22949 | 0.027878 | 0.004657 | 0.0085363 | -0.007543 | -0.0037662 | -0.0073701 | -0.14214 | -0.011059 | -0.0051846 | -0.0013352 | 0.0019717 | -0.014007 | 0.23804 | 0.26093 | 0.24719 | 0.21973 | 0.33875 | 0.10529 | -0.059509 | 0.23346 | 0.29755 | 0.17853 | 0.24719 | 0.22888 | 0 | -0.032043 | 122.8638 | 122.699 | 0.1648 | 123.0194 | 122.9782 | 0.27924 | 0.064087 | 122.7585 | 122.7264 | 0.073242 | 122.9919 | 122.937 | 0.21057 | 0.054932 | 123.0972 | 122.9965 | 123.0057 | -0.23346 | 123.0057 | 122.9874 | 123.056 | -0.20599
2801.1719 | 123.1476 | -122.7722 | 0.15564 | -0.12268 | 0.029373 | 0.0033752 | 0.0085363 | -0.0079702 | 0.0028562 | -0.0075837 | -0.14977 | -0.012341 | -0.003262 | -5.3406e-05 | 0.0056033 | -0.016998 | 0.17853 | 0.10071 | 0.068665 | 0.10529 | 0.32044 | 0.022888 | -0.14191 | 0.11444 | 0.16937 | -0.004578 | 0.21057 | 0.19684 | -0.10986 | -0.13733 | 122.7951 | 122.6303 | 0.1648 | 122.8729 | 122.8775 | 0.24719 | 0.022888 | 122.6624 | 122.6349 | 0.054931 | 122.8867 | 122.7676 | 0.13275 | 0.041198 | 123.0927 | 122.9507 | 122.8409 | -0.29755 | 122.9828 | 122.9691 | 122.9416 | -0.29297
2802.9219 | 123.1247 | -122.7493 | 0.16937 | -0.092163 | 0.031723 | 0.004657 | 0.0076819 | -0.0081838 | 0.0011472 | -0.0065155 | -0.17265 | -0.0089229 | -0.0030484 | 0.00037379 | 0.0041079 | -0.015716 | 0.13733 | 0.11902 | 0.073242 | 0.11902 | 0.3067 | 0.013733 | -0.14648 | 0.11902 | 0.14648 | -0.004578 | 0.2243 | 0.19226 | -0.082397 | -0.14648 | 122.7631 | 122.6028 | 0.13733 | 122.8683 | 122.8683 | 0.2655 | -0.032044 | 122.6669 | 122.6028 | 0.054931 | 122.8683 | 122.7448 | 0.14191 | 0.022888 | 123.056 | 122.8867 | 122.8226 | -0.31586 | 122.9736 | 122.9416 | 122.8958 | -0.31586
2804.6719 | 123.1155 | -122.7768 | 0.17853 | -0.16083 | 0.024246 | 0.0055114 | 0.0098181 | -0.0088248 | -0.006757 | -0.0069427 | -0.16502 | -0.011914 | -0.0056118 | -0.001976 | 0.0013309 | -0.013366 | 0.21515 | 0.28839 | 0.24719 | 0.21515 | 0.32959 | 0.082397 | -0.054932 | 0.24261 | 0.33417 | 0.20142 | 0.2655 | 0.2243 | 0.022888 | -0.032043 | 122.8592 | 122.7219 | 0.15106 | 123.0652 | 122.9919 | 0.27008 | 0.036621 | 122.7997 | 122.7448 | 0.086975 | 123.0194 | 122.9782 | 0.23346 | 0.045776 | 123.1064 | 122.9919 | 123.024 | -0.23346 | 123.0423 | 123.0011 | 123.111 | -0.21057
2806.375 | 123.0469 | -122.7997 | 0.18768 | 0.14435 | 0.025528 | 0.0065796 | 0.0036231 | -0.0069022 | -0.00163 | -0.0043793 | 0.17067 | -0.0117 | -0.008389 | -0.00090781 | 0.0058169 | -0.014007 | 0.10986 | 0.1236 | 0.086975 | 0.082397 | 0.21973 | -0.018311 | -0.16937 | 0.13275 | 0.16022 | 0.054932 | 0.15106 | 0.11902 | -0.11444 | -0.15106 | 122.7814 | 122.6303 | 0.032044 | 122.9233 | 122.8821 | 0.25177 | -0.07782 | 122.6852 | 122.6486 | -0.036621 | 122.9324 | 122.8546 | 0.20599 | -0.068664 | 123.0194 | 122.9095 | 122.8867 | -0.35706 | 122.9507 | 122.9187 | 122.9599 | -0.33874
2808.125 | 123.0194 | -122.8363 | 0.20599 | 0.15961 | 0.026596 | 0.0038024 | 0.0034093 | -0.0083974 | -0.0035526 | -0.0060883 | 0.11726 | -0.012127 | -0.0088162 | -0.0028306 | 0.0056033 | -0.014007 | 0.10529 | 0.13733 | 0.09613 | 0.091553 | 0.20599 | -0.009155 | -0.16022 | 0.16022 | 0.17395 | 0.064087 | 0.15564 | 0.12817 | -0.07782 | -0.11902 | 122.8271 | 122.6761 | 0 | 122.9736 | 122.9279 | 0.25177 | -0.10071 | 122.7585 | 122.7173 | -0.050354 | 122.9965 | 122.9004 | 0.18311 | -0.07782 | 123.0423 | 122.9416 | 122.9324 | -0.36621 | 122.9919 | 122.9645 | 123.0103 | -0.32501
2809.875 | 123.1338 | -122.7402 | 0.15106 | -0.13031 | 0.026596 | 0.0070068 | 0.0070409 | -0.010106 | -0.0065434 | -0.0080109 | -0.035324 | -0.012341 | -0.0068936 | -0.0017624 | 0.0021853 | -0.013366 | 0.21973 | 0.26093 | 0.22888 | 0.20599 | 0.35248 | 0.10529 | -0.064087 | 0.25177 | 0.3067 | 0.19226 | 0.25177 | 0.21057 | 0.013733 | -0.045776 | 122.8455 | 122.6761 | 0.20142 | 123.0011 | 122.9462 | 0.27008 | 0.068665 | 122.7539 | 122.6944 | 0.10071 | 122.9919 | 122.9324 | 0.23804 | 0.059509 | 123.0927 | 122.9599 | 122.9691 | -0.21515 | 122.9919 | 122.9507 | 123.0469 | -0.19684
2811.625 | 123.0194 | -122.8043 | 0.19226 | 0.1062 | 0.026169 | 0.0059388 | 0.0027685 | -0.0077566 | -0.0024844 | -0.0080109 | 0.13252 | -0.011059 | -0.0079618 | -0.0024032 | 0.0058169 | -0.013153 | 0.13275 | 0.11902 | 0.10986 | 0.082397 | 0.25177 | 0.022888 | -0.15106 | 0.16937 | 0.1831 | 0.073242 | 0.20599 | 0.16479 | -0.059509 | -0.10071 | 122.8271 | 122.6532 | 0.059509 | 122.9233 | 122.8867 | 0.23346 | -0.05951 | 122.7448 | 122.7036 | 0.013733 | 122.9736 | 122.8775 | 0.17395 | -0.027466 | 123.056 | 122.937 | 122.9141 | -0.34332 | 123.0103 | 122.9691 | 122.9874 | -0.29297
2813.3125 | 123.0972 | -122.7905 | 0.16937 | -0.2066 | 0.026383 | 0.0048706 | 0.0089635 | -0.0090384 | -0.00013458 | -0.0088653 | -0.25658 | -0.010418 | -0.0039028 | -0.0017624 | 0.0030399 | -0.01593 | 0.15564 | 0.11444 | 0.10986 | 0.13275 | 0.3891 | 0.054932 | -0.10071 | 0.12817 | 0.17395 | 0.045776 | 0.29755 | 0.25635 | -0.045776 | -0.086975 | 122.8455 | 122.6898 | 0.21973 | 122.905 | 122.9233 | 0.23346 | -0.013733 | 122.7448 | 122.7036 | 0.12817 | 122.9187 | 122.8363 | 0.13275 | 0.086975 | 123.1796 | 122.9462 | 122.9004 | -0.27008 | 123.0881 | 123.0469 | 122.9645 | -0.25635
2815.0625 | 123.024 | -122.8317 | 0.19684 | 0.083313 | 0.0298 | 0.0072204 | 0.0059729 | -0.0060476 | 0.0015744 | -0.0075837 | 0.025711 | -0.0074277 | -0.0036892 | -0.00026701 | 0.0077395 | -0.014862 | 0.050354 | -0.041199 | -0.054932 | 0 | 0.27466 | -0.036621 | -0.20599 | 0.036621 | 0.018311 | -0.091553 | 0.18768 | 0.16479 | -0.1236 | -0.20599 | 122.7951 | 122.6257 | 0.07782 | 122.7905 | 122.8317 | 0.20599 | -0.14648 | 122.7081 | 122.6257 | -0.009155 | 122.8683 | 122.7402 | 0.11444 | -0.032043 | 123.1064 | 122.8821 | 122.7768 | -0.40283 | 123.0194 | 122.9965 | 122.85 | -0.40283
2816.8125 | 123.0103 | -122.8271 | 0.20142 | 0.090942 | 0.032364 | 0.0038024 | 0.0070409 | -0.007543 | 0.0037106 | -0.0037385 | -0.035324 | -0.010205 | -0.0039028 | -5.3406e-05 | 0.0064577 | -0.012512 | 0.045776 | -0.018311 | -0.027466 | 0.009155 | 0.27924 | -0.050354 | -0.20142 | 0.018311 | 0.018311 | -0.11444 | 0.20599 | 0.17395 | -0.1236 | -0.17853 | 122.7768 | 122.6257 | 0.07782 | 122.8088 | 122.8363 | 0.21057 | -0.15564 | 122.7036 | 122.6486 | 0.004578 | 122.8455 | 122.7127 | 0.064087 | -0.027466 | 123.1064 | 122.8729 | 122.7997 | -0.40283 | 123.0331 | 123.0011 | 122.8455 | -0.37994
2818.5781 | 123.0469 | -122.8226 | 0.21973 | -0.069275 | 0.030228 | 0.0050842 | 0.0057593 | -0.0045522 | 0.004565 | -0.0054475 | -0.08873 | -0.0082821 | -0.0058254 | -0.0015488 | 0.0060305 | -0.011444 | 0.11902 | 0.082397 | 0.045776 | 0.073242 | 0.28381 | -0.004578 | -0.15106 | 0.07782 | 0.09613 | -0.050354 | 0.21515 | 0.17853 | -0.1236 | -0.15564 | 122.818 | 122.6715 | 0.064086 | 122.905 | 122.8958 | 0.2243 | -0.10071 | 122.699 | 122.6669 | -0.004578 | 122.9004 | 122.7722 | 0.10529 | -0.041199 | 123.1064 | 122.9416 | 122.8683 | -0.37079 | 123.0377 | 123.0011 | 122.9187 | -0.37537
2820.3281 | 123.1247 | -122.7585 | 0.15106 | 0.014648 | 0.023178 | 0.0076478 | 0.0074683 | -0.009252 | -0.0080386 | -0.0063019 | 0.056228 | -0.012341 | -0.0053982 | -0.001976 | 0.0011173 | -0.012726 | 0.09613 | 0.15106 | 0.14648 | 0.14191 | 0.29755 | 0.045776 | -0.10986 | 0.17395 | 0.23346 | 0.13733 | 0.24719 | 0.19684 | -0.027466 | -0.082397 | 122.8043 | 122.6486 | 0.14648 | 122.9095 | 122.9004 | 0.25177 | -0.054932 | 122.731 | 122.6761 | 0.09613 | 122.9324 | 122.8958 | 0.21973 | 0.045776 | 123.056 | 122.8546 | 122.905 | -0.26093 | 123.0057 | 122.9553 | 122.9919 | -0.23346
2822.0156 | 123.056 | -122.8043 | 0.19684 | -0.061646 | 0.030228 | 0.006366 | 0.0066137 | -0.0071158 | 0.0043514 | -0.0052337 | -0.11162 | -0.0089229 | -0.004971 | 0.00037379 | 0.0081667 | -0.01593 | 0.13275 | 0.091553 | 0.045776 | 0.10071 | 0.28381 | 0.004578 | -0.16022 | 0.091553 | 0.11902 | -0.027466 | 0.21515 | 0.19684 | -0.09613 | -0.14648 | 122.8088 | 122.644 | 0.086975 | 122.8958 | 122.905 | 0.26093 | -0.064087 | 122.7081 | 122.6578 | 0.018311 | 122.8958 | 122.7768 | 0.11902 | 0 | 123.0881 | 122.937 | 122.85 | -0.35706 | 123.0194 | 123.0011 | 122.9233 | -0.34332
2823.7812 | 123.0194 | -122.8317 | 0.20142 | -0.00061023 | 0.030441 | 0.0033752 | 0.0059729 | -0.0071158 | 0.0026424 | -0.0058747 | 0.025711 | -0.0091367 | -0.0058254 | 0.00016019 | 0.0053897 | -0.015075 | 0.059509 | 0.022888 | -0.013733 | 0.032043 | 0.26093 | -0.032043 | -0.18768 | 0.013733 | 0.050354 | -0.07782 | 0.19684 | 0.16937 | -0.13733 | -0.18768 | 122.7997 | 122.644 | 0.059509 | 122.8546 | 122.8638 | 0.21973 | -0.14191 | 122.6944 | 122.644 | -0.004578 | 122.8455 | 122.7539 | 0.10986 | -0.032043 | 123.0927 | 122.8912 | 122.818 | -0.3891 | 123.0286 | 123.0011 | 122.8821 | -0.3891
2825.4688 | 123.0469 | -122.7905 | 0.21057 | 0.083313 | 0.031296 | 0.0014526 | 0.0064001 | -0.0081838 | 0.0020016 | -0.0041657 | 0.071487 | -0.0084957 | -0.0058254 | -0.0011216 | 0.0064577 | -0.014007 | -0.004578 | -0.013733 | -0.032043 | -0.004578 | 0.25177 | -0.050354 | -0.21057 | 0.022888 | 0.022888 | -0.073242 | 0.19684 | 0.16479 | -0.11444 | -0.17853 | 122.7402 | 122.58 | 0.041199 | 122.7768 | 122.7859 | 0.20599 | -0.21515 | 122.6761 | 122.612 | -0.013733 | 122.8134 | 122.7173 | 0.10529 | -0.045776 | 123.0423 | 122.7859 | 122.7585 | -0.42114 | 122.9874 | 122.9553 | 122.8134 | -0.3891
2827.2188 | 123.0286 | -122.818 | 0.19226 | 0.045166 | 0.031082 | 0.0048706 | 0.0089635 | -0.0069022 | 0.00050622 | -0.0065155 | 0.14015 | -0.0095639 | -0.0030484 | 0.0010148 | 0.0056033 | -0.012512 | -0.009155 | -0.050354 | -0.059509 | -0.009155 | 0.25635 | -0.050354 | -0.21515 | 0.004578 | 0.022888 | -0.07782 | 0.19226 | 0.13733 | -0.14191 | -0.18768 | 122.7676 | 122.6028 | 0.064087 | 122.7676 | 122.8088 | 0.20599 | -0.20142 | 122.6761 | 122.6303 | 0 | 122.8226 | 122.7402 | 0.10986 | -0.054932 | 123.0743 | 122.8088 | 122.7585 | -0.40741 | 123.0103 | 122.9553 | 122.8409 | -0.37994
2828.9844 | 123.0469 | -122.8271 | 0.17853 | 0.1825 | 0.028519 | 0.0027344 | 0.0049047 | -0.0088248 | -0.0022708 | -0.0048065 | 0.2317 | -0.011273 | -0.0043302 | -0.0011216 | 0.0049625 | -0.01358 | 0.07782 | 0.1236 | 0.086975 | 0.091553 | 0.20142 | -0.022888 | -0.16479 | 0.13275 | 0.16022 | 0.045776 | 0.14191 | 0.10986 | -0.1236 | -0.16022 | 122.8043 | 122.6624 | 0.022888 | 122.9507 | 122.9187 | 0.25635 | -0.10071 | 122.7036 | 122.6669 | -0.036621 | 122.9599 | 122.8729 | 0.20599 | -0.068665 | 123.0286 | 122.905 | 122.9141 | -0.34332 | 122.9691 | 122.937 | 122.9874 | -0.33874
2830.6875 | 123.0057 | -122.8226 | 0.19226 | 0.15961 | 0.027664 | 0.004657 | 0.0042639 | -0.0062612 | -0.0037662 | -0.0058747 | 0.18593 | -0.011059 | -0.0062528 | 0.00016019 | 0.0026125 | -0.013366 | 0.091553 | 0.13733 | 0.10529 | 0.082397 | 0.19684 | 0 | -0.16937 | 0.15106 | 0.18768 | 0.086975 | 0.16022 | 0.13733 | -0.082397 | -0.13275 | 122.8226 | 122.6532 | 0.004577 | 122.9599 | 122.905 | 0.25177 | -0.10071 | 122.7402 | 122.6898 | -0.032044 | 122.9736 | 122.9095 | 0.21973 | -0.054932 | 123.0194 | 122.9141 | 122.9279 | -0.36163 | 122.9828 | 122.9599 | 123.0103 | -0.32501
2832.4531 | 123.1476 | -122.7814 | 0.14648 | -0.0082397 | 0.025955 | 0.007434 | 0.0078955 | -0.0054068 | -0.0056888 | -0.0097199 | 0.018082 | -0.010846 | -0.0086026 | -0.0034714 | 0.00047633 | -0.012298 | 0.10986 | 0.16479 | 0.15106 | 0.16022 | 0.31586 | 0.050354 | -0.10071 | 0.18768 | 0.2655 | 0.16937 | 0.25177 | 0.21973 | -0.036621 | -0.054932 | 122.8317 | 122.6807 | 0.16937 | 122.9462 | 122.9416 | 0.26093 | -0.036621 | 122.7448 | 122.7264 | 0.10529 | 122.9691 | 122.9507 | 0.22431 | 0.073243 | 123.0972 | 122.8912 | 122.9324 | -0.24719 | 123.0331 | 123.0011 | 123.0469 | -0.20142
2834.1562 | 123.1613 | -122.7814 | 0.16479 | -0.1532 | 0.029373 | 0.0042298 | 0.0072547 | -0.0056204 | 0.001788 | -0.0071563 | -0.27946 | -0.010205 | -0.0028348 | -0.00026701 | 0.0058169 | -0.015716 | 0.13275 | 0.10986 | 0.07782 | 0.13275 | 0.37079 | 0.050354 | -0.11902 | 0.11902 | 0.15564 | 0.022888 | 0.27924 | 0.22888 | -0.064087 | -0.10529 | 122.8317 | 122.6624 | 0.20599 | 122.8912 | 122.9141 | 0.25177 | -0.032044 | 122.7173 | 122.6761 | 0.11444 | 122.9004 | 122.8043 | 0.12817 | 0.064087 | 123.1522 | 122.9141 | 122.8592 | -0.28381 | 123.0606 | 123.0103 | 122.937 | -0.27008
2835.9219 | 123.1338 | -122.7631 | 0.17395 | -0.031128 | 0.024887 | 0.004657 | 0.0078955 | -0.0094656 | -0.005048 | -0.0099335 | 0.010452 | -0.011914 | -0.0039028 | -0.0024032 | 4.9132e-05 | -0.01358 | 0.10071 | 0.17395 | 0.15564 | 0.15106 | 0.3067 | 0.059509 | -0.091553 | 0.17853 | 0.25635 | 0.15564 | 0.23346 | 0.20599 | -0.022888 | -0.07782 | 122.8226 | 122.6715 | 0.13275 | 122.937 | 122.9141 | 0.24261 | -0.073242 | 122.7402 | 122.6852 | 0.059509 | 122.9416 | 122.9187 | 0.23346 | 0.032044 | 123.0698 | 122.8638 | 122.9187 | -0.2655 | 122.9965 | 122.9691 | 123.0194 | -0.25177
2837.6875 | 123.056 | -122.7814 | 0.1831 | 0.029907 | 0.026169 | 0.0052978 | 0.0064001 | -0.0066884 | -0.004407 | -0.0095063 | 0.079117 | -0.0117 | -0.0056118 | -0.0011216 | 0.0038943 | -0.012512 | 0.10529 | 0.13275 | 0.13275 | 0.12817 | 0.32044 | 0.032043 | -0.11444 | 0.13733 | 0.19226 | 0.10986 | 0.23346 | 0.21515 | -0.032043 | -0.09613 | 122.8134 | 122.6669 | 0.13733 | 122.9141 | 122.9095 | 0.24262 | -0.077819 | 122.7493 | 122.6852 | 0.050354 | 122.9187 | 122.8912 | 0.20599 | 0.032044 | 123.1018 | 122.8867 | 122.9141 | -0.29755 | 123.0148 | 122.9965 | 122.9736 | -0.27924
2839.3906 | 123.1476 | -122.7631 | 0.16937 | -0.12268 | 0.025314 | 0.0061524 | 0.0051183 | -0.008611 | -0.00077538 | -0.010361 | -0.042954 | -0.011273 | -0.007748 | -0.0026168 | 0.0013309 | -0.016784 | 0.23804 | 0.25635 | 0.21515 | 0.19684 | 0.32501 | 0.086975 | -0.064087 | 0.2655 | 0.31128 | 0.19226 | 0.25177 | 0.21515 | 0.004578 | -0.050354 | 122.85 | 122.699 | 0.15564 | 123.0194 | 122.9599 | 0.26093 | 0.068664 | 122.7676 | 122.7127 | 0.082397 | 123.0286 | 122.9553 | 0.24261 | 0.045776 | 123.0881 | 123.0011 | 122.9782 | -0.23346 | 123.0148 | 122.9782 | 123.0743 | -0.21973
2841.1406 | 123.0606 | -122.7951 | 0.19226 | 0.15961 | 0.027878 | 0.0042298 | 0.0034093 | -0.0081838 | 0.0041378 | -0.0052337 | 0.11726 | -0.010632 | -0.0073208 | 0.00016019 | 0.0075259 | -0.017212 | 0.059509 | 0.018311 | -0.013733 | -0.018311 | 0.24261 | -0.054932 | -0.20599 | 0.10529 | 0.082397 | 0 | 0.19226 | 0.13733 | -0.10986 | -0.16022 | 122.7402 | 122.5891 | 0.050354 | 122.8134 | 122.7768 | 0.18768 | -0.13275 | 122.6852 | 122.6349 | 0 | 122.9004 | 122.7951 | 0.16022 | -0.054932 | 123.0377 | 122.8546 | 122.7814 | -0.39826 | 122.9874 | 122.9324 | 122.8775 | -0.35248
2842.9062 | 123.1155 | -122.7859 | 0.18768 | -0.25238 | 0.026169 | 0.0061524 | 0.0078955 | -0.0090384 | -0.00077538 | -0.0075837 | -0.2108 | -0.010205 | -0.007748 | -0.0015488 | 0.0019717 | -0.012939 | 0.17853 | 0.15564 | 0.11902 | 0.13275 | 0.39368 | 0.086975 | -0.07782 | 0.13275 | 0.17395 | 0.054932 | 0.28839 | 0.26093 | -0.045776 | -0.091553 | 122.8729 | 122.7081 | 0.20599 | 122.9416 | 122.9187 | 0.21057 | -0.009155 | 122.7402 | 122.6944 | 0.10071 | 122.9187 | 122.8409 | 0.14649 | 0.073242 | 123.1796 | 122.9645 | 122.905 | -0.2655 | 123.0743 | 123.0469 | 122.9599 | -0.27924
2844.6719 | 123.0469 | -122.8043 | 0.17395 | 0.029907 | 0.027664 | 0.0042298 | 0.0064001 | -0.0096792 | -0.0014164 | -0.0080109 | 0.048599 | -0.011914 | -0.004971 | -5.3406e-05 | 0.0019717 | -0.013153 | 0.10986 | 0.14648 | 0.11902 | 0.1236 | 0.31128 | 0.036621 | -0.11444 | 0.15106 | 0.18768 | 0.09613 | 0.23804 | 0.19684 | -0.032043 | -0.086975 | 122.8409 | 122.6898 | 0.13733 | 122.9507 | 122.9279 | 0.23804 | -0.064087 | 122.7722 | 122.7173 | 0.064087 | 122.9553 | 122.9004 | 0.1831 | 0.022888 | 123.1155 | 122.9141 | 122.9233 | -0.28839 | 123.0423 | 123.0011 | 122.9919 | -0.26092
2846.375 | 123.0377 | -122.7997 | 0.20599 | 0.15961 | 0.028946 | 0.0059388 | 0.0038367 | -0.0071158 | 0.0043514 | -0.0039521 | 0.056228 | -0.010632 | -0.0071072 | 0.00058739 | 0.0073123 | -0.015503 | 0.032043 | -0.032043 | -0.050354 | 0 | 0.27008 | -0.064087 | -0.20142 | 0.045776 | 0.032043 | -0.07782 | 0.19226 | 0.17395 | -0.11902 | -0.17853 | 122.7356 | 122.5983 | 0.064087 | 122.7676 | 122.7997 | 0.20142 | -0.17395 | 122.6807 | 122.6212 | -0.013733 | 122.8455 | 122.7219 | 0.10071 | -0.032044 | 123.0698 | 122.8317 | 122.7493 | -0.40741 | 122.9919 | 122.9736 | 122.8317 | -0.38452
2848.125 | 123.1567 | -122.7859 | 0.16937 | -0.1532 | 0.028305 | 0.007434 | 0.0057593 | -0.0071158 | 0.0022152 | -0.0048065 | -0.19554 | -0.011273 | -0.0071072 | -0.0021896 | 0.0070987 | -0.015075 | 0.14648 | 0.12817 | 0.07782 | 0.11902 | 0.3479 | 0.004578 | -0.12817 | 0.10986 | 0.16022 | 0.013733 | 0.24261 | 0.19684 | -0.07782 | -0.13275 | 122.7905 | 122.6578 | 0.17853 | 122.9141 | 122.905 | 0.24719 | -0.022889 | 122.7081 | 122.6532 | 0.073242 | 122.8958 | 122.7997 | 0.14648 | 0.027465 | 123.1338 | 122.9324 | 122.8638 | -0.29755 | 123.0286 | 122.9828 | 122.9462 | -0.30212
2849.8281 | 123.0515 | -122.8088 | 0.19226 | 0.12146 | 0.028946 | 0.0033752 | 0.0031957 | -0.0073294 | 0.00071982 | -0.0058747 | 0.071487 | -0.011059 | -0.008389 | -0.001976 | 0.0066715 | -0.012512 | 0.009155 | -0.004578 | -0.050354 | -0.009155 | 0.26093 | -0.059509 | -0.20599 | 0.022888 | 0.013733 | -0.086975 | 0.19684 | 0.16022 | -0.13733 | -0.19226 | 122.7493 | 122.6028 | 0.068664 | 122.8043 | 122.7997 | 0.19684 | -0.18311 | 122.6715 | 122.6166 | 0.004577 | 122.8317 | 122.7219 | 0.10529 | -0.032044 | 123.0698 | 122.818 | 122.7585 | -0.39826 | 123.0057 | 122.9691 | 122.8226 | -0.38452
2851.5938 | 123.024 | -122.8363 | 0.21057 | 0.029907 | 0.031296 | 0.0061524 | 0.0053321 | -0.0064748 | 0.0011472 | -0.0035249 | -0.020065 | -0.011059 | -0.0041164 | -0.00090781 | 0.0053897 | -0.012726 | 0.022888 | 0.036621 | -0.018311 | 0.032043 | 0.27008 | -0.054932 | -0.20142 | 0.004578 | 0.032043 | -0.10529 | 0.19684 | 0.16022 | -0.12817 | -0.17395 | 122.7814 | 122.6349 | 0.05951 | 122.8729 | 122.8683 | 0.23346 | -0.18768 | 122.7081 | 122.6624 | -0.013733 | 122.8409 | 122.731 | 0.068664 | -0.050354 | 123.1064 | 122.8592 | 122.818 | -0.41199 | 123.0331 | 122.9965 | 122.8683 | -0.38452
2853.2969 | 123.1247 | -122.7631 | 0.16479 | -0.1532 | 0.025314 | 0.0055114 | 0.0081091 | -0.01032 | -0.006757 | -0.0063019 | -0.10399 | -0.012768 | -0.0056118 | -0.00048061 | 0.0023989 | -0.012939 | 0.19684 | 0.29297 | 0.24719 | 0.19684 | 0.32501 | 0.082397 | -0.059509 | 0.22888 | 0.34332 | 0.19226 | 0.2655 | 0.22888 | 0.004578 | -0.041199 | 122.8455 | 122.7036 | 0.16022 | 123.056 | 122.9599 | 0.25635 | 0.032043 | 122.7676 | 122.7219 | 0.10071 | 122.9919 | 122.9553 | 0.23346 | 0.064087 | 123.0881 | 122.9599 | 123.0103 | -0.2243 | 123.0286 | 122.9919 | 123.1064 | -0.20599
2855.0469 | 123.0331 | -122.8226 | 0.19226 | 0.060425 | 0.029587 | 0.0057252 | 0.0055457 | -0.0064748 | 0.005206 | -0.0075837 | 0.010452 | -0.0093503 | -0.0045438 | -0.0017624 | 0.0056033 | -0.01593 | 0.032043 | 0 | -0.036621 | 0.022888 | 0.29297 | -0.022888 | -0.21057 | 0.009155 | 0.041199 | -0.09613 | 0.19684 | 0.16937 | -0.13275 | -0.19226 | 122.7997 | 122.612 | 0.10071 | 122.8226 | 122.8455 | 0.23346 | -0.16022 | 122.6898 | 122.6303 | 0.004577 | 122.8317 | 122.7264 | 0.096131 | -0.022888 | 123.1155 | 122.8546 | 122.7859 | -0.40283 | 123.0194 | 122.9919 | 122.8638 | -0.38452
2856.8125 | 123.1567 | -122.7768 | 0.15106 | -0.22186 | 0.026169 | 0.0067932 | 0.0051183 | -0.0066884 | -0.0029118 | -0.0071563 | -0.20317 | -0.0089229 | -0.008389 | -0.0032578 | 0.0060305 | -0.013366 | 0.11902 | 0.13275 | 0.10071 | 0.14648 | 0.37994 | 0.068665 | -0.091553 | 0.082397 | 0.15564 | 0.022888 | 0.29297 | 0.27008 | -0.054932 | -0.10071 | 122.8455 | 122.6852 | 0.22888 | 122.9095 | 122.9233 | 0.23804 | -0.032043 | 122.7219 | 122.6761 | 0.14191 | 122.8592 | 122.7997 | 0.1236 | 0.11902 | 123.1567 | 122.8958 | 122.8775 | -0.24261 | 123.0698 | 123.0469 | 122.9324 | -0.25177
2858.5781 | 123.1613 | -122.7814 | 0.17395 | -0.27527 | 0.02916 | 0.0057252 | 0.0078955 | -0.0066884 | -0.00098918 | -0.0071563 | -0.2108 | -0.010205 | -0.0062528 | -0.0015488 | 0.0030399 | -0.012085 | 0.15564 | 0.13275 | 0.10529 | 0.14191 | 0.41657 | 0.07782 | -0.064087 | 0.086975 | 0.15564 | 0.032043 | 0.31128 | 0.2655 | -0.036621 | -0.10071 | 122.8592 | 122.7173 | 0.24262 | 122.9141 | 122.9233 | 0.20599 | -0.01831 | 122.7448 | 122.6807 | 0.13733 | 122.8683 | 122.8134 | 0.13275 | 0.091553 | 123.1979 | 122.937 | 122.8867 | -0.23804 | 123.0927 | 123.0469 | 122.937 | -0.27466
2860.3281 | 123.111 | -122.7814 | 0.16022 | -0.21423 | 0.026169 | 0.0085022 | 0.0053321 | -0.0079702 | -0.004407 | -0.0075837 | -0.12688 | -0.013623 | -0.010098 | -0.0026168 | 0.0019717 | -0.012939 | 0.21057 | 0.28381 | 0.23804 | 0.21973 | 0.33417 | 0.10986 | -0.059509 | 0.19226 | 0.28381 | 0.15106 | 0.26093 | 0.23346 | -0.013733 | -0.059509 | 122.8912 | 122.7219 | 0.17395 | 123.0652 | 123.0011 | 0.27924 | 0.050354 | 122.7676 | 122.7219 | 0.10071 | 122.9736 | 122.9324 | 0.21057 | 0.073242 | 123.1155 | 122.9919 | 123.0194 | -0.21973 | 123.0423 | 123.0148 | 123.0652 | -0.21973
2862.0312 | 123.0606 | -122.7905 | 0.21057 | -0.069275 | 0.0298 | 0.0048706 | 0.0066137 | -0.007543 | 0.0047788 | -0.0058747 | -0.11162 | -0.0099911 | -0.0053982 | -0.0011216 | 0.0073123 | -0.015289 | 0.13275 | 0.11902 | 0.050354 | 0.09613 | 0.30212 | 0 | -0.17395 | 0.10071 | 0.1236 | -0.027466 | 0.21973 | 0.1831 | -0.082397 | -0.15106 | 122.7905 | 122.6166 | 0.091553 | 122.9095 | 122.8867 | 0.27008 | -0.07782 | 122.7081 | 122.6395 | 0.009156 | 122.8912 | 122.7631 | 0.1236 | -0.027466 | 123.0927 | 122.9233 | 122.8409 | -0.38452 | 123.0103 | 122.9736 | 122.9141 | -0.36163
2863.7969 | 123.0606 | -122.7951 | 0.19684 | 0.19775 | 0.028305 | 0.0042298 | 0.0051183 | -0.0073294 | 0.00029262 | -0.0067291 | 0.14015 | -0.010632 | -0.0071072 | -0.0024032 | 0.0051761 | -0.014007 | 0.059509 | 0.032043 | 0.022888 | 0.032043 | 0.23346 | -0.032043 | -0.1831 | 0.1236 | 0.14191 | 0.050354 | 0.16479 | 0.13733 | -0.09613 | -0.16022 | 122.7631 | 122.612 | 0.036621 | 122.8271 | 122.8271 | 0.21515 | -0.13733 | 122.699 | 122.6349 | -0.032043 | 122.9187 | 122.8455 | 0.21057 | -0.059509 | 123.0286 | 122.8546 | 122.818 | -0.37994 | 122.9599 | 122.9324 | 122.937 | -0.35706
2865.5625 | 123.1476 | -122.7814 | 0.15564 | -0.22186 | 0.028732 | 0.0076478 | 0.0055457 | -0.0045522 | -0.0014164 | -0.0071563 | -0.24132 | -0.011273 | -0.0039028 | -0.0026168 | 0.0047489 | -0.012512 | 0.14191 | 0.14191 | 0.10071 | 0.15106 | 0.41199 | 0.073242 | -0.082397 | 0.082397 | 0.15106 | 0.022888 | 0.3067 | 0.28381 | -0.050354 | -0.09613 | 122.8546 | 122.699 | 0.25635 | 122.9233 | 122.9324 | 0.23346 | -0.013733 | 122.731 | 122.6852 | 0.15106 | 122.8638 | 122.8043 | 0.11902 | 0.12817 | 123.1934 | 122.9233 | 122.8821 | -0.23804 | 123.0881 | 123.0652 | 122.9324 | -0.25177
2867.25 | 123.0423 | -122.8226 | 0.19226 | -0.084534 | 0.031296 | 0.0044434 | 0.0078955 | -0.0079702 | 0.0020016 | -0.0054475 | -0.096359 | -0.0097775 | -0.004971 | 0.00037379 | 0.0049625 | -0.014221 | 0.11444 | 0.10071 | 0.054932 | 0.073242 | 0.29297 | 0.009155 | -0.17395 | 0.086975 | 0.10986 | -0.036621 | 0.2243 | 0.1831 | -0.10529 | -0.17853 | 122.8317 | 122.6486 | 0.10071 | 122.9233 | 122.8958 | 0.24719 | -0.07782 | 122.7173 | 122.644 | 0.032043 | 122.9095 | 122.7859 | 0.14191 | -0.009156 | 123.1155 | 122.937 | 122.8775 | -0.36621 | 123.0469 | 123.0057 | 122.9324 | -0.37079
2869.0156 | 123.056 | -122.7997 | 0.17853 | 0.11383 | 0.027023 | 0.0044434 | 0.0072547 | -0.0062612 | 0.00071982 | -0.0050201 | 0.12489 | -0.010846 | -0.0047574 | 0.00037379 | 0.0060305 | -0.014221 | 0.027466 | 0.027466 | -0.004578 | 0.004578 | 0.25635 | -0.050354 | -0.20599 | 0.059509 | 0.073242 | -0.045776 | 0.19226 | 0.13733 | -0.11902 | -0.1831 | 122.7493 | 122.5937 | 0.07782 | 122.8271 | 122.8043 | 0.21057 | -0.15106 | 122.6807 | 122.6166 | 0.013733 | 122.8592 | 122.7539 | 0.13733 | -0.041199 | 123.056 | 122.8271 | 122.7951 | -0.38452 | 122.9919 | 122.937 | 122.8729 | -0.36163
2870.7812 | 123.024 | -122.7997 | 0.18768 | 0.060425 | 0.031509 | 0.0061524 | 0.0083227 | -0.005834 | 0.0011472 | -0.0050201 | 0.048599 | -0.0082821 | -0.0051846 | -0.0028306 | 0.0053897 | -0.014221 | 0.009155 | 0.009155 | -0.022888 | 0.009155 | 0.28381 | -0.045776 | -0.19226 | -0.004578 | 0.027466 | -0.10071 | 0.19684 | 0.17853 | -0.1236 | -0.1831 | 122.7539 | 122.6074 | 0.09613 | 122.8088 | 122.8088 | 0.20142 | -0.17853 | 122.6761 | 122.6166 | 0.009155 | 122.7951 | 122.699 | 0.082397 | -0.009155 | 123.0835 | 122.8088 | 122.7768 | -0.37994 | 122.9965 | 122.9782 | 122.8271 | -0.37079
2872.5312 | 123.1522 | -122.7905 | 0.16479 | -0.16846 | 0.031082 | 0.0078614 | 0.0061865 | -0.007543 | -0.00013458 | -0.0052337 | -0.22606 | -0.010205 | -0.0045438 | -0.0011216 | 0.0045351 | -0.014862 | 0.1236 | 0.1236 | 0.091553 | 0.14191 | 0.37079 | 0.045776 | -0.09613 | 0.082397 | 0.16022 | 0.022888 | 0.28381 | 0.24719 | -0.059509 | -0.13275 | 122.8363 | 122.6944 | 0.20599 | 122.9141 | 122.9324 | 0.23804 | -0.041199 | 122.731 | 122.6578 | 0.11902 | 122.8729 | 122.8134 | 0.15564 | 0.082397 | 123.1613 | 122.9141 | 122.8821 | -0.26092 | 123.0743 | 123.0377 | 122.9507 | -0.29755
2874.25 | 123.0377 | -122.7997 | 0.18768 | -0.046387 | 0.030228 | 0.0044434 | 0.0044775 | -0.0098928 | 0.0013608 | -0.0048065 | -0.042954 | -0.0087093 | -0.0086026 | -0.00069421 | 0.0053897 | -0.014007 | 0.13733 | 0.09613 | 0.068665 | 0.10529 | 0.29755 | 0.004578 | -0.15106 | 0.086975 | 0.1236 | -0.018311 | 0.19684 | 0.19684 | -0.10071 | -0.16022 | 122.8043 | 122.6486 | 0.10986 | 122.8958 | 122.905 | 0.25635 | -0.050354 | 122.699 | 122.6395 | 0.009155 | 122.8867 | 122.7814 | 0.14191 | 0.009155 | 123.0972 | 122.937 | 122.8683 | -0.33874 | 122.9965 | 122.9965 | 122.9233 | -0.3479
2876.0156 | 123.0698 | -122.7997 | 0.16937 | 0.022278 | 0.022965 | 0.0059388 | 0.0051183 | -0.0081838 | -0.0065434 | -0.0082245 | 0.15541 | -0.0117 | -0.0075344 | -0.0032578 | 0.0015445 | -0.011444 | 0.10071 | 0.1236 | 0.11902 | 0.11902 | 0.3067 | 0.032043 | -0.10071 | 0.13275 | 0.18768 | 0.11444 | 0.2243 | 0.20599 | -0.059509 | -0.10071 | 122.8317 | 122.699 | 0.13733 | 122.9233 | 122.9187 | 0.21973 | -0.068665 | 122.7402 | 122.699 | 0.054931 | 122.9324 | 122.9141 | 0.21515 | 0.036621 | 123.1064 | 122.9004 | 122.9187 | -0.27008 | 123.024 | 123.0057 | 122.9874 | -0.27008
2877.7656 | 123.0927 | -122.7859 | 0.15106 | -0.16846 | 0.02916 | 0.0055114 | 0.0068273 | -0.0090384 | -0.004407 | -0.010574 | -0.11162 | -0.011487 | -0.006039 | -0.0041122 | 0.0017581 | -0.01358 | 0.23804 | 0.27008 | 0.23346 | 0.2243 | 0.34332 | 0.091553 | -0.041199 | 0.23346 | 0.31586 | 0.17853 | 0.27466 | 0.23804 | 0 | -0.059509 | 122.8775 | 122.7448 | 0.19226 | 123.056 | 123.0103 | 0.2655 | 0.086975 | 122.7859 | 122.7264 | 0.1236 | 123.0194 | 122.9645 | 0.23804 | 0.086975 | 123.1293 | 123.024 | 123.0194 | -0.19226 | 123.0606 | 123.024 | 123.1018 | -0.21057
2879.5156 | 123.0057 | -122.8088 | 0.19226 | 0.11383 | 0.027451 | 0.0057252 | 0.0074683 | -0.0069022 | -0.0031254 | -0.0095063 | 0.14015 | -0.012982 | -0.0053982 | -0.00026701 | 0.0013309 | -0.015289 | 0.14648 | 0.13733 | 0.10986 | 0.091553 | 0.21515 | -0.004578 | -0.16479 | 0.14648 | 0.16937 | 0.073242 | 0.17853 | 0.15106 | -0.086975 | -0.11902 | 122.8043 | 122.644 | 0.022888 | 122.9462 | 122.9004 | 0.25635 | -0.045777 | 122.7219 | 122.6898 | -0.013733 | 122.9553 | 122.8821 | 0.19226 | -0.041199 | 123.024 | 122.9553 | 122.9187 | -0.35706 | 122.9874 | 122.9599 | 122.9782 | -0.31128
2881.2188 | 123.0927 | -122.7905 | 0.16937 | -0.24475 | 0.027664 | 0.0072204 | 0.0078955 | -0.0077566 | -0.00077538 | -0.0063019 | -0.19554 | -0.012555 | -0.004971 | -0.0011216 | 0.0053897 | -0.015289 | 0.1831 | 0.18768 | 0.14191 | 0.19684 | 0.36163 | 0.073242 | -0.073242 | 0.11902 | 0.19684 | 0.054932 | 0.3067 | 0.27466 | -0.027466 | -0.091553 | 122.8638 | 122.7173 | 0.19226 | 122.9782 | 122.9874 | 0.27008 | 0.013732 | 122.7631 | 122.699 | 0.13733 | 122.9095 | 122.8455 | 0.14649 | 0.10529 | 123.1522 | 122.9736 | 122.9324 | -0.24261 | 123.0972 | 123.0652 | 122.9874 | -0.26093
2882.9688 | 123.056 | -122.7951 | 0.18768 | 0.14435 | 0.028092 | 0.0040162 | 0.0057593 | -0.0062612 | 0.0039242 | -0.0060883 | 0.04097 | -0.010632 | -0.0030484 | 0.00016019 | 0.0056033 | -0.015075 | 0.027466 | -0.041199 | -0.050354 | -0.004578 | 0.25177 | -0.082397 | -0.23346 | 0.036621 | 0.032043 | -0.073242 | 0.20142 | 0.16479 | -0.14191 | -0.1831 | 122.7127 | 122.5616 | 0.064087 | 122.7539 | 122.7905 | 0.22888 | -0.16022 | 122.6532 | 122.612 | 0.013733 | 122.8317 | 122.7219 | 0.10986 | -0.022888 | 123.0469 | 122.8226 | 122.7448 | -0.42114 | 122.9965 | 122.9599 | 122.8271 | -0.37079
2884.7188 | 123.0057 | -122.818 | 0.1831 | 0.12146 | 0.024887 | 0.0048706 | 0.0066137 | -0.0066884 | -0.0037662 | -0.0084381 | 0.15541 | -0.0117 | -0.0058254 | -0.00069421 | 0.00047633 | -0.013794 | 0.11444 | 0.13733 | 0.11444 | 0.086975 | 0.23804 | 0.009155 | -0.16022 | 0.15564 | 0.17395 | 0.10529 | 0.18768 | 0.16937 | -0.064087 | -0.10986 | 122.8271 | 122.6578 | 0.054932 | 122.9553 | 122.905 | 0.24719 | -0.068664 | 122.7539 | 122.7081 | 0.004578 | 122.9736 | 122.9233 | 0.21515 | -0.013732 | 123.056 | 122.9324 | 122.9324 | -0.34332 | 123.0057 | 122.9874 | 122.9919 | -0.29297
2886.4219 | 123.1247 | -122.7997 | 0.16479 | -0.17609 | 0.027878 | 0.006366 | 0.010459 | -0.0051932 | -0.005048 | -0.0086517 | -0.18791 | -0.0117 | -0.0064664 | -0.0013352 | 0.0019717 | -0.015075 | 0.24261 | 0.2655 | 0.24261 | 0.21515 | 0.35706 | 0.10071 | -0.054932 | 0.24261 | 0.32501 | 0.17853 | 0.25177 | 0.24719 | 0 | -0.045776 | 122.9004 | 122.7448 | 0.19226 | 123.0652 | 123.0148 | 0.27008 | 0.07782 | 122.7997 | 122.7539 | 0.086975 | 123.0423 | 122.9782 | 0.2243 | 0.082397 | 123.1567 | 123.0423 | 123.0423 | -0.21973 | 123.0515 | 123.0469 | 123.1247 | -0.21057
2888.1875 | 123.0194 | -122.8317 | 0.19226 | 0.12146 | 0.02446 | 0.0048706 | 0.0044775 | -0.0077566 | -0.0024844 | -0.0088653 | 0.13252 | -0.012982 | -0.0068936 | -0.0021896 | 0.0053897 | -0.014221 | 0.13275 | 0.13275 | 0.10986 | 0.082397 | 0.21515 | -0.013733 | -0.17395 | 0.17395 | 0.16479 | 0.068665 | 0.1831 | 0.14191 | -0.091553 | -0.14191 | 122.818 | 122.6578 | 0.022888 | 122.9645 | 122.9141 | 0.25635 | -0.05951 | 122.7402 | 122.6898 | -0.009156 | 123.0057 | 122.9004 | 0.21057 | -0.050354 | 123.0469 | 122.9645 | 122.9416 | -0.36621 | 123.0148 | 122.9736 | 122.9965 | -0.33417
2889.9531 | 123.1522 | -122.7859 | 0.16022 | -0.16083 | 0.031082 | 0.0042298 | 0.0078955 | -0.005834 | 0.0032834 | -0.0045929 | -0.22606 | -0.0095639 | -0.0045438 | 0.00058739 | 0.0066715 | -0.017425 | 0.17853 | 0.09613 | 0.07782 | 0.12817 | 0.35248 | 0.022888 | -0.14191 | 0.11444 | 0.15106 | 0.013733 | 0.26093 | 0.21057 | -0.086975 | -0.14648 | 122.8088 | 122.644 | 0.19226 | 122.8821 | 122.9141 | 0.27008 | 0.018311 | 122.699 | 122.6395 | 0.10071 | 122.9004 | 122.7997 | 0.16022 | 0.050354 | 123.1384 | 122.9645 | 122.8638 | -0.30212 | 123.0469 | 122.9965 | 122.937 | -0.3067
2891.6406 | 123.1705 | -122.7859 | 0.15564 | -0.19135 | 0.028305 | 0.0050842 | 0.0040503 | -0.0069022 | 0.0020016 | -0.0080109 | -0.24895 | -0.010632 | -0.0071072 | -0.0015488 | 0.0053897 | -0.014221 | 0.13275 | 0.11444 | 0.082397 | 0.13275 | 0.37079 | 0.045776 | -0.12817 | 0.09613 | 0.16479 | 0.018311 | 0.27924 | 0.23804 | -0.068665 | -0.11902 | 122.8317 | 122.6578 | 0.21515 | 122.9004 | 122.9187 | 0.26093 | -0.022889 | 122.7173 | 122.6669 | 0.1236 | 122.8821 | 122.8043 | 0.13733 | 0.082397 | 123.1567 | 122.9187 | 122.8683 | -0.28381 | 123.0652 | 123.024 | 122.9507 | -0.27466
2893.3438 | 123.024 | -122.818 | 0.18768 | 0.1062 | 0.025955 | 0.0042298 | 0.0076819 | -0.0064748 | -0.0037662 | -0.0082245 | 0.13252 | -0.012555 | -0.004971 | -0.0024032 | 0.0017581 | -0.012298 | 0.091553 | 0.14191 | 0.091553 | 0.073242 | 0.23804 | 0.004578 | -0.15564 | 0.15564 | 0.1831 | 0.082397 | 0.21057 | 0.1831 | -0.064087 | -0.10529 | 122.8226 | 122.6624 | 0.050354 | 122.9599 | 122.8912 | 0.22888 | -0.09613 | 122.7539 | 122.7127 | 0.022888 | 122.9736 | 122.9004 | 0.18768 | -0.004578 | 123.056 | 122.9095 | 122.9095 | -0.34332 | 123.0286 | 123.0011 | 123.0011 | -0.29297
2895.0938 | 123.0148 | -122.7997 | 0.19684 | 0.15961 | 0.025528 | 0.0072204 | 0.0036231 | -0.009252 | -0.0048344 | -0.0077973 | 0.11726 | -0.012341 | -0.009457 | -0.0017624 | 0.0066715 | -0.014221 | 0.10529 | 0.13733 | 0.10529 | 0.091553 | 0.2243 | -0.009155 | -0.1831 | 0.15564 | 0.1831 | 0.064087 | 0.17853 | 0.14191 | -0.086975 | -0.13275 | 122.7905 | 122.6166 | 0.027466 | 122.937 | 122.8912 | 0.27466 | -0.091552 | 122.7127 | 122.6669 | -0.01831 | 122.9553 | 122.8638 | 0.19684 | -0.054931 | 123.024 | 122.905 | 122.905 | -0.37994 | 122.9782 | 122.9416 | 122.9828 | -0.32959
2896.8438 | 123.0286 | -122.818 | 0.19684 | 0.1062 | 0.024887 | 0.0055114 | 0.0066137 | -0.007543 | -0.0022708 | -0.0075837 | 0.102 | -0.012982 | -0.0062528 | -0.00048061 | 0.00090353 | -0.012939 | 0.10529 | 0.15106 | 0.1236 | 0.10986 | 0.2655 | 0.032043 | -0.1236 | 0.14191 | 0.17853 | 0.07782 | 0.23346 | 0.1831 | -0.050354 | -0.10071 | 122.85 | 122.6944 | 0.068665 | 122.9691 | 122.9279 | 0.23346 | -0.091552 | 122.7676 | 122.7173 | 0.036621 | 122.9599 | 122.8958 | 0.17853 | -0.013733 | 123.0835 | 122.9233 | 122.9416 | -0.32043 | 123.0515 | 123.0011 | 122.9965 | -0.29755
2898.6094 | 123.1064 | -122.7997 | 0.16022 | -0.25238 | 0.026596 | 0.0061524 | 0.0064001 | -0.0062612 | 0.00071982 | -0.0071563 | -0.17265 | -0.011487 | -0.0075344 | -0.00090781 | 0.0043215 | -0.015716 | 0.19684 | 0.19226 | 0.16022 | 0.16937 | 0.37537 | 0.064087 | -0.07782 | 0.14648 | 0.1831 | 0.054932 | 0.29297 | 0.25635 | -0.032043 | -0.086975 | 122.8638 | 122.7219 | 0.21515 | 122.9919 | 122.9691 | 0.24719 | 0.036621 | 122.7676 | 122.7127 | 0.13275 | 122.9462 | 122.8546 | 0.14191 | 0.096131 | 123.175 | 122.9965 | 122.9599 | -0.23804 | 123.0927 | 123.056 | 122.9828 | -0.24719
2900.3125 | 123.0331 | -122.8409 | 0.1831 | 0.052795 | 0.02916 | 0.0052978 | 0.0027685 | -0.0049796 | 0.0043514 | -0.0058747 | 0.03334 | -0.0082821 | -0.0053982 | -0.0011216 | 0.0081667 | -0.016571 | 0.032043 | -0.022888 | -0.045776 | -0.004578 | 0.28839 | -0.054932 | -0.21057 | 0.032043 | 0.013733 | -0.09613 | 0.20142 | 0.16937 | -0.14648 | -0.19226 | 122.7859 | 122.6303 | 0.10529 | 122.818 | 122.8363 | 0.20599 | -0.15106 | 122.6944 | 122.6486 | 0.018311 | 122.8729 | 122.7448 | 0.096131 | -0.013732 | 123.1293 | 122.8729 | 122.7951 | -0.39368 | 123.0423 | 123.0103 | 122.8546 | -0.37537
2902.0781 | 123.0606 | -122.8134 | 0.17853 | 0.19775 | 0.030228 | 0.0050842 | 0.0036231 | -0.0069022 | -0.00077538 | -0.0058747 | 0.13252 | -0.0095639 | -0.008389 | -0.0011216 | 0.0066715 | -0.014435 | 0.10071 | 0.09613 | 0.054932 | 0.059509 | 0.21973 | -0.027466 | -0.19226 | 0.14648 | 0.15106 | 0.036621 | 0.17853 | 0.13275 | -0.086975 | -0.13733 | 122.7859 | 122.6212 | 0.041199 | 122.9095 | 122.8729 | 0.25177 | -0.07782 | 122.7264 | 122.6761 | 0 | 122.9599 | 122.85 | 0.17395 | -0.045777 | 123.0331 | 122.9141 | 122.8683 | -0.37079 | 122.9919 | 122.9462 | 122.9645 | -0.31586
2903.8438 | 123.1705 | -122.7905 | 0.15564 | -0.17609 | 0.02916 | 0.0061524 | 0.0093909 | -0.0088248 | 0.0026424 | -0.0045929 | -0.25658 | -0.0095639 | -0.0043302 | -0.00069421 | 0.0060305 | -0.016357 | 0.12817 | 0.10986 | 0.091553 | 0.12817 | 0.37079 | 0.045776 | -0.1236 | 0.10071 | 0.16937 | 0.013733 | 0.28381 | 0.24719 | -0.045776 | -0.11444 | 122.8363 | 122.6669 | 0.21515 | 122.9004 | 122.9187 | 0.25177 | -0.027466 | 122.7448 | 122.6761 | 0.12817 | 122.8912 | 122.8043 | 0.12817 | 0.091552 | 123.1613 | 122.9187 | 122.8821 | -0.27924 | 123.0743 | 123.0377 | 122.9599 | -0.27008
2905.5938 | 123.175 | -122.7859 | 0.16479 | -0.16083 | 0.0298 | 0.0065796 | 0.0046911 | -0.0071158 | 0.00071982 | -0.0069427 | -0.23369 | -0.010418 | -0.0045438 | -0.00069421 | 0.0032535 | -0.015716 | 0.1236 | 0.11444 | 0.091553 | 0.13275 | 0.36163 | 0.050354 | -0.11902 | 0.11902 | 0.16937 | 0.027466 | 0.28381 | 0.24719 | -0.064087 | -0.11902 | 122.8363 | 122.6669 | 0.19684 | 122.9004 | 122.9187 | 0.25177 | -0.041199 | 122.7219 | 122.6669 | 0.11902 | 122.905 | 122.8134 | 0.14649 | 0.082397 | 123.1476 | 122.9095 | 122.8775 | -0.28381 | 123.0698 | 123.0331 | 122.9553 | -0.28381
2907.2812 | 123.0743 | -122.8134 | 0.19684 | 0.15198 | 0.030655 | 0.0042298 | 0.0029821 | -0.007543 | 0.0013608 | -0.0058747 | 0.20119 | -0.011487 | -0.0056118 | -0.00069421 | 0.0051761 | -0.014007 | 0.022888 | 0.013733 | -0.009155 | 0.018311 | 0.24719 | -0.032043 | -0.20599 | 0.09613 | 0.1236 | -0.009155 | 0.16022 | 0.13733 | -0.11444 | -0.16479 | 122.7814 | 122.6074 | 0.050354 | 122.8271 | 122.8317 | 0.22431 | -0.17395 | 122.699 | 122.6486 | -0.036621 | 122.9095 | 122.8043 | 0.15564 | -0.059509 | 123.0606 | 122.8363 | 122.8043 | -0.40283 | 122.9736 | 122.9507 | 122.937 | -0.36163
2909.0469 | 123.1293 | -122.7722 | 0.16479 | -0.099793 | 0.030441 | 0.0055114 | 0.0070409 | -0.0049796 | 0.0030698 | -0.0075837 | -0.12688 | -0.0097775 | -0.0043302 | 0.00016019 | 0.0064577 | -0.015503 | 0.12817 | 0.14648 | 0.073242 | 0.10529 | 0.3067 | 0.009155 | -0.14648 | 0.10529 | 0.14191 | 0 | 0.21057 | 0.1831 | -0.091553 | -0.15106 | 122.7814 | 122.6257 | 0.14191 | 122.9187 | 122.8775 | 0.25177 | -0.036621 | 122.6807 | 122.6212 | 0.045776 | 122.8775 | 122.7722 | 0.15106 | 0.01831 | 123.0789 | 122.9004 | 122.8455 | -0.31128 | 122.9828 | 122.9553 | 122.9141 | -0.31586
2910.7969 | 123.1018 | -122.7951 | 0.16022 | 0.022278 | 0.027664 | 0.0057252 | 0.0053321 | -0.0090384 | -0.008466 | -0.0080109 | 0.102 | -0.010846 | -0.00668 | -0.0026168 | 0.0021853 | -0.012726 | 0.07782 | 0.15564 | 0.13275 | 0.12817 | 0.30212 | 0.041199 | -0.11444 | 0.13733 | 0.20599 | 0.11444 | 0.26093 | 0.21057 | -0.036621 | -0.09613 | 122.8363 | 122.6807 | 0.14191 | 122.9507 | 122.9233 | 0.24262 | -0.082397 | 122.7585 | 122.699 | 0.10071 | 122.9324 | 122.9095 | 0.21057 | 0.050354 | 123.0972 | 122.8729 | 122.9279 | -0.27466 | 123.056 | 123.0057 | 123.0011 | -0.25635
2912.5625 | 123.0789 | -122.8226 | 0.1831 | 0.1825 | 0.028946 | 0.006366 | 0.0046911 | -0.0081838 | 0.0020016 | -0.0060883 | 0.16304 | -0.012127 | -0.0056118 | -0.0013352 | 0.0045351 | -0.016143 | 0.041199 | 0.022888 | -0.004578 | 0.018311 | 0.23346 | -0.050354 | -0.22888 | 0.10529 | 0.10071 | 0.009155 | 0.16937 | 0.14191 | -0.11444 | -0.15106 | 122.7722 | 122.5937 | 0.050354 | 122.8455 | 122.8409 | 0.24719 | -0.14191 | 122.7081 | 122.6715 | -0.013732 | 122.9279 | 122.8317 | 0.16022 | -0.041198 | 123.056 | 122.8638 | 122.818 | -0.41199 | 122.9919 | 122.9645 | 122.9233 | -0.33417
2914.2812 | 123.1384 | -122.7631 | 0.15564 | -0.023499 | 0.026169 | 0.0055114 | 0.0064001 | -0.0079702 | -0.006116 | -0.0069427 | 0.018082 | -0.012982 | -0.0051846 | -0.001976 | 4.9132e-05 | -0.014862 | 0.12817 | 0.20599 | 0.17853 | 0.16479 | 0.31586 | 0.045776 | -0.07782 | 0.21515 | 0.27466 | 0.16937 | 0.23804 | 0.2243 | -0.018311 | -0.07782 | 122.8088 | 122.6852 | 0.16022 | 122.9691 | 122.9279 | 0.24261 | -0.027466 | 122.7448 | 122.6852 | 0.082397 | 122.9782 | 122.9324 | 0.24719 | 0.068664 | 123.0789 | 122.8912 | 122.9416 | -0.23346 | 123.0011 | 122.9874 | 123.0377 | -0.23346
2915.9844 | 123.1659 | -122.7722 | 0.16022 | -0.22949 | 0.02916 | 0.0061524 | 0.0068273 | -0.007543 | -0.00013458 | -0.0086517 | -0.19554 | -0.0093503 | -0.0041164 | 0.00016019 | 0.0041079 | -0.015503 | 0.13275 | 0.1236 | 0.086975 | 0.13733 | 0.37994 | 0.068665 | -0.10071 | 0.10986 | 0.14648 | 0 | 0.27924 | 0.24719 | -0.045776 | -0.11902 | 122.8409 | 122.6715 | 0.21973 | 122.8958 | 122.9095 | 0.23804 | -0.027466 | 122.7264 | 122.6532 | 0.11902 | 122.8821 | 122.7722 | 0.11902 | 0.086975 | 123.1522 | 122.905 | 122.8592 | -0.26093 | 123.0515 | 123.0194 | 122.9187 | -0.27924
2917.75 | 123.1293 | -122.7814 | 0.16937 | -0.25238 | 0.02916 | 0.0048706 | 0.0072547 | -0.0064748 | -0.003339 | -0.0099335 | -0.21843 | -0.012768 | -0.0062528 | -0.003685 | 0.0021853 | -0.014648 | 0.11902 | 0.16022 | 0.09613 | 0.13733 | 0.39825 | 0.059509 | -0.09613 | 0.11444 | 0.16937 | 0.041199 | 0.3067 | 0.26093 | -0.041199 | -0.09613 | 122.8409 | 122.6852 | 0.22888 | 122.9416 | 122.9187 | 0.23346 | -0.050354 | 122.7402 | 122.6852 | 0.13733 | 122.8958 | 122.8226 | 0.13733 | 0.091552 | 123.1796 | 122.9004 | 122.8775 | -0.2655 | 123.0881 | 123.0423 | 122.9507 | -0.2655
2919.5156 | 123.1155 | -122.818 | 0.17395 | -0.23712 | 0.029373 | 0.0044434 | 0.0076819 | -0.0081838 | -0.0022708 | -0.0075837 | -0.17265 | -0.010846 | -0.0064664 | -0.0030442 | 0.0041079 | -0.01358 | 0.16022 | 0.21057 | 0.15564 | 0.17853 | 0.39368 | 0.082397 | -0.068665 | 0.13733 | 0.20142 | 0.059509 | 0.29755 | 0.26093 | -0.027466 | -0.073242 | 122.9004 | 122.7493 | 0.21973 | 123.0286 | 122.9965 | 0.24719 | -0.013733 | 122.7905 | 122.7448 | 0.1236 | 122.9553 | 122.8775 | 0.13275 | 0.086975 | 123.2117 | 122.9782 | 122.9736 | -0.24261 | 123.1155 | 123.0789 | 123.0194 | -0.24719
2921.2188 | 123.0194 | -122.8088 | 0.21057 | 0.15198 | 0.026169 | 0.006366 | 0.0034093 | -0.007543 | -0.0029118 | -0.0054475 | 0.1783 | -0.011487 | -0.0073208 | 0.00016019 | 0.0051761 | -0.013366 | 0.07782 | 0.14191 | 0.091553 | 0.086975 | 0.1831 | -0.041199 | -0.17395 | 0.13733 | 0.17853 | 0.050354 | 0.14648 | 0.1236 | -0.11444 | -0.16479 | 122.7676 | 122.6349 | -0.027466 | 122.9507 | 122.8958 | 0.26092 | -0.13275 | 122.6944 | 122.644 | -0.064087 | 122.9462 | 122.8592 | 0.21515 | -0.086975 | 122.9919 | 122.8867 | 122.9004 | -0.38452 | 122.9553 | 122.9324 | 122.9874 | -0.37537
2922.9688 | 123.0515 | -122.85 | 0.19226 | 0.098572 | 0.029587 | 0.0044434 | 0.0038367 | -0.0077566 | 0.0043514 | -0.0039521 | 0.079117 | -0.0082821 | -0.0068936 | -0.0011216 | 0.0083805 | -0.014435 | 0.022888 | 0.004578 | -0.059509 | -0.009155 | 0.27008 | -0.064087 | -0.19226 | 0.018311 | 0.022888 | -0.068665 | 0.20142 | 0.16022 | -0.14648 | -0.20599 | 122.7859 | 122.6578 | 0.07782 | 122.8546 | 122.8409 | 0.18311 | -0.16937 | 122.7036 | 122.644 | 0.009155 | 122.8683 | 122.7814 | 0.13733 | -0.032044 | 123.1201 | 122.8729 | 122.7905 | -0.38452 | 123.0515 | 123.0103 | 122.8729 | -0.39826
2924.7188 | 123.0286 | -122.818 | 0.19226 | 0.1062 | 0.025314 | 0.0050842 | 0.0036231 | -0.008611 | -0.0052616 | -0.0054475 | 0.094375 | -0.012127 | -0.0088162 | -0.0028306 | 0.0019717 | -0.012298 | 0.073242 | 0.14191 | 0.10986 | 0.10071 | 0.27008 | 0.004578 | -0.1236 | 0.13733 | 0.17395 | 0.09613 | 0.22888 | 0.19226 | -0.054932 | -0.10986 | 122.8226 | 122.6944 | 0.07782 | 122.9599 | 122.9187 | 0.2243 | -0.11902 | 122.7631 | 122.7081 | 0.036621 | 122.9553 | 122.9141 | 0.20599 | 0 | 123.0881 | 122.8912 | 122.9279 | -0.31586 | 123.0469 | 123.0103 | 122.9919 | -0.30212
2926.4062 | 123.1247 | -122.7905 | 0.16937 | -0.23712 | 0.027023 | 0.0035888 | 0.011314 | -0.0051932 | -0.00098918 | -0.0084381 | -0.25658 | -0.012341 | -0.006039 | -0.00090781 | 0.0011173 | -0.01358 | 0.15106 | 0.14648 | 0.086975 | 0.12817 | 0.39368 | 0.073242 | -0.09613 | 0.10071 | 0.16937 | 0.041199 | 0.3067 | 0.27008 | -0.041199 | -0.09613 | 122.8638 | 122.6944 | 0.2243 | 122.937 | 122.9187 | 0.2243 | -0.018311 | 122.7493 | 122.6944 | 0.13733 | 122.8912 | 122.8317 | 0.13733 | 0.10071 | 123.1842 | 122.9416 | 122.8775 | -0.2655 | 123.0972 | 123.0606 | 122.9599 | -0.2655
2928.1562 | 123.0743 | -122.7905 | 0.1831 | 0.022278 | 0.023605 | 0.006366 | 0.0031957 | -0.0066884 | -0.0065434 | -0.0084381 | 0.063858 | -0.011059 | -0.0071072 | -0.00026701 | 0.0013309 | -0.012512 | 0.10529 | 0.14191 | 0.1236 | 0.11902 | 0.29755 | 0.045776 | -0.11444 | 0.14648 | 0.20142 | 0.11444 | 0.24261 | 0.19684 | -0.032043 | -0.09613 | 122.8363 | 122.6761 | 0.11444 | 122.9324 | 122.9095 | 0.23346 | -0.077819 | 122.7585 | 122.6944 | 0.05951 | 122.937 | 122.905 | 0.21057 | 0.013733 | 123.0881 | 122.8958 | 122.9141 | -0.29755 | 123.0331 | 122.9874 | 122.9919 | -0.27924
2929.8438 | 123.0331 | -122.818 | 0.19226 | 0.083313 | 0.031082 | 0.0044434 | 0.0034093 | -0.0066884 | 0.0037106 | -0.0054475 | 0.048599 | -0.0097775 | -0.0073208 | 0.00080099 | 0.0070987 | -0.016998 | 0.036621 | -0.009155 | -0.045776 | 0 | 0.29297 | -0.054932 | -0.20599 | 0.027466 | 0.013733 | -0.09613 | 0.20142 | 0.17853 | -0.13275 | -0.1831 | 122.7631 | 122.612 | 0.10071 | 122.8088 | 122.818 | 0.20599 | -0.15564 | 122.6852 | 122.6349 | 0.009155 | 122.8455 | 122.7219 | 0.086975 | -0.013733 | 123.111 | 122.8546 | 122.7722 | -0.39826 | 123.0194 | 122.9965 | 122.8317 | -0.37537
2931.5312 | 123.0789 | -122.8271 | 0.20142 | 0.098572 | 0.028519 | 0.0057252 | 0.0034093 | -0.010534 | 0.0011472 | -0.0043793 | 0.086746 | -0.010418 | -0.0068936 | -0.0021896 | 0.0066715 | -0.013153 | 0.022888 | 0.018311 | -0.022888 | 0 | 0.27466 | -0.045776 | -0.23346 | 0.059509 | 0.059509 | -0.041199 | 0.19684 | 0.15106 | -0.11902 | -0.17395 | 122.7814 | 122.5937 | 0.073242 | 122.8455 | 122.8271 | 0.23346 | -0.17853 | 122.7081 | 122.6532 | -0.004578 | 122.8867 | 122.7859 | 0.13275 | -0.050354 | 123.1018 | 122.85 | 122.8043 | -0.43488 | 123.024 | 122.9782 | 122.8867 | -0.37537
2933.2188 | 123.0743 | -122.8088 | 0.17853 | 0.13672 | 0.028519 | 0.0070068 | 0.0055457 | -0.0047658 | 0.0011472 | -0.0054475 | 0.13252 | -0.011273 | -0.0039028 | -0.0026168 | 0.0060305 | -0.013794 | 0.018311 | 0.036621 | -0.004578 | 0.009155 | 0.23804 | -0.045776 | -0.20142 | 0.07782 | 0.10071 | 0.004578 | 0.1831 | 0.14191 | -0.11444 | -0.16479 | 122.7631 | 122.6074 | 0.059509 | 122.8455 | 122.818 | 0.21057 | -0.16022 | 122.6944 | 122.644 | 0.004577 | 122.8867 | 122.8134 | 0.16937 | -0.036621 | 123.0469 | 122.8271 | 122.8043 | -0.37994 | 122.9919 | 122.9507 | 122.9095 | -0.34332
2934.9688 | 123.0789 | -122.8271 | 0.19684 | 0.090942 | 0.030441 | 0.0055114 | 0.0044775 | -0.0060476 | 0.0011472 | -0.0058747 | 0.12489 | -0.0087093 | -0.008389 | 0.00016019 | 0.0060305 | -0.014862 | 0.027466 | 0.013733 | -0.027466 | 0.018311 | 0.27008 | -0.032043 | -0.18768 | 0.064087 | 0.045776 | -0.027466 | 0.18768 | 0.15106 | -0.1236 | -0.18768 | 122.7951 | 122.6395 | 0.073243 | 122.8409 | 122.8455 | 0.20599 | -0.16937 | 122.7036 | 122.6395 | -0.009155 | 122.8912 | 122.7997 | 0.16022 | -0.045776 | 123.0972 | 122.8546 | 122.7997 | -0.38452 | 123.0148 | 122.9782 | 122.8729 | -0.38452
2936.7188 | 123.0331 | -122.8409 | 0.19684 | 0.083313 | 0.030228 | 0.004657 | 0.0053321 | -0.0060476 | 0.0011472 | -0.0052337 | 0.048599 | -0.0093503 | -0.0075344 | -0.0011216 | 0.0051761 | -0.01358 | 0.027466 | -0.032043 | -0.050354 | -0.018311 | 0.27924 | -0.036621 | -0.21515 | 0.018311 | 0.013733 | -0.07782 | 0.19684 | 0.15106 | -0.13733 | -0.17395 | 122.8043 | 122.6257 | 0.082398 | 122.8088 | 122.8226 | 0.19684 | -0.16937 | 122.7036 | 122.6669 | 0 | 122.8592 | 122.7631 | 0.09613 | -0.045776 | 123.1201 | 122.8683 | 122.7905 | -0.41199 | 123.0377 | 122.9919 | 122.8546 | -0.37079
2938.4688 | 123.0698 | -122.7997 | 0.19684 | 0.11383 | 0.030655 | 0.0072204 | 0.0057593 | -0.0056204 | 0.0020016 | -0.0060883 | 0.12489 | -0.0078549 | -0.0064664 | -0.00026701 | 0.0070987 | -0.01358 | 0.013733 | -0.036621 | -0.036621 | -0.009155 | 0.26093 | -0.045776 | -0.19226 | 0.032043 | 0.041199 | -0.059509 | 0.20142 | 0.16479 | -0.11902 | -0.1831 | 122.7539 | 122.6074 | 0.064087 | 122.7631 | 122.7905 | 0.18311 | -0.18311 | 122.6807 | 122.6166 | 0.004578 | 122.8317 | 122.7402 | 0.1236 | -0.032043 | 123.0606 | 122.8134 | 122.7631 | -0.3891 | 123.0011 | 122.9645 | 122.8409 | -0.37994
2940.1562 | 123.0698 | -122.818 | 0.17853 | 0.12909 | 0.028305 | 0.0052978 | 0.0064001 | -0.007543 | 0.00029262 | -0.0054475 | 0.17067 | -0.011059 | -0.0068936 | 0.00058739 | 0.0070987 | -0.015503 | 0.045776 | -0.004578 | -0.018311 | 0 | 0.2655 | -0.041199 | -0.21515 | 0.073242 | 0.059509 | -0.027466 | 0.1831 | 0.14648 | -0.1236 | -0.17395 | 122.7768 | 122.6028 | 0.086975 | 122.8134 | 122.818 | 0.21515 | -0.13275 | 122.6944 | 122.644 | 0.004577 | 122.8912 | 122.7905 | 0.14648 | -0.032044 | 123.0835 | 122.8638 | 122.7997 | -0.39368 | 123.0011 | 122.9645 | 122.8775 | -0.35248
2941.9375 | 123.1796 | -122.7768 | 0.16937 | -0.16083 | 0.029587 | 0.0027344 | 0.0072547 | -0.0088248 | -0.00077538 | -0.0065155 | -0.25658 | -0.012127 | -0.00668 | -0.0028306 | 0.0075259 | -0.014221 | 0.13275 | 0.10529 | 0.073242 | 0.12817 | 0.35706 | 0.041199 | -0.13275 | 0.10986 | 0.14648 | 0.022888 | 0.28381 | 0.23804 | -0.07782 | -0.11444 | 122.818 | 122.644 | 0.18768 | 122.8821 | 122.905 | 0.26093 | -0.036622 | 122.699 | 122.6624 | 0.11444 | 122.8867 | 122.7997 | 0.13733 | 0.068664 | 123.1338 | 122.9095 | 122.85 | -0.30212 | 123.0606 | 123.0148 | 122.9233 | -0.28381
2943.7031 | 123.0606 | -122.8363 | 0.20599 | 0.1062 | 0.030441 | 0.0038024 | 0.0059729 | -0.0081838 | 0.00093342 | -0.0058747 | 0.063858 | -0.0099911 | -0.003262 | -0.0011216 | 0.0041079 | -0.013794 | 0.004578 | -0.036621 | -0.050354 | -0.009155 | 0.25635 | -0.059509 | -0.2243 | 0.018311 | 0.045776 | -0.054932 | 0.19684 | 0.17395 | -0.13733 | -0.18768 | 122.7768 | 122.612 | 0.050354 | 122.7997 | 122.8271 | 0.21515 | -0.20142 | 122.699 | 122.6486 | -0.009156 | 122.8546 | 122.7814 | 0.13275 | -0.032044 | 123.0927 | 122.8409 | 122.7859 | -0.4303 | 123.0331 | 123.0103 | 122.8821 | -0.39368
2945.3906 | 123.0881 | -122.8134 | 0.20142 | 0.15961 | 0.03215 | 0.0055114 | 0.0085363 | -0.005834 | 0.00071982 | -0.0037385 | 0.086746 | -0.0089229 | -0.0073208 | 0.00037379 | 0.0056033 | -0.014007 | -0.013733 | -0.022888 | -0.050354 | 0 | 0.25177 | -0.059509 | -0.21515 | 0.018311 | 0.027466 | -0.059509 | 0.20599 | 0.17395 | -0.1236 | -0.17853 | 122.7539 | 122.5983 | 0.050354 | 122.7905 | 122.8134 | 0.21515 | -0.21515 | 122.6898 | 122.6349 | 0.004578 | 122.8317 | 122.7539 | 0.11902 | -0.027466 | 123.0652 | 122.7997 | 122.7631 | -0.41657 | 123.0194 | 122.9874 | 122.8409 | -0.37994
2947.1406 | 123.1201 | -122.7722 | 0.16479 | -0.22949 | 0.030014 | 0.0065796 | 0.011314 | -0.0077566 | -0.0059024 | -0.0084381 | -0.24895 | -0.011273 | -0.0041164 | -0.0034714 | 0.00068993 | -0.014648 | 0.11902 | 0.14648 | 0.10529 | 0.1236 | 0.39368 | 0.064087 | -0.10529 | 0.10986 | 0.16937 | 0.032043 | 0.31586 | 0.27466 | -0.054932 | -0.09613 | 122.8363 | 122.6669 | 0.22888 | 122.9187 | 122.8958 | 0.22888 | -0.045776 | 122.7173 | 122.6761 | 0.15106 | 122.8821 | 122.8043 | 0.12817 | 0.10986 | 123.1659 | 122.8912 | 122.8775 | -0.27008 | 123.0881 | 123.0469 | 122.9416 | -0.26092
2948.9062 | 123.0606 | -122.8317 | 0.20142 | 0.13672 | 0.028305 | 0.0048706 | 0.0055457 | -0.0081838 | -0.00056178 | -0.0073701 | 0.10963 | -0.0117 | -0.0062528 | -0.0015488 | 0.0064577 | -0.012939 | 0.009155 | -0.004578 | -0.032043 | 0.009155 | 0.27008 | -0.064087 | -0.20599 | 0.027466 | 0.054932 | -0.050354 | 0.19226 | 0.16479 | -0.13733 | -0.1831 | 122.7676 | 122.6257 | 0.068665 | 122.8271 | 122.8409 | 0.21515 | -0.19226 | 122.6944 | 122.6486 | -0.009155 | 122.8592 | 122.7814 | 0.13275 | -0.036621 | 123.1018 | 122.8409 | 122.7997 | -0.40741 | 123.024 | 122.9965 | 122.8867 | -0.38452
2950.6719 | 123.1247 | -122.8088 | 0.17853 | -0.084534 | 0.031509 | 0.0033752 | 0.0040503 | -0.0077566 | 0.00050622 | -0.0069427 | -0.14214 | -0.0072141 | -0.0051846 | -0.00069421 | 0.0066715 | -0.015289 | 0.13275 | 0.10071 | 0.064087 | 0.10529 | 0.3067 | 0.009155 | -0.14648 | 0.10071 | 0.15564 | -0.004578 | 0.2243 | 0.19226 | -0.10071 | -0.15564 | 122.818 | 122.6624 | 0.12817 | 122.9095 | 122.9141 | 0.25177 | -0.045777 | 122.7081 | 122.6532 | 0.045776 | 122.9095 | 122.8043 | 0.15106 | 0.013733 | 123.1155 | 122.9416 | 122.8729 | -0.32501 | 123.0331 | 123.0011 | 122.9645 | -0.33417
2952.375 | 123.1201 | -122.7676 | 0.16937 | -0.2066 | 0.027451 | 0.0055114 | 0.010459 | -0.007543 | -0.0059024 | -0.0067291 | -0.10399 | -0.012768 | -0.0073208 | -0.0028306 | -0.00037807 | -0.014221 | 0.19684 | 0.28839 | 0.25177 | 0.22888 | 0.3479 | 0.11902 | -0.054932 | 0.21057 | 0.3067 | 0.16937 | 0.25635 | 0.22888 | -0.009155 | -0.064087 | 122.8867 | 122.7127 | 0.17853 | 123.056 | 122.9965 | 0.28381 | 0.027465 | 122.7585 | 122.7036 | 0.086975 | 122.9782 | 122.937 | 0.23346 | 0.059509 | 123.1155 | 122.9645 | 123.0194 | -0.22431 | 123.024 | 122.9965 | 123.0743 | -0.23346
2954.125 | 123.175 | -122.7722 | 0.17853 | -0.24475 | 0.02916 | 0.0065796 | 0.0076819 | -0.0060476 | -0.0022708 | -0.0084381 | -0.2108 | -0.010205 | -0.0047574 | -0.00048061 | 0.0038943 | -0.013794 | 0.15106 | 0.11902 | 0.082397 | 0.14191 | 0.41199 | 0.059509 | -0.10071 | 0.082397 | 0.15106 | 0.013733 | 0.28839 | 0.25635 | -0.050354 | -0.091553 | 122.8317 | 122.6715 | 0.23346 | 122.8912 | 122.9141 | 0.24262 | -0.027466 | 122.7219 | 122.6807 | 0.10986 | 122.8546 | 122.7859 | 0.10529 | 0.07782 | 123.1842 | 122.9233 | 122.8546 | -0.27924 | 123.0606 | 123.0286 | 122.9233 | -0.27008
2955.8906 | 123.1567 | -122.7631 | 0.16937 | -0.046387 | 0.025528 | 0.0072204 | 0.0061865 | -0.0083974 | -0.0059024 | -0.0095063 | -0.012436 | -0.012768 | -0.0039028 | -0.0032578 | 4.9132e-05 | -0.013794 | 0.15564 | 0.19684 | 0.16937 | 0.16022 | 0.32501 | 0.059509 | -0.091553 | 0.21057 | 0.29297 | 0.19226 | 0.25635 | 0.2243 | -0.004578 | -0.059509 | 122.8226 | 122.6715 | 0.15564 | 122.9599 | 122.9233 | 0.25177 | -0.013733 | 122.7585 | 122.7036 | 0.086975 | 122.9736 | 122.9553 | 0.25177 | 0.054931 | 123.0881 | 122.9187 | 122.9324 | -0.26093 | 123.0194 | 122.9874 | 123.056 | -0.22888
2957.5781 | 123.1476 | -122.7722 | 0.1831 | -0.031128 | 0.027237 | 0.0033752 | 0.0076819 | -0.01032 | -0.0063296 | -0.0080109 | -0.050583 | -0.012341 | -0.0047574 | -0.0017624 | 0.0015445 | -0.014648 | 0.18768 | 0.1831 | 0.1831 | 0.16022 | 0.32959 | 0.054932 | -0.086975 | 0.22888 | 0.27466 | 0.19684 | 0.25635 | 0.24261 | 0 | -0.064087 | 122.8271 | 122.6852 | 0.14649 | 122.9553 | 122.9324 | 0.24719 | 0.004578 | 122.7722 | 122.7081 | 0.073243 | 123.0011 | 122.9691 | 0.26093 | 0.05951 | 123.1018 | 122.9599 | 122.9553 | -0.27008 | 123.0286 | 123.0148 | 123.0469 | -0.24719
2959.3438 | 123.0194 | -122.8363 | 0.18768 | 0.045166 | 0.030441 | 0.0038024 | 0.0042639 | -0.0088248 | 0.0049924 | -0.0071563 | -0.035324 | -0.0097775 | -0.0047574 | -0.00048061 | 0.0053897 | -0.016784 | 0.045776 | -0.022888 | -0.045776 | -0.004578 | 0.28381 | -0.041199 | -0.22888 | 0.009155 | 0.013733 | -0.11902 | 0.20142 | 0.1831 | -0.13733 | -0.20142 | 122.7951 | 122.6074 | 0.09613 | 122.8134 | 122.8317 | 0.2243 | -0.14191 | 122.699 | 122.6349 | 0.013733 | 122.8455 | 122.7173 | 0.082397 | -0.004578 | 123.1201 | 122.8821 | 122.7905 | -0.41656 | 123.0377 | 123.0194 | 122.85 | -0.3891
2961.0938 | 123.1293 | -122.7905 | 0.1831 | -0.22949 | 0.028732 | 0.0052978 | 0.0096045 | -0.0071158 | -0.0029118 | -0.0063019 | -0.24895 | -0.010632 | -0.0043302 | -5.3406e-05 | 0.0034671 | -0.015289 | 0.15106 | 0.15564 | 0.10529 | 0.1236 | 0.39825 | 0.073242 | -0.10529 | 0.10529 | 0.17395 | 0.027466 | 0.32501 | 0.27924 | -0.059509 | -0.09613 | 122.8638 | 122.6852 | 0.21515 | 122.9462 | 122.9141 | 0.22888 | -0.032043 | 122.731 | 122.6944 | 0.14191 | 122.8958 | 122.818 | 0.1236 | 0.096131 | 123.1888 | 122.9416 | 122.8958 | -0.28839 | 123.1155 | 123.0698 | 122.9645 | -0.27924
2962.8438 | 123.0606 | -122.8134 | 0.19226 | 0.029907 | 0.025528 | 0.0052978 | 0.0066137 | -0.0062612 | -0.0041934 | -0.0075837 | 0.086746 | -0.013196 | -0.0062528 | -0.00048061 | 0.0019717 | -0.011871 | 0.10986 | 0.14648 | 0.11444 | 0.11902 | 0.29755 | 0.036621 | -0.11902 | 0.13275 | 0.16937 | 0.09613 | 0.23804 | 0.1831 | -0.045776 | -0.09613 | 122.85 | 122.6944 | 0.10528 | 122.9599 | 122.9324 | 0.23804 | -0.082398 | 122.7676 | 122.7173 | 0.045776 | 122.9462 | 122.9095 | 0.19226 | -0.009156 | 123.111 | 122.9233 | 122.9279 | -0.31128 | 123.0515 | 122.9965 | 122.9828 | -0.28839
2964.6094 | 123.1842 | -122.7722 | 0.17395 | -0.16083 | 0.030228 | 0.0052978 | 0.0066137 | -0.0081838 | 0.0011472 | -0.0077973 | -0.24132 | -0.010846 | -0.0068936 | -0.00069421 | 0.0047489 | -0.017852 | 0.12817 | 0.11902 | 0.086975 | 0.1236 | 0.36163 | 0.041199 | -0.11444 | 0.10529 | 0.15106 | 0.009155 | 0.27924 | 0.2243 | -0.068665 | -0.12817 | 122.8134 | 122.6578 | 0.18768 | 122.8912 | 122.8958 | 0.23804 | -0.045776 | 122.7036 | 122.644 | 0.10529 | 122.8775 | 122.7814 | 0.13733 | 0.050354 | 123.1338 | 122.9004 | 122.8592 | -0.28839 | 123.0515 | 122.9965 | 122.9233 | -0.30212
2966.2969 | 123.0743 | -122.8134 | 0.20142 | 0.14435 | 0.028946 | 0.0055114 | 0.0042639 | -0.0079702 | 0.0039242 | -0.0060883 | 0.071487 | -0.0097775 | -0.0041164 | -0.0015488 | 0.0075259 | -0.01358 | 0.004578 | -0.013733 | -0.059509 | 0.009155 | 0.25177 | -0.050354 | -0.23804 | 0.032043 | 0.032043 | -0.073242 | 0.1831 | 0.16937 | -0.11444 | -0.1831 | 122.7631 | 122.5754 | 0.050354 | 122.7997 | 122.8226 | 0.24719 | -0.19684 | 122.699 | 122.6303 | -0.018311 | 122.8455 | 122.7402 | 0.10986 | -0.032043 | 123.0652 | 122.818 | 122.7539 | -0.43945 | 122.9965 | 122.9828 | 122.8455 | -0.38452
2968.0469 | 123.1247 | -122.7951 | 0.17395 | -0.2066 | 0.028092 | 0.0044434 | 0.0111 | -0.0064748 | -0.0054752 | -0.0073701 | -0.14214 | -0.013836 | -0.0056118 | -0.00090781 | -0.00016447 | -0.014435 | 0.18768 | 0.28381 | 0.25635 | 0.20599 | 0.36621 | 0.11444 | -0.091553 | 0.23804 | 0.32501 | 0.19226 | 0.26093 | 0.23346 | -0.013733 | -0.036621 | 122.9095 | 122.7036 | 0.19226 | 123.0789 | 123.0011 | 0.29755 | 0.013733 | 122.7814 | 122.7585 | 0.086975 | 123.0331 | 122.9874 | 0.22888 | 0.059509 | 123.1613 | 122.9828 | 123.0515 | -0.2655 | 123.056 | 123.0286 | 123.1201 | -0.21057
2969.8125 | 123.0469 | -122.818 | 0.19684 | 0.1062 | 0.030869 | 0.004657 | 0.0040503 | -0.011602 | 0.0024288 | -0.0063019 | 0.025711 | -0.010632 | -0.0064664 | 0.00016019 | 0.0062441 | -0.014221 | 0.013733 | -0.018311 | -0.059509 | -0.004578 | 0.27924 | -0.018311 | -0.19684 | 0.022888 | 0.009155 | -0.09613 | 0.20142 | 0.16022 | -0.14191 | -0.18768 | 122.7997 | 122.6212 | 0.082398 | 122.7997 | 122.8134 | 0.19226 | -0.18311 | 122.6761 | 122.6303 | 0.004578 | 122.8409 | 122.7219 | 0.091553 | -0.036621 | 123.0972 | 122.8317 | 122.7585 | -0.39368 | 123.0194 | 122.9782 | 122.8271 | -0.38452
2971.5 | 123.0743 | -122.8043 | 0.17853 | 0.1825 | 0.027237 | 0.0050842 | 0.0044775 | -0.0088248 | -0.00077538 | -0.0050201 | 0.10963 | -0.012127 | -0.0068936 | -0.00090781 | 0.0066715 | -0.013153 | 0.086975 | 0.10986 | 0.050354 | 0.082397 | 0.22888 | -0.022888 | -0.19684 | 0.13733 | 0.15564 | 0.064087 | 0.16937 | 0.1236 | -0.091553 | -0.15106 | 122.7814 | 122.6074 | 0.050354 | 122.9141 | 122.8867 | 0.27924 | -0.091553 | 122.7127 | 122.6532 | -0.009155 | 122.9416 | 122.8683 | 0.21515 | -0.054932 | 123.0331 | 122.8912 | 122.8546 | -0.37537 | 122.9736 | 122.9279 | 122.9599 | -0.32959
2973.1875 | 123.0652 | -122.8043 | 0.20142 | -0.092163 | 0.0298 | 0.0067932 | 0.0051183 | -0.0062612 | 0.0024288 | -0.0082245 | -0.08873 | -0.0080685 | -0.0051846 | -0.0013352 | 0.0081667 | -0.014007 | 0.13733 | 0.1236 | 0.059509 | 0.07782 | 0.27924 | 0 | -0.16022 | 0.10071 | 0.1236 | -0.022888 | 0.21973 | 0.19226 | -0.11444 | -0.16022 | 122.8043 | 122.644 | 0.07782 | 122.9279 | 122.8821 | 0.23804 | -0.064087 | 122.6898 | 122.644 | 0.018311 | 122.905 | 122.7814 | 0.13733 | -0.009155 | 123.0835 | 122.9416 | 122.8638 | -0.36163 | 123.024 | 122.9965 | 122.9279 | -0.36163
2974.9531 | 123.0927 | -122.8043 | 0.1831 | 0.17487 | 0.028092 | 0.0059388 | 0.0046911 | -0.0094656 | -0.00034818 | -0.0045929 | 0.14778 | -0.012555 | -0.0073208 | -0.0024032 | 0.0045351 | -0.014862 | 0.036621 | 0.059509 | 0.027466 | 0.022888 | 0.21973 | -0.045776 | -0.20599 | 0.10071 | 0.1236 | 0.027466 | 0.16937 | 0.12817 | -0.091553 | -0.16479 | 122.7585 | 122.5983 | 0.036622 | 122.8638 | 122.8271 | 0.22888 | -0.14648 | 122.7127 | 122.6395 | -0.013732 | 122.905 | 122.8317 | 0.19226 | -0.054931 | 123.024 | 122.8409 | 122.8317 | -0.3891 | 122.9736 | 122.9324 | 122.9279 | -0.3479
2976.6562 | 123.0377 | -122.8455 | 0.19226 | 0.029907 | 0.032364 | 0.004657 | 0.0051183 | -0.008611 | 0.0037106 | -0.0058747 | 0.018082 | -0.0087093 | -0.00668 | -0.0011216 | 0.0077395 | -0.014007 | 0.032043 | 0.009155 | -0.041199 | 0.013733 | 0.26093 | -0.059509 | -0.21057 | -0.004578 | 0.009155 | -0.10071 | 0.21515 | 0.17395 | -0.1236 | -0.20142 | 122.7859 | 122.6349 | 0.068664 | 122.8546 | 122.8592 | 0.2243 | -0.16022 | 122.7219 | 122.644 | 0.022888 | 122.8409 | 122.7448 | 0.10071 | -0.018311 | 123.1064 | 122.8775 | 122.8043 | -0.40283 | 123.0606 | 123.0194 | 122.8546 | -0.39368
2978.4062 | 123.1476 | -122.7905 | 0.16479 | -0.26001 | 0.030869 | 0.0057252 | 0.0076819 | -0.0081838 | -0.0024844 | -0.0073701 | -0.21843 | -0.010205 | -0.0056118 | -0.0015488 | 0.0019717 | -0.014435 | 0.14191 | 0.1236 | 0.09613 | 0.13733 | 0.40741 | 0.050354 | -0.10986 | 0.09613 | 0.15106 | 0.032043 | 0.29297 | 0.26093 | -0.054932 | -0.10529 | 122.8409 | 122.6807 | 0.24261 | 122.9141 | 122.9279 | 0.24719 | -0.022888 | 122.7356 | 122.6852 | 0.12817 | 122.8867 | 122.8226 | 0.13733 | 0.09613 | 123.1979 | 122.9324 | 122.8867 | -0.27466 | 123.0835 | 123.0515 | 122.9416 | -0.27008
2980.0938 | 123.0743 | -122.818 | 0.19226 | 0.15961 | 0.029587 | 0.0059388 | 0.0040503 | -0.0064748 | -0.0018436 | -0.0048065 | 0.13252 | -0.012127 | -0.0075344 | -0.0024032 | 0.0051761 | -0.013794 | 0.09613 | 0.082397 | 0.073242 | 0.07782 | 0.21973 | -0.022888 | -0.16937 | 0.11902 | 0.13733 | 0.054932 | 0.14648 | 0.13733 | -0.086975 | -0.14191 | 122.7951 | 122.6486 | 0.027466 | 122.9004 | 122.8958 | 0.24719 | -0.096131 | 122.731 | 122.6761 | -0.045777 | 122.937 | 122.8729 | 0.19684 | -0.054932 | 123.0377 | 122.9141 | 122.8912 | -0.36163 | 122.9645 | 122.9553 | 122.9553 | -0.33417
2981.8438 | 123.0606 | -122.8043 | 0.1831 | 0.20538 | 0.0298 | 0.0052978 | 0.0038367 | -0.0098928 | -0.00013458 | -0.0058747 | 0.18593 | -0.012768 | -0.0056118 | -0.0011216 | 0.0058169 | -0.016357 | 0.059509 | 0.018311 | 0 | 0.022888 | 0.22888 | -0.036621 | -0.20142 | 0.10071 | 0.12817 | 0.027466 | 0.16937 | 0.13733 | -0.1236 | -0.14648 | 122.7676 | 122.6028 | 0.045777 | 122.8226 | 122.8271 | 0.2243 | -0.1236 | 122.6807 | 122.6578 | -0.013732 | 122.905 | 122.8317 | 0.17395 | -0.045776 | 123.0331 | 122.8638 | 122.8043 | -0.38452 | 122.9736 | 122.9416 | 122.9324 | -0.32959
2983.5938 | 123.1613 | -122.7722 | 0.16937 | -0.19897 | 0.031937 | 0.0070068 | 0.0066137 | -0.008611 | -0.00034818 | -0.0077973 | -0.18791 | -0.012127 | -0.0030484 | -0.0017624 | 0.0036807 | -0.012085 | 0.1236 | 0.09613 | 0.07782 | 0.12817 | 0.37994 | 0.050354 | -0.11902 | 0.073242 | 0.14648 | 0.022888 | 0.28381 | 0.25635 | -0.054932 | -0.11444 | 122.8226 | 122.6532 | 0.21057 | 122.8683 | 122.9004 | 0.24719 | -0.045777 | 122.7173 | 122.6578 | 0.11444 | 122.8455 | 122.7951 | 0.13733 | 0.086975 | 123.1522 | 122.8958 | 122.85 | -0.28839 | 123.056 | 123.0286 | 122.9187 | -0.28381
2985.2969 | 122.9965 | -122.8134 | 0.19226 | 0.098572 | 0.028092 | 0.006366 | 0.0068273 | -0.011815 | -0.005048 | -0.0088653 | 0.20119 | -0.011914 | -0.0043302 | -0.0030442 | 0.0036807 | -0.011657 | 0.11902 | 0.13275 | 0.10071 | 0.082397 | 0.21515 | 0.004578 | -0.16937 | 0.12817 | 0.16479 | 0.059509 | 0.16937 | 0.14648 | -0.10071 | -0.16937 | 122.818 | 122.644 | 0.022888 | 122.9462 | 122.8958 | 0.25177 | -0.073242 | 122.7127 | 122.644 | -0.022888 | 122.9416 | 122.8729 | 0.22888 | -0.045777 | 123.0286 | 122.9324 | 122.9141 | -0.36163 | 122.9828 | 122.9599 | 122.9782 | -0.36163
2987.0469 | 123.111 | -122.8043 | 0.17853 | -0.10742 | 0.030014 | 0.0042298 | 0.0076819 | -0.0081838 | 0.0022152 | -0.0071563 | -0.11925 | -0.0093503 | -0.0058254 | -0.0017624 | 0.0032535 | -0.016357 | 0.16022 | 0.10529 | 0.064087 | 0.082397 | 0.27924 | -0.004578 | -0.16022 | 0.09613 | 0.13733 | -0.022888 | 0.21515 | 0.18768 | -0.09613 | -0.14191 | 122.7997 | 122.644 | 0.10071 | 122.9095 | 122.8867 | 0.24261 | -0.018311 | 122.7081 | 122.6624 | 0.036621 | 122.9004 | 122.7814 | 0.11902 | 0.009155 | 123.0835 | 122.9645 | 122.8683 | -0.33874 | 123.0194 | 122.9919 | 122.9416 | -0.32044
2988.7344 | 123.143 | -122.7768 | 0.16022 | -0.11505 | 0.030441 | 0.0042298 | 0.0059729 | -0.0066884 | 0.001788 | -0.0065155 | -0.13451 | -0.010418 | -0.0041164 | -0.0017624 | 0.0062441 | -0.014221 | 0.1236 | 0.10071 | 0.064087 | 0.10529 | 0.32959 | 0.009155 | -0.16479 | 0.10529 | 0.15564 | 0 | 0.21973 | 0.20142 | -0.09613 | -0.14648 | 122.7859 | 122.612 | 0.16937 | 122.8775 | 122.8821 | 0.27008 | -0.036621 | 122.6807 | 122.6303 | 0.05951 | 122.8821 | 122.7768 | 0.14648 | 0.041199 | 123.1064 | 122.9004 | 122.8409 | -0.32501 | 122.9965 | 122.9782 | 122.9324 | -0.3067
2990.5 | 123.0286 | -122.8134 | 0.20599 | 0.17487 | 0.025742 | 0.0048706 | 0.0044775 | -0.0083974 | -0.0029118 | -0.0058747 | 0.18593 | -0.012127 | -0.00668 | -5.3406e-05 | 0.0030399 | -0.013794 | 0.082397 | 0.10986 | 0.10986 | 0.082397 | 0.21057 | -0.022888 | -0.17853 | 0.13733 | 0.16022 | 0.07782 | 0.15106 | 0.13733 | -0.086975 | -0.14648 | 122.7905 | 122.6349 | 0.004577 | 122.9233 | 122.8958 | 0.26092 | -0.1236 | 122.7264 | 122.6669 | -0.054932 | 122.9507 | 122.8912 | 0.2243 | -0.068665 | 123.024 | 122.8958 | 122.9233 | -0.38452 | 122.9645 | 122.9507 | 122.9736 | -0.35248
2992.1875 | 123.1155 | -122.7905 | 0.16022 | -0.18372 | 0.026596 | 0.0067932 | 0.0074683 | -0.005834 | -0.007825 | -0.010361 | -0.12688 | -0.014477 | -0.006039 | -0.0030442 | 0.0028263 | -0.014862 | 0.23346 | 0.27008 | 0.23804 | 0.21973 | 0.3479 | 0.09613 | -0.054932 | 0.20599 | 0.30212 | 0.17853 | 0.25635 | 0.25177 | 0.004578 | -0.059509 | 122.8867 | 122.7356 | 0.18768 | 123.0606 | 123.0103 | 0.27466 | 0.073242 | 122.7951 | 122.731 | 0.096131 | 122.9965 | 122.9691 | 0.23804 | 0.091553 | 123.1384 | 123.024 | 123.0286 | -0.21515 | 123.0469 | 123.0423 | 123.0927 | -0.21973
2993.9375 | 123.143 | -122.7722 | 0.16937 | -0.14557 | 0.027023 | 0.0055114 | 0.0098181 | -0.0094656 | -0.0037662 | -0.0086517 | -0.17265 | -0.013623 | -0.0068936 | -0.0017624 | 0.00068993 | -0.015503 | 0.25177 | 0.25635 | 0.23346 | 0.20599 | 0.32959 | 0.073242 | -0.07782 | 0.22888 | 0.31586 | 0.18768 | 0.25177 | 0.22888 | -0.004578 | -0.050354 | 122.8455 | 122.6944 | 0.16022 | 123.0286 | 122.9782 | 0.28381 | 0.082397 | 122.7676 | 122.7219 | 0.082397 | 123.0011 | 122.9599 | 0.23804 | 0.059509 | 123.1018 | 123.024 | 123.0057 | -0.24719 | 123.024 | 123.0011 | 123.0881 | -0.21973
2995.6875 | 123.1476 | -122.8043 | 0.1831 | -0.13031 | 0.026596 | 0.0033752 | 0.0070409 | -0.0045522 | -0.0031254 | -0.010788 | -0.12688 | -0.01405 | -0.0041164 | -0.00069421 | 0.0023989 | -0.01593 | 0.23346 | 0.27008 | 0.21973 | 0.20599 | 0.33417 | 0.082397 | -0.086975 | 0.2243 | 0.31128 | 0.1831 | 0.25177 | 0.22888 | -0.004578 | -0.059509 | 122.8867 | 122.7173 | 0.15106 | 123.0743 | 123.0103 | 0.29297 | 0.050354 | 122.7997 | 122.7448 | 0.068665 | 123.0286 | 122.9874 | 0.24261 | 0.045777 | 123.1384 | 123.0377 | 123.024 | -0.27008 | 123.056 | 123.0331 | 123.1155 | -0.24261
2997.375 | 123.0423 | -122.8271 | 0.21515 | -0.00061023 | 0.029373 | 0.00038459 | 0.0055457 | -0.0064748 | 0.0039242 | -0.0071563 | -0.058212 | -0.0093503 | -0.0051846 | -0.00090781 | 0.0077395 | -0.018707 | 0.11444 | 0.041199 | -0.004578 | 0.032043 | 0.30212 | -0.018311 | -0.19684 | 0.027466 | 0.036621 | -0.10071 | 0.1831 | 0.1831 | -0.1236 | -0.18768 | 122.8088 | 122.6303 | 0.086975 | 122.8683 | 122.8592 | 0.22888 | -0.10071 | 122.7036 | 122.6395 | -0.032044 | 122.8546 | 122.7264 | 0.086975 | -0.032044 | 123.1293 | 122.9416 | 122.8226 | -0.41199 | 123.0103 | 123.0103 | 122.8638 | -0.40283
2999.125 | 123.0743 | -122.8088 | 0.20599 | 0.15198 | 0.027023 | 0.0038024 | 0.0017005 | -0.0083974 | 7.902e-05 | -0.0067291 | 0.16304 | -0.011273 | -0.0073208 | -0.00026701 | 0.0053897 | -0.012939 | 0.1236 | 0.10071 | 0.086975 | 0.091553 | 0.2243 | -0.004578 | -0.16479 | 0.14191 | 0.14191 | 0.036621 | 0.14648 | 0.11444 | -0.10071 | -0.15106 | 122.8043 | 122.644 | 0.01831 | 122.9095 | 122.9004 | 0.25635 | -0.082398 | 122.7081 | 122.6578 | -0.05951 | 122.9507 | 122.8455 | 0.18768 | -0.091553 | 123.0331 | 122.9324 | 122.8958 | -0.37079 | 122.9553 | 122.9233 | 122.9507 | -0.35706
3000.8281 | 123.1338 | -122.8134 | 0.1831 | -0.12268 | 0.031509 | 0.0050842 | 0.0059729 | -0.010106 | 0.0024288 | -0.0080109 | -0.12688 | -0.0082821 | -0.0043302 | -0.0028306 | 0.0070987 | -0.018921 | 0.14191 | 0.11444 | 0.059509 | 0.10986 | 0.31586 | 0.013733 | -0.16937 | 0.11902 | 0.14191 | 0 | 0.23346 | 0.19226 | -0.09613 | -0.16022 | 122.8271 | 122.644 | 0.13275 | 122.9279 | 122.9233 | 0.27924 | -0.041198 | 122.7173 | 122.6532 | 0.050354 | 122.9324 | 122.8134 | 0.16022 | 0.009156 | 123.1293 | 122.9553 | 122.8729 | -0.35248 | 123.0469 | 123.0057 | 122.9553 | -0.34332
3002.5781 | 123.1476 | -122.7676 | 0.17395 | -0.12268 | 0.02681 | 0.0076478 | 0.0087499 | -0.0083974 | -0.006757 | -0.0075837 | -0.073471 | -0.013409 | -0.0034756 | -0.0021896 | 0.00026273 | -0.013153 | 0.20142 | 0.29297 | 0.23804 | 0.21057 | 0.32959 | 0.09613 | -0.07782 | 0.2243 | 0.32959 | 0.20142 | 0.25635 | 0.21973 | -0.013733 | -0.050354 | 122.8638 | 122.6898 | 0.15564 | 123.0606 | 122.9782 | 0.28839 | 0.027466 | 122.7539 | 122.7173 | 0.082398 | 122.9919 | 122.9691 | 0.25177 | 0.045777 | 123.0972 | 122.9691 | 123.0057 | -0.25177 | 123.024 | 122.9874 | 123.0972 | -0.2243
3004.2812 | 123.0331 | -122.8317 | 0.18768 | 0.16724 | 0.027451 | 0.0067932 | 0.0038367 | -0.0062612 | 0.00029262 | -0.0067291 | 0.20119 | -0.011487 | -0.0071072 | 0.0010148 | 0.0045351 | -0.014862 | 0.10071 | 0.10986 | 0.091553 | 0.086975 | 0.21057 | -0.036621 | -0.20599 | 0.13275 | 0.14648 | 0.059509 | 0.13733 | 0.09613 | -0.12817 | -0.16479 | 122.7951 | 122.6257 | 0.022888 | 122.9416 | 122.9187 | 0.29297 | -0.086975 | 122.7036 | 122.6669 | -0.050354 | 122.9645 | 122.8912 | 0.2243 | -0.091553 | 123.0423 | 122.9324 | 122.9233 | -0.39368 | 122.9691 | 122.9279 | 122.9782 | -0.35248
3006.0312 | 123.0881 | -122.818 | 0.19226 | 0.1825 | 0.029587 | 0.0050842 | 0.0044775 | -0.0060476 | -0.00077538 | -0.0069427 | 0.12489 | -0.010205 | -0.0053982 | -0.001976 | 0.0070987 | -0.014435 | 0.064087 | 0.07782 | 0.041199 | 0.054932 | 0.22888 | -0.036621 | -0.19226 | 0.13275 | 0.14191 | 0.054932 | 0.16022 | 0.13275 | -0.09613 | -0.17853 | 122.7814 | 122.6257 | 0.036621 | 122.8958 | 122.8729 | 0.24719 | -0.12817 | 122.7219 | 122.6395 | -0.032044 | 122.9507 | 122.8729 | 0.23346 | -0.05951 | 123.0469 | 122.8821 | 122.8592 | -0.38452 | 122.9782 | 122.9507 | 122.9599 | -0.37079
3007.7812 | 123.0469 | -122.818 | 0.21515 | 0.060425 | 0.022965 | 0.0033752 | 0.0061865 | -0.0081838 | -0.0054752 | -0.0065155 | 0.11726 | -0.012982 | -0.007748 | -0.0045394 | 0.0053897 | -0.013366 | 0.10071 | 0.1236 | 0.10986 | 0.09613 | 0.28381 | 0.009155 | -0.13733 | 0.14648 | 0.17853 | 0.091553 | 0.2243 | 0.19684 | -0.050354 | -0.11902 | 122.8271 | 122.6807 | 0.068664 | 122.9416 | 122.9141 | 0.23346 | -0.11444 | 122.7676 | 122.699 | 0.009155 | 122.9645 | 122.9095 | 0.21057 | -0.018311 | 123.1018 | 122.9187 | 122.9279 | -0.35248 | 123.0423 | 123.0148 | 122.9965 | -0.33417
3009.4844 | 123.143 | -122.7905 | 0.19684 | -0.2066 | 0.029587 | 0.0078614 | 0.0061865 | -0.0073294 | -0.0022708 | -0.0082245 | -0.23369 | -0.0095639 | -0.00668 | -0.0011216 | 0.0053897 | -0.014435 | 0.16937 | 0.12817 | 0.10071 | 0.14191 | 0.40741 | 0.068665 | -0.10071 | 0.10529 | 0.16937 | 0.036621 | 0.31586 | 0.27466 | -0.045776 | -0.086975 | 122.8592 | 122.6898 | 0.21057 | 122.9187 | 122.9324 | 0.24262 | -0.027465 | 122.7448 | 122.7036 | 0.11902 | 122.8958 | 122.8271 | 0.1236 | 0.07782 | 123.1979 | 122.9599 | 122.8912 | -0.29755 | 123.1064 | 123.0652 | 122.9599 | -0.28381
3011.2344 | 123.0469 | -122.8317 | 0.20142 | 0.060425 | 0.023605 | 0.007434 | 0.0027685 | -0.010534 | -0.0046206 | -0.0075837 | 0.079117 | -0.011487 | -0.0047574 | -0.001976 | 0.0038943 | -0.01358 | 0.11902 | 0.12817 | 0.12817 | 0.10529 | 0.31128 | 0.018311 | -0.11444 | 0.13733 | 0.1831 | 0.082397 | 0.23346 | 0.21057 | -0.050354 | -0.10986 | 122.85 | 122.7173 | 0.10986 | 122.9599 | 122.937 | 0.21973 | -0.082397 | 122.7814 | 122.7219 | 0.032043 | 122.9691 | 122.9141 | 0.19226 | 0.009155 | 123.143 | 122.9507 | 122.9599 | -0.31586 | 123.0652 | 123.0423 | 123.0148 | -0.31128
3012.9844 | 123.1567 | -122.7768 | 0.17395 | -0.084534 | 0.027237 | 0.0078614 | 0.0078955 | -0.0090384 | -0.0041934 | -0.0082245 | -0.096359 | -0.010632 | -0.0053982 | -0.0021896 | 0.00090353 | -0.014435 | 0.21973 | 0.22888 | 0.20599 | 0.19226 | 0.32959 | 0.07782 | -0.068665 | 0.23346 | 0.27008 | 0.18768 | 0.27008 | 0.23346 | -0.009155 | -0.068665 | 122.8546 | 122.7081 | 0.15564 | 123.0057 | 122.9691 | 0.26093 | 0.045777 | 122.7676 | 122.7081 | 0.096131 | 123.0103 | 122.9645 | 0.25635 | 0.059509 | 123.1064 | 122.9965 | 122.9828 | -0.24261 | 123.0469 | 123.0103 | 123.0469 | -0.24261
3014.75 | 123.1201 | -122.7997 | 0.19684 | -0.16083 | 0.030014 | 0.0059388 | 0.0098181 | -0.0064748 | -0.0022708 | -0.010574 | -0.24132 | -0.011273 | -0.003262 | -0.00048061 | 0.0021853 | -0.01593 | 0.21515 | 0.23804 | 0.20142 | 0.21057 | 0.35248 | 0.082397 | -0.068665 | 0.18768 | 0.27466 | 0.11902 | 0.27466 | 0.23804 | -0.027466 | -0.07782 | 122.8821 | 122.731 | 0.15564 | 123.0377 | 123.0103 | 0.27924 | 0.018311 | 122.7722 | 122.7219 | 0.07782 | 122.9874 | 122.9187 | 0.19684 | 0.041199 | 123.1522 | 123.0148 | 123.0011 | -0.2655 | 123.0743 | 123.0377 | 123.0743 | -0.27466
3016.5156 | 123.0148 | -122.8683 | 0.19684 | 0.090942 | 0.023392 | 0.0065796 | 0.0055457 | -0.0081838 | -0.00056178 | -0.0092927 | 0.13252 | -0.011487 | -0.0058254 | -0.0021896 | 0.0034671 | -0.015289 | 0.10986 | 0.14191 | 0.091553 | 0.082397 | 0.25177 | -0.009155 | -0.16479 | 0.15106 | 0.14648 | 0.073242 | 0.17395 | 0.14191 | -0.10986 | -0.12817 | 122.8592 | 122.7036 | 0.054932 | 123.0103 | 122.9507 | 0.24719 | -0.086975 | 122.7585 | 122.7402 | -0.022888 | 123.0194 | 122.9416 | 0.20142 | -0.054931 | 123.1201 | 122.9782 | 122.9599 | -0.36163 | 123.0423 | 123.0103 | 123.0148 | -0.32501
3018.2031 | 123.0835 | -122.8088 | 0.16937 | 0.16724 | 0.028946 | 0.0055114 | 0.00084592 | -0.0073294 | 0.00093342 | -0.0073701 | 0.086746 | -0.012555 | -0.0081754 | -0.0013352 | 0.0070987 | -0.01593 | 0.1236 | 0.086975 | 0.068665 | 0.073242 | 0.20599 | -0.027466 | -0.18768 | 0.14648 | 0.14191 | 0.032043 | 0.16022 | 0.11902 | -0.10529 | -0.15564 | 122.7814 | 122.6212 | 0.036621 | 122.8958 | 122.8821 | 0.26092 | -0.045777 | 122.7036 | 122.6532 | -0.009156 | 122.9553 | 122.8409 | 0.18768 | -0.050354 | 123.0148 | 122.9324 | 122.8775 | -0.35706 | 122.9691 | 122.9279 | 122.9507 | -0.32501
3019.9688 | 123.1796 | -122.7814 | 0.1831 | -0.17609 | 0.030441 | 0.004657 | 0.0081091 | -0.009252 | 0.0013608 | -0.0063019 | -0.26421 | -0.010632 | -0.0071072 | -0.00048061 | 0.0056033 | -0.01593 | 0.15106 | 0.10071 | 0.068665 | 0.12817 | 0.37994 | 0.041199 | -0.11902 | 0.11902 | 0.14191 | 0.013733 | 0.28839 | 0.24719 | -0.059509 | -0.11902 | 122.8226 | 122.6624 | 0.19684 | 122.8821 | 122.9095 | 0.24719 | -0.032043 | 122.7219 | 122.6624 | 0.10529 | 122.9004 | 122.7951 | 0.13275 | 0.064087 | 123.1613 | 122.9324 | 122.85 | -0.30212 | 123.0698 | 123.0286 | 122.9233 | -0.30212
3021.7344 | 123.0469 | -122.8226 | 0.20142 | -0.046387 | 0.033432 | 0.004657 | 0.0051183 | -0.0071158 | 0.0024288 | -0.0035249 | -0.081101 | -0.010632 | -0.006039 | -0.0021896 | 0.0090213 | -0.01593 | 0.14191 | 0.09613 | 0.027466 | 0.073242 | 0.30212 | -0.009155 | -0.20142 | 0.068665 | 0.10071 | -0.059509 | 0.20142 | 0.17853 | -0.13275 | -0.16937 | 122.8134 | 122.6212 | 0.10071 | 122.9187 | 122.8958 | 0.27466 | -0.059509 | 122.6898 | 122.6532 | 0 | 122.8912 | 122.7631 | 0.10986 | -0.022888 | 123.1247 | 122.9645 | 122.85 | -0.40283 | 123.024 | 123.0011 | 122.9233 | -0.37079
3023.4375 | 123.0331 | -122.85 | 0.18768 | 0.12146 | 0.028305 | 0.0067932 | 0.0053321 | -0.0079702 | -0.0052616 | -0.0063019 | 0.11726 | -0.012341 | -0.0047574 | -0.0049668 | 0.0011173 | -0.012512 | 0.09613 | 0.14648 | 0.10986 | 0.086975 | 0.23346 | -0.018311 | -0.14648 | 0.14191 | 0.16937 | 0.091553 | 0.19226 | 0.1831 | -0.059509 | -0.12817 | 122.8317 | 122.7036 | 0.045776 | 122.9965 | 122.937 | 0.23346 | -0.091553 | 122.7905 | 122.7219 | 0.004578 | 122.9919 | 122.9416 | 0.21973 | -0.004578 | 123.0835 | 122.9462 | 122.9599 | -0.33417 | 123.0423 | 123.0331 | 123.0194 | -0.31586
3025.2031 | 123.0194 | -122.8043 | 0.21515 | 0.083313 | 0.027237 | 0.0067932 | 0.0057593 | -0.007543 | -0.0024844 | -0.0065155 | 0.17067 | -0.0117 | -0.0041164 | -0.001976 | 0.0032535 | -0.014221 | 0.10071 | 0.14191 | 0.10071 | 0.073242 | 0.23804 | 0.009155 | -0.16479 | 0.13275 | 0.15564 | 0.07782 | 0.1831 | 0.14648 | -0.07782 | -0.1236 | 122.8134 | 122.6395 | 0.022888 | 122.9462 | 122.8775 | 0.23804 | -0.11444 | 122.7264 | 122.6807 | -0.032044 | 122.937 | 122.8821 | 0.20142 | -0.068665 | 123.0423 | 122.905 | 122.905 | -0.37994 | 122.9874 | 122.9507 | 122.9599 | -0.33875
3026.9688 | 123.1613 | -122.7722 | 0.1831 | -0.099793 | 0.027451 | 0.007434 | 0.0081091 | -0.007543 | -0.0048344 | -0.0077973 | -0.11162 | -0.011914 | -0.0053982 | -0.003685 | 0.0011173 | -0.013153 | 0.21057 | 0.26093 | 0.20599 | 0.19684 | 0.32959 | 0.07782 | -0.10529 | 0.23346 | 0.29297 | 0.20599 | 0.25635 | 0.21057 | 0 | -0.050354 | 122.85 | 122.6669 | 0.14649 | 123.0331 | 122.9691 | 0.30212 | 0.027466 | 122.7722 | 122.7219 | 0.073243 | 123.0057 | 122.9782 | 0.25635 | 0.027466 | 123.1018 | 122.9828 | 122.9782 | -0.28839 | 123.0286 | 122.9828 | 123.0652 | -0.23346
3028.6562 | 123.1522 | -122.7722 | 0.17395 | -0.11505 | 0.025955 | 0.0042298 | 0.0087499 | -0.0077566 | -0.0037662 | -0.010361 | -0.08873 | -0.013623 | -0.0045438 | -0.0024032 | 0.0011173 | -0.014648 | 0.21515 | 0.29297 | 0.23346 | 0.20599 | 0.32959 | 0.073242 | -0.082397 | 0.27008 | 0.32044 | 0.19684 | 0.26093 | 0.23804 | -0.027466 | -0.059509 | 122.8455 | 122.6898 | 0.15564 | 123.0652 | 122.9782 | 0.28839 | 0.041199 | 122.7448 | 122.7127 | 0.086975 | 123.0423 | 122.9691 | 0.25635 | 0.064087 | 123.1018 | 122.9874 | 123.0057 | -0.25635 | 123.0331 | 123.0103 | 123.0927 | -0.23346
3030.375 | 123.1476 | -122.7951 | 0.17395 | -0.26764 | 0.030228 | 0.0067932 | 0.0064001 | -0.0090384 | 7.902e-05 | -0.0054475 | -0.29472 | -0.010418 | -0.0068936 | -0.0028306 | 0.0047489 | -0.015075 | 0.16022 | 0.15106 | 0.091553 | 0.13733 | 0.39825 | 0.07782 | -0.09613 | 0.10986 | 0.15564 | 0.032043 | 0.32044 | 0.2655 | -0.059509 | -0.10071 | 122.8729 | 122.699 | 0.2243 | 122.9462 | 122.9324 | 0.23346 | -0.013733 | 122.7356 | 122.6944 | 0.14649 | 122.905 | 122.8271 | 0.13275 | 0.091553 | 123.1934 | 122.9553 | 122.8867 | -0.27008 | 123.1155 | 123.0606 | 122.9507 | -0.27466
3032.125 | 123.0423 | -122.85 | 0.18768 | 0.12909 | 0.025314 | 0.0085022 | 0.0066137 | -0.0096792 | -0.0039798 | -0.0056611 | 0.102 | -0.010205 | -0.010098 | -0.0024032 | 0.0041079 | -0.01358 | 0.13733 | 0.15106 | 0.11902 | 0.10071 | 0.25635 | 0.004578 | -0.15106 | 0.14191 | 0.17853 | 0.07782 | 0.21057 | 0.19684 | -0.064087 | -0.11444 | 122.8546 | 122.699 | 0.068665 | 123.0011 | 122.9507 | 0.25177 | -0.050354 | 122.7859 | 122.7356 | 0.022888 | 122.9919 | 122.9279 | 0.19226 | 0.009155 | 123.1064 | 122.9874 | 122.9691 | -0.33874 | 123.0606 | 123.0469 | 123.0286 | -0.30212
3033.8125 | 123.1384 | -122.8088 | 0.16479 | -0.17609 | 0.027451 | 0.006366 | 0.0051183 | -0.0077566 | -0.003339 | -0.0084381 | -0.14214 | -0.013623 | -0.0053982 | -0.0021896 | 0.0030399 | -0.013153 | 0.26093 | 0.27924 | 0.22888 | 0.21515 | 0.35248 | 0.11444 | -0.050354 | 0.23804 | 0.31586 | 0.16937 | 0.2655 | 0.22888 | -0.009155 | -0.045776 | 122.9233 | 122.7585 | 0.18768 | 123.0881 | 123.024 | 0.2655 | 0.09613 | 122.7997 | 122.7631 | 0.10071 | 123.0469 | 122.9782 | 0.21515 | 0.064087 | 123.1613 | 123.0698 | 123.0377 | -0.21515 | 123.0743 | 123.0377 | 123.1247 | -0.21057
3035.5938 | 123.1201 | -122.7951 | 0.16479 | -0.16846 | 0.028946 | 0.0040162 | 0.0074683 | -0.0069022 | -0.0022708 | -0.0080109 | -0.20317 | -0.014264 | -0.00668 | -0.001976 | 0.0041079 | -0.015075 | 0.22888 | 0.23346 | 0.19684 | 0.19226 | 0.32959 | 0.082397 | -0.068665 | 0.21057 | 0.28839 | 0.14648 | 0.2655 | 0.24261 | -0.013733 | -0.068665 | 122.8775 | 122.7264 | 0.16479 | 123.0286 | 122.9874 | 0.26093 | 0.064087 | 122.7814 | 122.7264 | 0.10071 | 123.0057 | 122.9416 | 0.21515 | 0.07782 | 123.1247 | 123.024 | 122.9919 | -0.23346 | 123.0606 | 123.0377 | 123.0835 | -0.23346
3037.2812 | 123.1476 | -122.7722 | 0.18768 | -0.16083 | 0.031937 | 0.0035888 | 0.0070409 | -0.0077566 | 0.0049924 | -0.0058747 | -0.22606 | -0.010418 | -0.0047574 | -0.0017624 | 0.0070987 | -0.018066 | 0.17853 | 0.12817 | 0.073242 | 0.11444 | 0.3479 | 0.009155 | -0.13733 | 0.11444 | 0.15564 | 0 | 0.25177 | 0.19684 | -0.09613 | -0.14648 | 122.7814 | 122.6349 | 0.16022 | 122.9004 | 122.8867 | 0.25177 | -0.009155 | 122.6761 | 122.6257 | 0.064087 | 122.8867 | 122.7722 | 0.14648 | 0.009155 | 123.1201 | 122.9507 | 122.8455 | -0.32501 | 123.024 | 122.9691 | 122.9279 | -0.33417
3039.0469 | 123.143 | -122.8043 | 0.17853 | -0.1532 | 0.031509 | 0.0048706 | 0.0038367 | -0.0049796 | 0.0028562 | -0.0050201 | -0.18028 | -0.0087093 | -0.0062528 | -0.0017624 | 0.0062441 | -0.016143 | 0.13275 | 0.12817 | 0.045776 | 0.10071 | 0.31586 | 0.013733 | -0.16479 | 0.1236 | 0.15564 | -0.009155 | 0.2243 | 0.19684 | -0.10071 | -0.16479 | 122.818 | 122.6395 | 0.13733 | 122.9324 | 122.905 | 0.2655 | -0.045777 | 122.7036 | 122.6395 | 0.045776 | 122.9279 | 122.7951 | 0.15564 | 0.01831 | 123.1201 | 122.937 | 122.85 | -0.34332 | 123.0286 | 123.0011 | 122.9599 | -0.34332
3040.8125 | 123.0377 | -122.8226 | 0.20142 | 0.052795 | 0.031723 | 0.0065796 | 0.0051183 | -0.0073294 | 0.0032834 | -0.0037385 | -0.012436 | -0.012555 | -0.0064664 | -0.0013352 | 0.0073123 | -0.015716 | 0.036621 | 0 | -0.054932 | 0.032043 | 0.26093 | -0.045776 | -0.20599 | 0.009155 | 0.045776 | -0.09613 | 0.19684 | 0.16937 | -0.15106 | -0.20599 | 122.7768 | 122.6166 | 0.059509 | 122.8226 | 122.8546 | 0.23804 | -0.1648 | 122.6715 | 122.6166 | -0.004578 | 122.8317 | 122.7264 | 0.10986 | -0.032043 | 123.0835 | 122.8592 | 122.7676 | -0.40741 | 123.0194 | 122.9919 | 122.8683 | -0.40741
3042.5156 | 123.0698 | -122.818 | 0.1831 | 0.16724 | 0.02681 | 0.0072204 | 0.0040503 | -0.0077566 | -0.0022708 | -0.0056611 | 0.1783 | -0.0117 | -0.0058254 | -0.0013352 | 0.0083805 | -0.015503 | 0.09613 | 0.10529 | 0.086975 | 0.07782 | 0.20599 | -0.018311 | -0.1831 | 0.14191 | 0.15106 | 0.059509 | 0.15564 | 0.13275 | -0.10986 | -0.16479 | 122.7997 | 122.6349 | 0.022889 | 122.9233 | 122.8958 | 0.26092 | -0.086975 | 122.7081 | 122.6532 | -0.027465 | 122.9599 | 122.8775 | 0.2243 | -0.050354 | 123.024 | 122.9141 | 122.905 | -0.36621 | 122.9736 | 122.9507 | 122.9691 | -0.3479
3044.2812 | 123.0331 | -122.8363 | 0.20142 | 0.15198 | 0.025742 | 0.0042298 | 0.0078955 | -0.0079702 | -0.003339 | -0.0069427 | 0.15541 | -0.011487 | -0.0068936 | -0.0024032 | 0.0023989 | -0.014007 | 0.10986 | 0.13275 | 0.11902 | 0.086975 | 0.21973 | -0.013733 | -0.17853 | 0.13275 | 0.1831 | 0.07782 | 0.17395 | 0.15106 | -0.09613 | -0.15106 | 122.8226 | 122.6578 | 0.018311 | 122.9691 | 122.9233 | 0.2655 | -0.091553 | 122.7402 | 122.6852 | -0.027466 | 122.9691 | 122.9141 | 0.22888 | -0.050354 | 123.056 | 122.9462 | 122.9553 | -0.37994 | 123.0103 | 122.9874 | 123.0194 | -0.35248
3046.0469 | 123.0743 | -122.8317 | 0.18768 | 0.11383 | 0.031296 | 0.0048706 | 0.0055457 | -0.0088248 | 0.00050622 | -0.0084381 | 0.094375 | -0.0095639 | -0.010312 | -0.0013352 | 0.0079531 | -0.014435 | 0.045776 | 0 | -0.036621 | -0.004578 | 0.2655 | -0.059509 | -0.21973 | 0.054932 | 0.036621 | -0.064087 | 0.21515 | 0.15106 | -0.14191 | -0.1831 | 122.7722 | 122.612 | 0.07782 | 122.8317 | 122.8271 | 0.21515 | -0.14191 | 122.6898 | 122.6486 | 0.027466 | 122.8867 | 122.7676 | 0.11902 | -0.036621 | 123.0972 | 122.8775 | 122.7951 | -0.40741 | 123.0469 | 122.9828 | 122.8683 | -0.37079
3047.75 | 123.0469 | -122.7997 | 0.19226 | 0.15961 | 0.030014 | 0.0065796 | 0.0055457 | -0.0077566 | 7.902e-05 | -0.0054475 | 0.19356 | -0.011059 | -0.0071072 | -0.0021896 | 0.0060305 | -0.01358 | 0.086975 | 0.11444 | 0.082397 | 0.082397 | 0.20599 | -0.041199 | -0.19226 | 0.1236 | 0.15106 | 0.050354 | 0.15564 | 0.10071 | -0.1236 | -0.16022 | 122.7585 | 122.6074 | 0.013733 | 122.9141 | 122.8821 | 0.27466 | -0.10529 | 122.6761 | 122.6395 | -0.036621 | 122.9233 | 122.85 | 0.21057 | -0.091553 | 123.0057 | 122.8867 | 122.8821 | -0.38452 | 122.9553 | 122.9004 | 122.9507 | -0.35248
3049.5156 | 123.1613 | -122.7997 | 0.17395 | -0.13794 | 0.02681 | 0.007434 | 0.0098181 | -0.010106 | -0.0059024 | -0.0082245 | -0.096359 | -0.011914 | -0.0062528 | -0.0047532 | 0.0026125 | -0.013794 | 0.24719 | 0.28381 | 0.24719 | 0.20599 | 0.34332 | 0.091553 | -0.082397 | 0.22888 | 0.32044 | 0.19226 | 0.26093 | 0.2243 | -0.013733 | -0.054932 | 122.8912 | 122.7173 | 0.16937 | 123.0835 | 123.0057 | 0.28839 | 0.073242 | 122.7859 | 122.7448 | 0.086975 | 123.0286 | 122.9919 | 0.24719 | 0.050354 | 123.143 | 123.0469 | 123.0469 | -0.25635 | 123.0606 | 123.024 | 123.1201 | -0.22888
3051.2031 | 123.0835 | -122.8363 | 0.21057 | 0.12909 | 0.034073 | 0.0038024 | 0.0091773 | -0.0069022 | 0.0011472 | -0.0075837 | 0.063858 | -0.012341 | -0.0041164 | -0.00069421 | 0.0066715 | -0.016143 | 0.027466 | -0.004578 | -0.059509 | 0.004578 | 0.27466 | -0.064087 | -0.21515 | 0.050354 | 0.032043 | -0.041199 | 0.19684 | 0.16022 | -0.13275 | -0.17853 | 122.7722 | 122.6212 | 0.064087 | 122.8317 | 122.8409 | 0.21973 | -0.18311 | 122.7036 | 122.6578 | -0.013733 | 122.8867 | 122.7951 | 0.13733 | -0.050354 | 123.111 | 122.8638 | 122.7768 | -0.42572 | 123.0331 | 122.9965 | 122.8683 | -0.3891
3052.9531 | 123.1018 | -122.8455 | 0.19226 | 0.075684 | 0.029587 | 0.0035888 | 0.0055457 | -0.01032 | 0.0011472 | -0.0050201 | 0.079117 | -0.0084957 | -0.0058254 | 0.00080099 | 0.0049625 | -0.01593 | 0.018311 | 0.004578 | -0.018311 | 0 | 0.2655 | -0.045776 | -0.2243 | 0.045776 | 0.050354 | -0.064087 | 0.20142 | 0.16937 | -0.14191 | -0.19684 | 122.7997 | 122.6212 | 0.073242 | 122.85 | 122.8455 | 0.2243 | -0.17395 | 122.7036 | 122.6486 | 0.009155 | 122.8912 | 122.7814 | 0.13275 | -0.022888 | 123.111 | 122.8638 | 122.8271 | -0.41656 | 123.0469 | 123.0148 | 122.8958 | -0.3891
3054.6406 | 123.0652 | -122.85 | 0.20142 | 0.12909 | 0.028305 | 0.0050842 | 0.0040503 | -0.0069022 | -0.00098918 | -0.0065155 | 0.18593 | -0.012555 | -0.0051846 | -0.0011216 | 0.0064577 | -0.014862 | 0.10071 | 0.13275 | 0.082397 | 0.07782 | 0.2243 | -0.027466 | -0.19226 | 0.11902 | 0.15106 | 0.054932 | 0.15564 | 0.10986 | -0.11444 | -0.16479 | 122.8226 | 122.6578 | 0.022888 | 122.9828 | 122.9279 | 0.27008 | -0.10071 | 122.7356 | 122.6852 | -0.045776 | 122.9691 | 122.905 | 0.21973 | -0.091553 | 123.0743 | 122.9507 | 122.9324 | -0.39368 | 123.0057 | 122.9599 | 123.0011 | -0.36621
3056.3906 | 123.0652 | -122.8134 | 0.1831 | 0.0070193 | 0.02446 | 0.006366 | 0.0049047 | -0.0098928 | -0.006757 | -0.0088653 | 0.079117 | -0.0117 | -0.008389 | -0.0021896 | 0.0015445 | -0.015503 | 0.11902 | 0.13275 | 0.13275 | 0.11902 | 0.30212 | 0.036621 | -0.13275 | 0.13275 | 0.19226 | 0.091553 | 0.23346 | 0.20599 | -0.045776 | -0.09613 | 122.85 | 122.6807 | 0.11902 | 122.9462 | 122.9324 | 0.25177 | -0.064086 | 122.7676 | 122.7173 | 0.050354 | 122.9462 | 122.905 | 0.18768 | 0.022889 | 123.1155 | 122.9324 | 122.9462 | -0.31586 | 123.0469 | 123.0194 | 123.0057 | -0.27924
3058.1406 | 123.0835 | -122.8088 | 0.19226 | 0.13672 | 0.029373 | 0.0057252 | 0.0051183 | -0.0071158 | 0.001788 | -0.0077973 | 0.15541 | -0.0095639 | -0.0058254 | -0.0038986 | 0.0047489 | -0.017639 | 0.12817 | 0.10071 | 0.07782 | 0.086975 | 0.2243 | -0.013733 | -0.17395 | 0.14648 | 0.15106 | 0.050354 | 0.15564 | 0.11444 | -0.10529 | -0.15564 | 122.7951 | 122.6349 | 0.032043 | 122.9095 | 122.8958 | 0.26092 | -0.064087 | 122.7036 | 122.6532 | -0.036621 | 122.9553 | 122.8592 | 0.20599 | -0.07782 | 123.0331 | 122.937 | 122.8867 | -0.36621 | 122.9645 | 122.9233 | 122.9599 | -0.3479
3059.8906 | 123.0789 | -122.8134 | 0.1831 | 0.16724 | 0.028732 | 0.0059388 | 0.0042639 | -0.007543 | -0.0014164 | -0.0065155 | 0.10963 | -0.013409 | -0.0064664 | -0.001976 | 0.0073123 | -0.016143 | 0.11902 | 0.086975 | 0.07782 | 0.073242 | 0.20599 | -0.041199 | -0.19226 | 0.13275 | 0.13733 | 0.045776 | 0.16937 | 0.13733 | -0.11444 | -0.14648 | 122.7722 | 122.6212 | 0.022889 | 122.9004 | 122.8867 | 0.2655 | -0.064086 | 122.699 | 122.6669 | -0.013732 | 122.9462 | 122.8592 | 0.19226 | -0.045776 | 123.0194 | 122.9324 | 122.8912 | -0.37537 | 122.9828 | 122.9507 | 122.9507 | -0.32959
3061.5781 | 123.1659 | -122.7905 | 0.16479 | -0.11505 | 0.028519 | 0.0059388 | 0.0083227 | -0.0096792 | -0.0071842 | -0.0082245 | -0.065842 | -0.014477 | -0.0075344 | -0.0017624 | 0.0023989 | -0.014648 | 0.22888 | 0.24261 | 0.22888 | 0.19226 | 0.33417 | 0.10071 | -0.068665 | 0.23346 | 0.30212 | 0.1831 | 0.24261 | 0.23346 | 0 | -0.059509 | 122.8912 | 122.7219 | 0.16937 | 123.0331 | 122.9828 | 0.26093 | 0.064087 | 122.7905 | 122.731 | 0.07782 | 123.024 | 122.9736 | 0.24261 | 0.068664 | 123.1247 | 123.0194 | 123.0194 | -0.23346 | 123.0331 | 123.024 | 123.0927 | -0.2243
3063.3438 | 123.1659 | -122.7585 | 0.1831 | -0.17609 | 0.028732 | 0.0055114 | 0.0059729 | -0.0054068 | 0.0024288 | -0.0069427 | -0.20317 | -0.0117 | -0.0053982 | -0.0011216 | 0.0045351 | -0.017212 | 0.16479 | 0.091553 | 0.07782 | 0.12817 | 0.33875 | 0.018311 | -0.13275 | 0.10071 | 0.15564 | 0.004578 | 0.25177 | 0.20599 | -0.07782 | -0.14648 | 122.7768 | 122.6257 | 0.15564 | 122.85 | 122.8867 | 0.26093 | -0.01831 | 122.6807 | 122.612 | 0.068665 | 122.8592 | 122.7631 | 0.15106 | 0.022889 | 123.0972 | 122.9233 | 122.8363 | -0.31586 | 123.0103 | 122.9645 | 122.9141 | -0.32959
3065.1094 | 123.1613 | -122.7951 | 0.16479 | -0.13031 | 0.030869 | 0.008075 | 0.0044775 | -0.0071158 | 0.0013608 | -0.0077973 | -0.18028 | -0.011487 | -0.0062528 | -0.0017624 | 0.0081667 | -0.016998 | 0.15106 | 0.10529 | 0.059509 | 0.11444 | 0.32044 | 0.022888 | -0.16022 | 0.10071 | 0.13733 | 0.013733 | 0.21973 | 0.21057 | -0.10071 | -0.14648 | 122.818 | 122.6349 | 0.15564 | 122.9004 | 122.9095 | 0.27466 | -0.013733 | 122.6944 | 122.6486 | 0.054932 | 122.8958 | 122.8088 | 0.16022 | 0.045776 | 123.1155 | 122.9462 | 122.8546 | -0.32501 | 123.0148 | 123.0057 | 122.9324 | -0.31128
3066.8594 | 123.1476 | -122.818 | 0.17395 | -0.22949 | 0.028732 | 0.0059388 | 0.010032 | -0.0060476 | -0.0029118 | -0.0065155 | -0.24132 | -0.013836 | -0.0056118 | -0.0024032 | 0.0034671 | -0.015289 | 0.13275 | 0.12817 | 0.10071 | 0.12817 | 0.39368 | 0.050354 | -0.10071 | 0.10071 | 0.16479 | 0.041199 | 0.32044 | 0.25635 | -0.064087 | -0.082397 | 122.8683 | 122.7173 | 0.21973 | 122.9462 | 122.9462 | 0.22888 | -0.041199 | 122.7539 | 122.7356 | 0.14649 | 122.9187 | 122.8592 | 0.1236 | 0.082398 | 123.2117 | 122.9507 | 122.9187 | -0.27466 | 123.1384 | 123.0743 | 122.9828 | -0.25635
3068.5625 | 123.0377 | -122.8088 | 0.19226 | 0.060425 | 0.031937 | 0.0057252 | 0.0051183 | -0.005834 | 0.0020016 | -0.0067291 | 0.048599 | -0.0084957 | -0.0064664 | -5.3406e-05 | 0.0083805 | -0.014862 | 0.032043 | -0.009155 | -0.050354 | 0.009155 | 0.28381 | -0.059509 | -0.2243 | 0.004578 | 0.027466 | -0.082397 | 0.21057 | 0.16022 | -0.15106 | -0.18768 | 122.7493 | 122.5845 | 0.091552 | 122.7997 | 122.818 | 0.23346 | -0.16022 | 122.6578 | 122.6212 | 0.01831 | 122.8134 | 122.7264 | 0.10529 | -0.032044 | 123.0927 | 122.8409 | 122.7585 | -0.41656 | 123.0194 | 122.9691 | 122.8363 | -0.37994
3070.3281 | 123.1796 | -122.7814 | 0.17395 | -0.22186 | 0.028946 | 0.0070068 | 0.0076819 | -0.0079702 | -0.00034818 | -0.0067291 | -0.2108 | -0.012127 | -0.0028348 | -0.0026168 | 0.0041079 | -0.014435 | 0.10529 | 0.11902 | 0.064087 | 0.13275 | 0.37994 | 0.050354 | -0.11444 | 0.091553 | 0.16022 | 0.032043 | 0.27466 | 0.25177 | -0.068665 | -0.1236 | 122.8317 | 122.6669 | 0.20599 | 122.9004 | 122.9141 | 0.24719 | -0.068664 | 122.7127 | 122.6578 | 0.10071 | 122.8729 | 122.8134 | 0.15564 | 0.07782 | 123.1613 | 122.8867 | 122.8455 | -0.28839 | 123.056 | 123.0331 | 122.9416 | -0.29755
3072.0781 | 123.1293 | -122.8226 | 0.16937 | -0.21423 | 0.028946 | 0.0061524 | 0.0078955 | -0.011175 | -0.0035526 | -0.0071563 | -0.21843 | -0.011273 | -0.0043302 | -0.0013352 | 0.0011173 | -0.013153 | 0.11444 | 0.13275 | 0.10529 | 0.13733 | 0.3891 | 0.050354 | -0.10071 | 0.09613 | 0.17395 | 0.054932 | 0.3067 | 0.27924 | -0.064087 | -0.10071 | 122.8729 | 122.7219 | 0.21973 | 122.9553 | 122.9599 | 0.23804 | -0.054932 | 122.7585 | 122.7219 | 0.13733 | 122.9187 | 122.8775 | 0.15564 | 0.10986 | 123.2117 | 122.937 | 122.9279 | -0.27008 | 123.1293 | 123.1018 | 122.9965 | -0.27008
3073.8281 | 123.1338 | -122.7905 | 0.16022 | -0.19135 | 0.028092 | 0.0067932 | 0.010886 | -0.0073294 | -0.0069706 | -0.0063019 | -0.11925 | -0.012768 | -0.0056118 | -0.0021896 | 0.00090353 | -0.015503 | 0.21057 | 0.28839 | 0.24719 | 0.21973 | 0.35248 | 0.10986 | -0.059509 | 0.19684 | 0.30212 | 0.17853 | 0.25635 | 0.22888 | -0.009155 | -0.064087 | 122.9004 | 122.731 | 0.19226 | 123.0789 | 123.0103 | 0.27924 | 0.050354 | 122.7814 | 122.7264 | 0.096131 | 122.9874 | 122.9691 | 0.24261 | 0.068665 | 123.143 | 123.0011 | 123.0377 | -0.21973 | 123.0469 | 123.0194 | 123.0927 | -0.2243
3075.5312 | 123.111 | -122.8134 | 0.18768 | -0.25238 | 0.030014 | 0.0070068 | 0.0070409 | -0.0083974 | -0.0012028 | -0.0073701 | -0.21843 | -0.0099911 | -0.0034756 | -0.0011216 | 0.0021853 | -0.015716 | 0.1831 | 0.18768 | 0.14648 | 0.16479 | 0.39368 | 0.059509 | -0.064087 | 0.1236 | 0.17853 | 0.050354 | 0.31128 | 0.26093 | -0.050354 | -0.10071 | 122.8729 | 122.7493 | 0.20599 | 123.0011 | 122.9782 | 0.22888 | -0.004578 | 122.7631 | 122.7127 | 0.1236 | 122.937 | 122.8638 | 0.15106 | 0.073242 | 123.2071 | 122.9965 | 122.9599 | -0.25177 | 123.1247 | 123.0743 | 122.9919 | -0.28839
3077.2812 | 123.0377 | -122.8226 | 0.21515 | 0.090942 | 0.031296 | 0.0055114 | 0.0059729 | -0.0079702 | 0.0015744 | -0.0058747 | 0.025711 | -0.010205 | -0.0051846 | -0.00090781 | 0.0079531 | -0.016998 | 0.032043 | -0.018311 | -0.054932 | 0.018311 | 0.27008 | -0.050354 | -0.2243 | -0.009155 | 0.013733 | -0.10986 | 0.21057 | 0.18768 | -0.1236 | -0.20142 | 122.7722 | 122.5983 | 0.054932 | 122.8043 | 122.8409 | 0.24261 | -0.18311 | 122.699 | 122.6212 | -0.004578 | 122.8134 | 122.7127 | 0.091553 | -0.027466 | 123.0927 | 122.8546 | 122.7676 | -0.43945 | 123.0331 | 123.0103 | 122.8363 | -0.41657
3078.9688 | 123.0881 | -122.8088 | 0.1831 | -0.061646 | 0.030655 | 0.0048706 | 0.0059729 | -0.008611 | 0.0032834 | -0.0084381 | -0.18028 | -0.012555 | -0.0030484 | -0.0021896 | 0.0062441 | -0.015503 | 0.12817 | 0.11444 | 0.050354 | 0.082397 | 0.29297 | -0.027466 | -0.16479 | 0.10071 | 0.13733 | -0.022888 | 0.21515 | 0.20142 | -0.11444 | -0.1831 | 122.7814 | 122.644 | 0.10986 | 122.9233 | 122.8912 | 0.24719 | -0.054931 | 122.6944 | 122.6257 | 0.032044 | 122.9095 | 122.7859 | 0.16022 | 0.018311 | 123.1018 | 122.937 | 122.8592 | -0.3479 | 123.024 | 123.0103 | 122.9462 | -0.36621
3080.7188 | 123.0194 | -122.8226 | 0.19684 | 0.16724 | 0.025314 | 0.0055114 | 0.0025549 | -0.0094656 | -0.0029118 | -0.0035249 | 0.15541 | -0.011487 | -0.0064664 | -0.0026168 | 0.0036807 | -0.012939 | 0.086975 | 0.13275 | 0.091553 | 0.086975 | 0.21515 | -0.013733 | -0.17395 | 0.14191 | 0.16479 | 0.068665 | 0.17395 | 0.14191 | -0.09613 | -0.14648 | 122.8088 | 122.6486 | 0.018311 | 122.9553 | 122.9095 | 0.26092 | -0.10986 | 122.7264 | 122.6761 | -0.022888 | 122.9645 | 122.8912 | 0.21515 | -0.054931 | 123.0377 | 122.9095 | 122.9141 | -0.37079 | 122.9965 | 122.9645 | 122.9874 | -0.34332
3082.4062 | 123.1567 | -122.7722 | 0.16022 | -0.046387 | 0.025314 | 0.007434 | 0.0066137 | -0.008611 | -0.0056888 | -0.0077973 | -0.027695 | -0.014905 | -0.0068936 | -0.0028306 | 0.00026273 | -0.014435 | 0.15564 | 0.19226 | 0.17853 | 0.17395 | 0.32959 | 0.073242 | -0.086975 | 0.20599 | 0.27008 | 0.19226 | 0.25635 | 0.23346 | -0.027466 | -0.068665 | 122.8455 | 122.6852 | 0.16937 | 122.9645 | 122.9462 | 0.26092 | -0.004577 | 122.7448 | 122.7036 | 0.096131 | 122.9782 | 122.9645 | 0.26093 | 0.073242 | 123.1018 | 122.9279 | 122.9507 | -0.24719 | 123.0286 | 123.0057 | 123.0423 | -0.22888
3084.1562 | 123.1613 | -122.7997 | 0.16022 | -0.11505 | 0.028946 | 0.0055114 | 0.0089635 | -0.009252 | -0.0035526 | -0.0075837 | -0.096359 | -0.013409 | -0.0058254 | -0.00069421 | 0.00068993 | -0.016998 | 0.23346 | 0.26093 | 0.20142 | 0.20599 | 0.33417 | 0.082397 | -0.068665 | 0.25635 | 0.32044 | 0.20142 | 0.24719 | 0.2243 | -0.022888 | -0.068665 | 122.8821 | 122.731 | 0.17395 | 123.0606 | 123.0057 | 0.27466 | 0.073242 | 122.7768 | 122.731 | 0.086975 | 123.056 | 123.0011 | 0.27008 | 0.064087 | 123.1338 | 123.0331 | 123.0011 | -0.22888 | 123.0469 | 123.024 | 123.1201 | -0.22888
3085.8594 | 123.175 | -122.7722 | 0.16937 | -0.23712 | 0.027878 | 0.0070068 | 0.0057593 | -0.0083974 | 0.00071982 | -0.0084381 | -0.24895 | -0.011059 | -0.0068936 | -0.0013352 | 0.0036807 | -0.016143 | 0.17395 | 0.12817 | 0.09613 | 0.14191 | 0.40283 | 0.073242 | -0.10529 | 0.10071 | 0.13275 | 0.018311 | 0.32501 | 0.27008 | -0.045776 | -0.11902 | 122.8455 | 122.6669 | 0.23346 | 122.9004 | 122.9141 | 0.24719 | 0.004577 | 122.7264 | 122.6532 | 0.15564 | 122.8729 | 122.7905 | 0.13733 | 0.10071 | 123.175 | 122.9462 | 122.8683 | -0.27466 | 123.0972 | 123.0423 | 122.905 | -0.28839
3087.6094 | 123.143 | -122.7951 | 0.16937 | -0.16083 | 0.029587 | 0.0059388 | 0.0081091 | -0.0096792 | -0.0052616 | -0.0075837 | -0.17265 | -0.012555 | -0.0056118 | -0.001976 | 0.0041079 | -0.012726 | 0.23804 | 0.28381 | 0.23346 | 0.21057 | 0.33417 | 0.086975 | -0.064087 | 0.23804 | 0.31586 | 0.1831 | 0.26093 | 0.23804 | -0.004578 | -0.050354 | 122.8821 | 122.731 | 0.16479 | 123.0789 | 123.0057 | 0.27466 | 0.068664 | 122.7905 | 122.7448 | 0.091552 | 123.0331 | 122.9782 | 0.23346 | 0.068664 | 123.1293 | 123.0331 | 123.0286 | -0.23346 | 123.056 | 123.0331 | 123.111 | -0.21973
3089.2969 | 123.1293 | -122.7951 | 0.16937 | -0.22186 | 0.027878 | 0.0050842 | 0.0066137 | -0.0088248 | -0.0031254 | -0.0080109 | -0.17265 | -0.010205 | -0.0051846 | -0.0024032 | 0.0032535 | -0.016784 | 0.24719 | 0.25635 | 0.23346 | 0.21057 | 0.36621 | 0.10529 | -0.064087 | 0.21057 | 0.29755 | 0.15564 | 0.27924 | 0.23346 | -0.018311 | -0.07782 | 122.9004 | 122.731 | 0.19684 | 123.0515 | 123.0057 | 0.27466 | 0.077819 | 122.7768 | 122.7173 | 0.10986 | 123.0057 | 122.9507 | 0.23346 | 0.064086 | 123.1613 | 123.0423 | 123.0286 | -0.23346 | 123.0743 | 123.0286 | 123.0927 | -0.24719
3091.0469 | 123.175 | -122.7997 | 0.18768 | -0.26001 | 0.032364 | 0.004657 | 0.0098181 | -0.0056204 | 0.0011472 | -0.0084381 | -0.21843 | -0.0087093 | -0.0041164 | 0.001442 | 0.0049625 | -0.016784 | 0.16479 | 0.12817 | 0.10071 | 0.13733 | 0.40283 | 0.068665 | -0.11444 | 0.10986 | 0.13733 | 0.009155 | 0.28839 | 0.25177 | -0.064087 | -0.10986 | 122.8683 | 122.6852 | 0.21515 | 122.9279 | 122.937 | 0.25177 | -0.022888 | 122.7356 | 122.6898 | 0.10071 | 122.9095 | 122.8088 | 0.11902 | 0.064087 | 123.2025 | 122.9645 | 122.9004 | -0.30212 | 123.0881 | 123.0515 | 122.937 | -0.29755
3092.7969 | 123.1567 | -122.7905 | 0.17853 | -0.099793 | 0.031937 | 0.0044434 | 0.0059729 | -0.005834 | 0.0032834 | -0.0071563 | -0.18791 | -0.0089229 | -0.0051846 | -0.0013352 | 0.0077395 | -0.015503 | 0.13733 | 0.1236 | 0.059509 | 0.10529 | 0.31586 | 0 | -0.16937 | 0.10986 | 0.14191 | -0.027466 | 0.21057 | 0.1831 | -0.11902 | -0.15106 | 122.7905 | 122.6212 | 0.13733 | 122.9141 | 122.8958 | 0.27466 | -0.041199 | 122.6715 | 122.6395 | 0.032043 | 122.9004 | 122.7631 | 0.1236 | 0.004577 | 123.1064 | 122.9279 | 122.85 | -0.3479 | 123.0011 | 122.9736 | 122.9324 | -0.32959
3094.5625 | 123.0469 | -122.8592 | 0.20142 | 0.014648 | 0.032578 | 0.0033752 | 0.0051183 | -0.0090384 | 0.0022152 | -0.0065155 | -0.042954 | -0.0087093 | -0.0068936 | -0.0011216 | 0.0085941 | -0.015503 | 0.018311 | 0.022888 | -0.027466 | 0 | 0.26093 | -0.059509 | -0.21973 | 0.013733 | 0.022888 | -0.10529 | 0.19684 | 0.17395 | -0.14191 | -0.19226 | 122.7997 | 122.6395 | 0.059509 | 122.8821 | 122.8592 | 0.21973 | -0.18311 | 122.7173 | 122.6669 | -0.004578 | 122.8729 | 122.7539 | 0.086975 | -0.027466 | 123.1201 | 122.8775 | 122.8317 | -0.42114 | 123.056 | 123.0331 | 122.8821 | -0.39368
3096.2656 | 123.1522 | -122.7539 | 0.16479 | -0.26001 | 0.030014 | 0.0055114 | 0.011954 | -0.0079702 | -0.00056178 | -0.0084381 | -0.23369 | -0.010632 | -0.0056118 | -0.0013352 | 0.0028263 | -0.014648 | 0.13733 | 0.13275 | 0.10071 | 0.14191 | 0.39825 | 0.064087 | -0.086975 | 0.10071 | 0.15106 | 0.018311 | 0.30212 | 0.24261 | -0.068665 | -0.11902 | 122.818 | 122.6669 | 0.23346 | 122.8867 | 122.8958 | 0.22888 | -0.027466 | 122.6852 | 122.6349 | 0.13733 | 122.8546 | 122.7722 | 0.13733 | 0.07782 | 123.1522 | 122.8912 | 122.8546 | -0.25177 | 123.056 | 122.9965 | 122.905 | -0.28381
3098.0156 | 123.0515 | -122.8455 | 0.18768 | -0.00061023 | 0.028732 | 0.0042298 | 0.0070409 | -0.0077566 | 0.005206 | -0.0075837 | -0.0048066 | -0.010205 | -0.006039 | 0.00058739 | 0.0073123 | -0.014007 | 0.068665 | 0.050354 | -0.018311 | 0.032043 | 0.27924 | -0.036621 | -0.19684 | 0.004578 | 0.041199 | -0.091553 | 0.18768 | 0.19226 | -0.15564 | -0.19684 | 122.8088 | 122.6486 | 0.091553 | 122.8958 | 122.8775 | 0.22888 | -0.11902 | 122.6898 | 122.6486 | 0 | 122.85 | 122.7539 | 0.10529 | 0.004578 | 123.1247 | 122.9141 | 122.8271 | -0.38452 | 123.0331 | 123.0377 | 122.8867 | -0.38452
3099.7656 | 123.0835 | -122.818 | 0.20142 | 0.090942 | 0.030655 | 0.0040162 | 0.0051183 | -0.0079702 | 0.0013608 | -0.0043793 | 0.071487 | -0.0089229 | -0.0068936 | -0.0017624 | 0.0053897 | -0.01358 | 0 | -0.013733 | -0.050354 | -0.018311 | 0.25177 | -0.07782 | -0.23346 | 0.018311 | 0.036621 | -0.059509 | 0.21057 | 0.16479 | -0.16479 | -0.1831 | 122.7402 | 122.5845 | 0.050354 | 122.8043 | 122.7997 | 0.21515 | -0.20142 | 122.6532 | 122.6349 | 0.009155 | 122.8363 | 122.7585 | 0.1236 | -0.036621 | 123.0698 | 122.818 | 122.7676 | -0.43488 | 123.0286 | 122.9828 | 122.8546 | -0.38452
3101.5312 | 123.0881 | -122.8134 | 0.1831 | 0.17487 | 0.030869 | 0.0050842 | 0.0029821 | -0.005834 | -0.00034818 | -0.0056611 | 0.19356 | -0.011059 | -0.007748 | 0.00016019 | 0.0062441 | -0.013794 | 0.032043 | 0.036621 | 0.004578 | 0.027466 | 0.21515 | -0.036621 | -0.22888 | 0.09613 | 0.12817 | 0.032043 | 0.14648 | 0.13733 | -0.11444 | -0.16022 | 122.7768 | 122.5845 | 0.032044 | 122.85 | 122.8409 | 0.25635 | -0.15106 | 122.699 | 122.6532 | -0.036621 | 122.9095 | 122.8455 | 0.19226 | -0.045776 | 123.0286 | 122.8455 | 122.818 | -0.41199 | 122.9599 | 122.9507 | 122.9416 | -0.34332
3103.2188 | 123.1293 | -122.7905 | 0.16022 | -0.19897 | 0.026169 | 0.007434 | 0.0057593 | -0.0069022 | -0.0063296 | -0.0090791 | -0.14214 | -0.011059 | -0.0081754 | -0.0024032 | 0.0034671 | -0.015716 | 0.20599 | 0.27924 | 0.21973 | 0.21057 | 0.33875 | 0.09613 | -0.050354 | 0.21515 | 0.33417 | 0.19226 | 0.25635 | 0.24261 | -0.004578 | -0.054932 | 122.8867 | 122.7402 | 0.17853 | 123.0698 | 123.0011 | 0.26093 | 0.045777 | 122.7859 | 122.7356 | 0.096131 | 123.0057 | 122.9828 | 0.24719 | 0.082398 | 123.1293 | 122.9965 | 123.0103 | -0.21057 | 123.0469 | 123.0331 | 123.1247 | -0.21515
3104.9688 | 123.1476 | -122.7951 | 0.17853 | -0.24475 | 0.027023 | 0.0065796 | 0.0083227 | -0.007543 | 7.902e-05 | -0.0092927 | -0.23369 | -0.010632 | -0.0064664 | -0.0021896 | 0.0028263 | -0.015716 | 0.1236 | 0.14191 | 0.086975 | 0.13275 | 0.39825 | 0.054932 | -0.086975 | 0.10071 | 0.15106 | 0.022888 | 0.30212 | 0.2655 | -0.064087 | -0.10986 | 122.85 | 122.7081 | 0.21973 | 122.937 | 122.9279 | 0.21973 | -0.054932 | 122.731 | 122.6852 | 0.1236 | 122.8958 | 122.818 | 0.13275 | 0.086975 | 123.1934 | 122.9187 | 122.8821 | -0.2655 | 123.0972 | 123.0606 | 122.9462 | -0.28839
3106.7344 | 123.1613 | -122.7814 | 0.16022 | -0.11505 | 0.026596 | 0.0057252 | 0.0089635 | -0.0081838 | -0.0059024 | -0.0097199 | -0.050583 | -0.012341 | -0.0064664 | -0.0015488 | 0.00047633 | -0.015075 | 0.20599 | 0.2655 | 0.21973 | 0.19684 | 0.32959 | 0.091553 | -0.086975 | 0.23346 | 0.30212 | 0.1831 | 0.25635 | 0.20599 | -0.022888 | -0.082397 | 122.8729 | 122.6944 | 0.16937 | 123.0469 | 122.9782 | 0.28381 | 0.045777 | 122.7585 | 122.699 | 0.096131 | 123.0148 | 122.9645 | 0.2655 | 0.045777 | 123.111 | 122.9874 | 123.0011 | -0.24719 | 123.0377 | 122.9874 | 123.0835 | -0.24261
3108.5 | 123.0835 | -122.8043 | 0.19684 | 0.1062 | 0.028519 | 0.0061524 | 0.0031957 | -0.0069022 | 0.001788 | -0.0069427 | 0.17067 | -0.011487 | -0.0071072 | 0.00016019 | 0.0053897 | -0.016571 | 0.036621 | 0.004578 | -0.032043 | 0.004578 | 0.27008 | -0.059509 | -0.2243 | 0.064087 | 0.059509 | -0.036621 | 0.16479 | 0.13275 | -0.11444 | -0.19226 | 122.7448 | 122.58 | 0.073243 | 122.8088 | 122.8088 | 0.22888 | -0.16022 | 122.6898 | 122.612 | -0.032043 | 122.8683 | 122.7676 | 0.15564 | -0.064087 | 123.0743 | 122.8409 | 122.7722 | -0.42114 | 122.9691 | 122.937 | 122.8638 | -0.3891
3110.1875 | 123.1064 | -122.8134 | 0.1831 | 0.014648 | 0.02446 | 0.0050842 | 0.0064001 | -0.010106 | -0.0056888 | -0.0069427 | 0.079117 | -0.012341 | -0.0073208 | -0.0015488 | 0.0023989 | -0.013153 | 0.086975 | 0.13733 | 0.1236 | 0.12817 | 0.32501 | 0.050354 | -0.13275 | 0.13275 | 0.19684 | 0.10529 | 0.2243 | 0.20142 | -0.054932 | -0.10529 | 122.8638 | 122.6807 | 0.14191 | 122.9507 | 122.9416 | 0.26093 | -0.09613 | 122.7585 | 122.7081 | 0.041199 | 122.9462 | 122.9187 | 0.21057 | 0.018311 | 123.1384 | 122.9004 | 122.937 | -0.31586 | 123.0377 | 123.0148 | 123.0103 | -0.28839
3111.9531 | 123.1567 | -122.7905 | 0.16479 | -0.10742 | 0.030441 | 0.0035888 | 0.0059729 | -0.0066884 | 0.0049924 | -0.0067291 | -0.14214 | -0.010418 | -0.0062528 | -0.0030442 | 0.0070987 | -0.014862 | 0.13275 | 0.10529 | 0.073242 | 0.10071 | 0.32501 | 0.009155 | -0.15564 | 0.11902 | 0.13733 | -0.004578 | 0.21515 | 0.17853 | -0.09613 | -0.15564 | 122.7997 | 122.6349 | 0.16022 | 122.8958 | 122.8912 | 0.25635 | -0.032044 | 122.6944 | 122.6349 | 0.050354 | 122.9095 | 122.7859 | 0.15106 | 0.013733 | 123.1155 | 122.9233 | 122.8638 | -0.32044 | 123.0057 | 122.9691 | 122.9279 | -0.32044
3113.7188 | 123.1293 | -122.7997 | 0.16937 | -0.16846 | 0.028946 | 0.006366 | 0.0081091 | -0.007543 | -0.0041934 | -0.0073701 | -0.14977 | -0.0117 | -0.0045438 | -0.0030442 | 0.0026125 | -0.014435 | 0.21057 | 0.27466 | 0.2243 | 0.21973 | 0.34332 | 0.082397 | -0.068665 | 0.20142 | 0.28381 | 0.14191 | 0.24261 | 0.21973 | -0.018311 | -0.073242 | 122.8821 | 122.731 | 0.17395 | 123.0743 | 123.0194 | 0.28839 | 0.041198 | 122.7814 | 122.7264 | 0.073242 | 123.0011 | 122.9416 | 0.21515 | 0.050354 | 123.143 | 123.0103 | 123.024 | -0.23804 | 123.0423 | 123.0194 | 123.0835 | -0.24261
3115.4219 | 123.1567 | -122.7905 | 0.16479 | -0.069275 | 0.024674 | 0.0087158 | 0.0061865 | -0.010106 | -0.005048 | -0.010147 | -0.073471 | -0.013836 | -0.0043302 | -0.0038986 | 0.0026125 | -0.014007 | 0.16479 | 0.21057 | 0.17395 | 0.1831 | 0.33417 | 0.073242 | -0.09613 | 0.21973 | 0.29297 | 0.17853 | 0.24719 | 0.21973 | -0.013733 | -0.073242 | 122.8638 | 122.6944 | 0.16937 | 123.0011 | 122.9736 | 0.27924 | 0 | 122.7768 | 122.7173 | 0.082397 | 123.0103 | 122.9691 | 0.25177 | 0.054932 | 123.1247 | 122.9553 | 122.9645 | -0.26092 | 123.0377 | 123.0103 | 123.0835 | -0.23804
3117.1875 | 123.0469 | -122.8363 | 0.20599 | 0.060425 | 0.0298 | 0.0052978 | 0.0049047 | -0.0066884 | 0.0043514 | -0.0069427 | 0.063858 | -0.0089229 | -0.0019802 | 0.00080099 | 0.0068851 | -0.016784 | 0.027466 | -0.045776 | -0.07782 | -0.009155 | 0.27008 | -0.059509 | -0.23346 | 0.027466 | -0.009155 | -0.10529 | 0.21515 | 0.16022 | -0.15564 | -0.20599 | 122.7768 | 122.6028 | 0.064087 | 122.7905 | 122.8271 | 0.2243 | -0.17853 | 122.6807 | 122.6303 | 0.009155 | 122.8638 | 122.731 | 0.10071 | -0.045777 | 123.1064 | 122.8638 | 122.7585 | -0.43945 | 123.0515 | 122.9965 | 122.8271 | -0.41199
3118.9531 | 123.0927 | -122.8271 | 0.20142 | 0.21301 | 0.030869 | 0.0055114 | 0.0042639 | -0.0079702 | 0.001788 | -0.0052337 | 0.12489 | -0.0089229 | -0.0075344 | -0.0011216 | 0.0066715 | -0.014862 | 0.059509 | 0.032043 | 0 | 0.009155 | 0.21515 | -0.068665 | -0.23346 | 0.11902 | 0.13733 | 0.004578 | 0.15564 | 0.13733 | -0.10986 | -0.16022 | 122.7585 | 122.5937 | 0.013733 | 122.8592 | 122.8363 | 0.24261 | -0.14191 | 122.7173 | 122.6669 | -0.045776 | 122.9462 | 122.8317 | 0.16479 | -0.064087 | 123.0423 | 122.8867 | 122.8271 | -0.43488 | 122.9828 | 122.9645 | 122.9645 | -0.36163
3120.7031 | 123.0469 | -122.8455 | 0.21057 | 0.1062 | 0.025955 | 0.0061524 | 0.0051183 | -0.011388 | -0.0046206 | -0.0065155 | 0.14015 | -0.012982 | -0.0088162 | -0.00069421 | 0.0030399 | -0.013366 | 0.11902 | 0.13275 | 0.11444 | 0.082397 | 0.24261 | 0.004578 | -0.14648 | 0.13275 | 0.16937 | 0.07782 | 0.21515 | 0.1831 | -0.064087 | -0.11444 | 122.85 | 122.699 | 0.032044 | 122.9782 | 122.9279 | 0.22888 | -0.091552 | 122.7814 | 122.731 | 0.004578 | 122.9782 | 122.9233 | 0.19226 | -0.027466 | 123.0881 | 122.9645 | 122.9599 | -0.35706 | 123.0606 | 123.0286 | 123.0148 | -0.32501
3122.4688 | 123.1705 | -122.7951 | 0.17853 | -0.2066 | 0.0298 | 0.0065796 | 0.0061865 | -0.0077566 | 0.0032834 | -0.0065155 | -0.2108 | -0.013196 | -0.0051846 | -0.0021896 | 0.0060305 | -0.014435 | 0.15564 | 0.12817 | 0.091553 | 0.11902 | 0.37079 | 0.027466 | -0.13275 | 0.091553 | 0.16022 | 0 | 0.24719 | 0.21057 | -0.10529 | -0.15106 | 122.8226 | 122.6624 | 0.19226 | 122.9233 | 122.9141 | 0.25177 | -0.022888 | 122.6898 | 122.644 | 0.068664 | 122.8867 | 122.7951 | 0.15106 | 0.032043 | 123.1659 | 122.9507 | 122.8867 | -0.31128 | 123.0423 | 123.0057 | 122.9553 | -0.32959
3124.1719 | 123.1979 | -122.7768 | 0.17395 | -0.19135 | 0.030441 | 0.004657 | 0.0051183 | -0.0062612 | 0.0015744 | -0.0065155 | -0.22606 | -0.0099911 | -0.0056118 | -0.0017624 | 0.0060305 | -0.016998 | 0.13733 | 0.13275 | 0.086975 | 0.13733 | 0.35248 | 0.032043 | -0.14648 | 0.09613 | 0.13275 | -0.009155 | 0.27466 | 0.23346 | -0.086975 | -0.13733 | 122.8088 | 122.6303 | 0.17853 | 122.9095 | 122.9141 | 0.28381 | -0.036621 | 122.6898 | 122.6395 | 0.10071 | 122.8729 | 122.7676 | 0.12817 | 0.059509 | 123.1293 | 122.9141 | 122.8638 | -0.32043 | 123.0515 | 123.0103 | 122.9095 | -0.31128
3125.9375 | 123.056 | -122.8455 | 0.19226 | 0.090942 | 0.032578 | 0.0048706 | 0.0064001 | -0.0083974 | 0.0030698 | -0.0050201 | 0.094375 | -0.012341 | -0.0043302 | -0.00090781 | 0.0064577 | -0.016143 | 0.009155 | -0.032043 | -0.059509 | -0.004578 | 0.25635 | -0.050354 | -0.24261 | 0.013733 | 0.013733 | -0.091553 | 0.19684 | 0.16479 | -0.16022 | -0.19684 | 122.7951 | 122.6028 | 0.064087 | 122.8134 | 122.8409 | 0.23804 | -0.18311 | 122.6852 | 122.6486 | 0.004577 | 122.8592 | 122.7539 | 0.10529 | -0.027466 | 123.1018 | 122.8546 | 122.7859 | -0.43488 | 123.0423 | 123.0103 | 122.8592 | -0.3891
3127.7031 | 123.0423 | -122.85 | 0.21515 | 0.029907 | 0.031082 | 0.0038024 | 0.0042639 | -0.0081838 | 0.0020016 | -0.0058747 | 0.010452 | -0.0099911 | -0.0081754 | -0.0015488 | 0.0073123 | -0.015503 | 0.004578 | 0 | -0.036621 | 0.004578 | 0.25177 | -0.059509 | -0.21057 | 0 | 0.027466 | -0.10986 | 0.21057 | 0.17395 | -0.14648 | -0.20142 | 122.7905 | 122.6395 | 0.036621 | 122.85 | 122.8546 | 0.21515 | -0.21057 | 122.7036 | 122.6486 | -0.004578 | 122.85 | 122.7402 | 0.091553 | -0.041199 | 123.1018 | 122.8546 | 122.8134 | -0.42572 | 123.0606 | 123.024 | 122.8775 | -0.41657
3129.4062 | 123.0698 | -122.8363 | 0.20599 | 0.083313 | 0.031296 | 0.0055114 | 0.0061865 | -0.0079702 | 0.001788 | -0.0073701 | 0.086746 | -0.0095639 | -0.006039 | -0.001976 | 0.0068851 | -0.014221 | -0.009155 | -0.013733 | -0.045776 | -0.009155 | 0.27466 | -0.082397 | -0.2243 | -0.004578 | 0.004578 | -0.086975 | 0.21515 | 0.16479 | -0.14648 | -0.21057 | 122.7539 | 122.612 | 0.068664 | 122.8226 | 122.8271 | 0.21515 | -0.21515 | 122.6898 | 122.6257 | 0.009155 | 122.8317 | 122.7493 | 0.1236 | -0.041199 | 123.111 | 122.8271 | 122.7905 | -0.4303 | 123.0515 | 123.0011 | 122.8409 | -0.41657
3131.1719 | 123.1705 | -122.8088 | 0.16937 | -0.22186 | 0.0298 | 0.0040162 | 0.0034093 | -0.0088248 | -0.0014164 | -0.0060883 | -0.16502 | -0.011914 | -0.004971 | -0.0013352 | 0.0066715 | -0.013794 | 0.10986 | 0.11902 | 0.082397 | 0.10986 | 0.36163 | 0.013733 | -0.13733 | 0.073242 | 0.14648 | 0.009155 | 0.24261 | 0.21973 | -0.10529 | -0.15564 | 122.8226 | 122.6715 | 0.19226 | 122.9279 | 122.9187 | 0.24719 | -0.05951 | 122.7036 | 122.6532 | 0.073242 | 122.8821 | 122.818 | 0.16479 | 0.050354 | 123.1705 | 122.9187 | 122.8912 | -0.3067 | 123.0515 | 123.0286 | 122.9553 | -0.32501
3132.9375 | 123.056 | -122.8226 | 0.21973 | 0.045166 | 0.025101 | 0.008075 | 0.0057593 | -0.0098928 | -0.0069706 | -0.0092927 | 0.12489 | -0.011059 | -0.0075344 | -0.0021896 | 0.0036807 | -0.012726 | 0.086975 | 0.13275 | 0.10986 | 0.086975 | 0.28381 | 0.027466 | -0.13733 | 0.12817 | 0.19226 | 0.091553 | 0.20142 | 0.17395 | -0.082397 | -0.10986 | 122.85 | 122.6852 | 0.064086 | 122.9553 | 122.9095 | 0.2243 | -0.13275 | 122.7402 | 122.7127 | -0.018311 | 122.9507 | 122.9141 | 0.20142 | -0.045777 | 123.1064 | 122.9095 | 122.9324 | -0.35706 | 123.024 | 122.9965 | 123.0148 | -0.32959
3134.6875 | 123.0606 | -122.8729 | 0.21515 | -0.061646 | 0.030228 | 0.0038024 | 0.0053321 | -0.0045522 | 0.0022152 | -0.0060883 | -0.073471 | -0.010632 | -0.0071072 | 0.00037379 | 0.0058169 | -0.016998 | 0.1236 | 0.082397 | 0.032043 | 0.073242 | 0.29297 | -0.013733 | -0.19226 | 0.045776 | 0.082397 | -0.041199 | 0.23346 | 0.17395 | -0.14191 | -0.16479 | 122.8592 | 122.6807 | 0.07782 | 122.9553 | 122.9462 | 0.2655 | -0.091553 | 122.731 | 122.7081 | 0.01831 | 122.9187 | 122.8317 | 0.1236 | -0.041199 | 123.1659 | 122.9965 | 122.905 | -0.40741 | 123.1064 | 123.0469 | 122.9553 | -0.37994
3136.4531 | 123.1659 | -122.7722 | 0.16479 | -0.14557 | 0.025955 | 0.0055114 | 0.0096045 | -0.0064748 | -0.007825 | -0.0090791 | -0.073471 | -0.015332 | -0.0064664 | -0.0028306 | 0.00090353 | -0.013153 | 0.22888 | 0.23346 | 0.2243 | 0.20142 | 0.32501 | 0.059509 | -0.086975 | 0.21515 | 0.31128 | 0.17853 | 0.26093 | 0.23804 | -0.004578 | -0.059509 | 122.8317 | 122.6852 | 0.16022 | 123.0057 | 122.9736 | 0.28839 | 0.064087 | 122.7676 | 122.7127 | 0.09613 | 122.9874 | 122.9507 | 0.23804 | 0.073242 | 123.0972 | 123.0011 | 122.9965 | -0.25177 | 123.0331 | 123.0103 | 123.0835 | -0.2243
3138.1562 | 123.1476 | -122.7814 | 0.16937 | -0.2066 | 0.030441 | 0.0038024 | 0.0111 | -0.0062612 | -0.0020572 | -0.0090791 | -0.24132 | -0.012127 | -0.0056118 | -0.00090781 | 0.0013309 | -0.014862 | 0.1236 | 0.11902 | 0.10986 | 0.13733 | 0.40283 | 0.041199 | -0.10529 | 0.10986 | 0.16479 | 0.041199 | 0.31128 | 0.2655 | -0.045776 | -0.10529 | 122.8226 | 122.6761 | 0.23346 | 122.9004 | 122.9187 | 0.24262 | -0.045777 | 122.7356 | 122.6761 | 0.14191 | 122.8912 | 122.8226 | 0.14649 | 0.09613 | 123.1842 | 122.905 | 122.8912 | -0.27466 | 123.0927 | 123.0469 | 122.9462 | -0.27466
3139.9062 | 123.0743 | -122.7997 | 0.20599 | 0.037537 | 0.024246 | 0.0059388 | 0.0017005 | -0.0054068 | -0.004407 | -0.0090791 | 0.071487 | -0.014264 | -0.0064664 | -0.00090781 | 0.0045351 | -0.012298 | 0.10986 | 0.13733 | 0.13275 | 0.11444 | 0.30212 | 0.013733 | -0.13733 | 0.11902 | 0.17853 | 0.086975 | 0.22888 | 0.20142 | -0.059509 | -0.10986 | 122.8134 | 122.6624 | 0.09613 | 122.937 | 122.9141 | 0.25177 | -0.096131 | 122.7402 | 122.6898 | 0.022888 | 122.9187 | 122.8867 | 0.19684 | -0.004578 | 123.1018 | 122.9095 | 122.9324 | -0.34332 | 123.0286 | 123.0011 | 122.9782 | -0.31586
3141.6562 | 123.0469 | -122.8134 | 0.20142 | 0.14435 | 0.028732 | 0.0061524 | 0.0040503 | -0.0090384 | 0.00093342 | -0.0077973 | 0.1783 | -0.012982 | -0.004971 | -0.0017624 | 0.0066715 | -0.015075 | 0.11444 | 0.11444 | 0.07782 | 0.082397 | 0.19226 | -0.041199 | -0.1831 | 0.1236 | 0.14191 | 0.027466 | 0.15106 | 0.09613 | -0.12817 | -0.17395 | 122.7722 | 122.6303 | -0.009155 | 122.9279 | 122.8958 | 0.2655 | -0.086975 | 122.6852 | 122.6395 | -0.050354 | 122.937 | 122.8409 | 0.20142 | -0.10529 | 123.0057 | 122.9279 | 122.8912 | -0.38452 | 122.9645 | 122.9095 | 122.9553 | -0.37537
3143.4219 | 123.0881 | -122.818 | 0.1831 | 0.20538 | 0.030869 | 0.0052978 | 0.0074683 | -0.0083974 | 0.00093342 | -0.0073701 | 0.079117 | -0.011273 | -0.0073208 | -0.00026701 | 0.0068851 | -0.016571 | 0.07782 | 0.064087 | 0.027466 | 0.045776 | 0.2243 | -0.041199 | -0.21515 | 0.11902 | 0.13733 | 0.032043 | 0.16479 | 0.12817 | -0.10529 | -0.17395 | 122.7768 | 122.6028 | 0.041199 | 122.8821 | 122.8638 | 0.26093 | -0.10528 | 122.7127 | 122.644 | -0.01831 | 122.937 | 122.85 | 0.20599 | -0.054931 | 123.0423 | 122.8958 | 122.8455 | -0.39825 | 122.9828 | 122.9462 | 122.9553 | -0.35706
3145.1875 | 123.0835 | -122.8317 | 0.19684 | 0.098572 | 0.030014 | 0.0052978 | 0.0053321 | -0.0062612 | 0.0028562 | -0.0056611 | 0.13252 | -0.010846 | -0.0051846 | -0.00069421 | 0.0053897 | -0.015075 | 0.050354 | 0.022888 | -0.027466 | 0.004578 | 0.2655 | -0.073242 | -0.21973 | 0.050354 | 0.041199 | -0.064087 | 0.19684 | 0.14648 | -0.12817 | -0.20142 | 122.7585 | 122.612 | 0.068665 | 122.8546 | 122.8363 | 0.22431 | -0.14648 | 122.7036 | 122.6303 | 0 | 122.8821 | 122.7676 | 0.13733 | -0.050354 | 123.0972 | 122.8821 | 122.8043 | -0.41657 | 123.0286 | 122.9782 | 122.8729 | -0.39825
3146.8906 | 123.1705 | -122.7951 | 0.16479 | -0.11505 | 0.026596 | 0.0042298 | 0.0074683 | -0.0094656 | -0.0054752 | -0.0088653 | -0.027695 | -0.012555 | -0.0041164 | -0.0026168 | 0.0019717 | -0.011657 | 0.20599 | 0.2655 | 0.21057 | 0.1831 | 0.33417 | 0.073242 | -0.073242 | 0.24261 | 0.28839 | 0.17853 | 0.26093 | 0.2243 | -0.018311 | -0.07782 | 122.8683 | 122.7219 | 0.16937 | 123.0606 | 122.9782 | 0.25635 | 0.041199 | 122.7768 | 122.7173 | 0.09613 | 123.0377 | 122.9736 | 0.25635 | 0.059509 | 123.1293 | 123.0011 | 123.0057 | -0.23804 | 123.056 | 123.0194 | 123.0835 | -0.24261
3148.6406 | 123.0377 | -122.8455 | 0.21057 | 0.052795 | 0.030441 | 0.0055114 | 0.0040503 | -0.005834 | 0.0041378 | -0.0090791 | -0.0048066 | -0.010418 | -0.0096706 | -0.0013352 | 0.0081667 | -0.016143 | 0.036621 | -0.036621 | -0.045776 | 0.009155 | 0.2655 | -0.059509 | -0.21515 | 0.004578 | 0.009155 | -0.10071 | 0.20599 | 0.18768 | -0.13733 | -0.20599 | 122.7859 | 122.6303 | 0.054932 | 122.8088 | 122.8546 | 0.2243 | -0.17395 | 122.7081 | 122.6395 | -0.004577 | 122.85 | 122.7448 | 0.10529 | -0.022888 | 123.111 | 122.8821 | 122.7997 | -0.42572 | 123.0515 | 123.0331 | 122.8546 | -0.41657
3150.4062 | 123.0789 | -122.8317 | 0.19226 | 0.11383 | 0.031082 | 0.0033752 | 0.0027685 | -0.010534 | -0.00077538 | -0.0075837 | 0.086746 | -0.0078549 | -0.0073208 | -0.0024032 | 0.0058169 | -0.014862 | 0.054932 | -0.022888 | -0.041199 | 0.004578 | 0.27008 | -0.068665 | -0.21515 | 0.045776 | 0.018311 | -0.059509 | 0.19684 | 0.17395 | -0.1236 | -0.19684 | 122.7631 | 122.6166 | 0.07782 | 122.8088 | 122.8363 | 0.21973 | -0.13733 | 122.7081 | 122.6349 | 0.004577 | 122.8775 | 122.7722 | 0.13733 | -0.018311 | 123.1018 | 122.8867 | 122.7905 | -0.40741 | 123.0286 | 123.0057 | 122.85 | -0.3891
3152.1094 | 123.0972 | -122.8088 | 0.18768 | -0.10742 | 0.033646 | 0.0038024 | 0.0085363 | -0.0064748 | 0.0015744 | -0.0073701 | -0.08873 | -0.010846 | -0.0056118 | -0.0017624 | 0.0058169 | -0.014435 | 0.13733 | 0.09613 | 0.041199 | 0.07782 | 0.29297 | -0.009155 | -0.15564 | 0.09613 | 0.11902 | -0.027466 | 0.21057 | 0.19226 | -0.10529 | -0.16022 | 122.7997 | 122.6532 | 0.10529 | 122.905 | 122.8867 | 0.23346 | -0.050354 | 122.7036 | 122.6486 | 0.022888 | 122.905 | 122.7814 | 0.13275 | 0.004578 | 123.1018 | 122.9462 | 122.85 | -0.34332 | 123.0194 | 123.0011 | 122.9279 | -0.3479
3153.8438 | 123.0789 | -122.8088 | 0.21057 | 0.19012 | 0.031509 | 0.0044434 | 0.0027685 | -0.0088248 | -0.00013458 | -0.0058747 | 0.14778 | -0.0099911 | -0.0043302 | -0.001976 | 0.0051761 | -0.01358 | 0.013733 | -0.004578 | -0.018311 | 0.009155 | 0.2243 | -0.059509 | -0.21973 | 0.086975 | 0.10529 | -0.018311 | 0.16937 | 0.13275 | -0.10986 | -0.18768 | 122.7493 | 122.5891 | 0.013733 | 122.8043 | 122.818 | 0.22888 | -0.19684 | 122.699 | 122.6212 | -0.041198 | 122.8958 | 122.7905 | 0.16937 | -0.07782 | 123.0331 | 122.8226 | 122.7905 | -0.4303 | 122.9782 | 122.9416 | 122.9141 | -0.39825
3155.5938 | 123.1247 | -122.8043 | 0.19226 | -0.076904 | 0.033646 | 0.0042298 | 0.0085363 | -0.0071158 | 0.0026424 | -0.0058747 | -0.11925 | -0.0099911 | -0.0062528 | -0.00026701 | 0.0047489 | -0.01593 | 0.13733 | 0.082397 | 0.054932 | 0.086975 | 0.29297 | -0.004578 | -0.17853 | 0.082397 | 0.12817 | -0.022888 | 0.20599 | 0.17853 | -0.10986 | -0.15564 | 122.7997 | 122.6257 | 0.10071 | 122.8867 | 122.8912 | 0.2655 | -0.054932 | 122.6944 | 122.6486 | 0.013733 | 122.8867 | 122.7814 | 0.13275 | -0.013733 | 123.0972 | 122.9416 | 122.8592 | -0.37079 | 123.0103 | 122.9828 | 122.9324 | -0.3479
3157.3438 | 123.0835 | -122.8546 | 0.20599 | 0.12146 | 0.031296 | 0.0061524 | 0.0029821 | -0.0077566 | 0.0015744 | -0.0069427 | 0.12489 | -0.0093503 | -0.004971 | 0.00037379 | 0.0056033 | -0.015289 | 0 | -0.022888 | -0.064087 | -0.004578 | 0.26093 | -0.068665 | -0.24719 | 0.022888 | 0.036621 | -0.073242 | 0.20142 | 0.16937 | -0.14191 | -0.19684 | 122.7859 | 122.6074 | 0.054931 | 122.8317 | 122.85 | 0.24261 | -0.20599 | 122.7127 | 122.6578 | -0.004578 | 122.8775 | 122.7814 | 0.1236 | -0.036621 | 123.1155 | 122.8546 | 122.7905 | -0.45319 | 123.056 | 123.024 | 122.8912 | -0.40283
3159.0938 | 123.0469 | -122.8134 | 0.19226 | 0.11383 | 0.028092 | 0.0048706 | 0.0064001 | -0.0090384 | -0.006116 | -0.0082245 | 0.16304 | -0.012768 | -0.0047574 | -0.0015488 | -0.00037807 | -0.014435 | 0.082397 | 0.1236 | 0.10529 | 0.07782 | 0.23804 | -0.027466 | -0.16022 | 0.11902 | 0.15564 | 0.073242 | 0.20142 | 0.17853 | -0.091553 | -0.1236 | 122.7859 | 122.6532 | 0.045776 | 122.937 | 122.8912 | 0.23804 | -0.10986 | 122.7219 | 122.6898 | 0.009155 | 122.9324 | 122.8867 | 0.19684 | -0.013733 | 123.0515 | 122.8958 | 122.9187 | -0.35248 | 123.0148 | 122.9919 | 122.9691 | -0.31586
3160.8438 | 123.1476 | -122.8043 | 0.17395 | -0.076904 | 0.031296 | 0.0040162 | 0.0061865 | -0.0060476 | 0.0030698 | -0.0054475 | -0.14214 | -0.010846 | -0.0036892 | 0.00058739 | 0.0081667 | -0.015716 | 0.14191 | 0.10071 | 0.050354 | 0.082397 | 0.31128 | 0.004578 | -0.17853 | 0.09613 | 0.11902 | -0.009155 | 0.21057 | 0.19226 | -0.11444 | -0.16479 | 122.8088 | 122.6257 | 0.13733 | 122.905 | 122.8867 | 0.26092 | -0.032043 | 122.6898 | 122.6395 | 0.036621 | 122.9004 | 122.7951 | 0.15564 | 0.018311 | 123.1155 | 122.9462 | 122.8546 | -0.35248 | 123.0148 | 122.9965 | 122.9233 | -0.33874
3162.5469 | 123.0927 | -122.818 | 0.20142 | 0.12146 | 0.030441 | 0.0050842 | 0.0057593 | -0.0051932 | 0.0030698 | -0.0043793 | 0.16304 | -0.0117 | -0.0056118 | -0.0024032 | 0.0073123 | -0.013153 | 0.041199 | -0.009155 | -0.036621 | -0.004578 | 0.24261 | -0.054932 | -0.22888 | 0.059509 | 0.054932 | -0.041199 | 0.16937 | 0.14191 | -0.12817 | -0.19226 | 122.7631 | 122.5891 | 0.041199 | 122.8088 | 122.8134 | 0.2243 | -0.16022 | 122.6898 | 122.6257 | -0.032043 | 122.8775 | 122.7768 | 0.15106 | -0.059509 | 123.0606 | 122.8592 | 122.7814 | -0.4303 | 122.9874 | 122.9599 | 122.8729 | -0.39368
3164.2969 | 123.0743 | -122.8455 | 0.19684 | -0.069275 | 0.031723 | 0.0033752 | 0.0046911 | -0.0079702 | 7.902e-05 | -0.0069427 | -0.08873 | -0.0097775 | -0.0047574 | -5.3406e-05 | 0.0070987 | -0.015503 | 0.10529 | 0.082397 | 0.027466 | 0.091553 | 0.29755 | -0.022888 | -0.17853 | 0.064087 | 0.082397 | -0.054932 | 0.21973 | 0.18768 | -0.13275 | -0.16022 | 122.8226 | 122.6669 | 0.10071 | 122.9279 | 122.937 | 0.27008 | -0.091552 | 122.7127 | 122.6852 | 0.022889 | 122.9095 | 122.7905 | 0.10528 | -0.009155 | 123.143 | 122.9507 | 122.8729 | -0.37537 | 123.0652 | 123.0331 | 122.9279 | -0.35706
3166.0469 | 123.0423 | -122.8317 | 0.21057 | 0.0070193 | 0.033859 | 0.004657 | 0.0074683 | -0.008611 | -0.00013458 | -0.0054475 | 0.048599 | -0.0093503 | -0.0068936 | -0.0015488 | 0.0064577 | -0.015289 | 0.027466 | 0.013733 | -0.027466 | 0.018311 | 0.26093 | -0.059509 | -0.2243 | -0.004578 | 0.045776 | -0.10071 | 0.18768 | 0.16022 | -0.14191 | -0.20599 | 122.7722 | 122.6074 | 0.050354 | 122.8455 | 122.85 | 0.24261 | -0.18311 | 122.6898 | 122.6257 | -0.022888 | 122.8271 | 122.731 | 0.10529 | -0.050354 | 123.0927 | 122.8592 | 122.8043 | -0.43488 | 123.0194 | 122.9919 | 122.8775 | -0.41657
3167.75 | 123.1842 | -122.7814 | 0.18768 | -0.25238 | 0.028732 | 0.0044434 | 0.0091773 | -0.0073294 | -0.0020572 | -0.0097199 | -0.18791 | -0.011273 | -0.0045438 | 0.00016019 | 0.0019717 | -0.014648 | 0.10986 | 0.12817 | 0.073242 | 0.12817 | 0.40741 | 0.050354 | -0.10071 | 0.068665 | 0.13275 | 0.032043 | 0.28839 | 0.27924 | -0.086975 | -0.1236 | 122.8317 | 122.6807 | 0.21973 | 122.9095 | 122.9095 | 0.22888 | -0.07782 | 122.6944 | 122.6578 | 0.10071 | 122.85 | 122.8134 | 0.15564 | 0.091553 | 123.1888 | 122.8912 | 122.8546 | -0.28839 | 123.0698 | 123.0606 | 122.9141 | -0.31128
3169.5 | 123.1567 | -122.8043 | 0.16479 | -0.19897 | 0.025101 | 0.0067932 | 0.010245 | -0.0090384 | -0.008466 | -0.0099335 | -0.10399 | -0.015118 | -0.0081754 | -0.0013352 | 0.0023989 | -0.015289 | 0.21515 | 0.2655 | 0.24261 | 0.21973 | 0.37079 | 0.09613 | -0.07782 | 0.21057 | 0.29755 | 0.17395 | 0.27924 | 0.25177 | 0 | -0.07782 | 122.9004 | 122.7264 | 0.20599 | 123.0698 | 123.024 | 0.29755 | 0.050354 | 122.8043 | 122.7264 | 0.11444 | 123.0148 | 122.9782 | 0.25177 | 0.086975 | 123.175 | 123.0194 | 123.0469 | -0.24261 | 123.0835 | 123.056 | 123.1018 | -0.24261
3171.25 | 123.1476 | -122.7951 | 0.15106 | -0.17609 | 0.028092 | 0.0067932 | 0.0068273 | -0.010106 | -0.0059024 | -0.0086517 | -0.14977 | -0.013836 | -0.0064664 | -0.0021896 | -0.00059167 | -0.015075 | 0.21973 | 0.26093 | 0.21973 | 0.20599 | 0.33875 | 0.082397 | -0.086975 | 0.21057 | 0.31128 | 0.1831 | 0.27466 | 0.22888 | -0.013733 | -0.059509 | 122.8775 | 122.7081 | 0.18768 | 123.056 | 123.0011 | 0.29297 | 0.068665 | 122.7814 | 122.7356 | 0.1236 | 123.0057 | 122.9782 | 0.24261 | 0.07782 | 123.1339 | 123.0148 | 123.0148 | -0.23804 | 123.0698 | 123.024 | 123.1064 | -0.21057
3172.9531 | 123.1796 | -122.7997 | 0.16479 | -0.16846 | 0.031509 | 0.0059388 | 0.0068273 | -0.0071158 | 0.003497 | -0.0075837 | -0.2108 | -0.0091367 | -0.0047574 | -0.00048061 | 0.0034671 | -0.017212 | 0.13275 | 0.10071 | 0.045776 | 0.11902 | 0.3479 | 0.013733 | -0.15564 | 0.10071 | 0.14648 | 0.004578 | 0.25177 | 0.20599 | -0.10986 | -0.15564 | 122.8134 | 122.644 | 0.1831 | 122.9004 | 122.9187 | 0.27466 | -0.032044 | 122.6898 | 122.644 | 0.086975 | 122.9004 | 122.8043 | 0.16022 | 0.041199 | 123.1476 | 122.9324 | 122.8455 | -0.32044 | 123.0515 | 123.0057 | 122.9462 | -0.32044
3174.7031 | 123.1338 | -122.7722 | 0.16937 | -0.19897 | 0.027237 | 0.0059388 | 0.0096045 | -0.0079702 | -0.0046206 | -0.0092927 | -0.13451 | -0.011914 | -0.007748 | -0.0011216 | 0.0019717 | -0.015075 | 0.21973 | 0.27924 | 0.21973 | 0.21515 | 0.35248 | 0.086975 | -0.073242 | 0.20599 | 0.27924 | 0.16937 | 0.25177 | 0.23346 | -0.018311 | -0.068665 | 122.8592 | 122.699 | 0.18311 | 123.0515 | 122.9874 | 0.28839 | 0.050354 | 122.7539 | 122.7036 | 0.082397 | 122.9782 | 122.9416 | 0.23804 | 0.064086 | 123.1247 | 122.9919 | 122.9919 | -0.24261 | 123.024 | 123.0057 | 123.0515 | -0.23804
3176.4688 | 123.0515 | -122.8683 | 0.21515 | 0.060425 | 0.031723 | 0.0067932 | 0.0040503 | -0.007543 | 0.00093342 | -0.0058747 | -0.012436 | -0.011273 | -0.0068936 | -0.0015488 | 0.0081667 | -0.016571 | 0.027466 | -0.013733 | -0.054932 | 0.013733 | 0.2655 | -0.054932 | -0.22888 | -0.018311 | 0.009155 | -0.11444 | 0.21973 | 0.16479 | -0.15564 | -0.20142 | 122.8134 | 122.6395 | 0.050354 | 122.8546 | 122.8821 | 0.24261 | -0.18768 | 122.7127 | 122.6669 | 0.004578 | 122.85 | 122.7539 | 0.086975 | -0.050354 | 123.1338 | 122.8958 | 122.8134 | -0.44403 | 123.0881 | 123.0331 | 122.8775 | -0.41657
3178.2344 | 123.0515 | -122.8455 | 0.20142 | 0.037537 | 0.03215 | 0.0055114 | 0.0049047 | -0.007543 | 0.0054196 | -0.0052337 | 0.03334 | -0.0117 | -0.0051846 | -0.0024032 | 0.0079531 | -0.014007 | 0.018311 | -0.013733 | -0.059509 | -0.009155 | 0.28381 | -0.059509 | -0.21973 | -0.009155 | 0 | -0.1236 | 0.21515 | 0.17395 | -0.13733 | -0.21973 | 122.7859 | 122.6257 | 0.082397 | 122.8317 | 122.8363 | 0.21057 | -0.18311 | 122.7081 | 122.6257 | 0.013733 | 122.8363 | 122.7219 | 0.096131 | -0.027466 | 123.1293 | 122.8638 | 122.7859 | -0.42114 | 123.0606 | 123.0194 | 122.8455 | -0.42114
3180 | 123.0331 | -122.8455 | 0.20142 | 0.1825 | 0.026596 | 0.0042298 | 0.0053321 | -0.0047658 | -0.0035526 | -0.0082245 | 0.19356 | -0.013836 | -0.0088162 | -0.0013352 | 0.0056033 | -0.014221 | 0.086975 | 0.11444 | 0.068665 | 0.068665 | 0.18768 | -0.059509 | -0.1831 | 0.13733 | 0.17395 | 0.045776 | 0.13275 | 0.13275 | -0.1236 | -0.16022 | 122.7859 | 122.6624 | -0.013733 | 122.9599 | 122.9141 | 0.25177 | -0.11444 | 122.7219 | 122.6852 | -0.068665 | 122.9828 | 122.8912 | 0.20599 | -0.068665 | 123.0331 | 122.9324 | 122.9141 | -0.38452 | 122.9782 | 122.9782 | 123.0194 | -0.36163
3181.7031 | 123.175 | -122.7997 | 0.16937 | -0.14557 | 0.032791 | 0.0065796 | 0.0064001 | -0.0069022 | 0.0013608 | -0.0069427 | -0.14214 | -0.010418 | -0.0047574 | -0.0011216 | 0.0047489 | -0.015716 | 0.13275 | 0.086975 | 0.07782 | 0.12817 | 0.32959 | -0.013733 | -0.17395 | 0.11444 | 0.14648 | -0.009155 | 0.24261 | 0.21057 | -0.086975 | -0.15106 | 122.7859 | 122.6257 | 0.16022 | 122.8867 | 122.9279 | 0.30212 | -0.036622 | 122.7127 | 122.6486 | 0.073242 | 122.9141 | 122.7905 | 0.14191 | 0.041198 | 123.1293 | 122.9324 | 122.8775 | -0.34332 | 123.0423 | 123.0103 | 122.9462 | -0.32044
3183.4531 | 123.175 | -122.7997 | 0.16937 | -0.18372 | 0.029587 | 0.0038024 | 0.0085363 | -0.0069022 | 0.00050622 | -0.0067291 | -0.17265 | -0.011914 | -0.0058254 | -0.00069421 | 0.0049625 | -0.014221 | 0.13733 | 0.086975 | 0.064087 | 0.10071 | 0.34332 | 0 | -0.14648 | 0.09613 | 0.14648 | 0.009155 | 0.23804 | 0.21515 | -0.086975 | -0.15564 | 122.7997 | 122.6532 | 0.17395 | 122.8867 | 122.9004 | 0.24719 | -0.032044 | 122.7127 | 122.644 | 0.068664 | 122.8958 | 122.8088 | 0.16479 | 0.045776 | 123.143 | 122.937 | 122.8638 | -0.31586 | 123.0377 | 123.0148 | 122.9462 | -0.32501
3185.2031 | 123.0606 | -122.8363 | 0.21515 | 0.037537 | 0.035141 | 0.0014526 | 0.0087499 | -0.0060476 | 0.0013608 | -0.0058747 | 0.025711 | -0.011487 | -0.0047574 | 0.0022964 | 0.0060305 | -0.015075 | 0.009155 | -0.022888 | -0.032043 | 0.018311 | 0.27008 | -0.059509 | -0.2243 | -0.009155 | 0.036621 | -0.10529 | 0.21515 | 0.16937 | -0.15564 | -0.19684 | 122.7768 | 122.612 | 0.054932 | 122.8134 | 122.8546 | 0.24261 | -0.20599 | 122.6807 | 122.6395 | 0 | 122.8271 | 122.731 | 0.091552 | -0.045776 | 123.1064 | 122.8455 | 122.8043 | -0.43945 | 123.0515 | 123.0057 | 122.8729 | -0.41199
3186.9062 | 123.1201 | -122.7951 | 0.15564 | -0.19135 | 0.02916 | 0.0070068 | 0.010032 | -0.008611 | -0.0080386 | -0.0095063 | -0.096359 | -0.01405 | -0.0062528 | -0.0011216 | 0.0026125 | -0.014862 | 0.18768 | 0.27924 | 0.23804 | 0.20142 | 0.37079 | 0.073242 | -0.064087 | 0.19684 | 0.30212 | 0.15106 | 0.25177 | 0.2243 | -0.013733 | -0.073242 | 122.8683 | 122.731 | 0.21515 | 123.0743 | 122.9965 | 0.2655 | 0.032043 | 122.7814 | 122.7219 | 0.09613 | 122.9919 | 122.9462 | 0.2243 | 0.068664 | 123.1659 | 122.9828 | 123.0331 | -0.21973 | 123.0469 | 123.0194 | 123.0972 | -0.22888
3188.6562 | 123.056 | -122.8363 | 0.19226 | 0.17487 | 0.031082 | 0.0067932 | 0.0044775 | -0.0062612 | -0.0029118 | -0.0065155 | 0.2317 | -0.010846 | -0.0053982 | -0.0017624 | 0.0038943 | -0.014007 | 0.086975 | 0.09613 | 0.064087 | 0.073242 | 0.21057 | -0.045776 | -0.18768 | 0.10986 | 0.15106 | 0.050354 | 0.12817 | 0.11444 | -0.1236 | -0.16937 | 122.7905 | 122.6486 | 0.01831 | 122.9324 | 122.9095 | 0.26092 | -0.10529 | 122.7127 | 122.6669 | -0.064087 | 122.9462 | 122.8867 | 0.21973 | -0.07782 | 123.0469 | 122.9233 | 122.9004 | -0.37994 | 122.9645 | 122.9507 | 122.9874 | -0.36163
3190.3594 | 123.0423 | -122.8271 | 0.21973 | -0.038757 | 0.031509 | 0.004657 | 0.0040503 | -0.0096792 | 0.0030698 | -0.0069427 | -0.058212 | -0.010846 | -0.006039 | -0.0015488 | 0.0077395 | -0.015503 | 0.10071 | 0.036621 | -0.004578 | 0.036621 | 0.3067 | -0.036621 | -0.20599 | 0.032043 | 0.032043 | -0.086975 | 0.20599 | 0.19226 | -0.14648 | -0.2243 | 122.7905 | 122.6212 | 0.086975 | 122.8638 | 122.8638 | 0.24262 | -0.11902 | 122.6807 | 122.6028 | -0.013733 | 122.8592 | 122.7402 | 0.13733 | -0.027466 | 123.1338 | 122.9279 | 122.8226 | -0.42572 | 123.0331 | 123.0194 | 122.8592 | -0.44403
3192.125 | 123.143 | -122.8043 | 0.18768 | -0.25238 | 0.030014 | 0.0087158 | 0.0091773 | -0.0077566 | -0.0031254 | -0.0084381 | -0.16502 | -0.012768 | -0.0047574 | -0.0013352 | 4.9132e-05 | -0.014862 | 0.1831 | 0.18768 | 0.15564 | 0.17853 | 0.37994 | 0.064087 | -0.09613 | 0.1236 | 0.17395 | 0.050354 | 0.31128 | 0.28381 | -0.054932 | -0.091553 | 122.8683 | 122.7081 | 0.19226 | 122.9919 | 122.9828 | 0.27466 | -0.004578 | 122.7493 | 122.7127 | 0.1236 | 122.9279 | 122.8546 | 0.14191 | 0.09613 | 123.1842 | 122.9874 | 122.9599 | -0.28381 | 123.1155 | 123.0881 | 122.9782 | -0.27924
3193.8125 | 123.1293 | -122.7814 | 0.16479 | -0.22186 | 0.030869 | 0.0067932 | 0.010245 | -0.0060476 | -0.005048 | -0.0067291 | -0.21843 | -0.012127 | -0.0056118 | -0.00069421 | 0.00090353 | -0.01358 | 0.21057 | 0.23804 | 0.1831 | 0.18768 | 0.35706 | 0.082397 | -0.09613 | 0.15564 | 0.23346 | 0.09613 | 0.28839 | 0.25635 | -0.032043 | -0.086975 | 122.8638 | 122.6852 | 0.19226 | 123.0194 | 122.9691 | 0.28381 | 0.045776 | 122.7493 | 122.6944 | 0.1236 | 122.937 | 122.8775 | 0.1831 | 0.091553 | 123.1384 | 122.9919 | 122.9645 | -0.26092 | 123.0698 | 123.0377 | 123.0148 | -0.25177
3195.5781 | 123.0927 | -122.8043 | 0.17853 | 0.014648 | 0.028092 | 0.0052978 | 0.0051183 | -0.0073294 | -0.006116 | -0.0075837 | 0.094375 | -0.011914 | -0.0051846 | -0.0017624 | 0.00047633 | -0.01358 | 0.10071 | 0.12817 | 0.10529 | 0.11444 | 0.31128 | 0.032043 | -0.1236 | 0.1236 | 0.1831 | 0.09613 | 0.24261 | 0.21057 | -0.059509 | -0.09613 | 122.8363 | 122.6807 | 0.13275 | 122.9324 | 122.9187 | 0.23804 | -0.07782 | 122.7448 | 122.7081 | 0.064087 | 122.9279 | 122.9004 | 0.19226 | 0.032043 | 123.1155 | 122.905 | 122.9095 | -0.30212 | 123.0469 | 123.0148 | 122.9874 | -0.27466
3197.2812 | 123.0423 | -122.8271 | 0.20142 | 0.17487 | 0.028305 | 0.0067932 | 0.0027685 | -0.009252 | -0.0012028 | -0.0075837 | 0.14778 | -0.0117 | -0.0075344 | -0.00069421 | 0.0062441 | -0.015075 | 0.12817 | 0.11444 | 0.07782 | 0.07782 | 0.21057 | -0.032043 | -0.18768 | 0.12817 | 0.16022 | 0.045776 | 0.15564 | 0.14648 | -0.10986 | -0.15564 | 122.7951 | 122.6395 | 0.009155 | 122.9416 | 122.905 | 0.2655 | -0.073242 | 122.7173 | 122.6715 | -0.045776 | 122.9553 | 122.8729 | 0.20142 | -0.054932 | 123.0377 | 122.9553 | 122.905 | -0.3891 | 122.9828 | 122.9736 | 122.9874 | -0.35706
3199.0469 | 123.1567 | -122.7859 | 0.16022 | -0.0082397 | 0.028519 | 0.0072204 | 0.0078955 | -0.0098928 | -0.0048344 | -0.0082245 | -0.0048066 | -0.011273 | -0.004971 | -0.003685 | 0.0011173 | -0.015289 | 0.13275 | 0.15564 | 0.16479 | 0.14648 | 0.32044 | 0.013733 | -0.091553 | 0.1831 | 0.24719 | 0.14191 | 0.23804 | 0.21515 | -0.054932 | -0.086975 | 122.7997 | 122.6944 | 0.16022 | 122.9416 | 122.9324 | 0.23804 | -0.027466 | 122.731 | 122.699 | 0.07782 | 122.9691 | 122.9279 | 0.22888 | 0.054932 | 123.1064 | 122.9187 | 122.9507 | -0.25177 | 123.024 | 123.0011 | 123.0331 | -0.24719
3200.75 | 123.1293 | -122.8088 | 0.17395 | -0.16083 | 0.028519 | 0.0044434 | 0.0091773 | -0.0073294 | -0.00077538 | -0.0088653 | -0.21843 | -0.012768 | -0.0041164 | -0.00026701 | 0.0011173 | -0.016571 | 0.2243 | 0.23346 | 0.1831 | 0.19226 | 0.3479 | 0.068665 | -0.073242 | 0.17853 | 0.27008 | 0.1236 | 0.27008 | 0.24719 | -0.027466 | -0.07782 | 122.8775 | 122.7356 | 0.17395 | 123.0423 | 123.0011 | 0.2655 | 0.050354 | 122.7814 | 122.731 | 0.096131 | 122.9874 | 122.9324 | 0.20142 | 0.073242 | 123.1567 | 123.0331 | 122.9919 | -0.24719 | 123.0789 | 123.056 | 123.0789 | -0.25177
3202.5312 | 123.1247 | -122.8226 | 0.1831 | -0.21423 | 0.028305 | 0.0044434 | 0.0078955 | -0.0069022 | -0.0018436 | -0.0073701 | -0.15739 | -0.01405 | -0.0043302 | -0.0013352 | 0.0030399 | -0.017852 | 0.21515 | 0.2655 | 0.21973 | 0.21515 | 0.35248 | 0.10529 | -0.082397 | 0.19684 | 0.27466 | 0.14191 | 0.24719 | 0.21515 | -0.036621 | -0.07782 | 122.9279 | 122.7402 | 0.16937 | 123.0881 | 123.0377 | 0.29755 | 0.032044 | 122.7859 | 122.7448 | 0.064087 | 123.0194 | 122.9645 | 0.21973 | 0.032044 | 123.175 | 123.0377 | 123.0423 | -0.2655 | 123.0698 | 123.0377 | 123.0972 | -0.26092
3204.2344 | 123.1888 | -122.7951 | 0.16937 | -0.23712 | 0.028946 | 0.0052978 | 0.0059729 | -0.0071158 | 0.0041378 | -0.0065155 | -0.25658 | -0.010846 | -0.0062528 | 0.00037379 | 0.0053897 | -0.016357 | 0.13733 | 0.1236 | 0.073242 | 0.1236 | 0.40741 | 0.054932 | -0.10986 | 0.091553 | 0.13275 | 0.009155 | 0.3067 | 0.24719 | -0.073242 | -0.10986 | 122.85 | 122.6852 | 0.23804 | 122.9187 | 122.9187 | 0.23346 | -0.032044 | 122.7219 | 122.6852 | 0.13733 | 122.8867 | 122.8043 | 0.11902 | 0.077819 | 123.2025 | 122.9324 | 122.8683 | -0.27924 | 123.1018 | 123.0423 | 122.9279 | -0.27924
3205.9844 | 123.1247 | -122.8134 | 0.18768 | -0.21423 | 0.028519 | 0.006366 | 0.0083227 | -0.0079702 | -0.0020572 | -0.0063019 | -0.20317 | -0.014905 | -0.0047574 | -0.00090781 | 0.0026125 | -0.016357 | 0.12817 | 0.14191 | 0.10529 | 0.1236 | 0.3891 | 0.059509 | -0.10071 | 0.11902 | 0.16937 | 0.032043 | 0.30212 | 0.2655 | -0.064087 | -0.11444 | 122.8729 | 122.7127 | 0.20142 | 122.9553 | 122.937 | 0.2243 | -0.059509 | 122.7493 | 122.699 | 0.11444 | 122.9324 | 122.8455 | 0.14648 | 0.07782 | 123.2025 | 122.9416 | 122.9187 | -0.28839 | 123.1155 | 123.0789 | 122.9828 | -0.30212
3207.6875 | 123.1796 | -122.7905 | 0.17853 | -0.16083 | 0.026596 | 0.0078614 | 0.0046911 | -0.007543 | -0.0046206 | -0.0084381 | -0.08873 | -0.012341 | -0.0081754 | -0.0030442 | 0.0032535 | -0.012939 | 0.21515 | 0.27008 | 0.21973 | 0.19684 | 0.33875 | 0.054932 | -0.10071 | 0.23346 | 0.28381 | 0.19684 | 0.24719 | 0.21973 | -0.018311 | -0.064087 | 122.8455 | 122.6898 | 0.16022 | 123.0606 | 122.9874 | 0.29755 | 0.036621 | 122.7722 | 122.7264 | 0.068664 | 123.024 | 122.9874 | 0.26093 | 0.041199 | 123.1293 | 123.0057 | 123.0103 | -0.27924 | 123.0377 | 123.0103 | 123.0743 | -0.24261
3209.4375 | 123.143 | -122.8317 | 0.16937 | -0.26001 | 0.029373 | 0.007434 | 0.0061865 | -0.0069022 | -0.0018436 | -0.0058747 | -0.2108 | -0.010418 | -0.0064664 | 0.00058739 | 0.0030399 | -0.01593 | 0.18768 | 0.20142 | 0.16022 | 0.17853 | 0.37994 | 0.050354 | -0.091553 | 0.12817 | 0.16937 | 0.045776 | 0.30212 | 0.26093 | -0.050354 | -0.09613 | 122.8821 | 122.7402 | 0.21057 | 123.0331 | 123.0103 | 0.27008 | 0.01831 | 122.7814 | 122.7356 | 0.13275 | 122.9599 | 122.8775 | 0.14191 | 0.091552 | 123.2117 | 123.0194 | 122.9919 | -0.26093 | 123.1339 | 123.0927 | 123.0011 | -0.2655
3211.1406 | 123.0606 | -122.8455 | 0.19226 | 0.052795 | 0.030655 | 0.0042298 | 0.0051183 | -0.008611 | -0.003339 | -0.0071563 | 0.056228 | -0.013409 | -0.0056118 | -0.0024032 | 0.0017581 | -0.015716 | 0.10071 | 0.15106 | 0.10529 | 0.10529 | 0.29297 | 0.009155 | -0.13733 | 0.14191 | 0.17395 | 0.10986 | 0.23346 | 0.18768 | -0.073242 | -0.1236 | 122.8546 | 122.7081 | 0.10071 | 122.9965 | 122.9507 | 0.24262 | -0.091553 | 122.7722 | 122.7219 | 0.041198 | 122.9874 | 122.9553 | 0.23346 | -0.004578 | 123.1384 | 122.9462 | 122.9507 | -0.32959 | 123.0789 | 123.0331 | 123.0194 | -0.31586
3212.9062 | 123.0377 | -122.8317 | 0.21057 | 0.12146 | 0.030655 | 0.0038024 | 0.0066137 | -0.0064748 | -0.00034818 | -0.0092927 | 0.13252 | -0.0117 | -0.0045438 | -0.0026168 | 0.0043215 | -0.016784 | 0.10986 | 0.15106 | 0.10529 | 0.091553 | 0.2243 | -0.013733 | -0.16479 | 0.16022 | 0.15564 | 0.054932 | 0.19684 | 0.15106 | -0.10529 | -0.14191 | 122.818 | 122.6669 | 0.013733 | 122.9828 | 122.9233 | 0.25635 | -0.10071 | 122.7264 | 122.6898 | -0.013733 | 122.9919 | 122.8867 | 0.19684 | -0.059509 | 123.056 | 122.9416 | 122.937 | -0.37537 | 123.0286 | 122.9828 | 122.9874 | -0.35248
3214.6094 | 123.1659 | -122.818 | 0.17853 | -0.21423 | 0.032791 | 0.0067932 | 0.0055457 | -0.0081838 | 0.0049924 | -0.0077973 | -0.22606 | -0.0097775 | -0.0058254 | -0.0011216 | 0.0058169 | -0.017212 | 0.14648 | 0.14191 | 0.064087 | 0.1236 | 0.37537 | 0.027466 | -0.12817 | 0.11444 | 0.14648 | -0.013733 | 0.24261 | 0.21057 | -0.09613 | -0.15564 | 122.8455 | 122.6898 | 0.19684 | 122.9599 | 122.9416 | 0.25177 | -0.032044 | 122.7219 | 122.6624 | 0.064087 | 122.9324 | 122.8043 | 0.14191 | 0.032043 | 123.1934 | 122.9645 | 122.8821 | -0.3067 | 123.0606 | 123.0286 | 122.9645 | -0.33417
3216.3594 | 123.0606 | -122.8409 | 0.21057 | 0.060425 | 0.033005 | 0.0061524 | 0.0029821 | -0.01032 | 0.0037106 | -0.0052337 | 0.04097 | -0.0076413 | -0.006039 | -0.00090781 | 0.0083805 | -0.015716 | 0 | -0.041199 | -0.054932 | -0.013733 | 0.27466 | -0.050354 | -0.23346 | 0.013733 | -0.004578 | -0.09613 | 0.20599 | 0.16479 | -0.15564 | -0.20599 | 122.7905 | 122.6074 | 0.064087 | 122.7997 | 122.8271 | 0.21973 | -0.21057 | 122.6852 | 122.6349 | -0.004577 | 122.8546 | 122.7448 | 0.10986 | -0.045776 | 123.1155 | 122.8409 | 122.7859 | -0.44403 | 123.0469 | 123.0057 | 122.8363 | -0.41657
3218.125 | 123.0927 | -122.818 | 0.19226 | 0.029907 | 0.027023 | 0.0070068 | 0.0074683 | -0.0094656 | -0.0056888 | -0.0060883 | 0.063858 | -0.012127 | -0.0068936 | -0.0021896 | 0.0015445 | -0.014435 | 0.086975 | 0.12817 | 0.1236 | 0.1236 | 0.31586 | 0.027466 | -0.13275 | 0.14191 | 0.18768 | 0.10071 | 0.23346 | 0.20599 | -0.050354 | -0.11444 | 122.8455 | 122.6852 | 0.1236 | 122.9462 | 122.9416 | 0.25635 | -0.10529 | 122.7676 | 122.7036 | 0.041198 | 122.9599 | 122.9187 | 0.21515 | 0.013733 | 123.1338 | 122.905 | 122.9416 | -0.32501 | 123.0515 | 123.024 | 123.0057 | -0.3067
3219.8281 | 123.1613 | -122.7859 | 0.16022 | -0.1532 | 0.028732 | 0.0061524 | 0.0064001 | -0.0096792 | -0.003339 | -0.0084381 | -0.065842 | -0.011487 | -0.0062528 | -0.0013352 | 4.9132e-05 | -0.015075 | 0.21057 | 0.25635 | 0.20599 | 0.19226 | 0.32501 | 0.068665 | -0.09613 | 0.25177 | 0.29755 | 0.21057 | 0.25635 | 0.20599 | -0.009155 | -0.07782 | 122.8546 | 122.6898 | 0.1648 | 123.0423 | 122.9782 | 0.28839 | 0.050354 | 122.7768 | 122.7081 | 0.096131 | 123.0377 | 122.9965 | 0.28839 | 0.045777 | 123.111 | 122.9965 | 122.9919 | -0.25635 | 123.0423 | 122.9919 | 123.0835 | -0.23804
3221.5781 | 123.0743 | -122.8271 | 0.21515 | 0.098572 | 0.02916 | 0.0038024 | 0.0029821 | -0.0088248 | 0.0041378 | -0.0054475 | 0.048599 | -0.0097775 | -0.0053982 | -0.00090781 | 0.0094485 | -0.015716 | 0.027466 | -0.032043 | -0.068665 | -0.009155 | 0.2655 | -0.07782 | -0.22888 | 0.018311 | 0.009155 | -0.082397 | 0.20599 | 0.15106 | -0.17853 | -0.20142 | 122.7493 | 122.5983 | 0.050354 | 122.7951 | 122.818 | 0.21973 | -0.18768 | 122.6486 | 122.6257 | -0.009155 | 122.8455 | 122.7448 | 0.11902 | -0.064087 | 123.0927 | 122.8546 | 122.7585 | -0.44403 | 123.0331 | 122.9782 | 122.8363 | -0.41657
3223.2812 | 123.1201 | -122.818 | 0.18768 | -0.19135 | 0.029373 | 0.0067932 | 0.0070409 | -0.0083974 | -0.0031254 | -0.0073701 | -0.21843 | -0.0117 | -0.0051846 | -0.00069421 | 0.0021853 | -0.015716 | 0.21057 | 0.23804 | 0.18768 | 0.18768 | 0.35706 | 0.082397 | -0.082397 | 0.16479 | 0.22888 | 0.091553 | 0.29297 | 0.2655 | -0.054932 | -0.068665 | 122.9004 | 122.7356 | 0.16937 | 123.056 | 123.0057 | 0.27008 | 0.022888 | 122.7631 | 122.7493 | 0.10529 | 122.9828 | 122.9095 | 0.16022 | 0.07782 | 123.175 | 123.0286 | 123.0057 | -0.27008 | 123.111 | 123.0835 | 123.0469 | -0.25635
3225.0469 | 123.1384 | -122.818 | 0.16479 | -0.19135 | 0.028519 | 0.0067932 | 0.0061865 | -0.0094656 | -0.0041934 | -0.0088653 | -0.17265 | -0.012768 | -0.0039028 | -0.0026168 | 0.0023989 | -0.016357 | 0.24719 | 0.27466 | 0.21973 | 0.2243 | 0.3479 | 0.091553 | -0.073242 | 0.21515 | 0.29755 | 0.15106 | 0.27008 | 0.21973 | -0.018311 | -0.068665 | 122.9095 | 122.7448 | 0.1831 | 123.0927 | 123.0423 | 0.29755 | 0.082397 | 122.7997 | 122.7493 | 0.10529 | 123.0331 | 122.9691 | 0.21973 | 0.054932 | 123.1659 | 123.0652 | 123.0377 | -0.23804 | 123.0881 | 123.0377 | 123.1155 | -0.23346
3226.75 | 123.1934 | -122.8226 | 0.16022 | -0.18372 | 0.027451 | 0.0044434 | 0.0057593 | -0.0083974 | 0.00071982 | -0.0080109 | -0.27946 | -0.011487 | -0.006039 | -0.0030442 | 0.0064577 | -0.015289 | 0.14648 | 0.12817 | 0.068665 | 0.13733 | 0.37537 | 0.013733 | -0.11444 | 0.10529 | 0.16937 | 0.032043 | 0.28381 | 0.24261 | -0.07782 | -0.12817 | 122.8363 | 122.7081 | 0.21515 | 122.9507 | 122.9599 | 0.25177 | -0.013733 | 122.7448 | 122.6944 | 0.1236 | 122.9279 | 122.8546 | 0.16022 | 0.082398 | 123.1979 | 122.9691 | 122.8912 | -0.27466 | 123.1064 | 123.0652 | 122.9919 | -0.28839
3228.5156 | 123.1476 | -122.8043 | 0.16937 | 0.014648 | 0.027664 | 0.0050842 | 0.0087499 | -0.0090384 | -0.0073978 | -0.0075837 | 0.048599 | -0.012555 | -0.007748 | -0.0041122 | 0.0034671 | -0.014862 | 0.10529 | 0.14191 | 0.1236 | 0.1236 | 0.32044 | 0.045776 | -0.11902 | 0.15106 | 0.21057 | 0.13733 | 0.23346 | 0.20599 | -0.054932 | -0.10071 | 122.85 | 122.6852 | 0.15106 | 122.9462 | 122.9279 | 0.24261 | -0.064087 | 122.7493 | 122.7036 | 0.064086 | 122.9553 | 122.9416 | 0.23804 | 0.036621 | 123.1247 | 122.9095 | 122.9279 | -0.28839 | 123.0377 | 123.0103 | 123.0148 | -0.27008
3230.2031 | 123.1979 | -122.7859 | 0.17395 | -0.25238 | 0.030441 | 0.004657 | 0.0089635 | -0.0069022 | 0.00093342 | -0.0097199 | -0.26421 | -0.0117 | -0.0064664 | 0.00058739 | 0.0064577 | -0.015289 | 0.17395 | 0.13275 | 0.09613 | 0.12817 | 0.4303 | 0.064087 | -0.10986 | 0.091553 | 0.14191 | 0.009155 | 0.3067 | 0.2655 | -0.073242 | -0.10986 | 122.85 | 122.6761 | 0.25635 | 122.9187 | 122.9141 | 0.23804 | 0 | 122.7127 | 122.6761 | 0.13275 | 122.8775 | 122.7951 | 0.11902 | 0.091553 | 123.2162 | 122.9599 | 122.8821 | -0.28381 | 123.0927 | 123.0515 | 122.9279 | -0.28381
3231.9688 | 123.0469 | -122.8592 | 0.21057 | -0.00061023 | 0.034287 | 0.0044434 | 0.0038367 | -0.007543 | 0.0032834 | -0.0069427 | -0.020065 | -0.011487 | -0.0051846 | -0.0017624 | 0.0083805 | -0.015289 | 0.059509 | 0.036621 | -0.027466 | 0.022888 | 0.26093 | -0.045776 | -0.21973 | 0.018311 | 0.036621 | -0.10071 | 0.19226 | 0.14648 | -0.16022 | -0.21515 | 122.8134 | 122.6395 | 0.050354 | 122.8958 | 122.8821 | 0.24261 | -0.15106 | 122.699 | 122.644 | -0.01831 | 122.8775 | 122.7585 | 0.11444 | -0.064087 | 123.1201 | 122.9187 | 122.8317 | -0.4303 | 123.0515 | 123.0057 | 122.8958 | -0.42572
3233.7344 | 123.0469 | -122.8317 | 0.21057 | 0.16724 | 0.028305 | 0.0067932 | 0.0044775 | -0.008611 | -0.0048344 | -0.0063019 | 0.13252 | -0.011914 | -0.0079618 | -0.0013352 | 0.0060305 | -0.014435 | 0.082397 | 0.13275 | 0.091553 | 0.073242 | 0.21057 | -0.036621 | -0.19684 | 0.14648 | 0.17853 | 0.073242 | 0.16937 | 0.13733 | -0.091553 | -0.16479 | 122.7951 | 122.6349 | 0 | 122.9645 | 122.905 | 0.27008 | -0.12817 | 122.7402 | 122.6669 | -0.041198 | 122.9782 | 122.905 | 0.23804 | -0.073242 | 123.0423 | 122.9141 | 122.9233 | -0.40741 | 123.0011 | 122.9691 | 123.0103 | -0.37537
3235.4375 | 123.0881 | -122.8455 | 0.17395 | 0.13672 | 0.030655 | 0.0067932 | 0.0057593 | -0.0077566 | 0.00093342 | -0.0058747 | 0.16304 | -0.0091367 | -0.0068936 | -0.00090781 | 0.0053897 | -0.01593 | 0.022888 | 0.013733 | -0.022888 | 0 | 0.26093 | -0.073242 | -0.23346 | 0.073242 | 0.082397 | -0.004578 | 0.16479 | 0.12817 | -0.12817 | -0.16937 | 122.7722 | 122.612 | 0.086975 | 122.8592 | 122.8455 | 0.23346 | -0.15106 | 122.7173 | 122.6761 | -0.009155 | 122.9187 | 122.8409 | 0.16479 | -0.045776 | 123.1064 | 122.8683 | 122.8226 | -0.40741 | 123.0103 | 122.9736 | 122.9279 | -0.34332
3237.2031 | 123.1338 | -122.818 | 0.20142 | -0.11505 | 0.027451 | 0.0055114 | 0.0055457 | -0.010747 | 0.0028562 | -0.0037385 | -0.14214 | -0.0099911 | -0.0051846 | -0.0028306 | 0.0077395 | -0.015289 | 0.13275 | 0.1236 | 0.045776 | 0.091553 | 0.32044 | -0.013733 | -0.1831 | 0.09613 | 0.1236 | -0.018311 | 0.21515 | 0.19226 | -0.11902 | -0.16937 | 122.8043 | 122.6349 | 0.11902 | 122.9416 | 122.9095 | 0.27466 | -0.068665 | 122.699 | 122.6486 | 0.013733 | 122.9141 | 122.7997 | 0.15106 | -0.009155 | 123.1384 | 122.9507 | 122.8638 | -0.38452 | 123.0331 | 123.0103 | 122.9416 | -0.37079
3238.9062 | 123.0286 | -122.8409 | 0.19684 | 0.11383 | 0.028305 | 0.0055114 | 0.0068273 | -0.0083974 | -0.0059024 | -0.0088653 | 0.17067 | -0.011273 | -0.0073208 | 0.00037379 | 0.0038943 | -0.01358 | 0.086975 | 0.14191 | 0.091553 | 0.073242 | 0.23804 | -0.022888 | -0.18768 | 0.12817 | 0.17853 | 0.07782 | 0.17853 | 0.12817 | -0.086975 | -0.15564 | 122.818 | 122.6532 | 0.041199 | 122.9828 | 122.9141 | 0.26092 | -0.10986 | 122.7539 | 122.6852 | -0.01831 | 122.9691 | 122.9187 | 0.23346 | -0.068664 | 123.0789 | 122.9279 | 122.9324 | -0.38452 | 123.0194 | 122.9691 | 123.0194 | -0.35248
3240.6719 | 123.056 | -122.85 | 0.20599 | -0.054016 | 0.032791 | 0.0059388 | 0.0029821 | -0.0088248 | 0.0032834 | -0.0065155 | -0.11925 | -0.010846 | -0.006039 | -0.0015488 | 0.0056033 | -0.015289 | 0.13275 | 0.10071 | 0.027466 | 0.073242 | 0.29755 | -0.018311 | -0.17395 | 0.068665 | 0.086975 | -0.045776 | 0.21973 | 0.17395 | -0.13733 | -0.16479 | 122.8317 | 122.6761 | 0.091552 | 122.9507 | 122.9233 | 0.24719 | -0.073243 | 122.7127 | 122.6852 | 0.013733 | 122.9187 | 122.8043 | 0.11902 | -0.032044 | 123.1476 | 122.9828 | 122.8775 | -0.37994 | 123.0698 | 123.024 | 122.937 | -0.37079
3242.4531 | 123.111 | -122.8043 | 0.16937 | -0.21423 | 0.028092 | 0.0076478 | 0.0053321 | -0.009252 | -0.005048 | -0.0069427 | -0.11925 | -0.013409 | -0.0071072 | -0.001976 | 0.0021853 | -0.012726 | 0.19684 | 0.27466 | 0.21515 | 0.20142 | 0.34332 | 0.082397 | -0.07782 | 0.1831 | 0.29297 | 0.15564 | 0.23804 | 0.24261 | -0.032043 | -0.07782 | 122.8867 | 122.7264 | 0.17395 | 123.0789 | 123.0057 | 0.27924 | 0.027465 | 122.7722 | 122.7264 | 0.068664 | 122.9874 | 122.9599 | 0.23346 | 0.073242 | 123.1476 | 123.0011 | 123.0194 | -0.24719 | 123.0423 | 123.0469 | 123.0972 | -0.24719
3244.1406 | 123.2025 | -122.7905 | 0.16937 | -0.16083 | 0.033218 | 0.0048706 | 0.0087499 | -0.0056204 | -0.00056178 | -0.0080109 | -0.24895 | -0.011487 | -0.0039028 | -0.0026168 | 0.0058169 | -0.013366 | 0.12817 | 0.11444 | 0.073242 | 0.14191 | 0.36163 | 0.027466 | -0.14191 | 0.091553 | 0.14648 | 0.013733 | 0.28839 | 0.2243 | -0.07782 | -0.12817 | 122.818 | 122.6486 | 0.19226 | 122.905 | 122.9324 | 0.28381 | -0.041199 | 122.7127 | 122.6624 | 0.11902 | 122.8821 | 122.8043 | 0.14191 | 0.054931 | 123.1522 | 122.9187 | 122.8638 | -0.31128 | 123.0789 | 123.0148 | 122.937 | -0.29755
3245.8906 | 123.0515 | -122.8546 | 0.21057 | 0.1825 | 0.030655 | 0.0055114 | 0.0053321 | -0.009252 | -0.00077538 | -0.0075837 | 0.16304 | -0.011914 | -0.0041164 | -0.0038986 | 0.0036807 | -0.014648 | 0.082397 | 0.1236 | 0.086975 | 0.086975 | 0.20142 | -0.045776 | -0.20599 | 0.13733 | 0.16022 | 0.064087 | 0.15564 | 0.1236 | -0.11444 | -0.15564 | 122.8088 | 122.6486 | -0.009155 | 122.9782 | 122.9416 | 0.29297 | -0.12817 | 122.7402 | 122.699 | -0.054931 | 122.9919 | 122.9187 | 0.21973 | -0.086975 | 123.056 | 122.937 | 122.9416 | -0.41657 | 123.0103 | 122.9782 | 123.0148 | -0.36621
3247.6719 | 123.0698 | -122.8638 | 0.19684 | 0.19012 | 0.028092 | 0.0048706 | 0.0044775 | -0.0098928 | -0.0037662 | -0.0065155 | 0.17067 | -0.010205 | -0.0075344 | -0.0030442 | 0.0053897 | -0.014435 | 0.11902 | 0.10986 | 0.064087 | 0.082397 | 0.21515 | -0.041199 | -0.21057 | 0.11444 | 0.14648 | 0.022888 | 0.15106 | 0.10986 | -0.1236 | -0.19684 | 122.8226 | 122.6532 | 0.018311 | 122.9736 | 122.9462 | 0.29297 | -0.077819 | 122.7402 | 122.6669 | -0.045776 | 122.9782 | 122.8867 | 0.21973 | -0.086975 | 123.0789 | 122.9828 | 122.9279 | -0.40741 | 123.0148 | 122.9736 | 123.0103 | -0.39368
3249.4531 | 123.0423 | -122.8271 | 0.21973 | 0.12146 | 0.027664 | 0.0048706 | 0.0038367 | -0.0083974 | -0.0037662 | -0.0092927 | 0.15541 | -0.012555 | -0.0088162 | -0.0032578 | 0.0038943 | -0.012939 | 0.09613 | 0.15564 | 0.09613 | 0.073242 | 0.21515 | -0.027466 | -0.19226 | 0.13733 | 0.15564 | 0.050354 | 0.16937 | 0.15564 | -0.11444 | -0.16022 | 122.7997 | 122.6349 | -0.004578 | 122.9828 | 122.9004 | 0.2655 | -0.1236 | 122.7127 | 122.6669 | -0.050354 | 122.9645 | 122.8775 | 0.21057 | -0.064087 | 123.0423 | 122.9233 | 122.9233 | -0.41199 | 122.9965 | 122.9828 | 122.9828 | -0.37994
3251.1406 | 123.0423 | -122.8226 | 0.21057 | 0.16724 | 0.028519 | 0.0040162 | 0.0064001 | -0.0083974 | -0.00034818 | -0.0069427 | 0.14015 | -0.011059 | -0.0079618 | -0.0030442 | 0.0051761 | -0.015075 | 0.10986 | 0.11902 | 0.10071 | 0.07782 | 0.22888 | -0.045776 | -0.20599 | 0.15564 | 0.16479 | 0.054932 | 0.16937 | 0.15106 | -0.10529 | -0.16937 | 122.7768 | 122.6166 | 0.018311 | 122.9416 | 122.9004 | 0.28381 | -0.10071 | 122.7173 | 122.6532 | -0.041198 | 122.9782 | 122.8775 | 0.22431 | -0.059509 | 123.0515 | 122.9324 | 122.9233 | -0.41657 | 122.9919 | 122.9736 | 122.9874 | -0.37994
3252.9062 | 123.1293 | -122.8088 | 0.17395 | -0.19897 | 0.028946 | 0.006366 | 0.0061865 | -0.008611 | -0.0022708 | -0.0077973 | -0.18028 | -0.012768 | -0.0068936 | -0.0032578 | 0.0030399 | -0.015289 | 0.22888 | 0.24261 | 0.21057 | 0.19684 | 0.33875 | 0.086975 | -0.073242 | 0.19684 | 0.27466 | 0.1236 | 0.26093 | 0.20599 | -0.036621 | -0.091553 | 122.8958 | 122.7356 | 0.1648 | 123.0515 | 123.0057 | 0.27008 | 0.054932 | 122.7722 | 122.7173 | 0.086975 | 123.0057 | 122.9324 | 0.21515 | 0.032044 | 123.1476 | 123.0377 | 123.0194 | -0.24719 | 123.0698 | 123.0148 | 123.0835 | -0.2655
3254.5938 | 123.0881 | -122.8592 | 0.20599 | -0.084534 | 0.031509 | 0.0042298 | 0.0085363 | -0.0064748 | 0.0037106 | -0.0058747 | -0.14214 | -0.0097775 | -0.0043302 | -0.001976 | 0.0083805 | -0.018066 | 0.14191 | 0.10529 | 0.041199 | 0.073242 | 0.31128 | -0.009155 | -0.16937 | 0.09613 | 0.10071 | -0.036621 | 0.2243 | 0.1831 | -0.12817 | -0.17395 | 122.85 | 122.6898 | 0.10528 | 122.9645 | 122.9324 | 0.24261 | -0.064087 | 122.731 | 122.6852 | 0.01831 | 122.9553 | 122.8226 | 0.13733 | -0.022889 | 123.1705 | 123.0011 | 122.9004 | -0.37537 | 123.0835 | 123.0423 | 122.9599 | -0.37994
3256.3438 | 123.1201 | -122.8271 | 0.20599 | -0.092163 | 0.033218 | 0.004657 | 0.0040503 | -0.0064748 | 0.00093342 | -0.0065155 | -0.15739 | -0.011273 | -0.007748 | -0.0011216 | 0.0064577 | -0.018921 | 0.13733 | 0.1236 | 0.045776 | 0.086975 | 0.31128 | -0.018311 | -0.17853 | 0.10529 | 0.1236 | -0.027466 | 0.21515 | 0.18768 | -0.09613 | -0.17395 | 122.8088 | 122.6486 | 0.10528 | 122.9507 | 122.9141 | 0.2655 | -0.068665 | 122.731 | 122.6532 | 0.009155 | 122.9324 | 122.7997 | 0.14648 | -0.018311 | 123.1384 | 122.9645 | 122.8729 | -0.38452 | 123.0423 | 123.0148 | 122.9507 | -0.37994
3258.0469 | 123.1476 | -122.8043 | 0.16479 | -0.00061023 | 0.027664 | 0.007434 | 0.0081091 | -0.0064748 | -0.0071842 | -0.0097199 | 0.018082 | -0.013623 | -0.004971 | -0.0043258 | 0.0015445 | -0.015289 | 0.10529 | 0.15564 | 0.14191 | 0.13275 | 0.29755 | 0.013733 | -0.13275 | 0.15564 | 0.2243 | 0.1236 | 0.21973 | 0.21515 | -0.050354 | -0.09613 | 122.818 | 122.6715 | 0.13275 | 122.9599 | 122.937 | 0.2655 | -0.059509 | 122.7539 | 122.7081 | 0.054932 | 122.9599 | 122.9279 | 0.21973 | 0.050354 | 123.1018 | 122.9095 | 122.9462 | -0.29755 | 123.024 | 123.0194 | 123.0286 | -0.26092
3259.7969 | 123.0377 | -122.8363 | 0.19226 | 0.1062 | 0.026596 | 0.0059388 | 0.0040503 | -0.0064748 | -0.004407 | -0.0082245 | 0.13252 | -0.013409 | -0.0045438 | -0.0043258 | 0.0032535 | -0.014648 | 0.10529 | 0.13275 | 0.10071 | 0.073242 | 0.25635 | -0.032043 | -0.17853 | 0.14191 | 0.16479 | 0.054932 | 0.18768 | 0.17395 | -0.082397 | -0.14191 | 122.8043 | 122.6578 | 0.064087 | 122.9691 | 122.9095 | 0.25177 | -0.086975 | 122.7539 | 122.6944 | -0.004578 | 122.9782 | 122.8912 | 0.19684 | -0.018311 | 123.0927 | 122.9416 | 122.937 | -0.37079 | 123.024 | 123.0103 | 123.0011 | -0.33417
3261.5469 | 123.0423 | -122.8409 | 0.21515 | 0.022278 | 0.033432 | 0.0052978 | 0.0055457 | -0.0083974 | 0.006274 | -0.0054475 | -0.027695 | -0.0093503 | -0.007748 | -0.0011216 | 0.0092349 | -0.016998 | 0.059509 | -0.018311 | -0.041199 | 0.004578 | 0.27466 | -0.068665 | -0.21973 | 0.004578 | 0.018311 | -0.11444 | 0.20142 | 0.1831 | -0.15106 | -0.20599 | 122.7722 | 122.6212 | 0.059509 | 122.8226 | 122.8455 | 0.22431 | -0.15564 | 122.6898 | 122.6349 | -0.013733 | 122.8455 | 122.7264 | 0.091553 | -0.032044 | 123.1155 | 122.9004 | 122.7997 | -0.43488 | 123.0423 | 123.024 | 122.8592 | -0.42114
3263.25 | 123.1476 | -122.8088 | 0.17395 | -0.23712 | 0.030869 | 0.0078614 | 0.0078955 | -0.007543 | -0.0014164 | -0.0073701 | -0.24132 | -0.012768 | -0.0051846 | -0.0051804 | 0.0026125 | -0.014648 | 0.13275 | 0.14648 | 0.09613 | 0.1236 | 0.41657 | 0.050354 | -0.1236 | 0.10529 | 0.15564 | 0.032043 | 0.3067 | 0.26093 | -0.064087 | -0.10986 | 122.8592 | 122.6852 | 0.24262 | 122.9553 | 122.9324 | 0.24719 | -0.041199 | 122.7448 | 122.699 | 0.13275 | 122.9141 | 122.8409 | 0.14191 | 0.086975 | 123.2254 | 122.9416 | 122.905 | -0.29755 | 123.1155 | 123.0698 | 122.9645 | -0.28381
3265.0156 | 123.1842 | -122.8043 | 0.17395 | -0.26001 | 0.028732 | 0.007434 | 0.0085363 | -0.0077566 | -0.002698 | -0.0063019 | -0.27184 | -0.011059 | -0.0058254 | -0.00090781 | 0.0032535 | -0.015289 | 0.13733 | 0.15106 | 0.09613 | 0.1236 | 0.39825 | 0.054932 | -0.10986 | 0.091553 | 0.15564 | 0.022888 | 0.3067 | 0.26093 | -0.050354 | -0.09613 | 122.8592 | 122.6944 | 0.2243 | 122.9553 | 122.9279 | 0.23346 | -0.036621 | 122.7539 | 122.7081 | 0.13275 | 122.8958 | 122.8271 | 0.11902 | 0.086975 | 123.2025 | 122.9416 | 122.9004 | -0.28381 | 123.111 | 123.0652 | 122.9599 | -0.27008
3266.7812 | 123.1705 | -122.7905 | 0.15106 | -0.11505 | 0.028946 | 0.0057252 | 0.0089635 | -0.0071158 | -0.0073978 | -0.010147 | -0.08873 | -0.013623 | -0.004971 | -0.0043258 | 0.0034671 | -0.011871 | 0.19684 | 0.27466 | 0.20599 | 0.18768 | 0.33875 | 0.068665 | -0.09613 | 0.23346 | 0.30212 | 0.20599 | 0.25635 | 0.22888 | -0.041199 | -0.068665 | 122.8592 | 122.6944 | 0.18768 | 123.0652 | 122.9782 | 0.28381 | 0.045776 | 122.7493 | 122.7219 | 0.10529 | 123.024 | 122.9965 | 0.27466 | 0.07782 | 123.1293 | 122.9874 | 122.9965 | -0.24719 | 123.0469 | 123.0194 | 123.0927 | -0.21973
3268.5469 | 123.0743 | -122.8546 | 0.19226 | 0.083313 | 0.031082 | 0.0059388 | 0.0036231 | -0.0090384 | 0.0022152 | -0.0056611 | 0.048599 | -0.0099911 | -0.00668 | -5.3406e-05 | 0.0083805 | -0.015716 | 0.032043 | -0.022888 | -0.059509 | 0 | 0.27466 | -0.073242 | -0.23346 | 0.013733 | -0.009155 | -0.10071 | 0.18768 | 0.14191 | -0.14648 | -0.21515 | 122.7814 | 122.6212 | 0.082397 | 122.8317 | 122.8546 | 0.23346 | -0.16022 | 122.7081 | 122.6395 | -0.004578 | 122.8683 | 122.7539 | 0.11444 | -0.050354 | 123.1293 | 122.8867 | 122.7951 | -0.42572 | 123.0423 | 122.9965 | 122.8455 | -0.40741
3270.2344 | 123.1476 | -122.7951 | 0.17853 | -0.22186 | 0.031082 | 0.0057252 | 0.0074683 | -0.0064748 | -0.0024844 | -0.0060883 | -0.21843 | -0.0095639 | -0.006039 | -0.0028306 | 0.0026125 | -0.014862 | 0.16022 | 0.15106 | 0.11902 | 0.13275 | 0.3891 | 0.059509 | -0.10986 | 0.11444 | 0.16479 | 0.032043 | 0.31586 | 0.2655 | -0.068665 | -0.11444 | 122.8546 | 122.6852 | 0.21057 | 122.9462 | 122.9279 | 0.24261 | -0.018311 | 122.7264 | 122.6807 | 0.13733 | 122.9095 | 122.8271 | 0.14648 | 0.086975 | 123.1842 | 122.9553 | 122.9141 | -0.28839 | 123.111 | 123.0606 | 122.9599 | -0.29297
3272 | 123.056 | -122.85 | 0.19226 | -0.054016 | 0.031723 | 0.004657 | 0.0068273 | -0.010961 | 0.0039242 | -0.0056611 | -0.10399 | -0.0099911 | -0.0071072 | -0.0013352 | 0.0070987 | -0.015716 | 0.12817 | 0.10986 | 0.036621 | 0.091553 | 0.29755 | -0.045776 | -0.19226 | 0.054932 | 0.091553 | -0.059509 | 0.21057 | 0.1831 | -0.12817 | -0.17853 | 122.8043 | 122.6578 | 0.10528 | 122.9599 | 122.9416 | 0.28381 | -0.064087 | 122.7219 | 122.6715 | 0.01831 | 122.905 | 122.7905 | 0.11902 | -0.009156 | 123.1476 | 122.9782 | 122.8867 | -0.38452 | 123.0606 | 123.0331 | 122.9416 | -0.37079
3273.7031 | 123.056 | -122.8226 | 0.20142 | 0.083313 | 0.025955 | 0.0085022 | 0.0051183 | -0.0073294 | -0.006116 | -0.0075837 | 0.12489 | -0.0117 | -0.0079618 | -0.0030442 | 0.0036807 | -0.011871 | 0.073242 | 0.15106 | 0.10986 | 0.07782 | 0.25635 | 0 | -0.15106 | 0.11444 | 0.17853 | 0.07782 | 0.20599 | 0.18768 | -0.073242 | -0.12817 | 122.8226 | 122.6715 | 0.054932 | 122.9736 | 122.9004 | 0.22888 | -0.12817 | 122.7493 | 122.6944 | 0.004578 | 122.937 | 122.9004 | 0.20599 | -0.013733 | 123.0789 | 122.8958 | 122.9324 | -0.35248 | 123.0286 | 123.0103 | 123.0011 | -0.32959
3275.4688 | 123.1384 | -122.8271 | 0.19226 | -0.21423 | 0.032364 | 0.0055114 | 0.0074683 | -0.0094656 | -0.00098918 | -0.0065155 | -0.22606 | -0.012768 | -0.0045438 | -0.0013352 | 0.0015445 | -0.01593 | 0.1236 | 0.1236 | 0.09613 | 0.12817 | 0.39368 | 0.041199 | -0.10071 | 0.10529 | 0.16022 | 0.032043 | 0.31586 | 0.27466 | -0.059509 | -0.10986 | 122.8683 | 122.7264 | 0.20142 | 122.9507 | 122.9553 | 0.22888 | -0.068665 | 122.7676 | 122.7173 | 0.1236 | 122.9324 | 122.8592 | 0.14191 | 0.082397 | 123.2208 | 122.9507 | 122.9233 | -0.29297 | 123.143 | 123.1018 | 122.9874 | -0.30212
3277.1719 | 123.0423 | -122.8729 | 0.21973 | 0.0070193 | 0.030441 | 0.001239 | 0.0046911 | -0.0088248 | 0.0028562 | -0.0071563 | 0.018082 | -0.011487 | -0.0047574 | 0.00080099 | 0.0079531 | -0.016998 | 0.050354 | 0.009155 | -0.041199 | 0.018311 | 0.27466 | -0.041199 | -0.21515 | 0.009155 | 0.022888 | -0.10071 | 0.21057 | 0.16022 | -0.15106 | -0.20599 | 122.8317 | 122.6578 | 0.054931 | 122.8821 | 122.8912 | 0.23346 | -0.16937 | 122.7219 | 122.6669 | -0.009156 | 122.8821 | 122.7722 | 0.10529 | -0.05951 | 123.1476 | 122.9233 | 122.8317 | -0.43488 | 123.0835 | 123.0331 | 122.8958 | -0.42572
3278.9375 | 123.0789 | -122.8317 | 0.19684 | 0.1062 | 0.028305 | 0.006366 | 0.0046911 | -0.010961 | 0.001788 | -0.0063019 | 0.079117 | -0.0082821 | -0.0062528 | -0.0032578 | 0.0090213 | -0.01358 | 0 | -0.036621 | -0.07782 | -0.022888 | 0.25635 | -0.082397 | -0.24719 | 0 | 0.013733 | -0.082397 | 0.20599 | 0.15106 | -0.15564 | -0.21515 | 122.7493 | 122.5845 | 0.05951 | 122.7951 | 122.8088 | 0.2243 | -0.19684 | 122.6761 | 122.6166 | 0.009156 | 122.8317 | 122.7493 | 0.13275 | -0.045776 | 123.0881 | 122.8317 | 122.7539 | -0.44403 | 123.0377 | 122.9828 | 122.8455 | -0.41199
3280.6875 | 123.1842 | -122.7905 | 0.17853 | -0.17609 | 0.03215 | 0.0052978 | 0.0083227 | -0.0081838 | -0.00013458 | -0.0080109 | -0.2108 | -0.0095639 | -0.0041164 | -0.0032578 | 0.0045351 | -0.01593 | 0.11902 | 0.11902 | 0.082397 | 0.12817 | 0.36621 | 0.032043 | -0.13275 | 0.073242 | 0.15106 | 0.004578 | 0.25177 | 0.21515 | -0.086975 | -0.13733 | 122.8226 | 122.6578 | 0.18768 | 122.9095 | 122.9187 | 0.26093 | -0.059509 | 122.7036 | 122.6532 | 0.073242 | 122.8638 | 122.7951 | 0.14191 | 0.036621 | 123.1567 | 122.9095 | 122.8729 | -0.31128 | 123.0423 | 123.0057 | 122.9416 | -0.31586
3282.3906 | 123.175 | -122.7951 | 0.15564 | -0.054016 | 0.027451 | 0.0076478 | 0.0064001 | -0.0069022 | -0.0080386 | -0.0077973 | -0.020065 | -0.011487 | -0.0056118 | -0.0024032 | 0.00047633 | -0.012085 | 0.10986 | 0.20599 | 0.17395 | 0.15106 | 0.32044 | 0.041199 | -0.11902 | 0.19226 | 0.27924 | 0.16022 | 0.25177 | 0.21515 | -0.032043 | -0.068665 | 122.8363 | 122.6761 | 0.1648 | 123.0011 | 122.9462 | 0.27008 | -0.045777 | 122.7631 | 122.7264 | 0.09613 | 122.9874 | 122.9553 | 0.22888 | 0.059509 | 123.1155 | 122.905 | 122.9691 | -0.27466 | 123.0469 | 123.0103 | 123.0743 | -0.22431
3284.1562 | 123.1842 | -122.818 | 0.17395 | -0.26001 | 0.031723 | 0.0055114 | 0.0111 | -0.010747 | -0.00013458 | -0.0084381 | -0.19554 | -0.0095639 | -0.004971 | -0.00090781 | 0.0032535 | -0.017212 | 0.13275 | 0.1236 | 0.073242 | 0.11902 | 0.41657 | 0.036621 | -0.11902 | 0.086975 | 0.15106 | 0.004578 | 0.28381 | 0.27924 | -0.064087 | -0.12817 | 122.8546 | 122.699 | 0.24262 | 122.9416 | 122.937 | 0.23804 | -0.041199 | 122.7539 | 122.6898 | 0.10986 | 122.905 | 122.8226 | 0.13275 | 0.10529 | 123.2346 | 122.9507 | 122.8912 | -0.29297 | 123.1018 | 123.0972 | 122.9691 | -0.30212
3285.9062 | 123.1247 | -122.7859 | 0.16479 | -0.19897 | 0.027878 | 0.0050842 | 0.0093909 | -0.0071158 | -0.005048 | -0.0099335 | -0.11925 | -0.012982 | -0.004971 | -0.0013352 | 0.0034671 | -0.014221 | 0.21515 | 0.28839 | 0.23346 | 0.21057 | 0.37079 | 0.082397 | -0.068665 | 0.20599 | 0.29755 | 0.16479 | 0.27008 | 0.22888 | -0.027466 | -0.064087 | 122.8683 | 122.7173 | 0.20599 | 123.0743 | 122.9965 | 0.27924 | 0.050354 | 122.7585 | 122.7219 | 0.10529 | 122.9919 | 122.9507 | 0.22888 | 0.064087 | 123.1567 | 123.0011 | 123.0194 | -0.23346 | 123.056 | 123.0148 | 123.0835 | -0.22888
3287.6562 | 123.1842 | -122.7997 | 0.17395 | -0.17609 | 0.031296 | 0.0048706 | 0.0098181 | -0.007543 | 0.0015744 | -0.0052337 | -0.22606 | -0.0093503 | -0.0068936 | -0.0028306 | 0.0030399 | -0.016357 | 0.11902 | 0.10529 | 0.059509 | 0.11902 | 0.38452 | 0.022888 | -0.13733 | 0.09613 | 0.15564 | 0.004578 | 0.27924 | 0.25177 | -0.091553 | -0.13733 | 122.8226 | 122.6624 | 0.21057 | 122.905 | 122.9187 | 0.25635 | -0.054931 | 122.7081 | 122.6624 | 0.10529 | 122.8958 | 122.8043 | 0.14191 | 0.07782 | 123.1842 | 122.9187 | 122.8592 | -0.31128 | 123.0789 | 123.0515 | 122.9553 | -0.31128
3289.3594 | 123.1934 | -122.7905 | 0.17395 | -0.18372 | 0.031509 | 0.0052978 | 0.0087499 | -0.008611 | 0.001788 | -0.0067291 | -0.21843 | -0.0117 | -0.0053982 | 0.00037379 | 0.0056033 | -0.015716 | 0.1236 | 0.11444 | 0.073242 | 0.12817 | 0.3891 | 0.054932 | -0.10986 | 0.07782 | 0.14191 | 0.032043 | 0.27924 | 0.25177 | -0.059509 | -0.12817 | 122.8455 | 122.6807 | 0.21515 | 122.905 | 122.9187 | 0.23804 | -0.050354 | 122.731 | 122.6624 | 0.10529 | 122.8683 | 122.8226 | 0.16022 | 0.07782 | 123.1796 | 122.9141 | 122.8638 | -0.28381 | 123.0698 | 123.0423 | 122.9324 | -0.30212
3291.1094 | 123.0515 | -122.8088 | 0.1831 | 0.16724 | 0.028946 | 0.0035888 | 0.0034093 | -0.0090384 | -0.0041934 | -0.0063019 | 0.20882 | -0.014691 | -0.0086026 | -0.0026168 | 0.0062441 | -0.01593 | 0.09613 | 0.10986 | 0.082397 | 0.068665 | 0.20142 | -0.054932 | -0.21515 | 0.13733 | 0.16022 | 0.064087 | 0.14648 | 0.11902 | -0.13733 | -0.16479 | 122.7539 | 122.5937 | 0.018311 | 122.9187 | 122.8775 | 0.28381 | -0.086975 | 122.6715 | 122.644 | -0.036621 | 122.9462 | 122.8729 | 0.22888 | -0.064086 | 123.0103 | 122.905 | 122.8912 | -0.39825 | 122.9553 | 122.9279 | 122.9691 | -0.3479
3292.875 | 123.0377 | -122.85 | 0.21057 | 0.1062 | 0.0298 | 0.0035888 | 0.0070409 | -0.005834 | -0.0020572 | -0.0073701 | 0.14778 | -0.012982 | -0.0053982 | -0.0026168 | 0.0026125 | -0.015289 | 0.10071 | 0.11444 | 0.091553 | 0.064087 | 0.23346 | -0.018311 | -0.1831 | 0.13733 | 0.15564 | 0.082397 | 0.19226 | 0.16937 | -0.09613 | -0.12817 | 122.8317 | 122.6669 | 0.022888 | 122.9645 | 122.9141 | 0.24719 | -0.10986 | 122.7539 | 122.7219 | -0.01831 | 122.9874 | 122.9324 | 0.21057 | -0.041198 | 123.0835 | 122.9507 | 122.9416 | -0.39368 | 123.0423 | 123.0194 | 123.0057 | -0.33875
3294.5781 | 123.1201 | -122.8043 | 0.1831 | -0.22949 | 0.029587 | 0.0052978 | 0.0083227 | -0.0073294 | -0.0031254 | -0.0095063 | -0.19554 | -0.012555 | -0.004971 | -0.0017624 | 0.0019717 | -0.016357 | 0.20142 | 0.22888 | 0.16479 | 0.1831 | 0.3891 | 0.07782 | -0.07782 | 0.14648 | 0.2243 | 0.086975 | 0.3067 | 0.25177 | -0.054932 | -0.091553 | 122.8821 | 122.7264 | 0.20599 | 123.0331 | 122.9874 | 0.26092 | 0.018311 | 122.7493 | 122.7127 | 0.1236 | 122.9507 | 122.8912 | 0.17853 | 0.068665 | 123.1934 | 123.0057 | 122.9691 | -0.26092 | 123.111 | 123.056 | 123.0286 | -0.27466
3296.3438 | 123.111 | -122.8271 | 0.18768 | 0.0070193 | 0.027451 | 0.006366 | 0.0070409 | -0.0098928 | -0.0054752 | -0.0092927 | 0.056228 | -0.014477 | -0.0021938 | -0.0024032 | 0.0013309 | -0.01593 | 0.1236 | 0.11902 | 0.11902 | 0.10986 | 0.3067 | 0.027466 | -0.13275 | 0.11902 | 0.16937 | 0.091553 | 0.23804 | 0.20599 | -0.07782 | -0.11902 | 122.8546 | 122.6944 | 0.11902 | 122.9462 | 122.937 | 0.24261 | -0.064087 | 122.7493 | 122.7081 | 0.050354 | 122.9462 | 122.9187 | 0.21057 | 0.018311 | 123.1338 | 122.9507 | 122.9462 | -0.32043 | 123.0652 | 123.0331 | 122.9965 | -0.3067
3298.1094 | 123.0469 | -122.8363 | 0.20599 | 0.090942 | 0.028092 | 0.0048706 | 0.0053321 | -0.0066884 | -0.0020572 | -0.0090791 | 0.063858 | -0.013196 | -0.007748 | -0.0011216 | 0.0043215 | -0.017425 | 0.10986 | 0.13733 | 0.091553 | 0.082397 | 0.28381 | 0.009155 | -0.16022 | 0.12817 | 0.16479 | 0.07782 | 0.22888 | 0.19226 | -0.064087 | -0.13733 | 122.8455 | 122.6761 | 0.077819 | 122.9736 | 122.9187 | 0.24261 | -0.096131 | 122.7722 | 122.699 | 0.022888 | 122.9645 | 122.9141 | 0.21515 | -0.013733 | 123.1201 | 122.9462 | 122.9279 | -0.36621 | 123.0652 | 123.0286 | 123.0011 | -0.34332
3299.8125 | 123.0469 | -122.8592 | 0.19226 | 0.15198 | 0.027023 | 0.0061524 | 0.0029821 | -0.0056204 | 0.0011472 | -0.0071563 | 0.10963 | -0.012768 | -0.0073208 | -0.0024032 | 0.0064577 | -0.014862 | 0.10071 | 0.14191 | 0.086975 | 0.07782 | 0.21057 | -0.027466 | -0.1831 | 0.15106 | 0.16479 | 0.050354 | 0.16022 | 0.13275 | -0.10986 | -0.16022 | 122.8317 | 122.6761 | 0.01831 | 123.0011 | 122.937 | 0.26092 | -0.091553 | 122.7493 | 122.699 | -0.032044 | 123.0103 | 122.9095 | 0.21057 | -0.05951 | 123.0698 | 122.9599 | 122.9462 | -0.37537 | 123.0194 | 122.9919 | 123.024 | -0.35248
3301.5625 | 123.2025 | -122.7859 | 0.15564 | -0.2066 | 0.031082 | 0.0061524 | 0.0055457 | -0.0083974 | 0.0037106 | -0.0082245 | -0.25658 | -0.011487 | -0.0034756 | -0.0028306 | 0.0060305 | -0.016571 | 0.13733 | 0.10529 | 0.064087 | 0.1236 | 0.39368 | 0.059509 | -0.10529 | 0.09613 | 0.14191 | 0.013733 | 0.28381 | 0.24261 | -0.091553 | -0.11902 | 122.8455 | 122.6807 | 0.23804 | 122.8912 | 122.9095 | 0.22888 | -0.018311 | 122.6944 | 122.6669 | 0.12817 | 122.8821 | 122.7997 | 0.13275 | 0.086975 | 123.1796 | 122.9233 | 122.85 | -0.26093 | 123.0698 | 123.0286 | 122.9279 | -0.27466
3303.2656 | 123.0881 | -122.8455 | 0.19684 | 0.037537 | 0.024033 | 0.0059388 | 0.0055457 | -0.011388 | -0.005048 | -0.0071563 | 0.056228 | -0.014477 | -0.0081754 | -0.00048061 | 0.0038943 | -0.013153 | 0.10986 | 0.15564 | 0.10071 | 0.10986 | 0.30212 | 0.032043 | -0.13733 | 0.13275 | 0.1831 | 0.086975 | 0.23346 | 0.20599 | -0.059509 | -0.10071 | 122.8775 | 122.7081 | 0.10529 | 123.0011 | 122.9553 | 0.24719 | -0.086975 | 122.7859 | 122.7448 | 0.036621 | 122.9782 | 122.9324 | 0.18768 | 0.009156 | 123.1476 | 122.9553 | 122.9462 | -0.33417 | 123.0789 | 123.0515 | 123.0286 | -0.29755
3305.0156 | 123.1293 | -122.8134 | 0.19226 | -0.16846 | 0.028732 | 0.0065796 | 0.0091773 | -0.008611 | -0.0022708 | -0.0084381 | -0.17265 | -0.014264 | -0.0073208 | -0.0026168 | 0.0038943 | -0.016784 | 0.20599 | 0.27008 | 0.19226 | 0.18768 | 0.3479 | 0.07782 | -0.086975 | 0.20142 | 0.27008 | 0.15564 | 0.27008 | 0.23346 | -0.022888 | -0.091553 | 122.8912 | 122.7264 | 0.15564 | 123.0835 | 123.0011 | 0.27466 | 0.013733 | 122.7905 | 122.7219 | 0.07782 | 123.0148 | 122.9691 | 0.24719 | 0.041198 | 123.1613 | 123.0194 | 123.0057 | -0.27924 | 123.0835 | 123.0469 | 123.0835 | -0.28381
3306.7812 | 123.1888 | -122.7905 | 0.16937 | -0.18372 | 0.028519 | 0.0042298 | 0.0049047 | -0.008611 | 0.0028562 | -0.0065155 | -0.26421 | -0.0099911 | -0.004971 | -0.0056076 | 0.0083805 | -0.017425 | 0.12817 | 0.13733 | 0.054932 | 0.10986 | 0.37537 | 0.022888 | -0.14191 | 0.082397 | 0.15106 | -0.004578 | 0.28381 | 0.24719 | -0.082397 | -0.13733 | 122.8134 | 122.6486 | 0.20599 | 122.9279 | 122.9004 | 0.25177 | -0.041199 | 122.7081 | 122.6532 | 0.11444 | 122.8729 | 122.7859 | 0.13275 | 0.077819 | 123.1659 | 122.9187 | 122.8455 | -0.31128 | 123.0743 | 123.0377 | 122.9416 | -0.3067
3308.4844 | 123.0652 | -122.8226 | 0.19684 | 0.19012 | 0.030228 | 0.0055114 | 0.0061865 | -0.0079702 | -0.00013458 | -0.0048065 | 0.17067 | -0.011059 | -0.0071072 | -0.00069421 | 0.0064577 | -0.015289 | 0.09613 | 0.1236 | 0.068665 | 0.07782 | 0.19684 | -0.036621 | -0.20599 | 0.1236 | 0.15564 | 0.032043 | 0.15106 | 0.11444 | -0.14648 | -0.16937 | 122.7859 | 122.6166 | 0 | 122.9462 | 122.9004 | 0.28381 | -0.10071 | 122.6761 | 122.6532 | -0.045776 | 122.9462 | 122.8546 | 0.20142 | -0.082397 | 123.0194 | 122.9187 | 122.8912 | -0.40283 | 122.9736 | 122.937 | 122.9782 | -0.36621
3310.2344 | 123.0515 | -122.8226 | 0.21515 | 0.11383 | 0.026169 | 0.0067932 | 0.0044775 | -0.007543 | -0.0037662 | -0.0097199 | 0.11726 | -0.013409 | -0.0075344 | -0.0013352 | 0.0045351 | -0.013153 | 0.091553 | 0.1236 | 0.082397 | 0.07782 | 0.24261 | -0.018311 | -0.19226 | 0.13733 | 0.15564 | 0.064087 | 0.23346 | 0.1831 | -0.07782 | -0.11902 | 122.8043 | 122.6303 | 0.027466 | 122.9462 | 122.9004 | 0.27008 | -0.1236 | 122.7448 | 122.7036 | 0.01831 | 122.9599 | 122.8867 | 0.18311 | -0.032044 | 123.0652 | 122.9141 | 122.905 | -0.40741 | 123.056 | 123.0057 | 122.9782 | -0.33417
3311.9844 | 123.0515 | -122.8226 | 0.21973 | 0.037537 | 0.02681 | 0.0061524 | 0.0072547 | -0.011388 | -0.004407 | -0.0092927 | 0.063858 | -0.012555 | -0.010312 | -0.0032578 | 0.0049625 | -0.015075 | 0.1236 | 0.13275 | 0.091553 | 0.10071 | 0.28381 | 0.004578 | -0.12817 | 0.13275 | 0.17395 | 0.07782 | 0.2243 | 0.20142 | -0.073242 | -0.11902 | 122.8271 | 122.6944 | 0.064086 | 122.9553 | 122.9233 | 0.22888 | -0.096131 | 122.7493 | 122.7036 | 0.004577 | 122.9553 | 122.9004 | 0.19684 | -0.018311 | 123.1064 | 122.9462 | 122.9141 | -0.3479 | 123.0469 | 123.024 | 122.9965 | -0.33875
3313.6875 | 123.111 | -122.818 | 0.18768 | 0.014648 | 0.026383 | 0.0055114 | 0.0072547 | -0.0088248 | -0.0041934 | -0.0077973 | 0.03334 | -0.012341 | -0.00668 | -0.0024032 | 0.0049625 | -0.016143 | 0.10529 | 0.14191 | 0.1236 | 0.11444 | 0.29755 | 0.022888 | -0.13275 | 0.14191 | 0.1831 | 0.09613 | 0.2243 | 0.19226 | -0.068665 | -0.13733 | 122.8409 | 122.6852 | 0.10986 | 122.9599 | 122.9324 | 0.24719 | -0.082397 | 122.7493 | 122.6807 | 0.036621 | 122.9599 | 122.9141 | 0.23346 | 0.004578 | 123.1155 | 122.9233 | 122.9416 | -0.32043 | 123.0423 | 123.0103 | 123.0011 | -0.32501
3315.4531 | 123.1522 | -122.8226 | 0.17853 | -0.22949 | 0.027878 | 0.0085022 | 0.0087499 | -0.0073294 | 7.902e-05 | -0.010361 | -0.24895 | -0.011914 | -0.00668 | 0.00037379 | 0.0034671 | -0.015503 | 0.13275 | 0.15106 | 0.091553 | 0.11902 | 0.39368 | 0.041199 | -0.1236 | 0.1236 | 0.15106 | 0.036621 | 0.31128 | 0.27466 | -0.059509 | -0.10529 | 122.8638 | 122.699 | 0.21515 | 122.9736 | 122.9416 | 0.24261 | -0.045777 | 122.7631 | 122.7173 | 0.13275 | 122.9462 | 122.8592 | 0.14191 | 0.09613 | 123.2162 | 122.9553 | 122.9141 | -0.30212 | 123.1338 | 123.0972 | 122.9736 | -0.28381
3317.2031 | 123.0789 | -122.8455 | 0.21973 | 0.060425 | 0.03215 | 0.0057252 | 0.0053321 | -0.0079702 | 0.0030698 | -0.0054475 | 0.03334 | -0.0093503 | -0.0062528 | -0.0021896 | 0.0083805 | -0.015289 | 0.004578 | -0.041199 | -0.068665 | -0.022888 | 0.27466 | -0.068665 | -0.23346 | 0.022888 | -0.004578 | -0.10529 | 0.17853 | 0.13733 | -0.16022 | -0.20142 | 122.7768 | 122.612 | 0.054931 | 122.8043 | 122.8226 | 0.21057 | -0.21515 | 122.6852 | 122.644 | -0.041199 | 122.8683 | 122.7402 | 0.09613 | -0.082398 | 123.1201 | 122.85 | 122.7768 | -0.45319 | 123.024 | 122.9828 | 122.8409 | -0.42114
3318.9688 | 123.0469 | -122.8409 | 0.19684 | 0.15198 | 0.028305 | 0.0085022 | 0.0057593 | -0.008611 | -0.0037662 | -0.0058747 | 0.13252 | -0.012127 | -0.008389 | -0.0028306 | 0.0049625 | -0.014648 | 0.091553 | 0.16022 | 0.10071 | 0.068665 | 0.21515 | -0.041199 | -0.18768 | 0.14648 | 0.15564 | 0.059509 | 0.16937 | 0.1236 | -0.10529 | -0.15564 | 122.7997 | 122.6532 | 0.018311 | 123.0011 | 122.9095 | 0.25635 | -0.10529 | 122.7356 | 122.6852 | -0.027465 | 122.9874 | 122.9004 | 0.21515 | -0.073242 | 123.056 | 122.9324 | 122.9416 | -0.38452 | 123.0103 | 122.9645 | 122.9965 | -0.35248
3320.6562 | 123.1247 | -122.7859 | 0.16479 | -0.25238 | 0.028519 | 0.0050842 | 0.0087499 | -0.0079702 | -0.0020572 | -0.0056611 | -0.21843 | -0.011914 | -0.0039028 | -0.0028306 | 0.0021853 | -0.01593 | 0.19684 | 0.20599 | 0.17395 | 0.1831 | 0.37537 | 0.059509 | -0.086975 | 0.14191 | 0.20142 | 0.064087 | 0.31128 | 0.26093 | -0.059509 | -0.10071 | 122.8455 | 122.699 | 0.21057 | 122.9919 | 122.9691 | 0.27008 | 0.032043 | 122.7264 | 122.6852 | 0.14648 | 122.9279 | 122.85 | 0.1648 | 0.09613 | 123.1613 | 122.9828 | 122.9599 | -0.25177 | 123.0972 | 123.0469 | 122.9874 | -0.2655
3322.4062 | 123.1476 | -122.8271 | 0.18768 | -0.11505 | 0.033218 | 0.0035888 | 0.0074683 | -0.005834 | 0.0039242 | -0.0077973 | -0.18028 | -0.010846 | -0.0039028 | -0.001976 | 0.0077395 | -0.018066 | 0.13275 | 0.1236 | 0.073242 | 0.086975 | 0.3067 | -0.009155 | -0.18768 | 0.10986 | 0.13275 | -0.018311 | 0.22888 | 0.19684 | -0.11444 | -0.16937 | 122.818 | 122.6395 | 0.11902 | 122.9507 | 122.9141 | 0.27466 | -0.054932 | 122.7127 | 122.6578 | 0.041199 | 122.937 | 122.8088 | 0.15106 | 0.009155 | 123.1338 | 122.9599 | 122.9004 | -0.37537 | 123.056 | 123.024 | 122.9599 | -0.35706
3324.1719 | 123.1522 | -122.8363 | 0.16937 | -0.19897 | 0.027237 | 0.0050842 | 0.0083227 | -0.0056204 | -0.004407 | -0.0075837 | -0.15739 | -0.012341 | -0.0062528 | -0.0021896 | 0.0017581 | -0.014648 | 0.16937 | 0.27466 | 0.21515 | 0.20599 | 0.33417 | 0.07782 | -0.086975 | 0.19684 | 0.29297 | 0.14191 | 0.26093 | 0.21973 | -0.022888 | -0.086975 | 122.9141 | 122.7493 | 0.16479 | 123.111 | 123.0423 | 0.29297 | 0 | 122.8134 | 122.7493 | 0.091552 | 123.0331 | 122.9782 | 0.22888 | 0.050354 | 123.1705 | 123.0057 | 123.0515 | -0.25635 | 123.0972 | 123.056 | 123.1293 | -0.25635
3325.9219 | 123.1064 | -122.8317 | 0.19684 | 0.12146 | 0.034287 | 0.002948 | 0.0059729 | -0.0094656 | 0.0024288 | -0.0067291 | 0.056228 | -0.0099911 | -0.0045438 | 0.001442 | 0.0075259 | -0.014862 | 0.004578 | -0.027466 | -0.064087 | -0.022888 | 0.25177 | -0.086975 | -0.23804 | 0.036621 | 0.022888 | -0.064087 | 0.21515 | 0.16479 | -0.15564 | -0.17853 | 122.7448 | 122.5937 | 0.054932 | 122.8043 | 122.8088 | 0.21515 | -0.19226 | 122.6761 | 122.6532 | 0.018311 | 122.8683 | 122.7676 | 0.11444 | -0.032043 | 123.0835 | 122.8363 | 122.7676 | -0.43488 | 123.0469 | 122.9965 | 122.8546 | -0.37537
3327.625 | 123.1659 | -122.818 | 0.17853 | -0.22949 | 0.031937 | 0.0057252 | 0.0091773 | -0.0077566 | -0.00034818 | -0.0077973 | -0.24895 | -0.013196 | -0.0058254 | -0.0038986 | 0.0047489 | -0.014435 | 0.12817 | 0.15106 | 0.082397 | 0.1236 | 0.39825 | 0.054932 | -0.11444 | 0.10986 | 0.16022 | 0.036621 | 0.30212 | 0.27008 | -0.073242 | -0.11902 | 122.8729 | 122.7036 | 0.21973 | 122.9691 | 122.9416 | 0.23804 | -0.050354 | 122.7448 | 122.699 | 0.1236 | 122.9279 | 122.8546 | 0.15564 | 0.091553 | 123.2162 | 122.9462 | 122.9004 | -0.29297 | 123.1201 | 123.0881 | 122.9782 | -0.29755
3329.3906 | 123.1155 | -122.8455 | 0.20142 | 0.17487 | 0.031082 | 0.0052978 | 0.0021277 | -0.008611 | 0.00029262 | -0.0065155 | 0.11726 | -0.012768 | -0.0068936 | -0.0021896 | 0.0056033 | -0.015503 | 0.022888 | 0.054932 | 0.004578 | 0.022888 | 0.23346 | -0.054932 | -0.22888 | 0.10986 | 0.13733 | 0.032043 | 0.15564 | 0.13733 | -0.1236 | -0.17395 | 122.7905 | 122.6166 | 0.032043 | 122.9004 | 122.8683 | 0.25177 | -0.17853 | 122.7219 | 122.6715 | -0.045776 | 122.9553 | 122.8775 | 0.20599 | -0.064087 | 123.0789 | 122.8683 | 122.85 | -0.4303 | 123.0011 | 122.9828 | 122.9828 | -0.37537
3331.1406 | 123.111 | -122.8317 | 0.20142 | -0.069275 | 0.032578 | 0.0044434 | 0.0096045 | -0.0096792 | 0.0030698 | -0.0063019 | -0.13451 | -0.0093503 | -0.0068936 | -0.0024032 | 0.0068851 | -0.01593 | 0.11444 | 0.1236 | 0.050354 | 0.07782 | 0.29755 | -0.027466 | -0.18768 | 0.09613 | 0.12817 | -0.013733 | 0.2243 | 0.18768 | -0.10529 | -0.17395 | 122.8043 | 122.644 | 0.09613 | 122.9553 | 122.9095 | 0.2655 | -0.086975 | 122.7264 | 122.6578 | 0.022888 | 122.9279 | 122.818 | 0.16022 | -0.013733 | 123.1293 | 122.9462 | 122.8821 | -0.3891 | 123.056 | 123.0194 | 122.9599 | -0.37537
3332.8906 | 123.056 | -122.8683 | 0.21057 | -0.031128 | 0.030869 | 0.0055114 | 0.0034093 | -0.0077566 | 0.0028562 | -0.0065155 | -0.027695 | -0.0076413 | -0.0058254 | 0.00080099 | 0.0064577 | -0.01358 | 0.073242 | 0.082397 | 0.004578 | 0.054932 | 0.3067 | -0.041199 | -0.19684 | 0.032043 | 0.068665 | -0.068665 | 0.21515 | 0.16479 | -0.13733 | -0.18768 | 122.8271 | 122.6715 | 0.096131 | 122.9507 | 122.9233 | 0.25177 | -0.13733 | 122.731 | 122.6807 | 0.004578 | 122.9004 | 122.7997 | 0.11902 | -0.045776 | 123.175 | 122.9416 | 122.8729 | -0.40741 | 123.0835 | 123.0331 | 122.937 | -0.39825
3334.5938 | 123.0515 | -122.8821 | 0.21515 | 0.060425 | 0.025101 | 0.0055114 | 0.0068273 | -0.0066884 | -0.0052616 | -0.0084381 | 0.102 | -0.012127 | -0.0073208 | -0.0034714 | -0.00059167 | -0.0099484 | 0.068665 | 0.14191 | 0.10071 | 0.09613 | 0.28381 | 0.013733 | -0.15106 | 0.11902 | 0.1831 | 0.086975 | 0.22888 | 0.19226 | -0.054932 | -0.11902 | 122.8958 | 122.731 | 0.068664 | 123.024 | 122.9782 | 0.24719 | -0.14648 | 122.8271 | 122.7631 | 0.013733 | 123.0011 | 122.9691 | 0.20599 | -0.022888 | 123.1659 | 122.9507 | 122.9828 | -0.36621 | 123.111 | 123.0743 | 123.0652 | -0.33417
3336.3438 | 123.0698 | -122.8455 | 0.21973 | 0.037537 | 0.031937 | 0.0055114 | 0.0053321 | -0.010106 | 0.0043514 | -0.0063019 | 0.086746 | -0.0080685 | -0.0075344 | -0.00090781 | 0.0079531 | -0.013794 | -0.009155 | -0.050354 | -0.068665 | -0.009155 | 0.28381 | -0.073242 | -0.24719 | -0.004578 | -0.009155 | -0.091553 | 0.19684 | 0.14648 | -0.16479 | -0.21057 | 122.7722 | 122.5983 | 0.064086 | 122.7951 | 122.8363 | 0.23804 | -0.22888 | 122.6807 | 122.6349 | -0.022889 | 122.8409 | 122.7539 | 0.11902 | -0.073243 | 123.1293 | 122.8363 | 122.7768 | -0.46692 | 123.0423 | 122.9919 | 122.8363 | -0.4303
3338.0938 | 123.0515 | -122.8775 | 0.21973 | -0.023499 | 0.035141 | 0.0035888 | 0.0034093 | -0.0081838 | 0.0030698 | -0.0058747 | -0.042954 | -0.0117 | -0.004971 | -0.0034714 | 0.0079531 | -0.015075 | 0.059509 | 0.064087 | 0.004578 | 0.027466 | 0.31128 | -0.068665 | -0.20599 | 0.013733 | 0.050354 | -0.082397 | 0.21515 | 0.1831 | -0.14648 | -0.20599 | 122.8088 | 122.6715 | 0.091552 | 122.9416 | 122.905 | 0.23346 | -0.16022 | 122.731 | 122.6715 | -0.004578 | 122.8912 | 122.7951 | 0.1236 | -0.036622 | 123.1888 | 122.937 | 122.8821 | -0.42572 | 123.0927 | 123.0606 | 122.9279 | -0.42572
3339.7969 | 123.0331 | -122.818 | 0.21057 | 0.12146 | 0.028519 | 0.004657 | 0.0027685 | -0.0090384 | -0.0054752 | -0.0090791 | 0.18593 | -0.012555 | -0.0075344 | -0.0021896 | 0.0030399 | -0.015075 | 0.068665 | 0.13733 | 0.086975 | 0.073242 | 0.24261 | -0.032043 | -0.18768 | 0.12817 | 0.16022 | 0.086975 | 0.18768 | 0.16937 | -0.082397 | -0.13275 | 122.7859 | 122.6303 | 0.032044 | 122.9553 | 122.8912 | 0.26092 | -0.14191 | 122.7356 | 122.6852 | -0.022888 | 122.9462 | 122.905 | 0.21973 | -0.041198 | 123.0606 | 122.8867 | 122.905 | -0.39825 | 123.0057 | 122.9874 | 122.9782 | -0.34332
3341.5625 | 123.0331 | -122.8455 | 0.21515 | 0.098572 | 0.0298 | 0.0082886 | 0.0087499 | -0.0094656 | -0.0024844 | -0.0086517 | 0.20119 | -0.013623 | -0.0081754 | -0.0030442 | 0.0021853 | -0.013153 | 0.091553 | 0.12817 | 0.091553 | 0.07782 | 0.25177 | -0.018311 | -0.17853 | 0.11444 | 0.14191 | 0.064087 | 0.18768 | 0.15564 | -0.09613 | -0.16479 | 122.8271 | 122.6669 | 0.036621 | 122.9736 | 122.9233 | 0.25635 | -0.1236 | 122.7493 | 122.6807 | -0.027466 | 122.9599 | 122.9095 | 0.22888 | -0.059509 | 123.0972 | 122.937 | 122.937 | -0.39368 | 123.0331 | 123.0011 | 122.9874 | -0.37994
3343.25 | 123.0698 | -122.8271 | 0.19226 | -0.031128 | 0.027023 | 0.0065796 | 0.0072547 | -0.010747 | -0.0073978 | -0.0088653 | 0.102 | -0.013409 | -0.0071072 | -0.0045394 | 0.0045351 | -0.013794 | 0.10529 | 0.12817 | 0.10529 | 0.091553 | 0.29297 | 0.022888 | -0.14648 | 0.11444 | 0.17395 | 0.10071 | 0.23804 | 0.21973 | -0.091553 | -0.11902 | 122.85 | 122.6807 | 0.10071 | 122.9553 | 122.9187 | 0.23804 | -0.086975 | 122.7356 | 122.7081 | 0.045776 | 122.9416 | 122.9279 | 0.21973 | 0.027466 | 123.1201 | 122.9324 | 122.9324 | -0.33874 | 123.0652 | 123.0469 | 123.0011 | -0.31128
3345 | 123.0469 | -122.8546 | 0.19684 | 0.075684 | 0.026596 | 0.0052978 | 0.0055457 | -0.0094656 | -0.004407 | -0.011429 | 0.086746 | -0.012341 | -0.0096706 | -0.0017624 | 0.0028263 | -0.015289 | 0.11444 | 0.10071 | 0.10529 | 0.07782 | 0.27924 | 0.018311 | -0.14191 | 0.14191 | 0.15106 | 0.091553 | 0.23804 | 0.18768 | -0.064087 | -0.1236 | 122.8729 | 122.7127 | 0.082398 | 122.9553 | 122.9324 | 0.21973 | -0.082397 | 122.7905 | 122.731 | 0.041199 | 122.9965 | 122.9462 | 0.21515 | -0.009155 | 123.1338 | 122.9691 | 122.9599 | -0.33875 | 123.0927 | 123.0423 | 123.0057 | -0.32043
3346.75 | 123.0377 | -122.818 | 0.19684 | 0.17487 | 0.032578 | 0.0059388 | 0.0025549 | -0.0071158 | 7.902e-05 | -0.0088653 | 0.14778 | -0.014477 | -0.0064664 | -0.0030442 | 0.0070987 | -0.015503 | 0.10071 | 0.1236 | 0.073242 | 0.059509 | 0.21515 | -0.059509 | -0.19226 | 0.13733 | 0.15106 | 0.050354 | 0.16022 | 0.11444 | -0.10986 | -0.17395 | 122.7585 | 122.6257 | 0.018311 | 122.9416 | 122.8775 | 0.25177 | -0.09613 | 122.7081 | 122.644 | -0.036621 | 122.9553 | 122.8683 | 0.2243 | -0.082397 | 123.0331 | 122.9187 | 122.8912 | -0.3891 | 122.9782 | 122.9324 | 122.9691 | -0.37079
3348.5156 | 123.1613 | -122.8134 | 0.16479 | -0.14557 | 0.028305 | 0.007434 | 0.010459 | -0.0096792 | -0.0041934 | -0.0095063 | -0.14977 | -0.013836 | -0.0073208 | -0.0021896 | 0.0019717 | -0.016784 | 0.25635 | 0.29755 | 0.25635 | 0.21057 | 0.3479 | 0.07782 | -0.086975 | 0.22888 | 0.30212 | 0.16479 | 0.25177 | 0.2243 | -0.013733 | -0.07782 | 122.8912 | 122.7264 | 0.1831 | 123.111 | 123.024 | 0.29755 | 0.091553 | 122.7997 | 122.7356 | 0.086975 | 123.0423 | 122.9782 | 0.24261 | 0.059509 | 123.1613 | 123.0698 | 123.0698 | -0.25177 | 123.0652 | 123.0377 | 123.1155 | -0.24261
3350.2344 | 123.1201 | -122.8317 | 0.17395 | -0.24475 | 0.028946 | 0.0061524 | 0.0076819 | -0.007543 | -0.0012028 | -0.010574 | -0.25658 | -0.010632 | -0.0045438 | -0.0026168 | -0.00059167 | -0.014862 | 0.2243 | 0.2243 | 0.16937 | 0.17395 | 0.37079 | 0.082397 | -0.091553 | 0.15564 | 0.20142 | 0.068665 | 0.30212 | 0.2655 | -0.045776 | -0.10071 | 122.9141 | 122.7402 | 0.19684 | 123.056 | 123.0057 | 0.2655 | 0.050354 | 122.7859 | 122.731 | 0.12817 | 122.9874 | 122.9004 | 0.16937 | 0.091553 | 123.2025 | 123.056 | 123.0011 | -0.2655 | 123.1339 | 123.0972 | 123.0331 | -0.27466
3351.9844 | 123.0972 | -122.7859 | 0.20142 | 0.16724 | 0.028946 | 0.0082886 | 0.0051183 | -0.0069022 | 0.00093342 | -0.0071563 | 0.14778 | -0.012341 | -0.0051846 | -0.0030442 | 0.0066715 | -0.016143 | 0.13275 | 0.11902 | 0.054932 | 0.082397 | 0.22888 | -0.022888 | -0.19226 | 0.1236 | 0.12817 | 0.018311 | 0.14191 | 0.11444 | -0.12817 | -0.16937 | 122.7631 | 122.5937 | 0.027466 | 122.905 | 122.8683 | 0.27466 | -0.068665 | 122.6578 | 122.6166 | -0.059509 | 122.9095 | 122.8043 | 0.18768 | -0.086975 | 123.0148 | 122.9187 | 122.8409 | -0.39368 | 122.9279 | 122.9004 | 122.9141 | -0.37079
3353.7344 | 123.0652 | -122.8271 | 0.21057 | -0.038757 | 0.034073 | 0.0065796 | 0.0076819 | -0.0083974 | 0.0039242 | -0.0063019 | -0.11162 | -0.012341 | -0.0053982 | -0.00048061 | 0.0096621 | -0.018066 | 0.13275 | 0.086975 | 0.032043 | 0.064087 | 0.31586 | -0.032043 | -0.20142 | 0.064087 | 0.082397 | -0.091553 | 0.21973 | 0.1831 | -0.13733 | -0.18768 | 122.7951 | 122.6257 | 0.10529 | 122.9141 | 122.8912 | 0.2655 | -0.07782 | 122.6898 | 122.6395 | 0.009156 | 122.8912 | 122.7356 | 0.09613 | -0.027466 | 123.143 | 122.9599 | 122.8592 | -0.41199 | 123.0469 | 123.0103 | 122.9095 | -0.39825
3355.5 | 123.056 | -122.8363 | 0.20142 | 0.052795 | 0.027451 | 0.0055114 | 0.0072547 | -0.0094656 | -0.0054752 | -0.0075837 | 0.079117 | -0.013836 | -0.0081754 | -0.0038986 | 0.0036807 | -0.015075 | 0.10071 | 0.14191 | 0.10071 | 0.073242 | 0.27008 | 0.004578 | -0.16479 | 0.1236 | 0.17395 | 0.068665 | 0.20142 | 0.19684 | -0.07782 | -0.12817 | 122.8409 | 122.6715 | 0.068665 | 122.9782 | 122.9095 | 0.23804 | -0.10071 | 122.7585 | 122.7081 | 0 | 122.9599 | 122.905 | 0.19684 | -0.004578 | 123.1064 | 122.937 | 122.937 | -0.36621 | 123.0377 | 123.0331 | 123.0103 | -0.32959
3357.25 | 123.1064 | -122.8455 | 0.17853 | 0.14435 | 0.030014 | 0.0040162 | 0.0049047 | -0.0090384 | 0.00093342 | -0.0069427 | 0.15541 | -0.013836 | -0.008389 | -0.0045394 | 0.0068851 | -0.016784 | 0.10071 | 0.10986 | 0.07782 | 0.073242 | 0.21515 | -0.032043 | -0.21515 | 0.1236 | 0.12817 | 0.027466 | 0.14648 | 0.1236 | -0.12817 | -0.16937 | 122.8134 | 122.6303 | 0.036621 | 122.9553 | 122.9187 | 0.28839 | -0.07782 | 122.7173 | 122.6761 | -0.032044 | 122.9691 | 122.8729 | 0.19684 | -0.054932 | 123.0606 | 122.9462 | 122.9233 | -0.39368 | 122.9919 | 122.9691 | 122.9736 | -0.3479
3359 | 123.1155 | -122.7951 | 0.18768 | -0.0082397 | 0.024887 | 0.0065796 | 0.0057593 | -0.0079702 | -0.005048 | -0.0097199 | 0.056228 | -0.011487 | -0.0098844 | -0.00069421 | 0.0041079 | -0.012512 | 0.10071 | 0.14648 | 0.10986 | 0.10529 | 0.31586 | 0.013733 | -0.13733 | 0.12817 | 0.1831 | 0.068665 | 0.23804 | 0.20599 | -0.059509 | -0.11444 | 122.8088 | 122.6578 | 0.12817 | 122.9416 | 122.9004 | 0.24262 | -0.086975 | 122.7356 | 122.6807 | 0.050354 | 122.9233 | 122.8638 | 0.18311 | 0.018311 | 123.111 | 122.8958 | 122.905 | -0.32501 | 123.0331 | 123.0011 | 122.9782 | -0.30212
3360.6875 | 123.1338 | -122.818 | 0.17395 | -0.21423 | 0.02916 | 0.002948 | 0.011314 | -0.0066884 | -0.0020572 | -0.0086517 | -0.23369 | -0.0117 | -0.00668 | -0.0015488 | 0.0013309 | -0.016357 | 0.19684 | 0.20142 | 0.15106 | 0.18768 | 0.39825 | 0.073242 | -0.10529 | 0.13275 | 0.17395 | 0.054932 | 0.31586 | 0.27008 | -0.054932 | -0.086975 | 122.8912 | 122.7127 | 0.2243 | 123.0194 | 123.0057 | 0.29297 | 0.022888 | 122.7631 | 122.731 | 0.14191 | 122.9507 | 122.8729 | 0.14191 | 0.096131 | 123.2162 | 123.0148 | 122.9691 | -0.27924 | 123.1338 | 123.0881 | 122.9919 | -0.26092
3362.4531 | 123.1384 | -122.8134 | 0.19226 | -0.0082397 | 0.028092 | 0.0070068 | 0.0081091 | -0.010106 | -0.003339 | -0.0077973 | 0.025711 | -0.01405 | -0.006039 | -0.00048061 | 0.0011173 | -0.015503 | 0.10071 | 0.14191 | 0.11444 | 0.10986 | 0.31128 | 0.054932 | -0.14648 | 0.15106 | 0.19226 | 0.10986 | 0.23804 | 0.1831 | -0.059509 | -0.11902 | 122.8683 | 122.6669 | 0.11902 | 122.9553 | 122.9233 | 0.25635 | -0.091553 | 122.7539 | 122.6944 | 0.045776 | 122.9645 | 122.9233 | 0.22888 | -0.009156 | 123.1247 | 122.9141 | 122.9279 | -0.33874 | 123.0515 | 122.9965 | 123.0057 | -0.31128
3364.1562 | 123.1888 | -122.7905 | 0.16937 | -0.19135 | 0.031937 | 0.0040162 | 0.0072547 | -0.0077566 | 0.0043514 | -0.0082245 | -0.2108 | -0.011273 | -0.0058254 | -0.0021896 | 0.0062441 | -0.019775 | 0.14648 | 0.11902 | 0.064087 | 0.11444 | 0.37994 | 0.022888 | -0.14191 | 0.09613 | 0.1236 | -0.009155 | 0.25177 | 0.21057 | -0.10071 | -0.14648 | 122.8134 | 122.6486 | 0.21057 | 122.9095 | 122.905 | 0.25635 | -0.022889 | 122.6898 | 122.644 | 0.082397 | 122.8867 | 122.7814 | 0.13733 | 0.041198 | 123.1705 | 122.937 | 122.8546 | -0.31128 | 123.0423 | 123.0011 | 122.9141 | -0.31586
3365.9062 | 123.1979 | -122.8043 | 0.16479 | -0.069275 | 0.027023 | 0.004657 | 0.0072547 | -0.0081838 | -0.006116 | -0.0067291 | -0.065842 | -0.012768 | -0.0062528 | -0.0026168 | 0.0034671 | -0.01593 | 0.19226 | 0.25635 | 0.20142 | 0.1831 | 0.33875 | 0.064087 | -0.09613 | 0.21973 | 0.27466 | 0.16937 | 0.23804 | 0.23346 | -0.018311 | -0.082397 | 122.8683 | 122.7081 | 0.17395 | 123.0606 | 122.9874 | 0.27924 | 0.027466 | 122.7859 | 122.7219 | 0.073242 | 123.024 | 122.9736 | 0.25177 | 0.068664 | 123.143 | 122.9965 | 123.0057 | -0.26092 | 123.0423 | 123.0377 | 123.0789 | -0.24719
3367.6562 | 123.0881 | -122.8683 | 0.21973 | 0.11383 | 0.032578 | 0.0050842 | 0.0053321 | -0.010106 | 0.0037106 | -0.0069427 | 0.094375 | -0.012555 | -0.0043302 | 0.00080099 | 0.0075259 | -0.016998 | 0.027466 | -0.032043 | -0.07782 | -0.013733 | 0.25635 | -0.073242 | -0.23804 | 0.027466 | 0.009155 | -0.09613 | 0.20142 | 0.15106 | -0.16022 | -0.20142 | 122.7951 | 122.6303 | 0.036621 | 122.8363 | 122.8546 | 0.2243 | -0.19226 | 122.7081 | 122.6669 | -0.018311 | 122.8958 | 122.7722 | 0.10529 | -0.068665 | 123.1247 | 122.8958 | 122.7905 | -0.45776 | 123.0698 | 123.0194 | 122.8775 | -0.42114
3369.3594 | 123.1522 | -122.7997 | 0.18768 | -0.10742 | 0.033646 | 0.0057252 | 0.0068273 | -0.0088248 | 0.0022152 | -0.0052337 | -0.15739 | -0.010632 | -0.0071072 | -0.0024032 | 0.0077395 | -0.016998 | 0.12817 | 0.13275 | 0.036621 | 0.091553 | 0.32044 | 0.009155 | -0.18768 | 0.10529 | 0.14648 | -0.032043 | 0.24261 | 0.19684 | -0.13733 | -0.16937 | 122.8088 | 122.612 | 0.13275 | 122.9324 | 122.8912 | 0.27924 | -0.059509 | 122.6624 | 122.6303 | 0.054932 | 122.905 | 122.7676 | 0.13733 | 0.009155 | 123.1201 | 122.9279 | 122.8363 | -0.37537 | 123.0423 | 122.9965 | 122.9462 | -0.35706
3371.1094 | 123.0881 | -122.85 | 0.1831 | 0.0070193 | 0.025955 | 0.0055114 | 0.0070409 | -0.010534 | -0.0054752 | -0.0086517 | 0.079117 | -0.012127 | -0.0051846 | -0.0026168 | 0.0013309 | -0.014648 | 0.082397 | 0.13733 | 0.11902 | 0.10529 | 0.29297 | 0.018311 | -0.13275 | 0.11902 | 0.1831 | 0.10071 | 0.23804 | 0.19684 | -0.045776 | -0.10986 | 122.8683 | 122.7173 | 0.10986 | 122.9874 | 122.9553 | 0.23804 | -0.10071 | 122.8043 | 122.7402 | 0.054932 | 122.9691 | 122.9507 | 0.21057 | 0.013733 | 123.143 | 122.9324 | 122.9691 | -0.31586 | 123.0881 | 123.0469 | 123.0331 | -0.29297
3372.8281 | 123.0743 | -122.85 | 0.21057 | 0.060425 | 0.032791 | 0.0048706 | 0.0040503 | -0.0094656 | 0.0056332 | -0.0060883 | 0.03334 | -0.0082821 | -0.0041164 | -5.3406e-05 | 0.0090213 | -0.016998 | 0.022888 | -0.036621 | -0.073242 | -0.004578 | 0.27924 | -0.068665 | -0.23346 | 0.009155 | 0.004578 | -0.09613 | 0.20142 | 0.16479 | -0.15106 | -0.20142 | 122.7814 | 122.6166 | 0.068665 | 122.8134 | 122.8455 | 0.22888 | -0.18768 | 122.699 | 122.6486 | -0.009155 | 122.8592 | 122.7539 | 0.10529 | -0.045776 | 123.1293 | 122.8729 | 122.7768 | -0.44403 | 123.0515 | 123.0148 | 122.8546 | -0.41199
3374.5938 | 123.0606 | -122.8455 | 0.19684 | 0.13672 | 0.030869 | 0.0040162 | 0.0053321 | -0.008611 | 0.0020016 | -0.0054475 | 0.079117 | -0.0076413 | -0.0053982 | 0.00058739 | 0.0077395 | -0.014648 | 0.009155 | -0.022888 | -0.082397 | -0.009155 | 0.27008 | -0.064087 | -0.23804 | 0.004578 | 0.004578 | -0.11444 | 0.1831 | 0.17395 | -0.16022 | -0.20142 | 122.7814 | 122.6074 | 0.073243 | 122.8226 | 122.8363 | 0.22888 | -0.18768 | 122.6852 | 122.644 | -0.013733 | 122.85 | 122.731 | 0.086975 | -0.022888 | 123.1155 | 122.8546 | 122.7631 | -0.43488 | 123.0286 | 123.0194 | 122.85 | -0.39825
3376.3438 | 123.1338 | -122.818 | 0.17853 | -0.26764 | 0.030014 | 0.0052978 | 0.010245 | -0.0069022 | -0.006116 | -0.0052337 | -0.16502 | -0.012982 | -0.0045438 | -0.00026701 | 0.00068993 | -0.01358 | 0.14648 | 0.21515 | 0.14648 | 0.1831 | 0.3891 | 0.068665 | -0.10071 | 0.11444 | 0.20142 | 0.064087 | 0.29297 | 0.2655 | -0.050354 | -0.091553 | 122.8867 | 122.7173 | 0.21057 | 123.0331 | 123.0011 | 0.28381 | -0.032044 | 122.7676 | 122.7264 | 0.11444 | 122.9324 | 122.8821 | 0.15564 | 0.086975 | 123.2071 | 122.9645 | 122.9645 | -0.27924 | 123.111 | 123.0835 | 123.0194 | -0.27008
3378.0938 | 123.1384 | -122.8088 | 0.17853 | -0.031128 | 0.02681 | 0.0076478 | 0.0076819 | -0.0079702 | -0.0048344 | -0.0067291 | 0.04097 | -0.013409 | -0.0053982 | -0.001976 | 0.0019717 | -0.015503 | 0.10529 | 0.13733 | 0.11444 | 0.11902 | 0.31128 | 0.018311 | -0.13275 | 0.14191 | 0.19684 | 0.1236 | 0.21973 | 0.20599 | -0.059509 | -0.11902 | 122.8271 | 122.6761 | 0.13275 | 122.9462 | 122.9279 | 0.25177 | -0.073242 | 122.7493 | 122.6898 | 0.041199 | 122.9507 | 122.9324 | 0.24261 | 0.027466 | 123.1201 | 122.9141 | 122.9233 | -0.31128 | 123.0286 | 123.0148 | 123.0057 | -0.29755
3379.7969 | 123.1979 | -122.7905 | 0.1831 | -0.23712 | 0.032578 | 0.0070068 | 0.0049047 | -0.0069022 | -0.0012028 | -0.0071563 | -0.23369 | -0.011273 | -0.0073208 | -0.0032578 | 0.0036807 | -0.018493 | 0.16479 | 0.1236 | 0.064087 | 0.12817 | 0.41657 | 0.036621 | -0.09613 | 0.09613 | 0.13733 | 0.004578 | 0.29297 | 0.27008 | -0.073242 | -0.13733 | 122.8271 | 122.6944 | 0.23346 | 122.9141 | 122.9187 | 0.2243 | -0.01831 | 122.7173 | 122.6532 | 0.10986 | 122.8867 | 122.7951 | 0.14191 | 0.086976 | 123.2071 | 122.9553 | 122.8546 | -0.27924 | 123.0835 | 123.0606 | 122.9279 | -0.32043
3381.5469 | 123.0606 | -122.8775 | 0.20142 | 0.022278 | 0.032791 | 0.0031616 | 0.0046911 | -0.011175 | 0.004565 | -0.0073701 | 0.04097 | -0.010205 | -0.0045438 | 0.00037379 | 0.0092349 | -0.016784 | 0.013733 | -0.027466 | -0.07782 | -0.009155 | 0.27466 | -0.073242 | -0.22888 | 0.009155 | 0.004578 | -0.10529 | 0.21057 | 0.16022 | -0.16937 | -0.21973 | 122.8043 | 122.6486 | 0.073242 | 122.85 | 122.8683 | 0.21973 | -0.18768 | 122.7081 | 122.6578 | 0.009155 | 122.8867 | 122.7722 | 0.11444 | -0.041199 | 123.1522 | 122.8912 | 122.7997 | -0.4303 | 123.0881 | 123.0377 | 122.8821 | -0.42114
3383.2344 | 123.1247 | -122.8592 | 0.17395 | -0.00061023 | 0.028092 | 0.008075 | 0.0072547 | -0.0098928 | -0.0071842 | -0.0073701 | 0.056228 | -0.016614 | -0.0075344 | -0.0032578 | 0.0021853 | -0.012512 | 0.07782 | 0.14191 | 0.11444 | 0.10986 | 0.31128 | 0.032043 | -0.12817 | 0.13275 | 0.18768 | 0.09613 | 0.23346 | 0.19684 | -0.073242 | -0.12817 | 122.8912 | 122.731 | 0.13733 | 123.0011 | 122.9691 | 0.23804 | -0.09613 | 122.7859 | 122.731 | 0.059509 | 122.9919 | 122.9553 | 0.2243 | 0.022888 | 123.1705 | 122.937 | 122.9736 | -0.30212 | 123.0927 | 123.056 | 123.0469 | -0.30212
3385 | 123.0606 | -122.8546 | 0.20142 | -0.046387 | 0.032791 | 0.0038024 | 0.0083227 | -0.0064748 | 0.005206 | -0.0080109 | -0.08873 | -0.0089229 | -0.0034756 | -0.0015488 | 0.0062441 | -0.017425 | 0.13275 | 0.091553 | 0.032043 | 0.073242 | 0.30212 | -0.027466 | -0.1831 | 0.068665 | 0.07782 | -0.068665 | 0.21515 | 0.1831 | -0.14191 | -0.18768 | 122.8271 | 122.6715 | 0.10071 | 122.9462 | 122.9279 | 0.25635 | -0.068665 | 122.7127 | 122.6669 | 0.013733 | 122.9233 | 122.7859 | 0.11902 | -0.018311 | 123.1567 | 122.9874 | 122.8867 | -0.38452 | 123.0698 | 123.0377 | 122.9324 | -0.3891
3386.75 | 123.175 | -122.8226 | 0.1831 | -0.12268 | 0.030869 | 0.0052978 | 0.0070409 | -0.0088248 | -0.0035526 | -0.0084381 | -0.11925 | -0.014264 | -0.0068936 | -0.0030442 | 0.0026125 | -0.013794 | 0.21057 | 0.28381 | 0.21973 | 0.19684 | 0.33417 | 0.07782 | -0.086975 | 0.2243 | 0.3067 | 0.17395 | 0.25635 | 0.2243 | -0.027466 | -0.082397 | 122.9004 | 122.7356 | 0.15106 | 123.1064 | 123.0194 | 0.28381 | 0.027466 | 122.7951 | 122.7402 | 0.073243 | 123.0469 | 122.9965 | 0.25635 | 0.041199 | 123.1567 | 123.0331 | 123.0423 | -0.27008 | 123.0789 | 123.0469 | 123.1293 | -0.2655
3388.4531 | 123.1705 | -122.8088 | 0.17853 | -0.12268 | 0.032578 | 0.0070068 | 0.0064001 | -0.0098928 | 0.00093342 | -0.0084381 | -0.20317 | -0.0097775 | -0.007748 | -0.0013352 | 0.0083805 | -0.014648 | 0.11444 | 0.1236 | 0.050354 | 0.091553 | 0.31586 | -0.027466 | -0.19226 | 0.09613 | 0.1236 | 0.009155 | 0.2243 | 0.1831 | -0.13275 | -0.16937 | 122.7814 | 122.6166 | 0.13733 | 122.9324 | 122.9004 | 0.28381 | -0.064087 | 122.6761 | 122.6395 | 0.045776 | 122.905 | 122.818 | 0.17853 | 0.004577 | 123.1247 | 122.9233 | 122.8592 | -0.37079 | 123.0331 | 122.9919 | 122.9324 | -0.3479
3390.2344 | 123.1796 | -122.7631 | 0.16022 | -0.069275 | 0.029373 | 0.0085022 | 0.0068273 | -0.005834 | -0.0071842 | -0.0084381 | -0.065842 | -0.014691 | -0.0062528 | -0.0041122 | 4.9132e-05 | -0.012939 | 0.17395 | 0.25635 | 0.19684 | 0.19684 | 0.3479 | 0.064087 | -0.10071 | 0.20599 | 0.27466 | 0.20599 | 0.27008 | 0.21973 | -0.032043 | -0.10529 | 122.8271 | 122.6624 | 0.18768 | 123.0194 | 122.9599 | 0.29755 | 0.013733 | 122.731 | 122.6578 | 0.10986 | 122.9691 | 122.9691 | 0.31128 | 0.05951 | 123.111 | 122.937 | 122.9599 | -0.26093 | 123.0331 | 122.9828 | 123.0377 | -0.2655
3391.9844 | 123.1888 | -122.7676 | 0.14648 | -0.069275 | 0.026596 | 0.008075 | 0.0081091 | -0.0090384 | -0.0048344 | -0.0095063 | -0.096359 | -0.012768 | -0.0053982 | -0.0045394 | 0.0026125 | -0.017425 | 0.16937 | 0.23804 | 0.19684 | 0.1831 | 0.35248 | 0.068665 | -0.10529 | 0.21973 | 0.28381 | 0.1831 | 0.25635 | 0.23346 | -0.036621 | -0.073242 | 122.8363 | 122.6624 | 0.20599 | 123.0057 | 122.9507 | 0.28839 | 0.022889 | 122.731 | 122.6944 | 0.10986 | 122.9874 | 122.9507 | 0.25635 | 0.086975 | 123.1201 | 122.937 | 122.9645 | -0.25177 | 123.024 | 123.0011 | 123.0515 | -0.21973
3393.6719 | 123.1247 | -122.8455 | 0.19226 | -0.21423 | 0.030441 | 0.0052978 | 0.0076819 | -0.0060476 | -0.0054752 | -0.011215 | -0.22606 | -0.011273 | -0.0062528 | -0.0030442 | 0.0028263 | -0.016571 | 0.21515 | 0.2243 | 0.17395 | 0.18768 | 0.37537 | 0.082397 | -0.09613 | 0.16022 | 0.22888 | 0.07782 | 0.27466 | 0.27008 | -0.050354 | -0.07782 | 122.9279 | 122.7493 | 0.1831 | 123.0698 | 123.0331 | 0.28381 | 0.022888 | 122.7951 | 122.7676 | 0.082397 | 123.0057 | 122.9233 | 0.15564 | 0.07782 | 123.2208 | 123.0606 | 123.0194 | -0.28839 | 123.1201 | 123.1155 | 123.0743 | -0.27008
3395.4531 | 123.0515 | -122.8546 | 0.2243 | 0.075684 | 0.030869 | 0.0044434 | 0.0029821 | -0.0090384 | 0.0028562 | -0.0077973 | 0.04097 | -0.010418 | -0.0064664 | -0.00048061 | 0.0092349 | -0.01828 | 0.027466 | -0.032043 | -0.086975 | -0.036621 | 0.28381 | -0.068665 | -0.22888 | 0.009155 | 0 | -0.10986 | 0.20599 | 0.16479 | -0.15564 | -0.21515 | 122.7859 | 122.6257 | 0.059509 | 122.8226 | 122.818 | 0.19226 | -0.19684 | 122.699 | 122.6395 | -0.01831 | 122.8638 | 122.7448 | 0.10529 | -0.059509 | 123.1384 | 122.8821 | 122.7676 | -0.45319 | 123.0606 | 123.0194 | 122.8546 | -0.43945
3397.1562 | 123.1522 | -122.8043 | 0.1831 | -0.16846 | 0.027237 | 0.0087158 | 0.0049047 | -0.011175 | -0.0059024 | -0.0082245 | -0.16502 | -0.013196 | -0.0071072 | -0.0049668 | 0.0064577 | -0.01358 | 0.19684 | 0.31586 | 0.21057 | 0.19226 | 0.35706 | 0.07782 | -0.059509 | 0.23346 | 0.3067 | 0.17395 | 0.26093 | 0.22888 | -0.022888 | -0.073242 | 122.8821 | 122.7448 | 0.17395 | 123.1201 | 122.9965 | 0.25177 | 0.013733 | 122.7814 | 122.731 | 0.07782 | 123.0377 | 122.9782 | 0.24719 | 0.045777 | 123.1613 | 123.0011 | 123.0148 | -0.24261 | 123.0652 | 123.0331 | 123.111 | -0.25635
3398.9062 | 123.1064 | -122.8134 | 0.19226 | 0.20538 | 0.03215 | 0.0059388 | 0.0061865 | -0.0081838 | 0.00029262 | -0.0086517 | 0.13252 | -0.011059 | -0.0068936 | -0.0028306 | 0.0070987 | -0.01358 | 0.036621 | 0.018311 | -0.013733 | 0.004578 | 0.24261 | -0.059509 | -0.22888 | 0.09613 | 0.09613 | -0.004578 | 0.16937 | 0.13275 | -0.12817 | -0.16479 | 122.7539 | 122.5845 | 0.050354 | 122.8317 | 122.818 | 0.23346 | -0.15564 | 122.6852 | 122.6486 | -0.022888 | 122.9095 | 122.8088 | 0.16022 | -0.05951 | 123.056 | 122.85 | 122.7997 | -0.42114 | 122.9828 | 122.9462 | 122.9095 | -0.35706
3400.6719 | 123.1064 | -122.8363 | 0.19684 | 0.13672 | 0.030869 | 0.0042298 | 0.0036231 | -0.0090384 | 0.0022152 | -0.0082245 | 0.04097 | -0.0095639 | -0.0058254 | 0.00037379 | 0.0066715 | -0.015716 | 0.027466 | -0.009155 | -0.045776 | 0.004578 | 0.27466 | -0.07782 | -0.24719 | 0.045776 | 0.027466 | -0.064087 | 0.21057 | 0.15564 | -0.15106 | -0.20599 | 122.7585 | 122.5891 | 0.07782 | 122.8271 | 122.8409 | 0.25177 | -0.16937 | 122.6852 | 122.6303 | 0.013733 | 122.8821 | 122.7722 | 0.14191 | -0.041198 | 123.111 | 122.8638 | 122.7905 | -0.44403 | 123.0469 | 122.9919 | 122.8638 | -0.40283
3402.4375 | 123.1018 | -122.8729 | 0.1831 | 0.052795 | 0.027237 | 0.0065796 | 0.0025549 | -0.010747 | -0.0065434 | -0.0088653 | 0.094375 | -0.012341 | -0.007748 | -0.0047532 | 0.00047633 | -0.013794 | 0.091553 | 0.14191 | 0.10986 | 0.1236 | 0.30212 | 0.018311 | -0.15564 | 0.10986 | 0.17395 | 0.086975 | 0.24719 | 0.19684 | -0.068665 | -0.1236 | 122.8912 | 122.7173 | 0.11902 | 123.0148 | 122.9965 | 0.27924 | -0.091552 | 122.8043 | 122.7493 | 0.064087 | 122.9828 | 122.9599 | 0.21057 | 0.013733 | 123.175 | 122.9645 | 122.9828 | -0.33874 | 123.1201 | 123.0698 | 123.0469 | -0.3067
3404.1875 | 123.1613 | -122.7859 | 0.16479 | 0.0070193 | 0.025742 | 0.0048706 | 0.0078955 | -0.012456 | -0.005048 | -0.010361 | 0.010452 | -0.013409 | -0.0058254 | -0.0011216 | 0.0023989 | -0.013794 | 0.13275 | 0.16937 | 0.15106 | 0.15106 | 0.29755 | 0.036621 | -0.12817 | 0.16937 | 0.23804 | 0.14191 | 0.25635 | 0.21515 | -0.036621 | -0.082397 | 122.8226 | 122.6578 | 0.13275 | 122.9553 | 122.937 | 0.27924 | -0.032044 | 122.7493 | 122.7036 | 0.091553 | 122.9553 | 122.9279 | 0.2243 | 0.050354 | 123.0835 | 122.9187 | 122.937 | -0.29297 | 123.0423 | 123.0011 | 123.024 | -0.24719
3405.875 | 123.1384 | -122.8455 | 0.18768 | -0.23712 | 0.031723 | 0.0023072 | 0.011741 | -0.0096792 | -0.00056178 | -0.011002 | -0.17265 | -0.013409 | -0.006039 | -0.0017624 | 0.0023989 | -0.017639 | 0.17853 | 0.16479 | 0.13733 | 0.16022 | 0.3891 | 0.054932 | -0.10986 | 0.1236 | 0.15564 | 0.022888 | 0.29297 | 0.27466 | -0.068665 | -0.11444 | 122.9004 | 122.7356 | 0.20142 | 123.0103 | 123.0057 | 0.27008 | -0.009155 | 122.7768 | 122.731 | 0.10529 | 122.9691 | 122.8683 | 0.13733 | 0.086975 | 123.2346 | 123.024 | 122.9828 | -0.29755 | 123.1384 | 123.1201 | 123.0011 | -0.30212
3407.625 | 123.2071 | -122.7905 | 0.16937 | -0.19135 | 0.030655 | 0.0055114 | 0.0066137 | -0.011388 | 0.0020016 | -0.0056611 | -0.29472 | -0.011487 | -0.0053982 | -0.0015488 | 0.0060305 | -0.017852 | 0.13733 | 0.11444 | 0.064087 | 0.1236 | 0.37994 | 0.027466 | -0.11902 | 0.11444 | 0.14191 | 0.013733 | 0.28381 | 0.25177 | -0.068665 | -0.14648 | 122.818 | 122.6715 | 0.21057 | 122.905 | 122.9141 | 0.24261 | -0.032044 | 122.7219 | 122.644 | 0.11444 | 122.905 | 122.8043 | 0.16022 | 0.082397 | 123.1705 | 122.9279 | 122.8546 | -0.28839 | 123.0743 | 123.0423 | 122.9324 | -0.31586
3409.3125 | 123.0515 | -122.8317 | 0.21515 | 0.1825 | 0.029373 | 0.0048706 | 0.0034093 | -0.0069022 | -0.0031254 | -0.0058747 | 0.1783 | -0.015973 | -0.0073208 | -0.0026168 | 0.0088077 | -0.016571 | 0.09613 | 0.12817 | 0.082397 | 0.064087 | 0.19684 | -0.045776 | -0.20599 | 0.14648 | 0.16479 | 0.050354 | 0.15106 | 0.12817 | -0.11444 | -0.17853 | 122.7859 | 122.6257 | -0.018311 | 122.9599 | 122.8958 | 0.27008 | -0.11902 | 122.7173 | 122.6532 | -0.064087 | 122.9782 | 122.8821 | 0.22888 | -0.086975 | 123.0286 | 122.9279 | 122.9141 | -0.42114 | 122.9828 | 122.9599 | 122.9965 | -0.39368
3411.0781 | 123.0515 | -122.8455 | 0.20599 | 0.12146 | 0.027237 | 0.0059388 | 0.0046911 | -0.0071158 | -0.0046206 | -0.0067291 | 0.11726 | -0.014264 | -0.006039 | -0.00048061 | 0.0032535 | -0.016571 | 0.10071 | 0.13275 | 0.091553 | 0.082397 | 0.24719 | -0.013733 | -0.16937 | 0.13733 | 0.16022 | 0.050354 | 0.21515 | 0.18768 | -0.064087 | -0.1236 | 122.8317 | 122.6761 | 0.041198 | 122.9782 | 122.9279 | 0.25177 | -0.10529 | 122.7814 | 122.7219 | 0.009155 | 122.9828 | 122.8958 | 0.17395 | -0.018311 | 123.0927 | 122.9462 | 122.937 | -0.37537 | 123.0606 | 123.0331 | 123.0057 | -0.32959
3412.7812 | 123.0881 | -122.8409 | 0.19226 | 0.13672 | 0.031082 | 0.0057252 | 0.0036231 | -0.0064748 | 0.0011472 | -0.0060883 | 0.15541 | -0.010418 | -0.0073208 | -0.0013352 | 0.0085941 | -0.018066 | 0.045776 | 0 | -0.036621 | -0.013733 | 0.2655 | -0.073242 | -0.22888 | 0.082397 | 0.068665 | -0.041199 | 0.17853 | 0.14191 | -0.14191 | -0.16479 | 122.7676 | 122.612 | 0.073242 | 122.8409 | 122.8271 | 0.21515 | -0.14648 | 122.699 | 122.6761 | -0.013733 | 122.9233 | 122.7997 | 0.1236 | -0.050354 | 123.1064 | 122.8867 | 122.8043 | -0.42114 | 123.0194 | 122.9828 | 122.9095 | -0.35706
3414.5312 | 123.0972 | -122.85 | 0.19684 | 0.15198 | 0.034927 | 0.002948 | 0.0061865 | -0.0090384 | 0.0020016 | -0.0063019 | 0.048599 | -0.010418 | -0.0062528 | -0.0024032 | 0.0058169 | -0.015503 | 0.009155 | -0.027466 | -0.073242 | -0.009155 | 0.25635 | -0.073242 | -0.25177 | 0.009155 | -0.004578 | -0.086975 | 0.19226 | 0.15564 | -0.15106 | -0.21057 | 122.7768 | 122.5983 | 0.05951 | 122.8226 | 122.8409 | 0.24261 | -0.18768 | 122.699 | 122.6395 | -0.004577 | 122.8592 | 122.7631 | 0.1236 | -0.041198 | 123.1064 | 122.8592 | 122.7768 | -0.44861 | 123.0423 | 123.0057 | 122.8455 | -0.40741
3416.2969 | 123.1705 | -122.818 | 0.19226 | -0.00061023 | 0.031723 | 0.0055114 | 0.0078955 | -0.010534 | -0.0054752 | -0.0084381 | 0.048599 | -0.012341 | -0.006039 | -0.0011216 | -0.00016447 | -0.015075 | 0.091553 | 0.14191 | 0.13275 | 0.11444 | 0.32501 | 0.022888 | -0.14191 | 0.13733 | 0.19226 | 0.11444 | 0.22888 | 0.21515 | -0.059509 | -0.09613 | 122.8409 | 122.6761 | 0.13275 | 122.9599 | 122.9324 | 0.25635 | -0.10071 | 122.7585 | 122.7219 | 0.036621 | 122.9553 | 122.9324 | 0.21057 | 0.022888 | 123.143 | 122.9095 | 122.9507 | -0.33417 | 123.0469 | 123.0331 | 123.0103 | -0.28839
3418.0469 | 123.1018 | -122.8409 | 0.19684 | 0.20538 | 0.031082 | 0.0050842 | 0.0046911 | -0.0062612 | 0.0041378 | -0.0073701 | 0.12489 | -0.010846 | -0.0081754 | -0.00026701 | 0.0070987 | -0.017212 | 0.07782 | 0.064087 | 0.027466 | 0.036621 | 0.21515 | -0.054932 | -0.2243 | 0.1236 | 0.13733 | 0.018311 | 0.15106 | 0.1236 | -0.10529 | -0.15564 | 122.7859 | 122.6166 | 0.018311 | 122.905 | 122.8775 | 0.26093 | -0.11902 | 122.7356 | 122.6852 | -0.045776 | 122.9645 | 122.8592 | 0.17395 | -0.073242 | 123.056 | 122.9187 | 122.8683 | -0.42114 | 122.9919 | 122.9645 | 122.9782 | -0.35248
3419.7344 | 123.0789 | -122.8729 | 0.20142 | 0.068054 | 0.025955 | 0.0078614 | 0.0046911 | -0.011815 | -0.0069706 | -0.0090791 | 0.079117 | -0.013196 | -0.00668 | -0.0045394 | 0.0032535 | -0.014862 | 0.10529 | 0.14648 | 0.10071 | 0.10071 | 0.30212 | 0.022888 | -0.13733 | 0.13733 | 0.15564 | 0.073242 | 0.22888 | 0.19226 | -0.068665 | -0.1236 | 122.8958 | 122.7356 | 0.10071 | 123.0194 | 122.9736 | 0.23804 | -0.09613 | 122.8043 | 122.7493 | 0.027466 | 123.0103 | 122.9462 | 0.19684 | -0.009155 | 123.175 | 122.9782 | 122.9736 | -0.33875 | 123.1018 | 123.0652 | 123.0286 | -0.32501
3421.5 | 123.143 | -122.8134 | 0.17853 | -0.25238 | 0.029373 | 0.0057252 | 0.0093909 | -0.0071158 | -0.0031254 | -0.0075837 | -0.21843 | -0.012555 | -0.0058254 | -0.0015488 | 0.0045351 | -0.016143 | 0.21515 | 0.20599 | 0.14648 | 0.1831 | 0.38452 | 0.054932 | -0.11444 | 0.15564 | 0.19226 | 0.045776 | 0.29755 | 0.26093 | -0.054932 | -0.10529 | 122.8683 | 122.699 | 0.20599 | 123.0194 | 122.9965 | 0.29755 | 0.036621 | 122.7585 | 122.7081 | 0.11902 | 122.9691 | 122.8592 | 0.15106 | 0.082397 | 123.1979 | 123.0286 | 122.9599 | -0.29297 | 123.111 | 123.0743 | 123.0057 | -0.28381
3423.25 | 123.1888 | -122.7905 | 0.17853 | -0.12268 | 0.028732 | 0.0050842 | 0.0081091 | -0.0066884 | -0.0041934 | -0.0086517 | -0.065842 | -0.0117 | -0.0071072 | -0.0013352 | 0.0015445 | -0.015716 | 0.23804 | 0.24261 | 0.2243 | 0.17395 | 0.35706 | 0.068665 | -0.082397 | 0.22888 | 0.28839 | 0.17395 | 0.26093 | 0.2243 | -0.032043 | -0.073242 | 122.8592 | 122.7081 | 0.17853 | 123.0331 | 122.9645 | 0.25635 | 0.059509 | 122.7585 | 122.7173 | 0.082397 | 123.0194 | 122.9645 | 0.24719 | 0.045776 | 123.1476 | 123.0286 | 123.0148 | -0.26092 | 123.0515 | 123.0148 | 123.0789 | -0.25177
3424.9531 | 123.0377 | -122.8271 | 0.21515 | 0.098572 | 0.028305 | 0.0052978 | 0.0061865 | -0.0096792 | -0.00077538 | -0.0073701 | 0.14015 | -0.013409 | -0.0064664 | -0.00090781 | 0.0051761 | -0.015503 | 0.1236 | 0.11902 | 0.086975 | 0.059509 | 0.22888 | -0.041199 | -0.18768 | 0.14648 | 0.16022 | 0.059509 | 0.1831 | 0.16937 | -0.091553 | -0.16937 | 122.7859 | 122.6395 | 0.013733 | 122.9462 | 122.8867 | 0.24719 | -0.091553 | 122.7356 | 122.6578 | -0.032044 | 122.9736 | 122.8867 | 0.22888 | -0.045776 | 123.056 | 122.9507 | 122.9141 | -0.40283 | 123.0103 | 122.9965 | 122.9874 | -0.38452
3426.7031 | 123.0606 | -122.8409 | 0.21057 | 0.13672 | 0.0298 | 0.0065796 | 0.0051183 | -0.0079702 | 0.0011472 | -0.0080109 | 0.102 | -0.013409 | -0.008389 | -0.0013352 | 0.0064577 | -0.015289 | 0.13275 | 0.12817 | 0.091553 | 0.064087 | 0.24261 | -0.027466 | -0.19684 | 0.15106 | 0.15106 | 0.064087 | 0.17395 | 0.13733 | -0.11902 | -0.15106 | 122.8134 | 122.644 | 0.032044 | 122.9691 | 122.905 | 0.26093 | -0.07782 | 122.7219 | 122.6898 | -0.036621 | 122.9919 | 122.905 | 0.21515 | -0.073242 | 123.0835 | 122.9736 | 122.9324 | -0.40741 | 123.0148 | 122.9782 | 122.9919 | -0.36163
3428.4688 | 123.143 | -122.8043 | 0.17853 | -0.16083 | 0.0298 | 0.0078614 | 0.0076819 | -0.0083974 | 7.902e-05 | -0.0075837 | -0.25658 | -0.010846 | -0.0062528 | -0.0047532 | 0.0032535 | -0.016357 | 0.22888 | 0.24261 | 0.19226 | 0.18768 | 0.34332 | 0.054932 | -0.10071 | 0.20142 | 0.25177 | 0.10529 | 0.28839 | 0.25635 | -0.045776 | -0.091553 | 122.8592 | 122.7036 | 0.16479 | 123.0469 | 122.9919 | 0.28839 | 0.050354 | 122.7585 | 122.7127 | 0.10986 | 123.0057 | 122.9095 | 0.19684 | 0.07782 | 123.1476 | 123.0331 | 122.9965 | -0.27924 | 123.0927 | 123.0606 | 123.056 | -0.27008
3430.1719 | 123.1476 | -122.8271 | 0.19226 | -0.2829 | 0.031296 | 0.0067932 | 0.0083227 | -0.009252 | -0.00163 | -0.0088653 | -0.25658 | -0.0117 | -0.0071072 | -0.0041122 | 0.0043215 | -0.016784 | 0.21057 | 0.21057 | 0.16479 | 0.1831 | 0.39368 | 0.068665 | -0.10071 | 0.13733 | 0.18768 | 0.054932 | 0.31586 | 0.27924 | -0.041199 | -0.10986 | 122.8958 | 122.7264 | 0.20142 | 123.0377 | 123.0103 | 0.28381 | 0.01831 | 122.7859 | 122.7173 | 0.1236 | 122.9645 | 122.8821 | 0.16479 | 0.086975 | 123.2208 | 123.0377 | 122.9919 | -0.29297 | 123.143 | 123.1064 | 123.0148 | -0.30212
3431.9219 | 123.0881 | -122.8455 | 0.18768 | 0.037537 | 0.026169 | 0.0050842 | 0.0072547 | -0.0094656 | -0.0022708 | -0.010574 | 0.025711 | -0.012982 | -0.00668 | -0.00026701 | 0.0013309 | -0.014435 | 0.11902 | 0.12817 | 0.10529 | 0.11902 | 0.30212 | 0 | -0.16022 | 0.14648 | 0.16022 | 0.086975 | 0.25177 | 0.21057 | -0.064087 | -0.10986 | 122.8455 | 122.6852 | 0.11444 | 122.9736 | 122.9645 | 0.27924 | -0.068664 | 122.7814 | 122.7356 | 0.064087 | 122.9919 | 122.9324 | 0.19684 | 0.022888 | 123.1476 | 122.9645 | 122.9507 | -0.3479 | 123.0972 | 123.056 | 123.0057 | -0.29755
3433.6875 | 123.0652 | -122.8638 | 0.19684 | 0.022278 | 0.033432 | 0.0067932 | 0.0046911 | -0.010106 | 0.004565 | -0.0060883 | -0.0048066 | -0.0087093 | -0.0047574 | -0.00090781 | 0.0083805 | -0.018066 | 0.050354 | -0.013733 | -0.064087 | -0.004578 | 0.27924 | -0.059509 | -0.23346 | 0.013733 | 0.009155 | -0.10986 | 0.20142 | 0.16479 | -0.15106 | -0.21515 | 122.8043 | 122.6303 | 0.082398 | 122.85 | 122.8592 | 0.22888 | -0.14648 | 122.7127 | 122.6486 | 0.004578 | 122.8775 | 122.7539 | 0.10529 | -0.032043 | 123.143 | 122.9141 | 122.7997 | -0.4303 | 123.0652 | 123.0286 | 122.8729 | -0.41199
3435.4062 | 123.0606 | -122.8363 | 0.20142 | -0.031128 | 0.034073 | 0.0070068 | 0.0044775 | -0.0083974 | 0.004565 | -0.0035249 | -0.058212 | -0.010632 | -0.0056118 | -0.0015488 | 0.0098757 | -0.015075 | 0.1236 | 0.09613 | 0.009155 | 0.064087 | 0.30212 | -0.032043 | -0.20142 | 0.050354 | 0.073242 | -0.082397 | 0.2243 | 0.16479 | -0.16022 | -0.21057 | 122.8043 | 122.6349 | 0.10071 | 122.9324 | 122.9004 | 0.2655 | -0.07782 | 122.6761 | 122.6257 | 0.022888 | 122.8867 | 122.7539 | 0.12817 | -0.036621 | 123.1384 | 122.9599 | 122.8455 | -0.40283 | 123.0606 | 123.0011 | 122.9095 | -0.41199
3437.1562 | 123.0927 | -122.818 | 0.19226 | 0.029907 | 0.026383 | 0.0050842 | 0.0044775 | -0.0094656 | -0.0046206 | -0.0084381 | 0.056228 | -0.014264 | -0.0045438 | -0.0021896 | 0.0021853 | -0.011871 | 0.10071 | 0.14191 | 0.10529 | 0.091553 | 0.30212 | 0.027466 | -0.13275 | 0.13275 | 0.16479 | 0.082397 | 0.24261 | 0.20599 | -0.068665 | -0.11444 | 122.8455 | 122.6852 | 0.10986 | 122.9599 | 122.9095 | 0.2243 | -0.091553 | 122.7493 | 122.7036 | 0.050354 | 122.9507 | 122.9004 | 0.19684 | 0.013733 | 123.1201 | 122.9187 | 122.9233 | -0.32501 | 123.0606 | 123.024 | 122.9828 | -0.3067
3438.8594 | 123.0606 | -122.8546 | 0.21515 | 0.037537 | 0.0345 | 0.0040162 | 0.0044775 | -0.0083974 | 0.0037106 | -0.0056611 | -0.020065 | -0.010418 | -0.0056118 | -0.0011216 | 0.0088077 | -0.014862 | 0.027466 | -0.022888 | -0.064087 | -0.009155 | 0.27466 | -0.068665 | -0.23346 | 0.018311 | 0.009155 | -0.10986 | 0.19226 | 0.17395 | -0.14648 | -0.20142 | 122.7859 | 122.6212 | 0.059509 | 122.8317 | 122.8455 | 0.2243 | -0.18768 | 122.7081 | 122.6532 | -0.022888 | 122.8729 | 122.7448 | 0.091553 | -0.041199 | 123.1293 | 122.8821 | 122.7905 | -0.44861 | 123.0469 | 123.0286 | 122.8638 | -0.41657
3440.625 | 123.175 | -122.7768 | 0.19684 | -0.061646 | 0.030655 | 0.0076478 | 0.0070409 | -0.0079702 | -0.0063296 | -0.0080109 | -0.081101 | -0.013623 | -0.0058254 | -0.0043258 | 0.00068993 | -0.014007 | 0.16479 | 0.22888 | 0.17853 | 0.1831 | 0.34332 | 0.064087 | -0.086975 | 0.22888 | 0.27466 | 0.16937 | 0.27008 | 0.21515 | -0.032043 | -0.073242 | 122.8409 | 122.6898 | 0.14648 | 123.0057 | 122.9599 | 0.27008 | -0.032043 | 122.7448 | 122.7036 | 0.073243 | 123.0057 | 122.9462 | 0.24261 | 0.018311 | 123.1201 | 122.9416 | 122.9553 | -0.28381 | 123.0469 | 122.9919 | 123.0515 | -0.27008
3442.3125 | 123.2208 | -122.7859 | 0.17395 | -0.19897 | 0.035141 | 0.0048706 | 0.0078955 | -0.0096792 | 0.0030698 | -0.0069427 | -0.22606 | -0.010205 | -0.0036892 | 0.0010148 | 0.0066715 | -0.01593 | 0.13733 | 0.12817 | 0.059509 | 0.1236 | 0.37537 | 0.027466 | -0.13733 | 0.10071 | 0.13733 | 0 | 0.27008 | 0.23346 | -0.10071 | -0.14191 | 122.8134 | 122.6486 | 0.20142 | 122.9141 | 122.9095 | 0.26093 | -0.036621 | 122.6852 | 122.644 | 0.096131 | 122.8867 | 122.7859 | 0.14191 | 0.059509 | 123.1613 | 122.9233 | 122.8455 | -0.31128 | 123.056 | 123.0194 | 122.9233 | -0.31586
3444.0625 | 123.1842 | -122.8317 | 0.1831 | -0.22949 | 0.0345 | 0.0050842 | 0.0070409 | -0.0071158 | 0.0022152 | -0.0086517 | -0.14214 | -0.0080685 | -0.0064664 | -0.00090781 | 0.0079531 | -0.017425 | 0.13733 | 0.1236 | 0.050354 | 0.10071 | 0.32501 | -0.004578 | -0.17395 | 0.09613 | 0.14648 | 0 | 0.22888 | 0.20142 | -0.1236 | -0.16479 | 122.8271 | 122.6578 | 0.14191 | 122.9553 | 122.9324 | 0.27466 | -0.045776 | 122.7081 | 122.6669 | 0.045777 | 122.9279 | 122.8317 | 0.16479 | 0.018311 | 123.1567 | 122.9691 | 122.8821 | -0.35706 | 123.0606 | 123.0331 | 122.9782 | -0.3479
3445.7656 | 123.0881 | -122.8363 | 0.1831 | 0.014648 | 0.027878 | 0.0044434 | 0.0078955 | -0.008611 | -0.0052616 | -0.0088653 | 0.102 | -0.013196 | -0.00668 | -0.0026168 | 0.00047633 | -0.014648 | 0.073242 | 0.16022 | 0.11444 | 0.10529 | 0.31128 | 0 | -0.14648 | 0.1236 | 0.18768 | 0.09613 | 0.24719 | 0.21057 | -0.068665 | -0.13275 | 122.8363 | 122.6898 | 0.12817 | 122.9965 | 122.9416 | 0.25177 | -0.10986 | 122.7676 | 122.7036 | 0.064087 | 122.9599 | 122.9324 | 0.22888 | 0.027466 | 123.1476 | 122.9095 | 122.9507 | -0.32959 | 123.0835 | 123.0469 | 123.024 | -0.31586
3447.5312 | 123.0927 | -122.818 | 0.21057 | 0.12146 | 0.02916 | 0.0050842 | 0.0068273 | -0.005834 | 0.0032834 | -0.0065155 | 0.079117 | -0.0087093 | -0.0068936 | 0.00016019 | 0.0075259 | -0.016143 | 0.041199 | -0.004578 | -0.036621 | 0 | 0.28381 | -0.059509 | -0.25177 | 0.045776 | 0.032043 | -0.054932 | 0.19684 | 0.16022 | -0.13733 | -0.21057 | 122.7585 | 122.5662 | 0.073242 | 122.8134 | 122.818 | 0.25177 | -0.16937 | 122.6807 | 122.6074 | -0.013733 | 122.8638 | 122.7631 | 0.15564 | -0.050354 | 123.1018 | 122.8592 | 122.7814 | -0.46234 | 123.0148 | 122.9782 | 122.85 | -0.42114
3449.2344 | 123.1338 | -122.7951 | 0.18768 | -0.26764 | 0.032364 | 0.0061524 | 0.0093909 | -0.0073294 | -0.0012028 | -0.0080109 | -0.19554 | -0.011273 | -0.004971 | -0.001976 | 0.0041079 | -0.01593 | 0.1831 | 0.21515 | 0.16022 | 0.18768 | 0.39368 | 0.064087 | -0.10529 | 0.11444 | 0.20599 | 0.068665 | 0.31128 | 0.26093 | -0.050354 | -0.10071 | 122.8592 | 122.6898 | 0.20599 | 123.0103 | 122.9828 | 0.29297 | -0.004578 | 122.7448 | 122.6944 | 0.1236 | 122.9095 | 122.8638 | 0.16937 | 0.073242 | 123.1888 | 122.9782 | 122.9553 | -0.29297 | 123.1064 | 123.056 | 123.0011 | -0.28839
3450.9844 | 123.143 | -122.8134 | 0.18768 | -0.015869 | 0.025955 | 0.0052978 | 0.0057593 | -0.009252 | -0.0046206 | -0.0086517 | 0.03334 | -0.014477 | -0.0073208 | -0.00090781 | 0.0017581 | -0.014007 | 0.10529 | 0.14648 | 0.1236 | 0.09613 | 0.29755 | 0.013733 | -0.1236 | 0.13275 | 0.20142 | 0.11902 | 0.22888 | 0.2243 | -0.082397 | -0.1236 | 122.8271 | 122.6898 | 0.10986 | 122.9599 | 122.9095 | 0.21973 | -0.082397 | 122.731 | 122.6898 | 0.041199 | 122.9462 | 122.9324 | 0.24261 | 0.036621 | 123.111 | 122.9187 | 122.937 | -0.31128 | 123.0423 | 123.0377 | 123.0148 | -0.31128
3452.75 | 123.1888 | -122.8043 | 0.16022 | -0.13031 | 0.027237 | 0.0072204 | 0.0059729 | -0.0066884 | -0.0052616 | -0.0086517 | -0.10399 | -0.012768 | -0.0064664 | -0.0021896 | 0.0038943 | -0.017425 | 0.2243 | 0.24719 | 0.22888 | 0.18768 | 0.35706 | 0.059509 | -0.091553 | 0.23346 | 0.3067 | 0.1831 | 0.25635 | 0.2243 | -0.041199 | -0.073242 | 122.8638 | 122.7127 | 0.19684 | 123.0515 | 122.9919 | 0.27924 | 0.064087 | 122.7631 | 122.731 | 0.096131 | 123.0377 | 122.9874 | 0.25635 | 0.064087 | 123.1613 | 123.0286 | 123.0331 | -0.25177 | 123.0606 | 123.0286 | 123.111 | -0.23346
3454.5 | 123.1293 | -122.8134 | 0.19226 | -0.00061023 | 0.027664 | 0.0057252 | 0.0059729 | -0.0094656 | -0.0039798 | -0.0086517 | 0.063858 | -0.013836 | -0.0079618 | -0.0021896 | 0.0038943 | -0.015716 | 0.10986 | 0.14648 | 0.11444 | 0.12817 | 0.32044 | 0.009155 | -0.15106 | 0.12817 | 0.17853 | 0.10529 | 0.25177 | 0.20599 | -0.064087 | -0.1236 | 122.8226 | 122.6624 | 0.12817 | 122.9599 | 122.9416 | 0.27924 | -0.082398 | 122.7493 | 122.6898 | 0.059509 | 122.9416 | 122.9187 | 0.22888 | 0.013733 | 123.1339 | 122.9233 | 122.9279 | -0.34332 | 123.0652 | 123.0194 | 122.9919 | -0.31586
3456.2031 | 123.0927 | -122.8638 | 0.19226 | 0.14435 | 0.031937 | 0.0067932 | 0.0029821 | -0.011388 | 0.0032834 | -0.0069427 | 0.03334 | -0.011059 | -0.0064664 | -0.00090781 | 0.0081667 | -0.017852 | 0.041199 | -0.022888 | -0.068665 | -0.018311 | 0.25177 | -0.082397 | -0.23804 | 0.027466 | 0 | -0.091553 | 0.20599 | 0.14648 | -0.15106 | -0.20599 | 122.7814 | 122.6257 | 0.059509 | 122.8409 | 122.8455 | 0.21973 | -0.15106 | 122.7127 | 122.6578 | 0.013733 | 122.8912 | 122.7722 | 0.11444 | -0.045777 | 123.1155 | 122.905 | 122.7951 | -0.4303 | 123.0698 | 123.0103 | 122.8638 | -0.39826
3457.9844 | 123.1338 | -122.8226 | 0.18768 | -0.16846 | 0.031296 | 0.0072204 | 0.0070409 | -0.010106 | -0.00056178 | -0.0069427 | -0.21843 | -0.014691 | -0.0058254 | -0.001976 | 0.0047489 | -0.015075 | 0.1831 | 0.25635 | 0.19226 | 0.19684 | 0.36163 | 0.059509 | -0.10071 | 0.16937 | 0.25177 | 0.091553 | 0.28381 | 0.26093 | -0.036621 | -0.09613 | 122.8821 | 122.7219 | 0.17395 | 123.0789 | 123.0194 | 0.29755 | -0.004578 | 122.7859 | 122.7264 | 0.09613 | 122.9919 | 122.9141 | 0.18768 | 0.073242 | 123.1842 | 123.0057 | 123.0148 | -0.28839 | 123.1064 | 123.0835 | 123.0743 | -0.28381
3459.7344 | 123.1338 | -122.8088 | 0.19226 | -0.19897 | 0.030228 | 0.0042298 | 0.0072547 | -0.0088248 | -0.0024844 | -0.0077973 | -0.26421 | -0.011914 | -0.0079618 | -0.0034714 | 0.0032535 | -0.015716 | 0.21515 | 0.23346 | 0.17395 | 0.19226 | 0.36163 | 0.064087 | -0.10529 | 0.14191 | 0.24261 | 0.091553 | 0.29755 | 0.2655 | -0.054932 | -0.10986 | 122.8729 | 122.7036 | 0.16937 | 123.0423 | 123.0011 | 0.29755 | 0.022888 | 122.7539 | 122.699 | 0.10528 | 122.9507 | 122.9004 | 0.20142 | 0.073242 | 123.1705 | 123.024 | 122.9828 | -0.29755 | 123.1064 | 123.0743 | 123.0515 | -0.30212
3461.5156 | 123.1705 | -122.8226 | 0.16937 | -0.14557 | 0.03215 | 0.002948 | 0.0061865 | -0.0083974 | 0.0011472 | -0.0060883 | -0.20317 | -0.0091367 | -0.0045438 | -0.00069421 | 0.0088077 | -0.018493 | 0.14191 | 0.14191 | 0.068665 | 0.091553 | 0.32959 | -0.018311 | -0.17395 | 0.10986 | 0.14191 | -0.013733 | 0.22888 | 0.20142 | -0.09613 | -0.16479 | 122.8043 | 122.6486 | 0.16022 | 122.9645 | 122.9141 | 0.2655 | -0.027466 | 122.7264 | 122.6578 | 0.059509 | 122.9324 | 122.8088 | 0.15106 | 0.032043 | 123.1522 | 122.9645 | 122.8912 | -0.34332 | 123.0515 | 123.024 | 122.9645 | -0.33417
3463.2188 | 123.0789 | -122.8638 | 0.20142 | 0.060425 | 0.032364 | 0.004657 | 0.0044775 | -0.0098928 | 0.004565 | -0.0045929 | 0.025711 | -0.010205 | -0.0062528 | -5.3406e-05 | 0.0060305 | -0.015716 | 0 | -0.009155 | -0.07782 | -0.013733 | 0.29297 | -0.073242 | -0.24261 | 0.004578 | 0.013733 | -0.09613 | 0.20142 | 0.16937 | -0.16022 | -0.21515 | 122.7905 | 122.6212 | 0.091553 | 122.8546 | 122.85 | 0.22888 | -0.20142 | 122.7036 | 122.6486 | 0 | 122.8683 | 122.7676 | 0.11902 | -0.032043 | 123.1567 | 122.8638 | 122.7859 | -0.44403 | 123.0652 | 123.0331 | 122.8775 | -0.41657
3464.9844 | 123.1064 | -122.8409 | 0.18768 | 0.014648 | 0.028092 | 0.007434 | 0.0051183 | -0.0090384 | -0.0056888 | -0.0082245 | 0.079117 | -0.014477 | -0.008389 | -0.0013352 | 0.0034671 | -0.01123 | 0.07782 | 0.14191 | 0.10529 | 0.11902 | 0.31128 | 0.027466 | -0.13733 | 0.1236 | 0.1831 | 0.10529 | 0.24719 | 0.1831 | -0.068665 | -0.12817 | 122.8683 | 122.7036 | 0.1236 | 122.9828 | 122.9599 | 0.25635 | -0.10986 | 122.7722 | 122.7127 | 0.059509 | 122.9645 | 122.9462 | 0.23346 | -0.004578 | 123.1522 | 122.9187 | 122.9462 | -0.32501 | 123.0881 | 123.024 | 123.024 | -0.31586
3466.7344 | 123.1796 | -122.8134 | 0.16479 | -0.1532 | 0.02916 | 0.0085022 | 0.0089635 | -0.0083974 | -0.005048 | -0.0095063 | -0.065842 | -0.013836 | -0.0064664 | -0.001976 | 0.0011173 | -0.015289 | 0.17853 | 0.29297 | 0.21973 | 0.18768 | 0.33875 | 0.07782 | -0.09613 | 0.22888 | 0.30212 | 0.1831 | 0.27008 | 0.22888 | -0.036621 | -0.059509 | 122.8912 | 122.7173 | 0.17395 | 123.1064 | 123.0011 | 0.28381 | 0.013733 | 122.7768 | 122.7539 | 0.10529 | 123.0423 | 122.9965 | 0.24261 | 0.064087 | 123.1522 | 122.9919 | 123.0331 | -0.26092 | 123.0835 | 123.0423 | 123.1155 | -0.2243
3468.5 | 123.1705 | -122.7905 | 0.16937 | -0.076904 | 0.027451 | 0.0050842 | 0.0096045 | -0.0073294 | -0.0039798 | -0.0095063 | -0.081101 | -0.012341 | -0.0073208 | -0.0015488 | 0.0038943 | -0.016571 | 0.16022 | 0.19226 | 0.16022 | 0.14191 | 0.32959 | 0.045776 | -0.1236 | 0.20142 | 0.27008 | 0.15564 | 0.25635 | 0.23346 | -0.041199 | -0.09613 | 122.8363 | 122.6669 | 0.16022 | 122.9828 | 122.9324 | 0.2655 | -0.009156 | 122.7493 | 122.6944 | 0.086975 | 122.9919 | 122.9462 | 0.25177 | 0.064086 | 123.1201 | 122.9507 | 122.9507 | -0.29297 | 123.0469 | 123.024 | 123.0606 | -0.2655
3470.2031 | 123.0927 | -122.8592 | 0.21515 | 0.098572 | 0.033432 | 0.0055114 | 0.0061865 | -0.0094656 | 0.0037106 | -0.0067291 | 0.04097 | -0.010205 | -0.0075344 | 0.00016019 | 0.0053897 | -0.018066 | 0.027466 | -0.050354 | -0.073242 | -0.018311 | 0.2655 | -0.082397 | -0.25177 | 0.027466 | 0.009155 | -0.082397 | 0.19684 | 0.15106 | -0.16937 | -0.22888 | 122.7768 | 122.6074 | 0.050354 | 122.8088 | 122.8409 | 0.23346 | -0.18768 | 122.6898 | 122.6303 | -0.018311 | 122.8867 | 122.7768 | 0.14649 | -0.064087 | 123.1247 | 122.8867 | 122.7859 | -0.46692 | 123.056 | 123.0103 | 122.8683 | -0.44403
3471.9688 | 123.2025 | -122.7951 | 0.17395 | -0.2066 | 0.032791 | 0.0061524 | 0.010032 | -0.0073294 | 0.00093342 | -0.0075837 | -0.24132 | -0.011914 | -0.0062528 | -0.0015488 | 0.0051761 | -0.016357 | 0.12817 | 0.11902 | 0.064087 | 0.10986 | 0.3891 | 0.009155 | -0.15564 | 0.091553 | 0.13733 | 0 | 0.27466 | 0.23804 | -0.091553 | -0.14648 | 122.8043 | 122.6395 | 0.21515 | 122.9141 | 122.905 | 0.2655 | -0.045776 | 122.7036 | 122.6486 | 0.10071 | 122.8867 | 122.7951 | 0.14648 | 0.064087 | 123.1842 | 122.9233 | 122.8592 | -0.32959 | 123.0698 | 123.0331 | 122.9324 | -0.32043
3473.6719 | 123.1888 | -122.818 | 0.16937 | -0.16083 | 0.034927 | 0.006366 | 0.010673 | -0.0083974 | 0.0032834 | -0.0073701 | -0.18791 | -0.0091367 | -0.0045438 | 0.0010148 | 0.0079531 | -0.016784 | 0.12817 | 0.11444 | 0.054932 | 0.10529 | 0.35248 | -0.004578 | -0.14648 | 0.10071 | 0.15564 | -0.013733 | 0.22888 | 0.20142 | -0.10986 | -0.16022 | 122.8134 | 122.6715 | 0.18311 | 122.9324 | 122.9233 | 0.25177 | -0.041199 | 122.7081 | 122.6578 | 0.059509 | 122.9187 | 122.8043 | 0.14648 | 0.032043 | 123.1705 | 122.9462 | 122.8729 | -0.31586 | 123.0469 | 123.0194 | 122.9736 | -0.32959
3475.4375 | 123.0652 | -122.8546 | 0.21515 | 0.12146 | 0.027664 | 0.006366 | 0.0061865 | -0.0094656 | -0.0039798 | -0.0075837 | 0.11726 | -0.013836 | -0.0056118 | -0.0028306 | 0.0030399 | -0.013366 | 0.064087 | 0.15564 | 0.082397 | 0.07782 | 0.23804 | -0.022888 | -0.16479 | 0.11902 | 0.17395 | 0.07782 | 0.20142 | 0.16022 | -0.07782 | -0.13733 | 122.8317 | 122.6898 | 0.022888 | 123.0103 | 122.9324 | 0.24261 | -0.15106 | 122.7768 | 122.7173 | -0.013733 | 122.9736 | 122.9324 | 0.21515 | -0.054932 | 123.0927 | 122.9187 | 122.937 | -0.37994 | 123.056 | 123.0148 | 123.0286 | -0.35248
3477.2031 | 123.0652 | -122.8638 | 0.21515 | -0.046387 | 0.031723 | 0.0038024 | 0.0059729 | -0.0090384 | 0.004565 | -0.0056611 | -0.042954 | -0.011273 | -0.0075344 | -0.00048061 | 0.0083805 | -0.016784 | 0.054932 | 0.073242 | -0.036621 | 0.018311 | 0.29297 | -0.027466 | -0.19684 | 0.013733 | 0.045776 | -0.11902 | 0.19226 | 0.15564 | -0.15564 | -0.21057 | 122.8363 | 122.6669 | 0.07782 | 122.937 | 122.8821 | 0.21515 | -0.16022 | 122.7081 | 122.6532 | -0.022888 | 122.8775 | 122.7448 | 0.091552 | -0.059509 | 123.1567 | 122.9187 | 122.8271 | -0.41199 | 123.056 | 123.0194 | 122.9095 | -0.42572
3478.9531 | 123.1293 | -122.8088 | 0.1831 | -0.27527 | 0.029373 | 0.0055114 | 0.010673 | -0.01032 | -0.0046206 | -0.0075837 | -0.2108 | -0.014905 | -0.003262 | -0.00090781 | 0.0041079 | -0.014862 | 0.15106 | 0.23346 | 0.17853 | 0.1831 | 0.39825 | 0.059509 | -0.11902 | 0.11902 | 0.19226 | 0.064087 | 0.32044 | 0.25635 | -0.059509 | -0.09613 | 122.8683 | 122.6898 | 0.21515 | 123.0423 | 122.9919 | 0.30212 | -0.032043 | 122.7493 | 122.7127 | 0.13733 | 122.9279 | 122.8729 | 0.16022 | 0.073243 | 123.2071 | 122.9599 | 122.9874 | -0.30212 | 123.1293 | 123.0652 | 123.0011 | -0.27924
3480.6562 | 123.0377 | -122.8088 | 0.21057 | 0.12146 | 0.030228 | 0.0052978 | 0.0061865 | -0.0077566 | -0.004407 | -0.0099335 | 0.14778 | -0.0117 | -0.0071072 | -0.0041122 | 0.0023989 | -0.015075 | 0.068665 | 0.16937 | 0.082397 | 0.068665 | 0.23346 | -0.027466 | -0.1831 | 0.12817 | 0.17853 | 0.068665 | 0.19226 | 0.16022 | -0.10071 | -0.15106 | 122.7814 | 122.6257 | 0.022888 | 122.9782 | 122.8775 | 0.25177 | -0.14191 | 122.7081 | 122.6578 | -0.01831 | 122.937 | 122.8775 | 0.21973 | -0.050354 | 123.0423 | 122.8775 | 122.8912 | -0.39368 | 123.0011 | 122.9691 | 122.9874 | -0.36163
3482.4219 | 123.0743 | -122.8455 | 0.19226 | 0.014648 | 0.028305 | 0.0070068 | 0.0049047 | -0.009252 | -0.0037662 | -0.0099335 | 0.086746 | -0.013623 | -0.0043302 | -0.0047532 | 0.00068993 | -0.013153 | 0.07782 | 0.14191 | 0.10071 | 0.10529 | 0.29755 | 0.013733 | -0.15106 | 0.11444 | 0.17395 | 0.07782 | 0.24719 | 0.21515 | -0.068665 | -0.11444 | 122.8592 | 122.6944 | 0.10528 | 122.9874 | 122.9507 | 0.25635 | -0.11444 | 122.7768 | 122.731 | 0.054931 | 122.9599 | 122.9233 | 0.19226 | 0.022888 | 123.143 | 122.9233 | 122.9462 | -0.34332 | 123.0927 | 123.0606 | 123.0194 | -0.3067
3484.1875 | 123.0606 | -122.8317 | 0.21057 | 0.045166 | 0.033432 | 0.004657 | 0.0051183 | -0.0073294 | 0.005206 | -0.0056611 | 0.010452 | -0.010418 | -0.0056118 | -0.0032578 | 0.0081667 | -0.016998 | 0.009155 | -0.004578 | -0.059509 | 0.004578 | 0.29755 | -0.082397 | -0.2243 | 0.009155 | -0.004578 | -0.10071 | 0.20599 | 0.15564 | -0.15564 | -0.21973 | 122.7493 | 122.6074 | 0.086975 | 122.8271 | 122.8363 | 0.22888 | -0.20142 | 122.6761 | 122.612 | -0.004577 | 122.8409 | 122.731 | 0.11902 | -0.054931 | 123.1293 | 122.8409 | 122.7722 | -0.43488 | 123.0377 | 122.9874 | 122.8271 | -0.4303
3485.8906 | 123.1613 | -122.8088 | 0.19226 | -0.24475 | 0.031937 | 0.0082886 | 0.0091773 | -0.0096792 | -0.0022708 | -0.0084381 | -0.27946 | -0.012768 | -0.0047574 | -0.001976 | 0.0047489 | -0.014862 | 0.091553 | 0.16022 | 0.091553 | 0.1236 | 0.42572 | 0.032043 | -0.13733 | 0.09613 | 0.15564 | 0.004578 | 0.32501 | 0.27924 | -0.068665 | -0.12817 | 122.8409 | 122.6715 | 0.23346 | 122.9691 | 122.9324 | 0.26093 | -0.10071 | 122.7402 | 122.6807 | 0.13275 | 122.905 | 122.8134 | 0.13275 | 0.086975 | 123.2346 | 122.9004 | 122.9004 | -0.32959 | 123.1338 | 123.0881 | 122.9645 | -0.32044
3487.6406 | 123.1842 | -122.8271 | 0.17853 | -0.18372 | 0.033432 | 0.008075 | 0.0078955 | -0.009252 | 0.0026424 | -0.0075837 | -0.19554 | -0.0093503 | -0.0051846 | -0.0028306 | 0.0043215 | -0.01828 | 0.12817 | 0.12817 | 0.050354 | 0.11444 | 0.35248 | -0.004578 | -0.16937 | 0.091553 | 0.14648 | -0.004578 | 0.23346 | 0.20599 | -0.12817 | -0.17395 | 122.8226 | 122.6578 | 0.17395 | 122.9553 | 122.9416 | 0.28381 | -0.050354 | 122.699 | 122.6532 | 0.054931 | 122.9187 | 122.8226 | 0.16937 | 0.027466 | 123.1796 | 122.9553 | 122.8775 | -0.3479 | 123.0606 | 123.0331 | 122.9736 | -0.35248
3489.3906 | 123.1613 | -122.7951 | 0.16937 | -0.16846 | 0.030014 | 0.0057252 | 0.0064001 | -0.0098928 | -0.0046206 | -0.0088653 | -0.12688 | -0.013836 | -0.0056118 | 0.00037379 | -0.0014463 | -0.016998 | 0.20142 | 0.30212 | 0.21515 | 0.20142 | 0.35248 | 0.059509 | -0.07782 | 0.21515 | 0.32959 | 0.18768 | 0.27466 | 0.23804 | -0.018311 | -0.082397 | 122.8546 | 122.7173 | 0.18311 | 123.0972 | 122.9965 | 0.27924 | 0.032043 | 122.7768 | 122.7127 | 0.10529 | 123.0103 | 122.9828 | 0.27008 | 0.068664 | 123.1476 | 122.9965 | 123.0103 | -0.24719 | 123.0698 | 123.0331 | 123.1247 | -0.25177
3491.0938 | 123.0515 | -122.8683 | 0.21973 | 0.083313 | 0.035355 | 0.0040162 | 0.0057593 | -0.0096792 | 0.001788 | -0.0041657 | -0.050583 | -0.010846 | -0.0056118 | -0.0021896 | 0.0083805 | -0.018493 | 0.018311 | -0.022888 | -0.068665 | 0.004578 | 0.28381 | -0.073242 | -0.23346 | -0.018311 | 0.004578 | -0.1236 | 0.2243 | 0.17853 | -0.16022 | -0.21973 | 122.7951 | 122.6349 | 0.064086 | 122.8455 | 122.8729 | 0.23804 | -0.20142 | 122.7081 | 122.6486 | 0.004577 | 122.85 | 122.7448 | 0.096131 | -0.041199 | 123.1522 | 122.8867 | 122.7997 | -0.45319 | 123.0927 | 123.0469 | 122.8729 | -0.43945
3492.8594 | 123.1384 | -122.8043 | 0.19684 | -0.076904 | 0.033005 | 0.0035888 | 0.0074683 | -0.0090384 | 0.0024288 | -0.0054475 | -0.11925 | -0.0095639 | -0.0041164 | 0.00016019 | 0.0058169 | -0.016998 | 0.12817 | 0.11444 | 0.050354 | 0.091553 | 0.31586 | -0.041199 | -0.1831 | 0.10071 | 0.13275 | -0.027466 | 0.21057 | 0.17395 | -0.10529 | -0.16479 | 122.7631 | 122.6212 | 0.11902 | 122.9187 | 122.8958 | 0.27466 | -0.068664 | 122.699 | 122.6395 | 0.013733 | 122.905 | 122.7768 | 0.13733 | -0.022888 | 123.1201 | 122.9324 | 122.8546 | -0.37994 | 123.0148 | 122.9782 | 122.937 | -0.36163
3494.6094 | 123.1659 | -122.8134 | 0.1831 | -0.17609 | 0.027451 | 0.0078614 | 0.0068273 | -0.0071158 | -0.0056888 | -0.0069427 | -0.13451 | -0.013409 | -0.0045438 | -0.0015488 | 0.0015445 | -0.014862 | 0.19226 | 0.28381 | 0.2243 | 0.20599 | 0.35706 | 0.082397 | -0.082397 | 0.19684 | 0.31586 | 0.16479 | 0.27008 | 0.24261 | -0.032043 | -0.073242 | 122.8958 | 122.731 | 0.17395 | 123.0972 | 123.0194 | 0.28839 | 0.009156 | 122.7814 | 122.7402 | 0.086976 | 123.0103 | 122.9782 | 0.23804 | 0.05951 | 123.1705 | 123.0057 | 123.0377 | -0.2655 | 123.0835 | 123.056 | 123.1293 | -0.25635
3496.375 | 123.1979 | -122.8317 | 0.16022 | -0.17609 | 0.028092 | 0.0070068 | 0.0081091 | -0.010106 | -0.0069706 | -0.0095063 | -0.050583 | -0.014264 | -0.00668 | -0.00090781 | 0.0021853 | -0.016784 | 0.20142 | 0.25635 | 0.20599 | 0.17853 | 0.33875 | 0.050354 | -0.091553 | 0.21973 | 0.28839 | 0.19226 | 0.25177 | 0.2243 | -0.041199 | -0.10529 | 122.8821 | 122.7402 | 0.17853 | 123.0881 | 123.0103 | 0.27008 | 0.041199 | 122.7905 | 122.7264 | 0.091553 | 123.0515 | 123.024 | 0.29755 | 0.064087 | 123.1705 | 123.0331 | 123.0377 | -0.25177 | 123.0835 | 123.056 | 123.1201 | -0.2655
3498.125 | 123.0469 | -122.85 | 0.21515 | 0.16724 | 0.028946 | 0.0059388 | 0.0042639 | -0.0094656 | 0.00050622 | -0.0086517 | 0.14778 | -0.0117 | -0.0088162 | -0.0024032 | 0.0049625 | -0.014648 | 0.09613 | 0.13275 | 0.086975 | 0.064087 | 0.2243 | -0.054932 | -0.20599 | 0.13733 | 0.15564 | 0.054932 | 0.17395 | 0.14191 | -0.10071 | -0.17395 | 122.7951 | 122.644 | 0.009155 | 122.9828 | 122.9141 | 0.27008 | -0.11902 | 122.7493 | 122.6761 | -0.041199 | 122.9874 | 122.905 | 0.22888 | -0.073242 | 123.0743 | 122.9462 | 122.937 | -0.42114 | 123.024 | 122.9919 | 123.0057 | -0.3891
3499.875 | 123.111 | -122.85 | 0.18768 | 0.1062 | 0.03215 | 0.0078614 | 0.0061865 | -0.010747 | 0.00071982 | -0.0080109 | 0.1783 | -0.010418 | -0.0079618 | -0.001976 | 0.0077395 | -0.014435 | 0.10986 | 0.10986 | 0.054932 | 0.068665 | 0.21973 | -0.045776 | -0.19684 | 0.1236 | 0.1236 | 0.018311 | 0.16022 | 0.10071 | -0.13733 | -0.17395 | 122.8043 | 122.6532 | 0.032044 | 122.9599 | 122.9187 | 0.2655 | -0.07782 | 122.7127 | 122.6761 | -0.027466 | 122.9736 | 122.8683 | 0.19226 | -0.086975 | 123.0698 | 122.9599 | 122.905 | -0.38452 | 123.0103 | 122.9507 | 122.9736 | -0.36163
3501.6406 | 123.1522 | -122.7997 | 0.17395 | -0.17609 | 0.030869 | 0.0044434 | 0.0087499 | -0.0071158 | -0.0059024 | -0.0095063 | -0.13451 | -0.013196 | -0.0071072 | -0.00090781 | 0.0023989 | -0.014221 | 0.22888 | 0.2655 | 0.21057 | 0.21515 | 0.36621 | 0.07782 | -0.07782 | 0.21057 | 0.29755 | 0.15564 | 0.27008 | 0.23804 | -0.032043 | -0.073242 | 122.8775 | 122.7219 | 0.19226 | 123.0652 | 123.0148 | 0.29297 | 0.054932 | 122.7676 | 122.7264 | 0.096131 | 123.0103 | 122.9553 | 0.22888 | 0.064087 | 123.1659 | 123.0286 | 123.0103 | -0.25177 | 123.0698 | 123.0377 | 123.0972 | -0.24719
3503.3438 | 123.056 | -122.8821 | 0.21057 | 0.052795 | 0.031509 | 0.0048706 | 0.0074683 | -0.0079702 | 0.006274 | -0.0071563 | -0.027695 | -0.0087093 | -0.0051846 | -0.00090781 | 0.0081667 | -0.016784 | 0.027466 | -0.045776 | -0.073242 | 0 | 0.30212 | -0.082397 | -0.23346 | 0.009155 | 0 | -0.10071 | 0.21515 | 0.16022 | -0.16479 | -0.22888 | 122.7997 | 122.6486 | 0.091553 | 122.8363 | 122.8821 | 0.23346 | -0.18311 | 122.7173 | 122.6532 | 0.004578 | 122.8912 | 122.7814 | 0.12817 | -0.050354 | 123.1842 | 122.9095 | 122.8088 | -0.44403 | 123.0972 | 123.0423 | 122.8821 | -0.43945
3505.0938 | 123.1934 | -122.7997 | 0.20599 | -0.24475 | 0.028092 | 0.0067932 | 0.0074683 | -0.0077566 | -0.0014164 | -0.0080109 | -0.24132 | -0.010418 | -0.0041164 | 0.00058739 | 0.0030399 | -0.016998 | 0.14191 | 0.14191 | 0.091553 | 0.13275 | 0.41199 | 0.045776 | -0.12817 | 0.07782 | 0.14648 | 0 | 0.31586 | 0.2655 | -0.068665 | -0.11902 | 122.8455 | 122.6715 | 0.20599 | 122.9416 | 122.9324 | 0.26093 | -0.064087 | 122.731 | 122.6807 | 0.10986 | 122.8775 | 122.7997 | 0.11902 | 0.059509 | 123.2117 | 122.9416 | 122.8912 | -0.33417 | 123.1155 | 123.0652 | 122.9462 | -0.32501
3506.7969 | 123.0606 | -122.8546 | 0.21515 | 0.16724 | 0.029373 | 0.0067932 | 0.0061865 | -0.009252 | -0.0041934 | -0.0069427 | 0.079117 | -0.012341 | -0.010952 | -0.00090781 | 0.0032535 | -0.014221 | 0.086975 | 0.11902 | 0.082397 | 0.068665 | 0.25177 | -0.018311 | -0.1831 | 0.15106 | 0.16479 | 0.059509 | 0.2243 | 0.18768 | -0.068665 | -0.13275 | 122.8363 | 122.6715 | 0.036621 | 122.9736 | 122.9233 | 0.25177 | -0.12817 | 122.7859 | 122.7219 | 0.009155 | 123.0057 | 122.9141 | 0.19226 | -0.027466 | 123.1064 | 122.9416 | 122.937 | -0.39825 | 123.0789 | 123.0423 | 123.0194 | -0.3479
3508.5469 | 123.0606 | -122.8455 | 0.19684 | 0.17487 | 0.030655 | 0.0076478 | 0.0044775 | -0.0077566 | -0.0014164 | -0.0080109 | 0.13252 | -0.012768 | -0.0071072 | -0.0013352 | 0.0053897 | -0.014435 | 0.091553 | 0.10071 | 0.07782 | 0.059509 | 0.21515 | -0.050354 | -0.20599 | 0.13733 | 0.16022 | 0.064087 | 0.17395 | 0.14191 | -0.11902 | -0.16479 | 122.7951 | 122.6395 | 0.018311 | 122.9462 | 122.905 | 0.2655 | -0.10529 | 122.7264 | 122.6807 | -0.022888 | 122.9828 | 122.9095 | 0.22888 | -0.054931 | 123.0606 | 122.937 | 122.9233 | -0.40283 | 123.0194 | 122.9874 | 123.0057 | -0.36163
3510.2969 | 123.0469 | -122.8226 | 0.19684 | 0.13672 | 0.02681 | 0.006366 | 0.0053321 | -0.0088248 | -0.0024844 | -0.0092927 | 0.14015 | -0.014477 | -0.0073208 | -0.0026168 | 0.0028263 | -0.016143 | 0.10529 | 0.13275 | 0.09613 | 0.068665 | 0.23804 | -0.036621 | -0.19226 | 0.14191 | 0.17395 | 0.07782 | 0.20599 | 0.15564 | -0.10529 | -0.15106 | 122.7859 | 122.6303 | 0.041199 | 122.9553 | 122.8912 | 0.26093 | -0.091552 | 122.7173 | 122.6715 | 0.009156 | 122.9645 | 122.9004 | 0.22888 | -0.041198 | 123.0606 | 122.9279 | 122.9187 | -0.3891 | 123.0286 | 122.9782 | 122.9965 | -0.3479
3512.0625 | 123.0606 | -122.8729 | 0.20599 | 0.014648 | 0.034287 | 0.0055114 | 0.0049047 | -0.0090384 | 0.003497 | -0.0063019 | -0.012436 | -0.011914 | -0.0043302 | -0.0021896 | 0.0064577 | -0.018493 | 0.07782 | 0.041199 | -0.022888 | 0.036621 | 0.28839 | -0.054932 | -0.21973 | 0.004578 | 0.013733 | -0.10529 | 0.21057 | 0.16479 | -0.16479 | -0.21057 | 122.818 | 122.6532 | 0.082397 | 122.9141 | 122.9095 | 0.25635 | -0.12817 | 122.7081 | 122.6624 | 0.004577 | 122.8775 | 122.7676 | 0.10529 | -0.041199 | 123.1613 | 122.9507 | 122.85 | -0.42572 | 123.0835 | 123.0377 | 122.8867 | -0.41657
3513.7656 | 123.1018 | -122.8409 | 0.18768 | 0.19012 | 0.032791 | 0.0038024 | 0.0057593 | -0.0083974 | -0.0014164 | -0.0086517 | 0.16304 | -0.012341 | -0.0075344 | -0.0026168 | 0.0083805 | -0.016998 | 0.018311 | 0.018311 | -0.018311 | 0.013733 | 0.24261 | -0.073242 | -0.24719 | 0.086975 | 0.10529 | -0.004578 | 0.16022 | 0.13275 | -0.13275 | -0.20599 | 122.7676 | 122.5937 | 0.054932 | 122.8592 | 122.8546 | 0.26093 | -0.16937 | 122.7081 | 122.6349 | -0.027466 | 122.9279 | 122.8363 | 0.20142 | -0.054932 | 123.0835 | 122.8592 | 122.8226 | -0.43488 | 123.0011 | 122.9736 | 122.9462 | -0.39368
3515.5312 | 123.1796 | -122.8043 | 0.18768 | -0.13031 | 0.031937 | 0.0059388 | 0.0064001 | -0.0071158 | 0.001788 | -0.0067291 | -0.13451 | -0.011273 | -0.0062528 | -0.0028306 | 0.0049625 | -0.015716 | 0.11444 | 0.11902 | 0.059509 | 0.10986 | 0.32959 | -0.009155 | -0.16937 | 0.09613 | 0.13733 | -0.013733 | 0.23804 | 0.20142 | -0.12817 | -0.17395 | 122.7951 | 122.6349 | 0.14191 | 122.9233 | 122.9141 | 0.27924 | -0.073242 | 122.6761 | 122.6303 | 0.050354 | 122.9004 | 122.7905 | 0.16022 | 0.013733 | 123.1338 | 122.9187 | 122.8638 | -0.35706 | 123.0423 | 123.0057 | 122.9416 | -0.36163
3517.2969 | 123.0743 | -122.8271 | 0.2243 | 0.022278 | 0.030441 | 0.0065796 | 0.0059729 | -0.0090384 | 0.001788 | -0.0058747 | 0.048599 | -0.0093503 | -0.0043302 | -0.00026701 | 0.0062441 | -0.014648 | -0.004578 | -0.050354 | -0.073242 | -0.013733 | 0.28839 | -0.068665 | -0.23346 | 0.009155 | -0.004578 | -0.11444 | 0.20599 | 0.17853 | -0.17395 | -0.21973 | 122.7585 | 122.5937 | 0.064087 | 122.7768 | 122.8134 | 0.21973 | -0.22888 | 122.6532 | 122.6074 | -0.01831 | 122.8363 | 122.7127 | 0.10529 | -0.045776 | 123.1155 | 122.8226 | 122.7539 | -0.45776 | 123.0331 | 123.0057 | 122.8226 | -0.44403
3519.0625 | 123.2117 | -122.818 | 0.17395 | -0.16846 | 0.030655 | 0.0048706 | 0.0076819 | -0.0096792 | 0.001788 | -0.0069427 | -0.24895 | -0.011914 | -0.00668 | -5.3406e-05 | 0.0053897 | -0.01358 | 0.1236 | 0.11902 | 0.064087 | 0.12817 | 0.35706 | 0.013733 | -0.12817 | 0.073242 | 0.15106 | -0.009155 | 0.27466 | 0.22888 | -0.086975 | -0.14191 | 122.8317 | 122.6898 | 0.18311 | 122.937 | 122.9462 | 0.25635 | -0.050354 | 122.731 | 122.6761 | 0.10071 | 122.8912 | 122.8088 | 0.13275 | 0.054932 | 123.175 | 122.9416 | 122.8821 | -0.30212 | 123.0927 | 123.0469 | 122.9691 | -0.31586
3520.7656 | 123.0972 | -122.8409 | 0.21057 | 0.12146 | 0.030869 | 0.0050842 | 0.0059729 | -0.0090384 | -0.00098918 | -0.0080109 | 0.20119 | -0.012341 | -0.0056118 | -0.0015488 | 0.0079531 | -0.014007 | 0 | 0.018311 | -0.036621 | -0.004578 | 0.24719 | -0.082397 | -0.23346 | 0.054932 | 0.064087 | -0.027466 | 0.17853 | 0.15106 | -0.16022 | -0.19684 | 122.7585 | 122.6074 | 0.036621 | 122.8592 | 122.8363 | 0.22888 | -0.21057 | 122.6807 | 122.644 | -0.032043 | 122.8958 | 122.8134 | 0.16937 | -0.059509 | 123.0881 | 122.8409 | 122.8043 | -0.44403 | 123.0194 | 122.9919 | 122.905 | -0.40741
3522.5312 | 123.1613 | -122.8226 | 0.1831 | -0.19897 | 0.030869 | 0.0082886 | 0.0093909 | -0.0066884 | -0.004407 | -0.0071563 | -0.23369 | -0.011914 | -0.0034756 | -0.0021896 | -0.00016447 | -0.014221 | 0.09613 | 0.14191 | 0.10529 | 0.1236 | 0.41657 | 0.027466 | -0.11444 | 0.086975 | 0.15106 | 0.027466 | 0.31586 | 0.26093 | -0.068665 | -0.13275 | 122.85 | 122.7081 | 0.23346 | 122.9645 | 122.9462 | 0.23804 | -0.086975 | 122.7539 | 122.6898 | 0.13275 | 122.9095 | 122.85 | 0.16022 | 0.07782 | 123.2391 | 122.9187 | 122.9279 | -0.29755 | 123.1384 | 123.0835 | 122.9736 | -0.31586
3524.2969 | 123.1979 | -122.8271 | 0.1831 | -0.24475 | 0.027664 | 0.006366 | 0.0076819 | -0.009252 | -0.0035526 | -0.0080109 | -0.2108 | -0.011487 | -0.0062528 | -0.0030442 | 0.0038943 | -0.015503 | 0.1236 | 0.13275 | 0.091553 | 0.13733 | 0.41199 | 0.041199 | -0.11444 | 0.059509 | 0.12817 | 0.018311 | 0.31128 | 0.27008 | -0.068665 | -0.14648 | 122.8683 | 122.7127 | 0.22888 | 122.9599 | 122.9645 | 0.25177 | -0.059509 | 122.7585 | 122.6807 | 0.12817 | 122.8867 | 122.8455 | 0.16479 | 0.086976 | 123.2391 | 122.9507 | 122.9187 | -0.29755 | 123.1384 | 123.0972 | 122.9553 | -0.32959
3526 | 123.0698 | -122.8592 | 0.21057 | 0.052795 | 0.032364 | 0.0076478 | 0.0051183 | -0.0094656 | 0.0022152 | -0.0050201 | 0.048599 | -0.0099911 | -0.0058254 | -0.001976 | 0.0088077 | -0.015716 | 0.004578 | 0 | -0.059509 | -0.004578 | 0.28381 | -0.064087 | -0.23346 | -0.018311 | 0.009155 | -0.11444 | 0.19226 | 0.17853 | -0.16479 | -0.21057 | 122.7951 | 122.6257 | 0.073242 | 122.8592 | 122.8546 | 0.22888 | -0.20599 | 122.6944 | 122.6486 | -0.01831 | 122.8409 | 122.7448 | 0.09613 | -0.032043 | 123.143 | 122.8638 | 122.7997 | -0.44403 | 123.0515 | 123.0377 | 122.8683 | -0.42114
3527.7656 | 123.1384 | -122.85 | 0.17853 | -0.17609 | 0.031296 | 0.0055114 | 0.0096045 | -0.0069022 | -0.006757 | -0.0082245 | -0.23369 | -0.012768 | -0.0034756 | -0.0024032 | 0.0026125 | -0.015716 | 0.14648 | 0.26093 | 0.18768 | 0.21515 | 0.35248 | 0.059509 | -0.10529 | 0.14648 | 0.24261 | 0.10986 | 0.28381 | 0.2655 | -0.050354 | -0.10071 | 122.9095 | 122.7448 | 0.17395 | 123.111 | 123.0652 | 0.32044 | -0.032044 | 122.7997 | 122.7493 | 0.10528 | 122.9965 | 122.9599 | 0.21057 | 0.086975 | 123.2025 | 122.9965 | 123.0377 | -0.28381 | 123.1338 | 123.1155 | 123.0927 | -0.27924
3529.5156 | 123.1842 | -122.8088 | 0.16937 | -0.13794 | 0.02916 | 0.0078614 | 0.0087499 | -0.0081838 | -0.0056888 | -0.0099335 | -0.12688 | -0.013623 | -0.0039028 | -0.0051804 | 0.0015445 | -0.013153 | 0.19226 | 0.29297 | 0.21973 | 0.20142 | 0.34332 | 0.073242 | -0.09613 | 0.20142 | 0.3067 | 0.1831 | 0.27924 | 0.21057 | -0.041199 | -0.059509 | 122.8821 | 122.7127 | 0.17395 | 123.1018 | 123.0103 | 0.29755 | 0.022888 | 122.7676 | 122.7493 | 0.10986 | 123.0103 | 122.9919 | 0.24261 | 0.041198 | 123.1522 | 123.0011 | 123.0286 | -0.2655 | 123.0881 | 123.0194 | 123.1155 | -0.22888
3531.2656 | 123.1567 | -122.8043 | 0.16479 | -0.19135 | 0.026383 | 0.0057252 | 0.0072547 | -0.008611 | -0.0031254 | -0.0086517 | -0.17265 | -0.01405 | -0.0073208 | -0.0068894 | 0.0036807 | -0.015075 | 0.2243 | 0.28381 | 0.20599 | 0.21515 | 0.36163 | 0.064087 | -0.073242 | 0.20599 | 0.28381 | 0.16479 | 0.27008 | 0.2243 | -0.022888 | -0.073242 | 122.8683 | 122.731 | 0.19684 | 123.0881 | 123.0194 | 0.28839 | 0.059509 | 122.7814 | 122.731 | 0.10529 | 123.0103 | 122.9691 | 0.23804 | 0.059509 | 123.1659 | 123.0286 | 123.0103 | -0.23804 | 123.0743 | 123.0286 | 123.0881 | -0.23804
3533.0469 | 123.0469 | -122.8409 | 0.20142 | 0.1825 | 0.031082 | 0.0061524 | 0.0031957 | -0.010106 | -0.00034818 | -0.0073701 | 0.15541 | -0.012555 | -0.0098844 | -0.0038986 | 0.0060305 | -0.016357 | 0.09613 | 0.12817 | 0.086975 | 0.059509 | 0.21515 | -0.064087 | -0.20142 | 0.14191 | 0.15564 | 0.036621 | 0.16937 | 0.12817 | -0.11444 | -0.16479 | 122.7768 | 122.6395 | 0.013733 | 122.9691 | 122.9004 | 0.26093 | -0.10529 | 122.7264 | 122.6761 | -0.032043 | 122.9828 | 122.8775 | 0.20142 | -0.073242 | 123.056 | 122.937 | 122.9279 | -0.40283 | 123.0103 | 122.9691 | 122.9965 | -0.36621
3534.8125 | 123.0606 | -122.8592 | 0.21057 | 0.045166 | 0.030441 | 0.0050842 | 0.0085363 | -0.0073294 | -0.002698 | -0.0097199 | 0.086746 | -0.013196 | -0.0062528 | -0.00048061 | 4.9132e-05 | -0.016571 | 0.10071 | 0.10529 | 0.10529 | 0.091553 | 0.29297 | 0.009155 | -0.16022 | 0.11444 | 0.14648 | 0.091553 | 0.24719 | 0.21515 | -0.082397 | -0.13733 | 122.8683 | 122.699 | 0.082398 | 122.9645 | 122.9507 | 0.25177 | -0.10986 | 122.7768 | 122.7219 | 0.036621 | 122.9736 | 122.9507 | 0.22888 | 0.004578 | 123.1522 | 122.9599 | 122.9645 | -0.37079 | 123.1064 | 123.0743 | 123.0057 | -0.3479
3536.5781 | 123.1567 | -122.8134 | 0.19684 | -0.2066 | 0.030441 | 0.0065796 | 0.0089635 | -0.0071158 | 0.0030698 | -0.0086517 | -0.26421 | -0.011914 | -0.0051846 | -0.0021896 | 0.0026125 | -0.017212 | 0.15106 | 0.12817 | 0.082397 | 0.13733 | 0.40741 | 0.045776 | -0.11902 | 0.11444 | 0.14648 | 0.032043 | 0.32959 | 0.27924 | -0.082397 | -0.1236 | 122.8592 | 122.6944 | 0.21057 | 122.9416 | 122.9507 | 0.25635 | -0.045776 | 122.731 | 122.6898 | 0.13275 | 122.9279 | 122.8455 | 0.15564 | 0.082398 | 123.2208 | 122.9645 | 122.8958 | -0.31586 | 123.143 | 123.0927 | 122.9599 | -0.32043
3538.2812 | 123.111 | -122.8271 | 0.20599 | 0.1062 | 0.032578 | 0.0065796 | 0.0014867 | -0.0083974 | 0.0043514 | -0.0080109 | 0.10963 | -0.010205 | -0.0071072 | -0.00090781 | 0.0075259 | -0.016143 | 0.041199 | 0 | -0.041199 | 0.009155 | 0.28381 | -0.068665 | -0.25177 | 0.045776 | 0.032043 | -0.054932 | 0.19684 | 0.13275 | -0.15564 | -0.20142 | 122.7585 | 122.5754 | 0.077819 | 122.8271 | 122.8363 | 0.26093 | -0.1648 | 122.6715 | 122.6257 | -0.009156 | 122.8729 | 122.7722 | 0.14648 | -0.073243 | 123.111 | 122.8683 | 122.7859 | -0.45776 | 123.024 | 122.9599 | 122.8592 | -0.40741
3540.0312 | 123.0927 | -122.85 | 0.18768 | 0.045166 | 0.028305 | 0.0067932 | 0.0064001 | -0.0083974 | -0.0054752 | -0.0073701 | 0.079117 | -0.013623 | -0.011593 | -0.0032578 | 0.0032535 | -0.012726 | 0.10529 | 0.13275 | 0.1236 | 0.11444 | 0.29297 | 0.004578 | -0.14191 | 0.13733 | 0.16937 | 0.09613 | 0.25635 | 0.21057 | -0.073242 | -0.10986 | 122.8546 | 122.7081 | 0.10529 | 122.9828 | 122.9645 | 0.25635 | -0.082397 | 122.7768 | 122.7402 | 0.068665 | 122.9874 | 122.9462 | 0.20599 | 0.022888 | 123.143 | 122.9553 | 122.9736 | -0.32959 | 123.1064 | 123.0606 | 123.0194 | -0.29755
3541.8125 | 123.1522 | -122.8271 | 0.17395 | -0.19897 | 0.029373 | 0.0070068 | 0.0066137 | -0.0079702 | -0.004407 | -0.0088653 | -0.21843 | -0.013196 | -0.00668 | -0.0049668 | 0.0028263 | -0.018493 | 0.21515 | 0.23346 | 0.1831 | 0.19684 | 0.34332 | 0.064087 | -0.091553 | 0.15564 | 0.24261 | 0.10529 | 0.27008 | 0.26093 | -0.036621 | -0.091553 | 122.8912 | 122.7356 | 0.16937 | 123.0606 | 123.024 | 0.28839 | 0.041199 | 122.7905 | 122.7356 | 0.096131 | 122.9828 | 122.9324 | 0.19684 | 0.086975 | 123.1705 | 123.0423 | 123.0103 | -0.2655 | 123.0972 | 123.0881 | 123.0698 | -0.2655
3543.5781 | 123.1476 | -122.8043 | 0.1831 | -0.17609 | 0.031082 | 0.0067932 | 0.010459 | -0.0088248 | -0.0024844 | -0.0090791 | -0.2108 | -0.013196 | -0.0062528 | -0.0015488 | 0.0019717 | -0.015716 | 0.21515 | 0.24261 | 0.19226 | 0.20599 | 0.35706 | 0.059509 | -0.10986 | 0.19226 | 0.27008 | 0.13275 | 0.27008 | 0.25635 | -0.045776 | -0.091553 | 122.8638 | 122.6944 | 0.17395 | 123.0469 | 123.0103 | 0.31586 | 0.032044 | 122.7585 | 122.7127 | 0.086976 | 122.9965 | 122.937 | 0.2243 | 0.073243 | 123.1613 | 123.0194 | 122.9965 | -0.29297 | 123.0743 | 123.0606 | 123.0743 | -0.27466
3545.2812 | 123.0835 | -122.8271 | 0.21515 | 0.20538 | 0.030228 | 0.006366 | 0.0061865 | -0.0096792 | 0.0028562 | -0.0090791 | 0.17067 | -0.010418 | -0.0073208 | 0.00080099 | 0.0045351 | -0.018066 | 0.12817 | 0.09613 | 0.073242 | 0.068665 | 0.2243 | -0.050354 | -0.22888 | 0.11902 | 0.13733 | 0.018311 | 0.13733 | 0.11444 | -0.15106 | -0.1831 | 122.7768 | 122.5983 | 0.009155 | 122.9233 | 122.8958 | 0.29755 | -0.086975 | 122.6761 | 122.644 | -0.07782 | 122.9462 | 122.8455 | 0.20142 | -0.10071 | 123.0515 | 122.9553 | 122.9004 | -0.44403 | 122.9645 | 122.9416 | 122.9645 | -0.39825
3546.9844 | 123.1522 | -122.8043 | 0.19684 | -0.22949 | 0.033005 | 0.0038024 | 0.0096045 | -0.0090384 | -0.0022708 | -0.0075837 | -0.21843 | -0.012341 | -0.0051846 | -0.00069421 | 0.0045351 | -0.016143 | 0.18768 | 0.20142 | 0.13733 | 0.16479 | 0.39368 | 0.059509 | -0.11444 | 0.10529 | 0.17853 | 0.036621 | 0.3067 | 0.26093 | -0.064087 | -0.10986 | 122.8638 | 122.6898 | 0.19684 | 123.0057 | 122.9691 | 0.27924 | -0.009155 | 122.7402 | 122.6944 | 0.10986 | 122.9095 | 122.8409 | 0.14648 | 0.064087 | 123.1979 | 122.9919 | 122.9416 | -0.31128 | 123.111 | 123.0652 | 122.9828 | -0.3067
3548.75 | 123.143 | -122.8134 | 0.1831 | -0.092163 | 0.033432 | 0.0059388 | 0.0046911 | -0.0083974 | 0.0039242 | -0.0048065 | -0.16502 | -0.0095639 | -0.00668 | -0.00090781 | 0.0079531 | -0.017425 | 0.14191 | 0.11444 | 0.041199 | 0.086975 | 0.32044 | -0.018311 | -0.18768 | 0.11444 | 0.11444 | -0.041199 | 0.23346 | 0.18768 | -0.13275 | -0.19226 | 122.7951 | 122.6257 | 0.13733 | 122.9279 | 122.9004 | 0.27466 | -0.041198 | 122.6807 | 122.6212 | 0.050354 | 122.9279 | 122.7722 | 0.15106 | 0.004578 | 123.1339 | 122.9553 | 122.8546 | -0.37079 | 123.0469 | 123.0011 | 122.9279 | -0.37537
3550.5312 | 123.0698 | -122.8683 | 0.20599 | 0.052795 | 0.0345 | 0.0052978 | 0.0066137 | -0.010534 | 0.0047788 | -0.0077973 | -0.020065 | -0.0097775 | -0.0058254 | -0.001976 | 0.0060305 | -0.015716 | 0.013733 | -0.009155 | -0.064087 | 0.004578 | 0.28381 | -0.082397 | -0.22888 | 0 | 0.022888 | -0.11444 | 0.21057 | 0.16937 | -0.17395 | -0.2243 | 122.7859 | 122.6395 | 0.077819 | 122.8592 | 122.8729 | 0.23346 | -0.19226 | 122.6944 | 122.644 | 0.004577 | 122.8683 | 122.7539 | 0.10986 | -0.036621 | 123.1522 | 122.8821 | 122.8043 | -0.43488 | 123.0789 | 123.0377 | 122.8912 | -0.4303
3552.2344 | 123.1888 | -122.8226 | 0.1831 | -0.2066 | 0.032578 | 0.006366 | 0.0098181 | -0.0098928 | 7.902e-05 | -0.0058747 | -0.2108 | -0.011914 | -0.0062528 | -0.0021896 | 0.0068851 | -0.016784 | 0.10529 | 0.13733 | 0.064087 | 0.11444 | 0.37537 | 0.004578 | -0.16479 | 0.082397 | 0.14648 | 0.009155 | 0.25635 | 0.21973 | -0.10986 | -0.16937 | 122.8271 | 122.6578 | 0.19226 | 122.9599 | 122.937 | 0.27924 | -0.077819 | 122.7127 | 122.6532 | 0.073243 | 122.905 | 122.8317 | 0.17853 | 0.036622 | 123.1979 | 122.9279 | 122.8867 | -0.3479 | 123.0789 | 123.0423 | 122.9691 | -0.35248
3554.0156 | 123.175 | -122.7859 | 0.17395 | -0.076904 | 0.028305 | 0.0057252 | 0.0093909 | -0.007543 | -0.006757 | -0.0077973 | -0.081101 | -0.012768 | -0.0071072 | -0.0026168 | 0.00068993 | -0.014862 | 0.16022 | 0.20142 | 0.1831 | 0.15564 | 0.33875 | 0.045776 | -0.11444 | 0.21973 | 0.27466 | 0.17395 | 0.2655 | 0.25177 | -0.050354 | -0.082397 | 122.8317 | 122.6715 | 0.1648 | 122.9874 | 122.9416 | 0.27008 | -0.013733 | 122.7356 | 122.7036 | 0.091553 | 123.0057 | 122.9599 | 0.25635 | 0.07782 | 123.1247 | 122.9462 | 122.9691 | -0.28839 | 123.0515 | 123.0377 | 123.0606 | -0.25635
3555.7812 | 123.1842 | -122.7814 | 0.16937 | -0.076904 | 0.030441 | 0.006366 | 0.010245 | -0.010106 | -0.008466 | -0.0097199 | -0.058212 | -0.012768 | -0.004971 | -0.00048061 | -0.00037807 | -0.015503 | 0.17853 | 0.21973 | 0.17395 | 0.17853 | 0.3479 | 0.027466 | -0.11902 | 0.20599 | 0.27008 | 0.17853 | 0.26093 | 0.21515 | -0.032043 | -0.091553 | 122.8088 | 122.6624 | 0.17853 | 123.0011 | 122.9599 | 0.29755 | 0.009155 | 122.7493 | 122.6898 | 0.091552 | 122.9874 | 122.9599 | 0.27008 | 0.045776 | 123.1293 | 122.9599 | 122.9553 | -0.28839 | 123.0423 | 122.9965 | 123.0515 | -0.26093
3557.4844 | 123.1201 | -122.85 | 0.19684 | 0.11383 | 0.030014 | 0.0042298 | 0.0040503 | -0.0083974 | 0.003497 | -0.0060883 | 0.063858 | -0.0097775 | -0.004971 | -0.00026701 | 0.0066715 | -0.016998 | 0.041199 | -0.004578 | -0.041199 | 0.004578 | 0.27466 | -0.07782 | -0.24719 | 0.018311 | 0.018311 | -0.068665 | 0.20142 | 0.14191 | -0.16479 | -0.19684 | 122.7722 | 122.6028 | 0.07782 | 122.8455 | 122.8546 | 0.25177 | -0.15564 | 122.6852 | 122.6532 | 0.004578 | 122.8683 | 122.7814 | 0.12817 | -0.054931 | 123.1247 | 122.8912 | 122.8088 | -0.44403 | 123.0515 | 122.9919 | 122.8683 | -0.39368
3559.2344 | 123.1155 | -122.8409 | 0.19226 | 0.17487 | 0.031082 | 0.002948 | 0.0046911 | -0.0088248 | 0.00050622 | -0.0067291 | 0.19356 | -0.010418 | -0.004971 | -0.00069421 | 0.0062441 | -0.016784 | 0.041199 | 0.027466 | -0.013733 | -0.004578 | 0.24261 | -0.064087 | -0.21973 | 0.10071 | 0.10986 | -0.004578 | 0.16937 | 0.15564 | -0.14648 | -0.17853 | 122.7768 | 122.6212 | 0.050354 | 122.8683 | 122.8363 | 0.21515 | -0.15106 | 122.6944 | 122.6624 | -0.022888 | 122.9416 | 122.8363 | 0.17395 | -0.036621 | 123.0835 | 122.8821 | 122.8271 | -0.41199 | 123.0103 | 122.9965 | 122.9507 | -0.37079
3560.9844 | 123.0698 | -122.8271 | 0.20142 | 0.13672 | 0.02681 | 0.0076478 | 0.0055457 | -0.010961 | -0.004407 | -0.0082245 | 0.11726 | -0.014477 | -0.0075344 | -0.0026168 | 0.0034671 | -0.014007 | 0.068665 | 0.11444 | 0.082397 | 0.073242 | 0.25177 | -0.032043 | -0.19226 | 0.13275 | 0.16022 | 0.07782 | 0.21515 | 0.1831 | -0.059509 | -0.14191 | 122.7951 | 122.6349 | 0.050354 | 122.9416 | 122.9004 | 0.2655 | -0.13275 | 122.7676 | 122.6852 | 0.013733 | 122.9599 | 122.905 | 0.21973 | -0.018311 | 123.0789 | 122.8958 | 122.9095 | -0.39368 | 123.0423 | 123.0103 | 122.9874 | -0.34332
3562.6875 | 123.0698 | -122.8546 | 0.20142 | 0.075684 | 0.034073 | 0.0059388 | 0.0042639 | -0.0090384 | 0.0013608 | -0.0063019 | 0.071487 | -0.0097775 | -0.007748 | -0.0013352 | 0.0083805 | -0.017212 | 0.018311 | -0.022888 | -0.07782 | -0.022888 | 0.29755 | -0.073242 | -0.24261 | 0 | -0.004578 | -0.10529 | 0.16479 | 0.16937 | -0.15106 | -0.21973 | 122.7814 | 122.612 | 0.09613 | 122.8317 | 122.8317 | 0.21973 | -0.18311 | 122.7036 | 122.6349 | -0.036621 | 122.8546 | 122.7493 | 0.11444 | -0.032043 | 123.1522 | 122.8729 | 122.7768 | -0.44403 | 123.0194 | 123.024 | 122.85 | -0.42114
3564.4531 | 123.0927 | -122.8775 | 0.19684 | -0.099793 | 0.034714 | 0.004657 | 0.0042639 | -0.0096792 | 0.0032834 | -0.0069427 | -0.10399 | -0.0099911 | -0.0090298 | -0.0028306 | 0.0073123 | -0.014435 | 0.11444 | 0.11444 | 0.036621 | 0.07782 | 0.31128 | -0.036621 | -0.17853 | 0.064087 | 0.10071 | -0.059509 | 0.21973 | 0.15564 | -0.11902 | -0.1831 | 122.8409 | 122.699 | 0.11444 | 122.9919 | 122.9553 | 0.25635 | -0.082397 | 122.7585 | 122.6944 | 0.022889 | 122.9416 | 122.818 | 0.1236 | -0.041198 | 123.1888 | 122.9919 | 122.9141 | -0.37537 | 123.0972 | 123.0331 | 122.9782 | -0.37994
3566.2188 | 123.0743 | -122.8546 | 0.2243 | -0.069275 | 0.035141 | 0.0040162 | 0.0066137 | -0.0060476 | 0.0015744 | -0.0052337 | -0.042954 | -0.011914 | -0.0071072 | -0.0017624 | 0.0068851 | -0.016143 | 0.091553 | 0.10529 | 0.027466 | 0.068665 | 0.32959 | -0.050354 | -0.20142 | 0.036621 | 0.068665 | -0.068665 | 0.21973 | 0.1831 | -0.13275 | -0.20599 | 122.8043 | 122.6532 | 0.10529 | 122.9599 | 122.9233 | 0.27008 | -0.13275 | 122.7219 | 122.6486 | -0.004577 | 122.8912 | 122.7859 | 0.13733 | -0.041199 | 123.1842 | 122.9462 | 122.8821 | -0.42572 | 123.0743 | 123.0377 | 122.9233 | -0.4303
3568.0156 | 123.0606 | -122.8546 | 0.19226 | -0.031128 | 0.032364 | 0.0057252 | 0.0070409 | -0.0088248 | 0.0020016 | -0.0082245 | 0.04097 | -0.0097775 | -0.0068936 | -0.0021896 | 0.0075259 | -0.016784 | 0.036621 | 0.050354 | -0.022888 | 0.013733 | 0.28381 | -0.059509 | -0.22888 | -0.004578 | 0.018311 | -0.10986 | 0.21057 | 0.15564 | -0.16937 | -0.2243 | 122.7951 | 122.6257 | 0.091552 | 122.905 | 122.8683 | 0.24261 | -0.15564 | 122.6852 | 122.6303 | 0.01831 | 122.85 | 122.7448 | 0.11444 | -0.036621 | 123.1384 | 122.8912 | 122.8317 | -0.42114 | 123.0652 | 123.0103 | 122.8729 | -0.41656
3569.7656 | 123.0469 | -122.8546 | 0.20142 | 0.15961 | 0.030228 | 0.008075 | 0.0074683 | -0.010534 | -0.0035526 | -0.0054475 | 0.17067 | -0.014477 | -0.006039 | -0.0034714 | 0.0060305 | -0.013794 | 0.050354 | 0.14648 | 0.082397 | 0.068665 | 0.21515 | -0.045776 | -0.20599 | 0.10071 | 0.16479 | 0.050354 | 0.1831 | 0.13733 | -0.1236 | -0.16937 | 122.8088 | 122.6486 | 0.013733 | 123.0011 | 122.9233 | 0.27466 | -0.15106 | 122.731 | 122.6852 | -0.018311 | 122.9553 | 122.905 | 0.21973 | -0.064087 | 123.0698 | 122.905 | 122.937 | -0.40741 | 123.0377 | 122.9919 | 123.0194 | -0.37079
3571.5156 | 123.0652 | -122.8592 | 0.20599 | 0.12146 | 0.030014 | 0.0087158 | 0.0072547 | -0.0083974 | -0.005048 | -0.0092927 | 0.16304 | -0.010418 | -0.0064664 | -0.0030442 | 0.0021853 | -0.012085 | 0.086975 | 0.14648 | 0.091553 | 0.086975 | 0.23804 | -0.027466 | -0.18768 | 0.11444 | 0.16022 | 0.064087 | 0.19684 | 0.15106 | -0.10071 | -0.16022 | 122.8317 | 122.6715 | 0.032043 | 123.0057 | 122.9462 | 0.27466 | -0.11902 | 122.7585 | 122.699 | -0.009156 | 122.9736 | 122.9233 | 0.2243 | -0.054932 | 123.0972 | 122.9462 | 122.9507 | -0.39368 | 123.056 | 123.0103 | 123.0194 | -0.36621
3573.2188 | 123.0652 | -122.8455 | 0.21973 | 0.068054 | 0.035355 | 0.0044434 | 0.0064001 | -0.0098928 | 0.0024288 | -0.0060883 | 0.018082 | -0.0095639 | -0.00668 | -0.0028306 | 0.0073123 | -0.019134 | 0.032043 | -0.027466 | -0.045776 | 0 | 0.30212 | -0.07782 | -0.23804 | -0.022888 | -0.004578 | -0.13275 | 0.20599 | 0.16479 | -0.17395 | -0.21515 | 122.7676 | 122.6074 | 0.082397 | 122.818 | 122.8455 | 0.23804 | -0.18768 | 122.6715 | 122.6303 | -0.013733 | 122.8226 | 122.7127 | 0.082398 | -0.054932 | 123.1476 | 122.8775 | 122.7997 | -0.45776 | 123.0515 | 123.0103 | 122.8409 | -0.43488
3574.9844 | 123.143 | -122.8317 | 0.17853 | 0.0070193 | 0.028092 | 0.0076478 | 0.010032 | -0.010106 | -0.0093204 | -0.0090791 | 0.086746 | -0.013196 | -0.0086026 | -0.0026168 | 0.0013309 | -0.01358 | 0.07782 | 0.14648 | 0.10529 | 0.09613 | 0.32959 | 0.004578 | -0.15564 | 0.10986 | 0.1831 | 0.10071 | 0.25635 | 0.21057 | -0.09613 | -0.1236 | 122.8363 | 122.6761 | 0.15106 | 122.9782 | 122.9279 | 0.25177 | -0.10071 | 122.7356 | 122.7081 | 0.07782 | 122.9416 | 122.9324 | 0.2243 | 0.032043 | 123.1613 | 122.9095 | 122.937 | -0.33417 | 123.0881 | 123.0423 | 123.0148 | -0.30212
3576.7344 | 123.1567 | -122.8043 | 0.19226 | -0.18372 | 0.027664 | 0.006366 | 0.010245 | -0.0090384 | -0.0022708 | -0.010574 | -0.14977 | -0.01405 | -0.004971 | -0.0013352 | 0.00047633 | -0.016143 | 0.2243 | 0.25635 | 0.21515 | 0.20142 | 0.36163 | 0.07782 | -0.091553 | 0.19684 | 0.27466 | 0.14191 | 0.25635 | 0.23346 | -0.032043 | -0.082397 | 122.8821 | 122.7127 | 0.16937 | 123.0606 | 123.0057 | 0.29297 | 0.032043 | 122.7722 | 122.7219 | 0.064087 | 123.0011 | 122.9462 | 0.2243 | 0.041198 | 123.1659 | 123.0286 | 123.0194 | -0.28381 | 123.0606 | 123.0377 | 123.0789 | -0.27466
3578.5 | 123.1888 | -122.8271 | 0.17853 | -0.18372 | 0.033005 | 0.0038024 | 0.0078955 | -0.0071158 | 0.00029262 | -0.0082245 | -0.20317 | -0.011059 | -0.0068936 | -0.0024032 | 0.0060305 | -0.016571 | 0.13733 | 0.11444 | 0.054932 | 0.13275 | 0.37537 | 0.018311 | -0.14191 | 0.07782 | 0.13275 | -0.013733 | 0.27008 | 0.21973 | -0.1236 | -0.16479 | 122.8455 | 122.6852 | 0.19684 | 122.9416 | 122.9599 | 0.27466 | -0.041199 | 122.7036 | 122.6624 | 0.091553 | 122.905 | 122.8134 | 0.15106 | 0.041199 | 123.2025 | 122.9645 | 122.8821 | -0.32044 | 123.0972 | 123.0469 | 122.9599 | -0.34332
3580.2656 | 123.1018 | -122.8455 | 0.19684 | 0.20538 | 0.030441 | 0.0061524 | 0.0038367 | -0.0083974 | -0.00034818 | -0.0075837 | 0.14015 | -0.012768 | -0.0071072 | -0.0013352 | 0.0070987 | -0.014648 | 0.036621 | 0.041199 | -0.009155 | 0.013733 | 0.23346 | -0.073242 | -0.23804 | 0.09613 | 0.10071 | 0.013733 | 0.15564 | 0.12817 | -0.1236 | -0.18768 | 122.7722 | 122.6074 | 0.036621 | 122.8867 | 122.8592 | 0.25177 | -0.16022 | 122.7219 | 122.6578 | -0.041198 | 122.9416 | 122.8592 | 0.20142 | -0.068664 | 123.0789 | 122.8821 | 122.8363 | -0.43488 | 123.0011 | 122.9736 | 122.9462 | -0.38452
3582.0312 | 123.1155 | -122.85 | 0.21057 | 0.12146 | 0.030655 | 0.0050842 | 0.0068273 | -0.0066884 | 0.0020016 | -0.0067291 | 0.071487 | -0.011059 | -0.0090298 | 0.00037379 | 0.0049625 | -0.01593 | 0.013733 | -0.018311 | -0.064087 | -0.009155 | 0.26093 | -0.09613 | -0.25177 | 0.050354 | 0.013733 | -0.068665 | 0.20142 | 0.16479 | -0.15106 | -0.21057 | 122.7539 | 122.5983 | 0.050354 | 122.8317 | 122.8409 | 0.24261 | -0.19684 | 122.699 | 122.6395 | -0.009155 | 122.9004 | 122.7814 | 0.14191 | -0.045776 | 123.111 | 122.8638 | 122.7859 | -0.46234 | 123.0515 | 123.0148 | 122.8638 | -0.42114
3583.7969 | 123.1476 | -122.8271 | 0.16937 | -0.21423 | 0.030869 | 0.0072204 | 0.0093909 | -0.0066884 | -0.002698 | -0.0084381 | -0.23369 | -0.013409 | -0.0073208 | -0.0011216 | 0.0017581 | -0.015503 | 0.11444 | 0.14648 | 0.09613 | 0.1236 | 0.41657 | 0.045776 | -0.12817 | 0.091553 | 0.16022 | 0.027466 | 0.31128 | 0.28381 | -0.082397 | -0.13275 | 122.8729 | 122.699 | 0.24719 | 122.9736 | 122.9507 | 0.25177 | -0.054932 | 122.7448 | 122.6944 | 0.14191 | 122.9187 | 122.8546 | 0.16022 | 0.11444 | 123.2437 | 122.9416 | 122.9233 | -0.29755 | 123.1384 | 123.111 | 122.9874 | -0.30212
3585.5 | 123.1155 | -122.85 | 0.19684 | 0.12909 | 0.033646 | 0.0038024 | 0.0055457 | -0.0062612 | 0.00093342 | -0.0075837 | 0.063858 | -0.011914 | -0.0030484 | -0.0017624 | 0.0075259 | -0.018066 | -0.004578 | -0.022888 | -0.073242 | -0.013733 | 0.2655 | -0.068665 | -0.25177 | 0.009155 | 0.018311 | -0.086975 | 0.20142 | 0.16937 | -0.15564 | -0.23346 | 122.7814 | 122.5983 | 0.068665 | 122.8271 | 122.8363 | 0.23804 | -0.20142 | 122.6944 | 122.6166 | 0.004578 | 122.8592 | 122.7631 | 0.14648 | -0.027465 | 123.1155 | 122.8455 | 122.7768 | -0.44861 | 123.0515 | 123.0194 | 122.8683 | -0.4303
3587.2656 | 123.143 | -122.818 | 0.17853 | -0.1532 | 0.030869 | 0.0082886 | 0.0068273 | -0.0083974 | -0.0029118 | -0.0097199 | -0.19554 | -0.014905 | -0.0056118 | -0.0032578 | 0.0030399 | -0.01593 | 0.17395 | 0.25177 | 0.18768 | 0.19684 | 0.3479 | 0.050354 | -0.10986 | 0.16022 | 0.26093 | 0.10529 | 0.27924 | 0.25177 | -0.059509 | -0.091553 | 122.8683 | 122.7081 | 0.16937 | 123.0698 | 123.0148 | 0.3067 | -0.004578 | 122.7585 | 122.7264 | 0.10071 | 122.9782 | 122.9233 | 0.19684 | 0.073242 | 123.1659 | 122.9919 | 123.0057 | -0.28839 | 123.0972 | 123.0698 | 123.0789 | -0.27008
3588.9688 | 123.1842 | -122.8271 | 0.16479 | -0.11505 | 0.032364 | 0.0044434 | 0.0042639 | -0.009252 | 0.0020016 | -0.0086517 | -0.14214 | -0.012127 | -0.0062528 | -0.0032578 | 0.0075259 | -0.015716 | 0.11902 | 0.11902 | 0.054932 | 0.09613 | 0.34332 | -0.013733 | -0.17853 | 0.07782 | 0.1236 | -0.009155 | 0.24261 | 0.19684 | -0.11444 | -0.16479 | 122.8134 | 122.6486 | 0.17853 | 122.9462 | 122.9233 | 0.27466 | -0.045776 | 122.7127 | 122.6624 | 0.07782 | 122.905 | 122.818 | 0.15564 | 0.032043 | 123.1705 | 122.9462 | 122.8821 | -0.34332 | 123.0698 | 123.024 | 122.9507 | -0.32959
3590.7344 | 123.1888 | -122.818 | 0.18768 | -0.099793 | 0.034287 | 0.004657 | 0.0064001 | -0.0098928 | 0.00050622 | -0.0043793 | -0.11162 | -0.010418 | -0.0088162 | -0.001976 | 0.0056033 | -0.017639 | 0.11444 | 0.12817 | 0.045776 | 0.11444 | 0.34332 | -0.013733 | -0.17853 | 0.086975 | 0.1236 | -0.013733 | 0.24261 | 0.21057 | -0.11444 | -0.16937 | 122.8043 | 122.6395 | 0.15564 | 122.9462 | 122.9324 | 0.29297 | -0.073242 | 122.7036 | 122.6486 | 0.054932 | 122.905 | 122.8043 | 0.15564 | 0.022888 | 123.1613 | 122.9324 | 122.8638 | -0.36621 | 123.0606 | 123.0286 | 122.9416 | -0.35706
3592.5 | 123.0835 | -122.8088 | 0.19684 | -0.015869 | 0.026383 | 0.007434 | 0.0083227 | -0.011602 | -0.0059024 | -0.0069427 | 0.11726 | -0.013409 | -0.0071072 | -0.0013352 | 0.0023989 | -0.014435 | 0.073242 | 0.13733 | 0.10529 | 0.091553 | 0.32501 | -0.004578 | -0.15564 | 0.10529 | 0.16937 | 0.086975 | 0.23804 | 0.17853 | -0.086975 | -0.13275 | 122.8043 | 122.6532 | 0.12817 | 122.9462 | 122.9004 | 0.24719 | -0.1236 | 122.7219 | 122.6761 | 0.041199 | 122.9141 | 122.8958 | 0.21973 | -0.01831 | 123.1338 | 122.8821 | 122.9141 | -0.35248 | 123.0469 | 122.9874 | 122.9782 | -0.32959
3594.25 | 123.0743 | -122.8592 | 0.19684 | 0.15961 | 0.029587 | 0.0072204 | 0.0036231 | -0.0073294 | -0.00163 | -0.0069427 | 0.18593 | -0.0117 | -0.0071072 | -0.0049668 | 0.0051761 | -0.016357 | 0.086975 | 0.11902 | 0.068665 | 0.064087 | 0.20142 | -0.045776 | -0.21515 | 0.11444 | 0.14191 | 0.045776 | 0.16937 | 0.10986 | -0.14648 | -0.18768 | 122.8134 | 122.644 | 0.004578 | 122.9782 | 122.9233 | 0.27924 | -0.10986 | 122.7127 | 122.6715 | -0.027465 | 122.9736 | 122.905 | 0.23346 | -0.086975 | 123.0606 | 122.9462 | 122.9279 | -0.41199 | 123.0286 | 122.9691 | 123.0011 | -0.38452
3596.0156 | 123.1659 | -122.8409 | 0.19684 | 0.022278 | 0.030655 | 0.004657 | 0.010886 | -0.009252 | -0.0054752 | -0.010574 | 0.048599 | -0.012768 | -0.0045438 | -0.0017624 | 0.00026273 | -0.016143 | 0.09613 | 0.13275 | 0.10529 | 0.11444 | 0.32959 | 0.013733 | -0.14191 | 0.1236 | 0.16937 | 0.10529 | 0.23804 | 0.20142 | -0.091553 | -0.11444 | 122.8546 | 122.699 | 0.13275 | 122.9736 | 122.9553 | 0.25635 | -0.10071 | 122.7493 | 122.7264 | 0.041199 | 122.9645 | 122.9462 | 0.21973 | 0.004578 | 123.1705 | 122.937 | 122.9462 | -0.33875 | 123.0789 | 123.0423 | 123.0103 | -0.31128
3597.7188 | 123.0652 | -122.85 | 0.20599 | 0.068054 | 0.026383 | 0.0042298 | 0.0085363 | -0.0096792 | -0.0035526 | -0.010574 | 0.048599 | -0.011487 | -0.008389 | -0.00026701 | 0.0023989 | -0.01593 | 0.12817 | 0.10529 | 0.07782 | 0.082397 | 0.28381 | 0 | -0.16022 | 0.12817 | 0.14191 | 0.073242 | 0.23804 | 0.20142 | -0.07782 | -0.13275 | 122.85 | 122.6898 | 0.077819 | 122.9553 | 122.9324 | 0.24261 | -0.07782 | 122.7722 | 122.7173 | 0.032043 | 122.9782 | 122.9233 | 0.20599 | -0.004578 | 123.1338 | 122.9782 | 122.9279 | -0.36621 | 123.0881 | 123.0515 | 122.9919 | -0.33875
3599.4688 | 123.1064 | -122.8363 | 0.19684 | 0.022278 | 0.02681 | 0.0082886 | 0.0061865 | -0.0090384 | -0.0056888 | -0.010574 | 0.063858 | -0.012982 | -0.0071072 | -0.0030442 | 0.0062441 | -0.014862 | 0.10986 | 0.11444 | 0.10071 | 0.11902 | 0.32501 | 0.022888 | -0.16937 | 0.11444 | 0.16479 | 0.091553 | 0.26093 | 0.19226 | -0.059509 | -0.13275 | 122.8592 | 122.6669 | 0.12817 | 122.9507 | 122.9553 | 0.28839 | -0.086975 | 122.7768 | 122.7036 | 0.064087 | 122.9507 | 122.9279 | 0.2243 | -0.004577 | 123.1613 | 122.9462 | 122.937 | -0.36621 | 123.0972 | 123.0286 | 123.0011 | -0.32959
3601.2188 | 123.1842 | -122.8134 | 0.1831 | -0.16083 | 0.025314 | 0.007434 | 0.0053321 | -0.009252 | -0.004407 | -0.0090791 | -0.042954 | -0.013836 | -0.0073208 | -0.001976 | 0.0051761 | -0.016998 | 0.23804 | 0.24719 | 0.20142 | 0.18768 | 0.36621 | 0.068665 | -0.10529 | 0.23346 | 0.29297 | 0.16937 | 0.26093 | 0.22888 | -0.027466 | -0.07782 | 122.8821 | 122.7081 | 0.18311 | 123.0606 | 123.0011 | 0.29297 | 0.054932 | 122.7859 | 122.7356 | 0.07782 | 123.0469 | 122.9828 | 0.24719 | 0.045777 | 123.1796 | 123.0515 | 123.0148 | -0.28839 | 123.0743 | 123.0423 | 123.1064 | -0.26092
3602.9219 | 123.1659 | -122.7768 | 0.19684 | -0.015869 | 0.028946 | 0.0050842 | 0.0031957 | -0.0071158 | -0.0041934 | -0.0077973 | -0.027695 | -0.013196 | -0.0081754 | -0.0024032 | 0.0047489 | -0.01593 | 0.14191 | 0.13733 | 0.11902 | 0.11902 | 0.32044 | 0.022888 | -0.14648 | 0.16937 | 0.20599 | 0.12817 | 0.25177 | 0.20599 | -0.059509 | -0.12817 | 122.7997 | 122.6303 | 0.1236 | 122.9141 | 122.8958 | 0.2655 | -0.054931 | 122.7173 | 122.6486 | 0.054932 | 122.9462 | 122.905 | 0.25635 | 0.009156 | 123.0972 | 122.9187 | 122.8958 | -0.34332 | 123.0286 | 122.9828 | 122.9828 | -0.32501
3604.6719 | 123.111 | -122.8683 | 0.20599 | 0.13672 | 0.034714 | 0.0065796 | 0.0036231 | -0.010534 | 0.006915 | -0.0054475 | 0.025711 | -0.010205 | -0.0058254 | -0.00069421 | 0.0096621 | -0.018066 | 0.059509 | -0.036621 | -0.068665 | -0.018311 | 0.27466 | -0.10071 | -0.24261 | 0.050354 | 0.022888 | -0.091553 | 0.20142 | 0.17395 | -0.17395 | -0.21057 | 122.7676 | 122.6257 | 0.068664 | 122.8317 | 122.85 | 0.2243 | -0.14649 | 122.6944 | 122.6578 | -0.004578 | 122.9187 | 122.7768 | 0.11902 | -0.032044 | 123.143 | 122.9279 | 122.7997 | -0.44861 | 123.0698 | 123.0423 | 122.8912 | -0.41657
3606.375 | 123.1796 | -122.8317 | 0.1831 | -0.11505 | 0.033859 | 0.002948 | 0.0078955 | -0.0062612 | 0.0037106 | -0.0052337 | -0.21843 | -0.011273 | -0.0039028 | -0.00069421 | 0.0056033 | -0.016784 | 0.16479 | 0.10986 | 0.054932 | 0.10529 | 0.35706 | -0.027466 | -0.17853 | 0.10529 | 0.13733 | -0.027466 | 0.22888 | 0.20599 | -0.12817 | -0.16022 | 122.8043 | 122.6532 | 0.17395 | 122.9416 | 122.937 | 0.28381 | -0.01831 | 122.7036 | 122.6715 | 0.045777 | 122.937 | 122.8043 | 0.13275 | 0.022889 | 123.1888 | 122.9965 | 122.8867 | -0.36163 | 123.0606 | 123.0377 | 122.9691 | -0.34332
3608.1406 | 123.2071 | -122.818 | 0.17853 | -0.076904 | 0.026383 | 0.0059388 | 0.0081091 | -0.008611 | -0.005048 | -0.01207 | -0.073471 | -0.012341 | -0.0064664 | -0.0024032 | 0.00026273 | -0.015716 | 0.20142 | 0.24261 | 0.1831 | 0.19226 | 0.34332 | 0.054932 | -0.10986 | 0.21515 | 0.29755 | 0.17395 | 0.24719 | 0.21973 | -0.036621 | -0.086975 | 122.8729 | 122.7081 | 0.16479 | 123.0606 | 123.0103 | 0.30212 | 0.022888 | 122.7814 | 122.731 | 0.068664 | 123.0331 | 122.9919 | 0.26092 | 0.041199 | 123.1613 | 123.0194 | 123.0011 | -0.28839 | 123.0652 | 123.0377 | 123.1155 | -0.2655
3609.8438 | 123.1201 | -122.8455 | 0.19684 | 0.17487 | 0.034287 | 0.0050842 | 0.0023413 | -0.01032 | 0.0011472 | -0.0056611 | 0.15541 | -0.010632 | -0.0079618 | -0.003685 | 0.0083805 | -0.018066 | 0.064087 | 0.018311 | -0.041199 | -0.004578 | 0.25177 | -0.082397 | -0.25177 | 0.07782 | 0.059509 | -0.041199 | 0.16937 | 0.15564 | -0.15106 | -0.21057 | 122.7631 | 122.5937 | 0.054932 | 122.8638 | 122.8409 | 0.24719 | -0.13275 | 122.6944 | 122.6349 | -0.027465 | 122.9233 | 122.8043 | 0.16937 | -0.041198 | 123.0972 | 122.9095 | 122.8043 | -0.44861 | 123.0148 | 123.0011 | 122.905 | -0.40741
3611.5938 | 123.2071 | -122.8134 | 0.17853 | -0.18372 | 0.03685 | 0.002948 | 0.0083227 | -0.01032 | 0.00093342 | -0.0073701 | -0.18791 | -0.011914 | -0.0045438 | 0.00058739 | 0.0053897 | -0.017852 | 0.16479 | 0.09613 | 0.054932 | 0.10986 | 0.36163 | 0.004578 | -0.16479 | 0.10529 | 0.14191 | -0.013733 | 0.24261 | 0.21973 | -0.11444 | -0.16479 | 122.818 | 122.6486 | 0.1831 | 122.9095 | 122.9233 | 0.27466 | -0.013733 | 122.699 | 122.6486 | 0.064087 | 122.9187 | 122.7997 | 0.15106 | 0.041199 | 123.175 | 122.9782 | 122.8683 | -0.34332 | 123.056 | 123.0331 | 122.9553 | -0.34332
3613.3594 | 123.1659 | -122.8088 | 0.1831 | -0.023499 | 0.027451 | 0.0065796 | 0.0059729 | -0.011388 | -0.0059024 | -0.0086517 | 0.048599 | -0.013836 | -0.006039 | -0.0032578 | 0.0021853 | -0.013366 | 0.10071 | 0.13733 | 0.1236 | 0.11902 | 0.33875 | 0.022888 | -0.15106 | 0.13275 | 0.20142 | 0.10529 | 0.25177 | 0.21057 | -0.068665 | -0.10529 | 122.8317 | 122.6578 | 0.15564 | 122.9462 | 122.9279 | 0.27008 | -0.082397 | 122.7402 | 122.7036 | 0.068665 | 122.9416 | 122.9141 | 0.21057 | 0.027466 | 123.1476 | 122.9095 | 122.9324 | -0.33417 | 123.0606 | 123.0194 | 123.0103 | -0.28839
3615.125 | 123.111 | -122.8455 | 0.20142 | 0.17487 | 0.032791 | 0.0089294 | 0.0042639 | -0.0079702 | 0.0020016 | -0.0056611 | 0.13252 | -0.012127 | -0.0062528 | -0.0030442 | 0.0058169 | -0.016784 | 0.041199 | 0.018311 | -0.041199 | -0.009155 | 0.23804 | -0.082397 | -0.2243 | 0.086975 | 0.091553 | -0.013733 | 0.16937 | 0.14191 | -0.15106 | -0.19684 | 122.7631 | 122.6212 | 0.036621 | 122.8638 | 122.8363 | 0.21515 | -0.16022 | 122.6944 | 122.6486 | -0.032043 | 122.9324 | 122.8317 | 0.18311 | -0.059509 | 123.0835 | 122.8867 | 122.8043 | -0.42572 | 123.0148 | 122.9874 | 122.937 | -0.39825
3616.8281 | 123.1705 | -122.8271 | 0.1831 | -0.16846 | 0.030655 | 0.0078614 | 0.0091773 | -0.0096792 | -0.0059024 | -0.0086517 | -0.12688 | -0.013623 | -0.004971 | -0.0028306 | 0.0036807 | -0.016357 | 0.21515 | 0.27466 | 0.21973 | 0.20142 | 0.33875 | 0.068665 | -0.09613 | 0.21057 | 0.31586 | 0.16937 | 0.28839 | 0.2243 | -0.032043 | -0.082397 | 122.8958 | 122.731 | 0.15564 | 123.1018 | 123.0286 | 0.29755 | 0.032044 | 122.7951 | 122.7448 | 0.10529 | 123.0377 | 122.9965 | 0.25177 | 0.041199 | 123.1659 | 123.0423 | 123.0469 | -0.27924 | 123.1155 | 123.0515 | 123.143 | -0.2655
3618.5938 | 123.1613 | -122.8088 | 0.18768 | -0.17609 | 0.028092 | 0.0078614 | 0.0085363 | -0.011388 | -0.0031254 | -0.0095063 | -0.15739 | -0.013196 | -0.0045438 | -0.001976 | 0.0030399 | -0.017425 | 0.23804 | 0.27008 | 0.21973 | 0.20142 | 0.3479 | 0.064087 | -0.086975 | 0.20599 | 0.29755 | 0.16022 | 0.26093 | 0.22888 | -0.036621 | -0.09613 | 122.8729 | 122.7219 | 0.16022 | 123.0789 | 123.0103 | 0.28839 | 0.050354 | 122.7722 | 122.7127 | 0.073242 | 123.0148 | 122.9691 | 0.25635 | 0.041199 | 123.1567 | 123.0469 | 123.0286 | -0.27466 | 123.0698 | 123.0377 | 123.1064 | -0.28381
3620.3594 | 123.111 | -122.8455 | 0.19226 | 0.13672 | 0.031509 | 0.0052978 | 0.0044775 | -0.0094656 | 0.003497 | -0.0067291 | 0.048599 | -0.010846 | -0.007748 | 0.00016019 | 0.0081667 | -0.014648 | 0.050354 | -0.018311 | -0.054932 | -0.013733 | 0.28381 | -0.082397 | -0.24261 | 0.041199 | 0.022888 | -0.07782 | 0.21515 | 0.14191 | -0.15564 | -0.21057 | 122.7631 | 122.6028 | 0.091552 | 122.8271 | 122.8317 | 0.22888 | -0.14191 | 122.6898 | 122.6349 | 0.022888 | 122.8867 | 122.7676 | 0.13275 | -0.050354 | 123.1293 | 122.8958 | 122.7905 | -0.43488 | 123.0606 | 122.9874 | 122.8683 | -0.40283
3622.1094 | 123.0698 | -122.8638 | 0.20599 | -0.0082397 | 0.033005 | 0.0031616 | 0.0042639 | -0.010106 | 0.003497 | -0.0080109 | -0.0048066 | -0.012341 | -0.00668 | -0.0017624 | 0.0066715 | -0.016357 | 0.059509 | 0.036621 | -0.032043 | 0.022888 | 0.27924 | -0.059509 | -0.24261 | 0.018311 | 0.009155 | -0.10986 | 0.19684 | 0.16937 | -0.16937 | -0.2243 | 122.8043 | 122.6212 | 0.073242 | 122.9004 | 122.8867 | 0.2655 | -0.14649 | 122.6944 | 122.6395 | -0.009156 | 122.8821 | 122.7539 | 0.11444 | -0.036621 | 123.143 | 122.9233 | 122.8317 | -0.44861 | 123.0606 | 123.0331 | 122.8729 | -0.4303
3623.8125 | 123.1888 | -122.8043 | 0.1831 | -0.13031 | 0.033432 | 0.0038024 | 0.0068273 | -0.0083974 | 0.0028562 | -0.0063019 | -0.14977 | -0.0089229 | -0.0047574 | -0.0026168 | 0.0068851 | -0.017425 | 0.13733 | 0.11902 | 0.064087 | 0.11444 | 0.33875 | -0.022888 | -0.17395 | 0.082397 | 0.1236 | -0.027466 | 0.22888 | 0.20599 | -0.1236 | -0.17853 | 122.7814 | 122.6303 | 0.15564 | 122.9233 | 122.9187 | 0.28839 | -0.045776 | 122.6807 | 122.6257 | 0.045777 | 122.8867 | 122.7768 | 0.15106 | 0.022889 | 123.143 | 122.9416 | 122.8683 | -0.35706 | 123.0331 | 123.0103 | 122.9279 | -0.36163
3625.5625 | 123.1796 | -122.7859 | 0.17395 | -0.16083 | 0.02916 | 0.0076478 | 0.0096045 | -0.0083974 | -0.0063296 | -0.0097199 | -0.020065 | -0.013196 | -0.0064664 | -0.0021896 | 0.00047633 | -0.015503 | 0.19684 | 0.24261 | 0.21057 | 0.19684 | 0.35248 | 0.059509 | -0.09613 | 0.22888 | 0.31128 | 0.19684 | 0.24261 | 0.21515 | -0.022888 | -0.091553 | 122.8455 | 122.6898 | 0.17853 | 123.0286 | 122.9828 | 0.29297 | 0.022888 | 122.7631 | 122.6944 | 0.068665 | 123.0148 | 122.9828 | 0.28839 | 0.041199 | 123.1384 | 122.9828 | 122.9965 | -0.27008 | 123.0286 | 123.0011 | 123.0972 | -0.2655
3627.3125 | 123.111 | -122.8546 | 0.20142 | 0.1825 | 0.030441 | 0.008075 | 0.0019141 | -0.008611 | 0.0020016 | -0.0065155 | 0.17067 | -0.012982 | -0.0096706 | -0.0015488 | 0.0085941 | -0.016571 | 0.10529 | 0.10071 | 0.054932 | 0.086975 | 0.2243 | -0.050354 | -0.20599 | 0.11444 | 0.13275 | 0.022888 | 0.15106 | 0.13733 | -0.12817 | -0.20142 | 122.8043 | 122.6486 | 0.022888 | 122.9553 | 122.9416 | 0.29297 | -0.09613 | 122.7264 | 122.6532 | -0.050354 | 122.9691 | 122.8775 | 0.2243 | -0.064087 | 123.0789 | 122.9599 | 122.9095 | -0.40741 | 123.0057 | 122.9919 | 122.9874 | -0.40283
3629.0781 | 123.1842 | -122.818 | 0.17395 | -0.14557 | 0.031723 | 0.008075 | 0.0083227 | -0.0083974 | -0.0056888 | -0.0090791 | -0.042954 | -0.014691 | -0.0053982 | -0.0013352 | 0.0019717 | -0.014007 | 0.19684 | 0.24719 | 0.19684 | 0.20142 | 0.34332 | 0.050354 | -0.10071 | 0.21515 | 0.28839 | 0.1831 | 0.26093 | 0.22888 | -0.036621 | -0.082397 | 122.8683 | 122.7173 | 0.16937 | 123.0652 | 123.0194 | 0.30212 | 0.022888 | 122.7814 | 122.7356 | 0.086975 | 123.0331 | 123.0011 | 0.2655 | 0.054932 | 123.1613 | 123.0148 | 123.0148 | -0.27466 | 123.0789 | 123.0469 | 123.1064 | -0.25635
3630.7812 | 123.1888 | -122.8409 | 0.17395 | -0.26001 | 0.034073 | 0.0050842 | 0.010673 | -0.011388 | 0.0041378 | -0.0090791 | -0.10399 | -0.013196 | -0.0026212 | -0.0028306 | 0.0066715 | -0.01828 | 0.15106 | 0.10071 | 0.059509 | 0.10986 | 0.35706 | -0.004578 | -0.17853 | 0.09613 | 0.13275 | -0.018311 | 0.21973 | 0.19226 | -0.12817 | -0.16479 | 122.8363 | 122.6624 | 0.18311 | 122.9416 | 122.9507 | 0.28839 | -0.022888 | 122.7127 | 122.6761 | 0.045777 | 122.937 | 122.8226 | 0.14648 | 0.018311 | 123.1979 | 122.9919 | 122.9004 | -0.35248 | 123.0606 | 123.0331 | 122.9736 | -0.33874
3632.5469 | 123.0789 | -122.8363 | 0.21057 | 0.15198 | 0.029587 | 0.0070068 | 0.0034093 | -0.011388 | -0.004407 | -0.0075837 | -0.11925 | -0.014691 | -0.008389 | -0.0030442 | 0.0058169 | -0.015503 | 0.068665 | 0.1236 | 0.07782 | 0.07782 | 0.25177 | -0.036621 | -0.1831 | 0.1236 | 0.15106 | 0.068665 | 0.20142 | 0.1831 | -0.086975 | -0.13733 | 122.7997 | 122.6532 | 0.041199 | 122.9599 | 122.9141 | 0.26092 | -0.14191 | 122.7493 | 122.699 | -0.009155 | 122.9599 | 122.905 | 0.20599 | -0.027466 | 123.0881 | 122.905 | 122.9141 | -0.39368 | 123.0377 | 123.0194 | 122.9874 | -0.3479
3634.25 | 123.1842 | -122.8043 | 0.19684 | -0.26001 | 0.030655 | 0.0067932 | 0.0078955 | -0.005834 | 0.0011472 | -0.0073701 | -0.25658 | -0.011914 | -0.007748 | -0.0041122 | 0.0030399 | -0.017212 | 0.13275 | 0.13733 | 0.07782 | 0.13275 | 0.4303 | 0.041199 | -0.12817 | 0.086975 | 0.14191 | 0.022888 | 0.31128 | 0.28839 | -0.091553 | -0.13733 | 122.8455 | 122.6761 | 0.23346 | 122.9416 | 122.937 | 0.26093 | -0.064087 | 122.7127 | 122.6669 | 0.11444 | 122.8912 | 122.8271 | 0.16022 | 0.091553 | 123.2346 | 122.937 | 122.8821 | -0.32501 | 123.1155 | 123.0927 | 122.9462 | -0.33417
3636.0156 | 123.111 | -122.8409 | 0.18768 | 0.13672 | 0.034927 | 0.0076478 | 0.0046911 | -0.0043386 | 0.0020016 | -0.0071563 | 0.14778 | -0.0117 | -0.007748 | -0.0015488 | 0.0068851 | -0.015289 | 0.022888 | 0.018311 | -0.036621 | 0 | 0.26093 | -0.064087 | -0.23346 | 0.07782 | 0.07782 | -0.018311 | 0.17395 | 0.14648 | -0.14648 | -0.21515 | 122.7768 | 122.6074 | 0.073242 | 122.8592 | 122.8409 | 0.23346 | -0.16479 | 122.6944 | 122.6257 | -0.013733 | 122.9187 | 122.8226 | 0.19684 | -0.041199 | 123.1018 | 122.8638 | 122.8043 | -0.42114 | 123.0148 | 122.9874 | 122.9187 | -0.40283
3637.7188 | 123.1842 | -122.818 | 0.17395 | -0.27527 | 0.031509 | 0.0076478 | 0.0066137 | -0.0081838 | -0.0018436 | -0.0071563 | -0.26421 | -0.0097775 | -0.0064664 | -0.0015488 | 0.0038943 | -0.014648 | 0.1236 | 0.17395 | 0.07782 | 0.14191 | 0.42114 | 0.032043 | -0.1236 | 0.07782 | 0.14191 | 0.009155 | 0.31586 | 0.2655 | -0.059509 | -0.12817 | 122.85 | 122.6944 | 0.24719 | 122.9919 | 122.9599 | 0.2655 | -0.050354 | 122.7585 | 122.6898 | 0.14191 | 122.8958 | 122.8271 | 0.13733 | 0.091553 | 123.2391 | 122.9416 | 122.8958 | -0.29755 | 123.1338 | 123.0835 | 122.9599 | -0.30212
3639.4844 | 123.1842 | -122.8043 | 0.16937 | -0.11505 | 0.028732 | 0.0067932 | 0.0064001 | -0.008611 | -0.0059024 | -0.011215 | -0.058212 | -0.014691 | -0.0051846 | -0.0032578 | 0.0013309 | -0.016357 | 0.18768 | 0.27924 | 0.21515 | 0.19684 | 0.35706 | 0.064087 | -0.1236 | 0.24719 | 0.28381 | 0.17853 | 0.24719 | 0.21515 | -0.036621 | -0.082397 | 122.8683 | 122.6807 | 0.18768 | 123.0835 | 123.0011 | 0.32043 | 0.01831 | 122.7676 | 122.7219 | 0.077819 | 123.0515 | 122.9828 | 0.26092 | 0.045776 | 123.1613 | 122.9919 | 123.0194 | -0.29297 | 123.0515 | 123.0194 | 123.0881 | -0.25177
3641.1719 | 123.1979 | -122.818 | 0.16479 | -0.22186 | 0.030441 | 0.0070068 | 0.0085363 | -0.007543 | 0.0024288 | -0.0082245 | -0.21843 | -0.0089229 | -0.0047574 | 0.00037379 | 0.0036807 | -0.017425 | 0.13733 | 0.11444 | 0.07782 | 0.11902 | 0.40741 | 0.013733 | -0.11902 | 0.07782 | 0.13275 | -0.009155 | 0.27466 | 0.24261 | -0.09613 | -0.15564 | 122.8317 | 122.699 | 0.24261 | 122.9324 | 122.937 | 0.23804 | -0.027466 | 122.7219 | 122.6624 | 0.10986 | 122.8958 | 122.8088 | 0.14649 | 0.07782 | 123.2254 | 122.9553 | 122.8958 | -0.28381 | 123.0927 | 123.0606 | 122.9507 | -0.32044
3642.9219 | 123.1934 | -122.7997 | 0.17853 | -0.19135 | 0.032578 | 0.0052978 | 0.0085363 | -0.0081838 | 0.0032834 | -0.0058747 | -0.24132 | -0.010632 | -0.0062528 | -0.0021896 | 0.0058169 | -0.017212 | 0.13733 | 0.1236 | 0.059509 | 0.1236 | 0.36621 | 0.013733 | -0.14191 | 0.082397 | 0.14191 | -0.013733 | 0.24719 | 0.21515 | -0.11902 | -0.16479 | 122.8134 | 122.6578 | 0.18768 | 122.9233 | 122.9233 | 0.2655 | -0.041199 | 122.6807 | 122.6349 | 0.068664 | 122.8821 | 122.7859 | 0.15106 | 0.036621 | 123.1659 | 122.937 | 122.8592 | -0.32044 | 123.0469 | 123.0148 | 122.9416 | -0.34332
3644.625 | 123.1888 | -122.7997 | 0.18768 | -0.11505 | 0.027664 | 0.0040162 | 0.0087499 | -0.008611 | -0.0073978 | -0.0092927 | -0.096359 | -0.012982 | -0.0053982 | -0.0013352 | 0.0011173 | -0.015503 | 0.21515 | 0.27008 | 0.20599 | 0.18768 | 0.33875 | 0.054932 | -0.10986 | 0.20142 | 0.31128 | 0.17395 | 0.25635 | 0.2243 | -0.036621 | -0.086975 | 122.8546 | 122.6898 | 0.15106 | 123.0698 | 122.9874 | 0.29755 | 0.027466 | 122.7631 | 122.7127 | 0.068665 | 123.0011 | 122.9736 | 0.26092 | 0.036621 | 123.1384 | 123.0148 | 123.0057 | -0.29755 | 123.056 | 123.024 | 123.111 | -0.27466
3646.3906 | 123.1522 | -122.7997 | 0.19226 | -0.19135 | 0.028519 | 0.0055114 | 0.0059729 | -0.0073294 | -0.0029118 | -0.0097199 | -0.24132 | -0.013409 | -0.0056118 | -5.3406e-05 | 0.0021853 | -0.017425 | 0.20599 | 0.24261 | 0.19684 | 0.20599 | 0.32959 | 0.073242 | -0.09613 | 0.16022 | 0.25177 | 0.091553 | 0.29755 | 0.25635 | -0.036621 | -0.091553 | 122.8729 | 122.7036 | 0.13733 | 123.0423 | 123.0057 | 0.30212 | 0.013733 | 122.7631 | 122.7081 | 0.10528 | 122.9599 | 122.8912 | 0.18311 | 0.064087 | 123.1293 | 123.0057 | 122.9965 | -0.28839 | 123.0972 | 123.056 | 123.0515 | -0.28381
3648.1562 | 123.111 | -122.8683 | 0.20599 | 0.14435 | 0.030228 | 0.0065796 | 0.0034093 | -0.0073294 | -0.00077538 | -0.0071563 | 0.14778 | -0.012127 | -0.0068936 | -0.00069421 | 0.0066715 | -0.016998 | 0.10529 | 0.091553 | 0.041199 | 0.091553 | 0.22888 | -0.041199 | -0.21057 | 0.10986 | 0.14648 | 0.022888 | 0.16022 | 0.13275 | -0.14648 | -0.17853 | 122.8271 | 122.6578 | 0.022888 | 122.9599 | 122.9599 | 0.30212 | -0.10071 | 122.7219 | 122.6898 | -0.045777 | 122.9782 | 122.8912 | 0.20142 | -0.073243 | 123.0972 | 122.9736 | 122.9095 | -0.41657 | 123.0286 | 123.0011 | 123.0148 | -0.38452
3649.8594 | 123.1842 | -122.8134 | 0.17395 | -0.10742 | 0.0298 | 0.0059388 | 0.0096045 | -0.0069022 | -0.006116 | -0.011002 | -0.12688 | -0.012982 | -0.0056118 | -0.0034714 | 0.0026125 | -0.016143 | 0.23804 | 0.3067 | 0.21515 | 0.21973 | 0.35248 | 0.068665 | -0.10071 | 0.22888 | 0.31128 | 0.17853 | 0.26093 | 0.23804 | -0.032043 | -0.07782 | 122.8821 | 122.7127 | 0.17853 | 123.1201 | 123.0331 | 0.32044 | 0.064087 | 122.7814 | 122.7356 | 0.086975 | 123.0423 | 122.9919 | 0.25635 | 0.064087 | 123.1659 | 123.0515 | 123.0286 | -0.27466 | 123.0743 | 123.0515 | 123.1247 | -0.25177
3651.625 | 123.0881 | -122.8546 | 0.1831 | 0.029907 | 0.033005 | 0.0067932 | 0.0042639 | -0.0069022 | -0.00056178 | -0.010788 | 0.102 | -0.014477 | -0.0051846 | -0.0030442 | 0.0036807 | -0.014648 | 0.10986 | 0.1236 | 0.10071 | 0.10071 | 0.30212 | 0 | -0.14648 | 0.12817 | 0.1831 | 0.082397 | 0.23346 | 0.21515 | -0.086975 | -0.11902 | 122.8546 | 122.7081 | 0.11902 | 122.9782 | 122.9553 | 0.24719 | -0.073242 | 122.7676 | 122.7356 | 0.050354 | 122.9828 | 122.937 | 0.20142 | 0.032044 | 123.1567 | 122.9645 | 122.9553 | -0.32959 | 123.0881 | 123.0698 | 123.0377 | -0.30212
3653.3906 | 123.1934 | -122.8088 | 0.1831 | -0.13794 | 0.034073 | 0.0055114 | 0.0059729 | -0.0060476 | 0.004565 | -0.0075837 | -0.2108 | -0.011487 | -0.0058254 | -0.0011216 | 0.0092349 | -0.018493 | 0.13733 | 0.13275 | 0.036621 | 0.091553 | 0.33417 | -0.009155 | -0.17853 | 0.09613 | 0.12817 | -0.022888 | 0.23346 | 0.18768 | -0.14191 | -0.17853 | 122.7997 | 122.6303 | 0.15106 | 122.9416 | 122.9004 | 0.27008 | -0.045776 | 122.6669 | 122.6303 | 0.050354 | 122.905 | 122.7859 | 0.15564 | 0.004578 | 123.143 | 122.9462 | 122.8455 | -0.36163 | 123.0423 | 122.9965 | 122.937 | -0.36163
3655.1406 | 123.0606 | -122.8638 | 0.21973 | -0.0082397 | 0.034287 | 0.0042298 | 0.0068273 | -0.0079702 | 0.003497 | -0.0054475 | -0.012436 | -0.0097775 | -0.006039 | 0.00080099 | 0.0079531 | -0.017639 | 0.07782 | 0.050354 | -0.022888 | 0.018311 | 0.3067 | -0.059509 | -0.23346 | 0 | 0.013733 | -0.11444 | 0.20599 | 0.16937 | -0.1831 | -0.21057 | 122.8043 | 122.6303 | 0.086975 | 122.9141 | 122.8821 | 0.25177 | -0.14191 | 122.6807 | 122.6532 | -0.013733 | 122.8638 | 122.7493 | 0.09613 | -0.050354 | 123.1705 | 122.9416 | 122.8409 | -0.45319 | 123.0698 | 123.0331 | 122.8775 | -0.4303
3656.8438 | 123.0743 | -122.8638 | 0.20599 | 0.098572 | 0.031723 | 0.0050842 | 0.0061865 | -0.0081838 | -0.0052616 | -0.0077973 | 0.11726 | -0.014691 | -0.0064664 | -0.0024032 | 0.0021853 | -0.015289 | 0.086975 | 0.13733 | 0.09613 | 0.073242 | 0.26093 | 0.004578 | -0.16937 | 0.12817 | 0.15564 | 0.064087 | 0.23346 | 0.17395 | -0.091553 | -0.13275 | 122.8683 | 122.6944 | 0.054931 | 123.0011 | 122.937 | 0.24261 | -0.11902 | 122.7722 | 122.731 | 0.027465 | 122.9919 | 122.9279 | 0.19684 | -0.032044 | 123.1247 | 122.9507 | 122.9599 | -0.37537 | 123.0972 | 123.0377 | 123.0194 | -0.33875
3658.6094 | 123.1155 | -122.8409 | 0.20142 | 0.12146 | 0.031937 | 0.0055114 | 0.0057593 | -0.0079702 | 0.00050622 | -0.0060883 | 0.04097 | -0.010418 | -0.0056118 | -0.00026701 | 0.0075259 | -0.016357 | 0.022888 | -0.018311 | -0.054932 | -0.013733 | 0.27924 | -0.09613 | -0.24261 | 0.036621 | 0.022888 | -0.082397 | 0.19684 | 0.17853 | -0.15106 | -0.20599 | 122.7448 | 122.5983 | 0.07782 | 122.8226 | 122.8271 | 0.22888 | -0.17853 | 122.6898 | 122.6349 | -0.004578 | 122.8775 | 122.7585 | 0.1236 | -0.022888 | 123.1201 | 122.8638 | 122.7859 | -0.44403 | 123.0377 | 123.0194 | 122.8638 | -0.40741
3660.375 | 123.1842 | -122.8134 | 0.1831 | -0.092163 | 0.03215 | 0.0057252 | 0.0064001 | -0.0083974 | 0.0022152 | -0.0063019 | -0.17265 | -0.0097775 | -0.0062528 | -0.0011216 | 0.0085941 | -0.016784 | 0.12817 | 0.12817 | 0.050354 | 0.091553 | 0.33417 | -0.018311 | -0.16022 | 0.082397 | 0.13275 | -0.018311 | 0.21973 | 0.20142 | -0.13275 | -0.18768 | 122.7951 | 122.6532 | 0.15106 | 122.9416 | 122.905 | 0.25177 | -0.054931 | 122.6807 | 122.6257 | 0.036622 | 122.8958 | 122.7951 | 0.16937 | 0.018311 | 123.1476 | 122.9416 | 122.8638 | -0.34332 | 123.0331 | 123.0148 | 122.9462 | -0.37079
3662.125 | 123.0743 | -122.8729 | 0.19684 | 0.045166 | 0.030441 | 0.0061524 | 0.0055457 | -0.0079702 | -0.0069706 | -0.0095063 | 0.102 | -0.013836 | -0.0073208 | -0.0015488 | 0.0019717 | -0.012726 | 0.086975 | 0.13275 | 0.091553 | 0.09613 | 0.28381 | 0.009155 | -0.16479 | 0.1236 | 0.17853 | 0.064087 | 0.2243 | 0.20599 | -0.10071 | -0.13275 | 122.8821 | 122.7081 | 0.086975 | 123.0057 | 122.9691 | 0.26092 | -0.10986 | 122.7722 | 122.7402 | 0.027466 | 122.9965 | 122.937 | 0.19684 | 0.009156 | 123.1567 | 122.9599 | 122.9645 | -0.36163 | 123.0972 | 123.0789 | 123.0515 | -0.32959
3663.8281 | 123.1064 | -122.8455 | 0.21057 | 0.1825 | 0.030228 | 0.0072204 | 0.0040503 | -0.0094656 | -0.00077538 | -0.0056611 | 0.19356 | -0.013196 | -0.008389 | 0.0012284 | 0.0051761 | -0.017212 | 0.10529 | 0.10071 | 0.054932 | 0.064087 | 0.22888 | -0.054932 | -0.22888 | 0.10071 | 0.14648 | 0.036621 | 0.14648 | 0.10529 | -0.14648 | -0.20142 | 122.7905 | 122.6166 | 0.018311 | 122.9462 | 122.9095 | 0.29297 | -0.10529 | 122.699 | 122.644 | -0.064087 | 122.9462 | 122.8821 | 0.23804 | -0.10529 | 123.0743 | 122.9507 | 122.9004 | -0.43945 | 122.9919 | 122.9507 | 122.9919 | -0.41199
3665.5781 | 123.2162 | -122.818 | 0.1831 | -0.17609 | 0.031296 | 0.004657 | 0.0040503 | -0.0066884 | 0.0026424 | -0.0065155 | -0.24895 | -0.0117 | -0.007748 | -0.0028306 | 0.0049625 | -0.017852 | 0.16022 | 0.1236 | 0.059509 | 0.10529 | 0.39368 | 0.013733 | -0.14191 | 0.073242 | 0.13733 | -0.009155 | 0.2655 | 0.2243 | -0.10529 | -0.16479 | 122.8317 | 122.6761 | 0.21057 | 122.9416 | 122.9233 | 0.24719 | -0.022888 | 122.7127 | 122.6532 | 0.082398 | 122.8912 | 122.8088 | 0.15564 | 0.041199 | 123.2117 | 122.9782 | 122.8775 | -0.32501 | 123.0835 | 123.0423 | 122.9553 | -0.3479
3667.3438 | 123.0789 | -122.8546 | 0.19226 | 0.068054 | 0.035141 | 0.0044434 | 0.0055457 | -0.0090384 | 0.001788 | -0.0065155 | 0.04097 | -0.0093503 | -0.004971 | 0.00058739 | 0.0068851 | -0.015716 | 0.013733 | -0.050354 | -0.07782 | -0.027466 | 0.27924 | -0.059509 | -0.23346 | 0 | 0.004578 | -0.11444 | 0.19226 | 0.16022 | -0.16937 | -0.22888 | 122.7951 | 122.6212 | 0.086975 | 122.8043 | 122.8271 | 0.20599 | -0.17853 | 122.6852 | 122.6257 | 0 | 122.8546 | 122.7402 | 0.11444 | -0.032044 | 123.1338 | 122.8683 | 122.7768 | -0.42572 | 123.0469 | 123.0148 | 122.8592 | -0.42114
3669.0938 | 123.0743 | -122.85 | 0.20599 | 0.15198 | 0.028092 | 0.0050842 | 0.0046911 | -0.0083974 | -0.0065434 | -0.0052337 | 0.12489 | -0.012982 | -0.0081754 | -0.0034714 | 0.0047489 | -0.013366 | 0.082397 | 0.12817 | 0.082397 | 0.068665 | 0.25177 | -0.018311 | -0.19684 | 0.1236 | 0.16022 | 0.073242 | 0.20599 | 0.1831 | -0.086975 | -0.12817 | 122.8317 | 122.6532 | 0.045776 | 122.9782 | 122.9187 | 0.2655 | -0.1236 | 122.7631 | 122.7219 | 0 | 122.9736 | 122.9233 | 0.20142 | -0.022889 | 123.1018 | 122.9324 | 122.9324 | -0.40283 | 123.056 | 123.0331 | 123.0103 | -0.33417
3670.7969 | 123.1796 | -122.818 | 0.20142 | -0.13031 | 0.0298 | 0.0072204 | 0.010459 | -0.0079702 | -0.0039798 | -0.0099335 | -0.14977 | -0.015332 | -0.0051846 | -0.0032578 | 4.9132e-05 | -0.017212 | 0.2243 | 0.26093 | 0.20599 | 0.20142 | 0.36163 | 0.050354 | -0.091553 | 0.21973 | 0.31128 | 0.16937 | 0.2655 | 0.24261 | -0.022888 | -0.073242 | 122.8683 | 122.7264 | 0.16022 | 123.0789 | 123.0194 | 0.29297 | 0.022888 | 122.7951 | 122.7448 | 0.064087 | 123.0377 | 122.9874 | 0.24261 | 0.041199 | 123.1796 | 123.0423 | 123.024 | -0.29297 | 123.0835 | 123.0606 | 123.1293 | -0.27466
3672.5625 | 123.175 | -122.7905 | 0.17395 | 0.022278 | 0.029373 | 0.0059388 | 0.0078955 | -0.0081838 | -0.0041934 | -0.0097199 | 0.010452 | -0.013836 | -0.0068936 | -0.00069421 | 0.0015445 | -0.01593 | 0.11902 | 0.13733 | 0.1236 | 0.11444 | 0.32959 | 0.022888 | -0.1236 | 0.15106 | 0.18768 | 0.11902 | 0.24261 | 0.2243 | -0.068665 | -0.1236 | 122.8134 | 122.6669 | 0.15564 | 122.9279 | 122.905 | 0.23804 | -0.054931 | 122.7219 | 122.6669 | 0.068665 | 122.9416 | 122.9095 | 0.24261 | 0.050354 | 123.1201 | 122.9095 | 122.9141 | -0.29755 | 123.0331 | 123.0148 | 122.9782 | -0.29755
3674.3281 | 123.1796 | -122.8043 | 0.1831 | -0.0082397 | 0.028946 | 0.0052978 | 0.0091773 | -0.008611 | -0.0029118 | -0.0095063 | -0.012436 | -0.013409 | -0.0056118 | -0.0030442 | 0.0028263 | -0.015716 | 0.12817 | 0.1236 | 0.12817 | 0.1236 | 0.32959 | 0.022888 | -0.16937 | 0.16022 | 0.21973 | 0.1236 | 0.25177 | 0.20599 | -0.082397 | -0.11444 | 122.8271 | 122.6349 | 0.14649 | 122.9279 | 122.9279 | 0.29297 | -0.054931 | 122.7219 | 122.6898 | 0.068665 | 122.9645 | 122.9279 | 0.23804 | 0.022889 | 123.1338 | 122.9324 | 122.9324 | -0.35248 | 123.056 | 123.0103 | 123.024 | -0.29755
3676.0938 | 123.1613 | -122.7951 | 0.1831 | -0.22186 | 0.029587 | 0.0061524 | 0.0072547 | -0.0077566 | -0.00077538 | -0.0090791 | -0.16502 | -0.013196 | -0.0073208 | -0.0015488 | 0.0023989 | -0.017852 | 0.24719 | 0.26093 | 0.2243 | 0.20142 | 0.37537 | 0.091553 | -0.09613 | 0.20599 | 0.29755 | 0.16022 | 0.26093 | 0.21973 | -0.018311 | -0.086975 | 122.8867 | 122.699 | 0.19226 | 123.056 | 122.9965 | 0.29755 | 0.064087 | 122.7768 | 122.7081 | 0.07782 | 123.0011 | 122.9553 | 0.24719 | 0.036622 | 123.1705 | 123.0423 | 123.0194 | -0.27924 | 123.056 | 123.0148 | 123.0927 | -0.27008
3677.7969 | 123.1293 | -122.8317 | 0.20142 | -0.092163 | 0.030869 | 0.0055114 | 0.0055457 | -0.0090384 | 0.0064876 | -0.0084381 | -0.18791 | -0.010632 | -0.0039028 | -0.00026701 | 0.0096621 | -0.018921 | 0.17853 | 0.086975 | 0.022888 | 0.068665 | 0.31586 | -0.027466 | -0.19684 | 0.086975 | 0.10986 | -0.050354 | 0.21973 | 0.20599 | -0.11902 | -0.18768 | 122.8043 | 122.6349 | 0.11444 | 122.9187 | 122.9004 | 0.2655 | -0.022888 | 122.7127 | 122.644 | 0.018311 | 122.9187 | 122.7814 | 0.13733 | 0.004578 | 123.1476 | 123.0103 | 122.8546 | -0.39825 | 123.0515 | 123.0377 | 122.9416 | -0.3891
3679.5625 | 123.0743 | -122.8638 | 0.20599 | 0.12909 | 0.029587 | 0.006366 | 0.0034093 | -0.0094656 | -0.005048 | -0.0073701 | 0.10963 | -0.013409 | -0.0075344 | -0.0041122 | 0.0032535 | -0.015289 | 0.10529 | 0.13275 | 0.10071 | 0.086975 | 0.25177 | -0.013733 | -0.16937 | 0.12817 | 0.15564 | 0.064087 | 0.21973 | 0.17853 | -0.086975 | -0.13733 | 122.85 | 122.6944 | 0.045776 | 122.9965 | 122.9507 | 0.25635 | -0.10071 | 122.7768 | 122.7264 | 0.013733 | 122.9919 | 122.9279 | 0.20142 | -0.027466 | 123.1155 | 122.9691 | 122.9645 | -0.37537 | 123.0835 | 123.0423 | 123.0194 | -0.34332
3681.2656 | 123.2117 | -122.8363 | 0.16022 | -0.25238 | 0.02916 | 0.008075 | 0.0076819 | -0.0094656 | 0.00071982 | -0.0082245 | -0.25658 | -0.013196 | -0.0062528 | -0.00026701 | 0.0041079 | -0.017212 | 0.15564 | 0.11902 | 0.086975 | 0.11902 | 0.41657 | 0.032043 | -0.12817 | 0.082397 | 0.14191 | -0.009155 | 0.30212 | 0.27008 | -0.10071 | -0.14648 | 122.8683 | 122.7081 | 0.25635 | 122.9553 | 122.9553 | 0.24719 | -0.004577 | 122.7356 | 122.6898 | 0.14191 | 122.9187 | 122.8271 | 0.13733 | 0.10986 | 123.2529 | 122.9919 | 122.9233 | -0.28839 | 123.1384 | 123.1064 | 122.9782 | -0.3067
3683.0469 | 123.1567 | -122.8226 | 0.18768 | -0.16846 | 0.029373 | 0.0076478 | 0.0076819 | -0.0060476 | -0.003339 | -0.0065155 | -0.16502 | -0.01405 | -0.0075344 | -0.0028306 | 0.0026125 | -0.018066 | 0.20599 | 0.27466 | 0.20142 | 0.20142 | 0.35248 | 0.059509 | -0.082397 | 0.17853 | 0.26093 | 0.13275 | 0.25635 | 0.22888 | -0.045776 | -0.09613 | 122.8821 | 122.7402 | 0.1648 | 123.0972 | 123.024 | 0.28381 | 0.018311 | 122.7768 | 122.7264 | 0.068665 | 123.0011 | 122.9553 | 0.22888 | 0.041199 | 123.175 | 123.0286 | 123.024 | -0.27008 | 123.0789 | 123.0515 | 123.0835 | -0.28381
3684.75 | 123.1796 | -122.8271 | 0.16937 | -0.26764 | 0.034073 | 0.0055114 | 0.010673 | -0.0094656 | -0.00056178 | -0.0082245 | -0.29472 | -0.010846 | -0.0041164 | -0.00048061 | 0.0030399 | -0.016571 | 0.15564 | 0.14648 | 0.091553 | 0.1236 | 0.41657 | 0.050354 | -0.12817 | 0.091553 | 0.16479 | 0.018311 | 0.33417 | 0.28839 | -0.073242 | -0.1236 | 122.8775 | 122.699 | 0.24719 | 122.9736 | 122.9507 | 0.25177 | -0.013733 | 122.7539 | 122.7036 | 0.16479 | 122.9187 | 122.8455 | 0.14191 | 0.11902 | 123.2437 | 122.9828 | 122.9187 | -0.29755 | 123.1613 | 123.1155 | 122.9919 | -0.29297
3686.5156 | 123.0743 | -122.8546 | 0.20599 | 0.052795 | 0.035782 | 0.0055114 | 0.0055457 | -0.0081838 | 0.0039242 | -0.0073701 | 0.056228 | -0.010632 | -0.0056118 | -0.00090781 | 0.0092349 | -0.014435 | 0.018311 | -0.045776 | -0.07782 | -0.027466 | 0.28381 | -0.086975 | -0.25177 | -0.004578 | 0.004578 | -0.11902 | 0.21057 | 0.16937 | -0.17853 | -0.2243 | 122.7676 | 122.6028 | 0.077819 | 122.8088 | 122.8271 | 0.2243 | -0.18768 | 122.6761 | 122.6303 | 0.004577 | 122.85 | 122.7356 | 0.10529 | -0.036621 | 123.1384 | 122.8729 | 122.7768 | -0.45776 | 123.0652 | 123.024 | 122.8592 | -0.4303
3688.2188 | 123.1476 | -122.8271 | 0.17853 | -0.25238 | 0.033005 | 0.0040162 | 0.010886 | -0.0088248 | -0.0035526 | -0.0082245 | -0.19554 | -0.0117 | -0.0041164 | -0.0015488 | 0.00090353 | -0.015716 | 0.15564 | 0.19226 | 0.13275 | 0.16479 | 0.3891 | 0.050354 | -0.11444 | 0.11444 | 0.16937 | 0.032043 | 0.29755 | 0.27008 | -0.07782 | -0.11444 | 122.8775 | 122.7127 | 0.21057 | 123.0194 | 122.9919 | 0.27924 | -0.022888 | 122.7493 | 122.7127 | 0.11902 | 122.9416 | 122.8592 | 0.14648 | 0.091553 | 123.2162 | 122.9828 | 122.9599 | -0.29297 | 123.1247 | 123.0972 | 122.9965 | -0.29297
3689.9844 | 123.1567 | -122.8226 | 0.18768 | -0.2066 | 0.030441 | 0.0048706 | 0.0066137 | -0.008611 | -0.0046206 | -0.0056611 | -0.2108 | -0.012982 | -0.0096706 | -0.0028306 | 0.0036807 | -0.01593 | 0.18768 | 0.25635 | 0.18768 | 0.18768 | 0.34332 | 0.050354 | -0.07782 | 0.17853 | 0.26093 | 0.11902 | 0.27924 | 0.23804 | -0.059509 | -0.10986 | 122.8729 | 122.7448 | 0.15564 | 123.0789 | 123.0103 | 0.2655 | 0 | 122.7631 | 122.7127 | 0.091553 | 123.0011 | 122.9416 | 0.22888 | 0.050354 | 123.1659 | 123.0103 | 123.0103 | -0.2655 | 123.1018 | 123.0606 | 123.0835 | -0.29755
3691.6719 | 123.1155 | -122.8363 | 0.20142 | 0.098572 | 0.032791 | 0.007434 | 0.0078955 | -0.0096792 | 0.0039242 | -0.0052337 | 0.063858 | -0.011273 | -0.00668 | 0.00016019 | 0.0070987 | -0.017212 | 0.018311 | -0.036621 | -0.07782 | -0.013733 | 0.27924 | -0.10529 | -0.27008 | 0.009155 | 0.009155 | -0.082397 | 0.19684 | 0.16479 | -0.16479 | -0.21515 | 122.731 | 122.5662 | 0.07782 | 122.7997 | 122.8226 | 0.25635 | -0.18311 | 122.6715 | 122.6212 | -0.004578 | 122.8455 | 122.7539 | 0.13275 | -0.036621 | 123.1155 | 122.8546 | 122.7585 | -0.4715 | 123.0331 | 123.0011 | 122.8455 | -0.41657
3693.4219 | 123.1979 | -122.8226 | 0.17853 | -0.18372 | 0.03215 | 0.0042298 | 0.0074683 | -0.0096792 | 7.902e-05 | -0.0086517 | -0.22606 | -0.010418 | -0.0092434 | -0.0041122 | 0.0053897 | -0.017212 | 0.1236 | 0.11444 | 0.064087 | 0.11444 | 0.36621 | 0.027466 | -0.16937 | 0.07782 | 0.14191 | -0.018311 | 0.23804 | 0.21057 | -0.10986 | -0.16937 | 122.85 | 122.6532 | 0.18768 | 122.937 | 122.937 | 0.28381 | -0.054932 | 122.7127 | 122.6532 | 0.059509 | 122.9004 | 122.8043 | 0.15106 | 0.032043 | 123.1888 | 122.9462 | 122.8867 | -0.3479 | 123.0606 | 123.0331 | 122.9645 | -0.3479
3695.1719 | 123.0972 | -122.8134 | 0.21515 | 0.060425 | 0.034714 | 0.008075 | 0.0051183 | -0.0079702 | 7.902e-05 | -0.0060883 | 0.094375 | -0.010846 | -0.006039 | -0.00090781 | 0.0068851 | -0.014648 | 0.018311 | 0.013733 | -0.054932 | -0.018311 | 0.27924 | -0.07782 | -0.23804 | 0.022888 | 0.041199 | -0.068665 | 0.19226 | 0.15106 | -0.15106 | -0.21057 | 122.7356 | 122.5754 | 0.064087 | 122.8271 | 122.7951 | 0.21973 | -0.19684 | 122.6624 | 122.6028 | -0.022888 | 122.8363 | 122.7448 | 0.14191 | -0.064087 | 123.0927 | 122.8317 | 122.7585 | -0.45319 | 123.0057 | 122.9645 | 122.8546 | -0.42572
3696.875 | 123.0652 | -122.85 | 0.21057 | 0.075684 | 0.031296 | 0.0040162 | 0.0091773 | -0.0096792 | -0.0059024 | -0.011002 | 0.12489 | -0.014264 | -0.00668 | -5.3406e-05 | 0.00026273 | -0.014007 | 0.068665 | 0.12817 | 0.091553 | 0.091553 | 0.2655 | -0.009155 | -0.17853 | 0.10071 | 0.15564 | 0.07782 | 0.21515 | 0.1831 | -0.086975 | -0.14191 | 122.8409 | 122.6715 | 0.054932 | 122.9782 | 122.9416 | 0.27008 | -0.14191 | 122.7631 | 122.7081 | 0.004578 | 122.9507 | 122.9279 | 0.21973 | -0.027466 | 123.1155 | 122.9187 | 122.9416 | -0.3891 | 123.0652 | 123.0331 | 123.0057 | -0.35248
3698.6406 | 123.0789 | -122.85 | 0.20599 | 0.17487 | 0.032578 | 0.0061524 | 0.0029821 | -0.0094656 | -0.00056178 | -0.0082245 | 0.19356 | -0.010418 | -0.0056118 | -0.003685 | 0.0047489 | -0.016357 | 0.10071 | 0.09613 | 0.059509 | 0.073242 | 0.21973 | -0.045776 | -0.21973 | 0.10071 | 0.1236 | 0.022888 | 0.14191 | 0.10071 | -0.15564 | -0.19226 | 122.8043 | 122.6303 | 0.013733 | 122.9462 | 122.9233 | 0.29297 | -0.10529 | 122.6944 | 122.6578 | -0.064087 | 122.9507 | 122.8729 | 0.21515 | -0.10529 | 123.0698 | 122.9507 | 122.9095 | -0.42572 | 122.9919 | 122.9507 | 122.9736 | -0.39826
3700.4062 | 123.1155 | -122.8455 | 0.20599 | 0.1825 | 0.034287 | 0.0044434 | 0.0053321 | -0.009252 | 0.0026424 | -0.0077973 | 0.12489 | -0.011273 | -0.0098844 | -0.0028306 | 0.0068851 | -0.01593 | 0.050354 | 0.041199 | -0.009155 | 0.004578 | 0.24261 | -0.064087 | -0.2243 | 0.09613 | 0.11444 | 0.022888 | 0.17853 | 0.11902 | -0.15564 | -0.19226 | 122.7814 | 122.6212 | 0.036621 | 122.8867 | 122.85 | 0.22888 | -0.15564 | 122.6898 | 122.6532 | -0.027466 | 122.9416 | 122.8683 | 0.21515 | -0.086975 | 123.0881 | 122.8958 | 122.8363 | -0.4303 | 123.024 | 122.9645 | 122.9599 | -0.39826
3702.1562 | 123.0652 | -122.8867 | 0.2243 | 0.083313 | 0.034927 | 0.0048706 | 0.0053321 | -0.0079702 | 0.001788 | -0.0069427 | 0.063858 | -0.0117 | -0.006039 | -0.0026168 | 0.0088077 | -0.017425 | 0.018311 | -0.036621 | -0.082397 | -0.004578 | 0.28839 | -0.086975 | -0.23804 | -0.009155 | 0.009155 | -0.10071 | 0.20142 | 0.16937 | -0.16937 | -0.21973 | 122.7997 | 122.6486 | 0.064087 | 122.85 | 122.8821 | 0.23346 | -0.20599 | 122.7173 | 122.6669 | -0.022888 | 122.8775 | 122.7859 | 0.11902 | -0.054931 | 123.175 | 122.905 | 122.8043 | -0.46234 | 123.0881 | 123.056 | 122.8958 | -0.44403
3703.8438 | 123.0743 | -122.8271 | 0.19684 | 0.16724 | 0.031723 | 0.0050842 | 0.0061865 | -0.010534 | -0.0037662 | -0.0080109 | 0.2317 | -0.013836 | -0.0092434 | -0.0034714 | 0.0056033 | -0.015075 | 0.09613 | 0.10529 | 0.050354 | 0.059509 | 0.21515 | -0.059509 | -0.2243 | 0.09613 | 0.13733 | 0.032043 | 0.14648 | 0.10986 | -0.14191 | -0.21057 | 122.7676 | 122.6028 | 0.018311 | 122.9324 | 122.8867 | 0.28381 | -0.10071 | 122.6852 | 122.6166 | -0.050354 | 122.9233 | 122.8592 | 0.24261 | -0.086975 | 123.0423 | 122.9233 | 122.8775 | -0.42114 | 122.9736 | 122.937 | 122.9645 | -0.40741
3705.6094 | 123.1155 | -122.85 | 0.21515 | 0.12909 | 0.033218 | 0.0042298 | 0.0068273 | -0.0090384 | -0.00013458 | -0.0060883 | 0.16304 | -0.010632 | -0.0047574 | -0.0013352 | 0.0062441 | -0.016357 | 0.032043 | -0.004578 | -0.041199 | 0.004578 | 0.28839 | -0.07782 | -0.23346 | 0.027466 | 0.022888 | -0.068665 | 0.19226 | 0.16479 | -0.15564 | -0.20599 | 122.7722 | 122.6166 | 0.073242 | 122.8455 | 122.8546 | 0.23804 | -0.18311 | 122.6944 | 122.644 | -0.022888 | 122.8775 | 122.7814 | 0.13733 | -0.050354 | 123.1384 | 122.8821 | 122.8088 | -0.44861 | 123.0423 | 123.0148 | 122.8729 | -0.42114
3707.3594 | 123.0835 | -122.8638 | 0.2243 | 0.068054 | 0.033218 | 0.0042298 | 0.0061865 | -0.0096792 | 0.0015744 | -0.0084381 | 0.094375 | -0.010418 | -0.006039 | 0.00037379 | 0.0051761 | -0.017425 | -0.013733 | -0.059509 | -0.07782 | -0.022888 | 0.28381 | -0.073242 | -0.23346 | -0.013733 | -0.004578 | -0.11444 | 0.21057 | 0.18768 | -0.19226 | -0.21973 | 122.7905 | 122.6303 | 0.059509 | 122.8043 | 122.8409 | 0.21057 | -0.23804 | 122.6715 | 122.644 | -0.013733 | 122.85 | 122.7493 | 0.10529 | -0.036621 | 123.1476 | 122.85 | 122.7859 | -0.45776 | 123.0743 | 123.0515 | 122.8592 | -0.44403
3709.125 | 123.1293 | -122.85 | 0.19226 | -0.015869 | 0.031509 | 0.0067932 | 0.0093909 | -0.01032 | -0.0069706 | -0.0080109 | 0.048599 | -0.013836 | -0.0062528 | -0.0026168 | 0.0015445 | -0.014435 | 0.07782 | 0.13733 | 0.10986 | 0.11902 | 0.31586 | 0.013733 | -0.15106 | 0.10529 | 0.17853 | 0.091553 | 0.23346 | 0.19226 | -0.07782 | -0.15106 | 122.8638 | 122.699 | 0.1236 | 122.9874 | 122.9691 | 0.27008 | -0.11444 | 122.7722 | 122.699 | 0.041198 | 122.9553 | 122.9416 | 0.24261 | 0 | 123.1659 | 122.9279 | 122.9599 | -0.34332 | 123.0835 | 123.0423 | 123.0286 | -0.34332
3710.8906 | 123.1567 | -122.818 | 0.1831 | -0.19135 | 0.030655 | 0.0059388 | 0.0078955 | -0.011815 | -0.004407 | -0.010147 | -0.096359 | -0.014477 | -0.0062528 | -0.003685 | 0.0023989 | -0.016357 | 0.18768 | 0.25635 | 0.20142 | 0.21057 | 0.36621 | 0.068665 | -0.10529 | 0.17853 | 0.25635 | 0.13275 | 0.26093 | 0.2243 | -0.036621 | -0.10071 | 122.8867 | 122.7127 | 0.18311 | 123.0743 | 123.0286 | 0.31586 | 0.004578 | 122.7814 | 122.7173 | 0.07782 | 122.9965 | 122.9507 | 0.23346 | 0.041199 | 123.1842 | 123.0057 | 123.0194 | -0.28839 | 123.0789 | 123.0423 | 123.0743 | -0.28381
3712.5938 | 123.0743 | -122.8363 | 0.20599 | 0.052795 | 0.033218 | 0.0065796 | 0.0066137 | -0.0098928 | 0.004565 | -0.0084381 | 0.025711 | -0.010632 | -0.0051846 | -0.0021896 | 0.0081667 | -0.016143 | -0.013733 | -0.059509 | -0.07782 | -0.036621 | 0.27466 | -0.09613 | -0.25635 | -0.009155 | -0.013733 | -0.11444 | 0.19684 | 0.16937 | -0.18768 | -0.23804 | 122.7402 | 122.58 | 0.068664 | 122.7768 | 122.7997 | 0.21973 | -0.21973 | 122.6486 | 122.5983 | -0.009156 | 122.8271 | 122.7219 | 0.1236 | -0.036621 | 123.111 | 122.8226 | 122.7585 | -0.46234 | 123.0331 | 123.0057 | 122.8226 | -0.44403
3714.3438 | 123.0698 | -122.8546 | 0.21515 | 0.1062 | 0.025528 | 0.008075 | 0.0053321 | -0.01032 | -0.005048 | -0.0084381 | 0.16304 | -0.013196 | -0.0051846 | -0.0034714 | 0.0036807 | -0.015503 | 0.082397 | 0.17853 | 0.10071 | 0.07782 | 0.27008 | -0.013733 | -0.15564 | 0.10986 | 0.16479 | 0.054932 | 0.21973 | 0.1831 | -0.09613 | -0.14648 | 122.8409 | 122.699 | 0.054932 | 123.0331 | 122.9324 | 0.23346 | -0.13275 | 122.7585 | 122.7081 | 0.004578 | 122.9645 | 122.9095 | 0.20142 | -0.032044 | 123.1247 | 122.937 | 122.9553 | -0.37079 | 123.0743 | 123.0377 | 123.0194 | -0.36163
3716.0938 | 123.0881 | -122.8317 | 0.21057 | 0.037537 | 0.027451 | 0.0089294 | 0.0068273 | -0.0096792 | -0.0046206 | -0.010788 | 0.079117 | -0.015118 | -0.00668 | -0.0047532 | 0.0017581 | -0.014435 | 0.09613 | 0.14191 | 0.11444 | 0.09613 | 0.32044 | 0.013733 | -0.16022 | 0.11902 | 0.15106 | 0.07782 | 0.24261 | 0.19226 | -0.082397 | -0.14191 | 122.8455 | 122.6715 | 0.10986 | 122.9736 | 122.9279 | 0.25635 | -0.11444 | 122.7493 | 122.6898 | 0.032044 | 122.9507 | 122.9095 | 0.21973 | -0.01831 | 123.1522 | 122.9279 | 122.9462 | -0.37079 | 123.0743 | 123.024 | 122.9828 | -0.35248
3717.7969 | 123.0743 | -122.85 | 0.20599 | 0.075684 | 0.034287 | 0.0067932 | 0.0064001 | -0.010106 | 0.004565 | -0.0088653 | -0.012436 | -0.0087093 | -0.0086026 | 0.00080099 | 0.0092349 | -0.016143 | 0.041199 | -0.036621 | -0.086975 | -0.022888 | 0.28381 | -0.073242 | -0.25635 | -0.004578 | -0.009155 | -0.1236 | 0.21057 | 0.1831 | -0.16022 | -0.23346 | 122.7768 | 122.5937 | 0.077819 | 122.8134 | 122.8271 | 0.23346 | -0.1648 | 122.6898 | 122.6166 | 0.004577 | 122.8455 | 122.7264 | 0.10986 | -0.022889 | 123.1338 | 122.8912 | 122.7631 | -0.46234 | 123.0606 | 123.0331 | 122.8409 | -0.43945
3719.5625 | 123.0835 | -122.8592 | 0.2243 | 0.19012 | 0.03215 | 0.0042298 | 0.0031957 | -0.0079702 | -0.0018436 | -0.0058747 | 0.1783 | -0.013196 | -0.0079618 | -0.0017624 | 0.0043215 | -0.015716 | 0.086975 | 0.11902 | 0.073242 | 0.073242 | 0.21515 | -0.064087 | -0.2243 | 0.10986 | 0.14648 | 0.036621 | 0.14648 | 0.09613 | -0.13275 | -0.17395 | 122.7951 | 122.6349 | -0.009155 | 122.9782 | 122.9324 | 0.29755 | -0.13733 | 122.7264 | 122.6852 | -0.07782 | 122.9691 | 122.8958 | 0.21057 | -0.12817 | 123.0743 | 122.9462 | 122.9324 | -0.44861 | 123.0057 | 122.9553 | 123.0057 | -0.39825
3721.25 | 123.2162 | -122.8043 | 0.17853 | -0.18372 | 0.032791 | 0.0044434 | 0.010459 | -0.0096792 | 7.902e-05 | -0.0080109 | -0.22606 | -0.0099911 | -0.0043302 | 0.00058739 | 0.0073123 | -0.017852 | 0.13275 | 0.10529 | 0.07782 | 0.1236 | 0.3891 | 0.004578 | -0.13733 | 0.086975 | 0.13275 | -0.018311 | 0.28839 | 0.25177 | -0.10071 | -0.15564 | 122.8088 | 122.6669 | 0.21057 | 122.9095 | 122.9279 | 0.26093 | -0.045777 | 122.7036 | 122.6486 | 0.10986 | 122.8912 | 122.7859 | 0.13733 | 0.073242 | 123.1934 | 122.937 | 122.8821 | -0.31586 | 123.0927 | 123.056 | 122.937 | -0.33417
3723 | 123.1567 | -122.8271 | 0.17395 | -0.19897 | 0.030014 | 0.006366 | 0.010245 | -0.01032 | -0.0037662 | -0.0099335 | -0.13451 | -0.0117 | -0.0051846 | -0.0021896 | 0.0017581 | -0.019134 | 0.20599 | 0.26093 | 0.19684 | 0.19684 | 0.36621 | 0.064087 | -0.07782 | 0.16937 | 0.25635 | 0.12817 | 0.26093 | 0.21973 | -0.032043 | -0.082397 | 122.8912 | 122.7493 | 0.19226 | 123.0881 | 123.024 | 0.27466 | 0.032044 | 122.7951 | 122.7448 | 0.086975 | 122.9965 | 122.9553 | 0.21057 | 0.045777 | 123.1934 | 123.0331 | 123.024 | -0.25177 | 123.0881 | 123.0469 | 123.0835 | -0.25635
3724.7656 | 123.1522 | -122.8134 | 0.19226 | -0.21423 | 0.031509 | 0.008075 | 0.0074683 | -0.0098928 | -0.0035526 | -0.0082245 | -0.12688 | -0.014905 | -0.0045438 | -0.0043258 | 0.0041079 | -0.016357 | 0.21057 | 0.27008 | 0.19226 | 0.18768 | 0.36163 | 0.050354 | -0.10529 | 0.1831 | 0.27008 | 0.13275 | 0.2655 | 0.22888 | -0.041199 | -0.10071 | 122.8638 | 122.7081 | 0.16937 | 123.0835 | 123.0011 | 0.29297 | 0.01831 | 122.7722 | 122.7127 | 0.073242 | 122.9965 | 122.9462 | 0.23346 | 0.036621 | 123.175 | 123.024 | 123.0057 | -0.29755 | 123.0789 | 123.0423 | 123.0835 | -0.29297
3726.5156 | 123.1842 | -122.7997 | 0.16937 | -0.038757 | 0.028092 | 0.0055114 | 0.0087499 | -0.008611 | -0.0041934 | -0.010147 | 0.010452 | -0.014264 | -0.0088162 | -0.0024032 | 0.0015445 | -0.015289 | 0.13275 | 0.17853 | 0.14648 | 0.14648 | 0.32501 | 0.022888 | -0.15564 | 0.17853 | 0.26093 | 0.13733 | 0.24719 | 0.21973 | -0.068665 | -0.091553 | 122.8226 | 122.644 | 0.15564 | 122.9782 | 122.9462 | 0.30212 | -0.036622 | 122.731 | 122.7081 | 0.077819 | 122.9782 | 122.937 | 0.22888 | 0.050354 | 123.1247 | 122.9324 | 122.9462 | -0.32501 | 123.0469 | 123.0194 | 123.0606 | -0.26093
3728.2812 | 123.1888 | -122.8317 | 0.19226 | -0.076904 | 0.0345 | 0.0033752 | 0.0064001 | -0.009252 | 0.004565 | -0.0077973 | -0.21843 | -0.0099911 | -0.0068936 | -0.0011216 | 0.0088077 | -0.018921 | 0.15564 | 0.10071 | 0.045776 | 0.073242 | 0.32501 | -0.036621 | -0.1831 | 0.10071 | 0.1236 | -0.032043 | 0.2243 | 0.20142 | -0.13733 | -0.1831 | 122.7951 | 122.6486 | 0.13275 | 122.9324 | 122.905 | 0.25635 | -0.036621 | 122.6944 | 122.6486 | 0.032043 | 122.9324 | 122.7997 | 0.15106 | 0.009155 | 123.1567 | 122.9874 | 122.8775 | -0.37537 | 123.056 | 123.0331 | 122.9553 | -0.37537
3730.0469 | 123.1934 | -122.8043 | 0.1831 | -0.031128 | 0.028519 | 0.0078614 | 0.0044775 | -0.0081838 | -0.0071842 | -0.0080109 | -0.020065 | -0.013409 | -0.0062528 | -0.0038986 | 0.0026125 | -0.012726 | 0.11902 | 0.17395 | 0.15106 | 0.13733 | 0.33875 | 0.009155 | -0.13733 | 0.17395 | 0.23804 | 0.15106 | 0.26093 | 0.20599 | -0.054932 | -0.11902 | 122.8134 | 122.6669 | 0.15564 | 122.9782 | 122.9416 | 0.27466 | -0.064086 | 122.7493 | 122.6852 | 0.07782 | 122.9782 | 122.9553 | 0.27008 | 0.022889 | 123.143 | 122.9233 | 122.9553 | -0.32043 | 123.0652 | 123.0103 | 123.0423 | -0.30212
3731.7969 | 123.056 | -122.8638 | 0.21973 | 0.12146 | 0.028092 | 0.0061524 | 0.0053321 | -0.010534 | -0.0018436 | -0.0084381 | 0.094375 | -0.0117 | -0.0058254 | -0.00048061 | 0.0032535 | -0.016998 | 0.10529 | 0.11902 | 0.10071 | 0.07782 | 0.27008 | -0.032043 | -0.18768 | 0.13275 | 0.15564 | 0.050354 | 0.21515 | 0.18768 | -0.091553 | -0.14648 | 122.8317 | 122.6761 | 0.050354 | 122.9828 | 122.9416 | 0.2655 | -0.11444 | 122.7722 | 122.7173 | -0.004578 | 122.9965 | 122.9141 | 0.19684 | -0.032044 | 123.1339 | 122.9691 | 122.9645 | -0.40741 | 123.0789 | 123.0515 | 123.0194 | -0.36621
3733.5625 | 123.1201 | -122.8409 | 0.20599 | 0.098572 | 0.034287 | 0.007434 | 0.0057593 | -0.0096792 | 0.0039242 | -0.0075837 | 0.025711 | -0.011059 | -0.0068936 | -0.0015488 | 0.0090213 | -0.017852 | 0.004578 | -0.027466 | -0.082397 | -0.018311 | 0.27924 | -0.10529 | -0.2655 | 0.022888 | 0.009155 | -0.10986 | 0.21515 | 0.16022 | -0.17853 | -0.23804 | 122.7356 | 122.5754 | 0.073242 | 122.8134 | 122.8226 | 0.24719 | -0.20142 | 122.6624 | 122.6028 | 0.009155 | 122.8638 | 122.731 | 0.12817 | -0.045777 | 123.1201 | 122.8455 | 122.7585 | -0.4715 | 123.056 | 123.0011 | 122.85 | -0.44403
3735.25 | 123.1567 | -122.85 | 0.17853 | -0.19135 | 0.031082 | 0.0082886 | 0.0076819 | -0.0083974 | -0.0035526 | -0.0075837 | -0.23369 | -0.0117 | -0.0058254 | -0.0030442 | 0.0023989 | -0.016143 | 0.21057 | 0.23346 | 0.1831 | 0.19226 | 0.36163 | 0.054932 | -0.11444 | 0.16022 | 0.24261 | 0.10071 | 0.27466 | 0.2655 | -0.064087 | -0.09613 | 122.905 | 122.7356 | 0.1831 | 123.0835 | 123.0423 | 0.3067 | 0.032043 | 122.7859 | 122.7539 | 0.09613 | 123.0103 | 122.9507 | 0.19684 | 0.086975 | 123.2117 | 123.0606 | 123.0331 | -0.29297 | 123.1247 | 123.1155 | 123.0927 | -0.27466
3737 | 123.1567 | -122.8317 | 0.16937 | -0.19897 | 0.029373 | 0.0061524 | 0.010245 | -0.0071158 | -0.0022708 | -0.010788 | -0.18791 | -0.01405 | -0.0028348 | -0.0011216 | 0.0041079 | -0.016784 | 0.20142 | 0.23804 | 0.17853 | 0.17853 | 0.35706 | 0.054932 | -0.10529 | 0.17395 | 0.26093 | 0.10986 | 0.27924 | 0.23804 | -0.050354 | -0.09613 | 122.8867 | 122.7264 | 0.18768 | 123.0698 | 123.0103 | 0.28381 | 0.032043 | 122.7814 | 122.7356 | 0.10986 | 123.0057 | 122.9416 | 0.20599 | 0.068664 | 123.1888 | 123.0331 | 123.0103 | -0.27466 | 123.111 | 123.0698 | 123.0927 | -0.2655
3738.7656 | 123.0835 | -122.8592 | 0.21515 | -0.023499 | 0.031723 | 0.0072204 | 0.0053321 | -0.0079702 | 0.004565 | -0.0060883 | -0.012436 | -0.011487 | -0.0056118 | -0.0030442 | 0.0083805 | -0.016571 | 0.07782 | 0.050354 | -0.036621 | 0.018311 | 0.30212 | -0.059509 | -0.21973 | 0.009155 | 0.027466 | -0.11444 | 0.19684 | 0.16479 | -0.1831 | -0.22888 | 122.7997 | 122.6395 | 0.086975 | 122.9095 | 122.8775 | 0.23804 | -0.13733 | 122.6761 | 122.6303 | -0.018311 | 122.8683 | 122.7448 | 0.11444 | -0.050354 | 123.1613 | 122.937 | 122.8226 | -0.43488 | 123.056 | 123.024 | 122.8867 | -0.44403
3740.5469 | 123.1567 | -122.818 | 0.19684 | -0.2066 | 0.031723 | 0.0052978 | 0.0066137 | -0.0081838 | -0.002698 | -0.0075837 | -0.23369 | -0.014264 | -0.006039 | -0.0038986 | 0.0053897 | -0.015289 | 0.1236 | 0.16937 | 0.091553 | 0.11444 | 0.42114 | 0.041199 | -0.13275 | 0.086975 | 0.16022 | 0.041199 | 0.31586 | 0.25635 | -0.064087 | -0.13733 | 122.8592 | 122.6852 | 0.2243 | 122.9874 | 122.9324 | 0.24719 | -0.073242 | 122.7539 | 122.6807 | 0.11902 | 122.905 | 122.8592 | 0.17853 | 0.05951 | 123.2391 | 122.9416 | 122.9095 | -0.32959 | 123.1338 | 123.0743 | 122.9782 | -0.33417
3742.25 | 123.1705 | -122.8134 | 0.18768 | 0.022278 | 0.027664 | 0.0082886 | 0.0036231 | -0.0077566 | -0.0071842 | -0.0095063 | 0.03334 | -0.013196 | -0.0047574 | -5.3406e-05 | 0.0015445 | -0.01593 | 0.091553 | 0.15564 | 0.11444 | 0.11902 | 0.33417 | 0.022888 | -0.15106 | 0.14648 | 0.21057 | 0.10529 | 0.24719 | 0.20599 | -0.073242 | -0.13275 | 122.8363 | 122.6624 | 0.14648 | 122.9691 | 122.9324 | 0.27008 | -0.09613 | 122.7402 | 122.6807 | 0.059509 | 122.9599 | 122.9187 | 0.23804 | 0.018311 | 123.1476 | 122.905 | 122.9279 | -0.33874 | 123.0606 | 123.0194 | 123.024 | -0.32043
3744 | 123.1934 | -122.7905 | 0.17395 | -0.046387 | 0.028305 | 0.0067932 | 0.0085363 | -0.0083974 | -0.0048344 | -0.010574 | -0.073471 | -0.015759 | -0.0053982 | -0.0028306 | 0.00026273 | -0.016357 | 0.14648 | 0.19226 | 0.16022 | 0.15106 | 0.32959 | 0.036621 | -0.14648 | 0.20599 | 0.28381 | 0.15564 | 0.27466 | 0.21973 | -0.045776 | -0.091553 | 122.8271 | 122.644 | 0.15564 | 122.9828 | 122.9416 | 0.29755 | -0.027466 | 122.7448 | 122.699 | 0.10071 | 122.9965 | 122.9462 | 0.24719 | 0.045777 | 123.1201 | 122.937 | 122.9507 | -0.32043 | 123.0652 | 123.0103 | 123.0743 | -0.2655
3745.7656 | 123.1705 | -122.8088 | 0.19226 | -0.17609 | 0.030655 | 0.006366 | 0.0055457 | -0.010961 | 0.00050622 | -0.010574 | -0.28709 | -0.012127 | -0.0071072 | -0.0017624 | 0.0043215 | -0.015716 | 0.13275 | 0.16479 | 0.086975 | 0.12817 | 0.42114 | 0.041199 | -0.13275 | 0.091553 | 0.15106 | 0 | 0.3067 | 0.26093 | -0.07782 | -0.12817 | 122.85 | 122.6761 | 0.22888 | 122.9736 | 122.937 | 0.26093 | -0.05951 | 122.731 | 122.6807 | 0.11444 | 122.9004 | 122.8088 | 0.12817 | 0.068664 | 123.23 | 122.9416 | 122.8958 | -0.32501 | 123.1155 | 123.0698 | 122.9599 | -0.32044
3747.5469 | 123.1842 | -122.8271 | 0.17395 | -0.25238 | 0.03215 | 0.0078614 | 0.0076819 | -0.007543 | 0.00071982 | -0.0069427 | -0.26421 | -0.011487 | -0.0071072 | -0.0032578 | 0.0047489 | -0.016998 | 0.13733 | 0.15564 | 0.091553 | 0.12817 | 0.40741 | 0.041199 | -0.11902 | 0.082397 | 0.15564 | 0.013733 | 0.31128 | 0.27466 | -0.086975 | -0.13275 | 122.8683 | 122.7081 | 0.23346 | 122.9828 | 122.9553 | 0.24719 | -0.036621 | 122.7402 | 122.6944 | 0.13733 | 122.9095 | 122.8409 | 0.14648 | 0.10071 | 123.2346 | 122.9645 | 122.9187 | -0.29297 | 123.1384 | 123.1018 | 122.9828 | -0.3067
3749.25 | 123.1842 | -122.8134 | 0.19684 | -0.10742 | 0.03215 | 0.0027344 | 0.0091773 | -0.0083974 | 0.0060604 | -0.0058747 | -0.18028 | -0.010846 | -0.0073208 | -0.001976 | 0.0081667 | -0.019989 | 0.13275 | 0.11902 | 0.036621 | 0.10071 | 0.32044 | -0.041199 | -0.18768 | 0.082397 | 0.13275 | -0.045776 | 0.21515 | 0.19684 | -0.13733 | -0.19226 | 122.7722 | 122.6257 | 0.1236 | 122.9324 | 122.9141 | 0.28839 | -0.064087 | 122.6761 | 122.6212 | 0.018311 | 122.8958 | 122.7676 | 0.14648 | 0 | 123.1339 | 122.9462 | 122.85 | -0.38452 | 123.0286 | 123.0103 | 122.9462 | -0.3891
3751 | 123.1567 | -122.8409 | 0.19226 | -0.26001 | 0.032578 | 0.0061524 | 0.010673 | -0.0096792 | -0.00098918 | -0.0065155 | -0.24132 | -0.013196 | -0.0062528 | -0.0021896 | 0.00026273 | -0.015716 | 0.15106 | 0.21515 | 0.12817 | 0.16937 | 0.39368 | 0.041199 | -0.11444 | 0.10071 | 0.17395 | 0.032043 | 0.31586 | 0.27008 | -0.082397 | -0.12817 | 122.8821 | 122.7264 | 0.20142 | 123.056 | 123.0103 | 0.28381 | -0.041199 | 122.7585 | 122.7127 | 0.1236 | 122.9416 | 122.8729 | 0.16022 | 0.07782 | 123.2346 | 122.9919 | 122.9691 | -0.3067 | 123.1567 | 123.111 | 123.0148 | -0.32044
3752.7656 | 123.0789 | -122.8592 | 0.20142 | 0.16724 | 0.030014 | 0.0044434 | 0.0044775 | -0.0081838 | -0.002698 | -0.0069427 | 0.20119 | -0.013836 | -0.0086026 | -0.0032578 | 0.0049625 | -0.014862 | 0.091553 | 0.13733 | 0.054932 | 0.059509 | 0.21973 | -0.041199 | -0.21973 | 0.11444 | 0.15106 | 0.036621 | 0.14648 | 0.10529 | -0.14648 | -0.1831 | 122.818 | 122.6395 | 0.018311 | 122.9965 | 122.9187 | 0.27924 | -0.10986 | 122.7127 | 122.6761 | -0.054932 | 122.9736 | 122.8958 | 0.21973 | -0.09613 | 123.0789 | 122.9507 | 122.9141 | -0.42114 | 123.0057 | 122.9645 | 123.0103 | -0.38452
3754.4531 | 123.1888 | -122.818 | 0.15564 | -0.25238 | 0.030655 | 0.0065796 | 0.0085363 | -0.01032 | 0.00093342 | -0.0075837 | -0.29472 | -0.010632 | -0.0071072 | -0.0013352 | 0.0023989 | -0.016571 | 0.14191 | 0.15564 | 0.07782 | 0.10529 | 0.41657 | 0.036621 | -0.13275 | 0.086975 | 0.14191 | 0.009155 | 0.3067 | 0.27008 | -0.086975 | -0.14191 | 122.8546 | 122.6852 | 0.26093 | 122.9736 | 122.9233 | 0.23804 | -0.013733 | 122.731 | 122.6761 | 0.15106 | 122.905 | 122.8271 | 0.15106 | 0.11444 | 123.2346 | 122.9599 | 122.8958 | -0.28839 | 123.1247 | 123.0881 | 122.9599 | -0.29755
3756.2188 | 123.0972 | -122.8317 | 0.20142 | 0.12146 | 0.0298 | 0.0055114 | 0.0059729 | -0.008611 | -0.00098918 | -0.0067291 | 0.1783 | -0.010632 | -0.0075344 | -0.00026701 | 0.0058169 | -0.016143 | 0.09613 | 0.10529 | 0.054932 | 0.07782 | 0.21057 | -0.045776 | -0.20599 | 0.10986 | 0.1236 | 0.009155 | 0.14648 | 0.10986 | -0.13275 | -0.19684 | 122.7859 | 122.6257 | 0.009155 | 122.937 | 122.9095 | 0.28381 | -0.10529 | 122.699 | 122.6349 | -0.054932 | 122.9416 | 122.8409 | 0.20599 | -0.091553 | 123.0423 | 122.9279 | 122.8867 | -0.40741 | 122.9782 | 122.9416 | 122.9553 | -0.39825
3758 | 123.1476 | -122.8134 | 0.16022 | -0.18372 | 0.031723 | 0.004657 | 0.0046911 | -0.0083974 | -0.003339 | -0.0099335 | -0.22606 | -0.01405 | -0.0068936 | -0.0026168 | 0.0017581 | -0.015075 | 0.20142 | 0.21973 | 0.19226 | 0.19226 | 0.35248 | 0.059509 | -0.10529 | 0.17395 | 0.27008 | 0.10986 | 0.29755 | 0.26093 | -0.045776 | -0.10986 | 122.8729 | 122.7081 | 0.19226 | 123.0331 | 123.0057 | 0.29755 | 0.041199 | 122.7676 | 122.7036 | 0.13733 | 122.9874 | 122.9233 | 0.21973 | 0.10071 | 123.1659 | 123.0148 | 123.0057 | -0.2655 | 123.111 | 123.0743 | 123.0835 | -0.27008
3759.7656 | 123.0606 | -122.8638 | 0.20142 | 0.16724 | 0.029373 | 0.0067932 | 0.0055457 | -0.0081838 | -0.004407 | -0.0071563 | 0.11726 | -0.01405 | -0.0092434 | -0.0015488 | 0.0068851 | -0.015289 | 0.13275 | 0.12817 | 0.068665 | 0.054932 | 0.21057 | -0.082397 | -0.21057 | 0.12817 | 0.15106 | 0.032043 | 0.18768 | 0.13275 | -0.13733 | -0.16479 | 122.7814 | 122.6532 | 0.009155 | 122.9919 | 122.9187 | 0.2655 | -0.068665 | 122.7264 | 122.699 | -0.013733 | 122.9919 | 122.8958 | 0.19684 | -0.068665 | 123.0743 | 122.9965 | 122.9324 | -0.41199 | 123.0515 | 122.9965 | 123.0148 | -0.36621
3761.4531 | 123.1476 | -122.8271 | 0.19226 | -0.22186 | 0.029587 | 0.0050842 | 0.0091773 | -0.010106 | -0.004407 | -0.0075837 | -0.27184 | -0.012982 | -0.0051846 | -0.0028306 | 0.0023989 | -0.016357 | 0.20599 | 0.2243 | 0.16022 | 0.1831 | 0.37994 | 0.045776 | -0.11444 | 0.12817 | 0.21515 | 0.068665 | 0.3067 | 0.27008 | -0.054932 | -0.11444 | 122.8729 | 122.7127 | 0.18768 | 123.0515 | 123.0103 | 0.29755 | 0.013733 | 122.7722 | 122.7127 | 0.11444 | 122.9553 | 122.8958 | 0.18311 | 0.07782 | 123.2071 | 123.0331 | 122.9874 | -0.3067 | 123.1338 | 123.0972 | 123.0423 | -0.3067
3763.2031 | 123.1201 | -122.818 | 0.21057 | 0.12909 | 0.0345 | 0.004657 | 0.0072547 | -0.0079702 | 0.0041378 | -0.0063019 | 0.10963 | -0.011059 | -0.0017666 | -0.00026701 | 0.0073123 | -0.01593 | 0.054932 | 0 | -0.045776 | 0.004578 | 0.29297 | -0.091553 | -0.25635 | 0.041199 | 0.022888 | -0.068665 | 0.21515 | 0.15106 | -0.16937 | -0.22888 | 122.7264 | 122.5616 | 0.082398 | 122.818 | 122.8226 | 0.26093 | -0.15564 | 122.6486 | 122.5891 | 0.004578 | 122.8592 | 122.7493 | 0.16022 | -0.059509 | 123.111 | 122.8729 | 122.7722 | -0.46692 | 123.0331 | 122.9691 | 122.8409 | -0.43945
3764.9688 | 123.2025 | -122.7951 | 0.17853 | -0.25238 | 0.033432 | 0.007434 | 0.0076819 | -0.0069022 | 7.902e-05 | -0.0092927 | -0.20317 | -0.012768 | -0.0034756 | -0.0032578 | 0.0047489 | -0.016571 | 0.13733 | 0.1236 | 0.064087 | 0.10986 | 0.41657 | 0.041199 | -0.13275 | 0.064087 | 0.1236 | -0.009155 | 0.3067 | 0.24261 | -0.10529 | -0.16022 | 122.8363 | 122.6624 | 0.23804 | 122.9187 | 122.905 | 0.24261 | -0.041199 | 122.6898 | 122.6349 | 0.12817 | 122.8592 | 122.7859 | 0.15106 | 0.064087 | 123.2117 | 122.9324 | 122.8592 | -0.31128 | 123.1018 | 123.0377 | 122.9187 | -0.33874
3766.6719 | 123.0835 | -122.8638 | 0.19684 | 0.083313 | 0.034927 | 0.0042298 | 0.0057593 | -0.0073294 | 0.0011472 | -0.0060883 | 0.094375 | -0.010205 | -0.0073208 | -0.0024032 | 0.0092349 | -0.015503 | 0.004578 | -0.032043 | -0.059509 | -0.022888 | 0.28839 | -0.07782 | -0.24261 | 0 | -0.018311 | -0.11902 | 0.19684 | 0.15564 | -0.17853 | -0.23346 | 122.7859 | 122.6212 | 0.091553 | 122.8317 | 122.8409 | 0.21973 | -0.19226 | 122.6852 | 122.6303 | 0 | 122.8638 | 122.7448 | 0.11444 | -0.041198 | 123.1522 | 122.8683 | 122.8043 | -0.43945 | 123.0606 | 123.0194 | 122.8455 | -0.4303
3768.4375 | 123.0789 | -122.8592 | 0.20599 | 0.21301 | 0.0298 | 0.0040162 | 0.0055457 | -0.0083974 | -0.0014164 | -0.0071563 | 0.18593 | -0.012555 | -0.006039 | -0.0024032 | 0.0062441 | -0.01593 | 0.073242 | 0.10071 | 0.068665 | 0.068665 | 0.21515 | -0.073242 | -0.2243 | 0.10071 | 0.15564 | 0.045776 | 0.1236 | 0.11902 | -0.16479 | -0.19684 | 122.7859 | 122.6349 | 0.009155 | 122.9599 | 122.9279 | 0.29297 | -0.13275 | 122.6944 | 122.6624 | -0.082398 | 122.9599 | 122.905 | 0.24261 | -0.086975 | 123.0743 | 122.9324 | 122.9279 | -0.4303 | 122.9828 | 122.9782 | 123.0148 | -0.40283
3770.1562 | 123.111 | -122.85 | 0.21515 | 0.15961 | 0.03215 | 0.0050842 | 0.0068273 | -0.011388 | 0.00050622 | -0.0080109 | 0.12489 | -0.011273 | -0.0058254 | 0.0012284 | 0.0041079 | -0.017852 | 0.082397 | 0.07782 | 0.036621 | 0.050354 | 0.23804 | -0.064087 | -0.23346 | 0.11902 | 0.13275 | 0.022888 | 0.16937 | 0.13733 | -0.13275 | -0.17853 | 122.7859 | 122.6166 | 0.022888 | 122.9279 | 122.9004 | 0.28381 | -0.13275 | 122.7173 | 122.6715 | -0.045776 | 122.9691 | 122.8729 | 0.20142 | -0.07782 | 123.0881 | 122.9324 | 122.8867 | -0.44861 | 123.0194 | 122.9874 | 122.9828 | -0.39368
3771.9219 | 123.0652 | -122.8592 | 0.21515 | 0.083313 | 0.033005 | 0.0052978 | 0.0046911 | -0.009252 | 0.00093342 | -0.0077973 | -0.012436 | -0.010846 | -0.0075344 | 0.00016019 | 0.0066715 | -0.01593 | 0.018311 | -0.036621 | -0.086975 | 0.004578 | 0.28839 | -0.073242 | -0.25177 | -0.036621 | 0.009155 | -0.11444 | 0.21057 | 0.17853 | -0.16937 | -0.22888 | 122.7859 | 122.6074 | 0.073242 | 122.8226 | 122.8638 | 0.25635 | -0.19684 | 122.6898 | 122.6303 | -0.004578 | 122.8226 | 122.7448 | 0.11444 | -0.036621 | 123.1476 | 122.8775 | 122.7722 | -0.46692 | 123.0698 | 123.0377 | 122.8683 | -0.44403
3773.6875 | 123.1064 | -122.8455 | 0.20142 | 0.13672 | 0.033005 | 0.006366 | 0.0072547 | -0.0071158 | 0.0026424 | -0.0054475 | 0.094375 | -0.013196 | -0.0068936 | -0.0015488 | 0.0062441 | -0.015716 | 0 | -0.036621 | -0.068665 | -0.022888 | 0.24719 | -0.091553 | -0.2655 | -0.004578 | 0 | -0.10071 | 0.19684 | 0.17853 | -0.18768 | -0.24719 | 122.7539 | 122.58 | 0.045776 | 122.8088 | 122.8226 | 0.24261 | -0.20142 | 122.6578 | 122.5983 | -0.004578 | 122.8409 | 122.7448 | 0.14648 | -0.022888 | 123.0927 | 122.8455 | 122.7768 | -0.46692 | 123.0423 | 123.024 | 122.8455 | -0.44861
3775.4688 | 123.0835 | -122.8775 | 0.21515 | -0.031128 | 0.033646 | 0.0067932 | 0.0059729 | -0.008611 | 7.902e-05 | -0.0058747 | -0.020065 | -0.012768 | -0.0064664 | -0.00026701 | 0.0066715 | -0.016998 | 0.068665 | 0.050354 | -0.022888 | 0.018311 | 0.29297 | -0.050354 | -0.21515 | 0.009155 | 0.032043 | -0.11902 | 0.20142 | 0.16479 | -0.17853 | -0.2243 | 122.8271 | 122.6624 | 0.07782 | 122.9279 | 122.8958 | 0.23346 | -0.14648 | 122.699 | 122.6532 | -0.013733 | 122.8867 | 122.7585 | 0.10529 | -0.050354 | 123.1705 | 122.9462 | 122.8546 | -0.4303 | 123.0789 | 123.0423 | 122.9095 | -0.43945
3777.2188 | 123.1979 | -122.8546 | 0.18768 | -0.19135 | 0.035141 | 0.0044434 | 0.0093909 | -0.0098928 | -0.00034818 | -0.0080109 | -0.17265 | -0.011487 | -0.0034756 | -0.00069421 | 0.0036807 | -0.016143 | 0.11902 | 0.11444 | 0.07782 | 0.10986 | 0.37537 | 0.018311 | -0.16022 | 0.064087 | 0.14191 | 0 | 0.24719 | 0.21515 | -0.11444 | -0.19226 | 122.8729 | 122.6944 | 0.18768 | 122.9691 | 122.9645 | 0.27008 | -0.068664 | 122.7402 | 122.6624 | 0.059509 | 122.9187 | 122.8546 | 0.19226 | 0.027466 | 123.23 | 122.9736 | 122.9324 | -0.3479 | 123.1018 | 123.0698 | 122.9965 | -0.37994
3778.9844 | 123.0743 | -122.8958 | 0.22888 | 0.052795 | 0.032791 | 0.0044434 | 0.0044775 | -0.01032 | 0.00093342 | -0.0073701 | 0.04097 | -0.011914 | -0.0075344 | -0.0011216 | 0.0060305 | -0.015716 | 0.009155 | 0.009155 | -0.054932 | -0.004578 | 0.28839 | -0.068665 | -0.24261 | -0.036621 | 0.009155 | -0.10986 | 0.21515 | 0.16479 | -0.17853 | -0.25177 | 122.8271 | 122.6532 | 0.059509 | 122.905 | 122.8912 | 0.23804 | -0.21973 | 122.7173 | 122.644 | -0.013733 | 122.8592 | 122.7859 | 0.14191 | -0.064087 | 123.1842 | 122.905 | 122.8409 | -0.4715 | 123.111 | 123.0606 | 122.905 | -0.48065
3780.75 | 123.056 | -122.8729 | 0.19226 | 0.14435 | 0.031082 | 0.0072204 | 0.0046911 | -0.008611 | -0.0041934 | -0.0095063 | 0.17067 | -0.014691 | -0.0071072 | -0.0021896 | 0.0017581 | -0.017425 | 0.050354 | 0.11444 | 0.082397 | 0.082397 | 0.2243 | -0.059509 | -0.21515 | 0.10529 | 0.16022 | 0.054932 | 0.15564 | 0.13275 | -0.12817 | -0.15564 | 122.8134 | 122.6578 | 0.032043 | 122.9874 | 122.9553 | 0.29755 | -0.14191 | 122.7448 | 122.7173 | -0.036621 | 122.9782 | 122.9279 | 0.21057 | -0.05951 | 123.0972 | 122.9233 | 122.9553 | -0.40741 | 123.0286 | 123.0057 | 123.0331 | -0.3479
3782.5 | 123.1705 | -122.8271 | 0.17853 | 0.0070193 | 0.02916 | 0.0070068 | 0.0066137 | -0.0069022 | -0.0076114 | -0.010574 | 0.04097 | -0.01405 | -0.0030484 | -0.0032578 | 0.00026273 | -0.014007 | 0.086975 | 0.12817 | 0.10529 | 0.1236 | 0.32501 | 0.013733 | -0.15564 | 0.10986 | 0.19226 | 0.1236 | 0.24261 | 0.23346 | -0.082397 | -0.14191 | 122.8409 | 122.6715 | 0.14648 | 122.9553 | 122.9507 | 0.27924 | -0.091553 | 122.7448 | 122.6852 | 0.064087 | 122.937 | 122.9507 | 0.2655 | 0.054931 | 123.1522 | 122.9141 | 122.9324 | -0.33417 | 123.0698 | 123.0606 | 123.0194 | -0.32044
3784.2031 | 123.0835 | -122.8729 | 0.21057 | -0.061646 | 0.033005 | 0.0070068 | 0.0070409 | -0.0081838 | 0.0028562 | -0.0067291 | -0.058212 | -0.012127 | -0.0086026 | -5.3406e-05 | 0.0081667 | -0.019134 | 0.1236 | 0.07782 | 0 | 0.054932 | 0.31586 | -0.045776 | -0.21057 | 0.018311 | 0.064087 | -0.086975 | 0.21057 | 0.18768 | -0.16022 | -0.21057 | 122.8271 | 122.6624 | 0.10529 | 122.9507 | 122.9279 | 0.2655 | -0.086975 | 122.7127 | 122.6624 | 0 | 122.8912 | 122.7859 | 0.1236 | -0.022888 | 123.1888 | 122.9965 | 122.8729 | -0.42114 | 123.0835 | 123.0606 | 122.937 | -0.42114
3785.9688 | 123.1155 | -122.8592 | 0.20599 | 0.1062 | 0.0345 | 0.0050842 | 0.0055457 | -0.007543 | 0.0013608 | -0.0099335 | 0.18593 | -0.012127 | -0.007748 | -0.0038986 | 0.0075259 | -0.015289 | 0.022888 | -0.004578 | -0.050354 | -0.018311 | 0.27924 | -0.07782 | -0.25177 | 0.041199 | 0.041199 | -0.041199 | 0.1831 | 0.15564 | -0.16022 | -0.20142 | 122.7814 | 122.6074 | 0.073242 | 122.8546 | 122.8409 | 0.23346 | -0.18311 | 122.699 | 122.6578 | -0.022889 | 122.9004 | 122.818 | 0.16022 | -0.050354 | 123.1384 | 122.8821 | 122.8088 | -0.45776 | 123.0423 | 123.0148 | 122.9004 | -0.40741
3787.6719 | 123.1522 | -122.8363 | 0.1831 | -0.19897 | 0.032364 | 0.006366 | 0.0081091 | -0.0051932 | -0.004407 | -0.0077973 | -0.20317 | -0.013623 | -0.0039028 | -0.0038986 | 0.0030399 | -0.016998 | 0.17853 | 0.24261 | 0.17853 | 0.20142 | 0.36163 | 0.032043 | -0.10529 | 0.14191 | 0.2243 | 0.10986 | 0.28839 | 0.24261 | -0.041199 | -0.09613 | 122.8683 | 122.731 | 0.17853 | 123.0789 | 123.0377 | 0.3067 | -0.004577 | 122.7951 | 122.7402 | 0.10529 | 122.9782 | 122.9462 | 0.20599 | 0.05951 | 123.1979 | 123.0148 | 123.0148 | -0.28839 | 123.1247 | 123.0789 | 123.0606 | -0.27924
3789.4219 | 123.0835 | -122.8729 | 0.21515 | 0.075684 | 0.030869 | 0.004657 | 0.0074683 | -0.012029 | -0.0071842 | -0.010147 | 0.12489 | -0.014905 | -0.0036892 | -0.0017624 | 0.0030399 | -0.014221 | 0.082397 | 0.11902 | 0.091553 | 0.091553 | 0.30212 | -0.009155 | -0.16479 | 0.09613 | 0.15106 | 0.082397 | 0.20599 | 0.1831 | -0.10071 | -0.15106 | 122.8638 | 122.7081 | 0.086975 | 122.9919 | 122.9645 | 0.25635 | -0.13275 | 122.7722 | 122.7219 | -0.009155 | 122.9691 | 122.9553 | 0.23346 | -0.032044 | 123.175 | 122.9553 | 122.9645 | -0.37994 | 123.0789 | 123.056 | 123.024 | -0.36621
3791.1875 | 123.1613 | -122.8043 | 0.18768 | -0.18372 | 0.029373 | 0.0059388 | 0.0089635 | -0.0077566 | -0.0037662 | -0.0075837 | -0.16502 | -0.013409 | -0.003262 | -0.0030442 | 0.00026273 | -0.016143 | 0.20142 | 0.27924 | 0.24261 | 0.21057 | 0.37079 | 0.07782 | -0.086975 | 0.19684 | 0.28381 | 0.15564 | 0.25635 | 0.22888 | -0.045776 | -0.082397 | 122.8821 | 122.7173 | 0.18311 | 123.0835 | 123.0148 | 0.29755 | 0.013733 | 122.7585 | 122.7219 | 0.068665 | 123.0011 | 122.9599 | 0.23804 | 0.041199 | 123.175 | 123.0057 | 123.0469 | -0.27466 | 123.0606 | 123.0331 | 123.0881 | -0.27008
3792.8906 | 123.1522 | -122.85 | 0.1831 | -0.19135 | 0.030441 | 0.010211 | 0.0098181 | -0.009252 | -0.0018436 | -0.0092927 | -0.22606 | -0.01405 | -0.0068936 | -0.0047532 | 0.0015445 | -0.017852 | 0.1831 | 0.25635 | 0.1831 | 0.20142 | 0.36621 | 0.050354 | -0.10529 | 0.15106 | 0.23804 | 0.10071 | 0.28839 | 0.2243 | -0.064087 | -0.091553 | 122.9004 | 122.7448 | 0.18311 | 123.1064 | 123.0515 | 0.3067 | 0 | 122.7859 | 122.7585 | 0.10529 | 123.0011 | 122.9507 | 0.19226 | 0.041199 | 123.2162 | 123.0331 | 123.0331 | -0.28839 | 123.1384 | 123.0743 | 123.0881 | -0.27466
3794.6406 | 123.111 | -122.8226 | 0.20599 | -0.00061023 | 0.027664 | 0.0072204 | 0.0089635 | -0.0088248 | -0.0022708 | -0.011642 | 0.048599 | -0.01405 | -0.0068936 | -0.0041122 | 0.0028263 | -0.013153 | 0.091553 | 0.13275 | 0.10071 | 0.10529 | 0.3067 | 0.013733 | -0.16022 | 0.11444 | 0.16937 | 0.091553 | 0.23804 | 0.21515 | -0.091553 | -0.1236 | 122.8363 | 122.6624 | 0.10071 | 122.9553 | 122.9279 | 0.2655 | -0.11444 | 122.731 | 122.699 | 0.032043 | 122.937 | 122.9141 | 0.21515 | 0.009155 | 123.1293 | 122.9141 | 122.9233 | -0.36621 | 123.0606 | 123.0377 | 122.9919 | -0.32959
3796.4219 | 123.0743 | -122.8821 | 0.20599 | 0.1825 | 0.030869 | 0.0048706 | 0.0053321 | -0.0096792 | -0.0014164 | -0.0082245 | 0.11726 | -0.013196 | -0.0075344 | -0.001976 | 0.0064577 | -0.018493 | 0.10071 | 0.12817 | 0.073242 | 0.054932 | 0.20599 | -0.050354 | -0.19684 | 0.10529 | 0.15106 | 0.032043 | 0.16022 | 0.12817 | -0.13275 | -0.17395 | 122.8317 | 122.6852 | 0 | 123.0103 | 122.937 | 0.25177 | -0.10529 | 122.7493 | 122.7081 | -0.045777 | 122.9874 | 122.9141 | 0.20599 | -0.07782 | 123.0881 | 122.9828 | 122.9553 | -0.40283 | 123.0423 | 123.0103 | 123.0331 | -0.37994
3798.2031 | 123.1705 | -122.8363 | 0.1831 | -0.092163 | 0.034287 | 0.0059388 | 0.0066137 | -0.008611 | 0.0032834 | -0.0075837 | -0.23369 | -0.012341 | -0.0051846 | -0.001976 | 0.0079531 | -0.019134 | 0.12817 | 0.12817 | 0.032043 | 0.082397 | 0.31128 | -0.009155 | -0.19226 | 0.09613 | 0.091553 | -0.054932 | 0.23804 | 0.17853 | -0.13275 | -0.19226 | 122.8271 | 122.644 | 0.12817 | 122.9645 | 122.9187 | 0.27466 | -0.054931 | 122.7036 | 122.644 | 0.054932 | 122.9324 | 122.7814 | 0.13733 | -0.004577 | 123.1476 | 122.9645 | 122.8683 | -0.37537 | 123.0743 | 123.0148 | 122.9279 | -0.37537
3799.9062 | 123.1384 | -122.8455 | 0.19226 | -0.23712 | 0.032791 | 0.008075 | 0.0085363 | -0.007543 | -0.0024844 | -0.0088653 | -0.26421 | -0.013623 | -0.0062528 | -0.0041122 | 0.0023989 | -0.016357 | 0.16937 | 0.24719 | 0.16022 | 0.17395 | 0.3891 | 0.032043 | -0.11902 | 0.1236 | 0.20599 | 0.073242 | 0.29755 | 0.25635 | -0.068665 | -0.09613 | 122.8775 | 122.7264 | 0.19684 | 123.0927 | 123.0194 | 0.29297 | -0.022888 | 122.7768 | 122.7493 | 0.10528 | 122.9691 | 122.9187 | 0.16937 | 0.064087 | 123.2346 | 123.0148 | 123.0057 | -0.31128 | 123.143 | 123.1018 | 123.0515 | -0.28839
3801.6719 | 123.0927 | -122.8546 | 0.21515 | 0.060425 | 0.033646 | 0.004657 | 0.0049047 | -0.008611 | 0.003497 | -0.0080109 | 0.025711 | -0.011914 | -0.007748 | -0.00069421 | 0.0070987 | -0.016784 | 0.004578 | -0.018311 | -0.068665 | -0.018311 | 0.30212 | -0.059509 | -0.25635 | -0.004578 | -0.004578 | -0.11902 | 0.20599 | 0.16937 | -0.19226 | -0.2243 | 122.7951 | 122.5983 | 0.086975 | 122.8363 | 122.8363 | 0.23804 | -0.21057 | 122.6624 | 122.6303 | -0.009155 | 122.85 | 122.7356 | 0.10529 | -0.045776 | 123.1567 | 122.8592 | 122.7859 | -0.4715 | 123.0606 | 123.024 | 122.85 | -0.43945
3803.4375 | 123.0789 | -122.8775 | 0.21057 | 0.045166 | 0.031509 | 0.0055114 | 0.0076819 | -0.0066884 | -0.0059024 | -0.0090791 | 0.102 | -0.014264 | -0.0068936 | -0.0028306 | 0.0043215 | -0.014007 | 0.073242 | 0.14191 | 0.10071 | 0.10071 | 0.3067 | 0.013733 | -0.15106 | 0.10986 | 0.15106 | 0.073242 | 0.2243 | 0.19226 | -0.091553 | -0.12817 | 122.8912 | 122.7264 | 0.096131 | 123.0194 | 122.9782 | 0.25177 | -0.13733 | 122.7859 | 122.7493 | 0.013733 | 122.9874 | 122.9507 | 0.20142 | -0.01831 | 123.1842 | 122.9507 | 122.9782 | -0.36163 | 123.1018 | 123.0698 | 123.0286 | -0.33875
3805.1406 | 123.1705 | -122.8363 | 0.20599 | -0.11505 | 0.034287 | 0.0042298 | 0.0089635 | -0.0083974 | 0.0028562 | -0.0056611 | -0.16502 | -0.011273 | -0.0058254 | -0.0015488 | 0.0056033 | -0.019134 | 0.14191 | 0.10071 | 0.045776 | 0.068665 | 0.32959 | -0.041199 | -0.20142 | 0.082397 | 0.10071 | -0.032043 | 0.21973 | 0.16937 | -0.14648 | -0.17853 | 122.7951 | 122.6349 | 0.1236 | 122.937 | 122.905 | 0.27008 | -0.064087 | 122.6898 | 122.6578 | 0.013733 | 122.9187 | 122.8043 | 0.14648 | -0.036621 | 123.1659 | 122.9782 | 122.8821 | -0.40741 | 123.056 | 123.0057 | 122.937 | -0.38452
3806.9062 | 123.0789 | -122.8775 | 0.2243 | 0.13672 | 0.0298 | 0.0048706 | 0.0051183 | -0.009252 | -0.0037662 | -0.0069427 | 0.16304 | -0.010846 | -0.0068936 | -0.0015488 | 0.0043215 | -0.014862 | 0.082397 | 0.14648 | 0.082397 | 0.068665 | 0.21515 | -0.045776 | -0.18768 | 0.11902 | 0.15106 | 0.041199 | 0.17395 | 0.13733 | -0.11902 | -0.1831 | 122.8317 | 122.6898 | -0.009155 | 123.024 | 122.9462 | 0.25635 | -0.14191 | 122.7585 | 122.6944 | -0.050354 | 122.9965 | 122.9187 | 0.2243 | -0.086975 | 123.0927 | 122.9599 | 122.9599 | -0.41199 | 123.0515 | 123.0148 | 123.0286 | -0.40741
3808.6094 | 123.1613 | -122.85 | 0.16937 | -0.22186 | 0.033005 | 0.0085022 | 0.0083227 | -0.010106 | -0.003339 | -0.0082245 | -0.2108 | -0.012982 | -0.004971 | -0.0011216 | 0.0045351 | -0.016998 | 0.19684 | 0.23346 | 0.17853 | 0.18768 | 0.37537 | 0.054932 | -0.10986 | 0.14191 | 0.21973 | 0.091553 | 0.29297 | 0.26093 | -0.054932 | -0.11444 | 122.905 | 122.7402 | 0.20599 | 123.0835 | 123.0377 | 0.29755 | 0.027465 | 122.7951 | 122.7356 | 0.1236 | 122.9919 | 122.9416 | 0.20599 | 0.091552 | 123.2254 | 123.0469 | 123.0286 | -0.27924 | 123.143 | 123.111 | 123.0698 | -0.28381
3810.375 | 123.1201 | -122.8317 | 0.19226 | 0.098572 | 0.032578 | 0.0065796 | 0.0036231 | -0.010106 | 0.0026424 | -0.0067291 | 0.13252 | -0.010846 | -0.0064664 | -0.0017624 | 0.0064577 | -0.018066 | 0.036621 | -0.009155 | -0.064087 | -0.013733 | 0.27008 | -0.091553 | -0.25635 | 0.045776 | 0.041199 | -0.064087 | 0.16937 | 0.15106 | -0.15564 | -0.20599 | 122.7402 | 122.5754 | 0.07782 | 122.8226 | 122.818 | 0.24262 | -0.15564 | 122.6761 | 122.6257 | -0.022888 | 122.8775 | 122.7676 | 0.14191 | -0.041199 | 123.1018 | 122.8683 | 122.7676 | -0.44861 | 123.0011 | 122.9828 | 122.8729 | -0.39826
3812.1406 | 123.1064 | -122.8546 | 0.18768 | -0.00061023 | 0.029587 | 0.0099976 | 0.0064001 | -0.010961 | -0.006116 | -0.0086517 | 0.094375 | -0.012982 | -0.0068936 | -0.0032578 | 0.00047633 | -0.015289 | 0.10529 | 0.13275 | 0.11444 | 0.086975 | 0.3067 | 0.009155 | -0.15564 | 0.10529 | 0.17395 | 0.073242 | 0.23804 | 0.21515 | -0.068665 | -0.14648 | 122.8638 | 122.699 | 0.11902 | 122.9874 | 122.9416 | 0.24261 | -0.082397 | 122.7859 | 122.7081 | 0.050354 | 122.9599 | 122.9279 | 0.21973 | 0.027466 | 123.1613 | 122.9599 | 122.9691 | -0.34332 | 123.0927 | 123.0698 | 123.0286 | -0.33417
3813.8438 | 123.1522 | -122.8226 | 0.20599 | -0.24475 | 0.031082 | 0.007434 | 0.0091773 | -0.0088248 | 0.00029262 | -0.0075837 | -0.16502 | -0.012555 | -0.0071072 | -0.0011216 | 0.0030399 | -0.015716 | 0.1831 | 0.14648 | 0.11444 | 0.13733 | 0.39368 | 0.041199 | -0.13733 | 0.086975 | 0.14648 | 0.027466 | 0.31128 | 0.27924 | -0.086975 | -0.11444 | 122.8638 | 122.6852 | 0.18768 | 122.9691 | 122.9599 | 0.27466 | -0.022889 | 122.7356 | 122.7081 | 0.10528 | 122.9095 | 122.85 | 0.14191 | 0.073242 | 123.2162 | 123.0057 | 122.937 | -0.34332 | 123.1338 | 123.1018 | 122.9691 | -0.32044
3815.625 | 123.0789 | -122.8638 | 0.20599 | 0.060425 | 0.02916 | 0.0048706 | 0.0089635 | -0.0083974 | -0.005048 | -0.0082245 | 0.04097 | -0.014477 | -0.003262 | -0.0021896 | 0.0011173 | -0.017212 | 0.1236 | 0.1236 | 0.082397 | 0.073242 | 0.27466 | -0.013733 | -0.16937 | 0.12817 | 0.15564 | 0.073242 | 0.22888 | 0.20142 | -0.09613 | -0.14191 | 122.85 | 122.6944 | 0.068664 | 122.9874 | 122.937 | 0.24261 | -0.082398 | 122.7676 | 122.7219 | 0.022888 | 122.9919 | 122.937 | 0.21515 | -0.004578 | 123.1384 | 122.9874 | 122.9462 | -0.37537 | 123.0927 | 123.0652 | 123.0194 | -0.3479
3817.3906 | 123.0789 | -122.8592 | 0.22888 | 0.037537 | 0.029587 | 0.0087158 | 0.0055457 | -0.010534 | -0.0039798 | -0.0082245 | 0.094375 | -0.016186 | -0.0071072 | -0.0011216 | 0.0056033 | -0.013153 | 0.09613 | 0.11902 | 0.086975 | 0.091553 | 0.28839 | -0.018311 | -0.16479 | 0.10529 | 0.15106 | 0.059509 | 0.21973 | 0.19684 | -0.086975 | -0.1236 | 122.8409 | 122.6944 | 0.059509 | 122.9782 | 122.9507 | 0.25635 | -0.13275 | 122.7722 | 122.7356 | -0.009155 | 122.9645 | 122.9187 | 0.1831 | -0.032044 | 123.1476 | 122.9553 | 122.9462 | -0.39368 | 123.0789 | 123.056 | 123.0103 | -0.35248
3819.1562 | 123.1155 | -122.8271 | 0.1831 | 0.13672 | 0.031296 | 0.0059388 | 0.0040503 | -0.008611 | 0.00050622 | -0.0075837 | 0.086746 | -0.012555 | -0.006039 | -0.001976 | 0.0094485 | -0.019134 | 0.10071 | 0.091553 | 0.050354 | 0.082397 | 0.21973 | -0.064087 | -0.22888 | 0.11444 | 0.14191 | 0.018311 | 0.16022 | 0.10529 | -0.11444 | -0.1831 | 122.7631 | 122.5983 | 0.036622 | 122.9187 | 122.9095 | 0.31128 | -0.082397 | 122.7127 | 122.644 | -0.022888 | 122.9416 | 122.8455 | 0.20142 | -0.077819 | 123.0469 | 122.9279 | 122.8775 | -0.41199 | 122.9874 | 122.9324 | 122.9691 | -0.36621
3820.8594 | 123.1247 | -122.8409 | 0.19226 | 0.19775 | 0.031937 | 0.0050842 | 0.0044775 | -0.010747 | 0.0022152 | -0.0075837 | 0.102 | -0.012341 | -0.0079618 | -5.3406e-05 | 0.0068851 | -0.017212 | 0.091553 | 0.068665 | 0.004578 | 0.036621 | 0.22888 | -0.073242 | -0.2243 | 0.11444 | 0.13275 | 0.009155 | 0.14648 | 0.16022 | -0.14191 | -0.17853 | 122.7676 | 122.6166 | 0.036621 | 122.9095 | 122.8775 | 0.26093 | -0.10071 | 122.699 | 122.6624 | -0.045777 | 122.9553 | 122.85 | 0.18768 | -0.032044 | 123.0698 | 122.9324 | 122.8455 | -0.41656 | 122.9874 | 123.0011 | 122.9736 | -0.37079
3822.6094 | 123.0789 | -122.8821 | 0.21973 | 0.14435 | 0.030655 | 0.006366 | 0.0057593 | -0.0077566 | -0.0020572 | -0.0069427 | 0.11726 | -0.01405 | -0.0058254 | -0.0028306 | 0.0047489 | -0.016357 | 0.082397 | 0.14648 | 0.073242 | 0.068665 | 0.2243 | -0.050354 | -0.20599 | 0.13733 | 0.15106 | 0.036621 | 0.16479 | 0.13275 | -0.1236 | -0.18768 | 122.8317 | 122.6761 | 0.004577 | 123.0286 | 122.9507 | 0.27466 | -0.13733 | 122.7585 | 122.6944 | -0.054932 | 123.0194 | 122.9187 | 0.2243 | -0.086976 | 123.1064 | 122.9645 | 122.9553 | -0.42572 | 123.0469 | 123.0148 | 123.0331 | -0.40741
3824.375 | 123.0972 | -122.8821 | 0.19226 | 0.014648 | 0.031509 | 0.008075 | 0.0098181 | -0.0094656 | -0.0035526 | -0.0077973 | 0.03334 | -0.012555 | -0.004971 | -0.001976 | 0.0021853 | -0.015503 | 0.10529 | 0.12817 | 0.10986 | 0.091553 | 0.3067 | -0.009155 | -0.15564 | 0.11444 | 0.16937 | 0.082397 | 0.24261 | 0.21057 | -0.10071 | -0.13733 | 122.8729 | 122.7264 | 0.11444 | 123.0103 | 122.9736 | 0.24719 | -0.086975 | 122.7814 | 122.7448 | 0.050354 | 122.9965 | 122.9645 | 0.21973 | 0.01831 | 123.1888 | 122.9874 | 122.9919 | -0.3479 | 123.1247 | 123.0927 | 123.0515 | -0.32959
3826.1406 | 123.1934 | -122.8043 | 0.16937 | -0.031128 | 0.029373 | 0.0078614 | 0.0066137 | -0.01032 | -0.0037662 | -0.010788 | -0.027695 | -0.015332 | -0.0081754 | -0.0056076 | 0.0023989 | -0.014435 | 0.13275 | 0.15564 | 0.12817 | 0.12817 | 0.32959 | 0 | -0.12817 | 0.16022 | 0.20599 | 0.11444 | 0.23804 | 0.21973 | -0.07782 | -0.11902 | 122.8043 | 122.6761 | 0.16022 | 122.9599 | 122.9324 | 0.25635 | -0.036622 | 122.7264 | 122.6852 | 0.068664 | 122.9645 | 122.9187 | 0.23346 | 0.050354 | 123.1338 | 122.937 | 122.9324 | -0.29755 | 123.0423 | 123.024 | 123.0103 | -0.28839
3827.9219 | 123.1155 | -122.8638 | 0.21057 | 0.022278 | 0.030441 | 0.0052978 | 0.0046911 | -0.01032 | -0.0035526 | -0.0099335 | 0.04097 | -0.012768 | -0.0071072 | -0.0024032 | 0.0028263 | -0.013794 | 0.10986 | 0.1236 | 0.09613 | 0.09613 | 0.32044 | 0.004578 | -0.14648 | 0.12817 | 0.16937 | 0.086975 | 0.23346 | 0.20142 | -0.073242 | -0.13733 | 122.8683 | 122.7173 | 0.10986 | 122.9874 | 122.9599 | 0.24261 | -0.10071 | 122.7905 | 122.7264 | 0.022888 | 122.9919 | 122.9507 | 0.2243 | -0.009155 | 123.1842 | 122.9736 | 122.9599 | -0.35706 | 123.0972 | 123.0652 | 123.0331 | -0.3479
3829.625 | 123.0606 | -122.8638 | 0.21973 | 0.060425 | 0.031509 | 0.0061524 | 0.0044775 | -0.007543 | 0.0060604 | -0.0069427 | -0.050583 | -0.011273 | -0.006039 | -0.0026168 | 0.0094485 | -0.019989 | 0.082397 | -0.022888 | -0.073242 | 0.004578 | 0.27924 | -0.064087 | -0.24261 | -0.004578 | 0 | -0.13275 | 0.21515 | 0.17395 | -0.17853 | -0.22888 | 122.7997 | 122.6212 | 0.059509 | 122.8409 | 122.8683 | 0.24719 | -0.13733 | 122.6852 | 122.6349 | -0.004578 | 122.8592 | 122.731 | 0.096131 | -0.045777 | 123.143 | 122.9462 | 122.7905 | -0.46234 | 123.0789 | 123.0377 | 122.8638 | -0.44861
3831.3906 | 123.0698 | -122.8592 | 0.21515 | 0.1062 | 0.032791 | 0.0052978 | 0.0074683 | -0.0090384 | -0.0022708 | -0.0086517 | 0.18593 | -0.012555 | -0.0068936 | -0.0030442 | 0.0049625 | -0.017212 | 0.11444 | 0.13275 | 0.07782 | 0.064087 | 0.24261 | -0.050354 | -0.20142 | 0.13733 | 0.15106 | 0.054932 | 0.19226 | 0.16937 | -0.13733 | -0.15106 | 122.8088 | 122.6578 | 0.027466 | 122.9919 | 122.9233 | 0.2655 | -0.10071 | 122.7219 | 122.7081 | -0.022888 | 122.9965 | 122.9141 | 0.20599 | -0.045776 | 123.1018 | 122.9736 | 122.937 | -0.41657 | 123.0515 | 123.0286 | 123.0103 | -0.36621
3833.0938 | 123.1705 | -122.8271 | 0.17853 | -0.19897 | 0.031723 | 0.006366 | 0.0078955 | -0.0077566 | -0.0014164 | -0.0088653 | -0.2108 | -0.0117 | -0.006039 | -0.0017624 | 0.0030399 | -0.016357 | 0.16022 | 0.15106 | 0.10529 | 0.13275 | 0.40741 | 0.036621 | -0.11444 | 0.10071 | 0.15564 | 0.032043 | 0.3067 | 0.27466 | -0.07782 | -0.13733 | 122.8638 | 122.7127 | 0.22888 | 122.9782 | 122.9599 | 0.24719 | -0.018311 | 122.7493 | 122.6898 | 0.12817 | 122.9279 | 122.8592 | 0.16937 | 0.09613 | 123.2346 | 122.9874 | 122.9324 | -0.29297 | 123.1338 | 123.1018 | 122.9828 | -0.31586
3834.8594 | 123.0927 | -122.8821 | 0.20599 | 0.0070193 | 0.031723 | 0.006366 | 0.0087499 | -0.0090384 | -0.006757 | -0.0071563 | 0.071487 | -0.012341 | -0.0079618 | -0.0024032 | 0.0026125 | -0.015075 | 0.11444 | 0.13733 | 0.082397 | 0.091553 | 0.3067 | -0.004578 | -0.15106 | 0.11444 | 0.16937 | 0.082397 | 0.23346 | 0.19226 | -0.10071 | -0.12817 | 122.8775 | 122.731 | 0.10071 | 123.0194 | 122.9736 | 0.24261 | -0.091553 | 122.7814 | 122.7539 | 0.027465 | 122.9965 | 122.9645 | 0.21057 | -0.013733 | 123.1888 | 122.9965 | 122.9645 | -0.35706 | 123.1155 | 123.0743 | 123.0515 | -0.33417
3836.625 | 123.1201 | -122.8409 | 0.21973 | 0.13672 | 0.032578 | 0.0052978 | 0.0023413 | -0.0077566 | 0.00071982 | -0.0069427 | 0.094375 | -0.012555 | -0.0073208 | -0.00069421 | 0.010303 | -0.016571 | 0.10071 | 0.10529 | 0.036621 | 0.059509 | 0.23804 | -0.050354 | -0.2243 | 0.11902 | 0.13275 | 0.004578 | 0.16479 | 0.1236 | -0.14191 | -0.19684 | 122.7905 | 122.6166 | 0.01831 | 122.9462 | 122.9004 | 0.28381 | -0.11902 | 122.699 | 122.644 | -0.054932 | 122.9599 | 122.8455 | 0.20142 | -0.096131 | 123.0789 | 122.9416 | 122.8775 | -0.44403 | 123.0057 | 122.9645 | 122.9736 | -0.41657
3838.375 | 123.111 | -122.8455 | 0.20599 | 0.14435 | 0.031296 | 0.006366 | 0.0044775 | -0.010106 | -0.00077538 | -0.0063019 | 0.15541 | -0.011059 | -0.0092434 | -0.0026168 | 0.0062441 | -0.017212 | 0.086975 | 0.13275 | 0.054932 | 0.054932 | 0.22888 | -0.045776 | -0.21057 | 0.11444 | 0.12817 | 0.022888 | 0.14191 | 0.091553 | -0.16022 | -0.21515 | 122.7997 | 122.6349 | 0.022888 | 122.9782 | 122.9004 | 0.2655 | -0.11902 | 122.6852 | 122.6303 | -0.064087 | 122.9599 | 122.8683 | 0.23804 | -0.11444 | 123.0743 | 122.9324 | 122.9004 | -0.41657 | 122.9874 | 122.937 | 122.9736 | -0.42114
3840.125 | 123.0789 | -122.8683 | 0.2243 | 0.037537 | 0.034073 | 0.0057252 | 0.0057593 | -0.0079702 | 0.0071286 | -0.0065155 | -0.042954 | -0.010846 | -0.003262 | -5.3406e-05 | 0.0073123 | -0.016143 | 0.032043 | 0.004578 | -0.059509 | 0.013733 | 0.28839 | -0.068665 | -0.24261 | -0.004578 | 0 | -0.13275 | 0.20599 | 0.16937 | -0.17853 | -0.23346 | 122.7997 | 122.6257 | 0.064087 | 122.8729 | 122.8821 | 0.25635 | -0.19226 | 122.6898 | 122.6349 | -0.01831 | 122.8638 | 122.7356 | 0.10071 | -0.054931 | 123.1567 | 122.9004 | 122.8088 | -0.46692 | 123.0743 | 123.0377 | 122.8683 | -0.45776
3841.8438 | 123.1979 | -122.8271 | 0.1831 | -0.031128 | 0.031296 | 0.0061524 | 0.010673 | -0.0090384 | -0.0056888 | -0.0080109 | -0.13451 | -0.011273 | -0.0068936 | -0.0013352 | 0.00047633 | -0.014862 | 0.20599 | 0.28381 | 0.21973 | 0.19226 | 0.32959 | 0.054932 | -0.10071 | 0.19684 | 0.28839 | 0.17395 | 0.25635 | 0.23804 | -0.059509 | -0.091553 | 122.8821 | 122.7264 | 0.14649 | 123.111 | 123.0194 | 0.29297 | 0.022889 | 122.7676 | 122.7356 | 0.073243 | 123.024 | 123.0011 | 0.2655 | 0.054932 | 123.1567 | 123.0331 | 123.0469 | -0.28381 | 123.0835 | 123.0652 | 123.1155 | -0.27466
3843.6094 | 123.1888 | -122.8226 | 0.16479 | -0.038757 | 0.031296 | 0.007434 | 0.010032 | -0.0098928 | -0.0029118 | -0.0090791 | -0.035324 | -0.013623 | -0.0051846 | -0.0021896 | 0.0017581 | -0.015075 | 0.12817 | 0.1831 | 0.14648 | 0.12817 | 0.32044 | 0.018311 | -0.11444 | 0.17853 | 0.24261 | 0.14648 | 0.24261 | 0.21515 | -0.045776 | -0.11902 | 122.8409 | 122.7081 | 0.15564 | 123.0057 | 122.9507 | 0.24262 | -0.036621 | 122.7768 | 122.7036 | 0.07782 | 123.0011 | 122.9691 | 0.2655 | 0.050354 | 123.143 | 122.9507 | 122.9691 | -0.27924 | 123.0652 | 123.0377 | 123.0652 | -0.28381
3845.375 | 123.0835 | -122.8592 | 0.2243 | 0.075684 | 0.0345 | 0.0065796 | 0.0068273 | -0.01032 | 0.0037106 | -0.0073701 | 0.010452 | -0.011487 | -0.0058254 | -0.0013352 | 0.010089 | -0.018493 | 0.022888 | -0.027466 | -0.082397 | -0.013733 | 0.29755 | -0.086975 | -0.25177 | 0 | 0.004578 | -0.11902 | 0.21515 | 0.15106 | -0.16937 | -0.2243 | 122.7722 | 122.6074 | 0.073242 | 122.8317 | 122.8455 | 0.23804 | -0.20142 | 122.6898 | 122.6349 | -0.009155 | 122.8592 | 122.7402 | 0.10529 | -0.073242 | 123.1567 | 122.8821 | 122.7768 | -0.47607 | 123.0743 | 123.0103 | 122.8638 | -0.44861
3847.125 | 123.0927 | -122.8638 | 0.21057 | -0.076904 | 0.033859 | 0.0050842 | 0.0061865 | -0.0096792 | 0.0039242 | -0.0067291 | -0.073471 | -0.0097775 | -0.0051846 | -0.0021896 | 0.0073123 | -0.016784 | 0.11902 | 0.10529 | 0.022888 | 0.050354 | 0.30212 | -0.022888 | -0.21057 | 0.059509 | 0.07782 | -0.068665 | 0.20142 | 0.20142 | -0.15106 | -0.21515 | 122.8409 | 122.6532 | 0.091553 | 122.9691 | 122.9141 | 0.26093 | -0.091552 | 122.7127 | 122.6486 | -0.009155 | 122.9233 | 122.7951 | 0.14648 | -0.009155 | 123.1659 | 122.9828 | 122.8867 | -0.42114 | 123.0652 | 123.0652 | 122.9416 | -0.42572
3848.8281 | 123.111 | -122.8592 | 0.18768 | 0.037537 | 0.028732 | 0.0055114 | 0.0087499 | -0.010534 | -0.0054752 | -0.0082245 | 0.094375 | -0.014691 | -0.0051846 | -0.00048061 | 0.00090353 | -0.014862 | 0.082397 | 0.13733 | 0.10986 | 0.10986 | 0.33417 | 0.004578 | -0.16022 | 0.10529 | 0.18768 | 0.07782 | 0.2243 | 0.21057 | -0.10529 | -0.1236 | 122.8638 | 122.699 | 0.14648 | 122.9965 | 122.9691 | 0.27008 | -0.10529 | 122.7539 | 122.7356 | 0.036621 | 122.9645 | 122.937 | 0.20142 | 0.022888 | 123.1934 | 122.9416 | 122.9691 | -0.3479 | 123.0835 | 123.0698 | 123.0469 | -0.31128
3850.5938 | 123.0789 | -122.8821 | 0.21057 | 0.11383 | 0.030441 | 0.0055114 | 0.0064001 | -0.0094656 | -0.003339 | -0.0077973 | 0.13252 | -0.0117 | -0.0071072 | -0.0030442 | 0.0038943 | -0.013794 | 0.082397 | 0.11444 | 0.068665 | 0.050354 | 0.23804 | -0.045776 | -0.19226 | 0.11444 | 0.15106 | 0.054932 | 0.20142 | 0.16479 | -0.11444 | -0.14191 | 122.8363 | 122.6898 | 0.027466 | 122.9965 | 122.9324 | 0.24261 | -0.12817 | 122.7676 | 122.7402 | -0.009155 | 122.9965 | 122.937 | 0.19684 | -0.045776 | 123.1201 | 122.9645 | 122.9507 | -0.40283 | 123.0835 | 123.0469 | 123.0331 | -0.35248
3852.3594 | 123.1796 | -122.8134 | 0.19226 | -0.11505 | 0.028519 | 0.0050842 | 0.0089635 | -0.011388 | -0.0037662 | -0.0086517 | -0.14214 | -0.015118 | -0.0075344 | -5.3406e-05 | 0.00068993 | -0.014648 | 0.24719 | 0.29297 | 0.19226 | 0.20599 | 0.36163 | 0.050354 | -0.10986 | 0.21515 | 0.29755 | 0.16022 | 0.25177 | 0.22888 | -0.032043 | -0.082397 | 122.8638 | 122.7036 | 0.16937 | 123.1064 | 123.0194 | 0.31586 | 0.054931 | 122.7814 | 122.731 | 0.059509 | 123.0286 | 122.9736 | 0.24261 | 0.036621 | 123.175 | 123.0606 | 123.0057 | -0.30212 | 123.0652 | 123.0423 | 123.111 | -0.27466
3854.125 | 123.0743 | -122.9004 | 0.20599 | -0.00061023 | 0.035568 | 0.0052978 | 0.0061865 | -0.0062612 | 0.0028562 | -0.0045929 | -0.0048066 | -0.011487 | -0.007748 | -0.00048061 | 0.0081667 | -0.019134 | 0.068665 | 0.004578 | -0.059509 | 0.009155 | 0.28839 | -0.086975 | -0.24719 | 0.018311 | 0.032043 | -0.13275 | 0.21515 | 0.18768 | -0.1831 | -0.22888 | 122.8134 | 122.6532 | 0.082397 | 122.905 | 122.9095 | 0.25635 | -0.13733 | 122.7173 | 122.6715 | 0.009155 | 122.9187 | 122.7676 | 0.096131 | -0.018311 | 123.1888 | 122.9691 | 122.8409 | -0.45319 | 123.1155 | 123.0881 | 122.9324 | -0.43488
3855.8281 | 123.1888 | -122.8271 | 0.21057 | -0.16083 | 0.0298 | 0.0040162 | 0.0087499 | -0.0062612 | -0.005048 | -0.0086517 | -0.073471 | -0.013623 | -0.0058254 | -0.0034714 | 0.00026273 | -0.015503 | 0.19226 | 0.27008 | 0.19684 | 0.20142 | 0.36621 | 0.050354 | -0.10986 | 0.21515 | 0.28839 | 0.17853 | 0.25635 | 0.21515 | -0.041199 | -0.082397 | 122.8775 | 122.7173 | 0.15564 | 123.0972 | 123.0286 | 0.31128 | -0.01831 | 122.7859 | 122.7448 | 0.045777 | 123.0423 | 123.0057 | 0.26092 | 0.004578 | 123.1934 | 123.0194 | 123.024 | -0.32043 | 123.0835 | 123.0423 | 123.1155 | -0.29297
3857.5938 | 123.1155 | -122.8317 | 0.20599 | 0.15198 | 0.030869 | 0.0042298 | 0.0049047 | -0.0066884 | 0.0015744 | -0.0067291 | 0.14778 | -0.011487 | -0.001553 | 0.00037379 | 0.0058169 | -0.017852 | 0.054932 | 0.004578 | -0.045776 | -0.013733 | 0.26093 | -0.10529 | -0.24261 | 0.073242 | 0.064087 | -0.045776 | 0.19226 | 0.14191 | -0.16022 | -0.21973 | 122.7264 | 122.5891 | 0.054931 | 122.8363 | 122.818 | 0.22888 | -0.15106 | 122.6715 | 122.612 | -0.013733 | 122.905 | 122.7859 | 0.17395 | -0.064087 | 123.0927 | 122.8867 | 122.7859 | -0.44861 | 123.024 | 122.9736 | 122.8958 | -0.42572
3859.3438 | 123.1293 | -122.8546 | 0.21057 | 0.19775 | 0.033005 | 0.0059388 | 0.0046911 | -0.0090384 | -0.0012028 | -0.0067291 | 0.14778 | -0.0099911 | -0.0081754 | -0.00026701 | 0.0094485 | -0.015716 | 0.068665 | 0.082397 | 0.009155 | 0.045776 | 0.21973 | -0.068665 | -0.23346 | 0.11902 | 0.15564 | 0.018311 | 0.16022 | 0.12817 | -0.13733 | -0.19226 | 122.7859 | 122.6212 | 0.009156 | 122.937 | 122.9004 | 0.27924 | -0.14191 | 122.7173 | 122.6624 | -0.050354 | 122.9736 | 122.8729 | 0.21057 | -0.082397 | 123.0743 | 122.9233 | 122.8638 | -0.44403 | 123.0148 | 122.9828 | 123.0103 | -0.40283
3861.1094 | 123.1155 | -122.8455 | 0.19684 | 0.11383 | 0.032364 | 0.0044434 | 0.0078955 | -0.0081838 | 0.0024288 | -0.0058747 | 0.063858 | -0.013196 | -0.009457 | -0.0017624 | 0.0070987 | -0.01593 | 0.013733 | 0.013733 | -0.054932 | -0.018311 | 0.27924 | -0.086975 | -0.24261 | 0.032043 | 0.022888 | -0.07782 | 0.19226 | 0.15106 | -0.1831 | -0.20142 | 122.7585 | 122.6028 | 0.082398 | 122.8592 | 122.8271 | 0.2243 | -0.18311 | 122.6624 | 122.644 | -0.004577 | 122.8775 | 122.7676 | 0.1236 | -0.045776 | 123.1247 | 122.8592 | 122.7905 | -0.43945 | 123.0377 | 122.9965 | 122.8683 | -0.39825
3862.875 | 123.0835 | -122.8317 | 0.21515 | 0.060425 | 0.0298 | 0.006366 | 0.0087499 | -0.0081838 | -0.006116 | -0.0095063 | 0.048599 | -0.015759 | -0.007748 | -0.0024032 | 0.0011173 | -0.013366 | 0.082397 | 0.12817 | 0.091553 | 0.091553 | 0.30212 | 0 | -0.17853 | 0.11444 | 0.16022 | 0.07782 | 0.23346 | 0.20599 | -0.086975 | -0.14648 | 122.8317 | 122.6532 | 0.086975 | 122.9599 | 122.9233 | 0.27008 | -0.13275 | 122.7448 | 122.6852 | 0.01831 | 122.9462 | 122.9095 | 0.2243 | -0.009155 | 123.1339 | 122.9141 | 122.9233 | -0.39368 | 123.0652 | 123.0377 | 122.9919 | -0.36163
3864.5781 | 123.2025 | -122.7951 | 0.1831 | -0.19135 | 0.034287 | 0.0052978 | 0.0053321 | -0.010106 | 0.0020016 | -0.0071563 | -0.14977 | -0.0095639 | -0.0056118 | -0.0024032 | 0.0068851 | -0.017639 | 0.14191 | 0.11444 | 0.041199 | 0.10071 | 0.33875 | -0.013733 | -0.19226 | 0.086975 | 0.11902 | -0.022888 | 0.24261 | 0.20599 | -0.13733 | -0.19226 | 122.7814 | 122.6028 | 0.15564 | 122.9095 | 122.8958 | 0.29297 | -0.041198 | 122.6578 | 122.6028 | 0.05951 | 122.8821 | 122.7722 | 0.16937 | 0.022889 | 123.1339 | 122.937 | 122.8363 | -0.37537 | 123.0377 | 123.0011 | 122.9141 | -0.37537
3866.3281 | 123.0789 | -122.8821 | 0.21057 | -0.054016 | 0.032791 | 0.0070068 | 0.0049047 | -0.0098928 | 0.0024288 | -0.0054475 | -0.027695 | -0.010846 | -0.0068936 | -0.001976 | 0.0062441 | -0.016143 | 0.10071 | 0.082397 | 0 | 0.054932 | 0.29755 | -0.059509 | -0.21973 | 0.036621 | 0.045776 | -0.10071 | 0.21973 | 0.17395 | -0.17395 | -0.22888 | 122.8226 | 122.6624 | 0.086975 | 122.9645 | 122.937 | 0.27466 | -0.10986 | 122.7081 | 122.6532 | 0.009156 | 122.9187 | 122.7814 | 0.12817 | -0.036621 | 123.1796 | 122.9828 | 122.8821 | -0.4303 | 123.1018 | 123.056 | 122.9279 | -0.43945
3868.0938 | 123.1934 | -122.8638 | 0.18768 | -0.23712 | 0.032791 | 0.0078614 | 0.010459 | -0.0079702 | -0.0018436 | -0.0088653 | -0.25658 | -0.012127 | -0.0064664 | -0.0021896 | 0.0021853 | -0.015075 | 0.10529 | 0.14191 | 0.073242 | 0.12817 | 0.42572 | 0.027466 | -0.13275 | 0.091553 | 0.15564 | 0.013733 | 0.31586 | 0.27466 | -0.07782 | -0.13733 | 122.8912 | 122.731 | 0.23804 | 123.0057 | 122.9919 | 0.26093 | -0.082397 | 122.7859 | 122.7264 | 0.12817 | 122.9553 | 122.8775 | 0.15106 | 0.086975 | 123.2895 | 122.9691 | 122.937 | -0.32043 | 123.1796 | 123.1384 | 123.0194 | -0.32501
3869.7812 | 123.0927 | -122.8821 | 0.20142 | 0.075684 | 0.027023 | 0.0085022 | 0.0068273 | -0.010961 | -0.0059024 | -0.0088653 | 0.079117 | -0.014264 | -0.004971 | -0.0024032 | 0.0019717 | -0.014007 | 0.073242 | 0.12817 | 0.091553 | 0.07782 | 0.29297 | 0.009155 | -0.16022 | 0.11444 | 0.15106 | 0.073242 | 0.22888 | 0.17853 | -0.09613 | -0.16479 | 122.8912 | 122.7219 | 0.091553 | 123.0103 | 122.9599 | 0.23804 | -0.12817 | 122.7859 | 122.7173 | 0.027466 | 122.9965 | 122.9553 | 0.23804 | -0.022888 | 123.175 | 122.9553 | 122.9736 | -0.36163 | 123.111 | 123.0606 | 123.0331 | -0.36621
3871.5625 | 123.1979 | -122.818 | 0.16022 | -0.12268 | 0.032578 | 0.006366 | 0.0076819 | -0.0088248 | -0.0046206 | -0.01207 | -0.065842 | -0.014905 | -0.0053982 | -0.0038986 | 0.0011173 | -0.015503 | 0.20599 | 0.23804 | 0.1831 | 0.17853 | 0.37079 | 0.041199 | -0.12817 | 0.21057 | 0.27924 | 0.17395 | 0.2655 | 0.22888 | -0.064087 | -0.10071 | 122.8592 | 122.6898 | 0.21057 | 123.056 | 122.9965 | 0.3067 | 0.045777 | 122.7539 | 122.7173 | 0.10529 | 123.0286 | 122.9919 | 0.27466 | 0.068665 | 123.1888 | 123.024 | 123.0011 | -0.28839 | 123.0835 | 123.0469 | 123.0972 | -0.26093
3873.2812 | 123.1659 | -122.8363 | 0.17395 | -0.17609 | 0.030655 | 0.0048706 | 0.0111 | -0.011175 | -0.002698 | -0.010574 | -0.25658 | -0.011487 | -0.0079618 | -0.0043258 | 0.0043215 | -0.017639 | 0.20599 | 0.2243 | 0.17853 | 0.17853 | 0.33875 | 0.064087 | -0.10986 | 0.15564 | 0.23346 | 0.091553 | 0.27924 | 0.26093 | -0.050354 | -0.11444 | 122.9004 | 122.7264 | 0.1648 | 123.0606 | 123.0148 | 0.28839 | 0.032044 | 122.7859 | 122.7219 | 0.10529 | 122.9919 | 122.9279 | 0.20599 | 0.086975 | 123.175 | 123.0423 | 123.0148 | -0.28381 | 123.1155 | 123.0972 | 123.0698 | -0.28839
3875.0469 | 123.1979 | -122.818 | 0.17853 | -0.12268 | 0.029373 | 0.0070068 | 0.0096045 | -0.010747 | -0.0048344 | -0.0095063 | -0.08873 | -0.015759 | -0.0064664 | -0.0034714 | 0.0032535 | -0.015075 | 0.23804 | 0.27008 | 0.21515 | 0.20142 | 0.3479 | 0.064087 | -0.10071 | 0.23346 | 0.29755 | 0.15106 | 0.25635 | 0.20599 | -0.059509 | -0.09613 | 122.8821 | 122.7173 | 0.16937 | 123.0881 | 123.0194 | 0.30212 | 0.059509 | 122.7585 | 122.7219 | 0.07782 | 123.0515 | 122.9691 | 0.24719 | 0.027466 | 123.1659 | 123.056 | 123.0331 | -0.27924 | 123.0743 | 123.024 | 123.1155 | -0.27466
3876.7656 | 123.2025 | -122.8226 | 0.17395 | -0.14557 | 0.030228 | 0.0078614 | 0.0076819 | -0.007543 | -0.004407 | -0.0073701 | -0.11925 | -0.013623 | -0.0068936 | -0.0038986 | 0.0026125 | -0.016784 | 0.21515 | 0.27924 | 0.21057 | 0.20142 | 0.33875 | 0.050354 | -0.12817 | 0.21515 | 0.27466 | 0.16022 | 0.27466 | 0.22888 | -0.041199 | -0.10529 | 122.8729 | 122.6944 | 0.1648 | 123.1018 | 123.024 | 0.32959 | 0.041199 | 122.7814 | 122.7173 | 0.10071 | 123.0377 | 122.9828 | 0.2655 | 0.054932 | 123.1613 | 123.0377 | 123.0331 | -0.30212 | 123.0972 | 123.0515 | 123.0972 | -0.27924
3878.5312 | 123.175 | -122.8271 | 0.18768 | -0.14557 | 0.028732 | 0.0052978 | 0.0098181 | -0.0096792 | -0.0048344 | -0.0095063 | -0.14214 | -0.012555 | -0.004971 | -0.0043258 | 0.0026125 | -0.018066 | 0.24261 | 0.27466 | 0.21057 | 0.1831 | 0.32959 | 0.041199 | -0.1236 | 0.21973 | 0.27924 | 0.16022 | 0.26093 | 0.21973 | -0.045776 | -0.10071 | 122.8683 | 122.7036 | 0.14191 | 123.1018 | 123.0103 | 0.3067 | 0.054932 | 122.7814 | 122.7264 | 0.073242 | 123.0469 | 122.9874 | 0.26093 | 0.032044 | 123.1567 | 123.0698 | 123.0377 | -0.31128 | 123.0881 | 123.0469 | 123.1064 | -0.28839
3880.2969 | 123.1567 | -122.8638 | 0.19226 | -0.21423 | 0.030228 | 0.0057252 | 0.0066137 | -0.0081838 | -0.00056178 | -0.0080109 | -0.22606 | -0.011914 | -0.0053982 | -0.0021896 | 0.0038943 | -0.017425 | 0.22888 | 0.22888 | 0.15564 | 0.18768 | 0.36621 | 0.059509 | -0.11444 | 0.15564 | 0.21057 | 0.073242 | 0.29755 | 0.25177 | -0.045776 | -0.11444 | 122.9233 | 122.7493 | 0.17395 | 123.0927 | 123.0515 | 0.30212 | 0.036621 | 122.818 | 122.7493 | 0.10528 | 123.0194 | 122.937 | 0.18768 | 0.059509 | 123.23 | 123.0927 | 123.0194 | -0.3067 | 123.1613 | 123.1155 | 123.0743 | -0.3067
3882.0625 | 123.1018 | -122.8546 | 0.19684 | -0.076904 | 0.032791 | 0.0042298 | 0.0066137 | -0.0083974 | 0.006915 | -0.0060883 | -0.17265 | -0.0097775 | -0.0071072 | 0.0010148 | 0.0090213 | -0.019989 | 0.16022 | 0.11444 | 0.022888 | 0.091553 | 0.32501 | -0.032043 | -0.21515 | 0.091553 | 0.091553 | -0.050354 | 0.23346 | 0.17853 | -0.12817 | -0.19684 | 122.8226 | 122.6395 | 0.12817 | 122.9691 | 122.9462 | 0.3067 | -0.036621 | 122.7264 | 122.6578 | 0.036621 | 122.9462 | 122.8043 | 0.14648 | -0.01831 | 123.1796 | 123.0148 | 122.8775 | -0.41199 | 123.0881 | 123.0331 | 122.9462 | -0.39368
3883.7656 | 123.1613 | -122.8683 | 0.16937 | -0.22949 | 0.033859 | 0.0067932 | 0.0074683 | -0.0073294 | -0.0024844 | -0.0080109 | -0.22606 | -0.012555 | -0.0051846 | -0.001976 | 0.0032535 | -0.017852 | 0.15106 | 0.18768 | 0.10071 | 0.14191 | 0.39825 | 0.041199 | -0.10529 | 0.10071 | 0.15564 | 0.022888 | 0.31128 | 0.27466 | -0.091553 | -0.12817 | 122.9095 | 122.7631 | 0.22888 | 123.056 | 123.0103 | 0.24719 | -0.018311 | 122.7768 | 122.7402 | 0.14191 | 122.9691 | 122.8912 | 0.15106 | 0.10529 | 123.2666 | 123.0194 | 122.9691 | -0.27466 | 123.1796 | 123.143 | 123.024 | -0.29755
3885.5312 | 123.1476 | -122.8317 | 0.18768 | -0.17609 | 0.030228 | 0.0067932 | 0.0085363 | -0.0062612 | -0.002698 | -0.0063019 | -0.18791 | -0.017041 | -0.0058254 | -0.0034714 | 0.0045351 | -0.01593 | 0.19684 | 0.27008 | 0.1831 | 0.1831 | 0.35248 | 0.045776 | -0.10071 | 0.1831 | 0.28381 | 0.10529 | 0.2655 | 0.24719 | -0.064087 | -0.10986 | 122.8775 | 122.731 | 0.1648 | 123.1018 | 123.0148 | 0.28381 | 0.009155 | 122.7676 | 122.7219 | 0.07782 | 123.0148 | 122.937 | 0.21515 | 0.059509 | 123.1842 | 123.0286 | 123.0148 | -0.28839 | 123.0972 | 123.0789 | 123.1155 | -0.29755
3887.3125 | 123.0927 | -122.8546 | 0.1831 | 0.090942 | 0.033005 | 0.0052978 | 0.0042639 | -0.0073294 | 0.0020016 | -0.0067291 | 0.17067 | -0.012768 | -0.0071072 | -0.0034714 | 0.0066715 | -0.016143 | 0.10529 | 0.1236 | 0.050354 | 0.073242 | 0.22888 | -0.050354 | -0.2243 | 0.09613 | 0.1236 | 0.013733 | 0.13275 | 0.091553 | -0.15564 | -0.19684 | 122.8043 | 122.6303 | 0.045777 | 122.9782 | 122.9279 | 0.29755 | -0.077819 | 122.699 | 122.6578 | -0.050354 | 122.9507 | 122.8683 | 0.21057 | -0.091552 | 123.0835 | 122.9599 | 122.905 | -0.40741 | 122.9874 | 122.9462 | 122.9782 | -0.37994
3889.0781 | 123.1247 | -122.8455 | 0.20142 | 0.14435 | 0.032364 | 0.0061524 | 0.0040503 | -0.0098928 | 0.0011472 | -0.0058747 | 0.14015 | -0.0117 | -0.0041164 | -0.0043258 | 0.0070987 | -0.016571 | 0.032043 | 0.027466 | -0.041199 | 0 | 0.2655 | -0.091553 | -0.26093 | 0.068665 | 0.068665 | -0.013733 | 0.15564 | 0.14191 | -0.15106 | -0.21515 | 122.7539 | 122.5845 | 0.064087 | 122.8729 | 122.8455 | 0.26093 | -0.16937 | 122.6944 | 122.6303 | -0.045776 | 122.9141 | 122.8317 | 0.20142 | -0.059509 | 123.111 | 122.8775 | 122.8043 | -0.46234 | 123.0011 | 122.9874 | 122.9141 | -0.41657
3890.7812 | 123.1659 | -122.8271 | 0.1831 | -0.0082397 | 0.031082 | 0.0052978 | 0.0096045 | -0.010106 | -0.0056888 | -0.0075837 | 0.048599 | -0.012341 | -0.0058254 | -0.0026168 | 0.0023989 | -0.016143 | 0.086975 | 0.14648 | 0.10529 | 0.10529 | 0.31586 | 0.004578 | -0.14648 | 0.1236 | 0.18768 | 0.10071 | 0.23346 | 0.20142 | -0.068665 | -0.12817 | 122.8317 | 122.6807 | 0.13275 | 122.9736 | 122.9324 | 0.25177 | -0.09613 | 122.7585 | 122.699 | 0.050354 | 122.9507 | 122.9279 | 0.22888 | 0.018311 | 123.143 | 122.9141 | 122.9324 | -0.32959 | 123.0606 | 123.0286 | 123.0148 | -0.31128
3892.5469 | 123.1247 | -122.8409 | 0.19684 | 0.16724 | 0.030441 | 0.0076478 | 0.0044775 | -0.0096792 | -0.0014164 | -0.0069427 | 0.102 | -0.012555 | -0.0096706 | -0.0041122 | 0.0075259 | -0.016571 | 0.09613 | 0.10071 | 0.032043 | 0.050354 | 0.24719 | -0.059509 | -0.2243 | 0.11902 | 0.1236 | 0.022888 | 0.15106 | 0.13275 | -0.14191 | -0.19226 | 122.7814 | 122.6166 | 0.050354 | 122.9416 | 122.8912 | 0.27466 | -0.10071 | 122.699 | 122.6486 | -0.045776 | 122.9599 | 122.8638 | 0.21515 | -0.064087 | 123.0881 | 122.937 | 122.8729 | -0.42114 | 122.9919 | 122.9736 | 122.9645 | -0.3891
3894.25 | 123.1842 | -122.8271 | 0.18768 | -0.10742 | 0.0345 | 0.0044434 | 0.0076819 | -0.0069022 | 0.004565 | -0.0082245 | -0.14977 | -0.0087093 | -0.0071072 | -0.0030442 | 0.0073123 | -0.01828 | 0.14191 | 0.10529 | 0.036621 | 0.082397 | 0.32044 | -0.036621 | -0.20599 | 0.091553 | 0.1236 | -0.032043 | 0.21515 | 0.1831 | -0.15564 | -0.18768 | 122.7905 | 122.6212 | 0.13275 | 122.9324 | 122.9095 | 0.28839 | -0.045776 | 122.6715 | 122.6395 | 0.027466 | 122.9187 | 122.7951 | 0.15564 | -0.004578 | 123.1476 | 122.9691 | 122.8638 | -0.39368 | 123.0423 | 123.0103 | 122.9507 | -0.37537
3896.0156 | 123.143 | -122.8455 | 0.1831 | 0.029907 | 0.028519 | 0.0087158 | 0.0061865 | -0.010106 | -0.0054752 | -0.0086517 | 0.048599 | -0.013409 | -0.0071072 | -0.0041122 | 0.0021853 | -0.013366 | 0.07782 | 0.14648 | 0.10071 | 0.10986 | 0.32044 | 0.004578 | -0.16479 | 0.10529 | 0.18768 | 0.086975 | 0.25177 | 0.21057 | -0.10986 | -0.13733 | 122.85 | 122.6807 | 0.13733 | 122.9919 | 122.9553 | 0.27466 | -0.10528 | 122.7356 | 122.7081 | 0.068665 | 122.9507 | 122.9324 | 0.2243 | 0.027466 | 123.1659 | 122.9233 | 122.9462 | -0.3479 | 123.0972 | 123.056 | 123.0331 | -0.32043
3897.7344 | 123.1201 | -122.8455 | 0.20599 | 0.17487 | 0.033859 | 0.008075 | 0.0055457 | -0.0096792 | 0.0011472 | -0.0050201 | 0.14015 | -0.012768 | -0.007748 | -0.00048061 | 0.0077395 | -0.017639 | 0.068665 | 0.073242 | 0.022888 | 0.041199 | 0.2243 | -0.07782 | -0.22888 | 0.11902 | 0.14191 | 0.032043 | 0.15564 | 0.11902 | -0.14648 | -0.19684 | 122.7676 | 122.6166 | 0.01831 | 122.9187 | 122.8867 | 0.27008 | -0.13733 | 122.699 | 122.6486 | -0.050354 | 122.9645 | 122.8775 | 0.22888 | -0.086975 | 123.0698 | 122.9141 | 122.8683 | -0.43488 | 123.0011 | 122.9645 | 122.9874 | -0.40283
3899.4844 | 123.1247 | -122.8455 | 0.18768 | 0.052795 | 0.028732 | 0.0070068 | 0.0064001 | -0.010534 | -0.0063296 | -0.0086517 | 0.063858 | -0.013836 | -0.0079618 | -0.0049668 | 0.0032535 | -0.013794 | 0.082397 | 0.14191 | 0.11444 | 0.10071 | 0.31128 | -0.004578 | -0.15564 | 0.13275 | 0.16937 | 0.086975 | 0.2243 | 0.20142 | -0.07782 | -0.14191 | 122.8409 | 122.6898 | 0.1236 | 122.9874 | 122.9462 | 0.25635 | -0.10529 | 122.7676 | 122.7036 | 0.036621 | 122.9782 | 122.9324 | 0.22888 | 0.013733 | 123.1567 | 122.9279 | 122.9599 | -0.34332 | 123.0698 | 123.0469 | 123.0148 | -0.32959
3901.25 | 123.1842 | -122.8134 | 0.1831 | -0.13794 | 0.031082 | 0.0050842 | 0.0081091 | -0.0081838 | -0.0039798 | -0.0090791 | -0.14977 | -0.015332 | -0.007748 | -0.0038986 | 0.0028263 | -0.017639 | 0.2243 | 0.28381 | 0.20599 | 0.17853 | 0.36163 | 0.041199 | -0.10986 | 0.20599 | 0.27466 | 0.15564 | 0.27924 | 0.23804 | -0.032043 | -0.091553 | 122.8546 | 122.7036 | 0.17853 | 123.0972 | 122.9919 | 0.28839 | 0.041199 | 122.7814 | 122.7219 | 0.096131 | 123.0194 | 122.9691 | 0.24719 | 0.054932 | 123.175 | 123.0377 | 123.0194 | -0.29297 | 123.0927 | 123.0515 | 123.0881 | -0.27466
3903.0312 | 123.0881 | -122.8546 | 0.21515 | 0.0070193 | 0.030655 | 0.0082886 | 0.0046911 | -0.010747 | -0.0039798 | -0.010147 | 0.10963 | -0.014905 | -0.0051846 | -0.005394 | 0.0032535 | -0.015289 | 0.086975 | 0.13275 | 0.10071 | 0.10071 | 0.29297 | 0.004578 | -0.16479 | 0.11902 | 0.16022 | 0.073242 | 0.23804 | 0.19226 | -0.086975 | -0.16022 | 122.8592 | 122.6898 | 0.07782 | 122.9874 | 122.9553 | 0.2655 | -0.12817 | 122.7676 | 122.6944 | 0.022888 | 122.9736 | 122.9279 | 0.23346 | -0.022888 | 123.1476 | 122.9416 | 122.9553 | -0.37994 | 123.0927 | 123.0469 | 123.0148 | -0.37537
3904.7344 | 123.1934 | -122.8088 | 0.19684 | -0.13794 | 0.032791 | 0.0055114 | 0.0046911 | -0.0088248 | 0.003497 | -0.0054475 | -0.24132 | -0.010418 | -0.0053982 | -0.00026701 | 0.0070987 | -0.02063 | 0.16022 | 0.10986 | 0.036621 | 0.091553 | 0.35248 | -0.018311 | -0.18768 | 0.09613 | 0.11444 | -0.027466 | 0.24719 | 0.20599 | -0.10986 | -0.16022 | 122.7905 | 122.6212 | 0.15564 | 122.9187 | 122.9004 | 0.27924 | -0.036621 | 122.699 | 122.6486 | 0.050354 | 122.905 | 122.7814 | 0.13275 | 0.009156 | 123.1613 | 122.9691 | 122.8455 | -0.38452 | 123.056 | 123.0148 | 122.9233 | -0.35706
3906.5 | 123.1842 | -122.8317 | 0.19684 | -0.25238 | 0.033859 | 0.0044434 | 0.010673 | -0.0098928 | 0.00071982 | -0.0082245 | -0.27184 | -0.011914 | -0.0053982 | -0.00026701 | 0.0019717 | -0.017639 | 0.14191 | 0.14191 | 0.082397 | 0.12817 | 0.40741 | 0.036621 | -0.14191 | 0.10071 | 0.14191 | 0.009155 | 0.31128 | 0.27008 | -0.086975 | -0.14191 | 122.8683 | 122.6898 | 0.21057 | 122.9736 | 122.9599 | 0.27008 | -0.054931 | 122.7448 | 122.6898 | 0.11444 | 122.9324 | 122.8409 | 0.15106 | 0.073243 | 123.2391 | 122.9736 | 122.9141 | -0.33875 | 123.143 | 123.1018 | 122.9736 | -0.33875
3908.2812 | 123.1247 | -122.8546 | 0.21973 | 0.15961 | 0.032791 | 0.0070068 | 0.0038367 | -0.0094656 | 0.0026424 | -0.0063019 | 0.071487 | -0.011059 | -0.0062528 | -0.0028306 | 0.0079531 | -0.016357 | 0.013733 | -0.009155 | -0.059509 | -0.009155 | 0.27924 | -0.11444 | -0.23804 | 0.027466 | 0.013733 | -0.073242 | 0.19684 | 0.17853 | -0.17853 | -0.23346 | 122.7402 | 122.6166 | 0.059509 | 122.8455 | 122.8455 | 0.22888 | -0.20599 | 122.6761 | 122.6212 | -0.022889 | 122.8821 | 122.7814 | 0.16022 | -0.041199 | 123.1338 | 122.8683 | 122.7951 | -0.45776 | 123.0515 | 123.0331 | 122.8683 | -0.45319
3910.0312 | 123.0881 | -122.8455 | 0.21057 | 0.068054 | 0.034073 | 0.0038024 | 0.0074683 | -0.0077566 | 0.00071982 | -0.0077973 | 0.063858 | -0.011914 | -0.004971 | -0.0011216 | 0.0090213 | -0.01593 | 0.018311 | -0.027466 | -0.07782 | -0.009155 | 0.28381 | -0.082397 | -0.23346 | -0.013733 | 0.004578 | -0.11902 | 0.19226 | 0.17395 | -0.1831 | -0.24261 | 122.7631 | 122.612 | 0.073242 | 122.818 | 122.8363 | 0.2243 | -0.19226 | 122.6624 | 122.6028 | -0.01831 | 122.8317 | 122.7264 | 0.1236 | -0.036621 | 123.1293 | 122.8638 | 122.7676 | -0.44403 | 123.0377 | 123.0194 | 122.85 | -0.45319
3911.7188 | 123.1522 | -122.8134 | 0.19226 | -0.17609 | 0.033432 | 0.0078614 | 0.0087499 | -0.008611 | -0.0046206 | -0.0075837 | -0.13451 | -0.013836 | -0.0053982 | -0.0034714 | 4.9132e-05 | -0.015716 | 0.16479 | 0.26093 | 0.19226 | 0.1831 | 0.36163 | 0.032043 | -0.10071 | 0.17395 | 0.27008 | 0.11902 | 0.2655 | 0.23804 | -0.050354 | -0.10529 | 122.8455 | 122.7127 | 0.16937 | 123.0743 | 122.9965 | 0.28381 | -0.027466 | 122.7631 | 122.7081 | 0.073242 | 122.9874 | 122.9324 | 0.22431 | 0.045776 | 123.175 | 122.9782 | 123.0057 | -0.29297 | 123.0789 | 123.0515 | 123.0835 | -0.29755
3913.5 | 123.2071 | -122.818 | 0.18768 | -0.16083 | 0.033432 | 0.0055114 | 0.0061865 | -0.008611 | 0.0011472 | -0.0073701 | -0.21843 | -0.010205 | -0.0081754 | -0.0013352 | 0.0077395 | -0.017212 | 0.13733 | 0.1236 | 0.041199 | 0.11902 | 0.36621 | -0.009155 | -0.1831 | 0.064087 | 0.14191 | -0.027466 | 0.25177 | 0.21973 | -0.11902 | -0.16937 | 122.8088 | 122.6349 | 0.17853 | 122.9416 | 122.937 | 0.30212 | -0.050354 | 122.699 | 122.6486 | 0.064087 | 122.8821 | 122.7905 | 0.14191 | 0.032044 | 123.1842 | 122.9553 | 122.8592 | -0.37079 | 123.0698 | 123.0377 | 122.9599 | -0.35706
3915.2031 | 123.2162 | -122.8088 | 0.16937 | -0.12268 | 0.027878 | 0.0072204 | 0.0072547 | -0.0094656 | -0.0065434 | -0.010574 | -0.073471 | -0.016186 | -0.008389 | -0.0034714 | 0.0036807 | -0.014435 | 0.19684 | 0.30212 | 0.20599 | 0.19684 | 0.3479 | 0.064087 | -0.10986 | 0.18768 | 0.27924 | 0.16937 | 0.26093 | 0.2243 | -0.050354 | -0.11444 | 122.8729 | 122.699 | 0.17853 | 123.111 | 123.0057 | 0.3067 | 0.027465 | 122.7585 | 122.6944 | 0.091552 | 122.9965 | 122.9782 | 0.28381 | 0.054931 | 123.1567 | 123.0057 | 123.0148 | -0.27924 | 123.0698 | 123.0331 | 123.0881 | -0.28381
3916.9531 | 123.1659 | -122.8363 | 0.17395 | -0.24475 | 0.031509 | 0.0052978 | 0.0091773 | -0.0079702 | -0.002698 | -0.0082245 | -0.21843 | -0.012341 | -0.0045438 | -0.0015488 | 0.0023989 | -0.019348 | 0.20599 | 0.22888 | 0.16937 | 0.19684 | 0.37994 | 0.054932 | -0.09613 | 0.13275 | 0.21973 | 0.082397 | 0.29297 | 0.25635 | -0.068665 | -0.12817 | 122.8912 | 122.7402 | 0.20599 | 123.0652 | 123.0331 | 0.29297 | 0.032044 | 122.7676 | 122.7081 | 0.11902 | 122.9691 | 122.9187 | 0.21057 | 0.082398 | 123.2162 | 123.0423 | 123.0057 | -0.27008 | 123.1293 | 123.0927 | 123.056 | -0.30212
3918.7188 | 123.0927 | -122.8729 | 0.20142 | 0.068054 | 0.028519 | 0.0070068 | 0.0055457 | -0.011602 | -0.0056888 | -0.0092927 | 0.071487 | -0.0117 | -0.006039 | -0.00026701 | 0.0023989 | -0.016143 | 0.1236 | 0.12817 | 0.091553 | 0.10529 | 0.29297 | -0.018311 | -0.1831 | 0.12817 | 0.16022 | 0.068665 | 0.23346 | 0.21515 | -0.086975 | -0.12817 | 122.8546 | 122.6898 | 0.091553 | 123.0011 | 122.9782 | 0.28839 | -0.07782 | 122.7859 | 122.7448 | 0.032043 | 123.0011 | 122.9416 | 0.19684 | 0.013733 | 123.1659 | 122.9965 | 122.9645 | -0.38452 | 123.1064 | 123.0881 | 123.0331 | -0.32959
3920.4219 | 123.0743 | -122.85 | 0.2243 | 0.14435 | 0.031082 | 0.0059388 | 0.0034093 | -0.0064748 | -0.00098918 | -0.0073701 | 0.12489 | -0.012555 | -0.0086026 | -0.0015488 | 0.0053897 | -0.016571 | 0.11444 | 0.11902 | 0.068665 | 0.073242 | 0.2243 | -0.050354 | -0.23804 | 0.13275 | 0.14648 | 0.036621 | 0.17853 | 0.14648 | -0.12817 | -0.17395 | 122.7997 | 122.612 | 0 | 122.9691 | 122.9233 | 0.31128 | -0.10986 | 122.7219 | 122.6761 | -0.045776 | 122.9828 | 122.8867 | 0.21057 | -0.07782 | 123.0743 | 122.9645 | 122.9187 | -0.46234 | 123.0286 | 122.9965 | 122.9965 | -0.39825
3922.1875 | 123.2162 | -122.8134 | 0.1831 | -0.24475 | 0.031082 | 0.0067932 | 0.010245 | -0.0077566 | -0.00013458 | -0.0092927 | -0.22606 | -0.010418 | -0.0045438 | -0.001976 | 0.0051761 | -0.018066 | 0.16022 | 0.13275 | 0.064087 | 0.11902 | 0.41657 | 0.032043 | -0.13733 | 0.09613 | 0.10986 | -0.013733 | 0.28839 | 0.26093 | -0.11444 | -0.14648 | 122.8455 | 122.6761 | 0.23346 | 122.9462 | 122.9324 | 0.25635 | -0.022888 | 122.699 | 122.6669 | 0.10529 | 122.9095 | 122.7997 | 0.13275 | 0.07782 | 123.23 | 122.9736 | 122.8775 | -0.32043 | 123.1018 | 123.0743 | 122.9233 | -0.32959
3923.8906 | 123.1201 | -122.8775 | 0.21973 | 0.12146 | 0.033859 | 0.007434 | 0.0029821 | -0.0088248 | 0.00071982 | -0.0073701 | 0.12489 | -0.012768 | -0.0064664 | -0.0013352 | 0.0090213 | -0.016143 | 0.041199 | 0.004578 | -0.064087 | -0.004578 | 0.26093 | -0.086975 | -0.26093 | 0.059509 | 0.041199 | -0.032043 | 0.1831 | 0.15564 | -0.17853 | -0.21515 | 122.7905 | 122.6166 | 0.041198 | 122.8821 | 122.8729 | 0.25635 | -0.17853 | 122.699 | 122.6624 | -0.036622 | 122.937 | 122.8455 | 0.18311 | -0.064087 | 123.1384 | 122.9187 | 122.8134 | -0.48065 | 123.0606 | 123.0331 | 122.9187 | -0.43488
3925.6562 | 123.1384 | -122.8729 | 0.20142 | 0.14435 | 0.033859 | 0.0031616 | 0.0036231 | -0.0088248 | -0.00034818 | -0.0073701 | 0.03334 | -0.0117 | -0.0056118 | -0.00090781 | 0.0081667 | -0.016357 | 0.009155 | 0 | -0.068665 | -0.009155 | 0.26093 | -0.091553 | -0.27466 | 0.045776 | 0.032043 | -0.082397 | 0.21057 | 0.16937 | -0.16937 | -0.2243 | 122.7814 | 122.5983 | 0.059509 | 122.8729 | 122.8638 | 0.2655 | -0.19226 | 122.7036 | 122.6486 | 0.009155 | 122.9187 | 122.7905 | 0.14191 | -0.032043 | 123.1338 | 122.8821 | 122.8043 | -0.47607 | 123.0835 | 123.0423 | 122.905 | -0.42572
3927.4219 | 123.2208 | -122.8455 | 0.19226 | -0.24475 | 0.032364 | 0.0065796 | 0.0089635 | -0.0073294 | -0.00098918 | -0.010361 | -0.22606 | -0.010846 | -0.006039 | -0.0034714 | 0.0043215 | -0.016143 | 0.10529 | 0.13733 | 0.07782 | 0.11902 | 0.40741 | 0.018311 | -0.15564 | 0.064087 | 0.13275 | 0 | 0.30212 | 0.26093 | -0.10071 | -0.16022 | 122.8638 | 122.6898 | 0.21515 | 122.9828 | 122.9645 | 0.27466 | -0.086975 | 122.7448 | 122.6852 | 0.10986 | 122.9095 | 122.8455 | 0.16022 | 0.068664 | 123.2529 | 122.9507 | 122.9233 | -0.3479 | 123.1476 | 123.1064 | 122.9782 | -0.35248
3929.1719 | 123.1659 | -122.8455 | 0.16937 | -0.19135 | 0.030014 | 0.0085022 | 0.0087499 | -0.010961 | -0.0039798 | -0.0080109 | -0.11925 | -0.014264 | -0.0064664 | -0.0030442 | 0.0019717 | -0.015075 | 0.21057 | 0.27924 | 0.19684 | 0.21515 | 0.35706 | 0.064087 | -0.091553 | 0.18768 | 0.27924 | 0.15106 | 0.26093 | 0.21973 | -0.050354 | -0.091553 | 122.9095 | 122.7539 | 0.18768 | 123.1247 | 123.0606 | 0.3067 | 0.041198 | 122.7951 | 122.7539 | 0.091552 | 123.0331 | 122.9965 | 0.24261 | 0.050354 | 123.2025 | 123.056 | 123.0423 | -0.26093 | 123.1064 | 123.0652 | 123.1247 | -0.26093
3930.9219 | 123.0927 | -122.8958 | 0.21515 | 0.068054 | 0.0298 | 0.0050842 | 0.0068273 | -0.009252 | -0.0041934 | -0.0084381 | 0.102 | -0.014477 | -0.0041164 | -0.0015488 | 0.0015445 | -0.015503 | 0.082397 | 0.1236 | 0.082397 | 0.086975 | 0.28839 | -0.004578 | -0.1831 | 0.11444 | 0.15564 | 0.050354 | 0.22888 | 0.19684 | -0.086975 | -0.15106 | 122.8912 | 122.7127 | 0.073242 | 123.0194 | 122.9828 | 0.27008 | -0.13275 | 122.8088 | 122.7448 | 0.013733 | 123.0103 | 122.9462 | 0.20142 | -0.018311 | 123.1842 | 122.9782 | 122.9782 | -0.39825 | 123.1247 | 123.0927 | 123.0515 | -0.36621
3932.625 | 123.0927 | -122.8683 | 0.20599 | 0.060425 | 0.031509 | 0.0050842 | 0.0057593 | -0.0090384 | 0.0039242 | -0.0073701 | 0.079117 | -0.011059 | -0.006039 | 0.00080099 | 0.0081667 | -0.019561 | 0.018311 | -0.054932 | -0.12817 | -0.050354 | 0.30212 | -0.10986 | -0.27008 | 0 | -0.013733 | -0.10529 | 0.20142 | 0.17853 | -0.18768 | -0.24261 | 122.7585 | 122.5983 | 0.09613 | 122.8134 | 122.818 | 0.21973 | -0.18768 | 122.6807 | 122.6257 | -0.004578 | 122.8683 | 122.7631 | 0.13733 | -0.027466 | 123.1705 | 122.8867 | 122.7402 | -0.47608 | 123.0698 | 123.0469 | 122.8546 | -0.44861
3934.3906 | 123.0927 | -122.85 | 0.19684 | 0.16724 | 0.032364 | 0.0044434 | 0.0061865 | -0.0090384 | -0.0012028 | -0.0054475 | 0.18593 | -0.014477 | -0.0056118 | -0.0026168 | 0.0036807 | -0.017212 | 0.07782 | 0.11902 | 0.073242 | 0.068665 | 0.19684 | -0.054932 | -0.21057 | 0.10071 | 0.13733 | 0.032043 | 0.13275 | 0.11902 | -0.17395 | -0.18768 | 122.7951 | 122.6395 | 0 | 122.9691 | 122.9187 | 0.27924 | -0.11902 | 122.6761 | 122.6624 | -0.064087 | 122.9507 | 122.8821 | 0.21973 | -0.077819 | 123.0469 | 122.9279 | 122.9233 | -0.40741 | 122.9828 | 122.9691 | 122.9874 | -0.38452
3936.1562 | 123.1338 | -122.8363 | 0.20142 | -0.00061023 | 0.030014 | 0.0050842 | 0.0072547 | -0.0088248 | -0.0056888 | -0.0097199 | 0.04097 | -0.01405 | -0.0056118 | -0.0034714 | 0.0043215 | -0.016784 | 0.086975 | 0.13275 | 0.09613 | 0.10986 | 0.32501 | 0.018311 | -0.15106 | 0.11902 | 0.16937 | 0.091553 | 0.23804 | 0.20599 | -0.082397 | -0.14191 | 122.8546 | 122.6852 | 0.1236 | 122.9691 | 122.9462 | 0.26093 | -0.11444 | 122.7539 | 122.6944 | 0.036621 | 122.9553 | 122.9279 | 0.23346 | 0.004578 | 123.1613 | 122.9233 | 122.9324 | -0.35248 | 123.0743 | 123.0423 | 123.0057 | -0.34332
3937.8594 | 123.1338 | -122.8775 | 0.21973 | 0.12909 | 0.033005 | 0.0052978 | 0.0061865 | -0.0079702 | 0.0026424 | -0.0071563 | 0.048599 | -0.0097775 | -0.0043302 | -0.00048061 | 0.0045351 | -0.019561 | 0.041199 | -0.041199 | -0.068665 | -0.009155 | 0.26093 | -0.073242 | -0.27008 | 0.041199 | 0.009155 | -0.086975 | 0.20599 | 0.16479 | -0.1831 | -0.21515 | 122.8043 | 122.6074 | 0.041198 | 122.8363 | 122.8683 | 0.26093 | -0.17853 | 122.6944 | 122.6624 | -0.013733 | 122.9187 | 122.7905 | 0.12817 | -0.054932 | 123.1384 | 122.9187 | 122.8088 | -0.48981 | 123.0835 | 123.0423 | 122.8867 | -0.43488
3939.6094 | 123.1064 | -122.8638 | 0.21057 | 0.15961 | 0.031509 | 0.0067932 | 0.0053321 | -0.010961 | 0.00093342 | -0.0069427 | 0.14015 | -0.012982 | -0.010312 | -0.001976 | 0.0064577 | -0.017212 | 0.086975 | 0.10986 | 0.054932 | 0.050354 | 0.22888 | -0.073242 | -0.23346 | 0.10986 | 0.10986 | 0.027466 | 0.16937 | 0.1236 | -0.14648 | -0.19684 | 122.7905 | 122.6303 | 0.018311 | 122.9736 | 122.9141 | 0.28381 | -0.1236 | 122.7173 | 122.6669 | -0.041198 | 122.9736 | 122.8912 | 0.2243 | -0.086975 | 123.0927 | 122.9507 | 122.9187 | -0.44403 | 123.0331 | 122.9874 | 122.9736 | -0.40741
3941.3594 | 123.1338 | -122.8638 | 0.21057 | 0.12146 | 0.033218 | 0.008075 | 0.0057593 | -0.0098928 | 0.00050622 | -0.0084381 | 0.071487 | -0.0074277 | -0.006039 | 0.00016019 | 0.0070987 | -0.017639 | 0.018311 | 0.004578 | -0.064087 | -0.013733 | 0.27466 | -0.082397 | -0.25635 | 0.027466 | 0.018311 | -0.082397 | 0.20599 | 0.15564 | -0.16937 | -0.21515 | 122.7814 | 122.6074 | 0.064087 | 122.8683 | 122.85 | 0.24262 | -0.19226 | 122.6944 | 122.6486 | -0.004577 | 122.8912 | 122.7814 | 0.13275 | -0.054931 | 123.1384 | 122.8821 | 122.7997 | -0.46692 | 123.0698 | 123.0194 | 122.8821 | -0.42572
3943.0625 | 123.175 | -122.8363 | 0.16479 | -0.19135 | 0.031723 | 0.0087158 | 0.0061865 | -0.010747 | -0.004407 | -0.0097199 | -0.14214 | -0.014264 | -0.0071072 | -0.0049668 | 0.0034671 | -0.014862 | 0.20599 | 0.29297 | 0.20599 | 0.20599 | 0.35706 | 0.091553 | -0.09613 | 0.19684 | 0.29755 | 0.15564 | 0.26093 | 0.24261 | -0.050354 | -0.091553 | 122.9279 | 122.7402 | 0.19226 | 123.1293 | 123.0423 | 0.30212 | 0.041199 | 122.7859 | 122.7448 | 0.09613 | 123.0331 | 122.9919 | 0.24719 | 0.07782 | 123.1934 | 123.0423 | 123.0423 | -0.26092 | 123.0972 | 123.0789 | 123.1338 | -0.25635
3944.8125 | 123.143 | -122.8455 | 0.1831 | 0.0070193 | 0.028305 | 0.0076478 | 0.0057593 | -0.011602 | -0.004407 | -0.0097199 | 0.079117 | -0.01405 | -0.0079618 | -0.0038986 | 0.0030399 | -0.015503 | 0.10529 | 0.1236 | 0.09613 | 0.11902 | 0.3067 | 0.009155 | -0.16479 | 0.10986 | 0.16937 | 0.091553 | 0.24719 | 0.1831 | -0.082397 | -0.13733 | 122.8546 | 122.6807 | 0.1236 | 122.9691 | 122.9645 | 0.28381 | -0.077819 | 122.7631 | 122.7081 | 0.064087 | 122.9553 | 122.937 | 0.22888 | 0 | 123.1522 | 122.9507 | 122.9416 | -0.3479 | 123.0927 | 123.0286 | 123.0148 | -0.32043
3946.5625 | 123.0789 | -122.8409 | 0.21057 | 0.1825 | 0.0298 | 0.007434 | 0.0046911 | -0.010747 | 0.00029262 | -0.0099335 | 0.13252 | -0.013836 | -0.0064664 | -0.0041122 | 0.0081667 | -0.016784 | 0.11444 | 0.10986 | 0.054932 | 0.050354 | 0.21515 | -0.068665 | -0.2243 | 0.10986 | 0.15564 | 0.041199 | 0.17395 | 0.14648 | -0.13733 | -0.1831 | 122.7722 | 122.6166 | 0.004578 | 122.9507 | 122.8912 | 0.27466 | -0.09613 | 122.7036 | 122.6578 | -0.036621 | 122.9507 | 122.8821 | 0.2243 | -0.064087 | 123.056 | 122.9553 | 122.8958 | -0.43488 | 123.0148 | 122.9874 | 122.9965 | -0.39368
3948.3438 | 123.1842 | -122.8226 | 0.18768 | -0.0082397 | 0.029587 | 0.0072204 | 0.0078955 | -0.0083974 | -0.0041934 | -0.0099335 | -0.0048066 | -0.014477 | -0.0064664 | -5.3406e-05 | 0.0011173 | -0.016571 | 0.13275 | 0.15106 | 0.1236 | 0.13275 | 0.33417 | 0 | -0.14648 | 0.16479 | 0.21973 | 0.10986 | 0.26093 | 0.21515 | -0.082397 | -0.11902 | 122.8226 | 122.6761 | 0.14648 | 122.9736 | 122.9553 | 0.27924 | -0.054932 | 122.7402 | 122.7036 | 0.073242 | 122.9874 | 122.9324 | 0.22888 | 0.027466 | 123.1567 | 122.9553 | 122.9462 | -0.33417 | 123.0835 | 123.0377 | 123.0423 | -0.3067
3950.2031 | 123.1613 | -122.8317 | 0.1831 | -0.19135 | 0.0298 | 0.0035888 | 0.0091773 | -0.0094656 | -0.0041934 | -0.0084381 | -0.14977 | -0.013409 | -0.007748 | -0.0026168 | 0.0047489 | -0.018707 | 0.24261 | 0.2655 | 0.20142 | 0.21057 | 0.36163 | 0.073242 | -0.09613 | 0.1831 | 0.27924 | 0.12817 | 0.25177 | 0.22888 | -0.064087 | -0.09613 | 122.905 | 122.7356 | 0.17853 | 123.0972 | 123.0423 | 0.3067 | 0.05951 | 122.7676 | 122.7356 | 0.068665 | 123.0148 | 122.9599 | 0.2243 | 0.045777 | 123.1934 | 123.0743 | 123.0331 | -0.27924 | 123.0835 | 123.0606 | 123.111 | -0.27924
3952.0156 | 123.111 | -122.8592 | 0.21515 | 0.1062 | 0.031296 | 0.004657 | 0.0046911 | -0.0077566 | 0.0013608 | -0.0086517 | 0.14778 | -0.011914 | -0.0075344 | -0.0026168 | 0.0068851 | -0.019989 | 0.12817 | 0.10529 | 0.050354 | 0.059509 | 0.2243 | -0.050354 | -0.21973 | 0.10986 | 0.12817 | 0.032043 | 0.16022 | 0.11444 | -0.15564 | -0.21515 | 122.8088 | 122.6395 | 0.009155 | 122.9645 | 122.9187 | 0.27924 | -0.086975 | 122.7036 | 122.644 | -0.054932 | 122.9691 | 122.8912 | 0.24719 | -0.10071 | 123.0835 | 122.9874 | 122.9095 | -0.43488 | 123.0194 | 122.9736 | 122.9874 | -0.4303
3953.7188 | 123.0652 | -122.8638 | 0.21057 | 0.1062 | 0.0298 | 0.007434 | 0.0051183 | -0.011602 | 7.902e-05 | -0.0090791 | 0.15541 | -0.013409 | -0.008389 | -0.0028306 | 0.0051761 | -0.016784 | 0.1236 | 0.14648 | 0.068665 | 0.059509 | 0.24719 | -0.054932 | -0.23346 | 0.1236 | 0.15564 | 0.045776 | 0.19226 | 0.16022 | -0.12817 | -0.18768 | 122.8088 | 122.6303 | 0.036621 | 123.0103 | 122.9233 | 0.29297 | -0.086975 | 122.7356 | 122.6761 | -0.01831 | 122.9874 | 122.9095 | 0.23346 | -0.050354 | 123.111 | 122.9874 | 122.9324 | -0.44403 | 123.056 | 123.024 | 123.0194 | -0.39825
3955.4375 | 123.2071 | -122.8043 | 0.18768 | -0.023499 | 0.028946 | 0.0070068 | 0.010032 | -0.012456 | -0.0054752 | -0.0082245 | -0.08873 | -0.014905 | -0.0086026 | -0.00026701 | 0.0013309 | -0.016143 | 0.17395 | 0.19226 | 0.16022 | 0.14648 | 0.32959 | 0.022888 | -0.13275 | 0.21515 | 0.27008 | 0.15564 | 0.26093 | 0.21973 | -0.059509 | -0.10529 | 122.8271 | 122.6715 | 0.14191 | 122.9965 | 122.9507 | 0.27924 | -0.013733 | 122.7448 | 122.699 | 0.073242 | 123.0194 | 122.9599 | 0.26093 | 0.032044 | 123.1338 | 122.9782 | 122.9645 | -0.32043 | 123.0652 | 123.024 | 123.0743 | -0.29297
3957.1562 | 123.1659 | -122.8455 | 0.17395 | -0.19135 | 0.030014 | 0.0078614 | 0.0076819 | -0.010961 | -0.0014164 | -0.011002 | -0.25658 | -0.013196 | -0.0064664 | -0.0032578 | 0.0058169 | -0.017852 | 0.21515 | 0.23804 | 0.17853 | 0.18768 | 0.3479 | 0.064087 | -0.10071 | 0.16022 | 0.2243 | 0.064087 | 0.28381 | 0.25177 | -0.064087 | -0.10529 | 122.9095 | 122.7448 | 0.17395 | 123.0835 | 123.0331 | 0.28839 | 0.041199 | 122.7814 | 122.7402 | 0.10986 | 123.0057 | 122.9095 | 0.16937 | 0.07782 | 123.1934 | 123.0606 | 123.024 | -0.27466 | 123.1293 | 123.0972 | 123.0698 | -0.27924
3958.8906 | 123.1384 | -122.8821 | 0.19226 | 0.098572 | 0.031937 | 0.0052978 | 0.0051183 | -0.010747 | 0.0037106 | -0.0090791 | 0.04097 | -0.0082821 | -0.0064664 | -0.0021896 | 0.0088077 | -0.019775 | 0.009155 | -0.027466 | -0.082397 | -0.036621 | 0.28839 | -0.10071 | -0.27466 | 0.018311 | 0 | -0.11444 | 0.20142 | 0.16479 | -0.18768 | -0.22888 | 122.7814 | 122.6074 | 0.09613 | 122.8546 | 122.8455 | 0.23804 | -0.18311 | 122.6944 | 122.6532 | 0.009155 | 122.9004 | 122.7676 | 0.11444 | -0.027466 | 123.1705 | 122.8912 | 122.7997 | -0.46692 | 123.0835 | 123.0469 | 122.8821 | -0.42114
3960.6406 | 123.1338 | -122.8592 | 0.17853 | 0.12909 | 0.031509 | 0.0061524 | 0.0053321 | -0.010747 | 0.0028562 | -0.0067291 | 0.063858 | -0.011273 | -0.0056118 | -0.0017624 | 0.0070987 | -0.017852 | 0.027466 | 0 | -0.059509 | 0 | 0.3067 | -0.091553 | -0.2655 | 0.041199 | 0.013733 | -0.086975 | 0.19226 | 0.14648 | -0.16937 | -0.2243 | 122.7676 | 122.5937 | 0.12817 | 122.8592 | 122.8592 | 0.2655 | -0.15106 | 122.6898 | 122.6349 | 0.013733 | 122.9004 | 122.7722 | 0.13733 | -0.032044 | 123.1659 | 122.8867 | 122.7997 | -0.44403 | 123.0515 | 123.0057 | 122.8729 | -0.40283
3962.3438 | 123.1384 | -122.8409 | 0.20599 | 0.17487 | 0.031723 | 0.0067932 | 0.0059729 | -0.0079702 | 0.00029262 | -0.0065155 | 0.12489 | -0.010418 | -0.0075344 | -0.00069421 | 0.0062441 | -0.016143 | 0.036621 | 0.013733 | -0.041199 | -0.004578 | 0.2655 | -0.086975 | -0.25635 | 0.10071 | 0.091553 | -0.022888 | 0.1831 | 0.14191 | -0.16022 | -0.20599 | 122.7539 | 122.5845 | 0.059509 | 122.8546 | 122.8363 | 0.25177 | -0.16937 | 122.6807 | 122.6349 | -0.022889 | 122.9416 | 122.818 | 0.18311 | -0.064087 | 123.1064 | 122.8775 | 122.7997 | -0.46234 | 123.024 | 122.9828 | 122.9324 | -0.41199
3964.0625 | 123.0835 | -122.8821 | 0.21057 | 0.0070193 | 0.033432 | 0.0033752 | 0.0066137 | -0.008611 | 0.0047788 | -0.0054475 | -0.020065 | -0.010846 | -0.0056118 | -0.00090781 | 0.0051761 | -0.01828 | 0.082397 | 0.032043 | -0.027466 | 0.018311 | 0.3067 | -0.073242 | -0.20599 | 0 | 0.013733 | -0.11902 | 0.21515 | 0.18768 | -0.19226 | -0.22888 | 122.8088 | 122.6761 | 0.096131 | 122.9141 | 122.9004 | 0.22431 | -0.12817 | 122.6898 | 122.6532 | 0.004578 | 122.8821 | 122.7631 | 0.10986 | -0.022888 | 123.1888 | 122.9645 | 122.8546 | -0.41657 | 123.0972 | 123.0698 | 122.8958 | -0.43945
3965.7656 | 123.1247 | -122.8363 | 0.19684 | 0.13672 | 0.032578 | 0.0052978 | 0.0070409 | -0.010106 | -0.00013458 | -0.0069427 | 0.056228 | -0.0097775 | -0.0058254 | 0.00016019 | 0.0051761 | -0.015503 | 0.009155 | -0.022888 | -0.064087 | -0.022888 | 0.25635 | -0.10071 | -0.27008 | 0.013733 | 0.013733 | -0.07782 | 0.19226 | 0.16479 | -0.19226 | -0.22888 | 122.7356 | 122.5662 | 0.05951 | 122.8134 | 122.8134 | 0.24719 | -0.18768 | 122.644 | 122.6074 | -0.004577 | 122.85 | 122.7585 | 0.15106 | -0.032043 | 123.0927 | 122.8455 | 122.7722 | -0.46692 | 123.0286 | 123.0011 | 122.85 | -0.42572
3967.4688 | 123.0927 | -122.8729 | 0.19226 | 0.022278 | 0.027664 | 0.006366 | 0.0059729 | -0.0088248 | -0.0071842 | -0.0082245 | 0.102 | -0.013836 | -0.008389 | -0.0028306 | 0.0026125 | -0.014221 | 0.10071 | 0.11444 | 0.10071 | 0.11444 | 0.28381 | -0.004578 | -0.16479 | 0.10529 | 0.16022 | 0.091553 | 0.21973 | 0.21515 | -0.09613 | -0.12817 | 122.8683 | 122.7081 | 0.091552 | 122.9874 | 122.9874 | 0.27924 | -0.091553 | 122.7768 | 122.7448 | 0.027466 | 122.9782 | 122.9645 | 0.21973 | 0.022888 | 123.1567 | 122.9736 | 122.9736 | -0.35706 | 123.0927 | 123.0881 | 123.0331 | -0.32044
3969.2031 | 123.1888 | -122.8363 | 0.17853 | -0.084534 | 0.035355 | 0.0035888 | 0.011314 | -0.0073294 | 0.0030698 | -0.0067291 | -0.16502 | -0.010205 | -0.0019802 | 0.0012284 | 0.0043215 | -0.019775 | 0.14648 | 0.09613 | 0.032043 | 0.091553 | 0.32959 | -0.050354 | -0.21057 | 0.091553 | 0.11902 | -0.032043 | 0.21973 | 0.19684 | -0.14648 | -0.19226 | 122.7859 | 122.6257 | 0.15106 | 122.9324 | 122.9279 | 0.30212 | -0.032044 | 122.6898 | 122.644 | 0.041199 | 122.9279 | 122.8043 | 0.16022 | 0.01831 | 123.1659 | 122.9828 | 122.8683 | -0.3891 | 123.056 | 123.0331 | 122.9553 | -0.37079
3970.9531 | 123.2117 | -122.8134 | 0.1831 | -0.23712 | 0.032791 | 0.0059388 | 0.011527 | -0.0090384 | -0.0018436 | -0.0086517 | -0.26421 | -0.012555 | -0.0051846 | -0.00090781 | 0.0026125 | -0.017852 | 0.1236 | 0.13733 | 0.082397 | 0.12817 | 0.43488 | 0.032043 | -0.16022 | 0.064087 | 0.14648 | 0.009155 | 0.32044 | 0.27466 | -0.09613 | -0.1236 | 122.8455 | 122.6532 | 0.25177 | 122.9507 | 122.9416 | 0.28839 | -0.059509 | 122.7173 | 122.6898 | 0.13733 | 122.8775 | 122.8226 | 0.13275 | 0.091553 | 123.2483 | 122.937 | 122.8958 | -0.34332 | 123.1339 | 123.0881 | 122.9599 | -0.3067
3972.6719 | 123.1934 | -122.8226 | 0.17853 | -0.00061023 | 0.027878 | 0.0042298 | 0.0085363 | -0.0090384 | -0.0069706 | -0.0099335 | 0.010452 | -0.0164 | -0.0068936 | -0.0017624 | 0.0011173 | -0.015075 | 0.073242 | 0.16937 | 0.13275 | 0.1236 | 0.32501 | 0.004578 | -0.16022 | 0.15106 | 0.21973 | 0.13733 | 0.25177 | 0.20142 | -0.091553 | -0.13275 | 122.8271 | 122.6624 | 0.14648 | 122.9919 | 122.9462 | 0.28381 | -0.10529 | 122.731 | 122.6898 | 0.073242 | 122.9736 | 122.9599 | 0.27008 | 0.022888 | 123.1476 | 122.8958 | 122.9553 | -0.33874 | 123.0743 | 123.024 | 123.0423 | -0.31128
3974.3906 | 123.1979 | -122.8134 | 0.17853 | -0.11505 | 0.031509 | 0.0076478 | 0.0078955 | -0.0083974 | -0.0054752 | -0.0073701 | -0.035324 | -0.014905 | -0.0075344 | -0.0060348 | -0.00016447 | -0.016571 | 0.18768 | 0.27466 | 0.20142 | 0.1831 | 0.33417 | 0.050354 | -0.12817 | 0.20599 | 0.27008 | 0.16937 | 0.26093 | 0.2243 | -0.059509 | -0.10071 | 122.8638 | 122.6852 | 0.15564 | 123.0881 | 122.9965 | 0.31128 | 0.009155 | 122.7539 | 122.7127 | 0.082397 | 123.0194 | 122.9828 | 0.27008 | 0.045776 | 123.1476 | 123.0011 | 123.0148 | -0.3067 | 123.0743 | 123.0377 | 123.0835 | -0.27924
3976.0938 | 123.1247 | -122.8409 | 0.21057 | 0.16724 | 0.033432 | 0.0057252 | 0.0017005 | -0.009252 | 0.0020016 | -0.0082245 | 0.14778 | -0.012341 | -0.0075344 | -0.0013352 | 0.0090213 | -0.018493 | 0.064087 | 0.045776 | -0.013733 | 0.013733 | 0.25177 | -0.091553 | -0.24719 | 0.10986 | 0.10071 | 0.009155 | 0.16479 | 0.11902 | -0.14191 | -0.18768 | 122.7493 | 122.5937 | 0.041199 | 122.8867 | 122.8546 | 0.26093 | -0.14648 | 122.699 | 122.6532 | -0.045776 | 122.9507 | 122.85 | 0.19684 | -0.091552 | 123.0927 | 122.905 | 122.8271 | -0.45776 | 123.0057 | 122.9599 | 122.9416 | -0.39825
3977.8125 | 123.1476 | -122.8271 | 0.19684 | 0.037537 | 0.0298 | 0.0099976 | 0.0049047 | -0.007543 | -0.0063296 | -0.010361 | 0.056228 | -0.016827 | -0.0068936 | -0.003685 | 0.0051761 | -0.014435 | 0.054932 | 0.14648 | 0.091553 | 0.082397 | 0.32044 | -0.013733 | -0.16937 | 0.10986 | 0.16937 | 0.09613 | 0.2243 | 0.19684 | -0.082397 | -0.14191 | 122.8134 | 122.6578 | 0.1236 | 122.9736 | 122.9095 | 0.25177 | -0.14191 | 122.7448 | 122.6852 | 0.027466 | 122.937 | 122.9233 | 0.23804 | 0 | 123.1476 | 122.8821 | 122.9187 | -0.36621 | 123.0515 | 123.024 | 122.9965 | -0.33875
3979.5156 | 123.2117 | -122.8317 | 0.18768 | -0.13031 | 0.033646 | 0.0050842 | 0.0074683 | -0.0090384 | 0.0030698 | -0.0080109 | -0.2108 | -0.0099911 | -0.006039 | -5.3406e-05 | 0.0066715 | -0.018493 | 0.13733 | 0.14191 | 0.027466 | 0.10986 | 0.35706 | -0.009155 | -0.1831 | 0.086975 | 0.1236 | -0.018311 | 0.25635 | 0.21057 | -0.12817 | -0.17395 | 122.8226 | 122.6486 | 0.16937 | 122.9736 | 122.9416 | 0.29297 | -0.050354 | 122.7036 | 122.6578 | 0.068665 | 122.9187 | 122.8134 | 0.15564 | 0.022888 | 123.1888 | 122.9691 | 122.8592 | -0.37079 | 123.0881 | 123.0423 | 122.9553 | -0.36163
3981.2344 | 123.2162 | -122.818 | 0.18768 | -0.17609 | 0.033218 | 0.0048706 | 0.0096045 | -0.0098928 | 0.0020016 | -0.0067291 | -0.25658 | -0.0117 | -0.0030484 | 0.00058739 | 0.0041079 | -0.01828 | 0.11902 | 0.11444 | 0.068665 | 0.11444 | 0.38452 | 0.004578 | -0.13733 | 0.086975 | 0.15106 | 0.013733 | 0.29755 | 0.24261 | -0.1236 | -0.14191 | 122.8226 | 122.6807 | 0.19684 | 122.9324 | 122.9324 | 0.25177 | -0.068664 | 122.6944 | 122.6761 | 0.10986 | 122.905 | 122.8317 | 0.15564 | 0.054932 | 123.2025 | 122.937 | 122.8867 | -0.32501 | 123.1155 | 123.0606 | 122.9691 | -0.32959
3982.9375 | 123.2346 | -122.7859 | 0.18768 | -0.16846 | 0.036423 | 0.0055114 | 0.0087499 | -0.008611 | 0.0037106 | -0.0077973 | -0.26421 | -0.011487 | -0.006039 | -0.0017624 | 0.0053897 | -0.018921 | 0.10986 | 0.10986 | 0.045776 | 0.11902 | 0.37994 | 0 | -0.16479 | 0.10071 | 0.15106 | -0.013733 | 0.28381 | 0.23804 | -0.11444 | -0.13733 | 122.7859 | 122.6212 | 0.19226 | 122.8958 | 122.905 | 0.28381 | -0.07782 | 122.6715 | 122.6486 | 0.09613 | 122.8867 | 122.7722 | 0.1236 | 0.050354 | 123.1659 | 122.8958 | 122.8317 | -0.35248 | 123.0698 | 123.024 | 122.937 | -0.32501
3984.7031 | 123.1293 | -122.8317 | 0.20599 | 0.075684 | 0.031723 | 0.0048706 | 0.0040503 | -0.0081838 | 0.0022152 | -0.0069427 | 0.14015 | -0.011914 | -0.0088162 | -0.0011216 | 0.0060305 | -0.015075 | 0.022888 | 0.009155 | -0.059509 | 0 | 0.28381 | -0.07782 | -0.2655 | 0.041199 | 0.036621 | -0.054932 | 0.20599 | 0.15106 | -0.17395 | -0.20599 | 122.7539 | 122.5662 | 0.077819 | 122.8409 | 122.8317 | 0.2655 | -0.18311 | 122.6578 | 122.6257 | 0 | 122.8729 | 122.7768 | 0.15106 | -0.054932 | 123.1155 | 122.8546 | 122.7722 | -0.4715 | 123.0377 | 122.9828 | 122.8683 | -0.41199
3986.4062 | 123.2025 | -122.8363 | 0.18768 | -0.17609 | 0.035355 | 0.002948 | 0.011314 | -0.010747 | 0.0013608 | -0.0080109 | -0.18791 | -0.010632 | -0.0041164 | -0.0015488 | 0.0049625 | -0.017639 | 0.11902 | 0.10529 | 0.041199 | 0.10986 | 0.35706 | -0.018311 | -0.1831 | 0.07782 | 0.13275 | -0.013733 | 0.23346 | 0.20599 | -0.14648 | -0.1831 | 122.818 | 122.6532 | 0.16937 | 122.9416 | 122.9462 | 0.29297 | -0.068664 | 122.6898 | 122.6532 | 0.045776 | 122.9141 | 122.8226 | 0.16937 | 0.018311 | 123.1934 | 122.9553 | 122.8775 | -0.37079 | 123.0698 | 123.0423 | 122.9691 | -0.37079
3988.0938 | 123.1659 | -122.8592 | 0.18768 | -0.26001 | 0.031296 | 0.0087158 | 0.010032 | -0.0079702 | -0.003339 | -0.0097199 | -0.18028 | -0.014477 | -0.0047574 | -0.0049668 | 0.0015445 | -0.014435 | 0.13733 | 0.20142 | 0.12817 | 0.15564 | 0.39368 | 0.050354 | -0.11902 | 0.09613 | 0.1831 | 0.045776 | 0.31128 | 0.27924 | -0.082397 | -0.12817 | 122.9095 | 122.7402 | 0.20599 | 123.0606 | 123.0148 | 0.27466 | -0.050354 | 122.7768 | 122.731 | 0.1236 | 122.9553 | 122.905 | 0.17395 | 0.091553 | 123.2529 | 122.9965 | 122.9874 | -0.3067 | 123.1705 | 123.1384 | 123.0423 | -0.31586
3989.7812 | 123.1613 | -122.8317 | 0.17853 | -0.2066 | 0.033218 | 0.0078614 | 0.0061865 | -0.007543 | -0.004407 | -0.0077973 | -0.11162 | -0.014264 | -0.00668 | -0.0026168 | 0.0028263 | -0.014648 | 0.17395 | 0.26093 | 0.20142 | 0.19226 | 0.3479 | 0.068665 | -0.10986 | 0.16937 | 0.25177 | 0.13275 | 0.24261 | 0.23346 | -0.054932 | -0.11902 | 122.9004 | 122.7219 | 0.16937 | 123.0927 | 123.024 | 0.30212 | -0.004578 | 122.7768 | 122.7127 | 0.064087 | 123.0011 | 122.9645 | 0.25177 | 0.054931 | 123.1796 | 123.0057 | 123.0331 | -0.28839 | 123.0743 | 123.0652 | 123.0835 | -0.29755
3991.5312 | 123.0789 | -122.8409 | 0.21057 | 0.17487 | 0.028946 | 0.0070068 | 0.0034093 | -0.0094656 | -0.00034818 | -0.0073701 | 0.18593 | -0.011914 | -0.010739 | -0.003685 | 0.0073123 | -0.015289 | 0.09613 | 0.10071 | 0.050354 | 0.036621 | 0.24261 | -0.07782 | -0.23804 | 0.11902 | 0.13733 | 0.032043 | 0.15106 | 0.14191 | -0.15106 | -0.20142 | 122.7631 | 122.6028 | 0.032044 | 122.9416 | 122.8775 | 0.27466 | -0.11444 | 122.6898 | 122.6395 | -0.059509 | 122.9599 | 122.8729 | 0.23346 | -0.068664 | 123.0835 | 122.937 | 122.8912 | -0.44861 | 122.9919 | 122.9828 | 122.9782 | -0.41199
3993.2031 | 123.1796 | -122.8409 | 0.18768 | -0.10742 | 0.033005 | 0.0055114 | 0.010245 | -0.0098928 | 0.0022152 | -0.0054475 | -0.13451 | -0.010418 | -0.00668 | -0.0024032 | 0.0070987 | -0.019775 | 0.14191 | 0.10529 | 0.041199 | 0.064087 | 0.32959 | -0.027466 | -0.20599 | 0.09613 | 0.11444 | -0.027466 | 0.23346 | 0.18768 | -0.14648 | -0.18768 | 122.8134 | 122.6349 | 0.14191 | 122.9462 | 122.905 | 0.27008 | -0.045776 | 122.6944 | 122.6532 | 0.045776 | 122.937 | 122.8134 | 0.16022 | 0 | 123.1705 | 122.9828 | 122.8821 | -0.39368 | 123.0743 | 123.0286 | 122.9553 | -0.37537
3994.9219 | 123.0789 | -122.8592 | 0.2243 | 0.13672 | 0.031296 | 0.0065796 | 0.0055457 | -0.0098928 | -0.0024844 | -0.0058747 | 0.14015 | -0.014691 | -0.0064664 | -0.0024032 | 0.0043215 | -0.015289 | 0.10071 | 0.14191 | 0.073242 | 0.050354 | 0.22888 | -0.045776 | -0.21973 | 0.13275 | 0.14191 | 0.036621 | 0.1831 | 0.16479 | -0.13733 | -0.17853 | 122.8134 | 122.6395 | 0.004578 | 123.0011 | 122.9095 | 0.27008 | -0.1236 | 122.7219 | 122.6807 | -0.041199 | 122.9919 | 122.8958 | 0.21515 | -0.059509 | 123.0881 | 122.9599 | 122.9324 | -0.44403 | 123.0423 | 123.024 | 123.0011 | -0.40283
3996.6094 | 123.1247 | -122.8363 | 0.21057 | 0.1825 | 0.033432 | 0.0072204 | 0.0046911 | -0.008611 | 7.902e-05 | -0.0086517 | 0.12489 | -0.012127 | -0.0081754 | -0.00048061 | 0.0073123 | -0.017639 | 0.036621 | 0.022888 | -0.045776 | -0.013733 | 0.24261 | -0.073242 | -0.26093 | 0.073242 | 0.068665 | -0.013733 | 0.17853 | 0.13733 | -0.16479 | -0.21973 | 122.7631 | 122.5754 | 0.032044 | 122.8592 | 122.8226 | 0.24719 | -0.17395 | 122.6715 | 122.6166 | -0.032043 | 122.9095 | 122.8226 | 0.20599 | -0.073242 | 123.0789 | 122.8729 | 122.7905 | -0.4715 | 123.0148 | 122.9736 | 122.905 | -0.4303
3998.2969 | 123.0835 | -122.85 | 0.21515 | 0.0070193 | 0.036209 | 0.0050842 | 0.0055457 | -0.0083974 | 0.0026424 | -0.0067291 | -0.0048066 | -0.0093503 | -0.0086026 | -0.00048061 | 0.0092349 | -0.018707 | 0.068665 | 0.027466 | -0.045776 | 0.022888 | 0.29297 | -0.086975 | -0.24719 | -0.004578 | 0.027466 | -0.10986 | 0.1831 | 0.1831 | -0.17853 | -0.21973 | 122.7631 | 122.6028 | 0.07782 | 122.8775 | 122.8729 | 0.27008 | -0.14648 | 122.6715 | 122.6303 | -0.032044 | 122.8455 | 122.7402 | 0.10986 | -0.032044 | 123.143 | 122.9187 | 122.8043 | -0.46234 | 123.0331 | 123.0331 | 122.8775 | -0.43488
4000 | 123.0972 | -122.8592 | 0.20142 | 0.20538 | 0.033859 | 0.0070068 | 0.0038367 | -0.0062612 | -0.003339 | -0.0071563 | 0.20119 | -0.01405 | -0.0064664 | -0.0015488 | 0.0073123 | -0.014435 | 0.10071 | 0.091553 | 0.054932 | 0.054932 | 0.21973 | -0.064087 | -0.23346 | 0.10071 | 0.14648 | 0.045776 | 0.13275 | 0.11444 | -0.16479 | -0.20142 | 122.7951 | 122.6257 | 0.018311 | 122.9507 | 122.9141 | 0.28839 | -0.10071 | 122.6944 | 122.6578 | -0.068665 | 122.9599 | 122.905 | 0.24719 | -0.086975 | 123.0789 | 122.9599 | 122.9141 | -0.43488 | 122.9919 | 122.9736 | 123.0057 | -0.40283
4001.6875 | 123.0927 | -122.905 | 0.21057 | 0.068054 | 0.035996 | 0.0052978 | 0.0061865 | -0.008611 | 0.0030698 | -0.0082245 | 0.04097 | -0.011059 | -0.0064664 | -0.0021896 | 0.0068851 | -0.016571 | 0.009155 | -0.041199 | -0.068665 | -0.022888 | 0.28839 | -0.07782 | -0.26093 | -0.018311 | -0.009155 | -0.1236 | 0.21057 | 0.1831 | -0.19226 | -0.24261 | 122.8271 | 122.644 | 0.07782 | 122.8638 | 122.8821 | 0.23804 | -0.20142 | 122.7127 | 122.6624 | 0 | 122.8867 | 122.7814 | 0.11902 | -0.027466 | 123.1934 | 122.9141 | 122.8363 | -0.4715 | 123.1155 | 123.0881 | 122.8958 | -0.45319
4003.375 | 123.111 | -122.8546 | 0.21057 | 0.13672 | 0.034714 | 0.0044434 | 0.0040503 | -0.0073294 | 0.0013608 | -0.0063019 | 0.086746 | -0.012341 | -0.0045438 | -0.00048061 | 0.0051761 | -0.014862 | -0.009155 | -0.027466 | -0.07782 | -0.032043 | 0.27924 | -0.10529 | -0.27466 | 0.004578 | 0.013733 | -0.07782 | 0.20599 | 0.16937 | -0.1831 | -0.23346 | 122.7493 | 122.58 | 0.068665 | 122.8271 | 122.8226 | 0.24262 | -0.21973 | 122.6715 | 122.6212 | -0.004577 | 122.8592 | 122.7768 | 0.15564 | -0.041198 | 123.1338 | 122.8455 | 122.7768 | -0.48523 | 123.0606 | 123.024 | 122.8683 | -0.44403
4005.0625 | 123.1705 | -122.8638 | 0.19684 | -0.25238 | 0.031937 | 0.0025208 | 0.012595 | -0.010747 | -0.006116 | -0.0084381 | -0.17265 | -0.012768 | -0.0030484 | -0.0015488 | 0.00090353 | -0.014221 | 0.15564 | 0.20142 | 0.14191 | 0.16479 | 0.3891 | 0.041199 | -0.1236 | 0.10071 | 0.17395 | 0.050354 | 0.3067 | 0.27008 | -0.082397 | -0.1236 | 122.905 | 122.7402 | 0.19226 | 123.0652 | 123.0286 | 0.28839 | -0.041198 | 122.7814 | 122.7402 | 0.10986 | 122.9645 | 122.9141 | 0.17395 | 0.073243 | 123.2529 | 123.0194 | 123.0057 | -0.32043 | 123.1705 | 123.1339 | 123.0377 | -0.32043
4006.7656 | 123.0835 | -122.8592 | 0.22888 | 0.045166 | 0.028092 | 0.0070068 | 0.0083227 | -0.010106 | -0.004407 | -0.0088653 | 0.11726 | -0.01405 | -0.006039 | -0.0028306 | 0.0021853 | -0.014435 | 0.068665 | 0.15106 | 0.082397 | 0.091553 | 0.30212 | -0.022888 | -0.16022 | 0.086975 | 0.14648 | 0.082397 | 0.21057 | 0.20142 | -0.091553 | -0.14191 | 122.8363 | 122.699 | 0.073242 | 123.0103 | 122.9507 | 0.25177 | -0.16022 | 122.7676 | 122.7173 | -0.018311 | 122.9462 | 122.9416 | 0.2243 | -0.027466 | 123.1613 | 122.9279 | 122.9416 | -0.3891 | 123.0698 | 123.0606 | 123.0057 | -0.37079
4008.4531 | 123.1293 | -122.8409 | 0.1831 | 0.15961 | 0.032578 | 0.0042298 | 0.0076819 | -0.008611 | 0.00029262 | -0.0088653 | 0.12489 | -0.012768 | -0.0073208 | -0.0013352 | 0.0068851 | -0.016998 | 0.09613 | 0.10986 | 0.036621 | 0.073242 | 0.22888 | -0.068665 | -0.2243 | 0.10529 | 0.1236 | 0.027466 | 0.15564 | 0.11902 | -0.15106 | -0.19226 | 122.7722 | 122.6166 | 0.045777 | 122.9507 | 122.9141 | 0.29755 | -0.086975 | 122.6898 | 122.6486 | -0.027465 | 122.9462 | 122.8683 | 0.21973 | -0.064086 | 123.0698 | 122.937 | 122.8775 | -0.40741 | 122.9965 | 122.9599 | 122.9645 | -0.37537
4010.1406 | 123.1018 | -122.8821 | 0.20599 | 0.13672 | 0.037064 | 0.006366 | 0.0053321 | -0.0069022 | 0.001788 | -0.0071563 | 0.063858 | -0.0093503 | -0.0079618 | -5.3406e-05 | 0.0045351 | -0.019561 | 0.018311 | -0.050354 | -0.082397 | -0.022888 | 0.28839 | -0.086975 | -0.2655 | -0.004578 | -0.013733 | -0.11902 | 0.20142 | 0.16022 | -0.19226 | -0.2243 | 122.7951 | 122.6166 | 0.082397 | 122.8317 | 122.8592 | 0.24261 | -0.18768 | 122.6898 | 122.6578 | -0.004578 | 122.8775 | 122.7631 | 0.10529 | -0.045777 | 123.1705 | 122.9004 | 122.7997 | -0.4715 | 123.0835 | 123.0423 | 122.8683 | -0.4303
4011.8281 | 123.1888 | -122.8409 | 0.19226 | -0.099793 | 0.033859 | 0.0065796 | 0.0072547 | -0.0054068 | 0.001788 | -0.0056611 | -0.11925 | -0.0099911 | -0.006039 | -0.00048061 | 0.0068851 | -0.017212 | 0.11902 | 0.10071 | 0.036621 | 0.07782 | 0.33417 | -0.027466 | -0.20599 | 0.082397 | 0.11902 | -0.050354 | 0.23346 | 0.20142 | -0.15106 | -0.19226 | 122.8134 | 122.6349 | 0.14191 | 122.9416 | 122.9187 | 0.28381 | -0.073242 | 122.6898 | 122.6486 | 0.041198 | 122.9233 | 122.7905 | 0.14191 | 0.009155 | 123.175 | 122.9599 | 122.8775 | -0.39826 | 123.0743 | 123.0423 | 122.9599 | -0.38452
4013.5156 | 123.1934 | -122.8317 | 0.17853 | -0.10742 | 0.034073 | 0.0044434 | 0.0078955 | -0.0083974 | 0.0013608 | -0.0052337 | -0.14977 | -0.011273 | -0.0056118 | -0.0028306 | 0.0041079 | -0.01828 | 0.10986 | 0.12817 | 0.036621 | 0.086975 | 0.3479 | -0.022888 | -0.18768 | 0.064087 | 0.13275 | -0.041199 | 0.21973 | 0.19226 | -0.14648 | -0.17853 | 122.8088 | 122.644 | 0.16937 | 122.9599 | 122.9187 | 0.27466 | -0.068665 | 122.6852 | 122.6532 | 0.041199 | 122.8958 | 122.7905 | 0.13733 | 0.013733 | 123.1796 | 122.9416 | 122.8683 | -0.36621 | 123.0515 | 123.024 | 122.9645 | -0.35706
4015.2031 | 123.1842 | -122.8317 | 0.1831 | 0.022278 | 0.030869 | 0.0072204 | 0.0087499 | -0.0094656 | -0.0086796 | -0.0095063 | 0.056228 | -0.012982 | -0.0043302 | -0.0026168 | 0.0019717 | -0.015289 | 0.050354 | 0.15106 | 0.12817 | 0.11444 | 0.32044 | 0.018311 | -0.15564 | 0.1236 | 0.18768 | 0.1236 | 0.24261 | 0.20599 | -0.10071 | -0.12817 | 122.85 | 122.6761 | 0.13733 | 122.9828 | 122.9462 | 0.27008 | -0.13275 | 122.731 | 122.7036 | 0.05951 | 122.9553 | 122.9553 | 0.25177 | 0.022889 | 123.1522 | 122.8821 | 122.9599 | -0.33874 | 123.0743 | 123.0377 | 123.0194 | -0.31128
4016.9375 | 123.1338 | -122.8409 | 0.21057 | 0.15961 | 0.032364 | 0.0072204 | 0.0042639 | -0.0081838 | -0.0018436 | -0.0063019 | 0.13252 | -0.011059 | -0.0081754 | -0.0049668 | 0.0070987 | -0.016784 | 0.050354 | 0.064087 | 0.022888 | 0.027466 | 0.23346 | -0.082397 | -0.24719 | 0.091553 | 0.13733 | 0.013733 | 0.15106 | 0.13275 | -0.13733 | -0.1831 | 122.7585 | 122.5937 | 0.022888 | 122.905 | 122.8683 | 0.27466 | -0.16022 | 122.7036 | 122.6578 | -0.059509 | 122.9324 | 122.8546 | 0.19684 | -0.07782 | 123.0743 | 122.8912 | 122.8638 | -0.45776 | 122.9919 | 122.9736 | 122.9782 | -0.39368
4018.625 | 123.1293 | -122.8821 | 0.21515 | 0.1062 | 0.0345 | 0.0078614 | 0.0061865 | -0.0088248 | 0.0011472 | -0.0080109 | 0.048599 | -0.010205 | -0.0071072 | -0.0021896 | 0.0079531 | -0.015289 | 0.009155 | -0.027466 | -0.082397 | -0.032043 | 0.27924 | -0.10986 | -0.27924 | 0.013733 | 0.009155 | -0.09613 | 0.20599 | 0.1831 | -0.17395 | -0.2243 | 122.7722 | 122.6028 | 0.064087 | 122.8546 | 122.85 | 0.24719 | -0.20599 | 122.7081 | 122.6578 | -0.009155 | 122.8958 | 122.7859 | 0.12817 | -0.032044 | 123.1613 | 122.8912 | 122.7997 | -0.49438 | 123.0881 | 123.0652 | 122.8912 | -0.43945
4020.3125 | 123.2162 | -122.818 | 0.18768 | -0.19135 | 0.035141 | 0.0052978 | 0.0066137 | -0.010534 | 0.0013608 | -0.0090791 | -0.19554 | -0.013409 | -0.006039 | -0.0021896 | 0.0056033 | -0.01593 | 0.13275 | 0.091553 | 0.036621 | 0.09613 | 0.3479 | -0.004578 | -0.18768 | 0.068665 | 0.12817 | -0.009155 | 0.25177 | 0.20142 | -0.15106 | -0.17853 | 122.8134 | 122.6303 | 0.16022 | 122.9095 | 122.9141 | 0.28381 | -0.054932 | 122.6669 | 122.6395 | 0.064087 | 122.8867 | 122.8088 | 0.16937 | 0.013733 | 123.1659 | 122.9507 | 122.8546 | -0.37537 | 123.0698 | 123.0194 | 122.9462 | -0.36621
4022 | 123.2071 | -122.8363 | 0.17395 | -0.25238 | 0.033218 | 0.0093566 | 0.0087499 | -0.01032 | -0.0012028 | -0.0086517 | -0.2108 | -0.013196 | -0.0041164 | -0.0017624 | 0.0028263 | -0.018066 | 0.11902 | 0.13275 | 0.073242 | 0.1236 | 0.42572 | 0.032043 | -0.13275 | 0.07782 | 0.13275 | 0.004578 | 0.29755 | 0.27008 | -0.10529 | -0.14191 | 122.8683 | 122.7036 | 0.25177 | 122.9691 | 122.9599 | 0.25635 | -0.054931 | 122.731 | 122.6944 | 0.1236 | 122.9141 | 122.8409 | 0.14649 | 0.096131 | 123.262 | 122.9553 | 122.9095 | -0.3067 | 123.1338 | 123.1064 | 122.9691 | -0.31586
4023.6875 | 123.1613 | -122.8088 | 0.1831 | -0.22186 | 0.030869 | 0.0057252 | 0.0072547 | -0.009252 | -0.006757 | -0.0060883 | -0.10399 | -0.014691 | -0.0051846 | -0.0013352 | 0.0032535 | -0.015503 | 0.17395 | 0.2655 | 0.20142 | 0.19226 | 0.3479 | 0.054932 | -0.11902 | 0.16022 | 0.27008 | 0.12817 | 0.25635 | 0.22888 | -0.073242 | -0.10986 | 122.8638 | 122.6898 | 0.16479 | 123.0743 | 123.0011 | 0.31128 | -0.009155 | 122.7356 | 122.699 | 0.073243 | 122.9691 | 122.937 | 0.23804 | 0.045777 | 123.1567 | 122.9828 | 123.0103 | -0.30212 | 123.0652 | 123.0377 | 123.0789 | -0.29297
4025.4531 | 123.0972 | -122.8638 | 0.19684 | 0.052795 | 0.031296 | 0.0072204 | 0.0051183 | -0.011815 | -0.0056888 | -0.0090791 | 0.086746 | -0.014691 | -0.0056118 | -0.0017624 | 0.0013309 | -0.016357 | 0.07782 | 0.13275 | 0.10071 | 0.10529 | 0.3067 | -0.004578 | -0.17395 | 0.11444 | 0.15106 | 0.073242 | 0.23346 | 0.20142 | -0.09613 | -0.15106 | 122.8592 | 122.6898 | 0.10986 | 122.9965 | 122.9691 | 0.27924 | -0.11902 | 122.7676 | 122.7127 | 0.036621 | 122.9782 | 122.937 | 0.2243 | 0.004578 | 123.1705 | 122.9416 | 122.9645 | -0.37079 | 123.0972 | 123.0652 | 123.0148 | -0.3479
4027.1406 | 123.1064 | -122.8592 | 0.19684 | 0.13672 | 0.032791 | 0.0061524 | 0.0034093 | -0.0073294 | -0.00034818 | -0.0077973 | 0.16304 | -0.014477 | -0.0088162 | -0.00026701 | 0.0070987 | -0.014862 | 0.11444 | 0.11444 | 0.036621 | 0.086975 | 0.23346 | -0.059509 | -0.21515 | 0.091553 | 0.1236 | 0.009155 | 0.14648 | 0.11444 | -0.15564 | -0.20142 | 122.7997 | 122.644 | 0.036621 | 122.9736 | 122.9462 | 0.30212 | -0.082397 | 122.7036 | 122.6578 | -0.050354 | 122.9507 | 122.8683 | 0.21057 | -0.082397 | 123.0927 | 122.9736 | 122.8958 | -0.41199 | 123.0057 | 122.9736 | 122.9828 | -0.39825
4028.8438 | 123.175 | -122.8729 | 0.20142 | -0.29053 | 0.032364 | 0.0040162 | 0.0096045 | -0.010747 | -0.0035526 | -0.010788 | -0.22606 | -0.014477 | -0.0041164 | -0.0024032 | 0.0015445 | -0.01828 | 0.18768 | 0.20599 | 0.14191 | 0.15564 | 0.37994 | 0.032043 | -0.10986 | 0.11444 | 0.1831 | 0.059509 | 0.3067 | 0.27466 | -0.086975 | -0.11902 | 122.905 | 122.7631 | 0.17853 | 123.0789 | 123.0286 | 0.2655 | -0.013733 | 122.7859 | 122.7539 | 0.10529 | 122.9874 | 122.9324 | 0.17853 | 0.073242 | 123.2529 | 123.0606 | 123.0148 | -0.31128 | 123.1796 | 123.1476 | 123.056 | -0.32044
4030.5312 | 123.2208 | -122.8043 | 0.16937 | -0.069275 | 0.031082 | 0.006366 | 0.0074683 | -0.0098928 | -0.0059024 | -0.010361 | -0.11162 | -0.015545 | -0.0058254 | -0.0021896 | 0.0015445 | -0.015075 | 0.16937 | 0.24261 | 0.17853 | 0.1831 | 0.3479 | 0.036621 | -0.1236 | 0.20599 | 0.26093 | 0.16937 | 0.2655 | 0.22888 | -0.059509 | -0.10529 | 122.8409 | 122.6807 | 0.17853 | 123.0469 | 122.9874 | 0.3067 | 0 | 122.7448 | 122.699 | 0.09613 | 123.0103 | 122.9736 | 0.27466 | 0.059509 | 123.1522 | 122.9736 | 122.9828 | -0.29297 | 123.0698 | 123.0331 | 123.0652 | -0.27466
4032.2188 | 123.1979 | -122.7997 | 0.1831 | -0.099793 | 0.035782 | 0.0048706 | 0.0066137 | -0.010747 | 0.003497 | -0.0090791 | -0.2108 | -0.0099911 | -0.0039028 | -5.3406e-05 | 0.0083805 | -0.02063 | 0.13275 | 0.10071 | 0.032043 | 0.082397 | 0.32501 | -0.036621 | -0.21515 | 0.10529 | 0.12817 | -0.041199 | 0.2243 | 0.17853 | -0.12817 | -0.19226 | 122.7631 | 122.5845 | 0.14191 | 122.9004 | 122.8821 | 0.29755 | -0.050354 | 122.6715 | 122.6074 | 0.041199 | 122.905 | 122.7585 | 0.15106 | -0.004577 | 123.1247 | 122.9324 | 122.8317 | -0.39825 | 123.024 | 122.9782 | 122.9279 | -0.37537
4033.9688 | 123.111 | -122.85 | 0.20142 | 0.13672 | 0.033859 | 0.007434 | 0.0044775 | -0.0098928 | -0.00077538 | -0.0075837 | 0.17067 | -0.015545 | -0.0079618 | -0.0026168 | 0.0070987 | -0.017212 | 0.091553 | 0.11444 | 0.045776 | 0.068665 | 0.2243 | -0.064087 | -0.22888 | 0.10071 | 0.1236 | 0.018311 | 0.14648 | 0.11444 | -0.16479 | -0.21973 | 122.7859 | 122.6212 | 0.022888 | 122.9645 | 122.9187 | 0.29755 | -0.10986 | 122.6852 | 122.6303 | -0.054932 | 122.9507 | 122.8683 | 0.23804 | -0.086975 | 123.0743 | 122.9416 | 122.8958 | -0.4303 | 122.9965 | 122.9645 | 122.9736 | -0.42114
4035.6719 | 123.056 | -122.8546 | 0.20599 | 0.13672 | 0.031937 | 0.0065796 | 0.0051183 | -0.0098928 | -0.0022708 | -0.0092927 | 0.13252 | -0.013409 | -0.0068936 | -0.0028306 | 0.0030399 | -0.015503 | 0.086975 | 0.12817 | 0.086975 | 0.064087 | 0.25635 | -0.054932 | -0.2243 | 0.12817 | 0.17395 | 0.064087 | 0.20599 | 0.1831 | -0.11444 | -0.16479 | 122.7997 | 122.6303 | 0.050354 | 122.9828 | 122.9187 | 0.28839 | -0.11902 | 122.7402 | 122.6898 | 0 | 122.9828 | 122.9187 | 0.22888 | -0.022889 | 123.111 | 122.9416 | 122.9416 | -0.4303 | 123.0606 | 123.0377 | 123.0286 | -0.37079
4037.3594 | 123.2117 | -122.8134 | 0.1831 | -0.2066 | 0.033646 | 0.0059388 | 0.0078955 | -0.010534 | 0.001788 | -0.0097199 | -0.2108 | -0.011487 | -0.0024076 | -0.0015488 | 0.0058169 | -0.017425 | 0.14648 | 0.10986 | 0.064087 | 0.1236 | 0.3891 | 0.009155 | -0.16479 | 0.068665 | 0.11902 | -0.027466 | 0.27008 | 0.22888 | -0.13275 | -0.1831 | 122.8226 | 122.6486 | 0.20599 | 122.9233 | 122.937 | 0.28839 | -0.036621 | 122.6807 | 122.6303 | 0.086976 | 122.8821 | 122.7859 | 0.15564 | 0.045777 | 123.2025 | 122.9599 | 122.8775 | -0.3479 | 123.0835 | 123.0423 | 122.9324 | -0.36621
4039.0625 | 123.2117 | -122.8271 | 0.17853 | -0.16846 | 0.02916 | 0.0055114 | 0.0068273 | -0.007543 | 0.0024288 | -0.0069427 | -0.26421 | -0.0097775 | -0.00668 | -0.0013352 | 0.0070987 | -0.017852 | 0.12817 | 0.11902 | 0.054932 | 0.10986 | 0.37537 | 0 | -0.15106 | 0.086975 | 0.14648 | -0.018311 | 0.27924 | 0.26093 | -0.10529 | -0.16022 | 122.8271 | 122.6761 | 0.19684 | 122.9462 | 122.937 | 0.26093 | -0.050354 | 122.7219 | 122.6669 | 0.10071 | 122.9141 | 122.8088 | 0.14191 | 0.082397 | 123.2025 | 122.9553 | 122.8821 | -0.32959 | 123.1064 | 123.0881 | 122.9736 | -0.33874
4040.75 | 123.1705 | -122.818 | 0.1831 | -0.21423 | 0.031296 | 0.004657 | 0.0098181 | -0.0064748 | -0.0029118 | -0.0084381 | -0.21843 | -0.012555 | -0.0024076 | -0.0021896 | 0.0019717 | -0.015289 | 0.10986 | 0.14191 | 0.082397 | 0.10529 | 0.42114 | 0.018311 | -0.12817 | 0.082397 | 0.16479 | 0.022888 | 0.3067 | 0.25635 | -0.10071 | -0.14648 | 122.8363 | 122.6898 | 0.23804 | 122.9599 | 122.9233 | 0.23346 | -0.073242 | 122.7173 | 122.6715 | 0.1236 | 122.9004 | 122.8409 | 0.16937 | 0.073243 | 123.2391 | 122.9279 | 122.9004 | -0.31128 | 123.1247 | 123.0743 | 122.9828 | -0.32959
4042.4375 | 123.2162 | -122.8271 | 0.1831 | -0.13794 | 0.030441 | 0.0061524 | 0.0085363 | -0.0083974 | -0.0052616 | -0.010574 | -0.065842 | -0.013623 | -0.0064664 | -0.0034714 | 0.00090353 | -0.016784 | 0.1831 | 0.27924 | 0.20142 | 0.17853 | 0.35706 | 0.054932 | -0.10529 | 0.19684 | 0.27466 | 0.17395 | 0.2655 | 0.2243 | -0.073242 | -0.10071 | 122.8821 | 122.7219 | 0.17395 | 123.1064 | 123.0057 | 0.28381 | 0 | 122.7539 | 122.7264 | 0.082398 | 123.024 | 123.0011 | 0.27466 | 0.041199 | 123.1842 | 123.0103 | 123.0286 | -0.28839 | 123.0927 | 123.0515 | 123.1018 | -0.28381
4044.125 | 123.2071 | -122.8226 | 0.16022 | -0.031128 | 0.030441 | 0.0070068 | 0.0061865 | -0.010106 | -0.0046206 | -0.010574 | -0.035324 | -0.01405 | -0.0079618 | -0.0030442 | 0.0034671 | -0.016571 | 0.11444 | 0.18768 | 0.14191 | 0.15564 | 0.32959 | 0.022888 | -0.14648 | 0.16479 | 0.24261 | 0.14191 | 0.24719 | 0.21973 | -0.068665 | -0.10529 | 122.8455 | 122.6761 | 0.16937 | 123.0103 | 122.9782 | 0.30212 | -0.045776 | 122.7539 | 122.7173 | 0.086975 | 122.9874 | 122.9645 | 0.24719 | 0.05951 | 123.1522 | 122.937 | 122.9645 | -0.3067 | 123.0698 | 123.0423 | 123.0652 | -0.2655
4045.8125 | 123.0652 | -122.8683 | 0.19684 | 0.098572 | 0.028092 | 0.0076478 | 0.0044775 | -0.011175 | -0.00098918 | -0.0099335 | 0.10963 | -0.013196 | -0.008389 | -0.0024032 | 0.0073123 | -0.017212 | 0.11444 | 0.14191 | 0.064087 | 0.068665 | 0.26093 | -0.036621 | -0.2243 | 0.11902 | 0.15564 | 0.041199 | 0.17853 | 0.16022 | -0.1236 | -0.16937 | 122.8317 | 122.644 | 0.064087 | 123.0103 | 122.937 | 0.29297 | -0.082397 | 122.7448 | 122.699 | -0.01831 | 122.9874 | 122.9095 | 0.21057 | -0.036621 | 123.1293 | 122.9828 | 122.9324 | -0.42114 | 123.0469 | 123.0286 | 123.024 | -0.36621
4047.5312 | 123.1613 | -122.8638 | 0.21057 | -0.26764 | 0.031296 | 0.0070068 | 0.0087499 | -0.011602 | -0.0014164 | -0.0065155 | -0.22606 | -0.011273 | -0.0043302 | 0.00016019 | 0.0047489 | -0.017852 | 0.20142 | 0.18768 | 0.13733 | 0.16022 | 0.37994 | 0.027466 | -0.10986 | 0.11444 | 0.16479 | 0.032043 | 0.30212 | 0.27466 | -0.082397 | -0.1236 | 122.8912 | 122.7539 | 0.16937 | 123.0515 | 123.024 | 0.27008 | -0.009155 | 122.7814 | 122.7402 | 0.091553 | 122.9782 | 122.8958 | 0.15564 | 0.064087 | 123.2437 | 123.0652 | 123.0011 | -0.32043 | 123.1659 | 123.1384 | 123.0286 | -0.33417
4049.2188 | 123.2071 | -122.8271 | 0.16937 | -0.061646 | 0.027237 | 0.0087158 | 0.0046911 | -0.011602 | -0.0035526 | -0.0092927 | -0.073471 | -0.01405 | -0.0086026 | -0.0015488 | 0.0034671 | -0.018493 | 0.15564 | 0.18768 | 0.14191 | 0.14191 | 0.34332 | 0.013733 | -0.13733 | 0.16937 | 0.24719 | 0.15106 | 0.25635 | 0.20599 | -0.073242 | -0.11444 | 122.8409 | 122.6898 | 0.17395 | 123.0148 | 122.9691 | 0.27924 | -0.013733 | 122.7539 | 122.7127 | 0.086975 | 122.9965 | 122.9782 | 0.2655 | 0.036621 | 123.1705 | 122.9828 | 122.9691 | -0.3067 | 123.0835 | 123.0331 | 123.0743 | -0.28381
4050.9062 | 123.1247 | -122.8546 | 0.20599 | 0.075684 | 0.034287 | 0.0055114 | 0.0053321 | -0.0073294 | 0.0024288 | -0.0095063 | 0.102 | -0.011914 | -0.0088162 | -0.0015488 | 0.0085941 | -0.019348 | 0.059509 | -0.018311 | -0.050354 | -0.022888 | 0.28839 | -0.086975 | -0.2655 | 0.036621 | 0.027466 | -0.073242 | 0.17395 | 0.14191 | -0.1831 | -0.23804 | 122.7676 | 122.5891 | 0.082397 | 122.8363 | 122.8317 | 0.24261 | -0.14649 | 122.6715 | 122.6166 | -0.032044 | 122.8912 | 122.7814 | 0.16479 | -0.064087 | 123.143 | 122.9141 | 122.8043 | -0.4715 | 123.0286 | 122.9965 | 122.8821 | -0.44403
4052.5781 | 123.2025 | -122.818 | 0.1831 | -0.14557 | 0.030228 | 0.0061524 | 0.0078955 | -0.0090384 | -0.003339 | -0.0092927 | -0.14977 | -0.015545 | -0.0053982 | -0.003685 | 0.0011173 | -0.017425 | 0.25635 | 0.28839 | 0.22888 | 0.21057 | 0.36163 | 0.045776 | -0.10529 | 0.21057 | 0.3067 | 0.16022 | 0.26093 | 0.23804 | -0.059509 | -0.09613 | 122.8638 | 122.7127 | 0.17853 | 123.1064 | 123.0286 | 0.31586 | 0.073243 | 122.7585 | 122.7219 | 0.07782 | 123.0286 | 122.9782 | 0.25635 | 0.054932 | 123.1796 | 123.0743 | 123.0469 | -0.28839 | 123.0789 | 123.056 | 123.1247 | -0.27924
4054.2656 | 123.143 | -122.8592 | 0.19684 | 0.1825 | 0.033432 | 0.0042298 | 0.0044775 | -0.0094656 | 0.001788 | -0.0080109 | 0.14778 | -0.01405 | -0.0068936 | -0.0030442 | 0.0085941 | -0.016998 | 0.068665 | 0.018311 | -0.013733 | 0.013733 | 0.24719 | -0.10071 | -0.25177 | 0.091553 | 0.09613 | 0 | 0.16479 | 0.13275 | -0.17395 | -0.21057 | 122.7585 | 122.6074 | 0.050354 | 122.8775 | 122.8729 | 0.2655 | -0.12817 | 122.6852 | 122.6486 | -0.032043 | 122.9507 | 122.8592 | 0.21057 | -0.064087 | 123.1064 | 122.9279 | 122.8455 | -0.44861 | 123.024 | 122.9919 | 122.9553 | -0.40741
4056 | 123.2483 | -122.8363 | 0.18768 | -0.16083 | 0.035568 | 0.0033752 | 0.0081091 | -0.0079702 | 0.0037106 | -0.0088653 | -0.28709 | -0.011059 | -0.00668 | -0.0017624 | 0.0049625 | -0.017852 | 0.15106 | 0.10529 | 0.068665 | 0.13275 | 0.39825 | -0.004578 | -0.16937 | 0.07782 | 0.12817 | -0.009155 | 0.26093 | 0.23346 | -0.13733 | -0.1831 | 122.8317 | 122.6669 | 0.21057 | 122.9416 | 122.9691 | 0.30212 | -0.036621 | 122.699 | 122.6532 | 0.073242 | 122.9141 | 122.8271 | 0.17395 | 0.045776 | 123.2346 | 122.9874 | 122.905 | -0.35706 | 123.0972 | 123.0698 | 122.9645 | -0.37079
4057.6875 | 123.175 | -122.8271 | 0.1831 | -0.21423 | 0.033432 | 0.0082886 | 0.0093909 | -0.007543 | -0.002698 | -0.0086517 | -0.24132 | -0.012555 | -0.0056118 | -0.0030442 | 0.0041079 | -0.015716 | 0.13733 | 0.15564 | 0.10071 | 0.10529 | 0.41199 | 0.027466 | -0.14191 | 0.086975 | 0.16022 | 0.027466 | 0.32044 | 0.26093 | -0.10529 | -0.13275 | 122.8546 | 122.6852 | 0.22888 | 122.9828 | 122.9324 | 0.24719 | -0.045776 | 122.7219 | 122.6944 | 0.13733 | 122.9141 | 122.8546 | 0.16022 | 0.07782 | 123.2391 | 122.9645 | 122.9279 | -0.32501 | 123.1476 | 123.0881 | 122.9874 | -0.31586
4059.375 | 123.1247 | -122.8775 | 0.21057 | 0.083313 | 0.038345 | 0.0061524 | 0.0081091 | -0.009252 | 0.001788 | -0.0077973 | 0.102 | -0.010846 | -0.006039 | -0.00026701 | 0.0056033 | -0.016143 | 0.027466 | -0.009155 | -0.041199 | -0.004578 | 0.27008 | -0.091553 | -0.27008 | 0.027466 | 0.018311 | -0.073242 | 0.18768 | 0.15106 | -0.17395 | -0.22888 | 122.7859 | 122.6074 | 0.05951 | 122.8683 | 122.8729 | 0.2655 | -0.18311 | 122.7036 | 122.6486 | -0.022888 | 122.905 | 122.8043 | 0.15564 | -0.059509 | 123.1476 | 122.905 | 122.8363 | -0.48065 | 123.0652 | 123.0286 | 122.8958 | -0.43945
4061.0781 | 123.1201 | -122.8271 | 0.20142 | 0.12146 | 0.033432 | 0.0061524 | 0.0036231 | -0.0094656 | 0.0026424 | -0.0090791 | 0.094375 | -0.011914 | -0.0092434 | 0.00016019 | 0.0068851 | -0.015503 | 0.032043 | -0.022888 | -0.07782 | -0.027466 | 0.28381 | -0.1236 | -0.28381 | 0.013733 | 0.022888 | -0.07782 | 0.2243 | 0.17395 | -0.16937 | -0.23346 | 122.7036 | 122.5433 | 0.082397 | 122.8043 | 122.7997 | 0.25635 | -0.16937 | 122.6578 | 122.5937 | 0.022888 | 122.8409 | 122.7493 | 0.15564 | -0.027466 | 123.111 | 122.8592 | 122.7493 | -0.48523 | 123.0515 | 123.0011 | 122.85 | -0.43488
4062.7969 | 123.1064 | -122.8775 | 0.21515 | -0.076904 | 0.035568 | 0.0065796 | 0.0057593 | -0.0081838 | 0.0037106 | -0.0063019 | -0.10399 | -0.0097775 | -0.0068936 | -0.0028306 | 0.0088077 | -0.017852 | 0.13733 | 0.10986 | 0.009155 | 0.064087 | 0.29755 | -0.059509 | -0.20599 | 0.064087 | 0.09613 | -0.050354 | 0.21515 | 0.18768 | -0.17395 | -0.19226 | 122.818 | 122.6715 | 0.082397 | 122.9874 | 122.9416 | 0.27008 | -0.07782 | 122.7036 | 122.6852 | 0 | 122.9416 | 122.8271 | 0.14191 | -0.027466 | 123.175 | 123.0148 | 122.8867 | -0.42114 | 123.0927 | 123.0652 | 122.9736 | -0.40741
4064.5 | 123.1567 | -122.8546 | 0.21057 | -0.069275 | 0.036209 | 0.0040162 | 0.0061865 | -0.008611 | 0.00071982 | -0.0063019 | -0.13451 | -0.011914 | -0.004971 | -0.00026701 | 0.0079531 | -0.016571 | 0.11902 | 0.10071 | 0.018311 | 0.068665 | 0.32959 | -0.041199 | -0.20599 | 0.073242 | 0.1236 | -0.041199 | 0.21057 | 0.17395 | -0.14191 | -0.20142 | 122.8134 | 122.6486 | 0.11902 | 122.9553 | 122.9233 | 0.27466 | -0.091552 | 122.7127 | 122.6532 | 0 | 122.9279 | 122.8134 | 0.16022 | -0.036621 | 123.1842 | 122.9736 | 122.8729 | -0.41657 | 123.0652 | 123.0286 | 122.9782 | -0.41199
4066.2031 | 123.1613 | -122.8455 | 0.17395 | -0.19897 | 0.032578 | 0.0055114 | 0.0091773 | -0.008611 | -0.0056888 | -0.0090791 | -0.08873 | -0.015118 | -0.007748 | -0.001976 | 0.00068993 | -0.014435 | 0.17853 | 0.26093 | 0.21515 | 0.20142 | 0.34332 | 0.027466 | -0.091553 | 0.15564 | 0.28381 | 0.13275 | 0.2655 | 0.21515 | -0.059509 | -0.11902 | 122.8729 | 122.7539 | 0.16937 | 123.1064 | 123.0469 | 0.29297 | 0.004578 | 122.7859 | 122.7264 | 0.091553 | 123.0011 | 122.9782 | 0.25177 | 0.041199 | 123.1888 | 123.024 | 123.0606 | -0.2655 | 123.111 | 123.0606 | 123.1293 | -0.29297
4067.9375 | 123.0835 | -122.8867 | 0.21057 | -0.023499 | 0.036209 | 0.0059388 | 0.0074683 | -0.0064748 | 0.0028562 | -0.0060883 | 0.018082 | -0.010205 | -0.0058254 | -0.00090781 | 0.0068851 | -0.016143 | 0.064087 | 0.013733 | -0.041199 | 0.022888 | 0.28839 | -0.064087 | -0.23346 | -0.013733 | 0.013733 | -0.10986 | 0.19684 | 0.17853 | -0.1831 | -0.22888 | 122.8226 | 122.6532 | 0.07782 | 122.9004 | 122.9095 | 0.25635 | -0.14648 | 122.7036 | 122.6578 | -0.013733 | 122.8729 | 122.7768 | 0.11902 | -0.032043 | 123.175 | 122.9507 | 122.8455 | -0.44403 | 123.0835 | 123.0652 | 122.9004 | -0.43945
4069.6406 | 123.1705 | -122.8317 | 0.17395 | -0.2066 | 0.030228 | 0.0057252 | 0.0074683 | -0.0077566 | -0.0056888 | -0.010147 | -0.12688 | -0.015118 | -0.0051846 | -0.0032578 | 0.00090353 | -0.017425 | 0.19684 | 0.27008 | 0.22888 | 0.19684 | 0.36163 | 0.068665 | -0.10529 | 0.17853 | 0.29755 | 0.15106 | 0.25635 | 0.23804 | -0.041199 | -0.082397 | 122.9004 | 122.7264 | 0.18768 | 123.1018 | 123.0286 | 0.30212 | 0.022888 | 122.7905 | 122.7493 | 0.082398 | 123.0103 | 122.9828 | 0.23346 | 0.064087 | 123.1934 | 123.0286 | 123.0606 | -0.27924 | 123.0881 | 123.0698 | 123.1293 | -0.25635
4071.3281 | 123.1613 | -122.8363 | 0.19226 | 0.0070193 | 0.030228 | 0.0067932 | 0.0070409 | -0.007543 | -0.0071842 | -0.0097199 | 0.079117 | -0.013196 | -0.0071072 | -0.0021896 | 0.0041079 | -0.015716 | 0.082397 | 0.1236 | 0.091553 | 0.10986 | 0.32501 | 0.013733 | -0.16479 | 0.10986 | 0.19684 | 0.10071 | 0.22888 | 0.20599 | -0.091553 | -0.14191 | 122.85 | 122.6715 | 0.13275 | 122.9599 | 122.9462 | 0.27466 | -0.10986 | 122.7448 | 122.6944 | 0.036621 | 122.9462 | 122.937 | 0.24262 | 0.013733 | 123.1613 | 122.9187 | 122.9279 | -0.35706 | 123.0652 | 123.0423 | 123.0331 | -0.33417
4073.0469 | 123.1888 | -122.8088 | 0.19684 | -0.00061023 | 0.026596 | 0.0085022 | 0.0070409 | -0.01032 | -0.002698 | -0.0097199 | 0.063858 | -0.013409 | -0.0092434 | -0.0024032 | 0.0026125 | -0.017425 | 0.091553 | 0.13733 | 0.10529 | 0.11444 | 0.33417 | 0.009155 | -0.16022 | 0.1236 | 0.19226 | 0.09613 | 0.2655 | 0.21057 | -0.10529 | -0.14191 | 122.818 | 122.6486 | 0.13733 | 122.9462 | 122.9233 | 0.27466 | -0.10529 | 122.7036 | 122.6669 | 0.068665 | 122.9324 | 122.905 | 0.23804 | 0.013733 | 123.143 | 122.9004 | 122.9141 | -0.35706 | 123.0743 | 123.0194 | 123.0011 | -0.33875
4074.7344 | 123.1613 | -122.8271 | 0.19226 | -0.2066 | 0.035355 | 0.0059388 | 0.0091773 | -0.0096792 | 0.00050622 | -0.010574 | -0.22606 | -0.015118 | -0.0073208 | -0.0034714 | 0.0041079 | -0.018707 | 0.21515 | 0.23804 | 0.16479 | 0.19226 | 0.39368 | 0.045776 | -0.10529 | 0.12817 | 0.21515 | 0.073242 | 0.28839 | 0.24719 | -0.068665 | -0.11444 | 122.8729 | 122.7219 | 0.20142 | 123.0652 | 123.0194 | 0.29755 | 0.022888 | 122.7585 | 122.7127 | 0.09613 | 122.9553 | 122.9004 | 0.18768 | 0.054931 | 123.2208 | 123.0423 | 122.9919 | -0.29755 | 123.1155 | 123.0743 | 123.0423 | -0.3067
4076.4219 | 123.1247 | -122.85 | 0.19684 | 0.15961 | 0.033218 | 0.006366 | 0.0051183 | -0.0098928 | 0.0041378 | -0.0084381 | 0.063858 | -0.012127 | -0.0073208 | -0.0013352 | 0.0060305 | -0.017639 | 0.018311 | -0.022888 | -0.054932 | -0.013733 | 0.28381 | -0.09613 | -0.27924 | 0.018311 | 0.004578 | -0.091553 | 0.20599 | 0.15106 | -0.1831 | -0.21973 | 122.7539 | 122.5708 | 0.086975 | 122.8271 | 122.8363 | 0.2655 | -0.17853 | 122.6669 | 122.6303 | 0.009156 | 122.8683 | 122.7585 | 0.12817 | -0.045776 | 123.1338 | 122.8683 | 122.7951 | -0.47607 | 123.056 | 123.0011 | 122.8546 | -0.41657
4078.1094 | 123.1934 | -122.818 | 0.19684 | -0.12268 | 0.033859 | 0.0057252 | 0.0057593 | -0.0069022 | 0.00093342 | -0.0097199 | -0.17265 | -0.012555 | -0.004971 | -0.00026701 | 0.0058169 | -0.018066 | 0.13733 | 0.13275 | 0.045776 | 0.10529 | 0.35706 | -0.032043 | -0.17853 | 0.068665 | 0.1236 | -0.027466 | 0.24719 | 0.19226 | -0.13733 | -0.1831 | 122.7859 | 122.6395 | 0.16022 | 122.9507 | 122.9233 | 0.28381 | -0.059509 | 122.6807 | 122.6349 | 0.050354 | 122.8867 | 122.7905 | 0.15564 | -0.004577 | 123.175 | 122.9553 | 122.8638 | -0.37537 | 123.0652 | 123.0103 | 122.9416 | -0.37994
4079.8281 | 123.2117 | -122.8271 | 0.1831 | -0.26764 | 0.032791 | 0.0078614 | 0.0081091 | -0.0083974 | -0.0022708 | -0.0095063 | -0.24132 | -0.0117 | -0.0045438 | -0.00026701 | 0.0049625 | -0.015075 | 0.12817 | 0.13275 | 0.059509 | 0.12817 | 0.42572 | 0.027466 | -0.14191 | 0.068665 | 0.11902 | 0 | 0.31586 | 0.27924 | -0.10986 | -0.14648 | 122.8546 | 122.6852 | 0.24261 | 122.9599 | 122.9553 | 0.27008 | -0.054931 | 122.7173 | 122.6807 | 0.13275 | 122.8958 | 122.8271 | 0.14648 | 0.096131 | 123.2529 | 122.9553 | 122.8867 | -0.32501 | 123.143 | 123.1064 | 122.9462 | -0.32959
4081.5156 | 123.1979 | -122.85 | 0.1831 | -0.23712 | 0.033646 | 0.0055114 | 0.0098181 | -0.0088248 | -0.00163 | -0.0084381 | -0.23369 | -0.010846 | -0.004971 | -0.0017624 | 0.0015445 | -0.017425 | 0.10986 | 0.14648 | 0.09613 | 0.1236 | 0.40741 | 0.036621 | -0.15564 | 0.07782 | 0.14648 | 0.009155 | 0.32501 | 0.27466 | -0.086975 | -0.13733 | 122.8867 | 122.6944 | 0.22431 | 122.9965 | 122.9736 | 0.27924 | -0.073242 | 122.7631 | 122.7127 | 0.14191 | 122.9279 | 122.8592 | 0.14648 | 0.091553 | 123.2574 | 122.9599 | 122.9462 | -0.33874 | 123.175 | 123.1247 | 122.9965 | -0.32043
4083.2031 | 123.1476 | -122.8409 | 0.19684 | 0.014648 | 0.030869 | 0.0048706 | 0.0087499 | -0.009252 | -0.004407 | -0.0082245 | 0.071487 | -0.013196 | -0.0071072 | -0.0017624 | 0.0023989 | -0.016571 | 0.07782 | 0.14648 | 0.10986 | 0.11902 | 0.32044 | 0.009155 | -0.15564 | 0.11444 | 0.17395 | 0.10071 | 0.23804 | 0.20599 | -0.10529 | -0.14191 | 122.85 | 122.6852 | 0.1236 | 122.9874 | 122.9599 | 0.27466 | -0.11902 | 122.7356 | 122.699 | 0.041199 | 122.9553 | 122.9416 | 0.24262 | 0.009156 | 123.1613 | 122.9187 | 122.9507 | -0.35248 | 123.0789 | 123.0469 | 123.0148 | -0.33875
4084.9375 | 123.1522 | -122.8683 | 0.20142 | -0.10742 | 0.036209 | 0.0061524 | 0.0066137 | -0.0096792 | 0.004565 | -0.0077973 | -0.17265 | -0.010205 | -0.006039 | -0.0017624 | 0.0079531 | -0.017639 | 0.14648 | 0.11902 | 0.022888 | 0.068665 | 0.33875 | -0.036621 | -0.21057 | 0.068665 | 0.10529 | -0.045776 | 0.23804 | 0.1831 | -0.14648 | -0.20599 | 122.8317 | 122.6578 | 0.13733 | 122.9874 | 122.937 | 0.27924 | -0.054932 | 122.7219 | 122.6624 | 0.036621 | 122.937 | 122.8226 | 0.16022 | -0.018311 | 123.2071 | 123.0148 | 122.8912 | -0.41199 | 123.1064 | 123.0515 | 122.9736 | -0.40741
4086.625 | 123.23 | -122.8226 | 0.17853 | -0.21423 | 0.035141 | 0.0070068 | 0.0083227 | -0.0083974 | 7.902e-05 | -0.0080109 | -0.2108 | -0.011914 | -0.0071072 | -0.0017624 | 0.0062441 | -0.015716 | 0.10986 | 0.11444 | 0.068665 | 0.091553 | 0.38452 | 0.018311 | -0.17395 | 0.050354 | 0.14191 | -0.004578 | 0.27924 | 0.2243 | -0.10986 | -0.16022 | 122.8409 | 122.6486 | 0.20599 | 122.937 | 122.9141 | 0.2655 | -0.068665 | 122.7127 | 122.6624 | 0.10071 | 122.8729 | 122.818 | 0.15564 | 0.045776 | 123.2071 | 122.9324 | 122.8912 | -0.35248 | 123.1018 | 123.0469 | 122.9645 | -0.33874
4088.3281 | 123.1888 | -122.85 | 0.1831 | -0.16083 | 0.035996 | 0.0065796 | 0.010673 | -0.0088248 | 0.00093342 | -0.0086517 | -0.18028 | -0.010418 | -0.0045438 | 0.00037379 | 0.0058169 | -0.017425 | 0.10529 | 0.11444 | 0.050354 | 0.10529 | 0.36621 | -0.009155 | -0.16937 | 0.068665 | 0.1236 | -0.013733 | 0.25177 | 0.20142 | -0.1236 | -0.1831 | 122.8409 | 122.6807 | 0.18311 | 122.9645 | 122.9553 | 0.27466 | -0.077819 | 122.7264 | 122.6669 | 0.068665 | 122.9187 | 122.8363 | 0.16937 | 0.018311 | 123.2162 | 122.9553 | 122.9004 | -0.35248 | 123.1018 | 123.0515 | 122.9736 | -0.36621
4090.0156 | 123.1842 | -122.8455 | 0.19684 | -0.23712 | 0.032578 | 0.0055114 | 0.010886 | -0.0079702 | -0.0035526 | -0.0088653 | -0.2108 | -0.012341 | -0.0034756 | -0.0028306 | 0.0019717 | -0.016998 | 0.10529 | 0.16479 | 0.09613 | 0.1236 | 0.38452 | 0.032043 | -0.13733 | 0.07782 | 0.14191 | 0.036621 | 0.30212 | 0.26093 | -0.09613 | -0.13733 | 122.8775 | 122.7081 | 0.18768 | 123.0103 | 122.9691 | 0.26093 | -0.091552 | 122.7493 | 122.7081 | 0.10529 | 122.9233 | 122.8821 | 0.17395 | 0.064087 | 123.23 | 122.9507 | 122.9416 | -0.33417 | 123.1476 | 123.1064 | 122.9874 | -0.33417
4091.7188 | 123.2208 | -122.8271 | 0.18768 | -0.18372 | 0.034073 | 0.0072204 | 0.0096045 | -0.010961 | 0.00093342 | -0.0082245 | -0.23369 | -0.012341 | -0.0045438 | -0.00090781 | 0.0041079 | -0.019134 | 0.091553 | 0.12817 | 0.064087 | 0.1236 | 0.37537 | 0 | -0.15564 | 0.054932 | 0.12817 | -0.036621 | 0.2655 | 0.23346 | -0.12817 | -0.1831 | 122.8271 | 122.6715 | 0.18768 | 122.9553 | 122.9507 | 0.27924 | -0.09613 | 122.699 | 122.644 | 0.07782 | 122.8821 | 122.7905 | 0.14648 | 0.045776 | 123.2025 | 122.9187 | 122.8912 | -0.34332 | 123.0927 | 123.0606 | 122.9553 | -0.37079
4093.4062 | 123.2071 | -122.8226 | 0.17853 | -0.12268 | 0.030655 | 0.006366 | 0.0066137 | -0.005834 | -0.0065434 | -0.0086517 | -0.058212 | -0.014264 | -0.0056118 | -0.0038986 | 0.0013309 | -0.014862 | 0.14191 | 0.29755 | 0.18768 | 0.19226 | 0.3479 | 0.054932 | -0.11444 | 0.19226 | 0.29755 | 0.1831 | 0.25635 | 0.22888 | -0.068665 | -0.09613 | 122.8775 | 122.7081 | 0.16937 | 123.1201 | 123.0148 | 0.3067 | -0.036621 | 122.7539 | 122.7264 | 0.07782 | 123.0148 | 123.0057 | 0.27924 | 0.050354 | 123.1705 | 122.9645 | 123.0103 | -0.29297 | 123.0789 | 123.0515 | 123.1201 | -0.27466
4095.1094 | 123.2117 | -122.8317 | 0.16937 | -0.038757 | 0.028946 | 0.0050842 | 0.0059729 | -0.0079702 | -0.007825 | -0.010361 | 0.03334 | -0.012768 | -0.0079618 | -0.0026168 | 0.00090353 | -0.015503 | 0.10529 | 0.17853 | 0.13733 | 0.13275 | 0.32959 | -0.004578 | -0.14648 | 0.16022 | 0.22888 | 0.13733 | 0.24261 | 0.21515 | -0.07782 | -0.1236 | 122.8271 | 122.6852 | 0.16022 | 123.0103 | 122.9645 | 0.27924 | -0.064087 | 122.7539 | 122.7081 | 0.073242 | 122.9919 | 122.9691 | 0.26093 | 0.045776 | 123.1613 | 122.937 | 122.9691 | -0.31586 | 123.0743 | 123.0469 | 123.0606 | -0.29297
4096.7969 | 123.1888 | -122.818 | 0.18768 | -0.015869 | 0.028732 | 0.0078614 | 0.0066137 | -0.010961 | -0.0029118 | -0.010361 | -0.020065 | -0.013836 | -0.0043302 | -0.003685 | 0.0043215 | -0.015289 | 0.07782 | 0.15564 | 0.10529 | 0.11444 | 0.32044 | 0.009155 | -0.17853 | 0.15106 | 0.2243 | 0.12817 | 0.25177 | 0.20599 | -0.068665 | -0.11902 | 122.8271 | 122.6395 | 0.13275 | 122.9736 | 122.9324 | 0.29297 | -0.10986 | 122.7493 | 122.699 | 0.064087 | 122.9691 | 122.9462 | 0.24719 | 0.018311 | 123.1384 | 122.8958 | 122.9233 | -0.36621 | 123.0698 | 123.024 | 123.0423 | -0.3067
4098.4844 | 123.0698 | -122.8638 | 0.20142 | 0.1062 | 0.030655 | 0.0052978 | 0.0046911 | -0.008611 | -0.00056178 | -0.0088653 | 0.11726 | -0.015545 | -0.00668 | -0.0032578 | 0.0045351 | -0.01828 | 0.10986 | 0.14648 | 0.091553 | 0.073242 | 0.27924 | -0.054932 | -0.19684 | 0.11444 | 0.16022 | 0.045776 | 0.21515 | 0.1831 | -0.11444 | -0.16022 | 122.8088 | 122.6669 | 0.07782 | 123.0103 | 122.937 | 0.27008 | -0.091553 | 122.7493 | 122.7036 | 0.013733 | 122.9782 | 122.9095 | 0.20599 | -0.018311 | 123.143 | 122.9736 | 122.9553 | -0.39825 | 123.0789 | 123.0469 | 123.024 | -0.36163
4100.1719 | 123.0743 | -122.85 | 0.19226 | 0.1062 | 0.02916 | 0.007434 | 0.0027685 | -0.010106 | -0.0031254 | -0.0095063 | 0.13252 | -0.0117 | -0.0088162 | -0.0030442 | 0.0068851 | -0.01593 | 0.10071 | 0.1236 | 0.068665 | 0.045776 | 0.25177 | -0.045776 | -0.21973 | 0.12817 | 0.14191 | 0.054932 | 0.21057 | 0.16937 | -0.11444 | -0.15564 | 122.8043 | 122.6303 | 0.059509 | 122.9736 | 122.8958 | 0.2655 | -0.091553 | 122.7356 | 122.6944 | 0.01831 | 122.9782 | 122.905 | 0.21057 | -0.022888 | 123.1018 | 122.9507 | 122.9187 | -0.41199 | 123.0606 | 123.0194 | 122.9919 | -0.3479
4101.8594 | 123.2162 | -122.8409 | 0.17853 | -0.19897 | 0.033859 | 0.0067932 | 0.0049047 | -0.009252 | 0.0039242 | -0.0088653 | -0.25658 | -0.011273 | -0.0081754 | -0.0021896 | 0.0083805 | -0.019348 | 0.15564 | 0.10529 | 0.036621 | 0.091553 | 0.37079 | -0.009155 | -0.16022 | 0.086975 | 0.13733 | -0.018311 | 0.25635 | 0.2243 | -0.13733 | -0.18768 | 122.8317 | 122.6807 | 0.19226 | 122.9462 | 122.9324 | 0.25177 | -0.022888 | 122.7036 | 122.6532 | 0.07782 | 122.9279 | 122.8226 | 0.16937 | 0.045776 | 123.2117 | 122.9965 | 122.8775 | -0.33874 | 123.0972 | 123.0652 | 122.9782 | -0.36621
4103.5625 | 123.2117 | -122.8088 | 0.1831 | -0.19897 | 0.0345 | 0.0059388 | 0.0078955 | -0.01032 | 0.001788 | -0.0071563 | -0.28709 | -0.010846 | -0.0058254 | -0.0015488 | 0.0070987 | -0.016784 | 0.14191 | 0.10071 | 0.041199 | 0.09613 | 0.37079 | 0.009155 | -0.16937 | 0.086975 | 0.13733 | -0.027466 | 0.2655 | 0.21515 | -0.14191 | -0.1831 | 122.818 | 122.6395 | 0.18768 | 122.9095 | 122.905 | 0.2655 | -0.041198 | 122.6669 | 122.6257 | 0.082398 | 122.8958 | 122.7814 | 0.15564 | 0.032044 | 123.1796 | 122.9507 | 122.85 | -0.35248 | 123.0743 | 123.024 | 122.9462 | -0.36621
4105.25 | 123.2346 | -122.818 | 0.20599 | -0.16846 | 0.034927 | 0.0078614 | 0.0087499 | -0.0081838 | 7.902e-05 | -0.0067291 | -0.26421 | -0.011914 | -0.0021938 | -0.003685 | 0.0049625 | -0.018707 | 0.1236 | 0.15106 | 0.059509 | 0.11902 | 0.36621 | -0.004578 | -0.16479 | 0.068665 | 0.13733 | -0.027466 | 0.29297 | 0.24261 | -0.11444 | -0.17395 | 122.8134 | 122.6532 | 0.16022 | 122.9691 | 122.937 | 0.28381 | -0.082398 | 122.7036 | 122.644 | 0.086975 | 122.8867 | 122.7905 | 0.14648 | 0.036621 | 123.1842 | 122.9416 | 122.8775 | -0.37079 | 123.111 | 123.0606 | 122.9553 | -0.37994
4106.9375 | 123.2117 | -122.8088 | 0.18768 | -0.084534 | 0.030441 | 0.007434 | 0.0078955 | -0.01032 | -0.0063296 | -0.0084381 | -0.050583 | -0.014691 | -0.0045438 | -0.0028306 | 4.9132e-05 | -0.015503 | 0.13733 | 0.23346 | 0.17853 | 0.17395 | 0.37079 | 0.032043 | -0.11902 | 0.20142 | 0.2655 | 0.17395 | 0.26093 | 0.22888 | -0.059509 | -0.10071 | 122.8409 | 122.6898 | 0.18311 | 123.0423 | 122.9828 | 0.29297 | -0.050354 | 122.7493 | 122.7081 | 0.073242 | 123.0103 | 122.9828 | 0.27466 | 0.041199 | 123.1796 | 122.9462 | 122.9874 | -0.3067 | 123.0698 | 123.0377 | 123.0743 | -0.28839
4108.625 | 123.1201 | -122.8638 | 0.19684 | 0.022278 | 0.027237 | 0.0065796 | 0.0049047 | -0.0081838 | -0.0054752 | -0.0097199 | 0.071487 | -0.015118 | -0.0064664 | -0.0024032 | 0.00090353 | -0.017212 | 0.073242 | 0.13733 | 0.10529 | 0.10529 | 0.32044 | 0.004578 | -0.16479 | 0.10986 | 0.15564 | 0.068665 | 0.24261 | 0.21515 | -0.10071 | -0.14648 | 122.8683 | 122.699 | 0.1236 | 123.0011 | 122.9691 | 0.27008 | -0.1236 | 122.7631 | 122.7173 | 0.045777 | 122.9736 | 122.9324 | 0.21515 | 0.018311 | 123.1842 | 122.937 | 122.9691 | -0.36163 | 123.1064 | 123.0789 | 123.0194 | -0.34332
4110.3125 | 123.1201 | -122.8546 | 0.21973 | 0.1062 | 0.033005 | 0.006366 | 0.0038367 | -0.0094656 | 0.0011472 | -0.0080109 | 0.15541 | -0.011059 | -0.0075344 | -0.0030442 | 0.0083805 | -0.016998 | 0.11902 | 0.10986 | 0.045776 | 0.07782 | 0.22888 | -0.054932 | -0.2243 | 0.09613 | 0.10986 | 0.013733 | 0.16479 | 0.10986 | -0.16022 | -0.20142 | 122.7997 | 122.6303 | 0.009155 | 122.9645 | 122.9324 | 0.30212 | -0.10071 | 122.6944 | 122.6532 | -0.054932 | 122.9507 | 122.8683 | 0.21515 | -0.10986 | 123.0835 | 122.9736 | 122.9004 | -0.44403 | 123.0194 | 122.9645 | 122.9645 | -0.42114
4112.0469 | 123.1613 | -122.8363 | 0.18768 | -0.18372 | 0.031296 | 0.0044434 | 0.0098181 | -0.0083974 | -0.00163 | -0.0097199 | -0.18791 | -0.014477 | -0.0043302 | -0.003685 | 0.0034671 | -0.017639 | 0.19684 | 0.25177 | 0.18768 | 0.19684 | 0.36163 | 0.036621 | -0.10071 | 0.15564 | 0.24261 | 0.091553 | 0.28381 | 0.24719 | -0.050354 | -0.10986 | 122.8729 | 122.7356 | 0.17395 | 123.0881 | 123.0331 | 0.29755 | 0.009155 | 122.7859 | 122.7264 | 0.09613 | 122.9919 | 122.9279 | 0.20142 | 0.059509 | 123.1979 | 123.0331 | 123.024 | -0.28839 | 123.1201 | 123.0835 | 123.0789 | -0.29755
4113.7344 | 123.1796 | -122.8363 | 0.16937 | -0.023499 | 0.030655 | 0.007434 | 0.0083227 | -0.0096792 | -0.0020572 | -0.012283 | 0.018082 | -0.012768 | -0.0079618 | -0.0015488 | 0.00090353 | -0.017852 | 0.09613 | 0.13733 | 0.10986 | 0.10529 | 0.32044 | -0.009155 | -0.15564 | 0.14648 | 0.19226 | 0.10071 | 0.24261 | 0.20142 | -0.09613 | -0.14191 | 122.8271 | 122.6807 | 0.15106 | 122.9736 | 122.9416 | 0.26093 | -0.073243 | 122.7402 | 122.6944 | 0.073242 | 122.9828 | 122.937 | 0.24262 | 0.032043 | 123.1567 | 122.9324 | 122.9462 | -0.32501 | 123.0789 | 123.0377 | 123.0286 | -0.31128
4115.4375 | 123.111 | -122.8638 | 0.19226 | 0.1062 | 0.035355 | 0.004657 | 0.0061865 | -0.0077566 | 0.0043514 | -0.0088653 | 0.03334 | -0.011273 | -0.0073208 | -0.0021896 | 0.0092349 | -0.016784 | 0.018311 | -0.032043 | -0.07782 | -0.036621 | 0.27924 | -0.10529 | -0.27924 | 0.009155 | -0.022888 | -0.12817 | 0.20599 | 0.16479 | -0.20142 | -0.23346 | 122.7585 | 122.5845 | 0.086975 | 122.8317 | 122.8271 | 0.24261 | -0.17395 | 122.6624 | 122.6303 | 0.013733 | 122.8729 | 122.7356 | 0.10528 | -0.027466 | 123.143 | 122.8821 | 122.7859 | -0.4715 | 123.0698 | 123.0286 | 122.8409 | -0.42572
4117.1562 | 123.1659 | -122.8455 | 0.17853 | -0.16083 | 0.032364 | 0.0087158 | 0.0078955 | -0.0090384 | -0.005048 | -0.0090791 | -0.18028 | -0.013196 | -0.0071072 | -0.0026168 | 0.0036807 | -0.015503 | 0.18768 | 0.25177 | 0.16479 | 0.1831 | 0.35248 | 0.054932 | -0.12817 | 0.17853 | 0.2655 | 0.13275 | 0.2655 | 0.25177 | -0.068665 | -0.086975 | 122.9004 | 122.7173 | 0.17395 | 123.0972 | 123.0286 | 0.31128 | 0.009155 | 122.7768 | 122.7585 | 0.086975 | 123.024 | 122.9782 | 0.21973 | 0.073242 | 123.1979 | 123.0331 | 123.0103 | -0.3067 | 123.111 | 123.0972 | 123.111 | -0.2655
4118.8438 | 123.1613 | -122.8271 | 0.17395 | -0.18372 | 0.030441 | 0.0048706 | 0.0096045 | -0.010534 | -0.0020572 | -0.0095063 | -0.11925 | -0.015118 | -0.0058254 | -0.0030442 | 0.00047633 | -0.016143 | 0.20599 | 0.28839 | 0.19684 | 0.19684 | 0.37994 | 0.07782 | -0.09613 | 0.19684 | 0.27466 | 0.12817 | 0.2655 | 0.20142 | -0.054932 | -0.11444 | 122.905 | 122.731 | 0.20599 | 123.1155 | 123.024 | 0.29297 | 0.032044 | 122.7722 | 122.7127 | 0.091553 | 123.024 | 122.9553 | 0.24262 | 0.027466 | 123.2071 | 123.0331 | 123.024 | -0.27008 | 123.0927 | 123.0286 | 123.1018 | -0.28839
4120.5312 | 123.1476 | -122.85 | 0.1831 | 0.014648 | 0.032791 | 0.0072204 | 0.0072547 | -0.01032 | -0.0037662 | -0.0086517 | 0.079117 | -0.015332 | -0.0045438 | -0.00090781 | 4.9132e-05 | -0.016784 | 0.086975 | 0.13733 | 0.09613 | 0.10986 | 0.32044 | 0.009155 | -0.16937 | 0.1236 | 0.16479 | 0.07782 | 0.22888 | 0.19684 | -0.10986 | -0.13733 | 122.8592 | 122.6807 | 0.13733 | 122.9874 | 122.9599 | 0.27924 | -0.09613 | 122.7402 | 122.7127 | 0.045777 | 122.9736 | 122.9279 | 0.21515 | 0.013733 | 123.1705 | 122.937 | 122.9462 | -0.35248 | 123.0789 | 123.0469 | 123.0148 | -0.32043
4122.2188 | 123.1201 | -122.8638 | 0.21515 | 0.11383 | 0.032791 | 0.0052978 | 0.0051183 | -0.0088248 | 0.0022152 | -0.0088653 | 0.1783 | -0.010846 | -0.010525 | -0.001976 | 0.0081667 | -0.018066 | 0.11444 | 0.1236 | 0.032043 | 0.068665 | 0.22888 | -0.064087 | -0.21057 | 0.10529 | 0.12817 | 0.013733 | 0.1236 | 0.10986 | -0.16937 | -0.20142 | 122.7997 | 122.6532 | 0.013733 | 122.9874 | 122.9324 | 0.27924 | -0.10071 | 122.6944 | 122.6624 | -0.091553 | 122.9691 | 122.8775 | 0.21515 | -0.10529 | 123.0927 | 122.9782 | 122.8958 | -0.42572 | 122.9874 | 122.9736 | 122.9919 | -0.41657
4123.9688 | 123.1979 | -122.8271 | 0.19226 | -0.19897 | 0.033218 | 0.0061524 | 0.0085363 | -0.0090384 | -0.004407 | -0.0071563 | -0.16502 | -0.014477 | -0.0051846 | -0.0011216 | 0.0028263 | -0.017852 | 0.21973 | 0.27924 | 0.21515 | 0.20599 | 0.36621 | 0.064087 | -0.10529 | 0.21515 | 0.29755 | 0.16022 | 0.28381 | 0.22888 | -0.054932 | -0.091553 | 122.8912 | 122.7219 | 0.17395 | 123.1064 | 123.0331 | 0.31128 | 0.027466 | 122.7722 | 122.7356 | 0.091552 | 123.0423 | 122.9874 | 0.25177 | 0.036621 | 123.1934 | 123.0469 | 123.0423 | -0.29755 | 123.111 | 123.056 | 123.1247 | -0.28381
4125.7031 | 123.2117 | -122.8409 | 0.16937 | -0.076904 | 0.032364 | 0.0059388 | 0.0070409 | -0.0079702 | -0.00163 | -0.010574 | -0.08873 | -0.014477 | -0.0073208 | -0.0034714 | 0.0034671 | -0.015716 | 0.19226 | 0.22888 | 0.16937 | 0.16479 | 0.36163 | 0.045776 | -0.13733 | 0.21057 | 0.2655 | 0.16937 | 0.27008 | 0.21973 | -0.050354 | -0.091553 | 122.8867 | 122.7036 | 0.19226 | 123.0698 | 123.0057 | 0.30212 | 0.022888 | 122.7905 | 122.7493 | 0.10071 | 123.0515 | 123.0103 | 0.26093 | 0.050354 | 123.2025 | 123.0331 | 123.0103 | -0.3067 | 123.111 | 123.0606 | 123.1064 | -0.26093
4127.3906 | 123.2117 | -122.818 | 0.18768 | -0.14557 | 0.0298 | 0.0070068 | 0.0072547 | -0.011815 | -0.0029118 | -0.0097199 | -0.14214 | -0.013196 | -0.0088162 | -0.001976 | 0.0041079 | -0.016143 | 0.24261 | 0.28381 | 0.21057 | 0.18768 | 0.35248 | 0.041199 | -0.10071 | 0.21057 | 0.29297 | 0.16022 | 0.27008 | 0.24261 | -0.050354 | -0.091553 | 122.8592 | 122.7173 | 0.1648 | 123.1018 | 123.0057 | 0.28839 | 0.054932 | 122.7676 | 122.7264 | 0.082398 | 123.0286 | 122.9782 | 0.25177 | 0.054932 | 123.1705 | 123.0606 | 123.0286 | -0.28839 | 123.0881 | 123.0606 | 123.111 | -0.27924
4129.0938 | 123.1888 | -122.85 | 0.20142 | -0.19135 | 0.031937 | 0.0061524 | 0.0096045 | -0.009252 | -0.00013458 | -0.0086517 | -0.29472 | -0.012982 | -0.0030484 | -0.0030442 | 0.0038943 | -0.019134 | 0.16479 | 0.14191 | 0.086975 | 0.11444 | 0.40283 | 0.036621 | -0.13733 | 0.09613 | 0.12817 | 0.009155 | 0.3067 | 0.27924 | -0.10071 | -0.14191 | 122.8867 | 122.7127 | 0.20142 | 122.9919 | 122.9645 | 0.25177 | -0.036621 | 122.7493 | 122.7081 | 0.10529 | 122.9462 | 122.8592 | 0.15106 | 0.07782 | 123.2529 | 123.0148 | 122.937 | -0.33875 | 123.1567 | 123.1293 | 122.9782 | -0.34332
4130.7812 | 123.1338 | -122.8729 | 0.20142 | 0.014648 | 0.030655 | 0.006366 | 0.010459 | -0.0088248 | -0.0035526 | -0.010147 | 0.03334 | -0.01405 | -0.00668 | -0.0038986 | 0.0023989 | -0.017212 | 0.091553 | 0.13733 | 0.09613 | 0.10529 | 0.33417 | 0.004578 | -0.16937 | 0.12817 | 0.17395 | 0.073242 | 0.2243 | 0.19226 | -0.10986 | -0.15564 | 122.8775 | 122.7036 | 0.13275 | 123.0103 | 122.9782 | 0.27466 | -0.10986 | 122.7631 | 122.7173 | 0.022888 | 123.0011 | 122.9462 | 0.22888 | -0.009155 | 123.2071 | 122.9645 | 122.9691 | -0.37079 | 123.0972 | 123.0652 | 123.0469 | -0.35706
4132.4688 | 123.0743 | -122.8867 | 0.20142 | 0.098572 | 0.030228 | 0.0052978 | 0.0036231 | -0.0094656 | 0.001788 | -0.0084381 | 0.12489 | -0.014905 | -0.0090298 | -0.00090781 | 0.0064577 | -0.016998 | 0.11902 | 0.15106 | 0.054932 | 0.059509 | 0.25635 | -0.054932 | -0.22888 | 0.1236 | 0.15106 | 0.022888 | 0.17853 | 0.11444 | -0.16022 | -0.20142 | 122.8317 | 122.6578 | 0.054932 | 123.0377 | 122.9462 | 0.28839 | -0.082397 | 122.7264 | 122.6852 | -0.022888 | 123.0103 | 122.9095 | 0.2243 | -0.086975 | 123.143 | 123.0057 | 122.9416 | -0.4303 | 123.0652 | 123.0011 | 123.0377 | -0.40283
4134.1562 | 123.111 | -122.8683 | 0.20142 | 0.12909 | 0.031723 | 0.0059388 | 0.0021277 | -0.0094656 | 0.0013608 | -0.0075837 | 0.15541 | -0.014905 | -0.0096706 | -0.0021896 | 0.0070987 | -0.020202 | 0.11902 | 0.10529 | 0.045776 | 0.059509 | 0.22888 | -0.059509 | -0.21973 | 0.11444 | 0.12817 | 0.004578 | 0.14191 | 0.1236 | -0.17853 | -0.20599 | 122.8088 | 122.6486 | 0.027466 | 122.9736 | 122.9279 | 0.27924 | -0.082397 | 122.6898 | 122.6624 | -0.059509 | 122.9828 | 122.8729 | 0.21057 | -0.07782 | 123.0972 | 122.9874 | 122.9141 | -0.42114 | 123.0103 | 122.9919 | 122.9965 | -0.40741
4135.8438 | 123.0835 | -122.8775 | 0.22888 | 0.014648 | 0.035996 | 0.0048706 | 0.0046911 | -0.01032 | 0.0043514 | -0.0065155 | -0.050583 | -0.0099911 | -0.008389 | -0.0032578 | 0.010517 | -0.01593 | 0.086975 | 0.032043 | -0.054932 | 0.018311 | 0.28839 | -0.07782 | -0.24261 | -0.004578 | 0.018311 | -0.10529 | 0.2243 | 0.16937 | -0.18768 | -0.23804 | 122.7997 | 122.6349 | 0.059509 | 122.9095 | 122.8958 | 0.26093 | -0.14191 | 122.6898 | 122.6395 | -0.004578 | 122.8729 | 122.7722 | 0.13275 | -0.059509 | 123.1659 | 122.9645 | 122.8226 | -0.4715 | 123.1018 | 123.0469 | 122.8958 | -0.46692
4137.5312 | 123.1064 | -122.8867 | 0.22888 | 0.083313 | 0.034927 | 0.0052978 | 0.0061865 | -0.010747 | 0.0041378 | -0.0071563 | 0.018082 | -0.010632 | -0.00668 | -0.0015488 | 0.0068851 | -0.016998 | 0.013733 | -0.022888 | -0.073242 | -0.009155 | 0.30212 | -0.10071 | -0.25635 | -0.013733 | -0.009155 | -0.11444 | 0.21515 | 0.16937 | -0.20142 | -0.24719 | 122.7859 | 122.6303 | 0.073242 | 122.8638 | 122.8775 | 0.24719 | -0.21515 | 122.6852 | 122.6395 | -0.013733 | 122.8729 | 122.7722 | 0.13275 | -0.059509 | 123.1888 | 122.9004 | 122.8134 | -0.48523 | 123.1018 | 123.056 | 122.8775 | -0.47607
4139.25 | 123.1064 | -122.8683 | 0.21973 | 0.11383 | 0.036423 | 0.0072204 | 0.0070409 | -0.010534 | 0.001788 | -0.0063019 | 0.071487 | -0.0095639 | -0.0062528 | -5.3406e-05 | 0.0062441 | -0.015289 | -0.013733 | -0.027466 | -0.082397 | -0.022888 | 0.27924 | -0.11444 | -0.26093 | 0 | 0 | -0.11444 | 0.20142 | 0.16022 | -0.19226 | -0.23804 | 122.7539 | 122.6074 | 0.059509 | 122.8409 | 122.8455 | 0.23804 | -0.23346 | 122.6761 | 122.6303 | -0.018311 | 122.8683 | 122.7539 | 0.1236 | -0.05951 | 123.1476 | 122.8546 | 122.7859 | -0.48065 | 123.0698 | 123.0286 | 122.8683 | -0.45776
4140.9375 | 123.1796 | -122.85 | 0.17395 | -0.21423 | 0.033859 | 0.0035888 | 0.0091773 | -0.0062612 | -0.0022708 | -0.0082245 | -0.2108 | -0.012127 | -0.0047574 | -0.0017624 | 0.0036807 | -0.015289 | 0.09613 | 0.16479 | 0.086975 | 0.10986 | 0.40741 | 0.032043 | -0.14648 | 0.073242 | 0.15106 | 0.022888 | 0.29755 | 0.26093 | -0.10986 | -0.13733 | 122.8821 | 122.7036 | 0.23346 | 123.0148 | 122.9599 | 0.25635 | -0.07782 | 122.7402 | 122.7127 | 0.1236 | 122.9233 | 122.8729 | 0.16022 | 0.086975 | 123.2574 | 122.9462 | 122.937 | -0.32043 | 123.1476 | 123.111 | 123.0011 | -0.31128
4142.6562 | 123.1659 | -122.8592 | 0.18768 | 0.0070193 | 0.028519 | 0.0072204 | 0.0059729 | -0.009252 | -0.0054752 | -0.0088653 | 0.079117 | -0.01405 | -0.008389 | -0.003685 | 0.0041079 | -0.015289 | 0.054932 | 0.15564 | 0.11902 | 0.10071 | 0.31128 | 0.013733 | -0.16022 | 0.10986 | 0.1831 | 0.091553 | 0.25635 | 0.19226 | -0.091553 | -0.15106 | 122.8729 | 122.699 | 0.1236 | 123.0148 | 122.9599 | 0.26093 | -0.13275 | 122.7676 | 122.7081 | 0.068665 | 122.9691 | 122.9507 | 0.24261 | 0.004578 | 123.1705 | 122.9141 | 122.9782 | -0.3479 | 123.1155 | 123.0515 | 123.0423 | -0.33874
4144.3594 | 123.1979 | -122.8409 | 0.1831 | -0.13031 | 0.034927 | 0.0050842 | 0.010459 | -0.0096792 | 0.0047788 | -0.0065155 | -0.16502 | -0.012127 | -0.0058254 | -0.0013352 | 0.0060305 | -0.018921 | 0.1236 | 0.1236 | 0.041199 | 0.10071 | 0.36621 | -0.027466 | -0.21057 | 0.082397 | 0.13275 | -0.018311 | 0.26093 | 0.21515 | -0.13733 | -0.20142 | 122.8134 | 122.6303 | 0.18311 | 122.9645 | 122.9416 | 0.31128 | -0.059509 | 122.7036 | 122.6395 | 0.07782 | 122.9233 | 122.8226 | 0.18311 | 0.032044 | 123.2071 | 122.9645 | 122.8821 | -0.39368 | 123.1018 | 123.056 | 122.9736 | -0.38452
4146.0625 | 123.111 | -122.8592 | 0.21515 | 0.029907 | 0.030441 | 0.0059388 | 0.0072547 | -0.0094656 | -0.004407 | -0.0095063 | 0.094375 | -0.013409 | -0.006039 | -0.0017624 | 0.0028263 | -0.014862 | 0.10071 | 0.13275 | 0.10071 | 0.082397 | 0.32501 | -0.013733 | -0.17395 | 0.11444 | 0.16937 | 0.073242 | 0.23804 | 0.19226 | -0.091553 | -0.13733 | 122.8455 | 122.6852 | 0.10986 | 122.9919 | 122.9416 | 0.25635 | -0.11444 | 122.7676 | 122.7219 | 0.022888 | 122.9736 | 122.9324 | 0.21057 | -0.022888 | 123.1842 | 122.9599 | 122.9599 | -0.3891 | 123.0972 | 123.0515 | 123.0286 | -0.35248
4147.75 | 123.1018 | -122.8775 | 0.21057 | 0.045166 | 0.029373 | 0.0082886 | 0.0059729 | -0.011388 | -0.0029118 | -0.0097199 | 0.086746 | -0.014691 | -0.0090298 | -0.0024032 | 0.0038943 | -0.015075 | 0.09613 | 0.13733 | 0.068665 | 0.073242 | 0.29297 | -0.009155 | -0.16022 | 0.10529 | 0.16022 | 0.059509 | 0.22888 | 0.21057 | -0.082397 | -0.1831 | 122.8683 | 122.7173 | 0.082398 | 123.0148 | 122.9507 | 0.23346 | -0.11444 | 122.7951 | 122.6944 | 0.018311 | 122.9828 | 122.937 | 0.24261 | 0 | 123.1705 | 122.9736 | 122.9462 | -0.37079 | 123.1064 | 123.0881 | 123.0377 | -0.39368
4149.4375 | 123.1247 | -122.8638 | 0.19684 | 0.15961 | 0.031723 | 0.008075 | 0.0031957 | -0.0088248 | 0.0020016 | -0.0082245 | 0.14015 | -0.011273 | -0.010525 | -0.0015488 | 0.0083805 | -0.018921 | 0.1236 | 0.11902 | 0.050354 | 0.059509 | 0.23346 | -0.054932 | -0.22888 | 0.091553 | 0.11902 | 0.022888 | 0.14648 | 0.10529 | -0.17395 | -0.20599 | 122.8088 | 122.6349 | 0.036621 | 122.9828 | 122.9233 | 0.28839 | -0.073242 | 122.6898 | 122.6578 | -0.050354 | 122.9553 | 122.8867 | 0.22888 | -0.091552 | 123.0972 | 122.9874 | 122.9141 | -0.42572 | 123.0103 | 122.9691 | 122.9828 | -0.40283
4151.1094 | 123.1888 | -122.7997 | 0.1831 | -0.13794 | 0.034927 | 0.0040162 | 0.0068273 | -0.0079702 | 0.0030698 | -0.0067291 | -0.17265 | -0.0099911 | -0.0041164 | -0.0030442 | 0.0060305 | -0.01828 | 0.12817 | 0.10986 | 0.018311 | 0.09613 | 0.34332 | -0.036621 | -0.19226 | 0.09613 | 0.11902 | -0.041199 | 0.2243 | 0.18768 | -0.15106 | -0.18768 | 122.7631 | 122.6074 | 0.16022 | 122.9095 | 122.8958 | 0.28839 | -0.054931 | 122.6486 | 122.612 | 0.041199 | 122.8958 | 122.7585 | 0.14648 | 0.004578 | 123.143 | 122.9279 | 122.818 | -0.37537 | 123.024 | 122.9874 | 122.9187 | -0.37079
4152.7969 | 123.2162 | -122.8134 | 0.17395 | -0.19135 | 0.034287 | 0.0065796 | 0.011527 | -0.009252 | 0.00050622 | -0.0082245 | -0.21843 | -0.011914 | -0.004971 | -0.0015488 | 0.0032535 | -0.016784 | 0.12817 | 0.10529 | 0.059509 | 0.10529 | 0.39825 | 0.004578 | -0.16022 | 0.07782 | 0.14191 | -0.009155 | 0.27924 | 0.24261 | -0.11902 | -0.16937 | 122.818 | 122.6532 | 0.2243 | 122.9187 | 122.9187 | 0.2655 | -0.045776 | 122.6944 | 122.644 | 0.10529 | 122.8912 | 122.8043 | 0.16022 | 0.068665 | 123.2117 | 122.9416 | 122.8729 | -0.33417 | 123.0927 | 123.056 | 122.9553 | -0.34332
4154.4844 | 123.1705 | -122.8592 | 0.19684 | -0.21423 | 0.030869 | 0.0040162 | 0.0098181 | -0.0077566 | -0.0041934 | -0.0080109 | -0.14977 | -0.012768 | -0.0036892 | -0.00090781 | 0.00090353 | -0.015503 | 0.20599 | 0.25635 | 0.19684 | 0.18768 | 0.35248 | 0.059509 | -0.10529 | 0.1831 | 0.27924 | 0.13275 | 0.26093 | 0.24719 | -0.054932 | -0.10529 | 122.9187 | 122.7539 | 0.15564 | 123.1155 | 123.0469 | 0.29297 | 0.009156 | 122.8043 | 122.7539 | 0.064087 | 123.0423 | 122.9919 | 0.23804 | 0.050354 | 123.2117 | 123.0652 | 123.056 | -0.30212 | 123.1201 | 123.1064 | 123.1384 | -0.30212
4156.2031 | 123.175 | -122.8317 | 0.19684 | -0.092163 | 0.033005 | 0.0052978 | 0.0072547 | -0.010534 | 0.0039242 | -0.0054475 | -0.18028 | -0.0099911 | -0.00668 | -0.0011216 | 0.0085941 | -0.017425 | 0.13275 | 0.12817 | 0.032043 | 0.091553 | 0.33417 | -0.036621 | -0.1831 | 0.073242 | 0.11444 | -0.032043 | 0.22888 | 0.17853 | -0.15564 | -0.19684 | 122.7951 | 122.6486 | 0.13733 | 122.9599 | 122.9233 | 0.27466 | -0.064087 | 122.6761 | 122.6349 | 0.032044 | 122.905 | 122.7997 | 0.1648 | -0.01831 | 123.1659 | 122.9645 | 122.8638 | -0.37994 | 123.0606 | 123.0103 | 122.9462 | -0.39368
4157.9531 | 123.2346 | -122.8409 | 0.18768 | -0.26001 | 0.031723 | 0.0059388 | 0.0091773 | -0.0098928 | -0.0018436 | -0.0082245 | -0.21843 | -0.012127 | -0.004971 | -0.00090781 | 0.0045351 | -0.01593 | 0.11444 | 0.15564 | 0.059509 | 0.1236 | 0.4303 | 0.018311 | -0.15564 | 0.068665 | 0.12817 | 0.009155 | 0.31128 | 0.2655 | -0.10529 | -0.15106 | 122.8592 | 122.6852 | 0.24262 | 122.9965 | 122.9645 | 0.27924 | -0.073242 | 122.7356 | 122.6898 | 0.1236 | 122.9095 | 122.85 | 0.16022 | 0.07782 | 123.2712 | 122.9553 | 122.9004 | -0.34332 | 123.1522 | 123.1064 | 122.9691 | -0.33874
4159.6562 | 123.2117 | -122.8363 | 0.20599 | -0.12268 | 0.033859 | 0.0057252 | 0.0059729 | -0.0096792 | 0.00093342 | -0.0069427 | -0.15739 | -0.011487 | -0.0073208 | -0.0015488 | 0.0058169 | -0.016998 | 0.10071 | 0.12817 | 0.045776 | 0.07782 | 0.3479 | -0.032043 | -0.19684 | 0.07782 | 0.12817 | -0.027466 | 0.23346 | 0.19226 | -0.15564 | -0.19226 | 122.8043 | 122.6395 | 0.14191 | 122.9645 | 122.9141 | 0.27466 | -0.10529 | 122.6807 | 122.644 | 0.027465 | 122.9141 | 122.8088 | 0.16479 | -0.013733 | 123.1842 | 122.937 | 122.8821 | -0.40283 | 123.0698 | 123.0286 | 122.9645 | -0.39826
4161.3438 | 123.23 | -122.8226 | 0.1831 | -0.17609 | 0.0345 | 0.0059388 | 0.0093909 | -0.0098928 | 0.0028562 | -0.0054475 | -0.18028 | -0.013409 | -0.0047574 | 0.00016019 | 0.0034671 | -0.016357 | 0.091553 | 0.13733 | 0.050354 | 0.10071 | 0.36163 | 0 | -0.18768 | 0.07782 | 0.13275 | -0.013733 | 0.24719 | 0.21057 | -0.13275 | -0.1831 | 122.8226 | 122.6349 | 0.17853 | 122.9599 | 122.9233 | 0.28839 | -0.091552 | 122.6898 | 122.6395 | 0.064087 | 122.9004 | 122.8088 | 0.16937 | 0.027466 | 123.1842 | 122.9141 | 122.8729 | -0.37079 | 123.0698 | 123.0331 | 122.9553 | -0.36621
4163.0312 | 123.1247 | -122.8729 | 0.1831 | 0.11383 | 0.035141 | 0.008075 | 0.0034093 | -0.0083974 | -0.0014164 | -0.0080109 | 0.20882 | -0.010632 | -0.010312 | -0.0021896 | 0.0058169 | -0.016143 | 0.07782 | 0.11444 | 0.045776 | 0.054932 | 0.22888 | -0.064087 | -0.2243 | 0.10071 | 0.14191 | 0.022888 | 0.15564 | 0.11902 | -0.16937 | -0.19684 | 122.8088 | 122.6486 | 0.045777 | 122.9874 | 122.9279 | 0.27924 | -0.10528 | 122.7036 | 122.6761 | -0.027465 | 122.9736 | 122.8958 | 0.21973 | -0.064086 | 123.1018 | 122.9507 | 122.9187 | -0.40741 | 123.0286 | 122.9919 | 123.0148 | -0.37994
4164.7188 | 123.1293 | -122.905 | 0.19684 | 0.15961 | 0.032791 | 0.0072204 | 0.0034093 | -0.009252 | -0.00163 | -0.0080109 | 0.16304 | -0.012127 | -0.0079618 | -0.0030442 | 0.0079531 | -0.014435 | 0.036621 | 0.032043 | -0.009155 | 0.009155 | 0.25177 | -0.091553 | -0.25635 | 0.091553 | 0.11902 | 0.018311 | 0.16022 | 0.14191 | -0.16479 | -0.19684 | 122.8134 | 122.6486 | 0.054932 | 122.937 | 122.9141 | 0.2655 | -0.16022 | 122.7402 | 122.7081 | -0.036621 | 122.9965 | 122.9233 | 0.21515 | -0.054931 | 123.1567 | 122.9416 | 122.8958 | -0.45319 | 123.0652 | 123.0469 | 123.024 | -0.39368
4166.4219 | 123.23 | -122.8317 | 0.18768 | -0.1532 | 0.033646 | 0.0065796 | 0.0061865 | -0.0090384 | -0.0014164 | -0.0097199 | -0.21843 | -0.012127 | -0.006039 | -0.0034714 | 0.0043215 | -0.018707 | 0.10986 | 0.10529 | 0.050354 | 0.10986 | 0.38452 | 0 | -0.15106 | 0.059509 | 0.12817 | -0.009155 | 0.28839 | 0.23804 | -0.11902 | -0.17395 | 122.8317 | 122.6807 | 0.19684 | 122.937 | 122.9416 | 0.26093 | -0.07782 | 122.7127 | 122.6578 | 0.10071 | 122.8912 | 122.8226 | 0.16479 | 0.050354 | 123.2162 | 122.9416 | 122.8821 | -0.33874 | 123.1201 | 123.0698 | 122.9599 | -0.36163
4168.1094 | 123.1796 | -122.8455 | 0.19226 | -0.2066 | 0.033218 | 0.0059388 | 0.0096045 | -0.0094656 | -0.0018436 | -0.0088653 | -0.24895 | -0.013623 | -0.003262 | -0.00069421 | 0.0028263 | -0.015289 | 0.10071 | 0.15106 | 0.10529 | 0.1236 | 0.40283 | 0.018311 | -0.15564 | 0.07782 | 0.14648 | 0.018311 | 0.3067 | 0.27924 | -0.086975 | -0.13733 | 122.8638 | 122.6898 | 0.21057 | 122.9965 | 122.9691 | 0.27924 | -0.091553 | 122.7585 | 122.7081 | 0.11444 | 122.9233 | 122.8638 | 0.15564 | 0.086975 | 123.2483 | 122.9462 | 122.9507 | -0.3479 | 123.1522 | 123.1247 | 122.9919 | -0.32959
4169.7969 | 123.1613 | -122.8638 | 0.20599 | -0.17609 | 0.033432 | 0.0059388 | 0.011527 | -0.0069022 | -0.0041934 | -0.0088653 | -0.22606 | -0.016614 | -0.00668 | -0.0028306 | 0.0023989 | -0.016357 | 0.15564 | 0.25177 | 0.17853 | 0.19684 | 0.37994 | 0.041199 | -0.1236 | 0.14191 | 0.23804 | 0.09613 | 0.29297 | 0.25635 | -0.073242 | -0.10529 | 122.905 | 122.7402 | 0.17395 | 123.1155 | 123.0606 | 0.32043 | -0.050354 | 122.7905 | 122.7585 | 0.086975 | 123.0057 | 122.9599 | 0.20142 | 0.050354 | 123.2437 | 123.0194 | 123.0423 | -0.32959 | 123.1567 | 123.1201 | 123.1018 | -0.31128
4171.5156 | 123.1705 | -122.8409 | 0.16022 | -0.2066 | 0.030869 | 0.0061524 | 0.0093909 | -0.008611 | -0.006757 | -0.011856 | -0.14977 | -0.015973 | -0.0064664 | -0.001976 | 0.0019717 | -0.016784 | 0.19226 | 0.28381 | 0.21515 | 0.19226 | 0.37079 | 0.064087 | -0.091553 | 0.1831 | 0.27466 | 0.14648 | 0.26093 | 0.23804 | -0.050354 | -0.10071 | 122.905 | 122.7493 | 0.21057 | 123.1247 | 123.0331 | 0.28381 | 0.032044 | 122.7905 | 122.7402 | 0.10071 | 123.024 | 122.9874 | 0.24719 | 0.07782 | 123.2117 | 123.0331 | 123.056 | -0.25177 | 123.1018 | 123.0789 | 123.1155 | -0.26093
4173.2188 | 123.2162 | -122.8317 | 0.17395 | -0.16083 | 0.026383 | 0.0093566 | 0.0049047 | -0.0083974 | -0.006757 | -0.011856 | -0.065842 | -0.0164 | -0.007748 | -0.0030442 | 0.0019717 | -0.015289 | 0.20599 | 0.26093 | 0.19684 | 0.18768 | 0.35706 | 0.059509 | -0.12817 | 0.21057 | 0.27008 | 0.17395 | 0.24261 | 0.21973 | -0.050354 | -0.10986 | 122.8912 | 122.7036 | 0.18311 | 123.0927 | 123.0194 | 0.31586 | 0.032044 | 122.7814 | 122.7219 | 0.068665 | 123.0423 | 123.0057 | 0.28381 | 0.045777 | 123.1888 | 123.0377 | 123.0286 | -0.30212 | 123.0743 | 123.0515 | 123.1018 | -0.28381
4174.9688 | 123.1705 | -122.8363 | 0.17853 | -0.16846 | 0.029587 | 0.0089294 | 0.010886 | -0.008611 | -0.0041934 | -0.011856 | -0.16502 | -0.013836 | -0.00668 | -0.00026701 | 0.0015445 | -0.018921 | 0.22888 | 0.2655 | 0.2243 | 0.19684 | 0.36163 | 0.050354 | -0.10071 | 0.19684 | 0.27466 | 0.15106 | 0.2655 | 0.23804 | -0.045776 | -0.09613 | 122.8867 | 122.7356 | 0.1831 | 123.1018 | 123.0331 | 0.29755 | 0.050354 | 122.7905 | 122.7402 | 0.086975 | 123.0331 | 122.9874 | 0.24719 | 0.059509 | 123.1979 | 123.0652 | 123.0606 | -0.27924 | 123.1018 | 123.0743 | 123.111 | -0.27466
4176.6562 | 123.175 | -122.8317 | 0.19226 | -0.2066 | 0.031296 | 0.0057252 | 0.0061865 | -0.0096792 | -0.0037662 | -0.010361 | -0.15739 | -0.014905 | -0.0058254 | -0.0015488 | 0.0021853 | -0.016784 | 0.23804 | 0.26093 | 0.20599 | 0.20142 | 0.37079 | 0.054932 | -0.091553 | 0.17853 | 0.2655 | 0.13275 | 0.25177 | 0.2243 | -0.054932 | -0.086975 | 122.8867 | 122.7402 | 0.17853 | 123.0927 | 123.0331 | 0.29297 | 0.045776 | 122.7768 | 122.7448 | 0.059509 | 123.0103 | 122.9645 | 0.21973 | 0.032043 | 123.2025 | 123.0698 | 123.0377 | -0.28381 | 123.0835 | 123.056 | 123.0972 | -0.27924
4178.3438 | 123.1888 | -122.8043 | 0.17853 | -0.023499 | 0.030655 | 0.0089294 | 0.0087499 | -0.010961 | -0.004407 | -0.010788 | -0.020065 | -0.013836 | -0.0058254 | -0.0032578 | 0.0023989 | -0.017425 | 0.13275 | 0.16479 | 0.13275 | 0.13275 | 0.33417 | 0.004578 | -0.15106 | 0.16479 | 0.21973 | 0.1236 | 0.25177 | 0.21973 | -0.068665 | -0.1236 | 122.8088 | 122.6532 | 0.15564 | 122.9691 | 122.937 | 0.28381 | -0.045777 | 122.7356 | 122.6807 | 0.073242 | 122.9691 | 122.9279 | 0.24719 | 0.041199 | 123.1384 | 122.937 | 122.937 | -0.32959 | 123.056 | 123.024 | 123.024 | -0.30212
4180.0625 | 123.0972 | -122.8821 | 0.21515 | 0.075684 | 0.031723 | 0.0057252 | 0.0059729 | -0.0094656 | 0.00029262 | -0.010574 | 0.048599 | -0.014264 | -0.0071072 | -0.0017624 | 0.0058169 | -0.016571 | 0.10986 | 0.14191 | 0.082397 | 0.082397 | 0.30212 | -0.018311 | -0.19226 | 0.13275 | 0.14191 | 0.073242 | 0.23804 | 0.18768 | -0.11902 | -0.16937 | 122.8638 | 122.6898 | 0.086975 | 123.024 | 122.9645 | 0.27466 | -0.10529 | 122.7631 | 122.7127 | 0.022888 | 123.0148 | 122.9553 | 0.24261 | -0.027466 | 123.1842 | 122.9919 | 122.9645 | -0.40741 | 123.1201 | 123.0698 | 123.024 | -0.38452
4181.75 | 123.0743 | -122.8775 | 0.21973 | 0.11383 | 0.0298 | 0.0072204 | 0.0049047 | -0.010106 | -0.0020572 | -0.0090791 | 0.11726 | -0.013409 | -0.007748 | -0.0030442 | 0.0081667 | -0.016571 | 0.1236 | 0.12817 | 0.07782 | 0.064087 | 0.26093 | -0.050354 | -0.20599 | 0.13275 | 0.14191 | 0.050354 | 0.20142 | 0.17853 | -0.1236 | -0.16937 | 122.8271 | 122.6715 | 0.041198 | 123.0057 | 122.9416 | 0.27008 | -0.096131 | 122.7539 | 122.7081 | -0.018311 | 123.0103 | 122.9279 | 0.21973 | -0.041199 | 123.1384 | 123.0011 | 122.9553 | -0.42572 | 123.0789 | 123.056 | 123.0194 | -0.3891
4183.5 | 123.2071 | -122.8683 | 0.1831 | -0.22949 | 0.031296 | 0.0040162 | 0.0091773 | -0.0081838 | 0.0020016 | -0.0090791 | -0.28709 | -0.012127 | -0.0045438 | -0.0017624 | 0.0058169 | -0.019775 | 0.15564 | 0.14191 | 0.059509 | 0.11902 | 0.40741 | 0.027466 | -0.13275 | 0.086975 | 0.14191 | -0.013733 | 0.31586 | 0.29297 | -0.086975 | -0.15106 | 122.8958 | 122.7356 | 0.22431 | 123.0103 | 122.9874 | 0.25177 | -0.027465 | 122.7814 | 122.7173 | 0.13275 | 122.9553 | 122.8546 | 0.13733 | 0.10986 | 123.2758 | 123.024 | 122.9279 | -0.31586 | 123.1842 | 123.1613 | 123.0103 | -0.33417
4185.1875 | 123.1293 | -122.8455 | 0.21057 | 0.0070193 | 0.030441 | 0.0052978 | 0.0064001 | -0.0096792 | -0.0020572 | -0.0099335 | 0.063858 | -0.016614 | -0.010098 | -0.0017624 | 0.0028263 | -0.017212 | 0.10071 | 0.13275 | 0.10071 | 0.09613 | 0.30212 | -0.009155 | -0.16022 | 0.10986 | 0.16937 | 0.073242 | 0.23346 | 0.2243 | -0.09613 | -0.13733 | 122.8363 | 122.6852 | 0.091553 | 122.9782 | 122.9416 | 0.25635 | -0.10986 | 122.7493 | 122.7081 | 0.022888 | 122.9553 | 122.9187 | 0.21057 | 0.013733 | 123.1476 | 122.9462 | 122.9462 | -0.37079 | 123.0789 | 123.0698 | 123.0148 | -0.3479
4186.8906 | 123.111 | -122.8867 | 0.21057 | -0.099793 | 0.035568 | 0.0052978 | 0.0040503 | -0.008611 | 0.0047788 | -0.0090791 | -0.16502 | -0.010418 | -0.0079618 | -0.0030442 | 0.0085941 | -0.018066 | 0.14191 | 0.10529 | 0.004578 | 0.059509 | 0.30212 | -0.059509 | -0.20142 | 0.059509 | 0.073242 | -0.091553 | 0.2243 | 0.20599 | -0.14648 | -0.21057 | 122.8271 | 122.6852 | 0.091553 | 122.9919 | 122.9462 | 0.26093 | -0.068664 | 122.7402 | 122.6761 | 0.013733 | 122.9462 | 122.7951 | 0.11902 | -0.004577 | 123.1888 | 123.0286 | 122.8912 | -0.41199 | 123.111 | 123.0927 | 122.9599 | -0.42114
4188.5938 | 123.1384 | -122.8775 | 0.17395 | 0.11383 | 0.034927 | 0.0044434 | 0.0068273 | -0.0079702 | 0.0043514 | -0.0082245 | 0.079117 | -0.010632 | -0.0081754 | -0.0028306 | 0.0064577 | -0.015716 | 0.032043 | 0.004578 | -0.045776 | -0.018311 | 0.27466 | -0.10071 | -0.25635 | 0.041199 | 0.027466 | -0.07782 | 0.20599 | 0.14648 | -0.19226 | -0.2243 | 122.7768 | 122.6212 | 0.10071 | 122.8821 | 122.8592 | 0.23804 | -0.14191 | 122.6852 | 122.6532 | 0.032044 | 122.9187 | 122.7997 | 0.14648 | -0.027466 | 123.1522 | 122.9095 | 122.8317 | -0.4303 | 123.0835 | 123.024 | 122.905 | -0.39825
4190.2812 | 123.1064 | -122.8409 | 0.21057 | 0.14435 | 0.033432 | 0.0078614 | 0.0057593 | -0.0094656 | -0.0020572 | -0.0073701 | 0.20882 | -0.011059 | -0.008389 | -0.001976 | 0.0083805 | -0.016357 | 0.09613 | 0.10986 | 0.045776 | 0.059509 | 0.21515 | -0.068665 | -0.23346 | 0.082397 | 0.13275 | 0.009155 | 0.14648 | 0.10986 | -0.17395 | -0.2243 | 122.7722 | 122.6074 | 0.004578 | 122.9507 | 122.9004 | 0.29297 | -0.11444 | 122.6669 | 122.6166 | -0.064087 | 122.9233 | 122.85 | 0.23346 | -0.10071 | 123.056 | 122.937 | 122.8867 | -0.44403 | 122.9874 | 122.9507 | 122.9736 | -0.43488
4192.0469 | 123.1064 | -122.8821 | 0.20599 | 0.060425 | 0.031082 | 0.0044434 | 0.0078955 | -0.0066884 | -0.0037662 | -0.0097199 | 0.056228 | -0.015545 | -0.00668 | -0.0028306 | 0.0019717 | -0.016784 | 0.1236 | 0.11902 | 0.10529 | 0.10529 | 0.31128 | -0.018311 | -0.1831 | 0.11444 | 0.14648 | 0.054932 | 0.22888 | 0.20142 | -0.11444 | -0.12817 | 122.8638 | 122.699 | 0.10528 | 123.0011 | 122.9874 | 0.28839 | -0.082398 | 122.7676 | 122.7539 | 0.022888 | 122.9965 | 122.937 | 0.18311 | -0.004578 | 123.1934 | 123.0057 | 122.9874 | -0.3891 | 123.111 | 123.0835 | 123.0286 | -0.33417
4193.7344 | 123.0881 | -122.8821 | 0.22888 | 0.075684 | 0.030441 | 0.0048706 | 0.0076819 | -0.0081838 | -0.003339 | -0.0082245 | 0.048599 | -0.015332 | -0.00668 | -0.0030442 | 0.0028263 | -0.017212 | 0.11902 | 0.1236 | 0.091553 | 0.082397 | 0.29297 | -0.032043 | -0.17395 | 0.10529 | 0.15564 | 0.059509 | 0.2243 | 0.21057 | -0.10071 | -0.14648 | 122.85 | 122.7081 | 0.064087 | 123.0057 | 122.9645 | 0.25635 | -0.10986 | 122.7814 | 122.7356 | -0.004578 | 122.9874 | 122.9416 | 0.20599 | -0.018311 | 123.175 | 123.0011 | 122.9736 | -0.40283 | 123.1064 | 123.0927 | 123.0377 | -0.37537
4195.4219 | 123.1384 | -122.8455 | 0.18768 | 0.15198 | 0.032364 | 0.0048706 | 0.0059729 | -0.0071158 | 0.0028562 | -0.0097199 | 0.12489 | -0.012768 | -0.0086026 | -0.0013352 | 0.0070987 | -0.019561 | 0.13275 | 0.07782 | 0.050354 | 0.068665 | 0.23804 | -0.064087 | -0.22888 | 0.10071 | 0.11444 | 0.009155 | 0.15106 | 0.11902 | -0.15106 | -0.19684 | 122.7814 | 122.6166 | 0.050354 | 122.9233 | 122.9141 | 0.29755 | -0.054932 | 122.6944 | 122.6486 | -0.036621 | 122.9462 | 122.8546 | 0.20599 | -0.068664 | 123.0835 | 122.9782 | 122.8958 | -0.41656 | 122.9965 | 122.9645 | 122.9599 | -0.38452
4197.1094 | 123.1064 | -122.8821 | 0.21515 | -0.054016 | 0.036636 | 0.002948 | 0.0072547 | -0.01032 | 0.0056332 | -0.0069427 | -0.11925 | -0.0095639 | -0.0045438 | -0.0024032 | 0.0066715 | -0.019348 | 0.13733 | 0.07782 | 0.018311 | 0.064087 | 0.32501 | -0.045776 | -0.22888 | 0.054932 | 0.07782 | -0.082397 | 0.21515 | 0.17853 | -0.16479 | -0.19684 | 122.8363 | 122.6532 | 0.10986 | 122.9599 | 122.9462 | 0.29297 | -0.07782 | 122.7173 | 122.6852 | 0 | 122.937 | 122.7997 | 0.11444 | -0.036621 | 123.2071 | 123.0194 | 122.9004 | -0.44403 | 123.0972 | 123.0606 | 122.9599 | -0.41199
4198.7969 | 123.2391 | -122.8546 | 0.1831 | -0.19135 | 0.031509 | 0.0044434 | 0.0093909 | -0.008611 | 0.00029262 | -0.0092927 | -0.24132 | -0.0099911 | -0.0047574 | -0.00026701 | 0.0043215 | -0.016571 | 0.13275 | 0.11444 | 0.054932 | 0.11902 | 0.39825 | -0.004578 | -0.16479 | 0.068665 | 0.15106 | -0.013733 | 0.29755 | 0.25635 | -0.10986 | -0.16479 | 122.85 | 122.6898 | 0.21515 | 122.9691 | 122.9736 | 0.28381 | -0.050354 | 122.7448 | 122.6898 | 0.11444 | 122.9233 | 122.8409 | 0.15106 | 0.073243 | 123.2529 | 122.9874 | 122.9095 | -0.3479 | 123.1522 | 123.111 | 123.0057 | -0.3479
4200.5312 | 123.1567 | -122.8363 | 0.19684 | -0.092163 | 0.033432 | 0.0055114 | 0.0059729 | -0.0090384 | 0.0020016 | -0.0071563 | -0.11925 | -0.012127 | -0.008389 | -0.0028306 | 0.0079531 | -0.017639 | 0.12817 | 0.11902 | 0.036621 | 0.059509 | 0.3067 | -0.054932 | -0.21973 | 0.07782 | 0.11902 | -0.059509 | 0.21515 | 0.19684 | -0.16022 | -0.21515 | 122.7814 | 122.6166 | 0.10986 | 122.9553 | 122.8958 | 0.27924 | -0.068664 | 122.6761 | 122.6212 | 0.018311 | 122.9141 | 122.7768 | 0.15564 | 0 | 123.143 | 122.9645 | 122.8729 | -0.41657 | 123.0515 | 123.0331 | 122.9553 | -0.41199
4202.2188 | 123.2162 | -122.8226 | 0.18768 | -0.11505 | 0.036209 | 0.0040162 | 0.0091773 | -0.010106 | 0.00029262 | -0.0069427 | -0.14214 | -0.013409 | -0.0058254 | -0.0015488 | 0.0038943 | -0.016571 | 0.11902 | 0.11902 | 0.059509 | 0.10071 | 0.3479 | -0.018311 | -0.21057 | 0.059509 | 0.1236 | -0.027466 | 0.25177 | 0.20599 | -0.15106 | -0.19684 | 122.8043 | 122.612 | 0.16022 | 122.9416 | 122.9233 | 0.31128 | -0.068664 | 122.6715 | 122.6257 | 0.064087 | 122.8821 | 122.7951 | 0.16937 | 0.018311 | 123.1705 | 122.9416 | 122.8821 | -0.39825 | 123.0743 | 123.0286 | 122.9462 | -0.38452
4203.9688 | 123.1338 | -122.8638 | 0.20142 | 0.12909 | 0.034073 | 0.0072204 | 0.0053321 | -0.010106 | 0.0024288 | -0.0080109 | 0.079117 | -0.012127 | -0.0062528 | -0.0030442 | 0.0060305 | -0.016143 | -0.013733 | -0.004578 | -0.059509 | -0.013733 | 0.29755 | -0.09613 | -0.26093 | 0.009155 | 0.022888 | -0.07782 | 0.21057 | 0.16937 | -0.19226 | -0.24261 | 122.7676 | 122.6028 | 0.09613 | 122.8592 | 122.85 | 0.24719 | -0.21515 | 122.6715 | 122.6212 | 0.009155 | 122.8729 | 122.7859 | 0.16479 | -0.032043 | 123.1613 | 122.85 | 122.8043 | -0.46234 | 123.0743 | 123.0331 | 122.8867 | -0.44403
4205.6719 | 123.1155 | -122.8592 | 0.20142 | 0.1062 | 0.033005 | 0.0057252 | 0.0055457 | -0.010534 | -0.00034818 | -0.0075837 | 0.13252 | -0.012982 | -0.0056118 | -0.0017624 | 0.0056033 | -0.014648 | -0.009155 | 0.004578 | -0.054932 | -0.004578 | 0.29755 | -0.10986 | -0.2655 | 0.018311 | 0.022888 | -0.073242 | 0.20599 | 0.15564 | -0.19226 | -0.23346 | 122.7493 | 122.5937 | 0.09613 | 122.8638 | 122.8546 | 0.26092 | -0.21057 | 122.6669 | 122.6257 | 0.004578 | 122.8775 | 122.7859 | 0.16022 | -0.045776 | 123.1567 | 122.85 | 122.8043 | -0.46692 | 123.0652 | 123.0148 | 122.8821 | -0.43488
4207.3594 | 123.111 | -122.8912 | 0.22888 | 0.11383 | 0.0345 | 0.0044434 | 0.0081091 | -0.0077566 | -0.00013458 | -0.0084381 | 0.10963 | -0.011273 | -0.0071072 | -0.0034714 | 0.0041079 | -0.015289 | -0.018311 | -0.018311 | -0.086975 | -0.027466 | 0.28839 | -0.11444 | -0.27008 | -0.022888 | -0.022888 | -0.11902 | 0.21057 | 0.16937 | -0.20142 | -0.24261 | 122.7768 | 122.6212 | 0.059509 | 122.8729 | 122.8638 | 0.24262 | -0.24719 | 122.6898 | 122.6486 | -0.018311 | 122.8683 | 122.7722 | 0.1236 | -0.059509 | 123.1796 | 122.8729 | 122.8043 | -0.49896 | 123.1018 | 123.0606 | 122.8683 | -0.4715
4209.0469 | 123.1338 | -122.8363 | 0.1831 | 0.014648 | 0.028092 | 0.0067932 | 0.0081091 | -0.01032 | -0.0073978 | -0.0097199 | 0.071487 | -0.014264 | -0.0088162 | -0.001976 | 0.0013309 | -0.015503 | 0.050354 | 0.12817 | 0.10071 | 0.11444 | 0.32501 | 0 | -0.16479 | 0.086975 | 0.17395 | 0.091553 | 0.21973 | 0.20142 | -0.10986 | -0.14648 | 122.8363 | 122.6715 | 0.14191 | 122.9645 | 122.9507 | 0.27924 | -0.13275 | 122.7264 | 122.6898 | 0.036622 | 122.9233 | 122.9279 | 0.23804 | 0.018311 | 123.1613 | 122.8867 | 122.937 | -0.3479 | 123.056 | 123.0377 | 123.0103 | -0.32959
4210.7344 | 123.0743 | -122.8821 | 0.22888 | 0.17487 | 0.031509 | 0.0059388 | 0.0046911 | -0.011175 | -0.0022708 | -0.0088653 | 0.16304 | -0.013836 | -0.0058254 | -0.0047532 | 0.0056033 | -0.014862 | 0.082397 | 0.10529 | 0.054932 | 0.054932 | 0.22888 | -0.054932 | -0.23804 | 0.10529 | 0.13275 | 0.036621 | 0.15564 | 0.14191 | -0.14648 | -0.19684 | 122.8271 | 122.644 | 0 | 122.9874 | 122.937 | 0.29297 | -0.14649 | 122.7356 | 122.6852 | -0.073242 | 122.9874 | 122.9187 | 0.23346 | -0.086975 | 123.111 | 122.9645 | 122.937 | -0.46692 | 123.0377 | 123.024 | 123.0148 | -0.42572
4212.4531 | 123.1384 | -122.8455 | 0.19684 | 0.13672 | 0.035568 | 0.0057252 | 0.0061865 | -0.0088248 | -0.00077538 | -0.0088653 | 0.11726 | -0.0117 | -0.0092434 | -0.0021896 | 0.0079531 | -0.017425 | 0.082397 | 0.045776 | 0.004578 | 0.036621 | 0.24719 | -0.07782 | -0.22888 | 0.09613 | 0.1236 | 0.004578 | 0.16937 | 0.12817 | -0.14648 | -0.18768 | 122.7676 | 122.6166 | 0.050354 | 122.8912 | 122.8821 | 0.2655 | -0.11444 | 122.699 | 122.6578 | -0.027465 | 122.9416 | 122.85 | 0.19226 | -0.068664 | 123.0927 | 122.9279 | 122.85 | -0.42572 | 123.0148 | 122.9736 | 122.9691 | -0.38452
4214.1562 | 123.175 | -122.8546 | 0.20599 | -0.22186 | 0.032578 | 0.0048706 | 0.0087499 | -0.010961 | -0.0041934 | -0.0092927 | -0.18028 | -0.013623 | -0.004971 | -0.0021896 | 0.0036807 | -0.016143 | 0.14648 | 0.16479 | 0.10529 | 0.13733 | 0.42114 | 0.041199 | -0.12817 | 0.068665 | 0.16022 | 0.009155 | 0.32501 | 0.27924 | -0.10529 | -0.14648 | 122.8958 | 122.7264 | 0.21515 | 123.0194 | 122.9919 | 0.2655 | -0.05951 | 122.7493 | 122.7081 | 0.11902 | 122.9233 | 122.8638 | 0.15564 | 0.073242 | 123.2758 | 123.0011 | 122.9599 | -0.33417 | 123.1796 | 123.1338 | 123.0148 | -0.35248
4215.8906 | 123.2162 | -122.8455 | 0.17395 | -0.24475 | 0.034073 | 0.0055114 | 0.0091773 | -0.008611 | -0.00077538 | -0.0082245 | -0.22606 | -0.012982 | -0.006039 | -0.00026701 | 0.0028263 | -0.016998 | 0.13733 | 0.1236 | 0.068665 | 0.1236 | 0.43488 | 0.009155 | -0.13733 | 0.059509 | 0.12817 | -0.004578 | 0.32044 | 0.25177 | -0.12817 | -0.16022 | 122.8546 | 122.7081 | 0.26093 | 122.9691 | 122.9691 | 0.26093 | -0.036621 | 122.7173 | 122.6852 | 0.14649 | 122.905 | 122.8409 | 0.15564 | 0.07782 | 123.2803 | 122.9828 | 122.9141 | -0.31128 | 123.1659 | 123.0972 | 122.9736 | -0.33417
4217.5938 | 123.1934 | -122.8271 | 0.19226 | -0.25238 | 0.032364 | 0.0072204 | 0.0093909 | -0.0081838 | -0.0014164 | -0.011002 | -0.23369 | -0.013836 | -0.0039028 | -0.0021896 | 0.0045351 | -0.017425 | 0.1236 | 0.15106 | 0.059509 | 0.1236 | 0.40741 | 0.013733 | -0.13733 | 0.073242 | 0.14191 | 0.013733 | 0.32044 | 0.27466 | -0.11444 | -0.15106 | 122.8409 | 122.6898 | 0.21515 | 122.9782 | 122.9507 | 0.26093 | -0.068665 | 122.7127 | 122.6761 | 0.12817 | 122.9004 | 122.8409 | 0.16479 | 0.082397 | 123.2346 | 122.9507 | 122.8867 | -0.32959 | 123.1476 | 123.1018 | 122.9691 | -0.34332
4219.2969 | 123.2071 | -122.8363 | 0.16479 | -0.13794 | 0.028732 | 0.0089294 | 0.0059729 | -0.01032 | -0.0056888 | -0.010788 | -0.081101 | -0.014691 | -0.0064664 | -0.0038986 | 0.0023989 | -0.014221 | 0.1831 | 0.26093 | 0.18768 | 0.18768 | 0.37079 | 0.041199 | -0.1236 | 0.19684 | 0.27466 | 0.17395 | 0.2655 | 0.21515 | -0.059509 | -0.10986 | 122.8775 | 122.7127 | 0.20599 | 123.0972 | 123.024 | 0.31128 | 0.01831 | 122.7768 | 122.7264 | 0.10071 | 123.0331 | 123.0103 | 0.28381 | 0.050354 | 123.2071 | 123.0194 | 123.024 | -0.28839 | 123.1018 | 123.0515 | 123.111 | -0.27466
4221.0312 | 123.1018 | -122.8592 | 0.19684 | 0.083313 | 0.031937 | 0.0044434 | 0.0085363 | -0.0083974 | -0.0037662 | -0.0092927 | 0.094375 | -0.010205 | -0.0062528 | -0.0024032 | 0.0030399 | -0.015716 | 0.10071 | 0.12817 | 0.09613 | 0.068665 | 0.26093 | -0.013733 | -0.19684 | 0.11444 | 0.14648 | 0.054932 | 0.2243 | 0.1831 | -0.10529 | -0.14191 | 122.8455 | 122.6624 | 0.064087 | 122.9874 | 122.9279 | 0.2655 | -0.09613 | 122.7539 | 122.7173 | 0.027466 | 122.9736 | 122.9141 | 0.19684 | -0.013733 | 123.1201 | 122.9599 | 122.9553 | -0.39368 | 123.0835 | 123.0423 | 123.0057 | -0.33875
4222.7188 | 123.1293 | -122.8821 | 0.21515 | 0.1062 | 0.034714 | 0.008075 | 0.0038367 | -0.0096792 | 7.902e-05 | -0.0071563 | 0.16304 | -0.012982 | -0.0071072 | -0.0017624 | 0.0077395 | -0.018493 | 0.1236 | 0.10529 | 0.050354 | 0.064087 | 0.24719 | -0.054932 | -0.23804 | 0.10071 | 0.11902 | 0.013733 | 0.15564 | 0.12817 | -0.1831 | -0.21057 | 122.8271 | 122.644 | 0.032043 | 122.9874 | 122.9462 | 0.30212 | -0.091553 | 122.699 | 122.6715 | -0.059509 | 122.9828 | 122.8958 | 0.2243 | -0.086975 | 123.1293 | 123.0057 | 122.9324 | -0.45319 | 123.0377 | 123.0103 | 123.0011 | -0.42572
4224.4375 | 123.0927 | -122.8638 | 0.20599 | 0.045166 | 0.033005 | 0.0061524 | 0.0076819 | -0.007543 | -0.004407 | -0.011856 | 0.063858 | -0.013623 | -0.006039 | -0.0024032 | 0.0030399 | -0.01828 | 0.091553 | 0.11902 | 0.091553 | 0.082397 | 0.30212 | -0.009155 | -0.16937 | 0.10071 | 0.15564 | 0.059509 | 0.23346 | 0.18768 | -0.10986 | -0.14648 | 122.8546 | 122.6944 | 0.09613 | 122.9828 | 122.9462 | 0.25177 | -0.11444 | 122.7539 | 122.7173 | 0.027465 | 122.9645 | 122.9233 | 0.20599 | -0.018311 | 123.1659 | 122.9553 | 122.9553 | -0.37537 | 123.0972 | 123.0515 | 123.0194 | -0.35248
4226.1562 | 123.2162 | -122.8455 | 0.1831 | -0.099793 | 0.027878 | 0.0055114 | 0.0098181 | -0.0096792 | -0.0046206 | -0.0099335 | -0.065842 | -0.013409 | -0.0053982 | -0.0021896 | 0.0023989 | -0.015716 | 0.21057 | 0.25635 | 0.21515 | 0.18768 | 0.3479 | 0.032043 | -0.13275 | 0.21973 | 0.27008 | 0.16022 | 0.25635 | 0.2243 | -0.059509 | -0.10986 | 122.8775 | 122.7127 | 0.16479 | 123.1018 | 123.0331 | 0.32043 | 0.027466 | 122.7859 | 122.7356 | 0.073243 | 123.0652 | 123.0057 | 0.27008 | 0.041199 | 123.1934 | 123.056 | 123.0606 | -0.31586 | 123.1018 | 123.0698 | 123.1155 | -0.29297
4227.8438 | 123.1201 | -122.8546 | 0.19684 | 0.1062 | 0.03215 | 0.0085022 | 0.0059729 | -0.010961 | 0.0020016 | -0.0077973 | 0.16304 | -0.012341 | -0.007748 | -0.0013352 | 0.0081667 | -0.017212 | 0.13733 | 0.091553 | 0.054932 | 0.059509 | 0.25177 | -0.068665 | -0.2243 | 0.10071 | 0.11444 | 0.013733 | 0.13733 | 0.10986 | -0.17395 | -0.20599 | 122.7859 | 122.6303 | 0.054932 | 122.9462 | 122.9141 | 0.28381 | -0.059509 | 122.6807 | 122.6486 | -0.059509 | 122.9553 | 122.8683 | 0.21973 | -0.086975 | 123.1064 | 122.9919 | 122.9095 | -0.42114 | 122.9919 | 122.9645 | 122.9691 | -0.40283
4229.5469 | 123.1018 | -122.8821 | 0.20599 | 0.045166 | 0.033218 | 0.0072204 | 0.0053321 | -0.011175 | 0.0024288 | -0.0052337 | 0.025711 | -0.011273 | -0.0058254 | 0.00080099 | 0.0073123 | -0.016998 | 0.027466 | -0.032043 | -0.086975 | -0.018311 | 0.28839 | -0.09613 | -0.24261 | -0.009155 | -0.018311 | -0.12817 | 0.21057 | 0.19226 | -0.20142 | -0.25635 | 122.7859 | 122.6395 | 0.082397 | 122.85 | 122.8638 | 0.2243 | -0.17853 | 122.6807 | 122.6257 | 0.004577 | 122.8729 | 122.7539 | 0.12817 | -0.013733 | 123.1705 | 122.9095 | 122.7951 | -0.44861 | 123.0927 | 123.0743 | 122.8638 | -0.46234
4231.2344 | 123.175 | -122.85 | 0.1831 | -0.24475 | 0.033432 | 0.0076478 | 0.010459 | -0.0079702 | -0.0024844 | -0.0077973 | -0.18028 | -0.013196 | -0.0039028 | -0.0021896 | 0.0034671 | -0.014648 | 0.15564 | 0.21515 | 0.13275 | 0.16479 | 0.39368 | 0.022888 | -0.1236 | 0.10529 | 0.16937 | 0.041199 | 0.30212 | 0.27466 | -0.09613 | -0.12817 | 122.8729 | 122.7264 | 0.21057 | 123.0652 | 123.0148 | 0.28839 | -0.027465 | 122.7539 | 122.7219 | 0.11902 | 122.9553 | 122.8912 | 0.16937 | 0.091553 | 123.2437 | 123.0057 | 122.9828 | -0.3067 | 123.1522 | 123.1247 | 123.0194 | -0.31128
4232.9531 | 123.1842 | -122.85 | 0.17853 | -0.23712 | 0.032364 | 0.0059388 | 0.010032 | -0.010534 | -0.0020572 | -0.0088653 | -0.19554 | -0.014905 | -0.0071072 | -0.0015488 | 0.0036807 | -0.016143 | 0.13733 | 0.18768 | 0.11902 | 0.14191 | 0.39368 | 0.018311 | -0.11902 | 0.068665 | 0.14648 | 0.004578 | 0.3067 | 0.2655 | -0.10986 | -0.15106 | 122.8683 | 122.731 | 0.21515 | 123.0377 | 122.9919 | 0.26093 | -0.041199 | 122.7402 | 122.699 | 0.12817 | 122.9187 | 122.8546 | 0.15564 | 0.086975 | 123.2437 | 122.9874 | 122.9691 | -0.29755 | 123.1567 | 123.1155 | 122.9965 | -0.32959
4234.6562 | 123.1979 | -122.8363 | 0.20142 | -0.22949 | 0.03215 | 0.0067932 | 0.0087499 | -0.0079702 | -0.0029118 | -0.0086517 | -0.29472 | -0.013409 | -0.0053982 | -0.0015488 | 0.0053897 | -0.017425 | 0.11902 | 0.14191 | 0.059509 | 0.11444 | 0.41657 | 0.027466 | -0.16022 | 0.07782 | 0.14191 | 0 | 0.31128 | 0.28839 | -0.091553 | -0.14191 | 122.8638 | 122.6761 | 0.21515 | 122.9782 | 122.9507 | 0.27466 | -0.082397 | 122.7448 | 122.6944 | 0.10986 | 122.9141 | 122.8363 | 0.14191 | 0.086975 | 123.2529 | 122.9553 | 122.8958 | -0.36163 | 123.1476 | 123.1247 | 122.9782 | -0.34332
4236.3594 | 123.23 | -122.8271 | 0.17853 | -0.19897 | 0.033646 | 0.0057252 | 0.010032 | -0.01267 | 0.0015744 | -0.0073701 | -0.2108 | -0.011914 | -0.004971 | -0.00026701 | 0.0043215 | -0.018921 | 0.10071 | 0.1236 | 0.041199 | 0.10071 | 0.39368 | 0 | -0.16022 | 0.068665 | 0.13275 | 0 | 0.27008 | 0.24261 | -0.11902 | -0.17853 | 122.8271 | 122.6669 | 0.21515 | 122.9507 | 122.9279 | 0.26093 | -0.07782 | 122.7081 | 122.6486 | 0.091553 | 122.8958 | 122.8271 | 0.17853 | 0.064087 | 123.2208 | 122.9279 | 122.8683 | -0.33874 | 123.0972 | 123.0698 | 122.9599 | -0.35706
4238.0625 | 123.1796 | -122.8271 | 0.17395 | -0.19135 | 0.031937 | 0.004657 | 0.0098181 | -0.0064748 | -0.0052616 | -0.0092927 | -0.11925 | -0.015759 | -0.0053982 | -0.0021896 | 0.0015445 | -0.01593 | 0.17853 | 0.27924 | 0.19226 | 0.1831 | 0.37537 | 0.045776 | -0.10071 | 0.16022 | 0.27466 | 0.12817 | 0.26093 | 0.23804 | -0.059509 | -0.10529 | 122.8729 | 122.7264 | 0.20142 | 123.1064 | 123.0103 | 0.28381 | 0.004578 | 122.7676 | 122.7219 | 0.086975 | 122.9874 | 122.9553 | 0.23346 | 0.064087 | 123.2025 | 123.0057 | 123.0194 | -0.27466 | 123.0881 | 123.0652 | 123.1018 | -0.27924
4239.75 | 123.1934 | -122.85 | 0.16937 | -0.19897 | 0.030655 | 0.004657 | 0.010032 | -0.011815 | -0.0046206 | -0.0092927 | -0.14214 | -0.015973 | -0.0045438 | -0.0017624 | 0.0017581 | -0.017639 | 0.20142 | 0.27466 | 0.20599 | 0.19684 | 0.37537 | 0.059509 | -0.10529 | 0.18768 | 0.28381 | 0.13275 | 0.25635 | 0.23346 | -0.059509 | -0.10529 | 122.9095 | 122.7448 | 0.20599 | 123.1247 | 123.0469 | 0.30212 | 0.032043 | 122.7905 | 122.7448 | 0.086975 | 123.0377 | 122.9828 | 0.23804 | 0.064086 | 123.2254 | 123.0515 | 123.056 | -0.27466 | 123.1064 | 123.0835 | 123.1338 | -0.27466
4241.4531 | 123.0881 | -122.8729 | 0.19684 | 0.15961 | 0.028732 | 0.0078614 | 0.0031957 | -0.0090384 | -0.0035526 | -0.0088653 | 0.086746 | -0.012127 | -0.007748 | -0.0017624 | 0.0032535 | -0.017212 | 0.086975 | 0.1236 | 0.054932 | 0.073242 | 0.25635 | -0.050354 | -0.19684 | 0.1236 | 0.16022 | 0.041199 | 0.21515 | 0.18768 | -0.1236 | -0.16937 | 122.8226 | 122.6761 | 0.05951 | 122.9965 | 122.9462 | 0.27008 | -0.10986 | 122.7493 | 122.7036 | 0.018311 | 122.9965 | 122.9141 | 0.21057 | -0.009155 | 123.1293 | 122.9599 | 122.9279 | -0.39368 | 123.0881 | 123.0606 | 123.0331 | -0.36621
4243.1406 | 123.1842 | -122.85 | 0.19226 | -0.099793 | 0.033859 | 0.0076478 | 0.0031957 | -0.010747 | 0.0026424 | -0.0092927 | -0.20317 | -0.0099911 | -0.0073208 | -0.00026701 | 0.0096621 | -0.017639 | 0.15106 | 0.11902 | 0.027466 | 0.09613 | 0.32959 | -0.041199 | -0.19684 | 0.07782 | 0.11902 | -0.041199 | 0.23346 | 0.19684 | -0.15106 | -0.21057 | 122.8088 | 122.6532 | 0.13733 | 122.9691 | 122.9462 | 0.29297 | -0.041199 | 122.699 | 122.6395 | 0.041198 | 122.9279 | 122.8088 | 0.16937 | 0.004577 | 123.1796 | 123.0011 | 122.8775 | -0.3891 | 123.0835 | 123.0469 | 122.9691 | -0.40283
4244.8594 | 123.143 | -122.8592 | 0.21515 | 0.1062 | 0.03685 | 0.0055114 | 0.0049047 | -0.011175 | 0.0028562 | -0.0060883 | 0.048599 | -0.0097775 | -0.009457 | -0.0021896 | 0.0079531 | -0.015289 | -0.004578 | -0.036621 | -0.086975 | -0.032043 | 0.2655 | -0.10071 | -0.28381 | 0.004578 | -0.004578 | -0.09613 | 0.20142 | 0.17395 | -0.20599 | -0.22888 | 122.7585 | 122.5754 | 0.050354 | 122.8226 | 122.8271 | 0.25177 | -0.21973 | 122.6532 | 122.6303 | -0.013733 | 122.8638 | 122.7631 | 0.13275 | -0.041199 | 123.1247 | 122.8546 | 122.7722 | -0.49896 | 123.0606 | 123.0331 | 122.8546 | -0.44403
4246.5469 | 123.0927 | -122.8775 | 0.20142 | -0.0082397 | 0.036636 | 0.006366 | 0.0061865 | -0.0069022 | 0.004565 | -0.0092927 | 0.03334 | -0.012341 | -0.0056118 | -0.00069421 | 0.0079531 | -0.015716 | 0.059509 | 0.036621 | -0.041199 | 0 | 0.29297 | -0.082397 | -0.23804 | -0.022888 | 0.013733 | -0.14191 | 0.21057 | 0.1831 | -0.19684 | -0.24261 | 122.7951 | 122.6395 | 0.091553 | 122.9141 | 122.8775 | 0.23804 | -0.14191 | 122.6807 | 122.6349 | 0.009155 | 122.8546 | 122.7356 | 0.10071 | -0.018311 | 123.1705 | 122.937 | 122.8363 | -0.43945 | 123.0881 | 123.0606 | 122.8912 | -0.44403
4248.2344 | 123.1705 | -122.8409 | 0.21515 | -0.099793 | 0.034073 | 0.0044434 | 0.0074683 | -0.0090384 | 0.0028562 | -0.0077973 | -0.14214 | -0.012341 | -0.0068936 | -0.0026168 | 0.0053897 | -0.017639 | 0.13275 | 0.11902 | 0.041199 | 0.09613 | 0.32044 | -0.045776 | -0.19684 | 0.086975 | 0.1236 | -0.036621 | 0.21973 | 0.19684 | -0.14648 | -0.1831 | 122.7951 | 122.644 | 0.10529 | 122.9599 | 122.937 | 0.29297 | -0.082398 | 122.6944 | 122.6578 | 0.004578 | 122.9279 | 122.8043 | 0.14648 | -0.018311 | 123.1613 | 122.9736 | 122.8821 | -0.41199 | 123.0606 | 123.0377 | 122.9645 | -0.39825
4249.9219 | 123.2071 | -122.8088 | 0.20142 | -0.031128 | 0.030014 | 0.0082886 | 0.0068273 | -0.009252 | -0.0073978 | -0.0082245 | -0.012436 | -0.015118 | -0.00668 | -0.0021896 | 0.0021853 | -0.015716 | 0.10986 | 0.17853 | 0.14191 | 0.13275 | 0.33875 | 0.018311 | -0.16022 | 0.16479 | 0.24719 | 0.15106 | 0.26093 | 0.2243 | -0.073242 | -0.10071 | 122.8271 | 122.6486 | 0.13733 | 122.9874 | 122.9416 | 0.29297 | -0.091553 | 122.7356 | 122.7081 | 0.059509 | 122.9736 | 122.9599 | 0.25177 | 0.022888 | 123.1476 | 122.9187 | 122.9507 | -0.36163 | 123.0698 | 123.0331 | 123.056 | -0.30212
4251.6094 | 123.111 | -122.8821 | 0.21515 | 0.029907 | 0.030441 | 0.0067932 | 0.0049047 | -0.01032 | -0.0046206 | -0.010788 | 0.071487 | -0.014264 | -0.0090298 | -0.0030442 | 0.0045351 | -0.016143 | 0.10071 | 0.11902 | 0.09613 | 0.082397 | 0.32501 | -0.013733 | -0.16937 | 0.091553 | 0.16479 | 0.07782 | 0.23346 | 0.21515 | -0.09613 | -0.13733 | 122.8683 | 122.7127 | 0.10986 | 123.0011 | 122.9645 | 0.25177 | -0.11444 | 122.7859 | 122.7448 | 0.01831 | 122.9736 | 122.9599 | 0.21515 | 0 | 123.2071 | 122.9828 | 122.9782 | -0.38452 | 123.1155 | 123.0972 | 123.0469 | -0.35248
4253.2969 | 123.0743 | -122.8638 | 0.21515 | 0.1825 | 0.031937 | 0.007434 | 0.0029821 | -0.0094656 | -0.00098918 | -0.0071563 | 0.15541 | -0.011914 | -0.0090298 | -0.0051804 | 0.0062441 | -0.014435 | 0.10071 | 0.10986 | 0.073242 | 0.064087 | 0.23804 | -0.086975 | -0.24719 | 0.10986 | 0.14648 | 0.045776 | 0.16479 | 0.14191 | -0.16937 | -0.19226 | 122.7768 | 122.6166 | 0.022888 | 122.9736 | 122.9279 | 0.31128 | -0.11444 | 122.6944 | 122.6715 | -0.050354 | 122.9736 | 122.9095 | 0.23804 | -0.073242 | 123.1018 | 122.9645 | 122.937 | -0.46234 | 123.0286 | 123.0057 | 123.0103 | -0.40741
4254.9844 | 123.1934 | -122.8409 | 0.17853 | -0.22949 | 0.030869 | 0.004657 | 0.0091773 | -0.0081838 | -0.00013458 | -0.0099335 | -0.27946 | -0.013623 | -0.0073208 | -0.00048061 | 0.0034671 | -0.016784 | 0.14648 | 0.11902 | 0.068665 | 0.1236 | 0.40741 | 0.027466 | -0.14191 | 0.073242 | 0.15106 | 0.018311 | 0.31128 | 0.30212 | -0.10529 | -0.13733 | 122.8683 | 122.699 | 0.22888 | 122.9599 | 122.9645 | 0.2655 | -0.032044 | 122.7356 | 122.7036 | 0.13275 | 122.9141 | 122.8592 | 0.15564 | 0.1236 | 123.2483 | 122.9874 | 122.9095 | -0.32044 | 123.1522 | 123.143 | 122.9919 | -0.31586
4256.7188 | 123.1064 | -122.8683 | 0.20599 | 0.15961 | 0.033005 | 0.0070068 | 0.0083227 | -0.0071158 | 0.00029262 | -0.0065155 | 0.1783 | -0.011273 | -0.007748 | -0.0013352 | 0.0043215 | -0.018707 | 0.086975 | 0.10071 | 0.050354 | 0.054932 | 0.21057 | -0.068665 | -0.23346 | 0.10529 | 0.11902 | 0.013733 | 0.14648 | 0.10986 | -0.1831 | -0.22888 | 122.7997 | 122.6349 | 0.004577 | 122.9691 | 122.9233 | 0.28839 | -0.11902 | 122.6852 | 122.6395 | -0.05951 | 122.9736 | 122.8821 | 0.24261 | -0.096131 | 123.0789 | 122.9553 | 122.9187 | -0.43945 | 123.0148 | 122.9782 | 122.9874 | -0.43488
4258.4062 | 123.1201 | -122.8775 | 0.20142 | 0.014648 | 0.02916 | 0.0059388 | 0.0070409 | -0.01032 | -0.002698 | -0.010361 | 0.071487 | -0.014905 | -0.0068936 | -0.0021896 | 0.0049625 | -0.014435 | 0.11444 | 0.11902 | 0.086975 | 0.10071 | 0.32501 | -0.009155 | -0.16479 | 0.11444 | 0.16022 | 0.082397 | 0.24719 | 0.2243 | -0.091553 | -0.16022 | 122.8683 | 122.7127 | 0.1236 | 122.9965 | 122.9782 | 0.2655 | -0.086975 | 122.7859 | 122.7173 | 0.045776 | 122.9919 | 122.9599 | 0.24261 | 0.022888 | 123.2025 | 122.9919 | 122.9645 | -0.36621 | 123.1247 | 123.1018 | 123.0377 | -0.36163
4260.125 | 123.1018 | -122.8821 | 0.21515 | -0.084534 | 0.034927 | 0.0050842 | 0.0038367 | -0.0088248 | 0.0049924 | -0.0084381 | -0.13451 | -0.011059 | -0.0073208 | -0.0015488 | 0.0092349 | -0.019561 | 0.14648 | 0.073242 | -0.009155 | 0.064087 | 0.33875 | -0.054932 | -0.21057 | 0.041199 | 0.041199 | -0.091553 | 0.21515 | 0.19226 | -0.16022 | -0.23346 | 122.8271 | 122.6715 | 0.1236 | 122.9553 | 122.9462 | 0.27466 | -0.068665 | 122.7219 | 122.6486 | 0 | 122.9233 | 122.7905 | 0.14191 | -0.022888 | 123.2208 | 123.0286 | 122.8729 | -0.42572 | 123.0972 | 123.0743 | 122.9233 | -0.44861
4261.8125 | 123.1842 | -122.8455 | 0.18768 | -0.10742 | 0.038345 | 0.006366 | 0.0091773 | -0.0064748 | 0.00029262 | -0.0069427 | -0.18028 | -0.012555 | -0.0043302 | -0.00069421 | 0.0043215 | -0.019348 | 0.12817 | 0.11444 | 0.027466 | 0.091553 | 0.3479 | -0.027466 | -0.21515 | 0.086975 | 0.11444 | -0.022888 | 0.20599 | 0.17853 | -0.15106 | -0.19684 | 122.818 | 122.6303 | 0.16022 | 122.9599 | 122.937 | 0.3067 | -0.059509 | 122.6944 | 122.6486 | 0.018311 | 122.9324 | 122.8226 | 0.17395 | -0.009155 | 123.1934 | 122.9736 | 122.8729 | -0.40283 | 123.0515 | 123.024 | 122.9599 | -0.38452
4263.5 | 123.0881 | -122.9004 | 0.19684 | 0.14435 | 0.032791 | 0.0085022 | 0.0074683 | -0.0077566 | -0.003339 | -0.0082245 | 0.14015 | -0.012341 | -0.0073208 | -0.0026168 | 0.0043215 | -0.015503 | 0.09613 | 0.11902 | 0.068665 | 0.059509 | 0.21973 | -0.064087 | -0.2243 | 0.09613 | 0.13275 | 0.032043 | 0.19226 | 0.15106 | -0.16479 | -0.19684 | 122.8363 | 122.6761 | 0.022889 | 123.0194 | 122.9599 | 0.28381 | -0.10071 | 122.7356 | 122.7036 | -0.004577 | 122.9965 | 122.9324 | 0.22888 | -0.045776 | 123.1201 | 122.9965 | 122.9691 | -0.42114 | 123.0927 | 123.0515 | 123.0331 | -0.39368
4265.1875 | 123.0972 | -122.8821 | 0.2243 | 0.090942 | 0.035996 | 0.0061524 | 0.0085363 | -0.008611 | 0.0028562 | -0.0058747 | 0.063858 | -0.010418 | -0.0064664 | -0.001976 | 0.0092349 | -0.016784 | 0.022888 | -0.045776 | -0.086975 | -0.018311 | 0.29297 | -0.10529 | -0.2655 | -0.027466 | -0.004578 | -0.1236 | 0.18768 | 0.16479 | -0.19226 | -0.24261 | 122.7768 | 122.6166 | 0.068665 | 122.8363 | 122.8638 | 0.24719 | -0.20142 | 122.6898 | 122.6395 | -0.036621 | 122.8546 | 122.7585 | 0.11902 | -0.059509 | 123.175 | 122.905 | 122.7951 | -0.48981 | 123.0698 | 123.0469 | 122.8775 | -0.46692
4266.9375 | 123.1934 | -122.8546 | 0.18768 | -0.015869 | 0.028946 | 0.0087158 | 0.010032 | -0.0088248 | -0.0069706 | -0.0082245 | 0.04097 | -0.013409 | -0.0053982 | -0.0038986 | 0.0013309 | -0.016784 | 0.091553 | 0.14191 | 0.11444 | 0.09613 | 0.32501 | -0.009155 | -0.17853 | 0.12817 | 0.20599 | 0.11444 | 0.24261 | 0.21057 | -0.086975 | -0.13733 | 122.8455 | 122.6761 | 0.13733 | 122.9965 | 122.9507 | 0.27466 | -0.09613 | 122.7676 | 122.7173 | 0.054932 | 122.9828 | 122.9691 | 0.25177 | 0.022888 | 123.1796 | 122.9462 | 122.9691 | -0.36621 | 123.0972 | 123.0652 | 123.0606 | -0.32501
4268.625 | 123.2162 | -122.8271 | 0.16937 | -0.046387 | 0.030014 | 0.0082886 | 0.010245 | -0.0090384 | -0.0071842 | -0.010361 | -0.058212 | -0.014691 | -0.0073208 | -0.0041122 | 4.9132e-05 | -0.014007 | 0.16022 | 0.20599 | 0.16479 | 0.16479 | 0.36163 | 0.045776 | -0.15106 | 0.17395 | 0.24719 | 0.16479 | 0.27008 | 0.21973 | -0.07782 | -0.10529 | 122.8729 | 122.6761 | 0.19226 | 123.0331 | 122.9919 | 0.31586 | -0.009156 | 122.7493 | 122.7219 | 0.10071 | 123.0011 | 122.9919 | 0.27008 | 0.050354 | 123.1888 | 122.9874 | 122.9919 | -0.32044 | 123.0972 | 123.0469 | 123.0743 | -0.27466
4270.3125 | 123.1796 | -122.8455 | 0.18768 | -0.00061023 | 0.028092 | 0.008075 | 0.0070409 | -0.011175 | -0.0059024 | -0.010788 | 0.048599 | -0.013409 | -0.0088162 | -0.0028306 | 0.0034671 | -0.016571 | 0.09613 | 0.14648 | 0.10071 | 0.10986 | 0.34332 | -0.022888 | -0.16937 | 0.10986 | 0.17853 | 0.082397 | 0.23804 | 0.19684 | -0.091553 | -0.16022 | 122.8226 | 122.6761 | 0.15564 | 122.9919 | 122.9553 | 0.27924 | -0.091553 | 122.7539 | 122.6852 | 0.050354 | 122.9553 | 122.9279 | 0.24261 | 0.009155 | 123.1888 | 122.9416 | 122.9462 | -0.35706 | 123.0835 | 123.0423 | 123.024 | -0.3479
4272 | 123.111 | -122.8821 | 0.21057 | 0.060425 | 0.027664 | 0.0067932 | 0.0059729 | -0.0096792 | -0.0014164 | -0.010574 | 0.079117 | -0.011914 | -0.0079618 | -0.0026168 | 0.0051761 | -0.015716 | 0.10986 | 0.11444 | 0.073242 | 0.082397 | 0.3067 | -0.027466 | -0.1831 | 0.12817 | 0.13275 | 0.073242 | 0.22888 | 0.1831 | -0.09613 | -0.16937 | 122.8546 | 122.699 | 0.096131 | 122.9965 | 122.9645 | 0.2655 | -0.10071 | 122.7859 | 122.7127 | 0.018311 | 123.0103 | 122.9553 | 0.24261 | -0.027466 | 123.1888 | 122.9919 | 122.9553 | -0.39368 | 123.111 | 123.0652 | 123.0148 | -0.37994
4273.7031 | 123.0881 | -122.8683 | 0.20142 | 0.17487 | 0.032578 | 0.0055114 | 0.0051183 | -0.0073294 | -0.00056178 | -0.0084381 | 0.15541 | -0.011487 | -0.0086026 | -0.003685 | 0.0079531 | -0.018493 | 0.12817 | 0.086975 | 0.050354 | 0.054932 | 0.21973 | -0.068665 | -0.22888 | 0.10529 | 0.13275 | 0.018311 | 0.15106 | 0.1236 | -0.16022 | -0.20142 | 122.7997 | 122.6395 | 0.018311 | 122.9553 | 122.9233 | 0.28381 | -0.073242 | 122.7081 | 122.6669 | -0.050354 | 122.9736 | 122.8867 | 0.21973 | -0.07782 | 123.0881 | 122.9965 | 122.9187 | -0.4303 | 123.0194 | 122.9919 | 123.0011 | -0.40283
4275.3906 | 123.1338 | -122.8592 | 0.19684 | 0.16724 | 0.035568 | 0.0087158 | 0.0066137 | -0.0088248 | 0.00093342 | -0.0073701 | 0.14015 | -0.011914 | -0.0090298 | -0.0028306 | 0.0094485 | -0.019134 | 0.13733 | 0.10529 | 0.054932 | 0.082397 | 0.22888 | -0.045776 | -0.21057 | 0.09613 | 0.1236 | -0.013733 | 0.16022 | 0.11902 | -0.16479 | -0.19684 | 122.8134 | 122.6486 | 0.032044 | 122.9645 | 122.9416 | 0.29297 | -0.059509 | 122.6944 | 122.6624 | -0.036621 | 122.9553 | 122.8455 | 0.18311 | -0.077819 | 123.0881 | 122.9965 | 122.9141 | -0.40741 | 123.0194 | 122.9782 | 122.9828 | -0.39368
4277.0938 | 123.0881 | -122.8592 | 0.2243 | 0.13672 | 0.032364 | 0.0076478 | 0.0059729 | -0.0073294 | 7.902e-05 | -0.0067291 | 0.14015 | -0.013409 | -0.007748 | -0.0030442 | 0.0043215 | -0.017425 | 0.1236 | 0.11902 | 0.07782 | 0.064087 | 0.2243 | -0.041199 | -0.21515 | 0.12817 | 0.13275 | 0.022888 | 0.18768 | 0.15564 | -0.15564 | -0.19684 | 122.818 | 122.644 | 0 | 122.9782 | 122.9233 | 0.27924 | -0.10071 | 122.7036 | 122.6624 | -0.036621 | 122.9874 | 122.8821 | 0.21973 | -0.068664 | 123.0835 | 122.9828 | 122.937 | -0.43945 | 123.0469 | 123.0148 | 122.9919 | -0.42114
4278.7812 | 123.0698 | -122.8775 | 0.21515 | 0.16724 | 0.030655 | 0.0085022 | 0.0031957 | -0.0069022 | -0.0031254 | -0.0067291 | 0.11726 | -0.010632 | -0.0092434 | -0.0013352 | 0.0060305 | -0.017639 | 0.10986 | 0.11444 | 0.054932 | 0.064087 | 0.23804 | -0.073242 | -0.2243 | 0.11902 | 0.14191 | 0.027466 | 0.17395 | 0.14191 | -0.14648 | -0.1831 | 122.8043 | 122.6532 | 0.022888 | 122.9919 | 122.9416 | 0.28839 | -0.10529 | 122.731 | 122.6944 | -0.041199 | 122.9965 | 122.905 | 0.21057 | -0.073242 | 123.1155 | 122.9874 | 122.9324 | -0.43945 | 123.0515 | 123.0194 | 123.0194 | -0.39825
4280.4688 | 123.0835 | -122.8683 | 0.22888 | 0.12146 | 0.030441 | 0.007434 | 0.0055457 | -0.01032 | -0.002698 | -0.0088653 | 0.14015 | -0.01405 | -0.0079618 | -0.0030442 | 0.0045351 | -0.015503 | 0.11444 | 0.10529 | 0.064087 | 0.064087 | 0.2655 | -0.054932 | -0.2243 | 0.1236 | 0.14648 | 0.045776 | 0.19226 | 0.1831 | -0.11902 | -0.15106 | 122.8134 | 122.644 | 0.036621 | 122.9736 | 122.9324 | 0.28839 | -0.11444 | 122.7493 | 122.7173 | -0.036621 | 122.9919 | 122.9141 | 0.19684 | -0.045777 | 123.1338 | 122.9828 | 122.9324 | -0.45319 | 123.0606 | 123.0515 | 123.0148 | -0.37994
4282.1562 | 123.1018 | -122.8912 | 0.2243 | -0.054016 | 0.037064 | 0.0059388 | 0.0053321 | -0.007543 | 0.0043514 | -0.0080109 | -0.12688 | -0.0095639 | -0.0062528 | -0.0021896 | 0.0088077 | -0.017212 | 0.15564 | 0.050354 | -0.027466 | 0.032043 | 0.31586 | -0.059509 | -0.23804 | 0.032043 | 0.036621 | -0.11902 | 0.21515 | 0.1831 | -0.17395 | -0.23346 | 122.8317 | 122.6532 | 0.091553 | 122.9416 | 122.9233 | 0.27008 | -0.068664 | 122.7173 | 122.6578 | -0.009155 | 122.9233 | 122.7722 | 0.11444 | -0.041199 | 123.2071 | 123.0469 | 122.8638 | -0.46234 | 123.1064 | 123.0743 | 122.9279 | -0.45776
4283.8438 | 123.0789 | -122.8867 | 0.21057 | 0.12909 | 0.033218 | 0.0052978 | 0.0074683 | -0.010106 | -0.0037662 | -0.0073701 | 0.14015 | -0.013196 | -0.007748 | -0.00090781 | 0.0045351 | -0.014221 | 0.11444 | 0.11444 | 0.073242 | 0.064087 | 0.22888 | -0.036621 | -0.21973 | 0.1236 | 0.14648 | 0.045776 | 0.20599 | 0.16022 | -0.13275 | -0.17395 | 122.85 | 122.6669 | 0.018311 | 123.0011 | 122.9507 | 0.28381 | -0.09613 | 122.7539 | 122.7127 | -0.004577 | 123.0103 | 122.9324 | 0.21973 | -0.050354 | 123.1155 | 123.0011 | 122.9599 | -0.4303 | 123.0927 | 123.0469 | 123.0331 | -0.38452
4285.7188 | 123.1384 | -122.8409 | 0.20142 | 0.12146 | 0.034073 | 0.0061524 | 0.0089635 | -0.0088248 | 0.0032834 | -0.0077973 | 0.071487 | -0.010418 | -0.0047574 | -0.0013352 | 0.0058169 | -0.017852 | 0.068665 | -0.045776 | -0.059509 | -0.009155 | 0.29755 | -0.10071 | -0.25635 | 0.036621 | 0.013733 | -0.086975 | 0.20599 | 0.16479 | -0.19226 | -0.2243 | 122.7402 | 122.5845 | 0.09613 | 122.7951 | 122.8317 | 0.24719 | -0.13275 | 122.6486 | 122.6166 | 0.004578 | 122.8775 | 122.7539 | 0.13733 | -0.036621 | 123.1384 | 122.9095 | 122.7814 | -0.45776 | 123.0469 | 123.0057 | 122.8546 | -0.42572
4287.6562 | 123.2117 | -122.8363 | 0.17853 | -0.24475 | 0.034287 | 0.0078614 | 0.0091773 | -0.0096792 | 0.00050622 | -0.0092927 | -0.28709 | -0.012555 | -0.0071072 | -0.0015488 | 0.0021853 | -0.016998 | 0.15106 | 0.12817 | 0.07782 | 0.11444 | 0.42114 | 0.018311 | -0.16022 | 0.073242 | 0.13275 | -0.022888 | 0.31128 | 0.29297 | -0.11902 | -0.14648 | 122.8546 | 122.6761 | 0.24261 | 122.9645 | 122.9507 | 0.27466 | -0.027466 | 122.7173 | 122.6898 | 0.13275 | 122.9095 | 122.8134 | 0.1236 | 0.11444 | 123.2574 | 122.9874 | 122.9141 | -0.33874 | 123.1476 | 123.1293 | 122.9691 | -0.32501
4289.625 | 123.1247 | -122.8821 | 0.20142 | -0.069275 | 0.036636 | 0.004657 | 0.0064001 | -0.0079702 | 0.004565 | -0.0069427 | -0.12688 | -0.013409 | -0.0064664 | -0.00090781 | 0.0079531 | -0.017852 | 0.13275 | 0.086975 | 0.013733 | 0.064087 | 0.32044 | -0.054932 | -0.20599 | 0.068665 | 0.086975 | -0.064087 | 0.23804 | 0.20142 | -0.14648 | -0.21057 | 122.8271 | 122.6761 | 0.11902 | 122.9691 | 122.9462 | 0.27008 | -0.068665 | 122.7356 | 122.6715 | 0.036621 | 122.9507 | 122.818 | 0.14648 | 0 | 123.2025 | 123.0148 | 122.8958 | -0.40741 | 123.1201 | 123.0835 | 122.9691 | -0.41199
4291.75 | 123.2346 | -122.8409 | 0.1831 | -0.13031 | 0.033005 | 0.0057252 | 0.0085363 | -0.0079702 | 0.0013608 | -0.0082245 | -0.14977 | -0.011273 | -0.0039028 | -0.0011216 | 0.0075259 | -0.019775 | 0.1236 | 0.10071 | 0.041199 | 0.10071 | 0.32959 | -0.032043 | -0.21515 | 0.064087 | 0.11902 | -0.041199 | 0.22888 | 0.20142 | -0.13275 | -0.18768 | 122.8088 | 122.6257 | 0.14649 | 122.9416 | 122.9416 | 0.31586 | -0.059509 | 122.7081 | 122.6532 | 0.045777 | 122.905 | 122.7997 | 0.14648 | 0.018311 | 123.1705 | 122.9645 | 122.8821 | -0.39825 | 123.0698 | 123.0423 | 122.9599 | -0.37079
4293.5781 | 123.0835 | -122.8867 | 0.20599 | -0.00061023 | 0.034714 | 0.004657 | 0.0066137 | -0.01032 | 0.0024288 | -0.0045929 | 0.048599 | -0.010846 | -0.0073208 | -0.00026701 | 0.0066715 | -0.017425 | 0.064087 | 0.018311 | -0.041199 | 0.018311 | 0.29755 | -0.086975 | -0.25177 | -0.013733 | 0.018311 | -0.13275 | 0.21973 | 0.17395 | -0.19226 | -0.21973 | 122.7997 | 122.6349 | 0.091552 | 122.905 | 122.905 | 0.27008 | -0.14191 | 122.6944 | 122.6669 | 0.013733 | 122.8729 | 122.7539 | 0.086976 | -0.032044 | 123.1842 | 122.9507 | 122.8455 | -0.45776 | 123.1064 | 123.0606 | 122.905 | -0.42572
4296.4688 | 123.1842 | -122.8409 | 0.18768 | -0.16846 | 0.031937 | 0.0065796 | 0.0098181 | -0.0088248 | -0.0071842 | -0.0086517 | -0.18791 | -0.013196 | -0.0073208 | -0.0041122 | 0.00090353 | -0.015716 | 0.19226 | 0.23346 | 0.1831 | 0.18768 | 0.35248 | 0.041199 | -0.11902 | 0.12817 | 0.24261 | 0.09613 | 0.27466 | 0.27008 | -0.07782 | -0.12817 | 122.8821 | 122.7219 | 0.1648 | 123.0743 | 123.0286 | 0.3067 | 0.004578 | 122.7631 | 122.7127 | 0.086975 | 122.9691 | 122.937 | 0.2243 | 0.082398 | 123.1934 | 123.0331 | 123.024 | -0.3067 | 123.1155 | 123.111 | 123.0835 | -0.31586
4298.5781 | 123.1384 | -122.8775 | 0.20599 | -0.015869 | 0.028732 | 0.0087158 | 0.0044775 | -0.0081838 | -0.0073978 | -0.010361 | 0.048599 | -0.014905 | -0.0073208 | -0.0028306 | 0.0021853 | -0.016784 | 0.091553 | 0.14191 | 0.10071 | 0.10071 | 0.32501 | -0.009155 | -0.1831 | 0.10529 | 0.17395 | 0.09613 | 0.25635 | 0.21057 | -0.086975 | -0.13733 | 122.8683 | 122.6944 | 0.11902 | 123.0194 | 122.9782 | 0.28381 | -0.11444 | 122.7905 | 122.7402 | 0.050354 | 122.9828 | 122.9736 | 0.23346 | 0.004577 | 123.2025 | 122.9691 | 122.9782 | -0.3891 | 123.1339 | 123.0881 | 123.0515 | -0.34332
4300.2656 | 123.2346 | -122.8317 | 0.1831 | -0.12268 | 0.028305 | 0.0070068 | 0.0091773 | -0.0079702 | -0.0046206 | -0.0097199 | -0.08873 | -0.013409 | -0.006039 | -0.0032578 | 0.0013309 | -0.016571 | 0.19684 | 0.24719 | 0.19684 | 0.1831 | 0.35706 | 0.036621 | -0.11902 | 0.21515 | 0.3067 | 0.16479 | 0.26093 | 0.24261 | -0.064087 | -0.11902 | 122.8683 | 122.7127 | 0.17395 | 123.0789 | 123.0148 | 0.30212 | 0.013733 | 122.7676 | 122.7127 | 0.07782 | 123.0469 | 122.9965 | 0.28381 | 0.05951 | 123.1888 | 123.0286 | 123.0286 | -0.30212 | 123.0927 | 123.0743 | 123.1384 | -0.30212
4301.9531 | 123.2162 | -122.7951 | 0.1831 | -0.1532 | 0.030655 | 0.004657 | 0.0087499 | -0.0081838 | -0.002698 | -0.0099335 | -0.16502 | -0.014691 | -0.0073208 | -0.0045394 | 4.9132e-05 | -0.01828 | 0.2243 | 0.28839 | 0.21515 | 0.20142 | 0.35706 | 0.045776 | -0.1236 | 0.20142 | 0.28381 | 0.15564 | 0.27924 | 0.21515 | -0.045776 | -0.11444 | 122.8409 | 122.6715 | 0.17395 | 123.0835 | 122.9965 | 0.32501 | 0.041199 | 122.7493 | 122.6807 | 0.096131 | 122.9965 | 122.9507 | 0.27008 | 0.032044 | 123.1522 | 123.0194 | 123.0103 | -0.3067 | 123.0743 | 123.0103 | 123.0789 | -0.29755
4303.6406 | 123.2071 | -122.8409 | 0.17853 | -0.069275 | 0.0298 | 0.0085022 | 0.0083227 | -0.012029 | -0.0054752 | -0.0097199 | -0.050583 | -0.015332 | -0.0053982 | -0.0026168 | 0.0023989 | -0.017425 | 0.16022 | 0.19684 | 0.15564 | 0.16022 | 0.33417 | 0.027466 | -0.13275 | 0.1831 | 0.23804 | 0.14648 | 0.26093 | 0.21057 | -0.050354 | -0.09613 | 122.8683 | 122.7081 | 0.15564 | 123.0377 | 123.0011 | 0.29297 | -0.018311 | 122.7905 | 122.7448 | 0.082397 | 123.024 | 122.9874 | 0.24261 | 0.032043 | 123.175 | 123.0011 | 122.9965 | -0.31128 | 123.1018 | 123.0515 | 123.0789 | -0.27466
4305.3281 | 123.1247 | -122.8592 | 0.21515 | 0.037537 | 0.028092 | 0.0093566 | 0.0053321 | -0.0098928 | -0.0039798 | -0.010147 | 0.025711 | -0.013196 | -0.0079618 | -0.0024032 | 0.0045351 | -0.015503 | 0.12817 | 0.10986 | 0.10071 | 0.10071 | 0.31128 | 0.009155 | -0.16479 | 0.10071 | 0.15564 | 0.064087 | 0.24261 | 0.20142 | -0.09613 | -0.15564 | 122.8683 | 122.6944 | 0.09613 | 122.9691 | 122.9599 | 0.2655 | -0.086975 | 122.7631 | 122.7036 | 0.027466 | 122.9599 | 122.9233 | 0.21973 | -0.013733 | 123.1705 | 122.9874 | 122.9599 | -0.37994 | 123.1018 | 123.0606 | 123.0148 | -0.37079
4307.0312 | 123.1338 | -122.8638 | 0.21973 | -0.099793 | 0.035355 | 0.0065796 | 0.0066137 | -0.009252 | 0.0028562 | -0.0084381 | -0.18028 | -0.011487 | -0.0058254 | -0.0021896 | 0.0079531 | -0.019775 | 0.17395 | 0.091553 | 0.004578 | 0.064087 | 0.31128 | -0.041199 | -0.2243 | 0.07782 | 0.091553 | -0.07782 | 0.23346 | 0.19684 | -0.15564 | -0.21515 | 122.8226 | 122.6395 | 0.091552 | 122.9553 | 122.9279 | 0.28839 | -0.045777 | 122.7081 | 122.6486 | 0.013732 | 122.9416 | 122.7859 | 0.13733 | -0.022889 | 123.175 | 123.0377 | 122.8683 | -0.44403 | 123.0972 | 123.0606 | 122.9553 | -0.43488
4308.7188 | 123.1064 | -122.8729 | 0.21973 | -0.038757 | 0.033646 | 0.0059388 | 0.0055457 | -0.0071158 | 0.0032834 | -0.0075837 | -0.050583 | -0.011914 | -0.0036892 | -0.0015488 | 0.010303 | -0.018921 | 0.11444 | 0.059509 | -0.032043 | 0.032043 | 0.30212 | -0.07782 | -0.23804 | 0.022888 | 0.018311 | -0.11902 | 0.21057 | 0.16937 | -0.19226 | -0.23346 | 122.7951 | 122.6349 | 0.082397 | 122.9324 | 122.905 | 0.27008 | -0.10529 | 122.6807 | 122.6395 | -0.009156 | 122.8958 | 122.7539 | 0.11444 | -0.050354 | 123.175 | 122.9874 | 122.8409 | -0.45776 | 123.0835 | 123.0423 | 122.8912 | -0.45319
4310.4219 | 123.0881 | -122.8775 | 0.18768 | 0.15961 | 0.031937 | 0.0089294 | 0.0044775 | -0.010534 | -0.0052616 | -0.0071563 | 0.14778 | -0.014264 | -0.00668 | -0.0045394 | 0.0045351 | -0.016357 | 0.10071 | 0.12817 | 0.07782 | 0.054932 | 0.21515 | -0.054932 | -0.22888 | 0.10986 | 0.15106 | 0.036621 | 0.16022 | 0.13275 | -0.15564 | -0.17853 | 122.8226 | 122.6486 | 0.027466 | 123.0057 | 122.9324 | 0.28381 | -0.086975 | 122.7219 | 122.699 | -0.027466 | 122.9874 | 122.9141 | 0.21515 | -0.054932 | 123.0927 | 122.9782 | 122.9553 | -0.41656 | 123.0377 | 123.0103 | 123.0286 | -0.36621
4312.125 | 123.1522 | -122.8683 | 0.21057 | 0.17487 | 0.033432 | 0.0052978 | 0.0072547 | -0.0096792 | -0.00013458 | -0.0090791 | 0.12489 | -0.012555 | -0.0062528 | -0.00048061 | 0.0068851 | -0.016998 | 0.050354 | 0.018311 | -0.018311 | 0.009155 | 0.25635 | -0.07782 | -0.24719 | 0.082397 | 0.10986 | -0.018311 | 0.17395 | 0.14648 | -0.16022 | -0.21515 | 122.7905 | 122.6212 | 0.045777 | 122.8867 | 122.8775 | 0.25635 | -0.16022 | 122.7081 | 122.6532 | -0.036621 | 122.9507 | 122.85 | 0.19684 | -0.064087 | 123.1247 | 122.9187 | 122.85 | -0.45776 | 123.0423 | 123.0148 | 122.9782 | -0.42572
4313.8125 | 123.1064 | -122.8821 | 0.21515 | 0.022278 | 0.0345 | 0.0057252 | 0.0057593 | -0.010534 | 0.0041378 | -0.0077973 | 0.048599 | -0.011059 | -0.006039 | -0.0013352 | 0.0075259 | -0.016143 | 0 | -0.059509 | -0.091553 | -0.022888 | 0.28381 | -0.086975 | -0.27008 | -0.004578 | -0.004578 | -0.13275 | 0.20142 | 0.16937 | -0.20599 | -0.24261 | 122.7951 | 122.612 | 0.068664 | 122.8226 | 122.8592 | 0.24719 | -0.21515 | 122.6761 | 122.6395 | -0.013733 | 122.8775 | 122.7493 | 0.10986 | -0.045776 | 123.1659 | 122.8821 | 122.7905 | -0.48523 | 123.0835 | 123.0515 | 122.8775 | -0.45776
4315.5156 | 123.1201 | -122.8775 | 0.2243 | 0.083313 | 0.034073 | 0.0057252 | 0.0044775 | -0.0096792 | 7.902e-05 | -0.0058747 | 0.063858 | -0.010846 | -0.00668 | -0.00090781 | 0.0079531 | -0.017212 | 0 | -0.027466 | -0.082397 | -0.022888 | 0.29297 | -0.11444 | -0.27008 | 0 | -0.013733 | -0.11902 | 0.20599 | 0.16479 | -0.18768 | -0.24719 | 122.7631 | 122.6074 | 0.068665 | 122.85 | 122.8546 | 0.24719 | -0.2243 | 122.6898 | 122.6303 | -0.01831 | 122.8775 | 122.7585 | 0.12817 | -0.059509 | 123.1705 | 122.8775 | 122.7951 | -0.49439 | 123.0835 | 123.0423 | 122.8638 | -0.4715
4317.2031 | 123.0927 | -122.8821 | 0.19684 | 0.075684 | 0.037918 | 0.0033752 | 0.011314 | -0.0096792 | 0.0028562 | -0.0088653 | 0.071487 | -0.0117 | -0.0043302 | -0.0013352 | 0.0058169 | -0.016998 | -0.022888 | -0.032043 | -0.09613 | -0.036621 | 0.28381 | -0.09613 | -0.2655 | -0.022888 | -0.009155 | -0.11902 | 0.21973 | 0.16937 | -0.21057 | -0.25177 | 122.7859 | 122.6166 | 0.086975 | 122.85 | 122.8455 | 0.22888 | -0.21973 | 122.6715 | 122.6303 | 0.022889 | 122.8592 | 122.7631 | 0.13275 | -0.027465 | 123.1659 | 122.8592 | 122.7859 | -0.46234 | 123.1018 | 123.0515 | 122.8729 | -0.44861
4318.8906 | 123.0835 | -122.8683 | 0.2243 | 0.090942 | 0.0298 | 0.0078614 | 0.0081091 | -0.0079702 | -0.0046206 | -0.0086517 | 0.12489 | -0.014264 | -0.0090298 | -0.0030442 | 0.0019717 | -0.015075 | 0.059509 | 0.15106 | 0.073242 | 0.082397 | 0.28839 | -0.036621 | -0.18768 | 0.10529 | 0.17395 | 0.041199 | 0.21515 | 0.18768 | -0.13733 | -0.17395 | 122.8317 | 122.6807 | 0.064087 | 123.0194 | 122.9507 | 0.27008 | -0.16479 | 122.731 | 122.6944 | -0.009155 | 122.9736 | 122.9095 | 0.21515 | -0.036621 | 123.1567 | 122.9279 | 122.9416 | -0.41199 | 123.0835 | 123.056 | 123.0423 | -0.39825
4320.5781 | 123.1201 | -122.8638 | 0.21515 | 0.022278 | 0.029587 | 0.0076478 | 0.0070409 | -0.0094656 | -0.006757 | -0.010361 | 0.102 | -0.015545 | -0.010098 | -0.0017624 | 0.0043215 | -0.016143 | 0.07782 | 0.1236 | 0.091553 | 0.10071 | 0.31586 | -0.013733 | -0.1831 | 0.091553 | 0.16022 | 0.073242 | 0.25177 | 0.20599 | -0.091553 | -0.14648 | 122.85 | 122.6807 | 0.10071 | 122.9874 | 122.9645 | 0.28381 | -0.13733 | 122.7722 | 122.7173 | 0.036621 | 122.9553 | 122.937 | 0.21973 | -0.009155 | 123.1796 | 122.9416 | 122.9553 | -0.39825 | 123.1155 | 123.0698 | 123.024 | -0.36163
4322.2656 | 123.111 | -122.8867 | 0.20599 | 0.14435 | 0.032791 | 0.0050842 | 0.0055457 | -0.010961 | 0.00050622 | -0.0097199 | 0.18593 | -0.011487 | -0.0062528 | -0.0043258 | 0.0070987 | -0.020416 | 0.10986 | 0.091553 | 0.041199 | 0.059509 | 0.23804 | -0.059509 | -0.23346 | 0.082397 | 0.10986 | 0.013733 | 0.15106 | 0.10071 | -0.16937 | -0.19684 | 122.8271 | 122.6532 | 0.032043 | 122.9782 | 122.9462 | 0.29297 | -0.096131 | 122.7173 | 122.6898 | -0.054932 | 122.9691 | 122.9004 | 0.21057 | -0.10529 | 123.1247 | 122.9965 | 122.9279 | -0.43945 | 123.0377 | 122.9874 | 122.9965 | -0.40283
4323.9688 | 123.1842 | -122.8271 | 0.18768 | -0.17609 | 0.031296 | 0.0050842 | 0.0098181 | -0.0096792 | -0.0048344 | -0.0088653 | -0.13451 | -0.016186 | -0.0058254 | -0.0021896 | 0.0023989 | -0.018707 | 0.21057 | 0.27008 | 0.21057 | 0.20142 | 0.36163 | 0.050354 | -0.11444 | 0.1831 | 0.27924 | 0.11902 | 0.27008 | 0.2243 | -0.054932 | -0.091553 | 122.8775 | 122.7127 | 0.17395 | 123.0972 | 123.0286 | 0.31586 | 0.022888 | 122.7722 | 122.7356 | 0.082398 | 123.0103 | 122.9462 | 0.21057 | 0.036621 | 123.1888 | 123.0377 | 123.0377 | -0.30212 | 123.0972 | 123.0515 | 123.1064 | -0.27924
4325.6719 | 123.1979 | -122.8317 | 0.20599 | -0.19135 | 0.033646 | 0.0085022 | 0.010245 | -0.0077566 | -0.00077538 | -0.0069427 | -0.26421 | -0.014905 | -0.0051846 | -0.001976 | 0.0017581 | -0.017212 | 0.13733 | 0.15564 | 0.068665 | 0.11444 | 0.40741 | 0.013733 | -0.14191 | 0.082397 | 0.14191 | 0.013733 | 0.31128 | 0.28381 | -0.09613 | -0.1236 | 122.8455 | 122.6898 | 0.20142 | 122.9874 | 122.9462 | 0.25635 | -0.068665 | 122.7356 | 122.7081 | 0.10528 | 122.9141 | 122.8455 | 0.13733 | 0.077819 | 123.2391 | 122.9691 | 122.9004 | -0.3479 | 123.143 | 123.1155 | 122.9736 | -0.32959
4327.375 | 123.1705 | -122.85 | 0.18768 | -0.25238 | 0.031937 | 0.0061524 | 0.0081091 | -0.009252 | -0.0018436 | -0.010147 | -0.24895 | -0.012555 | -0.0047574 | -5.3406e-05 | 0.0038943 | -0.016784 | 0.1831 | 0.21515 | 0.14648 | 0.17853 | 0.40283 | 0.027466 | -0.13275 | 0.1236 | 0.19226 | 0.041199 | 0.3067 | 0.27924 | -0.09613 | -0.12817 | 122.8775 | 122.7173 | 0.21515 | 123.0652 | 123.0286 | 0.31128 | -0.004578 | 122.7539 | 122.7219 | 0.11902 | 122.9736 | 122.8912 | 0.16937 | 0.091553 | 123.2529 | 123.0331 | 122.9965 | -0.32043 | 123.1567 | 123.1293 | 123.0423 | -0.31586
4329.0625 | 123.1293 | -122.8912 | 0.21515 | 0.1062 | 0.035568 | 0.0065796 | 0.0040503 | -0.0098928 | 0.0041378 | -0.0060883 | 0.063858 | -0.010632 | -0.0088162 | -0.00069421 | 0.0090213 | -0.018921 | 0.018311 | -0.032043 | -0.07782 | -0.013733 | 0.28839 | -0.10071 | -0.27466 | -0.004578 | -0.009155 | -0.11444 | 0.20142 | 0.16937 | -0.19684 | -0.24719 | 122.7905 | 122.6166 | 0.073242 | 122.8592 | 122.8775 | 0.26093 | -0.19684 | 122.6944 | 122.644 | -0.013733 | 122.8867 | 122.7768 | 0.13275 | -0.045776 | 123.1796 | 122.9095 | 122.8134 | -0.48981 | 123.0927 | 123.0606 | 122.8821 | -0.46234
4330.7812 | 123.0927 | -122.8867 | 0.2243 | -0.038757 | 0.034073 | 0.0050842 | 0.0040503 | -0.008611 | 0.0032834 | -0.0065155 | -0.065842 | -0.0117 | -0.008389 | -0.00090781 | 0.0088077 | -0.017425 | 0.091553 | 0.082397 | -0.022888 | 0.045776 | 0.31128 | -0.068665 | -0.22888 | 0.032043 | 0.054932 | -0.11444 | 0.21057 | 0.1831 | -0.19226 | -0.23804 | 122.818 | 122.6578 | 0.086975 | 122.9691 | 122.9324 | 0.27466 | -0.13275 | 122.6944 | 122.6486 | -0.013733 | 122.9187 | 122.7722 | 0.1236 | -0.041199 | 123.1979 | 122.9782 | 122.8638 | -0.45319 | 123.0972 | 123.0698 | 122.9416 | -0.46234
4332.5312 | 123.0972 | -122.8821 | 0.21057 | 0.15198 | 0.031723 | 0.0061524 | 0.0074683 | -0.011175 | -0.006116 | -0.0067291 | 0.11726 | -0.014264 | -0.0051846 | -0.0028306 | 0.0015445 | -0.014648 | 0.068665 | 0.1236 | 0.082397 | 0.07782 | 0.2655 | -0.064087 | -0.20599 | 0.10071 | 0.16479 | 0.054932 | 0.21515 | 0.17853 | -0.091553 | -0.14648 | 122.818 | 122.6761 | 0.054932 | 123.0057 | 122.9599 | 0.28381 | -0.14191 | 122.7905 | 122.7356 | 0.004578 | 122.9828 | 122.937 | 0.20142 | -0.032043 | 123.1476 | 122.9507 | 122.9645 | -0.41657 | 123.0972 | 123.0606 | 123.0469 | -0.35706
4334.2188 | 123.1018 | -122.8867 | 0.19684 | 0.1825 | 0.03215 | 0.0040162 | 0.0051183 | -0.01032 | -0.0014164 | -0.0069427 | 0.17067 | -0.011914 | -0.007748 | -0.0013352 | 0.0077395 | -0.016571 | 0.09613 | 0.10529 | 0.036621 | 0.041199 | 0.20599 | -0.086975 | -0.23346 | 0.10529 | 0.14648 | 0.036621 | 0.13733 | 0.1236 | -0.16022 | -0.19226 | 122.7997 | 122.6532 | 0.009156 | 122.9919 | 122.9279 | 0.27466 | -0.10071 | 122.7264 | 122.6944 | -0.059509 | 122.9919 | 122.9233 | 0.22888 | -0.073242 | 123.0927 | 122.9828 | 122.9233 | -0.4303 | 123.024 | 123.0103 | 123.0331 | -0.3891
4335.9688 | 123.111 | -122.9095 | 0.23804 | -0.069275 | 0.035141 | 0.0057252 | 0.0076819 | -0.0094656 | 0.001788 | -0.0069427 | -0.073471 | -0.011914 | -0.0071072 | -0.0030442 | 0.0083805 | -0.018066 | 0.1236 | 0.07782 | -0.018311 | 0.054932 | 0.31586 | -0.054932 | -0.21973 | 0.041199 | 0.064087 | -0.09613 | 0.2243 | 0.1831 | -0.16937 | -0.20599 | 122.8546 | 122.6898 | 0.07782 | 122.9874 | 122.9645 | 0.27466 | -0.11444 | 122.7402 | 122.7036 | -0.013733 | 122.9507 | 122.8134 | 0.10986 | -0.054932 | 123.2254 | 123.0331 | 122.8912 | -0.45776 | 123.1339 | 123.0927 | 122.9736 | -0.44403
4337.6562 | 123.2391 | -122.8409 | 0.16937 | -0.22949 | 0.031937 | 0.0082886 | 0.0091773 | -0.008611 | 0.00029262 | -0.0086517 | -0.2108 | -0.010846 | -0.0058254 | -0.0013352 | 0.0053897 | -0.014221 | 0.10529 | 0.10986 | 0.068665 | 0.10986 | 0.4303 | 0.027466 | -0.15106 | 0.054932 | 0.13275 | -0.004578 | 0.3067 | 0.25177 | -0.1236 | -0.16022 | 122.8683 | 122.6898 | 0.26093 | 122.9507 | 122.9507 | 0.26093 | -0.064087 | 122.7173 | 122.6807 | 0.13733 | 122.8958 | 122.8363 | 0.15564 | 0.082397 | 123.2712 | 122.9462 | 122.9095 | -0.32044 | 123.1476 | 123.0927 | 122.9736 | -0.32959
4339.375 | 123.0927 | -122.8912 | 0.22888 | -0.0082397 | 0.03685 | 0.0038024 | 0.0061865 | -0.009252 | 0.0015744 | -0.0073701 | -0.027695 | -0.01405 | -0.0073208 | -0.0013352 | 0.0073123 | -0.017852 | 0.059509 | 0.054932 | -0.036621 | 0.027466 | 0.3067 | -0.068665 | -0.25177 | 0.004578 | 0.036621 | -0.10986 | 0.21515 | 0.17853 | -0.19684 | -0.2243 | 122.8226 | 122.6395 | 0.07782 | 122.9462 | 122.9187 | 0.27924 | -0.16937 | 122.6944 | 122.6669 | -0.013733 | 122.8958 | 122.7814 | 0.11444 | -0.050354 | 123.1979 | 122.9507 | 122.8546 | -0.48065 | 123.1064 | 123.0698 | 122.9279 | -0.45319
4341.0781 | 123.2254 | -122.8317 | 0.1831 | -0.29053 | 0.034073 | 0.007434 | 0.010886 | -0.0073294 | -0.0012028 | -0.0071563 | -0.24895 | -0.012341 | -0.0039028 | -0.0021896 | 0.00068993 | -0.016143 | 0.09613 | 0.16022 | 0.07782 | 0.11902 | 0.40741 | 0.022888 | -0.12817 | 0.054932 | 0.15106 | 0 | 0.33417 | 0.27466 | -0.11444 | -0.15564 | 122.8546 | 122.7036 | 0.22431 | 122.9919 | 122.9507 | 0.24719 | -0.086975 | 122.7173 | 122.6761 | 0.15106 | 122.8867 | 122.8317 | 0.15564 | 0.091553 | 123.2391 | 122.9279 | 122.9095 | -0.31128 | 123.1659 | 123.1064 | 122.9828 | -0.33874
4342.7656 | 123.1842 | -122.8363 | 0.19226 | 0.022278 | 0.030228 | 0.0072204 | 0.0089635 | -0.011602 | -0.0063296 | -0.0099335 | 0.04097 | -0.015332 | -0.0051846 | -0.0026168 | 0.00047633 | -0.015716 | 0.050354 | 0.15106 | 0.1236 | 0.11444 | 0.31128 | 0.004578 | -0.16022 | 0.12817 | 0.20142 | 0.11902 | 0.23804 | 0.20599 | -0.09613 | -0.13275 | 122.8409 | 122.6761 | 0.11902 | 122.9874 | 122.9507 | 0.27466 | -0.14191 | 122.7402 | 122.7036 | 0.045776 | 122.9645 | 122.9553 | 0.25177 | 0.013733 | 123.1476 | 122.8867 | 122.9599 | -0.35248 | 123.0743 | 123.0423 | 123.0377 | -0.32501
4344.4688 | 123.1842 | -122.8592 | 0.16479 | 0.0070193 | 0.033432 | 0.0061524 | 0.0087499 | -0.012884 | -0.0039798 | -0.0088653 | 0.03334 | -0.01405 | -0.0062528 | -0.0026168 | 0.00090353 | -0.016357 | 0.059509 | 0.15106 | 0.09613 | 0.10071 | 0.32959 | -0.004578 | -0.16479 | 0.10529 | 0.19226 | 0.10986 | 0.25177 | 0.19226 | -0.09613 | -0.13733 | 122.8546 | 122.6944 | 0.16479 | 123.0103 | 122.9599 | 0.2655 | -0.10529 | 122.7631 | 122.7219 | 0.086975 | 122.9645 | 122.9691 | 0.24719 | 0.027466 | 123.1888 | 122.9187 | 122.9553 | -0.32959 | 123.111 | 123.0515 | 123.0515 | -0.30212
4346.1719 | 123.2071 | -122.8271 | 0.17395 | -0.1532 | 0.035996 | 0.0050842 | 0.0072547 | -0.008611 | 0.0015744 | -0.0090791 | -0.18791 | -0.0074277 | -0.004971 | -0.001976 | 0.0079531 | -0.020202 | 0.1236 | 0.12817 | 0.041199 | 0.09613 | 0.33875 | -0.036621 | -0.20142 | 0.059509 | 0.11444 | -0.036621 | 0.24719 | 0.20142 | -0.15564 | -0.18768 | 122.7905 | 122.6257 | 0.1648 | 122.9553 | 122.9233 | 0.29755 | -0.050354 | 122.6715 | 122.6395 | 0.073242 | 122.8867 | 122.7905 | 0.15106 | 0.027466 | 123.1659 | 122.9507 | 122.8683 | -0.37537 | 123.0743 | 123.0286 | 122.9416 | -0.36163
4347.8594 | 123.1659 | -122.818 | 0.17395 | -0.19135 | 0.031296 | 0.008075 | 0.0098181 | -0.011175 | -0.0052616 | -0.0092927 | -0.11925 | -0.014264 | -0.0071072 | -0.0026168 | 0.0030399 | -0.016784 | 0.17395 | 0.27924 | 0.21057 | 0.19684 | 0.37994 | 0.068665 | -0.10529 | 0.17395 | 0.2655 | 0.12817 | 0.23804 | 0.23346 | -0.068665 | -0.10529 | 122.8867 | 122.7127 | 0.20599 | 123.0972 | 123.0148 | 0.30212 | 0 | 122.7493 | 122.7127 | 0.064087 | 122.9919 | 122.9462 | 0.23346 | 0.059509 | 123.1979 | 122.9919 | 123.0286 | -0.27924 | 123.056 | 123.0515 | 123.0835 | -0.27924
4349.5469 | 123.23 | -122.8363 | 0.19684 | -0.046387 | 0.031082 | 0.008075 | 0.0049047 | -0.010747 | -0.0056888 | -0.011642 | -0.035324 | -0.014691 | -0.00668 | -0.0051804 | 0.0032535 | -0.016357 | 0.12817 | 0.19226 | 0.15564 | 0.14191 | 0.35248 | 0.027466 | -0.14191 | 0.17853 | 0.24719 | 0.15564 | 0.26093 | 0.21057 | -0.07782 | -0.10071 | 122.8638 | 122.6944 | 0.15564 | 123.0286 | 122.9782 | 0.28381 | -0.068664 | 122.7585 | 122.7356 | 0.064087 | 123.0148 | 122.9919 | 0.25635 | 0.013733 | 123.1888 | 122.9645 | 122.9919 | -0.33875 | 123.0972 | 123.0469 | 123.0835 | -0.29755
4351.25 | 123.2025 | -122.8592 | 0.19226 | -0.16846 | 0.033218 | 0.0078614 | 0.0061865 | -0.010106 | -0.0012028 | -0.012283 | -0.26421 | -0.014905 | -0.0088162 | -0.00090781 | 0.0058169 | -0.017425 | 0.15106 | 0.14191 | 0.064087 | 0.11444 | 0.40741 | 0.022888 | -0.15564 | 0.09613 | 0.12817 | 0.013733 | 0.31586 | 0.28839 | -0.09613 | -0.13733 | 122.8821 | 122.7036 | 0.21515 | 123.0011 | 122.9736 | 0.27008 | -0.041199 | 122.7631 | 122.7219 | 0.1236 | 122.9553 | 122.8729 | 0.15106 | 0.09613 | 123.2666 | 123.0103 | 122.9233 | -0.3479 | 123.175 | 123.1476 | 122.9874 | -0.32959
4352.9375 | 123.0972 | -122.8775 | 0.2243 | 0.014648 | 0.035355 | 0.008075 | 0.0042639 | -0.0073294 | 0.00093342 | -0.0060883 | -0.042954 | -0.011914 | -0.0062528 | -0.00048061 | 0.010944 | -0.018493 | 0.041199 | 0 | -0.073242 | -0.004578 | 0.28839 | -0.091553 | -0.27466 | 0.004578 | 0.009155 | -0.12817 | 0.20599 | 0.19226 | -0.19226 | -0.24261 | 122.7859 | 122.6028 | 0.064087 | 122.8775 | 122.8729 | 0.27008 | -0.18311 | 122.6852 | 122.6349 | -0.01831 | 122.8821 | 122.7493 | 0.11444 | -0.032043 | 123.1659 | 122.9187 | 122.8043 | -0.49896 | 123.0835 | 123.0698 | 122.8867 | -0.46692
4354.6406 | 123.2025 | -122.8317 | 0.19226 | -0.16083 | 0.031082 | 0.0067932 | 0.0074683 | -0.010534 | -0.0052616 | -0.011215 | -0.065842 | -0.015332 | -0.00668 | -0.0047532 | 0.0038943 | -0.016998 | 0.18768 | 0.2655 | 0.18768 | 0.17395 | 0.35248 | 0.032043 | -0.13733 | 0.20599 | 0.28381 | 0.16022 | 0.23804 | 0.2243 | -0.064087 | -0.10986 | 122.8638 | 122.6944 | 0.16022 | 123.0972 | 123.0057 | 0.31128 | -0.004578 | 122.7676 | 122.7219 | 0.045776 | 123.0377 | 122.9919 | 0.27008 | 0.032043 | 123.1842 | 123.0194 | 123.0194 | -0.32959 | 123.0698 | 123.056 | 123.1155 | -0.30212
4356.3281 | 123.143 | -122.8638 | 0.21057 | 0.0070193 | 0.032791 | 0.0057252 | 0.0070409 | -0.010106 | -0.0037662 | -0.0075837 | 0.056228 | -0.012768 | -0.0053982 | -0.00069421 | 0.0021853 | -0.016998 | 0.09613 | 0.1236 | 0.10986 | 0.10071 | 0.32501 | 0.004578 | -0.16022 | 0.11444 | 0.16022 | 0.073242 | 0.24261 | 0.21515 | -0.11444 | -0.15106 | 122.8683 | 122.7036 | 0.11444 | 122.9874 | 122.9645 | 0.26093 | -0.11444 | 122.7493 | 122.7127 | 0.032044 | 122.9782 | 122.937 | 0.2243 | 0.004578 | 123.1888 | 122.9599 | 122.9736 | -0.37079 | 123.1064 | 123.0789 | 123.024 | -0.36163
4358.0625 | 123.2025 | -122.8409 | 0.16022 | 0.0070193 | 0.031082 | 0.0061524 | 0.0091773 | -0.010747 | -0.005048 | -0.011642 | -0.0048066 | -0.012768 | -0.006039 | -0.0017624 | 0.0015445 | -0.01828 | 0.09613 | 0.15564 | 0.10986 | 0.1236 | 0.33417 | 0.009155 | -0.16479 | 0.15564 | 0.18768 | 0.12817 | 0.25635 | 0.20599 | -0.073242 | -0.13733 | 122.85 | 122.6761 | 0.17395 | 122.9965 | 122.9645 | 0.28839 | -0.064087 | 122.7676 | 122.7036 | 0.096131 | 122.9965 | 122.9691 | 0.2655 | 0.045777 | 123.175 | 122.937 | 122.9507 | -0.32501 | 123.0972 | 123.0469 | 123.0286 | -0.29755
4359.75 | 123.1842 | -122.8363 | 0.19684 | -0.00061023 | 0.030655 | 0.0095704 | 0.0044775 | -0.0094656 | -0.004407 | -0.010147 | -0.027695 | -0.014477 | -0.007748 | -0.0034714 | 0.0064577 | -0.017212 | 0.10986 | 0.13733 | 0.10071 | 0.10529 | 0.31586 | -0.004578 | -0.18768 | 0.11902 | 0.1831 | 0.086975 | 0.25177 | 0.21515 | -0.10071 | -0.15106 | 122.8317 | 122.6486 | 0.11902 | 122.9736 | 122.9416 | 0.29297 | -0.086975 | 122.7356 | 122.6852 | 0.054932 | 122.9553 | 122.9233 | 0.23804 | 0.018311 | 123.1522 | 122.9462 | 122.937 | -0.38452 | 123.0881 | 123.0515 | 123.0194 | -0.3479
4361.4375 | 123.1842 | -122.8729 | 0.18768 | -0.19135 | 0.030655 | 0.0087158 | 0.0074683 | -0.01032 | -0.00056178 | -0.0080109 | -0.19554 | -0.015332 | -0.006039 | -0.001976 | 0.0060305 | -0.016998 | 0.22888 | 0.25635 | 0.1831 | 0.20142 | 0.37079 | 0.059509 | -0.11444 | 0.17853 | 0.23346 | 0.11444 | 0.27466 | 0.22888 | -0.064087 | -0.11902 | 122.9324 | 122.7585 | 0.18311 | 123.1293 | 123.0743 | 0.31586 | 0.041199 | 122.8088 | 122.7539 | 0.086975 | 123.0515 | 122.9874 | 0.23346 | 0.041199 | 123.2437 | 123.1018 | 123.056 | -0.30212 | 123.1476 | 123.1018 | 123.1064 | -0.3067
4363.125 | 123.1842 | -122.8409 | 0.1831 | -0.084534 | 0.037918 | 0.0057252 | 0.0055457 | -0.0071158 | 0.0047788 | -0.0073701 | -0.21843 | -0.011487 | -0.0051846 | -0.0021896 | 0.0088077 | -0.018921 | 0.16022 | 0.11444 | 0.022888 | 0.07782 | 0.32044 | -0.045776 | -0.23346 | 0.091553 | 0.10529 | -0.050354 | 0.23346 | 0.1831 | -0.14191 | -0.20142 | 122.7951 | 122.6074 | 0.13733 | 122.9553 | 122.9187 | 0.31128 | -0.022888 | 122.699 | 122.6395 | 0.050354 | 122.9324 | 122.7905 | 0.15106 | 0 | 123.1613 | 123.0011 | 122.8638 | -0.41656 | 123.0743 | 123.024 | 122.9462 | -0.38452
4364.8594 | 123.0698 | -122.8729 | 0.2243 | 0.11383 | 0.032364 | 0.0059388 | 0.0074683 | -0.012243 | -0.0022708 | -0.0086517 | 0.15541 | -0.015332 | -0.004971 | -0.003685 | 0.0017581 | -0.016143 | 0.07782 | 0.13733 | 0.073242 | 0.073242 | 0.24719 | -0.059509 | -0.21057 | 0.11444 | 0.13733 | 0.027466 | 0.1831 | 0.15106 | -0.1236 | -0.17853 | 122.8134 | 122.6624 | 0.022888 | 123.0103 | 122.9462 | 0.28381 | -0.14648 | 122.7493 | 122.6944 | -0.041199 | 122.9874 | 122.9004 | 0.20599 | -0.073242 | 123.1201 | 122.9507 | 122.9462 | -0.43488 | 123.056 | 123.024 | 123.0103 | -0.40283
4366.5469 | 123.0606 | -122.8683 | 0.20599 | 0.12146 | 0.029587 | 0.0070068 | 0.0025549 | -0.0079702 | -0.0020572 | -0.0071563 | 0.15541 | -0.01405 | -0.010525 | -0.0021896 | 0.0070987 | -0.016784 | 0.10529 | 0.13275 | 0.068665 | 0.050354 | 0.2243 | -0.050354 | -0.21973 | 0.10529 | 0.12817 | 0.032043 | 0.19226 | 0.15564 | -0.14191 | -0.17395 | 122.818 | 122.6486 | 0.01831 | 123.0011 | 122.9187 | 0.27008 | -0.10071 | 122.7264 | 122.6944 | -0.013733 | 122.9736 | 122.9004 | 0.20599 | -0.050354 | 123.0927 | 122.9736 | 122.937 | -0.42572 | 123.0606 | 123.024 | 122.9965 | -0.37994
4368.2344 | 123.1064 | -122.8912 | 0.21515 | 0.083313 | 0.036209 | 0.0052978 | 0.0044775 | -0.0083974 | 0.0043514 | -0.0086517 | -0.081101 | -0.011914 | -0.0096706 | 0.00037379 | 0.0096621 | -0.017852 | 0.036621 | -0.013733 | -0.082397 | -0.004578 | 0.3067 | -0.10529 | -0.27008 | -0.013733 | 0 | -0.12817 | 0.21973 | 0.16937 | -0.19684 | -0.24261 | 122.7859 | 122.6212 | 0.091553 | 122.8775 | 122.8867 | 0.2655 | -0.17853 | 122.6944 | 122.6486 | 0.004578 | 122.8775 | 122.7631 | 0.11444 | -0.045776 | 123.1979 | 122.9279 | 122.8088 | -0.48523 | 123.111 | 123.0606 | 122.8912 | -0.45776
4369.9844 | 123.1476 | -122.8821 | 0.21057 | 0.014648 | 0.028092 | 0.0093566 | 0.0051183 | -0.0098928 | -0.0046206 | -0.0082245 | 0.048599 | -0.012982 | -0.0086026 | -0.0043258 | 0.0017581 | -0.016357 | 0.086975 | 0.13733 | 0.10071 | 0.086975 | 0.32959 | -0.013733 | -0.17853 | 0.10986 | 0.17395 | 0.07782 | 0.23346 | 0.20599 | -0.10529 | -0.15106 | 122.8683 | 122.7036 | 0.11902 | 123.0194 | 122.9691 | 0.2655 | -0.1236 | 122.7768 | 122.731 | 0.022888 | 122.9919 | 122.9599 | 0.22888 | -0.004577 | 123.2117 | 122.9691 | 122.9828 | -0.3891 | 123.1155 | 123.0881 | 123.056 | -0.36163
4371.6719 | 123.0743 | -122.8729 | 0.21515 | 0.098572 | 0.032791 | 0.0070068 | 0.0059729 | -0.0083974 | -0.0012028 | -0.0084381 | 0.11726 | -0.012555 | -0.0090298 | -0.0041122 | 0.0034671 | -0.015289 | 0.1236 | 0.12817 | 0.068665 | 0.064087 | 0.23346 | -0.036621 | -0.21515 | 0.10529 | 0.13733 | 0.036621 | 0.19684 | 0.14648 | -0.14191 | -0.1831 | 122.8363 | 122.6578 | 0.01831 | 123.0011 | 122.937 | 0.27924 | -0.091553 | 122.731 | 122.6898 | -0.018311 | 122.9782 | 122.9095 | 0.21973 | -0.068665 | 123.1064 | 122.9965 | 122.9416 | -0.4303 | 123.0698 | 123.0194 | 123.0103 | -0.39825
4373.4062 | 123.1018 | -122.8638 | 0.23346 | 0.045166 | 0.034714 | 0.0067932 | 0.0061865 | -0.0064748 | 0.0049924 | -0.0065155 | 0.03334 | -0.010418 | -0.0081754 | -5.3406e-05 | 0.0070987 | -0.018707 | 0.022888 | -0.041199 | -0.10986 | -0.036621 | 0.3067 | -0.07782 | -0.25177 | -0.013733 | -0.018311 | -0.1236 | 0.20599 | 0.15564 | -0.20599 | -0.26093 | 122.7859 | 122.612 | 0.073243 | 122.8226 | 122.8271 | 0.21515 | -0.21057 | 122.6578 | 122.6028 | -0.027465 | 122.85 | 122.7402 | 0.13733 | -0.077819 | 123.1705 | 122.8867 | 122.7539 | -0.48523 | 123.0698 | 123.0194 | 122.8455 | -0.49438
4375.0938 | 123.2162 | -122.8363 | 0.18768 | -0.13794 | 0.035141 | 0.0057252 | 0.0091773 | -0.012243 | 0.00093342 | -0.0058747 | -0.19554 | -0.010418 | -0.0047574 | -0.001976 | 0.0056033 | -0.018493 | 0.1236 | 0.11902 | 0.050354 | 0.09613 | 0.33875 | -0.022888 | -0.19684 | 0.082397 | 0.12817 | -0.036621 | 0.25177 | 0.21515 | -0.14191 | -0.21515 | 122.8134 | 122.6395 | 0.15106 | 122.9553 | 122.9324 | 0.29297 | -0.064087 | 122.6944 | 122.6212 | 0.064087 | 122.9187 | 122.7997 | 0.17853 | 0.027466 | 123.175 | 122.9599 | 122.8867 | -0.38452 | 123.0881 | 123.0515 | 122.9645 | -0.40283
4376.7812 | 123.1979 | -122.85 | 0.1831 | -0.12268 | 0.030869 | 0.0082886 | 0.0093909 | -0.0098928 | -0.0041934 | -0.0082245 | -0.14214 | -0.016186 | -0.0053982 | -0.003685 | -0.0010191 | -0.016357 | 0.21057 | 0.3067 | 0.21973 | 0.20599 | 0.36163 | 0.064087 | -0.11444 | 0.19226 | 0.29755 | 0.14648 | 0.25635 | 0.22888 | -0.054932 | -0.11444 | 122.9141 | 122.7356 | 0.17853 | 123.1567 | 123.056 | 0.32044 | 0.027466 | 122.7951 | 122.7356 | 0.073243 | 123.0423 | 122.9965 | 0.26093 | 0.045777 | 123.2117 | 123.0606 | 123.0698 | -0.29755 | 123.1064 | 123.0789 | 123.1476 | -0.29755
4378.4844 | 123.0881 | -122.8683 | 0.21057 | 0.1825 | 0.032578 | 0.0070068 | 0.0057593 | -0.0079702 | -0.0022708 | -0.0069427 | 0.1783 | -0.013623 | -0.010312 | -0.0026168 | 0.0038943 | -0.017639 | 0.082397 | 0.10986 | 0.050354 | 0.041199 | 0.2243 | -0.073242 | -0.23346 | 0.10986 | 0.13275 | 0.027466 | 0.15106 | 0.1236 | -0.16937 | -0.20142 | 122.7951 | 122.6349 | 0.013733 | 122.9782 | 122.9095 | 0.27466 | -0.12817 | 122.699 | 122.6669 | -0.059509 | 122.9782 | 122.8958 | 0.22888 | -0.086975 | 123.0927 | 122.9507 | 122.9187 | -0.44403 | 123.0194 | 122.9919 | 123.0011 | -0.41199
4380.1719 | 123.1201 | -122.8638 | 0.21515 | 0.098572 | 0.036423 | 0.0076478 | 0.0034093 | -0.010106 | 0.0030698 | -0.0058747 | 0.04097 | -0.011487 | -0.009457 | -0.0021896 | 0.0079531 | -0.016571 | 0.018311 | -0.032043 | -0.091553 | -0.027466 | 0.27924 | -0.10529 | -0.28839 | 0 | 0 | -0.086975 | 0.19684 | 0.16937 | -0.1831 | -0.22888 | 122.7585 | 122.5754 | 0.064087 | 122.8317 | 122.8363 | 0.26093 | -0.19684 | 122.6807 | 122.6349 | -0.018311 | 122.8638 | 122.7768 | 0.14191 | -0.045776 | 123.143 | 122.8821 | 122.7722 | -0.50354 | 123.0606 | 123.0331 | 122.8638 | -0.44403
4381.9062 | 123.1064 | -122.8638 | 0.20599 | 0.060425 | 0.031723 | 0.0089294 | 0.0070409 | -0.012029 | -0.005048 | -0.010574 | 0.071487 | -0.01405 | -0.0068936 | -0.0032578 | 0.0019717 | -0.014862 | 0.068665 | 0.12817 | 0.10986 | 0.10071 | 0.3067 | -0.013733 | -0.19226 | 0.10071 | 0.14191 | 0.059509 | 0.21515 | 0.20142 | -0.10071 | -0.14648 | 122.85 | 122.6715 | 0.10071 | 122.9919 | 122.9645 | 0.29297 | -0.13733 | 122.7631 | 122.7173 | 0.009155 | 122.9645 | 122.9233 | 0.20599 | -0.004578 | 123.1705 | 122.9324 | 122.9736 | -0.39826 | 123.0789 | 123.0652 | 123.0057 | -0.35248
4383.5938 | 123.0972 | -122.8775 | 0.21973 | 0.022278 | 0.036636 | 0.0042298 | 0.0055457 | -0.011175 | 0.0030698 | -0.0056611 | -0.027695 | -0.010846 | -0.0073208 | -0.00069421 | 0.0060305 | -0.018707 | 0.050354 | -0.022888 | -0.07782 | -0.013733 | 0.29755 | -0.086975 | -0.2655 | -0.018311 | 0.018311 | -0.1236 | 0.2243 | 0.17853 | -0.20142 | -0.21515 | 122.7905 | 122.612 | 0.077819 | 122.8546 | 122.8638 | 0.25177 | -0.16937 | 122.6761 | 122.6624 | 0.004577 | 122.8592 | 122.7539 | 0.091553 | -0.041199 | 123.175 | 122.9279 | 122.7997 | -0.48523 | 123.1018 | 123.056 | 122.8958 | -0.43488
4385.2969 | 123.1888 | -122.8271 | 0.19226 | -0.13794 | 0.031509 | 0.0072204 | 0.0068273 | -0.010747 | -0.0065434 | -0.010361 | -0.15739 | -0.015118 | -0.0056118 | -0.0032578 | 0.0030399 | -0.017639 | 0.2243 | 0.26093 | 0.19684 | 0.18768 | 0.34332 | 0.036621 | -0.1236 | 0.20142 | 0.27924 | 0.16479 | 0.28839 | 0.23346 | -0.059509 | -0.091553 | 122.8638 | 122.7036 | 0.15106 | 123.0881 | 123.0148 | 0.31128 | 0.032043 | 122.7676 | 122.7356 | 0.09613 | 123.0286 | 122.9919 | 0.25635 | 0.041198 | 123.1705 | 123.0515 | 123.024 | -0.31586 | 123.1155 | 123.0606 | 123.1064 | -0.28381
4387.0312 | 123.0972 | -122.8638 | 0.21973 | 0.16724 | 0.031937 | 0.0052978 | 0.0036231 | -0.008611 | -0.00098918 | -0.010147 | 0.17067 | -0.013409 | -0.0098844 | -0.0043258 | 0.0066715 | -0.016571 | 0.10986 | 0.09613 | 0.059509 | 0.045776 | 0.21973 | -0.10529 | -0.24719 | 0.09613 | 0.13733 | 0.032043 | 0.16022 | 0.1236 | -0.16937 | -0.20142 | 122.7585 | 122.6166 | 0 | 122.9599 | 122.9095 | 0.29297 | -0.10986 | 122.6944 | 122.6624 | -0.05951 | 122.9599 | 122.8958 | 0.23346 | -0.096131 | 123.0835 | 122.9736 | 122.9233 | -0.46692 | 123.024 | 122.9874 | 123.0011 | -0.42114
4388.7188 | 123.1338 | -122.8912 | 0.19684 | 0.13672 | 0.035568 | 0.0048706 | 0.0049047 | -0.0094656 | 0.0011472 | -0.0075837 | 0.14015 | -0.013836 | -0.0079618 | -0.0026168 | 0.0092349 | -0.017639 | 0.041199 | -0.027466 | -0.045776 | -0.018311 | 0.27466 | -0.10529 | -0.27466 | 0.059509 | 0.036621 | -0.036621 | 0.16937 | 0.14648 | -0.19226 | -0.23804 | 122.7859 | 122.6166 | 0.07782 | 122.8638 | 122.8729 | 0.25635 | -0.15564 | 122.699 | 122.6532 | -0.027465 | 122.9507 | 122.8546 | 0.20142 | -0.050354 | 123.1659 | 122.9324 | 122.8455 | -0.4715 | 123.0606 | 123.0377 | 122.9279 | -0.43488
4390.4219 | 123.2071 | -122.8317 | 0.17853 | -0.0082397 | 0.032364 | 0.0061524 | 0.011314 | -0.0090384 | -0.006116 | -0.010361 | -0.027695 | -0.016827 | -0.0062528 | -0.0032578 | 0.00026273 | -0.016571 | 0.11444 | 0.14191 | 0.13275 | 0.12817 | 0.32501 | -0.004578 | -0.17853 | 0.15564 | 0.23346 | 0.12817 | 0.26093 | 0.20599 | -0.086975 | -0.13275 | 122.8271 | 122.6532 | 0.14648 | 122.9736 | 122.9599 | 0.3067 | -0.064087 | 122.7448 | 122.699 | 0.082397 | 122.9874 | 122.9599 | 0.26093 | 0.027466 | 123.1567 | 122.9462 | 122.9645 | -0.35706 | 123.0927 | 123.0377 | 123.0652 | -0.31128
4392.1406 | 123.0881 | -122.8638 | 0.21973 | 0.17487 | 0.031723 | 0.0059388 | 0.0057593 | -0.0096792 | -0.0035526 | -0.0090791 | 0.15541 | -0.014264 | -0.0098844 | -0.001976 | 0.0075259 | -0.018493 | 0.09613 | 0.082397 | 0.041199 | 0.068665 | 0.19226 | -0.07782 | -0.24261 | 0.10529 | 0.14191 | 0.022888 | 0.15564 | 0.12817 | -0.15564 | -0.21057 | 122.7859 | 122.6212 | -0.027466 | 122.9462 | 122.9324 | 0.31128 | -0.1236 | 122.7081 | 122.6532 | -0.064087 | 122.9691 | 122.8867 | 0.23346 | -0.091553 | 123.056 | 122.9599 | 122.905 | -0.46234 | 123.0194 | 122.9919 | 123.0057 | -0.4303
4393.8281 | 123.0835 | -122.8683 | 0.20142 | 0.11383 | 0.030655 | 0.0082886 | 0.0061865 | -0.0096792 | -0.0024844 | -0.0084381 | 0.15541 | -0.013409 | -0.0073208 | -0.0034714 | 0.0058169 | -0.017212 | 0.10986 | 0.1236 | 0.068665 | 0.064087 | 0.24719 | -0.045776 | -0.22888 | 0.13275 | 0.15564 | 0.064087 | 0.20599 | 0.16479 | -0.11902 | -0.15564 | 122.8226 | 122.6395 | 0.045776 | 122.9919 | 122.9324 | 0.29297 | -0.091553 | 122.7493 | 122.7127 | 0.004578 | 123.0011 | 122.9324 | 0.21973 | -0.036621 | 123.1155 | 122.9782 | 122.937 | -0.4303 | 123.0743 | 123.0331 | 123.024 | -0.35706
4395.5469 | 123.1018 | -122.8821 | 0.21057 | 0.090942 | 0.035782 | 0.007434 | 0.0066137 | -0.010534 | 0.0041378 | -0.0082245 | -0.027695 | -0.0095639 | -0.0062528 | -0.00090781 | 0.0081667 | -0.018921 | 0.064087 | 0.004578 | -0.068665 | -0.013733 | 0.28839 | -0.10071 | -0.25635 | -0.022888 | -0.018311 | -0.14191 | 0.20142 | 0.17395 | -0.18768 | -0.24261 | 122.7814 | 122.6257 | 0.07782 | 122.8867 | 122.8683 | 0.24262 | -0.14648 | 122.6944 | 122.6395 | -0.009155 | 122.8592 | 122.7402 | 0.10071 | -0.036621 | 123.1705 | 122.9462 | 122.8134 | -0.46692 | 123.0835 | 123.056 | 122.8638 | -0.45319
4397.2344 | 123.1018 | -122.8821 | 0.21515 | 0.052795 | 0.037277 | 0.0055114 | 0.0074683 | -0.0096792 | 0.004565 | -0.0056611 | -0.012436 | -0.011914 | -0.0073208 | -0.00048061 | 0.0068851 | -0.018066 | 0.013733 | 0 | -0.073242 | -0.004578 | 0.27924 | -0.09613 | -0.2655 | -0.027466 | 0.013733 | -0.14191 | 0.21515 | 0.17853 | -0.19684 | -0.23804 | 122.7859 | 122.6166 | 0.064087 | 122.8821 | 122.8775 | 0.26092 | -0.20142 | 122.6852 | 122.644 | 0 | 122.8546 | 122.7402 | 0.09613 | -0.036621 | 123.1613 | 122.8958 | 122.8088 | -0.48065 | 123.0972 | 123.0606 | 122.8958 | -0.45319
4398.9844 | 123.1476 | -122.8729 | 0.20142 | 0.1062 | 0.036209 | 0.0067932 | 0.0066137 | -0.0090384 | 0.0022152 | -0.0080109 | 0.094375 | -0.012127 | -0.0043302 | -0.0028306 | 0.0085941 | -0.015289 | -0.027466 | -0.027466 | -0.091553 | -0.018311 | 0.2655 | -0.11444 | -0.27924 | -0.018311 | 0.009155 | -0.10071 | 0.21973 | 0.17395 | -0.21515 | -0.23346 | 122.7585 | 122.5937 | 0.064087 | 122.8455 | 122.8546 | 0.26092 | -0.22888 | 122.6578 | 122.6395 | 0.018311 | 122.8546 | 122.7722 | 0.13275 | -0.027466 | 123.1384 | 122.8455 | 122.7814 | -0.48065 | 123.0927 | 123.0469 | 122.8821 | -0.43488
4400.6719 | 123.1293 | -122.8592 | 0.21057 | 0.098572 | 0.035996 | 0.0082886 | 0.0064001 | -0.0079702 | 0.0020016 | -0.0067291 | 0.14015 | -0.011059 | -0.0081754 | -0.0021896 | 0.0075259 | -0.015289 | 0.013733 | 0.004578 | -0.045776 | -0.009155 | 0.28381 | -0.10986 | -0.25635 | 0.022888 | 0.022888 | -0.068665 | 0.17395 | 0.15564 | -0.1831 | -0.23804 | 122.7493 | 122.6028 | 0.073242 | 122.8638 | 122.85 | 0.24719 | -0.19684 | 122.6761 | 122.6212 | -0.036621 | 122.8821 | 122.7905 | 0.16937 | -0.054931 | 123.143 | 122.8729 | 122.8134 | -0.46692 | 123.0331 | 123.0148 | 122.8821 | -0.44861
4402.3594 | 123.0835 | -122.8912 | 0.2243 | 0.083313 | 0.037491 | 0.0057252 | 0.0059729 | -0.0083974 | 0.0037106 | -0.0073701 | 0.048599 | -0.0093503 | -0.0064664 | -0.0011216 | 0.0070987 | -0.016571 | 0.013733 | -0.027466 | -0.086975 | 0.004578 | 0.27466 | -0.091553 | -0.28381 | -0.022888 | 0.004578 | -0.13275 | 0.21515 | 0.17853 | -0.18768 | -0.22888 | 122.7997 | 122.6074 | 0.050354 | 122.8638 | 122.8958 | 0.28839 | -0.21057 | 122.7036 | 122.6624 | -0.009155 | 122.8683 | 122.7585 | 0.096131 | -0.045776 | 123.1659 | 122.905 | 122.8043 | -0.50812 | 123.1064 | 123.0698 | 122.8958 | -0.45319
4404.0625 | 123.0972 | -122.8821 | 0.20599 | 0.060425 | 0.038132 | 0.0048706 | 0.0076819 | -0.0094656 | 0.00071982 | -0.0075837 | 0.063858 | -0.010632 | -0.006039 | -0.0021896 | 0.0070987 | -0.017212 | 0.013733 | -0.036621 | -0.082397 | -0.013733 | 0.29755 | -0.091553 | -0.27008 | -0.032043 | 0 | -0.11444 | 0.20599 | 0.1831 | -0.17395 | -0.22888 | 122.7905 | 122.612 | 0.091552 | 122.8455 | 122.8683 | 0.25635 | -0.19226 | 122.7081 | 122.6532 | 0 | 122.85 | 122.7676 | 0.11444 | -0.022889 | 123.1796 | 122.8958 | 122.7997 | -0.47608 | 123.0881 | 123.0652 | 122.8821 | -0.43488
4405.7656 | 123.1338 | -122.8867 | 0.21057 | 0.14435 | 0.033646 | 0.0059388 | 0.0049047 | -0.0094656 | 0.00029262 | -0.0073701 | 0.102 | -0.014264 | -0.0056118 | -0.0011216 | 0.0060305 | -0.014862 | -0.013733 | -0.018311 | -0.073242 | -0.027466 | 0.27924 | -0.11902 | -0.27924 | -0.009155 | 0.018311 | -0.082397 | 0.20599 | 0.17853 | -0.19226 | -0.2243 | 122.7676 | 122.6074 | 0.068665 | 122.8683 | 122.8592 | 0.25177 | -0.2243 | 122.6944 | 122.6624 | -0.004577 | 122.8775 | 122.8043 | 0.14191 | -0.032043 | 123.1659 | 122.8729 | 122.8134 | -0.48981 | 123.0927 | 123.0652 | 122.905 | -0.43488
4407.4531 | 123.1338 | -122.85 | 0.20142 | 0.11383 | 0.0345 | 0.0057252 | 0.0064001 | -0.0079702 | -0.00077538 | -0.0082245 | 0.1783 | -0.011914 | -0.0051846 | -0.0011216 | 0.0056033 | -0.018493 | -0.018311 | -0.018311 | -0.045776 | -0.027466 | 0.26093 | -0.10071 | -0.28381 | 0.041199 | 0.064087 | -0.032043 | 0.17395 | 0.13733 | -0.16937 | -0.21973 | 122.7493 | 122.5662 | 0.059509 | 122.8317 | 122.8226 | 0.25635 | -0.21973 | 122.6807 | 122.6303 | -0.027466 | 122.8912 | 122.818 | 0.18768 | -0.064087 | 123.111 | 122.8317 | 122.8043 | -0.48523 | 123.024 | 122.9874 | 122.9141 | -0.42114
4409.1406 | 123.23 | -122.8683 | 0.17853 | -0.19135 | 0.033646 | 0.0072204 | 0.0089635 | -0.0077566 | -0.00163 | -0.0082245 | -0.17265 | -0.012768 | -0.0064664 | -0.0021896 | 0.0047489 | -0.017212 | 0.091553 | 0.1236 | 0.041199 | 0.10529 | 0.37537 | -0.013733 | -0.17395 | 0.045776 | 0.13733 | -0.004578 | 0.28381 | 0.24719 | -0.11444 | -0.16937 | 122.8546 | 122.6944 | 0.19684 | 122.9919 | 122.9736 | 0.27924 | -0.086975 | 122.7539 | 122.699 | 0.10528 | 122.9141 | 122.8638 | 0.16479 | 0.068664 | 123.2437 | 122.9599 | 122.9095 | -0.35248 | 123.1522 | 123.1155 | 123.0057 | -0.3479
4410.8281 | 123.1796 | -122.85 | 0.17853 | -0.21423 | 0.031937 | 0.0052978 | 0.012382 | -0.0090384 | -0.0029118 | -0.0084381 | -0.22606 | -0.014264 | -0.0024076 | -0.0032578 | 0.0015445 | -0.016784 | 0.07782 | 0.12817 | 0.082397 | 0.11902 | 0.41199 | 0 | -0.15106 | 0.064087 | 0.14648 | 0.009155 | 0.30212 | 0.27008 | -0.10071 | -0.13733 | 122.85 | 122.699 | 0.23346 | 122.9782 | 122.9691 | 0.27008 | -0.10071 | 122.7493 | 122.7127 | 0.1236 | 122.9141 | 122.8592 | 0.14648 | 0.091553 | 123.262 | 122.9279 | 122.9324 | -0.32959 | 123.1522 | 123.1201 | 122.9965 | -0.31586
4412.5156 | 123.2483 | -122.8363 | 0.20142 | -0.16846 | 0.036636 | 0.0057252 | 0.0098181 | -0.008611 | -0.0012028 | -0.0069427 | -0.27184 | -0.013196 | -0.003262 | -0.0015488 | 0.0021853 | -0.018066 | 0.086975 | 0.11444 | 0.045776 | 0.10529 | 0.37994 | -0.004578 | -0.16479 | 0.07782 | 0.1236 | 0.004578 | 0.27924 | 0.22888 | -0.13275 | -0.17395 | 122.8317 | 122.6715 | 0.17853 | 122.9507 | 122.9416 | 0.27008 | -0.11444 | 122.7036 | 122.6624 | 0.07782 | 122.9141 | 122.8409 | 0.17853 | 0.027466 | 123.2162 | 122.9233 | 122.8821 | -0.36621 | 123.1155 | 123.0652 | 122.9599 | -0.37537
4414.2031 | 123.2025 | -122.85 | 0.18768 | -0.26764 | 0.033646 | 0.0070068 | 0.011954 | -0.0096792 | -0.0046206 | -0.0095063 | -0.22606 | -0.013623 | -0.0034756 | -0.0021896 | 0.0013309 | -0.017212 | 0.091553 | 0.14648 | 0.068665 | 0.11902 | 0.43945 | 0.022888 | -0.14191 | 0.054932 | 0.14191 | 0.013733 | 0.31128 | 0.27466 | -0.10071 | -0.15106 | 122.8729 | 122.7081 | 0.25177 | 122.9965 | 122.9691 | 0.26093 | -0.09613 | 122.7493 | 122.699 | 0.1236 | 122.905 | 122.8638 | 0.16479 | 0.086975 | 123.2895 | 122.9416 | 122.9187 | -0.32959 | 123.1613 | 123.1247 | 122.9919 | -0.33874
4415.9219 | 123.0789 | -122.8821 | 0.21973 | 0.12909 | 0.028305 | 0.0070068 | 0.0055457 | -0.010747 | -0.0076114 | -0.011429 | 0.16304 | -0.013623 | -0.0098844 | -0.0021896 | 0.0032535 | -0.016571 | 0.064087 | 0.1236 | 0.07782 | 0.07782 | 0.25635 | -0.059509 | -0.2243 | 0.091553 | 0.14648 | 0.050354 | 0.21515 | 0.1831 | -0.11444 | -0.16479 | 122.8226 | 122.6578 | 0.036621 | 123.0057 | 122.9599 | 0.30212 | -0.15564 | 122.7676 | 122.7173 | -0.004578 | 122.9736 | 122.9324 | 0.21515 | -0.036622 | 123.1384 | 122.9462 | 122.9599 | -0.44403 | 123.0972 | 123.0652 | 123.0286 | -0.38452
4417.6094 | 123.1247 | -122.8775 | 0.21973 | 0.098572 | 0.035568 | 0.0082886 | 0.0055457 | -0.0083974 | 0.0030698 | -0.0073701 | 0.094375 | -0.010418 | -0.0058254 | -0.00026701 | 0.0085941 | -0.017852 | 0.004578 | -0.036621 | -0.10071 | -0.027466 | 0.27924 | -0.10986 | -0.27924 | -0.004578 | -0.013733 | -0.11902 | 0.21057 | 0.16479 | -0.19684 | -0.24719 | 122.7676 | 122.5983 | 0.059509 | 122.8409 | 122.85 | 0.25177 | -0.21515 | 122.6807 | 122.6303 | -0.009156 | 122.8729 | 122.7585 | 0.12817 | -0.054932 | 123.1567 | 122.8821 | 122.7768 | -0.49896 | 123.0881 | 123.0423 | 122.8638 | -0.46692
4419.3125 | 123.1979 | -122.8363 | 0.18768 | -0.092163 | 0.034287 | 0.0078614 | 0.0064001 | -0.0083974 | 0.00093342 | -0.0075837 | -0.14214 | -0.012127 | -0.00668 | -0.0015488 | 0.0058169 | -0.016357 | 0.09613 | 0.11902 | 0.013733 | 0.07782 | 0.34332 | -0.041199 | -0.21515 | 0.068665 | 0.10529 | -0.041199 | 0.21515 | 0.1831 | -0.15106 | -0.1831 | 122.7951 | 122.6212 | 0.15564 | 122.9553 | 122.9141 | 0.29297 | -0.091553 | 122.6852 | 122.6532 | 0.027466 | 122.905 | 122.7951 | 0.14191 | -0.004578 | 123.1796 | 122.9324 | 122.85 | -0.40283 | 123.0515 | 123.0194 | 122.9416 | -0.37079
4421.0312 | 123.1018 | -122.8638 | 0.21973 | 0.083313 | 0.035355 | 0.0050842 | 0.0066137 | -0.010747 | 0.0022152 | -0.0073701 | 0.025711 | -0.011059 | -0.0079618 | -0.0021896 | 0.0068851 | -0.017852 | -0.004578 | -0.022888 | -0.073242 | -0.009155 | 0.28381 | -0.10529 | -0.27008 | -0.036621 | -0.004578 | -0.11902 | 0.21057 | 0.18768 | -0.19684 | -0.22888 | 122.7585 | 122.5937 | 0.064086 | 122.8409 | 122.8546 | 0.26093 | -0.22431 | 122.6669 | 122.6349 | -0.009156 | 122.8271 | 122.7448 | 0.10986 | -0.032044 | 123.1476 | 122.8592 | 122.7905 | -0.48981 | 123.0743 | 123.0515 | 122.8592 | -0.44861
4422.7188 | 123.1567 | -122.8546 | 0.21515 | 0.16724 | 0.034073 | 0.0052978 | 0.0055457 | -0.0094656 | -0.0022708 | -0.0084381 | 0.20119 | -0.010846 | -0.010952 | -0.0028306 | 0.0062441 | -0.016357 | 0.009155 | 0.036621 | -0.018311 | -0.004578 | 0.24719 | -0.086975 | -0.26093 | 0.064087 | 0.11902 | -0.004578 | 0.17853 | 0.13733 | -0.17853 | -0.20142 | 122.7676 | 122.5937 | 0.032043 | 122.8912 | 122.85 | 0.25635 | -0.20599 | 122.6761 | 122.6532 | -0.036621 | 122.9187 | 122.85 | 0.19684 | -0.07782 | 123.1018 | 122.8638 | 122.8363 | -0.47607 | 123.0331 | 122.9919 | 122.9736 | -0.41657
4424.4688 | 123.175 | -122.8592 | 0.19226 | -0.19135 | 0.031509 | 0.0072204 | 0.0111 | -0.010747 | -0.0093204 | -0.0088653 | -0.096359 | -0.012768 | -0.006039 | -0.0030442 | 0.00068993 | -0.016784 | 0.20599 | 0.26093 | 0.20599 | 0.20142 | 0.37079 | 0.059509 | -0.10986 | 0.15564 | 0.28381 | 0.14648 | 0.26093 | 0.24261 | -0.068665 | -0.11902 | 122.9187 | 122.7493 | 0.17853 | 123.1201 | 123.0606 | 0.31128 | 0.013733 | 122.7905 | 122.7402 | 0.068664 | 123.0148 | 123.0057 | 0.2655 | 0.050354 | 123.23 | 123.0652 | 123.0652 | -0.30212 | 123.1201 | 123.1018 | 123.143 | -0.31128
4426.1875 | 123.2162 | -122.8409 | 0.17853 | -0.069275 | 0.033005 | 0.0082886 | 0.010459 | -0.0088248 | -0.006116 | -0.012924 | -0.020065 | -0.014264 | -0.0034756 | -0.0041122 | 0.0013309 | -0.018066 | 0.13275 | 0.17395 | 0.15106 | 0.16022 | 0.34332 | 0.027466 | -0.14648 | 0.15564 | 0.25635 | 0.15564 | 0.26093 | 0.2243 | -0.086975 | -0.1236 | 122.8683 | 122.6944 | 0.16479 | 123.0148 | 123.0011 | 0.3067 | -0.045777 | 122.7539 | 122.7173 | 0.082397 | 122.9965 | 122.9965 | 0.27924 | 0.045776 | 123.1842 | 122.9736 | 122.9919 | -0.32501 | 123.1018 | 123.0652 | 123.0972 | -0.30212
4427.875 | 123.0972 | -122.8729 | 0.21973 | 0.12909 | 0.028092 | 0.0076478 | 0.0064001 | -0.0094656 | -0.003339 | -0.011856 | 0.12489 | -0.014691 | -0.010098 | -0.0024032 | 0.0047489 | -0.016143 | 0.09613 | 0.11444 | 0.073242 | 0.086975 | 0.2655 | -0.064087 | -0.19684 | 0.086975 | 0.13275 | 0.050354 | 0.20599 | 0.19226 | -0.11902 | -0.17395 | 122.8088 | 122.6761 | 0.045776 | 122.9874 | 122.9599 | 0.28381 | -0.1236 | 122.7539 | 122.699 | -0.013733 | 122.9599 | 122.9233 | 0.2243 | -0.027466 | 123.1384 | 122.9691 | 122.9462 | -0.41657 | 123.0789 | 123.0652 | 123.0057 | -0.39368
4429.5781 | 123.23 | -122.8455 | 0.19226 | -0.24475 | 0.035141 | 0.0067932 | 0.010245 | -0.009252 | -0.0012028 | -0.010788 | -0.29472 | -0.011914 | -0.0068936 | -0.0021896 | 0.0041079 | -0.019989 | 0.14191 | 0.10986 | 0.07782 | 0.11902 | 0.42114 | 0.022888 | -0.13733 | 0.082397 | 0.11444 | -0.013733 | 0.32501 | 0.27466 | -0.10529 | -0.14191 | 122.8683 | 122.7081 | 0.22888 | 122.9553 | 122.9645 | 0.25635 | -0.050354 | 122.7402 | 122.7036 | 0.13275 | 122.9279 | 122.8317 | 0.12817 | 0.082397 | 123.2666 | 122.9874 | 122.9233 | -0.32959 | 123.1705 | 123.1201 | 122.9599 | -0.33417
4431.2656 | 123.1155 | -122.8683 | 0.21973 | -0.038757 | 0.036423 | 0.0055114 | 0.0044775 | -0.0090384 | 0.0032834 | -0.0095063 | -0.058212 | -0.0117 | -0.006039 | 0.00058739 | 0.0090213 | -0.01828 | 0.11444 | 0.073242 | -0.022888 | 0.045776 | 0.32959 | -0.054932 | -0.23804 | 0.032043 | 0.054932 | -0.10071 | 0.21057 | 0.17395 | -0.19226 | -0.23346 | 122.8134 | 122.6303 | 0.10986 | 122.9416 | 122.9141 | 0.28381 | -0.10529 | 122.6761 | 122.6349 | -0.009156 | 122.9004 | 122.7676 | 0.13275 | -0.045777 | 123.1979 | 122.9828 | 122.8455 | -0.45776 | 123.0789 | 123.0423 | 122.9233 | -0.45319
4432.9688 | 123.0927 | -122.8683 | 0.2243 | 0.083313 | 0.037064 | 0.0042298 | 0.0046911 | -0.0096792 | 0.0024288 | -0.0065155 | -0.020065 | -0.011914 | -0.0062528 | -0.00048061 | 0.0079531 | -0.01828 | 0 | -0.018311 | -0.082397 | 0 | 0.30212 | -0.086975 | -0.25177 | -0.018311 | 0.004578 | -0.13733 | 0.21057 | 0.19226 | -0.19684 | -0.23346 | 122.7814 | 122.6166 | 0.07782 | 122.85 | 122.8683 | 0.25177 | -0.2243 | 122.6715 | 122.6349 | -0.013733 | 122.85 | 122.731 | 0.09613 | -0.032043 | 123.1705 | 122.8683 | 122.7859 | -0.47607 | 123.0789 | 123.0606 | 122.8729 | -0.45776
4434.6562 | 123.1796 | -122.8455 | 0.21057 | -0.21423 | 0.032364 | 0.007434 | 0.0072547 | -0.0090384 | -0.0037662 | -0.0095063 | -0.21843 | -0.0117 | -0.004971 | -0.00026701 | 0.0043215 | -0.014435 | 0.10071 | 0.13733 | 0.064087 | 0.10986 | 0.40283 | 0.013733 | -0.15564 | 0.068665 | 0.13733 | 0.013733 | 0.31128 | 0.28381 | -0.11444 | -0.16022 | 122.8592 | 122.6898 | 0.19226 | 122.9828 | 122.9553 | 0.2655 | -0.10986 | 122.731 | 122.6852 | 0.10071 | 122.9141 | 122.8592 | 0.17395 | 0.073242 | 123.2483 | 122.9462 | 122.9095 | -0.36621 | 123.1567 | 123.1293 | 122.9828 | -0.37079
4436.375 | 123.1567 | -122.85 | 0.19684 | 0.029907 | 0.031296 | 0.009143 | 0.0057593 | -0.0088248 | -0.0063296 | -0.0092927 | 0.071487 | -0.013196 | -0.0068936 | -0.0041122 | 0.00047633 | -0.015289 | 0.091553 | 0.1236 | 0.10986 | 0.10986 | 0.33417 | 0.004578 | -0.16937 | 0.091553 | 0.16022 | 0.07782 | 0.23804 | 0.21057 | -0.11444 | -0.15106 | 122.8546 | 122.6807 | 0.13733 | 122.9736 | 122.9599 | 0.27924 | -0.10529 | 122.7356 | 122.699 | 0.041199 | 122.9416 | 122.9279 | 0.22888 | 0.013733 | 123.1842 | 122.9416 | 122.9599 | -0.36621 | 123.0881 | 123.0606 | 123.0103 | -0.3479
4438.0625 | 123.1476 | -122.85 | 0.21973 | -0.00061023 | 0.03215 | 0.007434 | 0.010032 | -0.011175 | -0.0041934 | -0.011429 | 0.056228 | -0.015545 | -0.0073208 | -0.0047532 | 0.0011173 | -0.017425 | 0.091553 | 0.11902 | 0.086975 | 0.09613 | 0.33417 | 0 | -0.18768 | 0.09613 | 0.16937 | 0.082397 | 0.23346 | 0.21057 | -0.11902 | -0.15106 | 122.85 | 122.6624 | 0.11444 | 122.9691 | 122.9462 | 0.28381 | -0.12817 | 122.731 | 122.699 | 0.013732 | 122.9462 | 122.9324 | 0.23346 | -0.009156 | 123.1842 | 122.9416 | 122.937 | -0.40741 | 123.0835 | 123.0606 | 123.0194 | -0.37079
4439.7656 | 123.0789 | -122.8729 | 0.21057 | 0.11383 | 0.033859 | 0.0067932 | 0.0055457 | -0.010961 | -0.0024844 | -0.0088653 | 0.15541 | -0.011487 | -0.007748 | -0.0017624 | 0.0036807 | -0.01828 | 0.1236 | 0.11902 | 0.07782 | 0.059509 | 0.23804 | -0.064087 | -0.19684 | 0.10071 | 0.12817 | 0.032043 | 0.18768 | 0.15106 | -0.16479 | -0.19684 | 122.8088 | 122.6761 | 0.027466 | 122.9919 | 122.9324 | 0.25635 | -0.086975 | 122.7081 | 122.6761 | -0.022888 | 122.9736 | 122.905 | 0.22888 | -0.059509 | 123.111 | 122.9965 | 122.9507 | -0.40741 | 123.0606 | 123.024 | 123.0011 | -0.40741
4441.4844 | 123.23 | -122.85 | 0.1831 | -0.084534 | 0.029373 | 0.007434 | 0.0091773 | -0.0069022 | -0.005048 | -0.011642 | -0.096359 | -0.014264 | -0.006039 | -0.0026168 | 0.0023989 | -0.017639 | 0.17395 | 0.2243 | 0.16937 | 0.17853 | 0.3479 | 0.022888 | -0.13275 | 0.19226 | 0.2655 | 0.15564 | 0.24719 | 0.23804 | -0.068665 | -0.10986 | 122.8729 | 122.7173 | 0.16479 | 123.0743 | 123.0286 | 0.31128 | -0.009155 | 122.7814 | 122.7402 | 0.064087 | 123.0423 | 123.0057 | 0.2655 | 0.054932 | 123.1979 | 123.024 | 123.0194 | -0.31586 | 123.0972 | 123.0881 | 123.1155 | -0.29297
4443.2188 | 123.2162 | -122.85 | 0.17395 | -0.21423 | 0.034714 | 0.007434 | 0.0083227 | -0.0081838 | 0.0011472 | -0.0099335 | -0.24132 | -0.010632 | -0.007748 | -0.001976 | 0.0049625 | -0.018921 | 0.15564 | 0.091553 | 0.050354 | 0.10529 | 0.44403 | 0.013733 | -0.16937 | 0.064087 | 0.12817 | -0.018311 | 0.29755 | 0.24719 | -0.11444 | -0.16022 | 122.8638 | 122.6807 | 0.27008 | 122.9416 | 122.9553 | 0.27466 | -0.01831 | 122.7356 | 122.6898 | 0.1236 | 122.9141 | 122.8317 | 0.14191 | 0.073242 | 123.2941 | 123.0057 | 122.9004 | -0.34332 | 123.1476 | 123.0972 | 122.9782 | -0.33417
4444.9062 | 123.1842 | -122.85 | 0.19226 | -0.22186 | 0.035568 | 0.0067932 | 0.0089635 | -0.009252 | -0.00098918 | -0.011215 | -0.24132 | -0.01405 | -0.0064664 | -0.0017624 | 0.0036807 | -0.019561 | 0.13275 | 0.14191 | 0.091553 | 0.09613 | 0.41199 | 0.018311 | -0.14648 | 0.091553 | 0.15564 | 0.013733 | 0.32044 | 0.27008 | -0.1236 | -0.15106 | 122.8683 | 122.7036 | 0.21973 | 122.9919 | 122.9462 | 0.24261 | -0.05951 | 122.7264 | 122.699 | 0.12817 | 122.9416 | 122.8638 | 0.16479 | 0.07782 | 123.262 | 122.9828 | 122.9416 | -0.33874 | 123.1705 | 123.1201 | 123.0057 | -0.34332
4446.6094 | 123.1934 | -122.8409 | 0.18768 | -0.099793 | 0.036636 | 0.004657 | 0.0046911 | -0.010961 | 0.004565 | -0.0071563 | -0.15739 | -0.012127 | -0.0073208 | -0.0024032 | 0.0085941 | -0.018921 | 0.13733 | 0.10529 | 0.022888 | 0.07782 | 0.3479 | -0.036621 | -0.20599 | 0.073242 | 0.12817 | -0.032043 | 0.21515 | 0.20142 | -0.16022 | -0.19684 | 122.8043 | 122.6349 | 0.16022 | 122.9462 | 122.9187 | 0.28381 | -0.050354 | 122.6807 | 122.644 | 0.027466 | 122.9141 | 122.8088 | 0.1648 | 0.013733 | 123.1888 | 122.9782 | 122.8638 | -0.39368 | 123.056 | 123.0423 | 122.9691 | -0.38452
4448.2969 | 123.1522 | -122.8638 | 0.21515 | -0.076904 | 0.035568 | 0.0059388 | 0.0068273 | -0.011175 | 0.0022152 | -0.0056611 | -0.12688 | -0.011273 | -0.006039 | -0.0021896 | 0.0073123 | -0.019989 | 0.12817 | 0.1236 | 0.018311 | 0.073242 | 0.33875 | -0.050354 | -0.20599 | 0.068665 | 0.10071 | -0.054932 | 0.23804 | 0.21515 | -0.15564 | -0.21973 | 122.8134 | 122.6578 | 0.1236 | 122.9874 | 122.937 | 0.27924 | -0.086975 | 122.7081 | 122.644 | 0.022888 | 122.9324 | 122.8088 | 0.16479 | 0 | 123.2025 | 122.9919 | 122.8821 | -0.42114 | 123.1018 | 123.0789 | 122.9645 | -0.43488
4449.9844 | 123.1796 | -122.8409 | 0.19226 | -0.17609 | 0.030014 | 0.0072204 | 0.0098181 | -0.0098928 | -0.0080386 | -0.0092927 | -0.13451 | -0.01405 | -0.0062528 | -0.003685 | -0.0012327 | -0.016998 | 0.17853 | 0.27924 | 0.20599 | 0.18768 | 0.36163 | 0.050354 | -0.11444 | 0.20142 | 0.30212 | 0.16479 | 0.25177 | 0.24261 | -0.045776 | -0.09613 | 122.8912 | 122.7264 | 0.16937 | 123.1201 | 123.0286 | 0.30212 | -0.013733 | 122.7951 | 122.7448 | 0.059509 | 123.0423 | 123.0057 | 0.26092 | 0.050354 | 123.2025 | 123.0194 | 123.0469 | -0.3067 | 123.0927 | 123.0835 | 123.143 | -0.28839
4451.7031 | 123.2117 | -122.818 | 0.18768 | -0.12268 | 0.031082 | 0.0099976 | 0.0093909 | -0.011602 | -0.0037662 | -0.0090791 | -0.058212 | -0.013623 | -0.0081754 | -0.0017624 | 0.0011173 | -0.016357 | 0.1831 | 0.27008 | 0.18768 | 0.17395 | 0.35706 | 0.041199 | -0.12817 | 0.20599 | 0.28381 | 0.16937 | 0.25635 | 0.21973 | -0.086975 | -0.10986 | 122.8592 | 122.6898 | 0.16937 | 123.0881 | 122.9919 | 0.30212 | -0.004578 | 122.731 | 122.7081 | 0.068665 | 123.024 | 122.9874 | 0.27924 | 0.032044 | 123.175 | 123.0011 | 123.0057 | -0.31586 | 123.0743 | 123.0377 | 123.1018 | -0.29755
4453.4219 | 123.0927 | -122.8958 | 0.21973 | 0.083313 | 0.035355 | 0.006366 | 0.0042639 | -0.0079702 | 0.0037106 | -0.0065155 | -0.027695 | -0.012341 | -0.0075344 | -0.0038986 | 0.0075259 | -0.018921 | 0.013733 | 0 | -0.082397 | -0.018311 | 0.30212 | -0.10986 | -0.26093 | -0.027466 | 0.009155 | -0.12817 | 0.21057 | 0.17395 | -0.21057 | -0.2243 | 122.7859 | 122.6349 | 0.082397 | 122.8958 | 122.8775 | 0.24261 | -0.20599 | 122.6852 | 122.6715 | -0.009156 | 122.8683 | 122.7676 | 0.09613 | -0.045777 | 123.1979 | 122.9095 | 122.8134 | -0.48065 | 123.1064 | 123.0698 | 122.905 | -0.44403
4455.125 | 123.1064 | -122.8775 | 0.2243 | 0.17487 | 0.030655 | 0.0044434 | 0.0044775 | -0.010106 | -0.00056178 | -0.0082245 | 0.18593 | -0.014264 | -0.0068936 | -0.0011216 | 0.0051761 | -0.01593 | 0.068665 | 0.09613 | 0.054932 | 0.064087 | 0.2243 | -0.082397 | -0.24719 | 0.086975 | 0.12817 | 0.032043 | 0.14191 | 0.11444 | -0.16479 | -0.2243 | 122.7951 | 122.6303 | 0 | 122.9736 | 122.9416 | 0.31128 | -0.15564 | 122.7127 | 122.6532 | -0.082397 | 122.9645 | 122.9095 | 0.25635 | -0.10986 | 123.1018 | 122.9462 | 122.9324 | -0.4715 | 123.0194 | 122.9919 | 123.0057 | -0.44861
4456.8281 | 123.2117 | -122.8546 | 0.16937 | -0.046387 | 0.03215 | 0.0065796 | 0.010459 | -0.0073294 | -0.005048 | -0.0075837 | 0.010452 | -0.01405 | -0.0041164 | -0.0013352 | 0.0021853 | -0.015716 | 0.11444 | 0.20142 | 0.15564 | 0.15564 | 0.32501 | 0.004578 | -0.14648 | 0.17853 | 0.25177 | 0.15106 | 0.24719 | 0.23346 | -0.091553 | -0.12817 | 122.8592 | 122.7081 | 0.15564 | 123.056 | 123.0103 | 0.30212 | -0.054932 | 122.7631 | 122.7264 | 0.077819 | 123.0331 | 123.0057 | 0.27924 | 0.064086 | 123.1796 | 122.9691 | 123.0103 | -0.31586 | 123.1018 | 123.0881 | 123.1064 | -0.29755
4458.5469 | 123.1384 | -122.8912 | 0.1831 | 0.17487 | 0.036209 | 0.007434 | 0.0046911 | -0.012456 | 7.902e-05 | -0.0071563 | 0.12489 | -0.012982 | -0.008389 | -0.001976 | 0.0064577 | -0.017212 | 0.07782 | 0.054932 | 0.004578 | 0.036621 | 0.24261 | -0.09613 | -0.24261 | 0.10986 | 0.1236 | 0.018311 | 0.16937 | 0.1236 | -0.14648 | -0.20599 | 122.7951 | 122.6486 | 0.05951 | 122.9462 | 122.9279 | 0.27924 | -0.10528 | 122.7448 | 122.6852 | -0.013732 | 123.0011 | 122.9095 | 0.22431 | -0.059509 | 123.1338 | 122.9691 | 122.8958 | -0.42572 | 123.0606 | 123.0148 | 123.0148 | -0.3891
4460.2344 | 123.1338 | -122.8592 | 0.20599 | 0.17487 | 0.034927 | 0.0087158 | 0.0053321 | -0.011175 | 0.001788 | -0.0086517 | 0.15541 | -0.0117 | -0.010312 | -0.0028306 | 0.0062441 | -0.016784 | 0.041199 | 0.022888 | -0.045776 | -0.018311 | 0.25177 | -0.10529 | -0.27466 | 0.068665 | 0.091553 | -0.004578 | 0.16937 | 0.15564 | -0.17395 | -0.21057 | 122.7539 | 122.5845 | 0.045776 | 122.8821 | 122.8409 | 0.25635 | -0.1648 | 122.6852 | 122.6486 | -0.036621 | 122.9279 | 122.8546 | 0.20599 | -0.050354 | 123.111 | 122.9004 | 122.8134 | -0.48065 | 123.0286 | 123.0148 | 122.9507 | -0.41657
4461.9844 | 123.2162 | -122.8592 | 0.18768 | -0.26001 | 0.03215 | 0.0065796 | 0.0072547 | -0.011602 | -0.0020572 | -0.011002 | -0.24132 | -0.012341 | -0.0068936 | -0.001976 | 0.0028263 | -0.017425 | 0.14648 | 0.12817 | 0.059509 | 0.13275 | 0.43488 | 0.032043 | -0.14191 | 0.059509 | 0.1236 | -0.004578 | 0.32044 | 0.27008 | -0.10071 | -0.15106 | 122.8912 | 122.7173 | 0.24719 | 122.9874 | 122.9919 | 0.27466 | -0.041199 | 122.7585 | 122.7081 | 0.13275 | 122.9187 | 122.8546 | 0.14648 | 0.082398 | 123.2941 | 123.0057 | 122.9187 | -0.32959 | 123.1796 | 123.1293 | 122.9828 | -0.33874
4463.6719 | 123.175 | -122.8592 | 0.17853 | -0.2829 | 0.034287 | 0.0065796 | 0.012809 | -0.010534 | -0.0031254 | -0.011856 | -0.22606 | -0.013836 | -0.0051846 | -0.0028306 | 0.0011173 | -0.016143 | 0.17395 | 0.21515 | 0.15564 | 0.16937 | 0.3891 | 0.022888 | -0.15106 | 0.09613 | 0.17395 | 0.059509 | 0.31586 | 0.28839 | -0.086975 | -0.12817 | 122.8821 | 122.7081 | 0.21057 | 123.0743 | 123.0286 | 0.32044 | -0.004578 | 122.7722 | 122.731 | 0.13733 | 122.9553 | 122.9187 | 0.18768 | 0.10986 | 123.2483 | 123.0331 | 123.0148 | -0.32959 | 123.175 | 123.1476 | 123.0331 | -0.3067
4465.375 | 123.0972 | -122.8821 | 0.22888 | 0.1825 | 0.033432 | 0.007434 | 0.0059729 | -0.0079702 | -0.0018436 | -0.0077973 | 0.15541 | -0.015545 | -0.0056118 | -0.0028306 | 0.0062441 | -0.016784 | 0.086975 | 0.10071 | 0.045776 | 0.041199 | 0.21515 | -0.082397 | -0.26093 | 0.10071 | 0.11902 | 0.032043 | 0.17395 | 0.14648 | -0.16937 | -0.20599 | 122.7997 | 122.6212 | -0.013733 | 122.9828 | 122.9233 | 0.30212 | -0.14191 | 122.7127 | 122.6761 | -0.054932 | 122.9828 | 122.9141 | 0.23804 | -0.082398 | 123.0972 | 122.9691 | 122.9279 | -0.48981 | 123.056 | 123.0286 | 123.0011 | -0.43488
4467.0781 | 123.1155 | -122.8683 | 0.20599 | 0.052795 | 0.031082 | 0.0067932 | 0.0074683 | -0.009252 | -0.0071842 | -0.011429 | 0.071487 | -0.014905 | -0.0053982 | -0.0045394 | 0.0019717 | -0.015716 | 0.10986 | 0.11902 | 0.10071 | 0.086975 | 0.31128 | -0.022888 | -0.19684 | 0.10071 | 0.15106 | 0.073242 | 0.23804 | 0.20599 | -0.11444 | -0.16479 | 122.8455 | 122.6715 | 0.10528 | 122.9874 | 122.9553 | 0.28381 | -0.096131 | 122.7539 | 122.7036 | 0.032043 | 122.9691 | 122.9416 | 0.23804 | 0 | 123.1796 | 122.9782 | 122.9691 | -0.40283 | 123.1064 | 123.0743 | 123.0194 | -0.37079
4468.7656 | 123.0927 | -122.8821 | 0.23346 | 0.014648 | 0.033218 | 0.0042298 | 0.0070409 | -0.009252 | 0.0054196 | -0.0084381 | 0.0028229 | -0.0095639 | -0.0073208 | -0.00069421 | 0.0066715 | -0.02063 | 0.064087 | -0.009155 | -0.059509 | -0.018311 | 0.28381 | -0.09613 | -0.2655 | -0.013733 | 0.009155 | -0.11902 | 0.21057 | 0.17395 | -0.18768 | -0.24261 | 122.7859 | 122.6166 | 0.050354 | 122.8729 | 122.8638 | 0.24719 | -0.16937 | 122.6944 | 122.6395 | -0.022888 | 122.8683 | 122.7631 | 0.1236 | -0.059509 | 123.1659 | 122.9462 | 122.8226 | -0.49896 | 123.0927 | 123.056 | 122.8912 | -0.47607
4470.4531 | 123.2208 | -122.8409 | 0.20142 | -0.13031 | 0.036209 | 0.007434 | 0.0061865 | -0.0079702 | 0.00093342 | -0.0088653 | -0.19554 | -0.0117 | -0.00668 | -0.0030442 | 0.0062441 | -0.019561 | 0.14191 | 0.10529 | 0.022888 | 0.082397 | 0.3479 | -0.068665 | -0.21973 | 0.086975 | 0.11902 | -0.041199 | 0.2243 | 0.20599 | -0.15106 | -0.19684 | 122.7722 | 122.6212 | 0.14648 | 122.9462 | 122.9233 | 0.30212 | -0.059509 | 122.6898 | 122.644 | 0.022888 | 122.9279 | 122.7997 | 0.15564 | 0.004578 | 123.1888 | 122.9828 | 122.8638 | -0.42114 | 123.0652 | 123.0469 | 122.9599 | -0.39825
4472.1719 | 123.2117 | -122.8546 | 0.20142 | -0.092163 | 0.035782 | 0.0061524 | 0.0046911 | -0.0077566 | 0.0026424 | -0.0075837 | -0.16502 | -0.012555 | -0.0079618 | -0.0028306 | 0.0073123 | -0.016143 | 0.11902 | 0.11902 | 0.027466 | 0.07782 | 0.33417 | -0.054932 | -0.19684 | 0.073242 | 0.11444 | -0.032043 | 0.23346 | 0.18768 | -0.15106 | -0.21515 | 122.7997 | 122.6578 | 0.13275 | 122.9736 | 122.9324 | 0.27466 | -0.082397 | 122.7036 | 122.6395 | 0.032043 | 122.9279 | 122.8226 | 0.18311 | -0.013733 | 123.1888 | 122.9736 | 122.8821 | -0.39825 | 123.0881 | 123.0423 | 122.9691 | -0.41657
4473.8594 | 123.1522 | -122.8638 | 0.18768 | 0.014648 | 0.032578 | 0.0065796 | 0.0096045 | -0.011175 | -0.006116 | -0.010788 | 0.079117 | -0.015118 | -0.0058254 | -0.0041122 | 0.00026273 | -0.017425 | 0.07782 | 0.14648 | 0.10071 | 0.10529 | 0.32501 | 0 | -0.19684 | 0.091553 | 0.17853 | 0.086975 | 0.24719 | 0.20142 | -0.10529 | -0.15106 | 122.8638 | 122.6669 | 0.13733 | 123.0103 | 122.9691 | 0.30212 | -0.10986 | 122.7585 | 122.7127 | 0.059509 | 122.9553 | 122.9507 | 0.23804 | 0.013733 | 123.1888 | 122.9416 | 122.9645 | -0.38452 | 123.111 | 123.0652 | 123.0423 | -0.33874
4475.5625 | 123.0972 | -122.8729 | 0.21057 | 0.15961 | 0.033646 | 0.0059388 | 0.0066137 | -0.009252 | -0.006116 | -0.0088653 | 0.10963 | -0.013409 | -0.0071072 | -0.0026168 | 0.0019717 | -0.015716 | 0.07782 | 0.12817 | 0.10071 | 0.073242 | 0.28381 | -0.022888 | -0.18768 | 0.10071 | 0.16022 | 0.068665 | 0.21973 | 0.1831 | -0.11902 | -0.16479 | 122.85 | 122.6852 | 0.073242 | 123.0011 | 122.9462 | 0.26092 | -0.13275 | 122.7539 | 122.7081 | 0.009156 | 122.9736 | 122.9416 | 0.23346 | -0.027466 | 123.1567 | 122.9507 | 122.9736 | -0.39825 | 123.0927 | 123.056 | 123.0331 | -0.37537
4477.2656 | 123.23 | -122.8638 | 0.1831 | -0.2066 | 0.033859 | 0.0078614 | 0.0051183 | -0.0096792 | 0.00050622 | -0.0095063 | -0.21843 | -0.011487 | -0.0056118 | -0.00069421 | 0.0070987 | -0.018707 | 0.16022 | 0.09613 | 0.032043 | 0.10071 | 0.3891 | -0.013733 | -0.16479 | 0.059509 | 0.12817 | -0.013733 | 0.25177 | 0.21515 | -0.15106 | -0.19684 | 122.85 | 122.699 | 0.20599 | 122.9599 | 122.9645 | 0.2655 | -0.022888 | 122.7127 | 122.6669 | 0.068665 | 122.9233 | 122.85 | 0.18311 | 0.032044 | 123.2529 | 123.024 | 122.8958 | -0.3479 | 123.1155 | 123.0789 | 122.9919 | -0.37994
4478.9688 | 123.1796 | -122.8546 | 0.19684 | -0.21423 | 0.0298 | 0.0087158 | 0.0083227 | -0.0090384 | -0.0029118 | -0.0095063 | -0.24132 | -0.01405 | -0.0079618 | -0.0041122 | 0.0017581 | -0.017639 | 0.19226 | 0.24719 | 0.17395 | 0.17853 | 0.37537 | 0.041199 | -0.12817 | 0.11902 | 0.21973 | 0.068665 | 0.29755 | 0.25635 | -0.068665 | -0.12817 | 122.8958 | 122.7264 | 0.17853 | 123.1018 | 123.0331 | 0.3067 | -0.004577 | 122.7859 | 122.7264 | 0.10071 | 122.9736 | 122.9233 | 0.19684 | 0.05951 | 123.23 | 123.0469 | 123.0286 | -0.32501 | 123.1522 | 123.111 | 123.0743 | -0.32501
4480.6719 | 123.1934 | -122.8638 | 0.19226 | -0.22186 | 0.032364 | 0.0059388 | 0.0085363 | -0.0096792 | -0.0018436 | -0.010361 | -0.24132 | -0.013196 | -0.0047574 | -0.0017624 | 0.0030399 | -0.018493 | 0.1236 | 0.14191 | 0.07782 | 0.10986 | 0.41199 | 0.009155 | -0.15564 | 0.068665 | 0.14648 | 0.022888 | 0.31128 | 0.27924 | -0.10986 | -0.14648 | 122.8729 | 122.7081 | 0.21973 | 123.0057 | 122.9736 | 0.2655 | -0.068665 | 122.7539 | 122.7173 | 0.11902 | 122.9324 | 122.8867 | 0.16937 | 0.086975 | 123.2758 | 122.9874 | 122.9416 | -0.3479 | 123.175 | 123.143 | 123.0103 | -0.33874
4482.375 | 123.0972 | -122.8683 | 0.21973 | 0.0070193 | 0.033005 | 0.006366 | 0.0066137 | -0.008611 | 0.0047788 | -0.0092927 | -0.042954 | -0.010418 | -0.0064664 | -0.0028306 | 0.010089 | -0.018921 | 0.036621 | 0.018311 | -0.073242 | 0.004578 | 0.28839 | -0.09613 | -0.2655 | 0 | 0.027466 | -0.13733 | 0.20599 | 0.1831 | -0.20142 | -0.25635 | 122.7722 | 122.6028 | 0.068664 | 122.8867 | 122.8729 | 0.27008 | -0.18311 | 122.6669 | 122.612 | -0.013733 | 122.8683 | 122.731 | 0.11902 | -0.036622 | 123.1567 | 122.905 | 122.7951 | -0.48523 | 123.0743 | 123.0515 | 122.8958 | -0.47608
4484.0781 | 123.2025 | -122.8271 | 0.1831 | -0.076904 | 0.031082 | 0.0057252 | 0.010245 | -0.010106 | -0.004407 | -0.0090791 | -0.12688 | -0.01405 | -0.003262 | -0.003685 | 4.9132e-05 | -0.016998 | 0.17395 | 0.27924 | 0.20142 | 0.17395 | 0.35248 | 0.045776 | -0.13733 | 0.19684 | 0.28839 | 0.16937 | 0.25177 | 0.23346 | -0.045776 | -0.11444 | 122.8729 | 122.6898 | 0.16937 | 123.1064 | 123.0011 | 0.31128 | -0.009155 | 122.7814 | 122.7127 | 0.068665 | 123.024 | 122.9965 | 0.28381 | 0.050354 | 123.1796 | 123.0011 | 123.0286 | -0.32043 | 123.0789 | 123.0606 | 123.1155 | -0.29755
4485.7969 | 123.1155 | -122.8638 | 0.21515 | 0.037537 | 0.030441 | 0.0078614 | 0.0027685 | -0.01032 | -0.005048 | -0.011002 | 0.102 | -0.012341 | -0.008389 | -0.0024032 | 0.0047489 | -0.016143 | 0.091553 | 0.1236 | 0.086975 | 0.091553 | 0.3067 | -0.041199 | -0.17395 | 0.086975 | 0.15106 | 0.059509 | 0.24261 | 0.21057 | -0.10986 | -0.14648 | 122.8226 | 122.6898 | 0.091553 | 122.9874 | 122.9553 | 0.2655 | -0.1236 | 122.7539 | 122.7173 | 0.027466 | 122.9507 | 122.9233 | 0.20599 | -0.004578 | 123.1705 | 122.9553 | 122.9507 | -0.3891 | 123.1064 | 123.0743 | 123.0148 | -0.36163
4487.4844 | 123.1476 | -122.8455 | 0.18768 | 0.029907 | 0.030014 | 0.009143 | 0.0059729 | -0.010747 | -0.0048344 | -0.011642 | 0.04097 | -0.01405 | -0.008389 | -0.0026168 | 0.0036807 | -0.016357 | 0.1236 | 0.11902 | 0.091553 | 0.091553 | 0.32501 | -0.009155 | -0.15564 | 0.086975 | 0.16937 | 0.091553 | 0.24719 | 0.19684 | -0.11444 | -0.16022 | 122.8363 | 122.6898 | 0.13733 | 122.9645 | 122.937 | 0.24719 | -0.064087 | 122.731 | 122.6852 | 0.059509 | 122.9324 | 122.937 | 0.25177 | 0.009155 | 123.1705 | 122.9691 | 122.937 | -0.34332 | 123.0927 | 123.0423 | 123.0148 | -0.3479
4489.1719 | 123.1476 | -122.8683 | 0.21057 | 0.12146 | 0.036423 | 0.0055114 | 0.0042639 | -0.01032 | 0.0037106 | -0.0069427 | 0.04097 | -0.010846 | -0.009457 | -0.0024032 | 0.0073123 | -0.016998 | 0.036621 | -0.036621 | -0.07782 | -0.027466 | 0.28839 | -0.1236 | -0.28381 | 0.013733 | 0.013733 | -0.086975 | 0.21515 | 0.19226 | -0.19684 | -0.2243 | 122.7448 | 122.5845 | 0.07782 | 122.8317 | 122.8409 | 0.25635 | -0.17395 | 122.6715 | 122.644 | 0.004578 | 122.8821 | 122.7814 | 0.13733 | -0.01831 | 123.1567 | 122.905 | 122.7905 | -0.49438 | 123.0835 | 123.0606 | 122.8821 | -0.43488
4490.8594 | 123.1338 | -122.8775 | 0.24261 | 0.12146 | 0.036636 | 0.004657 | 0.0059729 | -0.009252 | 0.0041378 | -0.010147 | 0.071487 | -0.011273 | -0.0075344 | -0.00048061 | 0.0062441 | -0.016357 | 0.027466 | -0.041199 | -0.09613 | -0.018311 | 0.25635 | -0.11444 | -0.27466 | 0.004578 | -0.018311 | -0.10986 | 0.20599 | 0.19226 | -0.19226 | -0.24719 | 122.7631 | 122.6028 | 0.013733 | 122.8363 | 122.8592 | 0.25635 | -0.21515 | 122.6852 | 122.6303 | -0.036621 | 122.8821 | 122.7676 | 0.13733 | -0.050354 | 123.1339 | 122.905 | 122.7814 | -0.51727 | 123.0835 | 123.0698 | 122.8592 | -0.48981
4492.5469 | 123.1293 | -122.85 | 0.21973 | 0.11383 | 0.035355 | 0.0076478 | 0.0057593 | -0.008611 | 0.00050622 | -0.0088653 | 0.063858 | -0.011273 | -0.008389 | -0.00069421 | 0.0066715 | -0.016357 | 0.022888 | -0.036621 | -0.068665 | -0.013733 | 0.28381 | -0.10529 | -0.28381 | 0.004578 | 0.027466 | -0.07782 | 0.21973 | 0.17395 | -0.18768 | -0.24719 | 122.7448 | 122.5662 | 0.064086 | 122.8134 | 122.8363 | 0.27008 | -0.19684 | 122.6624 | 122.6028 | 0 | 122.8546 | 122.7722 | 0.16937 | -0.045777 | 123.1338 | 122.8729 | 122.7814 | -0.50354 | 123.0698 | 123.024 | 122.8775 | -0.46692
4494.2344 | 123.0789 | -122.8821 | 0.21057 | -0.046387 | 0.036423 | 0.0055114 | 0.0051183 | -0.007543 | 0.0022152 | -0.0075837 | -0.058212 | -0.011273 | -0.008389 | -0.0030442 | 0.0058169 | -0.01828 | 0.10071 | 0.050354 | -0.027466 | 0.032043 | 0.29755 | -0.068665 | -0.21973 | 0.004578 | 0.036621 | -0.11444 | 0.20142 | 0.19684 | -0.19684 | -0.2243 | 122.8134 | 122.6624 | 0.086975 | 122.9324 | 122.9141 | 0.25177 | -0.10986 | 122.6852 | 122.6578 | -0.009155 | 122.8867 | 122.7676 | 0.10986 | -0.013733 | 123.1796 | 122.9828 | 122.8546 | -0.4303 | 123.0835 | 123.0789 | 122.9187 | -0.43488
4495.9375 | 123.2025 | -122.8592 | 0.21057 | -0.13031 | 0.035782 | 0.0048706 | 0.0070409 | -0.010106 | 0.0022152 | -0.0063019 | -0.096359 | -0.012768 | -0.009457 | -0.0026168 | 0.0051761 | -0.015716 | 0.12817 | 0.09613 | 0.027466 | 0.068665 | 0.33875 | -0.022888 | -0.21973 | 0.064087 | 0.11902 | -0.041199 | 0.2243 | 0.19684 | -0.16937 | -0.21057 | 122.8363 | 122.6395 | 0.12817 | 122.9553 | 122.9279 | 0.28839 | -0.082397 | 122.6898 | 122.6486 | 0.013733 | 122.9233 | 122.818 | 0.16937 | -0.013733 | 123.1979 | 122.9874 | 122.8867 | -0.4303 | 123.0835 | 123.056 | 122.9782 | -0.42114
4497.625 | 123.1567 | -122.8729 | 0.21057 | -0.084534 | 0.036423 | 0.0044434 | 0.010032 | -0.0073294 | 0.0026424 | -0.0086517 | -0.13451 | -0.011487 | -0.0051846 | -0.00026701 | 0.0058169 | -0.017212 | 0.10071 | 0.11444 | 0.018311 | 0.068665 | 0.31586 | -0.068665 | -0.21515 | 0.068665 | 0.11902 | -0.032043 | 0.21973 | 0.1831 | -0.16022 | -0.21515 | 122.8043 | 122.6578 | 0.10529 | 122.9874 | 122.9416 | 0.28381 | -0.10986 | 122.7127 | 122.6578 | 0.009156 | 122.9416 | 122.8409 | 0.18311 | -0.027466 | 123.1888 | 122.9736 | 122.8912 | -0.42572 | 123.0927 | 123.056 | 122.9919 | -0.42572
4499.3125 | 123.1338 | -122.8638 | 0.21515 | -0.084534 | 0.036636 | 0.0052978 | 0.0091773 | -0.010961 | 0.00071982 | -0.0058747 | -0.058212 | -0.0095639 | -0.0043302 | 0.00016019 | 0.0060305 | -0.017639 | 0.11444 | 0.10529 | 0.022888 | 0.059509 | 0.32044 | -0.064087 | -0.26093 | 0.036621 | 0.07782 | -0.059509 | 0.2243 | 0.1831 | -0.17395 | -0.21057 | 122.7997 | 122.6028 | 0.10529 | 122.9691 | 122.9233 | 0.32043 | -0.10071 | 122.6898 | 122.6532 | 0.009155 | 122.9004 | 122.8043 | 0.15106 | -0.032044 | 123.1842 | 122.9782 | 122.8867 | -0.47607 | 123.0881 | 123.0469 | 122.9416 | -0.42572
4501.0156 | 123.1842 | -122.8409 | 0.1831 | -0.19135 | 0.031296 | 0.0055114 | 0.010886 | -0.010106 | -0.004407 | -0.010147 | -0.11162 | -0.017682 | -0.006039 | -0.001976 | 0.00090353 | -0.017212 | 0.18768 | 0.27466 | 0.20142 | 0.19226 | 0.37079 | 0.050354 | -0.11444 | 0.16937 | 0.28381 | 0.14648 | 0.26093 | 0.24261 | -0.050354 | -0.11902 | 122.8912 | 122.7264 | 0.18768 | 123.1155 | 123.0331 | 0.3067 | 0.004578 | 122.7905 | 122.7219 | 0.07782 | 123.0103 | 122.9874 | 0.2655 | 0.05951 | 123.2117 | 123.0286 | 123.0423 | -0.29755 | 123.1018 | 123.0835 | 123.1247 | -0.30212
4502.7031 | 123.2391 | -122.85 | 0.17395 | -0.13031 | 0.030014 | 0.0059388 | 0.010886 | -0.010534 | -0.005048 | -0.013779 | -0.065842 | -0.015545 | -0.0056118 | -0.0013352 | 0.00068993 | -0.017212 | 0.19226 | 0.2655 | 0.19684 | 0.17395 | 0.32959 | 0.050354 | -0.11902 | 0.17853 | 0.27924 | 0.16937 | 0.26093 | 0.22888 | -0.073242 | -0.10986 | 122.9004 | 122.731 | 0.15564 | 123.1155 | 123.024 | 0.29297 | 0.018311 | 122.7768 | 122.7402 | 0.086975 | 123.0286 | 123.0194 | 0.27924 | 0.054932 | 123.1796 | 123.0423 | 123.0469 | -0.29297 | 123.111 | 123.0789 | 123.1293 | -0.28381
4504.4531 | 123.1476 | -122.8775 | 0.20599 | -0.076904 | 0.033005 | 0.009784 | 0.0042639 | -0.0088248 | 0.0043514 | -0.0073701 | -0.15739 | -0.011914 | -0.0068936 | -0.0017624 | 0.0075259 | -0.017425 | 0.12817 | 0.10986 | 0.009155 | 0.07782 | 0.32044 | -0.073242 | -0.21057 | 0.068665 | 0.082397 | -0.041199 | 0.2243 | 0.16479 | -0.16479 | -0.19684 | 122.8043 | 122.6669 | 0.11444 | 122.9874 | 122.9553 | 0.28839 | -0.07782 | 122.7127 | 122.6807 | 0.01831 | 122.9462 | 122.8363 | 0.15564 | -0.041199 | 123.1979 | 123.0057 | 122.8867 | -0.41657 | 123.1018 | 123.0423 | 122.9599 | -0.40283
4506.1406 | 123.175 | -122.8546 | 0.19226 | -0.21423 | 0.031509 | 0.0061524 | 0.011314 | -0.0094656 | -0.004407 | -0.0077973 | -0.2108 | -0.012982 | -0.0039028 | -0.00090781 | 0.0017581 | -0.016143 | 0.12817 | 0.13733 | 0.07782 | 0.11902 | 0.42114 | 0.004578 | -0.15564 | 0.064087 | 0.14648 | 0.032043 | 0.31586 | 0.25635 | -0.09613 | -0.13733 | 122.8592 | 122.699 | 0.22888 | 122.9919 | 122.9736 | 0.27466 | -0.064087 | 122.7585 | 122.7173 | 0.1236 | 122.9187 | 122.8867 | 0.16937 | 0.064087 | 123.2758 | 122.9828 | 122.9324 | -0.3479 | 123.1705 | 123.111 | 123.0011 | -0.32959
4507.8281 | 123.1842 | -122.85 | 0.18768 | -0.13794 | 0.030869 | 0.0067932 | 0.010032 | -0.010747 | -0.0052616 | -0.011215 | -0.10399 | -0.013836 | -0.0051846 | -0.003685 | 0.0011173 | -0.015716 | 0.17853 | 0.26093 | 0.19684 | 0.1831 | 0.35706 | 0.041199 | -0.12817 | 0.1831 | 0.29755 | 0.16022 | 0.2655 | 0.23804 | -0.054932 | -0.10986 | 122.8912 | 122.7219 | 0.16937 | 123.111 | 123.0331 | 0.31128 | -0.009155 | 122.7951 | 122.7402 | 0.07782 | 123.0331 | 123.0103 | 0.27008 | 0.050354 | 123.2071 | 123.0286 | 123.0469 | -0.31586 | 123.1155 | 123.0881 | 123.1476 | -0.29755
4509.5312 | 123.1888 | -122.8546 | 0.21515 | -0.24475 | 0.032578 | 0.008075 | 0.0093909 | -0.01032 | -0.0037662 | -0.010361 | -0.24132 | -0.014691 | -0.0071072 | -0.0032578 | 0.0023989 | -0.018921 | 0.16479 | 0.2243 | 0.15106 | 0.16479 | 0.40741 | 0.022888 | -0.11444 | 0.09613 | 0.18768 | 0.054932 | 0.3067 | 0.26093 | -0.086975 | -0.1236 | 122.8775 | 122.7402 | 0.19226 | 123.0789 | 123.0194 | 0.27924 | -0.050354 | 122.7676 | 122.731 | 0.091553 | 122.9507 | 122.9095 | 0.17853 | 0.045776 | 123.262 | 123.0194 | 123.0057 | -0.32959 | 123.1613 | 123.1155 | 123.0423 | -0.33875
4511.2188 | 123.1842 | -122.8409 | 0.19684 | -0.26764 | 0.031082 | 0.0067932 | 0.0070409 | -0.0083974 | -0.0035526 | -0.0090791 | -0.24132 | -0.013623 | -0.0043302 | 0.00058739 | 0.0041079 | -0.017425 | 0.15106 | 0.19226 | 0.11444 | 0.15106 | 0.39368 | 0.013733 | -0.14191 | 0.086975 | 0.15564 | 0.041199 | 0.3067 | 0.25635 | -0.091553 | -0.14648 | 122.8546 | 122.699 | 0.19684 | 123.0331 | 122.9919 | 0.29297 | -0.045776 | 122.7493 | 122.6944 | 0.10986 | 122.9279 | 122.8821 | 0.18768 | 0.05951 | 123.2346 | 122.9919 | 122.9553 | -0.33875 | 123.1476 | 123.0972 | 122.9965 | -0.34332
4512.9062 | 123.1934 | -122.8363 | 0.17853 | -0.18372 | 0.032578 | 0.0065796 | 0.0087499 | -0.009252 | -0.005048 | -0.011002 | -0.14977 | -0.016186 | -0.004971 | -0.0030442 | 0.0019717 | -0.016998 | 0.20142 | 0.29297 | 0.19684 | 0.20142 | 0.36621 | 0.041199 | -0.13275 | 0.19226 | 0.27466 | 0.13733 | 0.27466 | 0.23346 | -0.068665 | -0.11902 | 122.8775 | 122.7036 | 0.18768 | 123.1293 | 123.0377 | 0.33417 | 0.022888 | 122.7676 | 122.7173 | 0.09613 | 123.0286 | 122.9736 | 0.25635 | 0.054931 | 123.2025 | 123.0377 | 123.0331 | -0.31128 | 123.111 | 123.0698 | 123.111 | -0.29755
4514.5938 | 123.1476 | -122.8729 | 0.19684 | 0.11383 | 0.035782 | 0.006366 | 0.0036231 | -0.0094656 | 0.0043514 | -0.0084381 | 0.14015 | -0.013409 | -0.0086026 | -0.0011216 | 0.0081667 | -0.01828 | 0.027466 | 0.004578 | -0.07782 | -0.018311 | 0.27008 | -0.11444 | -0.27924 | 0.054932 | 0.064087 | -0.032043 | 0.17853 | 0.14648 | -0.1831 | -0.2243 | 122.7585 | 122.5937 | 0.073243 | 122.8775 | 122.8546 | 0.26092 | -0.16937 | 122.6898 | 122.6486 | -0.01831 | 122.9279 | 122.8409 | 0.19226 | -0.050354 | 123.143 | 122.9004 | 122.7951 | -0.47607 | 123.0515 | 123.0194 | 122.937 | -0.42114
4516.2812 | 123.1338 | -122.8729 | 0.19684 | 0.22064 | 0.034927 | 0.0050842 | 0.0027685 | -0.0090384 | -0.00077538 | -0.0069427 | 0.14778 | -0.011273 | -0.008389 | -0.0030442 | 0.0075259 | -0.016784 | 0.059509 | 0.041199 | -0.004578 | -0.004578 | 0.25635 | -0.10071 | -0.26093 | 0.086975 | 0.10986 | 0.004578 | 0.15106 | 0.11902 | -0.15564 | -0.22888 | 122.7722 | 122.612 | 0.05951 | 122.9141 | 122.8683 | 0.25635 | -0.13733 | 122.7173 | 122.644 | -0.045776 | 122.9599 | 122.8775 | 0.23346 | -0.077819 | 123.1293 | 122.9324 | 122.8683 | -0.45776 | 123.024 | 122.9919 | 122.9828 | -0.42572
4518.0312 | 123.1384 | -122.8912 | 0.21973 | 0.13672 | 0.035355 | 0.0057252 | 0.0064001 | -0.0094656 | -0.00034818 | -0.0071563 | 0.17067 | -0.012982 | -0.0092434 | -0.0051804 | 0.0083805 | -0.016784 | 0.10986 | 0.10071 | 0.045776 | 0.045776 | 0.23804 | -0.068665 | -0.24261 | 0.082397 | 0.13275 | 0.022888 | 0.16479 | 0.1236 | -0.16022 | -0.21515 | 122.8226 | 122.6486 | 0.01831 | 122.9919 | 122.937 | 0.28839 | -0.10986 | 122.731 | 122.6761 | -0.054932 | 122.9736 | 122.9141 | 0.23804 | -0.096131 | 123.1293 | 123.0011 | 122.937 | -0.46234 | 123.056 | 123.0148 | 123.024 | -0.43488
4519.7188 | 123.1293 | -122.9004 | 0.21515 | 0.090942 | 0.035782 | 0.0067932 | 0.0066137 | -0.0073294 | 0.0028562 | -0.0075837 | 0.056228 | -0.0117 | -0.0079618 | -0.0032578 | 0.0090213 | -0.016998 | 0.013733 | -0.059509 | -0.10071 | -0.045776 | 0.27008 | -0.11444 | -0.28839 | -0.018311 | -0.004578 | -0.10986 | 0.21057 | 0.16937 | -0.21057 | -0.24719 | 122.7859 | 122.612 | 0.054932 | 122.8409 | 122.8546 | 0.24262 | -0.20142 | 122.6898 | 122.6532 | -0.004578 | 122.8821 | 122.7905 | 0.13733 | -0.045776 | 123.1705 | 122.9141 | 122.7997 | -0.50354 | 123.111 | 123.0698 | 122.8958 | -0.46234
4521.4688 | 123.1934 | -122.8683 | 0.18768 | -0.25238 | 0.036209 | 0.0061524 | 0.0087499 | -0.012029 | -0.00163 | -0.0090791 | -0.17265 | -0.013409 | -0.0053982 | -0.0030442 | 0.0030399 | -0.016998 | 0.1236 | 0.16022 | 0.09613 | 0.1236 | 0.41199 | 0.036621 | -0.14648 | 0.068665 | 0.15564 | 0.032043 | 0.32044 | 0.27466 | -0.11902 | -0.13733 | 122.905 | 122.7219 | 0.2243 | 123.0286 | 122.9919 | 0.27008 | -0.064087 | 122.7493 | 122.731 | 0.13275 | 122.937 | 122.9004 | 0.16937 | 0.086975 | 123.2803 | 122.9919 | 122.9645 | -0.33417 | 123.1888 | 123.143 | 123.024 | -0.32501
4523.1562 | 123.2208 | -122.8455 | 0.18768 | -0.054016 | 0.029587 | 0.0078614 | 0.0072547 | -0.009252 | -0.0065434 | -0.010574 | -0.012436 | -0.015332 | -0.00668 | -0.0030442 | 4.9132e-05 | -0.014221 | 0.10986 | 0.17395 | 0.14191 | 0.13275 | 0.32501 | 0.004578 | -0.15564 | 0.16479 | 0.23346 | 0.14191 | 0.24719 | 0.22888 | -0.082397 | -0.12817 | 122.85 | 122.6898 | 0.13733 | 123.0194 | 122.9782 | 0.28839 | -0.07782 | 122.7631 | 122.7173 | 0.059509 | 123.0103 | 122.9874 | 0.27008 | 0.041199 | 123.1705 | 122.9553 | 122.9874 | -0.34332 | 123.0927 | 123.0743 | 123.0789 | -0.31586
4524.8438 | 123.1201 | -122.8638 | 0.21057 | 0.029907 | 0.031937 | 0.009143 | 0.0091773 | -0.01032 | -0.002698 | -0.010361 | 0.094375 | -0.01405 | -0.0043302 | -0.0013352 | 0.0017581 | -0.015716 | 0.091553 | 0.10986 | 0.09613 | 0.086975 | 0.29755 | -0.018311 | -0.18768 | 0.11444 | 0.14191 | 0.082397 | 0.23346 | 0.20142 | -0.1236 | -0.16022 | 122.8455 | 122.6761 | 0.086975 | 122.9736 | 122.9507 | 0.27466 | -0.11902 | 122.7402 | 122.7036 | 0.022888 | 122.9782 | 122.9462 | 0.24261 | -0.009155 | 123.1613 | 122.9553 | 122.9599 | -0.39825 | 123.0972 | 123.0652 | 123.0057 | -0.37079
4526.5469 | 123.0698 | -122.8546 | 0.21973 | 0.090942 | 0.034714 | 0.0050842 | 0.0085363 | -0.012456 | -0.0020572 | -0.0092927 | 0.15541 | -0.012982 | -0.0062528 | -0.001976 | 0.0049625 | -0.017212 | 0.10986 | 0.14191 | 0.068665 | 0.054932 | 0.24719 | -0.059509 | -0.21515 | 0.10529 | 0.11444 | 0.032043 | 0.18768 | 0.14648 | -0.14191 | -0.21515 | 122.7951 | 122.6395 | 0.027465 | 122.9965 | 122.9095 | 0.27008 | -0.10986 | 122.7127 | 122.6395 | -0.032044 | 122.9599 | 122.8867 | 0.24719 | -0.073243 | 123.1018 | 122.9645 | 122.9233 | -0.43488 | 123.0423 | 123.0011 | 122.9691 | -0.43488
4528.2656 | 123.1613 | -122.8317 | 0.18768 | -0.18372 | 0.031296 | 0.0076478 | 0.010673 | -0.0094656 | -0.0031254 | -0.010147 | -0.14214 | -0.013623 | -0.0051846 | -0.003685 | 0.0028263 | -0.017425 | 0.21057 | 0.2655 | 0.19684 | 0.19684 | 0.37537 | 0.050354 | -0.10529 | 0.17853 | 0.25635 | 0.13275 | 0.27008 | 0.21515 | -0.07782 | -0.12817 | 122.8821 | 122.7264 | 0.18768 | 123.0972 | 123.0286 | 0.30212 | 0.022888 | 122.7539 | 122.7036 | 0.082398 | 123.0103 | 122.9645 | 0.26093 | 0.027466 | 123.2071 | 123.0423 | 123.0286 | -0.29297 | 123.1018 | 123.0469 | 123.0881 | -0.31586
4530 | 123.2254 | -122.8546 | 0.1831 | -0.092163 | 0.030655 | 0.0089294 | 0.0068273 | -0.010747 | -0.0035526 | -0.011429 | -0.096359 | -0.014905 | -0.007748 | -0.003685 | 0.00068993 | -0.018707 | 0.16479 | 0.23804 | 0.16022 | 0.14191 | 0.36163 | 0.009155 | -0.14191 | 0.21057 | 0.25177 | 0.16022 | 0.26093 | 0.22888 | -0.07782 | -0.1236 | 122.8638 | 122.7127 | 0.17853 | 123.0927 | 122.9965 | 0.28381 | -0.01831 | 122.7768 | 122.731 | 0.07782 | 123.0652 | 123.0148 | 0.28381 | 0.045777 | 123.2162 | 123.0194 | 123.0148 | -0.32501 | 123.1155 | 123.0835 | 123.1064 | -0.3067
4531.6875 | 123.2117 | -122.8409 | 0.18768 | -0.015869 | 0.031296 | 0.0082886 | 0.0074683 | -0.0088248 | -0.002698 | -0.010361 | -0.0048066 | -0.014905 | -0.008389 | -0.0011216 | 0.0041079 | -0.016357 | 0.11444 | 0.14648 | 0.10986 | 0.10986 | 0.31586 | -0.009155 | -0.17853 | 0.14191 | 0.20142 | 0.10986 | 0.25177 | 0.20142 | -0.10071 | -0.13275 | 122.8317 | 122.6624 | 0.12817 | 122.9874 | 122.9507 | 0.28839 | -0.073242 | 122.7402 | 122.7081 | 0.064087 | 122.9828 | 122.9507 | 0.24261 | 0.013733 | 123.1567 | 122.9553 | 122.9507 | -0.36621 | 123.0927 | 123.0423 | 123.0423 | -0.32043
4533.3906 | 123.2254 | -122.8317 | 0.20142 | -0.10742 | 0.031937 | 0.010211 | 0.0064001 | -0.0073294 | -0.0029118 | -0.0075837 | -0.17265 | -0.012982 | -0.0081754 | -0.0043258 | 0.0030399 | -0.020202 | 0.24261 | 0.27924 | 0.20142 | 0.19226 | 0.36621 | 0.036621 | -0.1236 | 0.21057 | 0.27924 | 0.15564 | 0.26093 | 0.21973 | -0.050354 | -0.082397 | 122.8683 | 122.7081 | 0.16479 | 123.111 | 123.024 | 0.31586 | 0.041199 | 122.7814 | 122.7493 | 0.059509 | 123.0423 | 122.9874 | 0.23804 | 0.018311 | 123.1979 | 123.0743 | 123.0331 | -0.32501 | 123.0927 | 123.0515 | 123.111 | -0.28381
4535.0781 | 123.2162 | -122.85 | 0.17853 | -0.11505 | 0.031509 | 0.0067932 | 0.0111 | -0.009252 | -0.0037662 | -0.0090791 | -0.13451 | -0.015545 | -0.0079618 | -0.003685 | 0.0017581 | -0.017852 | 0.23804 | 0.25177 | 0.20599 | 0.18768 | 0.34332 | 0.032043 | -0.14191 | 0.21515 | 0.29297 | 0.15564 | 0.27008 | 0.2243 | -0.07782 | -0.11902 | 122.8821 | 122.7081 | 0.16479 | 123.1018 | 123.0377 | 0.32959 | 0.059509 | 122.7722 | 122.731 | 0.091553 | 123.0652 | 123.0057 | 0.27466 | 0.045776 | 123.1934 | 123.0881 | 123.056 | -0.32044 | 123.1201 | 123.0743 | 123.143 | -0.29755
4536.7656 | 123.0972 | -122.8775 | 0.20142 | 0.12146 | 0.028732 | 0.0059388 | 0.0029821 | -0.010961 | 0.00029262 | -0.0099335 | 0.079117 | -0.013623 | -0.0086026 | -0.0013352 | 0.0058169 | -0.016571 | 0.11444 | 0.11444 | 0.068665 | 0.059509 | 0.27008 | -0.054932 | -0.2243 | 0.12817 | 0.13275 | 0.041199 | 0.20142 | 0.17853 | -0.13733 | -0.16937 | 122.8226 | 122.6532 | 0.068665 | 122.9919 | 122.937 | 0.28381 | -0.086975 | 122.7402 | 122.7081 | 0 | 123.0057 | 122.9187 | 0.21057 | -0.022888 | 123.1476 | 122.9919 | 122.9462 | -0.42572 | 123.0789 | 123.056 | 123.0103 | -0.37079
4538.5 | 123.0743 | -122.8867 | 0.2243 | 0.13672 | 0.030228 | 0.009143 | 0.0042639 | -0.0094656 | 0.00029262 | -0.010574 | 0.094375 | -0.014691 | -0.0096706 | -0.0024032 | 0.0066715 | -0.018066 | 0.13733 | 0.1236 | 0.064087 | 0.059509 | 0.21515 | -0.064087 | -0.2243 | 0.12817 | 0.11902 | 0.045776 | 0.17395 | 0.13275 | -0.14648 | -0.19684 | 122.8226 | 122.6624 | -0.009155 | 123.0103 | 122.9462 | 0.28381 | -0.086975 | 122.7402 | 122.6898 | -0.050354 | 123.0148 | 122.9324 | 0.24261 | -0.091553 | 123.1018 | 123.024 | 122.9507 | -0.44861 | 123.0606 | 123.0194 | 123.0057 | -0.42114
4540.1875 | 123.0927 | -122.8821 | 0.23346 | -0.031128 | 0.036209 | 0.006366 | 0.0066137 | -0.0071158 | 0.0056332 | -0.0067291 | -0.096359 | -0.011487 | -0.007748 | -0.00026701 | 0.011585 | -0.020202 | 0.1236 | 0.045776 | -0.045776 | 0.027466 | 0.32959 | -0.068665 | -0.23804 | 0.018311 | 0.009155 | -0.12817 | 0.21973 | 0.1831 | -0.1831 | -0.24261 | 122.8134 | 122.644 | 0.096131 | 122.9279 | 122.9095 | 0.2655 | -0.10986 | 122.699 | 122.6395 | -0.013732 | 122.9004 | 122.7539 | 0.11444 | -0.050354 | 123.2117 | 123.0057 | 122.8363 | -0.4715 | 123.1018 | 123.0652 | 122.8912 | -0.47607
4541.9375 | 123.23 | -122.8363 | 0.18768 | -0.054016 | 0.030014 | 0.007434 | 0.0064001 | -0.0098928 | -0.0076114 | -0.010361 | -0.08873 | -0.013623 | -0.0092434 | -0.0026168 | 4.9132e-05 | -0.017212 | 0.18768 | 0.22888 | 0.16479 | 0.15106 | 0.3479 | 0.022888 | -0.15106 | 0.21057 | 0.27008 | 0.16022 | 0.26093 | 0.2243 | -0.068665 | -0.1236 | 122.8592 | 122.6852 | 0.16022 | 123.0652 | 122.9874 | 0.30212 | 0 | 122.7676 | 122.7127 | 0.073242 | 123.0469 | 122.9965 | 0.28381 | 0.036621 | 123.1842 | 123.024 | 123.0011 | -0.33874 | 123.0972 | 123.0606 | 123.1064 | -0.31128
4543.625 | 123.1796 | -122.8638 | 0.19684 | -0.19897 | 0.034714 | 0.0070068 | 0.0083227 | -0.010106 | -0.003339 | -0.0099335 | -0.26421 | -0.013196 | -0.0068936 | -0.00090781 | 0.0034671 | -0.016998 | 0.21515 | 0.21973 | 0.17853 | 0.19684 | 0.36621 | 0.027466 | -0.1236 | 0.15106 | 0.23346 | 0.082397 | 0.29755 | 0.25635 | -0.086975 | -0.1236 | 122.8912 | 122.7402 | 0.16937 | 123.0835 | 123.0606 | 0.32043 | 0.018311 | 122.7768 | 122.7402 | 0.10071 | 123.0148 | 122.9462 | 0.20599 | 0.05951 | 123.23 | 123.0789 | 123.0423 | -0.32043 | 123.1613 | 123.1201 | 123.0972 | -0.32043
4545.3438 | 123.2483 | -122.8455 | 0.17395 | -0.21423 | 0.037705 | 0.0072204 | 0.010245 | -0.0090384 | 0.0013608 | -0.0065155 | -0.27184 | -0.0117 | -0.0053982 | -0.0030442 | 0.0062441 | -0.020843 | 0.13733 | 0.10529 | 0.041199 | 0.10071 | 0.41199 | -0.004578 | -0.20142 | 0.07782 | 0.13275 | -0.004578 | 0.30212 | 0.24261 | -0.13275 | -0.16022 | 122.8409 | 122.644 | 0.23804 | 122.9507 | 122.9462 | 0.30212 | -0.036621 | 122.7127 | 122.6852 | 0.12817 | 122.9233 | 122.8409 | 0.15564 | 0.068665 | 123.2574 | 122.9828 | 122.8867 | -0.37537 | 123.1476 | 123.0881 | 122.9782 | -0.33417
4547.0312 | 123.2208 | -122.8455 | 0.18768 | -0.12268 | 0.032364 | 0.0042298 | 0.010886 | -0.010961 | -0.0037662 | -0.010361 | -0.14214 | -0.014691 | -0.0064664 | -0.0041122 | 0.0019717 | -0.016998 | 0.20599 | 0.27466 | 0.21057 | 0.19684 | 0.33417 | 0.036621 | -0.10071 | 0.19684 | 0.29755 | 0.15564 | 0.27466 | 0.23346 | -0.050354 | -0.10986 | 122.8821 | 122.7448 | 0.14648 | 123.1201 | 123.0423 | 0.29755 | 0.018311 | 122.7951 | 122.7356 | 0.086975 | 123.0423 | 123.0011 | 0.2655 | 0.045776 | 123.1796 | 123.0515 | 123.056 | -0.28839 | 123.1201 | 123.0789 | 123.143 | -0.29755
4548.7188 | 123.2346 | -122.8134 | 0.19226 | -0.1532 | 0.033005 | 0.0061524 | 0.0068273 | -0.0090384 | -0.0046206 | -0.0092927 | -0.11162 | -0.014905 | -0.004971 | -0.00090781 | 0.0013309 | -0.017212 | 0.20142 | 0.27008 | 0.1831 | 0.16937 | 0.35706 | 0.022888 | -0.13275 | 0.21515 | 0.28839 | 0.16937 | 0.24719 | 0.2243 | -0.068665 | -0.11902 | 122.8363 | 122.6807 | 0.16479 | 123.0835 | 122.9828 | 0.30212 | 0.009155 | 122.7448 | 122.6944 | 0.054931 | 123.0286 | 122.9828 | 0.28839 | 0.032043 | 123.1705 | 123.0148 | 122.9965 | -0.32501 | 123.0606 | 123.0377 | 123.1018 | -0.31128
4550.4062 | 123.2483 | -122.8134 | 0.17853 | -0.16083 | 0.035782 | 0.0050842 | 0.0093909 | -0.011175 | 0.0039242 | -0.0097199 | -0.28709 | -0.013196 | -0.0034756 | -0.0028306 | 0.0051761 | -0.02063 | 0.1236 | 0.13275 | 0.054932 | 0.10986 | 0.3891 | -0.018311 | -0.17853 | 0.086975 | 0.1236 | -0.009155 | 0.29297 | 0.23804 | -0.1236 | -0.19684 | 122.7951 | 122.6349 | 0.21057 | 122.9462 | 122.9233 | 0.28839 | -0.054932 | 122.6898 | 122.6166 | 0.11444 | 122.9004 | 122.8043 | 0.18768 | 0.059509 | 123.2025 | 122.937 | 122.8683 | -0.35706 | 123.1064 | 123.0515 | 122.937 | -0.37537
4552.125 | 123.23 | -122.8317 | 0.17395 | -0.031128 | 0.031509 | 0.0057252 | 0.0078955 | -0.0096792 | -0.0056888 | -0.0092927 | -0.081101 | -0.015973 | -0.00668 | -0.00069421 | -0.00016447 | -0.016357 | 0.13733 | 0.21973 | 0.16022 | 0.15564 | 0.34332 | 0.004578 | -0.14648 | 0.19226 | 0.26093 | 0.16937 | 0.27008 | 0.2243 | -0.082397 | -0.15564 | 122.8363 | 122.6852 | 0.16937 | 123.0515 | 122.9874 | 0.30212 | -0.036621 | 122.7493 | 122.6761 | 0.096131 | 123.024 | 123.0011 | 0.32501 | 0.050354 | 123.175 | 122.9691 | 122.9919 | -0.32043 | 123.1018 | 123.056 | 123.0927 | -0.32959
4553.8125 | 123.111 | -122.8867 | 0.2243 | 0.098572 | 0.030655 | 0.0065796 | 0.0042639 | -0.010961 | -0.0024844 | -0.010361 | 0.12489 | -0.01405 | -0.0098844 | -0.0032578 | 0.0056033 | -0.016998 | 0.10529 | 0.13275 | 0.068665 | 0.07782 | 0.29755 | -0.032043 | -0.19684 | 0.09613 | 0.15106 | 0.07782 | 0.21515 | 0.16937 | -0.11444 | -0.16022 | 122.8546 | 122.6898 | 0.073242 | 123.0194 | 122.9645 | 0.27466 | -0.11902 | 122.7722 | 122.7264 | -0.009155 | 122.9828 | 122.9645 | 0.23804 | -0.054931 | 123.1842 | 122.9919 | 122.9553 | -0.42114 | 123.1018 | 123.056 | 123.0377 | -0.38452
4555.5312 | 123.23 | -122.8409 | 0.16937 | -0.13031 | 0.030869 | 0.0067932 | 0.0074683 | -0.011388 | -0.0035526 | -0.011002 | -0.14214 | -0.012555 | -0.0086026 | -0.0034714 | 0.0026125 | -0.016998 | 0.23346 | 0.2655 | 0.20142 | 0.20142 | 0.36621 | 0.041199 | -0.12817 | 0.20599 | 0.27924 | 0.14648 | 0.28381 | 0.24261 | -0.064087 | -0.11444 | 122.8821 | 122.7127 | 0.19684 | 123.1064 | 123.0423 | 0.32959 | 0.064086 | 122.7768 | 122.7264 | 0.11444 | 123.0469 | 122.9874 | 0.26093 | 0.073242 | 123.2071 | 123.0743 | 123.0423 | -0.29755 | 123.1247 | 123.0835 | 123.1201 | -0.28381
4557.2188 | 123.1888 | -122.8271 | 0.19684 | -0.21423 | 0.02681 | 0.0093566 | 0.0049047 | -0.0071158 | -0.00163 | -0.011002 | -0.20317 | -0.013623 | -0.010098 | -0.001976 | 0.0032535 | -0.016357 | 0.24719 | 0.27008 | 0.19684 | 0.21057 | 0.39825 | 0.054932 | -0.11444 | 0.18768 | 0.27008 | 0.14648 | 0.27008 | 0.23804 | -0.082397 | -0.11444 | 122.8821 | 122.7127 | 0.20142 | 123.0972 | 123.0377 | 0.32501 | 0.050354 | 122.7448 | 122.7127 | 0.073243 | 123.0148 | 122.9736 | 0.26093 | 0.041199 | 123.2254 | 123.0743 | 123.024 | -0.31128 | 123.0972 | 123.0652 | 123.0972 | -0.31128
4558.9062 | 123.1384 | -122.8683 | 0.21515 | 0.11383 | 0.033432 | 0.0048706 | 0.0074683 | -0.0090384 | 0.001788 | -0.0073701 | 0.17067 | -0.012555 | -0.0092434 | -0.001976 | 0.0066715 | -0.016784 | 0.13733 | 0.09613 | 0.036621 | 0.068665 | 0.24719 | -0.086975 | -0.25177 | 0.091553 | 0.10071 | 0.027466 | 0.15564 | 0.11902 | -0.17853 | -0.2243 | 122.7814 | 122.6166 | 0.032043 | 122.9645 | 122.937 | 0.32044 | -0.07782 | 122.6898 | 122.644 | -0.059509 | 122.9599 | 122.8958 | 0.25177 | -0.09613 | 123.1155 | 123.0057 | 122.905 | -0.46692 | 123.024 | 122.9874 | 122.9691 | -0.43945
4560.6094 | 123.2208 | -122.85 | 0.20599 | -0.13794 | 0.034927 | 0.0057252 | 0.011314 | -0.0098928 | 0.005206 | -0.0075837 | -0.2108 | -0.011914 | -0.0068936 | -0.0013352 | 0.0085941 | -0.019561 | 0.13275 | 0.11444 | 0.022888 | 0.09613 | 0.36163 | -0.054932 | -0.21057 | 0.086975 | 0.14191 | -0.036621 | 0.2655 | 0.20599 | -0.14191 | -0.19226 | 122.7951 | 122.6395 | 0.15564 | 122.9645 | 122.9462 | 0.3067 | -0.073243 | 122.7081 | 122.6578 | 0.059509 | 122.937 | 122.8134 | 0.15564 | 0 | 123.2117 | 122.9828 | 122.8729 | -0.41657 | 123.1155 | 123.056 | 122.9919 | -0.39826
4562.2969 | 123.2162 | -122.8409 | 0.19684 | -0.22949 | 0.034927 | 0.0085022 | 0.0081091 | -0.011388 | -0.0029118 | -0.0084381 | -0.26421 | -0.010632 | -0.0058254 | -0.0026168 | 0.0049625 | -0.017852 | 0.11902 | 0.13733 | 0.07782 | 0.10529 | 0.42114 | 0.013733 | -0.1831 | 0.10071 | 0.15564 | 0.027466 | 0.3067 | 0.2655 | -0.1236 | -0.14648 | 122.8546 | 122.6578 | 0.2243 | 122.9782 | 122.9462 | 0.28839 | -0.077819 | 122.7173 | 122.6944 | 0.10986 | 122.9416 | 122.8683 | 0.17395 | 0.068665 | 123.262 | 122.9599 | 122.9187 | -0.37994 | 123.1476 | 123.1064 | 122.9965 | -0.34332
4564 | 123.111 | -122.8867 | 0.24719 | -0.054016 | 0.037491 | 0.006366 | 0.0042639 | -0.0096792 | 0.0039242 | -0.0058747 | -0.073471 | -0.012341 | -0.0079618 | -0.0030442 | 0.010944 | -0.018493 | 0.10529 | 0.091553 | -0.013733 | 0.045776 | 0.33417 | -0.073242 | -0.24719 | 0.009155 | 0.050354 | -0.10529 | 0.20142 | 0.17395 | -0.19226 | -0.23804 | 122.8134 | 122.6395 | 0.086975 | 122.9782 | 122.9324 | 0.29297 | -0.14191 | 122.6944 | 122.6486 | -0.045776 | 122.8958 | 122.7814 | 0.13275 | -0.073242 | 123.2208 | 122.9919 | 122.8729 | -0.49438 | 123.0881 | 123.0606 | 122.937 | -0.48523
4565.6875 | 123.2437 | -122.8546 | 0.18768 | -0.2066 | 0.037918 | 0.0070068 | 0.0074683 | -0.0090384 | 0.0011472 | -0.0077973 | -0.19554 | -0.011487 | -0.0071072 | -0.0017624 | 0.0049625 | -0.01593 | 0.09613 | 0.13275 | 0.059509 | 0.11902 | 0.37994 | -0.004578 | -0.18768 | 0.050354 | 0.10986 | -0.022888 | 0.25635 | 0.21515 | -0.15106 | -0.1831 | 122.85 | 122.6669 | 0.19226 | 122.9874 | 122.9736 | 0.3067 | -0.091553 | 122.7036 | 122.6715 | 0.068665 | 122.905 | 122.8317 | 0.16022 | 0.027466 | 123.2346 | 122.9507 | 122.9141 | -0.37537 | 123.111 | 123.0698 | 122.9645 | -0.37079
4567.375 | 123.2208 | -122.8592 | 0.17853 | -0.13794 | 0.036423 | 0.0052978 | 0.0081091 | -0.0088248 | -0.00056178 | -0.0075837 | -0.11162 | -0.011273 | -0.004971 | -0.0015488 | 0.0049625 | -0.018066 | 0.09613 | 0.14191 | 0.041199 | 0.09613 | 0.3479 | -0.032043 | -0.2243 | 0.07782 | 0.14191 | -0.022888 | 0.24261 | 0.21515 | -0.14648 | -0.19684 | 122.8271 | 122.6349 | 0.16937 | 123.0011 | 122.9553 | 0.32043 | -0.082398 | 122.7127 | 122.6624 | 0.064087 | 122.937 | 122.8363 | 0.17395 | 0.036621 | 123.2071 | 122.9553 | 122.9004 | -0.40283 | 123.1018 | 123.0743 | 123.0011 | -0.37537
4569.0625 | 123.1934 | -122.8455 | 0.18768 | -0.13794 | 0.031723 | 0.0089294 | 0.0096045 | -0.0090384 | -0.0065434 | -0.0073701 | -0.096359 | -0.015332 | -0.0039028 | -0.0028306 | 0.00047633 | -0.015289 | 0.15564 | 0.28839 | 0.19684 | 0.18768 | 0.3479 | 0.027466 | -0.13275 | 0.19226 | 0.3067 | 0.1831 | 0.27008 | 0.23346 | -0.073242 | -0.10986 | 122.8729 | 122.7127 | 0.16022 | 123.1339 | 123.0331 | 0.32043 | -0.032043 | 122.7722 | 122.7356 | 0.082398 | 123.0377 | 123.0286 | 0.29297 | 0.045776 | 123.1934 | 123.0011 | 123.0423 | -0.32043 | 123.1155 | 123.0789 | 123.1522 | -0.29755
4570.7812 | 123.1338 | -122.8867 | 0.21057 | 0.083313 | 0.034287 | 0.0089294 | 0.0040503 | -0.0060476 | 0.00071982 | -0.0088653 | 0.1783 | -0.011914 | -0.010312 | -0.0017624 | 0.0090213 | -0.016357 | 0.07782 | 0.1236 | 0.041199 | 0.054932 | 0.24719 | -0.054932 | -0.24719 | 0.086975 | 0.11902 | 0.018311 | 0.17853 | 0.10071 | -0.18768 | -0.20599 | 122.8317 | 122.6395 | 0.036621 | 123.0103 | 122.9416 | 0.30212 | -0.13275 | 122.699 | 122.6807 | -0.032043 | 122.9736 | 122.905 | 0.22431 | -0.10986 | 123.1338 | 122.9645 | 122.9279 | -0.45776 | 123.0652 | 122.9874 | 123.0057 | -0.41657
4572.5156 | 123.2529 | -122.8271 | 0.17853 | -0.17609 | 0.036209 | 0.0052978 | 0.0074683 | -0.0096792 | 0.0024288 | -0.0095063 | -0.26421 | -0.012555 | -0.0064664 | -0.0028306 | 0.0047489 | -0.018066 | 0.1236 | 0.10529 | 0.036621 | 0.11902 | 0.37994 | 0 | -0.18768 | 0.059509 | 0.13275 | 0.009155 | 0.29755 | 0.24719 | -0.13275 | -0.17395 | 122.8271 | 122.6395 | 0.20142 | 122.9324 | 122.9462 | 0.3067 | -0.054932 | 122.6944 | 122.6532 | 0.11902 | 122.8867 | 122.8363 | 0.1831 | 0.068664 | 123.2071 | 122.9507 | 122.8638 | -0.36621 | 123.1247 | 123.0743 | 122.9599 | -0.35248
4574.2031 | 123.2208 | -122.8546 | 0.1831 | -0.16083 | 0.038132 | 0.0044434 | 0.0087499 | -0.01032 | 0.00093342 | -0.0086517 | -0.18791 | -0.012341 | -0.0036892 | -0.003685 | 0.0073123 | -0.020202 | 0.09613 | 0.11902 | 0.027466 | 0.10071 | 0.3479 | -0.022888 | -0.19684 | 0.064087 | 0.11902 | -0.027466 | 0.23804 | 0.20599 | -0.15106 | -0.18768 | 122.8317 | 122.6578 | 0.16479 | 122.9736 | 122.9553 | 0.29755 | -0.086975 | 122.7036 | 122.6669 | 0.054932 | 122.9187 | 122.8271 | 0.16022 | 0.022889 | 123.2025 | 122.9507 | 122.8821 | -0.37994 | 123.0927 | 123.0606 | 122.9736 | -0.37079
4575.9375 | 123.1064 | -122.9233 | 0.21057 | -0.031128 | 0.036423 | 0.0070068 | 0.0057593 | -0.012243 | 0.0028562 | -0.0060883 | -0.073471 | -0.011059 | -0.0041164 | -0.0030442 | 0.0092349 | -0.01828 | 0.086975 | 0.10986 | -0.009155 | 0.059509 | 0.3067 | -0.059509 | -0.21973 | 0.013733 | 0.050354 | -0.07782 | 0.19684 | 0.19226 | -0.1831 | -0.22888 | 122.8638 | 122.7036 | 0.096131 | 123.0331 | 122.9828 | 0.27924 | -0.1236 | 122.7402 | 122.6944 | -0.013733 | 122.937 | 122.8455 | 0.15106 | -0.01831 | 123.23 | 123.0103 | 122.9141 | -0.4303 | 123.1201 | 123.1155 | 122.9736 | -0.43945
4577.625 | 123.111 | -122.9004 | 0.2243 | 0.029907 | 0.036423 | 0.0061524 | 0.0072547 | -0.011602 | 0.0022152 | -0.0099335 | 0.04097 | -0.011487 | -0.0024076 | -0.0011216 | 0.0088077 | -0.015075 | 0 | 0.027466 | -0.073242 | -0.004578 | 0.2655 | -0.091553 | -0.27924 | -0.036621 | 0.018311 | -0.11444 | 0.20142 | 0.16937 | -0.19226 | -0.25177 | 122.8088 | 122.6212 | 0.041199 | 122.9279 | 122.8958 | 0.27466 | -0.2243 | 122.7081 | 122.6486 | -0.022888 | 122.8638 | 122.7859 | 0.13733 | -0.054931 | 123.1659 | 122.9004 | 122.8271 | -0.50354 | 123.1018 | 123.0698 | 122.9187 | -0.47607
4579.3125 | 123.143 | -122.8455 | 0.21515 | 0.19012 | 0.035996 | 0.0061524 | 0.0053321 | -0.007543 | 0.00050622 | -0.0088653 | 0.18593 | -0.011487 | -0.0079618 | -0.0024032 | 0.0060305 | -0.01593 | -0.018311 | 0.032043 | -0.045776 | -0.018311 | 0.25177 | -0.10529 | -0.2655 | 0.068665 | 0.07782 | 0 | 0.17395 | 0.13275 | -0.16479 | -0.21973 | 122.7402 | 122.58 | 0.036621 | 122.8775 | 122.8271 | 0.24719 | -0.23346 | 122.6807 | 122.6257 | -0.041199 | 122.9141 | 122.8455 | 0.21973 | -0.082398 | 123.0972 | 122.8271 | 122.7997 | -0.48065 | 123.0194 | 122.9782 | 122.9233 | -0.43488
4581.0312 | 123.111 | -122.9004 | 0.20599 | 0.029907 | 0.030441 | 0.008075 | 0.0066137 | -0.01267 | -0.006116 | -0.010788 | 0.14015 | -0.015118 | -0.0081754 | -0.0026168 | 0.0032535 | -0.014221 | 0.041199 | 0.14648 | 0.068665 | 0.064087 | 0.3067 | -0.018311 | -0.21057 | 0.091553 | 0.16022 | 0.086975 | 0.23804 | 0.1831 | -0.11444 | -0.17395 | 122.8821 | 122.6898 | 0.10071 | 123.0469 | 122.9645 | 0.27466 | -0.1648 | 122.7859 | 122.7264 | 0.032043 | 122.9919 | 122.9874 | 0.26092 | -0.022889 | 123.2071 | 122.9416 | 122.9691 | -0.41657 | 123.1384 | 123.0835 | 123.0606 | -0.37994
4582.7188 | 123.0789 | -122.8683 | 0.21057 | 0.1062 | 0.032791 | 0.0070068 | 0.0072547 | -0.010534 | -0.003339 | -0.0099335 | 0.1783 | -0.011914 | -0.0073208 | -0.0021896 | 0.0041079 | -0.017212 | 0.086975 | 0.10986 | 0.064087 | 0.059509 | 0.24261 | -0.054932 | -0.23804 | 0.10071 | 0.11902 | 0.036621 | 0.17853 | 0.16022 | -0.16479 | -0.19226 | 122.8134 | 122.6303 | 0.032044 | 122.9782 | 122.9279 | 0.29755 | -0.1236 | 122.7036 | 122.6761 | -0.032043 | 122.9691 | 122.905 | 0.22888 | -0.050354 | 123.111 | 122.9553 | 122.9324 | -0.44861 | 123.0469 | 123.0286 | 122.9874 | -0.40283
4584.4219 | 123.1384 | -122.8638 | 0.21515 | 0.19012 | 0.035141 | 0.0057252 | 0.0057593 | -0.010106 | -0.00034818 | -0.0065155 | 0.15541 | -0.012127 | -0.0086026 | -0.0013352 | 0.0064577 | -0.017852 | 0.050354 | 0.018311 | -0.041199 | -0.004578 | 0.25177 | -0.10529 | -0.27008 | 0.07782 | 0.09613 | -0.013733 | 0.16479 | 0.12817 | -0.16022 | -0.21057 | 122.7585 | 122.5937 | 0.036621 | 122.8821 | 122.8592 | 0.2655 | -0.16479 | 122.7036 | 122.6532 | -0.050354 | 122.9416 | 122.85 | 0.19684 | -0.086975 | 123.1155 | 122.9141 | 122.8226 | -0.48523 | 123.0286 | 122.9919 | 122.9599 | -0.42572
4586.1562 | 123.2254 | -122.818 | 0.17853 | -0.069275 | 0.034287 | 0.0055114 | 0.0091773 | -0.009252 | -0.0063296 | -0.011215 | -0.058212 | -0.014905 | -0.0092434 | -0.0041122 | 0.0013309 | -0.014862 | 0.19226 | 0.21515 | 0.19226 | 0.15564 | 0.33417 | 0.018311 | -0.13733 | 0.19226 | 0.23804 | 0.14648 | 0.26093 | 0.21057 | -0.073242 | -0.11902 | 122.8363 | 122.6807 | 0.15564 | 123.0331 | 122.9736 | 0.29297 | 0.013733 | 122.7448 | 122.699 | 0.082397 | 123.0103 | 122.9645 | 0.2655 | 0.032043 | 123.1522 | 123.0103 | 123.0103 | -0.31586 | 123.0789 | 123.0286 | 123.056 | -0.29755
4587.8438 | 123.0927 | -122.8683 | 0.21973 | 0.11383 | 0.033005 | 0.0082886 | 0.0057593 | -0.010961 | -0.0029118 | -0.0092927 | 0.16304 | -0.01405 | -0.0079618 | -0.003685 | 0.0056033 | -0.016784 | 0.13275 | 0.1236 | 0.064087 | 0.054932 | 0.24261 | -0.045776 | -0.21973 | 0.10986 | 0.10529 | 0.013733 | 0.19684 | 0.15564 | -0.16022 | -0.21057 | 122.8226 | 122.6486 | 0.022888 | 122.9919 | 122.9233 | 0.27466 | -0.086976 | 122.7081 | 122.6578 | -0.022889 | 122.9782 | 122.8821 | 0.2243 | -0.064087 | 123.111 | 123.0011 | 122.9324 | -0.43945 | 123.0652 | 123.024 | 122.9736 | -0.4303
4589.5312 | 123.1842 | -122.8455 | 0.18768 | -0.13794 | 0.033859 | 0.007434 | 0.010459 | -0.0096792 | -0.0012028 | -0.011856 | -0.19554 | -0.012127 | -0.0073208 | -0.0049668 | 0.0019717 | -0.016143 | 0.20599 | 0.20142 | 0.17395 | 0.17853 | 0.36163 | 0.032043 | -0.14191 | 0.17853 | 0.24719 | 0.11444 | 0.27466 | 0.25635 | -0.082397 | -0.12817 | 122.8775 | 122.7036 | 0.17395 | 123.0469 | 123.024 | 0.32044 | 0.018311 | 122.7631 | 122.7173 | 0.086975 | 123.024 | 122.9599 | 0.24262 | 0.068665 | 123.2071 | 123.0515 | 123.0194 | -0.32959 | 123.1201 | 123.1018 | 123.0927 | -0.31586
4591.2188 | 123.1796 | -122.8409 | 0.20599 | -0.25238 | 0.031723 | 0.0057252 | 0.0070409 | -0.007543 | -0.0012028 | -0.0088653 | -0.21843 | -0.013623 | -0.008389 | -0.00090781 | 0.0047489 | -0.017852 | 0.21057 | 0.19684 | 0.14191 | 0.18768 | 0.39368 | 0.041199 | -0.13275 | 0.11902 | 0.1831 | 0.059509 | 0.29755 | 0.27466 | -0.10071 | -0.13275 | 122.8821 | 122.7081 | 0.18768 | 123.0377 | 123.0286 | 0.32043 | 0.004577 | 122.7402 | 122.7081 | 0.091552 | 122.9599 | 122.9004 | 0.19226 | 0.068664 | 123.2346 | 123.0515 | 122.9828 | -0.33875 | 123.1384 | 123.1155 | 123.024 | -0.33875
4592.8906 | 123.0835 | -122.8683 | 0.2243 | 0.16724 | 0.032364 | 0.0076478 | 0.0057593 | -0.009252 | -0.0029118 | -0.0082245 | 0.11726 | -0.012555 | -0.0073208 | -0.0028306 | 0.0036807 | -0.017852 | 0.13275 | 0.10071 | 0.050354 | 0.050354 | 0.24719 | -0.07782 | -0.24261 | 0.11444 | 0.15106 | 0.036621 | 0.15564 | 0.12817 | -0.16479 | -0.20599 | 122.7905 | 122.6257 | 0.022888 | 122.9691 | 122.9187 | 0.29297 | -0.091553 | 122.7036 | 122.6624 | -0.068664 | 122.9828 | 122.905 | 0.24262 | -0.09613 | 123.1155 | 123.0011 | 122.9187 | -0.46692 | 123.024 | 122.9965 | 123.0194 | -0.4303
4594.5781 | 123.111 | -122.8729 | 0.2243 | 0.060425 | 0.030441 | 0.0070068 | 0.0061865 | -0.01032 | -0.0037662 | -0.011002 | 0.079117 | -0.015973 | -0.0098844 | -0.0034714 | 0.0019717 | -0.014435 | 0.10986 | 0.086975 | 0.091553 | 0.086975 | 0.30212 | -0.036621 | -0.17853 | 0.091553 | 0.14648 | 0.068665 | 0.22888 | 0.20142 | -0.10529 | -0.16937 | 122.8363 | 122.6944 | 0.07782 | 122.9599 | 122.9599 | 0.2655 | -0.11444 | 122.7676 | 122.7036 | 0.004578 | 122.9645 | 122.9416 | 0.23804 | -0.022888 | 123.175 | 122.9828 | 122.9645 | -0.40283 | 123.1018 | 123.0743 | 123.0194 | -0.39368
4596.2656 | 123.1476 | -122.8638 | 0.20599 | 0.029907 | 0.0298 | 0.0072204 | 0.0085363 | -0.012884 | -0.0031254 | -0.0099335 | 0.048599 | -0.01405 | -0.0075344 | -0.0021896 | 0.0028263 | -0.019561 | 0.13275 | 0.10071 | 0.09613 | 0.091553 | 0.32959 | -0.013733 | -0.17395 | 0.10986 | 0.15106 | 0.068665 | 0.25635 | 0.19684 | -0.10071 | -0.15564 | 122.85 | 122.6898 | 0.1236 | 122.9645 | 122.9553 | 0.2655 | -0.073243 | 122.7631 | 122.7081 | 0.050354 | 122.9736 | 122.9324 | 0.22431 | -0.009156 | 123.1934 | 122.9965 | 122.9599 | -0.37994 | 123.1201 | 123.0606 | 123.0148 | -0.36163
4598 | 123.2254 | -122.8455 | 0.19226 | -0.10742 | 0.035568 | 0.006366 | 0.0078955 | -0.0064748 | 0.0028562 | -0.0060883 | -0.18791 | -0.0095639 | -0.008389 | -0.00048061 | 0.0064577 | -0.019775 | 0.17395 | 0.086975 | 0.036621 | 0.09613 | 0.3479 | -0.032043 | -0.20599 | 0.082397 | 0.10986 | -0.045776 | 0.21515 | 0.21515 | -0.15106 | -0.19226 | 122.8134 | 122.6395 | 0.15564 | 122.9324 | 122.9416 | 0.30212 | -0.018311 | 122.6944 | 122.6532 | 0.022888 | 122.9279 | 122.7997 | 0.14648 | 0.022888 | 123.1934 | 123.0194 | 122.8821 | -0.39826 | 123.0606 | 123.0606 | 122.9553 | -0.38452
4599.7344 | 123.1705 | -122.8729 | 0.19684 | -0.26001 | 0.031723 | 0.0061524 | 0.010459 | -0.0088248 | -0.0024844 | -0.0060883 | -0.23369 | -0.013409 | -0.0058254 | -0.0021896 | 0.0021853 | -0.018493 | 0.19684 | 0.20142 | 0.15106 | 0.17395 | 0.37994 | 0.022888 | -0.13275 | 0.10986 | 0.18768 | 0.041199 | 0.30212 | 0.27466 | -0.086975 | -0.1236 | 122.8958 | 122.7402 | 0.18311 | 123.0743 | 123.0469 | 0.3067 | 0 | 122.7859 | 122.7493 | 0.10529 | 122.9828 | 122.9141 | 0.16479 | 0.07782 | 123.2529 | 123.0698 | 123.024 | -0.32959 | 123.175 | 123.1476 | 123.0606 | -0.32043
4601.4219 | 123.2437 | -122.8363 | 0.19684 | -0.17609 | 0.035141 | 0.0031616 | 0.012595 | -0.0088248 | 0.0041378 | -0.0082245 | -0.25658 | -0.015118 | -0.0062528 | -0.0017624 | 0.0043215 | -0.019989 | 0.13275 | 0.11444 | 0.059509 | 0.10986 | 0.40283 | -0.013733 | -0.18768 | 0.073242 | 0.11444 | -0.027466 | 0.25635 | 0.26093 | -0.15564 | -0.19226 | 122.8226 | 122.6486 | 0.20599 | 122.9507 | 122.9462 | 0.29755 | -0.064087 | 122.6807 | 122.644 | 0.05951 | 122.9095 | 122.8088 | 0.16479 | 0.064087 | 123.2391 | 122.9691 | 122.8958 | -0.38452 | 123.0927 | 123.0972 | 122.9507 | -0.3891
4603.125 | 123.23 | -122.818 | 0.19226 | -0.038757 | 0.03215 | 0.0076478 | 0.0078955 | -0.0094656 | -0.0071842 | -0.010147 | -0.035324 | -0.014477 | -0.0064664 | -0.0026168 | 0.0013309 | -0.017639 | 0.12817 | 0.16479 | 0.12817 | 0.13275 | 0.32959 | -0.004578 | -0.17395 | 0.16937 | 0.23804 | 0.13733 | 0.24719 | 0.20599 | -0.091553 | -0.1236 | 122.8134 | 122.644 | 0.13733 | 122.9828 | 122.9507 | 0.3067 | -0.064087 | 122.7264 | 122.6944 | 0.054931 | 122.9874 | 122.9553 | 0.26093 | 0.013733 | 123.1476 | 122.9462 | 122.9462 | -0.36621 | 123.0652 | 123.024 | 123.056 | -0.31586
4604.8125 | 123.1018 | -122.8821 | 0.21515 | 0.11383 | 0.030869 | 0.0076478 | 0.0021277 | -0.0083974 | -0.0035526 | -0.010361 | 0.14015 | -0.015759 | -0.0068936 | -0.001976 | 0.0049625 | -0.01828 | 0.10529 | 0.11902 | 0.045776 | 0.045776 | 0.26093 | -0.073242 | -0.2243 | 0.12817 | 0.15564 | 0.041199 | 0.19684 | 0.17853 | -0.13275 | -0.16022 | 122.8088 | 122.6578 | 0.045776 | 123.0011 | 122.9279 | 0.27008 | -0.10986 | 122.7493 | 122.7219 | -0.018311 | 123.0103 | 122.9233 | 0.20142 | -0.036621 | 123.143 | 122.9874 | 122.9279 | -0.43945 | 123.0789 | 123.0606 | 123.0377 | -0.37537
4606.5 | 123.0789 | -122.8958 | 0.21973 | 0.1062 | 0.03215 | 0.0095704 | 0.0057593 | -0.011602 | -0.00077538 | -0.010361 | 0.14778 | -0.012768 | -0.010098 | -0.0032578 | 0.0056033 | -0.016571 | 0.12817 | 0.10986 | 0.041199 | 0.054932 | 0.25177 | -0.045776 | -0.21973 | 0.12817 | 0.13733 | 0.045776 | 0.19226 | 0.16479 | -0.15106 | -0.19226 | 122.85 | 122.6761 | 0.032043 | 123.0057 | 122.9507 | 0.27466 | -0.091553 | 122.7448 | 122.7036 | -0.027466 | 123.024 | 122.9416 | 0.23804 | -0.054932 | 123.1476 | 123.024 | 122.937 | -0.43945 | 123.0881 | 123.0606 | 123.0331 | -0.41199
4608.2031 | 123.2025 | -122.8409 | 0.19684 | -0.22186 | 0.033432 | 0.0055114 | 0.0087499 | -0.011815 | -0.0014164 | -0.0086517 | -0.2108 | -0.013623 | -0.0026212 | -0.0017624 | 0.0023989 | -0.016571 | 0.16479 | 0.13275 | 0.082397 | 0.10071 | 0.42114 | 0.018311 | -0.13733 | 0.091553 | 0.15564 | 0.022888 | 0.30212 | 0.2655 | -0.11444 | -0.14191 | 122.8592 | 122.7036 | 0.2243 | 122.9736 | 122.9416 | 0.23804 | -0.032043 | 122.7264 | 122.699 | 0.10529 | 122.9324 | 122.8638 | 0.16479 | 0.068665 | 123.262 | 123.0057 | 122.9233 | -0.33417 | 123.143 | 123.1064 | 122.9965 | -0.33875
4609.8906 | 123.175 | -122.8409 | 0.19684 | -0.1532 | 0.031082 | 0.0055114 | 0.0098181 | -0.0083974 | -0.0029118 | -0.0090791 | -0.20317 | -0.014477 | -0.006039 | -0.0024032 | 0.0032535 | -0.017639 | 0.21057 | 0.23346 | 0.17853 | 0.1831 | 0.34332 | 0.036621 | -0.12817 | 0.16937 | 0.25635 | 0.12817 | 0.26093 | 0.24719 | -0.082397 | -0.11444 | 122.8775 | 122.7127 | 0.14648 | 123.0743 | 123.024 | 0.31128 | 0.013733 | 122.7585 | 122.7264 | 0.064087 | 123.0103 | 122.9691 | 0.24262 | 0.050354 | 123.1842 | 123.0515 | 123.0194 | -0.32501 | 123.1018 | 123.0881 | 123.0972 | -0.31128
4611.6094 | 123.1934 | -122.8592 | 0.19684 | -0.23712 | 0.034073 | 0.0065796 | 0.010032 | -0.012029 | -0.0024844 | -0.0084381 | -0.21843 | -0.013836 | -0.0071072 | -0.0013352 | 0.0032535 | -0.016571 | 0.16479 | 0.16479 | 0.10071 | 0.11902 | 0.40741 | 0.027466 | -0.13733 | 0.07782 | 0.14191 | 0.018311 | 0.31128 | 0.2655 | -0.10986 | -0.16479 | 122.8867 | 122.7219 | 0.21057 | 123.024 | 122.9782 | 0.25635 | -0.032043 | 122.7493 | 122.6944 | 0.11444 | 122.937 | 122.8775 | 0.18311 | 0.068665 | 123.2666 | 123.024 | 122.9599 | -0.33417 | 123.1705 | 123.1247 | 123.0011 | -0.36163
4613.3438 | 123.1567 | -122.8821 | 0.18768 | 0.014648 | 0.031723 | 0.0072204 | 0.0049047 | -0.0096792 | -0.0035526 | -0.0086517 | 0.018082 | -0.012555 | -0.0081754 | -0.0017624 | 0.0026125 | -0.016357 | 0.10071 | 0.14191 | 0.082397 | 0.09613 | 0.31128 | -0.013733 | -0.17853 | 0.11444 | 0.17395 | 0.07782 | 0.23804 | 0.21515 | -0.11902 | -0.15106 | 122.8683 | 122.7036 | 0.1236 | 123.024 | 122.9782 | 0.27466 | -0.086975 | 122.7631 | 122.731 | 0.050354 | 122.9965 | 122.9599 | 0.22888 | 0.027466 | 123.1934 | 122.9828 | 122.9645 | -0.36621 | 123.1201 | 123.0972 | 123.056 | -0.33874
4615.0312 | 123.23 | -122.8317 | 0.20142 | -0.099793 | 0.036423 | 0.0067932 | 0.0044775 | -0.0098928 | 0.0041378 | -0.0069427 | -0.20317 | -0.0117 | -0.008389 | -0.00090781 | 0.0088077 | -0.019348 | 0.15564 | 0.10529 | 0.022888 | 0.091553 | 0.35706 | -0.041199 | -0.21057 | 0.07782 | 0.1236 | -0.036621 | 0.23346 | 0.20599 | -0.14191 | -0.19226 | 122.7905 | 122.6212 | 0.15564 | 122.937 | 122.9233 | 0.30212 | -0.045776 | 122.6898 | 122.6395 | 0.032043 | 122.9095 | 122.7951 | 0.15564 | 0.004578 | 123.1888 | 122.9874 | 122.8546 | -0.41199 | 123.0652 | 123.0377 | 122.9553 | -0.39368
4616.75 | 123.1155 | -122.8775 | 0.22888 | 0.060425 | 0.037277 | 0.007434 | 0.0059729 | -0.012029 | 0.0030698 | -0.0080109 | 0.04097 | -0.0089229 | -0.007748 | -0.0015488 | 0.0075259 | -0.018707 | 0.009155 | -0.064087 | -0.11444 | -0.041199 | 0.27924 | -0.11444 | -0.27466 | -0.013733 | 0 | -0.11902 | 0.20142 | 0.1831 | -0.19226 | -0.26093 | 122.7631 | 122.6028 | 0.050354 | 122.8134 | 122.8363 | 0.23346 | -0.21973 | 122.6852 | 122.6166 | -0.027466 | 122.8638 | 122.7585 | 0.14191 | -0.045777 | 123.1567 | 122.8867 | 122.7631 | -0.50354 | 123.0789 | 123.0606 | 122.8775 | -0.48981
4618.5 | 123.2254 | -122.8409 | 0.19684 | -0.27527 | 0.034714 | 0.0065796 | 0.011314 | -0.011175 | 0.0011472 | -0.0095063 | -0.25658 | -0.010205 | -0.0047574 | -0.0030442 | 0.0021853 | -0.017425 | 0.13733 | 0.12817 | 0.07782 | 0.11444 | 0.41657 | 0.013733 | -0.15564 | 0.054932 | 0.15106 | 0.009155 | 0.31586 | 0.28839 | -0.11902 | -0.15564 | 122.8546 | 122.6852 | 0.21973 | 122.9691 | 122.9553 | 0.27008 | -0.059509 | 122.7219 | 122.6852 | 0.11902 | 122.8958 | 122.85 | 0.16479 | 0.091553 | 123.2574 | 122.9782 | 122.9187 | -0.35248 | 123.1567 | 123.1293 | 122.9919 | -0.35248
4620.1875 | 123.2025 | -122.8546 | 0.20599 | -0.092163 | 0.037491 | 0.004657 | 0.0083227 | -0.0090384 | 0.0032834 | -0.0077973 | -0.20317 | -0.013409 | -0.0053982 | -0.0026168 | 0.0058169 | -0.017212 | 0.10986 | 0.12817 | 0.022888 | 0.086975 | 0.32501 | -0.036621 | -0.23346 | 0.073242 | 0.11902 | -0.041199 | 0.20142 | 0.1831 | -0.16022 | -0.19684 | 122.818 | 122.6212 | 0.11902 | 122.9828 | 122.9416 | 0.32043 | -0.096131 | 122.6944 | 122.6578 | -0.004578 | 122.9279 | 122.8134 | 0.15564 | -0.022889 | 123.1796 | 122.9645 | 122.8775 | -0.43945 | 123.056 | 123.0377 | 122.9736 | -0.40283
4621.875 | 123.1934 | -122.8638 | 0.19226 | -0.19897 | 0.035568 | 0.0072204 | 0.0081091 | -0.0069022 | -0.0012028 | -0.0097199 | -0.19554 | -0.012982 | -0.0043302 | -0.0056076 | 0.0026125 | -0.014862 | 0.09613 | 0.15106 | 0.07782 | 0.10529 | 0.40741 | -0.004578 | -0.16479 | 0.091553 | 0.14648 | 0.041199 | 0.3067 | 0.27008 | -0.10529 | -0.14191 | 122.8592 | 122.699 | 0.21515 | 123.0148 | 122.9691 | 0.27008 | -0.096131 | 122.7585 | 122.7219 | 0.11444 | 122.9553 | 122.905 | 0.18311 | 0.07782 | 123.2712 | 122.9599 | 122.9416 | -0.35706 | 123.1705 | 123.1339 | 123.0103 | -0.33417
4623.5625 | 123.1888 | -122.8638 | 0.20142 | -0.2066 | 0.032364 | 0.0082886 | 0.010245 | -0.010747 | -0.005048 | -0.011642 | -0.14977 | -0.013409 | -0.0092434 | -0.0038986 | 0.0011173 | -0.015075 | 0.16937 | 0.2655 | 0.19226 | 0.17853 | 0.37079 | 0.045776 | -0.11902 | 0.15106 | 0.25635 | 0.11902 | 0.26093 | 0.21057 | -0.091553 | -0.12817 | 122.9095 | 122.7448 | 0.16937 | 123.1293 | 123.0423 | 0.29755 | -0.032043 | 122.7722 | 122.7356 | 0.059509 | 123.0148 | 122.9828 | 0.24719 | 0.009155 | 123.2346 | 123.0331 | 123.056 | -0.32044 | 123.1247 | 123.0743 | 123.1201 | -0.32959
4625.25 | 123.2391 | -122.85 | 0.19226 | -0.26764 | 0.035355 | 0.0050842 | 0.012382 | -0.0077566 | -0.00013458 | -0.0092927 | -0.21843 | -0.012341 | -0.0051846 | -0.0021896 | 0.0047489 | -0.018707 | 0.12817 | 0.1236 | 0.064087 | 0.11902 | 0.41199 | 0.013733 | -0.14648 | 0.064087 | 0.10986 | -0.004578 | 0.27924 | 0.2655 | -0.12817 | -0.16479 | 122.8638 | 122.7036 | 0.21973 | 122.9736 | 122.9691 | 0.2655 | -0.064087 | 122.7219 | 122.6852 | 0.086975 | 122.9141 | 122.8455 | 0.16022 | 0.073242 | 123.262 | 122.9782 | 122.9141 | -0.33874 | 123.1293 | 123.1155 | 122.9599 | -0.35706
4626.9375 | 123.2071 | -122.8455 | 0.1831 | -0.18372 | 0.033005 | 0.0065796 | 0.010459 | -0.0081838 | -0.0063296 | -0.0092927 | -0.14214 | -0.015759 | -0.0073208 | -0.0032578 | 0.0028263 | -0.01593 | 0.18768 | 0.28839 | 0.19226 | 0.20142 | 0.38452 | 0.041199 | -0.1236 | 0.16937 | 0.27466 | 0.15106 | 0.27008 | 0.25177 | -0.064087 | -0.10071 | 122.8867 | 122.7219 | 0.20142 | 123.1339 | 123.0469 | 0.32501 | 0.004578 | 122.7814 | 122.7448 | 0.086976 | 123.0148 | 122.9965 | 0.25177 | 0.068665 | 123.23 | 123.0331 | 123.0377 | -0.3067 | 123.1155 | 123.0972 | 123.1201 | -0.28381
4628.6406 | 123.1888 | -122.8363 | 0.19226 | -0.18372 | 0.034073 | 0.0076478 | 0.0083227 | -0.012884 | -0.0041934 | -0.0090791 | -0.21843 | -0.015118 | -0.0058254 | 0.00016019 | 0.0032535 | -0.016143 | 0.16022 | 0.2655 | 0.17395 | 0.19226 | 0.37079 | 0.032043 | -0.11444 | 0.14191 | 0.25635 | 0.11444 | 0.26093 | 0.25635 | -0.07782 | -0.11444 | 122.8683 | 122.7219 | 0.17853 | 123.1018 | 123.0286 | 0.3067 | -0.032044 | 122.7585 | 122.7219 | 0.068664 | 122.9782 | 122.9507 | 0.22888 | 0.064087 | 123.2071 | 122.9965 | 123.0103 | -0.3067 | 123.0972 | 123.0927 | 123.0927 | -0.3067
4630.4375 | 123.1934 | -122.8363 | 0.18768 | 0.022278 | 0.033005 | 0.0057252 | 0.0074683 | -0.011388 | -0.0031254 | -0.0092927 | 0.0028229 | -0.014905 | -0.0051846 | -0.0011216 | 0.00090353 | -0.016784 | 0.07782 | 0.16022 | 0.10986 | 0.09613 | 0.33417 | 0 | -0.1831 | 0.14648 | 0.18768 | 0.11902 | 0.24261 | 0.21057 | -0.11444 | -0.14191 | 122.8363 | 122.6532 | 0.14648 | 122.9965 | 122.9324 | 0.27924 | -0.10986 | 122.7219 | 122.6944 | 0.054932 | 122.9828 | 122.9553 | 0.26093 | 0.022888 | 123.1705 | 122.9141 | 122.9462 | -0.37079 | 123.0789 | 123.0469 | 123.024 | -0.32959
4632.1406 | 123.0881 | -122.8958 | 0.21515 | 0.12909 | 0.030655 | 0.0078614 | 0.0066137 | -0.0096792 | -0.0020572 | -0.0088653 | 0.11726 | -0.014477 | -0.0096706 | -0.0030442 | 0.0056033 | -0.015503 | 0.086975 | 0.12817 | 0.050354 | 0.064087 | 0.27008 | -0.050354 | -0.21515 | 0.10986 | 0.14648 | 0.050354 | 0.20599 | 0.16937 | -0.11902 | -0.17853 | 122.8455 | 122.6807 | 0.054932 | 123.024 | 122.9599 | 0.27924 | -0.12817 | 122.7768 | 122.7173 | -0.009155 | 123.0057 | 122.9462 | 0.22888 | -0.045776 | 123.1659 | 122.9828 | 122.9462 | -0.4303 | 123.1018 | 123.0652 | 123.0423 | -0.39368
4633.8281 | 123.1705 | -122.8729 | 0.19684 | -0.26764 | 0.036209 | 0.0078614 | 0.0096045 | -0.0090384 | -0.00163 | -0.011429 | -0.28709 | -0.014264 | -0.0062528 | -0.0038986 | 0.0045351 | -0.016571 | 0.18768 | 0.21057 | 0.13275 | 0.17395 | 0.39368 | 0.018311 | -0.15564 | 0.10986 | 0.17853 | 0.041199 | 0.32044 | 0.27008 | -0.091553 | -0.13275 | 122.8912 | 122.7173 | 0.19684 | 123.0835 | 123.0469 | 0.32959 | -0.009155 | 122.7814 | 122.7402 | 0.1236 | 122.9828 | 122.9141 | 0.17395 | 0.073243 | 123.2666 | 123.0606 | 123.0057 | -0.35248 | 123.1934 | 123.143 | 123.0515 | -0.32959
4635.5312 | 123.1018 | -122.9187 | 0.23804 | -0.054016 | 0.037918 | 0.0067932 | 0.0096045 | -0.0098928 | 0.0067014 | -0.0071563 | -0.11162 | -0.0097775 | -0.0041164 | -0.0015488 | 0.0070987 | -0.018707 | 0.10529 | 0.082397 | -0.027466 | 0.027466 | 0.32501 | -0.073242 | -0.25177 | 0.041199 | 0.045776 | -0.10986 | 0.20599 | 0.1831 | -0.20142 | -0.24261 | 122.8455 | 122.6669 | 0.086975 | 123.0011 | 122.9462 | 0.27924 | -0.13275 | 122.7173 | 122.6761 | -0.032043 | 122.9599 | 122.8088 | 0.13275 | -0.054932 | 123.2437 | 123.024 | 122.8912 | -0.48981 | 123.1247 | 123.1018 | 122.9645 | -0.48065
4637.25 | 123.1979 | -122.8226 | 0.19684 | -0.10742 | 0.036209 | 0.0067932 | 0.0085363 | -0.01032 | 0.0030698 | -0.0056611 | -0.20317 | -0.0117 | -0.0062528 | -5.3406e-05 | 0.0051761 | -0.016998 | 0.11902 | 0.1236 | 0.027466 | 0.082397 | 0.32501 | -0.041199 | -0.21515 | 0.073242 | 0.11902 | -0.041199 | 0.21973 | 0.21515 | -0.16479 | -0.19684 | 122.7814 | 122.6074 | 0.12817 | 122.9462 | 122.905 | 0.29755 | -0.077819 | 122.6578 | 122.6257 | 0.022889 | 122.8958 | 122.7814 | 0.15564 | 0.018311 | 123.1476 | 122.9416 | 122.85 | -0.41199 | 123.0423 | 123.0377 | 122.9416 | -0.39368
4639.0156 | 123.0789 | -122.8729 | 0.21515 | 0.090942 | 0.028732 | 0.0057252 | 0.0040503 | -0.0090384 | -0.0048344 | -0.0095063 | 0.15541 | -0.015545 | -0.0064664 | -0.0034714 | 0.0056033 | -0.016357 | 0.064087 | 0.12817 | 0.050354 | 0.050354 | 0.24719 | -0.050354 | -0.22888 | 0.10529 | 0.15564 | 0.050354 | 0.18768 | 0.14648 | -0.13733 | -0.1831 | 122.8226 | 122.644 | 0.032043 | 123.0011 | 122.9233 | 0.27924 | -0.15106 | 122.7356 | 122.6898 | -0.027466 | 122.9782 | 122.9233 | 0.23346 | -0.068665 | 123.1201 | 122.937 | 122.9233 | -0.44403 | 123.0606 | 123.0194 | 123.0286 | -0.39825
4640.7188 | 123.143 | -122.8821 | 0.20599 | 0.17487 | 0.035782 | 0.0065796 | 0.0059729 | -0.007543 | -0.00034818 | -0.0086517 | 0.13252 | -0.011914 | -0.010098 | -0.0032578 | 0.0083805 | -0.01593 | 0.091553 | 0.09613 | 0.032043 | 0.050354 | 0.25177 | -0.073242 | -0.25635 | 0.09613 | 0.1236 | 0.018311 | 0.16937 | 0.11902 | -0.15564 | -0.21515 | 122.8088 | 122.6257 | 0.045776 | 122.9782 | 122.9324 | 0.3067 | -0.11444 | 122.7264 | 122.6669 | -0.036621 | 122.9782 | 122.9004 | 0.23346 | -0.086975 | 123.1338 | 122.9736 | 122.9141 | -0.46234 | 123.0515 | 123.0011 | 123.0057 | -0.42114
4642.4375 | 123.1155 | -122.8638 | 0.21515 | 0.15198 | 0.035568 | 0.0067932 | 0.0057593 | -0.0083974 | 0.00050622 | -0.0075837 | 0.16304 | -0.012127 | -0.011593 | -0.005394 | 0.0075259 | -0.017852 | 0.064087 | 0.10529 | 0.027466 | 0.054932 | 0.21973 | -0.10071 | -0.25177 | 0.086975 | 0.13275 | 0 | 0.13275 | 0.11902 | -0.19226 | -0.23346 | 122.7631 | 122.612 | 0.004578 | 122.9691 | 122.9187 | 0.3067 | -0.15106 | 122.6715 | 122.6303 | -0.082398 | 122.9507 | 122.8638 | 0.23346 | -0.09613 | 123.0835 | 122.9279 | 122.8912 | -0.46692 | 122.9965 | 122.9828 | 122.9965 | -0.44861
4644.125 | 123.1018 | -122.8821 | 0.21515 | 0.15198 | 0.031082 | 0.0087158 | 0.0072547 | -0.011602 | -0.0048344 | -0.0088653 | 0.11726 | -0.013836 | -0.0090298 | -0.003685 | 0.0045351 | -0.015503 | 0.091553 | 0.10986 | 0.064087 | 0.054932 | 0.24261 | -0.068665 | -0.2243 | 0.10071 | 0.13733 | 0.041199 | 0.21057 | 0.17395 | -0.13733 | -0.17853 | 122.8134 | 122.6578 | 0.027466 | 122.9919 | 122.937 | 0.27924 | -0.1236 | 122.7448 | 122.7036 | -0.004578 | 122.9828 | 122.9233 | 0.21973 | -0.041199 | 123.1247 | 122.9736 | 122.9462 | -0.43945 | 123.0927 | 123.056 | 123.0194 | -0.39368
4645.8594 | 123.1018 | -122.8821 | 0.21057 | -0.069275 | 0.035782 | 0.0055114 | 0.0061865 | -0.0083974 | 0.0020016 | -0.0071563 | -0.10399 | -0.011273 | -0.0075344 | -0.0013352 | 0.0085941 | -0.019348 | 0.11444 | 0.091553 | -0.009155 | 0.050354 | 0.31128 | -0.07782 | -0.22888 | 0.036621 | 0.064087 | -0.086975 | 0.20599 | 0.1831 | -0.18768 | -0.2243 | 122.8043 | 122.6532 | 0.10071 | 122.9736 | 122.9324 | 0.27924 | -0.09613 | 122.6944 | 122.6578 | -0.004577 | 122.9187 | 122.7951 | 0.13733 | -0.027466 | 123.1934 | 122.9965 | 122.8729 | -0.43945 | 123.0881 | 123.0652 | 122.9462 | -0.43488
4647.5469 | 123.2437 | -122.8317 | 0.17853 | -0.16846 | 0.036423 | 0.0055114 | 0.010032 | -0.0088248 | 0.001788 | -0.0071563 | -0.24132 | -0.012127 | -0.003262 | -0.0034714 | 0.0036807 | -0.017212 | 0.10986 | 0.11902 | 0.050354 | 0.11444 | 0.39368 | -0.009155 | -0.19226 | 0.068665 | 0.1236 | -0.004578 | 0.27008 | 0.25177 | -0.13733 | -0.16479 | 122.8226 | 122.6395 | 0.21515 | 122.9507 | 122.9462 | 0.3067 | -0.068665 | 122.6944 | 122.6669 | 0.091553 | 122.9004 | 122.8271 | 0.16022 | 0.073242 | 123.2254 | 122.9416 | 122.8821 | -0.37079 | 123.1018 | 123.0835 | 122.9553 | -0.34332
4649.25 | 123.1659 | -122.8546 | 0.19684 | -0.10742 | 0.037064 | 0.0057252 | 0.010245 | -0.0094656 | 0.003497 | -0.0065155 | -0.13451 | -0.010205 | -0.0034756 | -0.0013352 | 0.0043215 | -0.018066 | 0.10986 | 0.10529 | 0.009155 | 0.059509 | 0.32959 | -0.064087 | -0.2243 | 0.068665 | 0.11902 | -0.045776 | 0.2243 | 0.19684 | -0.16479 | -0.2243 | 122.7905 | 122.6303 | 0.13275 | 122.9599 | 122.9141 | 0.28381 | -0.086975 | 122.6898 | 122.6303 | 0.027466 | 122.9233 | 122.8088 | 0.17853 | 0 | 123.1842 | 122.9645 | 122.8638 | -0.42114 | 123.0789 | 123.0515 | 122.9736 | -0.42114
4650.9844 | 123.143 | -122.9004 | 0.19684 | 0.13672 | 0.037277 | 0.0052978 | 0.0076819 | -0.01032 | 0.00050622 | -0.0071563 | 0.102 | -0.011487 | -0.0064664 | -5.3406e-05 | 0.0075259 | -0.016784 | 0.009155 | 0 | -0.068665 | -0.032043 | 0.28839 | -0.10529 | -0.2655 | 0.013733 | 0.018311 | -0.086975 | 0.19684 | 0.14648 | -0.19684 | -0.22888 | 122.7951 | 122.6349 | 0.091553 | 122.9004 | 122.8683 | 0.23346 | -0.18768 | 122.7036 | 122.6715 | 0 | 122.9141 | 122.8134 | 0.14191 | -0.050354 | 123.1888 | 122.9095 | 122.8317 | -0.46234 | 123.0972 | 123.0469 | 122.9187 | -0.42572
4652.6719 | 123.2437 | -122.8409 | 0.17853 | -0.18372 | 0.035996 | 0.0065796 | 0.0078955 | -0.0081838 | 0.00050622 | -0.0092927 | -0.27946 | -0.012555 | -0.0075344 | -0.0030442 | 0.0045351 | -0.015716 | 0.10529 | 0.11444 | 0.041199 | 0.09613 | 0.39825 | -0.013733 | -0.19684 | 0.045776 | 0.12817 | -0.018311 | 0.28381 | 0.24261 | -0.13275 | -0.16937 | 122.8271 | 122.644 | 0.21973 | 122.9553 | 122.937 | 0.29297 | -0.073242 | 122.7081 | 122.6715 | 0.10528 | 122.8867 | 122.8226 | 0.15106 | 0.064087 | 123.2391 | 122.9462 | 122.8821 | -0.37537 | 123.1247 | 123.0835 | 122.9691 | -0.3479
4654.3906 | 123.1293 | -122.8867 | 0.21973 | 0.13672 | 0.033432 | 0.0061524 | 0.0068273 | -0.0073294 | -0.0022708 | -0.0099335 | 0.20119 | -0.013623 | -0.0088162 | -0.0021896 | 0.0047489 | -0.016571 | 0.09613 | 0.10986 | 0.050354 | 0.068665 | 0.24719 | -0.064087 | -0.24261 | 0.064087 | 0.11444 | 0.013733 | 0.14648 | 0.10986 | -0.19226 | -0.22888 | 122.8226 | 122.644 | 0.027465 | 122.9965 | 122.9553 | 0.31128 | -0.1236 | 122.6944 | 122.6578 | -0.073243 | 122.9507 | 122.9004 | 0.24261 | -0.10986 | 123.1338 | 122.9828 | 122.937 | -0.46234 | 123.0331 | 122.9965 | 123.0011 | -0.44861
4656.0938 | 123.1659 | -122.8683 | 0.19684 | -0.0082397 | 0.032364 | 0.0076478 | 0.0070409 | -0.010747 | -0.007825 | -0.010361 | 0.094375 | -0.014905 | -0.0073208 | -0.0049668 | 4.9132e-05 | -0.016571 | 0.064087 | 0.10529 | 0.086975 | 0.086975 | 0.34332 | -0.009155 | -0.17395 | 0.086975 | 0.16937 | 0.082397 | 0.23804 | 0.21515 | -0.11902 | -0.16022 | 122.8592 | 122.6944 | 0.14648 | 122.9736 | 122.9553 | 0.26092 | -0.13275 | 122.7493 | 122.7081 | 0.041199 | 122.9553 | 122.9507 | 0.24261 | 0.018311 | 123.2117 | 122.9324 | 122.9553 | -0.37079 | 123.1064 | 123.0835 | 123.0377 | -0.35706
4657.7812 | 123.0927 | -122.8729 | 0.20599 | 0.14435 | 0.03215 | 0.0087158 | 0.0072547 | -0.0090384 | 0.00093342 | -0.0086517 | 0.16304 | -0.012982 | -0.0075344 | -0.0024032 | 0.0058169 | -0.016998 | 0.091553 | 0.10071 | 0.059509 | 0.050354 | 0.21973 | -0.068665 | -0.23346 | 0.10986 | 0.12817 | 0.036621 | 0.17853 | 0.13275 | -0.14648 | -0.21515 | 122.8043 | 122.6395 | 0.013733 | 122.9736 | 122.9233 | 0.28381 | -0.11444 | 122.7264 | 122.6578 | -0.027466 | 122.9828 | 122.9095 | 0.25177 | -0.073243 | 123.0927 | 122.9645 | 122.9324 | -0.43945 | 123.0515 | 123.0057 | 123.0011 | -0.42114
4659.4844 | 123.1018 | -122.9004 | 0.21057 | 0.17487 | 0.033005 | 0.0052978 | 0.0076819 | -0.0083974 | -0.0018436 | -0.0082245 | 0.19356 | -0.012341 | -0.0075344 | -0.0021896 | 0.0077395 | -0.018066 | 0.091553 | 0.073242 | 0.045776 | 0.045776 | 0.2243 | -0.086975 | -0.24261 | 0.086975 | 0.10529 | 0.027466 | 0.15564 | 0.1236 | -0.17853 | -0.21057 | 122.8134 | 122.6578 | 0.013733 | 122.9736 | 122.9462 | 0.28839 | -0.11902 | 122.7219 | 122.6898 | -0.054931 | 122.9874 | 122.9279 | 0.23804 | -0.086975 | 123.1247 | 122.9919 | 122.9462 | -0.45319 | 123.056 | 123.024 | 123.0057 | -0.42114
4661.1875 | 123.1888 | -122.8455 | 0.19684 | -0.21423 | 0.034073 | 0.0072204 | 0.0091773 | -0.0066884 | -0.0020572 | -0.010788 | -0.22606 | -0.013623 | -0.004971 | -0.0017624 | 0.0036807 | -0.018493 | 0.16022 | 0.13275 | 0.07782 | 0.12817 | 0.42114 | 0.036621 | -0.14648 | 0.091553 | 0.14648 | 0.022888 | 0.31586 | 0.2655 | -0.11444 | -0.12817 | 122.8821 | 122.699 | 0.2243 | 122.9782 | 122.9736 | 0.27466 | -0.036621 | 122.731 | 122.7173 | 0.11902 | 122.937 | 122.8683 | 0.15106 | 0.068665 | 123.2666 | 123.0057 | 122.9233 | -0.34332 | 123.1613 | 123.111 | 122.9919 | -0.32501
4662.9375 | 123.111 | -122.8958 | 0.21057 | 0.17487 | 0.034287 | 0.0050842 | 0.0057593 | -0.009252 | -0.00013458 | -0.0090791 | 0.18593 | -0.013623 | -0.0081754 | -0.0021896 | 0.0062441 | -0.01828 | 0.10529 | 0.091553 | 0.041199 | 0.045776 | 0.21057 | -0.082397 | -0.25635 | 0.086975 | 0.1236 | 0.009155 | 0.1236 | 0.11902 | -0.19684 | -0.21973 | 122.8134 | 122.6395 | 0 | 122.9874 | 122.9416 | 0.30212 | -0.10529 | 122.699 | 122.6761 | -0.086975 | 122.9828 | 122.905 | 0.22888 | -0.091552 | 123.1064 | 123.0011 | 122.937 | -0.46692 | 123.0194 | 123.0148 | 123.0194 | -0.4303
4664.625 | 123.1567 | -122.8683 | 0.21057 | 0.11383 | 0.0345 | 0.006366 | 0.0072547 | -0.010747 | 0.001788 | -0.0080109 | 0.11726 | -0.011059 | -0.0081754 | -0.0030442 | 0.0075259 | -0.018066 | 0.064087 | 0.036621 | -0.004578 | 0.027466 | 0.24261 | -0.086975 | -0.25635 | 0.091553 | 0.11902 | 0.009155 | 0.16937 | 0.14648 | -0.15106 | -0.19684 | 122.7814 | 122.612 | 0.032044 | 122.905 | 122.8958 | 0.28381 | -0.14648 | 122.7173 | 122.6715 | -0.041198 | 122.9599 | 122.8775 | 0.20599 | -0.064087 | 123.111 | 122.9324 | 122.8638 | -0.46692 | 123.0377 | 123.0148 | 122.9874 | -0.40741
4666.3125 | 123.1934 | -122.8775 | 0.19226 | -0.099793 | 0.035996 | 0.0070068 | 0.0074683 | -0.0098928 | 0.004565 | -0.0095063 | -0.16502 | -0.011487 | -0.0051846 | -0.0017624 | 0.0075259 | -0.018066 | 0.13733 | 0.07782 | 0.004578 | 0.064087 | 0.33417 | -0.064087 | -0.21057 | 0.059509 | 0.09613 | -0.045776 | 0.2243 | 0.20142 | -0.15564 | -0.19684 | 122.8134 | 122.6669 | 0.14191 | 122.9553 | 122.9416 | 0.27466 | -0.054932 | 122.7219 | 122.6807 | 0.032043 | 122.937 | 122.8317 | 0.15106 | 0.009155 | 123.2117 | 123.0148 | 122.8821 | -0.40283 | 123.1018 | 123.0789 | 122.9736 | -0.3891
4668.0625 | 123.2117 | -122.8729 | 0.19226 | -0.10742 | 0.035782 | 0.006366 | 0.0085363 | -0.009252 | 0.00093342 | -0.0084381 | -0.18028 | -0.012555 | -0.0056118 | -0.0017624 | 0.0077395 | -0.016998 | 0.11444 | 0.091553 | 0.004578 | 0.086975 | 0.3479 | -0.041199 | -0.21515 | 0.082397 | 0.13275 | -0.041199 | 0.23346 | 0.21515 | -0.19226 | -0.21515 | 122.8317 | 122.6578 | 0.15564 | 122.9645 | 122.9599 | 0.30212 | -0.07782 | 122.6807 | 122.6578 | 0.041198 | 122.9553 | 122.8317 | 0.17395 | 0.022888 | 123.2208 | 122.9874 | 122.8775 | -0.40741 | 123.1064 | 123.0881 | 123.0057 | -0.40741
4669.7656 | 123.0927 | -122.9004 | 0.2243 | 0.075684 | 0.036636 | 0.0076478 | 0.0096045 | -0.011815 | 0.00050622 | -0.0073701 | 0.025711 | -0.011059 | -0.006039 | 0.00016019 | 0.0075259 | -0.017639 | -0.004578 | -0.041199 | -0.082397 | -0.018311 | 0.3067 | -0.10071 | -0.28381 | -0.045776 | -0.004578 | -0.1236 | 0.21057 | 0.17395 | -0.21973 | -0.22888 | 122.7997 | 122.6166 | 0.082398 | 122.8592 | 122.8821 | 0.2655 | -0.22888 | 122.6807 | 122.6715 | -0.013733 | 122.8546 | 122.7768 | 0.10529 | -0.050354 | 123.2071 | 122.8958 | 122.818 | -0.50812 | 123.111 | 123.0743 | 122.8958 | -0.45319
4671.4688 | 123.23 | -122.8271 | 0.1831 | -0.13031 | 0.034287 | 0.0085022 | 0.0087499 | -0.011175 | -0.006757 | -0.0090791 | -0.08873 | -0.016827 | -0.0058254 | -0.0028306 | -0.0010191 | -0.015716 | 0.17395 | 0.2655 | 0.19684 | 0.1831 | 0.35706 | 0.045776 | -0.11902 | 0.1831 | 0.27924 | 0.16479 | 0.25177 | 0.23804 | -0.068665 | -0.11902 | 122.8729 | 122.7081 | 0.17395 | 123.0927 | 123.0103 | 0.30212 | -0.009155 | 122.7585 | 122.7081 | 0.068665 | 123.0103 | 122.9919 | 0.28381 | 0.054932 | 123.1842 | 123.0011 | 123.024 | -0.30212 | 123.0789 | 123.0652 | 123.1064 | -0.30212
4673.1719 | 123.2117 | -122.8455 | 0.18768 | -0.00061023 | 0.032578 | 0.004657 | 0.0111 | -0.009252 | -0.004407 | -0.011002 | 0.010452 | -0.015973 | -0.0047574 | -0.0015488 | -0.0014463 | -0.016998 | 0.07782 | 0.15106 | 0.10986 | 0.11444 | 0.32501 | -0.009155 | -0.17853 | 0.12817 | 0.20599 | 0.11444 | 0.25177 | 0.21057 | -0.09613 | -0.13733 | 122.8363 | 122.6669 | 0.13733 | 122.9965 | 122.9599 | 0.29297 | -0.10986 | 122.7493 | 122.7081 | 0.064087 | 122.9736 | 122.9599 | 0.25177 | 0.022888 | 123.1705 | 122.9233 | 122.9553 | -0.36621 | 123.0972 | 123.056 | 123.0515 | -0.32501
4674.8594 | 123.1384 | -122.8912 | 0.19226 | 0.022278 | 0.030869 | 0.004657 | 0.0072547 | -0.010106 | -0.0048344 | -0.0097199 | 0.079117 | -0.016186 | -0.0062528 | -0.0015488 | 0.0041079 | -0.018707 | 0.086975 | 0.13275 | 0.07782 | 0.086975 | 0.31128 | -0.018311 | -0.17853 | 0.10986 | 0.16022 | 0.07782 | 0.23346 | 0.21057 | -0.10529 | -0.16022 | 122.8729 | 122.7127 | 0.11902 | 123.024 | 122.9782 | 0.2655 | -0.10529 | 122.7859 | 122.731 | 0.041198 | 123.0011 | 122.9691 | 0.23804 | 0.01831 | 123.2025 | 122.9782 | 122.9691 | -0.37079 | 123.1247 | 123.1018 | 123.0515 | -0.35248
4676.5469 | 123.0972 | -122.8912 | 0.21515 | 0.045166 | 0.031723 | 0.0070068 | 0.0089635 | -0.011175 | -0.0039798 | -0.011002 | 0.063858 | -0.015332 | -0.008389 | -0.001976 | 0.0036807 | -0.016784 | 0.10071 | 0.13275 | 0.073242 | 0.07782 | 0.31128 | -0.027466 | -0.19226 | 0.10986 | 0.14648 | 0.064087 | 0.22888 | 0.20142 | -0.10986 | -0.15564 | 122.8638 | 122.699 | 0.09613 | 123.024 | 122.9691 | 0.27008 | -0.11444 | 122.7814 | 122.7356 | 0.013733 | 123.0011 | 122.9553 | 0.21973 | -0.013733 | 123.2025 | 122.9919 | 122.9645 | -0.40741 | 123.1201 | 123.0927 | 123.0377 | -0.37079
4678.25 | 123.111 | -122.8912 | 0.21515 | 0.17487 | 0.034073 | 0.004657 | 0.0083227 | -0.0071158 | 0.0026424 | -0.0075837 | 0.1783 | -0.01405 | -0.0090298 | -0.0015488 | 0.0030399 | -0.018707 | 0.10071 | 0.091553 | 0.027466 | 0.045776 | 0.21057 | -0.091553 | -0.26093 | 0.11444 | 0.1236 | 0.013733 | 0.15564 | 0.1236 | -0.19226 | -0.21973 | 122.7997 | 122.6303 | -0.004578 | 122.9828 | 122.937 | 0.3067 | -0.11444 | 122.699 | 122.6715 | -0.059509 | 123.0057 | 122.905 | 0.23346 | -0.091553 | 123.1018 | 122.9919 | 122.9187 | -0.47607 | 123.0469 | 123.0148 | 123.0148 | -0.43488
4680.0156 | 123.1064 | -122.8775 | 0.20599 | 0.1825 | 0.033859 | 0.0055114 | 0.0040503 | -0.0077566 | 0.00029262 | -0.0056611 | 0.18593 | -0.013836 | -0.007748 | -0.0017624 | 0.0058169 | -0.017425 | 0.11444 | 0.07782 | 0.045776 | 0.036621 | 0.21515 | -0.10071 | -0.2655 | 0.10986 | 0.11902 | 0.018311 | 0.15106 | 0.11902 | -0.1831 | -0.21057 | 122.7768 | 122.612 | 0.009155 | 122.9553 | 122.9141 | 0.30212 | -0.091553 | 122.6944 | 122.6669 | -0.054932 | 122.9874 | 122.8958 | 0.22888 | -0.086975 | 123.0927 | 122.9919 | 122.9233 | -0.4715 | 123.0286 | 122.9965 | 122.9965 | -0.41657
4681.7031 | 123.143 | -122.8867 | 0.21515 | 0.13672 | 0.03685 | 0.007434 | 0.0070409 | -0.0094656 | 0.0028562 | -0.0067291 | 0.063858 | -0.010632 | -0.0053982 | -0.0024032 | 0.0083805 | -0.017425 | 0.013733 | -0.059509 | -0.10071 | -0.041199 | 0.27008 | -0.11444 | -0.29755 | 0.022888 | 0 | -0.10986 | 0.20599 | 0.16937 | -0.21515 | -0.24261 | 122.7722 | 122.5891 | 0.054932 | 122.8271 | 122.8455 | 0.25635 | -0.20142 | 122.6715 | 122.644 | -0.009155 | 122.9095 | 122.7768 | 0.13275 | -0.045776 | 123.1567 | 122.9004 | 122.7859 | -0.5127 | 123.0927 | 123.056 | 122.8867 | -0.45776
4683.4219 | 123.1293 | -122.8638 | 0.21515 | 0.0070193 | 0.033859 | 0.0087158 | 0.0087499 | -0.008611 | -0.006757 | -0.011642 | 0.063858 | -0.014905 | -0.0071072 | -0.0028306 | 0.0026125 | -0.018066 | 0.091553 | 0.11444 | 0.10071 | 0.07782 | 0.32044 | -0.022888 | -0.20142 | 0.10071 | 0.15564 | 0.068665 | 0.24261 | 0.19684 | -0.12817 | -0.16479 | 122.8409 | 122.6624 | 0.10529 | 122.9782 | 122.9416 | 0.27924 | -0.1236 | 122.7356 | 122.699 | 0.027466 | 122.9645 | 122.9324 | 0.23346 | -0.018311 | 123.1842 | 122.9553 | 122.9645 | -0.41657 | 123.1064 | 123.0606 | 123.0194 | -0.37994
4685.125 | 123.143 | -122.8867 | 0.21057 | 0.098572 | 0.033859 | 0.0067932 | 0.0053321 | -0.008611 | 0.0026424 | -0.0075837 | 0.13252 | -0.011487 | -0.010952 | -0.001976 | 0.0079531 | -0.016357 | 0.064087 | -0.036621 | -0.059509 | -0.018311 | 0.28839 | -0.11444 | -0.25177 | 0.041199 | 0.036621 | -0.059509 | 0.1831 | 0.14648 | -0.17395 | -0.23804 | 122.7722 | 122.6349 | 0.07782 | 122.85 | 122.8683 | 0.23346 | -0.14648 | 122.7127 | 122.6486 | -0.027466 | 122.9279 | 122.8271 | 0.17853 | -0.064087 | 123.175 | 122.9507 | 122.8271 | -0.46234 | 123.0698 | 123.0331 | 122.9233 | -0.44861
4686.8125 | 123.0972 | -122.8867 | 0.21515 | -0.0082397 | 0.036423 | 0.0076478 | 0.0068273 | -0.0096792 | 0.0028562 | -0.0069427 | 0.0028229 | -0.0091367 | -0.00668 | -0.00026701 | 0.0083805 | -0.018921 | 0.064087 | -0.036621 | -0.07782 | -0.018311 | 0.28839 | -0.10071 | -0.2655 | -0.009155 | 0.018311 | -0.11902 | 0.21973 | 0.18768 | -0.21057 | -0.25177 | 122.7859 | 122.6212 | 0.073242 | 122.85 | 122.8683 | 0.24719 | -0.15106 | 122.6761 | 122.6349 | 0.004578 | 122.8775 | 122.7676 | 0.13275 | -0.027466 | 123.175 | 122.9507 | 122.8088 | -0.48065 | 123.1064 | 123.0743 | 122.905 | -0.46692
4688.5156 | 123.143 | -122.8409 | 0.21515 | -0.084534 | 0.036636 | 0.0072204 | 0.0087499 | -0.0079702 | 0.001788 | -0.0056611 | -0.11925 | -0.012127 | -0.0079618 | -0.0011216 | 0.0075259 | -0.017852 | 0.11444 | 0.091553 | 0.009155 | 0.059509 | 0.31128 | -0.073242 | -0.22888 | 0.054932 | 0.10071 | -0.059509 | 0.2243 | 0.17395 | -0.1831 | -0.20142 | 122.7676 | 122.612 | 0.09613 | 122.9324 | 122.9004 | 0.28839 | -0.10071 | 122.6578 | 122.6395 | 0.009155 | 122.8958 | 122.7814 | 0.14191 | -0.041199 | 123.1522 | 122.9553 | 122.85 | -0.44403 | 123.0652 | 123.0148 | 122.9416 | -0.41657
4690.2031 | 123.2529 | -122.8638 | 0.18768 | -0.24475 | 0.0345 | 0.0065796 | 0.010673 | -0.0083974 | -0.002698 | -0.0086517 | -0.20317 | -0.014477 | -0.0045438 | -0.0015488 | 0.0030399 | -0.01828 | 0.10071 | 0.10986 | 0.045776 | 0.10986 | 0.39368 | -0.004578 | -0.16479 | 0.050354 | 0.13275 | -0.018311 | 0.29755 | 0.25177 | -0.1236 | -0.17853 | 122.8592 | 122.699 | 0.20599 | 122.9736 | 122.9736 | 0.27466 | -0.086975 | 122.7402 | 122.6852 | 0.10986 | 122.9141 | 122.8455 | 0.16022 | 0.064087 | 123.2574 | 122.9645 | 122.9095 | -0.35248 | 123.1613 | 123.1155 | 122.9965 | -0.36621
4691.875 | 123.1338 | -122.8867 | 0.21515 | 0.11383 | 0.036209 | 0.0040162 | 0.0087499 | -0.008611 | 0.00071982 | -0.0069427 | 0.16304 | -0.013196 | -0.0079618 | -0.0015488 | 0.0075259 | -0.016571 | 0.009155 | -0.004578 | -0.054932 | -0.013733 | 0.24719 | -0.091553 | -0.27924 | 0.059509 | 0.045776 | -0.027466 | 0.16937 | 0.12817 | -0.20142 | -0.23804 | 122.7951 | 122.6074 | 0.032043 | 122.8821 | 122.8729 | 0.2655 | -0.20599 | 122.6852 | 122.6486 | -0.045776 | 122.9462 | 122.8592 | 0.21057 | -0.086975 | 123.1338 | 122.8958 | 122.8317 | -0.49438 | 123.056 | 123.0148 | 122.9324 | -0.45319
4693.5625 | 123.1979 | -122.8683 | 0.19684 | -0.099793 | 0.036423 | 0.0050842 | 0.0085363 | -0.0094656 | 0.0026424 | -0.0077973 | -0.12688 | -0.012127 | -0.006039 | -0.001976 | 0.0070987 | -0.017852 | 0.10986 | 0.10529 | 0.032043 | 0.073242 | 0.32959 | -0.050354 | -0.20599 | 0.059509 | 0.1236 | -0.045776 | 0.21515 | 0.17853 | -0.16937 | -0.21057 | 122.818 | 122.6624 | 0.13275 | 122.9736 | 122.9416 | 0.27924 | -0.086975 | 122.699 | 122.6578 | 0.018311 | 122.9279 | 122.8226 | 0.1648 | -0.01831 | 123.1979 | 122.9782 | 122.9004 | -0.40283 | 123.0835 | 123.0469 | 122.9919 | -0.40741
4695.25 | 123.1476 | -122.8546 | 0.20599 | -0.11505 | 0.037491 | 0.006366 | 0.0089635 | -0.010106 | 0.0020016 | -0.0075837 | -0.10399 | -0.011273 | -0.0075344 | -0.0034714 | 0.0073123 | -0.019348 | 0.086975 | 0.10529 | 0.013733 | 0.064087 | 0.32501 | -0.059509 | -0.23346 | 0.059509 | 0.09613 | -0.050354 | 0.21057 | 0.18768 | -0.16479 | -0.19684 | 122.7951 | 122.6212 | 0.11902 | 122.9599 | 122.9187 | 0.29755 | -0.11902 | 122.6898 | 122.6578 | 0.004577 | 122.9141 | 122.8043 | 0.14648 | -0.018311 | 123.1796 | 122.9416 | 122.8683 | -0.43945 | 123.0652 | 123.0423 | 122.9507 | -0.40283
4696.9844 | 123.1064 | -122.9004 | 0.21515 | -0.084534 | 0.036423 | 0.0059388 | 0.0093909 | -0.010534 | 0.0026424 | -0.0067291 | -0.073471 | -0.010632 | -0.0062528 | -0.0011216 | 0.0085941 | -0.018707 | 0.082397 | 0.10986 | 0.009155 | 0.050354 | 0.32501 | -0.073242 | -0.21973 | 0.027466 | 0.068665 | -0.091553 | 0.21515 | 0.19226 | -0.17853 | -0.23346 | 122.8271 | 122.6807 | 0.10986 | 123.0103 | 122.9507 | 0.27008 | -0.13275 | 122.7219 | 122.6669 | 0 | 122.9279 | 122.8088 | 0.14191 | -0.022888 | 123.2254 | 122.9828 | 122.9095 | -0.43488 | 123.1155 | 123.0927 | 122.9691 | -0.44861
4698.6719 | 123.0972 | -122.8821 | 0.20599 | -0.015869 | 0.035996 | 0.0076478 | 0.0089635 | -0.008611 | 0.00093342 | -0.0065155 | -0.035324 | -0.0091367 | -0.006039 | 0.0010148 | 0.0073123 | -0.018066 | 0.045776 | 0.082397 | -0.027466 | 0.022888 | 0.30212 | -0.073242 | -0.24719 | -0.009155 | 0.022888 | -0.09613 | 0.21515 | 0.17853 | -0.20142 | -0.24261 | 122.8088 | 122.6349 | 0.09613 | 122.9645 | 122.905 | 0.27008 | -0.16022 | 122.6807 | 122.6395 | 0.009155 | 122.8729 | 122.7859 | 0.14649 | -0.027466 | 123.1842 | 122.9279 | 122.8546 | -0.45319 | 123.0972 | 123.0606 | 122.905 | -0.44861
4700.3594 | 123.2346 | -122.8638 | 0.20599 | -0.2066 | 0.036209 | 0.0038024 | 0.011954 | -0.011175 | -0.00013458 | -0.0086517 | -0.14214 | -0.011487 | -0.006039 | -0.0028306 | 0.0034671 | -0.016998 | 0.09613 | 0.10986 | 0.041199 | 0.082397 | 0.37537 | -0.018311 | -0.21057 | 0.050354 | 0.1236 | -0.009155 | 0.25177 | 0.21057 | -0.15106 | -0.20142 | 122.8455 | 122.6532 | 0.16937 | 122.9736 | 122.9462 | 0.29297 | -0.10986 | 122.7127 | 122.6624 | 0.045776 | 122.9141 | 122.8546 | 0.19226 | 0.004577 | 123.2391 | 122.9599 | 122.905 | -0.41657 | 123.1155 | 123.0743 | 122.9874 | -0.40741
4702.0625 | 123.1888 | -122.85 | 0.17853 | -0.18372 | 0.030869 | 0.0061524 | 0.010245 | -0.007543 | -0.006116 | -0.0084381 | -0.11162 | -0.014477 | -0.0058254 | -0.0047532 | -0.00059167 | -0.016998 | 0.15106 | 0.27466 | 0.20599 | 0.19226 | 0.37079 | 0.045776 | -0.11444 | 0.17853 | 0.29297 | 0.16022 | 0.26093 | 0.2243 | -0.059509 | -0.09613 | 122.8958 | 122.7356 | 0.19226 | 123.1247 | 123.0423 | 0.3067 | -0.027466 | 122.7905 | 122.7539 | 0.082397 | 123.0286 | 123.0103 | 0.25635 | 0.045776 | 123.2208 | 123.0011 | 123.056 | -0.29297 | 123.111 | 123.0743 | 123.143 | -0.27466
4703.75 | 123.111 | -122.8729 | 0.20599 | 0.068054 | 0.031723 | 0.0076478 | 0.0087499 | -0.0094656 | -0.0037662 | -0.010788 | 0.10963 | -0.012768 | -0.0075344 | -0.0028306 | 0.00068993 | -0.016784 | 0.073242 | 0.1236 | 0.082397 | 0.082397 | 0.29297 | -0.036621 | -0.20142 | 0.07782 | 0.14648 | 0.068665 | 0.23346 | 0.21057 | -0.12817 | -0.15564 | 122.8363 | 122.6715 | 0.086975 | 122.9965 | 122.9553 | 0.28381 | -0.13275 | 122.7448 | 122.7173 | 0.027465 | 122.9507 | 122.9416 | 0.22431 | 0.004577 | 123.1659 | 122.9462 | 122.9553 | -0.40741 | 123.1064 | 123.0835 | 123.0194 | -0.36163
4705.4531 | 123.1293 | -122.8821 | 0.20142 | 0.12146 | 0.034073 | 0.0052978 | 0.0053321 | -0.0094656 | 0.0022152 | -0.0080109 | 0.19356 | -0.012555 | -0.0068936 | -0.0013352 | 0.0079531 | -0.016357 | 0.086975 | 0.082397 | 0.036621 | 0.059509 | 0.23804 | -0.068665 | -0.25177 | 0.073242 | 0.10986 | 0.009155 | 0.14191 | 0.11902 | -0.1831 | -0.21057 | 122.8134 | 122.6303 | 0.036621 | 122.9645 | 122.9416 | 0.31128 | -0.11444 | 122.699 | 122.6715 | -0.059509 | 122.9553 | 122.8912 | 0.21973 | -0.082397 | 123.1201 | 122.9691 | 122.9187 | -0.45319 | 123.024 | 123.0011 | 122.9919 | -0.41199
4707.1406 | 123.1476 | -122.8912 | 0.21515 | 0.11383 | 0.035141 | 0.0061524 | 0.0070409 | -0.0094656 | 0.0013608 | -0.0090791 | 0.071487 | -0.011487 | -0.0075344 | -0.0032578 | 0.0079531 | -0.020202 | 0.013733 | -0.027466 | -0.082397 | -0.032043 | 0.28381 | -0.11444 | -0.28381 | 0.009155 | 0.004578 | -0.086975 | 0.21057 | 0.1831 | -0.19226 | -0.22888 | 122.7768 | 122.6074 | 0.068664 | 122.8638 | 122.8592 | 0.25177 | -0.20142 | 122.699 | 122.6624 | -0.004578 | 122.9004 | 122.8043 | 0.14191 | -0.032044 | 123.175 | 122.905 | 122.8088 | -0.49896 | 123.1018 | 123.0743 | 122.8958 | -0.44403
4708.8594 | 123.1247 | -122.8729 | 0.19684 | 0.15198 | 0.0345 | 0.0059388 | 0.0044775 | -0.0081838 | -0.00056178 | -0.0082245 | 0.19356 | -0.01405 | -0.0064664 | -0.0021896 | 0.0060305 | -0.017212 | 0.10529 | 0.086975 | 0.045776 | 0.059509 | 0.21973 | -0.07782 | -0.25177 | 0.082397 | 0.11444 | 0.009155 | 0.14648 | 0.13275 | -0.1831 | -0.2243 | 122.7951 | 122.6212 | 0.022889 | 122.9599 | 122.9324 | 0.31128 | -0.091552 | 122.6898 | 122.6486 | -0.050354 | 122.9553 | 122.8821 | 0.23346 | -0.064087 | 123.0927 | 122.9782 | 122.9187 | -0.44861 | 123.0194 | 123.0057 | 122.9874 | -0.42114
4710.5469 | 123.0972 | -122.8821 | 0.20599 | 0.029907 | 0.035782 | 0.007434 | 0.0053321 | -0.0077566 | 0.0030698 | -0.0086517 | -0.065842 | -0.0095639 | -0.0075344 | -0.0017624 | 0.0081667 | -0.017425 | 0.036621 | -0.027466 | -0.07782 | -0.018311 | 0.28839 | -0.12817 | -0.2655 | -0.036621 | -0.013733 | -0.12817 | 0.20142 | 0.1831 | -0.20142 | -0.24261 | 122.7539 | 122.6166 | 0.082397 | 122.8546 | 122.8638 | 0.24719 | -0.16937 | 122.6807 | 122.6395 | -0.004578 | 122.8455 | 122.7539 | 0.11444 | -0.022889 | 123.1705 | 122.9187 | 122.8043 | -0.4715 | 123.0835 | 123.0652 | 122.8683 | -0.44861
4712.25 | 123.1842 | -122.8683 | 0.20599 | -0.092163 | 0.035568 | 0.0057252 | 0.0066137 | -0.0098928 | 0.00093342 | -0.0058747 | -0.096359 | -0.012127 | -0.008389 | -0.0017624 | 0.0088077 | -0.017212 | 0.11902 | 0.086975 | 0.018311 | 0.07782 | 0.31586 | -0.045776 | -0.23346 | 0.045776 | 0.10071 | -0.045776 | 0.21973 | 0.1831 | -0.19226 | -0.21057 | 122.8226 | 122.6349 | 0.10986 | 122.9553 | 122.9462 | 0.31128 | -0.086975 | 122.6761 | 122.6578 | 0.013733 | 122.9141 | 122.8226 | 0.1648 | -0.022889 | 123.1842 | 122.9874 | 122.8867 | -0.43945 | 123.0881 | 123.0515 | 122.9691 | -0.41657
4713.9375 | 123.2483 | -122.8592 | 0.19226 | -0.18372 | 0.037705 | 0.0042298 | 0.010032 | -0.0098928 | -0.0022708 | -0.0088653 | -0.21843 | -0.014477 | -0.0024076 | -0.0034714 | 0.0023989 | -0.017639 | 0.09613 | 0.11444 | 0.045776 | 0.10986 | 0.37994 | -0.022888 | -0.1831 | 0.045776 | 0.14648 | -0.018311 | 0.28839 | 0.23804 | -0.13275 | -0.17853 | 122.8363 | 122.6761 | 0.18768 | 122.9736 | 122.9691 | 0.29297 | -0.096131 | 122.7264 | 122.6807 | 0.09613 | 122.905 | 122.8409 | 0.16022 | 0.045776 | 123.2391 | 122.9553 | 122.905 | -0.37537 | 123.1476 | 123.0972 | 123.0057 | -0.37079
4715.625 | 123.2071 | -122.8271 | 0.19684 | -0.21423 | 0.032791 | 0.0089294 | 0.010886 | -0.0077566 | -0.0059024 | -0.0088653 | -0.12688 | -0.014477 | -0.0071072 | -0.0024032 | 0.0013309 | -0.016784 | 0.17395 | 0.27924 | 0.20599 | 0.20142 | 0.37994 | 0.059509 | -0.11902 | 0.16022 | 0.27008 | 0.15106 | 0.27924 | 0.24261 | -0.068665 | -0.10529 | 122.8867 | 122.7081 | 0.18311 | 123.1064 | 123.0286 | 0.32044 | -0.022888 | 122.7585 | 122.7219 | 0.082398 | 122.9874 | 122.9782 | 0.25635 | 0.045777 | 123.2071 | 123.0011 | 123.0331 | -0.31586 | 123.1064 | 123.0698 | 123.0972 | -0.30212
4717.3125 | 123.1384 | -122.8546 | 0.20142 | 0.014648 | 0.02916 | 0.0065796 | 0.0036231 | -0.0081838 | -0.0059024 | -0.01207 | 0.063858 | -0.013836 | -0.0073208 | -0.0043258 | 0.0026125 | -0.016357 | 0.086975 | 0.1236 | 0.10986 | 0.068665 | 0.32501 | -0.013733 | -0.18768 | 0.082397 | 0.16479 | 0.082397 | 0.23346 | 0.20142 | -0.10986 | -0.16937 | 122.8409 | 122.6669 | 0.1236 | 122.9782 | 122.9233 | 0.25635 | -0.11444 | 122.7448 | 122.6852 | 0.032043 | 122.937 | 122.937 | 0.25177 | 0 | 123.1796 | 122.9416 | 122.9645 | -0.3891 | 123.0881 | 123.056 | 123.0194 | -0.37079
4719.0312 | 123.0972 | -122.8867 | 0.22888 | 0.17487 | 0.032578 | 0.0089294 | 0.0074683 | -0.0083974 | -0.0012028 | -0.0097199 | 0.13252 | -0.013196 | -0.0086026 | -0.0024032 | 0.0062441 | -0.016357 | 0.10071 | 0.10071 | 0.050354 | 0.050354 | 0.21515 | -0.07782 | -0.26093 | 0.10529 | 0.13275 | 0.041199 | 0.17395 | 0.13275 | -0.16479 | -0.21973 | 122.8088 | 122.6257 | -0.013733 | 122.9874 | 122.937 | 0.31128 | -0.12817 | 122.7219 | 122.6669 | -0.054932 | 122.9919 | 122.9279 | 0.26093 | -0.096131 | 123.1018 | 122.9874 | 122.937 | -0.48981 | 123.0606 | 123.0194 | 123.0194 | -0.44861
4720.7188 | 123.143 | -122.8821 | 0.21515 | 0.052795 | 0.038132 | 0.0044434 | 0.0061865 | -0.01032 | 0.0028562 | -0.0099335 | 0.04097 | -0.012768 | -0.007748 | -0.0017624 | 0.0062441 | -0.022766 | 0.027466 | -0.054932 | -0.082397 | -0.036621 | 0.28381 | -0.10529 | -0.2655 | -0.027466 | -0.022888 | -0.13275 | 0.1831 | 0.15564 | -0.21973 | -0.24719 | 122.7768 | 122.6166 | 0.068664 | 122.8271 | 122.8455 | 0.22888 | -0.18768 | 122.6624 | 122.6349 | -0.032044 | 122.8546 | 122.7493 | 0.11444 | -0.059509 | 123.1659 | 122.9095 | 122.7997 | -0.48065 | 123.0652 | 123.0377 | 122.8592 | -0.46234
4722.4062 | 123.1247 | -122.8821 | 0.21057 | -0.076904 | 0.038986 | 0.0048706 | 0.0064001 | -0.0077566 | 0.0043514 | -0.0077973 | -0.096359 | -0.010846 | -0.0053982 | -0.0011216 | 0.0070987 | -0.018921 | 0.13733 | 0.086975 | 0.009155 | 0.054932 | 0.32044 | -0.068665 | -0.24261 | 0.032043 | 0.07782 | -0.07782 | 0.23804 | 0.20599 | -0.17853 | -0.23346 | 122.8134 | 122.6395 | 0.10986 | 122.9691 | 122.937 | 0.29755 | -0.073242 | 122.7036 | 122.6486 | 0.027466 | 122.9141 | 122.8043 | 0.15564 | -0.004577 | 123.2025 | 123.0194 | 122.8912 | -0.45319 | 123.1201 | 123.0881 | 122.9599 | -0.44403
4724.1094 | 123.2254 | -122.8409 | 0.18768 | -0.1532 | 0.037705 | 0.0033752 | 0.011741 | -0.0083974 | 0.0030698 | -0.0090791 | -0.15739 | -0.013409 | -0.0056118 | -0.001976 | 0.0056033 | -0.018707 | 0.11902 | 0.082397 | 0.027466 | 0.082397 | 0.34332 | -0.045776 | -0.21973 | 0.054932 | 0.11902 | -0.027466 | 0.23346 | 0.20599 | -0.16479 | -0.18768 | 122.7951 | 122.6212 | 0.15564 | 122.9233 | 122.9233 | 0.30212 | -0.068664 | 122.6761 | 122.6532 | 0.045776 | 122.8958 | 122.8134 | 0.16022 | 0.018311 | 123.1842 | 122.9599 | 122.8683 | -0.40741 | 123.0743 | 123.0469 | 122.9599 | -0.37537
4725.7969 | 123.1338 | -122.8821 | 0.20599 | -0.061646 | 0.035355 | 0.0065796 | 0.0074683 | -0.0079702 | 0.0028562 | -0.0077973 | -0.096359 | -0.013196 | -0.004971 | -0.001976 | 0.0062441 | -0.017425 | 0.09613 | 0.10529 | 0.013733 | 0.064087 | 0.32959 | -0.054932 | -0.21515 | 0.050354 | 0.07782 | -0.082397 | 0.23346 | 0.18768 | -0.18768 | -0.20142 | 122.8271 | 122.6669 | 0.1236 | 122.9874 | 122.9462 | 0.27924 | -0.10986 | 122.6944 | 122.6807 | 0.027465 | 122.9324 | 122.7997 | 0.11902 | -0.018311 | 123.2117 | 122.9782 | 122.8958 | -0.42114 | 123.1155 | 123.0698 | 122.9599 | -0.40741
4727.5 | 123.2071 | -122.8592 | 0.21057 | -0.27527 | 0.033218 | 0.0072204 | 0.013023 | -0.0098928 | -0.0039798 | -0.0095063 | -0.22606 | -0.012341 | -0.003262 | -0.00069421 | 0.0034671 | -0.016143 | 0.09613 | 0.13733 | 0.068665 | 0.10071 | 0.40741 | -0.004578 | -0.14191 | 0.064087 | 0.15106 | 0.009155 | 0.31128 | 0.27466 | -0.11902 | -0.14648 | 122.8546 | 122.7173 | 0.19684 | 122.9965 | 122.9599 | 0.24262 | -0.11444 | 122.7402 | 122.7127 | 0.10071 | 122.9233 | 122.8683 | 0.15564 | 0.064087 | 123.2666 | 122.9553 | 122.9279 | -0.35248 | 123.1705 | 123.1338 | 123.0103 | -0.35706
4729.1875 | 123.0789 | -122.9095 | 0.22888 | 0.14435 | 0.03215 | 0.0050842 | 0.0089635 | -0.0079702 | -0.0041934 | -0.0086517 | 0.15541 | -0.015545 | -0.006039 | -0.0015488 | 0.0030399 | -0.015503 | 0.059509 | 0.11902 | 0.073242 | 0.054932 | 0.2243 | -0.082397 | -0.23804 | 0.10071 | 0.14191 | 0.036621 | 0.19226 | 0.15106 | -0.16479 | -0.18768 | 122.8271 | 122.6715 | -0.004578 | 123.0286 | 122.9645 | 0.29297 | -0.16937 | 122.7448 | 122.7219 | -0.036621 | 123.0103 | 122.9462 | 0.2243 | -0.07782 | 123.1339 | 122.9691 | 122.9828 | -0.46692 | 123.1018 | 123.0606 | 123.0515 | -0.41656
4730.8906 | 123.1064 | -122.9095 | 0.20599 | 0.068054 | 0.03215 | 0.0072204 | 0.010032 | -0.0088248 | -0.0048344 | -0.0092927 | 0.11726 | -0.016827 | -0.006039 | -0.0030442 | 0.00047633 | -0.01593 | 0.073242 | 0.11444 | 0.07782 | 0.082397 | 0.29297 | -0.027466 | -0.20142 | 0.10986 | 0.15564 | 0.045776 | 0.22888 | 0.20599 | -0.11902 | -0.16022 | 122.8821 | 122.7081 | 0.086975 | 123.024 | 122.9919 | 0.28381 | -0.13275 | 122.7905 | 122.7493 | 0.022888 | 123.0194 | 122.9553 | 0.20599 | 0 | 123.2025 | 122.9828 | 122.9874 | -0.40741 | 123.1384 | 123.1155 | 123.0652 | -0.36621
4732.5781 | 123.1064 | -122.8912 | 0.21057 | 0.16724 | 0.033646 | 0.0070068 | 0.0034093 | -0.0090384 | -0.002698 | -0.0092927 | 0.15541 | -0.013836 | -0.009457 | -0.0015488 | 0.0064577 | -0.018066 | 0.10529 | 0.091553 | 0.050354 | 0.054932 | 0.2243 | -0.07782 | -0.26093 | 0.091553 | 0.13275 | 0.013733 | 0.16022 | 0.13275 | -0.17853 | -0.20599 | 122.8134 | 122.6303 | 0.013733 | 122.9828 | 122.9462 | 0.31586 | -0.10529 | 122.7127 | 122.6852 | -0.050354 | 122.9828 | 122.905 | 0.21973 | -0.07782 | 123.1155 | 122.9965 | 122.9416 | -0.4715 | 123.0515 | 123.024 | 123.024 | -0.41657
4734.2812 | 123.1476 | -122.8683 | 0.20142 | 0.045166 | 0.030655 | 0.0076478 | 0.0085363 | -0.010106 | -0.0035526 | -0.010147 | 0.048599 | -0.01405 | -0.0058254 | -0.0034714 | 0.0038943 | -0.016357 | 0.091553 | 0.10986 | 0.086975 | 0.091553 | 0.32044 | -0.009155 | -0.17853 | 0.10071 | 0.15564 | 0.068665 | 0.23346 | 0.21973 | -0.11444 | -0.14648 | 122.8592 | 122.6898 | 0.11902 | 122.9782 | 122.9599 | 0.27008 | -0.10986 | 122.7539 | 122.7219 | 0.032043 | 122.9691 | 122.937 | 0.21515 | 0.018311 | 123.1888 | 122.9599 | 122.9553 | -0.37994 | 123.1018 | 123.0881 | 123.024 | -0.3479
4736.0156 | 123.1888 | -122.8683 | 0.20142 | -0.22186 | 0.032364 | 0.0040162 | 0.010245 | -0.008611 | -0.0022708 | -0.0088653 | -0.16502 | -0.012127 | -0.0045438 | -0.0017624 | 0.0015445 | -0.019348 | 0.2243 | 0.23804 | 0.17395 | 0.19226 | 0.36621 | 0.050354 | -0.12817 | 0.16479 | 0.25635 | 0.11902 | 0.2655 | 0.21515 | -0.068665 | -0.13733 | 122.9187 | 122.7402 | 0.16479 | 123.1064 | 123.0606 | 0.32044 | 0.022888 | 122.7997 | 122.731 | 0.064087 | 123.0331 | 122.9874 | 0.25635 | 0.013733 | 123.2346 | 123.0927 | 123.0423 | -0.32959 | 123.1338 | 123.0835 | 123.1247 | -0.33875
4737.7031 | 123.2391 | -122.85 | 0.18768 | -0.14557 | 0.030228 | 0.010638 | 0.0091773 | -0.0083974 | -0.0041934 | -0.010361 | -0.081101 | -0.016827 | -0.0043302 | -0.003685 | 0.0045351 | -0.018707 | 0.21515 | 0.23804 | 0.19226 | 0.1831 | 0.36621 | 0.027466 | -0.13733 | 0.19684 | 0.24261 | 0.15564 | 0.25177 | 0.2243 | -0.059509 | -0.10529 | 122.8775 | 122.7127 | 0.17853 | 123.0881 | 123.0331 | 0.32043 | 0.027466 | 122.7905 | 122.7448 | 0.064087 | 123.0469 | 123.0057 | 0.26093 | 0.036621 | 123.2162 | 123.0652 | 123.0423 | -0.32501 | 123.1018 | 123.0743 | 123.0927 | -0.29297
4739.4062 | 123.1705 | -122.8729 | 0.21515 | 0.14435 | 0.034714 | 0.007434 | 0.0055457 | -0.0094656 | 0.00050622 | -0.0097199 | 0.11726 | -0.012341 | -0.0079618 | -0.0034714 | 0.0096621 | -0.019134 | 0.064087 | -0.027466 | -0.068665 | -0.027466 | 0.27924 | -0.12817 | -0.29297 | 0.064087 | 0.036621 | -0.050354 | 0.19226 | 0.16022 | -0.17853 | -0.2243 | 122.7448 | 122.58 | 0.064087 | 122.8455 | 122.8455 | 0.2655 | -0.15106 | 122.6944 | 122.6486 | -0.022888 | 122.937 | 122.8226 | 0.17395 | -0.054932 | 123.1522 | 122.937 | 122.8043 | -0.50812 | 123.0652 | 123.0331 | 122.9095 | -0.43945
4741.1094 | 123.1247 | -122.9187 | 0.21973 | 0.045166 | 0.039627 | 0.0059388 | 0.0059729 | -0.01032 | 0.005206 | -0.0058747 | -0.050583 | -0.011059 | -0.008389 | -0.00090781 | 0.0079531 | -0.017212 | 0.054932 | -0.022888 | -0.07782 | -0.022888 | 0.28839 | -0.10986 | -0.27466 | -0.013733 | -0.009155 | -0.14648 | 0.20142 | 0.17853 | -0.18768 | -0.25177 | 122.8088 | 122.644 | 0.068664 | 122.8958 | 122.8958 | 0.25177 | -0.16479 | 122.731 | 122.6669 | -0.018311 | 122.905 | 122.7722 | 0.10529 | -0.041199 | 123.2071 | 122.9736 | 122.8409 | -0.49439 | 123.1201 | 123.0972 | 122.9095 | -0.4715
4742.7969 | 123.2254 | -122.8271 | 0.20599 | -0.27527 | 0.033859 | 0.008075 | 0.0093909 | -0.0098928 | -0.0012028 | -0.010361 | -0.27946 | -0.012127 | -0.0062528 | -0.0034714 | 0.0049625 | -0.01828 | 0.14648 | 0.12817 | 0.073242 | 0.10529 | 0.40283 | 0.009155 | -0.15106 | 0.068665 | 0.13275 | -0.018311 | 0.3067 | 0.27924 | -0.13275 | -0.16937 | 122.8363 | 122.6761 | 0.19684 | 122.9553 | 122.9324 | 0.25635 | -0.05951 | 122.6944 | 122.6578 | 0.10071 | 122.8958 | 122.8088 | 0.15106 | 0.073242 | 123.23 | 122.9736 | 122.9004 | -0.35706 | 123.1338 | 123.1064 | 122.9599 | -0.37537
4744.5 | 123.2208 | -122.8363 | 0.17853 | -0.24475 | 0.034287 | 0.0067932 | 0.011741 | -0.0073294 | -0.00013458 | -0.0099335 | -0.25658 | -0.011487 | -0.006039 | -0.0041122 | 0.0047489 | -0.017212 | 0.1236 | 0.1236 | 0.064087 | 0.11444 | 0.41199 | 0.018311 | -0.17395 | 0.07782 | 0.14191 | -0.009155 | 0.31128 | 0.27008 | -0.11444 | -0.14191 | 122.8546 | 122.6624 | 0.23346 | 122.9599 | 122.9507 | 0.28839 | -0.054932 | 122.7219 | 122.6944 | 0.13275 | 122.9141 | 122.8271 | 0.13275 | 0.091553 | 123.2483 | 122.9599 | 122.9004 | -0.35248 | 123.1476 | 123.1064 | 122.9782 | -0.32044
4746.2031 | 123.2071 | -122.8546 | 0.21515 | -0.13031 | 0.035996 | 0.008075 | 0.0061865 | -0.013097 | 0.0020016 | -0.0075837 | -0.14977 | -0.010846 | -0.0068936 | -0.0028306 | 0.0077395 | -0.017425 | 0.12817 | 0.11902 | 0.027466 | 0.07782 | 0.33875 | -0.059509 | -0.21057 | 0.086975 | 0.10529 | -0.064087 | 0.21057 | 0.20142 | -0.16479 | -0.20142 | 122.7951 | 122.644 | 0.1236 | 122.9736 | 122.9324 | 0.28839 | -0.086975 | 122.6898 | 122.6532 | -0.004578 | 122.9416 | 122.7905 | 0.13733 | -0.013733 | 123.1934 | 122.9828 | 122.8821 | -0.42572 | 123.0652 | 123.056 | 122.9599 | -0.41657
4747.9375 | 123.2483 | -122.85 | 0.16479 | -0.19897 | 0.037918 | 0.0044434 | 0.012809 | -0.0088248 | 0.00050622 | -0.0086517 | -0.24132 | -0.015545 | -0.004971 | -0.0024032 | 0.0036807 | -0.016998 | 0.10071 | 0.10986 | 0.041199 | 0.10071 | 0.3891 | -0.036621 | -0.17395 | 0.050354 | 0.14648 | 0 | 0.29297 | 0.24719 | -0.13275 | -0.16937 | 122.8134 | 122.6761 | 0.2243 | 122.9599 | 122.9507 | 0.27466 | -0.064087 | 122.7173 | 122.6807 | 0.12817 | 122.9004 | 122.85 | 0.16937 | 0.082397 | 123.2391 | 122.9507 | 122.8912 | -0.33874 | 123.143 | 123.0972 | 122.9965 | -0.33417
4749.625 | 123.1979 | -122.8729 | 0.19684 | -0.19135 | 0.032578 | 0.006366 | 0.012168 | -0.0098928 | -0.0031254 | -0.0082245 | -0.21843 | -0.014691 | -0.0047574 | -0.0017624 | 0.00068993 | -0.016998 | 0.09613 | 0.14648 | 0.091553 | 0.09613 | 0.41657 | 0 | -0.15106 | 0.07782 | 0.15106 | 0.013733 | 0.3067 | 0.27924 | -0.10986 | -0.16022 | 122.8729 | 122.7219 | 0.21973 | 123.0194 | 122.9691 | 0.24719 | -0.10071 | 122.7631 | 122.7127 | 0.10986 | 122.9507 | 122.8867 | 0.17395 | 0.082398 | 123.2895 | 122.9691 | 122.9645 | -0.3479 | 123.1796 | 123.1522 | 123.024 | -0.35706
4751.3125 | 123.1888 | -122.8409 | 0.17853 | -0.16846 | 0.033218 | 0.0070068 | 0.0091773 | -0.0090384 | -0.0046206 | -0.0086517 | -0.16502 | -0.012341 | -0.0043302 | -0.00090781 | 0.00090353 | -0.016571 | 0.16479 | 0.24261 | 0.17395 | 0.17395 | 0.36163 | 0.018311 | -0.14191 | 0.13733 | 0.26093 | 0.10071 | 0.2655 | 0.24261 | -0.091553 | -0.13733 | 122.8592 | 122.699 | 0.1831 | 123.0835 | 123.0148 | 0.31586 | -0.013733 | 122.7493 | 122.7036 | 0.086975 | 122.9782 | 122.9416 | 0.23804 | 0.064087 | 123.2025 | 123.0057 | 123.0148 | -0.32044 | 123.1064 | 123.0835 | 123.1018 | -0.31586
4753 | 123.0972 | -122.9004 | 0.21515 | 0.11383 | 0.031082 | 0.0072204 | 0.0042639 | -0.011388 | -0.0018436 | -0.0095063 | 0.17067 | -0.014477 | -0.0086026 | -0.0024032 | 0.0045351 | -0.015716 | 0.09613 | 0.12817 | 0.073242 | 0.073242 | 0.26093 | -0.073242 | -0.24261 | 0.10071 | 0.12817 | 0.018311 | 0.16479 | 0.13733 | -0.14648 | -0.20142 | 122.8271 | 122.6578 | 0.045776 | 123.0286 | 122.9736 | 0.31586 | -0.11902 | 122.7539 | 122.699 | -0.050354 | 123.0011 | 122.9187 | 0.21973 | -0.07782 | 123.1613 | 122.9965 | 122.9736 | -0.45776 | 123.0652 | 123.0377 | 123.0286 | -0.41657
4754.6875 | 123.0881 | -122.8775 | 0.21057 | 0.13672 | 0.033646 | 0.006366 | 0.0083227 | -0.007543 | -0.0014164 | -0.0090791 | 0.11726 | -0.014905 | -0.00668 | -0.0034714 | 0.0056033 | -0.016784 | 0.10529 | 0.11444 | 0.064087 | 0.050354 | 0.25177 | -0.086975 | -0.24261 | 0.10986 | 0.1236 | 0.036621 | 0.16937 | 0.12817 | -0.16022 | -0.19226 | 122.7905 | 122.6349 | 0.041199 | 122.9919 | 122.9279 | 0.29297 | -0.10529 | 122.7173 | 122.6852 | -0.041198 | 122.9874 | 122.9141 | 0.22888 | -0.082397 | 123.1293 | 122.9828 | 122.9416 | -0.45319 | 123.0469 | 123.0057 | 123.0011 | -0.40283
4756.4062 | 123.1201 | -122.8821 | 0.22888 | 0.1062 | 0.035568 | 0.0057252 | 0.0081091 | -0.007543 | 0.0043514 | -0.0080109 | 0.063858 | -0.011914 | -0.009457 | -0.00090781 | 0.0081667 | -0.019134 | 0.013733 | -0.086975 | -0.086975 | -0.054932 | 0.27924 | -0.10071 | -0.28381 | -0.013733 | -0.013733 | -0.13733 | 0.17395 | 0.16022 | -0.20599 | -0.25635 | 122.7814 | 122.5983 | 0.050354 | 122.7951 | 122.8271 | 0.22888 | -0.21515 | 122.6761 | 122.6257 | -0.054932 | 122.8683 | 122.7448 | 0.11902 | -0.068665 | 123.1613 | 122.8958 | 122.7951 | -0.5127 | 123.056 | 123.0423 | 122.8683 | -0.48523
4758.0938 | 123.1018 | -122.8958 | 0.21057 | -0.069275 | 0.038132 | 0.008075 | 0.0096045 | -0.011388 | 0.0028562 | -0.0058747 | -0.081101 | -0.011487 | -0.0053982 | -0.0021896 | 0.0068851 | -0.017852 | 0.11444 | 0.059509 | -0.009155 | 0.041199 | 0.31586 | -0.068665 | -0.22888 | 0.009155 | 0.032043 | -0.09613 | 0.21973 | 0.15564 | -0.1831 | -0.2243 | 122.8271 | 122.6669 | 0.10529 | 122.9553 | 122.937 | 0.27008 | -0.09613 | 122.7127 | 122.6715 | 0.009156 | 122.905 | 122.7997 | 0.12817 | -0.054931 | 123.2117 | 123.0103 | 122.8867 | -0.43945 | 123.1155 | 123.0515 | 122.9279 | -0.43488
4759.7812 | 123.2346 | -122.8363 | 0.17853 | -0.26001 | 0.031296 | 0.0057252 | 0.0091773 | -0.011388 | -0.00098918 | -0.011429 | -0.20317 | -0.012127 | -0.0043302 | -0.0015488 | 0.0034671 | -0.01828 | 0.09613 | 0.11444 | 0.059509 | 0.11444 | 0.4303 | -0.009155 | -0.17853 | 0.054932 | 0.1236 | -0.027466 | 0.30212 | 0.27008 | -0.12817 | -0.16479 | 122.8271 | 122.6578 | 0.25177 | 122.9507 | 122.9507 | 0.29297 | -0.082398 | 122.7081 | 122.6715 | 0.1236 | 122.8912 | 122.8088 | 0.13733 | 0.091553 | 123.2666 | 122.9324 | 122.8958 | -0.35706 | 123.1384 | 123.1064 | 122.9599 | -0.34332
4761.4844 | 123.2162 | -122.8683 | 0.19226 | -0.24475 | 0.033859 | 0.0048706 | 0.0111 | -0.0094656 | -0.002698 | -0.0084381 | -0.23369 | -0.013196 | -0.0043302 | -0.0024032 | 0.0043215 | -0.015716 | 0.11444 | 0.13733 | 0.064087 | 0.1236 | 0.43488 | 0.018311 | -0.14648 | 0.064087 | 0.1236 | -0.004578 | 0.31128 | 0.27008 | -0.12817 | -0.16022 | 122.8867 | 122.7219 | 0.24261 | 123.0057 | 122.9919 | 0.27008 | -0.07782 | 122.7402 | 122.7081 | 0.11902 | 122.9324 | 122.8638 | 0.15564 | 0.07782 | 123.3032 | 122.9828 | 122.9324 | -0.33874 | 123.1796 | 123.1384 | 122.9919 | -0.35248
4763.1719 | 123.1705 | -122.85 | 0.21057 | -0.19135 | 0.0345 | 0.0052978 | 0.0098181 | -0.0090384 | -0.0041934 | -0.0080109 | -0.20317 | -0.013836 | -0.0058254 | -0.0024032 | 0.00026273 | -0.016571 | 0.16022 | 0.24719 | 0.17395 | 0.17853 | 0.37537 | 0.013733 | -0.12817 | 0.11444 | 0.21057 | 0.068665 | 0.29755 | 0.27008 | -0.07782 | -0.11444 | 122.8638 | 122.7219 | 0.16479 | 123.0972 | 123.0286 | 0.3067 | -0.050354 | 122.7722 | 122.7356 | 0.086975 | 122.9645 | 122.9187 | 0.18311 | 0.05951 | 123.2254 | 123.0103 | 123.024 | -0.33875 | 123.1476 | 123.1201 | 123.0606 | -0.32501
4764.8594 | 123.0972 | -122.9004 | 0.19226 | 0.16724 | 0.032364 | 0.0052978 | 0.0057593 | -0.012243 | -0.0029118 | -0.0099335 | 0.17067 | -0.014905 | -0.0071072 | -0.0032578 | 0.0053897 | -0.017212 | 0.068665 | 0.1236 | 0.054932 | 0.041199 | 0.21515 | -0.07782 | -0.24719 | 0.09613 | 0.13733 | 0.041199 | 0.16479 | 0.1236 | -0.17395 | -0.19684 | 122.8226 | 122.6532 | 0.022888 | 123.024 | 122.9416 | 0.28839 | -0.1236 | 122.7264 | 122.7036 | -0.027466 | 122.9965 | 122.9416 | 0.23804 | -0.068665 | 123.1155 | 122.9691 | 122.9553 | -0.43945 | 123.0652 | 123.024 | 123.0377 | -0.3891
4766.5625 | 123.1842 | -122.8455 | 0.20599 | -0.16846 | 0.033218 | 0.0055114 | 0.0098181 | -0.010106 | -0.003339 | -0.0080109 | -0.13451 | -0.014691 | -0.0056118 | -0.0030442 | -0.00016447 | -0.016143 | 0.17395 | 0.25635 | 0.1831 | 0.1831 | 0.36163 | 0.032043 | -0.13733 | 0.15564 | 0.25177 | 0.10986 | 0.25635 | 0.21515 | -0.091553 | -0.1236 | 122.8775 | 122.7081 | 0.15564 | 123.1018 | 123.0286 | 0.32043 | -0.032044 | 122.7539 | 122.7219 | 0.050354 | 123.0011 | 122.9553 | 0.23346 | 0.009155 | 123.2071 | 123.0194 | 123.0286 | -0.34332 | 123.1018 | 123.0606 | 123.0972 | -0.32959
4768.25 | 123.2162 | -122.8546 | 0.17395 | -0.13794 | 0.028092 | 0.0061524 | 0.010245 | -0.0081838 | -0.0056888 | -0.0092927 | -0.11162 | -0.015118 | -0.0086026 | -0.003685 | 0.00026273 | -0.017425 | 0.17395 | 0.26093 | 0.1831 | 0.17853 | 0.35248 | 0.013733 | -0.13275 | 0.20142 | 0.27008 | 0.15564 | 0.27924 | 0.21515 | -0.068665 | -0.13733 | 122.8683 | 122.7219 | 0.17853 | 123.1155 | 123.0331 | 0.31128 | 0 | 122.7859 | 122.7173 | 0.10529 | 123.056 | 123.0103 | 0.29297 | 0.041199 | 123.2071 | 123.0286 | 123.0377 | -0.3067 | 123.1338 | 123.0698 | 123.1247 | -0.31128
4769.9531 | 123.0972 | -122.8912 | 0.23346 | -0.038757 | 0.035568 | 0.0048706 | 0.0053321 | -0.010106 | 0.0024288 | -0.0073701 | -0.096359 | -0.0091367 | -0.0071072 | 0.00016019 | 0.010517 | -0.018493 | 0.091553 | 0.054932 | -0.022888 | 0.022888 | 0.32044 | -0.09613 | -0.25635 | 0.004578 | 0.004578 | -0.1236 | 0.20142 | 0.17395 | -0.19684 | -0.23346 | 122.7951 | 122.6349 | 0.086976 | 122.9462 | 122.9141 | 0.27924 | -0.14191 | 122.6944 | 122.6578 | -0.032043 | 122.8958 | 122.7676 | 0.10986 | -0.059509 | 123.2117 | 122.9828 | 122.8683 | -0.48981 | 123.0927 | 123.0652 | 122.8958 | -0.46692
4771.6719 | 123.1247 | -122.8912 | 0.21057 | 0.15198 | 0.034287 | 0.007434 | 0.0059729 | -0.011388 | -0.00077538 | -0.0063019 | 0.17067 | -0.010846 | -0.010312 | -0.0011216 | 0.0083805 | -0.016998 | 0.10071 | 0.10529 | 0.032043 | 0.059509 | 0.23346 | -0.091553 | -0.22888 | 0.082397 | 0.10986 | 0.004578 | 0.13275 | 0.10986 | -0.1831 | -0.21973 | 122.7997 | 122.6624 | 0.022888 | 122.9965 | 122.9507 | 0.28839 | -0.10986 | 122.7081 | 122.6715 | -0.07782 | 122.9736 | 122.8958 | 0.22431 | -0.10071 | 123.1247 | 122.9919 | 122.9233 | -0.43945 | 123.024 | 123.0011 | 123.0011 | -0.4303
4773.375 | 123.0789 | -122.8958 | 0.20142 | 0.1062 | 0.032791 | 0.0057252 | 0.0066137 | -0.01032 | -0.0039798 | -0.0082245 | 0.14778 | -0.014264 | -0.006039 | -0.0030442 | 0.0049625 | -0.016571 | 0.086975 | 0.1236 | 0.064087 | 0.064087 | 0.23804 | -0.064087 | -0.22888 | 0.11902 | 0.14648 | 0.050354 | 0.18768 | 0.16479 | -0.13733 | -0.19684 | 122.8317 | 122.6669 | 0.036621 | 123.0194 | 122.9599 | 0.29297 | -0.11444 | 122.7585 | 122.699 | -0.013733 | 123.0148 | 122.9462 | 0.24719 | -0.036621 | 123.1339 | 122.9828 | 122.9599 | -0.4303 | 123.0835 | 123.0606 | 123.0423 | -0.39825
4775.0938 | 123.1018 | -122.9141 | 0.19684 | 0.19012 | 0.032791 | 0.0065796 | 0.0078955 | -0.0094656 | -0.002698 | -0.0080109 | 0.1783 | -0.013196 | -0.0056118 | -0.0043258 | 0.0060305 | -0.016998 | 0.073242 | 0.09613 | 0.041199 | 0.036621 | 0.2243 | -0.082397 | -0.24719 | 0.10986 | 0.14191 | 0.045776 | 0.14648 | 0.10986 | -0.16937 | -0.21515 | 122.8317 | 122.6669 | 0.027466 | 123.0103 | 122.9507 | 0.28381 | -0.1236 | 122.7448 | 122.699 | -0.050354 | 123.024 | 122.9599 | 0.26093 | -0.086975 | 123.1384 | 122.9874 | 122.9553 | -0.44403 | 123.0606 | 123.024 | 123.056 | -0.41199
4776.7812 | 123.0881 | -122.9141 | 0.21973 | 0.15198 | 0.031723 | 0.004657 | 0.0055457 | -0.009252 | -0.0024844 | -0.0095063 | 0.11726 | -0.012982 | -0.01138 | -0.0043258 | 0.0066715 | -0.017212 | 0.091553 | 0.10986 | 0.054932 | 0.050354 | 0.21515 | -0.082397 | -0.26093 | 0.11902 | 0.14191 | 0.041199 | 0.16937 | 0.14191 | -0.14648 | -0.20599 | 122.8317 | 122.6532 | -0.004578 | 123.024 | 122.9645 | 0.31128 | -0.12817 | 122.7676 | 122.7081 | -0.050354 | 123.0331 | 122.9553 | 0.24719 | -0.07782 | 123.1293 | 123.0057 | 122.9691 | -0.48065 | 123.0835 | 123.056 | 123.056 | -0.42572
4778.5312 | 123.1934 | -122.8638 | 0.19684 | -0.00061023 | 0.030228 | 0.007434 | 0.0091773 | -0.0098928 | -0.0046206 | -0.010788 | 0.056228 | -0.013623 | -0.0075344 | -0.0034714 | 0.0023989 | -0.017639 | 0.11444 | 0.1236 | 0.091553 | 0.10529 | 0.32959 | 0 | -0.17853 | 0.12817 | 0.16937 | 0.07782 | 0.23346 | 0.21515 | -0.10529 | -0.14648 | 122.8638 | 122.6852 | 0.13275 | 122.9874 | 122.9691 | 0.28381 | -0.082397 | 122.7585 | 122.7173 | 0.036621 | 122.9919 | 122.9416 | 0.2243 | 0.018311 | 123.1934 | 122.9782 | 122.9553 | -0.37537 | 123.0972 | 123.0789 | 123.0331 | -0.34332
4780.2188 | 123.0927 | -122.9187 | 0.21515 | 0.15961 | 0.032791 | 0.0061524 | 0.0068273 | -0.010106 | -0.00056178 | -0.011856 | 0.102 | -0.014691 | -0.0088162 | -0.0038986 | 0.0038943 | -0.017852 | 0.11444 | 0.10986 | 0.07782 | 0.059509 | 0.2655 | -0.050354 | -0.21057 | 0.1236 | 0.15106 | 0.041199 | 0.21515 | 0.1831 | -0.13275 | -0.16479 | 122.8683 | 122.7081 | 0.050354 | 123.0286 | 122.9782 | 0.27008 | -0.10071 | 122.7859 | 122.7539 | 0 | 123.0423 | 122.9599 | 0.20599 | -0.032044 | 123.1842 | 123.0331 | 122.9965 | -0.42572 | 123.1338 | 123.1018 | 123.0698 | -0.37994
4781.9688 | 123.1796 | -122.85 | 0.20599 | -0.069275 | 0.0345 | 0.0070068 | 0.0089635 | -0.0088248 | 0.0037106 | -0.0067291 | -0.18791 | -0.011273 | -0.0079618 | -0.0021896 | 0.0085941 | -0.021911 | 0.16479 | 0.091553 | 0.004578 | 0.064087 | 0.32044 | -0.068665 | -0.23346 | 0.082397 | 0.086975 | -0.068665 | 0.21973 | 0.19684 | -0.16022 | -0.21057 | 122.7814 | 122.6166 | 0.11444 | 122.9416 | 122.9141 | 0.29755 | -0.041199 | 122.6898 | 122.6395 | 0.013733 | 122.9324 | 122.7814 | 0.14191 | -0.009156 | 123.1705 | 123.0148 | 122.8546 | -0.43945 | 123.0698 | 123.0469 | 122.937 | -0.41657
4783.7031 | 123.1064 | -122.9141 | 0.21057 | 0.14435 | 0.028305 | 0.0061524 | 0.0074683 | -0.010961 | -0.0048344 | -0.010788 | 0.10963 | -0.01405 | -0.0075344 | -0.00090781 | 0.0030399 | -0.017212 | 0.091553 | 0.10986 | 0.064087 | 0.068665 | 0.26093 | -0.059509 | -0.21973 | 0.10986 | 0.13733 | 0.032043 | 0.20599 | 0.19226 | -0.11902 | -0.17395 | 122.8546 | 122.6944 | 0.050354 | 123.024 | 122.9828 | 0.28839 | -0.11902 | 122.7951 | 122.7402 | -0.004577 | 123.024 | 122.9462 | 0.20599 | -0.01831 | 123.175 | 123.0057 | 122.9782 | -0.4303 | 123.1201 | 123.1064 | 123.0515 | -0.38452
4785.3906 | 123.1476 | -122.8592 | 0.19684 | 0.13672 | 0.0345 | 0.0057252 | 0.0055457 | -0.009252 | 0.0015744 | -0.0097199 | 0.12489 | -0.012341 | -0.0058254 | -0.0034714 | 0.0068851 | -0.018707 | 0.10071 | 0.07782 | 0.022888 | 0.041199 | 0.23804 | -0.091553 | -0.2655 | 0.10071 | 0.1236 | -0.009155 | 0.14648 | 0.14191 | -0.17395 | -0.20599 | 122.7676 | 122.5937 | 0.041199 | 122.937 | 122.9004 | 0.3067 | -0.09613 | 122.6852 | 122.6532 | -0.050354 | 122.9599 | 122.85 | 0.19684 | -0.054931 | 123.0972 | 122.9599 | 122.8821 | -0.46234 | 123.0057 | 123.0011 | 122.9828 | -0.40283
4787.1094 | 123.1476 | -122.8455 | 0.21515 | 0.11383 | 0.036423 | 0.0072204 | 0.0051183 | -0.008611 | 0.00050622 | -0.0077973 | 0.16304 | -0.011059 | -0.0079618 | -0.001976 | 0.0073123 | -0.017425 | 0.032043 | -0.004578 | -0.064087 | -0.027466 | 0.2655 | -0.10529 | -0.28381 | 0.041199 | 0.045776 | -0.064087 | 0.19226 | 0.13733 | -0.1831 | -0.23804 | 122.7402 | 122.5616 | 0.050354 | 122.8409 | 122.818 | 0.25635 | -0.18311 | 122.6624 | 122.6074 | -0.022888 | 122.8867 | 122.7814 | 0.17395 | -0.07782 | 123.111 | 122.8775 | 122.7814 | -0.49896 | 123.0377 | 122.9828 | 122.8912 | -0.45319
4788.7969 | 123.1567 | -122.8912 | 0.21057 | 0.12909 | 0.03685 | 0.0059388 | 0.010459 | -0.010106 | 0.0024288 | -0.0080109 | 0.04097 | -0.0117 | -0.0075344 | -0.0030442 | 0.0085941 | -0.016784 | 0.036621 | -0.041199 | -0.07782 | -0.032043 | 0.27008 | -0.13275 | -0.29755 | 0.013733 | 0.013733 | -0.09613 | 0.19226 | 0.17395 | -0.20599 | -0.23346 | 122.7585 | 122.5937 | 0.05951 | 122.85 | 122.8592 | 0.2655 | -0.17395 | 122.6852 | 122.6578 | -0.01831 | 122.905 | 122.7951 | 0.13733 | -0.036621 | 123.1613 | 122.9279 | 122.8134 | -0.50812 | 123.0835 | 123.0652 | 122.905 | -0.44403
4790.5 | 123.1888 | -122.85 | 0.19684 | -0.23712 | 0.033859 | 0.0065796 | 0.013236 | -0.010747 | -0.0014164 | -0.0086517 | -0.16502 | -0.014477 | -0.0056118 | -0.0030442 | 0.0019717 | -0.016784 | 0.14648 | 0.16022 | 0.11444 | 0.12817 | 0.40741 | 0.027466 | -0.15106 | 0.068665 | 0.14191 | 0.009155 | 0.31128 | 0.2655 | -0.11902 | -0.16022 | 122.8775 | 122.699 | 0.21057 | 123.0103 | 122.9782 | 0.27924 | -0.050354 | 122.731 | 122.6898 | 0.11444 | 122.9187 | 122.8592 | 0.16937 | 0.068665 | 123.2574 | 122.9965 | 122.9645 | -0.3479 | 123.1613 | 123.1155 | 122.9919 | -0.35706
4792.2031 | 123.1613 | -122.8867 | 0.2243 | 0.12146 | 0.0345 | 0.0050842 | 0.0074683 | -0.0094656 | 0.0011472 | -0.0069427 | 0.14778 | -0.012768 | -0.0086026 | -0.00048061 | 0.0068851 | -0.020202 | 0.032043 | -0.009155 | -0.064087 | -0.032043 | 0.2655 | -0.14191 | -0.28839 | 0.045776 | 0.050354 | -0.050354 | 0.16022 | 0.14191 | -0.18768 | -0.24261 | 122.7448 | 122.5983 | 0.041199 | 122.8775 | 122.8546 | 0.25635 | -0.19226 | 122.699 | 122.644 | -0.064087 | 122.9324 | 122.8363 | 0.19226 | -0.082397 | 123.1522 | 122.9187 | 122.8226 | -0.5127 | 123.0469 | 123.0286 | 122.937 | -0.46692
4793.9375 | 123.2529 | -122.85 | 0.19226 | -0.17609 | 0.035996 | 0.0057252 | 0.0087499 | -0.010961 | 0.00071982 | -0.0095063 | -0.25658 | -0.012768 | -0.00668 | -0.0021896 | 0.0058169 | -0.018493 | 0.11902 | 0.11902 | 0.059509 | 0.10986 | 0.41657 | -0.009155 | -0.16937 | 0.045776 | 0.14191 | -0.027466 | 0.2655 | 0.23346 | -0.14191 | -0.18768 | 122.8409 | 122.6807 | 0.2243 | 122.9691 | 122.9599 | 0.27924 | -0.073242 | 122.7081 | 122.6624 | 0.073242 | 122.8958 | 122.8226 | 0.16022 | 0.041198 | 123.2666 | 122.9691 | 122.9095 | -0.36163 | 123.1155 | 123.0835 | 122.9919 | -0.37994
4795.625 | 123.23 | -122.85 | 0.18768 | -0.17609 | 0.036636 | 0.0067932 | 0.013023 | -0.010747 | 0.00050622 | -0.0080109 | -0.17265 | -0.011914 | -0.0051846 | -0.0026168 | 0.0043215 | -0.018493 | 0.10071 | 0.11444 | 0.054932 | 0.10071 | 0.37537 | -0.032043 | -0.20599 | 0.073242 | 0.12817 | -0.032043 | 0.25177 | 0.21515 | -0.15106 | -0.19684 | 122.818 | 122.644 | 0.18768 | 122.9645 | 122.9507 | 0.3067 | -0.086975 | 122.699 | 122.6532 | 0.064087 | 122.9233 | 122.818 | 0.1648 | 0.027466 | 123.2254 | 122.9507 | 122.905 | -0.39368 | 123.1018 | 123.0652 | 122.9782 | -0.38452
4797.3438 | 123.2025 | -122.8546 | 0.18768 | -0.18372 | 0.034927 | 0.0076478 | 0.012382 | -0.010961 | -0.00163 | -0.0095063 | -0.23369 | -0.014691 | -0.0053982 | -0.0017624 | 0.0021853 | -0.016571 | 0.086975 | 0.15106 | 0.068665 | 0.10071 | 0.41199 | 0.013733 | -0.15564 | 0.059509 | 0.14648 | 0.004578 | 0.31128 | 0.27924 | -0.10529 | -0.13733 | 122.8683 | 122.699 | 0.2243 | 123.0057 | 122.9553 | 0.25635 | -0.10071 | 122.7493 | 122.7173 | 0.1236 | 122.9141 | 122.8592 | 0.14191 | 0.091553 | 123.2666 | 122.9416 | 122.9233 | -0.34332 | 123.1659 | 123.1338 | 123.0011 | -0.32501
4799.0312 | 123.2254 | -122.8271 | 0.19226 | -0.015869 | 0.031296 | 0.0061524 | 0.010886 | -0.0083974 | -0.0059024 | -0.011429 | 0.04097 | -0.01405 | -0.006039 | -0.0021896 | 0.00068993 | -0.015075 | 0.082397 | 0.14191 | 0.13275 | 0.1236 | 0.31128 | -0.013733 | -0.17853 | 0.13733 | 0.2243 | 0.10071 | 0.26093 | 0.22888 | -0.10071 | -0.14648 | 122.8134 | 122.6486 | 0.11902 | 122.9691 | 122.9507 | 0.30212 | -0.10986 | 122.7264 | 122.6807 | 0.068664 | 122.9645 | 122.9279 | 0.24719 | 0.036621 | 123.1384 | 122.9095 | 122.9599 | -0.37079 | 123.0881 | 123.056 | 123.0515 | -0.33874
4800.7188 | 123.1796 | -122.8775 | 0.19226 | 0.014648 | 0.031296 | 0.0052978 | 0.0074683 | -0.012243 | -0.0054752 | -0.012497 | 0.10963 | -0.015332 | -0.0075344 | -0.0026168 | 0.0011173 | -0.014862 | 0.091553 | 0.1236 | 0.10529 | 0.10071 | 0.32959 | -0.027466 | -0.1831 | 0.09613 | 0.17395 | 0.082397 | 0.24261 | 0.20142 | -0.10986 | -0.16479 | 122.85 | 122.6944 | 0.13733 | 123.0011 | 122.9782 | 0.28381 | -0.10071 | 122.7676 | 122.7127 | 0.050354 | 122.9736 | 122.9599 | 0.24719 | 0.009155 | 123.2071 | 122.9691 | 122.9828 | -0.37537 | 123.1201 | 123.0789 | 123.0515 | -0.35706
4802.4062 | 123.1888 | -122.8592 | 0.17395 | -0.1532 | 0.033646 | 0.0078614 | 0.012382 | -0.0083974 | -0.00098918 | -0.0088653 | -0.18028 | -0.01405 | -0.0058254 | -0.0013352 | 0.0023989 | -0.020843 | 0.1831 | 0.23804 | 0.17395 | 0.19684 | 0.36621 | 0.041199 | -0.1236 | 0.16937 | 0.27008 | 0.11444 | 0.2655 | 0.24261 | -0.07782 | -0.13275 | 122.9004 | 122.7356 | 0.19226 | 123.0972 | 123.056 | 0.32043 | 0.009155 | 122.7814 | 122.7264 | 0.091553 | 123.0286 | 122.9736 | 0.24719 | 0.068665 | 123.2254 | 123.0423 | 123.0331 | -0.29755 | 123.1247 | 123.1018 | 123.1293 | -0.3067
4804.125 | 123.1384 | -122.8546 | 0.21515 | 0.19775 | 0.035141 | 0.006366 | 0.0049047 | -0.0073294 | 0.001788 | -0.0088653 | 0.12489 | -0.013623 | -0.0073208 | -0.0026168 | 0.0075259 | -0.018493 | 0.045776 | 0.009155 | -0.041199 | -0.032043 | 0.25635 | -0.13275 | -0.28839 | 0.07782 | 0.07782 | -0.027466 | 0.17853 | 0.16022 | -0.16022 | -0.21057 | 122.7219 | 122.5662 | 0.041199 | 122.8638 | 122.8226 | 0.25635 | -0.16937 | 122.6944 | 122.644 | -0.036621 | 122.9324 | 122.8271 | 0.18311 | -0.054932 | 123.111 | 122.9004 | 122.8134 | -0.50354 | 123.0331 | 123.0148 | 122.9324 | -0.42572
4805.8125 | 123.1384 | -122.8729 | 0.21973 | 0.090942 | 0.037064 | 0.0052978 | 0.0061865 | -0.010106 | 0.0039242 | -0.0077973 | 0.056228 | -0.012341 | -0.0053982 | -0.0021896 | 0.0085941 | -0.01593 | 0.013733 | -0.013733 | -0.07782 | -0.027466 | 0.27466 | -0.13275 | -0.28381 | 0.032043 | 0.013733 | -0.09613 | 0.19226 | 0.16937 | -0.19226 | -0.22888 | 122.7402 | 122.5891 | 0.054931 | 122.8592 | 122.8455 | 0.25635 | -0.20599 | 122.6807 | 122.644 | -0.027466 | 122.905 | 122.7768 | 0.13275 | -0.050354 | 123.1476 | 122.8867 | 122.7951 | -0.50354 | 123.0652 | 123.0423 | 122.8867 | -0.44861
4807.5469 | 123.1796 | -122.85 | 0.19226 | -0.18372 | 0.03215 | 0.0078614 | 0.0098181 | -0.0077566 | -0.005048 | -0.01207 | -0.14977 | -0.015545 | -0.0073208 | -0.0041122 | 0.0038943 | -0.019561 | 0.17853 | 0.26093 | 0.1831 | 0.17395 | 0.38452 | 0.041199 | -0.14191 | 0.15564 | 0.26093 | 0.09613 | 0.27008 | 0.23346 | -0.09613 | -0.1236 | 122.8912 | 122.7081 | 0.19226 | 123.111 | 123.024 | 0.31586 | -0.013733 | 122.7539 | 122.7264 | 0.07782 | 123.0057 | 122.9462 | 0.21973 | 0.041198 | 123.2346 | 123.0286 | 123.0331 | -0.33417 | 123.1201 | 123.0835 | 123.111 | -0.31586
4809.2344 | 123.1979 | -122.8638 | 0.17853 | -0.16846 | 0.032578 | 0.0076478 | 0.0087499 | -0.0073294 | -0.0054752 | -0.0099335 | -0.16502 | -0.015118 | -0.007748 | -0.0011216 | 0.0036807 | -0.016143 | 0.20599 | 0.28381 | 0.19226 | 0.19226 | 0.37994 | 0.041199 | -0.13275 | 0.19684 | 0.28839 | 0.14648 | 0.27008 | 0.23346 | -0.082397 | -0.11444 | 122.905 | 122.731 | 0.20142 | 123.1476 | 123.056 | 0.32501 | 0.027466 | 122.7814 | 122.7493 | 0.091553 | 123.0606 | 123.0103 | 0.26093 | 0.054931 | 123.2437 | 123.0698 | 123.056 | -0.31128 | 123.1339 | 123.0972 | 123.1522 | -0.29297
4810.9688 | 123.1888 | -122.8592 | 0.19226 | -0.17609 | 0.030869 | 0.0033752 | 0.0098181 | -0.0098928 | -0.0012028 | -0.010574 | -0.18791 | -0.014264 | -0.0058254 | -0.0041122 | 0.00090353 | -0.018921 | 0.20599 | 0.21515 | 0.17853 | 0.16937 | 0.36163 | 0.018311 | -0.14648 | 0.16022 | 0.24261 | 0.10529 | 0.28381 | 0.25177 | -0.073242 | -0.10986 | 122.8775 | 122.7127 | 0.16937 | 123.0743 | 123.0286 | 0.31586 | 0.013733 | 122.7859 | 122.7493 | 0.091552 | 123.0194 | 122.9645 | 0.21515 | 0.059509 | 123.2208 | 123.0652 | 123.0377 | -0.33874 | 123.143 | 123.111 | 123.1018 | -0.30212
4812.6562 | 123.1888 | -122.8729 | 0.20599 | -0.25238 | 0.031723 | 0.0072204 | 0.0098181 | -0.008611 | -0.00098918 | -0.0084381 | -0.20317 | -0.014477 | -0.0034756 | -0.0034714 | 0.0041079 | -0.018066 | 0.14648 | 0.15106 | 0.07782 | 0.10986 | 0.41657 | 0.018311 | -0.15106 | 0.082397 | 0.14648 | 0.009155 | 0.31586 | 0.26093 | -0.12817 | -0.16022 | 122.8912 | 122.7219 | 0.21057 | 123.024 | 122.9828 | 0.26093 | -0.05951 | 122.7448 | 122.7127 | 0.10986 | 122.9553 | 122.8821 | 0.16937 | 0.054931 | 123.2895 | 123.0194 | 122.9507 | -0.35706 | 123.1888 | 123.1338 | 123.0194 | -0.36621
4814.3438 | 123.2391 | -122.8546 | 0.18768 | -0.25238 | 0.033859 | 0.006366 | 0.010673 | -0.008611 | 0.0011472 | -0.010788 | -0.26421 | -0.010846 | -0.004971 | -0.0017624 | 0.0038943 | -0.019561 | 0.1236 | 0.13275 | 0.045776 | 0.10071 | 0.42572 | 0.009155 | -0.15564 | 0.068665 | 0.12817 | -0.004578 | 0.29755 | 0.25635 | -0.11902 | -0.18768 | 122.8638 | 122.699 | 0.23804 | 122.9874 | 122.9553 | 0.25635 | -0.064087 | 122.7356 | 122.6669 | 0.10986 | 122.9233 | 122.85 | 0.1831 | 0.068665 | 123.2803 | 122.9782 | 122.9004 | -0.34332 | 123.1522 | 123.111 | 122.9828 | -0.37537
4816.0312 | 123.1796 | -122.8455 | 0.19226 | -0.2066 | 0.030655 | 0.0070068 | 0.0089635 | -0.0073294 | -0.00163 | -0.010147 | -0.19554 | -0.01405 | -0.0051846 | -0.0026168 | 0.0038943 | -0.019561 | 0.16937 | 0.27008 | 0.16937 | 0.17853 | 0.36621 | 0.036621 | -0.13275 | 0.16937 | 0.26093 | 0.10529 | 0.24719 | 0.21973 | -0.07782 | -0.13733 | 122.8821 | 122.7127 | 0.17395 | 123.1155 | 123.024 | 0.31128 | -0.022888 | 122.7676 | 122.7081 | 0.054931 | 123.0148 | 122.9507 | 0.24262 | 0.027466 | 123.2117 | 123.0148 | 123.0148 | -0.32501 | 123.0927 | 123.0652 | 123.1064 | -0.32959
4817.7188 | 123.2391 | -122.85 | 0.17395 | -0.046387 | 0.033859 | 0.007434 | 0.0083227 | -0.0090384 | -0.004407 | -0.0092927 | -0.08873 | -0.015545 | -0.0086026 | -0.0013352 | 0.0030399 | -0.015289 | 0.15106 | 0.21973 | 0.16479 | 0.14191 | 0.35248 | 0.032043 | -0.13733 | 0.21057 | 0.2655 | 0.16022 | 0.27466 | 0.21515 | -0.086975 | -0.10986 | 122.8821 | 122.7127 | 0.17853 | 123.0698 | 122.9919 | 0.27924 | -0.022888 | 122.7631 | 122.7402 | 0.10071 | 123.0606 | 123.0103 | 0.27008 | 0.041199 | 123.2025 | 123.0011 | 123.0148 | -0.31128 | 123.1247 | 123.0652 | 123.1155 | -0.28381
4819.4062 | 123.175 | -122.8271 | 0.19684 | -0.25238 | 0.033218 | 0.0072204 | 0.0089635 | -0.0066884 | -0.00077538 | -0.011642 | -0.24895 | -0.013623 | -0.006039 | -0.0013352 | 0.0051761 | -0.018921 | 0.16937 | 0.19226 | 0.11444 | 0.14648 | 0.40741 | 0.018311 | -0.16022 | 0.086975 | 0.16022 | 0.009155 | 0.31586 | 0.26093 | -0.10529 | -0.16022 | 122.8455 | 122.6669 | 0.21057 | 123.0194 | 122.9736 | 0.3067 | -0.027465 | 122.7219 | 122.6669 | 0.11902 | 122.9141 | 122.8363 | 0.16937 | 0.064087 | 123.2346 | 122.9965 | 122.9416 | -0.35706 | 123.143 | 123.0881 | 122.9874 | -0.35706
4821.0938 | 123.0881 | -122.8775 | 0.21515 | 0.13672 | 0.03215 | 0.0042298 | 0.0057593 | -0.01032 | -0.00013458 | -0.0077973 | 0.11726 | -0.012555 | -0.0073208 | -0.0024032 | 0.0049625 | -0.016784 | 0.09613 | 0.12817 | 0.059509 | 0.045776 | 0.22888 | -0.082397 | -0.24261 | 0.1236 | 0.13733 | 0.041199 | 0.17395 | 0.14648 | -0.16479 | -0.20142 | 122.7951 | 122.6349 | 0.013733 | 123.0057 | 122.9233 | 0.28839 | -0.11902 | 122.7127 | 122.6761 | -0.041199 | 123.0011 | 122.9187 | 0.24262 | -0.068665 | 123.1064 | 122.9736 | 122.937 | -0.45776 | 123.0515 | 123.024 | 123.0148 | -0.41657
4822.7969 | 123.1018 | -122.8821 | 0.21973 | 0.15198 | 0.0345 | 0.0067932 | 0.0066137 | -0.0077566 | 0.001788 | -0.0080109 | 0.1783 | -0.013623 | -0.0081754 | -0.0032578 | 0.0079531 | -0.018707 | 0.09613 | 0.10071 | 0.036621 | 0.027466 | 0.21057 | -0.09613 | -0.26093 | 0.11444 | 0.14648 | 0.032043 | 0.15564 | 0.10986 | -0.19226 | -0.21515 | 122.7859 | 122.6212 | -0.009156 | 122.9828 | 122.9095 | 0.28839 | -0.1236 | 122.6898 | 122.6669 | -0.064087 | 122.9965 | 122.9141 | 0.24719 | -0.10986 | 123.0927 | 122.9782 | 122.9187 | -0.48065 | 123.0377 | 122.9919 | 123.0286 | -0.43488
4824.5156 | 123.0927 | -122.8775 | 0.23346 | 0.11383 | 0.033432 | 0.0055114 | 0.0081091 | -0.011602 | -0.0024844 | -0.011429 | 0.14015 | -0.011914 | -0.00668 | -0.0032578 | 0.0056033 | -0.017852 | 0.10071 | 0.13275 | 0.054932 | 0.054932 | 0.23804 | -0.073242 | -0.21057 | 0.1236 | 0.1236 | 0.032043 | 0.17853 | 0.15564 | -0.15564 | -0.19226 | 122.8043 | 122.6669 | 0.004578 | 123.0103 | 122.9324 | 0.2655 | -0.13275 | 122.7219 | 122.6852 | -0.054931 | 123.0011 | 122.9095 | 0.2243 | -0.077819 | 123.1155 | 122.9782 | 122.9324 | -0.44403 | 123.056 | 123.0331 | 123.0011 | -0.42572
4826.2031 | 123.1796 | -122.8363 | 0.17853 | 0.014648 | 0.030441 | 0.009143 | 0.010245 | -0.0094656 | -0.0041934 | -0.0095063 | 0.018082 | -0.013196 | -0.0088162 | -0.0043258 | 0.0019717 | -0.016571 | 0.09613 | 0.13275 | 0.10071 | 0.09613 | 0.32501 | -0.009155 | -0.1831 | 0.13275 | 0.16479 | 0.07782 | 0.23804 | 0.21515 | -0.10529 | -0.14191 | 122.8271 | 122.6532 | 0.14648 | 122.9691 | 122.9324 | 0.27924 | -0.082398 | 122.731 | 122.6944 | 0.059509 | 122.9691 | 122.9141 | 0.21973 | 0.036621 | 123.1613 | 122.9324 | 122.937 | -0.36163 | 123.0743 | 123.0515 | 123.0011 | -0.32044
4827.9375 | 123.1338 | -122.8729 | 0.21057 | 0.037537 | 0.030655 | 0.0072204 | 0.0081091 | -0.010534 | -0.0039798 | -0.011856 | 0.056228 | -0.0164 | -0.0079618 | -0.0024032 | 0.0045351 | -0.01593 | 0.10986 | 0.11444 | 0.082397 | 0.086975 | 0.3067 | -0.032043 | -0.17853 | 0.11902 | 0.14648 | 0.064087 | 0.23804 | 0.21973 | -0.10529 | -0.16479 | 122.8409 | 122.6944 | 0.096131 | 122.9874 | 122.9599 | 0.2655 | -0.10071 | 122.7676 | 122.7081 | 0.027466 | 122.9919 | 122.937 | 0.22888 | 0.009156 | 123.1796 | 122.9828 | 122.9553 | -0.3891 | 123.111 | 123.0927 | 123.0194 | -0.37537
4829.625 | 123.1476 | -122.8775 | 0.20142 | 0.19775 | 0.035568 | 0.006366 | 0.0059729 | -0.009252 | 0.00071982 | -0.0099335 | 0.079117 | -0.012127 | -0.007748 | -0.0041122 | 0.0064577 | -0.018921 | 0.09613 | 0.036621 | -0.004578 | 0.027466 | 0.25177 | -0.10071 | -0.2655 | 0.12817 | 0.11444 | 0.013733 | 0.16479 | 0.10986 | -0.16022 | -0.19226 | 122.7768 | 122.612 | 0.050354 | 122.9141 | 122.905 | 0.29297 | -0.10529 | 122.7173 | 122.6852 | -0.036621 | 123.0057 | 122.8912 | 0.20599 | -0.091553 | 123.1293 | 122.9736 | 122.8729 | -0.46692 | 123.0423 | 122.9874 | 122.9919 | -0.39368
4831.3281 | 123.1338 | -122.8912 | 0.20599 | 0.12146 | 0.036209 | 0.0042298 | 0.0066137 | -0.0077566 | -0.00098918 | -0.0082245 | 0.15541 | -0.013836 | -0.0081754 | -0.0026168 | 0.0053897 | -0.016998 | 0.10986 | 0.09613 | 0.041199 | 0.041199 | 0.23346 | -0.082397 | -0.25177 | 0.10986 | 0.11444 | 0 | 0.13275 | 0.11444 | -0.19226 | -0.24261 | 122.8088 | 122.6395 | 0.027465 | 122.9874 | 122.9324 | 0.29297 | -0.096131 | 122.699 | 122.6486 | -0.073243 | 123.0011 | 122.8912 | 0.24261 | -0.091553 | 123.1247 | 123.0011 | 122.9324 | -0.45776 | 123.024 | 123.0057 | 123.0057 | -0.44861
4833.0156 | 123.1201 | -122.8775 | 0.21515 | -0.084534 | 0.037277 | 0.0050842 | 0.010032 | -0.010534 | 0.0058468 | -0.0069427 | -0.14214 | -0.010846 | -0.00668 | -0.003685 | 0.0073123 | -0.018921 | 0.13733 | 0.10071 | 0 | 0.054932 | 0.31128 | -0.068665 | -0.22888 | 0.068665 | 0.064087 | -0.082397 | 0.21973 | 0.18768 | -0.1831 | -0.21515 | 122.8088 | 122.6486 | 0.09613 | 122.9782 | 122.9324 | 0.28381 | -0.07782 | 122.6944 | 122.6624 | 0.004578 | 122.9462 | 122.7951 | 0.13275 | -0.027466 | 123.1888 | 123.0148 | 122.8775 | -0.44403 | 123.0972 | 123.0652 | 122.9416 | -0.4303
4834.7031 | 123.2391 | -122.85 | 0.19226 | -0.16846 | 0.035782 | 0.007434 | 0.0089635 | -0.0073294 | 0.0032834 | -0.0095063 | -0.24895 | -0.015332 | -0.00668 | -0.001976 | 0.0083805 | -0.018066 | 0.10529 | 0.11444 | 0.050354 | 0.10529 | 0.37994 | -0.022888 | -0.17853 | 0.073242 | 0.13733 | -0.022888 | 0.28839 | 0.2243 | -0.14191 | -0.16479 | 122.8271 | 122.6715 | 0.18768 | 122.9645 | 122.9553 | 0.28381 | -0.086975 | 122.7081 | 122.6852 | 0.09613 | 122.9233 | 122.8271 | 0.14191 | 0.032043 | 123.23 | 122.9553 | 122.9004 | -0.37079 | 123.1384 | 123.0743 | 122.9874 | -0.35706
4836.4219 | 123.23 | -122.8134 | 0.17395 | -0.14557 | 0.033859 | 0.0048706 | 0.010459 | -0.010961 | -0.0059024 | -0.010574 | -0.10399 | -0.015759 | -0.0034756 | -0.0038986 | 0.0017581 | -0.01828 | 0.17395 | 0.26093 | 0.1831 | 0.16937 | 0.36163 | 0.027466 | -0.14191 | 0.20142 | 0.27008 | 0.15564 | 0.24719 | 0.2243 | -0.054932 | -0.13275 | 122.8409 | 122.6715 | 0.18768 | 123.0743 | 122.9828 | 0.31128 | 0 | 122.7585 | 122.6807 | 0.073242 | 123.0148 | 122.9691 | 0.28839 | 0.050354 | 123.175 | 122.9874 | 122.9965 | -0.31586 | 123.0606 | 123.0377 | 123.0835 | -0.3067
4838.1094 | 123.2254 | -122.8363 | 0.17853 | -0.084534 | 0.031937 | 0.0085022 | 0.0089635 | -0.008611 | -0.0052616 | -0.0084381 | -0.10399 | -0.015545 | -0.0051846 | -0.0038986 | 0.0013309 | -0.017212 | 0.14648 | 0.20599 | 0.16479 | 0.16022 | 0.35706 | 0.022888 | -0.15564 | 0.19226 | 0.2655 | 0.16022 | 0.2655 | 0.23346 | -0.068665 | -0.10529 | 122.8592 | 122.6807 | 0.17853 | 123.0423 | 122.9965 | 0.31586 | -0.032044 | 122.7676 | 122.731 | 0.086975 | 123.0286 | 122.9965 | 0.2655 | 0.054931 | 123.1934 | 122.9828 | 123.0011 | -0.33417 | 123.1018 | 123.0698 | 123.1018 | -0.28381
4839.7969 | 123.1888 | -122.8775 | 0.19226 | 0.029907 | 0.031296 | 0.0085022 | 0.0078955 | -0.0098928 | -0.003339 | -0.010788 | 0.056228 | -0.012127 | -0.0051846 | -0.0051804 | 0.0021853 | -0.017852 | 0.10529 | 0.13275 | 0.09613 | 0.10529 | 0.32959 | -0.013733 | -0.19226 | 0.11902 | 0.16937 | 0.091553 | 0.24261 | 0.21515 | -0.11444 | -0.15564 | 122.8638 | 122.6852 | 0.13733 | 123.0103 | 122.9828 | 0.29755 | -0.086975 | 122.7631 | 122.7219 | 0.050354 | 122.9965 | 122.9691 | 0.24719 | 0.022888 | 123.2071 | 122.9828 | 122.9736 | -0.38452 | 123.1201 | 123.0927 | 123.0469 | -0.3479
4841.4844 | 123.1567 | -122.8729 | 0.20142 | 0.045166 | 0.028946 | 0.009784 | 0.0068273 | -0.0079702 | -0.0029118 | -0.0095063 | 0.04097 | -0.01405 | -0.00668 | -0.0028306 | 0.0045351 | -0.018493 | 0.10986 | 0.11444 | 0.068665 | 0.086975 | 0.32959 | -0.027466 | -0.18768 | 0.10986 | 0.15106 | 0.073242 | 0.24261 | 0.20142 | -0.12817 | -0.16022 | 122.8455 | 122.6852 | 0.12817 | 122.9874 | 122.9599 | 0.27466 | -0.091553 | 122.7448 | 122.7127 | 0.041199 | 122.9828 | 122.9462 | 0.23346 | 0 | 123.2025 | 122.9828 | 122.9416 | -0.3891 | 123.1155 | 123.0743 | 123.024 | -0.36163
4843.1719 | 123.143 | -122.8638 | 0.21515 | 0.11383 | 0.035355 | 0.0087158 | 0.0051183 | -0.01032 | 0.0015744 | -0.0095063 | 0.14015 | -0.013836 | -0.0098844 | -0.0024032 | 0.0088077 | -0.019348 | 0.13733 | 0.09613 | 0.027466 | 0.059509 | 0.23804 | -0.073242 | -0.24719 | 0.10071 | 0.1236 | 0 | 0.14648 | 0.11902 | -0.17853 | -0.22888 | 122.7905 | 122.6166 | 0.022888 | 122.9599 | 122.9233 | 0.3067 | -0.07782 | 122.6852 | 122.6349 | -0.068665 | 122.9645 | 122.8638 | 0.22888 | -0.09613 | 123.1018 | 123.0011 | 122.8912 | -0.46234 | 123.0103 | 122.9828 | 122.9874 | -0.44403
4844.8594 | 123.1476 | -122.8546 | 0.21515 | 0.12146 | 0.037064 | 0.0065796 | 0.0072547 | -0.0081838 | 0.0041378 | -0.010147 | 0.04097 | -0.010418 | -0.0081754 | 0.0010148 | 0.0073123 | -0.017852 | 0.041199 | -0.050354 | -0.09613 | -0.036621 | 0.28839 | -0.11902 | -0.29755 | 0.018311 | 0 | -0.10986 | 0.19684 | 0.17853 | -0.20599 | -0.26093 | 122.7356 | 122.5571 | 0.073242 | 122.8043 | 122.818 | 0.26092 | -0.17395 | 122.6486 | 122.5937 | -0.018311 | 122.8729 | 122.7448 | 0.15106 | -0.036621 | 123.143 | 122.8958 | 122.7585 | -0.5127 | 123.0515 | 123.0331 | 122.8546 | -0.47607
4846.5469 | 123.1293 | -122.8638 | 0.21515 | 0.15961 | 0.035996 | 0.0078614 | 0.0068273 | -0.010534 | 0.0011472 | -0.0090791 | 0.11726 | -0.010632 | -0.0090298 | -0.0028306 | 0.010303 | -0.016143 | 0.10529 | 0.082397 | 0.027466 | 0.041199 | 0.21973 | -0.068665 | -0.25635 | 0.091553 | 0.10986 | 0.004578 | 0.14648 | 0.13275 | -0.17853 | -0.22888 | 122.7951 | 122.6074 | 0.004578 | 122.9462 | 122.905 | 0.29755 | -0.10986 | 122.6852 | 122.6349 | -0.068665 | 122.9553 | 122.8683 | 0.23346 | -0.082398 | 123.0835 | 122.9691 | 122.8912 | -0.4715 | 123.0103 | 122.9965 | 122.9736 | -0.44403
4848.2344 | 123.111 | -122.8958 | 0.21515 | 0.068054 | 0.030014 | 0.009143 | 0.0057593 | -0.0096792 | -0.0059024 | -0.0092927 | 0.063858 | -0.014691 | -0.0088162 | -0.003685 | 0.0023989 | -0.017212 | 0.09613 | 0.10071 | 0.07782 | 0.068665 | 0.29755 | -0.036621 | -0.19684 | 0.10986 | 0.16022 | 0.064087 | 0.21973 | 0.20142 | -0.10986 | -0.16937 | 122.8592 | 122.699 | 0.082397 | 122.9965 | 122.9645 | 0.2655 | -0.11902 | 122.7859 | 122.7264 | 0.004578 | 123.0057 | 122.9599 | 0.23346 | -0.013733 | 123.1934 | 122.9919 | 122.9736 | -0.41199 | 123.1155 | 123.0972 | 123.056 | -0.38452
4849.9844 | 123.1979 | -122.8455 | 0.20599 | -0.23712 | 0.035782 | 0.0059388 | 0.011741 | -0.0083974 | -0.00013458 | -0.0090791 | -0.27184 | -0.014477 | -0.0047574 | -0.0013352 | 0.0038943 | -0.018066 | 0.19684 | 0.1831 | 0.11902 | 0.16022 | 0.40741 | 0.036621 | -0.14191 | 0.12817 | 0.16937 | 0.032043 | 0.31586 | 0.28381 | -0.09613 | -0.13733 | 122.8821 | 122.7036 | 0.20142 | 123.0286 | 123.0057 | 0.30212 | -0.009156 | 122.7493 | 122.7081 | 0.10986 | 122.9736 | 122.8775 | 0.16937 | 0.077819 | 123.2529 | 123.0423 | 122.9645 | -0.3479 | 123.1613 | 123.1293 | 123.0148 | -0.34332
4851.6719 | 123.1796 | -122.8546 | 0.19684 | -0.19135 | 0.034287 | 0.0057252 | 0.011314 | -0.0094656 | -0.003339 | -0.0099335 | -0.24132 | -0.012768 | -0.0064664 | -0.0011216 | 0.0028263 | -0.019775 | 0.21973 | 0.2243 | 0.17395 | 0.17395 | 0.36621 | 0.027466 | -0.14648 | 0.13733 | 0.21057 | 0.064087 | 0.30212 | 0.26093 | -0.10529 | -0.13733 | 122.8821 | 122.7081 | 0.16937 | 123.0789 | 123.0286 | 0.32043 | 0.022889 | 122.7493 | 122.7173 | 0.10529 | 122.9919 | 122.9187 | 0.20142 | 0.064087 | 123.2208 | 123.0743 | 123.0286 | -0.34332 | 123.1567 | 123.1155 | 123.0652 | -0.33417
4853.3906 | 123.1018 | -122.8867 | 0.21515 | -0.015869 | 0.035355 | 0.0059388 | 0.010459 | -0.010534 | 0.006274 | -0.0063019 | -0.096359 | -0.0117 | -0.006039 | -0.001976 | 0.0085941 | -0.018707 | 0.10529 | 0.064087 | -0.036621 | 0.027466 | 0.31586 | -0.073242 | -0.24719 | 0.022888 | 0.036621 | -0.11902 | 0.20599 | 0.17853 | -0.1831 | -0.24719 | 122.8134 | 122.6395 | 0.10071 | 122.9507 | 122.9141 | 0.27466 | -0.10986 | 122.7036 | 122.6395 | -0.009155 | 122.9095 | 122.7676 | 0.12817 | -0.036621 | 123.2025 | 122.9919 | 122.85 | -0.46234 | 123.0927 | 123.0652 | 122.9233 | -0.46234
4855.0938 | 123.1522 | -122.9004 | 0.20142 | 0.12909 | 0.034927 | 0.0052978 | 0.0053321 | -0.010106 | -0.00013458 | -0.0069427 | 0.13252 | -0.012127 | -0.0075344 | -0.0011216 | 0.0073123 | -0.016784 | 0.10529 | 0.086975 | 0.041199 | 0.045776 | 0.21973 | -0.07782 | -0.24261 | 0.091553 | 0.12817 | -0.004578 | 0.16022 | 0.14191 | -0.16937 | -0.21973 | 122.8226 | 122.6578 | 0.018311 | 122.9874 | 122.9462 | 0.28839 | -0.09613 | 122.731 | 122.6807 | -0.041199 | 122.9919 | 122.8958 | 0.21515 | -0.059509 | 123.1201 | 123.0057 | 122.9416 | -0.44403 | 123.0606 | 123.0423 | 123.0286 | -0.42114
4856.7812 | 123.1476 | -122.8775 | 0.20142 | 0.1062 | 0.035996 | 0.007434 | 0.0066137 | -0.0098928 | -0.00056178 | -0.0082245 | 0.12489 | -0.012127 | -0.0088162 | -0.0032578 | 0.0083805 | -0.016998 | 0.036621 | -0.013733 | -0.07782 | -0.027466 | 0.27924 | -0.10529 | -0.27466 | 0.013733 | 0.013733 | -0.07782 | 0.17853 | 0.14648 | -0.20599 | -0.24261 | 122.7722 | 122.6028 | 0.07782 | 122.8638 | 122.85 | 0.24719 | -0.1648 | 122.6715 | 122.6349 | -0.022888 | 122.8912 | 122.7997 | 0.16479 | -0.054932 | 123.1567 | 122.9141 | 122.7997 | -0.47607 | 123.056 | 123.024 | 122.8912 | -0.44403
4858.4688 | 123.1979 | -122.8546 | 0.19684 | -0.19135 | 0.034073 | 0.007434 | 0.011527 | -0.0094656 | -0.004407 | -0.010147 | -0.16502 | -0.015545 | -0.00668 | -0.003685 | 0.0019717 | -0.016784 | 0.20599 | 0.26093 | 0.19684 | 0.19226 | 0.37537 | 0.050354 | -0.11444 | 0.18768 | 0.27466 | 0.12817 | 0.27008 | 0.24719 | -0.073242 | -0.10529 | 122.905 | 122.7402 | 0.17853 | 123.1155 | 123.0469 | 0.3067 | 0.009156 | 122.7814 | 122.7493 | 0.073243 | 123.0423 | 122.9828 | 0.23346 | 0.050354 | 123.23 | 123.0606 | 123.0515 | -0.31128 | 123.1247 | 123.1018 | 123.1293 | -0.30212
4860.1719 | 123.1934 | -122.8363 | 0.20142 | -0.21423 | 0.033218 | 0.0048706 | 0.0096045 | -0.009252 | -0.00098918 | -0.010788 | -0.25658 | -0.014264 | -0.0056118 | -0.0034714 | 0.0030399 | -0.019134 | 0.13733 | 0.14191 | 0.082397 | 0.11444 | 0.40283 | 0.004578 | -0.15106 | 0.073242 | 0.14648 | 0 | 0.30212 | 0.26093 | -0.13275 | -0.14648 | 122.8409 | 122.6852 | 0.20142 | 122.9782 | 122.9507 | 0.2655 | -0.064087 | 122.7036 | 122.6898 | 0.10071 | 122.9095 | 122.8363 | 0.14648 | 0.059509 | 123.2391 | 122.9736 | 122.9187 | -0.35248 | 123.1384 | 123.0972 | 122.9828 | -0.3479
4861.8438 | 123.1613 | -122.8958 | 0.2243 | 0.090942 | 0.03685 | 0.0055114 | 0.0044775 | -0.0094656 | 0.0028562 | -0.0075837 | 0.03334 | -0.0095639 | -0.0075344 | 0.00037379 | 0.0083805 | -0.017425 | 0 | -0.041199 | -0.10986 | -0.041199 | 0.27924 | -0.13733 | -0.28381 | 0 | -0.009155 | -0.12817 | 0.21515 | 0.14191 | -0.21515 | -0.25177 | 122.7585 | 122.612 | 0.054932 | 122.8546 | 122.8546 | 0.24261 | -0.2243 | 122.6807 | 122.644 | -0.009155 | 122.8958 | 122.7676 | 0.1236 | -0.082397 | 123.175 | 122.8958 | 122.7859 | -0.50812 | 123.111 | 123.0377 | 122.8867 | -0.47607
4863.5312 | 123.1613 | -122.8867 | 0.20599 | 0.1825 | 0.036209 | 0.0078614 | 0.0068273 | -0.0088248 | 0.00050622 | -0.0086517 | 0.16304 | -0.011273 | -0.00668 | -0.0030442 | 0.0077395 | -0.017852 | 0.027466 | 0.027466 | -0.022888 | 0.009155 | 0.23346 | -0.09613 | -0.27466 | 0.086975 | 0.10529 | -0.022888 | 0.16022 | 0.12817 | -0.17853 | -0.2243 | 122.7905 | 122.612 | 0.027465 | 122.9141 | 122.8958 | 0.28381 | -0.17853 | 122.7081 | 122.6624 | -0.045777 | 122.9736 | 122.8638 | 0.20142 | -0.07782 | 123.1201 | 122.9141 | 122.8638 | -0.48065 | 123.0469 | 123.0148 | 122.9919 | -0.4303
4865.2188 | 123.2483 | -122.8546 | 0.17853 | -0.19135 | 0.035996 | 0.0035888 | 0.014304 | -0.0090384 | -0.0012028 | -0.010147 | -0.25658 | -0.013196 | -0.0034756 | -0.0011216 | 0.0036807 | -0.017212 | 0.10071 | 0.09613 | 0.059509 | 0.10071 | 0.3891 | -0.013733 | -0.18768 | 0.059509 | 0.10529 | -0.009155 | 0.27924 | 0.24719 | -0.13733 | -0.16479 | 122.8409 | 122.6669 | 0.21057 | 122.9507 | 122.9553 | 0.28839 | -0.07782 | 122.7173 | 122.6898 | 0.10071 | 122.9141 | 122.8455 | 0.15564 | 0.068664 | 123.2437 | 122.9553 | 122.9141 | -0.36621 | 123.1338 | 123.1018 | 122.9599 | -0.34332
4866.9688 | 123.2529 | -122.8455 | 0.18768 | -0.22186 | 0.034073 | 0.0065796 | 0.0087499 | -0.0081838 | -0.00034818 | -0.0065155 | -0.19554 | -0.014691 | -0.0051846 | -0.00090781 | 0.0032535 | -0.016998 | 0.09613 | 0.11444 | 0.041199 | 0.10986 | 0.41657 | -0.004578 | -0.16937 | 0.054932 | 0.11902 | -0.018311 | 0.29297 | 0.24719 | -0.14648 | -0.1831 | 122.8409 | 122.6761 | 0.22888 | 122.9599 | 122.9553 | 0.27924 | -0.091553 | 122.699 | 122.6624 | 0.10529 | 122.9004 | 122.8271 | 0.16479 | 0.059509 | 123.262 | 122.9416 | 122.8867 | -0.35706 | 123.1384 | 123.0927 | 122.9645 | -0.37079
4868.6562 | 123.23 | -122.8455 | 0.19226 | -0.26764 | 0.036423 | 0.0082886 | 0.011527 | -0.0077566 | -0.0014164 | -0.010788 | -0.27184 | -0.015118 | -0.0039028 | -0.00069421 | 0.0023989 | -0.016143 | 0.091553 | 0.14648 | 0.073242 | 0.11902 | 0.43945 | 0.009155 | -0.16937 | 0.054932 | 0.14648 | -0.009155 | 0.31128 | 0.27466 | -0.11444 | -0.16937 | 122.8546 | 122.6761 | 0.24719 | 122.9919 | 122.9645 | 0.28839 | -0.10071 | 122.731 | 122.6761 | 0.11902 | 122.9004 | 122.8363 | 0.16022 | 0.082397 | 123.2849 | 122.937 | 122.9187 | -0.36163 | 123.1567 | 123.1201 | 122.9919 | -0.36163
4870.375 | 123.111 | -122.8867 | 0.21515 | 0.075684 | 0.033646 | 0.0065796 | 0.0085363 | -0.010106 | -0.0059024 | -0.010147 | 0.13252 | -0.014477 | -0.0047574 | -0.0038986 | 0.0017581 | -0.016784 | 0.054932 | 0.14191 | 0.07782 | 0.064087 | 0.29297 | -0.036621 | -0.20599 | 0.086975 | 0.16479 | 0.073242 | 0.23346 | 0.18768 | -0.1236 | -0.15564 | 122.85 | 122.6807 | 0.07782 | 123.0286 | 122.9507 | 0.27008 | -0.16022 | 122.7631 | 122.731 | 0.01831 | 122.9736 | 122.9599 | 0.22888 | -0.027466 | 123.1796 | 122.9416 | 122.9645 | -0.42114 | 123.1201 | 123.0743 | 123.0515 | -0.37079
4872.0625 | 123.0927 | -122.8546 | 0.20142 | 0.19775 | 0.033432 | 0.0072204 | 0.0051183 | -0.0079702 | -0.0029118 | -0.0092927 | 0.20882 | -0.015759 | -0.006039 | -0.0028306 | 0.0068851 | -0.016571 | 0.07782 | 0.10986 | 0.022888 | 0.036621 | 0.21515 | -0.10071 | -0.26093 | 0.09613 | 0.14191 | 0.018311 | 0.15564 | 0.11902 | -0.17853 | -0.21515 | 122.7539 | 122.5937 | 0.013733 | 122.9645 | 122.8912 | 0.29755 | -0.1236 | 122.6761 | 122.6395 | -0.045776 | 122.9507 | 122.8729 | 0.23346 | -0.082397 | 123.0698 | 122.9324 | 122.8775 | -0.46234 | 123.0103 | 122.9736 | 122.9965 | -0.41657
4873.7656 | 123.1522 | -122.8867 | 0.19684 | 0.1825 | 0.034714 | 0.0072204 | 0.0072547 | -0.0098928 | -0.00056178 | -0.0069427 | 0.16304 | -0.013196 | -0.0056118 | -0.0026168 | 0.0075259 | -0.016784 | 0.041199 | 0.041199 | -0.022888 | -0.004578 | 0.2655 | -0.10529 | -0.24719 | 0.09613 | 0.10529 | -0.009155 | 0.16479 | 0.11902 | -0.17395 | -0.21057 | 122.7814 | 122.6395 | 0.068665 | 122.9279 | 122.8821 | 0.24261 | -0.15564 | 122.7127 | 122.6761 | -0.032043 | 122.9828 | 122.8775 | 0.20142 | -0.077819 | 123.1522 | 122.9279 | 122.8638 | -0.44403 | 123.0515 | 123.0057 | 122.9919 | -0.40741
4875.4688 | 123.1476 | -122.8867 | 0.21973 | -0.076904 | 0.038773 | 0.0050842 | 0.0085363 | -0.0096792 | 0.004565 | -0.0065155 | -0.11925 | -0.010418 | -0.0056118 | -0.0034714 | 0.0077395 | -0.019134 | 0.11444 | 0.10071 | 0 | 0.064087 | 0.32044 | -0.064087 | -0.24261 | 0.059509 | 0.073242 | -0.073242 | 0.21515 | 0.17853 | -0.16937 | -0.21973 | 122.8226 | 122.644 | 0.10071 | 122.9874 | 122.9507 | 0.3067 | -0.10529 | 122.7173 | 122.6669 | -0.004578 | 122.9462 | 122.8134 | 0.14649 | -0.041199 | 123.2071 | 123.0011 | 122.8867 | -0.46234 | 123.1018 | 123.0652 | 122.9599 | -0.43945
4877.1875 | 123.2666 | -122.8546 | 0.1831 | -0.16083 | 0.035141 | 0.0070068 | 0.010886 | -0.011388 | -0.0012028 | -0.0084381 | -0.23369 | -0.014264 | -0.006039 | -0.003685 | 0.0043215 | -0.018707 | 0.09613 | 0.11902 | 0.050354 | 0.10529 | 0.38452 | -0.018311 | -0.20142 | 0.059509 | 0.11902 | -0.027466 | 0.27924 | 0.23346 | -0.14648 | -0.19684 | 122.8363 | 122.6532 | 0.20142 | 122.9736 | 122.9599 | 0.3067 | -0.086975 | 122.7081 | 122.6578 | 0.096131 | 122.9141 | 122.8271 | 0.16937 | 0.050354 | 123.2391 | 122.9507 | 122.905 | -0.38452 | 123.1338 | 123.0881 | 122.9736 | -0.37994
4878.9375 | 123.2071 | -122.8363 | 0.16022 | -0.1532 | 0.032791 | 0.0067932 | 0.013023 | -0.0081838 | -0.005048 | -0.0097199 | -0.13451 | -0.015545 | -0.0068936 | -0.0032578 | 0.0015445 | -0.017639 | 0.16937 | 0.28381 | 0.19684 | 0.1831 | 0.36163 | 0.027466 | -0.14191 | 0.17853 | 0.28839 | 0.15564 | 0.24261 | 0.22888 | -0.064087 | -0.11444 | 122.8638 | 122.6944 | 0.20142 | 123.1201 | 123.0194 | 0.32501 | 0.009156 | 122.7722 | 122.7219 | 0.082398 | 123.0148 | 122.9919 | 0.27008 | 0.068665 | 123.1979 | 123.0057 | 123.0331 | -0.30212 | 123.0789 | 123.0652 | 123.1247 | -0.27466
4880.625 | 123.1155 | -122.8821 | 0.20599 | 0.068054 | 0.033859 | 0.0057252 | 0.0096045 | -0.010106 | -0.0046206 | -0.0095063 | 0.063858 | -0.012341 | -0.0036892 | -0.0024032 | 0.0023989 | -0.016143 | 0.059509 | 0.1236 | 0.07782 | 0.07782 | 0.29755 | -0.036621 | -0.21057 | 0.10986 | 0.16479 | 0.064087 | 0.23804 | 0.19226 | -0.10986 | -0.17395 | 122.8455 | 122.6715 | 0.091552 | 123.0057 | 122.9599 | 0.28839 | -0.14649 | 122.7722 | 122.7081 | 0.032043 | 122.9919 | 122.9462 | 0.23804 | -0.013733 | 123.1796 | 122.9416 | 122.9599 | -0.41657 | 123.1201 | 123.0743 | 123.0469 | -0.37994
4882.3438 | 123.0835 | -122.8958 | 0.2243 | 0.1062 | 0.031723 | 0.0078614 | 0.0072547 | -0.009252 | -0.002698 | -0.010361 | 0.16304 | -0.015332 | -0.0081754 | -0.0021896 | 0.0034671 | -0.017852 | 0.073242 | 0.11902 | 0.054932 | 0.064087 | 0.24719 | -0.07782 | -0.2243 | 0.11902 | 0.13275 | 0.064087 | 0.17853 | 0.16479 | -0.15564 | -0.17395 | 122.818 | 122.6715 | 0.022888 | 123.0148 | 122.9599 | 0.28839 | -0.15106 | 122.7402 | 122.7219 | -0.045776 | 123.0148 | 122.9599 | 0.23804 | -0.059509 | 123.143 | 122.9691 | 122.9507 | -0.44861 | 123.0743 | 123.0606 | 123.0286 | -0.39825
4884.0625 | 123.2117 | -122.8638 | 0.18768 | -0.015869 | 0.03215 | 0.008075 | 0.0089635 | -0.012456 | -0.0054752 | -0.011002 | 0.010452 | -0.015973 | -0.0051846 | -0.0034714 | 0.0023989 | -0.01593 | 0.09613 | 0.15106 | 0.09613 | 0.10071 | 0.32959 | -0.022888 | -0.16937 | 0.11444 | 0.17853 | 0.07782 | 0.24719 | 0.21057 | -0.10529 | -0.14191 | 122.8409 | 122.6944 | 0.14191 | 123.0148 | 122.9645 | 0.27008 | -0.091553 | 122.7585 | 122.7219 | 0.059509 | 122.9782 | 122.9416 | 0.21973 | 0.022888 | 123.1934 | 122.9599 | 122.9599 | -0.35706 | 123.111 | 123.0743 | 123.0423 | -0.32959
4885.75 | 123.143 | -122.8821 | 0.17853 | -0.00061023 | 0.032578 | 0.0072204 | 0.0072547 | -0.01032 | -0.0024844 | -0.011856 | 0.056228 | -0.014264 | -0.0081754 | -0.0034714 | 0.0032535 | -0.016998 | 0.11444 | 0.13275 | 0.07782 | 0.082397 | 0.32959 | -0.018311 | -0.19684 | 0.10986 | 0.13733 | 0.064087 | 0.25177 | 0.18768 | -0.1236 | -0.15564 | 122.8638 | 122.6852 | 0.15106 | 123.0148 | 122.9645 | 0.27924 | -0.064087 | 122.7585 | 122.7264 | 0.073242 | 122.9919 | 122.9462 | 0.21973 | 0.009155 | 123.2117 | 122.9965 | 122.9599 | -0.37537 | 123.1338 | 123.0698 | 123.0194 | -0.33417
4887.4375 | 123.0881 | -122.8821 | 0.21057 | 0.12909 | 0.031937 | 0.0087158 | 0.0044775 | -0.008611 | -0.0022708 | -0.010147 | 0.094375 | -0.01405 | -0.009457 | -0.0017624 | 0.0070987 | -0.018707 | 0.10986 | 0.11444 | 0.054932 | 0.050354 | 0.27008 | -0.07782 | -0.21973 | 0.11902 | 0.13733 | 0.045776 | 0.21515 | 0.16022 | -0.13275 | -0.16937 | 122.8043 | 122.6624 | 0.05951 | 122.9965 | 122.9324 | 0.27008 | -0.10071 | 122.7493 | 122.7127 | 0.004578 | 123.0011 | 122.9279 | 0.21515 | -0.050354 | 123.1522 | 122.9919 | 122.937 | -0.4303 | 123.0972 | 123.0423 | 123.0194 | -0.37994
4889.1094 | 123.143 | -122.8775 | 0.23346 | 0.083313 | 0.036636 | 0.0061524 | 0.0068273 | -0.0066884 | 0.0043514 | -0.0086517 | 0.04097 | -0.011059 | -0.0090298 | -0.001976 | 0.0085941 | -0.019561 | 0.032043 | -0.054932 | -0.10071 | -0.027466 | 0.27924 | -0.1236 | -0.29755 | 0 | -0.027466 | -0.14191 | 0.18768 | 0.15106 | -0.21973 | -0.2655 | 122.7539 | 122.58 | 0.045777 | 122.8226 | 122.85 | 0.27008 | -0.20142 | 122.6578 | 122.612 | -0.045776 | 122.8775 | 122.7356 | 0.1236 | -0.082397 | 123.1567 | 122.9095 | 122.7768 | -0.531 | 123.0652 | 123.0286 | 122.85 | -0.49896
4890.8281 | 123.2071 | -122.8546 | 0.20599 | 0.0070193 | 0.032791 | 0.0070068 | 0.0089635 | -0.0098928 | -0.0041934 | -0.0092927 | 0.010452 | -0.015332 | -0.0053982 | -0.0026168 | 0.0023989 | -0.016143 | 0.086975 | 0.12817 | 0.10071 | 0.10529 | 0.32959 | -0.022888 | -0.19226 | 0.11444 | 0.18768 | 0.091553 | 0.24719 | 0.21057 | -0.10986 | -0.14648 | 122.8317 | 122.6624 | 0.1236 | 122.9828 | 122.9599 | 0.29755 | -0.11902 | 122.7448 | 122.7081 | 0.041198 | 122.9691 | 122.9462 | 0.23804 | 0.004577 | 123.1842 | 122.9416 | 122.9553 | -0.39826 | 123.1018 | 123.0652 | 123.0423 | -0.35248
4892.5312 | 123.23 | -122.8317 | 0.17395 | -0.099793 | 0.031296 | 0.0089294 | 0.012382 | -0.008611 | -0.004407 | -0.01207 | -0.08873 | -0.015973 | -0.0068936 | -0.0024032 | 0.00047633 | -0.019134 | 0.20599 | 0.22888 | 0.19684 | 0.17395 | 0.36621 | 0 | -0.15106 | 0.21515 | 0.27924 | 0.15106 | 0.25635 | 0.23346 | -0.086975 | -0.13733 | 122.8317 | 122.6807 | 0.19226 | 123.0606 | 123.0057 | 0.32501 | 0.032044 | 122.7448 | 122.6944 | 0.082398 | 123.0469 | 122.9828 | 0.28839 | 0.059509 | 123.1979 | 123.0377 | 123.0286 | -0.32501 | 123.0881 | 123.0652 | 123.111 | -0.31128
4894.2188 | 123.175 | -122.8638 | 0.20142 | -0.0082397 | 0.031723 | 0.0082886 | 0.0087499 | -0.0096792 | -0.0024844 | -0.0099335 | 0.03334 | -0.014691 | -0.0068936 | -0.0026168 | 0.0060305 | -0.018707 | 0.10071 | 0.1236 | 0.082397 | 0.091553 | 0.32959 | -0.013733 | -0.18768 | 0.13733 | 0.16022 | 0.073242 | 0.23346 | 0.19226 | -0.09613 | -0.15564 | 122.85 | 122.6761 | 0.12817 | 122.9874 | 122.9553 | 0.27924 | -0.10071 | 122.7676 | 122.7081 | 0.032043 | 123.0011 | 122.937 | 0.22888 | -0.009155 | 123.1934 | 122.9645 | 122.9462 | -0.3891 | 123.0972 | 123.056 | 123.024 | -0.35706
4895.9688 | 123.2437 | -122.8317 | 0.16937 | -0.22186 | 0.035782 | 0.0076478 | 0.011954 | -0.0071158 | 0.0032834 | -0.0086517 | -0.24895 | -0.0117 | -0.0047574 | -0.00069421 | 0.0056033 | -0.019348 | 0.15106 | 0.086975 | 0.027466 | 0.082397 | 0.39368 | -0.013733 | -0.18768 | 0.086975 | 0.1236 | -0.022888 | 0.30212 | 0.24719 | -0.11902 | -0.18768 | 122.818 | 122.644 | 0.2243 | 122.9187 | 122.9141 | 0.27008 | -0.018311 | 122.7127 | 122.644 | 0.13275 | 122.9187 | 122.8088 | 0.16479 | 0.077819 | 123.2254 | 122.9828 | 122.8592 | -0.35706 | 123.1339 | 123.0789 | 122.9553 | -0.35706
4897.6562 | 123.2483 | -122.8546 | 0.1831 | -0.18372 | 0.038773 | 0.002948 | 0.012595 | -0.010534 | 0.0058468 | -0.0069427 | -0.23369 | -0.012982 | -0.0041164 | -0.0011216 | 0.0053897 | -0.02127 | 0.14191 | 0.11902 | 0.036621 | 0.09613 | 0.38452 | -0.045776 | -0.18768 | 0.082397 | 0.11444 | -0.036621 | 0.25177 | 0.2243 | -0.16479 | -0.19226 | 122.8088 | 122.6669 | 0.20142 | 122.9736 | 122.9507 | 0.28381 | -0.041198 | 122.6898 | 122.6624 | 0.068665 | 122.937 | 122.818 | 0.15564 | 0.041199 | 123.2391 | 122.9965 | 122.8912 | -0.37079 | 123.1064 | 123.0789 | 122.9691 | -0.37537
4899.3906 | 123.1293 | -122.9004 | 0.21057 | 0.15961 | 0.034714 | 0.0048706 | 0.0055457 | -0.010961 | -0.0024844 | -0.0075837 | 0.18593 | -0.014264 | -0.0056118 | 0.00058739 | 0.0070987 | -0.018493 | 0.082397 | 0.09613 | 0.032043 | 0.041199 | 0.22888 | -0.073242 | -0.2655 | 0.10071 | 0.12817 | -0.004578 | 0.13275 | 0.091553 | -0.20142 | -0.21973 | 122.8271 | 122.6349 | 0.018311 | 122.9965 | 122.9416 | 0.3067 | -0.12817 | 122.699 | 122.6807 | -0.07782 | 123.0011 | 122.8958 | 0.21515 | -0.11902 | 123.1293 | 122.9828 | 122.9324 | -0.47607 | 123.0331 | 122.9919 | 123.0286 | -0.4303
4901.0781 | 123.111 | -122.8912 | 0.21515 | -0.0082397 | 0.037064 | 0.0052978 | 0.0053321 | -0.011815 | 0.0049924 | -0.0071563 | -0.065842 | -0.011273 | -0.0098844 | -0.00048061 | 0.0090213 | -0.019348 | 0.068665 | 0.054932 | -0.041199 | 0.013733 | 0.3067 | -0.091553 | -0.26093 | 0.022888 | 0.022888 | -0.1236 | 0.21515 | 0.18768 | -0.19684 | -0.25177 | 122.7997 | 122.6303 | 0.091553 | 122.9462 | 122.905 | 0.27466 | -0.14648 | 122.6944 | 122.6395 | 0 | 122.9141 | 122.7676 | 0.12817 | -0.027466 | 123.1979 | 122.9599 | 122.85 | -0.47607 | 123.1064 | 123.0789 | 122.9141 | -0.46692
4902.7812 | 123.1842 | -122.8546 | 0.19684 | -0.22949 | 0.035141 | 0.0085022 | 0.0098181 | -0.0088248 | -0.0029118 | -0.0095063 | -0.18028 | -0.013836 | -0.0045438 | -0.0030442 | 0.0036807 | -0.017212 | 0.11444 | 0.15106 | 0.086975 | 0.1236 | 0.3891 | 0.009155 | -0.14648 | 0.082397 | 0.16022 | 0.004578 | 0.29755 | 0.25635 | -0.13275 | -0.15564 | 122.8638 | 122.7081 | 0.19226 | 123.0057 | 122.9782 | 0.27008 | -0.082397 | 122.7219 | 122.699 | 0.10071 | 122.937 | 122.8592 | 0.16022 | 0.05951 | 123.2437 | 122.9691 | 122.9416 | -0.34332 | 123.1522 | 123.111 | 123.0148 | -0.35248
4904.4844 | 123.2254 | -122.8317 | 0.17395 | -0.12268 | 0.028946 | 0.0059388 | 0.0078955 | -0.010106 | -0.007825 | -0.0088653 | -0.065842 | -0.015332 | -0.008389 | -0.0030442 | 0.0011173 | -0.017852 | 0.16479 | 0.2655 | 0.19226 | 0.17395 | 0.37079 | 0.022888 | -0.15106 | 0.20599 | 0.27924 | 0.16022 | 0.26093 | 0.21057 | -0.07782 | -0.10986 | 122.8546 | 122.6807 | 0.19684 | 123.0972 | 123.0057 | 0.32501 | -0.009155 | 122.7539 | 122.7219 | 0.086975 | 123.0377 | 122.9919 | 0.27008 | 0.036621 | 123.2025 | 122.9965 | 123.024 | -0.32501 | 123.0927 | 123.0423 | 123.111 | -0.28381
4906.1719 | 123.2391 | -122.8409 | 0.1831 | -0.22186 | 0.035782 | 0.0040162 | 0.011741 | -0.0090384 | 0.00050622 | -0.0086517 | -0.22606 | -0.012768 | -0.006039 | -0.0013352 | 0.0056033 | -0.018921 | 0.10986 | 0.10986 | 0.036621 | 0.10071 | 0.41199 | -0.004578 | -0.17395 | 0.050354 | 0.12817 | -0.018311 | 0.27466 | 0.24261 | -0.12817 | -0.16479 | 122.8363 | 122.6669 | 0.22888 | 122.9507 | 122.9416 | 0.27466 | -0.073242 | 122.7127 | 122.6761 | 0.091553 | 122.8912 | 122.8226 | 0.14648 | 0.05951 | 123.2529 | 122.9507 | 122.8775 | -0.35706 | 123.1155 | 123.0835 | 122.9691 | -0.3479
4907.8594 | 123.1613 | -122.8409 | 0.19684 | 0.014648 | 0.031082 | 0.0065796 | 0.0081091 | -0.01032 | -0.0037662 | -0.010574 | 0.048599 | -0.012768 | -0.0056118 | -5.3406e-05 | 0.0013309 | -0.018066 | 0.064087 | 0.14191 | 0.09613 | 0.091553 | 0.31586 | -0.022888 | -0.1831 | 0.10071 | 0.17395 | 0.082397 | 0.24719 | 0.21515 | -0.1236 | -0.15564 | 122.818 | 122.6578 | 0.11902 | 122.9828 | 122.9324 | 0.27466 | -0.13275 | 122.7173 | 122.6852 | 0.050354 | 122.9416 | 122.9233 | 0.23804 | 0.018311 | 123.1567 | 122.905 | 122.937 | -0.37994 | 123.0881 | 123.056 | 123.0148 | -0.35248
4909.5625 | 123.2346 | -122.8226 | 0.17395 | -0.12268 | 0.031082 | 0.0059388 | 0.0083227 | -0.011815 | -0.004407 | -0.012497 | -0.081101 | -0.015332 | -0.0062528 | -0.00090781 | 0.0023989 | -0.017852 | 0.20142 | 0.25177 | 0.17395 | 0.16937 | 0.35248 | 0.027466 | -0.15106 | 0.21973 | 0.27008 | 0.16022 | 0.26093 | 0.22888 | -0.07782 | -0.1236 | 122.85 | 122.6715 | 0.17853 | 123.0743 | 122.9919 | 0.32044 | 0.027466 | 122.7448 | 122.699 | 0.086975 | 123.0423 | 122.9828 | 0.28381 | 0.054932 | 123.175 | 123.024 | 122.9965 | -0.32501 | 123.0835 | 123.0515 | 123.0927 | -0.29755
4911.25 | 123.2254 | -122.8592 | 0.17853 | -0.13794 | 0.031723 | 0.0076478 | 0.0087499 | -0.01032 | -0.0056888 | -0.011002 | -0.14214 | -0.014691 | -0.0088162 | -0.0047532 | 0.0034671 | -0.01828 | 0.2243 | 0.27008 | 0.20599 | 0.19226 | 0.35248 | 0.013733 | -0.14648 | 0.21057 | 0.27466 | 0.15564 | 0.26093 | 0.23346 | -0.07782 | -0.10071 | 122.8729 | 122.7127 | 0.17395 | 123.1293 | 123.0515 | 0.33874 | 0.045776 | 122.7814 | 122.7585 | 0.082397 | 123.0698 | 123.0148 | 0.25635 | 0.054931 | 123.2117 | 123.0835 | 123.0652 | -0.32501 | 123.1201 | 123.0927 | 123.1338 | -0.27924
4912.9844 | 123.1842 | -122.85 | 0.21515 | -0.22186 | 0.033005 | 0.0087158 | 0.011527 | -0.0073294 | 0.00093342 | -0.010574 | -0.23369 | -0.010418 | -0.0071072 | -5.3406e-05 | 0.0034671 | -0.018921 | 0.16937 | 0.15106 | 0.091553 | 0.12817 | 0.41199 | 0.009155 | -0.16022 | 0.09613 | 0.13275 | 0.013733 | 0.31128 | 0.27466 | -0.10986 | -0.14648 | 122.8592 | 122.6898 | 0.19684 | 123.0011 | 122.9782 | 0.28839 | -0.045776 | 122.7402 | 122.7036 | 0.09613 | 122.9462 | 122.8638 | 0.16022 | 0.059509 | 123.262 | 123.0194 | 122.9416 | -0.37537 | 123.1613 | 123.1247 | 122.9828 | -0.36163
4914.6719 | 123.1155 | -122.9004 | 0.20142 | 0.052795 | 0.033859 | 0.0067932 | 0.010673 | -0.009252 | -0.002698 | -0.0075837 | 0.056228 | -0.014264 | -0.00668 | -0.00048061 | 0.0023989 | -0.017639 | 0.082397 | 0.11902 | 0.082397 | 0.086975 | 0.32044 | -0.027466 | -0.20599 | 0.10986 | 0.16022 | 0.064087 | 0.2243 | 0.19226 | -0.11444 | -0.16022 | 122.8729 | 122.6944 | 0.11902 | 123.0194 | 122.9874 | 0.29297 | -0.11902 | 122.7859 | 122.7402 | 0.022888 | 123.0103 | 122.9645 | 0.2243 | -0.009155 | 123.2208 | 122.9828 | 122.9828 | -0.40741 | 123.1247 | 123.0927 | 123.0606 | -0.36163
4916.3906 | 123.0972 | -122.9004 | 0.21973 | 0.11383 | 0.033432 | 0.008075 | 0.0064001 | -0.009252 | -0.00013458 | -0.0080109 | 0.079117 | -0.014905 | -0.0079618 | -0.0013352 | 0.0049625 | -0.016143 | 0.10071 | 0.11902 | 0.054932 | 0.036621 | 0.24719 | -0.068665 | -0.23804 | 0.14648 | 0.14648 | 0.045776 | 0.1831 | 0.17395 | -0.14648 | -0.20599 | 122.8317 | 122.6624 | 0.027465 | 123.0194 | 122.937 | 0.27466 | -0.11902 | 122.7539 | 122.6944 | -0.036622 | 123.0469 | 122.9462 | 0.25177 | -0.045777 | 123.1476 | 123.0011 | 122.9553 | -0.45776 | 123.0835 | 123.0743 | 123.0469 | -0.42572
4918.0938 | 123.2346 | -122.8271 | 0.18768 | -0.069275 | 0.034073 | 0.0055114 | 0.011954 | -0.010961 | -0.0031254 | -0.010147 | -0.096359 | -0.015759 | -0.0088162 | -0.0021896 | 0.0030399 | -0.016784 | 0.15106 | 0.20142 | 0.16022 | 0.13733 | 0.3479 | -0.009155 | -0.15564 | 0.20142 | 0.23804 | 0.15106 | 0.27008 | 0.21973 | -0.082397 | -0.12817 | 122.818 | 122.6715 | 0.16022 | 123.0286 | 122.9645 | 0.29297 | -0.036621 | 122.7448 | 122.699 | 0.082398 | 123.0286 | 122.9782 | 0.27924 | 0.032044 | 123.175 | 122.9782 | 122.9874 | -0.34332 | 123.0972 | 123.0469 | 123.0652 | -0.31586
4919.7969 | 123.2391 | -122.8226 | 0.17395 | -0.12268 | 0.032578 | 0.0087158 | 0.0098181 | -0.01032 | -0.0012028 | -0.011642 | -0.13451 | -0.015118 | -0.006039 | -0.0024032 | 0.0034671 | -0.017425 | 0.20599 | 0.27924 | 0.20142 | 0.17853 | 0.34332 | 0.022888 | -0.1236 | 0.23346 | 0.28839 | 0.14648 | 0.25177 | 0.21973 | -0.068665 | -0.1236 | 122.8455 | 122.699 | 0.16937 | 123.1018 | 123.0011 | 0.30212 | 0.032044 | 122.7539 | 122.699 | 0.07782 | 123.056 | 122.9691 | 0.27008 | 0.045777 | 123.1659 | 123.0286 | 123.024 | -0.29755 | 123.0743 | 123.0423 | 123.111 | -0.29755
4921.5312 | 123.2208 | -122.8317 | 0.1831 | -0.084534 | 0.032791 | 0.0067932 | 0.0070409 | -0.010961 | -0.0039798 | -0.011002 | -0.14214 | -0.01405 | -0.010312 | -0.0045394 | 0.0049625 | -0.014435 | 0.19226 | 0.21515 | 0.15106 | 0.14648 | 0.34332 | -0.004578 | -0.13733 | 0.21515 | 0.27008 | 0.15106 | 0.2655 | 0.22888 | -0.064087 | -0.11902 | 122.8271 | 122.6944 | 0.16022 | 123.0469 | 122.9782 | 0.28381 | 0.009156 | 122.7676 | 122.7127 | 0.082398 | 123.0469 | 122.9828 | 0.27008 | 0.045777 | 123.175 | 123.024 | 122.9828 | -0.32043 | 123.0972 | 123.0606 | 123.1018 | -0.30212
4923.2188 | 123.2254 | -122.85 | 0.18768 | -0.16083 | 0.028092 | 0.01192 | 0.0061865 | -0.010534 | -0.0029118 | -0.0086517 | -0.08873 | -0.015973 | -0.012021 | -0.0030442 | 0.0049625 | -0.016143 | 0.22888 | 0.24719 | 0.17853 | 0.14191 | 0.36163 | 0.032043 | -0.15106 | 0.21515 | 0.27466 | 0.15564 | 0.24261 | 0.2243 | -0.07782 | -0.11902 | 122.8821 | 122.699 | 0.17395 | 123.0972 | 122.9919 | 0.29297 | 0.041199 | 122.7722 | 122.731 | 0.054932 | 123.0652 | 123.0057 | 0.27466 | 0.036621 | 123.2117 | 123.0789 | 123.0286 | -0.33874 | 123.0927 | 123.0743 | 123.1247 | -0.3067
4924.8906 | 123.1522 | -122.8867 | 0.20142 | 0.1062 | 0.035568 | 0.0065796 | 0.0057593 | -0.009252 | 0.0047788 | -0.0063019 | 0.04097 | -0.012341 | -0.010098 | -0.0026168 | 0.010089 | -0.016571 | 0.07782 | -0.022888 | -0.064087 | -0.022888 | 0.27466 | -0.10529 | -0.28381 | 0.050354 | 0.018311 | -0.091553 | 0.21057 | 0.15106 | -0.20142 | -0.24719 | 122.7814 | 122.6028 | 0.073242 | 122.8638 | 122.8638 | 0.26092 | -0.1236 | 122.6852 | 122.6395 | 0.009155 | 122.937 | 122.7951 | 0.15564 | -0.050354 | 123.1613 | 122.9645 | 122.8226 | -0.48523 | 123.0972 | 123.0377 | 122.905 | -0.44861
4926.5781 | 123.1567 | -122.8546 | 0.21515 | 0.14435 | 0.035782 | 0.007434 | 0.0072547 | -0.010747 | 7.902e-05 | -0.0069427 | 0.14015 | -0.012768 | -0.010312 | -0.0026168 | 0.0085941 | -0.016784 | 0.13275 | 0.09613 | 0.050354 | 0.064087 | 0.23804 | -0.082397 | -0.24261 | 0.09613 | 0.1236 | 0 | 0.13733 | 0.10529 | -0.20142 | -0.21973 | 122.7722 | 122.612 | 0.022888 | 122.9507 | 122.9187 | 0.3067 | -0.082398 | 122.6532 | 122.6349 | -0.07782 | 122.9507 | 122.8546 | 0.21973 | -0.10986 | 123.0927 | 122.9874 | 122.905 | -0.45776 | 122.9919 | 122.9599 | 122.9782 | -0.43488
4928.2656 | 123.1293 | -122.8729 | 0.22888 | 0.17487 | 0.037705 | 0.0067932 | 0.0070409 | -0.010747 | -0.00077538 | -0.0092927 | 0.15541 | -0.012768 | -0.0090298 | -0.0032578 | 0.0066715 | -0.017639 | 0.11444 | 0.064087 | 0.032043 | 0.041199 | 0.2243 | -0.091553 | -0.24719 | 0.10529 | 0.13275 | -0.004578 | 0.13275 | 0.10986 | -0.19684 | -0.24261 | 122.7814 | 122.6257 | -0.004578 | 122.937 | 122.9141 | 0.28839 | -0.11444 | 122.6761 | 122.6303 | -0.096131 | 122.9782 | 122.8683 | 0.23804 | -0.11902 | 123.0972 | 122.9874 | 122.905 | -0.47607 | 123.0057 | 122.9828 | 123.0057 | -0.4715
4929.9688 | 123.175 | -122.8592 | 0.21973 | -0.12268 | 0.038345 | 0.004657 | 0.0085363 | -0.0098928 | 0.0037106 | -0.0071563 | -0.16502 | -0.012127 | -0.0092434 | -0.0028306 | 0.0085941 | -0.017425 | 0.15564 | 0.091553 | 0.004578 | 0.064087 | 0.31586 | -0.068665 | -0.25177 | 0.064087 | 0.091553 | -0.068665 | 0.23346 | 0.19684 | -0.16479 | -0.20599 | 122.7905 | 122.6074 | 0.09613 | 122.9507 | 122.9233 | 0.31586 | -0.064087 | 122.6944 | 122.6532 | 0.013732 | 122.9233 | 122.7905 | 0.13733 | -0.022889 | 123.175 | 123.0148 | 122.8638 | -0.4715 | 123.0927 | 123.056 | 122.9507 | -0.42572
4931.6719 | 123.1613 | -122.8867 | 0.21057 | 0.15198 | 0.037491 | 0.0057252 | 0.0066137 | -0.0064748 | 0.0011472 | -0.0075837 | 0.12489 | -0.012768 | -0.0034756 | -0.0032578 | 0.0066715 | -0.016998 | 0.082397 | 0.054932 | 0.018311 | 0.027466 | 0.24261 | -0.10071 | -0.2655 | 0.10071 | 0.13733 | 0.004578 | 0.15564 | 0.1236 | -0.16937 | -0.21515 | 122.7859 | 122.6212 | 0.032044 | 122.9416 | 122.9141 | 0.29297 | -0.12817 | 122.7173 | 122.6715 | -0.054931 | 122.9874 | 122.8912 | 0.21973 | -0.086975 | 123.1293 | 122.9691 | 122.905 | -0.47607 | 123.0423 | 123.0103 | 123.024 | -0.42572
4933.375 | 123.2346 | -122.8317 | 0.18768 | -0.14557 | 0.0345 | 0.006366 | 0.0093909 | -0.01032 | -0.0052616 | -0.0097199 | -0.073471 | -0.015118 | -0.0079618 | -0.0032578 | 0.0026125 | -0.015716 | 0.21973 | 0.24261 | 0.19684 | 0.17395 | 0.3479 | 0.032043 | -0.13733 | 0.19684 | 0.27924 | 0.16479 | 0.25177 | 0.21973 | -0.064087 | -0.11444 | 122.8638 | 122.6944 | 0.16022 | 123.0743 | 123.0057 | 0.31128 | 0.032044 | 122.7676 | 122.7173 | 0.064087 | 123.0286 | 122.9965 | 0.27924 | 0.032044 | 123.1796 | 123.0515 | 123.0286 | -0.32501 | 123.0835 | 123.0515 | 123.111 | -0.30212
4935.0781 | 123.2254 | -122.8271 | 0.19226 | -0.038757 | 0.030655 | 0.0095704 | 0.011314 | -0.009252 | -0.0039798 | -0.0097199 | -0.035324 | -0.014264 | -0.0068936 | -0.0011216 | 0.00026273 | -0.018707 | 0.14191 | 0.16479 | 0.13733 | 0.13733 | 0.35248 | 0.004578 | -0.16479 | 0.1831 | 0.22888 | 0.13275 | 0.25177 | 0.2243 | -0.09613 | -0.13275 | 122.8317 | 122.6624 | 0.16022 | 122.9919 | 122.9645 | 0.30212 | -0.050354 | 122.731 | 122.6944 | 0.059509 | 123.0103 | 122.9599 | 0.2655 | 0.032043 | 123.1796 | 122.9691 | 122.9645 | -0.35706 | 123.0789 | 123.0515 | 123.056 | -0.32501
4936.7656 | 123.1293 | -122.8912 | 0.20599 | 0.17487 | 0.033646 | 0.0082886 | 0.0051183 | -0.0094656 | 0.00071982 | -0.0086517 | 0.17067 | -0.0117 | -0.0088162 | -0.00026701 | 0.0070987 | -0.01828 | 0.11902 | 0.10071 | 0.041199 | 0.068665 | 0.21057 | -0.10071 | -0.24261 | 0.091553 | 0.11444 | 0 | 0.15106 | 0.11444 | -0.19684 | -0.24261 | 122.7905 | 122.6486 | 0.004577 | 122.9919 | 122.9599 | 0.31128 | -0.086975 | 122.6944 | 122.6486 | -0.054932 | 122.9828 | 122.8912 | 0.24261 | -0.091553 | 123.1018 | 123.0103 | 122.9324 | -0.44861 | 123.0423 | 123.0057 | 123.0057 | -0.44861
4938.4688 | 123.1934 | -122.8546 | 0.18768 | -0.16083 | 0.032791 | 0.006366 | 0.011954 | -0.009252 | -0.0054752 | -0.010361 | -0.17265 | -0.015118 | -0.0068936 | -0.0024032 | 0.0032535 | -0.01828 | 0.23346 | 0.27008 | 0.20142 | 0.19226 | 0.36163 | 0.036621 | -0.15564 | 0.20599 | 0.29297 | 0.15106 | 0.2655 | 0.24261 | -0.059509 | -0.09613 | 122.8912 | 122.699 | 0.17395 | 123.1247 | 123.0469 | 0.3479 | 0.045776 | 122.7951 | 122.7585 | 0.07782 | 123.0606 | 123.0057 | 0.24719 | 0.054932 | 123.2162 | 123.0881 | 123.056 | -0.34332 | 123.1201 | 123.0972 | 123.1476 | -0.28381
4940.1562 | 123.2346 | -122.8271 | 0.16479 | -0.092163 | 0.031296 | 0.007434 | 0.010886 | -0.0096792 | -0.00163 | -0.0086517 | -0.10399 | -0.015545 | -0.0051846 | -0.0017624 | 0.0026125 | -0.016998 | 0.19226 | 0.21515 | 0.1831 | 0.16937 | 0.36163 | 0.022888 | -0.13275 | 0.19226 | 0.25635 | 0.12817 | 0.24719 | 0.20599 | -0.086975 | -0.11902 | 122.85 | 122.6944 | 0.19684 | 123.0423 | 122.9965 | 0.30212 | 0.027466 | 122.7402 | 122.7081 | 0.082397 | 123.0194 | 122.9553 | 0.24719 | 0.041199 | 123.1888 | 123.0194 | 123.0103 | -0.29755 | 123.0743 | 123.0331 | 123.0835 | -0.28381
4941.8438 | 123.1567 | -122.8638 | 0.20142 | 0.19012 | 0.033859 | 0.0070068 | 0.0061865 | -0.0096792 | 0.001788 | -0.0073701 | 0.13252 | -0.011273 | -0.0090298 | 0.00080099 | 0.0081667 | -0.018707 | 0.068665 | 0 | -0.036621 | -0.013733 | 0.25635 | -0.12817 | -0.27924 | 0.10529 | 0.07782 | -0.022888 | 0.16937 | 0.15106 | -0.1831 | -0.23346 | 122.7356 | 122.5845 | 0.054932 | 122.8638 | 122.85 | 0.2655 | -0.13275 | 122.6807 | 122.6303 | -0.032043 | 122.9691 | 122.8409 | 0.21057 | -0.050354 | 123.1201 | 122.9324 | 122.8271 | -0.48065 | 123.0331 | 123.0148 | 122.9416 | -0.43488
4943.5469 | 123.1888 | -122.8775 | 0.19684 | -0.22186 | 0.034287 | 0.009143 | 0.0098181 | -0.0098928 | -0.004407 | -0.0075837 | -0.15739 | -0.013409 | -0.00668 | -0.0051804 | 0.0047489 | -0.019134 | 0.21973 | 0.26093 | 0.1831 | 0.19684 | 0.37994 | 0.036621 | -0.12817 | 0.17853 | 0.26093 | 0.10529 | 0.24719 | 0.23804 | -0.082397 | -0.12817 | 122.9141 | 122.7493 | 0.18311 | 123.1384 | 123.0743 | 0.32501 | 0.022889 | 122.7951 | 122.7493 | 0.050354 | 123.056 | 122.9828 | 0.23346 | 0.041199 | 123.2574 | 123.0972 | 123.0606 | -0.32501 | 123.1247 | 123.1155 | 123.1384 | -0.32501
4945.2812 | 123.2117 | -122.8775 | 0.19226 | -0.26764 | 0.033859 | 0.0078614 | 0.010032 | -0.0060476 | -0.00077538 | -0.0086517 | -0.28709 | -0.013623 | -0.0062528 | -0.00048061 | 0.0045351 | -0.015289 | 0.13733 | 0.11444 | 0.068665 | 0.11444 | 0.42572 | 0.004578 | -0.15106 | 0.091553 | 0.1236 | 0 | 0.32501 | 0.27008 | -0.10071 | -0.12817 | 122.8821 | 122.7264 | 0.23346 | 122.9919 | 122.9919 | 0.2655 | -0.054932 | 122.7768 | 122.7493 | 0.13275 | 122.9691 | 122.8775 | 0.12817 | 0.07782 | 123.3032 | 123.0148 | 122.9462 | -0.34332 | 123.2025 | 123.1476 | 123.0011 | -0.32044
4946.9688 | 123.1934 | -122.8592 | 0.1831 | 0.0070193 | 0.030441 | 0.0065796 | 0.0087499 | -0.011815 | -0.004407 | -0.0097199 | 0.010452 | -0.013196 | -0.008389 | -0.0026168 | 0.0049625 | -0.014862 | 0.10071 | 0.11902 | 0.09613 | 0.091553 | 0.33417 | -0.013733 | -0.1831 | 0.1236 | 0.17853 | 0.073242 | 0.22888 | 0.19684 | -0.12817 | -0.16479 | 122.8455 | 122.6761 | 0.15106 | 122.9782 | 122.9507 | 0.27466 | -0.082397 | 122.731 | 122.6944 | 0.045777 | 122.9828 | 122.9324 | 0.23804 | 0.013733 | 123.1934 | 122.9599 | 122.9553 | -0.36621 | 123.0881 | 123.056 | 123.0377 | -0.3479
4948.6875 | 123.1155 | -122.8683 | 0.2243 | 0.060425 | 0.030228 | 0.009784 | 0.0064001 | -0.0090384 | -0.0031254 | -0.0099335 | 0.056228 | -0.015759 | -0.0075344 | -0.0017624 | 0.0036807 | -0.01593 | 0.10986 | 0.11902 | 0.059509 | 0.059509 | 0.29755 | -0.032043 | -0.17853 | 0.1236 | 0.15106 | 0.064087 | 0.21515 | 0.1831 | -0.12817 | -0.17853 | 122.8363 | 122.6898 | 0.073242 | 122.9874 | 122.9279 | 0.23804 | -0.11444 | 122.7402 | 122.6898 | -0.009155 | 122.9919 | 122.9324 | 0.24261 | -0.041199 | 123.1659 | 122.9782 | 122.9279 | -0.40283 | 123.0835 | 123.0515 | 123.0194 | -0.40283
4950.3906 | 123.111 | -122.8912 | 0.21973 | 0.014648 | 0.037277 | 0.0050842 | 0.0091773 | -0.008611 | 0.0064876 | -0.0054475 | -0.020065 | -0.011059 | -0.00668 | -0.001976 | 0.010303 | -0.01828 | 0.091553 | -0.018311 | -0.073242 | 0.004578 | 0.30212 | -0.10986 | -0.27924 | -0.009155 | -0.018311 | -0.16022 | 0.19226 | 0.18768 | -0.20599 | -0.24719 | 122.7814 | 122.612 | 0.082397 | 122.8729 | 122.8958 | 0.28381 | -0.12817 | 122.6852 | 122.644 | -0.027466 | 122.8821 | 122.731 | 0.086975 | -0.032044 | 123.1934 | 122.9828 | 122.818 | -0.49896 | 123.0835 | 123.0789 | 122.8729 | -0.46692
4952.1094 | 123.1705 | -122.8638 | 0.21057 | -0.054016 | 0.037064 | 0.0059388 | 0.0076819 | -0.0073294 | 0.003497 | -0.0063019 | -0.16502 | -0.012341 | -0.0058254 | -0.0030442 | 0.0098757 | -0.017852 | 0.14648 | 0.091553 | 0.009155 | 0.073242 | 0.31586 | -0.073242 | -0.22888 | 0.091553 | 0.11444 | -0.050354 | 0.2243 | 0.21057 | -0.17395 | -0.19684 | 122.7905 | 122.6349 | 0.10529 | 122.9553 | 122.937 | 0.30212 | -0.064087 | 122.6898 | 122.6669 | 0.013733 | 122.9553 | 122.8134 | 0.14648 | 0 | 123.1796 | 123.0103 | 122.8729 | -0.43945 | 123.0881 | 123.0743 | 122.9782 | -0.40741
4953.7969 | 123.2071 | -122.8821 | 0.1831 | -0.11505 | 0.037705 | 0.0040162 | 0.010245 | -0.0083974 | 0.003497 | -0.0080109 | -0.15739 | -0.011273 | -0.0039028 | -0.0011216 | 0.0060305 | -0.018707 | 0.11902 | 0.10986 | 0.018311 | 0.07782 | 0.34332 | -0.054932 | -0.2243 | 0.068665 | 0.11444 | -0.059509 | 0.21973 | 0.19226 | -0.17395 | -0.21515 | 122.8271 | 122.6578 | 0.16022 | 122.9919 | 122.9599 | 0.30212 | -0.064086 | 122.7081 | 122.6669 | 0.036622 | 122.9507 | 122.8226 | 0.15564 | 0.009156 | 123.2254 | 123.0011 | 122.9004 | -0.40741 | 123.1018 | 123.0743 | 122.9965 | -0.39825
4955.5469 | 123.143 | -122.8775 | 0.2243 | 0.11383 | 0.037705 | 0.007434 | 0.0074683 | -0.01032 | 0.0011472 | -0.0073701 | 0.15541 | -0.012341 | -0.0075344 | -0.0034714 | 0.0068851 | -0.018921 | 0.004578 | 0 | -0.064087 | -0.032043 | 0.27466 | -0.10071 | -0.29297 | 0.045776 | 0.068665 | -0.059509 | 0.17853 | 0.11902 | -0.20142 | -0.23804 | 122.7768 | 122.5845 | 0.050354 | 122.8775 | 122.8455 | 0.26093 | -0.21973 | 122.6761 | 122.6395 | -0.045776 | 122.9233 | 122.818 | 0.17853 | -0.10529 | 123.1522 | 122.8821 | 122.8134 | -0.51727 | 123.056 | 122.9965 | 122.9462 | -0.46234
4957.2344 | 123.1384 | -122.8958 | 0.20142 | 0.12146 | 0.035996 | 0.0044434 | 0.0096045 | -0.011175 | 0.0015744 | -0.0082245 | 0.079117 | -0.0097775 | -0.0034756 | -0.00069421 | 0.0038943 | -0.017212 | -0.009155 | -0.027466 | -0.073242 | -0.032043 | 0.27466 | -0.11902 | -0.29297 | 0 | 0.009155 | -0.09613 | 0.20599 | 0.17853 | -0.19226 | -0.24261 | 122.7768 | 122.6028 | 0.073242 | 122.8683 | 122.8638 | 0.26093 | -0.21057 | 122.7036 | 122.6532 | 0.004578 | 122.8958 | 122.7997 | 0.14649 | -0.022888 | 123.1705 | 122.8867 | 122.8226 | -0.49438 | 123.1018 | 123.0743 | 122.905 | -0.44403
4958.9219 | 123.2208 | -122.85 | 0.17853 | -0.19897 | 0.037277 | 0.0065796 | 0.0089635 | -0.0069022 | -0.00013458 | -0.0086517 | -0.16502 | -0.0099911 | -0.0058254 | -0.0032578 | 0.0056033 | -0.017639 | 0.09613 | 0.10986 | 0.036621 | 0.10529 | 0.37079 | -0.027466 | -0.20599 | 0.064087 | 0.13275 | -0.032043 | 0.24719 | 0.21515 | -0.15106 | -0.21057 | 122.8226 | 122.644 | 0.19226 | 122.9599 | 122.9553 | 0.31128 | -0.082398 | 122.699 | 122.6395 | 0.068664 | 122.9141 | 122.818 | 0.17853 | 0.036621 | 123.2208 | 122.9462 | 122.8867 | -0.38452 | 123.0972 | 123.0652 | 122.9828 | -0.3891
4960.625 | 123.1522 | -122.8592 | 0.21057 | 0.1825 | 0.037491 | 0.0087158 | 0.0085363 | -0.0077566 | -0.0018436 | -0.0067291 | 0.15541 | -0.010846 | -0.0058254 | -0.0017624 | 0.0051761 | -0.017425 | 0.009155 | 0.018311 | -0.045776 | 0 | 0.24719 | -0.10529 | -0.24719 | 0.07782 | 0.11902 | -0.009155 | 0.17395 | 0.12817 | -0.17395 | -0.21973 | 122.7539 | 122.612 | 0.036621 | 122.8775 | 122.8592 | 0.24719 | -0.20142 | 122.6852 | 122.6395 | -0.036621 | 122.937 | 122.85 | 0.21057 | -0.082397 | 123.1064 | 122.8683 | 122.8134 | -0.45776 | 123.0331 | 122.9874 | 122.9782 | -0.4303
4962.3281 | 123.1522 | -122.8775 | 0.22888 | 0.12909 | 0.036636 | 0.0057252 | 0.0089635 | -0.009252 | 0.001788 | -0.0075837 | 0.11726 | -0.010418 | -0.007748 | -0.003685 | 0.0073123 | -0.017852 | -0.022888 | -0.059509 | -0.10071 | -0.036621 | 0.2655 | -0.13733 | -0.28839 | -0.013733 | 0 | -0.10986 | 0.20142 | 0.16479 | -0.21515 | -0.24261 | 122.7402 | 122.5891 | 0.036621 | 122.818 | 122.8409 | 0.25177 | -0.25177 | 122.6624 | 122.6349 | -0.027466 | 122.8638 | 122.7676 | 0.13275 | -0.064087 | 123.143 | 122.8546 | 122.7768 | -0.51727 | 123.0789 | 123.0423 | 122.8775 | -0.4715
4964.0469 | 123.0789 | -122.8958 | 0.21057 | 0.11383 | 0.034714 | 0.0078614 | 0.0085363 | -0.009252 | -0.0065434 | -0.0077973 | 0.22408 | -0.013836 | -0.0062528 | -0.0032578 | 0.0036807 | -0.014007 | 0.073242 | 0.11444 | 0.082397 | 0.050354 | 0.25177 | -0.068665 | -0.2243 | 0.10071 | 0.15106 | 0.045776 | 0.17853 | 0.17853 | -0.15106 | -0.17853 | 122.8271 | 122.6715 | 0.041199 | 123.0103 | 122.9462 | 0.27466 | -0.13733 | 122.7448 | 122.7173 | -0.032043 | 122.9965 | 122.9416 | 0.2243 | -0.032043 | 123.1476 | 122.9691 | 122.9782 | -0.43488 | 123.0743 | 123.0743 | 123.0469 | -0.3891
4965.7344 | 123.1476 | -122.8775 | 0.21973 | 0.1062 | 0.037064 | 0.0052978 | 0.0081091 | -0.011388 | 0.0028562 | -0.0071563 | 0.12489 | -0.011487 | -0.0062528 | -0.0013352 | 0.0081667 | -0.018066 | 0.013733 | -0.064087 | -0.09613 | -0.032043 | 0.27466 | -0.14648 | -0.3067 | -0.013733 | -0.018311 | -0.10986 | 0.21515 | 0.15564 | -0.21515 | -0.23346 | 122.731 | 122.5708 | 0.054931 | 122.8134 | 122.8455 | 0.27466 | -0.20599 | 122.6624 | 122.644 | -0.004578 | 122.8638 | 122.7676 | 0.1236 | -0.064087 | 123.1522 | 122.8912 | 122.7814 | -0.52643 | 123.0927 | 123.0331 | 122.8592 | -0.45319
4967.4219 | 123.1522 | -122.8638 | 0.21973 | -0.061646 | 0.035782 | 0.0078614 | 0.010032 | -0.010534 | 0.0015744 | -0.0058747 | -0.11925 | -0.014264 | -0.0058254 | -0.0015488 | 0.0056033 | -0.018921 | 0.10529 | 0.10071 | -0.009155 | 0.054932 | 0.31586 | -0.054932 | -0.24719 | 0.068665 | 0.091553 | -0.068665 | 0.21057 | 0.20142 | -0.17853 | -0.21515 | 122.8088 | 122.6166 | 0.09613 | 122.9645 | 122.9187 | 0.30212 | -0.11444 | 122.6852 | 122.6486 | -0.009156 | 122.9324 | 122.7951 | 0.14648 | -0.018311 | 123.1796 | 122.9691 | 122.8546 | -0.46692 | 123.0743 | 123.0652 | 122.9553 | -0.43488
4969.1406 | 123.2391 | -122.8638 | 0.20142 | -0.18372 | 0.034714 | 0.007434 | 0.010886 | -0.0079702 | -0.00077538 | -0.0092927 | -0.2108 | -0.011059 | -0.0079618 | -0.0011216 | 0.0053897 | -0.017212 | 0.09613 | 0.09613 | 0.027466 | 0.10986 | 0.37537 | -0.022888 | -0.16937 | 0.050354 | 0.14191 | -0.022888 | 0.2655 | 0.25177 | -0.12817 | -0.17853 | 122.8409 | 122.6944 | 0.17395 | 122.9599 | 122.9736 | 0.27924 | -0.10529 | 122.7356 | 122.6852 | 0.064087 | 122.9141 | 122.8409 | 0.15564 | 0.050354 | 123.2391 | 122.9599 | 122.8912 | -0.37079 | 123.1293 | 123.1155 | 123.0057 | -0.37994
4970.8281 | 123.2529 | -122.85 | 0.17853 | -0.16083 | 0.037491 | 0.006366 | 0.012595 | -0.0096792 | -0.00098918 | -0.0086517 | -0.20317 | -0.013196 | -0.0017666 | -0.0017624 | 0.0023989 | -0.016571 | 0.09613 | 0.11902 | 0.041199 | 0.10986 | 0.37994 | -0.009155 | -0.17853 | 0.054932 | 0.13275 | -0.022888 | 0.28381 | 0.23346 | -0.14648 | -0.17395 | 122.8409 | 122.6715 | 0.20142 | 122.9691 | 122.9599 | 0.28839 | -0.082398 | 122.7036 | 122.6761 | 0.10528 | 122.905 | 122.8271 | 0.15106 | 0.054931 | 123.23 | 122.9462 | 122.8912 | -0.35706 | 123.1338 | 123.0835 | 122.9828 | -0.35248
4972.5156 | 123.2483 | -122.8592 | 0.19226 | -0.18372 | 0.035568 | 0.0061524 | 0.010459 | -0.010534 | -0.0018436 | -0.0086517 | -0.2108 | -0.012127 | -0.0045438 | 0.00016019 | 0.0045351 | -0.017639 | 0.09613 | 0.11444 | 0.036621 | 0.10986 | 0.36621 | -0.009155 | -0.18768 | 0.045776 | 0.1236 | -0.027466 | 0.28839 | 0.23346 | -0.14648 | -0.21515 | 122.85 | 122.6715 | 0.17395 | 122.9736 | 122.9691 | 0.29755 | -0.096131 | 122.7127 | 122.644 | 0.09613 | 122.905 | 122.8317 | 0.18768 | 0.041198 | 123.2254 | 122.9553 | 122.8958 | -0.37994 | 123.1476 | 123.0927 | 122.9828 | -0.40741
4974.2031 | 123.1796 | -122.8546 | 0.18768 | -0.27527 | 0.034073 | 0.0070068 | 0.013236 | -0.010747 | -0.0039798 | -0.010147 | -0.17265 | -0.014264 | -0.0043302 | -0.00069421 | 0.0013309 | -0.017639 | 0.11902 | 0.21515 | 0.12817 | 0.15106 | 0.40283 | 0.004578 | -0.13733 | 0.086975 | 0.18768 | 0.036621 | 0.31586 | 0.2655 | -0.086975 | -0.14648 | 122.8592 | 122.7173 | 0.21515 | 123.0698 | 123.0057 | 0.28839 | -0.068664 | 122.7676 | 122.7081 | 0.12817 | 122.9416 | 122.8912 | 0.18311 | 0.07782 | 123.2574 | 122.9736 | 122.9828 | -0.32501 | 123.1705 | 123.1201 | 123.0423 | -0.33417
4975.8906 | 123.1842 | -122.8363 | 0.20599 | -0.16846 | 0.033646 | 0.0057252 | 0.012382 | -0.0077566 | -0.007825 | -0.0097199 | -0.12688 | -0.014477 | -0.0056118 | -0.0011216 | 0.00026273 | -0.01593 | 0.14648 | 0.23346 | 0.16937 | 0.16937 | 0.36163 | 0.032043 | -0.13733 | 0.14191 | 0.26093 | 0.11444 | 0.27924 | 0.25635 | -0.086975 | -0.13733 | 122.8683 | 122.699 | 0.15564 | 123.0698 | 123.0057 | 0.3067 | -0.05951 | 122.7493 | 122.699 | 0.073242 | 122.9782 | 122.9507 | 0.25177 | 0.050354 | 123.1979 | 122.9828 | 123.0057 | -0.34332 | 123.1155 | 123.0927 | 123.0972 | -0.34332
4977.5938 | 123.1064 | -122.8867 | 0.21057 | 0.075684 | 0.0298 | 0.008075 | 0.0081091 | -0.011175 | -0.0046206 | -0.011215 | 0.071487 | -0.014477 | -0.009457 | -0.0028306 | 0.0036807 | -0.017212 | 0.073242 | 0.11444 | 0.064087 | 0.054932 | 0.30212 | -0.041199 | -0.21057 | 0.091553 | 0.14648 | 0.064087 | 0.20599 | 0.17395 | -0.11444 | -0.16479 | 122.8455 | 122.6761 | 0.091553 | 123.0011 | 122.9416 | 0.2655 | -0.13733 | 122.7722 | 122.7219 | -0.004577 | 122.9782 | 122.9507 | 0.22888 | -0.036621 | 123.1888 | 122.9599 | 122.9507 | -0.42114 | 123.0927 | 123.0606 | 123.0331 | -0.37537
4979.2812 | 123.2346 | -122.85 | 0.17853 | -0.22186 | 0.037491 | 0.0082886 | 0.010459 | -0.0066884 | -0.00077538 | -0.010788 | -0.22606 | -0.014691 | -0.0047574 | -0.0021896 | 0.0045351 | -0.020843 | 0.10986 | 0.091553 | 0.032043 | 0.10529 | 0.40741 | -0.018311 | -0.20599 | 0.054932 | 0.1236 | -0.022888 | 0.3067 | 0.24719 | -0.14191 | -0.16937 | 122.8317 | 122.644 | 0.22888 | 122.9416 | 122.9553 | 0.31128 | -0.068665 | 122.7081 | 122.6807 | 0.12817 | 122.905 | 122.8271 | 0.14649 | 0.068664 | 123.2574 | 122.9599 | 122.8821 | -0.38452 | 123.1567 | 123.0972 | 122.9736 | -0.3479
4981.0312 | 123.1613 | -122.8775 | 0.17395 | -0.00061023 | 0.0345 | 0.010425 | 0.0070409 | -0.009252 | -0.0065434 | -0.011642 | 0.056228 | -0.014691 | -0.0075344 | -0.0034714 | 0.00090353 | -0.014435 | 0.054932 | 0.12817 | 0.09613 | 0.10071 | 0.32501 | -0.013733 | -0.20599 | 0.09613 | 0.14648 | 0.073242 | 0.25177 | 0.18768 | -0.14191 | -0.16937 | 122.8638 | 122.6715 | 0.15106 | 123.0057 | 122.9782 | 0.3067 | -0.11902 | 122.7356 | 122.7081 | 0.07782 | 122.9736 | 122.9507 | 0.24261 | 0.013733 | 123.2025 | 122.9324 | 122.9736 | -0.37994 | 123.1293 | 123.0652 | 123.024 | -0.34332
4982.7344 | 123.0972 | -122.8455 | 0.21057 | 0.14435 | 0.0345 | 0.0057252 | 0.0068273 | -0.009252 | -0.00077538 | -0.0082245 | 0.14015 | -0.012768 | -0.0073208 | -0.0017624 | 0.0030399 | -0.017425 | 0.091553 | 0.11444 | 0.054932 | 0.064087 | 0.25177 | -0.07782 | -0.21973 | 0.10986 | 0.11902 | 0.032043 | 0.19226 | 0.17853 | -0.12817 | -0.1831 | 122.7676 | 122.6257 | 0.041199 | 122.9599 | 122.9095 | 0.28381 | -0.11902 | 122.7173 | 122.6624 | -0.01831 | 122.9553 | 122.8775 | 0.21515 | -0.032043 | 123.0972 | 122.937 | 122.9004 | -0.4303 | 123.0377 | 123.024 | 122.9645 | -0.39368
4984.4844 | 123.2529 | -122.85 | 0.17395 | -0.17609 | 0.038345 | 0.0050842 | 0.0085363 | -0.0090384 | 0.0022152 | -0.0088653 | -0.27184 | -0.012127 | -0.006039 | -0.00048061 | 0.0053897 | -0.02063 | 0.14191 | 0.10071 | 0.032043 | 0.10071 | 0.37994 | -0.009155 | -0.18768 | 0.068665 | 0.10529 | -0.041199 | 0.28381 | 0.25635 | -0.13275 | -0.1831 | 122.8409 | 122.6624 | 0.20599 | 122.9507 | 122.9507 | 0.28839 | -0.032043 | 122.7173 | 122.6669 | 0.10986 | 122.9187 | 122.8088 | 0.14191 | 0.082398 | 123.23 | 122.9919 | 122.8821 | -0.36163 | 123.1338 | 123.1064 | 122.9553 | -0.35706
4986.1719 | 123.2254 | -122.8226 | 0.19226 | -0.19897 | 0.035568 | 0.0055114 | 0.0098181 | -0.0071158 | 0.003497 | -0.0069427 | -0.22606 | -0.012341 | -0.0056118 | -0.00090781 | 0.0058169 | -0.02127 | 0.11444 | 0.10071 | 0.013733 | 0.09613 | 0.36621 | -0.036621 | -0.18768 | 0.07782 | 0.1236 | -0.036621 | 0.26093 | 0.21515 | -0.15106 | -0.20142 | 122.7859 | 122.6349 | 0.17395 | 122.9233 | 122.9187 | 0.28381 | -0.07782 | 122.6715 | 122.6212 | 0.068664 | 122.9004 | 122.7859 | 0.1648 | 0.022888 | 123.1888 | 122.937 | 122.8363 | -0.37994 | 123.0835 | 123.0377 | 122.9462 | -0.39368
4987.875 | 123.1338 | -122.8775 | 0.20599 | 0.14435 | 0.034073 | 0.0050842 | 0.0061865 | -0.0079702 | 0.00071982 | -0.0090791 | 0.18593 | -0.012555 | -0.0081754 | -0.001976 | 0.0077395 | -0.019134 | 0.082397 | 0.091553 | 0.027466 | 0.045776 | 0.24719 | -0.086975 | -0.25177 | 0.086975 | 0.10529 | 0.004578 | 0.15106 | 0.12817 | -0.19684 | -0.22888 | 122.7905 | 122.6257 | 0.041198 | 122.9691 | 122.9233 | 0.29755 | -0.1236 | 122.6807 | 122.6486 | -0.054932 | 122.9645 | 122.8821 | 0.23346 | -0.07782 | 123.1247 | 122.9599 | 122.905 | -0.45776 | 123.0286 | 123.0057 | 122.9828 | -0.43488
4989.5781 | 123.2391 | -122.8455 | 0.19684 | -0.27527 | 0.037491 | 0.008075 | 0.011954 | -0.0098928 | -0.00077538 | -0.0080109 | -0.21843 | -0.012127 | -0.0047574 | -0.0015488 | 0.0043215 | -0.018066 | 0.11444 | 0.11902 | 0.054932 | 0.10071 | 0.41657 | 0.009155 | -0.16937 | 0.050354 | 0.11444 | -0.027466 | 0.28381 | 0.2655 | -0.13275 | -0.19226 | 122.8546 | 122.6761 | 0.21973 | 122.9645 | 122.9462 | 0.27008 | -0.082397 | 122.7127 | 122.6532 | 0.086975 | 122.8958 | 122.818 | 0.16479 | 0.068665 | 123.262 | 122.9599 | 122.9004 | -0.36621 | 123.1293 | 123.111 | 122.9599 | -0.3891
4991.2812 | 123.0972 | -122.8867 | 0.21515 | 0.15198 | 0.033218 | 0.0065796 | 0.0059729 | -0.0090384 | -0.0029118 | -0.0084381 | 0.15541 | -0.01405 | -0.0073208 | -0.0017624 | 0.0049625 | -0.017212 | 0.073242 | 0.11444 | 0.054932 | 0.054932 | 0.2243 | -0.07782 | -0.24719 | 0.11902 | 0.12817 | 0.032043 | 0.17395 | 0.15106 | -0.16022 | -0.21057 | 122.8088 | 122.6395 | 0.009155 | 123.0011 | 122.9416 | 0.30212 | -0.14191 | 122.7264 | 122.6761 | -0.041199 | 123.0057 | 122.9187 | 0.24261 | -0.064087 | 123.111 | 122.9599 | 122.9416 | -0.46234 | 123.0606 | 123.0377 | 123.0148 | -0.42572
4993.0312 | 123.2208 | -122.8271 | 0.18768 | -0.13794 | 0.03215 | 0.0048706 | 0.010673 | -0.0088248 | -0.0054752 | -0.011856 | -0.11162 | -0.014905 | -0.0068936 | -0.0045394 | 0.0021853 | -0.018493 | 0.19684 | 0.25635 | 0.20142 | 0.1831 | 0.3479 | 0.022888 | -0.14191 | 0.1831 | 0.27008 | 0.13275 | 0.25635 | 0.2243 | -0.073242 | -0.11444 | 122.85 | 122.6852 | 0.16022 | 123.0835 | 123.0103 | 0.32501 | 0.009155 | 122.7539 | 122.7127 | 0.068665 | 123.0103 | 122.9599 | 0.24719 | 0.036621 | 123.175 | 123.024 | 123.0286 | -0.32959 | 123.0835 | 123.0515 | 123.0972 | -0.30212
4994.7188 | 123.143 | -122.8867 | 0.21057 | 0.052795 | 0.033005 | 0.0067932 | 0.0083227 | -0.0081838 | -0.0039798 | -0.0090791 | 0.04097 | -0.013836 | -0.0064664 | -0.0011216 | 0.0038943 | -0.016357 | 0.082397 | 0.11444 | 0.09613 | 0.082397 | 0.32044 | -0.036621 | -0.19684 | 0.10071 | 0.14648 | 0.050354 | 0.2243 | 0.19226 | -0.10986 | -0.17395 | 122.85 | 122.6898 | 0.10986 | 123.0011 | 122.9691 | 0.27924 | -0.12817 | 122.7768 | 122.7127 | 0.013733 | 122.9874 | 122.937 | 0.2243 | -0.01831 | 123.2071 | 122.9691 | 122.9828 | -0.40741 | 123.111 | 123.0789 | 123.0331 | -0.38452
4996.4219 | 123.23 | -122.8546 | 0.19684 | -0.092163 | 0.031082 | 0.010852 | 0.0096045 | -0.008611 | -0.0052616 | -0.010361 | -0.073471 | -0.014905 | -0.007748 | -0.0013352 | 0.00026273 | -0.016571 | 0.17853 | 0.20599 | 0.15564 | 0.16479 | 0.3479 | 0.013733 | -0.14648 | 0.17395 | 0.25177 | 0.15106 | 0.26093 | 0.25635 | -0.086975 | -0.11902 | 122.8683 | 122.7081 | 0.15106 | 123.0606 | 123.0194 | 0.31128 | -0.01831 | 122.7676 | 122.7356 | 0.064087 | 123.0286 | 123.0057 | 0.27008 | 0.05951 | 123.2025 | 123.0331 | 123.0103 | -0.34332 | 123.1155 | 123.111 | 123.1064 | -0.31586
4998.125 | 123.0881 | -122.8821 | 0.2243 | 0.098572 | 0.031937 | 0.0070068 | 0.0029821 | -0.010747 | -0.00077538 | -0.010788 | 0.13252 | -0.012768 | -0.0086026 | -0.0024032 | 0.0058169 | -0.015503 | 0.11444 | 0.11902 | 0.073242 | 0.041199 | 0.25635 | -0.064087 | -0.23346 | 0.1236 | 0.10529 | 0.009155 | 0.1831 | 0.15106 | -0.16937 | -0.20599 | 122.818 | 122.6486 | 0.032044 | 123.0011 | 122.9233 | 0.27466 | -0.10986 | 122.7127 | 122.6761 | -0.041199 | 123.0057 | 122.8912 | 0.21515 | -0.073242 | 123.1384 | 122.9965 | 122.9553 | -0.45776 | 123.0652 | 123.0331 | 122.9874 | -0.4303
4999.8125 | 123.0835 | -122.8867 | 0.19684 | 0.12909 | 0.033859 | 0.0076478 | 0.0055457 | -0.010534 | -0.002698 | -0.0084381 | 0.063858 | -0.013196 | -0.008389 | -0.003685 | 0.0062441 | -0.018066 | 0.10529 | 0.09613 | 0.059509 | 0.050354 | 0.25177 | -0.068665 | -0.24261 | 0.1236 | 0.13275 | 0.050354 | 0.21515 | 0.18768 | -0.13275 | -0.17395 | 122.818 | 122.644 | 0.054932 | 122.9828 | 122.937 | 0.29297 | -0.091552 | 122.7539 | 122.7127 | 0.018311 | 123.0103 | 122.937 | 0.2243 | -0.009155 | 123.1384 | 122.9919 | 122.9462 | -0.43945 | 123.1018 | 123.0743 | 123.0194 | -0.37079
5001.5 | 123.1155 | -122.8775 | 0.21057 | 0.1825 | 0.035996 | 0.0050842 | 0.0061865 | -0.010534 | 0.0011472 | -0.0073701 | 0.102 | -0.013196 | -0.0062528 | -0.0045394 | 0.0058169 | -0.017639 | 0.10986 | 0.09613 | 0.045776 | 0.050354 | 0.22888 | -0.091553 | -0.2655 | 0.11902 | 0.14191 | 0.009155 | 0.16937 | 0.13733 | -0.17853 | -0.21973 | 122.7859 | 122.612 | 0.018311 | 122.9736 | 122.9279 | 0.31586 | -0.10071 | 122.699 | 122.6578 | -0.041198 | 122.9965 | 122.8867 | 0.22888 | -0.073242 | 123.1064 | 122.9874 | 122.9233 | -0.47607 | 123.0469 | 123.0148 | 123.0194 | -0.4303
5003.2188 | 123.2071 | -122.8409 | 0.1831 | -0.023499 | 0.030441 | -0.034436 | 0.0057593 | -0.011815 | -0.006116 | -0.0099335 | -0.020065 | -0.015545 | -0.0092434 | -0.0015488 | 0.0043215 | -0.017852 | 0.12817 | 0.12817 | 0.11444 | 0.10986 | 0.32044 | -0.004578 | -0.18768 | 0.14191 | 0.21515 | 0.10986 | 0.24261 | 0.2243 | -0.086975 | -0.13733 | 122.8363 | 122.6532 | 0.13733 | 122.9691 | 122.9507 | 0.29755 | -0.054931 | 122.7539 | 122.7036 | 0.05951 | 122.9828 | 122.9507 | 0.24719 | 0.041199 | 123.1613 | 122.9691 | 122.9553 | -0.37079 | 123.0835 | 123.0652 | 123.056 | -0.32043
5004.9688 | 123.2483 | -122.85 | 0.19684 | -0.21423 | 0.036209 | 0.0093566 | 0.010032 | -0.0081838 | 0.0022152 | -0.0073701 | -0.27184 | -0.012555 | -0.004971 | -0.0034714 | 0.0047489 | -0.02127 | 0.16479 | 0.07782 | 0.027466 | 0.09613 | 0.41657 | -0.022888 | -0.17395 | 0.07782 | 0.11902 | -0.036621 | 0.29755 | 0.24719 | -0.12817 | -0.17395 | 122.8271 | 122.6761 | 0.21973 | 122.9279 | 122.9462 | 0.27008 | -0.032043 | 122.7219 | 122.6761 | 0.10071 | 122.9279 | 122.8134 | 0.13733 | 0.050354 | 123.2666 | 123.0148 | 122.8775 | -0.37079 | 123.1476 | 123.0972 | 122.9691 | -0.37079
5006.7031 | 123.1796 | -122.8409 | 0.19684 | -0.2829 | 0.034287 | 0.0059388 | 0.010032 | -0.010534 | -0.0029118 | -0.0099335 | -0.25658 | -0.01405 | -0.0053982 | -0.0030442 | 0.0028263 | -0.017639 | 0.1831 | 0.2243 | 0.15106 | 0.16479 | 0.40283 | 0.009155 | -0.15564 | 0.10986 | 0.18768 | 0.036621 | 0.31128 | 0.27008 | -0.09613 | -0.15564 | 122.85 | 122.6852 | 0.20599 | 123.0652 | 123.0057 | 0.32044 | -0.013733 | 122.7448 | 122.6852 | 0.11444 | 122.9507 | 122.8775 | 0.19226 | 0.073243 | 123.2437 | 123.024 | 122.9919 | -0.35248 | 123.1522 | 123.111 | 123.0286 | -0.35248
5008.4844 | 123.1018 | -122.9004 | 0.22888 | 0.15198 | 0.0345 | 0.0076478 | 0.0081091 | -0.0090384 | 0.0013608 | -0.011002 | 0.10963 | -0.012555 | -0.007748 | -0.0021896 | 0.0056033 | -0.017639 | 0.10986 | 0.10529 | 0.064087 | 0.050354 | 0.23346 | -0.086975 | -0.25177 | 0.12817 | 0.14648 | 0.027466 | 0.16479 | 0.15106 | -0.16022 | -0.21057 | 122.8134 | 122.6486 | 0.004577 | 123.0057 | 122.9507 | 0.30212 | -0.11902 | 122.7402 | 122.6898 | -0.064087 | 123.0286 | 122.9279 | 0.23804 | -0.07782 | 123.1338 | 123.0103 | 122.9645 | -0.48065 | 123.0652 | 123.0515 | 123.0469 | -0.43945
5010.25 | 123.1384 | -122.8867 | 0.19226 | 0.19012 | 0.033432 | 0.0065796 | 0.0093909 | -0.007543 | 0.0020016 | -0.0082245 | 0.17067 | -0.0117 | -0.0058254 | -0.0013352 | 0.0045351 | -0.01828 | 0.086975 | 0.091553 | 0.032043 | 0.045776 | 0.22888 | -0.09613 | -0.26093 | 0.10529 | 0.1236 | 0.009155 | 0.14191 | 0.11444 | -0.20599 | -0.21515 | 122.7905 | 122.6257 | 0.036621 | 122.9782 | 122.9324 | 0.3067 | -0.10529 | 122.6807 | 122.6715 | -0.050354 | 122.9919 | 122.8958 | 0.2243 | -0.07782 | 123.1155 | 122.9736 | 122.9187 | -0.45319 | 123.0286 | 123.0011 | 123.0103 | -0.40741
5012.0156 | 123.1613 | -122.8867 | 0.20142 | 0.1825 | 0.034714 | 0.0070068 | 0.0074683 | -0.0083974 | -0.00013458 | -0.0084381 | 0.12489 | -0.012341 | -0.0096706 | -0.0030442 | 0.0068851 | -0.016143 | 0.07782 | 0.059509 | 0.009155 | 0.041199 | 0.23346 | -0.091553 | -0.2655 | 0.10071 | 0.11444 | -0.009155 | 0.15564 | 0.1236 | -0.17395 | -0.20599 | 122.7951 | 122.6212 | 0.032043 | 122.9462 | 122.9279 | 0.3067 | -0.1236 | 122.7127 | 122.6807 | -0.045776 | 122.9874 | 122.8775 | 0.19684 | -0.07782 | 123.1201 | 122.9645 | 122.8958 | -0.46692 | 123.0423 | 123.0103 | 123.0011 | -0.40741
5013.7812 | 123.1979 | -122.8775 | 0.17395 | -0.2066 | 0.033218 | 0.0065796 | 0.010673 | -0.0079702 | -0.002698 | -0.0092927 | -0.15739 | -0.013836 | -0.0064664 | -0.0032578 | 0.0030399 | -0.018066 | 0.21057 | 0.25177 | 0.19226 | 0.18768 | 0.37079 | 0.045776 | -0.13733 | 0.16479 | 0.27466 | 0.11902 | 0.26093 | 0.21515 | -0.09613 | -0.1236 | 122.9233 | 122.7402 | 0.19684 | 123.1293 | 123.0652 | 0.32501 | 0.036621 | 122.7814 | 122.7539 | 0.086975 | 123.0423 | 122.9965 | 0.24261 | 0.041199 | 123.2483 | 123.0881 | 123.0698 | -0.31128 | 123.1384 | 123.0927 | 123.1522 | -0.29755
5015.5312 | 123.2437 | -122.8867 | 0.20142 | -0.23712 | 0.037491 | 0.0061524 | 0.010459 | -0.012884 | -0.00013458 | -0.0092927 | -0.24895 | -0.01405 | -0.0058254 | -5.3406e-05 | 0.0064577 | -0.017639 | 0.1236 | 0.11444 | 0.064087 | 0.09613 | 0.41657 | 0 | -0.1831 | 0.07782 | 0.10071 | -0.032043 | 0.28381 | 0.24719 | -0.14191 | -0.16937 | 122.8867 | 122.7036 | 0.21515 | 123.0011 | 122.9828 | 0.27924 | -0.07782 | 122.7448 | 122.7173 | 0.082397 | 122.9645 | 122.8546 | 0.13733 | 0.045776 | 123.3032 | 123.0103 | 122.9507 | -0.38452 | 123.1705 | 123.1338 | 122.9874 | -0.37079
5017.2188 | 123.1064 | -122.9095 | 0.23346 | 0.0070193 | 0.038345 | -0.0011108 | 0.010032 | -0.0094656 | 0.0041378 | -0.0073701 | -0.042954 | -0.013623 | -0.0047574 | -0.0013352 | 0.0090213 | -0.021484 | 0.036621 | 0.032043 | -0.073242 | -0.009155 | 0.29297 | -0.086975 | -0.27924 | -0.009155 | 0.018311 | -0.12817 | 0.20142 | 0.17853 | -0.20142 | -0.25177 | 122.8226 | 122.6303 | 0.05951 | 122.9416 | 122.9004 | 0.27008 | -0.19684 | 122.7081 | 122.6578 | -0.032043 | 122.9004 | 122.7814 | 0.1236 | -0.054931 | 123.2025 | 122.9462 | 122.8363 | -0.5127 | 123.111 | 123.0881 | 122.9279 | -0.48523
5018.9531 | 123.1064 | -122.8821 | 0.19684 | 0.13672 | 0.031937 | 0.0078614 | 0.0087499 | -0.0083974 | -0.0041934 | -0.0073701 | 0.13252 | -0.014691 | -0.0073208 | -5.3406e-05 | 0.0041079 | -0.014862 | 0.07782 | 0.045776 | 0.082397 | 0.07782 | 0.27008 | -0.059509 | -0.21973 | 0.11444 | 0.15106 | 0.041199 | 0.2243 | 0.19226 | -0.1236 | -0.16937 | 122.8226 | 122.6624 | 0.073243 | 122.9279 | 122.9599 | 0.29755 | -0.11902 | 122.7585 | 122.7127 | 0.027466 | 122.9965 | 122.9233 | 0.21057 | -0.004577 | 123.1522 | 122.9599 | 122.9645 | -0.41657 | 123.1064 | 123.0743 | 123.0331 | -0.36621
5020.7031 | 123.0881 | -122.8867 | 0.21515 | 0.15198 | 0.033859 | 0.0076478 | 0.0061865 | -0.010961 | -0.0018436 | -0.0080109 | 0.12489 | -0.012768 | -0.0079618 | -0.0041122 | 0.0064577 | -0.017425 | 0.082397 | 0.11902 | 0.059509 | 0.054932 | 0.21973 | -0.091553 | -0.25635 | 0.10986 | 0.15564 | 0.032043 | 0.16022 | 0.14648 | -0.15106 | -0.21973 | 122.7951 | 122.6303 | 0.004578 | 123.0057 | 122.9416 | 0.31128 | -0.13275 | 122.7356 | 122.6669 | -0.054932 | 122.9965 | 122.9187 | 0.25177 | -0.068665 | 123.1064 | 122.9691 | 122.9462 | -0.4715 | 123.0469 | 123.0331 | 123.0423 | -0.43488
5022.4062 | 123.2346 | -122.85 | 0.17853 | -0.13794 | 0.033432 | 0.007434 | 0.012809 | -0.0096792 | -0.005048 | -0.011215 | -0.10399 | -0.015332 | -0.00668 | -0.0017624 | 0.0028263 | -0.016784 | 0.20142 | 0.24719 | 0.17853 | 0.16479 | 0.35248 | 0.032043 | -0.14191 | 0.20599 | 0.28839 | 0.17395 | 0.26093 | 0.2243 | -0.07782 | -0.1236 | 122.8821 | 122.7081 | 0.17395 | 123.0972 | 123.0148 | 0.3067 | 0.022888 | 122.7722 | 122.7264 | 0.082397 | 123.056 | 123.024 | 0.29755 | 0.045776 | 123.2025 | 123.0515 | 123.0286 | -0.32044 | 123.111 | 123.0743 | 123.1384 | -0.30212
5024.1562 | 123.1338 | -122.8775 | 0.21973 | -0.076904 | 0.035996 | 0.0042298 | 0.0081091 | -0.010961 | 0.0060604 | -0.0071563 | -0.15739 | -0.011487 | -0.004971 | -0.00026701 | 0.0068851 | -0.018707 | 0.13275 | 0.10071 | -0.004578 | 0.059509 | 0.31586 | -0.07782 | -0.23346 | 0.050354 | 0.086975 | -0.082397 | 0.23346 | 0.19226 | -0.17853 | -0.20599 | 122.7997 | 122.644 | 0.09613 | 122.9782 | 122.937 | 0.29297 | -0.086976 | 122.699 | 122.6715 | 0.013732 | 122.9279 | 122.7951 | 0.1236 | -0.027466 | 123.1934 | 123.0103 | 122.8729 | -0.45319 | 123.111 | 123.0698 | 122.9645 | -0.42572
5025.8594 | 123.1247 | -122.8775 | 0.21515 | 0.098572 | 0.036423 | 0.0048706 | 0.0078955 | -0.010534 | 0.00093342 | -0.0080109 | 0.063858 | -0.012341 | -0.0073208 | -0.00048061 | 0.0081667 | -0.019348 | -0.009155 | -0.027466 | -0.10986 | -0.022888 | 0.29755 | -0.12817 | -0.28381 | -0.009155 | -0.027466 | -0.12817 | 0.17853 | 0.15564 | -0.21973 | -0.27466 | 122.7493 | 122.5937 | 0.082397 | 122.85 | 122.8546 | 0.26092 | -0.2243 | 122.6578 | 122.6028 | -0.036621 | 122.8683 | 122.7493 | 0.14648 | -0.059509 | 123.175 | 122.8683 | 122.7676 | -0.49896 | 123.056 | 123.0331 | 122.85 | -0.48981
5027.625 | 123.2162 | -122.8592 | 0.18768 | -0.11505 | 0.037064 | 0.006366 | 0.0061865 | -0.007543 | 0.0039242 | -0.0058747 | -0.12688 | -0.0099911 | -0.0051846 | -0.0030442 | 0.0079531 | -0.019134 | 0.10071 | 0.13733 | 0.013733 | 0.068665 | 0.31586 | -0.054932 | -0.23346 | 0.073242 | 0.09613 | -0.054932 | 0.21057 | 0.17395 | -0.16937 | -0.21515 | 122.8043 | 122.6257 | 0.12817 | 122.9965 | 122.9279 | 0.30212 | -0.086975 | 122.6898 | 122.644 | 0.022888 | 122.9324 | 122.8043 | 0.16022 | -0.013733 | 123.175 | 122.9599 | 122.8729 | -0.42114 | 123.0698 | 123.0331 | 122.9553 | -0.40283
5029.3281 | 123.2254 | -122.818 | 0.17853 | -0.13031 | 0.032578 | 0.0072204 | 0.0098181 | -0.010961 | -0.0065434 | -0.0088653 | -0.11162 | -0.016186 | -0.004971 | -0.0024032 | -0.00037807 | -0.014862 | 0.12817 | 0.2655 | 0.21515 | 0.16479 | 0.35706 | 0.013733 | -0.12817 | 0.20599 | 0.30212 | 0.16937 | 0.24719 | 0.2243 | -0.073242 | -0.1236 | 122.8317 | 122.6898 | 0.17853 | 123.0835 | 122.9828 | 0.29297 | -0.050354 | 122.7448 | 122.6944 | 0.068664 | 123.024 | 122.9874 | 0.29297 | 0.045776 | 123.175 | 122.9462 | 123.0331 | -0.3067 | 123.0652 | 123.0423 | 123.1201 | -0.30212
5031.0156 | 123.23 | -122.8455 | 0.1831 | -0.11505 | 0.031082 | 0.006366 | 0.013877 | -0.01032 | -0.0071842 | -0.010788 | -0.073471 | -0.014905 | -0.0062528 | -0.005394 | 0.0013309 | -0.017212 | 0.16479 | 0.26093 | 0.18768 | 0.16937 | 0.35248 | 0.022888 | -0.13275 | 0.20142 | 0.26093 | 0.15564 | 0.25635 | 0.21515 | -0.07782 | -0.11902 | 122.8683 | 122.7127 | 0.16937 | 123.1064 | 123.0148 | 0.30212 | -0.01831 | 122.7676 | 122.7264 | 0.073243 | 123.0469 | 123.0011 | 0.27466 | 0.032044 | 123.1979 | 123.0103 | 123.0331 | -0.31586 | 123.1018 | 123.0606 | 123.1064 | -0.30212
5032.7188 | 123.1888 | -122.8546 | 0.20142 | -0.25238 | 0.034287 | 0.007434 | 0.0111 | -0.011388 | -0.0018436 | -0.010788 | -0.18791 | -0.012982 | -0.0064664 | -0.00048061 | 0.0056033 | -0.01828 | 0.1236 | 0.16937 | 0.09613 | 0.1236 | 0.40741 | -0.004578 | -0.16022 | 0.07782 | 0.14648 | 0.027466 | 0.31586 | 0.27008 | -0.11902 | -0.13733 | 122.85 | 122.6944 | 0.20599 | 123.024 | 122.9782 | 0.28381 | -0.07782 | 122.7356 | 122.7173 | 0.11444 | 122.9324 | 122.8821 | 0.16479 | 0.068665 | 123.262 | 122.9782 | 122.9507 | -0.36163 | 123.1705 | 123.1247 | 123.0011 | -0.33875
5034.4219 | 123.1293 | -122.8912 | 0.21515 | 0.014648 | 0.032791 | 0.0065796 | 0.0072547 | -0.010106 | -0.0029118 | -0.010361 | 0.056228 | -0.013836 | -0.0051846 | -0.0021896 | 0.0043215 | -0.015716 | 0.059509 | 0.14191 | 0.082397 | 0.07782 | 0.3067 | -0.045776 | -0.21515 | 0.10986 | 0.15106 | 0.059509 | 0.2243 | 0.20142 | -0.14191 | -0.17395 | 122.8455 | 122.6761 | 0.091553 | 123.0331 | 122.9691 | 0.29297 | -0.15564 | 122.7493 | 122.7173 | 0.009155 | 123.0011 | 122.9507 | 0.23346 | -0.013733 | 123.1979 | 122.9507 | 122.9736 | -0.4303 | 123.1155 | 123.0927 | 123.0423 | -0.3891
5036.1719 | 123.23 | -122.8409 | 0.16937 | -0.10742 | 0.032364 | 0.0076478 | 0.0089635 | -0.012029 | -0.0035526 | -0.0090791 | -0.12688 | -0.015332 | -0.0075344 | -0.0026168 | 0.0041079 | -0.018493 | 0.2243 | 0.29297 | 0.1831 | 0.1831 | 0.35248 | 0.027466 | -0.13733 | 0.20599 | 0.29755 | 0.15564 | 0.26093 | 0.24261 | -0.054932 | -0.10529 | 122.8683 | 122.7036 | 0.18311 | 123.1338 | 123.024 | 0.32043 | 0.054931 | 122.7859 | 122.7356 | 0.091552 | 123.0469 | 122.9965 | 0.26093 | 0.073242 | 123.1934 | 123.0652 | 123.024 | -0.3067 | 123.1018 | 123.0835 | 123.1384 | -0.27466
5037.8594 | 123.1064 | -122.9004 | 0.2243 | 0.022278 | 0.038773 | 0.004657 | 0.0046911 | -0.0096792 | 0.0047788 | -0.0080109 | -0.035324 | -0.012127 | -0.0068936 | -0.0030442 | 0.01073 | -0.019134 | 0.068665 | -0.018311 | -0.09613 | -0.009155 | 0.28381 | -0.10071 | -0.27008 | -0.027466 | -0.018311 | -0.15106 | 0.20142 | 0.17853 | -0.21057 | -0.25635 | 122.7997 | 122.6303 | 0.059509 | 122.8821 | 122.8912 | 0.26093 | -0.15564 | 122.6898 | 122.644 | -0.022888 | 122.8729 | 122.7493 | 0.10529 | -0.045776 | 123.1842 | 122.9691 | 122.8043 | -0.49439 | 123.1018 | 123.0789 | 122.8821 | -0.48065
5039.625 | 123.2437 | -122.8592 | 0.19226 | -0.19135 | 0.036209 | 0.0082886 | 0.0072547 | -0.010534 | 0.0013608 | -0.0075837 | -0.23369 | -0.011273 | -0.010312 | -0.0026168 | 0.0068851 | -0.018493 | 0.13275 | 0.10986 | 0.041199 | 0.10529 | 0.40741 | -0.018311 | -0.19226 | 0.082397 | 0.11902 | -0.036621 | 0.25177 | 0.21057 | -0.14648 | -0.20142 | 122.8409 | 122.6669 | 0.21515 | 122.9691 | 122.9645 | 0.29755 | -0.05951 | 122.7127 | 122.6578 | 0.059509 | 122.9416 | 122.8226 | 0.1648 | 0.01831 | 123.2666 | 122.9919 | 122.9004 | -0.38452 | 123.111 | 123.0698 | 122.9782 | -0.39368
5041.3906 | 123.2437 | -122.8409 | 0.17853 | -0.22186 | 0.034927 | 0.0076478 | 0.0096045 | -0.0096792 | -0.00034818 | -0.0092927 | -0.18791 | -0.011487 | -0.0075344 | -0.00048061 | 0.0038943 | -0.020416 | 0.1236 | 0.11444 | 0.041199 | 0.09613 | 0.40741 | -0.009155 | -0.1831 | 0.041199 | 0.12817 | -0.027466 | 0.28839 | 0.24261 | -0.14191 | -0.20142 | 122.8317 | 122.6578 | 0.22888 | 122.9553 | 122.937 | 0.27924 | -0.054932 | 122.699 | 122.6395 | 0.10986 | 122.8821 | 122.8134 | 0.17395 | 0.064087 | 123.2483 | 122.9645 | 122.8821 | -0.36163 | 123.1293 | 123.0835 | 122.9691 | -0.37994
5043.1562 | 123.0972 | -122.9141 | 0.21515 | 0.060425 | 0.037277 | 0.0070068 | 0.0070409 | -0.008611 | 0.0032834 | -0.0080109 | -0.020065 | -0.011273 | -0.0086026 | -0.0026168 | 0.0081667 | -0.016998 | 0.018311 | -0.054932 | -0.11444 | -0.032043 | 0.29297 | -0.10529 | -0.3067 | -0.050354 | -0.027466 | -0.14191 | 0.21515 | 0.17395 | -0.21973 | -0.23804 | 122.8088 | 122.6074 | 0.07782 | 122.8592 | 122.8821 | 0.27466 | -0.19684 | 122.6944 | 122.6761 | 0 | 122.8638 | 122.7722 | 0.09613 | -0.041199 | 123.2071 | 122.9324 | 122.7997 | -0.52185 | 123.1293 | 123.0881 | 122.8867 | -0.45319
5044.8594 | 123.1796 | -122.8775 | 0.16937 | 0.014648 | 0.033005 | 0.0095704 | 0.0089635 | -0.0083974 | -0.0076114 | -0.0099335 | 0.079117 | -0.012768 | -0.008389 | -0.003685 | 0.0019717 | -0.015075 | 0.082397 | 0.10529 | 0.086975 | 0.082397 | 0.32959 | -0.018311 | -0.1831 | 0.10071 | 0.17395 | 0.068665 | 0.25177 | 0.21973 | -0.11902 | -0.16937 | 122.8592 | 122.6944 | 0.16022 | 122.9828 | 122.9599 | 0.2655 | -0.086976 | 122.7585 | 122.7081 | 0.082397 | 122.9782 | 122.9462 | 0.23804 | 0.050354 | 123.2071 | 122.9599 | 122.9645 | -0.35248 | 123.1293 | 123.0972 | 123.0515 | -0.33875
5046.6094 | 123.1522 | -122.8271 | 0.19684 | 0.014648 | 0.031082 | 0.009784 | 0.010886 | -0.011602 | -0.0065434 | -0.010147 | 0.094375 | -0.013409 | -0.008389 | -0.0017624 | 0.0051761 | -0.014862 | 0.082397 | 0.10529 | 0.073242 | 0.091553 | 0.3067 | -0.013733 | -0.19684 | 0.10071 | 0.16937 | 0.068665 | 0.23804 | 0.20142 | -0.10529 | -0.15106 | 122.8134 | 122.6303 | 0.10986 | 122.9324 | 122.9187 | 0.28839 | -0.11444 | 122.7219 | 122.6761 | 0.041199 | 122.9279 | 122.8958 | 0.21973 | 0.004578 | 123.1338 | 122.9095 | 122.9004 | -0.39368 | 123.0652 | 123.0286 | 122.9965 | -0.3479
5048.2969 | 123.2437 | -122.8134 | 0.18768 | -0.099793 | 0.031723 | 0.010425 | 0.010245 | -0.0098928 | -0.0041934 | -0.010147 | -0.11162 | -0.012127 | -0.0081754 | -0.0032578 | 0.0017581 | -0.018921 | 0.21515 | 0.2243 | 0.19684 | 0.18768 | 0.35706 | 0.022888 | -0.15106 | 0.21057 | 0.27466 | 0.16937 | 0.26093 | 0.23346 | -0.068665 | -0.1236 | 122.8363 | 122.6624 | 0.16937 | 123.0377 | 123.0011 | 0.33874 | 0.027466 | 122.7448 | 122.6898 | 0.073242 | 123.024 | 122.9828 | 0.29297 | 0.045776 | 123.1705 | 123.0286 | 123.0103 | -0.33874 | 123.0743 | 123.0469 | 123.0881 | -0.31128
5050.0625 | 123.2346 | -122.85 | 0.1831 | -0.2066 | 0.03685 | 0.006366 | 0.010032 | -0.0096792 | 0.0030698 | -0.0090791 | -0.23369 | -0.011059 | -0.0045438 | -0.0011216 | 0.0083805 | -0.019989 | 0.16937 | 0.086975 | 0.036621 | 0.091553 | 0.37994 | -0.004578 | -0.19226 | 0.059509 | 0.11902 | -0.036621 | 0.27924 | 0.2243 | -0.16479 | -0.19226 | 122.8455 | 122.6578 | 0.19684 | 122.937 | 122.9416 | 0.28381 | -0.013732 | 122.6852 | 122.6578 | 0.096131 | 122.9095 | 122.8134 | 0.15564 | 0.041199 | 123.23 | 123.0194 | 122.8867 | -0.37537 | 123.1293 | 123.0743 | 122.9691 | -0.37537
5051.8125 | 123.1613 | -122.8775 | 0.20599 | -0.054016 | 0.037918 | 0.0052978 | 0.0055457 | -0.010747 | 0.0037106 | -0.0097199 | -0.08873 | -0.011059 | -0.0051846 | -0.0011216 | 0.0064577 | -0.017425 | 0.14191 | 0.086975 | 0.004578 | 0.068665 | 0.29297 | -0.073242 | -0.22888 | 0.064087 | 0.086975 | -0.086975 | 0.20599 | 0.19226 | -0.17853 | -0.2243 | 122.8043 | 122.6486 | 0.086975 | 122.9645 | 122.9462 | 0.29755 | -0.064087 | 122.699 | 122.6532 | 0 | 122.9416 | 122.7905 | 0.13733 | -0.013733 | 123.1705 | 123.0194 | 122.8821 | -0.43488 | 123.0835 | 123.0698 | 122.9645 | -0.4303
5053.5156 | 123.2254 | -122.8363 | 0.16937 | -0.054016 | 0.031723 | 0.006366 | 0.010459 | -0.010534 | -0.0069706 | -0.0086517 | -0.065842 | -0.016614 | -0.0043302 | -0.0034714 | 0.0013309 | -0.016998 | 0.13275 | 0.19684 | 0.16022 | 0.14191 | 0.32959 | 0.018311 | -0.16479 | 0.19684 | 0.2655 | 0.15106 | 0.24261 | 0.2243 | -0.086975 | -0.12817 | 122.8546 | 122.6715 | 0.16022 | 123.0331 | 122.9782 | 0.3067 | -0.036622 | 122.7493 | 122.7081 | 0.073242 | 123.0331 | 122.9874 | 0.27924 | 0.054931 | 123.1659 | 122.9691 | 122.9965 | -0.33417 | 123.0789 | 123.0606 | 123.1018 | -0.29755
5055.2812 | 123.1476 | -122.8683 | 0.20599 | 0.17487 | 0.033218 | 0.0059388 | 0.0055457 | -0.011175 | 0.0039242 | -0.0082245 | 0.14015 | -0.013196 | -0.0064664 | -0.0011216 | 0.0066715 | -0.017212 | 0.086975 | 0.09613 | 0.018311 | 0.050354 | 0.24261 | -0.09613 | -0.26093 | 0.09613 | 0.11444 | -0.013733 | 0.16022 | 0.10529 | -0.17395 | -0.23346 | 122.7722 | 122.6074 | 0.036621 | 122.9645 | 122.9187 | 0.31128 | -0.11902 | 122.6944 | 122.6349 | -0.045777 | 122.9645 | 122.8546 | 0.21973 | -0.10071 | 123.111 | 122.9553 | 122.8867 | -0.46692 | 123.0286 | 122.9736 | 122.9828 | -0.43945
5057.0312 | 123.0972 | -122.8729 | 0.2243 | 0.19012 | 0.0345 | 0.0065796 | 0.0051183 | -0.0083974 | -0.002698 | -0.0077973 | 0.17067 | -0.014691 | -0.0096706 | -0.0043258 | 0.0083805 | -0.017639 | 0.068665 | 0.11902 | 0.050354 | 0.045776 | 0.21057 | -0.09613 | -0.25635 | 0.11444 | 0.13275 | 0.022888 | 0.16479 | 0.11902 | -0.17395 | -0.23346 | 122.7768 | 122.6166 | -0.013733 | 122.9919 | 122.9187 | 0.30212 | -0.15564 | 122.699 | 122.6395 | -0.059509 | 122.9874 | 122.8958 | 0.25635 | -0.10529 | 123.0835 | 122.9416 | 122.9233 | -0.48065 | 123.0377 | 122.9919 | 123.0057 | -0.45776
5058.7969 | 123.1888 | -122.8546 | 0.18768 | -0.19135 | 0.03215 | 0.008075 | 0.012382 | -0.007543 | -0.0052616 | -0.010788 | -0.14214 | -0.014905 | -0.0071072 | -0.0028306 | 0.0015445 | -0.018707 | 0.21515 | 0.2655 | 0.19684 | 0.18768 | 0.35248 | 0.027466 | -0.12817 | 0.20142 | 0.27924 | 0.12817 | 0.27008 | 0.2243 | -0.059509 | -0.11902 | 122.8821 | 122.7264 | 0.1648 | 123.1201 | 123.0423 | 0.31586 | 0.027466 | 122.7951 | 122.7356 | 0.082398 | 123.056 | 122.9828 | 0.24719 | 0.036621 | 123.2071 | 123.0698 | 123.0515 | -0.31586 | 123.1247 | 123.0789 | 123.1338 | -0.3067
5060.5625 | 123.2117 | -122.8455 | 0.19226 | -0.12268 | 0.038559 | 0.0072204 | 0.0074683 | -0.010534 | 0.0039242 | -0.0090791 | -0.18028 | -0.011914 | -0.0068936 | -0.0030442 | 0.0075259 | -0.019989 | 0.14648 | 0.086975 | 0 | 0.07782 | 0.33417 | -0.054932 | -0.2243 | 0.086975 | 0.11902 | -0.050354 | 0.21515 | 0.19684 | -0.15106 | -0.21057 | 122.7905 | 122.6212 | 0.14191 | 122.9324 | 122.9233 | 0.30212 | -0.045777 | 122.6944 | 122.6349 | 0.022888 | 122.9324 | 122.7951 | 0.16022 | 0.004577 | 123.1796 | 122.9919 | 122.8455 | -0.41656 | 123.0606 | 123.0423 | 122.9645 | -0.40283
5062.25 | 123.1155 | -122.8912 | 0.22888 | -0.054016 | 0.035782 | 0.0050842 | 0.0076819 | -0.0079702 | 0.004565 | -0.0071563 | -0.065842 | -0.010846 | -0.0075344 | -0.0028306 | 0.0081667 | -0.018707 | 0.091553 | 0.086975 | -0.004578 | 0.036621 | 0.31586 | -0.082397 | -0.25177 | 0.032043 | 0.045776 | -0.10071 | 0.21515 | 0.17395 | -0.20599 | -0.23804 | 122.8088 | 122.6395 | 0.086975 | 122.9782 | 122.9279 | 0.28839 | -0.13733 | 122.6852 | 122.6532 | -0.013733 | 122.9233 | 122.7905 | 0.13733 | -0.054932 | 123.2071 | 122.9828 | 122.8867 | -0.48065 | 123.1064 | 123.0652 | 122.937 | -0.46692
5064 | 123.1018 | -122.8592 | 0.21515 | 0.060425 | 0.038132 | 0.0070068 | 0.0074683 | -0.0083974 | 0.0024288 | -0.0069427 | -0.012436 | -0.0093503 | -0.0058254 | -5.3406e-05 | 0.0070987 | -0.017425 | 0.036621 | -0.018311 | -0.082397 | -0.013733 | 0.28381 | -0.10986 | -0.29297 | -0.041199 | -0.004578 | -0.14648 | 0.20599 | 0.19684 | -0.20142 | -0.26093 | 122.7493 | 122.5662 | 0.068664 | 122.8409 | 122.8455 | 0.27924 | -0.17853 | 122.6578 | 122.5983 | -0.009155 | 122.818 | 122.7127 | 0.11444 | -0.018311 | 123.143 | 122.8958 | 122.7768 | -0.50812 | 123.0652 | 123.056 | 122.8546 | -0.47607
5065.75 | 123.143 | -122.8729 | 0.21973 | 0.17487 | 0.035141 | 0.0061524 | 0.0081091 | -0.010534 | -0.00034818 | -0.0082245 | 0.12489 | -0.013836 | -0.0081754 | -0.0021896 | 0.0062441 | -0.018066 | 0.064087 | 0.09613 | 0.027466 | 0.050354 | 0.2243 | -0.091553 | -0.25635 | 0.073242 | 0.1236 | 0.009155 | 0.16937 | 0.13733 | -0.1831 | -0.20142 | 122.7814 | 122.6166 | 0.004577 | 122.9691 | 122.9233 | 0.3067 | -0.15564 | 122.6898 | 122.6715 | -0.050354 | 122.9462 | 122.8821 | 0.21057 | -0.082398 | 123.0972 | 122.937 | 122.9004 | -0.47608 | 123.0423 | 123.0103 | 122.9965 | -0.42114
5067.5 | 123.1567 | -122.8729 | 0.21515 | 0.17487 | 0.036423 | 0.0076478 | 0.0061865 | -0.011175 | -0.0024844 | -0.0075837 | 0.13252 | -0.010632 | -0.0079618 | -0.0026168 | 0.0070987 | -0.016998 | 0.068665 | 0.068665 | 0.009155 | 0.041199 | 0.23346 | -0.09613 | -0.27466 | 0.07782 | 0.1236 | -0.004578 | 0.16937 | 0.1236 | -0.16937 | -0.21973 | 122.7768 | 122.5983 | 0.01831 | 122.9416 | 122.9141 | 0.31586 | -0.14648 | 122.7036 | 122.6532 | -0.045776 | 122.9507 | 122.8683 | 0.21515 | -0.091553 | 123.1064 | 122.9416 | 122.8821 | -0.48981 | 123.0423 | 122.9965 | 122.9965 | -0.43488
5069.1875 | 123.1338 | -122.8867 | 0.21973 | 0.083313 | 0.037705 | 0.0067932 | 0.0040503 | -0.0083974 | -0.00056178 | -0.0077973 | 0.10963 | -0.011487 | -0.0086026 | -0.001976 | 0.0077395 | -0.017212 | 0 | -0.064087 | -0.09613 | -0.050354 | 0.28381 | -0.13275 | -0.29755 | -0.027466 | -0.009155 | -0.11902 | 0.18768 | 0.16022 | -0.2243 | -0.26093 | 122.7539 | 122.5891 | 0.064086 | 122.8226 | 122.8363 | 0.24719 | -0.21973 | 122.6624 | 122.6257 | -0.032044 | 122.8592 | 122.7676 | 0.14191 | -0.05951 | 123.1705 | 122.8867 | 122.7905 | -0.51727 | 123.0743 | 123.0469 | 122.8775 | -0.48065
5070.9531 | 123.2025 | -122.8546 | 0.19684 | -0.092163 | 0.037064 | 0.0050842 | 0.0096045 | -0.008611 | 0.0013608 | -0.0080109 | -0.15739 | -0.010846 | -0.0056118 | -0.0021896 | 0.0056033 | -0.016571 | 0.11444 | 0.10071 | 0.004578 | 0.068665 | 0.32959 | -0.07782 | -0.23804 | 0.064087 | 0.10071 | -0.050354 | 0.23804 | 0.18768 | -0.17395 | -0.22888 | 122.7768 | 122.6166 | 0.13275 | 122.9553 | 122.9233 | 0.3067 | -0.082397 | 122.6807 | 122.6257 | 0.041199 | 122.9187 | 122.8043 | 0.17853 | -0.009155 | 123.1842 | 122.9691 | 122.8592 | -0.43488 | 123.0927 | 123.0423 | 122.9553 | -0.42572
5072.7031 | 123.2346 | -122.8363 | 0.18768 | -0.13794 | 0.033218 | 0.008075 | 0.012168 | -0.0079702 | -0.0069706 | -0.0082245 | -0.081101 | -0.014691 | -0.007748 | -0.0043258 | -0.00080527 | -0.016998 | 0.19226 | 0.2655 | 0.20142 | 0.1831 | 0.35248 | 0.027466 | -0.14191 | 0.20599 | 0.27924 | 0.15564 | 0.26093 | 0.2243 | -0.073242 | -0.13275 | 122.8638 | 122.6944 | 0.1648 | 123.1018 | 123.0194 | 0.32501 | 0.004578 | 122.7631 | 122.7036 | 0.073242 | 123.0423 | 122.9919 | 0.28839 | 0.036621 | 123.1888 | 123.0286 | 123.0377 | -0.32959 | 123.0972 | 123.0606 | 123.1155 | -0.32043
5074.4531 | 123.2346 | -122.8409 | 0.19226 | -0.12268 | 0.031509 | 0.009143 | 0.0098181 | -0.010961 | -0.006757 | -0.011429 | -0.042954 | -0.016186 | -0.0073208 | -0.0030442 | 0.0019717 | -0.018921 | 0.16479 | 0.24261 | 0.20142 | 0.17395 | 0.35706 | 0.036621 | -0.14648 | 0.21057 | 0.29755 | 0.16937 | 0.25177 | 0.21515 | -0.068665 | -0.1236 | 122.8775 | 122.6944 | 0.16479 | 123.0835 | 123.0148 | 0.32043 | -0.027466 | 122.7722 | 122.7173 | 0.059509 | 123.0515 | 123.0103 | 0.29297 | 0.022888 | 123.1979 | 123.0057 | 123.0423 | -0.33874 | 123.0927 | 123.056 | 123.1384 | -0.31586
5076.1562 | 123.111 | -122.8821 | 0.2243 | 0.17487 | 0.032364 | 0.006366 | 0.0057593 | -0.0088248 | -0.0012028 | -0.0086517 | 0.19356 | -0.013196 | -0.0075344 | -0.0026168 | 0.0062441 | -0.017852 | 0.082397 | 0.082397 | 0.022888 | 0.045776 | 0.2243 | -0.09613 | -0.25635 | 0.091553 | 0.10986 | 0.004578 | 0.15106 | 0.10071 | -0.19684 | -0.21515 | 122.7859 | 122.6257 | 0 | 122.9645 | 122.9279 | 0.30212 | -0.14191 | 122.6852 | 122.6669 | -0.073242 | 122.9736 | 122.8867 | 0.21973 | -0.1236 | 123.1064 | 122.9645 | 122.905 | -0.48065 | 123.0331 | 122.9828 | 122.9919 | -0.43945
5077.9219 | 123.2437 | -122.8455 | 0.18768 | -0.18372 | 0.037064 | 0.0078614 | 0.0087499 | -0.0060476 | 0.0028562 | -0.0082245 | -0.23369 | -0.013409 | -0.0068936 | -0.0017624 | 0.0070987 | -0.019561 | 0.10529 | 0.10986 | 0.041199 | 0.09613 | 0.39368 | -0.013733 | -0.1831 | 0.059509 | 0.11444 | -0.045776 | 0.26093 | 0.23804 | -0.14648 | -0.19684 | 122.8317 | 122.6624 | 0.20599 | 122.9553 | 122.9416 | 0.27924 | -0.082397 | 122.699 | 122.6486 | 0.073242 | 122.905 | 122.7997 | 0.15106 | 0.050354 | 123.2391 | 122.9507 | 122.8867 | -0.37079 | 123.1064 | 123.0835 | 122.9599 | -0.38452
5079.6719 | 123.2574 | -122.8455 | 0.19226 | -0.16846 | 0.039627 | 0.0067932 | 0.0087499 | -0.0079702 | 0.0011472 | -0.0092927 | -0.23369 | -0.011487 | -0.004971 | -0.0024032 | 0.0053897 | -0.017639 | 0.1236 | 0.091553 | 0.041199 | 0.10071 | 0.40283 | -0.022888 | -0.18768 | 0.064087 | 0.11902 | -0.018311 | 0.27008 | 0.24261 | -0.14191 | -0.1831 | 122.8226 | 122.6578 | 0.21057 | 122.937 | 122.9462 | 0.28839 | -0.068665 | 122.7036 | 122.6624 | 0.07782 | 122.9095 | 122.8271 | 0.16479 | 0.050354 | 123.2483 | 122.9691 | 122.8867 | -0.37994 | 123.1155 | 123.0881 | 122.9645 | -0.37537
5081.4375 | 123.1247 | -122.9187 | 0.19684 | 0.014648 | 0.031509 | 0.0076478 | 0.0061865 | -0.011388 | -0.0076114 | -0.0082245 | 0.11726 | -0.013836 | -0.0058254 | -0.0034714 | 0.0034671 | -0.01593 | 0.073242 | 0.1236 | 0.07782 | 0.086975 | 0.31586 | -0.027466 | -0.19684 | 0.10071 | 0.16479 | 0.050354 | 0.23346 | 0.19684 | -0.11902 | -0.16479 | 122.8912 | 122.7219 | 0.11902 | 123.0423 | 123.0057 | 0.28381 | -0.1236 | 122.7997 | 122.7539 | 0.036621 | 123.0194 | 122.9691 | 0.21515 | 0 | 123.2346 | 122.9919 | 122.9965 | -0.39368 | 123.1522 | 123.1155 | 123.0835 | -0.36163
5083.125 | 123.1018 | -122.8958 | 0.2243 | 0.12146 | 0.03215 | 0.0078614 | 0.0072547 | -0.01032 | -0.0035526 | -0.010147 | 0.11726 | -0.013836 | -0.0098844 | -0.0028306 | 0.0060305 | -0.016998 | 0.086975 | 0.11444 | 0.064087 | 0.054932 | 0.24261 | -0.064087 | -0.23804 | 0.10529 | 0.13733 | 0.041199 | 0.20142 | 0.17853 | -0.15106 | -0.16479 | 122.8317 | 122.6578 | 0.018311 | 123.0103 | 122.9507 | 0.29297 | -0.13733 | 122.7448 | 122.731 | -0.022888 | 123.0011 | 122.937 | 0.20599 | -0.045776 | 123.1384 | 122.9828 | 122.9599 | -0.46234 | 123.0972 | 123.0743 | 123.0331 | -0.3891
5084.875 | 123.2071 | -122.85 | 0.1831 | -0.099793 | 0.038773 | 0.0076478 | 0.0093909 | -0.010961 | 0.0028562 | -0.0090791 | -0.20317 | -0.0099911 | -0.0045438 | -0.0017624 | 0.0070987 | -0.018921 | 0.13275 | 0.10071 | 0.018311 | 0.068665 | 0.33417 | -0.059509 | -0.21515 | 0.068665 | 0.091553 | -0.059509 | 0.22888 | 0.18768 | -0.16937 | -0.21973 | 122.7905 | 122.6349 | 0.15106 | 122.9507 | 122.9187 | 0.28381 | -0.050354 | 122.6807 | 122.6303 | 0.045777 | 122.9187 | 122.7905 | 0.16022 | 0.004578 | 123.1842 | 122.9828 | 122.8683 | -0.39825 | 123.0789 | 123.0377 | 122.9416 | -0.40283
5086.6406 | 123.1384 | -122.8775 | 0.21973 | 0.14435 | 0.036636 | 0.0087158 | 0.0072547 | -0.010106 | -0.0018436 | -0.0097199 | 0.1783 | -0.011487 | -0.0086026 | -0.0013352 | 0.0058169 | -0.016998 | 0.091553 | 0.10071 | 0.050354 | 0.068665 | 0.23346 | -0.091553 | -0.24261 | 0.086975 | 0.10986 | 0.004578 | 0.15564 | 0.10529 | -0.19226 | -0.21515 | 122.7859 | 122.6349 | 0.013732 | 122.9782 | 122.9462 | 0.31128 | -0.12817 | 122.6852 | 122.6624 | -0.064087 | 122.9645 | 122.8821 | 0.21973 | -0.11444 | 123.111 | 122.9691 | 122.9279 | -0.46234 | 123.0331 | 122.9828 | 122.9874 | -0.43488
5088.4062 | 123.1018 | -122.8683 | 0.23804 | 0.15961 | 0.033646 | 0.0050842 | 0.0059729 | -0.0096792 | -0.0039798 | -0.012283 | 0.16304 | -0.013196 | -0.0075344 | -0.0024032 | 0.0043215 | -0.016357 | 0.09613 | 0.10986 | 0.054932 | 0.054932 | 0.21973 | -0.068665 | -0.23346 | 0.11902 | 0.12817 | 0.041199 | 0.17395 | 0.13733 | -0.16937 | -0.19226 | 122.7997 | 122.6349 | -0.01831 | 122.9782 | 122.9233 | 0.28839 | -0.14191 | 122.699 | 122.6761 | -0.064087 | 122.9874 | 122.9095 | 0.23346 | -0.10071 | 123.0881 | 122.9645 | 122.9233 | -0.4715 | 123.0423 | 123.0057 | 122.9965 | -0.4303
5090.1094 | 123.1613 | -122.8867 | 0.2243 | 0.12909 | 0.037277 | 0.0035888 | 0.0076819 | -0.0079702 | 0.0020016 | -0.0077973 | 0.079117 | -0.0117 | -0.0064664 | -0.00048061 | 0.0079531 | -0.016571 | 0.013733 | -0.054932 | -0.086975 | -0.032043 | 0.27924 | -0.13275 | -0.29297 | 0.004578 | 0 | -0.10529 | 0.18768 | 0.15564 | -0.21973 | -0.23804 | 122.7539 | 122.5937 | 0.054932 | 122.8317 | 122.8546 | 0.26093 | -0.21057 | 122.6669 | 122.6486 | -0.036621 | 122.8912 | 122.7814 | 0.13275 | -0.068664 | 123.1659 | 122.9004 | 122.7997 | -0.51727 | 123.0743 | 123.0423 | 122.8867 | -0.46234
5091.8594 | 123.1247 | -122.8867 | 0.21515 | 0.022278 | 0.035568 | 0.0052978 | 0.011527 | -0.011602 | -0.005048 | -0.011215 | 0.11726 | -0.015118 | -0.0068936 | -0.00069421 | 0.0013309 | -0.018066 | 0.091553 | 0.1236 | 0.086975 | 0.082397 | 0.31128 | -0.022888 | -0.19226 | 0.10986 | 0.16479 | 0.054932 | 0.23346 | 0.2243 | -0.12817 | -0.16479 | 122.8638 | 122.6944 | 0.09613 | 123.0103 | 122.9691 | 0.27466 | -0.1236 | 122.7585 | 122.7219 | 0.01831 | 122.9965 | 122.9416 | 0.21973 | 0.009155 | 123.1979 | 122.9782 | 122.9736 | -0.40741 | 123.1201 | 123.111 | 123.0515 | -0.37994
5093.625 | 123.1064 | -122.9004 | 0.2243 | -0.023499 | 0.037064 | 0.0061524 | 0.0081091 | -0.0077566 | 0.0047788 | -0.0069427 | -0.050583 | -0.012768 | -0.0062528 | -0.0015488 | 0.0062441 | -0.017425 | 0.10071 | 0.059509 | -0.027466 | 0.045776 | 0.3067 | -0.091553 | -0.23804 | 0.018311 | 0.013733 | -0.12817 | 0.21515 | 0.17395 | -0.19684 | -0.23804 | 122.8088 | 122.6624 | 0.082398 | 122.9599 | 122.9462 | 0.28381 | -0.1236 | 122.7036 | 122.6624 | -0.009155 | 122.9187 | 122.7722 | 0.10986 | -0.050354 | 123.2071 | 123.0011 | 122.8729 | -0.46234 | 123.1155 | 123.0743 | 122.9141 | -0.46234
5095.3281 | 123.1888 | -122.8592 | 0.19226 | -0.015869 | 0.032364 | 0.0057252 | 0.010673 | -0.011602 | -0.006116 | -0.011642 | 0.025711 | -0.012982 | -0.0043302 | -0.0024032 | 0.0015445 | -0.016784 | 0.050354 | 0.13275 | 0.10071 | 0.10529 | 0.32501 | -0.004578 | -0.19684 | 0.10986 | 0.16022 | 0.073242 | 0.2243 | 0.20142 | -0.13275 | -0.16022 | 122.8546 | 122.6624 | 0.13275 | 122.9919 | 122.9645 | 0.30212 | -0.14191 | 122.7264 | 122.699 | 0.032043 | 122.9691 | 122.9324 | 0.23346 | 0.009155 | 123.1842 | 122.9095 | 122.9599 | -0.3891 | 123.0835 | 123.0606 | 123.0194 | -0.35248
5097.0781 | 123.2254 | -122.8455 | 0.1831 | -0.031128 | 0.030228 | 0.0085022 | 0.011527 | -0.008611 | -0.005048 | -0.0097199 | 0.0028229 | -0.015973 | -0.0053982 | 0.00016019 | 0.00090353 | -0.017425 | 0.10986 | 0.17853 | 0.14191 | 0.14191 | 0.3479 | -0.004578 | -0.16022 | 0.17853 | 0.24719 | 0.11444 | 0.25635 | 0.21515 | -0.091553 | -0.13275 | 122.8409 | 122.6852 | 0.16479 | 123.024 | 122.9874 | 0.30212 | -0.073242 | 122.7539 | 122.7127 | 0.073243 | 123.024 | 122.9599 | 0.24719 | 0.032044 | 123.1934 | 122.9553 | 122.9874 | -0.34332 | 123.1018 | 123.0606 | 123.0927 | -0.31586
5098.8438 | 123.23 | -122.8592 | 0.20142 | -0.13794 | 0.038132 | 0.0057252 | 0.0083227 | -0.009252 | 0.0026424 | -0.0082245 | -0.18028 | -0.011914 | -0.0071072 | -0.0028306 | 0.0073123 | -0.019561 | 0.13275 | 0.10986 | 0.004578 | 0.064087 | 0.33875 | -0.045776 | -0.22888 | 0.082397 | 0.091553 | -0.050354 | 0.23346 | 0.20142 | -0.1831 | -0.21515 | 122.8134 | 122.6303 | 0.13733 | 122.9691 | 122.9233 | 0.29297 | -0.068665 | 122.6761 | 122.644 | 0.032043 | 122.9416 | 122.8088 | 0.16479 | 0 | 123.1979 | 122.9919 | 122.8638 | -0.4303 | 123.0927 | 123.0606 | 122.9507 | -0.41657
5100.5312 | 123.1293 | -122.8683 | 0.21515 | 0.029907 | 0.030014 | 0.007434 | 0.0083227 | -0.010106 | -0.005048 | -0.0097199 | 0.102 | -0.014264 | -0.0081754 | -0.0028306 | 0.0045351 | -0.016571 | 0.082397 | 0.13275 | 0.09613 | 0.10071 | 0.31128 | -0.045776 | -0.21057 | 0.10071 | 0.14648 | 0.050354 | 0.24719 | 0.20599 | -0.15106 | -0.18768 | 122.8226 | 122.6578 | 0.09613 | 123.0011 | 122.9691 | 0.31128 | -0.13275 | 122.7173 | 122.6807 | 0.032043 | 122.9691 | 122.9187 | 0.23804 | -0.009155 | 123.1796 | 122.9507 | 122.9645 | -0.42572 | 123.1155 | 123.0743 | 123.0148 | -0.40283

## Thermal Data
Fire Time | E Position - 3' | E Position - Middle | E Position - 7'
-0.9333 | 18.7364 | 18.7641 | 23.202
0.0667 | 18.7316 | 18.7607 | 23.1874
1.0667 | 18.7354 | 18.763 | 23.1845
2.0667 | 18.7476 | 18.7674 | 23.1996
3.0667 | 18.7527 | 18.7664 | 23.2246
4.0667 | 18.7885 | 18.7269 | 22.6162
5.0667 | 18.834 | 18.7812 | 23.1676
6.0667 | 19.3207 | 19.3961 | 27.0645
7.0667 | 20.6543 | 21.3993 | 27.082
8.0667 | 21.8181 | 22.6879 | 27.0742
9.0823 | 26.0198 | 27.9641 | 27.083
10.0667 | 30.7664 | 33.2421 | 27.0738
11.0667 | 36.1213 | 36.4494 | 27.0786
12.0667 | 40.6777 | 41.2541 | 27.0768
13.0667 | 44.4149 | 45.3608 | 27.0785
14.0667 | 46.862 | 48.1101 | 27.0898
15.0667 | 50.444 | 51.8309 | 27.0764
16.0667 | 53.6533 | 55.0114 | 27.0728
17.0667 | 55.6013 | 58.8447 | 27.0777
18.0667 | 57.7345 | 60.7408 | 27.0733
19.0667 | 60.1124 | 62.8643 | 27.0723
20.0667 | 62.6961 | 65.1172 | 27.0805
21.0667 | 64.3819 | 67.252 | 27.0768
22.0667 | 66.4203 | 69.3489 | 27.0785
23.0823 | 68.7133 | 71.1271 | 27.071
24.0823 | 70.8117 | 73.0585 | 27.0695
25.0667 | 72.467 | 75.9315 | 27.0749
26.0667 | 74.5055 | 77.528 | 27.0749
27.0667 | 75.4448 | 79.1648 | 27.074
28.0667 | 76.0105 | 80.6532 | 27.0753
29.0667 | 77.0719 | 81.5856 | 27.0721
30.0667 | 78.0816 | 82.0561 | 27.0763
31.0667 | 79.1211 | 82.8909 | 27.0767
32.0667 | 80.0527 | 83.672 | 27.0737
33.0667 | 80.8665 | 84.144 | 27.0757
34.0667 | 81.3668 | 84.4727 | 27.0739
35.0667 | 81.9559 | 85.3718 | 27.0717
36.0667 | 82.8889 | 85.617 | 27.0738
37.0667 | 83.74 | 86.0848 | 27.0687
38.0667 | 84.1041 | 86.1877 | 27.07
39.0667 | 84.5621 | 86.1845 | 27.0742
40.0667 | 84.5163 | 86.3339 | 27.0736
41.0667 | 84.7283 | 86.768 | 27.0691
42.0667 | 85.0117 | 86.8687 | 27.0684
43.0823 | 85.2477 | 86.9271 | 27.0697
44.0667 | 85.2189 | 86.7815 | 27.0686
45.0667 | 85.1447 | 87.1137 | 27.0709
46.0667 | 85.1261 | 87.2054 | 27.0579
47.0667 | 84.9751 | 87.184 | 27.0616
48.0667 | 85.2984 | 86.9952 | 27.0631
49.0667 | 85.2759 | 86.7194 | 27.0651
50.0667 | 85.0904 | 86.7152 | 27.0651
51.0823 | 85.06 | 86.6536 | 27.0562
52.0667 | 84.9494 | 86.6941 | 27.0573
53.0823 | 84.9008 | 86.677 | 27.0611
54.0667 | 84.6845 | 86.6382 | 27.0607
55.0667 | 84.6415 | 86.4837 | 27.0616
56.0667 | 84.4645 | 86.4154 | 27.0628
57.0667 | 84.2252 | 86.232 | 27.0615
58.0667 | 83.961 | 85.9106 | 27.0663
59.0667 | 83.8866 | 85.6369 | 27.0645
60.0667 | 83.9512 | 85.4689 | 27.0583
61.0667 | 83.9452 | 85.4714 | 27.0536
62.0667 | 83.8687 | 85.4851 | 27.065
63.0667 | 83.5371 | 85.4224 | 27.0638
64.0823 | 83.474 | 85.3525 | 27.0669
65.0667 | 83.4612 | 85.4271 | 27.0605
66.0667 | 83.557 | 85.3256 | 27.0593
67.0667 | 83.5313 | 85.296 | 27.0611
68.0667 | 83.2406 | 85.3755 | 27.0549
69.0667 | 82.9535 | 85.3782 | 27.0534
70.0667 | 82.8714 | 85.3108 | 27.0521
71.0667 | 82.7593 | 85.2147 | 27.0535
72.0667 | 82.6357 | 85.1097 | 27.0566
73.0667 | 82.5463 | 84.9755 | 27.0561
74.0667 | 82.3861 | 84.8325 | 27.0488
75.0667 | 82.406 | 84.7225 | 27.0542
76.0667 | 82.4269 | 84.5804 | 27.0588
77.0667 | 82.4359 | 84.4697 | 27.0557
78.0667 | 82.4246 | 84.4197 | 27.0526
79.0667 | 82.5018 | 84.3386 | 27.0544
80.0667 | 82.546 | 84.356 | 27.0551
81.0667 | 82.5484 | 84.5726 | 27.0526
82.0667 | 82.3633 | 84.5184 | 27.0554
83.0667 | 82.1107 | 84.5049 | 27.0573
84.0667 | 82.1877 | 84.5859 | 27.0592
85.0667 | 82.2799 | 84.5203 | 27.0493
86.0667 | 82.4091 | 84.683 | 27.0501
87.0667 | 82.6367 | 84.8031 | 27.0573
88.0667 | 82.5826 | 84.7625 | 27.0519
89.0667 | 82.5031 | 84.7079 | 27.0505
90.0667 | 82.6087 | 84.5602 | 27.0476
91.0667 | 82.7034 | 84.6403 | 27.0479
92.0667 | 82.6443 | 84.63 | 27.0503
93.0667 | 82.5986 | 84.7888 | 27.0505
94.0667 | 82.6646 | 84.9009 | 27.0485
95.0667 | 82.7504 | 84.9803 | 27.0566
96.0667 | 82.7757 | 84.9974 | 27.0479
97.0667 | 82.8525 | 84.9772 | 27.0498
98.0667 | 82.8916 | 85.011 | 27.0478
99.0667 | 82.9593 | 85.1695 | 27.0544
100.0667 | 83.0276 | 85.2578 | 27.0424
101.0667 | 83.0305 | 85.1382 | 27.0475
102.0667 | 83.0763 | 85.0132 | 27.0481
103.0667 | 82.8857 | 84.9866 | 27.042
104.0667 | 82.8898 | 84.9954 | 27.0445
105.0667 | 82.9691 | 85.108 | 27.0424
106.0667 | 83.107 | 85.0169 | 27.0489
107.0667 | 83.0768 | 84.8798 | 27.036
108.0667 | 83.078 | 84.892 | 27.049
109.0667 | 83.2311 | 85.112 | 27.0458
110.0667 | 83.4109 | 85.0924 | 27.047
111.0667 | 83.4607 | 85.2969 | 27.0423
112.0667 | 83.4577 | 85.5437 | 27.0465
113.0667 | 83.4506 | 85.5114 | 27.0438
114.0667 | 83.3645 | 85.4677 | 27.0408
115.0667 | 83.4621 | 85.5068 | 27.0407
116.0667 | 83.4349 | 85.6824 | 27.0361
117.0667 | 83.3651 | 85.9695 | 27.0381
118.0667 | 83.3388 | 86.0176 | 27.0453
119.0667 | 83.3674 | 85.9714 | 27.0386
120.0667 | 83.3439 | 86.277 | 27.0453
121.0667 | 83.2328 | 86.5238 | 27.0325
122.0667 | 83.4339 | 86.4891 | 27.0365
123.0667 | 83.7744 | 86.5781 | 27.0368
124.0667 | 83.9711 | 86.8116 | 27.0397
125.0667 | 84.0536 | 87.0396 | 27.0452
126.0667 | 84.3756 | 87.1066 | 27.0391
127.0667 | 84.4796 | 87.3038 | 27.038
128.0667 | 84.8013 | 87.4292 | 27.036
129.0667 | 84.9967 | 87.4996 | 27.0322
130.0667 | 85.2388 | 87.5619 | 27.0337
131.0667 | 85.3646 | 87.5417 | 27.0382
132.0667 | 85.4688 | 87.5574 | 27.0382
133.0667 | 85.5986 | 87.8022 | 27.0391
134.0667 | 85.9508 | 87.9387 | 27.0391
135.0667 | 85.8845 | 87.9137 | 27.0368
136.0667 | 86.0183 | 87.9352 | 27.0343
137.0667 | 86.0123 | 88.048 | 27.0312
138.0667 | 86.351 | 88.091 | 27.035
139.0667 | 86.6926 | 87.9688 | 27.0349
140.0667 | 86.5579 | 88.0128 | 27.0292
141.0667 | 86.7721 | 87.956 | 27.0361
142.0667 | 87.062 | 88.6136 | 27.0255
143.0667 | 87.2405 | 88.6795 | 27.0333
144.0823 | 87.3692 | 88.8778 | 27.0306
145.0667 | 87.5156 | 89.052 | 27.0303
146.0667 | 87.5785 | 89.3699 | 27.0331
147.0667 | 87.8148 | 89.4454 | 27.0304
148.0667 | 87.7358 | 89.542 | 27.0266
149.0667 | 87.7388 | 89.7441 | 27.0259
150.0667 | 87.9288 | 90.1039 | 27.0286
151.0667 | 88.2794 | 90.4937 | 27.0249
152.0667 | 88.7148 | 90.6697 | 27.0188
153.0667 | 88.7869 | 90.6106 | 27.0245
154.0667 | 88.9829 | 90.7236 | 27.0246
155.0667 | 89.1224 | 90.9764 | 27.0212
156.0667 | 89.1976 | 91.0679 | 27.03
157.0667 | 89.2114 | 91.1235 | 27.0296
158.0667 | 89.387 | 91.0788 | 27.0304
159.0823 | 89.4354 | 91.1576 | 27.0263
160.0667 | 89.5957 | 91.4045 | 27.0265
161.0667 | 89.5819 | 91.4167 | 27.0222
162.0667 | 89.6262 | 91.5616 | 27.0187
163.0667 | 89.7559 | 91.7611 | 27.0173
164.0667 | 89.8033 | 91.9241 | 27.0201
165.0667 | 89.9568 | 92.224 | 27.0195
166.0667 | 90.0603 | 92.6542 | 27.0234
167.0667 | 90.2329 | 92.8051 | 27.0171
168.0667 | 90.3745 | 93.116 | 27.0204
169.0667 | 90.7202 | 93.2649 | 27.0254
170.0667 | 90.9845 | 93.5243 | 27.0188
171.0667 | 91.0779 | 93.7103 | 27.0225
172.0667 | 91.4569 | 93.96 | 27.0152
173.0667 | 91.6663 | 94.1367 | 27.0185
174.0667 | 91.8862 | 94.3974 | 27.0118
175.0667 | 92.0703 | 94.5911 | 27.0149
176.0667 | 92.1606 | 94.6288 | 27.0219
177.0667 | 92.2492 | 94.5994 | 27.0208
178.0667 | 92.3415 | 94.8148 | 27.011
179.0667 | 92.4944 | 94.923 | 27.0197
180.0667 | 92.5605 | 94.9478 | 27.0199
181.0667 | 92.6614 | 95.0628 | 27.009
182.0667 | 92.6925 | 95.0265 | 27.0176
183.0667 | 92.7979 | 95.0527 | 27.0166
184.0823 | 92.8028 | 95.0581 | 27.017
185.0667 | 93.0036 | 94.9436 | 27.0165
186.0667 | 93.2116 | 94.997 | 27.0129
187.0667 | 93.1958 | 94.8584 | 27.0206
188.0667 | 93.1223 | 94.8806 | 27.0126
189.0667 | 93.386 | 94.9845 | 27.0135
190.0667 | 93.4104 | 95.0804 | 27.0113
191.0667 | 93.4585 | 95.1016 | 27.0059
192.0667 | 93.662 | 95.1439 | 27.0082
193.0667 | 93.7436 | 95.0912 | 27.0051
194.0667 | 93.8804 | 95.1965 | 27.0145
195.0667 | 94.0325 | 95.1684 | 27.0147
196.0667 | 94.5175 | 95.1246 | 27.007
197.0667 | 94.6626 | 95.2862 | 27.0074
198.0667 | 94.9568 | 95.49 | 27.0113
199.0667 | 95.1753 | 95.6017 | 27.0135
200.0667 | 95.3724 | 95.7875 | 27.0103
201.0667 | 95.7805 | 95.8862 | 27.0122
202.0667 | 95.9656 | 96.0482 | 27.0079
203.0667 | 96.0253 | 96.2267 | 27.0131
204.0667 | 96.216 | 96.4135 | 27.0125
205.0667 | 96.2525 | 96.5312 | 27.0133
206.0667 | 96.2869 | 96.7166 | 27.0144
207.0667 | 96.5464 | 97.2958 | 27.0044
208.0667 | 96.6201 | 97.293 | 27.0026
209.0667 | 96.8709 | 97.5067 | 27.0101
210.0667 | 97.2485 | 97.4996 | 27.0125
211.0667 | 97.4321 | 98.0769 | 27.0128
212.0667 | 97.6295 | 98.3135 | 27.0078
213.0667 | 97.5902 | 98.6277 | 27.0055
214.0667 | 97.6122 | 98.9433 | 27.0036
215.0667 | 97.7645 | 99.3049 | 27.0085
216.0667 | 97.9863 | 99.3809 | 27.012
217.0667 | 98.2985 | 99.664 | 27.0072
218.0667 | 98.4572 | 100.184 | 27.0096
219.0667 | 98.388 | 100.5302 | 27.0099
220.0667 | 98.6849 | 100.7202 | 27.0018
221.0667 | 99.3418 | 100.9095 | 27.0159
222.0667 | 99.9318 | 101.2116 | 27.0113
223.0667 | 100.302 | 101.338 | 27.0056
224.0667 | 100.6706 | 101.7081 | 27.0089
225.0667 | 101.1714 | 102.2095 | 27.003
226.0667 | 101.4803 | 102.7739 | 27.0108
227.0667 | 101.5833 | 102.8275 | 27.0094
228.0667 | 101.5295 | 103.0537 | 27.0082
229.0823 | 101.7382 | 103.4477 | 27.0148
230.0667 | 102.4186 | 103.8936 | 27.0139
231.0667 | 103.4395 | 104.3026 | 27.0106
232.0667 | 103.839 | 104.3227 | 27.0068
233.0667 | 104.3043 | 104.4956 | 27.022
234.0667 | 104.7613 | 105.7287 | 27.0343
235.0667 | 105.1267 | 105.9677 | 27.0412
236.0667 | 105.7723 | 106.3052 | 27.0406
237.0667 | 106.4869 | 107.4742 | 27.0485
238.0667 | 107.2912 | 108.4084 | 27.1406
239.0667 | 108.0181 | 108.9415 | 27.2456
240.0667 | 108.744 | 109.5438 | 27.212
241.0667 | 109.1265 | 110.0895 | 27.2005
242.0667 | 109.8689 | 110.5005 | 27.3077
243.0667 | 110.0282 | 110.9226 | 27.2594
244.0823 | 110.446 | 111.234 | 27.4315
245.0667 | 110.8695 | 111.5096 | 27.357
246.0667 | 111.2011 | 111.5638 | 27.3757
247.0667 | 111.5168 | 111.7943 | 27.4638
248.0667 | 111.8787 | 111.8768 | 28.0641
249.0667 | 112.0407 | 112.2502 | 27.8167
250.0667 | 112.2319 | 112.4666 | 28.4946
251.0667 | 112.8281 | 112.5727 | 28.8606
252.0667 | 113.3037 | 113.0867 | 28.6536
253.0667 | 113.626 | 113.7374 | 30.116
254.0667 | 113.9233 | 114.5954 | 29.9024
255.0667 | 114.577 | 115.5347 | 31.0339
256.0667 | 115.7431 | 116.7681 | 32.1362
257.0667 | 116.8794 | 117.5056 | 31.6086
258.0667 | 117.6916 | 118.1816 | 31.7473
259.0667 | 118.5177 | 119.1888 | 32.1681
260.0667 | 118.9933 | 119.8556 | 32.6997
261.0667 | 119.5735 | 120.158 | 33.6752
262.0667 | 120.0318 | 120.9221 | 34.4975
263.0667 | 120.9098 | 121.8762 | 35.0141
264.0667 | 121.744 | 122.7712 | 35.4922
265.0667 | 122.2055 | 123.7323 | 38.2969
266.0667 | 122.5701 | 124.5906 | 39.3659
267.0667 | 122.833 | 124.9732 | 40.5618
268.0667 | 123.2521 | 125.8673 | 40.5604
269.0667 | 123.8175 | 127.2995 | 42.2316
270.0667 | 124.5609 | 128.254 | 45.1162
271.0667 | 125.511 | 128.7762 | 39.0605
272.0667 | 126.3117 | 130.1136 | 48.7816
273.0823 | 127.3042 | 131.3381 | 51.1525
274.0667 | 128.3159 | 132.5306 | 58.4776
275.0667 | 129.0914 | 133.6906 | 57.2369
276.0667 | 130.2309 | 134.2994 | 119.4239
277.0667 | 131.3647 | 135.6234 | 127.6085
278.0667 | 132.1263 | 136.9894 | 128.8464
279.0667 | 133.2702 | 137.6949 | 129.8988
280.0667 | 134.6255 | 138.9818 | 131.0547
281.0667 | 135.5232 | 140.0439 | 131.7376
282.0667 | 136.0425 | 140.5652 | 132.9447
283.0667 | 136.8713 | 141.424 | 133.9971
284.0667 | 137.9441 | 142.3284 | 135.3208
285.0667 | 138.8552 | 143.1003 | 135.909
286.0667 | 139.3481 | 144.1347 | 136.1652
287.0667 | 139.9083 | 145.2405 | 136.2632
288.0667 | 141.0173 | 146.0369 | 136.3103
289.0667 | 141.7024 | 146.4421 | 136.8816
290.0667 | 141.8062 | 147.103 | 138.4912
291.0667 | 142.3345 | 147.4354 | 138.4674
292.0667 | 143.2504 | 147.6242 | 139.1879
293.0667 | 143.7483 | 147.9171 | 139.4527
294.0667 | 144.3671 | 148.2153 | 140.1065
295.0667 | 144.5532 | 148.4935 | 141.0309
296.0667 | 145.0138 | 148.7927 | 141.9062
297.0667 | 145.4221 | 148.8556 | 141.9069
298.0667 | 145.6936 | 148.8478 | 141.84
299.0667 | 145.7518 | 149.2246 | 141.6623
300.0667 | 145.7133 | 148.8987 | 141.7994
301.0667 | 145.9037 | 149.047 | 142.1769
302.0667 | 146.1062 | 149.1848 | 142.7048
303.0667 | 147.1135 | 149.7965 | 142.9976
304.0667 | 147.1075 | 150.6024 | 143.2652
305.0667 | 147.5388 | 150.7248 | 143.7219
306.0667 | 148.2563 | 151.5108 | 143.8449
307.0667 | 148.4999 | 151.5073 | 144.469
308.0667 | 149.3323 | 151.595 | 144.6342
309.0667 | 149.9407 | 151.6028 | 145.0453
310.0667 | 149.8841 | 152.112 | 145.177
311.0667 | 150.1492 | 152.5534 | 145.3747
312.0667 | 150.4646 | 152.8403 | 145.2684
313.0667 | 150.9196 | 153.0221 | 145.0521
314.0667 | 151.4107 | 153.4136 | 144.9441
315.0667 | 151.8341 | 154.1078 | 145.4923
316.0667 | 152.3639 | 154.6894 | 145.5143
317.0667 | 152.6358 | 154.7347 | 146.146
318.0667 | 152.9804 | 155.5063 | 146.6916
319.0667 | 153.1442 | 156.2297 | 146.9893
320.0667 | 153.1779 | 156.9645 | 147.4587
321.0667 | 153.5405 | 157.1705 | 147.6248
322.0667 | 153.8445 | 157.6978 | 147.9303
323.0667 | 153.9341 | 158.4554 | 148.6681
324.0667 | 154.7138 | 158.1391 | 149.1781
325.0667 | 154.9462 | 158.8381 | 149.9276
326.0667 | 155.2303 | 159.4095 | 150.6511
327.0667 | 155.6793 | 160.1269 | 151.0917
328.0667 | 156.8509 | 160.2733 | 151.6169
329.0667 | 157.2615 | 160.7305 | 152.4515
330.0667 | 157.756 | 161.3739 | 152.644
331.0667 | 158.1408 | 161.895 | 152.8544
332.0667 | 158.4814 | 162.3142 | 153.1905
333.0667 | 159.0818 | 162.6689 | 153.3462
334.0667 | 159.188 | 162.9247 | 153.7485
335.0667 | 159.17 | 163.27 | 154.3126
336.0667 | 159.4779 | 163.6353 | 154.0785
337.0667 | 159.8774 | 164.5217 | 154.2589
338.0667 | 160.0499 | 164.7428 | 154.9678
339.0667 | 160.524 | 165.1803 | 155.5838
340.0667 | 160.9689 | 165.3712 | 156.2421
341.0667 | 161.3757 | 166.1679 | 156.9137
342.0667 | 161.6292 | 166.1707 | 157.8782
343.0667 | 162.2663 | 166.781 | 157.9075
344.0667 | 162.5388 | 167.625 | 158.2858
345.0667 | 162.6111 | 167.9559 | 158.7946
346.0667 | 162.9443 | 168.5799 | 158.8554
347.0667 | 163.4648 | 168.8665 | 159.5498
348.0667 | 163.3199 | 168.9744 | 159.9807
349.0667 | 163.1609 | 169.3424 | 160.5139
350.0667 | 163.46 | 169.388 | 160.2742
351.0667 | 163.9363 | 169.1464 | 160.0033
352.0667 | 164.1911 | 168.9434 | 160.2715
353.0667 | 164.191 | 168.713 | 160.8982
354.0667 | 164.0169 | 168.8305 | 160.9946
355.0667 | 164.4584 | 168.6843 | 160.9907
356.0667 | 163.96 | 168.2403 | 160.9466
357.0667 | 163.7326 | 168.1859 | 160.8968
358.0667 | 163.7951 | 168.1129 | 160.58
359.0667 | 163.7359 | 168.1583 | 160.1194
360.0667 | 163.8766 | 168.0151 | 160.416
361.0667 | 164.1503 | 168.3543 | 160.421
362.0667 | 164.1001 | 168.6809 | 160.5612
363.0667 | 164.4004 | 169.2341 | 161.1608
364.0823 | 165.2807 | 169.8047 | 161.4865
365.0667 | 165.5016 | 169.9949 | 162.2894
366.0667 | 166.041 | 169.942 | 162.4767
367.0667 | 167.0238 | 170.1688 | 162.7352
368.0667 | 167.1827 | 170.6283 | 162.8524
369.0667 | 167.2985 | 170.8458 | 162.691
370.0667 | 167.5669 | 171.0453 | 163.142
371.0667 | 167.995 | 171.4317 | 163.8106
372.0667 | 168.2697 | 171.4567 | 164.4708
373.0667 | 168.5649 | 171.8988 | 164.6311
374.0667 | 168.8206 | 172.1367 | 164.4023
375.0667 | 168.4476 | 172.0308 | 164.1158
376.0667 | 168.857 | 172.0439 | 164.4484
377.0667 | 168.7891 | 172.1388 | 164.5207
378.0667 | 168.5511 | 172.37 | 164.2513
379.0823 | 168.4704 | 172.6213 | 163.9814
380.0667 | 168.2115 | 172.6505 | 164.311
381.0667 | 168.3648 | 173.0277 | 164.3416
382.0667 | 168.2151 | 173.1811 | 164.2196
383.0667 | 168.11 | 173.3048 | 164.7508
384.0667 | 168.733 | 173.7935 | 165.3526
385.0667 | 169.112 | 174.1643 | 165.9217
386.0667 | 169.4947 | 174.5301 | 166.2198
387.0667 | 169.9055 | 174.3472 | 166.6283
388.0667 | 170.3615 | 174.6647 | 166.593
389.0667 | 170.4354 | 174.4961 | 166.786
390.0667 | 170.4777 | 174.3992 | 167.0789
391.0667 | 170.8776 | 174.8202 | 167.5723
392.0667 | 171.1386 | 175.0989 | 168.4915
393.0667 | 171.8824 | 175.5687 | 169.1513
394.0667 | 172.3628 | 176.4404 | 169.437
395.0667 | 172.3909 | 176.4998 | 169.8581
396.0667 | 172.6294 | 177.2755 | 169.3698
397.0667 | 172.8058 | 178.0191 | 169.2477
398.0667 | 173.1332 | 177.8886 | 169.2563
399.0667 | 173.4288 | 177.9673 | 169.2331
400.0667 | 173.8104 | 178.4819 | 169.4198
401.0667 | 174.0147 | 178.8902 | 169.8398
402.0667 | 174.1081 | 178.9454 | 169.7436
403.0667 | 174.3088 | 178.7078 | 169.8814
404.0823 | 175.1156 | 178.7798 | 170.2392
405.0667 | 175.4671 | 179.4557 | 171.1101
406.0667 | 175.9164 | 179.7772 | 171.2412
407.0667 | 175.9521 | 179.8871 | 171.5745
408.0667 | 176.1884 | 180.5834 | 171.4361
409.0667 | 176.7597 | 180.6867 | 171.8542
410.0667 | 177.1107 | 180.9253 | 172.4168
411.0667 | 177.7019 | 181.3978 | 172.9576
412.0667 | 177.6918 | 181.8162 | 173.2266
413.0667 | 177.5871 | 182.0566 | 173.4103
414.0667 | 177.5154 | 181.8478 | 173.0882
415.0667 | 177.7514 | 181.464 | 173.3382
416.0667 | 178.1327 | 181.8319 | 173.3633
417.0667 | 178.1819 | 182.1545 | 174.1291
418.0667 | 178.2281 | 181.9553 | 174.1656
419.0667 | 178.3527 | 182.0126 | 174.5492
420.0667 | 178.5095 | 183.0141 | 174.8004
421.0667 | 179.0077 | 182.4566 | 175.0451
422.0667 | 179.0332 | 182.8273 | 174.815
423.0667 | 179.2513 | 182.453 | 174.556
424.0667 | 179.3687 | 182.5473 | 174.5151
425.0667 | 179.1211 | 183.1679 | 174.5505
426.0667 | 179.7761 | 183.2961 | 174.8416
427.0667 | 179.6747 | 183.2055 | 174.6215
428.0667 | 179.4004 | 183.0108 | 174.4963
429.0667 | 179.3835 | 183.3444 | 174.419
430.0667 | 179.8503 | 183.5151 | 174.859
431.0667 | 179.9158 | 183.2604 | 174.7241
432.0667 | 179.6934 | 182.8801 | 174.5225
433.0667 | 179.5127 | 182.874 | 174.3153
434.0667 | 179.3776 | 182.8336 | 174.2945
435.0667 | 178.9738 | 182.5618 | 174.5762
436.0667 | 178.8257 | 182.5488 | 174.717
437.0667 | 178.6706 | 182.5664 | 174.6543
438.0667 | 179.0364 | 182.7428 | 174.9073
439.0667 | 179.1063 | 183.026 | 175.0134
440.0667 | 178.8361 | 183.3076 | 175.3514
441.0667 | 179.2193 | 183.1089 | 175.208
442.0667 | 179.7188 | 183.3337 | 175.5168
443.0667 | 179.9063 | 183.6871 | 175.5679
444.0667 | 179.8725 | 183.8642 | 176.9014
445.0667 | 179.8522 | 183.8591 | 177.8665
446.0667 | 180.1042 | 184.0245 | 177.7541
447.0667 | 180.5842 | 184.4551 | 177.7235
448.0667 | 181.3736 | 184.6648 | 177.5364
449.0667 | 181.4377 | 184.5361 | 177.7034
450.0823 | 182.0337 | 184.6445 | 178.2567
451.0667 | 182.3513 | 185.057 | 178.4266
452.0667 | 183.0206 | 185.7231 | 179.1247
453.0667 | 183.8804 | 186.0599 | 179.9813
454.0667 | 184.5655 | 186.6272 | 180.3562
455.0667 | 184.6411 | 187.0087 | 180.1859
456.0667 | 184.7186 | 187.0109 | 180.518
457.0667 | 184.8516 | 187.2898 | 180.402
458.0667 | 185.3628 | 187.8219 | 180.3101
459.0667 | 185.4276 | 188.2678 | 179.9381
460.0667 | 185.3879 | 188.3696 | 180.2371
461.0667 | 185.5985 | 188.8334 | 180.2371
462.0667 | 185.4398 | 188.9983 | 180.8311
463.0667 | 185.5377 | 189.3928 | 181.216
464.0823 | 185.7097 | 189.3591 | 180.8545
465.0667 | 186.3563 | 189.555 | 180.691
466.0667 | 186.9315 | 189.6879 | 180.8581
467.0823 | 187.0755 | 190.2217 | 181.5885
468.0667 | 187.5544 | 190.3426 | 181.628
469.0667 | 187.546 | 190.1569 | 181.9642
470.0667 | 187.9072 | 190.8274 | 182.1428
471.0667 | 188.5049 | 190.8993 | 182.4822
472.0667 | 188.5768 | 190.9037 | 182.8442
473.0667 | 188.9007 | 190.5752 | 182.62
474.0667 | 188.7547 | 190.6175 | 183.0964
475.0667 | 189.8506 | 191.1085 | 183.3602
476.0667 | 189.6109 | 191.0955 | 184.5715
477.0667 | 189.6648 | 191.0272 | 184.4392
478.0667 | 189.8701 | 190.8787 | 184.2956
479.0667 | 189.6474 | 190.8369 | 183.9687
480.0667 | 189.2045 | 190.5366 | 184.2804
481.0667 | 189.0237 | 190.2497 | 185.065
482.0667 | 189.3435 | 190.5552 | 184.8852
483.0667 | 189.8211 | 190.9391 | 185.6851
484.0667 | 189.9753 | 191.154 | 185.7635
485.0667 | 190.059 | 191.8467 | 185.5703
486.0667 | 189.951 | 192.2333 | 185.8433
487.0667 | 190.0056 | 192.6103 | 186.2779
488.0667 | 190.6281 | 192.756 | 186.4546
489.0667 | 191.0143 | 193.3477 | 186.8491
490.0667 | 191.1663 | 193.6727 | 186.902
491.0667 | 191.052 | 194.0615 | 186.761
492.0667 | 190.906 | 194.088 | 186.883
493.0667 | 190.7634 | 194.6487 | 186.6644
494.0667 | 191.0963 | 194.9399 | 186.7124
495.0667 | 191.4577 | 195.3436 | 186.9785
496.0667 | 192.3715 | 195.4314 | 187.114
497.0667 | 192.7216 | 195.5671 | 187.4261
498.0667 | 192.8645 | 195.7822 | 187.7284
499.0667 | 193.2119 | 195.9831 | 188.2024
500.0667 | 193.7281 | 196.6318 | 188.2537
501.0667 | 193.8164 | 196.7809 | 188.0418
502.0667 | 193.979 | 197.07 | 187.9782
503.0667 | 194.6353 | 197.3705 | 188.7799
504.0823 | 195.3653 | 197.3809 | 189.398
505.0667 | 195.7941 | 197.5986 | 189.9211
506.0667 | 195.6513 | 198.3723 | 189.628
507.0667 | 195.9617 | 198.7587 | 189.4331
508.0667 | 196.5651 | 198.367 | 189.9571
509.0667 | 197.205 | 198.7284 | 190.4697
510.0667 | 197.5759 | 199.0844 | 190.7314
511.0667 | 198.0337 | 199.2525 | 192.0855
512.0667 | 197.9137 | 199.2976 | 191.7573
513.0667 | 198.2792 | 199.3139 | 191.9441
514.0667 | 198.1191 | 199.563 | 191.8935
515.0667 | 198.5033 | 199.7673 | 192.1002
516.0667 | 197.8012 | 199.6638 | 192.2116
517.0667 | 197.6961 | 199.5291 | 191.9593
518.0667 | 198.1036 | 199.792 | 192.208
519.0667 | 198.0583 | 200.2802 | 192.423
520.0667 | 198.4005 | 200.4501 | 192.8705
521.0667 | 198.6845 | 200.7819 | 193.0471
522.0667 | 199.4509 | 200.8028 | 193.2302
523.0667 | 199.7818 | 200.7552 | 193.6544
524.0667 | 200.4277 | 201.0872 | 193.9313
525.0667 | 200.1583 | 201.0417 | 194.3161
526.0667 | 199.8138 | 200.8592 | 193.9683
527.0667 | 200.0783 | 200.7589 | 194.4467
528.0667 | 200.124 | 200.9976 | 194.848
529.0667 | 200.1681 | 201.3284 | 195.5382
530.0667 | 200.663 | 201.9086 | 195.269
531.0667 | 200.6827 | 201.6662 | 194.7873
532.0667 | 201.1164 | 202.1757 | 194.5211
533.0667 | 201.0697 | 202.8905 | 194.7075
534.0667 | 200.8104 | 203.0647 | 194.8424
535.0667 | 201.0339 | 203.6902 | 194.7592
536.0667 | 200.8761 | 203.291 | 195.0402
537.0667 | 201.0902 | 203.5702 | 194.9679
538.0667 | 201.3655 | 203.5396 | 195.3203
539.0667 | 202.0208 | 203.964 | 196.122
540.0667 | 202.4556 | 204.0968 | 196.9225
541.0667 | 202.7022 | 204.4861 | 197.2278
542.0667 | 202.7034 | 204.785 | 197.4587
543.0667 | 202.4792 | 205.2459 | 197.309
544.0667 | 202.5337 | 205.4346 | 197.5494
545.0667 | 202.6023 | 205.4019 | 197.2613
546.0667 | 203.0572 | 205.1974 | 197.18
547.0667 | 203.7675 | 205.4019 | 197.2995
548.0667 | 203.9057 | 206.238 | 197.5563
549.0667 | 203.9829 | 206.8496 | 197.7353
550.0667 | 204.9489 | 207.5707 | 197.6059
551.0667 | 205.7782 | 207.9618 | 197.8523
552.0667 | 205.337 | 208.1932 | 197.8536
553.0667 | 205.2522 | 208.2358 | 198.1287
554.0667 | 205.1766 | 208.1529 | 198.1694
555.0667 | 205.2348 | 207.9012 | 198.128
556.0667 | 205.3773 | 207.9244 | 198.0992
557.0667 | 205.9335 | 207.5431 | 197.8223
558.0667 | 206.1272 | 207.6943 | 197.8423
559.0667 | 205.8345 | 207.5517 | 197.6424
560.0667 | 205.9088 | 207.6665 | 197.7603
561.0667 | 205.9436 | 207.6949 | 198.2048
562.0667 | 205.9867 | 208.0906 | 198.9025
563.0667 | 206.2237 | 208.1457 | 199.2592
564.0667 | 206.5111 | 208.6201 | 199.3045
565.0667 | 206.6571 | 208.7517 | 199.221
566.0667 | 206.363 | 208.9947 | 199.7744
567.0667 | 206.19 | 209.0476 | 200.1357
568.0667 | 206.4436 | 209.2413 | 200.1659
569.0667 | 206.2872 | 209.2402 | 200.4667
570.0667 | 206.6596 | 209.7057 | 199.9913
571.0667 | 206.8364 | 210.2649 | 200.3721
572.0667 | 206.6016 | 210.1042 | 200.9716
573.0667 | 206.4398 | 210.0195 | 201.3588
574.0667 | 206.5354 | 209.7919 | 201.0076
575.0667 | 206.1736 | 209.7255 | 200.8628
576.0667 | 205.9527 | 209.7453 | 200.4387
577.0667 | 206.0011 | 209.6243 | 200.2043
578.0667 | 206.4192 | 209.3057 | 200.4356
579.0667 | 206.1374 | 209.4514 | 200.0403
580.0667 | 206.0347 | 209.3014 | 199.8999
581.0667 | 205.9329 | 209.6827 | 200.3146
582.0667 | 206.1404 | 209.9611 | 200.9082
583.0667 | 205.9995 | 209.9724 | 201.3445
584.0667 | 205.9106 | 209.6174 | 201.1845
585.0667 | 205.5881 | 209.7016 | 200.9772
586.0667 | 205.9393 | 209.6447 | 200.8312
587.0667 | 206.103 | 210.0125 | 200.9355
588.0667 | 206.495 | 210.6795 | 200.8988
589.0667 | 206.7933 | 210.6644 | 200.7696
590.0667 | 206.8531 | 210.6321 | 200.7621
591.0667 | 206.6852 | 210.678 | 201.1908
592.0667 | 206.5005 | 210.9002 | 201.7815
593.0667 | 206.53 | 211.123 | 201.8594
594.0667 | 206.687 | 211.1455 | 201.5668
595.0667 | 206.9099 | 211.3904 | 201.351
596.0667 | 206.8746 | 211.5259 | 201.2727
597.0667 | 206.8516 | 211.0621 | 201.2547
598.0667 | 206.4427 | 211.0532 | 201.2925
599.0667 | 206.0539 | 211.3544 | 201.4205
600.0667 | 205.6389 | 211.3471 | 201.6177
601.0667 | 205.5245 | 211.4712 | 201.699
602.0667 | 205.6035 | 211.5769 | 202.2597
603.0667 | 205.4623 | 211.7222 | 202.7568
604.0667 | 205.4479 | 211.9349 | 202.5345
605.0667 | 205.5004 | 211.9817 | 202.8112
606.0667 | 206.2683 | 212.389 | 202.9727
607.0667 | 206.1726 | 212.5673 | 203.0278
608.0667 | 206.6609 | 212.7213 | 202.9149
609.0667 | 207.206 | 212.9526 | 203.4091
610.0667 | 207.4569 | 212.979 | 203.3919
611.0667 | 207.7717 | 213.0584 | 203.52
612.0667 | 207.8626 | 213.288 | 203.8536
613.0667 | 207.9009 | 213.9399 | 204.1718
614.0667 | 208.007 | 214.0975 | 204.1495
615.0667 | 208.3132 | 213.837 | 203.9819
616.0667 | 208.5947 | 213.5964 | 204.8359
617.0667 | 208.4344 | 213.4786 | 205.7811
618.0667 | 208.4225 | 213.3099 | 205.3575
619.0667 | 208.7328 | 213.1515 | 205.1639
620.0667 | 209.0712 | 213.3152 | 204.9756
621.0667 | 208.8474 | 213.0834 | 205.3906
622.0667 | 208.7215 | 213.073 | 205.2229
623.0667 | 208.6838 | 213.3587 | 205.4508
624.0667 | 208.965 | 213.7541 | 205.8288
625.0667 | 208.7634 | 214.0904 | 206.1319
626.0667 | 209.0781 | 213.9952 | 206.1629
627.0667 | 209.4022 | 213.7503 | 205.9096
628.0667 | 209.2444 | 213.8763 | 205.7485
629.0667 | 208.961 | 214.007 | 205.7531
630.0667 | 209.0569 | 213.8696 | 206.1383
631.0667 | 209.4321 | 213.6174 | 206.4798
632.0667 | 209.735 | 214.0496 | 206.87
633.0667 | 209.4626 | 214.0571 | 207.0643
634.0667 | 209.2569 | 214.6876 | 206.7898
635.0667 | 209.246 | 214.9776 | 207.1424
636.0667 | 209.339 | 214.7895 | 207.2383
637.0667 | 209.3822 | 214.7424 | 207.4413
638.0667 | 208.7871 | 214.6482 | 207.2726
639.0823 | 208.5303 | 214.498 | 207.5106
640.0667 | 208.4281 | 214.5636 | 207.3943
641.0667 | 208.452 | 214.4594 | 207.1276
642.0667 | 208.4897 | 214.5267 | 207.1519
643.0667 | 208.5545 | 214.4842 | 207.3662
644.0667 | 208.1792 | 214.3823 | 207.7497
645.0667 | 207.8796 | 214.4014 | 207.5014
646.0667 | 207.5692 | 214.3257 | 207.5334
647.0667 | 207.2966 | 214.3794 | 208.1178
648.0667 | 207.7246 | 214.193 | 208.3339
649.0667 | 207.7224 | 214.0492 | 208.4337
650.0667 | 207.8983 | 213.7926 | 208.0062
651.0667 | 208.1453 | 214.3545 | 208.1719
652.0667 | 208.4491 | 214.4588 | 208.7591
653.0667 | 208.6476 | 214.7192 | 209.2083
654.0823 | 208.9302 | 214.6164 | 209.9479
655.0667 | 208.8052 | 214.4068 | 210.243
656.0667 | 208.6417 | 214.2549 | 210.2927
657.0667 | 208.3 | 214.5973 | 209.9863
658.0667 | 207.9786 | 214.6039 | 209.589
659.0667 | 208.2531 | 214.8605 | 209.3919
660.0667 | 208.4048 | 214.5139 | 209.3303
661.0667 | 208.5305 | 215.1483 | 209.3346
662.0667 | 208.5554 | 215.4311 | 209.4021
663.0667 | 208.9909 | 214.8457 | 209.1568
664.0667 | 208.704 | 214.6346 | 209.2191
665.0667 | 208.3679 | 214.5443 | 209.1319
666.0667 | 208.2208 | 214.2542 | 209.1755
667.0667 | 207.8007 | 214.551 | 209.6664
668.0667 | 207.4088 | 214.6798 | 209.6712
669.0667 | 206.9705 | 214.2588 | 209.8207
670.0667 | 206.337 | 213.6404 | 209.2619
671.0667 | 206.1458 | 213.8578 | 209.186
672.0667 | 206.5099 | 213.6435 | 209.0867
673.0667 | 206.5678 | 213.595 | 208.6991
674.0667 | 206.4598 | 213.6954 | 208.2739
675.0667 | 206.2291 | 213.7347 | 208.0428
676.0667 | 206.0709 | 213.3607 | 208.021
677.0667 | 206.1627 | 213.5422 | 207.4807
678.0667 | 206.5489 | 213.5169 | 207.1264
679.0823 | 206.5893 | 213.3006 | 207.2134
680.0667 | 206.843 | 212.719 | 207.3909
681.0667 | 206.6826 | 212.1393 | 207.3126
682.0667 | 206.8131 | 211.7632 | 206.7081
683.0667 | 207.0438 | 212.217 | 206.3555
684.0667 | 207.6509 | 212.4039 | 206.3967
685.0667 | 207.8633 | 212.3581 | 206.3272
686.0667 | 208.2839 | 212.368 | 206.6475
687.0667 | 208.4107 | 213.2258 | 206.9262
688.0667 | 208.6361 | 213.7499 | 207.1156
689.0667 | 208.3761 | 214.1534 | 207.3651
690.0667 | 208.7816 | 214.4593 | 207.0103
691.0667 | 209.0667 | 215.0083 | 207.7432
692.0667 | 209.5838 | 215.0531 | 208.3109
693.0667 | 209.9945 | 215.4378 | 209.0319
694.0667 | 209.893 | 215.2841 | 209.0448
695.0667 | 210.0753 | 215.0949 | 208.7742
696.0667 | 210.1911 | 214.7877 | 209.3124
697.0667 | 209.889 | 215.2589 | 208.8392
698.0667 | 209.4926 | 214.9503 | 208.6502
699.0667 | 209.0518 | 214.8696 | 208.5343
700.0667 | 208.7235 | 214.6907 | 208.5526
701.0667 | 208.3748 | 214.4405 | 208.8067
702.0667 | 208.5787 | 214.592 | 208.7635
703.0667 | 208.5595 | 214.2998 | 208.5478
704.0667 | 208.5532 | 214.06 | 208.7309
705.0667 | 208.4871 | 213.9441 | 208.4569
706.0667 | 208.2042 | 214.0014 | 208.5908
707.0667 | 207.7497 | 213.3975 | 208.7651
708.0667 | 207.5828 | 213.3512 | 208.7098
709.0667 | 207.7405 | 213.0838 | 208.5658
710.0667 | 208.1339 | 213.2662 | 208.5057
711.0667 | 208.0234 | 213.1757 | 208.8833
712.0667 | 207.813 | 213.1222 | 209.0464
713.0667 | 207.7807 | 213.1974 | 209.1984
714.0667 | 207.4593 | 213.2495 | 209.3587
715.0667 | 207.5845 | 212.8608 | 209.3294
716.0667 | 207.6979 | 212.628 | 208.888
717.0667 | 207.6018 | 213.1386 | 208.7219
718.0667 | 207.4024 | 212.7935 | 208.2765
719.0667 | 206.9411 | 212.7581 | 207.9087
720.0667 | 207.0471 | 212.9133 | 208.1533
721.0667 | 206.9362 | 212.8525 | 208.2212
722.0667 | 206.6021 | 212.6081 | 208.1619
723.0667 | 206.6607 | 212.6411 | 208.1064
724.0667 | 206.5276 | 212.3727 | 207.9492
725.0667 | 206.3621 | 212.2917 | 207.5736
726.0667 | 206.4047 | 212.2182 | 207.1594
727.0667 | 207.654 | 212.6356 | 207.3214
728.0667 | 208.3973 | 213.2348 | 207.6821
729.0667 | 209.1201 | 213.8066 | 207.9615
730.0823 | 209.8092 | 214.0125 | 208.3076
731.0823 | 210.2235 | 214.0689 | 208.4108
732.0667 | 210.296 | 214.0681 | 208.3162
733.0667 | 209.9853 | 213.8206 | 208.4744
734.0667 | 209.7115 | 213.694 | 208.3725
735.0667 | 209.7999 | 213.8312 | 208.3093
736.0667 | 209.7527 | 213.861 | 208.1034
737.0667 | 209.5198 | 213.5431 | 208.0616
738.0667 | 209.3478 | 213.3355 | 207.9962
739.0823 | 209.0821 | 213.4114 | 208.3235
740.0667 | 209.0569 | 213.4742 | 208.1623
741.0667 | 209.5976 | 213.4808 | 208.1439
742.0667 | 209.5496 | 213.7514 | 208.2643
743.0667 | 209.5684 | 213.7079 | 208.4238
744.0667 | 209.5397 | 213.607 | 208.5306
745.0667 | 209.1255 | 213.5408 | 208.4483
746.0667 | 208.7862 | 213.4938 | 208.6549
747.0667 | 208.5723 | 213.061 | 208.553
748.0667 | 208.2691 | 213.0029 | 208.2776
749.0667 | 207.745 | 212.7767 | 207.8802
750.0667 | 207.3552 | 212.4935 | 207.3845
751.0667 | 206.9374 | 212.1072 | 206.9275
752.0667 | 207.5052 | 211.7773 | 206.6199
753.0667 | 207.3736 | 211.5116 | 206.3294
754.0667 | 207.414 | 211.8242 | 206.2466
755.0667 | 207.2818 | 211.9264 | 206.1117
756.0667 | 206.9518 | 211.7254 | 206.0471
757.0667 | 206.648 | 212.3634 | 206.2258
758.0667 | 206.6344 | 212.1613 | 206.9455
759.0667 | 206.7198 | 212.2426 | 206.6691
760.0667 | 206.7774 | 212.1619 | 206.3467
761.0667 | 206.6652 | 212.1852 | 206.143
762.0667 | 206.3407 | 212.0859 | 205.9039
763.0667 | 206.3603 | 212.0486 | 205.9242
764.0667 | 206.2609 | 211.9527 | 205.6057
765.0667 | 206.5058 | 212.0134 | 206.0183
766.0667 | 206.7182 | 212.2511 | 206.0313
767.0667 | 207.0292 | 212.2949 | 205.7724
768.0667 | 206.7557 | 212.2401 | 205.6595
769.0667 | 206.523 | 212.0563 | 205.4679
770.0667 | 206.309 | 212.0036 | 206.1099
771.0667 | 206.3265 | 212.0329 | 205.9291
772.0667 | 206.1807 | 212.0269 | 206.6562
773.0667 | 205.9939 | 212.1115 | 206.8679
774.0667 | 206.071 | 212.186 | 206.7218
775.0667 | 206.3149 | 212.1418 | 206.5815
776.0667 | 206.2416 | 211.9881 | 206.2657
777.0667 | 206.1568 | 211.6571 | 206.183
778.0667 | 205.9944 | 211.7893 | 206.0832
779.0823 | 206.2104 | 211.5192 | 205.9674
780.0667 | 206.0547 | 211.4477 | 205.9582
781.0667 | 205.7766 | 211.7067 | 205.9306
782.0667 | 205.8605 | 211.526 | 206.0519
783.0667 | 205.776 | 211.2768 | 205.7922
784.0667 | 205.9312 | 211.1013 | 205.8248
785.0667 | 206.0545 | 210.7319 | 206.4089
786.0667 | 206.3808 | 210.4855 | 206.7301
787.0667 | 206.1926 | 210.4186 | 206.3229
788.0667 | 206.2422 | 210.4601 | 206.3282
789.0667 | 206.2853 | 210.563 | 206.458
790.0667 | 206.4155 | 210.469 | 206.2929
791.0667 | 206.7581 | 210.5786 | 205.9669
792.0667 | 206.9368 | 210.5783 | 205.5601
793.0667 | 207.6218 | 210.6786 | 205.5005
794.0823 | 207.7547 | 210.7588 | 205.3724
795.0667 | 207.8276 | 210.4064 | 205.1046
796.0667 | 207.7395 | 210.2365 | 204.7302
797.0667 | 207.8319 | 210.5256 | 204.5794
798.0667 | 208.4402 | 210.6475 | 204.6948
799.0667 | 208.762 | 210.5754 | 204.498
800.0667 | 208.6855 | 210.4404 | 204.2765
801.0667 | 208.6808 | 210.6983 | 204.3113
802.0667 | 208.6437 | 210.6734 | 204.3881
803.0667 | 208.4011 | 211.2615 | 204.3144
804.0667 | 208.2681 | 211.0327 | 204.0849
805.0667 | 208.13 | 210.8106 | 204.0453
806.0667 | 208.136 | 210.6291 | 204.7241
807.0667 | 207.992 | 210.7938 | 204.7318
808.0667 | 207.9519 | 210.6251 | 205.1285
809.0667 | 207.5873 | 210.7265 | 204.7185
810.0667 | 207.1903 | 210.8954 | 204.6147
811.0667 | 206.9184 | 210.7666 | 204.312
812.0667 | 206.9721 | 210.6316 | 203.9735
813.0667 | 206.9638 | 210.3429 | 203.8706
814.0667 | 207.0973 | 210.2008 | 203.6915
815.0667 | 207.0032 | 209.9062 | 203.7846
816.0667 | 206.6323 | 210.212 | 204.0247
817.0667 | 207.0763 | 209.9355 | 204.3669
818.0667 | 207.2007 | 209.741 | 204.1908
819.0667 | 207.3065 | 209.5063 | 204.9831
820.0667 | 207.3095 | 209.2166 | 204.8793
821.0667 | 207.2101 | 209.2536 | 204.6845
822.0667 | 206.9067 | 208.8615 | 204.2951
823.0667 | 206.866 | 208.5481 | 204.1595
824.0667 | 206.6342 | 208.652 | 203.8372
825.0667 | 206.5678 | 208.8983 | 204.3015
826.0667 | 206.3342 | 208.7815 | 204.1973
827.0667 | 206.2102 | 208.5534 | 203.9014
828.0667 | 206.0236 | 209.3214 | 203.5759
829.0667 | 206.6285 | 209.4232 | 203.8262
830.0667 | 206.8603 | 209.341 | 203.7066
831.0667 | 206.8485 | 209.1993 | 203.6147
832.0667 | 206.6585 | 209.6968 | 203.584
833.0667 | 206.2634 | 209.7139 | 203.8436
834.0667 | 206.0697 | 209.5312 | 204.2429
835.0667 | 205.8823 | 209.5808 | 204.3738
836.0667 | 205.6718 | 209.6049 | 204.8009
837.0667 | 205.7104 | 209.578 | 204.3937
838.0667 | 205.6211 | 209.3853 | 204.0935
839.0667 | 205.6118 | 209.1338 | 203.8374
840.0667 | 205.5488 | 208.9274 | 203.6642
841.0667 | 205.7632 | 208.5672 | 203.6411
842.0667 | 205.7275 | 208.4051 | 203.3832
843.0667 | 205.5842 | 208.3429 | 203.4264
844.0667 | 205.7216 | 208.4085 | 203.2328
845.0667 | 205.6467 | 208.4686 | 203.2236
846.0667 | 205.3442 | 208.2747 | 203.3438
847.0667 | 204.9999 | 208.2015 | 203.6693
848.0667 | 204.664 | 207.9978 | 203.6276
849.0667 | 205.0137 | 208.088 | 203.7449
850.0667 | 204.7995 | 208.1321 | 203.6675
851.0667 | 204.7527 | 208.242 | 203.78
852.0667 | 204.7345 | 208.4806 | 203.8227
853.0667 | 204.8819 | 208.4808 | 203.9946
854.0667 | 205.298 | 209.1271 | 204.655
855.0667 | 205.7026 | 209.3846 | 205.3107
856.0667 | 206.0842 | 209.4304 | 205.635
857.0667 | 206.1742 | 209.7358 | 205.8356
858.0667 | 206.4575 | 210.2455 | 205.984
859.0667 | 206.5837 | 210.6594 | 205.918
860.0667 | 206.5918 | 210.986 | 206.4453
861.0667 | 206.7885 | 211.4381 | 206.8
862.0823 | 206.7332 | 211.2468 | 206.8792
863.0667 | 206.5525 | 210.8787 | 206.8217
864.0667 | 206.2618 | 210.7398 | 207.0303
865.0667 | 206.6351 | 211.4203 | 207.084
866.0667 | 206.9064 | 211.2045 | 207.2483
867.0667 | 206.595 | 211.051 | 207.697
868.0667 | 206.456 | 211.0368 | 207.5159
869.0667 | 206.4446 | 210.9607 | 207.2599
870.0667 | 206.5775 | 211.0151 | 207.4595
871.0667 | 206.9864 | 211.3389 | 207.4029
872.0667 | 207.085 | 211.1126 | 207.1097
873.0667 | 207.1578 | 211.131 | 207.2083
874.0667 | 207.0668 | 210.915 | 207.0143
875.0667 | 207.2886 | 210.7631 | 207.2309
876.0667 | 207.3662 | 210.6211 | 207.0015
877.0667 | 207.3015 | 210.5082 | 206.9568
878.0667 | 207.2015 | 210.4802 | 207.1477
879.0667 | 206.9012 | 210.487 | 207.0382
880.0667 | 206.7764 | 210.133 | 207.0932
881.0667 | 206.9737 | 210.4106 | 207.1448
882.0667 | 207.0171 | 210.5776 | 207.4712
883.0667 | 207.4808 | 210.9713 | 208.1484
884.0667 | 208.1168 | 211.6138 | 208.0371
885.0667 | 208.6812 | 211.9477 | 208.0748
886.0667 | 208.8257 | 212.5829 | 208.3257
887.0667 | 208.8686 | 212.6151 | 208.6885
888.0667 | 209.1929 | 213.1493 | 209.0039
889.0667 | 210.6431 | 213.2748 | 209.0721
890.0667 | 210.9051 | 213.4403 | 209.2839
891.0667 | 210.8963 | 213.6597 | 209.5141
892.0667 | 211.1178 | 214.2626 | 209.63
893.0667 | 211.5092 | 214.2905 | 210.0658
894.0667 | 211.5968 | 214.4032 | 210.5793
895.0667 | 211.6711 | 214.7951 | 210.6984
896.0667 | 211.781 | 214.5285 | 210.7574
897.0667 | 211.9553 | 214.2384 | 210.5872
898.0667 | 212.4964 | 214.0028 | 210.6578
899.0667 | 212.4083 | 213.9489 | 210.8635
900.0667 | 212.2868 | 214.3023 | 210.6603
901.0667 | 212.1221 | 214.5105 | 210.468
902.0667 | 212.2308 | 214.5162 | 210.6592
903.0667 | 212.1292 | 214.4877 | 210.7989
904.0667 | 211.8546 | 214.4849 | 210.5754
905.0667 | 211.725 | 214.637 | 210.4862
906.0667 | 211.8356 | 214.2761 | 210.4119
907.0667 | 211.653 | 213.9651 | 210.4516
908.0667 | 211.5712 | 213.9071 | 210.3735
909.0667 | 211.4834 | 213.7032 | 210.5511
910.0667 | 211.4871 | 213.7447 | 210.7287
911.0667 | 211.459 | 213.6783 | 211.2593
912.0667 | 211.3301 | 213.7931 | 211.3655
913.0667 | 211.64 | 213.6783 | 211.3871
914.0823 | 211.7766 | 214.1492 | 210.9944
915.0667 | 211.6966 | 214.1534 | 210.867
916.0667 | 211.6023 | 214.2302 | 210.5027
917.0667 | 211.9552 | 214.4778 | 210.4853
918.0667 | 212.2459 | 215.4075 | 210.9792
919.0667 | 212.6148 | 215.7185 | 211.7151
920.0667 | 213.2287 | 216.4773 | 212.2929
921.0667 | 213.8046 | 217.0934 | 212.7515
922.0667 | 214.024 | 217.2252 | 212.972
923.0667 | 213.8321 | 217.2923 | 212.9681
924.0823 | 213.6776 | 217.6832 | 212.6367
925.0667 | 213.5356 | 217.5189 | 212.7665
926.0667 | 213.1967 | 217.3832 | 212.7731
927.0667 | 212.782 | 217.1923 | 212.9617
928.0667 | 213.0542 | 216.8366 | 213.0389
929.0823 | 213.588 | 216.6787 | 213.0257
930.0667 | 213.2705 | 216.7188 | 212.7051
931.0667 | 212.9031 | 216.9104 | 212.4415
932.0667 | 212.809 | 216.9049 | 212.2448
933.0667 | 212.9172 | 216.7062 | 212.2577
934.0667 | 213.1508 | 216.6425 | 212.1213
935.0667 | 213.138 | 216.5933 | 211.8206
936.0667 | 213.5124 | 216.7123 | 211.683
937.0667 | 213.2823 | 216.2449 | 211.3427
938.0667 | 213.1589 | 216.2307 | 211.363
939.0667 | 212.9904 | 215.9343 | 211.5553
940.0667 | 212.9349 | 215.6723 | 211.5424
941.0667 | 212.7913 | 215.7516 | 211.875
942.0667 | 213.5102 | 216.0956 | 211.9472
943.0667 | 214.2725 | 216.8371 | 212.5432
944.0667 | 214.4109 | 217.2487 | 213.1254
945.0823 | 214.8306 | 217.5729 | 213.3717
946.0667 | 214.9153 | 218.1192 | 213.545
947.0667 | 214.8187 | 218.2836 | 213.781
948.0667 | 214.5665 | 218.2218 | 213.7213
949.0667 | 214.4549 | 217.9207 | 213.6653
950.0667 | 214.3462 | 217.658 | 213.5055
951.0667 | 214.2757 | 217.6874 | 213.3965
952.0667 | 214.2815 | 217.602 | 213.3022
953.0667 | 214.2315 | 217.4542 | 213.4921
954.0823 | 214.4156 | 217.5563 | 213.659
955.0667 | 214.4519 | 217.5149 | 214.0449
956.0667 | 214.6495 | 217.4836 | 214.2894
957.0667 | 214.4036 | 217.2233 | 214.2693
958.0667 | 214.7507 | 217.4503 | 214.1529
959.0667 | 214.9915 | 217.7576 | 214.3342
960.0667 | 215.3507 | 218.1731 | 214.8112
961.0667 | 216.1101 | 219.2717 | 215.4106
962.0667 | 217.0799 | 220.3127 | 215.9143
963.0667 | 217.834 | 221.6577 | 216.537
964.0667 | 218.8387 | 223.5095 | 217.0284
965.0667 | 219.5949 | 224.106 | 217.999
966.0667 | 220.2144 | 224.763 | 219.3318
967.0667 | 221.0256 | 225.7361 | 219.9437
968.0667 | 221.9877 | 226.7563 | 221.0269
969.0823 | 222.811 | 227.5868 | 221.8121
970.0667 | 223.6196 | 227.897 | 222.2147
971.0667 | 224.4321 | 228.6443 | 222.635
972.0667 | 225.152 | 229.5471 | 223.3995
973.0667 | 225.933 | 230.6419 | 223.7399
974.0667 | 226.4198 | 231.3416 | 224.9183
975.0667 | 227.0933 | 232.137 | 225.9369
976.0667 | 228.5551 | 233.5206 | 226.5271
977.0667 | 229.8444 | 234.5356 | 227.3858
978.0667 | 231.1312 | 235.6431 | 229.1923
979.0667 | 231.7669 | 236.2555 | 230.5366
980.0667 | 232.3699 | 236.7279 | 231.1283
981.0667 | 233.1543 | 237.1593 | 231.7151
982.0667 | 233.7696 | 237.8512 | 232.1386
983.0667 | 234.1846 | 238.4142 | 232.5108
984.0823 | 235.0842 | 239.2971 | 233.6901
985.0667 | 236.0215 | 240.2107 | 233.9579
986.0667 | 237.0905 | 240.9856 | 234.3031
987.0667 | 237.5184 | 241.5699 | 234.7245
988.0667 | 237.9815 | 242.089 | 235.6035
989.0667 | 239.1888 | 242.8817 | 236.4248
990.0667 | 240.29 | 243.6502 | 237.0753
991.0667 | 240.9663 | 244.6903 | 238.3854
992.0667 | 243.3658 | 245.1502 | 239.4766
993.0667 | 244.5879 | 245.775 | 240.1221
994.0667 | 245.5766 | 246.8623 | 240.9598
995.0667 | 246.2078 | 247.5509 | 242.4804
996.0667 | 246.4136 | 248.554 | 243.3183
997.0667 | 248.0475 | 250.1898 | 244.9489
998.0667 | 249.3094 | 251.2381 | 246.4289
999.0667 | 250.5539 | 253.3788 | 247.2412
1000.0667 | 251.8274 | 254.3773 | 248.5782
1001.0667 | 253.3843 | 256.7924 | 250.2255
1002.0667 | 254.3574 | 256.8408 | 250.6857
1003.0667 | 255.5852 | 257.7307 | 251.9047
1004.0667 | 256.6488 | 258.6672 | 253.9481
1005.0667 | 258.0706 | 259.8684 | 254.0997
1006.0667 | 259.6817 | 261.6538 | 255.2918
1007.0667 | 260.8483 | 263.1716 | 257.0887
1008.0667 | 261.5553 | 263.8153 | 258.1518
1009.0823 | 262.2626 | 264.7825 | 258.502
1010.0667 | 262.9115 | 265.5106 | 259.1776
1011.0667 | 264.4986 | 265.9441 | 259.5177
1012.0667 | 264.4546 | 266.6639 | 259.8979
1013.0667 | 264.8918 | 267.0372 | 260.6019
1014.0823 | 265.6811 | 267.8894 | 261.6565
1015.0667 | 266.0044 | 268.8617 | 261.9359
1016.0667 | 266.3314 | 268.8736 | 261.8726
1017.0667 | 266.4384 | 268.9498 | 261.6595
1018.0667 | 266.2627 | 269.4208 | 261.6079
1019.0667 | 266.3117 | 269.3437 | 262.1648
1020.0667 | 266.2173 | 269.0132 | 262.8345
1021.0667 | 266.327 | 269.1271 | 262.5869
1022.0667 | 266.4401 | 269.0824 | 262.4883
1023.0667 | 266.3924 | 269.0782 | 262.5933
1024.0667 | 266.6405 | 269.4251 | 262.9076
1025.0667 | 266.3626 | 269.2901 | 263.4681
1026.0667 | 266.5436 | 269.8796 | 263.3333
1027.0667 | 266.3079 | 269.8175 | 263.4389
1028.0667 | 265.7989 | 269.4845 | 264.2615
1029.0667 | 265.3755 | 269.2542 | 264.0366
1030.0667 | 265.4549 | 269.4244 | 263.5691
1031.0667 | 265.5616 | 269.3788 | 263.9698
1032.0667 | 265.637 | 269.1341 | 264.6668
1033.0667 | 265.5262 | 269.0469 | 264.7263
1034.0667 | 265.536 | 269.1327 | 264.9673
1035.0667 | 265.5398 | 269.2719 | 264.8986
1036.0667 | 265.5677 | 269.6374 | 264.6752
1037.0667 | 265.9247 | 269.9818 | 265.1777
1038.0667 | 266.0722 | 269.7631 | 265.4169
1039.0667 | 266.0863 | 270.1533 | 265.1138
1040.0667 | 266.4127 | 270.5635 | 265.5873
1041.0667 | 266.3388 | 270.0302 | 265.674
1042.0667 | 265.6681 | 270.0412 | 266.094
1043.0667 | 265.5619 | 270.1091 | 266.0826
1044.0823 | 266.0912 | 270.2149 | 266.8969
1045.0667 | 266.1078 | 270.3298 | 267.0635
1046.0667 | 265.9832 | 270.3466 | 267.4732
1047.0667 | 266.5114 | 270.4288 | 267.6969
1048.0667 | 266.5747 | 270.5253 | 267.5786
1049.0667 | 266.339 | 271.069 | 267.6223
1050.0667 | 266.1803 | 271.4165 | 267.2664
1051.0667 | 266.3104 | 271.4397 | 267.6734
1052.0667 | 266.5269 | 271.5272 | 268.1031
1053.0667 | 266.4073 | 271.5868 | 268.1768
1054.0667 | 266.5215 | 271.7021 | 268.5498
1055.0667 | 266.8398 | 272.0122 | 269.0381
1056.0667 | 267.7545 | 272.186 | 269.8891
1057.0667 | 268.5415 | 272.4373 | 269.5205
1058.0667 | 268.6108 | 273.0798 | 270.4275
1059.0667 | 269.163 | 273.5087 | 270.8355
1060.0667 | 269.9639 | 273.9325 | 271.0675
1061.0667 | 270.3741 | 274.3983 | 270.7731
1062.0667 | 270.6431 | 274.5528 | 271.3003
1063.0667 | 270.8288 | 274.8874 | 271.2694
1064.0667 | 271.1192 | 275.5504 | 271.3875
1065.0667 | 271.797 | 275.9641 | 272.4079
1066.0667 | 271.6902 | 276.5771 | 272.4824
1067.0667 | 272.21 | 277.9222 | 273.0242
1068.0667 | 272.4628 | 277.7054 | 273.045
1069.0823 | 272.4912 | 278.3265 | 273.329
1070.0667 | 272.5861 | 277.9658 | 273.6373
1071.0667 | 272.6529 | 278.0137 | 273.43
1072.0667 | 273.3 | 278.0443 | 273.2774
1073.0667 | 273.9011 | 277.9129 | 273.5736
1074.0823 | 273.9858 | 277.879 | 273.9147
1075.0667 | 274.3849 | 278.3232 | 273.7993
1076.0667 | 274.6729 | 278.4868 | 274.3906
1077.0667 | 275.7226 | 279.1646 | 274.5452
1078.0667 | 275.4999 | 279.5518 | 275.3394
1079.0667 | 275.6323 | 279.4923 | 275.7433
1080.0667 | 275.9165 | 279.52 | 275.4417
1081.0667 | 276.3398 | 279.873 | 275.5717
1082.0667 | 276.3784 | 280.1805 | 276.5938
1083.0667 | 276.615 | 280.3739 | 276.4395
1084.0667 | 277.5702 | 280.7018 | 277.0166
1085.0667 | 277.5404 | 280.7438 | 277.3482
1086.0667 | 277.4712 | 280.7955 | 277.5814
1087.0667 | 277.8208 | 281.0787 | 277.6541
1088.0667 | 278.0187 | 281.88 | 278.1145
1089.0667 | 278.6787 | 282.4849 | 279.3043
1090.0667 | 278.399 | 282.8038 | 280.232
1091.0667 | 278.4874 | 282.8847 | 280.3569
1092.0667 | 278.5729 | 283.0115 | 279.713
1093.0667 | 278.5257 | 283.1527 | 279.5127
1094.0667 | 278.9131 | 283.0928 | 280.5386
1095.0667 | 279.3934 | 284.0267 | 280.9002
1096.0667 | 280.1995 | 284.7461 | 281.3398
1097.0667 | 280.0805 | 285.507 | 281.0909
1098.0667 | 280.5546 | 286.9658 | 281.1083
1099.0667 | 281.2053 | 287.5629 | 281.5389
1100.0667 | 281.5192 | 287.9783 | 281.4445
1101.0667 | 281.498 | 288.6581 | 281.6272
1102.0667 | 281.8021 | 288.7234 | 282.5246
1103.0667 | 282.0619 | 289.2989 | 282.9647
1104.0667 | 282.4917 | 289.8595 | 284.376
1105.0667 | 282.8244 | 290.8453 | 284.6385
1106.0667 | 282.9119 | 291.3627 | 284.7732
1107.0823 | 283.1033 | 291.7118 | 286.4162
1108.0823 | 283.3219 | 292.0779 | 286.3668
1109.0823 | 283.1413 | 291.9187 | 286.332
1110.0667 | 283.2373 | 291.76 | 286.2415
1111.0823 | 282.9197 | 291.4115 | 285.9203
1112.0823 | 282.864 | 291.1842 | 285.9199
1113.0823 | 283.0457 | 291.2859 | 285.9877
1114.0823 | 283.2056 | 291.0775 | 285.0666
1115.0667 | 283.457 | 291.109 | 284.7499
1116.0667 | 284.3105 | 290.9683 | 284.7234
1117.0667 | 284.285 | 290.858 | 284.2705
1118.0667 | 283.8328 | 290.9626 | 283.9886
1119.0667 | 283.8476 | 290.8502 | 284.0723
1120.0667 | 283.8766 | 290.5685 | 284.279
1121.0667 | 283.9646 | 290.4459 | 284.3152
1122.0667 | 283.9751 | 290.8453 | 284.0516
1123.0667 | 284.5938 | 290.5883 | 284.0672
1124.0823 | 284.5916 | 290.6629 | 284.4715
1125.0667 | 284.9461 | 291.4146 | 284.7804
1126.0667 | 285.1214 | 291.3581 | 285.1493
1127.0667 | 284.7312 | 291.4695 | 285.3
1128.0667 | 284.4561 | 291.3365 | 285.4983
1129.0667 | 284.2113 | 291.7108 | 285.6435
1130.0667 | 284.0514 | 291.6019 | 285.3331
1131.0667 | 284.007 | 291.4771 | 284.5563
1132.0667 | 283.8392 | 291.4044 | 284.2708
1133.0667 | 283.8636 | 291.2724 | 284.5684
1134.0667 | 284.1156 | 291.02 | 284.7861
1135.0667 | 284.4432 | 290.855 | 285.1594
1136.0667 | 284.7533 | 290.915 | 285.2771
1137.0667 | 284.858 | 290.8781 | 285.7721
1138.0667 | 285.2126 | 291.1706 | 285.7629
1139.0667 | 285.6661 | 291.5215 | 285.9025
1140.0667 | 285.8988 | 291.5621 | 286.4476
1141.0667 | 285.6433 | 291.609 | 286.7535
1142.0667 | 285.5608 | 292.5413 | 286.6218
1143.0667 | 285.714 | 292.9333 | 286.6499
1144.0667 | 285.9036 | 293.3993 | 286.5735
1145.0667 | 286.5392 | 294.1516 | 286.9548
1146.0667 | 286.3957 | 294.7401 | 286.4481
1147.0667 | 286.6405 | 294.5882 | 286.4362
1148.0667 | 287.2361 | 294.4731 | 286.2479
1149.0667 | 287.3384 | 294.6486 | 286.1566
1150.0667 | 287.4204 | 294.4378 | 286.5742
1151.0667 | 287.588 | 294.6375 | 287.1152
1152.0667 | 287.5369 | 294.5488 | 287.0799
1153.0667 | 287.7604 | 294.4584 | 287.205
1154.0667 | 287.7711 | 294.1467 | 287.5339
1155.0667 | 287.8584 | 294.0572 | 288.8903
1156.0667 | 287.8068 | 294.3845 | 289.0041
1157.0667 | 288.2186 | 295.2383 | 289.5853
1158.0667 | 288.2224 | 295.6911 | 290.9355
1159.0667 | 289.1356 | 296.8567 | 291.5664
1160.0667 | 289.6403 | 297.6897 | 291.7569
1161.0667 | 290.3661 | 298.0279 | 291.6535
1162.0667 | 290.008 | 298.9653 | 292.2737
1163.0667 | 289.8481 | 298.9949 | 292.299
1164.0667 | 290.0198 | 299.6613 | 291.7655
1165.0667 | 290.8206 | 299.7652 | 291.0938
1166.0667 | 290.7872 | 300.0036 | 290.539
1167.0667 | 290.9986 | 299.7886 | 290.5694
1168.0667 | 291.1168 | 299.5642 | 291.3215
1169.0667 | 290.5427 | 299.2908 | 291.662
1170.0667 | 290.4875 | 299.2282 | 291.9893
1171.0667 | 290.1809 | 299.254 | 291.7859
1172.0667 | 289.9424 | 298.9362 | 291.4239
1173.0667 | 290.1 | 298.7317 | 291.8422
1174.0667 | 290.6218 | 298.4841 | 291.9972
1175.0667 | 291.2299 | 298.4689 | 291.6917
1176.0667 | 291.3709 | 298.3224 | 291.5671
1177.0667 | 291.5922 | 298.0478 | 291.2281
1178.0667 | 291.7908 | 298.1822 | 291.3922
1179.0667 | 291.9339 | 298.2343 | 292.2676
1180.0667 | 291.8801 | 298.2564 | 292.3026
1181.0667 | 291.7088 | 298.9675 | 292.1103
1182.0667 | 291.8167 | 298.8411 | 292.7011
1183.0667 | 292.0396 | 298.8459 | 293.0719
1184.0667 | 291.5741 | 298.6038 | 293.8484
1185.0667 | 291.8948 | 298.6083 | 294.0809
1186.0667 | 291.8427 | 298.5483 | 294.0305
1187.0667 | 291.4708 | 298.2812 | 294.0538
1188.0667 | 291.6337 | 298.2229 | 293.8079
1189.0667 | 292.1063 | 298.3178 | 293.39
1190.0667 | 292.4706 | 298.1344 | 293.9069
1191.0667 | 292.3128 | 298.0522 | 293.751
1192.0667 | 292.5496 | 298.1792 | 294.32
1193.0667 | 292.5815 | 298.8377 | 294.4141
1194.0667 | 293.0409 | 299.5164 | 295.2995
1195.0667 | 292.9801 | 300.247 | 295.5678
1196.0667 | 293.4367 | 300.7171 | 295.3481
1197.0667 | 294.0427 | 301.1846 | 295.6361
1198.0667 | 294.3337 | 301.4192 | 296.1003
1199.0667 | 295.1355 | 301.4834 | 296.2038
1200.0667 | 295.9869 | 301.5957 | 296.3882
1201.0667 | 296.6014 | 301.8137 | 296.9213
1202.0667 | 297.2825 | 301.817 | 297.0098
1203.0667 | 297.3446 | 302.0314 | 296.9381
1204.0667 | 298.6526 | 302.6978 | 296.9483
1205.0667 | 298.0275 | 302.7083 | 298.3421
1206.0667 | 298.3517 | 302.8064 | 297.9995
1207.0667 | 298.8191 | 302.7109 | 298.0951
1208.0667 | 298.9045 | 303.1706 | 297.9106
1209.0667 | 298.5349 | 303.1244 | 298.322
1210.0667 | 298.5587 | 303.5588 | 300.7845
1211.0667 | 298.4744 | 303.9263 | 301.215
1212.0667 | 298.3217 | 304.2162 | 301.611
1213.0667 | 298.6179 | 304.7425 | 301.661
1214.0667 | 299.2936 | 304.9488 | 301.2846
1215.0667 | 299.5336 | 305.325 | 301.4335
1216.0667 | 301.1053 | 305.5887 | 300.9757
1217.0667 | 302.0395 | 305.5638 | 300.6434
1218.0667 | 302.5372 | 305.4962 | 300.3819
1219.0667 | 302.7246 | 306.3029 | 300.3208
1220.0667 | 303.5184 | 306.0493 | 300.8629
1221.0667 | 303.3075 | 305.7911 | 300.7436
1222.0667 | 303.2031 | 305.7649 | 300.6307
1223.0667 | 303.2008 | 305.5955 | 301.6634
1224.0667 | 303.325 | 305.8461 | 301.5085
1225.0667 | 303.5545 | 305.7145 | 301.3394
1226.0667 | 304.0113 | 307.8287 | 301.517
1227.0667 | 303.914 | 307.6613 | 301.7344
1228.0667 | 304.5735 | 307.6711 | 302.4378
1229.0667 | 304.8899 | 307.9874 | 302.5488
1230.0667 | 305.1717 | 307.6729 | 302.7288
1231.0667 | 305.1775 | 307.8696 | 302.8772
1232.0667 | 305.337 | 307.8544 | 303.0095
1233.0667 | 304.8451 | 307.7614 | 303.9572
1234.0667 | 304.432 | 307.6012 | 304.2957
1235.0667 | 304.3326 | 307.5568 | 304.3167
1236.0667 | 304.1019 | 307.4913 | 304.8164
1237.0667 | 304.2544 | 307.3995 | 304.8476
1238.0667 | 304.2744 | 307.7023 | 304.6943
1239.0667 | 304.6627 | 307.9603 | 304.6188
1240.0667 | 304.5494 | 308.0513 | 304.7495
1241.0667 | 304.722 | 308.1655 | 305.4897
1242.0667 | 304.9415 | 308.5067 | 305.338
1243.0667 | 305.395 | 308.8317 | 305.322
1244.0823 | 305.8965 | 308.8205 | 305.2421
1245.0667 | 305.8956 | 308.7828 | 304.7373
1246.0667 | 305.6902 | 308.5155 | 304.9402
1247.0667 | 305.5875 | 308.8377 | 305.3412
1248.0667 | 305.856 | 308.9155 | 305.2291
1249.0667 | 306.122 | 309.0773 | 305.5113
1250.0667 | 307.0412 | 308.8145 | 304.9363
1251.0667 | 307.8023 | 309.1595 | 305.2081
1252.0667 | 308.0201 | 309.3334 | 305.3352
1253.0667 | 308.2205 | 309.8561 | 305.8055
1254.0667 | 308.2521 | 310.3169 | 306.1016
1255.0667 | 308.5085 | 310.6852 | 306.021
1256.0667 | 308.4642 | 310.7553 | 305.8158
1257.0667 | 308.2657 | 310.8326 | 305.324
1258.0667 | 308.4395 | 310.6782 | 304.5132
1259.0823 | 308.3588 | 310.7466 | 304.1886
1260.0667 | 308.1145 | 310.9695 | 304.7922
1261.0667 | 308.8462 | 311.6684 | 304.9148
1262.0667 | 309.4786 | 312.4019 | 305.3336
1263.0667 | 309.2254 | 313.7673 | 305.5923
1264.0667 | 309.6871 | 314.0664 | 305.8366
1265.0667 | 309.3215 | 314.9457 | 306.204
1266.0667 | 309.4786 | 314.8605 | 306.7636
1267.0667 | 309.5764 | 314.8782 | 307.1605
1268.0667 | 309.4969 | 315.2706 | 307.7053
1269.0667 | 309.6383 | 315.4285 | 307.7213
1270.0667 | 309.9993 | 315.4534 | 308.0713
1271.0667 | 310.0579 | 315.0743 | 308.1653
1272.0667 | 309.7747 | 314.8654 | 308.4114
1273.0667 | 309.2361 | 314.6805 | 308.6876
1274.0667 | 309.0835 | 314.5829 | 308.7663
1275.0667 | 309.0393 | 314.4665 | 308.8173
1276.0667 | 309.4439 | 314.5356 | 309.3111
1277.0667 | 310.5877 | 315.4004 | 309.6026
1278.0667 | 310.7607 | 315.5959 | 310.4166
1279.0667 | 310.966 | 315.8709 | 311.723
1280.0667 | 311.7973 | 316.5014 | 312.5357
1281.0667 | 312.4818 | 317.4706 | 313.2345
1282.0667 | 312.7699 | 317.9933 | 313.7646
1283.0667 | 313.6215 | 318.0789 | 313.5709
1284.0823 | 314.1502 | 318.7316 | 313.722
1285.0667 | 314.4762 | 318.7652 | 314.4634
1286.0667 | 314.9169 | 319.7636 | 315.2089
1287.0667 | 314.8897 | 319.9725 | 315.6668
1288.0667 | 314.7185 | 320.3812 | 315.7753
1289.0667 | 315.2186 | 320.1966 | 315.6321
1290.0667 | 315.3531 | 320.4144 | 315.9367
1291.0667 | 315.718 | 320.31 | 315.9088
1292.0667 | 315.9052 | 320.4759 | 315.4715
1293.0667 | 315.968 | 320.316 | 315.8571
1294.0667 | 315.9381 | 320.0687 | 315.8568
1295.0667 | 316.0446 | 320.0517 | 315.8144
1296.0667 | 316.0885 | 320.2271 | 315.2928
1297.0667 | 315.7181 | 320.4068 | 314.5317
1298.0667 | 315.4004 | 320.8457 | 315.0272
1299.0823 | 315.6538 | 321.3755 | 315.0314
1300.0667 | 316.2383 | 321.6008 | 314.651
1301.0667 | 316.1299 | 321.7458 | 314.5158
1302.0667 | 316.0007 | 321.5571 | 315.0518
1303.0667 | 316.2808 | 321.2958 | 315.8715
1304.0667 | 316.4059 | 321.2888 | 316.7859
1305.0667 | 316.4604 | 321.3983 | 317.5173
1306.0667 | 316.6852 | 321.7083 | 318.0219
1307.0667 | 316.9795 | 321.9471 | 318.69
1308.0667 | 317.7097 | 322.4297 | 319.1752
1309.0667 | 318.4769 | 322.7322 | 319.0881
1310.0667 | 319.0479 | 323.9388 | 319.4208
1311.0667 | 319.4449 | 323.9638 | 319.3121
1312.0667 | 319.6637 | 323.5519 | 319.4388
1313.0667 | 319.7946 | 323.5207 | 319.6705
1314.0667 | 320.3448 | 323.345 | 320.6498
1315.0667 | 320.2121 | 323.1948 | 320.2413
1316.0667 | 320.317 | 323.3502 | 320.4539
1317.0667 | 319.947 | 323.1865 | 320.1583
1318.0667 | 319.5895 | 322.8702 | 320.2385
1319.0667 | 319.7225 | 322.8822 | 319.4518
1320.0667 | 319.2961 | 322.8327 | 319.3293
1321.0667 | 319.4244 | 322.602 | 319.2851
1322.0667 | 319.303 | 322.4985 | 319.5024
1323.0667 | 319.3222 | 322.4564 | 319.3396
1324.0667 | 319.4682 | 322.6969 | 320.445
1325.0667 | 319.7178 | 322.4539 | 320.3209
1326.0667 | 319.7 | 322.7232 | 319.6398
1327.0667 | 319.7137 | 322.901 | 319.9746
1328.0667 | 319.8088 | 323.1593 | 320.2064
1329.0667 | 319.9635 | 323.1511 | 320.0176
1330.0667 | 320.6044 | 323.2277 | 320.0783
1331.0667 | 320.7799 | 323.2339 | 319.9881
1332.0667 | 320.51 | 323.1708 | 320.2484
1333.0667 | 320.2494 | 323.2451 | 320.5503
1334.0667 | 320.585 | 323.0999 | 320.1408
1335.0667 | 320.3 | 323.3297 | 319.4305
1336.0667 | 320.3225 | 323.4877 | 319.4739
1337.0667 | 319.957 | 323.6879 | 318.9898
1338.0667 | 319.8264 | 323.9686 | 318.4367
1339.0823 | 319.6188 | 323.6964 | 318.4953
1340.0667 | 319.7238 | 323.6019 | 318.0913
1341.0667 | 319.9416 | 323.4787 | 317.7669
1342.0667 | 320.3222 | 323.5224 | 317.4381
1343.0667 | 320.1435 | 323.8927 | 316.8082
1344.0823 | 320.5306 | 324.066 | 316.784
1345.0667 | 320.4551 | 324.1238 | 316.8715
1346.0667 | 320.1618 | 323.925 | 316.524
1347.0667 | 320.612 | 323.724 | 316.5402
1348.0667 | 320.9342 | 323.4448 | 316.1921
1349.0667 | 321.1145 | 323.4668 | 316.9357
1350.0667 | 320.8786 | 323.4105 | 317.0486
1351.0667 | 320.6889 | 323.3201 | 317.4578
1352.0667 | 320.8483 | 323.4339 | 317.903
1353.0667 | 320.6834 | 323.0243 | 317.9587
1354.0667 | 320.9077 | 323.1917 | 317.5351
1355.0667 | 320.3446 | 323.3542 | 317.7354
1356.0667 | 320.3648 | 323.5669 | 317.8556
1357.0667 | 320.6964 | 323.9434 | 318.1091
1358.0667 | 320.9911 | 324.3667 | 318.3968
1359.0667 | 321.2779 | 325.1752 | 318.8034
1360.0667 | 321.8017 | 325.0447 | 319.8277
1361.0667 | 322.1132 | 325.1617 | 320.6379
1362.0667 | 322.1473 | 324.7428 | 320.6793
1363.0667 | 321.8731 | 324.4568 | 320.7581
1364.0667 | 321.7133 | 324.3453 | 320.524
1365.0667 | 321.2705 | 324.4516 | 319.9448
1366.0667 | 321.6136 | 324.5562 | 319.4317
1367.0667 | 321.3836 | 324.2988 | 319.294
1368.0667 | 321.7459 | 324.0728 | 319.2697
1369.0667 | 321.9446 | 323.8291 | 318.8535
1370.0667 | 321.7152 | 323.7073 | 318.0921
1371.0667 | 321.3714 | 323.9956 | 317.8674
1372.0667 | 321.567 | 323.7205 | 317.4933
1373.0667 | 321.9189 | 323.6932 | 317.479
1374.0667 | 321.9551 | 324.5007 | 317.4369
1375.0667 | 321.6508 | 324.4154 | 317.3955
1376.0667 | 321.8302 | 325.0894 | 317.7559
1377.0667 | 321.8062 | 325.0732 | 318.2396
1378.0667 | 322.4097 | 324.9705 | 318.2782
1379.0667 | 322.3275 | 324.9312 | 318.2568
1380.0667 | 322.12 | 324.6527 | 319.5055
1381.0667 | 322.076 | 324.3599 | 319.4683
1382.0667 | 321.8654 | 324.1021 | 318.8255
1383.0667 | 321.7785 | 323.9506 | 319.0959
1384.0823 | 321.9541 | 323.9087 | 319.3099
1385.0667 | 321.9542 | 323.9518 | 319.9113
1386.0667 | 321.7661 | 323.9921 | 319.4406
1387.0667 | 321.8916 | 324.2586 | 318.8844
1388.0667 | 321.7972 | 324.515 | 318.5967
1389.0823 | 321.788 | 325.6016 | 318.9184
1390.0667 | 321.4892 | 325.3609 | 318.4816
1391.0667 | 321.4658 | 325.3796 | 318.1218
1392.0667 | 321.6189 | 325.421 | 318.0293
1393.0823 | 321.6452 | 325.1955 | 318.7221
1394.0667 | 321.7915 | 325.0944 | 318.0811
1395.0667 | 321.6632 | 325.0626 | 317.9223
1396.0667 | 322.2291 | 325.256 | 318.2549
1397.0667 | 322.8432 | 325.7535 | 318.9254
1398.0667 | 323.0559 | 326.2797 | 319.014
1399.0823 | 323.7939 | 326.1442 | 319.1416
1400.0667 | 324.2701 | 326.352 | 319.0513
1401.0823 | 324.625 | 327.0119 | 318.6164
1402.0667 | 324.9284 | 327.076 | 319.2551
1403.0667 | 325.1885 | 327.2216 | 319.9775
1404.0667 | 325.4676 | 327.4183 | 319.8805
1405.0823 | 325.6671 | 328.2958 | 320.1087
1406.0667 | 325.7657 | 328.3712 | 320.5954
1407.0667 | 325.7245 | 328.0469 | 320.9675
1408.0667 | 325.5731 | 327.6561 | 321.0782
1409.0667 | 325.4582 | 327.3402 | 321.9182
1410.0667 | 325.7879 | 328.0445 | 321.8943
1411.0667 | 326.0504 | 327.9626 | 321.9787
1412.0667 | 326.054 | 328.2003 | 322.1983
1413.0667 | 326.7827 | 328.4006 | 322.5085
1414.0667 | 327.407 | 328.8087 | 323.1924
1415.0667 | 327.9674 | 329.21 | 323.4255
1416.0667 | 327.9576 | 329.1751 | 323.5795
1417.0667 | 327.8977 | 328.8302 | 323.3932
1418.0667 | 327.5507 | 329.8996 | 322.9966
1419.0667 | 327.086 | 329.6193 | 323.2864
1420.0667 | 327.0065 | 329.3824 | 323.5328
1421.0667 | 327.049 | 329.2378 | 323.3806
1422.0667 | 326.7574 | 328.8744 | 323.2566
1423.0667 | 326.8822 | 329.1851 | 323.6561
1424.0667 | 326.7595 | 329.2218 | 323.5606
1425.0667 | 326.8587 | 329.1995 | 323.7581
1426.0667 | 327.2362 | 329.2233 | 323.1491
1427.0667 | 327.2488 | 329.2121 | 322.5552
1428.0667 | 327.4855 | 329.5295 | 322.5337
1429.0667 | 327.6435 | 329.5973 | 323.5118
1430.0667 | 327.6667 | 329.9886 | 323.2097
1431.0667 | 327.8452 | 329.7883 | 323.1572
1432.0667 | 327.6212 | 329.4614 | 322.9127
1433.0667 | 327.4913 | 329.2129 | 322.1418
1434.0667 | 326.8827 | 329.0332 | 322.0627
1435.0667 | 327.3795 | 328.5961 | 321.943
1436.0667 | 327.1828 | 328.2684 | 321.8671
1437.0667 | 326.8017 | 328.215 | 321.9044
1438.0667 | 326.6128 | 328.0052 | 321.2914
1439.0823 | 326.3865 | 327.8452 | 320.9889
1440.0667 | 326.3778 | 327.6271 | 320.7725
1441.0823 | 326.3735 | 327.7799 | 320.6184
1442.0667 | 326.1678 | 327.7563 | 321.3997
1443.0667 | 325.6298 | 327.4768 | 321.3493
1444.0823 | 325.2581 | 327.55 | 321.3948
1445.0667 | 325.513 | 327.4834 | 321.7951
1446.0667 | 325.7926 | 327.9274 | 321.8249
1447.0667 | 325.7818 | 327.9694 | 321.7354
1448.0667 | 326.0568 | 327.9665 | 322.3628
1449.0667 | 326.0861 | 327.7242 | 322.9147
1450.0667 | 326.2873 | 327.7225 | 322.9393
1451.0667 | 326.0776 | 327.8787 | 322.7763
1452.0667 | 326.0055 | 327.7537 | 323.402
1453.0667 | 325.9006 | 327.5053 | 323.5232
1454.0823 | 326.041 | 328.7064 | 323.6846
1455.0667 | 326.0033 | 328.7237 | 323.3019
1456.0667 | 326.0249 | 329.4178 | 323.3929
1457.0667 | 326.37 | 329.3594 | 323.5903
1458.0667 | 326.7572 | 329.4896 | 324.5407
1459.0667 | 326.9715 | 329.136 | 324.6146
1460.0667 | 327.0281 | 328.998 | 324.1436
1461.0667 | 327.0091 | 328.9755 | 324.3178
1462.0667 | 326.8601 | 329.2135 | 324.1252
1463.0667 | 326.7342 | 328.9655 | 324.2604
1464.0667 | 326.9815 | 328.6579 | 324.0505
1465.0667 | 327.0784 | 328.2935 | 323.999
1466.0667 | 326.8265 | 328.2192 | 323.9022
1467.0667 | 327.2801 | 328.087 | 324.1598
1468.0667 | 327.6924 | 328.0178 | 324.1822
1469.0667 | 327.5026 | 328.1919 | 323.7312
1470.0667 | 327.9217 | 328.0575 | 323.8175
1471.0667 | 328.0062 | 327.9555 | 324.027
1472.0667 | 327.6175 | 328.013 | 323.9102
1473.0667 | 327.5178 | 327.9923 | 324.2747
1474.0667 | 327.9055 | 327.8668 | 324.8793
1475.0667 | 327.9455 | 327.7439 | 324.8912
1476.0667 | 328.0201 | 328.1716 | 324.9683
1477.0667 | 327.6876 | 328.1649 | 325.1831
1478.0667 | 327.3962 | 327.9731 | 325.1317
1479.0667 | 327.3518 | 328.0439 | 325.0569
1480.0667 | 327.3215 | 327.9729 | 324.829
1481.0667 | 327.4026 | 328.0652 | 324.9296
1482.0667 | 327.4654 | 328.2878 | 325.1352
1483.0667 | 327.9634 | 328.2933 | 325.1294
1484.0667 | 327.9416 | 328.3174 | 324.9992
1485.0667 | 327.5637 | 328.2079 | 325.138
1486.0667 | 327.7398 | 328.3609 | 324.9618
1487.0667 | 328.3976 | 328.3905 | 324.8291
1488.0667 | 328.138 | 328.5201 | 324.3654
1489.0667 | 328.3612 | 328.4464 | 323.7259
1490.0667 | 328.0885 | 328.5199 | 323.3704
1491.0667 | 327.9075 | 328.2236 | 323.026
1492.0667 | 327.8859 | 328.0062 | 322.9059
1493.0667 | 327.5579 | 327.9082 | 322.7753
1494.0667 | 327.4 | 327.6884 | 322.4586
1495.0667 | 327.9447 | 327.8222 | 322.8211
1496.0667 | 328.0664 | 327.7179 | 322.9242
1497.0667 | 328.3621 | 327.7665 | 322.82
1498.0667 | 328.4863 | 327.6538 | 322.6286
1499.0667 | 328.3766 | 327.8433 | 322.7684
1500.0667 | 328.3685 | 328.0504 | 322.6036
1501.0667 | 328.1586 | 328.2335 | 322.4846
1502.0667 | 328.4341 | 328.591 | 322.5476
1503.0667 | 328.2155 | 328.7527 | 322.3115
1504.0667 | 328.6117 | 328.9651 | 321.8819
1505.0667 | 328.5086 | 329.1347 | 321.6617
1506.0667 | 328.6573 | 329.2754 | 321.761
1507.0667 | 328.8416 | 329.2057 | 322.6084
1508.0667 | 329.3008 | 329.4196 | 322.2595
1509.0667 | 329.1582 | 329.5881 | 322.0544
1510.0667 | 329.0749 | 329.5223 | 321.9101
1511.0667 | 329.1829 | 329.5384 | 321.6967
1512.0667 | 329.2135 | 329.6106 | 321.4819
1513.0667 | 329.5424 | 329.7629 | 321.573
1514.0667 | 329.8438 | 331.0542 | 322.042
1515.0667 | 330.1311 | 330.7744 | 321.9901
1516.0667 | 330.1035 | 331.1147 | 321.8387
1517.0667 | 330.5624 | 331.6652 | 322.0796
1518.0667 | 330.8236 | 331.7825 | 322.5189
1519.0667 | 331.0483 | 331.4562 | 322.3901
1520.0667 | 331.6598 | 332.1033 | 323.1218
1521.0667 | 332.1411 | 331.9481 | 323.4022
1522.0667 | 332.2158 | 332.1391 | 322.9726
1523.0667 | 332.5169 | 332.1184 | 322.8411
1524.0667 | 332.198 | 333.3614 | 322.6842
1525.0667 | 332.0765 | 333.0304 | 322.6901
1526.0667 | 331.7796 | 332.6917 | 322.623
1527.0667 | 331.6232 | 332.4323 | 322.7493
1528.0667 | 332.0623 | 332.0287 | 322.8627
1529.0667 | 331.9421 | 332.1708 | 323.1956
1530.0667 | 331.8778 | 331.7713 | 323.9396
1531.0667 | 331.5379 | 331.4581 | 323.9768
1532.0667 | 331.3507 | 331.1571 | 324.1979
1533.0667 | 331.0029 | 331.0762 | 324.1716
1534.0667 | 330.7269 | 331.1082 | 324.4129
1535.0667 | 330.6998 | 330.9942 | 324.4848
1536.0667 | 330.4426 | 330.7324 | 324.2969
1537.0667 | 330.6881 | 330.9228 | 324.4094
1538.0667 | 330.6824 | 331.157 | 324.2146
1539.0667 | 330.6945 | 331.1851 | 323.7872
1540.0667 | 330.7819 | 331.5033 | 323.7467
1541.0667 | 330.7312 | 331.6089 | 323.794
1542.0667 | 330.8813 | 331.5319 | 323.8188
1543.0667 | 330.6122 | 331.982 | 323.9417
1544.0667 | 329.8357 | 331.9426 | 324.2551
1545.0667 | 329.3382 | 331.877 | 324.0583
1546.0667 | 329.2891 | 331.6574 | 323.7905
1547.0667 | 329.0334 | 331.6607 | 324.0357
1548.0667 | 328.8524 | 331.7031 | 323.924
1549.0667 | 329.0654 | 331.9663 | 324.1846
1550.0667 | 329.2302 | 332.7017 | 324.6577
1551.0667 | 329.5316 | 332.907 | 324.3931
1552.0667 | 331.18 | 333.8829 | 324.425
1553.0667 | 331.0212 | 334.0454 | 324.2407
1554.0667 | 331.1222 | 333.7902 | 324.5735
1555.0667 | 331.1316 | 333.471 | 324.7466
1556.0667 | 330.8679 | 333.0985 | 324.6657
1557.0667 | 330.972 | 332.5771 | 324.2447
1558.0667 | 330.9729 | 332.3612 | 324.2664
1559.0667 | 330.8628 | 331.9477 | 324.2314
1560.0667 | 330.3875 | 331.8418 | 323.7889
1561.0667 | 329.9601 | 332.0199 | 323.4499
1562.0667 | 329.9644 | 332.3376 | 323.635
1563.0667 | 329.8604 | 331.8125 | 323.3899
1564.0667 | 330.0569 | 331.4646 | 323.0334
1565.0667 | 330.4416 | 331.6531 | 322.7483
1566.0667 | 330.8724 | 331.3516 | 322.4934
1567.0667 | 330.8984 | 331.0689 | 322.4711
1568.0667 | 331.2115 | 331.0419 | 322.518
1569.0667 | 330.9488 | 331.0112 | 322.4089
1570.0667 | 330.6326 | 331.5825 | 322.3529
1571.0667 | 330.0519 | 331.608 | 322.6418
1572.0667 | 330.1363 | 331.4152 | 322.7098
1573.0667 | 329.8115 | 331.3762 | 322.7555
1574.0667 | 329.4474 | 331.2142 | 322.9951
1575.0667 | 330.0465 | 330.9101 | 323.4315
1576.0667 | 329.9891 | 330.7869 | 323.8518
1577.0667 | 329.9525 | 330.9003 | 323.3037
1578.0667 | 329.5734 | 330.7068 | 323.5782
1579.0667 | 329.4281 | 330.6517 | 323.4953
1580.0667 | 329.5674 | 330.3684 | 323.5166
1581.0667 | 329.477 | 330.5579 | 323.5557
1582.0667 | 329.4027 | 331.0258 | 324.2249
1583.0667 | 329.719 | 331.3535 | 324.2301
1584.0667 | 329.9025 | 331.6214 | 324.0423
1585.0667 | 329.9964 | 331.4676 | 323.8985
1586.0667 | 329.9654 | 331.1319 | 324.0252
1587.0667 | 329.7463 | 330.8102 | 323.7273
1588.0667 | 329.4434 | 330.5303 | 323.8794
1589.0667 | 329.1349 | 330.4856 | 323.8675
1590.0667 | 328.7662 | 330.4944 | 324.2615
1591.0667 | 328.7562 | 330.4358 | 324.9311
1592.0667 | 328.4695 | 330.0522 | 325.1572
1593.0667 | 328.4509 | 329.8635 | 325.4557
1594.0667 | 328.4932 | 329.6079 | 325.3175
1595.0667 | 328.8817 | 329.5202 | 325.6773
1596.0667 | 329.5579 | 329.7222 | 326.1466
1597.0667 | 329.8991 | 329.3722 | 326.1711
1598.0667 | 330.4785 | 329.5988 | 325.8084
1599.0667 | 330.8319 | 329.8598 | 325.4284
1600.0667 | 330.8804 | 330.9868 | 325.5832
1601.0667 | 330.922 | 331.0261 | 325.4054
1602.0667 | 331.127 | 330.9152 | 325.8524
1603.0667 | 331.1432 | 330.7867 | 325.7113
1604.0667 | 331.3134 | 330.9306 | 325.727
1605.0667 | 331.6438 | 330.7456 | 325.8924
1606.0667 | 331.7293 | 330.8998 | 326.0411
1607.0667 | 331.7357 | 330.8851 | 326.4676
1608.0667 | 331.9516 | 330.7757 | 326.5144
1609.0667 | 331.8979 | 330.8858 | 326.4305
1610.0667 | 331.7976 | 330.9082 | 327.0451
1611.0667 | 331.8247 | 330.9029 | 327.5378
1612.0667 | 332.0028 | 331.1502 | 327.7202
1613.0667 | 331.9944 | 331.1806 | 327.9559
1614.0667 | 331.6914 | 331.2556 | 327.8742
1615.0667 | 331.5924 | 331.443 | 328.269
1616.0667 | 331.6741 | 331.6277 | 328.4419
1617.0667 | 331.5945 | 331.7336 | 328.3654
1618.0667 | 331.5975 | 332.3607 | 328.5122
1619.0667 | 331.4169 | 332.4625 | 328.4642
1620.0667 | 331.6452 | 332.4295 | 328.5044
1621.0667 | 331.5842 | 332.3883 | 329.1092
1622.0667 | 331.3248 | 332.5247 | 328.788
1623.0667 | 331.2543 | 332.5777 | 328.4662
1624.0667 | 331.4595 | 332.751 | 329.0504
1625.0667 | 331.3498 | 332.6706 | 328.4548
1626.0667 | 331.8878 | 333.0829 | 328.0716
1627.0667 | 332.4962 | 332.8596 | 327.6191
1628.0667 | 332.5214 | 333.0876 | 327.3468
1629.0823 | 332.391 | 333.1099 | 327.5471
1630.0667 | 332.4351 | 333.259 | 327.9463
1631.0667 | 332.4615 | 333.4585 | 327.7322
1632.0667 | 332.2003 | 333.5091 | 327.6065
1633.0667 | 332.2875 | 333.9079 | 327.5814
1634.0667 | 332.5771 | 333.7876 | 328.0313
1635.0667 | 332.8677 | 333.8219 | 327.8524
1636.0667 | 333.314 | 334.2748 | 328.1404
1637.0667 | 333.408 | 334.7281 | 327.917
1638.0667 | 333.3614 | 334.4582 | 328.0028
1639.0667 | 333.2431 | 334.4156 | 328.5907
1640.0667 | 332.8355 | 334.0511 | 328.54
1641.0667 | 332.6374 | 333.8921 | 328.4893
1642.0667 | 332.8686 | 333.6991 | 328.9693
1643.0667 | 332.6994 | 333.5238 | 328.9156
1644.0823 | 332.4763 | 333.8011 | 329.2134
1645.0667 | 332.8088 | 333.6788 | 329.8007
1646.0667 | 333.1382 | 333.6753 | 329.9932
1647.0667 | 333.3237 | 333.6854 | 329.9154
1648.0667 | 333.303 | 333.6194 | 329.7451
1649.0667 | 333.1684 | 333.6306 | 330.1099
1650.0667 | 333.2919 | 333.632 | 329.75
1651.0667 | 332.9361 | 334.0237 | 329.3501
1652.0667 | 332.8441 | 334.1284 | 329.1516
1653.0667 | 333.1722 | 334.3512 | 329.4974
1654.0667 | 333.3995 | 334.6532 | 329.4072
1655.0667 | 333.6748 | 335.0095 | 329.9786
1656.0667 | 333.809 | 335.3818 | 330.9533
1657.0667 | 334.613 | 336.1963 | 331.328
1658.0667 | 335.8528 | 336.609 | 331.6346
1659.0667 | 335.7895 | 336.8626 | 331.6731
1660.0667 | 335.6433 | 336.7311 | 331.7859
1661.0667 | 335.5044 | 336.6123 | 331.347
1662.0667 | 335.2851 | 336.3626 | 330.9628
1663.0667 | 335.3787 | 336.1056 | 330.8327
1664.0667 | 334.9595 | 335.7933 | 330.6715
1665.0667 | 335.2564 | 335.5318 | 330.9103
1666.0667 | 335.0904 | 335.3225 | 331.0636
1667.0667 | 334.7797 | 335.2145 | 330.4877
1668.0667 | 334.5753 | 335.0879 | 330.3371
1669.0823 | 334.691 | 334.9522 | 329.6829
1670.0667 | 335.2505 | 334.8532 | 329.327
1671.0667 | 335.5968 | 334.8907 | 329.0869
1672.0667 | 335.7872 | 334.8644 | 329.3772
1673.0667 | 335.6598 | 334.8129 | 329.5804
1674.0667 | 335.2737 | 334.6009 | 329.2872
1675.0667 | 334.8563 | 334.3474 | 328.6372
1676.0667 | 334.8661 | 334.557 | 328.7755
1677.0667 | 334.7359 | 334.624 | 328.7269
1678.0667 | 334.858 | 334.7932 | 328.1933
1679.0667 | 334.9333 | 334.6491 | 327.9416
1680.0667 | 335.0454 | 334.4607 | 327.451
1681.0667 | 335.5024 | 334.9245 | 327.4887
1682.0667 | 335.2923 | 334.6332 | 327.1989
1683.0667 | 335.1648 | 334.6499 | 327.1964
1684.0667 | 334.7466 | 335.0109 | 326.963
1685.0667 | 334.4503 | 334.8813 | 327.0011
1686.0667 | 334.1129 | 334.5041 | 327.0967
1687.0667 | 334.3104 | 334.2039 | 327.0469
1688.0667 | 334.6423 | 334.7617 | 326.9825
1689.0667 | 335.324 | 334.8305 | 327.5141
1690.0667 | 335.8751 | 334.7258 | 327.2496
1691.0667 | 336.4368 | 334.9679 | 327.648
1692.0667 | 336.5576 | 334.8325 | 328.3639
1693.0667 | 336.315 | 334.7444 | 328.8247
1694.0667 | 335.662 | 334.9527 | 328.9559
1695.0667 | 335.5267 | 334.8441 | 328.7709
1696.0667 | 335.7167 | 334.7307 | 328.7605
1697.0667 | 335.3223 | 334.861 | 328.9433
1698.0667 | 335.0122 | 335.2964 | 329.1451
1699.0667 | 334.9376 | 335.3162 | 329.3918
1700.0667 | 335.2775 | 336.2309 | 329.8972
1701.0667 | 335.513 | 336.1507 | 330.3783
1702.0667 | 335.7341 | 335.9631 | 330.0402
1703.0667 | 335.3172 | 336.6202 | 329.358
1704.0667 | 335.2795 | 336.7118 | 328.9736
1705.0667 | 335.3 | 336.8219 | 328.7149
1706.0667 | 335.5045 | 336.8466 | 328.2573
1707.0667 | 335.7989 | 336.7751 | 328.0856
1708.0667 | 336.5316 | 337.1117 | 328.5738
1709.0667 | 336.8004 | 337.3403 | 329.2314
1710.0667 | 337.1554 | 338.1021 | 329.3627
1711.0667 | 337.5116 | 338.3887 | 329.6942
1712.0667 | 337.6658 | 338.7904 | 330.0203
1713.0667 | 338.1806 | 338.8212 | 330.2903
1714.0667 | 338.4011 | 338.7109 | 330.5028
1715.0667 | 338.4642 | 338.4653 | 330.7951
1716.0667 | 338.4595 | 338.2083 | 330.5393
1717.0667 | 338.2045 | 338.0462 | 330.5505
1718.0667 | 337.8744 | 337.8098 | 330.591
1719.0667 | 337.7083 | 337.6622 | 330.9347
1720.0667 | 337.5891 | 337.8754 | 331.5575
1721.0667 | 337.8523 | 338.0936 | 331.1214
1722.0667 | 338.4071 | 338.0973 | 331.2808
1723.0667 | 338.6705 | 337.9284 | 331.3123
1724.0667 | 338.5013 | 337.6247 | 331.4736
1725.0667 | 338.3926 | 337.3384 | 331.2276
1726.0667 | 338.1981 | 337.0496 | 330.7563
1727.0667 | 338.1003 | 337.0147 | 330.2935
1728.0667 | 338.1762 | 336.9068 | 329.7621
1729.0823 | 338.3093 | 336.9088 | 329.6045
1730.0667 | 337.9175 | 336.8869 | 329.2041
1731.0667 | 337.4583 | 336.9884 | 328.7598
1732.0667 | 337.4055 | 337.0775 | 328.7837
1733.0667 | 337.3726 | 336.8993 | 328.8168
1734.0667 | 337.711 | 336.8243 | 328.3673
1735.0667 | 338.2738 | 336.5856 | 328.2531
1736.0667 | 338.2242 | 336.4748 | 328.4176
1737.0667 | 338.4514 | 336.3994 | 328.2749
1738.0667 | 338.6298 | 336.3528 | 328.0145
1739.0667 | 338.1478 | 336.4431 | 327.7732
1740.0667 | 337.7746 | 336.2492 | 327.3633
1741.0667 | 338.1931 | 335.9357 | 327.2333
1742.0667 | 337.9271 | 336.0126 | 326.7488
1743.0667 | 337.6985 | 335.9963 | 326.4719
1744.0667 | 337.5193 | 336.1352 | 326.4854
1745.0667 | 337.6408 | 335.9313 | 326.3743
1746.0667 | 337.8957 | 335.7417 | 326.2329
1747.0667 | 337.9181 | 335.5961 | 326.4418
1748.0667 | 337.8667 | 335.3255 | 326.3906
1749.0667 | 337.5834 | 334.9929 | 326.6432
1750.0667 | 337.3209 | 334.8672 | 326.6555
1751.0667 | 337.2635 | 334.6727 | 326.5984
1752.0667 | 337.4531 | 334.7294 | 326.2376
1753.0667 | 337.6519 | 334.9913 | 326.1172
1754.0667 | 337.0847 | 334.9982 | 326.0409
1755.0667 | 337.1746 | 335.4029 | 326.1194
1756.0667 | 337.3833 | 335.6453 | 326.2646
1757.0667 | 337.4731 | 335.5989 | 326.6839
1758.0667 | 337.5975 | 335.7423 | 326.9332
1759.0667 | 338.0852 | 335.7881 | 328.4438
1760.0667 | 338.1187 | 336.5811 | 328.9373
1761.0667 | 339.3549 | 336.9266 | 329.4948
1762.0667 | 340.2374 | 337.6704 | 329.5373
1763.0667 | 340.4918 | 337.892 | 330.0804
1764.0667 | 340.7919 | 338.3113 | 329.8778
1765.0667 | 340.816 | 338.6161 | 330.0582
1766.0667 | 340.7835 | 338.5416 | 330.3914
1767.0667 | 340.8964 | 338.5082 | 330.7853
1768.0667 | 340.6385 | 338.4408 | 330.4197
1769.0823 | 340.539 | 338.2636 | 330.1075
1770.0667 | 340.3493 | 338.5321 | 329.8332
1771.0667 | 340.6918 | 338.9535 | 329.6268
1772.0667 | 340.9645 | 339.0477 | 329.5403
1773.0667 | 340.9605 | 339.892 | 329.6516
1774.0667 | 341.3344 | 339.6756 | 329.7689
1775.0667 | 341.4515 | 339.4935 | 329.7319
1776.0667 | 341.386 | 339.562 | 329.9052
1777.0667 | 341.0665 | 339.5096 | 330.0989
1778.0667 | 341.0378 | 340.0135 | 329.9594
1779.0667 | 342.2978 | 340.0404 | 330.257
1780.0667 | 342.2463 | 339.4241 | 330.156
1781.0667 | 341.7349 | 339.2082 | 330.5261
1782.0667 | 341.1998 | 338.8465 | 330.6307
1783.0667 | 340.7418 | 338.8101 | 330.9229
1784.0823 | 340.0105 | 339.0828 | 331.179
1785.0667 | 339.9638 | 339.202 | 331.5049
1786.0667 | 339.6718 | 339.3515 | 331.6565
1787.0667 | 339.4114 | 339.3023 | 331.6389
1788.0667 | 339.5211 | 339.4032 | 331.8703
1789.0667 | 339.363 | 339.7168 | 332.2614
1790.0667 | 339.3285 | 339.9984 | 333.1387
1791.0667 | 339.5088 | 339.917 | 333.2801
1792.0667 | 339.805 | 339.9509 | 333.346
1793.0667 | 340.1828 | 340.1519 | 333.1836
1794.0667 | 340.3743 | 339.9126 | 332.5316
1795.0667 | 340.4318 | 340.1262 | 332.5962
1796.0667 | 340.2747 | 340.3588 | 332.1635
1797.0667 | 340.1577 | 340.2804 | 332.049
1798.0667 | 340.24 | 340.5083 | 332.1525
1799.0667 | 340.2505 | 340.2122 | 332.1276
1800.0823 | 340.3034 | 340.4132 | 331.5082
1801.0667 | 340.6915 | 340.3564 | 330.9297
1802.0667 | 340.9445 | 340.8575 | 330.7346
1803.0667 | 340.8308 | 340.2749 | 330.3845
1804.0667 | 340.8335 | 339.9423 | 330.6003
1805.0667 | 340.8746 | 339.8246 | 330.512
1806.0667 | 341.3168 | 339.5664 | 330.1038
1807.0667 | 340.9614 | 339.5433 | 329.863
1808.0667 | 341.2212 | 339.6616 | 329.4136
1809.0667 | 341.0963 | 339.4603 | 329.7697
1810.0667 | 341.3373 | 339.3109 | 329.3147
1811.0667 | 341.0151 | 339.6134 | 329.1992
1812.0667 | 341.2881 | 339.8035 | 329.3461
1813.0667 | 340.8365 | 339.7783 | 329.2872
1814.0667 | 340.364 | 339.3653 | 329.5534
1815.0667 | 339.6529 | 338.9606 | 329.6926
1816.0667 | 339.0976 | 338.6341 | 329.2564
1817.0667 | 338.6534 | 338.4676 | 328.7888
1818.0667 | 338.0878 | 338.3815 | 328.6861
1819.0667 | 337.6888 | 338.2893 | 328.1409
1820.0667 | 337.7826 | 338.2577 | 327.8714
1821.0667 | 338.0867 | 338.3726 | 327.6822
1822.0667 | 338.2232 | 338.1437 | 327.6495
1823.0667 | 338.0088 | 338.2006 | 328.1193
1824.0667 | 337.88 | 338.2782 | 328.2118
1825.0667 | 338.1283 | 338.078 | 327.9235
1826.0667 | 338.2684 | 337.9073 | 328.0392
1827.0667 | 338.2549 | 337.8715 | 328.2439
1828.0667 | 338.2776 | 338.0496 | 328.4805
1829.0667 | 337.8846 | 338.3434 | 328.5154
1830.0667 | 338.0342 | 338.4192 | 328.4715
1831.0667 | 338.2203 | 338.4852 | 329.0201
1832.0667 | 337.7883 | 338.7473 | 329.6801
1833.0667 | 337.9187 | 338.7139 | 329.9587
1834.0667 | 338.4738 | 338.7922 | 330.3424
1835.0667 | 339.2926 | 338.6827 | 330.2358
1836.0667 | 339.5071 | 339.1281 | 330.1727
1837.0667 | 339.9221 | 339.6385 | 329.9282
1838.0667 | 340.2509 | 339.6253 | 330.0989
1839.0667 | 340.3665 | 339.9129 | 330.2819
1840.0667 | 340.5869 | 340.0529 | 330.0578
1841.0667 | 340.8218 | 340.3568 | 330.4291
1842.0667 | 340.8395 | 340.441 | 329.772
1843.0667 | 340.301 | 340.6756 | 329.3941
1844.0667 | 340.1097 | 340.8508 | 329.37
1845.0667 | 339.8018 | 340.5777 | 329.5568
1846.0667 | 339.5205 | 340.4972 | 330.2588
1847.0667 | 339.655 | 340.4772 | 330.4938
1848.0667 | 339.7217 | 340.4718 | 330.2721
1849.0667 | 340.0361 | 340.5059 | 330.3944
1850.0667 | 340.0481 | 340.6333 | 330.3315
1851.0667 | 339.8498 | 341.0034 | 330.0932
1852.0667 | 339.9295 | 341.1774 | 329.6836
1853.0667 | 340.2593 | 341.1737 | 329.561
1854.0667 | 340.4409 | 341.4626 | 329.5372
1855.0667 | 340.2332 | 341.4783 | 329.4077
1856.0667 | 340.5252 | 341.4206 | 329.0444
1857.0667 | 340.0847 | 341.3827 | 329.0868
1858.0667 | 340.0399 | 341.1894 | 329.1514
1859.0667 | 340.1989 | 341.046 | 329.6747
1860.0667 | 339.7564 | 341.068 | 330.4374
1861.0667 | 339.5946 | 341.2508 | 330.3757
1862.0667 | 339.5273 | 341.1899 | 330.5573
1863.0667 | 339.7676 | 341.3877 | 331.1526
1864.0667 | 340.0838 | 341.1346 | 330.9877
1865.0667 | 339.7472 | 341.0579 | 330.4772
1866.0667 | 340.1683 | 340.8638 | 330.492
1867.0667 | 340.287 | 340.9305 | 330.6211
1868.0667 | 340.1271 | 341.0809 | 330.8685
1869.0667 | 339.9392 | 340.9641 | 330.7594
1870.0667 | 339.5858 | 340.9657 | 330.6931
1871.0667 | 339.5414 | 340.9612 | 330.902
1872.0667 | 339.1705 | 340.9493 | 331.0977
1873.0667 | 339.3467 | 341.3067 | 331.9319
1874.0667 | 339.1917 | 341.3323 | 332.0767
1875.0667 | 338.7889 | 341.5302 | 332.0001
1876.0667 | 338.4679 | 341.6805 | 331.8825
1877.0667 | 338.2975 | 342.3105 | 331.7904
1878.0667 | 338.4132 | 342.5242 | 332.0038
1879.0667 | 338.6934 | 342.3538 | 332.2028
1880.0667 | 338.5818 | 342.2931 | 332.2939
1881.0667 | 338.8876 | 342.81 | 332.4453
1882.0667 | 339.4113 | 344.0594 | 332.4878
1883.0667 | 339.7931 | 343.8954 | 332.5133
1884.0667 | 339.9939 | 344.1206 | 332.5288
1885.0667 | 340.8539 | 343.8737 | 332.7989
1886.0667 | 341.3479 | 343.784 | 332.712
1887.0667 | 341.8952 | 343.6416 | 332.4192
1888.0667 | 342.0422 | 343.5953 | 331.9431
1889.0667 | 342.5296 | 343.8051 | 332.11
1890.0667 | 342.6778 | 343.9628 | 332.7967
1891.0667 | 342.8588 | 343.9035 | 333.8954
1892.0667 | 342.9255 | 344.2847 | 334.0839
1893.0667 | 343.0287 | 344.2514 | 334.3254
1894.0667 | 342.8928 | 344.6047 | 334.4684
1895.0667 | 342.9426 | 344.9793 | 334.3574
1896.0667 | 342.7252 | 344.733 | 334.4014
1897.0667 | 342.7627 | 344.4458 | 334.8549
1898.0667 | 343.1453 | 344.0935 | 334.6672
1899.0667 | 342.9141 | 343.5084 | 334.8216
1900.0667 | 342.3624 | 343.6464 | 335.0156
1901.0667 | 342.3278 | 343.6797 | 334.9898
1902.0667 | 342.3671 | 343.7579 | 334.8443
1903.0667 | 342.4902 | 343.5609 | 335.021
1904.0667 | 342.6408 | 344.3005 | 335.0272
1905.0667 | 342.4947 | 344.1048 | 334.7571
1906.0667 | 342.2815 | 344.0546 | 334.9031
1907.0667 | 342.7695 | 344.0428 | 334.7226
1908.0667 | 342.8848 | 344.0602 | 334.5293
1909.0667 | 343.1426 | 344.7528 | 334.5563
1910.0667 | 343.3868 | 345.6812 | 334.3354
1911.0667 | 343.2919 | 345.5426 | 334.1606
1912.0667 | 343.11 | 346.9476 | 334.0604
1913.0667 | 343.2357 | 346.8543 | 334.3766
1914.0667 | 343.7926 | 346.7482 | 334.589
1915.0667 | 344.2354 | 346.2465 | 334.4623
1916.0667 | 344.6155 | 345.9411 | 334.5387
1917.0667 | 344.3197 | 345.3253 | 334.203
1918.0667 | 344.1782 | 345.0968 | 334.4044
1919.0667 | 344.4069 | 344.9466 | 334.0689
1920.0667 | 344.0174 | 344.9284 | 333.895
1921.0667 | 343.9458 | 344.8249 | 333.6804
1922.0667 | 343.9573 | 344.9825 | 333.8578
1923.0667 | 344.0986 | 345.3288 | 334.5674
1924.0667 | 344.1991 | 345.7341 | 335.2631
1925.0667 | 344.35 | 346.6954 | 335.2695
1926.0667 | 344.6986 | 347.1252 | 335.1535
1927.0667 | 344.55 | 347.5995 | 335.2463
1928.0667 | 344.7842 | 347.7768 | 335.6952
1929.0667 | 345.0288 | 347.6768 | 335.8953
1930.0667 | 344.8927 | 347.2624 | 335.5305
1931.0667 | 344.6495 | 347.1601 | 335.5826
1932.0667 | 344.1851 | 346.936 | 335.6984
1933.0667 | 343.6914 | 346.3838 | 335.5936
1934.0667 | 343.2973 | 346.2723 | 335.3648
1935.0667 | 343.0984 | 346.0852 | 335.0288
1936.0667 | 342.8298 | 346.2717 | 335.0716
1937.0667 | 342.7481 | 346.6729 | 335.61
1938.0667 | 343.1807 | 347.3161 | 336.1544
1939.0667 | 343.2197 | 347.3374 | 336.2426
1940.0667 | 343.6741 | 347.3266 | 336.3358
1941.0667 | 343.9879 | 347.2763 | 336.3128
1942.0667 | 344.819 | 347.0383 | 336.9091
1943.0667 | 345.2901 | 346.8478 | 337.1099
1944.0667 | 345.8528 | 347.2507 | 337.0115
1945.0823 | 346.0931 | 347.553 | 337.383
1946.0667 | 346.1498 | 347.5774 | 338.0558
1947.0667 | 346.1128 | 347.4503 | 338.2097
1948.0667 | 345.6945 | 347.435 | 338.0522
1949.0667 | 345.8397 | 347.2544 | 338.3532
1950.0667 | 345.8955 | 347.2157 | 338.4938
1951.0667 | 345.9548 | 347.3408 | 337.9829
1952.0667 | 346.4382 | 347.5489 | 337.6442
1953.0667 | 346.608 | 347.7777 | 338.0382
1954.0667 | 346.4664 | 347.6525 | 338.6911
1955.0667 | 346.6662 | 347.7618 | 338.6996
1956.0667 | 346.6859 | 347.7511 | 339.1181
1957.0667 | 346.4862 | 347.7741 | 338.9921
1958.0667 | 346.589 | 348.1277 | 338.7443
1959.0823 | 346.6402 | 348.3964 | 338.8259
1960.0667 | 347.2761 | 348.3335 | 339.2277
1961.0667 | 347.6095 | 348.3281 | 339.2412
1962.0667 | 347.5731 | 348.2013 | 339.4248
1963.0667 | 347.3938 | 347.8248 | 339.552
1964.0667 | 347.8816 | 347.8276 | 339.3176
1965.0667 | 347.669 | 347.6676 | 339.2846
1966.0667 | 347.9889 | 347.5784 | 339.2141
1967.0667 | 347.9278 | 347.9537 | 339.3055
1968.0667 | 347.5787 | 347.5086 | 339.2975
1969.0667 | 347.0711 | 347.5691 | 338.7803
1970.0667 | 347.0247 | 347.4332 | 338.914
1971.0667 | 347.0153 | 347.2176 | 339.1987
1972.0667 | 346.9783 | 347.1021 | 339.6743
1973.0667 | 347.1529 | 346.9163 | 339.3178
1974.0823 | 348.0955 | 346.6778 | 339.1065
1975.0823 | 347.861 | 346.6583 | 338.9877
1976.0667 | 348.016 | 346.7953 | 339.6475
1977.0667 | 348.6273 | 347.4835 | 339.5656
1978.0667 | 348.704 | 348.0814 | 339.7533
1979.0667 | 348.6214 | 348.1205 | 340.0257
1980.0667 | 348.5592 | 347.5625 | 339.9209
1981.0667 | 348.4845 | 349.0727 | 340.1838
1982.0667 | 348.4699 | 348.6643 | 340.163
1983.0667 | 348.5104 | 348.4423 | 339.5938
1984.0667 | 348.5373 | 348.4456 | 339.0569
1985.0667 | 348.5723 | 348.4173 | 338.7756
1986.0667 | 348.7706 | 348.5202 | 338.5491
1987.0667 | 348.7616 | 348.6239 | 338.6667
1988.0667 | 348.7968 | 348.6151 | 338.2588
1989.0667 | 349.0967 | 348.853 | 338.536
1990.0667 | 348.9522 | 348.8695 | 339.505
1991.0667 | 348.724 | 348.9886 | 339.8244
1992.0667 | 349.6859 | 348.9981 | 339.7917
1993.0667 | 349.7535 | 349.6214 | 340.1944
1994.0667 | 349.3865 | 349.7796 | 339.9201
1995.0667 | 349.0921 | 349.7173 | 339.8257
1996.0667 | 348.9225 | 349.7554 | 340.1798
1997.0667 | 348.8884 | 349.5634 | 339.6678
1998.0667 | 348.6807 | 349.956 | 339.3534
1999.0667 | 349.2722 | 350.4455 | 339.1516
2000.0667 | 349.6653 | 350.8175 | 339.7079
2001.0667 | 349.5493 | 351.3579 | 339.882
2002.0667 | 349.5765 | 351.8641 | 340.5852
2003.0667 | 349.9364 | 351.5538 | 341.3226
2004.0667 | 349.8032 | 351.2682 | 340.8072
2005.0667 | 349.7957 | 351.2218 | 340.438
2006.0667 | 349.7313 | 350.904 | 340.8406
2007.0667 | 349.6667 | 350.5507 | 340.6908
2008.0667 | 349.458 | 350.0753 | 340.0835
2009.0667 | 349.1664 | 349.803 | 339.8224
2010.0667 | 348.8284 | 349.7698 | 340.2147
2011.0667 | 348.5353 | 349.8225 | 340.1637
2012.0667 | 348.2268 | 349.4973 | 340.1095
2013.0667 | 347.9384 | 349.547 | 340.5123
2014.0823 | 347.923 | 349.9942 | 340.4966
2015.0667 | 347.8275 | 349.7088 | 340.5499
2016.0667 | 347.868 | 349.7313 | 339.9864
2017.0667 | 347.4986 | 349.7746 | 339.5938
2018.0667 | 347.1293 | 349.8565 | 339.1294
2019.0667 | 346.8124 | 349.5634 | 338.9694
2020.0667 | 346.6613 | 349.5154 | 339.4855
2021.0667 | 346.8911 | 349.7508 | 339.3701
2022.0667 | 346.6729 | 349.7527 | 339.3312
2023.0667 | 346.4957 | 349.4164 | 339.1689
2024.0667 | 346.6233 | 349.7366 | 339.4923
2025.0667 | 346.6047 | 350.081 | 339.6682
2026.0667 | 346.7241 | 350.2304 | 339.1057
2027.0667 | 346.7593 | 350.4052 | 339.2724
2028.0667 | 346.7473 | 350.6026 | 339.0765
2029.0667 | 347.2504 | 350.8443 | 339.3685
2030.0667 | 347.3091 | 350.0497 | 339.5447
2031.0667 | 347.1792 | 349.4957 | 339.7163
2032.0667 | 347.6923 | 349.2594 | 339.9137
2033.0667 | 347.7844 | 349.2965 | 339.8725
2034.0667 | 347.5245 | 349.2427 | 339.6817
2035.0667 | 347.2634 | 349.3134 | 339.4011
2036.0667 | 347.3462 | 349.5527 | 339.4995
2037.0667 | 347.2414 | 349.5253 | 340.0126
2038.0667 | 346.9918 | 349.6805 | 340.4565
2039.0667 | 347.1017 | 349.665 | 340.3523
2040.0667 | 347.3423 | 349.8373 | 340.6071
2041.0667 | 347.1763 | 349.7451 | 340.4892
2042.0667 | 347.573 | 349.8998 | 340.2576
2043.0667 | 347.4361 | 349.9738 | 340.4739
2044.0667 | 347.6802 | 349.7272 | 340.9635
2045.0667 | 347.3263 | 350.2498 | 341.1953
2046.0667 | 347.2111 | 349.9217 | 340.5883
2047.0667 | 347.0553 | 349.62 | 340.2921
2048.0667 | 346.6213 | 349.8018 | 340.4944
2049.0667 | 346.345 | 349.8615 | 340.91
2050.0667 | 346.2402 | 349.7889 | 340.8108
2051.0667 | 346.6993 | 349.8637 | 340.5877
2052.0667 | 346.4398 | 350.2831 | 340.4949
2053.0667 | 346.358 | 350.743 | 340.0661
2054.0667 | 346.4114 | 351.1075 | 339.9326
2055.0667 | 346.3121 | 351.0891 | 340.1009
2056.0667 | 346.6909 | 351.0723 | 340.3331
2057.0667 | 347.2641 | 351.238 | 340.683
2058.0667 | 347.6164 | 351.2002 | 340.3302
2059.0667 | 347.7624 | 351.0679 | 340.1041
2060.0667 | 348.0008 | 351.2915 | 340.4411
2061.0667 | 348.7722 | 351.7289 | 340.778
2062.0667 | 349.1758 | 352.2009 | 341.3106
2063.0667 | 349.5845 | 352.7694 | 341.6098
2064.0667 | 349.9585 | 353.1346 | 342.3862
2065.0823 | 349.9244 | 353.0306 | 342.6734
2066.0667 | 349.9526 | 352.772 | 342.5347
2067.0667 | 349.6284 | 352.3984 | 342.1401
2068.0667 | 349.4822 | 352.1502 | 341.8717
2069.0667 | 350.0074 | 352.5138 | 341.5371
2070.0667 | 350.1296 | 352.6009 | 341.8791
2071.0667 | 350.1793 | 352.7597 | 341.9361
2072.0667 | 350.4855 | 353.0064 | 341.903
2073.0667 | 350.3546 | 353.0732 | 341.8887
2074.0667 | 349.9277 | 352.8645 | 342.2945
2075.0667 | 350.2589 | 352.7995 | 342.1075
2076.0667 | 350.4298 | 352.6941 | 342.5235
2077.0667 | 350.3269 | 352.8638 | 342.6186
2078.0667 | 350.6756 | 352.8699 | 342.7425
2079.0667 | 351.7358 | 353.1413 | 343.3618
2080.0667 | 351.7362 | 352.9372 | 344.0957
2081.0667 | 351.7584 | 352.8331 | 344.2414
2082.0667 | 351.3983 | 353.0878 | 345.0799
2083.0667 | 351.2451 | 353.1866 | 345.2303
2084.0667 | 350.7017 | 353.051 | 345.1663
2085.0667 | 350.6453 | 353.0601 | 344.6568
2086.0667 | 350.8849 | 352.8637 | 344.1648
2087.0667 | 350.7978 | 352.5719 | 344.1885
2088.0667 | 350.6464 | 352.2537 | 344.3895
2089.0667 | 350.5034 | 352.0193 | 343.9388
2090.0667 | 350.2963 | 351.7811 | 344.0651
2091.0667 | 350.8157 | 351.8637 | 344.2495
2092.0667 | 351.2265 | 352.0392 | 344.3435
2093.0667 | 351.1821 | 352.1418 | 344.3337
2094.0667 | 351.432 | 352.1499 | 344.0168
2095.0667 | 352.1473 | 352.2932 | 344.0772
2096.0667 | 352.5253 | 353.0032 | 344.4416
2097.0667 | 352.159 | 353.053 | 344.5736
2098.0667 | 352.0336 | 353.0264 | 344.9095
2099.0823 | 352.714 | 353.1305 | 344.8215
2100.0667 | 352.7667 | 353.1546 | 344.829
2101.0667 | 352.9611 | 352.877 | 344.5527
2102.0667 | 352.9686 | 353.0419 | 344.3412
2103.0667 | 353.3322 | 353.1283 | 345.2044
2104.0667 | 353.4345 | 353.3784 | 345.2255
2105.0667 | 353.4123 | 354.1095 | 344.9946
2106.0667 | 353.2925 | 354.1674 | 345.2298
2107.0667 | 353.023 | 353.8632 | 345.5476
2108.0667 | 352.6679 | 353.6033 | 345.6344
2109.0667 | 352.7846 | 353.4334 | 345.5745
2110.0667 | 353.03 | 353.807 | 345.6908
2111.0667 | 352.7893 | 353.5183 | 346.5853
2112.0667 | 352.5725 | 353.3162 | 346.299
2113.0667 | 352.5482 | 353.3731 | 346.4836
2114.0823 | 352.9308 | 353.3587 | 346.2358
2115.0667 | 353.2583 | 353.3238 | 345.7224
2116.0667 | 353.2052 | 353.5611 | 345.25
2117.0667 | 353.0176 | 353.1312 | 344.9614
2118.0667 | 353.415 | 353.1606 | 344.385
2119.0667 | 353.7404 | 353.0288 | 343.9439
2120.0667 | 353.6443 | 352.9232 | 343.6217
2121.0667 | 354.1047 | 352.8038 | 343.6493
2122.0667 | 353.9709 | 352.8635 | 344.1244
2123.0667 | 354.094 | 353.9082 | 343.8874
2124.0667 | 354.0678 | 353.937 | 344.1834
2125.0667 | 353.7608 | 354.2419 | 344.4404
2126.0667 | 353.3175 | 354.1971 | 344.7984
2127.0667 | 353.0869 | 354.3214 | 344.6486
2128.0667 | 352.9224 | 354.5473 | 344.2088
2129.0667 | 353.1684 | 354.3538 | 344.4372
2130.0667 | 353.5886 | 354.2148 | 344.452
2131.0667 | 353.4712 | 354.0479 | 344.3827
2132.0667 | 353.2661 | 353.9242 | 344.0168
2133.0667 | 352.8689 | 354.4385 | 344.0127
2134.0667 | 352.3277 | 354.0825 | 343.7143
2135.0667 | 351.9126 | 354.0162 | 343.6199
2136.0667 | 351.9152 | 354.2171 | 343.2491
2137.0823 | 352.3908 | 354.3393 | 342.864
2138.0823 | 352.4862 | 354.2841 | 342.5642
2139.0667 | 352.0613 | 354.2453 | 343.1543
2140.0667 | 352.8052 | 354.6106 | 343.424
2141.0667 | 353.4023 | 355.0904 | 343.2195
2142.0667 | 353.8436 | 355.186 | 343.242
2143.0667 | 354.1592 | 355.5184 | 343.8445
2144.0667 | 354.5538 | 355.6531 | 344.4413
2145.0667 | 354.5329 | 355.969 | 344.5093
2146.0667 | 355.0893 | 356.3609 | 345.3581
2147.0667 | 355.5288 | 356.5968 | 345.2069
2148.0667 | 355.3405 | 356.6768 | 345.2311
2149.0667 | 354.9246 | 356.5133 | 345.6133
2150.0667 | 354.7414 | 356.2616 | 345.434
2151.0667 | 354.7335 | 356.0326 | 345.3779
2152.0667 | 354.1425 | 355.7176 | 345.4072
2153.0667 | 354.1426 | 355.7159 | 345.2893
2154.0667 | 353.7542 | 355.465 | 345.1675
2155.0667 | 353.2712 | 355.3298 | 345.0557
2156.0667 | 353.2478 | 355.7024 | 344.6124
2157.0667 | 353.2714 | 355.834 | 344.8519
2158.0667 | 352.8789 | 355.7858 | 345.6313
2159.0667 | 352.6563 | 355.913 | 345.6848
2160.0667 | 352.5003 | 355.936 | 345.3412
2161.0667 | 352.6211 | 356.3537 | 345.7826
2162.0667 | 353.7081 | 356.7609 | 345.9218
2163.0667 | 354.0673 | 356.998 | 346.0658
2164.0667 | 354.6001 | 357.206 | 346.8609
2165.0667 | 354.858 | 357.8147 | 346.9721
2166.0667 | 355.0852 | 357.6694 | 346.9825
2167.0667 | 355.1357 | 357.4253 | 347.0399
2168.0667 | 355.005 | 357.2281 | 346.9808
2169.0667 | 355.1712 | 357.035 | 346.7566
2170.0667 | 354.8805 | 357.4539 | 346.4492
2171.0667 | 354.5004 | 357.3398 | 346.343
2172.0667 | 354.1209 | 357.3423 | 346.2929
2173.0667 | 353.9462 | 357.4834 | 346.2832
2174.0667 | 353.8126 | 357.4524 | 345.9681
2175.0667 | 353.8022 | 357.3611 | 345.5628
2176.0667 | 353.6529 | 357.3104 | 345.5348
2177.0667 | 353.8151 | 357.5991 | 345.4794
2178.0667 | 354.1021 | 357.2405 | 345.8379
2179.0667 | 354.324 | 357.5409 | 345.9998
2180.0667 | 354.5051 | 357.3382 | 346.2676
2181.0667 | 354.3637 | 357.3251 | 345.9282
2182.0667 | 355.2542 | 357.1394 | 345.5887
2183.0667 | 355.5009 | 357.4392 | 345.4207
2184.0667 | 355.9985 | 357.4307 | 345.5383
2185.0667 | 356.3304 | 357.7676 | 345.678
2186.0667 | 356.535 | 357.7446 | 345.7308
2187.0667 | 356.9418 | 357.2907 | 345.6415
2188.0667 | 356.9862 | 357.376 | 346.2338
2189.0667 | 357.4388 | 357.0317 | 346.2846
2190.0667 | 357.389 | 356.7887 | 346.7669
2191.0667 | 357.5859 | 356.8688 | 347.3089
2192.0667 | 357.2935 | 357.0885 | 347.1293
2193.0667 | 356.9945 | 356.8826 | 346.6792
2194.0667 | 356.6436 | 357.0855 | 346.3026
2195.0667 | 356.2815 | 357.243 | 346.0179
2196.0667 | 357.0758 | 357.5531 | 345.4937
2197.0667 | 357.2767 | 357.5725 | 345.8809
2198.0667 | 357.6219 | 357.0668 | 345.7621
2199.0667 | 357.7143 | 356.899 | 345.6749
2200.0667 | 358.3416 | 356.8046 | 345.9536
2201.0667 | 358.2313 | 356.3581 | 346.0898
2202.0667 | 357.6349 | 356.0665 | 345.9131
2203.0667 | 357.4472 | 356.1667 | 345.6761
2204.0667 | 357.2287 | 356.1558 | 345.3053
2205.0667 | 356.9112 | 356.0291 | 345.4983
2206.0667 | 356.8592 | 355.9855 | 345.9046
2207.0667 | 356.908 | 356.5959 | 346.778
2208.0667 | 357.1908 | 356.957 | 347.8583
2209.0667 | 357.3506 | 357.3989 | 348.12
2210.0667 | 357.5503 | 357.7362 | 347.9153
2211.0667 | 357.6108 | 357.384 | 347.919
2212.0667 | 357.5766 | 357.0732 | 347.6069
2213.0667 | 357.4434 | 357.064 | 347.1424
2214.0667 | 357.3217 | 356.7794 | 346.6646
2215.0667 | 357.058 | 356.4585 | 346.2244
2216.0667 | 356.5257 | 356.3773 | 346.2374
2217.0667 | 356.2351 | 356.2573 | 346.8304
2218.0667 | 355.9874 | 356.1788 | 346.9506
2219.0667 | 355.6722 | 356.1333 | 346.7515
2220.0667 | 355.3476 | 356.2742 | 346.3172
2221.0667 | 354.9217 | 356.08 | 345.8164
2222.0667 | 354.6426 | 356.0154 | 345.2757
2223.0667 | 354.4622 | 355.5529 | 344.8064
2224.0667 | 354.1456 | 355.1996 | 345.0347
2225.0667 | 354.2759 | 355.2969 | 345.262
2226.0667 | 354.4628 | 355.5879 | 345.6741
2227.0667 | 353.9764 | 355.4739 | 346.1677
2228.0667 | 353.6781 | 356.0993 | 345.9238
2229.0667 | 353.8159 | 356.1122 | 345.6971
2230.0667 | 353.4558 | 355.7738 | 345.3851
2231.0667 | 353.6496 | 355.7277 | 344.8955
2232.0667 | 353.3814 | 355.8562 | 344.5177
2233.0667 | 353.1619 | 355.796 | 344.5075
2234.0667 | 352.9728 | 355.964 | 344.4252
2235.0667 | 352.8527 | 356.4948 | 344.8656
2236.0667 | 352.6885 | 356.5194 | 345.1526
2237.0667 | 353.4867 | 356.8353 | 345.9447
2238.0667 | 353.9702 | 356.8298 | 345.9154
2239.0667 | 353.9228 | 356.696 | 346.2218
2240.0667 | 354.0518 | 356.9186 | 346.3444
2241.0667 | 354.3878 | 356.8634 | 346.4998
2242.0667 | 354.6081 | 356.8937 | 346.6233
2243.0667 | 354.685 | 357.2151 | 346.6434
2244.0667 | 354.7284 | 357.3544 | 346.7953
2245.0667 | 354.4211 | 357.1081 | 346.6543
2246.0667 | 354.0769 | 356.835 | 346.6545
2247.0667 | 354.1955 | 356.6858 | 346.6435
2248.0667 | 354.2156 | 357.1839 | 346.8504
2249.0667 | 354.0102 | 356.6956 | 346.9283
2250.0667 | 353.8916 | 356.4561 | 346.8809
2251.0667 | 353.5753 | 356.7016 | 347.0997
2252.0667 | 353.4854 | 356.4253 | 346.9319
2253.0667 | 353.6785 | 356.2607 | 346.7096
2254.0667 | 353.4122 | 355.8931 | 346.7001
2255.0667 | 353.577 | 355.7238 | 346.2127
2256.0667 | 353.3181 | 355.3687 | 345.7358
2257.0667 | 352.9979 | 355.6405 | 345.6425
2258.0667 | 352.6489 | 355.748 | 345.2428
2259.0667 | 352.6272 | 355.7821 | 344.9356
2260.0667 | 352.8789 | 355.6433 | 344.7646
2261.0667 | 353.095 | 355.8141 | 344.8798
2262.0667 | 353.999 | 356.1849 | 345.3541
2263.0667 | 354.2489 | 356.5657 | 345.738
2264.0667 | 354.3108 | 357.2615 | 346.113
2265.0667 | 354.5362 | 357.8064 | 347.0933
2266.0667 | 354.4196 | 357.9017 | 347.3925
2267.0667 | 354.6671 | 357.6522 | 347.1705
2268.0667 | 354.6894 | 357.4578 | 346.9002
2269.0667 | 354.703 | 357.3677 | 346.6597
2270.0667 | 354.4222 | 357.2858 | 346.6538
2271.0667 | 354.1873 | 357.2775 | 346.6794
2272.0667 | 354.4668 | 357.2813 | 346.9782
2273.0667 | 354.1909 | 357.4518 | 346.5965
2274.0823 | 354.1714 | 357.2884 | 346.224
2275.0667 | 354.4928 | 357.3077 | 345.8657
2276.0667 | 354.4831 | 357.3941 | 345.5508
2277.0667 | 354.7203 | 357.7153 | 345.8265
2278.0667 | 354.5195 | 357.7935 | 345.8361
2279.0667 | 354.499 | 357.9192 | 345.5891
2280.0667 | 354.6631 | 357.9134 | 345.3663
2281.0667 | 354.7102 | 358.2585 | 345.3709
2282.0667 | 354.6137 | 358.1452 | 345.3182
2283.0667 | 354.6558 | 357.7286 | 345.1977
2284.0667 | 354.5491 | 357.2905 | 345.0715
2285.0667 | 354.4521 | 356.9822 | 345.142
2286.0667 | 354.9197 | 357.2088 | 345.3008
2287.0667 | 354.7528 | 357.4771 | 345.6508
2288.0667 | 354.6081 | 357.3454 | 345.874
2289.0823 | 354.4079 | 357.5909 | 346.8505
2290.0667 | 354.3846 | 357.5235 | 346.4549
2291.0667 | 354.0848 | 357.2357 | 346.2756
2292.0667 | 354.7254 | 357.0316 | 345.8336
2293.0667 | 354.4778 | 356.7896 | 345.3559
2294.0667 | 354.9231 | 356.7241 | 345.1941
2295.0667 | 354.5226 | 356.5366 | 344.6156
2296.0667 | 354.1311 | 356.9473 | 344.4179
2297.0667 | 353.8593 | 356.711 | 344.2736
2298.0667 | 353.9233 | 356.5476 | 344.0494
2299.0667 | 354.0501 | 356.7854 | 343.8823
2300.0667 | 353.9121 | 357.1538 | 343.8025
2301.0667 | 354.1595 | 358.3171 | 343.9749
2302.0667 | 354.7238 | 358.082 | 344.0537
2303.0667 | 354.7906 | 357.8867 | 343.7665
2304.0667 | 354.5053 | 357.9344 | 344.1039
2305.0667 | 354.2265 | 357.8096 | 344.3922
2306.0667 | 354.0635 | 357.6952 | 344.6478
2307.0667 | 353.8708 | 357.817 | 344.4787
2308.0667 | 353.5311 | 358.0384 | 344.4254
2309.0667 | 353.5619 | 358.325 | 344.9231
2310.0667 | 354.0066 | 358.2259 | 345.4231
2311.0667 | 354.1072 | 358.923 | 345.5498
2312.0667 | 354.5657 | 359.524 | 345.9042
2313.0667 | 354.4721 | 359.2256 | 345.9493
2314.0667 | 354.6841 | 359.3638 | 345.9648
2315.0667 | 354.7767 | 359.2983 | 346.1981
2316.0667 | 354.5296 | 358.7706 | 346.1112
2317.0667 | 354.5616 | 358.6193 | 345.8555
2318.0667 | 354.6686 | 358.5028 | 345.424
2319.0667 | 355.1581 | 359.6085 | 345.314
2320.0667 | 355.0667 | 359.5733 | 345.2671
2321.0667 | 354.6732 | 359.6607 | 345.3712
2322.0667 | 355.1939 | 359.459 | 345.3138
2323.0667 | 355.6178 | 359.0972 | 345.2521
2324.0667 | 355.2767 | 360.1642 | 344.8082
2325.0667 | 354.9248 | 359.6022 | 344.8788
2326.0667 | 354.9909 | 359.5111 | 344.5116
2327.0667 | 354.728 | 359.464 | 344.2906
2328.0667 | 354.421 | 359.207 | 344.2098
2329.0667 | 355.1378 | 359.2448 | 344.9245
2330.0667 | 355.2202 | 359.1851 | 344.7484
2331.0667 | 355.9834 | 359.4482 | 344.8288
2332.0667 | 356.0301 | 359.1356 | 344.6855
2333.0667 | 356.0843 | 358.6609 | 345.1218
2334.0823 | 356.0055 | 358.5428 | 345.6188
2335.0667 | 356.0203 | 358.536 | 345.7813
2336.0667 | 355.832 | 358.581 | 345.7286
2337.0667 | 356.0293 | 358.5487 | 345.6714
2338.0667 | 355.9502 | 358.3855 | 345.4055
2339.0667 | 355.4785 | 358.1787 | 345.5393
2340.0667 | 355.3364 | 358.528 | 345.5559
2341.0667 | 355.2042 | 358.2764 | 345.464
2342.0667 | 355.2984 | 358.07 | 345.4194
2343.0667 | 355.1895 | 358.8324 | 345.4541
2344.0667 | 355.2178 | 358.8135 | 345.2793
2345.0667 | 355.6747 | 358.5514 | 345.7361
2346.0667 | 355.2816 | 358.706 | 345.3896
2347.0667 | 355.6045 | 358.9033 | 345.2424
2348.0667 | 355.1133 | 358.6017 | 345.2309
2349.0667 | 354.5771 | 358.4168 | 345.1259
2350.0667 | 354.3451 | 358.2439 | 345.1701
2351.0667 | 353.7873 | 358.368 | 345.8678
2352.0667 | 353.2885 | 358.186 | 346.165
2353.0667 | 352.9464 | 357.9956 | 346.2567
2354.0667 | 352.7884 | 357.8043 | 346.0679
2355.0667 | 353.0391 | 357.7993 | 345.8537
2356.0667 | 353.5687 | 357.6738 | 345.7099
2357.0667 | 354.0016 | 357.7848 | 346.0105
2358.0667 | 354.3409 | 357.9177 | 346.0047
2359.0667 | 354.8434 | 358.3986 | 346.5997
2360.0667 | 355.5928 | 359.3888 | 346.9408
2361.0667 | 356.1111 | 359.4934 | 347.2848
2362.0667 | 356.2623 | 359.5349 | 347.648
2363.0667 | 356.9586 | 359.8417 | 348.0954
2364.0667 | 357.1536 | 359.7066 | 348.1105
2365.0667 | 358.539 | 359.5531 | 347.9729
2366.0667 | 359.2685 | 359.148 | 348.1428
2367.0667 | 359.102 | 359.2351 | 347.8725
2368.0667 | 358.6136 | 358.9864 | 347.4948
2369.0667 | 358.3988 | 358.5714 | 346.9646
2370.0667 | 357.997 | 358.1079 | 346.6218
2371.0667 | 357.7979 | 357.8204 | 346.0038
2372.0667 | 357.3508 | 357.4027 | 345.5972
2373.0667 | 356.8827 | 357.1539 | 345.3161
2374.0823 | 356.4089 | 356.9494 | 345.4673
2375.0667 | 355.8515 | 357.4766 | 345.4345
2376.0667 | 355.4134 | 357.6417 | 346.0036
2377.0667 | 355.3175 | 357.688 | 346.252
2378.0667 | 355.8729 | 358.0541 | 346.7003
2379.0667 | 356.2983 | 357.8629 | 346.8522
2380.0667 | 356.2404 | 357.8571 | 346.5807
2381.0667 | 356.645 | 358.529 | 346.5933
2382.0667 | 356.4813 | 358.7411 | 346.8314
2383.0667 | 356.5667 | 359.1789 | 347.2702
2384.0667 | 357.4376 | 359.0949 | 347.3093
2385.0667 | 358.0961 | 359.4469 | 347.2974
2386.0667 | 359.0417 | 359.7504 | 347.0422
2387.0667 | 359.4863 | 360.3665 | 346.8397
2388.0667 | 359.6005 | 361.2926 | 347.1386
2389.0823 | 359.0375 | 361.6575 | 347.1968
2390.0667 | 358.5387 | 360.893 | 347.1389
2391.0667 | 357.8617 | 360.4873 | 347.4741
2392.0667 | 357.0891 | 360.1325 | 347.1762
2393.0667 | 356.655 | 359.8194 | 347.0191
2394.0667 | 356.3998 | 359.4944 | 347.0749
2395.0667 | 355.9701 | 359.2711 | 346.9948
2396.0667 | 355.5483 | 359.0939 | 346.603
2397.0667 | 355.4146 | 359.1277 | 346.3114
2398.0667 | 355.5722 | 359.4018 | 346.0861
2399.0667 | 355.2757 | 359.3951 | 346.2652
2400.0667 | 355.5729 | 359.5101 | 346.7316
2401.0667 | 355.2591 | 359.6633 | 347.3419
2402.0667 | 355.057 | 359.5554 | 347.3561
2403.0667 | 355.0421 | 359.3999 | 347.2539
2404.0667 | 355.061 | 359.1258 | 347.0288
2405.0667 | 354.963 | 359.0738 | 347.3713
2406.0667 | 354.6897 | 359.7947 | 347.7852
2407.0667 | 354.8518 | 360.4888 | 348.0968
2408.0667 | 354.6654 | 361.1088 | 348.1837
2409.0667 | 354.5304 | 362.1921 | 348.4428
2410.0667 | 354.4675 | 363.0391 | 348.3149
2411.0667 | 354.4163 | 362.7272 | 348.5308
2412.0667 | 354.3354 | 362.3722 | 348.3359
2413.0667 | 354.3256 | 361.9164 | 348.2222
2414.0667 | 353.9815 | 361.4635 | 347.9922
2415.0667 | 353.5783 | 360.9197 | 347.5851
2416.0667 | 354.2059 | 361.1901 | 347.5637
2417.0667 | 353.8033 | 360.9107 | 347.3473
2418.0667 | 353.6258 | 360.7766 | 347.2072
2419.0667 | 353.384 | 360.8557 | 347.2031
2420.0667 | 353.2699 | 361.0312 | 347.3071
2421.0667 | 353.0451 | 362.1641 | 348.7926
2422.0667 | 353.009 | 361.9645 | 349.2275
2423.0667 | 353.1788 | 362.1318 | 349.2445
2424.0667 | 353.1809 | 362.2752 | 349.5941
2425.0667 | 353.1405 | 362.1983 | 349.4424
2426.0667 | 352.8734 | 361.8775 | 349.699
2427.0667 | 353.3149 | 361.2379 | 349.733
2428.0667 | 353.4599 | 360.7704 | 349.8345
2429.0667 | 353.2246 | 360.4463 | 349.2444
2430.0667 | 353.336 | 360.3097 | 348.8601
2431.0667 | 353.4423 | 360.0818 | 348.6424
2432.0667 | 353.2936 | 359.856 | 348.3542
2433.0667 | 354.1734 | 360.0718 | 348.5196
2434.0667 | 354.0807 | 360.218 | 348.7584
2435.0667 | 353.9606 | 360.2678 | 348.8677
2436.0667 | 354.3966 | 359.9678 | 349.3113
2437.0667 | 354.3593 | 359.637 | 350.0364
2438.0667 | 354.2804 | 359.5938 | 349.7484
2439.0667 | 354.0398 | 359.5227 | 349.4786
2440.0667 | 353.9631 | 359.2324 | 349.4762
2441.0667 | 353.7855 | 359.0305 | 349.3068
2442.0667 | 354.243 | 358.8946 | 349.7018
2443.0667 | 354.6787 | 358.7663 | 349.8189
2444.0667 | 355.3828 | 359.3853 | 350.0641
2445.0667 | 355.7391 | 360.4219 | 350.4844
2446.0667 | 355.6932 | 360.2859 | 350.2891
2447.0667 | 355.6618 | 360.2572 | 349.8714
2448.0667 | 355.5752 | 360.1279 | 349.7391
2449.0667 | 355.2444 | 359.7392 | 349.4571
2450.0667 | 355.1685 | 359.6973 | 349.2099
2451.0667 | 355.4556 | 359.5889 | 349.1202
2452.0667 | 355.1347 | 359.7033 | 348.9333
2453.0667 | 355.0706 | 359.5333 | 348.8185
2454.0667 | 354.8916 | 359.4684 | 348.9042
2455.0667 | 354.9971 | 359.3974 | 348.6037
2456.0667 | 355.4101 | 359.1458 | 348.6401
2457.0667 | 355.5735 | 359.0312 | 348.5679
2458.0667 | 356.1642 | 359.153 | 348.6793
2459.0667 | 356.2367 | 359.565 | 348.5961
2460.0667 | 356.3361 | 359.7177 | 348.687
2461.0667 | 356.0959 | 359.2428 | 348.3627
2462.0667 | 355.9663 | 359.027 | 348.0888
2463.0667 | 355.7262 | 359.0789 | 348.3485
2464.0667 | 356.1236 | 359.115 | 348.3792
2465.0667 | 356.9314 | 359.1559 | 348.8136
2466.0667 | 356.6368 | 359.2344 | 348.6412
2467.0667 | 356.4402 | 359.0966 | 348.8605
2468.0667 | 356.1471 | 359.07 | 348.7329
2469.0667 | 356.1645 | 359.0872 | 348.4896
2470.0667 | 355.8514 | 358.8963 | 348.1045
2471.0667 | 356.1619 | 358.68 | 348.2369
2472.0667 | 356.2086 | 358.697 | 348.4757
2473.0667 | 356.5662 | 358.943 | 349.5084
2474.0667 | 357.1959 | 359.3891 | 350.0395
2475.0667 | 357.5124 | 359.3212 | 350.1007
2476.0667 | 357.714 | 359.4277 | 350.8381
2477.0667 | 357.8063 | 359.3512 | 350.5372
2478.0667 | 357.7663 | 359.2418 | 350.3939
2479.0667 | 358.006 | 359.0871 | 350.4896
2480.0667 | 358.3844 | 359.1886 | 350.5945
2481.0667 | 358.2053 | 359.2777 | 350.3702
2482.0667 | 357.9354 | 359.651 | 349.884
2483.0667 | 357.4997 | 359.5085 | 349.6615
2484.0667 | 357.2198 | 359.3099 | 350.1422
2485.0667 | 356.9397 | 359.1044 | 350.1447
2486.0667 | 356.9769 | 359.4537 | 349.8817
2487.0667 | 357.0481 | 359.4298 | 350.7189
2488.0667 | 356.9619 | 360.019 | 350.7181
2489.0667 | 356.9986 | 360.392 | 351.3773
2490.0667 | 356.6248 | 360.5356 | 352.1992
2491.0667 | 356.249 | 360.5862 | 352.5159
2492.0667 | 356.5857 | 361.3368 | 352.4057
2493.0667 | 356.7923 | 361.3231 | 352.8394
2494.0667 | 356.7846 | 361.446 | 352.91
2495.0667 | 356.4263 | 361.4374 | 352.5074
2496.0667 | 356.5413 | 361.1999 | 352.2355
2497.0667 | 356.3536 | 361.0581 | 352.0794
2498.0667 | 356.7307 | 360.7119 | 352.1809
2499.0667 | 356.6097 | 360.1556 | 352.0056
2500.0667 | 356.3264 | 359.7323 | 352.091
2501.0667 | 356.2307 | 360.2613 | 351.8768
2502.0667 | 356.219 | 360.6986 | 351.8986
2503.0667 | 356.4177 | 360.696 | 351.4506
2504.0667 | 355.8584 | 360.5649 | 351.1281
2505.0667 | 355.4466 | 360.7495 | 351.0032
2506.0667 | 355.0492 | 360.4749 | 350.8394
2507.0667 | 355.0124 | 360.7116 | 350.8406
2508.0667 | 354.5334 | 360.6859 | 350.9445
2509.0823 | 354.338 | 360.6677 | 350.6958
2510.0667 | 354.7921 | 360.5803 | 350.5142
2511.0667 | 355.32 | 360.4822 | 350.8102
2512.0667 | 355.1138 | 360.2141 | 351.1422
2513.0667 | 354.8228 | 360.2131 | 351.3803
2514.0667 | 354.7304 | 359.9768 | 351.3994
2515.0667 | 354.8335 | 359.8343 | 351.6143
2516.0667 | 354.6643 | 359.4264 | 351.3744
2517.0667 | 354.5853 | 360.4956 | 351.1173
2518.0667 | 354.4591 | 360.4097 | 350.5293
2519.0667 | 354.5885 | 360.7046 | 350.9682
2520.0667 | 354.5276 | 360.7978 | 351.4789
2521.0667 | 354.7575 | 360.4976 | 351.5601
2522.0667 | 354.9876 | 360.5164 | 351.3481
2523.0667 | 356.1028 | 360.4367 | 351.1915
2524.0667 | 356.4906 | 360.2234 | 351.3247
2525.0667 | 356.4731 | 360.7401 | 351.5349
2526.0667 | 356.328 | 360.4395 | 351.5057
2527.0667 | 355.9786 | 360.3892 | 351.4372
2528.0667 | 356.4972 | 360.4298 | 351.3801
2529.0667 | 356.5241 | 360.7057 | 351.3493
2530.0667 | 356.6415 | 360.8252 | 350.9809
2531.0667 | 356.6557 | 360.6361 | 350.9681
2532.0667 | 357.0038 | 360.7419 | 350.8571
2533.0667 | 356.8934 | 361.0199 | 350.4568
2534.0667 | 356.6906 | 360.9634 | 351.0394
2535.0667 | 356.6908 | 360.7986 | 351.3399
2536.0667 | 356.4733 | 360.3584 | 350.9336
2537.0667 | 356.5782 | 360.2771 | 350.5275
2538.0667 | 356.4614 | 360.4051 | 350.3648
2539.0667 | 356.4901 | 360.5265 | 350.9434
2540.0667 | 356.9484 | 360.8092 | 351.3178
2541.0667 | 356.9869 | 361.6113 | 351.5175
2542.0667 | 356.7639 | 361.6946 | 351.4468
2543.0667 | 356.5631 | 361.1236 | 351.2166
2544.0667 | 356.998 | 360.8495 | 351.4783
2545.0667 | 356.9185 | 361.7524 | 351.6068
2546.0667 | 356.5643 | 361.4281 | 351.6638
2547.0667 | 356.2081 | 361.7238 | 351.1957
2548.0667 | 356.0892 | 361.7084 | 350.8933
2549.0667 | 356.0945 | 361.5533 | 350.6154
2550.0667 | 356.0832 | 361.2424 | 350.8473
2551.0667 | 356.2851 | 361.1173 | 350.4371
2552.0667 | 356.1846 | 361.7158 | 351.3001
2553.0667 | 356.0853 | 362.2902 | 351.3355
2554.0667 | 356.2332 | 362.4281 | 351.8862
2555.0667 | 355.9136 | 362.4814 | 351.8369
2556.0667 | 356.4157 | 362.5362 | 352.5868
2557.0667 | 356.7881 | 362.1008 | 352.5743
2558.0667 | 356.6636 | 361.9265 | 352.3075
2559.0667 | 356.2735 | 361.8378 | 352.0848
2560.0667 | 356.0035 | 361.8377 | 352.1548
2561.0667 | 355.7998 | 361.4533 | 351.8976
2562.0667 | 355.7323 | 361.1528 | 352.0624
2563.0667 | 355.7041 | 360.9977 | 352.1278
2564.0667 | 355.8093 | 361.1887 | 352.6472
2565.0667 | 355.6835 | 361.2529 | 353.1049
2566.0667 | 355.5906 | 360.9407 | 352.9131
2567.0667 | 356.1051 | 361.0118 | 353.1747
2568.0667 | 356.2441 | 361.3881 | 353.6413
2569.0667 | 356.007 | 361.9609 | 353.3555
2570.0667 | 355.9626 | 361.8173 | 353.0858
2571.0667 | 355.9984 | 361.4536 | 353.1853
2572.0667 | 356.2171 | 362.1288 | 353.2146
2573.0667 | 356.3639 | 362.4694 | 353.4765
2574.0667 | 356.3976 | 362.3239 | 353.2663
2575.0667 | 356.0814 | 362.0604 | 353.1034
2576.0667 | 355.8708 | 361.7579 | 352.7201
2577.0667 | 355.5189 | 361.5045 | 352.469
2578.0667 | 355.5462 | 361.8287 | 351.9882
2579.0667 | 355.1425 | 361.7528 | 351.7712
2580.0667 | 354.9212 | 361.9159 | 352.3517
2581.0667 | 354.7062 | 361.4733 | 352.0635
2582.0667 | 354.4919 | 361.1907 | 351.8095
2583.0667 | 354.4756 | 360.8694 | 351.6114
2584.0667 | 354.4973 | 360.3796 | 351.293
2585.0667 | 354.6811 | 360.1929 | 350.9447
2586.0667 | 355.5978 | 360.0516 | 350.5213
2587.0667 | 355.7636 | 359.8258 | 350.4553
2588.0667 | 355.5479 | 359.7039 | 350.1239
2589.0667 | 355.8788 | 360.0896 | 349.9641
2590.0667 | 356.5781 | 360.5724 | 350.282
2591.0667 | 357.2033 | 360.8554 | 350.9742
2592.0667 | 357.8695 | 360.6993 | 350.8422
2593.0667 | 358.076 | 360.8647 | 350.9007
2594.0823 | 357.954 | 360.5599 | 351.0452
2595.0667 | 358.1629 | 360.9021 | 351.3379
2596.0667 | 358.4503 | 361.1341 | 351.9219
2597.0667 | 358.9024 | 361.478 | 352.2959
2598.0667 | 358.9558 | 361.3455 | 352.0732
2599.0667 | 358.556 | 361.0861 | 351.5724
2600.0667 | 358.3111 | 360.9671 | 351.3653
2601.0667 | 357.9752 | 360.9737 | 351.0434
2602.0667 | 357.5868 | 360.5336 | 350.8767
2603.0667 | 357.0652 | 359.8328 | 350.4412
2604.0667 | 356.9086 | 359.9564 | 350.1288
2605.0667 | 357.3908 | 360.3127 | 349.8737
2606.0667 | 357.2742 | 360.3395 | 349.7376
2607.0667 | 357.1905 | 360.4488 | 350.4978
2608.0667 | 357.0322 | 360.4311 | 350.8707
2609.0823 | 357.2049 | 360.4523 | 351.6896
2610.0667 | 357.8741 | 360.6716 | 352.0228
2611.0667 | 358.0269 | 361.1292 | 352.4012
2612.0667 | 358.5678 | 361.473 | 352.2924
2613.0667 | 358.7896 | 361.3838 | 352.769
2614.0667 | 359.0327 | 361.7498 | 352.9246
2615.0667 | 359.315 | 361.9817 | 353.3725
2616.0667 | 359.6811 | 361.4132 | 353.2698
2617.0667 | 359.7918 | 361.3128 | 353.0351
2618.0667 | 359.3049 | 360.9306 | 352.7328
2619.0667 | 358.947 | 360.966 | 352.608
2620.0667 | 358.3948 | 360.6001 | 352.3514
2621.0667 | 358.7955 | 360.486 | 351.9548
2622.0667 | 358.4393 | 360.1358 | 352.5307
2623.0667 | 357.871 | 360.2253 | 352.1721
2624.0667 | 357.4285 | 360.4899 | 352.3775
2625.0667 | 357.7671 | 360.7973 | 352.0461
2626.0667 | 357.4115 | 360.7758 | 351.8046
2627.0667 | 356.752 | 360.4348 | 351.7351
2628.0667 | 356.4646 | 360.646 | 351.2304
2629.0667 | 356.2001 | 360.4976 | 351.5047
2630.0667 | 355.9053 | 360.0638 | 351.3865
2631.0667 | 356.2399 | 359.765 | 351.5196
2632.0667 | 356.3694 | 359.7306 | 351.3054
2633.0667 | 356.533 | 359.3391 | 350.9189
2634.0667 | 356.1389 | 359.1051 | 350.9105
2635.0667 | 355.8396 | 359.0171 | 350.8053
2636.0667 | 356.046 | 359.2172 | 351.1588
2637.0667 | 356.159 | 359.1447 | 351.4959
2638.0667 | 356.6569 | 359.4836 | 351.5969
2639.0667 | 357.1176 | 359.8797 | 351.534
2640.0667 | 357.6504 | 360.2236 | 351.5307
2641.0667 | 357.5583 | 360.1558 | 351.4061
2642.0667 | 357.3483 | 359.8657 | 351.6601
2643.0667 | 357.627 | 360.1041 | 352.1312
2644.0667 | 357.5155 | 360.8577 | 351.9019
2645.0667 | 357.8717 | 361.1114 | 351.6462
2646.0667 | 357.9393 | 360.8025 | 351.8637
2647.0667 | 357.5616 | 360.1974 | 352.4997
2648.0667 | 357.2285 | 360.1284 | 352.2929
2649.0667 | 356.8942 | 361.372 | 352.5481
2650.0667 | 356.5638 | 361.0705 | 353.3993
2651.0667 | 356.0099 | 360.7827 | 353.2909
2652.0667 | 355.7566 | 360.1831 | 353.1363
2653.0667 | 355.7766 | 359.9395 | 353.6232
2654.0667 | 355.5819 | 359.8488 | 353.0442
2655.0667 | 355.9699 | 359.7997 | 352.8379
2656.0667 | 355.9526 | 359.6819 | 353.1465
2657.0667 | 355.8465 | 359.7628 | 353.4922
2658.0667 | 355.6862 | 359.7996 | 353.3099
2659.0667 | 356.0204 | 360.3887 | 353.5292
2660.0667 | 355.7061 | 360.8426 | 353.1529
2661.0667 | 355.3924 | 360.9833 | 353.3142
2662.0667 | 355.6904 | 360.6822 | 353.4449
2663.0667 | 355.9843 | 360.5076 | 353.5536
2664.0667 | 356.2137 | 360.4887 | 353.4006
2665.0667 | 356.4018 | 360.2893 | 353.3299
2666.0667 | 356.3098 | 360.4568 | 353.4187
2667.0667 | 356.1385 | 361.1631 | 353.3788
2668.0667 | 355.972 | 361.8337 | 353.1862
2669.0667 | 356.6737 | 362.2425 | 353.162
2670.0667 | 357.1622 | 361.9662 | 353.3339
2671.0667 | 356.8605 | 361.5782 | 353.1084
2672.0667 | 356.5614 | 361.2836 | 353.2799
2673.0667 | 356.6979 | 361.0411 | 353.3455
2674.0667 | 356.3587 | 360.7935 | 353.1752
2675.0667 | 356.0694 | 360.6033 | 352.736
2676.0667 | 355.9423 | 360.5234 | 352.4718
2677.0667 | 355.7532 | 360.3528 | 352.337
2678.0667 | 355.5662 | 360.4407 | 352.1991
2679.0667 | 355.4837 | 360.2101 | 351.8284
2680.0667 | 355.3921 | 360.1368 | 351.5767
2681.0667 | 355.178 | 360.1929 | 351.3984
2682.0667 | 355.1306 | 359.6183 | 351.8265
2683.0667 | 354.9916 | 359.2815 | 351.7407
2684.0667 | 355.547 | 359.2983 | 352.0571
2685.0667 | 356.0526 | 359.1202 | 352.3177
2686.0667 | 355.5647 | 358.8376 | 352.314
2687.0667 | 355.0574 | 358.9604 | 352.6756
2688.0667 | 354.5532 | 359.0871 | 352.5667
2689.0667 | 354.3988 | 358.9867 | 352.1208
2690.0667 | 354.1165 | 359.0183 | 351.907
2691.0667 | 353.9156 | 360.3142 | 351.5724
2692.0667 | 353.7908 | 360.0305 | 351.3921
2693.0667 | 353.6107 | 360.2882 | 351.2328
2694.0667 | 353.7639 | 360.3288 | 351.7515
2695.0667 | 353.6 | 360.1085 | 351.8762
2696.0667 | 353.3898 | 360.1824 | 351.7551
2697.0667 | 353.4026 | 359.7925 | 351.2099
2698.0667 | 353.2815 | 359.6511 | 350.9307
2699.0667 | 353.248 | 359.0916 | 350.739
2700.0667 | 353.0037 | 358.9391 | 350.8808
2701.0667 | 353.0248 | 358.5042 | 350.7835
2702.0667 | 352.9841 | 358.4194 | 350.7457
2703.0667 | 352.7623 | 358.2258 | 350.43
2704.0823 | 352.6206 | 358.2855 | 350.3945
2705.0667 | 352.7071 | 358.3691 | 350.4483
2706.0667 | 353.2348 | 358.8742 | 351.0208
2707.0667 | 353.4434 | 359.808 | 351.7563
2708.0667 | 353.406 | 359.9636 | 352.2582
2709.0667 | 353.3709 | 359.8631 | 352.7054
2710.0667 | 353.3769 | 360.0454 | 352.797
2711.0667 | 353.7388 | 360.1076 | 352.8941
2712.0667 | 353.793 | 359.934 | 352.7863
2713.0667 | 353.7606 | 359.9215 | 352.4498
2714.0667 | 353.8081 | 360.0085 | 352.7256
2715.0667 | 353.9981 | 360.5655 | 352.9076
2716.0667 | 353.8681 | 361.0047 | 353.4327
2717.0667 | 353.9363 | 361.4436 | 353.2872
2718.0667 | 354.4237 | 361.2196 | 353.5703
2719.0667 | 354.3768 | 360.9208 | 353.439
2720.0667 | 354.6653 | 360.7906 | 353.3917
2721.0667 | 354.5588 | 360.6488 | 353.7437
2722.0667 | 354.2585 | 360.8358 | 354.1517
2723.0667 | 354.1367 | 360.6221 | 354.9432
2724.0667 | 353.8694 | 360.7734 | 354.8058
2725.0667 | 353.376 | 361.0399 | 354.7278
2726.0667 | 353.1855 | 360.9703 | 354.945
2727.0667 | 353.3386 | 360.2746 | 354.7022
2728.0667 | 353.4653 | 359.9908 | 354.3176
2729.0667 | 353.4277 | 359.5637 | 354.2095
2730.0667 | 353.3658 | 359.9704 | 354.0189
2731.0667 | 353.3801 | 359.6973 | 353.3558
2732.0667 | 353.5851 | 360.0122 | 352.8659
2733.0667 | 353.487 | 360.2613 | 352.6911
2734.0667 | 353.6083 | 360.4706 | 352.8246
2735.0667 | 353.5981 | 361.0166 | 352.6009
2736.0667 | 353.8994 | 361.3227 | 352.382
2737.0667 | 353.8062 | 361.3816 | 352.0627
2738.0667 | 353.8835 | 361.522 | 351.9938
2739.0667 | 354.1675 | 361.7482 | 352.1113
2740.0667 | 354.2191 | 361.7938 | 351.9812
2741.0667 | 354.2614 | 361.822 | 353.3513
2742.0667 | 354.3159 | 361.8223 | 353.3659
2743.0667 | 354.3493 | 361.5726 | 353.3923
2744.0667 | 354.0877 | 362.2557 | 352.8872
2745.0667 | 353.6324 | 362.2768 | 352.6316
2746.0667 | 353.7447 | 361.6857 | 352.2253
2747.0667 | 353.8003 | 361.2635 | 351.9625
2748.0667 | 353.6671 | 361.294 | 351.5515
2749.0667 | 353.6358 | 361.5747 | 351.3528
2750.0667 | 353.5095 | 361.5134 | 351.13
2751.0667 | 353.4811 | 361.5947 | 350.9205
2752.0667 | 353.4245 | 361.202 | 350.5827
2753.0667 | 353.4102 | 361.1409 | 350.4031
2754.0667 | 353.098 | 361.1603 | 350.2805
2755.0667 | 352.8651 | 360.6217 | 351.0183
2756.0667 | 352.9796 | 360.7558 | 351.0516
2757.0667 | 352.9572 | 360.6519 | 351.0162
2758.0667 | 353.2472 | 360.3999 | 350.7691
2759.0667 | 354.011 | 360.403 | 350.6206
2760.0667 | 355.4471 | 362.2747 | 350.7605
2761.0667 | 356.7089 | 363.2483 | 350.8917
2762.0667 | 357.3352 | 364.2128 | 351.4621
2763.0667 | 357.8769 | 364.4974 | 351.7702
2764.0667 | 357.8408 | 365.0794 | 351.747
2765.0667 | 357.5649 | 365.3605 | 352.0408
2766.0667 | 357.3781 | 366.2114 | 352.382
2767.0667 | 357.3204 | 366.1317 | 352.3371
2768.0667 | 357.5041 | 365.9509 | 352.6318
2769.0823 | 357.586 | 366.2641 | 352.6515
2770.0667 | 358.0891 | 366.1927 | 352.6776
2771.0667 | 358.0728 | 366.3198 | 353.0708
2772.0667 | 358.2491 | 366.2776 | 353.6007
2773.0667 | 358.2532 | 366.514 | 353.4025
2774.0667 | 358.8878 | 367.1028 | 353.7704
2775.0667 | 359.0012 | 367.4366 | 353.5555
2776.0667 | 359.0765 | 367.8051 | 353.5374
2777.0667 | 359.1212 | 367.9083 | 354.7346
2778.0823 | 359.1992 | 367.9153 | 355.3009
2779.0667 | 359.2776 | 367.9333 | 355.535
2780.0667 | 359.0074 | 367.8276 | 355.3413
2781.0823 | 358.6652 | 367.5855 | 355.3207
2782.0667 | 358.2124 | 367.4973 | 355.4402
2783.0667 | 357.843 | 366.8485 | 356.2868
2784.0667 | 357.9158 | 366.5037 | 356.5403
2785.0667 | 357.7284 | 366.3589 | 356.5071
2786.0667 | 357.374 | 366.0512 | 356.3132
2787.0667 | 357.4125 | 365.6804 | 356.1946
2788.0667 | 357.1122 | 365.4012 | 355.9463
2789.0667 | 356.7365 | 365.1081 | 355.4656
2790.0667 | 356.9923 | 365.2317 | 355.5803
2791.0667 | 356.6744 | 365.2913 | 355.3862
2792.0667 | 356.8391 | 365.9478 | 355.0711
2793.0667 | 357.6743 | 366.8295 | 355.3393
2794.0667 | 357.623 | 366.6033 | 355.4911
2795.0667 | 357.6268 | 366.4279 | 355.5204
2796.0667 | 357.3145 | 367.0675 | 355.1459
2797.0667 | 357.3728 | 368.3553 | 355.0063
2798.0667 | 357.463 | 367.947 | 354.6959
2799.0667 | 357.6722 | 367.7063 | 354.2021
2800.0667 | 357.5282 | 367.4369 | 353.8685
2801.0667 | 357.4878 | 367.5425 | 353.5141
2802.0667 | 357.3265 | 367.0445 | 353.2919
2803.0823 | 357.4445 | 366.708 | 353.4364
2804.0823 | 357.2665 | 366.3013 | 353.216
2805.0667 | 356.903 | 366.013 | 353.0862
2806.0667 | 356.4926 | 365.9931 | 352.6065
2807.0667 | 356.4421 | 365.8689 | 352.3024
2808.0667 | 356.0927 | 365.6241 | 351.8773
2809.0667 | 356.0303 | 365.3281 | 352.2328
2810.0667 | 355.7364 | 365.2955 | 352.2027
2811.0667 | 355.4511 | 364.9864 | 352.2691
2812.0667 | 355.2934 | 364.5664 | 352.0235
2813.0667 | 355.7056 | 364.3149 | 352.9457
2814.0823 | 355.8232 | 364.4113 | 353.193
2815.0667 | 355.8063 | 364.6532 | 352.9477
2816.0667 | 355.9965 | 365.0123 | 352.7625
2817.0667 | 356.3184 | 364.9929 | 353.0946
2818.0667 | 356.7372 | 364.793 | 353.1411
2819.0667 | 357.0388 | 365.0971 | 353.0023
2820.0667 | 357.2468 | 365.0462 | 353.1609
2821.0667 | 357.1921 | 364.916 | 353.4556
2822.0667 | 356.8706 | 364.8706 | 353.7974
2823.0667 | 356.5462 | 364.6531 | 353.6939
2824.0667 | 356.4429 | 364.2227 | 353.5284
2825.0667 | 356.4196 | 363.894 | 353.0754
2826.0667 | 356.3125 | 363.5143 | 352.7456
2827.0667 | 356.0308 | 363.3669 | 352.7127
2828.0667 | 355.7864 | 363.4765 | 352.3608
2829.0823 | 355.6483 | 363.5972 | 352.6555
2830.0667 | 355.5438 | 363.9635 | 353.1762
2831.0667 | 355.5636 | 363.6419 | 352.7239
2832.0667 | 355.7357 | 363.8867 | 352.5261
2833.0667 | 355.6348 | 364.355 | 353.107
2834.0667 | 355.5282 | 364.1052 | 353.1869
2835.0667 | 355.455 | 363.9077 | 353.1271
2836.0667 | 355.3726 | 363.7525 | 353.1418
2837.0667 | 355.0881 | 363.9679 | 352.9605
2838.0667 | 354.8543 | 363.689 | 353.0159
2839.0667 | 355.1585 | 364.0947 | 352.8612
2840.0667 | 354.9549 | 364.8219 | 352.6454
2841.0667 | 354.9507 | 365.5736 | 352.5378
2842.0667 | 355.0539 | 365.2854 | 353.1152
2843.0667 | 355.4739 | 365.4413 | 353.7292
2844.0667 | 356.4648 | 365.9456 | 353.9147
2845.0667 | 356.7166 | 366.1454 | 353.612
2846.0667 | 356.715 | 366.3312 | 353.1992
2847.0667 | 356.844 | 365.9859 | 353.1012
2848.0667 | 356.9392 | 365.5165 | 352.9545
2849.0667 | 358.6165 | 365.5084 | 353.4226
2850.0667 | 358.5359 | 365.6588 | 353.8994
2851.0667 | 358.9069 | 365.4136 | 354.3586
2852.0667 | 358.9508 | 365.1325 | 354.7757
2853.0667 | 358.8291 | 365.0702 | 355.2458
2854.0667 | 359.4281 | 365.2578 | 355.5334
2855.0667 | 359.6164 | 366.0335 | 356.0033
2856.0667 | 359.4355 | 366.1641 | 355.7891
2857.0667 | 359.411 | 366.5746 | 355.6883
2858.0667 | 359.3963 | 366.4382 | 355.7894
2859.0667 | 359.5052 | 366.9959 | 355.9285
2860.0667 | 359.4045 | 367.1445 | 355.8556
2861.0667 | 359.5945 | 367.5674 | 355.9311
2862.0667 | 359.5223 | 367.57 | 355.9513
2863.0667 | 359.537 | 367.9438 | 355.8845
2864.0667 | 359.6878 | 368.6368 | 355.7053
2865.0667 | 360.8669 | 368.8156 | 356.2228
2866.0667 | 360.6714 | 368.9234 | 356.1029
2867.0667 | 360.4827 | 368.9267 | 355.7794
2868.0667 | 360.4881 | 368.468 | 355.4562
2869.0667 | 360.5655 | 368.3993 | 355.3897
2870.0667 | 360.378 | 368.2003 | 355.3467
2871.0667 | 360.1075 | 368.1471 | 355.5266
2872.0667 | 360.0024 | 367.9577 | 355.8198
2873.0667 | 359.4878 | 367.8041 | 356.2045
2874.0667 | 359.4281 | 367.595 | 356.1468
2875.0667 | 359.3954 | 367.1273 | 355.781
2876.0667 | 359.1465 | 366.9607 | 356.1862
2877.0667 | 359.0945 | 367.2008 | 355.7708
2878.0667 | 358.9252 | 367.4384 | 356.1369
2879.0667 | 358.679 | 367.528 | 355.9565
2880.0667 | 359.0362 | 367.98 | 355.8751
2881.0667 | 359.1536 | 367.7287 | 355.6045
2882.0667 | 359.3935 | 367.379 | 355.6453
2883.0667 | 359.2549 | 367.2519 | 355.6627
2884.0667 | 358.9342 | 366.6633 | 355.4261
2885.0823 | 358.5068 | 366.6542 | 354.8552
2886.0667 | 357.9309 | 366.2627 | 354.3591
2887.0667 | 357.6815 | 365.9778 | 354.3128
2888.0667 | 357.6534 | 366.2268 | 354.4521
2889.0667 | 357.6212 | 366.0888 | 354.3575
2890.0667 | 357.5535 | 365.9336 | 354.0853
2891.0667 | 357.5083 | 366.2613 | 353.7447
2892.0667 | 357.6624 | 366.0448 | 353.6647
2893.0667 | 357.5087 | 365.7846 | 353.7148
2894.0667 | 357.5247 | 365.9107 | 353.5578
2895.0667 | 357.9799 | 367.0699 | 353.9593
2896.0667 | 357.7036 | 366.6172 | 353.663
2897.0667 | 357.5015 | 366.5346 | 353.9239
2898.0667 | 357.3078 | 366.7646 | 354.1764
2899.0667 | 357.0998 | 366.5812 | 354.7095
2900.0667 | 357.087 | 366.3957 | 354.3014
2901.0667 | 356.9577 | 365.9975 | 353.964
2902.0667 | 356.894 | 365.7545 | 354.4045
2903.0667 | 356.964 | 365.3272 | 353.9337
2904.0667 | 356.7928 | 364.9738 | 353.7074
2905.0667 | 356.8449 | 364.5706 | 353.459
2906.0667 | 356.5501 | 364.0939 | 353.0092
2907.0667 | 356.4276 | 363.9395 | 352.628
2908.0667 | 356.2546 | 363.6572 | 352.4324
2909.0823 | 355.9952 | 363.4688 | 352.4396
2910.0667 | 355.924 | 363.4531 | 352.0028
2911.0667 | 355.9043 | 363.8799 | 352.057
2912.0667 | 356.1235 | 364.1375 | 352.4237
2913.0667 | 356.1992 | 364.6658 | 352.8914
2914.0667 | 356.5567 | 364.2507 | 352.9296
2915.0667 | 356.7887 | 365.6927 | 352.9736
2916.0667 | 357.3183 | 365.6594 | 352.7809
2917.0667 | 357.4739 | 365.2222 | 352.9326
2918.0667 | 357.2674 | 364.851 | 353.0741
2919.0667 | 356.949 | 364.3562 | 352.7549
2920.0667 | 356.8011 | 364.166 | 352.5193
2921.0667 | 356.5028 | 363.5553 | 352.2791
2922.0667 | 356.0658 | 362.7316 | 352.0111
2923.0667 | 355.6098 | 362.0492 | 352.5801
2924.0667 | 355.3934 | 361.328 | 352.7206
2925.0667 | 355.8543 | 360.8715 | 352.3514
2926.0667 | 355.6557 | 361.1357 | 353.1359
2927.0667 | 355.5245 | 361.9865 | 352.815
2928.0667 | 355.43 | 361.4714 | 352.4143
2929.0667 | 355.3612 | 362.0746 | 352.5994
2930.0667 | 355.6821 | 362.2616 | 352.4729
2931.0667 | 355.5292 | 362.0963 | 352.3681
2932.0667 | 355.4082 | 362.2865 | 352.2921
2933.0667 | 355.4286 | 362.1758 | 352.8251
2934.0823 | 355.9159 | 362.4413 | 352.9948
2935.0667 | 356.1824 | 362.9331 | 353.3929
2936.0667 | 356.2365 | 362.8374 | 353.265
2937.0667 | 356.8388 | 362.4852 | 353.4226
2938.0667 | 356.9978 | 362.4139 | 353.4301
2939.0667 | 357.0726 | 362.5513 | 353.4048
2940.0667 | 356.8655 | 362.6278 | 353.0688
2941.0667 | 356.3599 | 363.19 | 352.8424
2942.0667 | 356.1467 | 363.4682 | 353.8984
2943.0667 | 356.1094 | 363.7818 | 353.9101
2944.0667 | 356.3628 | 363.9091 | 353.5177
2945.0823 | 356.484 | 364.2544 | 353.5727
2946.0667 | 356.2296 | 364.0106 | 353.296
2947.0667 | 356.2676 | 363.6212 | 352.8559
2948.0667 | 356.9498 | 363.3082 | 352.5605
2949.0667 | 356.7888 | 363.4444 | 352.4673
2950.0667 | 356.762 | 363.4495 | 351.8817
2951.0667 | 356.5663 | 363.1375 | 351.5967
2952.0667 | 356.3913 | 362.9945 | 351.3362
2953.0667 | 356.5421 | 362.8634 | 351.5891
2954.0667 | 356.4251 | 362.7009 | 352.0755
2955.0667 | 356.279 | 362.3446 | 351.9064
2956.0667 | 356.0501 | 361.9995 | 352.0725
2957.0667 | 355.8752 | 361.4524 | 352.1578
2958.0667 | 355.7924 | 361.632 | 351.9775
2959.0667 | 355.7821 | 361.8554 | 351.6208
2960.0667 | 355.8791 | 362.1388 | 351.4299
2961.0667 | 356.123 | 362.5209 | 351.6581
2962.0667 | 357.0485 | 363.1181 | 351.9394
2963.0667 | 357.4515 | 363.6428 | 352.4305
2964.0667 | 357.4771 | 363.8417 | 352.5042
2965.0667 | 357.8357 | 364.1127 | 352.2871
2966.0667 | 357.7873 | 364.2436 | 352.4747
2967.0667 | 357.6287 | 364.0211 | 352.4798
2968.0667 | 357.4998 | 363.8741 | 352.6323
2969.0667 | 357.5845 | 364.0636 | 352.4036
2970.0667 | 357.46 | 364.3033 | 352.1436
2971.0667 | 357.2716 | 364.5281 | 352.0426
2972.0667 | 357.1454 | 364.4391 | 351.8765
2973.0667 | 357.1663 | 364.3559 | 351.3822
2974.0667 | 356.996 | 364.0693 | 351.2058
2975.0667 | 357.0148 | 363.8226 | 351.2601
2976.0667 | 356.9408 | 363.6633 | 351.8276
2977.0667 | 356.6796 | 363.5455 | 351.7893
2978.0667 | 356.5482 | 363.658 | 352.2397
2979.0823 | 356.7982 | 363.7659 | 352.1751
2980.0667 | 356.9622 | 363.8504 | 352.8689
2981.0667 | 356.7417 | 364.4339 | 352.6041
2982.0667 | 356.6472 | 364.9557 | 353.0141
2983.0667 | 356.4286 | 365.2385 | 353.4323
2984.0667 | 356.3127 | 365.4388 | 353.1791
2985.0667 | 356.8075 | 365.4 | 353.5861
2986.0667 | 357.2479 | 366.0823 | 354.1113
2987.0667 | 357.1425 | 365.5844 | 354.0842
2988.0667 | 356.8696 | 365.2295 | 353.8847
2989.0667 | 357.8068 | 365.4227 | 353.5546
2990.0667 | 357.7424 | 365.1715 | 353.3152
2991.0667 | 358.5229 | 365.2079 | 353.2517
2992.0667 | 358.3854 | 365.2084 | 353.2105
2993.0667 | 358.5033 | 365.8729 | 353.0671
2994.0823 | 358.159 | 365.571 | 352.804
2995.0667 | 358.2877 | 365.2461 | 352.7483
2996.0823 | 358.8332 | 365.159 | 352.7775
2997.0667 | 358.7489 | 365.0936 | 353.0994
2998.0667 | 358.6736 | 364.8931 | 352.907
2999.0667 | 358.9303 | 364.9615 | 352.7147
3000.0667 | 358.79 | 364.87 | 354.0116
3001.0667 | 358.7202 | 365.0796 | 354.1033
3002.0667 | 358.9023 | 365.0975 | 354.1561
3003.0667 | 360.0011 | 365.8618 | 354.1499
3004.0667 | 360.4009 | 366.2414 | 354.0755
3005.0823 | 360.9113 | 366.7989 | 354.1357
3006.0667 | 361.4517 | 366.9133 | 354.0399
3007.0667 | 362.301 | 367.7906 | 354.3735
3008.0667 | 362.4583 | 367.2751 | 354.3812
3009.0667 | 362.035 | 366.9519 | 354.2616
3010.0667 | 361.6592 | 366.6811 | 353.7673
3011.0667 | 361.3586 | 365.8969 | 353.7559
3012.0667 | 361.0468 | 365.1847 | 353.4264
3013.0667 | 360.336 | 365.0706 | 352.8876
3014.0667 | 359.6302 | 364.707 | 353.5316
3015.0667 | 359.0544 | 364.7135 | 353.604
3016.0667 | 358.6404 | 364.5704 | 353.4266
3017.0667 | 358.1888 | 364.3253 | 353.0701
3018.0667 | 357.9668 | 364.0767 | 352.9077
3019.0667 | 357.7352 | 363.8563 | 352.7703
3020.0667 | 357.5586 | 363.773 | 352.4668
3021.0667 | 357.5771 | 363.5662 | 352.2649
3022.0667 | 357.3388 | 363.1385 | 352.0532
3023.0667 | 357.2406 | 363.051 | 351.976
3024.0667 | 357.2479 | 363.1847 | 351.8104
3025.0667 | 357.032 | 363.0432 | 351.6784
3026.0823 | 357.3459 | 363.0249 | 351.9251
3027.0667 | 357.587 | 363.5718 | 352.3074
3028.0667 | 357.6329 | 363.4577 | 352.1398
3029.0667 | 358.4305 | 363.4071 | 352.2148
3030.0667 | 358.3868 | 363.2126 | 352.0039
3031.0667 | 358.3178 | 363.0137 | 351.8369
3032.0667 | 358.1064 | 362.7601 | 351.6558
3033.0667 | 357.9561 | 362.4927 | 352.1261
3034.0667 | 357.9924 | 362.2984 | 352.6026
3035.0667 | 357.7576 | 362.2207 | 352.8476
3036.0667 | 357.4564 | 362.3122 | 352.4885
3037.0667 | 357.4443 | 362.0607 | 352.1657
3038.0667 | 357.235 | 362.0274 | 352.0745
3039.0667 | 357.3803 | 362.1419 | 352.0886
3040.0667 | 357.3717 | 363.1727 | 351.9338
3041.0667 | 357.2434 | 363.0125 | 351.69
3042.0667 | 356.9443 | 363.0608 | 351.3998
3043.0667 | 356.6451 | 362.6758 | 351.1183
3044.0667 | 356.9618 | 362.9298 | 351.0195
3045.0667 | 356.57 | 362.9306 | 350.9217
3046.0667 | 356.4076 | 362.4207 | 350.5001
3047.0667 | 356.5279 | 362.2441 | 350.4167
3048.0667 | 356.4399 | 362.0084 | 350.6897
3049.0667 | 356.3639 | 361.8134 | 350.5009
3050.0667 | 356.2222 | 361.4599 | 350.1054
3051.0667 | 356.039 | 361.3718 | 350.4951
3052.0667 | 355.7587 | 361.2772 | 351.2966
3053.0667 | 355.7764 | 361.1551 | 351.2696
3054.0667 | 355.6053 | 361.2298 | 351.191
3055.0667 | 355.404 | 360.9928 | 351.2002
3056.0667 | 355.5524 | 360.9036 | 351.0634
3057.0667 | 355.4161 | 360.9922 | 350.8571
3058.0667 | 355.2897 | 361.1533 | 352.0157
3059.0667 | 355.473 | 361.1949 | 352.1998
3060.0667 | 355.5992 | 361.1905 | 352.0065
3061.0667 | 355.6321 | 361.1512 | 352.1793
3062.0667 | 355.6424 | 360.9455 | 352.4077
3063.0667 | 355.5452 | 360.809 | 352.2468
3064.0667 | 355.3505 | 360.7836 | 351.9534
3065.0823 | 355.1674 | 360.7808 | 351.8428
3066.0667 | 355.962 | 360.4813 | 351.5277
3067.0667 | 355.901 | 360.5598 | 351.0158
3068.0667 | 355.8198 | 360.4479 | 350.5992
3069.0667 | 355.6364 | 360.5829 | 350.7279
3070.0667 | 355.6247 | 360.3411 | 350.8949
3071.0667 | 355.5423 | 360.5471 | 350.8241
3072.0667 | 355.4469 | 360.8069 | 351.297
3073.0667 | 355.336 | 361.0392 | 351.0891
3074.0823 | 355.2473 | 361.527 | 350.853
3075.0667 | 355.1725 | 361.5606 | 351.7113
3076.0667 | 355.4002 | 361.7035 | 351.7684
3077.0667 | 355.1996 | 361.3224 | 351.4338
3078.0667 | 355.231 | 362.0271 | 351.0816
3079.0667 | 355.0763 | 362.4555 | 351.2457
3080.0667 | 354.962 | 362.1223 | 350.9494
3081.0667 | 355.0361 | 361.8347 | 351.0159
3082.0667 | 355.027 | 361.7288 | 351.3789
3083.0667 | 354.7495 | 361.0149 | 351.2045
3084.0667 | 354.8177 | 360.6637 | 350.8731
3085.0667 | 354.6983 | 360.5276 | 350.5869
3086.0667 | 354.824 | 360.426 | 350.3361
3087.0667 | 354.863 | 360.6178 | 350.9899
3088.0667 | 354.723 | 360.8858 | 350.8422
3089.0667 | 354.5038 | 360.8593 | 350.5573
3090.0667 | 354.6844 | 360.9333 | 350.4529
3091.0667 | 354.8779 | 360.9083 | 350.3193
3092.0667 | 355.1996 | 360.9445 | 350.0435
3093.0667 | 355.1204 | 360.6618 | 350.0406
3094.0667 | 355.217 | 360.8742 | 349.5687
3095.0667 | 355.2903 | 360.66 | 349.4806
3096.0667 | 355.1424 | 360.2885 | 349.5229
3097.0667 | 354.8915 | 360.051 | 349.8818
3098.0667 | 354.6114 | 360.2069 | 349.4756
3099.0823 | 354.3516 | 360.0113 | 349.6339
3100.0667 | 354.2194 | 359.5611 | 350.1161
3101.0667 | 354.4882 | 359.6019 | 350.1827
3102.0823 | 354.9999 | 360.1113 | 350.3473
3103.0667 | 354.8111 | 360.4228 | 350.1991
3104.0667 | 354.8564 | 360.5374 | 350.4512
3105.0667 | 355.1038 | 361.2673 | 350.4707
3106.0667 | 355.6072 | 361.3799 | 350.4086
3107.0667 | 355.4235 | 361.5987 | 350.314
3108.0667 | 355.4005 | 361.6249 | 350.2989
3109.0667 | 355.4899 | 362.1307 | 351.6292
3110.0667 | 355.4045 | 361.9241 | 351.9615
3111.0667 | 355.2998 | 361.6119 | 351.8924
3112.0667 | 355.3886 | 361.4007 | 351.735
3113.0667 | 355.3871 | 360.9333 | 351.4683
3114.0823 | 356.2043 | 360.47 | 351.1575
3115.0667 | 355.9345 | 360.116 | 351.3872
3116.0823 | 355.9215 | 360.0666 | 351.8352
3117.0667 | 355.7982 | 360.1806 | 351.5899
3118.0667 | 355.6285 | 360.7175 | 351.586
3119.0667 | 355.5715 | 360.5329 | 351.1832
3120.0667 | 355.7268 | 360.2431 | 350.9457
3121.0667 | 356.1312 | 360.3684 | 350.9332
3122.0667 | 356.0316 | 360.1827 | 351.0101
3123.0667 | 355.7417 | 360.0671 | 350.8048
3124.0667 | 355.5394 | 360.2147 | 350.8551
3125.0667 | 355.1578 | 360.562 | 350.775
3126.0667 | 354.9432 | 360.4637 | 350.519
3127.0667 | 354.7181 | 360.581 | 350.4227
3128.0667 | 354.518 | 360.5265 | 350.4373
3129.0667 | 354.637 | 360.2814 | 350.2149
3130.0667 | 354.2876 | 361.1545 | 349.9785
3131.0667 | 354.4336 | 361.2668 | 351.1714
3132.0667 | 354.6043 | 361.0635 | 351.2227
3133.0667 | 354.5033 | 361.437 | 350.9966
3134.0667 | 354.3066 | 361.5323 | 351.016
3135.0667 | 354.1474 | 361.1559 | 351.1823
3136.0667 | 354.091 | 361.663 | 351.3139
3137.0667 | 353.945 | 361.8025 | 351.3956
3138.0667 | 353.9787 | 362.2757 | 351.3354
3139.0667 | 354.2977 | 362.6622 | 351.6243
3140.0667 | 354.4102 | 362.8518 | 351.5452
3141.0667 | 354.5569 | 363.0925 | 351.4689
3142.0667 | 355.2695 | 363.4412 | 352.0718
3143.0667 | 355.6414 | 363.2245 | 352.0163
3144.0667 | 355.8142 | 362.9603 | 352.1723
3145.0667 | 355.5361 | 362.6767 | 351.8911
3146.0667 | 355.2039 | 362.7601 | 351.8745
3147.0667 | 355.6091 | 362.2284 | 351.6813
3148.0667 | 355.5003 | 361.876 | 351.8395
3149.0667 | 355.4173 | 361.5246 | 352.0259
3150.0667 | 355.4919 | 361.5535 | 351.6412
3151.0667 | 355.4796 | 361.7011 | 352.1866
3152.0667 | 355.1996 | 361.6161 | 352.1488
3153.0667 | 354.9379 | 361.5256 | 352.6647
3154.0667 | 354.7922 | 361.3 | 353.3062
3155.0667 | 354.5414 | 361.2524 | 352.6669
3156.0667 | 354.2729 | 360.8527 | 352.4428
3157.0667 | 354.4614 | 360.4502 | 352.0492
3158.0667 | 354.5475 | 361.4517 | 351.6642
3159.0823 | 354.4295 | 360.9039 | 351.3805
3160.0667 | 354.1753 | 360.6625 | 351.0357
3161.0667 | 354.0012 | 360.113 | 350.6552
3162.0667 | 353.781 | 359.8512 | 350.4592
3163.0667 | 353.6922 | 359.6421 | 350.402
3164.0667 | 353.59 | 359.2248 | 350.6982
3165.0667 | 353.3523 | 359.0446 | 350.5884
3166.0667 | 353.0955 | 359.1147 | 350.275
3167.0667 | 353.0325 | 359.244 | 350.0133
3168.0667 | 353.0078 | 359.7716 | 349.7783
3169.0667 | 353.3442 | 359.5018 | 350.4693
3170.0667 | 354.0035 | 359.3011 | 350.6739
3171.0667 | 354.2006 | 359.1039 | 350.5313
3172.0667 | 354.3485 | 358.9503 | 350.4427
3173.0667 | 354.4448 | 358.7779 | 350.466
3174.0667 | 354.2092 | 358.5643 | 350.3309
3175.0667 | 354.27 | 358.4285 | 350.1192
3176.0823 | 354.6655 | 358.4027 | 350.4857
3177.0667 | 354.9914 | 358.3832 | 350.5633
3178.0667 | 355.0762 | 358.9451 | 350.3813
3179.0667 | 356.0047 | 359.3416 | 350.5267
3180.0667 | 356.1177 | 359.3199 | 350.3751
3181.0667 | 356.2904 | 359.1811 | 351.1015
3182.0667 | 356.1899 | 358.9256 | 350.7622
3183.0667 | 356.8031 | 358.5201 | 350.4516
3184.0667 | 356.6535 | 358.0376 | 350.2613
3185.0823 | 356.715 | 359.152 | 350.0491
3186.0667 | 356.9743 | 359.1928 | 349.6965
3187.0667 | 356.7034 | 359.5313 | 349.6252
3188.0667 | 356.5605 | 359.6749 | 349.4752
3189.0667 | 356.4808 | 359.5595 | 349.2579
3190.0667 | 356.0454 | 360.0467 | 349.0236
3191.0667 | 355.6146 | 360.6005 | 349.1936
3192.0667 | 355.6226 | 360.6859 | 348.9769
3193.0667 | 355.3707 | 360.5413 | 349.4677
3194.0667 | 355.1759 | 360.603 | 349.2076
3195.0667 | 355.2881 | 360.6153 | 349.1714
3196.0667 | 355.3042 | 360.675 | 349.2888
3197.0667 | 355.457 | 360.6653 | 349.4676
3198.0667 | 355.4886 | 360.687 | 349.4043
3199.0667 | 355.5552 | 360.4861 | 349.6894
3200.0667 | 355.6134 | 360.6127 | 349.6796
3201.0667 | 356.3132 | 360.7404 | 349.4442
3202.0667 | 356.0932 | 361.0654 | 349.2869
3203.0667 | 356.5031 | 361.4436 | 349.3248
3204.0667 | 356.2962 | 362.1222 | 349.2281
3205.0667 | 356.2748 | 362.1601 | 349.1306
3206.0667 | 356.1894 | 362.0078 | 348.8879
3207.0667 | 356.4134 | 361.7034 | 349.003
3208.0667 | 356.281 | 361.8376 | 348.9949
3209.0667 | 355.9498 | 361.4851 | 348.7851
3210.0667 | 356.1086 | 361.3315 | 348.9109
3211.0667 | 355.9612 | 361.2437 | 349.0247
3212.0667 | 356.0475 | 361.1159 | 349.4787
3213.0667 | 356.2338 | 360.8847 | 349.5748
3214.0667 | 356.1633 | 361.108 | 349.5896
3215.0667 | 356.2214 | 361.7499 | 349.4144
3216.0667 | 356.2592 | 361.5521 | 349.5945
3217.0667 | 356.1616 | 361.3632 | 349.7726
3218.0667 | 355.9693 | 361.6559 | 349.524
3219.0667 | 355.898 | 362.1394 | 349.4674
3220.0667 | 355.8023 | 362.2307 | 349.4816
3221.0667 | 356.1206 | 362.1254 | 349.4457
3222.0667 | 356.1231 | 362.1928 | 349.3041
3223.0667 | 356.2536 | 362.4018 | 349.287
3224.0667 | 356.2302 | 362.5792 | 348.932
3225.0667 | 356.0617 | 362.5951 | 348.8761
3226.0667 | 355.8875 | 363.6154 | 349.7597
3227.0667 | 355.8459 | 364.7437 | 349.9297
3228.0667 | 355.6685 | 366.2025 | 350.1361
3229.0667 | 355.7412 | 365.7473 | 350.0576
3230.0667 | 355.4434 | 365.0176 | 350.174
3231.0667 | 355.2327 | 364.3008 | 350.3388
3232.0667 | 355.0108 | 363.8019 | 350.1382
3233.0667 | 354.9716 | 363.6699 | 349.9494
3234.0667 | 354.9861 | 363.4999 | 350.0472
3235.0667 | 354.7794 | 363.3736 | 350.3179
3236.0667 | 354.8107 | 363.1384 | 350.4168
3237.0667 | 354.8165 | 362.9176 | 350.4169
3238.0667 | 354.9738 | 362.6575 | 350.3922
3239.0667 | 355.2932 | 362.6055 | 350.7313
3240.0667 | 355.7017 | 362.8241 | 351.1646
3241.0667 | 355.854 | 362.6795 | 351.0382
3242.0667 | 356.403 | 362.8204 | 350.9597
3243.0667 | 356.9177 | 363.3032 | 351.4829
3244.0667 | 357.1506 | 363.7289 | 351.5866
3245.0667 | 357.3142 | 363.4219 | 351.9848
3246.0667 | 357.4693 | 363.2519 | 351.8488
3247.0667 | 357.5822 | 363.277 | 352.4084
3248.0667 | 357.5112 | 363.6235 | 352.8945
3249.0667 | 357.6678 | 363.5003 | 353.8014
3250.0667 | 357.5101 | 363.8947 | 354.1072
3251.0667 | 357.4048 | 363.7773 | 353.9538
3252.0667 | 357.5214 | 363.6358 | 354.0484
3253.0667 | 357.3842 | 363.9906 | 353.9586
3254.0667 | 357.7717 | 363.8619 | 353.5715
3255.0667 | 357.7116 | 363.3737 | 353.1377
3256.0667 | 358.1314 | 363.1399 | 353.206
3257.0667 | 358.5299 | 362.7716 | 353.1375
3258.0667 | 358.5473 | 362.8771 | 353.2348
3259.0667 | 358.613 | 363.3389 | 353.1888
3260.0667 | 358.4319 | 363.4615 | 353.3597
3261.0667 | 359.1607 | 363.6538 | 352.9035
3262.0667 | 358.838 | 363.727 | 352.536
3263.0667 | 358.8706 | 363.8198 | 353.0253
3264.0667 | 358.5897 | 364.0497 | 353.2274
3265.0667 | 358.6717 | 364.4227 | 353.0994
3266.0823 | 359.1321 | 364.2502 | 352.6327
3267.0667 | 358.9851 | 364.254 | 352.4484
3268.0667 | 358.9138 | 364.4852 | 352.199
3269.0667 | 359.1157 | 364.404 | 352.0543
3270.0667 | 359.1051 | 364.1851 | 351.7969
3271.0667 | 358.8036 | 364.0995 | 351.6924
3272.0667 | 358.5434 | 363.9226 | 351.4192
3273.0667 | 358.2846 | 363.8617 | 351.2698
3274.0667 | 358.2747 | 363.8064 | 350.923
3275.0667 | 358.4985 | 364.2571 | 351.5899
3276.0667 | 358.4405 | 364.068 | 351.5311
3277.0667 | 358.4623 | 363.8479 | 351.832
3278.0667 | 358.7933 | 364.0871 | 352.2552
3279.0667 | 358.5984 | 363.6308 | 352.3055
3280.0667 | 358.4029 | 363.107 | 352.3508
3281.0667 | 358.0595 | 363.2436 | 352.1642
3282.0667 | 357.888 | 362.8867 | 351.8045
3283.0667 | 357.6903 | 362.8453 | 351.6307
3284.0667 | 357.3641 | 363.0325 | 351.4663
3285.0667 | 357.1345 | 362.8133 | 351.7532
3286.0667 | 356.7672 | 363.203 | 352.073
3287.0667 | 356.3954 | 362.8121 | 351.8364
3288.0667 | 356.2361 | 362.4316 | 351.8343
3289.0667 | 356.2752 | 362.3223 | 351.6886
3290.0667 | 356.3917 | 362.739 | 351.4401
3291.0667 | 356.8429 | 363.0465 | 351.3151
3292.0667 | 356.8892 | 363.1239 | 351.6201
3293.0667 | 357.1195 | 362.803 | 352.0943
3294.0823 | 357.199 | 362.6175 | 351.9888
3295.0667 | 357.6873 | 362.5401 | 351.6194
3296.0667 | 357.5984 | 363.5207 | 351.5735
3297.0667 | 358.0347 | 363.5207 | 351.7434
3298.0667 | 357.7465 | 363.1613 | 352.0054
3299.0667 | 357.6744 | 362.8959 | 351.5985
3300.0667 | 357.7287 | 362.96 | 351.3584
3301.0667 | 358.5461 | 363.2292 | 351.5166
3302.0667 | 358.6533 | 363.3563 | 352.2694
3303.0667 | 358.7486 | 363.1878 | 352.0497
3304.0667 | 358.6635 | 363.4051 | 352.0592
3305.0823 | 358.9937 | 363.4783 | 351.9821
3306.0667 | 359.1135 | 363.5678 | 352.0261
3307.0667 | 359.0897 | 363.3169 | 351.799
3308.0667 | 359.4114 | 363.1707 | 351.7328
3309.0667 | 359.3836 | 362.839 | 351.789
3310.0667 | 359.3087 | 362.9141 | 351.7319
3311.0667 | 358.984 | 362.5624 | 352.255
3312.0667 | 358.509 | 362.1538 | 351.9092
3313.0667 | 358.1642 | 362.0512 | 351.5827
3314.0667 | 358.1977 | 362.5368 | 351.976
3315.0667 | 358.5069 | 362.5227 | 351.9406
3316.0667 | 358.2013 | 362.5362 | 352.4355
3317.0667 | 358.3238 | 362.8635 | 352.5653
3318.0667 | 358.1542 | 362.9439 | 352.1709
3319.0823 | 358.0322 | 363.048 | 351.7553
3320.0667 | 357.9738 | 363.9754 | 351.4733
3321.0667 | 357.8956 | 363.6502 | 351.1564
3322.0667 | 357.6413 | 363.8842 | 351.4586
3323.0667 | 357.5041 | 363.5262 | 351.9076
3324.0667 | 357.3984 | 362.9139 | 351.6118
3325.0667 | 357.2819 | 362.8481 | 351.4557
3326.0667 | 357.3303 | 362.8127 | 351.1584
3327.0667 | 357.7039 | 362.6837 | 351.0487
3328.0667 | 357.7902 | 362.8199 | 351.1262
3329.0667 | 357.6303 | 362.6787 | 350.6466
3330.0667 | 357.535 | 362.7398 | 350.7705
3331.0667 | 357.3605 | 362.4608 | 350.7608
3332.0667 | 357.3753 | 362.1726 | 350.6241
3333.0667 | 357.3305 | 361.9381 | 350.5732
3334.0667 | 357.4815 | 362.0042 | 350.7952
3335.0667 | 357.4859 | 362.1795 | 350.513
3336.0667 | 357.3491 | 361.8329 | 350.1035
3337.0667 | 357.19 | 361.2553 | 350.1534
3338.0667 | 356.8833 | 360.9115 | 350.1204
3339.0667 | 356.7243 | 360.8776 | 350.0871
3340.0667 | 356.4671 | 360.8126 | 350.0591
3341.0667 | 356.6594 | 361.3147 | 349.9828
3342.0667 | 357.029 | 362.1617 | 349.8152
3343.0667 | 356.9347 | 361.6208 | 350.418
3344.0667 | 357.2827 | 361.0882 | 350.6192
3345.0667 | 357.2853 | 360.8766 | 350.6437
3346.0667 | 357.0842 | 360.7046 | 351.0793
3347.0667 | 356.821 | 360.2471 | 351.2634
3348.0667 | 356.6773 | 361.5577 | 351.25
3349.0667 | 356.4902 | 361.2864 | 351.4007
3350.0667 | 356.3562 | 361.7326 | 351.1541
3351.0667 | 356.1103 | 361.361 | 350.9817
3352.0667 | 355.9221 | 361.1728 | 351.1929
3353.0667 | 356.3645 | 361.2129 | 351.0156
3354.0667 | 356.4627 | 360.9745 | 350.8783
3355.0667 | 356.6093 | 360.7295 | 350.4922
3356.0667 | 356.49 | 361.0604 | 350.2492
3357.0667 | 356.4528 | 361.0499 | 350.3449
3358.0667 | 356.2635 | 360.8232 | 350.3393
3359.0667 | 356.1398 | 360.6832 | 350.0856
3360.0667 | 356.8493 | 360.614 | 350.3391
3361.0667 | 356.8077 | 360.5424 | 350.4031
3362.0667 | 357.0193 | 360.6843 | 350.6965
3363.0667 | 357.1933 | 361.1181 | 350.8104
3364.0823 | 357.4287 | 361.6961 | 350.5591
3365.0823 | 357.4397 | 361.8062 | 350.5135
3366.0667 | 357.4235 | 362.2727 | 350.215
3367.0667 | 357.564 | 362.2579 | 349.9026
3368.0667 | 357.6329 | 362.1537 | 350.3933
3369.0667 | 358.0365 | 362.813 | 350.3508
3370.0667 | 357.7271 | 362.7867 | 350.3413
3371.0667 | 357.3284 | 362.384 | 350.3708
3372.0667 | 358.6188 | 362.2867 | 350.0202
3373.0667 | 358.7274 | 362.4893 | 349.9872
3374.0667 | 358.8106 | 362.1276 | 350.7258
3375.0667 | 359.5208 | 361.7279 | 351.3502
3376.0667 | 359.4411 | 361.5206 | 351.9037
3377.0667 | 359.3336 | 361.2336 | 352.2408
3378.0667 | 359.2744 | 361.6118 | 352.3812
3379.0823 | 359.0412 | 361.6216 | 352.3115
3380.0667 | 358.968 | 361.4811 | 351.8979
3381.0667 | 358.8731 | 361.5272 | 352.3212
3382.0667 | 359.002 | 361.7591 | 352.4562
3383.0667 | 358.9465 | 363.214 | 352.4054
3384.0667 | 359.4823 | 363.1464 | 352.4797
3385.0667 | 359.2556 | 363.3567 | 352.3605
3386.0667 | 358.9461 | 363.6743 | 352.3898
3387.0667 | 359.2509 | 364.7429 | 353.6914
3388.0667 | 360.669 | 365.0032 | 355.7339
3389.0667 | 361.3875 | 365.5331 | 355.9523
3390.0667 | 361.369 | 365.9964 | 356.5741
3391.0667 | 361.2646 | 365.9679 | 356.289
3392.0667 | 361.3292 | 365.6004 | 355.9382
3393.0667 | 362.0304 | 365.2768 | 355.3521
3394.0667 | 361.6545 | 364.7858 | 355.1814
3395.0667 | 361.8214 | 364.415 | 354.8761
3396.0667 | 361.9691 | 364.4396 | 354.771
3397.0667 | 361.6749 | 364.6286 | 354.8437
3398.0667 | 361.4416 | 364.9257 | 354.9179
3399.0667 | 361.9508 | 364.8655 | 355.1728
3400.0667 | 361.9606 | 365.1784 | 354.9185
3401.0667 | 361.9756 | 364.8171 | 356.4477
3402.0667 | 362.6375 | 364.6189 | 355.9416
3403.0667 | 362.4623 | 365.6433 | 355.9746
3404.0667 | 361.882 | 365.1424 | 355.7282
3405.0667 | 361.3711 | 364.5416 | 355.27
3406.0667 | 361.034 | 363.9988 | 354.7412
3407.0667 | 361.3978 | 363.6297 | 354.7077
3408.0667 | 361.1894 | 363.7096 | 354.2157
3409.0667 | 361.155 | 364.1852 | 353.8921
3410.0667 | 360.9549 | 364.9276 | 354.0769
3411.0667 | 360.8626 | 365.0282 | 353.6826
3412.0667 | 361.4258 | 365.9045 | 353.1783
3413.0667 | 361.141 | 365.7014 | 353.1099
3414.0667 | 361.6479 | 365.5388 | 353.344
3415.0667 | 361.4997 | 365.1316 | 353.2308
3416.0667 | 361.0877 | 364.5275 | 352.8498
3417.0667 | 360.6366 | 364.2811 | 352.6058
3418.0667 | 360.5925 | 363.913 | 352.6277
3419.0667 | 360.3559 | 364.8729 | 352.7795
3420.0667 | 360.1062 | 364.8812 | 352.5513
3421.0667 | 360.0168 | 364.9684 | 352.4386
3422.0667 | 359.6175 | 365.1891 | 352.3715
3423.0667 | 360.4663 | 365.0225 | 352.2227
3424.0667 | 359.971 | 364.408 | 352.0005
3425.0667 | 359.677 | 364.0999 | 351.7114
3426.0667 | 359.2056 | 363.8048 | 352.2567
3427.0667 | 358.7431 | 363.8485 | 352.1624
3428.0667 | 358.3919 | 363.9859 | 352.1481
3429.0667 | 358.1167 | 364.2258 | 352.0826
3430.0667 | 357.7631 | 364.2097 | 351.8829
3431.0667 | 357.4784 | 364.2455 | 351.9054
3432.0667 | 357.625 | 363.8893 | 352.1074
3433.0667 | 357.9185 | 363.9222 | 352.1887
3434.0667 | 357.9215 | 363.925 | 352.787
3435.0667 | 357.7396 | 363.9386 | 352.7383
3436.0667 | 359.0377 | 364.0694 | 352.7953
3437.0667 | 359.071 | 363.9726 | 352.9832
3438.0667 | 359.3496 | 363.6476 | 353.1565
3439.0667 | 359.7251 | 363.6266 | 353.4159
3440.0667 | 359.6412 | 364.2826 | 353.1347
3441.0667 | 359.4947 | 364.4656 | 354.2991
3442.0667 | 359.3763 | 364.4783 | 354.2083
3443.0667 | 359.0038 | 364.0394 | 353.8546
3444.0667 | 358.8833 | 363.9865 | 353.5063
3445.0667 | 359.5904 | 364.0484 | 353.3148
3446.0667 | 359.4714 | 364.1123 | 353.4119
3447.0667 | 359.2886 | 364.9663 | 353.1619
3448.0667 | 359.1756 | 365.0878 | 353.1387
3449.0667 | 358.864 | 364.9071 | 353.4688
3450.0667 | 358.5106 | 364.791 | 353.9817
3451.0667 | 358.2443 | 364.7902 | 354.0741
3452.0667 | 357.995 | 364.9302 | 353.9482
3453.0667 | 358.2536 | 364.7446 | 353.6536
3454.0667 | 358.0377 | 364.5625 | 353.3284
3455.0667 | 358.0363 | 364.4201 | 353.5178
3456.0667 | 357.7133 | 364.0613 | 353.953
3457.0667 | 357.6381 | 363.6278 | 353.8843
3458.0667 | 357.6876 | 364.3615 | 353.5627
3459.0667 | 357.5867 | 364.1833 | 353.2382
3460.0667 | 357.7004 | 363.9126 | 353.1927
3461.0667 | 357.6414 | 363.6866 | 352.9172
3462.0667 | 358.1027 | 363.5474 | 352.9923
3463.0667 | 358.3736 | 363.4311 | 353.2384
3464.0667 | 358.6782 | 363.192 | 352.9719
3465.0667 | 358.5193 | 363.2142 | 353.3667
3466.0667 | 358.2146 | 363.0036 | 353.0891
3467.0667 | 357.997 | 362.4986 | 352.7783
3468.0667 | 357.7213 | 362.1237 | 352.6769
3469.0667 | 357.4937 | 361.613 | 352.4677
3470.0667 | 357.2032 | 361.2662 | 352.2823
3471.0667 | 356.852 | 361.2004 | 351.8861
3472.0667 | 356.5706 | 361.1569 | 351.6645
3473.0667 | 356.5307 | 360.9207 | 351.317
3474.0667 | 356.4907 | 360.693 | 351.1203
3475.0667 | 356.6391 | 360.9656 | 351.1589
3476.0667 | 357.2453 | 361.1367 | 351.7433
3477.0667 | 357.7174 | 361.3758 | 351.6109
3478.0667 | 358.0502 | 361.3728 | 351.6404
3479.0667 | 358.4487 | 361.2757 | 351.4152
3480.0667 | 358.5983 | 361.4287 | 351.5366
3481.0667 | 358.6514 | 361.4971 | 351.4508
3482.0667 | 358.8192 | 361.748 | 351.4415
3483.0667 | 358.8216 | 362.3976 | 351.8888
3484.0823 | 359.0444 | 362.5775 | 352.3282
3485.0667 | 359.1068 | 362.6955 | 352.2338
3486.0667 | 359.4699 | 363.0765 | 352.276
3487.0667 | 359.3253 | 363.097 | 352.0893
3488.0667 | 359.359 | 363.2751 | 352.2021
3489.0667 | 359.2881 | 363.1935 | 351.7828
3490.0667 | 358.9348 | 362.7271 | 351.5575
3491.0667 | 358.8016 | 362.4971 | 351.2501
3492.0667 | 358.5934 | 362.3209 | 351.3279
3493.0667 | 358.5508 | 362.4291 | 351.6759
3494.0667 | 358.4282 | 362.4295 | 351.3917
3495.0667 | 358.1065 | 362.2155 | 351.4017
3496.0667 | 358.1196 | 361.9438 | 351.2792
3497.0667 | 358.1323 | 361.7308 | 351.354
3498.0667 | 358.1768 | 361.7001 | 351.1584
3499.0823 | 358.4072 | 363.0671 | 351.1524
3500.0667 | 358.2744 | 362.8031 | 351.2084
3501.0667 | 358.2259 | 362.5615 | 351.1498
3502.0667 | 358.0626 | 362.1939 | 351.0181
3503.0667 | 358.1393 | 361.7522 | 350.796
3504.0667 | 358.4973 | 361.6194 | 350.4783
3505.0667 | 358.7395 | 361.595 | 350.3475
3506.0667 | 358.6565 | 361.5463 | 350.2613
3507.0667 | 359.2558 | 361.8108 | 350.439
3508.0667 | 359.3642 | 361.8721 | 350.6221
3509.0667 | 359.3052 | 362.1812 | 350.5896
3510.0667 | 359.2348 | 362.1667 | 350.517
3511.0667 | 359.1105 | 362.4273 | 350.7983
3512.0667 | 359.1065 | 362.6362 | 351.6717
3513.0667 | 359.0448 | 363.0302 | 351.6247
3514.0667 | 358.9801 | 363.3873 | 351.4217
3515.0667 | 359.1117 | 363.7082 | 351.3145
3516.0667 | 360.6747 | 363.5541 | 351.229
3517.0667 | 360.973 | 363.3687 | 351.0263
3518.0667 | 361.2133 | 363.2818 | 350.8795
3519.0667 | 361.4936 | 363.219 | 350.9028
3520.0667 | 361.4624 | 363.2686 | 350.7609
3521.0667 | 361.3237 | 363.4094 | 351.2663
3522.0667 | 361.2336 | 363.7604 | 351.9181
3523.0667 | 361.1455 | 363.7112 | 352.0722
3524.0667 | 361.0152 | 363.911 | 352.3065
3525.0667 | 360.6617 | 363.5198 | 352.5682
3526.0667 | 360.3028 | 363.1232 | 353.1495
3527.0667 | 361.0888 | 362.9223 | 352.8653
3528.0667 | 360.7199 | 362.6685 | 352.7717
3529.0667 | 360.7347 | 362.4316 | 352.5837
3530.0667 | 360.572 | 362.4189 | 352.4963
3531.0667 | 360.0097 | 362.3526 | 352.5666
3532.0667 | 359.5109 | 361.9388 | 352.1119
3533.0667 | 359.2632 | 362.1029 | 351.8901
3534.0667 | 359.2989 | 362.1008 | 351.7819
3535.0667 | 359.3199 | 362.9489 | 351.762
3536.0667 | 359.0377 | 363.5211 | 351.9067
3537.0667 | 358.781 | 363.4262 | 352.109
3538.0667 | 358.4217 | 363.1339 | 352.1326
3539.0667 | 358.2264 | 363.8535 | 353.3863
3540.0667 | 358.2894 | 363.5144 | 352.9782
3541.0667 | 358.0894 | 364.1271 | 353.2011
3542.0667 | 357.8879 | 364.0865 | 353.0125
3543.0667 | 357.7716 | 364.2406 | 352.7823
3544.0823 | 357.7459 | 364.0217 | 352.5122
3545.0667 | 357.6538 | 364.71 | 352.3986
3546.0667 | 357.467 | 364.2329 | 352.137
3547.0823 | 357.415 | 363.74 | 352.2797
3548.0667 | 357.2758 | 363.2042 | 351.8018
3549.0667 | 357.2886 | 362.9126 | 351.6188
3550.0823 | 357.3453 | 363.1151 | 351.3977
3551.0823 | 357.3956 | 362.5829 | 351.2932
3552.0667 | 357.3092 | 362.136 | 350.933
3553.0667 | 357.2382 | 362.1665 | 350.584
3554.0667 | 357.0624 | 362.5362 | 350.3473
3555.0667 | 356.8735 | 362.189 | 350.1318
3556.0667 | 356.7743 | 361.8929 | 350.4473
3557.0667 | 356.6558 | 361.9312 | 351.4413
3558.0667 | 356.5825 | 361.8121 | 351.7795
3559.0667 | 356.7927 | 362.2432 | 351.9407
3560.0667 | 356.7706 | 362.1145 | 351.841
3561.0667 | 357.0753 | 362.394 | 351.8046
3562.0667 | 357.0983 | 362.1905 | 351.7709
3563.0667 | 357.9134 | 362.1782 | 351.7101
3564.0667 | 358.287 | 362.6383 | 351.3339
3565.0667 | 358.0952 | 362.7957 | 350.9373
3566.0667 | 357.8148 | 362.2994 | 350.5505
3567.0667 | 357.4215 | 361.9237 | 350.4506
3568.0667 | 357.3517 | 362.1683 | 350.9355
3569.0667 | 357.5304 | 362.5056 | 351.1561
3570.0667 | 357.4063 | 363.4545 | 350.9001
3571.0667 | 357.3696 | 363.1866 | 350.8105
3572.0667 | 357.2304 | 363.065 | 350.5525
3573.0667 | 357.073 | 362.9855 | 350.2831
3574.0667 | 357.0571 | 362.8437 | 349.9438
3575.0667 | 357.2444 | 362.7283 | 349.795
3576.0667 | 357.6332 | 362.6288 | 349.5179
3577.0667 | 357.8842 | 362.9227 | 349.4029
3578.0667 | 357.8606 | 362.928 | 349.3506
3579.0667 | 358.1204 | 364.3231 | 350.2479
3580.0667 | 358.1429 | 365.4771 | 350.8201
3581.0667 | 358.5209 | 367.0245 | 351.8968
3582.0667 | 358.7029 | 366.9992 | 352.8382
3583.0667 | 359.6154 | 367.3403 | 353.0591
3584.0823 | 360.0768 | 367.8913 | 353.1332
3585.0667 | 360.0047 | 367.6373 | 352.8011
3586.0667 | 360.0164 | 367.7362 | 352.8889
3587.0667 | 359.7439 | 367.0901 | 352.5886
3588.0667 | 359.4527 | 366.526 | 352.1709
3589.0667 | 359.3217 | 366.2226 | 351.9138
3590.0667 | 359.0629 | 365.6733 | 351.784
3591.0667 | 358.5824 | 365.1043 | 352.0665
3592.0667 | 358.2003 | 364.8618 | 352.1183
3593.0667 | 357.8641 | 365.3356 | 351.8586
3594.0667 | 357.8849 | 364.9866 | 351.7681
3595.0667 | 357.5288 | 364.5138 | 352.2122
3596.0667 | 357.3675 | 365.198 | 352.0614
3597.0667 | 357.8387 | 365.1167 | 352.4523
3598.0667 | 357.6704 | 364.5201 | 351.9945
3599.0667 | 357.5061 | 364.109 | 351.5999
3600.0667 | 357.4301 | 363.6645 | 351.1871
3601.0667 | 357.4144 | 362.9991 | 350.8906
3602.0667 | 357.5955 | 363.7359 | 350.6515
3603.0667 | 357.5217 | 363.7546 | 350.5264
3604.0667 | 357.4071 | 364.5637 | 350.6287
3605.0667 | 357.9114 | 364.028 | 350.4436
3606.0667 | 358.0752 | 364.3758 | 350.3572
3607.0667 | 358.137 | 364.5281 | 350.5755
3608.0667 | 358.0914 | 364.3686 | 350.835
3609.0667 | 358.0435 | 364.3162 | 350.9256
3610.0667 | 358.1697 | 364.2874 | 352.3838
3611.0667 | 358.3268 | 363.9102 | 352.5786
3612.0667 | 358.1209 | 364.211 | 352.4365
3613.0667 | 358.6384 | 363.9982 | 352.32
3614.0667 | 358.577 | 363.8292 | 352.4933
3615.0667 | 358.2855 | 363.6722 | 352.9162
3616.0667 | 358.095 | 363.6507 | 352.5915
3617.0667 | 358.3825 | 363.7226 | 352.3344
3618.0667 | 358.449 | 363.8058 | 352.2254
3619.0667 | 358.4956 | 364.2355 | 352.3836
3620.0667 | 358.4042 | 364.5227 | 353.0986
3621.0667 | 358.729 | 364.6099 | 353.3548
3622.0667 | 359.0275 | 364.6624 | 354.3725
3623.0667 | 359.8664 | 364.7698 | 354.1035
3624.0667 | 359.688 | 364.901 | 354.6477
3625.0667 | 359.4232 | 364.5474 | 354.1588
3626.0667 | 359.1318 | 364.3183 | 353.5772
3627.0667 | 359.0271 | 363.9768 | 353.0565
3628.0667 | 359.313 | 363.7178 | 352.7403
3629.0667 | 359.6689 | 363.4157 | 352.554
3630.0667 | 361.3413 | 363.9955 | 352.5362
3631.0667 | 361.9618 | 364.5565 | 352.28
3632.0667 | 362.6757 | 364.8724 | 352.0496
3633.0667 | 362.4421 | 364.6825 | 351.8044
3634.0667 | 362.3198 | 364.7606 | 351.597
3635.0667 | 362.2706 | 364.3806 | 351.3633
3636.0667 | 362.0606 | 364.2267 | 351.3437
3637.0667 | 362.1785 | 364.2294 | 351.8349
3638.0667 | 361.6061 | 364.4307 | 351.6776
3639.0667 | 361.1839 | 364.397 | 351.7491
3640.0667 | 360.7982 | 364.4325 | 352.29
3641.0667 | 360.3902 | 364.6788 | 352.8421
3642.0667 | 360.1095 | 364.729 | 352.5143
3643.0667 | 360.2168 | 364.7179 | 352.678
3644.0667 | 359.9864 | 364.6929 | 352.3389
3645.0667 | 359.6863 | 365.3577 | 352.2741
3646.0667 | 359.4774 | 364.9157 | 352.1133
3647.0667 | 359.2649 | 364.5242 | 351.6603
3648.0667 | 358.9853 | 364.563 | 351.5617
3649.0667 | 359.0863 | 364.4602 | 351.8743
3650.0667 | 359.337 | 364.2846 | 351.8841
3651.0667 | 359.4969 | 364.8075 | 351.9625
3652.0667 | 359.6003 | 365.0679 | 351.9356
3653.0667 | 359.5779 | 364.9272 | 351.8094
3654.0667 | 360.565 | 364.8168 | 351.7538
3655.0667 | 360.5842 | 364.8672 | 351.6233
3656.0667 | 360.2451 | 364.5828 | 351.7334
3657.0667 | 360.4578 | 364.1688 | 351.5137
3658.0667 | 360.2583 | 364.6208 | 351.478
3659.0667 | 360.126 | 363.9858 | 351.335
3660.0667 | 359.8746 | 363.552 | 351.3111
3661.0667 | 359.9313 | 363.5092 | 351.4603
3662.0667 | 359.7717 | 363.5943 | 351.5008
3663.0667 | 359.6121 | 363.3908 | 351.6328
3664.0823 | 359.5301 | 363.2334 | 351.5186
3665.0667 | 359.4025 | 363.1891 | 351.1675
3666.0667 | 359.449 | 363.2951 | 351.0479
3667.0667 | 359.0189 | 363.0275 | 350.8967
3668.0667 | 359.1834 | 362.9505 | 350.7665
3669.0667 | 359.124 | 363.0529 | 350.8819
3670.0667 | 358.782 | 362.9981 | 351.0359
3671.0667 | 358.7538 | 363.2018 | 350.5926
3672.0667 | 358.6304 | 363.1739 | 350.7962
3673.0667 | 358.8649 | 362.8213 | 351.5968
3674.0667 | 358.7231 | 363.1076 | 351.5443
3675.0667 | 358.6423 | 362.9665 | 351.3753
3676.0667 | 358.5177 | 363.1797 | 351.2041
3677.0667 | 358.2706 | 363.0557 | 351.0531
3678.0667 | 357.9687 | 362.7868 | 350.8223
3679.0823 | 357.7293 | 362.9363 | 350.8107
3680.0667 | 357.3289 | 363.5004 | 351.3555
3681.0667 | 357.3626 | 363.388 | 351.6765
3682.0667 | 357.8607 | 363.4421 | 352.2848
3683.0667 | 357.8659 | 363.8059 | 352.2528
3684.0667 | 358.5012 | 363.7772 | 352.0251
3685.0667 | 358.8797 | 363.9404 | 351.7129
3686.0667 | 359.4699 | 363.5948 | 351.2923
3687.0667 | 359.2575 | 363.4716 | 350.9048
3688.0667 | 359.0871 | 363.7391 | 350.5417
3689.0667 | 359.11 | 363.6159 | 350.3333
3690.0667 | 359.0328 | 363.6663 | 350.8267
3691.0667 | 358.9245 | 364.0736 | 351.7811
3692.0667 | 358.9218 | 363.9127 | 352.478
3693.0667 | 358.8722 | 363.694 | 353.1142
3694.0667 | 358.9842 | 363.4857 | 353.3156
3695.0667 | 358.9458 | 364.0069 | 353.6485
3696.0667 | 358.9034 | 363.9527 | 353.5355
3697.0667 | 358.9458 | 363.6651 | 353.6294
3698.0667 | 358.9276 | 363.686 | 353.5188
3699.0667 | 359.4421 | 364.267 | 354.0855
3700.0667 | 360.1483 | 364.5929 | 354.1796
3701.0667 | 360.4273 | 364.5598 | 353.8843
3702.0823 | 360.7821 | 364.3484 | 353.8604
3703.0667 | 360.8377 | 363.9877 | 353.5968
3704.0823 | 360.6018 | 363.6628 | 353.5112
3705.0667 | 360.2325 | 364.3909 | 353.2272
3706.0667 | 359.9263 | 363.8437 | 353.2317
3707.0667 | 360.0614 | 363.6292 | 352.8383
3708.0667 | 359.7697 | 363.129 | 352.4738
3709.0667 | 359.536 | 362.4435 | 351.8196
3710.0667 | 359.8383 | 361.7254 | 351.2461
3711.0667 | 359.7178 | 361.639 | 350.8799
3712.0667 | 359.4985 | 361.7754 | 350.7416
3713.0667 | 359.123 | 362.0432 | 351.4783
3714.0667 | 358.7623 | 361.8542 | 351.5986
3715.0667 | 358.4015 | 361.9785 | 351.8467
3716.0667 | 358.0825 | 362.1434 | 351.8048
3717.0667 | 357.7856 | 361.8685 | 351.5368
3718.0667 | 357.4693 | 361.7669 | 351.4817
3719.0823 | 357.651 | 361.3189 | 351.5145
3720.0667 | 358.2753 | 361.1601 | 351.2566
3721.0667 | 358.7458 | 360.8263 | 350.8767
3722.0667 | 358.7544 | 360.6302 | 350.3861
3723.0667 | 358.7198 | 360.676 | 350.2817
3724.0667 | 358.5737 | 360.5723 | 350.8891
3725.0667 | 358.6684 | 360.4437 | 350.8381
3726.0667 | 359.2343 | 360.8019 | 351.3591
3727.0667 | 360.0257 | 361.0634 | 351.8367
3728.0667 | 360.0852 | 361.6854 | 351.7629
3729.0667 | 360.1784 | 361.9767 | 351.7481
3730.0667 | 360.0897 | 361.7513 | 351.3704
3731.0667 | 360.0373 | 361.7047 | 351.3748
3732.0667 | 360.0306 | 361.4532 | 351.1261
3733.0667 | 360.1043 | 361.2964 | 351.1004
3734.0667 | 360.0654 | 361.4223 | 351.018
3735.0667 | 360.3238 | 362.0845 | 351.6031
3736.0667 | 360.734 | 362.133 | 352.1596
3737.0667 | 361.6689 | 362.8231 | 352.0505
3738.0667 | 362.1613 | 364.6821 | 351.9784
3739.0667 | 361.9141 | 365.3524 | 352.079
3740.0667 | 361.589 | 365.2297 | 352.3434
3741.0667 | 361.2681 | 365.1068 | 352.35
3742.0667 | 361.0167 | 364.9969 | 352.0713
3743.0667 | 360.6147 | 365.1286 | 352.059
3744.0667 | 360.335 | 364.7013 | 352.8004
3745.0667 | 360.0742 | 364.2077 | 353.0809
3746.0667 | 360.1436 | 364.2668 | 352.8935
3747.0667 | 360.1594 | 363.8745 | 352.386
3748.0667 | 359.7956 | 363.545 | 352.4127
3749.0667 | 359.5834 | 363.5342 | 352.302
3750.0667 | 359.5299 | 363.6459 | 352.0466
3751.0667 | 359.4987 | 363.9911 | 351.7221
3752.0667 | 359.1207 | 363.818 | 351.6203
3753.0667 | 359.0087 | 363.8492 | 351.4198
3754.0667 | 359.1249 | 364.9032 | 351.2726
3755.0667 | 359.1317 | 365.3312 | 351.5205
3756.0667 | 360.1785 | 366.1176 | 351.5925
3757.0667 | 360.3083 | 365.9103 | 351.7502
3758.0667 | 360.2739 | 365.9243 | 352.1618
3759.0667 | 360.0763 | 365.6113 | 352.8031
3760.0667 | 360.0535 | 365.327 | 353.1229
3761.0667 | 359.7985 | 365.0872 | 353.2307
3762.0667 | 359.4987 | 364.9067 | 353.2838
3763.0667 | 359.0348 | 364.6972 | 353.4147
3764.0823 | 358.8634 | 364.6222 | 354.5535
3765.0667 | 358.6236 | 364.6375 | 354.7644
3766.0667 | 358.5956 | 364.4977 | 355.0377
3767.0667 | 358.1979 | 364.5953 | 355.2303
3768.0667 | 357.822 | 364.2285 | 354.8919
3769.0667 | 358.0321 | 363.7021 | 354.8451
3770.0667 | 357.8313 | 363.5687 | 354.8514
3771.0667 | 357.6232 | 363.595 | 354.4911
3772.0667 | 357.5047 | 364.8765 | 354.1115
3773.0667 | 357.5618 | 364.8826 | 354.1313
3774.0667 | 357.4583 | 364.7452 | 353.9542
3775.0667 | 357.5787 | 364.8407 | 353.7001
3776.0667 | 358.001 | 364.6026 | 353.376
3777.0667 | 357.8646 | 364.3701 | 353.289
3778.0667 | 357.7999 | 364.4724 | 353.311
3779.0667 | 357.8592 | 364.4721 | 353.8969
3780.0823 | 358.1747 | 364.7327 | 353.8575
3781.0823 | 358.2566 | 365.7716 | 353.944
3782.0667 | 358.5911 | 365.5317 | 353.8216
3783.0667 | 358.4843 | 365.4854 | 353.7689
3784.0823 | 358.5346 | 365.1578 | 353.7109
3785.0667 | 358.5242 | 365.179 | 353.3064
3786.0823 | 358.414 | 364.6538 | 353.1172
3787.0823 | 358.3589 | 364.2238 | 353.147
3788.0667 | 358.3627 | 363.8739 | 353.1702
3789.0667 | 358.5001 | 363.8901 | 352.9777
3790.0667 | 358.6343 | 363.7344 | 352.6139
3791.0667 | 358.6183 | 363.6438 | 352.2498
3792.0667 | 358.6838 | 363.2205 | 352.2569
3793.0667 | 359.3617 | 363.2612 | 352.4868
3794.0667 | 359.9007 | 363.8806 | 352.7042
3795.0667 | 359.9043 | 363.7956 | 352.4032
3796.0667 | 359.8803 | 363.6654 | 352.3335
3797.0667 | 359.6773 | 363.4139 | 352.2381
3798.0667 | 359.3188 | 363.1847 | 352.0459
3799.0667 | 358.9642 | 362.7827 | 351.9526
3800.0667 | 358.519 | 362.4091 | 352.0618
3801.0823 | 358.0202 | 362.2715 | 351.9584
3802.0667 | 357.6172 | 362.4524 | 351.6865
3803.0667 | 357.1952 | 362.2655 | 351.3129
3804.0823 | 356.93 | 361.9828 | 351.4825
3805.0667 | 357.2608 | 362.1638 | 351.3347
3806.0667 | 357.5719 | 362.7408 | 351.3684
3807.0667 | 357.6516 | 363.1314 | 351.6401
3808.0667 | 358.3749 | 363.2419 | 352.2776
3809.0667 | 358.5175 | 363.2851 | 352.986
3810.0667 | 358.8074 | 363.1005 | 352.9187
3811.0667 | 358.7564 | 362.9376 | 352.5429
3812.0667 | 358.5858 | 363.0163 | 352.0624
3813.0667 | 358.4279 | 362.938 | 351.7729
3814.0667 | 358.3157 | 362.6442 | 351.7756
3815.0667 | 358.1026 | 362.3761 | 351.4953
3816.0667 | 358.0801 | 362.7123 | 351.3744
3817.0667 | 358.0167 | 362.4134 | 351.2854
3818.0667 | 358.0367 | 362.4593 | 351.1536
3819.0667 | 358.0274 | 362.7 | 351.5071
3820.0667 | 358.1746 | 362.6992 | 351.3105
3821.0667 | 358.3984 | 363.1194 | 351.3708
3822.0667 | 358.4594 | 364.5114 | 351.0722
3823.0667 | 358.2921 | 364.2847 | 351.2035
3824.0667 | 358.0745 | 363.9286 | 351.1279
3825.0667 | 358.0522 | 363.5943 | 350.9081
3826.0667 | 358.256 | 363.6395 | 351.1459
3827.0667 | 358.1836 | 363.2827 | 351.2492
3828.0667 | 358.4438 | 363.836 | 351.4677
3829.0667 | 358.5405 | 363.6965 | 351.8923
3830.0667 | 358.6425 | 363.7509 | 351.862
3831.0667 | 358.6956 | 363.7755 | 351.8905
3832.0667 | 359.2021 | 364.1503 | 351.8305
3833.0667 | 359.0844 | 363.5969 | 351.5804
3834.0667 | 359.059 | 363.7128 | 351.3
3835.0667 | 358.9551 | 363.5943 | 351.7482
3836.0667 | 359.3963 | 363.3759 | 351.5355
3837.0667 | 359.3843 | 363.3401 | 351.7076
3838.0667 | 359.2143 | 363.5475 | 352.0284
3839.0667 | 359.2493 | 363.4423 | 352.2085
3840.0667 | 359.1349 | 363.4182 | 352.3724
3841.0667 | 359.0672 | 363.5452 | 352.6125
3842.0667 | 359.2886 | 363.6397 | 353.1922
3843.0667 | 359.7151 | 364.1926 | 354.6987
3844.0667 | 360.4217 | 364.5838 | 355.619
3845.0667 | 360.7296 | 364.4411 | 355.2264
3846.0667 | 361.3244 | 364.2695 | 355.3903
3847.0667 | 361.8562 | 364.3874 | 355.9993
3848.0667 | 362.0179 | 364.465 | 355.7491
3849.0667 | 362.2375 | 364.8136 | 355.5801
3850.0667 | 362.1178 | 364.8589 | 355.4205
3851.0667 | 362.3131 | 364.5606 | 355.0691
3852.0667 | 362.4444 | 364.5769 | 354.783
3853.0667 | 362.5479 | 364.799 | 354.4455
3854.0667 | 362.3924 | 364.9405 | 354.4772
3855.0667 | 362.3554 | 365.1363 | 354.6638
3856.0667 | 362.6626 | 365.004 | 354.8364
3857.0667 | 362.2953 | 365.3529 | 354.5946
3858.0667 | 362.2719 | 365.8144 | 354.6751
3859.0667 | 363.1493 | 366.1636 | 354.359
3860.0667 | 362.9792 | 366.306 | 353.9821
3861.0667 | 363.5157 | 366.1294 | 353.8685
3862.0667 | 363.4068 | 366.0729 | 353.8202
3863.0667 | 362.9133 | 365.6743 | 353.5414
3864.0667 | 362.3676 | 365.3168 | 353.6429
3865.0667 | 361.9301 | 365.1218 | 353.5007
3866.0667 | 361.5354 | 364.6981 | 353.184
3867.0667 | 361.2539 | 364.8231 | 353.0729
3868.0667 | 360.9843 | 365.0809 | 353.3849
3869.0667 | 360.6293 | 364.9799 | 353.5301
3870.0667 | 360.2609 | 365.1319 | 353.4421
3871.0667 | 360.1529 | 365.8093 | 353.373
3872.0667 | 359.9815 | 366.1658 | 353.2777
3873.0667 | 359.8859 | 365.7092 | 353.2786
3874.0667 | 359.6658 | 365.4907 | 353.66
3875.0667 | 359.5946 | 365.3856 | 353.5662
3876.0667 | 359.9266 | 365.6498 | 353.2846
3877.0667 | 359.7905 | 365.4196 | 352.9785
3878.0667 | 359.4536 | 365.1394 | 352.8497
3879.0667 | 359.3953 | 365.0055 | 352.624
3880.0667 | 359.1038 | 364.8467 | 352.3317
3881.0667 | 358.826 | 364.6358 | 352.4043
3882.0667 | 358.5508 | 364.6801 | 352.2577
3883.0667 | 358.7918 | 364.6197 | 352.2379
3884.0823 | 359.1067 | 364.5011 | 352.1322
3885.0667 | 359.8325 | 364.8911 | 351.9871
3886.0667 | 361.2457 | 365.1428 | 351.9467
3887.0667 | 361.0773 | 365.0025 | 351.7124
3888.0667 | 361.1055 | 364.7336 | 351.7256
3889.0667 | 360.8598 | 364.4248 | 352.2185
3890.0667 | 360.5866 | 364.3686 | 352.6206
3891.0667 | 360.2924 | 364.5942 | 352.9622
3892.0667 | 360.4538 | 364.4921 | 353.1996
3893.0667 | 360.4327 | 364.7346 | 353.1607
3894.0823 | 360.2929 | 365.2787 | 353.1352
3895.0667 | 360.123 | 365.2359 | 353.0324
3896.0667 | 359.9832 | 365.0744 | 353.4835
3897.0667 | 360.2301 | 365.8596 | 353.2403
3898.0667 | 360.0362 | 365.6606 | 352.944
3899.0823 | 359.9427 | 365.2604 | 352.8125
3900.0667 | 359.5736 | 364.6922 | 352.6414
3901.0667 | 359.3198 | 364.6585 | 352.1981
3902.0667 | 359.0983 | 364.3571 | 351.9373
3903.0667 | 359.053 | 364.0029 | 351.7547
3904.0667 | 358.9834 | 364.1827 | 352.2652
3905.0667 | 358.8251 | 363.7984 | 352.8224
3906.0667 | 358.6725 | 363.9251 | 352.9696
3907.0667 | 358.6863 | 364.0983 | 353.1535
3908.0667 | 358.747 | 364.309 | 353.3398
3909.0667 | 358.7842 | 364.4462 | 353.4818
3910.0667 | 358.6787 | 364.9527 | 354.0436
3911.0667 | 358.8366 | 364.748 | 354.2235
3912.0667 | 358.9837 | 364.5418 | 354.0171
3913.0667 | 358.7973 | 364.8096 | 353.6599
3914.0667 | 359.1331 | 364.3155 | 353.4005
3915.0667 | 358.8078 | 364.0618 | 353.6071
3916.0667 | 358.6431 | 364.0906 | 353.4894
3917.0667 | 358.6198 | 364.505 | 353.159
3918.0667 | 358.8407 | 364.3802 | 353.3137
3919.0667 | 359.2409 | 364.2361 | 353.1907
3920.0667 | 359.6911 | 364.095 | 353.552
3921.0667 | 359.8896 | 364.095 | 353.6806
3922.0667 | 359.8012 | 364.2613 | 353.5161
3923.0667 | 359.9508 | 364.7977 | 353.6347
3924.0823 | 361.0405 | 364.9629 | 353.6975
3925.0667 | 361.3338 | 365.1143 | 353.9582
3926.0667 | 361.3104 | 364.8384 | 353.9518
3927.0667 | 361.5411 | 364.8969 | 354.007
3928.0667 | 361.5062 | 364.7189 | 354.259
3929.0667 | 361.3379 | 364.3967 | 354.155
3930.0667 | 361.124 | 364.5668 | 355.1044
3931.0667 | 360.8816 | 364.6654 | 355.2005
3932.0667 | 360.5638 | 364.3256 | 355.0052
3933.0667 | 360.1646 | 364.5108 | 354.8615
3934.0823 | 359.7789 | 364.7554 | 354.5897
3935.0667 | 359.6319 | 364.5978 | 354.7268
3936.0667 | 359.6187 | 364.394 | 354.3969
3937.0667 | 359.4727 | 364.3521 | 354.3477
3938.0667 | 359.292 | 364.5185 | 354.3895
3939.0823 | 359.4155 | 364.8726 | 354.1789
3940.0667 | 359.2175 | 364.6276 | 353.9258
3941.0667 | 359.2762 | 364.9522 | 353.6682
3942.0667 | 359.4837 | 365.297 | 353.4383
3943.0667 | 359.6363 | 365.2615 | 353.4873
3944.0667 | 359.6117 | 365.4808 | 353.5943
3945.0667 | 359.6573 | 366.071 | 353.7239
3946.0667 | 359.6515 | 366.5407 | 353.5738
3947.0667 | 359.8233 | 366.8346 | 354.0271
3948.0667 | 361.0504 | 366.7334 | 354.3608
3949.0667 | 361.2591 | 366.8189 | 354.284
3950.0667 | 361.3451 | 366.9731 | 354.4256
3951.0667 | 361.2556 | 366.9127 | 354.2046
3952.0667 | 361.0902 | 367.2247 | 353.9898
3953.0667 | 361.1612 | 367.7089 | 354.1351
3954.0667 | 361.138 | 367.7557 | 353.9114
3955.0667 | 361.2482 | 367.6401 | 353.9965
3956.0667 | 361.2852 | 367.6337 | 354.8209
3957.0667 | 361.1553 | 367.7839 | 355.2129
3958.0667 | 361.0922 | 367.9008 | 355.2033
3959.0667 | 361.2362 | 368.0319 | 355.8658
3960.0667 | 361.2433 | 368.0699 | 355.749
3961.0667 | 361.0155 | 367.6052 | 355.4445
3962.0667 | 360.8593 | 367.2312 | 355.5462
3963.0667 | 361.5072 | 367.0842 | 355.1317
3964.0667 | 361.4577 | 367.526 | 354.9552
3965.0823 | 361.2844 | 367.5503 | 355.2081
3966.0667 | 361.2994 | 367.3047 | 355.0001
3967.0667 | 361.2212 | 367.0381 | 354.6048
3968.0667 | 361.1151 | 366.8943 | 354.2729
3969.0667 | 361.0814 | 366.8045 | 354.3524
3970.0667 | 361.0995 | 366.6812 | 354.7813
3971.0667 | 361.1498 | 366.9666 | 355.613
3972.0667 | 362.129 | 367.0203 | 355.8856
3973.0667 | 362.9011 | 367.9684 | 355.6898
3974.0667 | 362.8957 | 367.8377 | 355.7069
3975.0667 | 362.6224 | 368.1067 | 355.4077
3976.0667 | 363.8912 | 368.2716 | 355.5239
3977.0667 | 363.987 | 368.1768 | 355.5421
3978.0667 | 364.26 | 367.6932 | 355.3427
3979.0667 | 363.9805 | 367.7106 | 355.4302
3980.0667 | 364.2031 | 367.7094 | 355.2884
3981.0667 | 363.5686 | 367.6007 | 355.1173
3982.0667 | 362.9841 | 367.3389 | 354.9613
3983.0667 | 362.4746 | 367.1403 | 355.1074
3984.0823 | 362.0804 | 366.5596 | 355.0226
3985.0667 | 361.9241 | 366.0066 | 355.3478
3986.0667 | 361.644 | 366.5611 | 355.139
3987.0667 | 362.0792 | 366.7246 | 355.0656
3988.0667 | 362.4712 | 367.3156 | 355.573
3989.0667 | 364.0176 | 367.8151 | 355.3713
3990.0667 | 364.2653 | 367.5569 | 355.2624
3991.0667 | 364.5572 | 367.5397 | 355.0133
3992.0667 | 364.5689 | 368.3113 | 355.1798
3993.0667 | 364.5482 | 368.2393 | 355.8514
3994.0667 | 364.4213 | 368.1463 | 355.5279
3995.0667 | 364.2716 | 367.8621 | 355.1395
3996.0667 | 363.9198 | 367.5519 | 354.7441
3997.0667 | 363.5208 | 366.8936 | 354.4863
3998.0667 | 363.1352 | 366.6984 | 354.1036
3999.0667 | 362.7409 | 366.5233 | 354.3939
4000.0667 | 362.3037 | 366.5132 | 354.6967
4001.0667 | 361.7989 | 366.2824 | 354.2544
4002.0667 | 361.7144 | 366.201 | 354.5225
4003.0667 | 361.448 | 366.1091 | 354.354
4004.0667 | 361.5798 | 366.5814 | 355.8672
4005.0667 | 361.4243 | 366.7139 | 356.6256
4006.0667 | 361.3467 | 366.6609 | 356.6376
4007.0667 | 361.2189 | 367.2159 | 356.4978
4008.0667 | 361.0315 | 366.9698 | 356.6714
4009.0667 | 360.7917 | 366.6221 | 356.2362
4010.0667 | 361.2801 | 366.3473 | 355.9277
4011.0667 | 361.7161 | 365.7573 | 356.0399
4012.0667 | 361.767 | 365.5749 | 355.8702
4013.0667 | 361.7148 | 366.5926 | 355.6841
4014.0667 | 361.4072 | 366.7661 | 356.7616
4015.0667 | 361.2372 | 366.7538 | 357.1395
4016.0667 | 361.0608 | 366.6083 | 357.2334
4017.0667 | 360.8069 | 366.272 | 356.9774
4018.0667 | 361.3614 | 365.8594 | 356.7066
4019.0667 | 361.5282 | 365.6428 | 356.4198
4020.0667 | 361.1737 | 365.3138 | 356.2767
4021.0667 | 361.2645 | 364.9747 | 355.8539
4022.0667 | 360.9567 | 364.8801 | 355.5213
4023.0823 | 360.7351 | 364.646 | 355.6879
4024.0823 | 360.6165 | 365.3895 | 355.8825
4025.0667 | 360.5971 | 365.6973 | 356.701
4026.0667 | 360.4253 | 365.9159 | 357.2983
4027.0667 | 360.994 | 367.6477 | 357.0234
4028.0667 | 361.8379 | 368.0489 | 356.907
4029.0667 | 361.8215 | 368.1209 | 356.7671
4030.0667 | 361.9993 | 368.2859 | 356.5665
4031.0667 | 361.9007 | 368.0669 | 356.2287
4032.0667 | 361.9512 | 367.8219 | 355.7254
4033.0667 | 361.9425 | 368.3312 | 355.5301
4034.0667 | 362.4131 | 367.7556 | 355.2482
4035.0667 | 362.2857 | 367.5457 | 354.8403
4036.0667 | 362.2498 | 367.4585 | 354.8369
4037.0667 | 362.1406 | 367.2211 | 355.9559
4038.0667 | 362.1733 | 367.0056 | 355.7789
4039.0667 | 361.9096 | 367.0686 | 356.4535
4040.0667 | 361.686 | 367.0914 | 356.4809
4041.0667 | 361.521 | 366.9683 | 356.4119
4042.0667 | 361.3689 | 366.7337 | 356.6361
4043.0667 | 361.4998 | 366.5902 | 356.2573
4044.0667 | 361.4114 | 366.4899 | 356.1782
4045.0667 | 361.3379 | 366.3649 | 356.1053
4046.0667 | 361.4515 | 366.2806 | 355.9569
4047.0667 | 361.3734 | 366.2696 | 355.8325
4048.0667 | 361.5967 | 366.6228 | 356.3426
4049.0667 | 361.5934 | 366.9071 | 357.2539
4050.0667 | 361.821 | 366.9758 | 357.4115
4051.0667 | 361.7523 | 366.9186 | 357.1797
4052.0667 | 362.0475 | 366.7501 | 356.9829
4053.0667 | 361.8704 | 366.9866 | 357.2339
4054.0667 | 361.8496 | 366.6298 | 357.3669
4055.0667 | 361.4022 | 366.5974 | 357.1472
4056.0667 | 361.0656 | 367.06 | 356.6085
4057.0667 | 361.0337 | 366.8717 | 356.5192
4058.0667 | 361.1352 | 366.8603 | 356.3451
4059.0667 | 361.3299 | 366.5744 | 356.752
4060.0667 | 361.4279 | 366.2433 | 356.4504
4061.0667 | 361.3268 | 366.6461 | 356.7244
4062.0667 | 361.3745 | 366.8128 | 357.0036
4063.0667 | 361.7231 | 367.1648 | 357.587
4064.0667 | 362.2014 | 368.4733 | 357.3988
4065.0667 | 362.0028 | 369.2477 | 357.0765
4066.0667 | 362.972 | 369.1348 | 356.6669
4067.0667 | 363.1297 | 368.6686 | 357.8645
4068.0667 | 362.8792 | 368.398 | 357.4678
4069.0667 | 362.6699 | 367.8607 | 357.2084
4070.0667 | 362.6199 | 367.8545 | 357.2156
4071.0667 | 362.2794 | 368.041 | 357.394
4072.0667 | 362.1958 | 367.71 | 357.9504
4073.0667 | 362.1268 | 368.1228 | 358.4397
4074.0667 | 362.0091 | 368.0912 | 358.1643
4075.0667 | 361.9682 | 367.912 | 358.1973
4076.0667 | 361.9049 | 367.8487 | 358.073
4077.0667 | 362.8889 | 367.4784 | 357.8564
4078.0667 | 362.8622 | 367.073 | 357.546
4079.0667 | 362.6077 | 367.6344 | 357.0742
4080.0667 | 363.3897 | 367.1328 | 356.6525
4081.0667 | 363.5799 | 366.4233 | 356.3417
4082.0667 | 363.5891 | 365.6465 | 356.1626
4083.0667 | 363.2503 | 365.4803 | 355.8916
4084.0667 | 363.0442 | 365.7205 | 356.473
4085.0667 | 362.7065 | 366.0669 | 356.6791
4086.0667 | 363.5159 | 367.4284 | 356.5648
4087.0667 | 363.5634 | 367.5531 | 357.4051
4088.0667 | 363.4836 | 367.8549 | 357.4401
4089.0667 | 363.4264 | 368.7944 | 357.6746
4090.0667 | 363.473 | 369.0727 | 357.6893
4091.0667 | 363.6844 | 369.0488 | 357.6484
4092.0667 | 363.995 | 368.983 | 357.8782
4093.0667 | 364.0067 | 369.1165 | 357.8526
4094.0667 | 363.8687 | 369.1916 | 357.7138
4095.0667 | 363.6814 | 369.2702 | 357.566
4096.0667 | 363.4954 | 369.3521 | 357.5485
4097.0667 | 363.213 | 368.9981 | 357.2269
4098.0667 | 362.913 | 368.7075 | 358.426
4099.0667 | 362.5953 | 368.3813 | 358.1011
4100.0667 | 362.5398 | 368.5496 | 357.8417
4101.0667 | 362.5026 | 368.542 | 357.4626
4102.0667 | 362.2836 | 368.8044 | 357.4979
4103.0667 | 362.027 | 368.6434 | 357.1973
4104.0667 | 361.8298 | 368.6706 | 356.7645
4105.0667 | 361.6323 | 368.685 | 356.9849
4106.0667 | 361.3048 | 368.3422 | 356.7692
4107.0667 | 361.2876 | 367.9973 | 356.6373
4108.0667 | 362.0266 | 368.0668 | 356.7646
4109.0667 | 362.3429 | 368.074 | 356.9033
4110.0667 | 362.5246 | 368.2013 | 356.8325
4111.0667 | 362.6721 | 368.8872 | 356.7094
4112.0667 | 363.448 | 369.1952 | 356.6267
4113.0667 | 364.1103 | 369.7819 | 357.5105
4114.0667 | 364.5654 | 369.8671 | 357.6587
4115.0667 | 364.7053 | 370.232 | 357.9367
4116.0667 | 364.9357 | 370.6616 | 358.0471
4117.0667 | 364.9951 | 370.9971 | 358.4829
4118.0667 | 364.8665 | 371.3051 | 358.5338
4119.0667 | 365.0215 | 371.4266 | 358.4998
4120.0667 | 365.5503 | 372.1759 | 358.3004
4121.0667 | 365.1457 | 371.5983 | 357.9619
4122.0667 | 364.8053 | 371.2639 | 357.5163
4123.0667 | 364.4161 | 370.7416 | 357.3259
4124.0667 | 364.064 | 370.1251 | 357.423
4125.0667 | 364.1494 | 369.4849 | 357.109
4126.0667 | 364.1519 | 369.6188 | 356.7378
4127.0667 | 364.1189 | 369.7381 | 357.4625
4128.0667 | 364.4205 | 369.844 | 357.3883
4129.0667 | 364.4232 | 369.8707 | 357.5804
4130.0667 | 364.6224 | 369.8946 | 357.9309
4131.0667 | 365.7236 | 370.0531 | 358.1089
4132.0667 | 366.0728 | 370.2619 | 358.0014
4133.0667 | 366.2567 | 370.4037 | 358.2161
4134.0667 | 366.1679 | 370.8809 | 358.5
4135.0667 | 366.3834 | 370.7493 | 358.2666
4136.0667 | 365.8998 | 370.2278 | 357.9245
4137.0667 | 365.5347 | 369.671 | 358.1517
4138.0667 | 365.0664 | 369.6859 | 357.8335
4139.0667 | 364.576 | 369.4908 | 357.5545
4140.0667 | 364.355 | 369.4176 | 357.456
4141.0667 | 364.4308 | 369.5023 | 357.2966
4142.0667 | 363.8755 | 369.334 | 358.4445
4143.0667 | 363.734 | 368.9 | 358.1832
4144.0667 | 363.4691 | 368.315 | 357.6823
4145.0667 | 363.2476 | 368.0621 | 357.4276
4146.0667 | 363.459 | 367.7956 | 357.5335
4147.0667 | 363.493 | 368.0604 | 357.4297
4148.0667 | 364.0479 | 368.9571 | 357.8843
4149.0667 | 364.1277 | 369.4287 | 358.0024
4150.0667 | 363.9717 | 369.7583 | 358.4624
4151.0667 | 364.1696 | 370.0358 | 358.761
4152.0667 | 364.4977 | 370.7911 | 358.5607
4153.0667 | 364.7929 | 371.0954 | 358.4514
4154.0667 | 364.8301 | 371.056 | 358.3239
4155.0667 | 364.8594 | 370.5715 | 358.1657
4156.0667 | 364.6955 | 370.2508 | 358.7242
4157.0667 | 364.6885 | 369.7292 | 358.3456
4158.0667 | 364.751 | 369.9014 | 357.984
4159.0823 | 364.4677 | 369.7707 | 357.7229
4160.0667 | 364.2801 | 369.5816 | 357.5286
4161.0667 | 364.0601 | 369.7676 | 357.4564
4162.0667 | 363.8709 | 370.0511 | 357.6621
4163.0667 | 363.4953 | 369.9684 | 357.6281
4164.0667 | 363.8038 | 370.1517 | 357.6722
4165.0667 | 364.0593 | 369.8852 | 357.6639
4166.0667 | 363.7655 | 369.9447 | 357.3793
4167.0667 | 363.7614 | 369.9007 | 357.231
4168.0667 | 363.8403 | 369.9184 | 357.0923
4169.0667 | 363.9638 | 369.8705 | 357.1168
4170.0667 | 363.9257 | 369.9587 | 357.0279
4171.0667 | 363.8542 | 369.9209 | 356.9284
4172.0667 | 363.5881 | 369.9522 | 356.6276
4173.0667 | 363.518 | 369.6286 | 356.8353
4174.0667 | 363.4522 | 369.5605 | 357.0857
4175.0667 | 363.6905 | 369.2856 | 356.7116
4176.0667 | 363.9053 | 369.5024 | 356.3823
4177.0667 | 364.2806 | 369.672 | 356.2388
4178.0667 | 364.2757 | 369.6734 | 356.8019
4179.0667 | 364.0915 | 369.5868 | 356.7768
4180.0667 | 363.8206 | 369.6636 | 356.6324
4181.0667 | 363.7327 | 369.5032 | 356.4058
4182.0667 | 364.0433 | 369.555 | 356.1534
4183.0667 | 364.3254 | 369.5574 | 356.5742
4184.0667 | 364.2835 | 369.2419 | 356.8394
4185.0667 | 364.1654 | 369.1026 | 356.6138
4186.0667 | 364.1261 | 369.8276 | 356.1992
4187.0667 | 364.1089 | 369.3789 | 356.1517
4188.0667 | 364.0249 | 369.1456 | 356.1356
4189.0667 | 363.9746 | 369.1604 | 355.8666
4190.0667 | 364.0929 | 368.9875 | 355.4475
4191.0667 | 364.4524 | 368.6114 | 354.89
4192.0667 | 364.2477 | 368.1798 | 354.4466
4193.0667 | 364.052 | 367.9418 | 354.1838
4194.0667 | 364.7028 | 367.7692 | 354.5291
4195.0667 | 365.0634 | 367.9465 | 355.2831
4196.0667 | 365.268 | 367.9645 | 355.512
4197.0823 | 365.4403 | 368.4974 | 356.2822
4198.0667 | 365.9371 | 368.6004 | 356.5546
4199.0823 | 365.9624 | 368.8787 | 357.5092
4200.0667 | 365.6618 | 368.6627 | 358.0204
4201.0667 | 365.1652 | 368.3313 | 357.948
4202.0667 | 364.6837 | 368.6272 | 358.1949
4203.0667 | 364.4608 | 368.1862 | 357.7669
4204.0667 | 364.0292 | 367.774 | 357.2021
4205.0667 | 363.8893 | 367.2915 | 357.0882
4206.0667 | 363.5394 | 366.7028 | 356.6236
4207.0667 | 363.48 | 367.2159 | 356.8278
4208.0667 | 364.0707 | 367.1402 | 357.1413
4209.0667 | 364.214 | 367.8171 | 356.7666
4210.0667 | 364.2773 | 367.5964 | 356.6171
4211.0667 | 364.7021 | 367.7578 | 356.355
4212.0667 | 364.9451 | 367.5594 | 356.1905
4213.0667 | 364.929 | 367.4584 | 356.1127
4214.0667 | 364.6952 | 367.5692 | 355.9527
4215.0667 | 364.3975 | 367.434 | 355.839
4216.0667 | 364.0791 | 367.4125 | 355.4848
4217.0667 | 363.6643 | 367.3243 | 355.6105
4218.0667 | 363.684 | 367.3757 | 355.6006
4219.0667 | 363.5435 | 367.3134 | 356.0856
4220.0667 | 363.2506 | 367.8456 | 356.4752
4221.0667 | 363.3216 | 367.6343 | 356.201
4222.0667 | 363.2286 | 367.4996 | 356.1042
4223.0667 | 363.1453 | 367.2552 | 355.9849
4224.0667 | 362.9032 | 367.3517 | 356.3457
4225.0667 | 362.6728 | 368.7921 | 356.5152
4226.0667 | 362.5729 | 368.8117 | 356.9243
4227.0823 | 362.6286 | 368.8525 | 357.8151
4228.0667 | 362.3624 | 368.4761 | 357.6537
4229.0667 | 362.1809 | 368.3593 | 357.5187
4230.0667 | 362.3192 | 368.3025 | 357.2427
4231.0667 | 362.0497 | 367.9345 | 356.8045
4232.0667 | 361.9525 | 368.094 | 356.6406
4233.0667 | 362.4817 | 367.694 | 356.3921
4234.0667 | 363.7098 | 367.2361 | 356.1873
4235.0667 | 363.7612 | 367.1394 | 355.8304
4236.0667 | 363.539 | 367.2293 | 355.6445
4237.0667 | 363.3257 | 367.5602 | 356.4467
4238.0667 | 363.075 | 367.9203 | 356.56
4239.0667 | 362.934 | 367.8802 | 356.8549
4240.0667 | 362.8708 | 367.9983 | 357.7082
4241.0667 | 362.9545 | 368.6246 | 357.8514
4242.0667 | 363.2785 | 369.2826 | 358.0027
4243.0667 | 363.5116 | 369.7559 | 358.3875
4244.0823 | 363.4804 | 370.121 | 358.4011
4245.0667 | 363.6554 | 370.2174 | 358.5635
4246.0667 | 363.5939 | 370.2453 | 358.5254
4247.0667 | 363.8071 | 370.2363 | 358.4156
4248.0667 | 363.7799 | 370.1113 | 358.5858
4249.0667 | 363.9 | 370.2994 | 358.6356
4250.0667 | 363.8124 | 370.001 | 358.6811
4251.0667 | 363.5835 | 370.0394 | 359.1062
4252.0667 | 364.0322 | 370.8082 | 359.1126
4253.0667 | 363.8819 | 371.9306 | 358.8143
4254.0667 | 363.7176 | 371.5463 | 358.4222
4255.0667 | 363.4214 | 372.2916 | 358.1094
4256.0667 | 363.2355 | 372.0819 | 357.9714
4257.0823 | 362.9005 | 372.43 | 357.745
4258.0667 | 362.5877 | 371.6458 | 357.5886
4259.0823 | 362.5787 | 371.0195 | 357.2561
4260.0667 | 362.7121 | 370.7765 | 357.5406
4261.0667 | 362.9047 | 370.4895 | 357.3896
4262.0667 | 362.7809 | 371.1849 | 357.3768
4263.0667 | 363.2733 | 371.2778 | 357.5412
4264.0667 | 363.9244 | 371.5914 | 357.7505
4265.0667 | 363.9753 | 371.6966 | 357.4911
4266.0667 | 363.8514 | 371.3696 | 357.6157
4267.0667 | 363.7469 | 371.3984 | 357.4874
4268.0823 | 363.5422 | 371.068 | 357.2506
4269.0667 | 363.5648 | 370.8791 | 357.0799
4270.0667 | 363.3073 | 370.6411 | 356.8405
4271.0823 | 363.0637 | 371.1653 | 357.3991
4272.0823 | 363.1383 | 371.3054 | 357.2675
4273.0667 | 363.2803 | 371.5874 | 357.0159
4274.0823 | 362.9059 | 371.3018 | 356.9699
4275.0667 | 362.6668 | 371.0932 | 356.6128
4276.0667 | 362.3885 | 371.6888 | 356.6373
4277.0823 | 362.2759 | 371.4014 | 357.0726
4278.0667 | 362.2102 | 370.7843 | 357.1779
4279.0667 | 361.9606 | 370.2167 | 357.0124
4280.0667 | 361.803 | 369.768 | 357.0132
4281.0667 | 361.5781 | 370.1254 | 356.763
4282.0667 | 361.2331 | 370.6348 | 356.5778
4283.0667 | 361.9092 | 370.5465 | 356.9077
4284.0667 | 362.3436 | 370.472 | 356.6005
4285.0667 | 362.4169 | 370.2186 | 356.3994
4286.0667 | 362.6126 | 369.8735 | 356.396
4287.0667 | 362.6607 | 369.7559 | 356.3461
4288.0667 | 362.807 | 369.6564 | 356.1916
4289.0667 | 363.3265 | 369.7167 | 356.2221
4290.0667 | 363.4747 | 369.8895 | 356.4257
4291.0667 | 363.4804 | 370.3581 | 356.6732
4292.0667 | 363.8187 | 370.332 | 357.2639
4293.0667 | 363.6771 | 370.3633 | 357.1282
4294.0667 | 363.7067 | 370.4591 | 357.027
4295.0667 | 363.6562 | 370.059 | 357.0093
4296.0667 | 363.437 | 369.7227 | 357.1746
4297.0667 | 363.2625 | 369.7188 | 357.0048
4298.0667 | 363.0154 | 370.1723 | 356.946
4299.0667 | 362.9096 | 370.026 | 356.6388
4300.0667 | 363.0304 | 369.792 | 356.4003
4301.0667 | 363.2613 | 369.7551 | 356.2632
4302.0979 | 363.289 | 369.7106 | 356.4161
4303.0667 | 363.1553 | 369.8643 | 356.299
4304.0667 | 363.2041 | 370.1331 | 356.7041
4305.0667 | 363.2745 | 370.1239 | 357.6097
4306.0667 | 363.6573 | 370.5813 | 357.7707
4307.0667 | 363.8766 | 370.6002 | 357.8868
4308.0667 | 363.7072 | 370.745 | 357.6912
4309.0667 | 363.7663 | 372.1632 | 358.0395
4310.0667 | 363.9782 | 371.6897 | 358.0508
4311.0667 | 364.0487 | 371.149 | 358.4522
4312.0667 | 363.7138 | 370.7813 | 359.0019
4313.0667 | 363.3831 | 370.5541 | 358.6364
4314.0667 | 363.667 | 370.0062 | 358.1202
4315.0667 | 363.4225 | 369.4795 | 357.6632
4316.0667 | 363.2077 | 368.9667 | 357.5508
4317.0823 | 362.7857 | 368.8488 | 357.3914
4318.0667 | 362.5387 | 369.0637 | 357.1862
4319.0667 | 362.7994 | 369.0007 | 357.1374
4320.0667 | 363.0368 | 368.9905 | 357.1631
4321.0667 | 363.1789 | 369.0534 | 357.4102
4322.0667 | 363.5664 | 369.4221 | 357.6649
4323.0667 | 363.9066 | 369.6814 | 358.3117
4324.0667 | 364.4165 | 369.8833 | 358.7887
4325.0667 | 364.8768 | 370.1092 | 358.9717
4326.0667 | 365.3157 | 370.9265 | 359.4975
4327.0667 | 365.4489 | 370.8516 | 359.8858
4328.0667 | 365.8082 | 371.0444 | 359.9563
4329.0667 | 366.452 | 371.3979 | 359.9772
4330.0667 | 366.7168 | 371.6422 | 359.8465
4331.0667 | 366.7549 | 371.6111 | 360.0104
4332.0667 | 366.6688 | 371.3983 | 359.5777
4333.0667 | 366.4358 | 371.4579 | 359.3043
4334.0667 | 366.4529 | 371.309 | 359.6746
4335.0667 | 366.4384 | 371.3079 | 359.6817
4336.0667 | 366.5189 | 370.9095 | 359.4209
4337.0667 | 366.3789 | 370.7027 | 359.096
4338.0667 | 366.315 | 370.8567 | 359.0848
4339.0667 | 366.48 | 370.7891 | 358.8599
4340.0667 | 366.5142 | 371.2007 | 358.9655
4341.0667 | 366.8381 | 371.4005 | 359.49
4342.0667 | 366.8508 | 371.1464 | 359.9359
4343.0667 | 366.6123 | 371.0503 | 359.9681
4344.0667 | 366.2355 | 370.8617 | 359.5849
4345.0667 | 365.9854 | 370.8784 | 359.3649
4346.0667 | 365.7344 | 371.0987 | 359.1206
4347.0667 | 365.3678 | 370.8212 | 358.838
4348.0667 | 365.3306 | 371.0758 | 359.2798
4349.0667 | 365.9736 | 371.6385 | 360.0028
4350.0667 | 366.2449 | 372.1472 | 360.5732
4351.0667 | 366.5281 | 372.4567 | 360.9049
4352.0667 | 367.0523 | 372.3458 | 361.4374
4353.0667 | 367.1531 | 372.1101 | 361.1051
4354.0667 | 367.0656 | 372.0282 | 361.193
4355.0667 | 366.7219 | 371.5603 | 361.1122
4356.0667 | 366.8 | 371.5825 | 361.9642
4357.0667 | 366.9746 | 371.732 | 362.1238
4358.0667 | 366.8733 | 371.8615 | 361.8648
4359.0667 | 366.5737 | 372.1348 | 362.0375
4360.0667 | 366.5168 | 372.0448 | 361.8457
4361.0667 | 366.1554 | 371.9989 | 361.9511
4362.0667 | 366.1218 | 372.3178 | 361.9779
4363.0667 | 365.9088 | 372.282 | 361.6922
4364.0667 | 365.9803 | 372.8933 | 361.5724
4365.0667 | 365.8677 | 373.1389 | 362.2698
4366.0667 | 365.6343 | 373.0637 | 361.7363
4367.0667 | 365.7208 | 373.1202 | 361.5779
4368.0667 | 365.8483 | 373.109 | 361.2509
4369.0667 | 365.9071 | 372.634 | 361.0849
4370.0667 | 366.0326 | 372.2611 | 360.6471
4371.0667 | 365.9187 | 372.4047 | 360.8166
4372.0667 | 366.2631 | 372.4564 | 360.6582
4373.0667 | 366.4644 | 372.2794 | 360.4394
4374.0667 | 366.321 | 372.0234 | 360.5194
4375.0667 | 366.2219 | 372.1905 | 360.9658
4376.0667 | 365.9797 | 371.7521 | 360.6599
4377.0667 | 365.6768 | 371.3279 | 360.5069
4378.0667 | 365.4077 | 370.817 | 360.2539
4379.0667 | 365.5279 | 371.2713 | 359.8269
4380.0667 | 365.5605 | 370.5968 | 359.6353
4381.0667 | 365.7044 | 370.6165 | 360.0616
4382.0667 | 365.6891 | 370.3617 | 359.8057
4383.0667 | 365.7375 | 369.9512 | 360.281
4384.0667 | 365.7151 | 369.9658 | 360.003
4385.0667 | 365.6891 | 370.0508 | 360.3905
4386.0667 | 365.7316 | 370.8874 | 360.5235
4387.0667 | 365.3544 | 370.6528 | 360.5788
4388.0667 | 364.9402 | 370.4208 | 360.1353
4389.0667 | 364.74 | 370.0397 | 359.5811
4390.0667 | 364.3663 | 369.842 | 359.0282
4391.0667 | 364.2997 | 369.5252 | 358.511
4392.0667 | 364.1734 | 369.1385 | 358.2718
4393.0667 | 364.1527 | 370.0913 | 359.6533
4394.0667 | 364.051 | 370.0379 | 359.8228
4395.0667 | 364.6228 | 370.0674 | 359.5395
4396.0667 | 364.6144 | 370.077 | 359.1282
4397.0667 | 364.3972 | 370.0397 | 358.7276
4398.0667 | 364.1739 | 369.8386 | 358.3765
4399.0667 | 364.5097 | 369.616 | 358.0703
4400.0667 | 364.5519 | 369.5187 | 357.8261
4401.0667 | 364.6151 | 370.4093 | 357.812
4402.0667 | 364.5869 | 370.7864 | 358.5377
4403.0667 | 364.6513 | 370.947 | 358.7555
4404.0667 | 364.5483 | 371.4184 | 358.7093
4405.0667 | 364.4133 | 371.4239 | 358.6757
4406.0667 | 364.3379 | 371.1741 | 358.3257
4407.0823 | 364.46 | 371.3017 | 358.0213
4408.0667 | 364.5599 | 371.3682 | 358.0531
4409.0667 | 364.5097 | 371.6155 | 358.0431
4410.0667 | 365.3852 | 372.4015 | 358.2957
4411.0667 | 365.6819 | 372.4623 | 358.0799
4412.0667 | 365.7682 | 372.0871 | 357.8491
4413.0667 | 365.6586 | 372.1434 | 357.7147
4414.0667 | 365.7166 | 371.7974 | 357.5099
4415.0667 | 365.4377 | 371.2974 | 357.1603
4416.0667 | 365.2314 | 370.942 | 357.0249
4417.0667 | 365.4506 | 370.8782 | 356.6941
4418.0667 | 366.2626 | 371.4587 | 356.936
4419.0823 | 366.2094 | 371.0802 | 357.3532
4420.0667 | 366.2389 | 370.7519 | 357.3465
4421.0667 | 366.631 | 370.6209 | 357.1904
4422.0667 | 366.8931 | 370.7294 | 357.1695
4423.0667 | 366.8296 | 370.8511 | 357.8973
4424.0667 | 366.6356 | 371.0541 | 358.4353
4425.0667 | 366.3505 | 370.6292 | 358.8236
4426.0667 | 366.3816 | 370.3889 | 358.6614
4427.0667 | 366.4519 | 370.4369 | 358.5183
4428.0667 | 366.4246 | 370.6125 | 358.169
4429.0667 | 366.6417 | 371.142 | 358.4603
4430.0667 | 366.8442 | 371.7779 | 358.8418
4431.0667 | 366.8423 | 372.2878 | 359.2045
4432.0667 | 367.2012 | 372.2984 | 359.5278
4433.0667 | 367.808 | 372.0601 | 359.2138
4434.0667 | 367.8892 | 372.359 | 358.9957
4435.0667 | 367.7043 | 371.8646 | 359.0663
4436.0667 | 367.7348 | 372.1755 | 359.0148
4437.0823 | 367.6922 | 371.5345 | 359.142
4438.0667 | 367.5095 | 371.493 | 359.4163
4439.0667 | 367.4686 | 371.8292 | 359.9279
4440.0667 | 367.6301 | 371.8061 | 360.486
4441.0667 | 367.7201 | 371.9904 | 360.2848
4442.0667 | 367.8067 | 372.8361 | 360.54
4443.0667 | 367.7137 | 372.6029 | 361.0958
4444.0667 | 367.4027 | 372.1567 | 360.9012
4445.0667 | 367.119 | 371.5666 | 360.4933
4446.0667 | 366.7289 | 370.9711 | 360.0747
4447.0667 | 366.5047 | 370.72 | 359.7203
4448.0667 | 366.5468 | 370.6084 | 359.2762
4449.0667 | 366.3984 | 370.4475 | 358.8789
4450.0667 | 366.6582 | 370.6086 | 358.7573
4451.0667 | 366.6907 | 370.8938 | 359.4104
4452.0667 | 366.3393 | 370.3863 | 359.2261
4453.0667 | 365.9789 | 370.1316 | 359.0317
4454.0667 | 365.5211 | 370.3837 | 359.3776
4455.0667 | 365.1395 | 370.2913 | 359.5756
4456.0667 | 365.0447 | 370.0518 | 359.2665
4457.0667 | 365.1096 | 369.8873 | 359.0754
4458.0667 | 365.4538 | 369.6039 | 358.6409
4459.0667 | 365.5284 | 369.5705 | 358.6374
4460.0667 | 365.7379 | 369.6938 | 358.6596
4461.0667 | 365.6422 | 369.6728 | 359.0591
4462.0667 | 365.3991 | 369.7465 | 359.3459
4463.0667 | 365.1399 | 369.5213 | 359.1237
4464.0667 | 364.7525 | 369.4207 | 358.8716
4465.0667 | 364.507 | 369.3719 | 358.5424
4466.0667 | 364.3025 | 369.5913 | 358.1402
4467.0667 | 364.0967 | 369.2988 | 357.9321
4468.0667 | 364.058 | 369.2049 | 357.6938
4469.0667 | 364.4616 | 370.0543 | 357.3367
4470.0667 | 364.7648 | 370.1402 | 357.3857
4471.0667 | 365.1064 | 370.229 | 358.1252
4472.0667 | 365.8938 | 371.3832 | 358.4721
4473.0667 | 366.9787 | 373.1295 | 359.1808
4474.0823 | 367.1672 | 373.3067 | 359.6947
4475.0667 | 366.8894 | 373.2809 | 359.6168
4476.0667 | 366.6078 | 372.4888 | 359.4394
4477.0667 | 366.1527 | 371.7466 | 359.3039
4478.0667 | 365.6776 | 371.5419 | 358.8006
4479.0667 | 366.1783 | 371.4537 | 358.628
4480.0667 | 366.8934 | 371.2456 | 358.2475
4481.0667 | 367.1806 | 370.9631 | 357.7866
4482.0667 | 367.279 | 370.8223 | 357.5754
4483.0667 | 367.2805 | 371.5684 | 357.7957
4484.0667 | 367.3619 | 371.8467 | 358.3627
4485.0667 | 367.3142 | 371.6023 | 358.4809
4486.0667 | 366.9068 | 371.5401 | 358.4217
4487.0667 | 367.0089 | 371.6316 | 358.3618
4488.0667 | 367.0424 | 371.696 | 358.93
4489.0667 | 366.992 | 371.6459 | 359.6878
4490.0667 | 367.1201 | 372.1083 | 359.5796
4491.0667 | 367.03 | 371.6916 | 359.4655
4492.0667 | 366.7863 | 372.0805 | 359.3528
4493.0667 | 366.3666 | 371.2665 | 359.0983
4494.0667 | 366.0557 | 371.8012 | 358.7272
4495.0667 | 366.7057 | 371.0751 | 358.3329
4496.0667 | 366.3248 | 370.8938 | 358.1889
4497.0667 | 365.933 | 370.2872 | 357.9052
4498.0667 | 365.541 | 369.8274 | 358.05
4499.0667 | 365.2156 | 369.5894 | 357.9095
4500.0667 | 365.0636 | 369.6531 | 358.1032
4501.0667 | 364.9982 | 369.368 | 358.1176
4502.0667 | 365.118 | 369.4323 | 358.5194
4503.0823 | 365.0144 | 370.0398 | 359.0249
4504.0823 | 364.9967 | 369.9651 | 359.414
4505.0667 | 364.9449 | 370.5164 | 359.1199
4506.0667 | 364.9808 | 370.5124 | 359.7722
4507.0823 | 364.7009 | 370.2228 | 359.9484
4508.0823 | 364.4782 | 370.0008 | 359.6865
4509.0823 | 364.2561 | 369.6035 | 359.4062
4510.0667 | 364.1719 | 369.316 | 359.0306
4511.0667 | 363.921 | 369.1854 | 358.7228
4512.0667 | 363.5556 | 369.1905 | 358.8653
4513.0667 | 363.2403 | 368.8581 | 359.046
4514.0667 | 363.3007 | 369.1563 | 359.3658
4515.0667 | 363.3878 | 369.3218 | 359.7054
4516.0667 | 363.1797 | 369.8916 | 359.6501
4517.0667 | 363.1187 | 370.0036 | 359.4861
4518.0667 | 363.4866 | 370.5124 | 359.5348
4519.0823 | 363.5466 | 370.9408 | 360.4739
4520.0667 | 363.546 | 370.6595 | 360.3985
4521.0667 | 363.4278 | 370.2953 | 360.1841
4522.0667 | 363.9464 | 370.0602 | 359.7733
4523.0667 | 363.8535 | 369.9343 | 360.0089
4524.0667 | 363.9386 | 369.608 | 359.9228
4525.0667 | 363.9819 | 369.1414 | 359.6065
4526.0667 | 364.5868 | 369.044 | 359.5487
4527.0667 | 364.5021 | 368.8097 | 359.4233
4528.0667 | 364.3096 | 368.7798 | 359.1928
4529.0667 | 364.1371 | 368.9966 | 358.8386
4530.0667 | 364.0585 | 368.9427 | 358.5787
4531.0667 | 364.1821 | 369.0618 | 358.5668
4532.0667 | 363.9599 | 369.1188 | 358.6928
4533.0667 | 363.7813 | 369.5061 | 358.5941
4534.0823 | 363.8283 | 369.5431 | 358.9991
4535.0667 | 363.854 | 369.7046 | 359.131
4536.0667 | 363.9688 | 369.955 | 358.7213
4537.0667 | 363.9167 | 369.9915 | 358.8063
4538.0667 | 363.8945 | 370.024 | 358.9401
4539.0667 | 364.0126 | 371.2882 | 358.9029
4540.0667 | 364.1836 | 370.7306 | 358.9505
4541.0667 | 364.7102 | 371.4416 | 358.7622
4542.0667 | 364.9275 | 371.4805 | 358.8419
4543.0667 | 364.9489 | 371.2649 | 359.0965
4544.0667 | 364.8765 | 370.8754 | 358.8207
4545.0667 | 364.6843 | 370.633 | 359.0069
4546.0667 | 364.543 | 370.8794 | 358.8651
4547.0667 | 364.7213 | 370.848 | 358.7248
4548.0667 | 364.362 | 371.3071 | 358.4054
4549.0667 | 364.1634 | 371.5142 | 358.8618
4550.0667 | 364.135 | 371.4634 | 359.1531
4551.0823 | 363.9311 | 371.5327 | 359.6373
4552.0667 | 363.8238 | 371.1719 | 359.5949
4553.0667 | 364.3097 | 371.1072 | 359.4578
4554.0667 | 364.2069 | 371.1574 | 359.4793
4555.0667 | 364.5862 | 371.1204 | 359.3592
4556.0667 | 364.7858 | 371.0895 | 359.3932
4557.0667 | 364.9932 | 371.1823 | 359.5406
4558.0667 | 365.1798 | 371.209 | 359.9475
4559.0667 | 365.219 | 370.869 | 360.0334
4560.0667 | 365.0652 | 370.4815 | 359.6978
4561.0667 | 364.7403 | 370.3827 | 359.1376
4562.0667 | 364.5026 | 370.1413 | 358.5368
4563.0667 | 364.4871 | 369.6981 | 358.0967
4564.0667 | 364.7782 | 369.4777 | 357.8728
4565.0667 | 364.9894 | 369.59 | 358.5246
4566.0667 | 365.2488 | 370.5436 | 359.3844
4567.0667 | 365.672 | 370.9345 | 359.4018
4568.0667 | 366.3616 | 371.75 | 360.0478
4569.0667 | 366.7712 | 372.4098 | 360.5534
4570.0667 | 367.1314 | 373.0344 | 360.5266
4571.0667 | 367.2455 | 373.3139 | 360.4851
4572.0667 | 367.0758 | 372.9915 | 360.6166
4573.0667 | 366.9317 | 372.8059 | 360.5797
4574.0667 | 366.795 | 372.738 | 360.92
4575.0667 | 366.4189 | 372.3194 | 361.1657
4576.0667 | 366.0878 | 372.3739 | 361.5049
4577.0667 | 365.8747 | 372.0517 | 361.152
4578.0667 | 365.7131 | 371.5053 | 360.9682
4579.0667 | 365.5901 | 371.0857 | 361.0426
4580.0667 | 365.2884 | 370.6583 | 360.6056
4581.0667 | 365.3972 | 370.4886 | 360.1406
4582.0667 | 365.2795 | 370.2054 | 359.8988
4583.0667 | 365.5441 | 370.5471 | 360.2285
4584.0667 | 365.4983 | 370.6983 | 360.5078
4585.0667 | 365.1008 | 370.8818 | 360.5201
4586.0667 | 365.1672 | 370.9471 | 360.3126
4587.0667 | 364.7209 | 370.7081 | 359.8469
4588.0667 | 364.4591 | 370.5601 | 359.3502
4589.0667 | 364.6678 | 370.641 | 359.1552
4590.0667 | 364.8314 | 370.7174 | 359.2916
4591.0667 | 364.8883 | 370.8247 | 359.1902
4592.0667 | 364.9641 | 370.8203 | 359.3029
4593.0667 | 364.9799 | 370.9442 | 359.1421
4594.0667 | 365.0699 | 370.5485 | 359.4502
4595.0667 | 364.785 | 370.5458 | 359.2114
4596.0667 | 364.5472 | 370.3638 | 359.6601
4597.0667 | 364.4314 | 370.3731 | 359.3813
4598.0667 | 364.2048 | 370.1653 | 359.4349
4599.0667 | 363.9211 | 369.8504 | 359.5752
4600.0667 | 363.932 | 369.6126 | 359.2803
4601.0667 | 363.9474 | 369.2701 | 359.03
4602.0667 | 364.3082 | 369.2062 | 359.3726
4603.0667 | 364.3796 | 369.0919 | 359.3527
4604.0667 | 364.6375 | 369.5007 | 359.1049
4605.0667 | 364.4406 | 369.5559 | 359.5711
4606.0667 | 364.4734 | 369.7626 | 359.7094
4607.0667 | 364.4744 | 369.9137 | 359.435
4608.0667 | 364.6287 | 370.2249 | 359.9637
4609.0667 | 364.5046 | 370.4905 | 359.8726
4610.0667 | 364.2372 | 370.5095 | 359.9458
4611.0667 | 364.0828 | 369.9675 | 359.844
4612.0667 | 363.7404 | 370.2735 | 359.888
4613.0667 | 363.4171 | 369.9896 | 359.8668
4614.0667 | 363.2601 | 369.9467 | 359.6339
4615.0667 | 363.1731 | 369.848 | 359.5
4616.0667 | 363.4034 | 370.1262 | 359.8324
4617.0667 | 363.6351 | 370.2663 | 359.5697
4618.0667 | 363.6827 | 370.8381 | 359.564
4619.0667 | 363.6685 | 371.0474 | 359.6192
4620.0667 | 363.5475 | 371.0858 | 359.4123
4621.0667 | 363.4802 | 371.1576 | 359.2837
4622.0667 | 363.3893 | 371.1394 | 359.1352
4623.0667 | 363.257 | 371.2052 | 359.2525
4624.0667 | 363.2794 | 371.3691 | 360.3752
4625.0667 | 363.6493 | 371.5809 | 360.4897
4626.0667 | 363.83 | 372.019 | 360.256
4627.0667 | 363.9352 | 371.9859 | 360.256
4628.0667 | 364.063 | 371.8635 | 360.0724
4629.0667 | 364.125 | 371.7911 | 360.0524
4630.0667 | 364.3768 | 371.9394 | 360.4804
4631.0667 | 365.2382 | 372.2001 | 360.448
4632.0667 | 365.8689 | 372.5139 | 360.3019
4633.0667 | 366.4079 | 372.9517 | 360.5661
4634.0667 | 366.2801 | 372.588 | 360.4232
4635.0667 | 366.3159 | 372.5487 | 360.4942
4636.0667 | 366.8556 | 372.4905 | 360.7447
4637.0667 | 366.6457 | 372.4761 | 360.7756
4638.0667 | 366.3651 | 372.6836 | 361.0171
4639.0667 | 366.1859 | 372.6894 | 361.4069
4640.0667 | 366.1583 | 373.0529 | 361.8402
4641.0667 | 366.151 | 372.8464 | 362.5916
4642.0667 | 366.2984 | 373.2293 | 363.5624
4643.0667 | 366.9278 | 375.3394 | 363.6786
4644.0667 | 367.4033 | 374.5478 | 363.615
4645.0667 | 367.8911 | 374.8206 | 363.764
4646.0667 | 367.887 | 375.4141 | 363.8646
4647.0667 | 367.8301 | 375.3789 | 363.6234
4648.0667 | 367.874 | 375.4542 | 363.875
4649.0667 | 367.7971 | 375.4352 | 364.4001
4650.0667 | 367.7934 | 375.0878 | 364.3509
4651.0667 | 367.8652 | 374.8685 | 364.4989
4652.0667 | 368.0862 | 375.3478 | 364.6499
4653.0667 | 368.1802 | 376.0607 | 364.684
4654.0667 | 368.1492 | 376.1952 | 364.402
4655.0667 | 368.3411 | 375.8922 | 364.0547
4656.0667 | 368.3189 | 375.7847 | 363.6859
4657.0667 | 368.4324 | 375.4289 | 363.5345
4658.0667 | 368.1392 | 374.7717 | 363.5164
4659.0667 | 367.7886 | 374.3331 | 363.2299
4660.0667 | 367.5439 | 373.8533 | 363.0612
4661.0667 | 367.3651 | 373.8276 | 362.5981
4662.0667 | 366.818 | 373.6678 | 362.3684
4663.0667 | 366.3464 | 373.2471 | 361.9884
4664.0667 | 366.0005 | 372.8197 | 361.9418
4665.0667 | 365.6888 | 372.3939 | 361.9372
4666.0667 | 365.5005 | 371.9209 | 362.3342
4667.0667 | 365.8761 | 371.6418 | 362.033
4668.0667 | 365.8663 | 371.3552 | 361.9971
4669.0823 | 365.5251 | 371.3914 | 361.9472
4670.0667 | 365.3047 | 371.3351 | 361.7614
4671.0667 | 365.0496 | 371.1052 | 362.6192
4672.0667 | 364.9549 | 370.604 | 362.5563
4673.0667 | 364.9303 | 370.3751 | 362.8801
4674.0667 | 365.3896 | 370.4506 | 363.2692
4675.0667 | 365.2983 | 370.2682 | 362.9576
4676.0667 | 365.3289 | 369.9807 | 362.7342
4677.0667 | 365.306 | 370.5516 | 362.1252
4678.0667 | 365.2222 | 370.395 | 361.8202
4679.0667 | 365.2633 | 370.2997 | 361.4178
4680.0667 | 365.2028 | 372.0554 | 361.3565
4681.0667 | 365.7596 | 372.0234 | 361.8514
4682.0667 | 365.8166 | 371.5747 | 361.5447
4683.0667 | 365.792 | 371.0587 | 361.2848
4684.0667 | 365.8372 | 370.7517 | 361.6545
4685.0667 | 365.5293 | 370.4195 | 361.9182
4686.0667 | 365.1209 | 370.1173 | 361.7908
4687.0667 | 364.9144 | 370.3502 | 361.5848
4688.0667 | 364.9777 | 370.2785 | 361.6141
4689.0667 | 365.115 | 370.5167 | 361.9369
4690.0667 | 365.2944 | 370.6993 | 361.681
4691.0667 | 365.2199 | 370.5856 | 361.702
4692.0667 | 365.2296 | 370.3546 | 361.5426
4693.0667 | 365.1926 | 370.5828 | 361.2606
4694.0667 | 365.0658 | 370.9292 | 360.9005
4695.0667 | 365.1936 | 371.1334 | 360.8388
4696.0667 | 365.0207 | 371.0089 | 361.0315
4697.0667 | 365.023 | 370.8089 | 360.794
4698.0667 | 365.2105 | 370.5331 | 360.632
4699.0667 | 365.1692 | 370.6062 | 360.3935
4700.0667 | 365.3402 | 371.1135 | 360.255
4701.0667 | 365.4414 | 371.0242 | 360.4548
4702.0667 | 365.4144 | 370.7749 | 360.1956
4703.0667 | 365.6408 | 371.2808 | 360.0412
4704.0667 | 365.6258 | 371.2103 | 360.0348
4705.0667 | 365.5305 | 371.5978 | 359.9653
4706.0667 | 365.1456 | 371.5682 | 360.3223
4707.0667 | 365.0408 | 371.5908 | 360.116
4708.0667 | 365.0163 | 371.9799 | 360.0308
4709.0823 | 365.081 | 371.6223 | 359.9062
4710.0667 | 365.0574 | 371.4884 | 359.6772
4711.0667 | 365.0113 | 371.645 | 360.2843
4712.0667 | 365.0608 | 371.7643 | 360.4512
4713.0667 | 365.5947 | 371.9458 | 360.714
4714.0667 | 365.647 | 371.9803 | 360.558
4715.0667 | 365.6975 | 372.1771 | 360.6793
4716.0667 | 365.808 | 372.6032 | 361.9675
4717.0667 | 365.7623 | 372.608 | 362.0389
4718.0667 | 365.8468 | 372.6434 | 361.8319
4719.0667 | 366.0349 | 373.6815 | 361.9389
4720.0667 | 366.2283 | 373.971 | 361.7542
4721.0667 | 366.3781 | 374.0446 | 361.4318
4722.0667 | 366.5216 | 374.2767 | 361.1795
4723.0667 | 366.8771 | 374.2112 | 361.4492
4724.0667 | 366.9964 | 373.9511 | 361.1667
4725.0667 | 367.0001 | 373.5993 | 361.4719
4726.0667 | 366.9376 | 373.3783 | 361.2534
4727.0667 | 366.7096 | 373.327 | 361.0348
4728.0667 | 366.4654 | 373.1718 | 360.9325
4729.0667 | 366.3311 | 373.1089 | 361.257
4730.0667 | 366.0856 | 372.8832 | 361.4421
4731.0667 | 365.9128 | 372.694 | 361.7154
4732.0667 | 365.8419 | 372.7484 | 361.8692
4733.0667 | 365.6758 | 372.6848 | 362.2219
4734.0667 | 366.462 | 372.7635 | 362.0914
4735.0667 | 366.3936 | 372.2474 | 361.8545
4736.0667 | 366.3326 | 372.6398 | 362.172
4737.0667 | 366.3897 | 372.6902 | 362.5323
4738.0667 | 366.3239 | 372.6569 | 362.6506
4739.0667 | 366.3015 | 372.7364 | 362.4227
4740.0667 | 366.3981 | 372.6616 | 362.1668
4741.0667 | 366.4144 | 373.0401 | 361.9801
4742.0667 | 366.2396 | 372.7385 | 361.7381
4743.0667 | 365.9403 | 372.9962 | 361.6688
4744.0667 | 365.6469 | 372.9502 | 361.9112
4745.0667 | 365.4367 | 372.7428 | 361.7651
4746.0667 | 365.4118 | 372.6099 | 361.2841
4747.0667 | 365.4652 | 372.433 | 361.2246
4748.0667 | 365.8278 | 372.4667 | 361.5932
4749.0823 | 366.3777 | 372.3513 | 361.5442
4750.0667 | 366.9444 | 372.2056 | 361.5471
4751.0667 | 367.6998 | 372.1404 | 362.1542
4752.0667 | 368.1911 | 372.4401 | 362.5458
4753.0667 | 368.3176 | 372.7566 | 363.2862
4754.0667 | 368.8408 | 372.8806 | 363.3855
4755.0667 | 368.9993 | 372.819 | 363.3746
4756.0667 | 368.9653 | 372.9802 | 364.0734
4757.0667 | 369.0811 | 373.0757 | 363.9457
4758.0667 | 369.2848 | 373.2861 | 364.5817
4759.0667 | 369.2596 | 373.2373 | 364.5801
4760.0667 | 369.3534 | 374.4913 | 364.8692
4761.0667 | 369.1683 | 375.6898 | 364.8913
4762.0667 | 368.9118 | 376.2651 | 365.7164
4763.0667 | 368.4915 | 375.8109 | 365.1519
4764.0667 | 368.1883 | 375.35 | 364.9261
4765.0667 | 367.8957 | 374.9437 | 364.4817
4766.0667 | 367.5315 | 374.8373 | 364.0985
4767.0667 | 367.5973 | 374.6686 | 364.3485
4768.0667 | 367.8444 | 374.5487 | 364.13
4769.0667 | 367.7499 | 374.3572 | 364.8414
4770.0667 | 367.5451 | 374.0212 | 364.6217
4771.0667 | 367.4686 | 374.253 | 364.3827
4772.0667 | 367.607 | 373.8751 | 364.1417
4773.0667 | 367.749 | 373.791 | 363.7593
4774.0667 | 368.2631 | 374.033 | 363.9891
4775.0667 | 368.1978 | 374.0606 | 364.1444
4776.0667 | 368.0086 | 373.911 | 363.6305
4777.0667 | 367.8215 | 374.2169 | 363.3657
4778.0667 | 367.6553 | 373.6191 | 363.1302
4779.0667 | 367.3688 | 373.2905 | 362.786
4780.0667 | 367.0611 | 373.5393 | 362.3729
4781.0667 | 366.9955 | 373.4184 | 361.9879
4782.0667 | 366.7196 | 373.1755 | 361.5582
4783.0667 | 366.4761 | 372.9101 | 361.4236
4784.0667 | 366.6985 | 372.8117 | 361.4214
4785.0667 | 366.5459 | 372.544 | 361.522
4786.0667 | 366.376 | 372.5855 | 361.1899
4787.0667 | 366.3191 | 372.2086 | 360.9276
4788.0667 | 367.2441 | 371.8392 | 360.6536
4789.0667 | 367.0241 | 371.4148 | 360.3198
4790.0667 | 366.9192 | 371.1112 | 360.4367
4791.0667 | 366.6526 | 370.9978 | 360.449
4792.0667 | 366.3797 | 370.8286 | 360.5291
4793.0667 | 366.2491 | 370.831 | 360.235
4794.0823 | 365.9958 | 370.7315 | 360.1155
4795.0667 | 365.8513 | 371.7241 | 360.9038
4796.0667 | 365.5158 | 371.9344 | 361.0761
4797.0667 | 365.4891 | 372.1438 | 361.3317
4798.0667 | 365.6885 | 372.683 | 361.394
4799.0667 | 365.4831 | 372.9415 | 361.2823
4800.0667 | 365.2052 | 372.861 | 361.1362
4801.0667 | 364.9324 | 373.087 | 360.9802
4802.0667 | 364.7 | 372.714 | 361.3203
4803.0667 | 364.4087 | 372.3612 | 361.5439
4804.0667 | 364.5181 | 372.3947 | 361.4399
4805.0667 | 364.8395 | 372.1309 | 361.3881
4806.0667 | 364.6501 | 371.8917 | 361.3551
4807.0667 | 364.7557 | 371.8383 | 361.1708
4808.0667 | 364.6331 | 371.3482 | 360.9296
4809.0823 | 364.5456 | 371.0778 | 360.8366
4810.0667 | 364.5549 | 370.677 | 360.6607
4811.0667 | 364.6353 | 370.2589 | 360.4732
4812.0667 | 364.6738 | 369.637 | 360.4078
4813.0667 | 364.8962 | 369.9904 | 360.2928
4814.0667 | 365.1674 | 370.8306 | 360.2565
4815.0667 | 365.352 | 370.691 | 360.4467
4816.0667 | 365.2445 | 371.1799 | 360.3027
4817.0667 | 365.4707 | 371.4752 | 360.1321
4818.0667 | 365.6566 | 371.297 | 359.9329
4819.0667 | 365.7159 | 371.3392 | 359.9565
4820.0667 | 366.0871 | 371.7616 | 360.3391
4821.0667 | 366.9627 | 372.9529 | 360.8134
4822.0667 | 366.9865 | 372.8911 | 360.8708
4823.0667 | 367.0096 | 373.7528 | 360.8173
4824.0667 | 367.089 | 374.1838 | 361.1603
4825.0667 | 366.9774 | 374.0822 | 361.8675
4826.0667 | 366.9775 | 374.1081 | 362.0447
4827.0667 | 366.9678 | 373.7421 | 361.8979
4828.0667 | 367.0292 | 373.3926 | 361.8231
4829.0667 | 366.98 | 373.1916 | 361.8239
4830.0667 | 366.7534 | 373.4091 | 361.5493
4831.0667 | 366.4829 | 373.8229 | 361.4063
4832.0667 | 366.3938 | 373.646 | 361.172
4833.0667 | 366.3762 | 373.6309 | 361.746
4834.0667 | 367.1755 | 373.8937 | 362.0839
4835.0667 | 367.9567 | 374.1597 | 362.7288
4836.0667 | 368.0874 | 374.4114 | 362.8692
4837.0667 | 367.8423 | 374.9441 | 362.6697
4838.0667 | 367.6803 | 374.6793 | 362.6673
4839.0667 | 368.0069 | 375.1484 | 362.5885
4840.0667 | 367.9421 | 375.388 | 362.621
4841.0667 | 367.7341 | 375.369 | 362.836
4842.0667 | 367.7888 | 375.3771 | 362.8446
4843.0667 | 367.7407 | 375.8736 | 363.9112
4844.0667 | 367.6403 | 375.6552 | 364.8578
4845.0667 | 367.8145 | 375.4465 | 364.4903
4846.0667 | 368.4244 | 375.2156 | 364.8651
4847.0667 | 368.726 | 375.6077 | 365.0085
4848.0667 | 368.6565 | 375.8374 | 364.5654
4849.0823 | 368.443 | 375.815 | 364.3714
4850.0667 | 368.3864 | 375.8467 | 364.1764
4851.0667 | 368.6772 | 375.5346 | 363.9807
4852.0667 | 369.5236 | 375.206 | 363.9909
4853.0667 | 369.661 | 375.5086 | 364.6202
4854.0667 | 369.7038 | 375.9157 | 365.487
4855.0667 | 370.2156 | 376.4231 | 365.11
4856.0667 | 370.694 | 377.7387 | 365.1595
4857.0667 | 370.5268 | 377.4804 | 364.8114
4858.0667 | 370.3065 | 377.2162 | 364.8384
4859.0667 | 370.1844 | 377.1346 | 364.623
4860.0667 | 370.3024 | 376.6195 | 364.5979
4861.0667 | 370.1007 | 376.2788 | 365.5195
4862.0667 | 369.9952 | 376.1197 | 365.4254
4863.0667 | 370.4918 | 376.4101 | 365.9688
4864.0667 | 370.8369 | 376.4002 | 366.0582
4865.0667 | 370.8747 | 377.4384 | 366.3396
4866.0667 | 370.7943 | 377.6135 | 366.267
4867.0667 | 370.6837 | 377.6489 | 366.3486
4868.0667 | 370.6462 | 376.9934 | 365.7073
4869.0667 | 370.5714 | 376.4971 | 365.5052
4870.0667 | 370.6476 | 376.288 | 365.8948
4871.0667 | 370.5292 | 376.256 | 365.7471
4872.0667 | 370.5394 | 376.2241 | 365.5009
4873.0667 | 370.2416 | 376.3756 | 365.6436
4874.0667 | 370.1487 | 376.4231 | 365.1693
4875.0667 | 369.9293 | 376.3393 | 364.8971
4876.0667 | 369.4519 | 376.5429 | 364.5754
4877.0667 | 369.8818 | 376.3166 | 364.2288
4878.0667 | 369.8239 | 376.1871 | 363.7702
4879.0667 | 369.6002 | 375.8852 | 363.7512
4880.0667 | 369.2704 | 375.9863 | 363.3546
4881.0667 | 369.4628 | 376.1151 | 363.1837
4882.0667 | 369.4439 | 375.8999 | 363.9909
4883.0667 | 369.1973 | 375.6714 | 364.5053
4884.0667 | 369.0072 | 375.9863 | 364.6381
4885.0667 | 368.799 | 375.8053 | 364.4169
4886.0667 | 369.4748 | 375.7693 | 365.1344
4887.0667 | 369.8664 | 375.3571 | 365.4898
4888.0667 | 369.9832 | 375.3316 | 365.4828
4889.0667 | 370.0071 | 375.5435 | 365.0365
4890.0667 | 369.7608 | 375.4454 | 364.9759
4891.0667 | 369.5874 | 375.5488 | 364.484
4892.0667 | 369.3734 | 375.64 | 364.1657
4893.0667 | 369.3792 | 375.771 | 364.2544
4894.0667 | 369.6483 | 375.8499 | 364.7486
4895.0667 | 370.0681 | 376.0531 | 365.4517
4896.0667 | 370.2976 | 376.0926 | 365.7263
4897.0667 | 370.0636 | 376.0676 | 365.8998
4898.0667 | 369.8436 | 375.7358 | 366.8182
4899.0667 | 369.7216 | 375.5685 | 367.1101
4900.0667 | 369.4134 | 375.4523 | 367.633
4901.0667 | 369.11 | 375.3314 | 367.3837
4902.0667 | 368.9362 | 375.1492 | 367.2455
4903.0667 | 368.7222 | 375.342 | 367.0084
4904.0667 | 368.5246 | 374.8766 | 367.7903
4905.0667 | 368.4208 | 374.253 | 368.0086
4906.0667 | 368.2712 | 374.3119 | 367.7565
4907.0667 | 368.1845 | 374.3534 | 367.6288
4908.0667 | 368.0812 | 374.3779 | 367.9082
4909.0667 | 367.9159 | 374.8221 | 367.6388
4910.0667 | 367.8786 | 375.4497 | 367.7619
4911.0667 | 368.1775 | 375.4927 | 367.6137
4912.0667 | 368.3651 | 375.323 | 367.5386
4913.0667 | 368.3198 | 375.3739 | 367.7342
4914.0667 | 368.2986 | 375.535 | 367.9772
4915.0667 | 368.8531 | 376.6875 | 367.9623
4916.0667 | 369.3963 | 376.9988 | 367.6984
4917.0667 | 369.7587 | 377.1428 | 367.3891
4918.0667 | 371.3975 | 377.3876 | 367.168
4919.0667 | 371.5585 | 377.5808 | 367.4205
4920.0667 | 371.6679 | 377.4125 | 367.2166
4921.0667 | 371.6859 | 376.9664 | 366.6551
4922.0667 | 371.3535 | 376.5702 | 366.3905
4923.0667 | 371.2138 | 376.8314 | 366.0607
4924.0667 | 371.1069 | 376.7257 | 365.4308
4925.0667 | 370.9568 | 376.4908 | 365.6512
4926.0667 | 370.7409 | 376.6483 | 365.63
4927.0667 | 370.4419 | 376.6214 | 365.9975
4928.0667 | 370.4754 | 376.0749 | 365.3837
4929.0667 | 370.1527 | 376.8527 | 364.7846
4930.0667 | 369.889 | 376.828 | 364.3654
4931.0667 | 369.6772 | 376.3767 | 363.8894
4932.0667 | 369.6263 | 376.386 | 363.5972
4933.0667 | 369.6679 | 376.3034 | 363.5152
4934.0667 | 369.684 | 376.3241 | 363.1812
4935.0667 | 369.5984 | 376.3843 | 363.2749
4936.0667 | 369.343 | 376.0496 | 363.0685
4937.0667 | 369.4868 | 375.8076 | 362.9529
4938.0667 | 369.3929 | 375.6679 | 363.0072
4939.0667 | 369.882 | 375.8593 | 363.0686
4940.0667 | 369.7864 | 375.7423 | 363.5027
4941.0667 | 369.7197 | 375.5532 | 364.0075
4942.0667 | 369.6887 | 375.2811 | 364.0214
4943.0667 | 369.7037 | 375.2474 | 363.8778
4944.0667 | 369.6884 | 375.3419 | 363.5778
4945.0667 | 370.2982 | 375.6565 | 364.4247
4946.0667 | 371.3191 | 376.582 | 364.5506
4947.0667 | 371.7642 | 376.8553 | 364.5016
4948.0667 | 371.5421 | 377.6798 | 364.5844
4949.0667 | 371.4114 | 378.6594 | 364.6387
4950.0667 | 371.1904 | 379.001 | 364.6145
4951.0667 | 371.1487 | 379.2492 | 365.2546
4952.0667 | 371.418 | 379.517 | 365.908
4953.0667 | 371.1255 | 379.7111 | 367.1972
4954.0667 | 371.0374 | 379.8917 | 367.5488
4955.0667 | 371.1683 | 380.0059 | 367.1944
4956.0667 | 371.142 | 379.6528 | 366.9884
4957.0667 | 371.3113 | 379.7129 | 366.8073
4958.0667 | 371.8481 | 379.9457 | 367.1927
4959.0667 | 371.8466 | 379.9311 | 367.311
4960.0667 | 372.4091 | 380.3023 | 367.8318
4961.0667 | 372.2384 | 380.5186 | 367.7431
4962.0667 | 372.8973 | 380.6019 | 367.5314
4963.0667 | 373.2575 | 380.7738 | 367.4084
4964.0667 | 373.9696 | 381.4927 | 367.5847
4965.0667 | 374.0253 | 381.335 | 367.4827
4966.0667 | 373.7891 | 381.0802 | 367.1362
4967.0667 | 373.7225 | 380.7151 | 367.273
4968.0667 | 373.1422 | 380.2583 | 366.8428
4969.0667 | 373.0557 | 380.224 | 366.5522
4970.0667 | 372.6397 | 379.5075 | 366.3306
4971.0667 | 372.6416 | 379.547 | 366.0776
4972.0667 | 372.4639 | 379.4277 | 366.1507
4973.0667 | 372.1168 | 379.5735 | 365.9279
4974.0667 | 372.1037 | 379.4872 | 365.8677
4975.0667 | 372.6354 | 379.6944 | 366.2395
4976.0667 | 373.0032 | 379.5757 | 366.5063
4977.0667 | 373.0845 | 379.9232 | 366.5145
4978.0667 | 372.9274 | 380.6884 | 367.1079
4979.0667 | 372.5897 | 380.8712 | 367.2308
4980.0667 | 372.2901 | 380.9741 | 367.7177
4981.0667 | 371.8385 | 380.337 | 367.9745
4982.0667 | 372.0419 | 379.5819 | 367.7241
4983.0667 | 372.7942 | 378.9751 | 367.3655
4984.0823 | 373.1389 | 378.8992 | 367.3179
4985.0667 | 373.405 | 380.4413 | 367.7265
4986.0667 | 373.5396 | 380.5347 | 367.6374
4987.0667 | 373.5121 | 380.5806 | 367.6407
4988.0667 | 373.1546 | 380.285 | 367.9566
4989.0667 | 373.0928 | 379.9083 | 367.7355
4990.0667 | 373.9177 | 380.4436 | 367.4974
4991.0667 | 373.8017 | 380.0093 | 367.5661
4992.0667 | 373.761 | 379.6367 | 367.101
4993.0667 | 374.1154 | 379.5042 | 367.106
4994.0667 | 374.2149 | 379.5243 | 367.5791
4995.0667 | 374.3656 | 379.4312 | 367.5747
4996.0667 | 374.4227 | 379.7808 | 367.6419
4997.0667 | 374.564 | 379.4471 | 367.593
4998.0667 | 374.3734 | 379.408 | 367.8937
4999.0823 | 374.0779 | 379.1651 | 367.829
5000.0667 | 373.6706 | 379.0617 | 367.5145
5001.0667 | 373.3467 | 379.2286 | 367.4719
5002.0667 | 373.2396 | 379.2086 | 367.7506
5003.0667 | 373.6977 | 379.7411 | 367.727
5004.0667 | 373.8726 | 380.1173 | 367.9181
5005.0667 | 373.8043 | 380.031 | 368.1722
5006.0667 | 374.1423 | 380.8129 | 368.2008
5007.0667 | 374.3355 | 380.6585 | 368.7388
5008.0667 | 374.6199 | 380.3896 | 368.5248
5009.0667 | 374.4671 | 380.379 | 369.2208
5010.0667 | 374.4397 | 380.7241 | 369.9427
5011.0667 | 374.6765 | 381.3106 | 369.563
5012.0667 | 374.8217 | 381.5791 | 369.9701
5013.0667 | 375.4144 | 381.6392 | 369.8237
5014.0667 | 375.6865 | 381.8777 | 369.4554
5015.0667 | 375.4621 | 382.1302 | 369.2425
5016.0667 | 375.4912 | 382.5855 | 369.8814
5017.0667 | 375.3083 | 382.7437 | 370.6385
5018.0667 | 374.9508 | 382.175 | 370.4234
5019.0667 | 374.5868 | 381.8488 | 369.9519
5020.0667 | 374.2626 | 381.4476 | 369.5238
5021.0667 | 374.3682 | 381.1409 | 369.196
5022.0667 | 374.6665 | 381.0913 | 369.1234
5023.0667 | 374.7951 | 381.3075 | 369.194
5024.0823 | 375.0067 | 381.5813 | 368.8467
5025.0667 | 375.7341 | 381.5713 | 368.6993
5026.0667 | 376.047 | 381.7207 | 368.4223
5027.0667 | 375.9957 | 381.8846 | 368.6327
5028.0667 | 376.091 | 382.124 | 369.4943
5029.0667 | 375.9584 | 382.0011 | 369.6813
5030.0667 | 375.608 | 381.447 | 369.3289
5031.0667 | 375.0086 | 381.0182 | 368.9742
5032.0667 | 374.7511 | 381.0437 | 368.7786
5033.0667 | 374.8216 | 382.0019 | 369.2368
5034.0667 | 374.8126 | 382.1472 | 369.61
5035.0667 | 374.5389 | 382.3645 | 369.1961
5036.0667 | 375.104 | 382.0507 | 370.0695
5037.0667 | 375.0286 | 382.0594 | 369.8928
5038.0667 | 374.7432 | 382.2157 | 370.6382
5039.0823 | 374.4414 | 382.2576 | 370.3826
5040.0667 | 373.9669 | 381.6902 | 370.1465
5041.0667 | 373.5224 | 381.0305 | 370.1803
5042.0667 | 373.0176 | 380.4389 | 369.7951
5043.0667 | 373.4511 | 380.0117 | 369.3666
5044.0667 | 373.4592 | 379.5247 | 368.9954
5045.0667 | 373.8063 | 379.4547 | 368.8135
5046.0667 | 373.3037 | 378.8869 | 368.8532
5047.0667 | 373.0002 | 379.1645 | 368.6842
5048.0667 | 372.7754 | 379.2201 | 368.6716
5049.0667 | 372.8646 | 379.3795 | 368.6705
5050.0667 | 372.7906 | 379.752 | 368.9046
5051.0667 | 373.2549 | 379.7876 | 368.9971
5052.0667 | 373.1132 | 379.6806 | 368.6911
5053.0667 | 372.8934 | 379.5911 | 368.6757
5054.0667 | 373.1068 | 379.8179 | 368.5991
5055.0667 | 373.7411 | 380.3265 | 368.8023
5056.0667 | 373.6864 | 380.4302 | 368.7502
5057.0667 | 373.9365 | 380.8665 | 368.6354
5058.0667 | 373.6415 | 380.9469 | 369.2158
5059.0667 | 373.2689 | 381.2229 | 369.4097
5060.0667 | 372.8838 | 381.0332 | 369.3255
5061.0667 | 372.3292 | 380.7082 | 369.181
5062.0667 | 372.1488 | 380.5619 | 369.0646
5063.0667 | 372.2114 | 380.2109 | 368.7618
5064.0667 | 372.0706 | 380.1369 | 368.4676
5065.0667 | 371.9624 | 379.7422 | 368.0778
5066.0667 | 371.8181 | 379.5967 | 367.8485
5067.0667 | 371.8497 | 379.3765 | 367.9909
5068.0667 | 372.4235 | 379.0112 | 368.29
5069.0667 | 373.6188 | 378.9206 | 368.3651
5070.0667 | 373.6377 | 379.0427 | 368.4197
5071.0667 | 373.6268 | 379.1211 | 368.0947
5072.0667 | 373.772 | 378.8974 | 367.7785
5073.0667 | 373.4931 | 378.6466 | 367.2425
5074.0667 | 373.3926 | 378.5697 | 366.788
5075.0667 | 373.5841 | 378.6009 | 366.6965
5076.0667 | 373.4382 | 378.1467 | 366.7401
5077.0667 | 373.3361 | 378.1317 | 366.4282
5078.0667 | 373.1512 | 378.0806 | 366.5297
5079.0823 | 373.1894 | 378.2072 | 366.6325
5080.0667 | 372.9768 | 378.4318 | 366.7188
5081.0667 | 372.6344 | 377.9814 | 366.6213
5082.0667 | 372.4734 | 377.8825 | 366.3243
5083.0667 | 372.7232 | 377.7524 | 366.2431
5084.0667 | 372.6647 | 377.7506 | 366.984
5085.0667 | 373.0994 | 377.6554 | 367.1273
5086.0667 | 373.1528 | 377.6235 | 367.8298
5087.0667 | 373.3704 | 378.0007 | 367.7946
5088.0667 | 373.4358 | 378.1195 | 368.2491
5089.0667 | 373.4222 | 378.574 | 368.278
5090.0667 | 373.581 | 378.916 | 368.8603
5091.0667 | 373.6649 | 378.8212 | 369.4301
5092.0667 | 373.5541 | 378.8333 | 369.337
5093.0667 | 373.7706 | 378.7319 | 369.2627
5094.0667 | 373.6369 | 378.4812 | 369.1654
5095.0667 | 373.3586 | 378.122 | 368.9468
5096.0667 | 373.0169 | 377.797 | 368.8421
5097.0667 | 372.6041 | 377.9577 | 368.5975
5098.0667 | 372.2025 | 377.7358 | 368.34
5099.0667 | 371.8687 | 377.581 | 367.8601
5100.0667 | 371.6043 | 377.8285 | 367.4462