## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number Prelim 2 - Circuit Simulator Data Only
Test Date: | 2009-11-04
DCSim DAQ Start Time | 16:26
DCSim Time for Synchronization | 17:24
Heat Source Synchronization | 0:46 | hour:minutes:seconds
Heat Source DAQ Start Time | 16:38
Fire Time | 17:26
Offset | 1:00 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3620 | seconds
Heat Source Offset | 0:48 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2895 | seconds
Heat Source Stop Time | 17:49
Test Duration | 0:23 | hour:minutes:seconds
| 1360 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0, 1, and 2 represents the air temperature 3', 5', and 7' down the cable tray located in A Position. These are labeled as "north top", "north mid", "north bottom", respectively.
MOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 7, 8, and 9 represents the air temperature 3', 5', and 7' down the cable tray located in E Position. These are labeled as "south top", "south mid", "south bottom", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.875 | 123.1155 | -64.4211 | 58.4381 | -0.0077822 | -0.0017731 | 0.00083303 | -0.00067711 | -0.00032902 | -0.00044001 | 0.0013992 | 0.056641 | -0.00078177 | 0.00035453 | -0.00046783 | -0.00070273 | -0.00077127 | 0.0018287 | -0.19684 | 58.3969 | -64.5493 | 58.3557 | -64.2334 | -64.6454 | -64.5493 | -0.050354 | 58.429 | -64.5035 | 58.4702 | -64.3616 | -64.4577 | -64.2059 | -0.12817 | -0.041198 | -0.082397 | 0.18768 | -0.12817 | -0.2243 | 0 | -0.096131 | -0.082397 | -0.009155 | 0.032044 | 0.05951 | 0.21515 | -0.036621 | 0.29755 | 0.045776 | 0.31586 | 122.905 | 0.14191 | 122.9736 | 122.9462 | 122.9324 | 122.818 | 122.85 | -122.9874 | -122.9416 | 122.7768 | 122.8912 | 64.2242 | 64.3707
0.79688 | 123.1567 | -64.4211 | 58.4061 | -0.03067 | 0.0014313 | 0.0033966 | 0.00060449 | 0.0018072 | 0.0034052 | 0.0013992 | -0.019653 | 0.002636 | 0.00035453 | -0.0021768 | -6.1934e-05 | -0.00098487 | 0.0018287 | -0.17853 | 58.3923 | -64.5447 | 58.3557 | -64.2517 | -64.682 | -64.5767 | 0.004578 | 58.4015 | -64.4989 | 58.5114 | -64.3341 | -64.4485 | -64.1464 | -0.1236 | -0.013733 | -0.050354 | 0.16937 | -0.15564 | -0.26093 | -0.032043 | -0.13733 | -0.077819 | -0.004578 | 0.10529 | 0.086976 | 0.27466 | -0.027465 | 0.35248 | 0.050354 | 0.29297 | 122.9004 | 0.16479 | 123.0103 | 122.937 | 122.9004 | 122.8134 | 122.8226 | -122.9507 | -122.905 | 122.7768 | 122.9324 | 64.2426 | 64.4257
2.5312 | 123.1384 | -64.4257 | 58.4015 | 0.045624 | -0.00070494 | 0.002542 | 0.0031681 | -0.00032902 | 0.00041439 | -0.00030975 | -0.037964 | 0.00028623 | 0.0050543 | 0.010213 | -0.0013437 | -0.0033347 | 0.00033326 | -0.16937 | 58.4061 | -64.5813 | 58.3328 | -64.3021 | -64.7369 | -64.6133 | -0.059509 | 58.4152 | -64.5081 | 58.4702 | -64.3616 | -64.4943 | -64.2014 | -0.15564 | 0.004578 | -0.068664 | 0.1236 | -0.18768 | -0.31128 | -0.032043 | -0.15564 | -0.082398 | 0.013733 | 0.068665 | 0.064087 | 0.2243 | -0.068665 | 0.3067 | 0.013733 | 0.27924 | 122.9141 | 0.14648 | 122.9782 | 122.9874 | 122.9233 | 122.8317 | 122.8409 | -122.9828 | -122.9095 | 122.7585 | 122.8958 | 64.2563 | 64.3661
4.2656 | 123.0469 | -64.4073 | 58.5114 | 0.030365 | -0.0013457 | 0.00040583 | 0.00060449 | -0.00054262 | -0.001081 | 0.0041762 | -0.041016 | 0.00028623 | 0.0020635 | -0.0053812 | -0.00027553 | -0.0020529 | -0.0013757 | -0.10529 | 58.4839 | -64.5493 | 58.3374 | -64.2746 | -64.6591 | -64.5859 | -0.022888 | 58.4885 | -64.4852 | 58.4473 | -64.3753 | -64.4943 | -64.2242 | -0.14191 | -0.027466 | -0.17395 | 0.13275 | -0.17853 | -0.25177 | -0.036621 | -0.10986 | -0.077819 | -0.022889 | -0.064087 | 0.032044 | 0.18311 | -0.086975 | 0.26093 | -0.009156 | 0.27466 | 122.8867 | 0.10986 | 122.9324 | 123.0331 | 122.9736 | 122.8912 | 122.8958 | -123.0606 | -122.9965 | 122.7448 | 122.8546 | 64.3021 | 64.3845
6 | 123.1705 | -64.4165 | 58.429 | -0.0383 | -0.00070494 | 0.0019012 | -0.0030271 | -0.00054262 | 0.001269 | 0.00075845 | 0.074951 | -0.0020636 | 0.0014227 | -0.0011086 | 0.0022879 | -0.0035483 | 0.0035377 | -0.15564 | 58.4015 | -64.5264 | 58.3649 | -64.2059 | -64.6133 | -64.5218 | -0.009155 | 58.4015 | -64.4623 | 58.5205 | -64.27 | -64.3845 | -64.1373 | -0.10986 | -0.027466 | -0.064087 | 0.21057 | -0.10529 | -0.19684 | 0.004577 | -0.086975 | -0.045776 | -0.027466 | 0.091553 | 0.14648 | 0.27924 | 0.032044 | 0.32501 | 0.07782 | 0.32043 | 122.8912 | 0.19226 | 122.9828 | 122.9279 | 122.8638 | 122.818 | 122.818 | -122.9553 | -122.8912 | 122.7814 | 122.937 | 64.2609 | 64.4073
7.75 | 123.143 | -64.3936 | 58.4015 | -0.068817 | 0.0018585 | 0.0038238 | -0.00046351 | 0.00138 | 0.00062799 | -0.0011642 | 0.001709 | 7.2626e-05 | 0.00035453 | -0.0036722 | -6.1934e-05 | -0.00013027 | -0.0024439 | -0.13733 | 58.3511 | -64.5264 | 58.3969 | -64.1968 | -64.6317 | -64.5264 | 0.036621 | 58.4015 | -64.476 | 58.5114 | -64.3204 | -64.444 | -64.1739 | -0.13275 | -0.050354 | -0.004577 | 0.19684 | -0.13275 | -0.23804 | 0 | -0.10529 | -0.082397 | 0 | 0.10986 | 0.073242 | 0.21973 | -0.050354 | 0.30212 | 0.032043 | 0.32959 | 122.9233 | 0.15564 | 122.9874 | 122.8775 | 122.8775 | 122.7448 | 122.7951 | -122.9279 | -122.8775 | 122.7905 | 122.905 | 64.2563 | 64.4302
9.4375 | 123.1201 | -64.3753 | 58.4885 | -0.00015269 | -0.0024139 | 0.0012604 | -0.0013181 | 0.0020208 | 0.00084159 | -0.00030975 | 0.029175 | -0.0024908 | -0.00028627 | -0.0040994 | -6.1934e-05 | -0.0016257 | 0.0016151 | -0.082397 | 58.4106 | -64.5126 | 58.4427 | -64.1556 | -64.5538 | -64.4714 | 0.086975 | 58.4427 | -64.4211 | 58.5205 | -64.2792 | -64.3799 | -64.1373 | -0.13733 | -0.077819 | -0.045776 | 0.21973 | -0.096131 | -0.17853 | 0.041198 | -0.041199 | -0.045777 | -0.045776 | 0.032044 | 0.09613 | 0.23804 | -0.004578 | 0.28381 | 0.041199 | 0.35706 | 122.9553 | 0.14191 | 122.9416 | 122.9233 | 122.8638 | 122.7859 | 122.818 | -123.0011 | -122.9095 | 122.818 | 122.8958 | 64.2929 | 64.4623
11.1719 | 123.0743 | -64.4485 | 58.4427 | 0.037994 | -0.00027774 | 0.00061943 | 0.0020999 | -0.0033196 | 0.0010554 | -0.00073695 | -0.050171 | 0.0019952 | 0.0018499 | 0.002523 | -0.00070273 | 0.00029693 | 0.00097406 | -0.16479 | 58.4015 | -64.5538 | 58.3099 | -64.325 | -64.7415 | -64.6362 | -0.086975 | 58.4473 | -64.5355 | 58.429 | -64.4257 | -64.5447 | -64.238 | -0.10529 | -0.041199 | -0.13275 | 0.1236 | -0.18768 | -0.29297 | -0.082397 | -0.18768 | -0.086975 | 0.004578 | -0.013733 | 0.022888 | 0.21057 | -0.096131 | 0.29755 | -0.009156 | 0.22888 | 122.8638 | 0.10986 | 122.9645 | 122.9553 | 122.9828 | 122.85 | 122.8958 | -122.9965 | -122.9782 | 122.7585 | 122.8775 | 64.2838 | 64.3616
12.8906 | 123.1476 | -64.4073 | 58.461 | -0.015411 | -6.4144e-05 | 0.0019012 | -0.00089091 | -0.003106 | -1.2808e-05 | -9.6154e-05 | 0.053589 | -0.00035457 | 0.0029181 | 0.003591 | 0.00036527 | -0.0026939 | 0.0037513 | -0.16022 | 58.4198 | -64.5355 | 58.3557 | -64.2242 | -64.6317 | -64.5355 | -0.032043 | 58.4335 | -64.4806 | 58.5022 | -64.2929 | -64.4028 | -64.1464 | -0.12817 | -0.041199 | -0.10529 | 0.18311 | -0.12817 | -0.2243 | 0 | -0.096131 | -0.073242 | -0.027466 | 0.041198 | 0.11444 | 0.26093 | 0.004578 | 0.33417 | 0.07782 | 0.31128 | 122.8912 | 0.18768 | 122.9828 | 122.9553 | 122.9141 | 122.8271 | 122.8409 | -122.9965 | -122.9416 | 122.7631 | 122.9095 | 64.2471 | 64.3753
14.6406 | 123.1705 | -64.4028 | 58.3923 | -0.0077822 | -0.00027774 | 0.0012604 | 0.00081809 | 9.818e-05 | 0.0019098 | 0.0028946 | -0.034912 | -0.0014228 | 0.00078193 | -0.00089503 | -0.0013437 | -0.0026939 | -0.0022301 | -0.13275 | 58.374 | -64.563 | 58.3923 | -64.2014 | -64.6545 | -64.5355 | 0.013733 | 58.3923 | -64.4989 | 58.5205 | -64.3204 | -64.4485 | -64.1464 | -0.16022 | -0.018311 | 0 | 0.20142 | -0.13275 | -0.25177 | 0.027466 | -0.091553 | -0.09613 | 0 | 0.12817 | 0.082397 | 0.25635 | -0.045776 | 0.35248 | 0.050354 | 0.36163 | 122.9553 | 0.17853 | 123.0194 | 122.937 | 122.8912 | 122.7768 | 122.7951 | -122.9553 | -122.8912 | 122.7951 | 122.9233 | 64.27 | 64.4165
16.2969 | 123.0789 | -64.4257 | 58.4747 | 0.022736 | 0.00036326 | 0.0016876 | 0.0020999 | 0.0015936 | -1.2808e-05 | 0.0016128 | -0.06543 | 0.0019952 | -0.00028627 | 0.00017297 | -0.0015573 | -0.0016257 | 0.00076046 | -0.050354 | 58.4473 | -64.5721 | 58.3878 | -64.2334 | -64.6545 | -64.5767 | 0.027466 | 58.4427 | -64.444 | 58.4747 | -64.3616 | -64.4989 | -64.2151 | -0.14648 | -0.027465 | -0.086975 | 0.19226 | -0.15106 | -0.22888 | -0.004577 | -0.082397 | -0.018311 | -0.032043 | 0 | 0.064087 | 0.21057 | -0.073242 | 0.22888 | -0.054931 | 0.33875 | 122.9599 | 0.082398 | 122.9187 | 123.0194 | 122.8867 | 122.8729 | 122.8683 | -123.0469 | -122.9187 | 122.8134 | 122.9004 | 64.3753 | 64.4531
18.0312 | 123.1384 | -64.4028 | 58.4198 | 0.022736 | 0.0014313 | 0.00083303 | -0.00024991 | 0.00073918 | 0.00062799 | -0.00095055 | 0.056641 | -0.00056817 | 0.0022773 | -0.0053812 | 0.0025015 | -0.0018393 | -0.0026575 | -0.16937 | 58.4015 | -64.5401 | 58.3649 | -64.1876 | -64.6454 | -64.5401 | -0.004578 | 58.3969 | -64.4943 | 58.4793 | -64.3433 | -64.4485 | -64.1876 | -0.13733 | -0.018311 | -0.054932 | 0.21515 | -0.13733 | -0.24262 | 0 | -0.10529 | -0.091553 | -0.022888 | 0.059509 | 0.059509 | 0.21515 | -0.045776 | 0.3067 | 0.045777 | 0.35248 | 122.905 | 0.15106 | 122.9736 | 122.9416 | 122.8912 | 122.8043 | 122.7997 | -122.9599 | -122.9141 | 122.7676 | 122.8821 | 64.2334 | 64.3982
19.7812 | 123.0789 | -64.3936 | 58.5022 | 0.10666 | -0.0013457 | -0.00044857 | -0.00089091 | 0.004798 | -0.0019354 | 0.00439 | -0.010498 | 0.0013544 | 0.0018499 | 0.0012412 | 0.00079247 | -0.00055747 | -0.00094854 | -0.10986 | 58.4793 | -64.5538 | 58.3282 | -64.2746 | -64.6591 | -64.5905 | -0.027466 | 58.5022 | -64.476 | 58.4427 | -64.3707 | -64.4714 | -64.2059 | -0.16022 | -0.022888 | -0.17395 | 0.11902 | -0.19684 | -0.2655 | -0.036621 | -0.10529 | -0.082397 | 0 | -0.059509 | 0.022888 | 0.18768 | -0.07782 | 0.27008 | 0.004577 | 0.27924 | 122.8821 | 0.10528 | 122.9187 | 123.0331 | 122.9782 | 122.8729 | 122.8958 | -123.056 | -122.9782 | 122.7219 | 122.8363 | 64.2838 | 64.3661
21.4531 | 123.1979 | -64.3616 | 58.4473 | 0.053253 | -0.0028411 | -0.00044857 | -0.0015317 | -0.0035334 | -0.0040716 | 0.00011745 | 0.068848 | 0.00092703 | -7.2674e-05 | -0.0028176 | -0.00091653 | -0.0018393 | -0.0015893 | -0.10529 | 58.4015 | -64.5309 | 58.4381 | -64.1281 | -64.563 | -64.4623 | 0.10529 | 58.4061 | -64.444 | 58.5617 | -64.2334 | -64.3387 | -64.0915 | -0.16937 | -0.045777 | -0.009156 | 0.23346 | -0.10071 | -0.20142 | 0.068665 | -0.032043 | -0.082398 | -0.041199 | 0.11444 | 0.12817 | 0.27008 | 0.022888 | 0.35248 | 0.10529 | 0.40283 | 122.9691 | 0.21057 | 123.0057 | 122.9324 | 122.85 | 122.7631 | 122.7676 | -122.9782 | -122.8912 | 122.7997 | 122.9233 | 64.2563 | 64.4669
23.1875 | 123.1522 | -64.4257 | 58.3969 | -0.023041 | 0.0012177 | 0.0019012 | 0.0018863 | -0.00075622 | -0.001081 | -0.0015916 | -0.041016 | 0.0013544 | -0.00028627 | 0.0040182 | 0.00015167 | -0.0016257 | -0.00073494 | -0.16022 | 58.3969 | -64.5401 | 58.3694 | -64.2242 | -64.6683 | -64.5676 | -0.004578 | 58.3878 | -64.4897 | 58.5068 | -64.3341 | -64.4531 | -64.1418 | -0.11444 | 0 | -0.027466 | 0.20142 | -0.14191 | -0.24262 | -0.027466 | -0.12817 | -0.064087 | -0.009156 | 0.10986 | 0.091553 | 0.28381 | -0.027466 | 0.3479 | 0.036621 | 0.31586 | 122.9095 | 0.15564 | 122.9965 | 122.937 | 122.8775 | 122.8226 | 122.8134 | -122.937 | -122.8867 | 122.7951 | 122.9324 | 64.2654 | 64.4211
24.875 | 123.0743 | -64.4165 | 58.4747 | -0.00015269 | 0.0020721 | 0.0021148 | 0.0023135 | 0.0024482 | 0.00020079 | 0.00033105 | -0.068481 | 0.00071343 | 0.0029181 | 0.00081397 | -0.0013437 | -0.00034387 | -0.00094854 | -0.064087 | 58.4427 | -64.5172 | 58.3786 | -64.2242 | -64.6637 | -64.5859 | 0.018311 | 58.4564 | -64.476 | 58.461 | -64.3707 | -64.5035 | -64.2151 | -0.10071 | -0.032043 | -0.09613 | 0.19226 | -0.16937 | -0.24719 | -0.068664 | -0.14648 | -0.059509 | -0.01831 | -0.013732 | 0.045776 | 0.20142 | -0.086975 | 0.26093 | -0.027466 | 0.29297 | 122.8958 | 0.10528 | 122.937 | 122.9599 | 122.9324 | 122.8592 | 122.8729 | -122.9919 | -122.9507 | 122.7951 | 122.8775 | 64.3524 | 64.4348
26.6094 | 123.1842 | -64.3799 | 58.4427 | -0.0383 | -0.00027774 | 0.0012604 | -0.00089091 | -0.0043878 | -0.00086721 | 0.0018264 | 0.078003 | -0.00185 | 0.0012091 | -0.0030312 | -0.00070273 | -0.0011985 | -0.00030754 | -0.15106 | 58.4106 | -64.5355 | 58.4015 | -64.1876 | -64.5905 | -64.5035 | 0.041199 | 58.4335 | -64.4577 | 58.5434 | -64.27 | -64.3662 | -64.119 | -0.15564 | -0.032043 | -0.041199 | 0.19226 | -0.1236 | -0.21057 | 0.032043 | -0.054932 | -0.07782 | -0.009155 | 0.10071 | 0.10986 | 0.26093 | 0.013733 | 0.33874 | 0.091553 | 0.3479 | 122.937 | 0.18768 | 123.0011 | 122.9462 | 122.8912 | 122.7905 | 122.8134 | -122.9782 | -122.9004 | 122.7814 | 122.9233 | 64.2288 | 64.4211
28.2812 | 123.1064 | -64.4119 | 58.4106 | 0.0074768 | -6.4144e-05 | 0.002542 | 0.0023135 | 0.0043708 | -1.2808e-05 | -0.0018052 | -0.037964 | 0.0022088 | 0.0022773 | 0.0040182 | -0.0017709 | -0.0011985 | -0.0024439 | -0.17853 | 58.4518 | -64.5721 | 58.3191 | -64.2975 | -64.7415 | -64.6225 | -0.064087 | 58.429 | -64.5264 | 58.4564 | -64.4028 | -64.5172 | -64.2059 | -0.16022 | 0.041198 | -0.091553 | 0.11444 | -0.21057 | -0.32959 | -0.050354 | -0.16937 | -0.11444 | 0.01831 | 0.045776 | 0.009155 | 0.20599 | -0.10529 | 0.32043 | 0.009155 | 0.27466 | 122.8912 | 0.1236 | 122.9828 | 123.024 | 122.9553 | 122.8638 | 122.8409 | -122.9828 | -122.937 | 122.731 | 122.8683 | 64.2334 | 64.3478
30.0156 | 123.143 | -64.4119 | 58.3923 | 0.022736 | 0.0022859 | 0.003183 | 0.0016727 | 0.0022346 | 0.00084159 | -0.002446 | -0.041016 | 0.0028498 | 0.0014227 | -0.0028176 | -0.00070273 | -0.0024803 | -0.00094854 | -0.17853 | 58.429 | -64.5721 | 58.2962 | -64.2838 | -64.7278 | -64.6271 | -0.050354 | 58.4106 | -64.5126 | 58.4885 | -64.357 | -64.4669 | -64.1785 | -0.16022 | 0.036621 | -0.09613 | 0.12817 | -0.21515 | -0.31586 | -0.054931 | -0.15564 | -0.10071 | 0.018311 | 0.09613 | 0.054931 | 0.23346 | -0.054932 | 0.33417 | 0.045776 | 0.28839 | 122.8683 | 0.15564 | 123.0011 | 123.0011 | 122.9233 | 122.8409 | 122.8226 | -122.9645 | -122.905 | 122.7081 | 122.9004 | 64.2334 | 64.3616
31.75 | 123.175 | -64.3936 | 58.4564 | 0.076141 | -0.0022003 | 0.002542 | -0.0017453 | -0.0041742 | -0.00022641 | -0.00030975 | 0.041382 | -0.00185 | -0.00028627 | -0.0083718 | 0.00057887 | -0.0016257 | -0.00094854 | -0.07782 | 58.4015 | -64.5172 | 58.4473 | -64.1235 | -64.5493 | -64.476 | 0.09613 | 58.4473 | -64.4531 | 58.5434 | -64.2654 | -64.3524 | -64.1144 | -0.1236 | -0.054932 | -0.009155 | 0.27008 | -0.082397 | -0.15564 | 0.041199 | -0.032043 | -0.059509 | -0.009155 | 0.086975 | 0.12817 | 0.27924 | 0.041199 | 0.33875 | 0.10071 | 0.39368 | 122.9645 | 0.18768 | 122.9965 | 122.9187 | 122.9004 | 122.7951 | 122.8409 | -122.9736 | -122.9095 | 122.8409 | 122.937 | 64.3158 | 64.4897
33.5 | 123.1293 | -64.4073 | 58.3969 | 0.037994 | 0.00036326 | 0.0023284 | 0.0012455 | -0.00054262 | 0.00020079 | -0.0020188 | 0.016968 | 0.00028623 | 0.0022773 | -0.0045266 | -0.0026253 | 0.00029693 | 0.0022559 | -0.17395 | 58.3649 | -64.5355 | 58.3786 | -64.1968 | -64.65 | -64.5401 | 0.013733 | 58.3923 | -64.4852 | 58.4839 | -64.3478 | -64.4394 | -64.183 | -0.12817 | -0.032044 | -0.018311 | 0.21057 | -0.13275 | -0.24261 | -0.004578 | -0.11444 | -0.077819 | -0.004578 | 0.086975 | 0.05951 | 0.22431 | -0.032043 | 0.30212 | 0.045776 | 0.33875 | 122.9141 | 0.13733 | 122.9691 | 122.9004 | 122.8775 | 122.7722 | 122.7997 | -122.9324 | -122.8821 | 122.7859 | 122.8912 | 64.2334 | 64.4211
35.1719 | 123.1293 | -64.4073 | 58.4335 | -0.023041 | 0.00036326 | 0.0021148 | -0.0013181 | -0.00054262 | 0.00062799 | 0.00033105 | 0.023071 | -0.00078177 | 0.00035453 | 0.0048728 | -0.00027553 | -0.0029075 | -0.00052114 | -0.1831 | 58.3923 | -64.5447 | 58.3557 | -64.2334 | -64.6408 | -64.5447 | -0.027466 | 58.4061 | -64.4806 | 58.4793 | -64.3387 | -64.444 | -64.1922 | -0.13733 | -0.041199 | -0.07782 | 0.17395 | -0.13733 | -0.23346 | 0 | -0.09613 | -0.073242 | -0.027466 | 0.045776 | 0.068665 | 0.21515 | -0.036621 | 0.28839 | 0.036621 | 0.31128 | 122.9004 | 0.14191 | 122.9599 | 122.937 | 122.8867 | 122.7997 | 122.8134 | -122.9782 | -122.9141 | 122.7631 | 122.8867 | 64.2242 | 64.3799
36.9062 | 123.0743 | -64.389 | 58.5159 | -0.0077822 | -0.0015595 | -2.1372e-05 | -0.00046351 | -0.0043878 | -1.2808e-05 | 0.00075845 | -0.0013428 | 0.001568 | 0.0027045 | -0.0068766 | -0.00048913 | -0.0024803 | 0.00033326 | -0.082397 | 58.429 | -64.5126 | 58.4015 | -64.1876 | -64.5859 | -64.5035 | 0.032043 | 58.4885 | -64.4348 | 58.4564 | -64.3524 | -64.4485 | -64.2151 | -0.1236 | -0.086975 | -0.11444 | 0.20142 | -0.11444 | -0.19684 | 0.009155 | -0.073242 | -0.045776 | -0.027466 | -0.059509 | 0.036621 | 0.17395 | -0.059509 | 0.21973 | -0.013733 | 0.32501 | 122.9141 | 0.082397 | 122.8912 | 122.9416 | 122.9233 | 122.818 | 122.8775 | -123.0286 | -122.9507 | 122.7905 | 122.8455 | 64.3066 | 64.4211
38.6406 | 123.1247 | -64.444 | 58.4106 | -0.0383 | 0.00057686 | 0.0027558 | -0.0021725 | -0.0016106 | -1.2808e-05 | 0.002681 | 0.0078126 | 0.0011408 | 0.0016363 | -0.0058084 | -6.1934e-05 | -0.0044029 | 0.0028967 | -0.14191 | 58.3786 | -64.5309 | 58.3878 | -64.2105 | -64.6591 | -64.5538 | 0 | 58.4015 | -64.4806 | 58.4976 | -64.3433 | -64.4394 | -64.1739 | -0.086975 | -0.032044 | -0.022889 | 0.23346 | -0.10986 | -0.21515 | -0.022888 | -0.12817 | -0.036621 | -0.009156 | 0.086975 | 0.10071 | 0.27008 | 0.004578 | 0.3067 | 0.041199 | 0.32044 | 122.9187 | 0.13733 | 122.9782 | 122.9095 | 122.8821 | 122.8226 | 122.8455 | -122.9416 | -122.8912 | 122.8317 | 122.9416 | 64.3021 | 64.444
40.3125 | 123.1567 | -64.4211 | 58.3969 | -0.023041 | 0.00079046 | 0.0021148 | 0.0018863 | 0.00052558 | 0.00062799 | 0.0035354 | -0.047119 | 0.00071343 | 0.0014227 | -0.00089503 | 0.00079247 | -0.00098487 | -0.00073494 | -0.16022 | 58.3969 | -64.5538 | 58.3603 | -64.2105 | -64.6454 | -64.5767 | 0 | 58.3878 | -64.4897 | 58.5159 | -64.3387 | -64.4394 | -64.1373 | -0.13275 | 0 | -0.036621 | 0.21057 | -0.15564 | -0.2243 | -0.022888 | -0.091553 | -0.068664 | -0.009156 | 0.11902 | 0.082398 | 0.28381 | -0.01831 | 0.35248 | 0.050354 | 0.34332 | 122.9141 | 0.15106 | 123.0057 | 122.9507 | 122.8775 | 122.818 | 122.8088 | -122.9507 | -122.8867 | 122.7814 | 122.937 | 64.2609 | 64.4211
42.0625 | 123.111 | -64.4348 | 58.4015 | 0.015106 | -0.00027774 | 0.0040374 | 0.0033817 | 0.0018072 | 0.0025506 | 0.00097205 | -0.056274 | 0.0017816 | 0.0027045 | -0.0013224 | -0.00027553 | -0.0014121 | 0.0024695 | -0.16937 | 58.4152 | -64.5676 | 58.3237 | -64.3112 | -64.7324 | -64.6408 | -0.068665 | 58.4152 | -64.5126 | 58.4518 | -64.3936 | -64.4852 | -64.2059 | -0.13275 | 0.013733 | -0.07782 | 0.1236 | -0.20599 | -0.29755 | -0.073242 | -0.16479 | -0.07782 | 0.013733 | 0.050354 | 0.041198 | 0.22888 | -0.050354 | 0.3067 | 0.027466 | 0.25635 | 122.8912 | 0.11902 | 122.9645 | 122.9828 | 122.9279 | 122.85 | 122.85 | -122.9691 | -122.9141 | 122.7585 | 122.8867 | 64.2654 | 64.3661
43.7344 | 123.0927 | -64.4577 | 58.4152 | 0.022736 | -0.00027774 | 0.0012604 | 0.0012455 | 0.0035162 | 0.00084159 | -0.00030975 | -0.062378 | 0.00092703 | 0.0027045 | -0.0011086 | 0.00015167 | -0.0016257 | -0.0018029 | -0.17853 | 58.429 | -64.5676 | 58.2916 | -64.3112 | -64.7461 | -64.6179 | -0.086975 | 58.4152 | -64.5035 | 58.4427 | -64.4257 | -64.5355 | -64.2426 | -0.10986 | 0.013733 | -0.1236 | 0.14648 | -0.16022 | -0.28839 | -0.050354 | -0.17853 | -0.045776 | 0 | 0.027466 | 0.032044 | 0.21515 | -0.077819 | 0.26093 | -0.032043 | 0.25635 | 122.8592 | 0.07782 | 122.9462 | 122.9965 | 122.9187 | 122.8867 | 122.8729 | -122.9828 | -122.9187 | 122.7493 | 122.9004 | 64.2792 | 64.3707
45.4688 | 123.1018 | -64.4211 | 58.461 | 0.076141 | -0.00070494 | 0.0016876 | 0.0018863 | 0.0022346 | -0.00044001 | -0.00052335 | -0.059326 | 0.0017816 | 0.0012091 | 0.0016684 | -0.0024117 | -0.00098487 | 0.00033326 | -0.064087 | 58.4564 | -64.5493 | 58.3694 | -64.2059 | -64.6454 | -64.5721 | 0.041199 | 58.4885 | -64.4714 | 58.5022 | -64.3295 | -64.4577 | -64.1968 | -0.12817 | -0.004578 | -0.091553 | 0.21515 | -0.15106 | -0.2243 | -0.022889 | -0.096131 | -0.050354 | 0.027465 | 0.041198 | 0.091553 | 0.22431 | -0.036621 | 0.27466 | 0.013733 | 0.34332 | 122.9187 | 0.14191 | 122.9736 | 123.0057 | 122.9599 | 122.8775 | 122.9095 | -123.0103 | -122.9324 | 122.7905 | 122.9233 | 64.357 | 64.4623
47.2031 | 123.1155 | -64.4348 | 58.429 | -0.00015269 | -0.0019867 | 0.0027558 | -0.00024991 | -0.0024652 | 0.002978 | -9.6154e-05 | 0.059692 | -0.00056817 | 0.0037725 | -0.0023904 | 0.0022879 | -0.0020529 | -0.0022301 | -0.1831 | 58.374 | -64.5447 | 58.3557 | -64.2288 | -64.65 | -64.5493 | -0.050354 | 58.3969 | -64.4577 | 58.4656 | -64.3478 | -64.4531 | -64.1876 | -0.10986 | -0.054932 | -0.073242 | 0.20599 | -0.11444 | -0.21515 | -0.004577 | -0.10528 | -0.022889 | -0.032043 | 0.036621 | 0.086975 | 0.24719 | -0.018311 | 0.27008 | 0.004578 | 0.31586 | 122.9004 | 0.10986 | 122.9233 | 122.9187 | 122.8546 | 122.8088 | 122.8317 | -122.9736 | -122.8867 | 122.7905 | 122.9004 | 64.2517 | 64.3845
48.9375 | 123.0927 | -64.4165 | 58.4702 | 0.0074768 | -6.4144e-05 | 0.001474 | 0.0010319 | -0.00032902 | -1.2808e-05 | 0.0013992 | -0.041016 | -0.00056817 | 0.00099553 | -0.00046783 | -0.0011301 | -0.00077127 | -0.00030754 | -0.091553 | 58.4564 | -64.5172 | 58.3466 | -64.2609 | -64.6362 | -64.5859 | -0.009155 | 58.5022 | -64.4806 | 58.4839 | -64.3524 | -64.4714 | -64.1922 | -0.10071 | -0.013733 | -0.1236 | 0.15564 | -0.16937 | -0.21973 | -0.068664 | -0.11902 | -0.064087 | 0.032043 | 0.013733 | 0.064087 | 0.2243 | -0.054932 | 0.28839 | 0.009155 | 0.25635 | 122.8638 | 0.12817 | 122.9645 | 122.9736 | 122.9828 | 122.8729 | 122.9187 | -122.9874 | -122.9507 | 122.7631 | 122.9004 | 64.325 | 64.4073
50.6719 | 123.1613 | -64.3616 | 58.4427 | 0.030365 | -0.0022003 | 0.0033966 | -0.0017453 | -0.0016106 | 0.00062799 | -9.6154e-05 | 0.065796 | -0.00035457 | 0.00035453 | 0.00017297 | -0.00070273 | -0.0024803 | 0.00011966 | -0.082397 | 58.4244 | -64.4852 | 58.4518 | -64.1327 | -64.5538 | -64.4714 | 0.10529 | 58.4381 | -64.444 | 58.5342 | -64.2563 | -64.3478 | -64.1281 | -0.1236 | -0.018311 | 0.009155 | 0.22888 | -0.10986 | -0.19226 | 0.013732 | -0.068665 | -0.082398 | -0.004578 | 0.091553 | 0.10528 | 0.23346 | 0.013733 | 0.31586 | 0.096131 | 0.35248 | 122.937 | 0.18768 | 122.9782 | 122.9095 | 122.8821 | 122.7859 | 122.7997 | -122.9279 | -122.8867 | 122.8134 | 122.8958 | 64.2792 | 64.4669
52.4219 | 123.1842 | -64.3707 | 58.4335 | -0.0077822 | -0.0022003 | 0.0033966 | -0.0011045 | -0.003106 | -0.0025762 | -0.00073695 | 0.068848 | 0.00049983 | 0.0012091 | -0.00089503 | -0.00048913 | -0.0014121 | -0.0011621 | -0.11902 | 58.4015 | -64.5264 | 58.4244 | -64.1556 | -64.5676 | -64.4714 | 0.091553 | 58.4198 | -64.4531 | 58.5617 | -64.2471 | -64.3387 | -64.1006 | -0.15564 | -0.032044 | -0.009156 | 0.21515 | -0.10071 | -0.19684 | 0.054931 | -0.041199 | -0.082397 | -0.013733 | 0.12817 | 0.1236 | 0.27008 | 0.032044 | 0.35248 | 0.11444 | 0.37079 | 122.9507 | 0.20599 | 123.0148 | 122.9279 | 122.8729 | 122.7722 | 122.7905 | -122.9599 | -122.8867 | 122.7951 | 122.9324 | 64.2517 | 64.4623
54.0938 | 123.1796 | -64.4394 | 58.4061 | -0.0383 | 0.0020721 | 0.0044646 | -0.00024991 | -0.0024652 | 0.001269 | -0.00095055 | -0.0013428 | 0.0017816 | 0.0018499 | 0.0027366 | -0.0024117 | -0.0011985 | 0.0046057 | -0.13275 | 58.374 | -64.5401 | 58.3923 | -64.2014 | -64.6454 | -64.5355 | 0.013733 | 58.3969 | -64.476 | 58.5114 | -64.3112 | -64.4211 | -64.151 | -0.10071 | -0.032044 | -0.013733 | 0.23804 | -0.09613 | -0.20599 | 0.004578 | -0.10529 | -0.036621 | -0.009155 | 0.10529 | 0.12817 | 0.28839 | 0.01831 | 0.32501 | 0.054931 | 0.33874 | 122.9324 | 0.16479 | 122.9874 | 122.9141 | 122.8729 | 122.8134 | 122.8363 | -122.9462 | -122.8821 | 122.8317 | 122.9507 | 64.3066 | 64.4531
55.8281 | 123.1476 | -64.3982 | 58.4656 | -0.00015269 | -0.0024139 | 0.00061943 | -0.0021725 | -0.00096982 | 0.00020079 | 0.0018264 | 0.044434 | -0.00014097 | 0.0035589 | -0.0047402 | -0.00048913 | -0.0018393 | 0.00033326 | -0.068665 | 58.3969 | -64.5309 | 58.4518 | -64.1418 | -64.5538 | -64.476 | 0.082397 | 58.4473 | -64.4577 | 58.548 | -64.2563 | -64.3799 | -64.1281 | -0.13275 | -0.068664 | -0.013733 | 0.25635 | -0.07782 | -0.15564 | 0.054932 | -0.022888 | -0.05951 | -0.01831 | 0.082398 | 0.14191 | 0.27008 | 0.01831 | 0.32959 | 0.07782 | 0.3891 | 122.9828 | 0.20142 | 123.0057 | 122.9279 | 122.905 | 122.7951 | 122.8455 | -122.9965 | -122.9233 | 122.85 | 122.9462 | 64.3295 | 64.4806
57.5781 | 123.1842 | -64.3753 | 58.4244 | -0.00015269 | -0.0024139 | 0.0016876 | -0.0030271 | -0.002038 | 0.0016962 | 0.00033105 | 0.047485 | 0.00028623 | 0.00056833 | -0.0028176 | -0.0013437 | -0.0024803 | -0.0030847 | -0.11444 | 58.4061 | -64.5309 | 58.4244 | -64.1647 | -64.563 | -64.4623 | 0.09613 | 58.4198 | -64.4348 | 58.5663 | -64.2426 | -64.3295 | -64.1052 | -0.15564 | -0.01831 | 0 | 0.21057 | -0.086975 | -0.18768 | 0.068665 | -0.032043 | -0.059509 | -0.004577 | 0.14191 | 0.13275 | 0.27008 | 0.045776 | 0.32959 | 0.10529 | 0.36621 | 122.9553 | 0.19226 | 123.0011 | 122.937 | 122.8546 | 122.7814 | 122.7951 | -122.9553 | -122.8592 | 122.7997 | 122.9416 | 64.2609 | 64.4714
59.25 | 123.1384 | -64.4073 | 58.4381 | 0.0074768 | -0.0022003 | 0.0040374 | 0.00081809 | -0.002038 | 0.00020079 | -0.0011642 | 0.041382 | -0.00099557 | -0.0017817 | 0.00038657 | 0.0014335 | -0.00077127 | 0.0018287 | -0.17395 | 58.4152 | -64.5493 | 58.3557 | -64.2517 | -64.6591 | -64.5401 | -0.036621 | 58.4244 | -64.4623 | 58.4839 | -64.3158 | -64.4165 | -64.1647 | -0.14191 | -0.022888 | -0.082397 | 0.15564 | -0.13275 | -0.25177 | 0.009155 | -0.10986 | -0.054931 | -0.013733 | 0.045777 | 0.091553 | 0.24262 | -0.009155 | 0.29755 | 0.045776 | 0.29755 | 122.905 | 0.14648 | 122.9462 | 122.9645 | 122.8867 | 122.8226 | 122.8317 | -122.9874 | -122.9004 | 122.7631 | 122.8912 | 64.2334 | 64.3707
61 | 123.0423 | -64.4394 | 58.4885 | 0.053253 | 0.0031403 | 0.0019012 | 0.0020999 | -0.0026788 | -0.00065361 | 0.00033105 | -0.089844 | -0.00099557 | 0.0014227 | 0.0074362 | 0.00079247 | 8.3332e-05 | -0.0026575 | -0.11902 | 58.429 | -64.5493 | 58.3282 | -64.3021 | -64.7415 | -64.65 | -0.068665 | 58.4564 | -64.5035 | 58.4244 | -64.4485 | -64.5538 | -64.2563 | -0.10986 | -0.059509 | -0.16022 | 0.13733 | -0.21057 | -0.30212 | -0.10071 | -0.19226 | -0.064087 | -0.032043 | -0.064087 | -0.009155 | 0.1831 | -0.11444 | 0.24719 | -0.050354 | 0.24719 | 122.8775 | 0.054932 | 122.9279 | 122.9782 | 122.9599 | 122.8683 | 122.8958 | -123.0377 | -122.9919 | 122.7676 | 122.8638 | 64.3204 | 64.3707
63.4375 | 123.1338 | -64.3707 | 58.4839 | 0.053253 | 0.00079046 | 0.0010468 | -0.0023861 | 0.0022346 | -0.0012946 | -0.00052335 | 0.02002 | 0.0013544 | -0.0019953 | 0.00038657 | -0.0028391 | -0.0033347 | -0.0011621 | -0.059509 | 58.4061 | -64.5309 | 58.4427 | -64.1556 | -64.563 | -64.4897 | 0.082397 | 58.461 | -64.4302 | 58.5251 | -64.2838 | -64.3707 | -64.1373 | -0.16022 | -0.07782 | -0.041199 | 0.21515 | -0.11902 | -0.19226 | 0.041199 | -0.032043 | -0.059509 | -0.022888 | 0.041198 | 0.086976 | 0.23346 | 0 | 0.29297 | 0.059509 | 0.37537 | 122.9736 | 0.14648 | 122.9553 | 122.937 | 122.8912 | 122.7768 | 122.8317 | -123.0148 | -122.9141 | 122.8134 | 122.8958 | 64.3112 | 64.4531
65.3594 | 123.1705 | -64.3982 | 58.4061 | -0.03067 | 0.00014946 | 0.003183 | 0.00081809 | 0.00095278 | 0.0019098 | 0.00011745 | -0.025757 | -0.0016364 | 0.00078193 | 0.0031638 | -0.00070273 | -0.0011985 | -0.0026575 | -0.11902 | 58.374 | -64.5447 | 58.3832 | -64.2151 | -64.6454 | -64.5401 | 0.018311 | 58.3923 | -64.4943 | 58.5297 | -64.3158 | -64.4394 | -64.1418 | -0.14648 | -0.032044 | -0.022888 | 0.18311 | -0.14191 | -0.24719 | 0.004578 | -0.10071 | -0.096131 | -0.013733 | 0.1236 | 0.082397 | 0.25635 | -0.041199 | 0.35248 | 0.054932 | 0.32959 | 122.9279 | 0.17853 | 123.024 | 122.9187 | 122.8867 | 122.7722 | 122.7905 | -122.9507 | -122.9004 | 122.7814 | 122.9279 | 64.2792 | 64.4165
67.0312 | 123.0835 | -64.4073 | 58.4656 | -0.00015269 | 0.00014946 | 0.0019012 | 0.0055179 | -0.0039606 | 0.00084159 | -0.0022324 | -0.071533 | 0.0011408 | -0.00092707 | -0.00068143 | -0.0015573 | -0.00034387 | -0.0013757 | -0.064087 | 58.4656 | -64.5172 | 58.3786 | -64.2105 | -64.6408 | -64.5767 | 0.041199 | 58.4793 | -64.444 | 58.493 | -64.3662 | -64.4714 | -64.2059 | -0.10986 | 0 | -0.086975 | 0.19684 | -0.16937 | -0.23346 | -0.059509 | -0.1236 | -0.036621 | 0.013733 | 0.027466 | 0.041199 | 0.20142 | -0.064087 | 0.23804 | -0.027466 | 0.3067 | 122.8958 | 0.07782 | 122.937 | 122.9828 | 122.9233 | 122.8729 | 122.8867 | -122.9828 | -122.9095 | 122.7859 | 122.9004 | 64.3433 | 64.4485
68.7031 | 123.1064 | -64.4028 | 58.4747 | -0.015411 | 0.0012177 | 0.0033966 | -0.00067711 | 0.0020208 | 0.001269 | 0.0016128 | -0.047119 | 0.0022088 | 0.0024909 | 0.0078634 | 0.0010061 | -0.0014121 | -0.00073494 | -0.059509 | 58.461 | -64.5172 | 58.3878 | -64.2151 | -64.65 | -64.563 | 0.032043 | 58.4747 | -64.4714 | 58.4885 | -64.3478 | -64.4897 | -64.2014 | -0.11444 | -0.013732 | -0.086975 | 0.18768 | -0.16022 | -0.24719 | -0.045776 | -0.13275 | -0.068665 | 0 | 0.013733 | 0.054932 | 0.20142 | -0.086975 | 0.27008 | -0.01831 | 0.30212 | 122.905 | 0.1236 | 122.9599 | 122.9782 | 122.9462 | 122.8638 | 122.8775 | -122.9919 | -122.9462 | 122.7905 | 122.8912 | 64.3433 | 64.4348
70.4375 | 123.1476 | -64.4348 | 58.4061 | -0.023041 | -0.0015595 | 0.0019012 | 0.0014591 | -0.00011542 | 0.00062799 | -9.6154e-05 | 0.016968 | 0.00049983 | 0.0020635 | -0.0013224 | 0.0014335 | -0.0020529 | 0.0014015 | -0.14191 | 58.342 | -64.563 | 58.3969 | -64.1922 | -64.6408 | -64.5218 | 0.018311 | 58.3832 | -64.476 | 58.5251 | -64.2975 | -64.4257 | -64.1602 | -0.12817 | -0.064087 | -0.009155 | 0.24261 | -0.086976 | -0.20599 | 0.041198 | -0.07782 | -0.041199 | -0.022888 | 0.11902 | 0.13733 | 0.27466 | 0.009155 | 0.31586 | 0.050354 | 0.37079 | 122.9599 | 0.17853 | 123.0011 | 122.905 | 122.8592 | 122.7768 | 122.818 | -122.9691 | -122.8821 | 122.8317 | 122.9599 | 64.2929 | 64.4531
72.1875 | 123.0515 | -64.4531 | 58.4427 | -0.076447 | 0.0018585 | 0.0021148 | 0.0033817 | 9.818e-05 | 0.002337 | 0.002681 | -0.071533 | 0.0019952 | 0.0020635 | -0.0038858 | 0.00015167 | -0.0016257 | 0.00076046 | -0.16937 | 58.4381 | -64.5859 | 58.2687 | -64.3616 | -64.7461 | -64.6637 | -0.10986 | 58.4335 | -64.5172 | 58.4152 | -64.4485 | -64.5859 | -64.2563 | -0.13275 | -0.004578 | -0.17395 | 0.091553 | -0.21057 | -0.29297 | -0.07782 | -0.16022 | -0.064087 | -0.009155 | -0.027466 | 0.004578 | 0.19684 | -0.13275 | 0.26093 | -0.068664 | 0.2243 | 122.8546 | 0.068665 | 122.9324 | 123.024 | 122.9507 | 122.8912 | 122.8867 | -123.0286 | -122.9599 | 122.7219 | 122.8683 | 64.2838 | 64.3433
73.8594 | 123.0377 | -64.4348 | 58.4702 | 0.083771 | 0.00036326 | 0.0016876 | 0.0012455 | 0.0024482 | 0.00020079 | 0.002681 | -0.068481 | -0.00056817 | 0.0014227 | 0.0012412 | 0.00057887 | -0.00055747 | -0.0024439 | -0.10071 | 58.4198 | -64.5721 | 58.3282 | -64.2838 | -64.7186 | -64.6362 | -0.064087 | 58.4564 | -64.4943 | 58.4335 | -64.4302 | -64.5493 | -64.2471 | -0.13733 | -0.050354 | -0.14191 | 0.15106 | -0.20142 | -0.28381 | -0.064086 | -0.14648 | -0.05951 | -0.013733 | -0.036621 | 0.004577 | 0.18768 | -0.11444 | 0.24719 | -0.054931 | 0.28839 | 122.9004 | 0.064087 | 122.9279 | 122.9919 | 122.9507 | 122.8546 | 122.8912 | -123.0423 | -122.9645 | 122.7631 | 122.8683 | 64.3341 | 64.3707
75.5938 | 123.1064 | -64.4165 | 58.4564 | 0.015106 | -0.0017731 | 0.001474 | 0.0010319 | -0.0016106 | 0.0016962 | 0.0013992 | -0.050171 | 0.00049983 | -0.00028627 | -0.00025423 | -0.00027553 | -0.0024803 | 0.0031103 | -0.064087 | 58.461 | -64.5538 | 58.3649 | -64.2334 | -64.6408 | -64.5859 | 0.036621 | 58.461 | -64.4577 | 58.4976 | -64.3341 | -64.4577 | -64.1922 | -0.13733 | 0.004578 | -0.091553 | 0.18311 | -0.16937 | -0.2243 | -0.032043 | -0.086975 | -0.041199 | 0.004578 | 0.041199 | 0.082398 | 0.2243 | -0.041199 | 0.2655 | 0 | 0.32044 | 122.9187 | 0.1236 | 122.9553 | 123.0148 | 122.9187 | 122.8775 | 122.8775 | -123.0103 | -122.9141 | 122.7814 | 122.9141 | 64.3524 | 64.4531
77.3281 | 123.0423 | -64.4073 | 58.5205 | 0.053253 | 0.00014946 | -0.00066217 | -0.0019589 | -0.0041742 | 0.00062799 | 0.00075845 | 0.026123 | 0.00028623 | 0.0012091 | -0.004313 | -0.00048913 | -0.0011985 | 0.0046057 | -0.13275 | 58.4335 | -64.5493 | 58.3099 | -64.2517 | -64.6545 | -64.5905 | -0.018311 | 58.5114 | -64.4669 | 58.4427 | -64.3616 | -64.4623 | -64.2014 | -0.14191 | -0.086975 | -0.21057 | 0.15564 | -0.1831 | -0.24719 | -0.041199 | -0.10529 | -0.059509 | -0.009155 | -0.07782 | 0.045777 | 0.20599 | -0.054931 | 0.2655 | 0.004578 | 0.29755 | 122.8592 | 0.10529 | 122.9095 | 122.9828 | 122.9782 | 122.8409 | 122.9187 | -123.0698 | -122.9874 | 122.7173 | 122.85 | 64.2746 | 64.389
79.0625 | 123.1384 | -64.4073 | 58.4244 | -0.023041 | 0.0012177 | 0.0033966 | -0.00046351 | -0.0016106 | 0.0036188 | -0.0015916 | 0.032227 | -0.00035457 | 0.0014227 | -0.0058084 | -6.1934e-05 | -0.0041891 | -0.0045801 | -0.13275 | 58.3832 | -64.5172 | 58.3786 | -64.1739 | -64.65 | -64.5309 | 0.009155 | 58.3786 | -64.4897 | 58.5068 | -64.3295 | -64.4394 | -64.1647 | -0.10986 | -0.041198 | -0.045776 | 0.23346 | -0.1236 | -0.24261 | -0.013733 | -0.13275 | -0.082397 | -0.045776 | 0.082398 | 0.07782 | 0.24262 | -0.032043 | 0.32501 | 0.050354 | 0.34332 | 122.8958 | 0.16022 | 122.9965 | 122.9004 | 122.8683 | 122.7905 | 122.7859 | -122.9416 | -122.9141 | 122.7859 | 122.9141 | 64.2746 | 64.4165
80.75 | 123.0835 | -64.4073 | 58.5022 | 0.015106 | -0.0019867 | 0.0033966 | 0.00060449 | 0.0039436 | -0.00044001 | 0.0033218 | -0.022705 | 0.00092703 | 0.0020635 | -0.0013224 | -0.0019845 | -0.0018393 | 0.00054686 | -0.09613 | 58.461 | -64.5401 | 58.3237 | -64.2838 | -64.6683 | -64.5905 | -0.009155 | 58.4747 | -64.4943 | 58.4473 | -64.3662 | -64.4714 | -64.1968 | -0.13275 | -0.041198 | -0.17853 | 0.1236 | -0.1831 | -0.26093 | -0.050354 | -0.12817 | -0.086975 | -0.027466 | -0.054931 | 0.041199 | 0.21057 | -0.064087 | 0.29755 | 0.022888 | 0.25635 | 122.8638 | 0.12817 | 122.9416 | 123.0011 | 122.9691 | 122.8683 | 122.8821 | -123.0423 | -122.9965 | 122.731 | 122.8546 | 64.3112 | 64.3982
82.4844 | 123.1155 | -64.4211 | 58.4335 | 0.0074768 | -0.0013457 | 0.0021148 | -0.0013181 | 9.818e-05 | 0.0010554 | 0.00097205 | 0.053589 | -0.0020636 | -0.00071347 | -0.0019632 | 0.00015167 | -0.0046165 | 0.0050331 | -0.16937 | 58.3923 | -64.5447 | 58.3466 | -64.2426 | -64.6454 | -64.5447 | -0.045776 | 58.4152 | -64.4852 | 58.4564 | -64.3616 | -64.4348 | -64.1693 | -0.1236 | -0.041199 | -0.086975 | 0.17853 | -0.1236 | -0.2243 | 0 | -0.10071 | -0.064086 | -0.018311 | 0.022888 | 0.05951 | 0.25177 | -0.013732 | 0.31586 | 0.050354 | 0.30212 | 122.8912 | 0.1236 | 122.9416 | 122.937 | 122.9004 | 122.8134 | 122.8363 | -122.9782 | -122.9187 | 122.7676 | 122.8775 | 64.2517 | 64.3753
84.2188 | 123.1064 | -64.4165 | 58.493 | -0.00015269 | -0.00091854 | 0.0012604 | 0.00017729 | 0.0011664 | -0.0015082 | 0.0039626 | -0.016602 | 0.00049983 | 0.00056833 | -0.0023904 | 0.00057887 | -0.00055747 | -0.0011621 | -0.091553 | 58.461 | -64.5493 | 58.3466 | -64.2563 | -64.6454 | -64.5721 | -0.013733 | 58.4976 | -64.4577 | 58.461 | -64.3524 | -64.4714 | -64.1968 | -0.13275 | -0.032043 | -0.14648 | 0.16022 | -0.15564 | -0.22888 | -0.022889 | -0.096131 | -0.041199 | 0.004578 | -0.032043 | 0.064087 | 0.21973 | -0.054932 | 0.26093 | -0.013733 | 0.29297 | 122.8958 | 0.10529 | 122.9187 | 123.0103 | 122.9553 | 122.8775 | 122.9141 | -123.0423 | -122.9507 | 122.7631 | 122.8775 | 64.325 | 64.4028
85.9531 | 123.1705 | -64.4485 | 58.4244 | -0.00015269 | 0.00014946 | 0.002542 | 0.00039089 | 0.0037298 | 0.0014826 | -0.00030975 | -0.019653 | -0.00014097 | 0.0016363 | -0.001536 | 0.00036527 | -0.0020529 | -0.0018029 | -0.16937 | 58.4198 | -64.5676 | 58.3603 | -64.2563 | -64.6591 | -64.5676 | -0.027466 | 58.3878 | -64.5035 | 58.5114 | -64.3433 | -64.4485 | -64.151 | -0.11902 | -0.004577 | -0.064086 | 0.19226 | -0.11902 | -0.21057 | 0 | -0.091553 | -0.054932 | -0.036621 | 0.086976 | 0.10529 | 0.29755 | 0 | 0.35248 | 0.054932 | 0.31128 | 122.9279 | 0.16022 | 123.0148 | 122.9874 | 122.8912 | 122.8683 | 122.8363 | -122.9919 | -122.9279 | 122.8088 | 122.9599 | 64.2792 | 64.4211
87.6406 | 123.024 | -64.4394 | 58.4656 | 0.045624 | 0.00079046 | 0.0040374 | -3.6308e-05 | 0.0015936 | 0.0027644 | -0.0011642 | -0.056274 | -0.00014097 | 0.0016363 | 0.00038657 | 0.0010061 | -0.0033347 | -0.0032983 | -0.14648 | 58.461 | -64.5584 | 58.2825 | -64.3295 | -64.7461 | -64.6591 | -0.11444 | 58.4473 | -64.5126 | 58.3832 | -64.4623 | -64.595 | -64.2838 | -0.11902 | -0.004577 | -0.1831 | 0.10986 | -0.21973 | -0.3067 | -0.10071 | -0.18768 | -0.073242 | -0.01831 | -0.082397 | -0.022888 | 0.15564 | -0.15564 | 0.22888 | -0.082398 | 0.22888 | 122.8409 | 0.050354 | 122.8958 | 123.0194 | 122.9599 | 122.9004 | 122.8867 | -123.024 | -122.9782 | 122.7219 | 122.8226 | 64.2929 | 64.325
89.375 | 123.0835 | -64.4165 | 58.4885 | 0.060882 | 0.0016449 | 0.0038238 | 0.00060449 | 0.0018072 | 0.0010554 | 0.00011745 | 0.010864 | 0.00071343 | -0.00028627 | -0.0011086 | 0.0020743 | -0.0016257 | -0.0028711 | -0.086975 | 58.4839 | -64.5401 | 58.3282 | -64.2654 | -64.6454 | -64.5767 | -0.022888 | 58.4656 | -64.4714 | 58.4793 | -64.3524 | -64.4623 | -64.2014 | -0.1236 | -0.004577 | -0.16022 | 0.15106 | -0.16022 | -0.22888 | -0.036621 | -0.10529 | -0.054932 | -0.022888 | -0.009155 | 0.064087 | 0.21515 | -0.045776 | 0.27008 | 0.009156 | 0.27466 | 122.8683 | 0.11902 | 122.9507 | 123.024 | 122.937 | 122.9004 | 122.8821 | -123.0286 | -122.9599 | 122.7448 | 122.8958 | 64.3295 | 64.3936
91.1094 | 123.0789 | -64.4073 | 58.4656 | -0.015411 | -0.0017731 | 0.0012604 | 0.00039089 | -0.003106 | 0.00041439 | 0.0035354 | 0.047485 | -0.00014097 | 0.00099553 | -0.002604 | 0.0010061 | -0.00077127 | -9.3938e-05 | -0.041199 | 58.4152 | -64.4852 | 58.4152 | -64.1647 | -64.563 | -64.5035 | 0.045776 | 58.4518 | -64.4348 | 58.4793 | -64.3204 | -64.4165 | -64.1739 | -0.077819 | -0.050354 | -0.050354 | 0.24262 | -0.09613 | -0.15564 | -0.018311 | -0.07782 | -0.027465 | -0.013733 | 0.013733 | 0.086975 | 0.23346 | -0.009155 | 0.26093 | 0.01831 | 0.32043 | 122.9004 | 0.11444 | 122.9141 | 122.9004 | 122.8867 | 122.8226 | 122.8592 | -122.9507 | -122.9004 | 122.8226 | 122.8867 | 64.3661 | 64.4531
92.7812 | 123.1201 | -64.4211 | 58.4198 | -0.0077822 | -0.0028411 | 0.0021148 | -0.0013181 | -0.001397 | 0.0010554 | 0.0018264 | 0.053589 | -0.00078177 | 0.0027045 | -0.0055948 | -0.0011301 | -0.0016257 | -0.0030847 | -0.19226 | 58.3878 | -64.5538 | 58.3374 | -64.2334 | -64.6637 | -64.5447 | -0.054932 | 58.4061 | -64.4897 | 58.4747 | -64.3478 | -64.4394 | -64.1785 | -0.13275 | -0.032044 | -0.082398 | 0.18768 | -0.1236 | -0.24261 | 0.009155 | -0.10986 | -0.068664 | -0.013733 | 0.054931 | 0.073243 | 0.24262 | -0.01831 | 0.31128 | 0.050354 | 0.32044 | 122.8912 | 0.14191 | 122.9645 | 122.9416 | 122.8958 | 122.8088 | 122.8271 | -122.9736 | -122.9095 | 122.7585 | 122.8958 | 64.2288 | 64.3662
94.5156 | 123.0743 | -64.4394 | 58.4427 | 0.022736 | 0.00014946 | 0.0029694 | 0.0023135 | 0.0039436 | 0.00062799 | 0.00054465 | -0.037964 | 0.00071343 | 0.0022773 | 0.0012412 | -0.0013437 | -0.00034387 | -0.00030754 | -0.16937 | 58.4427 | -64.5859 | 58.287 | -64.3204 | -64.7507 | -64.65 | -0.10529 | 58.4473 | -64.5126 | 58.429 | -64.4302 | -64.5493 | -64.2471 | -0.14648 | 0 | -0.15564 | 0.11902 | -0.21057 | -0.31128 | -0.064087 | -0.16479 | -0.073242 | 0.004578 | -0.013733 | 0.009155 | 0.19226 | -0.10986 | 0.2655 | -0.036621 | 0.2655 | 122.8729 | 0.082397 | 122.9416 | 123.0286 | 122.9599 | 122.8821 | 122.8867 | -123.0286 | -122.9553 | 122.7264 | 122.8683 | 64.27 | 64.3341
96.25 | 123.0927 | -64.4257 | 58.4976 | 0.053253 | 0.00057686 | 0.0016876 | 0.0012455 | 0.0033026 | 0.0014826 | 0.00075845 | -0.010498 | 0.0022088 | 0.00099553 | 0.0031638 | -0.00027553 | -0.0016257 | -0.0062891 | -0.073242 | 58.461 | -64.5264 | 58.3649 | -64.2242 | -64.6271 | -64.563 | 0.022888 | 58.4702 | -64.4623 | 58.4793 | -64.3433 | -64.4623 | -64.1876 | -0.10071 | -0.036621 | -0.13275 | 0.20142 | -0.13733 | -0.20142 | -0.036621 | -0.10071 | -0.036621 | -0.027466 | -0.018311 | 0.082397 | 0.23804 | -0.036621 | 0.27466 | 0 | 0.30212 | 122.8912 | 0.11902 | 122.9416 | 122.9874 | 122.9324 | 122.8867 | 122.8958 | -123.024 | -122.9599 | 122.7905 | 122.905 | 64.3524 | 64.4485
97.9219 | 123.056 | -64.4119 | 58.5114 | -0.0077822 | 0.0018585 | 0.002542 | 0.00039089 | -0.0011834 | -0.001081 | 0.00011745 | 0.035278 | 0.00049983 | 0.0014227 | -0.0036722 | 0.00015167 | -0.0014121 | 0.00011966 | -0.082397 | 58.4381 | -64.5218 | 58.374 | -64.2105 | -64.6225 | -64.5401 | 0 | 58.4793 | -64.4577 | 58.4427 | -64.3524 | -64.4623 | -64.238 | -0.10986 | -0.073243 | -0.13733 | 0.20142 | -0.12817 | -0.21057 | -0.01831 | -0.10071 | -0.045777 | -0.032044 | -0.068665 | 0.059509 | 0.17395 | -0.050354 | 0.21973 | -0.004577 | 0.31128 | 122.8958 | 0.10529 | 122.9004 | 122.9599 | 122.937 | 122.85 | 122.8912 | -123.0331 | -122.9691 | 122.7859 | 122.8546 | 64.3295 | 64.4119
99.6562 | 123.1842 | -64.4302 | 58.4198 | -0.023041 | 0.0022859 | 0.0029694 | 0.0014591 | 0.00073918 | 0.0014826 | 0.00054465 | 0.010864 | -0.00056817 | 0.0016363 | 0.00017297 | -0.00070273 | -0.0020529 | 0.0011877 | -0.13733 | 58.3649 | -64.5447 | 58.374 | -64.1968 | -64.6317 | -64.5447 | 0.018311 | 58.374 | -64.4897 | 58.5251 | -64.3112 | -64.4165 | -64.1281 | -0.11444 | -0.054932 | -0.045777 | 0.23346 | -0.11444 | -0.20142 | 0 | -0.086975 | -0.059509 | -0.045777 | 0.10528 | 0.11902 | 0.30212 | 0.013733 | 0.36163 | 0.073242 | 0.3479 | 122.9187 | 0.17853 | 123.0148 | 122.9095 | 122.8638 | 122.7951 | 122.8043 | -122.9645 | -122.9095 | 122.8043 | 122.9553 | 64.2929 | 64.4485
101.4062 | 123.0423 | -64.3845 | 58.5159 | 0.060882 | -0.0015595 | 0.0010468 | 0.00060449 | -0.00054262 | 0.00062799 | 0.00033105 | 0.026123 | 0.0019952 | 0.0024909 | 0.0023092 | 0.00036527 | -0.0014121 | -0.0024439 | -0.10986 | 58.461 | -64.5538 | 58.342 | -64.27 | -64.6454 | -64.595 | -0.013733 | 58.493 | -64.444 | 58.4427 | -64.389 | -64.4806 | -64.2151 | -0.16937 | -0.054931 | -0.17395 | 0.11444 | -0.21057 | -0.26093 | -0.041199 | -0.091553 | -0.05951 | -0.022888 | -0.073242 | -0.004578 | 0.16937 | -0.096131 | 0.22888 | -0.036621 | 0.28381 | 122.8958 | 0.054932 | 122.8867 | 123.0148 | 122.937 | 122.8455 | 122.8775 | -123.0698 | -122.9599 | 122.7264 | 122.8271 | 64.2746 | 64.3707
103.0781 | 123.1796 | -64.3662 | 58.4564 | -0.00015269 | -0.0030547 | 0.0012604 | -0.0017453 | -0.0069512 | -0.0015082 | 0.0011856 | 0.081055 | -0.00035457 | 0.0014227 | -0.0045266 | 0.00079247 | -0.0026939 | 0.0011877 | -0.091553 | 58.3923 | -64.5309 | 58.4381 | -64.119 | -64.5493 | -64.4485 | 0.1236 | 58.4427 | -64.4348 | 58.5663 | -64.2334 | -64.3433 | -64.1052 | -0.16479 | -0.064087 | -0.018311 | 0.24719 | -0.082397 | -0.1831 | 0.082398 | -0.01831 | -0.068664 | -0.013733 | 0.10986 | 0.13275 | 0.26093 | 0.022888 | 0.32959 | 0.091552 | 0.41199 | 122.9691 | 0.20142 | 123.0011 | 122.9233 | 122.8775 | 122.7585 | 122.8088 | -122.9874 | -122.8912 | 122.8043 | 122.9324 | 64.2746 | 64.4897
104.8125 | 123.1659 | -64.4165 | 58.4106 | -0.023041 | 0.0024995 | 0.0010468 | 0.00039089 | 9.818e-05 | -0.00044001 | -0.00052335 | -0.01355 | 0.00071343 | 0.00014093 | -0.0036722 | -0.0021981 | -0.0014121 | 0.0022559 | -0.11902 | 58.374 | -64.5538 | 58.3923 | -64.1968 | -64.6408 | -64.5355 | 0.018311 | 58.3603 | -64.4897 | 58.5297 | -64.3066 | -64.4302 | -64.1556 | -0.13733 | -0.036622 | -0.018311 | 0.21973 | -0.11902 | -0.2243 | 0.018311 | -0.086975 | -0.073242 | -0.050354 | 0.11902 | 0.10986 | 0.26093 | -0.013733 | 0.33417 | 0.059509 | 0.35706 | 122.9462 | 0.1831 | 123.0194 | 122.9279 | 122.85 | 122.7905 | 122.7768 | -122.9645 | -122.9004 | 122.8088 | 122.9462 | 64.2975 | 64.4348
106.5625 | 123.0515 | -64.4577 | 58.4564 | 0.015106 | 0.0031403 | 0.004251 | 0.0020999 | -0.00075622 | 0.00041439 | -9.6154e-05 | -0.06543 | 0.00092703 | 0.0014227 | 0.0057272 | -0.00027553 | -0.0020529 | -0.00073494 | -0.10529 | 58.4518 | -64.5584 | 58.3374 | -64.2883 | -64.7049 | -64.6271 | -0.054932 | 58.4747 | -64.5035 | 58.4198 | -64.4348 | -64.5447 | -64.2609 | -0.10071 | -0.004578 | -0.11902 | 0.16937 | -0.16937 | -0.24719 | -0.068664 | -0.14648 | -0.045776 | 0.01831 | -0.036621 | 0.022889 | 0.19684 | -0.086975 | 0.24262 | -0.041199 | 0.27008 | 122.8958 | 0.068665 | 122.9233 | 123.0103 | 122.9782 | 122.9095 | 122.9324 | -123.0148 | -122.9599 | 122.7951 | 122.8775 | 64.3524 | 64.4028
108.2812 | 123.1247 | -64.4394 | 58.429 | -0.023041 | -0.0013457 | 0.00040583 | 0.00039089 | -0.0016106 | -0.00065361 | -0.00030975 | 0.068848 | -0.00014097 | 0.0018499 | -0.0058084 | -0.00070273 | -0.0037619 | -0.0030847 | -0.18768 | 58.4198 | -64.5401 | 58.3511 | -64.2426 | -64.6591 | -64.5493 | -0.045776 | 58.4106 | -64.4989 | 58.461 | -64.3387 | -64.444 | -64.1739 | -0.10071 | -0.009155 | -0.07782 | 0.19684 | -0.10986 | -0.21973 | -0.009155 | -0.11902 | -0.059509 | -0.01831 | 0.032044 | 0.10071 | 0.2655 | -0.004578 | 0.32501 | 0.054931 | 0.29755 | 122.8912 | 0.16022 | 122.9599 | 122.9599 | 122.9095 | 122.8592 | 122.85 | -122.9691 | -122.9279 | 122.7905 | 122.9004 | 64.2517 | 64.3936
109.9531 | 123.1293 | -64.4028 | 58.429 | 0.0074768 | -0.0028411 | 0.00083303 | -0.0025997 | -0.0016106 | 0.0014826 | 0.0011856 | 0.050537 | -0.00014097 | 0.00056833 | -0.0011086 | 0.0016471 | -0.0039755 | 0.00097406 | -0.17395 | 58.4061 | -64.5264 | 58.3511 | -64.2288 | -64.65 | -64.5493 | -0.036621 | 58.4106 | -64.4852 | 58.4747 | -64.3524 | -64.444 | -64.183 | -0.1236 | -0.022888 | -0.07782 | 0.17395 | -0.14648 | -0.24719 | -0.022888 | -0.1236 | -0.082397 | -0.01831 | 0.045776 | 0.050354 | 0.21973 | -0.041199 | 0.30212 | 0.041198 | 0.29755 | 122.8775 | 0.13275 | 122.9599 | 122.9324 | 122.8958 | 122.8088 | 122.8134 | -122.9553 | -122.9141 | 122.7539 | 122.8775 | 64.2288 | 64.3662
111.6875 | 123.056 | -64.4577 | 58.461 | 0.022736 | 0.00014946 | 0.0023284 | 0.0029545 | 9.818e-05 | 0.0010554 | 0.00033105 | -0.068481 | 0.0019952 | 0.00035453 | 0.0014548 | -0.0013437 | -0.00055747 | -0.0011621 | -0.16479 | 58.4473 | -64.5767 | 58.2687 | -64.3662 | -64.7781 | -64.6545 | -0.11444 | 58.4702 | -64.5218 | 58.4198 | -64.4531 | -64.563 | -64.27 | -0.11902 | -0.013733 | -0.19226 | 0.091553 | -0.19684 | -0.32043 | -0.07782 | -0.20142 | -0.064087 | 0.009155 | -0.041199 | 0.004578 | 0.18768 | -0.10529 | 0.25177 | -0.041198 | 0.21057 | 122.8455 | 0.068665 | 122.9416 | 123.024 | 122.9919 | 122.905 | 122.9279 | -123.0377 | -122.9828 | 122.7264 | 122.8775 | 64.2929 | 64.3433
113.4375 | 123.0515 | -64.4211 | 58.4702 | 0.0074768 | -0.00070494 | 0.00083303 | 0.0044497 | 0.0024482 | 0.0010554 | 0.00011745 | -0.062378 | 7.2626e-05 | 0.0020635 | -0.0021768 | -0.00070273 | -0.0011985 | 0.0018287 | -0.073242 | 58.4747 | -64.563 | 58.3557 | -64.2746 | -64.6957 | -64.6042 | -0.004578 | 58.4656 | -64.4897 | 58.4427 | -64.3936 | -64.5218 | -64.2197 | -0.14191 | 0.004577 | -0.11444 | 0.14648 | -0.1831 | -0.27466 | -0.041199 | -0.13275 | -0.068664 | -0.004578 | -0.027466 | 0.027466 | 0.20142 | -0.10071 | 0.27008 | -0.032044 | 0.28839 | 122.9187 | 0.09613 | 122.9324 | 123.0377 | 122.9553 | 122.8958 | 122.8867 | -123.0331 | -122.9599 | 122.7768 | 122.8638 | 64.3478 | 64.4165
115.1719 | 123.1247 | -64.4073 | 58.4198 | 0.015106 | -0.0013457 | -0.00066217 | -0.0036679 | -0.0011834 | 0.00084159 | 0.0013992 | 0.041382 | -0.00078177 | 0.00078193 | -0.0092264 | -0.00070273 | -0.0016257 | -0.0015893 | -0.17853 | 58.3878 | -64.5493 | 58.3557 | -64.2426 | -64.6454 | -64.5447 | -0.059509 | 58.4106 | -64.4806 | 58.4702 | -64.3524 | -64.444 | -64.1739 | -0.14191 | -0.032044 | -0.064087 | 0.16479 | -0.13733 | -0.23804 | 0.004577 | -0.096131 | -0.073242 | -0.009155 | 0.050354 | 0.054932 | 0.23346 | -0.036621 | 0.3067 | 0.036621 | 0.3067 | 122.905 | 0.12817 | 122.9507 | 122.937 | 122.8912 | 122.7951 | 122.818 | -122.9691 | -122.9004 | 122.7631 | 122.8775 | 64.2288 | 64.3478
116.8594 | 123.0606 | -64.4623 | 58.4564 | 0.015106 | 0.0037811 | 0.0021148 | 0.0027407 | 0.00095278 | 0.0027644 | 0.0016128 | -0.059326 | 0.0017816 | 0.00078193 | 0.0016684 | -0.0019845 | -0.0024803 | -0.00073494 | -0.1831 | 58.4381 | -64.595 | 58.2825 | -64.3387 | -64.7552 | -64.6317 | -0.10071 | 58.4427 | -64.5081 | 58.4381 | -64.4394 | -64.5447 | -64.2563 | -0.13275 | -0.018311 | -0.17395 | 0.1236 | -0.16937 | -0.29297 | -0.036621 | -0.16022 | -0.045777 | -0.013733 | -0.018311 | 0.022888 | 0.20599 | -0.082398 | 0.25177 | -0.036621 | 0.25635 | 122.8775 | 0.068665 | 122.9462 | 123.0331 | 122.9507 | 122.9004 | 122.905 | -123.0515 | -122.9645 | 122.7448 | 122.9004 | 64.2792 | 64.3616
118.5938 | 123.175 | -64.3982 | 58.4518 | -0.0077822 | -0.0026275 | 0.0012604 | -0.0021725 | 0.00138 | -0.00044001 | 0.0013992 | 0.056641 | -0.00078177 | -7.2674e-05 | -0.0038858 | 0.0010061 | -0.0024803 | 0.00011966 | -0.16479 | 58.4106 | -64.5538 | 58.3786 | -64.2059 | -64.5996 | -64.5218 | 0.027466 | 58.3969 | -64.4806 | 58.5022 | -64.2792 | -64.3662 | -64.1281 | -0.15564 | -0.041198 | -0.073242 | 0.19226 | -0.1236 | -0.20142 | 0.032043 | -0.045776 | -0.082398 | -0.054931 | 0.050354 | 0.11902 | 0.27008 | 0.032043 | 0.35248 | 0.11444 | 0.3479 | 122.9324 | 0.20142 | 122.9828 | 122.9645 | 122.8775 | 122.8088 | 122.7951 | -123.0057 | -122.9324 | 122.7768 | 122.9004 | 64.2334 | 64.4257
120.3281 | 123.056 | -64.4257 | 58.4976 | 0.060882 | -0.0011321 | -0.00044857 | 0.00081809 | 0.0018072 | -0.0032172 | 0.0016128 | -0.028809 | 0.00028623 | 0.0035589 | 0.001882 | -0.00027553 | -0.0014121 | 0.00097406 | -0.10986 | 58.4747 | -64.5264 | 58.3191 | -64.2883 | -64.6683 | -64.5859 | -0.027466 | 58.5114 | -64.4577 | 58.4427 | -64.3799 | -64.476 | -64.2242 | -0.10071 | -0.022889 | -0.17853 | 0.13733 | -0.16022 | -0.24262 | -0.059509 | -0.14191 | -0.032044 | 0.013733 | -0.054932 | 0.045776 | 0.20142 | -0.050354 | 0.23346 | -0.01831 | 0.23804 | 122.8455 | 0.07782 | 122.9004 | 123.0011 | 122.9691 | 122.9004 | 122.937 | -123.024 | -122.9553 | 122.7448 | 122.8683 | 64.3158 | 64.3982
122 | 123.0789 | -64.4577 | 58.4564 | -0.053558 | -0.00070494 | 0.0012604 | 0.0038089 | -0.00032902 | 0.0014826 | 0.00097205 | -0.037964 | 0.00071343 | 0.0022773 | 0.0012412 | 0.00036527 | -0.00055747 | 0.00011966 | -0.17853 | 58.4335 | -64.5767 | 58.287 | -64.3295 | -64.7598 | -64.6454 | -0.09613 | 58.4381 | -64.5081 | 58.4198 | -64.4348 | -64.5447 | -64.2517 | -0.11902 | -0.022888 | -0.16937 | 0.12817 | -0.18768 | -0.30212 | -0.068665 | -0.18311 | -0.050354 | -0.018311 | -0.036621 | 0.022889 | 0.20599 | -0.086975 | 0.25635 | -0.036621 | 0.24719 | 122.8638 | 0.073243 | 122.9279 | 123.0103 | 122.9462 | 122.8912 | 122.8958 | -123.0331 | -122.9645 | 122.7448 | 122.8775 | 64.2792 | 64.3616
123.7188 | 123.1247 | -64.4119 | 58.4244 | 0.015106 | -0.00091854 | 0.0019012 | 0.00060449 | 0.00095278 | -0.0030036 | 0.0011856 | 0.023071 | -0.0014228 | 0.0016363 | -0.0021768 | 0.00057887 | -0.0035483 | -0.00073494 | -0.17395 | 58.3832 | -64.563 | 58.3649 | -64.2242 | -64.65 | -64.5401 | -0.018311 | 58.4061 | -64.476 | 58.4885 | -64.3387 | -64.444 | -64.183 | -0.15106 | -0.041198 | -0.059509 | 0.18768 | -0.12817 | -0.23804 | 0.022888 | -0.086975 | -0.064087 | -0.01831 | 0.064087 | 0.073242 | 0.22888 | -0.032044 | 0.29297 | 0.032043 | 0.33875 | 122.9279 | 0.13733 | 122.9645 | 122.9462 | 122.8821 | 122.7951 | 122.818 | -122.9874 | -122.9004 | 122.7768 | 122.9004 | 64.238 | 64.3936
125.4531 | 123.0927 | -64.4165 | 58.461 | 0.037994 | -0.00070494 | 0.0019012 | 0.0018863 | -0.0024652 | 0.0019098 | 0.0022536 | -0.053223 | 0.0022088 | 0.0020635 | -0.0038858 | -0.0013437 | 0.00051053 | 0.0011877 | -0.073242 | 58.4747 | -64.5401 | 58.3557 | -64.2471 | -64.65 | -64.5676 | 0.032043 | 58.4747 | -64.4623 | 58.4839 | -64.3341 | -64.4577 | -64.1876 | -0.1236 | 0.013732 | -0.10529 | 0.16937 | -0.15106 | -0.23346 | -0.027466 | -0.10986 | -0.045776 | 0.013732 | 0.022888 | 0.082398 | 0.22888 | -0.041199 | 0.27466 | 0.004577 | 0.29297 | 122.8958 | 0.12817 | 122.9462 | 123.0148 | 122.937 | 122.8912 | 122.8912 | -123.0011 | -122.9233 | 122.7722 | 122.9004 | 64.3433 | 64.4485
127.2031 | 123.056 | -64.4028 | 58.5297 | 0.045624 | -0.0026275 | 0.00040583 | -0.00024991 | -0.0011834 | 0.00041439 | 0.00054465 | 0.026123 | 0.00092703 | 0.0029181 | -0.001536 | 0.0012199 | -0.0026939 | 0.0016151 | -0.11444 | 58.461 | -64.5309 | 58.3191 | -64.2609 | -64.65 | -64.5721 | -0.009155 | 58.4793 | -64.4531 | 58.461 | -64.3662 | -64.4669 | -64.2105 | -0.12817 | -0.068664 | -0.21057 | 0.14191 | -0.16937 | -0.24719 | -0.041199 | -0.11902 | -0.050354 | -0.050354 | -0.068664 | 0.036621 | 0.19226 | -0.064087 | 0.24262 | -0.013733 | 0.27008 | 122.85 | 0.086975 | 122.9141 | 122.9919 | 122.9324 | 122.8638 | 122.8821 | -123.0606 | -122.9828 | 122.7219 | 122.8638 | 64.2883 | 64.3936
128.875 | 123.056 | -64.3707 | 58.5114 | 0.022736 | -0.00091854 | 0.0010468 | -0.00067711 | -0.0028924 | -0.0017218 | -0.0011642 | 0.026123 | -0.00078177 | 0.00099553 | -0.0053812 | -0.00070273 | -0.0020529 | -0.0013757 | -0.10071 | 58.4976 | -64.4806 | 58.3374 | -64.2334 | -64.6362 | -64.5584 | -0.013733 | 58.5342 | -64.4669 | 58.461 | -64.3707 | -64.4577 | -64.2151 | -0.10986 | -0.013733 | -0.17395 | 0.13733 | -0.18768 | -0.2655 | -0.07782 | -0.15564 | -0.09613 | 0.022888 | -0.050354 | 0 | 0.15564 | -0.086975 | 0.25177 | 0.009155 | 0.24719 | 122.818 | 0.09613 | 122.9279 | 122.9782 | 123.0011 | 122.8683 | 122.905 | -122.9919 | -122.9782 | 122.7081 | 122.8317 | 64.27 | 64.357
130.6094 | 123.0972 | -64.4028 | 58.5205 | 0.076141 | -0.0011321 | -2.1372e-05 | 0.0010319 | 9.818e-05 | 0.0010554 | 0.0018264 | -0.03186 | 0.00049983 | -7.2674e-05 | 0.00017297 | -0.00048913 | -0.00034387 | -0.0035119 | -0.09613 | 58.4793 | -64.5126 | 58.3466 | -64.2471 | -64.6408 | -64.5721 | -0.009155 | 58.548 | -64.4348 | 58.4793 | -64.3478 | -64.4394 | -64.1739 | -0.10986 | -0.041199 | -0.17395 | 0.15564 | -0.16937 | -0.23804 | -0.05951 | -0.12817 | -0.032043 | 0.027466 | -0.041199 | 0.054932 | 0.22888 | -0.036621 | 0.26093 | -0.004578 | 0.2655 | 122.8592 | 0.086975 | 122.9141 | 122.9919 | 122.9828 | 122.8821 | 122.9507 | -123.0331 | -122.9553 | 122.7493 | 122.8821 | 64.3066 | 64.3936
132.2812 | 123.1522 | -64.3478 | 58.4564 | -0.023041 | 0.00079046 | 0.0051056 | -3.6308e-05 | 0.0022346 | 0.0049006 | -0.00052335 | -0.016602 | 0.00049983 | 0.0024909 | 0.0014548 | -0.00091653 | -0.0011985 | -9.3938e-05 | -0.16479 | 58.4839 | -64.4897 | 58.3923 | -64.1739 | -64.6408 | -64.5264 | -0.036621 | 58.4747 | -64.4257 | 58.5617 | -64.27 | -64.3845 | -64.0915 | -0.14191 | 0.027466 | -0.064087 | 0.17395 | -0.17853 | -0.29297 | -0.036621 | -0.15106 | -0.07782 | 0.01831 | 0.10529 | 0.077819 | 0.25635 | -0.036621 | 0.33417 | 0.041199 | 0.31586 | 122.8821 | 0.15564 | 122.9874 | 122.9736 | 122.9004 | 122.8317 | 122.8226 | -122.9462 | -122.8821 | 122.7402 | 122.9095 | 64.183 | 64.3112
133.9531 | 123.0698 | -64.3433 | 58.548 | 0.0074768 | -6.4144e-05 | 0.0019012 | 0.0023135 | 0.0039436 | -0.00044001 | 0.0011856 | -0.062378 | -0.00185 | 0.0033453 | 0.0044456 | -0.0011301 | -0.00098487 | 0.0031103 | -0.082397 | 58.5114 | -64.4806 | 58.4152 | -64.1373 | -64.6042 | -64.5264 | -0.018311 | 58.5434 | -64.4348 | 58.5159 | -64.3524 | -64.4485 | -64.1602 | -0.13733 | -0.036621 | -0.13275 | 0.20599 | -0.1831 | -0.26093 | -0.045776 | -0.1236 | -0.091552 | -0.004578 | -0.032044 | -0.009155 | 0.18311 | -0.10529 | 0.27466 | -0.013733 | 0.34332 | 122.8958 | 0.082397 | 122.9507 | 122.9919 | 122.9782 | 122.8546 | 122.8867 | -123.0286 | -122.9828 | 122.7585 | 122.8592 | 64.2609 | 64.325
135.6875 | 123.1888 | -64.2838 | 58.5297 | 0.037994 | -0.0011321 | 0.002542 | -0.0011045 | 0.00031198 | 0.0019098 | 0.0018264 | 0.087158 | 0.0013544 | 0.0020635 | 0.0012412 | 0.0022879 | -0.0024803 | 0.0011877 | -0.10529 | 58.5022 | -64.4257 | 58.5114 | -63.9908 | -64.4714 | -64.3936 | 0.10529 | 58.5159 | -64.3753 | 58.6441 | -64.1693 | -64.2471 | -64.0274 | -0.14191 | -0.027466 | -0.01831 | 0.29297 | -0.10986 | -0.18768 | 0.032043 | -0.045777 | -0.091553 | -0.013733 | 0.11444 | 0.11444 | 0.25635 | 0.036621 | 0.3479 | 0.12817 | 0.43487 | 122.937 | 0.20599 | 123.0194 | 122.9279 | 122.8912 | 122.7859 | 122.7997 | -122.9553 | -122.905 | 122.7951 | 122.9279 | 64.1785 | 64.389
137.3594 | 123.0698 | -64.357 | 58.5892 | -0.00015269 | -0.0013457 | 0.0010468 | -0.0021725 | -0.0026788 | -0.00022641 | -0.0011642 | -0.010498 | 0.00092703 | 0.00035453 | -0.003245 | 0.0018607 | -0.0016257 | 0.0033241 | -0.09613 | 58.5617 | -64.444 | 58.4106 | -64.1602 | -64.5905 | -64.5264 | -0.022888 | 58.5709 | -64.4211 | 58.5114 | -64.2975 | -64.4119 | -64.1418 | -0.086975 | -0.027465 | -0.17853 | 0.19684 | -0.16937 | -0.23346 | -0.082397 | -0.14648 | -0.064087 | -0.01831 | -0.077819 | 0.05951 | 0.21515 | -0.054931 | 0.27924 | 0.009156 | 0.28381 | 122.8546 | 0.1236 | 122.9324 | 123.0057 | 122.9919 | 122.9187 | 122.9279 | -123.0331 | -123.0103 | 122.7676 | 122.8683 | 64.2609 | 64.3341
139.0938 | 123.0515 | -64.3845 | 58.4885 | -0.0383 | 0.0012177 | 0.0010468 | 0.0012455 | 0.0011664 | 0.00020079 | -9.6154e-05 | -0.028809 | 0.001568 | 0.0022773 | 0.007009 | 0.00079247 | -0.0018393 | 0.0024695 | -0.17395 | 58.493 | -64.5309 | 58.3374 | -64.2471 | -64.6866 | -64.5813 | -0.10071 | 58.4747 | -64.4394 | 58.4839 | -64.3845 | -64.4897 | -64.1876 | -0.14648 | 0.004578 | -0.15106 | 0.13733 | -0.19684 | -0.30212 | -0.050354 | -0.15564 | -0.054932 | -0.013733 | -0.004577 | 0 | 0.19684 | -0.10529 | 0.25177 | -0.050354 | 0.28381 | 122.8683 | 0.054932 | 122.9233 | 123.024 | 122.9141 | 122.8775 | 122.8592 | -123.0194 | -122.9279 | 122.7219 | 122.8683 | 64.2105 | 64.2838
140.8281 | 123.0469 | -64.325 | 58.5571 | 0.037994 | -0.0015595 | 0.0012604 | -0.0013181 | -0.0016106 | -0.00044001 | 0.00033105 | 0.013916 | -0.00056817 | -7.2674e-05 | -0.004313 | 0.0016471 | -0.0037619 | 0.00033326 | -0.13275 | 58.5022 | -64.476 | 58.3786 | -64.1739 | -64.595 | -64.5264 | -0.013733 | 58.5297 | -64.4119 | 58.4885 | -64.325 | -64.4257 | -64.1556 | -0.15106 | -0.054932 | -0.17853 | 0.15106 | -0.20142 | -0.27008 | -0.050354 | -0.11902 | -0.086975 | -0.027466 | -0.068665 | 0 | 0.16937 | -0.10071 | 0.25635 | -0.013733 | 0.30212 | 122.8546 | 0.086975 | 122.9004 | 122.9782 | 122.9416 | 122.8271 | 122.8546 | -123.0331 | -122.9691 | 122.7036 | 122.8134 | 64.1922 | 64.3112
142.5625 | 123.0652 | -64.3524 | 58.5114 | 0.060882 | -0.00027774 | 0.001474 | -0.00024991 | 0.0020208 | 0.00084159 | 0.00097205 | -0.047119 | 7.2626e-05 | 0.0018499 | 0.0033774 | -0.0017709 | -0.0035483 | 0.0024695 | -0.059509 | 58.5022 | -64.4852 | 58.4152 | -64.1556 | -64.6271 | -64.5401 | 0.032043 | 58.5114 | -64.4211 | 58.5159 | -64.3295 | -64.444 | -64.1418 | -0.13275 | -0.009156 | -0.096131 | 0.19684 | -0.18768 | -0.27466 | -0.054932 | -0.14191 | -0.068665 | 0 | 0.004577 | 0.022888 | 0.21057 | -0.091553 | 0.27924 | -0.022888 | 0.32959 | 122.9004 | 0.091553 | 122.937 | 122.9874 | 122.9324 | 122.8546 | 122.8638 | -122.9965 | -122.9324 | 122.7676 | 122.8683 | 64.2929 | 64.3845
144.2344 | 123.056 | -64.3524 | 58.58 | 0.045624 | -0.00091854 | -2.1372e-05 | -0.0017453 | -0.00054262 | -0.0012946 | -0.00052335 | 0.02002 | 0.0011408 | 0.0022773 | -0.001536 | 0.00015167 | -0.0026939 | 0.0033241 | -0.13275 | 58.548 | -64.4714 | 58.3923 | -64.151 | -64.5859 | -64.5126 | -0.009155 | 58.5663 | -64.4028 | 58.5114 | -64.2792 | -64.3936 | -64.1418 | -0.11902 | -0.032043 | -0.18768 | 0.20142 | -0.16022 | -0.23346 | -0.041198 | -0.11444 | -0.050354 | -0.013733 | -0.068664 | 0.073242 | 0.21057 | -0.041199 | 0.26093 | 0.009155 | 0.32044 | 122.8638 | 0.1236 | 122.9141 | 123.0194 | 122.9691 | 122.9004 | 122.9187 | -123.0515 | -122.9828 | 122.7448 | 122.8638 | 64.2197 | 64.3433
145.9688 | 123.0743 | -64.3341 | 58.5388 | 0.015106 | 0.0048493 | 0.0016876 | 0.0025271 | 0.00052558 | -1.2808e-05 | 0.0011856 | -0.034912 | -0.00014097 | 0.0016363 | 0.0023092 | 0.00079247 | -0.00098487 | 0.00076046 | -0.068665 | 58.5571 | -64.4485 | 58.4335 | -64.1052 | -64.5859 | -64.5081 | 0.036621 | 58.5388 | -64.4028 | 58.5434 | -64.3112 | -64.4211 | -64.1281 | -0.11444 | 0.018311 | -0.10529 | 0.22888 | -0.17395 | -0.25177 | -0.05951 | -0.13733 | -0.068665 | 0 | 0.004578 | 0.022888 | 0.20599 | -0.086976 | 0.27466 | -0.018311 | 0.34332 | 122.8821 | 0.091553 | 122.9462 | 123.0057 | 122.9416 | 122.8912 | 122.8729 | -122.9874 | -122.9416 | 122.7676 | 122.8775 | 64.2654 | 64.3707
147.6562 | 123.143 | -64.3295 | 58.5297 | -0.0383 | 0.0014313 | 0.0033966 | 0.0023135 | 0.0022346 | 0.0036188 | 0.00097205 | -0.010498 | 0.00049983 | 0.0018499 | -0.003245 | 0.00036527 | -0.00077127 | 0.00011966 | -0.16022 | 58.5251 | -64.476 | 58.4061 | -64.1418 | -64.6408 | -64.5264 | -0.068665 | 58.5297 | -64.4028 | 58.5663 | -64.2654 | -64.389 | -64.0915 | -0.14648 | -0.004578 | -0.1236 | 0.18768 | -0.19684 | -0.31128 | -0.050354 | -0.1648 | -0.073242 | 0 | 0.036621 | 0.064087 | 0.23804 | -0.059509 | 0.31128 | 0.013733 | 0.33417 | 122.8821 | 0.13733 | 122.9691 | 123.0011 | 122.9324 | 122.8546 | 122.8592 | -123.0057 | -122.9324 | 122.7356 | 122.8958 | 64.1693 | 64.2609
149.3906 | 123.1613 | -64.2517 | 58.5388 | 0.0074768 | -0.0019867 | 0.0029694 | -0.00046351 | -0.0018244 | 0.00062799 | -0.0015916 | 0.093262 | 0.00092703 | -0.0011407 | 0.0010276 | 0.0022879 | -0.0037619 | -0.00052114 | -0.1831 | 58.5205 | -64.4302 | 58.4747 | -64.032 | -64.5035 | -64.4028 | -0.018311 | 58.5251 | -64.3662 | 58.6212 | -64.183 | -64.2746 | -64.0182 | -0.17853 | -0.01831 | -0.064087 | 0.21973 | -0.15106 | -0.25177 | 0.027466 | -0.073242 | -0.11444 | -0.013733 | 0.082398 | 0.068665 | 0.23346 | -0.022888 | 0.3479 | 0.091553 | 0.39826 | 122.905 | 0.18311 | 122.9874 | 122.9507 | 122.8912 | 122.7722 | 122.7768 | -122.9691 | -122.905 | 122.7264 | 122.8729 | 64.0686 | 64.2334
151.125 | 123.0515 | -64.2654 | 58.6441 | -0.023041 | 0.00057686 | 0.0044646 | 0.0010319 | 0.0015936 | 0.002337 | -9.6154e-05 | -0.050171 | 0.0019952 | 0.0037725 | -0.0021768 | 0.0010061 | 0.00029693 | -0.00030754 | -0.16022 | 58.6533 | -64.3982 | 58.4656 | -64.0411 | -64.5676 | -64.4577 | -0.10071 | 58.6853 | -64.3295 | 58.6121 | -64.2471 | -64.3662 | -64.0457 | -0.13275 | 0.009155 | -0.17853 | 0.2243 | -0.19226 | -0.30212 | -0.05951 | -0.16937 | -0.064087 | 0.041199 | -0.032043 | 0.018311 | 0.21973 | -0.10071 | 0.28381 | -0.036621 | 0.35706 | 122.8638 | 0.082398 | 122.9416 | 123.0515 | 123.0148 | 122.9187 | 122.9507 | -123.0423 | -122.9736 | 122.731 | 122.8775 | 64.1052 | 64.1647
152.8125 | 123.1613 | -64.2929 | 58.5617 | -0.0383 | -0.00070494 | 0.0019012 | 0.0040225 | 0.0024482 | 0.00084159 | 0.0013992 | -0.019653 | 7.2626e-05 | 0.00078193 | 0.0020956 | -0.0024117 | -0.0029075 | -9.3938e-05 | -0.16022 | 58.5709 | -64.4211 | 58.4656 | -64.0457 | -64.5676 | -64.4485 | -0.045776 | 58.5526 | -64.3433 | 58.6624 | -64.1968 | -64.3158 | -64.0228 | -0.12817 | 0.009155 | -0.096131 | 0.24719 | -0.15564 | -0.27466 | -0.027465 | -0.14648 | -0.050354 | -0.009156 | 0.10071 | 0.096131 | 0.27008 | -0.022888 | 0.32043 | 0.027466 | 0.37537 | 122.8867 | 0.14648 | 123.0057 | 122.9919 | 122.8958 | 122.8638 | 122.8455 | -122.9828 | -122.905 | 122.7585 | 122.9553 | 64.1327 | 64.2471
154.5469 | 123.0423 | -64.3341 | 58.5754 | 0.015106 | -0.00049134 | 0.0016876 | 0.0023135 | 0.0018072 | -1.2808e-05 | 0.00204 | -0.041016 | 7.2626e-05 | 0.0018499 | -0.0066628 | 0.0012199 | -0.0024803 | -0.0018029 | -0.16937 | 58.5617 | -64.4577 | 58.4015 | -64.1739 | -64.6454 | -64.5264 | -0.11444 | 58.5571 | -64.389 | 58.5297 | -64.3204 | -64.4531 | -64.1281 | -0.1236 | -0.013732 | -0.17395 | 0.16022 | -0.19226 | -0.31128 | -0.068664 | -0.18768 | -0.054932 | -0.01831 | -0.045776 | 0.013732 | 0.20599 | -0.11902 | 0.26093 | -0.064087 | 0.28381 | 122.8592 | 0.068664 | 122.9187 | 123.0194 | 122.9462 | 122.8958 | 122.8912 | -123.0331 | -122.9645 | 122.7356 | 122.8638 | 64.1647 | 64.2197
156.2188 | 123.0377 | -64.2517 | 58.6487 | 0.10666 | -0.0011321 | 0.0046784 | -0.0015317 | -0.00075622 | 0.00041439 | 0.002681 | 0.0047608 | 0.00028623 | 0.00078193 | -4.063e-05 | 0.00079247 | -0.00098487 | -0.0018029 | -0.11444 | 58.5983 | -64.4257 | 58.4656 | -64.0778 | -64.5309 | -64.4531 | -0.009155 | 58.6441 | -64.3295 | 58.5709 | -64.238 | -64.3387 | -64.0823 | -0.17395 | -0.050354 | -0.18311 | 0.17395 | -0.20142 | -0.27924 | -0.027466 | -0.10529 | -0.07782 | -0.004578 | -0.07782 | 0.013733 | 0.16937 | -0.086975 | 0.24719 | -0.009155 | 0.3479 | 122.8912 | 0.091553 | 122.9004 | 123.024 | 122.9736 | 122.85 | 122.8958 | -123.0743 | -122.9782 | 122.7173 | 122.8226 | 64.1373 | 64.2426
157.9531 | 123.1476 | -64.2242 | 58.6395 | 0.037994 | -0.0011321 | 0.002542 | -0.0017453 | -0.002038 | -0.00022641 | 0.0016128 | 0.050537 | 7.2626e-05 | 0.0041999 | -0.006022 | 0.00079247 | -0.0020529 | -0.0047937 | -0.07782 | 58.5571 | -64.3662 | 58.5617 | -63.9175 | -64.4257 | -64.325 | 0.086975 | 58.5938 | -64.2883 | 58.6716 | -64.1281 | -64.2288 | -63.9862 | -0.14191 | -0.082397 | -0.077819 | 0.3067 | -0.10071 | -0.20142 | 0.041199 | -0.059509 | -0.064087 | -0.045776 | 0.032044 | 0.09613 | 0.23804 | -0.004578 | 0.30212 | 0.059509 | 0.44861 | 122.9279 | 0.16022 | 122.9599 | 122.9233 | 122.8821 | 122.7814 | 122.818 | -123.0057 | -122.9279 | 122.7859 | 122.8958 | 64.1464 | 64.3112
159.6875 | 123.2025 | -64.3204 | 58.5251 | 0.037994 | -0.00091854 | 0.0016876 | -0.00024991 | 0.0018072 | -0.00022641 | 0.0016128 | 0.062744 | -0.00056817 | 0.0014227 | -0.0045266 | -0.0032663 | -0.0018393 | 0.0031103 | -0.11902 | 58.4427 | -64.4897 | 58.493 | -64.0411 | -64.476 | -64.4119 | 0.09613 | 58.4747 | -64.3753 | 58.6258 | -64.1785 | -64.2746 | -64.0411 | -0.16937 | -0.082397 | -0.032043 | 0.27924 | -0.091552 | -0.15564 | 0.07782 | 0.013733 | -0.054931 | -0.050354 | 0.10071 | 0.14191 | 0.27924 | 0.045777 | 0.33417 | 0.10071 | 0.44861 | 122.9828 | 0.19684 | 123.0011 | 122.9324 | 122.85 | 122.7631 | 122.7951 | -123.0148 | -122.9004 | 122.8134 | 122.9462 | 64.2014 | 64.4165
161.3594 | 123.0469 | -64.3387 | 58.58 | 0.076141 | -0.0043365 | 0.0012604 | 0.0023135 | 0.0015936 | 0.00041439 | 0.0016128 | 0.02002 | -0.00099557 | 0.00099553 | -0.001536 | -0.00048913 | -0.0016257 | 0.00033326 | -0.1236 | 58.5297 | -64.4485 | 58.3786 | -64.1693 | -64.5859 | -64.5035 | -0.022888 | 58.5617 | -64.4073 | 58.5205 | -64.3066 | -64.3982 | -64.1647 | -0.10986 | -0.050354 | -0.20142 | 0.16937 | -0.16479 | -0.24719 | -0.054932 | -0.13733 | -0.068665 | -0.01831 | -0.059509 | 0.032043 | 0.17395 | -0.059509 | 0.24262 | 0.009156 | 0.27923 | 122.8271 | 0.10071 | 122.9279 | 122.9782 | 122.9691 | 122.8683 | 122.9004 | -123.0286 | -122.9874 | 122.7173 | 122.8592 | 64.2151 | 64.3158
163.0938 | 123.1476 | -64.3478 | 58.4793 | -0.0383 | 0.0014313 | 0.0046784 | 0.00081809 | 0.0028754 | -0.002149 | -0.00073695 | 0.02002 | -0.00014097 | 0.00099553 | 0.00017297 | -0.00027553 | -0.0024803 | -0.0022301 | -0.15106 | 58.4747 | -64.4669 | 58.4976 | -64.0503 | -64.5493 | -64.4302 | 0.032043 | 58.4702 | -64.4257 | 58.6121 | -64.2197 | -64.325 | -64.064 | -0.11902 | -0.004578 | 0.018311 | 0.29755 | -0.082398 | -0.20142 | 0.036621 | -0.082397 | -0.07782 | -0.009155 | 0.13275 | 0.12817 | 0.28381 | 0.022888 | 0.36163 | 0.10071 | 0.41657 | 122.9645 | 0.20599 | 123.0377 | 122.9416 | 122.8958 | 122.8226 | 122.818 | -122.9462 | -122.905 | 122.8455 | 122.9599 | 64.1968 | 64.3799
164.7969 | 123.1522 | -64.2654 | 58.5709 | -0.0077822 | -0.0011321 | -0.0010896 | 0.00017729 | -0.0035334 | 0.00020079 | 0.00075845 | 0.044434 | 0.00028623 | -0.00028627 | -0.0013224 | -0.0017709 | -0.0033347 | 0.0039649 | -0.20142 | 58.5388 | -64.4119 | 58.4518 | -64.0686 | -64.5218 | -64.4211 | -0.050354 | 58.5571 | -64.357 | 58.6258 | -64.1739 | -64.2883 | -64.0182 | -0.14648 | -0.032044 | -0.11902 | 0.19684 | -0.15564 | -0.25635 | -0.009156 | -0.10986 | -0.091553 | -0.013733 | 0.054931 | 0.091553 | 0.24719 | -0.022888 | 0.33875 | 0.068665 | 0.34332 | 122.8638 | 0.18311 | 122.9828 | 122.9507 | 122.9141 | 122.8043 | 122.8226 | -122.9828 | -122.9279 | 122.7173 | 122.8912 | 64.064 | 64.2151
166.5469 | 123.1842 | -64.2838 | 58.5571 | 0.045624 | -0.0030547 | 0.0010468 | -0.00089091 | -0.00096982 | -0.002149 | 0.00054465 | 0.053589 | 0.00049983 | 0.00014093 | 0.00038657 | -0.00091653 | -0.0024803 | -0.00094854 | -0.11444 | 58.4839 | -64.4211 | 58.548 | -63.9633 | -64.4485 | -64.3478 | 0.11444 | 58.5251 | -64.3112 | 58.6853 | -64.1281 | -64.2471 | -63.9999 | -0.13733 | -0.073242 | -0.009155 | 0.32043 | -0.064087 | -0.16479 | 0.073243 | -0.027465 | -0.027466 | -0.032044 | 0.12817 | 0.15564 | 0.28381 | 0.036621 | 0.31128 | 0.064087 | 0.45776 | 122.9691 | 0.1831 | 122.9965 | 122.905 | 122.8363 | 122.7676 | 122.8088 | -122.9782 | -122.8683 | 122.8317 | 122.9691 | 64.1693 | 64.3982
168.2188 | 123.1842 | -64.3158 | 58.4747 | -0.0383 | 0.0020721 | 0.0021148 | 0.0012455 | 0.00052558 | 0.00020079 | -0.00052335 | -0.0074462 | 0.0013544 | 0.0020635 | 0.0053 | 0.00079247 | -0.0011985 | -0.0011621 | -0.10529 | 58.4564 | -64.4577 | 58.461 | -64.1006 | -64.5721 | -64.4577 | 0.013733 | 58.4518 | -64.4119 | 58.6075 | -64.2471 | -64.3524 | -64.064 | -0.14191 | -0.01831 | -0.013732 | 0.21515 | -0.14191 | -0.25635 | 0 | -0.11444 | -0.09613 | -0.022888 | 0.13275 | 0.068665 | 0.25177 | -0.036621 | 0.3479 | 0.059509 | 0.35706 | 122.9187 | 0.16479 | 123.0194 | 122.9141 | 122.8638 | 122.7722 | 122.7676 | -122.9324 | -122.8867 | 122.7768 | 122.9233 | 64.2105 | 64.3295
169.8906 | 123.0515 | -64.3387 | 58.5388 | -0.061188 | 0.0012177 | 0.0016876 | 0.0023135 | -0.00032902 | 0.0010554 | 0.0022536 | -0.089844 | -0.0012092 | 0.0012091 | 0.0055136 | -0.00070273 | -0.0039755 | 0.00076046 | -0.16022 | 58.5388 | -64.4714 | 58.3832 | -64.2197 | -64.6683 | -64.5584 | -0.10071 | 58.5617 | -64.4073 | 58.4976 | -64.3662 | -64.4669 | -64.1693 | -0.13275 | 0 | -0.15564 | 0.11902 | -0.21973 | -0.32959 | -0.086975 | -0.19684 | -0.068665 | 0.022889 | -0.041198 | -0.027466 | 0.16937 | -0.12817 | 0.23804 | -0.059509 | 0.25177 | 122.8546 | 0.041199 | 122.905 | 123.0103 | 122.9691 | 122.8775 | 122.9004 | -123.0103 | -122.9462 | 122.7219 | 122.8363 | 64.1785 | 64.238
171.6406 | 123.1796 | -64.2838 | 58.5068 | -0.0077822 | 0.0018585 | 0.0036102 | 0.0020999 | -0.003106 | 0.0025506 | 0.00011745 | -0.025757 | -0.00056817 | 0.0016363 | 0.00060037 | -0.0013437 | -0.0022665 | -0.0020165 | -0.11444 | 58.4976 | -64.4348 | 58.5068 | -64.0411 | -64.5447 | -64.4211 | 0 | 58.5114 | -64.3662 | 58.6395 | -64.2105 | -64.3158 | -64.0274 | -0.15106 | -0.009155 | 0 | 0.24261 | -0.13733 | -0.26093 | 0.013732 | -0.10986 | -0.082398 | 0.004578 | 0.13275 | 0.073242 | 0.25635 | -0.032044 | 0.33875 | 0.050354 | 0.39368 | 122.9416 | 0.15564 | 123.0057 | 122.9324 | 122.8775 | 122.7814 | 122.7951 | -122.9416 | -122.8729 | 122.7905 | 122.9233 | 64.1693 | 64.2838
173.375 | 123.1064 | -64.2838 | 58.6166 | 0.015106 | -0.0022003 | 0.0023284 | -0.00067711 | 0.00073918 | -0.002149 | 0.0028946 | 0.053589 | -0.00099557 | -0.0015681 | -0.00089503 | 0.0022879 | -0.0033347 | -0.00094854 | -0.086975 | 58.5251 | -64.4119 | 58.5526 | -63.9908 | -64.4394 | -64.3662 | 0.064087 | 58.5709 | -64.325 | 58.6395 | -64.1647 | -64.2838 | -64.0045 | -0.12817 | -0.091553 | -0.064087 | 0.29297 | -0.082398 | -0.15564 | 0.045776 | -0.027466 | -0.041199 | -0.045776 | 0.022888 | 0.11902 | 0.27923 | 0 | 0.32043 | 0.041199 | 0.42114 | 122.9645 | 0.16022 | 122.9645 | 122.937 | 122.8958 | 122.8088 | 122.8546 | -123.0286 | -122.9416 | 122.8363 | 122.9233 | 64.1968 | 64.3478
175.0469 | 123.1705 | -64.238 | 58.5892 | 0.030365 | -0.0024139 | 0.0021148 | -0.0015317 | -0.0022516 | -1.2808e-05 | 0.00075845 | 0.056641 | -0.00185 | 0.0035589 | -0.0021768 | -0.0011301 | -0.0050437 | -9.3938e-05 | -0.16479 | 58.5388 | -64.4119 | 58.5342 | -64.0182 | -64.4714 | -64.3845 | 0.013733 | 58.5526 | -64.3158 | 58.6716 | -64.1235 | -64.2471 | -63.9999 | -0.17395 | -0.050354 | -0.054931 | 0.21973 | -0.14648 | -0.23346 | 0.027466 | -0.05951 | -0.07782 | -0.036621 | 0.082398 | 0.11444 | 0.23804 | -0.009155 | 0.31586 | 0.068665 | 0.39368 | 122.9462 | 0.19226 | 122.9874 | 122.9507 | 122.8683 | 122.7768 | 122.7905 | -123.0011 | -122.905 | 122.7722 | 122.9095 | 64.0732 | 64.2517
176.7344 | 123.0515 | -64.3021 | 58.6075 | -0.03067 | 0.00014946 | 0.0027558 | 0.0025271 | 0.0011664 | 0.002978 | -0.001378 | -0.059326 | 0.0019952 | 0.00056833 | 0.0012412 | -0.00048913 | -0.0024803 | 0.00033326 | -0.15106 | 58.6212 | -64.4257 | 58.4335 | -64.1327 | -64.5767 | -64.4989 | -0.09613 | 58.6304 | -64.3478 | 58.58 | -64.2929 | -64.4028 | -64.1098 | -0.1236 | 0.013733 | -0.17395 | 0.16937 | -0.19684 | -0.27466 | -0.073242 | -0.15106 | -0.045776 | 0.022888 | -0.027466 | 0.009155 | 0.19226 | -0.10071 | 0.23804 | -0.054932 | 0.29297 | 122.8592 | 0.054931 | 122.9279 | 123.0469 | 122.9782 | 122.9233 | 122.9324 | -123.0331 | -122.9553 | 122.7356 | 122.8821 | 64.151 | 64.2059
178.4531 | 123.0743 | -32.5882 | 90.3122 | -0.00015269 | 0.00079046 | 0.011728 | -0.0023861 | -0.0022516 | 0.00062799 | -0.00073695 | 0.016968 | -0.0012092 | 0.0037725 | -0.0021768 | 0.0016471 | -0.0022665 | 0.0014015 | 0.050354 | 90.2756 | -32.6797 | 90.2023 | -13.4857 | -32.8766 | -32.7576 | 0.20599 | 90.2847 | -32.6202 | 90.3488 | -32.6065 | -32.6981 | -32.5378 | -0.091553 | -0.036621 | -0.10986 | 19.1025 | -0.16937 | -0.28839 | -0.077819 | -0.19684 | -0.032043 | -0.027466 | 0.036621 | -0.01831 | 0.050354 | -0.10986 | 0.082397 | -0.07782 | 19.194 | 122.8821 | 0.013733 | 122.9691 | 122.9553 | 122.905 | 122.8638 | 122.8729 | -122.9919 | -122.9324 | 122.7905 | 122.937 | 32.6386 | 32.7942
180.1406 | 123.1247 | -64.0778 | 58.7906 | 0.045624 | 0.00057686 | -2.1372e-05 | 0.0038089 | 0.0035162 | -0.0025762 | -0.00052335 | -0.034912 | 0.00071343 | 0.0016363 | -0.002604 | 0.00036527 | -0.0020529 | -0.0043665 | -0.17853 | 58.7448 | -64.2838 | 58.6121 | -63.9038 | -64.389 | -64.3021 | -0.064087 | 58.786 | -64.1876 | 58.7585 | -64.0732 | -64.1876 | -63.9038 | -0.20599 | -0.045776 | -0.17853 | 0.17395 | -0.2243 | -0.31128 | -0.018311 | -0.10529 | -0.10986 | -0.004577 | -0.032043 | 0.004578 | 0.17395 | -0.10986 | 0.28381 | 0 | 0.37994 | 122.8958 | 0.11444 | 122.9462 | 123.0286 | 122.9736 | 122.8226 | 122.8638 | -123.0743 | -122.9782 | 122.6898 | 122.8363 | 63.8992 | 64.0137
181.8281 | 123.0743 | -64.0686 | 58.8135 | -0.045929 | 0.0018585 | 0.00083303 | 0.0044497 | 0.0028754 | 0.004046 | 0.0024674 | -0.06543 | 7.2626e-05 | 0.00099553 | 0.0031638 | -0.00027553 | -0.00055747 | -0.0032983 | -0.21973 | 58.7814 | -64.2242 | 58.6258 | -63.8763 | -64.4028 | -64.3204 | -0.13733 | 58.7814 | -64.1418 | 58.7585 | -64.1281 | -64.2197 | -63.8992 | -0.15564 | -0.032044 | -0.18768 | 0.19226 | -0.25177 | -0.33417 | -0.096131 | -0.17853 | -0.073242 | -0.032044 | -0.054932 | -0.059509 | 0.16937 | -0.15106 | 0.24262 | -0.07782 | 0.3479 | 122.85 | 0.013733 | 122.9004 | 123.0057 | 122.9233 | 122.85 | 122.85 | -123.0377 | -122.9553 | 122.6944 | 122.8271 | 63.8489 | 63.9313
183.5625 | 123.1934 | -63.4689 | 59.3399 | -0.0077822 | -0.0015595 | 0.0019012 | -0.0017453 | -0.0024652 | -0.0015082 | 0.00075845 | 0.081055 | 0.0019952 | 0.0024909 | -0.0038858 | -0.00091653 | -0.0035483 | -0.0013757 | -0.18768 | 59.3399 | -63.588 | 59.3399 | -62.7777 | -63.0844 | -62.7136 | 0.1236 | 59.5322 | -63.4094 | 59.4543 | -63.3728 | -63.4552 | -63.2492 | -0.11902 | 0 | 0 | 0.69122 | 0.75531 | 0.38452 | 0.87433 | 0.50354 | 0.059509 | 0.19226 | 0.11444 | 0.09613 | 0.21973 | 0.013733 | 0.16022 | -0.045776 | 0.81024 | 122.9279 | 0.036621 | 122.8638 | 122.9279 | 122.9416 | 122.8088 | 123.0011 | -122.9279 | -122.7493 | 122.8088 | 122.9233 | 63.2812 | 63.5925
185.3125 | 123.0377 | -32.254 | 90.6693 | 0.015106 | 0.0018585 | 0.01301 | 0.0016727 | 0.00052558 | 0.00041439 | -0.00073695 | -0.071533 | 0.00092703 | 0.0024909 | -0.003245 | -0.00070273 | -0.00098487 | -0.0041527 | 0.10529 | 90.8432 | -32.2037 | 90.6876 | -12.7167 | -32.4188 | -32.3364 | 0.21515 | 90.8615 | -32.1213 | 90.77 | -32.2495 | -32.3685 | -32.222 | 0.050354 | 0.17395 | 0.018311 | 19.5374 | -0.082398 | -0.1648 | -0.13275 | -0.21515 | 0.13275 | 0.19226 | 0.10071 | 0.004577 | 0.032043 | -0.11444 | -0.10071 | -0.24719 | 19.487 | 122.8912 | -0.12817 | 122.8912 | 123.0469 | 122.9828 | 123.0972 | 123.1155 | -122.8729 | -122.7905 | 122.9416 | 123.024 | 32.3593 | 32.4692
187.0625 | 123.0377 | -30.4413 | 92.5964 | 0.0914 | 0.00014946 | 0.011087 | -0.0013181 | 0.0022346 | -0.00065361 | 0.0013992 | -0.022705 | 0.002636 | 0.0041999 | 0.0040182 | -0.00048913 | -0.0026939 | -9.3938e-05 | 0.091553 | 92.5278 | -30.5283 | 92.2989 | -10.0662 | -30.7297 | -30.6335 | 0.17853 | 92.5186 | -30.4459 | 92.4545 | -30.4642 | -30.5511 | -30.4184 | -0.086975 | -0.068665 | -0.29755 | 20.3751 | -0.19226 | -0.28839 | -0.10529 | -0.20142 | -0.004578 | -0.07782 | -0.14191 | -0.022888 | 0.022888 | -0.10986 | 0.027466 | -0.10528 | 20.462 | 122.8271 | -0.01831 | 122.9004 | 123.056 | 122.9645 | 122.9691 | 122.9599 | -123.1247 | -123.0423 | 122.7402 | 122.8958 | 30.5328 | 30.6198
188.7344 | 123.0927 | -29.6585 | 93.2602 | -0.03067 | -0.0024139 | 0.01365 | -0.0034543 | -0.0022516 | 0.0019098 | 0.00011745 | 0.041382 | 7.2626e-05 | 0.00014093 | -0.00025423 | 0.00015167 | -0.0024803 | -0.0011621 | 0.054932 | 93.1778 | -29.7318 | 93.1412 | -8.757 | -29.8691 | -29.7867 | 0.2243 | 93.2465 | -29.7089 | 93.2419 | -29.6768 | -29.7684 | -29.6494 | -0.073242 | -0.082398 | -0.11902 | 20.9015 | -0.12817 | -0.21057 | -0.054932 | -0.13733 | -0.050354 | -0.013733 | -0.018311 | -0.018311 | 0.009155 | -0.10986 | 0.059509 | -0.05951 | 20.9747 | 122.8729 | 0.032043 | 122.9507 | 122.9095 | 122.9553 | 122.8363 | 122.905 | -122.9919 | -122.9691 | 122.7997 | 122.9004 | 29.7134 | 29.8828
190.4688 | 123.1064 | -29.4479 | 93.4387 | -0.061188 | 0.0016449 | 0.014719 | -0.0025997 | -0.00032902 | 0.0021234 | 0.0013992 | 0.016968 | 0.00028623 | 0.0018499 | -0.002604 | 0.00036527 | -0.0044029 | -0.0015893 | 0.032043 | 93.4113 | -29.5166 | 93.3426 | -8.4549 | -29.7638 | -29.6402 | 0.16479 | 93.3884 | -29.5258 | 93.457 | -29.4891 | -29.5807 | -29.425 | -0.068665 | -0.027466 | -0.096131 | 20.993 | -0.19226 | -0.31586 | -0.1236 | -0.24719 | -0.07782 | -0.050354 | 0.01831 | -0.041199 | 0.022888 | -0.13275 | 0.10071 | -0.054931 | 21.0617 | 122.8592 | 0.036621 | 122.9828 | 122.9279 | 122.9141 | 122.8592 | 122.8363 | -122.9553 | -122.9645 | 122.7905 | 122.905 | 29.48 | 29.6127
192.2031 | 123.0927 | -29.0863 | 93.8232 | -0.03067 | -0.00049134 | 0.012796 | -0.0017453 | 0.00031198 | 0.0025506 | -0.002446 | 0.056641 | 0.00049983 | 0.0022773 | 0.0014548 | -0.00027553 | -0.0031211 | -0.00052114 | -0.068665 | 93.7408 | -29.2053 | 93.6081 | -7.9788 | -29.4296 | -29.3106 | 0.10071 | 93.75 | -29.155 | 93.7683 | -29.1733 | -29.2511 | -29.1046 | -0.11902 | -0.082397 | -0.21515 | 21.1075 | -0.2243 | -0.34332 | -0.10529 | -0.2243 | -0.068664 | -0.073242 | -0.054931 | -0.086975 | -0.01831 | -0.1648 | 0.050354 | -0.096131 | 21.2265 | 122.8134 | -0.018311 | 122.9233 | 122.9462 | 122.905 | 122.8271 | 122.8363 | -123.0286 | -122.9782 | 122.6944 | 122.8546 | 29.0176 | 29.187
193.8906 | 123.0331 | -29.2328 | 93.7363 | 0.0074768 | 0.0018585 | 0.014291 | 0.0012455 | 0.0035162 | 0.0014826 | -0.00030975 | -0.080688 | -0.00185 | 0.0012091 | 0.002523 | -0.00027553 | -0.0016257 | 0.0035377 | -0.027466 | 93.6951 | -29.3381 | 93.4616 | -8.2169 | -29.6265 | -29.5212 | 0.064087 | 93.7134 | -29.3015 | 93.6356 | -29.3701 | -29.4479 | -29.2831 | -0.10529 | -0.041199 | -0.27466 | 21.0159 | -0.28839 | -0.39368 | -0.18311 | -0.28839 | -0.068665 | -0.022888 | -0.10071 | -0.13733 | -0.050354 | -0.21515 | 0.018311 | -0.14648 | 21.1212 | 122.7997 | -0.068664 | 122.937 | 123.0331 | 123.0148 | 122.9279 | 122.9462 | -123.0743 | -123.0377 | 122.6944 | 122.8683 | 29.2053 | 29.2969
195.6094 | 123.0789 | -29.0405 | 93.9102 | 0.0074768 | -0.00049134 | 0.013437 | -0.0017453 | 9.818e-05 | -0.00065361 | 0.0013992 | -0.016602 | 0.001568 | 0.0016363 | 0.0057272 | -0.0013437 | -0.0035483 | 0.0022559 | 0.045776 | 93.8736 | -29.1641 | 93.6722 | -7.8918 | -29.3655 | -29.2786 | 0.13275 | 93.924 | -29.0771 | 93.8461 | -29.1 | -29.1824 | -29.0451 | -0.1236 | -0.036621 | -0.23804 | 21.1487 | -0.23804 | -0.32501 | -0.11444 | -0.20142 | -0.036621 | 0.013733 | -0.064087 | -0.05951 | -0.004578 | -0.14191 | 0.032043 | -0.10529 | 21.2723 | 122.8363 | -0.022889 | 122.9233 | 123.0377 | 123.0011 | 122.9141 | 122.9645 | -123.0743 | -122.9874 | 122.7127 | 122.8867 | 29.0863 | 29.1733
197.3438 | 123.0194 | -28.8345 | 94.0933 | 0.0074768 | -0.0026275 | 0.012582 | 0.00060449 | -0.0035334 | 0.00084159 | -0.0018052 | -0.025757 | 0.0011408 | 0.00035453 | -0.004313 | 0.0010061 | -0.0020529 | 0.00054686 | 0.041199 | 94.0155 | -29.0085 | 93.8141 | -7.5989 | -29.1824 | -29.1138 | 0.14191 | 94.0887 | -28.9078 | 93.9789 | -28.9581 | -29.0359 | -28.8895 | -0.17395 | -0.07782 | -0.27924 | 21.2357 | -0.27924 | -0.3479 | -0.10529 | -0.17395 | -0.073242 | -0.004578 | -0.11444 | -0.1236 | -0.054931 | -0.20142 | 0.018311 | -0.12817 | 21.4096 | 122.8226 | -0.050354 | 122.8867 | 123.024 | 122.9965 | 122.85 | 122.9233 | -123.1018 | -123.0011 | 122.6486 | 122.8134 | 28.8757 | 28.9764
199.0781 | 123.1384 | -28.6514 | 94.2032 | -0.00015269 | 0.0010041 | 0.014291 | 0.0023135 | 0.0011664 | 0.0027644 | -0.00052335 | -0.0074462 | 0.00092703 | 0.00099553 | 0.0040182 | 0.0010061 | 8.3332e-05 | -0.00052114 | 0.013733 | 94.1803 | -28.8345 | 94.0109 | -7.3334 | -29.0359 | -28.9307 | 0.11444 | 94.1437 | -28.7704 | 94.2307 | -28.7384 | -28.8208 | -28.6423 | -0.18311 | -0.022888 | -0.19226 | 21.3181 | -0.27924 | -0.38452 | -0.09613 | -0.20142 | -0.11902 | -0.059509 | 0.027466 | -0.086975 | 0.009155 | -0.16937 | 0.12817 | -0.050354 | 21.5012 | 122.8455 | 0.032044 | 123.0011 | 123.0148 | 122.9141 | 122.8317 | 122.7951 | -123.0377 | -122.9736 | 122.6624 | 122.8821 | 28.6652 | 28.7659
200.8125 | 123.0515 | -28.9627 | 93.9743 | 0.022736 | -0.0024139 | 0.01301 | -0.00067711 | -0.00032902 | -0.002149 | 0.00075845 | 0.03833 | -0.00014097 | 0.00099553 | 0.0014548 | 0.00036527 | -0.0039755 | 0.00054686 | 0.050354 | 93.9423 | -29.0359 | 93.8141 | -7.7087 | -29.2145 | -29.1458 | 0.15106 | 93.9285 | -29.0176 | 93.9102 | -29.0268 | -29.0909 | -28.9856 | -0.073242 | -0.032043 | -0.16022 | 21.254 | -0.18311 | -0.25177 | -0.10986 | -0.17853 | -0.054931 | -0.045776 | -0.064087 | -0.064086 | -0.022888 | -0.12817 | 0.032043 | -0.073242 | 21.3272 | 122.85 | -0.009155 | 122.9279 | 122.9782 | 122.9462 | 122.905 | 122.8912 | -123.0103 | -122.9919 | 122.7768 | 122.8729 | 29.0131 | 29.1138
202.5469 | 123.0286 | -29.0039 | 93.9423 | 0.083771 | -0.00027774 | 0.011514 | -0.0013181 | -0.00011542 | -0.0027898 | 0.00075845 | 0.02002 | 0.00049983 | 0.0029181 | 0.0023092 | -6.1934e-05 | -0.0033347 | -0.0020165 | -0.018311 | 93.9056 | -29.1046 | 93.6813 | -7.8827 | -29.3472 | -29.2511 | 0.091553 | 93.9331 | -29.0726 | 93.8187 | -29.1183 | -29.1733 | -29.0543 | -0.10071 | -0.036621 | -0.26093 | 21.1212 | -0.24719 | -0.34332 | -0.14648 | -0.24261 | -0.068665 | -0.009156 | -0.1236 | -0.11444 | -0.050354 | -0.16937 | 0.018311 | -0.10071 | 21.2219 | 122.7859 | -0.045776 | 122.8912 | 123.0103 | 123.0057 | 122.9095 | 122.937 | -123.0469 | -123.0148 | 122.6852 | 122.8226 | 28.9856 | 29.0955
204.2188 | 123.1155 | -28.8071 | 94.0247 | -0.053558 | 0.0024995 | 0.013437 | 0.00060449 | 0.003089 | 0.0010554 | 0.0028946 | 0.053589 | -0.00014097 | 0.0016363 | -0.0047402 | 0.0025015 | -0.0022665 | 0.00054686 | -0.013733 | 93.9743 | -28.9352 | 93.8828 | -7.5302 | -29.1412 | -29.0405 | 0.11902 | 94.0338 | -28.8895 | 94.0613 | -28.9078 | -28.981 | -28.8345 | -0.12817 | -0.050354 | -0.14191 | 21.2769 | -0.23346 | -0.33417 | -0.10529 | -0.20599 | -0.082397 | 0.009155 | 0.036621 | -0.10071 | -0.027466 | -0.17395 | 0.054931 | -0.091553 | 21.405 | 122.818 | -0.018311 | 122.9507 | 122.9095 | 122.9233 | 122.7814 | 122.8409 | -122.9599 | -122.9141 | 122.6898 | 122.8683 | 28.7933 | 28.9261
205.9531 | 123.0835 | -29.0176 | 93.956 | -0.00015269 | 0.00079046 | 0.013864 | 0.0010319 | 9.818e-05 | 0.00020079 | -0.00073695 | -0.044067 | 0.0017816 | 0.00099553 | 0.0014548 | -0.00027553 | 8.3332e-05 | -0.00052114 | 0.059509 | 93.9102 | -29.068 | 93.7225 | -7.8369 | -29.3152 | -29.2236 | 0.17853 | 93.9743 | -29.0451 | 93.9148 | -29.068 | -29.187 | -29.0314 | -0.050354 | -0.045777 | -0.23346 | 21.1807 | -0.20599 | -0.29755 | -0.15564 | -0.24719 | -0.027466 | 0.01831 | -0.041199 | -0.050354 | -0.013733 | -0.16937 | 0.013733 | -0.14191 | 21.2311 | 122.7905 | -0.022888 | 122.9599 | 122.9782 | 123.0194 | 122.9279 | 122.9919 | -123.024 | -123.0011 | 122.7402 | 122.9324 | 29.0771 | 29.1962
207.625 | 123.1567 | -28.8528 | 94.0338 | 0.030365 | -0.00070494 | 0.014078 | -0.0019589 | -0.0024652 | 0.00084159 | 0.0018264 | 0.065796 | -0.00056817 | -0.00028627 | -0.0013224 | 0.00036527 | -0.0031211 | -0.0035119 | -0.07782 | 94.0018 | -28.9536 | 93.8553 | -7.5989 | -29.155 | -29.0451 | 0.10986 | 93.9972 | -28.9215 | 94.0567 | -28.8849 | -28.9673 | -28.8345 | -0.10071 | -0.032043 | -0.17853 | 21.254 | -0.19226 | -0.30212 | -0.091553 | -0.20142 | -0.068665 | -0.036621 | 0.022889 | -0.032044 | 0.01831 | -0.11444 | 0.086975 | -0.045776 | 21.3547 | 122.8088 | 0.036621 | 122.9782 | 122.9553 | 122.9187 | 122.8546 | 122.85 | -122.9874 | -122.9553 | 122.7081 | 122.9095 | 28.775 | 28.9627
209.3594 | 123.1155 | -28.9307 | 93.9789 | -0.0383 | -0.00091854 | 0.011728 | -0.0021725 | -0.0024652 | -0.0023626 | 0.00033105 | 0.041382 | 0.00049983 | 0.0012091 | -0.0013224 | -6.1934e-05 | -0.0035483 | -0.0022301 | -0.050354 | 93.9194 | -29.0405 | 93.7958 | -7.7179 | -29.2465 | -29.1229 | 0.059509 | 93.956 | -28.9856 | 93.9606 | -28.9993 | -29.0726 | -28.9352 | -0.10986 | -0.059509 | -0.18311 | 21.2128 | -0.19226 | -0.31586 | -0.082398 | -0.20599 | -0.054932 | -0.022888 | -0.018311 | -0.068665 | -0.004578 | -0.14191 | 0.050354 | -0.086975 | 21.3226 | 122.8363 | -0.013733 | 122.9462 | 122.9599 | 122.9416 | 122.85 | 122.8867 | -123.0194 | -122.9645 | 122.7264 | 122.8912 | 28.8803 | 28.9902
211.0781 | 123.056 | -28.7842 | 94.1345 | 0.037994 | -0.0013457 | 0.01301 | -0.00067711 | 0.00073918 | 0.00020079 | 0.00033105 | 0.0047608 | -0.00014097 | -7.2674e-05 | -0.0019632 | 0.00057887 | -0.0031211 | -0.0041527 | -0.009155 | 94.0887 | -28.8895 | 93.9514 | -7.4753 | -29.0634 | -28.9902 | 0.14648 | 94.1299 | -28.8391 | 94.0659 | -28.894 | -28.9627 | -28.8391 | -0.10529 | -0.045776 | -0.18311 | 21.3089 | -0.20599 | -0.27924 | -0.10071 | -0.17395 | -0.054931 | -0.004577 | -0.068664 | -0.10986 | -0.054931 | -0.17853 | 0 | -0.1236 | 21.4142 | 122.8409 | -0.054932 | 122.905 | 122.9782 | 122.9691 | 122.8729 | 122.9141 | -123.024 | -122.9736 | 122.7356 | 122.85 | 28.775 | 28.9307
212.75 | 123.024 | -28.6789 | 94.2719 | -0.0077822 | 0.0016449 | 0.014291 | 0.0025271 | -0.00054262 | 0.001269 | 0.00054465 | -0.068481 | -0.00014097 | 0.00014093 | 0.0038046 | -0.00091653 | -0.0031211 | -0.00094854 | -0.009155 | 94.2581 | -28.7979 | 93.9148 | -7.5027 | -29.1595 | -29.0314 | 0.032043 | 94.2398 | -28.7613 | 94.1803 | -28.83 | -28.9169 | -28.7338 | -0.11902 | -0.013733 | -0.35706 | 21.1761 | -0.35248 | -0.48065 | -0.23346 | -0.36163 | -0.082398 | -0.032044 | -0.091553 | -0.15106 | -0.054932 | -0.23804 | 0.027466 | -0.15564 | 21.2952 | 122.7127 | -0.068664 | 122.9416 | 123.056 | 123.0011 | 122.937 | 122.9187 | -123.0698 | -123.0331 | 122.5937 | 122.8592 | 28.6697 | 28.7109
214.4844 | 123.0743 | -28.6469 | 94.313 | 0.015106 | -0.0015595 | 0.012582 | 0.0016727 | -0.00096982 | -0.00065361 | 0.0041762 | -0.041016 | 0.00071343 | 0.0024909 | 0.008718 | -0.00048913 | -0.0011985 | 0.00011966 | 0.004578 | 94.2719 | -28.7567 | 94.0613 | -7.3059 | -28.9902 | -28.9078 | 0.10071 | 94.3039 | -28.7064 | 94.2398 | -28.7338 | -28.8254 | -28.6789 | -0.10986 | -0.041198 | -0.25177 | 21.3409 | -0.26092 | -0.34332 | -0.15106 | -0.23346 | -0.059509 | -0.009155 | -0.073242 | -0.086975 | -0.032043 | -0.17853 | 0.027466 | -0.11902 | 21.4508 | 122.818 | -0.027466 | 122.9462 | 123.0286 | 123.0103 | 122.9187 | 122.9507 | -123.0698 | -123.0194 | 122.7081 | 122.8867 | 28.6514 | 28.7476
216.2031 | 123.1476 | -28.6835 | 94.1986 | 0.030365 | 0.0016449 | 0.014719 | -0.00067711 | -0.0016106 | -0.0034308 | -9.6154e-05 | 0.074951 | -0.00035457 | 0.0022773 | -0.0051676 | 0.0012199 | -0.0035483 | 0.00076046 | -0.21973 | 94.1483 | -28.8025 | 94.0201 | -7.3471 | -29.0176 | -28.9124 | 0.054932 | 94.1895 | -28.775 | 94.194 | -28.7384 | -28.8025 | -28.6926 | -0.11902 | -0.050354 | -0.17853 | 21.3364 | -0.22888 | -0.33417 | -0.10986 | -0.21515 | -0.091552 | -0.009155 | -0.004577 | -0.054931 | -0.009155 | -0.11902 | 0.082397 | -0.027466 | 21.4554 | 122.8226 | 0.036621 | 122.9691 | 122.9507 | 122.9645 | 122.8317 | 122.8729 | -123.0011 | -122.9736 | 122.7036 | 122.8775 | 28.4637 | 28.7384
217.9375 | 123.1384 | -28.6926 | 94.1574 | -0.03067 | 0.00057686 | 0.014932 | 0.00039089 | 0.0024482 | 0.00020079 | -0.00030975 | 0.0047608 | 0.0019952 | 0.00014093 | -0.001536 | 0.00015167 | 8.3332e-05 | -0.0011621 | 0.032043 | 94.1711 | -28.7888 | 94.0613 | -7.2922 | -28.9902 | -28.8803 | 0.13275 | 94.1345 | -28.743 | 94.2123 | -28.743 | -28.8162 | -28.6789 | -0.09613 | 0.013733 | -0.096131 | 21.4005 | -0.18768 | -0.29755 | -0.091553 | -0.20142 | -0.050354 | -0.022889 | 0.054931 | -0.050354 | 0.013733 | -0.1236 | 0.064087 | -0.073242 | 21.4966 | 122.85 | 0 | 122.9553 | 122.9599 | 122.8775 | 122.8638 | 122.8271 | -122.9462 | -122.9004 | 122.7539 | 122.905 | 28.7247 | 28.8254
219.6719 | 123.0743 | -28.6057 | 94.2856 | 0.030365 | -0.0013457 | 0.011941 | -0.0021725 | -0.003106 | -0.00044001 | -0.0022324 | 0.023071 | 0.00071343 | 0.0018499 | 0.0029502 | -0.00027553 | -0.0033347 | -0.0015893 | 0.091553 | 94.2627 | -28.7109 | 94.1528 | -7.1686 | -28.862 | -28.7842 | 0.16022 | 94.281 | -28.6469 | 94.2856 | -28.6697 | -28.7384 | -28.6102 | -0.10529 | -0.022888 | -0.13275 | 21.4371 | -0.17853 | -0.25635 | -0.073243 | -0.15106 | -0.041199 | -0.004577 | 0 | -0.064087 | -0.004577 | -0.13275 | 0.036622 | -0.091552 | 21.5424 | 122.8638 | -0.022888 | 122.9324 | 122.9736 | 122.9279 | 122.8683 | 122.8867 | -122.9965 | -122.9324 | 122.7585 | 122.8912 | 28.6972 | 28.7659
221.3438 | 123.0469 | -28.3859 | 94.5786 | 0.022736 | -0.0017731 | 0.010873 | 0.00017729 | -0.0024652 | -0.0030036 | 0.0033218 | -0.022705 | 0.001568 | 0.00078193 | -0.0045266 | 0.00057887 | -0.0026939 | -0.0037255 | 0.09613 | 94.5419 | -28.4912 | 94.2902 | -6.8939 | -28.7155 | -28.6285 | 0.091553 | 94.5511 | -28.4454 | 94.4458 | -28.4958 | -28.5873 | -28.4592 | -0.10529 | -0.036621 | -0.28839 | 21.492 | -0.24262 | -0.32959 | -0.13733 | -0.2243 | -0.05951 | -0.027466 | -0.13275 | -0.10986 | -0.073242 | -0.20142 | -0.013732 | -0.14191 | 21.5973 | 122.7814 | -0.050354 | 122.8912 | 123.0331 | 122.9965 | 122.9279 | 122.937 | -123.0698 | -123.024 | 122.6761 | 122.8317 | 28.4821 | 28.4775
223.0781 | 123.111 | -28.4821 | 94.4092 | 0.0074768 | 0.00014946 | 0.01365 | 0.00081809 | -0.0022516 | 0.002337 | 0.0013992 | 0.059692 | 0.00028623 | 0.00056833 | -0.0028176 | 0.0010061 | -0.0024803 | -0.0037255 | 0.32501 | 94.3863 | -28.5828 | 94.2307 | -7.0129 | -28.8071 | -28.7064 | 0.050354 | 94.368 | -28.5416 | 94.368 | -28.537 | -28.6423 | -28.5049 | -0.10071 | -0.022888 | -0.17853 | 21.4691 | -0.2243 | -0.32501 | -0.1236 | -0.2243 | -0.059509 | -0.041199 | -0.041199 | -0.054931 | -0.022888 | -0.16022 | 0.036621 | -0.10071 | 21.5698 | 122.8134 | 0.004578 | 122.9095 | 122.9691 | 122.9095 | 122.8683 | 122.85 | -122.9919 | -122.9507 | 122.7127 | 122.85 | 28.8071 | 28.5324
224.7656 | 123.143 | -28.5187 | 94.3268 | 0.022736 | -0.0024139 | 0.012155 | -0.0034543 | -0.0039606 | 0.0019098 | 0.0024674 | 0.065796 | -0.00078177 | 0.00099553 | -0.004313 | -0.0026253 | -0.0020529 | 0.00011966 | 0.2655 | 94.194 | -28.7292 | 94.194 | -7.2281 | -28.8254 | -28.7201 | 0.17853 | 94.313 | -28.5828 | 94.4 | -28.5233 | -28.6011 | -28.4958 | -0.21057 | -0.13275 | -0.13275 | 21.2906 | -0.20142 | -0.3067 | 0.009155 | -0.09613 | -0.064087 | -0.013733 | 0.073242 | -0.004577 | 0.022888 | -0.082397 | 0.086975 | -0.01831 | 21.5012 | 122.9233 | 0.05951 | 122.9828 | 122.9233 | 122.8958 | 122.7127 | 122.8317 | -123.056 | -122.9095 | 122.7127 | 122.9187 | 28.7842 | 28.6972
226.5156 | 123.1064 | -28.3356 | 94.5374 | -0.045929 | -0.00070494 | 0.012369 | 0.00039089 | -0.00011542 | -0.0015082 | 0.00075845 | 0.03833 | 0.00071343 | 0.0020635 | 0.0057272 | 0.00079247 | -0.0024803 | 0.0011877 | 0.32044 | 94.4962 | -28.4409 | 94.3817 | -7.045 | -28.6697 | -28.5507 | 0.09613 | 94.5099 | -28.4134 | 94.5465 | -28.418 | -28.4866 | -28.3447 | -0.10529 | -0.041199 | -0.15564 | 21.2906 | -0.21515 | -0.33417 | -0.10986 | -0.22888 | -0.07782 | -0.027466 | 0.009155 | -0.082398 | -0.009156 | -0.15106 | 0.068664 | -0.073242 | 21.3959 | 122.8226 | -0.004578 | 122.9599 | 122.937 | 122.9233 | 122.8317 | 122.8455 | -122.9782 | -122.9507 | 122.7173 | 122.8821 | 28.656 | 28.4317
228.25 | 123.0972 | -27.8549 | 95.0272 | 0.015106 | 0.00057686 | 0.015787 | 0.0018863 | -0.00032902 | -0.001081 | 0.0035354 | -0.077637 | -0.00056817 | -7.2674e-05 | 0.0031638 | -0.0017709 | -0.00034387 | 0.00054686 | 0.34332 | 95.0638 | -27.9694 | 94.8212 | -6.8253 | -28.2394 | -28.1158 | 0.059509 | 95.0546 | -27.9327 | 95.0363 | -27.9556 | -28.038 | -27.8687 | -0.11444 | 0.036621 | -0.20599 | 21.0297 | -0.26093 | -0.38452 | -0.14648 | -0.27008 | -0.07782 | 0.027465 | 0.009155 | -0.10071 | -0.013733 | -0.18311 | 0.064087 | -0.10529 | 21.1441 | 122.7905 | -0.022888 | 122.9691 | 123.0331 | 122.9874 | 122.9187 | 122.9095 | -122.9965 | -122.9599 | 122.6761 | 122.8912 | 28.1982 | 27.9144
229.9219 | 123.0698 | -26.6281 | 96.3226 | 0.0074768 | 0.00079046 | 0.015573 | 0.0020999 | -0.0024652 | 0.00020079 | 0.00097205 | -0.044067 | 0.002636 | 0.0012091 | -0.00068143 | 0.00036527 | -0.0048301 | -0.0015893 | 0.48981 | 96.3089 | -26.7014 | 96.1304 | -6.5643 | -26.9348 | -26.8295 | 0.17395 | 96.3272 | -26.6647 | 96.286 | -26.6602 | -26.7792 | -26.6281 | -0.073242 | -0.013733 | -0.19226 | 20.0638 | -0.20142 | -0.3067 | -0.12817 | -0.23346 | -0.036621 | 0.004577 | -0.036621 | -0.032043 | 0 | -0.15106 | 0.036621 | -0.11444 | 20.137 | 122.8317 | 0.004578 | 122.9507 | 123.0103 | 122.9919 | 122.937 | 122.9553 | -123.024 | -122.9874 | 122.7585 | 122.9141 | 27.1179 | 26.8021
231.6562 | 123.1567 | -26.2482 | 96.5973 | -0.00015269 | -0.0015595 | 0.01365 | -3.6308e-05 | 9.818e-05 | 0.00062799 | -0.00052335 | 0.047485 | -0.00056817 | 0.0022773 | -0.0040994 | 0.00079247 | -0.0039755 | 0.00097406 | 0.43488 | 96.6064 | -26.3351 | 96.5012 | -6.4133 | -26.4771 | -26.3992 | 0.16937 | 96.6064 | -26.3214 | 96.6797 | -26.2299 | -26.3214 | -26.2344 | -0.086975 | 0.009155 | -0.09613 | 19.8349 | -0.15106 | -0.22888 | -0.064087 | -0.14191 | -0.073242 | 0.009155 | 0.082397 | 0.018311 | 0.013733 | -0.073242 | 0.086975 | 0 | 19.9219 | 122.8363 | 0.091553 | 123.0011 | 122.9416 | 122.9279 | 122.8546 | 122.8546 | -122.9324 | -122.9187 | 122.7493 | 122.9279 | 26.683 | 26.4175
233.3281 | 123.024 | -26.1612 | 96.8033 | 0.045624 | -0.00027774 | 0.015359 | 0.0016727 | 0.00138 | 0.00084159 | 0.00075845 | -0.028809 | 0.001568 | 0.0018499 | -0.00025423 | 0.00079247 | -0.0056845 | -0.0022301 | 0.4303 | 96.7667 | -26.2619 | 96.5149 | -6.3034 | -26.4999 | -26.413 | 0.10071 | 96.7667 | -26.2115 | 96.698 | -26.2573 | -26.3535 | -26.2024 | -0.10071 | -0.036621 | -0.28839 | 19.8578 | -0.25177 | -0.33875 | -0.15106 | -0.23804 | -0.050354 | -0.036621 | -0.10529 | -0.09613 | -0.041199 | -0.19226 | 0.009155 | -0.14191 | 19.9585 | 122.7768 | -0.045776 | 122.9095 | 123.0286 | 122.9782 | 122.9279 | 122.9279 | -123.0652 | -123.0148 | 122.6761 | 122.8592 | 26.5915 | 26.2619
235.0469 | 123.1567 | -25.5936 | 97.2519 | 0.022736 | 0.0014313 | 0.015787 | 0.0014591 | -0.0011834 | 0.00062799 | 0.00054465 | -0.016602 | 0.0019952 | 0.0012091 | 0.002523 | 0.00036527 | -0.0018393 | -0.0026575 | 0.37537 | 97.2473 | -25.7309 | 97.1146 | -6.5048 | -25.9232 | -25.8133 | 0.14191 | 97.2473 | -25.6897 | 97.3343 | -25.6302 | -25.7217 | -25.5707 | -0.13733 | -0.004578 | -0.13733 | 19.0887 | -0.21973 | -0.32959 | -0.082397 | -0.19226 | -0.09613 | -0.004578 | 0.082398 | -0.036621 | 0.022888 | -0.12817 | 0.11902 | -0.032044 | 19.2261 | 122.8455 | 0.059509 | 123.024 | 122.9782 | 122.937 | 122.8409 | 122.8409 | -122.9828 | -122.9416 | 122.7081 | 122.9279 | 25.9689 | 25.7355
236.7812 | 123.0515 | -25.8224 | 97.1558 | -0.0077822 | 0.0020721 | 0.016 | 0.0027407 | 0.0033026 | 0.0010554 | -0.0015916 | -0.037964 | 7.2626e-05 | 0.00078193 | -0.0021768 | 0.00057887 | -0.0016257 | 0.0020423 | 0.43945 | 97.0963 | -25.9415 | 96.8948 | -6.4087 | -26.12 | -26.033 | 0.24719 | 97.1008 | -25.8499 | 97.0917 | -25.8957 | -25.9781 | -25.827 | -0.11902 | -0.05951 | -0.26093 | 19.4138 | -0.21057 | -0.29755 | -0.091553 | -0.17853 | -0.027466 | -0.054932 | -0.064087 | -0.073242 | -0.004577 | -0.15564 | 0.022889 | -0.12817 | 19.5328 | 122.8363 | -0.045776 | 122.9416 | 123.0377 | 122.9507 | 122.9187 | 122.9233 | -123.0972 | -123.0057 | 122.7173 | 122.9141 | 26.2619 | 26.0696
238.5156 | 123.0331 | -24.9893 | 97.9614 | 0.076141 | 0.0012177 | 0.016 | 0.0012455 | 0.0045844 | -0.00086721 | 0.00011745 | -0.077637 | 0.002636 | 0.0022773 | 0.0012412 | 0.00079247 | -0.0016257 | 0.0020423 | 0.19226 | 97.9523 | -25.0717 | 97.728 | -6.1752 | -25.3098 | -25.2045 | 0.13275 | 97.9614 | -25.0122 | 97.9156 | -25.0763 | -25.1862 | -25.0305 | -0.082397 | -0.009155 | -0.23346 | 18.8141 | -0.21515 | -0.32043 | -0.13275 | -0.23804 | -0.022888 | 0 | -0.045777 | -0.086975 | -0.041199 | -0.19684 | -0.018311 | -0.17395 | 18.8965 | 122.7997 | -0.064087 | 122.9279 | 123.024 | 122.9736 | 122.9416 | 122.9507 | -123.0331 | -122.9736 | 122.7173 | 122.905 | 25.1816 | 25.1221
240.25 | 123.1613 | -24.4675 | 98.4283 | 0.030365 | -0.0030547 | 0.013223 | -0.0015317 | 0.0024482 | -0.00022641 | 0.0035354 | 0.084106 | 0.0011408 | 0.00078193 | -0.0062356 | 0.00036527 | -0.0022665 | -0.0015893 | -0.054932 | 98.3597 | -24.5865 | 98.2315 | -5.8228 | -24.7559 | -24.6414 | 0.11444 | 98.3963 | -24.5316 | 98.4283 | -24.5224 | -24.5773 | -24.4675 | -0.11902 | -0.068665 | -0.19684 | 18.6447 | -0.17395 | -0.28839 | -0.054931 | -0.16937 | -0.064087 | -0.032044 | 0 | -0.054932 | 0 | -0.10986 | 0.064087 | -0.045777 | 18.7637 | 122.818 | 0.009155 | 122.9599 | 122.9462 | 122.9279 | 122.8271 | 122.8638 | -123.0148 | -122.9599 | 122.699 | 122.8958 | 24.4125 | 24.5819
241.9219 | 123.1522 | -24.353 | 98.497 | 0.053253 | -0.00049134 | 0.013864 | -0.0013181 | -0.00096982 | 0.0014826 | 0.00075845 | 0.047485 | 0.00071343 | 0.0029181 | -0.0034586 | 0.00057887 | -0.0035483 | -0.00052114 | -0.018311 | 98.4695 | -24.4583 | 98.3963 | -6.0425 | -24.6094 | -24.4949 | 0.23804 | 98.497 | -24.4217 | 98.5428 | -24.3713 | -24.44 | -24.3576 | -0.10529 | -0.027466 | -0.10071 | 18.3105 | -0.14191 | -0.25635 | -0.036621 | -0.15106 | -0.068665 | 0 | 0.045777 | -0.018311 | -0.004578 | -0.086975 | 0.064087 | -0.01831 | 18.4158 | 122.8546 | 0.050354 | 122.9645 | 122.9279 | 122.9187 | 122.8226 | 122.85 | -122.9553 | -122.9187 | 122.7493 | 122.8958 | 24.3347 | 24.5911
243.6562 | 123.0286 | -24.733 | 98.1857 | 0.0914 | -0.0022003 | 0.013223 | 0.00039089 | 0.00095278 | 0.0010554 | 0.00011745 | 0.02002 | 0.00092703 | 0.00099553 | 0.0042318 | -0.0013437 | -0.0031211 | -0.00094854 | -0.14191 | 98.1766 | -24.852 | 97.934 | -6.2164 | -25.0397 | -24.971 | 0.082397 | 98.1949 | -24.8016 | 98.1079 | -24.8383 | -24.939 | -24.8108 | -0.11902 | -0.009155 | -0.25177 | 18.5165 | -0.23804 | -0.3067 | -0.11902 | -0.18768 | -0.068665 | 0.009155 | -0.07782 | -0.10529 | -0.07782 | -0.20599 | -0.009155 | -0.13733 | 18.6356 | 122.7859 | -0.036621 | 122.9095 | 123.0286 | 122.9965 | 122.9095 | 122.9279 | -123.0377 | -122.9874 | 122.6669 | 122.8409 | 24.5911 | 24.8154
245.3281 | 123.1064 | -24.6826 | 98.2132 | -0.0077822 | 0.00036326 | 0.016855 | -0.00067711 | -0.00096982 | 0.00062799 | 0.0018264 | 0.016968 | -0.00014097 | 0.0024909 | -0.00046783 | -6.1934e-05 | -0.0037619 | -0.0018029 | -0.19226 | 98.204 | -24.7833 | 98.0301 | -6.3858 | -24.9802 | -24.8611 | 0.068665 | 98.204 | -24.7284 | 98.1995 | -24.733 | -24.8062 | -24.678 | -0.10071 | -0.009155 | -0.18311 | 18.2968 | -0.17853 | -0.29755 | -0.07782 | -0.19684 | -0.045777 | -0.009155 | -0.013733 | -0.050354 | 0.004577 | -0.1236 | 0.050354 | -0.077819 | 18.3975 | 122.8134 | -0.004577 | 122.9279 | 122.9874 | 122.9324 | 122.8867 | 122.8867 | -122.9965 | -122.9416 | 122.7127 | 122.8821 | 24.4904 | 24.7513
247.0938 | 123.1613 | -25.1816 | 97.6685 | 0.022736 | 0.00036326 | 0.013864 | 0.00060449 | -0.002038 | -0.0027898 | 0.00204 | 0.071899 | 0.00028623 | 0.0031317 | -0.0038858 | -6.1934e-05 | -0.0020529 | -0.0015893 | -0.5127 | 97.6364 | -25.3143 | 97.5266 | -6.7795 | -25.4745 | -25.3601 | 0.14191 | 97.673 | -25.2731 | 97.7325 | -25.1953 | -25.2777 | -25.1724 | -0.13275 | -0.032043 | -0.14191 | 18.4021 | -0.17853 | -0.29297 | -0.045776 | -0.16022 | -0.091552 | 0.004578 | 0.064087 | -0.013732 | 0.009156 | -0.09613 | 0.10071 | -0.004578 | 18.5349 | 122.8409 | 0.07782 | 123.0057 | 122.9507 | 122.9462 | 122.818 | 122.8546 | -122.9828 | -122.9416 | 122.7081 | 122.9141 | 24.6689 | 25.3235
248.7812 | 123.0835 | -24.9344 | 97.998 | 0.022736 | 0.0039947 | 0.015573 | 0.0023135 | -0.00096982 | -0.0015082 | -0.0011642 | -0.059326 | -0.00014097 | -7.2674e-05 | 0.0038046 | -0.00070273 | -0.0022665 | 0.00011966 | -0.62714 | 97.9843 | -25.0488 | 97.8058 | -6.6238 | -25.2274 | -25.1541 | 0.1831 | 97.9935 | -25.0031 | 97.9523 | -25.0214 | -25.1221 | -24.9619 | -0.11444 | -0.013733 | -0.19226 | 18.3105 | -0.21973 | -0.29297 | -0.10529 | -0.17853 | -0.068665 | -0.004578 | -0.045776 | -0.086975 | -0.027466 | -0.18768 | 0.041199 | -0.11902 | 18.425 | 122.8546 | -0.01831 | 122.9553 | 123.0331 | 122.9965 | 122.9187 | 122.9279 | -123.0469 | -123.0011 | 122.7402 | 122.8867 | 24.3073 | 25.1175
250.5 | 123.1522 | -23.5565 | 99.3301 | -0.068817 | 0.0014313 | 0.015787 | 0.00039089 | -0.00075622 | -0.00044001 | 0.0016128 | 0.084106 | -0.00014097 | 0.0039861 | 0.00038657 | -0.00070273 | -0.0035483 | 0.0026831 | -1.7853 | 99.3073 | -23.6298 | 99.1516 | -4.1611 | -23.8403 | -23.7396 | 0.064087 | 99.3027 | -23.6206 | 99.3393 | -23.5886 | -23.6572 | -23.5657 | -0.073242 | -0.022888 | -0.17853 | 19.3954 | -0.1831 | -0.28381 | -0.10986 | -0.21057 | -0.064086 | -0.027466 | 0.009155 | -0.032043 | -0.009155 | -0.10071 | 0.054931 | -0.036622 | 19.4687 | 122.7814 | 0.032043 | 122.9599 | 122.937 | 122.9233 | 122.8638 | 122.8592 | -122.9599 | -122.9507 | 122.7081 | 122.8958 | 21.7712 | 23.6206
252.2344 | 123.0698 | -22.5632 | 100.3922 | 0.053253 | 0.00057686 | 0.015359 | 0.0014591 | 0.00095278 | -0.00065361 | -9.6154e-05 | -0.056274 | 0.001568 | 0.00056833 | -0.0011086 | -0.00070273 | -0.0031211 | -0.0028711 | -2.0187 | 100.383 | -22.6501 | 100.1587 | -2.0966 | -22.847 | -22.7783 | 0.1831 | 100.3967 | -22.5906 | 100.3326 | -22.5906 | -22.7188 | -22.5815 | -0.086975 | -0.009155 | -0.23346 | 20.4666 | -0.21515 | -0.28381 | -0.12817 | -0.19684 | -0.027466 | 0.004578 | -0.059509 | -0.027466 | -0.018311 | -0.15564 | 0.009155 | -0.12817 | 20.5536 | 122.8088 | 0 | 122.9233 | 123.0331 | 122.9874 | 122.9462 | 122.9599 | -123.0423 | -122.9828 | 122.7219 | 122.8958 | 20.5444 | 22.7463
253.9844 | 123.0652 | -22.8699 | 100.0626 | 0.037994 | 0.0020721 | 0.014719 | 0.0012455 | -0.0022516 | 0.0016962 | 0.00075845 | -0.06543 | 0.0013544 | 0.00056833 | 0.0059408 | -6.1934e-05 | -0.00055747 | 0.0024695 | -1.7853 | 100.0305 | -22.9843 | 99.8291 | -2.655 | -23.1812 | -23.085 | 0.16937 | 100.0717 | -22.9156 | 100.0168 | -22.9248 | -23.0484 | -22.9019 | -0.11444 | -0.032043 | -0.23346 | 20.2148 | -0.21515 | -0.31128 | -0.10071 | -0.19684 | -0.045776 | 0.009155 | -0.045776 | -0.054932 | -0.032044 | -0.17853 | 0.013732 | -0.13275 | 20.3293 | 122.8134 | -0.009156 | 122.9324 | 123.0148 | 122.9874 | 122.9004 | 122.9416 | -123.0469 | -122.9782 | 122.699 | 122.8867 | 21.0846 | 23.0392
255.7188 | 123.1155 | -22.316 | 100.5661 | -0.053558 | 0.00079046 | 0.016641 | 0.0016727 | 0.00073918 | 0.0021234 | 0.0035354 | 0.041382 | 0.001568 | 0.00014093 | -0.0066628 | 0.00036527 | -0.0024803 | 0.0028967 | -2.1057 | 100.5981 | -22.3755 | 100.415 | -1.4328 | -22.6044 | -22.4762 | 0.086975 | 100.5707 | -22.3572 | 100.5844 | -22.3526 | -22.4213 | -22.3114 | -0.059509 | 0.032044 | -0.15106 | 20.8832 | -0.16022 | -0.28839 | -0.10071 | -0.22888 | -0.041199 | 0.004578 | 0.018311 | -0.036621 | 0.004578 | -0.10529 | 0.045777 | -0.064087 | 20.9427 | 122.7905 | 0.004578 | 122.9416 | 122.9736 | 122.9279 | 122.9141 | 122.8867 | -122.9416 | -122.9233 | 122.731 | 122.9004 | 20.2103 | 22.403
257.3906 | 123.1567 | -23.3368 | 99.5453 | -0.0383 | 0.0037811 | 0.018137 | 0.00039089 | -0.003106 | 0.00041439 | 0.0060988 | 0.010864 | -0.00056817 | 0.0027045 | -0.0049538 | -0.0015573 | 0.00029693 | -0.00094854 | -2.3071 | 99.472 | -23.4421 | 99.4995 | -3.3142 | -23.4283 | -23.2315 | 0.35248 | 99.7147 | -23.1766 | 99.559 | -23.3826 | -23.4467 | -23.3231 | -0.10529 | -0.073242 | -0.045776 | 20.0226 | 0.10529 | -0.091553 | 0.21057 | 0.013733 | 0.16022 | 0.16937 | 0.013733 | -0.045776 | 0.013733 | -0.10986 | -0.14648 | -0.27008 | 20.1279 | 122.9416 | -0.20599 | 122.7356 | 122.9141 | 122.8912 | 122.8088 | 123.0515 | -122.9874 | -122.7219 | 122.8363 | 122.8958 | 21.0297 | 23.6893
259.1406 | 123.0194 | -22.7417 | 100.2136 | 0.037994 | 0.0027131 | 0.016855 | 0.0018863 | 0.0018072 | 0.0021234 | -0.00073695 | -0.068481 | 0.0022088 | 0.0014227 | 0.0033774 | 0.0020743 | 0.00051053 | -0.0013757 | -2.1835 | 100.2136 | -22.8561 | 99.9069 | -2.6276 | -23.1308 | -23.0255 | 0.050354 | 100.1862 | -22.8104 | 100.1083 | -22.8836 | -22.9889 | -22.8287 | -0.11444 | 0 | -0.3067 | 20.1141 | -0.28381 | -0.3891 | -0.16937 | -0.27466 | -0.068665 | -0.027466 | -0.10529 | -0.14191 | -0.086975 | -0.24719 | -0.01831 | -0.17853 | 20.2286 | 122.7631 | -0.073242 | 122.9187 | 123.0698 | 122.9965 | 122.9553 | 122.9279 | -123.0698 | -123.024 | 122.6486 | 122.85 | 20.5582 | 22.7921
260.8125 | 123.056 | -22.2244 | 100.7584 | -0.015411 | -0.0011321 | 0.016214 | 0.0035953 | 0.0020208 | -0.00086721 | 0.0011856 | -0.053223 | 0.0019952 | 0.0020635 | 0.0042318 | 0.00057887 | -0.00034387 | -0.00052114 | -2.3575 | 100.7217 | -22.3251 | 100.502 | -1.6296 | -22.5128 | -22.4258 | 0.16022 | 100.6668 | -22.2702 | 100.6897 | -22.2702 | -22.3618 | -22.2427 | -0.10071 | -0.036621 | -0.25635 | 20.5948 | -0.20142 | -0.28839 | -0.10071 | -0.18768 | -0.045777 | -0.091553 | -0.068665 | -0.045777 | -0.018311 | -0.13733 | 0.027466 | -0.091552 | 20.6955 | 122.8271 | 0 | 122.9599 | 123.0469 | 122.937 | 122.9462 | 122.8912 | -123.0835 | -123.0286 | 122.7264 | 122.9141 | 19.8669 | 22.3846
262.5469 | 123.0194 | -21.9406 | 101.0193 | -0.015411 | -0.00049134 | 0.013864 | 0.0029545 | -0.002038 | -0.001081 | -0.00095055 | -0.050171 | 0.0013544 | 0.00078193 | 0.001882 | 0.0016471 | -0.0035483 | -0.00052114 | -1.6022 | 101.0239 | -22.0322 | 100.7126 | -1.2405 | -22.3068 | -22.1924 | 0.041199 | 101.0239 | -21.9955 | 100.9186 | -22.0505 | -22.1512 | -22.0047 | -0.091553 | 0.004578 | -0.3067 | 20.7001 | -0.25177 | -0.36621 | -0.16022 | -0.27466 | -0.054931 | 0.004578 | -0.10071 | -0.10986 | -0.064087 | -0.21057 | -0.009156 | -0.15564 | 20.7916 | 122.7448 | -0.054932 | 122.9141 | 123.056 | 123.0194 | 122.9645 | 122.9645 | -123.0515 | -123.0148 | 122.6532 | 122.8592 | 20.3384 | 21.9818
264.2188 | 123.0698 | -21.4279 | 101.532 | 0.060882 | -0.0011321 | 0.016428 | 0.0020999 | -0.0028924 | -0.00086721 | -0.0018052 | 0.001709 | 0.0022088 | 0.0016363 | 0.001882 | 0.00036527 | -0.0024803 | -0.00073494 | -0.32959 | 101.4816 | -21.5424 | 101.2344 | -0.39825 | -21.7255 | -21.6568 | 0.13275 | 101.5091 | -21.4783 | 101.4359 | -21.4966 | -21.5927 | -21.4737 | -0.11444 | -0.050354 | -0.29755 | 21.0297 | -0.22888 | -0.29755 | -0.11444 | -0.18311 | -0.050354 | -0.022888 | -0.09613 | -0.068665 | -0.045777 | -0.16479 | 0.004577 | -0.11444 | 21.1441 | 122.7768 | -0.018311 | 122.9141 | 123.024 | 122.9874 | 122.9095 | 122.937 | -123.0743 | -123.0103 | 122.6624 | 122.8638 | 21.0983 | 21.5607
265.9531 | 123.175 | -21.4142 | 101.4587 | -0.00015269 | -0.00049134 | 0.015359 | -0.00024991 | -0.0041742 | -0.00065361 | 0.0011856 | 0.099365 | -0.0016364 | 0.0016363 | -0.002604 | 0.00079247 | -0.0037619 | 0.00033326 | -0.24719 | 101.3855 | -21.5286 | 101.3306 | -0.15564 | -21.611 | -21.5561 | 0.21057 | 101.413 | -21.4966 | 101.4816 | -21.4096 | -21.4874 | -21.405 | -0.11444 | -0.073242 | -0.12817 | 21.2585 | -0.14191 | -0.19684 | -0.027466 | -0.082398 | -0.082397 | -0.045776 | 0.022888 | 0.004578 | 0.009156 | -0.073242 | 0.091553 | 0.009155 | 21.373 | 122.8592 | 0.086975 | 122.9782 | 122.9141 | 122.9095 | 122.7997 | 122.8271 | -122.9874 | -122.9553 | 122.7448 | 122.8958 | 21.167 | 21.6248
267.625 | 123.1613 | -23.1903 | 99.6735 | 0.022736 | 0.00079046 | 0.016641 | -0.0032407 | -0.003106 | 0.00020079 | 0.0013992 | 0.078003 | 7.2626e-05 | 0.0016363 | 0.0044456 | 0.00015167 | -0.0016257 | 0.0026831 | -0.32044 | 99.6002 | -23.3276 | 99.6048 | -3.7491 | -23.3963 | -23.3871 | 0.17395 | 99.6368 | -23.3047 | 99.6552 | -23.2132 | -23.2224 | -23.085 | -0.13733 | -0.073242 | -0.068665 | 19.4412 | -0.19684 | -0.20599 | -0.059509 | -0.068664 | -0.11444 | -0.036621 | -0.018311 | -0.022888 | 0.10529 | -0.032043 | 0.21973 | 0.082398 | 19.5786 | 122.9324 | 0.091553 | 122.9599 | 122.9279 | 122.9416 | 122.7905 | 122.8271 | -123.0011 | -122.9782 | 122.7951 | 122.8455 | 22.8699 | 23.3643
269.3594 | 123.0606 | -22.0276 | 100.9323 | 0.037994 | 0.00014946 | 0.014505 | 0.0025271 | 0.00052558 | 0.0036188 | -0.00030975 | -0.053223 | 0.0024224 | 0.00056833 | 0.0040182 | -0.0011301 | -0.00098487 | -0.0015893 | 0.26093 | 100.9415 | -22.0734 | 100.7126 | -1.4603 | -22.261 | -22.1878 | 0.21057 | 100.9552 | -22.0322 | 100.8591 | -22.1008 | -22.1832 | -22.0688 | -0.045776 | 0.009155 | -0.21973 | 20.5673 | -0.16022 | -0.23346 | -0.11444 | -0.18768 | -0.004578 | 0.022888 | -0.073242 | -0.073242 | -0.041199 | -0.15564 | -0.036621 | -0.15106 | 20.6131 | 122.7859 | -0.068664 | 122.8912 | 123.0148 | 122.9874 | 122.9691 | 122.9828 | -123.0057 | -122.9645 | 122.7402 | 122.8867 | 22.2885 | 22.2382
271.0938 | 123.1384 | -21.698 | 101.1978 | -0.00015269 | 0.0027131 | 0.016 | 0.00081809 | 0.0039436 | -0.00044001 | -0.00052335 | -0.0013428 | -0.00014097 | 0.00099553 | 0.0033774 | 0.00079247 | -0.0035483 | -0.00030754 | 0.6134 | 101.1887 | -21.8079 | 100.9827 | -0.92468 | -22.023 | -21.9269 | 0.14191 | 101.1887 | -21.7529 | 101.2024 | -21.7392 | -21.817 | -21.6705 | -0.10986 | -0.009155 | -0.21515 | 20.7733 | -0.22888 | -0.32501 | -0.11902 | -0.21515 | -0.054932 | -0.009155 | 0.004578 | -0.041199 | 0.027466 | -0.11902 | 0.082398 | -0.064087 | 20.8832 | 122.7905 | 0.013733 | 122.9553 | 122.9965 | 122.9416 | 122.8867 | 122.8867 | -123.0057 | -122.9507 | 122.6807 | 122.9004 | 22.3114 | 21.8399
272.8438 | 123.0743 | -21.4508 | 101.5091 | 0.053253 | -0.00091854 | 0.017068 | 0.0014591 | -0.0016106 | -0.00022641 | -0.00030975 | -0.0074462 | 0.0011408 | 0.0024909 | -4.063e-05 | -0.00091653 | -0.0029075 | 0.0026831 | 0.72784 | 101.4908 | -21.5515 | 101.2299 | -0.50812 | -21.73 | -21.666 | 0.15106 | 101.4862 | -21.4874 | 101.4359 | -21.5103 | -21.5927 | -21.4737 | -0.10071 | -0.01831 | -0.27924 | 20.9427 | -0.21515 | -0.27924 | -0.11444 | -0.17853 | -0.036621 | -0.022888 | -0.073242 | -0.059509 | -0.022888 | -0.14191 | 0.013733 | -0.10528 | 21.0434 | 122.7814 | -0.022888 | 122.9233 | 123.0423 | 122.9736 | 122.9416 | 122.937 | -123.0606 | -122.9965 | 122.6807 | 122.8867 | 22.1787 | 21.6019
274.5781 | 123.175 | -23.0896 | 99.7925 | 0.022736 | -6.4144e-05 | 0.015787 | -0.00089091 | -0.00054262 | -0.0012946 | -0.00073695 | 0.084106 | 0.00028623 | -0.0013543 | -0.006022 | -0.00091653 | -0.0024803 | 0.0033241 | 0.59509 | 99.765 | -23.204 | 99.646 | -3.5751 | -23.3139 | -23.2269 | 0.24261 | 99.7787 | -23.1354 | 99.8154 | -23.0804 | -23.1354 | -23.053 | -0.11444 | -0.027465 | -0.14648 | 19.5145 | -0.13733 | -0.2243 | -0.022888 | -0.10986 | -0.045776 | -0.013732 | 0.022889 | 0.009156 | 0.036621 | -0.045776 | 0.082397 | 0 | 19.6289 | 122.85 | 0.054932 | 122.9507 | 122.9691 | 122.9141 | 122.8546 | 122.8683 | -122.9965 | -122.9279 | 122.7356 | 122.905 | 23.6847 | 23.3322
276.2344 | 123.0423 | -22.2107 | 100.7492 | -0.00015269 | 0.0020721 | 0.016428 | 0.0025271 | -0.00011542 | 0.00041439 | 0.00033105 | -0.037964 | 0.00071343 | 0.0052679 | -0.0034586 | -6.1934e-05 | -0.00034387 | 0.00076046 | 1.6708 | 100.6393 | -22.4258 | 100.5249 | -1.5656 | -22.4899 | -22.5037 | -0.050354 | 100.7126 | -22.3068 | 100.6851 | -22.3022 | -22.4304 | -22.2427 | -0.21515 | -0.10986 | -0.22431 | 20.6451 | -0.29297 | -0.27924 | -0.07782 | -0.064087 | -0.096131 | -0.036622 | -0.064087 | -0.091553 | -0.032044 | -0.21973 | 0.064087 | -0.1236 | 20.8603 | 122.9507 | 0.004578 | 122.9919 | 123.0652 | 123.0194 | 122.85 | 122.9233 | -123.175 | -123.056 | 122.7356 | 122.8958 | 23.8815 | 22.1603
277.9688 | 123.143 | -24.3896 | 98.4924 | 0.053253 | -0.00049134 | 0.01365 | -0.00046351 | -0.003106 | -0.0015082 | -0.00073695 | 0.047485 | 0.0030634 | 0.0018499 | -0.00089503 | -0.0028391 | -0.0024803 | 0.0018287 | 1.1902 | 98.4558 | -24.5041 | 98.3505 | -6.6147 | -24.6277 | -24.5316 | 0.2655 | 98.5016 | -24.4537 | 98.5657 | -24.4171 | -24.5132 | -24.3896 | -0.11444 | -0.036621 | -0.14191 | 17.775 | -0.14191 | -0.23804 | -0.027466 | -0.1236 | -0.064087 | 0.009155 | 0.073242 | -0.027466 | 0 | -0.1236 | 0.064087 | -0.05951 | 17.8894 | 122.8546 | 0.036621 | 123.0194 | 122.9599 | 122.9553 | 122.8455 | 122.8912 | -122.9965 | -122.9462 | 122.7402 | 122.9553 | 25.5798 | 24.6552
279.7031 | 123.1522 | -24.1241 | 98.7488 | -0.084076 | 0.00079046 | 0.015787 | 0.0029545 | 0.0028754 | 0.001269 | 0.00011745 | -0.019653 | 0.00049983 | 0.0014227 | 0.001882 | -0.0017709 | -0.0022665 | -0.0050073 | 0.98877 | 98.6023 | -24.3668 | 98.5016 | -6.3492 | -24.4583 | -24.4812 | 0.16479 | 98.6481 | -24.2569 | 98.7808 | -24.202 | -24.2981 | -24.1196 | -0.24261 | -0.14648 | -0.24719 | 17.775 | -0.35705 | -0.33417 | -0.11444 | -0.091553 | -0.13275 | -0.10071 | 0.032044 | -0.077819 | 0.004578 | -0.17395 | 0.13733 | -0.041199 | 18.0176 | 122.8683 | 0.054932 | 123.0377 | 122.9691 | 122.905 | 122.7264 | 122.7722 | -123.1155 | -123.0057 | 122.6257 | 122.905 | 25.1129 | 24.2889
281.375 | 123.1155 | -23.8541 | 99.0601 | -0.0077822 | 0.00057686 | 0.012369 | 0.0023135 | 0.0043708 | -0.00065361 | 0.0011856 | -0.016602 | 0.00028623 | 0.0033453 | -0.0017496 | 0.00015167 | -0.0011985 | 0.0028967 | 1.5427 | 98.7991 | -24.1882 | 98.8174 | -5.1636 | -24.1928 | -24.1013 | 0.27008 | 99.0738 | -23.9044 | 99.0738 | -23.8998 | -24.0051 | -23.8586 | -0.33417 | -0.26093 | -0.24262 | 18.6905 | -0.24719 | -0.33875 | 0.086975 | -0.004578 | -0.050354 | 0.013733 | 0.013733 | -0.045776 | -0.004578 | -0.15106 | 0.045776 | -0.10071 | 19.0247 | 123.0057 | 0.004578 | 122.9782 | 122.9874 | 122.9782 | 122.6532 | 122.9279 | -123.2483 | -122.9645 | 122.6715 | 122.9279 | 25.3967 | 24.1241
283.125 | 123.0652 | -22.4075 | 100.5524 | -0.023041 | 0.00057686 | 0.014078 | -3.6308e-05 | 0.0015936 | 0.0016962 | 0.00204 | -0.03186 | 0.0019952 | 0.00056833 | 0.00060037 | 0.0012199 | -0.0037619 | 0.0024695 | 2.2888 | 100.5203 | -22.5128 | 100.2777 | -1.9913 | -22.7142 | -22.6456 | 0.26093 | 100.5341 | -22.4625 | 100.4608 | -22.4625 | -22.5769 | -22.4396 | -0.10528 | -0.032043 | -0.27466 | 20.4163 | -0.23804 | -0.3067 | -0.13275 | -0.20142 | -0.054931 | -0.01831 | -0.091553 | -0.054931 | -0.032043 | -0.16937 | 0.022888 | -0.11444 | 20.5215 | 122.7905 | 0 | 122.9233 | 123.0331 | 122.9965 | 122.9279 | 122.9416 | -123.0652 | -123.0148 | 122.6852 | 122.8683 | 24.6963 | 22.6685
284.8125 | 123.1247 | -23.1491 | 99.733 | 0.0074768 | 0.00079046 | 0.016641 | 0.00039089 | 0.0020208 | -0.001081 | 0.0024674 | 0.035278 | -0.00014097 | 0.0024909 | 0.00038657 | -0.00070273 | -0.0016257 | -0.0043665 | 1.8494 | 99.7192 | -23.2452 | 99.6048 | -2.2202 | -23.3871 | -23.2819 | 0.18768 | 99.7147 | -23.1903 | 99.7604 | -23.1857 | -23.2544 | -23.1445 | -0.09613 | -0.013733 | -0.12817 | 20.929 | -0.13275 | -0.23804 | -0.036621 | -0.14191 | -0.041199 | -0.01831 | 0.027466 | -0.036621 | 0.004578 | -0.10529 | 0.045777 | -0.064087 | 21.0251 | 122.85 | 0.004578 | 122.9507 | 122.9645 | 122.905 | 122.8683 | 122.8638 | -122.9782 | -122.9233 | 122.7539 | 122.9095 | 24.9985 | 23.3368
286.5469 | 123.0835 | -27.507 | 95.4025 | -0.00015269 | 0.0010041 | 0.015146 | 0.0025271 | -0.002038 | 0.0021234 | 0.00075845 | -0.044067 | 0.0013544 | 0.0018499 | 0.0027366 | -0.00070273 | -0.0014121 | -9.3938e-05 | 0.82855 | 95.3751 | -27.6398 | 95.1233 | -10.0388 | -27.9099 | -27.8 | 0.013733 | 95.3659 | -27.6215 | 95.3796 | -27.6306 | -27.7176 | -27.5665 | -0.13275 | -0.027466 | -0.27924 | 17.4683 | -0.29297 | -0.40283 | -0.16022 | -0.27008 | -0.11444 | -0.036621 | -0.022888 | -0.1236 | -0.059509 | -0.21057 | 0.054932 | -0.09613 | 17.601 | 122.7631 | -0.009155 | 123.0011 | 123.0148 | 122.9874 | 122.8821 | 122.8729 | -123.0423 | -123.024 | 122.6303 | 122.8867 | 28.3356 | 27.5208
288.2969 | 123.0606 | -28.5278 | 94.4733 | 0.099029 | -0.0034821 | 0.010233 | 0.0016727 | -0.00011542 | -0.00065361 | -0.00073695 | 0.035278 | 0.0022088 | 0.0018499 | -0.0021768 | -0.00027553 | -0.0029075 | -0.0043665 | 0.49896 | 94.3222 | -28.6972 | 94.1116 | -12.2772 | -28.949 | -28.8712 | -0.068665 | 94.3405 | -28.6285 | 94.2902 | -28.6377 | -28.7109 | -28.569 | -0.16937 | -0.15106 | -0.36163 | 16.2506 | -0.34332 | -0.42114 | -0.17395 | -0.25177 | -0.10071 | -0.13275 | -0.18311 | -0.10986 | -0.041199 | -0.18311 | 0.059509 | -0.082397 | 16.42 | 122.8088 | -0.009155 | 122.9187 | 123.0194 | 122.9691 | 122.85 | 122.8683 | -123.1705 | -123.1018 | 122.6395 | 122.818 | 29.0268 | 28.4592
289.9688 | 123.1293 | -24.7101 | 98.2132 | -0.0077822 | 0.00014946 | 0.014505 | -3.6308e-05 | -0.0018244 | 0.0025506 | 0.00033105 | 0.062744 | 0.0013544 | 0.00056833 | -0.010081 | 0.00079247 | -0.0029075 | 0.0014015 | 1.0117 | 98.1674 | -24.8154 | 97.998 | -3.7949 | -24.9893 | -24.8749 | 0.054932 | 98.1995 | -24.733 | 98.1812 | -24.7513 | -24.8337 | -24.7147 | -0.10529 | -0.045777 | -0.21515 | 20.9152 | -0.16479 | -0.27924 | -0.059509 | -0.17395 | -0.022888 | -0.013733 | -0.032044 | -0.041199 | -0.004578 | -0.1236 | 0.01831 | -0.10071 | 21.0205 | 122.8134 | -0.018311 | 122.9141 | 122.9828 | 122.9324 | 122.8775 | 122.9095 | -123.0286 | -122.9462 | 122.7081 | 122.8912 | 25.7217 | 24.765
291.7031 | 122.9965 | -23.8037 | 99.1333 | -0.00015269 | -0.00049134 | 0.015573 | 0.0031681 | -0.00011542 | 0.00084159 | 0.0016128 | -0.053223 | 0.0022088 | 0.00099553 | 0.00017297 | 0.0018607 | -0.00055747 | -0.0018029 | 1.3641 | 99.0738 | -23.9273 | 98.8312 | -3.3508 | -24.2065 | -24.1058 | 0.13275 | 99.1104 | -23.8907 | 99.0189 | -23.9502 | -24.0463 | -23.8815 | -0.1236 | -0.059509 | -0.30212 | 20.4529 | -0.30212 | -0.40283 | -0.17853 | -0.27924 | -0.086975 | -0.022888 | -0.11444 | -0.14648 | -0.07782 | -0.24262 | 0.009155 | -0.15564 | 20.5765 | 122.7585 | -0.059509 | 122.9095 | 123.0011 | 123.0011 | 122.8775 | 122.9141 | -123.0606 | -123.024 | 122.6349 | 122.8226 | 25.1678 | 23.9365
293.375 | 123.0103 | -20.2332 | 102.7359 | 0.015106 | 0.0018585 | 0.017923 | 0.0023135 | -0.00011542 | 0.00084159 | 0.0022536 | -0.041016 | 0.0024224 | -7.2674e-05 | 0.0040182 | -0.00070273 | -0.0020529 | 0.00076046 | 1.7944 | 102.7817 | -20.2927 | 102.5024 | -5.6305 | -20.4941 | -20.3979 | 0.15106 | 102.8046 | -20.2148 | 102.626 | -20.3201 | -20.4254 | -20.2927 | -0.05951 | 0.045776 | -0.23346 | 14.6027 | -0.1648 | -0.26093 | -0.10529 | -0.20142 | 0.01831 | 0.068664 | -0.10986 | -0.086975 | -0.05951 | -0.19226 | -0.07782 | -0.21057 | 14.6622 | 122.7951 | -0.10529 | 122.8409 | 123.0743 | 123.0194 | 123.0148 | 123.0377 | -123.0286 | -122.9507 | 122.7356 | 122.8592 | 22.0276 | 20.3842
295.0938 | 123.111 | -20.4483 | 102.4429 | -0.023041 | 0.00079046 | 0.016 | -0.00067711 | 0.00031198 | 0.00020079 | 0.00097205 | 0.059692 | 0.00071343 | -0.00028627 | -0.0070902 | 0.00057887 | -0.0037619 | 0.0037513 | 2.037 | 102.4429 | -20.4803 | 102.3514 | -7.4066 | -20.5994 | -20.4849 | 0.18768 | 102.507 | -20.4117 | 102.4521 | -20.4758 | -20.5399 | -20.43 | -0.032044 | 0 | -0.091553 | 13.0417 | -0.036621 | -0.15106 | -0.004577 | -0.11902 | 0.036621 | 0.064087 | 0.009155 | -0.027466 | 0.01831 | -0.091553 | -0.018311 | -0.12817 | 13.0737 | 122.8317 | -0.064087 | 122.8638 | 122.9233 | 122.9187 | 122.8912 | 122.9553 | -122.9233 | -122.8546 | 122.7997 | 122.9004 | 22.4854 | 20.636
296.8281 | 123.0194 | -21.286 | 101.7014 | 0.083771 | -0.0017731 | 0.016428 | 0.0012455 | 0.00052558 | -1.2808e-05 | -0.0018052 | 0.023071 | 0.00028623 | 0.0018499 | -0.0021768 | -0.00048913 | -0.0037619 | -0.0013757 | 1.2772 | 101.6922 | -21.3684 | 101.3855 | -6.1935 | -21.5561 | -21.4737 | 0.10986 | 101.6739 | -21.3409 | 101.5732 | -21.3684 | -21.4554 | -21.3272 | -0.082397 | -0.009155 | -0.31586 | 15.0925 | -0.18768 | -0.27008 | -0.10529 | -0.18768 | -0.054931 | -0.027466 | -0.12817 | -0.082397 | -0.041198 | -0.16937 | 0.013733 | -0.11444 | 15.1749 | 122.7539 | -0.027466 | 122.9141 | 123.0606 | 123.0148 | 122.9782 | 122.9599 | -123.0698 | -123.0423 | 122.6715 | 122.8592 | 22.5632 | 21.3959
298.5781 | 123.0194 | -19.3359 | 103.6331 | -0.03067 | 0.0033539 | 0.017709 | 0.0023135 | 0.0043708 | 0.00084159 | 0.00011745 | -0.041016 | 0.001568 | 0.0016363 | 0.003591 | 0.00079247 | -0.0046165 | -0.0018029 | 1.4557 | 103.7933 | -19.2673 | 103.4225 | -9.2972 | -19.5831 | -19.4962 | 0.036621 | 103.7292 | -19.2947 | 103.569 | -19.4092 | -19.5923 | -19.4321 | 0.068664 | 0.16022 | -0.21057 | 10.0388 | -0.16022 | -0.24719 | -0.22888 | -0.31586 | 0.041198 | 0.09613 | -0.064087 | -0.073243 | -0.096131 | -0.25635 | -0.13733 | -0.29755 | 9.9701 | 122.6898 | -0.11444 | 122.8638 | 123.0606 | 123.024 | 123.1293 | 123.0652 | -122.9004 | -122.9279 | 122.7585 | 122.905 | 20.7916 | 19.3726
300.2344 | 123.0423 | -15.5548 | 107.428 | 0.10666 | 0.0012177 | 0.016641 | 0.00039089 | 0.0033026 | -1.2808e-05 | 0.0039626 | 0.001709 | 7.2626e-05 | 0.0012091 | -0.0013224 | 0.00057887 | -0.0022665 | -0.0026575 | 1.886 | 107.4738 | -15.5777 | 107.1854 | -8.4915 | -15.683 | -15.6189 | 0.15564 | 107.4738 | -15.5548 | 107.3181 | -15.5594 | -15.6647 | -15.564 | -0.022888 | 0.045776 | -0.24261 | 7.0633 | -0.064086 | -0.12817 | -0.041198 | -0.10529 | 0 | 0.045776 | -0.10986 | -0.004577 | -0.009155 | -0.10986 | -0.009155 | -0.10986 | 7.0862 | 122.7631 | -0.004577 | 122.8729 | 123.0515 | 123.0286 | 123.0286 | 123.0286 | -123.0057 | -122.9828 | 122.7402 | 122.8729 | 17.4408 | 15.7104
301.9688 | 123.1338 | -12.5244 | 110.4309 | -0.0077822 | -0.0024139 | 0.018777 | -0.0011045 | -0.0022516 | 0.00062799 | -9.6154e-05 | 0.078003 | 0.0017816 | 0.0020635 | -0.0034586 | 0.0014335 | -0.0046165 | 0.0037513 | 2.3163 | 110.408 | -12.5931 | 110.1929 | -7.196 | -12.6434 | -12.5565 | 0.21973 | 110.3989 | -12.5702 | 110.4126 | -12.41 | -12.5015 | -12.4283 | -0.068665 | -0.022888 | -0.23804 | 5.3284 | -0.032044 | -0.11902 | 0.036621 | -0.050354 | -0.045776 | -0.032043 | -0.01831 | 0.11444 | 0.09613 | 0.022888 | 0.14191 | 0.068664 | 5.397 | 122.7859 | 0.16022 | 122.9828 | 123.0011 | 122.9691 | 122.9324 | 122.9233 | -123.024 | -123.0011 | 122.7173 | 122.937 | 14.8407 | 12.7441
303.7031 | 123.0927 | -11.4944 | 111.438 | -0.023041 | 0.00014946 | 0.020486 | -0.0013181 | -0.00032902 | -1.2808e-05 | -0.00052335 | 0.023071 | 0.00071343 | -7.2674e-05 | -0.00089503 | -0.0013437 | -0.0037619 | -0.00052114 | 1.4465 | 111.4838 | -11.5219 | 111.2823 | -5.6442 | -11.5677 | -11.4761 | 0.20142 | 111.4471 | -11.5265 | 111.4105 | -11.3937 | -11.4761 | -11.3846 | -0.027466 | 0.045777 | -0.15564 | 5.8502 | 0.018311 | -0.073242 | 0.045777 | -0.045776 | -0.032043 | 0.009156 | -0.027466 | 0.10071 | 0.10986 | 0.018311 | 0.14191 | 0.050354 | 5.8777 | 122.8043 | 0.13275 | 122.937 | 123.0057 | 122.9736 | 122.9782 | 122.9416 | -122.9599 | -122.9645 | 122.7768 | 122.905 | 12.941 | 11.6959
305.4531 | 123.1247 | -13.9389 | 108.989 | 0.037994 | 0.0020721 | 0.017923 | -0.0011045 | -0.00032902 | -0.00044001 | -0.0015916 | 0.053589 | 0.00049983 | 0.0012091 | 0.00038657 | -0.00027553 | -0.0033347 | -0.0069299 | 0.64087 | 108.9249 | -14.0625 | 108.7189 | -7.1136 | -14.1083 | -14.0533 | 0.19226 | 108.9478 | -14.0121 | 109.0073 | -13.829 | -13.8977 | -13.9023 | -0.1236 | -0.064087 | -0.27008 | 6.8253 | -0.11444 | -0.16937 | 0.009155 | -0.045776 | -0.073242 | -0.041199 | 0.01831 | 0.10986 | 0.036621 | 0.041199 | 0.10986 | 0.11444 | 6.9489 | 122.7814 | 0.1831 | 123.0194 | 122.9874 | 122.9599 | 122.8638 | 122.8867 | -123.0515 | -123.0011 | 122.6578 | 122.9462 | 14.5798 | 14.1312
307.125 | 123.1567 | -11.3388 | 111.6119 | -0.045929 | -0.0024139 | 0.017923 | -0.0011045 | -0.003747 | -0.00086721 | 0.00075845 | 0.059692 | -0.00099557 | 0.0014227 | -0.0019632 | -6.1934e-05 | -0.0024803 | -0.0018029 | 2.6138 | 111.5158 | -11.4304 | 111.4197 | -5.8273 | -11.4075 | -11.3205 | 0.32501 | 111.5799 | -11.4029 | 111.6028 | -11.1969 | -11.261 | -11.2061 | -0.091553 | -0.09613 | -0.19226 | 5.5115 | 0.01831 | -0.068665 | 0.10986 | 0.022888 | -0.064087 | -0.032043 | -0.009155 | 0.14191 | 0.13275 | 0.07782 | 0.19684 | 0.14191 | 5.603 | 122.85 | 0.20599 | 123.0057 | 122.9462 | 122.9828 | 122.8546 | 122.9187 | -123.0423 | -123.0148 | 122.7585 | 122.9416 | 13.9526 | 11.6638
308.875 | 123.0606 | -12.3779 | 110.6277 | 0.015106 | -0.0015595 | 0.017923 | 0.0029545 | 0.00095278 | -1.2808e-05 | 0.0022536 | -0.01355 | 0.001568 | 0.00056833 | -0.0023904 | 0.00036527 | -0.00077127 | 0.00054686 | 0.94299 | 110.6049 | -12.4191 | 110.3348 | -6.3721 | -12.5198 | -12.4786 | 0.16937 | 110.6369 | -12.4191 | 110.5225 | -12.3093 | -12.4283 | -12.3459 | -0.041198 | -0.022889 | -0.29297 | 6.0059 | -0.10071 | -0.14191 | -0.05951 | -0.10071 | -0.041198 | 0.009155 | -0.10529 | 0.068665 | 0.032044 | -0.050354 | 0.073242 | -0.009156 | 6.0471 | 122.7539 | 0.10986 | 122.9416 | 123.024 | 123.056 | 122.9828 | 123.0148 | -123.0469 | -123.0469 | 122.7127 | 122.9004 | 13.3209 | 12.5473
310.5469 | 123.1522 | -11.8607 | 111.0214 | -0.0077822 | 0.00014946 | 0.0207 | -0.0023861 | -0.006524 | 0.0019098 | 0.0016128 | 0.056641 | 0.00049983 | 0.00078193 | -0.00089503 | -0.00070273 | -0.0050437 | -0.00052114 | 2.2385 | 111.0306 | -11.9339 | 110.8749 | -5.8136 | -11.9476 | -11.8423 | 0.27466 | 111.0168 | -11.9202 | 111.0992 | -11.7371 | -11.8286 | -11.7599 | -0.073242 | 0.009156 | -0.14648 | 6.0471 | 0.018311 | -0.086975 | 0.091553 | -0.013733 | -0.059509 | -0.004577 | 0.07782 | 0.1236 | 0.10071 | 0.032044 | 0.16022 | 0.091553 | 6.1203 | 122.8088 | 0.1831 | 123.0194 | 122.9645 | 122.937 | 122.8912 | 122.8775 | -122.9553 | -122.9416 | 122.7356 | 122.9599 | 14.0991 | 12.1353
312.2812 | 123.0743 | -1.0483 | 121.9574 | 0.037994 | 0.0010041 | 0.036722 | 0.0023135 | -0.001397 | -0.0012946 | -9.6154e-05 | -0.047119 | 0.0019952 | 0.00099553 | -0.0011086 | -0.0019845 | 0.00051053 | -0.00094854 | 6.2805 | 121.9391 | -1.1124 | 121.6827 | -0.52185 | -1.0529 | -0.95673 | 0.31586 | 121.9803 | -1.1078 | 121.9025 | -0.86975 | -0.94757 | -0.8606 | -0.064087 | -0.01831 | -0.27466 | 0.52643 | 0.091553 | -0.004577 | 0.15564 | 0.05951 | -0.059509 | 0.022889 | -0.054931 | 0.17853 | 0.18768 | 0.10071 | 0.24719 | 0.16022 | 0.59052 | 122.7951 | 0.23804 | 123.0103 | 123.0515 | 123.0881 | 122.9874 | 123.0286 | -123.0698 | -123.0652 | 122.731 | 122.9507 | 7.3288 | 1.3641
314.0312 | 123.0423 | -1.0254 | 122.0398 | 0.037994 | -0.00049134 | 0.035654 | 0.00017729 | -0.0041742 | 0.0014826 | 0.0024674 | -0.0043944 | 0.0028498 | -0.0013543 | 0.0038046 | 0.0018607 | -0.0044029 | 0.00033326 | 8.0292 | 122.0169 | -1.0803 | 121.669 | -0.56763 | -1.0254 | -0.94299 | 0.20599 | 122.0398 | -1.0941 | 121.8887 | -0.85144 | -0.92468 | -0.86517 | -0.054931 | -0.022888 | -0.37079 | 0.45776 | 0.082398 | 0 | 0.13733 | 0.054931 | -0.068664 | 0 | -0.15106 | 0.17395 | 0.16022 | 0.10071 | 0.22888 | 0.16937 | 0.5127 | 122.7493 | 0.24262 | 122.9828 | 123.0972 | 123.1338 | 123.0423 | 123.0652 | -123.1201 | -123.1338 | 122.6944 | 122.9141 | 9.0546 | 1.2314
315.7031 | 123.0469 | -1.0574 | 121.9666 | 0.045624 | -0.0026275 | 0.036081 | 0.00039089 | -0.00075622 | -0.00065361 | 0.0018264 | 0.0047608 | 0.00028623 | -0.00028627 | -0.0011086 | -0.00091653 | -0.0029075 | 0.0022559 | 6.1386 | 121.962 | -1.1032 | 121.6553 | -0.56305 | -1.0437 | -0.95215 | 0.21973 | 122.0078 | -1.1169 | 121.8521 | -0.87891 | -0.94757 | -0.90179 | -0.045776 | -0.004578 | -0.31128 | 0.49438 | 0.10529 | 0.013733 | 0.15106 | 0.059509 | -0.059509 | 0.041198 | -0.11444 | 0.17853 | 0.15564 | 0.10986 | 0.21515 | 0.16937 | 0.54016 | 122.7585 | 0.23804 | 122.9691 | 123.0652 | 123.1247 | 123.0194 | 123.0652 | -123.0698 | -123.0835 | 122.7127 | 122.9095 | 7.196 | 1.2772
317.4375 | 123.1522 | -0.98419 | 121.9849 | -0.03067 | 0.00079046 | 0.036935 | 0.0027407 | 0.0037298 | 0.0034052 | -9.6154e-05 | 0.0047608 | 0.0013544 | 0.00056833 | -0.003245 | 0.00057887 | -0.0014121 | -0.00030754 | 7.0633 | 121.9849 | -1.0666 | 121.7606 | -0.50812 | -0.98419 | -0.8606 | 0.25177 | 121.9757 | -1.0529 | 122.0123 | -0.76446 | -0.83771 | -0.74158 | -0.082397 | 0 | -0.2243 | 0.47607 | 0.1236 | 0 | 0.20599 | 0.082397 | -0.068664 | -0.009155 | 0.027466 | 0.21973 | 0.24261 | 0.14648 | 0.31128 | 0.21515 | 0.55847 | 122.8271 | 0.28839 | 123.0652 | 123.0515 | 123.0286 | 122.9691 | 122.9599 | -123.0515 | -123.0377 | 122.7448 | 122.9965 | 8.0475 | 1.236
319.1719 | 123.0698 | -1.181 | 121.8567 | -0.023041 | -0.00049134 | 0.038217 | 0.00017729 | 0.0022346 | -0.0012946 | -0.0018052 | -0.050171 | 0.0017816 | -7.2674e-05 | 0.00017297 | -0.00027553 | -0.0018393 | 0.0011877 | 5.5161 | 121.8201 | -1.2543 | 121.5363 | -0.70496 | -1.1765 | -1.0986 | 0.27466 | 121.8613 | -1.2589 | 121.788 | -0.99792 | -1.0849 | -1.0162 | -0.073242 | -0.036621 | -0.32043 | 0.47607 | 0.082397 | 0.004577 | 0.15564 | 0.077819 | -0.07782 | 0.004578 | -0.068664 | 0.18311 | 0.1648 | 0.09613 | 0.24262 | 0.17395 | 0.54932 | 122.7905 | 0.26093 | 123.0469 | 123.0743 | 123.1201 | 123.0011 | 123.0423 | -123.111 | -123.1155 | 122.7173 | 122.9691 | 6.6971 | 1.4557
320.9062 | 123.1613 | -1.3138 | 121.6736 | -0.023041 | -0.0015595 | 0.036081 | -0.00046351 | -0.00075622 | 0.001269 | 0.0013992 | 0.096314 | 0.00092703 | 0.00035453 | 0.0014548 | 0.0010061 | -0.0026939 | 0.00054686 | 4.6509 | 121.6415 | -1.355 | 121.4447 | -0.71869 | -1.2405 | -1.149 | 0.25635 | 121.6599 | -1.3779 | 121.6873 | -1.03 | -1.0986 | -1.0483 | -0.041198 | -0.032043 | -0.22888 | 0.59509 | 0.1648 | 0.073242 | 0.20599 | 0.11444 | -0.064087 | -0.013733 | 0.013733 | 0.28381 | 0.2655 | 0.21515 | 0.32959 | 0.27924 | 0.63629 | 122.7997 | 0.3479 | 123.0652 | 122.9965 | 123.0377 | 122.9553 | 122.9736 | -123.0286 | -123.0515 | 122.7585 | 123.0011 | 5.9647 | 1.5701
322.6406 | 123.0286 | -1.5335 | 121.5179 | 0.037994 | 0.00036326 | 0.039072 | 0.0042361 | -0.0028924 | 0.00041439 | 0.0011856 | -0.034912 | 0.00092703 | 0.0029181 | -0.0017496 | 0.0027151 | -0.0018393 | -0.0041527 | 3.3005 | 121.5042 | -1.6251 | 121.1472 | -1.0803 | -1.5976 | -1.4923 | 0.13275 | 121.5134 | -1.5976 | 121.3852 | -1.3962 | -1.474 | -1.3687 | -0.091553 | -0.013733 | -0.37079 | 0.45319 | 0.041198 | -0.064087 | 0.13275 | 0.027466 | -0.064087 | -0.004577 | -0.13275 | 0.13733 | 0.1648 | 0.059509 | 0.22888 | 0.1236 | 0.54474 | 122.7722 | 0.20142 | 122.9828 | 123.1293 | 123.111 | 123.0377 | 123.0469 | -123.143 | -123.1155 | 122.6807 | 122.9187 | 4.834 | 1.6663
324.3125 | 123.0652 | -2.8702 | 120.1584 | 0.0074768 | 0.0022859 | 0.037149 | 0.0010319 | 0.00138 | 0.0016962 | -0.0020188 | -0.037964 | 0.003277 | 0.00078193 | 0.0012412 | -0.0039071 | -0.0035483 | -0.0011621 | 1.8265 | 120.1447 | -2.9617 | 119.7968 | -1.9867 | -2.948 | -2.8336 | 0.10986 | 120.1538 | -2.9388 | 120.0485 | -2.7374 | -2.829 | -2.7054 | -0.091553 | -0.013733 | -0.36163 | 0.88348 | 0.036621 | -0.07782 | 0.12817 | 0.013733 | -0.068665 | -0.004577 | -0.10986 | 0.13275 | 0.1648 | 0.041199 | 0.23346 | 0.10986 | 0.97504 | 122.7585 | 0.20142 | 122.9874 | 123.1064 | 123.0927 | 123.0148 | 123.024 | -123.1201 | -123.0972 | 122.6669 | 122.9187 | 4.6967 | 2.98
326.0469 | 123.0743 | -3.2135 | 119.7922 | -0.068817 | 0.0018585 | 0.037149 | 0.0031681 | 0.0018072 | 0.0016962 | -0.00095055 | -0.03186 | 0.00071343 | -7.2674e-05 | -0.0028176 | 0.0020743 | -0.0048301 | 0.00033326 | 0.71869 | 119.7922 | -3.2867 | 119.4443 | -2.179 | -3.2822 | -3.1815 | 0.14648 | 119.7876 | -3.3005 | 119.7189 | -3.0487 | -3.1494 | -3.0258 | -0.073242 | 0 | -0.3479 | 1.0345 | 0.032043 | -0.068665 | 0.10528 | 0.004577 | -0.086975 | -0.004577 | -0.073242 | 0.16479 | 0.18768 | 0.064087 | 0.27466 | 0.15106 | 1.1078 | 122.731 | 0.25177 | 123.0194 | 123.0789 | 123.0881 | 123.0057 | 123.0011 | -123.0789 | -123.0927 | 122.6578 | 122.9324 | 3.9322 | 3.36
327.7188 | 123.024 | -6.3766 | 116.6382 | 0.030365 | 0.0010041 | 0.034799 | 0.0029545 | 0.0020208 | 0.0021234 | -0.0018052 | -0.059326 | 0.001568 | -0.00071347 | 0.00060037 | -0.00027553 | -0.0024803 | 0.0024695 | -3.7033 | 116.6107 | -6.4865 | 116.2628 | -4.422 | -6.5048 | -6.427 | 0.091553 | 116.6336 | -6.4499 | 116.5054 | -6.2988 | -6.3858 | -6.2759 | -0.10986 | -0.027466 | -0.37537 | 1.9547 | -0.050354 | -0.12817 | 0.059509 | -0.018311 | -0.073242 | -0.004578 | -0.13275 | 0.07782 | 0.10071 | -0.009155 | 0.17395 | 0.064087 | 2.0645 | 122.7493 | 0.15106 | 122.9553 | 123.0972 | 123.0835 | 122.9874 | 123.0103 | -123.1247 | -123.0881 | 122.6395 | 122.8821 | 2.6733 | 6.4682
329.4688 | 123.0286 | -4.8981 | 118.1259 | 0.015106 | 0.0012177 | 0.036295 | 0.0020999 | -0.00075622 | 0.0016962 | 0.00075845 | -0.044067 | 0.0013544 | 0.0018499 | 0.0067954 | 0.0018607 | -0.0024803 | -0.00094854 | -2.0599 | 118.1076 | -4.953 | 117.7826 | -3.4287 | -4.9805 | -4.8798 | 0.12817 | 118.1259 | -4.9667 | 118.0206 | -4.7791 | -4.8752 | -4.7562 | -0.054932 | -0.018311 | -0.34332 | 1.4694 | 0.01831 | -0.082398 | 0.073242 | -0.027466 | -0.068665 | 0 | -0.10529 | 0.11902 | 0.14191 | 0.022888 | 0.21057 | 0.091553 | 1.5244 | 122.7356 | 0.18768 | 122.9874 | 123.0606 | 123.0927 | 123.0057 | 123.024 | -123.0789 | -123.0927 | 122.6807 | 122.9187 | 2.8381 | 5.0262
331.1406 | 123.1567 | -4.8981 | 118.0527 | 0.015106 | 0.0029267 | 0.037149 | 0.0027407 | 0.0037298 | -1.2808e-05 | 0.0016128 | 0.001709 | -0.0012092 | 0.0029181 | -4.063e-05 | 0.00079247 | -0.0022665 | -0.0024439 | -4.8706 | 118.0298 | -4.9805 | 117.8421 | -3.2684 | -4.921 | -4.8157 | 0.21515 | 118.0161 | -4.9713 | 118.0756 | -4.6829 | -4.7653 | -4.6738 | -0.082398 | -0.022888 | -0.21057 | 1.6296 | 0.082397 | -0.022888 | 0.1648 | 0.05951 | -0.073242 | -0.036621 | 0.022889 | 0.21515 | 0.2243 | 0.13275 | 0.29755 | 0.20599 | 1.712 | 122.8226 | 0.28839 | 123.0469 | 123.0103 | 122.9874 | 122.9279 | 122.9141 | -123.0331 | -123.024 | 122.7402 | 122.9736 | 0.027466 | 5.1132
332.875 | 123.0789 | -4.3259 | 118.6981 | 0.022736 | -0.00070494 | 0.037576 | 0.0035953 | 0.0037298 | -0.00065361 | -9.6154e-05 | -0.019653 | 0.0013544 | 0.00056833 | -0.004313 | 0.00057887 | -0.0011985 | 0.0011877 | -4.2847 | 118.6981 | -4.3854 | 118.3777 | -3.0716 | -4.3396 | -4.2709 | 0.21515 | 118.7164 | -4.3762 | 118.602 | -4.1336 | -4.2252 | -4.1428 | -0.059509 | 0 | -0.32043 | 1.2543 | 0.054932 | -0.013733 | 0.11444 | 0.045776 | -0.050354 | 0.018311 | -0.09613 | 0.19226 | 0.18311 | 0.10071 | 0.23346 | 0.15106 | 1.3138 | 122.7631 | 0.24261 | 122.9782 | 123.0835 | 123.0927 | 123.024 | 123.0423 | -123.0835 | -123.0743 | 122.7036 | 122.9279 | 0.041199 | 4.541
334.625 | 123.1476 | -6.2256 | 116.7252 | 0.030365 | -0.00049134 | 0.038644 | 0.00039089 | -0.0024652 | 0.00062799 | -0.00073695 | 0.062744 | 0.00049983 | 0.00035453 | 0.00038657 | -6.1934e-05 | -0.0041891 | 0.0026831 | -6.221 | 116.6931 | -6.2805 | 116.5283 | -3.4287 | -6.1615 | -6.102 | 0.27008 | 116.6977 | -6.2805 | 116.7068 | -6.0059 | -6.0837 | -6.0333 | -0.054932 | -0.032044 | -0.19684 | 2.7969 | 0.1236 | 0.064087 | 0.17853 | 0.11902 | -0.054932 | -0.027466 | -0.018311 | 0.21973 | 0.19226 | 0.14191 | 0.24719 | 0.19684 | 2.8519 | 122.8088 | 0.27466 | 122.9874 | 122.9736 | 122.9782 | 122.9187 | 122.9233 | -123.0057 | -123.0057 | 122.7539 | 122.9324 | 0.004578 | 6.4957
336.2969 | 123.111 | -6.0654 | 116.8625 | -0.015411 | -6.4144e-05 | 0.036081 | -0.00046351 | -0.00011542 | 0.0021234 | 0.0016128 | 0.071899 | 0.00028623 | 0.00099553 | -0.0064492 | 0.0012199 | -0.0024803 | -0.00052114 | -6.1111 | 116.9083 | -6.1111 | 116.6016 | -4.1061 | -6.1203 | -5.9921 | 0.07782 | 116.8716 | -6.1295 | 116.8304 | -5.9143 | -6.0013 | -5.9418 | -0.045776 | 0.045776 | -0.26093 | 1.9592 | 0.073243 | -0.054931 | 0.11902 | -0.009155 | -0.064087 | 0.009155 | -0.032044 | 0.15106 | 0.1236 | 0.064087 | 0.18768 | 0.12817 | 2.005 | 122.7127 | 0.21515 | 122.9599 | 123.0194 | 123.0011 | 122.9736 | 122.937 | -122.9736 | -122.9919 | 122.6669 | 122.8958 | -0.045776 | 6.1432
338.0312 | 123.0743 | -8.2581 | 114.7293 | 0.037994 | 0.0020721 | 0.041208 | 0.0087223 | 9.818e-05 | 0.0010554 | 0.0018264 | -0.053223 | 0.00092703 | 0.0012091 | -0.0021768 | -0.00091653 | -0.0018393 | -0.0030847 | -8.2947 | 114.7064 | -8.3679 | 114.4272 | -4.985 | -8.3267 | -8.2306 | 0.24719 | 114.7339 | -8.3221 | 114.6698 | -8.1436 | -8.226 | -8.1482 | -0.10986 | -0.022888 | -0.30212 | 3.273 | 0.027466 | -0.068664 | 0.13733 | 0.041199 | -0.064087 | 0.004578 | -0.059509 | 0.11444 | 0.10986 | 0.032044 | 0.17395 | 0.096131 | 3.3829 | 122.7951 | 0.17853 | 122.9919 | 123.0743 | 123.056 | 122.9645 | 122.9919 | -123.0972 | -123.0515 | 122.6852 | 122.9279 | -0.036621 | 8.5052
339.7188 | 123.1567 | -5.3787 | 117.6041 | -0.0077822 | 0.0022859 | 0.043558 | 0.0080813 | 0.00073918 | 0.0016962 | 0.00097205 | -0.0043944 | -0.00014097 | 0.0044135 | -0.0013224 | -6.1934e-05 | -0.0011985 | 0.00076046 | -5.3558 | 117.5537 | -5.452 | 117.3706 | -2.9984 | -5.3604 | -5.2048 | 0.2243 | 117.5629 | -5.4382 | 117.5949 | -5.1636 | -5.246 | -5.1453 | -0.073242 | -0.050354 | -0.23346 | 2.3804 | 0.17395 | 0.01831 | 0.24719 | 0.091552 | -0.059509 | -0.041199 | -0.009155 | 0.21515 | 0.23346 | 0.13275 | 0.29297 | 0.19226 | 2.4536 | 122.8226 | 0.27466 | 123.0331 | 123.0057 | 123.0011 | 122.9324 | 122.9416 | -123.056 | -123.0423 | 122.7493 | 122.9736 | 0.022888 | 5.603
341.4531 | 123.0286 | -6.8253 | 116.1942 | 0.076141 | 0.0014313 | 0.037149 | 0.0023135 | 0.00073918 | -0.00044001 | 0.0018264 | 0.0078126 | -0.00078177 | -0.0013543 | -4.063e-05 | 0.00015167 | -0.0014121 | -9.3938e-05 | -6.8665 | 116.1804 | -6.8939 | 115.8371 | -4.5502 | -6.8207 | -6.7612 | 0.14191 | 116.2033 | -6.871 | 116.0522 | -6.7017 | -6.7841 | -6.6971 | -0.068665 | -0.013733 | -0.35706 | 2.2751 | 0.064087 | 0.004577 | 0.13275 | 0.073242 | -0.045777 | 0.009155 | -0.14191 | 0.1236 | 0.12817 | 0.041198 | 0.17395 | 0.086975 | 2.3438 | 122.731 | 0.16937 | 122.9233 | 123.0743 | 123.0743 | 123.0057 | 123.0286 | -123.0881 | -123.0652 | 122.6624 | 122.8775 | -0.041199 | 6.9672
343.1875 | 122.9187 | -55.394 | 67.4515 | -0.19089 | -0.00049134 | 0.02305 | 0.016626 | -0.0016106 | 0.0010554 | 0.00204 | -0.047119 | 0.00028623 | 0.00035453 | 0.0012412 | -0.00048913 | -0.0011985 | 0.0024695 | -0.14191 | 0.60883 | -0.15106 | 0.23804 | -0.086975 | -0.19226 | -0.068665 | -0.3479 | 67.4469 | -55.4581 | 67.4103 | -55.394 | -55.4993 | -55.2475 | 55.2429 | -66.8427 | -67.2134 | 55.307 | 55.3253 | 55.2017 | 0.082397 | -0.041199 | -0.064087 | -0.004578 | -0.041199 | 0 | 0.14648 | -0.10529 | 0.21057 | -0.041199 | 0.064087 | 0.3891 | 0.064087 | 122.8683 | 0.75989 | 122.905 | 56.0028 | 122.8409 | -67.6025 | -122.9095 | 55.632 | 122.8043 | 55.2521 | 55.0461
344.9375 | 122.9462 | -55.5679 | 67.3096 | -0.17563 | 0.0020721 | 0.020486 | 0.018122 | 0.0039436 | 0.0014826 | -0.0030868 | -0.056274 | 0.0028498 | -0.00092707 | 0.0042318 | 0.00057887 | -0.0026939 | 0.0018287 | -0.16937 | 0.36621 | -0.13275 | 0.013733 | -0.091553 | -0.21515 | -0.07782 | -0.21973 | 67.2913 | -55.6091 | 67.2546 | -55.5862 | -55.6961 | -55.4306 | 55.4352 | -66.9434 | -67.2958 | 55.4764 | 55.4901 | 55.3528 | 0.054931 | -0.082398 | -0.041199 | -0.01831 | -0.054931 | -0.018311 | 0.13733 | -0.12817 | 0.17853 | -0.086975 | 0.041198 | 0.14648 | 0.022888 | 122.8638 | 0.49896 | 122.9004 | 55.9341 | 122.8592 | -67.4423 | -122.9187 | 55.5817 | 122.8226 | 55.3986 | 55.3482
346.6719 | 123.024 | -55.2109 | 67.6117 | -0.20615 | -0.0019867 | 0.018991 | 0.017053 | 0.00052558 | -0.00022641 | 0.0013992 | -0.047119 | -0.00014097 | -0.00071347 | -0.0021768 | -0.0013437 | -0.0011985 | -0.0028711 | -0.11444 | 0.32044 | -0.14191 | 0.045776 | 0.032043 | -0.10986 | 0.004578 | -0.045776 | 67.6209 | -55.2795 | 67.662 | -55.188 | -55.307 | -55.0552 | 55.069 | -67.2913 | -67.5659 | 55.2429 | 55.2155 | 55.101 | 0.14649 | 0.032044 | -0.068665 | 0.009156 | 0.050354 | 0.022888 | 0.15564 | -0.096131 | 0.2243 | -0.027466 | 0.17395 | 0.18768 | 0.091553 | 122.9416 | 0.46234 | 122.9004 | 55.5313 | 122.8317 | -67.7536 | -122.8912 | 55.2567 | 122.8729 | 55.0964 | 55.1651
348.4062 | 123.1018 | -55.9845 | 66.7969 | -0.13748 | -0.0011321 | 0.018991 | 0.019617 | -0.00011542 | 0.0010554 | 0.0031082 | 0.0047608 | -0.00099557 | 0.00078193 | 0.0044456 | 0.00057887 | -0.0020529 | 0.0024695 | -0.11444 | 0.16479 | -0.13275 | -0.064087 | 0.045776 | -0.07782 | 0.036621 | -0.050354 | 66.7786 | -56.0532 | 66.9022 | -55.9204 | -56.0257 | -55.751 | 55.8517 | -66.6321 | -66.861 | 56.0303 | 56.0211 | 55.9067 | 0.16937 | 0.054931 | -0.068665 | -0.018311 | 0.10529 | 0.064087 | 0.23346 | -0.041199 | 0.30212 | 0.027466 | 0.17853 | 0.068664 | 0.13275 | 122.9553 | 0.29755 | 122.8317 | 56.1493 | 122.7631 | -66.9296 | -122.85 | 55.9204 | 122.8867 | 55.8701 | 55.9341
350.1406 | 122.9782 | -56.5201 | 66.362 | -0.16037 | -0.0024139 | 0.016641 | 0.015558 | 0.0039436 | -0.00022641 | -0.0026596 | 0.023071 | 0.0017816 | 0.00099553 | 0.0033774 | 0.0012199 | -0.0029075 | 0.0048193 | -0.17395 | 0.30212 | -0.14648 | -0.050354 | -0.036621 | -0.13733 | -0.059509 | -0.068665 | 66.3712 | -56.5704 | 66.275 | -56.5155 | -56.6162 | -56.3965 | 56.3736 | -66.0599 | -66.4124 | 56.4835 | 56.4606 | 56.3828 | 0.086975 | 0.009155 | -0.050354 | 0.009155 | -0.086976 | 0.004578 | 0.1236 | -0.09613 | 0.17395 | -0.045776 | 0.10986 | 0.09613 | 0.054932 | 122.8455 | 0.44861 | 122.9416 | 56.8222 | 122.8912 | -66.5085 | -122.9324 | 56.4697 | 122.7951 | 56.3461 | 56.4514
351.8125 | 123.024 | -55.2063 | 67.6575 | -0.11459 | -0.00070494 | 0.020486 | 0.016626 | -0.00054262 | -0.00065361 | 0.00033105 | -0.0013428 | 0.00071343 | 0.0012091 | -0.00089503 | 0.0016471 | -0.0022665 | 0.0028967 | -0.13733 | 0.27924 | -0.13733 | -0.059509 | -0.036621 | -0.13733 | -0.041199 | -0.036621 | 67.6712 | -55.2429 | 67.6117 | -55.188 | -55.2795 | -55.0598 | 55.069 | -67.3782 | -67.717 | 55.1697 | 55.1651 | 55.069 | 0.09613 | 0 | -0.036621 | 0.013733 | -0.045777 | 0.018311 | 0.14648 | -0.073242 | 0.18311 | -0.036621 | 0.10071 | 0.07782 | 0.054932 | 122.8546 | 0.41656 | 122.9141 | 55.4855 | 122.8775 | -67.7948 | -122.9004 | 55.1468 | 122.818 | 55.069 | 55.1697
353.5469 | 123.1064 | -54.6204 | 68.2068 | -0.18326 | -0.0026275 | 0.019205 | 0.014917 | -0.001397 | 0.0010554 | 0.00033105 | 0.099365 | 7.2626e-05 | 0.0018499 | -0.0068766 | 0.0018607 | -0.0011985 | 0.0024695 | -0.12817 | 0.17853 | -0.11444 | -0.022888 | 0.064087 | -0.068665 | 0.050354 | -0.022888 | 68.2068 | -54.6799 | 68.2663 | -54.5334 | -54.6249 | -54.4052 | 54.5059 | -68.0283 | -68.2297 | 54.6844 | 54.6707 | 54.5517 | 0.16479 | 0.045776 | -0.05951 | 0 | 0.059509 | 0.086975 | 0.21515 | -0.004578 | 0.27466 | 0.054932 | 0.17853 | 0.091553 | 0.14648 | 122.9462 | 0.29297 | 122.8867 | 54.7989 | 122.8271 | -68.3212 | -122.8867 | 54.5975 | 122.8867 | 54.4922 | 54.5975
355.2188 | 123.1201 | -52.9861 | 69.8273 | -0.18326 | -0.0024139 | 0.019846 | 0.01449 | 0.00052558 | 0.0016962 | 0.0016128 | 0.081055 | -0.00185 | 0.00014093 | 0.0048728 | -0.0021981 | -0.0039755 | -9.3938e-05 | -0.086975 | 0.1236 | -0.10529 | -0.013733 | 0.13733 | 0 | 0.10071 | 0.11902 | 69.8135 | -53.0319 | 69.8914 | -52.8854 | -52.9816 | -52.7756 | 52.8809 | -69.7037 | -69.841 | 53.1235 | 53.0869 | 52.9861 | 0.20599 | 0.10529 | -0.045776 | -0.013733 | 0.064086 | 0.10071 | 0.21057 | 0.004578 | 0.25635 | 0.050354 | 0.24262 | 0.091553 | 0.14648 | 122.9233 | 0.22888 | 122.8455 | 53.1097 | 122.7997 | -69.9326 | -122.8592 | 52.9724 | 122.8775 | 52.8992 | 53.1052
356.9531 | 123.0652 | -51.3931 | 71.4294 | -0.168 | -0.0024139 | 0.017496 | 0.015558 | -0.002038 | 0.0014826 | 0.0011856 | 0.056641 | -0.0031318 | 0.0014227 | -0.00089503 | 0.0010061 | -0.0035483 | 0.00011966 | -0.13275 | 0.1236 | -0.13275 | -0.082397 | 0.004578 | -0.091553 | 0.041199 | -0.032043 | 71.4249 | -51.4297 | 71.4249 | -51.3977 | -51.4709 | -51.2421 | 51.2604 | -71.3058 | -71.5118 | 51.3977 | 51.4343 | 51.3016 | 0.17395 | 0.041198 | -0.036622 | -0.004577 | -0.004577 | -0.004578 | 0.15106 | -0.07782 | 0.18768 | -0.041198 | 0.13733 | 0.050354 | 0.032044 | 122.8546 | 0.25635 | 122.8546 | 51.5167 | 122.818 | -71.5622 | -122.8592 | 51.3107 | 122.818 | 51.2604 | 51.3611
358.6875 | 123.1064 | -48.4543 | 74.35 | -0.19852 | -0.00027774 | 0.019846 | 0.016199 | 0.0015936 | 0.00062799 | 0.0011856 | -0.034912 | -0.00078177 | 0.00056833 | -0.0017496 | -0.00070273 | -0.0014121 | 0.0014015 | -0.09613 | 0.13733 | -0.10529 | -0.068665 | 0.036621 | -0.09613 | 0.041199 | 0.13275 | 74.35 | -48.5046 | 74.4324 | -48.436 | -48.5458 | -48.2895 | 48.349 | -74.2126 | -74.4186 | 48.4909 | 48.4955 | 48.3582 | 0.14649 | 0.009156 | -0.050354 | 0 | 0.082397 | 0.018311 | 0.16479 | -0.091552 | 0.21515 | -0.041198 | 0.14191 | 0.036621 | 0.068665 | 122.937 | 0.24262 | 122.8546 | 48.5916 | 122.8043 | -74.4553 | -122.8546 | 48.3856 | 122.8867 | 48.3582 | 48.587
360.3594 | 122.9782 | -47.9233 | 74.9954 | -0.19852 | 0.00036326 | 0.0207 | 0.019617 | 0.00095278 | 0.001269 | 0.0011856 | -0.06543 | 0.00071343 | 0.00014093 | 0.0063682 | -0.0013437 | -0.0026939 | -0.0026575 | -0.16479 | 0.15106 | -0.13733 | -0.14648 | -0.086975 | -0.19684 | -0.054932 | -0.041199 | 74.9725 | -47.9462 | 74.913 | -47.9965 | -48.0972 | -47.8409 | 47.7859 | -74.8444 | -75.1419 | 47.8363 | 47.8683 | 47.7264 | 0.082397 | -0.059509 | -0.022888 | -0.022888 | -0.082397 | -0.073242 | 0.082398 | -0.17395 | 0.10529 | -0.15106 | 0.050354 | -0.009155 | -0.050354 | 122.8592 | 0.28839 | 122.9187 | 48.0743 | 122.8958 | -75.1328 | -122.9416 | 47.7768 | 122.8363 | 47.7585 | 47.8821
362.0938 | 122.9965 | -44.7372 | 78.1448 | -0.17563 | -0.0015595 | 0.019205 | 0.017267 | -0.0046014 | -0.001081 | 0.0011856 | -0.053223 | 0.00071343 | 0.0022773 | 0.0014548 | -6.1934e-05 | -0.0020529 | -0.00052114 | -0.11444 | 0.14648 | -0.14191 | -0.10071 | 0.013733 | -0.14191 | -0.018311 | 0.11444 | 78.1815 | -44.7647 | 78.1128 | -44.7647 | -44.8975 | -44.6457 | 44.5953 | -77.9984 | -78.2455 | 44.751 | 44.7189 | 44.5953 | 0.1236 | 0 | -0.027465 | 0.036622 | -0.032043 | -0.027465 | 0.091553 | -0.16022 | 0.11902 | -0.13275 | 0.15564 | 0.041199 | 0 | 122.8775 | 0.28839 | 122.9462 | 44.8837 | 122.9187 | -78.2867 | -122.9095 | 44.6365 | 122.85 | 44.6228 | 44.8517
363.8281 | 123.0743 | -39.4501 | 83.4412 | -0.15274 | -0.0024139 | 0.019846 | 0.014276 | 0.00073918 | 0.0021234 | 0.0016128 | 0.044434 | -0.0014228 | 0.0018499 | 0.0010276 | -0.00091653 | -0.0011985 | -0.0028711 | -0.086975 | 0.10986 | -0.1236 | -0.032043 | 0.11444 | -0.032043 | 0.068665 | 1.4099 | 83.2535 | -39.5874 | 83.4 | -39.4592 | -39.5782 | -39.3448 | 39.3265 | -83.3313 | -83.4732 | 39.5645 | 39.5187 | 39.418 | 0.19226 | 0.091553 | -0.13733 | -0.18768 | -0.041199 | -0.009156 | 0.10529 | -0.12817 | 0.24261 | 0.009155 | 0.23804 | 0.091553 | 0.12817 | 122.9874 | 0.23346 | 122.8409 | 39.5599 | 122.7036 | -83.5648 | -123.0286 | 39.418 | 122.85 | 39.3631 | 40.86
365.5781 | 123.111 | -37.8387 | 85.0067 | -0.14511 | -0.0034821 | 0.018777 | 0.013208 | 9.818e-05 | 0.00041439 | 0.00075845 | 0.068848 | 7.2626e-05 | 0.00014093 | -0.0019632 | 0.00015167 | -0.0037619 | -0.0026575 | -0.13733 | 0.14191 | -0.11444 | -0.064087 | 0.073242 | -0.050354 | 0.073242 | 0.27008 | 84.9289 | -37.9715 | 85.0296 | -37.8387 | -37.9074 | -37.7151 | 37.7243 | -84.8648 | -85.0708 | 37.912 | 37.912 | 37.7884 | 0.18768 | 0.064087 | -0.13275 | -0.07782 | 0.022888 | 0 | 0.1236 | -0.068665 | 0.25635 | 0.064087 | 0.18768 | 0.050354 | 0.13275 | 123.0011 | 0.25635 | 122.9004 | 37.9807 | 122.7676 | -85.1212 | -122.9782 | 37.7747 | 122.8683 | 37.7014 | 38.1088
367.25 | 123.0606 | -36.8134 | 86.0229 | -0.12985 | -0.0017731 | 0.019205 | 0.013208 | -0.003747 | 0.00062799 | 0.00054465 | 0.047485 | 0.00071343 | 0.00035453 | -0.0051676 | -0.0028391 | -0.0033347 | -0.0030847 | -0.13275 | 0.11902 | -0.10529 | -0.082397 | 0.032043 | -0.10529 | 0.045776 | 0.032043 | 86.0229 | -36.8774 | 86.0092 | -36.8774 | -36.9507 | -36.7859 | 36.7081 | -85.9039 | -86.1053 | 36.8454 | 36.8591 | 36.7081 | 0.15106 | 0 | -0.064087 | 0 | -0.013733 | -0.064087 | 0.027465 | -0.13733 | 0.091552 | -0.073243 | 0.13733 | 0.022889 | 0 | 122.8867 | 0.22431 | 122.9004 | 36.9324 | 122.8363 | -86.1282 | -122.9004 | 36.731 | 122.8226 | 36.6806 | 36.8454
368.9844 | 123.0194 | -32.3181 | 90.596 | -0.16037 | 0.0010041 | 0.020486 | 0.020471 | 0.00031198 | 0.00041439 | 0.00033105 | -0.074585 | 0.00092703 | -0.0024225 | -0.0017496 | -0.0024117 | -0.00034387 | 0.00054686 | -0.086975 | 0.16479 | -0.13275 | -0.086975 | 0.022888 | -0.10986 | -0.013733 | 0.004578 | 90.5731 | -32.3547 | 90.5731 | -32.3639 | -32.4463 | -32.2998 | 32.1854 | -90.4312 | -90.683 | 32.341 | 32.3044 | 32.2083 | 0.11902 | 0.022888 | -0.036621 | -0.022888 | -0.022888 | -0.045777 | 0.01831 | -0.12817 | 0.054931 | -0.091553 | 0.15564 | 0.045776 | -0.009156 | 122.9279 | 0.29755 | 122.9279 | 32.4829 | 122.8912 | -90.7288 | -122.9507 | 32.2311 | 122.8912 | 32.2311 | 32.3227
370.7344 | 123.0469 | -26.976 | 95.929 | -0.12985 | -0.0039093 | 0.018991 | 0.013208 | -0.0011834 | 0.0036188 | 0.00054465 | 0.050537 | 0.00049983 | 0.0018499 | -0.0036722 | -6.1934e-05 | -0.0041891 | 0.00054686 | -0.10071 | 0.11444 | -0.11444 | -0.036621 | 0.09613 | -0.050354 | 0.07782 | 0.22888 | 95.9106 | -27.0081 | 95.8649 | -27.0035 | -27.0584 | -26.9257 | 26.8616 | -95.8145 | -95.9656 | 27.0721 | 27.0538 | 26.9257 | 0.19226 | 0.064087 | -0.032044 | -0.01831 | -0.064087 | -0.027466 | 0.050354 | -0.082398 | 0.082398 | -0.050354 | 0.21057 | 0.07782 | 0.004578 | 122.8729 | 0.22888 | 122.9187 | 27.0905 | 122.8867 | -96.0434 | -122.937 | 26.9394 | 122.8409 | 26.8753 | 27.2049
372.4062 | 123.1018 | -24.5636 | 98.2727 | -0.17563 | 0.00057686 | 0.0207 | 0.015985 | 0.0022346 | 0.00020079 | -9.6154e-05 | -0.019653 | -0.00014097 | 0.0014227 | -0.0075174 | -0.0011301 | -0.0016257 | 0.0014015 | -0.068665 | 0.11902 | -0.10986 | -0.022888 | 0.09613 | -0.064087 | 0.045776 | 0.21973 | 98.2635 | -24.614 | 98.3459 | -24.5682 | -24.6689 | -24.5316 | 24.4537 | -98.1537 | -98.2956 | 24.6597 | 24.6094 | 24.4995 | 0.15564 | 0.045776 | -0.050354 | -0.009155 | 0.073242 | -0.004577 | 0.032044 | -0.10528 | 0.082398 | -0.054931 | 0.20599 | 0.086975 | 0.045777 | 122.9599 | 0.22888 | 122.8775 | 24.6826 | 122.8271 | -98.3826 | -122.8867 | 24.5407 | 122.9095 | 24.4949 | 24.7833
374.1562 | 122.9874 | -23.8083 | 99.1516 | -0.19089 | 0.0010041 | 0.018564 | 0.016626 | 9.818e-05 | 0.00041439 | -0.0022324 | -0.071533 | 0.00049983 | 0.0016363 | 0.0029502 | 0.0012199 | -0.0031211 | -0.00052114 | -0.16022 | 0.16937 | -0.13275 | -0.14648 | -0.07782 | -0.20599 | -0.07782 | 0.064087 | 99.1425 | -23.8724 | 99.0143 | -23.9182 | -24.0143 | -23.8678 | 23.6755 | -98.9822 | -99.2981 | 23.7305 | 23.7305 | 23.6023 | 0.054931 | -0.073243 | -0.064086 | -0.009155 | -0.13733 | -0.10986 | -0.059509 | -0.20599 | 0.004577 | -0.14191 | 0.054931 | -0.013733 | -0.045777 | 122.8867 | 0.30212 | 123.0148 | 23.9777 | 122.9507 | -99.2844 | -123.024 | 23.6618 | 122.8226 | 23.6481 | 23.8724
375.8906 | 123.1201 | -26.976 | 95.8511 | -0.17563 | -0.00070494 | 0.020486 | 0.01684 | 0.0033026 | 0.0019098 | 0.00204 | -0.016602 | -0.0020636 | 0.00078193 | -0.003245 | 0.0010061 | -0.0014121 | 0.0016151 | -0.073242 | 0.11444 | -0.082397 | -0.013733 | 0.10529 | -0.064087 | 0.082397 | 0.17395 | 95.842 | -27.063 | 95.8969 | -27.0218 | -27.095 | -26.9623 | 26.8936 | -95.7367 | -95.8649 | 27.0813 | 27.0584 | 26.9119 | 0.16479 | 0.01831 | -0.086975 | -0.009155 | 0.045777 | -0.045777 | 0.013733 | -0.11902 | 0.10071 | -0.032044 | 0.18768 | 0.068664 | 0.041198 | 122.9599 | 0.19684 | 122.905 | 27.0905 | 122.818 | -95.9335 | -122.9141 | 26.9623 | 122.8729 | 26.9028 | 27.15
377.625 | 123.0148 | -25.0351 | 97.9019 | -0.068817 | -0.0013457 | 0.017496 | 0.016626 | 0.0022346 | 0.00062799 | 0.00033105 | -0.037964 | -0.00056817 | 0.00056833 | 0.00038657 | -0.0019845 | -0.0029075 | -0.0030847 | -0.13733 | 0.15106 | -0.16479 | -0.10986 | -0.009155 | -0.12817 | -0.022888 | 0.2243 | 97.9019 | -25.0671 | 97.8424 | -25.0854 | -25.1724 | -25.0671 | 24.8703 | -97.7509 | -98.0118 | 25.0259 | 25.0122 | 24.9069 | 0.14191 | 0.036621 | -0.032044 | 0 | -0.05951 | -0.050354 | -0.032044 | -0.13733 | 0 | -0.10528 | 0.15564 | 0.054932 | -0.01831 | 122.9095 | 0.31586 | 122.9691 | 25.1862 | 122.937 | -98.0667 | -122.9691 | 24.9252 | 122.8775 | 24.8978 | 25.2594
379.2969 | 122.9919 | -22.9019 | 100.0534 | -0.17563 | -0.0017731 | 0.020914 | 0.017481 | 0.00095278 | 0.0016962 | 0.00097205 | -0.077637 | 0.00028623 | 0.0018499 | 0.001882 | -0.00027553 | -0.0033347 | 0.0022559 | -0.16937 | 0.15106 | -0.14191 | -0.15106 | -0.082397 | -0.21057 | -0.07782 | 0.07782 | 99.9985 | -22.998 | 99.8978 | -23.0484 | -23.1354 | -22.9752 | 22.76 | -99.9023 | -100.2045 | 22.8195 | 22.8241 | 22.6913 | 0.064087 | -0.068664 | -0.09613 | -0.054932 | -0.15564 | -0.14648 | -0.073242 | -0.23346 | 0.022888 | -0.13733 | 0.05951 | -0.009155 | -0.050354 | 122.8958 | 0.29297 | 122.9965 | 23.053 | 122.9004 | -100.1953 | -123.0515 | 22.7509 | 122.7997 | 22.7325 | 22.9797
381.0312 | 123.0698 | -21.08 | 101.8204 | -0.21378 | -0.0026275 | 0.020273 | 0.016199 | -0.0035334 | 0.0010554 | 0.0028946 | 0.053589 | -0.0016364 | 0.0041999 | -0.010081 | 0.00057887 | -0.0033347 | 0.00076046 | -0.14648 | 0.12817 | -0.13733 | -0.10071 | 0.036621 | -0.091553 | 0.041199 | 0.091553 | 101.8433 | -21.0983 | 101.77 | -21.0938 | -21.1761 | -21.0983 | 20.9427 | -101.6922 | -101.9211 | 21.1166 | 21.1212 | 20.9885 | 0.17853 | 0.045776 | -0.018311 | 0.022888 | -0.050354 | -0.013733 | -0.018311 | -0.09613 | 0 | -0.077819 | 0.17395 | 0.036621 | 0.004578 | 122.8683 | 0.2655 | 122.9416 | 21.2082 | 122.9233 | -101.9577 | -122.9187 | 20.9793 | 122.85 | 20.9335 | 21.1716
382.7031 | 123.0606 | -18.6859 | 104.2419 | -0.15274 | -0.0028411 | 0.016855 | 0.016626 | 0.00095278 | 0.0038324 | 0.0013992 | 0.044434 | -0.00056817 | 0.00078193 | -0.0017496 | -0.00070273 | -0.0048301 | -0.0011621 | -0.13275 | 0.11902 | -0.10986 | -0.073242 | 0.054932 | -0.086975 | 0.032043 | 0.1236 | 104.1962 | -18.7454 | 104.1962 | -18.6996 | -18.7683 | -18.6768 | 18.576 | -104.1229 | -104.3152 | 18.7408 | 18.718 | 18.5989 | 0.14191 | 0.022888 | -0.059509 | -0.045776 | -0.045776 | -0.013733 | 0.009155 | -0.082398 | 0.068664 | -0.022889 | 0.16479 | 0.036621 | 0.045776 | 122.9416 | 0.22888 | 122.9416 | 18.8049 | 122.8821 | -104.3518 | -122.9874 | 18.6127 | 122.8821 | 18.5532 | 18.8095
384.4375 | 123.0972 | -17.1066 | 105.8121 | -0.21378 | 0.0014313 | 0.020273 | 0.015344 | -0.00011542 | 0.0027644 | 0.00054465 | -0.047119 | 0.00071343 | -0.00028627 | 0.0020956 | -0.00070273 | -0.0031211 | -0.0018029 | -0.1236 | 0.1236 | -0.1236 | -0.073242 | 0.032043 | -0.11444 | 0.018311 | 0.2243 | 105.8029 | -17.1432 | 105.7938 | -17.0975 | -17.1844 | -17.0334 | 16.983 | -105.6885 | -105.8853 | 17.1387 | 17.1249 | 16.9922 | 0.14191 | 0.009155 | -0.036622 | -0.009156 | -0.018311 | 0.009155 | 0.073242 | -0.07782 | 0.10986 | -0.041198 | 0.15564 | 0.050354 | 0.045777 | 122.937 | 0.24719 | 122.9462 | 17.2302 | 122.9095 | -105.9357 | -122.9553 | 17.0334 | 122.9004 | 16.983 | 17.3309
386.1094 | 128.1097 | -15.239 | 107.6843 | -0.15274 | -0.00091854 | 0.019205 | 0.017694 | -0.00075622 | -1.2808e-05 | 0.0018264 | -0.071533 | 0.00049983 | 0.0035589 | -0.0017496 | -0.00070273 | -0.0018393 | -0.00073494 | 6.5598 | 0.14191 | -0.14191 | 1.7715 | 1.6525 | -0.25177 | 0.54474 | 0.13275 | 107.6843 | -15.3168 | 107.3273 | -14.4882 | -11.9385 | -15.3076 | 15.097 | -107.5424 | -105.9128 | 16.8915 | 15.7837 | 14.9872 | 0.68665 | -0.10986 | -0.077819 | 0 | -0.35706 | 0.75073 | -0.068664 | 3.3005 | 0.009155 | 3.3783 | 1.7944 | 1.9135 | 0.82855 | 122.644 | 0.28381 | 123.0011 | 15.3809 | 122.9233 | -107.8262 | -123.0011 | 17.0105 | 122.5662 | 21.7987 | 15.3717
387.8438 | 123.1293 | -14.1678 | 108.7143 | -0.16037 | -0.0028411 | 0.018991 | 0.015131 | -0.0046014 | 0.002337 | 0.0022536 | 0.062744 | -0.00035457 | 0.00035453 | -0.0028176 | -0.00027553 | -0.0046165 | -0.00030754 | -0.091553 | 0.10986 | -0.1236 | -0.009155 | 0.13275 | -0.013733 | 0.10986 | 0.29297 | 108.696 | -14.2227 | 108.7418 | -14.0442 | -14.1312 | -14.0717 | 14.0442 | -108.6044 | -108.7234 | 14.3005 | 14.2776 | 14.1541 | 0.23346 | 0.10986 | -0.054931 | -0.01831 | 0.027466 | 0.1236 | 0.096131 | 0.036621 | 0.15106 | 0.091552 | 0.25635 | 0.11444 | 0.17853 | 122.9645 | 0.23346 | 122.9187 | 14.2776 | 122.8638 | -108.8379 | -122.937 | 14.1586 | 122.9095 | 14.0762 | 14.4608
389.5938 | 123.0423 | -11.8652 | 111.0535 | -0.17563 | -0.0015595 | 0.017923 | 0.017694 | 0.0039436 | 0.0016962 | 0.00011745 | -0.028809 | 0.0019952 | 0.00099553 | -0.0021768 | -0.00048913 | -0.00098487 | -0.0035119 | -0.14648 | 0.15106 | -0.13275 | -0.12817 | -0.022888 | -0.16937 | -0.032043 | 0.1831 | 111.0901 | -11.911 | 111.0214 | -11.8332 | -11.9247 | -11.7874 | 11.7325 | -110.9024 | -111.1816 | 11.8423 | 11.8332 | 11.6959 | 0.10071 | -0.036622 | -0.045777 | 0.036621 | -0.032044 | 0.032043 | 0.077819 | -0.05951 | 0.1236 | -0.013733 | 0.10986 | 0.004577 | 0.07782 | 122.9324 | 0.28381 | 123.0011 | 12.0163 | 122.9553 | -111.1862 | -122.9645 | 11.7371 | 122.8867 | 11.7188 | 12.0483
391.2656 | 123.0148 | -10.9314 | 112.0468 | -0.16037 | -0.00070494 | 0.018991 | 0.018335 | 0.00052558 | 0.00020079 | 0.00204 | -0.025757 | 0.0017816 | -7.2674e-05 | 0.0012412 | -0.00070273 | -0.0041891 | 0.0033241 | -0.14191 | 0.14191 | -0.15106 | -0.15106 | -0.018311 | -0.16937 | -0.059509 | 0.12817 | 112.0789 | -11.0046 | 111.9415 | -10.8902 | -11.0001 | -10.8994 | 10.7803 | -111.9049 | -112.1979 | 10.9131 | 10.8719 | 10.762 | 0.091553 | -0.018311 | -0.073243 | 0.032043 | -0.10529 | 0.041198 | 0.032043 | -0.068665 | 0.10529 | 0.004578 | 0.13275 | 0 | 0.11444 | 122.9462 | 0.29297 | 123.0835 | 11.0733 | 123.0103 | -112.1979 | -123.0515 | 10.7803 | 122.8729 | 10.7895 | 11.0596
393 | 123.0743 | -9.3704 | 113.5391 | -0.15274 | -0.00091854 | 0.018991 | 0.013635 | -0.0028924 | 0.001269 | 0.00204 | 0.047485 | 7.2626e-05 | 0.0012091 | -0.0049538 | 0.00015167 | -0.0022665 | 0.0018287 | -0.16022 | 0.13275 | -0.11444 | -0.086975 | 0.036621 | -0.10529 | 0.032043 | 0.19684 | 113.5849 | -9.4116 | 113.4705 | -9.2468 | -9.3201 | -9.2651 | 9.256 | -113.4064 | -113.6261 | 9.407 | 9.4025 | 9.2651 | 0.14648 | 0.009155 | -0.041199 | 0.045776 | -0.068665 | 0.1236 | 0.10529 | 0.050354 | 0.14648 | 0.091553 | 0.15106 | 0.027466 | 0.16479 | 122.8821 | 0.24719 | 122.9965 | 9.5032 | 122.9553 | -113.6536 | -122.9507 | 9.2834 | 122.8409 | 9.2102 | 9.5673
394.7344 | 123.0469 | -8.5968 | 114.4089 | -0.14511 | -0.00027774 | 0.021341 | 0.01684 | 0.0024482 | 0.00084159 | 0.0033218 | -0.041016 | 0.001568 | 0.0018499 | -0.0017496 | 0.0014335 | -0.0014121 | 0.0026831 | -0.11902 | 0.14191 | -0.12817 | -0.09613 | 0.022888 | -0.11444 | -0.009155 | 0.13275 | 114.5599 | -8.4915 | 114.3173 | -8.4366 | -8.5464 | -8.4869 | 8.4686 | -114.267 | -114.505 | 8.6197 | 8.5876 | 8.4824 | 0.11902 | 0.013733 | 0.10529 | 0.15106 | -0.091553 | 0.16022 | 0.10986 | 0.050354 | 0.004578 | -0.054932 | 0.15106 | 0.032044 | 0.054932 | 122.8088 | 0.27008 | 123.0515 | 8.7387 | 123.1567 | -114.537 | -122.9004 | 8.5007 | 122.9141 | 8.4778 | 8.7296
396.4062 | 122.9874 | -4.7699 | 118.4784 | -0.10696 | -0.0032683 | 0.015573 | 0.013849 | 0.0018072 | -0.00086721 | -0.00030975 | 0.001709 | -0.0027044 | 0.0016363 | -0.001536 | 0.0020743 | -0.0024803 | -0.0013757 | -0.1831 | 0.14648 | -0.14191 | -0.16022 | -0.027466 | -0.15106 | -0.036621 | 0.25635 | 118.4738 | -4.6646 | 118.3228 | -4.3579 | -4.4449 | -4.4174 | 4.628 | -118.3319 | -118.6386 | 4.7424 | 4.7333 | 4.6188 | 0.10529 | -0.009155 | 0.10529 | -0.004578 | -0.15564 | 0.41199 | 0.35248 | 0.32501 | 0.24719 | 0.21973 | 0.11444 | -0.01831 | 0.3067 | 122.9874 | 0.28839 | 123.1384 | 4.9164 | 123.2437 | -118.6203 | -123.143 | 4.6097 | 123.0927 | 4.5868 | 5.0262
398.1406 | 123.0789 | -6.4682 | 116.3361 | -0.16037 | -0.00070494 | 0.019418 | 0.015344 | 0.0039436 | 0.0027644 | 0.00011745 | 0.016968 | -0.00035457 | -0.0019953 | -0.0066628 | 0.00036527 | -0.0031211 | 0.00033326 | -0.09613 | 0.10529 | -0.09613 | -0.036621 | 0.09613 | -0.073242 | 0.050354 | 0.11444 | 116.7343 | -6.2576 | 116.6061 | -6.3812 | -6.5964 | -6.5552 | 6.3721 | -116.2308 | -116.3727 | 6.5643 | 6.5186 | 6.395 | 0.14648 | 0.022888 | 0.21057 | 0.39825 | 0.27008 | 0.086975 | -0.086975 | -0.12817 | -0.29755 | -0.33875 | 0.19226 | 0.059509 | -0.1236 | 122.8638 | 0.20142 | 122.9919 | 6.5735 | 123.2025 | -116.4322 | -122.5937 | 6.4316 | 123.0743 | 6.3721 | 6.5826
399.8281 | 123.0011 | -5.0949 | 118.1351 | -0.19089 | -0.00049134 | 0.019846 | 0.016199 | -0.0011834 | 0.0027644 | 0.00075845 | -0.044067 | 0.00092703 | -7.2674e-05 | 0.0067954 | -0.00070273 | -0.0022665 | 0.00076046 | -0.15106 | 0.13733 | -0.15106 | -0.15564 | -0.054932 | -0.2243 | -0.059509 | 0.1236 | 118.2495 | -4.8477 | 117.5812 | -5.1636 | -5.0812 | -4.8614 | 4.9438 | -117.9977 | -118.2907 | 5.04 | 5.0354 | 4.8706 | 0.091553 | -0.073242 | 0.24719 | 0.11444 | -0.55389 | -0.068664 | 0.23346 | 0.013733 | -0.013733 | -0.23346 | 0.09613 | -0.004578 | -0.31586 | 122.4289 | 0.28839 | 123.0972 | 5.2322 | 123.3444 | -118.2861 | -122.9828 | 4.9393 | 122.6761 | 4.9438 | 5.2185
401.5625 | 122.9874 | -5.4611 | 117.5766 | -0.091705 | -0.0022003 | 0.017709 | 0.015131 | -0.0024652 | -0.0012946 | 0.00011745 | 0.0078126 | 0.0011408 | 0.0035589 | -0.0034586 | -0.00070273 | -0.0033347 | -0.0037255 | -0.17853 | 0.14191 | -0.14191 | -0.15106 | -0.013733 | -0.14191 | -0.032043 | 0.29755 | 117.5537 | -5.5161 | 117.2745 | -5.2689 | -5.365 | -5.4657 | 5.3192 | -117.4347 | -117.7277 | 5.4474 | 5.4291 | 5.3192 | 0.10986 | 0 | -0.054931 | -0.022888 | -0.30212 | 0.19226 | -0.004577 | 0.096131 | 0.050354 | 0.15106 | 0.12817 | -0.009155 | 0.24719 | 122.7905 | 0.28381 | 123.0698 | 5.603 | 123.0148 | -117.7185 | -123.0927 | 5.3101 | 122.7356 | 5.2826 | 5.7587
403.2969 | 122.9919 | -2.5772 | 120.4376 | -0.22903 | -0.00027774 | 0.0207 | 0.017908 | 0.0015936 | -0.00065361 | -0.00073695 | -0.037964 | 0.00028623 | 0.0020635 | -0.0030312 | 0.00057887 | -0.0020529 | -0.00052114 | -0.16022 | 0.14191 | -0.13733 | -0.15564 | -0.068665 | -0.20142 | -0.064087 | 0.20142 | 120.4239 | -2.655 | 120.3186 | -2.4399 | -2.5452 | -2.4445 | 2.4399 | -120.2957 | -120.5933 | 2.5085 | 2.5131 | 2.3758 | 0.073242 | -0.064087 | -0.07782 | -0.013733 | -0.11902 | 0.13733 | 0.13275 | 0.032043 | 0.21057 | 0.10986 | 0.068664 | -0.018311 | 0.21515 | 122.9736 | 0.27924 | 123.0789 | 2.7191 | 123.0011 | -120.575 | -123.0927 | 2.4216 | 122.8958 | 2.417 | 2.7786
404.9844 | 129.1122 | -2.6321 | 120.3735 | -0.168 | -0.0028411 | 0.019205 | 0.011499 | -0.002038 | 0.00084159 | -9.6154e-05 | -0.0013428 | 0.0013544 | 0.00056833 | -0.0049538 | 0.00079247 | -0.0033347 | -0.0030847 | 6.0333 | 0.11444 | -0.11444 | 1.0666 | 0.21057 | -0.23346 | 3.7354 | 0.52185 | 120.3873 | -2.6871 | 120.401 | -2.2614 | -1.0666 | -2.449 | 2.5177 | -120.2591 | -119.3069 | 2.8427 | 6.3675 | 2.3987 | 3.8498 | -0.11902 | -0.054932 | 0.013733 | 0.027466 | 0.37079 | 0.1831 | 1.5656 | 0.23804 | 1.6205 | 0.32501 | 1.181 | 0.42572 | 123.0881 | 0.22888 | 123.0743 | 2.7466 | 123.0194 | -120.488 | -123.0606 | 3.6987 | 123.0331 | 8.6655 | 3.154
406.7188 | 123.0789 | -2.5269 | 120.4788 | -0.22141 | -0.0024139 | 0.020059 | 0.014917 | 0.0028754 | -0.00044001 | 0.0028946 | 0.026123 | -0.00014097 | 0.00078193 | -0.0051676 | 0.0016471 | -0.0035483 | 0.0011877 | -0.10529 | 0.11444 | -0.091553 | -0.064087 | 0.07782 | -0.082397 | 0.022888 | 0.19226 | 120.4376 | -2.6093 | 120.3827 | -2.3438 | -2.4033 | -2.3117 | 2.4353 | -120.3644 | -120.5429 | 2.6047 | 2.5497 | 2.4445 | 0.11444 | 0.009156 | -0.082398 | -0.041199 | -0.096131 | 0.1831 | 0.21515 | 0.1236 | 0.29755 | 0.20599 | 0.16937 | 0.027466 | 0.2655 | 122.9919 | 0.20599 | 123.0469 | 2.6413 | 122.9645 | -120.5704 | -123.0881 | 2.4628 | 122.9095 | 2.4216 | 2.7191
408.3906 | 123.0011 | -2.2659 | 120.7581 | -0.12222 | -6.4144e-05 | 0.018137 | 0.018976 | 0.0020208 | 0.001269 | -0.001378 | -0.053223 | 0.00049983 | 0.0020635 | 0.0014548 | 0.00079247 | -0.0026939 | -0.00052114 | -0.11444 | 0.13733 | -0.12817 | -0.10529 | -0.004578 | -0.14648 | -0.054932 | 0.24719 | 120.7535 | -2.3483 | 120.6436 | -2.1194 | -2.211 | -2.1194 | 2.1378 | -120.6207 | -120.8633 | 2.2614 | 2.211 | 2.1194 | 0.073242 | -0.01831 | -0.082398 | -0.004578 | -0.11444 | 0.14648 | 0.14648 | 0.054931 | 0.22888 | 0.13733 | 0.1236 | 0.022888 | 0.22888 | 122.9919 | 0.2655 | 123.1018 | 2.4033 | 123.0194 | -120.8862 | -123.1064 | 2.1606 | 122.9095 | 2.1515 | 2.5131
410.125 | 123.0606 | -2.2659 | 120.7809 | -0.22141 | -0.0015595 | 0.020059 | 0.016626 | 0.0015936 | 0.0027644 | -0.00073695 | -0.022705 | 0.0013544 | 0.0018499 | 0.0048728 | -0.00027553 | 0.00029693 | 0.0026831 | -0.15106 | 0.13733 | -0.14191 | -0.14648 | -0.022888 | -0.1831 | -0.054932 | 0.16479 | 120.7809 | -2.3117 | 120.694 | -2.0782 | -2.1652 | -2.0508 | 2.124 | -120.6436 | -120.9274 | 2.243 | 2.211 | 2.0828 | 0.086975 | -0.041198 | -0.045777 | 0 | -0.086975 | 0.18768 | 0.21515 | 0.10071 | 0.26093 | 0.14649 | 0.11902 | -0.004577 | 0.23346 | 123.0057 | 0.27924 | 123.0927 | 2.4033 | 123.0469 | -120.9229 | -123.0927 | 2.1194 | 122.9599 | 2.1149 | 2.4307
411.7969 | 123.0972 | -2.0645 | 120.9274 | -0.23666 | -6.4144e-05 | 0.019418 | 0.015558 | -0.00075622 | 0.0027644 | -0.001378 | 0.035278 | 0.0024224 | 0.0018499 | -0.0064492 | 0.00079247 | -0.0041891 | 0.0016151 | -0.09613 | 0.086975 | -0.09613 | -0.032043 | 0.10986 | -0.064087 | 0.059509 | 0.25177 | 120.8725 | -2.1286 | 120.8862 | -1.8448 | -1.9272 | -1.8494 | 1.9684 | -120.8405 | -120.9595 | 2.1744 | 2.124 | 2.0004 | 0.15564 | 0.032043 | -0.064087 | -0.054931 | -0.041199 | 0.21973 | 0.21515 | 0.13733 | 0.27924 | 0.20142 | 0.20599 | 0.064087 | 0.28381 | 123.0148 | 0.1831 | 123.0011 | 2.1515 | 122.937 | -121.0236 | -123.056 | 2.0325 | 122.9507 | 1.9684 | 2.3163
413.5312 | 123.1247 | -2.037 | 120.9503 | -0.168 | -6.4144e-05 | 0.019205 | 0.016626 | -0.0028924 | 0.0034052 | -0.00095055 | -0.019653 | 0.00028623 | 0.0012091 | -0.0070902 | -0.00048913 | -0.00077127 | -0.0015893 | -0.11444 | 0.11444 | -0.1236 | -0.059509 | 0.064087 | -0.073242 | 0.009155 | 0.23804 | 120.9457 | -2.1057 | 120.9457 | -1.7853 | -1.8951 | -1.7761 | 1.9135 | -120.8359 | -121.0098 | 2.1011 | 2.0462 | 1.9638 | 0.13275 | 0.050354 | -0.068665 | -0.004577 | -0.004577 | 0.25177 | 0.26093 | 0.14191 | 0.32959 | 0.21057 | 0.18768 | 0.064087 | 0.32044 | 123.0515 | 0.23804 | 123.0515 | 2.1515 | 122.9828 | -121.0739 | -123.056 | 1.9775 | 122.9828 | 1.9226 | 2.2751
415.2188 | 123.0698 | -1.9958 | 121.0281 | -0.15274 | -0.0051909 | 0.018137 | 0.015558 | -0.0011834 | 0.00084159 | 0.00011745 | 0.041382 | 0.00071343 | 0.0016363 | -0.0036722 | -0.00027553 | -0.0022665 | 0.00054686 | -0.10529 | 0.09613 | -0.10529 | -0.054932 | 0.082397 | -0.045776 | 0.045776 | 0.27466 | 120.9961 | -2.0737 | 120.9274 | -1.7807 | -1.8448 | -1.7944 | 1.8906 | -120.932 | -121.0831 | 2.0782 | 2.0416 | 1.9501 | 0.15106 | 0.05951 | -0.077819 | -0.032043 | -0.10071 | 0.21515 | 0.20142 | 0.15106 | 0.27924 | 0.22888 | 0.18768 | 0.050354 | 0.29297 | 123.0011 | 0.20142 | 123.0698 | 2.092 | 122.9919 | -121.1334 | -123.1018 | 1.9409 | 122.9233 | 1.8906 | 2.2705
416.9531 | 123.0469 | -1.8997 | 121.1517 | -0.13748 | -0.0024139 | 0.0207 | 0.017694 | 0.0043708 | 0.0027644 | -9.6154e-05 | -0.03186 | 0.00049983 | 0.00078193 | 0.0012412 | -6.1934e-05 | -0.0031211 | 0.0018287 | -0.13275 | 0.1236 | -0.14191 | -0.14648 | -0.054932 | -0.19684 | -0.068665 | 0.14648 | 121.1288 | -1.9684 | 121.0098 | -1.7441 | -1.8448 | -1.7303 | 1.7578 | -121.0281 | -121.2982 | 1.8448 | 1.8311 | 1.7029 | 0.073242 | -0.054931 | -0.068665 | -0.022888 | -0.14191 | 0.15564 | 0.16937 | 0.054931 | 0.23804 | 0.1236 | 0.086975 | -0.004577 | 0.2243 | 122.9782 | 0.2655 | 123.0972 | 2.0233 | 123.0286 | -121.2936 | -123.1201 | 1.7532 | 122.9095 | 1.767 | 2.0462
418.6875 | 123.1338 | -1.799 | 121.1746 | -0.16037 | -0.0039093 | 0.017709 | 0.013849 | -0.0033196 | -0.0015082 | 0.00054465 | 0.053589 | 0.00028623 | 0.00056833 | -0.0047402 | 0.00015167 | -0.0048301 | -9.3938e-05 | -0.13275 | 0.11444 | -0.1236 | -0.082397 | 0.059509 | -0.07782 | 0.064087 | 0.20599 | 121.1655 | -1.8906 | 121.1334 | -1.5701 | -1.6342 | -1.593 | 1.6754 | -121.0602 | -121.257 | 1.8585 | 1.8631 | 1.7212 | 0.18768 | 0.045776 | -0.091553 | -0.009156 | -0.041199 | 0.22888 | 0.20599 | 0.1648 | 0.29755 | 0.25635 | 0.1831 | 0.041199 | 0.32043 | 123.024 | 0.23804 | 123.056 | 1.9135 | 122.9645 | -121.2982 | -123.0652 | 1.7166 | 122.9324 | 1.6663 | 2.005
420.375 | 123.1384 | -1.799 | 121.1746 | -0.14511 | -0.0051909 | 0.017709 | 0.013208 | -0.00011542 | 0.00062799 | 0.0011856 | 0.071899 | 0.00028623 | 0.00056833 | -0.00068143 | -0.00048913 | -0.0044029 | -0.0015893 | -0.09613 | 0.10071 | -0.10071 | -0.018311 | 0.12817 | -0.027466 | 0.091553 | 0.29755 | 121.1655 | -1.8677 | 121.1929 | -1.5106 | -1.5884 | -1.5427 | 1.6983 | -121.0739 | -121.1929 | 1.9272 | 1.8906 | 1.7715 | 0.19226 | 0.073242 | -0.068665 | -0.009156 | 0.01831 | 0.28839 | 0.25635 | 0.21057 | 0.32501 | 0.27924 | 0.22888 | 0.082397 | 0.35706 | 123.0606 | 0.20142 | 123.0331 | 1.8997 | 122.9645 | -121.2753 | -123.0423 | 1.7807 | 122.9919 | 1.7029 | 2.0966
422.1406 | 123.0469 | -1.799 | 121.2341 | -0.17563 | -6.4144e-05 | 0.017282 | 0.018762 | 0.0018072 | 0.0014826 | 0.00204 | -0.044067 | 0.0011408 | -7.2674e-05 | 0.0027366 | -0.0015573 | -0.00034387 | 0.0026831 | -0.14648 | 0.14648 | -0.14191 | -0.14191 | -0.027466 | -0.17395 | -0.059509 | 0.16937 | 121.2204 | -1.8677 | 121.1334 | -1.6251 | -1.7349 | -1.6113 | 1.6571 | -121.0876 | -121.376 | 1.7715 | 1.7395 | 1.6251 | 0.082398 | -0.032043 | -0.068665 | -0.013733 | -0.10071 | 0.17395 | 0.18768 | 0.064087 | 0.25635 | 0.13275 | 0.11444 | 0 | 0.24261 | 123.0011 | 0.28839 | 123.0881 | 1.9455 | 123.0194 | -121.376 | -123.1018 | 1.6571 | 122.9324 | 1.6525 | 1.9684
423.8125 | 123.1201 | -1.6708 | 121.344 | -0.18326 | -0.00070494 | 0.0207 | 0.018976 | 0.0011664 | 0.0021234 | -0.001378 | -0.041016 | 0.0011408 | 0.0012091 | 0.0010276 | 0.00015167 | -0.0046165 | -0.0039391 | -0.1236 | 0.11444 | -0.13733 | -0.091553 | 0.022888 | -0.13275 | 0 | 0.20599 | 121.3486 | -1.7441 | 121.3165 | -1.442 | -1.5289 | -1.4145 | 1.5335 | -121.2296 | -121.4355 | 1.6937 | 1.6708 | 1.5381 | 0.13733 | 0.004578 | -0.073243 | 0.004578 | -0.027466 | 0.22888 | 0.25635 | 0.14191 | 0.32959 | 0.21515 | 0.16022 | 0.045776 | 0.30212 | 123.0606 | 0.25177 | 123.0927 | 1.7853 | 123.0194 | -121.4813 | -123.0881 | 1.5793 | 122.9874 | 1.5472 | 1.8768
425.5625 | 122.9828 | -1.593 | 121.4722 | -0.11459 | -0.00027774 | 0.018777 | 0.018976 | 0.0043708 | 0.002978 | 0.0018264 | -0.074585 | 0.00092703 | -0.00028627 | 0.0055136 | -6.1934e-05 | -0.0022665 | -0.0013757 | -0.13733 | 0.14191 | -0.14648 | -0.14648 | -0.050354 | -0.20599 | -0.073242 | 0.16479 | 121.4859 | -1.6479 | 121.3211 | -1.4557 | -1.5518 | -1.4374 | 1.4465 | -121.3303 | -121.6187 | 1.5427 | 1.5198 | 1.387 | 0.073242 | -0.05951 | -0.054931 | 0.013733 | -0.15106 | 0.13733 | 0.15564 | 0.041199 | 0.21057 | 0.09613 | 0.09613 | 0 | 0.19226 | 122.9691 | 0.28839 | 123.1338 | 1.7349 | 123.0789 | -121.6187 | -123.1201 | 1.4465 | 122.9141 | 1.4557 | 1.7578
427.2344 | 123.0194 | -1.4969 | 121.5179 | -0.18326 | -0.0030547 | 0.019846 | 0.016626 | 0.0020208 | 0.0038324 | 0.0016128 | -0.059326 | 0.0024224 | 0.00014093 | -0.002604 | 0.00057887 | -0.0018393 | 0.0022559 | -0.15106 | 0.11444 | -0.13275 | -0.16479 | -0.068665 | -0.19684 | -0.064087 | 0.1236 | 121.5866 | -1.5839 | 121.4264 | -1.3641 | -1.4511 | -1.3458 | 1.3641 | -121.4035 | -121.6827 | 1.4282 | 1.4328 | 1.3 | 0.068664 | -0.064087 | -0.086975 | 0.068665 | -0.091552 | 0.13275 | 0.15106 | 0.045776 | 0.23804 | 0.13275 | 0.064086 | -0.032044 | 0.21973 | 123.0103 | 0.24719 | 123.1705 | 1.6113 | 123.0835 | -121.6507 | -123.1018 | 1.3321 | 122.9233 | 1.3458 | 1.6205
428.9688 | 123.1155 | -1.387 | 121.6187 | -0.16037 | -0.0026275 | 0.018564 | 0.014276 | 0.0028754 | -0.00022641 | 0.0033218 | 0.053589 | -0.00014097 | 0.0016363 | -0.0038858 | 0.0016471 | -0.0031211 | 0.00054686 | -0.10986 | 0.10071 | -0.11444 | -0.022888 | 0.10071 | -0.032043 | 0.054932 | 0.29297 | 121.6324 | -1.4648 | 121.5546 | -1.149 | -1.2131 | -1.1536 | 1.2726 | -121.5179 | -121.6415 | 1.4877 | 1.442 | 1.355 | 0.16937 | 0.082398 | -0.07782 | 0.013733 | -0.064087 | 0.23804 | 0.23346 | 0.17395 | 0.31128 | 0.25177 | 0.21515 | 0.091553 | 0.31586 | 123.0194 | 0.21515 | 123.0972 | 1.4877 | 123.0194 | -121.7331 | -123.0835 | 1.3641 | 122.9416 | 1.2772 | 1.68
430.7031 | 123.143 | -1.3 | 121.6599 | -0.21378 | 0.00057686 | 0.019418 | 0.014276 | 0.0022346 | 0.0016962 | -9.6154e-05 | 0.023071 | 0.00049983 | 0.0014227 | -0.0047402 | 0.00015167 | -0.0035483 | -0.00094854 | -0.07782 | 0.09613 | -0.086975 | -0.032043 | 0.10529 | -0.064087 | 0.045776 | 0.2655 | 121.6324 | -1.3824 | 121.669 | -1.0757 | -1.1627 | -1.0666 | 1.2131 | -121.5637 | -121.6919 | 1.4053 | 1.3458 | 1.236 | 0.13275 | 0.022888 | -0.082397 | -0.027466 | 0.009155 | 0.2243 | 0.23346 | 0.13733 | 0.31586 | 0.21973 | 0.19226 | 0.054932 | 0.3067 | 123.0515 | 0.1831 | 123.0148 | 1.3962 | 122.9324 | -121.7468 | -123.0423 | 1.268 | 122.9691 | 1.2222 | 1.5656
432.375 | 123.1247 | -1.2497 | 121.7514 | -0.19852 | -0.00091854 | 0.019632 | 0.017481 | 0.0015936 | 0.0051142 | 0.00033105 | -0.0043944 | 0.00071343 | 0.00035453 | -0.0030312 | -0.0017709 | -0.0024803 | -0.0028711 | -0.091553 | 0.09613 | -0.10986 | -0.041199 | 0.086975 | -0.082397 | 0.036621 | 0.26093 | 121.7422 | -1.3138 | 121.7606 | -1.0117 | -1.0895 | -0.98877 | 1.1398 | -121.6553 | -121.7926 | 1.3367 | 1.2863 | 1.1673 | 0.14648 | 0.027466 | -0.064087 | -0.009155 | 0.009155 | 0.23804 | 0.26092 | 0.16022 | 0.32501 | 0.2243 | 0.19684 | 0.068664 | 0.30212 | 123.0743 | 0.20599 | 123.056 | 1.3458 | 122.9919 | -121.8613 | -123.0652 | 1.2085 | 123.0103 | 1.1581 | 1.5106
434.1094 | 123.0469 | -1.2772 | 121.7926 | -0.14511 | -0.0030547 | 0.016428 | 0.015131 | -0.0024652 | -0.0015082 | 0.00054465 | -0.016602 | 0.0019952 | 0.0012091 | -0.0019632 | -0.00048913 | -0.0016257 | -0.0043665 | -0.16022 | 0.14191 | -0.14191 | -0.13733 | -0.036621 | -0.13733 | -0.041199 | 0.20599 | 121.8246 | -1.3092 | 121.6873 | -1.0712 | -1.1581 | -1.0757 | 1.1353 | -121.6507 | -121.9299 | 1.2405 | 1.236 | 1.1398 | 0.10071 | 0.004578 | -0.032043 | 0.032043 | -0.10529 | 0.20599 | 0.20142 | 0.11902 | 0.23346 | 0.15106 | 0.10529 | 0.004578 | 0.23804 | 122.9965 | 0.28381 | 123.1338 | 1.4191 | 123.1018 | -121.9345 | -123.1018 | 1.1398 | 122.9645 | 1.1169 | 1.4832
435.7812 | 123.0698 | -1.2314 | 121.8109 | -0.16037 | -0.0026275 | 0.020273 | 0.01684 | 0.0018072 | 0.00041439 | -0.00095055 | -0.022705 | 0.0024224 | 0.0016363 | 0.0067954 | 0.0014335 | -0.0058981 | 0.0014015 | -0.10986 | 0.11444 | -0.13733 | -0.091553 | 0.045776 | -0.10529 | -0.018311 | 0.27466 | 121.8109 | -1.3 | 121.7377 | -1.0345 | -1.1124 | -1.0437 | 1.0941 | -121.6965 | -121.9025 | 1.2772 | 1.2131 | 1.1261 | 0.11902 | 0.032043 | -0.068665 | 0 | -0.073242 | 0.19684 | 0.18768 | 0.11902 | 0.25635 | 0.18768 | 0.18311 | 0.045776 | 0.2655 | 123.0377 | 0.25177 | 123.111 | 1.3458 | 123.0423 | -121.9482 | -123.111 | 1.1398 | 122.9691 | 1.1215 | 1.506
437.5156 | 123.1659 | -1.1536 | 121.8246 | -0.18326 | -0.0019867 | 0.019846 | 0.013635 | -0.00096982 | 0.0014826 | 0.00033105 | 0.099365 | 0.00071343 | 0.00035453 | -0.015208 | 0.00079247 | -0.0046165 | 0.00011966 | -0.10529 | 0.10986 | -0.10071 | -0.036621 | 0.11444 | -0.013733 | 0.09613 | 0.29755 | 121.8018 | -1.2589 | 121.8201 | -0.87891 | -0.96588 | -0.92926 | 1.0529 | -121.7148 | -121.8613 | 1.268 | 1.2497 | 1.1398 | 0.19684 | 0.086975 | -0.10529 | -0.022888 | -0.004578 | 0.27466 | 0.2243 | 0.18768 | 0.32959 | 0.29297 | 0.21515 | 0.064087 | 0.37994 | 123.0789 | 0.21057 | 123.0606 | 1.2634 | 122.9553 | -121.9254 | -123.0835 | 1.1169 | 122.9736 | 1.0483 | 1.4511
439.1875 | 123.0698 | -1.1536 | 121.8613 | -0.168 | -0.0015595 | 0.01835 | 0.017267 | -0.001397 | 0.0036188 | -0.00030975 | 0.050537 | 0.001568 | 0.0037725 | -0.0019632 | -6.1934e-05 | -0.0037619 | -0.0015893 | -0.086975 | 0.10986 | -0.11902 | -0.027466 | 0.086975 | -0.045776 | 0.059509 | 0.27008 | 121.8521 | -1.2314 | 121.788 | -0.93842 | -0.99792 | -0.94757 | 1.0345 | -121.7514 | -121.8887 | 1.2405 | 1.2131 | 1.1078 | 0.17853 | 0.073243 | -0.07782 | -0.009155 | -0.073242 | 0.21515 | 0.20599 | 0.15564 | 0.28381 | 0.23346 | 0.20599 | 0.091553 | 0.29297 | 123.0194 | 0.22888 | 123.0835 | 1.2634 | 123.0057 | -121.9803 | -123.0927 | 1.1261 | 122.9416 | 1.0666 | 1.4236
440.9062 | 123.111 | -1.1261 | 121.8521 | -0.17563 | -0.00070494 | 0.018777 | 0.015985 | -0.0022516 | 0.00041439 | 0.00011745 | 0.053589 | 0.0022088 | -0.00049987 | -0.0096536 | 0.0016471 | -0.0050437 | -0.0024439 | -0.14191 | 0.11902 | -0.10986 | -0.082397 | 0.041199 | -0.091553 | 0.045776 | 0.19226 | 121.8658 | -1.1993 | 121.8338 | -0.89722 | -0.97046 | -0.90637 | 1.0162 | -121.7331 | -121.9345 | 1.1673 | 1.1719 | 1.0345 | 0.15564 | 0.01831 | -0.073242 | 0.013733 | -0.018311 | 0.22888 | 0.21973 | 0.15564 | 0.29297 | 0.22888 | 0.15106 | 0.027466 | 0.30212 | 123.0331 | 0.22888 | 123.0652 | 1.2451 | 122.9919 | -121.962 | -123.0515 | 1.0437 | 122.9599 | 0.98419 | 1.3184
442.6094 | 123.0606 | -1.1169 | 121.9391 | -0.14511 | -0.00049134 | 0.017496 | 0.015772 | 0.00031198 | -0.001081 | -0.00052335 | -0.025757 | 0.00092703 | 0.0020635 | -0.0019632 | -0.00070273 | -0.0035483 | -0.0011621 | -0.16022 | 0.12817 | -0.14648 | -0.13733 | -0.059509 | -0.13733 | -0.032043 | 0.21973 | 121.9666 | -1.1902 | 121.8201 | -0.92468 | -1.0254 | -0.93842 | 0.97046 | -121.8109 | -122.0764 | 1.0574 | 1.0849 | 0.97961 | 0.11444 | 0.009155 | -0.073243 | 0.027466 | -0.11902 | 0.19226 | 0.17853 | 0.091552 | 0.25177 | 0.1648 | 0.086975 | 0.009155 | 0.2655 | 123.0103 | 0.27466 | 123.1567 | 1.2451 | 123.0835 | -122.0856 | -123.1293 | 0.97961 | 122.937 | 0.95673 | 1.3367
444.3281 | 123.1155 | -1.062 | 121.9254 | -0.21378 | -0.0013457 | 0.019846 | 0.013422 | -0.0016106 | -0.00022641 | 0.00054465 | 0.035278 | 0.0011408 | -7.2674e-05 | -0.00089503 | 0.0010061 | -0.0018393 | 0.00011966 | -0.091553 | 0.073242 | -0.091553 | -0.022888 | 0.10986 | -0.07782 | 0.050354 | 0.24261 | 121.9254 | -1.1398 | 121.9254 | -0.82855 | -0.91553 | -0.83313 | 0.97046 | -121.8521 | -121.9482 | 1.1719 | 1.1124 | 0.98419 | 0.14191 | 0.013733 | -0.07782 | 0 | 0 | 0.23346 | 0.22888 | 0.14648 | 0.3067 | 0.2243 | 0.20142 | 0.068665 | 0.31128 | 123.0652 | 0.16479 | 123.0652 | 1.1353 | 122.9874 | -122.0169 | -123.0652 | 1.0391 | 122.9874 | 0.97046 | 1.3046
446.0625 | 123.0331 | -1.0483 | 122.0078 | -0.12985 | -0.0015595 | 0.018777 | 0.018549 | 0.0043708 | 0.0016962 | 0.00075845 | -0.071533 | 0.00092703 | 0.0029181 | -0.0011086 | -0.0039071 | -0.0026939 | -9.3938e-05 | -0.15564 | 0.13733 | -0.14191 | -0.14648 | -0.041199 | -0.18768 | -0.050354 | 0.16022 | 122.0169 | -1.1261 | 121.8887 | -0.90179 | -0.99335 | -0.88348 | 0.90637 | -121.8704 | -122.1542 | 1.0071 | 0.99792 | 0.8606 | 0.091553 | -0.045776 | -0.07782 | 0.009156 | -0.11902 | 0.14648 | 0.16479 | 0.054932 | 0.24261 | 0.13275 | 0.10071 | -0.004577 | 0.2243 | 123.0148 | 0.27924 | 123.143 | 1.1856 | 123.0652 | -122.1497 | -123.1338 | 0.90179 | 122.937 | 0.89264 | 1.2085
447.7969 | 123.143 | -1.0117 | 121.9711 | -0.168 | -0.0039093 | 0.018564 | 0.013849 | 0.0020208 | -0.00086721 | 0.00054465 | 0.084106 | -0.00014097 | -0.00049987 | -0.003245 | 0.0018607 | -0.0046165 | 0.00054686 | -0.09613 | 0.07782 | -0.10529 | -0.013733 | 0.16479 | 0.004578 | 0.086975 | 0.3067 | 121.9757 | -1.0849 | 121.9711 | -0.71869 | -0.8194 | -0.76904 | 0.90637 | -121.8933 | -121.9849 | 1.1765 | 1.0986 | 1.0162 | 0.19226 | 0.10986 | -0.073242 | 0.004578 | 0 | 0.29297 | 0.24261 | 0.19226 | 0.31586 | 0.2655 | 0.27008 | 0.091553 | 0.36621 | 123.056 | 0.18311 | 123.0606 | 1.0895 | 122.9874 | -122.0764 | -123.056 | 0.99792 | 122.9828 | 0.91553 | 1.3184
449.5312 | 123.056 | -1.03 | 122.0169 | -0.068817 | -6.4144e-05 | 0.019205 | 0.017481 | 0.0026618 | 0.0014826 | 0.0022536 | -0.034912 | 0.0011408 | 0.00035453 | 0.0014548 | -0.00048913 | -0.0026939 | -0.0052209 | -0.11902 | 0.1236 | -0.14191 | -0.09613 | 0.004578 | -0.11444 | 0 | 0.27924 | 122.0215 | -1.0895 | 121.9345 | -0.82398 | -0.90637 | -0.83313 | 0.88806 | -121.8933 | -122.113 | 1.0345 | 1.03 | 0.91553 | 0.14191 | 0.027466 | -0.05951 | 0.004577 | -0.082398 | 0.20599 | 0.19684 | 0.1236 | 0.25635 | 0.18311 | 0.14649 | 0.045777 | 0.2655 | 123.024 | 0.2655 | 123.111 | 1.1536 | 123.0515 | -122.1588 | -123.1064 | 0.93384 | 122.9645 | 0.91095 | 1.3092
451.2188 | 123.0972 | -1.0071 | 122.0032 | -0.19089 | -6.4144e-05 | 0.020273 | 0.015344 | 0.00052558 | 0.0025506 | -0.0033006 | 0.053589 | 0.00028623 | 0.0035589 | -0.012431 | 0.0025015 | -0.0033347 | 0.00033326 | -0.10071 | 0.068665 | -0.10529 | -0.054932 | 0.09613 | -0.082397 | 0.036621 | 0.20142 | 121.994 | -1.0712 | 121.9528 | -0.78735 | -0.84686 | -0.78735 | 0.90179 | -121.9345 | -122.0581 | 1.1032 | 1.0437 | 0.92468 | 0.14191 | 0.022889 | -0.064087 | -0.009155 | -0.050354 | 0.21973 | 0.21973 | 0.16022 | 0.28381 | 0.2243 | 0.20142 | 0.050354 | 0.28381 | 123.024 | 0.17395 | 123.0652 | 1.0757 | 123.0011 | -122.1085 | -123.0743 | 0.95215 | 122.9599 | 0.90637 | 1.2085
452.8906 | 123.024 | -1.0208 | 122.0444 | -0.19852 | -0.00027774 | 0.020059 | 0.018976 | -0.0016106 | 0.0031916 | -0.0020188 | -0.053223 | 0.0013544 | -0.0011407 | -0.0023904 | 0.00015167 | -0.0014121 | 0.0011877 | -0.16022 | 0.12817 | -0.14648 | -0.15106 | -0.045776 | -0.19226 | -0.050354 | 0.16022 | 122.0581 | -1.062 | 121.9299 | -0.85144 | -0.94757 | -0.84228 | 0.87433 | -121.9162 | -122.1954 | 0.97504 | 0.97046 | 0.82855 | 0.09613 | -0.045777 | -0.041199 | 0.013732 | -0.11444 | 0.16937 | 0.17853 | 0.073242 | 0.21973 | 0.11444 | 0.10071 | -0.004578 | 0.21057 | 122.9919 | 0.27466 | 123.1201 | 1.149 | 123.0789 | -122.1909 | -123.1064 | 0.86975 | 122.9507 | 0.8606 | 1.181
454.625 | 123.0194 | -1.0025 | 122.081 | -0.168 | -0.0034821 | 0.018137 | 0.016413 | 0.0035162 | -1.2808e-05 | 0.00204 | 0.035278 | 0.001568 | 0.0016363 | 0.0010276 | 0.0010061 | -0.0041891 | -0.00073494 | -0.12817 | 0.12817 | -0.13275 | -0.1236 | 0.013733 | -0.11444 | -0.013733 | 0.21057 | 122.0901 | -1.0666 | 121.9391 | -0.78735 | -0.86517 | -0.82398 | 0.86975 | -121.9528 | -122.2046 | 1.0162 | 0.98877 | 0.88806 | 0.11902 | 0.01831 | -0.064087 | 0.009155 | -0.14191 | 0.21515 | 0.17853 | 0.13733 | 0.24261 | 0.20142 | 0.14648 | 0.009155 | 0.27924 | 123.0057 | 0.26093 | 123.1567 | 1.1307 | 123.0927 | -122.2137 | -123.1476 | 0.87891 | 122.9416 | 0.87433 | 1.2131
456.2969 | 123.0331 | -0.98419 | 122.1039 | -0.099335 | -0.0041229 | 0.016428 | 0.014276 | 0.00073918 | 0.00084159 | 0.0024674 | 0.02002 | -0.00014097 | 0.0016363 | 0.00081397 | 0.00057887 | -0.0031211 | 0.00033326 | -0.1831 | 0.13275 | -0.14191 | -0.16479 | -0.050354 | -0.15106 | -0.045776 | 0.18768 | 122.113 | -1.0483 | 121.9345 | -0.81024 | -0.88806 | -0.82398 | 0.84228 | -121.9711 | -122.2687 | 0.93384 | 0.93842 | 0.83313 | 0.096131 | -0.009155 | -0.064087 | 0.009155 | -0.16937 | 0.17395 | 0.16022 | 0.09613 | 0.2243 | 0.16022 | 0.091553 | -0.022888 | 0.23804 | 122.9828 | 0.27466 | 123.1613 | 1.1169 | 123.0972 | -122.2458 | -123.1522 | 0.8194 | 122.9187 | 0.80109 | 1.1719
458.0312 | 123.1293 | -0.9201 | 122.0673 | -0.168 | 0.0010041 | 0.020059 | 0.014063 | 0.0015936 | 0.001269 | -9.6154e-05 | 0.02002 | -0.00014097 | 0.00014093 | -0.0053812 | 0.00057887 | -0.00098487 | -0.0020165 | -0.07782 | 0.10071 | -0.086975 | -0.027466 | 0.09613 | -0.054932 | 0.054932 | 0.25635 | 122.0764 | -0.97961 | 122.081 | -0.68207 | -0.75531 | -0.68207 | 0.83313 | -121.9666 | -122.0947 | 1.0162 | 0.97504 | 0.86517 | 0.14191 | 0.032043 | -0.059509 | 0.009155 | 0.013733 | 0.23804 | 0.23804 | 0.16479 | 0.29755 | 0.2243 | 0.1831 | 0.059509 | 0.29755 | 123.0606 | 0.18768 | 123.056 | 1.0208 | 122.9965 | -122.1542 | -123.0469 | 0.89264 | 123.0011 | 0.84228 | 1.1765
459.7656 | 123.0972 | -0.88348 | 122.1085 | -0.19089 | -0.0022003 | 0.019418 | 0.014063 | -0.0026788 | -0.00086721 | 0.0028946 | 0.050537 | -0.00035457 | 0.0014227 | 0.00081397 | 0.0010061 | -0.0031211 | -0.0032983 | -0.13275 | 0.091553 | -0.10529 | -0.064087 | 0.082397 | -0.10071 | 0.041199 | 0.17395 | 122.113 | -0.9613 | 122.0627 | -0.68207 | -0.75073 | -0.68665 | 0.7782 | -122.0169 | -122.1725 | 0.96588 | 0.92468 | 0.78278 | 0.14649 | 0.004578 | -0.07782 | 0.004578 | -0.045776 | 0.20142 | 0.19684 | 0.13275 | 0.27466 | 0.21057 | 0.18768 | 0.041199 | 0.27924 | 123.024 | 0.19684 | 123.0743 | 0.97504 | 122.9965 | -122.2137 | -123.0698 | 0.8194 | 122.9462 | 0.75073 | 1.0574
461.5 | 123.1155 | -0.87433 | 122.1085 | -0.22903 | 0.00014946 | 0.020486 | 0.015772 | -0.0060968 | 0.0019098 | 0.0024674 | 0.016968 | 0.00071343 | -0.00049987 | -0.0021768 | -0.0013437 | -0.0046165 | -0.0022301 | -0.086975 | 0.07782 | -0.10071 | -0.027466 | 0.10986 | -0.064087 | 0.054932 | 0.25635 | 122.1451 | -0.92468 | 122.1268 | -0.63171 | -0.70953 | -0.64087 | 0.77362 | -122.0306 | -122.1359 | 0.98419 | 0.92926 | 0.81024 | 0.15564 | 0.036621 | -0.050354 | 0.036622 | 0.018311 | 0.24262 | 0.23346 | 0.1648 | 0.28381 | 0.21515 | 0.21057 | 0.073242 | 0.29297 | 123.0515 | 0.17853 | 123.0698 | 0.95215 | 123.0194 | -122.2092 | -123.0331 | 0.84686 | 123.0011 | 0.78735 | 1.1307
463.1719 | 123.0286 | -0.87891 | 122.1909 | -0.18326 | 0.0020721 | 0.019632 | 0.019403 | 0.00031198 | 0.00084159 | 0.0011856 | -0.068481 | 0.0017816 | -0.00049987 | 0.0095724 | 0.00057887 | -0.00055747 | -0.00094854 | -0.14191 | 0.10986 | -0.14191 | -0.15564 | -0.045776 | -0.20142 | -0.068665 | 0.16479 | 122.2 | -0.93842 | 122.0718 | -0.70038 | -0.80109 | -0.70496 | 0.737 | -122.081 | -122.3465 | 0.83313 | 0.81024 | 0.67749 | 0.073242 | -0.059509 | -0.05951 | 0.009155 | -0.11902 | 0.17853 | 0.17395 | 0.07782 | 0.23346 | 0.13733 | 0.096131 | -0.013733 | 0.23804 | 123.0103 | 0.25177 | 123.1384 | 0.98877 | 123.0789 | -122.3328 | -123.1293 | 0.72327 | 122.9507 | 0.737 | 1.0437
464.9062 | 123.0515 | -0.83771 | 122.2366 | -0.12222 | -0.0036957 | 0.017709 | 0.018122 | 0.0018072 | -0.00044001 | 0.00097205 | -0.047119 | 0.00071343 | -0.00028627 | -0.00046783 | 0.00015167 | -0.0026939 | -0.00052114 | -0.16937 | 0.12817 | -0.15106 | -0.11902 | -0.027466 | -0.12817 | -0.041199 | 0.21515 | 122.2366 | -0.90179 | 122.081 | -0.63629 | -0.75073 | -0.6546 | 0.68665 | -122.1085 | -122.3557 | 0.81024 | 0.79651 | 0.70953 | 0.10986 | 0.022888 | -0.064086 | 0 | -0.15564 | 0.20142 | 0.18311 | 0.086976 | 0.24719 | 0.15106 | 0.1236 | 0.032043 | 0.2655 | 122.9828 | 0.27924 | 123.1384 | 0.96588 | 123.0743 | -122.3877 | -123.1384 | 0.71869 | 122.9187 | 0.66834 | 1.0529
466.6406 | 123.143 | -0.78735 | 122.2092 | -0.18326 | -6.4144e-05 | 0.020486 | 0.016626 | 0.0015936 | -0.00086721 | 0.00075845 | 0.0047608 | -0.00014097 | -0.0011407 | -0.0036722 | -0.00027553 | -0.0022665 | 0.00011966 | -0.082397 | 0.09613 | -0.10986 | -0.036621 | 0.10071 | -0.068665 | 0.050354 | 0.25635 | 122.2321 | -0.84228 | 122.2183 | -0.53101 | -0.63171 | -0.52643 | 0.67749 | -122.113 | -122.2458 | 0.88806 | 0.83771 | 0.71869 | 0.16022 | 0.041198 | -0.054931 | 0.022889 | 0.009156 | 0.25635 | 0.26093 | 0.15564 | 0.31586 | 0.21057 | 0.21057 | 0.073242 | 0.31128 | 123.0606 | 0.20599 | 123.0743 | 0.88348 | 123.0194 | -122.319 | -123.0515 | 0.75073 | 123.0057 | 0.70496 | 1.0437
468.375 | 123.143 | -0.737 | 122.2412 | -0.14511 | -0.0043365 | 0.017709 | 0.014063 | 0.0011664 | 0.0014826 | 0.0016128 | 0.081055 | -0.00035457 | -0.00028627 | -0.00025423 | -0.0024117 | -0.0052573 | 0.0016151 | -0.086975 | 0.091553 | -0.10529 | -0.036621 | 0.12817 | -0.018311 | 0.082397 | 0.31128 | 122.2366 | -0.82855 | 122.2504 | -0.48065 | -0.54016 | -0.5127 | 0.63171 | -122.1497 | -122.2778 | 0.86517 | 0.8194 | 0.71869 | 0.18768 | 0.086975 | -0.091552 | -0.004578 | 0.009155 | 0.25635 | 0.2243 | 0.19684 | 0.31586 | 0.28839 | 0.23346 | 0.068665 | 0.3479 | 123.0789 | 0.19684 | 123.0652 | 0.82855 | 122.9736 | -122.3465 | -123.0698 | 0.70038 | 122.9874 | 0.65002 | 1.0483
470.0469 | 123.056 | -0.75989 | 122.2961 | -0.17563 | -0.0026275 | 0.020273 | 0.015772 | 0.0043708 | -0.0017218 | 0.00011745 | -0.080688 | 0.003277 | 0.0022773 | 0.0023092 | 0.00036527 | -0.0018393 | -9.3938e-05 | -0.09613 | 0.10986 | -0.12817 | -0.10071 | 0.027466 | -0.10529 | -0.004578 | 0.29755 | 122.2961 | -0.81482 | 122.2137 | -0.54932 | -0.63629 | -0.55389 | 0.63171 | -122.1863 | -122.3969 | 0.78735 | 0.75531 | 0.6546 | 0.1236 | 0.022888 | -0.054931 | 0 | -0.082398 | 0.21057 | 0.20599 | 0.1236 | 0.26092 | 0.17853 | 0.15564 | 0.027466 | 0.2655 | 123.0286 | 0.23804 | 123.111 | 0.86975 | 123.056 | -122.4243 | -123.111 | 0.65918 | 122.9736 | 0.66376 | 1.0574
471.7188 | 123.0057 | -0.74616 | 122.3145 | -0.13748 | 0.0012177 | 0.018991 | 0.015558 | -0.001397 | 0.0025506 | -0.001378 | -0.06543 | 0.002636 | -0.0013543 | 0.0033774 | 0.0022879 | -0.0020529 | -0.0032983 | -0.16937 | 0.1236 | -0.13275 | -0.16937 | -0.086975 | -0.2243 | -0.082397 | 0.14191 | 122.319 | -0.80109 | 122.1863 | -0.59967 | -0.69122 | -0.59052 | 0.6134 | -122.1909 | -122.4838 | 0.65918 | 0.66376 | 0.52185 | 0.050354 | -0.091553 | -0.054931 | 0.004578 | -0.12817 | 0.14648 | 0.15564 | 0.054932 | 0.21057 | 0.10986 | 0.045776 | -0.036622 | 0.20142 | 122.9874 | 0.25635 | 123.1201 | 0.86975 | 123.0652 | -122.4472 | -123.1155 | 0.57678 | 122.9324 | 0.57678 | 0.88806
473.4375 | 123.1293 | -0.67291 | 122.3099 | -0.168 | -0.0030547 | 0.018564 | 0.012995 | -0.00096982 | 0.00041439 | -9.6154e-05 | 0.099365 | -0.00078177 | 0.00099553 | -0.0047402 | 0.00079247 | -0.0014121 | -0.0024439 | -0.082397 | 0.073242 | -0.10986 | -0.022888 | 0.13275 | -0.018311 | 0.068665 | 0.3067 | 122.3007 | -0.737 | 122.3053 | -0.41199 | -0.47607 | -0.43945 | 0.56305 | -122.2366 | -122.3328 | 0.80566 | 0.74158 | 0.6546 | 0.17853 | 0.091552 | -0.064087 | -0.009155 | -0.004577 | 0.26093 | 0.23346 | 0.19684 | 0.29755 | 0.26093 | 0.24261 | 0.086975 | 0.32501 | 123.0423 | 0.18311 | 123.0377 | 0.74616 | 122.9736 | -122.4197 | -123.0469 | 0.65002 | 122.9782 | 0.59052 | 0.97961
475.1719 | 123.1613 | -0.66834 | 122.3236 | -0.13748 | -0.0032683 | 0.017282 | 0.014917 | -0.00096982 | 0.0014826 | 0.0033218 | 0.065796 | 0.00071343 | 0.0016363 | -0.0034586 | -0.00027553 | -0.0050437 | -0.00073494 | -0.10529 | 0.10071 | -0.10529 | -0.041199 | 0.086975 | -0.054932 | 0.086975 | 0.27924 | 122.3511 | -0.72327 | 122.3373 | -0.39368 | -0.43945 | -0.41657 | 0.56305 | -122.2229 | -122.3648 | 0.75531 | 0.75531 | 0.6134 | 0.19226 | 0.050354 | -0.054932 | 0.027466 | 0.013733 | 0.27466 | 0.25177 | 0.22888 | 0.3067 | 0.28381 | 0.19226 | 0.064087 | 0.32959 | 123.0606 | 0.20599 | 123.0743 | 0.76904 | 123.0194 | -122.4289 | -123.0469 | 0.62714 | 123.0057 | 0.56305 | 0.94757
476.8438 | 123.111 | -0.64545 | 122.3694 | -0.168 | -0.0028411 | 0.017068 | 0.01449 | -0.003106 | 0.0019098 | 0.0013992 | 0.044434 | 0.00028623 | 0.00056833 | 0.0014548 | 0.00057887 | -0.0037619 | 0.0026831 | -0.09613 | 0.07782 | -0.10071 | -0.036621 | 0.091553 | -0.036621 | 0.07782 | 0.31128 | 122.3648 | -0.69122 | 122.3557 | -0.37079 | -0.44403 | -0.40283 | 0.54474 | -122.2916 | -122.406 | 0.737 | 0.72327 | 0.60883 | 0.17853 | 0.064087 | -0.045776 | -0.004578 | -0.013733 | 0.27466 | 0.24261 | 0.20142 | 0.28839 | 0.24719 | 0.19226 | 0.064087 | 0.32043 | 123.0469 | 0.17853 | 123.056 | 0.72327 | 123.0103 | -122.4701 | -123.0606 | 0.60883 | 123.0011 | 0.54932 | 0.95673
478.5781 | 123.0972 | -0.62256 | 122.3831 | -0.168 | -0.00091854 | 0.018564 | 0.018122 | 0.0037298 | 0.0010554 | 0.00097205 | 0.026123 | 0.00092703 | -0.0017817 | -0.0040994 | -0.00027553 | -0.0024803 | -0.0024439 | -0.10529 | 0.091553 | -0.073242 | -0.041199 | 0.082397 | -0.086975 | 0.041199 | 0.21515 | 122.3877 | -0.6958 | 122.3602 | -0.41657 | -0.48523 | -0.39825 | 0.54932 | -122.2916 | -122.4243 | 0.70496 | 0.66376 | 0.53558 | 0.11444 | -0.013733 | -0.073242 | 0.004577 | -0.022889 | 0.20599 | 0.2243 | 0.13733 | 0.29755 | 0.21057 | 0.15564 | 0.032043 | 0.27924 | 123.056 | 0.16479 | 123.0835 | 0.71411 | 123.0103 | -122.4564 | -123.0789 | 0.58136 | 122.9828 | 0.51727 | 0.83771
480.3281 | 123.0057 | -0.64087 | 122.4609 | -0.14511 | 0.00014946 | 0.019632 | 0.019831 | -0.0016106 | 0.00041439 | 0.0013992 | -0.077637 | 0.0013544 | 0.0014227 | 0.00017297 | -0.00048913 | -0.0035483 | -0.0032983 | -0.11902 | 0.10071 | -0.14191 | -0.10529 | -0.022888 | -0.16022 | -0.045776 | 0.2243 | 122.438 | -0.68207 | 122.2961 | -0.50354 | -0.58136 | -0.4715 | 0.49896 | -122.3602 | -122.5662 | 0.61798 | 0.59509 | 0.48065 | 0.096131 | -0.01831 | -0.041199 | -0.022888 | -0.16479 | 0.13733 | 0.16937 | 0.059509 | 0.21057 | 0.10071 | 0.11902 | 0.036621 | 0.17853 | 122.9782 | 0.24262 | 123.1201 | 0.74158 | 123.0789 | -122.6028 | -123.143 | 0.53558 | 122.937 | 0.52185 | 0.86517
482.0156 | 123.1476 | -0.58594 | 122.3877 | -0.20615 | 0.0016449 | 0.019418 | 0.017267 | 0.0039436 | 0.0027644 | 0.0016128 | -0.0013428 | -0.00014097 | 0.0024909 | -0.0051676 | 0.00015167 | -0.0020529 | 0.0011877 | -0.07782 | 0.073242 | -0.10986 | -0.027466 | 0.10071 | -0.068665 | 0.064087 | 0.24719 | 122.4106 | -0.6546 | 122.3923 | -0.3479 | -0.43945 | -0.35706 | 0.47607 | -122.3145 | -122.4152 | 0.68665 | 0.65002 | 0.51727 | 0.17395 | 0.041198 | -0.068665 | 0.022888 | 0.004578 | 0.23804 | 0.22888 | 0.14648 | 0.29755 | 0.21515 | 0.21057 | 0.082397 | 0.3067 | 123.0469 | 0.18311 | 123.0652 | 0.65918 | 122.9965 | -122.4976 | -123.0423 | 0.55847 | 122.9782 | 0.50812 | 0.83313
483.75 | 123.1522 | -0.59052 | 122.4197 | -0.12222 | -0.0013457 | 0.020486 | 0.016413 | -0.0022516 | -0.0015082 | -0.00073695 | 0.078003 | -0.0014228 | 0.0022773 | -0.001536 | 0.0018607 | -0.0063255 | -0.00030754 | -0.10071 | 0.082397 | -0.091553 | -0.013733 | 0.15106 | -0.009155 | 0.09613 | 0.32501 | 122.406 | -0.64545 | 122.4426 | -0.30212 | -0.37079 | -0.33875 | 0.49896 | -122.3373 | -122.4335 | 0.74158 | 0.68664 | 0.58136 | 0.18768 | 0.082398 | -0.054932 | -0.013733 | 0.022888 | 0.28839 | 0.25177 | 0.21973 | 0.3067 | 0.27466 | 0.24261 | 0.07782 | 0.34332 | 123.0881 | 0.17395 | 123.0515 | 0.67291 | 122.9965 | -122.5113 | -123.0652 | 0.57678 | 123.0331 | 0.48981 | 0.91553
485.5 | 123.0331 | -0.63171 | 122.4472 | -0.12985 | -0.0045501 | 0.016855 | 0.017694 | 0.00031198 | 0.0016962 | -0.0018052 | -0.03186 | 0.00028623 | 0.0039861 | 0.00060037 | -0.00027553 | -0.0050437 | -9.3938e-05 | -0.16479 | 0.11902 | -0.13733 | -0.15106 | -0.036621 | -0.15106 | -0.041199 | 0.20599 | 122.4792 | -0.68665 | 122.3053 | -0.45776 | -0.53558 | -0.47607 | 0.49438 | -122.3282 | -122.5983 | 0.59509 | 0.59052 | 0.48065 | 0.09613 | -0.013733 | -0.054932 | 0.032043 | -0.14191 | 0.17395 | 0.15564 | 0.096131 | 0.21057 | 0.15106 | 0.10071 | -0.013733 | 0.22888 | 122.9919 | 0.25635 | 123.1659 | 0.75073 | 123.111 | -122.5845 | -123.1339 | 0.48065 | 122.937 | 0.46692 | 0.83771
487.2344 | 123.0927 | -0.59509 | 122.4197 | -0.12985 | -0.0039093 | 0.019632 | 0.015985 | -0.003747 | 0.0019098 | -0.001378 | 0.065796 | -0.00035457 | 0.0012091 | -0.0019632 | 0.00036527 | -0.0046165 | 0.0014015 | -0.14191 | 0.09613 | -0.09613 | -0.07782 | 0.036621 | -0.10071 | 0.027466 | 0.17395 | 122.438 | -0.66834 | 122.3648 | -0.37537 | -0.45776 | -0.38452 | 0.49896 | -122.3236 | -122.4976 | 0.63171 | 0.62256 | 0.49438 | 0.1236 | -0.004578 | -0.073242 | 0.01831 | -0.054932 | 0.21973 | 0.21057 | 0.13733 | 0.28381 | 0.21057 | 0.13275 | 0.01831 | 0.29297 | 123.0331 | 0.19226 | 123.1064 | 0.69122 | 123.0331 | -122.5159 | -123.0881 | 0.51727 | 122.9599 | 0.45319 | 0.76904
488.9062 | 123.0972 | -0.56763 | 122.4655 | -0.16037 | -0.0019867 | 0.019418 | 0.017053 | 0.00052558 | 0.00062799 | -0.0018052 | 0.050537 | 0.00049983 | -0.00049987 | -0.00025423 | -0.00070273 | -0.0033347 | -9.3938e-05 | -0.13733 | 0.09613 | -0.10986 | -0.086975 | 0.032043 | -0.091553 | 0.027466 | 0.18768 | 122.4747 | -0.61798 | 122.406 | -0.32959 | -0.3891 | -0.33875 | 0.45776 | -122.3694 | -122.5525 | 0.59967 | 0.59509 | 0.47607 | 0.13733 | 0.01831 | -0.050354 | 0.009155 | -0.059509 | 0.23804 | 0.22888 | 0.17853 | 0.27924 | 0.22888 | 0.14191 | 0.022888 | 0.28839 | 123.024 | 0.20599 | 123.0927 | 0.66376 | 123.0423 | -122.5754 | -123.0835 | 0.48065 | 122.9736 | 0.4303 | 0.75531
490.6406 | 123.0743 | -0.54932 | 122.4701 | -0.17563 | -0.0032683 | 0.017068 | 0.016199 | -0.00054262 | 0.0019098 | -0.00095055 | 0.016968 | 0.00028623 | 0.00014093 | -0.0051676 | -0.0019845 | -0.0026939 | -0.0047937 | -0.13275 | 0.091553 | -0.11444 | -0.091553 | 0.032043 | -0.09613 | 0.027466 | 0.16479 | 122.4655 | -0.61798 | 122.3969 | -0.32959 | -0.40741 | -0.34332 | 0.43488 | -122.3785 | -122.5616 | 0.58136 | 0.57678 | 0.45319 | 0.14191 | 0.018311 | -0.068665 | -0.004578 | -0.073242 | 0.21973 | 0.20599 | 0.14191 | 0.27466 | 0.21057 | 0.14648 | 0.022888 | 0.28839 | 123.0148 | 0.20599 | 123.0835 | 0.64087 | 123.0148 | -122.5845 | -123.0881 | 0.45776 | 122.9462 | 0.41657 | 0.71411
492.375 | 123.1155 | -0.54474 | 122.4472 | -0.11459 | 0.00014946 | 0.0207 | 0.017267 | 0.0022346 | -0.00022641 | 0.00054465 | -0.068481 | 0.002636 | 0.00078193 | 0.0014548 | -0.0013437 | -0.0022665 | -0.00094854 | -0.14191 | 0.11902 | -0.1236 | -0.11444 | 0 | -0.16022 | -0.027466 | 0.20599 | 122.4884 | -0.61798 | 122.4289 | -0.33417 | -0.42572 | -0.31586 | 0.42114 | -122.3282 | -122.5616 | 0.54474 | 0.51727 | 0.38452 | 0.09613 | -0.036621 | -0.073242 | 0.041198 | -0.018311 | 0.21057 | 0.22888 | 0.11902 | 0.30212 | 0.19226 | 0.1236 | 0.009155 | 0.28381 | 123.0469 | 0.24261 | 123.1064 | 0.66376 | 123.0331 | -122.5708 | -123.0652 | 0.4303 | 122.9736 | 0.40283 | 0.75073
494.0469 | 123.0423 | -0.56305 | 122.5113 | -0.18326 | -0.0013457 | 0.020059 | 0.018976 | 9.818e-05 | 0.002978 | 0.00033105 | -0.068481 | 0.0013544 | 0.00056833 | 0.0042318 | -0.0024117 | -0.0016257 | 0.0018287 | -0.10986 | 0.11444 | -0.12817 | -0.073242 | 0.018311 | -0.11444 | -0.013733 | 0.28839 | 122.5113 | -0.63171 | 122.3969 | -0.37994 | -0.46692 | -0.3891 | 0.43488 | -122.3969 | -122.5845 | 0.58136 | 0.54932 | 0.44861 | 0.11444 | 0.013733 | -0.068665 | 0 | -0.11444 | 0.18311 | 0.17395 | 0.09613 | 0.24262 | 0.1648 | 0.14649 | 0.054932 | 0.25177 | 123.0286 | 0.24262 | 123.143 | 0.67749 | 123.0743 | -122.6395 | -123.143 | 0.48981 | 122.9599 | 0.45319 | 0.85144
495.7812 | 123.0377 | -0.59052 | 122.5159 | -0.061188 | -0.0034821 | 0.017496 | 0.017267 | -0.0024652 | 0.00084159 | 0.002681 | -0.01355 | 0.0030634 | -0.00028627 | 0.00038657 | 0.0014335 | -0.0050437 | -0.0015893 | -0.15564 | 0.13275 | -0.12817 | -0.15106 | -0.041199 | -0.15106 | -0.036621 | 0.20599 | 122.5342 | -0.64087 | 122.3648 | -0.37994 | -0.48065 | -0.39368 | 0.46234 | -122.3831 | -122.6669 | 0.54932 | 0.55389 | 0.43945 | 0.091553 | -0.022888 | -0.050354 | 0.018311 | -0.15106 | 0.21057 | 0.19684 | 0.10986 | 0.24719 | 0.16022 | 0.086975 | -0.022888 | 0.26093 | 123.0057 | 0.26093 | 123.175 | 0.72327 | 123.1247 | -122.644 | -123.1567 | 0.43945 | 122.9553 | 0.43488 | 0.79651
497.5156 | 123.0103 | -0.57678 | 122.525 | -0.091705 | -0.0022003 | 0.017496 | 0.015985 | -0.0011834 | -0.00044001 | 0.0016128 | 0.013916 | 0.0013544 | 0.0016363 | 0.003591 | -6.1934e-05 | -0.0029075 | -0.00052114 | -0.18768 | 0.13275 | -0.16022 | -0.15106 | -0.027466 | -0.15106 | -0.041199 | 0.21057 | 122.5525 | -0.63629 | 122.3465 | -0.38452 | -0.48065 | -0.41199 | 0.41657 | -122.3923 | -122.6761 | 0.54932 | 0.53558 | 0.42572 | 0.11902 | 0.009155 | -0.05951 | 0.027466 | -0.17853 | 0.19226 | 0.1648 | 0.09613 | 0.2243 | 0.15564 | 0.13275 | 0.009155 | 0.25177 | 122.9828 | 0.29297 | 123.1888 | 0.70953 | 123.1293 | -122.6852 | -123.1613 | 0.42572 | 122.9233 | 0.3891 | 0.78735
499.1875 | 123.1659 | -0.49896 | 122.4976 | -0.15274 | -0.0049773 | 0.016641 | 0.013635 | -0.00096982 | 0.0027644 | -0.00052335 | 0.035278 | -0.0012092 | 0.0022773 | -0.0049538 | 0.0016471 | -0.0037619 | -0.0043665 | -0.10071 | 0.09613 | -0.10986 | -0.018311 | 0.12817 | -0.013733 | 0.091553 | 0.32044 | 122.5021 | -0.56763 | 122.5159 | -0.21057 | -0.32044 | -0.25177 | 0.3891 | -122.4014 | -122.5159 | 0.62714 | 0.59052 | 0.48523 | 0.20142 | 0.09613 | -0.068665 | 0.004577 | 0.01831 | 0.28839 | 0.24719 | 0.17853 | 0.31586 | 0.24719 | 0.23804 | 0.091552 | 0.35706 | 123.0835 | 0.20599 | 123.0698 | 0.59509 | 123.0011 | -122.6074 | -123.0652 | 0.48065 | 123.0148 | 0.39825 | 0.8194
500.9219 | 122.9965 | -0.54932 | 122.5388 | -0.19089 | -0.00049134 | 0.018777 | 0.018549 | 0.0026618 | 0.00041439 | 0.003749 | -0.080688 | 0.0022088 | 0.0022773 | 0.003591 | -0.0013437 | -0.0011985 | -0.0028711 | -0.15564 | 0.11902 | -0.13275 | -0.15564 | -0.068665 | -0.20599 | -0.091553 | 0.13275 | 122.5479 | -0.60883 | 122.3785 | -0.39825 | -0.48981 | -0.37994 | 0.41657 | -122.4197 | -122.6944 | 0.48065 | 0.45776 | 0.34332 | 0.041198 | -0.073243 | -0.05951 | 0.009156 | -0.16022 | 0.15106 | 0.16937 | 0.059509 | 0.22888 | 0.11902 | 0.064086 | -0.022889 | 0.21057 | 122.9874 | 0.25177 | 123.1567 | 0.66834 | 123.0972 | -122.6715 | -123.1476 | 0.39368 | 122.9279 | 0.39368 | 0.68207
502.6094 | 123.0148 | -0.59052 | 122.4792 | -0.17563 | -0.0015595 | 0.021555 | 0.019831 | -0.0016106 | 0.002978 | -0.00095055 | -0.053223 | 0.0011408 | 0.0018499 | 0.0033774 | -0.0011301 | -0.0024803 | -0.0030847 | -0.16937 | 0.13733 | -0.14191 | -0.15564 | -0.068665 | -0.19226 | -0.07782 | 0.15106 | 122.5021 | -0.65918 | 122.3373 | -0.44861 | -0.54016 | -0.42572 | 0.44861 | -122.3419 | -122.6349 | 0.52185 | 0.5127 | 0.39825 | 0.064087 | -0.050354 | -0.068665 | 0.022888 | -0.14191 | 0.14191 | 0.1648 | 0.050354 | 0.23346 | 0.11902 | 0.073242 | -0.013733 | 0.21057 | 122.9965 | 0.27924 | 123.1613 | 0.72784 | 123.0927 | -122.6212 | -123.1384 | 0.43488 | 122.9279 | 0.42114 | 0.74158
504.3438 | 123.1384 | -0.55389 | 122.4426 | -0.18326 | 0.00014946 | 0.021555 | 0.016199 | 0.0041572 | -0.00022641 | -0.00030975 | 0.0078126 | 0.00092703 | 0.0014227 | 0.001882 | 0.00079247 | -0.0035483 | -0.00094854 | -0.073242 | 0.091553 | -0.086975 | -0.032043 | 0.09613 | -0.073242 | 0.064087 | 0.25635 | 122.4518 | -0.60425 | 122.4518 | -0.27466 | -0.37537 | -0.29297 | 0.46692 | -122.3511 | -122.4747 | 0.65002 | 0.61798 | 0.48065 | 0.15106 | 0.013733 | -0.050354 | 0.009155 | 0.009155 | 0.27924 | 0.26093 | 0.17853 | 0.31128 | 0.22888 | 0.1831 | 0.054932 | 0.32959 | 123.056 | 0.17853 | 123.056 | 0.64545 | 123.0057 | -122.5296 | -123.0469 | 0.52185 | 123.0057 | 0.48065 | 0.81024
506.0156 | 123.0835 | -0.19684 | 122.8363 | -0.13748 | -0.0019867 | 0.019418 | 0.014704 | 0.0022346 | 0.0025506 | -9.6154e-05 | 0.056641 | 0.0017816 | 0.0037725 | 0.00060037 | -0.00070273 | -0.0044029 | 0.0016151 | -0.15106 | 0.082397 | -0.11444 | -0.086975 | 0.045776 | -0.091553 | 0.027466 | 0.16937 | 122.8363 | -0.27008 | 122.7722 | 0.027466 | -0.054932 | 0.013733 | 0.082397 | -122.7539 | -122.9233 | 0.24261 | 0.2243 | 0.10529 | 0.14191 | 0.022888 | -0.073243 | 0 | -0.064087 | 0.2243 | 0.21057 | 0.14191 | 0.28381 | 0.21515 | 0.16022 | 0.027466 | 0.29755 | 123.0423 | 0.19684 | 123.1064 | 0.27924 | 123.0331 | -122.9507 | -123.1064 | 0.10986 | 122.9691 | 0.045776 | 0.36621
507.75 | 123.0606 | -0.13733 | 122.9141 | -0.12222 | -0.0015595 | 0.020914 | 0.020044 | 0.00095278 | 0.00020079 | 0.0011856 | -0.068481 | 7.2626e-05 | 0.0014227 | 0.010854 | 0.00057887 | -0.0022665 | 0.00076046 | -0.10986 | 0.10986 | -0.13275 | -0.086975 | 0.032043 | -0.10986 | -0.009155 | 0.29297 | 122.9095 | -0.20599 | 122.8088 | 0.036621 | -0.050354 | 0.059509 | 0.004578 | -122.8043 | -123.0011 | 0.16937 | 0.12817 | 0.027466 | 0.1236 | 0.022888 | -0.068665 | -0.004578 | -0.10529 | 0.17395 | 0.19684 | 0.086975 | 0.2655 | 0.15564 | 0.16479 | 0.045776 | 0.24262 | 123.0148 | 0.24261 | 123.1155 | 0.24719 | 123.0469 | -123.0469 | -123.1201 | 0.050354 | 122.9462 | 0.027466 | 0.4303
509.4219 | 123.0057 | -0.16479 | 122.9416 | -0.16037 | 0.00014946 | 0.018564 | 0.01919 | 0.00073918 | 0.0036188 | -0.0011642 | -0.037964 | 0.0017816 | -0.00049987 | -0.0049538 | 0.00036527 | -0.0031211 | -0.0013757 | -0.14648 | 0.10986 | -0.12817 | -0.13733 | -0.013733 | -0.17395 | -0.054932 | 0.20142 | 122.9553 | -0.20142 | 122.7951 | 0 | -0.091553 | 0.004578 | 0.036621 | -122.8317 | -123.0789 | 0.15106 | 0.10986 | -0.009155 | 0.073242 | -0.045776 | -0.036621 | 0.013733 | -0.14648 | 0.16479 | 0.16937 | 0.073242 | 0.20599 | 0.10986 | 0.11444 | -0.009155 | 0.20142 | 122.9965 | 0.23804 | 123.1567 | 0.27466 | 123.1201 | -123.0698 | -123.143 | 0.027466 | 122.9599 | 0.018311 | 0.36621
511.1562 | 123.0011 | -0.16937 | 122.9462 | -0.099335 | -0.0032683 | 0.018777 | 0.017694 | 0.0054388 | -0.001081 | 0.00033105 | 0.023071 | 0.0022088 | 0.0012091 | -4.063e-05 | -0.00070273 | -0.0020529 | 0.00011966 | -0.19684 | 0.11444 | -0.1236 | -0.14191 | -0.022888 | -0.14191 | -0.036621 | 0.21057 | 122.9507 | -0.21515 | 122.7676 | 0.027466 | -0.064087 | -0.018311 | 0.045777 | -122.8317 | -123.0881 | 0.14649 | 0.13275 | 0.027466 | 0.086975 | -0.018311 | -0.045776 | 0.004578 | -0.17853 | 0.19684 | 0.15106 | 0.10529 | 0.19684 | 0.15106 | 0.10071 | -0.018311 | 0.24261 | 122.9828 | 0.23804 | 123.1659 | 0.28381 | 123.1201 | -123.0698 | -123.1613 | 0.027466 | 122.937 | -0.027465 | 0.37994
512.8438 | 123.0377 | -0.16479 | 122.9004 | -0.10696 | -0.0032683 | 0.018564 | 0.017694 | 0.0018072 | -0.00044001 | 0.0011856 | 0.013916 | 7.2626e-05 | 0.00099553 | -0.0038858 | -0.00027553 | -0.0035483 | -0.0060753 | -0.16022 | 0.12817 | -0.13733 | -0.15106 | -0.045776 | -0.14191 | -0.041199 | 0.21973 | 122.937 | -0.2243 | 122.7814 | 0.022888 | -0.064087 | 0.004578 | 0.027466 | -122.7722 | -123.0515 | 0.11902 | 0.1236 | 0.022888 | 0.09613 | -0.004578 | -0.059509 | 0.036621 | -0.11902 | 0.18768 | 0.16937 | 0.10071 | 0.22888 | 0.16022 | 0.091553 | -0.013733 | 0.24719 | 123.0057 | 0.2655 | 123.1613 | 0.29297 | 123.1018 | -123.0377 | -123.1247 | 0.013733 | 122.9462 | 0.004578 | 0.38452
514.5781 | 123.0331 | -0.16479 | 122.8867 | -0.15274 | -0.0028411 | 0.017068 | 0.013635 | 0.0011664 | 0.0016962 | 0.0011856 | 0.053589 | 0.00028623 | 0.0012091 | -0.0036722 | 0.0016471 | -0.0033347 | -0.0043665 | -0.11444 | 0.091553 | -0.11444 | -0.086975 | 0.041199 | -0.07782 | 0.018311 | 0.26093 | 122.9004 | -0.21057 | 122.7768 | 0.022888 | -0.041199 | 0.013733 | 0.050354 | -122.7951 | -122.9736 | 0.20599 | 0.18311 | 0.086975 | 0.13275 | 0.036621 | -0.045776 | 0.013733 | -0.10986 | 0.18768 | 0.17853 | 0.1236 | 0.2243 | 0.16937 | 0.15564 | 0.027466 | 0.23346 | 122.9874 | 0.20599 | 123.111 | 0.25635 | 123.0652 | -123.0011 | -123.0972 | 0.07782 | 122.9416 | 0.050354 | 0.42572
516.25 | 123.0011 | -0.17853 | 122.9324 | -0.15274 | -0.0028411 | 0.020914 | 0.019617 | 0.0028754 | 0.0016962 | -0.0030868 | -0.034912 | 0.0019952 | 0.00056833 | 0.001882 | -0.00027553 | -0.0022665 | 0.0016151 | -0.13733 | 0.11444 | -0.13275 | -0.13733 | -0.041199 | -0.18768 | -0.082397 | 0.16479 | 122.9324 | -0.24261 | 122.7493 | -0.050354 | -0.11444 | -0.013733 | 0.045777 | -122.818 | -123.0698 | 0.13733 | 0.096131 | -0.009155 | 0.050354 | -0.054932 | -0.064087 | 0 | -0.1831 | 0.12817 | 0.16479 | 0.064087 | 0.22888 | 0.12817 | 0.091552 | -0.004578 | 0.19226 | 122.9919 | 0.24719 | 123.175 | 0.29297 | 123.111 | -123.0652 | -123.175 | 0.041199 | 122.9279 | 0.041199 | 0.34332
517.9844 | 123.111 | -0.15564 | 122.8867 | -0.22141 | -0.0049773 | 0.018777 | 0.015772 | -0.0018244 | 0.0010554 | -0.0011642 | 0.09021 | -0.00056817 | -0.00049987 | -0.0045266 | 0.0010061 | -0.0039755 | -9.3938e-05 | -0.12817 | 0.091553 | -0.11444 | -0.09613 | 0.036621 | -0.10071 | 0.022888 | 0.17395 | 122.8729 | -0.2243 | 122.8226 | 0.082397 | 0.018311 | 0.068665 | 0.041199 | -122.7951 | -122.9828 | 0.19226 | 0.17853 | 0.054932 | 0.13733 | 0.013733 | -0.068664 | -0.013733 | -0.064087 | 0.23804 | 0.22431 | 0.17395 | 0.29297 | 0.24261 | 0.15106 | 0.018311 | 0.3067 | 123.0469 | 0.20599 | 123.0972 | 0.24719 | 123.0286 | -123.0011 | -123.111 | 0.05951 | 122.9782 | 0.027466 | 0.32959
519.6562 | 123.1476 | -0.13733 | 122.8729 | -0.21378 | -0.0015595 | 0.021341 | 0.018122 | 0.0041572 | 0.001269 | 0.00033105 | 0.0078126 | -0.00056817 | 0.00014093 | 0.0033774 | -0.00070273 | -0.0029075 | -0.00052114 | -0.073242 | 0.086975 | -0.09613 | -0.027466 | 0.091553 | -0.059509 | 0.045776 | 0.27466 | 122.8958 | -0.18768 | 122.8729 | 0.1236 | 0.036621 | 0.13275 | 0.041199 | -122.7859 | -122.9004 | 0.22888 | 0.18311 | 0.07782 | 0.14191 | 0.036621 | -0.050354 | 0.022888 | 0 | 0.26093 | 0.27008 | 0.17395 | 0.32043 | 0.2243 | 0.18768 | 0.068664 | 0.31128 | 123.0606 | 0.1831 | 123.0835 | 0.2243 | 123.0331 | -122.9691 | -123.0606 | 0.10986 | 123.0103 | 0.064087 | 0.41199
521.3906 | 123.1064 | -0.21057 | 122.8134 | -0.16037 | -0.0049773 | 0.017709 | 0.017053 | -0.001397 | -0.00044001 | 0.00011745 | 0.053589 | -0.00056817 | 0.0033453 | -0.0034586 | 0.00057887 | -0.0024803 | -9.3938e-05 | -0.10071 | 0.082397 | -0.11902 | -0.032043 | 0.091553 | -0.018311 | 0.064087 | 0.29297 | 122.8226 | -0.27466 | 122.7768 | 0.032043 | -0.041199 | 0.009155 | 0.091552 | -122.731 | -122.8455 | 0.30212 | 0.27466 | 0.19226 | 0.18311 | 0.10071 | -0.064087 | 0.009155 | -0.036622 | 0.24261 | 0.21973 | 0.16937 | 0.28381 | 0.23346 | 0.21057 | 0.086976 | 0.3067 | 123.0515 | 0.20142 | 123.0972 | 0.29297 | 123.0331 | -122.9324 | -123.0881 | 0.17853 | 122.9874 | 0.10986 | 0.50354
523.1406 | 123.1338 | -0.3891 | 122.6303 | -0.13748 | -0.0041229 | 0.018777 | 0.015344 | -0.0016106 | 0.00041439 | 0.0018264 | 0.062744 | 0.00049983 | -0.00049987 | -0.003245 | -6.1934e-05 | -0.0037619 | -0.0028711 | -0.10071 | 0.073242 | -0.10071 | -0.027466 | 0.13733 | -0.013733 | 0.07782 | 0.31586 | 122.6212 | -0.45776 | 122.6074 | -0.11444 | -0.20142 | -0.15564 | 0.28839 | -122.5571 | -122.6578 | 0.52643 | 0.46692 | 0.37537 | 0.17853 | 0.086975 | -0.068665 | -0.009155 | -0.022888 | 0.27466 | 0.23346 | 0.18768 | 0.30212 | 0.25635 | 0.23804 | 0.073242 | 0.34332 | 123.0652 | 0.17395 | 123.0789 | 0.46234 | 123.0103 | -122.731 | -123.0881 | 0.36163 | 122.9965 | 0.28839 | 0.70496
524.8281 | 123.1293 | -0.40741 | 122.5433 | -0.16037 | -6.4144e-05 | 0.021341 | 0.018335 | 0.00052558 | 0.0044732 | -0.0028732 | -0.019653 | 7.2626e-05 | 0.00014093 | 0.0020956 | -0.0011301 | -0.0029075 | -0.0028711 | -0.073242 | 0.082397 | -0.09613 | -0.022888 | 0.082397 | -0.064087 | 0.045776 | 0.27008 | 122.5845 | -0.49439 | 122.6028 | -0.16937 | -0.26093 | -0.16479 | 0.31128 | -122.4609 | -122.5662 | 0.48981 | 0.45319 | 0.34332 | 0.14191 | 0.032043 | -0.086975 | 0.041199 | 0.059509 | 0.23804 | 0.24261 | 0.14648 | 0.32959 | 0.23346 | 0.17853 | 0.073242 | 0.32501 | 123.0972 | 0.17853 | 123.0789 | 0.48981 | 122.9919 | -122.6395 | -123.0377 | 0.38452 | 123.0103 | 0.33417 | 0.67749
526.5625 | 123.1384 | -0.37537 | 122.5845 | -0.18326 | -0.00070494 | 0.021555 | 0.017694 | 0.0028754 | 0.00084159 | 0.00054465 | 0.016968 | 0.0011408 | 0.00099553 | 0.0072226 | 0.0014335 | -0.0024803 | 0.00076046 | -0.07782 | 0.07782 | -0.07782 | -0.018311 | 0.10529 | -0.064087 | 0.054932 | 0.26093 | 122.6028 | -0.45319 | 122.6212 | -0.16022 | -0.23804 | -0.14648 | 0.29755 | -122.5067 | -122.6028 | 0.48065 | 0.4303 | 0.31128 | 0.13275 | 0.013733 | -0.07782 | 0.01831 | 0.036621 | 0.21515 | 0.22888 | 0.13733 | 0.3067 | 0.21515 | 0.18311 | 0.059509 | 0.29297 | 123.0743 | 0.15564 | 123.056 | 0.45319 | 122.9782 | -122.6624 | -123.0377 | 0.35705 | 122.9965 | 0.29755 | 0.63629
528.2969 | 123.056 | -0.39825 | 122.6532 | -0.14511 | -0.0019867 | 0.021982 | 0.018976 | 9.818e-05 | 0.001269 | 0.00075845 | -0.044067 | 0.0030634 | 0.00056833 | -0.0019632 | -0.00027553 | -0.0016257 | -0.0024439 | -0.10529 | 0.11444 | -0.12817 | -0.09613 | 0.022888 | -0.11444 | -0.004578 | 0.28839 | 122.6715 | -0.46692 | 122.5891 | -0.21057 | -0.29755 | -0.20599 | 0.27008 | -122.5388 | -122.7493 | 0.42114 | 0.39368 | 0.28381 | 0.1236 | 0.013733 | -0.068665 | 0.018311 | -0.064087 | 0.18768 | 0.19226 | 0.10071 | 0.26092 | 0.16937 | 0.15106 | 0.032044 | 0.25635 | 123.056 | 0.24262 | 123.1384 | 0.5127 | 123.0698 | -122.7814 | -123.1201 | 0.30212 | 122.9874 | 0.29297 | 0.68664
529.9688 | 123.0331 | -0.58594 | 122.4976 | -0.053558 | -0.0024139 | 0.018777 | 0.015985 | -0.0018244 | 0.001269 | -9.6154e-05 | -0.019653 | 0.001568 | -0.00049987 | -0.0021768 | 0.00015167 | -0.0033347 | -0.0030847 | -0.16937 | 0.10986 | -0.1236 | -0.16022 | -0.045776 | -0.16937 | -0.036621 | 0.20599 | 122.5113 | -0.64545 | 122.3465 | -0.40283 | -0.48981 | -0.42572 | 0.46234 | -122.3877 | -122.6578 | 0.54016 | 0.54932 | 0.41656 | 0.086975 | -0.045777 | -0.05951 | 0.013733 | -0.15106 | 0.18311 | 0.16022 | 0.09613 | 0.21973 | 0.15564 | 0.07782 | -0.036621 | 0.24261 | 122.9919 | 0.23346 | 123.1567 | 0.6958 | 123.0972 | -122.6212 | -123.143 | 0.42572 | 122.9324 | 0.41656 | 0.79193
531.7031 | 123.0743 | -0.55847 | 122.4792 | -0.14511 | -0.0019867 | 0.020273 | 0.018122 | 0.0024482 | -0.00065361 | 0.0022536 | -0.041016 | 0.001568 | -0.0013543 | -0.0034586 | -0.00070273 | -0.0033347 | 0.0016151 | -0.11902 | 0.10529 | -0.13275 | -0.082397 | 0.036621 | -0.1236 | -0.004578 | 0.29297 | 122.493 | -0.60883 | 122.4152 | -0.35248 | -0.44403 | -0.35706 | 0.42572 | -122.374 | -122.5616 | 0.59509 | 0.55389 | 0.43488 | 0.12817 | 0.009155 | -0.050354 | 0.013733 | -0.064087 | 0.20599 | 0.20142 | 0.11444 | 0.25177 | 0.16479 | 0.16937 | 0.050354 | 0.25635 | 123.024 | 0.23804 | 123.1018 | 0.66376 | 123.0515 | -122.612 | -123.0881 | 0.47607 | 122.9736 | 0.43945 | 0.85144
533.375 | 123.0469 | -0.54932 | 122.5067 | -0.099335 | -0.0043365 | 0.017282 | 0.017053 | -0.0018244 | -0.001081 | -0.00030975 | 0.0078126 | 0.0024224 | 0.00056833 | -0.0011086 | 0.00057887 | -0.0026939 | -0.0020165 | -0.16937 | 0.11444 | -0.13275 | -0.16022 | -0.036621 | -0.13275 | -0.045776 | 0.21515 | 122.5388 | -0.63629 | 122.3877 | -0.37537 | -0.45776 | -0.40283 | 0.41657 | -122.3923 | -122.6669 | 0.5127 | 0.50354 | 0.41657 | 0.086975 | 0 | -0.086976 | 0.032043 | -0.11902 | 0.17395 | 0.14648 | 0.091552 | 0.23346 | 0.17853 | 0.09613 | -0.027466 | 0.26093 | 123.024 | 0.24719 | 123.175 | 0.66376 | 123.0881 | -122.6395 | -123.143 | 0.3891 | 122.937 | 0.37994 | 0.76447
535.1094 | 123.1384 | -0.53558 | 122.4426 | -0.14511 | -0.0043365 | 0.018564 | 0.012781 | 9.818e-05 | 0.0027644 | 0.0013992 | 0.071899 | 0.0011408 | 0.00035453 | -0.0028176 | -0.00048913 | -0.0050437 | 0.00076046 | -0.086975 | 0.086975 | -0.09613 | -0.027466 | 0.1236 | -0.018311 | 0.07782 | 0.33417 | 122.4838 | -0.59052 | 122.4701 | -0.23804 | -0.33417 | -0.29297 | 0.43945 | -122.3557 | -122.4701 | 0.65918 | 0.6134 | 0.51727 | 0.17395 | 0.077819 | -0.054932 | 0.041199 | 0.027466 | 0.29755 | 0.24261 | 0.20142 | 0.29755 | 0.25635 | 0.21973 | 0.068664 | 0.35248 | 123.0606 | 0.1831 | 123.0743 | 0.62256 | 123.0194 | -122.5388 | -123.0331 | 0.50812 | 123.0057 | 0.44861 | 0.86975
536.8125 | 123.1384 | -0.52643 | 122.4609 | -0.17563 | -0.0022003 | 0.017282 | 0.015131 | -0.00075622 | 0.00041439 | -0.00073695 | 0.062744 | -0.00035457 | 0.00035453 | -0.0017496 | 0.0020743 | -0.0029075 | -0.0018029 | -0.15564 | 0.086975 | -0.10529 | -0.07782 | 0.036621 | -0.073242 | 0.041199 | 0.21057 | 122.5021 | -0.62256 | 122.4335 | -0.29297 | -0.36621 | -0.31128 | 0.42114 | -122.374 | -122.5388 | 0.56305 | 0.56763 | 0.45319 | 0.14649 | 0.032044 | -0.096131 | 0.041199 | -0.027465 | 0.23346 | 0.21515 | 0.16022 | 0.31128 | 0.25635 | 0.14191 | 0.027466 | 0.32959 | 123.056 | 0.19226 | 123.1247 | 0.6134 | 123.0286 | -122.5662 | -123.0835 | 0.44861 | 122.9599 | 0.37079 | 0.737
538.5469 | 123.0881 | -0.54932 | 122.4838 | -0.17563 | -0.0041229 | 0.018777 | 0.012567 | -0.003747 | -0.0019354 | 0.00204 | 0.047485 | 0.00028623 | -0.0011407 | -0.0040994 | -0.0019845 | -0.0037619 | -0.00030754 | -0.10529 | 0.082397 | -0.07782 | -0.027466 | 0.086975 | -0.018311 | 0.059509 | 0.3067 | 122.4884 | -0.60883 | 122.4289 | -0.3067 | -0.38452 | -0.33417 | 0.4715 | -122.4014 | -122.5113 | 0.63629 | 0.60883 | 0.53101 | 0.13733 | 0.059509 | -0.05951 | 0.004577 | -0.054932 | 0.24261 | 0.21515 | 0.1648 | 0.27466 | 0.2243 | 0.16479 | 0.050354 | 0.30212 | 123.0377 | 0.16022 | 123.0972 | 0.63171 | 123.0377 | -122.5616 | -123.0927 | 0.52185 | 122.9782 | 0.44403 | 0.85602
540.2812 | 123.024 | -0.57678 | 122.4884 | -0.10696 | 0.0014313 | 0.01835 | 0.018549 | -0.0018244 | 0.0019098 | 0.0011856 | -0.06543 | 0.001568 | 0.0027045 | 0.0029502 | 0.00079247 | -0.0029075 | 0.00054686 | -0.11444 | 0.10529 | -0.1236 | -0.11444 | 0 | -0.13733 | -0.032043 | 0.24719 | 122.5296 | -0.62256 | 122.3923 | -0.41199 | -0.50354 | -0.39368 | 0.45319 | -122.3831 | -122.6028 | 0.57678 | 0.54474 | 0.43945 | 0.091553 | -0.013733 | -0.045777 | 0.041199 | -0.09613 | 0.1648 | 0.18311 | 0.073242 | 0.22888 | 0.11902 | 0.1236 | 0.009155 | 0.21057 | 123.0148 | 0.22888 | 123.1522 | 0.68207 | 123.1064 | -122.612 | -123.111 | 0.46234 | 122.9691 | 0.46234 | 0.82397
541.9531 | 123.0972 | -0.54016 | 122.4792 | -0.10696 | -0.0022003 | 0.018777 | 0.01449 | 0.00073918 | 0.0014826 | 0.0018264 | 0.078003 | 0.00028623 | 0.0018499 | -0.0045266 | -0.00070273 | -0.0018393 | -0.00094854 | -0.14191 | 0.07782 | -0.10986 | -0.082397 | 0.022888 | -0.10529 | 0.013733 | 0.19226 | 122.4838 | -0.59967 | 122.406 | -0.31586 | -0.37994 | -0.33417 | 0.4303 | -122.4014 | -122.5616 | 0.56305 | 0.55389 | 0.43488 | 0.1236 | 0.004577 | -0.059509 | 0.004578 | -0.073242 | 0.2243 | 0.20599 | 0.16022 | 0.2655 | 0.21973 | 0.13275 | 0.027466 | 0.28381 | 123.0057 | 0.18768 | 123.0835 | 0.61798 | 123.024 | -122.5891 | -123.0789 | 0.45776 | 122.9462 | 0.39825 | 0.73242
543.6875 | 123.0423 | -0.60883 | 122.493 | -0.084076 | -0.0015595 | 0.017282 | 0.018762 | -0.00096982 | 0.00062799 | -0.00052335 | -0.019653 | 0.003277 | 0.0027045 | 0.0059408 | 0.0025015 | -0.0022665 | 0.0026831 | -0.16479 | 0.11902 | -0.15106 | -0.14648 | -0.050354 | -0.14191 | -0.027466 | 0.21057 | 122.5067 | -0.66376 | 122.3328 | -0.41657 | -0.52643 | -0.42572 | 0.45776 | -122.374 | -122.6395 | 0.55847 | 0.58136 | 0.46692 | 0.1236 | 0.009155 | -0.054931 | 0.013733 | -0.16022 | 0.19226 | 0.18311 | 0.082398 | 0.23804 | 0.13733 | 0.10071 | 0.004578 | 0.24719 | 122.9965 | 0.27008 | 123.1705 | 0.72784 | 123.1155 | -122.644 | -123.1567 | 0.46234 | 122.9416 | 0.44403 | 0.8194
545.3594 | 123.0606 | -0.58136 | 122.5067 | -0.10696 | -6.4144e-05 | 0.016214 | 0.018335 | 0.00138 | 0.00041439 | 0.0018264 | -0.041016 | 0.0022088 | -7.2674e-05 | 0.00038657 | -0.00070273 | -0.0029075 | -0.0015893 | -0.11902 | 0.09613 | -0.11902 | -0.082397 | 0.036621 | -0.10986 | -0.009155 | 0.30212 | 122.4747 | -0.6546 | 122.3648 | -0.38452 | -0.4715 | -0.3891 | 0.46234 | -122.4106 | -122.5891 | 0.61798 | 0.5722 | 0.4715 | 0.10986 | 0.009156 | -0.073242 | -0.032044 | -0.14191 | 0.19684 | 0.19226 | 0.10986 | 0.2655 | 0.18311 | 0.15564 | 0.036622 | 0.27008 | 123.0194 | 0.21515 | 123.1293 | 0.67749 | 123.056 | -122.6257 | -123.1613 | 0.49896 | 122.9462 | 0.46234 | 0.88348
547.0938 | 123.0011 | -0.62256 | 122.4426 | -0.14511 | 0.0010041 | 0.019632 | 0.018762 | 0.0015936 | -1.2808e-05 | 0.0013992 | -0.056274 | 0.00092703 | 0.00099553 | 0.0014548 | 0.00015167 | -0.0022665 | 0.00097406 | -0.14648 | 0.11902 | -0.12817 | -0.15106 | -0.082397 | -0.21057 | -0.073242 | 0.14191 | 122.4884 | -0.67749 | 122.3007 | -0.48523 | -0.56763 | -0.46692 | 0.49438 | -122.3236 | -122.5937 | 0.54016 | 0.54932 | 0.41199 | 0.054932 | -0.082397 | -0.054931 | 0.045776 | -0.14191 | 0.13733 | 0.15564 | 0.054932 | 0.21057 | 0.10986 | 0.045777 | -0.022888 | 0.19226 | 122.9782 | 0.24719 | 123.1659 | 0.74158 | 123.111 | -122.5708 | -123.1201 | 0.4715 | 122.9233 | 0.47607 | 0.76447
548.7656 | 122.9919 | -0.61798 | 122.4884 | -0.091705 | 0.0010041 | 0.020273 | 0.019403 | 0.00138 | 0.0025506 | -0.00052335 | -0.047119 | 0.0013544 | 0.00056833 | 0.0012412 | 0.00036527 | -0.0020529 | -9.3938e-05 | -0.15564 | 0.10986 | -0.11444 | -0.16479 | -0.064087 | -0.19226 | -0.073242 | 0.16022 | 122.4884 | -0.67749 | 122.3053 | -0.48523 | -0.59052 | -0.4715 | 0.50354 | -122.3785 | -122.6532 | 0.55389 | 0.54474 | 0.42572 | 0.041199 | -0.07782 | -0.059509 | 0 | -0.18311 | 0.13275 | 0.14648 | 0.027466 | 0.20599 | 0.086975 | 0.050354 | -0.050354 | 0.19226 | 122.9828 | 0.2243 | 123.1659 | 0.72784 | 123.1064 | -122.6028 | -123.1659 | 0.45319 | 122.9233 | 0.46234 | 0.7782
550.7031 | 123.0469 | -0.65918 | 122.438 | -0.12985 | -0.0019867 | 0.017709 | 0.017267 | 0.0050116 | 0.0016962 | -0.00073695 | -0.025757 | 0.0024224 | 0.00035453 | -0.0090128 | 0.00079247 | -0.0026939 | 0.00011966 | -0.15106 | 0.11444 | -0.14191 | -0.12817 | -0.027466 | -0.14191 | -0.032043 | 0.23804 | 122.4289 | -0.70038 | 122.3007 | -0.44403 | -0.51727 | -0.44403 | 0.51727 | -122.3236 | -122.5662 | 0.63171 | 0.62714 | 0.51727 | 0.10986 | 0 | -0.041198 | -0.009155 | -0.13733 | 0.21515 | 0.21515 | 0.14191 | 0.25635 | 0.1831 | 0.11444 | 0.013733 | 0.25635 | 123.0011 | 0.25635 | 123.1293 | 0.77362 | 123.0881 | -122.58 | -123.1384 | 0.53101 | 122.9599 | 0.50812 | 0.89722
552.4531 | 123.024 | -0.67749 | 122.4197 | -0.099335 | 0.00057686 | 0.01835 | 0.016199 | 0.00031198 | 0.00084159 | -0.0015916 | 0.023071 | -0.00014097 | 0.0035589 | 0.00017297 | 0.0012199 | -0.0037619 | -0.0011621 | -0.17853 | 0.1236 | -0.13275 | -0.17395 | -0.018311 | -0.14648 | -0.022888 | 0.19684 | 122.4335 | -0.72784 | 122.2504 | -0.49896 | -0.5722 | -0.52643 | 0.54474 | -122.2961 | -122.5937 | 0.65918 | 0.6546 | 0.53101 | 0.10986 | -0.013733 | -0.050354 | 0.013733 | -0.16937 | 0.17853 | 0.15106 | 0.10529 | 0.20142 | 0.15564 | 0.11444 | -0.041199 | 0.22888 | 122.9782 | 0.25635 | 123.1613 | 0.80109 | 123.111 | -122.5525 | -123.1476 | 0.50354 | 122.9279 | 0.49896 | 0.87433
554.1875 | 123.0057 | -0.67749 | 122.406 | -0.18326 | -0.0017731 | 0.020273 | 0.017908 | 9.818e-05 | -1.2808e-05 | -9.6154e-05 | -0.025757 | 0.00092703 | 0.0027045 | 0.0038046 | -0.0013437 | -0.00034387 | -0.0015893 | -0.13733 | 0.12817 | -0.12817 | -0.14191 | -0.027466 | -0.1831 | -0.068665 | 0.19684 | 122.4197 | -0.74158 | 122.2595 | -0.53558 | -0.62714 | -0.51727 | 0.54932 | -122.2778 | -122.5479 | 0.65002 | 0.60883 | 0.49439 | 0.059509 | -0.054931 | -0.064087 | 0.013733 | -0.14648 | 0.14191 | 0.16022 | 0.050354 | 0.2243 | 0.11444 | 0.10071 | -0.013733 | 0.20599 | 123.0011 | 0.25635 | 123.1613 | 0.80566 | 123.0972 | -122.5342 | -123.1476 | 0.53558 | 122.937 | 0.54016 | 0.87433
555.9688 | 123.0103 | -0.70038 | 122.3877 | -0.12222 | -0.0019867 | 0.017496 | 0.014063 | 0.00052558 | 0.0010554 | 0.0016128 | 0.044434 | 0.00049983 | -0.00071347 | 0.0016684 | 0.0020743 | -0.0037619 | 0.0016151 | -0.16937 | 0.10986 | -0.15106 | -0.15106 | -0.032043 | -0.14191 | -0.032043 | 0.19684 | 122.4014 | -0.75531 | 122.2046 | -0.52643 | -0.60425 | -0.54932 | 0.54932 | -122.2778 | -122.5388 | 0.66833 | 0.66833 | 0.55847 | 0.11902 | 0.009155 | -0.054932 | 0.013733 | -0.1831 | 0.17395 | 0.15106 | 0.09613 | 0.20599 | 0.15106 | 0.11902 | 0 | 0.22888 | 122.9599 | 0.26093 | 123.1567 | 0.81024 | 123.1018 | -122.5388 | -123.143 | 0.54932 | 122.905 | 0.531 | 0.89722
557.6562 | 123.1796 | -0.65002 | 122.3694 | -0.17563 | -0.0034821 | 0.017709 | 0.015558 | -0.002038 | 0.0010554 | -0.001378 | 0.093262 | 0.00092703 | 0.0033453 | -0.0028176 | -0.00048913 | -0.0058981 | 0.0014015 | -0.10071 | 0.086975 | -0.10071 | -0.054932 | 0.09613 | -0.018311 | 0.082397 | 0.29297 | 122.3557 | -0.70953 | 122.3465 | -0.37537 | -0.45319 | -0.40283 | 0.54932 | -122.2824 | -122.4243 | 0.74615 | 0.73242 | 0.63171 | 0.18311 | 0.082397 | -0.05951 | -0.013733 | -0.022888 | 0.27466 | 0.24719 | 0.19684 | 0.3067 | 0.25635 | 0.19684 | 0.045776 | 0.33417 | 123.056 | 0.18768 | 123.0652 | 0.737 | 123.0057 | -122.4701 | -123.0789 | 0.59509 | 122.9965 | 0.54932 | 0.94299
559.3906 | 123.0286 | -0.74616 | 122.319 | -0.168 | -0.0013457 | 0.018777 | 0.017053 | 0.0022346 | 0.002337 | 0.00075845 | -0.059326 | 0.001568 | 0.00056833 | 0.00017297 | -0.00091653 | -0.0022665 | -0.00094854 | -0.15106 | 0.12817 | -0.12817 | -0.16022 | -0.068665 | -0.18768 | -0.064087 | 0.17395 | 122.3602 | -0.79651 | 122.168 | -0.59509 | -0.70496 | -0.5722 | 0.61798 | -122.1909 | -122.4792 | 0.67749 | 0.68207 | 0.55847 | 0.064087 | -0.059509 | -0.050354 | 0.041198 | -0.15106 | 0.15106 | 0.17395 | 0.041199 | 0.2243 | 0.091553 | 0.059509 | -0.032043 | 0.20142 | 122.9645 | 0.25635 | 123.1567 | 0.87433 | 123.1064 | -122.4472 | -123.1155 | 0.58594 | 122.9141 | 0.59509 | 0.9201
561.1406 | 123.0331 | -0.78735 | 122.3145 | -0.12222 | -0.0026275 | 0.019418 | 0.015344 | -0.0011834 | 0.00020079 | 0.00054465 | 0.02002 | -0.00035457 | 0.0012091 | 0.002523 | 0.0027151 | -0.0041891 | -0.0039391 | -0.19684 | 0.10071 | -0.16022 | -0.17853 | -0.054932 | -0.16022 | -0.041199 | 0.21057 | 122.3419 | -0.84228 | 122.1359 | -0.61798 | -0.67749 | -0.62256 | 0.62714 | -122.2137 | -122.493 | 0.73242 | 0.74616 | 0.62714 | 0.11902 | 0 | -0.054931 | 0.027466 | -0.17853 | 0.16937 | 0.1648 | 0.10986 | 0.21973 | 0.16479 | 0.10528 | -0.018311 | 0.2243 | 122.9782 | 0.26093 | 123.1842 | 0.88806 | 123.1293 | -122.4747 | -123.1567 | 0.60883 | 122.9233 | 0.59052 | 0.99792
562.8125 | 123.0652 | -0.75073 | 122.3099 | -0.14511 | -0.0024139 | 0.016855 | 0.017267 | 0.00031198 | 0.001269 | 0.0018264 | -0.022705 | 0.0028498 | 0.0022773 | 0.0040182 | -0.00070273 | 0.0013651 | -0.00094854 | -0.1236 | 0.13275 | -0.10986 | -0.10529 | 0.004578 | -0.10529 | -0.013733 | 0.30212 | 122.3328 | -0.8194 | 122.2183 | -0.54932 | -0.6546 | -0.55847 | 0.64087 | -122.1771 | -122.4152 | 0.75531 | 0.737 | 0.64545 | 0.09613 | 0.004577 | -0.068665 | 0.022889 | -0.091552 | 0.20142 | 0.19226 | 0.09613 | 0.26093 | 0.1648 | 0.11444 | 0.004577 | 0.27008 | 123.0377 | 0.24261 | 123.1522 | 0.88348 | 123.0835 | -122.4197 | -123.1293 | 0.64545 | 122.9691 | 0.62714 | 1.0529
564.5469 | 123.1064 | -0.71869 | 122.2824 | -0.21378 | -0.0024139 | 0.020059 | 0.015131 | -0.0026788 | 0.001269 | -0.0011642 | 0.078003 | 0.00049983 | 0.0014227 | -0.01179 | -0.0011301 | -0.0037619 | -0.0011621 | -0.15106 | 0.086975 | -0.11444 | -0.082397 | 0.032043 | -0.086975 | 0.027466 | -0.25177 | 122.3145 | -0.7782 | 122.2321 | -0.50812 | -0.59509 | -0.50812 | 0.60425 | -122.1954 | -122.3648 | 0.75073 | 0.74616 | 0.63171 | 0.14191 | 0.027466 | -0.059509 | 0.032043 | -0.050354 | 0.21057 | 0.21057 | 0.1236 | 0.27008 | 0.1831 | 0.14648 | 0.032044 | 0.27008 | 123.0103 | 0.20142 | 123.0927 | 0.80566 | 123.0331 | -122.3969 | -123.0606 | 0.63629 | 122.9507 | 0.56763 | 0.46692
566.2344 | 123.0469 | -0.65002 | 122.4335 | -0.12222 | -0.0034821 | 0.017496 | 0.014917 | -0.00075622 | -0.0012946 | 0.00054465 | 0.053589 | -0.00035457 | 0.00078193 | -0.0017496 | -0.00048913 | -0.0031211 | 0.0035377 | -0.10529 | 0.082397 | -0.10529 | -0.054932 | 0.07782 | -0.059509 | 0.041199 | 0.28839 | 122.4289 | -0.68665 | 122.3053 | -0.43488 | -0.50354 | -0.45776 | 0.54474 | -122.3511 | -122.4884 | 0.72784 | 0.69122 | 0.59052 | 0.14649 | 0.045777 | -0.036622 | -0.004578 | -0.12817 | 0.21515 | 0.19226 | 0.14648 | 0.22888 | 0.18311 | 0.18311 | 0.050354 | 0.25177 | 122.9919 | 0.18768 | 123.1155 | 0.73242 | 123.0789 | -122.5388 | -123.1201 | 0.59509 | 122.9553 | 0.54474 | 0.93841
567.9688 | 123.1613 | -0.6134 | 122.3831 | -0.18326 | -0.00091854 | 0.020486 | 0.016413 | 9.818e-05 | 0.00084159 | 0.00075845 | 0.032227 | 0.00049983 | -0.0026361 | -0.0058084 | -0.0019845 | -0.00055747 | -0.0011621 | -0.07782 | 0.059509 | -0.10071 | -0.013733 | 0.09613 | -0.068665 | 0.054932 | 0.32044 | 122.406 | -0.68207 | 122.3877 | -0.37537 | -0.45776 | -0.37537 | 0.5127 | -122.3236 | -122.3969 | 0.70953 | 0.66834 | 0.54474 | 0.15564 | 0.032043 | -0.068665 | 0.022888 | 0.004577 | 0.23804 | 0.23804 | 0.15564 | 0.3067 | 0.2243 | 0.19684 | 0.086975 | 0.3067 | 123.0698 | 0.16022 | 123.0881 | 0.67291 | 123.0194 | -122.4838 | -123.0652 | 0.59967 | 123.0011 | 0.53558 | 0.93384
569.7031 | 123.1293 | -0.59509 | 122.4243 | -0.22141 | 0.00014946 | 0.021341 | 0.017267 | -0.0035334 | 0.002978 | -0.0020188 | 0.02002 | -0.00035457 | 0.0012091 | -0.0011086 | 0.00079247 | -0.0033347 | -0.0015893 | -0.07782 | 0.086975 | -0.086975 | -0.032043 | 0.091553 | -0.054932 | 0.050354 | 0.27924 | 122.4152 | -0.63629 | 122.4152 | -0.32959 | -0.42572 | -0.32959 | 0.50812 | -122.3373 | -122.4564 | 0.68665 | 0.64545 | 0.54016 | 0.13733 | 0.032043 | -0.041199 | -0.009155 | -0.009155 | 0.2655 | 0.2655 | 0.16937 | 0.3067 | 0.21057 | 0.17853 | 0.054932 | 0.3067 | 123.0515 | 0.17395 | 123.0515 | 0.68207 | 123.0103 | -122.5113 | -123.0606 | 0.56305 | 123.0103 | 0.51727 | 0.87433
571.375 | 123.143 | -0.70038 | 122.3099 | -0.15274 | -0.00091854 | 0.019205 | 0.014276 | -0.00011542 | 0.001269 | -0.0015916 | 0.056641 | -0.00014097 | -0.0024225 | -0.006022 | -0.0015573 | -0.0033347 | -0.0028711 | -0.09613 | 0.07782 | -0.091553 | -0.013733 | 0.10071 | -0.041199 | 0.064087 | 0.35248 | 122.319 | -0.7782 | 122.2687 | -0.45776 | -0.53101 | -0.48065 | 0.60882 | -122.2321 | -122.3236 | 0.80109 | 0.76446 | 0.65918 | 0.15564 | 0.050354 | -0.07782 | 0.009156 | -0.041198 | 0.24261 | 0.21973 | 0.16937 | 0.29755 | 0.24719 | 0.19226 | 0.07782 | 0.32043 | 123.0469 | 0.16937 | 123.0972 | 0.7782 | 123.0194 | -122.4014 | -123.0881 | 0.68664 | 122.9691 | 0.60425 | 1.0529
573.0938 | 123.0286 | -0.66376 | 122.3877 | -0.16037 | -0.0022003 | 0.018564 | 0.017908 | 0.0052252 | 0.00062799 | 0.0016128 | -0.062378 | 0.001568 | 0.0022773 | -0.00025423 | -0.00091653 | -0.0022665 | 0.0022559 | -0.1236 | 0.091553 | -0.11444 | -0.10529 | -0.009155 | -0.14648 | -0.036621 | 0.25635 | 122.4335 | -0.73242 | 122.2778 | -0.51727 | -0.61798 | -0.49896 | 0.54932 | -122.2961 | -122.493 | 0.6546 | 0.62714 | 0.51727 | 0.07782 | -0.032043 | -0.068665 | 0.045777 | -0.10986 | 0.14648 | 0.1648 | 0.045776 | 0.23346 | 0.11444 | 0.10529 | 0.009155 | 0.21515 | 123.0103 | 0.20599 | 123.1659 | 0.75531 | 123.0972 | -122.5021 | -123.1201 | 0.55847 | 122.9416 | 0.54016 | 0.92011
574.8281 | 123.0057 | -0.56305 | 122.5525 | -0.099335 | -0.0026275 | 0.019632 | 0.014704 | -0.0026788 | -0.00065361 | 0.00204 | 0.016968 | 0.00092703 | 0.00035453 | 0.002523 | 0.0014335 | -0.0044029 | 0.0041785 | -0.18768 | 0.11902 | -0.1236 | -0.14648 | -0.041199 | -0.14648 | -0.036621 | 0.20599 | 122.5342 | -0.60883 | 122.3465 | -0.3891 | -0.46692 | -0.40283 | 0.43945 | -122.4335 | -122.699 | 0.52185 | 0.52643 | 0.41657 | 0.086975 | -0.022888 | -0.045777 | -0.01831 | -0.20599 | 0.17395 | 0.16022 | 0.09613 | 0.20599 | 0.14191 | 0.082397 | -0.022888 | 0.21973 | 122.9553 | 0.24261 | 123.143 | 0.68207 | 123.0972 | -122.6761 | -123.1613 | 0.41657 | 122.9095 | 0.37537 | 0.76904
576.5 | 123.143 | -0.43488 | 122.5479 | -0.20615 | -0.00049134 | 0.02305 | 0.016413 | -0.00011542 | 0.00041439 | 0.00097205 | -0.010498 | 0.0019952 | 0.0027045 | -0.0047402 | -0.00070273 | -0.0031211 | 0.0016151 | -0.11902 | 0.082397 | -0.1236 | -0.064087 | 0.045776 | -0.091553 | 0.036621 | 0.26093 | 122.6028 | -0.50812 | 122.5616 | -0.19684 | -0.29297 | -0.18768 | 0.31128 | -122.4655 | -122.612 | 0.48065 | 0.4715 | 0.34332 | 0.16022 | 0.032043 | -0.073243 | 0.054931 | 0.013733 | 0.23804 | 0.24719 | 0.14191 | 0.32043 | 0.21515 | 0.16937 | 0.059509 | 0.31128 | 123.0698 | 0.20599 | 123.111 | 0.51727 | 123.0377 | -122.6715 | -123.056 | 0.37079 | 122.9965 | 0.31586 | 0.6958
578.2344 | 123.143 | -0.47607 | 122.4747 | -0.099335 | -0.0051909 | 0.017496 | 0.015131 | -0.002038 | -0.002149 | 0.0013992 | 0.059692 | 0.00028623 | 0.0024909 | -0.0051676 | -0.00027553 | -0.0039755 | -0.00094854 | -0.10529 | 0.059509 | -0.10071 | -0.004578 | 0.14191 | -0.004578 | 0.11444 | 0.35248 | 122.5159 | -0.56763 | 122.4884 | -0.21973 | -0.29297 | -0.27008 | 0.37537 | -122.4152 | -122.4792 | 0.61798 | 0.59052 | 0.4715 | 0.21515 | 0.09613 | -0.091553 | 0.041199 | 0.013733 | 0.25635 | 0.20599 | 0.18311 | 0.29755 | 0.27466 | 0.24262 | 0.09613 | 0.3479 | 123.056 | 0.16022 | 123.0835 | 0.53558 | 122.9919 | -122.5754 | -123.0423 | 0.4715 | 122.9645 | 0.37079 | 0.82855
579.9688 | 123.1064 | -0.38452 | 122.6074 | -0.20615 | -0.0013457 | 0.018991 | 0.017053 | -0.0018244 | 0.0019098 | -9.6154e-05 | 0.02002 | -0.0012092 | 0.0014227 | -0.0070902 | -0.0013437 | -0.0048301 | -0.0043665 | -0.10529 | 0.054932 | -0.09613 | -0.032043 | 0.09613 | -0.086975 | 0.068665 | 0.27466 | 122.6257 | -0.45319 | 122.5662 | -0.16479 | -0.24719 | -0.17853 | 0.28839 | -122.5525 | -122.6395 | 0.48065 | 0.45319 | 0.29755 | 0.16479 | 0.009155 | -0.068665 | 0.01831 | -0.041199 | 0.21973 | 0.20599 | 0.13733 | 0.27466 | 0.20599 | 0.19226 | 0.064087 | 0.28839 | 123.0194 | 0.15106 | 123.0789 | 0.43945 | 123.0103 | -122.7036 | -123.0606 | 0.35248 | 122.9507 | 0.27924 | 0.65918
581.6406 | 123.1338 | -0.41657 | 122.6074 | -0.068817 | -0.0039093 | 0.018777 | 0.013849 | -0.0018244 | -0.0017218 | 0.0011856 | 0.059692 | 0.00071343 | 0.00035453 | -0.0028176 | -0.00091653 | -0.0054709 | -0.0015893 | -0.11444 | 0.064087 | -0.09613 | -0.018311 | 0.13275 | -0.022888 | 0.073242 | 0.35248 | 122.5754 | -0.48065 | 122.5754 | -0.16937 | -0.24261 | -0.1831 | 0.32044 | -122.5433 | -122.6257 | 0.54932 | 0.48981 | 0.39368 | 0.16937 | 0.073242 | -0.064087 | -0.032044 | -0.032044 | 0.24719 | 0.23346 | 0.17395 | 0.29755 | 0.23804 | 0.22888 | 0.077819 | 0.31128 | 123.056 | 0.16022 | 123.056 | 0.48065 | 122.9919 | -122.7036 | -123.0881 | 0.39825 | 122.9919 | 0.30212 | 0.76904
583.375 | 123.1338 | -0.35706 | 122.6395 | -0.14511 | 0.00079046 | 0.01835 | 0.020044 | 0.0024482 | 0.00020079 | -0.00052335 | -0.025757 | 0.001568 | -0.0024225 | 0.0055136 | -0.0036935 | -0.0022665 | -0.0026575 | -0.073242 | 0.082397 | -0.10986 | -0.022888 | 0.086975 | -0.07782 | 0.036621 | 0.30212 | 122.6669 | -0.40283 | 122.6761 | -0.10071 | -0.19684 | -0.07782 | 0.24719 | -122.5571 | -122.6624 | 0.44403 | 0.39368 | 0.27924 | 0.14648 | 0.032043 | -0.045776 | 0.027466 | 0.036621 | 0.25635 | 0.27924 | 0.16022 | 0.32501 | 0.20599 | 0.19684 | 0.086975 | 0.30212 | 123.0789 | 0.19226 | 123.0698 | 0.43945 | 123.024 | -122.7493 | -123.0423 | 0.33417 | 123.0331 | 0.28381 | 0.65918
585.1094 | 123.0698 | -0.35248 | 122.7173 | -0.14511 | 0.00036326 | 0.0207 | 0.017267 | 0.0033026 | 0.002337 | 0.00033105 | -0.044067 | 0.00028623 | -0.0011407 | 0.0042318 | 0.0012199 | -0.0026939 | -0.0013757 | -0.10986 | 0.10071 | -0.13733 | -0.086975 | 0.032043 | -0.11444 | -0.013733 | 0.29755 | 122.731 | -0.39825 | 122.6074 | -0.12817 | -0.23804 | -0.15564 | 0.21515 | -122.6166 | -122.8043 | 0.38452 | 0.33875 | 0.23804 | 0.1236 | 0.022888 | -0.045776 | 0.013733 | -0.10986 | 0.2243 | 0.19684 | 0.11444 | 0.24261 | 0.16022 | 0.16937 | 0.050354 | 0.27008 | 123.0057 | 0.23804 | 123.1293 | 0.45319 | 123.0835 | -122.8546 | -123.1155 | 0.2655 | 122.9599 | 0.24262 | 0.65002
586.7969 | 123.1201 | -0.28839 | 122.7264 | -0.18326 | -0.0024139 | 0.01835 | 0.016199 | 0.0015936 | 0.00041439 | 0.0016128 | 0.053589 | 0.0024224 | 0.00035453 | -0.0023904 | 0.0022879 | -0.0031211 | -0.0013757 | -0.15106 | 0.086975 | -0.10529 | -0.086975 | 0.041199 | -0.10071 | 0.036621 | 0.21515 | 122.7448 | -0.36163 | 122.6715 | -0.068665 | -0.13275 | -0.086975 | 0.18311 | -122.6395 | -122.8134 | 0.32959 | 0.32501 | 0.18768 | 0.14191 | 0.004578 | -0.073242 | 0.018311 | -0.054931 | 0.21973 | 0.20142 | 0.15564 | 0.27466 | 0.22888 | 0.14649 | 0.018311 | 0.29297 | 123.0331 | 0.19226 | 123.1064 | 0.37537 | 123.0331 | -122.8317 | -123.0881 | 0.20142 | 122.9599 | 0.13733 | 0.50354
588.5156 | 123.0515 | -0.32501 | 122.7585 | -0.14511 | -0.00070494 | 0.018137 | 0.018549 | 0.0022346 | 0.00084159 | -0.00073695 | -0.068481 | 0.003277 | 0.00014093 | 0.0042318 | 0.00015167 | -0.00077127 | 0.0011877 | -0.1236 | 0.091553 | -0.13275 | -0.09613 | 0.013733 | -0.1236 | -0.022888 | 0.28381 | 122.7631 | -0.37537 | 122.6395 | -0.13733 | -0.24719 | -0.13275 | 0.19226 | -122.6669 | -122.8546 | 0.33875 | 0.30212 | 0.20142 | 0.10986 | 0.009155 | -0.050354 | 0.004578 | -0.11902 | 0.18768 | 0.19226 | 0.07782 | 0.24261 | 0.12817 | 0.14648 | 0.036621 | 0.23804 | 123.0148 | 0.2243 | 123.1384 | 0.41657 | 123.0881 | -122.8912 | -123.1338 | 0.22888 | 122.9645 | 0.20142 | 0.60882
590.25 | 123.0881 | -0.27466 | 122.7219 | -0.19089 | -0.0015595 | 0.01835 | 0.016413 | -0.00011542 | 0.0021234 | -9.6154e-05 | 0.03833 | -0.00078177 | 0.0016363 | -0.00089503 | 0.0012199 | -0.0033347 | -0.0013757 | -0.12817 | 0.059509 | -0.091553 | -0.086975 | 0.045776 | -0.10529 | 0.018311 | 0.22888 | 122.7768 | -0.32501 | 122.6944 | -0.045776 | -0.11902 | -0.050354 | 0.18311 | -122.6624 | -122.8088 | 0.32043 | 0.29297 | 0.16937 | 0.10986 | -0.013733 | -0.050354 | 0.054931 | -0.027466 | 0.22888 | 0.2243 | 0.15564 | 0.27466 | 0.20599 | 0.13733 | 0.004578 | 0.27924 | 123.0194 | 0.15106 | 123.1018 | 0.33417 | 123.0515 | -122.8134 | -123.0469 | 0.18768 | 122.9691 | 0.14648 | 0.50354
591.9375 | 123.111 | -0.25635 | 122.7493 | -0.14511 | 0.0024995 | 0.022409 | 0.020471 | 0.00095278 | -1.2808e-05 | 0.005458 | -0.037964 | -0.00014097 | 0.0018499 | 0.0027366 | -0.00048913 | -0.0050437 | -0.00030754 | -0.14648 | 0.09613 | -0.11902 | -0.11902 | 0 | -0.17395 | -0.032043 | 0.21515 | 122.8271 | -0.32044 | 122.7173 | -0.050354 | -0.14648 | -0.036621 | 0.13733 | -122.6532 | -122.8683 | 0.25635 | 0.22431 | 0.082398 | 0.086976 | -0.054931 | -0.064087 | 0.077819 | -0.032044 | 0.20599 | 0.21973 | 0.10986 | 0.28381 | 0.17395 | 0.11902 | 0 | 0.27008 | 123.0377 | 0.21515 | 123.1476 | 0.35248 | 123.0835 | -122.8683 | -123.0698 | 0.13733 | 122.9736 | 0.10986 | 0.4715
593.6719 | 123.0927 | -0.23804 | 122.7448 | -0.16037 | -0.0039093 | 0.019205 | 0.015985 | 0.00073918 | 0.0010554 | 0.00439 | 0.041382 | -0.00035457 | 0.0014227 | -0.0019632 | -0.00091653 | -0.0029075 | -0.0067163 | -0.16937 | 0.068665 | -0.11444 | -0.086975 | 0.027466 | -0.10986 | 0.013733 | 0.21515 | 122.8088 | -0.31586 | 122.7081 | -0.036621 | -0.11902 | -0.045776 | 0.1236 | -122.6761 | -122.8317 | 0.2655 | 0.25177 | 0.12817 | 0.12817 | 0.004578 | -0.07782 | 0.064087 | -0.036621 | 0.20142 | 0.19226 | 0.11902 | 0.27008 | 0.19684 | 0.14191 | 0.027466 | 0.27924 | 123.024 | 0.18311 | 123.1247 | 0.3067 | 123.0469 | -122.8592 | -123.0606 | 0.15106 | 122.9462 | 0.068664 | 0.45319
595.3594 | 123.1522 | -0.26093 | 122.731 | -0.16037 | -0.00091854 | 0.018137 | 0.013208 | -0.0018244 | -0.00022641 | -0.00095055 | 0.053589 | 7.2626e-05 | 0.00099553 | -0.00089503 | -0.0013437 | -0.0033347 | -0.0015893 | -0.14648 | 0.073242 | -0.11444 | -0.059509 | 0.07782 | -0.054932 | 0.054932 | 0.30212 | 122.7631 | -0.32959 | 122.7356 | 0 | -0.059509 | -0.022888 | 0.14648 | -122.6578 | -122.7905 | 0.33875 | 0.31586 | 0.20599 | 0.16937 | 0.059509 | -0.068665 | 0.032044 | 0.004578 | 0.26093 | 0.23804 | 0.20142 | 0.3067 | 0.27008 | 0.19226 | 0.054932 | 0.32959 | 123.0652 | 0.18768 | 123.0927 | 0.33417 | 123.024 | -122.8455 | -123.0606 | 0.20142 | 122.9965 | 0.11444 | 0.56305
597.1094 | 122.9919 | -0.30212 | 122.7905 | -0.14511 | 0.00079046 | 0.017709 | 0.018762 | -0.00096982 | 0.0021234 | 0.0033218 | -0.086792 | 0.00092703 | -0.0015681 | 0.0027366 | -0.00070273 | -0.0022665 | -0.0015893 | -0.16022 | 0.09613 | -0.14648 | -0.15564 | -0.050354 | -0.20142 | -0.07782 | 0.17395 | 122.818 | -0.34332 | 122.6532 | -0.16022 | -0.24719 | -0.12817 | 0.15564 | -122.6944 | -122.9462 | 0.25177 | 0.2243 | 0.10071 | 0.068664 | -0.054932 | -0.041199 | 0.027466 | -0.13733 | 0.14191 | 0.17395 | 0.054932 | 0.21515 | 0.096131 | 0.09613 | -0.009156 | 0.18311 | 122.9965 | 0.24261 | 123.1613 | 0.39825 | 123.1201 | -122.937 | -123.1338 | 0.14648 | 122.9553 | 0.14191 | 0.47607
598.7812 | 123.024 | -0.29755 | 122.8088 | -0.061188 | -0.0017731 | 0.016855 | 0.016199 | 0.00031198 | -0.00022641 | -0.00095055 | -0.016602 | 0.001568 | 0.00014093 | -0.00089503 | -0.0017709 | -0.0024803 | 0.00011966 | -0.16937 | 0.11902 | -0.12817 | -0.16022 | -0.045776 | -0.15106 | -0.054932 | 0.21515 | 122.8226 | -0.33417 | 122.6395 | -0.10529 | -0.1831 | -0.11902 | 0.16937 | -122.6898 | -122.9691 | 0.25177 | 0.24261 | 0.14648 | 0.073242 | -0.022888 | -0.036621 | 0.013733 | -0.16937 | 0.19226 | 0.17853 | 0.11444 | 0.21515 | 0.15106 | 0.082398 | -0.032043 | 0.22888 | 122.9736 | 0.24719 | 123.1567 | 0.41656 | 123.1201 | -122.937 | -123.143 | 0.13733 | 122.937 | 0.12817 | 0.5127
600.5156 | 123.0515 | -0.3067 | 122.7448 | -0.18326 | -0.0011321 | 0.019846 | 0.017908 | -0.00054262 | 0.00041439 | 0.0022536 | -0.044067 | 0.0019952 | 0.00056833 | 0.00060037 | 0.00015167 | -0.0024803 | 0.00033326 | -0.16479 | 0.10071 | -0.15564 | -0.16022 | -0.054932 | -0.16937 | -0.068665 | 0.17395 | 122.7814 | -0.36621 | 122.644 | -0.14191 | -0.24261 | -0.13275 | 0.15106 | -122.644 | -122.905 | 0.25177 | 0.23804 | 0.13733 | 0.086975 | -0.013733 | -0.059509 | 0.036621 | -0.10071 | 0.16479 | 0.17395 | 0.064087 | 0.23346 | 0.1236 | 0.10071 | -0.004577 | 0.2243 | 123.0103 | 0.25635 | 123.1476 | 0.40741 | 123.0881 | -122.9004 | -123.111 | 0.14648 | 122.9507 | 0.14191 | 0.48065
602.2656 | 123.1567 | -0.27008 | 122.7264 | -0.091705 | -0.0024139 | 0.019846 | 0.014063 | 0.00073918 | 0.001269 | -0.0011642 | 0.041382 | 0.00028623 | 0.00014093 | -0.00025423 | -0.00070273 | -0.0052573 | -0.0041527 | -0.10529 | 0.064087 | -0.11444 | -0.018311 | 0.11902 | -0.018311 | 0.073242 | 0.35706 | 122.7493 | -0.32501 | 122.7264 | 0 | -0.082397 | -0.032043 | 0.15564 | -122.6624 | -122.7448 | 0.3891 | 0.34332 | 0.25177 | 0.18768 | 0.09613 | -0.054931 | 0.022889 | 0 | 0.27008 | 0.23804 | 0.18768 | 0.29297 | 0.24262 | 0.23346 | 0.09613 | 0.32501 | 123.0515 | 0.17853 | 123.0743 | 0.33417 | 123.0194 | -122.8409 | -123.0515 | 0.25177 | 122.9965 | 0.1648 | 0.62714
603.9375 | 123.0148 | -0.3891 | 122.6898 | -0.10696 | -0.0030547 | 0.019632 | 0.015558 | -0.00032902 | 0.00084159 | -0.00030975 | 0.035278 | 0.0013544 | 0.0029181 | -4.063e-05 | 0.00015167 | -0.0035483 | -0.0018029 | -0.11902 | 0.064087 | -0.13733 | -0.10071 | 0.032043 | -0.09613 | 0.004578 | 0.28381 | 122.7127 | -0.42572 | 122.5616 | -0.20142 | -0.2655 | -0.22888 | 0.25177 | -122.6257 | -122.7905 | 0.42114 | 0.39368 | 0.29297 | 0.14191 | 0.041199 | -0.036621 | 0.022889 | -0.12817 | 0.18768 | 0.16022 | 0.1236 | 0.19684 | 0.16022 | 0.16937 | 0.036621 | 0.2243 | 122.9874 | 0.20142 | 123.1384 | 0.45319 | 123.1018 | -122.8271 | -123.1155 | 0.28839 | 122.9507 | 0.27008 | 0.67291
605.6094 | 123.1247 | -0.30212 | 122.6944 | -0.16037 | 0.00014946 | 0.019205 | 0.016199 | 9.818e-05 | 0.00041439 | 0.0011856 | 0.001709 | 0.00071343 | 0.0020635 | 0.0044456 | 0.00036527 | -0.0024803 | -0.0024439 | -0.07782 | 0.045776 | -0.10071 | -0.022888 | 0.09613 | -0.050354 | 0.036621 | 0.31128 | 122.699 | -0.37079 | 122.6944 | -0.064087 | -0.14191 | -0.064087 | 0.20142 | -122.6486 | -122.7173 | 0.39825 | 0.33875 | 0.25177 | 0.13733 | 0.050354 | -0.068665 | 0.004578 | 0 | 0.23804 | 0.23804 | 0.16022 | 0.3067 | 0.22888 | 0.19684 | 0.07782 | 0.3067 | 123.0652 | 0.14648 | 123.0698 | 0.3479 | 123.0011 | -122.7951 | -123.0652 | 0.27924 | 122.9965 | 0.2243 | 0.6134
607.375 | 123.056 | -0.40283 | 122.6578 | -0.13748 | -0.0015595 | 0.018991 | 0.017694 | 9.818e-05 | -0.00086721 | -9.6154e-05 | -0.044067 | 0.0017816 | 0.00099553 | -0.001536 | 0.00057887 | -0.0011985 | 0.00097406 | -0.15564 | 0.10986 | -0.13733 | -0.10071 | 0.004578 | -0.11444 | -0.032043 | 0.31586 | 122.7081 | -0.44861 | 122.5662 | -0.17853 | -0.28381 | -0.20599 | 0.2655 | -122.5479 | -122.7585 | 0.40741 | 0.37079 | 0.28839 | 0.10529 | 0.022888 | -0.045776 | 0.050354 | -0.091553 | 0.2243 | 0.19684 | 0.11902 | 0.24261 | 0.1648 | 0.14191 | 0.036621 | 0.27008 | 123.0148 | 0.24719 | 123.1567 | 0.5127 | 123.111 | -122.7951 | -123.1064 | 0.30212 | 122.9691 | 0.24719 | 0.71869
609.1094 | 123.0972 | -0.34332 | 122.6669 | -0.19089 | -0.0017731 | 0.018137 | 0.017267 | -0.0035334 | 0.00020079 | 0.00011745 | 0.023071 | 0.0017816 | 0.0012091 | -0.0013224 | 0.00015167 | -0.0035483 | 0.0011877 | -0.11444 | 0.068665 | -0.10529 | -0.050354 | 0.091553 | -0.082397 | 0.032043 | 0.27924 | 122.6807 | -0.40741 | 122.6212 | -0.11902 | -0.21515 | -0.13733 | 0.23804 | -122.5983 | -122.7173 | 0.43488 | 0.37537 | 0.26093 | 0.13733 | 0.022889 | -0.064087 | 0.013733 | -0.045776 | 0.2243 | 0.20599 | 0.12817 | 0.27008 | 0.19226 | 0.19684 | 0.054932 | 0.28839 | 123.0286 | 0.17395 | 123.0881 | 0.41199 | 123.024 | -122.7722 | -123.0743 | 0.29297 | 122.9645 | 0.22888 | 0.62256
610.875 | 123.0286 | -0.38452 | 122.6898 | -0.16037 | 0.00057686 | 0.020914 | 0.020258 | 0.00052558 | 0.0016962 | 0.00204 | -0.047119 | 0.0017816 | -0.0022089 | 0.0044456 | -0.0015573 | -0.0020529 | 0.00033326 | -0.16479 | 0.10986 | -0.14191 | -0.15106 | -0.059509 | -0.20142 | -0.050354 | 0.19226 | 122.6944 | -0.44861 | 122.5616 | -0.2243 | -0.31586 | -0.21973 | 0.24261 | -122.58 | -122.8409 | 0.32501 | 0.33417 | 0.1831 | 0.091553 | -0.059509 | -0.064087 | 0.004578 | -0.12817 | 0.16022 | 0.16479 | 0.068664 | 0.22888 | 0.13275 | 0.082398 | -0.009155 | 0.2243 | 123.0103 | 0.25177 | 123.143 | 0.49438 | 123.0789 | -122.8317 | -123.1384 | 0.23346 | 122.9462 | 0.21973 | 0.57678
612.5625 | 123.1293 | -0.37537 | 122.6166 | -0.084076 | -0.0026275 | 0.020273 | 0.013422 | 0.00073918 | -0.001081 | 0.002681 | 0.041382 | 0.00028623 | 0.00014093 | -0.0047402 | 0.00036527 | -0.0037619 | -9.3938e-05 | -0.11902 | 0.045776 | -0.10071 | -0.027466 | 0.11444 | -0.036621 | 0.073242 | 0.37079 | 122.6486 | -0.43945 | 122.6166 | -0.10071 | -0.16937 | -0.14191 | 0.27466 | -122.5708 | -122.644 | 0.48981 | 0.44861 | 0.33874 | 0.17395 | 0.064087 | -0.064087 | 0.032044 | 0 | 0.27466 | 0.23346 | 0.20599 | 0.29755 | 0.27008 | 0.21515 | 0.073242 | 0.33874 | 123.056 | 0.14648 | 123.0881 | 0.42114 | 123.024 | -122.7173 | -123.056 | 0.3479 | 122.9919 | 0.25635 | 0.74615
614.2969 | 123.0148 | -0.43488 | 122.6395 | -0.11459 | 0.00057686 | 0.018991 | 0.018549 | 0.0043708 | 0.0019098 | 0.0013992 | -0.053223 | 0.0011408 | 0.00035453 | 0.0042318 | -0.0013437 | -0.0026939 | 0.0024695 | -0.14648 | 0.09613 | -0.14648 | -0.11444 | -0.004578 | -0.16479 | -0.036621 | 0.26093 | 122.6395 | -0.49896 | 122.4838 | -0.29297 | -0.39825 | -0.28839 | 0.28839 | -122.5433 | -122.7539 | 0.4303 | 0.39825 | 0.27008 | 0.10986 | -0.018311 | -0.064087 | 0 | -0.15564 | 0.14191 | 0.14648 | 0.036621 | 0.21057 | 0.10071 | 0.14191 | 0.032043 | 0.20599 | 122.9828 | 0.24261 | 123.1384 | 0.531 | 123.0743 | -122.7859 | -123.1384 | 0.32043 | 122.9187 | 0.28839 | 0.6958
616.0312 | 123.1155 | -0.47607 | 122.5433 | -0.15274 | -0.0015595 | 0.018991 | 0.014917 | -0.0022516 | 0.00084159 | 0.0016128 | 0.074951 | 0.00071343 | 0.00099553 | -0.0087992 | 0.00057887 | -0.0041891 | -0.0024439 | -0.16937 | 0.068665 | -0.11444 | -0.086975 | 0.045776 | -0.10071 | 0.027466 | 0.24719 | 122.5571 | -0.55847 | 122.4884 | -0.23804 | -0.31128 | -0.25635 | 0.36163 | -122.4747 | -122.6303 | 0.52185 | 0.50354 | 0.37537 | 0.14191 | 0.013733 | -0.082398 | 0.013733 | -0.054932 | 0.23804 | 0.21973 | 0.1648 | 0.30212 | 0.24719 | 0.16022 | 0.027466 | 0.32043 | 123.0469 | 0.18311 | 123.1155 | 0.54474 | 123.0331 | -122.6578 | -123.1018 | 0.3891 | 122.9645 | 0.3067 | 0.72327
617.7812 | 123.0881 | -0.5127 | 122.4884 | -0.19089 | -0.0013457 | 0.018777 | 0.015985 | -0.0035334 | 0.0025506 | 0.0011856 | 0.050537 | -0.00099557 | 0.0020635 | -0.0030312 | 0.00079247 | -0.0052573 | -0.0020165 | -0.14191 | 0.059509 | -0.1236 | -0.082397 | 0.036621 | -0.10986 | 0.022888 | 0.25177 | 122.5113 | -0.58136 | 122.4335 | -0.32501 | -0.39368 | -0.33417 | 0.3891 | -122.4289 | -122.5708 | 0.54932 | 0.53558 | 0.40283 | 0.14648 | 0.013733 | -0.068665 | 0.022889 | -0.054931 | 0.18768 | 0.17853 | 0.11902 | 0.24719 | 0.18768 | 0.16022 | 0.041199 | 0.25635 | 123.0148 | 0.1831 | 123.0927 | 0.5722 | 123.024 | -122.612 | -123.0698 | 0.4303 | 122.9462 | 0.37079 | 0.76446
619.5156 | 123.1064 | -0.55847 | 122.4472 | -0.19852 | 0.00036326 | 0.021341 | 0.015558 | 0.0011664 | 0.0051142 | -0.0020188 | 0.0078126 | 0.0019952 | -0.00071347 | 0.002523 | -0.00070273 | -0.0037619 | -0.0013757 | -0.091553 | 0.050354 | -0.086975 | -0.027466 | 0.10529 | -0.082397 | 0.050354 | 0.32501 | 122.4838 | -0.59967 | 122.4518 | -0.3067 | -0.37079 | -0.31128 | 0.4715 | -122.3969 | -122.4747 | 0.66376 | 0.60883 | 0.47607 | 0.13733 | 0.004578 | -0.041198 | 0.036621 | 0.004577 | 0.25177 | 0.24719 | 0.18768 | 0.28839 | 0.22888 | 0.19226 | 0.059509 | 0.29297 | 123.0515 | 0.13733 | 123.0835 | 0.60883 | 123.0423 | -122.5342 | -123.0469 | 0.53101 | 123.0103 | 0.46692 | 0.88348
621.2656 | 123.1338 | -0.60425 | 122.406 | -0.091705 | -0.0039093 | 0.017068 | 0.015131 | -0.0018244 | -0.00086721 | 0.00097205 | 0.050537 | 0.0013544 | -7.2674e-05 | -0.0045266 | -0.00091653 | -0.0063255 | -9.3938e-05 | -0.10986 | 0.064087 | -0.10071 | -0.041199 | 0.13275 | -0.032043 | 0.07782 | 0.37079 | 122.4472 | -0.66376 | 122.3969 | -0.32501 | -0.39368 | -0.37079 | 0.50354 | -122.3419 | -122.4472 | 0.737 | 0.68207 | 0.5722 | 0.17853 | 0.068665 | -0.059509 | 0.041199 | -0.009155 | 0.27924 | 0.23346 | 0.21057 | 0.29297 | 0.27008 | 0.23346 | 0.059509 | 0.33875 | 123.0606 | 0.1648 | 123.111 | 0.66834 | 123.0515 | -122.5067 | -123.0698 | 0.56305 | 123.0011 | 0.49439 | 0.97504
622.9531 | 123.0286 | -0.62714 | 122.4472 | -0.11459 | -0.0024139 | 0.01835 | 0.018335 | -0.00032902 | -0.0025762 | -0.0011642 | 0.0078126 | 0.00071343 | 0.0031317 | 0.0031638 | -6.1934e-05 | -0.0050437 | -0.0011621 | -0.16022 | 0.07782 | -0.11902 | -0.10529 | -0.004578 | -0.1236 | -0.022888 | 0.2655 | 122.493 | -0.67749 | 122.3007 | -0.43945 | -0.50354 | -0.4715 | 0.50812 | -122.3694 | -122.5525 | 0.62256 | 0.60425 | 0.50354 | 0.096131 | -0.004577 | -0.050354 | 0.045776 | -0.14648 | 0.18768 | 0.15564 | 0.1236 | 0.20599 | 0.17395 | 0.11444 | 0.013733 | 0.23804 | 122.9782 | 0.19684 | 123.1705 | 0.70496 | 123.1201 | -122.5662 | -123.1247 | 0.52185 | 122.9279 | 0.46692 | 0.89264
624.6875 | 123.0469 | -0.65002 | 122.4197 | -0.14511 | -0.00070494 | 0.018777 | 0.017694 | -0.002038 | 0.0014826 | 0.00033105 | -0.062378 | 0.0017816 | 0.0016363 | 0.0020956 | 0.0010061 | -0.0029075 | -0.0018029 | -0.12817 | 0.10071 | -0.12817 | -0.091553 | 0.009155 | -0.12817 | -0.027466 | 0.33417 | 122.4518 | -0.69122 | 122.3373 | -0.43945 | -0.53101 | -0.45319 | 0.52185 | -122.319 | -122.5113 | 0.65918 | 0.62256 | 0.52185 | 0.10071 | 0 | -0.041199 | 0.032043 | -0.082398 | 0.21057 | 0.19684 | 0.11902 | 0.23804 | 0.16022 | 0.13733 | 0.036621 | 0.25177 | 123.0286 | 0.22888 | 123.143 | 0.75073 | 123.1018 | -122.5479 | -123.111 | 0.55847 | 122.9874 | 0.52185 | 0.98419
626.4219 | 123.0103 | -0.67749 | 122.4014 | -0.11459 | -0.0030547 | 0.017496 | 0.017053 | -0.001397 | -0.00065361 | 0.00011745 | -0.010498 | 0.0011408 | 0.0012091 | 0.0023092 | 0.0022879 | -0.0039755 | -0.0011621 | -0.1831 | 0.082397 | -0.15564 | -0.14648 | -0.027466 | -0.13275 | -0.041199 | 0.24261 | 122.4426 | -0.71869 | 122.2595 | -0.49439 | -0.5722 | -0.53101 | 0.52185 | -122.319 | -122.5479 | 0.65002 | 0.63629 | 0.54474 | 0.11444 | 0.022889 | -0.041199 | 0.041199 | -0.14191 | 0.18311 | 0.14648 | 0.10529 | 0.18768 | 0.14648 | 0.12817 | 0.009156 | 0.2243 | 122.9782 | 0.23804 | 123.1613 | 0.75989 | 123.1201 | -122.5571 | -123.1201 | 0.53101 | 122.937 | 0.49439 | 0.92011
628.1094 | 123.1064 | -0.64087 | 122.3785 | -0.16037 | 0.0014313 | 0.020486 | 0.017053 | 0.0043708 | 0.002978 | -0.0020188 | -0.044067 | 0.0011408 | 0.00078193 | 0.0053 | 0.00036527 | -0.0033347 | 0.0011877 | -0.15564 | 0.10529 | -0.1236 | -0.1236 | 0.004578 | -0.15564 | -0.036621 | 0.25177 | 122.4243 | -0.70038 | 122.3419 | -0.42114 | -0.52185 | -0.41199 | 0.51727 | -122.2733 | -122.5021 | 0.64545 | 0.60425 | 0.48523 | 0.086975 | -0.032044 | -0.059509 | 0.045776 | -0.036621 | 0.21973 | 0.22888 | 0.11902 | 0.28839 | 0.17853 | 0.12817 | 0 | 0.27923 | 123.0423 | 0.22888 | 123.1247 | 0.74616 | 123.0652 | -122.5021 | -123.0789 | 0.51727 | 122.9828 | 0.48523 | 0.89264
629.8594 | 123.1338 | -0.68207 | 122.3373 | -0.11459 | -0.0015595 | 0.016855 | 0.015131 | 0.0020208 | 0.0021234 | 0.0035354 | 0.081055 | 0.001568 | 0.0014227 | 0.0027366 | 0.00057887 | -0.0020529 | -0.0039391 | -0.13733 | 0.064087 | -0.11902 | -0.059509 | 0.068665 | -0.050354 | 0.050354 | 0.33417 | 122.3557 | -0.737 | 122.3145 | -0.39368 | -0.48981 | -0.43488 | 0.56305 | -122.2733 | -122.3969 | 0.75073 | 0.73242 | 0.63171 | 0.16937 | 0.068665 | -0.054932 | 0.018311 | -0.022888 | 0.28839 | 0.24719 | 0.19226 | 0.30212 | 0.24719 | 0.18768 | 0.05951 | 0.34332 | 123.0515 | 0.18311 | 123.0927 | 0.74616 | 123.0377 | -122.4564 | -123.0743 | 0.62256 | 122.9965 | 0.54474 | 1.0162
631.5312 | 123.0927 | -0.68207 | 122.3511 | -0.11459 | -0.0022003 | 0.019632 | 0.017267 | -0.0028924 | 0.002337 | 0.0013992 | 0.035278 | 0.00028623 | 0.00056833 | -0.0068766 | -0.0011301 | -0.0033347 | 0.0028967 | -0.14648 | 0.07782 | -0.10071 | -0.10071 | 0.022888 | -0.1236 | 0.009155 | 0.25177 | 122.3694 | -0.72784 | 122.2961 | -0.4715 | -0.53558 | -0.46692 | 0.58136 | -122.2733 | -122.4518 | 0.70496 | 0.69122 | 0.55847 | 0.10986 | -0.022888 | -0.045776 | 0.018311 | -0.054931 | 0.21057 | 0.21515 | 0.14648 | 0.26093 | 0.19226 | 0.1236 | 0 | 0.25635 | 123.024 | 0.17853 | 123.0972 | 0.75989 | 123.0515 | -122.4518 | -123.0789 | 0.58136 | 122.9782 | 0.53558 | 0.93384
633.2656 | 123.1293 | -0.65918 | 122.3557 | -0.19089 | -0.0028411 | 0.020914 | 0.017267 | 0.0026618 | 0.0010554 | 0.00033105 | -0.022705 | 0.0011408 | 0.0016363 | -0.0011086 | -0.00048913 | -0.0014121 | -0.0030847 | -0.082397 | 0.059509 | -0.086975 | -0.027466 | 0.09613 | -0.07782 | 0.027466 | 0.34332 | 122.3328 | -0.72327 | 122.3557 | -0.40283 | -0.50354 | -0.42572 | 0.5722 | -122.2961 | -122.3831 | 0.75531 | 0.68665 | 0.58136 | 0.11444 | 0.009155 | -0.064087 | -0.022888 | 0 | 0.25635 | 0.23346 | 0.15564 | 0.29755 | 0.21973 | 0.1831 | 0.059509 | 0.32043 | 123.0789 | 0.14648 | 123.056 | 0.71869 | 122.9919 | -122.4426 | -123.0789 | 0.63171 | 123.0148 | 0.57678 | 1.0025
635 | 123.0148 | -0.81482 | 122.2778 | -0.17563 | 0.00057686 | 0.019205 | 0.018122 | 0.0033026 | -0.00022641 | 0.0022536 | -0.080688 | 0.00071343 | 0.0012091 | -0.002604 | 0.00057887 | -0.0029075 | -0.0022301 | -0.17395 | 0.10529 | -0.13275 | -0.16937 | -0.09613 | -0.21057 | -0.10071 | 0.16937 | 122.287 | -0.85602 | 122.0993 | -0.6546 | -0.74616 | -0.63171 | 0.68207 | -122.1725 | -122.4472 | 0.71869 | 0.71411 | 0.60425 | 0.032043 | -0.07782 | -0.041199 | 0.009155 | -0.17853 | 0.16022 | 0.1831 | 0.068664 | 0.2243 | 0.10986 | 0.036621 | -0.036622 | 0.20142 | 122.9553 | 0.23804 | 123.143 | 0.9201 | 123.1018 | -122.4106 | -123.1339 | 0.64545 | 122.9141 | 0.64087 | 0.98419
636.7344 | 123.143 | -0.73242 | 122.2321 | -0.20615 | -0.00049134 | 0.019418 | 0.016626 | 0.00073918 | 0.00020079 | 0.00097205 | 0.0078126 | 0.001568 | -0.0019953 | 0.0050864 | 0.00079247 | -0.0041891 | -0.0043665 | -0.09613 | 0.045776 | -0.10071 | -0.022888 | 0.10529 | -0.07782 | 0.032043 | 0.33417 | 122.2733 | -0.79651 | 122.2778 | -0.49896 | -0.57678 | -0.48981 | 0.63171 | -122.1863 | -122.2549 | 0.83771 | 0.76447 | 0.6546 | 0.13275 | 0.022888 | -0.064087 | 0.041198 | 0.045776 | 0.23346 | 0.24262 | 0.15564 | 0.3067 | 0.21973 | 0.20599 | 0.07782 | 0.29755 | 123.0743 | 0.14648 | 123.0698 | 0.7782 | 123.0057 | -122.3328 | -123.0286 | 0.70953 | 123.0103 | 0.63629 | 1.0666
638.4062 | 123.0927 | -0.75989 | 122.2641 | -0.13748 | -0.00070494 | 0.0207 | 0.015344 | -0.00032902 | 0.0025506 | 0.00033105 | 0.041382 | -0.003559 | 0.0012091 | 0.0016684 | 0.0012199 | -0.0018393 | -0.0045801 | -0.14191 | 0.064087 | -0.10986 | -0.07782 | 0.027466 | -0.10529 | 0.009155 | 0.24261 | 122.2916 | -0.81482 | 122.2046 | -0.55847 | -0.63629 | -0.55847 | 0.65002 | -122.2 | -122.3419 | 0.78735 | 0.76904 | 0.6546 | 0.11902 | 0.004577 | -0.054931 | 0.027466 | -0.059509 | 0.20142 | 0.20142 | 0.1236 | 0.25635 | 0.17853 | 0.13733 | 0.032043 | 0.25635 | 123.0194 | 0.17395 | 123.1064 | 0.82398 | 123.0515 | -122.374 | -123.0789 | 0.68207 | 122.9645 | 0.61798 | 1.0025
640.125 | 123.056 | -0.86517 | 122.2092 | -0.045929 | -0.0022003 | 0.017923 | 0.017694 | 0.00052558 | -0.00022641 | 0.00204 | -0.047119 | 0.0019952 | 0.0012091 | 0.0046592 | -0.00091653 | -0.0014121 | -0.0015893 | -0.16937 | 0.086975 | -0.14191 | -0.12817 | -0.050354 | -0.15564 | -0.054932 | 0.25635 | 122.2504 | -0.90637 | 122.0764 | -0.67749 | -0.76446 | -0.6958 | 0.72327 | -122.1222 | -122.3373 | 0.81482 | 0.81024 | 0.70953 | 0.086975 | -0.013733 | -0.041199 | 0.041199 | -0.13275 | 0.18768 | 0.16937 | 0.10071 | 0.21057 | 0.14191 | 0.091553 | 0.013733 | 0.22888 | 122.9828 | 0.22888 | 123.1567 | 0.95215 | 123.1155 | -122.3511 | -123.1155 | 0.737 | 122.9416 | 0.6958 | 1.1215
641.875 | 123.0606 | -0.91095 | 122.1176 | -0.14511 | -0.00049134 | 0.020273 | 0.018549 | 0.0045844 | 0.0019098 | 0.00204 | -0.059326 | 0.00092703 | -7.2674e-05 | 0.00060037 | -0.00091653 | -0.0035483 | -0.0015893 | -0.1236 | 0.086975 | -0.13733 | -0.086975 | 0.022888 | -0.10986 | -0.009155 | 0.35248 | 122.1909 | -0.97046 | 122.0673 | -0.69122 | -0.79651 | -0.70953 | 0.77362 | -122.0306 | -122.2046 | 0.93384 | 0.9018 | 0.80109 | 0.12817 | 0.027466 | -0.059509 | 0.073242 | -0.050354 | 0.21973 | 0.20142 | 0.11444 | 0.26092 | 0.17395 | 0.16022 | 0.050354 | 0.27924 | 123.0377 | 0.2243 | 123.1613 | 0.99793 | 123.1018 | -122.2549 | -123.0881 | 0.82398 | 122.9782 | 0.78735 | 1.2634
643.5781 | 123.0835 | -0.89264 | 122.1268 | -0.14511 | -0.00091854 | 0.018564 | 0.013849 | 9.818e-05 | 0.0021234 | 0.00075845 | 0.053589 | 0.001568 | 0.00014093 | -0.0045266 | 0.0022879 | -0.0046165 | 0.0024695 | -0.16022 | 0.068665 | -0.10529 | -0.10071 | 0.032043 | -0.11444 | 0 | 0.24719 | 122.1359 | -0.94757 | 122.0718 | -0.6546 | -0.737 | -0.67749 | 0.78735 | -122.0581 | -122.2275 | 0.92468 | 0.89264 | 0.7782 | 0.10529 | -0.009155 | -0.054932 | 0.009155 | -0.054932 | 0.23804 | 0.21515 | 0.15564 | 0.27008 | 0.21057 | 0.13733 | 0.004578 | 0.29297 | 123.0194 | 0.17395 | 123.0835 | 0.9613 | 123.0286 | -122.2321 | -123.0743 | 0.79193 | 122.9645 | 0.73242 | 1.1398
645.3281 | 123.1293 | -0.83771 | 122.1634 | -0.12985 | -0.0056183 | 0.019205 | 0.012567 | -0.003106 | 0.002337 | 0.00097205 | 0.047485 | 7.2626e-05 | -0.00028627 | 0.00017297 | 0.00036527 | -0.0050437 | -9.3938e-05 | -0.10529 | 0.050354 | -0.09613 | -0.036621 | 0.10986 | -0.032043 | 0.064087 | 0.3891 | 122.2092 | -0.88806 | 122.1451 | -0.58594 | -0.65002 | -0.61798 | 0.74158 | -122.113 | -122.2 | 0.94757 | 0.9018 | 0.80566 | 0.16022 | 0.064087 | -0.050354 | 0.045776 | -0.01831 | 0.25177 | 0.21973 | 0.18768 | 0.27008 | 0.23804 | 0.20599 | 0.059509 | 0.30212 | 123.0331 | 0.14648 | 123.0972 | 0.88806 | 123.0469 | -122.2595 | -123.0515 | 0.80109 | 122.9828 | 0.73242 | 1.2268
647.2812 | 123.143 | -0.82855 | 122.1405 | -0.14511 | -0.0022003 | 0.019205 | 0.014917 | -0.00011542 | -0.00044001 | 0.0035354 | 0.053589 | 0.001568 | -0.00071347 | 0.0014548 | -0.00027553 | -0.0046165 | -9.3938e-05 | -0.13275 | 0.054932 | -0.11902 | -0.064087 | 0.059509 | -0.068665 | 0.054932 | 0.33875 | 122.1954 | -0.89722 | 122.1497 | -0.5722 | -0.64545 | -0.60425 | 0.70953 | -122.0856 | -122.2046 | 0.88806 | 0.88348 | 0.75989 | 0.17395 | 0.050354 | -0.068665 | 0.054932 | 0.009155 | 0.25635 | 0.2243 | 0.1831 | 0.29297 | 0.25177 | 0.17853 | 0.054932 | 0.32501 | 123.0469 | 0.17395 | 123.0927 | 0.88348 | 123.024 | -122.2595 | -123.0377 | 0.76446 | 122.9782 | 0.6958 | 1.1673
649.0156 | 123.0103 | -0.86975 | 122.2183 | -0.15274 | -0.0015595 | 0.0207 | 0.017267 | 0.00031198 | 0.0025506 | -0.00030975 | -0.071533 | 0.00071343 | 0.00099553 | 0.0080772 | 0.0012199 | -0.0037619 | -0.0032983 | -0.15106 | 0.10529 | -0.12817 | -0.14648 | -0.036621 | -0.1831 | -0.07782 | 0.23346 | 122.2412 | -0.9201 | 122.0398 | -0.73242 | -0.83771 | -0.72327 | 0.74158 | -122.113 | -122.3648 | 0.83313 | 0.79193 | 0.68665 | 0.050354 | -0.054931 | -0.050354 | 0.022888 | -0.17853 | 0.13733 | 0.14648 | 0.032043 | 0.19684 | 0.082397 | 0.091553 | -0.01831 | 0.18768 | 122.9599 | 0.23346 | 123.1613 | 0.97504 | 123.111 | -122.3465 | -123.1384 | 0.72327 | 122.9095 | 0.71869 | 1.1032
650.6875 | 123.056 | -0.87891 | 122.1725 | -0.091705 | -0.0032683 | 0.01835 | 0.015772 | 0.00138 | 0.00020079 | 0.0035354 | -0.016602 | 0.0017816 | 0.0024909 | -0.00025423 | 0.0012199 | -0.0020529 | 0.0033241 | -0.14648 | 0.091553 | -0.13275 | -0.12817 | -0.018311 | -0.1236 | -0.022888 | 0.31586 | 122.2183 | -0.95673 | 122.0764 | -0.67749 | -0.7782 | -0.70038 | 0.74615 | -122.081 | -122.3007 | 0.86059 | 0.85602 | 0.75531 | 0.10986 | 0.009155 | -0.07782 | 0.045777 | -0.09613 | 0.20142 | 0.17853 | 0.10071 | 0.25635 | 0.17853 | 0.11444 | 0.004577 | 0.27924 | 123.0331 | 0.2243 | 123.175 | 0.97046 | 123.0972 | -122.3053 | -123.1293 | 0.75073 | 122.9553 | 0.73242 | 1.1948
652.4375 | 123.056 | -0.87891 | 122.1771 | -0.17563 | -0.00070494 | 0.020059 | 0.020258 | 0.0043708 | -0.00065361 | 0.00075845 | -0.068481 | 0.0022088 | -0.0022089 | 0.0016684 | -0.0013437 | -0.0035483 | -0.0028711 | -0.12817 | 0.091553 | -0.11902 | -0.091553 | 0.036621 | -0.11444 | -0.009155 | 0.36163 | 122.1954 | -0.94757 | 122.0856 | -0.68665 | -0.7782 | -0.70038 | 0.75989 | -122.0856 | -122.2687 | 0.91553 | 0.86975 | 0.76446 | 0.10986 | 0.004578 | -0.068665 | 0.018311 | -0.091553 | 0.19226 | 0.17853 | 0.10071 | 0.24719 | 0.16937 | 0.15564 | 0.027466 | 0.26093 | 123.0331 | 0.21057 | 123.143 | 0.97046 | 123.0743 | -122.2961 | -123.1247 | 0.78735 | 122.9645 | 0.75073 | 1.2405
654.1719 | 123.0148 | -0.91553 | 122.1588 | -0.168 | -0.0028411 | 0.019205 | 0.013849 | -0.00032902 | 0.0014826 | 0.00075845 | 0.044434 | 0.002636 | 0.0027045 | -0.0013224 | 0.0018607 | -0.0016257 | 0.00033326 | -0.13275 | 0.073242 | -0.11902 | -0.11444 | 0.027466 | -0.13275 | -0.013733 | 0.30212 | 122.2 | -0.9613 | 122.0123 | -0.74158 | -0.81024 | -0.75531 | 0.79651 | -122.0856 | -122.2733 | 0.94299 | 0.90179 | 0.78278 | 0.10529 | -0.013732 | -0.045777 | 0.041199 | -0.14648 | 0.17395 | 0.16022 | 0.10528 | 0.20599 | 0.15106 | 0.14649 | 0.004578 | 0.21973 | 122.9736 | 0.19226 | 123.1613 | 0.98877 | 123.1155 | -122.2778 | -123.1201 | 0.80109 | 122.9279 | 0.78278 | 1.2177
655.875 | 123.0652 | -0.90637 | 122.1359 | -0.12985 | -0.0013457 | 0.019632 | 0.014704 | -0.00075622 | 0.00084159 | -0.00052335 | 0.044434 | 0.00028623 | 0.00014093 | 0.0031638 | 0.00036527 | -0.0044029 | 0.0043921 | -0.10986 | 0.045776 | -0.11444 | -0.050354 | 0.086975 | -0.050354 | 0.045776 | 0.35248 | 122.1359 | -0.96588 | 122.0627 | -0.68665 | -0.76446 | -0.70953 | 0.79193 | -122.0901 | -122.1863 | 0.99335 | 0.95215 | 0.85602 | 0.16022 | 0.064087 | -0.059509 | 0 | -0.073242 | 0.21973 | 0.19684 | 0.14191 | 0.25635 | 0.20142 | 0.20142 | 0.064087 | 0.27924 | 123.0286 | 0.16022 | 123.1018 | 0.95215 | 123.0423 | -122.2504 | -123.1018 | 0.85602 | 122.9691 | 0.79651 | 1.2589
657.625 | 123.0698 | -0.91095 | 122.1313 | -0.099335 | -0.0017731 | 0.017496 | 0.018976 | 0.0026618 | 0.002978 | 0.00075845 | -0.041016 | 0.001568 | 0.00099553 | -0.0017496 | 0.0012199 | -0.0029075 | -0.00094854 | -0.11902 | 0.10071 | -0.12817 | -0.086975 | 0.027466 | -0.11444 | -0.018311 | 0.36163 | 122.1863 | -0.96588 | 122.0673 | -0.70953 | -0.78735 | -0.71411 | 0.78278 | -122.0306 | -122.2183 | 0.93842 | 0.89264 | 0.79651 | 0.10986 | 0.013733 | -0.054931 | 0.054931 | -0.064087 | 0.20142 | 0.19684 | 0.1236 | 0.25177 | 0.17853 | 0.15564 | 0.041199 | 0.25635 | 123.0331 | 0.22888 | 123.1522 | 1.0117 | 123.0972 | -122.2595 | -123.0972 | 0.82398 | 122.9782 | 0.79193 | 1.2726
659.375 | 123.0972 | -0.90637 | 122.0901 | -0.21378 | -0.00070494 | 0.018137 | 0.014917 | 0.00052558 | 0.00020079 | 0.00054465 | 0.023071 | -0.00014097 | 0.00078193 | 0.00081397 | 0.00015167 | -0.0061117 | -0.0024439 | -0.10071 | 0.068665 | -0.09613 | -0.032043 | 0.086975 | -0.086975 | 0.045776 | 0.29297 | 122.0856 | -0.97046 | 122.049 | -0.70953 | -0.76904 | -0.70038 | 0.81024 | -122.0215 | -122.1222 | 0.99335 | 0.95215 | 0.8194 | 0.14191 | 0.009155 | -0.064087 | -0.004578 | -0.041199 | 0.19684 | 0.20599 | 0.13733 | 0.27008 | 0.20142 | 0.1831 | 0.064087 | 0.26092 | 123.0194 | 0.16479 | 123.056 | 0.97504 | 122.9919 | -122.1863 | -123.0606 | 0.87433 | 122.9553 | 0.80566 | 1.1993
661.1094 | 122.9965 | -1.0849 | 122.0032 | -0.16037 | 0.00057686 | 0.020914 | 0.019617 | 0.00052558 | -0.002149 | -9.6154e-05 | -0.062378 | 0.0013544 | 0.00035453 | 0.003591 | -0.0011301 | -0.0033347 | -0.00052114 | -0.14648 | 0.11444 | -0.14191 | -0.16022 | -0.091553 | -0.20142 | -0.068665 | 0.19684 | 122.049 | -1.1078 | 121.8475 | -0.9201 | -1.0117 | -0.89722 | 0.94299 | -121.8887 | -122.1634 | 0.99335 | 1.0162 | 0.88348 | 0.073242 | -0.059509 | -0.022888 | 0.045776 | -0.15564 | 0.1648 | 0.18768 | 0.073242 | 0.21057 | 0.09613 | 0.050354 | -0.01831 | 0.18768 | 122.9553 | 0.25635 | 123.1567 | 1.1993 | 123.1339 | -122.1451 | -123.111 | 0.92468 | 122.9324 | 0.93842 | 1.2817
662.8125 | 123.1201 | -1.0208 | 121.9574 | -0.14511 | 0.00036326 | 0.021127 | 0.016413 | -0.00054262 | 0.0034052 | -0.00052335 | -0.010498 | 0.002636 | 0.0020635 | -0.0030312 | 0.0020743 | -0.0050437 | -0.0013757 | -0.14191 | 0.082397 | -0.09613 | -0.10071 | 0.022888 | -0.14648 | -0.009155 | 0.28839 | 121.994 | -1.1124 | 121.9345 | -0.8194 | -0.90179 | -0.81024 | 0.92468 | -121.875 | -122.0581 | 1.0437 | 1.0117 | 0.87433 | 0.086975 | -0.050354 | -0.091553 | 0.036622 | -0.022888 | 0.20142 | 0.21057 | 0.11902 | 0.30212 | 0.21057 | 0.11902 | -0.004578 | 0.29297 | 123.0469 | 0.17853 | 123.1064 | 1.1032 | 123.0148 | -122.0535 | -123.0698 | 0.9201 | 122.9553 | 0.87891 | 1.3092
664.6094 | 123.1155 | -1.0757 | 121.9391 | -0.12985 | -0.00091854 | 0.020273 | 0.014704 | 0.0026618 | 0.00084159 | 0.00097205 | 0.047485 | -0.00035457 | -0.0011407 | 0.00060037 | 0.0022879 | -0.0033347 | 0.0031103 | -0.1236 | 0.054932 | -0.10986 | -0.073242 | 0.054932 | -0.10986 | 0.022888 | 0.27924 | 121.9574 | -1.1536 | 121.875 | -0.87433 | -0.95673 | -0.87891 | 0.96588 | -121.8842 | -122.0123 | 1.1307 | 1.0986 | 0.96588 | 0.13275 | 0 | -0.077819 | 0.01831 | -0.064087 | 0.20142 | 0.19684 | 0.11902 | 0.27466 | 0.19684 | 0.16479 | 0.036621 | 0.27924 | 123.0286 | 0.16479 | 123.111 | 1.1307 | 123.0331 | -122.049 | -123.0927 | 1.0025 | 122.9507 | 0.95215 | 1.355
666.375 | 123.1293 | -1.0529 | 121.9345 | -0.21378 | -0.0011321 | 0.020914 | 0.017267 | 0.0011664 | 0.0021234 | 0.00097205 | 0.03833 | -0.00078177 | -0.0028497 | 0.0010276 | 0.00015167 | -0.0031211 | -0.0047937 | -0.10071 | 0.068665 | -0.073242 | -0.018311 | 0.10986 | -0.059509 | 0.045776 | 0.3479 | 121.9391 | -1.1261 | 121.9299 | -0.8194 | -0.90179 | -0.83313 | 0.97961 | -121.8658 | -121.9528 | 1.1627 | 1.0986 | 0.99335 | 0.11902 | 0.013733 | -0.073243 | 0.004578 | -0.004577 | 0.23346 | 0.21973 | 0.15106 | 0.29297 | 0.2243 | 0.18311 | 0.054931 | 0.3067 | 123.056 | 0.14191 | 123.0652 | 1.1215 | 122.9919 | -122.0078 | -123.0606 | 1.0345 | 122.9828 | 0.95215 | 1.4008
668.0625 | 123.0148 | -1.1536 | 121.9299 | -0.13748 | -0.00070494 | 0.019846 | 0.018549 | -0.00032902 | 0.0019098 | 0.0018264 | -0.053223 | 0.00071343 | -0.00092707 | -0.0045266 | -0.00027553 | -0.0020529 | -0.0020165 | -0.16479 | 0.10071 | -0.13275 | -0.13733 | -0.064087 | -0.19684 | -0.064087 | 0.23346 | 121.9299 | -1.1993 | 121.7697 | -1.03 | -1.1078 | -0.98877 | 1.0208 | -121.8292 | -122.0673 | 1.0895 | 1.0895 | 0.95673 | 0.068664 | -0.064087 | -0.045777 | 0 | -0.16022 | 0.1236 | 0.16479 | 0.045776 | 0.21057 | 0.091553 | 0.068664 | -0.004578 | 0.16937 | 122.9691 | 0.23346 | 123.1293 | 1.2543 | 123.0835 | -122.0627 | -123.1293 | 1.0162 | 122.9233 | 0.98877 | 1.387
669.75 | 123.0743 | -1.1536 | 121.8933 | -0.14511 | -0.0024139 | 0.018564 | 0.017053 | -0.00075622 | 0.001269 | -0.0018052 | -0.03186 | 0.0024224 | 0.00099553 | -0.0021768 | 0.00036527 | -0.0029075 | 0.00054686 | -0.12817 | 0.086975 | -0.12817 | -0.07782 | 0.022888 | -0.11902 | -0.009155 | 0.3479 | 121.9437 | -1.2085 | 121.8155 | -0.94299 | -1.0483 | -0.95673 | 1.0254 | -121.8063 | -121.9711 | 1.1765 | 1.1444 | 1.0345 | 0.11902 | 0.009155 | -0.054932 | 0.050354 | -0.07782 | 0.21057 | 0.19684 | 0.10529 | 0.25177 | 0.16022 | 0.15106 | 0.050354 | 0.2655 | 123.024 | 0.21515 | 123.1522 | 1.2405 | 123.0972 | -122.0215 | -123.1018 | 1.0757 | 122.9691 | 1.0254 | 1.5015
671.4375 | 123.0743 | -1.1719 | 121.9116 | -0.10696 | -0.0034821 | 0.019418 | 0.01684 | 0.0018072 | 0.0014826 | 0.00439 | -0.022705 | 0.0024224 | -7.2674e-05 | 0.0048728 | -0.0011301 | -0.0016257 | -0.0032983 | -0.16022 | 0.10071 | -0.14648 | -0.12817 | -0.022888 | -0.12817 | -0.022888 | 0.31128 | 121.9208 | -1.2451 | 121.7697 | -0.96588 | -1.0666 | -0.99792 | 1.0254 | -121.8109 | -122.0398 | 1.149 | 1.149 | 1.0437 | 0.1236 | 0.01831 | -0.073242 | 0.009155 | -0.14191 | 0.20599 | 0.17395 | 0.10529 | 0.24719 | 0.17853 | 0.1236 | 0.01831 | 0.27924 | 123.0148 | 0.24719 | 123.1659 | 1.2726 | 123.0927 | -122.0581 | -123.1567 | 1.0437 | 122.9416 | 1.0117 | 1.4832
673.125 | 123.1567 | -1.1536 | 121.8842 | -0.099335 | -0.00091854 | 0.017282 | 0.013635 | -0.0022516 | 0.00041439 | 0.0013992 | 0.074951 | 0.00092703 | 0.0059087 | -0.0073038 | -0.0013437 | -0.0035483 | 0.00033326 | -0.082397 | 0.050354 | -0.086975 | -0.027466 | 0.11902 | -0.004578 | 0.073242 | 0.39825 | 121.8842 | -1.2222 | 121.843 | -0.87433 | -0.94299 | -0.91553 | 1.0666 | -121.8338 | -121.9116 | 1.2726 | 1.2268 | 1.149 | 0.16022 | 0.082397 | -0.068665 | 0 | -0.041198 | 0.27924 | 0.23804 | 0.21057 | 0.3067 | 0.27924 | 0.20599 | 0.059509 | 0.3479 | 123.0652 | 0.13733 | 123.1064 | 1.2039 | 123.0377 | -121.9711 | -123.1064 | 1.1261 | 122.9965 | 1.0712 | 1.5518
674.8125 | 123.1064 | -1.1673 | 121.8613 | -0.14511 | -0.0017731 | 0.017282 | 0.012567 | -0.0011834 | -0.0027898 | 0.0011856 | 0.053589 | -0.00099557 | 0.0012091 | -0.0023904 | -0.00048913 | -0.0054709 | -0.0024439 | -0.10529 | 0.032043 | -0.09613 | -0.027466 | 0.09613 | -0.045776 | 0.068665 | 0.35706 | 121.8704 | -1.2131 | 121.8018 | -0.9201 | -0.99792 | -0.95673 | 1.0712 | -121.8292 | -121.8887 | 1.2634 | 1.236 | 1.1215 | 0.16479 | 0.050354 | -0.045777 | 0.009155 | -0.059509 | 0.24719 | 0.21057 | 0.16937 | 0.25635 | 0.21515 | 0.19226 | 0.068664 | 0.29297 | 123.0148 | 0.12817 | 123.0835 | 1.1993 | 123.0377 | -121.9574 | -123.0743 | 1.1398 | 122.9691 | 1.062 | 1.5244
676.5781 | 123.056 | -1.2039 | 121.8796 | -0.091705 | -0.00049134 | 0.01835 | 0.017481 | 0.00031198 | -0.0019354 | -9.6154e-05 | 0.010864 | 0.00071343 | 0.00099553 | -0.0028176 | -0.0019845 | -0.0039755 | 0.0026831 | -0.16022 | 0.10529 | -0.14191 | -0.14191 | -0.054932 | -0.14191 | -0.036621 | 0.30212 | 121.9208 | -1.2314 | 121.7514 | -1.0117 | -1.1032 | -1.0208 | 1.062 | -121.7743 | -122.0215 | 1.149 | 1.1673 | 1.062 | 0.10529 | 0 | -0.027466 | 0.041198 | -0.12817 | 0.19226 | 0.18311 | 0.10071 | 0.21057 | 0.12817 | 0.086975 | 0 | 0.21973 | 122.9828 | 0.24719 | 123.1522 | 1.3092 | 123.1247 | -122.0215 | -123.111 | 1.062 | 122.9553 | 1.0437 | 1.506
678.2812 | 123.0011 | -1.1169 | 121.962 | -0.12222 | -0.0011321 | 0.019846 | 0.019617 | 0.0028754 | 0.001269 | 0.00097205 | -0.044067 | 0.003277 | 0.0027045 | 0.0014548 | -0.0013437 | -0.0039755 | 0.0011877 | -0.17395 | 0.10986 | -0.13275 | -0.16479 | -0.073242 | -0.19226 | -0.07782 | 0.22888 | 121.9986 | -1.1719 | 121.8201 | -0.98877 | -1.0757 | -0.9613 | 0.98419 | -121.8521 | -122.1268 | 1.0437 | 1.0391 | 0.92468 | 0.054931 | -0.05951 | -0.054932 | 0.036621 | -0.14191 | 0.12817 | 0.15564 | 0.041198 | 0.21057 | 0.09613 | 0.059509 | -0.032044 | 0.1831 | 122.9919 | 0.24261 | 123.1705 | 1.2268 | 123.1155 | -122.0947 | -123.1338 | 0.95215 | 122.937 | 0.94299 | 1.3458
679.9844 | 122.9782 | -1.2405 | 121.843 | -0.20615 | -0.0013457 | 0.021555 | 0.017053 | 0.003089 | 0.0014826 | -0.00030975 | -0.044067 | 0.0019952 | 0.0035589 | 0.0031638 | 0.00057887 | -0.0035483 | -0.0013757 | -0.16479 | 0.10529 | -0.1236 | -0.16937 | -0.086975 | -0.21057 | -0.09613 | 0.20142 | 121.8658 | -1.3046 | 121.6553 | -1.1032 | -1.1902 | -1.0849 | 1.1169 | -121.7377 | -122.0123 | 1.1536 | 1.1444 | 1.03 | 0.027466 | -0.086975 | -0.064086 | 0.022888 | -0.18768 | 0.13733 | 0.15564 | 0.050354 | 0.21973 | 0.11444 | 0.036621 | -0.045777 | 0.20142 | 122.9599 | 0.22888 | 123.1705 | 1.3458 | 123.1064 | -121.9666 | -123.1476 | 1.0712 | 122.8958 | 1.0757 | 1.442
681.6875 | 123.0789 | -1.2039 | 121.843 | -0.068817 | -0.00070494 | 0.021768 | 0.018549 | 0.00138 | -0.00086721 | -0.00030975 | -0.01355 | 7.2626e-05 | 0.0014227 | -0.0064492 | 0.0010061 | -0.0041891 | -0.0035119 | -0.13275 | 0.09613 | -0.13733 | -0.10986 | 0.013733 | -0.10529 | -0.013733 | 0.35706 | 121.8567 | -1.2909 | 121.7239 | -1.0208 | -1.1078 | -1.0254 | 1.0666 | -121.7468 | -121.9528 | 1.2177 | 1.1902 | 1.0986 | 0.1236 | 0.032043 | -0.086976 | 0.013732 | -0.11902 | 0.18311 | 0.17853 | 0.09613 | 0.2655 | 0.18311 | 0.15106 | 0.027466 | 0.27008 | 123.0148 | 0.23346 | 123.1476 | 1.3 | 123.0606 | -121.9803 | -123.1339 | 1.0941 | 122.9279 | 1.0712 | 1.561
683.3906 | 123.1522 | -1.0895 | 121.8979 | -0.091705 | -0.0045501 | 0.018137 | 0.015558 | 0.0020208 | -0.00022641 | -9.6154e-05 | 0.078003 | 0.0013544 | 0.00099553 | -0.0085854 | 0.0020743 | -0.0052573 | -0.00052114 | -0.11902 | 0.059509 | -0.091553 | -0.036621 | 0.11902 | -0.022888 | 0.064087 | 0.3891 | 121.9025 | -1.181 | 121.8658 | -0.83771 | -0.9201 | -0.87891 | 0.99792 | -121.8384 | -121.9345 | 1.2085 | 1.1536 | 1.0666 | 0.15564 | 0.068665 | -0.091552 | 0.004578 | -0.032043 | 0.25177 | 0.21057 | 0.16937 | 0.30212 | 0.26093 | 0.21057 | 0.054932 | 0.34332 | 123.0469 | 0.15106 | 123.0835 | 1.149 | 122.9919 | -121.9894 | -123.0789 | 1.0529 | 122.9553 | 0.97046 | 1.4786
685.0781 | 123.0789 | -1.149 | 121.8933 | -0.168 | -0.0039093 | 0.01835 | 0.01684 | -0.0024652 | 0.001269 | 0.0013992 | 0.0047608 | 0.0024224 | 0.0012091 | 0.0055136 | 0.00057887 | -0.00077127 | -0.0035119 | -0.15106 | 0.091553 | -0.13733 | -0.14191 | -0.018311 | -0.13275 | -0.027466 | 0.31586 | 121.9345 | -1.2039 | 121.7926 | -0.96588 | -1.0529 | -0.9613 | 1.0117 | -121.8018 | -122.0352 | 1.1307 | 1.1215 | 1.0162 | 0.10986 | 0.004578 | -0.054931 | 0.041198 | -0.10071 | 0.18311 | 0.18768 | 0.096131 | 0.24261 | 0.15106 | 0.11902 | -0.004578 | 0.23804 | 122.9965 | 0.22888 | 123.1384 | 1.2405 | 123.0835 | -122.0306 | -123.0972 | 1.0071 | 122.9416 | 0.99792 | 1.4648
686.7656 | 123.111 | -1.1719 | 121.8475 | -0.15274 | -0.0026275 | 0.016 | 0.015131 | 0.0011664 | 0.0016962 | 0.0056716 | 0.071899 | -0.00014097 | 0.0018499 | -0.0019632 | 0.00079247 | -0.0035483 | -0.00052114 | -0.16022 | 0.050354 | -0.10071 | -0.086975 | 0.018311 | -0.11444 | 0.004578 | 0.27008 | 121.8613 | -1.2268 | 121.7743 | -0.9613 | -1.03 | -0.96588 | 1.0712 | -121.7972 | -121.9345 | 1.1902 | 1.1765 | 1.0574 | 0.10529 | -0.013733 | -0.054932 | 0.013733 | -0.073242 | 0.21057 | 0.20599 | 0.14191 | 0.26093 | 0.19684 | 0.11902 | 0.013733 | 0.2655 | 123.0011 | 0.15106 | 123.0881 | 1.2222 | 123.0331 | -121.9482 | -123.0743 | 1.0849 | 122.9462 | 1.0117 | 1.442
688.4531 | 123.143 | -1.1719 | 121.8384 | -0.16037 | -6.4144e-05 | 0.0207 | 0.018762 | 0.0018072 | -0.00022641 | -0.0018052 | -0.019653 | 0.00092703 | -7.2674e-05 | 0.00017297 | -0.0011301 | -0.0026939 | -0.00094854 | -0.091553 | 0.07782 | -0.086975 | -0.032043 | 0.068665 | -0.068665 | 0.027466 | 0.37537 | 121.8292 | -1.2405 | 121.8246 | -0.94299 | -1.0254 | -0.91553 | 1.0849 | -121.7606 | -121.8704 | 1.2405 | 1.1993 | 1.1032 | 0.11444 | 0.01831 | -0.068665 | -0.009155 | -0.013733 | 0.22888 | 0.25635 | 0.14648 | 0.32501 | 0.21515 | 0.15564 | 0.054932 | 0.29755 | 123.0652 | 0.16479 | 123.0698 | 1.2497 | 123.0011 | -121.9254 | -123.0789 | 1.1398 | 122.9965 | 1.0803 | 1.5472
690.1406 | 123.0057 | -1.2451 | 121.8338 | -0.14511 | -6.4144e-05 | 0.019846 | 0.018976 | 0.0033026 | 0.0034052 | -0.00030975 | -0.03186 | -0.00014097 | 0.0016363 | 0.0085044 | -6.1934e-05 | -0.0039755 | 0.0011877 | -0.14648 | 0.091553 | -0.14648 | -0.16479 | -0.091553 | -0.22888 | -0.07782 | 0.23346 | 121.8887 | -1.2909 | 121.6644 | -1.0849 | -1.1719 | -1.0803 | 1.0986 | -121.7422 | -121.9986 | 1.1536 | 1.1673 | 1.0162 | 0.068664 | -0.082398 | -0.045777 | 0.054932 | -0.16937 | 0.16022 | 0.1648 | 0.073242 | 0.21057 | 0.11902 | 0.054931 | -0.018311 | 0.20599 | 122.9553 | 0.23804 | 123.1796 | 1.3367 | 123.1338 | -121.9803 | -123.1247 | 1.0803 | 122.9095 | 1.0986 | 1.4786
691.8281 | 123.1476 | -1.2177 | 121.8292 | -0.18326 | -0.0022003 | 0.017282 | 0.012781 | -0.0033196 | 0.0010554 | 0.00033105 | 0.096314 | 0.00049983 | 0.00099553 | -0.0038858 | 0.00036527 | -0.0048301 | 0.00033326 | -0.10986 | 0.059509 | -0.10071 | -0.018311 | 0.10986 | -0.018311 | 0.07782 | 0.42572 | 121.7972 | -1.2634 | 121.7789 | -0.93842 | -1.0162 | -0.9613 | 1.1169 | -121.7697 | -121.8475 | 1.3275 | 1.2955 | 1.1993 | 0.17853 | 0.082397 | -0.045777 | -0.032044 | -0.050354 | 0.27924 | 0.25635 | 0.20142 | 0.30212 | 0.24719 | 0.21057 | 0.082397 | 0.32501 | 123.0423 | 0.16022 | 123.0606 | 1.2772 | 123.0148 | -121.9299 | -123.0927 | 1.1993 | 122.9965 | 1.1078 | 1.6434
693.5469 | 123.143 | -1.2039 | 121.788 | -0.18326 | -0.0011321 | 0.018564 | 0.015558 | 0.00073918 | 0.00020079 | -0.001378 | -0.010498 | 0.00071343 | 0.0014227 | -0.0073038 | -0.0011301 | -0.00077127 | -0.0018029 | -0.09613 | 0.068665 | -0.10071 | -0.045776 | 0.082397 | -0.068665 | 0.050354 | 0.35706 | 121.8063 | -1.268 | 121.7972 | -0.96588 | -1.0574 | -0.95215 | 1.1032 | -121.7194 | -121.8338 | 1.2863 | 1.2543 | 1.1353 | 0.15106 | 0.032043 | -0.064087 | 0.01831 | 0.009155 | 0.23804 | 0.25177 | 0.14648 | 0.31586 | 0.21057 | 0.18311 | 0.054932 | 0.30212 | 123.0652 | 0.16937 | 123.0743 | 1.2726 | 123.0103 | -121.8887 | -123.056 | 1.1581 | 123.0011 | 1.1078 | 1.561
695.2188 | 123.0515 | -1.2772 | 121.8063 | -0.15274 | -0.0045501 | 0.018991 | 0.020685 | 0.0011664 | -0.00086721 | 0.0033218 | -0.01355 | 0.00028623 | 0.00099553 | 0.0042318 | -0.00027553 | -0.0050437 | -0.0011621 | -0.16937 | 0.091553 | -0.14191 | -0.16022 | -0.054932 | -0.15106 | -0.054932 | 0.29297 | 121.843 | -1.3458 | 121.6644 | -1.1032 | -1.1856 | -1.1124 | 1.1353 | -121.7148 | -121.9666 | 1.2222 | 1.2222 | 1.1261 | 0.086975 | -0.009155 | -0.068664 | 0.036622 | -0.14191 | 0.17395 | 0.1648 | 0.091553 | 0.23346 | 0.16022 | 0.086975 | -0.01831 | 0.24262 | 123.0103 | 0.23346 | 123.1888 | 1.3687 | 123.1201 | -121.9482 | -123.1522 | 1.1169 | 122.9416 | 1.1078 | 1.5701
696.8906 | 123.0286 | -1.2772 | 121.7972 | -0.053558 | -0.0028411 | 0.020273 | 0.01684 | 0.0022346 | -0.00044001 | 0.00097205 | -0.0043944 | 0.0011408 | 0.00035453 | 0.0010276 | 0.00036527 | -0.0037619 | -0.0011621 | -0.17395 | 0.11444 | -0.13733 | -0.15564 | -0.059509 | -0.16022 | -0.045776 | 0.3067 | 121.8384 | -1.3412 | 121.6415 | -1.0941 | -1.1902 | -1.1169 | 1.1398 | -121.6827 | -121.9528 | 1.2177 | 1.2314 | 1.1169 | 0.091553 | -0.022888 | -0.064087 | 0.041199 | -0.15564 | 0.18311 | 0.16022 | 0.086975 | 0.2243 | 0.15106 | 0.07782 | -0.018311 | 0.24719 | 122.9828 | 0.25177 | 123.1796 | 1.3916 | 123.1155 | -121.9345 | -123.1384 | 1.1215 | 122.9187 | 1.1032 | 1.5839
698.625 | 123.111 | -1.2863 | 121.7285 | -0.12222 | -0.0013457 | 0.019418 | 0.015985 | -0.002038 | 0.0016962 | 0.00204 | 0.059692 | 7.2626e-05 | -0.00049987 | -0.00025423 | 0.00015167 | -0.0058981 | -0.0015893 | -0.10986 | 0.045776 | -0.09613 | -0.032043 | 0.09613 | -0.041199 | 0.068665 | 0.43945 | 121.7789 | -1.3321 | 121.6919 | -1.03 | -1.1215 | -1.0666 | 1.1902 | -121.6827 | -121.7606 | 1.3824 | 1.355 | 1.2451 | 0.16479 | 0.054931 | -0.045776 | 0.050354 | -0.036621 | 0.25635 | 0.21973 | 0.1648 | 0.2655 | 0.21057 | 0.19226 | 0.064087 | 0.30212 | 123.024 | 0.14191 | 123.111 | 1.3321 | 123.0652 | -121.8246 | -123.0606 | 1.2543 | 122.9782 | 1.1765 | 1.7258
700.3281 | 123.024 | -1.3641 | 121.6965 | -0.12985 | -0.0022003 | 0.019418 | 0.018122 | -0.00096982 | -0.0012946 | 0.0011856 | -0.01355 | 0.002636 | 0.0020635 | -0.0034586 | -0.0011301 | -0.0046165 | 0.0016151 | -0.1831 | 0.10529 | -0.14191 | -0.16937 | -0.045776 | -0.16022 | -0.045776 | 0.3067 | 121.7422 | -1.4008 | 121.5363 | -1.2039 | -1.2726 | -1.2131 | 1.2222 | -121.5912 | -121.8658 | 1.3184 | 1.3184 | 1.2039 | 0.096131 | -0.01831 | -0.036621 | 0.045777 | -0.16022 | 0.16022 | 0.15106 | 0.091553 | 0.18768 | 0.12817 | 0.096131 | -0.027466 | 0.19684 | 122.937 | 0.24719 | 123.143 | 1.4694 | 123.1064 | -121.8384 | -123.0972 | 1.1948 | 122.9004 | 1.181 | 1.6708
702 | 123.1338 | -1.2772 | 121.6919 | -0.15274 | -0.0026275 | 0.018991 | 0.015344 | 0.00031198 | 0.00062799 | 0.00075845 | 0.062744 | -0.0020636 | 0.0018499 | -0.004313 | 0.0010061 | -0.0031211 | 0.0028967 | -0.073242 | 0.050354 | -0.09613 | -0.027466 | 0.12817 | -0.022888 | 0.073242 | 0.40741 | 121.7285 | -1.3504 | 121.6736 | -1.0254 | -1.0941 | -1.062 | 1.181 | -121.6415 | -121.7194 | 1.4053 | 1.3504 | 1.2543 | 0.16937 | 0.073242 | -0.073242 | 0.036621 | -0.018311 | 0.25177 | 0.21515 | 0.18311 | 0.28839 | 0.25635 | 0.2243 | 0.068664 | 0.32501 | 123.024 | 0.14648 | 123.0789 | 1.3275 | 123.0057 | -121.788 | -123.0423 | 1.2497 | 122.9507 | 1.2039 | 1.6846
703.7031 | 123.0606 | -1.3046 | 121.7377 | -0.12985 | -0.0036957 | 0.018991 | 0.015558 | 0.0037298 | 0.00041439 | -0.00052335 | -0.037964 | 0.0011408 | 0.00035453 | 0.0020956 | -0.0017709 | -0.00077127 | -0.0022301 | -0.11902 | 0.073242 | -0.12817 | -0.086975 | -0.004578 | -0.11902 | -0.022888 | 0.37079 | 121.7606 | -1.3687 | 121.6461 | -1.1124 | -1.2085 | -1.1124 | 1.1765 | -121.6644 | -121.8246 | 1.3 | 1.2817 | 1.1856 | 0.10529 | 0.009155 | -0.064087 | 0.022888 | -0.091553 | 0.19226 | 0.19226 | 0.09613 | 0.25635 | 0.16022 | 0.1236 | 0.041199 | 0.25635 | 123.0148 | 0.20142 | 123.1293 | 1.3779 | 123.0652 | -121.8658 | -123.1064 | 1.2177 | 122.9507 | 1.1856 | 1.6754
705.4219 | 123.0286 | -1.3962 | 121.6965 | -0.13748 | -0.0030547 | 0.016214 | 0.01449 | 0.00095278 | -0.0012946 | 0.0016128 | 0.032227 | 0.0011408 | 0.00056833 | -0.003245 | 0.0012199 | -0.0044029 | 0.00054686 | -0.16022 | 0.068665 | -0.1236 | -0.14648 | 0 | -0.15564 | -0.036621 | 0.28839 | 121.7239 | -1.4145 | 121.5042 | -1.2039 | -1.2863 | -1.2497 | 1.2726 | -121.6278 | -121.843 | 1.3962 | 1.3596 | 1.2405 | 0.086975 | -0.032044 | -0.018311 | 0.027466 | -0.19226 | 0.19226 | 0.14648 | 0.10986 | 0.1648 | 0.12817 | 0.1236 | -0.022888 | 0.21057 | 122.9187 | 0.19226 | 123.1384 | 1.4648 | 123.1201 | -121.8201 | -123.111 | 1.2497 | 122.9004 | 1.236 | 1.6846
707.1094 | 123.0972 | -1.3138 | 121.6553 | -0.19089 | -0.0011321 | 0.0207 | 0.013422 | -0.0011834 | 0.00084159 | -0.0020188 | 0.035278 | -0.00078177 | 0.0020635 | 0.00017297 | 0.0022879 | -0.0039755 | -0.0035119 | -0.10529 | 0.036621 | -0.09613 | -0.041199 | 0.086975 | -0.07782 | 0.032043 | 0.35706 | 121.6965 | -1.3779 | 121.6461 | -1.0986 | -1.1719 | -1.1124 | 1.2177 | -121.6187 | -121.6965 | 1.4008 | 1.3458 | 1.236 | 0.12817 | 0.01831 | -0.064087 | 0.041199 | -0.009155 | 0.21515 | 0.20142 | 0.14191 | 0.2655 | 0.20599 | 0.1831 | 0.054931 | 0.27924 | 123.024 | 0.13275 | 123.0743 | 1.3504 | 123.0103 | -121.7514 | -123.0331 | 1.2726 | 122.9599 | 1.2085 | 1.6708
708.8125 | 123.0194 | -1.4053 | 121.6919 | -0.13748 | -0.0017731 | 0.0207 | 0.020471 | 0.0050116 | -1.2808e-05 | -9.6154e-05 | -0.050171 | 0.0028498 | 0.0012091 | 0.003591 | 0.00036527 | -0.0048301 | -0.0018029 | -0.12817 | 0.086975 | -0.10986 | -0.10529 | -0.018311 | -0.15564 | -0.064087 | 0.32501 | 121.701 | -1.4603 | 121.5271 | -1.2405 | -1.3458 | -1.2543 | 1.2955 | -121.6049 | -121.7972 | 1.387 | 1.3412 | 1.2497 | 0.045776 | -0.045777 | -0.054932 | 0.009155 | -0.16479 | 0.16479 | 0.15106 | 0.059509 | 0.20599 | 0.11444 | 0.091552 | 0.004577 | 0.21973 | 122.9874 | 0.19684 | 123.1613 | 1.4923 | 123.1064 | -121.8018 | -123.1522 | 1.3 | 122.9324 | 1.2772 | 1.7303
710.5156 | 123.0743 | -1.4145 | 121.669 | -0.16037 | -0.0026275 | 0.019205 | 0.018762 | -0.00032902 | 0.0016962 | 0.00075845 | -0.025757 | -0.00035457 | -0.00092707 | 0.0042318 | -0.00027553 | -0.0020529 | 0.00011966 | -0.14191 | 0.09613 | -0.1236 | -0.1236 | -0.027466 | -0.10986 | -0.022888 | 0.34332 | 121.7056 | -1.4648 | 121.5454 | -1.2039 | -1.2817 | -1.2177 | 1.2909 | -121.5729 | -121.7926 | 1.387 | 1.3916 | 1.3046 | 0.10071 | 0.013733 | -0.050354 | 0.036621 | -0.1236 | 0.21057 | 0.19684 | 0.13275 | 0.24719 | 0.18311 | 0.09613 | 0 | 0.26093 | 123.0103 | 0.21973 | 123.1705 | 1.5106 | 123.1201 | -121.7926 | -123.1338 | 1.2909 | 122.9599 | 1.2726 | 1.7578
712.2188 | 123.0103 | -1.4465 | 121.6415 | -0.099335 | -0.0036957 | 0.016428 | 0.015344 | 0.00073918 | -0.00022641 | -9.6154e-05 | 0.02002 | 0.0011408 | 0.0031317 | -0.001536 | 0.0022879 | -0.0039755 | -0.00052114 | -0.17853 | 0.09613 | -0.14191 | -0.16937 | -0.054932 | -0.14191 | -0.041199 | 0.27466 | 121.6736 | -1.4832 | 121.4539 | -1.2772 | -1.3504 | -1.2863 | 1.3046 | -121.5454 | -121.8109 | 1.3916 | 1.4053 | 1.3046 | 0.10071 | 0 | -0.036621 | 0.032043 | -0.18768 | 0.16937 | 0.16022 | 0.09613 | 0.19684 | 0.13275 | 0.086975 | -0.027466 | 0.20599 | 122.937 | 0.23804 | 123.1567 | 1.5427 | 123.1201 | -121.7834 | -123.1247 | 1.2772 | 122.9004 | 1.268 | 1.7212
713.8906 | 123.0606 | -1.4603 | 121.5958 | -0.11459 | -0.0017731 | 0.017282 | 0.015985 | -0.0011834 | 0.00062799 | 0.00075845 | -0.010498 | -0.00035457 | 0.00099553 | -0.0013224 | -0.00070273 | -0.0029075 | 0.00011966 | -0.1236 | 0.07782 | -0.14191 | -0.11902 | -0.013733 | -0.11902 | -0.027466 | 0.32501 | 121.6507 | -1.5106 | 121.5088 | -1.2589 | -1.3412 | -1.2772 | 1.3184 | -121.5179 | -121.7148 | 1.4465 | 1.4328 | 1.3412 | 0.11444 | 0.022888 | -0.050354 | 0.054932 | -0.086975 | 0.20142 | 0.18311 | 0.11902 | 0.23346 | 0.16937 | 0.12817 | 0.022888 | 0.25177 | 123.0194 | 0.21973 | 123.1613 | 1.5381 | 123.111 | -121.7377 | -123.1064 | 1.3412 | 122.9691 | 1.3367 | 1.7853
715.5938 | 123.1064 | -1.4511 | 121.5729 | -0.18326 | 0.00036326 | 0.020273 | 0.019403 | 0.00031198 | 0.0034052 | -0.0015916 | -0.010498 | -0.00014097 | 0.0027045 | -0.00089503 | 0.0012199 | -0.0026939 | 0.0028967 | -0.16479 | 0.086975 | -0.10986 | -0.13275 | -0.018311 | -0.17395 | -0.032043 | 0.30212 | 121.6187 | -1.5152 | 121.5271 | -1.2314 | -1.3321 | -1.2222 | 1.3412 | -121.4859 | -121.7056 | 1.4328 | 1.4191 | 1.2772 | 0.07782 | -0.064087 | -0.064087 | 0.045776 | -0.045776 | 0.21973 | 0.22888 | 0.11902 | 0.29297 | 0.18311 | 0.091552 | -0.022888 | 0.28381 | 123.0423 | 0.19684 | 123.1338 | 1.5381 | 123.0698 | -121.6827 | -123.0881 | 1.3184 | 122.9782 | 1.2863 | 1.7532
717.2812 | 123.1659 | -1.4328 | 121.5637 | -0.17563 | -0.0054047 | 0.020914 | 0.012781 | -0.002038 | 0.0010554 | 0.00075845 | 0.087158 | -0.00035457 | 0.0016363 | -0.0038858 | 0.00079247 | -0.0020529 | 0.0020423 | -0.10986 | 0.045776 | -0.091553 | -0.018311 | 0.10529 | -0.032043 | 0.086975 | 0.42572 | 121.6049 | -1.474 | 121.5775 | -1.1444 | -1.2085 | -1.1856 | 1.3412 | -121.5179 | -121.582 | 1.5381 | 1.5198 | 1.4008 | 0.17853 | 0.05951 | -0.041199 | 0.041198 | 0.013733 | 0.28839 | 0.24719 | 0.2243 | 0.28839 | 0.2655 | 0.19684 | 0.073242 | 0.32959 | 123.0515 | 0.13733 | 123.0789 | 1.4786 | 123.0377 | -121.6553 | -123.0377 | 1.4145 | 123.0103 | 1.3229 | 1.8585
718.9531 | 123.1064 | -1.4099 | 121.6141 | -0.12985 | -0.0013457 | 0.019632 | 0.014276 | 0.00031198 | 0.00084159 | 0.0033218 | 0.056641 | -0.00099557 | 0.00099553 | -0.0045266 | -0.00027553 | -0.0029075 | 0.00076046 | -0.091553 | 0.045776 | -0.082397 | -0.041199 | 0.091553 | -0.041199 | 0.064087 | 0.41657 | 121.6232 | -1.4648 | 121.5637 | -1.1581 | -1.2222 | -1.1902 | 1.3275 | -121.5683 | -121.6553 | 1.5015 | 1.474 | 1.3687 | 0.14648 | 0.041198 | -0.054932 | 0.009155 | -0.050354 | 0.25177 | 0.21973 | 0.18768 | 0.27466 | 0.24262 | 0.17395 | 0.041198 | 0.3067 | 123.0286 | 0.12817 | 123.0881 | 1.4557 | 123.0331 | -121.6965 | -123.0789 | 1.3687 | 122.9736 | 1.3184 | 1.8265
720.6406 | 123.1384 | -1.4374 | 121.5408 | -0.19089 | -0.0051909 | 0.016855 | 0.014704 | 9.818e-05 | 0.002978 | 0.00033105 | 0.056641 | 0.00028623 | 0.0018499 | -0.0045266 | 0.00079247 | -0.0054709 | 0.0016151 | -0.1236 | 0.050354 | -0.086975 | -0.045776 | 0.068665 | -0.064087 | 0.064087 | 0.3479 | 121.5683 | -1.4923 | 121.55 | -1.1856 | -1.2405 | -1.1993 | 1.3504 | -121.4905 | -121.5866 | 1.506 | 1.5015 | 1.3733 | 0.15106 | 0.022888 | -0.054932 | 0.027465 | 0.009155 | 0.25177 | 0.23804 | 0.19684 | 0.29297 | 0.25177 | 0.15564 | 0.041199 | 0.3067 | 123.0423 | 0.13733 | 123.0606 | 1.4877 | 123.0057 | -121.6278 | -123.0331 | 1.3916 | 122.9874 | 1.3138 | 1.7853
722.3125 | 123.0606 | -1.4603 | 121.5958 | -0.16037 | -0.0015595 | 0.017068 | 0.018335 | 0.0024482 | 0.00041439 | 0.0013992 | -0.037964 | 0.0028498 | -0.0013543 | 0.0023092 | -0.0011301 | -0.0016257 | 0.00011966 | -0.1236 | 0.082397 | -0.12817 | -0.082397 | 0.013733 | -0.11902 | -0.004578 | 0.40283 | 121.637 | -1.4832 | 121.5225 | -1.2497 | -1.3458 | -1.2451 | 1.3321 | -121.5134 | -121.6782 | 1.474 | 1.4557 | 1.3412 | 0.1236 | 0.009155 | -0.022888 | 0.041199 | -0.073242 | 0.21057 | 0.21515 | 0.11444 | 0.23804 | 0.13733 | 0.14191 | 0.045777 | 0.23346 | 123.0057 | 0.21057 | 123.1201 | 1.5427 | 123.0972 | -121.7239 | -123.0789 | 1.3779 | 122.9828 | 1.3367 | 1.8631
724.0156 | 123.0286 | -1.4786 | 121.5546 | -0.12222 | -0.0026275 | 0.020059 | 0.018976 | 0.00095278 | 0.00084159 | 0.0016128 | -0.034912 | 0.0013544 | 0.0012091 | 0.00060037 | -0.0011301 | -0.0039755 | 0.0011877 | -0.10986 | 0.073242 | -0.11444 | -0.09613 | 0.004578 | -0.13733 | -0.032043 | 0.35706 | 121.6095 | -1.5381 | 121.463 | -1.2909 | -1.4053 | -1.3046 | 1.3641 | -121.4813 | -121.6507 | 1.4832 | 1.4465 | 1.3412 | 0.082398 | -0.022888 | -0.059509 | 0.054932 | -0.091552 | 0.18768 | 0.17395 | 0.073243 | 0.23346 | 0.13275 | 0.11902 | 0.018311 | 0.24719 | 123.0011 | 0.18768 | 123.1476 | 1.5518 | 123.0881 | -121.669 | -123.0927 | 1.3824 | 122.9416 | 1.3687 | 1.8356
725.6875 | 123.0835 | -1.4923 | 121.5271 | -0.11459 | -0.0028411 | 0.020486 | 0.014704 | 0.0022346 | -1.2808e-05 | -0.0035142 | 0.065796 | 0.0019952 | 0.00056833 | -0.0011086 | 0.00079247 | -0.0044029 | -0.0013757 | -0.091553 | 0.064087 | -0.091553 | -0.045776 | 0.091553 | -0.036621 | 0.059509 | 0.39368 | 121.5454 | -1.5518 | 121.4447 | -1.2589 | -1.3504 | -1.2909 | 1.4008 | -121.463 | -121.5729 | 1.5839 | 1.5518 | 1.4557 | 0.15106 | 0.054932 | -0.059509 | 0.01831 | -0.082398 | 0.23346 | 0.20142 | 0.14191 | 0.26093 | 0.20142 | 0.18311 | 0.045777 | 0.29297 | 122.9965 | 0.15564 | 123.0972 | 1.5564 | 123.0377 | -121.6187 | -123.0789 | 1.4465 | 122.937 | 1.4008 | 1.886
727.3594 | 123.1201 | -1.4557 | 121.5637 | -0.168 | -0.0015595 | 0.021127 | 0.014276 | -0.001397 | 0.00041439 | 0.0016128 | 0.03833 | 0.00028623 | 0.0018499 | -0.003245 | 0.00057887 | -0.0041891 | -0.0022301 | -0.086975 | 0.059509 | -0.086975 | -0.022888 | 0.09613 | -0.041199 | 0.050354 | 0.3891 | 121.5775 | -1.5015 | 121.5225 | -1.1993 | -1.2726 | -1.2314 | 1.3687 | -121.5042 | -121.5866 | 1.5518 | 1.506 | 1.4145 | 0.13733 | 0.045776 | -0.045777 | 0.013733 | -0.041199 | 0.25635 | 0.2243 | 0.18311 | 0.27008 | 0.22888 | 0.1831 | 0.064087 | 0.30212 | 123.024 | 0.14648 | 123.0789 | 1.5152 | 123.0331 | -121.6507 | -123.0652 | 1.4328 | 122.9782 | 1.3687 | 1.8448
729.0312 | 123.0972 | -1.6113 | 121.3989 | -0.18326 | -0.0026275 | 0.018564 | 0.016626 | 0.00138 | 0.00062799 | 0.0024674 | 0.050537 | 0.00049983 | 0.00099553 | -0.00025423 | -0.00027553 | -0.0031211 | 0.00097406 | -0.13275 | 0.064087 | -0.10529 | -0.082397 | 0.032043 | -0.09613 | 0.022888 | 0.25635 | 121.4172 | -1.6434 | 121.3165 | -1.3962 | -1.4694 | -1.4099 | 1.506 | -121.3348 | -121.4813 | 1.6434 | 1.6342 | 1.5152 | 0.12817 | 0.009156 | -0.032044 | 0.01831 | -0.082398 | 0.21515 | 0.20142 | 0.14191 | 0.23346 | 0.17395 | 0.13733 | 0.022889 | 0.24719 | 122.9599 | 0.16937 | 123.0606 | 1.6754 | 123.0286 | -121.5042 | -123.0423 | 1.5289 | 122.9279 | 1.4786 | 1.8677
730.75 | 123.0606 | -1.5244 | 121.5088 | -0.19089 | 0.00014946 | 0.019418 | 0.017908 | 0.0026618 | 0.0027644 | -9.6154e-05 | -0.053223 | 0.0019952 | 0.0033453 | -0.00025423 | -0.0011301 | -0.0052573 | -0.00052114 | -0.091553 | 0.10071 | -0.1236 | -0.086975 | 0.032043 | -0.10529 | -0.009155 | 0.37994 | 121.5546 | -1.5747 | 121.4401 | -1.3412 | -1.4008 | -1.3367 | 1.4008 | -121.4081 | -121.5958 | 1.5564 | 1.5152 | 1.4191 | 0.11444 | 0.01831 | -0.050354 | 0.045776 | -0.068664 | 0.18311 | 0.18768 | 0.1236 | 0.23804 | 0.17395 | 0.15564 | 0.036621 | 0.23346 | 123.0148 | 0.2243 | 123.1293 | 1.6251 | 123.0789 | -121.6324 | -123.0835 | 1.4374 | 122.9645 | 1.4328 | 1.9043
732.4062 | 123.1293 | -1.4557 | 121.5271 | -0.168 | -0.0026275 | 0.017709 | 0.015131 | -0.00075622 | -1.2808e-05 | 0.0011856 | 0.044434 | -0.00056817 | 0.00035453 | 0.0010276 | 0.00036527 | -0.0054709 | 0.0024695 | -0.091553 | 0.064087 | -0.09613 | -0.009155 | 0.12817 | -0.009155 | 0.073242 | 0.44861 | 121.5683 | -1.5335 | 121.5042 | -1.2085 | -1.2817 | -1.2589 | 1.3596 | -121.463 | -121.5363 | 1.5839 | 1.5289 | 1.4465 | 0.16937 | 0.086975 | -0.07782 | 0.041198 | -0.022889 | 0.24719 | 0.19684 | 0.17395 | 0.27466 | 0.25177 | 0.2243 | 0.086975 | 0.32501 | 123.0377 | 0.16022 | 123.1018 | 1.5198 | 123.024 | -121.6232 | -123.0606 | 1.4465 | 122.9599 | 1.3641 | 1.9043
734.0781 | 123.1338 | -1.6251 | 121.3806 | -0.14511 | -0.0030547 | 0.01835 | 0.015344 | -0.0026788 | 0.0021234 | -0.00052335 | 0.065796 | -0.00078177 | -0.00028627 | -0.0030312 | -6.1934e-05 | -0.0037619 | 0.0039649 | -0.1236 | 0.068665 | -0.09613 | -0.032043 | 0.10071 | -0.022888 | 0.091553 | 0.39368 | 121.3989 | -1.68 | 121.3715 | -1.3412 | -1.4099 | -1.3824 | 1.5289 | -121.312 | -121.4127 | 1.7258 | 1.7166 | 1.6022 | 0.18768 | 0.073242 | -0.054932 | 0.018311 | -0.009155 | 0.28381 | 0.24262 | 0.21515 | 0.29755 | 0.27008 | 0.19684 | 0.064087 | 0.33875 | 123.0515 | 0.16479 | 123.0789 | 1.6937 | 123.024 | -121.4767 | -123.0606 | 1.593 | 122.9965 | 1.5015 | 2.0187
735.7344 | 123.1338 | -1.6342 | 121.3394 | -0.14511 | 0.00014946 | 0.020273 | 0.017908 | -0.0035334 | 0.0010554 | 0.0022536 | -0.034912 | 0.0011408 | 0.0016363 | 0.0044456 | 0.00057887 | -0.0033347 | -0.0045801 | -0.12817 | 0.091553 | -0.10986 | -0.059509 | 0.036621 | -0.11444 | 0.027466 | 0.35248 | 121.431 | -1.6891 | 121.3669 | -1.3916 | -1.4786 | -1.3824 | 1.5244 | -121.2479 | -121.3989 | 1.6708 | 1.6617 | 1.5198 | 0.13733 | -0.004578 | -0.054932 | 0.091552 | 0.027465 | 0.24261 | 0.25177 | 0.15564 | 0.3067 | 0.21057 | 0.14648 | 0.050354 | 0.29755 | 123.056 | 0.20142 | 123.1201 | 1.7258 | 123.0652 | -121.4493 | -123.0286 | 1.5747 | 123.0011 | 1.506 | 1.9867
737.4219 | 122.9965 | -1.712 | 121.376 | -0.15274 | -0.00070494 | 0.022409 | 0.018335 | -0.00075622 | -0.00044001 | 0.00054465 | -0.068481 | 0.0022088 | -7.2674e-05 | 0.0076498 | -0.00027553 | -0.0029075 | 0.00033326 | -0.15106 | 0.10071 | -0.12817 | -0.12817 | -0.032043 | -0.16937 | -0.059509 | 0.25177 | 121.4127 | -1.7303 | 121.2341 | -1.561 | -1.6571 | -1.5564 | 1.5839 | -121.2753 | -121.5042 | 1.68 | 1.6525 | 1.5427 | 0.068665 | -0.041199 | -0.018311 | 0.036621 | -0.14191 | 0.15106 | 0.15564 | 0.054932 | 0.17395 | 0.073243 | 0.096131 | 0 | 0.16937 | 122.9645 | 0.22888 | 123.143 | 1.8127 | 123.1247 | -121.5042 | -123.1064 | 1.5839 | 122.9462 | 1.561 | 1.9638
739.0938 | 123.0927 | -1.7029 | 121.2891 | -0.10696 | -0.0024139 | 0.018777 | 0.014276 | -0.0011834 | 0.00084159 | 0.0018264 | 0.023071 | -0.00099557 | 0.0012091 | -0.0028176 | 0.0018607 | -0.0050437 | 0.00011966 | -0.091553 | 0.059509 | -0.10529 | -0.036621 | 0.091553 | -0.045776 | 0.054932 | 0.37537 | 121.2845 | -1.7807 | 121.2387 | -1.4969 | -1.561 | -1.5244 | 1.5976 | -121.2296 | -121.3257 | 1.7944 | 1.7578 | 1.6571 | 0.16022 | 0.05951 | -0.07782 | -0.004577 | -0.050354 | 0.20599 | 0.17853 | 0.14191 | 0.25635 | 0.21973 | 0.19684 | 0.068665 | 0.28381 | 123.0194 | 0.16479 | 123.0652 | 1.7624 | 122.9874 | -121.3943 | -123.0698 | 1.6663 | 122.9416 | 1.6113 | 2.0782
740.7656 | 123.0789 | -1.7715 | 121.2479 | -0.16037 | -0.0030547 | 0.018564 | 0.015558 | -0.00032902 | 0.0019098 | 0.00204 | 0.035278 | 0.00028623 | -0.00071347 | -0.0028176 | 0.00036527 | -0.0031211 | 0.0011877 | -0.12817 | 0.073242 | -0.091553 | -0.10071 | 0.032043 | -0.10986 | 0.004578 | 0.27924 | 121.2616 | -1.8127 | 121.1838 | -1.5472 | -1.6388 | -1.5793 | 1.68 | -121.1746 | -121.3486 | 1.8036 | 1.7761 | 1.6617 | 0.096131 | -0.01831 | -0.041199 | 0.013733 | -0.064087 | 0.2243 | 0.19226 | 0.13275 | 0.23346 | 0.17395 | 0.1236 | -0.009155 | 0.2655 | 122.9965 | 0.16479 | 123.0743 | 1.8448 | 123.0331 | -121.3394 | -123.0606 | 1.6708 | 122.9553 | 1.6434 | 2.0508
742.4375 | 123.1338 | -1.8585 | 121.1151 | -0.19852 | -6.4144e-05 | 0.018777 | 0.018335 | 0.0028754 | 0.00041439 | -0.001378 | -0.025757 | 0.00049983 | 0.0031317 | -0.0038858 | -0.0017709 | -0.0011985 | -0.0013757 | -0.11902 | 0.07782 | -0.10986 | -0.059509 | 0.045776 | -0.10986 | 0.027466 | 0.33417 | 121.17 | -1.9226 | 121.1243 | -1.6479 | -1.7395 | -1.6388 | 1.7487 | -121.0373 | -121.1746 | 1.9043 | 1.886 | 1.7487 | 0.13733 | 0 | -0.064086 | 0.054932 | 0.009156 | 0.21057 | 0.21973 | 0.11902 | 0.28381 | 0.1831 | 0.15564 | 0.050354 | 0.27466 | 123.0469 | 0.18768 | 123.0927 | 1.9363 | 123.0286 | -121.225 | -123.0377 | 1.799 | 122.9828 | 1.7395 | 2.1927
744.1094 | 123.0194 | -1.9684 | 121.1334 | -0.068817 | -0.00091854 | 0.016 | 0.015558 | -0.0039606 | -0.00022641 | -0.0018052 | 0.001709 | 0.0011408 | 0.00056833 | -0.0028176 | -6.1934e-05 | -0.0033347 | 0.0026831 | -0.18768 | 0.11444 | -0.15106 | -0.15564 | -0.041199 | -0.14191 | -0.036621 | 0.29755 | 121.1655 | -2.0187 | 120.9457 | -1.7899 | -1.8906 | -1.8127 | 1.8173 | -121.019 | -121.2891 | 1.9272 | 1.9318 | 1.8265 | 0.11444 | 0.009155 | -0.050354 | 0.032043 | -0.18768 | 0.17853 | 0.15564 | 0.07782 | 0.20599 | 0.12817 | 0.10986 | -0.004578 | 0.22888 | 122.9645 | 0.2655 | 123.1842 | 2.0828 | 123.1338 | -121.2845 | -123.1522 | 1.8127 | 122.9141 | 1.7807 | 2.2659
745.7969 | 123.0698 | -1.9958 | 121.0648 | -0.061188 | -0.0019867 | 0.017923 | 0.017481 | -0.00075622 | -0.0015082 | 0.00075845 | -0.019653 | 0.00049983 | 0.00014093 | 0.002523 | -0.0017709 | -0.0016257 | -0.00052114 | -0.15106 | 0.11902 | -0.13275 | -0.13275 | -0.032043 | -0.14648 | -0.022888 | 0.31128 | 121.1151 | -2.0554 | 120.9457 | -1.7899 | -1.8814 | -1.8082 | 1.8631 | -120.9457 | -121.1975 | 1.9638 | 1.973 | 1.8494 | 0.10986 | -0.013733 | -0.059509 | 0.050354 | -0.11902 | 0.20599 | 0.18768 | 0.11444 | 0.24719 | 0.17395 | 0.10071 | 0 | 0.2655 | 123.0011 | 0.25177 | 123.1705 | 2.1149 | 123.111 | -121.1975 | -123.1201 | 1.8631 | 122.9416 | 1.8448 | 2.3071
747.5 | 123.0148 | -2.0187 | 121.0556 | -0.068817 | -0.0017731 | 0.01835 | 0.016199 | -0.00032902 | -0.00086721 | 0.0011856 | -0.01355 | 0.0019952 | 0.00099553 | -0.0011086 | 0.0018607 | -0.0044029 | -0.0013757 | -0.17853 | 0.09613 | -0.12817 | -0.16022 | -0.041199 | -0.14191 | -0.036621 | 0.29755 | 121.0876 | -2.0599 | 120.8954 | -1.8448 | -1.9363 | -1.8448 | 1.8906 | -120.9595 | -121.2158 | 1.9775 | 1.9821 | 1.8768 | 0.091553 | -0.013733 | -0.041199 | 0.032043 | -0.16022 | 0.17395 | 0.17395 | 0.082398 | 0.21515 | 0.1236 | 0.086975 | -0.032043 | 0.21515 | 122.9553 | 0.2243 | 123.1476 | 2.1149 | 123.1064 | -121.1838 | -123.1155 | 1.8585 | 122.9141 | 1.8402 | 2.3163
749.1719 | 123.0606 | -1.9958 | 121.0373 | -0.13748 | -0.0032683 | 0.018777 | 0.018762 | -0.00075622 | 0.0010554 | 0.0013992 | -0.028809 | 0.0024224 | 0.00035453 | 0.0044456 | -0.0013437 | -0.0039755 | -0.0030847 | -0.12817 | 0.091553 | -0.13733 | -0.10529 | 0.022888 | -0.10071 | -0.022888 | 0.38452 | 121.0922 | -2.0554 | 120.9595 | -1.799 | -1.8906 | -1.8082 | 1.8585 | -120.9457 | -121.1426 | 2.0187 | 1.973 | 1.8951 | 0.11444 | 0.036621 | -0.059509 | 0.054932 | -0.077819 | 0.19684 | 0.18768 | 0.10529 | 0.24719 | 0.1648 | 0.16022 | 0.032043 | 0.25635 | 123.0148 | 0.22888 | 123.1476 | 2.0874 | 123.0881 | -121.1746 | -123.0927 | 1.8906 | 122.9553 | 1.8677 | 2.3804
750.8594 | 123.056 | -2.0508 | 121.0281 | -0.13748 | -0.0011321 | 0.018991 | 0.01684 | 0.00138 | 0.0016962 | 0.0018264 | -0.0074462 | 0.00071343 | 0.0020635 | -0.001536 | 0.00036527 | -0.0037619 | 0.0035377 | -0.15564 | 0.10529 | -0.10986 | -0.1236 | -0.027466 | -0.14648 | -0.045776 | 0.32044 | 121.0556 | -2.0966 | 120.9 | -1.8448 | -1.9547 | -1.8768 | 1.9409 | -120.9229 | -121.1517 | 2.0233 | 2.005 | 1.9043 | 0.064087 | -0.036621 | -0.045777 | 0.027466 | -0.12817 | 0.20599 | 0.17395 | 0.09613 | 0.21973 | 0.14191 | 0.082397 | -0.013733 | 0.25177 | 122.9965 | 0.21515 | 123.1522 | 2.1561 | 123.1064 | -121.138 | -123.1247 | 1.9272 | 122.9507 | 1.8951 | 2.3712
752.625 | 123.111 | -2.0737 | 120.9503 | -0.16037 | -0.0045501 | 0.019418 | 0.013208 | -0.002038 | -0.001081 | 0.0016128 | 0.053589 | 0.00028623 | 0.0018499 | -0.006022 | 0.0010061 | -0.0033347 | 0.0016151 | -0.07782 | 0.064087 | -0.086975 | -0.022888 | 0.09613 | -0.041199 | 0.064087 | 0.44403 | 120.9549 | -2.124 | 120.9045 | -1.8082 | -1.8997 | -1.8494 | 1.9867 | -120.8862 | -120.9732 | 2.1698 | 2.1378 | 2.0325 | 0.15106 | 0.045776 | -0.050354 | 0.004578 | -0.045776 | 0.2655 | 0.2243 | 0.17395 | 0.27466 | 0.2243 | 0.1831 | 0.064087 | 0.31586 | 123.0286 | 0.15106 | 123.0789 | 2.1378 | 123.0286 | -121.0373 | -123.0743 | 2.0508 | 122.9782 | 1.9958 | 2.5177
754.3281 | 123.1293 | -2.1973 | 120.7809 | -0.13748 | -0.0011321 | 0.020486 | 0.016199 | 0.0039436 | 0.0027644 | -0.001378 | 0.001709 | -0.00035457 | 0.0014227 | -0.00025423 | 0.00036527 | -0.0026939 | -9.3938e-05 | -0.091553 | 0.059509 | -0.09613 | -0.022888 | 0.082397 | -0.07782 | 0.041199 | 0.35248 | 120.7947 | -2.2659 | 120.8176 | -1.9638 | -2.0325 | -1.9318 | 2.1011 | -120.7214 | -120.8038 | 2.2797 | 2.2385 | 2.1194 | 0.13733 | 0.01831 | -0.068664 | 0.013733 | 0.036621 | 0.23346 | 0.2655 | 0.16479 | 0.33417 | 0.23346 | 0.17853 | 0.073242 | 0.30212 | 123.0835 | 0.15564 | 123.0606 | 2.2568 | 122.9919 | -120.8771 | -123.0469 | 2.1744 | 123.0148 | 2.1057 | 2.5497
756.0156 | 123.024 | -2.2476 | 120.8221 | -0.17563 | -0.00070494 | 0.016855 | 0.017267 | 9.818e-05 | 0.00084159 | 0.00033105 | 0.0047608 | 0.0028498 | -0.00028627 | 0.0023092 | 0.00015167 | -0.0050437 | -0.00030754 | -0.17853 | 0.091553 | -0.13733 | -0.17853 | -0.036621 | -0.15106 | -0.041199 | 0.3067 | 120.8496 | -2.2934 | 120.6482 | -2.092 | -2.179 | -2.1057 | 2.1103 | -120.7306 | -121.0007 | 2.211 | 2.2064 | 2.0966 | 0.09613 | -0.013733 | -0.045776 | 0.027465 | -0.17395 | 0.15564 | 0.14191 | 0.068665 | 0.18768 | 0.11444 | 0.10071 | -0.041199 | 0.20142 | 122.9416 | 0.22888 | 123.143 | 2.3392 | 123.0972 | -120.9595 | -123.1155 | 2.0691 | 122.8958 | 2.0691 | 2.5543
757.75 | 123.1293 | -2.1332 | 120.8633 | -0.20615 | -0.0047637 | 0.020273 | 0.015985 | -0.0022516 | -0.00044001 | -0.0018052 | 0.078003 | -0.00014097 | 0.0029181 | 0.001882 | 0.00015167 | -0.0050437 | -0.0011621 | -0.13275 | 0.054932 | -0.11902 | -0.068665 | 0.045776 | -0.091553 | 0.036621 | 0.34332 | 120.9229 | -2.179 | 120.8313 | -1.9089 | -1.9684 | -1.9089 | 2.0142 | -120.8084 | -120.932 | 2.179 | 2.1698 | 2.0416 | 0.15564 | 0.027466 | -0.045776 | 0.05951 | -0.032043 | 0.2243 | 0.2243 | 0.1648 | 0.27008 | 0.21057 | 0.16479 | 0.050354 | 0.27008 | 123.0103 | 0.17395 | 123.1018 | 2.1881 | 123.056 | -120.9824 | -123.0423 | 2.0645 | 122.9645 | 2.0004 | 2.4765
759.4844 | 123.0469 | -2.2202 | 120.8267 | -0.091705 | -0.0011321 | 0.019418 | 0.018122 | 0.0011664 | 0.00020079 | 0.00075845 | 0.016968 | 0.00049983 | 0.00035453 | 0.00017297 | -0.0021981 | -0.0046165 | -0.00094854 | -0.16479 | 0.09613 | -0.13275 | -0.14648 | -0.054932 | -0.15564 | -0.045776 | 0.30212 | 120.8908 | -2.2751 | 120.726 | -2.037 | -2.1149 | -2.037 | 2.0874 | -120.7306 | -120.9732 | 2.1652 | 2.1744 | 2.0645 | 0.086975 | -0.022889 | -0.054931 | 0.064087 | -0.10071 | 0.18311 | 0.18311 | 0.10529 | 0.23804 | 0.16022 | 0.077819 | -0.013733 | 0.23804 | 123.0011 | 0.22888 | 123.1659 | 2.3163 | 123.111 | -120.9595 | -123.1018 | 2.0737 | 122.9462 | 2.0554 | 2.5223
761.2188 | 123.0057 | -2.2156 | 120.8038 | -0.18326 | 0.0024995 | 0.020059 | 0.017053 | -0.0060968 | 0.004046 | 0.00054465 | -0.053223 | 0.00092703 | 0.0018499 | 0.0048728 | 0.0016471 | -0.0041891 | -0.0032983 | -0.14191 | 0.10071 | -0.13275 | -0.16937 | -0.09613 | -0.2243 | -0.091553 | 0.27466 | 120.8679 | -2.2888 | 120.6894 | -2.0828 | -2.1881 | -2.0737 | 2.0828 | -120.7031 | -120.9732 | 2.1194 | 2.124 | 1.9913 | 0.041198 | -0.091553 | -0.073242 | 0.064087 | -0.11444 | 0.13275 | 0.14191 | 0.027466 | 0.21515 | 0.10071 | 0.036621 | -0.036622 | 0.20599 | 122.9782 | 0.23346 | 123.1567 | 2.3163 | 123.0835 | -120.9366 | -123.0927 | 2.0462 | 122.905 | 2.0737 | 2.4902
762.9375 | 123.0148 | -2.1423 | 120.9137 | -0.10696 | -0.0015595 | 0.018991 | 0.018335 | -0.00032902 | 0.00084159 | 0.00097205 | -0.062378 | 0.00071343 | 0.00014093 | -0.00068143 | -0.00027553 | -0.0039755 | 0.00011966 | -0.1236 | 0.091553 | -0.11444 | -0.10986 | 0.004578 | -0.13733 | -0.032043 | 0.36163 | 120.9732 | -2.1881 | 120.7901 | -1.9821 | -2.1057 | -1.9958 | 2.0279 | -120.8221 | -121.0236 | 2.1469 | 2.1103 | 2.005 | 0.082398 | -0.022888 | -0.045776 | 0.05951 | -0.1236 | 0.16022 | 0.14648 | 0.036621 | 0.19226 | 0.082397 | 0.11902 | 0.004578 | 0.20599 | 122.9782 | 0.20599 | 123.1613 | 2.2339 | 123.1155 | -121.0281 | -123.1018 | 2.0325 | 122.9324 | 2.0187 | 2.504
764.6562 | 123.0011 | -2.1927 | 120.8954 | -0.14511 | -6.4144e-05 | 0.018777 | 0.019403 | 0.0039436 | 0.0025506 | 0.0013992 | -0.037964 | 0.0013544 | 0.0024909 | -0.0013224 | 0.0016471 | -0.0024803 | -9.3938e-05 | -0.14191 | 0.073242 | -0.10529 | -0.14648 | -0.036621 | -0.17853 | -0.064087 | 0.2655 | 120.9183 | -2.243 | 120.7169 | -2.0554 | -2.1561 | -2.0462 | 2.0874 | -120.8221 | -121.0419 | 2.1561 | 2.1286 | 2.0142 | 0.041199 | -0.073242 | -0.050354 | 0.022888 | -0.17853 | 0.13733 | 0.14648 | 0.036621 | 0.19684 | 0.086975 | 0.068665 | -0.041198 | 0.18768 | 122.9599 | 0.17853 | 123.1613 | 2.2659 | 123.111 | -121.0007 | -123.1384 | 2.0462 | 122.9095 | 2.0508 | 2.4582
766.3438 | 123.0972 | -2.211 | 120.7764 | -0.18326 | -6.4144e-05 | 0.017923 | 0.01449 | 0.00095278 | -0.00044001 | 0.00054465 | 0.059692 | 0.00092703 | 0.0012091 | -0.0079446 | 0.0016471 | -0.0050437 | 0.0035377 | -0.14191 | 0.054932 | -0.09613 | -0.09613 | 0.054932 | -0.10071 | 0.009155 | 0.3067 | 120.8313 | -2.2705 | 120.7169 | -2.0279 | -2.1149 | -2.0233 | 2.1149 | -120.7214 | -120.8725 | 2.2659 | 2.2202 | 2.1103 | 0.10528 | -0.004578 | -0.059509 | 0.054932 | -0.059509 | 0.18311 | 0.18768 | 0.096131 | 0.24719 | 0.15564 | 0.15106 | 0 | 0.24261 | 122.9874 | 0.15106 | 123.1018 | 2.2659 | 123.0423 | -120.8725 | -123.0469 | 2.1149 | 122.9279 | 2.0691 | 2.5177
768.0625 | 123.0286 | -2.2064 | 120.8542 | -0.099335 | -0.0032683 | 0.018991 | 0.01684 | -0.00075622 | -1.2808e-05 | -9.6154e-05 | -0.0013428 | -0.00014097 | 0.0031317 | -0.0045266 | -0.00091653 | -0.0050437 | 0.00011966 | -0.16937 | 0.10529 | -0.13275 | -0.16022 | -0.041199 | -0.14648 | -0.050354 | 0.33417 | 120.9045 | -2.2614 | 120.694 | -2.0508 | -2.124 | -2.0554 | 2.0737 | -120.7489 | -121.0144 | 2.1652 | 2.1561 | 2.0599 | 0.082397 | -0.013733 | -0.054932 | 0.050354 | -0.16022 | 0.15564 | 0.15106 | 0.082398 | 0.20599 | 0.13733 | 0.091552 | -0.027466 | 0.21057 | 122.9553 | 0.23804 | 123.1659 | 2.3117 | 123.111 | -120.9869 | -123.1155 | 2.0462 | 122.9004 | 2.037 | 2.5406
769.7812 | 123.143 | -2.2385 | 120.7489 | -0.15274 | -0.0047637 | 0.020059 | 0.011926 | -0.001397 | 0.0025506 | -0.00095055 | 0.068848 | 7.2626e-05 | 0.00056833 | -0.006022 | -0.00027553 | -0.0024803 | -0.0020165 | -0.09613 | 0.059509 | -0.09613 | -0.032043 | 0.11902 | -0.018311 | 0.07782 | 0.45776 | 120.7718 | -2.2888 | 120.7489 | -1.9592 | -2.0554 | -2.0187 | 2.1423 | -120.6894 | -120.7809 | 2.3575 | 2.3163 | 2.2202 | 0.17395 | 0.077819 | -0.050354 | 0.022889 | 0 | 0.27923 | 0.21973 | 0.1831 | 0.27008 | 0.23346 | 0.21515 | 0.064087 | 0.32959 | 123.0377 | 0.15564 | 123.0606 | 2.298 | 123.0103 | -120.845 | -123.0377 | 2.2064 | 122.9874 | 2.1423 | 2.6962
771.4844 | 123.0148 | -2.2156 | 120.8542 | -0.17563 | -0.0039093 | 0.017068 | 0.015772 | -0.0016106 | 0.0010554 | 0.00204 | 0.0078126 | 0.00092703 | 0.00035453 | -0.0070902 | 0.00079247 | -0.0031211 | 0.00097406 | -0.16479 | 0.091553 | -0.13275 | -0.15106 | -0.018311 | -0.14648 | -0.027466 | 0.31586 | 120.9045 | -2.2385 | 120.6848 | -2.0416 | -2.1286 | -2.0782 | 2.0828 | -120.7626 | -121.0052 | 2.1973 | 2.1881 | 2.0691 | 0.10529 | -0.013733 | -0.022888 | 0.050354 | -0.16937 | 0.17395 | 0.13733 | 0.086975 | 0.16022 | 0.10986 | 0.11444 | -0.018311 | 0.19684 | 122.9233 | 0.2243 | 123.143 | 2.3071 | 123.1201 | -120.9869 | -123.0927 | 2.0645 | 122.9004 | 2.0508 | 2.5314
773.1719 | 123.0423 | -2.2522 | 120.8267 | -0.12985 | -6.4144e-05 | 0.016428 | 0.017053 | 0.0011664 | -1.2808e-05 | -0.0015916 | -0.010498 | 0.0024224 | 0.00078193 | -0.0058084 | 0.00036527 | -0.0054709 | 0.0011877 | -0.15106 | 0.10529 | -0.13275 | -0.15564 | -0.050354 | -0.15106 | -0.045776 | 0.32044 | 120.8588 | -2.2934 | 120.6894 | -2.0599 | -2.1561 | -2.0737 | 2.1194 | -120.7214 | -120.9824 | 2.2018 | 2.2064 | 2.1011 | 0.086975 | -0.018311 | -0.041199 | 0.032044 | -0.13733 | 0.19226 | 0.17853 | 0.09613 | 0.21973 | 0.13733 | 0.082397 | -0.022889 | 0.23346 | 122.9828 | 0.23804 | 123.1522 | 2.3575 | 123.111 | -120.9595 | -123.1201 | 2.0966 | 122.9416 | 2.1011 | 2.5726
774.875 | 123.0835 | -2.2385 | 120.7718 | -0.13748 | -0.00070494 | 0.017709 | 0.014276 | -0.0033196 | 0.00084159 | 0.0011856 | 0.03833 | -0.00035457 | -7.2674e-05 | 0.0016684 | 0.0010061 | -0.0037619 | 0.00054686 | -0.086975 | 0.054932 | -0.10986 | -0.041199 | 0.09613 | -0.036621 | 0.059509 | 0.42572 | 120.8084 | -2.2705 | 120.7077 | -2.0096 | -2.0828 | -2.0416 | 2.1286 | -120.7169 | -120.813 | 2.3346 | 2.298 | 2.2018 | 0.16937 | 0.073242 | -0.032044 | 0.036621 | -0.064087 | 0.22888 | 0.19684 | 0.15564 | 0.22888 | 0.18768 | 0.20599 | 0.068664 | 0.26092 | 122.9782 | 0.16479 | 123.0789 | 2.2934 | 123.0469 | -120.8817 | -123.0423 | 2.1973 | 122.9462 | 2.1515 | 2.6642
776.625 | 123.1018 | -2.1927 | 120.7581 | -0.19089 | 0.00014946 | 0.020486 | 0.015344 | -0.00075622 | 0.0025506 | 0.00011745 | 0.026123 | 0.0013544 | 0.0014227 | -0.010935 | 0.00079247 | -0.0052573 | -0.00094854 | -0.091553 | 0.059509 | -0.073242 | -0.050354 | 0.10529 | -0.07782 | 0.041199 | 0.39368 | 120.7993 | -2.2568 | 120.7443 | -1.9958 | -2.0874 | -2.0233 | 2.1194 | -120.6985 | -120.8084 | 2.298 | 2.2339 | 2.1149 | 0.11444 | -0.004578 | -0.064087 | 0.041198 | -0.013733 | 0.19684 | 0.16937 | 0.10529 | 0.23346 | 0.16937 | 0.17853 | 0.022888 | 0.26093 | 123.0011 | 0.13275 | 123.056 | 2.2522 | 122.9919 | -120.8313 | -123.0148 | 2.1423 | 122.937 | 2.1011 | 2.5864
778.3125 | 123.0194 | -2.2476 | 120.813 | -0.19089 | -0.0013457 | 0.017709 | 0.018122 | 0.0011664 | 0.0051142 | 0.0013992 | -0.068481 | -0.00056817 | 0.0024909 | 0.0074362 | 0.0012199 | -0.0037619 | -0.0011621 | -0.13733 | 0.086975 | -0.1236 | -0.16937 | -0.073242 | -0.18768 | -0.064087 | 0.27466 | 120.8588 | -2.2842 | 120.694 | -2.1011 | -2.1881 | -2.0782 | 2.124 | -120.726 | -120.9824 | 2.1744 | 2.1835 | 2.0599 | 0.059509 | -0.064087 | -0.036621 | 0.045777 | -0.11902 | 0.14648 | 0.16937 | 0.05951 | 0.20599 | 0.096131 | 0.050354 | -0.045777 | 0.18311 | 122.9782 | 0.21057 | 123.143 | 2.3346 | 123.1064 | -120.9366 | -123.0972 | 2.0782 | 122.9416 | 2.1103 | 2.5223
780.0156 | 123.0103 | -2.2842 | 120.7855 | -0.18326 | -0.0024139 | 0.019846 | 0.018122 | 0.003089 | -0.00022641 | -0.0028732 | -0.044067 | 7.2626e-05 | 0.0012091 | -0.00025423 | -0.00027553 | -0.0041891 | -0.0015893 | -0.1236 | 0.09613 | -0.1236 | -0.11902 | 0 | -0.14648 | -0.050354 | 0.34332 | 120.8038 | -2.3254 | 120.6482 | -2.1194 | -2.2293 | -2.1103 | 2.1606 | -120.6894 | -120.9045 | 2.2842 | 2.2339 | 2.1378 | 0.073242 | -0.022888 | -0.041198 | 0.018311 | -0.13733 | 0.1648 | 0.17395 | 0.054932 | 0.21515 | 0.09613 | 0.1236 | 0.004577 | 0.20599 | 122.9736 | 0.21973 | 123.1293 | 2.3804 | 123.0881 | -120.9091 | -123.111 | 2.1652 | 122.9324 | 2.1606 | 2.6276
781.7344 | 123.0652 | -2.1332 | 120.9 | -0.15274 | -0.0011321 | 0.018991 | 0.017694 | -0.0022516 | 0.002337 | -0.00095055 | -0.053223 | 0.001568 | 0.0012091 | -4.063e-05 | 0.0014335 | -0.0037619 | -0.0022301 | -0.10071 | 0.086975 | -0.11444 | -0.07782 | 0.027466 | -0.11444 | -0.022888 | 0.40283 | 120.9457 | -2.1927 | 120.8313 | -1.9318 | -2.037 | -1.9455 | 2.0187 | -120.813 | -120.9778 | 2.1606 | 2.1103 | 2.0187 | 0.091553 | 0 | -0.059509 | 0.045777 | -0.068664 | 0.20142 | 0.18768 | 0.096131 | 0.24719 | 0.15564 | 0.14191 | 0.036621 | 0.26093 | 123.024 | 0.20142 | 123.1384 | 2.2202 | 123.0789 | -121.0144 | -123.0927 | 2.0554 | 122.9645 | 2.0325 | 2.536
783.4375 | 123.1338 | -2.1698 | 120.8084 | -0.14511 | -0.0019867 | 0.022195 | 0.014917 | 0.0015936 | 0.0021234 | 0.0018264 | 0.03833 | -0.00056817 | -0.00071347 | -0.010294 | 0.0022879 | -0.0037619 | -9.3938e-05 | -0.091553 | 0.041199 | -0.091553 | -0.027466 | 0.091553 | -0.059509 | 0.041199 | 0.40741 | 120.8221 | -2.2293 | 120.813 | -1.9318 | -2.0233 | -1.9318 | 2.0782 | -120.7672 | -120.8359 | 2.2614 | 2.211 | 2.1103 | 0.13275 | 0.032044 | -0.059509 | 0.013733 | 0.004577 | 0.23804 | 0.23804 | 0.14648 | 0.29755 | 0.20599 | 0.18311 | 0.064087 | 0.29755 | 123.0423 | 0.13275 | 123.0515 | 2.211 | 122.9919 | -120.9 | -123.0377 | 2.1423 | 122.9828 | 2.0782 | 2.5772
785.0938 | 123.0103 | -2.1744 | 120.8908 | -0.16037 | -0.0011321 | 0.019418 | 0.016413 | 0.0045844 | 0.001269 | 0.0011856 | -0.047119 | 0.001568 | 0.00099553 | 0.0038046 | 0.0012199 | -0.0037619 | 0.00054686 | -0.15106 | 0.10071 | -0.14191 | -0.16022 | -0.09613 | -0.21515 | -0.10529 | 0.2655 | 120.9229 | -2.2202 | 120.7214 | -2.0508 | -2.1423 | -2.0187 | 2.0325 | -120.7901 | -121.051 | 2.0782 | 2.0691 | 1.9592 | 0.036621 | -0.073242 | -0.045777 | 0.032044 | -0.16937 | 0.1236 | 0.15564 | 0.032043 | 0.20142 | 0.07782 | 0.045777 | -0.01831 | 0.16937 | 122.9416 | 0.24262 | 123.143 | 2.2751 | 123.0972 | -121.0327 | -123.111 | 2.0142 | 122.8958 | 2.0233 | 2.4399
786.7969 | 123.0652 | -2.3483 | 120.7352 | -0.12222 | 0.0016449 | 0.019632 | 0.018976 | 0.0039436 | 0.00020079 | 0.0018264 | -0.028809 | -0.00078177 | -0.00028627 | 0.0014548 | 0.0010061 | -0.0044029 | 0.00076046 | -0.10986 | 0.10071 | -0.10986 | -0.09613 | 0.022888 | -0.13275 | -0.041199 | 0.4303 | 120.7489 | -2.3666 | 120.6162 | -2.1423 | -2.2202 | -2.1469 | 2.2385 | -120.6345 | -120.8313 | 2.3712 | 2.3071 | 2.2156 | 0.068664 | -0.022888 | -0.01831 | 0.013733 | -0.11902 | 0.20599 | 0.20142 | 0.12817 | 0.21973 | 0.14648 | 0.13275 | 0.013733 | 0.2243 | 122.9828 | 0.21057 | 123.1155 | 2.449 | 123.0972 | -120.845 | -123.1018 | 2.2522 | 122.9645 | 2.2385 | 2.7786
788.5469 | 123.0881 | -2.3346 | 120.639 | -0.19852 | -0.0043365 | 0.01835 | 0.015558 | -0.002038 | 0.00020079 | 0.00097205 | 0.074951 | 0.0019952 | -7.2674e-05 | -0.0045266 | 0.00036527 | -0.0050437 | 0.0046057 | -0.10071 | 0.054932 | -0.082397 | -0.07782 | 0.050354 | -0.09613 | 0.013733 | 0.36163 | 120.6436 | -2.3987 | 120.5933 | -2.1469 | -2.2202 | -2.1378 | 2.2522 | -120.5841 | -120.7169 | 2.3849 | 2.3483 | 2.2385 | 0.09613 | -0.013733 | -0.064087 | 0.004578 | -0.045776 | 0.18768 | 0.19684 | 0.11444 | 0.26093 | 0.17853 | 0.13275 | 0.004577 | 0.25177 | 122.9919 | 0.13733 | 123.0423 | 2.3895 | 122.9782 | -120.7214 | -123.0377 | 2.2568 | 122.9279 | 2.2339 | 2.6962
790.2656 | 123.0743 | -2.3026 | 120.7031 | -0.099335 | -0.0015595 | 0.020914 | 0.014917 | 0.0018072 | -0.00065361 | 0.0018264 | 0.062744 | 0.0017816 | 0.00014093 | -0.0055948 | -0.0011301 | -0.0041891 | 0.00033326 | -0.086975 | 0.045776 | -0.082397 | -0.036621 | 0.073242 | -0.059509 | 0.059509 | 0.48065 | 120.726 | -2.3529 | 120.6207 | -2.0691 | -2.1378 | -2.1057 | 2.2202 | -120.6573 | -120.7397 | 2.3758 | 2.3621 | 2.243 | 0.14191 | 0.022888 | -0.050354 | 0.022888 | -0.082397 | 0.23346 | 0.19684 | 0.16479 | 0.24719 | 0.21515 | 0.15564 | 0.045776 | 0.28381 | 122.9736 | 0.12817 | 123.0789 | 2.3483 | 123.0286 | -120.7855 | -123.056 | 2.2659 | 122.9233 | 2.2156 | 2.7832
791.9375 | 123.1018 | -2.3071 | 120.6894 | -0.18326 | -0.0026275 | 0.018991 | 0.015131 | 9.818e-05 | 0.0010554 | 0.00033105 | 0.068848 | 0.00028623 | 0.0027045 | -0.0073038 | 0.00057887 | -0.0044029 | -0.0011621 | -0.082397 | 0.045776 | -0.091553 | -0.022888 | 0.082397 | -0.036621 | 0.054932 | 0.48981 | 120.694 | -2.3529 | 120.607 | -2.0828 | -2.1423 | -2.1011 | 2.2156 | -120.6436 | -120.7123 | 2.3895 | 2.3621 | 2.2705 | 0.14649 | 0.054932 | -0.045776 | 0.004578 | -0.082397 | 0.2243 | 0.20599 | 0.1648 | 0.25177 | 0.21057 | 0.17395 | 0.068665 | 0.27008 | 122.9599 | 0.13733 | 123.0469 | 2.3529 | 123.0011 | -120.7809 | -123.0423 | 2.2842 | 122.9141 | 2.2247 | 2.7969
793.6406 | 123.0103 | -2.4124 | 120.607 | -0.17563 | -0.00070494 | 0.019632 | 0.017908 | -0.00011542 | 0.0021234 | 0.0022536 | -0.074585 | 7.2626e-05 | 0.0014227 | -4.063e-05 | 0.00057887 | -0.0026939 | -0.00094854 | -0.10071 | 0.07782 | -0.10986 | -0.10071 | -0.009155 | -0.13733 | -0.041199 | 0.42572 | 120.6482 | -2.4673 | 120.5063 | -2.243 | -2.3529 | -2.2568 | 2.3026 | -120.5292 | -120.7077 | 2.4033 | 2.3712 | 2.2751 | 0.068664 | -0.027466 | -0.054931 | 0.041198 | -0.10071 | 0.16937 | 0.15564 | 0.05951 | 0.21057 | 0.11444 | 0.10071 | 0.009155 | 0.2243 | 122.9736 | 0.18768 | 123.1155 | 2.4902 | 123.0606 | -120.7169 | -123.0743 | 2.3117 | 122.9187 | 2.3117 | 2.8381
795.375 | 123.1201 | -2.3666 | 120.5887 | -0.13748 | -0.0036957 | 0.019632 | 0.015558 | -0.0033196 | 0.00041439 | -9.6154e-05 | 0.084106 | 0.00071343 | 0.00056833 | -0.0066628 | 0.0010061 | -0.0052573 | 0.00097406 | -0.1236 | 0.054932 | -0.091553 | -0.064087 | 0.054932 | -0.059509 | 0.050354 | 0.43488 | 120.6345 | -2.4216 | 120.5841 | -2.1103 | -2.1744 | -2.1423 | 2.2751 | -120.5338 | -120.6528 | 2.4216 | 2.417 | 2.3071 | 0.14191 | 0.032044 | -0.054932 | 0.045776 | -0.004578 | 0.25635 | 0.2243 | 0.19226 | 0.27924 | 0.24719 | 0.14649 | 0.027466 | 0.31128 | 123.0057 | 0.14649 | 123.056 | 2.4216 | 123.0011 | -120.6802 | -123.0103 | 2.3026 | 122.9507 | 2.243 | 2.8015
797.0625 | 122.9874 | -2.298 | 120.7123 | -0.18326 | -0.0015595 | 0.019205 | 0.019831 | 0.00095278 | 0.0027644 | -0.0011642 | -0.047119 | 0.0024224 | 0.00078193 | -0.0017496 | -0.00091653 | -0.0046165 | 0.0016151 | -0.12817 | 0.10071 | -0.1236 | -0.15564 | -0.07782 | -0.19684 | -0.082397 | 0.34332 | 120.7718 | -2.3392 | 120.6253 | -2.1332 | -2.243 | -2.1378 | 2.1744 | -120.6116 | -120.8679 | 2.2202 | 2.2156 | 2.1011 | 0.041199 | -0.073242 | -0.041198 | 0.05951 | -0.086975 | 0.16479 | 0.16022 | 0.054932 | 0.20142 | 0.09613 | 0.045776 | -0.032044 | 0.20599 | 122.9645 | 0.2243 | 123.111 | 2.3987 | 123.0698 | -120.8359 | -123.0515 | 2.1423 | 122.9233 | 2.1698 | 2.6413
798.7344 | 122.9828 | -2.2476 | 120.7626 | -0.12222 | 0.00057686 | 0.021127 | 0.019617 | 9.818e-05 | 0.00084159 | -0.0022324 | -0.053223 | 0.0019952 | 0.0024909 | 0.0065818 | 0.00057887 | -0.0041891 | 0.00054686 | -0.10986 | 0.09613 | -0.11902 | -0.1236 | -0.027466 | -0.15564 | -0.059509 | 0.39825 | 120.8313 | -2.3209 | 120.6253 | -2.1332 | -2.2156 | -2.124 | 2.1286 | -120.6665 | -120.8862 | 2.2202 | 2.1881 | 2.092 | 0.05951 | -0.036621 | -0.073242 | 0.068665 | -0.13733 | 0.11444 | 0.1236 | 0.032044 | 0.19684 | 0.10529 | 0.091553 | -0.004577 | 0.18768 | 122.9462 | 0.21515 | 123.1522 | 2.3438 | 123.0789 | -120.8817 | -123.0835 | 2.124 | 122.8729 | 2.1378 | 2.6459
800.4375 | 123.1247 | -2.243 | 120.7443 | -0.23666 | -0.0024139 | 0.019205 | 0.015344 | -0.002038 | 0.0016962 | -0.00073695 | 0.09021 | 0.0017816 | 0.0018499 | -0.0013224 | -0.00048913 | -0.0035483 | -0.0026575 | -0.10529 | 0.068665 | -0.10986 | -0.045776 | 0.091553 | -0.041199 | 0.068665 | 0.45319 | 120.7352 | -2.3117 | 120.7123 | -1.973 | -2.0599 | -2.0096 | 2.1332 | -120.6757 | -120.7901 | 2.3346 | 2.3117 | 2.2018 | 0.17853 | 0.068664 | -0.068665 | -0.009156 | -0.032044 | 0.27008 | 0.23346 | 0.1831 | 0.30212 | 0.25177 | 0.20142 | 0.064087 | 0.33875 | 123.024 | 0.17853 | 123.0469 | 2.3117 | 122.9782 | -120.8542 | -123.056 | 2.1973 | 122.9553 | 2.1378 | 2.6962
802.1094 | 123.1155 | -2.1561 | 120.7993 | -0.091705 | -0.0030547 | 0.019632 | 0.014704 | -0.0039606 | 0.00062799 | -0.00052335 | 0.071899 | -0.00056817 | 0.0012091 | -0.0079446 | 0.0016471 | -0.0054709 | -0.00094854 | -0.086975 | 0.059509 | -0.091553 | -0.022888 | 0.14191 | -0.022888 | 0.10071 | 0.54016 | 120.8221 | -2.2064 | 120.8084 | -1.8906 | -1.9684 | -1.9318 | 2.0645 | -120.7397 | -120.8221 | 2.298 | 2.2568 | 2.1332 | 0.19226 | 0.068665 | -0.050354 | 0.022889 | 0.009156 | 0.2655 | 0.2243 | 0.18768 | 0.27466 | 0.23804 | 0.23346 | 0.068665 | 0.31586 | 123.0148 | 0.15106 | 123.0286 | 2.2156 | 122.9782 | -120.8908 | -123.0057 | 2.1332 | 122.9645 | 2.0691 | 2.6962
803.7812 | 123.0698 | -2.0508 | 120.9229 | -0.20615 | -0.0054047 | 0.019418 | 0.014063 | -0.0011834 | 0.00084159 | 0.0013992 | 0.062744 | 0.00049983 | 0.0016363 | -0.0011086 | -0.00091653 | -0.0044029 | -0.0013757 | -0.14191 | 0.054932 | -0.086975 | -0.10071 | 0.032043 | -0.1236 | 0.018311 | 0.39368 | 120.9457 | -2.1057 | 120.8542 | -1.8494 | -1.9043 | -1.8539 | 1.9638 | -120.8679 | -121.0236 | 2.0828 | 2.0691 | 1.9272 | 0.10529 | -0.036621 | -0.054932 | 0.022888 | -0.068665 | 0.20142 | 0.19684 | 0.14648 | 0.25177 | 0.20142 | 0.11902 | -0.013733 | 0.25635 | 122.9599 | 0.14191 | 123.0515 | 2.1057 | 122.9965 | -121.0098 | -123.0286 | 1.9501 | 122.905 | 1.9089 | 2.4445
805.4844 | 123.1155 | -1.9089 | 121.0419 | -0.19089 | -0.0041229 | 0.018564 | 0.014276 | -0.002038 | 0.002978 | 0.0052444 | 0.062744 | -0.0012092 | -0.00049987 | 0.0027366 | 0.00079247 | -0.0031211 | -0.0039391 | -0.082397 | 0.059509 | -0.10071 | -0.027466 | 0.11902 | -0.036621 | 0.091553 | 0.51727 | 121.0739 | -1.9455 | 121.0602 | -1.6205 | -1.6983 | -1.6571 | 1.8082 | -120.9824 | -121.0693 | 2.0279 | 2.0004 | 1.8723 | 0.19226 | 0.064087 | -0.036621 | 0.032044 | 0.018311 | 0.28839 | 0.25177 | 0.21057 | 0.28839 | 0.24719 | 0.21973 | 0.073242 | 0.32501 | 123.0057 | 0.16022 | 123.0194 | 1.9684 | 122.9828 | -121.1426 | -122.9874 | 1.8814 | 122.9691 | 1.8265 | 2.4261
807.1562 | 123.0835 | -1.918 | 120.9778 | -0.168 | -0.0013457 | 0.021127 | 0.017481 | 0.0052252 | 0.00041439 | 0.0024674 | -0.034912 | -0.00035457 | 0.0018499 | -4.063e-05 | -0.0019845 | -0.0033347 | -0.0013757 | -0.091553 | 0.054932 | -0.10071 | -0.045776 | 0.068665 | -0.10071 | 0.036621 | 0.4715 | 121.0236 | -2.0096 | 121.0281 | -1.7029 | -1.799 | -1.6891 | 1.8173 | -120.9229 | -121.0236 | 1.9867 | 1.9547 | 1.8173 | 0.13733 | 0 | -0.091553 | 0.045777 | 0.050354 | 0.21515 | 0.22888 | 0.11902 | 0.32044 | 0.21057 | 0.16937 | 0.054932 | 0.3067 | 123.0377 | 0.15564 | 123.0331 | 1.973 | 122.9416 | -121.0785 | -122.9874 | 1.8723 | 122.9462 | 1.8265 | 2.3895
808.8125 | 123.0927 | -1.8951 | 121.0739 | -0.14511 | -0.00049134 | 0.021127 | 0.017267 | 0.00095278 | -0.00044001 | 0.0018264 | -0.01355 | 0.0019952 | 0.0014227 | 0.0033774 | -0.00070273 | -0.0026939 | 0.00076046 | -0.07782 | 0.041199 | -0.091553 | -0.018311 | 0.086975 | -0.091553 | 0.032043 | 0.45776 | 121.1105 | -1.9455 | 121.0831 | -1.6342 | -1.7349 | -1.6434 | 1.8036 | -121.0327 | -121.0922 | 1.9821 | 1.9272 | 1.8036 | 0.1236 | 0 | -0.050354 | 0.036621 | 0.009155 | 0.26093 | 0.25177 | 0.16022 | 0.30212 | 0.21057 | 0.17853 | 0.073242 | 0.31128 | 123.0286 | 0.13275 | 123.056 | 1.9363 | 123.0057 | -121.1655 | -123.0194 | 1.8768 | 122.9782 | 1.8173 | 2.3529
810.5156 | 123.0515 | -1.8997 | 121.0693 | -0.21378 | -0.0032683 | 0.019418 | 0.018122 | -0.00032902 | 0.0038324 | 0.00011745 | 0.013916 | 0.00092703 | 0.0016363 | -0.0064492 | 0.00036527 | -0.0050437 | -0.00073494 | -0.09613 | 0.036621 | -0.07782 | -0.054932 | 0.082397 | -0.11902 | 0.045776 | 0.41657 | 121.0922 | -1.9501 | 121.0236 | -1.6937 | -1.7578 | -1.7029 | 1.8219 | -121.0327 | -121.1243 | 1.9821 | 1.9455 | 1.7807 | 0.1236 | -0.041199 | -0.050354 | 0.022888 | -0.045776 | 0.20599 | 0.19684 | 0.14191 | 0.24719 | 0.19226 | 0.16022 | 0.022888 | 0.25635 | 122.9736 | 0.11444 | 123.0423 | 1.9363 | 122.9919 | -121.1472 | -123.0194 | 1.8448 | 122.9233 | 1.8036 | 2.3163
812.1875 | 123.0835 | -1.7853 | 121.1563 | -0.14511 | 0.00057686 | 0.019205 | 0.017694 | -0.003747 | 0.0014826 | 0.00204 | 0.0047608 | -0.0016364 | 0.0016363 | 0.002523 | 0.0014335 | -0.0052573 | -0.0024439 | -0.059509 | 0.027466 | -0.091553 | -0.022888 | 0.10529 | -0.086975 | 0.036621 | 0.47607 | 121.1884 | -1.8539 | 121.1609 | -1.5518 | -1.6479 | -1.5701 | 1.6937 | -121.1288 | -121.1792 | 1.8906 | 1.8219 | 1.6983 | 0.12817 | 0.004578 | -0.068665 | 0.032043 | 0.004578 | 0.23346 | 0.21515 | 0.13733 | 0.28381 | 0.20599 | 0.19684 | 0.068665 | 0.30212 | 123.0148 | 0.11902 | 123.0423 | 1.8127 | 122.9736 | -121.2479 | -123.0103 | 1.7624 | 122.9462 | 1.7258 | 2.2614
813.875 | 123.0515 | -1.8219 | 121.1197 | -0.17563 | -0.00027774 | 0.018991 | 0.017267 | -0.0033196 | 0.0019098 | 0.0031082 | 0.0078126 | -0.00035457 | 0.0016363 | -0.0023904 | -0.0011301 | -0.0046165 | -0.00073494 | -0.091553 | 0.013733 | -0.073242 | -0.041199 | 0.10071 | -0.09613 | 0.022888 | 0.4715 | 121.1243 | -1.886 | 121.0968 | -1.6113 | -1.6891 | -1.6342 | 1.7487 | -121.106 | -121.1609 | 1.9226 | 1.8448 | 1.7258 | 0.09613 | -0.022888 | -0.064087 | 0.004578 | -0.022888 | 0.21057 | 0.18768 | 0.13275 | 0.25177 | 0.19684 | 0.17395 | 0.032043 | 0.27466 | 122.9828 | 0.086975 | 123.0103 | 1.8356 | 122.9462 | -121.1929 | -123.0057 | 1.7807 | 122.9187 | 1.7303 | 2.2934
815.5781 | 122.9553 | -1.8768 | 121.1288 | -0.11459 | -0.0041229 | 0.017709 | 0.015985 | -0.0011834 | 0.00084159 | 0.0056716 | -0.016602 | 0.0017816 | 0.0014227 | 0.00017297 | 0.0014335 | -0.0041891 | 0.00011966 | -0.16479 | 0.086975 | -0.14648 | -0.15106 | -0.054932 | -0.16479 | -0.054932 | 0.40283 | 121.1929 | -1.9318 | 120.9915 | -1.7212 | -1.7853 | -1.712 | 1.7303 | -121.0419 | -121.2799 | 1.8219 | 1.8219 | 1.712 | 0.091552 | -0.018311 | -0.054932 | 0.064087 | -0.13733 | 0.15564 | 0.1648 | 0.091553 | 0.21973 | 0.14648 | 0.091552 | -0.004578 | 0.21057 | 122.9233 | 0.23346 | 123.1247 | 1.9638 | 123.0698 | -121.2753 | -123.0606 | 1.7258 | 122.8683 | 1.712 | 2.2797
817.2812 | 123.0698 | -1.7258 | 121.1929 | -0.19089 | -0.0013457 | 0.020486 | 0.015985 | 0.00031198 | 0.0021234 | -9.6154e-05 | -0.0043944 | 0.0011408 | 0.00056833 | 0.00038657 | 0.00015167 | -0.0041891 | 0.0022559 | -0.054932 | 0.045776 | -0.082397 | -0.018311 | 0.10986 | -0.07782 | 0.027466 | 0.48065 | 121.2387 | -1.799 | 121.2296 | -1.4969 | -1.5747 | -1.4923 | 1.6434 | -121.1472 | -121.2112 | 1.8356 | 1.7532 | 1.6479 | 0.10986 | 0.004577 | -0.073242 | 0.045776 | 0.036621 | 0.22888 | 0.23346 | 0.15106 | 0.3067 | 0.2243 | 0.19226 | 0.064086 | 0.30212 | 123.0286 | 0.12817 | 123.0377 | 1.7715 | 122.9645 | -121.2753 | -122.9919 | 1.7075 | 122.9553 | 1.6708 | 2.2064
818.9688 | 123.0469 | -1.7395 | 121.2112 | -0.168 | -0.0030547 | 0.019205 | 0.01684 | -0.00096982 | -0.00065361 | 0.00204 | 0.050537 | -0.00014097 | -0.00092707 | -0.0034586 | -6.1934e-05 | -0.0029075 | -0.0020165 | -0.12817 | 0.068665 | -0.11902 | -0.086975 | 0.036621 | -0.11902 | 0.022888 | 0.41199 | 121.2296 | -1.7944 | 121.1609 | -1.5015 | -1.5884 | -1.5289 | 1.6205 | -121.1426 | -121.2982 | 1.7761 | 1.7624 | 1.6205 | 0.14191 | 0 | -0.054932 | 0.01831 | -0.050354 | 0.23804 | 0.21057 | 0.15106 | 0.2655 | 0.20599 | 0.15564 | 0.032044 | 0.29297 | 122.9553 | 0.18768 | 123.024 | 1.8082 | 122.9691 | -121.3303 | -123.0057 | 1.6525 | 122.9004 | 1.6113 | 2.1515
820.6406 | 123.0423 | -1.7349 | 121.2067 | -0.23666 | -0.0028411 | 0.017709 | 0.017481 | -0.00054262 | 0.00062799 | 0.00097205 | 0.0078126 | 0.00028623 | 0.13344 | -0.0019632 | 0.068725 | 0.10006 | -0.0026575 | -0.1236 | 0.054932 | -0.10071 | -0.073242 | 0.045776 | -0.12817 | 0.004578 | 0.71411 | 121.2204 | -1.7899 | 1.8265 | 121.1929 | 120.932 | 0.33875 | 1.6342 | -121.1517 | -121.2799 | 1.7807 | 1.7395 | 1.6067 | 0.10529 | -0.027466 | -0.054932 | 0.013733 | -119.3802 | 122.9279 | 2.0737 | 122.6669 | 2.1286 | 122.7219 | 0.14648 | 0.027466 | 122.9828 | 3.6163 | 0.15564 | 123.0103 | 1.7899 | 122.9553 | -121.3074 | -122.9965 | 1.6617 | 3.5614 | 1.6113 | 2.449
822.3125 | 123.0011 | -1.7075 | 121.225 | -0.17563 | -0.0045501 | 0.019846 | 0.015985 | -0.00032902 | 0.0031916 | 0.0024674 | -0.022705 | 0.00092703 | 0.1328 | 0.0048728 | 0.068725 | 0.1007 | -0.0013757 | -0.12817 | 0.045776 | -0.091553 | -0.07782 | 0.036621 | -0.11902 | 0 | 0.59967 | 121.2387 | -1.7487 | 1.0483 | 121.2204 | 120.9457 | 0.37079 | 1.6159 | -121.1792 | -121.3028 | 1.7441 | 1.7075 | 1.5884 | 0.091553 | -0.027466 | -0.041199 | 0.013732 | -120.1767 | 122.9279 | 2.0782 | 122.6532 | 2.1194 | 122.6944 | 0.12817 | 0.013733 | 122.9691 | 2.7969 | 0.13733 | 122.9874 | 1.7532 | 122.9462 | -121.3165 | -122.9736 | 1.6296 | 2.7557 | 1.5793 | 2.3071
824 | 122.9141 | -1.8082 | 121.138 | -0.10696 | -0.0026275 | 0.018564 | 0.016413 | -0.00011542 | -0.00022641 | 0.00054465 | -0.03186 | 0.00049983 | 0.13387 | 0.0014548 | 0.069152 | 0.10006 | -0.0020165 | -0.15564 | 0.07782 | -0.12817 | -0.12817 | 0.013733 | -0.13275 | -0.041199 | 0.59509 | 121.225 | -1.8311 | 0.97046 | 121.1014 | 120.7535 | 0.41199 | 1.68 | -121.0602 | -121.2662 | 1.8219 | 1.767 | 1.6754 | 0.086975 | -0.004577 | -0.022888 | 0.086976 | -120.1675 | 122.9095 | 2.2202 | 122.5616 | 2.243 | 122.5845 | 0.14191 | 0 | 122.9324 | 2.8015 | 0.20599 | 123.056 | 1.886 | 123.0331 | -121.2662 | -122.9691 | 1.68 | 2.7786 | 1.6525 | 2.4033
825.6719 | 123.0194 | -1.7715 | 121.1151 | -0.168 | -0.0032683 | 0.019205 | 0.017694 | 0.0015936 | 0.0016962 | -0.00030975 | -0.077637 | 7.2626e-05 | 0.13515 | -0.0049538 | 0.069793 | 0.1007 | -0.0026575 | -0.13733 | 0.073242 | -0.11902 | -0.10986 | -0.009155 | -0.17395 | -0.022888 | 0.59509 | 121.1655 | -1.8311 | 0.83771 | 121.1243 | 120.8084 | 0.36163 | 1.6525 | -121.0419 | -121.225 | 1.7624 | 1.7487 | 1.5976 | 0.096131 | -0.054931 | -0.05951 | 0.050354 | -120.2774 | 122.8958 | 2.1332 | 122.58 | 2.1927 | 122.6395 | 0.10986 | 0.009156 | 122.9553 | 2.6688 | 0.19226 | 122.9965 | 1.8448 | 122.937 | -121.2341 | -122.9462 | 1.6617 | 2.6093 | 1.6342 | 2.3666
827.3438 | 122.9782 | -1.7761 | 121.1151 | -0.21378 | -0.0022003 | 0.021341 | 0.018762 | 0.0033026 | 0.0016962 | 0.00097205 | -0.074585 | -0.00056817 | 0.13344 | 0.001882 | 0.069793 | 0.10262 | -0.0032983 | -0.15106 | 0.068665 | -0.12817 | -0.12817 | -0.004578 | -0.1831 | -0.045776 | 0.57678 | 121.1334 | -1.8539 | 0.76446 | 121.106 | 120.8542 | 0.33417 | 1.6479 | -121.0464 | -121.2433 | 1.7715 | 1.7303 | 1.593 | 0.082398 | -0.054931 | -0.07782 | 0.018311 | -120.3506 | 122.8821 | 2.1103 | 122.6303 | 2.1881 | 122.7081 | 0.1236 | 0 | 122.9599 | 2.6184 | 0.19684 | 122.9874 | 1.8448 | 122.9095 | -121.2433 | -122.9691 | 1.6479 | 2.5406 | 1.6251 | 2.3529
829.0156 | 122.9965 | -1.8265 | 121.0144 | -0.168 | -0.00027774 | 0.020059 | 0.018549 | -0.00075622 | 0.00020079 | -0.00052335 | -0.068481 | 0.00071343 | 0.13323 | -0.0045266 | 0.069365 | 0.099632 | 0.0018287 | -0.13275 | 0.054932 | -0.10529 | -0.091553 | 0.022888 | -0.14191 | -0.009155 | 0.6134 | 121.0831 | -1.8814 | 0.74158 | 121.0831 | 120.7306 | 0.36621 | 1.7212 | -120.9595 | -121.106 | 1.8494 | 1.8173 | 1.6846 | 0.096131 | -0.036621 | -0.054932 | 0.068665 | -120.2728 | 122.9095 | 2.1927 | 122.5571 | 2.2476 | 122.612 | 0.12817 | 0.013733 | 122.9645 | 2.623 | 0.16022 | 122.9645 | 1.8814 | 122.9095 | -121.1197 | -122.8958 | 1.7349 | 2.5681 | 1.6937 | 2.4399
830.75 | 122.9645 | -1.8173 | 121.0602 | -0.19852 | -0.0019867 | 0.020273 | 0.015344 | -0.00075622 | -0.001081 | 0.0016128 | 0.02002 | -0.00099557 | 0.1343 | 0.0012412 | 0.069579 | 0.09835 | 0.0037513 | -0.13275 | 0.036621 | -0.07782 | -0.086975 | 0.050354 | -0.11444 | 0 | 0.53101 | 121.0968 | -1.8677 | 0.67749 | 121.0648 | 120.7718 | 0.32501 | 1.7395 | -121.0236 | -121.1472 | 1.8677 | 1.8173 | 1.7029 | 0.07782 | -0.036621 | -0.050354 | 0.036621 | -120.3827 | 122.8821 | 2.1423 | 122.5891 | 2.1927 | 122.6395 | 0.12817 | -0.009155 | 122.9324 | 2.5452 | 0.11444 | 122.9645 | 1.8539 | 122.9141 | -121.138 | -122.9279 | 1.7303 | 2.4948 | 1.6846 | 2.3483
832.5469 | 122.8867 | -1.8494 | 121.0693 | -0.099335 | -0.0034821 | 0.019205 | 0.018549 | -0.0024652 | -0.0012946 | 0.0024674 | -0.019653 | -0.00014097 | 0.13088 | -0.0053812 | 0.068511 | 0.098777 | 0.00054686 | -0.13733 | 0.073242 | -0.1236 | -0.13275 | -0.004578 | -0.10529 | -0.009155 | 0.54932 | 121.1197 | -1.8768 | 0.72784 | 121.0007 | 120.5383 | 0.38452 | 1.7258 | -120.9961 | -121.2021 | 1.8448 | 1.8402 | 1.7441 | 0.11444 | 0.01831 | -0.027466 | 0.050354 | -120.3415 | 122.85 | 2.2339 | 122.3877 | 2.2614 | 122.4152 | 0.11902 | -0.009155 | 122.8775 | 2.6047 | 0.19684 | 122.9965 | 1.9226 | 122.9691 | -121.1929 | -122.9462 | 1.7166 | 2.5772 | 1.712 | 2.3987
834.2344 | 122.9141 | -1.9043 | 120.9686 | -0.099335 | -0.0032683 | 0.020486 | 0.015558 | -0.003106 | 0.0021234 | 0.00075845 | -0.0013428 | -0.00056817 | 0.13622 | -0.007731 | 0.069152 | 0.099204 | -0.0011621 | -0.086975 | 0.045776 | -0.091553 | -0.050354 | 0.086975 | -0.068665 | 0.036621 | 0.65918 | 121.0144 | -1.9135 | 0.76446 | 120.9869 | 120.6665 | 0.43488 | 1.8127 | -120.9229 | -121.019 | 1.9913 | 1.9409 | 1.8356 | 0.12817 | 0.022888 | -0.009155 | 0.045776 | -120.2042 | 122.8912 | 2.3392 | 122.5708 | 2.3483 | 122.58 | 0.17853 | 0.041199 | 122.9004 | 2.6779 | 0.13733 | 122.9279 | 1.9501 | 122.9187 | -121.0602 | -122.8821 | 1.8539 | 2.6688 | 1.8173 | 2.5635
835.9688 | 122.8546 | -1.9272 | 121.019 | -0.099335 | -0.0026275 | 0.018991 | 0.015772 | -0.0011834 | -0.0030036 | 0.00097205 | -0.050171 | -0.0020636 | 0.13237 | 0.001882 | 0.070006 | 0.09835 | 0.00033326 | -0.19226 | 0.068665 | -0.12817 | -0.15106 | -0.045776 | -0.15564 | -0.050354 | 0.57678 | 121.0327 | -1.9272 | 0.71411 | 120.9366 | 120.6757 | 0.39368 | 1.799 | -120.9503 | -121.17 | 1.8814 | 1.8768 | 1.7715 | 0.07782 | -0.027466 | 0 | 0.013733 | -120.3049 | 122.8638 | 2.3209 | 122.6028 | 2.3209 | 122.6028 | 0.082398 | -0.022888 | 122.8638 | 2.6413 | 0.19684 | 122.9599 | 1.9958 | 122.9599 | -121.1472 | -122.9462 | 1.7761 | 2.6413 | 1.7349 | 2.504
837.7031 | 123.0011 | -1.8723 | 120.9503 | -0.12985 | -0.0032683 | 0.017923 | 0.01449 | -0.0011834 | 0.0034052 | -0.0028732 | 0.023071 | -0.00056817 | 0.13152 | -0.0051676 | 0.068297 | 0.098991 | -0.0035119 | -0.09613 | 0.059509 | -0.10529 | -0.036621 | 0.10986 | -0.054932 | 0.082397 | 0.70496 | 120.9503 | -1.9089 | 0.77362 | 121.0464 | 120.8221 | 0.45319 | 1.767 | -120.8908 | -120.9869 | 1.9821 | 1.9546 | 1.8173 | 0.18768 | 0.050354 | -0.036622 | 0 | -120.1767 | 122.9187 | 2.3254 | 122.6944 | 2.3621 | 122.731 | 0.21515 | 0.068665 | 122.9553 | 2.6825 | 0.16479 | 122.8592 | 1.9318 | 122.8226 | -121.0556 | -122.8592 | 1.8356 | 2.6459 | 1.7761 | 2.5772
839.4531 | 122.9507 | -1.9913 | 120.8405 | -0.18326 | -0.0026275 | 0.017496 | 0.013635 | -0.002038 | -0.0015082 | -0.0026596 | 0.010864 | 0.00028623 | 0.13366 | -0.00025423 | 0.068938 | 0.09835 | 0.0020423 | -0.13733 | 0.064087 | -0.10071 | -0.09613 | 0.036621 | -0.10529 | 0.018311 | 0.57678 | 120.8633 | -2.0142 | 0.66834 | 120.8908 | 120.52 | 0.37079 | 1.8906 | -120.7764 | -120.9366 | 2.0279 | 2.0096 | 1.886 | 0.11902 | -0.004578 | -0.022888 | 0.022888 | -120.1721 | 122.8821 | 2.3621 | 122.5113 | 2.3849 | 122.5342 | 0.13733 | 0.004578 | 122.905 | 2.6825 | 0.1648 | 122.8775 | 2.0554 | 122.8546 | -120.9412 | -122.8546 | 1.8951 | 2.6596 | 1.8539 | 2.5681
841.2031 | 122.9141 | -2.0279 | 120.7993 | -0.14511 | -0.0022003 | 0.020486 | 0.016199 | -0.00032902 | -0.00065361 | 0.00033105 | -0.01355 | -0.00099557 | 0.13259 | -0.0038858 | 0.069152 | 0.098777 | -0.0015893 | -0.13275 | 0.073242 | -0.086975 | -0.073242 | 0.045776 | -0.11444 | 0.022888 | 0.54474 | 120.8176 | -2.0782 | 0.64087 | 120.8084 | 120.4514 | 0.33417 | 1.9409 | -120.726 | -120.8725 | 2.0737 | 2.0508 | 1.9135 | 0.10986 | -0.027466 | -0.050354 | 0.018311 | -120.1584 | 122.8363 | 2.3621 | 122.4792 | 2.4124 | 122.5296 | 0.13275 | 0.013733 | 122.8867 | 2.7191 | 0.16022 | 122.8958 | 2.1011 | 122.8455 | -120.8862 | -122.8775 | 1.9547 | 2.6688 | 1.8951 | 2.5726
842.8906 | 122.9095 | -2.092 | 120.7489 | -0.15274 | -0.0022003 | 0.020273 | 0.018762 | 0.0020208 | 0.00062799 | 0.00054465 | 0.001709 | -0.00014097 | 0.13536 | -0.00025423 | 0.068938 | 0.098564 | -0.00073494 | -0.14191 | 0.059509 | -0.11444 | -0.07782 | 0.027466 | -0.09613 | 0.027466 | 0.75073 | 120.7352 | -2.1332 | 120.6436 | 120.7489 | 120.4376 | 0.51727 | 1.9775 | -120.6894 | -120.8267 | 2.1194 | 2.1194 | 1.9958 | 0.14191 | 0.018311 | -0.041199 | -0.013733 | -0.10529 | 122.8409 | 2.6093 | 122.5296 | 2.6505 | 122.5708 | 0.14191 | 0.036621 | 122.8821 | 122.7768 | 0.17395 | 122.8683 | 2.1515 | 122.8271 | -120.8633 | -122.8821 | 2.0142 | 122.7356 | 1.9501 | 2.8427
844.6406 | 122.9233 | -2.1057 | 120.7031 | -0.19089 | -0.0030547 | 0.020914 | 0.016413 | -0.00075622 | -0.00086721 | -0.00095055 | -0.010498 | 0.0013544 | 0.13366 | -0.0051676 | 0.067443 | 0.099845 | -0.00052114 | -0.13275 | 0.045776 | -0.09613 | -0.073242 | 0.045776 | -0.11902 | 0.027466 | 0.71869 | 120.7718 | -2.1469 | 120.6573 | 120.7397 | 120.3918 | 0.48523 | 2.0096 | -120.6573 | -120.7764 | 2.1515 | 2.1332 | 1.9867 | 0.1236 | -0.022889 | -0.041199 | 0.068665 | -0.045776 | 122.8455 | 2.5909 | 122.4976 | 2.6321 | 122.5388 | 0.14191 | 0.022888 | 122.8867 | 122.8043 | 0.14191 | 122.9187 | 2.1515 | 122.8775 | -120.7993 | -122.85 | 2.0325 | 122.7631 | 1.973 | 2.8244
846.375 | 122.8363 | -2.3438 | 120.5338 | -0.19852 | 0.00014946 | 0.020914 | 0.018762 | -0.0026788 | 0.00041439 | -0.00073695 | -0.11426 | 0.0013544 | 0.13515 | 0.0053 | 0.068084 | 0.097282 | -0.0024439 | -0.13733 | 0.11444 | -0.13275 | -0.15106 | -0.07782 | -0.21973 | -0.07782 | 0.65918 | 120.5841 | -2.3529 | 120.4102 | 120.4559 | 120.1904 | 0.45776 | 2.211 | -120.4193 | -120.6848 | 2.2659 | 2.2659 | 2.124 | 0.054931 | -0.086976 | -0.009155 | 0.050354 | -0.1236 | 122.7997 | 2.8015 | 122.5342 | 2.8107 | 122.5433 | 0.054931 | -0.018311 | 122.8088 | 122.7631 | 0.24719 | 122.937 | 2.4582 | 122.9279 | -120.6665 | -122.8867 | 2.1927 | 122.7539 | 2.2064 | 3.0029
848.1094 | 122.818 | -2.3529 | 120.5475 | -0.10696 | -0.0015595 | 0.017709 | 0.015558 | -0.00054262 | -0.0012946 | -0.00030975 | -0.019653 | -0.0014228 | 0.13408 | -0.00068143 | 0.068725 | 0.099632 | -0.0022301 | -0.16022 | 0.07782 | -0.1236 | -0.14648 | -0.032043 | -0.16937 | -0.027466 | 0.71869 | 120.5933 | -2.3758 | 120.3598 | 120.4559 | 120.1996 | 0.54474 | 2.2293 | -120.4697 | -120.694 | 2.3209 | 2.3254 | 2.1835 | 0.09613 | -0.045777 | -0.022888 | 0.045777 | -0.18768 | 122.8088 | 2.8976 | 122.5525 | 2.9205 | 122.5754 | 0.091553 | -0.022888 | 122.8317 | 122.7356 | 0.20142 | 122.9691 | 2.4307 | 122.9462 | -120.6711 | -122.9233 | 2.2064 | 122.7127 | 2.1927 | 3.0716
849.8125 | 122.8409 | -2.4307 | 120.4376 | -0.10696 | -0.0041229 | 0.019632 | 0.017267 | -0.002038 | -0.00086721 | 0.0016128 | -0.022705 | -0.00099557 | 0.13195 | -0.0045266 | 0.068084 | 0.097923 | 0.0035377 | -0.1236 | 0.07782 | -0.11444 | -0.10529 | 0.004578 | -0.13733 | -0.009155 | 0.6958 | 120.4605 | -2.4628 | 120.282 | 120.3598 | 120.0989 | 0.52643 | 2.3163 | -120.3598 | -120.5429 | 2.4353 | 2.4216 | 2.2934 | 0.10529 | -0.022888 | -0.032044 | 0.022888 | -0.15564 | 122.7905 | 2.9572 | 122.5296 | 2.9892 | 122.5616 | 0.11902 | 0.009155 | 122.8226 | 122.7448 | 0.19226 | 122.9233 | 2.5085 | 122.8912 | -120.5521 | -122.9004 | 2.3254 | 122.7127 | 2.3071 | 3.1265
851.5469 | 122.8958 | -2.4124 | 120.3735 | -0.15274 | -0.0028411 | 0.020273 | 0.015131 | -0.0043878 | -0.00022641 | 0.00054465 | 0.001709 | 0.00092703 | 0.13173 | -0.0047402 | 0.070434 | 0.098564 | -0.0043665 | -0.13275 | 0.059509 | -0.091553 | -0.073242 | 0.022888 | -0.12817 | 0.022888 | 0.67749 | 120.4102 | -2.449 | 120.3232 | 120.4147 | 120.0256 | 0.48065 | 2.3209 | -120.314 | -120.4468 | 2.4353 | 2.4353 | 2.2842 | 0.11444 | -0.036621 | -0.036621 | 0.036621 | -0.050354 | 122.8271 | 2.8931 | 122.438 | 2.9297 | 122.4747 | 0.11444 | 0.018311 | 122.8638 | 122.7722 | 0.15106 | 122.8592 | 2.4719 | 122.8226 | -120.4651 | -122.8226 | 2.3392 | 122.7356 | 2.2797 | 3.0899
853.2812 | 122.8317 | -2.4033 | 120.4147 | -0.14511 | -0.00049134 | 0.020914 | 0.018335 | 0.0033026 | 0.00062799 | 0.00097205 | -0.10815 | 0.00028623 | 0.13301 | -0.00068143 | 0.070434 | 0.10155 | -0.00030754 | -0.10529 | 0.068665 | -0.13733 | -0.10071 | -0.013733 | -0.15106 | -0.032043 | 0.72327 | 120.4834 | -2.4445 | 120.3232 | 120.3827 | 120.1263 | 0.52643 | 2.2659 | -120.3461 | -120.5154 | 2.3895 | 2.3712 | 2.2522 | 0.10529 | -0.013733 | -0.041199 | 0.068664 | -0.091553 | 122.7859 | 2.9297 | 122.5296 | 2.9709 | 122.5708 | 0.1236 | 0.036621 | 122.8271 | 122.7676 | 0.20599 | 122.9279 | 2.4719 | 122.8867 | -120.5521 | -122.8592 | 2.3026 | 122.7264 | 2.298 | 3.1265
854.9688 | 122.8867 | -2.5314 | 120.2545 | -0.20615 | -0.0015595 | 0.018777 | 0.013849 | 0.0018072 | 0.0031916 | 0.0016128 | 0.0078126 | 0.00071343 | 0.13472 | -0.00025423 | 0.070006 | 0.098991 | -0.0011621 | -0.10986 | 0.045776 | -0.064087 | -0.036621 | 0.073242 | -0.11444 | 0.045776 | 0.70038 | 120.2866 | -2.5635 | 120.2271 | 120.2774 | 119.9341 | 0.47607 | 2.4673 | -120.2087 | -120.2911 | 2.6047 | 2.5772 | 2.417 | 0.10986 | -0.050354 | -0.032044 | 0.032043 | -0.027466 | 122.8088 | 3.0075 | 122.4655 | 3.0396 | 122.4976 | 0.13733 | 0.027466 | 122.8409 | 122.7905 | 0.10986 | 122.85 | 2.5772 | 122.818 | -120.3186 | -122.818 | 2.4948 | 122.7585 | 2.4216 | 3.2318
856.7031 | 122.7859 | -2.536 | 120.3323 | -0.15274 | -0.00027774 | 0.019418 | 0.019831 | -0.0011834 | 0.00084159 | 0.0011856 | -0.10815 | 0.001568 | 0.13216 | 0.002523 | 0.069365 | 0.099845 | 0.0020423 | -0.14648 | 0.07782 | -0.12817 | -0.16479 | -0.086975 | -0.23804 | -0.082397 | 0.61798 | 120.3644 | -2.5497 | 120.1584 | 120.2133 | 119.9341 | 0.48523 | 2.4078 | -120.2545 | -120.4971 | 2.449 | 2.4536 | 2.298 | 0.045777 | -0.10986 | -0.013733 | 0.032044 | -0.17395 | 122.7493 | 3.0212 | 122.4701 | 3.035 | 122.4838 | 0.041199 | -0.036621 | 122.7631 | 122.7081 | 0.20599 | 122.9141 | 2.6138 | 122.9004 | -120.4605 | -122.8821 | 2.3712 | 122.6944 | 2.3895 | 3.154
858.4375 | 122.9279 | -2.5085 | 120.2866 | -0.19852 | 0.00057686 | 0.020486 | 0.014917 | 0.00052558 | -0.00044001 | 0.00075845 | -0.050171 | -0.00014097 | 0.13366 | -0.00046783 | 0.068725 | 0.099418 | 0.0041785 | -0.07782 | 0.045776 | -0.082397 | -0.027466 | 0.082397 | -0.10529 | 0.041199 | 0.74158 | 120.314 | -2.5314 | 120.3049 | 120.3461 | 120.0943 | 0.53101 | 2.4261 | -120.2408 | -120.314 | 2.5909 | 2.5497 | 2.4033 | 0.1236 | -0.022889 | -0.022888 | 0.027466 | 0.018311 | 122.8546 | 3.0396 | 122.6028 | 3.0624 | 122.6257 | 0.16479 | 0.054931 | 122.8775 | 122.8363 | 0.12817 | 122.8455 | 2.5543 | 122.8226 | -120.369 | -122.818 | 2.4811 | 122.8134 | 2.4307 | 3.2501
860.125 | 122.9324 | -2.4902 | 120.2866 | -0.19852 | 0.00036326 | 0.020486 | 0.017694 | -0.00032902 | 0.002337 | 0.00075845 | -0.01355 | 0.00092703 | 0.13152 | -0.001536 | 0.068297 | 0.098991 | -0.0011621 | -0.086975 | 0.027466 | -0.073242 | -0.018311 | 0.09613 | -0.091553 | 0.068665 | 0.79193 | 120.3003 | -2.5223 | 120.2866 | 120.3369 | 120.0073 | 0.52643 | 2.417 | -120.2591 | -120.3049 | 2.5864 | 2.5589 | 2.3987 | 0.14191 | -0.018311 | -0.032044 | 0.013733 | 0 | 122.8271 | 3.0167 | 122.4976 | 3.0487 | 122.5296 | 0.16937 | 0.054931 | 122.8592 | 122.8088 | 0.10071 | 122.8226 | 2.5177 | 122.7905 | -120.3598 | -122.8088 | 2.4719 | 122.7768 | 2.4033 | 3.2822
861.7969 | 122.8821 | -2.4948 | 120.2911 | -0.22903 | -0.00070494 | 0.019846 | 0.015772 | -0.00032902 | 0.0010554 | 0.00204 | 0.02002 | 0.00092703 | 0.1328 | 0.00060037 | 0.069793 | 0.10049 | -0.0015893 | -0.10986 | 0.059509 | -0.086975 | -0.07782 | 0.027466 | -0.12817 | 0.036621 | 0.67291 | 120.2911 | -2.5269 | 120.2316 | 120.314 | 120.0623 | 0.48981 | 2.4078 | -120.2316 | -120.369 | 2.5223 | 2.5314 | 2.3666 | 0.1236 | -0.041199 | -0.032043 | 0 | -0.05951 | 122.8088 | 2.9846 | 122.5571 | 3.0167 | 122.5891 | 0.11444 | 0.009155 | 122.8409 | 122.7585 | 0.14648 | 122.818 | 2.5543 | 122.7859 | -120.3781 | -122.818 | 2.417 | 122.7264 | 2.3849 | 3.1677
863.4688 | 122.8683 | -2.6321 | 120.1447 | -0.14511 | -0.0034821 | 0.019418 | 0.013422 | 0.00073918 | 0.002337 | 0.00204 | 0.023071 | -0.00099557 | 0.13195 | -0.002604 | 0.070647 | 0.096855 | -0.0030847 | -0.13733 | 0.054932 | -0.09613 | -0.07782 | 0.018311 | -0.12817 | 0.022888 | 0.67291 | 120.1996 | -2.6505 | 120.108 | 120.195 | 119.8746 | 0.48065 | 2.536 | -120.0897 | -120.2225 | 2.6505 | 2.655 | 2.504 | 0.11902 | -0.032044 | -0.018311 | 0.054932 | -0.036621 | 122.8271 | 3.1128 | 122.5067 | 3.1311 | 122.525 | 0.11444 | 0.01831 | 122.8455 | 122.7585 | 0.15106 | 122.85 | 2.6871 | 122.8317 | -120.2408 | -122.7951 | 2.5543 | 122.7402 | 2.4948 | 3.3051
865.2031 | 122.7951 | -2.7924 | 120.076 | -0.12222 | -0.0028411 | 0.019632 | 0.015344 | -0.00096982 | 0.00041439 | 0.00033105 | -0.01355 | -0.0016364 | 0.13344 | 0.0046592 | 0.070434 | 0.09835 | -0.0026575 | -0.12817 | 0.064087 | -0.13275 | -0.13733 | -0.009155 | -0.16022 | 0.013733 | 0.70496 | 120.0714 | -2.7969 | 119.8975 | 119.9799 | 119.7281 | 0.53101 | 2.6596 | -120.0119 | -120.2133 | 2.7832 | 2.8061 | 2.6321 | 0.14648 | -0.027466 | -0.004578 | -0.004578 | -0.17853 | 122.7722 | 3.3234 | 122.5204 | 3.3279 | 122.525 | 0.1236 | -0.004578 | 122.7768 | 122.6944 | 0.19684 | 122.8683 | 2.8564 | 122.8638 | -120.2087 | -122.8729 | 2.655 | 122.6898 | 2.6642 | 3.4973
866.875 | 122.818 | -2.8152 | 120.0073 | -0.11459 | -0.0041229 | 0.017282 | 0.019831 | 0.00052558 | 0.00041439 | -0.0020188 | -0.062378 | 0.0011408 | 0.13387 | 0.00081397 | 0.068511 | 0.097709 | -0.00073494 | -0.16479 | 0.09613 | -0.11444 | -0.16022 | -0.050354 | -0.1831 | 0 | 0.61798 | 120.0668 | -2.8107 | 119.87 | 119.957 | 119.6228 | 0.52643 | 2.7008 | -119.9112 | -120.1675 | 2.7649 | 2.8152 | 2.6321 | 0.11444 | -0.068664 | 0.004578 | 0.059509 | -0.13733 | 122.7722 | 3.3417 | 122.4381 | 3.3371 | 122.4335 | 0.064087 | -0.045776 | 122.7676 | 122.6807 | 0.21057 | 122.8775 | 2.9114 | 122.8821 | -120.1218 | -122.818 | 2.655 | 122.6852 | 2.6505 | 3.4332
868.6094 | 122.8592 | -2.8473 | 119.9295 | -0.13748 | -0.0028411 | 0.018777 | 0.016199 | -0.0018244 | 0.00041439 | 0.00204 | 0.013916 | -0.00056817 | 0.13323 | -0.0036722 | 0.070006 | 0.099418 | 0.00033326 | -0.14648 | 0.036621 | -0.091553 | -0.082397 | 0.054932 | -0.11444 | 0.054932 | 0.6546 | 119.9615 | -2.8656 | 119.8929 | 119.9661 | 119.6823 | 0.4715 | 2.7557 | -119.8929 | -120.0119 | 2.9022 | 2.9022 | 2.7328 | 0.14649 | -0.022888 | -0.018311 | 0.032044 | -0.036621 | 122.8134 | 3.3188 | 122.5296 | 3.3371 | 122.5479 | 0.14649 | 0.009156 | 122.8317 | 122.7585 | 0.12817 | 122.8271 | 2.8839 | 122.8088 | -120.0211 | -122.7951 | 2.7649 | 122.7402 | 2.7008 | 3.5019
870.3594 | 122.905 | -2.8564 | 119.8746 | -0.20615 | -0.0011321 | 0.020273 | 0.017053 | -0.00011542 | 0.0019098 | 0.00033105 | -0.095947 | 0.15709 | 0.13259 | -0.0019632 | 0.069365 | 0.098777 | -0.0018029 | -0.073242 | 0.032043 | -0.082397 | -0.027466 | 0.09613 | -0.082397 | 0.07782 | 0.78278 | 119.902 | -2.8793 | 119.8608 | 119.9432 | 119.7006 | 0.50354 | 2.774 | -119.8425 | -119.902 | 2.9526 | 2.9343 | 2.774 | 0.16022 | 0 | -0.022888 | 0.027466 | -0.013733 | 122.7997 | 3.36 | 122.5571 | 3.3829 | 122.58 | 0.17853 | 0.054931 | 122.8226 | 122.7402 | 0.11444 | 122.7814 | 2.8885 | 122.7585 | -119.957 | -122.7539 | 2.829 | 122.7173 | 2.7832 | 3.6392
872.0312 | 122.8775 | -2.8931 | 119.8929 | -0.13748 | -0.0026275 | 0.019205 | 0.013635 | 0.00095278 | 0.0025506 | -0.0015916 | -0.044067 | 0.15452 | 0.1343 | 0.0040182 | 0.069793 | 0.099845 | 0.00011966 | -0.082397 | 0.050354 | -0.086975 | -0.027466 | 0.10529 | -0.045776 | 0.09613 | 0.82398 | 119.902 | -2.8976 | 119.8059 | 119.9249 | 119.7235 | 0.54016 | 2.8061 | -119.8425 | -119.9203 | 2.9984 | 2.9892 | 2.8473 | 0.1831 | 0.041199 | -0.004578 | 0.009156 | -0.086975 | 122.818 | 3.4332 | 122.6166 | 3.4378 | 122.6212 | 0.19226 | 0.059509 | 122.8226 | 122.7036 | 0.13733 | 122.7997 | 2.9434 | 122.7951 | -119.9799 | -122.7905 | 2.8656 | 122.699 | 2.8107 | 3.717
873.7656 | 122.8729 | -2.9892 | 119.8013 | -0.17563 | 0.00057686 | 0.018777 | 0.01684 | 0.00138 | 0.00062799 | 0.0011856 | -0.086792 | 0.15196 | 0.13195 | -0.0021768 | 0.069365 | 0.096855 | 0.00011966 | -0.10071 | 0.050354 | -0.068665 | -0.036621 | 0.10071 | -0.09613 | 0.07782 | 0.70953 | 119.7647 | -3.035 | 119.7144 | 119.7922 | 119.5908 | 0.43488 | 2.9205 | -119.751 | -119.838 | 3.0899 | 3.067 | 2.8931 | 0.14649 | -0.027465 | -0.045776 | -0.036622 | -0.086976 | 122.7814 | 3.4241 | 122.58 | 3.4698 | 122.6257 | 0.16937 | 0.032044 | 122.8271 | 122.7493 | 0.11902 | 122.7997 | 3.0396 | 122.7539 | -119.87 | -122.8363 | 2.9526 | 122.7036 | 2.8885 | 3.6987
875.5 | 122.8729 | -2.948 | 119.8059 | -0.14511 | -0.0036957 | 0.019632 | 0.017053 | 0.0037298 | -0.0019354 | 0.0011856 | -0.059326 | 0.15089 | 0.13237 | 0.0012412 | 0.068084 | 0.096214 | 0.0020423 | -0.14191 | 0.045776 | -0.11444 | -0.086975 | 0.045776 | -0.11902 | 0.050354 | 0.71411 | 119.8471 | -3.0075 | 119.7189 | 119.8242 | 119.6228 | 0.4715 | 2.8336 | -119.7601 | -119.8929 | 2.9938 | 2.9984 | 2.829 | 0.16479 | -0.004578 | -0.059509 | 0.041199 | -0.086975 | 122.7722 | 3.4195 | 122.5708 | 3.479 | 122.6303 | 0.16022 | 0.027466 | 122.8317 | 122.7264 | 0.16022 | 122.8546 | 2.9938 | 122.7951 | -119.9203 | -122.8134 | 2.861 | 122.6669 | 2.8061 | 3.6621
877.25 | 122.7905 | -2.9434 | 119.87 | -0.084076 | -0.0022003 | 0.018777 | 0.018335 | -0.00054262 | -0.00022641 | -0.00095055 | -0.098999 | 0.11009 | 0.1328 | 0.0012412 | 0.06787 | 0.097495 | -0.0020165 | -0.16479 | 0.086975 | -0.1236 | -0.16022 | -0.054932 | -0.16937 | 0.009155 | 0.71869 | 119.9203 | -2.9663 | 119.696 | 119.7784 | 119.5816 | 0.48981 | 2.8198 | -119.783 | -120.0302 | 2.8885 | 2.9526 | 2.774 | 0.13275 | -0.045777 | -0.022889 | 0.050354 | -0.17395 | 122.7219 | 3.4332 | 122.525 | 3.4561 | 122.5479 | 0.068664 | -0.036621 | 122.7448 | 122.6624 | 0.21057 | 122.8867 | 3.0304 | 122.8638 | -119.9936 | -122.8363 | 2.7832 | 122.6395 | 2.7786 | 3.6621
878.9844 | 122.8958 | -2.9205 | 119.8196 | -0.21378 | -0.0013457 | 0.019846 | 0.015772 | 0.0011664 | 0.001269 | -9.6154e-05 | -0.0074462 | 0.12846 | 0.1343 | 0.0016684 | 0.068511 | 0.098777 | 0.00054686 | -0.14648 | 0.036621 | -0.10071 | -0.068665 | 0.050354 | -0.10529 | 0.091553 | 0.78278 | 119.8654 | -2.9663 | 119.7647 | 119.8929 | 119.6869 | 0.51727 | 2.8198 | -119.783 | -119.8883 | 2.9709 | 3.0121 | 2.8152 | 0.19226 | -0.004578 | -0.045777 | 0.045776 | -0.054932 | 122.8134 | 3.4378 | 122.6074 | 3.4836 | 122.6532 | 0.15106 | 0.032043 | 122.8592 | 122.731 | 0.13733 | 122.8317 | 2.9572 | 122.7859 | -119.9203 | -122.7859 | 2.8519 | 122.6852 | 2.774 | 3.7033
880.6719 | 122.9004 | -2.7878 | 119.9432 | -0.12222 | -0.0011321 | 0.019418 | 0.022394 | 0.00052558 | 0.0021234 | -0.00073695 | -0.12036 | 0.11457 | 0.13045 | 0.0029502 | 0.068084 | 0.098777 | -0.0043665 | -0.13275 | 0.073242 | -0.09613 | -0.068665 | 0.041199 | -0.11444 | 0.07782 | 0.81482 | 119.9524 | -2.8336 | 119.9112 | 119.9707 | 119.7647 | 0.52643 | 2.6917 | -119.87 | -120.0119 | 2.829 | 2.8656 | 2.6733 | 0.17395 | -0.018311 | -0.045776 | 0.009156 | -0.032043 | 122.7585 | 3.3142 | 122.5525 | 3.36 | 122.5983 | 0.13733 | 0.027465 | 122.8043 | 122.7448 | 0.16937 | 122.7859 | 2.861 | 122.7402 | -120.0394 | -122.7768 | 2.7191 | 122.699 | 2.655 | 3.6026
882.4219 | 122.8592 | -2.8427 | 119.8837 | -0.19852 | -0.0041229 | 0.019418 | 0.017908 | -0.0016106 | -0.0012946 | -0.00052335 | -0.050171 | 0.15666 | 0.13002 | -0.002604 | 0.069793 | 0.097923 | 0.00054686 | -0.15564 | 0.045776 | -0.10986 | -0.086975 | 0.018311 | -0.13733 | 0.064087 | 0.75989 | 119.9432 | -2.8839 | 119.7922 | 119.9112 | 119.7052 | 0.52643 | 2.7328 | -119.838 | -119.9707 | 2.861 | 2.9068 | 2.7054 | 0.17395 | -0.027466 | -0.041199 | 0.059509 | -0.091553 | 122.7539 | 3.3691 | 122.5479 | 3.4103 | 122.5891 | 0.12817 | 0.022888 | 122.7951 | 122.6761 | 0.15564 | 122.8271 | 2.8885 | 122.7859 | -119.9936 | -122.7676 | 2.7557 | 122.6349 | 2.6871 | 3.6026
884.1562 | 122.8867 | -2.8564 | 119.8791 | -0.21378 | 0.00079046 | 0.019632 | 0.017908 | 0.00031198 | 0.0025506 | -9.6154e-05 | -0.12952 | 0.15345 | 0.1328 | -0.003245 | 0.067656 | 0.099632 | -0.0015893 | -0.10529 | 0.059509 | -0.086975 | -0.054932 | 0.059509 | -0.10986 | 0.10529 | 0.89722 | 119.9066 | -2.8976 | 119.8425 | 119.9387 | 119.7098 | 0.57678 | 2.7695 | -119.8196 | -119.9341 | 2.916 | 2.9617 | 2.7466 | 0.19226 | -0.022888 | -0.041199 | 0.027466 | -0.036621 | 122.7951 | 3.4332 | 122.5662 | 3.4744 | 122.6074 | 0.14648 | 0.032043 | 122.8363 | 122.7402 | 0.14648 | 122.8043 | 2.916 | 122.7631 | -119.9661 | -122.7768 | 2.8015 | 122.699 | 2.7512 | 3.7537
885.8438 | 122.8821 | -2.7969 | 119.9341 | -0.14511 | -0.0019867 | 0.020273 | 0.017267 | 0.0011664 | 0.001269 | -0.00052335 | -0.12036 | 0.16029 | 0.13643 | 0.0033774 | 0.068084 | 0.097068 | -0.0020165 | -0.11444 | 0.054932 | -0.09613 | -0.041199 | 0.041199 | -0.10986 | 0.10071 | 0.84686 | 119.9387 | -2.8336 | 119.8975 | 119.9844 | 119.783 | 0.58594 | 2.7008 | -119.8792 | -119.9753 | 2.8381 | 2.8976 | 2.6871 | 0.19684 | -0.013733 | -0.036621 | 0.004578 | -0.036621 | 122.7814 | 3.3829 | 122.58 | 3.4195 | 122.6166 | 0.13733 | 0.054931 | 122.818 | 122.731 | 0.15106 | 122.7722 | 2.8519 | 122.7356 | -120.0302 | -122.7676 | 2.7557 | 122.6944 | 2.6825 | 3.6438
887.5781 | 122.7676 | -2.8244 | 119.957 | -0.12985 | -0.0024139 | 0.016641 | 0.015131 | 0.0024482 | -0.00022641 | 0.00204 | -0.12341 | 0.16349 | 0.13216 | -0.00089503 | 0.07022 | 0.097495 | 0.0011877 | -0.19684 | 0.091553 | -0.1236 | -0.17395 | -0.064087 | -0.16479 | 0.013733 | 0.97961 | 119.9753 | -2.861 | 119.7647 | 119.8837 | 119.6732 | 119.8929 | 2.7008 | -119.8654 | -120.1309 | 2.7603 | 2.8381 | 2.6596 | 0.13733 | -0.041199 | -0.036621 | 0.018311 | -0.19226 | 122.7081 | 122.7173 | 122.4976 | 122.7539 | 122.5342 | 0.059509 | -0.050354 | 122.7448 | 122.6257 | 0.21515 | 122.8363 | 2.916 | 122.7997 | -120.0806 | -122.818 | 2.6505 | 122.5891 | 2.6276 | 3.804
889.3125 | 122.8455 | -2.8473 | 119.8837 | -0.15274 | -0.0024139 | 0.018991 | 0.012567 | -0.0035334 | 0.00084159 | 0.0046036 | -0.062378 | 0.16478 | 0.13173 | -0.0019632 | 0.067656 | 0.097282 | -0.0022301 | -0.11902 | 0.018311 | -0.091553 | -0.054932 | 0.086975 | -0.059509 | 0.11444 | 1.0437 | 119.8929 | -2.8931 | 119.783 | 119.9203 | 119.7052 | 119.8883 | 2.7557 | -119.8654 | -119.9387 | 2.9343 | 2.9617 | 2.7878 | 0.20599 | 0.032044 | -0.045776 | 0.009155 | -0.10071 | 122.7676 | 122.7356 | 122.5525 | 122.7814 | 122.5983 | 0.17853 | 0.036621 | 122.8134 | 122.6761 | 0.10986 | 122.7859 | 2.8656 | 122.7402 | -119.9753 | -122.7768 | 2.7924 | 122.6303 | 2.7283 | 3.891
890.9844 | 122.7448 | -2.7878 | 119.989 | -0.16037 | -0.00049134 | 0.018991 | 0.017053 | 0.003089 | 0.00062799 | 0.00075845 | -0.15393 | 0.16606 | 0.13088 | 0.0091452 | 0.068938 | 0.098991 | -0.00030754 | -0.16022 | 0.086975 | -0.10986 | -0.16022 | -0.086975 | -0.22888 | -0.045776 | 0.87433 | 119.9936 | -2.8244 | 119.8059 | 119.8746 | 119.6732 | 119.9158 | 2.6779 | -119.902 | -120.1492 | 2.7008 | 2.742 | 2.5589 | 0.064087 | -0.11902 | -0.036621 | 0.004577 | -0.18311 | 122.6624 | 122.7036 | 122.4609 | 122.7402 | 122.4976 | 0.022888 | -0.050354 | 122.699 | 122.6303 | 0.19684 | 122.818 | 2.8748 | 122.7814 | -120.0989 | -122.8134 | 2.6276 | 122.5937 | 2.6276 | 3.6621
892.7344 | 122.85 | -2.8107 | 119.957 | -0.17563 | -0.0032683 | 0.0207 | 0.013849 | -0.003747 | -1.2808e-05 | 0.0022536 | -0.025757 | 0.12825 | 0.13216 | -0.0070902 | 0.068938 | 0.097923 | -9.3938e-05 | -0.10986 | 0.045776 | -0.07782 | -0.036621 | 0.082397 | -0.041199 | 0.1236 | 1.0437 | 119.9707 | -2.8427 | 119.8654 | 119.9982 | 119.8013 | 119.9799 | 2.7328 | -119.9112 | -119.9936 | 2.8931 | 2.9343 | 2.7695 | 0.20142 | 0.036621 | -0.032043 | 0.013733 | -0.091553 | 122.8088 | 122.7905 | 122.612 | 122.8226 | 122.644 | 0.16022 | 0.041199 | 122.8409 | 122.7081 | 0.1236 | 122.8134 | 2.8564 | 122.7814 | -120.0348 | -122.7997 | 2.774 | 122.6761 | 2.7008 | 3.8544
894.4844 | 122.9004 | -2.774 | 119.8929 | -0.13748 | -0.0024139 | 0.017068 | 0.01449 | -0.00011542 | -1.2808e-05 | -0.0028732 | -0.034912 | 0.14 | 0.13216 | -0.0028176 | 0.068511 | 0.096855 | -0.0022301 | -0.1236 | 0.041199 | -0.086975 | -0.036621 | 0.07782 | -0.054932 | 0.11444 | 1.0483 | 119.9112 | -2.8381 | 119.8929 | 120.0211 | 119.8334 | 120.0073 | 2.6871 | -119.8517 | -119.9295 | 2.8519 | 2.8885 | 2.7191 | 0.20142 | 0.032043 | -0.064087 | 0.018311 | 0 | 122.7951 | 122.7814 | 122.6074 | 122.8455 | 122.6715 | 0.16479 | 0.050354 | 122.8592 | 122.731 | 0.12817 | 122.7493 | 2.8152 | 122.6852 | -119.9799 | -122.731 | 2.7374 | 122.6669 | 2.6505 | 3.8223
896.1719 | 122.8317 | -2.9022 | 119.8151 | -0.19852 | -0.0032683 | 0.018991 | 0.014276 | 0.0018072 | 0.00062799 | 0.00033105 | -0.047119 | 0.14 | 0.13323 | -0.0028176 | 0.070006 | 0.097068 | -0.0013757 | -0.09613 | 0.032043 | -0.068665 | -0.032043 | 0.07782 | -0.050354 | 0.10986 | 1.0574 | 119.8288 | -2.9068 | 119.7418 | 119.8883 | 119.696 | 119.8791 | 2.8336 | -119.783 | -119.8471 | 2.98 | 3.0121 | 2.8519 | 0.17853 | 0.018311 | -0.004577 | 0.013733 | -0.073242 | 122.7905 | 122.7814 | 122.5983 | 122.7859 | 122.6028 | 0.14649 | 0.036622 | 122.7951 | 122.6486 | 0.10071 | 122.7356 | 2.9343 | 122.731 | -119.8837 | -122.7219 | 2.8702 | 122.644 | 2.8061 | 3.9597
897.9062 | 122.818 | -2.7374 | 119.9982 | -0.19089 | -0.0026275 | 0.018777 | 0.017267 | -0.0041742 | -0.00086721 | 0.0011856 | -0.059326 | 0.15239 | 0.13259 | 0.0014548 | 0.068938 | 0.096641 | 0.0024695 | -0.12817 | 0.064087 | -0.091553 | -0.064087 | 0.032043 | -0.11902 | 0.07782 | 0.98419 | 120.0119 | -2.7832 | 119.8883 | 119.9844 | 119.7784 | 119.989 | 2.6459 | -119.9341 | -120.0623 | 2.7695 | 2.8152 | 2.6184 | 0.16937 | -0.027466 | -0.045776 | 0.013733 | -0.10986 | 122.7219 | 122.7264 | 122.5159 | 122.7722 | 122.5616 | 0.1236 | 0.027466 | 122.7676 | 122.6715 | 0.15564 | 122.7951 | 2.8015 | 122.7493 | -120.0897 | -122.7814 | 2.6733 | 122.6257 | 2.6093 | 3.7216
899.5781 | 122.731 | -1.918 | 120.8862 | -0.076447 | -0.0030547 | 0.018564 | 0.015772 | -0.001397 | 0.0025506 | 0.0011856 | -0.074585 | 0.12846 | 0.1328 | -0.00068143 | 0.068297 | 0.099632 | -0.00073494 | -0.16479 | 0.086975 | -0.12817 | -0.14648 | -0.036621 | -0.16022 | 0.022888 | 1.0117 | 120.9 | -1.9501 | 120.6985 | 120.7993 | 120.5978 | 120.7993 | 1.7899 | -120.7993 | -121.0327 | 1.8814 | 1.9409 | 1.7578 | 0.15106 | -0.032043 | -0.032043 | 0.013733 | -0.18768 | 122.7173 | 122.7173 | 122.5159 | 122.7493 | 122.5479 | 0.091553 | -0.01831 | 122.7493 | 122.6486 | 0.21515 | 122.85 | 2.005 | 122.818 | -121.0144 | -122.8363 | 1.7715 | 122.6166 | 1.7532 | 2.9297
901.3281 | 122.7722 | -1.9913 | 120.8267 | -0.11459 | -0.0043365 | 0.018137 | 0.015558 | -0.00032902 | -0.001081 | 0.00075845 | -0.12952 | 0.11543 | 0.13301 | 0.00038657 | 0.06787 | 0.097709 | 0.00097406 | -0.16479 | 0.068665 | -0.14191 | -0.14648 | -0.045776 | -0.16479 | 0.032043 | 0.98419 | 120.8221 | -2.0142 | 120.639 | 120.7443 | 120.5521 | 120.7809 | 1.8494 | -120.7581 | -120.9732 | 1.9455 | 2.0233 | 1.8265 | 0.17395 | -0.022888 | -0.022888 | -0.004577 | -0.18768 | 122.7356 | 122.7722 | 122.5433 | 122.7951 | 122.5662 | 0.096131 | -0.004577 | 122.7585 | 122.6532 | 0.21057 | 122.8363 | 2.0599 | 122.8134 | -120.9686 | -122.8409 | 1.8448 | 122.6303 | 1.8265 | 2.9755
903.0625 | 122.731 | -1.9592 | 120.8359 | -0.14511 | -0.0013457 | 0.019205 | 0.013635 | -0.004815 | 0.0010554 | 0.0013992 | -0.041016 | 0.11287 | 0.13494 | 0.0010276 | 0.069152 | 0.095573 | -0.0045801 | -0.11902 | 0.068665 | -0.10071 | -0.09613 | 0.036621 | -0.10986 | 0.082397 | 1.0483 | 120.8588 | -1.9638 | 120.6573 | 120.7672 | 120.5887 | 120.7718 | 1.8585 | -120.7672 | -120.932 | 1.9959 | 2.0416 | 1.8494 | 0.18311 | -0.009155 | -0.004577 | 0.022889 | -0.17853 | 122.7264 | 122.731 | 122.5479 | 122.7356 | 122.5525 | 0.13733 | 0.004578 | 122.731 | 122.6212 | 0.16937 | 122.8226 | 2.0279 | 122.818 | -120.9366 | -122.7997 | 1.8631 | 122.6166 | 1.8402 | 3.0075
904.7344 | 122.7814 | -2.0142 | 120.7718 | -0.11459 | 0.0010041 | 0.020273 | 0.017053 | 0.00095278 | 0.0021234 | 0.00075845 | -0.14783 | 0.11073 | 0.13344 | 0.0012412 | 0.068725 | 0.099632 | -0.0013757 | -0.10529 | 0.086975 | -0.11444 | -0.068665 | 0.032043 | -0.13733 | 0.068665 | 1.0941 | 120.7947 | -2.0142 | 120.6665 | 120.7352 | 120.5383 | 120.7397 | 1.8997 | -120.6848 | -120.8405 | 2.0462 | 2.0828 | 1.8768 | 0.18311 | -0.022888 | 0 | 0.022888 | -0.10529 | 122.7493 | 122.7539 | 122.5525 | 122.7539 | 122.5525 | 0.14648 | 0.045776 | 122.7493 | 122.6807 | 0.20142 | 122.8088 | 2.1011 | 122.8088 | -120.8862 | -122.7859 | 1.9455 | 122.6807 | 1.9089 | 3.1082
906.4688 | 122.7402 | -1.9913 | 120.8267 | -0.15274 | -0.0011321 | 0.019632 | 0.017694 | 9.818e-05 | -0.00044001 | -0.0011642 | -0.14478 | 0.12077 | 0.13173 | -0.00025423 | 0.069793 | 0.098136 | 0.00054686 | -0.14648 | 0.091553 | -0.11444 | -0.15564 | -0.054932 | -0.21057 | 0.009155 | 0.91553 | 120.8176 | -2.0187 | 120.6162 | 120.7031 | 120.5246 | 120.7489 | 1.8768 | -120.7352 | -120.9824 | 1.9363 | 2.0004 | 1.7807 | 0.1236 | -0.09613 | -0.027466 | -0.009155 | -0.21057 | 122.6944 | 122.7402 | 122.5159 | 122.7676 | 122.5433 | 0.059509 | -0.041199 | 122.7219 | 122.6349 | 0.20599 | 122.8363 | 2.0828 | 122.8088 | -120.9412 | -122.8455 | 1.8356 | 122.6074 | 1.8448 | 2.9068
908.2031 | 122.7219 | -2.0279 | 120.7718 | -0.12222 | -0.00049134 | 0.01835 | 0.018335 | 0.0020208 | 0.00062799 | -0.00052335 | -0.13867 | 0.12953 | 0.13259 | 0.0012412 | 0.069793 | 0.099632 | -0.0026575 | -0.10986 | 0.07782 | -0.12817 | -0.11902 | 0.004578 | -0.17395 | 0.027466 | 1.0254 | 120.7993 | -2.0462 | 120.5933 | 120.6573 | 120.4559 | 120.6985 | 1.8997 | -120.694 | -120.8908 | 2.0325 | 2.0554 | 1.8539 | 0.15564 | -0.045776 | -0.018311 | 0.027465 | -0.17853 | 122.6852 | 122.7264 | 122.4838 | 122.7448 | 122.5021 | 0.13275 | 0.009155 | 122.7036 | 122.6395 | 0.20599 | 122.8455 | 2.1057 | 122.8271 | -120.9 | -122.818 | 1.9089 | 122.6212 | 1.918 | 3.0533
909.875 | 122.7905 | -1.9684 | 120.7672 | -0.16037 | -0.00070494 | 0.018564 | 0.018976 | 0.003089 | 0.001269 | 0.00075845 | -0.10815 | 0.14149 | 0.13579 | -0.003245 | 0.069579 | 0.099418 | 0.00076046 | -0.14191 | 0.10529 | -0.1236 | -0.14191 | -0.018311 | -0.19684 | 0.032043 | 0.95673 | 120.8038 | -2.0142 | 120.6573 | 120.726 | 120.52 | 120.7672 | 1.8448 | -120.6619 | -120.9091 | 1.9501 | 2.0004 | 1.7715 | 0.15564 | -0.073242 | -0.045776 | 0.036621 | -0.10986 | 122.6944 | 122.7356 | 122.4884 | 122.7814 | 122.5342 | 0.10528 | -0.018311 | 122.7402 | 122.6715 | 0.22888 | 122.818 | 2.0737 | 122.7722 | -120.8908 | -122.7814 | 1.8265 | 122.6257 | 1.8265 | 2.9251
911.625 | 122.8775 | -1.9089 | 120.7809 | -0.17563 | -0.0028411 | 0.016428 | 0.014704 | -0.006524 | 0.00020079 | 0.00097205 | -0.016602 | 0.14982 | 0.13088 | -0.0019632 | 0.069579 | 0.098564 | -0.0015893 | -0.10986 | 0.050354 | -0.086975 | -0.022888 | 0.13275 | -0.032043 | 0.16479 | 1.1673 | 120.8176 | -1.9318 | 120.7397 | 120.8862 | 120.6711 | 120.8588 | 1.8219 | -120.7306 | -120.8038 | 2.0416 | 2.0737 | 1.8768 | 0.25177 | 0.054932 | -0.022888 | 0.036621 | -0.041199 | 122.7951 | 122.7676 | 122.58 | 122.7905 | 122.6028 | 0.21973 | 0.064087 | 122.818 | 122.6715 | 0.13733 | 122.7493 | 1.9592 | 122.7264 | -120.8679 | -122.7127 | 1.886 | 122.6486 | 1.799 | 3.0762
913.3594 | 122.7219 | -2.0142 | 120.7809 | -0.15274 | 0.0012177 | 0.018991 | 0.019403 | -0.0033196 | -0.0015082 | 0.00075845 | -0.12952 | 0.11949 | 0.13259 | 0.0023092 | 0.071074 | 0.098991 | -0.0015893 | -0.15106 | 0.091553 | -0.10986 | -0.17853 | -0.082397 | -0.23804 | -0.022888 | 1.03 | 120.7855 | -2.0325 | 120.5887 | 120.6528 | 120.4605 | 120.7031 | 1.9043 | -120.6894 | -120.9595 | 1.9318 | 1.9913 | 1.7761 | 0.086975 | -0.12817 | -0.018311 | 0.004577 | -0.19226 | 122.6669 | 122.7173 | 122.4747 | 122.7356 | 122.493 | 0.027466 | -0.068665 | 122.6852 | 122.6212 | 0.20142 | 122.818 | 2.1057 | 122.7997 | -120.8908 | -122.8134 | 1.8356 | 122.6028 | 1.8631 | 3.0441
915.0938 | 122.8317 | -2.0096 | 120.7031 | -0.15274 | -0.0013457 | 0.022836 | 0.01919 | -0.0011834 | 0.0021234 | 0.00204 | -0.095947 | 0.13188 | 0.13216 | -0.0017496 | 0.069152 | 0.098777 | 0.0020423 | -0.13275 | 0.086975 | -0.10529 | -0.10986 | 0.032043 | -0.16022 | 0.054932 | 1.0529 | 120.7123 | -2.0599 | 120.6345 | 120.726 | 120.5109 | 120.7214 | 1.9043 | -120.6162 | -120.813 | 2.0416 | 2.0645 | 1.8494 | 0.16022 | -0.054931 | -0.050354 | 0.009155 | -0.068665 | 122.7356 | 122.731 | 122.5204 | 122.7814 | 122.5708 | 0.13733 | -0.004577 | 122.7859 | 122.6944 | 0.19226 | 122.7722 | 2.0966 | 122.7219 | -120.8084 | -122.7631 | 1.8997 | 122.644 | 1.8768 | 3.0624
916.7656 | 122.8592 | -2.0279 | 120.6345 | -0.13748 | -0.0030547 | 0.019632 | 0.014276 | -0.003747 | 0.001269 | -0.0022324 | 0.001709 | 0.10838 | 0.13323 | -0.0049538 | 0.070647 | 0.097495 | -0.00094854 | -0.086975 | 0.041199 | -0.09613 | -0.022888 | 0.13275 | -0.022888 | 0.15106 | 1.1581 | 120.6757 | -2.0737 | 120.6162 | 120.7535 | 120.5475 | 120.7352 | 1.9318 | -120.5933 | -120.6573 | 2.1606 | 2.179 | 2.005 | 0.24719 | 0.073242 | -0.045776 | 0.041199 | -0.01831 | 122.7814 | 122.7631 | 122.5754 | 122.8088 | 122.6212 | 0.22888 | 0.073242 | 122.8271 | 122.6898 | 0.13733 | 122.7493 | 2.0691 | 122.7036 | -120.7306 | -122.7081 | 2.005 | 122.644 | 1.9409 | 3.186
918.5 | 122.7173 | -2.0508 | 120.7214 | -0.099335 | -0.0013457 | 0.019632 | 0.019403 | 0.0018072 | 0.00062799 | 0.0028946 | -0.16614 | 0.14341 | 0.13259 | 0.0053 | 0.067229 | 0.09835 | -0.00052114 | -0.1236 | 0.073242 | -0.10529 | -0.11902 | -0.018311 | -0.16022 | 0.027466 | 1.0391 | 120.7077 | -2.0828 | 120.5338 | 120.6162 | 120.3827 | 120.639 | 1.9455 | -120.6482 | -120.8405 | 2.0325 | 2.0782 | 1.8906 | 0.13275 | -0.054931 | -0.032044 | -0.013733 | -0.18768 | 122.6669 | 122.6898 | 122.4335 | 122.7219 | 122.4655 | 0.086975 | -0.013733 | 122.699 | 122.6166 | 0.17853 | 122.7905 | 2.124 | 122.7585 | -120.8267 | -122.8043 | 1.9318 | 122.5845 | 1.9272 | 3.0899
920.1875 | 122.8363 | -2.0325 | 120.6619 | -0.19852 | -0.0011321 | 0.021982 | 0.017481 | -0.00075622 | 0.002978 | 0.0016128 | -0.059326 | 0.15217 | 0.13323 | -0.0013224 | 0.068938 | 0.09835 | -0.0054345 | -0.091553 | 0.041199 | -0.073242 | -0.027466 | 0.091553 | -0.073242 | 0.11902 | 1.0483 | 120.6711 | -2.0645 | 120.6207 | 120.7077 | 120.5063 | 120.7169 | 1.9592 | -120.6207 | -120.6894 | 2.124 | 2.1515 | 1.9592 | 0.19226 | 0 | -0.032043 | 0.009156 | -0.041198 | 122.7402 | 122.7493 | 122.5388 | 122.7814 | 122.5708 | 0.16479 | 0.045776 | 122.7722 | 122.6852 | 0.11444 | 122.7356 | 2.0737 | 122.7036 | -120.7352 | -122.7264 | 2.005 | 122.6532 | 1.9409 | 3.0808
921.9375 | 122.7493 | -2.1194 | 120.6665 | -0.17563 | -0.0022003 | 0.0207 | 0.017694 | 0.00052558 | 0.00084159 | -9.6154e-05 | -0.12646 | 0.12333 | 0.13195 | 0.007009 | 0.068511 | 0.098777 | -0.00030754 | -0.1236 | 0.059509 | -0.11444 | -0.10071 | -0.009155 | -0.12817 | 0.027466 | 1.03 | 120.6711 | -2.1194 | 120.488 | 120.5521 | 120.369 | 120.607 | 2.005 | -120.607 | -120.7672 | 2.1103 | 2.1469 | 1.9913 | 0.14191 | -0.013733 | 0 | 0.004578 | -0.17853 | 122.6715 | 122.7264 | 122.4884 | 122.7264 | 122.4884 | 0.10529 | 0.013733 | 122.6715 | 122.6074 | 0.17395 | 122.7905 | 2.179 | 122.7905 | -120.7809 | -122.7859 | 2.0187 | 122.6074 | 1.9958 | 3.1494
923.6719 | 122.7173 | -2.1469 | 120.6345 | -0.12985 | -0.0056183 | 0.018991 | 0.014276 | -0.0011834 | -1.2808e-05 | 0.0018264 | -0.050171 | 0.1244 | 0.13536 | -0.004313 | 0.068297 | 0.099418 | 0.00076046 | -0.12817 | 0.07782 | -0.10529 | -0.13275 | -0.009155 | -0.13733 | 0.064087 | 0.94299 | 120.6436 | -2.1515 | 120.4193 | 120.5429 | 120.3415 | 120.5383 | 2.0416 | -120.5566 | -120.7672 | 2.1378 | 2.211 | 2.0096 | 0.16937 | -0.032043 | -0.004577 | 0.009156 | -0.21515 | 122.6898 | 122.6852 | 122.4884 | 122.6898 | 122.493 | 0.096131 | -0.027465 | 122.6944 | 122.5708 | 0.18311 | 122.7951 | 2.2247 | 122.7905 | -120.7397 | -122.7859 | 2.0142 | 122.5662 | 2.0187 | 3.0899
925.3438 | 122.7493 | -2.1698 | 120.5841 | -0.099335 | -0.0015595 | 0.017709 | 0.016413 | 0.0062934 | -0.00022641 | 0.0022536 | -0.10815 | 0.16414 | 0.13173 | 0.0020956 | 0.067016 | 0.097709 | -0.0015893 | -0.14191 | 0.10071 | -0.11902 | -0.11902 | -0.018311 | -0.1236 | 0.041199 | 1.0574 | 120.6116 | -2.1835 | 120.433 | 120.5429 | 120.3369 | 120.5704 | 2.0508 | -120.4834 | -120.7031 | 2.1515 | 2.211 | 2.0462 | 0.16022 | -0.004577 | -0.013733 | 0.027466 | -0.15106 | 122.7127 | 122.7402 | 122.5067 | 122.7539 | 122.5204 | 0.10071 | 0 | 122.7264 | 122.6166 | 0.21973 | 122.7951 | 2.2705 | 122.7814 | -120.7031 | -122.7676 | 2.0508 | 122.6028 | 2.0279 | 3.2272
927.0938 | 122.8134 | -2.0645 | 120.639 | -0.18326 | -0.00091854 | 0.020486 | 0.014917 | 0.00052558 | 0.0019098 | 0.00075845 | -0.022705 | 0.12355 | 0.13344 | 0.002523 | 0.069793 | 0.097923 | -0.0050073 | -0.07782 | 0.059509 | -0.068665 | -0.027466 | 0.086975 | -0.068665 | 0.11902 | 1.1078 | 120.6482 | -2.0737 | 120.5612 | 120.6573 | 120.4422 | 120.6573 | 1.9958 | -120.5795 | -120.6665 | 2.1515 | 2.1835 | 1.9958 | 0.18768 | 0 | -0.009155 | 0.009155 | -0.07782 | 122.7219 | 122.7219 | 122.5067 | 122.731 | 122.5159 | 0.15564 | 0.041199 | 122.731 | 122.6349 | 0.12817 | 122.7219 | 2.124 | 122.7127 | -120.7077 | -122.7127 | 2.037 | 122.6257 | 1.9867 | 3.1723
928.7656 | 122.8043 | -1.9501 | 120.7626 | -0.168 | -0.0015595 | 0.020059 | 0.016199 | 0.0024482 | 0.00041439 | 0.0018264 | -0.022705 | 0.1118 | 0.13366 | -0.00089503 | 0.069365 | 0.097709 | 0.00076046 | -0.09613 | 0.050354 | -0.068665 | -0.036621 | 0.091553 | -0.086975 | 0.086975 | 1.0437 | 120.7397 | -1.9958 | 120.6345 | 120.7535 | 120.5704 | 120.7855 | 1.8814 | -120.7123 | -120.7993 | 2.0416 | 2.037 | 1.8631 | 0.15564 | -0.01831 | -0.045777 | -0.022888 | -0.12817 | 122.7036 | 122.7356 | 122.5204 | 122.7814 | 122.5662 | 0.16022 | 0.032044 | 122.7493 | 122.6303 | 0.11902 | 122.7356 | 2.0004 | 122.6898 | -120.8313 | -122.7585 | 1.9135 | 122.5845 | 1.8539 | 2.9938
930.5 | 122.7539 | -1.9135 | 120.8313 | -0.15274 | 0.0012177 | 0.018777 | 0.019831 | 0.003089 | 0.00020079 | 0.0016128 | -0.098999 | 0.11586 | 0.13195 | -0.00025423 | 0.068725 | 0.098564 | -0.0030847 | -0.10529 | 0.082397 | -0.10529 | -0.073242 | 0.018311 | -0.11902 | 0.045776 | 1.1169 | 120.8817 | -1.9547 | 120.6894 | 120.7535 | 120.607 | 120.8267 | 1.8082 | -120.7489 | -120.9045 | 1.9318 | 1.9592 | 1.7944 | 0.15106 | -0.013733 | -0.041199 | 0.050354 | -0.14191 | 122.6669 | 122.7402 | 122.5204 | 122.7814 | 122.5616 | 0.1236 | 0.032044 | 122.7081 | 122.644 | 0.18768 | 122.8363 | 1.9958 | 122.7951 | -120.9366 | -122.7859 | 1.8402 | 122.6028 | 1.8082 | 3.0304
932.25 | 122.8363 | -2.0187 | 120.6436 | -0.18326 | -0.0024139 | 0.020059 | 0.016413 | 0.00031198 | 0.0031916 | 0.0022536 | -0.077637 | 0.11244 | 0.13088 | -0.0062356 | 0.069152 | 0.098991 | 0.00097406 | -0.073242 | 0.032043 | -0.086975 | -0.027466 | 0.068665 | -0.064087 | 0.10071 | 1.0895 | 120.6711 | -2.0416 | 120.6345 | 120.7031 | 120.5109 | 120.7214 | 1.9318 | -120.6116 | -120.6711 | 2.0874 | 2.1194 | 1.9547 | 0.18768 | 0.022888 | -0.022888 | 0.027466 | -0.009156 | 122.7219 | 122.7402 | 122.5296 | 122.7631 | 122.5525 | 0.15564 | 0.059509 | 122.7448 | 122.6761 | 0.11902 | 122.7127 | 2.0508 | 122.6898 | -120.7306 | -122.6852 | 1.9913 | 122.6532 | 1.9455 | 3.1082
933.9375 | 122.7402 | -2.1103 | 120.607 | -0.15274 | -0.00091854 | 0.018991 | 0.017267 | 0.0033026 | 0.00084159 | 0.0050308 | -0.095947 | 0.11393 | 0.13323 | 0.0059408 | 0.067443 | 0.099418 | -0.0011621 | -0.091553 | 0.059509 | -0.10986 | -0.07782 | 0.018311 | -0.11902 | 0.036621 | 1.0986 | 120.6528 | -2.1286 | 120.5017 | 120.5704 | 120.3918 | 120.607 | 2.0004 | -120.5475 | -120.6848 | 2.1286 | 2.1469 | 1.9913 | 0.14648 | -0.009156 | -0.01831 | 0.045776 | -0.10529 | 122.6807 | 122.7173 | 122.5021 | 122.7356 | 122.5204 | 0.12817 | 0.032043 | 122.699 | 122.6303 | 0.16937 | 122.7814 | 2.1698 | 122.7631 | -120.7169 | -122.7356 | 2.0325 | 122.612 | 2.0187 | 3.2089
935.6875 | 122.7585 | -2.1011 | 120.6528 | -0.15274 | 0.00014946 | 0.019205 | 0.018549 | -0.00075622 | 0.00020079 | 0.00204 | -0.10815 | 0.11244 | 0.13494 | 0.0010276 | 0.068511 | 0.099632 | 0.0037513 | -0.10986 | 0.07782 | -0.10529 | -0.09613 | 0.022888 | -0.11444 | 0.036621 | 1.1353 | 120.6482 | -2.124 | 120.5154 | 120.5887 | 120.3964 | 120.6207 | 1.9958 | -120.575 | -120.7489 | 2.124 | 2.1378 | 1.9867 | 0.14191 | -0.009155 | -0.022888 | -0.004578 | -0.13733 | 122.6898 | 122.7219 | 122.4976 | 122.7448 | 122.5204 | 0.12817 | 0.009156 | 122.7127 | 122.6395 | 0.18311 | 122.7722 | 2.179 | 122.7493 | -120.7581 | -122.7768 | 2.005 | 122.6166 | 1.9913 | 3.2364
937.375 | 122.7402 | -2.1011 | 120.6299 | -0.12985 | -0.00091854 | 0.018991 | 0.017267 | -0.00011542 | 0.00062799 | 0.00075845 | -0.095947 | 0.11842 | 0.13259 | -0.0075174 | 0.068511 | 0.097495 | -0.00073494 | -0.16479 | 0.07782 | -0.12817 | -0.13733 | -0.045776 | -0.19684 | -0.009155 | 1.0345 | 120.6573 | -2.1515 | 120.5063 | 120.575 | 120.3735 | 120.6207 | 1.973 | -120.5521 | -120.7672 | 2.0554 | 2.092 | 1.9043 | 0.11902 | -0.068664 | -0.050354 | 0.027466 | -0.1236 | 122.6761 | 122.7219 | 122.4747 | 122.7722 | 122.525 | 0.082398 | -0.009155 | 122.7264 | 122.6578 | 0.20599 | 122.8088 | 2.179 | 122.7585 | -120.7581 | -122.7814 | 1.9638 | 122.6074 | 1.9363 | 3.1357
939.125 | 122.731 | -2.0645 | 120.7077 | -0.076447 | -0.0011321 | 0.019632 | 0.015772 | -0.0018244 | 0.0021234 | 0.0016128 | -0.053223 | 0.12098 | 0.13216 | 0.00017297 | 0.069579 | 0.096427 | -0.00094854 | -0.17395 | 0.091553 | -0.1236 | -0.16022 | -0.059509 | -0.13733 | 0 | 1.03 | 120.7031 | -2.1011 | 120.4834 | 120.5841 | 120.4147 | 120.607 | 1.9409 | -120.6161 | -120.8679 | 2.005 | 2.0645 | 1.9272 | 0.1236 | -0.013733 | -0.036621 | -0.004578 | -0.22431 | 122.6486 | 122.6715 | 122.4792 | 122.7081 | 122.5159 | 0.064087 | -0.036621 | 122.6852 | 122.5845 | 0.21515 | 122.8043 | 2.1561 | 122.7676 | -120.8313 | -122.8088 | 1.9043 | 122.5479 | 1.8906 | 3.0945
940.8125 | 122.699 | -2.1011 | 120.6436 | -0.168 | -0.0022003 | 0.020914 | 0.018976 | 0.00095278 | -0.00065361 | 0.00097205 | -0.089844 | 0.11863 | 0.1343 | 0.0042318 | 0.069152 | 0.09835 | -0.00030754 | -0.16937 | 0.091553 | -0.10986 | -0.16479 | -0.082397 | -0.20599 | -0.032043 | 0.97504 | 120.6665 | -2.1423 | 120.4651 | 120.5292 | 120.3369 | 120.5933 | 1.9913 | -120.5521 | -120.8084 | 2.0187 | 2.0691 | 1.8951 | 0.07782 | -0.096131 | -0.041199 | 0.022888 | -0.17853 | 122.6303 | 122.6944 | 122.438 | 122.7356 | 122.4792 | 0.027466 | -0.054932 | 122.6715 | 122.6074 | 0.20142 | 122.8088 | 2.1927 | 122.7676 | -120.7535 | -122.7859 | 1.9363 | 122.5662 | 1.9318 | 3.0762
942.5625 | 122.6761 | -2.0462 | 120.6894 | -0.168 | -0.00091854 | 0.021127 | 0.018976 | 0.0024482 | 0.001269 | -0.00052335 | -0.095947 | 0.11607 | 0.13366 | -0.004313 | 0.071074 | 0.099418 | 0.0035377 | -0.13275 | 0.091553 | -0.1236 | -0.16022 | -0.07782 | -0.17853 | -0.032043 | 0.95673 | 120.7306 | -2.092 | 120.4788 | 120.5612 | 120.3598 | 120.607 | 1.9226 | -120.5978 | -120.8496 | 1.9684 | 2.0142 | 1.8677 | 0.091553 | -0.054932 | -0.045776 | 0.041199 | -0.21057 | 122.6074 | 122.6532 | 122.406 | 122.699 | 122.4518 | 0.045776 | -0.036621 | 122.6532 | 122.5708 | 0.21515 | 122.8226 | 2.1378 | 122.7768 | -120.813 | -122.7814 | 1.886 | 122.525 | 1.9135 | 3.0029
944.3125 | 122.6944 | -1.9363 | 120.8221 | -0.18326 | -0.0017731 | 0.0207 | 0.017053 | 0.0028754 | 0.0021234 | 0.0013992 | -0.092895 | 0.11607 | 0.13088 | 0.0020956 | 0.069579 | 0.097709 | -0.0013757 | -0.1236 | 0.068665 | -0.11444 | -0.1236 | -0.027466 | -0.16479 | -0.013733 | 1.0803 | 120.8588 | -1.9409 | 120.6207 | 120.7031 | 120.4834 | 120.7214 | 1.8219 | -120.7535 | -120.9457 | 1.9089 | 1.9226 | 1.7715 | 0.10071 | -0.050354 | -0.004578 | 0.036621 | -0.20142 | 122.6395 | 122.6578 | 122.4197 | 122.6624 | 122.4243 | 0.086975 | -0.009155 | 122.644 | 122.5616 | 0.18311 | 122.7997 | 2.005 | 122.7951 | -120.9366 | -122.7631 | 1.8127 | 122.5571 | 1.8127 | 3.0167
946 | 122.7859 | -1.9775 | 120.7397 | -0.168 | -0.0028411 | 0.019632 | 0.016199 | 0.00073918 | 0.0021234 | 0.00097205 | 0.023071 | 0.10817 | 0.13344 | -0.004313 | 0.069793 | 0.097282 | 0.00076046 | -0.13733 | 0.050354 | -0.09613 | -0.082397 | 0.036621 | -0.09613 | 0.068665 | 1.0437 | 120.7352 | -2.0187 | 120.5887 | 120.7031 | 120.5154 | 120.7214 | 1.8814 | -120.6894 | -120.8221 | 2.0142 | 2.0462 | 1.8814 | 0.16479 | 0 | -0.041199 | -0.004578 | -0.15106 | 122.6807 | 122.699 | 122.493 | 122.7402 | 122.5342 | 0.13275 | 0.013733 | 122.7219 | 122.6074 | 0.14648 | 122.7539 | 2.0279 | 122.7127 | -120.8359 | -122.7585 | 1.8951 | 122.5662 | 1.8402 | 3.0212
947.75 | 122.7814 | -1.9867 | 120.7077 | -0.19852 | -0.0026275 | 0.020059 | 0.013635 | 0.00031198 | 0.0019098 | 0.00033105 | 0.001709 | 0.12312 | 0.13259 | -0.00068143 | 0.069365 | 0.097282 | -0.0015893 | -0.09613 | 0.059509 | -0.068665 | -0.068665 | 0.086975 | -0.082397 | 0.086975 | 1.0941 | 120.6985 | -2.0096 | 120.5978 | 120.694 | 120.5109 | 120.7169 | 1.918 | -120.6482 | -120.7764 | 2.0737 | 2.0737 | 1.9043 | 0.15564 | -0.013732 | -0.022889 | -0.009156 | -0.10986 | 122.6807 | 122.7036 | 122.4976 | 122.7264 | 122.5204 | 0.15564 | 0 | 122.7036 | 122.6074 | 0.12817 | 122.7081 | 2.0462 | 122.6852 | -120.7764 | -122.7173 | 1.918 | 122.5845 | 1.8906 | 3.0807
949.4375 | 122.7814 | -2.0142 | 120.6848 | -0.13748 | -0.0019867 | 0.016428 | 0.013422 | -0.003106 | 0.0014826 | -9.6154e-05 | -0.0043944 | 0.12205 | 0.13216 | -0.00068143 | 0.068725 | 0.095573 | -0.0043665 | -0.086975 | 0.059509 | -0.073242 | -0.032043 | 0.073242 | -0.036621 | 0.10071 | 1.1993 | 120.6802 | -2.0508 | 120.5704 | 120.6848 | 120.52 | 120.7077 | 1.9409 | -120.6253 | -120.7169 | 2.0874 | 2.1149 | 1.9775 | 0.17395 | 0.036621 | -0.036621 | -0.004577 | -0.11444 | 122.699 | 122.7219 | 122.5342 | 122.7585 | 122.5708 | 0.14648 | 0.041199 | 122.7356 | 122.6212 | 0.13275 | 122.731 | 2.0737 | 122.6944 | -120.7581 | -122.7356 | 1.9821 | 122.5845 | 1.9272 | 3.2135
951.1875 | 122.7081 | -2.037 | 120.694 | -0.16037 | -6.4144e-05 | 0.019632 | 0.019831 | -0.00032902 | 0.0051142 | 0.00097205 | -0.092895 | 0.11073 | 0.1343 | -0.0021768 | 0.068084 | 0.097923 | 0.0016151 | -0.15106 | 0.10071 | -0.10986 | -0.15564 | -0.064087 | -0.1831 | -0.004578 | 1.0025 | 120.694 | -2.0599 | 120.5383 | 120.5978 | 120.401 | 120.6757 | 1.9272 | -120.5933 | -120.8496 | 1.973 | 2.0325 | 1.8539 | 0.10529 | -0.073242 | -0.022889 | 0 | -0.15564 | 122.6349 | 122.7127 | 122.438 | 122.7356 | 122.4609 | 0.045776 | -0.045777 | 122.6578 | 122.5983 | 0.21057 | 122.7539 | 2.1378 | 122.731 | -120.8038 | -122.7539 | 1.8814 | 122.5754 | 1.886 | 3.0396
952.9219 | 122.8043 | -2.1835 | 120.4788 | -0.12222 | -0.0034821 | 0.017068 | 0.015344 | -0.0022516 | -1.2808e-05 | 0.0039626 | 0.023071 | 0.089581 | 0.13216 | -0.0030312 | 0.069793 | 0.097495 | -0.00052114 | -0.11902 | 0.050354 | -0.091553 | -0.091553 | 0.013733 | -0.11444 | 0.064087 | 1.1307 | 120.52 | -2.2339 | 120.4147 | 120.5017 | 120.3323 | 120.5246 | 2.092 | -120.4285 | -120.5704 | 2.1973 | 2.2476 | 2.0691 | 0.15564 | -0.022888 | -0.050354 | 0.041199 | -0.064087 | 122.6852 | 122.7081 | 122.5159 | 122.7585 | 122.5662 | 0.10529 | 0 | 122.7356 | 122.6486 | 0.14191 | 122.7539 | 2.2339 | 122.7036 | -120.5704 | -122.7127 | 2.092 | 122.5983 | 2.0645 | 3.3142
954.6562 | 122.8226 | -2.1332 | 120.5109 | -0.19089 | -0.0011321 | 0.020914 | 0.017267 | 0.0026618 | 0.0016962 | -0.0011642 | -0.037964 | 0.085949 | 0.1328 | 0.0020956 | 0.068297 | 0.09835 | 0.0020423 | -0.068665 | 0.050354 | -0.064087 | -0.013733 | 0.09613 | -0.064087 | 0.09613 | 1.2039 | 120.5338 | -2.1606 | 120.5017 | 120.575 | 120.3873 | 120.5978 | 2.0691 | -120.4605 | -120.5246 | 2.2293 | 2.2293 | 2.0691 | 0.16022 | 0 | -0.027466 | 0.022888 | -0.009155 | 122.7081 | 122.731 | 122.5204 | 122.7585 | 122.5479 | 0.16022 | 0.050354 | 122.7356 | 122.6624 | 0.11444 | 122.6944 | 2.1835 | 122.6669 | -120.575 | -122.6715 | 2.1194 | 122.6349 | 2.0645 | 3.3371
956.3906 | 122.8226 | -2.2064 | 120.4651 | -0.20615 | -0.0013457 | 0.019205 | 0.018549 | 0.0052252 | 0.0038324 | 0.00097205 | -0.086792 | 0.092571 | 0.13088 | -0.0017496 | 0.066802 | 0.09835 | -0.0041527 | -0.086975 | 0.059509 | -0.10071 | -0.041199 | 0.068665 | -0.07782 | 0.07782 | 1.2085 | 120.4559 | -2.2522 | 120.4376 | 120.4971 | 120.3232 | 120.5429 | 2.1057 | -120.4056 | -120.5063 | 2.2751 | 2.2842 | 2.1286 | 0.17853 | 0.022888 | -0.045776 | -0.009155 | -0.027466 | 122.7036 | 122.7493 | 122.5296 | 122.7951 | 122.5754 | 0.16937 | 0.059509 | 122.7493 | 122.6898 | 0.16022 | 122.7081 | 2.2659 | 122.6624 | -120.5658 | -122.7173 | 2.1652 | 122.644 | 2.1194 | 3.4149
958.125 | 122.8226 | -2.2385 | 120.4239 | -0.19852 | -0.00070494 | 0.020273 | 0.016199 | 0.00073918 | 0.002978 | 0.0013992 | -0.080688 | 0.10411 | 0.13195 | 0.0016684 | 0.067229 | 0.096641 | 0.0028967 | -0.07782 | 0.068665 | -0.086975 | -0.027466 | 0.082397 | -0.059509 | 0.086975 | 1.1902 | 120.4239 | -2.2705 | 120.3964 | 120.4468 | 120.2682 | 120.4971 | 2.1515 | -120.3552 | -120.4514 | 2.3209 | 2.3254 | 2.179 | 0.17395 | 0.027466 | -0.032044 | 0 | -0.027466 | 122.6852 | 122.7356 | 122.5067 | 122.7676 | 122.5388 | 0.16937 | 0.059509 | 122.7173 | 122.6669 | 0.15564 | 122.6944 | 2.3071 | 122.6624 | -120.5109 | -122.6944 | 2.211 | 122.6349 | 2.1606 | 3.4287
959.7969 | 122.8409 | -2.2476 | 120.4239 | -0.15274 | -0.0028411 | 0.01835 | 0.015344 | 0.0011664 | 0.0027644 | 0.00075845 | -0.010498 | 0.095135 | 0.13323 | -0.0019632 | 0.067443 | 0.096855 | 0.00011966 | -0.10986 | 0.054932 | -0.091553 | -0.022888 | 0.09613 | -0.022888 | 0.1236 | 1.2817 | 120.433 | -2.2659 | 120.401 | 120.4971 | 120.3323 | 120.5109 | 2.1561 | -120.369 | -120.4468 | 2.3438 | 2.3712 | 2.2247 | 0.21515 | 0.068665 | -0.01831 | 0.009155 | -0.022888 | 122.7448 | 122.7585 | 122.58 | 122.7768 | 122.5983 | 0.18768 | 0.068665 | 122.7631 | 122.6669 | 0.14649 | 122.699 | 2.3026 | 122.6807 | -120.5154 | -122.6898 | 2.2247 | 122.6486 | 2.1378 | 3.5294
961.5312 | 122.7356 | -2.3209 | 120.4193 | -0.15274 | -0.0019867 | 0.017709 | 0.017053 | -0.0039606 | 0.0014826 | 0.00097205 | -0.10205 | 0.085735 | 0.13387 | 0.0029502 | 0.069152 | 0.099204 | -0.00030754 | -0.14191 | 0.086975 | -0.1236 | -0.11444 | -0.027466 | -0.13733 | 0.004578 | 1.2268 | 120.4788 | -2.3346 | 120.3094 | 120.3827 | 120.195 | 120.4193 | 2.1973 | -120.3323 | -120.5338 | 2.2934 | 2.3254 | 2.1835 | 0.12817 | -0.013733 | -0.013733 | 0.059509 | -0.10986 | 122.7036 | 122.7402 | 122.5159 | 122.7539 | 122.5296 | 0.09613 | 0.009155 | 122.7173 | 122.644 | 0.21057 | 122.8134 | 2.4078 | 122.7997 | -120.5429 | -122.7539 | 2.2064 | 122.6303 | 2.179 | 3.5477
963.2812 | 122.6944 | -2.3163 | 120.4102 | -0.12985 | -0.00091854 | 0.020486 | 0.017481 | 0.00073918 | 0.0038324 | -0.00052335 | -0.13562 | 0.089153 | 0.13366 | 0.00017297 | 0.068511 | 0.099632 | -0.0013757 | -0.1236 | 0.068665 | -0.10986 | -0.11902 | -0.009155 | -0.16022 | 0.004578 | 1.2222 | 120.4697 | -2.3575 | 120.2591 | 120.3186 | 120.1218 | 120.369 | 2.2064 | -120.3415 | -120.5292 | 2.3071 | 2.3209 | 2.1561 | 0.11444 | -0.050354 | -0.041199 | 0.05951 | -0.15106 | 122.6349 | 122.6852 | 122.438 | 122.7264 | 122.4792 | 0.10071 | -0.009156 | 122.6761 | 122.6166 | 0.17853 | 122.8271 | 2.3849 | 122.7859 | -120.52 | -122.7676 | 2.1973 | 122.5754 | 2.1927 | 3.5385
964.9531 | 122.7951 | -2.2614 | 120.3964 | -0.13748 | -6.4144e-05 | 0.020486 | 0.018762 | 0.0035162 | 0.0021234 | 0.0011856 | -0.089844 | 0.093639 | 0.1343 | -0.00944 | 0.07022 | 0.099632 | -0.0013757 | -0.14191 | 0.086975 | -0.11444 | -0.10071 | 0 | -0.16022 | 0.009155 | 1.2268 | 120.4422 | -2.3071 | 120.3735 | 120.4285 | 120.2362 | 120.4788 | 2.1469 | -120.3094 | -120.4971 | 2.2614 | 2.2705 | 2.1011 | 0.1236 | -0.045776 | -0.045776 | 0.045777 | -0.022888 | 122.6898 | 122.7402 | 122.4976 | 122.7859 | 122.5433 | 0.11444 | 0.013733 | 122.7356 | 122.6807 | 0.20142 | 122.7493 | 2.3483 | 122.7036 | -120.5109 | -122.7036 | 2.1606 | 122.6349 | 2.1194 | 3.4882
966.7031 | 122.731 | -2.3666 | 120.3598 | -0.13748 | -0.0026275 | 0.020273 | 0.018335 | -0.00054262 | 0.002337 | 0.0024674 | -0.086792 | 0.095135 | 0.13237 | -0.0058084 | 0.069152 | 0.095359 | -0.0015893 | -0.13733 | 0.091553 | -0.11444 | -0.11444 | -0.032043 | -0.17853 | 0.004578 | 1.2039 | 120.3644 | -2.4033 | 120.2316 | 120.2911 | 120.108 | 120.3506 | 2.2522 | -120.2682 | -120.4742 | 2.3346 | 2.3712 | 2.1881 | 0.11902 | -0.064087 | -0.036621 | 0.004578 | -0.12817 | 122.6578 | 122.7173 | 122.4747 | 122.7539 | 122.5113 | 0.082398 | 0 | 122.6944 | 122.6349 | 0.20599 | 122.7676 | 2.4582 | 122.731 | -120.4742 | -122.7631 | 2.2522 | 122.5983 | 2.2293 | 3.5706
968.375 | 122.7814 | -2.3529 | 120.3415 | -0.20615 | -0.0013457 | 0.020059 | 0.015558 | 0.00031198 | 0.00084159 | 0.00033105 | 0.001709 | 0.084667 | 0.1343 | -0.0036722 | 0.069793 | 0.095787 | -9.3938e-05 | -0.11444 | 0.064087 | -0.082397 | -0.022888 | 0.11444 | -0.059509 | 0.086975 | 1.2726 | 120.3232 | -2.3758 | 120.2774 | 120.3461 | 120.1767 | 120.3781 | 2.2705 | -120.2774 | -120.3644 | 2.4673 | 2.4399 | 2.2934 | 0.16937 | 0.022888 | -0.022888 | -0.018311 | -0.064087 | 122.699 | 122.731 | 122.5296 | 122.7539 | 122.5525 | 0.19684 | 0.059509 | 122.7219 | 122.6532 | 0.14648 | 122.699 | 2.417 | 122.6761 | -120.4239 | -122.7173 | 2.33 | 122.6303 | 2.2385 | 3.6255
970.1094 | 122.818 | -2.4445 | 120.2042 | -0.13748 | -0.0019867 | 0.01835 | 0.016199 | 0.00052558 | 0.0027644 | -0.0011642 | -0.06543 | 0.084881 | 0.13344 | -0.0051676 | 0.068938 | 0.097495 | -0.00052114 | -0.07782 | 0.059509 | -0.086975 | -0.027466 | 0.082397 | -0.059509 | 0.086975 | 1.3458 | 120.2042 | -2.4902 | 120.1996 | 120.2545 | 120.0668 | 120.2911 | 2.3575 | -120.1447 | -120.2316 | 2.5269 | 2.5314 | 2.3849 | 0.17395 | 0.027466 | -0.045776 | 0 | -0.004578 | 122.699 | 122.7356 | 122.5113 | 122.7814 | 122.5571 | 0.16937 | 0.059509 | 122.7448 | 122.6898 | 0.14648 | 122.6944 | 2.504 | 122.6486 | -120.2911 | -122.6944 | 2.417 | 122.644 | 2.3666 | 3.7903
971.8438 | 122.818 | -2.4261 | 120.2637 | -0.22141 | -0.0028411 | 0.015146 | 0.014063 | -0.00096982 | 0.0021234 | -0.0030868 | -0.0043944 | 0.097271 | 0.13131 | -0.00068143 | 0.068938 | 0.095573 | 0.0018287 | -0.13275 | 0.068665 | -0.09613 | -0.059509 | 0.041199 | -0.068665 | 0.086975 | 1.2726 | 120.2774 | -2.4582 | 120.1813 | 120.3049 | 120.1263 | 120.3278 | 2.33 | -120.195 | -120.3232 | 2.4673 | 2.5131 | 2.3575 | 0.1831 | 0.027465 | -0.032044 | 0.013733 | -0.082398 | 122.731 | 122.7539 | 122.5525 | 122.7859 | 122.5845 | 0.13733 | 0.036621 | 122.7631 | 122.6395 | 0.16479 | 122.7356 | 2.4948 | 122.7036 | -120.3598 | -122.7219 | 2.3666 | 122.6074 | 2.2934 | 3.6987
973.5156 | 122.7493 | -2.5314 | 120.1904 | -0.14511 | -0.0013457 | 0.017709 | 0.016626 | 0.0041572 | 0.00084159 | 0.0035354 | -0.10815 | 0.091717 | 0.13237 | 0.0020956 | 0.068725 | 0.098564 | -0.0022301 | -0.10071 | 0.091553 | -0.10986 | -0.07782 | 0.013733 | -0.10071 | 0.032043 | 1.3 | 120.2179 | -2.5497 | 120.076 | 120.1401 | 119.9661 | 120.1904 | 2.4216 | -120.0989 | -120.2683 | 2.5452 | 2.5635 | 2.4307 | 0.14191 | 0.009155 | -0.018311 | 0.027466 | -0.11444 | 122.6715 | 122.7219 | 122.4976 | 122.7402 | 122.5159 | 0.1236 | 0.032043 | 122.6898 | 122.6257 | 0.20142 | 122.7676 | 2.623 | 122.7493 | -120.3003 | -122.7402 | 2.4536 | 122.6074 | 2.4307 | 3.8315
975.25 | 122.818 | -2.4857 | 120.1447 | -0.20615 | -0.0013457 | 0.017496 | 0.015344 | -0.0016106 | 0.0021234 | 0.00097205 | 0.010864 | 0.10667 | 0.13451 | -0.0040994 | 0.068511 | 0.09835 | 0.00033326 | -0.086975 | 0.045776 | -0.07782 | 0 | 0.13733 | -0.009155 | 0.10986 | 1.3596 | 120.2087 | -2.5223 | 120.1172 | 120.2316 | 120.0531 | 120.2408 | 2.4078 | -120.0989 | -120.1447 | 2.623 | 2.5955 | 2.4765 | 0.18768 | 0.068665 | -0.036621 | 0.064087 | -0.027466 | 122.7173 | 122.7264 | 122.5388 | 122.7631 | 122.5754 | 0.21515 | 0.07782 | 122.7539 | 122.6395 | 0.1236 | 122.731 | 2.5314 | 122.6944 | -120.2225 | -122.6669 | 2.4857 | 122.6028 | 2.3987 | 3.8452
976.9844 | 122.7676 | -2.4902 | 120.2271 | -0.16037 | -0.0047637 | 0.020059 | 0.015558 | -0.0035334 | 0.0010554 | 0.00097205 | -0.03186 | 0.092571 | 0.13366 | 0.0012412 | 0.068938 | 0.095573 | -0.0039391 | -0.07782 | 0.045776 | -0.091553 | -0.032043 | 0.086975 | -0.032043 | 0.09613 | 1.3824 | 120.2545 | -2.504 | 120.1126 | 120.2271 | 120.0485 | 120.2408 | 2.3987 | -120.1813 | -120.2591 | 2.5772 | 2.5864 | 2.4582 | 0.18768 | 0.05951 | -0.013733 | 0.027466 | -0.11444 | 122.7173 | 122.731 | 122.5388 | 122.7448 | 122.5525 | 0.17853 | 0.05951 | 122.731 | 122.6166 | 0.13733 | 122.7585 | 2.536 | 122.7448 | -120.3186 | -122.731 | 2.4582 | 122.6028 | 2.4124 | 3.8727
978.6562 | 122.7173 | -2.4902 | 120.2591 | -0.099335 | -0.0026275 | 0.020059 | 0.016626 | -0.0033196 | 0.0021234 | 0.00097205 | -0.095947 | 0.10112 | 0.13237 | -0.0013224 | 0.069365 | 0.095787 | -0.0030847 | -0.15106 | 0.086975 | -0.10071 | -0.13733 | -0.050354 | -0.13733 | -0.009155 | 1.268 | 120.2591 | -2.5131 | 120.1035 | 120.195 | 119.9982 | 120.2225 | 2.3895 | -120.1721 | -120.3964 | 2.4399 | 2.4811 | 2.3529 | 0.091553 | -0.036621 | -0.022889 | 0 | -0.15564 | 122.6852 | 122.7127 | 122.4884 | 122.7356 | 122.5113 | 0.050354 | -0.036621 | 122.7081 | 122.6166 | 0.18768 | 122.7722 | 2.5772 | 122.7493 | -120.3598 | -122.7722 | 2.3529 | 122.5937 | 2.3392 | 3.7582
980.3906 | 122.7951 | -2.4857 | 120.1767 | -0.19089 | -0.0028411 | 0.017709 | 0.014063 | -0.001397 | -0.00044001 | 0.0039626 | -0.0013428 | 0.089153 | 0.13131 | -0.0030312 | 0.069365 | 0.095359 | -0.0015893 | -0.1236 | 0.059509 | -0.10986 | -0.068665 | 0.041199 | -0.086975 | 0.073242 | 1.3229 | 120.2133 | -2.5406 | 120.1263 | 120.2087 | 120.0577 | 120.2408 | 2.3758 | -120.1172 | -120.2454 | 2.5269 | 2.5589 | 2.3987 | 0.18311 | 0.022888 | -0.054931 | 0.036621 | -0.050354 | 122.6944 | 122.7264 | 122.5433 | 122.7814 | 122.5983 | 0.15106 | 0.041198 | 122.7493 | 122.6669 | 0.16937 | 122.7539 | 2.5452 | 122.699 | -120.2866 | -122.7173 | 2.417 | 122.612 | 2.3621 | 3.8086
982.125 | 122.8088 | -2.449 | 120.1996 | -0.17563 | -0.00049134 | 0.0207 | 0.014276 | -0.0016106 | 0.00020079 | 0.0022536 | 0.013916 | 0.087017 | 0.13259 | -0.00046783 | 0.068725 | 0.09835 | 0.0028967 | -0.064087 | 0.041199 | -0.068665 | -0.022888 | 0.1236 | -0.022888 | 0.13733 | 1.4282 | 120.2179 | -2.4948 | 120.163 | 120.2728 | 120.1218 | 120.282 | 2.3804 | -120.1584 | -120.2225 | 2.5726 | 2.5864 | 2.4261 | 0.20599 | 0.045777 | -0.045776 | 0.018311 | -0.036621 | 122.7219 | 122.731 | 122.5708 | 122.7768 | 122.6166 | 0.19226 | 0.045777 | 122.7676 | 122.6578 | 0.10986 | 122.7127 | 2.4902 | 122.6669 | -120.2682 | -122.6944 | 2.4261 | 122.612 | 2.3849 | 3.8773
983.8594 | 122.8088 | -2.4628 | 120.1767 | -0.15274 | -0.0034821 | 0.019846 | 0.018335 | -0.001397 | -1.2808e-05 | -9.6154e-05 | -0.1051 | 0.10218 | 0.13237 | -0.0011086 | 0.068084 | 0.097709 | -0.0013757 | -0.086975 | 0.073242 | -0.091553 | -0.059509 | 0.064087 | -0.073242 | 0.068665 | 1.3687 | 120.2087 | -2.4948 | 120.163 | 120.2362 | 120.0439 | 120.2911 | 2.3712 | -120.1035 | -120.2362 | 2.5269 | 2.5314 | 2.3895 | 0.16022 | 0.018311 | -0.032043 | 0.032043 | -0.013733 | 122.699 | 122.7539 | 122.5067 | 122.7859 | 122.5388 | 0.15564 | 0.032044 | 122.731 | 122.6578 | 0.16479 | 122.7036 | 2.536 | 122.6715 | -120.2683 | -122.6715 | 2.4033 | 122.6257 | 2.3758 | 3.8315
985.5938 | 122.6807 | -2.4673 | 120.2545 | -0.17563 | -0.0015595 | 0.018564 | 0.018549 | 0.0039436 | -0.00044001 | 0.0013992 | -0.13562 | 0.08894 | 0.1343 | 0.003591 | 0.069152 | 0.097068 | -0.00094854 | -0.15564 | 0.091553 | -0.11902 | -0.14648 | -0.068665 | -0.20142 | -0.032043 | 1.2497 | 120.3232 | -2.5131 | 120.1035 | 120.1401 | 119.9615 | 120.2133 | 2.3483 | -120.163 | -120.401 | 2.3987 | 2.4353 | 2.2659 | 0.086976 | -0.082397 | -0.045777 | 0.068664 | -0.15106 | 122.6074 | 122.6807 | 122.4289 | 122.7264 | 122.4747 | 0.050354 | -0.027465 | 122.6532 | 122.6166 | 0.21057 | 122.8363 | 2.5589 | 122.7905 | -120.3735 | -122.7676 | 2.3209 | 122.5708 | 2.3117 | 3.717
987.3438 | 122.7036 | -2.4307 | 120.314 | -0.15274 | -0.0011321 | 0.019632 | 0.017053 | 0.004798 | 0.004687 | 0.0016128 | -0.13257 | 0.089153 | 0.13216 | 0.0031638 | 0.070006 | 0.097068 | 0.0014015 | -0.10071 | 0.09613 | -0.10071 | -0.09613 | 0.013733 | -0.13275 | 0 | 1.2909 | 120.3415 | -2.4536 | 120.1492 | 120.2225 | 120.0439 | 120.2728 | 2.33 | -120.2179 | -120.4102 | 2.4445 | 2.4307 | 2.298 | 0.10071 | -0.032043 | -0.022888 | 0.027466 | -0.16479 | 122.6532 | 122.7036 | 122.4747 | 122.7264 | 122.4976 | 0.11444 | 0.004578 | 122.6761 | 122.6028 | 0.19684 | 122.7951 | 2.5269 | 122.7722 | -120.4147 | -122.7676 | 2.3346 | 122.58 | 2.33 | 3.7216
989.0156 | 122.8043 | -2.504 | 120.1492 | -0.21378 | -0.0011321 | 0.020059 | 0.017694 | -0.001397 | 0.0027644 | 0.0024674 | -0.041016 | 0.088513 | 0.13259 | -0.0079446 | 0.068084 | 0.098777 | 0.00076046 | -0.07782 | 0.068665 | -0.086975 | -0.013733 | 0.10529 | -0.054932 | 0.07782 | 1.3367 | 120.1767 | -2.5314 | 120.1401 | 120.2179 | 120.0394 | 120.2545 | 2.417 | -120.0806 | -120.163 | 2.6093 | 2.5818 | 2.449 | 0.16479 | 0.032043 | -0.027466 | 0.027466 | -0.009155 | 122.7219 | 122.7585 | 122.5433 | 122.786 | 122.5708 | 0.19226 | 0.073242 | 122.7493 | 122.6715 | 0.15564 | 122.7081 | 2.5726 | 122.6807 | -120.2362 | -122.6807 | 2.4902 | 122.644 | 2.4261 | 3.8406
990.75 | 122.6852 | -2.6276 | 120.1263 | -0.084076 | -0.0039093 | 0.018564 | 0.016199 | -0.0043878 | 0.00041439 | -0.0018052 | -0.041016 | 0.090862 | 0.13366 | -0.0092264 | 0.06317 | 0.094291 | -0.0032983 | -0.14648 | 0.082397 | -0.10986 | -0.14191 | -0.022888 | -0.14648 | 0.009155 | 1.2817 | 120.163 | -2.6505 | 119.9432 | 120.0348 | 119.8563 | 120.0577 | 2.5177 | -120.0439 | -120.2683 | 2.6047 | 2.6367 | 2.4811 | 0.11902 | -0.036621 | -0.022889 | 0.036621 | -0.18311 | 122.6624 | 122.6852 | 122.4838 | 122.7081 | 122.5067 | 0.086975 | -0.032044 | 122.6852 | 122.5937 | 0.19226 | 122.8134 | 2.71 | 122.7905 | -120.2362 | -122.7768 | 2.4857 | 122.5708 | 2.4811 | 3.9093
992.4375 | 122.6715 | -2.4765 | 120.282 | -0.18326 | -0.0030547 | 0.016855 | 0.017481 | 0.00095278 | 0.00020079 | -0.00052335 | -0.044067 | 0.092785 | 0.13259 | 0.00060037 | 0.060607 | 0.095573 | -0.00052114 | -0.14648 | 0.082397 | -0.10529 | -0.13275 | 0 | -0.11902 | 0.009155 | 1.2497 | 120.2866 | -2.4948 | 120.0806 | 120.1721 | 120.0211 | 120.2087 | 2.3712 | -120.1996 | -120.4147 | 2.4765 | 2.4857 | 2.3575 | 0.11444 | -0.013733 | -0.018311 | 0.004578 | -0.20142 | 122.6486 | 122.6852 | 122.4976 | 122.7036 | 122.5159 | 0.10529 | -0.027465 | 122.6669 | 122.5754 | 0.18768 | 122.7814 | 2.5589 | 122.7631 | -120.3873 | -122.7768 | 2.3438 | 122.5571 | 2.33 | 3.7262
994.1719 | 122.7722 | -2.4261 | 120.2408 | -0.16037 | -0.0026275 | 0.018777 | 0.015772 | -0.0039606 | 0.0021234 | 0.00011745 | -0.041016 | 0.09663 | 0.13152 | -0.0049538 | 0.06253 | 0.094932 | 0.00076046 | -0.082397 | 0.041199 | -0.082397 | -0.018311 | 0.10986 | -0.054932 | 0.086975 | 1.3046 | 120.2179 | -2.4719 | 120.1447 | 120.2362 | 120.0577 | 120.2911 | 2.3438 | -120.1996 | -120.2591 | 2.536 | 2.5131 | 2.3712 | 0.16937 | 0.027465 | -0.045777 | -0.022888 | -0.096131 | 122.6624 | 122.7173 | 122.4838 | 122.7631 | 122.5296 | 0.19226 | 0.064086 | 122.7081 | 122.6166 | 0.1236 | 122.6898 | 2.4673 | 122.644 | -120.3232 | -122.7127 | 2.4078 | 122.5708 | 2.3438 | 3.7308
995.9062 | 122.731 | -2.4811 | 120.2225 | -0.099335 | -0.0017731 | 0.019418 | 0.018122 | -0.00032902 | -1.2808e-05 | 0.00204 | -0.11121 | 0.096417 | 0.13088 | 0.0067954 | 0.063384 | 0.096855 | 0.00054686 | -0.11444 | 0.086975 | -0.1236 | -0.082397 | 0.022888 | -0.10529 | 0.022888 | 1.3367 | 120.2591 | -2.5131 | 120.108 | 120.1813 | 120.0165 | 120.2316 | 2.3575 | -120.1355 | -120.3049 | 2.504 | 2.504 | 2.3758 | 0.14648 | 0.01831 | -0.032044 | 0.036621 | -0.11444 | 122.6624 | 122.7127 | 122.4976 | 122.7448 | 122.5296 | 0.14648 | 0.041199 | 122.6944 | 122.6212 | 0.21057 | 122.7722 | 2.5681 | 122.7402 | -120.3461 | -122.7356 | 2.3987 | 122.5891 | 2.3666 | 3.8177
997.6406 | 122.6761 | -2.4399 | 120.2728 | -0.13748 | -0.0011321 | 0.019632 | 0.017908 | 0.0020208 | 0.0019098 | 0.0031082 | -0.12646 | 0.094921 | 0.13387 | -0.003245 | 0.061034 | 0.098136 | -0.00030754 | -0.10529 | 0.086975 | -0.10986 | -0.11444 | 0 | -0.13733 | -0.009155 | 1.2268 | 120.3049 | -2.4765 | 120.1263 | 120.1813 | 119.9936 | 120.2316 | 2.33 | -120.1859 | -120.3873 | 2.4399 | 2.4307 | 2.3026 | 0.10071 | -0.027466 | -0.036621 | 0.032044 | -0.14648 | 122.6212 | 122.6715 | 122.4335 | 122.7081 | 122.4701 | 0.10986 | -0.004578 | 122.6578 | 122.6028 | 0.19684 | 122.7814 | 2.5269 | 122.7448 | -120.3827 | -122.7493 | 2.3254 | 122.5662 | 2.3346 | 3.6667
999.375 | 122.6852 | -2.4628 | 120.2682 | -0.17563 | -0.00091854 | 0.0207 | 0.018122 | -0.0018244 | 0.0016962 | 0.0013992 | -0.092895 | 0.098126 | 0.13408 | -0.001536 | 0.063811 | 0.098991 | 0.0020423 | -0.11444 | 0.082397 | -0.11444 | -0.10071 | 0 | -0.14191 | 0.009155 | 1.2726 | 120.2866 | -2.4673 | 120.1035 | 120.1584 | 119.9753 | 120.2225 | 2.3483 | -120.1859 | -120.369 | 2.4628 | 2.4719 | 2.3209 | 0.1236 | -0.027466 | -0.004577 | 0.01831 | -0.16479 | 122.6212 | 122.6852 | 122.438 | 122.6898 | 122.4426 | 0.11444 | 0.013733 | 122.6257 | 122.5708 | 0.19684 | 122.7539 | 2.5452 | 122.7493 | -120.3827 | -122.7356 | 2.3621 | 122.5662 | 2.3483 | 3.7354
1001.0469 | 122.6578 | -2.4353 | 120.3186 | -0.168 | -0.0022003 | 0.020273 | 0.017267 | 0.0020208 | 0.0014826 | 0.0031082 | -0.11426 | 0.10026 | 0.13408 | 0.00081397 | 0.068511 | 0.097282 | 0.00033326 | -0.13733 | 0.091553 | -0.11902 | -0.14191 | -0.032043 | -0.16937 | -0.032043 | 1.2177 | 120.3415 | -2.449 | 120.1218 | 120.1721 | 119.9982 | 120.2591 | 2.3163 | -120.2271 | -120.4605 | 2.4033 | 2.4033 | 2.2659 | 0.086976 | -0.050354 | -0.013733 | 0.022888 | -0.19684 | 122.6074 | 122.6944 | 122.4335 | 122.7081 | 122.4472 | 0.086976 | -0.022888 | 122.6212 | 122.5708 | 0.21057 | 122.7905 | 2.5269 | 122.7768 | -120.4376 | -122.7676 | 2.2934 | 122.5571 | 2.298 | 3.653
1002.7969 | 122.7722 | -2.4628 | 120.2087 | -0.20615 | -0.0024139 | 0.016641 | 0.013849 | -0.0024652 | 0.00041439 | 0.00097205 | 0.02002 | 0.096844 | 0.13195 | -0.0040994 | 0.067016 | 0.098136 | 0.0016151 | -0.12817 | 0.073242 | -0.09613 | -0.086975 | 0.045776 | -0.09613 | 0.059509 | 1.2268 | 120.2179 | -2.4811 | 120.1309 | 120.2271 | 120.0668 | 120.2545 | 2.3666 | -120.1355 | -120.2957 | 2.5085 | 2.5223 | 2.3666 | 0.15564 | 0 | -0.01831 | 0.009156 | -0.07782 | 122.6898 | 122.7173 | 122.5296 | 122.7356 | 122.5479 | 0.14191 | 0.009155 | 122.7081 | 122.612 | 0.16937 | 122.699 | 2.536 | 122.6807 | -120.3049 | -122.6898 | 2.3758 | 122.5937 | 2.3346 | 3.6896
1004.4688 | 122.7493 | -2.5085 | 120.2087 | -0.22903 | -0.00091854 | 0.019418 | 0.014917 | -0.003747 | 0.0031916 | -0.00030975 | -0.01355 | 0.095135 | 0.13216 | -0.0096536 | 0.064239 | 0.097282 | 0.00033326 | -0.09613 | 0.054932 | -0.082397 | -0.073242 | 0.041199 | -0.091553 | 0.068665 | 1.268 | 120.195 | -2.536 | 120.0806 | 120.1767 | 120.0165 | 120.2225 | 2.4261 | -120.1538 | -120.282 | 2.5497 | 2.5772 | 2.417 | 0.15106 | -0.009156 | -0.027466 | -0.013733 | -0.12817 | 122.6852 | 122.731 | 122.525 | 122.7585 | 122.5525 | 0.1236 | 0.009155 | 122.7127 | 122.6166 | 0.13733 | 122.731 | 2.5635 | 122.7036 | -120.2911 | -122.7448 | 2.4353 | 122.5891 | 2.4124 | 3.7765
1006.2031 | 122.7127 | -2.4994 | 120.2042 | -0.084076 | -0.00049134 | 0.018137 | 0.017481 | -0.0018244 | 0.0021234 | 0.00011745 | -0.10815 | 0.098766 | 0.13237 | 0.0016684 | 0.06787 | 0.097923 | -0.0032983 | -0.091553 | 0.086975 | -0.10529 | -0.07782 | 0.032043 | -0.10071 | 0.022888 | 1.3596 | 120.2362 | -2.536 | 120.0989 | 120.1538 | 119.9844 | 120.2042 | 2.3941 | -120.1172 | -120.282 | 2.5314 | 2.5223 | 2.3987 | 0.12817 | 0.004578 | -0.036621 | 0.032043 | -0.10529 | 122.6532 | 122.7036 | 122.4838 | 122.7402 | 122.5204 | 0.13733 | 0.027466 | 122.6898 | 122.6349 | 0.19226 | 122.7722 | 2.5864 | 122.7356 | -120.3094 | -122.7402 | 2.4216 | 122.5983 | 2.4078 | 3.8589
1007.9531 | 122.818 | -2.5772 | 120.0714 | -0.11459 | -0.0045501 | 0.018991 | 0.014917 | -0.003747 | 0.0025506 | 0.00204 | 0.016968 | 0.099835 | 0.13216 | -0.0028176 | 0.069365 | 0.097495 | -9.3938e-05 | -0.082397 | 0.050354 | -0.091553 | -0.009155 | 0.15106 | -0.018311 | 0.13275 | 1.4099 | 120.1035 | -2.6093 | 120.0577 | 120.1675 | 119.989 | 120.1721 | 2.4857 | -120.0211 | -120.0806 | 2.7283 | 2.71 | 2.5589 | 0.2243 | 0.073242 | -0.032044 | 0.032044 | -0.013733 | 122.7448 | 122.7493 | 122.5662 | 122.7814 | 122.5983 | 0.24261 | 0.082398 | 122.7768 | 122.6669 | 0.14191 | 122.7127 | 2.6276 | 122.6807 | -120.163 | -122.6807 | 2.5681 | 122.6349 | 2.4948 | 3.9871
1009.6875 | 122.7722 | -2.5085 | 120.1263 | -0.19089 | -0.00049134 | 0.019846 | 0.015985 | -0.00011542 | 0.0021234 | 0.00033105 | -0.053223 | 0.098553 | 0.13259 | 0.00060037 | 0.068511 | 0.097068 | -0.00094854 | -0.068665 | 0.050354 | -0.073242 | -0.018311 | 0.11444 | -0.064087 | 0.10071 | 1.3229 | 120.1675 | -2.5269 | 120.0989 | 120.163 | 119.9936 | 120.2087 | 2.4353 | -120.076 | -120.1447 | 2.623 | 2.6093 | 2.4445 | 0.17395 | 0.009155 | -0.01831 | 0.041199 | -0.027466 | 122.6715 | 122.7173 | 122.5021 | 122.7356 | 122.5204 | 0.18768 | 0.054931 | 122.6898 | 122.6257 | 0.1236 | 122.6944 | 2.5589 | 122.6761 | -120.1996 | -122.6532 | 2.4902 | 122.6074 | 2.4399 | 3.8315
1011.4219 | 122.7264 | -2.5955 | 120.1218 | -0.12985 | 0.00079046 | 0.018777 | 0.018549 | -0.0016106 | 0.002337 | 0.0024674 | -0.092895 | 0.098553 | 0.13088 | 0.0014548 | 0.059752 | 0.098777 | -0.0030847 | -0.1236 | 0.082397 | -0.11444 | -0.10986 | -0.018311 | -0.10529 | 0.013733 | 1.2955 | 120.1309 | -2.6413 | 119.9844 | 120.0714 | 119.8746 | 120.0989 | 2.4811 | -120.0394 | -120.2316 | 2.5772 | 2.6093 | 2.4902 | 0.12817 | 0.009155 | -0.045776 | 0.009155 | -0.13733 | 122.6669 | 122.6944 | 122.4701 | 122.7402 | 122.5159 | 0.09613 | 0.004578 | 122.7127 | 122.6257 | 0.19684 | 122.7722 | 2.6779 | 122.7264 | -120.2362 | -122.7631 | 2.4857 | 122.58 | 2.4719 | 3.891
1013.1094 | 122.6761 | -2.6321 | 120.1126 | -0.14511 | -0.00049134 | 0.018777 | 0.018122 | 0.00073918 | 0.001269 | -0.0015916 | -0.11426 | 0.10112 | 0.13109 | 0.0020956 | 0.061248 | 0.098136 | 0.00033326 | -0.10071 | 0.07782 | -0.082397 | -0.091553 | 0.022888 | -0.14191 | 0.004578 | 1.2726 | 120.1035 | -2.6688 | 119.9387 | 119.9844 | 119.8151 | 120.0485 | 2.5497 | -120.0348 | -120.2042 | 2.655 | 2.6367 | 2.4902 | 0.086975 | -0.05951 | -0.036621 | -0.009155 | -0.17395 | 122.6166 | 122.6807 | 122.4472 | 122.7173 | 122.4838 | 0.10528 | -0.009156 | 122.6532 | 122.6074 | 0.16022 | 122.7722 | 2.71 | 122.7356 | -120.195 | -122.7814 | 2.5406 | 122.5708 | 2.5314 | 3.9047
1014.7969 | 122.7264 | -2.6184 | 120.0348 | -0.16037 | -0.0015595 | 0.018564 | 0.01919 | 0.00073918 | 0.00041439 | 0.0024674 | -0.098999 | 0.11222 | 0.1328 | 0.0048728 | 0.072356 | 0.098564 | 0.00076046 | -0.09613 | 0.07782 | -0.09613 | -0.07782 | 0.022888 | -0.10529 | 0.018311 | 1.3138 | 120.0806 | -2.6688 | 119.9524 | 120.0348 | 119.8334 | 120.0714 | 2.5223 | -119.957 | -120.1126 | 2.6413 | 2.6367 | 2.5131 | 0.11444 | -0.009156 | -0.050354 | 0.045776 | -0.082397 | 122.6532 | 122.6898 | 122.4518 | 122.7402 | 122.5021 | 0.11902 | 0.01831 | 122.7036 | 122.6212 | 0.17395 | 122.7493 | 2.6962 | 122.699 | -120.1309 | -122.7036 | 2.5406 | 122.5708 | 2.5223 | 3.9322
1016.5312 | 122.7631 | -2.6825 | 119.9844 | -0.13748 | -0.0026275 | 0.018564 | 0.014276 | -0.0011834 | 0.001269 | 0.0011856 | -0.0013428 | 0.1118 | 0.13366 | -0.0047402 | 0.074492 | 0.094932 | 0.00011966 | -0.13275 | 0.068665 | -0.07782 | -0.07782 | 0.050354 | -0.10071 | 0.045776 | 1.2222 | 120.0027 | -2.6962 | 119.902 | 120.0027 | 119.8196 | 120.0348 | 2.6047 | -119.9158 | -120.0623 | 2.7328 | 2.7283 | 2.5818 | 0.1236 | -0.022888 | -0.013733 | 0.018311 | -0.082397 | 122.6852 | 122.7173 | 122.5021 | 122.731 | 122.5159 | 0.12817 | 0 | 122.699 | 122.5983 | 0.14649 | 122.699 | 2.7512 | 122.6852 | -120.0623 | -122.6807 | 2.6047 | 122.5845 | 2.5497 | 3.9047
1018.2812 | 122.7814 | -2.7374 | 119.8975 | -0.17563 | -0.0019867 | 0.019846 | 0.015772 | -0.0011834 | -0.00022641 | -0.0011642 | -0.016602 | 0.1103 | 0.13494 | -0.0028176 | 0.071929 | 0.096 | -0.0011621 | -0.082397 | 0.041199 | -0.07782 | -0.022888 | 0.11444 | -0.018311 | 0.091553 | 1.3687 | 119.9203 | -2.7512 | 119.838 | 119.9661 | 119.7968 | 119.9799 | 2.6596 | -119.8563 | -119.9203 | 2.8519 | 2.829 | 2.7191 | 0.16937 | 0.059509 | -0.013733 | 0.022888 | -0.059509 | 122.7036 | 122.7173 | 122.5342 | 122.731 | 122.5479 | 0.19226 | 0.054932 | 122.7173 | 122.5891 | 0.11902 | 122.6715 | 2.7786 | 122.6578 | -119.9753 | -122.6486 | 2.7145 | 122.5754 | 2.655 | 4.1061
1020 | 122.7173 | -71.5485 | 50.9262 | -0.18326 | -0.00027774 | 0.020486 | 0.018549 | 0.0050116 | 0.002337 | -9.6154e-05 | -0.098999 | 0.10176 | 0.13665 | 0.0020956 | 0.08731 | 0.096855 | -0.0015893 | -0.14191 | 0.10986 | -0.10529 | -0.14648 | -0.054932 | -0.18768 | -0.032043 | -0.6958 | 50.9766 | -71.6812 | 50.8484 | 50.9171 | 50.7477 | 50.9537 | 71.4432 | -50.8163 | -51.0727 | 71.4935 | 71.5164 | 71.3608 | 0.073243 | -0.082397 | -0.13275 | 0.050354 | -0.077819 | 122.4655 | 122.5021 | 122.2961 | 122.6349 | 122.4289 | 0.050354 | -0.041198 | 122.5983 | 122.5296 | 0.21515 | 122.6578 | 71.6583 | 122.525 | -51.0315 | -122.6074 | 71.402 | 122.3969 | 71.4066 | 70.8527
1021.75 | 122.8088 | -122.3877 | 0.22888 | -0.19089 | -0.0022003 | 0.021127 | 0.017908 | -0.001397 | 0.0010554 | 0.00097205 | -0.08374 | 0.11564 | 0.13259 | -0.0021768 | 0.10376 | 0.097709 | -0.00052114 | -0.073242 | 0.064087 | -0.07782 | -0.013733 | 0.10071 | -0.064087 | 0.082397 | -1.8036 | 0.2655 | -122.4426 | 0.064087 | 0.18768 | 0.059509 | 0.17395 | 122.3099 | -0.16479 | -0.24261 | 122.4884 | 122.4701 | 122.3236 | 0.16022 | 0.013733 | -0.054932 | 0.036621 | -0.16479 | 122.5754 | 122.5616 | 122.4472 | 122.6166 | 122.5021 | 0.17853 | 0.064087 | 122.6303 | 122.5067 | 0.14191 | 122.7081 | 122.4518 | 122.6532 | -0.3067 | -122.6715 | 122.374 | 122.4518 | 122.3145 | 120.5841
1023.4375 | 122.8043 | -122.4014 | 0.21515 | -0.17563 | -0.0039093 | 0.018991 | 0.014704 | 0.0015936 | -0.0015082 | 0.0024674 | 0.013916 | 0.10688 | 0.13173 | -0.001536 | 0.09735 | 0.098136 | -0.0020165 | -0.1236 | 0.07782 | -0.086975 | -0.054932 | 0.059509 | -0.045776 | 0.086975 | -1.6846 | 0.2655 | -122.4335 | 0.041199 | 0.16479 | 0.073242 | 0.14648 | 122.3145 | -0.13733 | -0.27008 | 122.4609 | 122.4884 | 122.3557 | 0.17395 | 0.041199 | -0.032044 | 0.050354 | -0.17395 | 122.5662 | 122.5479 | 122.4747 | 122.58 | 122.5067 | 0.14648 | 0.032043 | 122.5983 | 122.4747 | 0.16479 | 122.699 | 122.4792 | 122.6669 | -0.30212 | -122.6486 | 122.3465 | 122.4426 | 122.2778 | 120.7169
1025.1719 | 122.6898 | -122.4152 | 0.24261 | -0.17563 | -0.0017731 | 0.019418 | 0.017053 | 0.0026618 | 0.0010554 | 0.0024674 | -0.098999 | 0.096203 | 0.13237 | -0.0049538 | 0.087737 | 0.098991 | -0.0047937 | -0.10986 | 0.09613 | -0.091553 | -0.10071 | -0.009155 | -0.13733 | -0.009155 | -1.6525 | 0.30212 | -122.4518 | -0.041199 | 0.054932 | -0.068665 | 0.050354 | 122.3236 | -0.14649 | -0.34332 | 122.406 | 122.406 | 122.2778 | 0.082398 | -0.045776 | -0.036621 | 0.059509 | -0.28381 | 122.4701 | 122.4655 | 122.3465 | 122.5021 | 122.3831 | 0.082398 | -0.009155 | 122.5067 | 122.4106 | 0.18768 | 122.7539 | 122.5113 | 122.7173 | -0.33417 | -122.6944 | 122.3145 | 122.374 | 122.3053 | 120.7626
1026.9219 | 122.7036 | -122.4197 | 0.24261 | -0.20615 | -0.0030547 | 0.018991 | 0.01684 | 0.00095278 | 0.004687 | 0.00033105 | -0.12036 | 0.09663 | 0.1328 | 0.0031638 | 0.088164 | 0.097709 | -0.0043665 | -0.14648 | 0.082397 | -0.09613 | -0.13733 | -0.059509 | -0.16937 | -0.027466 | -1.7075 | 0.28381 | -122.4609 | -0.050354 | 0.036621 | -0.068665 | 0.054932 | 122.3236 | -0.16022 | -0.37994 | 122.3602 | 122.3923 | 122.2504 | 0.068664 | -0.073243 | -0.041198 | 0.041198 | -0.29297 | 122.4564 | 122.4747 | 122.3511 | 122.5159 | 122.3923 | 0.036621 | -0.041199 | 122.4976 | 122.4106 | 0.17853 | 122.7447 | 122.5021 | 122.7036 | -0.33874 | -122.7036 | 122.2824 | 122.3694 | 122.2733 | 120.7123
1028.6562 | 122.6898 | -122.4472 | 0.25635 | -0.053558 | -0.0030547 | 0.017496 | 0.018122 | -0.00075622 | 0.00041439 | 0.00204 | -0.034912 | 0.092358 | 0.13451 | -0.0090128 | 0.085174 | 0.096214 | 0.00011966 | -0.15106 | 0.10529 | -0.11902 | -0.15106 | -0.045776 | -0.1236 | 0 | -1.6205 | 0.28839 | -122.4655 | -0.07782 | 0.073242 | -0.050354 | 0.050354 | 122.3282 | -0.15106 | -0.40741 | 122.4014 | 122.4472 | 122.3236 | 0.11902 | -0.004577 | -0.01831 | 0.032043 | -0.33417 | 122.5204 | 122.4976 | 122.3969 | 122.5159 | 122.4152 | 0.073243 | -0.032043 | 122.5388 | 122.3877 | 0.22431 | 122.7539 | 122.5525 | 122.7356 | -0.37537 | -122.7219 | 122.2961 | 122.3694 | 122.2961 | 120.8267
1030.3906 | 122.7722 | -122.3694 | 0.2243 | -0.22141 | -0.0024139 | 0.019418 | 0.01449 | -0.0011834 | 0.004046 | -0.0020188 | 0.023071 | 0.097057 | 0.13066 | -0.0075174 | 0.089873 | 0.097068 | 0.0033241 | -0.10986 | 0.07782 | -0.086975 | -0.082397 | 0.013733 | -0.091553 | 0.050354 | -1.6159 | 0.26093 | -122.438 | 0.032043 | 0.14648 | 0.045776 | 0.11902 | 122.2824 | -0.14648 | -0.3067 | 122.3831 | 122.4197 | 122.2778 | 0.13733 | -0.004578 | -0.068664 | 0.036621 | -0.19226 | 122.5159 | 122.4884 | 122.4152 | 122.5571 | 122.4838 | 0.10071 | 0.004578 | 122.5845 | 122.4701 | 0.16479 | 122.699 | 122.4472 | 122.6303 | -0.31128 | -122.6624 | 122.287 | 122.4014 | 122.2595 | 120.7535
1032.0781 | 122.6944 | -122.4106 | 0.23346 | -0.18326 | -0.00027774 | 0.018777 | 0.020685 | 0.00031198 | 0.0025506 | 0.00075845 | -0.11426 | 0.10496 | 0.13387 | 0.0033774 | 0.09201 | 0.097495 | 0.00033326 | -0.14191 | 0.10529 | -0.091553 | -0.15106 | -0.086975 | -0.19226 | -0.036621 | -1.6479 | 0.29755 | -122.4518 | -0.045776 | 0.032043 | -0.082397 | 0.045776 | 122.319 | -0.12817 | -0.38452 | 122.3236 | 122.374 | 122.2183 | 0.054932 | -0.10071 | -0.041199 | 0.064087 | -0.27924 | 122.4426 | 122.4564 | 122.3282 | 122.4976 | 122.3694 | 0.004578 | -0.059509 | 122.4838 | 122.406 | 0.19684 | 122.7493 | 122.5159 | 122.7081 | -0.32501 | -122.6852 | 122.2595 | 122.3648 | 122.2687 | 120.7626
1033.8281 | 122.818 | -122.3419 | 0.21057 | -0.25192 | -0.00091854 | 0.019632 | 0.014917 | -0.0011834 | 0.0019098 | 0.0018264 | -0.019653 | 0.095776 | 0.13109 | -0.0011086 | 0.085387 | 0.097282 | 0.0016151 | -0.059509 | 0.059509 | -0.059509 | -0.013733 | 0.09613 | -0.068665 | 0.073242 | -1.5335 | 0.24719 | -122.3969 | 0.068665 | 0.19226 | 0.059509 | 0.16479 | 122.2824 | -0.15106 | -0.2243 | 122.438 | 122.4152 | 122.2733 | 0.13275 | -0.009156 | -0.054932 | 0.036621 | -0.14191 | 122.5342 | 122.5067 | 122.4014 | 122.5616 | 122.4564 | 0.15564 | 0.045776 | 122.5891 | 122.4655 | 0.11902 | 122.644 | 122.4014 | 122.5891 | -0.27008 | -122.6074 | 122.3282 | 122.4106 | 122.2824 | 120.8084
1035.5781 | 122.7356 | -122.3969 | 0.22888 | -0.168 | -0.0045501 | 0.019846 | 0.014917 | -0.001397 | -0.00044001 | 0.002681 | -0.01355 | 0.095562 | 0.13237 | -0.0070902 | 0.086028 | 0.095359 | 0.00033326 | -0.07782 | 0.045776 | -0.073242 | -0.027466 | 0.082397 | -0.027466 | 0.091553 | -1.5106 | 0.27008 | -122.4426 | 0 | 0.12817 | 0.027466 | 0.09613 | 122.3236 | -0.18311 | -0.25635 | 122.4792 | 122.4884 | 122.3694 | 0.16479 | 0.045776 | -0.045776 | 0.041199 | -0.22888 | 122.525 | 122.493 | 122.4243 | 122.5388 | 122.4701 | 0.15564 | 0.045776 | 122.5708 | 122.4426 | 0.11902 | 122.7127 | 122.4426 | 122.6669 | -0.30212 | -122.6715 | 122.3694 | 122.3969 | 122.319 | 120.8862
1037.3281 | 122.7997 | -122.374 | 0.21515 | -0.168 | -0.0036957 | 0.01835 | 0.015985 | 9.818e-05 | 0.00062799 | -0.00052335 | 0.013916 | 0.092785 | 0.13237 | -0.0038858 | 0.084533 | 0.095573 | -0.0050073 | -0.10986 | 0.068665 | -0.091553 | -0.041199 | 0.059509 | -0.045776 | 0.10071 | -1.5335 | 0.24261 | -122.4289 | 0.054932 | 0.19226 | 0.082397 | 0.15564 | 122.2824 | -0.14648 | -0.25635 | 122.4335 | 122.4747 | 122.3282 | 0.19226 | 0.045777 | -0.054932 | 0.027466 | -0.16022 | 122.5662 | 122.5296 | 122.4564 | 122.5845 | 122.5113 | 0.15106 | 0.050354 | 122.6212 | 122.4838 | 0.16022 | 122.6715 | 122.4426 | 122.6166 | -0.3067 | -122.644 | 122.3328 | 122.4289 | 122.2641 | 120.8405
1039.0938 | 122.7493 | -122.4014 | 0.22888 | -0.17563 | -0.0030547 | 0.019846 | 0.018335 | -0.0028924 | 0.00020079 | 0.0033218 | -0.019653 | 0.095348 | 0.13131 | 0.002523 | 0.086242 | 0.096855 | -0.00094854 | -0.073242 | 0.059509 | -0.073242 | -0.013733 | 0.086975 | -0.041199 | 0.091553 | -1.4786 | 0.25635 | -122.4106 | 0.018311 | 0.16022 | 0.054932 | 0.10986 | 122.3282 | -0.16937 | -0.24261 | 122.4884 | 122.493 | 122.3602 | 0.16479 | 0.032043 | -0.009155 | 0.027466 | -0.21057 | 122.5616 | 122.5113 | 122.4564 | 122.5204 | 122.4655 | 0.16022 | 0.059509 | 122.5708 | 122.4289 | 0.13275 | 122.6669 | 122.4609 | 122.6578 | -0.30212 | -122.6395 | 122.3877 | 122.4197 | 122.3282 | 120.9229
1040.8438 | 122.6944 | -122.3877 | 0.24261 | -0.19089 | -0.0017731 | 0.019418 | 0.019831 | 0.00031198 | 0.001269 | -0.00073695 | -0.11426 | 0.09428 | 0.13323 | -4.063e-05 | 0.083678 | 0.098777 | 0.00076046 | -0.13733 | 0.10529 | -0.12817 | -0.12817 | -0.064087 | -0.1831 | -0.013733 | -1.6891 | 0.28839 | -122.4426 | -0.045776 | 0.050354 | -0.068665 | 0.073242 | 122.2595 | -0.13733 | -0.37079 | 122.3236 | 122.374 | 122.2046 | 0.11444 | -0.054931 | -0.054932 | 0.045776 | -0.28839 | 122.438 | 122.4609 | 122.319 | 122.5159 | 122.374 | 0.064087 | 0 | 122.493 | 122.3969 | 0.23346 | 122.731 | 122.493 | 122.6761 | -0.37079 | -122.6852 | 122.2595 | 122.3419 | 122.2504 | 120.6985
1042.5938 | 122.7951 | -122.3648 | 0.20599 | -0.15274 | -0.0034821 | 0.019205 | 0.012781 | -0.00075622 | 0.0010554 | 0.0039626 | 0.001709 | 0.090222 | 0.13472 | 0.0027366 | 0.08496 | 0.096855 | 0.00011966 | -0.073242 | 0.07782 | -0.073242 | 0.004578 | 0.09613 | -0.009155 | 0.11902 | -1.4832 | 0.25635 | -122.4243 | 0.064087 | 0.19684 | 0.091553 | 0.15106 | 122.2916 | -0.12817 | -0.20142 | 122.4609 | 122.4838 | 122.3557 | 0.19226 | 0.064087 | -0.059509 | 0.050354 | -0.14191 | 122.5616 | 122.5159 | 122.4564 | 122.5754 | 122.5159 | 0.16937 | 0.07782 | 122.6212 | 122.4884 | 0.15106 | 122.6807 | 122.4426 | 122.6212 | -0.27924 | -122.6303 | 122.3694 | 122.4289 | 122.2916 | 120.8817
1044.3438 | 122.8043 | -122.3511 | 0.20599 | -0.18326 | -0.0034821 | 0.018137 | 0.014063 | -0.0011834 | 0.0014826 | 0.00204 | 0.0078126 | 0.090435 | 0.13066 | -0.00025423 | 0.085601 | 0.096855 | -0.0015893 | -0.064087 | 0.054932 | -0.064087 | -0.004578 | 0.1236 | 0.013733 | 0.13275 | -1.4923 | 0.23346 | -122.3877 | 0.059509 | 0.20599 | 0.10529 | 0.15564 | 122.287 | -0.15106 | -0.21057 | 122.4747 | 122.4838 | 122.3648 | 0.19684 | 0.07782 | -0.036621 | 0.027465 | -0.14649 | 122.5571 | 122.5067 | 122.4564 | 122.5433 | 122.493 | 0.18768 | 0.059509 | 122.5937 | 122.4472 | 0.11902 | 122.6212 | 122.406 | 122.5845 | -0.27008 | -122.5937 | 122.3465 | 122.4106 | 122.287 | 120.8588
1046.1094 | 122.7539 | -122.3648 | 0.19684 | -0.16037 | -0.0024139 | 0.020273 | 0.017481 | -0.0011834 | 0.0025506 | -0.0022324 | -0.050171 | 0.093853 | 0.13472 | -0.0038858 | 0.087951 | 0.094505 | -0.0011621 | -0.086975 | 0.07782 | -0.068665 | -0.036621 | 0.064087 | -0.064087 | 0.091553 | -1.6846 | 0.25177 | -122.4335 | 0.027466 | 0.13733 | 0.022888 | 0.11444 | 122.2961 | -0.11902 | -0.23346 | 122.4289 | 122.4564 | 122.3007 | 0.16022 | 0.004578 | -0.068665 | 0.054932 | -0.16937 | 122.5021 | 122.4792 | 122.3877 | 122.5479 | 122.4564 | 0.13275 | 0.032044 | 122.5708 | 122.4609 | 0.14649 | 122.6852 | 122.4426 | 122.6166 | -0.2655 | -122.6303 | 122.3282 | 122.3923 | 122.2778 | 120.6802
1047.8281 | 122.7402 | -122.3785 | 0.2243 | -0.19852 | -0.0019867 | 0.020914 | 0.01684 | -0.0018244 | -0.00022641 | 0.0018264 | -0.022705 | 0.096417 | 0.13024 | 0.0014548 | 0.089019 | 0.094291 | -0.00052114 | -0.1236 | 0.064087 | -0.082397 | -0.068665 | 0.013733 | -0.086975 | 0.059509 | -1.7166 | 0.24261 | -122.3969 | 0.013733 | 0.14191 | 0.013733 | 0.11444 | 122.2961 | -0.16022 | -0.29297 | 122.3923 | 122.438 | 122.2916 | 0.14191 | -0.004578 | -0.018311 | 0.018311 | -0.21057 | 122.5204 | 122.493 | 122.3923 | 122.5113 | 122.4106 | 0.09613 | 0.013732 | 122.5388 | 122.4106 | 0.14648 | 122.6395 | 122.4426 | 122.6212 | -0.3067 | -122.6212 | 122.3099 | 122.3923 | 122.2549 | 120.6619
1049.5625 | 122.7539 | -122.3785 | 0.22888 | -0.13748 | -6.4144e-05 | 0.019846 | 0.01919 | -0.0028924 | 0.00084159 | -0.00073695 | -0.13867 | 0.097057 | 0.13323 | 0.0053 | 0.087096 | 0.097282 | 0.00054686 | -0.13733 | 0.082397 | -0.10529 | -0.091553 | -0.032043 | -0.16937 | 0 | -1.7487 | 0.27008 | -122.4472 | 0.013733 | 0.10986 | -0.032043 | 0.10071 | 122.2733 | -0.14649 | -0.32044 | 122.3465 | 122.3785 | 122.2092 | 0.10529 | -0.064087 | -0.068665 | 0.041199 | -0.21515 | 122.4884 | 122.4792 | 122.3465 | 122.5479 | 122.4152 | 0.073243 | 0.013733 | 122.5571 | 122.4609 | 0.18768 | 122.7173 | 122.4609 | 122.6486 | -0.33417 | -122.6761 | 122.287 | 122.3923 | 122.2412 | 120.6299
1051.2969 | 122.6715 | -122.3785 | 0.24261 | -0.18326 | 0.00014946 | 0.019418 | 0.020471 | 0.0039436 | 0.0019098 | 0.003749 | -0.14478 | 0.096203 | 0.13387 | 0.0014548 | 0.084533 | 0.097068 | -0.0020165 | -0.14191 | 0.082397 | -0.11902 | -0.12817 | -0.07782 | -0.16479 | -0.027466 | -1.8311 | 0.28839 | -122.438 | -0.041199 | 0.041199 | -0.082397 | 0.050354 | 122.2595 | -0.16022 | -0.37079 | 122.3007 | 122.3511 | 122.2137 | 0.091553 | -0.045776 | -0.059509 | 0.045776 | -0.28381 | 122.4197 | 122.4289 | 122.2961 | 122.4884 | 122.3557 | 0.041199 | -0.009155 | 122.4792 | 122.3969 | 0.20142 | 122.7264 | 122.4609 | 122.6669 | -0.36163 | -122.6807 | 122.2504 | 122.3373 | 122.2366 | 120.5475
1052.9688 | 122.7722 | -122.3557 | 0.21057 | -0.15274 | -0.0026275 | 0.01835 | 0.013208 | -0.0016106 | 0.00062799 | -0.00052335 | -0.0074462 | 0.094067 | 0.13173 | -0.0062356 | 0.087523 | 0.096214 | -9.3938e-05 | -0.064087 | 0.064087 | -0.086975 | -0.009155 | 0.11902 | 0 | 0.11444 | -1.68 | 0.22888 | -122.406 | 0.054932 | 0.2243 | 0.10071 | 0.13733 | 122.2687 | -0.14648 | -0.21973 | 122.4747 | 122.4701 | 122.3557 | 0.20142 | 0.086975 | -0.050354 | 0.018311 | -0.15564 | 122.58 | 122.493 | 122.4564 | 122.5433 | 122.5067 | 0.20599 | 0.07782 | 122.6303 | 122.4609 | 0.15106 | 122.6349 | 122.4197 | 122.5845 | -0.29755 | -122.6166 | 122.3465 | 122.4106 | 122.2916 | 120.6757
1054.7031 | 122.6578 | -122.374 | 0.25635 | -0.12222 | -0.0022003 | 0.016214 | 0.016626 | 0.00031198 | -0.0023626 | -0.00030975 | -0.056274 | 0.095562 | 0.13259 | -0.0040994 | 0.087951 | 0.096641 | -0.0015893 | -0.16022 | 0.11444 | -0.091553 | -0.12817 | -0.050354 | -0.1236 | 0.013733 | -1.8951 | 0.28381 | -122.4472 | -0.068665 | 0.050354 | -0.064087 | 0.041199 | 122.2824 | -0.14191 | -0.38452 | 122.3236 | 122.3877 | 122.2504 | 0.10529 | -0.032043 | -0.073243 | 0.027465 | -0.32501 | 122.4243 | 122.4152 | 122.3099 | 122.4884 | 122.3831 | 0.041199 | -0.036621 | 122.4976 | 122.3785 | 0.20599 | 122.731 | 122.4884 | 122.6578 | -0.3479 | -122.7036 | 122.2458 | 122.3053 | 122.2137 | 120.4788
1056.375 | 122.6532 | -122.3969 | 0.24719 | -0.068817 | -0.0024139 | 0.016428 | 0.016413 | -0.00054262 | 0.00062799 | 0.00204 | -0.08374 | 0.091931 | 0.13344 | -0.003245 | 0.085814 | 0.097068 | -0.00073494 | -0.16479 | 0.10529 | -0.11444 | -0.12817 | -0.041199 | -0.11444 | -0.004578 | -1.8768 | 0.29297 | -122.4426 | -0.045776 | 0.07782 | -0.045776 | 0.054932 | 122.2824 | -0.14191 | -0.37537 | 122.3557 | 122.3923 | 122.2824 | 0.10986 | 0 | -0.045776 | 0.045777 | -0.29297 | 122.4747 | 122.4518 | 122.3511 | 122.4976 | 122.3969 | 0.073242 | -0.013733 | 122.5204 | 122.3969 | 0.21973 | 122.7356 | 122.5021 | 122.6898 | -0.36163 | -122.6898 | 122.2687 | 122.3511 | 122.2321 | 120.52
1058.125 | 122.7814 | -122.3328 | 0.19684 | -0.20615 | -0.0013457 | 0.018991 | 0.01684 | -0.00032902 | 0.0034052 | 0.00097205 | -0.11121 | 0.091717 | 0.13301 | -0.00089503 | 0.088378 | 0.097282 | -9.3938e-05 | -0.086975 | 0.068665 | -0.07782 | -0.027466 | 0.018311 | -0.068665 | 0.073242 | -1.8402 | 0.23804 | -122.3969 | 0.07782 | 0.19226 | 0.064087 | 0.1831 | 122.2549 | -0.12817 | -0.2243 | 122.3511 | 122.406 | 122.2641 | 0.15106 | 0.009155 | -0.064087 | 0.041199 | -0.11902 | 122.525 | 122.5159 | 122.3969 | 122.58 | 122.4609 | 0.096131 | 0.050354 | 122.5891 | 122.4747 | 0.14649 | 122.6349 | 122.4014 | 122.5708 | -0.27466 | -122.5937 | 122.3053 | 122.4106 | 122.2458 | 120.4926
1059.8281 | 122.731 | -122.3511 | 0.23804 | -0.12985 | -0.0011321 | 0.019632 | 0.019617 | 0.0022346 | 0.001269 | 0.0011856 | -0.11426 | 0.10389 | 0.13601 | -4.063e-05 | 0.1029 | 0.097068 | -0.0015893 | -0.13275 | 0.07782 | -0.10071 | -0.10986 | -0.050354 | -0.14648 | -0.004578 | -1.9958 | 0.27466 | -122.4335 | 0.027466 | 0.1236 | 0 | 0.11902 | 122.2504 | -0.16022 | -0.3479 | 122.3007 | 122.3465 | 122.2046 | 0.09613 | -0.045776 | -0.082398 | 0.036621 | -0.21057 | 122.4747 | 122.4701 | 122.3511 | 122.5525 | 122.4335 | 0.050354 | -0.009155 | 122.5571 | 122.4609 | 0.17853 | 122.7081 | 122.4289 | 122.6257 | -0.33875 | -122.6715 | 122.2412 | 122.3785 | 122.2183 | 120.3552
1061.5938 | 122.6532 | -122.3648 | 0.24719 | -0.17563 | -0.0022003 | 0.016214 | 0.020258 | 0.00138 | 0.001269 | 0.00097205 | -0.14783 | 0.097912 | 0.13173 | 0.0067954 | 0.09735 | 0.095787 | -0.0022301 | -0.15564 | 0.10986 | -0.11902 | -0.13733 | -0.082397 | -0.1831 | -0.054932 | -2.1011 | 0.27008 | -122.4289 | -0.041199 | 0.041199 | -0.082397 | 0.054932 | 122.2458 | -0.13733 | -0.38452 | 122.2824 | 122.3099 | 122.1817 | 0.064087 | -0.064086 | -0.064087 | 0.022889 | -0.28839 | 122.406 | 122.4197 | 122.2824 | 122.4838 | 122.3465 | 0.036622 | -0.01831 | 122.4701 | 122.3877 | 0.22888 | 122.699 | 122.4747 | 122.6349 | -0.36621 | -122.6761 | 122.2275 | 122.3236 | 122.2092 | 120.2637
1063.3438 | 122.6257 | -72.3267 | 50.3265 | -0.168 | -0.0015595 | 0.015787 | 0.017267 | 0.0015936 | 0.002337 | -0.0011642 | -0.11426 | 0.095348 | 0.13515 | -0.0013224 | 0.089873 | 0.096 | -0.00052114 | -0.12817 | 0.09613 | -0.10986 | -0.11902 | -0.045776 | -0.16022 | -0.018311 | -6.5186 | 48.3994 | -75.6821 | 50.3906 | 50.4822 | 50.3403 | 50.4547 | 72.2168 | -50.2304 | -50.4456 | 72.2809 | 72.3083 | 72.1664 | 0.091552 | -0.050354 | -3.3554 | -1.9272 | 0.064087 | 122.8088 | 122.7814 | 122.6669 | 126.1368 | 126.0223 | 0.064087 | -0.009156 | 126.1642 | 126.0727 | 0.20599 | 124.0814 | 72.4228 | 120.726 | -50.4364 | -126.0086 | 72.2076 | 122.7173 | 72.1985 | 65.8081
1065.0938 | 122.6852 | -118.2907 | 4.2114 | -0.14511 | 0.00057686 | 0.019846 | 0.016199 | 0.0054388 | 0.002978 | 0.0018264 | -0.13257 | 0.092358 | 0.13451 | -0.0047402 | 0.090087 | 0.097923 | 0.0011877 | -0.082397 | 0.10986 | -0.10986 | -0.086975 | -0.022888 | -0.12817 | -0.009155 | -1.9455 | 4.2618 | -118.4097 | 3.9963 | 4.0741 | 3.923 | 4.0512 | 118.1808 | -4.1016 | -4.2984 | 118.2678 | 118.2816 | 118.1625 | 0.10071 | -0.018311 | -0.11902 | 0.050354 | -0.21515 | 122.3648 | 122.3419 | 122.2137 | 122.4609 | 122.3328 | 0.086975 | 0.022888 | 122.4838 | 122.406 | 0.21973 | 122.6715 | 118.4006 | 122.5525 | -4.3213 | -122.6212 | 118.2037 | 122.287 | 118.2083 | 116.3452
1066.7812 | 122.8683 | -121.9391 | 0.53101 | -0.068817 | -0.0034821 | 0.017709 | 0.013208 | -0.00054262 | 0.0016962 | -0.00052335 | -0.0074462 | 0.090222 | 0.13494 | -0.00944 | 0.087737 | 0.094291 | -0.0065027 | -0.09613 | 0.059509 | -0.073242 | -0.013733 | 0.11444 | 0 | 0.11444 | -2.1378 | 0.59052 | -122.0535 | 0.42114 | 0.54932 | 0.43488 | 0.49896 | 121.8658 | -0.4715 | -0.54474 | 122.0535 | 122.0535 | 121.9391 | 0.18768 | 0.073242 | -0.11444 | 0.059509 | -0.10986 | 122.4884 | 122.438 | 122.374 | 122.5525 | 122.4884 | 0.18768 | 0.059509 | 122.6028 | 122.4747 | 0.13275 | 122.644 | 121.9986 | 122.5296 | -0.60425 | -122.5845 | 121.9254 | 122.3602 | 121.843 | 119.8013
1068.5156 | 122.8134 | -121.8613 | 0.64087 | -0.24429 | 0.00014946 | 0.018991 | 0.015344 | 0.0015936 | 0.0010554 | -0.00030975 | -0.062378 | 0.092144 | 0.13259 | -0.00068143 | 0.091582 | 0.097495 | -0.00073494 | -0.054932 | 0.07782 | -0.073242 | -0.004578 | 0.054932 | -0.059509 | 0.082397 | -2.1927 | 0.6958 | -121.9574 | 0.54932 | 0.61798 | 0.50354 | 0.60425 | 121.788 | -0.56305 | -0.64545 | 121.9162 | 121.9437 | 121.8018 | 0.15564 | 0.013733 | -0.09613 | 0.054932 | -0.091553 | 122.4792 | 122.4655 | 122.3648 | 122.5616 | 122.4609 | 0.12817 | 0.068664 | 122.5754 | 122.5067 | 0.15106 | 122.6532 | 121.9391 | 122.5571 | -0.71411 | -122.5983 | 121.8567 | 122.4106 | 121.8063 | 119.6686
1070.25 | 122.6852 | -122.2916 | 0.3067 | -0.12222 | -0.0022003 | 0.021127 | 0.017694 | 0.0018072 | 0.0016962 | 0.0028946 | -0.13257 | 0.10325 | 0.13472 | -0.00025423 | 0.095214 | 0.097068 | -0.0026575 | -0.10529 | 0.086975 | -0.09613 | -0.091553 | -0.022888 | -0.13733 | -0.013733 | -2.2385 | 0.3479 | -122.3831 | 0.054932 | 0.13275 | 0 | 0.13275 | 122.1954 | -0.21973 | -0.39825 | 122.2687 | 122.2778 | 122.1542 | 0.082397 | -0.041199 | -0.091553 | 0.041198 | -0.25177 | 122.4243 | 122.4243 | 122.2916 | 122.5159 | 122.3831 | 0.073242 | 0.004577 | 122.5159 | 122.438 | 0.1831 | 122.731 | 122.3785 | 122.6395 | -0.40283 | -122.6898 | 122.2 | 122.3465 | 122.1863 | 120.0531
1071.9219 | 122.7402 | -122.2458 | 0.32044 | -0.17563 | -0.00091854 | 0.022409 | 0.016626 | -0.00011542 | 0.0031916 | 0.002681 | -0.1051 | 0.10283 | 0.13408 | -0.0064492 | 0.10226 | 0.095787 | 0.00033326 | -0.13733 | 0.10071 | -0.10986 | -0.10986 | -0.050354 | -0.15564 | -0.013733 | -2.3712 | 0.37079 | -122.3053 | 0.11444 | 0.21057 | 0.091553 | 0.20599 | 122.1359 | -0.21973 | -0.4303 | 122.1954 | 122.2321 | 122.0901 | 0.09613 | -0.045777 | -0.059509 | 0.050354 | -0.20599 | 122.4564 | 122.4518 | 122.3373 | 122.5113 | 122.3969 | 0.059509 | 0 | 122.5159 | 122.4197 | 0.21057 | 122.6761 | 122.3465 | 122.6166 | -0.4303 | -122.6257 | 122.1359 | 122.3602 | 122.1085 | 119.8746
1073.6719 | 122.6807 | -121.9849 | 0.59509 | -0.12222 | -0.0013457 | 0.018777 | 0.017481 | -0.001397 | 0.0016962 | 0.00011745 | -0.074585 | 0.094708 | 0.13451 | -0.0030312 | 0.094787 | 0.097709 | 0.00033326 | -0.14648 | 0.091553 | -0.10529 | -0.14648 | -0.082397 | -0.12817 | -0.004578 | -2.5635 | 0.63171 | -122.0627 | 0.31128 | 0.42572 | 0.32501 | 0.43945 | 121.8796 | -0.50354 | -0.74158 | 121.9025 | 121.9803 | 121.8567 | 0.10071 | -0.022888 | -0.07782 | 0.036621 | -0.28381 | 122.4106 | 122.4243 | 122.3099 | 122.5021 | 122.3877 | 0.022889 | -0.041198 | 122.4884 | 122.374 | 0.19684 | 122.6944 | 122.0764 | 122.6166 | -0.70038 | -122.6578 | 121.8384 | 122.2961 | 121.8384 | 119.4214
1075.3594 | 122.6669 | -120.3049 | 2.2705 | -0.15274 | -0.0013457 | 0.018991 | 0.020044 | 0.0033026 | 0.00084159 | 0.00075845 | -0.11426 | 0.10582 | 0.13408 | 0.0040182 | 0.097136 | 0.097923 | 0.00054686 | -0.12817 | 0.10529 | -0.09613 | -0.14191 | -0.10529 | -0.17853 | -0.041199 | -1.6525 | 2.3621 | -120.3323 | 1.9638 | 2.037 | 1.9363 | 2.1378 | 120.2087 | -2.1652 | -2.4124 | 120.1996 | 120.2637 | 120.1263 | 0.054931 | -0.082398 | -0.027465 | 0.091553 | -0.3067 | 122.3419 | 122.4426 | 122.2412 | 122.4701 | 122.2687 | -0.009156 | -0.045777 | 122.3694 | 122.2961 | 0.20142 | 122.6944 | 120.4102 | 122.6669 | -2.3666 | -122.6028 | 120.163 | 122.2687 | 120.1767 | 118.6523
1077.0938 | 122.6898 | -119.3253 | 3.241 | -0.168 | -0.0032683 | 0.017709 | 0.015558 | 0.0037298 | 0.00041439 | 0.00011745 | 0.001709 | 0.10154 | 0.13237 | -0.0023904 | 0.093291 | 0.096427 | -0.00094854 | -0.091553 | 0.07782 | -0.068665 | -0.064087 | 0.027466 | -0.050354 | 0.068665 | -1.6708 | 3.1311 | -119.4717 | 2.9892 | 3.1494 | 3.0304 | 3.1265 | 119.2566 | -3.1631 | -3.3051 | 119.3527 | 119.3939 | 119.2749 | 0.13733 | 0.018311 | -0.14648 | -0.10986 | -0.25177 | 122.4747 | 122.4518 | 122.3557 | 122.5983 | 122.5021 | 0.096131 | 0.004578 | 122.6212 | 122.4609 | 0.14649 | 122.6028 | 119.4031 | 122.4564 | -3.3096 | -122.7127 | 119.2612 | 122.3145 | 119.2337 | 117.6544
1078.8438 | 122.7768 | -120.5566 | 2.0416 | -0.19089 | -0.0039093 | 0.018564 | 0.015558 | -0.0060968 | 0.0025506 | -0.00095055 | 0.0047608 | 0.093853 | 0.13344 | -0.0030312 | 0.090941 | 0.096855 | -0.00052114 | -0.09613 | 0.064087 | -0.073242 | 0 | 0.10071 | 0 | 0.11444 | -2.4948 | 1.9821 | -120.5475 | 1.8951 | 2.092 | 1.9363 | 1.8997 | 120.4834 | -1.9775 | -2.0416 | 120.6573 | 120.6711 | 120.5566 | 0.18768 | 0.073242 | 0.009156 | -0.059509 | -0.14648 | 122.6486 | 122.4564 | 122.493 | 122.4472 | 122.4838 | 0.17395 | 0.073242 | 122.6395 | 122.4426 | 0.13733 | 122.5296 | 120.6207 | 122.5388 | -2.1149 | -122.5891 | 120.5566 | 122.4518 | 120.4605 | 118.0618
1080.5781 | 122.7859 | -119.783 | 2.7237 | -0.15274 | -0.0034821 | 0.018777 | 0.016413 | 0.0018072 | 0.00084159 | 0.00204 | -0.019653 | 0.098126 | 0.1328 | -0.0040994 | 0.088592 | 0.096214 | -0.0032983 | -0.068665 | 0.054932 | -0.073242 | 0.004578 | 0.10071 | 0.009155 | 0.11444 | -2.4078 | 2.7695 | -119.8196 | 2.5909 | 2.7374 | 2.6093 | 2.6871 | 119.7098 | -2.6688 | -2.7191 | 119.8837 | 119.8975 | 119.7922 | 0.18768 | 0.082397 | -0.036621 | 0.045776 | -0.13275 | 122.5204 | 122.4701 | 122.3923 | 122.5067 | 122.4289 | 0.17395 | 0.07782 | 122.5571 | 122.4106 | 0.12817 | 122.5891 | 119.838 | 122.5525 | -2.7969 | -122.5433 | 119.7876 | 122.374 | 119.7144 | 117.3752
1082.3125 | 122.7722 | -119.2154 | 3.3234 | -0.15274 | -0.0030547 | 0.017282 | 0.013422 | -0.00032902 | 0.00062799 | 0.00054465 | -0.010498 | 0.099407 | 0.13558 | -0.0034586 | 0.090728 | 0.095146 | -0.0024439 | -0.09613 | 0.086975 | -0.086975 | -0.041199 | 0.059509 | -0.036621 | 0.09613 | -2.5269 | 3.3554 | -119.22 | 3.1998 | 3.3005 | 3.1494 | 3.2181 | 119.1284 | -3.2364 | -3.3646 | 119.2749 | 119.3115 | 119.1788 | 0.1831 | 0.050354 | -0.004578 | 0.032044 | -0.1236 | 122.5159 | 122.4335 | 122.3648 | 122.4381 | 122.3694 | 0.14648 | 0.045776 | 122.5204 | 122.4197 | 0.17395 | 122.5754 | 119.3024 | 122.5708 | -3.4103 | -122.5433 | 119.1742 | 122.4152 | 119.1193 | 116.6885
1084.0469 | 122.7631 | -121.3303 | 1.1719 | -0.19089 | -0.0030547 | 0.018564 | 0.017267 | -0.00032902 | 0.001269 | 0.00011745 | -0.056274 | 0.098126 | 0.13301 | -0.0070902 | 0.09201 | 0.096214 | -0.0013757 | -0.073242 | 0.050354 | -0.064087 | -0.004578 | 0.09613 | -0.045776 | 0.091553 | -2.7237 | 1.1124 | -121.463 | 1.0895 | 1.1902 | 1.0529 | 1.1124 | 121.2662 | -1.1215 | -1.1765 | 121.4264 | 121.4218 | 121.2845 | 0.15564 | 0.018311 | -0.13275 | -0.059509 | -0.082397 | 122.5204 | 122.4426 | 122.3831 | 122.5754 | 122.5159 | 0.16022 | 0.059509 | 122.6532 | 122.5525 | 0.11444 | 122.5754 | 121.3806 | 122.4426 | -1.236 | -122.6349 | 121.3257 | 122.4197 | 121.257 | 118.6066
1085.7344 | 122.7722 | -121.4035 | 1.1353 | -0.19089 | -0.0019867 | 0.016641 | 0.01449 | -0.0011834 | 0.0014826 | -0.00030975 | -0.03186 | 0.095562 | 0.13344 | 0.0020956 | 0.090728 | 0.097068 | -0.00073494 | -0.082397 | 0.050354 | -0.064087 | -0.009155 | 0.10071 | 0 | 0.10071 | -2.5543 | 1.1673 | -121.4264 | 0.96588 | 1.0986 | 0.98877 | 1.062 | 121.3394 | -1.0849 | -1.1444 | 121.5042 | 121.5042 | 121.4035 | 0.1648 | 0.064087 | -0.022889 | 0.032043 | -0.16937 | 122.5021 | 122.4655 | 122.3923 | 122.4884 | 122.4152 | 0.1648 | 0.054932 | 122.525 | 122.3923 | 0.11444 | 122.5937 | 121.4539 | 122.5708 | -1.1993 | -122.5616 | 121.3943 | 122.3694 | 121.3211 | 118.8492
1087.4844 | 122.6486 | -116.8945 | 5.69 | -0.084076 | -0.0022003 | 0.019632 | 0.016413 | 9.818e-05 | 0.002337 | 0.0024674 | -0.086792 | 0.097271 | 0.13344 | -0.0047402 | 0.090301 | 0.094291 | -0.0039391 | -0.15106 | 0.10986 | -0.10071 | -0.13275 | -0.068665 | -0.1236 | 0.004578 | -2.6642 | 5.7358 | -116.9998 | 5.3833 | 5.4932 | 5.4474 | 5.5161 | 116.7938 | -5.5801 | -5.8228 | 116.8259 | 116.8991 | 116.7709 | 0.10529 | -0.022888 | -0.10529 | 0.045777 | -0.3067 | 122.3877 | 122.4106 | 122.3419 | 122.5159 | 122.4472 | 0.032043 | -0.032043 | 122.493 | 122.3831 | 0.21057 | 122.7356 | 117.0044 | 122.6303 | -5.7907 | -122.6898 | 116.7618 | 122.2778 | 116.7435 | 114.2303
1089.2188 | 122.7448 | -116.7068 | 5.7999 | -0.25192 | -0.0013457 | 0.021127 | 0.017481 | 0.00073918 | 0.00084159 | -0.001378 | -0.056274 | 0.095989 | 0.13301 | -0.0073038 | 0.092864 | 0.097068 | -0.0013757 | -0.068665 | 0.045776 | -0.054932 | -0.004578 | 0.07782 | -0.054932 | 0.064087 | -2.5131 | 5.8685 | -116.7068 | 5.7449 | 5.8273 | 5.6534 | 5.7953 | 116.6519 | -5.7541 | -5.8044 | 116.7847 | 116.7709 | 116.6519 | 0.11902 | 0 | 0 | 0.068664 | -0.054932 | 122.5342 | 122.5021 | 122.3602 | 122.5021 | 122.3602 | 0.13275 | 0.050354 | 122.5342 | 122.4518 | 0.10071 | 122.5754 | 116.7526 | 122.5754 | -5.8548 | -122.5067 | 116.7023 | 122.4518 | 116.6382 | 114.1937
1090.9531 | 122.6807 | -116.8671 | 5.6763 | -0.12222 | -0.0026275 | 0.018991 | 0.018335 | -0.0022516 | 0.0019098 | 0.0013992 | -0.10815 | 0.094067 | 0.13344 | 0.00017297 | 0.089873 | 0.097495 | -0.0037255 | -0.11444 | 0.09613 | -0.10529 | -0.10529 | -0.027466 | -0.10529 | 0.013733 | -2.7008 | 5.7816 | -116.8625 | 5.484 | 5.5984 | 5.4565 | 5.5618 | 116.7618 | -5.5801 | -5.7816 | 116.8396 | 116.8808 | 116.7618 | 0.11902 | 0 | 0.004577 | 0.10529 | -0.19226 | 122.4655 | 122.4289 | 122.3236 | 122.4243 | 122.319 | 0.07782 | 0 | 122.4609 | 122.3465 | 0.20142 | 122.644 | 116.9632 | 122.6486 | -5.7816 | -122.5388 | 116.7618 | 122.3511 | 116.7526 | 114.1663
1092.625 | 122.7722 | -116.684 | 5.8228 | -0.13748 | -0.0062591 | 0.018991 | 0.015344 | 0.00095278 | 0.00062799 | 0.00204 | 0.001709 | 0.10325 | 0.13045 | -0.002604 | 0.099059 | 0.094505 | -0.00073494 | -0.068665 | 0.059509 | -0.073242 | -0.009155 | 0.10529 | 0.009155 | 0.12817 | -2.5864 | 5.8594 | -116.7343 | 5.7541 | 5.9052 | 5.7404 | 5.809 | 116.6107 | -5.7632 | -5.8319 | 116.7892 | 116.8121 | 116.6931 | 0.20142 | 0.082397 | -0.050354 | 0.036621 | -0.068665 | 122.5891 | 122.493 | 122.4243 | 122.5433 | 122.4747 | 0.17853 | 0.064087 | 122.6395 | 122.4884 | 0.13275 | 122.5937 | 116.7435 | 122.5433 | -5.896 | -122.5571 | 116.6748 | 122.438 | 116.6153 | 114.0976
1094.3594 | 122.6669 | -116.3498 | 6.2119 | -0.168 | -6.4144e-05 | 0.019418 | 0.021326 | 0.0020208 | -0.00065361 | 0.00033105 | -0.13562 | 0.09898 | 0.13259 | -0.0021768 | 0.094359 | 0.096855 | -0.0013757 | -0.086975 | 0.091553 | -0.091553 | -0.07782 | -0.004578 | -0.10529 | 0.027466 | -2.7328 | 6.2485 | -116.3727 | 6.0059 | 6.1066 | 5.9647 | 6.0883 | 116.2582 | -6.1203 | -6.2897 | 116.3452 | 116.3773 | 116.2445 | 0.11902 | -0.013733 | -0.022889 | 0.036621 | -0.20599 | 122.4564 | 122.438 | 122.3145 | 122.4609 | 122.3373 | 0.086975 | 0.013733 | 122.4792 | 122.3785 | 0.18311 | 122.6212 | 116.4413 | 122.5983 | -6.3034 | -122.5845 | 116.272 | 122.3557 | 116.2628 | 113.6169
1096.0469 | 122.6532 | -115.8005 | 6.7657 | -0.11459 | 0.00036326 | 0.020059 | 0.016413 | 0.0035162 | 0.0010554 | 0.0016128 | -0.14783 | 0.10966 | 0.13216 | -0.00089503 | 0.10504 | 0.096855 | 0.0018287 | -0.10529 | 0.07782 | -0.082397 | -0.091553 | -0.018311 | -0.10986 | -0.004578 | -2.7786 | 6.7932 | -115.8325 | 6.5872 | 6.6696 | 6.5094 | 6.6467 | 115.7181 | -6.6879 | -6.8573 | 115.7822 | 115.7959 | 115.6906 | 0.077819 | -0.027466 | -0.032044 | 0.027466 | -0.17853 | 122.4701 | 122.4472 | 122.3099 | 122.4792 | 122.3419 | 0.064086 | -0.009156 | 122.5021 | 122.4197 | 0.16022 | 122.6257 | 115.8783 | 122.5937 | -6.8481 | -122.5983 | 115.7089 | 122.3877 | 115.6952 | 113.0219
1097.7812 | 122.4609 | -72.2672 | 50.3448 | -0.12222 | -0.0026275 | 0.017282 | 0.015344 | 0.0015936 | 0.00084159 | 0.0033218 | -0.071533 | 0.10624 | 0.13301 | -0.0055948 | 0.1012 | 0.094505 | -0.0050073 | -0.16022 | 0.10071 | -0.10529 | -0.14191 | -0.068665 | -0.12817 | -0.013733 | -0.60883 | 50.3403 | -72.1939 | 50.2487 | 50.3769 | 50.1755 | 50.3494 | 72.1619 | -50.2441 | -50.4868 | 72.1985 | 72.2534 | 72.139 | 0.091553 | -0.022888 | 0.073242 | -0.004578 | -0.096131 | 122.644 | 122.6166 | 122.4426 | 122.5433 | 122.3694 | 0.036621 | -0.036621 | 122.5708 | 122.4426 | 0.20599 | 122.5342 | 72.3679 | 122.6074 | -50.4501 | -122.5388 | 72.1252 | 122.5159 | 72.1069 | 71.6583
1099.5156 | 122.6715 | -72.2351 | 50.2396 | -0.168 | -0.0034821 | 0.018991 | 0.014704 | -0.0018244 | -1.2808e-05 | 0.00097205 | -0.0013428 | 0.091717 | 0.13344 | -0.0028176 | 0.087951 | 0.096 | 0.0026831 | -0.1236 | 0.064087 | -0.082397 | -0.086975 | -0.013733 | -0.086975 | 0.050354 | -0.82398 | 50.235 | -72.226 | 50.2716 | 50.3998 | 50.235 | 50.386 | 72.1527 | -50.1755 | -50.3265 | 72.2214 | 72.2855 | 72.1481 | 0.13275 | -0.004578 | 0.009155 | -0.004578 | 0.032043 | 122.6349 | 122.6212 | 122.4701 | 122.612 | 122.4609 | 0.068664 | -0.004578 | 122.6257 | 122.4976 | 0.14648 | 122.4609 | 72.2992 | 122.4701 | -50.322 | -122.4655 | 72.1481 | 122.5067 | 72.1115 | 71.4111
1101.2656 | 122.5983 | -72.2946 | 50.2258 | -0.12985 | -0.00049134 | 0.018777 | 0.014276 | -0.0022516 | 0.00062799 | 0.0018264 | -0.044067 | 0.092571 | 0.1343 | 0.0014548 | 0.087951 | 0.096 | -0.0043665 | -0.10529 | 0.07782 | -0.07782 | -0.064087 | 0 | -0.050354 | 0.054932 | -0.83313 | 50.2075 | -72.3129 | 50.148 | 50.2899 | 50.1068 | 50.2533 | 72.2168 | -50.148 | -50.2899 | 72.2946 | 72.3495 | 72.2443 | 0.13275 | 0.027466 | -0.01831 | -0.01831 | -0.07782 | 122.5845 | 122.5479 | 122.4014 | 122.5662 | 122.4197 | 0.07782 | 0.013733 | 122.6028 | 122.4609 | 0.15564 | 122.5204 | 72.3724 | 122.5021 | -50.3037 | -122.5388 | 72.2305 | 122.4426 | 72.1893 | 71.4615
1103 | 122.7173 | -72.5052 | 49.9191 | -0.19852 | -0.0041229 | 0.018564 | 0.015772 | -0.00075622 | 0.00020079 | -0.00073695 | -0.0043944 | 0.092571 | 0.13558 | -0.0034586 | 0.086669 | 0.094078 | -0.00030754 | -0.11902 | 0.068665 | -0.09613 | -0.041199 | 0.032043 | -0.050354 | 0.064087 | -0.85602 | 49.9191 | -72.5555 | 49.9649 | 50.1389 | 49.9512 | 50.1022 | 72.4091 | -49.8505 | -49.9603 | 72.5372 | 72.5693 | 72.4548 | 0.16022 | 0.045776 | -0.050354 | 0 | 0.045777 | 122.644 | 122.6074 | 122.4564 | 122.6578 | 122.5067 | 0.12817 | 0.054931 | 122.6944 | 122.5204 | 0.16479 | 122.4747 | 72.5739 | 122.4243 | -50.0153 | -122.4747 | 72.464 | 122.4701 | 72.3862 | 71.6492
1104.6875 | 122.6486 | -72.0612 | 50.4044 | -0.084076 | -0.0045501 | 0.019418 | 0.016199 | -0.0043878 | -0.001081 | 0.0022536 | -0.037964 | 0.092144 | 0.13301 | -0.010294 | 0.086669 | 0.094932 | -9.3938e-05 | -0.086975 | 0.064087 | -0.073242 | -0.041199 | 0.018311 | -0.041199 | 0.068665 | -71.9833 | 50.4318 | -72.0657 | 50.3769 | 50.5096 | 50.3311 | 50.4684 | 71.9879 | -50.3403 | -50.4456 | 72.0795 | 72.1298 | 72.02 | 0.14191 | 0.032043 | -0.004578 | 0.027466 | -0.027466 | 122.5708 | 122.5296 | 122.3923 | 122.5342 | 122.3969 | 0.091553 | 0.032043 | 122.5754 | 122.4426 | 0.13733 | 122.4976 | 72.1252 | 122.493 | -50.4776 | -122.4701 | 72.02 | 122.438 | 71.9742 | 0.07782
1106.4219 | 122.6807 | -72.0703 | 50.3632 | -0.19852 | -0.0013457 | 0.019418 | 0.018762 | -0.0043878 | 0.00084159 | 0.00054465 | -0.025757 | 0.091931 | 0.13301 | -0.004313 | 0.086455 | 0.094505 | -0.00094854 | -0.1236 | 0.050354 | -0.059509 | -0.059509 | 0.013733 | -0.086975 | 0.050354 | -72.0337 | 50.3632 | -72.0749 | 50.3906 | 50.5051 | 50.3082 | 50.4913 | 72.0108 | -50.3128 | -50.4227 | 72.084 | 72.1207 | 71.9833 | 0.10986 | -0.027466 | -0.004578 | 0 | 0.027466 | 122.5754 | 122.5616 | 122.3785 | 122.5662 | 122.3831 | 0.073242 | 0 | 122.58 | 122.4655 | 0.10986 | 122.438 | 72.1207 | 122.4335 | -50.4227 | -122.438 | 72.0108 | 122.4609 | 71.9467 | 0.036621
1108.1719 | 122.7539 | -116.3818 | 6.0196 | -0.21378 | -0.0022003 | 0.019846 | 0.015131 | -0.0043878 | -0.00044001 | 0.00075845 | -0.028809 | 0.098553 | 0.13451 | 0.0012412 | 0.09201 | 0.095146 | 0.00011966 | -0.11444 | 0.041199 | -0.082397 | -0.054932 | 0.013733 | -0.082397 | 0.050354 | -116.2811 | 6.0287 | -116.5421 | 5.9006 | 6.015 | 5.8823 | 5.9784 | 116.2994 | -5.9784 | -6.0745 | 116.3956 | 116.4322 | 116.2994 | 0.13275 | 0 | -0.16022 | 0.009156 | -0.11902 | 122.3969 | 122.3602 | 122.2641 | 122.5204 | 122.4243 | 0.09613 | 0.027465 | 122.5571 | 122.4426 | 0.1236 | 122.5708 | 116.423 | 122.4106 | -6.102 | -122.5616 | 116.3269 | 122.2824 | 116.2674 | 0.10071
1109.8438 | 122.7676 | -114.6332 | 7.8323 | -0.15274 | -0.0028411 | 0.018777 | 0.019617 | -0.0011834 | -0.0015082 | 0.0011856 | -0.03186 | 0.093426 | 0.13366 | 0.0010276 | 0.089873 | 0.096427 | -0.0026575 | -0.07782 | 0.032043 | -0.073242 | -0.004578 | 0.082397 | -0.004578 | 0.09613 | -114.3356 | 7.7362 | -114.7064 | 7.8461 | 7.9834 | 7.6859 | 7.7316 | 114.5599 | -7.8003 | -7.8369 | 114.7156 | 114.7293 | 114.6286 | 0.16937 | 0.068664 | -0.073242 | -0.09613 | 0.013733 | 122.6166 | 122.3648 | 122.319 | 122.438 | 122.3923 | 0.15564 | 0.068664 | 122.6898 | 122.5525 | 0.10529 | 122.4426 | 114.6652 | 122.3694 | -7.9056 | -122.5388 | 114.6286 | 122.4792 | 114.5554 | 0.29755
1111.5781 | 122.7219 | -115.1184 | 7.37 | -0.19852 | -0.0019867 | 0.018564 | 0.018335 | -0.00032902 | 0.0021234 | -9.6154e-05 | -0.041016 | 0.097271 | 0.13408 | -0.007731 | 0.090728 | 0.096214 | -0.0030847 | -0.11902 | 0.073242 | -0.064087 | -0.059509 | -0.013733 | -0.082397 | 0.050354 | -114.9765 | 7.3425 | -115.1962 | 7.2281 | 7.3471 | 7.2372 | 7.3288 | 115.0543 | -7.2968 | -7.4295 | 115.1047 | 115.1688 | 115.036 | 0.11444 | -0.01831 | -0.07782 | -0.027466 | -0.14191 | 122.4655 | 122.4472 | 122.3557 | 122.525 | 122.4335 | 0.050354 | 0.004578 | 122.5433 | 122.4243 | 0.13733 | 122.5388 | 115.1916 | 122.4609 | -7.4341 | -122.5662 | 115.0589 | 122.3465 | 114.9994 | 0.14191
1113.3281 | 122.6486 | -113.7131 | 8.8257 | -0.099335 | -0.0034821 | 0.020914 | 0.017694 | 0.0015936 | -0.00065361 | 0.00033105 | -0.071533 | 0.095989 | 0.13344 | -0.00046783 | 0.089019 | 0.096641 | -0.0022301 | -0.15106 | 0.091553 | -0.11444 | -0.1236 | -0.054932 | -0.11902 | -0.018311 | -113.443 | 8.9859 | -113.6353 | 8.638 | 8.725 | 8.5648 | 8.6655 | 113.5986 | -8.7341 | -8.9493 | 113.6581 | 113.6948 | 113.5941 | 0.09613 | -0.004578 | 0.07782 | 0.16022 | -0.18768 | 122.4381 | 122.3785 | 122.2778 | 122.3007 | 122.2 | 0.059509 | -0.009155 | 122.3602 | 122.2733 | 0.20599 | 122.6212 | 113.8046 | 122.699 | -8.9401 | -122.4609 | 113.5895 | 122.3511 | 113.562 | 0.27008
1115 | 122.7036 | -113.4384 | 9.0546 | -0.10696 | -0.0036957 | 0.017709 | 0.017053 | -0.0024652 | 0.0014826 | 0.0011856 | -0.041016 | 0.095989 | 0.13494 | 0.0076498 | 0.091796 | 0.095573 | -0.00030754 | -0.082397 | 0.068665 | -0.064087 | -0.018311 | 0.041199 | -0.022888 | 0.073242 | -113.1363 | 9.2194 | -113.3606 | 8.9813 | 9.0683 | 8.9081 | 8.9951 | 113.3743 | -8.9859 | -9.0729 | 113.4796 | 113.5117 | 113.4155 | 0.13733 | 0.041199 | 0.07782 | 0.16479 | -0.073242 | 122.5067 | 122.4335 | 122.3465 | 122.3557 | 122.2687 | 0.10529 | 0.045776 | 122.4289 | 122.3419 | 0.13275 | 122.58 | 113.5071 | 122.6578 | -9.1187 | -122.4152 | 113.4201 | 122.4197 | 113.356 | 0.30212
1116.7344 | 122.7127 | -114.1434 | 8.3771 | -0.19852 | -0.0017731 | 0.01835 | 0.015344 | -0.00011542 | 0.001269 | 0.0011856 | -0.044067 | 0.096203 | 0.13301 | -0.0017496 | 0.08966 | 0.095787 | -0.0015893 | -0.07782 | 0.059509 | -0.073242 | -0.018311 | 0.041199 | -0.022888 | 0.086975 | -113.9099 | 8.3633 | -114.18 | 8.2581 | 8.3588 | 8.2352 | 8.345 | 114.0701 | -8.3176 | -8.3954 | 114.1846 | 114.2303 | 114.1205 | 0.16022 | 0.050354 | -0.036621 | -0.013733 | -0.11902 | 122.5021 | 122.4884 | 122.3785 | 122.525 | 122.4152 | 0.11444 | 0.054931 | 122.5388 | 122.4381 | 0.13275 | 122.5433 | 114.2029 | 122.5067 | -8.4503 | -122.5571 | 114.1251 | 122.4014 | 114.0656 | 0.23346
1118.4219 | 122.7219 | -114.4684 | 8.0246 | -0.168 | -0.0026275 | 0.020273 | 0.015985 | 0.00095278 | -1.2808e-05 | 0.0013992 | -0.056274 | 0.09428 | 0.13408 | -0.0011086 | 0.089446 | 0.096641 | -0.0026575 | -0.10529 | 0.054932 | -0.064087 | -0.068665 | 0.022888 | -0.073242 | 0.041199 | -114.2303 | 8.0475 | -114.4684 | 7.9422 | 8.0292 | 7.8552 | 7.9926 | 114.4043 | -7.9697 | -8.0933 | 114.4913 | 114.5096 | 114.3951 | 0.10529 | -0.009155 | 0 | 0.022888 | -0.082397 | 122.4976 | 122.4609 | 122.3236 | 122.4609 | 122.3236 | 0.086975 | -0.004578 | 122.4976 | 122.4106 | 0.11902 | 122.5159 | 114.5233 | 122.5159 | -8.0887 | -122.493 | 114.3997 | 122.4106 | 114.3631 | 0.23804
1120.1719 | 122.6761 | -114.2441 | 8.2764 | -0.11459 | -0.00049134 | 0.021555 | 0.020471 | -0.00075622 | 0.002337 | -0.00073695 | -0.14172 | 0.096203 | 0.13259 | 0.00038657 | 0.090941 | 0.094078 | -0.0022301 | -0.12817 | 0.09613 | -0.10071 | -0.1236 | -0.036621 | -0.16937 | -0.027466 | -114.0976 | 8.3084 | -114.3173 | 8.1207 | 8.2352 | 8.0795 | 8.2443 | 114.1434 | -8.1802 | -8.4 | 114.2075 | 114.2166 | 114.0747 | 0.073242 | -0.068665 | -0.073242 | 0.032044 | -0.15564 | 122.4792 | 122.4884 | 122.3236 | 122.5616 | 122.3969 | 0.064087 | -0.022888 | 122.5525 | 122.4381 | 0.19684 | 122.6257 | 114.3402 | 122.5525 | -8.3771 | -122.5937 | 114.1205 | 122.3648 | 114.1159 | 0.14648
1121.8594 | 122.6532 | -113.7955 | 8.7341 | -0.13748 | -0.0017731 | 0.018564 | 0.020471 | -0.00032902 | 0.0016962 | 0.00204 | -0.17224 | 0.091931 | 0.13387 | 0.0050864 | 0.089446 | 0.097068 | 0.00076046 | -0.086975 | 0.086975 | -0.10529 | -0.07782 | 0.004578 | -0.10529 | 0.022888 | -113.6124 | 8.7021 | -113.855 | 8.5831 | 8.6746 | 8.5327 | 8.6517 | 113.6902 | -8.6472 | -8.812 | 113.8 | 113.8184 | 113.6902 | 0.12817 | 0 | -0.059509 | -0.032044 | -0.15106 | 122.4701 | 122.4472 | 122.3282 | 122.5067 | 122.3877 | 0.10986 | 0.027466 | 122.5296 | 122.438 | 0.19226 | 122.5571 | 113.8824 | 122.4976 | -8.8394 | -122.5891 | 113.7177 | 122.3785 | 113.7085 | 0.18311
1123.6094 | 122.7722 | -111.9644 | 10.4553 | -0.12222 | 0.00036326 | 0.018564 | 0.015131 | -0.00075622 | 0.00041439 | -9.6154e-05 | -0.041016 | 0.094494 | 0.13558 | -0.0023904 | 0.08966 | 0.094505 | -0.0011621 | -0.086975 | 0.059509 | -0.064087 | -0.032043 | 0.082397 | -0.054932 | 0.068665 | -111.7813 | 10.4691 | -112.0056 | 10.4187 | 10.524 | 10.3729 | 10.4782 | 111.9003 | -10.3958 | -10.4874 | 112.0468 | 112.0331 | 111.9095 | 0.13275 | 0.009155 | -0.041198 | 0.013733 | -0.036621 | 122.4884 | 122.4426 | 122.3373 | 122.4838 | 122.3785 | 0.14648 | 0.032044 | 122.5296 | 122.4243 | 0.1236 | 122.4747 | 112.0239 | 122.4335 | -10.5194 | -122.4609 | 111.9324 | 122.3831 | 111.8774 | 0.18311
1125.2812 | 122.7493 | -112.0056 | 10.405 | -0.22141 | -0.0022003 | 0.0207 | 0.017694 | 0.00138 | 0.0025506 | 0.0018264 | -0.044067 | 0.094067 | 0.13387 | -0.0055948 | 0.093291 | 0.095787 | 0.0011877 | -0.068665 | 0.045776 | -0.054932 | -0.009155 | 0.10071 | -0.041199 | 0.068665 | -111.8179 | 10.4095 | -112.0514 | 10.3775 | 10.4782 | 10.3317 | 10.4279 | 111.9507 | -10.3592 | -10.4141 | 112.1063 | 112.0743 | 111.9644 | 0.1236 | 0.013733 | -0.045777 | 0.004578 | -0.027466 | 122.4838 | 122.4335 | 122.3373 | 122.4792 | 122.3831 | 0.15564 | 0.045777 | 122.5296 | 122.4289 | 0.10071 | 122.4609 | 112.0514 | 122.4152 | -10.4599 | -122.4564 | 111.9965 | 122.3831 | 111.937 | 0.18768
1127.0156 | 122.6944 | -112.4084 | 10.0845 | -0.16037 | -0.0013457 | 0.017923 | 0.014704 | 0.0043708 | 0.0025506 | 0.0022536 | -0.12646 | 0.094921 | 0.13387 | 0.0014548 | 0.088805 | 0.097923 | -0.0032983 | -0.10071 | 0.07782 | -0.091553 | -0.068665 | 0.032043 | -0.10529 | 0.022888 | -112.2345 | 10.0845 | -112.4771 | 9.9838 | 10.0754 | 9.9243 | 10.0571 | 112.3169 | -10.0067 | -10.1532 | 112.4405 | 112.4313 | 112.3032 | 0.11444 | -0.013733 | -0.068665 | 0 | -0.10071 | 122.4838 | 122.4655 | 122.3328 | 122.5342 | 122.4014 | 0.1236 | 0.022888 | 122.5525 | 122.4609 | 0.16937 | 122.5616 | 112.4863 | 122.493 | -10.1761 | -122.5616 | 112.3398 | 122.3923 | 112.3077 | 0.17395
1128.7031 | 122.6852 | -110.9207 | 11.6135 | -0.13748 | -0.0026275 | 0.020273 | 0.016199 | -0.00075622 | 0.0019098 | 0.0016128 | -0.06543 | 0.092785 | 0.13579 | -0.0047402 | 0.091796 | 0.095573 | 0.0033241 | -0.13733 | 0.10071 | -0.12817 | -0.12817 | -0.036621 | -0.10529 | -0.013733 | -110.7742 | 11.6135 | -110.9573 | 11.4807 | 11.5723 | 11.412 | 11.5402 | 110.7925 | -11.5128 | -11.7416 | 110.8841 | 110.907 | 110.8154 | 0.11444 | 0.022888 | -0.036621 | 0 | -0.13275 | 122.493 | 122.4609 | 122.3328 | 122.4976 | 122.3694 | 0.091553 | 0 | 122.5296 | 122.438 | 0.22888 | 122.5708 | 111.0214 | 122.5342 | -11.7416 | -122.5708 | 110.7925 | 122.4014 | 110.7834 | 0.14648
1130.4375 | 122.7768 | -111.8591 | 10.6064 | -0.168 | -0.0024139 | 0.017709 | 0.015772 | -0.001397 | -1.2808e-05 | 0.0022536 | -0.01355 | 0.090222 | 0.13366 | -0.00944 | 0.090514 | 0.095787 | -0.0011621 | -0.064087 | 0.059509 | -0.054932 | 0.004578 | 0.12817 | 0.004578 | 0.10529 | -111.6074 | 10.5835 | -111.9186 | 10.5789 | 10.7254 | 10.5606 | 10.6522 | 111.8042 | -10.5469 | -10.6018 | 111.9873 | 111.9644 | 111.8637 | 0.16022 | 0.05951 | -0.059509 | -0.022888 | -0.027466 | 122.5845 | 122.5113 | 122.4197 | 122.5708 | 122.4792 | 0.18311 | 0.05951 | 122.644 | 122.4976 | 0.11444 | 122.5021 | 111.9186 | 122.4426 | -10.6613 | -122.525 | 111.8637 | 122.438 | 111.795 | 0.25177
1132.1719 | 122.7127 | -111.4883 | 10.9955 | -0.21378 | -0.0013457 | 0.019418 | 0.019831 | -0.00011542 | 0.002978 | -0.0015916 | -0.12341 | 0.095348 | 0.13408 | -0.0013224 | 0.089873 | 0.097495 | 0.0024695 | -0.1236 | 0.082397 | -0.10529 | -0.10529 | -0.018311 | -0.14191 | -0.022888 | -111.3144 | 11.0184 | -111.5616 | 10.9314 | 11.0001 | 10.8673 | 11.0046 | 111.3831 | -10.9131 | -11.1008 | 111.47 | 111.4655 | 111.3464 | 0.082398 | -0.036621 | -0.073242 | 0.022889 | -0.064087 | 122.4884 | 122.493 | 122.3557 | 122.5662 | 122.4289 | 0.086975 | 0 | 122.5616 | 122.493 | 0.18768 | 122.58 | 111.5707 | 122.5067 | -11.1008 | -122.5571 | 111.3831 | 122.4197 | 111.3647 | 0.17395
1133.9219 | 122.7219 | -111.4792 | 10.9909 | -0.12222 | -0.0024139 | 0.018991 | 0.016199 | -0.0011834 | -0.002149 | 0.00097205 | -0.016602 | 0.095562 | 0.13536 | -0.0019632 | 0.091582 | 0.095146 | -0.00030754 | -0.07782 | 0.064087 | -0.09613 | -0.018311 | 0.09613 | -0.004578 | 0.086975 | -111.2686 | 10.9634 | -111.5387 | 10.9314 | 11.0641 | 10.9085 | 11.0001 | 111.3831 | -10.9268 | -11.0092 | 111.5753 | 111.5662 | 111.4746 | 0.1831 | 0.091552 | -0.059509 | -0.027466 | -0.05951 | 122.5433 | 122.4792 | 122.3877 | 122.5388 | 122.4472 | 0.19226 | 0.077819 | 122.6028 | 122.4701 | 0.16022 | 122.5021 | 111.5433 | 122.4426 | -11.087 | -122.5296 | 111.4609 | 122.4106 | 111.4014 | 0.21057
1135.5938 | 122.7219 | -115.4114 | 7.0541 | -0.13748 | -0.0011321 | 0.019418 | 0.015131 | 9.818e-05 | 0.0014826 | 0.0018264 | -0.03186 | 0.097271 | 0.13472 | -0.0011086 | 0.091155 | 0.094505 | -0.0054345 | -0.07782 | 0.045776 | -0.064087 | -0.022888 | 0.064087 | -0.027466 | 0.064087 | -115.2786 | 7.0312 | -115.4846 | 6.9077 | 7.0496 | 6.8756 | 6.9214 | 115.3473 | -7.0084 | -7.077 | 115.4755 | 115.4755 | 115.3839 | 0.12817 | 0.036621 | -0.073242 | -0.022888 | -0.14648 | 122.4609 | 122.3328 | 122.287 | 122.406 | 122.3602 | 0.12817 | 0.041199 | 122.5342 | 122.3923 | 0.10986 | 122.5159 | 115.4572 | 122.4426 | -7.1182 | -122.5388 | 115.3885 | 122.319 | 115.3336 | 0.13275
1137.3281 | 122.7814 | -115.2237 | 7.196 | -0.18326 | -0.00070494 | 0.018777 | 0.01919 | 0.004798 | 0.002978 | 0.00204 | -0.068481 | 0.098126 | 0.13472 | -0.00025423 | 0.091796 | 0.096427 | -0.00030754 | -0.054932 | 0.032043 | -0.07782 | 0.004578 | 0.10071 | -0.041199 | 0.073242 | -115.0269 | 7.3013 | -115.3061 | 7.2372 | 7.3837 | 7.1548 | 7.1869 | 115.1459 | -7.164 | -7.1915 | 115.3244 | 115.2969 | 115.1825 | 0.15106 | 0.036621 | -0.082397 | 0.10529 | 0.041199 | 122.6074 | 122.4106 | 122.3785 | 122.493 | 122.4609 | 0.17853 | 0.082398 | 122.6898 | 122.5433 | 0.10986 | 122.6074 | 115.2557 | 122.525 | -7.2739 | -122.5021 | 115.2283 | 122.4609 | 115.1688 | 0.19684
1139.0781 | 122.644 | -114.8987 | 7.6538 | -0.15274 | -0.0013457 | 0.019418 | 0.019617 | 0.00138 | 0.00041439 | 0.0011856 | -0.14783 | 0.093853 | 0.13451 | 0.0012412 | 0.08966 | 0.097923 | -0.0058617 | -0.13275 | 0.10986 | -0.11444 | -0.12817 | -0.082397 | -0.1831 | -0.050354 | -114.8392 | 7.695 | -114.9216 | 7.5073 | 7.4799 | 7.2784 | 7.4661 | 114.7842 | -7.5439 | -7.782 | 114.8163 | 114.8483 | 114.7156 | 0.064087 | -0.068664 | -0.022888 | 0.041198 | -0.14649 | 122.3785 | 122.3648 | 122.1771 | 122.3877 | 122.2 | 0.032044 | -0.013733 | 122.4014 | 122.4289 | 0.2243 | 122.6166 | 115.0085 | 122.5937 | -7.7683 | -122.5754 | 114.7705 | 122.406 | 114.7659 | 0.05951
1140.8125 | 122.6852 | -115.6952 | 6.8207 | -0.15274 | -0.00070494 | 0.020486 | 0.018762 | 0.00073918 | 0.0019098 | 0.00075845 | -0.10815 | 0.095776 | 0.13408 | -0.0034586 | 0.089232 | 0.096214 | 0.0011877 | -0.10071 | 0.091553 | -0.10529 | -0.073242 | 0.009155 | -0.10529 | -0.004578 | -115.4892 | 6.9214 | -115.6815 | 6.6879 | 6.752 | 6.601 | 6.6925 | 115.5899 | -6.7291 | -6.8939 | 115.7043 | 115.6906 | 115.5899 | 0.10071 | 0 | 0.013732 | 0.10071 | -0.13275 | 122.4472 | 122.3877 | 122.2961 | 122.374 | 122.2824 | 0.11444 | 0.032044 | 122.4335 | 122.3694 | 0.19684 | 122.6028 | 115.7867 | 122.6166 | -6.926 | -122.5021 | 115.6219 | 122.3831 | 115.5945 | 0.20599
1142.5469 | 122.7631 | -114.3997 | 8.1024 | -0.17563 | -0.0036957 | 0.018564 | 0.014276 | -0.00075622 | -0.00022641 | 0.0028946 | 0.001709 | 0.091931 | 0.13536 | -0.0013224 | 0.090941 | 0.095787 | -0.0013757 | -0.13733 | 0.068665 | -0.082397 | -0.045776 | 0.059509 | -0.050354 | 0.082397 | -114.1937 | 8.1253 | -114.386 | 8.0246 | 8.1436 | 7.9971 | 8.1207 | 114.3173 | -8.0338 | -8.1482 | 114.4592 | 114.4821 | 114.3494 | 0.16479 | 0.032043 | 0.013733 | 0.022888 | -0.07782 | 122.5433 | 122.5204 | 122.3969 | 122.5067 | 122.3831 | 0.14191 | 0.036621 | 122.5296 | 122.4106 | 0.15106 | 122.5113 | 114.4684 | 122.525 | -8.1848 | -122.4884 | 114.3539 | 122.4243 | 114.2624 | 0.20599
1144.2344 | 122.6669 | -114.0472 | 8.5098 | -0.076447 | -0.0013457 | 0.019205 | 0.018762 | -0.0033196 | 0.00062799 | 0.00033105 | -0.12036 | 0.096844 | 0.13366 | 0.0040182 | 0.089873 | 0.096214 | -0.0045801 | -0.10071 | 0.082397 | -0.10071 | -0.064087 | 0.022888 | -0.073242 | 0.004578 | -113.8321 | 8.6838 | -114.006 | 8.3862 | 8.5327 | 8.3405 | 8.4595 | 113.9465 | -8.4274 | -8.5739 | 114.0701 | 114.0518 | 113.974 | 0.10529 | 0.027466 | 0.041199 | 0.17395 | -0.1236 | 122.58 | 122.5067 | 122.3877 | 122.4655 | 122.3465 | 0.1236 | 0.036621 | 122.5388 | 122.3923 | 0.18311 | 122.6898 | 114.1296 | 122.731 | -8.6105 | -122.5159 | 113.9832 | 122.4335 | 113.9465 | 0.21515
1145.9531 | 122.7493 | -113.5803 | 8.9081 | -0.10696 | -0.0019867 | 0.018777 | 0.018976 | -0.0028924 | -0.00022641 | -0.00095055 | 0.001709 | 0.092144 | 0.1343 | -0.0028176 | 0.090728 | 0.096214 | 0.00011966 | -0.09613 | 0.068665 | -0.082397 | -0.041199 | 0.086975 | -0.022888 | 0.082397 | -113.4247 | 8.7845 | -113.6353 | 8.9493 | 9.0225 | 8.757 | 8.7753 | 113.4979 | -8.8394 | -8.9493 | 113.6673 | 113.6627 | 113.5574 | 0.16479 | 0.059509 | -0.054932 | -0.1236 | 0.041199 | 122.6028 | 122.3557 | 122.3373 | 122.4106 | 122.3923 | 0.16937 | 0.041198 | 122.6578 | 122.5845 | 0.15106 | 122.4197 | 113.649 | 122.3648 | -8.9905 | -122.5433 | 113.5391 | 122.5296 | 113.4842 | 0.15564
1147.6875 | 122.7264 | -114.1571 | 8.345 | -0.20615 | -0.00027774 | 0.020059 | 0.018549 | 0.0028754 | 0.0025506 | 0.00033105 | -0.08374 | 0.094067 | 0.13152 | -0.0019632 | 0.088805 | 0.095573 | 0.00011966 | -0.11902 | 0.073242 | -0.10529 | -0.07782 | 0.009155 | -0.12817 | 0 | -113.8916 | 8.3725 | -114.1479 | 8.3588 | 8.4915 | 8.2718 | 8.2855 | 114.0518 | -8.2718 | -8.4229 | 114.1663 | 114.1571 | 114.0289 | 0.10529 | -0.022888 | 0.009155 | 0.027466 | 0.013733 | 122.6486 | 122.4426 | 122.4289 | 122.4335 | 122.4197 | 0.11444 | 0.027466 | 122.6395 | 122.5067 | 0.17853 | 122.5204 | 114.2303 | 122.5296 | -8.4503 | -122.493 | 114.0793 | 122.5159 | 114.0381 | 0.2655
1149.3594 | 122.6166 | -113.6261 | 8.8715 | -0.12222 | -0.0056183 | 0.016855 | 0.016626 | -0.0050286 | -0.00044001 | -0.00030975 | -0.041016 | 0.096417 | 0.13601 | 0.0010276 | 0.089232 | 0.096641 | -0.0024439 | -0.16937 | 0.09613 | -0.11444 | -0.12817 | -0.041199 | -0.12817 | -0.018311 | -113.4521 | 9.2056 | -113.4979 | 8.7067 | 8.8257 | 8.6792 | 8.7753 | 113.5117 | -8.7753 | -8.9996 | 113.5849 | 113.6078 | 113.4979 | 0.09613 | -0.013733 | 0.12817 | 0.33417 | -0.1648 | 122.4518 | 122.4014 | 122.3053 | 122.2733 | 122.1771 | 0.073242 | -0.013733 | 122.3236 | 122.2046 | 0.21057 | 122.7036 | 113.7222 | 122.8317 | -8.9859 | -122.3694 | 113.4979 | 122.3328 | 113.4567 | 0.17395
1151.0938 | 122.6349 | -114.0106 | 8.5052 | -0.16037 | -0.0030547 | 0.020273 | 0.017908 | 0.0043708 | 0.0021234 | 0.00204 | -0.12646 | 0.095562 | 0.13408 | 0.0033774 | 0.090941 | 0.096427 | 0.00054686 | -0.09613 | 0.091553 | -0.082397 | -0.082397 | 0.036621 | -0.10071 | -0.009155 | -113.887 | 8.5602 | -114.0839 | 8.4 | 8.4366 | 8.1894 | 8.4091 | 113.9282 | -8.4137 | -8.5876 | 114.0472 | 114.0015 | 113.9099 | 0.073242 | -0.018311 | -0.073242 | 0.054932 | -0.10529 | 122.4472 | 122.4197 | 122.2 | 122.493 | 122.2733 | 0.11902 | 0 | 122.5204 | 122.4838 | 0.17395 | 122.644 | 114.1022 | 122.5708 | -8.5876 | -122.5891 | 113.9282 | 122.4106 | 113.9145 | 0.1236
1152.8281 | 122.6257 | -113.8458 | 8.7067 | -0.12985 | -0.0028411 | 0.017709 | 0.013849 | -0.0035334 | -0.00044001 | 0.00097205 | -0.041016 | 0.095562 | 0.13259 | -0.0079446 | 0.090087 | 0.096427 | -0.0013757 | -0.10986 | 0.068665 | -0.091553 | -0.10071 | -0.009155 | -0.11902 | 0.004578 | -113.7177 | 8.6609 | -113.9008 | 8.4595 | 8.606 | 8.5007 | 8.5602 | 113.7543 | -8.638 | -8.8074 | 113.8367 | 113.8504 | 113.7268 | 0.096131 | -0.027466 | -0.054932 | -0.045776 | -0.24719 | 122.4518 | 122.406 | 122.3465 | 122.4609 | 122.4014 | 0.082398 | -0.009155 | 122.5067 | 122.3602 | 0.16022 | 122.5616 | 113.9145 | 122.5067 | -8.7982 | -122.6074 | 113.7451 | 122.3053 | 113.736 | 0.12817
1154.5781 | 122.612 | -114.1434 | 8.3725 | -0.168 | -0.0013457 | 0.021555 | 0.018762 | -0.00075622 | 0.0014826 | 0.0024674 | -0.12646 | 0.095989 | 0.13366 | 0.002523 | 0.088592 | 0.098564 | -9.3938e-05 | -0.13733 | 0.09613 | -0.086975 | -0.16022 | -0.10071 | -0.20142 | -0.059509 | -114.1068 | 8.3633 | -114.2075 | 8.1848 | 8.2489 | 8.107 | 8.2581 | 114.0564 | -8.2764 | -8.5327 | 114.0427 | 114.0839 | 113.942 | 0.027466 | -0.11444 | -0.064086 | -0.009156 | -0.18768 | 122.3923 | 122.4014 | 122.2504 | 122.4655 | 122.3145 | -0.013733 | -0.073242 | 122.4564 | 122.3923 | 0.1831 | 122.5708 | 114.2395 | 122.5067 | -8.4595 | -122.58 | 113.9832 | 122.3282 | 114.006 | 0.036622
1156.25 | 122.6028 | -111.8179 | 10.6979 | -0.11459 | -0.0011321 | 0.020273 | 0.019617 | 0.0033026 | 0.001269 | -0.0018052 | -0.11426 | 0.097271 | 0.13536 | -4.063e-05 | 0.090087 | 0.097282 | 0.00033326 | -0.13733 | 0.09613 | -0.10071 | -0.13275 | -0.068665 | -0.16479 | -0.059509 | -111.7081 | 10.6888 | -111.8317 | 10.5331 | 10.6064 | 10.4645 | 10.6201 | 111.7172 | -10.6018 | -10.8307 | 111.7493 | 111.7584 | 111.6531 | 0.041199 | -0.064087 | -0.013733 | -0.009155 | -0.16479 | 122.4243 | 122.438 | 122.2824 | 122.4518 | 122.2961 | 0.032043 | -0.032043 | 122.438 | 122.3648 | 0.19684 | 122.5204 | 111.9141 | 122.5067 | -10.7986 | -122.5296 | 111.6852 | 122.3511 | 111.6806 | 0.10986
1157.9844 | 122.6166 | -111.7172 | 10.8307 | -0.17563 | -0.0024139 | 0.017709 | 0.013422 | -0.0016106 | 0.00062799 | -0.00030975 | -0.025757 | 0.097912 | 0.13259 | -0.0021768 | 0.090301 | 0.093864 | 0.00076046 | -0.13733 | 0.091553 | -0.082397 | -0.10071 | -0.013733 | -0.11444 | 0.004578 | -111.5799 | 10.817 | -111.7035 | 10.6522 | 10.7666 | 10.6247 | 10.7391 | 111.6348 | -10.7391 | -10.9314 | 111.7035 | 111.7218 | 111.6028 | 0.086975 | -0.032044 | 0.013733 | -0.013732 | -0.17853 | 122.4838 | 122.4564 | 122.3419 | 122.4426 | 122.3282 | 0.068664 | -0.018311 | 122.4701 | 122.3557 | 0.17395 | 122.5204 | 111.8088 | 122.5342 | -10.9131 | -122.5342 | 111.6165 | 122.3694 | 111.5799 | 0.13733
1159.7188 | 122.6486 | -112.056 | 10.4599 | -0.084076 | -0.0030547 | 0.018564 | 0.015772 | -0.00075622 | 0.0014826 | 0.00097205 | -0.056274 | 0.09898 | 0.13558 | -0.00089503 | 0.08966 | 0.094932 | 0.00011966 | -0.14648 | 0.10529 | -0.10071 | -0.13733 | -0.041199 | -0.12817 | 0 | -111.9232 | 10.4645 | -112.0926 | 10.2997 | 10.4233 | 10.2722 | 10.4095 | 111.9553 | -10.3546 | -10.5972 | 112.0148 | 112.056 | 111.9278 | 0.10071 | -0.027466 | -0.036621 | 0.004578 | -0.16022 | 122.4792 | 122.4655 | 122.3282 | 122.5021 | 122.3648 | 0.059509 | -0.036621 | 122.5159 | 122.3923 | 0.20599 | 122.5571 | 112.1613 | 122.5204 | -10.5606 | -122.5525 | 111.9186 | 122.3557 | 111.9095 | 0.13275
1161.4688 | 122.6532 | -72.2031 | 50.3036 | -0.168 | -0.0015595 | 0.019632 | 0.017694 | 0.00052558 | 0.0034052 | -9.6154e-05 | -0.095947 | 0.095562 | 0.13109 | -0.0085854 | 0.088592 | 0.096855 | 0.0020423 | -0.11902 | 0.073242 | -0.09613 | -0.09613 | 0.004578 | -0.12817 | 0.009155 | -72.1115 | 50.2625 | -72.139 | 50.3403 | 50.4547 | 50.2213 | 50.4456 | 72.1069 | -50.2304 | -50.3998 | 72.2076 | 72.2122 | 72.0749 | 0.10528 | -0.032044 | 0.064087 | -0.041199 | 0.036621 | 122.6578 | 122.6486 | 122.4243 | 122.5845 | 122.3602 | 0.10071 | 0 | 122.5937 | 122.4792 | 0.16937 | 122.4014 | 72.2763 | 122.4655 | -50.3998 | -122.4426 | 72.1069 | 122.5433 | 72.084 | 0.091553
1163.1406 | 122.6807 | -72.4091 | 50.0244 | -0.19089 | -0.00049134 | 0.019632 | 0.018122 | -0.0016106 | 0.0010554 | -0.002446 | -0.044067 | 0.096203 | 0.13558 | -0.00944 | 0.085601 | 0.097068 | -0.0035119 | -0.059509 | 0.050354 | -0.068665 | 0 | 0.073242 | -0.050354 | 0.064087 | -72.2809 | 49.9969 | -72.4182 | 50.1205 | 50.2258 | 50.0381 | 50.2167 | 72.3404 | -49.9741 | -50.0244 | 72.4823 | 72.4731 | 72.3587 | 0.13275 | 0.018311 | -0.009155 | -0.027466 | 0.09613 | 122.6349 | 122.6257 | 122.4472 | 122.6349 | 122.4564 | 0.14191 | 0.068665 | 122.644 | 122.5388 | 0.11902 | 122.4152 | 72.4594 | 122.406 | -50.0931 | -122.4426 | 72.4091 | 122.5296 | 72.3495 | 0.12817
1164.8906 | 122.6944 | -72.6242 | 49.7818 | -0.19852 | -0.00091854 | 0.018564 | 0.016626 | 0.0018072 | 0.0031916 | 0.0024674 | -0.034912 | 0.09428 | 0.13344 | -0.0017496 | 0.085601 | 0.096641 | -0.00094854 | -0.068665 | 0.050354 | -0.054932 | 0 | 0.11444 | -0.059509 | 0.082397 | -72.5281 | 49.7543 | -72.6242 | 49.855 | 49.9924 | 49.791 | 49.9558 | 72.5693 | -49.7314 | -49.7818 | 72.7386 | 72.7066 | 72.5647 | 0.13733 | -0.004577 | 0 | -0.027466 | 0.073243 | 122.6166 | 122.58 | 122.4152 | 122.58 | 122.4152 | 0.16937 | 0.054932 | 122.6166 | 122.4792 | 0.10529 | 122.3785 | 72.6746 | 122.3785 | -49.8367 | -122.406 | 72.6242 | 122.4792 | 72.5555 | 0.096131
1166.6406 | 122.7219 | -72.5052 | 49.8779 | -0.076447 | -0.0041229 | 0.017496 | 0.012781 | -0.0011834 | -0.00086721 | 0.0011856 | 0.013916 | 0.093426 | 0.1328 | -0.006022 | 0.085174 | 0.094932 | 0.0016151 | -0.091553 | 0.045776 | -0.073242 | -0.013733 | 0.11444 | -0.004578 | 0.09613 | -72.4228 | 49.8596 | -72.5372 | 49.9558 | 50.1114 | 49.9374 | 50.061 | 72.4319 | -49.8322 | -49.8917 | 72.6196 | 72.6013 | 72.5006 | 0.16937 | 0.068664 | -0.032043 | -0.018311 | 0.07782 | 122.6166 | 122.5662 | 122.4426 | 122.5983 | 122.4747 | 0.18768 | 0.059509 | 122.6486 | 122.493 | 0.11902 | 122.3969 | 72.551 | 122.3648 | -49.9512 | -122.4152 | 72.4915 | 122.4609 | 72.4136 | 0.082397
1168.3281 | 122.6669 | -117.5034 | 4.9713 | -0.099335 | -0.00070494 | 0.018564 | 0.014063 | 0.0018072 | 0.0019098 | 0.0011856 | -0.019653 | 0.096203 | 0.13387 | -0.003245 | 0.088805 | 0.093864 | -0.0011621 | -0.10529 | 0.082397 | -0.073242 | -0.086975 | 0.018311 | -0.10071 | 0.022888 | -117.4164 | 4.9667 | -117.5903 | 4.7195 | 4.866 | 4.7333 | 4.8294 | 117.4301 | -4.8889 | -5.0583 | 117.5217 | 117.5262 | 117.4026 | 0.09613 | -0.027466 | -0.086975 | -0.004577 | -0.25177 | 122.3694 | 122.3328 | 122.2366 | 122.4197 | 122.3236 | 0.091553 | -0.013733 | 122.4564 | 122.3099 | 0.15564 | 122.5571 | 117.5858 | 122.4701 | -5.0446 | -122.5616 | 117.4164 | 122.2229 | 117.3981 | 0.086975
1170.0781 | 122.731 | -117.3889 | 5.0766 | -0.21378 | -0.0045501 | 0.017496 | 0.015985 | 0.00095278 | 0.00041439 | 0.00097205 | -0.0074462 | 0.095776 | 0.13622 | 0.0020956 | 0.091369 | 0.094078 | -0.0020165 | -0.10071 | 0.064087 | -0.073242 | -0.018311 | 0.10071 | -0.009155 | 0.07782 | -117.1646 | 5.0308 | -117.4576 | 4.8935 | 5.0446 | 4.9164 | 5.0034 | 117.3157 | -5.0125 | -5.0949 | 117.4896 | 117.4667 | 117.3798 | 0.15106 | 0.064087 | -0.068665 | -0.045776 | -0.18311 | 122.4335 | 122.3923 | 122.3053 | 122.4609 | 122.374 | 0.17395 | 0.054931 | 122.5021 | 122.3511 | 0.13733 | 122.4884 | 117.453 | 122.4197 | -5.1498 | -122.5342 | 117.3706 | 122.2824 | 117.2882 | 0.2243
1171.8281 | 122.6669 | -116.2628 | 6.2393 | -0.12985 | -0.0017731 | 0.017496 | 0.017694 | -0.0011834 | 0.001269 | 0.00033105 | -0.13562 | 0.099407 | 0.13344 | 0.002523 | 0.088805 | 0.096 | 0.00011966 | -0.10986 | 0.073242 | -0.07782 | -0.068665 | 0.041199 | -0.10071 | 0.009155 | -116.0934 | 6.221 | -116.3406 | 6.0883 | 6.1752 | 6.0379 | 6.1478 | 116.185 | -6.1661 | -6.308 | 116.304 | 116.272 | 116.1621 | 0.086975 | -0.022888 | -0.07782 | -0.018311 | -0.15106 | 122.438 | 122.4106 | 122.3007 | 122.4884 | 122.3785 | 0.11902 | 0.009155 | 122.5159 | 122.4289 | 0.15106 | 122.5616 | 116.3361 | 122.4838 | -6.3171 | -122.58 | 116.1942 | 122.3511 | 116.153 | 0.16937
1173.5156 | 122.6898 | -116.2811 | 6.2531 | -0.14511 | -0.0032683 | 0.018564 | 0.015558 | 0.0020208 | 0.00062799 | 0.00075845 | -0.0074462 | 0.097698 | 0.1328 | -0.00025423 | 0.092864 | 0.096214 | -0.00030754 | -0.09613 | 0.050354 | -0.073242 | -0.032043 | 0.10071 | -0.022888 | 0.068665 | -116.0522 | 6.1295 | -116.3681 | 6.134 | 6.3034 | 6.0699 | 6.1203 | 116.2079 | -6.2027 | -6.2851 | 116.3818 | 116.3498 | 116.2582 | 0.14191 | 0.050354 | -0.086975 | -0.1236 | -0.11902 | 122.5845 | 122.4014 | 122.3511 | 122.4884 | 122.438 | 0.17395 | 0.041199 | 122.6715 | 122.5021 | 0.1236 | 122.4976 | 116.3315 | 122.4106 | -6.3263 | -122.6212 | 116.2491 | 122.4152 | 116.185 | 0.22888
1175.3125 | 122.6486 | -114.4501 | 8.0429 | -0.14511 | -0.0013457 | 0.01835 | 0.019617 | 0.0022346 | 0.0021234 | 0.00097205 | -0.12036 | 0.098766 | 0.13643 | 0.010427 | 0.090728 | 0.098136 | 0.0018287 | -0.11444 | 0.07782 | -0.10529 | -0.064087 | 0.032043 | -0.10529 | 0 | -114.2258 | 8.0612 | -114.4455 | 7.901 | 8.0612 | 7.869 | 7.9651 | 114.3448 | -7.9651 | -8.107 | 114.4821 | 114.4501 | 114.3448 | 0.10529 | 0 | 0.004577 | 0.01831 | -0.14191 | 122.5113 | 122.4152 | 122.319 | 122.4106 | 122.3145 | 0.13733 | 0.041199 | 122.5067 | 122.3465 | 0.18311 | 122.5067 | 114.5279 | 122.5113 | -8.1482 | -122.4884 | 114.386 | 122.3511 | 114.3356 | 0.2243
1177.0469 | 122.612 | -114.7522 | 7.782 | -0.16037 | -0.0034821 | 0.019846 | 0.015344 | 0.0015936 | 0.00041439 | -9.6154e-05 | -0.056274 | 0.095562 | 0.13494 | -0.0019632 | 0.089873 | 0.095573 | -0.0043665 | -0.15106 | 0.086975 | -0.10071 | -0.13733 | -0.013733 | -0.1236 | -0.013733 | -114.6561 | 7.7316 | -114.8163 | 7.5485 | 7.6584 | 7.5531 | 7.6767 | 114.6515 | -7.695 | -7.9193 | 114.7385 | 114.7385 | 114.6286 | 0.086975 | -0.022888 | -0.064087 | -0.050354 | -0.23346 | 122.4106 | 122.4289 | 122.3053 | 122.493 | 122.3694 | 0.086975 | -0.036621 | 122.4747 | 122.3648 | 0.18768 | 122.5479 | 114.8392 | 122.4838 | -7.8827 | -122.5983 | 114.6149 | 122.3007 | 114.6011 | 0.09613
1178.7969 | 122.6257 | -113.974 | 8.5693 | -0.13748 | -0.00049134 | 0.017282 | 0.017908 | -0.00054262 | 0.00041439 | 0.0018264 | -0.10205 | 0.095776 | 0.13494 | 0.0048728 | 0.087737 | 0.097495 | -0.0022301 | -0.10986 | 0.10529 | -0.09613 | -0.082397 | 0.027466 | -0.09613 | 0.004578 | -113.768 | 8.5144 | -113.9923 | 8.4457 | 8.5098 | 8.313 | 8.4457 | 113.8779 | -8.4641 | -8.6517 | 114.0015 | 113.9786 | 113.8779 | 0.10071 | 0 | -0.018311 | -0.054932 | -0.1236 | 122.4838 | 122.4197 | 122.287 | 122.4381 | 122.3053 | 0.1236 | 0.013733 | 122.5021 | 122.4381 | 0.20142 | 122.5067 | 114.0793 | 122.4884 | -8.6655 | -122.5616 | 113.8916 | 122.4197 | 113.8641 | 0.20599
1180.5 | 122.5983 | -113.9648 | 8.5281 | -0.17563 | -0.0011321 | 0.019205 | 0.018976 | 0.00052558 | -0.00022641 | 0.00033105 | -0.11426 | 0.096844 | 0.13451 | 0.001882 | 0.086883 | 0.096427 | -0.00030754 | -0.14191 | 0.10529 | -0.10529 | -0.14648 | -0.041199 | -0.17395 | -0.045776 | -113.736 | 8.5373 | -113.9465 | 8.3908 | 8.4457 | 8.2855 | 8.4686 | 113.8596 | -8.4229 | -8.6746 | 113.9236 | 113.9191 | 113.7909 | 0.05951 | -0.068664 | 0.018311 | 0.009155 | -0.13733 | 122.4106 | 122.4335 | 122.2504 | 122.4152 | 122.2321 | 0.064087 | -0.041198 | 122.3923 | 122.3373 | 0.21057 | 122.4838 | 114.0701 | 122.5021 | -8.6334 | -122.4747 | 113.8184 | 122.3557 | 113.8229 | 0.22888
1182.2031 | 122.699 | -113.6398 | 8.8394 | -0.168 | -0.0036957 | 0.01835 | 0.014063 | -0.001397 | -0.00086721 | 0.0013992 | -0.010498 | 0.095776 | 0.13515 | -0.0079446 | 0.088378 | 0.094718 | -0.0054345 | -0.091553 | 0.050354 | -0.054932 | -0.018311 | 0.10529 | -0.004578 | 0.07782 | -113.5483 | 8.6563 | -113.7909 | 8.6838 | 8.8165 | 8.7158 | 8.8531 | 113.5849 | -8.7891 | -8.8577 | 113.7451 | 113.7177 | 113.6353 | 0.13275 | 0.050354 | -0.15106 | -0.18311 | -0.15564 | 122.4564 | 122.493 | 122.3557 | 122.644 | 122.5067 | 0.16022 | 0.036621 | 122.6074 | 122.4747 | 0.10529 | 122.4472 | 113.6902 | 122.2961 | -8.8943 | -122.6303 | 113.6215 | 122.3236 | 113.5483 | 0.091553
1183.875 | 122.6532 | -113.681 | 8.7891 | -0.099335 | -0.00070494 | 0.018991 | 0.017267 | 0.00073918 | 0.002337 | 0.0028946 | -0.074585 | 0.096203 | 0.13344 | 0.0016684 | 0.086669 | 0.095146 | -0.00030754 | -0.11902 | 0.10529 | -0.11902 | -0.11444 | 0.004578 | -0.091553 | 0.009155 | -113.5345 | 8.7387 | -113.768 | 8.67 | 8.7616 | 8.6014 | 8.7112 | 113.562 | -8.6838 | -8.9035 | 113.6856 | 113.6902 | 113.5895 | 0.12817 | 0.027466 | -0.086975 | -0.050354 | -0.11902 | 122.4426 | 122.3923 | 122.2824 | 122.4792 | 122.3694 | 0.1236 | 0.004578 | 122.5296 | 122.438 | 0.22431 | 122.5067 | 113.7863 | 122.4197 | -8.9081 | -122.5571 | 113.5666 | 122.3511 | 113.562 | 0.14648
1185.5469 | 122.6532 | -113.4613 | 9.0408 | -0.15274 | -0.00049134 | 0.017282 | 0.017053 | -0.00032902 | 0.001269 | 0.00054465 | -0.089844 | 0.097271 | 0.13323 | -0.0023904 | 0.090941 | 0.097495 | -0.0052209 | -0.10529 | 0.07782 | -0.091553 | -0.073242 | 0.027466 | -0.10529 | 0.004578 | -113.2828 | 9.0225 | -113.5025 | 8.876 | 8.9767 | 8.8531 | 8.9813 | 113.3698 | -8.963 | -9.1141 | 113.4888 | 113.4659 | 113.356 | 0.096131 | -0.013733 | -0.041198 | -0.018311 | -0.16479 | 122.4381 | 122.4426 | 122.3145 | 122.4838 | 122.3557 | 0.11902 | 0.018311 | 122.4792 | 122.3785 | 0.16937 | 122.525 | 113.5391 | 122.4838 | -9.1324 | -122.5433 | 113.3881 | 122.3373 | 113.356 | 0.17853
1187.2969 | 122.612 | -113.6353 | 8.876 | -0.084076 | -0.0039093 | 0.018777 | 0.016413 | 0.00052558 | 0.00084159 | -0.0011642 | -0.041016 | 0.095989 | 0.13579 | 0.002523 | 0.089873 | 0.097282 | -0.0018029 | -0.15106 | 0.082397 | -0.10529 | -0.14191 | -0.036621 | -0.13275 | -0.032043 | -113.5666 | 8.7982 | -113.681 | 8.6838 | 8.7936 | 8.6563 | 8.8028 | 113.53 | -8.7936 | -9.0179 | 113.5986 | 113.6032 | 113.5025 | 0.073243 | -0.027465 | -0.045776 | -0.07782 | -0.19226 | 122.4289 | 122.438 | 122.2916 | 122.4838 | 122.3373 | 0.068665 | -0.036621 | 122.4747 | 122.3648 | 0.18768 | 122.4792 | 113.7177 | 122.4335 | -8.9813 | -122.5571 | 113.4933 | 122.319 | 113.4842 | 0.068665
1188.9844 | 122.699 | -113.9923 | 8.4641 | -0.21378 | -0.0030547 | 0.019418 | 0.014917 | -0.00032902 | 0.0019098 | 0.00097205 | -0.025757 | 0.095562 | 0.13558 | -0.0068766 | 0.091155 | 0.095359 | 0.0020423 | -0.09613 | 0.059509 | -0.068665 | -0.036621 | 0.11444 | -0.064087 | 0.059509 | -113.7634 | 8.4366 | -114.0198 | 8.3588 | 8.4961 | 8.3405 | 8.4503 | 113.9236 | -8.4045 | -8.5007 | 114.1068 | 114.0518 | 113.9282 | 0.12817 | 0.004578 | -0.027465 | -0.027466 | -0.10529 | 122.4884 | 122.4426 | 122.3328 | 122.4701 | 122.3602 | 0.18311 | 0.032044 | 122.5159 | 122.3785 | 0.12817 | 122.4564 | 114.0518 | 122.4289 | -8.5327 | -122.4838 | 113.9557 | 122.3511 | 113.8962 | 0.22888
1190.6719 | 122.5754 | -113.6398 | 8.8577 | -0.14511 | -0.00027774 | 0.0207 | 0.019617 | 0.0035162 | 0.0049006 | 0.00204 | -0.12341 | 0.10603 | 0.13558 | -0.0036722 | 0.093505 | 0.096214 | -0.0030847 | -0.13733 | 0.10529 | -0.10986 | -0.15106 | -0.064087 | -0.1831 | -0.054932 | -113.5391 | 8.8394 | -113.6902 | 8.6609 | 8.7479 | 8.6014 | 8.7799 | 113.53 | -8.7524 | -9.0088 | 113.5757 | 113.5849 | 113.4567 | 0.054931 | -0.073242 | -0.050354 | -0.01831 | -0.19684 | 122.3877 | 122.4197 | 122.2412 | 122.4701 | 122.2916 | 0.045776 | -0.041199 | 122.4381 | 122.3511 | 0.21515 | 122.5296 | 113.7451 | 122.4792 | -8.9676 | -122.5479 | 113.4888 | 122.3007 | 113.5025 | 0.10071
1192.3594 | 122.7402 | -113.6902 | 8.725 | -0.18326 | -0.00070494 | 0.019205 | 0.017908 | 0.00031198 | 0.0019098 | -0.00030975 | -0.068481 | 0.098553 | 0.13195 | 0.0010276 | 0.086455 | 0.097068 | -0.0018029 | -0.073242 | 0.073242 | -0.073242 | -0.027466 | 0.10071 | -0.041199 | 0.073242 | -113.4933 | 8.67 | -113.7634 | 8.6746 | 8.7799 | 8.638 | 8.7662 | 113.6169 | -8.6517 | -8.7524 | 113.7909 | 113.7634 | 113.649 | 0.14648 | 0.032043 | -0.073242 | -0.054932 | -0.050354 | 122.4701 | 122.4564 | 122.3282 | 122.5296 | 122.4014 | 0.17395 | 0.045776 | 122.5433 | 122.4381 | 0.14648 | 122.4335 | 113.7634 | 122.3602 | -8.7982 | -122.4884 | 113.6627 | 122.3648 | 113.6169 | 0.19684
1194.0781 | 122.5616 | -113.1592 | 9.4025 | -0.17563 | -0.00091854 | 0.019846 | 0.020258 | 0.0026618 | 0.0014826 | 0.002681 | -0.12646 | 0.094494 | 0.13301 | -0.002604 | 0.088164 | 0.098777 | -0.0013757 | -0.12817 | 0.091553 | -0.091553 | -0.15564 | -0.064087 | -0.17853 | -0.082397 | -113.0356 | 9.3658 | -113.1683 | 9.1736 | 9.2651 | 9.1141 | 9.256 | 113.0676 | -9.3109 | -9.5581 | 113.0951 | 113.0768 | 112.9807 | 0.009156 | -0.086975 | -0.009155 | -0.036621 | -0.22888 | 122.4243 | 122.4152 | 122.2733 | 122.4243 | 122.2824 | 0.027466 | -0.064087 | 122.4335 | 122.3419 | 0.18311 | 122.5342 | 113.2507 | 122.525 | -9.494 | -122.5708 | 113.0035 | 122.3328 | 113.031 | 0.1236
1195.7656 | 122.6761 | -113.0173 | 9.4986 | -0.17563 | -0.0039093 | 0.019205 | 0.011713 | 0.0050116 | 0.0010554 | 0.0035354 | 0.0078126 | 0.094067 | 0.1343 | -0.007731 | 0.087096 | 0.095787 | 0.0031103 | -0.086975 | 0.054932 | -0.073242 | -0.027466 | 0.09613 | -0.022888 | 0.091553 | -112.7975 | 9.4345 | -113.0447 | 9.3567 | 9.5032 | 9.3521 | 9.4528 | 112.944 | -9.4437 | -9.5261 | 113.1134 | 113.1088 | 112.9944 | 0.16479 | 0.050354 | -0.027466 | -0.064087 | -0.14191 | 122.5204 | 122.4701 | 122.3694 | 122.4976 | 122.3969 | 0.16937 | 0.045776 | 122.5479 | 122.4014 | 0.12817 | 122.4792 | 113.0722 | 122.4518 | -9.5718 | -122.5433 | 112.9898 | 122.374 | 112.9303 | 0.21973
1197.4688 | 122.7173 | -112.674 | 9.7549 | -0.20615 | -0.00091854 | 0.019418 | 0.015985 | -0.00075622 | 0.0010554 | 0.0016128 | -0.06543 | 0.094708 | 0.13344 | 0.0031638 | 0.084319 | 0.094932 | -0.0026575 | -0.1236 | 0.086975 | -0.10071 | -0.07782 | 0.027466 | -0.10529 | 0.022888 | -112.5092 | 9.7458 | -112.7563 | 9.7183 | 9.8099 | 9.6817 | 9.787 | 112.5732 | -9.668 | -9.8328 | 112.7014 | 112.6968 | 112.5687 | 0.1236 | -0.004578 | -0.082398 | -0.009155 | -0.036621 | 122.4838 | 122.4609 | 122.3557 | 122.5433 | 122.4381 | 0.12817 | 0.022888 | 122.5662 | 122.4747 | 0.18768 | 122.5021 | 112.7609 | 122.4197 | -9.8557 | -122.5113 | 112.5961 | 122.3923 | 112.5504 | 0.16479
1199.1562 | 122.5525 | -72.7158 | 49.791 | -0.099335 | -0.0054047 | 0.019632 | 0.014704 | 0.0011664 | 0.00084159 | 0.00011745 | -0.019653 | 0.091931 | 0.13408 | -0.0066628 | 0.083892 | 0.094505 | -0.0015893 | -0.068665 | 0.050354 | -0.07782 | -0.064087 | 0.059509 | -0.041199 | 0.045776 | -72.6059 | 49.7772 | -72.6608 | 49.7498 | 49.8962 | 49.7086 | 49.8596 | 72.6379 | -49.7406 | -49.855 | 72.7753 | 72.7615 | 72.6746 | 0.1236 | 0.036621 | 0.054931 | -0.013733 | -0.041199 | 122.612 | 122.5754 | 122.4243 | 122.5204 | 122.3694 | 0.13733 | 0.013733 | 122.5571 | 122.4106 | 0.12817 | 122.4381 | 72.7661 | 122.493 | -49.8688 | -122.4518 | 72.6517 | 122.4655 | 72.6471 | 0.10986
1200.8438 | 122.6624 | -73.3246 | 49.0723 | -0.19089 | -0.00070494 | 0.019205 | 0.016199 | 0.0011664 | 0.0042596 | 0.00011745 | -0.01355 | 0.089581 | 0.13579 | -0.0049538 | 0.083892 | 0.097495 | -0.0028711 | -0.059509 | 0.022888 | -0.045776 | -0.004578 | 0.11444 | -0.050354 | 0.068665 | -73.233 | 49.0494 | -73.3749 | 49.118 | 49.2599 | 49.0631 | 49.2233 | 73.2788 | -49.0494 | -49.0768 | 73.439 | 73.3932 | 73.2742 | 0.11444 | -0.004578 | -0.050354 | -0.022889 | 0.045776 | 122.5845 | 122.5479 | 122.3877 | 122.5983 | 122.438 | 0.16022 | 0.041198 | 122.6349 | 122.493 | 0.068664 | 122.4243 | 73.3475 | 122.374 | -49.118 | -122.4472 | 73.32 | 122.4426 | 73.2651 | 0.091553
1202.5312 | 122.5616 | -73.2468 | 49.1776 | -0.13748 | -0.0011321 | 0.019205 | 0.017908 | -0.0022516 | 0.00062799 | 0.0048172 | -0.13867 | 0.093853 | 0.13408 | 0.0038046 | 0.082183 | 0.097068 | -0.00094854 | -0.10529 | 0.07782 | -0.10986 | -0.10071 | -0.009155 | -0.13733 | -0.032043 | -73.2925 | 49.1638 | -73.3292 | 49.1089 | 49.2004 | 49.0082 | 49.2233 | 73.1369 | -49.0997 | -49.2783 | 73.2376 | 73.2147 | 73.1094 | 0.07782 | -0.027466 | -0.082398 | -0.013733 | -0.068664 | 122.4472 | 122.4701 | 122.2549 | 122.5525 | 122.3373 | 0.10071 | 0.009155 | 122.5296 | 122.4381 | 0.18768 | 122.493 | 73.3246 | 122.4106 | -49.2874 | -122.5067 | 73.1461 | 122.3557 | 73.1415 | -0.045777
1204.25 | 122.6395 | -73.4024 | 49.0173 | -0.21378 | -0.0017731 | 0.0207 | 0.017481 | -0.0052422 | 0.0025506 | 0.0016128 | -0.03186 | 0.091717 | 0.1343 | -0.0038858 | 0.082824 | 0.093864 | -0.00094854 | -0.10529 | 0.059509 | -0.068665 | -0.036621 | 0.10071 | -0.068665 | 0.050354 | -73.3612 | 48.9716 | -73.4116 | 49.0356 | 49.1684 | 48.9761 | 49.1364 | 73.3337 | -48.9578 | -49.054 | 73.5031 | 73.4528 | 73.3337 | 0.11902 | 0 | -0.009155 | -0.045776 | 0.018311 | 122.5708 | 122.5388 | 122.3785 | 122.5479 | 122.3877 | 0.16937 | 0.032044 | 122.58 | 122.4472 | 0.12817 | 122.3831 | 73.4619 | 122.374 | -49.086 | -122.4289 | 73.3658 | 122.4381 | 73.2971 | 0.041199
1205.9375 | 122.5708 | -73.5672 | 48.8937 | -0.16037 | -0.0024139 | 0.020059 | 0.017267 | -0.001397 | 0.00062799 | 0.0018264 | -0.13867 | 0.094708 | 0.13323 | -0.002604 | 0.081969 | 0.096855 | -0.0018029 | -0.10071 | 0.086975 | -0.10986 | -0.09613 | 0 | -0.13733 | -0.032043 | -73.613 | 48.848 | -73.6313 | 48.7976 | 48.912 | 48.7427 | 48.9304 | 73.4573 | -48.8068 | -48.9899 | 73.5672 | 73.5352 | 73.4299 | 0.07782 | -0.027466 | -0.064087 | -0.045777 | -0.096131 | 122.4792 | 122.4976 | 122.3099 | 122.5616 | 122.374 | 0.10986 | 0.013733 | 122.5433 | 122.4289 | 0.19684 | 122.4792 | 73.6542 | 122.4152 | -49.0036 | -122.525 | 73.4711 | 122.3648 | 73.4665 | -0.045776
1207.6719 | 122.5845 | -73.5352 | 48.8892 | -0.18326 | -0.00091854 | 0.0207 | 0.017267 | 0.0020208 | 0.0021234 | 0.00097205 | -0.086792 | 0.094494 | 0.13707 | 0.0012412 | 0.081756 | 0.096427 | 0.0020423 | -0.14191 | 0.091553 | -0.10529 | -0.14648 | -0.050354 | -0.16937 | -0.054932 | -73.5672 | 48.9075 | -73.5764 | 48.8525 | 48.9578 | 48.7839 | 48.967 | 73.4299 | -48.7976 | -49.0356 | 73.4848 | 73.4802 | 73.3658 | 0.050354 | -0.064087 | -0.041199 | 0.018311 | -0.036621 | 122.493 | 122.5021 | 122.319 | 122.5433 | 122.3602 | 0.054932 | -0.041198 | 122.5342 | 122.4289 | 0.19684 | 122.4838 | 73.6267 | 122.4426 | -48.9944 | -122.4655 | 73.3887 | 122.3877 | 73.3932 | -0.032044
1209.3594 | 122.7219 | -73.9334 | 48.468 | -0.15274 | -0.0032683 | 0.020486 | 0.011713 | -0.0016106 | 0.0010554 | -0.00095055 | 0.026123 | 0.093639 | 0.13665 | -0.0064492 | 0.081756 | 0.096214 | -0.0020165 | -0.086975 | 0.045776 | -0.07782 | -0.022888 | 0.13275 | 0 | 0.11902 | -73.8419 | 48.4406 | -73.9746 | 48.5184 | 48.6923 | 48.5275 | 48.6511 | 73.8556 | -48.4222 | -48.4909 | 74.0662 | 74.0524 | 73.9334 | 0.19684 | 0.07782 | -0.041198 | -0.027466 | 0.050354 | 122.6257 | 122.5845 | 122.4609 | 122.6257 | 122.5021 | 0.21057 | 0.054932 | 122.6669 | 122.493 | 0.1236 | 122.4152 | 73.9792 | 122.374 | -48.5458 | -122.4426 | 73.9105 | 122.4518 | 73.8464 | 0.091553
1211.0469 | 122.6578 | -74.501 | 47.9095 | -0.14511 | -0.0041229 | 0.01835 | 0.012567 | 9.818e-05 | 0.0016962 | 0.0016128 | 0.0047608 | 0.093212 | 0.13686 | -0.0055948 | 0.078979 | 0.093864 | 0.00076046 | -0.086975 | 0.059509 | -0.07782 | -0.013733 | 0.086975 | -0.032043 | 0.059509 | -74.4644 | 47.8912 | -74.5285 | 47.9141 | 48.0652 | 47.8821 | 48.0194 | 74.4232 | -47.85 | -47.9233 | 74.588 | 74.5605 | 74.469 | 0.13733 | 0.045777 | -0.027465 | -0.018311 | 0.004578 | 122.5662 | 122.5204 | 122.3831 | 122.5479 | 122.4106 | 0.16479 | 0.064087 | 122.5937 | 122.4426 | 0.13733 | 122.4197 | 74.5605 | 122.3923 | -47.9874 | -122.438 | 74.4873 | 122.4152 | 74.4141 | 0.036621
1212.7656 | 122.7036 | -74.8352 | 47.5342 | -0.15274 | -0.0022003 | 0.01835 | 0.014276 | 0.0037298 | -0.00086721 | -0.0018052 | 0.0047608 | 0.094708 | 0.13472 | -4.063e-05 | 0.080687 | 0.095787 | -0.0015893 | -0.07782 | 0.059509 | -0.041199 | 0.009155 | 0.14648 | -0.004578 | 0.09613 | -74.7253 | 47.4976 | -74.8718 | 47.6212 | 47.7539 | 47.5662 | 47.699 | 74.794 | -47.4747 | -47.525 | 74.9817 | 74.9313 | 74.8306 | 0.13733 | 0.036621 | -0.036621 | -0.036621 | 0.086975 | 122.5891 | 122.5342 | 122.4014 | 122.5708 | 122.438 | 0.18768 | 0.050354 | 122.6257 | 122.493 | 0.10071 | 122.3694 | 74.8947 | 122.3328 | -47.5754 | -122.406 | 74.8444 | 122.4564 | 74.7574 | 0.10986
1214.4375 | 122.6715 | -82.3059 | 40.0223 | -0.16037 | -0.0017731 | 0.021555 | 0.017267 | 0.00138 | -0.00065361 | 0.0052444 | -0.022705 | 0.093639 | 0.13408 | -0.0073038 | 0.082183 | 0.093223 | 0.00076046 | -0.1236 | 0.064087 | -0.086975 | -0.068665 | 0.041199 | -0.073242 | 0.027466 | -82.1594 | 40.1505 | -82.2189 | 40.0955 | 40.1459 | 39.9582 | 40.1047 | 82.2189 | -39.9582 | -40.0909 | 82.3471 | 82.3334 | 82.2327 | 0.11444 | 0.013733 | 0.086975 | 0.12817 | 0.073242 | 122.4518 | 122.4106 | 122.2641 | 122.3236 | 122.1771 | 0.12817 | 0.01831 | 122.3648 | 122.3145 | 0.15106 | 122.3694 | 82.37 | 122.4564 | -40.1093 | -122.2412 | 82.2372 | 122.4014 | 82.1823 | 0.14648
1216.1094 | 122.7264 | -86.2244 | 36.1267 | -0.12222 | -0.0041229 | 0.018564 | 0.01449 | -0.003106 | -1.2808e-05 | -0.00073695 | -0.025757 | 0.095135 | 0.13344 | -0.0036722 | 0.081115 | 0.095359 | -0.0015893 | -0.07782 | 0.064087 | -0.064087 | 0.004578 | 0.12817 | 0 | 0.091553 | -86.1145 | 36.2366 | -86.2427 | 36.1954 | 36.3098 | 36.1221 | 36.232 | 86.1603 | -36.0626 | -36.1221 | 86.3525 | 86.3159 | 86.2244 | 0.15564 | 0.064087 | -0.018311 | 0.10986 | 0.068665 | 122.5342 | 122.4564 | 122.3465 | 122.4747 | 122.3648 | 0.19226 | 0.068665 | 122.5525 | 122.4381 | 0.12817 | 122.4792 | 86.2885 | 122.4609 | -36.1908 | -122.3694 | 86.2289 | 122.4197 | 86.1465 | 0.10986
1217.8125 | 122.7356 | -118.2129 | 4.2297 | -0.15274 | -0.0030547 | 0.020273 | 0.012567 | -0.00054262 | 0.00041439 | -0.0022324 | -0.037964 | 0.098553 | 0.13344 | 0.0055136 | 0.084105 | 0.095146 | -9.3938e-05 | -0.07782 | 0.059509 | -0.059509 | -0.004578 | 0.11902 | -0.022888 | 0.07782 | -118.0115 | 4.2023 | -118.277 | 4.097 | 4.216 | 4.0924 | 4.1611 | 118.1534 | -4.1702 | -4.2343 | 118.3319 | 118.2907 | 118.19 | 0.13733 | 0.036621 | -0.064087 | -0.027465 | -0.13275 | 122.4289 | 122.374 | 122.3053 | 122.4381 | 122.3694 | 0.17853 | 0.054931 | 122.493 | 122.374 | 0.11902 | 122.4792 | 118.2724 | 122.4152 | -4.2892 | -122.5067 | 118.2083 | 122.3099 | 118.1351 | 0.20142
1219.5469 | 122.6807 | -119.2474 | 3.2318 | -0.16037 | -0.0024139 | 0.017496 | 0.01919 | -0.0022516 | -0.001081 | 0.0022536 | -0.080688 | 0.097912 | 0.1343 | 0.001882 | 0.084105 | 0.095787 | -9.3938e-05 | -0.14648 | 0.07782 | -0.1236 | -0.12817 | -0.036621 | -0.10986 | -0.027466 | -119.1971 | 3.2043 | -119.4077 | 3.0487 | 3.1219 | 2.9526 | 3.1311 | 119.1238 | -3.154 | -3.36 | 119.2108 | 119.22 | 119.1376 | 0.09613 | 0.013733 | -0.16022 | -0.027466 | -0.18311 | 122.3694 | 122.3785 | 122.2 | 122.5388 | 122.3602 | 0.086975 | -0.004578 | 122.5296 | 122.4564 | 0.20142 | 122.612 | 119.3253 | 122.4518 | -3.3554 | -122.6395 | 119.1193 | 122.2961 | 119.101 | 0.050354
1221.2188 | 122.6212 | -122.3099 | 0.19226 | -0.12985 | -0.00091854 | 0.018991 | 0.018976 | 0.00073918 | -0.00065361 | 0.0011856 | -0.077637 | 0.03532 | 0.015522 | 0.0063682 | 0.01361 | -0.0024803 | -0.0039391 | -0.11902 | 0.07782 | -0.09613 | -0.11444 | -0.022888 | -0.14648 | -0.041199 | -0.059509 | 0.23346 | -0.14191 | -0.036621 | 0.027466 | -0.045776 | 0.045776 | 122.2137 | -0.11444 | -0.3067 | 122.287 | 122.2687 | 122.1634 | 0.054931 | -0.050354 | 122.168 | 0.041198 | -0.22888 | 122.3373 | 122.3557 | 122.2641 | 0.18768 | 0.096131 | 0.073242 | -0.018311 | 0.16937 | 0.10529 | 0.17395 | 0.37537 | 122.3877 | 122.5433 | -0.28839 | -0.33417 | 122.1954 | 122.2733 | 122.1909 | 122.2504
1222.9219 | 122.7768 | -122.3099 | 0.16022 | -0.16037 | -0.0041229 | 0.020486 | 0.015344 | 0.00031198 | 0.00062799 | 0.00011745 | 0.068848 | 0.034466 | 0.016376 | 0.0014548 | 0.011901 | -0.0044029 | -0.0032983 | -0.091553 | 0.064087 | -0.073242 | -0.022888 | 0.11444 | -0.009155 | 0.09613 | 0.082397 | 0.21515 | -0.13733 | 0.082397 | 0.20599 | 0.11902 | 0.16479 | 122.2366 | -0.09613 | -0.1831 | 122.4243 | 122.406 | 122.3007 | 0.16937 | 0.064087 | 122.1725 | 0.054932 | -0.07782 | 122.5159 | 122.4747 | 122.4289 | 0.30212 | 0.25635 | 0.18768 | 0.050354 | 0.34332 | 0.21973 | 0.13733 | 0.35248 | 122.374 | 122.525 | -0.23346 | -0.29755 | 122.287 | 122.3923 | 122.2183 | 122.3923
1224.7031 | 122.7448 | -122.3602 | 0.19684 | -0.168 | -0.0024139 | 0.021127 | 0.02154 | 0.0035162 | 0.0036188 | 0.0013992 | -0.06543 | 0.035961 | 0.016804 | 0.012777 | 0.011687 | -0.0018393 | -0.0013757 | -0.13275 | 0.082397 | -0.09613 | -0.086975 | -0.004578 | -0.12817 | -0.004578 | 0.022888 | 0.22888 | -0.12817 | 0.050354 | 0.14191 | 0.054932 | 0.14191 | 122.2641 | -0.11444 | -0.28381 | 122.3557 | 122.3557 | 122.2321 | 0.091552 | -0.032044 | 122.2321 | 0.032044 | -0.14648 | 122.5021 | 122.5021 | 122.4152 | 0.27008 | 0.18311 | 0.091552 | 0.009155 | 0.27008 | 0.17853 | 0.17853 | 0.35706 | 122.4426 | 122.5891 | -0.29297 | -0.32501 | 122.2733 | 122.4106 | 122.2275 | 122.3831
1226.4531 | 122.7814 | -122.3419 | 0.16022 | -0.21378 | -0.0011321 | 0.021555 | 0.018122 | 0.0033026 | 0.0034052 | 0.0018264 | -0.044067 | 0.034252 | 0.014881 | 0.0076498 | 0.011046 | -0.0022665 | -0.0018029 | -0.07782 | 0.059509 | -0.082397 | -0.022888 | 0.068665 | -0.068665 | 0.045776 | 0.068665 | 0.21057 | -0.1236 | 0.086975 | 0.15564 | 0.082397 | 0.16022 | 122.2595 | -0.10071 | -0.1831 | 122.4106 | 122.3877 | 122.2733 | 0.12817 | 0.013732 | 122.2183 | 0.050354 | -0.073242 | 122.4976 | 122.5021 | 122.4243 | 0.28381 | 0.20599 | 0.15106 | 0.059509 | 0.27924 | 0.21057 | 0.14191 | 0.33417 | 122.4014 | 122.5525 | -0.24261 | -0.28381 | 122.319 | 122.4289 | 122.2641 | 122.4106
1228.2031 | 122.7676 | -122.3557 | 0.16022 | -0.18326 | -0.0017731 | 0.022409 | 0.016626 | -0.0026788 | 0.001269 | 0.0011856 | -0.041016 | 0.033611 | 0.016163 | -0.001536 | 0.013183 | -0.0026939 | -0.00073494 | -0.10071 | 0.082397 | -0.082397 | -0.050354 | 0.054932 | -0.068665 | 0.041199 | 0.050354 | 0.20599 | -0.12817 | 0.091553 | 0.16479 | 0.073242 | 0.16022 | 122.2733 | -0.07782 | -0.21057 | 122.4106 | 122.3969 | 122.287 | 0.1236 | 0.013732 | 122.2275 | 0.045777 | -0.068664 | 122.5204 | 122.5159 | 122.4289 | 0.28839 | 0.20142 | 0.13733 | 0.032043 | 0.29297 | 0.21973 | 0.16479 | 0.33417 | 122.438 | 122.5616 | -0.24261 | -0.28839 | 122.3053 | 122.4472 | 122.2549 | 122.406
1229.9062 | 122.8088 | -122.3785 | 0.17853 | -0.16037 | -0.0058319 | 0.019418 | 0.015772 | -0.00011542 | -0.00065361 | 0.0024674 | 0.065796 | 0.035961 | 0.015095 | 0.0078634 | 0.014251 | -0.0071799 | -0.0041527 | -0.10071 | 0.050354 | -0.086975 | 0 | 0.14648 | -0.004578 | 0.10529 | 0.11444 | 0.21057 | -0.13275 | 0.068665 | 0.20142 | 0.11444 | 0.15106 | 122.2916 | -0.12817 | -0.17853 | 122.525 | 122.4838 | 122.374 | 0.19226 | 0.082397 | 122.2458 | 0.032043 | -0.10986 | 122.58 | 122.5296 | 122.493 | 0.28381 | 0.24719 | 0.23346 | 0.086975 | 0.33417 | 0.20142 | 0.13733 | 0.34332 | 122.4289 | 122.5891 | -0.2655 | -0.31128 | 122.3785 | 122.4472 | 122.2778 | 122.493
1231.6562 | 122.7036 | -122.4106 | 0.20142 | -0.168 | -0.00070494 | 0.021127 | 0.019831 | 0.0022346 | 0.00041439 | 0.00204 | -0.068481 | 0.037457 | 0.01894 | 0.0040182 | 0.012542 | -0.0020529 | -0.0062891 | -0.09613 | 0.073242 | -0.091553 | -0.068665 | 0.041199 | -0.10071 | -0.004578 | 0.036621 | 0.2243 | -0.13275 | 0.022888 | 0.091553 | -0.018311 | 0.07782 | 122.319 | -0.12817 | -0.27008 | 122.4518 | 122.406 | 122.3099 | 0.086975 | -0.009155 | 122.2778 | 0.022888 | -0.17853 | 122.5021 | 122.4884 | 122.3923 | 0.21057 | 0.11444 | 0.13275 | 0.022888 | 0.2243 | 0.15564 | 0.16479 | 0.35706 | 122.4838 | 122.6349 | -0.29297 | -0.33417 | 122.3419 | 122.4335 | 122.3145 | 122.4472
1233.3906 | 122.6807 | -122.4335 | 0.19684 | -0.15274 | -0.0028411 | 0.018777 | 0.017267 | 0.00052558 | 0.0010554 | 0.00033105 | -0.06543 | 0.034893 | 0.017017 | 0.013631 | 0.013823 | -0.0033347 | -0.0067163 | -0.14191 | 0.09613 | -0.10071 | -0.15106 | -0.059509 | -0.1831 | -0.064087 | -0.07782 | 0.24261 | -0.16022 | -0.041199 | 0.027466 | -0.050354 | 0.059509 | 122.3328 | -0.10071 | -0.3479 | 122.374 | 122.3694 | 122.2504 | 0.036621 | -0.082397 | 122.2733 | 0.045777 | -0.23804 | 122.4609 | 122.493 | 122.3831 | 0.21973 | 0.10986 | 0.041199 | -0.050354 | 0.18768 | 0.11902 | 0.19684 | 0.40283 | 122.5296 | 122.6761 | -0.29755 | -0.35706 | 122.2824 | 122.3923 | 122.2916 | 122.3557
1235.1406 | 122.7859 | -122.4014 | 0.14648 | -0.12985 | -0.0039093 | 0.016855 | 0.015772 | -0.0022516 | 0.0019098 | 0.0018264 | 0.068848 | 0.03532 | 0.018085 | 0.0033774 | 0.015319 | -0.0063255 | -0.0028711 | -0.086975 | 0.050354 | -0.082397 | -0.004578 | 0.15564 | 0 | 0.1236 | 0.11902 | 0.18768 | -0.11902 | 0.073242 | 0.20599 | 0.1236 | 0.14648 | 122.319 | -0.09613 | -0.15106 | 122.5571 | 122.525 | 122.4014 | 0.20599 | 0.082397 | 122.2824 | 0.041199 | -0.073242 | 122.6074 | 122.5479 | 122.525 | 0.2655 | 0.24261 | 0.23804 | 0.077819 | 0.32501 | 0.19226 | 0.13275 | 0.3067 | 122.4518 | 122.5891 | -0.22888 | -0.2655 | 122.3969 | 122.4747 | 122.3145 | 122.5204
1236.8281 | 122.7814 | -122.374 | 0.14191 | -0.18326 | -0.00091854 | 0.020059 | 0.015344 | 0.0018072 | 0.001269 | 0.00075845 | -0.0043944 | 0.03468 | 0.016163 | -0.00046783 | 0.014251 | -0.0024803 | -0.00094854 | -0.054932 | 0.045776 | -0.054932 | -0.004578 | 0.11444 | -0.036621 | 0.073242 | 0.09613 | 0.19684 | -0.10529 | 0.073242 | 0.1831 | 0.07782 | 0.14648 | 122.319 | -0.096131 | -0.14649 | 122.4884 | 122.4472 | 122.3373 | 0.12817 | 0.018311 | 122.2687 | 0.054931 | -0.068665 | 122.5571 | 122.5204 | 122.4518 | 0.25177 | 0.18311 | 0.16937 | 0.050354 | 0.28839 | 0.17853 | 0.10071 | 0.30212 | 122.4197 | 122.5708 | -0.19684 | -0.24719 | 122.3694 | 122.4472 | 122.319 | 122.4701
1238.5625 | 122.7859 | -122.4243 | 0.16937 | -0.12222 | -0.0045501 | 0.017709 | 0.014917 | -0.003106 | -0.00022641 | 0.00033105 | 0.03833 | 0.034466 | 0.015522 | 0.0020956 | 0.014251 | -0.0039755 | -0.0037255 | -0.073242 | 0.041199 | -0.054932 | -0.013733 | 0.12817 | -0.009155 | 0.091553 | 0.050354 | 0.19226 | -0.13275 | 0.054932 | 0.17853 | 0.091553 | 0.14191 | 122.3694 | -0.12817 | -0.18311 | 122.5525 | 122.5159 | 122.4152 | 0.14649 | 0.045777 | 122.2916 | 0.022888 | -0.11444 | 122.6028 | 122.5662 | 122.5159 | 0.27466 | 0.2243 | 0.18311 | 0.041199 | 0.31128 | 0.18768 | 0.096131 | 0.32501 | 122.4655 | 122.6166 | -0.22431 | -0.30212 | 122.4106 | 122.4792 | 122.3511 | 122.4747
1240.3125 | 122.7127 | -122.438 | 0.1831 | -0.14511 | -0.0019867 | 0.021982 | 0.017267 | -0.0018244 | 0.0025506 | 0.002681 | -0.059326 | 0.035534 | 0.016163 | 0.002523 | 0.011687 | -0.0026939 | -0.00073494 | -0.13275 | 0.091553 | -0.10529 | -0.10986 | -0.022888 | -0.11444 | -0.013733 | -0.027466 | 0.23346 | -0.15106 | -0.004578 | 0.10071 | 0 | 0.10529 | 122.3328 | -0.091552 | -0.29297 | 122.4152 | 122.4243 | 122.3236 | 0.091553 | -0.009155 | 122.287 | 0.050354 | -0.18768 | 122.5388 | 122.5433 | 122.438 | 0.25635 | 0.15106 | 0.082398 | -0.004577 | 0.25177 | 0.14648 | 0.19684 | 0.38452 | 122.5296 | 122.6715 | -0.28839 | -0.33417 | 122.3282 | 122.4335 | 122.3053 | 122.4106
1242.0938 | 122.7676 | -122.4289 | 0.1831 | -0.15274 | -0.0039093 | 0.017923 | 0.015985 | -0.0046014 | 0.00041439 | -0.0011642 | 0.044434 | 0.034252 | 0.015522 | 0.002523 | 0.012969 | -0.0033347 | -0.0024439 | -0.13733 | 0.086975 | -0.086975 | -0.082397 | 0.050354 | -0.059509 | 0.036621 | -0.018311 | 0.20142 | -0.14648 | 0.018311 | 0.15564 | 0.059509 | 0.14191 | 122.3419 | -0.09613 | -0.2655 | 122.4792 | 122.4655 | 122.3694 | 0.1236 | 0.027466 | 122.2824 | 0.018311 | -0.16479 | 122.5845 | 122.5708 | 122.4884 | 0.28839 | 0.20599 | 0.13733 | 0.004578 | 0.30212 | 0.16479 | 0.17395 | 0.3479 | 122.5159 | 122.6303 | -0.27008 | -0.32959 | 122.3465 | 122.4472 | 122.2916 | 122.4106
1243.7969 | 122.8271 | -122.4106 | 0.17853 | -0.15274 | -0.0049773 | 0.017709 | 0.016199 | 0.00052558 | 0.0014826 | -0.00052335 | 0.029175 | 0.032543 | 0.015522 | 0.0067954 | 0.012969 | -0.0018393 | 0.0024695 | -0.086975 | 0.054932 | -0.068665 | 0 | 0.16022 | 0.004578 | 0.11902 | 0.07782 | 0.19226 | -0.14191 | 0.068665 | 0.21057 | 0.12817 | 0.12817 | 122.3419 | -0.1236 | -0.17853 | 122.5708 | 122.5296 | 122.4152 | 0.18768 | 0.073243 | 122.2687 | 0.013733 | -0.10986 | 122.6212 | 122.5388 | 122.5388 | 0.27008 | 0.27008 | 0.22888 | 0.068665 | 0.35248 | 0.21057 | 0.1236 | 0.33417 | 122.4655 | 122.6028 | -0.24719 | -0.32044 | 122.4106 | 122.4792 | 122.3236 | 122.4884
1245.4844 | 122.7585 | -122.4609 | 0.15564 | -0.168 | -0.0015595 | 0.019418 | 0.017481 | -0.0011834 | 0.00041439 | 0.00054465 | 0.023071 | 0.035534 | 0.016804 | 0.00081397 | 0.011687 | -0.0041891 | -0.0028711 | -0.11902 | 0.073242 | -0.064087 | -0.082397 | 0.054932 | -0.07782 | 0.050354 | 0.004578 | 0.20142 | -0.14191 | 0.032043 | 0.11902 | 0.050354 | 0.10986 | 122.3969 | -0.082398 | -0.23804 | 122.5159 | 122.5113 | 122.3831 | 0.11444 | -0.013733 | 122.319 | 0.045776 | -0.1236 | 122.58 | 122.5708 | 122.5113 | 0.25177 | 0.19226 | 0.11902 | -0.01831 | 0.26093 | 0.17395 | 0.13733 | 0.34332 | 122.5342 | 122.6624 | -0.21973 | -0.29755 | 122.3785 | 122.493 | 122.3419 | 122.4655
1247.1719 | 122.7722 | -122.4564 | 0.17395 | -0.14511 | -0.0011321 | 0.019632 | 0.020471 | 0.0028754 | 0.0016962 | -0.00052335 | -0.086792 | 0.034893 | 0.017658 | 0.009786 | 0.012114 | -0.0016257 | 0.00011966 | -0.13275 | 0.07782 | -0.10529 | -0.10071 | -0.009155 | -0.15106 | -0.027466 | 0 | 0.22888 | -0.1236 | 0.018311 | 0.1236 | 0.013733 | 0.1236 | 122.3511 | -0.09613 | -0.27466 | 122.4472 | 122.4289 | 122.3053 | 0.07782 | -0.045776 | 122.3328 | 0.054932 | -0.15564 | 122.58 | 122.58 | 122.4701 | 0.24719 | 0.13733 | 0.096131 | 0.004578 | 0.24719 | 0.14191 | 0.18311 | 0.35248 | 122.5342 | 122.6852 | -0.27924 | -0.29755 | 122.3557 | 122.4747 | 122.3236 | 122.4564
1248.875 | 122.7036 | -122.4701 | 0.19684 | -0.12985 | -0.0039093 | 0.020273 | 0.017053 | 0.00031198 | 0.0014826 | -0.0011642 | 0.013916 | 0.035748 | 0.017445 | 0.0080772 | 0.014678 | -0.0022665 | -0.00094854 | -0.10986 | 0.064087 | -0.086975 | -0.09613 | 0.018311 | -0.11444 | 0.004578 | -0.032043 | 0.23346 | -0.15564 | -0.054932 | 0.068665 | -0.009155 | 0.054932 | 122.3831 | -0.13275 | -0.29297 | 122.4884 | 122.4747 | 122.3557 | 0.091553 | -0.027466 | 122.3145 | 0.036621 | -0.25177 | 122.5388 | 122.525 | 122.4609 | 0.21057 | 0.14649 | 0.10529 | -0.009155 | 0.22431 | 0.10071 | 0.15106 | 0.3891 | 122.5342 | 122.7036 | -0.28381 | -0.35248 | 122.374 | 122.4152 | 122.3602 | 122.4381
1250.625 | 122.7402 | -122.4747 | 0.1831 | -0.099335 | -0.0028411 | 0.0207 | 0.018762 | 0.0018072 | 0.0019098 | 0.0031082 | -0.074585 | 0.036389 | 0.015736 | 0.0010276 | 0.012542 | -0.0014121 | 0.0024695 | -0.11902 | 0.091553 | -0.086975 | -0.091553 | 0.018311 | -0.10071 | 0.013733 | 0.013733 | 0.23804 | -0.13733 | 0.004578 | 0.091553 | 0.022888 | 0.086975 | 122.3877 | -0.091552 | -0.27466 | 122.493 | 122.4884 | 122.374 | 0.10071 | -0.013733 | 122.3373 | 0.054932 | -0.17853 | 122.5662 | 122.5616 | 122.4976 | 0.2243 | 0.16022 | 0.10529 | -0.004578 | 0.22888 | 0.14191 | 0.17853 | 0.37537 | 122.5662 | 122.7127 | -0.27008 | -0.32043 | 122.3831 | 122.4792 | 122.3557 | 122.4884
1252.3281 | 122.7173 | -122.4838 | 0.18768 | -0.12222 | -0.0043365 | 0.016 | 0.018335 | 0.0026618 | -0.002149 | 0.00011745 | -0.022705 | 0.03532 | 0.016376 | 0.0055136 | 0.015746 | -0.0041891 | -0.0013757 | -0.15564 | 0.082397 | -0.10986 | -0.1236 | -0.050354 | -0.15106 | -0.036621 | -0.07782 | 0.23804 | -0.14191 | -0.041199 | 0.07782 | -0.004578 | 0.068665 | 122.374 | -0.10529 | -0.31128 | 122.4335 | 122.4472 | 122.3328 | 0.073242 | -0.041199 | 122.3419 | 0.050354 | -0.22888 | 122.5616 | 122.5525 | 122.4792 | 0.21057 | 0.13733 | 0.059509 | -0.013733 | 0.21973 | 0.10071 | 0.19226 | 0.37994 | 122.5662 | 122.7219 | -0.29755 | -0.32959 | 122.3602 | 122.4426 | 122.3282 | 122.406
1254.0156 | 122.731 | -122.4838 | 0.19226 | -0.12222 | -0.00091854 | 0.019418 | 0.018976 | 0.00073918 | 0.001269 | 0.00097205 | -0.08374 | 0.035534 | 0.01659 | 0.0044456 | 0.013396 | -0.0016257 | -0.0011621 | -0.10071 | 0.082397 | -0.091553 | -0.068665 | 0.022888 | -0.091553 | 0 | 0.013733 | 0.22888 | -0.14191 | 0 | 0.086975 | 0.004578 | 0.086975 | 122.3923 | -0.10986 | -0.26093 | 122.5067 | 122.4838 | 122.3923 | 0.091553 | 0 | 122.3419 | 0.036621 | -0.19226 | 122.5708 | 122.5708 | 122.4884 | 0.22888 | 0.14649 | 0.11444 | 0.022888 | 0.22888 | 0.14191 | 0.17395 | 0.37079 | 122.5662 | 122.7127 | -0.28381 | -0.33417 | 122.4152 | 122.4838 | 122.3831 | 122.4976
1255.7344 | 122.8226 | -122.4335 | 0.1831 | -0.168 | -0.0030547 | 0.019846 | 0.013849 | -0.002038 | 0.0025506 | -0.00030975 | 0.056641 | 0.033611 | 0.015949 | -0.0055948 | 0.015105 | -0.0039755 | -0.0024439 | -0.13275 | 0.054932 | -0.07782 | -0.050354 | 0.07782 | -0.041199 | 0.064087 | 0.041199 | 0.20599 | -0.14191 | 0.036621 | 0.19684 | 0.10529 | 0.16479 | 122.3557 | -0.12817 | -0.23346 | 122.5113 | 122.4976 | 122.3923 | 0.14191 | 0.036621 | 122.2916 | 0.022889 | -0.14648 | 122.6303 | 122.5983 | 122.5388 | 0.3067 | 0.24719 | 0.15564 | 0.027466 | 0.33875 | 0.17853 | 0.13275 | 0.3479 | 122.4884 | 122.6395 | -0.26092 | -0.32501 | 122.3831 | 122.4701 | 122.3007 | 122.4747
1257.4375 | 122.8134 | -122.4152 | 0.13733 | -0.22903 | 0.0010041 | 0.020914 | 0.017694 | -0.0024652 | -0.00044001 | 0.00011745 | -0.01355 | 0.033611 | 0.015095 | 0.0044456 | 0.012542 | -0.0041891 | -0.00030754 | -0.07782 | 0.027466 | -0.050354 | -0.013733 | 0.1236 | -0.054932 | 0.050354 | 0.086975 | 0.1831 | -0.10986 | 0.064087 | 0.17853 | 0.091553 | 0.14648 | 122.3648 | -0.10986 | -0.15106 | 122.5388 | 122.4655 | 122.3602 | 0.10071 | -0.004578 | 122.3053 | 0.045776 | -0.073242 | 122.5937 | 122.5616 | 122.5067 | 0.25635 | 0.20142 | 0.17395 | 0.036621 | 0.28839 | 0.17395 | 0.07782 | 0.29297 | 122.4426 | 122.5983 | -0.18768 | -0.24719 | 122.4014 | 122.4792 | 122.3373 | 122.5021
1259.125 | 122.731 | -122.4564 | 0.17395 | -0.13748 | 0.0018585 | 0.021127 | 0.018122 | -0.0022516 | 0.0034052 | 0.0039626 | -0.062378 | 0.036175 | 0.015522 | 0.0040182 | 0.014037 | -0.0018393 | -0.0024439 | -0.13275 | 0.10986 | -0.10071 | -0.13275 | -0.036621 | -0.17395 | -0.054932 | -0.050354 | 0.2243 | -0.14191 | -0.022888 | 0.041199 | -0.027466 | 0.064087 | 122.3557 | -0.064087 | -0.3067 | 122.4197 | 122.4014 | 122.2824 | 0.045776 | -0.073242 | 122.3145 | 0.050354 | -0.19684 | 122.4976 | 122.5204 | 122.4289 | 0.20599 | 0.11444 | 0.064087 | -0.032043 | 0.18311 | 0.11902 | 0.21057 | 0.36621 | 122.5662 | 122.6807 | -0.27466 | -0.31586 | 122.3236 | 122.4335 | 122.3236 | 122.406
1260.7969 | 122.7127 | -122.4701 | 0.20142 | -0.19089 | -0.0011321 | 0.01835 | 0.017053 | 0.003089 | 0.0014826 | -0.0018052 | -0.086792 | 0.034466 | 0.018085 | 0.0042318 | 0.014464 | -0.0029075 | 0.00054686 | -0.14648 | 0.09613 | -0.10529 | -0.13733 | -0.068665 | -0.17853 | -0.059509 | -0.073242 | 0.23804 | -0.14191 | -0.036621 | 0.027466 | -0.064087 | 0.068665 | 122.3648 | -0.10529 | -0.33875 | 122.4014 | 122.4106 | 122.2916 | 0.045777 | -0.073242 | 122.3282 | 0.036621 | -0.23804 | 122.4976 | 122.5388 | 122.406 | 0.21057 | 0.07782 | 0.036621 | -0.032043 | 0.16937 | 0.10529 | 0.20142 | 0.37994 | 122.5662 | 122.7081 | -0.3067 | -0.34332 | 122.3328 | 122.4335 | 122.3236 | 122.3969
1262.5 | 122.6944 | -122.5021 | 0.19226 | -0.13748 | -0.0030547 | 0.018991 | 0.014704 | -0.00011542 | 0.001269 | 0.0013992 | -0.010498 | 0.03532 | 0.017017 | 0.00038657 | 0.013396 | -0.0033347 | -0.00073494 | -0.17395 | 0.086975 | -0.10986 | -0.13275 | -0.018311 | -0.13733 | -0.027466 | -0.073242 | 0.24261 | -0.14191 | -0.082397 | 0.059509 | -0.018311 | 0.045776 | 122.3923 | -0.10529 | -0.32501 | 122.4838 | 122.4747 | 122.3648 | 0.082397 | -0.027466 | 122.3602 | 0.050354 | -0.27466 | 122.5616 | 122.5479 | 122.4838 | 0.18768 | 0.1236 | 0.091552 | -0.022888 | 0.20142 | 0.05951 | 0.19684 | 0.38452 | 122.5891 | 122.7448 | -0.30212 | -0.33417 | 122.3694 | 122.4197 | 122.3282 | 122.4289
1264.1719 | 122.7585 | -122.4701 | 0.17853 | -0.12222 | -0.0013457 | 0.0207 | 0.017053 | 0.0060798 | 0.00062799 | -0.00073695 | -0.053223 | 0.034039 | 0.017872 | 0.0042318 | 0.013823 | -0.0024803 | -9.3938e-05 | -0.14191 | 0.07782 | -0.1236 | -0.10529 | -0.013733 | -0.16479 | -0.032043 | -0.013733 | 0.21973 | -0.14648 | -0.004578 | 0.07782 | 0.013733 | 0.10529 | 122.3465 | -0.10071 | -0.28381 | 122.4564 | 122.4381 | 122.3053 | 0.091553 | -0.041199 | 122.3236 | 0.041199 | -0.18311 | 122.5479 | 122.5754 | 122.4838 | 0.25177 | 0.16022 | 0.10986 | 0.01831 | 0.2243 | 0.14191 | 0.20142 | 0.36621 | 122.5479 | 122.6898 | -0.30212 | -0.32501 | 122.3648 | 122.4655 | 122.3282 | 122.4564
1265.8438 | 122.8088 | -122.4518 | 0.16479 | -0.22141 | -0.0034821 | 0.018991 | 0.013422 | 0.00031198 | -1.2808e-05 | -9.6154e-05 | 0.053589 | 0.034893 | 0.01659 | 0.0016684 | 0.012969 | -0.0069663 | 0.00076046 | -0.11902 | 0.073242 | -0.068665 | -0.086975 | 0.050354 | -0.091553 | 0.041199 | 0.009155 | 0.21057 | -0.13733 | 0.013733 | 0.14648 | 0.073242 | 0.11902 | 122.3831 | -0.091553 | -0.25177 | 122.5021 | 122.493 | 122.3602 | 0.10986 | -0.022888 | 122.3145 | 0.045776 | -0.15106 | 122.5983 | 122.5708 | 122.525 | 0.25635 | 0.21057 | 0.11902 | -0.01831 | 0.28381 | 0.15106 | 0.14191 | 0.3479 | 122.525 | 122.6624 | -0.23346 | -0.30212 | 122.3648 | 122.4655 | 122.3328 | 122.4609
1267.5312 | 122.7036 | -122.4838 | 0.20142 | -0.14511 | -0.0041229 | 0.018564 | 0.016199 | -0.0024652 | -0.00065361 | 0.00033105 | -0.0074462 | 0.034466 | 0.017231 | 0.0044456 | 0.011901 | -0.0039755 | -0.0052209 | -0.17395 | 0.09613 | -0.10071 | -0.14191 | -0.032043 | -0.1236 | -0.032043 | -0.073242 | 0.23346 | -0.14648 | -0.07782 | 0.050354 | -0.013733 | 0.045776 | 122.3831 | -0.10529 | -0.34332 | 122.4518 | 122.4518 | 122.3602 | 0.068665 | -0.022888 | 122.3373 | 0.032043 | -0.27924 | 122.5342 | 122.5296 | 122.4701 | 0.19226 | 0.13275 | 0.068665 | -0.041199 | 0.19684 | 0.068664 | 0.19684 | 0.37994 | 122.58 | 122.7173 | -0.30212 | -0.3479 | 122.3419 | 122.406 | 122.3099 | 122.4106
1269.2344 | 122.7173 | -122.5067 | 0.19226 | -0.15274 | 0.0012177 | 0.020059 | 0.019831 | 0.0020208 | 0.002978 | -0.00095055 | -0.080688 | 0.034252 | 0.019794 | 0.0046592 | 0.012969 | -0.0024803 | -0.0020165 | -0.14648 | 0.091553 | -0.10986 | -0.13733 | -0.059509 | -0.17395 | -0.050354 | -0.082397 | 0.22888 | -0.15564 | -0.041199 | 0.032043 | -0.036621 | 0.050354 | 122.3969 | -0.10071 | -0.32959 | 122.4472 | 122.4564 | 122.3328 | 0.059509 | -0.064087 | 122.3511 | 0.036621 | -0.23346 | 122.5388 | 122.5571 | 122.4701 | 0.20599 | 0.11902 | 0.050354 | -0.027466 | 0.18768 | 0.11444 | 0.20142 | 0.38452 | 122.5983 | 122.7356 | -0.30212 | -0.3479 | 122.3694 | 122.4655 | 122.3602 | 122.4243
1270.9062 | 122.8226 | -122.4472 | 0.16937 | -0.22141 | -0.0024139 | 0.018137 | 0.017481 | 0.0035162 | 0.0014826 | -0.001378 | 0.029175 | 0.03532 | 0.017872 | 0.007009 | 0.013823 | -0.0046165 | 0.00097406 | -0.064087 | 0.045776 | -0.068665 | -0.009155 | 0.12817 | -0.064087 | 0.045776 | 0.086975 | 0.1831 | -0.10986 | 0.068665 | 0.18768 | 0.073242 | 0.16022 | 122.3785 | -0.1236 | -0.17853 | 122.5754 | 122.493 | 122.3831 | 0.11444 | 0.004578 | 122.3373 | 0.013732 | -0.10071 | 122.6349 | 122.6074 | 122.5204 | 0.27008 | 0.18311 | 0.19684 | 0.05951 | 0.29755 | 0.17853 | 0.11444 | 0.29297 | 122.493 | 122.6303 | -0.23804 | -0.27924 | 122.438 | 122.5159 | 122.3831 | 122.5342
1272.625 | 122.8088 | -122.4518 | 0.16479 | -0.23666 | -0.0034821 | 0.020914 | 0.015558 | 0.00052558 | 0.0027644 | -9.6154e-05 | 0.02002 | 0.035534 | 0.01894 | -0.0030312 | 0.015532 | -0.0044029 | -0.0011621 | -0.091553 | 0.041199 | -0.054932 | -0.032043 | 0.11444 | -0.073242 | 0.054932 | 0.064087 | 0.18768 | -0.10071 | 0.027466 | 0.13275 | 0.068665 | 0.11902 | 122.3969 | -0.1236 | -0.19684 | 122.5662 | 122.5067 | 122.3785 | 0.10986 | -0.01831 | 122.3511 | 0.022888 | -0.13733 | 122.5845 | 122.5708 | 122.5204 | 0.21973 | 0.16937 | 0.16937 | 0.022889 | 0.23346 | 0.12817 | 0.096131 | 0.28839 | 122.493 | 122.6395 | -0.21973 | -0.2655 | 122.4197 | 122.4792 | 122.3602 | 122.5159
1274.2969 | 122.8867 | -122.4655 | 0.16479 | -0.18326 | -0.00070494 | 0.017282 | 0.014276 | 0.00031198 | 0.0010554 | 0.0018264 | 0.056641 | 0.034039 | 0.017231 | 0.0042318 | 0.011687 | -0.0054709 | 0.0028967 | -0.082397 | 0.054932 | -0.07782 | 0.004578 | 0.15106 | 0.009155 | 0.09613 | 0.14191 | 0.17395 | -0.09613 | 0.064087 | 0.19684 | 0.11902 | 0.15564 | 122.3877 | -0.10986 | -0.16022 | 122.6166 | 122.5616 | 122.4747 | 0.17395 | 0.086975 | 122.3694 | 0.009155 | -0.10071 | 122.6624 | 122.6212 | 122.5845 | 0.25177 | 0.21515 | 0.22888 | 0.082398 | 0.29297 | 0.16022 | 0.13275 | 0.27008 | 122.5204 | 122.6395 | -0.24261 | -0.26092 | 122.4701 | 122.5296 | 122.3831 | 122.6074
1275.9688 | 122.818 | -122.4701 | 0.1831 | -0.19089 | -0.0026275 | 0.018137 | 0.014276 | 0.0033026 | -0.002149 | 0.0011856 | 0.026123 | 0.034466 | 0.017017 | 0.0038046 | 0.012328 | -0.0054709 | -0.0039391 | -0.086975 | 0.041199 | -0.054932 | -0.004578 | 0.091553 | -0.013733 | 0.068665 | 0.068665 | 0.20599 | -0.11902 | 0.018311 | 0.15106 | 0.086975 | 0.11902 | 122.4152 | -0.14191 | -0.18768 | 122.5616 | 122.5388 | 122.4564 | 0.1236 | 0.041199 | 122.3511 | 0.022889 | -0.16479 | 122.6212 | 122.5891 | 122.5571 | 0.23804 | 0.20599 | 0.14649 | 0.050354 | 0.27008 | 0.13733 | 0.096131 | 0.32501 | 122.5113 | 122.6761 | -0.23804 | -0.30212 | 122.4655 | 122.4884 | 122.3831 | 122.5388
1277.6719 | 122.8088 | -122.4472 | 0.17395 | -0.168 | -0.0034821 | 0.020059 | 0.016413 | 0.00031198 | 0.0021234 | 0.00075845 | 0.029175 | 0.03468 | 0.018299 | 0.0012412 | 0.011474 | -0.0033347 | -0.0015893 | -0.11444 | 0.050354 | -0.064087 | -0.064087 | 0.050354 | -0.082397 | 0.041199 | 0.009155 | 0.21515 | -0.13733 | 0.013733 | 0.11902 | 0.041199 | 0.10986 | 122.3831 | -0.1236 | -0.23804 | 122.4976 | 122.4884 | 122.3648 | 0.10529 | -0.01831 | 122.3099 | 0.041199 | -0.16022 | 122.5662 | 122.5571 | 122.4884 | 0.24719 | 0.17853 | 0.11444 | 0 | 0.25635 | 0.15106 | 0.11444 | 0.35248 | 122.4976 | 122.6624 | -0.23804 | -0.31128 | 122.3831 | 122.4609 | 122.3328 | 122.4564
1279.3594 | 122.8226 | -122.4609 | 0.16022 | -0.19852 | -0.0015595 | 0.018137 | 0.014917 | -0.003106 | 0.00084159 | -0.0022324 | 0.029175 | 0.036175 | 0.016163 | 0.00038657 | 0.011901 | -0.0052573 | 0.0011877 | -0.11444 | 0.064087 | -0.07782 | -0.068665 | 0.041199 | -0.10071 | 0.036621 | 0.009155 | 0.20599 | -0.11902 | 0.009155 | 0.1236 | 0.041199 | 0.11902 | 122.3831 | -0.09613 | -0.22888 | 122.5021 | 122.4976 | 122.3602 | 0.11444 | -0.022888 | 122.3419 | 0.045777 | -0.15106 | 122.5845 | 122.58 | 122.5021 | 0.23804 | 0.16022 | 0.11902 | 0.009155 | 0.24261 | 0.12817 | 0.14191 | 0.32501 | 122.525 | 122.6669 | -0.23804 | -0.27924 | 122.3923 | 122.4701 | 122.3465 | 122.4701
1281.0469 | 122.8775 | -122.4747 | 0.16479 | -0.17563 | -0.0034821 | 0.017923 | 0.017267 | 0.00052558 | 0.00062799 | -0.0020188 | 0.029175 | 0.034893 | 0.014667 | -0.0021768 | 0.011474 | -0.0029075 | -0.0024439 | -0.068665 | 0.045776 | -0.068665 | 0.004578 | 0.1236 | -0.013733 | 0.10529 | 0.11902 | 0.19684 | -0.10529 | 0.086975 | 0.2243 | 0.1236 | 0.1831 | 122.406 | -0.11902 | -0.16022 | 122.5983 | 122.58 | 122.4609 | 0.17395 | 0.054932 | 122.3694 | 0.032043 | -0.07782 | 122.699 | 122.6578 | 122.5983 | 0.28839 | 0.22888 | 0.19226 | 0.073243 | 0.32959 | 0.19226 | 0.11444 | 0.30212 | 122.5204 | 122.6715 | -0.23346 | -0.27008 | 122.4792 | 122.5616 | 122.406 | 122.5937
1282.7188 | 122.7448 | -122.5067 | 0.19226 | -0.12985 | -0.0030547 | 0.018564 | 0.017481 | -0.0035334 | -0.00065361 | 0.00033105 | -0.044067 | 0.03532 | 0.018299 | 0.007009 | 0.01126 | -0.0044029 | -0.0011621 | -0.16022 | 0.09613 | -0.1236 | -0.14191 | -0.032043 | -0.13733 | -0.018311 | -0.073242 | 0.25177 | -0.15564 | -0.064087 | 0.059509 | -0.041199 | 0.041199 | 122.3831 | -0.096131 | -0.33417 | 122.4747 | 122.4884 | 122.3694 | 0.10528 | -0.013733 | 122.3511 | 0.059509 | -0.25635 | 122.5662 | 122.5479 | 122.4655 | 0.19684 | 0.11444 | 0.091553 | -0.018311 | 0.21515 | 0.091553 | 0.21973 | 0.40741 | 122.6028 | 122.7585 | -0.31586 | -0.3479 | 122.3648 | 122.4426 | 122.3465 | 122.4335
1284.3906 | 122.7814 | -122.5388 | 0.19684 | -0.15274 | -0.0041229 | 0.017068 | 0.017267 | -0.0018244 | 0.0021234 | 0.00011745 | -0.071533 | 0.035961 | 0.015736 | 0.0050864 | 0.012755 | -0.0014121 | -0.00030754 | -0.11902 | 0.082397 | -0.091553 | -0.10071 | -0.018311 | -0.11902 | -0.018311 | -0.041199 | 0.2243 | -0.13275 | -0.027466 | 0.11444 | 0.013733 | 0.10529 | 122.4472 | -0.11444 | -0.29755 | 122.5204 | 122.5204 | 122.4197 | 0.073242 | -0.027466 | 122.406 | 0.027466 | -0.2243 | 122.6532 | 122.644 | 122.5525 | 0.23804 | 0.14648 | 0.073242 | -0.009155 | 0.24719 | 0.10529 | 0.17395 | 0.35706 | 122.6212 | 122.7631 | -0.28839 | -0.32959 | 122.438 | 122.5113 | 122.4197 | 122.4976
1286.0625 | 122.7356 | -122.4884 | 0.17395 | -0.13748 | -0.00091854 | 0.020059 | 0.01684 | 0.0028754 | 0.00062799 | 0.00011745 | -0.086792 | 0.035748 | 0.01659 | 0.0020956 | 0.01361 | -0.0014121 | -0.0013757 | -0.13733 | 0.082397 | -0.10529 | -0.15106 | -0.07782 | -0.18768 | -0.073242 | -0.1236 | 0.23346 | -0.14191 | -0.050354 | 0.036621 | -0.059509 | 0.050354 | 122.3831 | -0.091553 | -0.32501 | 122.4106 | 122.4152 | 122.3007 | 0.032044 | -0.082397 | 122.3465 | 0.059509 | -0.2243 | 122.525 | 122.5388 | 122.4289 | 0.19226 | 0.082398 | 0.027466 | -0.045776 | 0.17853 | 0.091553 | 0.18768 | 0.37537 | 122.5708 | 122.7219 | -0.27924 | -0.31586 | 122.3373 | 122.438 | 122.3511 | 122.3648
1287.7344 | 122.8638 | -122.4747 | 0.16022 | -0.24429 | -0.0017731 | 0.020273 | 0.015344 | -0.0022516 | 0.0025506 | 0.00204 | -0.019653 | 0.03468 | 0.017017 | -0.0019632 | 0.012969 | -0.0035483 | -0.0024439 | -0.059509 | 0.041199 | -0.045776 | -0.004578 | 0.10986 | -0.064087 | 0.059509 | 0.091553 | 0.19684 | -0.10529 | 0.086975 | 0.17853 | 0.086975 | 0.16479 | 122.4289 | -0.11902 | -0.16479 | 122.5845 | 122.5342 | 122.4106 | 0.10528 | -0.018311 | 122.3694 | 0.036621 | -0.073242 | 122.6532 | 122.6395 | 122.5616 | 0.27008 | 0.19226 | 0.15564 | 0.041198 | 0.28381 | 0.19226 | 0.086975 | 0.30212 | 122.5159 | 122.6715 | -0.20599 | -0.2655 | 122.4701 | 122.5616 | 122.4152 | 122.5662
1289.4062 | 122.8546 | -122.4976 | 0.16937 | -0.14511 | -0.0041229 | 0.019205 | 0.015772 | -0.0028924 | -0.0025762 | 0.00033105 | 0.026123 | 0.034466 | 0.017017 | -0.0011086 | 0.010406 | -0.0041891 | -0.0026575 | -0.082397 | 0.045776 | -0.059509 | -0.004578 | 0.13733 | -0.009155 | 0.073242 | 0.082397 | 0.1831 | -0.11902 | 0.059509 | 0.20142 | 0.1236 | 0.15106 | 122.438 | -0.1236 | -0.17395 | 122.6349 | 122.5708 | 122.4884 | 0.13275 | 0.050354 | 122.3785 | 0.013732 | -0.10986 | 122.699 | 122.6486 | 122.6212 | 0.27008 | 0.24261 | 0.19684 | 0.054931 | 0.32044 | 0.17853 | 0.10528 | 0.30212 | 122.5433 | 122.6807 | -0.22888 | -0.28839 | 122.493 | 122.5571 | 122.4152 | 122.58
1291.0781 | 122.8775 | -122.4838 | 0.15106 | -0.13748 | -0.0051909 | 0.019632 | 0.015131 | -0.00054262 | 0.0010554 | 0.0033218 | 0.035278 | 0.033184 | 0.017445 | -0.002604 | 0.012755 | -0.0054709 | 0.0026831 | -0.082397 | 0.050354 | -0.068665 | -0.009155 | 0.13733 | -0.004578 | 0.086975 | 0.086975 | 0.20599 | -0.10529 | 0.064087 | 0.18768 | 0.1236 | 0.14648 | 122.4152 | -0.10071 | -0.16022 | 122.6212 | 122.5708 | 122.4792 | 0.15564 | 0.064087 | 122.3785 | 0.054932 | -0.086975 | 122.6715 | 122.6303 | 122.6074 | 0.25177 | 0.22888 | 0.20599 | 0.05951 | 0.29297 | 0.16937 | 0.11902 | 0.31128 | 122.5342 | 122.6898 | -0.21973 | -0.25635 | 122.4747 | 122.5479 | 122.4014 | 122.5708
1292.7812 | 122.85 | -122.4655 | 0.15106 | -0.12985 | -0.0019867 | 0.017709 | 0.017481 | 0.0011664 | 0.001269 | 0.0035354 | -0.071533 | 0.034466 | 0.017017 | 0.0029502 | 0.012755 | -0.00098487 | -0.00030754 | -0.11902 | 0.064087 | -0.09613 | -0.073242 | 0.027466 | -0.1236 | 0.004578 | 0.045776 | 0.20599 | -0.11902 | 0.07782 | 0.15564 | 0.068665 | 0.14648 | 122.3694 | -0.086975 | -0.2243 | 122.493 | 122.4701 | 122.3419 | 0.10071 | -0.027466 | 122.3465 | 0.054932 | -0.073242 | 122.6212 | 122.612 | 122.5342 | 0.2655 | 0.18768 | 0.1236 | 0.022888 | 0.27466 | 0.19684 | 0.16022 | 0.32501 | 122.5296 | 122.6715 | -0.24719 | -0.27008 | 122.3923 | 122.5433 | 122.3465 | 122.5113
1294.5 | 122.7951 | -122.4976 | 0.17853 | -0.15274 | -0.0024139 | 0.018564 | 0.017694 | 9.818e-05 | 0.0021234 | 0.00097205 | -0.062378 | 0.033825 | 0.016804 | 0.0072226 | 0.014251 | -0.0031211 | -0.0015893 | -0.14191 | 0.073242 | -0.11902 | -0.1236 | -0.018311 | -0.1236 | -0.032043 | -0.045776 | 0.22888 | -0.15106 | -0.036621 | 0.10529 | 0 | 0.07782 | 122.3785 | -0.10529 | -0.30212 | 122.4792 | 122.4655 | 122.374 | 0.086976 | -0.004577 | 122.3465 | 0.050354 | -0.21515 | 122.6028 | 122.5754 | 122.4976 | 0.22888 | 0.15106 | 0.10071 | -0.004577 | 0.25635 | 0.11444 | 0.19226 | 0.37994 | 122.5708 | 122.7264 | -0.29755 | -0.32959 | 122.374 | 122.4609 | 122.3557 | 122.4518
1296.1875 | 122.7722 | -122.5296 | 0.17395 | -0.17563 | -0.0028411 | 0.020486 | 0.017053 | -0.00032902 | 0.002978 | 0.00054465 | -0.068481 | 0.035748 | 0.015522 | 0.0040182 | 0.012542 | -0.00055747 | -0.0043665 | -0.10529 | 0.07782 | -0.086975 | -0.091553 | 0.036621 | -0.10529 | -0.004578 | 0.004578 | 0.23346 | -0.1236 | -0.009155 | 0.07782 | 0.004578 | 0.091553 | 122.4426 | -0.09613 | -0.2655 | 122.5662 | 122.525 | 122.4243 | 0.082397 | -0.018311 | 122.406 | 0.059509 | -0.1831 | 122.6074 | 122.6212 | 122.5342 | 0.21515 | 0.12817 | 0.1236 | -0.004578 | 0.20142 | 0.11444 | 0.16479 | 0.35706 | 122.6074 | 122.7631 | -0.26092 | -0.29755 | 122.438 | 122.5204 | 122.4243 | 122.5342
1297.9062 | 122.7585 | -122.5433 | 0.21057 | -0.10696 | -0.0028411 | 0.019846 | 0.016199 | -0.0050286 | -0.0015082 | 0.003749 | 0.016968 | 0.03532 | 0.017017 | -0.00089503 | 0.013396 | -0.0065391 | -0.00094854 | -0.11902 | 0.07782 | -0.091553 | -0.091553 | 0.036621 | -0.086975 | 0.013733 | -0.041199 | 0.23346 | -0.13275 | -0.045776 | 0.073242 | -0.004578 | 0.045776 | 122.4518 | -0.13275 | -0.30212 | 122.58 | 122.5571 | 122.4564 | 0.10529 | 0.004578 | 122.4106 | 0.022888 | -0.25635 | 122.6166 | 122.5891 | 122.5388 | 0.17853 | 0.12817 | 0.12817 | 0 | 0.20599 | 0.086975 | 0.16937 | 0.36621 | 122.6212 | 122.7768 | -0.30212 | -0.34332 | 122.4518 | 122.4976 | 122.4243 | 122.5021
1299.625 | 122.7768 | -122.5204 | 0.17853 | -0.099335 | -0.0022003 | 0.019632 | 0.015985 | -0.003106 | -0.0015082 | -0.0011642 | 0.010864 | 0.033398 | 0.017872 | -0.0013224 | 0.013823 | -0.0022665 | -9.3938e-05 | -0.10071 | 0.059509 | -0.09613 | -0.068665 | 0.073242 | -0.064087 | 0.036621 | -0.022888 | 0.21973 | -0.13275 | -0.032043 | 0.09613 | 0.018311 | 0.068665 | 122.4243 | -0.11902 | -0.24719 | 122.5937 | 122.5571 | 122.4564 | 0.13275 | 0.032043 | 122.3877 | 0.041199 | -0.21057 | 122.6166 | 122.5891 | 122.5388 | 0.20142 | 0.15106 | 0.16937 | 0.027465 | 0.22888 | 0.10071 | 0.15564 | 0.35248 | 122.58 | 122.7402 | -0.27466 | -0.31128 | 122.4518 | 122.4884 | 122.4197 | 122.4976
1301.3438 | 122.8775 | -122.4747 | 0.16022 | -0.168 | -0.00091854 | 0.020914 | 0.015558 | 0.0035162 | 0.0021234 | -0.001378 | -0.0013428 | 0.03532 | 0.017658 | 0.0020956 | 0.012755 | -0.0016257 | 0.0024695 | -0.064087 | 0.041199 | -0.045776 | 0.009155 | 0.11902 | -0.050354 | 0.059509 | 0.09613 | 0.17395 | -0.091553 | 0.068665 | 0.17853 | 0.10071 | 0.16022 | 122.4289 | -0.11902 | -0.15106 | 122.5937 | 122.5342 | 122.4243 | 0.10528 | -0.004578 | 122.3831 | 0.013733 | -0.091552 | 122.6532 | 122.6349 | 122.5754 | 0.25177 | 0.19226 | 0.16479 | 0.054931 | 0.27008 | 0.16022 | 0.086975 | 0.2655 | 122.5159 | 122.6486 | -0.20599 | -0.25177 | 122.4838 | 122.5433 | 122.4106 | 122.5708
1303.0625 | 122.7631 | -122.5296 | 0.18768 | -0.11459 | -0.0054047 | 0.020059 | 0.017908 | -0.001397 | 0.002337 | -0.00073695 | -0.053223 | 0.034039 | 0.018299 | 0.0046592 | 0.014037 | -0.0016257 | -0.0020165 | -0.16479 | 0.10529 | -0.11444 | -0.14191 | -0.022888 | -0.12817 | -0.032043 | -0.086975 | 0.23346 | -0.14648 | -0.059509 | 0.059509 | -0.009155 | 0.045776 | 122.4152 | -0.082397 | -0.32959 | 122.5067 | 122.4976 | 122.4014 | 0.082398 | -0.013733 | 122.3831 | 0.045776 | -0.24719 | 122.5891 | 122.5754 | 122.5204 | 0.19226 | 0.13733 | 0.091553 | -0.027466 | 0.20599 | 0.086975 | 0.21973 | 0.37994 | 122.6349 | 122.7631 | -0.30212 | -0.33417 | 122.3877 | 122.4701 | 122.3648 | 122.4426
1304.7344 | 122.7539 | -122.5616 | 0.17853 | -0.168 | -0.0039093 | 0.020059 | 0.014063 | -0.00032902 | 0.0031916 | 0.0013992 | 0.010864 | 0.035107 | 0.018726 | 0.0038046 | 0.012755 | -0.0052573 | -0.0011621 | -0.13733 | 0.07782 | -0.11444 | -0.11902 | -0.004578 | -0.13733 | -0.018311 | -0.073242 | 0.23346 | -0.15564 | -0.073242 | 0.064087 | -0.027466 | 0.036621 | 122.4472 | -0.10071 | -0.29755 | 122.5571 | 122.5433 | 122.4243 | 0.09613 | -0.022888 | 122.406 | 0.054931 | -0.25177 | 122.6257 | 122.5983 | 122.5342 | 0.19226 | 0.12817 | 0.10986 | -0.004578 | 0.21973 | 0.082398 | 0.19226 | 0.3891 | 122.6395 | 122.7951 | -0.29297 | -0.33417 | 122.4426 | 122.4884 | 122.4243 | 122.4884
1306.4219 | 122.7539 | -122.5204 | 0.1831 | -0.12985 | -0.0030547 | 0.019205 | 0.015558 | 0.00138 | 0.004046 | 0.00033105 | -0.03186 | 0.035107 | 0.017231 | 0.0023092 | 0.013183 | -0.0029075 | 0.00033326 | -0.16479 | 0.09613 | -0.11444 | -0.12817 | -0.022888 | -0.14191 | -0.041199 | -0.091553 | 0.22888 | -0.14648 | -0.059509 | 0.059509 | -0.009155 | 0.050354 | 122.406 | -0.086975 | -0.31128 | 122.4976 | 122.4792 | 122.3785 | 0.073242 | -0.027466 | 122.374 | 0.045777 | -0.24261 | 122.58 | 122.5708 | 122.5113 | 0.19684 | 0.13733 | 0.091553 | -0.013733 | 0.20599 | 0.086975 | 0.21057 | 0.37537 | 122.6166 | 122.7493 | -0.29755 | -0.32959 | 122.3923 | 122.4609 | 122.3557 | 122.4289
1308.1094 | 122.7676 | -122.5159 | 0.18768 | -0.16037 | -0.0011321 | 0.0207 | 0.017053 | 9.818e-05 | 0.001269 | 0.0016128 | -0.080688 | 0.035107 | 0.015949 | -4.063e-05 | 0.011901 | -0.0016257 | -0.00030754 | -0.10529 | 0.07782 | -0.09613 | -0.10071 | 0.027466 | -0.11902 | -0.022888 | -0.013733 | 0.23804 | -0.13733 | -0.018311 | 0.073242 | -0.018311 | 0.073242 | 122.4197 | -0.10986 | -0.28839 | 122.5433 | 122.493 | 122.3969 | 0.073242 | -0.022889 | 122.3785 | 0.050354 | -0.20599 | 122.5891 | 122.5891 | 122.4976 | 0.21057 | 0.11902 | 0.1236 | -0.004578 | 0.21057 | 0.11902 | 0.17395 | 0.37537 | 122.5937 | 122.7539 | -0.28381 | -0.32501 | 122.4152 | 122.4976 | 122.4106 | 122.5021
1309.7812 | 122.7997 | -122.5388 | 0.16937 | -0.16037 | 0.00036326 | 0.019632 | 0.018762 | 0.0022346 | 0.0016962 | -0.00073695 | -0.047119 | 0.036602 | 0.017872 | 0.0061546 | 0.015746 | -0.0016257 | -0.0054345 | -0.10529 | 0.059509 | -0.09613 | -0.07782 | 0.041199 | -0.11444 | 0.009155 | 0 | 0.20142 | -0.12817 | -0.009155 | 0.082397 | 0.013733 | 0.086975 | 122.4426 | -0.10986 | -0.24719 | 122.58 | 122.5479 | 122.4243 | 0.10528 | -0.018311 | 122.4106 | 0.032043 | -0.17853 | 122.6212 | 122.6257 | 122.5525 | 0.21515 | 0.14191 | 0.13733 | 0.01831 | 0.21057 | 0.11902 | 0.15564 | 0.32959 | 122.5983 | 122.7402 | -0.2655 | -0.29755 | 122.4609 | 122.5296 | 122.4335 | 122.5388
1311.4688 | 122.7539 | -122.5616 | 0.19684 | -0.15274 | -0.0041229 | 0.018777 | 0.01449 | -0.002038 | 0.00041439 | 0.00075845 | 0.026123 | 0.036389 | 0.015308 | -0.00068143 | 0.014678 | -0.0041891 | -0.0035119 | -0.15564 | 0.082397 | -0.09613 | -0.12817 | 0 | -0.12817 | -0.018311 | -0.059509 | 0.23804 | -0.14191 | -0.082397 | 0.059509 | -0.022888 | 0.041199 | 122.4655 | -0.11444 | -0.32501 | 122.5616 | 122.5433 | 122.4335 | 0.077819 | -0.032044 | 122.4197 | 0.041199 | -0.27924 | 122.6212 | 122.6028 | 122.5388 | 0.18311 | 0.11902 | 0.09613 | -0.032044 | 0.20142 | 0.05951 | 0.17853 | 0.37994 | 122.644 | 122.7997 | -0.29297 | -0.33875 | 122.4335 | 122.4792 | 122.406 | 122.5021
1313.1719 | 122.8638 | -122.4655 | 0.16479 | -0.13748 | -0.0024139 | 0.020273 | 0.016626 | -0.0018244 | 0.0019098 | 0.0011856 | -0.050171 | 0.034893 | 0.017872 | 0.0033774 | 0.010833 | -0.0035483 | 0.00097406 | -0.11444 | 0.073242 | -0.082397 | -0.064087 | 0.045776 | -0.10071 | 0.018311 | 0.050354 | 0.19684 | -0.1236 | 0.068665 | 0.16022 | 0.064087 | 0.16022 | 122.3831 | -0.091553 | -0.22888 | 122.5113 | 122.4838 | 122.3648 | 0.10071 | -0.018311 | 122.3419 | 0.032043 | -0.09613 | 122.6257 | 122.6257 | 122.5296 | 0.28381 | 0.18768 | 0.12817 | 0.01831 | 0.28381 | 0.19226 | 0.15564 | 0.32043 | 122.5388 | 122.6624 | -0.24719 | -0.28839 | 122.4014 | 122.5342 | 122.3511 | 122.5159
1314.8438 | 122.905 | -122.4838 | 0.16937 | -0.12985 | -0.0034821 | 0.018137 | 0.013849 | -0.00032902 | -0.0012946 | -0.00030975 | 0.065796 | 0.036389 | 0.017658 | -0.0030312 | 0.014251 | -0.0048301 | -0.00052114 | -0.07782 | 0.041199 | -0.082397 | -0.027466 | 0.10986 | -0.009155 | 0.10529 | 0.10986 | 0.16937 | -0.10071 | 0.064087 | 0.20599 | 0.1236 | 0.16937 | 122.4014 | -0.12817 | -0.19684 | 122.5937 | 122.5891 | 122.4747 | 0.18768 | 0.073242 | 122.3831 | 0 | -0.10529 | 122.6898 | 122.6532 | 122.6074 | 0.27008 | 0.2243 | 0.19226 | 0.054931 | 0.3067 | 0.1648 | 0.1236 | 0.27008 | 122.525 | 122.6532 | -0.25177 | -0.27008 | 122.4564 | 122.5479 | 122.406 | 122.5937
1316.5156 | 122.7493 | -122.5479 | 0.18768 | -0.15274 | -0.00091854 | 0.018777 | 0.017267 | -0.0022516 | 0.002978 | -0.00030975 | -0.068481 | 0.03532 | 0.01659 | -0.00089503 | 0.012969 | -0.0026939 | -0.0052209 | -0.13275 | 0.086975 | -0.10071 | -0.14191 | -0.041199 | -0.18768 | -0.068665 | -0.10529 | 0.21973 | -0.12817 | -0.073242 | 0 | -0.07782 | 0.027466 | 122.4472 | -0.10071 | -0.32959 | 122.5067 | 122.4792 | 122.3602 | 0.032043 | -0.086975 | 122.4197 | 0.032044 | -0.26092 | 122.5479 | 122.5754 | 122.4701 | 0.15564 | 0.050354 | 0.059509 | -0.041199 | 0.12817 | 0.054932 | 0.18768 | 0.3479 | 122.6349 | 122.7676 | -0.28839 | -0.31586 | 122.406 | 122.4747 | 122.4152 | 122.4426
1318.2031 | 122.8912 | -122.4884 | 0.15106 | -0.12222 | -0.0026275 | 0.019205 | 0.012354 | 0.0035162 | 0.00084159 | 0.0011856 | 0.059692 | 0.03532 | 0.017231 | -0.0021768 | 0.014892 | -0.0056845 | 0.00076046 | -0.10529 | 0.059509 | -0.068665 | -0.036621 | 0.091553 | -0.022888 | 0.10071 | 0.082397 | 0.1831 | -0.10071 | 0.064087 | 0.19684 | 0.13275 | 0.15564 | 122.4197 | -0.091553 | -0.18768 | 122.58 | 122.5891 | 122.4655 | 0.16937 | 0.045777 | 122.3877 | 0.032043 | -0.086975 | 122.6852 | 122.644 | 122.6212 | 0.25635 | 0.23346 | 0.16022 | 0.032044 | 0.29755 | 0.1648 | 0.12817 | 0.28381 | 122.5479 | 122.6715 | -0.21973 | -0.25177 | 122.4518 | 122.5525 | 122.3831 | 122.5708
1319.9219 | 122.8134 | -122.5021 | 0.1831 | -0.12222 | -0.0032683 | 0.019205 | 0.018122 | 0.0024482 | -0.00065361 | 0.0033218 | -0.062378 | 0.034252 | 0.017445 | 0.0076498 | 0.012969 | -0.0039755 | -0.00052114 | -0.10529 | 0.091553 | -0.09613 | -0.073242 | 0.022888 | -0.09613 | 0 | 0.018311 | 0.2243 | -0.1236 | 0.004578 | 0.10986 | 0.013733 | 0.10529 | 122.406 | -0.091552 | -0.25635 | 122.525 | 122.5021 | 122.406 | 0.09613 | 0 | 122.3785 | 0.041199 | -0.17853 | 122.612 | 122.6074 | 122.5159 | 0.22888 | 0.13733 | 0.11902 | 0.022888 | 0.23346 | 0.12817 | 0.18768 | 0.3479 | 122.5937 | 122.7264 | -0.27924 | -0.3067 | 122.4289 | 122.5067 | 122.3968 | 122.5204
1321.5938 | 122.8867 | -122.4884 | 0.14648 | -0.20615 | -0.0013457 | 0.019418 | 0.017908 | -0.00032902 | 0.0016962 | -9.6154e-05 | -0.037964 | 0.03532 | 0.014667 | 0.0063682 | 0.01361 | -0.0024803 | 0.0018287 | -0.059509 | 0.054932 | -0.068665 | -0.018311 | 0.10529 | -0.050354 | 0.050354 | 0.07782 | 0.1831 | -0.10071 | 0.073242 | 0.17853 | 0.091553 | 0.16022 | 122.4197 | -0.091552 | -0.16479 | 122.5937 | 122.5388 | 122.438 | 0.11902 | 0.018311 | 122.3877 | 0.036621 | -0.073242 | 122.6669 | 122.6486 | 122.58 | 0.26093 | 0.19226 | 0.17395 | 0.050354 | 0.27924 | 0.17395 | 0.1236 | 0.28381 | 122.5433 | 122.6715 | -0.21515 | -0.24719 | 122.4701 | 122.5616 | 122.4289 | 122.5662
1323.2656 | 122.7859 | -122.5708 | 0.17853 | -0.17563 | 0.00014946 | 0.021555 | 0.021112 | 0.00031198 | 0.002978 | 0.00075845 | -0.077637 | 0.035748 | 0.017658 | 0.0053 | 0.013183 | -0.0018393 | -0.0013757 | -0.13733 | 0.10529 | -0.11444 | -0.14191 | -0.050354 | -0.18768 | -0.050354 | -0.068665 | 0.21515 | -0.14191 | -0.050354 | 0.050354 | -0.050354 | 0.059509 | 122.4564 | -0.073242 | -0.32044 | 122.5204 | 122.5204 | 122.3831 | 0.064087 | -0.073242 | 122.4289 | 0.036621 | -0.22888 | 122.6212 | 122.6303 | 122.5204 | 0.20142 | 0.091553 | 0.064087 | -0.027466 | 0.19226 | 0.091553 | 0.21973 | 0.35706 | 122.6761 | 122.7859 | -0.29297 | -0.32044 | 122.4289 | 122.5204 | 122.4335 | 122.5021
1324.9531 | 122.8775 | -122.4976 | 0.19226 | -0.168 | -0.0030547 | 0.018991 | 0.015344 | -0.0035334 | 0.0010554 | 0.0035354 | 0.059692 | 0.034466 | 0.017017 | -0.0011086 | 0.014678 | -0.0041891 | -0.0037255 | -0.12817 | 0.054932 | -0.064087 | -0.068665 | 0.059509 | -0.073242 | 0.059509 | 0.004578 | 0.20599 | -0.12817 | 0.013733 | 0.14648 | 0.064087 | 0.12817 | 122.4335 | -0.13733 | -0.26093 | 122.5571 | 122.5571 | 122.4243 | 0.1236 | -0.009155 | 122.3694 | 0.013733 | -0.17853 | 122.644 | 122.6257 | 122.5616 | 0.25635 | 0.19226 | 0.1236 | -0.004578 | 0.27466 | 0.14191 | 0.11902 | 0.33417 | 122.5525 | 122.7036 | -0.25635 | -0.32044 | 122.4289 | 122.5113 | 122.3694 | 122.5021
1326.6562 | 122.8912 | -122.5067 | 0.16479 | -0.19852 | -0.00070494 | 0.020914 | 0.018762 | 0.0011664 | 0.0010554 | 0.00097205 | -0.037964 | 0.035748 | 0.01659 | 0.0072226 | 0.013396 | -0.0058981 | -0.0022301 | -0.086975 | 0.050354 | -0.068665 | -0.032043 | 0.050354 | -0.073242 | 0.045776 | 0.064087 | 0.17853 | -0.11444 | 0.07782 | 0.17853 | 0.068665 | 0.1831 | 122.438 | -0.11444 | -0.19684 | 122.5571 | 122.5525 | 122.4335 | 0.11444 | -0.004577 | 122.3923 | 0.013733 | -0.086975 | 122.6852 | 122.6898 | 122.5754 | 0.29755 | 0.18311 | 0.11902 | 0.036622 | 0.29297 | 0.19226 | 0.11902 | 0.29297 | 122.5571 | 122.6852 | -0.23346 | -0.27924 | 122.4747 | 122.5845 | 122.4197 | 122.5708
1328.3281 | 122.8729 | -122.5159 | 0.1831 | -0.13748 | -0.0013457 | 0.018991 | 0.017908 | 0.0020208 | 0.0021234 | 0.002681 | -0.053223 | 0.035107 | 0.017658 | 0.0016684 | 0.011901 | -0.0035483 | 0.0031103 | -0.12817 | 0.082397 | -0.091553 | -0.09613 | 0.004578 | -0.13733 | -0.013733 | 0.013733 | 0.1831 | -0.11444 | 0.045776 | 0.13275 | 0.050354 | 0.14648 | 122.4243 | -0.10071 | -0.27924 | 122.5204 | 122.5021 | 122.3785 | 0.07782 | -0.045776 | 122.4014 | 0 | -0.13733 | 122.6486 | 122.6624 | 122.5662 | 0.26093 | 0.16479 | 0.096131 | -0.004577 | 0.24719 | 0.16022 | 0.17395 | 0.29755 | 122.5983 | 122.699 | -0.27466 | -0.29755 | 122.4197 | 122.5616 | 122.3877 | 122.5296
1330 | 122.8363 | -122.5342 | 0.17853 | -0.16037 | -0.0019867 | 0.021768 | 0.019831 | -0.00054262 | 0.0016962 | -0.001378 | -0.056274 | 0.035107 | 0.017445 | 0.0023092 | 0.012755 | -0.0044029 | -0.0028711 | -0.14191 | 0.10071 | -0.10986 | -0.11902 | -0.018311 | -0.15564 | -0.022888 | -0.013733 | 0.20599 | -0.11444 | 0.004578 | 0.091553 | 0.004578 | 0.11902 | 122.4243 | -0.07782 | -0.29755 | 122.5159 | 122.5113 | 122.3785 | 0.086975 | -0.045777 | 122.4197 | 0.027466 | -0.17395 | 122.6257 | 122.6532 | 122.5388 | 0.23346 | 0.11902 | 0.091552 | -0.009156 | 0.20599 | 0.11902 | 0.21057 | 0.32044 | 122.6349 | 122.7402 | -0.28839 | -0.29297 | 122.4152 | 122.5388 | 122.3923 | 122.5204
1331.6875 | 122.8134 | -122.525 | 0.16937 | -0.11459 | -0.0047637 | 0.017923 | 0.017694 | -0.001397 | 0.001269 | 0.0035354 | -0.019653 | 0.03532 | 0.017872 | 0.0033774 | 0.013183 | -0.0011985 | -0.0020165 | -0.1236 | 0.09613 | -0.10071 | -0.10071 | -0.004578 | -0.10986 | -0.009155 | -0.036621 | 0.23804 | -0.14648 | -0.009155 | 0.10529 | 0.013733 | 0.091553 | 122.4243 | -0.073243 | -0.27008 | 122.5204 | 122.5159 | 122.4152 | 0.091553 | -0.009155 | 122.3785 | 0.068664 | -0.17853 | 122.6303 | 122.6166 | 122.5388 | 0.23804 | 0.16022 | 0.09613 | 0 | 0.25177 | 0.13733 | 0.19684 | 0.38452 | 122.6212 | 122.7631 | -0.27008 | -0.31586 | 122.4243 | 122.5159 | 122.4014 | 122.4884
1333.3594 | 122.85 | -122.5342 | 0.16937 | -0.14511 | -0.0032683 | 0.01835 | 0.014063 | -0.00054262 | 0.00020079 | 0.00054465 | 0.044434 | 0.03532 | 0.016376 | -0.0017496 | 0.011901 | -0.0050437 | 0.00054686 | -0.086975 | 0.050354 | -0.059509 | -0.022888 | 0.10986 | -0.018311 | 0.07782 | 0.050354 | 0.19684 | -0.10529 | 0.022888 | 0.16022 | 0.068665 | 0.11902 | 122.4747 | -0.11902 | -0.19226 | 122.644 | 122.612 | 122.5159 | 0.13733 | 0.041198 | 122.4289 | 0.027465 | -0.14649 | 122.6944 | 122.6532 | 122.6028 | 0.22431 | 0.17395 | 0.16937 | 0.036621 | 0.2655 | 0.12817 | 0.10986 | 0.30212 | 122.5845 | 122.731 | -0.22888 | -0.27466 | 122.5113 | 122.5571 | 122.4472 | 122.5845
1335.0469 | 122.9141 | -122.4884 | 0.15564 | -0.168 | -0.0030547 | 0.019418 | 0.015772 | -0.0028924 | -0.00022641 | 0.0022536 | 0.026123 | 0.033825 | 0.016163 | 0.0065818 | 0.012969 | -0.0052573 | -0.0015893 | -0.068665 | 0.041199 | -0.059509 | -0.022888 | 0.15106 | 0 | 0.10071 | 0.10529 | 0.19684 | -0.09613 | 0.068665 | 0.21057 | 0.12817 | 0.15106 | 122.4289 | -0.11444 | -0.17853 | 122.6395 | 122.5891 | 122.4884 | 0.16022 | 0.059509 | 122.3923 | 0.041198 | -0.086975 | 122.699 | 122.6395 | 122.6166 | 0.24719 | 0.2243 | 0.21057 | 0.036621 | 0.3067 | 0.16479 | 0.10071 | 0.29297 | 122.5296 | 122.6852 | -0.21515 | -0.25177 | 122.4655 | 122.5571 | 122.4197 | 122.5937
1336.75 | 122.8043 | -122.5159 | 0.19684 | -0.11459 | -0.00027774 | 0.020273 | 0.017694 | -0.003106 | 0.0016962 | 0.00204 | -0.077637 | 0.036602 | 0.016163 | 0.0053 | 0.013396 | -0.0048301 | 0.00076046 | -0.082397 | 0.086975 | -0.11902 | -0.059509 | 0.022888 | -0.091553 | 0.004578 | 0.027466 | 0.21973 | -0.13275 | 0.009155 | 0.09613 | 0.004578 | 0.10071 | 122.3969 | -0.10986 | -0.25635 | 122.5388 | 122.5204 | 122.4243 | 0.1236 | 0.027466 | 122.3831 | 0.022889 | -0.18768 | 122.612 | 122.6166 | 122.5204 | 0.23346 | 0.13733 | 0.14191 | 0.05951 | 0.22888 | 0.14191 | 0.20599 | 0.35248 | 122.6028 | 122.7356 | -0.31586 | -0.32959 | 122.4564 | 122.525 | 122.4335 | 122.5433
1338.4688 | 122.8958 | -122.5296 | 0.17395 | -0.17563 | -0.0051909 | 0.019632 | 0.013208 | -0.003747 | 0.0019098 | -0.0018052 | 0.03833 | 0.03532 | 0.016163 | -0.0028176 | 0.014251 | -0.0061117 | -9.3938e-05 | -0.086975 | 0.050354 | -0.059509 | 0 | 0.13275 | 0 | 0.09613 | 0.082397 | 0.18768 | -0.086975 | 0.050354 | 0.18768 | 0.10529 | 0.15106 | 122.4701 | -0.1236 | -0.17395 | 122.6624 | 122.6257 | 122.5296 | 0.15564 | 0.059509 | 122.4426 | 0.013733 | -0.1236 | 122.7173 | 122.6807 | 122.6349 | 0.23804 | 0.19226 | 0.19226 | 0.059509 | 0.27466 | 0.13733 | 0.10986 | 0.27466 | 122.58 | 122.7173 | -0.23346 | -0.26092 | 122.5296 | 122.58 | 122.4426 | 122.612
1340.1406 | 122.8958 | -122.525 | 0.15564 | -0.17563 | -0.0030547 | 0.0207 | 0.015344 | 0.00052558 | -0.00065361 | 0.0033218 | 0.071899 | 0.034466 | 0.017872 | -0.0049538 | 0.012969 | -0.0052573 | -0.00052114 | -0.1236 | 0.054932 | -0.064087 | -0.054932 | 0.073242 | -0.045776 | 0.064087 | 0.036621 | 0.20142 | -0.10986 | 0.064087 | 0.17395 | 0.091553 | 0.14191 | 122.4609 | -0.10071 | -0.21057 | 122.5983 | 122.5891 | 122.4792 | 0.12817 | 0.018311 | 122.4152 | 0.045776 | -0.091553 | 122.699 | 122.6669 | 122.6166 | 0.25177 | 0.20142 | 0.13733 | 0.009155 | 0.28381 | 0.17395 | 0.11902 | 0.31128 | 122.58 | 122.7264 | -0.21973 | -0.2655 | 122.4701 | 122.5891 | 122.4014 | 122.5616
1341.8438 | 122.9233 | -122.5113 | 0.15564 | -0.17563 | -0.0047637 | 0.019846 | 0.017053 | -0.0033196 | 0.00062799 | -0.0018052 | 0.02002 | 0.034466 | 0.017445 | 0.0059408 | 0.011474 | -0.0054709 | 0.0011877 | -0.07782 | 0.041199 | -0.064087 | 0.004578 | 0.15564 | -0.004578 | 0.10986 | 0.1236 | 0.17395 | -0.10071 | 0.068665 | 0.21057 | 0.1236 | 0.15564 | 122.4472 | -0.11444 | -0.15106 | 122.6669 | 122.6212 | 122.5067 | 0.17395 | 0.059509 | 122.4106 | 0.01831 | -0.086975 | 122.7219 | 122.6669 | 122.6349 | 0.25635 | 0.2243 | 0.21973 | 0.068665 | 0.31128 | 0.16937 | 0.10529 | 0.27466 | 122.5525 | 122.6852 | -0.21973 | -0.25635 | 122.5159 | 122.58 | 122.4335 | 122.6349
1343.5781 | 122.9095 | -122.4792 | 0.16937 | -0.20615 | -0.0013457 | 0.0207 | 0.017908 | 0.00095278 | 0.0027644 | 0.0013992 | -0.044067 | 0.03468 | 0.016376 | 0.0063682 | 0.010833 | -0.0020529 | -0.0037255 | -0.064087 | 0.045776 | -0.064087 | -0.022888 | 0.11444 | -0.059509 | 0.045776 | 0.09613 | 0.17853 | -0.09613 | 0.091553 | 0.1831 | 0.091553 | 0.16479 | 122.4152 | -0.1236 | -0.19226 | 122.5937 | 122.525 | 122.4197 | 0.10986 | 0.004578 | 122.3831 | 0.009155 | -0.07782 | 122.6624 | 122.644 | 122.5708 | 0.26092 | 0.18768 | 0.17853 | 0.041199 | 0.27924 | 0.18768 | 0.10986 | 0.27466 | 122.525 | 122.6578 | -0.23346 | -0.2655 | 122.4564 | 122.5708 | 122.4152 | 122.5754
1345.25 | 122.8546 | -122.5479 | 0.17853 | -0.168 | -0.0019867 | 0.019418 | 0.019403 | -0.0018244 | 0.002337 | 0.00033105 | -0.074585 | 0.033398 | 0.015736 | 0.0072226 | 0.011687 | -0.0039755 | 0.0033241 | -0.12817 | 0.086975 | -0.10071 | -0.10529 | -0.022888 | -0.16022 | -0.041199 | -0.022888 | 0.20599 | -0.12817 | 0.009155 | 0.082397 | -0.009155 | 0.09613 | 122.4472 | -0.091553 | -0.28381 | 122.525 | 122.5067 | 122.3877 | 0.059509 | -0.059509 | 122.4197 | 0.027466 | -0.16937 | 122.6303 | 122.644 | 122.5388 | 0.2243 | 0.11902 | 0.07782 | -0.004578 | 0.21057 | 0.13733 | 0.18768 | 0.33417 | 122.6349 | 122.7539 | -0.27924 | -0.3067 | 122.4426 | 122.5571 | 122.4197 | 122.525
1346.9375 | 122.7859 | -122.5662 | 0.17853 | -0.10696 | -0.00091854 | 0.021127 | 0.018976 | 9.818e-05 | 0.00062799 | 0.00033105 | -0.080688 | 0.035534 | 0.018299 | 0.0023092 | 0.014464 | -0.0011985 | -0.0013757 | -0.10986 | 0.068665 | -0.091553 | -0.091553 | 0 | -0.12817 | -0.036621 | -0.018311 | 0.21515 | -0.13275 | -0.022888 | 0.059509 | -0.045776 | 0.068665 | 122.4747 | -0.10986 | -0.27008 | 122.5662 | 122.5296 | 122.438 | 0.054932 | -0.036621 | 122.4335 | 0.036621 | -0.20142 | 122.6257 | 122.6349 | 122.5204 | 0.20142 | 0.086975 | 0.091553 | 0 | 0.19226 | 0.10986 | 0.16022 | 0.3479 | 122.6349 | 122.7814 | -0.27008 | -0.31128 | 122.4747 | 122.5433 | 122.4564 | 122.5479
1348.6875 | 122.7905 | -122.58 | 0.19226 | -0.16037 | -0.0030547 | 0.017709 | 0.015558 | -0.00054262 | 0.0010554 | 0.00054465 | 0.010864 | 0.036389 | 0.017872 | 0.0061546 | 0.015105 | -0.0046165 | -0.0015893 | -0.17395 | 0.10529 | -0.086975 | -0.13275 | -0.013733 | -0.11902 | -0.013733 | -0.073242 | 0.2243 | -0.1236 | -0.045776 | 0.064087 | -0.018311 | 0.054932 | 122.493 | -0.086975 | -0.32501 | 122.5662 | 122.5662 | 122.4609 | 0.073242 | -0.032044 | 122.4564 | 0.032043 | -0.23804 | 122.644 | 122.6349 | 122.5616 | 0.17853 | 0.10528 | 0.073242 | -0.045776 | 0.18768 | 0.07782 | 0.19226 | 0.3479 | 122.6852 | 122.8043 | -0.27924 | -0.31586 | 122.4472 | 122.5342 | 122.406 | 122.5067
1350.3906 | 122.8958 | -122.5021 | 0.16022 | -0.20615 | 0.0010041 | 0.0207 | 0.016626 | 0.00095278 | 0.0019098 | -0.00052335 | -0.01355 | 0.034893 | 0.017231 | 0.0016684 | 0.013823 | -0.0039755 | -0.0026575 | -0.054932 | 0.050354 | -0.054932 | -0.004578 | 0.10986 | -0.054932 | 0.07782 | 0.091553 | 0.18768 | -0.10071 | 0.082397 | 0.18768 | 0.09613 | 0.16022 | 122.4472 | -0.10986 | -0.16479 | 122.612 | 122.58 | 122.4472 | 0.13275 | 0 | 122.4014 | 0.027466 | -0.07782 | 122.6898 | 122.6624 | 122.5983 | 0.26093 | 0.19684 | 0.16479 | 0.050354 | 0.28839 | 0.18311 | 0.10529 | 0.28839 | 122.5525 | 122.6898 | -0.21515 | -0.26093 | 122.4976 | 122.5845 | 122.4472 | 122.5937
1352.1562 | 122.8775 | -122.5204 | 0.15564 | -0.18326 | -0.0026275 | 0.021555 | 0.017694 | -0.002038 | 0.0016962 | 0.00054465 | 0.0047608 | 0.033398 | 0.014027 | -4.063e-05 | 0.013183 | -0.0033347 | -0.0032983 | -0.091553 | 0.045776 | -0.064087 | -0.018311 | 0.10071 | -0.054932 | 0.050354 | 0.09613 | 0.19226 | -0.11444 | 0.041199 | 0.14648 | 0.064087 | 0.14191 | 122.4564 | -0.10986 | -0.17395 | 122.6212 | 122.5708 | 122.4655 | 0.11444 | 0.009155 | 122.406 | 0.036621 | -0.11444 | 122.6669 | 122.6624 | 122.5845 | 0.25635 | 0.17853 | 0.1648 | 0.045776 | 0.26093 | 0.15564 | 0.10986 | 0.3067 | 122.5662 | 122.7127 | -0.21973 | -0.27008 | 122.5021 | 122.5616 | 122.4289 | 122.6166
1353.9062 | 122.8683 | -122.5342 | 0.15564 | -0.21378 | -0.00091854 | 0.019846 | 0.017694 | 0.00138 | 0.0010554 | -0.00030975 | 0.02002 | 0.035961 | 0.019581 | -0.00089503 | 0.014251 | -0.0037619 | -0.0030847 | -0.091553 | 0.064087 | -0.054932 | -0.013733 | 0.11444 | -0.068665 | 0.036621 | 0.068665 | 0.19226 | -0.10071 | 0.041199 | 0.13733 | 0.054932 | 0.10986 | 122.4792 | -0.091553 | -0.16937 | 122.6486 | 122.5708 | 122.4655 | 0.091553 | -0.013733 | 122.4335 | 0.036621 | -0.11444 | 122.6715 | 122.644 | 122.5891 | 0.21057 | 0.15564 | 0.16937 | 0.041199 | 0.23804 | 0.14191 | 0.11902 | 0.29297 | 122.5983 | 122.7264 | -0.21057 | -0.25635 | 122.5204 | 122.5754 | 122.4426 | 122.6028
1355.5781 | 122.8088 | -122.58 | 0.19684 | -0.12985 | -0.0030547 | 0.018137 | 0.01684 | -0.0026788 | -0.001081 | 0.0018264 | -0.053223 | 0.035961 | 0.018085 | 0.0078634 | 0.012755 | -0.0033347 | -0.0011621 | -0.15106 | 0.09613 | -0.10529 | -0.13275 | -0.032043 | -0.14191 | -0.032043 | -0.068665 | 0.2243 | -0.13733 | -0.045776 | 0.07782 | -0.004578 | 0.07782 | 122.4747 | -0.10071 | -0.32959 | 122.5479 | 122.5479 | 122.438 | 0.073243 | -0.036621 | 122.4426 | 0.027466 | -0.24261 | 122.6578 | 122.6578 | 122.5754 | 0.21515 | 0.13275 | 0.073243 | -0.027465 | 0.21515 | 0.091553 | 0.20142 | 0.36163 | 122.6761 | 122.8043 | -0.30212 | -0.33417 | 122.4472 | 122.5342 | 122.4289 | 122.5113
1357.3125 | 122.8134 | -122.5433 | 0.17853 | -0.19089 | -0.0034821 | 0.017282 | 0.014276 | -0.00075622 | -0.001081 | 0.00075845 | 0.026123 | 0.034252 | 0.016376 | -0.00089503 | 0.014464 | -0.0035483 | -0.00052114 | -0.09613 | 0.054932 | -0.059509 | -0.032043 | 0.073242 | -0.045776 | 0.041199 | 0.027466 | 0.19684 | -0.10529 | -0.027466 | 0.10986 | 0.022888 | 0.086975 | 122.4838 | -0.1236 | -0.21057 | 122.6166 | 122.5845 | 122.4976 | 0.10071 | 0.013733 | 122.438 | 0.01831 | -0.20599 | 122.6532 | 122.6303 | 122.5662 | 0.19226 | 0.12817 | 0.13275 | 0.027466 | 0.21515 | 0.07782 | 0.11444 | 0.30212 | 122.5983 | 122.7402 | -0.23804 | -0.28381 | 122.5113 | 122.5159 | 122.4472 | 122.5708
1358.9844 | 122.7676 | -122.5433 | 0.16479 | -0.14511 | 0.0012177 | 0.020914 | 0.017694 | 0.0018072 | 0.0021234 | 0.0016128 | -0.092895 | 0.03532 | 0.016163 | 0.0080772 | 0.012755 | -0.0033347 | -0.0045801 | -0.13275 | 0.09613 | -0.10986 | -0.11444 | -0.018311 | -0.16937 | -0.054932 | -0.036621 | 0.21973 | -0.13275 | -0.050354 | 0.027466 | -0.041199 | 0.068665 | 122.4335 | -0.068665 | -0.27924 | 122.525 | 122.4884 | 122.374 | 0.054931 | -0.05951 | 122.4106 | 0.054932 | -0.21515 | 122.5708 | 122.612 | 122.5021 | 0.20142 | 0.091552 | 0.091552 | -0.004578 | 0.16022 | 0.082397 | 0.20599 | 0.35248 | 122.6395 | 122.7631 | -0.27466 | -0.29755 | 122.4289 | 122.493 | 122.4106 | 122.5067
1360.7188 | 122.8271 | -122.5754 | 0.17853 | -0.14511 | -0.00027774 | 0.021555 | 0.01919 | 0.00052558 | -0.00065361 | 0.0013992 | -0.074585 | 0.035961 | 0.016163 | 0.0099998 | 0.014037 | -0.0029075 | -0.0052209 | -0.09613 | 0.07782 | -0.09613 | -0.064087 | 0.045776 | -0.10071 | 0 | 0.027466 | 0.2243 | -0.1236 | 0.022888 | 0.09613 | 0 | 0.09613 | 122.4792 | -0.10071 | -0.24261 | 122.6212 | 122.5754 | 122.4747 | 0.09613 | -0.004578 | 122.4518 | 0.045776 | -0.15564 | 122.6715 | 122.6715 | 122.5754 | 0.21973 | 0.1236 | 0.14191 | 0.032043 | 0.21973 | 0.14648 | 0.17395 | 0.3479 | 122.6532 | 122.7997 | -0.27466 | -0.30212 | 122.5113 | 122.5983 | 122.4792 | 122.6028

## Thermal Data
Fire Time | north top | north mid | north bottom | south top | south mid | south bottom
-0.1521 | 18.2242 | 18.1558 | 17.7366 | 18.0663 | 17.8723 | 17.9888
0.8479 | 18.2463 | 18.1463 | 17.7632 | 18.087 | 17.8593 | 17.9725
1.8479 | 18.7657 | 53.7732 | 18.0188 | 18.1475 | 17.8387 | 17.9795
2.8479 | 19.6845 | 114.248 | 18.3772 | 18.2408 | 17.8369 | 18.0378
3.8479 | 20.5925 | 184.8614 | 18.9654 | 18.5379 | 17.8682 | 18.1251
4.8479 | 22.1628 | 227.2802 | 19.8206 | 19.8252 | 17.9439 | 18.9014
5.8479 | 23.9425 | 301.5167 | 20.84 | 20.2352 | 18.0794 | 19.5109
6.8479 | 25.9472 | 366.969 | 21.9299 | 22.0303 | 18.844 | 20.2747
7.8479 | 27.83 | 416.4108 | 22.988 | 24.6266 | 21.163 | 21.8346
8.8479 | 30.3325 | 461.3779 | 24.216 | 28.0874 | 23.8294 | 24.5954
9.8479 | 32.0636 | 518.8523 | 25.1904 | 32.181 | 26.3666 | 27.1146
10.8479 | 33.4652 | 534.8389 | 26.0511 | 35.1764 | 29.8406 | 29.0368
11.8479 | 34.936 | 550.1456 | 27.2412 | 38.4419 | 32.883 | 33.2438
12.8479 | 36.2334 | 555.5603 | 27.9563 | 41.3097 | 35.937 | 34.8438
13.8479 | 37.1068 | 572.4979 | 28.5262 | 44.3972 | 38.6905 | 37.2313
14.8479 | 37.8426 | 575.6008 | 29.0303 | 48.5706 | 42.0497 | 39.9729
15.8479 | 38.5935 | 567.1843 | 29.4787 | 51.8513 | 45.0538 | 43.4604
16.8479 | 39.2189 | 555.9507 | 29.8463 | 54.268 | 47.488 | 45.7097
17.8479 | 39.8323 | 541.9012 | 30.2157 | 57.8002 | 49.0998 | 48.5365
18.8479 | 40.4836 | 544.1355 | 30.5726 | 60.1406 | 51.5244 | 51.0649
19.8479 | 40.9447 | 523.2871 | 30.9056 | 62.7588 | 53.7961 | 53.2363
20.8479 | 41.1753 | 511.3186 | 31.2557 | 63.7428 | 55.0336 | 54.4128
21.8479 | 41.4759 | 487.7621 | 31.5232 | 63.5551 | 57.0333 | 57.0472
22.8479 | 41.7134 | 477.2798 | 31.6374 | 66.7372 | 58.1072 | 59.3275
23.8479 | 42.0872 | 472.9115 | 31.8817 | 67.8544 | 59.2838 | 60.1448
24.8479 | 42.3229 | 458.2497 | 32.096 | 68.907 | 60.4323 | 61.3714
25.8479 | 42.5511 | 451.2044 | 32.2275 | 69.3583 | 61.8905 | 61.7516
26.8479 | 42.845 | 451.3417 | 32.3944 | 70.4205 | 62.9111 | 62.1599
27.8479 | 43.3048 | 431.7164 | 32.6316 | 71.138 | 63.8929 | 63.2241
28.8479 | 43.3719 | 424.9876 | 32.8307 | 72.5575 | 65.2886 | 64.0657
29.8479 | 43.6165 | 411.5081 | 32.9679 | 73.403 | 66.0429 | 64.6601
30.8479 | 43.8543 | 405.8568 | 33.085 | 74.3241 | 67.026 | 65.3109
31.8479 | 44.0226 | 393.899 | 33.1421 | 75.0246 | 67.891 | 65.7678
32.8479 | 44.2477 | 396.285 | 33.2237 | 75.0052 | 68.7123 | 66.4818
33.8479 | 44.4607 | 390.2703 | 33.2841 | 75.8963 | 69.378 | 66.8383
34.8479 | 44.8014 | 391.9853 | 33.3723 | 76.3822 | 69.6182 | 67.3367
35.8479 | 45.0169 | 381.5361 | 33.4037 | 76.7115 | 70.4319 | 67.6638
36.8479 | 45.3394 | 370.9636 | 33.4293 | 76.8474 | 70.9123 | 68.387
37.8479 | 45.3556 | 372.0999 | 33.5199 | 77.309 | 71.301 | 69.3346
38.8479 | 45.5809 | 381.6576 | 33.5263 | 77.5946 | 71.9764 | 69.8246
39.8479 | 45.8319 | 379.1641 | 33.4654 | 78.0857 | 72.4456 | 70.052
40.8479 | 45.9831 | 385.0951 | 33.539 | 78.5615 | 72.7412 | 70.7179
41.8479 | 46.0891 | 384.0883 | 33.4927 | 78.8449 | 72.881 | 71.1249
42.8479 | 46.2321 | 379.4517 | 33.5109 | 79.0676 | 73.2834 | 71.7012
43.8479 | 46.2779 | 382.8048 | 33.486 | 79.2976 | 73.7315 | 72.3646
44.8479 | 46.3119 | 375.8466 | 33.4205 | 79.9777 | 74.097 | 72.7524
45.8479 | 46.3051 | 385.739 | 33.3722 | 80.5241 | 74.3897 | 73.1928
46.8479 | 46.4369 | 384.14 | 33.3142 | 80.8761 | 74.7723 | 73.7119
47.8479 | 46.3519 | 383.8755 | 33.2184 | 81.3218 | 75.4662 | 74.4084
48.8479 | 46.3702 | 385.6967 | 33.2102 | 81.7565 | 76.0537 | 74.757
49.8479 | 46.4524 | 378.2458 | 33.2739 | 80.5719 | 76.137 | 75.3482
50.8479 | 46.6907 | 376.5542 | 33.2946 | 82.0975 | 76.5154 | 75.5469
51.8479 | 46.7677 | 369.9193 | 33.3576 | 82.4215 | 76.6905 | 75.8454
52.8479 | 46.9304 | 372.1389 | 33.4041 | 82.3829 | 77.0353 | 76.2446
53.8479 | 47.0977 | 376.3231 | 33.5204 | 82.778 | 77.3373 | 76.3535
54.8479 | 47.4027 | 387.7401 | 33.6034 | 83.1306 | 77.6704 | 76.7705
55.8479 | 47.5736 | 385.7012 | 33.7091 | 83.2959 | 77.9082 | 76.9322
56.8479 | 47.6434 | 382.6418 | 33.763 | 83.4253 | 77.9894 | 77.3724
57.8479 | 48.0235 | 397.3167 | 33.8379 | 80.4691 | 78.0577 | 77.7632
58.8479 | 48.1162 | 411.3126 | 33.9076 | 83.2813 | 78.5642 | 78.1486
59.8479 | 48.3098 | 419.4703 | 33.9689 | 83.7592 | 78.7747 | 78.2065
60.8479 | 48.5859 | 425.5783 | 34.1513 | 84.0732 | 79.1334 | 78.2566
61.8479 | 48.9551 | 418.2332 | 34.4263 | 83.7077 | 79.5096 | 78.2705
62.8479 | 49.2544 | 422.837 | 34.559 | 85.4169 | 80.1467 | 78.8148
63.8479 | 49.5842 | 426.5945 | 34.6434 | 86.0045 | 80.0658 | 79.6174
64.8479 | 50.0589 | 441.0233 | 34.9351 | 86.4727 | 80.4555 | 79.7561
65.8479 | 50.4413 | 444.5328 | 35.2232 | 87.1837 | 81.2141 | 80.6288
66.8479 | 50.8675 | 452.2867 | 35.4846 | 88.0194 | 81.5406 | 81.7894
67.8479 | 51.3258 | 451.2028 | 35.7656 | 88.3155 | 81.7106 | 82.0552
68.8479 | 51.6381 | 467.3937 | 36.0268 | 89.1191 | 82.5526 | 82.3987
69.8479 | 52.0871 | 478.701 | 36.4329 | 89.7647 | 83.1854 | 82.7032
70.8479 | 52.6803 | 474.9538 | 36.6917 | 89.7054 | 83.2853 | 83.4799
71.8479 | 53.0283 | 463.2906 | 36.997 | 90.5359 | 83.4227 | 83.6195
72.8479 | 53.4581 | 466.1786 | 37.2208 | 90.7204 | 83.8838 | 83.6204
73.8479 | 53.6951 | 472.8955 | 37.4184 | 91.2438 | 84.7581 | 83.6882
74.8479 | 54.1099 | 471.3131 | 37.5882 | 91.8085 | 85.5152 | 84.5438
75.8479 | 54.4848 | 467.1155 | 37.7103 | 92.3874 | 86.5317 | 85.2913
76.8479 | 54.8167 | 468.2224 | 37.735 | 93.165 | 87.0251 | 85.5348
77.8479 | 55.2118 | 482.742 | 37.856 | 93.6721 | 87.532 | 86.329
78.8479 | 55.5726 | 495.7414 | 37.9805 | 94.3962 | 88.4966 | 87.015
79.8479 | 55.8232 | 508.8117 | 38.3588 | 94.7896 | 88.4937 | 87.5961
80.8479 | 56.2761 | 504.8213 | 38.7652 | 95.453 | 88.7337 | 88.5328
81.8479 | 56.5179 | 503.2117 | 38.9447 | 95.6558 | 89.3655 | 89.2576
82.8635 | 56.969 | 502.7367 | 39.1125 | 96.4035 | 89.6682 | 89.388
83.8479 | 57.3915 | 514.6 | 39.3287 | 97.1924 | 90.0659 | 89.8639
84.8479 | 57.9512 | 516.2984 | 39.5598 | 98.0004 | 90.7551 | 90.1169
85.8479 | 58.276 | 513.8523 | 39.717 | 98.3394 | 91.7949 | 90.6527
86.8479 | 58.6002 | 516.7769 | 40.0063 | 98.7628 | 92.3634 | 90.7728
87.8479 | 59.0882 | 513.6352 | 40.3817 | 99.0371 | 92.7909 | 91.0351
88.8479 | 59.4011 | 522.33 | 40.6409 | 99.4422 | 93.459 | 91.7948
89.8479 | 59.8226 | 522.1788 | 40.9667 | 100.0901 | 93.7353 | 92.3504
90.8479 | 59.7996 | 520.2976 | 41.1916 | 100.4918 | 94.1091 | 92.9782
91.8479 | 60.1015 | 518.4582 | 41.4584 | 100.959 | 94.5704 | 93.2967
92.8479 | 60.4633 | 524.5028 | 41.6616 | 101.2848 | 94.7802 | 94.2574
93.8479 | 60.5914 | 512.0633 | 41.8874 | 101.447 | 95.0599 | 94.918
94.8479 | 60.6301 | 490.9048 | 42.0723 | 101.6109 | 95.5238 | 94.9052
95.8479 | 60.7545 | 490.2624 | 42.3318 | 101.8746 | 96.365 | 95.3941
96.8479 | 60.8094 | 486.9656 | 42.4884 | 102.081 | 97.3107 | 95.946
97.8479 | 60.8286 | 493.213 | 42.9377 | 102.7133 | 98.0485 | 96.3233
98.8479 | 60.8547 | 471.798 | 43.0789 | 103.2432 | 98.5436 | 96.9251
99.8479 | 60.9533 | 490.5949 | 43.304 | 103.7219 | 98.856 | 96.9608
100.8479 | 60.9918 | 497.7889 | 43.6152 | 103.7454 | 99.1886 | 98.0096
101.8479 | 61.2023 | 509.2305 | 43.764 | 103.836 | 99.4196 | 98.4003
102.8479 | 61.2764 | 508.3594 | 43.8962 | 104.1173 | 99.8189 | 98.5527
103.8479 | 61.4407 | 519.8168 | 44.0601 | 104.8391 | 99.6074 | 99.3571
104.8479 | 61.3877 | 508.1043 | 44.2384 | 105.4651 | 99.9951 | 99.7644
105.8479 | 61.603 | 494.2052 | 44.5066 | 105.9518 | 100.4264 | 100.1154
106.8479 | 61.6791 | 499.5623 | 44.8076 | 106.718 | 101.048 | 100.5255
107.8479 | 61.7708 | 511.3242 | 45.0656 | 107.2005 | 101.3822 | 101.4727
108.8479 | 61.8814 | 501.5508 | 45.046 | 107.509 | 101.8063 | 101.5508
109.8479 | 61.9786 | 488.0172 | 45.2798 | 107.6653 | 101.9615 | 101.6955
110.8479 | 61.9524 | 480.6047 | 45.3552 | 107.8143 | 102.2804 | 101.9545
111.8479 | 62.056 | 479.9788 | 45.4073 | 108.2765 | 102.538 | 102.3664
112.8479 | 62.1083 | 480.6969 | 45.5511 | 108.2915 | 102.9807 | 102.4731
113.8479 | 62.3346 | 473.8673 | 45.7384 | 108.2741 | 103.2124 | 102.7741
114.8479 | 62.5678 | 482.114 | 45.9174 | 108.4525 | 103.6694 | 102.8813
115.8479 | 62.7986 | 483.0583 | 46.132 | 108.7486 | 104.4991 | 103.1792
116.8479 | 62.7982 | 478.7314 | 46.463 | 109.0446 | 104.6408 | 103.086
117.8479 | 63.0214 | 482.8834 | 46.7489 | 109.0877 | 104.8186 | 103.2871
118.8479 | 63.2601 | 498.2307 | 46.9984 | 109.4002 | 105.2959 | 103.4999
119.8479 | 63.6523 | 504.7673 | 46.9206 | 109.3487 | 105.3482 | 103.5657
120.8479 | 63.76 | 506.4321 | 46.9951 | 109.5758 | 105.437 | 104.2934
121.8479 | 64.0323 | 523.7841 | 46.8205 | 109.4989 | 105.8217 | 104.6295
122.8479 | 64.2018 | 515.2835 | 46.7087 | 109.6517 | 106.1291 | 104.8662
123.8479 | 64.3034 | 515.3656 | 46.8668 | 109.7979 | 106.4236 | 105.0418
124.8479 | 64.4533 | 517.3986 | 46.9629 | 110.2303 | 106.4476 | 105.2269
125.8479 | 64.4916 | 532.8052 | 47.1343 | 110.5865 | 106.6126 | 105.2662
126.8479 | 64.685 | 529.0086 | 46.9809 | 111.0147 | 106.7616 | 105.4699
127.8479 | 64.8186 | 534.4954 | 47.1264 | 110.9992 | 107.1812 | 105.7444
128.8479 | 64.6936 | 540.202 | 47.1966 | 111.0737 | 107.5635 | 105.8836
129.8479 | 64.6806 | 549.1464 | 47.2594 | 111.2276 | 107.6307 | 105.9533
130.8479 | 64.7713 | 546.5959 | 47.7126 | 111.3736 | 107.998 | 106.4502
131.8479 | 64.7912 | 539.8309 | 47.8789 | 111.6525 | 108.1036 | 106.573
132.8479 | 64.6638 | 542.4169 | 47.9372 | 111.7285 | 108.2756 | 107.2967
133.8479 | 64.7771 | 545.5886 | 47.8325 | 112.2306 | 108.3874 | 107.5862
134.8479 | 64.7181 | 531.0004 | 47.9718 | 112.4998 | 108.2882 | 108.1576
135.8479 | 64.83 | 549.4125 | 47.8631 | 112.9727 | 108.18 | 108.4951
136.8479 | 64.8197 | 540.4532 | 47.8822 | 113.3587 | 108.619 | 109.4306
137.8479 | 64.8643 | 543.1656 | 47.9737 | 113.4825 | 108.9592 | 109.3695
138.8479 | 64.8604 | 546.7477 | 47.8757 | 113.4356 | 109.304 | 109.1523
139.8479 | 65.0813 | 546.3911 | 47.8743 | 113.9959 | 109.9202 | 109.0232
140.8479 | 65.1273 | 533.38 | 47.9877 | 114.3157 | 110.4104 | 109.7174
141.8479 | 65.0981 | 518.1577 | 47.9685 | 114.6879 | 110.4171 | 110.3421
142.8479 | 65.2762 | 530.8438 | 47.9594 | 115.4173 | 110.4454 | 110.3648
143.8479 | 65.2641 | 536.5945 | 47.9796 | 115.5544 | 110.8631 | 110.8311
144.8479 | 65.1609 | 555.6041 | 47.9421 | 115.9791 | 110.7371 | 111.2053
145.8479 | 65.1572 | 558.2329 | 47.7411 | 116.237 | 110.9474 | 111.3751
146.8479 | 65.2239 | 537.3586 | 47.7311 | 116.2626 | 111.2529 | 111.2623
147.8479 | 65.2907 | 519.2706 | 47.8609 | 116.4222 | 111.4675 | 111.5304
148.8479 | 65.4422 | 522.122 | 48.1387 | 116.3345 | 111.5374 | 111.9776
149.8479 | 65.5395 | 529.777 | 48.1257 | 116.1023 | 111.8388 | 111.8757
150.8479 | 65.6842 | 537.5199 | 48.0761 | 116.3682 | 112.2814 | 112.1378
151.8479 | 65.8425 | 539.0945 | 48.1426 | 116.625 | 112.7108 | 112.2064
152.8479 | 66.1035 | 533.0552 | 48.0867 | 117.015 | 113.2608 | 112.1248
153.8479 | 66.4582 | 540.6607 | 48.2372 | 117.0094 | 113.422 | 112.3346
154.8479 | 66.6956 | 545.3243 | 48.4105 | 117.0464 | 113.2541 | 111.9786
155.8479 | 66.7461 | 549.7467 | 48.2499 | 117.2426 | 113.3874 | 111.6994
156.8479 | 66.9299 | 562.0001 | 48.1872 | 117.5277 | 113.5723 | 111.8387
157.8479 | 66.7917 | 583.7266 | 48.1538 | 117.6794 | 114.1308 | 112.0342
158.8479 | 66.8253 | 581.0473 | 48.144 | 117.8633 | 114.2146 | 112.3727
159.8479 | 67.032 | 592.4918 | 48.3969 | 118.1703 | 114.2274 | 112.525
160.8479 | 67.0806 | 576.2729 | 48.4463 | 118.2425 | 114.2696 | 112.5967
161.8479 | 67.1969 | 571.7909 | 48.6705 | 118.2539 | 114.4864 | 113.0693
162.8479 | 67.1115 | 560.9749 | 49.0361 | 118.3666 | 114.8918 | 113.5688
163.8479 | 67.2685 | 569.7383 | 49.2469 | 118.9036 | 115.2249 | 113.8244
164.8479 | 67.6688 | 560.8055 | 49.3711 | 119.0672 | 115.5554 | 113.7315
165.8479 | 67.3656 | 565.0108 | 49.3143 | 118.9605 | 115.9276 | 114.1566
166.8479 | 67.4707 | 556.8605 | 49.2556 | 119.4193 | 115.8206 | 114.6985
167.8479 | 67.6947 | 549.4381 | 49.3625 | 119.3404 | 116.123 | 114.4647
168.8479 | 67.695 | 541.0355 | 49.5494 | 119.6626 | 116.3787 | 114.3125
169.8479 | 67.8477 | 547.1696 | 49.848 | 119.7712 | 116.3538 | 114.214
170.8479 | 67.9625 | 543.6376 | 50.1148 | 120.0136 | 116.6433 | 114.4276
171.8479 | 68.1192 | 548.2724 | 50.2136 | 120.3836 | 116.811 | 114.3036
172.8479 | 68.31 | 546.6685 | 50.4005 | 120.5728 | 116.8 | 114.5743
173.8479 | 68.4436 | 540.7841 | 50.4713 | 120.4833 | 116.7925 | 114.5472
174.8479 | 68.6594 | 543.3222 | 50.3789 | 120.4096 | 116.7825 | 114.7841
175.8479 | 68.7708 | 536.9169 | 50.4098 | 120.6465 | 117.1543 | 115.5176
176.8479 | 68.8621 | 520.7274 | 50.4186 | 120.7742 | 117.4231 | 116.027
177.8479 | 68.8965 | 514.552 | 50.2898 | 121.027 | 117.3874 | 116.2334
178.8479 | 69.0636 | 517.9887 | 50.3783 | 121.4631 | 117.4569 | 117.0761
179.8479 | 69.2623 | 511.5806 | 50.2592 | 121.9173 | 117.6408 | 117.0709
180.8479 | 69.3103 | 500.4506 | 50.0021 | 121.9263 | 118.0969 | 117.4254
181.8479 | 69.4751 | 496.0882 | 50.0484 | 122.0299 | 118.3901 | 117.9343
182.8479 | 69.3898 | 517.2868 | 50.1889 | 122.1762 | 118.3483 | 118.2304
183.8479 | 69.5936 | 524.133 | 50.2703 | 122.0985 | 118.3993 | 118.1284
184.8479 | 69.6587 | 533.6445 | 50.5496 | 121.9446 | 118.4804 | 117.8343
185.8479 | 69.9159 | 531.3926 | 50.5692 | 121.6906 | 118.3096 | 117.8597
186.8479 | 69.8853 | 532.5298 | 50.5759 | 122.0179 | 118.3288 | 117.8658
187.8479 | 69.9667 | 536.0708 | 50.5125 | 122.0738 | 118.3584 | 117.8943
188.8479 | 70.1321 | 541.3337 | 50.3885 | 121.9049 | 118.5479 | 117.9758
189.8479 | 70.1934 | 538.4357 | 50.2069 | 121.7002 | 118.9439 | 117.8255
190.8479 | 70.3262 | 526.614 | 50.1827 | 121.6939 | 118.9928 | 117.8323
191.8479 | 70.1883 | 524.7688 | 50.1546 | 122.0995 | 119.061 | 117.7986
192.8479 | 70.4953 | 522.7274 | 50.095 | 122.1531 | 119.275 | 117.961
193.8479 | 70.5623 | 510.542 | 50.1383 | 122.1127 | 119.1356 | 118.0709
194.8479 | 70.5879 | 517.3998 | 50.1553 | 122.3083 | 118.8468 | 118.5967
195.8479 | 70.892 | 529.9891 | 50.23 | 122.1194 | 118.9284 | 118.7072
196.8479 | 71.0634 | 538.3694 | 50.4405 | 121.9578 | 119.2549 | 119.0361
197.8479 | 71.1746 | 540.9198 | 50.5717 | 122.1787 | 119.3223 | 118.7616
198.8479 | 71.4688 | 557.8313 | 50.6529 | 122.2374 | 119.2832 | 118.6334
199.8479 | 71.7472 | 570.171 | 50.8221 | 122.5311 | 119.5824 | 118.6188
200.8479 | 71.9976 | 566.8024 | 50.9106 | 122.9387 | 119.4463 | 118.3643
201.8479 | 72.1508 | 562.2623 | 50.9899 | 122.7421 | 119.427 | 118.1701
202.8479 | 72.1502 | 562.7783 | 50.9357 | 123.0171 | 120.04 | 117.8519
203.8479 | 72.5778 | 579.1895 | 50.997 | 123.516 | 120.456 | 117.6746
204.8479 | 72.7963 | 585.9437 | 50.9876 | 123.6676 | 120.7764 | 118.6553
205.8479 | 72.6908 | 593.9541 | 51.0547 | 123.8542 | 121.1306 | 118.7444
206.8479 | 73.0466 | 607.2892 | 51.1012 | 124.2007 | 121.2081 | 118.6152
207.8479 | 73.1623 | 599.9878 | 51.0753 | 124.4735 | 121.1904 | 119.0028
208.8479 | 73.0631 | 594.9658 | 51.1188 | 124.8426 | 121.2985 | 119.043
209.8479 | 73.2532 | 606.1619 | 51.0554 | 125.0199 | 121.3469 | 119.7706
210.8479 | 73.3186 | 609.748 | 50.9582 | 125.8039 | 121.4499 | 120.2388
211.8479 | 73.2951 | 615.9198 | 50.8893 | 126.0444 | 121.5102 | 120.4157
212.8479 | 73.3826 | 618.3633 | 50.779 | 126.4384 | 121.4256 | 120.1682
213.8479 | 73.334 | 630.0631 | 50.578 | 126.606 | 121.7942 | 120.2145
214.8479 | 73.3675 | 631.0991 | 50.5799 | 126.7779 | 122.0937 | 120.4091
215.8479 | 73.3448 | 630.3946 | 50.5016 | 127.0186 | 122.4227 | 120.1451
216.8479 | 73.4411 | 633.8419 | 50.5113 | 127.3916 | 122.2459 | 120.2964
217.8479 | 73.5409 | 623.3283 | 50.5849 | 127.6525 | 122.5224 | 120.2663
218.8479 | 73.5471 | 626.8451 | 50.5932 | 128.2358 | 122.8159 | 120.0238
219.8479 | 73.5539 | 631.4347 | 50.6983 | 128.1896 | 123.1428 | 120.0205
220.8479 | 73.495 | 639.8822 | 50.7098 | 128.0924 | 123.4623 | 119.7678
221.8479 | 73.668 | 632.5694 | 50.7315 | 128.3548 | 123.4772 | 119.5366
222.8479 | 73.9444 | 623.4743 | 50.6321 | 128.3201 | 123.3813 | 120.0981
223.8479 | 74.1123 | 629.9663 | 50.5652 | 128.1563 | 123.6332 | 120.4455
224.8479 | 74.249 | 613.7455 | 50.4681 | 127.9472 | 124.0454 | 120.5499
225.8479 | 74.3082 | 614.0868 | 50.5607 | 128.2158 | 124.2467 | 120.702
226.8479 | 74.6001 | 622.8819 | 50.6815 | 128.4275 | 124.5819 | 121.4047
227.8479 | 74.7446 | 609.2618 | 50.7532 | 128.7537 | 124.7164 | 121.5675
228.8479 | 74.9839 | 617.3804 | 50.8465 | 129.0811 | 124.3653 | 121.3729
229.8479 | 75.3081 | 623.3553 | 50.8464 | 129.1133 | 124.1564 | 121.6859
230.8479 | 75.4901 | 623.7283 | 50.8255 | 128.9299 | 124.3318 | 121.8208
231.8479 | 75.5684 | 603.0675 | 51.0184 | 128.6681 | 124.4359 | 121.9229
232.8479 | 75.6846 | 609.6943 | 51.3486 | 128.3991 | 124.3826 | 121.9796
233.8479 | 75.953 | 613.8974 | 51.4434 | 128.3132 | 124.4806 | 122.801
234.8479 | 76.0059 | 605.7459 | 51.5977 | 128.2507 | 124.6362 | 123.1387
235.8479 | 76.1233 | 602.9868 | 51.8275 | 128.3014 | 124.4703 | 123.3026
236.8479 | 76.2426 | 595.6483 | 51.9548 | 128.1616 | 124.7059 | 123.4821
237.8479 | 76.4464 | 589.1031 | 51.7531 | 128.2831 | 124.9765 | 123.7358
238.8479 | 76.5936 | 593.4761 | 51.8748 | 128.1114 | 125.2202 | 123.8618
239.8479 | 76.8837 | 588.7034 | 51.874 | 127.8791 | 125.2718 | 124.0168
240.8479 | 76.9174 | 583.2873 | 52.0975 | 127.8813 | 125.2482 | 124.2751
241.8479 | 77.1068 | 569.293 | 52.4047 | 128.1592 | 125.2623 | 124.9079
242.8479 | 77.2913 | 571.4468 | 52.7079 | 128.1194 | 125.1229 | 125.1352
243.8479 | 77.5342 | 566.1828 | 52.8458 | 127.9389 | 125.2403 | 126.0643
244.8479 | 77.5312 | 558.5293 | 53.0587 | 127.9308 | 125.2661 | 126.324
245.8479 | 77.4225 | 544.0251 | 53.0974 | 127.7622 | 125.2143 | 126.6223
246.8479 | 77.5488 | 550.3803 | 53.2464 | 127.5129 | 125.4991 | 126.7297
247.8479 | 77.7328 | 555.1974 | 53.2915 | 127.4238 | 125.7837 | 127.0224
248.8479 | 77.8126 | 560.7077 | 53.2203 | 128.0482 | 126.0026 | 127.3963
249.8479 | 77.8544 | 558.6734 | 53.3707 | 128.2139 | 126.06 | 127.9748
250.8479 | 77.9475 | 568.701 | 53.5105 | 128.1565 | 125.8971 | 128.2823
251.8479 | 77.9211 | 553.4141 | 53.5165 | 128.4189 | 126.0265 | 128.1312
252.8479 | 77.9743 | 577.8581 | 53.6496 | 128.2057 | 126.141 | 128.1791
253.8479 | 77.9106 | 573.118 | 53.7935 | 127.9649 | 126.0974 | 127.9172
254.8479 | 77.7926 | 567.8665 | 53.963 | 128.0819 | 126.0065 | 128.188
255.8479 | 77.6138 | 589.3282 | 54.1751 | 128.3607 | 126.2368 | 128.3787
256.8479 | 77.7625 | 605.1957 | 54.4396 | 128.467 | 126.5534 | 128.7181
257.8479 | 77.8146 | 605.4896 | 54.5589 | 128.5974 | 126.5551 | 128.6264
258.8479 | 77.5902 | 603.5744 | 54.7377 | 128.6307 | 126.458 | 129.7044
259.8479 | 77.6985 | 600.3667 | 54.8327 | 128.7105 | 126.5781 | 129.8928
260.8479 | 77.5331 | 607.2618 | 55.0146 | 128.9136 | 126.8975 | 130.0987
261.8479 | 77.6987 | 619.0041 | 55.1161 | 129.1922 | 127.2175 | 129.7793
262.8479 | 77.6517 | 605.9731 | 55.1126 | 129.3924 | 127.1318 | 129.6245
263.8479 | 77.5615 | 595.9715 | 55.253 | 129.4677 | 127.011 | 129.7008
264.8479 | 77.8542 | 584.4744 | 55.4371 | 129.5925 | 127.1909 | 129.4901
265.8479 | 77.9587 | 591.1706 | 55.4981 | 129.5416 | 127.455 | 129.397
266.8479 | 78.0548 | 585.3444 | 55.4919 | 129.5404 | 127.2494 | 129.5098
267.8479 | 78.0087 | 586.4024 | 55.3519 | 129.3358 | 127.2546 | 129.469
268.8479 | 77.829 | 593.7051 | 55.2056 | 129.8481 | 127.4552 | 129.341
269.8479 | 77.7781 | 609.6135 | 55.5237 | 129.8284 | 127.4213 | 129.3058
270.8479 | 77.7681 | 598.2315 | 55.7646 | 129.7654 | 127.544 | 129.4866
271.8479 | 77.9837 | 614.8186 | 56.0025 | 129.5791 | 127.6093 | 129.9076
272.8479 | 78.1422 | 632.9897 | 56.2039 | 129.4556 | 127.9029 | 130.1513
273.8479 | 78.269 | 641.9065 | 56.1369 | 129.5737 | 128.1171 | 129.9858
274.8479 | 78.2351 | 673.5118 | 56.0782 | 129.8066 | 128.2767 | 129.9987
275.8479 | 78.4471 | 683.1095 | 55.9891 | 130.2027 | 128.2291 | 130.1014
276.8479 | 78.5957 | 682.8583 | 55.9451 | 130.4232 | 128.6048 | 130.2935
277.8479 | 78.5479 | 703.9934 | 55.8853 | 130.608 | 128.8003 | 130.0249
278.8479 | 78.753 | 709.6289 | 55.8008 | 130.9318 | 128.8563 | 130.1517
279.8479 | 78.9316 | 701.7535 | 55.9194 | 131.373 | 128.9085 | 129.9937
280.8479 | 79.0435 | 704.1757 | 55.9004 | 131.5552 | 129.3137 | 130.3223
281.8479 | 79.1093 | 700.7698 | 55.8345 | 131.6809 | 129.4856 | 130.599
282.8479 | 79.344 | 697.3235 | 55.7939 | 131.7429 | 129.7762 | 130.5304
283.8479 | 79.5932 | 699.2715 | 55.8872 | 131.658 | 129.833 | 130.9942
284.8479 | 79.6927 | 694.857 | 56.4547 | 131.7298 | 129.9601 | 130.7317
285.8479 | 80.0354 | 700.0442 | 56.6322 | 132.065 | 129.9051 | 130.7931
286.8479 | 80.234 | 707.1231 | 56.5319 | 131.9003 | 130.0042 | 131.0338
287.8479 | 80.4143 | 702.4462 | 56.6531 | 131.8295 | 129.7585 | 131.0961
288.8479 | 80.5002 | 698.6783 | 56.9014 | 132.0384 | 129.5861 | 131.4471
289.8479 | 80.6461 | 705.3938 | 57.1514 | 132.0798 | 129.6931 | 132.5107
290.8479 | 80.7876 | 702.492 | 57.5528 | 131.9676 | 129.7658 | 132.6291
291.8479 | 80.9311 | 697.852 | 57.7442 | 131.8847 | 129.8305 | 132.9503
292.8479 | 81.0492 | 694.9413 | 57.845 | 132.1956 | 130.3167 | 132.9966
293.8479 | 81.0422 | 697.9464 | 58.0573 | 132.7956 | 130.8166 | 133.2396
294.8479 | 81.2074 | 697.8789 | 58.1659 | 132.9374 | 130.6234 | 133.0034
295.8479 | 80.9219 | 705.8895 | 58.3672 | 132.967 | 130.5689 | 132.8683
296.8479 | 80.9889 | 714.2817 | 58.5675 | 133.2221 | 130.6846 | 132.6307
297.8479 | 80.8164 | 714.2654 | 58.5564 | 133.089 | 131.0906 | 132.8048
298.8479 | 80.6846 | 712.9332 | 58.6024 | 133.2267 | 130.8607 | 132.7379
299.8479 | 80.8097 | 723.4112 | 58.8693 | 133.4763 | 130.6741 | 132.6623
300.8479 | 81.0124 | 725.225 | 58.9388 | 133.6748 | 130.8196 | 132.5272
301.8479 | 81.1941 | 723.8723 | 59.356 | 134.1117 | 130.8695 | 132.3541
302.8479 | 81.2114 | 719.6146 | 59.4138 | 134.3243 | 130.817 | 132.9191
303.8479 | 81.0927 | 723.2903 | 59.6348 | 134.3272 | 131.0437 | 133.0512
304.8479 | 81.5532 | 728.3159 | 59.7229 | 134.3903 | 131.6209 | 133.3191
305.8479 | 81.6112 | 708.1466 | 59.765 | 134.8331 | 131.9708 | 133.3771
306.8479 | 81.551 | 712.3391 | 59.978 | 134.8904 | 132.2118 | 133.3648
307.8479 | 81.7281 | 714.91 | 60.229 | 135.2279 | 132.5805 | 133.3418
308.8479 | 82.0792 | 701.6848 | 60.5535 | 135.4408 | 132.9505 | 133.7041
309.8479 | 82.1965 | 719.114 | 60.6533 | 135.6682 | 132.8395 | 133.8512
310.8479 | 82.3308 | 718.679 | 60.9308 | 135.5406 | 132.7557 | 133.8138
311.8479 | 82.5525 | 720.5445 | 61.0814 | 135.397 | 132.6349 | 134.4597
312.8479 | 82.5351 | 718.2923 | 60.9861 | 135.2669 | 132.7588 | 134.4534
313.8479 | 82.7448 | 703.6896 | 60.8263 | 135.2863 | 132.8287 | 134.4709
314.8479 | 83.1605 | 715.2463 | 60.7671 | 135.1551 | 133.0852 | 134.88
315.8479 | 83.2548 | 730.6309 | 61.0389 | 135.1679 | 133.3226 | 134.9083
316.8479 | 83.3846 | 671.3464 | 61.2379 | 135.059 | 133.4664 | 134.7066
317.8479 | 83.54 | 755.8549 | 61.1619 | 135.1463 | 133.7616 | 134.5259
318.8479 | 83.5832 | 760.8964 | 61.2475 | 135.4066 | 134.0597 | 134.7752
319.8479 | 83.6571 | 767.1092 | 61.497 | 135.6708 | 134.5443 | 135.0103
320.8479 | 83.8419 | 780.1697 | 61.3995 | 135.6315 | 134.9167 | 135.1466
321.8479 | 83.736 | 783.0736 | 61.5289 | 135.871 | 135.0023 | 135.0815
322.8479 | 83.6954 | 787.5858 | 61.7018 | 135.8176 | 135.0994 | 135.4584
323.8479 | 83.711 | 799.8358 | 61.7683 | 136.0616 | 135.4381 | 135.7642
324.8479 | 83.9167 | 772.0281 | 61.9878 | 136.0557 | 135.9018 | 135.898
325.8479 | 83.9075 | 785.2488 | 62.01 | 136.6419 | 136.2733 | 136.1635
326.8479 | 84.0579 | 785.8895 | 62.1597 | 137.1789 | 136.1687 | 136.0284
327.8479 | 84.0236 | 796.7062 | 62.251 | 137.427 | 136.1611 | 136.0076
328.8479 | 84.4383 | 788.7962 | 62.4539 | 137.6492 | 135.8972 | 136.1254
329.8479 | 84.4551 | 782.9894 | 62.6987 | 137.706 | 135.8083 | 136.5964
330.8479 | 84.6963 | 800.9889 | 63.0629 | 137.4473 | 135.9105 | 136.4349
331.8479 | 84.8323 | 797.6887 | 63.1584 | 137.6481 | 136.1571 | 137.0782
332.8479 | 84.8546 | 785.0144 | 63.2398 | 137.9925 | 136.1267 | 137.4694
333.8479 | 84.5937 | 783.9056 | 63.3452 | 138.2071 | 136.1079 | 137.5594
334.8479 | 84.7594 | 789.8103 | 63.2195 | 138.5507 | 136.4045 | 137.8418
335.8479 | 84.8938 | 420.4721 | 63.0273 | 138.7149 | 136.539 | 138.3188
336.8479 | 85.0474 | 159.3102 | 63.0492 | 138.7353 | 136.7491 | 138.4553
337.8479 | 87.379 | 651.1855 | 63.0454 | 138.736 | 137.1485 | 138.5553
338.8479 | 86.7358 | 775.9779 | 63.1596 | 139.0981 | 137.4393 | 138.512
339.8479 | 86.743 | 344.4306 | 63.1304 | 139.4081 | 137.5022 | 138.651
340.8479 | 86.5559 | 50.1405 | 63.3687 | 139.799 | 137.355 | 138.8566
341.8479 | 86.4352 | 87.5893 | 63.4661 | 140.2537 | 137.6589 | 139.1889
342.8479 | 86.3676 | 455.6598 | 63.3728 | 140.376 | 137.8467 | 139.3247
343.8479 | 86.4128 | 52.5462 | 63.3166 | 140.3423 | 137.5919 | 139.1709
344.8479 | 86.5254 | 613.022 | 63.448 | 140.1962 | 137.4328 | 139.7536
345.8479 | 86.3913 | 50.6161 | 63.7351 | 140.4289 | 137.5482 | 139.853
346.8479 | 86.3994 | 739.6281 | 64.0406 | 140.7759 | 137.8458 | 140.6223
347.8479 | 86.6749 | 183.2833 | 64.1513 | 140.7863 | 138.1674 | 140.9612
348.8479 | 86.8894 | 734.4734 | 64.327 | 140.9306 | 138.1442 | 141.0562
349.8479 | 86.8384 | 750.9866 | 64.5086 | 141.0074 | 138.0582 | 141.0827
350.8479 | 86.77 | 735.1826 | 64.559 | 140.9966 | 138.0877 | 140.8701
351.8479 | 86.9301 | 731.6145 | 64.7036 | 141.1725 | 138.2654 | 140.723
352.8479 | 86.946 | 719.1246 | 64.3615 | 141.2285 | 138.2968 | 140.3741
353.8479 | 87.2831 | 713.4637 | 64.3042 | 141.251 | 138.0238 | 140.145
354.8479 | 87.1707 | 716.0354 | 63.9699 | 140.9962 | 138.2404 | 140.1658
355.8479 | 87.0617 | 703.7268 | 63.7964 | 140.9967 | 138.1311 | 140.7692
356.8479 | 86.7549 | 701.5259 | 63.8028 | 141.1927 | 137.9928 | 141.1
357.8479 | 86.7284 | 703.1466 | 63.7318 | 141.3031 | 137.943 | 140.7507
358.8479 | 86.7809 | 698.0854 | 63.585 | 141.3051 | 138.0668 | 140.4075
359.8479 | 86.7064 | 699.0849 | 63.7203 | 141.6587 | 138.1536 | 140.2315
360.8479 | 86.7609 | 699.688 | 63.5297 | 141.488 | 138.0298 | 140.1547
361.8479 | 87.0989 | 701.8481 | 63.7297 | 141.6861 | 138.0415 | 139.8713
362.8479 | 87.0376 | 694.9487 | 63.8526 | 142.0155 | 138.2534 | 139.6336
363.8479 | 87.0167 | 703.9408 | 64.2165 | 142.2232 | 138.4758 | 139.7385
364.8479 | 86.983 | 706.3554 | 64.1137 | 142.1206 | 138.8552 | 140.0257
365.8479 | 86.9761 | 693.6736 | 64.3654 | 142.146 | 139.0241 | 139.8837
366.8479 | 86.9097 | 682.7745 | 64.3695 | 142.0679 | 138.8825 | 140.1513
367.8479 | 86.9553 | 681.8568 | 64.4635 | 141.84 | 138.8937 | 140.419
368.8479 | 86.7616 | 699.6673 | 65.0585 | 141.8969 | 139.037 | 140.6991
369.8479 | 86.8256 | 701.0006 | 65.3862 | 142.1384 | 138.75 | 140.6708
370.8479 | 86.9181 | 693.2971 | 65.5506 | 142.3524 | 138.7179 | 140.8115
371.8479 | 87.0431 | 690.9745 | 65.4764 | 142.638 | 139.1532 | 140.9308
372.8479 | 87.3268 | 694.6566 | 65.2185 | 142.7492 | 139.1431 | 140.868
373.8479 | 87.7174 | 687.2995 | 65.0054 | 142.7525 | 139.2697 | 141.2732
374.8479 | 87.8259 | 677.8889 | 64.9387 | 143.0766 | 139.2656 | 141.6461
375.8479 | 87.7562 | 669.2099 | 65.1992 | 143.5368 | 139.1417 | 141.5202
376.8479 | 87.7166 | 660.6955 | 65.4497 | 143.5396 | 139.3219 | 141.8674
377.8479 | 87.653 | 669.0383 | 65.7625 | 143.8164 | 139.4847 | 141.8357
378.8479 | 87.4287 | 657.5759 | 66.107 | 143.8425 | 139.2671 | 142.123
379.8479 | 87.5867 | 651.3634 | 66.3069 | 143.708 | 139.5466 | 142.5484
380.8479 | 87.4011 | 643.8911 | 66.4796 | 143.7923 | 139.6333 | 143.1303
381.8479 | 87.4661 | 637.6563 | 66.7155 | 143.658 | 139.651 | 143.3601
382.8479 | 87.5104 | 645.236 | 66.6275 | 143.5162 | 139.5496 | 143.5661
383.8479 | 87.8395 | 635.1945 | 66.9092 | 143.349 | 139.8057 | 143.4512
384.8479 | 88.0555 | 636.4575 | 67.0948 | 144.3689 | 140.1959 | 143.7348
385.8479 | 88.0045 | 629.0897 | 67.2337 | 144.5047 | 140.3435 | 143.7081
386.8479 | 87.9075 | 621.829 | 66.8249 | 144.7267 | 140.4735 | 143.7225
387.8479 | 87.9864 | 634.6575 | 66.6218 | 145.0015 | 140.3654 | 143.9761
388.8479 | 88.2371 | 649.4601 | 66.411 | 145.2785 | 140.4761 | 144.1312
389.8479 | 88.1607 | 647.6159 | 66.3241 | 145.4453 | 140.5336 | 144.0323
390.8479 | 88.1991 | 651.0042 | 66.6932 | 145.2208 | 140.569 | 144.0915
391.8479 | 88.3977 | 641.1914 | 66.9351 | 145.1545 | 140.6222 | 144.0097
392.8479 | 88.3356 | 639.2669 | 67.0879 | 145.1832 | 140.261 | 143.8586
393.8479 | 88.2558 | 626.394 | 67.0473 | 145.3008 | 140.4923 | 144.2423
394.8479 | 88.2016 | 617.8626 | 67.012 | 145.6617 | 140.7426 | 144.3988
395.8479 | 87.8602 | 618.2134 | 66.8011 | 145.7466 | 140.3125 | 144.9621
396.8479 | 88.1521 | 604.217 | 66.5119 | 145.5537 | 140.1281 | 145.6928
397.8479 | 87.8261 | 611.5087 | 66.4127 | 145.4876 | 140.3109 | 145.7872
398.8479 | 87.5118 | 613.3552 | 66.3576 | 145.4692 | 140.4855 | 145.6532
399.8479 | 87.343 | 610.6768 | 66.3527 | 145.3452 | 140.3017 | 145.5163
400.8479 | 86.9387 | 626.6339 | 66.6128 | 145.1057 | 140.1118 | 145.564
401.8479 | 86.8924 | 629.8965 | 66.6666 | 144.9879 | 139.9476 | 145.7428
402.8479 | 86.7369 | 620.276 | 66.4956 | 145.0093 | 140.2809 | 145.7188
403.8479 | 86.6557 | 622.3762 | 66.7938 | 145.1594 | 140.5095 | 145.5771
404.8479 | 86.4976 | 629.4175 | 66.7886 | 144.921 | 140.8475 | 145.3611
405.8479 | 86.2569 | 621.3645 | 66.7763 | 144.7729 | 140.9908 | 145.6219
406.8479 | 85.9381 | 610.4922 | 66.6534 | 144.9549 | 140.9604 | 145.7491
407.8479 | 85.7489 | 607.399 | 66.8345 | 144.9763 | 140.5836 | 145.6835
408.8479 | 85.8111 | 619.0906 | 67.1132 | 145.1839 | 140.428 | 145.8525
409.8479 | 85.9085 | 610.9815 | 67.4398 | 145.1449 | 140.7651 | 145.9469
410.8479 | 85.8986 | 615.6891 | 67.7506 | 145.113 | 140.6433 | 146.1759
411.8479 | 85.9194 | 603.2831 | 67.7512 | 145.0015 | 140.7611 | 146.1167
412.8479 | 86.08 | 602.0604 | 68.1016 | 145.1679 | 140.7255 | 146.5593
413.8479 | 86.233 | 608.456 | 68.4156 | 145.318 | 140.866 | 146.477
414.8479 | 86.0925 | 591.3288 | 68.3096 | 145.4704 | 140.965 | 146.7382
415.8479 | 86.2119 | 598.8503 | 68.0912 | 145.723 | 141.0567 | 146.7518
416.8479 | 86.3238 | 612.3189 | 68.0346 | 145.7245 | 141.4311 | 146.8202
417.8479 | 86.6251 | 599.035 | 68.1538 | 145.6383 | 141.2902 | 147.0599
418.8479 | 86.6547 | 592.9672 | 68.2951 | 145.6455 | 141.1475 | 146.9294
419.8479 | 86.6107 | 582.4422 | 67.8045 | 145.6252 | 141.1549 | 146.9068
420.8479 | 86.8179 | 578.9712 | 67.9068 | 145.9571 | 141.4391 | 147.0615
421.8479 | 86.7132 | 578.9066 | 68.1125 | 145.9868 | 141.7767 | 147.3602
422.8479 | 86.8114 | 576.4223 | 68.2282 | 145.7605 | 142.0141 | 147.5584
423.8479 | 86.8157 | 561.1605 | 68.4693 | 145.7353 | 141.9944 | 147.5385
424.8479 | 86.7583 | 589.9988 | 68.614 | 145.6878 | 142.0645 | 147.7855
425.8479 | 86.831 | 611.149 | 68.7806 | 146.2362 | 142.2054 | 147.6553
426.8479 | 87.0753 | 588.572 | 68.8423 | 146.2844 | 142.4153 | 147.4455
427.8479 | 87.3084 | 593.5163 | 68.8057 | 146.0783 | 142.4982 | 147.2689
428.8479 | 87.3457 | 593.8938 | 68.6174 | 146.0748 | 142.6426 | 147.4232
429.8479 | 87.5313 | 612.8853 | 68.8371 | 146.2516 | 143.0632 | 147.1397
430.8479 | 87.7041 | 615.5462 | 69.1201 | 146.76 | 143.0172 | 147.1509
431.8479 | 87.8327 | 617.7668 | 69.3938 | 147.0395 | 142.7847 | 146.8168
432.8479 | 87.8372 | 621.2734 | 69.0769 | 147.1196 | 142.7308 | 146.8313
433.8479 | 87.6945 | 615.6438 | 69.3194 | 147.4834 | 142.517 | 146.9526
434.8479 | 87.7677 | 607.0823 | 69.4195 | 148.1945 | 142.8949 | 146.6891
435.8479 | 87.7245 | 621.5732 | 69.1907 | 148.4251 | 143.3542 | 147.3054
436.8479 | 87.6905 | 620.8001 | 68.907 | 148.2283 | 143.5294 | 147.8858
437.8479 | 87.7442 | 612.5117 | 68.8605 | 148.2079 | 143.6945 | 148.6021
438.8479 | 87.9062 | 616.3212 | 68.9517 | 148.0493 | 143.4998 | 148.9071
439.8479 | 87.551 | 631.7363 | 68.9796 | 147.7695 | 143.3696 | 149.4211
440.8479 | 87.735 | 628.541 | 69.235 | 147.4243 | 143.4302 | 149.8172
441.8479 | 87.5261 | 626.4139 | 69.5002 | 147.1814 | 143.6046 | 149.6779
442.8479 | 87.5409 | 632.5505 | 69.3583 | 147.0092 | 143.9793 | 149.7251
443.8479 | 87.4853 | 619.8665 | 69.2217 | 147.3274 | 144.2717 | 149.5235
444.8479 | 87.7427 | 619.5823 | 69.281 | 147.5428 | 143.9767 | 149.4603
445.8479 | 88.0076 | 615.9186 | 69.3069 | 147.4229 | 144.0099 | 149.1984
446.8479 | 88.0286 | 603.1647 | 69.1896 | 147.4799 | 144.0261 | 149.2085
447.8479 | 88.4366 | 591.286 | 69.5043 | 147.3307 | 144.1193 | 149.4922
448.8479 | 88.6695 | 586.3058 | 69.5391 | 147.2405 | 144.107 | 149.8959
449.8479 | 88.6029 | 591.4477 | 69.333 | 147.1882 | 144.081 | 150.192
450.8479 | 88.5785 | 600.0051 | 68.9158 | 147.0489 | 144.2781 | 149.909
451.8479 | 88.5709 | 589.6189 | 68.8484 | 146.9171 | 144.1949 | 149.9753
452.8479 | 88.7504 | 586.9016 | 69.0353 | 146.7764 | 144.074 | 149.7935
453.8479 | 88.6438 | 604.3 | 69.1925 | 146.7944 | 144.1555 | 149.7939
454.8479 | 88.73 | 593.0732 | 69.1841 | 146.915 | 144.3712 | 150.0819
455.8479 | 88.7508 | 610.4394 | 69.4641 | 147.1404 | 144.4926 | 150.2353
456.8479 | 88.8324 | 617.0689 | 69.6506 | 147.093 | 144.6137 | 150.4343
457.8479 | 88.7328 | 596.2942 | 69.6557 | 146.8475 | 144.6998 | 150.5254
458.8479 | 88.7342 | 604.9679 | 69.7085 | 146.7815 | 144.8487 | 150.3615
459.8479 | 88.9632 | 618.7064 | 69.8208 | 146.7907 | 144.5654 | 150.7298
460.8479 | 89.2845 | 614.068 | 70.1058 | 146.6998 | 144.6208 | 150.7548
461.8479 | 89.9743 | 631.1403 | 70.152 | 146.7808 | 144.5113 | 151.1281
462.8479 | 90.6408 | 629.96 | 70.3001 | 147.0073 | 144.4813 | 152.258
463.8479 | 91.3188 | 641.4207 | 70.4635 | 147.1674 | 144.8457 | 153.4923
464.8479 | 91.7262 | 655.1785 | 70.4042 | 147.9051 | 145.0887 | 154.4531
465.8479 | 92.3564 | 669.2883 | 70.9629 | 148.2887 | 145.4217 | 155.2035
466.8479 | 92.9625 | 674.5167 | 71.2852 | 148.4121 | 145.7482 | 155.5462
467.8479 | 93.6752 | 664.8272 | 71.6436 | 148.4022 | 146.3378 | 155.798
468.8479 | 94.3786 | 664.0826 | 72.2626 | 149.3875 | 147.0247 | 155.9416
469.8479 | 94.9569 | 675.2451 | 72.4566 | 149.9354 | 147.5574 | 157.0366
470.8479 | 95.6767 | 694.8839 | 72.7686 | 150.2232 | 148.2614 | 158.0425
471.8479 | 96.0595 | 707.02 | 73.07 | 150.9308 | 149.1142 | 159.1194
472.8479 | 96.7747 | 724.324 | 73.439 | 151.947 | 149.6385 | 159.2582
473.8479 | 97.1602 | 702.2662 | 73.9424 | 152.6145 | 150.4072 | 160.7242
474.8479 | 97.5746 | 716.4572 | 74.3568 | 153.079 | 151.2367 | 162.5343
475.8479 | 98.5052 | 715.3633 | 74.7455 | 153.605 | 152.1595 | 162.9894
476.8479 | 98.6892 | 712.0387 | 75.1441 | 153.9802 | 152.8585 | 163.4503
477.8479 | 99.187 | 709.505 | 75.3126 | 154.7788 | 154.0699 | 163.9105
478.8479 | 99.7486 | 705.2423 | 75.6413 | 155.9597 | 155.1915 | 164.3016
479.8479 | 100.2217 | 713.8443 | 75.6951 | 156.9629 | 155.7274 | 164.7632
480.8479 | 100.6786 | 710.912 | 75.6046 | 157.6086 | 156.1944 | 165.6814
481.8479 | 101.2716 | 715.1398 | 75.5231 | 158.4863 | 156.9933 | 166.6013
482.8479 | 101.3955 | 703.9933 | 75.8487 | 158.7843 | 158.4542 | 167.5876
483.8479 | 101.7526 | 690.7241 | 75.9361 | 159.4262 | 159.6538 | 168.2845
484.8479 | 102.0621 | 692.1654 | 76.1852 | 160.377 | 160.9641 | 169.3482
485.8479 | 102.6992 | 691.5915 | 76.2458 | 161.2177 | 161.8205 | 170.1189
486.8479 | 103.4578 | 690.2162 | 76.6131 | 162.2087 | 162.3118 | 171.4477
487.8479 | 103.6833 | 689.0772 | 76.5238 | 163.704 | 163.0884 | 171.9928
488.8479 | 104.4188 | 689.9803 | 76.7755 | 164.8208 | 164.072 | 173.0078
489.8479 | 105.0697 | 691.9984 | 76.9645 | 165.6754 | 165.0474 | 173.8052
490.8479 | 105.7722 | 684.7011 | 76.8629 | 166.3121 | 165.8642 | 174.141
491.8479 | 106.5992 | 699.4175 | 76.7356 | 167.3178 | 166.4372 | 174.5889
492.8479 | 106.9507 | 693.7282 | 76.881 | 168.419 | 167.5788 | 174.9268
493.8479 | 107.4586 | 687.6983 | 77.0248 | 169.5789 | 168.4997 | 175.4687
494.8479 | 108.0663 | 698.5007 | 77.3252 | 170.8786 | 169.823 | 176.2874
495.8479 | 108.6249 | 687.8395 | 77.371 | 172.8428 | 171.4523 | 177.1709
496.8479 | 109.1017 | 692.1221 | 77.1067 | 174.0062 | 172.5755 | 178.2362
497.8479 | 109.6947 | 685.4938 | 77.1626 | 175.1126 | 173.3821 | 178.7085
498.8479 | 110.1098 | 675.53 | 77.2503 | 177.1883 | 174.108 | 179.1534
499.8479 | 110.4742 | 686.5328 | 77.597 | 177.906 | 175.0388 | 179.8641
500.8479 | 110.8374 | 693.5187 | 77.8327 | 178.5974 | 175.9555 | 181.3436
501.8479 | 110.9261 | 688.0306 | 78.2744 | 179.6987 | 177.4647 | 181.8227
502.8479 | 111.0326 | 701.5588 | 78.6165 | 180.434 | 178.967 | 182.691
503.8479 | 111.4326 | 708.4287 | 79.0345 | 181.7948 | 179.3979 | 184.2513
504.8479 | 111.769 | 693.2134 | 78.9422 | 182.6454 | 180.2785 | 184.3712
505.8479 | 112.0042 | 692.7571 | 78.9252 | 184.3231 | 181.6986 | 184.1731
506.8479 | 112.3445 | 704.7957 | 79.0331 | 185.0029 | 183.1767 | 184.8715
507.8479 | 112.5617 | 699.5269 | 79.3505 | 185.6984 | 184.1693 | 187.604
508.8479 | 113.0635 | 696.735 | 79.3298 | 187.1753 | 185.2158 | 189.1749
509.8479 | 113.3251 | 680.3035 | 79.0809 | 187.747 | 186.5187 | 189.6647
510.8479 | 113.7081 | 676.3242 | 79.2066 | 188.9322 | 187.3078 | 189.447
511.8479 | 113.8813 | 670.8659 | 79.3315 | 189.6074 | 189.1207 | 190.2083
512.8479 | 114.3737 | 679.1568 | 79.4948 | 190.1523 | 189.7174 | 190.5541
513.8479 | 114.313 | 671.1623 | 80.1413 | 190.5564 | 190.8125 | 191.4759
514.8479 | 114.4345 | 678.8855 | 80.2892 | 192.36 | 191.6109 | 192.0386
515.8479 | 114.3601 | 680.9206 | 80.6175 | 192.2756 | 192.1142 | 193.5549
516.8479 | 114.4792 | 660.4248 | 80.7516 | 193.0132 | 193.222 | 193.6133
517.8479 | 114.7399 | 662.7783 | 81.1154 | 193.2817 | 194.2163 | 194.9157
518.8479 | 114.6668 | 654.359 | 81.1087 | 194.8652 | 195.1304 | 195.2574
519.8479 | 115.0706 | 646.694 | 81.276 | 195.1718 | 196.1234 | 195.527
520.8479 | 114.7407 | 646.13 | 81.1304 | 196.0325 | 197.3628 | 195.104
521.8479 | 114.7897 | 649.678 | 81.3679 | 197.386 | 198.6963 | 194.5516
522.8479 | 114.6682 | 662.1958 | 81.0874 | 198.9341 | 198.9537 | 196.4279
523.8479 | 115.1312 | 656.0374 | 80.9063 | 199.8725 | 200.0383 | 197.2958
524.8479 | 114.9312 | 653.282 | 80.8352 | 201.1744 | 200.7256 | 199.0131
525.8479 | 114.9381 | 643.4259 | 80.9156 | 201.437 | 201.3977 | 200.0501
526.8479 | 115.2052 | 643.2545 | 80.863 | 201.6145 | 202.2311 | 200.7222
527.8479 | 115.706 | 649.2597 | 81.2162 | 202.2318 | 203.3106 | 201.4421
528.8479 | 115.8853 | 639.1022 | 81.7975 | 203.5013 | 203.9641 | 201.8581
529.8479 | 116.0157 | 630.0438 | 81.7341 | 204.5789 | 204.5385 | 201.7073
530.8479 | 116.4002 | 627.9418 | 81.8182 | 204.5708 | 205.7329 | 202.1534
531.8479 | 116.7086 | 646.6036 | 81.6931 | 205.4551 | 206.4909 | 204.7999
532.8479 | 116.6746 | 644.4997 | 81.737 | 206.5387 | 207.0902 | 205.9605
533.8479 | 116.9819 | 652.1161 | 81.9223 | 206.5528 | 207.9352 | 206.6298
534.8479 | 117.4217 | 659.908 | 81.8014 | 206.8406 | 208.7622 | 207.25
535.8479 | 117.5517 | 647.1223 | 81.7526 | 206.8581 | 209.398 | 207.2987
536.8479 | 117.7781 | 638.8047 | 81.7189 | 207.2038 | 209.966 | 207.8087
537.8479 | 117.7154 | 638.3107 | 81.6822 | 207.8079 | 210.1897 | 208.161
538.8479 | 117.8261 | 627.3099 | 81.6786 | 207.9748 | 210.6179 | 208.3756
539.8479 | 117.8346 | 624.8022 | 81.8873 | 208.1787 | 211.0588 | 208.879
540.8479 | 117.7164 | 619.7401 | 81.7387 | 209.1672 | 212.0599 | 209.5394
541.8479 | 117.79 | 629.8593 | 81.7935 | 209.8688 | 212.2007 | 210.1522
542.8479 | 117.8339 | 607.7297 | 81.6814 | 210.8963 | 212.5075 | 210.8416
543.8479 | 117.783 | 606.4195 | 81.7322 | 212.116 | 213.2502 | 211.2225
544.8479 | 117.998 | 604.5835 | 81.6285 | 213.0867 | 214.0657 | 211.6165
545.8479 | 118.3595 | 606.0078 | 81.7078 | 213.5565 | 214.3585 | 212.9545
546.8479 | 118.3323 | 585.4799 | 81.8137 | 214.2228 | 214.2896 | 213.6803
547.8479 | 118.2516 | 582.0904 | 82.1025 | 214.9472 | 214.7513 | 214.7215
548.8479 | 118.1376 | 589.8852 | 81.9679 | 215.493 | 215.0906 | 216.2009
549.8479 | 117.6791 | 596.8466 | 81.9903 | 215.4661 | 215.5349 | 215.7874
550.8479 | 117.5434 | 599.6732 | 82.3073 | 215.8381 | 215.812 | 217.2923
551.8479 | 117.4655 | 593.7954 | 82.1613 | 215.3294 | 216.4623 | 217.4904
552.8479 | 117.2999 | 590.9889 | 82.2383 | 215.218 | 217.1073 | 219.2191
553.8479 | 117.176 | 598.5321 | 82.4994 | 215.419 | 217.6722 | 220.2627
554.8479 | 116.8717 | 618.5043 | 82.5962 | 216.0941 | 217.5002 | 221.0013
555.8479 | 117.01 | 616.1782 | 82.8122 | 216.3435 | 217.535 | 222.2443
556.8479 | 117.3283 | 618.4355 | 82.9883 | 216.4435 | 217.6321 | 223.611
557.8479 | 117.4487 | 628.9116 | 83.1027 | 216.5697 | 217.668 | 224.4215
558.8479 | 117.6266 | 634.0096 | 83.1522 | 216.3311 | 217.9301 | 224.0817
559.8479 | 117.8382 | 629.7165 | 83.4809 | 215.9998 | 218.6789 | 222.7656
560.8479 | 117.9828 | 637.1689 | 83.4297 | 215.7576 | 219.0074 | 221.5558
561.8479 | 118.1781 | 631.9782 | 83.8391 | 216.9313 | 219.57 | 220.3513
562.8479 | 118.4408 | 641.7844 | 83.8326 | 217.3012 | 219.712 | 220.622
563.8479 | 118.4317 | 653.9224 | 84.0876 | 217.8502 | 220.2257 | 220.5252
564.8479 | 118.4358 | 648.6934 | 83.9253 | 218.6309 | 220.6283 | 221.6782
565.8479 | 118.4716 | 658.6977 | 84.2106 | 218.8771 | 221.3556 | 221.7697
566.8479 | 118.6438 | 665.884 | 84.5876 | 218.8892 | 221.4167 | 220.917
567.8479 | 118.7756 | 664.1654 | 84.729 | 218.3979 | 221.752 | 220.384
568.8479 | 118.8845 | 677.1766 | 85.0431 | 218.0841 | 221.9258 | 220.9805
569.8479 | 119.2511 | 673.6893 | 85.2292 | 218.0716 | 221.9798 | 220.9882
570.8479 | 119.5543 | 677.4488 | 85.408 | 217.8623 | 221.9526 | 220.8522
571.8479 | 120.0192 | 683.0072 | 85.8021 | 217.6722 | 222.4822 | 220.5934
572.8479 | 120.0993 | 697.1532 | 85.7439 | 217.5341 | 222.6518 | 220.7853
573.8479 | 120.1539 | 695.1444 | 86.1081 | 217.2555 | 222.8377 | 220.4759
574.8479 | 120.0789 | 707.3502 | 86.151 | 217.9096 | 223.0359 | 220.2795
575.8479 | 120.3629 | 700.1377 | 86.1004 | 218.8337 | 223.3686 | 220.6394
576.8479 | 120.4817 | 696.5766 | 85.9903 | 218.6655 | 223.5987 | 220.1924
577.8479 | 120.5446 | 698.4088 | 85.8647 | 218.5678 | 223.5167 | 221.7866
578.8479 | 120.487 | 702.7444 | 86.0557 | 218.7735 | 223.8251 | 222.1036
579.8479 | 120.4727 | 711.0682 | 86.0566 | 219.3486 | 224.0933 | 222.0799
580.8479 | 120.3969 | 711.957 | 85.9737 | 219.5182 | 224.4205 | 222.1709
581.8479 | 120.6419 | 704.3456 | 86.0095 | 219.4902 | 224.5522 | 221.2847
582.8479 | 120.7651 | 710.173 | 86.2133 | 219.997 | 225.0118 | 221.3931
583.8479 | 121.3078 | 701.6484 | 86.4896 | 220.711 | 224.8169 | 220.9886
584.8479 | 121.6448 | 684.1588 | 86.7085 | 221.3115 | 224.5354 | 220.7274
585.8479 | 121.8758 | 670.9616 | 86.9057 | 221.1532 | 224.8619 | 220.9049
586.8479 | 122.0748 | 670.3217 | 86.9107 | 221.5061 | 225.0808 | 220.6957
587.8479 | 122.0048 | 653.1505 | 87.2748 | 221.9798 | 225.5326 | 220.2112
588.8479 | 121.9676 | 661.4001 | 87.4914 | 222.7215 | 226.1693 | 221.3031
589.8479 | 122.0912 | 672.7231 | 87.5158 | 223.3459 | 227.2704 | 221.8572
590.8479 | 122.2686 | 668.0831 | 87.7464 | 223.5971 | 228.0556 | 222.2371
591.8479 | 122.4047 | 675.6067 | 87.6617 | 223.3877 | 227.7867 | 222.165
592.8479 | 122.346 | 660.3767 | 87.733 | 223.5313 | 228.3959 | 222.1953
593.8479 | 122.4991 | 649.3842 | 87.9356 | 224.2133 | 228.8841 | 222.5756
594.8479 | 122.4259 | 659.688 | 87.9697 | 225.3014 | 228.8665 | 223.1723
595.8479 | 122.5816 | 677.1365 | 88.4035 | 226.5508 | 228.9059 | 223.3921
596.8479 | 123.0702 | 675.5398 | 88.7401 | 226.8368 | 229.4518 | 223.9543
597.8479 | 123.1166 | 675.7104 | 88.6299 | 227.5308 | 229.3511 | 224.1481
598.8479 | 123.286 | 665.8351 | 88.8434 | 227.4737 | 229.5738 | 224.5607
599.8479 | 123.2337 | 654.7015 | 88.7564 | 227.1921 | 230.0683 | 224.3599
600.8479 | 123.3812 | 642.2012 | 88.8816 | 227.516 | 231.0823 | 224.174
601.8479 | 123.6064 | 634.7845 | 89.2604 | 228.0477 | 231.7805 | 226.9829
602.8479 | 123.5788 | 627.8925 | 89.3603 | 228.4381 | 231.9788 | 227.3713
603.8479 | 123.5506 | 630.083 | 89.5227 | 228.3939 | 232.311 | 227.022
604.8479 | 123.6567 | 629.6832 | 89.5406 | 228.1592 | 232.2404 | 226.5608
605.8479 | 123.7247 | 633.561 | 89.748 | 228.8919 | 232.7903 | 227.0104
606.8479 | 124.0631 | 635.5564 | 90.0159 | 229.2748 | 233.2611 | 227.5306
607.8479 | 124.2862 | 633.195 | 90.5373 | 229.2905 | 233.187 | 228.1934
608.8479 | 124.4233 | 626.8951 | 90.7613 | 230.175 | 233.1259 | 229.4048
609.8479 | 124.6212 | 628.9145 | 90.9681 | 230.6815 | 233.4603 | 230.9637
610.8479 | 124.8632 | 614.6751 | 91.0496 | 230.3719 | 234.0966 | 232.1015
611.8479 | 124.7399 | 592.285 | 91.077 | 230.3611 | 234.868 | 233.3004
612.8479 | 125.0065 | 587.5283 | 91.3042 | 230.8488 | 235.3843 | 236.5218
613.8479 | 125.0519 | 571.738 | 91.281 | 230.7906 | 235.3791 | 237.1786
614.8479 | 125.0871 | 586.1211 | 91.6936 | 230.8312 | 235.8212 | 238.1766
615.8479 | 125.0476 | 587.8946 | 91.5353 | 230.8298 | 236.4876 | 238.4759
616.8479 | 125.3944 | 584.7459 | 91.7218 | 230.9601 | 236.8716 | 239.3657
617.8479 | 125.4379 | 588.7602 | 91.7082 | 231.2235 | 237.3939 | 240.2354
618.8479 | 125.5636 | 581.8085 | 91.8098 | 231.647 | 237.8677 | 239.7081
619.8479 | 125.7245 | 573.2442 | 92.2804 | 231.7598 | 238.1934 | 239.7617
620.8479 | 125.5853 | 560.027 | 92.4826 | 232.6077 | 237.904 | 240.018
621.8479 | 125.2666 | 574.3201 | 93.0647 | 233.3328 | 238.2368 | 241.1585
622.8479 | 125.0894 | 551.0839 | 93.1301 | 233.5256 | 239.8544 | 241.3608
623.8479 | 124.9223 | 544.4163 | 93.0241 | 233.9121 | 239.6826 | 241.7951
624.8479 | 125.0646 | 552.9643 | 93.4632 | 234.2022 | 239.3155 | 242.1589
625.8479 | 125.201 | 582.9476 | 93.8167 | 234.0499 | 238.1898 | 243.6568
626.8479 | 125.5343 | 585.6442 | 94.1251 | 234.9051 | 238.2109 | 243.9445
627.8479 | 126.0679 | 592.7192 | 94.3247 | 234.7422 | 237.6287 | 244.6556
628.8479 | 125.8616 | 592.2331 | 94.4894 | 235.3956 | 236.8896 | 244.3825
629.8479 | 125.6272 | 595.7285 | 94.7193 | 235.6838 | 232.3504 | 243.6125
630.8479 | 125.5532 | 604.7926 | 94.8566 | 235.6729 | 229.459 | 245.2162
631.8479 | 125.4555 | 578.888 | 94.9813 | 236.2999 | 226.8945 | 245.7109
632.8479 | 125.5701 | 566.4444 | 94.7888 | 236.8102 | 224.8479 | 245.6979
633.8479 | 125.6136 | 567.8795 | 95.0329 | 236.5678 | 222.9621 | 247.0625
634.8479 | 125.9377 | 578.2212 | 95.3502 | 237.4101 | 221.3658 | 248.0138
635.8479 | 125.8322 | 568.4709 | 95.2826 | 237.8503 | 220.265 | 247.7866
636.8479 | 125.8231 | 566.883 | 95.1818 | 237.7804 | 219.8099 | 247.1099
637.8479 | 125.9018 | 560.9199 | 95.3594 | 237.5166 | 219.0993 | 247.0558
638.8479 | 125.9602 | 568.591 | 95.7144 | 237.267 | 218.0489 | 247.9586
639.8479 | 126.3791 | 561.231 | 95.6637 | 237.5022 | 216.8387 | 247.7419
640.8479 | 126.5999 | 557.7563 | 95.5654 | 237.3009 | 215.9356 | 248.487
641.8635 | 126.7415 | 544.8978 | 95.9807 | 237.764 | 215.9988 | 248.2749
642.8479 | 127.0077 | 552.5141 | 96.3197 | 238.069 | 216.1824 | 247.6764
643.8479 | 127.295 | 552.257 | 96.5603 | 239.3872 | 215.9685 | 248.1468
644.8479 | 127.625 | 545.6819 | 96.6519 | 239.9452 | 215.6394 | 249.1673
645.8479 | 128.0794 | 553.4116 | 96.6974 | 241.3641 | 215.084 | 250.8294
646.8479 | 128.5087 | 583.3619 | 96.7102 | 241.4935 | 214.62 | 251.4325
647.8479 | 128.6784 | 578.3708 | 96.7475 | 241.5027 | 214.2074 | 251.5218
648.8479 | 128.6483 | 564.9104 | 96.6571 | 241.9533 | 214.325 | 252.1855
649.8479 | 128.4542 | 555.7895 | 96.7207 | 242.2736 | 214.2744 | 253.096
650.8479 | 128.4761 | 553.5256 | 96.8322 | 242.0659 | 213.9391 | 255.3546
651.8479 | 128.7079 | 554.0228 | 96.8578 | 242.121 | 213.8813 | 255.3345
652.8479 | 129.4238 | 552.5608 | 96.8376 | 242.7001 | 213.928 | 255.5949
653.8479 | 129.9533 | 563.7508 | 97.182 | 243.4791 | 214.0738 | 255.2855
654.8479 | 129.9029 | 552.7661 | 97.7012 | 242.9195 | 214.1587 | 256.596
655.8479 | 129.8115 | 544.0496 | 97.7721 | 243.0822 | 214.2895 | 256.4174
656.8479 | 129.6642 | 569.1323 | 97.8789 | 242.6274 | 214.3429 | 257.0708
657.8479 | 129.6258 | 549.7571 | 97.6691 | 242.5329 | 214.3102 | 258.0485
658.8479 | 129.7306 | 547.1343 | 98.1366 | 242.4618 | 214.155 | 258.4415
659.8479 | 129.5398 | 570.1144 | 98.2073 | 242.3506 | 214.2269 | 258.3087
660.8479 | 129.7876 | 581.1193 | 98.6404 | 242.3825 | 214.0283 | 258.9119
661.8479 | 130.4217 | 575.2319 | 99.3017 | 242.4914 | 213.6696 | 258.9799
662.8479 | 130.6522 | 579.121 | 99.5902 | 243.2954 | 213.3023 | 259.7882
663.8479 | 131.1347 | 584.8426 | 99.512 | 243.4484 | 213.1182 | 259.2223
664.8479 | 131.4679 | 571.07 | 99.6502 | 243.5913 | 213.1088 | 258.8851
665.8479 | 131.4251 | 556.5464 | 99.4898 | 243.5738 | 213.0243 | 258.6547
666.8479 | 131.6269 | 538.2806 | 99.6136 | 243.8771 | 212.9506 | 260.292
667.8479 | 131.5264 | 536.0632 | 99.7538 | 244.1696 | 212.6205 | 260.8816
668.8479 | 131.5914 | 543.5021 | 100.0769 | 244.6236 | 212.0969 | 261.4505
669.8479 | 131.7373 | 539.1706 | 100.3214 | 245.3713 | 211.5577 | 263.1037
670.8479 | 132.0283 | 541.4898 | 100.6165 | 245.4019 | 211.2636 | 264.0229
671.8479 | 132.1446 | 544.9485 | 100.7384 | 245.6511 | 211.0365 | 264.4944
672.8479 | 132.5306 | 545.2712 | 100.6762 | 245.5144 | 210.7197 | 263.7643
673.8479 | 132.8233 | 555.4897 | 100.7458 | 245.3454 | 210.4175 | 265.2716
674.8479 | 132.894 | 552.6394 | 100.689 | 245.6262 | 210.2169 | 264.8672
675.8479 | 133.0319 | 559.1303 | 100.7439 | 246.3456 | 209.7079 | 264.097
676.8479 | 133.3141 | 555.6256 | 101.0401 | 246.0857 | 209.1346 | 263.3607
677.8479 | 133.7716 | 554.4891 | 101.0771 | 246.1263 | 208.9155 | 263.5435
678.8479 | 133.9941 | 555.296 | 101.1254 | 245.4803 | 209.2868 | 264.4907
679.8479 | 134.147 | 579.5535 | 101.3359 | 245.5091 | 209.328 | 264.5602
680.8479 | 134.1921 | 583.4112 | 101.4134 | 245.1152 | 209.3497 | 264.3508
681.8479 | 134.052 | 572.7746 | 101.6353 | 243.6956 | 209.3074 | 265.4255
682.8479 | 133.8739 | 560.102 | 102.1564 | 240.9767 | 209.2675 | 265.8167
683.8479 | 134.1326 | 569.7519 | 102.3684 | 238.6067 | 209.0922 | 266.0156
684.8479 | 134.4294 | 588.0313 | 102.4906 | 235.475 | 208.8802 | 267.2004
685.8479 | 134.7277 | 571.224 | 102.8038 | 232.5302 | 208.6991 | 267.6647
686.8479 | 134.708 | 588.8358 | 102.9314 | 229.8471 | 208.7033 | 267.2509
687.8479 | 135.1649 | 607.1254 | 102.9065 | 227.499 | 208.7674 | 267.0254
688.8479 | 135.3462 | 632.2984 | 102.8938 | 225.4285 | 209.2047 | 266.2131
689.8479 | 135.653 | 642.9464 | 102.6609 | 223.2636 | 209.7603 | 264.9777
690.8479 | 135.6554 | 644.1809 | 102.5933 | 222.4496 | 210.0823 | 264.1694
691.8479 | 135.5961 | 624.2311 | 102.8224 | 221.3094 | 210.2411 | 263.6315
692.8479 | 135.5134 | 598.7085 | 102.8285 | 220.2849 | 210.7746 | 263.4722
693.8479 | 135.4054 | 580.1278 | 102.6359 | 218.8421 | 211.1628 | 263.8449
694.8479 | 135.0989 | 573.5993 | 102.8916 | 217.6448 | 211.5869 | 264.3409
695.8479 | 135.0858 | 557.518 | 102.9947 | 216.6673 | 211.0984 | 264.7356
696.8479 | 135.1142 | 570.3833 | 103.3702 | 215.5804 | 211.6291 | 264.9411
697.8479 | 135.3601 | 580.2853 | 103.5814 | 214.6306 | 212.5754 | 266.8307
698.8479 | 136.127 | 596.4252 | 103.9074 | 213.4704 | 213.5537 | 266.5348
699.8479 | 136.1407 | 590.0641 | 103.9462 | 212.9334 | 214.6191 | 266.708
700.8479 | 136.6142 | 602.1196 | 103.8622 | 214.0623 | 218.8127 | 267.1152
701.8479 | 137.1507 | 594.8469 | 103.8672 | 217.111 | 224.0039 | 266.562
702.8479 | 137.4207 | 596.1224 | 104.3163 | 220.178 | 227.9495 | 266.935
703.8479 | 137.6955 | 576.8063 | 104.4748 | 223.7681 | 231.2905 | 267.1326
704.8479 | 137.5878 | 580.2407 | 104.9028 | 226.8434 | 234.4743 | 267.1041
705.8479 | 137.8078 | 569.563 | 104.7413 | 229.4947 | 236.646 | 267.7656
706.8479 | 138.125 | 571.6576 | 104.8692 | 231.9726 | 238.4991 | 268.5913
707.8479 | 138.2855 | 576.1738 | 105.2398 | 234.2948 | 240.4089 | 268.2915
708.8479 | 138.3322 | 571.893 | 105.0739 | 235.9757 | 242.206 | 267.7194
709.8479 | 138.8319 | 573.9788 | 105.0937 | 237.3892 | 243.7879 | 267.3531
710.8479 | 139.2247 | 571.7005 | 105.0575 | 238.9811 | 245.0321 | 267.0471
711.8479 | 139.4006 | 573.5339 | 104.7964 | 240.6325 | 246.4755 | 267.2192
712.8479 | 139.4978 | 545.0401 | 104.7069 | 242.0629 | 247.7846 | 266.925
713.8479 | 139.942 | 533.885 | 104.7825 | 243.527 | 249.0766 | 266.6613
714.8479 | 139.7924 | 530.1935 | 104.7306 | 245.3163 | 250.413 | 266.4859
715.8479 | 139.8557 | 545.7618 | 105.2546 | 246.7308 | 251.1279 | 266.258
716.8479 | 139.9162 | 539.5637 | 105.4613 | 248.0377 | 251.8368 | 266.6104
717.8479 | 139.9275 | 539.5578 | 105.7668 | 249.9004 | 252.5214 | 267.4281
718.8479 | 139.9628 | 546.4908 | 105.7761 | 250.9853 | 253.564 | 267.7791
719.8479 | 140.1646 | 551.2872 | 105.6338 | 251.4892 | 254.5934 | 267.5394
720.8479 | 140.1472 | 562.9344 | 105.8732 | 251.8898 | 255.2913 | 267.4086
721.8479 | 140.1174 | 561.2052 | 106.252 | 252.4598 | 255.8911 | 267.2351
722.8479 | 140.0257 | 560.5072 | 106.3396 | 252.9944 | 256.2339 | 267.1524
723.8479 | 140.045 | 543.9329 | 106.2167 | 254.2172 | 256.6239 | 268.3669
724.8479 | 139.837 | 536.1419 | 106.3971 | 254.7779 | 256.9609 | 268.2823
725.8479 | 139.5124 | 544.0454 | 106.7657 | 255.0083 | 257.196 | 269.2326
726.8479 | 139.4849 | 536.8532 | 106.8641 | 255.1994 | 257.01 | 270.9176
727.8479 | 139.2269 | 545.2409 | 106.7622 | 255.8468 | 256.9959 | 271.9617
728.8479 | 139.2935 | 562.0536 | 106.8734 | 256.3173 | 256.9829 | 273.3022
729.8479 | 139.2421 | 562.0865 | 106.7808 | 256.5407 | 257.5683 | 274.4959
730.8479 | 139.7157 | 572.7101 | 106.6876 | 256.828 | 257.797 | 274.5078
731.8479 | 139.9427 | 544.3743 | 106.8387 | 257.1214 | 257.8353 | 274.0533
732.8479 | 139.9944 | 539.5208 | 107.1634 | 258.1054 | 257.4692 | 274.8723
733.8479 | 139.9423 | 523.9196 | 107.4683 | 258.6194 | 257.9513 | 274.2103
734.8479 | 140.3587 | 528.2148 | 107.3803 | 258.7319 | 258.5929 | 273.5127
735.8479 | 140.9159 | 519.4514 | 107.408 | 259.4851 | 258.4321 | 272.9404
736.8479 | 141.1619 | 536.546 | 107.3912 | 259.577 | 258.7668 | 272.8146
737.8479 | 141.5198 | 553.6375 | 107.9132 | 259.9705 | 258.9793 | 272.8032
738.8479 | 141.722 | 536.4307 | 108.4278 | 260.2324 | 259.5945 | 272.2076
739.8479 | 141.6877 | 526.7371 | 108.7802 | 260.671 | 260.0792 | 271.4606
740.8479 | 142.0605 | 518.6998 | 108.8609 | 260.6807 | 260.628 | 271.0718
741.8479 | 142.4999 | 535.6944 | 109.0453 | 261.1004 | 260.9366 | 272.3388
742.8479 | 142.504 | 529.8042 | 109.1346 | 261.0771 | 261.2527 | 273.4293
743.8479 | 142.517 | 535.4866 | 109.3485 | 261.2821 | 261.5272 | 274.6944
744.8479 | 142.6111 | 539.1489 | 109.2881 | 261.3777 | 262.277 | 275.2673
745.8479 | 142.5936 | 536.5828 | 109.4325 | 261.2904 | 262.7636 | 275.0523
746.8479 | 142.4471 | 532.0706 | 109.2285 | 261.2508 | 262.6813 | 275.7049
747.8479 | 142.3223 | 517.1608 | 109.3987 | 261.0246 | 262.6454 | 275.7111
748.8479 | 142.0261 | 543.3452 | 109.615 | 261.2114 | 262.5498 | 275.6057
749.8479 | 142.0266 | 553.7697 | 109.5059 | 261.1523 | 262.3361 | 275.3143
750.8479 | 142.0958 | 573.2513 | 109.4885 | 261.3678 | 262.304 | 274.3095
751.8479 | 141.8934 | 562.0895 | 109.4652 | 261.2493 | 262.3225 | 273.9673
752.8479 | 141.7753 | 560.1343 | 109.8347 | 260.9683 | 261.9865 | 273.5002
753.8479 | 141.7779 | 555.0722 | 110.2114 | 261.2129 | 262.1774 | 273.8287
754.8479 | 141.691 | 545.51 | 110.3984 | 261.3678 | 262.9102 | 273.9356
755.8479 | 141.4094 | 540.1396 | 110.4674 | 261.8167 | 263.3764 | 273.3774
756.8479 | 141.154 | 539.2233 | 110.7405 | 262.0635 | 263.3025 | 274.4578
757.8479 | 140.9312 | 552.3586 | 111.3053 | 261.8763 | 263.4013 | 274.25
758.8479 | 140.9802 | 541.2638 | 111.4581 | 261.6454 | 263.6654 | 273.9311
759.8479 | 141.0524 | 543.4037 | 111.2748 | 261.5787 | 263.7416 | 274.6282
760.8479 | 140.876 | 559.8012 | 111.2572 | 261.3306 | 263.706 | 273.9158
761.8479 | 140.5938 | 554.1618 | 111.6011 | 261.2434 | 263.7182 | 273.6419
762.8479 | 140.7877 | 560.1248 | 111.8509 | 260.983 | 264.0134 | 274.0051
763.8479 | 140.8622 | 574.9787 | 111.875 | 260.5763 | 264.1209 | 274.2863
764.8479 | 140.7229 | 579.3433 | 111.7385 | 260.8118 | 264.1907 | 274.1366
765.8479 | 140.5883 | 577.7749 | 111.7556 | 260.612 | 264.3804 | 274.8586
766.8479 | 140.6348 | 590.2169 | 111.9006 | 260.4815 | 264.5847 | 274.2009
767.8479 | 140.8826 | 584.8861 | 111.7649 | 260.2198 | 265.0773 | 274.7074
768.8479 | 141.1689 | 575.5901 | 111.9209 | 260.2831 | 265.1537 | 274.5668
769.8479 | 141.7542 | 570.3658 | 112.1537 | 260.561 | 265.4646 | 274.2074
770.8479 | 141.9189 | 554.4756 | 112.213 | 260.8007 | 265.4833 | 273.5205
771.8479 | 142.1257 | 550.7189 | 111.8626 | 261.413 | 264.7561 | 272.95
772.8479 | 142.3988 | 546.5454 | 112.0839 | 262.2297 | 264.6309 | 272.6966
773.8479 | 142.6658 | 540.3364 | 112.1298 | 262.1207 | 264.7164 | 272.9053
774.8479 | 142.6054 | 527.5498 | 112.5006 | 262.2567 | 265.2575 | 272.4969
775.8479 | 142.6703 | 552.6056 | 112.6653 | 262.2933 | 264.9396 | 272.7346
776.8479 | 142.8528 | 554.0025 | 112.7482 | 262.2258 | 264.7955 | 273.8812
777.8479 | 143.2139 | 562.5806 | 112.8078 | 261.8543 | 264.6846 | 274.3611
778.8479 | 143.2835 | 559.8684 | 113.1275 | 261.8757 | 264.7765 | 274.1039
779.8479 | 143.2516 | 537.9261 | 113.2626 | 261.8633 | 264.4397 | 274.0141
780.8479 | 143.2112 | 529.1691 | 113.3637 | 261.9457 | 264.5193 | 273.6098
781.8479 | 143.1041 | 533.459 | 113.3813 | 262.0959 | 264.436 | 274.5192
782.8479 | 143.0047 | 527.5667 | 113.1509 | 262.0329 | 264.6012 | 274.2484
783.8479 | 143.4551 | 532.7498 | 113.0714 | 261.841 | 265.0465 | 274.7194
784.8479 | 143.9281 | 522.4619 | 112.9448 | 261.4786 | 265.5605 | 274.7949
785.8479 | 143.8591 | 547.6013 | 112.705 | 261.2653 | 266.2746 | 274.3799
786.8479 | 143.4307 | 554.2814 | 113.089 | 261.3016 | 266.4397 | 274.2984
787.8479 | 143.6294 | 542.6755 | 112.8667 | 261.1585 | 266.6856 | 275.4026
788.8479 | 143.3964 | 535.0452 | 112.9224 | 261.2303 | 266.9758 | 275.3877
789.8479 | 143.1237 | 547.3729 | 112.5833 | 261.1794 | 266.6461 | 275.2607
790.8479 | 142.6596 | 545.3357 | 112.8943 | 261.2896 | 265.967 | 274.7269
791.8479 | 142.2021 | 541.2644 | 113.2155 | 261.4927 | 266.0691 | 274.3434
792.8479 | 142.4183 | 529.4127 | 113.2388 | 262.1995 | 266.7707 | 274.519
793.8479 | 142.2473 | 541.4632 | 113.8007 | 262.4078 | 266.7928 | 274.8582
794.8479 | 141.8831 | 542.3033 | 113.9455 | 262.3507 | 266.4866 | 274.7095
795.8479 | 141.9127 | 543.8231 | 114.4129 | 262.5705 | 266.7009 | 275.3258
796.8479 | 142.2366 | 533.7766 | 114.4069 | 262.1946 | 266.5391 | 275.9631
797.8479 | 142.5723 | 540.4467 | 114.3216 | 262.1445 | 266.5234 | 275.7129
798.8479 | 142.7512 | 543.808 | 114.2018 | 261.9523 | 266.6651 | 275.1899
799.8479 | 143.2059 | 549.7685 | 114.2541 | 261.8343 | 266.9323 | 274.6427
800.8479 | 143.4054 | 563.7324 | 114.4773 | 261.5368 | 266.7514 | 273.9705
801.8479 | 143.5986 | 577.1946 | 115.0363 | 261.671 | 266.8832 | 273.2306
802.8479 | 143.9708 | 592.6333 | 115.0922 | 261.7982 | 267.0353 | 272.8007
803.8479 | 144.4055 | 602.4028 | 114.6943 | 261.9559 | 267.2373 | 272.3073
804.8479 | 144.9187 | 617.7002 | 114.9345 | 261.9648 | 267.1907 | 272.2474
805.8479 | 145.3488 | 625.3702 | 115.1726 | 262.1718 | 267.5693 | 272.0969
806.8479 | 145.6841 | 626.1046 | 115.59 | 262.9085 | 267.4748 | 272.2876
807.8479 | 146.3591 | 618.4543 | 115.805 | 263.935 | 267.6369 | 272.7915
808.8479 | 146.8127 | 602.2684 | 116.0008 | 264.3216 | 267.6336 | 272.7793
809.8479 | 146.9318 | 601.8668 | 115.7631 | 264.8825 | 268.1603 | 273.7073
810.8479 | 147.3546 | 600.5805 | 116.2362 | 265.2658 | 268.6708 | 273.9257
811.8479 | 147.9748 | 602.374 | 116.8913 | 265.7339 | 268.8534 | 274.1074
812.8479 | 148.1617 | 606.5363 | 117.2762 | 266.1163 | 268.768 | 274.9907
813.8479 | 148.1516 | 588.6397 | 117.3253 | 265.9474 | 269.1413 | 275.8082
814.8479 | 148.3205 | 588.8146 | 117.4309 | 266.2376 | 269.8443 | 276.177
815.8479 | 148.2877 | 590.3669 | 117.4327 | 266.2877 | 269.9644 | 276.5294
816.8479 | 148.4403 | 602.0227 | 117.3737 | 266.3974 | 270.0902 | 276.473
817.8479 | 148.2934 | 595.3442 | 117.1973 | 266.9999 | 270.3495 | 276.516
818.8479 | 148.3593 | 596.1767 | 117.6777 | 267.2831 | 270.4079 | 276.1223
819.8479 | 148.1679 | 576.1221 | 117.6506 | 267.6759 | 270.5733 | 275.6852
820.8479 | 147.9583 | 573.0362 | 117.7372 | 268.1005 | 271.0526 | 275.5305
821.8479 | 147.8135 | 567.6527 | 117.6136 | 268.4787 | 271.6614 | 275.4867
822.8479 | 147.5941 | 564.4781 | 117.8054 | 268.9017 | 271.9955 | 275.5883
823.8479 | 147.48 | 560.3202 | 117.7297 | 268.8805 | 272.2447 | 277.2097
824.8479 | 147.2943 | 552.9479 | 117.9091 | 269.0832 | 272.3062 | 278.2613
825.8479 | 147.3789 | 548.9533 | 118.1037 | 269.0133 | 272.6745 | 279.2818
826.8479 | 147.1111 | 542.352 | 118.1306 | 269.3096 | 272.8955 | 280.5
827.8479 | 147.0821 | 534.7708 | 118.4668 | 269.4244 | 273.1401 | 281.8873
828.8479 | 146.9067 | 548.2279 | 118.7114 | 269.439 | 273.1907 | 282.6632
829.8479 | 147.1973 | 562.3416 | 118.5071 | 269.1731 | 273.3078 | 282.3303
830.8479 | 147.1904 | 549.9151 | 118.7696 | 268.7249 | 273.238 | 281.8865
831.8479 | 147.2886 | 553.5754 | 118.477 | 268.9471 | 272.8464 | 281.7137
832.8479 | 147.2989 | 549.3958 | 118.9829 | 268.9117 | 272.8222 | 281.7957
833.8479 | 147.232 | 556.1697 | 119.1223 | 268.884 | 273.3822 | 281.6912
834.8479 | 147.3554 | 552.2514 | 118.9076 | 268.5179 | 274.5559 | 281.3997
835.8479 | 147.3549 | 562.2447 | 119.4552 | 268.2644 | 275.0364 | 281.703
836.8479 | 147.2838 | 553.1588 | 120.0736 | 268.02 | 274.8259 | 281.5118
837.8479 | 146.9675 | 554.7337 | 120.55 | 267.8793 | 274.4753 | 281.2511
838.8479 | 147.0209 | 556.4437 | 120.2058 | 268.1545 | 273.9466 | 281.8929
839.8479 | 147.0847 | 545.4558 | 120.2106 | 268.5521 | 273.415 | 281.601
840.8479 | 147.0229 | 539.529 | 120.3102 | 268.6294 | 273.3331 | 282.3481
841.8479 | 147.1302 | 542.0847 | 120.4073 | 268.5222 | 273.0814 | 281.9917
842.8479 | 146.9752 | 546.1907 | 120.3504 | 268.4356 | 272.9128 | 283.2632
843.8479 | 146.9946 | 562.1211 | 120.7849 | 268.2713 | 273.7086 | 283.478
844.8479 | 147.2529 | 576.8831 | 121.4057 | 268.0418 | 274.4454 | 283.9363
845.8479 | 147.2824 | 564.3127 | 121.7232 | 267.9145 | 274.4151 | 283.6106
846.8479 | 147.5638 | 577.2593 | 121.8939 | 267.8646 | 273.8912 | 284.096
847.8479 | 147.5446 | 563.4113 | 122.2939 | 267.6932 | 273.6225 | 284.3053
848.8479 | 147.4715 | 551.8154 | 122.1164 | 267.6851 | 273.503 | 284.3997
849.8479 | 147.3315 | 558.8448 | 121.9967 | 267.8977 | 273.4796 | 284.016
850.8479 | 147.142 | 565.3392 | 122.4637 | 268.0619 | 273.41 | 284.3033
851.8479 | 147.021 | 578.4426 | 122.7378 | 268.1123 | 273.0667 | 285.0858
852.8479 | 146.9013 | 586.2284 | 122.9996 | 267.9894 | 272.8878 | 284.3265
853.8479 | 146.9437 | 596.3622 | 122.9515 | 267.9112 | 272.9877 | 283.7261
854.8479 | 146.8314 | 612.1242 | 123.0125 | 267.817 | 273.3719 | 284.3516
855.8479 | 146.9327 | 611.4717 | 123.0978 | 267.5403 | 273.4986 | 283.8402
856.8479 | 146.6371 | 601.7023 | 122.7724 | 267.3561 | 273.5863 | 283.3988
857.8479 | 146.4597 | 591.1392 | 123.2653 | 267.609 | 274.7022 | 283.149
858.8479 | 146.304 | 589.2579 | 123.2021 | 267.8535 | 274.6469 | 282.8053
859.8479 | 146.718 | 592.8198 | 123.034 | 268.2076 | 274.5722 | 282.5958
860.8479 | 146.6929 | 579.684 | 122.8847 | 268.662 | 274.6872 | 282.1628
861.8479 | 146.7913 | 572.7228 | 122.6453 | 268.735 | 274.6756 | 282.2519
862.8479 | 146.7683 | 574.1515 | 122.6315 | 268.8352 | 274.7273 | 282.5109
863.8479 | 146.7259 | 563.2593 | 122.3228 | 268.9818 | 274.8779 | 282.5625
864.8479 | 146.5875 | 564.7251 | 122.2004 | 269.0535 | 274.8789 | 283.0302
865.8479 | 146.5432 | 577.8047 | 122.3675 | 269.2597 | 275.0558 | 282.9233
866.8479 | 146.4107 | 572.5386 | 122.2724 | 269.5842 | 275.4918 | 282.6882
867.8479 | 146.3139 | 576.5179 | 123.0866 | 269.7161 | 275.6916 | 282.3517
868.8479 | 146.0647 | 577.1418 | 123.3707 | 269.7762 | 275.7163 | 282.141
869.8479 | 145.9722 | 585.6724 | 123.2674 | 270.2949 | 275.4726 | 282.7808
870.8479 | 145.9919 | 601.6882 | 123.3009 | 270.5494 | 275.2386 | 282.6204
871.8479 | 146.0902 | 613.5025 | 123.712 | 270.9332 | 275.2578 | 283.0729
872.8479 | 146.3446 | 608.3812 | 123.9676 | 271.2713 | 275.2226 | 282.5191
873.8479 | 146.4355 | 618.6117 | 124.3533 | 270.9782 | 275.3665 | 282.5363
874.8479 | 146.4091 | 611.8829 | 124.5214 | 270.9501 | 275.6605 | 283.6053
875.8479 | 146.3921 | 598.9055 | 124.8113 | 271.0782 | 275.9127 | 284.3976
876.8479 | 146.5901 | 606.1998 | 124.9124 | 271.5724 | 276.5861 | 284.2407
877.8479 | 146.689 | 605.9204 | 124.6998 | 271.9307 | 276.6338 | 283.7112
878.8479 | 146.8326 | 620.6934 | 124.6293 | 271.8448 | 276.5764 | 283.4153
879.8479 | 147.1931 | 628.423 | 124.9251 | 271.8061 | 276.6641 | 283.9497
880.8479 | 147.237 | 628.6058 | 125.0936 | 271.723 | 276.7635 | 283.8608
881.8479 | 147.2695 | 630.4504 | 124.5867 | 271.585 | 277.2303 | 283.8787
882.8479 | 147.3487 | 614.9156 | 124.6648 | 271.7474 | 277.6346 | 283.6541
883.8479 | 147.756 | 628.0544 | 124.9004 | 272.2822 | 277.4597 | 283.8293
884.8479 | 147.8645 | 637.8396 | 125.0211 | 272.31 | 277.477 | 283.7445
885.8479 | 148.1172 | 626.4133 | 124.8714 | 272.3473 | 277.7312 | 283.5218
886.8479 | 148.3968 | 636.859 | 124.8013 | 272.341 | 277.5967 | 283.4046
887.8479 | 148.7629 | 646.225 | 124.3404 | 272.4128 | 277.5874 | 283.4654
888.8479 | 148.636 | 625.9242 | 124.6163 | 272.7441 | 277.6554 | 283.3347
889.8479 | 148.599 | 632.4528 | 125.0306 | 273.1798 | 277.6544 | 283.8799
890.8479 | 148.4195 | 630.2282 | 125.2978 | 273.1723 | 277.5248 | 283.9647
891.8479 | 148.592 | 625.5616 | 125.6758 | 273.4027 | 277.189 | 284.0077
892.8479 | 148.8766 | 617.7138 | 126.3072 | 273.8342 | 277.6333 | 284.0288
893.8479 | 149.2961 | 617.5956 | 126.4145 | 274.7859 | 277.7793 | 283.8895
894.8479 | 149.4316 | 618.2845 | 126.7897 | 275.2182 | 278.2722 | 283.7716
895.8479 | 149.2849 | 604.0702 | 126.6934 | 275.5468 | 278.2087 | 283.5685
896.8479 | 149.2844 | 605.1045 | 126.8867 | 275.3885 | 278.3412 | 283.4607
897.8479 | 148.9568 | 582.1934 | 127.1501 | 275.7207 | 278.2904 | 284.0024
898.8479 | 148.5321 | 571.4277 | 127.4279 | 275.568 | 278.5302 | 284.0893
899.8479 | 148.7721 | 560.52 | 127.8138 | 275.5024 | 278.556 | 284.2334
900.8479 | 149.4171 | 571.2701 | 127.6396 | 275.2465 | 278.8369 | 284.788
901.8479 | 149.8046 | 565.2986 | 127.28 | 274.9566 | 279.2435 | 284.3178
902.8479 | 149.7756 | 568.2376 | 127.46 | 274.8943 | 279.1305 | 284.2201
903.8479 | 149.9016 | 570.2072 | 127.4249 | 274.739 | 279.3142 | 283.9457
904.8479 | 149.7216 | 564.9152 | 127.5732 | 274.556 | 280.1702 | 283.5802
905.8479 | 149.7529 | 576.0184 | 128.4943 | 274.4141 | 280.0213 | 283.4845
906.8479 | 149.8332 | 593.2322 | 128.3736 | 274.3746 | 279.6161 | 283.3822
907.8479 | 150.0999 | 592.6162 | 128.3923 | 274.4435 | 279.4271 | 283.3302
908.8479 | 150.7911 | 604.8102 | 128.518 | 274.4931 | 279.2667 | 283.05
909.8479 | 151.0899 | 584.5313 | 128.3195 | 274.6031 | 278.8229 | 282.7453
910.8479 | 151.4364 | 593.0182 | 129.0215 | 274.1366 | 278.2419 | 282.9543
911.8479 | 151.4839 | 601.9255 | 129.1674 | 273.8971 | 277.86 | 283.0629
912.8479 | 151.4912 | 583.8302 | 128.9182 | 273.9275 | 277.5545 | 282.9658
913.8479 | 151.3983 | 584.3428 | 128.6429 | 274.1901 | 277.1972 | 283.0169
914.8479 | 151.2322 | 575.524 | 128.342 | 274.0204 | 276.7694 | 283.2709
915.8479 | 151.1822 | 571.7237 | 128.4185 | 274.0063 | 276.8525 | 283.6229
916.8479 | 151.106 | 569.8609 | 129.2344 | 274.0852 | 277.1029 | 283.352
917.8479 | 150.8839 | 571.3458 | 129.0727 | 274.038 | 277.3588 | 284.0482
918.8479 | 150.8751 | 549.504 | 129.8826 | 273.9191 | 277.3093 | 284.2067
919.8479 | 150.9794 | 565.6536 | 130.3669 | 273.5399 | 277.0121 | 284.3697
920.8479 | 150.9089 | 595.8365 | 130.6298 | 273.3508 | 276.5033 | 284.3583
921.8479 | 150.965 | 584.6693 | 130.4674 | 273.2711 | 276.0055 | 284.7866
922.8479 | 151.0217 | 581.7933 | 130.3811 | 273.034 | 275.4795 | 284.5466
923.8479 | 151.1483 | 603.0189 | 130.1827 | 272.6714 | 275.0793 | 284.0385
924.8479 | 151.245 | 594.2305 | 129.9902 | 272.4712 | 274.96 | 283.3387
925.8479 | 151.2195 | 585.7206 | 129.9096 | 272.294 | 274.98 | 282.7628
926.8479 | 151.2327 | 586.7199 | 129.6591 | 272.276 | 274.8192 | 283.215
927.8479 | 151.5616 | 590.0054 | 129.5527 | 272.2606 | 274.5684 | 283.1316
928.8479 | 151.6402 | 579.8826 | 129.0779 | 271.96 | 274.6093 | 282.6693
929.8479 | 151.5913 | 577.3915 | 128.5808 | 271.6242 | 274.6727 | 282.261
930.8479 | 151.7771 | 571.2013 | 128.8514 | 271.2862 | 274.7241 | 281.8317
931.8479 | 151.4482 | 567.619 | 128.5181 | 271.0518 | 275.2279 | 281.9922
932.8479 | 151.3448 | 557.9417 | 128.6376 | 271.0385 | 275.2464 | 281.7847
933.8479 | 151.2316 | 555.4007 | 128.5575 | 271.166 | 274.9933 | 282.1288
934.8479 | 151.2305 | 543.457 | 128.6387 | 271.1538 | 274.8199 | 282.6013
935.8479 | 150.9776 | 534.7171 | 128.7924 | 271.4241 | 274.5332 | 282.6151
936.8479 | 151.0529 | 536.4711 | 128.6358 | 271.4949 | 274.7986 | 282.2651
937.8479 | 151.1451 | 532.5844 | 128.4716 | 271.4626 | 274.8713 | 282.2533
938.8479 | 151.348 | 520.7121 | 128.5405 | 271.4064 | 274.8808 | 281.8662
939.8479 | 151.4266 | 506.2575 | 128.4579 | 271.3337 | 275.513 | 281.4709
940.8479 | 151.2649 | 506.6816 | 128.6884 | 271.0061 | 275.2032 | 282.0336
941.8479 | 151.2161 | 501.7276 | 128.3074 | 270.9539 | 275.2259 | 282.3258
942.8479 | 150.9839 | 492.9164 | 128.2607 | 270.9303 | 275.4052 | 282.0256
943.8479 | 151.0167 | 503.3783 | 128.0249 | 270.6026 | 275.3782 | 281.8022
944.8479 | 151.2086 | 508.8931 | 127.7549 | 270.3992 | 275.2694 | 281.2592
945.8479 | 151.9941 | 500.992 | 128.0248 | 270.456 | 275.6544 | 281.0748
946.8479 | 151.9172 | 501.9734 | 127.9493 | 270.8366 | 275.605 | 280.8053
947.8479 | 152.1941 | 497.8253 | 128.3159 | 270.7065 | 275.607 | 280.6545
948.8479 | 152.2096 | 486.8748 | 128.282 | 270.525 | 276.1638 | 280.3627
949.8479 | 152.276 | 489.1236 | 128.4704 | 270.5402 | 276.4405 | 279.964
950.8479 | 152.1246 | 490.4173 | 128.6008 | 270.9009 | 276.532 | 280.1748
951.8479 | 151.6901 | 490.2841 | 129.0912 | 271.1688 | 276.6362 | 280.1113
952.8479 | 151.4408 | 499.4745 | 128.9619 | 271.5163 | 276.9612 | 279.9852
953.8479 | 151.3656 | 511.8086 | 129.1341 | 271.573 | 277.1453 | 279.9064
954.8479 | 151.4112 | 519.9449 | 129.1509 | 271.9261 | 277.3937 | 280.5611
955.8479 | 151.3414 | 522.828 | 128.8657 | 272.1723 | 277.4474 | 280.9045
956.8479 | 151.1642 | 540.9277 | 128.7925 | 271.9601 | 277.4844 | 280.53
957.8479 | 151.0098 | 552.9827 | 128.8814 | 271.959 | 277.6678 | 280.3887
958.8479 | 150.9421 | 534.6585 | 128.7602 | 271.5968 | 277.6188 | 280.3369
959.8479 | 151.197 | 532.352 | 128.8202 | 271.1355 | 277.6552 | 279.9964
960.8479 | 151.4585 | 545.7935 | 128.6808 | 270.9198 | 277.5549 | 279.8086
961.8479 | 151.5112 | 568.2449 | 128.6021 | 270.7881 | 277.3296 | 279.6816
962.8479 | 151.9839 | 566.1197 | 128.7124 | 270.6839 | 277.3025 | 279.4902
963.8479 | 152.0772 | 564.4042 | 129.0749 | 270.6535 | 277.1929 | 279.2115
964.8479 | 151.9069 | 561.1036 | 129.3786 | 270.5584 | 277.0662 | 279.0829
965.8479 | 152.0043 | 585.1901 | 129.5715 | 270.7785 | 276.9423 | 279.3304
966.8479 | 151.8642 | 569.7749 | 129.7781 | 270.6525 | 277.1541 | 279.9288
967.8479 | 151.7119 | 573.2867 | 129.9061 | 270.8336 | 277.3629 | 279.75
968.8479 | 151.8066 | 571.1981 | 130.5908 | 271.2111 | 277.589 | 279.6273
969.8479 | 151.7348 | 569.8699 | 130.9402 | 271.204 | 277.4674 | 279.4725
970.8479 | 151.7661 | 589.0453 | 131.4313 | 271.0415 | 277.379 | 279.2237
971.8479 | 152.1286 | 590.5835 | 131.9607 | 270.972 | 277.0329 | 278.9606
972.8479 | 152.4086 | 612.4864 | 131.7091 | 271.1527 | 276.8438 | 278.929
973.8479 | 152.7437 | 614.904 | 131.6415 | 270.8001 | 276.8048 | 278.7017
974.8479 | 153.1899 | 624.9037 | 131.6772 | 270.5434 | 276.642 | 278.6317
975.8479 | 153.3517 | 611.3505 | 132.2089 | 270.8447 | 276.5121 | 278.4679
976.8479 | 153.2871 | 603.3868 | 131.8466 | 270.7695 | 276.2852 | 278.4765
977.8479 | 153.1161 | 613.4038 | 132.0089 | 270.7935 | 276.5409 | 278.4538
978.8479 | 153.028 | 612.6287 | 132.442 | 271.019 | 276.3808 | 278.4468
979.8479 | 153.1023 | 598.3942 | 132.6436 | 271.2489 | 276.0883 | 278.3414
980.8479 | 152.9775 | 591.8636 | 133.1216 | 271.2103 | 276.3064 | 278.0557
981.8479 | 153.0439 | 575.2196 | 133.4319 | 271.1096 | 276.185 | 277.9884
982.8479 | 152.931 | 566.9436 | 133.7059 | 271.0948 | 275.8635 | 278.1843
983.8479 | 152.6927 | 568.4761 | 134.2284 | 271.0546 | 275.6487 | 278.2571
984.8479 | 152.6856 | 563.3669 | 134.2141 | 271.1098 | 275.6474 | 279.9233
985.8479 | 153.0131 | 571.3393 | 134.3161 | 270.8349 | 275.7821 | 280.1867
986.8479 | 153.2579 | 556.508 | 134.1317 | 270.6426 | 276.1298 | 280.345
987.8479 | 153.2299 | 553.8945 | 134.6541 | 270.6033 | 276.522 | 280.2538
988.8479 | 153.3392 | 579.5964 | 134.5501 | 270.5232 | 276.7689 | 281.4872
989.8479 | 153.256 | 563.3319 | 134.542 | 270.5619 | 277.1194 | 281.1732
990.8479 | 153.5931 | 575.5478 | 134.659 | 270.6091 | 277.3183 | 280.8906
991.8479 | 153.6695 | 586.4977 | 134.9158 | 270.5382 | 277.363 | 280.5677
992.8479 | 153.5735 | 577.6264 | 134.4707 | 270.3406 | 277.2608 | 280.5314
993.8479 | 153.3087 | 583.8766 | 135.0277 | 270.4989 | 277.3487 | 280.2339
994.8479 | 153.3745 | 586.8732 | 135.049 | 270.5437 | 277.6479 | 279.8957
995.8479 | 153.0647 | 583.0124 | 135.554 | 270.7692 | 277.8642 | 280.7047
996.8479 | 152.9413 | 566.126 | 135.9998 | 270.8378 | 277.72 | 280.5942
997.8479 | 153.0725 | 546.4564 | 135.9838 | 271.2532 | 277.8326 | 280.718
998.8479 | 152.8325 | 533.4344 | 136.4065 | 271.2228 | 277.9644 | 281.6826
999.8479 | 152.7045 | 539.8811 | 136.2663 | 271.0302 | 278.1348 | 282.9249
1000.8479 | 153.0255 | 539.1478 | 136.1598 | 270.9186 | 278.3307 | 282.4702
1001.8479 | 153.4515 | 541.7884 | 135.9802 | 270.9444 | 278.2266 | 282.7531
1002.8479 | 153.3938 | 535.4965 | 135.9074 | 270.8051 | 277.9182 | 282.3202
1003.8479 | 153.1471 | 538.33 | 135.7722 | 270.824 | 277.8747 | 282.5403
1004.8479 | 153.159 | 546.7106 | 135.8879 | 270.7581 | 277.7558 | 282.6945
1005.8479 | 152.794 | 533.4489 | 135.1226 | 270.4649 | 277.7399 | 282.866
1006.8479 | 152.6685 | 534.256 | 135.359 | 270.475 | 277.9281 | 282.7228
1007.8479 | 152.5259 | 535.9657 | 135.6416 | 270.9574 | 278.0722 | 283.6504
1008.8479 | 152.4738 | 543.8386 | 135.421 | 270.6341 | 278.4048 | 283.8084
1009.8479 | 152.2939 | 556.8038 | 135.089 | 270.3521 | 278.3901 | 284.214
1010.8479 | 152.3726 | 549.0947 | 134.6213 | 270.7452 | 278.4718 | 283.7254
1011.8479 | 152.565 | 545.7905 | 134.9621 | 270.5712 | 278.2101 | 284.6761
1012.8479 | 152.6973 | 553.0357 | 134.457 | 270.2691 | 278.0373 | 284.9199
1013.8479 | 152.7433 | 538.7937 | 134.2252 | 270.0687 | 278.0204 | 284.6111
1014.8479 | 152.7531 | 534.5589 | 134.4154 | 269.6254 | 278.6722 | 283.9382
1015.8479 | 153.0633 | 539.4099 | 134.1129 | 269.2174 | 278.4235 | 283.2123
1016.8479 | 153.2115 | 547.0771 | 134.0796 | 268.9902 | 277.8562 | 284.3112
1017.8479 | 153.3175 | 548.4092 | 133.9424 | 269.0028 | 277.2595 | 284.9619
1018.8479 | 152.977 | 540.6964 | 133.8041 | 268.9571 | 276.6271 | 285.5324
1019.8479 | 152.6896 | 536.5381 | 134.2984 | 269.0449 | 276.4585 | 286.378
1020.8479 | 152.3806 | 539.212 | 134.1739 | 268.8886 | 276.2148 | 285.9969
1021.8479 | 151.974 | 552.0306 | 134.1605 | 268.7995 | 276.2292 | 285.3848
1022.8479 | 151.9168 | 548.1212 | 134.5099 | 268.491 | 276.3904 | 284.8954
1023.8479 | 151.9762 | 552.7964 | 134.1799 | 268.6819 | 277.3035 | 284.3705
1024.8479 | 152.0908 | 556.3333 | 134.1061 | 268.4541 | 277.5244 | 284.4431
1025.8479 | 151.9734 | 556.332 | 134.2113 | 268.2009 | 277.4733 | 284.0002
1026.8479 | 151.8018 | 559.6296 | 134.0731 | 267.9827 | 277.3421 | 284.1875
1027.8479 | 151.7954 | 553.7644 | 134.4524 | 268.0269 | 277.1471 | 284.1334
1028.8479 | 151.5711 | 541.4464 | 134.2854 | 267.7683 | 276.7497 | 283.7441
1029.8479 | 151.4741 | 530.9089 | 134.574 | 267.5846 | 276.6784 | 283.5091
1030.8479 | 151.6599 | 523.8751 | 135.1364 | 267.5035 | 277.1206 | 283.4804
1031.8479 | 151.6452 | 517.7953 | 135.5988 | 267.2854 | 277.6216 | 283.5468
1032.8479 | 151.3384 | 500.0513 | 136.2834 | 267.087 | 277.995 | 283.3291
1033.8479 | 151.3785 | 492.5461 | 136.3854 | 267.2682 | 278.065 | 283.627
1034.8479 | 151.3592 | 499.1255 | 136.1984 | 267.0592 | 277.9541 | 283.6868
1035.8479 | 151.2593 | 496.5206 | 136.0096 | 267.196 | 277.9531 | 283.276
1036.8479 | 151.4454 | 496.6922 | 136.1 | 267.4235 | 278.1596 | 282.9802
1037.8479 | 151.4214 | 503.9061 | 135.4462 | 267.5576 | 278.1721 | 282.7059
1038.8479 | 151.8496 | 503.302 | 135.3027 | 267.3685 | 278.0961 | 282.4019
1039.8479 | 152.0192 | 518.4528 | 134.8914 | 267.5787 | 277.8842 | 281.9376
1040.8479 | 152.4829 | 535.5547 | 135.0691 | 267.72 | 277.721 | 282.0615
1041.8479 | 152.6805 | 555.4264 | 134.707 | 268.0612 | 277.8747 | 282.8097
1042.8479 | 152.9838 | 561.8845 | 135.033 | 268.2587 | 277.8484 | 282.6449
1043.8479 | 152.9651 | 573.3264 | 135.1243 | 268.4971 | 277.8633 | 282.5101
1044.8479 | 153.1417 | 575.0503 | 134.8093 | 268.7833 | 277.7762 | 282.0093
1045.8479 | 153.5377 | 596.2087 | 134.6438 | 269.1419 | 277.6817 | 282.0906
1046.8479 | 153.6289 | 586.8195 | 134.2612 | 269.4942 | 277.6602 | 281.6654
1047.8479 | 153.5751 | 578.4803 | 134.1839 | 269.744 | 277.5633 | 281.5354
1048.8479 | 153.5372 | 565.3988 | 134.3977 | 269.6407 | 277.5083 | 281.0122
1049.8479 | 153.5359 | 570.5615 | 134.2781 | 269.6084 | 277.5023 | 280.6301
1050.8479 | 153.8456 | 574.2145 | 134.8004 | 269.2847 | 277.5829 | 280.5946
1051.8479 | 153.918 | 576.8229 | 134.8048 | 268.9743 | 277.5119 | 280.4174
1052.8479 | 153.8193 | 580.8617 | 135.2307 | 268.8541 | 277.5908 | 280.273
1053.8479 | 153.606 | 571.9236 | 135.8948 | 268.6263 | 277.3511 | 279.9343
1054.8479 | 153.3449 | 574.7744 | 136.2408 | 268.3695 | 277.2148 | 280.3944
1055.8479 | 153.2766 | 578.6722 | 136.0048 | 268.0743 | 277.0354 | 281.2672
1056.8479 | 153.5271 | 576.4674 | 136.0725 | 267.8025 | 276.9192 | 281.4168
1057.8479 | 153.5677 | 566.3755 | 135.8118 | 267.7239 | 277.5375 | 281.745
1058.8479 | 153.6565 | 566.2686 | 136.3809 | 267.717 | 277.5914 | 281.6773
1059.8479 | 153.6083 | 559.516 | 136.6409 | 268.2211 | 277.4699 | 281.2612
1060.8479 | 153.5985 | 559.5759 | 136.5288 | 268.4763 | 277.3681 | 281.2833
1061.8479 | 153.2515 | 542.6217 | 136.5553 | 268.371 | 277.422 | 280.7925
1062.8479 | 153.2599 | 540.268 | 136.4445 | 268.4421 | 277.4114 | 281.1541
1063.8479 | 153.3902 | 531.3098 | 136.4479 | 268.3056 | 277.3324 | 280.7501
1064.8479 | 153.1894 | 532.9736 | 136.6923 | 268.6275 | 277.246 | 281.3825
1065.8479 | 152.945 | 530.0036 | 137.0568 | 268.5299 | 277.3823 | 281.2553
1066.8479 | 152.7011 | 528.732 | 137.5769 | 268.5426 | 277.4392 | 280.6773
1067.8479 | 152.2706 | 530.7907 | 137.6103 | 268.6831 | 277.5097 | 281.131
1068.8479 | 152.1292 | 528.1011 | 137.61 | 268.664 | 277.3778 | 281.2381
1069.8479 | 151.8951 | 538.3807 | 137.8499 | 268.6793 | 277.4676 | 282.1254
1070.8479 | 151.6282 | 529.4809 | 138.0752 | 268.5177 | 277.3583 | 281.8738
1071.8479 | 151.5766 | 521.0948 | 137.9299 | 268.5138 | 277.496 | 281.7877
1072.8479 | 151.2044 | 527.9306 | 137.8925 | 268.5173 | 277.5937 | 282.4999
1073.8479 | 151.1057 | 522.8352 | 137.7849 | 268.1872 | 277.7917 | 282.6804
1074.8479 | 151.1274 | 514.7839 | 137.6631 | 267.8075 | 277.9061 | 282.9077
1075.8479 | 150.9702 | 508.3356 | 137.724 | 267.7748 | 277.7886 | 282.8697
1076.8479 | 151.1344 | 509.5083 | 137.0764 | 267.6418 | 277.8868 | 282.831
1077.8479 | 151.44 | 513.9681 | 137.4176 | 267.6002 | 277.8437 | 283.0163
1078.8479 | 151.6626 | 525.9726 | 137.5455 | 267.5057 | 278.0614 | 282.8757
1079.8479 | 151.9629 | 541.7151 | 137.3829 | 267.3666 | 278.0177 | 282.6346
1080.8479 | 152.3132 | 562.5471 | 137.0456 | 267.1378 | 278.1191 | 282.0024
1081.8479 | 152.5435 | 579.4117 | 136.6558 | 266.8105 | 278.0431 | 281.7275
1082.8479 | 152.6987 | 574.6878 | 136.9918 | 266.6962 | 277.736 | 281.4321
1083.8479 | 152.6652 | 570.7807 | 136.9809 | 267.1434 | 277.4696 | 281.7912
1084.8479 | 152.7107 | 583.0799 | 136.4972 | 267.7098 | 277.1999 | 282.2643
1085.8479 | 152.8144 | 601.461 | 135.9807 | 268.2135 | 277.1839 | 282.4015
1086.8479 | 153.0607 | 583.7133 | 135.8031 | 268.251 | 277.1425 | 282.6336
1087.8479 | 153.2154 | 589.3294 | 136.5571 | 268.364 | 276.9839 | 282.9214
1088.8479 | 152.9436 | 585.7299 | 136.6374 | 268.1974 | 276.8731 | 282.5277
1089.8479 | 152.8801 | 592.9714 | 136.8712 | 268.0701 | 276.8296 | 283.6747
1090.8479 | 153.1806 | 605.8953 | 136.8902 | 267.9049 | 276.9611 | 283.1023
1091.8479 | 153.4254 | 617.8581 | 136.298 | 267.5757 | 276.833 | 282.9788
1092.8479 | 153.9988 | 635.0597 | 136.2655 | 267.455 | 276.6159 | 283.2197
1093.8479 | 154.2267 | 651.4042 | 136.7064 | 267.9269 | 277.0735 | 283.2417
1094.8479 | 154.317 | 644.7468 | 137.5717 | 267.5113 | 277.3989 | 282.9102
1095.8479 | 154.2313 | 638.6724 | 136.7637 | 267.065 | 277.2069 | 282.1304
1096.8479 | 154.2976 | 626.2751 | 136.9419 | 267.072 | 277.1383 | 281.9626
1097.8479 | 154.3873 | 617.1216 | 136.4222 | 267.1179 | 277.2709 | 282.1741
1098.8479 | 154.2791 | 605.1569 | 136.2093 | 267.422 | 276.9821 | 281.9239
1099.8479 | 154.436 | 605.7757 | 135.7592 | 267.2861 | 277.1261 | 282.4352
1100.8479 | 154.6139 | 610.7503 | 135.8431 | 267.6065 | 277.3592 | 282.2627
1101.8479 | 154.7211 | 598.2624 | 135.5687 | 267.7135 | 277.6265 | 281.8314
1102.8479 | 154.8327 | 605.699 | 135.8804 | 267.7266 | 277.6719 | 281.6803
1103.8479 | 154.8979 | 603.8566 | 135.699 | 267.8864 | 277.7087 | 281.0721
1104.8479 | 154.851 | 603.575 | 135.43 | 268.058 | 277.4918 | 280.5858
1105.8479 | 155.1516 | 607.7879 | 135.2278 | 268.2329 | 277.6011 | 280.1564
1106.8479 | 155.0691 | 607.8542 | 135.3198 | 268.448 | 277.8054 | 279.8786
1107.8479 | 155.0485 | 602.3224 | 135.0817 | 268.8907 | 278.0644 | 279.479
1108.8479 | 155.467 | 572.2943 | 135.9006 | 269.1721 | 278.1695 | 279.1686
1109.8479 | 155.8533 | 565.1099 | 136.3743 | 269.1795 | 278.4085 | 278.9106
1110.8479 | 156.1312 | 563.2051 | 137.0487 | 269.0524 | 278.2264 | 278.8103
1111.8479 | 156.423 | 540.739 | 137.1319 | 269.3642 | 278.3472 | 278.6534
1112.8479 | 156.4104 | 543.1212 | 137.5553 | 269.2356 | 278.6539 | 278.4926
1113.8479 | 156.3085 | 544.3644 | 137.9142 | 269.0769 | 278.6594 | 279.3738
1114.8479 | 156.2979 | 537.2564 | 137.8994 | 268.8408 | 278.58 | 279.8926
1115.8479 | 156.1178 | 541.4665 | 137.3972 | 268.699 | 278.4876 | 280.7435
1116.8479 | 156.0938 | 545.5016 | 137.3417 | 268.568 | 278.3141 | 281.4198
1117.8479 | 156.342 | 545.5359 | 137.6806 | 268.4636 | 278.4768 | 282.313
1118.8479 | 156.3538 | 534.823 | 137.6988 | 268.2631 | 278.4778 | 282.4794
1119.8479 | 156.4101 | 538.4027 | 137.6652 | 268.1717 | 278.3182 | 283.9348
1120.8479 | 156.6368 | 533.2699 | 137.9474 | 267.8985 | 278.245 | 284.1157
1121.8479 | 156.5106 | 557.8273 | 138.141 | 267.6978 | 278.1428 | 284.9372
1122.8479 | 156.7129 | 573.1343 | 137.8092 | 267.5916 | 277.9545 | 284.6782
1123.8479 | 156.8032 | 573.4327 | 137.8955 | 267.4471 | 277.8097 | 284.7629
1124.8479 | 156.7626 | 595.9805 | 138.2163 | 267.3351 | 277.6973 | 284.6305
1125.8479 | 156.5652 | 587.656 | 138.3522 | 267.0766 | 277.5273 | 285.2422
1126.8479 | 156.3095 | 576.9584 | 137.9849 | 266.7494 | 277.6582 | 284.7914
1127.8479 | 156.1711 | 574.896 | 137.7242 | 266.574 | 277.4542 | 284.3197
1128.8479 | 155.9456 | 566.8254 | 137.5117 | 266.5392 | 277.3966 | 283.7402
1129.8479 | 155.7867 | 550.3263 | 137.4407 | 265.9492 | 277.1106 | 283.0098
1130.8479 | 155.5628 | 556.6371 | 137.5321 | 265.72 | 276.7207 | 282.739
1131.8479 | 155.3669 | 560.8566 | 137.4363 | 265.3579 | 276.2387 | 282.9238
1132.8479 | 155.1132 | 574.5915 | 137.7825 | 265.1289 | 275.9576 | 283.3524
1133.8479 | 154.907 | 584.3474 | 137.6307 | 264.8088 | 275.9302 | 283.3861
1134.8479 | 154.7346 | 601.9022 | 138.0027 | 264.6162 | 275.751 | 283.8907
1135.8479 | 154.5301 | 602.54 | 137.525 | 264.5128 | 275.5177 | 283.5128
1136.8479 | 154.2754 | 598.782 | 137.7166 | 264.3256 | 275.3061 | 282.6809
1137.8479 | 153.9311 | 590.8099 | 137.5518 | 264.0314 | 275.2469 | 282.0184
1138.8479 | 154.0165 | 594.6913 | 137.8337 | 263.9216 | 275.132 | 281.357
1139.8479 | 153.9296 | 583.2301 | 137.8249 | 263.7518 | 274.9296 | 280.7049
1140.8479 | 154.0029 | 566.7921 | 137.9504 | 263.7221 | 274.5747 | 280.5299
1141.8479 | 153.9872 | 551.3526 | 138.4451 | 263.7254 | 274.474 | 281.2347
1142.8479 | 153.8416 | 543.3698 | 138.5792 | 263.6907 | 274.4905 | 281.1158
1143.8479 | 153.6557 | 533.3867 | 138.4632 | 263.4015 | 274.5587 | 281.9245
1144.8479 | 153.5378 | 521.9866 | 138.288 | 263.1422 | 274.8477 | 281.4837
1145.8479 | 153.3662 | 513.874 | 138.4012 | 263.4881 | 275.1202 | 281.7254
1146.8479 | 153.1205 | 511.1529 | 138.5761 | 263.6172 | 274.8549 | 281.313
1147.8479 | 152.863 | 508.5493 | 138.1199 | 263.5278 | 274.6899 | 280.989
1148.8479 | 152.5973 | 502.4037 | 137.3337 | 263.4841 | 274.6207 | 280.8811
1149.8479 | 152.3893 | 502.9806 | 136.6637 | 263.4556 | 274.452 | 281.3303
1150.8479 | 152.4163 | 518.7596 | 136.714 | 263.4749 | 274.2857 | 280.8259
1151.8479 | 152.2692 | 522.6647 | 136.7872 | 263.2511 | 274.1253 | 280.3495
1152.8479 | 152.2644 | 515.4363 | 136.6395 | 263.0651 | 273.8197 | 280.2871
1153.8479 | 152.2778 | 525.0664 | 137.2625 | 262.7337 | 273.7908 | 280.947
1154.8479 | 152.2544 | 536.0506 | 137.0901 | 262.5269 | 273.734 | 280.5855
1155.8479 | 152.5195 | 534.9975 | 137.1197 | 262.518 | 273.8004 | 280.6466
1156.8479 | 152.7458 | 553.9418 | 137.3446 | 262.4698 | 273.9061 | 280.7235
1157.8479 | 152.9631 | 568.1933 | 136.9877 | 262.3064 | 273.6643 | 281.3047
1158.8479 | 153.3134 | 574.5481 | 136.6919 | 262.1351 | 273.5797 | 281.3381
1159.8479 | 153.4863 | 569.9267 | 136.6644 | 261.888 | 273.5628 | 280.5736
1160.8479 | 153.5395 | 574.8886 | 136.2036 | 261.5928 | 273.596 | 281.3504
1161.8479 | 153.5394 | 579.1728 | 136.3036 | 261.4487 | 273.4747 | 280.574
1162.8479 | 153.4597 | 568.2032 | 135.9781 | 261.6464 | 273.3177 | 279.9908
1163.8479 | 153.4829 | 575.4274 | 136.2122 | 261.7348 | 273.0364 | 279.9562
1164.8479 | 153.5459 | 582.4979 | 136.7343 | 261.5571 | 273.204 | 279.7072
1165.8479 | 153.5912 | 592.5072 | 136.2878 | 261.5585 | 273.3183 | 279.7767
1166.8479 | 153.8535 | 577.0432 | 135.9578 | 261.9658 | 273.2341 | 279.6332
1167.8479 | 154.0051 | 581.9171 | 135.9049 | 262.2565 | 272.9192 | 278.9171
1168.8479 | 154.1181 | 586.0012 | 135.8668 | 262.1861 | 272.5686 | 278.3916
1169.8479 | 154.1664 | 606.1577 | 136.1704 | 262.1505 | 272.3567 | 277.8139
1170.8479 | 154.3981 | 611.0344 | 136.2936 | 262.0311 | 272.4562 | 277.9987
1171.8479 | 154.4483 | 627.5352 | 136.4972 | 262.0916 | 272.4189 | 278.6561
1172.8479 | 154.3439 | 636.4364 | 136.4417 | 262.2987 | 272.5056 | 278.6897
1173.8479 | 154.2274 | 640.4234 | 136.4286 | 262.2112 | 272.3818 | 278.227
1174.8479 | 153.952 | 628.2313 | 136.7709 | 262.1665 | 272.2697 | 277.6944
1175.8479 | 153.8103 | 648.2858 | 137.1338 | 262.1053 | 272.1802 | 277.0477
1176.8479 | 153.9759 | 663.3658 | 137.3802 | 262.4213 | 271.9616 | 276.3668
1177.8479 | 154.0225 | 651.2652 | 137.3004 | 262.7094 | 271.809 | 275.8045
1178.8479 | 154.0126 | 641.272 | 137.846 | 262.6341 | 271.5734 | 276.1373
1179.8479 | 154.0646 | 640.3461 | 137.3403 | 262.2588 | 271.3181 | 275.9695
1180.8479 | 154.207 | 640.843 | 138.1634 | 262.1867 | 271.0571 | 276.3039
1181.8479 | 154.2239 | 649.4267 | 138.5276 | 261.8698 | 270.8563 | 276.3025
1182.8479 | 154.4556 | 659.6517 | 139.1544 | 261.6534 | 270.7947 | 275.8476
1183.8479 | 154.3969 | 658.5116 | 138.6968 | 261.6111 | 270.6218 | 275.4011
1184.8479 | 154.2977 | 660.8346 | 139.0043 | 261.4407 | 270.6782 | 274.818
1185.8479 | 154.3312 | 652.7672 | 139.6419 | 261.142 | 270.6369 | 274.3578
1186.8479 | 154.3987 | 656.5717 | 140.3726 | 261.1563 | 270.5602 | 274.0993
1187.8479 | 154.6547 | 666.0093 | 140.6421 | 260.9284 | 270.4476 | 274.1122
1188.8479 | 154.7999 | 657.2337 | 140.8486 | 260.7693 | 270.402 | 274.1121
1189.8479 | 154.993 | 668.7296 | 140.9624 | 260.8199 | 270.2264 | 274.3627
1190.8479 | 154.9294 | 644.3407 | 141.2231 | 260.7766 | 270.2496 | 276.1173
1191.8479 | 154.8128 | 620.0459 | 141.7435 | 260.6967 | 270.1061 | 276.0064
1192.8479 | 154.4882 | 605.3321 | 142.1755 | 260.5941 | 270.1755 | 275.7718
1193.8479 | 154.1356 | 603.0651 | 142.549 | 260.6979 | 270.2114 | 276.9807
1194.8479 | 153.7725 | 590.4437 | 142.5903 | 260.7597 | 270.3183 | 277.6459
1195.8479 | 153.9518 | 576.6541 | 141.8925 | 260.8353 | 270.5998 | 277.0436
1196.8479 | 154.0754 | 568.4855 | 141.5458 | 260.8502 | 270.8914 | 276.9184
1197.8479 | 154.0207 | 546.037 | 141.8015 | 260.6598 | 270.943 | 277.2503
1198.8479 | 153.8148 | 538.8797 | 141.4368 | 260.6452 | 271.0446 | 277.2654
1199.8479 | 153.6009 | 554.6161 | 141.7646 | 260.8183 | 271.1277 | 277.8088
1200.8479 | 153.7128 | 561.9245 | 142.2575 | 260.9463 | 271.2821 | 278.7716
1201.8479 | 153.6138 | 568.5647 | 142.3201 | 260.7631 | 271.1792 | 279.0018
1202.8479 | 153.4835 | 556.285 | 142.2104 | 260.5463 | 271.0486 | 279.5052
1203.8479 | 153.2033 | 543.7861 | 142.4923 | 260.5631 | 271.0757 | 280.0794
1204.8479 | 153.1173 | 535.6852 | 142.7625 | 260.6718 | 271.2801 | 279.8655
1205.8479 | 152.9804 | 553.5212 | 143.6621 | 260.7182 | 271.2751 | 279.9997
1206.8479 | 152.8185 | 578.6308 | 143.1637 | 260.6777 | 271.4286 | 280.5073
1207.8479 | 152.5914 | 568.3378 | 143.127 | 260.6974 | 271.5101 | 281.1324
1208.8479 | 152.4634 | 569.2166 | 142.7042 | 260.5752 | 271.4716 | 282.2345
1209.8479 | 152.3008 | 551.519 | 142.3931 | 260.5663 | 271.5441 | 282.7159
1210.8479 | 151.9842 | 539.6641 | 142.0315 | 260.5458 | 271.6952 | 282.7168
1211.8479 | 151.5504 | 525.9204 | 141.8563 | 260.608 | 271.8663 | 282.6695
1212.8479 | 151.2925 | 521.5043 | 142.0767 | 261.6892 | 272.0594 | 282.6806
1213.8479 | 150.9502 | 511.7833 | 142.5252 | 262.4175 | 272.2662 | 283.3941
1214.8479 | 150.6137 | 504.6323 | 142.4298 | 262.6389 | 272.3473 | 283.9914
1215.8479 | 150.614 | 496.2279 | 142.2477 | 262.6537 | 272.1643 | 284.2486
1216.8479 | 150.386 | 487.9793 | 141.5159 | 263.0945 | 272.0168 | 284.1376
1217.8479 | 150.2023 | 479.4584 | 140.493 | 263.1474 | 272.0178 | 285.5524
1218.8479 | 150.1294 | 483.2096 | 140.6733 | 263.0197 | 272.1643 | 285.4419
1219.8479 | 150.0703 | 486.8879 | 140.6255 | 262.8058 | 272.264 | 285.6372
1220.8479 | 150.2219 | 479.3719 | 140.7828 | 262.5905 | 272.5349 | 284.7902
1221.8479 | 150.5016 | 495.2252 | 140.3989 | 262.3622 | 272.5779 | 284.472
1222.8479 | 150.6745 | 500.7298 | 140.4287 | 262.5609 | 272.4496 | 283.6666
1223.8479 | 150.8167 | 508.8438 | 140.3175 | 263.0918 | 272.1767 | 283.3732
1224.8479 | 150.6012 | 526.1193 | 140.1514 | 263.0974 | 272.0242 | 282.6622
1225.8479 | 150.655 | 537.5964 | 140.0604 | 264.0093 | 271.8128 | 282.0103
1226.8479 | 150.5128 | 549.8106 | 139.6237 | 263.8696 | 271.7365 | 282.4669
1227.8479 | 150.4456 | 543.2583 | 139.4499 | 263.5556 | 271.6755 | 281.9909
1228.8479 | 150.2225 | 545.5537 | 139.8713 | 263.2251 | 271.6679 | 281.8101
1229.8479 | 150.3766 | 561.6014 | 139.6107 | 262.9022 | 271.5356 | 281.1139
1230.8479 | 150.5289 | 556.6813 | 139.6247 | 262.7798 | 271.3665 | 280.6844
1231.8479 | 150.4938 | 558.6646 | 139.1318 | 262.8127 | 271.3537 | 280.3931
1232.8479 | 150.4062 | 551.0627 | 139.1277 | 262.6411 | 271.1563 | 280.0087
1233.8479 | 150.3715 | 571.2253 | 139.1709 | 262.4513 | 270.8719 | 280.135
1234.8479 | 150.3733 | 560.6383 | 138.3529 | 262.2445 | 270.9336 | 279.9929
1235.8479 | 150.5453 | 564.7726 | 138.5683 | 262.2443 | 271.2004 | 280.2914
1236.8479 | 150.4695 | 560.5796 | 138.5188 | 262.1019 | 271.4653 | 280.0105
1237.8479 | 150.4819 | 558.6758 | 138.4416 | 262.0834 | 271.4499 | 280.6642
1238.8479 | 150.4932 | 560.9204 | 138.1914 | 262.0952 | 271.6116 | 280.5989
1239.8479 | 150.6295 | 552.5165 | 137.8446 | 261.8772 | 271.7538 | 280.2992
1240.8479 | 150.66 | 541.0558 | 137.7735 | 261.6103 | 271.8363 | 280.0976
1241.8479 | 150.5849 | 536.7219 | 137.6927 | 261.744 | 271.7459 | 280.3055
1242.8479 | 150.5885 | 532.5889 | 137.7039 | 261.7441 | 271.5902 | 281.216
1243.8479 | 150.7419 | 536.2213 | 138.2588 | 261.6298 | 271.6454 | 281.0334
1244.8479 | 150.9937 | 544.9032 | 138.273 | 261.5906 | 271.9977 | 281.5864
1245.8479 | 151.3525 | 537.1362 | 138.4273 | 261.9416 | 271.9876 | 282.5092
1246.8479 | 151.3799 | 545.0478 | 138.1714 | 261.9268 | 272.0752 | 282.9186
1247.8479 | 151.4737 | 559.3125 | 138.6973 | 261.7756 | 272.2685 | 283.5105
1248.8479 | 151.6583 | 568.3801 | 139.0634 | 261.5383 | 272.0634 | 283.1895
1249.8479 | 151.8481 | 591.3257 | 139.1844 | 261.48 | 272.0981 | 282.3124
1250.8479 | 151.8772 | 611.9162 | 139.5467 | 262.0991 | 272.1742 | 282.2687
1251.8479 | 151.9309 | 633.1492 | 139.8037 | 262.4118 | 272.021 | 281.1853
1252.8479 | 152.0547 | 645.78 | 140.1437 | 262.4347 | 271.8818 | 280.2273
1253.8479 | 151.9178 | 674.3354 | 140.8056 | 262.1577 | 271.6032 | 279.5523
1254.8479 | 151.9988 | 673.4749 | 140.8076 | 261.5628 | 271.2916 | 278.9319
1255.8479 | 151.9754 | 663.0864 | 141.2427 | 261.0218 | 270.9006 | 278.5115
1256.8479 | 152.0345 | 654.9847 | 140.7869 | 260.8607 | 270.5288 | 278.2636
1257.8479 | 152.1279 | 634.283 | 140.737 | 260.7408 | 270.3083 | 277.7698
1258.8479 | 152.2353 | 610.5864 | 141.3184 | 260.5775 | 269.9515 | 277.3623
1259.8479 | 152.2429 | 622.4235 | 141.6447 | 260.6585 | 269.4952 | 276.7102
1260.8479 | 152.2304 | 603.6919 | 141.8821 | 260.5194 | 269.2696 | 276.4719
1261.8479 | 152.3797 | 593.1244 | 141.623 | 260.2352 | 269.1112 | 276.8681
1262.8479 | 152.28 | 584.389 | 141.7444 | 259.936 | 269.0206 | 276.9438
1263.8479 | 151.992 | 564.398 | 142.1407 | 259.6511 | 268.979 | 276.9937
1264.8479 | 151.7404 | 547.7576 | 142.1641 | 259.6457 | 269.0658 | 278.0198
1265.8479 | 151.647 | 547.063 | 142.6426 | 260.2614 | 269.214 | 278.9046
1266.8479 | 151.3079 | 533.5684 | 142.4503 | 260.4287 | 269.1685 | 278.9216
1267.8479 | 151.0321 | 538.8202 | 142.2716 | 260.4923 | 269.3076 | 278.4719
1268.8479 | 151.0558 | 517.9334 | 142.7597 | 260.443 | 269.5638 | 277.9966
1269.8479 | 150.8199 | 509.3166 | 142.175 | 260.6188 | 269.5726 | 277.8515
1270.8479 | 150.7362 | 502.4745 | 142.0852 | 260.6907 | 269.4891 | 277.7495
1271.8479 | 150.717 | 500.426 | 141.8638 | 260.5567 | 269.2567 | 277.8292
1272.8479 | 150.5866 | 509.7406 | 141.9536 | 260.4741 | 268.9386 | 278.2041
1273.8479 | 150.5102 | 524.436 | 141.6345 | 260.3414 | 268.7799 | 279.2483
1274.8479 | 150.4427 | 524.6969 | 141.6629 | 260.7613 | 268.6075 | 279.561
1275.8479 | 150.1493 | 517.9548 | 142.5771 | 260.9202 | 268.5523 | 279.7765
1276.8479 | 149.9679 | 507.4205 | 142.5294 | 260.8104 | 268.5283 | 280.622
1277.8479 | 149.8773 | 492.5081 | 142.7302 | 260.7573 | 268.7229 | 281.0934
1278.8479 | 149.7422 | 488.3832 | 142.1501 | 261.0221 | 268.9676 | 281.0627
1279.8479 | 149.6377 | 474.337 | 142.0023 | 260.9848 | 269.5798 | 280.8954
1280.8479 | 149.6332 | 476.0902 | 142.575 | 261.0154 | 269.8823 | 280.6963
1281.8479 | 149.7652 | 497.3395 | 142.1185 | 261.1314 | 270.0477 | 280.7475
1282.8479 | 149.9469 | 528.7918 | 142.2209 | 261.035 | 270.0686 | 281.1044
1283.8479 | 150.1284 | 514.0997 | 141.5029 | 261.4426 | 269.9138 | 280.9719
1284.8479 | 150.1687 | 514.1288 | 141.065 | 261.4359 | 269.7722 | 280.5594
1285.8479 | 150.0346 | 496.2768 | 141.4696 | 261.3759 | 269.7092 | 280.8582
1286.8479 | 149.9341 | 500.6114 | 141.333 | 261.2402 | 269.6254 | 280.4614
1287.8479 | 149.7663 | 515.7102 | 142.075 | 260.9156 | 269.5202 | 280.174
1288.8479 | 149.671 | 535.4091 | 142.9517 | 261.0604 | 269.4581 | 279.3714
1289.8479 | 149.5581 | 542.4266 | 143.4883 | 261.2318 | 269.4777 | 278.7743
1290.8479 | 149.0555 | 540.2923 | 143.8724 | 261.3249 | 269.3418 | 278.5644
1291.8479 | 148.9776 | 541.008 | 144.3243 | 261.3809 | 269.4314 | 278.4819
1292.8479 | 148.8451 | 533.8928 | 144.5281 | 261.2611 | 269.2722 | 277.8805
1293.8479 | 148.6963 | 522.1289 | 143.9898 | 261.1158 | 269.0704 | 277.7222
1294.8479 | 148.4451 | 514.9163 | 144.1293 | 260.8537 | 268.8674 | 278.4591
1295.8479 | 148.198 | 518.013 | 144.2059 | 260.8475 | 268.6872 | 278.7296
1296.8479 | 148.0488 | 504.4291 | 143.1819 | 260.7594 | 268.708 | 278.5847
1297.8479 | 147.7636 | 498.3477 | 142.8948 | 260.7062 | 268.765 | 278.9595
1298.8479 | 147.3898 | 490.072 | 142.5812 | 260.7911 | 268.7531 | 278.052
1299.8479 | 147.2964 | 502.2787 | 142.0995 | 260.6798 | 268.6802 | 277.1781
1300.8479 | 147.3868 | 493.0619 | 141.4661 | 260.5269 | 268.6369 | 276.5431
1301.8479 | 147.4547 | 502.1951 | 141.1823 | 260.4029 | 268.743 | 276.6785
1302.8479 | 147.5619 | 514.8946 | 141.3797 | 260.4402 | 268.712 | 277.0093
1303.8479 | 147.7277 | 530.0101 | 141.5493 | 261.2992 | 268.6898 | 278.2667
1304.8479 | 147.9215 | 549.1674 | 141.1423 | 261.2955 | 268.6195 | 278.6434
1305.8479 | 147.8323 | 539.3037 | 141.3439 | 261.1222 | 268.7155 | 278.7545
1306.8479 | 147.8346 | 554.2839 | 142.1401 | 260.9075 | 268.8961 | 279.0258
1307.8479 | 147.9874 | 559.8254 | 142.7126 | 260.7157 | 269.1155 | 279.4206
1308.8479 | 148.0819 | 568.0883 | 143.0501 | 260.6223 | 269.407 | 279.4634
1309.8479 | 148.1211 | 554.5035 | 143.7218 | 260.3368 | 269.5948 | 279.099
1310.8479 | 148.1586 | 553.005 | 143.6159 | 260.2905 | 269.7924 | 279.8157
1311.8479 | 148.3647 | 551.6969 | 143.4623 | 260.0279 | 270.293 | 279.7408
1312.8479 | 148.1216 | 530.6914 | 142.9931 | 259.9506 | 270.2962 | 279.1447
1313.8479 | 148.2265 | 520.1768 | 142.3578 | 260.1468 | 270.3062 | 278.4395
1314.8479 | 148.3698 | 504.5392 | 142.9452 | 260.2067 | 270.2152 | 278.3038
1315.8479 | 148.4709 | 500.2065 | 142.4287 | 260.0995 | 270.0601 | 278.3875
1316.8479 | 148.4481 | 499.0447 | 142.5386 | 259.9263 | 269.7574 | 278.9114
1317.8479 | 148.4264 | 509.1493 | 142.6034 | 259.6674 | 269.7408 | 278.7361
1318.8479 | 148.4506 | 506.5541 | 142.1571 | 259.7387 | 270.035 | 278.3
1319.8479 | 148.1602 | 507.7267 | 142.043 | 259.6709 | 270.4988 | 279.056
1320.8479 | 147.845 | 496.2804 | 141.4093 | 259.4059 | 270.4331 | 279.6046
1321.8479 | 147.6887 | 493.8039 | 141.5472 | 259.1661 | 270.456 | 279.5658
1322.8479 | 147.6349 | 498.6785 | 142.1211 | 259.0306 | 270.3744 | 279.9344
1323.8479 | 147.4666 | 507.1709 | 142.379 | 259.4045 | 270.3531 | 279.7255
1324.8479 | 147.3934 | 503.0966 | 141.9926 | 259.6369 | 270.9835 | 279.2979
1325.8479 | 147.3015 | 510.8196 | 141.8466 | 260.1994 | 271.5338 | 279.5218
1326.8479 | 147.1728 | 517.164 | 141.081 | 260.4936 | 271.35 | 279.434
1327.8479 | 147.4062 | 516.2542 | 141.1564 | 260.561 | 271.123 | 280.1219
1328.8479 | 147.283 | 519.7116 | 141.4427 | 260.477 | 270.8189 | 280.0365
1329.8479 | 147.1408 | 520.5577 | 141.1924 | 260.2574 | 270.5804 | 280.5929
1330.8479 | 147.1462 | 523.4447 | 141.0534 | 260.2522 | 270.459 | 281.5136
1331.8479 | 147.0987 | 519.0816 | 140.7353 | 260.3179 | 270.3875 | 281.2603
1332.8479 | 147.0038 | 528.5033 | 139.9874 | 260.2842 | 270.6429 | 281.5768
1333.8479 | 147.1417 | 521.9643 | 139.4342 | 260.1553 | 270.8865 | 281.0206
1334.8479 | 147.0754 | 515.5693 | 139.188 | 260.0162 | 271.2499 | 281.6306
1335.8479 | 147.0278 | 512.1001 | 139.4232 | 260.0991 | 271.3633 | 281.5762
1336.8479 | 146.6337 | 507.5255 | 139.4706 | 260.6671 | 271.5463 | 281.959
1337.8479 | 146.3164 | 504.9599 | 139.2391 | 260.9012 | 271.662 | 281.8298
1338.8479 | 146.0567 | 498.2012 | 139.209 | 261.1253 | 271.8033 | 282.8258
1339.8479 | 146.0789 | 496.2395 | 139.4071 | 261.3346 | 271.9807 | 282.9386
1340.8479 | 146.1506 | 505.0079 | 139.8187 | 261.6119 | 272.2872 | 282.166
1341.8479 | 146.1716 | 511.5023 | 139.0513 | 261.6791 | 272.3597 | 281.5767
1342.8479 | 146.3986 | 526.9769 | 139.2499 | 261.5983 | 272.2495 | 282.0919
1343.8479 | 146.7899 | 536.0853 | 139.4651 | 261.4725 | 272.204 | 281.8281
1344.8479 | 147.0607 | 539.996 | 139.3113 | 261.3928 | 272.0733 | 280.9849
1345.8479 | 146.9931 | 559.0675 | 139.1937 | 261.106 | 271.8379 | 281.2023
1346.8479 | 146.8661 | 555.967 | 139.0366 | 261.0642 | 271.6983 | 280.4866
1347.8479 | 146.5407 | 555.3463 | 138.8853 | 260.8515 | 271.6632 | 280.582
1348.8479 | 146.6395 | 560.485 | 138.6151 | 260.8351 | 271.546 | 281.0842
1349.8479 | 146.3934 | 555.4229 | 138.6896 | 260.8213 | 271.5641 | 280.8768
1350.8479 | 146.3674 | 554.8316 | 138.6014 | 260.5142 | 271.779 | 280.4716
1351.8479 | 146.3904 | 563.1606 | 138.4375 | 260.2432 | 271.8627 | 280.433
1352.8479 | 146.4256 | 576.3201 | 138.5324 | 259.9139 | 271.8597 | 280.4626
1353.8479 | 146.6726 | 588.2496 | 138.5433 | 260.1309 | 271.823 | 280.5384
1354.8479 | 146.6677 | 593.9557 | 139.3266 | 260.2668 | 271.7666 | 280.4412
1355.8479 | 146.5483 | 585.5313 | 139.7396 | 260.1466 | 271.5326 | 279.924
1356.8479 | 146.6174 | 581.0818 | 140.0348 | 259.9414 | 271.2424 | 280.2285
1357.8479 | 146.8515 | 581.0505 | 140.4681 | 259.8121 | 271.0073 | 279.5149
1358.8479 | 147.1942 | 582.2038 | 141.2434 | 259.6182 | 270.7125 | 278.6975
1359.8479 | 147.3885 | 577.3301 | 141.2404 | 259.5115 | 270.7442 | 278.3222
1360.8479 | 147.7933 | 576.1331 | 141.6595 | 259.6805 | 270.8582 | 277.8712