## Test Conditions
DESIREE-FIRE Intermediate Scale Test Preliminary 2 - Circuit Simulator Data Only
Test Date: | 2010-11-04
DCSim DAQ Start Time | 16:26
DCSim Time for Synchronization | 17:24
Heat Source Synchronization | 0:46 | hour:minutes:seconds
Heat Source DAQ Start Time | 16:38
Fire Time | 17:26
Offset | 1:00 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3620 | seconds
Heat Source Offset | 0:48 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2895 | seconds
Heat Source Stop Time | 17:49
Test Duration | 0:23 | hour:minutes:seconds
| 1360 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0, 1, and 2 represents the air temperature 3', 5', and 7' down the cable tray located in A Position. These are labeled as "north top", "north mid", "north bottom", respectively.
SOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 7, 8, and 9 represents the air temperature 3', 5', and 7' down the cable tray located in E Position. These are labeled as "south top", "south mid", "south bottom", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.875 | 123.1155 | -64.4211 | 58.4381 | -0.00068679 | -0.0034978 | 0.00016232 | 0.00042522 | -0.00041024 | 0.0011774 | 0.0014498 | 0.00089729 | 0.00060248 | 8.5404e-05 | 0.0034829 | -1.2882e-05 | -64.3619 | 0.015142 | -64.4752 | 58.3899 | 58.3359 | 58.3635 | -64.4565 | -64.3436 | 0.073618 | -64.5109 | 58.2543 | 58.4275 | 58.0644 | -64.6522 | -0.035391 | -0.048164 | 0.059153 | -0.054096 | -0.018705 | -0.10225 | -0.074634 | -0.23113 | -0.18382 | 0.07752 | -0.089768 | 0.14136 | -0.010593 | -0.37368 | 122.811 | 122.7569 | 122.7846 | 64.4362 | -122.8946 | 122.6754 | 122.8486 | 122.4855 | 64.4947 | -123.0903
0.79688 | 123.1567 | -64.4211 | 58.4061 | -0.015949 | -0.0037114 | 0.00058972 | 0.00021162 | -0.00041024 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00060248 | 0.0002992 | 0.0034829 | 0.00020092 | -64.3711 | 0.010564 | -64.4752 | 58.3991 | 58.3313 | 58.3635 | -64.4565 | -64.339 | 0.06904 | -64.4971 | 58.2543 | 58.4413 | 58.0186 | -64.6476 | -0.035391 | -0.006964 | 0.049996 | -0.054096 | -0.018705 | -0.074788 | -0.042591 | -0.22655 | -0.15178 | 0.082099 | -0.076032 | 0.15052 | 0.035186 | -0.38742 | 122.8202 | 122.7524 | 122.7846 | 64.4316 | -122.8625 | 122.6754 | 122.8623 | 122.4397 | 64.4901 | -123.0537
2.5312 | 123.1384 | -64.4257 | 58.4015 | -0.0083178 | -0.0037114 | 0.00016232 | 0.00021162 | -0.00083764 | 0.00032255 | -0.0061807 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0034829 | -0.00022648 | -64.3757 | 0.019721 | -64.4798 | 58.3945 | 58.3084 | 58.3635 | -64.4519 | -64.3481 | 0.073618 | -64.5017 | 58.2589 | 58.4367 | 57.9866 | -64.6476 | -0.026235 | -0.006965 | 0.049995 | -0.054097 | -0.027862 | -0.093105 | -0.038013 | -0.22197 | -0.14262 | 0.077518 | -0.076033 | 0.14594 | 0.035186 | -0.4149 | 122.8202 | 122.734 | 122.7891 | 64.4454 | -122.8534 | 122.6845 | 122.8623 | 122.4123 | 64.4993 | -123.0491
4.2656 | 123.0469 | -64.4073 | 58.5114 | -0.00068679 | -0.0037114 | 0.00037612 | -2.18e-06 | -0.00062384 | 0.00074995 | 0.016711 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0036965 | 0.00020092 | -64.3711 | 0.015142 | -64.4752 | 58.3945 | 58.3084 | 58.3635 | -64.4519 | -64.3573 | 0.073618 | -64.5063 | 58.2543 | 58.4321 | 57.9454 | -64.6431 | -0.044545 | -0.11683 | 0.036263 | -0.067829 | -0.023284 | -0.20297 | -0.14788 | -0.2357 | -0.25706 | 0.050051 | -0.098922 | 0.13678 | -0.079257 | -0.56597 | 122.8019 | 122.7157 | 122.7708 | 64.4225 | -122.9632 | 122.6616 | 122.8394 | 122.3527 | 64.481 | -123.1544
6 | 123.1705 | -64.4165 | 58.429 | 0.0069442 | -0.0034978 | 0.00037612 | 0.00021162 | -0.00062384 | 0.0011774 | -0.0061807 | 4.2686e-05 | 0.00081608 | 8.5404e-05 | 0.0036965 | 0.00020092 | -64.3711 | 0.019721 | -64.4706 | 58.3854 | 58.3359 | 58.3589 | -64.4565 | -64.3436 | 0.06904 | -64.5063 | 58.2543 | 58.4367 | 57.9958 | -64.6431 | -0.039969 | -0.043588 | 0.045418 | -0.054095 | -0.014126 | -0.093097 | -0.070058 | -0.22655 | -0.17467 | 0.072942 | -0.089767 | 0.13678 | 0.00772 | -0.4332 | 122.8019 | 122.7524 | 122.7754 | 64.4362 | -122.8854 | 122.6708 | 122.8532 | 122.4123 | 64.4855 | -123.072
7.75 | 123.143 | -64.3936 | 58.4015 | -0.0083178 | -0.0034978 | 0.00037612 | -2.18e-06 | -0.00062384 | 0.00053635 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0036965 | 0.00041452 | -64.3665 | 0.028878 | -64.4798 | 58.3945 | 58.3404 | 58.3681 | -64.4611 | -64.3481 | 0.06904 | -64.4971 | 58.2543 | 58.4367 | 57.9912 | -64.6476 | -0.067436 | -0.006965 | 0.027109 | -0.08614 | -0.018704 | -0.061052 | -0.033435 | -0.25402 | -0.1472 | 0.045475 | -0.1035 | 0.15052 | 0.035186 | -0.41032 | 122.7881 | 122.7341 | 122.7617 | 64.4225 | -122.8625 | 122.6479 | 122.8303 | 122.3848 | 64.4627 | -123.0491
9.4375 | 123.1201 | -64.3753 | 58.4885 | -0.00068679 | -0.0034978 | 0.00080352 | 0.00063882 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00089729 | 0.00060248 | 8.5404e-05 | 0.0034829 | 0.00041452 | -64.3757 | 0.0243 | -64.4798 | 58.3945 | 58.3359 | 58.3635 | -64.4656 | -64.3527 | 0.064461 | -64.5063 | 58.2543 | 58.4367 | 57.9958 | -64.6476 | -0.090326 | -0.09394 | -0.000359 | -0.10445 | -0.014125 | -0.15261 | -0.12499 | -0.27233 | -0.23418 | 0.022586 | -0.13097 | 0.14136 | -0.051789 | -0.49271 | 122.7698 | 122.7112 | 122.7388 | 64.3996 | -122.9541 | 122.6296 | 122.812 | 122.3711 | 64.4398 | -123.1361
11.1719 | 123.0743 | -64.4485 | 58.4427 | -0.00068679 | -0.0037114 | 0.00016232 | 0.00021162 | -0.0010512 | 0.00053635 | 0.0014498 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0039103 | 0.00020092 | -64.3757 | 0.0243 | -64.4752 | 58.3991 | 58.3404 | 58.3681 | -64.4519 | -64.3481 | 0.06904 | -64.5063 | 58.2589 | 58.4413 | 57.8676 | -64.6476 | -0.003347 | -0.043585 | 0.072883 | -0.026631 | -0.023284 | -0.10225 | -0.074634 | -0.19908 | -0.18382 | 0.10041 | -0.057724 | 0.14136 | -0.001435 | -0.57514 | 122.8477 | 122.789 | 122.8166 | 64.4728 | -122.8946 | 122.7074 | 122.8898 | 122.3161 | 64.5176 | -123.0903
12.8906 | 123.1476 | -64.4073 | 58.461 | 0.0069442 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00041024 | 0.00053635 | 0.0014498 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3757 | 0.0243 | -64.4706 | 58.3945 | 58.3221 | 58.3681 | -64.4519 | -64.3573 | 0.06904 | -64.5063 | 58.2543 | 58.4367 | 58.0003 | -64.6476 | -0.044545 | -0.066475 | 0.031685 | -0.06325 | -0.018705 | -0.13888 | -0.092945 | -0.24028 | -0.20671 | 0.050051 | -0.098922 | 0.14136 | -0.024324 | -0.46067 | 122.8019 | 122.7295 | 122.7754 | 64.4316 | -122.9129 | 122.6616 | 122.844 | 122.4077 | 64.4764 | -123.1086
14.6406 | 123.1705 | -64.4028 | 58.3923 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0036965 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4798 | 58.3991 | 58.3267 | 58.3635 | -64.4565 | -64.3481 | 0.078197 | -64.5063 | 58.2543 | 58.4413 | 57.9225 | -64.6476 | -0.053702 | 0.006769 | 0.027107 | -0.076985 | -0.023283 | -0.065634 | -0.028858 | -0.24486 | -0.13804 | 0.05463 | -0.1035 | 0.14136 | 0.048919 | -0.46984 | 122.8019 | 122.7295 | 122.7662 | 64.4225 | -122.8488 | 122.6571 | 122.844 | 122.3253 | 64.481 | -123.04
16.2969 | 123.0789 | -64.4257 | 58.4747 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4798 | 58.4037 | 58.3404 | 58.3635 | -64.4611 | -64.3527 | 0.06904 | -64.5017 | 58.2589 | 58.4367 | 58.1102 | -64.6385 | -0.035393 | -0.07105 | 0.054573 | -0.054097 | -0.018704 | -0.13429 | -0.11125 | -0.21282 | -0.21586 | 0.07294 | -0.076033 | 0.13678 | -0.038056 | -0.36451 | 122.8293 | 122.7661 | 122.7891 | 64.4454 | -122.9358 | 122.6845 | 122.8623 | 122.5359 | 64.4947 | -123.1132
18.0312 | 123.1384 | -64.4028 | 58.4198 | -0.0083178 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00083764 | 0.00096355 | -0.0061807 | 0.00047009 | 0.00038888 | 0.0002992 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4752 | 58.3899 | 58.313 | 58.3635 | -64.4565 | -64.3436 | 0.073618 | -64.4971 | 58.2543 | 58.4367 | 57.982 | -64.6431 | -0.053702 | -0.029854 | 0.031685 | -0.072407 | -0.018705 | -0.10684 | -0.056324 | -0.24028 | -0.16551 | 0.059209 | -0.094343 | 0.14594 | 0.016875 | -0.43778 | 122.7927 | 122.7157 | 122.7662 | 64.4225 | -122.8763 | 122.6571 | 122.8394 | 122.3848 | 64.4764 | -123.0629
19.7812 | 123.0789 | -64.3936 | 58.5022 | 0.0069442 | -0.0037114 | 0.00016232 | 0.00042522 | -0.0010512 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00060248 | 0.0002992 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4706 | 58.3899 | 58.3267 | 58.3726 | -64.4519 | -64.3481 | 0.064461 | -64.5063 | 58.2543 | 58.4321 | 57.9866 | -64.6431 | -0.058278 | -0.11225 | 0.02253 | -0.076983 | -0.018705 | -0.1755 | -0.12956 | -0.24944 | -0.24791 | 0.045475 | -0.11266 | 0.13678 | -0.070101 | -0.5156 | 122.7836 | 122.7203 | 122.7662 | 64.4133 | -122.9541 | 122.6479 | 122.8257 | 122.3802 | 64.4581 | -123.1453
21.4531 | 123.1979 | -64.3616 | 58.4473 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00083764 | 0.00096355 | -0.013811 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0034829 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4752 | 58.3945 | 58.3359 | 58.3681 | -64.4565 | -64.3527 | 0.073618 | -64.5063 | 58.2543 | 58.4413 | 58.0232 | -64.6476 | -0.094901 | -0.052742 | -0.014092 | -0.11361 | -0.018705 | -0.11141 | -0.079212 | -0.28606 | -0.19298 | 0.008853 | -0.1447 | 0.14136 | -0.006013 | -0.42404 | 122.7561 | 122.6974 | 122.7296 | 64.3813 | -122.9037 | 122.6159 | 122.8028 | 122.3848 | 64.4352 | -123.0949
23.1875 | 123.1522 | -64.4257 | 58.3969 | -0.00068679 | -0.0034978 | 0.00037612 | 0.00021162 | -0.0010512 | 0.00053635 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0003418 | 0.0036965 | -1.2882e-05 | -64.3757 | 0.0243 | -64.4798 | 58.3945 | 58.3175 | 58.3589 | -64.4473 | -64.3527 | 0.06904 | -64.5017 | 58.2543 | 58.4367 | 57.8721 | -64.6522 | -0.021656 | -0.002388 | 0.049995 | -0.054097 | -0.032441 | -0.07937 | -0.038015 | -0.22655 | -0.14262 | 0.07294 | -0.076033 | 0.15052 | 0.039763 | -0.52478 | 122.8202 | 122.7432 | 122.7846 | 64.45 | -122.8442 | 122.6799 | 122.8623 | 122.2978 | 64.4947 | -123.0491
24.875 | 123.0743 | -64.4165 | 58.4747 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00021162 | -0.0010512 | 0.00032255 | 0.0090803 | 0.00025649 | 0.00038888 | 8.5404e-05 | 0.0036965 | 0.00020092 | -64.3711 | 0.019721 | -64.4706 | 58.3945 | 58.3313 | 58.3726 | -64.4565 | -64.3481 | 0.073618 | -64.5017 | 58.2543 | 58.4367 | 57.9408 | -64.6476 | -0.039969 | -0.080207 | 0.045418 | -0.054095 | -0.014126 | -0.14345 | -0.1021 | -0.23113 | -0.22044 | 0.068363 | -0.085188 | 0.14594 | -0.038056 | -0.53392 | 122.811 | 122.7478 | 122.7891 | 64.4362 | -122.9312 | 122.6708 | 122.8532 | 122.3573 | 64.4901 | -123.1224
26.6094 | 123.1842 | -64.3799 | 58.4427 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00041024 | 0.0011774 | -0.0061807 | 0.00047009 | 0.00081608 | -0.0001282 | 0.0034829 | 0.00041452 | -64.3757 | 0.019721 | -64.4706 | 58.3991 | 58.313 | 58.3635 | -64.4519 | -64.3573 | 0.06904 | -64.4971 | 58.2543 | 58.4413 | 57.8859 | -64.6431 | -0.072011 | -0.043585 | 0.004219 | -0.090716 | -0.018705 | -0.12972 | -0.079212 | -0.26317 | -0.1884 | 0.022585 | -0.11723 | 0.14594 | -0.001435 | -0.55682 | 122.779 | 122.6928 | 122.7434 | 64.3996 | -122.8946 | 122.6342 | 122.8211 | 122.2657 | 64.4489 | -123.0857
28.2812 | 123.1064 | -64.4119 | 58.4106 | 0.0069442 | -0.0034978 | -5.128e-05 | 0.00021162 | -0.00041024 | 0.00074995 | -0.0061807 | 4.2686e-05 | 0.00081608 | -0.0003418 | 0.0041239 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4752 | 58.3945 | 58.3221 | 58.3681 | -64.4565 | -64.3436 | 0.06904 | -64.5017 | 58.2543 | 58.4367 | 57.9362 | -64.6476 | -0.044547 | -0.016121 | 0.04084 | -0.063252 | -0.018705 | -0.088524 | -0.042591 | -0.23571 | -0.15636 | 0.068364 | -0.089766 | 0.14594 | 0.02603 | -0.47442 | 122.8064 | 122.734 | 122.78 | 64.4316 | -122.8671 | 122.6662 | 122.8486 | 122.3482 | 64.481 | -123.0583
30.0156 | 123.143 | -64.4119 | 58.3923 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.00032255 | -0.0061807 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0039103 | -0.00022648 | -64.3711 | 0.0243 | -64.4843 | 58.3991 | 58.3221 | 58.3681 | -64.4611 | -64.3481 | 0.06904 | -64.5017 | 58.2497 | 58.4321 | 57.9408 | -64.6476 | -0.049126 | 0.006769 | 0.04084 | -0.072408 | -0.023282 | -0.070213 | -0.02428 | -0.23571 | -0.14262 | 0.063785 | -0.089766 | 0.14594 | 0.039762 | -0.45153 | 122.811 | 122.734 | 122.78 | 64.4362 | -122.8534 | 122.6616 | 122.844 | 122.3527 | 64.481 | -123.04
31.75 | 123.175 | -64.3936 | 58.4564 | -0.00068679 | -0.0039252 | 0.00058972 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0039103 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4752 | 58.3945 | 58.313 | 58.3635 | -64.4656 | -64.3527 | 0.073618 | -64.4971 | 58.2543 | 58.4413 | 58.037 | -64.6431 | -0.072015 | -0.061897 | 0.02253 | -0.081562 | -0.009547 | -0.14346 | -0.092945 | -0.24944 | -0.20213 | 0.040897 | -0.1035 | 0.14594 | -0.015168 | -0.41946 | 122.7881 | 122.7066 | 122.7571 | 64.4133 | -122.9221 | 122.6479 | 122.8349 | 122.4306 | 64.4672 | -123.0995
33.5 | 123.1293 | -64.4073 | 58.3969 | -0.0083178 | -0.0034978 | 0.00037612 | 0.00085262 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00081608 | -0.0001282 | 0.0036965 | 0.00020092 | -64.3757 | 0.015142 | -64.4798 | 58.3899 | 58.2809 | 58.3543 | -64.4519 | -64.3527 | 0.073618 | -64.5063 | 58.2543 | 58.4413 | 57.8813 | -64.6385 | -0.044545 | -0.006966 | 0.031685 | -0.072407 | -0.027862 | -0.116 | -0.042594 | -0.23113 | -0.14262 | 0.05463 | -0.098922 | 0.1322 | 0.044341 | -0.51563 | 122.7973 | 122.6883 | 122.7617 | 64.4225 | -122.8488 | 122.6616 | 122.8486 | 122.2886 | 64.481 | -123.0354
35.1719 | 123.1293 | -64.4073 | 58.4335 | -0.0083178 | -0.0034978 | 0.00037612 | 0.00042522 | -0.00041024 | 0.00074995 | -0.0061807 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0039103 | 0.00062812 | -64.3711 | 0.028878 | -64.4798 | 58.3945 | 58.3359 | 58.3726 | -64.4565 | -64.3481 | 0.073618 | -64.5017 | 58.2589 | 58.4413 | 58.1652 | -64.6522 | -0.049124 | -0.039009 | 0.036263 | -0.072407 | -0.023283 | -0.097675 | -0.0609 | -0.24486 | -0.17466 | 0.059208 | -0.094343 | 0.15052 | 0.00772 | -0.26837 | 122.8019 | 122.7432 | 122.78 | 64.4362 | -122.89 | 122.6662 | 122.8486 | 122.5725 | 64.481 | -123.0857
36.9062 | 123.0743 | -64.389 | 58.5159 | -0.00068679 | -0.0039252 | 0.00037612 | -2.18e-06 | -0.00041024 | 0.00074995 | 0.0014498 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0039103 | 0.00020092 | -64.3757 | 0.019721 | -64.4706 | 58.3945 | 58.3175 | 58.3681 | -64.4611 | -64.3527 | 0.06904 | -64.4971 | 58.2589 | 58.4321 | 58.0003 | -64.6522 | -0.072014 | -0.12141 | 0.013374 | -0.081561 | -0.009547 | -0.19839 | -0.14788 | -0.26317 | -0.25706 | 0.036319 | -0.10808 | 0.1551 | -0.083834 | -0.5156 | 122.7836 | 122.7066 | 122.7571 | 64.4088 | -122.977 | 122.6479 | 122.8211 | 122.3894 | 64.4581 | -123.1681
38.6406 | 123.1247 | -64.444 | 58.4106 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00041024 | 0.00096355 | -0.0061807 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0036965 | -1.2882e-05 | -64.3802 | 0.019721 | -64.4752 | 58.3854 | 58.3359 | 58.3726 | -64.4611 | -64.3481 | 0.06904 | -64.4925 | 58.2589 | 58.4413 | 57.9133 | -64.6385 | -0.017082 | -0.025278 | 0.063727 | -0.031208 | -0.014126 | -0.074787 | -0.038012 | -0.1945 | -0.15178 | 0.095829 | -0.048565 | 0.14594 | 0.030608 | -0.49731 | 122.8293 | 122.7798 | 122.8166 | 64.4637 | -122.8717 | 122.7028 | 122.8852 | 122.3573 | 64.513 | -123.0491
40.3125 | 123.1567 | -64.4211 | 58.3969 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00062384 | 0.00032255 | -0.0061807 | 4.2686e-05 | 0.00081608 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.0243 | -64.4798 | 58.3899 | 58.3313 | 58.3635 | -64.4473 | -64.3573 | 0.073618 | -64.5063 | 58.2543 | 58.4367 | 57.95 | -64.6431 | -0.026233 | -0.006966 | 0.049996 | -0.058674 | -0.032441 | -0.065633 | -0.033436 | -0.22197 | -0.14262 | 0.063784 | -0.085189 | 0.13678 | 0.039763 | -0.44695 | 122.811 | 122.7524 | 122.7846 | 64.4454 | -122.8442 | 122.6754 | 122.8578 | 122.371 | 64.4947 | -123.04
42.0625 | 123.111 | -64.4348 | 58.4015 | -0.0083178 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00062384 | 0.00053635 | 0.0014498 | 0.00025649 | 0.00081608 | 0.0002992 | 0.0036965 | -0.00022648 | -64.3848 | 0.019721 | -64.4752 | 58.3899 | 58.3267 | 58.3681 | -64.4611 | -64.3481 | 0.073618 | -64.5017 | 58.2589 | 58.4367 | 57.9637 | -64.6431 | -0.026238 | -0.011543 | 0.049993 | -0.040364 | -0.014126 | -0.074789 | -0.033435 | -0.20824 | -0.14262 | 0.086673 | -0.066878 | 0.14136 | 0.035186 | -0.43779 | 122.8248 | 122.7615 | 122.8029 | 64.4545 | -122.8625 | 122.6937 | 122.8715 | 122.3985 | 64.5084 | -123.0445
43.7344 | 123.0927 | -64.4577 | 58.4152 | -0.0083178 | -0.0034978 | 0.00016232 | 0.00021162 | -0.00083764 | 0.00096355 | -0.0061807 | 0.00068369 | 0.00060248 | -0.0001282 | 0.0036965 | -0.00022648 | -64.3757 | 0.028878 | -64.4752 | 58.3945 | 58.3404 | 58.3726 | -64.4565 | -64.3527 | 0.073618 | -64.4971 | 58.2589 | 58.4413 | 57.9591 | -64.6431 | 0.00123 | -0.020698 | 0.082039 | -0.017475 | -0.018705 | -0.074785 | -0.042589 | -0.18535 | -0.15635 | 0.10498 | -0.039411 | 0.14594 | 0.026031 | -0.4561 | 122.8522 | 122.7981 | 122.8303 | 64.4866 | -122.8717 | 122.7166 | 122.899 | 122.4168 | 64.5313 | -123.0583
45.4688 | 123.1018 | -64.4211 | 58.461 | 0.0069442 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.00074995 | 0.0014498 | -0.00017091 | 0.00017528 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3802 | 0.019721 | -64.4752 | 58.3945 | 58.3313 | 58.3681 | -64.4656 | -64.3527 | 0.073618 | -64.4971 | 58.2497 | 58.4458 | 57.8813 | -64.6431 | -0.044549 | -0.066475 | 0.040839 | -0.054096 | -0.009547 | -0.12972 | -0.092945 | -0.22197 | -0.21129 | 0.068363 | -0.076032 | 0.14594 | -0.015167 | -0.57971 | 122.8156 | 122.7524 | 122.7891 | 64.4408 | -122.9266 | 122.6708 | 122.8669 | 122.3024 | 64.4947 | -123.1041
47.2031 | 123.1155 | -64.4348 | 58.429 | 0.0069442 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.3757 | 0.019721 | -64.4752 | 58.3899 | 58.3313 | 58.3681 | -64.4611 | -64.3481 | 0.073618 | -64.5017 | 58.268 | 58.4413 | 57.9408 | -64.6522 | -0.026238 | -0.039009 | 0.05915 | -0.040364 | -0.014126 | -0.097676 | -0.060901 | -0.2174 | -0.16093 | 0.086673 | -0.066878 | 0.15052 | 0.012298 | -0.48815 | 122.8248 | 122.7661 | 122.8029 | 64.4545 | -122.89 | 122.7028 | 122.8761 | 122.3756 | 64.5084 | -123.0812
48.9375 | 123.0927 | -64.4165 | 58.4702 | -0.00068679 | -0.0037114 | 0.00016232 | 0.00042522 | -0.00062384 | 0.00074995 | 0.0090803 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3711 | 0.028878 | -64.4798 | 58.3899 | 58.3313 | 58.3726 | -64.4656 | -64.3527 | 0.073618 | -64.5017 | 58.2543 | 58.4367 | 57.9774 | -64.6568 | -0.049127 | -0.080208 | 0.045418 | -0.063252 | -0.014125 | -0.13887 | -0.097521 | -0.24029 | -0.21587 | 0.063785 | -0.085188 | 0.1551 | -0.033479 | -0.49272 | 122.8065 | 122.7478 | 122.7891 | 64.4454 | -122.9358 | 122.6708 | 122.8532 | 122.3939 | 64.4901 | -123.1269
50.6719 | 123.1613 | -64.3616 | 58.4427 | 0.0069442 | -0.0037114 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0090803 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0043375 | 0.00020092 | -64.3757 | 0.0243 | -64.4706 | 58.3945 | 58.3359 | 58.3726 | -64.4611 | -64.3527 | 0.073618 | -64.5017 | 58.2543 | 58.4321 | 58.1468 | -64.6476 | -0.09948 | -0.048164 | -0.014092 | -0.10903 | -0.009547 | -0.10683 | -0.070055 | -0.28606 | -0.1884 | 0.008853 | -0.14012 | 0.14594 | -0.010592 | -0.29584 | 122.7561 | 122.6974 | 122.7342 | 64.3859 | -122.9037 | 122.6159 | 122.7937 | 122.5084 | 64.4352 | -123.0903
52.4219 | 123.1842 | -64.3707 | 58.4335 | -0.00068679 | -0.0041388 | -5.128e-05 | 0.00021162 | -0.00062384 | 0.00053635 | 0.0090803 | 4.2686e-05 | 0.00038888 | -0.0005554 | 0.0039103 | 0.00020092 | -64.3711 | 0.0243 | -64.4798 | 58.3945 | 58.3313 | 58.3635 | -64.4519 | -64.3527 | 0.059882 | -64.5017 | 58.2543 | 58.4413 | 57.9774 | -64.6476 | -0.081166 | -0.039009 | -0.000358 | -0.10903 | -0.027862 | -0.10225 | -0.070057 | -0.2769 | -0.17924 | 0.018009 | -0.13096 | 0.14594 | 0.00772 | -0.4561 | 122.7653 | 122.702 | 122.7342 | 64.395 | -122.8854 | 122.625 | 122.812 | 122.3482 | 64.4306 | -123.0812
54.0938 | 123.1796 | -64.4394 | 58.4061 | -0.015949 | -0.0037114 | 0.00058972 | 0.00042522 | -0.00062384 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00081608 | -0.0001282 | 0.0039103 | 0.00020092 | -64.3711 | 0.0243 | -64.4843 | 58.3899 | 58.3404 | 58.3726 | -64.4565 | -64.3481 | 0.073618 | -64.5017 | 58.2543 | 58.4413 | 58.1285 | -64.6431 | -0.017081 | -0.016121 | 0.068306 | -0.044942 | -0.027861 | -0.06563 | -0.033434 | -0.20366 | -0.15178 | 0.091251 | -0.0623 | 0.14136 | 0.035186 | -0.27754 | 122.8293 | 122.7798 | 122.812 | 64.4637 | -122.8625 | 122.6937 | 122.8806 | 122.5679 | 64.513 | -123.0491
55.8281 | 123.1476 | -64.3982 | 58.4656 | 0.014575 | -0.0039252 | 0.00058972 | 0.00042522 | -0.00062384 | 0.00074995 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3757 | 0.0243 | -64.4889 | 58.3991 | 58.3267 | 58.3681 | -64.4565 | -64.3527 | 0.06904 | -64.5063 | 58.2589 | 58.4367 | 57.8904 | -64.6476 | -0.05828 | -0.066473 | 0.022529 | -0.09072 | -0.03244 | -0.13888 | -0.097522 | -0.24944 | -0.20671 | 0.045474 | -0.10808 | 0.14136 | -0.028901 | -0.57513 | 122.7973 | 122.7249 | 122.7662 | 64.4225 | -122.922 | 122.6571 | 122.8349 | 122.2886 | 64.4672 | -123.1132
57.5781 | 123.1842 | -64.3753 | 58.4244 | -0.0083178 | -0.0043526 | 0.00037612 | 0.00042522 | -0.00041024 | 0.00074995 | 0.0014498 | 4.2686e-05 | 0.00081608 | -0.0001282 | 0.0036965 | 0.00020092 | -64.3757 | 0.0243 | -64.4752 | 58.3899 | 58.3359 | 58.3681 | -64.4611 | -64.3573 | 0.059882 | -64.5017 | 58.2589 | 58.4458 | 58.0507 | -64.6476 | -0.085747 | -0.034431 | -0.000359 | -0.099873 | -0.014126 | -0.088519 | -0.056323 | -0.27233 | -0.16551 | 0.018007 | -0.12639 | 0.14594 | 0.021455 | -0.37368 | 122.7653 | 122.7112 | 122.7434 | 64.3996 | -122.8854 | 122.6342 | 122.8211 | 122.426 | 64.4352 | -123.072
59.25 | 123.1384 | -64.4073 | 58.4381 | -0.0083178 | -0.0039252 | 0.00016232 | 0.00063882 | -0.00019664 | 0.00053635 | 0.0090803 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.028878 | -64.4752 | 58.3945 | 58.3313 | 58.3681 | -64.4656 | -64.3481 | 0.06904 | -64.5063 | 58.2589 | 58.4367 | 58.0782 | -64.6431 | -0.058282 | -0.043586 | 0.036263 | -0.067829 | -0.009547 | -0.10683 | -0.070056 | -0.2357 | -0.17924 | 0.059208 | -0.098922 | 0.13678 | -0.001435 | -0.35994 | 122.8019 | 122.7386 | 122.7754 | 64.4362 | -122.9037 | 122.6662 | 122.844 | 122.4855 | 64.4764 | -123.0812
61 | 123.0423 | -64.4394 | 58.4885 | -0.0083178 | -0.0037114 | 0.00037612 | 0.00042522 | -0.0010512 | 0.00053635 | 0.0014498 | 0.00025649 | 0.00081608 | -0.0001282 | 0.0036965 | -0.00022648 | -64.3802 | 0.019721 | -64.4752 | 58.3945 | 58.3359 | 58.3681 | -64.4656 | -64.3573 | 0.064461 | -64.5063 | 58.2589 | 58.4367 | 58.1789 | -64.6431 | -0.026239 | -0.09394 | 0.059149 | -0.035786 | -0.009547 | -0.15261 | -0.12041 | -0.20366 | -0.2296 | 0.082094 | -0.066879 | 0.13678 | -0.051789 | -0.30957 | 122.8339 | 122.7752 | 122.8074 | 64.4591 | -122.9541 | 122.6983 | 122.8761 | 122.6183 | 64.5039 | -123.1315
63.4375 | 123.1338 | -64.3707 | 58.4839 | 0.0069442 | -0.0039252 | -5.128e-05 | -2.18e-06 | -0.00083764 | 0.00053635 | 0.0014498 | 0.00025649 | 0.00038888 | 0.0002992 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4752 | 58.3945 | 58.3313 | 58.3681 | -64.4656 | -64.339 | 0.073618 | -64.4971 | 58.2543 | 58.4367 | 58.1606 | -64.6476 | -0.094903 | -0.089363 | -0.000358 | -0.10445 | -0.009547 | -0.15261 | -0.11583 | -0.2769 | -0.2296 | 0.031745 | -0.12639 | 0.15052 | -0.047212 | -0.32331 | 122.7653 | 122.702 | 122.7388 | 64.3904 | -122.9495 | 122.625 | 122.8074 | 122.5313 | 64.4443 | -123.1315
65.3594 | 123.1705 | -64.3982 | 58.4061 | -0.0083178 | -0.0039252 | 0.00058972 | 0.00042522 | -0.00062384 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0036965 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4798 | 58.3945 | 58.3404 | 58.3635 | -64.4519 | -64.3527 | 0.064461 | -64.5063 | 58.2589 | 58.4367 | 58.1652 | -64.6476 | -0.053701 | -0.011543 | 0.027107 | -0.081563 | -0.027862 | -0.06563 | -0.042591 | -0.24944 | -0.1472 | 0.045474 | -0.10808 | 0.14136 | 0.030608 | -0.24091 | 122.7927 | 122.7386 | 122.7617 | 64.4179 | -122.858 | 122.6571 | 122.8349 | 122.5634 | 64.4627 | -123.0537
67.0312 | 123.0835 | -64.4073 | 58.4656 | 0.0069442 | -0.0039252 | -5.128e-05 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0090803 | 4.2686e-05 | 0.00081608 | -0.0001282 | 0.0041239 | 0.00020092 | -64.3757 | 0.019721 | -64.4752 | 58.3991 | 58.3359 | 58.3726 | -64.4656 | -64.3481 | 0.064461 | -64.5063 | 58.2497 | 58.4321 | 57.9912 | -64.6476 | -0.058282 | -0.066473 | 0.031685 | -0.067829 | -0.009547 | -0.12972 | -0.092943 | -0.24028 | -0.21587 | 0.059208 | -0.098922 | 0.14136 | -0.03348 | -0.4744 | 122.8065 | 122.7432 | 122.78 | 64.4271 | -122.9312 | 122.6571 | 122.8394 | 122.3985 | 64.4718 | -123.1132
68.7031 | 123.1064 | -64.4028 | 58.4747 | -0.0083178 | -0.0041388 | 0.00058972 | 0.00042522 | -0.0010512 | 0.00053635 | -0.0061807 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0036965 | -1.2882e-05 | -64.3711 | 0.0243 | -64.4798 | 58.3991 | 58.3404 | 58.3681 | -64.4656 | -64.3573 | 0.073618 | -64.5017 | 58.2634 | 58.4367 | 58.037 | -64.6568 | -0.06286 | -0.075628 | 0.031685 | -0.076985 | -0.014125 | -0.13429 | -0.10668 | -0.25402 | -0.21128 | 0.045473 | -0.098921 | 0.1551 | -0.038056 | -0.43777 | 122.8019 | 122.7432 | 122.7708 | 64.4271 | -122.9404 | 122.6662 | 122.8394 | 122.4397 | 64.4764 | -123.1315
70.4375 | 123.1476 | -64.4348 | 58.4061 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00083764 | 0.00096355 | -0.0061807 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0036965 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4798 | 58.3991 | 58.3404 | 58.3635 | -64.4565 | -64.3481 | 0.078197 | -64.5063 | 58.2543 | 58.4458 | 57.9362 | -64.6522 | -0.021659 | -0.006964 | 0.05915 | -0.044942 | -0.023283 | -0.06563 | -0.042591 | -0.2174 | -0.15178 | 0.086673 | -0.071457 | 0.14594 | 0.039765 | -0.46984 | 122.8339 | 122.7753 | 122.7983 | 64.4545 | -122.8625 | 122.6891 | 122.8806 | 122.371 | 64.513 | -123.0583
72.1875 | 123.0515 | -64.4531 | 58.4427 | -0.00068679 | -0.0034978 | 0.00037612 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3802 | 0.019721 | -64.4843 | 58.3991 | 58.3404 | 58.3726 | -64.4611 | -64.3527 | 0.078197 | -64.5017 | 58.2497 | 58.4458 | 58.0095 | -64.6385 | -0.007927 | -0.043585 | 0.072882 | -0.031209 | -0.023282 | -0.10225 | -0.070055 | -0.18535 | -0.19298 | 0.10041 | -0.048567 | 0.13678 | 0.003144 | -0.4332 | 122.8522 | 122.7936 | 122.8258 | 64.4728 | -122.9037 | 122.7028 | 122.899 | 122.4626 | 64.5313 | -123.0812
73.8594 | 123.0377 | -64.4348 | 58.4702 | -0.015949 | -0.0041388 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0041239 | -0.00022648 | -64.3711 | 0.015142 | -64.4798 | 58.4037 | 58.3267 | 58.3726 | -64.4656 | -64.3481 | 0.064461 | -64.5017 | 58.2543 | 58.4413 | 58.1331 | -64.6431 | -0.030817 | -0.066473 | 0.063728 | -0.044942 | -0.014125 | -0.14345 | -0.097521 | -0.20824 | -0.21587 | 0.086673 | -0.066878 | 0.14136 | -0.028901 | -0.33704 | 122.8385 | 122.7615 | 122.8074 | 64.45 | -122.9358 | 122.6891 | 122.8761 | 122.5679 | 64.4993 | -123.1132
75.5938 | 123.1064 | -64.4165 | 58.4564 | -0.0083178 | -0.0037114 | 0.00016232 | 0.00042522 | -0.00083764 | 0.0011774 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0039103 | -0.00022648 | -64.3665 | 0.0243 | -64.4798 | 58.3991 | 58.3221 | 58.3681 | -64.4611 | -64.3527 | 0.06904 | -64.4971 | 58.2589 | 58.4367 | 57.9088 | -64.6431 | -0.044548 | -0.057318 | 0.049997 | -0.063252 | -0.018704 | -0.1343 | -0.088367 | -0.22655 | -0.19755 | 0.063785 | -0.08061 | 0.14594 | -0.019746 | -0.54766 | 122.8156 | 122.7386 | 122.7846 | 64.4408 | -122.9175 | 122.6754 | 122.8532 | 122.3253 | 64.4855 | -123.0995
77.3281 | 123.0423 | -64.4073 | 58.5205 | 0.014575 | -0.0039252 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00096355 | 0.016711 | 0.00025649 | 0.0010299 | -0.0003418 | 0.0039103 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4798 | 58.3899 | 58.3175 | 58.3726 | -64.4611 | -64.3573 | 0.06904 | -64.5063 | 58.2589 | 58.4458 | 58.1194 | -64.6568 | -0.053703 | -0.13056 | 0.031685 | -0.072407 | -0.018704 | -0.20297 | -0.14787 | -0.24944 | -0.26164 | 0.050051 | -0.098922 | 0.15052 | -0.074676 | -0.40113 | 122.7973 | 122.7249 | 122.78 | 64.4271 | -122.9816 | 122.6662 | 122.8532 | 122.5267 | 64.4764 | -123.1773
79.0625 | 123.1384 | -64.4073 | 58.4244 | -0.0083178 | -0.0037114 | 0.00058972 | -2.18e-06 | -0.00019664 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00038888 | 0.0002992 | 0.0036965 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4889 | 58.3899 | 58.3359 | 58.3635 | -64.4611 | -64.3481 | 0.073618 | -64.5017 | 58.2543 | 58.4413 | 58.0599 | -64.6522 | -0.053703 | -0.034431 | 0.036263 | -0.081564 | -0.027861 | -0.088519 | -0.060901 | -0.24486 | -0.17009 | 0.059208 | -0.094343 | 0.15052 | 0.016876 | -0.36453 | 122.7973 | 122.7432 | 122.7708 | 64.4271 | -122.8854 | 122.6616 | 122.8486 | 122.4672 | 64.481 | -123.0766
80.75 | 123.0835 | -64.4073 | 58.5022 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00062384 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3757 | 0.015142 | -64.4798 | 58.3945 | 58.3359 | 58.3772 | -64.4565 | -64.3527 | 0.064461 | -64.5017 | 58.2497 | 58.4367 | 58.0553 | -64.6476 | -0.049124 | -0.10767 | 0.031685 | -0.072407 | -0.023283 | -0.16634 | -0.12499 | -0.24028 | -0.25249 | 0.05463 | -0.094343 | 0.14594 | -0.065522 | -0.44692 | 122.8019 | 122.7432 | 122.7846 | 64.4225 | -122.9587 | 122.6571 | 122.844 | 122.4626 | 64.4718 | -123.1498
82.4844 | 123.1155 | -64.4211 | 58.4335 | 0.014575 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00041024 | 0.001391 | -0.013811 | 0.00025649 | 0.00038888 | 0.0002992 | 0.0039103 | -0.00065368 | -64.3711 | 0.015142 | -64.4843 | 58.3899 | 58.3221 | 58.3726 | -64.4611 | -64.3436 | 0.073618 | -64.4971 | 58.2589 | 58.4367 | 57.8904 | -64.6522 | -0.03997 | -0.043587 | 0.049996 | -0.063252 | -0.023282 | -0.11141 | -0.0609 | -0.23113 | -0.17466 | 0.07752 | -0.076032 | 0.1551 | 0.003142 | -0.54309 | 122.811 | 122.7432 | 122.7937 | 64.4362 | -122.8946 | 122.6799 | 122.8578 | 122.3115 | 64.4947 | -123.0857
84.2188 | 123.1064 | -64.4165 | 58.493 | 0.0069442 | -0.0039252 | 0.00058972 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0039103 | -1.2882e-05 | -64.3757 | 0.028878 | -64.4843 | 58.4037 | 58.3359 | 58.3681 | -64.4565 | -64.3527 | 0.073618 | -64.5109 | 58.2589 | 58.4413 | 58.0873 | -64.6431 | -0.039969 | -0.089361 | 0.04084 | -0.06783 | -0.027861 | -0.15718 | -0.12499 | -0.22655 | -0.23417 | 0.063785 | -0.094346 | 0.1322 | -0.051789 | -0.40572 | 122.8202 | 122.7524 | 122.7846 | 64.4454 | -122.9495 | 122.6754 | 122.8578 | 122.5038 | 64.4901 | -123.1361
85.9531 | 123.1705 | -64.4485 | 58.4244 | -0.0083178 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00083764 | 0.001391 | 0.0014498 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0041239 | -0.00022648 | -64.3802 | 0.019721 | -64.4843 | 58.3945 | 58.3404 | 58.3681 | -64.4611 | -64.3481 | 0.082776 | -64.5017 | 58.2497 | 58.4413 | 58.0461 | -64.6385 | -0.012505 | -0.029853 | 0.068304 | -0.035787 | -0.023282 | -0.08394 | -0.056323 | -0.18993 | -0.17467 | 0.10041 | -0.053145 | 0.13678 | 0.016876 | -0.37826 | 122.8431 | 122.789 | 122.8166 | 64.4683 | -122.8854 | 122.6983 | 122.8898 | 122.4947 | 64.5313 | -123.0629
87.6406 | 123.024 | -64.4394 | 58.4656 | -0.0083178 | -0.0039252 | 0.00058972 | 0.00021162 | -0.00083764 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00038888 | -0.0001282 | 0.0034829 | -1.2882e-05 | -64.3757 | 0.0243 | -64.4843 | 58.4083 | 58.3404 | 58.3772 | -64.4565 | -64.3481 | 0.078197 | -64.4971 | 58.2543 | 58.4413 | 57.9088 | -64.6568 | -0.017081 | -0.057317 | 0.063728 | -0.044942 | -0.027861 | -0.12514 | -0.088365 | -0.2174 | -0.21129 | 0.091251 | -0.057722 | 0.15968 | -0.024323 | -0.55682 | 122.8477 | 122.7798 | 122.8166 | 64.4637 | -122.922 | 122.6937 | 122.8806 | 122.3482 | 64.5176 | -123.1224
89.375 | 123.0835 | -64.4165 | 58.4885 | -0.00068679 | -0.0037114 | -5.128e-05 | 0.00021162 | -0.00062384 | 0.0011774 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0036965 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4798 | 58.3991 | 58.3313 | 58.3818 | -64.4611 | -64.3481 | 0.06904 | -64.5063 | 58.2543 | 58.4367 | 58.0278 | -64.6476 | -0.044548 | -0.089361 | 0.04084 | -0.063252 | -0.018704 | -0.15718 | -0.10667 | -0.23113 | -0.23418 | 0.068363 | -0.089767 | 0.14136 | -0.051789 | -0.46066 | 122.8156 | 122.7478 | 122.7983 | 64.4362 | -122.9495 | 122.6708 | 122.8532 | 122.4443 | 64.4855 | -123.1361
91.1094 | 123.0789 | -64.4073 | 58.4656 | -0.015949 | -0.0039252 | 0.00016232 | -2.18e-06 | -0.00062384 | 0.001391 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0041239 | -0.00022648 | -64.3711 | 0.015142 | -64.4752 | 58.3945 | 58.3404 | 58.3681 | -64.4519 | -64.3573 | 0.078197 | -64.5017 | 58.2497 | 58.4367 | 57.9408 | -64.6476 | -0.044545 | -0.071052 | 0.036263 | -0.067829 | -0.023284 | -0.12514 | -0.097522 | -0.24028 | -0.21587 | 0.050051 | -0.094343 | 0.14594 | -0.028901 | -0.52477 | 122.8019 | 122.7478 | 122.7754 | 64.4225 | -122.9175 | 122.6571 | 122.844 | 122.3482 | 64.4855 | -123.1132
92.7812 | 123.1201 | -64.4211 | 58.4198 | -0.00068679 | -0.0037114 | 0.00037612 | -2.18e-06 | -0.00062384 | 0.0011774 | -0.013811 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.3711 | 0.0243 | -64.4843 | 58.3991 | 58.3267 | 58.3681 | -64.4519 | -64.3573 | 0.064461 | -64.4971 | 58.2543 | 58.4367 | 57.95 | -64.6476 | -0.030812 | -0.020697 | 0.049996 | -0.063252 | -0.03244 | -0.0931 | -0.051746 | -0.22655 | -0.16551 | 0.063784 | -0.076032 | 0.15052 | 0.016875 | -0.46983 | 122.8202 | 122.7478 | 122.7891 | 64.4454 | -122.8717 | 122.6754 | 122.8578 | 122.371 | 64.4855 | -123.0674
94.5156 | 123.0743 | -64.4394 | 58.4427 | -0.00068679 | -0.0041388 | -5.128e-05 | 0.00021162 | -0.00083764 | 0.00096355 | 0.0014498 | -0.00017091 | 0.00060248 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3802 | 0.0243 | -64.4752 | 58.4037 | 58.345 | 58.3772 | -64.4565 | -64.3481 | 0.078197 | -64.5017 | 58.2497 | 58.4367 | 58.0324 | -64.6476 | -0.017081 | -0.039007 | 0.059149 | -0.035786 | -0.018705 | -0.097673 | -0.065477 | -0.20824 | -0.19298 | 0.091251 | -0.0623 | 0.14594 | -0.006013 | -0.41031 | 122.8431 | 122.7844 | 122.8166 | 64.4637 | -122.8992 | 122.6891 | 122.8761 | 122.4718 | 64.5176 | -123.0903
96.25 | 123.0927 | -64.4257 | 58.4976 | 0.0069442 | -0.0041388 | 0.00058972 | 0.00042522 | -0.00083764 | 0.001391 | 0.0014498 | 4.2686e-05 | 0.00038888 | -0.0001282 | 0.0043375 | -1.2882e-05 | -64.3665 | 0.0243 | -64.4798 | 58.3899 | 58.3404 | 58.3818 | -64.4611 | -64.3436 | 0.064461 | -64.4971 | 58.2634 | 58.4413 | 57.9866 | -64.6385 | -0.035393 | -0.10767 | 0.059152 | -0.054097 | -0.018704 | -0.15718 | -0.11583 | -0.21282 | -0.23417 | 0.082097 | -0.071455 | 0.14136 | -0.056367 | -0.51103 | 122.8156 | 122.7661 | 122.8074 | 64.45 | -122.9587 | 122.6891 | 122.8669 | 122.4123 | 64.4901 | -123.1361
97.9219 | 123.056 | -64.4119 | 58.5114 | -0.015949 | -0.0037114 | -0.00026488 | 0.00021162 | -0.00062384 | 0.0011774 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0041239 | -0.00022648 | -64.3711 | 0.019721 | -64.4843 | 58.3991 | 58.3038 | 58.3635 | -64.4519 | -64.3481 | 0.073618 | -64.5063 | 58.2589 | 58.4321 | 57.9454 | -64.5606 | -0.039968 | -0.11225 | 0.04084 | -0.072408 | -0.03244 | -0.20755 | -0.14788 | -0.14871 | -0.25249 | 0.063785 | -0.094345 | 0.054363 | -0.079257 | -0.56597 | 122.811 | 122.7157 | 122.7754 | 64.4316 | -122.9632 | 122.6708 | 122.844 | 122.3573 | 64.4855 | -123.072
99.6562 | 123.1842 | -64.4302 | 58.4198 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00062384 | 0.001391 | -0.0061807 | 0.00025649 | 0.00038888 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4752 | 58.3945 | 58.3267 | 58.3726 | -64.4611 | -64.3481 | 0.073618 | -64.4971 | 58.2497 | 58.4367 | 57.9545 | -64.5561 | -0.030815 | -0.025276 | 0.059151 | -0.044941 | -0.014126 | -0.0931 | -0.047167 | -0.12582 | -0.17009 | 0.082096 | -0.066877 | 0.058941 | 0.016875 | -0.46526 | 122.8248 | 122.7569 | 122.8029 | 64.45 | -122.8809 | 122.6799 | 122.8669 | 122.3848 | 64.5039 | -122.9759
101.4062 | 123.0423 | -64.3845 | 58.5159 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.001391 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0003418 | 0.0039103 | -1.2882e-05 | -64.3757 | 0.019721 | -64.4752 | 58.3854 | 58.3404 | 58.3726 | -64.4611 | -64.3481 | 0.064461 | -64.4971 | 58.2543 | 58.4458 | 58.0095 | -64.5698 | -0.076592 | -0.13056 | 0.008796 | -0.090718 | -0.014126 | -0.17549 | -0.1433 | -0.18533 | -0.26164 | 0.036319 | -0.11265 | 0.072677 | -0.070098 | -0.50644 | 122.7698 | 122.7249 | 122.7571 | 64.4042 | -122.977 | 122.6387 | 122.8303 | 122.3939 | 64.4489 | -123.0857
103.0781 | 123.1796 | -64.3662 | 58.4564 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.001391 | 0.0014498 | 0.00025649 | 0.00038888 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.019721 | -64.4843 | 58.3899 | 58.3313 | 58.3726 | -64.4565 | -64.3527 | 0.073618 | -64.5017 | 58.2589 | 58.4367 | 58.1102 | -64.5652 | -0.090323 | -0.066475 | -0.004936 | -0.11818 | -0.027861 | -0.12514 | -0.083788 | -0.19906 | -0.19755 | 0.013431 | -0.13554 | 0.063521 | -0.019746 | -0.3462 | 122.7561 | 122.6974 | 122.7388 | 64.3859 | -122.9129 | 122.625 | 122.8028 | 122.4764 | 64.4398 | -123.0216
104.8125 | 123.1659 | -64.4165 | 58.4106 | -0.0083178 | -0.0034978 | 0.00016232 | 0.00042522 | -0.00041024 | 0.001391 | 0.0014498 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.3802 | 0.019721 | -64.4889 | 58.3945 | 58.3404 | 58.3681 | -64.4565 | -64.3481 | 0.078197 | -64.5017 | 58.2543 | 58.4367 | 57.9271 | -64.5606 | -0.039969 | -0.016121 | 0.036261 | -0.072409 | -0.03244 | -0.070208 | -0.042591 | -0.14413 | -0.15636 | 0.068363 | -0.085188 | 0.058942 | 0.02603 | -0.48357 | 122.811 | 122.7569 | 122.7846 | 64.4362 | -122.8671 | 122.6708 | 122.8532 | 122.3436 | 64.4947 | -122.9713
106.5625 | 123.0515 | -64.4577 | 58.4564 | -0.00068679 | -0.0041388 | 0.00016232 | 0.00021162 | -0.0010512 | 0.0011774 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0039103 | 0.00020092 | -64.3757 | 0.015142 | -64.4798 | 58.4037 | 58.3359 | 58.3772 | -64.4702 | -64.3481 | 0.06904 | -64.5063 | 58.2589 | 58.4413 | 58.0232 | -64.5744 | -0.012507 | -0.05274 | 0.082039 | -0.022053 | -0.009546 | -0.12056 | -0.07921 | -0.11667 | -0.19755 | 0.10956 | -0.048568 | 0.068099 | -0.015168 | -0.4332 | 122.8614 | 122.7936 | 122.8349 | 64.4728 | -122.9266 | 122.7166 | 122.899 | 122.4809 | 64.5267 | -123.0308
108.2812 | 123.1247 | -64.4394 | 58.429 | -0.0083178 | -0.0037114 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0090803 | 0.00068369 | 0.00060248 | 0.0005128 | 0.0039103 | -1.2882e-05 | -64.3711 | 0.015142 | -64.4843 | 58.3899 | 58.3404 | 58.3772 | -64.4611 | -64.3481 | 0.059882 | -64.5017 | 58.268 | 58.4367 | 58.124 | -64.5698 | -0.02166 | -0.039009 | 0.068306 | -0.044942 | -0.023282 | -0.088518 | -0.051744 | -0.1304 | -0.16093 | 0.091251 | -0.0623 | 0.068099 | 0.00772 | -0.305 | 122.8293 | 122.7798 | 122.8166 | 64.4545 | -122.89 | 122.7074 | 122.8761 | 122.5633 | 64.4993 | -122.9987
109.9531 | 123.1293 | -64.4028 | 58.429 | -0.00068679 | -0.0041388 | 0.00058972 | 0.00042522 | -0.00083764 | 0.0011774 | -0.013811 | 0.00047009 | 0.00038888 | -0.0001282 | 0.0039103 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4843 | 58.3945 | 58.3404 | 58.3772 | -64.4611 | -64.3573 | 0.06904 | -64.4971 | 58.2589 | 58.4413 | 58.0599 | -64.5606 | -0.058281 | -0.034431 | 0.031685 | -0.081563 | -0.023282 | -0.088518 | -0.051744 | -0.15786 | -0.17009 | 0.045473 | -0.094343 | 0.06352 | 0.012298 | -0.3691 | 122.7973 | 122.7432 | 122.78 | 64.4225 | -122.89 | 122.6616 | 122.844 | 122.4626 | 64.4718 | -122.9896
111.6875 | 123.056 | -64.4577 | 58.461 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.0011774 | -0.0061807 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0041239 | -0.00022648 | -64.3802 | 0.019721 | -64.4889 | 58.3991 | 58.3359 | 58.3726 | -64.4519 | -64.3481 | 0.073618 | -64.5017 | 58.2543 | 58.4458 | 57.9179 | -64.5652 | 0.005809 | -0.061896 | 0.07746 | -0.03121 | -0.037019 | -0.12514 | -0.088366 | -0.10751 | -0.20671 | 0.10956 | -0.043989 | 0.063521 | -0.015167 | -0.54308 | 122.8568 | 122.7936 | 122.8303 | 64.4774 | -122.9129 | 122.712 | 122.9035 | 122.3756 | 64.5313 | -123.0262
113.4375 | 123.0515 | -64.4211 | 58.4702 | -0.0083178 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00083764 | 0.00096355 | -0.0061807 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0043375 | 0.00020092 | -64.3711 | 0.019721 | -64.4798 | 58.4037 | 58.345 | 58.3772 | -64.4656 | -64.3481 | 0.06904 | -64.5017 | 58.2543 | 58.4321 | 57.8676 | -64.5698 | -0.044549 | -0.066473 | 0.049996 | -0.058674 | -0.014125 | -0.12514 | -0.092943 | -0.14871 | -0.21587 | 0.072941 | -0.08061 | 0.068099 | -0.038058 | -0.6026 | 122.8248 | 122.7661 | 122.7983 | 64.4408 | -122.9358 | 122.6754 | 122.8532 | 122.2886 | 64.4901 | -123.0399
115.1719 | 123.1247 | -64.4073 | 58.4198 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.0016046 | -0.013811 | 4.2686e-05 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00041452 | -64.3619 | 0.015142 | -64.4889 | 58.3945 | 58.3404 | 58.3818 | -64.4656 | -64.3481 | 0.073618 | -64.5017 | 58.2497 | 58.4413 | 58.0415 | -64.5652 | -0.058282 | -0.025276 | 0.04542 | -0.081564 | -0.023282 | -0.079363 | -0.03801 | -0.15786 | -0.17009 | 0.059208 | -0.094343 | 0.063521 | 0.021453 | -0.37826 | 122.8019 | 122.7478 | 122.7891 | 64.4225 | -122.8854 | 122.6571 | 122.8486 | 122.4489 | 64.481 | -122.985
116.8594 | 123.0606 | -64.4623 | 58.4564 | 0.0069442 | -0.0039252 | 0.00016232 | 0.00021162 | -0.00083764 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00017528 | -0.0001282 | 0.0041239 | -1.2882e-05 | -64.3711 | 0.0243 | -64.4843 | 58.3991 | 58.345 | 58.3818 | -64.4611 | -64.3527 | 0.06904 | -64.4971 | 58.2589 | 58.4367 | 58.1285 | -64.5652 | 0.001228 | -0.057318 | 0.091194 | -0.022054 | -0.023282 | -0.11141 | -0.074631 | -0.10293 | -0.19755 | 0.10956 | -0.034834 | 0.068099 | -0.019746 | -0.32789 | 122.8614 | 122.8073 | 122.8441 | 64.4866 | -122.9175 | 122.7211 | 122.899 | 122.5908 | 64.5313 | -123.0216
118.5938 | 123.175 | -64.3982 | 58.4518 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00042522 | -0.0010512 | 0.001391 | 0.0014498 | 0.00068369 | 0.00017528 | -0.0001282 | 0.0045513 | 0.00020092 | -64.3757 | 0.0243 | -64.4843 | 58.3945 | 58.3221 | 58.3772 | -64.4519 | -64.3527 | 0.073618 | -64.5063 | 58.2543 | 58.4367 | 57.8996 | -64.5606 | -0.053701 | -0.057319 | 0.022529 | -0.086141 | -0.03244 | -0.12972 | -0.074632 | -0.16244 | -0.19755 | 0.045474 | -0.10808 | 0.054363 | -0.015168 | -0.55224 | 122.7927 | 122.7203 | 122.7754 | 64.4225 | -122.9037 | 122.6525 | 122.8349 | 122.2978 | 64.4718 | -123.0125
120.3281 | 123.056 | -64.4257 | 58.4976 | -0.00068679 | -0.0039252 | -0.00026488 | 0.00021162 | -0.00062384 | 0.001391 | 0.0090803 | 0.00025649 | 0.00060248 | 0.0002992 | 0.0041239 | -1.2882e-05 | -64.3711 | 0.015142 | -64.4752 | 58.3991 | 58.3313 | 58.3772 | -64.4611 | -64.3481 | 0.078197 | -64.4971 | 58.2543 | 58.4413 | 58.0553 | -64.5652 | -0.035393 | -0.098517 | 0.054573 | -0.049519 | -0.014126 | -0.16634 | -0.12041 | -0.13955 | -0.24333 | 0.077518 | -0.071455 | 0.068099 | -0.056367 | -0.44235 | 122.8248 | 122.7569 | 122.8029 | 64.4408 | -122.9587 | 122.6799 | 122.8669 | 122.4809 | 64.5039 | -123.0628
122 | 123.0789 | -64.4577 | 58.4564 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00041024 | 0.001391 | -0.0061807 | 0.00025649 | 0.00038888 | 0.0002992 | 0.0041239 | -0.00022648 | -64.3802 | 0.028878 | -64.4798 | 58.3945 | 58.345 | 58.3772 | -64.4519 | -64.3573 | 0.078197 | -64.4925 | 58.2634 | 58.4458 | 57.9866 | -64.5652 | 0.005809 | -0.061897 | 0.07746 | -0.022053 | -0.027862 | -0.11141 | -0.07921 | -0.10751 | -0.19297 | 0.1004 | -0.034832 | 0.072678 | -0.010589 | -0.46983 | 122.8522 | 122.8027 | 122.8349 | 64.4866 | -122.9083 | 122.7211 | 122.9035 | 122.4443 | 64.5359 | -123.0216
123.7188 | 123.1247 | -64.4119 | 58.4244 | -0.015949 | -0.0041388 | 0.00037612 | 0.00021162 | -0.0010512 | 0.001391 | 0.0014498 | 0.00068369 | 0.00060248 | 8.5404e-05 | 0.0039103 | -1.2882e-05 | -64.3711 | 0.019721 | -64.4798 | 58.3991 | 58.3221 | 58.3726 | -64.4565 | -64.3481 | 0.064461 | -64.5063 | 58.2543 | 58.4413 | 57.9866 | -64.5606 | -0.044547 | -0.025274 | 0.04084 | -0.06783 | -0.023283 | -0.10226 | -0.051744 | -0.14871 | -0.17009 | 0.063785 | -0.094345 | 0.054363 | 0.016876 | -0.43778 | 122.811 | 122.734 | 122.7846 | 64.4316 | -122.8809 | 122.6662 | 122.8532 | 122.3985 | 64.4764 | -122.985
125.4531 | 123.0927 | -64.4165 | 58.461 | 0.0069442 | -0.0039252 | 0.00016232 | 0.00021162 | -0.00041024 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0039103 | 0.00020092 | -64.3711 | 0.0243 | -64.4889 | 58.3991 | 58.3313 | 58.3681 | -64.4656 | -64.3527 | 0.06904 | -64.5017 | 58.2634 | 58.4458 | 57.95 | -64.5698 | -0.049127 | -0.061896 | 0.045418 | -0.072409 | -0.023282 | -0.12972 | -0.092945 | -0.15329 | -0.19755 | 0.063785 | -0.085188 | 0.068099 | -0.015167 | -0.51103 | 122.8156 | 122.7478 | 122.7846 | 64.4408 | -122.9266 | 122.68 | 122.8623 | 122.3665 | 64.4855 | -123.0308
127.2031 | 123.056 | -64.4028 | 58.5297 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00042522 | -0.0010512 | 0.0011774 | -0.0061807 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0041239 | 0.00020092 | -64.3711 | 0.019721 | -64.4798 | 58.3945 | 58.345 | 58.3726 | -64.4565 | -64.3481 | 0.06904 | -64.4971 | 58.2543 | 58.4458 | 58.1377 | -64.5606 | -0.053702 | -0.13514 | 0.031685 | -0.076985 | -0.023283 | -0.18465 | -0.15703 | -0.15786 | -0.27537 | 0.05463 | -0.094343 | 0.06352 | -0.083831 | -0.39198 | 122.7973 | 122.7478 | 122.7754 | 64.4225 | -122.9861 | 122.6571 | 122.8486 | 122.5405 | 64.4718 | -123.0903
128.875 | 123.056 | -64.3707 | 58.5114 | 0.014575 | -0.0041388 | 0.00058972 | 0.00021162 | -0.0010512 | 0.001391 | 0.0090803 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0041239 | -0.00022648 | -64.3619 | 0.0243 | -64.4752 | 58.4037 | 58.345 | 58.3909 | -64.4519 | -64.3344 | 0.073618 | -64.488 | 58.2634 | 58.4458 | 57.9271 | -64.5606 | -0.081166 | -0.10767 | 0.008799 | -0.10445 | -0.023284 | -0.16634 | -0.12041 | -0.18991 | -0.24791 | 0.036323 | -0.11723 | 0.072678 | -0.065521 | -0.58428 | 122.7744 | 122.7157 | 122.7617 | 64.395 | -122.9632 | 122.6342 | 122.8166 | 122.2978 | 64.4443 | -123.072
130.6094 | 123.0972 | -64.4028 | 58.5205 | -0.00068679 | -0.0041388 | 0.00016232 | 0.00021162 | -0.00062384 | 0.001391 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0043375 | 0.00020092 | -64.3528 | 0.0243 | -64.4614 | 58.4174 | 58.3588 | 58.3955 | -64.4427 | -64.3344 | 0.06904 | -64.4788 | 58.2726 | 58.4641 | 57.8996 | -64.5469 | -0.039965 | -0.10309 | 0.049999 | -0.058672 | -0.018707 | -0.16176 | -0.12498 | -0.14413 | -0.24791 | 0.068366 | -0.076028 | 0.068098 | -0.056362 | -0.62091 | 122.8202 | 122.7615 | 122.7983 | 64.4271 | -122.9632 | 122.6754 | 122.8669 | 122.3024 | 64.4718 | -123.0674
132.2812 | 123.1522 | -64.3478 | 58.4564 | -0.00068679 | -0.0037114 | -5.128e-05 | 0.00042522 | -0.0010512 | 0.001391 | -0.013811 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0039103 | 0.00020092 | -64.307 | 0.0243 | -64.4157 | 58.4632 | 58.4045 | 58.4367 | -64.3924 | -64.2886 | 0.06904 | -64.433 | 58.323 | 58.5099 | 58.0599 | -64.5057 | -0.044529 | 0.006779 | 0.040851 | -0.067821 | -0.023292 | -0.051879 | -0.019688 | -0.15785 | -0.13345 | 0.059222 | -0.085173 | 0.072676 | 0.053511 | -0.39657 | 122.811 | 122.7524 | 122.7846 | 64.3721 | -122.8488 | 122.6708 | 122.8578 | 122.4077 | 64.4169 | -122.9621
133.9531 | 123.0698 | -64.3433 | 58.548 | -0.00068679 | -0.0039252 | 0.00016232 | 0.00021162 | -0.00062384 | 0.0016046 | 0.0014498 | 4.2686e-05 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.3024 | 0.010564 | -64.4065 | 58.4678 | 58.4045 | 58.4459 | -64.3969 | -64.284 | 0.06904 | -64.4376 | 58.3184 | 58.5099 | 58.1148 | -64.5011 | -0.053685 | -0.080196 | 0.040852 | -0.063241 | -0.009556 | -0.14343 | -0.10208 | -0.15785 | -0.22959 | 0.059223 | -0.094328 | 0.063519 | -0.038042 | -0.43318 | 122.811 | 122.7478 | 122.7892 | 64.3538 | -122.9449 | 122.6616 | 122.8532 | 122.4581 | 64.4123 | -123.0491
135.6875 | 123.1888 | -64.2838 | 58.5297 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00042522 | -0.00083764 | 0.0011774 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0041239 | 0.00020092 | -64.2978 | 0.019721 | -64.4111 | 58.4724 | 58.4183 | 58.4505 | -64.3786 | -64.2703 | 0.06904 | -64.433 | 58.3413 | 58.5237 | 58.1377 | -64.492 | -0.094879 | -0.057306 | -0.01408 | -0.12733 | -0.032451 | -0.11138 | -0.079194 | -0.2082 | -0.18838 | 0.013449 | -0.14926 | 0.05894 | -0.005995 | -0.39198 | 122.7561 | 122.702 | 122.7342 | 64.3035 | -122.9083 | 122.625 | 122.8074 | 122.4214 | 64.3528 | -123.0216
137.3594 | 123.0698 | -64.357 | 58.5892 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00042522 | -0.00062384 | 0.0011774 | 0.0014498 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0043375 | 0.00020092 | -64.3024 | 0.028878 | -64.4065 | 58.4769 | 58.4137 | 58.455 | -64.3832 | -64.2749 | 0.073618 | -64.4284 | 58.3367 | 58.5191 | 57.9866 | -64.4828 | -0.026215 | -0.11224 | 0.054585 | -0.049508 | -0.023293 | -0.17547 | -0.13412 | -0.1258 | -0.25247 | 0.082114 | -0.071438 | 0.054361 | -0.070083 | -0.60258 | 122.8339 | 122.7707 | 122.812 | 64.3859 | -122.9724 | 122.6937 | 122.8761 | 122.3436 | 64.4306 | -123.072
139.0938 | 123.0515 | -64.3845 | 58.4885 | -0.00068679 | -0.0037114 | 0.00037612 | 0.00021162 | -0.00062384 | 0.00074995 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.3116 | 0.028878 | -64.4248 | 58.4495 | 58.3954 | 58.4276 | -64.4015 | -64.284 | 0.073618 | -64.4513 | 58.3138 | 58.4916 | 58.1881 | -64.5148 | -0.017066 | -0.038999 | 0.072893 | -0.040357 | -0.023291 | -0.09308 | -0.060888 | -0.13039 | -0.17465 | 0.10042 | -0.066866 | 0.06352 | 0.003154 | -0.30041 | 122.8339 | 122.7798 | 122.812 | 64.4133 | -122.89 | 122.6983 | 122.8761 | 122.5725 | 64.4581 | -123.0033
140.8281 | 123.0469 | -64.325 | 58.5571 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00021162 | -0.0010512 | 0.0016046 | -0.0061807 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0043375 | 0.00041452 | -64.3345 | 0.0243 | -64.4477 | 58.4403 | 58.3816 | 58.4184 | -64.4107 | -64.3069 | 0.06904 | -64.4651 | 58.3001 | 58.487 | 57.9408 | -64.5103 | -0.085733 | -0.11682 | -0.009508 | -0.12276 | -0.037024 | -0.17548 | -0.13871 | -0.18532 | -0.25706 | 0.018019 | -0.14011 | 0.045204 | -0.07009 | -0.61632 | 122.7653 | 122.7066 | 122.7434 | 64.3493 | -122.9678 | 122.625 | 122.812 | 122.2658 | 64.394 | -123.0674
142.5625 | 123.0652 | -64.3524 | 58.5114 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00083764 | 0.0011774 | 0.0090803 | 0.00047009 | 0.00038888 | -0.0001282 | 0.0045513 | 0.00020092 | -64.3345 | 0.019721 | -64.4477 | 58.4357 | 58.3771 | 58.4184 | -64.4107 | -64.3024 | 0.078197 | -64.4605 | 58.3001 | 58.4825 | 58.124 | -64.5194 | -0.058267 | -0.075623 | 0.017958 | -0.095291 | -0.037024 | -0.13428 | -0.092934 | -0.16701 | -0.21128 | 0.050063 | -0.10807 | 0.05894 | -0.028892 | -0.3874 | 122.7881 | 122.7295 | 122.7708 | 64.3721 | -122.922 | 122.6525 | 122.8349 | 122.4764 | 64.4306 | -123.0308
144.2344 | 123.056 | -64.3524 | 58.58 | -0.00068679 | -0.0039252 | -5.128e-05 | 0.00021162 | -0.00062384 | 0.0011774 | 0.0014498 | 0.00025649 | 0.00081608 | -0.0001282 | 0.0041239 | -1.2882e-05 | -64.3161 | 0.010564 | -64.4248 | 58.4586 | 58.4091 | 58.4413 | -64.3969 | -64.2886 | 0.073618 | -64.4467 | 58.3184 | 58.5008 | 58.0278 | -64.5011 | -0.04453 | -0.12139 | 0.036272 | -0.0724 | -0.02787 | -0.1709 | -0.1387 | -0.14869 | -0.26163 | 0.0638 | -0.094331 | 0.054361 | -0.079242 | -0.55221 | 122.811 | 122.7615 | 122.7937 | 64.363 | -122.977 | 122.6708 | 122.8532 | 122.3802 | 64.426 | -123.0811
145.9688 | 123.0743 | -64.3341 | 58.5388 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00062384 | 0.0016046 | 0.0014498 | 0.00025649 | 0.00017528 | 8.5404e-05 | 0.0043375 | -1.2882e-05 | -64.2978 | 0.019721 | -64.4019 | 58.4769 | 58.3954 | 58.4505 | -64.3878 | -64.2749 | 0.06904 | -64.4284 | 58.3321 | 58.5145 | 57.9545 | -64.4874 | -0.053683 | -0.061883 | 0.036274 | -0.067819 | -0.014136 | -0.14343 | -0.088349 | -0.15327 | -0.20669 | 0.059225 | -0.094327 | 0.05894 | -0.024307 | -0.58427 | 122.811 | 122.7295 | 122.7846 | 64.3538 | -122.9266 | 122.6662 | 122.8486 | 122.2887 | 64.4031 | -123.0262
147.6562 | 123.143 | -64.3295 | 58.5297 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00021162 | -0.0012648 | 0.001391 | 0.0090803 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.2749 | 0.0243 | -64.3882 | 58.4952 | 58.4366 | 58.4825 | -64.3649 | -64.252 | 0.064461 | -64.4055 | 58.3504 | 58.542 | 58.0782 | -64.4599 | -0.035366 | -0.034414 | 0.054589 | -0.058661 | -0.023295 | -0.093069 | -0.047144 | -0.13037 | -0.17923 | 0.077541 | -0.07601 | 0.054361 | 0.012319 | -0.4515 | 122.8248 | 122.7661 | 122.812 | 64.3538 | -122.8946 | 122.68 | 122.8715 | 122.4077 | 64.394 | -122.9896
149.3906 | 123.1613 | -64.2517 | 58.5388 | -0.0083178 | -0.0041388 | 0.00016232 | 0.00021162 | -0.00062384 | 0.001391 | 0.0014498 | -0.00017091 | 0.00060248 | -0.0003418 | 0.0039103 | -1.2882e-05 | -64.2704 | 0.019721 | -64.3836 | 58.4998 | 58.4458 | 58.4825 | -64.3512 | -64.2383 | 0.064461 | -64.401 | 58.3688 | 58.5511 | 58.0782 | -64.4599 | -0.099449 | -0.038991 | -0.018652 | -0.1319 | -0.032454 | -0.093066 | -0.056299 | -0.20819 | -0.17007 | 0.013457 | -0.14925 | 0.058939 | 0.012322 | -0.46065 | 122.7515 | 122.6975 | 122.7342 | 64.2714 | -122.89 | 122.6205 | 122.8028 | 122.3299 | 64.3162 | -122.9987
151.125 | 123.0515 | -64.2654 | 58.6441 | -0.0083178 | -0.0043526 | -5.128e-05 | 0.00042522 | -0.0010512 | 0.0011774 | 0.0014498 | 4.2686e-05 | 0.00038888 | -0.0003418 | 0.0041239 | 0.00020092 | -64.1742 | 0.028878 | -64.2829 | 58.5914 | 58.5419 | 58.5741 | -64.2596 | -64.1513 | 0.073618 | -64.3048 | 58.4557 | 58.6427 | 58.0644 | -64.3683 | 0.005863 | -0.052709 | 0.091227 | -0.017448 | -0.023311 | -0.1022 | -0.070013 | -0.10288 | -0.18836 | 0.11419 | -0.039366 | 0.063515 | -0.001392 | -0.57967 | 122.8568 | 122.8074 | 122.8395 | 64.2943 | -122.9037 | 122.7212 | 122.9082 | 122.3299 | 64.3391 | -123.0124
152.8125 | 123.1613 | -64.2929 | 58.5617 | -0.0083178 | -0.0041388 | 0.00058972 | 0.00021162 | -0.0010512 | 0.001391 | -0.013811 | 4.2686e-05 | 0.0010299 | -0.0001282 | 0.0045513 | -1.2882e-05 | -64.2292 | 0.028878 | -64.3424 | 58.541 | 58.487 | 58.5237 | -64.3145 | -64.2016 | 0.06904 | -64.3598 | 58.41 | 58.5923 | 58.2155 | -64.4187 | -0.021618 | -0.020674 | 0.063752 | -0.0495 | -0.027882 | -0.074745 | -0.03798 | -0.12578 | -0.15175 | 0.091286 | -0.066844 | 0.058938 | 0.03064 | -0.34618 | 122.8339 | 122.7799 | 122.8166 | 64.3218 | -122.8762 | 122.7029 | 122.8853 | 122.5084 | 64.3619 | -122.9804
154.5469 | 123.0423 | -64.3341 | 58.5754 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00021162 | -0.00062384 | 0.001391 | 0.0014498 | 0.00047009 | 0.00017528 | -0.0003418 | 0.0043375 | -1.2882e-05 | -64.2337 | 0.019721 | -64.3424 | 58.541 | 58.4778 | 58.5191 | -64.3191 | -64.2108 | 0.06904 | -64.3689 | 58.4008 | 58.5786 | 58.243 | -64.437 | 0.015001 | -0.034406 | 0.10037 | -0.008302 | -0.023303 | -0.097635 | -0.056291 | -0.1029 | -0.17464 | 0.12333 | -0.034804 | 0.068096 | 0.003172 | -0.33244 | 122.8751 | 122.8119 | 122.8533 | 64.3538 | -122.8945 | 122.7349 | 122.9127 | 122.5771 | 64.4031 | -123.0124
156.2188 | 123.0377 | -64.2517 | 58.6487 | -0.00068679 | -0.0039252 | -5.128e-05 | 0.00042522 | -0.00062384 | 0.0016046 | -0.0061807 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0041239 | -1.2882e-05 | -64.2337 | 0.019721 | -64.347 | 58.5365 | 58.4824 | 58.5146 | -64.3283 | -64.2108 | 0.064461 | -64.3598 | 58.3962 | 58.5832 | 58.1743 | -64.4278 | -0.076554 | -0.11223 | 0.017975 | -0.095277 | -0.018723 | -0.1663 | -0.13411 | -0.17614 | -0.25246 | 0.04093 | -0.10804 | 0.068096 | -0.065492 | -0.47436 | 122.7882 | 122.7341 | 122.7663 | 64.2714 | -122.9769 | 122.6479 | 122.8349 | 122.426 | 64.3162 | -123.0765
157.9531 | 123.1476 | -64.2242 | 58.6395 | 0.0069442 | -0.0039252 | 0.00080352 | 0.00042522 | -0.0012648 | 0.0011774 | -0.0061807 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0043375 | 0.00020092 | -64.2292 | 0.0243 | -64.3424 | 58.541 | 58.4824 | 58.5191 | -64.3145 | -64.2062 | 0.06904 | -64.3598 | 58.3962 | 58.5832 | 58.0324 | -64.4233 | -0.090283 | -0.098493 | -0.004913 | -0.11817 | -0.027882 | -0.15714 | -0.12038 | -0.19903 | -0.2433 | 0.018042 | -0.13551 | 0.063517 | -0.056336 | -0.60715 | 122.7653 | 122.7066 | 122.7434 | 64.2485 | -122.9541 | 122.6205 | 122.8074 | 122.2566 | 64.2933 | -123.0628
159.6875 | 123.2025 | -64.3204 | 58.5251 | -0.00068679 | -0.0041388 | 0.00058972 | 0.00063882 | -0.00083764 | 0.00096355 | 0.016711 | 0.00025649 | 0.00081608 | -0.0001282 | 0.0041239 | 0.00041452 | -64.2749 | 0.015142 | -64.3928 | 58.4861 | 58.432 | 58.4642 | -64.3603 | -64.2566 | 0.064461 | -64.4193 | 58.3459 | 58.5237 | 58.1789 | -64.4736 | -0.039942 | -0.038993 | 0.045434 | -0.072395 | -0.032453 | -0.09307 | -0.06088 | -0.15326 | -0.17923 | 0.063808 | -0.098902 | 0.05436 | -0.001417 | -0.34619 | 122.8065 | 122.7524 | 122.7846 | 64.3355 | -122.8854 | 122.6662 | 122.844 | 122.4993 | 64.3848 | -122.9987
161.3594 | 123.0469 | -64.3387 | 58.58 | -0.00068679 | -0.0039252 | 0.00058972 | 0.00021162 | -0.00083764 | 0.001391 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0043375 | -1.2882e-05 | -64.2933 | 0.015142 | -64.4111 | 58.4815 | 58.4183 | 58.4459 | -64.3786 | -64.2657 | 0.06904 | -64.4284 | 58.3367 | 58.5191 | 58.0827 | -64.4828 | -0.039947 | -0.098503 | 0.045431 | -0.072398 | -0.032451 | -0.16174 | -0.13413 | -0.14411 | -0.24331 | 0.07296 | -0.089749 | 0.054361 | -0.060928 | -0.49727 | 122.8202 | 122.757 | 122.7846 | 64.3538 | -122.9586 | 122.6754 | 122.8578 | 122.4214 | 64.4077 | -123.0628
163.0938 | 123.1476 | -64.3478 | 58.4793 | 0.0069442 | -0.0039252 | 0.00016232 | 0.00042522 | -0.0010512 | 0.0011774 | -0.013811 | 4.2686e-05 | 0.00081608 | 8.5404e-05 | 0.0041239 | 0.00020092 | -64.2749 | 0.019721 | -64.3882 | 58.4952 | 58.4366 | 58.4642 | -64.3695 | -64.252 | 0.064461 | -64.4147 | 58.3504 | 58.5282 | 58.1148 | -64.4691 | -0.021635 | 0.01594 | 0.072899 | -0.040351 | -0.018716 | -0.042715 | -0.015104 | -0.12122 | -0.12887 | 0.095851 | -0.066858 | 0.05436 | 0.048938 | -0.36451 | 122.8431 | 122.7844 | 122.812 | 64.3676 | -122.8488 | 122.6983 | 122.8761 | 122.4626 | 64.4123 | -122.9484
164.7969 | 123.1522 | -64.2654 | 58.5709 | 0.0069442 | -0.0039252 | 0.00016232 | 0.00042522 | -0.00062384 | 0.0016046 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0043375 | -1.2882e-05 | -64.2658 | 0.019721 | -64.3745 | 58.509 | 58.4549 | 58.4825 | -64.3512 | -64.2337 | 0.06904 | -64.401 | 58.3733 | 58.5466 | 58.0873 | -64.4599 | -0.085716 | -0.061878 | -0.000341 | -0.10901 | -0.023297 | -0.11595 | -0.088343 | -0.19446 | -0.19753 | 0.031769 | -0.13552 | 0.058939 | -0.024301 | -0.48354 | 122.7744 | 122.7204 | 122.748 | 64.2852 | -122.922 | 122.6388 | 122.812 | 122.3528 | 64.3345 | -123.0308
166.5469 | 123.1842 | -64.2838 | 58.5571 | -0.0083178 | -0.0037114 | 0.00016232 | 0.00042522 | -0.0010512 | 0.0011774 | 0.0090803 | 0.00047009 | 0.00081608 | -0.0001282 | 0.0039103 | 0.00020092 | -64.2566 | 0.019721 | -64.3745 | 58.509 | 58.4595 | 58.4917 | -64.3512 | -64.2383 | 0.073618 | -64.3964 | 58.3733 | 58.5511 | 58.1011 | -64.4599 | -0.067406 | -0.048145 | 0.027126 | -0.090703 | -0.023297 | -0.09764 | -0.065453 | -0.17615 | -0.1838 | 0.0455 | -0.11263 | 0.063518 | -0.005989 | -0.45607 | 122.7927 | 122.7432 | 122.7754 | 64.3035 | -122.9083 | 122.6571 | 122.8349 | 122.3848 | 64.3574 | -123.017
168.2188 | 123.1842 | -64.3158 | 58.4747 | -0.0083178 | -0.0041388 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 4.2686e-05 | 0.00038888 | 8.5404e-05 | 0.0041239 | -0.00022648 | -64.2887 | 0.0243 | -64.3973 | 58.4769 | 58.4229 | 58.455 | -64.3832 | -64.2749 | 0.073618 | -64.4239 | 58.3367 | 58.5145 | 57.9683 | -64.492 | -0.067414 | 0.002204 | 0.027121 | -0.081551 | -0.014137 | -0.051874 | -0.019683 | -0.17616 | -0.13803 | 0.040915 | -0.10806 | 0.068098 | 0.03978 | -0.50645 | 122.7927 | 122.7387 | 122.7708 | 64.3401 | -122.8579 | 122.6525 | 122.8303 | 122.2841 | 64.3894 | -122.9667
169.8906 | 123.0515 | -64.3387 | 58.5388 | 0.0069442 | -0.0043526 | -5.128e-05 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00025649 | 0.00038888 | -0.0001282 | 0.0043375 | -1.2882e-05 | -64.2749 | 0.019721 | -64.3836 | 58.4952 | 58.4366 | 58.4688 | -64.3741 | -64.2566 | 0.064461 | -64.4101 | 58.3504 | 58.5328 | 58.1881 | -64.4782 | -0.035368 | -0.043569 | 0.063744 | -0.044928 | -0.00956 | -0.10222 | -0.070035 | -0.13953 | -0.18838 | 0.082118 | -0.071434 | 0.068097 | -0.005993 | -0.35077 | 122.8339 | 122.7753 | 122.8075 | 64.3584 | -122.9129 | 122.6891 | 122.8715 | 122.5267 | 64.4031 | -123.017
171.6406 | 123.1796 | -64.2838 | 58.5068 | -0.00068679 | -0.0043526 | 0.00016232 | 0.00021162 | -0.00062384 | 0.00096355 | -0.0061807 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0043375 | 0.00020092 | -64.2612 | 0.0243 | -64.3745 | 58.5044 | 58.4503 | 58.4825 | -64.3512 | -64.2383 | 0.064461 | -64.3826 | 58.3688 | 58.5466 | 58.1377 | -64.4553 | -0.067406 | -0.002369 | 0.022548 | -0.090703 | -0.023297 | -0.056444 | -0.024256 | -0.17157 | -0.13802 | 0.0455 | -0.098894 | 0.072675 | 0.039786 | -0.36909 | 122.7882 | 122.7341 | 122.7663 | 64.3081 | -122.8579 | 122.6525 | 122.8303 | 122.4214 | 64.3482 | -122.9621
173.375 | 123.1064 | -64.2838 | 58.6166 | -0.00068679 | -0.0041388 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00068369 | 0.00038888 | 8.5404e-05 | 0.0043375 | 0.00020092 | -64.2612 | 0.019721 | -64.3699 | 58.509 | 58.4549 | 58.4825 | -64.3466 | -64.2337 | 0.06904 | -64.3872 | 58.3779 | 58.5557 | 58.1423 | -64.4507 | -0.062827 | -0.10765 | 0.022548 | -0.086125 | -0.023298 | -0.16173 | -0.13412 | -0.16699 | -0.23873 | 0.050079 | -0.10347 | 0.063517 | -0.06092 | -0.47437 | 122.7927 | 122.7387 | 122.7663 | 64.3035 | -122.9632 | 122.6617 | 122.8395 | 122.426 | 64.3528 | -123.0674
175.0469 | 123.1705 | -64.238 | 58.5892 | -0.0083178 | -0.0041388 | 0.00037612 | 0.00021162 | -0.0010512 | 0.0011774 | 0.0090803 | 0.00047009 | 0.00081608 | -0.0003418 | 0.0043375 | 0.00041452 | -64.2475 | 0.015142 | -64.3561 | 58.5227 | 58.4458 | 58.5008 | -64.3328 | -64.2291 | 0.064461 | -64.3735 | 58.3825 | 58.5695 | 58.1972 | -64.437 | -0.094866 | -0.066453 | -0.009493 | -0.11817 | -0.0233 | -0.14342 | -0.088338 | -0.19903 | -0.20669 | 0.008882 | -0.13551 | 0.063518 | -0.019718 | -0.39196 | 122.7607 | 122.6837 | 122.7388 | 64.2531 | -122.922 | 122.6205 | 122.8074 | 122.4352 | 64.3024 | -123.0262
176.7344 | 123.0515 | -64.3021 | 58.6075 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.0012648 | 0.0016046 | 0.0014498 | 0.00025649 | 0.00060248 | -0.0003418 | 0.0039103 | -1.2882e-05 | -64.22 | 0.015142 | -64.3287 | 58.5639 | 58.5099 | 58.5466 | -64.2916 | -64.1833 | 0.073618 | -64.346 | 58.4283 | 58.6015 | 58.1194 | -64.4095 | 0.010431 | -0.043558 | 0.082064 | -0.02661 | -0.037041 | -0.097626 | -0.060863 | -0.10747 | -0.17921 | 0.11876 | -0.043953 | 0.063517 | -0.005979 | -0.48811 | 122.866 | 122.8119 | 122.8487 | 64.3172 | -122.8991 | 122.7303 | 122.9036 | 122.4214 | 64.3757 | -123.017
178.4531 | 123.0743 | -32.5882 | 90.3122 | -0.015949 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00083764 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00022648 | -32.7115 | 0.19829 | -32.734 | 90.3425 | 90.2418 | 90.2305 | -32.5505 | -32.6452 | 0.22014 | -32.7712 | 90.1481 | 90.3587 | 89.7072 | -32.6554 | 0.037669 | 0.03032 | -0.12334 | -0.14576 | -0.18343 | -0.070391 | -0.081646 | -0.06724 | -0.16411 | -0.056958 | -0.18304 | -0.1158 | 0.046496 | -0.60504 | 122.9307 | 122.83 | 122.8187 | 32.7865 | -122.8627 | 122.7363 | 122.9469 | 122.2953 | 32.8083 | -122.9676
180.1406 | 123.1247 | -64.0778 | 58.7906 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00083764 | 0.0016046 | 0.0090803 | 4.2686e-05 | 0.00060248 | -0.0003418 | 0.0045513 | -0.00022648 | -64.1055 | -0.044379 | -64.1822 | 58.7837 | 58.7342 | 58.7572 | -64.2367 | -64.0459 | 0.014095 | -64.1903 | 58.561 | 58.7526 | 58.2247 | -64.3409 | -0.15893 | -0.006901 | -0.02778 | -0.10441 | 0.054517 | -0.056364 | -0.033353 | -0.26309 | -0.22954 | 0.031813 | -0.11258 | 0.15051 | -0.03799 | -0.56591 | 122.8614 | 122.812 | 122.835 | 64.0334 | -123.0273 | 122.6388 | 122.8304 | 122.3024 | 64.0919 | -123.1314
181.8281 | 123.0743 | -64.0686 | 58.8135 | -0.0083178 | -0.0041388 | -5.128e-05 | 0.00063882 | -0.0010512 | 0.001391 | 0.0090803 | 4.2686e-05 | 0.00038888 | -0.0005554 | 0.0041239 | -0.00022648 | -64.0598 | -0.012329 | -64.1272 | 58.7608 | 58.7113 | 58.8122 | -64.0947 | -63.9773 | 0.046146 | -64.14 | 58.6206 | 58.8075 | 58.1972 | -64.2859 | -0.026134 | -0.052682 | 0.008849 | -0.058624 | -0.03249 | -0.10215 | -0.001298 | -0.2173 | -0.19291 | 0.091339 | -0.07137 | 0.14593 | -0.005936 | -0.61627 | 122.8294 | 122.7799 | 122.8808 | 64.0563 | -122.9082 | 122.6892 | 122.8761 | 122.2658 | 64.1147 | -123.0994
183.5625 | 123.1934 | -63.4689 | 59.3399 | -0.00068679 | -0.0043526 | -5.128e-05 | 0.00021162 | -0.00062384 | 0.001391 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0041239 | -1.2882e-05 | -63.5332 | 0.005985 | -63.587 | 59.2919 | 59.2287 | 59.27 | -63.5773 | -63.4507 | 0.055303 | -63.6134 | 59.1517 | 59.3341 | 58.9618 | -63.7548 | -0.10839 | -0.048017 | -0.064308 | -0.11806 | -0.009671 | -0.11116 | -0.069866 | -0.28583 | -0.18823 | 0.018219 | -0.14449 | 0.14134 | -0.005824 | -0.37807 | 122.7608 | 122.6977 | 122.739 | 63.4749 | -122.9172 | 122.6206 | 122.803 | 122.4308 | 63.5242 | -123.0947
185.3125 | 123.0377 | -32.254 | 90.6693 | -0.015949 | -0.0039252 | 0.00037612 | 0.00042522 | -0.00062384 | 0.00053635 | 0.0014498 | 4.2686e-05 | 0.00081608 | 0.0005128 | 0.0039103 | -0.00022648 | -32.1392 | 0.23034 | -32.1617 | 90.9285 | 90.8325 | 90.8212 | -31.9827 | -32.0774 | 0.25677 | -32.2035 | 90.6426 | 90.9448 | 90.2841 | -32.0739 | 0.27129 | 0.2593 | 0.11479 | 0.092354 | -0.17893 | 0.16324 | 0.15194 | 0.1801 | -0.026686 | 0.17663 | 0.050555 | -0.12955 | 0.2755 | -0.38519 | 123.1826 | 123.0865 | 123.0752 | 32.4844 | -122.652 | 122.8966 | 123.1988 | 122.5381 | 32.5108 | -122.7432
187.0625 | 123.0377 | -30.4413 | 92.5964 | 0.0069442 | -0.0034978 | 0.00016232 | 0.00063882 | -0.00083764 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00044008 | -30.7932 | 0.22118 | -30.7745 | 92.2792 | 92.1787 | 92.1581 | -30.6228 | -30.7175 | 0.2064 | -30.8436 | 91.9978 | 92.3 | 91.6851 | -30.7186 | -0.18152 | -0.31726 | -0.35191 | -0.33317 | -0.15165 | -0.41775 | -0.43829 | -0.27731 | -0.59864 | -0.27623 | -0.40231 | -0.125 | -0.29642 | -0.91133 | 122.7205 | 122.62 | 122.5994 | 30.6625 | -123.2192 | 122.4391 | 122.7413 | 122.1264 | 30.6477 | -123.315
188.7344 | 123.0927 | -29.6585 | 93.2602 | -0.00068679 | -0.0039252 | 0.00016232 | 0.00063882 | -0.0010512 | 0.00074995 | 0.0090803 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00044008 | -29.731 | 0.17539 | -29.7123 | 93.3414 | 93.2364 | 93.2204 | -29.5605 | -29.6324 | 0.17435 | -29.7905 | 93.0692 | 93.3577 | 92.7657 | -29.6517 | 0.098019 | 0.081166 | -0.072495 | -0.053786 | -0.1518 | -0.023773 | -0.039816 | 0.006776 | -0.19103 | 0.026145 | -0.13199 | -0.13876 | 0.097483 | -0.49453 | 122.9999 | 122.8949 | 122.8789 | 29.8339 | -122.8207 | 122.7277 | 123.0162 | 122.4242 | 29.8329 | -122.9119
190.4688 | 123.1064 | -29.4479 | 93.4387 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00063882 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0041239 | -0.00022648 | -29.6303 | 0.16624 | -29.6116 | 93.4558 | 93.3417 | 93.3303 | -29.4552 | -29.5225 | 0.16977 | -29.6943 | 93.1699 | 93.4676 | 92.7794 | -29.551 | -0.007237 | 0.017097 | -0.18234 | -0.16363 | -0.1564 | -0.096985 | -0.10846 | -0.10306 | -0.26883 | -0.074537 | -0.2464 | -0.14334 | 0.028841 | -0.65933 | 122.9038 | 122.7897 | 122.7782 | 29.6142 | -122.8939 | 122.6178 | 122.9155 | 122.2273 | 29.6177 | -122.9897
192.2031 | 123.0927 | -29.0863 | 93.8232 | -0.0083178 | -0.0034978 | 0.00058972 | 0.00063882 | -0.0010512 | 0.00074995 | -0.013811 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00044008 | -29.383 | 0.15708 | -29.3598 | 93.6939 | 93.6027 | 93.5729 | -29.2033 | -29.2661 | 0.16061 | -29.4425 | 93.4171 | 93.724 | 93.0953 | -29.2946 | -0.11703 | -0.12935 | -0.29674 | -0.27346 | -0.15643 | -0.22051 | -0.25031 | -0.20828 | -0.40611 | -0.17976 | -0.35621 | -0.14793 | -0.099278 | -0.72792 | 122.7802 | 122.689 | 122.6592 | 29.2434 | -123.0266 | 122.5034 | 122.8103 | 122.1816 | 29.2469 | -123.1178
193.8906 | 123.0331 | -29.2328 | 93.7363 | -0.00068679 | -0.0039252 | -5.128e-05 | -2.18e-06 | -0.00083764 | 0.00096355 | -0.013811 | 0.00025649 | 0.0010299 | -0.0001282 | 0.0045513 | -0.00044008 | -29.3922 | 0.1525 | -29.3735 | 93.6893 | 93.5844 | 93.5592 | -29.2262 | -29.2844 | 0.15146 | -29.4562 | 93.4034 | 93.7011 | 93.0404 | -29.3129 | 0.00656 | -0.046951 | -0.15941 | -0.14071 | -0.14727 | -0.15185 | -0.17707 | -0.080111 | -0.33287 | -0.051593 | -0.22346 | -0.14335 | -0.035196 | -0.69589 | 122.9221 | 122.8172 | 122.792 | 29.3853 | -122.9625 | 122.6362 | 122.9339 | 122.2732 | 29.3842 | -123.0492
195.6094 | 123.0789 | -29.0405 | 93.9102 | 0.0069442 | -0.0039252 | 0.00037612 | 0.00063882 | -0.00083764 | 0.00096355 | 0.0090803 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0041239 | -0.00022648 | -29.2274 | 0.14334 | -29.2133 | 93.8496 | 93.7584 | 93.7423 | -29.0522 | -29.115 | 0.15146 | -29.296 | 93.5728 | 93.8751 | 93.1915 | -29.1389 | -0.011702 | -0.060657 | -0.18685 | -0.17273 | -0.16103 | -0.1518 | -0.16788 | -0.098377 | -0.33742 | -0.074441 | -0.25546 | -0.15709 | -0.035159 | -0.71875 | 122.8901 | 122.7989 | 122.7829 | 29.1839 | -122.9624 | 122.6133 | 122.9156 | 122.232 | 29.192 | -123.0491
197.3438 | 123.0194 | -28.8345 | 94.0933 | 0.0069442 | -0.0039252 | 0.00037612 | 0.00063882 | -0.0012648 | 0.00074995 | 0.0090803 | 0.00047009 | 0.00038888 | 0.0002992 | 0.0043375 | -0.00022648 | -29.09 | 0.12045 | -29.0713 | 93.9915 | 93.8912 | 93.8797 | -28.9194 | -28.973 | 0.15146 | -29.1541 | 93.7102 | 94.0078 | 93.3655 | -29.0015 | -0.084906 | -0.10183 | -0.25549 | -0.2368 | -0.15189 | -0.20212 | -0.21363 | -0.167 | -0.38317 | -0.13849 | -0.31952 | -0.15251 | -0.085485 | -0.72787 | 122.826 | 122.7257 | 122.7142 | 28.955 | -123.0128 | 122.5447 | 122.8424 | 122.2 | 28.986 | -123.0949
199.0781 | 123.1384 | -28.6514 | 94.2032 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00042522 | -0.0010512 | 0.00032255 | -0.0061807 | 0.00068369 | 0.00060248 | 0.0002992 | 0.0043375 | -0.00022648 | -28.9573 | 0.11587 | -28.9248 | 94.1243 | 94.024 | 94.0079 | -28.7867 | -28.8402 | 0.14688 | -29.0213 | 93.8429 | 94.1452 | 93.6173 | -28.8642 | -0.13522 | -0.078923 | -0.30583 | -0.2734 | -0.13818 | -0.17919 | -0.19529 | -0.21275 | -0.36025 | -0.18882 | -0.36984 | -0.1571 | -0.05799 | -0.58591 | 122.7757 | 122.6754 | 122.6593 | 28.7673 | -122.9898 | 122.4944 | 122.7966 | 122.2687 | 28.7983 | -123.0674
200.8125 | 123.0515 | -28.9627 | 93.9743 | 0.0069442 | -0.0041388 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00074995 | 0.0090803 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0043375 | -1.2882e-05 | -29.1221 | 0.11129 | -29.1125 | 93.9503 | 93.8546 | 93.8339 | -28.9607 | -29.0188 | 0.14688 | -29.1953 | 93.6689 | 93.9758 | 93.4112 | -29.0382 | 0.002058 | -0.02402 | -0.15937 | -0.14983 | -0.15189 | -0.11973 | -0.14039 | -0.075462 | -0.30535 | -0.056107 | -0.23255 | -0.15709 | 0.001483 | -0.56306 | 122.913 | 122.8173 | 122.7966 | 29.074 | -122.935 | 122.6317 | 122.9385 | 122.374 | 29.1096 | -123.0125
202.5469 | 123.0286 | -29.0039 | 93.9423 | -0.00068679 | -0.0043526 | 0.00058972 | 0.00085262 | -0.0010512 | 0.00074995 | 0.0090803 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0041239 | -0.00044008 | -29.1816 | 0.10671 | -29.1629 | 93.8953 | 93.795 | 93.779 | -29.011 | -29.0692 | 0.13772 | -29.2456 | 93.614 | 93.9163 | 93.2418 | -29.0977 | -0.007112 | -0.046917 | -0.17769 | -0.15899 | -0.15188 | -0.14721 | -0.1633 | -0.093789 | -0.32825 | -0.065275 | -0.24172 | -0.14793 | -0.025995 | -0.70043 | 122.8992 | 122.799 | 122.7829 | 29.1106 | -122.9533 | 122.6179 | 122.9202 | 122.2457 | 29.1416 | -123.04
204.2188 | 123.1155 | -28.8071 | 94.0247 | -0.015949 | -0.0039252 | 0.00037612 | 0.00042522 | -0.0010512 | 0.00032255 | -0.0061807 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0045513 | -0.00022648 | -29.1083 | 0.083821 | -29.0805 | 93.9686 | 93.8683 | 93.8522 | -28.9423 | -29.0051 | 0.14688 | -29.1724 | 93.6918 | 93.9987 | 93.4021 | -29.029 | -0.13527 | -0.05606 | -0.30127 | -0.27342 | -0.13816 | -0.15635 | -0.17243 | -0.22194 | -0.33282 | -0.19801 | -0.3653 | -0.14335 | -0.025978 | -0.62257 | 122.7757 | 122.6754 | 122.6593 | 28.8909 | -122.967 | 122.4989 | 122.8057 | 122.2092 | 28.9539 | -123.0537
205.9531 | 123.0835 | -29.0176 | 93.956 | -0.00068679 | -0.0039252 | 0.00016232 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0034829 | -0.00022648 | -29.1862 | 0.092979 | -29.1675 | 93.8953 | 93.8042 | 93.779 | -29.0202 | -29.0646 | 0.1423 | -29.2456 | 93.614 | 93.9208 | 93.3014 | -29.0977 | -0.002537 | -0.06065 | -0.16854 | -0.14984 | -0.1473 | -0.15179 | -0.17703 | -0.080056 | -0.34199 | -0.046964 | -0.22799 | -0.14793 | -0.03515 | -0.65464 | 122.913 | 122.8218 | 122.7966 | 29.1106 | -122.9762 | 122.6316 | 122.9385 | 122.319 | 29.1599 | -123.0537
207.625 | 123.1567 | -28.8528 | 94.0338 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00085262 | -0.00062384 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0043375 | -0.00044008 | -29.0351 | 0.11587 | -29.0072 | 94.0419 | 93.9462 | 93.9392 | -28.8599 | -28.9181 | 0.13772 | -29.0991 | 93.7743 | 94.0674 | 93.512 | -28.9374 | -0.00707 | 0.008039 | -0.18224 | -0.15439 | -0.14732 | -0.087659 | -0.094596 | -0.084592 | -0.25956 | -0.06524 | -0.24626 | -0.16167 | 0.033546 | -0.52184 | 122.8947 | 122.799 | 122.7921 | 28.9687 | -122.8937 | 122.6271 | 122.9202 | 122.3648 | 28.9906 | -122.9712
209.3594 | 123.1155 | -28.9307 | 93.9789 | -0.0083178 | -0.0041388 | 0.00037612 | 0.00063882 | -0.00062384 | 0.001391 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0043375 | 0.00020092 | -29.058 | 0.10214 | -29.021 | 94.0281 | 93.9324 | 93.9117 | -28.8828 | -28.9456 | 0.1423 | -29.1128 | 93.7514 | 94.049 | 93.4479 | -28.9649 | 0.047856 | 0.049235 | -0.12732 | -0.090309 | -0.13817 | -0.046465 | -0.067136 | -0.034245 | -0.22752 | -0.014892 | -0.18218 | -0.14794 | 0.070163 | -0.53101 | 122.9588 | 122.8631 | 122.8424 | 29.0328 | -122.8617 | 122.682 | 122.9797 | 122.3785 | 29.073 | -122.9438
211.0781 | 123.056 | -28.7842 | 94.1345 | -0.00068679 | -0.0041388 | 0.00058972 | 0.00063882 | -0.00062384 | 0.00096355 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0041239 | -0.00022648 | -29.0397 | 0.13876 | -29.0164 | 94.0419 | 93.9462 | 93.9346 | -28.8737 | -28.9135 | 0.13772 | -29.0991 | 93.7605 | 94.0674 | 93.4158 | -28.9466 | -0.08947 | -0.092669 | -0.25549 | -0.23222 | -0.14274 | -0.18837 | -0.19988 | -0.16241 | -0.374 | -0.12933 | -0.31493 | -0.15251 | -0.067162 | -0.7187 | 122.826 | 122.7303 | 122.7188 | 28.9229 | -123.0082 | 122.5447 | 122.8515 | 122.2 | 28.9219 | -123.0811
212.75 | 123.024 | -28.6789 | 94.2719 | -0.0083178 | -0.0043526 | 0.00080352 | 0.00042522 | -0.0010512 | 0.00096355 | -0.0061807 | 0.00025649 | 0.00081608 | 0.0002992 | 0.0043375 | -0.00022648 | -28.8794 | 0.27612 | -28.8562 | 94.2113 | 94.1064 | 94.0857 | -28.7088 | -28.7761 | 0.13314 | -28.9389 | 93.9299 | 94.2276 | 93.7089 | -28.7909 | -0.029915 | -0.060599 | -0.20053 | -0.17726 | -0.14735 | -0.16544 | -0.18612 | -0.11202 | -0.34193 | -0.09725 | -0.25996 | -0.14794 | -0.04424 | -0.563 | 122.8901 | 122.7853 | 122.7646 | 28.955 | -122.9807 | 122.6088 | 122.9065 | 122.3877 | 28.812 | -123.0628
214.4844 | 123.0743 | -28.6469 | 94.313 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00085262 | -0.0012648 | 0.00096355 | 0.0014498 | 0.00068369 | 0.0010299 | -0.0001282 | 0.0039103 | -0.00022648 | -28.884 | 0.31275 | -28.8516 | 94.1975 | 94.0927 | 94.0857 | -28.7225 | -28.7807 | 0.14688 | -28.948 | 93.9162 | 94.2276 | 93.6997 | -28.8092 | -0.075695 | -0.11553 | -0.23715 | -0.20473 | -0.12903 | -0.22037 | -0.22732 | -0.16238 | -0.39686 | -0.13387 | -0.30116 | -0.13878 | -0.085438 | -0.61336 | 122.8444 | 122.7395 | 122.7326 | 28.9596 | -123.0356 | 122.563 | 122.8745 | 122.3465 | 28.7937 | -123.1223
216.2031 | 123.1476 | -28.6835 | 94.1986 | -0.00068679 | -0.0041388 | 0.00058972 | 0.00085262 | -0.00083764 | 0.00032255 | -0.0061807 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0045513 | -0.00022648 | -28.8703 | 0.30817 | -28.8424 | 94.2158 | 94.1156 | 94.0857 | -28.7088 | -28.7578 | 0.13314 | -28.9343 | 93.9299 | 94.2368 | 93.5761 | -28.7863 | -0.025337 | 0.017223 | -0.18679 | -0.15895 | -0.13361 | -0.083034 | -0.11288 | -0.10286 | -0.26868 | -0.074357 | -0.2508 | -0.14794 | 0.03816 | -0.62254 | 122.8993 | 122.799 | 122.7692 | 28.9916 | -122.9074 | 122.6134 | 122.9202 | 122.2595 | 28.8166 | -122.9849
217.9375 | 123.1384 | -28.6926 | 94.1574 | 0.0069442 | -0.0043526 | 0.00037612 | 0.00042522 | -0.0010512 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0041239 | -0.00022648 | -28.9023 | 0.28528 | -28.879 | 94.1838 | 94.0835 | 94.0628 | -28.7363 | -28.7899 | 0.13314 | -28.9709 | 93.8887 | 94.2047 | 93.5303 | -28.8138 | -0.043656 | 0.026372 | -0.20969 | -0.18642 | -0.14276 | -0.073888 | -0.094571 | -0.12118 | -0.26869 | -0.097253 | -0.27828 | -0.1571 | 0.047307 | -0.62712 | 122.8764 | 122.7761 | 122.7555 | 28.9779 | -122.8937 | 122.5813 | 122.8973 | 122.2229 | 28.8258 | -122.9712
219.6719 | 123.0743 | -28.6057 | 94.2856 | -0.0083178 | -0.0039252 | 0.0010171 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0090803 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0045513 | -1.2882e-05 | -28.8107 | 0.28528 | -28.7875 | 94.2754 | 94.1751 | 94.1636 | -28.6401 | -28.6983 | 0.13314 | -28.8702 | 93.994 | 94.2963 | 93.7546 | -28.7222 | -0.034473 | -0.010233 | -0.2051 | -0.18183 | -0.14736 | -0.11048 | -0.12201 | -0.11658 | -0.29156 | -0.092654 | -0.26452 | -0.14794 | 0.010707 | -0.53095 | 122.881 | 122.7808 | 122.7692 | 28.8909 | -122.9257 | 122.5997 | 122.9019 | 122.3603 | 28.7388 | -123.0078
221.3438 | 123.0469 | -28.3859 | 94.5786 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00074995 | -0.0061807 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0045513 | -0.00044008 | -28.5864 | 0.43637 | -28.5631 | 94.5043 | 94.3995 | 94.3833 | -28.4158 | -28.4739 | 0.13772 | -28.6412 | 94.2138 | 94.5252 | 93.9836 | -28.4979 | -0.029833 | -0.074283 | -0.20048 | -0.17722 | -0.14739 | -0.17909 | -0.19521 | -0.11194 | -0.36476 | -0.088024 | -0.25531 | -0.14337 | -0.053332 | -0.59499 | 122.8902 | 122.7854 | 122.7693 | 28.8223 | -122.9943 | 122.5997 | 122.9111 | 122.3695 | 28.5236 | -123.0764
223.0781 | 123.111 | -28.4821 | 94.4092 | -0.00068679 | -0.0043526 | 0.00058972 | 0.00042522 | -0.00083764 | 0.00074995 | 0.0090803 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0045513 | -1.2882e-05 | -28.6917 | 0.50505 | -28.6684 | 94.3944 | 94.2987 | 94.278 | -28.5165 | -28.5747 | 0.13772 | -28.7511 | 94.1131 | 94.4153 | 93.7638 | -28.6032 | -0.034438 | -0.014792 | -0.20965 | -0.18639 | -0.15195 | -0.11045 | -0.13115 | -0.12113 | -0.29612 | -0.092625 | -0.26907 | -0.14794 | 0.006153 | -0.64539 | 122.8764 | 122.7808 | 122.7601 | 28.9871 | -122.9257 | 122.5951 | 122.8974 | 122.2459 | 28.6198 | -123.0124
224.7656 | 123.143 | -28.5187 | 94.3268 | -0.00068679 | -0.0045662 | 0.00080352 | 0.00063882 | -0.0010512 | 0.00053635 | 0.0014498 | 0.00068369 | 0.00038888 | 0.0005128 | 0.0041239 | -1.2882e-05 | -28.4445 | 0.59205 | -28.4304 | 94.6325 | 94.5414 | 94.5207 | -28.2692 | -28.3366 | 0.1423 | -28.5039 | 94.3511 | 94.6672 | 93.9698 | -28.3559 | 0.24945 | 0.30568 | 0.074201 | 0.088302 | -0.16114 | 0.21463 | 0.19392 | 0.16275 | 0.024363 | 0.18209 | 0.014802 | -0.14795 | 0.34037 | -0.35695 | 123.1511 | 123.0601 | 123.0394 | 29.1107 | -122.596 | 122.8698 | 123.1858 | 122.4885 | 28.661 | -122.6827
226.5156 | 123.1064 | -28.3356 | 94.5374 | -0.0083178 | -0.0037114 | 0.00080352 | 0.00042522 | -0.00083764 | 0.0011774 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0043375 | -1.2882e-05 | -28.6047 | 0.55542 | -28.5952 | 94.4722 | 94.3674 | 94.3559 | -28.4387 | -28.5014 | 0.13772 | -28.6733 | 94.1863 | 94.4932 | 93.8554 | -28.5253 | -0.10308 | -0.065133 | -0.26915 | -0.25962 | -0.15654 | -0.16994 | -0.18148 | -0.18977 | -0.35103 | -0.16585 | -0.33772 | -0.14795 | -0.044185 | -0.68199 | 122.8078 | 122.703 | 122.6914 | 28.891 | -122.976 | 122.5219 | 122.8287 | 122.1909 | 28.4733 | -123.0627
228.25 | 123.0972 | -27.8549 | 95.0272 | -0.0083178 | -0.0037114 | 0.00080352 | 0.00042522 | -0.00062384 | 0.00074995 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0043375 | -0.00044008 | -28.0736 | 0.57831 | -28.0641 | 95.0125 | 94.9123 | 94.9007 | -27.9075 | -27.9657 | 0.13772 | -28.1376 | 94.7266 | 95.0289 | 94.5788 | -27.985 | -0.052578 | -0.014691 | -0.21871 | -0.20919 | -0.15662 | -0.11485 | -0.12644 | -0.13012 | -0.30058 | -0.11079 | -0.28266 | -0.15254 | 0.001705 | -0.44838 | 122.8674 | 122.7672 | 122.7556 | 28.4332 | -122.9347 | 122.5815 | 122.8838 | 122.4337 | 27.9926 | -123.0122
229.9219 | 123.0698 | -26.6281 | 96.3226 | 0.014575 | -0.0039252 | 0.00080352 | 0.00042522 | -0.00083764 | 0.001391 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0043375 | -1.2882e-05 | -26.8466 | 0.6012 | -26.8371 | 96.2303 | 96.1349 | 96.1141 | -26.6849 | -26.7386 | 0.14688 | -26.9105 | 95.949 | 96.2605 | 95.6044 | -26.7671 | -0.056812 | -0.092311 | -0.21851 | -0.20902 | -0.15221 | -0.18775 | -0.20858 | -0.13896 | -0.37359 | -0.1105 | -0.28237 | -0.14341 | -0.062122 | -0.71824 | 122.8584 | 122.763 | 122.7422 | 27.2293 | -123.0076 | 122.5772 | 122.8886 | 122.2325 | 26.775 | -123.0897
231.6562 | 123.1567 | -26.2482 | 96.5973 | -0.00068679 | -0.0043526 | 0.00080352 | 0.00063882 | -0.0010512 | 0.00074995 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0045513 | -1.2882e-05 | -26.4895 | 0.58747 | -26.48 | 96.5966 | 96.4966 | 96.4758 | -26.3232 | -26.3769 | 0.14688 | -26.5533 | 96.3062 | 96.6268 | 96.021 | -26.4008 | -0.075021 | -0.000697 | -0.24134 | -0.23186 | -0.15684 | -0.10067 | -0.12153 | -0.1526 | -0.29113 | -0.12873 | -0.30518 | -0.15257 | 0.029508 | -0.57625 | 122.8448 | 122.7448 | 122.7239 | 26.8356 | -122.9205 | 122.5543 | 122.875 | 122.2692 | 26.395 | -122.9981
233.3281 | 123.024 | -26.1612 | 96.8033 | -0.0083178 | -0.0041388 | 0.00037612 | 0.0010662 | -0.0010512 | 0.00096355 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.00022648 | -26.343 | 0.58747 | -26.3289 | 96.7385 | 96.6431 | 96.6223 | -26.1721 | -26.235 | 0.1423 | -26.4114 | 96.4573 | 96.7642 | 96.1584 | -26.2497 | -0.010891 | -0.064761 | -0.1818 | -0.16775 | -0.15686 | -0.16014 | -0.18101 | -0.088476 | -0.34603 | -0.073766 | -0.25021 | -0.16174 | -0.039128 | -0.64488 | 122.8997 | 122.8043 | 122.7835 | 26.7487 | -122.9754 | 122.6184 | 122.9253 | 122.3196 | 26.3035 | -123.053
235.0469 | 123.1567 | -25.5936 | 97.2519 | -0.00068679 | -0.0045662 | 0.00058972 | 0.00042522 | -0.0010512 | 0.00074995 | -0.013811 | 0.00068369 | 0.0010299 | -0.0003418 | 0.0043375 | -0.00022648 | -25.8211 | 0.75688 | -25.8162 | 97.2605 | 97.1651 | 97.1442 | -25.6592 | -25.7176 | 0.14688 | -25.894 | 96.9746 | 97.2907 | 96.6025 | -25.7323 | -0.065678 | 0.008567 | -0.22749 | -0.22261 | -0.15693 | -0.086754 | -0.10765 | -0.1387 | -0.27727 | -0.124 | -0.30044 | -0.16175 | 0.038804 | -0.64936 | 122.854 | 122.7587 | 122.7378 | 26.3504 | -122.9111 | 122.5682 | 122.8843 | 122.1961 | 25.7404 | -122.9842
236.7812 | 123.0515 | -25.8224 | 97.1558 | -0.00068679 | -0.0039252 | 0.00080352 | 0.0010662 | -0.0012648 | 0.00074995 | -0.013811 | 0.00025649 | 0.00081608 | 0.0002992 | 0.0041239 | -0.00044008 | -26.6635 | 0.64241 | -26.6586 | 96.418 | 96.3226 | 96.2926 | -26.5063 | -26.5646 | 0.16061 | -26.7457 | 96.1276 | 96.4345 | 95.7784 | -26.5931 | -0.6839 | -0.73773 | -0.84103 | -0.83613 | -0.15223 | -0.83315 | -0.86314 | -0.77063 | -1.0282 | -0.74218 | -0.9232 | -0.15257 | -0.72127 | -1.3774 | 122.2405 | 122.1451 | 122.1151 | 26.4649 | -123.6621 | 121.9501 | 122.2569 | 121.6008 | 25.9831 | -123.7488
238.5156 | 123.0331 | -24.9893 | 97.9614 | -0.0083178 | -0.0043526 | 0.00037612 | 0.00042522 | -0.0012648 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0041239 | -0.00044008 | -25.3724 | 0.59662 | -25.3721 | 97.6954 | 97.5956 | 97.5792 | -25.2151 | -25.278 | 0.14688 | -25.4499 | 97.4096 | 97.7302 | 97.0421 | -25.2973 | -0.22577 | -0.26602 | -0.38306 | -0.38277 | -0.15699 | -0.36587 | -0.38222 | -0.30796 | -0.55185 | -0.28869 | -0.46056 | -0.1526 | -0.23118 | -0.91935 | 122.6847 | 122.5849 | 122.5685 | 25.5859 | -123.1765 | 122.3989 | 122.7196 | 122.0314 | 25.1362 | -123.2587
240.25 | 123.1613 | -24.4675 | 98.4283 | -0.0083178 | -0.0043526 | 0.00058972 | 0.00085262 | -0.00083764 | 0.00074995 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0043375 | -1.2882e-05 | -24.5986 | 0.50963 | -24.6075 | 98.4646 | 98.3648 | 98.3438 | -24.4458 | -24.5134 | 0.1423 | -24.6944 | 98.1742 | 98.4949 | 97.8708 | -24.5326 | 0.021638 | 0.03623 | -0.13116 | -0.14004 | -0.16168 | -0.063529 | -0.084512 | -0.065146 | -0.25416 | -0.045897 | -0.22692 | -0.16178 | 0.066523 | -0.55754 | 122.932 | 122.8323 | 122.8113 | 24.9771 | -122.8742 | 122.6417 | 122.9623 | 122.3383 | 24.6098 | -122.961
241.9219 | 123.1522 | -24.353 | 98.497 | -0.00068679 | -0.0039252 | 0.00058972 | 0.00042522 | -0.00062384 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0049787 | -0.00044008 | -24.6124 | 0.6012 | -24.6121 | 98.46 | 98.3602 | 98.3393 | -24.455 | -24.5179 | 0.14688 | -24.699 | 98.1742 | 98.4903 | 97.8891 | -24.5326 | -0.10196 | -0.037013 | -0.25934 | -0.25906 | -0.1571 | -0.13677 | -0.15776 | -0.17959 | -0.32282 | -0.16492 | -0.34594 | -0.16635 | -0.00672 | -0.60789 | 122.813 | 122.7133 | 122.6923 | 24.9542 | -122.952 | 122.5272 | 122.8433 | 122.2421 | 24.4999 | -123.0296
243.6562 | 123.0286 | -24.733 | 98.1857 | -0.00068679 | -0.0041388 | 0.00058972 | 0.00085262 | -0.0010512 | 0.00096355 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0045513 | -0.00044008 | -24.942 | 0.67904 | -24.9463 | 98.1349 | 98.026 | 98.0096 | -24.7847 | -24.8476 | 0.1423 | -25.0241 | 97.8445 | 98.1515 | 97.5549 | -24.8669 | -0.0517 | -0.050799 | -0.20904 | -0.21333 | -0.16163 | -0.15975 | -0.17614 | -0.1339 | -0.34119 | -0.11464 | -0.29109 | -0.15719 | -0.034257 | -0.63085 | 122.8679 | 122.7589 | 122.7426 | 25.412 | -122.9704 | 122.5775 | 122.8844 | 122.2878 | 24.8753 | -123.0526
245.3281 | 123.1064 | -24.6826 | 98.2132 | -0.00068679 | -0.0039252 | 0.00058972 | 0.00063882 | -0.00083764 | 0.00074995 | 0.0090803 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0041239 | -0.00022648 | -24.9191 | 0.68362 | -24.9188 | 98.1532 | 98.0534 | 98.0371 | -24.7618 | -24.8293 | 0.15146 | -24.9966 | 97.8583 | 98.1744 | 97.6007 | -24.8394 | -0.079159 | -0.059952 | -0.2365 | -0.23622 | -0.15706 | -0.15975 | -0.17613 | -0.15678 | -0.35492 | -0.14668 | -0.31397 | -0.15719 | -0.03883 | -0.61253 | 122.8359 | 122.7361 | 122.7197 | 25.3662 | -122.975 | 122.5409 | 122.857 | 122.2833 | 24.8341 | -123.0526
247.0938 | 123.1613 | -25.1816 | 97.6685 | -0.00068679 | -0.0039252 | 0.00058972 | 0.00042522 | -0.0010512 | 0.0011774 | 0.0014498 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0041239 | -0.00065368 | -25.4182 | 0.74772 | -25.4224 | 97.6542 | 97.5589 | 97.5426 | -25.2609 | -25.3238 | 0.14688 | -25.5002 | 97.373 | 97.6845 | 97.1428 | -25.3385 | -0.079299 | -0.014257 | -0.23658 | -0.24086 | -0.16157 | -0.10953 | -0.12588 | -0.15691 | -0.29551 | -0.14222 | -0.31866 | -0.16176 | 0.015998 | -0.52565 | 122.8358 | 122.7405 | 122.7242 | 25.9293 | -122.9293 | 122.5545 | 122.866 | 122.3244 | 25.3285 | -123.0069
248.7812 | 123.0835 | -24.9344 | 97.998 | -0.00068679 | -0.0043526 | 0.00058972 | 0.00042522 | -0.00083764 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0043375 | -0.00022648 | -25.0885 | 0.82098 | -25.102 | 97.9701 | 97.8795 | 97.8585 | -24.9449 | -25.0033 | 0.14688 | -25.1889 | 97.6889 | 98.005 | 97.4633 | -25.0225 | -0.010546 | -0.027938 | -0.15413 | -0.16758 | -0.15703 | -0.1186 | -0.13955 | -0.08816 | -0.30918 | -0.0689 | -0.2545 | -0.16634 | 0.006911 | -0.53474 | 122.9045 | 122.8138 | 122.7929 | 25.7554 | -122.943 | 122.6233 | 122.9393 | 122.3977 | 25.0813 | -123.0206
250.5 | 123.1522 | -23.5565 | 99.3301 | -0.0083178 | -0.0041388 | 0.00016232 | 0.0010662 | -0.0010512 | 0.0011774 | -0.021442 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0045513 | -0.00022648 | -23.7242 | 1.0682 | -23.7331 | 99.3482 | 99.244 | 99.2229 | -23.5758 | -23.6205 | 0.15146 | -23.8061 | 99.0533 | 99.3785 | 98.7224 | -23.6535 | -0.019316 | 0.018065 | -0.16764 | -0.17654 | -0.15722 | -0.08617 | -0.10721 | -0.096962 | -0.27688 | -0.063998 | -0.2496 | -0.15264 | 0.048399 | -0.60772 | 122.9047 | 122.8005 | 122.7794 | 24.6247 | -122.906 | 122.6098 | 122.9351 | 122.2789 | 23.708 | -122.9836
252.2344 | 123.0698 | -22.5632 | 100.3922 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00063882 | -0.0010512 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0043375 | -0.00044008 | -22.868 | 1.288 | -22.8769 | 100.2089 | 100.1094 | 100.0745 | -22.715 | -22.7735 | 0.15146 | -22.9453 | 99.9232 | 100.2256 | 99.6748 | -22.7835 | -0.15183 | -0.18321 | -0.30483 | -0.31375 | -0.16192 | -0.28276 | -0.31761 | -0.22033 | -0.46898 | -0.21028 | -0.38215 | -0.16182 | -0.16657 | -0.71738 | 122.7721 | 122.6726 | 122.6377 | 23.8512 | -123.1071 | 122.4863 | 122.7888 | 122.2379 | 22.7146 | -123.1757
253.9844 | 123.0652 | -22.8699 | 100.0626 | 0.0069442 | -0.0043526 | 0.00058972 | 0.00063882 | -0.0010512 | 0.00096355 | 0.0014498 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0041239 | -0.00044008 | -22.9229 | 1.4757 | -22.9364 | 100.154 | 100.0544 | 100.0288 | -22.7699 | -22.8238 | 0.14688 | -23.0094 | 99.8637 | 100.1798 | 99.4779 | -22.8476 | 0.099929 | 0.091439 | -0.053067 | -0.066565 | -0.16649 | -0.008122 | -0.033802 | 0.022264 | -0.19891 | 0.046052 | -0.13955 | -0.16182 | 0.11723 | -0.58467 | 123.0239 | 122.9243 | 122.8986 | 24.3456 | -122.8325 | 122.7335 | 123.0497 | 122.3478 | 23.0168 | -122.9102
255.7188 | 123.1155 | -22.316 | 100.5661 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00063882 | -0.0010512 | 0.00096355 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0047649 | -0.00022648 | -22.5109 | 1.494 | -22.5152 | 100.5706 | 100.4528 | 100.4454 | -22.3533 | -22.4117 | 0.15146 | -22.5928 | 100.2666 | 100.5873 | 99.9449 | -22.4309 | -0.037283 | 0.004532 | -0.19491 | -0.19926 | -0.16197 | -0.1133 | -0.12069 | -0.11496 | -0.29954 | -0.095758 | -0.27678 | -0.16182 | 0.021188 | -0.62119 | 122.8866 | 122.7688 | 122.7614 | 23.81 | -122.9194 | 122.5825 | 122.9033 | 122.2609 | 22.4674 | -122.997
257.3906 | 123.1567 | -23.3368 | 99.5453 | 0.0069442 | -0.0041388 | 0.00058972 | 0.00085262 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00022648 | -23.3945 | 1.4757 | -23.408 | 99.6778 | 99.5737 | 99.5526 | -23.2599 | -23.3046 | 0.13772 | -23.4856 | 99.3875 | 99.7082 | 99.0887 | -23.3284 | 0.076903 | 0.13256 | -0.057722 | -0.071209 | -0.14811 | 0.028364 | 0.007296 | 0.008407 | -0.1578 | 0.032206 | -0.14882 | -0.15722 | 0.16291 | -0.45658 | 123.0146 | 122.9104 | 122.8894 | 24.8125 | -122.8052 | 122.7243 | 123.045 | 122.4255 | 23.4745 | -122.8737
259.1406 | 123.0194 | -22.7417 | 100.2136 | -0.00068679 | -0.0043526 | 0.00016232 | 0.00085262 | -0.0010512 | 0.00096355 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0043375 | -0.00044008 | -22.9733 | 1.755 | -22.9822 | 100.1082 | 99.9949 | 99.9692 | -22.8157 | -22.8788 | 0.15146 | -23.0506 | 99.8179 | 100.1294 | 99.4275 | -22.8934 | -0.074034 | -0.10541 | -0.2316 | -0.24052 | -0.16649 | -0.21871 | -0.24439 | -0.1517 | -0.39575 | -0.13707 | -0.30893 | -0.15724 | -0.084194 | -0.7861 | 122.8499 | 122.7366 | 122.7109 | 24.4967 | -123.0294 | 122.5596 | 122.8711 | 122.1692 | 22.8932 | -123.107
260.8125 | 123.056 | -22.2244 | 100.7584 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00085262 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00025649 | 0.00060248 | -0.0001282 | 0.0045513 | -0.00065368 | -22.2911 | 2.135 | -22.2955 | 100.7904 | 100.6863 | 100.6514 | -22.1335 | -22.192 | 0.14688 | -22.373 | 100.4909 | 100.8071 | 100.1235 | -22.2157 | 0.090952 | 0.032034 | -0.066697 | -0.071053 | -0.16201 | -0.072031 | -0.10691 | 0.008694 | -0.26745 | 0.032467 | -0.14856 | -0.15725 | 0.0487 | -0.63489 | 123.0148 | 122.9108 | 122.8759 | 24.3595 | -122.8918 | 122.7153 | 123.0315 | 122.3479 | 22.3713 | -122.9741
262.5469 | 123.0194 | -21.9406 | 101.0193 | -0.00068679 | -0.0047798 | 0.00058972 | 0.00063882 | -0.00062384 | 0.00032255 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0047649 | -0.00044008 | -22.1538 | 2.2129 | -22.1627 | 100.9369 | 100.8237 | 100.8071 | -22.0007 | -22.0546 | 0.15604 | -22.2402 | 100.6283 | 100.9536 | 100.302 | -22.0875 | -0.060072 | -0.082383 | -0.21316 | -0.2221 | -0.16202 | -0.19559 | -0.21217 | -0.14691 | -0.39102 | -0.11398 | -0.29959 | -0.15268 | -0.065709 | -0.71725 | 122.8775 | 122.7643 | 122.7477 | 24.1535 | -123.02 | 122.5689 | 122.8942 | 122.2427 | 22.0966 | -123.1068
264.2188 | 123.0698 | -21.4279 | 101.532 | -0.0083178 | -0.0041388 | 0.00080352 | 0.00085262 | -0.00062384 | 0.00074995 | 0.0090803 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.00065368 | -21.5952 | 2.3136 | -21.6087 | 101.4817 | 101.3686 | 101.3566 | -21.4421 | -21.4914 | 0.14688 | -21.677 | 101.1868 | 101.4984 | 100.9385 | -21.5243 | -0.014139 | -0.05025 | -0.16729 | -0.18082 | -0.16668 | -0.16339 | -0.17543 | -0.096414 | -0.34514 | -0.063499 | -0.2491 | -0.15269 | -0.033551 | -0.59352 | 122.9096 | 122.7965 | 122.7845 | 23.7415 | -122.974 | 122.6148 | 122.9263 | 122.3664 | 21.5748 | -123.0563
265.9531 | 123.175 | -21.4142 | 101.4587 | -0.00068679 | -0.0043526 | 0.00058972 | 0.00063882 | -0.0014786 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0045513 | -1.2882e-05 | -21.6089 | 2.0206 | -21.6042 | 101.4726 | 101.3594 | 101.3428 | -21.4558 | -21.5097 | 0.15146 | -21.6953 | 101.1731 | 101.4939 | 100.8057 | -21.5335 | -0.041608 | 0.013836 | -0.19476 | -0.18997 | -0.14837 | -0.099307 | -0.11592 | -0.1193 | -0.28564 | -0.095546 | -0.28115 | -0.16184 | 0.035113 | -0.65306 | 122.8868 | 122.7736 | 122.757 | 23.4348 | -122.9145 | 122.5873 | 122.908 | 122.2199 | 21.5656 | -122.9922
267.625 | 123.1613 | -23.1903 | 99.6735 | -0.00068679 | -0.0043526 | 0.00080352 | 0.00085262 | -0.00062384 | 0.00074995 | 0.0090803 | 0.00089729 | 0.0010299 | -0.0001282 | 0.0045513 | -1.2882e-05 | -22.6437 | 1.8557 | -22.648 | 100.4287 | 100.3338 | 100.3035 | -22.5135 | -22.5537 | 0.12398 | -22.7393 | 100.1292 | 100.4545 | 100.0868 | -22.6049 | 0.67678 | 0.75524 | 0.54665 | 0.5423 | -0.13448 | 0.66029 | 0.63001 | 0.58538 | 0.45574 | 0.63663 | 0.45103 | -0.13435 | 0.78105 | 0.41338 | 123.619 | 123.5241 | 123.4938 | 25.046 | -122.187 | 123.3195 | 123.6448 | 123.2772 | 23.3143 | -122.2784
269.3594 | 123.0606 | -22.0276 | 100.9323 | -0.00068679 | -0.0041388 | 0.00080352 | 0.00042522 | -0.0012648 | 0.00074995 | 0.0090803 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0043375 | -0.00044008 | -22.2545 | 2.0618 | -22.2543 | 100.8316 | 100.723 | 100.7064 | -22.1014 | -22.1553 | 0.15604 | -22.3318 | 100.5367 | 100.8528 | 100.1509 | -22.1791 | -0.073833 | -0.10071 | -0.22691 | -0.22669 | -0.15285 | -0.20935 | -0.22592 | -0.15151 | -0.39562 | -0.12774 | -0.30419 | -0.15267 | -0.079464 | -0.78137 | 122.8592 | 122.7506 | 122.734 | 24.0894 | -123.0337 | 122.5643 | 122.8804 | 122.1785 | 22.1836 | -123.1114
271.0938 | 123.1384 | -21.698 | 101.1978 | -0.0083178 | -0.0039252 | 0.00037612 | 0.00085262 | -0.00062384 | 0.00096355 | -0.0061807 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0043375 | -0.00065368 | -21.8379 | 2.3228 | -21.8331 | 101.2437 | 101.1351 | 101.1139 | -21.6893 | -21.7341 | 0.14688 | -21.9243 | 100.9488 | 101.2649 | 100.6271 | -21.767 | 0.00868 | 0.045841 | -0.13987 | -0.13508 | -0.14375 | -0.06275 | -0.083928 | -0.06901 | -0.24906 | -0.03609 | -0.22627 | -0.15726 | 0.067108 | -0.5707 | 122.9417 | 122.8331 | 122.8119 | 24.0208 | -122.8871 | 122.6468 | 122.9629 | 122.3251 | 21.8449 | -122.9648
272.8438 | 123.0743 | -21.4508 | 101.5091 | 0.0069442 | -0.0039252 | 0.00080352 | 0.00085262 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00025649 | 0.0010299 | 0.0002992 | 0.0043375 | -0.00022648 | -21.6181 | 2.309 | -21.6179 | 101.4588 | 101.3457 | 101.3291 | -21.4741 | -21.5235 | 0.15604 | -21.7136 | 101.1594 | 101.4801 | 100.8057 | -21.5564 | -0.023302 | -0.050254 | -0.16729 | -0.16709 | -0.14379 | -0.1634 | -0.18001 | -0.10558 | -0.34973 | -0.072661 | -0.26284 | -0.15727 | -0.028977 | -0.70341 | 122.9096 | 122.7965 | 122.7799 | 23.7598 | -122.9832 | 122.6102 | 122.9309 | 122.2565 | 21.6068 | -123.0655
274.5781 | 123.175 | -23.0896 | 99.7925 | -0.00068679 | -0.0043526 | 0.00037612 | 0.00063882 | -0.00062384 | 0.00074995 | 0.0014498 | 0.00068369 | 0.0010299 | -0.0001282 | 0.0043375 | -0.00022648 | -23.074 | 2.3319 | -23.0692 | 100.0029 | 99.8988 | 99.8822 | -22.921 | -22.9749 | 0.12856 | -23.1651 | 99.7126 | 100.0241 | 99.3543 | -22.9987 | 0.16855 | 0.21043 | 0.015573 | 0.020392 | -0.14816 | 0.10628 | 0.089763 | 0.09089 | -0.079917 | 0.11468 | -0.0755 | -0.16639 | 0.23164 | -0.43821 | 123.0925 | 122.9884 | 122.9718 | 25.4215 | -122.7135 | 122.8022 | 123.1137 | 122.4439 | 23.2182 | -122.7912
276.2344 | 123.0423 | -22.2107 | 100.7492 | -0.0083178 | -0.0041388 | 0.00080352 | 0.00063882 | -0.0010512 | 0.00074995 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0043375 | -0.00044008 | -22.5796 | 2.5517 | -22.5839 | 100.4928 | 100.3979 | 100.3722 | -22.4403 | -22.4804 | 0.16061 | -22.6614 | 100.2025 | 100.5186 | 100.0502 | -22.5134 | -0.22957 | -0.25641 | -0.36887 | -0.37322 | -0.14365 | -0.35135 | -0.37705 | -0.30266 | -0.54675 | -0.26973 | -0.45075 | -0.14809 | -0.2306 | -0.69899 | 122.7035 | 122.6086 | 122.5828 | 24.7624 | -123.1895 | 122.4132 | 122.7293 | 122.2609 | 22.3713 | -123.2626
277.9688 | 123.143 | -24.3896 | 98.4924 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0045513 | -1.2882e-05 | -23.5914 | 2.9638 | -23.582 | 99.4993 | 99.3768 | 99.3832 | -23.4568 | -23.5106 | 0.10567 | -23.7008 | 99.1815 | 99.5113 | 98.901 | -23.5527 | 0.93286 | 1.0069 | 0.79826 | 0.80767 | -0.12519 | 0.88433 | 0.89074 | 0.8369 | 0.68903 | 0.87902 | 0.68884 | -0.14806 | 1.0189 | 0.40855 | 123.8889 | 123.7664 | 123.7728 | 27.3534 | -121.9492 | 123.5711 | 123.901 | 123.2906 | 24.4953 | -122.0452
279.7031 | 123.1522 | -24.1241 | 98.7488 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00032255 | 0.0014498 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0047649 | -0.00065368 | -24.3514 | 3.1057 | -24.342 | 98.7255 | 98.6258 | 98.6094 | -24.2077 | -24.2524 | 0.13314 | -24.4334 | 98.4352 | 98.7421 | 98.2417 | -24.2762 | -0.08358 | -0.023236 | -0.22725 | -0.21782 | -0.13424 | -0.12296 | -0.13939 | -0.15205 | -0.31362 | -0.12823 | -0.30926 | -0.1572 | -0.006666 | -0.50711 | 122.8497 | 122.75 | 122.7335 | 27.2298 | -122.9565 | 122.5593 | 122.8663 | 122.3658 | 24.2573 | -123.025
281.375 | 123.1155 | -23.8541 | 99.0601 | -0.015949 | -0.0041388 | 0.00058972 | 0.0010662 | -0.0010512 | 0.00074995 | 0.0014498 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0043375 | -0.00022648 | -24.0538 | 3.3942 | -24.049 | 99.0231 | 98.9189 | 98.9024 | -23.8918 | -23.9548 | 0.13772 | -24.1404 | 98.7328 | 99.0397 | 98.4385 | -23.974 | -0.037716 | -0.036921 | -0.19974 | -0.1949 | -0.15718 | -0.14119 | -0.15764 | -0.11993 | -0.32729 | -0.1007 | -0.2863 | -0.16637 | -0.020337 | -0.62151 | 122.8772 | 122.7729 | 122.7565 | 27.2482 | -122.9518 | 122.5868 | 122.8938 | 122.2926 | 23.9918 | -123.0341
283.125 | 123.0652 | -22.4075 | 100.5524 | 0.014575 | -0.0043526 | 0.00058972 | 0.00085262 | -0.00083764 | 0.00074995 | -0.013811 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0045513 | -0.00044008 | -23.0282 | 3.7375 | -23.0188 | 100.0487 | 99.9537 | 99.9372 | -22.8844 | -22.9291 | 0.13772 | -23.1193 | 99.7583 | 100.0882 | 99.4962 | -22.9575 | -0.47688 | -0.50367 | -0.62071 | -0.61132 | -0.13443 | -0.59866 | -0.61518 | -0.54997 | -0.79402 | -0.5216 | -0.71178 | -0.16181 | -0.46415 | -1.0562 | 122.4562 | 122.3612 | 122.3447 | 26.1451 | -123.4368 | 122.1659 | 122.4958 | 121.9037 | 22.5453 | -123.5099
284.8125 | 123.1247 | -23.1491 | 99.733 | -0.00068679 | -0.0045662 | 0.00058972 | 0.00085262 | -0.00083764 | 0.00074995 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0041239 | -1.2882e-05 | -23.4632 | 3.5819 | -23.4629 | 99.6183 | 99.5141 | 99.4976 | -23.3194 | -23.3641 | 0.1423 | -23.5497 | 99.3188 | 99.6395 | 98.9514 | -23.3925 | -0.17031 | -0.11464 | -0.31408 | -0.31383 | -0.14353 | -0.21885 | -0.23533 | -0.24338 | -0.41416 | -0.215 | -0.4006 | -0.15722 | -0.093452 | -0.78162 | 122.7674 | 122.6632 | 122.6467 | 26.731 | -123.0524 | 122.4679 | 122.7886 | 122.1005 | 23.2914 | -123.1255
286.5469 | 123.0835 | -27.507 | 95.4025 | -0.0083178 | -0.0041388 | 0.00058972 | 0.00063882 | -0.0010512 | 0.00096355 | 0.0014498 | 0.00089729 | 0.00081608 | 8.5404e-05 | 0.0045513 | -1.2882e-05 | -26.8787 | 3.2522 | -26.8463 | 96.2532 | 96.1486 | 96.1644 | -26.7857 | -26.7981 | 0.078197 | -26.97 | 95.9857 | 96.2422 | 95.9982 | -26.8587 | 0.72136 | 0.85069 | 0.62835 | 0.66073 | -0.060629 | 0.74609 | 0.76189 | 0.64837 | 0.58314 | 0.70888 | 0.53701 | -0.11135 | 0.83967 | 0.59562 | 123.7602 | 123.6556 | 123.6714 | 30.7592 | -122.1882 | 123.4927 | 123.7492 | 123.5052 | 27.5852 | -122.2612
288.2969 | 123.0606 | -28.5278 | 94.4733 | 0.0069442 | -0.0041388 | 0.00037612 | 0.00085262 | -0.0012648 | 0.00096355 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0045513 | -0.00022648 | -24.7818 | 2.7257 | -24.7723 | 98.2814 | 98.1954 | 98.1836 | -24.629 | -24.7011 | 0.091933 | -24.8867 | 98.0597 | 98.3071 | 97.6327 | -24.7936 | 3.8988 | 3.8082 | 3.7461 | 3.7555 | -0.14334 | 3.7221 | 3.7103 | 3.7342 | 3.5865 | 3.8267 | 3.6411 | -0.093089 | 3.8339 | 3.1594 | 126.8093 | 126.7232 | 126.7114 | 31.2535 | -119.1023 | 126.5876 | 126.835 | 126.1605 | 28.6198 | -119.2669
289.9688 | 123.1293 | -24.7101 | 98.2132 | 0.0069442 | -0.0041388 | 0.00037612 | 0.0010662 | -0.0010512 | 0.00096355 | 0.0014498 | 0.00047009 | 0.00081608 | -0.0001282 | 0.0047649 | -0.00044008 | -24.8367 | 3.005 | -24.8181 | 98.2402 | 98.1359 | 98.1149 | -24.6656 | -24.7423 | 0.13772 | -24.9233 | 98.0277 | 98.2659 | 97.7563 | -24.7478 | 0.044464 | 0.027038 | -0.12662 | -0.10803 | -0.15249 | -0.077326 | -0.098293 | -0.037735 | -0.18552 | -0.032217 | -0.21324 | -0.17551 | 0.052742 | -0.45686 | 122.9503 | 122.846 | 122.825 | 27.7151 | -122.8788 | 122.7378 | 122.976 | 122.4664 | 24.8478 | -122.961
291.7031 | 122.9965 | -23.8037 | 99.1333 | -0.00068679 | -0.0043526 | 0.00058972 | 0.00085262 | -0.0014786 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0047649 | -0.00022648 | -24.4384 | 2.9088 | -24.4335 | 98.6294 | 98.5342 | 98.5132 | -24.281 | -24.3485 | 0.14688 | -24.5204 | 98.4077 | 98.6597 | 97.9944 | -24.354 | -0.47728 | -0.5039 | -0.63468 | -0.62983 | -0.15255 | -0.59906 | -0.62006 | -0.55033 | -0.72561 | -0.54482 | -0.71669 | -0.16636 | -0.4736 | -1.1389 | 122.4331 | 122.3379 | 122.317 | 26.7125 | -123.4143 | 122.2114 | 122.4634 | 121.7981 | 23.9506 | -123.4873
293.375 | 123.0103 | -20.2332 | 102.7359 | -0.00068679 | -0.0045662 | 0.00037612 | 0.00042522 | -0.0012648 | 0.00096355 | -0.0061807 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0043375 | -0.00044008 | -20.24 | 3.3484 | -20.2307 | 102.8507 | 102.7331 | 102.7118 | -20.0913 | -20.1361 | 0.15604 | -20.3263 | 102.6062 | 102.8583 | 102.2067 | -20.1782 | 0.14188 | 0.11477 | -0.006851 | 0.002479 | -0.1394 | -0.002791 | -0.024081 | 0.054995 | -0.12973 | 0.097036 | -0.093146 | -0.14814 | 0.12238 | -0.52916 | 123.0838 | 122.9663 | 122.945 | 23.5815 | -122.8272 | 122.8393 | 123.0914 | 122.4399 | 20.3892 | -122.9141
295.0938 | 123.111 | -20.4483 | 102.4429 | -0.00068679 | -0.0041388 | 0.00080352 | 0.00085262 | -0.0012648 | 0.00032255 | -0.0061807 | 0.00089729 | 0.0012435 | 8.5404e-05 | 0.0045513 | -0.00022648 | -20.9542 | 3.4674 | -20.9586 | 102.109 | 102.0142 | 101.9976 | -20.801 | -20.8641 | 0.16061 | -21.0406 | 101.8965 | 102.1394 | 101.4467 | -20.8833 | -0.3527 | -0.33396 | -0.50593 | -0.51032 | -0.15761 | -0.42871 | -0.44537 | -0.43499 | -0.54643 | -0.41583 | -0.59228 | -0.15728 | -0.3035 | -0.99624 | 122.5573 | 122.4625 | 122.4459 | 23.9157 | -123.2439 | 122.3448 | 122.5877 | 121.895 | 20.6089 | -123.3262
296.8281 | 123.0194 | -21.286 | 101.7014 | -0.0083178 | -0.0045662 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00096355 | 0.016711 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0045513 | -0.00044008 | -21.5769 | 3.385 | -21.5584 | 101.5092 | 101.4098 | 101.384 | -21.4237 | -21.4777 | 0.14688 | -21.6587 | 101.2876 | 101.5305 | 100.911 | -21.506 | -0.13773 | -0.19215 | -0.29088 | -0.27237 | -0.13464 | -0.29155 | -0.31733 | -0.22001 | -0.41379 | -0.19167 | -0.37269 | -0.15269 | -0.17087 | -0.79036 | 122.7952 | 122.6958 | 122.67 | 24.671 | -123.1251 | 122.5736 | 122.8165 | 122.197 | 21.4329 | -123.2074
298.5781 | 123.0194 | -19.3359 | 103.6331 | -0.00068679 | -0.0041388 | 0.00080352 | 0.00085262 | -0.0012648 | 0.00053635 | 0.0090803 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.00065368 | -19.6036 | 3.4308 | -19.608 | 103.4733 | 103.3558 | 103.3299 | -19.464 | -19.5043 | 0.16977 | -19.6899 | 103.238 | 103.481 | 102.8386 | -19.5417 | -0.12802 | -0.15979 | -0.26767 | -0.27209 | -0.14407 | -0.27727 | -0.30319 | -0.20577 | -0.39511 | -0.16832 | -0.35392 | -0.14816 | -0.15215 | -0.79453 | 122.8093 | 122.6918 | 122.6659 | 22.7667 | -123.0971 | 122.5739 | 122.8169 | 122.1745 | 19.5057 | -123.1748
300.2344 | 123.0423 | -15.5548 | 107.428 | -0.00068679 | -0.0043526 | 0.00037612 | 0.0010662 | -0.0012648 | 0.00096355 | 0.0014498 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.00044008 | -15.9913 | 2.2632 | -16.0141 | 107.0399 | 106.932 | 106.8967 | -15.8924 | -15.9054 | 0.18809 | -16.091 | 106.8092 | 107.0523 | 106.5381 | -15.9611 | -0.33759 | -0.38808 | -0.43645 | -0.45927 | -0.12168 | -0.49599 | -0.53132 | -0.40626 | -0.61875 | -0.35058 | -0.53618 | -0.12993 | -0.3757 | -0.88988 | 122.5947 | 122.4868 | 122.4515 | 17.818 | -123.3204 | 122.364 | 122.6071 | 122.0929 | 15.7429 | -123.389
301.9688 | 123.1338 | -12.5244 | 110.4309 | -0.00068679 | -0.0041388 | 0.00058972 | 0.0010662 | -0.0014786 | 0.00074995 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0047649 | -0.00065368 | -13.0428 | 1.3567 | -13.0519 | 109.9655 | 109.8533 | 109.8178 | -12.9756 | -12.9521 | 0.19267 | -13.1423 | 109.7303 | 109.9826 | 109.3127 | -13.0535 | -0.45121 | -0.46542 | -0.51836 | -0.52752 | -0.076307 | -0.57757 | -0.6131 | -0.5291 | -0.7006 | -0.42771 | -0.61789 | -0.088785 | -0.44833 | -1.1182 | 122.4899 | 122.3778 | 122.3422 | 13.8811 | -123.4065 | 122.2547 | 122.507 | 121.8371 | 12.7171 | -123.4844
303.7031 | 123.0927 | -11.4944 | 111.438 | -0.00068679 | -0.0041388 | 0.00037612 | 0.00085262 | -0.0012648 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0043375 | -0.00044008 | -11.5273 | 0.83013 | -11.5365 | 111.4626 | 111.3461 | 111.315 | -11.4875 | -11.4411 | 0.18351 | -11.6313 | 111.2366 | 111.4935 | 110.7779 | -11.5562 | 0.006972 | 0.02463 | -0.032887 | -0.042074 | -0.049046 | -0.091921 | -0.12297 | -0.0618 | -0.20135 | 0.053298 | -0.13688 | -0.075084 | 0.055533 | -0.66011 | 122.9571 | 122.8405 | 122.8095 | 12.3246 | -122.9255 | 122.7311 | 122.988 | 122.2723 | 11.678 | -122.9942
305.4531 | 123.1247 | -13.9389 | 108.989 | -0.00068679 | -0.0039252 | 0.00037612 | 0.00085262 | -0.0010512 | 0.00074995 | -0.0061807 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0043375 | -0.00044008 | -13.9401 | 0.59662 | -13.9355 | 109.0819 | 108.9788 | 108.9433 | -13.8594 | -13.8496 | 0.16977 | -14.0397 | 108.8604 | 109.1035 | 108.5069 | -14.0151 | 0.079547 | 0.092903 | -0.00124 | 0.003365 | -0.076182 | -0.01019 | -0.045655 | -0.076167 | -0.12856 | 0.089354 | -0.10083 | -0.02466 | 0.11454 | -0.48206 | 123.0208 | 122.9177 | 122.8822 | 14.5355 | -122.8483 | 122.7993 | 123.0424 | 122.4458 | 14.1087 | -123.004
307.125 | 123.1567 | -11.3388 | 111.6119 | 0.0069442 | -0.0043526 | 0.00058972 | 0.00128 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0047649 | -0.00022648 | -11.3946 | 0.69735 | -11.3992 | 111.6091 | 111.4789 | 111.4524 | -11.3547 | -11.3129 | 0.18351 | -11.494 | 111.3603 | 111.6171 | 110.9198 | -11.515 | -0.015879 | -0.002812 | -0.055754 | -0.060365 | -0.044486 | -0.13308 | -0.15957 | -0.17623 | -0.25168 | 0.025862 | -0.15516 | 0.021069 | 0.005205 | -0.69212 | 122.9479 | 122.8177 | 122.7912 | 12.0362 | -122.9666 | 122.6991 | 122.9559 | 122.2586 | 11.5223 | -123.127
308.875 | 123.0606 | -12.3779 | 110.6277 | 0.022206 | -0.0043526 | 0.00037612 | 0.00063882 | -0.0010512 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0047649 | -0.00044008 | -12.6902 | 0.55084 | -12.6857 | 110.3226 | 110.2059 | 110.1749 | -12.6276 | -12.5996 | 0.17893 | -12.7897 | 110.0966 | 110.3534 | 109.7797 | -12.7788 | -0.2497 | -0.30515 | -0.31231 | -0.30774 | -0.058042 | -0.42183 | -0.4528 | -0.40086 | -0.53116 | -0.22163 | -0.41181 | -0.010953 | -0.2743 | -0.848 | 122.7005 | 122.5838 | 122.5529 | 12.9288 | -123.2554 | 122.4745 | 122.7314 | 122.1577 | 12.5569 | -123.4065
310.5469 | 123.1522 | -11.8607 | 111.0214 | -0.0083178 | -0.0043526 | 0.00058972 | 0.00128 | -0.00083764 | 0.00074995 | 0.0014498 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0045513 | -0.00022648 | -11.9989 | 0.45011 | -11.9898 | 111.0094 | 110.8928 | 110.8572 | -11.9545 | -11.9173 | 0.17435 | -12.0984 | 110.7696 | 111.0219 | 110.3154 | -12.0965 | -0.093867 | -0.012066 | -0.13825 | -0.12911 | -0.035246 | -0.12867 | -0.16427 | -0.23589 | -0.25179 | -0.056677 | -0.2377 | -0.001812 | 0.000502 | -0.70598 | 122.87 | 122.7534 | 122.7178 | 12.3108 | -122.9759 | 122.6303 | 122.8826 | 122.1761 | 12.035 | -123.118
312.2812 | 123.0743 | -1.0483 | 121.9574 | 0.0069442 | -0.0052072 | -0.00047868 | 0.023503 | -0.00083764 | -0.00010465 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0045513 | -0.00065368 | -1.0382 | 0.10214 | -1.0431 | 0.50539 | 0.49946 | 0.67308 | -1.1483 | -0.95132 | 0.2705 | -1.0545 | 121.6298 | 121.9053 | 121.185 | -1.2127 | -0.099983 | -121.452 | 0.010032 | 0.005178 | 0.10516 | -121.4579 | -121.2843 | -0.16442 | -0.32758 | 0.096955 | -0.006231 | 0.15819 | -0.052134 | -0.77235 | 1.5537 | 1.5477 | 1.7214 | 1.1504 | -123.1057 | 122.6781 | 122.9535 | 122.2333 | 1.3188 | -123.1701
314.0312 | 123.0423 | -1.0254 | 122.0398 | -0.00068679 | -0.0056346 | -0.00026488 | 0.022648 | -0.00083764 | 0.00032255 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0043375 | -0.00065368 | -0.92836 | 0.0884 | -0.9378 | 0.249 | 0.27052 | 0.40295 | -0.99716 | -0.83686 | 0.24303 | -0.94462 | 121.7855 | 122.0564 | 121.4506 | -1.112 | 0.028233 | -121.7908 | 0.097026 | 0.087591 | 0.059358 | -121.7693 | -121.6368 | -0.086573 | -0.25431 | 0.18853 | 0.08077 | 0.16734 | 0.016562 | -0.58919 | 1.2744 | 1.2959 | 1.4283 | 1.1138 | -123.037 | 122.8109 | 123.0817 | 122.476 | 1.2684 | -123.1518
315.7031 | 123.0469 | -1.0574 | 121.9666 | -0.015949 | -0.0049936 | 0.00016232 | 0.022648 | -0.00062384 | 0.00032255 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0045513 | -0.00065368 | -0.94668 | 0.0884 | -0.91949 | 0.22153 | 0.23846 | 0.38005 | -0.99258 | -0.86433 | 0.22929 | -0.96294 | 121.7489 | 122.0335 | 121.3316 | -1.1486 | 0.064855 | -121.745 | 0.11075 | 0.13795 | 0.073092 | -121.7281 | -121.5865 | -0.09116 | -0.21769 | 0.1931 | 0.094498 | 0.18566 | 0.066911 | -0.63499 | 1.279 | 1.2959 | 1.4375 | 1.1458 | -122.9591 | 122.8063 | 123.0909 | 122.389 | 1.2867 | -123.1151
317.4375 | 123.1522 | -0.98419 | 121.9849 | -0.00068679 | -0.0049936 | -0.00026488 | 0.022862 | -0.0010512 | 0.00032255 | 0.0014498 | 0.0011109 | 0.00081608 | 0.0002992 | 0.0045513 | -0.00065368 | -0.93752 | 0.079243 | -0.90575 | 0.16659 | 0.22473 | 0.36174 | -0.988 | -0.85059 | 0.23387 | -0.95836 | 121.7763 | 122.0426 | 121.3087 | -1.1303 | -0.003808 | -121.8183 | 0.04667 | 0.07844 | 0.082248 | -121.7601 | -121.6231 | -0.14609 | -0.20853 | 0.1336 | 0.025835 | 0.17192 | 0.057758 | -0.6762 | 1.1508 | 1.2089 | 1.3459 | 1.0634 | -122.9729 | 122.7605 | 123.0268 | 122.2929 | 1.2181 | -123.1151
319.1719 | 123.0698 | -1.181 | 121.8567 | 0.0069442 | -0.0054208 | -5.128e-05 | 0.022435 | -0.0010512 | 0.00010895 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0043375 | -0.00044008 | -1.0932 | 0.070086 | -1.0751 | 0.15743 | 0.20641 | 0.35258 | -1.1528 | -1.0154 | 0.22472 | -1.1232 | 121.6069 | 121.8869 | 121.2354 | -1.2814 | 0.028189 | -121.6993 | 0.087843 | 0.10588 | 0.077692 | -121.6503 | -121.5041 | -0.10035 | -0.24976 | 0.1656 | 0.05784 | 0.15819 | 0.030259 | -0.62128 | 1.3385 | 1.3874 | 1.5336 | 1.2511 | -123.0095 | 122.788 | 123.068 | 122.4164 | 1.4057 | -123.1381
320.9062 | 123.1613 | -1.3138 | 121.6736 | -0.00068679 | -0.0052072 | -0.00026488 | 0.022648 | -0.0012648 | 0.00074995 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00065368 | -1.2351 | 0.065507 | -1.2217 | 0.16201 | 0.21557 | 0.348 | -1.2811 | -1.1253 | 0.19267 | -1.2606 | 121.4604 | 121.7359 | 121.034 | -1.4279 | 0.032731 | -121.5116 | 0.078665 | 0.092128 | 0.059397 | -121.458 | -121.3256 | -0.11412 | -0.21317 | 0.18847 | 0.05323 | 0.16735 | 0.06227 | -0.63963 | 1.4758 | 1.5293 | 1.6618 | 1.3793 | -122.9546 | 122.7742 | 123.0496 | 122.3477 | 1.5064 | -123.1015
322.6406 | 123.0286 | -1.5335 | 121.5179 | -0.0083178 | -0.0049936 | -5.128e-05 | 0.022648 | -0.00083764 | 0.00053635 | 0.0090803 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0049787 | -0.00065368 | -1.4503 | 0.070086 | -1.4231 | 0.16659 | 0.11483 | 0.36632 | -1.4963 | -1.3268 | 0.19267 | -1.4712 | 121.259 | 121.5344 | 120.8004 | -1.6339 | 0.037247 | -121.3514 | 0.083207 | 0.11041 | 0.073163 | -121.4031 | -121.1516 | -0.10044 | -0.25898 | 0.20673 | 0.062336 | 0.16278 | 0.016452 | -0.7175 | 1.7001 | 1.6483 | 1.8998 | 1.6036 | -123.0142 | 122.7925 | 123.0679 | 122.334 | 1.7262 | -123.1519
324.3125 | 123.0652 | -2.8702 | 120.1584 | 0.0069442 | -0.0052072 | -0.00026488 | 0.022648 | -0.0010512 | 0.00074995 | -0.0061807 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0045513 | -0.00065368 | -2.8009 | 0.05635 | -2.7783 | 0.14827 | 0.096516 | 0.33885 | -2.847 | -2.6821 | 0.17893 | -2.8356 | 119.9037 | 120.1746 | 119.5688 | -2.9847 | 0.023135 | -120.0101 | 0.069252 | 0.091909 | 0.068774 | -120.0619 | -119.8195 | -0.11452 | -0.25466 | 0.1881 | 0.03455 | 0.14907 | 0.016165 | -0.58959 | 3.0185 | 2.9667 | 3.209 | 2.9265 | -123.0054 | 122.7739 | 123.0447 | 122.439 | 3.0491 | -123.1431
326.0469 | 123.0743 | -3.2135 | 119.7922 | -0.00068679 | -0.0049936 | -0.00026488 | 0.022862 | -0.00083764 | 0.00032255 | 0.0014498 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0047649 | -0.00065368 | -3.1535 | 0.05635 | -3.1537 | 0.13912 | 0.1011 | 0.32969 | -3.2088 | -3.0346 | 0.17435 | -3.1928 | 119.5466 | 119.8174 | 119.1705 | -3.3418 | 0.004723 | -119.6531 | 0.060039 | 0.059813 | 0.05509 | -119.6911 | -119.4625 | -0.12835 | -0.24557 | 0.17886 | 0.020734 | 0.14908 | 0.025245 | -0.62171 | 3.3526 | 3.3146 | 3.5432 | 3.2699 | -123.001 | 122.7601 | 123.0309 | 122.384 | 3.3879 | -123.134
327.7188 | 123.024 | -6.3766 | 116.6382 | -0.0083178 | -0.0049936 | -0.00026488 | 0.022648 | -0.00083764 | 0.00053635 | 0.0014498 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0043375 | -0.00065368 | -6.2668 | 0.047193 | -6.2715 | 0.12538 | 0.08278 | 0.31137 | -6.2812 | -6.1665 | 0.16977 | -6.3338 | 116.4515 | 116.7131 | 116.0112 | -6.428 | 0.095411 | -116.5128 | 0.10988 | 0.10515 | 0.00974 | -116.5554 | -116.3268 | -0.051323 | -0.18664 | 0.21017 | 0.042886 | 0.094209 | 0.074943 | -0.62696 | 6.502 | 6.4594 | 6.688 | 6.4238 | -122.9194 | 122.8282 | 123.0898 | 122.3879 | 6.5464 | -123.0662
329.4688 | 123.0286 | -4.8981 | 118.1259 | -0.0083178 | -0.0054208 | -0.00026488 | 0.022648 | -0.00083764 | 0.00074995 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0045513 | -0.00065368 | -4.8017 | 0.047193 | -4.7973 | 0.12538 | 0.087359 | 0.31595 | -4.8389 | -4.6921 | 0.17893 | -4.8548 | 117.9029 | 118.1691 | 117.5817 | -4.9765 | 0.059195 | -118.0005 | 0.09639 | 0.10078 | 0.041585 | -118.0386 | -117.81 | -0.078415 | -0.22299 | 0.20594 | 0.043232 | 0.12165 | 0.043207 | -0.54423 | 5.0235 | 4.9854 | 5.214 | 4.9453 | -122.9648 | 122.801 | 123.0672 | 122.4798 | 5.077 | -123.1024
331.1406 | 123.1567 | -4.8981 | 118.0527 | 0.0069442 | -0.0052072 | -0.00026488 | 0.022648 | -0.0010512 | 0.00053635 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0047649 | -0.00086748 | -4.7879 | 0.042614 | -4.7836 | 0.14369 | 0.096516 | 0.32969 | -4.816 | -4.6738 | 0.17435 | -4.8457 | 117.9121 | 118.1874 | 117.4489 | -4.9673 | 0.08209 | -117.909 | 0.11013 | 0.11451 | 0.032425 | -117.9562 | -117.723 | -0.069257 | -0.14059 | 0.22426 | 0.052389 | 0.12165 | 0.13476 | -0.60377 | 5.0418 | 4.9946 | 5.2278 | 4.9407 | -122.8687 | 122.8102 | 123.0855 | 122.347 | 5.0724 | -123.02
332.875 | 123.0789 | -4.3259 | 118.6981 | 0.014575 | -0.0052072 | -5.128e-05 | 0.022648 | -0.00062384 | 0.00053635 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0045513 | -0.00086748 | -4.2752 | 0.042614 | -4.2525 | 0.17574 | 0.11941 | 0.36174 | -4.3123 | -4.1656 | 0.17893 | -4.3329 | 118.4203 | 118.7002 | 117.9846 | -4.4591 | 0.013568 | -118.5224 | 0.0507 | 0.073392 | 0.059824 | -118.5787 | -118.3364 | -0.13321 | -0.27783 | 0.16029 | -0.006999 | 0.12621 | 0.002121 | -0.71352 | 4.5016 | 4.4453 | 4.6876 | 4.3685 | -123.0104 | 122.7462 | 123.0261 | 122.3105 | 4.5048 | -123.1572
334.625 | 123.1476 | -6.2256 | 116.7252 | -0.00068679 | -0.0054208 | -0.00026488 | 0.022648 | -0.0010512 | 0.00032255 | -0.0061807 | 0.00089729 | 0.0010299 | 0.0002992 | 0.0047649 | -0.00065368 | -6.2393 | 0.033457 | -6.212 | 0.14827 | 0.091937 | 0.32511 | -6.2492 | -6.1298 | 0.16519 | -6.3017 | 116.4744 | 116.7406 | 116.0799 | -6.3868 | -0.023598 | -116.5769 | -0.013709 | 0.013606 | 0.037204 | -116.6332 | -116.4 | -0.16118 | -0.25073 | 0.095741 | -0.076125 | 0.08505 | 0.01544 | -0.64526 | 6.3739 | 6.3175 | 6.5507 | 6.259 | -122.9743 | 122.7 | 122.9662 | 122.3055 | 6.3908 | -123.1119
336.2969 | 123.111 | -6.0654 | 116.8625 | -0.00068679 | -0.0049936 | -5.128e-05 | 0.022648 | -0.00083764 | 0.00032255 | 0.0014498 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0041239 | -0.00065368 | -6.0607 | 0.028878 | -6.0151 | 0.12538 | 0.03699 | 0.31595 | -6.0843 | -5.9559 | 0.17435 | -6.1323 | 116.6438 | 116.91 | 116.2218 | -6.2311 | -0.018974 | -116.7371 | 0.004631 | 0.050256 | 0.06923 | -116.8255 | -116.5465 | -0.16571 | -0.21865 | 0.10951 | -0.06693 | 0.098783 | 0.047519 | -0.64065 | 6.1908 | 6.1024 | 6.3813 | 6.0942 | -122.9468 | 122.7092 | 122.9754 | 122.2872 | 6.2397 | -123.0936
338.0312 | 123.0743 | -8.2581 | 114.7293 | -0.00068679 | -0.0054208 | -0.00047868 | 0.022862 | -0.0012648 | 0.00074995 | -0.0061807 | 0.00025649 | 0.00081608 | 0.0002992 | 0.0045513 | -0.00044008 | -8.1439 | 0.028878 | -8.0662 | 0.11622 | 0.078201 | 0.29764 | -8.1357 | -8.0437 | 0.15604 | -8.2202 | 114.5973 | 114.8542 | 114.3263 | -8.2687 | 0.12236 | -114.6131 | 0.11415 | 0.19187 | 0.069518 | -114.6511 | -114.4317 | -0.010598 | -0.13206 | 0.21431 | 0.037866 | 0.048464 | 0.12491 | -0.40301 | 8.3743 | 8.3363 | 8.5557 | 8.2869 | -122.865 | 122.8553 | 123.1123 | 122.5844 | 8.4141 | -122.998
339.7188 | 123.1567 | -5.3787 | 117.6041 | -0.00068679 | -0.0052072 | -5.128e-05 | 0.023076 | -0.0012648 | 0.00032255 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0047649 | -0.00044008 | -5.2778 | 0.019721 | -5.2093 | 0.14827 | 0.091937 | 0.32969 | -5.2968 | -5.1683 | 0.18351 | -5.3356 | 117.4313 | 117.6975 | 116.9819 | -5.4573 | 0.081955 | -117.4558 | 0.10089 | 0.16939 | 0.087432 | -117.5121 | -117.2744 | -0.078538 | -0.17272 | 0.21041 | 0.043119 | 0.12166 | 0.093462 | -0.62218 | 5.527 | 5.4707 | 5.7084 | 5.3984 | -122.9008 | 122.8101 | 123.0763 | 122.3606 | 5.5622 | -123.0613
341.4531 | 123.0286 | -6.8253 | 116.1942 | 0.0069442 | -0.0052072 | -0.00069228 | 0.022648 | -0.00062384 | 0.00053635 | 0.016711 | 0.00068369 | 0.0014571 | 0.0005128 | 0.0045513 | -0.00065368 | -6.6834 | 0.005985 | -6.6011 | 0.079598 | -0.068325 | 0.24727 | -6.6888 | -6.5694 | 0.17435 | -6.7367 | 116.0486 | 116.3011 | 115.5946 | -6.8263 | 0.1365 | -116.1146 | 0.14186 | 0.22412 | 0.087628 | -116.2625 | -115.9469 | -0.001072 | -0.14552 | 0.25586 | 0.088567 | 0.089639 | 0.1069 | -0.59958 | 6.9049 | 6.7569 | 7.0725 | 6.8312 | -122.8829 | 122.8739 | 123.1263 | 122.4198 | 6.9996 | -123.0205
343.1875 | 122.9187 | -55.394 | 67.4515 | -0.00068679 | -0.0049936 | -5.128e-05 | 0.022862 | -0.00041024 | 0.0018184 | 0.016711 | 4.2686e-05 | 0.00081608 | -0.0003418 | 0.0049787 | -0.00086748 | -54.3398 | -0.062694 | -53.4003 | 0.088755 | -0.00422 | 0.27017 | -54.479 | -54.3666 | -0.21026 | -54.5109 | 68.2858 | 68.5462 | 68.3388 | -54.588 | 0.91499 | -67.3627 | 1.0541 | 1.9937 | 1.0787 | -67.4557 | -67.1813 | 0.80601 | 0.83429 | 1.0274 | 0.88303 | 0.077023 | 1.0948 | 0.88734 | 55.4827 | 55.3898 | 55.6641 | 55.3313 | -121.9305 | 123.6798 | 123.9402 | 123.7328 | 55.1837 | -122.0394
344.9375 | 122.9462 | -55.5679 | 67.3096 | -0.00068679 | -0.0052072 | -0.00047868 | 0.022862 | -0.00019664 | 0.0011774 | -0.0061807 | 4.2686e-05 | 0.00038888 | -0.0001282 | 0.0047649 | -0.00044008 | -55.5256 | -0.071851 | -54.6227 | 0.088755 | -0.017957 | 0.22896 | -55.6512 | -55.5021 | -0.040849 | -55.6602 | 67.0862 | 67.278 | 66.8187 | -55.7418 | -0.083269 | -67.2208 | 0.042292 | 0.94521 | 1.0285 | -67.3275 | -67.0806 | -0.1739 | -0.22336 | 0.065859 | -0.092272 | 0.081628 | -0.031614 | -0.49085 | 55.6567 | 55.55 | 55.7969 | 55.4961 | -122.9608 | 122.6541 | 122.8459 | 122.3867 | 55.5271 | -123.0514
346.6719 | 123.024 | -55.2109 | 67.6117 | 0.0069442 | -0.0052072 | -5.128e-05 | 0.022862 | -0.00019664 | 0.0016046 | 0.0090803 | 4.2686e-05 | 0.00038888 | -0.0003418 | 0.0049787 | -0.00044008 | -55.1777 | -0.07643 | -54.229 | 0.093333 | 0.014096 | 0.22896 | -55.3169 | -55.177 | 0.000359 | -55.3305 | 67.4113 | 67.6168 | 67.2995 | -55.3984 | -0.10606 | -67.5184 | 0.033193 | 0.98189 | 1.088 | -67.5976 | -67.3827 | -0.18755 | -0.20041 | 0.033891 | -0.11966 | 0.067885 | 0.005079 | -0.31222 | 55.3042 | 55.225 | 55.4398 | 55.1344 | -122.9286 | 122.6222 | 122.8276 | 122.5103 | 55.2112 | -123.0101
348.4062 | 123.1018 | -55.9845 | 66.7969 | -0.00068679 | -0.0054208 | 0.00016232 | 0.022435 | -0.00019664 | 0.001391 | 0.0014498 | 4.2686e-05 | 0.00060248 | -0.0001282 | 0.0047649 | -0.00022648 | -55.9469 | -0.071851 | -55.1721 | 0.093333 | 0.004938 | 0.23354 | -56.0084 | -55.9554 | 0.004938 | -56.1043 | 66.6421 | 66.843 | 66.4387 | -56.186 | -0.02386 | -66.7035 | 0.037645 | 0.81238 | 0.83624 | -66.7919 | -66.5633 | -0.20148 | -0.15478 | 0.029131 | -0.11984 | 0.081639 | 0.046114 | -0.35818 | 56.0778 | 55.9894 | 56.218 | 55.9126 | -122.8052 | 122.6266 | 122.8275 | 122.4232 | 55.9894 | -122.9829
350.1406 | 122.9782 | -56.5201 | 66.362 | -0.00068679 | -0.0054208 | -5.128e-05 | 0.023289 | -0.00019664 | 0.0018184 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0001282 | 0.0047649 | -1.2882e-05 | -56.4001 | -0.053537 | -55.7764 | 0.088755 | -0.013378 | 0.22438 | -56.4891 | -56.4361 | 0.018674 | -56.5943 | 66.1614 | 66.3668 | 65.9259 | -56.6668 | 0.030937 | -66.2732 | 0.11997 | 0.74364 | 0.7127 | -66.3754 | -66.1376 | -0.14667 | -0.20065 | 0.083951 | -0.074179 | 0.072493 | 0.004814 | -0.43611 | 56.6088 | 56.5067 | 56.7445 | 56.4665 | -122.8511 | 122.6814 | 122.8869 | 122.446 | 56.5388 | -123.0288
351.8125 | 123.024 | -55.2063 | 67.6575 | 0.0069442 | -0.0056346 | -0.00026488 | 0.022862 | -0.00019664 | 0.0016046 | 0.0090803 | 4.2686e-05 | 0.00038888 | 8.5404e-05 | 0.0045513 | -0.00022648 | -55.1411 | -0.094744 | -54.2565 | 0.07502 | -0.059167 | 0.21522 | -55.2345 | -55.1861 | 0.036989 | -55.3351 | 67.4204 | 67.6214 | 67.1346 | -55.4076 | -0.02822 | -67.5825 | 0.065243 | 0.94984 | 0.97806 | -67.7166 | -67.4422 | -0.20128 | -0.23703 | 0.020157 | -0.12882 | 0.072463 | -0.03612 | -0.52283 | 55.2813 | 55.1471 | 55.4215 | 55.1116 | -122.892 | 122.6267 | 122.8277 | 122.3409 | 55.2433 | -123.065
353.5469 | 123.1064 | -54.6204 | 68.2068 | -0.0083178 | -0.0052072 | -0.00047868 | 0.022862 | -0.00019664 | 0.0018184 | 0.0090803 | 4.2686e-05 | 0.0012435 | 0.0002992 | 0.0047649 | 0.00020092 | -54.5001 | -0.12222 | -53.5056 | 0.056706 | -0.086641 | 0.19233 | -54.6026 | -54.5543 | 0.041567 | -54.7216 | 68.0523 | 68.2532 | 67.6658 | -54.7849 | 0.017734 | -68.1501 | 0.12028 | 1.1147 | 1.097 | -68.2934 | -68.0145 | -0.1645 | -0.15452 | 0.066081 | -0.10121 | 0.063291 | 0.046411 | -0.54103 | 54.6771 | 54.5337 | 54.8127 | 54.4981 | -122.8094 | 122.6726 | 122.8736 | 122.2861 | 54.6619 | -122.9916
355.2188 | 123.1201 | -52.9861 | 69.8273 | 0.0069442 | -0.0054208 | -5.128e-05 | 0.023076 | -0.00041024 | 0.0022456 | 0.0090803 | 0.00025649 | 0.00060248 | 8.5404e-05 | 0.0043375 | -1.2882e-05 | -53.1952 | -0.12222 | -51.8986 | 0.047549 | -0.086641 | 0.17402 | -53.2839 | -53.2448 | 0.073618 | -53.4029 | 69.3709 | 69.5718 | 69.0577 | -53.4662 | -0.29775 | -69.7797 | -0.2091 | 1.0875 | 1.3853 | -69.9139 | -69.6533 | -0.48002 | -0.4564 | -0.25862 | -0.41676 | 0.06326 | -0.25543 | -0.76962 | 53.0337 | 52.8995 | 53.1602 | 52.8639 | -123.1112 | 122.357 | 122.558 | 122.0438 | 53.0598 | -123.2934
356.9531 | 123.0652 | -51.3931 | 71.4294 | -0.00068679 | -0.0052072 | -0.00026488 | 0.022648 | 0.00044436 | 0.002032 | 0.0014498 | 0.00025649 | 0.00081608 | -0.0003418 | 0.0047649 | -1.2882e-05 | -51.5653 | -0.11764 | -49.9346 | 0.024657 | -0.082062 | 0.16028 | -51.6584 | -51.6285 | 0.06904 | -51.7775 | 71.0008 | 71.2064 | 70.7105 | -51.8361 | -0.26525 | -71.4048 | -0.17221 | 1.4586 | 1.7238 | -71.5115 | -71.2692 | -0.44297 | -0.42862 | -0.23536 | -0.38433 | 0.058643 | -0.22305 | -0.71891 | 51.4178 | 51.3111 | 51.5534 | 51.2755 | -123.0878 | 122.3939 | 122.5995 | 122.1037 | 51.4622 | -123.2655
358.6875 | 123.1064 | -48.4543 | 74.35 | -0.0083178 | -0.0052072 | -0.00026488 | 0.023076 | 0.0010854 | 0.002673 | -0.0061807 | 0.00047009 | 0.00060248 | -0.0003418 | 0.0047649 | -0.00044008 | -49.0335 | -0.11306 | -46.8305 | -0.002813 | -0.068325 | 0.13281 | -49.1033 | -49.0781 | 0.10109 | -49.2363 | 73.5648 | 73.7658 | 73.2562 | -49.2765 | -0.64905 | -74.3528 | -0.5792 | 1.6238 | 2.2729 | -74.4183 | -74.2172 | -0.82226 | -0.7852 | -0.62386 | -0.78199 | 0.040268 | -0.58414 | -1.0937 | 48.4515 | 48.386 | 48.5871 | 48.3412 | -123.4533 | 122.0191 | 122.2201 | 121.7105 | 48.5554 | -123.6265
360.3594 | 122.9782 | -47.9233 | 74.9954 | 0.0069442 | -0.0052072 | -5.128e-05 | 0.022435 | 0.0012992 | 0.0028866 | 0.0014498 | 0.00047009 | 0.00060248 | -0.0003418 | 0.0049787 | -0.00022648 | -47.9438 | -0.12222 | -45.4982 | -0.01197 | -0.063746 | 0.11907 | -48.0044 | -47.9976 | 0.096512 | -48.1557 | 74.6499 | 74.8647 | 74.3414 | -48.1868 | -0.081118 | -75.0074 | -0.020551 | 2.4251 | 2.5062 | -75.0592 | -74.8763 | -0.26351 | -0.34554 | -0.074289 | -0.23242 | 0.031086 | -0.13072 | -0.65406 | 47.9113 | 47.8595 | 48.0424 | 47.8011 | -122.9998 | 122.5732 | 122.788 | 122.2646 | 48.0198 | -123.1822
362.0938 | 122.9965 | -44.7372 | 78.1448 | 0.0069442 | -0.0054208 | -5.128e-05 | 0.022648 | 0.0015128 | 0.002673 | 0.0090803 | 0.00025649 | 0.00017528 | -0.0001282 | 0.0047649 | -0.00044008 | -44.7206 | -0.12679 | -41.5884 | -0.025705 | -0.063746 | 0.10534 | -44.7763 | -44.7833 | 0.11025 | -44.9506 | 77.8869 | 78.0972 | 77.7341 | -44.9587 | -0.039011 | -78.1705 | 0.016599 | 3.1489 | 3.1879 | -78.2086 | -78.0395 | -0.22147 | -0.25796 | -0.046069 | -0.21336 | 0.008116 | -0.047642 | -0.41073 | 44.7115 | 44.6735 | 44.8426 | 44.6105 | -122.9211 | 122.6241 | 122.8344 | 122.4714 | 44.8475 | -123.1036
363.8281 | 123.0743 | -39.4501 | 83.4412 | -0.00068679 | -0.0052072 | -5.128e-05 | 0.022435 | 0.0023674 | 0.003314 | 0.0014498 | 0.00025649 | 0.00060248 | 0.0002992 | 0.0049787 | -1.2882e-05 | -40.9755 | -0.14511 | -36.9963 | -0.098959 | -0.031693 | -0.054914 | -41.0124 | -41.0242 | 0.12856 | -41.1823 | 81.6687 | 81.8837 | 81.3512 | -41.172 | -1.5623 | -83.5401 | -1.5255 | 2.4537 | 4.016 | -83.4729 | -83.4961 | -1.722 | -1.7724 | -1.5741 | -1.7322 | -0.010287 | -1.5575 | -2.09 | 39.3511 | 39.4184 | 39.3952 | 39.305 | -124.4535 | 121.1188 | 121.3338 | 120.8013 | 39.5786 | -124.6132
365.5781 | 123.111 | -37.8387 | 85.0067 | -0.00068679 | -0.0056346 | 0.0010171 | 0.022007 | 0.0027948 | 0.003955 | -0.0061807 | 0.00025649 | 0.00081608 | 8.5404e-05 | 0.0049787 | -0.00065368 | -38.9702 | -0.17258 | -34.5698 | -0.18137 | -0.022536 | -0.0366 | -38.9839 | -39.0141 | 0.15146 | -39.1814 | 83.6833 | 83.8983 | 83.3978 | -39.1482 | -1.1452 | -85.1881 | -1.1314 | 3.2689 | 4.4141 | -85.0293 | -85.0433 | -1.3095 | -1.3235 | -1.1754 | -1.3427 | -0.033229 | -1.1084 | -1.6089 | 37.6574 | 37.8162 | 37.8021 | 37.6662 | -123.9906 | 121.522 | 121.737 | 121.2366 | 37.9902 | -124.1549
367.25 | 123.0606 | -36.8134 | 86.0229 | -0.00068679 | -0.0062756 | 0.0020855 | 0.021794 | 0.003222 | 0.0037412 | -0.0061807 | 0.00068369 | 0.00060248 | 8.5404e-05 | 0.0047649 | -0.00044008 | -35.3716 | -0.17716 | -30.1976 | -0.41945 | -0.32932 | -0.26095 | -35.3849 | -35.4382 | 0.091933 | -35.61 | 87.2865 | 87.52 | 86.96 | -35.563 | 1.4285 | -86.4424 | 1.4418 | 6.6158 | 5.1873 | -86.3523 | -86.2839 | 1.2504 | 1.2636 | 1.3752 | 1.2033 | -0.047049 | 1.497 | 0.93704 | 36.3939 | 36.484 | 36.5524 | 36.6362 | -121.4078 | 124.0999 | 124.3333 | 123.7733 | 36.9053 | -121.5859
368.9844 | 123.0194 | -32.3181 | 90.596 | -0.00068679 | -0.007344 | 0.0035813 | 0.020725 | 0.0036494 | 0.0041686 | 0.0014498 | 0.00025649 | 0.0010299 | -0.0003418 | 0.0047649 | -0.00044008 | -31.3746 | -0.16342 | -25.3126 | -0.74451 | -0.62695 | -0.60435 | -31.3646 | -31.4318 | 0.1194 | -31.5991 | 91.3064 | 91.5445 | 90.9022 | -31.5336 | 0.95353 | -91.3405 | 0.94347 | 7.0055 | 6.052 | -91.223 | -91.2004 | 0.78449 | 0.71044 | 0.88632 | 0.71903 | -0.065458 | 0.94854 | 0.30616 | 31.5736 | 31.6912 | 31.7138 | 32.1547 | -121.9606 | 123.6246 | 123.8627 | 123.2203 | 32.4375 | -122.1296
370.7344 | 123.0469 | -26.976 | 95.929 | -0.00068679 | -0.008626 | 0.0061453 | 0.019657 | 0.0042904 | 0.005237 | 0.0014498 | 0.00025649 | 0.0010299 | -0.0001282 | 0.0045513 | -0.00044008 | -27.3548 | -0.15884 | -20.3818 | -1.2252 | -1.1123 | -1.0668 | -27.326 | -27.3842 | 0.18809 | -27.5744 | 95.3493 | 95.5783 | 94.9359 | -27.4814 | -0.34996 | -97.1542 | -0.37881 | 6.5943 | 6.9442 | -97.0413 | -96.9957 | -0.50536 | -0.5797 | -0.4082 | -0.59838 | -0.093025 | -0.35066 | -0.99304 | 25.7508 | 25.8637 | 25.9092 | 26.8172 | -123.2549 | 122.3253 | 122.5543 | 121.9119 | 27.1641 | -123.4103
372.4062 | 123.1018 | -24.5636 | 98.2727 | -0.00068679 | -0.0090534 | 0.0072137 | 0.019016 | 0.005145 | 0.005237 | -0.0061807 | 4.2686e-05 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.00044008 | -24.3834 | -0.14511 | -16.7466 | -1.4084 | -1.2909 | -1.2545 | -24.3588 | -24.4309 | 0.16977 | -24.612 | 98.3161 | 98.5635 | 97.8937 | -24.528 | 0.20477 | -99.6811 | 0.18015 | 7.817 | 7.6122 | -99.5636 | -99.5272 | 0.035564 | 0.043417 | 0.13265 | -0.048373 | -0.083937 | 0.29084 | -0.37901 | 23.1552 | 23.2727 | 23.3091 | 24.4185 | -122.6315 | 122.8797 | 123.1271 | 122.4573 | 24.7334 | -122.8007
374.1562 | 122.9874 | -23.8083 | 99.1516 | 0.0069442 | -0.0090534 | 0.0074275 | 0.018802 | 0.0049314 | 0.005237 | -0.0061807 | 0.00047009 | 0.00060248 | 0.0002992 | 0.0049787 | -0.00044008 | -23.5364 | -0.18632 | -15.7256 | -1.5091 | -1.4008 | -1.3598 | -23.4888 | -23.5702 | 0.15146 | -23.742 | 99.1723 | 99.4289 | 98.9376 | -23.6581 | 0.31945 | -100.6607 | 0.27184 | 8.0826 | 7.7632 | -100.5524 | -100.5114 | 0.15023 | 0.02069 | 0.23814 | 0.066272 | -0.083957 | 0.27729 | -0.214 | 22.2992 | 22.4075 | 22.4485 | 23.622 | -122.6404 | 122.9806 | 123.2372 | 122.7459 | 23.9597 | -122.8097
375.8906 | 123.1201 | -26.976 | 95.8511 | -0.00068679 | -0.0060618 | 0.0016581 | 0.02158 | 0.004504 | 0.005237 | -0.0061807 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0049787 | -0.00044008 | -27.2312 | -0.54345 | -20.3863 | -0.78114 | -0.67274 | -0.63182 | -27.2207 | -27.2972 | 0.16061 | -27.4737 | 95.4408 | 95.6836 | 95.1648 | -27.3852 | -0.24465 | -96.6323 | -0.25519 | 6.5897 | 6.8343 | -96.5239 | -96.483 | -0.4092 | -0.41031 | -0.32121 | -0.49765 | -0.088449 | -0.16753 | -0.68629 | 26.1949 | 26.3033 | 26.3442 | 26.4326 | -123.0718 | 122.4168 | 122.6596 | 122.1409 | 27.1366 | -123.2364
377.625 | 123.0148 | -25.0351 | 97.9019 | -0.00068679 | -0.0060618 | 0.0014445 | 0.02158 | 0.0049314 | 0.0050232 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00044008 | -25.1114 | -0.47477 | -17.8958 | -1.1062 | -0.99785 | -0.96606 | -25.1647 | -25.2231 | 0.15604 | -25.3995 | 97.5195 | 97.7669 | 97.2802 | -25.3156 | -0.12963 | -99.0081 | -0.076315 | 7.1393 | 7.269 | -98.8998 | -98.868 | -0.2805 | -0.38245 | -0.18797 | -0.36442 | -0.083918 | -0.13505 | -0.62176 | 23.9289 | 24.0372 | 24.069 | 24.5603 | -123.0666 | 122.5546 | 122.802 | 122.3153 | 25.1911 | -123.2175
379.2969 | 122.9919 | -22.9019 | 100.0534 | -0.00068679 | -0.0064892 | 0.0014445 | 0.022007 | 0.0049314 | 0.005237 | 0.0014498 | 0.00025649 | 0.00081608 | 0.0002992 | 0.0045513 | -0.00044008 | -23.0557 | -0.49308 | -15.515 | -1.184 | -1.0757 | -1.0302 | -23.1637 | -23.2176 | 0.17893 | -23.3986 | 99.5157 | 99.7631 | 99.1803 | -23.3238 | -0.26181 | -101.2374 | -0.1538 | 7.3869 | 7.6487 | -101.1291 | -101.0836 | -0.42189 | -0.53772 | -0.31567 | -0.4967 | -0.074808 | -0.29026 | -0.87313 | 21.7179 | 21.8262 | 21.8718 | 22.4088 | -123.2171 | 122.4176 | 122.6651 | 122.0822 | 23.0808 | -123.3772
381.0312 | 123.0698 | -21.08 | 101.8204 | -0.00068679 | -0.0060618 | 0.0014445 | 0.021794 | 0.0053588 | 0.0056642 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0047649 | -0.00044008 | -21.1511 | -0.54803 | -13.3358 | -1.1932 | -1.0894 | -1.0485 | -21.3047 | -21.3678 | 0.17893 | -21.558 | 101.3654 | 101.6129 | 100.9202 | -21.474 | -0.22467 | -103.0136 | -0.071087 | 7.7442 | 7.9689 | -102.9098 | -102.8688 | -0.39395 | -0.45497 | -0.28777 | -0.47796 | -0.084009 | -0.20748 | -0.90022 | 19.8868 | 19.9906 | 20.0315 | 20.532 | -123.1251 | 122.4454 | 122.6929 | 122.0002 | 21.2589 | -123.2943
382.7031 | 123.0606 | -18.6859 | 104.2419 | -0.00068679 | -0.0062756 | 0.0012307 | 0.021794 | 0.0055724 | 0.005878 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0043375 | -0.00044008 | -18.6101 | -0.57092 | -10.4652 | -1.3168 | -1.1993 | -1.1675 | -18.9008 | -18.9594 | 0.17893 | -19.1404 | 103.7783 | 104.035 | 103.3422 | -19.0655 | -0.21484 | -105.5588 | 0.075814 | 8.2207 | 8.4356 | -105.4413 | -105.4095 | -0.37959 | -0.46368 | -0.27348 | -0.4545 | -0.074908 | -0.20697 | -0.89971 | 17.3691 | 17.4866 | 17.5184 | 18.115 | -123.1427 | 122.4642 | 122.7209 | 122.0281 | 18.8648 | -123.3074
384.4375 | 123.0972 | -17.1066 | 105.8121 | -0.00068679 | -0.0062756 | 0.0018717 | 0.021366 | 0.005786 | 0.0060916 | 0.0014498 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0047649 | -0.00044008 | -15.538 | 0.19829 | -8.0891 | -1.3534 | -1.2451 | -1.2087 | -17.2569 | -16.8944 | 0.30255 | -17.2448 | 105.4219 | 105.665 | 104.9493 | -17.4126 | -0.15029 | -107.1655 | 1.5686 | 9.0176 | 9.1678 | -107.0572 | -107.0208 | -0.30592 | -0.39013 | 0.21224 | -0.1382 | 0.16773 | -0.14711 | -0.86275 | 15.7532 | 15.8615 | 15.8979 | 17.3049 | -123.069 | 122.5286 | 122.7716 | 122.0559 | 17.4092 | -123.2246
386.1094 | 128.1097 | -15.239 | 107.6843 | 0.0069442 | -0.007344 | 0.0042223 | 0.020511 | 0.0055724 | 0.006519 | 0.0090803 | 0.00025649 | 0.00060248 | 0.0002992 | 0.0045513 | -0.00065368 | -13.1435 | 1.1598 | -5.4795 | -1.4633 | -1.3687 | -1.3323 | -15.3017 | -14.0647 | 2.1157 | -13.4262 | 107.3861 | 107.5468 | 106.9319 | -15.4528 | -0.062765 | -109.1476 | 2.0954 | 9.7595 | 9.8223 | -109.0531 | -109.0167 | -0.21387 | -0.2982 | 1.1742 | 1.8128 | 2.0266 | -0.13756 | -0.75247 | 13.7756 | 13.8702 | 13.9066 | 16.3987 | -122.986 | 122.6251 | 122.7857 | 122.1708 | 17.3547 | -123.1371
387.8438 | 123.1293 | -14.1678 | 108.7143 | -0.00068679 | -0.007344 | 0.0042223 | 0.020084 | 0.0059996 | 0.0071598 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0047649 | -1.2882e-05 | -13.2168 | -0.88684 | -5.3284 | -1.3946 | -1.2863 | -1.2454 | -14.1707 | -14.1655 | 0.17435 | -14.3557 | 108.5262 | 108.7876 | 108.1452 | -14.3264 | -0.002938 | -110.1089 | 0.95103 | 8.8394 | 8.8424 | -110.0006 | -109.9596 | -0.15864 | -0.18813 | 0.002305 | -0.18788 | -0.029232 | 0.073273 | -0.56911 | 12.7731 | 12.8815 | 12.9224 | 13.2809 | -122.885 | 122.694 | 122.9554 | 122.313 | 14.3421 | -123.0407
389.5938 | 123.0423 | -11.8652 | 111.0535 | -0.0083178 | -0.007985 | 0.0048633 | 0.019657 | 0.005145 | 0.0084418 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.00044008 | -8.3637 | -1.1204 | -3.8404 | -1.4267 | -1.3138 | -1.282 | -11.9362 | -11.899 | 0.18351 | -12.0846 | 110.7605 | 111.0357 | 110.4894 | -12.0874 | -0.070975 | -112.4802 | 3.5016 | 8.0248 | 8.0958 | -112.3673 | -112.3354 | -0.22216 | -0.293 | -0.033785 | -0.21939 | 0.002767 | -0.017807 | -0.56404 | 10.4385 | 10.5514 | 10.5833 | 10.7449 | -122.9897 | 122.6257 | 122.9009 | 122.3547 | 12.0487 | -123.1409
391.2656 | 123.0148 | -10.9314 | 112.0468 | -0.00068679 | -0.0081986 | 0.0050769 | 0.01987 | 0.0049314 | 0.0088692 | 0.0090803 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0049787 | -0.00065368 | -6.8391 | -1.3584 | -3.2773 | -1.358 | -1.2497 | -1.2041 | -10.9288 | -10.8825 | 0.18351 | -11.0727 | 111.7677 | 112.043 | 111.3731 | -11.0846 | 0.002551 | -113.4048 | 4.0923 | 7.6541 | 7.6515 | -113.2965 | -113.251 | -0.15323 | -0.27907 | 0.04885 | -0.14133 | 0.011901 | -0.003861 | -0.67371 | 9.5734 | 9.6817 | 9.7273 | 9.573 | -122.9757 | 122.6991 | 122.9743 | 122.3045 | 11.1149 | -123.1314
393 | 123.0743 | -9.3704 | 113.5391 | -0.00068679 | -0.0081986 | 0.0046497 | 0.01987 | 0.0040768 | 0.0099376 | -0.013811 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0047649 | -0.00065368 | -5.4793 | -1.6194 | -2.8195 | -1.2893 | -1.1718 | -1.1309 | -9.5689 | -9.5044 | 0.19724 | -9.6808 | 113.1276 | 113.4074 | 112.8199 | -9.7293 | -0.19848 | -114.8285 | 3.8911 | 6.5509 | 6.7494 | -114.711 | -114.67 | -0.35888 | -0.41157 | -0.13393 | -0.31038 | 0.048499 | -0.13175 | -0.71919 | 8.0811 | 8.1986 | 8.2395 | 7.751 | -123.108 | 122.498 | 122.7778 | 122.1904 | 9.5677 | -123.2684
394.7344 | 123.0469 | -8.5968 | 114.4089 | 0.0069442 | -0.0077712 | 0.0042223 | 0.01987 | 0.0036494 | 0.011219 | 0.0014498 | 0.00068369 | 0.0014571 | 0.0005128 | 0.0043375 | -0.00086748 | -4.2889 | -1.5324 | -2.2747 | -1.3305 | -1.2268 | -1.1767 | -8.1082 | -8.0117 | 0.20182 | -8.1927 | 114.611 | 114.8771 | 114.2576 | -8.2549 | 0.48857 | -115.7394 | 4.3079 | 6.3221 | 5.8336 | -115.6357 | -115.5855 | 0.34188 | 0.20211 | 0.58511 | 0.40408 | 0.0622 | 0.46823 | -0.15126 | 7.2663 | 7.37 | 7.4201 | 7.0644 | -122.5171 | 123.2078 | 123.4739 | 122.8544 | 8.7986 | -122.6638
396.4062 | 122.9874 | -4.7699 | 118.4784 | 0.0069442 | -0.0062756 | 0.0014445 | 0.022007 | 0.0015128 | 0.014211 | 0.0090803 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0049787 | -0.00086748 | -2.9749 | -1.2943 | -1.9679 | -1.4908 | -1.3779 | -1.3369 | -5.164 | -5.0218 | 0.23387 | -5.1845 | 117.5504 | 117.8166 | 117.2291 | -5.3016 | -0.39408 | -119.9692 | 1.795 | 2.802 | 3.1961 | -119.8563 | -119.8153 | -0.53168 | -0.92801 | -0.2519 | -0.41461 | 0.11708 | -0.66182 | -1.2493 | 3.2791 | 3.392 | 3.433 | 3.4756 | -123.6424 | 122.3203 | 122.5865 | 121.999 | 5.0038 | -123.78
398.1406 | 123.0789 | -6.4682 | 116.3361 | -0.0083178 | -0.0069166 | 0.0027265 | 0.020939 | 0.0021538 | 0.012715 | 0.0090803 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0049787 | -0.00065368 | -2.6361 | -1.3035 | -1.8718 | -1.3168 | -1.2085 | -1.1721 | -6.2034 | -6.0749 | 0.2064 | -6.2422 | 116.534 | 116.8139 | 116.0891 | -6.3364 | 0.26481 | -117.6529 | 3.8321 | 4.5964 | 4.3316 | -117.5445 | -117.5082 | 0.13181 | 0.1979 | 0.3933 | 0.22601 | 0.094206 | 0.4778 | -0.247 | 5.1514 | 5.2597 | 5.2961 | 5.1647 | -122.5395 | 123.0022 | 123.2821 | 122.5573 | 6.6746 | -122.6725
399.8281 | 123.0011 | -5.0949 | 118.1351 | 0.0069442 | -0.006703 | 0.0020855 | 0.021366 | 0.0017264 | 0.013142 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0007264 | 0.0047649 | -0.0010811 | -2.485 | -1.2119 | -1.7482 | -1.3168 | -1.2085 | -1.1629 | -5.512 | -5.3423 | 0.23387 | -5.5004 | 117.2436 | 117.519 | 117.0735 | -5.6129 | -0.41707 | -119.4519 | 2.6099 | 3.3468 | 3.7638 | -119.3435 | -119.298 | -0.51803 | -0.89145 | -0.2474 | -0.40553 | 0.1125 | -0.61611 | -1.0616 | 3.7781 | 3.8864 | 3.932 | 3.883 | -123.647 | 122.3385 | 122.6139 | 122.1684 | 5.3288 | -123.748
401.5625 | 122.9874 | -5.4611 | 117.5766 | 0.0069442 | -0.0071302 | 0.0037949 | 0.020511 | 0.0021538 | 0.013142 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0049787 | -0.00086748 | -1.9493 | -1.2531 | -1.6245 | -1.1978 | -1.0894 | -1.053 | -5.805 | -5.6537 | 0.21098 | -5.8255 | 116.9369 | 117.2122 | 116.5561 | -5.9289 | -0.34391 | -118.7744 | 3.5118 | 3.8366 | 4.1805 | -118.666 | -118.6296 | -0.46776 | -0.63974 | -0.19254 | -0.3644 | 0.10335 | -0.3644 | -1.0205 | 4.2633 | 4.3717 | 4.4081 | 4.208 | -123.3816 | 122.398 | 122.6733 | 122.0172 | 5.6721 | -123.5055
403.2969 | 122.9919 | -2.5772 | 120.4376 | -0.00068679 | -0.0047798 | -0.00090608 | 0.022862 | 1.7156e-05 | 0.01592 | -0.0061807 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0047649 | -0.00065368 | -1.6701 | -1.07 | -1.5009 | -1.3489 | -1.236 | -1.1904 | -2.8928 | -2.7279 | 0.21556 | -2.886 | 119.8442 | 120.1196 | 119.436 | -3.0305 | -0.31562 | -121.7865 | 0.90714 | 1.0763 | 1.3919 | -121.6736 | -121.628 | -0.45328 | -0.59342 | -0.15065 | -0.30879 | 0.14449 | -0.31801 | -1.0016 | 1.2283 | 1.3413 | 1.3868 | 1.5072 | -123.3305 | 122.4214 | 122.6968 | 122.0132 | 2.7928 | -123.4681
404.9844 | 129.1122 | -2.6321 | 120.3735 | -0.00068679 | -0.0045662 | -0.0021881 | 0.02393 | -0.00019664 | 0.016561 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.00086748 | -0.34233 | -0.5526 | -1.3315 | -1.651 | -1.5473 | -1.5246 | -2.8058 | -2.0823 | 1.374 | -1.4162 | 119.9266 | 120.1425 | 119.5184 | -2.9481 | -0.17369 | -122.0246 | 2.2898 | 1.3006 | 1.4743 | -121.9209 | -121.8982 | -0.31593 | -0.44692 | 0.54988 | 1.2159 | 1.5318 | -0.23103 | -0.8551 | 0.98111 | 1.0848 | 1.1075 | 2.0795 | -123.1794 | 122.5588 | 122.7746 | 122.1506 | 4.0061 | -123.3216
406.7188 | 123.0789 | -2.5269 | 120.4788 | -0.015949 | -0.0041388 | -0.0032565 | 0.024571 | -0.00062384 | 0.016988 | -0.0061807 | 0.00068369 | 0.0012435 | -0.0001282 | 0.0049787 | -0.00086748 | -1.9173 | -1.2989 | -1.739 | -1.6785 | -1.5656 | -1.5292 | -2.4304 | -2.27 | 0.20182 | -2.4235 | 120.3066 | 120.582 | 119.8481 | -2.5818 | 0.096494 | -122.1573 | 0.60956 | 0.78786 | 0.69136 | -122.0445 | -122.008 | -0.054909 | -0.17219 | 0.25686 | 0.10331 | 0.15822 | 0.10323 | -0.63073 | 0.84835 | 0.96122 | 0.99763 | 1.2279 | -122.9092 | 122.8335 | 123.1089 | 122.3749 | 2.7287 | -123.0606
408.3906 | 123.0011 | -2.2659 | 120.7581 | 0.0069442 | -0.0039252 | -0.0032565 | 0.024358 | -0.00019664 | 0.016988 | -0.0061807 | 0.00089729 | 0.00081608 | 8.5404e-05 | 0.0049787 | -0.00086748 | -1.8669 | -1.276 | -1.6978 | -1.6419 | -1.529 | -1.4834 | -2.2884 | -2.1281 | 0.19267 | -2.2679 | 120.4531 | 120.7377 | 120.0724 | -2.4261 | -0.022485 | -122.3999 | 0.39899 | 0.56814 | 0.59062 | -122.2871 | -122.2415 | -0.16015 | -0.30491 | 0.13788 | -0.001938 | 0.15822 | -0.020338 | -0.68561 | 0.62405 | 0.73693 | 0.78249 | 0.98991 | -123.0465 | 122.7191 | 123.0036 | 122.3384 | 2.4586 | -123.1841
410.125 | 123.0606 | -2.2659 | 120.7809 | -0.0083178 | -0.0039252 | -0.0036839 | 0.024785 | -0.00041024 | 0.016988 | 0.0090803 | 0.00068369 | 0.0014571 | 0.0002992 | 0.0049787 | -0.0010811 | -1.8578 | -1.2623 | -1.707 | -1.6373 | -1.5336 | -1.4972 | -2.206 | -2.0502 | 0.20182 | -2.2038 | 120.531 | 120.8156 | 120.0679 | -2.3574 | 0.059936 | -122.4182 | 0.40815 | 0.55898 | 0.49904 | -122.3145 | -122.2781 | -0.091472 | -0.24996 | 0.21572 | 0.062164 | 0.15364 | 0.03461 | -0.71308 | 0.62863 | 0.73235 | 0.76876 | 1.0036 | -122.9869 | 122.7969 | 123.0815 | 122.3338 | 2.4678 | -123.1383
411.7969 | 123.0972 | -2.0645 | 120.9274 | -0.0083178 | -0.0037114 | -0.0041111 | 0.024785 | -0.00062384 | 0.016775 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00065368 | -1.8349 | -1.2028 | -1.7024 | -1.6281 | -1.5198 | -1.4789 | -2.0732 | -1.9129 | 0.18809 | -2.0572 | 120.6729 | 120.9438 | 120.2144 | -2.22 | -0.008691 | -122.5556 | 0.22963 | 0.36214 | 0.37083 | -122.4473 | -122.4063 | -0.15552 | -0.25451 | 0.15166 | 0.007267 | 0.16279 | 0.016327 | -0.71305 | 0.43637 | 0.54467 | 0.58566 | 0.86175 | -123.0006 | 122.7374 | 123.0083 | 122.2789 | 2.2526 | -123.1475
413.5312 | 123.1247 | -2.037 | 120.9503 | -0.0083178 | -0.0037114 | -0.0036839 | 0.024571 | -0.0010512 | 0.017416 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.00065368 | -1.7845 | -1.1341 | -1.6337 | -1.5686 | -1.4466 | -1.4148 | -2.0183 | -1.8625 | 0.19724 | -2.0115 | 120.7141 | 120.9987 | 120.251 | -2.1651 | 0.01879 | -122.5189 | 0.25252 | 0.40335 | 0.38456 | -122.3969 | -122.3651 | -0.12804 | -0.2362 | 0.17456 | 0.025588 | 0.15363 | 0.048382 | -0.69931 | 0.46843 | 0.59047 | 0.62229 | 0.90296 | -122.9686 | 122.7512 | 123.0357 | 122.2881 | 2.2343 | -123.1154
415.2188 | 123.0698 | -1.9958 | 121.0281 | -0.00068679 | -0.0034978 | -0.0038975 | 0.024571 | -0.00083764 | 0.016988 | -0.029072 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0047649 | -0.00086748 | -1.7296 | -1.1204 | -1.6017 | -1.4999 | -1.3871 | -1.3552 | -2.0183 | -1.8671 | 0.18809 | -2.0115 | 120.7187 | 121.0033 | 120.3838 | -2.1697 | -0.022408 | -122.5281 | 0.26627 | 0.3942 | 0.41661 | -122.4152 | -122.3834 | -0.17382 | -0.30944 | 0.12878 | -0.01561 | 0.15821 | -0.024859 | -0.64435 | 0.4959 | 0.60879 | 0.64061 | 0.8755 | -123.0464 | 122.7145 | 122.9991 | 122.3796 | 2.1839 | -123.1978
416.9531 | 123.0469 | -1.8997 | 121.1517 | -0.00068679 | -0.0041388 | -0.0036839 | 0.024358 | -0.00083764 | 0.016988 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -1.693 | -1.0517 | -1.5696 | -1.4771 | -1.3687 | -1.3323 | -1.8672 | -1.716 | 0.18809 | -1.8558 | 120.8698 | 121.1544 | 120.457 | -2.0186 | 0.032565 | -122.6288 | 0.20676 | 0.33012 | 0.29755 | -122.5205 | -122.4841 | -0.11885 | -0.28194 | 0.18375 | 0.043935 | 0.16279 | 0.002639 | -0.69469 | 0.42266 | 0.53098 | 0.56737 | 0.84805 | -123.0189 | 122.7695 | 123.0541 | 122.3568 | 2.0878 | -123.1703
418.6875 | 123.1338 | -1.799 | 121.1746 | -0.0083178 | -0.0037114 | -0.0038975 | 0.024571 | -0.00083764 | 0.017416 | -0.013811 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0047649 | -0.0010811 | -1.638 | -1.0059 | -1.5284 | -1.445 | -1.3367 | -1.2911 | -1.7985 | -1.6427 | 0.19267 | -1.8008 | 120.9385 | 121.2185 | 120.6265 | -1.9453 | 0.000541 | -122.6196 | 0.161 | 0.27061 | 0.27007 | -122.5113 | -122.4658 | -0.1463 | -0.23615 | 0.1563 | -0.001829 | 0.14447 | 0.04385 | -0.54817 | 0.35401 | 0.46232 | 0.50787 | 0.79312 | -122.9731 | 122.7375 | 123.0175 | 122.4255 | 1.9917 | -123.1199
420.375 | 123.1384 | -1.799 | 121.1746 | -0.0083178 | -0.0041388 | -0.0030429 | 0.024358 | -0.00041024 | 0.017416 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0005128 | 0.0045513 | -0.00086748 | -1.5739 | -1.0746 | -1.4643 | -1.3672 | -1.2543 | -1.2179 | -1.7985 | -1.6336 | 0.18809 | -1.7779 | 120.943 | 121.2322 | 120.5349 | -1.9407 | 0.000541 | -122.5418 | 0.22509 | 0.33471 | 0.33417 | -122.4289 | -122.3925 | -0.14172 | -0.23158 | 0.16546 | 0.021065 | 0.16278 | 0.057586 | -0.63974 | 0.43184 | 0.54474 | 0.58113 | 0.72445 | -122.9731 | 122.7421 | 123.0312 | 122.3339 | 1.9871 | -123.1154
422.1406 | 123.0469 | -1.799 | 121.2341 | -0.00068679 | -0.0045662 | -0.0026155 | 0.02393 | -0.00083764 | 0.016988 | -0.0061807 | 0.00089729 | 0.00081608 | 0.0002992 | 0.0047649 | -0.0010811 | -1.464 | -1.0654 | -1.3773 | -1.2573 | -1.1535 | -1.1172 | -1.8305 | -1.6748 | 0.17893 | -1.8146 | 120.9156 | 121.1864 | 120.457 | -1.9774 | -0.031511 | -122.4914 | 0.33497 | 0.4217 | 0.45321 | -122.3877 | -122.3513 | -0.17835 | -0.31856 | 0.12425 | -0.015565 | 0.16278 | -0.047709 | -0.77708 | 0.54172 | 0.64548 | 0.68186 | 0.7336 | -123.0647 | 122.7146 | 122.9854 | 122.2561 | 1.9779 | -123.2115
423.8125 | 123.1201 | -1.6708 | 121.344 | -0.0083178 | -0.0041388 | -0.0024017 | 0.02393 | -0.00062384 | 0.016988 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0047649 | -0.00044008 | -1.3725 | -1.0654 | -1.3132 | -1.184 | -1.0803 | -1.0439 | -1.6565 | -1.4962 | 0.19724 | -1.636 | 121.0896 | 121.365 | 120.6493 | -1.8034 | 0.014314 | -122.528 | 0.29837 | 0.35762 | 0.3433 | -122.4243 | -122.3879 | -0.13253 | -0.25444 | 0.17465 | 0.034831 | 0.16736 | 0.020994 | -0.69465 | 0.4868 | 0.59057 | 0.62694 | 0.60543 | -123.0005 | 122.7604 | 123.0358 | 122.3202 | 1.8681 | -123.1474
425.5625 | 122.9828 | -1.593 | 121.4722 | -0.015949 | -0.0043526 | -0.0026155 | 0.02393 | -0.00083764 | 0.017416 | 0.016711 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0049787 | -0.0010811 | -1.313 | -1.0563 | -1.2491 | -1.1291 | -1.0162 | -0.97063 | -1.5558 | -1.3955 | 0.19724 | -1.5444 | 121.1903 | 121.4657 | 120.7501 | -1.7026 | 0.037231 | -122.6013 | 0.28007 | 0.3439 | 0.30666 | -122.4883 | -122.4428 | -0.10961 | -0.28188 | 0.19756 | 0.048586 | 0.1582 | -0.006451 | -0.72209 | 0.46392 | 0.57686 | 0.62238 | 0.53677 | -123.028 | 122.7833 | 123.0587 | 122.3431 | 1.7903 | -123.1748
427.2344 | 123.0194 | -1.4969 | 121.5179 | -0.0083178 | -0.0045662 | -0.0021881 | 0.023503 | -0.00062384 | 0.016988 | 0.0014498 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0045513 | -0.0010811 | -1.2626 | -1.0471 | -1.2033 | -1.0696 | -0.97037 | -0.92485 | -1.4688 | -1.3085 | 0.18351 | -1.4574 | 121.2773 | 121.5527 | 120.8737 | -1.6202 | 0.0281 | -122.5875 | 0.2343 | 0.29355 | 0.26545 | -122.4883 | -122.4428 | -0.12333 | -0.24067 | 0.18842 | 0.039451 | 0.16278 | 0.034766 | -0.64424 | 0.42731 | 0.52651 | 0.57204 | 0.44979 | -122.9867 | 122.7742 | 123.0496 | 122.3706 | 1.6804 | -123.1382
428.9688 | 123.1155 | -1.387 | 121.6187 | 0.0069442 | -0.0045662 | -0.0021881 | 0.02393 | -0.00083764 | 0.017202 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00065368 | -1.2031 | -1.015 | -1.1209 | -0.99632 | -0.87879 | -0.84701 | -1.3589 | -1.194 | 0.18809 | -1.3338 | 121.3917 | 121.6718 | 120.9286 | -1.5012 | 0.028131 | -122.615 | 0.18396 | 0.26609 | 0.23796 | -122.4974 | -122.4657 | -0.11414 | -0.22691 | 0.19303 | 0.053213 | 0.16735 | 0.053102 | -0.69001 | 0.3907 | 0.50823 | 0.54001 | 0.37198 | -122.9775 | 122.7788 | 123.0588 | 122.3157 | 1.5751 | -123.1198
430.7031 | 123.143 | -1.3 | 121.6599 | -0.00068679 | -0.0047798 | -0.0021881 | 0.024144 | -0.00062384 | 0.017629 | -0.0061807 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0049787 | -0.0010811 | -1.1985 | -0.98757 | -1.0706 | -0.95512 | -0.83758 | -0.80123 | -1.3131 | -1.1436 | 0.18809 | -1.2972 | 121.4329 | 121.7084 | 121.0248 | -1.46 | -0.013055 | -122.615 | 0.10156 | 0.22948 | 0.24253 | -122.4974 | -122.4611 | -0.1599 | -0.22691 | 0.15642 | 0.002868 | 0.16277 | 0.048532 | -0.63506 | 0.34493 | 0.46247 | 0.49882 | 0.31248 | -122.973 | 122.733 | 123.0084 | 122.3248 | 1.4881 | -123.1198
432.375 | 123.1247 | -1.2497 | 121.7514 | 0.014575 | -0.0045662 | -0.0021881 | 0.023717 | -0.00062384 | 0.016988 | -0.0061807 | 0.00025649 | 0.0010299 | 0.0002992 | 0.0049787 | -0.00065368 | -1.1344 | -0.92805 | -1.0248 | -0.90018 | -0.7918 | -0.76002 | -1.2353 | -1.0795 | 0.18809 | -1.2193 | 121.5199 | 121.7862 | 121.1438 | -1.3821 | 0.014433 | -122.6516 | 0.1153 | 0.22491 | 0.21047 | -122.5432 | -122.5114 | -0.13242 | -0.23147 | 0.17017 | 0.030352 | 0.16277 | 0.034815 | -0.60757 | 0.34952 | 0.4579 | 0.48968 | 0.32164 | -122.9867 | 122.7696 | 123.0359 | 122.3935 | 1.4378 | -123.1335
434.1094 | 123.0469 | -1.2772 | 121.7926 | 0.0069442 | -0.0043526 | -0.0024017 | 0.023717 | -0.0012648 | 0.017416 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0051923 | -0.0010811 | -1.1252 | -0.83648 | -1.0248 | -0.8956 | -0.7918 | -0.74628 | -1.2169 | -1.0475 | 0.19267 | -1.1965 | 121.5337 | 121.8183 | 121.0843 | -1.3546 | 0.060215 | -122.6882 | 0.15193 | 0.25237 | 0.19216 | -122.5844 | -122.5389 | -0.07748 | -0.25893 | 0.22968 | 0.080711 | 0.15819 | 0.025666 | -0.70829 | 0.38156 | 0.48537 | 0.53088 | 0.44068 | -123.0095 | 122.8108 | 123.0954 | 122.3615 | 1.4698 | -123.1472
435.7812 | 123.0698 | -1.2314 | 121.8109 | 0.0069442 | -0.0039252 | -0.0024017 | 0.02393 | -0.0012648 | 0.017416 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0049787 | -0.00086748 | -1.1207 | -0.70828 | -1.0156 | -0.88644 | -0.77806 | -0.7417 | -1.1986 | -1.0292 | 0.19267 | -1.1827 | 121.5611 | 121.832 | 121.1713 | -1.3409 | 0.032753 | -122.6974 | 0.11073 | 0.21575 | 0.183 | -122.589 | -122.5526 | -0.10952 | -0.24977 | 0.20222 | 0.04867 | 0.15819 | 0.021092 | -0.6396 | 0.34494 | 0.45333 | 0.48968 | 0.52311 | -123.0095 | 122.7925 | 123.0634 | 122.4027 | 1.424 | -123.1518
437.5156 | 123.1659 | -1.1536 | 121.8246 | 0.0069442 | -0.0045662 | -0.0026155 | 0.02393 | -0.0010512 | 0.017629 | -0.0061807 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0049787 | -0.00044008 | -1.0795 | -0.69912 | -1.0019 | -0.85897 | -0.75058 | -0.71423 | -1.162 | -0.99711 | 0.18809 | -1.1415 | 121.5978 | 121.8686 | 121.1347 | -1.2997 | -0.008435 | -122.6836 | 0.074112 | 0.15167 | 0.1601 | -122.5752 | -122.5389 | -0.14613 | -0.22688 | 0.15645 | 0.012059 | 0.15819 | 0.043988 | -0.68997 | 0.29459 | 0.40298 | 0.43933 | 0.45444 | -122.9866 | 122.7513 | 123.0222 | 122.2882 | 1.3417 | -123.1243
439.1875 | 123.0698 | -1.1536 | 121.8613 | -0.00068679 | -0.0045662 | -0.0028291 | 0.024358 | -0.0012648 | 0.017629 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0007264 | 0.0047649 | -0.00086748 | -1.0566 | -0.68996 | -0.97443 | -0.8315 | -0.72311 | -0.69592 | -1.1299 | -0.96048 | 0.18351 | -1.1095 | 121.6252 | 121.9007 | 121.2034 | -1.2722 | 0.023617 | -122.6928 | 0.097004 | 0.17914 | 0.15552 | -122.5844 | -122.5572 | -0.11866 | -0.23603 | 0.19308 | 0.04411 | 0.16277 | 0.039417 | -0.65791 | 0.32206 | 0.43045 | 0.45765 | 0.4636 | -122.9912 | 122.7788 | 123.0542 | 122.3569 | 1.3371 | -123.1335
440.9062 | 123.111 | -1.1261 | 121.8521 | -0.015949 | -0.0045662 | -0.0024017 | 0.02393 | -0.0010512 | 0.017629 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0051923 | -0.0010811 | -1.0428 | -0.67165 | -0.96527 | -0.81319 | -0.70937 | -0.67302 | -1.1116 | -0.94217 | 0.18351 | -1.0866 | 121.6436 | 121.9282 | 121.3224 | -1.2585 | 0.014468 | -122.6653 | 0.083274 | 0.16083 | 0.14636 | -122.5615 | -122.5251 | -0.13239 | -0.20856 | 0.18393 | 0.039538 | 0.17192 | 0.076044 | -0.52971 | 0.31291 | 0.41673 | 0.45307 | 0.45445 | -122.9637 | 122.7697 | 123.0543 | 122.4485 | 1.3096 | -123.1106
442.6094 | 123.0606 | -1.1169 | 121.9391 | 0.0069442 | -0.0045662 | -0.0026155 | 0.02393 | -0.0010512 | 0.017202 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -1.0062 | -0.65333 | -0.93322 | -0.78572 | -0.67732 | -0.6364 | -1.0658 | -0.90554 | 0.18809 | -1.0545 | 121.6848 | 121.9648 | 121.327 | -1.2127 | 0.051101 | -122.7248 | 0.11075 | 0.18372 | 0.13262 | -122.6164 | -122.5755 | -0.095755 | -0.25432 | 0.21141 | 0.062433 | 0.15819 | 0.025698 | -0.6121 | 0.33123 | 0.43962 | 0.48055 | 0.46361 | -123.0049 | 122.8017 | 123.0817 | 122.4439 | 1.305 | -123.1518
444.3281 | 123.1155 | -1.062 | 121.9254 | -0.0083178 | -0.0045662 | -0.0026155 | 0.02393 | -0.0010512 | 0.017416 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -0.98331 | -0.64418 | -0.91033 | -0.76282 | -0.64985 | -0.6135 | -1.0475 | -0.87806 | 0.18809 | -1.0225 | 121.7077 | 121.9877 | 121.2995 | -1.1898 | 0.014486 | -122.6882 | 0.078706 | 0.15168 | 0.13719 | -122.5752 | -122.5389 | -0.12779 | -0.2177 | 0.18395 | 0.039553 | 0.16735 | 0.062324 | -0.62584 | 0.29919 | 0.41216 | 0.44851 | 0.41784 | -122.9729 | 122.7697 | 123.0497 | 122.3615 | 1.2501 | -123.1152
446.0625 | 123.0331 | -1.0483 | 122.0078 | -0.0083178 | -0.0047798 | -0.0021881 | 0.023717 | -0.0010512 | 0.017416 | 0.0014498 | 0.00025649 | 0.0012435 | 8.5404e-05 | 0.0045513 | -0.00022648 | -0.95126 | -0.63044 | -0.88744 | -0.7262 | -0.62695 | -0.58603 | -1.0155 | -0.85059 | 0.18809 | -0.99499 | 121.7351 | 122.0289 | 121.3728 | -1.1578 | 0.032805 | -122.7339 | 0.097022 | 0.16084 | 0.12804 | -122.6347 | -122.5938 | -0.10947 | -0.27263 | 0.19769 | 0.053292 | 0.16276 | 0.021134 | -0.63498 | 0.32208 | 0.42132 | 0.46225 | 0.41784 | -123.0232 | 122.7834 | 123.0772 | 122.421 | 1.2364 | -123.1655
447.7969 | 123.143 | -1.0117 | 121.9711 | -0.0083178 | -0.0043526 | -0.0019745 | 0.02393 | -0.00083764 | 0.017629 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00065368 | -0.95584 | -0.62586 | -0.8737 | -0.71704 | -0.61322 | -0.5723 | -1.0017 | -0.83228 | 0.18809 | -0.98583 | 121.758 | 122.0289 | 121.3178 | -1.1486 | 0.009921 | -122.6882 | 0.055822 | 0.13795 | 0.12803 | -122.5843 | -122.5434 | -0.13694 | -0.21311 | 0.17938 | 0.025829 | 0.16276 | 0.057755 | -0.65331 | 0.29462 | 0.39844 | 0.43936 | 0.3858 | -122.9729 | 122.7697 | 123.0405 | 122.3295 | 1.1997 | -123.1197
449.5312 | 123.056 | -1.03 | 122.0169 | -0.0083178 | -0.0047798 | -0.0017607 | 0.023503 | -0.0010512 | 0.017629 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0005128 | 0.0049787 | -0.00086748 | -0.93294 | -0.62128 | -0.86455 | -0.70331 | -0.59948 | -0.56314 | -0.98342 | -0.82312 | 0.18351 | -0.96751 | 121.7763 | 122.0609 | 121.3316 | -1.1349 | 0.046547 | -122.7202 | 0.097024 | 0.16542 | 0.11887 | -122.6164 | -122.58 | -0.10489 | -0.24058 | 0.20685 | 0.062454 | 0.16734 | 0.044028 | -0.68535 | 0.32666 | 0.43049 | 0.46683 | 0.40868 | -123.0003 | 122.8063 | 123.0909 | 122.3615 | 1.2135 | -123.1518
451.2188 | 123.0972 | -1.0071 | 122.0032 | 0.0069442 | -0.0045662 | -0.0019745 | 0.023503 | -0.00083764 | 0.017629 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00086748 | -0.91921 | -0.62128 | -0.85997 | -0.69415 | -0.5949 | -0.55398 | -0.97426 | -0.81396 | 0.18809 | -0.95836 | 121.7809 | 122.0564 | 121.3087 | -1.1211 | 0.032817 | -122.6973 | 0.087872 | 0.14711 | 0.11429 | -122.5981 | -122.5572 | -0.11404 | -0.22226 | 0.19312 | 0.048723 | 0.16276 | 0.053183 | -0.69451 | 0.31293 | 0.41218 | 0.4531 | 0.3858 | -122.9774 | 122.788 | 123.0634 | 122.3157 | 1.1952 | -123.1243
452.8906 | 123.024 | -1.0208 | 122.0444 | -0.0083178 | -0.0045662 | -0.0017607 | 0.023503 | -0.0012648 | 0.017629 | -0.013811 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0045513 | -0.00065368 | -0.91005 | -0.61213 | -0.84623 | -0.67126 | -0.57201 | -0.53109 | -0.9651 | -0.79565 | 0.18809 | -0.94462 | 121.7992 | 122.0793 | 121.4323 | -1.0982 | 0.055708 | -122.7156 | 0.11076 | 0.17458 | 0.11887 | -122.6164 | -122.5755 | -0.077414 | -0.24515 | 0.22516 | 0.076192 | 0.15361 | 0.034877 | -0.61208 | 0.34955 | 0.44881 | 0.48972 | 0.40869 | -123.0095 | 122.82 | 123.1001 | 122.4531 | 1.2089 | -123.1426
454.625 | 123.0194 | -1.0025 | 122.081 | 0.0069442 | -0.0045662 | -0.0019745 | 0.023717 | -0.00083764 | 0.017416 | 0.0014498 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0047649 | -0.0010811 | -0.878 | -0.59839 | -0.81876 | -0.65752 | -0.54453 | -0.5082 | -0.92847 | -0.77275 | 0.19267 | -0.91257 | 121.8221 | 122.1021 | 121.3773 | -1.0708 | 0.074028 | -122.7385 | 0.1245 | 0.18374 | 0.10971 | -122.6255 | -122.5892 | -0.068253 | -0.25888 | 0.22975 | 0.089932 | 0.15818 | 0.021149 | -0.70365 | 0.34498 | 0.45797 | 0.49431 | 0.40411 | -123.0095 | 122.8246 | 123.1046 | 122.3798 | 1.1952 | -123.1517
456.2969 | 123.0331 | -0.98419 | 122.1039 | -0.00068679 | -0.0045662 | -0.0017607 | 0.023503 | -0.00062384 | 0.017629 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0047649 | -0.00086748 | -0.878 | -0.59839 | -0.80961 | -0.64379 | -0.54453 | -0.5082 | -0.91932 | -0.75902 | 0.18809 | -0.89883 | 121.8313 | 122.1159 | 121.501 | -1.0616 | 0.064876 | -122.7477 | 0.10619 | 0.17458 | 0.10971 | -122.6484 | -122.6121 | -0.077405 | -0.27261 | 0.22517 | 0.085358 | 0.16276 | 0.011996 | -0.60291 | 0.3404 | 0.43966 | 0.476 | 0.3858 | -123.0232 | 122.8155 | 123.1001 | 122.4852 | 1.1723 | -123.1655
458.0312 | 123.1293 | -0.9201 | 122.0673 | -0.00068679 | -0.0049936 | -0.0013333 | 0.023503 | -0.00041024 | 0.017629 | -0.013811 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0054059 | -0.00086748 | -0.85053 | -0.5755 | -0.79129 | -0.63005 | -0.51248 | -0.48072 | -0.901 | -0.7407 | 0.18809 | -0.88052 | 121.8542 | 122.1388 | 121.414 | -1.0479 | 0.019105 | -122.6973 | 0.069572 | 0.12881 | 0.10971 | -122.5797 | -122.548 | -0.12776 | -0.21309 | 0.1794 | 0.039586 | 0.16734 | 0.07151 | -0.65329 | 0.29005 | 0.40762 | 0.43938 | 0.34461 | -122.9683 | 122.7743 | 123.0589 | 122.3341 | 1.1082 | -123.1151
459.7656 | 123.0972 | -0.88348 | 122.1085 | -0.015949 | -0.0049936 | -0.0017607 | 0.023503 | -0.00083764 | 0.017629 | 0.0014498 | 0.00089729 | 0.0012435 | 0.0002992 | 0.0051923 | -0.00065368 | -0.80933 | -0.5526 | -0.75467 | -0.58885 | -0.48501 | -0.45325 | -0.87353 | -0.70407 | 0.17893 | -0.85305 | 121.8954 | 122.1708 | 121.5468 | -1.0112 | 0.009957 | -122.6973 | 0.074157 | 0.12882 | 0.11886 | -122.5935 | -122.5617 | -0.12775 | -0.21309 | 0.17941 | 0.030437 | 0.15818 | 0.062363 | -0.5617 | 0.29464 | 0.39848 | 0.43023 | 0.33088 | -122.982 | 122.7789 | 123.0543 | 122.4302 | 1.0624 | -123.1197
461.5 | 123.1155 | -0.87433 | 122.1085 | -0.0083178 | -0.0047798 | -0.0015471 | 0.023503 | -0.0010512 | 0.017629 | 0.0014498 | 0.00025649 | 0.0010299 | 0.0005128 | 0.0049787 | -0.0010811 | -0.80933 | -0.55718 | -0.74551 | -0.58427 | -0.46669 | -0.43952 | -0.85979 | -0.69492 | 0.18809 | -0.83931 | 121.9045 | 122.1846 | 121.5101 | -1.0021 | 0.014539 | -122.6927 | 0.065002 | 0.12882 | 0.11428 | -122.5751 | -122.548 | -0.12774 | -0.20393 | 0.17941 | 0.035019 | 0.16276 | 0.076098 | -0.59833 | 0.29006 | 0.40764 | 0.43481 | 0.31715 | -122.9682 | 122.7789 | 123.0589 | 122.3845 | 1.0624 | -123.1105
463.1719 | 123.0286 | -0.87891 | 122.1909 | -0.00068679 | -0.0047798 | -0.0015471 | 0.023503 | -0.0010512 | 0.017416 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0049787 | -0.00065368 | -0.72692 | -0.52971 | -0.70889 | -0.53848 | -0.43922 | -0.41204 | -0.81858 | -0.64913 | 0.18809 | -0.79352 | 121.9412 | 122.2212 | 121.4781 | -0.96086 | 0.060326 | -122.7293 | 0.15199 | 0.17002 | 0.10969 | -122.6301 | -122.6029 | -0.081957 | -0.2497 | 0.22978 | 0.085383 | 0.16734 | 0.030329 | -0.71278 | 0.34042 | 0.43969 | 0.46686 | 0.34919 | -123.0094 | 122.8201 | 123.1001 | 122.357 | 1.067 | -123.1517
464.9062 | 123.0515 | -0.83771 | 122.2366 | 0.0069442 | -0.0052072 | -0.0013333 | 0.023503 | -0.0012648 | 0.017843 | -0.013811 | 0.00089729 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00086748 | -0.69945 | -0.51598 | -0.68142 | -0.52017 | -0.41174 | -0.38457 | -0.79111 | -0.62166 | 0.19267 | -0.77063 | 121.9686 | 122.2532 | 121.5605 | -0.93339 | 0.046602 | -122.7568 | 0.13826 | 0.15629 | 0.10969 | -122.6484 | -122.6212 | -0.095682 | -0.26801 | 0.21605 | 0.067078 | 0.16276 | 0.016604 | -0.67614 | 0.31754 | 0.42596 | 0.45314 | 0.32173 | -123.0277 | 122.8063 | 123.0909 | 122.3982 | 1.0304 | -123.17
466.6406 | 123.143 | -0.78735 | 122.2092 | -0.015949 | -0.0052072 | -0.0013333 | 0.023289 | -0.0010512 | 0.017843 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0047649 | -0.00086748 | -0.6674 | -0.51598 | -0.65853 | -0.4927 | -0.39801 | -0.36168 | -0.76363 | -0.59876 | 0.19267 | -0.75231 | 122.0007 | 122.2807 | 121.533 | -0.90592 | 0.023721 | -122.7019 | 0.11996 | 0.12883 | 0.10511 | -122.6072 | -122.5708 | -0.11856 | -0.20849 | 0.18859 | 0.035039 | 0.1536 | 0.071541 | -0.67615 | 0.29465 | 0.38935 | 0.42567 | 0.27138 | -122.9728 | 122.788 | 123.0681 | 122.3204 | 0.98002 | -123.1151
468.375 | 123.143 | -0.737 | 122.2412 | -0.00068679 | -0.0049936 | -0.00090608 | 0.023076 | -0.00083764 | 0.017843 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00065368 | -0.64908 | -0.5114 | -0.63106 | -0.46981 | -0.37053 | -0.34337 | -0.7499 | -0.57587 | 0.19267 | -0.72484 | 122.0236 | 122.299 | 121.6017 | -0.89676 | -0.012896 | -122.711 | 0.087916 | 0.10594 | 0.11884 | -122.6117 | -122.5846 | -0.15976 | -0.21764 | 0.16113 | 0.012157 | 0.17192 | 0.057812 | -0.63951 | 0.26719 | 0.36647 | 0.39363 | 0.2256 | -122.9911 | 122.7606 | 123.036 | 122.3387 | 0.92966 | -123.138
470.0469 | 123.056 | -0.75989 | 122.2961 | -0.0083178 | -0.0049936 | -0.00069228 | 0.022862 | -0.00062384 | 0.017629 | 0.0014498 | 4.2686e-05 | 0.0012435 | 0.0002992 | 0.0047649 | -0.00086748 | -0.63077 | -0.49308 | -0.61274 | -0.45607 | -0.36595 | -0.32047 | -0.71784 | -0.56213 | 0.19267 | -0.70195 | 122.0419 | 122.3173 | 121.6475 | -0.86471 | 0.042045 | -122.7522 | 0.12912 | 0.14715 | 0.1051 | -122.6621 | -122.6166 | -0.10482 | -0.25426 | 0.19775 | 0.057939 | 0.16276 | 0.021194 | -0.64866 | 0.30382 | 0.39393 | 0.43942 | 0.26681 | -123.014 | 122.8018 | 123.0772 | 122.4074 | 0.95255 | -123.1609
471.7188 | 123.0057 | -0.74616 | 122.3145 | -0.00068679 | -0.0052072 | -0.00090608 | 0.023289 | -0.0010512 | 0.017629 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0049787 | -0.0010811 | -0.60788 | -0.49308 | -0.59901 | -0.43776 | -0.33848 | -0.29758 | -0.68579 | -0.53466 | 0.19267 | -0.6699 | 122.0739 | 122.3448 | 121.6063 | -0.84639 | 0.060364 | -122.7522 | 0.13828 | 0.14715 | 0.086783 | -122.6529 | -122.612 | -0.10024 | -0.24052 | 0.21149 | 0.076257 | 0.17649 | 0.030356 | -0.70818 | 0.3084 | 0.40767 | 0.44858 | 0.25307 | -123.0002 | 122.8201 | 123.091 | 122.3524 | 0.93882 | -123.1608
473.4375 | 123.1293 | -0.67291 | 122.3099 | 0.0069442 | -0.0052072 | -0.0011197 | 0.023076 | -0.00083764 | 0.017202 | -0.0061807 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00086748 | -0.58041 | -0.47935 | -0.56238 | -0.40571 | -0.32017 | -0.27469 | -0.66748 | -0.50719 | 0.18809 | -0.64701 | 122.0968 | 122.3769 | 121.6795 | -0.80976 | 0.005438 | -122.7156 | 0.092505 | 0.11053 | 0.10509 | -122.63 | -122.5846 | -0.13685 | -0.21305 | 0.16572 | 0.025908 | 0.16276 | 0.066984 | -0.63034 | 0.2672 | 0.35275 | 0.39823 | 0.19357 | -122.9774 | 122.7697 | 123.0498 | 122.3524 | 0.861 | -123.1196
475.1719 | 123.1613 | -0.66834 | 122.3236 | -0.0083178 | -0.0054208 | -0.00090608 | 0.023076 | -0.0012648 | 0.017416 | 0.0014498 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0047649 | -0.0010811 | -0.55752 | -0.47019 | -0.55322 | -0.37824 | -0.29727 | -0.24721 | -0.63542 | -0.48887 | 0.19267 | -0.62411 | 122.1243 | 122.4043 | 121.6658 | -0.78229 | 0.032912 | -122.7018 | 0.11082 | 0.11511 | 0.082198 | -122.6209 | -122.5708 | -0.11395 | -0.19931 | 0.17946 | 0.044224 | 0.15818 | 0.080722 | -0.65781 | 0.29009 | 0.37106 | 0.42112 | 0.19815 | -122.959 | 122.7926 | 123.0727 | 122.3341 | 0.861 | -123.1059
476.8438 | 123.111 | -0.64545 | 122.3694 | -0.0083178 | -0.0054208 | -0.00069228 | 0.023076 | -0.00083764 | 0.017843 | 0.016711 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0047649 | -0.00086748 | -0.53462 | -0.4473 | -0.53491 | -0.36451 | -0.29269 | -0.23806 | -0.62169 | -0.47514 | 0.18809 | -0.60122 | 122.138 | 122.4272 | 121.7665 | -0.7594 | 0.023761 | -122.7339 | 0.11082 | 0.11053 | 0.086774 | -122.6621 | -122.6074 | -0.11395 | -0.23135 | 0.17031 | 0.044229 | 0.15818 | 0.057838 | -0.60286 | 0.28094 | 0.35275 | 0.40739 | 0.19815 | -122.9911 | 122.7835 | 123.0727 | 122.412 | 0.83353 | -123.1288
478.5781 | 123.0972 | -0.62256 | 122.3831 | -0.00068679 | -0.0054208 | -0.00069228 | 0.022648 | -0.0010512 | 0.017629 | 0.0014498 | 0.00089729 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00086748 | -0.52089 | -0.43356 | -0.5166 | -0.34619 | -0.27896 | -0.21059 | -0.60337 | -0.44767 | 0.18809 | -0.5829 | 122.1563 | 122.441 | 121.7436 | -0.74566 | 0.019189 | -122.7293 | 0.10167 | 0.10596 | 0.086771 | -122.6621 | -122.5937 | -0.1231 | -0.22677 | 0.17489 | 0.039656 | 0.16276 | 0.057841 | -0.63948 | 0.27637 | 0.3436 | 0.41197 | 0.189 | -122.9865 | 122.7789 | 123.0635 | 122.3662 | 0.81064 | -123.1288
480.3281 | 123.0057 | -0.64087 | 122.4609 | -0.00068679 | -0.0052072 | -0.00069228 | 0.022862 | -0.0010512 | 0.017416 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0047649 | -0.00086748 | -0.51173 | -0.4244 | -0.5166 | -0.34619 | -0.2698 | -0.19227 | -0.58963 | -0.44309 | 0.19267 | -0.56917 | 122.1701 | 122.4593 | 121.7528 | -0.73192 | 0.051235 | -122.8071 | 0.12914 | 0.12427 | 0.073035 | -122.7307 | -122.6532 | -0.091053 | -0.29086 | 0.19778 | 0.071702 | 0.16275 | -0.001663 | -0.70815 | 0.29468 | 0.37107 | 0.4486 | 0.21647 | -123.0506 | 122.811 | 123.1001 | 122.3937 | 0.83353 | -123.1929
482.0156 | 123.1476 | -0.58594 | 122.3877 | -0.015949 | -0.0052072 | -0.00069228 | 0.023076 | -0.0010512 | 0.017843 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0047649 | -0.0012947 | -0.50257 | -0.41525 | -0.50744 | -0.34161 | -0.27438 | -0.19685 | -0.58505 | -0.43851 | 0.18809 | -0.56459 | 122.1792 | 122.4547 | 121.7345 | -0.72734 | 0.000882 | -122.7293 | 0.083362 | 0.078495 | 0.077613 | -122.6621 | -122.5845 | -0.14141 | -0.20846 | 0.14743 | 0.021349 | 0.16275 | 0.067 | -0.65322 | 0.24432 | 0.31156 | 0.38909 | 0.17069 | -122.9727 | 122.7652 | 123.0406 | 122.3204 | 0.77402 | -123.115
483.75 | 123.1522 | -0.59052 | 122.4197 | -0.00068679 | -0.0049936 | -0.00047868 | 0.023076 | -0.0012648 | 0.017629 | -0.0061807 | 0.00068369 | 0.0014571 | 0.0005128 | 0.0043375 | -0.00086748 | -0.498 | -0.39693 | -0.48913 | -0.30956 | -0.25148 | -0.14191 | -0.55758 | -0.40646 | 0.18809 | -0.54169 | 122.193 | 122.4776 | 121.8902 | -0.70903 | 0.032934 | -122.7293 | 0.092518 | 0.10139 | 0.068452 | -122.6712 | -122.5616 | -0.11851 | -0.22676 | 0.18406 | 0.048821 | 0.16733 | 0.057849 | -0.52959 | 0.28095 | 0.33903 | 0.44861 | 0.19358 | -122.9773 | 122.7835 | 123.0681 | 122.4807 | 0.7786 | -123.1288
485.5 | 123.0331 | -0.63171 | 122.4472 | 0.0069442 | -0.0056346 | -5.128e-05 | 0.022435 | -0.0012648 | 0.017629 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0002992 | 0.0045513 | -0.00086748 | -0.49342 | -0.41525 | -0.49371 | -0.31872 | -0.26064 | -0.15107 | -0.56674 | -0.41562 | 0.19267 | -0.55085 | 122.193 | 122.4776 | 121.8444 | -0.70903 | 0.064975 | -122.7659 | 0.1383 | 0.13801 | 0.073032 | -122.7078 | -122.5983 | -0.077314 | -0.25423 | 0.2161 | 0.080862 | 0.15818 | 0.030383 | -0.60284 | 0.31299 | 0.37107 | 0.48065 | 0.21647 | -123.0139 | 122.8247 | 123.1093 | 122.4761 | 0.82438 | -123.1562
487.2344 | 123.0927 | -0.59509 | 122.4197 | -0.00068679 | -0.0054208 | -0.00047868 | 0.023289 | -0.0010512 | 0.017843 | 0.0014498 | 0.00089729 | 0.0010299 | 0.0002992 | 0.0049787 | -0.00086748 | -0.48884 | -0.40609 | -0.49371 | -0.3233 | -0.25148 | -0.12359 | -0.55758 | -0.41104 | 0.19267 | -0.54627 | 122.1884 | 122.4822 | 121.8489 | -0.70445 | 0.037512 | -122.743 | 0.10625 | 0.10139 | 0.063874 | -122.6712 | -122.5433 | -0.10936 | -0.23134 | 0.18406 | 0.04882 | 0.15818 | 0.062428 | -0.5708 | 0.27179 | 0.34361 | 0.4715 | 0.189 | -122.9773 | 122.7835 | 123.0773 | 122.444 | 0.78776 | -123.1242
488.9062 | 123.0972 | -0.56763 | 122.4655 | -0.00068679 | -0.0054208 | -5.128e-05 | 0.022435 | -0.0014786 | 0.017629 | -0.0061807 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0049787 | -0.00065368 | -0.46137 | -0.38777 | -0.46624 | -0.29125 | -0.22859 | -0.06865 | -0.52553 | -0.38814 | 0.18351 | -0.5188 | 122.225 | 122.5096 | 121.8215 | -0.67698 | 0.042098 | -122.7568 | 0.10626 | 0.10139 | 0.059292 | -122.6941 | -122.5342 | -0.10935 | -0.24049 | 0.17948 | 0.048826 | 0.15818 | 0.044123 | -0.64404 | 0.27638 | 0.33904 | 0.49898 | 0.17985 | -122.991 | 122.7927 | 123.0773 | 122.3891 | 0.75113 | -123.1425
490.6406 | 123.0743 | -0.54932 | 122.4701 | -0.0083178 | -0.0056346 | -0.00047868 | 0.022435 | -0.00083764 | 0.017843 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -0.44763 | -0.37862 | -0.44792 | -0.27294 | -0.21485 | -0.050335 | -0.51637 | -0.36525 | 0.18351 | -0.50049 | 122.2388 | 122.5325 | 121.7803 | -0.65408 | 0.032945 | -122.743 | 0.10168 | 0.10139 | 0.068447 | -122.6849 | -122.5204 | -0.10477 | -0.23133 | 0.18407 | 0.04883 | 0.1536 | 0.062438 | -0.68983 | 0.27638 | 0.33447 | 0.49898 | 0.1707 | -122.9865 | 122.7881 | 123.0818 | 122.3296 | 0.73282 | -123.1242
492.375 | 123.1155 | -0.54474 | 122.4472 | -0.00068679 | -0.0052072 | 0.00016232 | 0.022862 | -0.0010512 | 0.017629 | -0.0061807 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.00086748 | -0.43848 | -0.36488 | -0.44335 | -0.26378 | -0.20569 | -0.032021 | -0.50721 | -0.36525 | 0.19267 | -0.49133 | 122.2479 | 122.5325 | 121.8993 | -0.65408 | 0.037526 | -122.711 | 0.10626 | 0.10139 | 0.063867 | -122.6529 | -122.4792 | -0.10934 | -0.19929 | 0.17949 | 0.05341 | 0.16275 | 0.085326 | -0.5479 | 0.28096 | 0.33905 | 0.51272 | 0.17986 | -122.9544 | 122.7927 | 123.0773 | 122.444 | 0.7374 | -123.1013
494.0469 | 123.0423 | -0.56305 | 122.5113 | 0.0069442 | -0.0054208 | 0.00016232 | 0.022648 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0049787 | -0.00065368 | -0.45221 | -0.3832 | -0.45708 | -0.27294 | -0.21027 | -0.050335 | -0.52553 | -0.37899 | 0.19724 | -0.50049 | 122.2296 | 122.5234 | 121.8306 | -0.66324 | 0.03752 | -122.7842 | 0.11084 | 0.10597 | 0.068448 | -122.7216 | -122.5616 | -0.10019 | -0.28169 | 0.18406 | 0.062563 | 0.16275 | 0.012082 | -0.68066 | 0.29011 | 0.35278 | 0.51271 | 0.17985 | -123.0368 | 122.7927 | 123.0864 | 122.3937 | 0.76029 | -123.1745
495.7812 | 123.0377 | -0.59052 | 122.5159 | -0.00068679 | -0.0056346 | -0.00026488 | 0.022862 | -0.0010512 | 0.017843 | 0.0014498 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00086748 | -0.43848 | -0.3603 | -0.44335 | -0.26378 | -0.21485 | -0.032021 | -0.51179 | -0.36067 | 0.18351 | -0.48675 | 122.2433 | 122.5417 | 121.7986 | -0.65866 | 0.078723 | -122.7796 | 0.15204 | 0.14717 | 0.068446 | -122.7307 | -122.5479 | -0.068146 | -0.27253 | 0.22985 | 0.10376 | 0.17191 | 0.025819 | -0.71729 | 0.32673 | 0.37567 | 0.55849 | 0.23021 | -123.0277 | 122.8339 | 123.1322 | 122.3891 | 0.77402 | -123.1745
497.5156 | 123.0103 | -0.57678 | 122.525 | -0.00068679 | -0.0054208 | 0.00016232 | 0.022862 | -0.00083764 | 0.017843 | 0.0090803 | 0.00025649 | 0.0010299 | 0.0002992 | 0.0047649 | -0.00086748 | -0.42932 | -0.36488 | -0.43877 | -0.26378 | -0.21027 | -0.045757 | -0.50263 | -0.36067 | 0.19267 | -0.49133 | 122.2571 | 122.5417 | 121.7986 | -0.64492 | 0.074148 | -122.7888 | 0.14746 | 0.13801 | 0.063866 | -122.7353 | -122.5708 | -0.068143 | -0.26795 | 0.21611 | 0.085453 | 0.1536 | 0.016664 | -0.72645 | 0.313 | 0.36651 | 0.53102 | 0.2119 | -123.0277 | 122.8339 | 123.1185 | 122.3754 | 0.76945 | -123.1699
499.1875 | 123.1659 | -0.49896 | 122.4976 | -0.00068679 | -0.0058482 | -5.128e-05 | 0.023076 | -0.00062384 | 0.017843 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00086748 | -0.41559 | -0.34199 | -0.42961 | -0.24547 | -0.17364 | -0.027442 | -0.47974 | -0.33778 | 0.19267 | -0.45928 | 122.2708 | 122.5692 | 121.8993 | -0.62661 | 0.019223 | -122.743 | 0.083376 | 0.069351 | 0.050128 | -122.6712 | -122.525 | -0.12765 | -0.22675 | 0.16119 | 0.039684 | 0.16733 | 0.071601 | -0.59825 | 0.25349 | 0.32532 | 0.47152 | 0.15697 | -122.9773 | 122.7698 | 123.0681 | 122.3983 | 0.69163 | -123.1242
500.9219 | 122.9965 | -0.54932 | 122.5388 | -0.00068679 | -0.0056346 | -0.00026488 | 0.022862 | -0.0012648 | 0.017416 | 0.0014498 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.00044008 | -0.41559 | -0.3191 | -0.42961 | -0.25005 | -0.19653 | -0.027442 | -0.4889 | -0.34236 | 0.20182 | -0.47301 | 122.2662 | 122.56 | 121.8352 | -0.62203 | 0.060419 | -122.7888 | 0.13373 | 0.11971 | 0.059286 | -122.7353 | -122.5662 | -0.072714 | -0.27253 | 0.20696 | 0.076302 | 0.14902 | 0.021246 | -0.70355 | 0.29927 | 0.35278 | 0.52187 | 0.23022 | -123.0277 | 122.8155 | 123.1093 | 122.3845 | 0.75114 | -123.1608
502.6094 | 123.0148 | -0.59052 | 122.4792 | -0.00068679 | -0.0056346 | -0.00047868 | 0.022648 | -0.0012648 | 0.017416 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0047649 | -0.00065368 | -0.46137 | -0.37862 | -0.47082 | -0.30041 | -0.23317 | -0.10986 | -0.53926 | -0.38814 | 0.18809 | -0.5188 | 122.2159 | 122.5005 | 121.9588 | -0.67698 | 0.05125 | -122.7797 | 0.12915 | 0.1197 | 0.068449 | -122.7124 | -122.5891 | -0.086461 | -0.26338 | 0.20237 | 0.071714 | 0.15818 | 0.021233 | -0.52042 | 0.29011 | 0.35735 | 0.48066 | 0.2119 | -123.0185 | 122.8064 | 123.091 | 122.5493 | 0.7786 | -123.1562
504.3438 | 123.1384 | -0.55389 | 122.4426 | -0.00068679 | -0.0056346 | -5.128e-05 | 0.022862 | -0.0010512 | 0.017843 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0047649 | -0.00086748 | -0.45679 | -0.3603 | -0.46624 | -0.28667 | -0.22401 | -0.086964 | -0.52553 | -0.37899 | 0.18809 | -0.51422 | 122.2296 | 122.5142 | 121.8764 | -0.66782 | 0.028365 | -122.7293 | 0.097103 | 0.087657 | 0.059292 | -122.6666 | -122.5296 | -0.11393 | -0.21302 | 0.17491 | 0.039672 | 0.1536 | 0.07159 | -0.56621 | 0.26722 | 0.32989 | 0.46693 | 0.19359 | -122.9682 | 122.7835 | 123.0681 | 122.4303 | 0.74198 | -123.1104
506.0156 | 123.0835 | -0.19684 | 122.8363 | -0.015949 | -0.0045662 | -0.0019745 | 0.023289 | -0.00083764 | 0.017843 | 0.0090803 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0051923 | -0.00065368 | -0.11799 | -0.048958 | -0.12287 | 0.006344 | -0.077483 | 0.14197 | -0.17753 | -0.049318 | 0.19724 | -0.14793 | 122.5959 | 122.8805 | 122.1374 | -0.31525 | 0.019308 | -122.83 | 0.078847 | 0.073972 | 0.054664 | -122.9138 | -122.6943 | -0.11841 | -0.24042 | 0.14752 | 0.048913 | 0.16732 | 0.044201 | -0.69891 | 0.20318 | 0.11936 | 0.3388 | 0.14788 | -123.0138 | 122.7927 | 123.0773 | 122.3342 | 0.39408 | -123.1516
507.75 | 123.0606 | -0.13733 | 122.9141 | 0.0069442 | -0.0047798 | -0.0017607 | 0.023717 | -0.0010512 | 0.017843 | -0.0061807 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0047649 | -0.0010811 | -0.06305 | 0.001407 | -0.054192 | 0.070441 | -0.086641 | 0.19233 | 0.097205 | 0.010205 | 0.19724 | -0.088402 | 122.66 | 122.9538 | 122.2015 | -0.25115 | 0.23453 | -122.8437 | 0.074279 | 0.083137 | -0.1514 | -123.0008 | -122.7218 | -0.11382 | -0.25414 | 0.14753 | 0.048927 | 0.16274 | 0.039639 | -0.71263 | 0.20777 | 0.050688 | 0.32966 | 0.13874 | -122.8169 | 122.7973 | 123.0911 | 122.3388 | 0.33457 | -123.1653
509.4219 | 123.0057 | -0.16479 | 122.9416 | -0.00068679 | -0.0047798 | -0.0015471 | 0.023076 | -0.00083764 | 0.017629 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0047649 | -0.0010811 | -0.053893 | 0.001407 | -0.054192 | 0.084176 | -0.027115 | 0.20149 | 0.010206 | 0.010205 | 0.19267 | -0.074666 | 122.6646 | 122.9629 | 122.2152 | -0.23283 | 0.175 | -122.8574 | 0.1109 | 0.1106 | -0.064398 | -122.9687 | -122.7401 | -0.068036 | -0.27703 | 0.175 | 0.090129 | 0.15817 | 0.021331 | -0.72636 | 0.24897 | 0.13768 | 0.36628 | 0.1662 | -122.9314 | 122.8294 | 123.1277 | 122.38 | 0.35746 | -123.1744
511.1562 | 123.0011 | -0.16937 | 122.9462 | 0.0069442 | -0.0049936 | -0.0015471 | 0.023503 | -0.00083764 | 0.017843 | 0.0014498 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0051923 | -0.00086748 | -0.044736 | 0.005985 | -0.054192 | 0.088755 | -0.050009 | 0.20607 | 0.097205 | 0.014784 | 0.20182 | -0.065509 | 122.6691 | 122.9583 | 122.2152 | -0.23741 | 0.26658 | -122.8574 | 0.12464 | 0.11518 | -0.1514 | -122.9962 | -122.7401 | -0.068037 | -0.27703 | 0.18416 | 0.10386 | 0.1719 | 0.012174 | -0.73094 | 0.25813 | 0.11936 | 0.37544 | 0.17536 | -122.849 | 122.8385 | 123.1277 | 122.3846 | 0.37119 | -123.1836
512.8438 | 123.0377 | -0.16479 | 122.9004 | 0.014575 | -0.0052072 | -0.00069228 | 0.022862 | -0.0010512 | 0.017843 | 0.0014498 | 0.00047009 | 0.00060248 | 0.0007264 | 0.0047649 | -0.00065368 | -0.06305 | -0.007751 | -0.05877 | 0.079598 | -0.054588 | 0.20607 | 0.019363 | 0.010205 | 0.19724 | -0.083823 | 122.66 | 122.9492 | 122.3801 | -0.24657 | 0.18416 | -122.8208 | 0.10175 | 0.10602 | -0.078133 | -122.955 | -122.6943 | -0.081772 | -0.24041 | 0.175 | 0.080972 | 0.16274 | 0.048793 | -0.52033 | 0.24439 | 0.11021 | 0.37086 | 0.15704 | -122.881 | 122.8248 | 123.114 | 122.5449 | 0.36204 | -123.147
514.5781 | 123.0331 | -0.16479 | 122.8867 | -0.00068679 | -0.0049936 | -0.0011197 | 0.023076 | -0.00083764 | 0.017843 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00065368 | -0.06305 | 0.001407 | -0.063349 | 0.065863 | -0.059167 | 0.19233 | 0.023942 | 0.010205 | 0.19267 | -0.088402 | 122.6508 | 122.9492 | 122.348 | -0.25115 | 0.18874 | -122.8208 | 0.10175 | 0.10145 | -0.087291 | -122.9458 | -122.6943 | -0.086351 | -0.23583 | 0.175 | 0.076393 | 0.16274 | 0.062526 | -0.53865 | 0.23066 | 0.10563 | 0.35713 | 0.1662 | -122.8627 | 122.8156 | 123.114 | 122.5128 | 0.35746 | -123.1378
516.25 | 123.0011 | -0.17853 | 122.9324 | 0.014575 | -0.0049936 | -0.0011197 | 0.022862 | -0.0014786 | 0.017843 | -0.0061807 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0049787 | -0.00086748 | -0.06305 | -0.003172 | -0.072505 | 0.070441 | -0.09122 | 0.19233 | -0.026426 | -0.003531 | 0.19724 | -0.097559 | 122.6508 | 122.94 | 122.2335 | -0.25572 | 0.1521 | -122.862 | 0.11548 | 0.10602 | -0.046079 | -123.0237 | -122.7401 | -0.077197 | -0.28161 | 0.175 | 0.080969 | 0.15817 | 0.007593 | -0.69889 | 0.24897 | 0.087308 | 0.37086 | 0.17536 | -122.9589 | 122.8294 | 123.1186 | 122.4121 | 0.37577 | -123.1882
517.9844 | 123.111 | -0.15564 | 122.8867 | -0.0083178 | -0.0049936 | -0.0013333 | 0.022862 | -0.00083764 | 0.017629 | -0.0061807 | 0.0011109 | 0.0010299 | 0.0002992 | 0.0049787 | -0.0010811 | -0.06305 | 0.001407 | -0.063349 | 0.065863 | -0.082062 | 0.18775 | 0.065153 | 0.001048 | 0.18809 | -0.088402 | 122.6462 | 122.9446 | 122.2519 | -0.25572 | 0.22079 | -122.8208 | 0.09259 | 0.092291 | -0.1285 | -122.9687 | -122.6989 | -0.10008 | -0.24041 | 0.15669 | 0.067238 | 0.16732 | 0.057948 | -0.6348 | 0.2215 | 0.073578 | 0.34339 | 0.15705 | -122.8215 | 122.8019 | 123.1002 | 122.4075 | 0.34373 | -123.1424
519.6562 | 123.1476 | -0.13733 | 122.8729 | -0.00068679 | -0.0049936 | -0.0013333 | 0.022648 | -0.00083764 | 0.017843 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.0012947 | -0.06305 | -0.007751 | -0.077084 | 0.056706 | -0.082062 | 0.18317 | 0.078889 | 0.001048 | 0.19724 | -0.097559 | 122.6462 | 122.9354 | 122.2381 | -0.25572 | 0.21622 | -122.8162 | 0.074279 | 0.060245 | -0.15597 | -122.955 | -122.6898 | -0.1184 | -0.22668 | 0.13838 | 0.03977 | 0.15817 | 0.062523 | -0.6348 | 0.19404 | 0.055267 | 0.3205 | 0.12958 | -122.794 | 122.7836 | 123.0728 | 122.3755 | 0.33457 | -123.1286
521.3906 | 123.1064 | -0.21057 | 122.8134 | 0.022206 | -0.0043526 | -0.0017607 | 0.023289 | -0.00062384 | 0.018057 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00044008 | -0.12715 | -0.058115 | -0.13202 | 0.015501 | -0.082062 | 0.12823 | -0.19127 | -0.058476 | 0.18809 | -0.15708 | 122.5867 | 122.8759 | 122.2473 | -0.31525 | 0.019304 | -122.7979 | 0.083424 | 0.078548 | 0.059244 | -122.8955 | -122.6852 | -0.10468 | -0.22669 | 0.1521 | 0.053488 | 0.15817 | 0.06251 | -0.56614 | 0.22607 | 0.12851 | 0.3388 | 0.15246 | -123.0047 | 122.7973 | 123.0865 | 122.4579 | 0.39866 | -123.1287
523.1406 | 123.1338 | -0.3891 | 122.6303 | 0.0069442 | -0.0045662 | -0.0015471 | 0.022862 | -0.0010512 | 0.017843 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0054059 | -0.00065368 | -0.29197 | -0.21379 | -0.30142 | -0.13559 | -0.017957 | -0.050335 | -0.36069 | -0.22789 | 0.19267 | -0.34023 | 122.399 | 122.6882 | 122.1053 | -0.50298 | 0.028412 | -122.7659 | 0.09713 | 0.08768 | 0.059268 | -122.6483 | -122.6806 | -0.11388 | -0.2313 | 0.16121 | 0.048868 | 0.16275 | 0.057894 | -0.52497 | 0.25351 | 0.37114 | 0.33876 | 0.17531 | -122.991 | 122.7881 | 123.0773 | 122.4944 | 0.58176 | -123.1333
524.8281 | 123.1293 | -0.40741 | 122.5433 | -0.00068679 | -0.0022158 | -0.0019745 | 0.021152 | -0.0010512 | 0.017416 | 0.0014498 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0049787 | -0.0012947 | -0.33317 | -0.2321 | -0.33347 | -0.16764 | -0.031693 | -0.027442 | -0.40648 | -0.25536 | 0.19724 | -0.3677 | 122.367 | 122.6607 | 121.9451 | -0.54419 | 0.000933 | -122.711 | 0.074235 | 0.073943 | 0.07301 | -122.575 | -122.5708 | -0.13678 | -0.17638 | 0.15205 | 0.039707 | 0.17649 | 0.1174 | -0.59824 | 0.23977 | 0.37572 | 0.37997 | 0.17531 | -122.9498 | 122.7744 | 123.0681 | 122.3525 | 0.60465 | -123.0875
526.5625 | 123.1384 | -0.37537 | 122.5845 | -0.00068679 | -7.8988e-05 | -0.0030429 | 0.020084 | -0.0012648 | 0.017843 | 0.0014498 | 0.00068369 | 0.0014571 | 0.0002992 | 0.0049787 | -0.00086748 | -0.31944 | -0.22752 | -0.31515 | -0.1539 | -0.008799 | -0.041178 | -0.38816 | -0.23705 | 0.19724 | -0.36312 | 122.3761 | 122.6745 | 121.9909 | -0.52587 | -0.012795 | -122.7384 | 0.055926 | 0.060212 | 0.073007 | -122.5933 | -122.6257 | -0.15051 | -0.20842 | 0.13832 | 0.012241 | 0.16275 | 0.089934 | -0.59365 | 0.22147 | 0.36657 | 0.33419 | 0.14784 | -122.9727 | 122.7515 | 123.0498 | 122.3662 | 0.57261 | -123.1104
528.2969 | 123.056 | -0.39825 | 122.6532 | -0.015949 | 0.001844 | -0.0051795 | 0.019443 | -0.00083764 | 0.017629 | -0.0061807 | 0.00047009 | 0.00060248 | 8.5404e-05 | 0.0051923 | -0.0010811 | -0.29197 | -0.20921 | -0.28311 | -0.13101 | -0.013378 | -0.045757 | -0.36984 | -0.21873 | 0.19267 | -0.33565 | 122.4036 | 122.6974 | 122.0825 | -0.4984 | 0.028409 | -122.7842 | 0.10629 | 0.11515 | 0.086739 | -122.6666 | -122.699 | -0.10015 | -0.24961 | 0.17952 | 0.062602 | 0.16275 | 0.044163 | -0.57075 | 0.26725 | 0.38488 | 0.3525 | 0.18904 | -123.023 | 122.8018 | 123.0956 | 122.4807 | 0.59092 | -123.1516
529.9688 | 123.0331 | -0.58594 | 122.4976 | 0.0069442 | 0.00098941 | -0.0041111 | 0.01987 | -0.0010512 | 0.018057 | 0.0014498 | 0.00047009 | 0.0014571 | 0.0005128 | 0.0051923 | -0.00086748 | -0.3286 | -0.2321 | -0.31973 | -0.16306 | -0.063746 | -0.059493 | -0.38358 | -0.25536 | 0.18809 | -0.37228 | 122.3761 | 122.6653 | 122.0321 | -0.53503 | 0.20236 | -122.6606 | 0.25734 | 0.26621 | 0.06385 | -122.5613 | -122.5571 | 0.050904 | -0.12144 | 0.33058 | 0.21366 | 0.16275 | 0.16775 | -0.46547 | 0.42288 | 0.52219 | 0.52644 | 0.35384 | -122.8811 | 122.9621 | 123.2512 | 122.618 | 0.77402 | -123.0326
531.7031 | 123.0743 | -0.55847 | 122.4792 | -0.00068679 | -0.0017884 | -0.0011197 | 0.019657 | -0.0010512 | 0.017416 | 0.0014498 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0049787 | -0.0010811 | -0.44763 | -0.35115 | -0.45708 | -0.27294 | -0.21027 | -0.073228 | -0.51179 | -0.36983 | 0.19267 | -0.50049 | 122.2388 | 122.5417 | 121.8352 | -0.65866 | 0.04668 | -122.7522 | 0.11084 | 0.10139 | 0.054711 | -122.6895 | -122.5525 | -0.10019 | -0.24049 | 0.18864 | 0.057986 | 0.15818 | 0.06244 | -0.64404 | 0.28553 | 0.3482 | 0.48524 | 0.20733 | -122.991 | 122.7972 | 123.1002 | 122.3937 | 0.75114 | -123.1379
533.375 | 123.0469 | -0.54932 | 122.5067 | -0.00068679 | -0.001361 | -0.0011197 | 0.020084 | -0.00083764 | 0.017843 | -0.0061807 | 0.00047009 | 0.0014571 | 0.0002992 | 0.0051923 | -0.00086748 | -0.44306 | -0.34657 | -0.44335 | -0.28209 | -0.21485 | -0.050335 | -0.51179 | -0.36525 | 0.19724 | -0.49133 | 122.2433 | 122.5371 | 121.8764 | -0.6495 | 0.037524 | -122.7888 | 0.10626 | 0.10597 | 0.068446 | -122.7216 | -122.557 | -0.10019 | -0.26338 | 0.18407 | 0.057987 | 0.15817 | 0.030396 | -0.6303 | 0.26722 | 0.33447 | 0.49898 | 0.20275 | -123.0185 | 122.7927 | 123.0864 | 122.4257 | 0.74656 | -123.1562
535.1094 | 123.1384 | -0.53558 | 122.4426 | 0.014575 | -0.0015748 | -0.00090608 | 0.019657 | -0.00062384 | 0.017629 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0045513 | -0.00065368 | -0.43848 | -0.35115 | -0.44335 | -0.27294 | -0.21027 | -0.0366 | -0.49806 | -0.36525 | 0.19724 | -0.49133 | 122.2479 | 122.5508 | 121.8077 | -0.6495 | 0.037528 | -122.7156 | 0.097105 | 0.092237 | 0.054709 | -122.6529 | -122.4792 | -0.11392 | -0.19471 | 0.17033 | 0.044254 | 0.15817 | 0.10822 | -0.63489 | 0.26265 | 0.32531 | 0.49898 | 0.18444 | -122.9407 | 122.7835 | 123.0864 | 122.3433 | 0.73283 | -123.0921
536.8125 | 123.1384 | -0.52643 | 122.4609 | -0.00068679 | -0.0020022 | -0.0011197 | 0.01987 | -0.0010512 | 0.017416 | -0.0061807 | 0.00025649 | 0.0010299 | 0.0002992 | 0.0049787 | -0.00086748 | -0.44763 | -0.3603 | -0.45708 | -0.27294 | -0.21943 | -0.0366 | -0.50721 | -0.37899 | 0.19267 | -0.50964 | 122.2479 | 122.5371 | 121.8581 | -0.65866 | 0.019215 | -122.7339 | 0.078794 | 0.069347 | 0.050132 | -122.6804 | -122.4975 | -0.13223 | -0.21302 | 0.14744 | 0.016785 | 0.14902 | 0.076173 | -0.60284 | 0.25349 | 0.307 | 0.48983 | 0.16613 | -122.9681 | 122.7743 | 123.0635 | 122.3845 | 0.71909 | -123.1196
538.5469 | 123.0881 | -0.54932 | 122.4838 | -0.00068679 | -0.0026432 | -0.0011197 | 0.020725 | -0.00083764 | 0.017629 | 0.0014498 | 0.00047009 | 0.0014571 | 0.0002992 | 0.0051923 | -0.00065368 | -0.44306 | -0.35572 | -0.4525 | -0.27294 | -0.21485 | -0.041178 | -0.50263 | -0.36525 | 0.19267 | -0.50049 | 122.2433 | 122.5463 | 121.8032 | -0.65408 | 0.046682 | -122.7568 | 0.10626 | 0.096813 | 0.050131 | -122.6987 | -122.525 | -0.10477 | -0.24049 | 0.18407 | 0.04883 | 0.1536 | 0.062441 | -0.68067 | 0.27638 | 0.33447 | 0.50814 | 0.19359 | -122.9865 | 122.7927 | 123.0956 | 122.3525 | 0.74198 | -123.1379
540.2812 | 123.024 | -0.57678 | 122.4884 | -0.00068679 | -0.0030704 | -0.00090608 | 0.020511 | -0.0010512 | 0.017629 | 0.0014498 | 0.00025649 | 0.0012435 | 8.5404e-05 | 0.0049787 | -0.00065368 | -0.43848 | -0.3603 | -0.44335 | -0.27752 | -0.21943 | -0.0366 | -0.51179 | -0.36525 | 0.19724 | -0.49133 | 122.2433 | 122.5325 | 121.8627 | -0.65408 | 0.06499 | -122.7659 | 0.1383 | 0.13344 | 0.068446 | -122.7078 | -122.525 | -0.0773 | -0.24507 | 0.21153 | 0.085453 | 0.16275 | 0.044128 | -0.62573 | 0.29927 | 0.35735 | 0.54018 | 0.21648 | -123.0002 | 122.8201 | 123.1093 | 122.4395 | 0.77402 | -123.1425
541.9531 | 123.0972 | -0.54016 | 122.4792 | -0.00068679 | -0.0032842 | -0.00069228 | 0.020939 | -0.0010512 | 0.017843 | 0.0014498 | 0.00089729 | 0.0010299 | 0.0007264 | 0.0051923 | -0.00086748 | -0.44763 | -0.3603 | -0.44792 | -0.27752 | -0.21027 | -0.06865 | -0.51637 | -0.36525 | 0.19267 | -0.50049 | 122.2479 | 122.5325 | 122.0046 | -0.65866 | 0.02379 | -122.7568 | 0.092527 | 0.092237 | 0.068447 | -122.6895 | -122.5479 | -0.1185 | -0.23133 | 0.17491 | 0.039675 | 0.15818 | 0.053283 | -0.47463 | 0.26265 | 0.32989 | 0.47151 | 0.17986 | -122.9956 | 122.7881 | 123.0727 | 122.5448 | 0.73283 | -123.1379
543.6875 | 123.0423 | -0.60883 | 122.493 | 0.0069442 | -0.0037114 | -0.00047868 | 0.021152 | -0.0010512 | 0.018057 | 0.0014498 | 0.00047009 | 0.0012435 | -0.0001282 | 0.0049787 | -0.0010811 | -0.47053 | -0.39235 | -0.47539 | -0.30499 | -0.23775 | -0.13733 | -0.53926 | -0.40188 | 0.19724 | -0.53254 | 122.2021 | 122.5005 | 121.9543 | -0.69529 | 0.069561 | -122.798 | 0.1383 | 0.13343 | 0.063871 | -122.7307 | -122.6303 | -0.086466 | -0.29085 | 0.20695 | 0.076289 | 0.16275 | 0.0075 | -0.53873 | 0.30384 | 0.37108 | 0.4715 | 0.21647 | -123.0322 | 122.811 | 123.1093 | 122.5631 | 0.80607 | -123.1883
545.3594 | 123.0606 | -0.58136 | 122.5067 | 0.0069442 | -0.0037114 | -0.00047868 | 0.021366 | -0.0010512 | 0.017843 | 0.0014498 | 0.00089729 | 0.0012435 | 8.5404e-05 | 0.0051923 | -0.00086748 | -0.4751 | -0.39235 | -0.48455 | -0.30956 | -0.24232 | -0.11901 | -0.54384 | -0.40188 | 0.19724 | -0.53254 | 122.2159 | 122.5051 | 121.7619 | -0.68613 | 0.037516 | -122.8163 | 0.10625 | 0.096809 | 0.059293 | -122.749 | -122.6257 | -0.10477 | -0.29085 | 0.17948 | 0.048823 | 0.1536 | -0.001654 | -0.74477 | 0.2718 | 0.33904 | 0.46235 | 0.18901 | -123.0506 | 122.7972 | 123.0864 | 122.3433 | 0.7786 | -123.1928
547.0938 | 123.0011 | -0.62256 | 122.4426 | -0.00068679 | -0.0039252 | -0.00090608 | 0.021152 | -0.00083764 | 0.017843 | -0.013811 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0051923 | -0.00065368 | -0.48884 | -0.40609 | -0.48455 | -0.30041 | -0.2469 | -0.13733 | -0.54842 | -0.40646 | 0.20182 | -0.53254 | 122.2021 | 122.5005 | 121.8673 | -0.68613 | 0.074136 | -122.743 | 0.13372 | 0.13801 | 0.063872 | -122.6895 | -122.58 | -0.063575 | -0.24049 | 0.2161 | 0.090022 | 0.1536 | 0.057854 | -0.57537 | 0.32215 | 0.37566 | 0.48523 | 0.21647 | -122.9911 | 122.8247 | 123.123 | 122.4898 | 0.82438 | -123.1288
548.7656 | 122.9919 | -0.61798 | 122.4884 | -0.00068679 | -0.0037114 | -0.00069228 | 0.021152 | -0.0010512 | 0.017629 | 0.0014498 | 0.00025649 | 0.0010299 | 0.0002992 | 0.0049787 | -0.0015083 | -0.47968 | -0.40609 | -0.49371 | -0.31872 | -0.2469 | -0.11444 | -0.55758 | -0.42019 | 0.19724 | -0.55085 | 122.1976 | 122.4867 | 121.7619 | -0.70445 | 0.0604 | -122.8071 | 0.1383 | 0.12427 | 0.063874 | -122.7353 | -122.6028 | -0.086468 | -0.29085 | 0.19779 | 0.067129 | 0.1536 | -0.001658 | -0.72645 | 0.29926 | 0.37108 | 0.50355 | 0.21189 | -123.046 | 122.8155 | 123.1047 | 122.3799 | 0.81522 | -123.1929
550.7031 | 123.0469 | -0.65918 | 122.438 | -0.00068679 | -0.0039252 | -0.00026488 | 0.02158 | -0.00083764 | 0.018057 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0002992 | 0.0049787 | -0.00065368 | -0.51631 | -0.42898 | -0.5166 | -0.33703 | -0.2698 | -0.19685 | -0.58505 | -0.44309 | 0.20182 | -0.56917 | 122.1655 | 122.4593 | 121.7894 | -0.73192 | 0.074125 | -122.7751 | 0.14287 | 0.14258 | 0.068456 | -122.7078 | -122.6349 | -0.072742 | -0.27255 | 0.21609 | 0.090013 | 0.16275 | 0.021225 | -0.64863 | 0.32215 | 0.38938 | 0.46233 | 0.2302 | -123.0231 | 122.8247 | 123.1185 | 122.4486 | 0.861 | -123.17
552.4531 | 123.024 | -0.67749 | 122.4197 | -0.0083178 | -0.0037114 | -0.00026488 | 0.021366 | -0.00083764 | 0.017843 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0051923 | -0.0010811 | -0.53004 | -0.45188 | -0.53491 | -0.35077 | -0.28353 | -0.22432 | -0.60337 | -0.45682 | 0.20182 | -0.57832 | 122.1518 | 122.4455 | 121.7207 | -0.74566 | 0.07412 | -122.7705 | 0.14745 | 0.14258 | 0.068458 | -122.7033 | -122.6441 | -0.068169 | -0.26797 | 0.22067 | 0.099166 | 0.16734 | 0.025799 | -0.699 | 0.32672 | 0.39396 | 0.45317 | 0.22562 | -123.0231 | 122.8293 | 123.123 | 122.3982 | 0.87931 | -123.1654
554.1875 | 123.0057 | -0.67749 | 122.406 | 0.0069442 | -0.0045662 | -0.00069228 | 0.02158 | -0.0012648 | 0.017843 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0051923 | -0.0010811 | -0.5392 | -0.46561 | -0.54407 | -0.37366 | -0.30185 | -0.23806 | -0.61253 | -0.47056 | 0.20182 | -0.60122 | 122.1472 | 122.4272 | 121.7803 | -0.76855 | 0.064962 | -122.7797 | 0.13829 | 0.13342 | 0.06846 | -122.7079 | -122.6441 | -0.091063 | -0.25882 | 0.20693 | 0.076272 | 0.16734 | 0.021217 | -0.62574 | 0.30383 | 0.37564 | 0.43943 | 0.21188 | -123.0185 | 122.8247 | 123.1047 | 122.4578 | 0.87931 | -123.1746
555.9688 | 123.0103 | -0.70038 | 122.3877 | 0.0069442 | -0.0039252 | -0.00047868 | 0.02158 | -0.00083764 | 0.017843 | 0.0014498 | 0.00089729 | 0.0012435 | 0.0005128 | 0.0049787 | -0.00086748 | -0.55752 | -0.48392 | -0.56696 | -0.37824 | -0.31101 | -0.25179 | -0.63542 | -0.47514 | 0.19267 | -0.61953 | 122.1243 | 122.4226 | 121.7803 | -0.77771 | 0.064955 | -122.7659 | 0.14286 | 0.13342 | 0.068463 | -122.6987 | -122.6395 | -0.077332 | -0.2634 | 0.22524 | 0.080846 | 0.15818 | 0.03495 | -0.60743 | 0.32214 | 0.38937 | 0.44858 | 0.21645 | -123.0231 | 122.8247 | 123.123 | 122.4806 | 0.89304 | -123.1654
557.6562 | 123.1796 | -0.65002 | 122.3694 | 0.014575 | -0.0041388 | -5.128e-05 | 0.021794 | -0.00062384 | 0.017843 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0047649 | -0.00065368 | -0.54378 | -0.46561 | -0.54865 | -0.37366 | -0.29269 | -0.23348 | -0.62169 | -0.47056 | 0.19267 | -0.6058 | 122.1335 | 122.4226 | 121.6933 | -0.76855 | 0.028338 | -122.743 | 0.10624 | 0.10138 | 0.07304 | -122.6621 | -122.6029 | -0.11853 | -0.23593 | 0.17946 | 0.044228 | 0.16276 | 0.05326 | -0.67611 | 0.27636 | 0.35733 | 0.41655 | 0.18441 | -122.9911 | 122.7835 | 123.0727 | 122.3433 | 0.84269 | -123.1379
559.3906 | 123.0286 | -0.74616 | 122.319 | 0.0069442 | -0.0045662 | -5.128e-05 | 0.02158 | -0.00083764 | 0.017629 | 0.0014498 | 0.00025649 | 0.0012435 | 8.5404e-05 | 0.0054059 | -0.00065368 | -0.60788 | -0.52971 | -0.61274 | -0.43318 | -0.34306 | -0.30674 | -0.69495 | -0.53924 | 0.20182 | -0.67448 | 122.0694 | 122.3677 | 121.6154 | -0.83723 | 0.051206 | -122.7522 | 0.13828 | 0.13341 | 0.082207 | -122.6621 | -122.6258 | -0.09108 | -0.24968 | 0.20691 | 0.071678 | 0.16276 | 0.048671 | -0.7036 | 0.31297 | 0.4031 | 0.43942 | 0.21644 | -123.014 | 122.8155 | 123.1139 | 122.3616 | 0.94798 | -123.1563
561.1406 | 123.0331 | -0.78735 | 122.3145 | -0.00068679 | -0.0045662 | -5.128e-05 | 0.022007 | -0.0010512 | 0.017629 | 0.0014498 | 0.00068369 | 0.0012435 | -0.0001282 | 0.0051923 | -0.00065368 | -0.44763 | -0.37862 | -0.45708 | -0.26836 | -0.1828 | -0.14191 | -0.53926 | -0.38814 | 0.19267 | -0.53254 | 122.2067 | 122.528 | 121.826 | -0.68156 | 0.24809 | -122.5828 | 0.33972 | 0.33027 | 0.082184 | -122.4973 | -122.4564 | 0.1058 | -0.10774 | 0.39921 | 0.25482 | 0.14902 | 0.2135 | -0.4884 | 0.51899 | 0.60456 | 0.64545 | 0.40874 | -122.8537 | 122.9941 | 123.3153 | 122.6134 | 0.98002 | -122.996
562.8125 | 123.0652 | -0.75073 | 122.3099 | 0.014575 | -0.0043526 | -0.00026488 | 0.021794 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0049787 | -0.0010811 | -0.59872 | -0.51598 | -0.60816 | -0.4286 | -0.33848 | -0.293 | -0.68579 | -0.53008 | 0.20182 | -0.6699 | 122.0739 | 122.3723 | 121.8169 | -0.83266 | 0.064941 | -122.7385 | 0.15201 | 0.14257 | 0.077627 | -122.6484 | -122.6029 | -0.081924 | -0.23594 | 0.22065 | 0.080834 | 0.16276 | 0.062405 | -0.49298 | 0.32213 | 0.41225 | 0.45773 | 0.23476 | -122.9957 | 122.8247 | 123.123 | 122.5676 | 0.95255 | -123.1425
564.5469 | 123.1064 | -0.71869 | 122.2824 | -0.015949 | -0.0047798 | -0.00026488 | 0.022007 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0054059 | -0.0010811 | -0.68571 | -0.61213 | -0.69057 | -0.50644 | -0.4209 | -0.38 | -0.76821 | -0.6125 | 0.19267 | -0.75689 | 121.9869 | 122.2853 | 121.5422 | -0.9105 | -0.049523 | -122.7888 | 0.032978 | 0.028116 | 0.077639 | -122.7033 | -122.6624 | -0.19181 | -0.29547 | 0.10619 | -0.038205 | 0.1536 | 0.002877 | -0.74023 | 0.21225 | 0.29779 | 0.33869 | 0.10656 | -123.0506 | 122.7056 | 123.004 | 122.2609 | 0.91135 | -123.1929
566.2344 | 123.0469 | -0.65002 | 122.4335 | -0.0083178 | -0.0047798 | -0.00047868 | 0.022221 | -0.0010512 | 0.017416 | 0.0014498 | 4.2686e-05 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00065368 | -0.53004 | -0.4473 | -0.53491 | -0.35993 | -0.28811 | -0.22432 | -0.61253 | -0.46598 | 0.20182 | -0.6058 | 122.1426 | 122.4364 | 121.7986 | -0.7594 | 0.037496 | -122.7934 | 0.11998 | 0.11511 | 0.077616 | -122.7216 | -122.6578 | -0.10937 | -0.29086 | 0.18404 | 0.044228 | 0.1536 | 0.002909 | -0.63489 | 0.2901 | 0.36191 | 0.4257 | 0.20273 | -123.046 | 122.7926 | 123.0864 | 122.4486 | 0.85185 | -123.1929
567.9688 | 123.1613 | -0.6134 | 122.3831 | -0.015949 | -0.0047798 | -0.00047868 | 0.022007 | -0.00083764 | 0.017416 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0051923 | -0.00086748 | -0.54836 | -0.46103 | -0.56238 | -0.37366 | -0.29727 | -0.2289 | -0.64458 | -0.47056 | 0.19724 | -0.59664 | 122.1518 | 122.4455 | 121.8123 | -0.75482 | -0.031178 | -122.7568 | 0.065044 | 0.051022 | 0.0822 | -122.6804 | -122.612 | -0.14141 | -0.23135 | 0.14284 | 0.016764 | 0.15818 | 0.06242 | -0.5708 | 0.23974 | 0.31613 | 0.3845 | 0.15237 | -123.0277 | 122.7652 | 123.0589 | 122.4257 | 0.81065 | -123.1379
569.7031 | 123.1293 | -0.59509 | 122.4243 | -0.00068679 | -0.0047798 | -0.00026488 | 0.021794 | -0.0010512 | 0.017629 | -0.013811 | 0.00068369 | 0.00081608 | 0.0007264 | 0.0054059 | -0.00065368 | -0.498 | -0.37862 | -0.47082 | -0.30041 | -0.22859 | -0.11901 | -0.553 | -0.40646 | 0.2064 | -0.54169 | 122.2067 | 122.5096 | 121.9085 | -0.69071 | 0.042091 | -122.7247 | 0.097096 | 0.12428 | 0.082186 | -122.6529 | -122.5433 | -0.09562 | -0.21761 | 0.18863 | 0.053399 | 0.14902 | 0.085322 | -0.51585 | 0.29468 | 0.36651 | 0.47608 | 0.21648 | -122.9773 | 122.8018 | 123.1047 | 122.5036 | 0.80149 | -123.115
571.375 | 123.143 | -0.70038 | 122.3099 | 0.0069442 | -0.0052072 | -0.00026488 | 0.021794 | -0.0010512 | 0.017629 | 0.0090803 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0056197 | -0.0010811 | -0.66282 | -0.53429 | -0.61732 | -0.43318 | -0.34764 | -0.31132 | -0.70869 | -0.55298 | 0.19724 | -0.70195 | 122.051 | 122.354 | 121.5971 | -0.85097 | -0.008308 | -122.7431 | 0.037559 | 0.083057 | 0.091365 | -122.6575 | -122.6212 | -0.15059 | -0.25883 | 0.1474 | -0.001571 | 0.14902 | 0.044091 | -0.71276 | 0.2672 | 0.35274 | 0.38906 | 0.16609 | -123.0186 | 122.7514 | 123.0543 | 122.2975 | 0.89762 | -123.1608
573.0938 | 123.0286 | -0.66376 | 122.3877 | -0.00068679 | -0.0047798 | -0.00090608 | 0.022648 | -0.0012648 | 0.017416 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0054059 | -0.00086748 | -0.57583 | -0.46103 | -0.54865 | -0.37366 | -0.29269 | -0.23806 | -0.62626 | -0.47056 | 0.20182 | -0.61495 | 122.1335 | 122.4318 | 121.6795 | -0.76855 | 0.037492 | -122.7614 | 0.087928 | 0.11511 | 0.077619 | -122.6804 | -122.6258 | -0.1048 | -0.25424 | 0.1932 | 0.048803 | 0.1536 | 0.044107 | -0.70816 | 0.2901 | 0.37107 | 0.4257 | 0.20273 | -123.014 | 122.7972 | 123.0956 | 122.3433 | 0.86558 | -123.1562
574.8281 | 123.0057 | -0.56305 | 122.5525 | -0.00068679 | -0.0047798 | -0.00090608 | 0.022221 | -0.00083764 | 0.017416 | 0.0090803 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -0.498 | -0.3832 | -0.47539 | -0.29583 | -0.23317 | -0.10986 | -0.54842 | -0.40188 | 0.20182 | -0.53254 | 122.2113 | 122.5005 | 121.7574 | -0.69071 | 0.014626 | -122.8483 | 0.065052 | 0.087655 | 0.073029 | -122.7857 | -122.6623 | -0.12766 | -0.3412 | 0.16117 | 0.030512 | 0.15818 | -0.052009 | -0.79512 | 0.26722 | 0.32988 | 0.45319 | 0.17985 | -123.1009 | 122.7743 | 123.0635 | 122.3204 | 0.76487 | -123.2432
576.5 | 123.143 | -0.43488 | 122.5479 | -0.00068679 | -0.0045662 | -0.0011197 | 0.022862 | -0.0010512 | 0.017416 | 0.0014498 | 0.00068369 | 0.0012435 | -0.0001282 | 0.0049787 | -0.0010811 | -0.3698 | -0.26415 | -0.3472 | -0.18137 | -0.04543 | -0.032021 | -0.42021 | -0.29199 | 0.2064 | -0.39975 | 122.3349 | 122.6241 | 121.8856 | -0.57166 | 0.014662 | -122.7293 | 0.065073 | 0.087673 | 0.073011 | -122.5933 | -122.5799 | -0.13679 | -0.213 | 0.14288 | 0.035121 | 0.17191 | 0.07619 | -0.66234 | 0.2535 | 0.38945 | 0.40285 | 0.17072 | -122.9681 | 122.7698 | 123.059 | 122.3204 | 0.64128 | -123.1196
578.2344 | 123.143 | -0.47607 | 122.4747 | -0.00068679 | -0.0043526 | -0.00090608 | 0.022648 | -0.00083764 | 0.017416 | -0.013811 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0054059 | -0.00065368 | -0.4339 | -0.32825 | -0.41588 | -0.24089 | -0.18738 | -0.0366 | -0.48432 | -0.34693 | 0.2064 | -0.48675 | 122.2662 | 122.5554 | 121.826 | -0.63119 | -0.008244 | -122.7156 | 0.042175 | 0.060198 | 0.068442 | -122.662 | -122.5113 | -0.15511 | -0.20844 | 0.12914 | -0.010676 | 0.14444 | 0.080754 | -0.64862 | 0.23519 | 0.2887 | 0.43947 | 0.14782 | -122.959 | 122.7423 | 123.0315 | 122.3021 | 0.68247 | -123.1059
579.9688 | 123.1064 | -0.38452 | 122.6074 | -0.0083178 | -0.0047798 | -0.00090608 | 0.022221 | -0.0010512 | 0.017629 | 0.0090803 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.00086748 | -0.32402 | -0.22295 | -0.31973 | -0.14932 | -0.008799 | -0.041178 | -0.39274 | -0.25078 | 0.19267 | -0.37686 | 122.367 | 122.6653 | 121.9359 | -0.53045 | -0.008219 | -122.7567 | 0.060503 | 0.064789 | 0.073008 | -122.6162 | -122.6486 | -0.14593 | -0.24047 | 0.13374 | 0.00766 | 0.15359 | 0.057889 | -0.67149 | 0.2352 | 0.37572 | 0.34334 | 0.16158 | -123.0002 | 122.7515 | 123.0498 | 122.3205 | 0.57719 | -123.1379
581.6406 | 123.1338 | -0.41657 | 122.6074 | -0.0083178 | -0.0043526 | -0.0011197 | 0.022648 | -0.00062384 | 0.017202 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0051923 | -0.0010811 | -0.33775 | -0.25042 | -0.32431 | -0.16306 | -0.013378 | -0.0366 | -0.4019 | -0.26452 | 0.20182 | -0.39518 | 122.3578 | 122.6424 | 121.9222 | -0.54877 | 0.014667 | -122.7705 | 0.078812 | 0.092254 | 0.077587 | -122.6208 | -122.644 | -0.1322 | -0.24962 | 0.15205 | 0.021389 | 0.15359 | 0.034996 | -0.68522 | 0.25351 | 0.40319 | 0.37996 | 0.16615 | -123.0093 | 122.7744 | 123.059 | 122.3388 | 0.61839 | -123.1562
583.375 | 123.1338 | -0.35706 | 122.6395 | -0.00068679 | -0.0045662 | -0.0011197 | 0.022648 | -0.00083764 | 0.017416 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0054059 | -0.00065368 | -0.2645 | -0.168 | -0.25106 | -0.094381 | -0.031693 | -0.059493 | -0.33779 | -0.19126 | 0.20182 | -0.31734 | 122.4265 | 122.7203 | 122.0229 | -0.47093 | 0.019263 | -122.7338 | 0.092557 | 0.106 | 0.086735 | -122.6712 | -122.699 | -0.11387 | -0.21299 | 0.1658 | 0.039718 | 0.15359 | 0.080789 | -0.61654 | 0.26267 | 0.32536 | 0.29756 | 0.18905 | -122.9773 | 122.7835 | 123.0773 | 122.38 | 0.55888 | -123.1104
585.1094 | 123.0698 | -0.35248 | 122.7173 | 0.0069442 | -0.0045662 | -0.00090608 | 0.022435 | -0.00062384 | 0.017416 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0049787 | -0.00086748 | -0.22787 | -0.13595 | -0.22359 | -0.071489 | -0.036272 | 0.018344 | -0.30574 | -0.15921 | 0.2064 | -0.27155 | 122.4677 | 122.766 | 122.1878 | -0.4343 | 0.046738 | -122.7888 | 0.12461 | 0.12889 | 0.082151 | -122.7536 | -122.6989 | -0.081821 | -0.2496 | 0.19327 | 0.080928 | 0.16275 | 0.048755 | -0.52953 | 0.28099 | 0.31621 | 0.37082 | 0.21653 | -123.023 | 122.8202 | 123.1185 | 122.5402 | 0.55888 | -123.1516
586.7969 | 123.1201 | -0.28839 | 122.7264 | -0.0083178 | -0.0043526 | -0.00069228 | 0.022648 | -0.0010512 | 0.017843 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0049787 | -0.0010811 | -0.20498 | -0.11306 | -0.20528 | -0.057754 | -0.04543 | 0.045815 | -0.28285 | -0.14547 | 0.2064 | -0.25781 | 122.4906 | 122.7752 | 122.1786 | -0.41598 | 0.005545 | -122.7842 | 0.083411 | 0.083116 | 0.077571 | -122.7719 | -122.6806 | -0.12759 | -0.23586 | 0.14292 | 0.030577 | 0.15817 | 0.048757 | -0.54784 | 0.23064 | 0.24296 | 0.33421 | 0.17533 | -123.0093 | 122.779 | 123.0636 | 122.467 | 0.49479 | -123.1424
588.5156 | 123.0515 | -0.32501 | 122.7585 | -0.00068679 | -0.0047798 | -0.00090608 | 0.022648 | -0.00083764 | 0.017416 | -0.0061807 | 0.00068369 | 0.0014571 | 0.0002992 | 0.0054059 | -0.00086748 | -0.21414 | -0.12222 | -0.2007 | -0.057754 | -0.040851 | 0.022922 | -0.28742 | -0.13631 | 0.19724 | -0.25781 | 122.486 | 122.7752 | 122.0687 | -0.41598 | 0.037587 | -122.8162 | 0.11088 | 0.12432 | 0.086728 | -122.7993 | -122.7356 | -0.090972 | -0.27249 | 0.1887 | 0.067198 | 0.15817 | 0.016713 | -0.68977 | 0.26726 | 0.28416 | 0.34793 | 0.2028 | -123.0459 | 122.811 | 123.1002 | 122.3937 | 0.52226 | -123.1745
590.25 | 123.0881 | -0.27466 | 122.7219 | 0.0069442 | -0.0047798 | -0.00090608 | 0.022648 | -0.00062384 | 0.016988 | -0.0061807 | 0.00025649 | 0.00081608 | 0.0005128 | 0.0051923 | -0.0010811 | -0.17293 | -0.085587 | -0.17781 | -0.030283 | -0.063746 | 0.087023 | -0.25537 | -0.11342 | 0.20182 | -0.22576 | 122.5226 | 122.8164 | 122.0779 | -0.38393 | 0.019286 | -122.7521 | 0.10173 | 0.096852 | 0.077566 | -122.7856 | -122.6348 | -0.10927 | -0.19924 | 0.16124 | 0.048895 | 0.15817 | 0.094542 | -0.64399 | 0.24438 | 0.21091 | 0.36168 | 0.18907 | -122.9772 | 122.7973 | 123.0911 | 122.3525 | 0.47648 | -123.1058
591.9375 | 123.111 | -0.25635 | 122.7493 | -0.00068679 | -0.0047798 | -0.00069228 | 0.022648 | -0.00083764 | 0.017416 | 0.0090803 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0056197 | -0.0010811 | -0.16835 | -0.07643 | -0.15491 | -0.016548 | -0.063746 | 0.09618 | -0.24621 | -0.10426 | 0.20182 | -0.22118 | 122.5318 | 122.821 | 122.1466 | -0.3702 | 0.010134 | -122.7659 | 0.087995 | 0.10143 | 0.0913 | -122.8131 | -122.6531 | -0.11385 | -0.21755 | 0.15209 | 0.035163 | 0.14901 | 0.071654 | -0.60278 | 0.2398 | 0.1926 | 0.35253 | 0.17992 | -122.9955 | 122.7881 | 123.0773 | 122.4029 | 0.45817 | -123.1195
593.6719 | 123.0927 | -0.23804 | 122.7448 | -0.00068679 | -0.0045662 | -0.00047868 | 0.022648 | -0.0010512 | 0.017416 | 0.0090803 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0054059 | -0.0012947 | -0.15004 | -0.07643 | -0.15491 | -0.021127 | -0.068325 | 0.10076 | -0.23706 | -0.090527 | 0.2064 | -0.20745 | 122.5364 | 122.8347 | 122.1099 | -0.36104 | 0.000981 | -122.7659 | 0.087998 | 0.083123 | 0.082142 | -122.8131 | -122.644 | -0.123 | -0.20839 | 0.14751 | 0.030588 | 0.15359 | 0.089968 | -0.63483 | 0.21691 | 0.16971 | 0.3388 | 0.16161 | -122.9818 | 122.7744 | 123.0728 | 122.348 | 0.44444 | -123.1058
595.3594 | 123.1522 | -0.26093 | 122.731 | -0.0083178 | -0.0045662 | -0.0013333 | 0.022435 | -0.0010512 | 0.017629 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0051923 | -0.00086748 | -0.17293 | -0.090166 | -0.17781 | -0.025705 | -0.059167 | 0.068708 | -0.25537 | -0.11342 | 0.20182 | -0.22118 | 122.518 | 122.821 | 122.087 | -0.37935 | 0.005553 | -122.7567 | 0.087994 | 0.083119 | 0.077566 | -122.7902 | -122.6623 | -0.11843 | -0.21297 | 0.1475 | 0.03974 | 0.15817 | 0.089965 | -0.64399 | 0.23522 | 0.20176 | 0.32963 | 0.17076 | -122.9864 | 122.779 | 123.0819 | 122.348 | 0.46275 | -123.1104
597.1094 | 122.9919 | -0.30212 | 122.7905 | -0.0083178 | -0.0049936 | -0.00069228 | 0.022221 | -0.00062384 | 0.016988 | 0.0014498 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0049787 | -0.00086748 | -0.1592 | -0.081008 | -0.16407 | -0.021127 | -0.077483 | 0.10076 | -0.24621 | -0.099684 | 0.21098 | -0.22118 | 122.5409 | 122.8256 | 122.0779 | -0.3702 | 0.05591 | -122.8117 | 0.14293 | 0.13805 | 0.082143 | -122.868 | -122.6898 | -0.068072 | -0.24959 | 0.20244 | 0.080939 | 0.14901 | 0.035035 | -0.71265 | 0.281 | 0.22464 | 0.40288 | 0.22112 | -123.0367 | 122.8431 | 123.1277 | 122.38 | 0.5131 | -123.1607
598.7812 | 123.024 | -0.29755 | 122.8088 | 0.0069442 | -0.0045662 | -0.00090608 | 0.022648 | -0.00062384 | 0.017416 | 0.0014498 | 0.00025649 | 0.0012435 | 8.5404e-05 | 0.0049787 | -0.00086748 | -0.15462 | -0.071851 | -0.15034 | -0.016548 | -0.063746 | 0.09618 | -0.24163 | -0.099684 | 0.19724 | -0.20745 | 122.5364 | 122.8393 | 122.0916 | -0.3702 | 0.055911 | -122.8254 | 0.14293 | 0.14721 | 0.091299 | -122.8726 | -122.7127 | -0.07265 | -0.27248 | 0.19786 | 0.090097 | 0.16275 | 0.03046 | -0.71723 | 0.281 | 0.2338 | 0.39373 | 0.22569 | -123.0505 | 122.8339 | 123.1368 | 122.3892 | 0.49479 | -123.179
600.5156 | 123.0515 | -0.3067 | 122.7448 | -0.0083178 | -0.0043526 | -0.0011197 | 0.022007 | -0.00083764 | 0.017629 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0054059 | -0.0010811 | -0.19124 | -0.10848 | -0.18238 | -0.044018 | -0.054588 | 0.06413 | -0.27369 | -0.12716 | 0.2064 | -0.24866 | 122.5089 | 122.7935 | 122.055 | -0.40225 | 0.033014 | -122.7888 | 0.11546 | 0.12432 | 0.091304 | -122.7993 | -122.6806 | -0.095545 | -0.23586 | 0.17955 | 0.058045 | 0.15359 | 0.048761 | -0.68977 | 0.26268 | 0.25211 | 0.37083 | 0.19822 | -123.0184 | 122.8156 | 123.1002 | 122.3617 | 0.5131 | -123.147
602.2656 | 123.1567 | -0.27008 | 122.7264 | -0.00068679 | -0.0037114 | -0.00090608 | 0.021794 | -0.00083764 | 0.018057 | 0.0014498 | 0.00089729 | 0.0012435 | 0.0002992 | 0.0051923 | -0.00086748 | -0.18667 | -0.1039 | -0.17323 | -0.044018 | -0.050009 | 0.073287 | -0.25995 | -0.118 | 0.19724 | -0.2395 | 122.518 | 122.8027 | 122.0596 | -0.38851 | 0.01013 | -122.7705 | 0.083415 | 0.096854 | 0.086724 | -122.7764 | -122.6532 | -0.11843 | -0.20839 | 0.15208 | 0.030582 | 0.14901 | 0.076229 | -0.66688 | 0.22606 | 0.22007 | 0.34337 | 0.16618 | -122.9864 | 122.7881 | 123.0727 | 122.3296 | 0.46732 | -123.115
603.9375 | 123.0148 | -0.3891 | 122.6898 | -0.00068679 | -0.0041388 | -0.0011197 | 0.021794 | -0.0010512 | 0.017202 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0051923 | -0.0010811 | -0.22329 | -0.14053 | -0.22817 | -0.076067 | -0.04543 | -0.013707 | -0.29658 | -0.15921 | 0.20182 | -0.27155 | 122.4768 | 122.766 | 122.0138 | -0.42972 | 0.092517 | -122.7659 | 0.16581 | 0.16093 | 0.068415 | -122.7352 | -122.7035 | -0.040621 | -0.21298 | 0.22989 | 0.11755 | 0.15817 | 0.076221 | -0.67605 | 0.31303 | 0.34367 | 0.37539 | 0.24857 | -122.9864 | 122.8659 | 123.1551 | 122.4029 | 0.59092 | -123.1195
605.6094 | 123.1247 | -0.30212 | 122.6944 | -0.0083178 | -0.0037114 | -0.0013333 | 0.021794 | -0.00083764 | 0.017843 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0051923 | -0.0010811 | -0.23703 | -0.14511 | -0.23275 | -0.076067 | -0.040851 | -0.022864 | -0.30116 | -0.16379 | 0.21098 | -0.28071 | 122.4677 | 122.7615 | 122.087 | -0.42972 | 0.000963 | -122.7705 | 0.065095 | 0.069379 | 0.068416 | -122.7352 | -122.7173 | -0.1276 | -0.22671 | 0.13834 | 0.021416 | 0.14901 | 0.067064 | -0.60737 | 0.22606 | 0.26127 | 0.27926 | 0.15702 | -122.9956 | 122.7698 | 123.0636 | 122.3892 | 0.5131 | -123.1241
607.375 | 123.056 | -0.40283 | 122.6578 | -0.0083178 | -0.0032842 | -0.0015471 | 0.02158 | -0.0014786 | 0.017416 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0051923 | -0.00086748 | -0.27823 | -0.18632 | -0.27853 | -0.11269 | -0.027115 | -0.054914 | -0.33779 | -0.20042 | 0.2064 | -0.31276 | 122.4356 | 122.7203 | 122.0138 | -0.47551 | 0.065039 | -122.7705 | 0.1246 | 0.1243 | 0.059265 | -122.6849 | -122.7127 | -0.072676 | -0.22214 | 0.20242 | 0.090073 | 0.16275 | 0.062478 | -0.644 | 0.29014 | 0.37572 | 0.34792 | 0.21652 | -122.9956 | 122.8385 | 123.1231 | 122.4166 | 0.60923 | -123.1333
609.1094 | 123.0972 | -0.34332 | 122.6669 | -0.00068679 | -0.0032842 | -0.0013333 | 0.02158 | -0.0012648 | 0.017629 | -0.0061807 | 0.00089729 | 0.0010299 | 0.0005128 | 0.0049787 | -0.00086748 | -0.26908 | -0.17716 | -0.26937 | -0.098959 | -0.027115 | -0.064071 | -0.32864 | -0.19126 | 0.2064 | -0.31276 | 122.4402 | 122.734 | 121.9863 | -0.46635 | 0.014688 | -122.7659 | 0.074246 | 0.073952 | 0.059264 | -122.694 | -122.731 | -0.12303 | -0.22672 | 0.15206 | 0.030564 | 0.15359 | 0.067059 | -0.68063 | 0.24436 | 0.31621 | 0.27925 | 0.16616 | -122.9956 | 122.7835 | 123.0773 | 122.3296 | 0.54972 | -123.1333
610.875 | 123.0286 | -0.38452 | 122.6898 | 0.0069442 | -0.0037114 | -0.00090608 | 0.02158 | -0.0010512 | 0.016988 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00086748 | -0.26908 | -0.17716 | -0.26479 | -0.10354 | -0.036272 | -0.059493 | -0.33779 | -0.18668 | 0.21098 | -0.31276 | 122.4311 | 122.7294 | 121.9771 | -0.48009 | 0.046728 | -122.7934 | 0.11544 | 0.11973 | 0.073 | -122.7261 | -122.7493 | -0.095566 | -0.25876 | 0.19784 | 0.071762 | 0.16733 | 0.039592 | -0.71268 | 0.28098 | 0.34825 | 0.32503 | 0.20736 | -123.0276 | 122.8156 | 123.1139 | 122.3617 | 0.5955 | -123.1699
612.5625 | 123.1293 | -0.37537 | 122.6166 | -0.0083178 | -0.0037114 | -0.0013333 | 0.021366 | -0.0010512 | 0.017416 | 0.0014498 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0054059 | -0.0010811 | -0.27823 | -0.1909 | -0.27853 | -0.11727 | -0.017957 | -0.054914 | -0.35153 | -0.22331 | 0.2064 | -0.34481 | 122.4082 | 122.6974 | 121.9543 | -0.49382 | 0.023836 | -122.7339 | 0.097132 | 0.096838 | 0.073002 | -122.6345 | -122.6715 | -0.11846 | -0.20841 | 0.15206 | 0.030556 | 0.14901 | 0.080784 | -0.66233 | 0.25809 | 0.35741 | 0.32045 | 0.18447 | -122.9681 | 122.7835 | 123.0727 | 122.3296 | 0.58177 | -123.1104
614.2969 | 123.0148 | -0.43488 | 122.6395 | -0.00068679 | -0.0034978 | -0.0013333 | 0.021152 | -0.00083764 | 0.017202 | 0.0014498 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.0010811 | -0.3286 | -0.23668 | -0.31515 | -0.1539 | -0.008799 | -0.0366 | -0.39732 | -0.25994 | 0.21098 | -0.38144 | 122.3624 | 122.6562 | 121.9955 | -0.54877 | 0.037556 | -122.7934 | 0.10628 | 0.11972 | 0.082165 | -122.6483 | -122.6761 | -0.11389 | -0.27709 | 0.17494 | 0.053436 | 0.16733 | 0.016689 | -0.64401 | 0.28097 | 0.42608 | 0.39827 | 0.19819 | -123.0368 | 122.7973 | 123.091 | 122.4303 | 0.64586 | -123.1882
616.0312 | 123.1155 | -0.47607 | 122.5433 | -0.0083178 | -0.0032842 | -0.0011197 | 0.021152 | -0.0012648 | 0.017629 | -0.0061807 | 0.00025649 | 0.0012435 | 0.0005128 | 0.0054059 | -0.00086748 | -0.37896 | -0.28704 | -0.36551 | -0.19968 | -0.11411 | -0.018285 | -0.44769 | -0.30573 | 0.21098 | -0.44096 | 122.3029 | 122.6104 | 121.8993 | -0.58998 | 0.028387 | -122.743 | 0.097115 | 0.11056 | 0.082172 | -122.6574 | -122.5616 | -0.11391 | -0.24048 | 0.17035 | 0.035111 | 0.14902 | 0.067033 | -0.64403 | 0.27639 | 0.36196 | 0.45779 | 0.18903 | -122.991 | 122.7789 | 123.0864 | 122.3754 | 0.68705 | -123.1333
617.7812 | 123.0881 | -0.5127 | 122.4884 | 0.0069442 | -0.0026432 | -0.0015471 | 0.021366 | -0.0010512 | 0.017629 | -0.0061807 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0051923 | -0.0012947 | -0.43848 | -0.33283 | -0.42046 | -0.25005 | -0.19196 | -0.013707 | -0.49806 | -0.36525 | 0.19724 | -0.49591 | 122.2571 | 122.5554 | 121.913 | -0.64492 | 0.01464 | -122.7384 | 0.074217 | 0.09224 | 0.0776 | -122.6804 | -122.5021 | -0.13223 | -0.23133 | 0.14745 | 0.016788 | 0.14902 | 0.067021 | -0.57536 | 0.26265 | 0.32074 | 0.49899 | 0.17986 | -122.9865 | 122.7698 | 123.0681 | 122.4257 | 0.70994 | -123.1333
619.5156 | 123.1064 | -0.55847 | 122.4472 | -0.00068679 | -0.0026432 | -0.0019745 | 0.021366 | -0.0012648 | 0.017416 | 0.0090803 | 0.00025649 | 0.0012435 | 8.5404e-05 | 0.0051923 | -0.0010811 | -0.46595 | -0.3603 | -0.45708 | -0.28209 | -0.21485 | -0.050335 | -0.53011 | -0.38814 | 0.21556 | -0.51422 | 122.2388 | 122.528 | 121.7803 | -0.6724 | 0.028364 | -122.7293 | 0.092524 | 0.10139 | 0.073027 | -122.6621 | -122.4975 | -0.11393 | -0.20844 | 0.17033 | 0.04425 | 0.15818 | 0.080748 | -0.66694 | 0.27638 | 0.34362 | 0.50814 | 0.19817 | -122.9773 | 122.7972 | 123.0864 | 122.3387 | 0.77403 | -123.1196
621.2656 | 123.1338 | -0.60425 | 122.406 | 0.0069442 | -0.0020022 | -0.0021881 | 0.020725 | -0.0012648 | 0.017416 | 0.0090803 | 0.00025649 | 0.0012435 | 0.0005128 | 0.0051923 | -0.00086748 | -0.51173 | -0.41067 | -0.48455 | -0.31872 | -0.2469 | -0.13275 | -0.5759 | -0.42477 | 0.21098 | -0.56459 | 122.1838 | 122.4822 | 121.7345 | -0.71819 | 0.028351 | -122.7247 | 0.092516 | 0.1197 | 0.091346 | -122.6529 | -122.5388 | -0.11394 | -0.22219 | 0.17948 | 0.03966 | 0.1536 | 0.076161 | -0.67153 | 0.28553 | 0.35735 | 0.4715 | 0.19358 | -122.9819 | 122.7881 | 123.0864 | 122.3387 | 0.81523 | -123.1242
622.9531 | 123.0286 | -0.62714 | 122.4472 | 0.0069442 | -0.0024294 | -0.0015471 | 0.021152 | -0.0012648 | 0.017629 | 0.016711 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0054059 | -0.00065368 | -0.46595 | -0.37404 | -0.4525 | -0.27294 | -0.22401 | -0.06865 | -0.54842 | -0.40188 | 0.19724 | -0.53712 | 122.2159 | 122.5188 | 122 | -0.69071 | 0.078713 | -122.7201 | 0.16119 | 0.17463 | 0.09592 | -122.6712 | -122.5159 | -0.063577 | -0.23134 | 0.22526 | 0.09002 | 0.1536 | 0.07159 | -0.44717 | 0.3542 | 0.40313 | 0.55849 | 0.2531 | -122.9956 | 122.843 | 123.1459 | 122.6272 | 0.82438 | -123.1379
624.6875 | 123.0469 | -0.65002 | 122.4197 | -0.00068679 | -0.0020022 | -0.0019745 | 0.021366 | -0.00062384 | 0.017416 | -0.0061807 | 0.00089729 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00065368 | -0.51173 | -0.41525 | -0.49828 | -0.32788 | -0.26064 | -0.1648 | -0.58963 | -0.43851 | 0.2064 | -0.57832 | 122.1792 | 122.4684 | 121.7436 | -0.72734 | 0.06039 | -122.7476 | 0.13829 | 0.15174 | 0.091349 | -122.6804 | -122.5845 | -0.077319 | -0.2405 | 0.21152 | 0.0717 | 0.14902 | 0.048692 | -0.67611 | 0.32215 | 0.38938 | 0.48522 | 0.23478 | -123.0094 | 122.8293 | 123.1185 | 122.3937 | 0.85642 | -123.1471
626.4219 | 123.0103 | -0.67749 | 122.4014 | 0.014575 | -0.001361 | -0.0021881 | 0.020725 | -0.0014786 | 0.017416 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0054059 | -0.00086748 | -0.54378 | -0.4244 | -0.51202 | -0.34619 | -0.27896 | -0.21059 | -0.59879 | -0.4614 | 0.20182 | -0.59206 | 122.1563 | 122.4501 | 121.7116 | -0.74566 | 0.078699 | -122.7476 | 0.13371 | 0.16547 | 0.086771 | -122.6804 | -122.612 | -0.068169 | -0.24508 | 0.21609 | 0.08543 | 0.1536 | 0.048688 | -0.68984 | 0.3313 | 0.39854 | 0.4669 | 0.25309 | -123.0002 | 122.8338 | 123.1276 | 122.3891 | 0.87931 | -123.1471
628.1094 | 123.1064 | -0.64087 | 122.3785 | -0.00068679 | -0.0011474 | -0.0019745 | 0.020725 | -0.0010512 | 0.017629 | -0.0061807 | 0.00068369 | 0.00060248 | 8.5404e-05 | 0.0051923 | -0.00044008 | -0.54378 | -0.43356 | -0.5166 | -0.34619 | -0.28353 | -0.20143 | -0.61711 | -0.46598 | 0.21098 | -0.59206 | 122.1609 | 122.4455 | 121.7848 | -0.75024 | 0.023762 | -122.7247 | 0.097088 | 0.12427 | 0.10051 | -122.6621 | -122.58 | -0.10937 | -0.21761 | 0.17489 | 0.048809 | 0.15818 | 0.066998 | -0.5937 | 0.29468 | 0.35734 | 0.43944 | 0.20731 | -122.9956 | 122.8018 | 123.0864 | 122.4257 | 0.85185 | -123.1288
629.8594 | 123.1338 | -0.68207 | 122.3373 | -0.015949 | -0.00093379 | -0.0021881 | 0.020511 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0007264 | 0.0054059 | -0.00086748 | -0.6033 | -0.4885 | -0.58527 | -0.40571 | -0.31101 | -0.26553 | -0.6629 | -0.51635 | 0.21098 | -0.65158 | 122.0968 | 122.3814 | 121.6292 | -0.80518 | 0.019172 | -122.7431 | 0.078768 | 0.096795 | 0.077623 | -122.6483 | -122.6029 | -0.12311 | -0.24052 | 0.16572 | 0.030485 | 0.1536 | 0.044096 | -0.70817 | 0.27636 | 0.37106 | 0.41654 | 0.19356 | -123.0002 | 122.7789 | 123.0635 | 122.3112 | 0.89305 | -123.1425
631.5312 | 123.0927 | -0.68207 | 122.3511 | 0.0069442 | -0.00050639 | -0.0021881 | 0.020084 | -0.00062384 | 0.017629 | 0.0014498 | 0.00068369 | 0.0014571 | 0.0005128 | 0.0051923 | -0.00086748 | -0.56667 | -0.47019 | -0.55322 | -0.38282 | -0.29269 | -0.23806 | -0.63084 | -0.48887 | 0.21556 | -0.62411 | 122.1151 | 122.4135 | 121.7894 | -0.77771 | 0.051224 | -122.7339 | 0.1154 | 0.12884 | 0.077619 | -122.6438 | -122.5891 | -0.095642 | -0.23593 | 0.19319 | 0.057957 | 0.1536 | 0.062414 | -0.56165 | 0.29925 | 0.38938 | 0.44401 | 0.21188 | -122.9819 | 122.7972 | 123.0956 | 122.4715 | 0.89763 | -123.1288
633.2656 | 123.1293 | -0.65918 | 122.3557 | -0.015949 | -7.8988e-05 | -0.0026155 | 0.01987 | -0.00083764 | 0.017416 | -0.0061807 | 0.00089729 | 0.0012435 | 8.5404e-05 | 0.0051923 | -0.00086748 | -0.58041 | -0.46103 | -0.54865 | -0.37366 | -0.29269 | -0.25179 | -0.64 | -0.49803 | 0.21098 | -0.61953 | 122.1197 | 122.4089 | 121.8718 | -0.78229 | 0.019178 | -122.7293 | 0.078772 | 0.11053 | 0.091356 | -122.6483 | -122.6074 | -0.12311 | -0.23593 | 0.16115 | 0.039648 | 0.16276 | 0.053257 | -0.48382 | 0.28552 | 0.36649 | 0.40739 | 0.19815 | -122.9957 | 122.7789 | 123.0681 | 122.531 | 0.87016 | -123.1379
635 | 123.0148 | -0.81482 | 122.2778 | -0.00068679 | 0.00056201 | -0.0024017 | 0.019657 | -0.0012648 | 0.017202 | 0.0014498 | 0.00047009 | 0.0014571 | 8.5404e-05 | 0.0054059 | -0.00086748 | -0.68113 | -0.57092 | -0.64937 | -0.47439 | -0.37511 | -0.34337 | -0.73616 | -0.59418 | 0.21098 | -0.734 | 122.0236 | 122.3128 | 121.6658 | -0.88302 | 0.07866 | -122.7522 | 0.13369 | 0.16545 | 0.08679 | -122.6529 | -122.6212 | -0.068204 | -0.25426 | 0.22063 | 0.080819 | 0.14902 | 0.034926 | -0.61203 | 0.34043 | 0.43971 | 0.47145 | 0.2439 | -123.014 | 122.8384 | 123.1276 | 122.4806 | 1.0258 | -123.1609
636.7344 | 123.143 | -0.73242 | 122.2321 | -0.0083178 | 0.00056201 | -0.0026155 | 0.019443 | -0.0012648 | 0.017202 | -0.0061807 | 0.00025649 | 0.00081608 | 0.0005128 | 0.0051923 | -0.0010811 | -0.64908 | -0.53887 | -0.61732 | -0.44692 | -0.35222 | -0.31589 | -0.70411 | -0.55756 | 0.2064 | -0.70195 | 122.0465 | 122.3448 | 121.6475 | -0.84639 | 0.028315 | -122.679 | 0.083338 | 0.1151 | 0.086786 | -122.5843 | -122.548 | -0.11397 | -0.18559 | 0.17487 | 0.030473 | 0.14444 | 0.11275 | -0.58457 | 0.28551 | 0.3802 | 0.41653 | 0.19355 | -122.9362 | 122.7789 | 123.0772 | 122.3799 | 0.93882 | -123.0784
638.4062 | 123.0927 | -0.75989 | 122.2641 | -0.0083178 | 0.001203 | -0.0030429 | 0.019229 | -0.0012648 | 0.017416 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0054059 | -0.00086748 | -0.67655 | -0.5526 | -0.65395 | -0.46065 | -0.37511 | -0.34337 | -0.71784 | -0.57587 | 0.21556 | -0.71569 | 122.0327 | 122.3265 | 121.5834 | -0.86929 | 0.042045 | -122.7248 | 0.083334 | 0.10594 | 0.063896 | -122.6392 | -122.6075 | -0.1094 | -0.23137 | 0.18402 | 0.044203 | 0.1536 | 0.062395 | -0.68072 | 0.29924 | 0.38478 | 0.41652 | 0.20728 | -122.9819 | 122.7926 | 123.0864 | 122.3433 | 0.97545 | -123.1334
640.125 | 123.056 | -0.86517 | 122.2092 | 0.0069442 | 0.001844 | -0.0030429 | 0.018588 | -0.0012648 | 0.016988 | 0.016711 | 0.00068369 | 0.0012435 | -0.0001282 | 0.0051923 | -0.0010811 | -0.75439 | -0.6396 | -0.7272 | -0.53391 | -0.43006 | -0.41204 | -0.80942 | -0.63997 | 0.21098 | -0.78895 | 121.9503 | 122.2487 | 121.5055 | -0.94713 | 0.055751 | -122.7431 | 0.11079 | 0.13797 | 0.082223 | -122.6392 | -122.6212 | -0.081954 | -0.25885 | 0.2252 | 0.076228 | 0.15818 | 0.039491 | -0.70362 | 0.33127 | 0.43511 | 0.45313 | 0.22557 | -123.0186 | 122.8155 | 123.1138 | 122.3707 | 1.0762 | -123.1563
641.875 | 123.0606 | -0.91095 | 122.1176 | 0.0069442 | 0.0014166 | -0.0030429 | 0.018802 | -0.0010512 | 0.017202 | 0.0014498 | 0.00068369 | 0.0014571 | 0.0002992 | 0.0051923 | -0.0010811 | -0.79101 | -0.6808 | -0.77298 | -0.58427 | -0.47585 | -0.44867 | -0.85063 | -0.69492 | 0.21556 | -0.83931 | 121.9091 | 122.1983 | 121.5422 | -0.99291 | 0.060318 | -122.7019 | 0.11994 | 0.13797 | 0.07765 | -122.5935 | -122.5663 | -0.081965 | -0.20851 | 0.21603 | 0.07164 | 0.1536 | 0.080678 | -0.57544 | 0.32668 | 0.4351 | 0.46228 | 0.23015 | -122.9682 | 122.8201 | 123.1092 | 122.4531 | 1.1265 | -123.1105
643.5781 | 123.0835 | -0.89264 | 122.1268 | -0.015949 | 0.0022714 | -0.0032565 | 0.018375 | -0.0010512 | 0.017202 | -0.0061807 | 0.00025649 | 0.0014571 | 0.0002992 | 0.0054059 | -0.00065368 | -0.79101 | -0.67165 | -0.77298 | -0.57511 | -0.46211 | -0.44867 | -0.83232 | -0.68576 | 0.2064 | -0.83931 | 121.9183 | 122.2074 | 121.4643 | -0.98376 | 0.060322 | -122.7019 | 0.10162 | 0.11966 | 0.059335 | -122.5889 | -122.5754 | -0.091118 | -0.2085 | 0.20688 | 0.053329 | 0.14445 | 0.08068 | -0.66243 | 0.31753 | 0.43053 | 0.44396 | 0.22099 | -122.9591 | 122.8109 | 123.1001 | 122.357 | 1.099 | -123.1105
645.3281 | 123.1293 | -0.83771 | 122.1634 | -0.0083178 | 0.001844 | -0.0030429 | 0.018588 | -0.00062384 | 0.017629 | 0.0014498 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0054059 | -0.00086748 | -0.75897 | -0.64875 | -0.73636 | -0.53848 | -0.4438 | -0.4212 | -0.80942 | -0.65371 | 0.21098 | -0.7981 | 121.9503 | 122.2441 | 121.501 | -0.95171 | 0.028286 | -122.7019 | 0.078743 | 0.10135 | 0.073066 | -122.6072 | -122.5846 | -0.114 | -0.21308 | 0.184 | 0.039606 | 0.1536 | 0.080688 | -0.66242 | 0.29922 | 0.39391 | 0.41651 | 0.18895 | -122.9728 | 122.788 | 123.0818 | 122.3387 | 1.0487 | -123.1151
647.2812 | 123.143 | -0.82855 | 122.1405 | -0.00068679 | 0.001844 | -0.0028291 | 0.018588 | -0.0010512 | 0.017416 | 0.0090803 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0049787 | -0.0010811 | -0.75897 | -0.64418 | -0.73636 | -0.54764 | -0.43006 | -0.41662 | -0.80484 | -0.65829 | 0.21098 | -0.80268 | 121.9457 | 122.2441 | 121.4918 | -0.96086 | 0.023709 | -122.6881 | 0.069587 | 0.092196 | 0.068487 | -122.5706 | -122.5571 | -0.13231 | -0.19477 | 0.17026 | 0.025871 | 0.15818 | 0.10358 | -0.64869 | 0.28091 | 0.39849 | 0.41193 | 0.18438 | -122.9453 | 122.7743 | 123.0726 | 122.3204 | 1.0395 | -123.1014
649.0156 | 123.0103 | -0.86975 | 122.2183 | -0.0083178 | 0.0022714 | -0.0032565 | 0.018588 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0047649 | -0.00086748 | -0.75897 | -0.6396 | -0.75009 | -0.55222 | -0.43922 | -0.42578 | -0.814 | -0.65829 | 0.22014 | -0.80726 | 121.9457 | 122.2395 | 121.5925 | -0.96086 | 0.05575 | -122.7705 | 0.11079 | 0.11966 | 0.06391 | -122.6575 | -122.6441 | -0.091112 | -0.27259 | 0.21146 | 0.062491 | 0.1536 | 0.021178 | -0.62578 | 0.31753 | 0.43053 | 0.44397 | 0.23015 | -123.0323 | 122.8155 | 123.1093 | 122.4623 | 1.0899 | -123.1792
650.6875 | 123.056 | -0.87891 | 122.1725 | -0.00068679 | 0.002485 | -0.0036839 | 0.018588 | -0.0010512 | 0.017202 | 0.0090803 | 0.00089729 | 0.0012435 | 0.0005128 | 0.0051923 | -0.00086748 | -0.79101 | -0.67165 | -0.78214 | -0.57969 | -0.47127 | -0.45783 | -0.84605 | -0.6766 | 0.22014 | -0.83473 | 121.9091 | 122.2074 | 121.4689 | -0.98834 | 0.032853 | -122.7522 | 0.087892 | 0.096767 | 0.063914 | -122.6438 | -122.6304 | -0.10943 | -0.26344 | 0.2023 | 0.044174 | 0.1536 | 0.034904 | -0.70363 | 0.29922 | 0.40764 | 0.42107 | 0.20726 | -123.0186 | 122.788 | 123.0864 | 122.3478 | 1.099 | -123.1609
652.4375 | 123.056 | -0.87891 | 122.1771 | 0.0069442 | 0.0022714 | -0.0038975 | 0.018588 | -0.00062384 | 0.017629 | 0.0090803 | 0.0011109 | 0.0010299 | 0.0005128 | 0.0054059 | -0.00086748 | -0.79559 | -0.66249 | -0.7684 | -0.58427 | -0.47127 | -0.45325 | -0.84147 | -0.68576 | 0.21556 | -0.82557 | 121.9228 | 122.212 | 121.5651 | -0.97918 | 0.037432 | -122.7614 | 0.083314 | 0.1105 | 0.07307 | -122.6484 | -122.6304 | -0.10027 | -0.25428 | 0.19315 | 0.053332 | 0.1536 | 0.034905 | -0.61206 | 0.29464 | 0.40764 | 0.42565 | 0.21641 | -123.0186 | 122.8017 | 123.0909 | 122.444 | 1.0945 | -123.1563
654.1719 | 123.0148 | -0.91553 | 122.1588 | 0.0069442 | 0.0029124 | -0.0036839 | 0.018802 | -0.00062384 | 0.017416 | 0.0090803 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0056197 | -0.00065368 | -0.78643 | -0.67165 | -0.77298 | -0.57969 | -0.46211 | -0.4441 | -0.8369 | -0.68118 | 0.21098 | -0.83015 | 121.9137 | 122.2166 | 121.4781 | -0.98376 | 0.078631 | -122.7385 | 0.12909 | 0.14255 | 0.063914 | -122.6209 | -122.6029 | -0.06823 | -0.24513 | 0.23435 | 0.085374 | 0.1536 | 0.057795 | -0.68074 | 0.33584 | 0.45341 | 0.47143 | 0.24388 | -122.9957 | 122.8292 | 123.1321 | 122.3936 | 1.1265 | -123.1426
655.875 | 123.0652 | -0.90637 | 122.1359 | -0.00068679 | 0.003126 | -0.0043249 | 0.018588 | -0.00083764 | 0.017416 | 0.0014498 | 0.00089729 | 0.0014571 | 8.5404e-05 | 0.0056197 | -0.0010811 | -0.81391 | -0.6808 | -0.78672 | -0.60258 | -0.48959 | -0.47157 | -0.85979 | -0.70407 | 0.21556 | -0.85762 | 121.9045 | 122.1983 | 121.4414 | -1.0067 | 0.046582 | -122.7385 | 0.092466 | 0.11965 | 0.073073 | -122.6255 | -122.6075 | -0.10028 | -0.2314 | 0.2023 | 0.048747 | 0.14903 | 0.062368 | -0.69448 | 0.30379 | 0.41679 | 0.4348 | 0.22557 | -122.9957 | 122.8109 | 123.1047 | 122.3478 | 1.1219 | -123.1426
657.625 | 123.0698 | -0.91095 | 122.1313 | -0.00068679 | 0.003126 | -0.0041111 | 0.018802 | -0.00083764 | 0.017629 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0054059 | -0.0010811 | -0.80475 | -0.67623 | -0.7684 | -0.58427 | -0.48959 | -0.45783 | -0.85521 | -0.69949 | 0.22014 | -0.85305 | 121.9 | 122.2029 | 121.4552 | -0.99749 | 0.055739 | -122.7156 | 0.1062 | 0.14255 | 0.086807 | -122.6209 | -122.5892 | -0.086543 | -0.2314 | 0.21146 | 0.057903 | 0.14445 | 0.071524 | -0.67617 | 0.32668 | 0.42136 | 0.45312 | 0.23472 | -122.9866 | 122.8109 | 123.1138 | 122.3661 | 1.1311 | -123.1288
659.375 | 123.0972 | -0.90637 | 122.0901 | -0.015949 | 0.002485 | -0.0036839 | 0.018588 | -0.0010512 | 0.017416 | -0.013811 | 0.00068369 | 0.0012435 | 8.5404e-05 | 0.0054059 | -0.00065368 | -0.84595 | -0.70828 | -0.81876 | -0.62089 | -0.52164 | -0.49446 | -0.89184 | -0.74528 | 0.21556 | -0.88968 | 121.8587 | 122.1571 | 121.4277 | -1.0387 | 0.014529 | -122.711 | 0.060418 | 0.087607 | 0.073078 | -122.6118 | -122.5846 | -0.13233 | -0.2314 | 0.16109 | 0.016696 | 0.14903 | 0.066937 | -0.66244 | 0.28548 | 0.38473 | 0.41191 | 0.19809 | -122.982 | 122.7651 | 123.0635 | 122.3341 | 1.1219 | -123.1289
661.1094 | 122.9965 | -1.0849 | 122.0032 | -0.00068679 | 0.001844 | -0.0036839 | 0.019016 | -0.0010512 | 0.016988 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.0012947 | -0.94668 | -0.80901 | -0.92407 | -0.7262 | -0.62238 | -0.58603 | -0.99716 | -0.83228 | 0.22014 | -0.99041 | 121.758 | 122.0564 | 121.3087 | -1.144 | 0.087742 | -122.7294 | 0.13822 | 0.16083 | 0.073093 | -122.6255 | -122.5892 | -0.059116 | -0.24516 | 0.25262 | 0.094492 | 0.15361 | 0.053183 | -0.69451 | 0.3587 | 0.46252 | 0.49887 | 0.27589 | -123.0003 | 122.8429 | 123.1413 | 122.3936 | 1.305 | -123.1472
662.8125 | 123.1201 | -1.0208 | 121.9574 | -0.0083178 | 0.0022714 | -0.0034701 | 0.018588 | -0.0012648 | 0.017202 | -0.0061807 | 0.00068369 | 0.0014571 | 0.0005128 | 0.0054059 | -0.0010811 | -0.96957 | -0.84106 | -0.94238 | -0.75367 | -0.64069 | -0.61808 | -1.0292 | -0.86891 | 0.21556 | -1.0133 | 121.7305 | 122.0289 | 121.2858 | -1.1623 | -0.008397 | -122.7111 | 0.051242 | 0.078434 | 0.086831 | -122.5981 | -122.5755 | -0.14152 | -0.22685 | 0.15191 | 0.007512 | 0.14903 | 0.071488 | -0.67162 | 0.26714 | 0.38012 | 0.40273 | 0.17976 | -122.9866 | 122.7514 | 123.0497 | 122.3066 | 1.2364 | -123.1197
664.6094 | 123.1155 | -1.0757 | 121.9391 | -0.015949 | 0.0022714 | -0.0034701 | 0.018802 | -0.0010512 | 0.017202 | -0.0061807 | 0.00047009 | 0.0012435 | 0.0002992 | 0.0051923 | -0.00065368 | -1.0062 | -0.86395 | -0.97901 | -0.78572 | -0.67732 | -0.65013 | -1.0475 | -0.89638 | 0.21098 | -1.0408 | 121.7031 | 122.0014 | 121.3819 | -1.1898 | 0.028219 | -122.7248 | 0.069547 | 0.09674 | 0.068521 | -122.6164 | -122.5892 | -0.11406 | -0.23601 | 0.17936 | 0.034971 | 0.14903 | 0.062326 | -0.55716 | 0.29003 | 0.39842 | 0.42561 | 0.2118 | -122.9866 | 122.7788 | 123.0772 | 122.4577 | 1.2867 | -123.1289
666.375 | 123.1293 | -1.0529 | 121.9345 | 0.0069442 | 0.002485 | -0.0032565 | 0.018375 | -0.00083764 | 0.017202 | -0.013811 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0056197 | -0.00086748 | -0.99246 | -0.85479 | -0.96527 | -0.77656 | -0.66816 | -0.6364 | -1.0521 | -0.88722 | 0.21098 | -1.0408 | 121.7168 | 122.0014 | 121.3819 | -1.1898 | 0.000751 | -122.7111 | 0.060393 | 0.087586 | 0.086835 | -122.6027 | -122.5709 | -0.13695 | -0.2177 | 0.16563 | 0.012082 | 0.14903 | 0.066904 | -0.55258 | 0.2763 | 0.38469 | 0.41646 | 0.19806 | -122.9866 | 122.7697 | 123.0543 | 122.4348 | 1.2638 | -123.1243
668.0625 | 123.0148 | -1.1536 | 121.9299 | -0.0083178 | 0.0026988 | -0.0036839 | 0.018375 | -0.00062384 | 0.016988 | 0.0014498 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0054059 | -0.0012947 | -1.0337 | -0.896 | -1.0202 | -0.82234 | -0.71853 | -0.68676 | -1.0979 | -0.94217 | 0.21098 | -1.0866 | 121.6619 | 121.9602 | 121.2904 | -1.2356 | 0.05567 | -122.7523 | 0.1199 | 0.13336 | 0.077685 | -122.6485 | -122.6167 | -0.082028 | -0.26806 | 0.2114 | 0.067003 | 0.14903 | 0.030274 | -0.63958 | 0.33122 | 0.43503 | 0.4668 | 0.25756 | -123.0278 | 122.8154 | 123.1138 | 122.4439 | 1.3645 | -123.1655
669.75 | 123.0743 | -1.1536 | 121.8933 | -0.00068679 | 0.0029124 | -0.0036839 | 0.018161 | -0.0012648 | 0.017416 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0051923 | -0.0015083 | -1.0474 | -0.90516 | -1.0202 | -0.8315 | -0.72311 | -0.69134 | -1.0979 | -0.94217 | 0.21556 | -1.0957 | 121.6573 | 121.9556 | 121.24 | -1.231 | 0.05567 | -122.7248 | 0.10616 | 0.13336 | 0.077685 | -122.6164 | -122.5847 | -0.077449 | -0.23602 | 0.2114 | 0.057846 | 0.13529 | 0.062316 | -0.65332 | 0.32206 | 0.43045 | 0.46222 | 0.24841 | -122.9912 | 122.8109 | 123.1092 | 122.3936 | 1.3691 | -123.1243
671.4375 | 123.0743 | -1.1719 | 121.9116 | -0.00068679 | 0.0035534 | -0.0041111 | 0.017734 | -0.00083764 | 0.016988 | -0.0061807 | 0.00025649 | 0.0010299 | 8.5404e-05 | 0.0054059 | -0.00086748 | -1.0611 | -0.90516 | -1.0385 | -0.84066 | -0.73227 | -0.7005 | -1.1162 | -0.96506 | 0.22014 | -1.1049 | 121.639 | 121.9373 | 121.2171 | -1.2493 | 0.055665 | -122.7523 | 0.11074 | 0.13335 | 0.077687 | -122.6439 | -122.6121 | -0.077453 | -0.27264 | 0.20681 | 0.066999 | 0.14445 | 0.025692 | -0.69453 | 0.33122 | 0.43961 | 0.47138 | 0.26672 | -123.0278 | 122.8109 | 123.1092 | 122.389 | 1.392 | -123.1609
673.125 | 123.1567 | -1.1536 | 121.8842 | -0.00068679 | 0.004408 | -0.0041111 | 0.017306 | -0.0010512 | 0.016988 | -0.0061807 | 0.00047009 | 0.0012435 | 8.5404e-05 | 0.0054059 | -0.0010811 | -1.0978 | -0.94179 | -1.0706 | -0.88186 | -0.76432 | -0.73713 | -1.1437 | -1.0017 | 0.21556 | -1.1323 | 121.6023 | 121.9053 | 121.1759 | -1.2814 | 0.009881 | -122.766 | 0.055798 | 0.082994 | 0.073113 | -122.6485 | -122.6213 | -0.12782 | -0.28181 | 0.15187 | 0.021216 | 0.14903 | 0.021108 | -0.70827 | 0.2717 | 0.38924 | 0.41644 | 0.21178 | -123.0278 | 122.7559 | 123.0588 | 122.3295 | 1.3691 | -123.1655
674.8125 | 123.1064 | -1.1673 | 121.8613 | 0.0069442 | 0.004408 | -0.0038975 | 0.016879 | -0.00083764 | 0.017843 | -0.013811 | 0.00089729 | 0.0010299 | 0.0002992 | 0.0056197 | -0.00086748 | -1.084 | -0.91889 | -1.0568 | -0.85897 | -0.75516 | -0.71881 | -1.1254 | -0.9788 | 0.21556 | -1.1323 | 121.6207 | 121.919 | 121.24 | -1.2676 | 0.041929 | -122.7202 | 0.083267 | 0.11046 | 0.068532 | -122.6164 | -122.5801 | -0.10035 | -0.2406 | 0.1885 | 0.034949 | 0.1353 | 0.057732 | -0.62128 | 0.30833 | 0.41213 | 0.44849 | 0.2484 | -122.9866 | 122.788 | 123.0863 | 122.4073 | 1.3829 | -123.1289
676.5781 | 123.056 | -1.2039 | 121.8796 | 0.014575 | 0.0041944 | -0.0036839 | 0.016879 | -0.00083764 | 0.017416 | -0.013811 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.00065368 | -1.0611 | -0.90973 | -1.0477 | -0.85897 | -0.75058 | -0.71881 | -1.1299 | -0.96964 | 0.22472 | -1.1278 | 121.6298 | 121.919 | 121.2217 | -1.2676 | 0.073971 | -122.7385 | 0.14278 | 0.15624 | 0.082268 | -122.6302 | -122.5984 | -0.063726 | -0.24976 | 0.23428 | 0.076149 | 0.13987 | 0.039421 | -0.6579 | 0.34495 | 0.45333 | 0.48511 | 0.29418 | -123.0095 | 122.8337 | 123.1229 | 122.4256 | 1.4286 | -123.1472
678.2812 | 123.0011 | -1.1169 | 121.962 | -0.00068679 | 0.0039808 | -0.0036839 | 0.016879 | -0.00083764 | 0.016988 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0054059 | -0.00086748 | -1.0566 | -0.89142 | -1.0294 | -0.84066 | -0.73227 | -0.70965 | -1.1254 | -0.96506 | 0.22472 | -1.1095 | 121.639 | 121.9282 | 121.2812 | -1.2585 | -0.008425 | -122.8026 | 0.060383 | 0.087577 | 0.096002 | -122.6942 | -122.6716 | -0.14154 | -0.323 | 0.15188 | 0.007489 | 0.14903 | -0.033819 | -0.68078 | 0.27629 | 0.38467 | 0.40729 | 0.22552 | -123.0873 | 122.7559 | 123.0451 | 122.3981 | 1.3417 | -123.2205
679.9844 | 122.9782 | -1.2405 | 121.843 | -0.00068679 | 0.0039808 | -0.0036839 | 0.017093 | -0.0012648 | 0.017202 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0005128 | 0.0056197 | -0.0010811 | -1.139 | -0.97841 | -1.1209 | -0.93223 | -0.81927 | -0.78749 | -1.1986 | -1.0521 | 0.22014 | -1.1965 | 121.5566 | 121.8503 | 121.1942 | -1.3363 | 0.041909 | -122.7752 | 0.10157 | 0.11961 | 0.077699 | -122.6622 | -122.6304 | -0.095786 | -0.28639 | 0.18848 | 0.04409 | 0.13988 | 0.007363 | -0.64875 | 0.30831 | 0.42127 | 0.45305 | 0.26213 | -123.0416 | 122.7971 | 123.0909 | 122.4347 | 1.4607 | -123.1793
681.6875 | 123.0789 | -1.2039 | 121.843 | -0.00068679 | 0.0039808 | -0.0041111 | 0.017093 | -0.0010512 | 0.017202 | 0.0090803 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0054059 | -0.00086748 | -1.1207 | -0.9601 | -1.098 | -0.90018 | -0.80095 | -0.77375 | -1.1895 | -1.0383 | 0.22014 | -1.1781 | 121.5703 | 121.8595 | 121.1209 | -1.3272 | 0.014445 | -122.7431 | 0.083261 | 0.10588 | 0.091433 | -122.6439 | -122.6167 | -0.12325 | -0.27266 | 0.1656 | 0.025783 | 0.14903 | 0.01652 | -0.72201 | 0.30374 | 0.40297 | 0.43016 | 0.24382 | -123.0324 | 122.7742 | 123.0634 | 122.3249 | 1.4241 | -123.1701
683.3906 | 123.1522 | -1.0895 | 121.8979 | -0.00068679 | 0.0035534 | -0.0036839 | 0.017306 | -0.00083764 | 0.017202 | -0.0061807 | 0.00068369 | 0.0010299 | -0.0001282 | 0.0051923 | -0.0010811 | -1.0016 | -0.84106 | -0.97901 | -0.78572 | -0.67732 | -0.65013 | -1.0796 | -0.93301 | 0.22929 | -1.0728 | 121.671 | 121.9648 | 121.2812 | -1.2219 | 0.009899 | -122.6836 | 0.087859 | 0.11047 | 0.10057 | -122.5752 | -122.548 | -0.13238 | -0.22686 | 0.15647 | 0.016653 | 0.14903 | 0.066897 | -0.61669 | 0.30376 | 0.41216 | 0.43935 | 0.24842 | -122.9775 | 122.7605 | 123.0543 | 122.3707 | 1.3188 | -123.1197
685.0781 | 123.0789 | -1.149 | 121.8933 | 0.0069442 | 0.003767 | -0.0032565 | 0.017093 | -0.00062384 | 0.017416 | -0.0061807 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.0010811 | -1.0291 | -0.87769 | -1.0019 | -0.82234 | -0.70937 | -0.68218 | -1.1071 | -0.95132 | 0.21556 | -1.1049 | 121.6481 | 121.9419 | 121.3545 | -1.2539 | 0.041935 | -122.7157 | 0.1199 | 0.14709 | 0.10516 | -122.6027 | -122.5755 | -0.10492 | -0.24518 | 0.19766 | 0.044111 | 0.14903 | 0.048581 | -0.53886 | 0.32664 | 0.43961 | 0.46681 | 0.2713 | -123.0004 | 122.7971 | 123.0909 | 122.5034 | 1.3645 | -123.1472
686.7656 | 123.111 | -1.1719 | 121.8475 | -0.00068679 | 0.003767 | -0.0034701 | 0.01752 | -0.0010512 | 0.017202 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0005128 | 0.0054059 | -0.00086748 | -1.0428 | -0.87311 | -1.0111 | -0.82234 | -0.71853 | -0.68218 | -1.1208 | -0.96964 | 0.22014 | -1.1186 | 121.6436 | 121.9236 | 121.2812 | -1.2631 | 0.051086 | -122.6699 | 0.12905 | 0.16082 | 0.10974 | -122.5661 | -122.5297 | -0.09119 | -0.20398 | 0.20224 | 0.053263 | 0.14445 | 0.076043 | -0.56634 | 0.34953 | 0.45334 | 0.48969 | 0.29877 | -122.9683 | 122.8154 | 123.0955 | 122.4531 | 1.392 | -123.1106
688.4531 | 123.143 | -1.1719 | 121.8384 | -0.00068679 | 0.003767 | -0.0032565 | 0.017947 | -0.00062384 | 0.017416 | -0.013811 | 0.00025649 | 0.0014571 | 0.0002992 | 0.0056197 | -0.0010811 | -1.0749 | -0.90973 | -1.0568 | -0.85897 | -0.75516 | -0.72339 | -1.162 | -1.0108 | 0.22014 | -1.1552 | 121.5886 | 121.8915 | 121.2995 | -1.3043 | 0.009876 | -122.6974 | 0.097001 | 0.11504 | 0.10516 | -122.5935 | -122.5618 | -0.1324 | -0.24977 | 0.16103 | 0.016634 | 0.14903 | 0.053148 | -0.53887 | 0.3129 | 0.41671 | 0.44849 | 0.26214 | -123.0004 | 122.7605 | 123.0634 | 122.4714 | 1.392 | -123.1427
690.1406 | 123.0057 | -1.2451 | 121.8338 | -0.0083178 | 0.002485 | -0.0034701 | 0.018161 | -0.0010512 | 0.017629 | 0.0014498 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0051923 | -0.00086748 | -1.0703 | -0.91431 | -1.0523 | -0.86355 | -0.75516 | -0.72797 | -1.1757 | -1.02 | 0.22929 | -1.1644 | 121.5795 | 121.8824 | 121.3957 | -1.3226 | 0.069381 | -122.6974 | 0.17482 | 0.19286 | 0.12348 | -122.589 | -122.5618 | -0.077473 | -0.25435 | 0.22511 | 0.080718 | 0.15819 | 0.048569 | -0.43814 | 0.38157 | 0.48995 | 0.51715 | 0.3308 | -123.0095 | 122.8246 | 123.1275 | 122.6408 | 1.4744 | -123.1564
691.8281 | 123.1476 | -1.2177 | 121.8292 | 0.0069442 | 0.0022714 | -0.0032565 | 0.018375 | -0.0010512 | 0.016775 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0051923 | -0.00086748 | -1.0886 | -0.90973 | -1.066 | -0.87271 | -0.75974 | -0.73255 | -1.1895 | -1.0337 | 0.22014 | -1.1827 | 121.5657 | 121.8732 | 121.2629 | -1.3317 | 0.028178 | -122.7019 | 0.12904 | 0.15166 | 0.12348 | -122.589 | -122.5618 | -0.1141 | -0.2635 | 0.18391 | 0.034937 | 0.14903 | 0.043989 | -0.56634 | 0.34494 | 0.45791 | 0.4851 | 0.30792 | -123.0187 | 122.7834 | 123.0909 | 122.4805 | 1.4378 | -123.161
693.5469 | 123.143 | -1.2039 | 121.788 | -0.00068679 | 0.0022714 | -0.0036839 | 0.018802 | -0.0010512 | 0.017202 | 0.0014498 | 0.00089729 | 0.0014571 | 8.5404e-05 | 0.0054059 | -0.00086748 | -1.0886 | -0.896 | -1.0614 | -0.86813 | -0.75516 | -0.72339 | -1.1941 | -1.0383 | 0.22472 | -1.1781 | 121.5703 | 121.8595 | 121.24 | -1.3317 | 0.009866 | -122.6562 | 0.11531 | 0.1425 | 0.13264 | -122.5432 | -122.5114 | -0.12783 | -0.21773 | 0.1656 | 0.025783 | 0.15361 | 0.071452 | -0.54804 | 0.33579 | 0.44875 | 0.48053 | 0.30792 | -122.9821 | 122.7742 | 123.0634 | 122.4439 | 1.4286 | -123.1198
695.2188 | 123.0515 | -1.2772 | 121.8063 | -0.00068679 | 0.0020576 | -0.0036839 | 0.018588 | -0.0010512 | 0.017416 | -0.0061807 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0056197 | -0.0010811 | -1.1115 | -0.93263 | -1.0889 | -0.90018 | -0.80095 | -0.7646 | -1.2353 | -1.0658 | 0.22014 | -1.2239 | 121.5383 | 121.8228 | 121.1026 | -1.3638 | 0.041899 | -122.7065 | 0.16566 | 0.18828 | 0.14638 | -122.6073 | -122.5709 | -0.086638 | -0.26808 | 0.21137 | 0.053239 | 0.13988 | 0.016513 | -0.7037 | 0.37698 | 0.47621 | 0.51256 | 0.34453 | -123.0416 | 122.8154 | 123.1 | 122.3798 | 1.4973 | -123.1701
696.8906 | 123.0286 | -1.2772 | 121.7972 | -0.00068679 | 0.001844 | -0.0032565 | 0.019443 | -0.0010512 | 0.017416 | 0.0090803 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0054059 | -0.00065368 | -1.0886 | -0.89142 | -1.0523 | -0.86813 | -0.75058 | -0.72797 | -1.2078 | -1.0521 | 0.22472 | -1.2056 | 121.5428 | 121.8366 | 121.1118 | -1.3409 | 0.069373 | -122.6653 | 0.18855 | 0.2249 | 0.15553 | -122.5478 | -122.5251 | -0.063744 | -0.25435 | 0.2251 | 0.071554 | 0.1353 | 0.039404 | -0.68539 | 0.40903 | 0.52658 | 0.54919 | 0.38574 | -123.005 | 122.82 | 123.1137 | 122.3889 | 1.5019 | -123.1381
698.625 | 123.111 | -1.2863 | 121.7285 | -0.00068679 | 0.0020576 | -0.0032565 | 0.018802 | -0.0010512 | 0.017416 | -0.0061807 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0054059 | -0.00086748 | -1.1207 | -0.94179 | -1.098 | -0.90018 | -0.78722 | -0.7646 | -1.249 | -1.1024 | 0.21098 | -1.2468 | 121.5108 | 121.7908 | 121.1667 | -1.3821 | 0.037317 | -122.6287 | 0.16566 | 0.18828 | 0.15096 | -122.5157 | -122.4931 | -0.095798 | -0.21774 | 0.18389 | 0.0395 | 0.1353 | 0.062282 | -0.56179 | 0.38614 | 0.4991 | 0.52172 | 0.34453 | -122.9775 | 122.7971 | 123.0771 | 122.453 | 1.4973 | -123.1106
700.3281 | 123.024 | -1.3641 | 121.6965 | -0.0083178 | 0.001844 | -0.0034701 | 0.019016 | -0.0012648 | 0.016988 | 0.0014498 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0056197 | -0.0015083 | -1.1664 | -0.98757 | -1.1484 | -0.94596 | -0.84674 | -0.81496 | -1.2902 | -1.1528 | 0.22472 | -1.2972 | 121.4558 | 121.7359 | 121.0156 | -1.4416 | 0.073927 | -122.6424 | 0.19769 | 0.21574 | 0.14181 | -122.5432 | -122.5114 | -0.077503 | -0.24063 | 0.21135 | 0.066955 | 0.14446 | 0.039382 | -0.68084 | 0.41817 | 0.51739 | 0.54917 | 0.37656 | -122.9867 | 122.82 | 123.1 | 122.3798 | 1.5889 | -123.1381
702 | 123.1338 | -1.2772 | 121.6919 | -0.00068679 | 0.001203 | -0.0030429 | 0.018802 | -0.00083764 | 0.017416 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.0012947 | -1.1252 | -0.94179 | -1.098 | -0.90018 | -0.80095 | -0.7646 | -1.2627 | -1.1116 | 0.22472 | -1.2606 | 121.497 | 121.7816 | 121.1347 | -1.4096 | 0.014425 | -122.5921 | 0.15193 | 0.17912 | 0.1647 | -122.4928 | -122.4565 | -0.13243 | -0.19485 | 0.16558 | 0.016609 | 0.14904 | 0.089745 | -0.55721 | 0.37698 | 0.47621 | 0.51256 | 0.33537 | -122.9546 | 122.7742 | 123.0588 | 122.4118 | 1.5019 | -123.1015
703.7031 | 123.0606 | -1.3046 | 121.7377 | -0.00068679 | 0.001203 | -0.0030429 | 0.019016 | -0.0010512 | 0.017202 | 0.0090803 | 0.00047009 | 0.00081608 | 8.5404e-05 | 0.0054059 | -0.0010811 | -1.1252 | -0.94179 | -1.1026 | -0.90018 | -0.80553 | -0.7646 | -1.2673 | -1.1253 | 0.22929 | -1.2651 | 121.4879 | 121.7771 | 121.0477 | -1.4142 | 0.037312 | -122.6378 | 0.17939 | 0.20201 | 0.1647 | -122.5432 | -122.5023 | -0.10954 | -0.24979 | 0.17931 | 0.039496 | 0.14904 | 0.039391 | -0.68998 | 0.40445 | 0.49909 | 0.54003 | 0.36284 | -123.005 | 122.7925 | 123.0817 | 122.3523 | 1.5339 | -123.1518
705.4219 | 123.0286 | -1.3962 | 121.6965 | 0.014575 | 0.00098941 | -0.0030429 | 0.019657 | -0.0010512 | 0.017202 | -0.0061807 | 0.00068369 | 0.0014571 | 8.5404e-05 | 0.0056197 | -0.0010811 | -1.1252 | -0.95094 | -1.098 | -0.90475 | -0.79637 | -0.75544 | -1.3039 | -1.1574 | 0.23387 | -1.2972 | 121.4513 | 121.745 | 121.1713 | -1.4462 | 0.092233 | -122.6012 | 0.27094 | 0.29814 | 0.20591 | -122.4928 | -122.4519 | -0.050039 | -0.24521 | 0.23881 | 0.098998 | 0.14904 | 0.04854 | -0.52516 | 0.49142 | 0.59981 | 0.64074 | 0.44524 | -123.0004 | 122.8474 | 123.1412 | 122.5675 | 1.6301 | -123.1427
707.1094 | 123.0972 | -1.3138 | 121.6553 | -0.00068679 | 0.00056201 | -0.0024017 | 0.020084 | -0.00083764 | 0.017416 | 0.0014498 | 0.00025649 | 0.0014571 | 0.0002992 | 0.0054059 | -0.00086748 | -1.0932 | -0.92805 | -1.066 | -0.86813 | -0.75516 | -0.72339 | -1.2994 | -1.1436 | 0.22014 | -1.2972 | 121.4558 | 121.7496 | 121.0431 | -1.4371 | 0.014415 | -122.5234 | 0.2206 | 0.24779 | 0.23337 | -122.4104 | -122.3787 | -0.12328 | -0.19944 | 0.17015 | 0.016601 | 0.13988 | 0.094317 | -0.61216 | 0.44565 | 0.55862 | 0.59039 | 0.38573 | -122.9546 | 122.7696 | 123.0634 | 122.3569 | 1.5339 | -123.0923
708.8125 | 123.0194 | -1.4053 | 121.6919 | -0.00068679 | -0.0024294 | -0.0024017 | 0.022007 | -0.00083764 | 0.016988 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0002992 | 0.0051923 | -0.00086748 | -1.0016 | -0.91431 | -0.97901 | -0.76282 | -0.65901 | -0.6364 | -1.3726 | -1.2215 | 0.22929 | -1.3521 | 121.3917 | 121.6809 | 120.9332 | -1.5012 | 0.032704 | -122.4547 | 0.40372 | 0.42633 | 0.39363 | -122.3509 | -122.3283 | -0.095829 | -0.30016 | 0.18387 | 0.053208 | 0.14904 | -0.010984 | -0.75867 | 0.64251 | 0.74633 | 0.76894 | 0.49102 | -123.0645 | 122.7971 | 123.0862 | 122.3386 | 1.6346 | -123.1931
710.5156 | 123.0743 | -1.4145 | 121.669 | -0.0083178 | -0.0017884 | -0.0024017 | 0.022221 | -0.00062384 | 0.016988 | 0.016711 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0056197 | -0.0010811 | -1.0245 | -0.91889 | -0.98358 | -0.78572 | -0.68648 | -0.65471 | -1.3681 | -1.2215 | 0.22929 | -1.3613 | 121.3872 | 121.6718 | 121.0111 | -1.5103 | 0.046439 | -122.4547 | 0.38998 | 0.43091 | 0.38447 | -122.3555 | -122.3237 | -0.095831 | -0.28185 | 0.19302 | 0.053207 | 0.14904 | 0.002748 | -0.65795 | 0.62877 | 0.72801 | 0.75978 | 0.4956 | -123.0371 | 122.8016 | 123.0862 | 122.4255 | 1.6438 | -123.1793
712.2188 | 123.0103 | -1.4465 | 121.6415 | -0.00068679 | -0.0022158 | -0.0019745 | 0.022221 | -0.00062384 | 0.017416 | 0.0090803 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0056197 | -0.00086748 | -1.0337 | -0.93721 | -0.99274 | -0.7903 | -0.68648 | -0.66387 | -1.3909 | -1.2444 | 0.22014 | -1.3888 | 121.3643 | 121.6534 | 120.9195 | -1.5332 | 0.055588 | -122.4318 | 0.41287 | 0.45379 | 0.39821 | -122.328 | -122.3054 | -0.086682 | -0.27727 | 0.20217 | 0.057777 | 0.14446 | 0.011899 | -0.72205 | 0.65624 | 0.76005 | 0.78267 | 0.50933 | -123.0325 | 122.8108 | 123.1 | 122.366 | 1.6667 | -123.1748
713.8906 | 123.0606 | -1.4603 | 121.5958 | -0.00068679 | -0.0022158 | -0.0021881 | 0.022007 | -0.00062384 | 0.016775 | -0.0061807 | 0.00089729 | 0.00081608 | 0.0002992 | 0.0056197 | -0.0010811 | -1.0382 | -0.93721 | -0.99732 | -0.79945 | -0.69564 | -0.66387 | -1.4138 | -1.2489 | 0.22929 | -1.3979 | 121.3551 | 121.6351 | 121.0889 | -1.547 | 0.046426 | -122.3952 | 0.42202 | 0.46295 | 0.41652 | -122.2914 | -122.2596 | -0.086686 | -0.24065 | 0.21133 | 0.062353 | 0.14904 | 0.039361 | -0.50687 | 0.66081 | 0.76463 | 0.7964 | 0.52306 | -123.0096 | 122.8154 | 123.0954 | 122.5492 | 1.6896 | -123.1427
715.5938 | 123.1064 | -1.4511 | 121.5729 | 0.0069442 | -0.0017884 | -0.0021881 | 0.022221 | -0.00062384 | 0.017202 | 0.0090803 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.00086748 | -1.0337 | -0.92805 | -0.99732 | -0.79487 | -0.67732 | -0.65471 | -1.4138 | -1.2627 | 0.22929 | -1.4116 | 121.3505 | 121.6397 | 120.9653 | -1.5515 | 0.037271 | -122.3677 | 0.41744 | 0.45379 | 0.41652 | -122.2502 | -122.2276 | -0.10042 | -0.22234 | 0.18844 | 0.039462 | 0.13988 | 0.066828 | -0.6076 | 0.65624 | 0.77379 | 0.7964 | 0.52306 | -122.9867 | 122.8016 | 123.0908 | 122.4164 | 1.6804 | -123.1244
717.2812 | 123.1659 | -1.4328 | 121.5637 | 0.014575 | -0.0017884 | -0.0021881 | 0.021794 | -0.00062384 | 0.016988 | 0.0090803 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0058333 | -0.00086748 | -1.0245 | -0.90973 | -0.98358 | -0.77656 | -0.67732 | -0.64097 | -1.4138 | -1.2673 | 0.23387 | -1.4116 | 121.3505 | 121.6305 | 120.892 | -1.5561 | 0.01896 | -122.3403 | 0.40829 | 0.44922 | 0.43026 | -122.241 | -122.2047 | -0.12331 | -0.21319 | 0.16555 | 0.021151 | 0.14446 | 0.066826 | -0.67171 | 0.65624 | 0.75548 | 0.79183 | 0.52307 | -122.9776 | 122.7833 | 123.0633 | 122.3248 | 1.6667 | -123.1198
718.9531 | 123.1064 | -1.4099 | 121.6141 | -0.00068679 | -0.0024294 | -0.0019745 | 0.021794 | -0.00062384 | 0.016775 | 0.0014498 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0058333 | -0.00086748 | -0.99704 | -0.87311 | -0.96069 | -0.75367 | -0.64985 | -0.62266 | -1.3864 | -1.2444 | 0.23387 | -1.3888 | 121.3688 | 121.6534 | 120.9882 | -1.5378 | 0.023546 | -122.3677 | 0.41287 | 0.44922 | 0.42567 | -122.2639 | -122.2367 | -0.12788 | -0.24523 | 0.16555 | 0.021156 | 0.14904 | 0.039365 | -0.62591 | 0.65624 | 0.76006 | 0.78725 | 0.53681 | -123.0004 | 122.7788 | 123.0634 | 122.3981 | 1.6438 | -123.1519
720.6406 | 123.1384 | -1.4374 | 121.5408 | -0.0083178 | -0.0026432 | -0.0024017 | 0.022007 | -0.00019664 | 0.016988 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0054059 | -0.00086748 | -0.99246 | -0.87311 | -0.96527 | -0.74451 | -0.64985 | -0.62266 | -1.4184 | -1.2581 | 0.22929 | -1.4071 | 121.346 | 121.6305 | 120.9103 | -1.5515 | 0.018959 | -122.2853 | 0.44492 | 0.47211 | 0.45315 | -122.1907 | -122.1635 | -0.11415 | -0.19488 | 0.17928 | 0.030307 | 0.14446 | 0.089714 | -0.6305 | 0.69287 | 0.78753 | 0.81472 | 0.56427 | -122.9593 | 122.7833 | 123.0679 | 122.3477 | 1.6667 | -123.0924
722.3125 | 123.0606 | -1.4603 | 121.5958 | -0.0083178 | -0.0026432 | -0.0021881 | 0.022007 | -0.00062384 | 0.016988 | 0.0014498 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.0010811 | -1.0016 | -0.87769 | -0.95611 | -0.75825 | -0.64985 | -0.6135 | -1.4276 | -1.281 | 0.22929 | -1.43 | 121.3276 | 121.6214 | 120.9699 | -1.5698 | 0.032689 | -122.354 | 0.45865 | 0.50415 | 0.47146 | -122.2456 | -122.2093 | -0.10958 | -0.26812 | 0.17928 | 0.030302 | 0.13988 | 0.025625 | -0.62591 | 0.70202 | 0.81042 | 0.84676 | 0.58258 | -123.0233 | 122.7879 | 123.0817 | 122.4301 | 1.6896 | -123.1656
724.0156 | 123.0286 | -1.4786 | 121.5546 | 0.0069442 | -0.0026432 | -0.0017607 | 0.022221 | -0.00041024 | 0.016775 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0005128 | 0.0056197 | -0.0010811 | -0.96041 | -0.82732 | -0.92407 | -0.72162 | -0.61322 | -0.58603 | -1.4138 | -1.2581 | 0.22929 | -1.4116 | 121.346 | 121.6351 | 121.0385 | -1.5515 | 0.064737 | -122.2762 | 0.51816 | 0.55451 | 0.48977 | -122.1678 | -122.1406 | -0.072953 | -0.20861 | 0.22048 | 0.066928 | 0.13988 | 0.08056 | -0.51604 | 0.75696 | 0.86536 | 0.89255 | 0.65126 | -122.9684 | 122.8245 | 123.1137 | 122.5171 | 1.7079 | -123.1061
725.6875 | 123.0835 | -1.4923 | 121.5271 | -0.00068679 | -0.0026432 | -0.0017607 | 0.021794 | -0.00062384 | 0.016775 | 0.016711 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0054059 | -0.0010811 | -1.0062 | -0.86853 | -0.97443 | -0.75825 | -0.65901 | -0.62724 | -1.4688 | -1.3268 | 0.22929 | -1.4712 | 121.2819 | 121.5756 | 120.8371 | -1.6202 | 0.023523 | -122.2853 | 0.48611 | 0.51788 | 0.49436 | -122.1861 | -122.1543 | -0.1279 | -0.24525 | 0.16553 | 0.021138 | 0.14904 | 0.048503 | -0.69003 | 0.73406 | 0.8333 | 0.86507 | 0.62378 | -122.9959 | 122.7742 | 123.0679 | 122.3294 | 1.7216 | -123.1473
727.3594 | 123.1201 | -1.4557 | 121.5637 | 0.0069442 | -0.0024294 | -0.0017607 | 0.021794 | -0.00062384 | 0.016988 | 0.0090803 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0058333 | -0.0010811 | -0.97873 | -0.82274 | -0.94696 | -0.72162 | -0.62238 | -0.59061 | -1.4367 | -1.2993 | 0.23387 | -1.4391 | 121.3185 | 121.6031 | 120.979 | -1.5973 | 0.018953 | -122.2853 | 0.47696 | 0.50873 | 0.48978 | -122.1861 | -122.1543 | -0.14163 | -0.24524 | 0.15638 | 0.016567 | 0.1582 | 0.039354 | -0.58471 | 0.73407 | 0.83331 | 0.86508 | 0.63295 | -123.0005 | 122.7742 | 123.0588 | 122.4347 | 1.6896 | -123.161
729.0312 | 123.0972 | -1.6113 | 121.3989 | -0.00068679 | -0.0024294 | -0.0019745 | 0.022221 | -0.00019664 | 0.016988 | 0.0090803 | 0.00047009 | 0.0016709 | 0.0005128 | 0.0056197 | -0.00086748 | -1.0611 | -0.91431 | -1.0202 | -0.79945 | -0.69564 | -0.66845 | -1.5375 | -1.3863 | 0.23387 | -1.5399 | 121.2132 | 121.5023 | 120.7867 | -1.6843 | 0.073857 | -122.1984 | 0.55019 | 0.59112 | 0.51726 | -122.0946 | -122.0674 | -0.072988 | -0.18575 | 0.22503 | 0.071475 | 0.14446 | 0.10342 | -0.61222 | 0.81188 | 0.91569 | 0.94288 | 0.69701 | -122.9364 | 122.8245 | 123.1137 | 122.398 | 1.8452 | -123.0832
730.75 | 123.0606 | -1.5244 | 121.5088 | -0.00068679 | -0.0028568 | -0.0015471 | 0.021794 | -0.00062384 | 0.016561 | 0.0090803 | 0.00089729 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.0012947 | -1.0016 | -0.82732 | -0.95154 | -0.75367 | -0.64069 | -0.60893 | -1.4825 | -1.3359 | 0.23387 | -1.4803 | 121.2727 | 121.5619 | 120.8417 | -1.6294 | 0.041829 | -122.2625 | 0.52273 | 0.57282 | 0.53099 | -122.1495 | -122.1177 | -0.10502 | -0.23609 | 0.18842 | 0.044023 | 0.14904 | 0.053079 | -0.66714 | 0.77068 | 0.88366 | 0.91543 | 0.69703 | -122.9913 | 122.797 | 123.0862 | 122.366 | 1.7582 | -123.1382
732.4062 | 123.1293 | -1.4557 | 121.5271 | -0.0083178 | -0.0026432 | -0.0013333 | 0.02158 | -0.00062384 | 0.016988 | 0.0090803 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.0010811 | -0.97873 | -0.78611 | -0.93322 | -0.71704 | -0.60864 | -0.57688 | -1.4596 | -1.3085 | 0.22472 | -1.462 | 121.2956 | 121.5802 | 120.8417 | -1.6065 | -0.003941 | -122.2441 | 0.47696 | 0.52247 | 0.52641 | -122.1357 | -122.104 | -0.15079 | -0.23151 | 0.14723 | -0.006327 | 0.14446 | 0.053082 | -0.68545 | 0.73865 | 0.84705 | 0.87881 | 0.66958 | -122.9867 | 122.7513 | 123.0359 | 122.2973 | 1.6804 | -123.1336
734.0781 | 123.1338 | -1.6251 | 121.3806 | -0.0083178 | -0.0024294 | -0.0015471 | 0.021152 | -0.00062384 | 0.016775 | -0.0061807 | 0.00089729 | 0.0012435 | 8.5404e-05 | 0.0051923 | -0.0010811 | -1.1069 | -0.92805 | -1.0614 | -0.84066 | -0.74143 | -0.71423 | -1.6107 | -1.4641 | 0.22472 | -1.6131 | 121.1445 | 121.4337 | 120.8279 | -1.753 | 0.014327 | -122.2213 | 0.51814 | 0.56365 | 0.54932 | -122.122 | -122.0948 | -0.12794 | -0.23612 | 0.16092 | 0.011949 | 0.13989 | 0.053052 | -0.5527 | 0.7844 | 0.88363 | 0.91083 | 0.69701 | -122.9913 | 122.7696 | 123.0587 | 122.453 | 1.8498 | -123.1336
735.7344 | 123.1338 | -1.6342 | 121.3394 | -0.0083178 | -0.0022158 | -0.0015471 | 0.02158 | -0.00041024 | 0.016775 | 0.0090803 | 0.00068369 | 0.0014571 | 8.5404e-05 | 0.0056197 | -0.00086748 | -1.0245 | -0.84106 | -0.97443 | -0.75825 | -0.65443 | -0.62266 | -1.5558 | -1.4092 | 0.22929 | -1.5536 | 121.1994 | 121.484 | 120.7867 | -1.6981 | 0.078429 | -122.0977 | 0.6097 | 0.65979 | 0.58136 | -121.9938 | -121.9621 | -0.063837 | -0.13998 | 0.22502 | 0.080627 | 0.14446 | 0.14461 | -0.55271 | 0.87597 | 0.97979 | 1.0116 | 0.79316 | -122.8952 | 122.8337 | 123.1182 | 122.4209 | 1.8635 | -123.0375
737.4219 | 122.9965 | -1.712 | 121.376 | -0.0083178 | -0.0024294 | -0.0015471 | 0.02158 | -0.00062384 | 0.016775 | 0.0014498 | 0.00025649 | 0.0010299 | 0.0005128 | 0.0056197 | -0.0010811 | -1.0611 | -0.85021 | -1.0065 | -0.7903 | -0.69106 | -0.65471 | -1.629 | -1.4825 | 0.22929 | -1.636 | 121.1308 | 121.4108 | 120.6906 | -1.7713 | 0.082987 | -122.1663 | 0.6509 | 0.70556 | 0.62257 | -122.0671 | -122.0307 | -0.059278 | -0.24527 | 0.22958 | 0.07603 | 0.13531 | 0.034736 | -0.68548 | 0.92174 | 1.021 | 1.0573 | 0.86182 | -123.0051 | 122.8428 | 123.1228 | 122.4026 | 1.9413 | -123.1474
739.0938 | 123.0927 | -1.7029 | 121.2891 | -0.0083178 | -0.0015748 | -0.0015471 | 0.021152 | -0.00041024 | 0.016988 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0056197 | -0.00065368 | -1.1069 | -0.86853 | -1.0431 | -0.81777 | -0.71395 | -0.68676 | -1.6932 | -1.5374 | 0.22929 | -1.6864 | 121.0667 | 121.3604 | 120.6219 | -1.8263 | 0.009727 | -122.1068 | 0.59596 | 0.65978 | 0.65005 | -122.003 | -121.9758 | -0.12338 | -0.2224 | 0.16548 | 0.016509 | 0.13989 | 0.071347 | -0.66719 | 0.88512 | 0.98893 | 1.0161 | 0.83435 | -122.9822 | 122.7695 | 123.0633 | 122.3248 | 1.9322 | -123.1153
740.7656 | 123.0789 | -1.7715 | 121.2479 | -0.00068679 | -0.0015748 | -0.0017607 | 0.020511 | -0.00041024 | 0.016775 | 0.0014498 | 0.00068369 | 0.00081608 | 0.0002992 | 0.0058333 | -0.00086748 | -1.1207 | -0.85937 | -1.0614 | -0.82692 | -0.72311 | -0.69592 | -1.7206 | -1.574 | 0.22929 | -1.723 | 121.0346 | 121.3192 | 120.6219 | -1.8629 | 0.050917 | -122.0748 | 0.65089 | 0.71013 | 0.65921 | -121.971 | -121.9438 | -0.091345 | -0.21325 | 0.19752 | 0.048544 | 0.13989 | 0.071338 | -0.62599 | 0.94462 | 1.0484 | 1.0756 | 0.91217 | -122.9685 | 122.8062 | 123.0907 | 122.3934 | 2.0008 | -123.1108
742.4375 | 123.1338 | -1.8585 | 121.1151 | -0.0083178 | -0.0011474 | -0.00090608 | 0.019657 | -0.00083764 | 0.016561 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0056197 | -0.00044008 | -1.1252 | -0.8319 | -1.0614 | -0.84066 | -0.73227 | -0.70508 | -1.8488 | -1.6977 | 0.22929 | -1.8466 | 120.9064 | 121.2002 | 120.4983 | -1.9957 | 0.009683 | -121.9558 | 0.73329 | 0.79711 | 0.78742 | -121.8474 | -121.8202 | -0.13715 | -0.20869 | 0.16087 | 0.011894 | 0.14905 | 0.085046 | -0.61686 | 1.0179 | 1.1263 | 1.1534 | 1.0266 | -122.9639 | 122.7649 | 123.0587 | 122.3568 | 2.0878 | -123.1108
744.1094 | 123.0194 | -1.9684 | 121.1334 | -0.0083178 | -0.0011474 | -0.00090608 | 0.020298 | -0.00041024 | 0.016561 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0058333 | -0.0010811 | -1.1848 | -0.86395 | -1.1164 | -0.89102 | -0.78264 | -0.75544 | -1.9084 | -1.7618 | 0.23387 | -1.9107 | 120.8469 | 121.1269 | 120.4433 | -2.0506 | 0.06002 | -122.0244 | 0.78363 | 0.85203 | 0.79201 | -121.9161 | -121.8889 | -0.082237 | -0.28653 | 0.20663 | 0.057655 | 0.13989 | -0.006523 | -0.69011 | 1.0774 | 1.1857 | 1.2129 | 1.1044 | -123.0418 | 122.8153 | 123.0953 | 122.4117 | 2.2023 | -123.184
745.7969 | 123.0698 | -1.9958 | 121.0648 | 0.0069442 | -0.0011474 | -0.0015471 | 0.020511 | -0.00019664 | 0.016775 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0058333 | -0.0010811 | -1.2443 | -0.94636 | -1.1804 | -0.95512 | -0.84216 | -0.81496 | -1.945 | -1.7984 | 0.22929 | -1.9474 | 120.8103 | 121.104 | 120.3517 | -2.0964 | 0.050855 | -122.0199 | 0.75158 | 0.8154 | 0.76455 | -121.9069 | -121.8797 | -0.10056 | -0.25449 | 0.19747 | 0.048492 | 0.14905 | 0.039249 | -0.71302 | 1.0407 | 1.1537 | 1.1809 | 1.0495 | -123.0098 | 122.8061 | 123.0999 | 122.3476 | 2.2251 | -123.1612
747.5 | 123.0148 | -2.0187 | 121.0556 | -0.0083178 | -0.001361 | -0.0011197 | 0.020298 | -0.00041024 | 0.016561 | 0.0090803 | 0.00068369 | 0.0012435 | 0.0005128 | 0.0056197 | -0.00065368 | -1.2489 | -0.95094 | -1.1804 | -0.94596 | -0.83758 | -0.81038 | -1.945 | -1.7938 | 0.22929 | -1.9474 | 120.8148 | 121.104 | 120.4021 | -2.0873 | 0.073743 | -122.0016 | 0.76989 | 0.83829 | 0.76455 | -121.8932 | -121.866 | -0.068514 | -0.24076 | 0.22493 | 0.07138 | 0.13989 | 0.048404 | -0.6535 | 1.0728 | 1.1812 | 1.2084 | 1.0678 | -123.0006 | 122.8336 | 123.1227 | 122.4208 | 2.248 | -123.1429
749.1719 | 123.0606 | -1.9958 | 121.0373 | -0.00068679 | -0.00093379 | -0.0015471 | 0.020298 | -0.00041024 | 0.016561 | 0.0014498 | 0.00089729 | 0.00081608 | 0.0002992 | 0.0056197 | -0.00086748 | -1.258 | -0.96926 | -1.1759 | -0.95054 | -0.85132 | -0.8058 | -1.9908 | -1.8304 | 0.23387 | -1.9748 | 120.7782 | 121.0582 | 120.306 | -2.1193 | 0.005065 | -121.9878 | 0.73784 | 0.81998 | 0.81491 | -121.8886 | -121.8431 | -0.12345 | -0.25907 | 0.16541 | 0.021019 | 0.14447 | 0.020929 | -0.73134 | 1.0453 | 1.1445 | 1.19 | 1.0266 | -123.0281 | 122.7741 | 123.0541 | 122.3018 | 2.2297 | -123.1566
750.8594 | 123.056 | -2.0508 | 121.0281 | -0.0083178 | -0.0011474 | -0.0013333 | 0.020725 | -0.00062384 | 0.016775 | 0.0014498 | 0.00089729 | 0.0014571 | 0.0002992 | 0.0056197 | -0.00065368 | -1.2443 | -0.95094 | -1.1713 | -0.94138 | -0.82843 | -0.79665 | -2.0091 | -1.8488 | 0.22929 | -2.0115 | 120.7462 | 121.0399 | 120.5074 | -2.1468 | 0.041681 | -121.9695 | 0.80651 | 0.87949 | 0.83781 | -121.8566 | -121.8248 | -0.095996 | -0.28197 | 0.20203 | 0.039321 | 0.13532 | 0.01177 | -0.52072 | 1.1094 | 1.2224 | 1.2541 | 1.0998 | -123.0372 | 122.797 | 123.0907 | 122.5582 | 2.2801 | -123.1749
752.625 | 123.111 | -2.0737 | 120.9503 | -0.00068679 | -0.001361 | -0.0013333 | 0.020298 | -0.00019664 | 0.016347 | 0.0014498 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.00065368 | -1.2809 | -0.99215 | -1.2033 | -0.97343 | -0.87422 | -0.83786 | -2.0412 | -1.9037 | 0.22472 | -2.0527 | 120.7141 | 120.9895 | 120.2876 | -2.1788 | 0.032516 | -121.9237 | 0.79277 | 0.87033 | 0.83781 | -121.8245 | -121.7882 | -0.10516 | -0.2362 | 0.16997 | 0.021 | 0.12616 | 0.039225 | -0.66268 | 1.1002 | 1.1995 | 1.2358 | 1.0815 | -122.9915 | 122.7878 | 123.0632 | 122.3613 | 2.2984 | -123.1291
754.3281 | 123.1293 | -2.1973 | 120.7809 | -0.015949 | -0.0011474 | -0.0013333 | 0.020511 | 1.7156e-05 | 0.016561 | 0.0014498 | 0.00089729 | 0.0010299 | -0.0001282 | 0.0056197 | -0.0010811 | -1.3816 | -1.0929 | -1.3041 | -1.0558 | -0.95664 | -0.92485 | -2.1785 | -2.0365 | 0.23387 | -2.1855 | 120.5768 | 120.8705 | 120.1457 | -2.3208 | 0.018746 | -121.8368 | 0.81564 | 0.8932 | 0.87446 | -121.7376 | -121.7058 | -0.12351 | -0.20418 | 0.16079 | 0.011815 | 0.13532 | 0.089554 | -0.63524 | 1.1414 | 1.2406 | 1.2724 | 1.1044 | -122.9595 | 122.774 | 123.0678 | 122.343 | 2.4311 | -123.1017
756.0156 | 123.024 | -2.2476 | 120.8221 | -0.00068679 | -0.00093379 | -0.0015471 | 0.020511 | -0.00019664 | 0.016561 | -0.013811 | 0.00068369 | 0.0012435 | 0.0002992 | 0.0058333 | -0.0010811 | -1.3816 | -1.1066 | -1.2949 | -1.065 | -0.96122 | -0.92027 | -2.1785 | -2.0227 | 0.22929 | -2.1809 | 120.5768 | 120.8705 | 120.3288 | -2.3162 | 0.0691 | -121.8871 | 0.86599 | 0.95271 | 0.88361 | -121.7834 | -121.7424 | -0.068573 | -0.24538 | 0.22488 | 0.066748 | 0.13532 | 0.048355 | -0.4933 | 1.1826 | 1.2864 | 1.3274 | 1.141 | -123.0007 | 122.8244 | 123.1181 | 122.5765 | 2.4769 | -123.1383
757.75 | 123.1293 | -2.1332 | 120.8633 | -0.00068679 | -0.0011474 | -0.0013333 | 0.020725 | -0.00062384 | 0.016561 | -0.0061807 | 0.00068369 | 0.0010299 | -0.0001282 | 0.0058333 | -0.00065368 | -1.3084 | -1.0242 | -1.24 | -1.0009 | -0.88795 | -0.86075 | -2.0824 | -1.9312 | 0.23845 | -2.0847 | 120.6729 | 120.9621 | 120.2785 | -2.22 | 0.050816 | -121.8642 | 0.82481 | 0.89321 | 0.8424 | -121.7513 | -121.7241 | -0.086859 | -0.19043 | 0.20201 | 0.048459 | 0.13532 | 0.098729 | -0.58486 | 1.1323 | 1.2452 | 1.2724 | 1.109 | -122.9457 | 122.8061 | 123.0952 | 122.4117 | 2.3716 | -123.0834
759.4844 | 123.0469 | -2.2202 | 120.8267 | -0.0083178 | -0.00050639 | -0.0015471 | 0.020511 | -0.00041024 | 0.016561 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0058333 | -0.00086748 | -1.4045 | -1.1158 | -1.3178 | -1.0833 | -0.97953 | -0.94316 | -2.1831 | -2.0319 | 0.23845 | -2.1855 | 120.5813 | 120.8613 | 120.1503 | -2.3208 | 0.037055 | -121.91 | 0.81564 | 0.90236 | 0.8653 | -121.8063 | -121.7699 | -0.10062 | -0.24538 | 0.18825 | 0.034703 | 0.13532 | 0.03462 | -0.67644 | 1.1368 | 1.2406 | 1.277 | 1.1044 | -123.0098 | 122.8015 | 123.0815 | 122.3704 | 2.4586 | -123.1475
761.2188 | 123.0057 | -2.2156 | 120.8038 | -0.00068679 | -0.0011474 | -0.0019745 | 0.020725 | -0.00019664 | 0.016561 | 0.0014498 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0054059 | -0.0010811 | -1.3862 | -1.102 | -1.2995 | -1.065 | -0.94748 | -0.92485 | -2.1602 | -2.009 | 0.24303 | -2.1671 | 120.5997 | 120.8888 | 120.219 | -2.2979 | 0.055371 | -121.8688 | 0.82937 | 0.91609 | 0.86072 | -121.7513 | -121.7287 | -0.082302 | -0.20417 | 0.20657 | 0.04844 | 0.13074 | 0.08498 | -0.58487 | 1.1506 | 1.2681 | 1.2907 | 1.1135 | -122.964 | 122.8152 | 123.1044 | 122.4345 | 2.4586 | -123.1017
762.9375 | 123.0148 | -2.1423 | 120.9137 | -0.00068679 | -0.00093379 | -0.0013333 | 0.020511 | -0.00062384 | 0.016775 | -0.0061807 | 0.00047009 | 0.0010299 | 8.5404e-05 | 0.0056197 | -0.00086748 | -1.3404 | -1.0471 | -1.2629 | -1.0192 | -0.91085 | -0.88364 | -2.0869 | -1.9403 | 0.22929 | -2.103 | 120.6683 | 120.9575 | 120.219 | -2.2246 | 0.055392 | -121.9329 | 0.80191 | 0.87948 | 0.82408 | -121.8245 | -121.7973 | -0.082283 | -0.24536 | 0.20201 | 0.0393 | 0.12158 | 0.043796 | -0.69474 | 1.1231 | 1.2315 | 1.2587 | 1.0952 | -123.0006 | 122.8107 | 123.0998 | 122.3613 | 2.3716 | -123.1383
764.6562 | 123.0011 | -2.1927 | 120.8954 | -0.0083178 | -0.0011474 | -0.0017607 | 0.020725 | -0.00062384 | 0.016347 | 0.0014498 | 0.00068369 | 0.0010299 | 0.0002992 | 0.0058333 | -0.0012947 | -1.3542 | -1.0883 | -1.2445 | -1.0192 | -0.91543 | -0.88364 | -2.1419 | -1.9953 | 0.24303 | -2.1351 | 120.6088 | 120.9117 | 120.1915 | -2.2887 | 0.050799 | -121.9146 | 0.83853 | 0.94814 | 0.89734 | -121.8108 | -121.779 | -0.096032 | -0.28657 | 0.19742 | 0.057603 | 0.15363 | 0.01632 | -0.7039 | 1.1735 | 1.2773 | 1.309 | 1.1044 | -123.0373 | 122.8015 | 123.1044 | 122.3842 | 2.4357 | -123.1841
766.3438 | 123.0972 | -2.211 | 120.7764 | -0.00068679 | -0.0015748 | -0.0015471 | 0.020725 | -0.00019664 | 0.016561 | -0.0061807 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0056197 | -0.0010811 | -1.3679 | -1.102 | -1.2674 | -1.0238 | -0.92458 | -0.88822 | -2.1465 | -2.009 | 0.23845 | -2.1488 | 120.6088 | 120.8934 | 120.2647 | -2.2933 | 0.064531 | -121.8002 | 0.84311 | 0.94356 | 0.87903 | -121.701 | -121.6646 | -0.0823 | -0.16755 | 0.20199 | 0.062177 | 0.14448 | 0.11703 | -0.51162 | 1.1872 | 1.2864 | 1.3228 | 1.109 | -122.9228 | 122.8198 | 123.1044 | 122.4757 | 2.4495 | -123.0697
768.0625 | 123.0286 | -2.2064 | 120.8542 | -0.00068679 | -0.0017884 | -0.0011197 | 0.020939 | 1.7156e-05 | 0.016561 | 0.0014498 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0056197 | -0.0010811 | -1.3633 | -1.1249 | -1.2766 | -1.0238 | -0.91085 | -0.8928 | -2.1602 | -2.0044 | 0.22929 | -2.1626 | 120.5951 | 120.8888 | 120.2052 | -2.2933 | 0.046216 | -121.878 | 0.84311 | 0.92983 | 0.88361 | -121.765 | -121.747 | -0.086878 | -0.25911 | 0.20199 | 0.043863 | 0.13074 | 0.034626 | -0.64896 | 1.1826 | 1.2956 | 1.3136 | 1.0815 | -123.0144 | 122.8015 | 123.0952 | 122.4116 | 2.4357 | -123.1475
769.7812 | 123.143 | -2.2385 | 120.7489 | -0.00068679 | -0.0017884 | -0.0015471 | 0.020939 | -0.00041024 | 0.016561 | 0.0090803 | 0.00068369 | 0.0014571 | -0.0001282 | 0.0058333 | -0.0010811 | -1.4183 | -1.1661 | -1.3224 | -1.0742 | -0.97953 | -0.94316 | -2.2152 | -2.0548 | 0.23387 | -2.2129 | 120.5447 | 120.8293 | 120.1045 | -2.3482 | 0.023312 | -121.8231 | 0.82021 | 0.91609 | 0.89278 | -121.7284 | -121.6921 | -0.10978 | -0.20419 | 0.18367 | 0.025541 | 0.13532 | 0.08039 | -0.64441 | 1.1643 | 1.2589 | 1.2953 | 1.0723 | -122.9641 | 122.7832 | 123.0678 | 122.343 | 2.4723 | -123.0971
771.4844 | 123.0148 | -2.2156 | 120.8542 | 0.0069442 | -0.0024294 | -0.00090608 | 0.021366 | -0.00019664 | 0.016134 | 0.0014498 | 0.00047009 | 0.0014571 | -0.0001282 | 0.0058333 | -0.00086748 | -1.3816 | -1.1524 | -1.2812 | -1.0421 | -0.93374 | -0.90653 | -2.1877 | -2.0319 | 0.23845 | -2.1855 | 120.5722 | 120.8568 | 120.3334 | -2.3253 | 0.027898 | -121.8963 | 0.83395 | 0.9344 | 0.90651 | -121.7879 | -121.7607 | -0.10977 | -0.282 | 0.18368 | 0.030125 | 0.1399 | 0.002576 | -0.52076 | 1.1735 | 1.2818 | 1.309 | 1.0632 | -123.0419 | 122.7878 | 123.0723 | 122.549 | 2.454 | -123.1795
773.1719 | 123.0423 | -2.2522 | 120.8267 | 0.0069442 | -0.0022158 | -0.00026488 | 0.021152 | -0.00062384 | 0.016134 | 0.0014498 | 0.00089729 | 0.0012435 | 0.0002992 | 0.0054059 | -0.00086748 | -1.345 | -1.1066 | -1.2445 | -1.0009 | -0.89711 | -0.86075 | -2.1602 | -2.009 | 0.23845 | -2.1626 | 120.6042 | 120.8797 | 120.1457 | -2.3025 | 0.091992 | -121.8276 | 0.9072 | 1.0077 | 0.91566 | -121.7238 | -121.6875 | -0.050259 | -0.22248 | 0.24319 | 0.089639 | 0.1399 | 0.052935 | -0.68102 | 1.2513 | 1.3551 | 1.3914 | 1.1456 | -122.9869 | 122.8564 | 123.1319 | 122.3979 | 2.4906 | -123.1292
774.875 | 123.0835 | -2.2385 | 120.7718 | 0.0069442 | -0.001361 | -0.00069228 | 0.020939 | -0.00019664 | 0.016775 | 0.0090803 | 0.00068369 | 0.00081608 | 0.0005128 | 0.0058333 | -0.0010811 | -1.3908 | -1.1387 | -1.2949 | -1.0558 | -0.95206 | -0.92027 | -2.1923 | -2.0502 | 0.22929 | -2.1992 | 120.5585 | 120.8476 | 120.2373 | -2.3437 | 0.046207 | -121.8276 | 0.84768 | 0.94356 | 0.89735 | -121.7238 | -121.6921 | -0.1052 | -0.21334 | 0.18825 | 0.039277 | 0.14448 | 0.075816 | -0.53452 | 1.1826 | 1.2864 | 1.3182 | 1.0998 | -122.964 | 122.7969 | 123.0861 | 122.4757 | 2.4678 | -123.1155
776.625 | 123.1018 | -2.1927 | 120.7581 | -0.00068679 | -0.001361 | -0.0011197 | 0.020298 | -0.00041024 | 0.016561 | -0.0061807 | 0.00047009 | 0.0010299 | 0.0002992 | 0.0056197 | -0.0012947 | -1.4183 | -1.1616 | -1.3178 | -1.0833 | -0.96579 | -0.93858 | -2.1831 | -2.0411 | 0.23845 | -2.1855 | 120.5676 | 120.843 | 120.132 | -2.3299 | 0.009589 | -121.8414 | 0.77443 | 0.87489 | 0.8653 | -121.7239 | -121.6966 | -0.13724 | -0.19045 | 0.15163 | 0.007237 | 0.14448 | 0.08497 | -0.62609 | 1.1094 | 1.2269 | 1.2541 | 1.0311 | -122.9412 | 122.7603 | 123.0357 | 122.3247 | 2.4311 | -123.088
778.3125 | 123.0194 | -2.2476 | 120.813 | -0.00068679 | -0.001361 | -0.00090608 | 0.020511 | -0.00062384 | 0.016347 | 0.0014498 | 0.00047009 | 0.0012435 | 0.0005128 | 0.0056197 | -0.0010811 | -1.4091 | -1.1707 | -1.3178 | -1.0833 | -0.97037 | -0.93858 | -2.1694 | -2.0136 | 0.24303 | -2.1671 | 120.5997 | 120.8842 | 120.2464 | -2.307 | 0.078257 | -121.8963 | 0.83852 | 0.92982 | 0.85157 | -121.7834 | -121.7516 | -0.059415 | -0.21333 | 0.23403 | 0.080484 | 0.1399 | 0.071246 | -0.56656 | 1.1643 | 1.2772 | 1.309 | 1.0769 | -122.9824 | 122.8473 | 123.1319 | 122.4941 | 2.4907 | -123.12
780.0156 | 123.0103 | -2.2842 | 120.7855 | -0.00068679 | -0.0011474 | -0.00090608 | 0.020298 | -0.00062384 | 0.016561 | 0.0014498 | 0.00025649 | 0.0012435 | 0.0002992 | 0.0058333 | -0.00086748 | -1.4686 | -1.2119 | -1.3727 | -1.1474 | -1.0391 | -1.0027 | -2.2152 | -2.0731 | 0.23845 | -2.2175 | 120.5401 | 120.8293 | 120.0816 | -2.362 | 0.069089 | -121.9329 | 0.81563 | 0.9115 | 0.84241 | -121.8246 | -121.7882 | -0.07774 | -0.24538 | 0.21113 | 0.066739 | 0.14448 | 0.043769 | -0.70392 | 1.1368 | 1.2452 | 1.2816 | 1.0723 | -123.0007 | 122.8244 | 123.1135 | 122.3658 | 2.5227 | -123.1475
781.7344 | 123.0652 | -2.1332 | 120.9 | 0.014575 | -0.0011474 | -0.00090608 | 0.020298 | -0.00083764 | 0.016561 | 0.0090803 | 0.00068369 | 0.0010299 | 8.5404e-05 | 0.0058333 | -0.0010811 | -1.3954 | -1.1249 | -1.2995 | -1.065 | -0.96122 | -0.92943 | -2.0961 | -1.9586 | 0.24761 | -2.103 | 120.6546 | 120.9438 | 120.2876 | -2.2429 | 0.037079 | -121.965 | 0.73782 | 0.8337 | 0.79662 | -121.8612 | -121.8294 | -0.10975 | -0.24536 | 0.17454 | 0.030145 | 0.1399 | 0.043793 | -0.61232 | 1.0682 | 1.172 | 1.2038 | 1.0082 | -122.9961 | 122.7878 | 123.0769 | 122.4208 | 2.3808 | -123.1429
783.4375 | 123.1338 | -2.1698 | 120.8084 | -0.0083178 | -0.001361 | -0.00090608 | 0.020084 | -0.00041024 | 0.016561 | 0.0014498 | 0.00068369 | 0.00081608 | 8.5404e-05 | 0.0056197 | -0.0010811 | -1.4411 | -1.1799 | -1.3315 | -1.1016 | -0.98869 | -0.96148 | -2.1602 | -2.0182 | 0.23845 | -2.158 | 120.6042 | 120.8842 | 120.2693 | -2.2887 | 0.009595 | -121.91 | 0.72866 | 0.83827 | 0.82867 | -121.7971 | -121.7699 | -0.11892 | -0.20417 | 0.15164 | 0.011821 | 0.13074 | 0.075823 | -0.53909 | 1.0682 | 1.1811 | 1.2083 | 0.98993 | -122.9686 | 122.774 | 123.054 | 122.4391 | 2.4083 | -123.0971
785.0938 | 123.0103 | -2.1744 | 120.8908 | -0.0083178 | -0.0017884 | -0.00069228 | 0.020084 | -0.00041024 | 0.01592 | 0.0014498 | 0.00047009 | 0.0010299 | -0.0001282 | 0.0056197 | -0.0010811 | -1.4274 | -1.1707 | -1.3132 | -1.0833 | -0.97495 | -0.94316 | -2.1419 | -1.9861 | 0.24303 | -2.1442 | 120.618 | 120.9071 | 120.164 | -2.2796 | 0.032488 | -121.9741 | 0.74697 | 0.86116 | 0.82867 | -121.8658 | -121.834 | -0.10519 | -0.27284 | 0.18826 | 0.030134 | 0.13532 | 0.016319 | -0.72679 | 1.0911 | 1.1994 | 1.2312 | 1.0037 | -123.0327 | 122.7923 | 123.0815 | 122.3384 | 2.4174 | -123.1704
786.7969 | 123.0652 | -2.3483 | 120.7352 | 0.0069442 | -0.0024294 | -0.00069228 | 0.020725 | -0.00041024 | 0.016134 | 0.016711 | 0.00047009 | 0.00081608 | 0.0002992 | 0.0058333 | -0.00065368 | -1.5052 | -1.2257 | -1.3819 | -1.1474 | -1.0345 | -0.99811 | -2.2793 | -2.1235 | 0.23845 | -2.277 | 120.4806 | 120.7606 | 120.0267 | -2.4078 | 0.069071 | -121.8826 | 0.84309 | 0.96643 | 0.89736 | -121.7696 | -121.7333 | -0.059441 | -0.25455 | 0.22485 | 0.071303 | 0.13074 | 0.025444 | -0.70851 | 1.2009 | 1.3138 | 1.3502 | 1.1227 | -123.0144 | 122.8289 | 123.1089 | 122.375 | 2.5868 | -123.1429
788.5469 | 123.0881 | -2.3346 | 120.639 | -0.00068679 | -0.0024294 | -0.00069228 | 0.020725 | -0.00019664 | 0.016775 | 0.0014498 | 0.00047009 | 0.066623 | 0.0002992 | 0.0056197 | 0.06387 | -1.5236 | -1.2348 | -1.4048 | -1.152 | -1.0574 | -1.021 | -2.3159 | 120.3708 | 0.29797 | -2.3091 | 120.4257 | 120.724 | 120.0816 | -2.4536 | 0.018707 | -121.791 | 0.81104 | 0.92981 | 0.9111 | -121.6964 | -121.66 | -0.11896 | -0.21336 | 122.7053 | 0.025519 | 0.14448 | 0.084945 | -0.55744 | 1.1826 | 1.2772 | 1.3136 | 1.0998 | -122.9549 | 122.7603 | 123.0586 | 122.4162 | 2.6326 | -123.0926
790.2656 | 123.0743 | -2.3026 | 120.7031 | 0.0069442 | -0.0022158 | -0.00090608 | 0.020939 | -0.00062384 | 0.016347 | -0.0061807 | 0.00025649 | 0.066409 | 0.0005128 | 0.0054059 | 0.06387 | -1.5281 | -1.2577 | -1.4002 | -1.1566 | -1.0482 | -1.021 | -2.2884 | 120.4303 | 0.27508 | -2.277 | 120.4531 | 120.7469 | 120.0083 | -2.4215 | 0.014136 | -121.8597 | 0.77442 | 0.90234 | 0.88821 | -121.7513 | -121.7241 | -0.11896 | -0.24998 | 122.7328 | 0.025526 | 0.14448 | 0.043751 | -0.69478 | 1.146 | 1.2543 | 1.2816 | 1.0448 | -122.9915 | 122.7557 | 123.0494 | 122.3109 | 2.5776 | -123.1246
791.9375 | 123.1018 | -2.3071 | 120.6894 | -0.00068679 | -0.0022158 | -0.00069228 | 0.021152 | -0.00041024 | 0.016775 | -0.0061807 | 0.00047009 | 0.065768 | 0.0002992 | 0.0058333 | 0.063442 | -1.519 | -1.2577 | -1.3865 | -1.1383 | -1.0391 | -1.0027 | -2.2793 | 120.4486 | 0.27508 | -2.2724 | 120.4531 | 120.7515 | 120.1228 | -2.4215 | 0.027872 | -121.8276 | 0.78815 | 0.92066 | 0.89278 | -121.7284 | -121.6921 | -0.11438 | -0.23625 | 122.7557 | 0.034682 | 0.14906 | 0.062063 | -0.56658 | 1.1689 | 1.2681 | 1.3044 | 1.0494 | -122.9686 | 122.7603 | 123.0586 | 122.4299 | 2.5822 | -123.1109
793.6406 | 123.0103 | -2.4124 | 120.607 | -0.00068679 | -0.0024294 | -0.00047868 | 0.020939 | -0.00041024 | 0.016347 | 0.0014498 | 4.2686e-05 | 0.066409 | 0.0002992 | 0.0056197 | 0.063442 | -1.5922 | -1.331 | -1.4597 | -1.2024 | -1.1032 | -1.0714 | -2.3754 | 120.3662 | 0.26134 | -2.3549 | 120.3616 | 120.6507 | 119.9534 | -2.5039 | 0.037001 | -121.8093 | 0.82018 | 0.95269 | 0.91569 | -121.7102 | -121.6784 | -0.091509 | -0.24542 | 122.7786 | 0.057552 | 0.14906 | 0.043731 | -0.65359 | 1.2101 | 1.3093 | 1.3411 | 1.0814 | -122.9824 | 122.774 | 123.0631 | 122.3658 | 2.6738 | -123.1109
795.375 | 123.1201 | -2.3666 | 120.5887 | -0.015949 | -0.0022158 | -0.00047868 | 0.020939 | -0.00041024 | 0.016775 | -0.0061807 | 0.00047009 | 0.066409 | 0.0002992 | 0.0058333 | 0.063442 | -1.5922 | -1.3127 | -1.4597 | -1.2161 | -1.1077 | -1.0759 | -2.3525 | 120.3662 | 0.26592 | -2.3503 | 120.3753 | 120.6507 | 119.9305 | -2.4902 | 0.014118 | -121.8048 | 0.77441 | 0.90691 | 0.8928 | -121.6964 | -121.6646 | -0.12355 | -0.21337 | 122.7328 | 0.016353 | 0.1399 | 0.062042 | -0.65818 | 1.1506 | 1.2589 | 1.2907 | 1.054 | -122.9412 | 122.7419 | 123.0174 | 122.2971 | 2.6326 | -123.0789
797.0625 | 122.9874 | -2.298 | 120.7123 | -0.00068679 | -0.0017884 | -0.00069228 | 0.020939 | -0.00062384 | 0.016775 | -0.0061807 | 0.00047009 | 0.066195 | 0.0005128 | 0.0056197 | 0.063229 | -1.4869 | -1.1753 | -1.3498 | -1.1016 | -0.99327 | -0.96606 | -2.2243 | 120.4898 | 0.2705 | -2.2221 | 120.4989 | 120.7743 | 120.1091 | -2.3666 | 0.073664 | -121.8139 | 0.81105 | 0.94813 | 0.87446 | -121.7055 | -121.6783 | -0.068586 | -0.21335 | 122.7878 | 0.075893 | 0.14448 | 0.062068 | -0.60321 | 1.1963 | 1.3047 | 1.3319 | 1.1227 | -122.9366 | 122.7969 | 123.0723 | 122.407 | 2.5685 | -123.0788
798.7344 | 122.9828 | -2.2476 | 120.7626 | -0.015949 | -0.0017884 | -0.00069228 | 0.020939 | -0.00062384 | 0.016561 | -0.0061807 | 0.00047009 | 0.066195 | 0.0002992 | 0.0056197 | 0.063656 | -1.4778 | -1.1753 | -1.3498 | -1.1062 | -1.007 | -0.97979 | -2.2152 | 120.5035 | 0.26592 | -2.1992 | 120.5081 | 120.8018 | 120.0862 | -2.3437 | 0.032468 | -121.8688 | 0.76985 | 0.89777 | 0.86531 | -121.7696 | -121.7424 | -0.096046 | -0.25455 | 122.7512 | 0.048433 | 0.14448 | 0.039186 | -0.67645 | 1.1414 | 1.2406 | 1.2678 | 1.0723 | -122.9778 | 122.7557 | 123.0494 | 122.3338 | 2.5135 | -123.1063
800.4375 | 123.1247 | -2.243 | 120.7443 | -0.00068679 | -0.0017884 | -0.00026488 | 0.021366 | -0.00062384 | 0.016347 | 0.0014498 | 0.00068369 | 0.066409 | 0.0005128 | 0.0056197 | 0.063229 | -1.5144 | -1.189 | -1.3636 | -1.1245 | -1.0207 | -0.98895 | -2.2289 | 120.4898 | 0.2705 | -2.2267 | 120.4944 | 120.7835 | 120.045 | -2.3574 | 0.014153 | -121.8688 | 0.72864 | 0.87946 | 0.86531 | -121.7651 | -121.7333 | -0.11436 | -0.24997 | 122.7328 | 0.016382 | 0.13074 | 0.039181 | -0.69935 | 1.1185 | 1.2223 | 1.2541 | 1.054 | -122.9732 | 122.7374 | 123.0265 | 122.288 | 2.5135 | -123.1017
802.1094 | 123.1155 | -2.1561 | 120.7993 | -0.0083178 | -0.0022158 | -0.00047868 | 0.020939 | -0.00019664 | 0.016775 | 0.0014498 | 0.00047009 | 0.065982 | 0.0002992 | 0.0058333 | 0.063442 | -1.4549 | -1.1341 | -1.3224 | -1.0696 | -0.96579 | -0.92943 | -2.1648 | 120.5585 | 0.26592 | -2.1534 | 120.5539 | 120.8384 | 120.1045 | -2.2979 | -0.008717 | -121.8688 | 0.70119 | 0.83369 | 0.84241 | -121.765 | -121.7287 | -0.14181 | -0.24538 | 122.7145 | 0.002667 | 0.14448 | 0.039193 | -0.69476 | 1.0865 | 1.1903 | 1.2266 | 1.022 | -122.964 | 122.7099 | 122.9945 | 122.2606 | 2.422 | -123.0971
803.7812 | 123.0698 | -2.0508 | 120.9229 | -0.00068679 | -0.0022158 | -0.00069228 | 0.020939 | -0.00019664 | 0.016775 | -0.0061807 | 0.00068369 | 0.065982 | 0.0005128 | 0.0056197 | 0.062801 | -1.3404 | -0.99673 | -1.1942 | -0.95054 | -0.84674 | -0.81954 | -2.0274 | 120.6913 | 0.25677 | -2.0115 | 120.6867 | 120.9712 | 120.2968 | -2.1605 | 0.023365 | -121.8734 | 0.71036 | 0.8566 | 0.83323 | -121.7696 | -121.7424 | -0.10973 | -0.2362 | 122.742 | 0.039321 | 0.14905 | 0.048376 | -0.62606 | 1.1002 | 1.204 | 1.2312 | 1.0541 | -122.9503 | 122.7374 | 123.022 | 122.3476 | 2.3075 | -123.0834
805.4844 | 123.1155 | -1.9089 | 121.0419 | 0.0069442 | -0.0017884 | -0.00026488 | 0.021152 | -0.00041024 | 0.016561 | 0.0090803 | 0.00025649 | 0.065768 | 0.0002992 | 0.0058333 | 0.063015 | -1.2351 | -0.896 | -1.0843 | -0.84066 | -0.73227 | -0.70965 | -1.8809 | 120.824 | 0.26134 | -1.8649 | 120.8332 | 121.1132 | 120.5669 | -2.0048 | 0.027985 | -121.8825 | 0.67376 | 0.82457 | 0.79658 | -121.7741 | -121.7515 | -0.095958 | -0.20871 | 122.7329 | 0.043934 | 0.13989 | 0.071294 | -0.47494 | 1.0682 | 1.1766 | 1.1992 | 1.0129 | -122.9228 | 122.742 | 123.022 | 122.4758 | 2.1702 | -123.0467
807.1562 | 123.0835 | -1.918 | 120.9778 | -0.00068679 | -0.0020022 | -0.00026488 | 0.020511 | -0.00041024 | 0.016775 | -0.0061807 | 0.00025649 | 0.066195 | 8.5404e-05 | 0.0058333 | 0.063442 | -1.2626 | -0.92347 | -1.1118 | -0.85897 | -0.75974 | -0.73255 | -1.9267 | 120.792 | 0.26134 | -1.9199 | 120.7828 | 121.0674 | 120.3288 | -2.0644 | -0.00865 | -121.8368 | 0.65544 | 0.80625 | 0.8149 | -121.7375 | -121.7103 | -0.14633 | -0.19499 | 122.71 | -0.001856 | 0.14447 | 0.089595 | -0.64894 | 1.0591 | 1.1583 | 1.1855 | 0.99456 | -122.9045 | 122.7008 | 122.9854 | 122.2469 | 2.1794 | -123.0421
808.8125 | 123.0927 | -1.8951 | 121.0739 | -0.00068679 | -0.0015748 | -0.00069228 | 0.020511 | -0.00041024 | 0.016561 | -0.0061807 | 0.00068369 | 0.066195 | 8.5404e-05 | 0.0060469 | 0.063229 | -1.2351 | -0.91889 | -1.066 | -0.82234 | -0.73227 | -0.7005 | -1.8717 | 120.8378 | 0.27508 | -1.8604 | 120.8286 | 121.1177 | 120.5944 | -2.0048 | 0.02341 | -121.8963 | 0.66003 | 0.82915 | 0.80574 | -121.8062 | -121.7744 | -0.10969 | -0.24533 | 122.7329 | 0.034779 | 0.14447 | 0.043829 | -0.47951 | 1.0728 | 1.1629 | 1.1946 | 0.97625 | -122.9456 | 122.7237 | 123.0129 | 122.4895 | 2.1702 | -123.0787
810.5156 | 123.0515 | -1.8997 | 121.0693 | -0.00068679 | -0.0017884 | -0.00026488 | 0.020511 | -0.00062384 | 0.016988 | -0.0061807 | 0.00025649 | 0.065768 | 8.5404e-05 | 0.0058333 | 0.062801 | -1.2214 | -0.90058 | -1.0568 | -0.81319 | -0.71395 | -0.68676 | -1.8397 | 120.8607 | 0.26592 | -1.842 | 120.8561 | 121.1406 | 120.6356 | -1.9911 | 0.060039 | -121.8825 | 0.67834 | 0.84288 | 0.78284 | -121.7833 | -121.7561 | -0.091378 | -0.21328 | 122.7604 | 0.057671 | 0.14905 | 0.0713 | -0.43372 | 1.0865 | 1.1858 | 1.213 | 0.99914 | -122.909 | 122.7558 | 123.0404 | 122.5353 | 2.1656 | -123.0604
812.1875 | 123.0835 | -1.7853 | 121.1563 | -0.00068679 | -0.0017884 | -5.128e-05 | 0.020298 | -0.00041024 | 0.016775 | -0.0061807 | 0.00047009 | 0.065982 | 8.5404e-05 | 0.0056197 | 0.062801 | -1.1985 | -0.86395 | -1.0202 | -0.78114 | -0.67274 | -0.6364 | -1.7939 | 120.911 | 0.2705 | -1.7734 | 120.9156 | 121.2093 | 120.4616 | -1.9224 | -0.008613 | -121.9374 | 0.58679 | 0.76507 | 0.77368 | -121.8291 | -121.7927 | -0.13714 | -0.24074 | 122.6963 | 0.011911 | 0.14905 | 0.053004 | -0.69469 | 1.0041 | 1.1125 | 1.1489 | 0.92133 | -122.9502 | 122.7009 | 122.9946 | 122.2469 | 2.0558 | -123.0787
813.875 | 123.0515 | -1.8219 | 121.1197 | -0.00068679 | -0.0015748 | 0.00016232 | 0.020298 | -0.00041024 | 0.016988 | -0.0061807 | 0.00068369 | 0.065768 | 0.0002992 | 0.0058333 | 0.062801 | -1.2168 | -0.896 | -1.0248 | -0.78572 | -0.67274 | -0.64555 | -1.7985 | 120.8881 | 0.26592 | -1.7871 | 120.9064 | 121.1864 | 120.512 | -1.9362 | 0.023429 | -121.9054 | 0.60509 | 0.79711 | 0.77368 | -121.7924 | -121.7652 | -0.11425 | -0.21327 | 122.71 | 0.034796 | 0.14905 | 0.066732 | -0.6077 | 1.0362 | 1.1492 | 1.1763 | 0.9259 | -122.9182 | 122.7283 | 123.0083 | 122.3339 | 2.0878 | -123.0558
815.5781 | 122.9553 | -1.8768 | 121.1288 | 0.0069442 | -0.0011474 | -0.00026488 | 0.020511 | -0.00041024 | 0.017202 | -0.0061807 | 0.00025649 | 0.065982 | 0.0005128 | 0.0058333 | 0.063015 | -1.226 | -0.88226 | -1.0065 | -0.78114 | -0.67732 | -0.64555 | -1.7893 | 120.8927 | 0.27508 | -1.7825 | 120.9018 | 121.191 | 120.6036 | -1.9362 | 0.087519 | -121.91 | 0.65087 | 0.87036 | 0.78284 | -121.8062 | -121.7744 | -0.05932 | -0.22701 | 122.7696 | 0.094306 | 0.15363 | 0.062156 | -0.52528 | 1.0957 | 1.1995 | 1.2313 | 0.99457 | -122.9182 | 122.7787 | 123.0678 | 122.4804 | 2.1519 | -123.065
817.2812 | 123.0698 | -1.7258 | 121.1929 | -0.00068679 | -0.0017884 | -5.128e-05 | 0.01987 | -0.00019664 | 0.016988 | -0.0061807 | 0.00047009 | 0.065768 | 0.0002992 | 0.0056197 | 0.062801 | -1.1664 | -0.81359 | -0.96069 | -0.7262 | -0.62695 | -0.59977 | -1.7023 | 120.9889 | 0.27508 | -1.7001 | 120.9888 | 121.278 | 120.5898 | -1.8446 | 0.023457 | -121.9191 | 0.55933 | 0.76508 | 0.74162 | -121.8199 | -121.7927 | -0.11881 | -0.2041 | 122.7146 | 0.025661 | 0.14447 | 0.085062 | -0.6031 | 0.99957 | 1.0988 | 1.126 | 0.91218 | -122.8952 | 122.7146 | 123.0038 | 122.3156 | 2.0009 | -123.0375
818.9688 | 123.0469 | -1.7395 | 121.2112 | -0.00068679 | -0.0017884 | -0.00026488 | 0.020084 | -0.00019664 | 0.016775 | -0.0061807 | 0.00025649 | 0.065768 | 8.5404e-05 | 0.0058333 | 0.062801 | -1.2076 | -0.88684 | -0.98358 | -0.7674 | -0.64985 | -0.6364 | -1.6932 | 120.998 | 0.27508 | -1.691 | 120.9934 | 121.2917 | 120.544 | -1.8354 | 0.046348 | -121.9786 | 0.53186 | 0.75592 | 0.70957 | -121.8611 | -121.8476 | -0.095915 | -0.21783 | 122.7375 | 0.048551 | 0.14447 | 0.080487 | -0.6672 | 0.9721 | 1.0897 | 1.1031 | 0.85266 | -122.9044 | 122.7329 | 123.0312 | 122.2835 | 2.0146 | -123.0467
820.6406 | 123.0423 | -1.7349 | 121.2067 | -0.00068679 | -0.0015748 | -0.00069228 | 0.020511 | -0.00062384 | 0.016988 | 0.0090803 | 0.00068369 | 0.23648 | 0.0005128 | 0.0060469 | 0.063229 | -1.2122 | -0.88684 | -1.0019 | -0.77198 | -0.66358 | -0.6364 | -1.7389 | 120.9294 | 0.27508 | -1.7047 | 120.9614 | 121.2414 | 120.5028 | -1.8446 | -0.00402 | -121.9786 | 0.5227 | 0.73303 | 0.73705 | -121.8702 | -121.8431 | -0.10965 | -0.24531 | 122.6643 | 0.030237 | 0.13989 | 0.0347 | -0.70383 | 0.96294 | 1.0713 | 1.0985 | 0.84808 | -122.9456 | 122.6963 | 122.9763 | 122.2378 | 2.01 | -123.0512
822.3125 | 123.0011 | -1.7075 | 121.225 | -0.00068679 | -0.001361 | -0.00026488 | 0.020084 | -0.00019664 | 0.017202 | -0.0061807 | 0.00068369 | 0.2352 | 0.0002992 | 0.0056197 | 0.062588 | -1.1756 | -0.85479 | -0.97443 | -0.74909 | -0.63611 | -0.60893 | -1.6565 | 120.9431 | 0.26592 | -1.6452 | 120.9843 | 121.2734 | 120.5257 | -1.8034 | 0.050935 | -121.9741 | 0.53186 | 0.73303 | 0.6821 | -121.8611 | -121.8339 | -0.095907 | -0.24072 | 122.6505 | 0.062295 | 0.1582 | 0.04844 | -0.69925 | 0.95837 | 1.0713 | 1.0985 | 0.85267 | -122.8815 | 122.6917 | 122.9809 | 122.2332 | 1.9734 | -123.0283
824 | 122.9141 | -1.8082 | 121.138 | 0.0069442 | -0.0015748 | -0.00047868 | 0.020084 | -0.00041024 | 0.017202 | -0.0061807 | 0.00025649 | 0.23499 | 0.0002992 | 0.0056197 | 0.063015 | -1.226 | -0.90973 | -1.0156 | -0.78572 | -0.68648 | -0.65471 | -1.716 | 120.8881 | 0.26592 | -1.7001 | 120.9156 | 121.2002 | 120.5578 | -1.8537 | 0.092118 | -121.9237 | 0.58221 | 0.79254 | 0.70042 | -121.8245 | -121.7927 | -0.045565 | -0.22243 | 122.6963 | 0.10806 | 0.15362 | 0.062158 | -0.58022 | 1.0225 | 1.1217 | 1.1535 | 0.89843 | -122.854 | 122.7237 | 123.0083 | 122.3659 | 2.0741 | -122.9917
825.6719 | 123.0194 | -1.7715 | 121.1151 | -0.0083178 | -0.001361 | -0.00047868 | 0.01987 | -0.00019664 | 0.016988 | 0.0014498 | 0.00047009 | 0.23499 | 0.0002992 | 0.0056197 | 0.062588 | -1.258 | -0.93263 | -1.0431 | -0.81319 | -0.70937 | -0.68218 | -1.7618 | 120.8378 | 0.26592 | -1.7459 | 120.8652 | 121.1498 | 120.4708 | -1.8995 | 0.009707 | -121.9283 | 0.51354 | 0.72844 | 0.71874 | -121.8245 | -121.7973 | -0.12798 | -0.2499 | 122.6093 | 0.02565 | 0.15363 | 0.034681 | -0.64433 | 0.95836 | 1.0622 | 1.0894 | 0.83892 | -122.8769 | 122.6368 | 122.9213 | 122.2423 | 2.0375 | -123.0146
827.3438 | 122.9782 | -1.7761 | 121.1151 | -0.00068679 | -0.00093379 | -0.00047868 | 0.020084 | -0.00062384 | 0.017202 | 0.0014498 | 0.00047009 | 0.23456 | 0.0002992 | 0.0054059 | 0.062588 | -1.2443 | -0.95094 | -1.0568 | -0.82692 | -0.72769 | -0.7005 | -1.7573 | 120.8149 | 0.27508 | -1.7551 | 120.8469 | 121.1269 | 120.5578 | -1.8995 | 0.018864 | -121.942 | 0.53185 | 0.71929 | 0.70042 | -121.8428 | -121.8156 | -0.1234 | -0.26821 | 122.591 | 0.021071 | 0.14447 | 0.011788 | -0.55734 | 0.9492 | 1.0484 | 1.0756 | 0.82518 | -122.8724 | 122.623 | 122.903 | 122.3339 | 2.0512 | -123.0146
829.0156 | 122.9965 | -1.8265 | 121.0144 | 0.0069442 | -0.001361 | -0.00026488 | 0.020511 | -0.00062384 | 0.017202 | -0.0061807 | 0.00047009 | 0.23456 | 0.0002992 | 0.0060469 | 0.062801 | -1.2901 | -1.015 | -1.1026 | -0.87271 | -0.77348 | -0.74628 | -1.8076 | 120.7554 | 0.26592 | -1.8054 | 120.7965 | 121.072 | 120.4342 | -1.959 | 0.018849 | -121.8871 | 0.53642 | 0.72386 | 0.70501 | -121.7879 | -121.7607 | -0.13257 | -0.21787 | 122.5818 | 0.021059 | 0.15363 | 0.057553 | -0.58025 | 0.95377 | 1.053 | 1.0802 | 0.81143 | -122.822 | 122.623 | 122.8984 | 122.2606 | 2.0924 | -122.9734
830.75 | 122.9645 | -1.8173 | 121.0602 | -0.00068679 | -0.001361 | -0.00047868 | 0.020084 | -0.00083764 | 0.016988 | 0.0014498 | 0.00025649 | 0.23434 | 0.0007264 | 0.0058333 | 0.062801 | -1.2901 | -1.0059 | -1.098 | -0.87728 | -0.75974 | -0.7417 | -1.803 | 120.7737 | 0.26592 | -1.7871 | 120.7965 | 121.0811 | 120.3975 | -1.9316 | 0.014273 | -121.9375 | 0.52726 | 0.71928 | 0.70501 | -121.8199 | -121.8019 | -0.11425 | -0.26365 | 122.591 | 0.030219 | 0.14447 | 0.020933 | -0.66266 | 0.94004 | 1.0576 | 1.0756 | 0.81144 | -122.8632 | 122.6139 | 122.8984 | 122.2148 | 2.0832 | -122.9918
832.5469 | 122.8867 | -1.8494 | 121.0693 | -0.00068679 | -0.001361 | -0.00090608 | 0.020298 | -0.00041024 | 0.017202 | 0.0014498 | 0.00025649 | 0.23413 | 8.5404e-05 | 0.0056197 | 0.062801 | -1.2946 | -1.0059 | -1.1118 | -0.88186 | -0.77348 | -0.75544 | -1.7847 | 120.7737 | 0.26134 | -1.7734 | 120.8011 | 121.0857 | 120.3472 | -1.9178 | 0.064632 | -121.9512 | 0.55473 | 0.73759 | 0.67296 | -121.8428 | -121.8248 | -0.068471 | -0.26822 | 122.623 | 0.075998 | 0.14447 | 0.016357 | -0.72218 | 0.9675 | 1.0759 | 1.0939 | 0.84348 | -122.8541 | 122.6505 | 122.9351 | 122.1965 | 2.1107 | -122.9872
834.2344 | 122.9141 | -1.9043 | 120.9686 | -0.00068679 | -0.0011474 | -0.00069228 | 0.020084 | -0.00041024 | 0.017416 | 0.0014498 | 0.00047009 | 0.23392 | 0.0002992 | 0.0056197 | 0.062801 | -1.3542 | -1.0883 | -1.1713 | -0.94138 | -0.83758 | -0.81038 | -1.8443 | 120.7096 | 0.27508 | -1.842 | 120.7416 | 121.017 | 120.4433 | -1.9774 | 0.060038 | -121.91 | 0.55014 | 0.733 | 0.67297 | -121.8062 | -121.779 | -0.073063 | -0.22704 | 122.6139 | 0.062249 | 0.13531 | 0.048386 | -0.52532 | 0.96291 | 1.0667 | 1.0939 | 0.816 | -122.8129 | 122.6459 | 122.9213 | 122.3476 | 2.1794 | -122.946
835.9688 | 122.8546 | -1.9272 | 121.019 | 0.0069442 | -0.00093379 | -0.00069228 | 0.020084 | -0.00062384 | 0.016988 | 0.0090803 | 0.00025649 | 0.23413 | 0.0005128 | 0.0060469 | 0.062588 | -1.377 | -1.0883 | -1.1759 | -0.9597 | -0.85132 | -0.8287 | -1.8488 | 120.705 | 0.2705 | -1.842 | 120.7279 | 121.0124 | 120.2693 | -1.9819 | 0.078347 | -121.9787 | 0.55014 | 0.75131 | 0.67297 | -121.8703 | -121.8477 | -0.054754 | -0.29113 | 122.6322 | 0.085137 | 0.13989 | -0.006547 | -0.74966 | 0.96749 | 1.0759 | 1.0985 | 0.83888 | -122.8678 | 122.655 | 122.9396 | 122.1965 | 2.1977 | -123.0009
837.7031 | 123.0011 | -1.8723 | 120.9503 | -0.00068679 | -0.00093379 | -0.00069228 | 0.01987 | -0.00041024 | 0.017416 | 0.0014498 | 0.00089729 | 0.2337 | 0.0002992 | 0.0058333 | 0.062374 | -1.377 | -1.0746 | -1.185 | -0.95054 | -0.84216 | -0.82412 | -1.8488 | 120.6913 | 0.28424 | -1.842 | 120.7141 | 121.0033 | 120.2876 | -1.9819 | 0.023415 | -121.9009 | 0.49521 | 0.68723 | 0.66381 | -121.7925 | -121.7744 | -0.10969 | -0.2362 | 122.5635 | 0.030205 | 0.13989 | 0.052961 | -0.66268 | 0.92171 | 1.0301 | 1.0481 | 0.79769 | -122.7992 | 122.5864 | 122.8755 | 122.1599 | 2.1565 | -122.9323
839.4531 | 122.9507 | -1.9913 | 120.8405 | 0.0069442 | -0.0011474 | -0.00047868 | 0.01987 | -0.00062384 | 0.016988 | 0.0090803 | 0.00025649 | 0.23349 | 0.0002992 | 0.0056197 | 0.062374 | -1.4824 | -1.1661 | -1.272 | -1.0467 | -0.93832 | -0.92027 | -1.9542 | 120.5631 | 0.27966 | -1.9565 | 120.6088 | 120.898 | 120.2647 | -2.101 | 0.037119 | -121.8871 | 0.50892 | 0.71926 | 0.68214 | -121.7788 | -121.7607 | -0.10972 | -0.23164 | 122.5543 | 0.034756 | 0.14447 | 0.057516 | -0.57571 | 0.94459 | 1.053 | 1.071 | 0.82513 | -122.7946 | 122.6001 | 122.8892 | 122.256 | 2.2709 | -122.9414
841.2031 | 122.9141 | -2.0279 | 120.7993 | -0.00068679 | -0.00093379 | -0.0011197 | 0.019657 | -0.00041024 | 0.017202 | -0.0061807 | 0.00047009 | 0.23328 | 0.0007264 | 0.0060469 | 0.062801 | -1.4961 | -1.1707 | -1.2903 | -1.0696 | -0.96122 | -0.92943 | -1.9999 | 120.531 | 0.27966 | -1.9977 | 120.5539 | 120.843 | 120.3655 | -2.1285 | 0.027951 | -121.8688 | 0.53181 | 0.73757 | 0.70961 | -121.7605 | -121.7287 | -0.10057 | -0.24538 | 122.5589 | 0.030169 | 0.13074 | 0.043772 | -0.43378 | 0.95832 | 1.0667 | 1.0985 | 0.85718 | -122.7992 | 122.5818 | 122.8709 | 122.3934 | 2.3076 | -122.9277
842.8906 | 122.9095 | -2.092 | 120.7489 | -0.00068679 | -0.00071999 | -0.00047868 | 0.01987 | -0.00062384 | 0.017202 | -0.0061807 | 0.00025649 | 0.23306 | 0.0002992 | 0.0060469 | 0.062588 | -1.5693 | -1.2348 | -1.3636 | -1.1108 | -1.0162 | -0.98895 | -2.0732 | 120.4486 | 0.2934 | -2.0756 | 120.4806 | 120.7606 | 120.0312 | -2.2109 | 0.018775 | -121.8597 | 0.52264 | 0.7284 | 0.70963 | -121.7651 | -121.7379 | -0.1189 | -0.26828 | 122.5406 | 0.016418 | 0.13532 | 0.011711 | -0.71766 | 0.9812 | 1.0758 | 1.103 | 0.85716 | -122.8221 | 122.5726 | 122.8526 | 122.1232 | 2.3854 | -122.9598
844.6406 | 122.9233 | -2.1057 | 120.7031 | -0.00068679 | -0.00050639 | -0.00047868 | 0.019657 | -0.00041024 | 0.017416 | 0.0090803 | 0.00047009 | 0.23306 | 0.0002992 | 0.0058333 | 0.062588 | -1.5785 | -1.2119 | -1.3544 | -1.1154 | -1.0116 | -0.97521 | -2.0732 | 120.4394 | 0.29797 | -2.0618 | 120.4806 | 120.7652 | 120.0679 | -2.2063 | 0.032508 | -121.8185 | 0.52722 | 0.75129 | 0.71878 | -121.7147 | -121.6783 | -0.10059 | -0.22251 | 122.5451 | 0.043887 | 0.14447 | 0.062066 | -0.63526 | 0.99035 | 1.0941 | 1.1305 | 0.89379 | -122.7763 | 122.5863 | 122.8709 | 122.1736 | 2.4037 | -122.9094
846.375 | 122.8363 | -2.3438 | 120.5338 | 0.0069442 | -0.00050639 | -0.00069228 | 0.019229 | -0.00041024 | 0.016988 | 0.0014498 | 0.00025649 | 0.23328 | 8.5404e-05 | 0.0058333 | 0.062588 | -1.7342 | -1.3539 | -1.5192 | -1.2664 | -1.1627 | -1.1355 | -2.2701 | 120.2425 | 0.29797 | -2.277 | 120.27 | 120.55 | 119.8344 | -2.4078 | 0.073651 | -121.8002 | 0.60959 | 0.82451 | 0.75086 | -121.6964 | -121.6692 | -0.064019 | -0.26375 | 122.5863 | 0.066725 | 0.13074 | 0.016244 | -0.6994 | 1.0773 | 1.1811 | 1.2083 | 0.98989 | -122.8039 | 122.6138 | 122.8937 | 122.1781 | 2.6417 | -122.9415
848.1094 | 122.818 | -2.3529 | 120.5475 | -0.0083178 | -7.8988e-05 | -0.00090608 | 0.019443 | -0.00041024 | 0.017202 | 0.0014498 | 0.00025649 | 0.23306 | -0.0001282 | 0.0056197 | 0.062588 | -1.7616 | -1.3722 | -1.5513 | -1.2985 | -1.1902 | -1.1675 | -2.3022 | 120.2151 | 0.30713 | -2.2908 | 120.238 | 120.5271 | 119.8298 | -2.4352 | 0.050754 | -121.846 | 0.59127 | 0.80161 | 0.75086 | -121.7376 | -121.715 | -0.082337 | -0.30953 | 122.568 | 0.062143 | 0.14448 | -0.020382 | -0.71771 | 1.0544 | 1.1627 | 1.1854 | 0.98073 | -122.8496 | 122.5909 | 122.88 | 122.1827 | 2.66 | -122.9827
849.8125 | 122.8409 | -2.4307 | 120.4376 | 0.014575 | 0.00077561 | -0.0013333 | 0.019016 | -0.00041024 | 0.016988 | 0.0014498 | 0.00068369 | 0.23285 | -0.0001282 | 0.0056197 | 0.062588 | -1.8578 | -1.4592 | -1.6429 | -1.4038 | -1.2955 | -1.2682 | -2.3846 | 120.1235 | 0.32087 | -2.3778 | 120.1601 | 120.4447 | 120.0862 | -2.5039 | 0.046153 | -121.8414 | 0.57295 | 0.78787 | 0.74172 | -121.7331 | -121.7059 | -0.073199 | -0.2775 | 122.5542 | 0.052968 | 0.12617 | 0.007067 | -0.35144 | 1.0269 | 1.1352 | 1.1625 | 0.97156 | -122.8222 | 122.5908 | 122.8754 | 122.5169 | 2.7516 | -122.9415
851.5469 | 122.8958 | -2.4124 | 120.3735 | -0.0083178 | 0.00077561 | -0.0011197 | 0.018802 | -0.00041024 | 0.016988 | 0.0014498 | 0.00047009 | 0.23285 | 8.5404e-05 | 0.0058333 | 0.06216 | -1.8852 | -1.4683 | -1.6795 | -1.445 | -1.3321 | -1.3003 | -2.3846 | 120.1281 | 0.35292 | -2.3823 | 120.1418 | 120.431 | 119.7016 | -2.5177 | 0.027843 | -121.8185 | 0.52717 | 0.73293 | 0.70509 | -121.7056 | -121.6738 | -0.10525 | -0.23173 | 122.5405 | 0.030079 | 0.13532 | 0.057418 | -0.67196 | 0.96741 | 1.0803 | 1.1121 | 0.94409 | -122.7581 | 122.5542 | 122.8434 | 122.114 | 2.7653 | -122.8912
853.2812 | 122.8317 | -2.4033 | 120.4147 | -0.00068679 | 0.00056201 | -0.0013333 | 0.018802 | -0.00041024 | 0.017416 | -0.0061807 | 0.00025649 | 0.23285 | 0.0002992 | 0.0054059 | 0.062588 | -1.8532 | -1.418 | -1.6612 | -1.4221 | -1.3184 | -1.2866 | -2.3937 | 120.1143 | 0.3575 | -2.3869 | 120.1464 | 120.4218 | 119.7748 | -2.5222 | 0.009529 | -121.8368 | 0.55006 | 0.74209 | 0.73256 | -121.7331 | -121.7013 | -0.11898 | -0.26835 | 122.5176 | 0.016345 | 0.13533 | 0.007062 | -0.6399 | 0.98115 | 1.0849 | 1.1167 | 0.9853 | -122.8085 | 122.5496 | 122.8251 | 122.1781 | 2.7608 | -122.937
854.9688 | 122.8867 | -2.5314 | 120.2545 | -0.00068679 | 0.00056201 | -0.0013333 | 0.019229 | -0.00062384 | 0.016988 | -0.0061807 | 0.00047009 | 0.23242 | 0.0002992 | 0.0058333 | 0.062374 | -1.9356 | -1.537 | -1.7436 | -1.4908 | -1.3871 | -1.3552 | -2.5128 | 119.9861 | 0.37123 | -2.5105 | 120.009 | 120.2936 | 119.578 | -2.6459 | 0.018651 | -121.7453 | 0.59582 | 0.78785 | 0.7692 | -121.6416 | -121.6098 | -0.11444 | -0.24549 | 122.5176 | 0.020893 | 0.13533 | 0.039078 | -0.67656 | 1.0406 | 1.1444 | 1.1762 | 0.99443 | -122.7673 | 122.5405 | 122.825 | 122.1094 | 2.9027 | -122.9004
856.7031 | 122.7859 | -2.536 | 120.3323 | -0.0083178 | 0.00056201 | -0.0015471 | 0.019016 | -0.00019664 | 0.016988 | 0.0014498 | 0.00047009 | 0.23285 | 0.0002992 | 0.0058333 | 0.062374 | -1.8807 | -1.4546 | -1.6886 | -1.4404 | -1.3413 | -1.3095 | -2.4624 | 120.0182 | 0.40329 | -2.4602 | 120.0502 | 120.3394 | 119.6146 | -2.6047 | 0.073597 | -121.7728 | 0.65534 | 0.84737 | 0.77378 | -121.6736 | -121.6418 | -0.068647 | -0.2821 | 122.5542 | 0.075837 | 0.14448 | 0.007045 | -0.71775 | 1.0956 | 1.1947 | 1.2266 | 1.0814 | -122.7947 | 122.5863 | 122.8754 | 122.1506 | 2.9393 | -122.937
858.4375 | 122.9279 | -2.5085 | 120.2866 | -0.0083178 | 0.00056201 | -0.0013333 | 0.018588 | -0.00062384 | 0.016775 | 0.0014498 | 4.2686e-05 | 0.23285 | 8.5404e-05 | 0.0060469 | 0.062801 | -1.899 | -1.45 | -1.7024 | -1.4587 | -1.3413 | -1.3186 | -2.4624 | 120.0365 | 0.40786 | -2.4602 | 120.0548 | 120.3394 | 119.6466 | -2.6001 | 0.046131 | -121.7453 | 0.60956 | 0.80617 | 0.76004 | -121.6278 | -121.6052 | -0.091535 | -0.23174 | 122.5451 | 0.048371 | 0.13991 | 0.052821 | -0.63993 | 1.0498 | 1.1673 | 1.1899 | 1.0585 | -122.749 | 122.5634 | 122.8479 | 122.1552 | 2.9164 | -122.8866
860.125 | 122.9324 | -2.4902 | 120.2866 | -0.00068679 | 0.001203 | -0.0013333 | 0.018588 | -0.00041024 | 0.017202 | -0.0061807 | 0.00047009 | 0.23264 | 0.0007264 | 0.0060469 | 0.062374 | -1.9036 | -1.4592 | -1.707 | -1.4633 | -1.355 | -1.3369 | -2.4807 | 119.9999 | 0.40329 | -2.4831 | 120.0319 | 120.3165 | 119.6466 | -2.6138 | 0.009505 | -121.7499 | 0.58667 | 0.78328 | 0.77378 | -121.6416 | -121.6235 | -0.12358 | -0.25463 | 122.4901 | 0.007167 | 0.13075 | 0.029928 | -0.63993 | 1.0269 | 1.1352 | 1.1533 | 1.0311 | -122.7673 | 122.5222 | 122.8067 | 122.1369 | 2.8935 | -122.9004
861.7969 | 122.8821 | -2.4948 | 120.2911 | -0.0083178 | 0.00098941 | -0.0013333 | 0.019016 | -0.00019664 | 0.016988 | 0.0014498 | 0.00025649 | 0.23242 | 0.0002992 | 0.0058333 | 0.062588 | -1.8669 | -1.4088 | -1.6657 | -1.4175 | -1.3092 | -1.2774 | -2.4807 | 119.9999 | 0.37581 | -2.4739 | 120.0365 | 120.3211 | 119.6604 | -2.6138 | 0.014083 | -121.7087 | 0.62788 | 0.82906 | 0.81498 | -121.6004 | -121.5685 | -0.119 | -0.25464 | 122.4947 | 0.020902 | 0.13991 | 0.029928 | -0.63077 | 1.0773 | 1.1856 | 1.2174 | 1.086 | -122.7719 | 122.5313 | 122.8159 | 122.1552 | 2.8706 | -122.905
863.4688 | 122.8683 | -2.6321 | 120.1447 | -0.015949 | 0.0014166 | -0.0013333 | 0.018802 | -0.00019664 | 0.016988 | -0.0061807 | 0.00089729 | 0.23221 | 0.0002992 | 0.0060469 | 0.062588 | -1.9219 | -1.4821 | -1.7298 | -1.4816 | -1.3779 | -1.3415 | -2.5769 | 119.8991 | 0.37123 | -2.5838 | 119.9312 | 120.2203 | 119.6329 | -2.7146 | 0.055254 | -121.6263 | 0.71027 | 0.9023 | 0.84704 | -121.5226 | -121.4862 | -0.082409 | -0.21346 | 122.5313 | 0.048342 | 0.13075 | 0.075684 | -0.51175 | 1.1505 | 1.2542 | 1.2906 | 1.1501 | -122.7215 | 122.5633 | 122.8525 | 122.265 | 3.0034 | -122.8592
865.2031 | 122.7951 | -2.7924 | 120.076 | -0.00068679 | 0.00056201 | -0.0015471 | 0.019229 | -0.00062384 | 0.016988 | 0.0014498 | 0.00047009 | 0.23221 | 0.0005128 | 0.0058333 | 0.062588 | -2.0501 | -1.5965 | -1.8489 | -1.6007 | -1.4924 | -1.4605 | -2.7509 | 119.7297 | 0.34834 | -2.7441 | 119.7526 | 120.0372 | 119.3994 | -2.8885 | 0.041472 | -121.6767 | 0.74229 | 0.94348 | 0.90201 | -121.5684 | -121.5365 | -0.096187 | -0.32335 | 122.5221 | 0.048304 | 0.14449 | -0.038796 | -0.6766 | 1.1917 | 1.3 | 1.3318 | 1.1958 | -122.8269 | 122.545 | 122.8296 | 122.1917 | 3.1407 | -122.9645
866.875 | 122.818 | -2.8152 | 120.0073 | -0.00068679 | 0.00056201 | -0.0011197 | 0.019443 | -0.00019664 | 0.016988 | 0.0014498 | 0.00025649 | 0.23242 | 0.0002992 | 0.0060469 | 0.062374 | -2.0226 | -1.5919 | -1.8123 | -1.5732 | -1.4741 | -1.4422 | -2.728 | 119.7435 | 0.34376 | -2.7303 | 119.7664 | 120.0647 | 119.3536 | -2.8657 | 0.087256 | -121.5805 | 0.79265 | 1.003 | 0.91574 | -121.4814 | -121.4496 | -0.050404 | -0.24095 | 122.5587 | 0.084929 | 0.13533 | 0.057341 | -0.65372 | 1.242 | 1.3412 | 1.373 | 1.2233 | -122.7353 | 122.5816 | 122.8799 | 122.1689 | 3.159 | -122.873
868.6094 | 122.8592 | -2.8473 | 119.9295 | -0.00068679 | 0.00056201 | -0.0013333 | 0.019016 | 1.7156e-05 | 0.016988 | 0.0014498 | 0.00047009 | 0.23178 | 0.0002992 | 0.0058333 | 0.062588 | -2.0867 | -1.656 | -1.8855 | -1.6373 | -1.5427 | -1.5018 | -2.815 | 119.6611 | 0.33003 | -2.8127 | 119.6977 | 119.9822 | 119.4452 | -2.9389 | 0.032299 | -121.5668 | 0.76059 | 0.96179 | 0.92949 | -121.4722 | -121.4313 | -0.091622 | -0.23181 | 122.5083 | 0.034556 | 0.12618 | 0.052746 | -0.48433 | 1.21 | 1.3046 | 1.3455 | 1.1912 | -122.7445 | 122.545 | 122.8295 | 122.2925 | 3.1773 | -122.8684
870.3594 | 122.905 | -2.8564 | 119.8746 | -0.0083178 | 0.00098941 | -0.0015471 | 0.018802 | -0.00041024 | 0.016775 | 0.0014498 | 0.00068369 | 0.12239 | 8.5404e-05 | 0.0056197 | 0.062588 | -2.1233 | -1.6835 | -1.913 | -1.6693 | -1.5611 | -1.5384 | -2.8425 | 119.6611 | 0.36208 | -2.8402 | 119.6748 | 119.9548 | 119.2162 | -2.9755 | 0.013981 | -121.5439 | 0.73312 | 0.94347 | 0.92949 | -121.4356 | -121.413 | -0.1191 | -0.19977 | 122.5175 | 0.016238 | 0.13534 | 0.080205 | -0.65833 | 1.1871 | 1.2954 | 1.3181 | 1.1729 | -122.717 | 122.5312 | 122.8112 | 122.0727 | 3.2185 | -122.8501
872.0312 | 122.8775 | -2.8931 | 119.8929 | -0.00068679 | 0.001203 | -0.0019745 | 0.018588 | -0.00019664 | 0.017202 | 0.0090803 | 4.2686e-05 | 0.082006 | 0.0007264 | 0.0054059 | 0.06216 | -2.1508 | -1.6881 | -1.9359 | -1.6968 | -1.5839 | -1.5567 | -2.8516 | 119.6565 | 0.39871 | -2.8631 | 119.6473 | 119.941 | 119.2483 | -2.9939 | 0.041444 | -121.5897 | 0.74227 | 0.9572 | 0.91576 | -121.4768 | -121.4496 | -0.10079 | -0.24555 | 122.5495 | 0.029966 | 0.13076 | 0.048159 | -0.64459 | 1.1963 | 1.3091 | 1.3364 | 1.205 | -122.7445 | 122.5404 | 122.8341 | 122.1414 | 3.2918 | -122.8867
873.7656 | 122.8729 | -2.9892 | 119.8013 | -0.00068679 | 0.001203 | -0.0015471 | 0.018588 | -0.00019664 | 0.016775 | -0.0061807 | 0.00047009 | 0.07816 | 0.0005128 | 0.0060469 | 0.062374 | -2.105 | -1.6423 | -1.8718 | -1.6465 | -1.5336 | -1.5018 | -2.8837 | 119.6244 | 0.40329 | -2.8952 | 119.6199 | 119.9136 | 119.2895 | -3.0305 | 0.10552 | -121.4478 | 0.88419 | 1.1174 | 1.0119 | -121.3349 | -121.3031 | -0.041291 | -0.18147 | 122.6136 | 0.094046 | 0.13534 | 0.11224 | -0.51183 | 1.3427 | 1.4556 | 1.4874 | 1.3469 | -122.685 | 122.6091 | 122.9028 | 122.2787 | 3.3925 | -122.8318
875.5 | 122.8729 | -2.948 | 119.8059 | -0.0083178 | 0.0016304 | -0.0017607 | 0.018375 | 1.7156e-05 | 0.017202 | -0.013811 | 0.00047009 | 0.071537 | 0.0002992 | 0.0062607 | 0.062588 | -2.1371 | -1.6744 | -1.9267 | -1.6739 | -1.5748 | -1.5384 | -2.8883 | 119.6198 | 0.40786 | -2.8906 | 119.6153 | 119.909 | 119.2666 | -3.0259 | 0.059744 | -121.4798 | 0.81094 | 1.0213 | 0.96154 | -121.3807 | -121.3443 | -0.077912 | -0.19063 | 122.5678 | 0.057426 | 0.13534 | 0.10308 | -0.5393 | 1.2741 | 1.3732 | 1.4096 | 1.2736 | -122.6942 | 122.5633 | 122.857 | 122.2146 | 3.3559 | -122.8318
877.25 | 122.7905 | -2.9434 | 119.87 | 0.0069442 | 0.001844 | -0.0017607 | 0.017947 | -0.00041024 | 0.016988 | 0.0014498 | 0.00025649 | 0.12111 | 0.0002992 | 0.0058333 | 0.06216 | -2.16 | -1.6698 | -1.9633 | -1.6968 | -1.5931 | -1.5704 | -2.9066 | 119.5878 | 0.39871 | -2.9089 | 119.5878 | 119.8769 | 119.1521 | -3.0442 | 0.036851 | -121.5668 | 0.78347 | 0.98009 | 0.94323 | -121.4631 | -121.4404 | -0.1008 | -0.28218 | 122.5312 | 0.034533 | 0.13534 | 0.006947 | -0.71785 | 1.2466 | 1.3503 | 1.373 | 1.2736 | -122.7766 | 122.5312 | 122.8204 | 122.0956 | 3.3421 | -122.9142
878.9844 | 122.8958 | -2.9205 | 119.8196 | -0.00068679 | 0.0016304 | -0.0015471 | 0.017947 | -0.00041024 | 0.016988 | -0.0061807 | 0.00047009 | 0.11277 | 8.5404e-05 | 0.0058333 | 0.06216 | -2.1371 | -1.624 | -1.9267 | -1.6693 | -1.5565 | -1.5338 | -2.8928 | 119.6107 | 0.41244 | -2.8952 | 119.6015 | 119.8998 | 119.2712 | -3.0259 | 0.027699 | -121.489 | 0.78347 | 0.99382 | 0.96612 | -121.3761 | -121.3534 | -0.10538 | -0.2181 | 122.5312 | 0.025381 | 0.13076 | 0.080194 | -0.54845 | 1.2512 | 1.3641 | 1.3867 | 1.2965 | -122.7125 | 122.5221 | 122.8204 | 122.1917 | 3.333 | -122.8456
880.6719 | 122.9004 | -2.7878 | 119.9432 | -0.00068679 | 0.0020576 | -0.0017607 | 0.017306 | -0.00062384 | 0.016988 | 0.0014498 | 0.00025649 | 0.1117 | 8.5404e-05 | 0.0058333 | 0.061947 | -2.0318 | -1.4821 | -1.8077 | -1.5549 | -1.4512 | -1.4239 | -2.7921 | 119.7023 | 0.44449 | -2.7898 | 119.7114 | 119.9914 | 119.2712 | -2.9298 | -0.004315 | -121.4981 | 0.75602 | 0.98011 | 0.98442 | -121.3944 | -121.3672 | -0.14197 | -0.23181 | 122.49 | -0.00206 | 0.13991 | 0.04817 | -0.67205 | 1.2329 | 1.3366 | 1.3639 | 1.3057 | -122.7353 | 122.4992 | 122.7792 | 122.059 | 3.2323 | -122.873
882.4219 | 122.8592 | -2.8427 | 119.8837 | 0.0069442 | 0.0020576 | -0.0015471 | 0.017734 | -0.00019664 | 0.016775 | 0.0014498 | 0.00025649 | 0.078588 | -0.0001282 | 0.0058333 | 0.062374 | -2.1325 | -1.5416 | -1.8535 | -1.6281 | -1.529 | -1.4972 | -2.8333 | 119.6702 | 0.46739 | -2.8356 | 119.6656 | 119.9502 | 119.2437 | -2.9664 | 0.009405 | -121.5119 | 0.71023 | 0.98926 | 0.97985 | -121.4127 | -121.3809 | -0.12367 | -0.21808 | 122.5129 | 0.007084 | 0.13076 | 0.066471 | -0.64001 | 1.2146 | 1.3137 | 1.3455 | 1.3011 | -122.717 | 122.5084 | 122.7929 | 122.0864 | 3.3101 | -122.8501
884.1562 | 122.8867 | -2.8564 | 119.8791 | -0.0083178 | 0.0020576 | -0.0017607 | 0.017093 | 1.7156e-05 | 0.016988 | -0.013811 | 0.00047009 | 0.087348 | 0.0005128 | 0.0060469 | 0.061947 | -2.1233 | -1.5507 | -1.8443 | -1.6373 | -1.529 | -1.488 | -2.8608 | 119.6336 | 0.49486 | -2.8631 | 119.629 | 119.909 | 119.2254 | -2.9893 | -0.004335 | -121.5164 | 0.73312 | 1.0121 | 1.0165 | -121.4082 | -121.3672 | -0.13283 | -0.25013 | 122.49 | -0.006655 | 0.12618 | 0.029842 | -0.65375 | 1.2191 | 1.3274 | 1.3684 | 1.3057 | -122.7399 | 122.4855 | 122.7654 | 122.0818 | 3.3513 | -122.8684
885.8438 | 122.8821 | -2.7969 | 119.9341 | -0.00068679 | 0.0022714 | -0.0015471 | 0.017306 | -0.00041024 | 0.016988 | -0.0061807 | 0.00025649 | 0.072605 | 0.0002992 | 0.0056197 | 0.06216 | -2.0546 | -1.5004 | -1.7619 | -1.5503 | -1.4512 | -1.4239 | -2.7784 | 119.7114 | 0.47654 | -2.7807 | 119.7069 | 120.0006 | 119.2666 | -2.9069 | 0.018576 | -121.4844 | 0.74229 | 1.035 | 1.0165 | -121.3852 | -121.358 | -0.10992 | -0.22723 | 122.5084 | 0.016253 | 0.12618 | 0.066482 | -0.66747 | 1.2466 | 1.3458 | 1.373 | 1.2966 | -122.7124 | 122.5038 | 122.7975 | 122.0635 | 3.2735 | -122.8409
887.5781 | 122.7676 | -2.8244 | 119.957 | 0.0069442 | 0.002485 | -0.0013333 | 0.017093 | -0.00019664 | 0.017416 | 0.0014498 | 0.00068369 | 0.068759 | 0.0007264 | 0.0058333 | 0.062801 | -2.0226 | -1.4363 | -1.7756 | -1.5183 | -1.4191 | -1.3827 | -2.7555 | 119.7343 | 119.3353 | -2.7532 | 119.7297 | 120.0189 | 119.2666 | -2.8977 | 0.068937 | -121.4752 | 0.8018 | 1.0488 | 0.97984 | -121.3761 | -121.3397 | -0.073301 | -0.22723 | 122.5587 | 0.071191 | 0.14449 | 0.061908 | -0.69036 | 1.3061 | 1.4053 | 1.4417 | 1.3881 | -122.7124 | 122.5541 | 122.8433 | 122.091 | 122.1597 | -122.8547
889.3125 | 122.8455 | -2.8473 | 119.8837 | -0.00068679 | 0.0022714 | -0.0013333 | 0.017093 | -0.00019664 | 0.017202 | 0.0014498 | 0.00068369 | 0.066836 | 0.0002992 | 0.0056197 | 0.062588 | -2.1187 | -1.5141 | -1.8763 | -1.6052 | -1.5015 | -1.4697 | -2.847 | 119.6382 | 119.3215 | -2.8631 | 119.6244 | 119.9136 | 119.1842 | -2.9939 | 0.000247 | -121.489 | 0.72854 | 0.97094 | 0.9707 | -121.3853 | -121.3534 | -0.14657 | -0.25929 | 122.4854 | -0.01581 | 0.13076 | 0.029843 | -0.69953 | 1.242 | 1.3458 | 1.3776 | 1.3332 | -122.7308 | 122.4717 | 122.7609 | 122.0315 | 122.1688 | -122.8776
890.9844 | 122.7448 | -2.7878 | 119.989 | 0.0069442 | 0.002485 | -0.0015471 | 0.016451 | -0.00041024 | 0.017416 | -0.0061807 | 0.00047009 | 0.067691 | 8.5404e-05 | 0.0060469 | 0.062374 | -2.0089 | -1.45 | -1.7848 | -1.5091 | -1.41 | -1.3781 | -2.7646 | 119.7297 | 119.4223 | -2.7578 | 119.7252 | 119.996 | 119.2803 | -2.9023 | 0.023158 | -121.4981 | 0.77892 | 1.003 | 0.97984 | -121.399 | -121.3671 | -0.1145 | -0.26385 | 122.5175 | 0.029991 | 0.14449 | 0.006971 | -0.70867 | 1.2787 | 1.3778 | 1.4097 | 1.3378 | -122.7536 | 122.5129 | 122.7838 | 122.0681 | 122.21 | -122.8913
892.7344 | 122.85 | -2.8107 | 119.957 | 0.0069442 | 0.0029124 | -0.0013333 | 0.016451 | -0.00019664 | 0.017202 | 0.0090803 | 0.00047009 | 0.083074 | 0.0002992 | 0.0058333 | 0.062588 | -2.0272 | -1.4775 | -1.7756 | -1.5137 | -1.41 | -1.3827 | -2.7555 | 119.7343 | 119.4452 | -2.7532 | 119.7206 | 120.0189 | 119.317 | -2.8885 | 0.055204 | -121.4707 | 0.78349 | 1.035 | 0.97984 | -121.3669 | -121.3397 | -0.077876 | -0.23638 | 122.545 | 0.057458 | 0.13533 | 0.061908 | -0.63999 | 1.297 | 1.4007 | 1.428 | 1.3332 | -122.7124 | 122.5313 | 122.8295 | 122.1276 | 122.2558 | -122.8455
894.4844 | 122.9004 | -2.774 | 119.8929 | -0.00068679 | 0.0026988 | -0.0019745 | 0.017947 | -0.00041024 | 0.018057 | -0.013811 | 0.00068369 | 0.092048 | 0.0002992 | 0.0058333 | 0.06216 | -0.88258 | -1.0563 | -1.2949 | -1.0284 | -0.93374 | -0.8928 | -2.2152 | 120.2792 | 119.9946 | -2.1992 | 120.2792 | 120.5637 | 119.9351 | -2.3528 | 0.5589 | -120.9213 | 1.8915 | 1.4791 | 0.92025 | -120.8266 | -120.7857 | 0.42123 | 0.38628 | 123.0532 | 0.57486 | 0.15364 | 0.67085 | 0.042203 | 1.7457 | 1.8403 | 1.8813 | 1.7178 | -122.108 | 123.0532 | 123.3378 | 122.7091 | 122.7687 | -122.2457
896.1719 | 122.8317 | -2.9022 | 119.8151 | 0.0069442 | 0.0033398 | -0.0017607 | 0.016451 | -0.00019664 | 0.017629 | 0.0014498 | 0.00068369 | 0.076024 | 0.0007264 | 0.0060469 | 0.06216 | -2.1004 | -1.5324 | -1.8626 | -1.6007 | -1.4924 | -1.4605 | -2.815 | 119.6702 | 119.3811 | -2.8173 | 119.6611 | 119.941 | 119.2437 | -2.9526 | 0.087231 | -121.4157 | 0.80179 | 1.0396 | 0.95238 | -121.3074 | -121.2756 | -0.050426 | -0.154 | 122.5724 | 0.084909 | 0.13533 | 0.12598 | -0.57135 | 1.3016 | 1.4099 | 1.4417 | 1.3698 | -122.6301 | 122.5633 | 122.8433 | 122.1459 | 122.2833 | -122.7677
897.9062 | 122.818 | -2.7374 | 119.9982 | -0.00068679 | 0.0026988 | -0.0013333 | 0.016451 | -0.00041024 | 0.017202 | 0.0014498 | 0.00025649 | 0.086066 | 0.0005128 | 0.0060469 | 0.061947 | -2.0821 | -1.5278 | -1.8306 | -1.564 | -1.4649 | -1.4285 | -2.7417 | 119.7389 | 119.4864 | -2.7349 | 119.7343 | 120.0235 | 119.3673 | -2.8702 | -0.004301 | -121.5622 | 0.65531 | 0.90686 | 0.91116 | -121.4631 | -121.4267 | -0.1328 | -0.26385 | 122.4763 | 0.002531 | 0.13533 | 0.025288 | -0.63083 | 1.1734 | 1.2725 | 1.3089 | 1.2096 | -122.7399 | 122.4718 | 122.7609 | 122.1048 | 122.2238 | -122.8684
899.5781 | 122.731 | -1.918 | 120.8862 | -0.00068679 | 0.0014166 | -0.0032565 | 0.019443 | -0.00019664 | 0.017843 | 0.0014498 | 0.00047009 | 0.11021 | 8.5404e-05 | 0.0058333 | 0.062374 | -0.099677 | -0.82274 | -1.0156 | -0.77198 | -0.67732 | -0.6364 | -1.8397 | 120.6134 | 120.3746 | -1.8375 | 120.6226 | 120.9071 | 120.1869 | -1.9819 | 0.07835 | -121.6582 | 1.8184 | 0.9024 | 0.82405 | -121.5636 | -121.5226 | -0.063909 | -0.26368 | 122.5315 | 0.080561 | 0.14447 | 0.020897 | -0.69932 | 1.146 | 1.2407 | 1.2816 | 1.0953 | -122.7259 | 122.5406 | 122.8252 | 122.1049 | 122.2927 | -122.8682
901.3281 | 122.7722 | -1.9913 | 120.8267 | 0.0069442 | 0.001203 | -0.0030429 | 0.019443 | -0.00019664 | 0.017843 | 0.0090803 | 0.00025649 | 0.11641 | 8.5404e-05 | 0.0060469 | 0.061733 | -0.10426 | -0.85937 | -1.066 | -0.81777 | -0.71395 | -0.68218 | -1.9175 | 120.5493 | 120.3105 | -1.9107 | 120.5447 | 120.8384 | 120.1365 | -2.046 | 0.07375 | -121.6445 | 1.887 | 0.92528 | 0.85153 | -121.5407 | -121.5089 | -0.054771 | -0.28201 | 122.5406 | 0.080543 | 0.13531 | 0.011727 | -0.69018 | 1.1735 | 1.2773 | 1.3091 | 1.1319 | -122.7442 | 122.536 | 122.8297 | 122.1278 | 122.3018 | -122.8728
903.0625 | 122.731 | -1.9592 | 120.8359 | 0.0069442 | 0.001844 | -0.0026155 | 0.019657 | -0.00041024 | 0.017629 | 0.0014498 | 0.00047009 | 0.11683 | 0.0002992 | 0.0060469 | 0.062801 | -0.044736 | -0.83648 | -1.0339 | -0.7903 | -0.6819 | -0.65929 | -1.8855 | 120.5768 | 120.3517 | -1.8787 | 120.5859 | 120.8659 | 120.3105 | -2.0231 | 0.07376 | -121.6262 | 1.9145 | 0.92529 | 0.85153 | -121.5178 | -121.4952 | -0.06392 | -0.24995 | 122.536 | 0.080551 | 0.14447 | 0.030044 | -0.52534 | 1.1689 | 1.2773 | 1.2999 | 1.1228 | -122.7213 | 122.5452 | 122.8251 | 122.2698 | 122.311 | -122.859
904.7344 | 122.7814 | -2.0142 | 120.7718 | -0.00068679 | 0.001844 | -0.0032565 | 0.019443 | -0.00019664 | 0.017843 | 0.0090803 | 0.00068369 | 0.12153 | 0.0005128 | 0.0062607 | 0.062374 | -0.026423 | -0.89142 | -1.0843 | -0.84066 | -0.73685 | -0.70508 | -1.9587 | 120.5035 | 120.2648 | -1.9519 | 120.5127 | 120.7927 | 120.0862 | -2.0873 | 0.055428 | -121.6124 | 1.9877 | 0.92985 | 0.87443 | -121.5086 | -121.4769 | -0.073092 | -0.25912 | 122.5177 | 0.062223 | 0.13531 | 0.020872 | -0.68561 | 1.1735 | 1.2773 | 1.3091 | 1.1227 | -122.7305 | 122.5268 | 122.8068 | 122.1003 | 122.2789 | -122.859
906.4688 | 122.7402 | -1.9913 | 120.8267 | -0.015949 | 0.001844 | -0.0030429 | 0.019229 | -0.00041024 | 0.017843 | 0.0014498 | 0.00047009 | 0.10529 | 8.5404e-05 | 0.0056197 | 0.06216 | -0.031001 | -0.83648 | -1.0477 | -0.80403 | -0.69106 | -0.66387 | -1.9221 | 120.5402 | 120.306 | -1.9062 | 120.5447 | 120.8384 | 120.0908 | -2.0598 | 0.069171 | -121.6308 | 1.9603 | 0.94359 | 0.87442 | -121.5178 | -121.4906 | -0.068507 | -0.28201 | 122.5314 | 0.085122 | 0.15363 | 0.011727 | -0.73596 | 1.1872 | 1.3002 | 1.3274 | 1.1548 | -122.7488 | 122.536 | 122.8297 | 122.082 | 122.2972 | -122.8865
908.2031 | 122.7219 | -2.0279 | 120.7718 | 0.0069442 | 0.0020576 | -0.0030429 | 0.019229 | -0.00041024 | 0.017843 | -0.0061807 | 0.00025649 | 0.10786 | 8.5404e-05 | 0.0060469 | 0.062588 | -0.026423 | -0.82732 | -1.0523 | -0.79487 | -0.69564 | -0.66845 | -1.9542 | 120.5035 | 120.2785 | -1.9428 | 120.5035 | 120.7927 | 120.0541 | -2.0827 | 0.07374 | -121.5667 | 2.0015 | 0.97564 | 0.9019 | -121.4674 | -121.4402 | -0.05478 | -0.26828 | 122.5314 | 0.085113 | 0.13989 | 0.020872 | -0.71766 | 1.233 | 1.3323 | 1.3594 | 1.2006 | -122.7259 | 122.5314 | 122.8206 | 122.082 | 122.3064 | -122.8545
909.875 | 122.7905 | -1.9684 | 120.7672 | -0.00068679 | 0.0022714 | -0.0028291 | 0.018802 | -0.00041024 | 0.017629 | -0.0061807 | 0.00025649 | 0.08692 | 8.5404e-05 | 0.0060469 | 0.06216 | -0.03558 | -0.77238 | -1.0111 | -0.77198 | -0.66358 | -0.61808 | -1.9267 | 120.5402 | 120.2922 | -1.9107 | 120.5447 | 120.8293 | 120.2144 | -2.0598 | 0.041704 | -121.5392 | 1.9328 | 0.95733 | 0.91563 | -121.4308 | -121.3853 | -0.091395 | -0.2225 | 122.5085 | 0.057655 | 0.14905 | 0.062079 | -0.55283 | 1.1964 | 1.3048 | 1.3503 | 1.196 | -122.6939 | 122.5131 | 122.7977 | 122.1828 | 122.2606 | -122.827
911.625 | 122.8775 | -1.9089 | 120.7809 | -0.00068679 | 0.0020576 | -0.0026155 | 0.018588 | -0.00019664 | 0.017843 | 0.0014498 | 0.00025649 | 0.072178 | 0.0002992 | 0.0058333 | 0.06216 | -0.040158 | -0.77238 | -1.0111 | -0.75825 | -0.64985 | -0.6364 | -1.9084 | 120.5631 | 120.306 | -1.8924 | 120.5539 | 120.843 | 120.1778 | -2.0369 | 0.000511 | -121.5392 | 1.8687 | 0.89782 | 0.89731 | -121.4308 | -121.4173 | -0.12801 | -0.22707 | 122.4719 | 0.016461 | 0.14447 | 0.062082 | -0.60319 | 1.1506 | 1.259 | 1.2725 | 1.1365 | -122.6893 | 122.4627 | 122.7519 | 122.0866 | 122.2148 | -122.8178
913.3594 | 122.7219 | -2.0142 | 120.7809 | -0.0083178 | 0.0022714 | -0.0028291 | 0.017947 | -0.00041024 | 0.017416 | 0.0014498 | 0.00047009 | 0.11769 | 0.0005128 | 0.0060469 | 0.062374 | -0.03558 | -0.7678 | -1.0385 | -0.78572 | -0.6819 | -0.65471 | -1.9404 | 120.5173 | 120.2922 | -1.9153 | 120.531 | 120.8156 | 120.2785 | -2.0598 | 0.073744 | -121.5667 | 1.9786 | 0.97564 | 0.90189 | -121.4628 | -121.4357 | -0.045619 | -0.24996 | 122.5314 | 0.098853 | 0.14447 | 0.03461 | -0.50246 | 1.2284 | 1.3323 | 1.3594 | 1.2464 | -122.7214 | 122.5451 | 122.8297 | 122.2926 | 122.3064 | -122.8407
915.0938 | 122.8317 | -2.0096 | 120.7031 | -0.00068679 | 0.0029124 | -0.0032565 | 0.018161 | 1.7156e-05 | 0.017843 | 0.0014498 | 0.00025649 | 0.10487 | 8.5404e-05 | 0.0058333 | 0.062374 | -0.026423 | -0.81816 | -1.0935 | -0.84066 | -0.73685 | -0.70508 | -1.9679 | 120.4761 | 120.251 | -1.9611 | 120.4852 | 120.7789 | 120.0358 | -2.1056 | 0.041693 | -121.5438 | 1.9832 | 0.91612 | 0.87443 | -121.44 | -121.4082 | -0.095984 | -0.21793 | 122.4856 | 0.048489 | 0.14447 | 0.075802 | -0.66731 | 1.1689 | 1.2727 | 1.3045 | 1.1914 | -122.671 | 122.4948 | 122.7885 | 122.0454 | 122.2606 | -122.8087
916.7656 | 122.8592 | -2.0279 | 120.6345 | -0.0083178 | 0.0029124 | -0.0028291 | 0.018588 | -0.00019664 | 0.017843 | 0.0090803 | 0.00025649 | 0.11042 | 8.5404e-05 | 0.0060469 | 0.06216 | -0.040158 | -0.80901 | -1.0843 | -0.82692 | -0.72311 | -0.69592 | -1.9862 | 120.4623 | 120.2235 | -1.9794 | 120.4623 | 120.7469 | 120.0862 | -2.1193 | 0.041687 | -121.4614 | 1.9877 | 0.94359 | 0.9019 | -121.3576 | -121.3304 | -0.091411 | -0.17216 | 122.4902 | 0.048484 | 0.1399 | 0.11242 | -0.54828 | 1.201 | 1.3048 | 1.332 | 1.2189 | -122.6207 | 122.4902 | 122.7748 | 122.1141 | 122.2514 | -122.7538
918.5 | 122.7173 | -2.0508 | 120.7214 | -0.00068679 | 0.003126 | -0.0030429 | 0.017947 | -0.00019664 | 0.017629 | 0.0014498 | 0.00025649 | 0.094398 | 8.5404e-05 | 0.0062607 | 0.062374 | -0.031001 | -0.83648 | -1.1118 | -0.85897 | -0.75974 | -0.72797 | -2.0228 | 120.4257 | 120.1869 | -2.0115 | 120.4348 | 120.7148 | 120.1778 | -2.1514 | 0.027944 | -121.5804 | 2.0198 | 0.93901 | 0.91106 | -121.4812 | -121.4494 | -0.10057 | -0.2866 | 122.4765 | 0.039321 | 0.1399 | -0.00661 | -0.54368 | 1.1918 | 1.291 | 1.3228 | 1.2143 | -122.7443 | 122.4856 | 122.7656 | 122.2285 | 122.2377 | -122.8728
920.1875 | 122.8363 | -2.0325 | 120.6619 | -0.00068679 | 0.003126 | -0.0034701 | 0.018161 | -0.00062384 | 0.017843 | -0.013811 | 0.00047009 | 0.081579 | 0.0002992 | 0.0058333 | 0.06216 | -0.03558 | -0.84106 | -1.1301 | -0.86355 | -0.7689 | -0.7417 | -2.032 | 120.4165 | 120.164 | -2.0252 | 120.4119 | 120.7011 | 120.0816 | -2.1697 | 0.000476 | -121.5255 | 1.9969 | 0.90238 | 0.90191 | -121.4308 | -121.4036 | -0.1372 | -0.24999 | 122.449 | 0.007275 | 0.14447 | 0.039164 | -0.58032 | 1.1689 | 1.2636 | 1.2908 | 1.1914 | -122.6939 | 122.4444 | 122.7336 | 122.1141 | 122.1965 | -122.8316
921.9375 | 122.7493 | -2.1194 | 120.6665 | 0.0069442 | 0.0033398 | -0.0032565 | 0.018588 | -0.00062384 | 0.017843 | -0.0061807 | 0.00047009 | 0.10081 | 8.5404e-05 | 0.0060469 | 0.06216 | -0.03558 | -0.85937 | -1.153 | -0.89102 | -0.80095 | -0.75544 | -2.0549 | 120.3982 | 120.1594 | -2.0344 | 120.3982 | 120.6828 | 119.958 | -2.1971 | 0.064557 | -121.5575 | 2.0839 | 0.96647 | 0.90191 | -121.4675 | -121.4219 | -0.077698 | -0.2683 | 122.5177 | 0.085092 | 0.16279 | 0.016272 | -0.70853 | 1.2284 | 1.3185 | 1.364 | 1.2601 | -122.7214 | 122.5177 | 122.8022 | 122.0774 | 122.2789 | -122.8636
923.6719 | 122.7173 | -2.1469 | 120.6345 | -0.00068679 | 0.0033398 | -0.0034701 | 0.017734 | -0.00041024 | 0.017843 | 0.0014498 | 4.2686e-05 | 0.10829 | 0.0002992 | 0.0058333 | 0.061947 | -0.026423 | -0.85937 | -1.1576 | -0.90475 | -0.79637 | -0.7646 | -2.0778 | 120.3753 | 120.1365 | -2.0664 | 120.3707 | 120.6599 | 120.0999 | -2.2017 | 0.069128 | -121.5392 | 2.1205 | 0.98935 | 0.92023 | -121.4308 | -121.3991 | -0.05481 | -0.26373 | 122.5222 | 0.080507 | 0.13532 | 0.025423 | -0.53454 | 1.2422 | 1.3505 | 1.3823 | 1.2875 | -122.7122 | 122.5176 | 122.8068 | 122.2468 | 122.2835 | -122.8362
925.3438 | 122.7493 | -2.1698 | 120.5841 | 0.0069442 | 0.0029124 | -0.0026155 | 0.016879 | -0.00019664 | 0.017843 | 0.0014498 | 0.00025649 | 0.086707 | 8.5404e-05 | 0.0060469 | 0.061947 | -0.026423 | -0.81359 | -1.1667 | -0.8956 | -0.78722 | -0.76002 | -2.0961 | 120.3524 | 120.1045 | -2.0847 | 120.3524 | 120.6416 | 119.9305 | -2.2338 | 0.0737 | -121.4797 | 2.1434 | 1.0031 | 0.92939 | -121.3713 | -121.3441 | -0.063974 | -0.23169 | 122.5222 | 0.08508 | 0.14905 | 0.057462 | -0.6536 | 1.2742 | 1.3826 | 1.4098 | 1.3562 | -122.6802 | 122.5222 | 122.8114 | 122.1003 | 122.2743 | -122.8179
927.0938 | 122.8134 | -2.0645 | 120.639 | -0.00068679 | 0.004408 | -0.0024017 | 0.015383 | -0.00019664 | 0.017416 | 0.0090803 | 0.00025649 | 0.097176 | 8.5404e-05 | 0.0058333 | 0.06216 | -0.35607 | -0.83648 | -1.272 | -1.0238 | -0.92 | -0.88822 | -2.0778 | 120.3616 | 120.1274 | -2.0664 | 120.3662 | 120.6416 | 120.132 | -2.2155 | -0.01327 | -121.6628 | 1.7084 | 0.7925 | 0.80577 | -121.559 | -121.5273 | -0.15095 | -0.27288 | 122.4261 | -0.001891 | 0.14905 | 0.00253 | -0.50707 | 1.0407 | 1.1445 | 1.1763 | 1.228 | -122.7168 | 122.4307 | 122.7061 | 122.1965 | 122.1919 | -122.8545
928.7656 | 122.8043 | -1.9501 | 120.7626 | -0.00068679 | 0.0048354 | -0.0024017 | 0.01581 | -0.00019664 | 0.018057 | -0.0061807 | 0.00047009 | 0.11726 | 8.5404e-05 | 0.0060469 | 0.06216 | -0.026423 | -0.75406 | -1.1896 | -0.96427 | -0.86964 | -0.83328 | -1.8534 | 120.5722 | 120.3792 | -1.8604 | 120.5768 | 120.8522 | 120.338 | -2.0003 | 0.096656 | -121.7269 | 1.9236 | 0.76047 | 0.66381 | -121.6323 | -121.5959 | -0.050181 | -0.18587 | 122.5223 | 0.08971 | 0.13989 | 0.08955 | -0.42463 | 0.9858 | 1.0804 | 1.1168 | 1.196 | -122.6161 | 122.5268 | 122.8023 | 122.2881 | 122.3293 | -122.7629
930.5 | 122.7539 | -1.9135 | 120.8313 | 0.0069442 | 0.0046218 | -0.0024017 | 0.015597 | -0.00062384 | 0.01827 | -0.0061807 | 0.00047009 | 0.11555 | 0.0005128 | 0.0058333 | 0.06216 | -0.026423 | -0.74491 | -1.1896 | -0.9597 | -0.86048 | -0.8287 | -1.9175 | 120.5081 | 120.3151 | -1.9153 | 120.5172 | 120.8018 | 120.251 | -2.0598 | -0.00407 | -121.791 | 1.887 | 0.72385 | 0.72792 | -121.6918 | -121.66 | -0.14633 | -0.31405 | 122.4216 | -0.001855 | 0.14447 | -0.029479 | -0.58029 | 0.95376 | 1.053 | 1.0848 | 1.1685 | -122.7488 | 122.4307 | 122.7153 | 122.1645 | 122.2286 | -122.8911
932.25 | 122.8363 | -2.0187 | 120.6436 | -0.015949 | 0.0050492 | -0.0026155 | 0.01581 | -0.00062384 | 0.018057 | 0.0014498 | 0.00047009 | 0.11747 | 8.5404e-05 | 0.0060469 | 0.061947 | -0.031001 | -0.75864 | -1.2033 | -0.9597 | -0.85132 | -0.82412 | -1.9725 | 120.4623 | 120.2235 | -1.9519 | 120.4715 | 120.7515 | 120.2785 | -2.101 | 0.046269 | -121.6033 | 1.9877 | 0.8154 | 0.76913 | -121.4949 | -121.4677 | -0.08225 | -0.17216 | 122.4811 | 0.066801 | 0.14905 | 0.10784 | -0.36513 | 1.059 | 1.1674 | 1.1946 | 1.2601 | -122.6161 | 122.4902 | 122.7702 | 122.2972 | 122.2423 | -122.7446
933.9375 | 122.7402 | -2.1103 | 120.607 | -0.00068679 | 0.0039808 | -0.0019745 | 0.01581 | -0.00062384 | 0.017843 | -0.0061807 | 0.00047009 | 0.11876 | 0.0002992 | 0.0056197 | 0.06216 | -0.031001 | -0.76322 | -1.1988 | -0.94138 | -0.83758 | -0.79665 | -2.032 | 120.3982 | 120.1869 | -2.0206 | 120.4074 | 120.6782 | 120.077 | -2.1605 | 0.078296 | -121.5484 | 2.0793 | 0.91153 | 0.83323 | -121.4446 | -121.4036 | -0.050222 | -0.19963 | 122.5085 | 0.089673 | 0.1399 | 0.071202 | -0.52997 | 1.1689 | 1.2727 | 1.3136 | 1.3471 | -122.639 | 122.5177 | 122.7885 | 122.1873 | 122.2972 | -122.7675
935.6875 | 122.7585 | -2.1011 | 120.6528 | 0.0069442 | 0.004408 | -0.0019745 | 0.016024 | -0.00083764 | 0.017629 | -0.0061807 | 0.00025649 | 0.11876 | 0.0002992 | 0.0058333 | 0.061947 | -0.040158 | -0.77696 | -1.2125 | -0.94596 | -0.84216 | -0.81496 | -2.064 | 120.3708 | 120.1686 | -2.0435 | 120.3799 | 120.6736 | 119.9855 | -2.1971 | 0.037088 | -121.5987 | 2.061 | 0.88864 | 0.85155 | -121.4949 | -121.4677 | -0.096009 | -0.27288 | 122.4719 | 0.057624 | 0.15363 | 0.020848 | -0.66732 | 1.1552 | 1.259 | 1.2862 | 1.3242 | -122.7168 | 122.481 | 122.7748 | 122.0866 | 122.2697 | -122.8499
937.375 | 122.7402 | -2.1011 | 120.6299 | -0.0083178 | 0.0041944 | -0.0024017 | 0.016024 | -0.00083764 | 0.017416 | 0.0014498 | 0.00025649 | 0.1038 | 0.0002992 | 0.0060469 | 0.062588 | -0.031001 | -0.76322 | -1.2033 | -0.94138 | -0.83758 | -0.8058 | -2.0457 | 120.3845 | 120.1594 | -2.0435 | 120.3845 | 120.669 | 120.0908 | -2.1834 | 0.055403 | -121.5713 | 2.0701 | 0.89779 | 0.84239 | -121.4675 | -121.4357 | -0.082272 | -0.24541 | 122.4856 | 0.057624 | 0.1399 | 0.039157 | -0.53912 | 1.1598 | 1.2636 | 1.2953 | 1.3379 | -122.6756 | 122.4856 | 122.7702 | 122.1919 | 122.2606 | -122.8133
939.125 | 122.731 | -2.0645 | 120.7077 | 0.0069442 | 0.0039808 | -0.0024017 | 0.01581 | -0.00041024 | 0.017416 | 0.0090803 | 0.00047009 | 0.10722 | 8.5404e-05 | 0.0062607 | 0.062374 | -0.12715 | -0.78153 | -1.2262 | -0.96427 | -0.86048 | -0.83328 | -2.0274 | 120.3982 | 120.2419 | -2.0115 | 120.4028 | 120.6874 | 119.9534 | -2.1651 | 0.037098 | -121.672 | 1.9374 | 0.83828 | 0.80118 | -121.5682 | -121.541 | -0.10058 | -0.30492 | 122.4627 | 0.053054 | 0.15363 | -0.020349 | -0.7543 | 1.1002 | 1.204 | 1.2312 | 1.283 | -122.7351 | 122.4673 | 122.7519 | 122.0179 | 122.3064 | -122.8728
940.8125 | 122.699 | -2.1011 | 120.6436 | 0.0069442 | 0.004408 | -0.0019745 | 0.015597 | 1.7156e-05 | 0.017629 | -0.0061807 | 4.2686e-05 | 0.11341 | 8.5404e-05 | 0.0058333 | 0.06216 | -0.11799 | -0.76322 | -1.2308 | -0.97343 | -0.86964 | -0.84243 | -2.032 | 120.3982 | 120.251 | -2.016 | 120.4028 | 120.6874 | 119.9442 | -2.1697 | 0.06914 | -121.617 | 1.9831 | 0.87033 | 0.80119 | -121.5133 | -121.486 | -0.068536 | -0.24083 | 122.4994 | 0.085096 | 0.15363 | 0.043738 | -0.69937 | 1.1277 | 1.2315 | 1.2587 | 1.3379 | -122.6756 | 122.5039 | 122.7885 | 122.0454 | 122.3522 | -122.8133
942.5625 | 122.6761 | -2.0462 | 120.6894 | -0.00068679 | 0.0048354 | -0.0017607 | 0.015169 | -0.00041024 | 0.017629 | 0.0014498 | 0.0034611 | 0.11256 | 8.5404e-05 | 0.0062607 | 0.06216 | -0.03558 | -0.74033 | -1.2171 | -0.97801 | -0.86964 | -0.84701 | -1.945 | 120.4806 | 120.2144 | -1.9382 | 120.4806 | 120.7606 | 120.1961 | -2.0873 | 0.10121 | -121.6674 | 2.0106 | 0.82913 | 0.72792 | -121.559 | -121.5364 | -0.041048 | -0.20878 | 122.5268 | 0.108 | 0.14905 | 0.07122 | -0.49332 | 1.0682 | 1.1766 | 1.1992 | 1.3059 | -122.6344 | 122.5268 | 122.8068 | 122.2423 | 122.2606 | -122.7766
944.3125 | 122.6944 | -1.9363 | 120.8221 | -0.0083178 | 0.0052628 | -0.0024017 | 0.014742 | -0.00062384 | 0.018057 | -0.0061807 | 0.0028201 | 0.1023 | 0.0056404 | 0.0060469 | 0.062374 | -0.026423 | -0.73575 | -1.2629 | -1.0238 | -0.92 | -0.8928 | -1.9129 | 120.5081 | 120.3243 | -1.9062 | 120.5081 | 120.7881 | 120.0633 | -2.0506 | 0.023397 | -121.8459 | 1.9099 | 0.67348 | 0.65009 | -121.7421 | -121.7149 | -0.11428 | -0.31406 | 122.4445 | 0.03019 | 0.14447 | -0.03406 | -0.75886 | 0.91255 | 1.0163 | 1.0435 | 1.2006 | -122.7351 | 122.4444 | 122.7244 | 121.9996 | 122.2606 | -122.8728
946 | 122.7859 | -1.9775 | 120.7397 | -0.015949 | 0.0056902 | -0.0019745 | 0.014315 | -0.00041024 | 0.018057 | 0.0014498 | 0.0034611 | 0.10294 | 0.012477 | 0.0064743 | 0.062588 | -0.031001 | -0.74948 | -1.2629 | -1.0192 | -0.92 | -0.8928 | -1.9404 | 120.4852 | 120.2739 | -1.9245 | 120.4852 | 120.7743 | 120.3334 | -2.0781 | 0.037123 | -121.759 | 1.9465 | 0.71468 | 0.67756 | -121.6598 | -121.6325 | -0.10056 | -0.25455 | 122.4628 | 0.053074 | 0.15363 | 0.034602 | -0.40632 | 0.95832 | 1.0575 | 1.0847 | 1.2281 | -122.6802 | 122.4627 | 122.7519 | 122.311 | 122.2514 | -122.8178
947.75 | 122.7814 | -1.9867 | 120.7077 | -0.0083178 | 0.0054764 | -0.0019745 | 0.014101 | -0.00019664 | 0.018057 | 0.0014498 | 0.0034611 | 0.1023 | 0.0030766 | 0.0060469 | 0.06216 | -0.031001 | -0.75406 | -1.2949 | -1.0513 | -0.9429 | -0.92027 | -1.9862 | 120.4349 | 120.2419 | -1.9703 | 120.4348 | 120.724 | 120.0908 | -2.1147 | 0.000488 | -121.759 | 1.9557 | 0.69179 | 0.6913 | -121.6506 | -121.628 | -0.12803 | -0.27287 | 122.4215 | 0.016442 | 0.14447 | 0.01628 | -0.61694 | 0.93543 | 1.0438 | 1.0664 | 1.2326 | -122.6939 | 122.4215 | 122.7107 | 122.0775 | 122.2286 | -122.8224
949.4375 | 122.7814 | -2.0142 | 120.6848 | 0.0069442 | 0.0054764 | -0.0019745 | 0.014528 | -0.00041024 | 0.018484 | 0.0014498 | 0.0026065 | 0.10786 | 0.0013674 | 0.0062607 | 0.06216 | -0.040158 | -0.78611 | -1.3315 | -1.1062 | -0.99327 | -0.96606 | -1.9908 | 120.4303 | 120.2419 | -1.9748 | 120.4303 | 120.7148 | 119.9992 | -2.1285 | 0.023375 | -121.791 | 1.974 | 0.68263 | 0.65925 | -121.6781 | -121.6509 | -0.1143 | -0.25456 | 122.4444 | 0.039329 | 0.15363 | 0.030012 | -0.68563 | 0.90796 | 1.0209 | 1.0481 | 1.228 | -122.6756 | 122.4444 | 122.729 | 122.0133 | 122.256 | -122.8133
951.1875 | 122.7081 | -2.037 | 120.694 | -0.00068679 | 0.0056902 | -0.0021881 | 0.013887 | -0.00062384 | 0.017843 | 0.0090803 | 0.0013247 | 0.10679 | 0.015468 | 0.0058333 | 0.06216 | -0.03558 | -0.79985 | -1.3544 | -1.1199 | -1.0162 | -0.98895 | -2.0091 | 120.4028 | 120.2098 | -1.9931 | 120.4165 | 120.6965 | 119.9992 | -2.1468 | 0.027948 | -121.8139 | 2.0015 | 0.68262 | 0.65468 | -121.7101 | -121.6829 | -0.10973 | -0.27745 | 122.4398 | 0.043903 | 0.15363 | 0.002542 | -0.69478 | 0.91711 | 1.0209 | 1.0481 | 1.2372 | -122.7031 | 122.4536 | 122.7336 | 122.0362 | 122.2469 | -122.8407
952.9219 | 122.8043 | -2.1835 | 120.4788 | -0.00068679 | 0.0061174 | -0.0026155 | 0.013674 | -0.00062384 | 0.019125 | 0.0014498 | -0.0065799 | 0.036711 | -0.018716 | 0.0066879 | 0.021994 | -0.049315 | -0.88684 | -1.4826 | -1.2344 | -1.1261 | -1.0988 | -2.1785 | 120.238 | 120.0358 | 119.7548 | 120.2334 | 120.5225 | 119.7931 | 8.3525 | 0.005013 | -121.7132 | 2.1342 | 0.70092 | 0.6959 | -121.6049 | -121.5777 | 10.536 | -0.24544 | 122.4215 | 121.9383 | 111.4023 | 0.043704 | -0.68567 | 0.94913 | 1.0575 | 1.0847 | 1.2967 | -122.6573 | 122.4169 | 122.7061 | 121.9767 | 122.2193 | -112.1264
954.6562 | 122.8226 | -2.1332 | 120.5109 | -0.0083178 | 0.0063312 | -0.0024017 | 0.013887 | -0.00062384 | 0.019125 | -0.0061807 | -0.0070073 | 0.036283 | -0.017861 | 0.0064743 | 0.02178 | -0.058472 | -0.90516 | -1.4826 | -1.2619 | -1.1444 | -1.1217 | -2.151 | 120.2746 | 120.0724 | 120.1439 | 120.2654 | 120.55 | 119.816 | 8.4166 | -0.017868 | -121.7727 | 2.0747 | 0.65056 | 0.66843 | -121.6552 | -121.6326 | 10.5497 | -0.24544 | 122.4078 | 122.2771 | 111.7274 | 0.039132 | -0.69482 | 0.87131 | 0.98881 | 1.0115 | 1.228 | -122.6619 | 122.3986 | 122.6832 | 121.9492 | 122.2056 | -112.0943
956.3906 | 122.8226 | -2.2064 | 120.4651 | -0.0083178 | 0.0061174 | -0.0028291 | 0.013674 | -0.00019664 | 0.018911 | 0.0014498 | -0.012562 | 0.030087 | -0.01017 | 0.0066879 | 0.02178 | -0.044736 | -0.93721 | -1.5238 | -1.2893 | -1.1764 | -1.1492 | -2.1968 | 120.238 | 120.0267 | 120.1302 | 120.2196 | 120.5134 | 119.8847 | 8.4303 | 0.009585 | -121.7544 | 2.1617 | 0.6826 | 0.67302 | -121.6415 | -121.6143 | 10.6367 | -0.24544 | 122.4444 | 122.3366 | 111.6999 | 0.04828 | -0.58037 | 0.91708 | 1.03 | 1.0572 | 1.2692 | -122.6619 | 122.4261 | 122.7198 | 122.0911 | 122.2331 | -112.0348
958.125 | 122.8226 | -2.2385 | 120.4239 | -0.00068679 | 0.0061174 | -0.0026155 | 0.01346 | -0.00062384 | 0.018698 | 0.0090803 | -0.016407 | 0.026241 | -0.01017 | 0.0064743 | 0.021566 | -0.044736 | -0.93263 | -1.5376 | -1.2939 | -1.1856 | -1.1629 | -2.2197 | 120.2151 | 119.9855 | 120.1073 | 120.1922 | 120.4905 | 119.7519 | 8.4715 | 0.018733 | -121.7178 | 2.1937 | 0.70091 | 0.68218 | -121.6095 | -121.5868 | 10.71 | -0.23172 | 122.4535 | 122.3458 | 111.6358 | 0.066586 | -0.67195 | 0.94455 | 1.0529 | 1.0755 | 1.3058 | -122.6436 | 122.4306 | 122.7289 | 121.9904 | 122.2239 | -111.9524
959.7969 | 122.8409 | -2.2476 | 120.4239 | 0.0069442 | 0.0067584 | -0.0024017 | 0.013246 | -0.00062384 | 0.019125 | 0.0014498 | -0.012348 | 0.030728 | -0.012947 | 0.0066879 | 0.02178 | -0.053893 | -0.88684 | -1.5147 | -1.2802 | -1.1673 | -1.14 | -2.1831 | 120.2471 | 120.0312 | 120.1485 | 120.238 | 120.5271 | 119.9946 | 8.4715 | 0.064521 | -121.7041 | 2.1937 | 0.73296 | 0.66843 | -121.5912 | -121.5639 | 10.7191 | -0.18593 | 122.4947 | 122.3961 | 111.677 | 0.10321 | -0.42928 | 0.96744 | 1.0804 | 1.1076 | 1.3608 | -122.607 | 122.4856 | 122.7747 | 122.2422 | 122.2789 | -111.9524
961.5312 | 122.7356 | -2.3209 | 120.4193 | -0.00068679 | 0.0065448 | -0.0024017 | 0.013033 | -0.00062384 | 0.018698 | 0.0014498 | -0.013203 | 0.02966 | -0.002692 | 0.0066879 | 0.021994 | -0.040158 | -0.92805 | -1.5559 | -1.3122 | -1.2039 | -1.1812 | -2.2518 | 120.183 | 120.0404 | 120.0936 | 120.1784 | 120.463 | 119.8939 | 8.4486 | 0.069079 | -121.7315 | 2.2807 | 0.76499 | 0.69592 | -121.6232 | -121.6006 | 10.7695 | -0.24088 | 122.5039 | 122.4144 | 111.645 | 0.043691 | -0.52543 | 1.0086 | 1.117 | 1.1396 | 1.3928 | -122.6711 | 122.4993 | 122.7839 | 122.2147 | 122.3613 | -111.9707
963.2812 | 122.6944 | -2.3163 | 120.4102 | -0.00068679 | 0.0061174 | -0.0026155 | 0.01346 | -0.00041024 | 0.018911 | 0.0014498 | -0.020894 | 0.021114 | 0.011622 | 0.0064743 | 0.021566 | -0.044736 | -0.97841 | -1.5788 | -1.358 | -1.236 | -1.2179 | -2.2701 | 120.1693 | 119.99 | 120.0707 | 120.1555 | 120.4447 | 119.8618 | 8.4807 | 0.046185 | -121.7682 | 2.2715 | 0.73752 | 0.69134 | -121.6461 | -121.628 | 10.7969 | -0.25461 | 122.4856 | 122.387 | 111.59 | 0.034533 | -0.54833 | 0.95827 | 1.0803 | 1.0984 | 1.3379 | -122.6803 | 122.4718 | 122.761 | 122.1781 | 122.3063 | -111.9295
964.9531 | 122.7951 | -2.2614 | 120.3964 | -0.0083178 | 0.0065448 | -0.0026155 | 0.013246 | -0.00041024 | 0.018911 | 0.0090803 | -0.024953 | 0.017054 | 0.016109 | 0.0064743 | 0.02178 | -0.026423 | -0.96468 | -1.5696 | -1.3214 | -1.2085 | -1.1858 | -2.2655 | 120.1693 | 119.9763 | 120.0753 | 120.1601 | 120.4447 | 119.9305 | 8.4394 | -0.004167 | -121.7178 | 2.2349 | 0.69175 | 0.69592 | -121.6049 | -121.5823 | 10.7008 | -0.2363 | 122.4306 | 122.3366 | 111.6358 | 0.048266 | -0.46591 | 0.93996 | 1.0529 | 1.0755 | 1.2967 | -122.6619 | 122.4215 | 122.706 | 122.1919 | 122.2376 | -111.957
966.7031 | 122.731 | -2.3666 | 120.3598 | -0.0083178 | 0.0059038 | -0.0024017 | 0.013674 | -0.00062384 | 0.018911 | 0.0014498 | -0.022176 | 0.019404 | 0.008845 | 0.0064743 | 0.02178 | -0.03558 | -1.0105 | -1.6291 | -1.3763 | -1.2634 | -1.2362 | -2.3388 | 120.1189 | 119.9168 | 120.0066 | 120.1006 | 120.376 | 119.7748 | 8.4807 | 0.027855 | -121.7361 | 2.3311 | 0.73752 | 0.70966 | -121.6232 | -121.596 | 10.8473 | -0.2592 | 122.4856 | 122.3732 | 111.5259 | 0.016207 | -0.58497 | 0.99031 | 1.1032 | 1.1304 | 1.3562 | -122.6986 | 122.4672 | 122.7426 | 122.1415 | 122.2834 | -111.8791
968.375 | 122.7814 | -2.3529 | 120.3415 | -0.00068679 | 0.0065448 | -0.0019745 | 0.013246 | -0.00041024 | 0.018911 | 0.0014498 | -0.017903 | 0.023891 | 0.008845 | 0.0064743 | 0.02178 | -0.031001 | -0.99673 | -1.5971 | -1.358 | -1.2497 | -1.2179 | -2.293 | 120.1372 | 119.958 | 120.0432 | 120.1327 | 120.4172 | 119.7977 | 8.4715 | 0.059911 | -121.6995 | 2.3219 | 0.75583 | 0.69592 | -121.5912 | -121.5594 | 10.8244 | -0.20884 | 122.4901 | 122.3961 | 111.5717 | 0.075725 | -0.54376 | 0.99489 | 1.1032 | 1.135 | 1.3562 | -122.6345 | 122.4856 | 122.7701 | 122.1506 | 122.3109 | -111.87
970.1094 | 122.818 | -2.4445 | 120.2042 | -0.00068679 | 0.0054764 | -0.0017607 | 0.01346 | -0.00062384 | 0.018911 | 0.0014498 | -0.014485 | 0.027096 | 0.0020082 | 0.0064743 | 0.02178 | -0.021844 | -1.1066 | -1.7436 | -1.5045 | -1.3962 | -1.369 | -2.4533 | 119.9724 | 119.8344 | 119.883 | 119.9632 | 120.2478 | 119.5642 | 8.4532 | -0.008798 | -121.7087 | 2.4226 | 0.70088 | 0.70968 | -121.6004 | -121.5731 | 10.8976 | -0.24092 | 122.4169 | 122.3274 | 111.4298 | 0.043646 | -0.63994 | 0.93993 | 1.0482 | 1.0755 | 1.3378 | -122.6574 | 122.4077 | 122.6923 | 122.0087 | 122.2788 | -111.751
971.8438 | 122.818 | -2.4261 | 120.2637 | -0.0083178 | 0.0063312 | -0.0021881 | 0.013246 | -0.00062384 | 0.019339 | 0.0014498 | -0.023671 | 0.017695 | 0.0144 | 0.0066879 | 0.021566 | -0.040158 | -1.0517 | -1.6841 | -1.4404 | -1.3275 | -1.3003 | -2.3892 | 120.0502 | 119.871 | 119.9562 | 120.0365 | 120.3211 | 119.7428 | 8.4761 | 0.036996 | -121.7041 | 2.386 | 0.74209 | 0.70509 | -121.5912 | -121.564 | 10.9022 | -0.22717 | 122.4764 | 122.3824 | 111.4801 | 0.057394 | -0.52089 | 0.98572 | 1.0986 | 1.1259 | 1.3745 | -122.6528 | 122.4626 | 122.7472 | 122.1689 | 122.2971 | -111.7876
973.5156 | 122.7493 | -2.5314 | 120.1904 | 0.0069442 | 0.0063312 | -0.0021881 | 0.013246 | -0.00083764 | 0.019125 | 0.0090803 | -0.02538 | 0.016413 | 0.017177 | 0.0066879 | 0.022207 | -0.031001 | -1.1845 | -1.7894 | -1.564 | -1.4466 | -1.4193 | -2.4624 | 119.9632 | 119.8069 | 119.8875 | 119.9541 | 120.2387 | 119.5413 | 8.4852 | 0.069019 | -121.7545 | 2.5004 | 0.74207 | 0.67305 | -121.637 | -121.6098 | 11.0167 | -0.23634 | 122.4947 | 122.419 | 111.4023 | 0.048221 | -0.6491 | 0.96739 | 1.0849 | 1.1121 | 1.347 | -122.6528 | 122.4855 | 122.7701 | 122.0728 | 122.3383 | -111.7052
975.25 | 122.818 | -2.4857 | 120.1447 | -0.0083178 | 0.0063312 | -0.0021881 | 0.013246 | -0.00062384 | 0.019125 | -0.0061807 | -0.016194 | 0.025387 | -0.017006 | 0.0069017 | 0.021994 | -0.031001 | -1.1753 | -1.7985 | -1.5549 | -1.4512 | -1.4285 | -2.5036 | 119.9266 | 119.784 | 119.8372 | 119.9175 | 120.1974 | 119.4589 | 8.4669 | -0.017967 | -121.6995 | 2.4547 | 0.68714 | 0.70511 | -121.5958 | -121.5731 | 10.9526 | -0.22719 | 122.4123 | 122.3228 | 111.3702 | 0.052791 | -0.68574 | 0.93077 | 1.0345 | 1.0572 | 1.3104 | -122.6483 | 122.4031 | 122.6831 | 121.9446 | 122.2696 | -111.6777
976.9844 | 122.7676 | -2.4902 | 120.2271 | -0.00068679 | 0.0067584 | -0.0017607 | 0.013246 | -0.00062384 | 0.019125 | 0.016711 | -0.010853 | 0.031369 | -0.01017 | 0.0069017 | 0.02178 | -0.03558 | -1.1387 | -1.7756 | -1.5412 | -1.4328 | -1.3964 | -2.4441 | 119.9907 | 119.8572 | 119.9013 | 119.977 | 120.2615 | 119.5413 | 8.3753 | 0.046136 | -121.7682 | 2.4547 | 0.71461 | 0.66847 | -121.6599 | -121.6235 | 10.8656 | -0.25007 | 122.481 | 122.3915 | 111.5259 | 0.034493 | -0.68572 | 0.94908 | 1.0574 | 1.0938 | 1.3516 | -122.6711 | 122.4672 | 122.7518 | 122.0316 | 122.3475 | -111.8517
978.6562 | 122.7173 | -2.4902 | 120.2591 | -0.00068679 | 0.0061174 | -0.0017607 | 0.012819 | -0.00019664 | 0.018698 | 0.0090803 | -0.014698 | 0.02731 | -0.010811 | 0.0062607 | 0.021994 | -0.026423 | -1.0791 | -1.7253 | -1.4816 | -1.3733 | -1.3507 | -2.4075 | 120.0273 | 119.9351 | 119.9287 | 120.009 | 120.2982 | 119.6375 | 8.4715 | 0.082767 | -121.7407 | 2.4638 | 0.76497 | 0.6822 | -121.6324 | -121.6098 | 10.9617 | -0.25006 | 122.5176 | 122.419 | 111.4572 | 0.039079 | -0.62162 | 1.0086 | 1.1169 | 1.1396 | 1.4111 | -122.6666 | 122.4993 | 122.7884 | 122.1277 | 122.4253 | -111.7876
980.3906 | 122.7951 | -2.4857 | 120.1767 | -0.00068679 | 0.0067584 | -0.0024017 | 0.013033 | -0.00041024 | 0.019125 | 0.0014498 | -0.0091437 | 0.032651 | -0.011238 | 0.0069017 | 0.021994 | -0.03558 | -1.102 | -1.7619 | -1.5183 | -1.4054 | -1.3827 | -2.4533 | 119.9632 | 119.8618 | 119.8784 | 119.9541 | 120.2387 | 119.5047 | 8.444 | 0.032401 | -121.695 | 2.4501 | 0.72377 | 0.69137 | -121.5821 | -121.5594 | 10.9297 | -0.22261 | 122.4489 | 122.364 | 111.4343 | 0.061954 | -0.672 | 0.9674 | 1.0803 | 1.1029 | 1.3836 | -122.63 | 122.4397 | 122.7243 | 121.9904 | 122.3475 | -111.7327
982.125 | 122.8088 | -2.449 | 120.1996 | 0.0069442 | 0.0063312 | -0.0019745 | 0.012819 | -0.00062384 | 0.018911 | 0.0014498 | -0.014912 | 0.027096 | 0.0035038 | 0.0064743 | 0.021994 | -0.031001 | -1.0975 | -1.739 | -1.4999 | -1.3916 | -1.369 | -2.4212 | 120.0136 | 119.903 | 119.9196 | 119.9907 | 120.2799 | 119.6741 | 8.4532 | 0.027833 | -121.6995 | 2.418 | 0.71004 | 0.6822 | -121.5912 | -121.5686 | 10.9022 | -0.20887 | 122.4626 | 122.3686 | 111.4664 | 0.080274 | -0.52548 | 0.94909 | 1.0574 | 1.0801 | 1.3516 | -122.6208 | 122.4398 | 122.7289 | 122.1231 | 122.3521 | -111.7464
983.8594 | 122.8088 | -2.4628 | 120.1767 | 0.0069442 | 0.0067584 | -0.0017607 | 0.012819 | -0.00083764 | 0.018698 | -0.0061807 | -0.019398 | 0.022823 | 0.0017946 | 0.0066879 | 0.021994 | -0.03558 | -1.1204 | -1.7848 | -1.5457 | -1.4328 | -1.4056 | -2.467 | 119.9632 | 119.8618 | 119.8646 | 119.9587 | 120.2295 | 119.5688 | 8.4578 | -0.004224 | -121.7224 | 2.4272 | 0.67799 | 0.68221 | -121.6095 | -121.5823 | 10.9205 | -0.21803 | 122.426 | 122.3274 | 111.4069 | 0.052797 | -0.6079 | 0.91704 | 1.0299 | 1.0572 | 1.3424 | -122.6437 | 122.4214 | 122.6923 | 122.0316 | 122.3246 | -111.7189
985.5938 | 122.6807 | -2.4673 | 120.2545 | -0.00068679 | 0.0063312 | -0.0017607 | 0.013033 | -0.00083764 | 0.018698 | 0.0090803 | -0.010212 | 0.031583 | -0.0084604 | 0.0069017 | 0.021994 | -0.026423 | -1.0929 | -1.7298 | -1.4862 | -1.3916 | -1.3552 | -2.4258 | 120.0045 | 119.9122 | 119.9104 | 119.9953 | 120.2799 | 119.61 | 8.4761 | 0.041564 | -121.7407 | 2.4409 | 0.7375 | 0.69594 | -121.6462 | -121.6098 | 10.9434 | -0.25922 | 122.4718 | 122.3778 | 111.4343 | 0.025342 | -0.64451 | 0.98114 | 1.0757 | 1.1121 | 1.3745 | -122.6803 | 122.4626 | 122.7472 | 122.0774 | 122.3795 | -111.7784
987.3438 | 122.7036 | -2.4307 | 120.314 | -0.00068679 | 0.0067584 | -0.0017607 | 0.012178 | -0.00041024 | 0.018911 | -0.0061807 | -0.0097845 | 0.03201 | -0.0097424 | 0.0064743 | 0.02178 | -0.026423 | -1.0517 | -1.7115 | -1.4725 | -1.3642 | -1.3369 | -2.38 | 120.0457 | 119.9442 | 119.9608 | 120.0365 | 120.3211 | 119.7886 | 8.4394 | 0.050732 | -121.7865 | 2.4043 | 0.71919 | 0.66846 | -121.6782 | -121.6509 | 10.8702 | -0.27752 | 122.4764 | 122.3915 | 111.5213 | 0.00704 | -0.52545 | 0.95825 | 1.0666 | 1.0938 | 1.3791 | -122.694 | 122.4672 | 122.7518 | 122.2193 | 122.375 | -111.8746
989.0156 | 122.8043 | -2.504 | 120.1492 | -0.0083178 | 0.0065448 | -0.0019745 | 0.012391 | -0.00062384 | 0.018698 | 0.0090803 | -0.010639 | 0.031583 | -0.0084604 | 0.0062607 | 0.021566 | -0.026423 | -1.1112 | -1.7756 | -1.532 | -1.4283 | -1.4056 | -2.4807 | 119.9449 | 119.8389 | 119.8509 | 119.9358 | 120.2158 | 119.4772 | 8.4669 | 0.023238 | -121.6812 | 2.4775 | 0.72834 | 0.7051 | -121.5775 | -121.5548 | 10.9709 | -0.21345 | 122.4489 | 122.3549 | 111.384 | 0.066527 | -0.672 | 0.97197 | 1.0757 | 1.0984 | 1.3928 | -122.63 | 122.4397 | 122.7197 | 121.9812 | 122.3429 | -111.6823
990.75 | 122.6852 | -2.6276 | 120.1263 | 0.0069442 | 0.0069722 | -0.0017607 | 0.012605 | -0.00041024 | 0.019339 | 0.0014498 | -0.016835 | 0.025814 | 0.0043584 | 0.0062607 | 0.021566 | -0.026423 | -1.1066 | -1.7802 | -1.5366 | -1.4237 | -1.3919 | -2.5448 | 119.8717 | 119.7794 | 119.7868 | 119.8671 | 120.1562 | 119.4681 | 8.4715 | 0.082729 | -121.6629 | 2.6011 | 0.84736 | 0.76463 | -121.55 | -121.5182 | 11.0991 | -0.25924 | 122.4992 | 122.4144 | 111.3153 | 0.029894 | -0.65827 | 1.091 | 1.2039 | 1.2357 | 1.5209 | -122.6712 | 122.4947 | 122.7838 | 122.0956 | 122.407 | -111.6548
992.4375 | 122.6715 | -2.4765 | 120.282 | -0.00068679 | 0.0071858 | -0.0019745 | 0.012178 | -0.00019664 | 0.019125 | 0.0014498 | -0.011921 | 0.02966 | -0.00141 | 0.0066879 | 0.02178 | -0.031001 | -1.0425 | -1.7436 | -1.4999 | -1.3916 | -1.369 | -2.4258 | 119.9999 | 119.8985 | 119.9104 | 119.9816 | 120.2615 | 119.6237 | 8.4669 | 0.050719 | -121.7819 | 2.4455 | 0.73292 | 0.6822 | -121.6736 | -121.651 | 10.9434 | -0.30042 | 122.4764 | 122.3869 | 111.4435 | -0.020438 | -0.65824 | 0.97655 | 1.0849 | 1.1075 | 1.434 | -122.7078 | 122.4581 | 122.738 | 122.1002 | 122.375 | -111.8151
994.1719 | 122.7722 | -2.4261 | 120.2408 | 0.014575 | 0.0069722 | -0.0017607 | 0.01175 | -0.00041024 | 0.019125 | -0.0061807 | -0.0087163 | 0.033078 | -0.011238 | 0.0062607 | 0.02178 | -0.03558 | -1.0517 | -1.739 | -1.4771 | -1.3733 | -1.3552 | -2.4487 | 119.9678 | 119.871 | 119.8875 | 119.9587 | 120.2478 | 119.6833 | 8.4578 | -0.02253 | -121.7178 | 2.3906 | 0.68715 | 0.70968 | -121.6141 | -121.596 | 10.8839 | -0.28212 | 122.394 | 122.3137 | 111.4298 | 0.007025 | -0.55752 | 0.94909 | 1.0528 | 1.0709 | 1.3745 | -122.6895 | 122.3848 | 122.674 | 122.1094 | 122.2971 | -111.783
995.9062 | 122.731 | -2.4811 | 120.2225 | -0.00068679 | 0.0069722 | -0.0017607 | 0.012391 | -0.00083764 | 0.018698 | 0.0090803 | -0.0046573 | 0.035001 | -0.020425 | 0.0064743 | 0.02178 | -0.026423 | -1.0517 | -1.7482 | -1.5137 | -1.41 | -1.3736 | -2.4304 | 119.9907 | 119.8939 | 119.9013 | 119.9907 | 120.2661 | 119.5825 | 8.4486 | 0.050718 | -121.7362 | 2.4547 | 0.73292 | 0.6822 | -121.6324 | -121.596 | 10.9297 | -0.23175 | 122.4718 | 122.3823 | 111.4527 | 0.04365 | -0.63994 | 0.9674 | 1.0711 | 1.1075 | 1.4294 | -122.6528 | 122.4718 | 122.7472 | 122.0636 | 122.375 | -111.7739
997.6406 | 122.6761 | -2.4399 | 120.2728 | -0.00068679 | 0.0076132 | -0.0017607 | 0.011964 | -0.00062384 | 0.019125 | 0.0090803 | -0.0033755 | 0.037779 | -0.021279 | 0.0066879 | 0.021566 | -0.031001 | -1.0242 | -1.7253 | -1.4908 | -1.3779 | -1.3552 | -2.3846 | 120.0273 | 119.9259 | 119.9471 | 120.0273 | 120.3119 | 119.7199 | 8.4669 | 0.055308 | -121.7636 | 2.4089 | 0.71462 | 0.65931 | -121.6507 | -121.6281 | 10.9068 | -0.24548 | 122.4672 | 122.3869 | 111.4801 | 0.039082 | -0.55294 | 0.94909 | 1.062 | 1.0846 | 1.4157 | -122.6574 | 122.4672 | 122.7518 | 122.1598 | 122.3658 | -111.8059
999.375 | 122.6852 | -2.4628 | 120.2682 | -0.015949 | 0.0071858 | -0.0021881 | 0.011964 | -0.00019664 | 0.019125 | 0.0014498 | -0.0040163 | 0.035001 | -0.021279 | 0.0064743 | 0.021994 | -0.026423 | -1.0196 | -1.7344 | -1.4908 | -1.3825 | -1.3461 | -2.4075 | 120.0045 | 119.8985 | 119.9196 | 119.9999 | 120.2844 | 119.6512 | 8.4532 | 0.055302 | -121.759 | 2.4363 | 0.72835 | 0.67305 | -121.6507 | -121.6143 | 10.916 | -0.26837 | 122.4672 | 122.3824 | 111.4664 | 0.016187 | -0.61704 | 0.97198 | 1.0803 | 1.1167 | 1.4431 | -122.6757 | 122.4626 | 122.7472 | 122.114 | 122.3612 | -111.8151
1001.0469 | 122.6578 | -2.4353 | 120.3186 | -0.00068679 | 0.0078268 | -0.0019745 | 0.01175 | -0.00041024 | 0.018911 | -0.0061807 | -0.0063663 | 0.032437 | -0.021493 | 0.0066879 | 0.021566 | -0.026423 | -0.99673 | -1.739 | -1.4908 | -1.3825 | -1.3552 | -2.3846 | 120.0319 | 119.9351 | 119.9471 | 120.0228 | 120.3119 | 119.6192 | 8.4807 | 0.050731 | -121.8094 | 2.4089 | 0.6963 | 0.64557 | -121.7011 | -121.6738 | 10.916 | -0.29584 | 122.4672 | 122.3824 | 111.4664 | -0.006695 | -0.69944 | 0.94451 | 1.0528 | 1.0801 | 1.4386 | -122.7032 | 122.4581 | 122.7472 | 122.0545 | 122.3704 | -111.8379
1002.7969 | 122.7722 | -2.4628 | 120.2087 | 0.0069442 | 0.0080406 | -0.0015471 | 0.011323 | 1.7156e-05 | 0.018698 | 0.0014498 | -0.0048709 | 0.033719 | -0.021707 | 0.0064743 | 0.02178 | -0.026423 | -1.1478 | -1.7756 | -1.5137 | -1.41 | -1.3827 | -2.4212 | 119.9907 | 119.8893 | 119.9013 | 119.9861 | 120.2615 | 119.5459 | 8.4303 | 0.041566 | -121.7224 | 2.4363 | 0.68714 | 0.64558 | -121.6187 | -121.5914 | 10.8931 | -0.2226 | 122.4535 | 122.364 | 111.471 | 0.052804 | -0.66284 | 0.94909 | 1.0528 | 1.0801 | 1.3149 | -122.6299 | 122.4489 | 122.7243 | 122.0087 | 122.3521 | -111.7784
1004.4688 | 122.7493 | -2.5085 | 120.2087 | -0.0083178 | 0.0073996 | -0.0017607 | 0.012178 | -0.00062384 | 0.019125 | -0.0061807 | -0.0046573 | 0.034147 | -0.021493 | 0.0064743 | 0.021994 | -0.03558 | -1.1661 | -1.8077 | -1.5457 | -1.4374 | -1.4193 | -2.4624 | 119.9449 | 119.8435 | 119.8646 | 119.9404 | 120.2249 | 119.6558 | 8.4807 | 0.046131 | -121.7545 | 2.473 | 0.70087 | 0.65474 | -121.6462 | -121.6281 | 10.9892 | -0.26839 | 122.4535 | 122.3732 | 111.384 | 0.016176 | -0.55295 | 0.96281 | 1.0711 | 1.0892 | 1.3424 | -122.6712 | 122.4489 | 122.7335 | 122.1643 | 122.3521 | -111.7281
1006.2031 | 122.7127 | -2.4994 | 120.2042 | 0.0069442 | 0.0071858 | -0.0017607 | 0.011964 | -0.00041024 | 0.018911 | -0.0061807 | -0.0046573 | 0.031797 | -0.021493 | 0.0066879 | 0.021566 | -0.026423 | -1.1524 | -1.7985 | -1.5366 | -1.4191 | -1.3964 | -2.4716 | 119.9358 | 119.8344 | 119.8509 | 119.9358 | 120.2249 | 119.5871 | 8.4669 | 0.027818 | -121.7407 | 2.473 | 0.70087 | 0.67306 | -121.6233 | -121.6006 | 10.9663 | -0.26839 | 122.4352 | 122.3503 | 111.384 | 0.020753 | -0.61705 | 0.96282 | 1.0803 | 1.1029 | 1.347 | -122.6757 | 122.4352 | 122.7243 | 122.0865 | 122.3337 | -111.7372
1007.9531 | 122.818 | -2.5772 | 120.0714 | 0.0069442 | 0.0071858 | -0.0017607 | 0.011964 | -0.00041024 | 0.019339 | -0.013811 | -0.0040163 | 0.031156 | -0.021279 | 0.0066879 | 0.021994 | -0.12715 | -1.2257 | -1.8763 | -1.6007 | -1.4969 | -1.4605 | -2.5677 | 119.8442 | 119.7474 | 119.7548 | 119.8442 | 120.1333 | 119.4955 | 8.4761 | 0.00948 | -121.6721 | 2.4501 | 0.70086 | 0.69138 | -121.5684 | -121.532 | 11.0533 | -0.2272 | 122.4214 | 122.332 | 111.2787 | 0.061933 | -0.57587 | 0.97654 | 1.0803 | 1.1167 | 1.3515 | -122.6391 | 122.4214 | 122.7106 | 122.0727 | 122.3246 | -111.5953
1009.6875 | 122.7722 | -2.5085 | 120.1263 | -0.0083178 | 0.0067584 | -0.0015471 | 0.011964 | -0.00062384 | 0.019125 | -0.021442 | -0.0080755 | 0.02966 | -0.021493 | 0.0066879 | 0.021994 | -0.040158 | -1.1982 | -1.858 | -1.5869 | -1.4786 | -1.456 | -2.5219 | 119.89 | 119.784 | 119.8051 | 119.8854 | 120.17 | 119.6695 | 8.4761 | -0.013395 | -121.7133 | 2.4684 | 0.65051 | 0.6639 | -121.605 | -121.5823 | 10.9846 | -0.24093 | 122.3985 | 122.3137 | 111.329 | 0.043629 | -0.45682 | 0.92161 | 1.0299 | 1.0526 | 1.3104 | -122.6483 | 122.394 | 122.6785 | 122.1781 | 122.2925 | -111.6503
1011.4219 | 122.7264 | -2.5955 | 120.1218 | -0.00068679 | 0.0067584 | -0.0017607 | 0.012391 | -0.00041024 | 0.018698 | -0.0061807 | -0.0029481 | 0.037352 | -0.021279 | 0.0066879 | 0.021566 | -0.031001 | -1.2028 | -1.8672 | -1.6007 | -1.4924 | -1.4605 | -2.5403 | 119.8717 | 119.7703 | 119.7868 | 119.8534 | 120.1471 | 119.5047 | 8.4303 | 0.055265 | -121.7224 | 2.5645 | 0.72833 | 0.67306 | -121.6141 | -121.5823 | 11.0258 | -0.2684 | 122.4672 | 122.3823 | 111.3565 | 0.025314 | -0.61707 | 0.99485 | 1.1032 | 1.135 | 1.3928 | -122.662 | 122.4489 | 122.7426 | 122.1002 | 122.3658 | -111.6915
1013.1094 | 122.6761 | -2.6321 | 120.1126 | -0.00068679 | 0.0067584 | -0.0017607 | 0.011964 | -0.00041024 | 0.018911 | 0.0090803 | -0.0040163 | 0.035856 | -0.021279 | 0.0062607 | 0.021994 | -0.031001 | -1.244 | -1.9084 | -1.6373 | -1.5244 | -1.5018 | -2.6044 | 119.803 | 119.697 | 119.7181 | 119.803 | 120.0738 | 119.3628 | 8.4715 | 0.027781 | -121.7499 | 2.6011 | 0.72374 | 0.69596 | -121.637 | -121.6144 | 11.1036 | -0.30961 | 122.4351 | 122.3503 | 111.2466 | -0.038788 | -0.74985 | 0.99484 | 1.1077 | 1.1304 | 1.3882 | -122.717 | 122.4351 | 122.706 | 121.9949 | 122.3291 | -111.6411
1014.7969 | 122.7264 | -2.6184 | 120.0348 | -0.00068679 | 0.0067584 | -0.0015471 | 0.012391 | -0.00083764 | 0.018698 | -0.0061807 | -0.014485 | 0.025173 | -0.021493 | 0.0064743 | 0.02178 | -0.031001 | -1.2486 | -1.9176 | -1.6373 | -1.5427 | -1.5063 | -2.6227 | 119.7893 | 119.6833 | 119.7044 | 119.7847 | 120.0692 | 119.6237 | 8.4807 | -0.004268 | -121.6721 | 2.5874 | 0.70086 | 0.70512 | -121.5775 | -121.5411 | 11.0991 | -0.2501 | 122.4077 | 122.3228 | 111.2237 | 0.034453 | -0.41105 | 0.98111 | 1.0757 | 1.1121 | 1.3699 | -122.6575 | 122.4031 | 122.6877 | 122.2421 | 122.3017 | -111.5541
1016.5312 | 122.7631 | -2.6825 | 119.9844 | -0.00068679 | 0.0071858 | -0.0019745 | 0.011964 | -0.00062384 | 0.018698 | 0.0014498 | -0.015126 | 0.021755 | -0.021279 | 0.0069017 | 0.021566 | -0.031001 | -1.2669 | -1.9633 | -1.6922 | -1.5839 | -1.5567 | -2.6135 | 119.7893 | 119.6878 | 119.709 | 119.7847 | 120.0647 | 119.3536 | 8.4349 | 0.068977 | -121.6767 | 2.6515 | 0.71916 | 0.65018 | -121.5684 | -121.5411 | 11.1174 | -0.19975 | 122.4718 | 122.3915 | 111.2741 | 0.080229 | -0.63083 | 0.99026 | 1.0985 | 1.1258 | 1.4156 | -122.598 | 122.4672 | 122.7472 | 122.0361 | 122.3703 | -111.5496
1018.2812 | 122.7814 | -2.7374 | 119.8975 | -0.0083178 | 0.0071858 | -0.0017607 | 0.011964 | -0.00083764 | 0.019125 | 0.0014498 | -0.013203 | 0.023677 | -0.021279 | 0.0069017 | 0.021994 | -0.026423 | -1.3081 | -2.0091 | -1.738 | -1.6206 | -1.5979 | -2.6776 | 119.7252 | 119.6192 | 119.6494 | 119.716 | 120.0051 | 119.2849 | 8.4486 | 0.059804 | -121.6355 | 2.711 | 0.72831 | 0.66851 | -121.518 | -121.4954 | 11.186 | -0.18145 | 122.4626 | 122.3869 | 111.2008 | 0.10768 | -0.61254 | 0.9994 | 1.1168 | 1.1395 | 1.4294 | -122.5751 | 122.4534 | 122.7426 | 122.0224 | 122.3566 | -111.4489
1020 | 122.7173 | -71.5485 | 50.9262 | -0.00068679 | 0.021929 | -0.065009 | 0.018375 | -0.0010512 | 0.023185 | 0.016711 | 0.051316 | 0.061495 | 0.044738 | 0.0064743 | 0.02178 | -0.026423 | 0.092979 | -0.022144 | 0.093333 | -0.031693 | 0.21064 | -0.13632 | 51.017 | 50.9614 | 50.9642 | 50.8371 | 51.0331 | 51.0088 | 8.5631 | 71.4121 | -50.8329 | 71.522 | 71.5263 | 0.11418 | -50.9579 | -50.7156 | 80.1115 | -0.089081 | 122.5655 | 122.5127 | 42.4011 | 0.10687 | 0.082596 | 71.6418 | 71.5168 | 71.7591 | 71.6414 | -51.0625 | 122.3856 | 122.5815 | 122.5573 | 122.5099 | -42.3631
1021.75 | 122.8088 | -122.3877 | 0.22888 | -0.0083178 | 0.020434 | -0.063941 | 0.018588 | -0.0012648 | 0.022116 | 0.0014498 | 0.042984 | 0.051667 | 0.040465 | 0.0066879 | 0.02178 | -0.021844 | 0.10214 | -0.012988 | 0.093333 | -0.00422 | 0.21064 | 0.13842 | 0.12009 | 0.13314 | 0.026066 | 0.15776 | 0.33421 | 0.30536 | -0.15499 | 122.5261 | -0.13555 | 122.3659 | 122.3747 | -0.1514 | -0.2331 | -0.018237 | 122.2327 | -0.071118 | 122.5078 | 122.4138 | 0.18106 | 0.10533 | 0.076478 | 122.481 | 122.3835 | 122.5983 | 122.4898 | -0.090467 | 122.5455 | 122.7219 | 122.6931 | 122.5208 | -0.38387
1023.4375 | 122.8043 | -122.4014 | 0.21515 | 0.0069442 | 0.020647 | -0.063941 | 0.018375 | -0.0010512 | 0.021903 | 0.0090803 | 0.048539 | 0.052949 | 0.048797 | 0.0069017 | 0.021566 | -0.017266 | 0.070086 | -0.017566 | 0.097912 | -0.040851 | 0.20607 | 0.12926 | 0.092622 | 0.11025 | -0.010564 | 0.13945 | 0.31132 | 0.28704 | -0.15957 | 122.5307 | -0.11724 | 122.3842 | 122.3839 | -0.14682 | -0.256 | -0.009083 | 122.2419 | -0.075699 | 122.4941 | 122.3909 | 0.14901 | 0.096167 | 0.071896 | 122.4993 | 122.3606 | 122.6075 | 122.4715 | -0.085891 | 122.5409 | 122.7127 | 122.6885 | 122.5117 | -0.37472
1025.1719 | 122.6898 | -122.4152 | 0.24261 | 0.0069442 | 0.020434 | -0.064155 | 0.018375 | -0.0010512 | 0.022544 | 0.0014498 | 0.055802 | 0.060854 | 0.055634 | 0.0071153 | 0.021566 | -0.012688 | 0.074664 | -0.017566 | 0.097912 | 0.004938 | 0.21064 | 0.12468 | 0.078886 | 0.096512 | -0.019721 | 0.11656 | 0.29758 | 0.26873 | -0.16873 | 122.5398 | -0.1447 | 122.4025 | 122.3976 | -0.14225 | -0.23768 | -0.03197 | 122.2464 | -0.12606 | 122.494 | 122.3954 | 0.14901 | 0.054965 | 0.026116 | 122.5131 | 122.4201 | 122.6258 | 122.4898 | -0.11794 | 122.5317 | 122.7127 | 122.6839 | 122.5117 | -0.41134
1026.9219 | 122.7036 | -122.4197 | 0.24261 | -0.0083178 | 0.020647 | -0.063514 | 0.018375 | -0.0010512 | 0.022544 | 0.0014498 | 0.054307 | 0.058931 | 0.055634 | 0.0066879 | 0.021566 | -0.017266 | 0.070086 | -0.017566 | 0.093333 | 0.004938 | 0.21522 | 0.13384 | 0.083464 | 0.096512 | -0.0243 | 0.12571 | 0.293 | 0.26873 | -0.17788 | 122.5536 | -0.14928 | 122.4025 | 122.4022 | -0.1514 | -0.23768 | -0.027391 | 122.2419 | -0.1169 | 122.5032 | 122.3954 | 0.15358 | 0.050386 | 0.026116 | 122.5131 | 122.4247 | 122.635 | 122.4898 | -0.10878 | 122.5455 | 122.7127 | 122.6885 | 122.5163 | -0.4205
1028.6562 | 122.6898 | -122.4472 | 0.25635 | 0.0069442 | 0.020861 | -0.063727 | 0.018375 | -0.0010512 | 0.02233 | 0.0014498 | 0.05687 | 0.064486 | 0.054352 | 0.0071153 | 0.021353 | -0.026423 | 0.060928 | -0.022144 | 0.10249 | -0.013378 | 0.21064 | 0.12468 | 0.078886 | 0.091933 | -0.033458 | 0.11198 | 0.28842 | 0.26415 | -0.16415 | 122.5719 | -0.15386 | 122.4208 | 122.4251 | -0.14682 | -0.26973 | -0.045703 | 122.2831 | -0.14437 | 122.5261 | 122.4137 | 0.13069 | 0.032075 | 0.007804 | 122.5497 | 122.4338 | 122.6578 | 122.5081 | -0.13167 | 122.5592 | 122.7356 | 122.7114 | 122.5391 | -0.4205
1030.3906 | 122.7722 | -122.3694 | 0.2243 | -0.0083178 | 0.020434 | -0.063941 | 0.018161 | -0.0012648 | 0.023398 | -0.0061807 | 0.05452 | 0.064059 | 0.051575 | 0.0064743 | 0.021353 | -0.017266 | 0.065507 | -0.017566 | 0.097912 | -0.036272 | 0.21522 | 0.12926 | 0.078886 | 0.087354 | -0.028879 | 0.11198 | 0.27926 | -0.065507 | -0.17331 | 122.4986 | -0.12639 | 122.3521 | 122.3518 | -0.14682 | -0.26058 | -0.00908 | 122.1961 | -0.11233 | 122.4483 | 122.3405 | 0.14443 | 0.054961 | -0.28981 | 122.4673 | 122.3331 | 122.5846 | 122.4349 | -0.095046 | 122.4814 | 122.6486 | 122.3039 | 122.4567 | -0.39761
1032.0781 | 122.6944 | -122.4106 | 0.23346 | -0.0083178 | 0.020647 | -0.063941 | 0.018588 | -0.0016922 | 0.023612 | 0.0090803 | 0.050248 | 0.059358 | 0.04837 | 0.0069017 | 0.021566 | -0.017266 | 0.074664 | -0.017566 | 0.10249 | 0.004938 | 0.21064 | 0.12926 | 0.083464 | 0.096512 | -0.033458 | 0.1074 | 0.28384 | -0.047193 | -0.16873 | 122.5398 | -0.13097 | 122.3933 | 122.393 | -0.14682 | -0.22852 | -0.022814 | 122.2419 | -0.12606 | 122.494 | 122.3771 | 0.13527 | 0.050385 | -0.28065 | 122.5131 | 122.4155 | 122.6212 | 122.4852 | -0.1042 | 122.518 | 122.6944 | 122.3634 | 122.5071 | -0.40219
1033.8281 | 122.818 | -122.3419 | 0.21057 | -0.015949 | 0.020647 | -0.063727 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.053025 | 0.063418 | 0.049652 | 0.0066879 | 0.02178 | -0.017266 | 0.074664 | -0.017566 | 0.097912 | 0.009517 | 0.21064 | 0.1201 | 0.074307 | 0.087354 | -0.033458 | 0.1074 | 0.27469 | 0.048958 | -0.17331 | 122.462 | -0.11266 | 122.3247 | 122.3244 | -0.13767 | -0.20105 | 7.4e-05 | 122.1686 | -0.10317 | 122.4162 | 122.3085 | 0.13985 | 0.064116 | -0.16161 | 122.4398 | 122.3514 | 122.5526 | 122.4166 | -0.090471 | 122.4493 | 122.6166 | 122.3909 | 122.4293 | -0.38388
1035.5781 | 122.7356 | -122.3969 | 0.22888 | 0.014575 | 0.021075 | -0.063941 | 0.018375 | -0.0012648 | 0.023612 | 0.0090803 | 0.05452 | 0.059999 | 0.056061 | 0.0069017 | 0.021994 | -0.026423 | 0.065507 | -0.003831 | 0.10707 | 0.018675 | 0.21064 | 0.12468 | 0.074307 | 0.091933 | -0.028879 | 0.098244 | 0.27469 | 0.094744 | -0.17788 | 122.5215 | -0.12181 | 122.3704 | 122.393 | -0.12851 | -0.21021 | -0.018237 | 122.219 | -0.13064 | 122.4712 | 122.368 | 0.14901 | 0.045805 | -0.13414 | 122.5039 | 122.4155 | 122.6075 | 122.4624 | -0.1042 | 122.4951 | 122.6715 | 122.4916 | 122.4888 | -0.40677
1037.3281 | 122.7997 | -122.374 | 0.21515 | -0.0083178 | 0.020861 | -0.062873 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.056016 | 0.061922 | 0.055848 | 0.0066879 | 0.021994 | -0.031001 | 0.070086 | -0.012988 | 0.10249 | -0.022536 | 0.21522 | 0.1201 | 0.074307 | 0.06904 | -0.033458 | 0.093665 | 0.27011 | -0.042614 | -0.18246 | 122.4941 | -0.11266 | 122.343 | 122.361 | -0.13309 | -0.23769 | 7.5e-05 | 122.1915 | -0.12148 | 122.4483 | 122.3405 | 0.14901 | 0.054959 | -0.25776 | 122.4765 | 122.3514 | 122.5892 | 122.444 | -0.095049 | 122.4676 | 122.6441 | 122.3313 | 122.443 | -0.39761
1039.0938 | 122.7493 | -122.4014 | 0.22888 | -0.00068679 | 0.021075 | -0.062873 | 0.018802 | -0.0012648 | 0.023612 | -0.0061807 | 0.051743 | 0.061709 | 0.048797 | 0.0069017 | 0.021994 | -0.017266 | 0.074664 | -0.012988 | 0.097912 | -0.036272 | 0.2198 | 0.1201 | 0.078886 | 0.073618 | -0.0243 | 0.098244 | 0.28842 | -0.065507 | -0.17331 | 122.5215 | -0.13097 | 122.3842 | 122.3884 | -0.13309 | -0.26515 | -0.00908 | 122.2281 | -0.13064 | 122.4803 | 122.3771 | 0.14901 | 0.059541 | -0.29439 | 122.4993 | 122.3652 | 122.6212 | 122.4761 | -0.10878 | 122.4997 | 122.6899 | 122.3359 | 122.475 | -0.40219
1040.8438 | 122.6944 | -122.3877 | 0.24261 | -0.00068679 | 0.021075 | -0.063514 | 0.018588 | -0.0012648 | 0.023398 | -0.0061807 | 0.056016 | 0.06235 | 0.05542 | 0.0069017 | 0.021353 | -0.021844 | 0.065507 | -0.008409 | 0.10707 | 0.000359 | 0.22438 | 0.1201 | 0.074307 | 0.064461 | -0.033458 | 0.098244 | 0.26553 | -0.074664 | -0.17788 | 122.5078 | -0.13555 | 122.3659 | 122.3793 | -0.12851 | -0.24226 | -0.018234 | 122.2098 | -0.14437 | 122.462 | 122.3542 | 0.14443 | 0.022915 | -0.31728 | 122.4948 | 122.3881 | 122.6121 | 122.4532 | -0.12251 | 122.4859 | 122.6532 | 122.313 | 122.4522 | -0.4205
1042.5938 | 122.7951 | -122.3648 | 0.20599 | -0.00068679 | 0.021075 | -0.062873 | 0.018802 | -0.0010512 | 0.023398 | 0.0090803 | 0.056443 | 0.0647 | 0.053711 | 0.0069017 | 0.021566 | -0.026423 | 0.074664 | -0.008409 | 0.10249 | 0.000359 | 0.2198 | 0.12468 | 0.069728 | 0.064461 | -0.033458 | 0.098244 | 0.27469 | -0.0243 | -0.17331 | 122.4895 | -0.1035 | 122.3384 | 122.3564 | -0.13309 | -0.20564 | 0.013808 | 122.1915 | -0.10775 | 122.4345 | 122.3313 | 0.13985 | 0.068693 | -0.23029 | 122.4673 | 122.3652 | 122.5846 | 122.4395 | -0.081315 | 122.4631 | 122.6395 | 122.3405 | 122.4293 | -0.3793
1044.3438 | 122.8043 | -122.3511 | 0.20599 | -0.00068679 | 0.020861 | -0.062873 | 0.018375 | -0.0010512 | 0.023612 | 0.0090803 | 0.055589 | 0.062991 | 0.054138 | 0.0069017 | 0.021353 | -0.021844 | 0.11587 | -0.003831 | 0.093333 | -0.036272 | 0.21064 | 0.12468 | 0.074307 | 0.059882 | -0.033458 | 0.098244 | 0.26553 | -0.11129 | -0.17788 | 122.4758 | -0.11266 | 122.3292 | 122.3472 | -0.12851 | -0.24227 | 0.004651 | 122.1732 | -0.10775 | 122.4254 | 122.3176 | 0.14443 | 0.059536 | -0.31729 | 122.4444 | 122.3148 | 122.5617 | 122.4669 | -0.081315 | 122.4493 | 122.6166 | 122.2398 | 122.411 | -0.38388
1046.1094 | 122.7539 | -122.3648 | 0.19684 | -0.015949 | 0.020861 | -0.063086 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.054734 | 0.062991 | 0.052216 | 0.0069017 | 0.021994 | -0.017266 | 0.092979 | -0.003831 | 0.097912 | -0.013378 | 0.2198 | 0.1201 | 0.074307 | 0.06904 | -0.033458 | 0.089087 | 0.27011 | -0.047193 | -0.17331 | 122.4849 | -0.098926 | 122.3475 | 122.361 | -0.12393 | -0.21022 | 0.022964 | 122.1915 | -0.10775 | 122.4391 | 122.3313 | 0.13985 | 0.07327 | -0.24403 | 122.4627 | 122.3514 | 122.5846 | 122.4578 | -0.076738 | 122.4539 | 122.6349 | 122.3176 | 122.4338 | -0.37014
1047.8281 | 122.7402 | -122.3785 | 0.2243 | -0.00068679 | 0.020647 | -0.063514 | 0.018375 | -0.0010512 | 0.023826 | 0.0014498 | 0.052811 | 0.06235 | 0.049652 | 0.0069017 | 0.021566 | -0.017266 | 0.092979 | 0.000747 | 0.097912 | 0.018675 | 0.21522 | 0.12468 | 0.078886 | 0.06904 | -0.0243 | 0.093665 | 0.26095 | -0.060928 | -0.17788 | 122.5032 | -0.12639 | 122.3613 | 122.3793 | -0.12393 | -0.20563 | -0.00908 | 122.2007 | -0.13064 | 122.4574 | 122.3542 | 0.15358 | 0.036647 | -0.28523 | 122.4765 | 122.3972 | 122.5938 | 122.4715 | -0.099625 | 122.4722 | 122.6395 | 122.3176 | 122.4476 | -0.40219
1049.5625 | 122.7539 | -122.3785 | 0.22888 | 0.0069442 | 0.020861 | -0.062873 | 0.018375 | -0.0012648 | 0.023185 | -0.013811 | 0.055161 | 0.063632 | 0.052643 | 0.0073291 | 0.02178 | -0.017266 | 0.097557 | 0.009904 | 0.10249 | -0.017957 | 0.2198 | 0.1201 | 0.074307 | 0.06904 | -0.028879 | 0.089087 | 0.26553 | -0.033457 | -0.17331 | 122.4986 | -0.12639 | 122.3613 | 122.3884 | -0.1102 | -0.24684 | -0.00908 | 122.2052 | -0.1398 | 122.4528 | 122.3497 | 0.14443 | 0.036648 | -0.26234 | 122.481 | 122.3606 | 122.5983 | 122.4761 | -0.10878 | 122.4676 | 122.6441 | 122.3451 | 122.4476 | -0.40219
1051.2969 | 122.6715 | -122.3785 | 0.24261 | 0.0069442 | 0.020861 | -0.063514 | 0.018588 | -0.0012648 | 0.023612 | 0.0090803 | 0.056016 | 0.060854 | 0.053925 | 0.0064743 | 0.02178 | -0.017266 | 0.0884 | 0.023639 | 0.10249 | -0.031693 | 0.2198 | 0.1201 | 0.074307 | 0.064461 | -0.028879 | 0.093665 | 0.26095 | -0.038035 | -0.17331 | 122.4986 | -0.14012 | 122.3613 | 122.4022 | -0.096461 | -0.27431 | -0.022813 | 122.2052 | -0.14895 | 122.4528 | 122.3497 | 0.14443 | 0.018336 | -0.28065 | 122.481 | 122.3468 | 122.5983 | 122.4669 | -0.12251 | 122.4722 | 122.6395 | 122.3405 | 122.443 | -0.41592
1052.9688 | 122.7722 | -122.3557 | 0.21057 | -0.00068679 | 0.020861 | -0.062659 | 0.018802 | -0.00083764 | 0.023612 | 0.0090803 | 0.053879 | 0.063204 | 0.047943 | 0.0066879 | 0.021566 | -0.017266 | 0.070086 | 0.005325 | 0.10707 | 0.004938 | 0.2198 | 0.11552 | 0.074307 | 0.064461 | -0.028879 | 0.098244 | 0.26095 | -0.015142 | -0.17331 | 122.4712 | -0.1035 | 122.3384 | 122.361 | -0.1102 | -0.20563 | 0.009231 | 122.1823 | -0.11233 | 122.43 | 122.3268 | 0.14443 | 0.05038 | -0.22571 | 122.4627 | 122.3606 | 122.5755 | 122.4257 | -0.09505 | 122.4539 | 122.6166 | 122.3405 | 122.4201 | -0.38388
1054.7031 | 122.6578 | -122.374 | 0.25635 | -0.00068679 | 0.020861 | -0.063086 | 0.018588 | -0.0012648 | 0.023612 | -0.0061807 | 0.055589 | 0.061068 | 0.054352 | 0.0066879 | 0.021566 | -0.021844 | 0.079243 | 0.014482 | 0.10707 | -0.04543 | 0.21522 | 0.12926 | 0.074307 | 0.064461 | -0.028879 | 0.089087 | 0.26095 | -0.051771 | -0.18246 | 122.5032 | -0.14928 | 122.3521 | 122.3884 | -0.11478 | -0.30178 | -0.041124 | 122.1915 | -0.16726 | 122.4483 | 122.3451 | 0.15358 | 0.004603 | -0.30812 | 122.481 | 122.3285 | 122.5892 | 122.4532 | -0.12709 | 122.463 | 122.6349 | 122.3222 | 122.4384 | -0.43881
1056.375 | 122.6532 | -122.3969 | 0.24719 | 0.0069442 | 0.020861 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.05623 | 0.067264 | 0.050079 | 0.0066879 | 0.02178 | -0.021844 | 0.083821 | 0.014482 | 0.10249 | 0.046148 | 0.22438 | 0.1201 | 0.074307 | 0.06904 | -0.0243 | 0.084508 | 0.26553 | 0.021486 | -0.18246 | 122.517 | -0.1447 | 122.375 | 122.4113 | -0.10562 | -0.20104 | -0.022811 | 122.2144 | -0.16268 | 122.4712 | 122.3726 | 0.15816 | 0.018338 | -0.22571 | 122.4993 | 122.443 | 122.6212 | 122.4807 | -0.12709 | 122.4814 | 122.6624 | 122.4183 | 122.4659 | -0.42966
1058.125 | 122.7814 | -122.3328 | 0.19684 | -0.00068679 | 0.021075 | -0.0633 | 0.018375 | -0.0014786 | 0.023185 | -0.0061807 | 0.055375 | 0.065127 | 0.051361 | 0.0069017 | 0.02178 | -0.017266 | 0.074664 | 0.009904 | 0.093333 | -0.022536 | 0.21522 | 0.12926 | 0.074307 | 0.06904 | -0.038036 | 0.093665 | 0.26553 | -0.028878 | -0.18704 | 122.462 | -0.10351 | 122.3155 | 122.3427 | -0.11935 | -0.21937 | 0.018386 | 122.1457 | -0.10317 | 122.4071 | 122.2947 | 0.14901 | 0.068692 | -0.22572 | 122.4261 | 122.3102 | 122.548 | 122.4074 | -0.06758 | 122.4264 | 122.5983 | 122.3039 | 122.4018 | -0.38388
1059.8281 | 122.731 | -122.3511 | 0.23804 | -0.00068679 | 0.021075 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0090803 | 0.046829 | 0.050171 | 0.049865 | 0.0066879 | 0.021994 | -0.021844 | 0.11129 | 0.009904 | 0.097912 | 0.018675 | 0.2198 | 0.1201 | 0.088043 | 0.078197 | -0.019721 | 0.093665 | 0.27011 | -0.028878 | -0.16873 | 122.4712 | -0.14012 | 122.3292 | 122.361 | -0.1102 | -0.21936 | -0.018235 | 122.1823 | -0.14437 | 122.4391 | 122.3314 | 0.14901 | 0.032071 | -0.26692 | 122.449 | 122.3697 | 122.5709 | 122.4624 | -0.11794 | 122.4447 | 122.6212 | 122.3222 | 122.4293 | -0.40676
1061.5938 | 122.6532 | -122.3648 | 0.24719 | -0.00068679 | 0.020647 | -0.063086 | 0.018802 | -0.0012648 | 0.023612 | 0.0014498 | 0.051102 | 0.056581 | 0.050506 | 0.0066879 | 0.021566 | -0.012688 | 0.092979 | 0.014482 | 0.10707 | 0.018675 | 0.2198 | 0.12468 | 0.078886 | 0.082776 | -0.033458 | 0.089087 | 0.26553 | 0.003172 | -0.17331 | 122.4895 | -0.14012 | 122.3521 | 122.3793 | -0.1102 | -0.22852 | -0.02739 | 122.1915 | -0.1581 | 122.4437 | 122.3313 | 0.13985 | 0.018338 | -0.24402 | 122.4719 | 122.3835 | 122.5846 | 122.4578 | -0.12251 | 122.4539 | 122.6303 | 122.368 | 122.4476 | -0.4205
1063.3438 | 122.6257 | -72.3267 | 50.3265 | -0.0083178 | 0.020647 | -0.0633 | 0.018375 | -0.0012648 | 0.023612 | 0.0014498 | 0.051743 | 0.059999 | 0.049011 | 0.0069017 | 0.021566 | -0.012688 | 0.13876 | 0.01906 | 0.093333 | 0.009517 | 0.21522 | 0.078889 | 44.7991 | 44.9724 | 44.8287 | 44.7477 | 44.7558 | 44.8918 | 7.7068 | 72.4055 | -50.2332 | 72.314 | 72.3457 | -0.059829 | -50.317 | -50.1113 | 80.0335 | -5.5788 | 117.1258 | 117.1554 | 37.1219 | -5.5707 | -5.4347 | 72.42 | 72.3362 | 72.5419 | 72.4654 | -50.2476 | 117.0744 | 117.0825 | 117.2185 | 117.2991 | -42.6197
1065.0938 | 122.6852 | -118.2907 | 4.2114 | 0.014575 | 0.020861 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.05452 | 0.062991 | 0.052002 | 0.0064743 | 0.021994 | -0.021844 | 0.12503 | 0.01906 | 0.11165 | 0.004938 | 0.21522 | 0.11094 | 4.1906 | 4.1807 | 4.0874 | 4.1594 | 4.3359 | 4.3162 | 3.8698 | 118.4017 | -4.0998 | 118.2689 | 118.3098 | -0.091882 | -4.2065 | -3.9962 | 122.1605 | -0.052057 | 122.4813 | 122.3781 | 0.21759 | 0.12448 | 0.10479 | 118.4024 | 118.2956 | 118.5059 | 118.4157 | -4.1005 | 122.4501 | 122.6266 | 122.6069 | 122.4714 | -0.34164
1066.7812 | 122.8683 | -121.9391 | 0.53101 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.0012648 | 0.023612 | 0.0014498 | 0.054734 | 0.063632 | 0.052002 | 0.0071153 | 0.021566 | -0.008109 | 0.12503 | 0.01906 | 0.10707 | 0.027833 | 0.22438 | 0.1201 | 0.89848 | 0.89779 | 0.79529 | 0.89948 | 1.0897 | 1.0517 | 0.62799 | 122.0592 | -0.42394 | 121.931 | 121.9581 | -0.10104 | -0.50317 | -0.30662 | 122.5671 | 0.36847 | 122.8376 | 122.7344 | 0.1673 | 0.55867 | 0.52067 | 122.0462 | 121.9669 | 122.1635 | 122.0641 | -0.41091 | 122.8386 | 123.0288 | 122.9908 | 122.8369 | 0.096981
1068.5156 | 122.8134 | -121.8613 | 0.64087 | -0.00068679 | 0.021075 | -0.062873 | 0.018588 | -0.0012648 | 0.023185 | 0.0014498 | 0.053666 | 0.060427 | 0.05307 | 0.0069017 | 0.021566 | -0.012688 | 0.13419 | 0.009904 | 0.097912 | 0.014096 | 0.21064 | 0.1201 | 0.79774 | 0.80621 | 0.69914 | 0.80791 | 0.98895 | 0.94636 | 0.53641 | 121.9814 | -0.54296 | 121.8486 | 121.8712 | -0.1102 | -0.62677 | -0.43022 | 122.3977 | 0.16704 | 122.659 | 122.5604 | 0.16273 | 0.34808 | 0.30549 | 121.9592 | 121.8754 | 122.0719 | 121.9955 | -0.52077 | 122.6692 | 122.8502 | 122.8076 | 122.6675 | -0.10446
1070.25 | 122.6852 | -122.2916 | 0.3067 | -0.00068679 | 0.020647 | -0.063086 | 0.018588 | -0.0014786 | 0.023398 | 0.0014498 | 0.050889 | 0.062777 | 0.044097 | 0.0069017 | 0.021139 | -0.021844 | 0.13419 | 0.014482 | 0.10249 | -0.008799 | 0.2198 | 0.1201 | 0.14757 | 0.16061 | 0.044381 | 0.15776 | 0.32963 | 0.058115 | -0.11378 | 122.4117 | -0.20421 | 122.2697 | 122.306 | -0.10562 | -0.3155 | -0.0869 | 122.1778 | -0.14894 | 122.4391 | 122.3359 | 0.15816 | 0.022928 | -0.24859 | 122.3941 | 122.2828 | 122.5114 | 122.4258 | -0.1866 | 122.4493 | 122.6212 | 122.3497 | 122.4522 | -0.42048
1071.9219 | 122.7402 | -122.2458 | 0.32044 | -0.015949 | 0.020434 | -0.062873 | 0.018588 | -0.0012648 | 0.023185 | -0.0061807 | 0.049393 | 0.058931 | 0.046447 | 0.0066879 | 0.02178 | -0.021844 | 0.12503 | 0.01906 | 0.10249 | 0.014096 | 0.22438 | 0.1201 | 0.17962 | 0.19724 | 0.08101 | 0.19439 | 0.37084 | 0.168 | -0.072572 | 122.3659 | -0.21795 | 122.2239 | 122.2648 | -0.10104 | -0.30634 | -0.096054 | 122.1732 | -0.12604 | 122.4254 | 122.3268 | 0.15358 | 0.050403 | -0.15243 | 122.3483 | 122.2599 | 122.4702 | 122.3708 | -0.20034 | 122.4402 | 122.6166 | 122.4138 | 122.443 | -0.39301
1073.6719 | 122.6807 | -121.9849 | 0.59509 | 0.0069442 | 0.020861 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.052384 | 0.057649 | 0.053497 | 0.0066879 | 0.021353 | -0.021844 | 0.12961 | 0.014482 | 0.10249 | 0.014096 | 0.22438 | 0.12468 | 0.41771 | 0.42618 | 0.30995 | 0.42332 | 0.59977 | 0.56634 | 0.16095 | 122.1095 | -0.4926 | 121.963 | 121.9993 | -0.1102 | -0.581 | -0.37071 | 122.1458 | -0.17178 | 122.4026 | 122.2948 | 0.149 | 0.004675 | -0.028753 | 122.0874 | 121.999 | 122.2092 | 122.1145 | -0.47041 | 122.4082 | 122.5846 | 122.5512 | 122.411 | -0.43415
1075.3594 | 122.6669 | -120.3049 | 2.2705 | -0.00068679 | 0.020861 | -0.063086 | 0.018588 | -0.00083764 | 0.023612 | 0.0090803 | 0.050889 | 0.059145 | 0.047943 | 0.0064743 | 0.021353 | -0.012688 | 0.12503 | 0.01906 | 0.10707 | 0.027833 | 0.22438 | 0.1201 | 0.55049 | 0.55896 | 0.44731 | 0.55609 | 0.73255 | 0.54345 | 0.29831 | 120.425 | -2.1634 | 120.2922 | 120.3239 | -0.10104 | -2.2427 | -2.0461 | 120.6032 | -1.7144 | 120.8554 | 120.7522 | 0.14899 | -1.538 | -1.7271 | 120.4119 | 120.3327 | 120.5293 | 120.4299 | -2.1504 | 120.861 | 121.0374 | 120.8483 | 120.8638 | -1.9722
1077.0938 | 122.6898 | -119.3253 | 3.241 | -0.00068679 | 0.020647 | -0.062873 | 0.018375 | -0.0014786 | 0.023185 | 0.0090803 | 0.051316 | 0.063632 | 0.044738 | 0.0066879 | 0.02178 | -0.017266 | 0.083821 | 0.014482 | 0.10249 | -0.00422 | 0.2198 | 0.1201 | 0.45434 | 0.43076 | 0.35115 | 0.45537 | 0.6364 | 0.4473 | 0.18384 | 119.4454 | -3.1385 | 119.308 | 119.3397 | -0.10562 | -3.2452 | -3.0212 | 119.5091 | -2.7856 | 119.7796 | 119.6764 | 0.16731 | -2.6046 | -2.7937 | 119.4277 | 119.321 | 119.5451 | 119.4091 | -3.1209 | 119.7806 | 119.9617 | 119.7726 | 119.756 | -3.0571
1078.8438 | 122.7768 | -120.5566 | 2.0416 | 0.0069442 | 0.021075 | -0.062659 | 0.019016 | -0.0010512 | 0.023612 | 0.0014498 | 0.051529 | 0.063418 | 0.046233 | 0.0066879 | 0.021353 | -0.017266 | 0.070086 | -0.003831 | 0.10249 | 0.041569 | 0.2198 | 0.1201 | 2.1073 | 2.0608 | 2.0178 | 2.1036 | 2.2801 | 2.0544 | 1.846 | 120.6767 | -1.9391 | 120.5394 | 120.5528 | -0.12393 | -2.0001 | -1.8218 | 122.4026 | 0.061998 | 122.6639 | 122.5744 | 0.17185 | 0.23849 | 0.01276 | 120.6591 | 120.5982 | 120.7764 | 120.6267 | -1.9215 | 122.6603 | 122.8368 | 122.611 | 122.6174 | -0.19567
1080.5781 | 122.7859 | -119.783 | 2.7237 | 0.014575 | 0.020861 | -0.063086 | 0.018588 | -0.0014786 | 0.023398 | -0.013811 | 0.051316 | 0.063845 | 0.045379 | 0.0066879 | 0.021994 | -0.017266 | 0.079243 | -0.003831 | 0.10707 | 0.023254 | 0.22438 | 0.12468 | 3.0596 | 3.0544 | 2.961 | 3.0468 | 3.2142 | 3.199 | 2.78 | 119.9077 | -2.6166 | 119.7658 | 119.7792 | -0.12851 | -2.7004 | -2.4993 | 122.5631 | 0.3231 | 122.8426 | 122.744 | 0.18099 | 0.49046 | 0.47534 | 119.8901 | 119.8063 | 120.0074 | 119.8623 | -2.599 | 122.8298 | 122.9972 | 122.9821 | 122.8374 | 0.056337
1082.3125 | 122.7722 | -119.2154 | 3.3234 | -0.0083178 | 0.020434 | -0.063086 | 0.018588 | -0.0012648 | 0.023185 | 0.0014498 | 0.051743 | 0.063845 | 0.045165 | 0.0064743 | 0.02178 | -0.012688 | 0.14334 | 0.01906 | 0.097912 | 0.000359 | 0.2198 | 0.12926 | 2.9452 | 2.9399 | 2.8511 | 2.9278 | 3.0997 | 3.08 | 2.6656 | 119.3447 | -3.2255 | 119.2027 | 119.2345 | -0.1102 | -3.323 | -3.1036 | 121.881 | -0.39561 | 122.1606 | 122.0665 | 0.18557 | -0.22368 | -0.24337 | 119.3133 | 119.2158 | 119.4352 | 119.3587 | -3.1941 | 122.1431 | 122.3151 | 122.2954 | 122.1553 | -0.6578
1084.0469 | 122.7631 | -121.3303 | 1.1719 | -0.015949 | 0.020647 | -0.0633 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.051316 | 0.063845 | 0.045593 | 0.0066879 | 0.02178 | -0.017266 | 0.13876 | 0.028217 | 0.10707 | -0.022536 | 0.2198 | 0.10636 | 3.1283 | 3.1047 | 3.0297 | 3.1109 | 3.292 | 3.1075 | 2.8167 | 121.4366 | -1.0648 | 121.313 | 121.3585 | -0.078146 | -1.1944 | -0.95207 | 124.1469 | 1.939 | 124.4586 | 124.36 | 0.21304 | 2.1201 | 1.9356 | 121.4373 | 121.3077 | 121.5501 | 121.469 | -1.0655 | 124.4412 | 124.6222 | 124.4377 | 124.435 | 1.6448
1085.7344 | 122.7722 | -121.4035 | 1.1353 | 0.0069442 | 0.020647 | -0.0633 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.051743 | 0.064059 | 0.045379 | 0.0073291 | 0.02178 | -0.008109 | 0.14334 | 0.037373 | 0.10249 | -0.013378 | 0.2198 | 0.11552 | 0.9351 | 0.89321 | 0.83192 | 0.93153 | 1.1034 | 0.82274 | 0.67378 | 121.519 | -1.0328 | 121.3954 | 121.4409 | -0.078148 | -1.1486 | -0.91545 | 122.0773 | -0.20372 | 122.3386 | 122.2354 | 0.15814 | -0.03184 | -0.31251 | 121.506 | 121.3901 | 121.6233 | 121.5468 | -1.0197 | 122.335 | 122.5069 | 122.2262 | 122.2967 | -0.46148
1087.4844 | 122.6486 | -116.8945 | 5.69 | 0.0069442 | 0.020861 | -0.063086 | 0.018161 | -0.0012648 | 0.023612 | -0.0061807 | 0.051529 | 0.063418 | 0.045593 | 0.0069017 | 0.021566 | -0.012688 | 0.13876 | 0.037373 | 0.10249 | 0.032411 | 0.2198 | 0.1201 | 5.5779 | 5.5085 | 5.4885 | 5.5375 | 5.7049 | 5.5936 | 5.2389 | 117.0146 | -5.5875 | 116.8818 | 116.9319 | -0.082727 | -5.6576 | -5.4702 | 122.1334 | -0.15251 | 122.4724 | 122.383 | 0.24961 | 0.014907 | -0.096356 | 116.997 | 116.9269 | 117.1143 | 117.0333 | -5.5699 | 122.432 | 122.5994 | 122.4882 | 122.4031 | -0.45115
1089.2188 | 122.7448 | -116.7068 | 5.7999 | -0.00068679 | 0.020647 | -0.063086 | 0.018588 | -0.0010512 | 0.023398 | 0.0090803 | 0.051957 | 0.062991 | 0.046874 | 0.0066879 | 0.021566 | -0.003531 | 0.14334 | 0.037373 | 0.097912 | 0.014096 | 0.22438 | 0.10178 | 5.6603 | 5.6047 | 5.5846 | 5.6199 | 5.7965 | 5.6211 | 5.3259 | 116.8086 | -5.702 | 116.7033 | 116.7442 | -0.064411 | -5.7858 | -5.5755 | 122.0327 | -0.17996 | 122.3672 | 122.2915 | 0.25877 | -0.003385 | -0.17875 | 116.8048 | 116.7209 | 116.9312 | 116.8502 | -5.6981 | 122.3268 | 122.5033 | 122.328 | 122.3115 | -0.47401
1090.9531 | 122.6807 | -116.8671 | 5.6763 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.0012648 | 0.023826 | 0.0014498 | 0.052598 | 0.062991 | 0.047729 | 0.0069017 | 0.02178 | 0.001048 | 0.14334 | 0.041952 | 0.10249 | 0.023254 | 0.2198 | 0.10636 | 5.5642 | 5.504 | 5.4747 | 5.5192 | 5.6958 | 5.4975 | 5.2205 | 116.9734 | -5.5738 | 116.8681 | 116.909 | -0.064411 | -5.653 | -5.4565 | 122.0876 | -0.15709 | 122.4312 | 122.3418 | 0.25419 | 0.019482 | -0.17877 | 116.9696 | 116.8903 | 117.0869 | 117.0104 | -5.5699 | 122.3862 | 122.5628 | 122.3646 | 122.371 | -0.45573
1092.625 | 122.7722 | -116.684 | 5.8228 | 0.0069442 | 0.020434 | -0.062873 | 0.018802 | -0.0012648 | 0.023398 | -0.0061807 | 0.048325 | 0.057435 | 0.045165 | 0.0066879 | 0.021353 | 0.010204 | 0.14792 | 0.04653 | 0.10707 | 0.032411 | 0.22438 | 0.11094 | 5.4085 | 5.3803 | 5.3648 | 5.4093 | 5.5767 | 5.4013 | 5.1152 | 116.7949 | -5.7157 | 116.6942 | 116.7305 | -0.064412 | -5.7903 | -5.5984 | 121.7992 | -0.41346 | 122.0925 | 122.0488 | 0.24961 | -0.24604 | -0.42141 | 116.791 | 116.7164 | 116.9083 | 116.8319 | -5.7118 | 122.0933 | 122.2607 | 122.0853 | 122.0643 | -0.70753
1094.3594 | 122.6669 | -116.3498 | 6.2119 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.0010512 | 0.023185 | -0.0061807 | 0.050889 | 0.05829 | 0.050079 | 0.0069017 | 0.021566 | -0.008109 | 0.097557 | 0.037373 | 0.11165 | 0.032411 | 0.22438 | 0.11552 | 6.0266 | 5.9985 | 5.9738 | 6.0228 | 6.1811 | 5.9828 | 5.6967 | 116.4653 | -6.1002 | 116.3417 | 116.3872 | -0.078148 | -6.1794 | -5.9875 | 122.0465 | -0.18904 | 122.3764 | 122.3236 | 0.27707 | -0.030769 | -0.22903 | 116.4614 | 116.3822 | 116.5742 | 116.4473 | -6.0963 | 122.3726 | 122.5309 | 122.3326 | 122.3483 | -0.51512
1096.0469 | 122.6532 | -115.8005 | 6.7657 | -0.00068679 | 0.020434 | -0.062659 | 0.018802 | -0.0012648 | 0.022971 | 0.0014498 | 0.043198 | 0.050171 | 0.042388 | 0.0064743 | 0.02178 | 0.001048 | 0.097557 | 0.037373 | 0.11165 | -0.013378 | 0.2198 | 0.1201 | 6.6173 | 6.58 | 6.5736 | 6.5951 | 6.7671 | 6.4361 | 6.2599 | 115.9206 | -6.6541 | 115.8015 | 115.8378 | -0.082727 | -6.7791 | -6.5459 | 122.0604 | -0.17062 | 122.4178 | 122.3741 | 0.31369 | 0.001398 | -0.32964 | 115.9121 | 115.7871 | 116.0203 | 115.898 | -6.6456 | 122.3956 | 122.5676 | 122.2366 | 122.3804 | -0.50582
1097.7812 | 122.4609 | -72.2672 | 50.3448 | 0.0069442 | 0.020647 | -0.063086 | 0.018802 | -0.00083764 | 0.023398 | 0.0090803 | 0.044907 | 0.053376 | 0.041533 | 0.0069017 | 0.02178 | -0.021844 | 0.10214 | 0.023639 | 0.10707 | 0.027833 | 0.21522 | 0.11552 | 49.941 | 49.8121 | 50.0073 | 49.7795 | 49.9617 | 49.736 | 8.4166 | 72.3827 | -50.2378 | 72.2453 | 72.2908 | -0.091882 | -50.317 | -50.1296 | 80.6837 | -0.56535 | 122.2082 | 122.2744 | 41.5907 | -0.38317 | -0.6089 | 72.3742 | 72.295 | 72.4824 | 72.3693 | -50.2293 | 122.0466 | 122.2288 | 122.0031 | 122.0793 | -41.9283
1099.5156 | 122.6715 | -72.2351 | 50.2396 | 0.0069442 | 0.020861 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.051529 | 0.06235 | 0.046233 | 0.0069017 | 0.021994 | -0.012688 | 0.14334 | 0.028217 | 0.10249 | 0.004938 | 0.21522 | 0.11094 | 50.2112 | 50.1098 | 50.2866 | 50.0588 | 50.2501 | 49.8642 | 8.4166 | 72.346 | -50.1371 | 72.2224 | 72.2633 | -0.082725 | -50.2346 | -50.0243 | 80.6517 | -0.18078 | 122.4463 | 122.5217 | 41.87 | 0.01057 | -0.37541 | 72.3376 | 72.24 | 72.4503 | 72.3785 | -50.1286 | 122.2939 | 122.4852 | 122.0993 | 122.3449 | -41.823
1101.2656 | 122.5983 | -72.2946 | 50.2258 | 0.0069442 | 0.020647 | -0.062659 | 0.018375 | -0.0012648 | 0.023398 | -0.0061807 | 0.051102 | 0.062777 | 0.046233 | 0.0064743 | 0.021566 | -0.012688 | 0.13876 | 0.032795 | 0.10249 | 0.000359 | 0.22438 | 0.11552 | 50.1608 | 50.0411 | 50.2408 | 49.9993 | 50.1952 | 49.8275 | 8.4761 | 72.4101 | -50.1233 | 72.2819 | 72.3274 | -0.082726 | -50.2255 | -50.0014 | 80.7707 | -0.22657 | 122.4554 | 122.5354 | 41.7647 | -0.03064 | -0.39831 | 72.3971 | 72.295 | 72.519 | 72.4334 | -50.1103 | 122.2939 | 122.4898 | 122.1221 | 122.3357 | -41.7498
1103 | 122.7173 | -72.5052 | 49.9191 | -0.00068679 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023398 | 0.0090803 | 0.053025 | 0.063418 | 0.045165 | 0.0071153 | 0.021566 | -0.003531 | 0.14792 | 0.028217 | 0.093333 | 0.009517 | 0.2198 | 0.11094 | 49.8998 | 49.8167 | 49.9752 | 49.7383 | 49.9342 | 49.6535 | 8.4349 | 72.6161 | -49.8258 | 72.5017 | 72.5334 | -0.082725 | -49.9096 | -49.6993 | 80.9401 | -0.18084 | 122.405 | 122.4804 | 41.5403 | 0.015082 | -0.26559 | 72.5985 | 72.5147 | 72.725 | 72.6531 | -49.8082 | 122.2435 | 122.4394 | 122.1587 | 122.3219 | -41.4843
1104.6875 | 122.6486 | -72.0612 | 50.4044 | -0.0083178 | 0.020861 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.053452 | 0.065127 | 0.041533 | 0.0069017 | 0.021566 | -0.012688 | 0.16166 | 0.028217 | 0.10249 | -0.00422 | 0.2198 | 0.11094 | 50.3211 | 50.2563 | 50.3965 | 50.1687 | 50.36 | 50.0748 | 8.4486 | 72.1721 | -50.3019 | 72.0485 | 72.0894 | -0.082725 | -50.4086 | -50.1846 | 80.5098 | -0.23569 | 122.3822 | 122.4576 | 41.9478 | -0.044338 | -0.32959 | 72.1636 | 72.0569 | 72.281 | 72.2228 | -50.2934 | 122.2298 | 122.4212 | 122.1359 | 122.3174 | -41.9558
1106.4219 | 122.6807 | -72.0703 | 50.3632 | -0.015949 | 0.020434 | -0.062659 | 0.018802 | -0.0012648 | 0.023612 | 0.0090803 | 0.053666 | 0.064914 | 0.041106 | 0.0071153 | 0.02178 | 0.005626 | 0.1525 | 0.032795 | 0.10249 | -0.008799 | 0.21522 | 0.1201 | 50.2615 | 50.1784 | 50.3369 | 50.1 | 50.3005 | 49.7726 | 8.4623 | 72.1904 | -50.2607 | 72.0759 | 72.1031 | -0.087305 | -50.372 | -50.1479 | 80.5327 | -0.26317 | 122.3319 | 122.4072 | 41.8746 | -0.062661 | -0.59058 | 72.1728 | 72.0615 | 72.2855 | 72.2228 | -50.2431 | 122.1703 | 122.3708 | 121.8429 | 122.2488 | -41.9008
1108.1719 | 122.7539 | -116.3818 | 6.0196 | -0.0083178 | 0.020861 | -0.0633 | 0.019229 | -0.0012648 | 0.023612 | -0.0061807 | 0.060075 | 0.070469 | 0.030851 | 0.0066879 | 0.02178 | 0.042253 | 0.16624 | 0.051108 | 0.11622 | 0.041569 | 0.23354 | 0.10636 | 6.7684 | 6.7631 | 6.6881 | 6.7233 | 6.8862 | 6.8711 | 6.3607 | 116.4882 | -5.9034 | 116.4241 | 116.4329 | -0.055255 | -5.978 | -5.7861 | 122.7425 | 0.70373 | 123.1502 | 123.0699 | 0.32742 | 0.8666 | 0.85148 | 116.4981 | 116.4234 | 116.6154 | 116.5481 | -5.9132 | 123.1052 | 123.268 | 123.2529 | 123.1449 | 0.34107
1109.8438 | 122.7676 | -114.6332 | 7.8323 | -0.00068679 | 0.020434 | -0.062659 | 0.018588 | -0.00062384 | 0.023398 | -0.0061807 | 0.054734 | 0.065982 | 0.042174 | 0.0066879 | 0.021566 | 0.037675 | 0.15708 | 0.055687 | 0.11165 | 0.055306 | 0.22896 | 0.10636 | 7.5284 | 7.5323 | 7.4482 | 7.4788 | 7.6371 | 7.6265 | 7.0521 | 114.7395 | -7.7207 | 114.6709 | 114.6889 | -0.050676 | -7.777 | -7.6034 | 121.6852 | -0.35356 | 122.1616 | 122.0813 | 0.39609 | -0.19526 | -0.20579 | 114.7448 | 114.6885 | 114.8621 | 114.7903 | -7.726 | 122.112 | 122.2703 | 122.2597 | 122.1655 | -0.78027
1111.5781 | 122.7219 | -115.1184 | 7.37 | -0.0083178 | 0.02022 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.058152 | 0.069187 | 0.033842 | 0.0071153 | 0.02178 | 0.10177 | 0.17081 | 0.060265 | 0.12538 | 0.064464 | 0.23812 | 0.097205 | 7.4277 | 7.4224 | 7.352 | 7.3826 | 7.5501 | 7.5304 | 6.9742 | 115.2156 | -7.2446 | 115.2202 | 115.1787 | -0.03694 | -7.3055 | -7.1319 | 122.0926 | 0.012634 | 122.5461 | 122.4704 | 0.37777 | 0.18009 | 0.1604 | 115.2438 | 115.1829 | 115.3565 | 115.2892 | -7.2728 | 122.501 | 122.6685 | 122.6488 | 122.5409 | -0.39577
1113.3281 | 122.6486 | -113.7131 | 8.8257 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.00083764 | 0.023398 | 0.0090803 | 0.055375 | 0.066623 | 0.04132 | 0.0069017 | 0.021353 | 0.037675 | 0.15708 | 0.051108 | 0.11165 | 0.055306 | 0.22896 | 0.10178 | 8.174 | 8.155 | 8.0938 | 8.106 | 8.2872 | 8.2675 | 7.4321 | 113.8149 | -8.714 | 113.7507 | 113.7642 | -0.050676 | -8.7704 | -8.5967 | 121.1452 | -0.71965 | 121.8871 | 121.8068 | 0.66164 | -0.53844 | -0.55813 | 113.8247 | 113.7684 | 113.942 | 113.8702 | -8.7239 | 121.8191 | 122.0003 | 121.9806 | 121.8681 | -1.3936
1115 | 122.7036 | -113.4384 | 9.0546 | -0.0083178 | 0.020647 | -0.063086 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.053025 | 0.064914 | 0.046233 | 0.0071153 | 0.022635 | 0.07888 | 0.16166 | 0.051108 | 0.12538 | 0.059885 | 0.24269 | 0.10178 | 8.4076 | 8.4252 | 8.3593 | 8.3578 | 8.5116 | 8.4003 | 7.02 | 113.5402 | -8.9292 | 113.5173 | 113.4895 | -0.050676 | -8.9947 | -8.8119 | 120.4584 | -0.69672 | 121.846 | 121.7977 | 1.3393 | -0.54297 | -0.65424 | 113.5638 | 113.4983 | 113.6811 | 113.6001 | -8.9528 | 121.7963 | 121.95 | 121.8387 | 121.8636 | -2.0346
1116.7344 | 122.7127 | -114.1434 | 8.3771 | -0.00068679 | 0.020434 | -0.063086 | 0.018588 | -0.0014786 | 0.023185 | -0.0061807 | 0.053666 | 0.064486 | 0.046447 | 0.0069017 | 0.022421 | 0.092615 | 0.16166 | 0.055687 | 0.12538 | 0.073622 | 0.23812 | 0.092626 | 8.3389 | 8.2832 | 8.2677 | 8.2663 | 8.4338 | 8.3042 | 7.7023 | 114.236 | -8.2517 | 114.236 | 114.1991 | -0.036939 | -8.3035 | -8.139 | 121.8456 | -0.1108 | 122.4822 | 122.4111 | 0.56548 | 0.056682 | -0.072897 | 114.2688 | 114.217 | 114.3815 | 114.305 | -8.2844 | 122.4097 | 122.5771 | 122.4476 | 122.4266 | -0.67482
1118.4219 | 122.7219 | -114.4684 | 8.0246 | -0.00068679 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023185 | -0.0061807 | 0.054093 | 0.064273 | 0.049225 | 0.0069017 | 0.022421 | 0.097194 | 0.16166 | 0.060265 | 0.13454 | 0.069043 | 0.24269 | 0.097205 | 7.8306 | 7.7842 | 7.7641 | 7.7764 | 7.9438 | 7.7593 | 7.3222 | 114.5656 | -7.8901 | 114.5656 | 114.5286 | -0.03694 | -7.9556 | -7.7819 | 121.7906 | -0.24822 | 122.299 | 122.2325 | 0.44187 | -0.080751 | -0.26527 | 114.6029 | 114.5374 | 114.7111 | 114.63 | -7.9274 | 122.2448 | 122.4122 | 122.2277 | 122.2525 | -0.70238
1120.1719 | 122.6761 | -114.2441 | 8.2764 | -0.015949 | 0.020861 | -0.062659 | 0.018588 | -0.0012648 | 0.022971 | -0.013811 | 0.060502 | 0.068546 | 0.036833 | 0.0066879 | 0.022421 | 0.083459 | 0.16624 | 0.060265 | 0.13454 | 0.073622 | 0.24269 | 0.097205 | 8.1328 | 8.0909 | 8.0709 | 8.074 | 8.2415 | 8.121 | 7.5512 | 114.3413 | -8.1418 | 114.3275 | 114.3043 | -0.03694 | -8.2027 | -8.0337 | 121.7952 | -0.20238 | 122.3769 | 122.3149 | 0.5197 | -0.034912 | -0.15533 | 114.3786 | 114.3177 | 114.4868 | 114.4103 | -8.1792 | 122.3181 | 122.4855 | 122.3651 | 122.335 | -0.72521
1121.8594 | 122.6532 | -113.7955 | 8.7341 | -0.00068679 | 0.020861 | -0.062659 | 0.018802 | -0.0012648 | 0.023398 | -0.0061807 | 0.053666 | 0.064059 | 0.048584 | 0.0069017 | 0.022421 | 0.088037 | 0.16166 | 0.060265 | 0.12996 | 0.073622 | 0.24727 | 0.10178 | 8.3755 | 8.3153 | 8.3044 | 8.3075 | 8.4887 | 8.263 | 7.7206 | 113.8973 | -8.6042 | 113.8835 | 113.8557 | -0.041519 | -8.6605 | -8.4869 | 121.516 | -0.42665 | 122.171 | 122.0998 | 0.5838 | -0.24543 | -0.47116 | 113.9254 | 113.8691 | 114.0427 | 113.9571 | -8.6323 | 122.103 | 122.2842 | 122.0584 | 122.1108 | -1.0136
1123.6094 | 122.7722 | -111.9644 | 10.4553 | -0.0083178 | 0.020861 | -0.063086 | 0.018802 | -0.0012648 | 0.023612 | 0.0014498 | 0.053666 | 0.063632 | 0.04837 | 0.0066879 | 0.022207 | 0.074302 | 0.15708 | 0.051108 | 0.1208 | 0.064464 | 0.24269 | 0.10178 | 10.7656 | 10.6962 | 10.7128 | 10.6608 | 10.8696 | 10.772 | 8.3799 | 112.0662 | -10.3345 | 112.0387 | 112.0155 | -0.050676 | -10.3909 | -10.2126 | 120.3443 | 0.20551 | 122.73 | 122.6772 | 2.3328 | 0.41425 | 0.31672 | 112.0852 | 112.0289 | 112.2071 | 112.1215 | -10.3535 | 122.6252 | 122.834 | 122.7365 | 122.6606 | -2.0754
1125.2812 | 122.7493 | -112.0056 | 10.405 | -0.0083178 | 0.020647 | -0.062873 | 0.018588 | -0.0012648 | 0.023612 | 0.0014498 | 0.055589 | 0.064486 | 0.046661 | 0.0069017 | 0.022421 | 0.074302 | 0.1525 | 0.041952 | 0.12538 | 0.064464 | 0.24269 | 0.11094 | 10.3398 | 10.3254 | 10.2778 | 10.2533 | 10.4163 | 10.4012 | 8.4578 | 112.1166 | -10.2796 | 112.0799 | 112.0476 | -0.06899 | -10.3405 | -10.1623 | 120.4634 | -0.15162 | 122.3454 | 122.2834 | 1.82 | 0.011323 | -0.00379 | 112.131 | 112.0701 | 112.2483 | 112.1581 | -10.294 | 122.259 | 122.4219 | 122.4068 | 122.331 | -1.9472
1127.0156 | 122.6944 | -112.4084 | 10.0845 | -0.00068679 | 0.020647 | -0.062659 | 0.018375 | -0.0012648 | 0.023612 | -0.013811 | 0.056657 | 0.065341 | 0.04367 | 0.0069017 | 0.022635 | 0.083459 | 0.15708 | 0.037373 | 0.12996 | 0.073622 | 0.24727 | 0.10636 | 9.9323 | 9.9224 | 9.8749 | 9.8504 | 10.0088 | 9.8746 | 8.3937 | 112.5148 | -9.9546 | 112.4919 | 112.4458 | -0.06899 | -10.0109 | -9.8373 | 120.8021 | -0.2341 | 122.3407 | 122.2833 | 1.4812 | -0.075738 | -0.20989 | 112.5384 | 112.4821 | 112.6557 | 112.5655 | -9.9782 | 122.2589 | 122.4172 | 122.2831 | 122.3309 | -1.6909
1128.7031 | 122.6852 | -110.9207 | 11.6135 | 0.0069442 | 0.02022 | -0.063086 | 0.019016 | -0.00083764 | 0.023612 | -0.0061807 | 0.05623 | 0.064486 | 0.047088 | 0.0071153 | 0.022421 | 0.074302 | 0.1525 | 0.041952 | 0.12538 | 0.078201 | 0.24727 | 0.10636 | 11.2738 | 11.2365 | 11.2119 | 11.1736 | 11.332 | 11.1933 | 8.531 | 111.0271 | -11.4881 | 110.995 | 110.9627 | -0.064411 | -11.5353 | -11.3662 | 119.4517 | -0.43984 | 122.1945 | 122.1326 | 2.6808 | -0.28145 | -0.42019 | 111.0461 | 110.9989 | 111.168 | 111.0732 | -11.5071 | 122.0943 | 122.2527 | 122.114 | 122.1572 | -3.0824
1130.4375 | 122.7768 | -111.8591 | 10.6064 | -0.00068679 | 0.020434 | -0.063086 | 0.019016 | -0.0016922 | 0.023185 | -0.0061807 | 0.054307 | 0.063204 | 0.050293 | 0.0069017 | 0.022207 | 0.074302 | 0.14334 | 0.041952 | 0.1208 | 0.073622 | 0.24269 | 0.097205 | 10.587 | 10.5177 | 10.5113 | 10.4823 | 10.6544 | 10.392 | 8.4898 | 111.9563 | -10.4856 | 111.9334 | 111.9011 | -0.055253 | -10.5328 | -10.3637 | 120.3489 | -0.12411 | 122.4462 | 122.3704 | 2.0215 | 0.047995 | -0.21436 | 111.9799 | 111.9328 | 112.1018 | 112.0025 | -10.5092 | 122.3414 | 122.5135 | 122.2512 | 122.3768 | -2.1166
1132.1719 | 122.7127 | -111.4883 | 10.9955 | -0.0083178 | 0.020647 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | -0.0061807 | 0.05452 | 0.065127 | 0.045379 | 0.0069017 | 0.022421 | 0.074302 | 0.14334 | 0.037373 | 0.1208 | 0.069043 | 0.24727 | 0.10636 | 10.9487 | 10.9023 | 10.8913 | 10.8577 | 11.0161 | 10.8499 | 8.5173 | 111.5947 | -10.8747 | 111.5626 | 111.5257 | -0.06899 | -10.9264 | -10.7482 | 120.0056 | -0.13778 | 122.4371 | 122.3797 | 2.3741 | 0.020605 | -0.1456 | 111.6091 | 111.5574 | 111.7356 | 111.6317 | -10.8891 | 122.346 | 122.5044 | 122.3382 | 122.3906 | -2.4782
1133.9219 | 122.7219 | -111.4792 | 10.9909 | 0.0069442 | 0.020861 | -0.063086 | 0.018802 | -0.00083764 | 0.023398 | 0.0090803 | 0.055802 | 0.066195 | 0.042601 | 0.0069017 | 0.022421 | 0.065145 | 0.13876 | 0.032795 | 0.12538 | 0.069043 | 0.24269 | 0.10178 | 10.9442 | 10.8885 | 10.8822 | 10.8531 | 11.0161 | 10.8682 | 8.5219 | 111.581 | -10.8655 | 111.5443 | 111.512 | -0.068989 | -10.9219 | -10.7482 | 120.0011 | -0.13778 | 122.4234 | 122.3614 | 2.3603 | 0.025182 | -0.12271 | 111.6046 | 111.5482 | 111.7219 | 111.618 | -10.8891 | 122.3323 | 122.4953 | 122.3474 | 122.3677 | -2.469
1135.5938 | 122.7219 | -115.4114 | 7.0541 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.00062384 | 0.023612 | 0.0090803 | 0.055375 | 0.068332 | 0.03726 | 0.0069017 | 0.022635 | 0.065145 | 0.14334 | 0.041952 | 0.12538 | 0.069043 | 0.23812 | 0.11094 | 6.6676 | 6.6441 | 6.5874 | 6.6134 | 6.7946 | 6.7612 | 6.1638 | 115.5223 | -6.9288 | 115.4765 | 115.4533 | -0.06899 | -6.9851 | -6.816 | 121.5752 | -0.4407 | 122.079 | 121.9987 | 0.42358 | -0.25952 | -0.29295 | 115.5368 | 115.4804 | 115.6495 | 115.5547 | -6.9432 | 122.0248 | 122.206 | 122.1726 | 122.0554 | -0.89036
1137.3281 | 122.7814 | -115.2237 | 7.196 | -0.00068679 | 0.020861 | -0.0633 | 0.018802 | -0.0012648 | 0.023612 | 0.0090803 | 0.053239 | 0.067477 | 0.040892 | 0.0066879 | 0.021994 | 0.060567 | 0.13876 | 0.028217 | 0.1208 | 0.069043 | 0.23812 | 0.10178 | 7.1759 | 7.1798 | 7.1048 | 7.1171 | 7.2799 | 7.274 | 6.7407 | 115.3255 | -7.0752 | 115.2843 | 115.2519 | -0.073567 | -7.127 | -6.9579 | 121.9644 | -0.078968 | 122.3996 | 122.3284 | 0.36404 | 0.083904 | 0.077948 | 115.3445 | 115.2927 | 115.4618 | 115.3625 | -7.0943 | 122.3408 | 122.5036 | 122.4977 | 122.4035 | -0.45534
1139.0781 | 122.644 | -114.8987 | 7.6538 | -0.0083178 | 0.020861 | -0.062873 | 0.018161 | -0.0014786 | 0.023398 | -0.0061807 | 0.05452 | 0.06705 | 0.049438 | 0.0069017 | 0.022421 | 0.065145 | 0.13419 | 0.01906 | 0.12996 | 0.073622 | 0.23812 | 0.10636 | 7.6475 | 7.656 | 7.5626 | 7.5887 | 7.7607 | 7.741 | 7.162 | 115.005 | -7.5238 | 114.9638 | 114.9177 | -0.087303 | -7.5802 | -7.4157 | 122.0606 | -0.065147 | 122.5462 | 122.4613 | 0.40066 | 0.10689 | 0.087201 | 115.0286 | 114.9723 | 115.1368 | 115.0329 | -7.5474 | 122.4873 | 122.6594 | 122.6397 | 122.5546 | -0.49185
1140.8125 | 122.6852 | -115.6952 | 6.8207 | 0.014575 | 0.020434 | -0.062659 | 0.018161 | -0.0014786 | 0.023398 | 0.0090803 | 0.051957 | 0.066623 | 0.045806 | 0.0066879 | 0.022421 | 0.055988 | 0.13876 | 0.014482 | 0.12996 | 0.069043 | 0.24269 | 0.10636 | 7.2079 | 7.2164 | 7.146 | 7.1629 | 7.3257 | 7.1916 | 6.7773 | 115.8016 | -6.6907 | 115.7512 | 115.7097 | -0.091881 | -6.7516 | -6.578 | 122.4725 | 0.34218 | 122.9031 | 122.8411 | 0.36862 | 0.50506 | 0.3709 | 115.8251 | 115.7642 | 115.9379 | 115.834 | -6.7143 | 122.8581 | 123.0209 | 122.8868 | 122.9116 | -0.043341
1142.5469 | 122.7631 | -114.3997 | 8.1024 | -0.00068679 | 0.021075 | -0.062873 | 0.018588 | -0.0012648 | 0.023826 | 0.0014498 | 0.053239 | 0.064914 | 0.048584 | 0.0071153 | 0.022421 | 0.055988 | 0.13419 | 0.014482 | 0.11622 | 0.069043 | 0.24269 | 0.11552 | 8.2473 | 8.2054 | 8.1807 | 8.1701 | 8.3468 | 8.1714 | 7.6382 | 114.5152 | -7.9862 | 114.4557 | 114.4142 | -0.10104 | -8.0334 | -7.8597 | 122.0379 | 0.067714 | 122.647 | 122.5805 | 0.54259 | 0.24435 | 0.068982 | 114.5159 | 114.4688 | 114.6424 | 114.5339 | -7.9869 | 122.5699 | 122.7465 | 122.5711 | 122.6051 | -0.46426
1144.2344 | 122.6669 | -114.0472 | 8.5098 | 0.0069442 | 0.020647 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | -0.0061807 | 0.051529 | 0.065341 | 0.046447 | 0.0069017 | 0.022421 | 0.055988 | 0.12503 | 0.014482 | 0.1208 | 0.069043 | 0.24269 | 0.10636 | 8.5907 | 8.5397 | 8.5196 | 8.5227 | 8.6856 | 8.5514 | 7.8579 | 114.1536 | -8.389 | 114.1032 | 114.0617 | -0.091881 | -8.4408 | -8.2671 | 121.9052 | 0.012848 | 122.6379 | 122.5668 | 0.66163 | 0.17575 | 0.041596 | 114.168 | 114.1163 | 114.2899 | 114.1723 | -8.4035 | 122.5699 | 122.7328 | 122.5987 | 122.5869 | -0.65189
1145.9531 | 122.7493 | -113.5803 | 8.9081 | -0.00068679 | 0.020647 | -0.063086 | 0.018588 | -0.00083764 | 0.023612 | 0.0014498 | 0.053452 | 0.064273 | 0.050079 | 0.0064743 | 0.022421 | 0.05141 | 0.12503 | 0.023639 | 0.12538 | 0.073622 | 0.23812 | 0.11094 | 9.0852 | 9.0342 | 9.0278 | 9.0126 | 9.1801 | 9.0642 | 8.1372 | 113.6913 | -8.7827 | 113.6317 | 113.604 | -0.087303 | -8.8345 | -8.67 | 121.7176 | 0.10449 | 122.6655 | 122.6081 | 0.89056 | 0.27199 | 0.15615 | 113.7057 | 113.6539 | 113.8184 | 113.7054 | -8.7971 | 122.5929 | 122.7604 | 122.6445 | 122.6145 | -0.77083
1147.6875 | 122.7264 | -114.1571 | 8.345 | -0.00068679 | 0.020647 | -0.063514 | 0.018588 | -0.0014786 | 0.023398 | -0.0061807 | 0.054093 | 0.063418 | 0.051147 | 0.0064743 | 0.021994 | 0.05141 | 0.13419 | 0.01906 | 0.1208 | 0.059885 | 0.23812 | 0.10636 | 8.783 | 8.7274 | 8.7119 | 8.7012 | 8.8733 | 8.5926 | 7.977 | 114.2635 | -8.2242 | 114.2085 | 114.1762 | -0.087303 | -8.2851 | -8.1069 | 122.1341 | 0.3562 | 122.9401 | 122.869 | 0.73489 | 0.52827 | 0.2476 | 114.2779 | 114.217 | 114.3952 | 114.2913 | -8.2387 | 122.8583 | 123.0304 | 122.7497 | 122.8845 | -0.36804
1149.3594 | 122.6166 | -113.6261 | 8.8715 | -0.00068679 | 0.020647 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | 0.0014498 | 0.052384 | 0.0647 | 0.048584 | 0.0066879 | 0.022421 | 0.055988 | 0.12503 | 0.01906 | 0.12996 | 0.073622 | 0.24727 | 0.10636 | 8.8975 | 8.8647 | 8.8263 | 8.8203 | 8.9878 | 8.7849 | 8.0274 | 113.7325 | -8.7415 | 113.6821 | 113.6452 | -0.087303 | -8.7978 | -8.6242 | 121.6535 | -0.051183 | 122.5236 | 122.4524 | 0.79899 | 0.11631 | -0.086528 | 113.7561 | 113.6997 | 113.8734 | 113.7511 | -8.7651 | 122.4464 | 122.6139 | 122.411 | 122.4908 | -0.84411
1151.0938 | 122.6349 | -114.0106 | 8.5052 | -0.00068679 | 0.020434 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | 0.0014498 | 0.051529 | 0.0647 | 0.047515 | 0.0066879 | 0.022207 | 0.055988 | 0.12961 | 0.032795 | 0.13454 | 0.064464 | 0.24727 | 0.10636 | 8.5953 | 8.5397 | 8.5287 | 8.5135 | 8.6902 | 8.4644 | 7.8717 | 114.117 | -8.3707 | 114.0666 | 114.0434 | -0.073568 | -8.4408 | -8.258 | 121.8823 | 0.008269 | 122.6059 | 122.5393 | 0.65705 | 0.18491 | -0.040819 | 114.1452 | 114.0751 | 114.2579 | 114.1402 | -8.3989 | 122.5241 | 122.7008 | 122.4751 | 122.5503 | -0.63357
1152.8281 | 122.6257 | -113.8458 | 8.7067 | -0.00068679 | 0.020861 | -0.062659 | 0.018802 | -0.0010512 | 0.023826 | -0.0061807 | 0.05217 | 0.064486 | 0.048797 | 0.0069017 | 0.022207 | 0.060567 | 0.13419 | 0.01906 | 0.12996 | 0.078201 | 0.24269 | 0.10178 | 8.6319 | 8.5809 | 8.5699 | 8.5639 | 8.7176 | 8.6247 | 7.8991 | 113.9476 | -8.5767 | 113.9064 | 113.8649 | -0.082724 | -8.6285 | -8.464 | 121.745 | -0.14278 | 122.4777 | 122.4158 | 0.67079 | 0.010965 | -0.081984 | 113.9758 | 113.924 | 114.0885 | 113.98 | -8.6049 | 122.4097 | 122.5635 | 122.4705 | 122.4267 | -0.80752
1154.5781 | 122.612 | -114.1434 | 8.3725 | -0.0083178 | 0.020647 | -0.063086 | 0.018588 | -0.0014786 | 0.023612 | 0.0014498 | 0.053666 | 0.063204 | 0.051788 | 0.0071153 | 0.022207 | 0.065145 | 0.14334 | 0.028217 | 0.13454 | 0.069043 | 0.24727 | 0.097205 | 8.5037 | 8.4847 | 8.4692 | 8.4723 | 8.6352 | 8.4324 | 7.8305 | 114.2406 | -8.238 | 114.2085 | 114.1716 | -0.068988 | -8.3035 | -8.1252 | 121.9738 | 0.099813 | 122.6471 | 122.6126 | 0.63874 | 0.26272 | 0.059881 | 114.2779 | 114.2124 | 114.3906 | 114.2867 | -8.2753 | 122.6157 | 122.7786 | 122.5758 | 122.6281 | -0.54203
1156.25 | 122.6028 | -111.8179 | 10.6979 | -0.0083178 | 0.020647 | -0.0633 | 0.018802 | -0.0012648 | 0.023398 | -0.0061807 | 0.052384 | 0.063845 | 0.049011 | 0.0069017 | 0.022207 | 0.060567 | 0.14334 | 0.032795 | 0.12996 | 0.073622 | 0.24727 | 0.10636 | 10.6557 | 10.6459 | 10.6395 | 10.6059 | 10.7597 | 10.6438 | 8.5081 | 111.9243 | -10.568 | 111.8785 | 111.8507 | -0.073568 | -10.6243 | -10.4507 | 120.3261 | -0.092047 | 122.4736 | 122.4574 | 2.1314 | 0.06175 | -0.054093 | 111.9479 | 111.8916 | 112.0652 | 111.9613 | -10.5916 | 122.4238 | 122.5776 | 122.4618 | 122.4638 | -2.1898
1157.9844 | 122.6166 | -111.7172 | 10.8307 | 0.0069442 | 0.020647 | -0.063086 | 0.018588 | -0.0012648 | 0.023612 | 0.0090803 | 0.050461 | 0.065341 | 0.045379 | 0.0069017 | 0.022421 | 0.065145 | 0.13419 | 0.037373 | 0.12538 | 0.08278 | 0.25185 | 0.10178 | 10.7061 | 10.6916 | 10.6853 | 10.6471 | 10.8238 | 10.5706 | 8.5036 | 111.819 | -10.7053 | 111.7824 | 111.7546 | -0.064411 | -10.7479 | -10.5788 | 120.2208 | -0.18359 | 122.4233 | 122.4025 | 2.1817 | -0.006901 | -0.2601 | 111.8426 | 111.8 | 111.9691 | 111.8514 | -10.7289 | 122.3643 | 122.541 | 122.2878 | 122.4089 | -2.3271
1159.7188 | 122.6486 | -112.056 | 10.4599 | -0.00068679 | 0.020434 | -0.0633 | 0.018588 | -0.0010512 | 0.023826 | 0.0090803 | 0.050889 | 0.065341 | 0.045593 | 0.0069017 | 0.022421 | 0.060567 | 0.13419 | 0.032795 | 0.13454 | 0.078201 | 0.25643 | 0.10636 | 10.4313 | 10.4169 | 10.4106 | 10.3724 | 10.5445 | 10.3325 | 8.4807 | 112.1623 | -10.3254 | 112.1165 | 112.0888 | -0.073568 | -10.3817 | -10.2035 | 120.5366 | -0.087513 | 122.4873 | 122.4665 | 1.9299 | 0.084592 | -0.1274 | 112.1905 | 112.1342 | 112.3124 | 112.1902 | -10.3535 | 122.4284 | 122.6005 | 122.3885 | 122.4729 | -1.9792
1161.4688 | 122.6532 | -72.2031 | 50.3036 | -0.0083178 | 0.020647 | -0.063086 | 0.018375 | -0.0010512 | 0.023398 | 0.0090803 | 0.04982 | 0.064059 | 0.044524 | 0.0073291 | 0.022421 | 0.065145 | 0.12961 | 0.01906 | 0.13454 | 0.073622 | 0.24727 | 0.10636 | 50.2799 | 50.1876 | 50.3415 | 50.1091 | 50.2959 | 50.0244 | 8.4852 | 72.3094 | -50.1691 | 72.2682 | 72.2221 | -0.087303 | -50.23 | -50.0564 | 80.6883 | -0.1945 | 122.4829 | 122.5446 | 41.8563 | -0.007731 | -0.27924 | 72.3376 | 72.2767 | 72.4503 | 72.3327 | -50.1973 | 122.3122 | 122.499 | 122.2275 | 122.3907 | -41.8184
1163.1406 | 122.6807 | -72.4091 | 50.0244 | -0.0083178 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.04982 | 0.064273 | 0.044738 | 0.0066879 | 0.022635 | 0.055988 | 0.13876 | 0.028217 | 0.12996 | 0.078201 | 0.24269 | 0.10636 | 50.0143 | 49.9175 | 50.0805 | 49.8482 | 50.0349 | 49.6947 | 8.4623 | 72.5154 | -49.8945 | 72.465 | 72.4373 | -0.078146 | -49.9462 | -49.7817 | 80.8714 | -0.17624 | 122.4234 | 122.4896 | 41.6182 | 0.010525 | -0.32967 | 72.539 | 72.4873 | 72.6518 | 72.5478 | -49.9181 | 122.2572 | 122.444 | 122.1038 | 122.3265 | -41.5621
1164.8906 | 122.6944 | -72.6242 | 49.7818 | -0.0083178 | 0.020434 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | 0.0014498 | 0.050248 | 0.064273 | 0.044952 | 0.0064743 | 0.022421 | 0.05141 | 0.12961 | 0.01906 | 0.12538 | 0.078201 | 0.24727 | 0.10178 | 49.8449 | 49.7435 | 49.9111 | 49.6788 | 49.8747 | 49.5391 | 8.4715 | 72.726 | -49.6564 | 72.6756 | 72.6433 | -0.082724 | -49.7036 | -49.5345 | 81.0957 | -0.10303 | 122.4691 | 122.5353 | 41.4396 | 0.092889 | -0.24273 | 72.7496 | 72.7024 | 72.8715 | 72.7538 | -49.68 | 122.303 | 122.4989 | 122.1633 | 122.3677 | -41.3103
1166.6406 | 122.7219 | -72.5052 | 49.8779 | -0.00068679 | 0.02022 | -0.062659 | 0.018375 | -0.0010512 | 0.023612 | -0.0061807 | 0.050461 | 0.063845 | 0.04602 | 0.0064743 | 0.022207 | 0.055988 | 0.13876 | 0.01906 | 0.1208 | 0.073622 | 0.24727 | 0.10636 | 49.7121 | 49.6198 | 49.7829 | 49.5323 | 49.7465 | 49.562 | 8.4715 | 72.6116 | -49.7571 | 72.5612 | 72.5242 | -0.087303 | -49.8043 | -49.6307 | 80.9767 | -0.34567 | 122.2173 | 122.2881 | 41.3114 | -0.13144 | -0.31596 | 72.626 | 72.5788 | 72.7525 | 72.644 | -49.7716 | 122.0374 | 122.2517 | 122.0672 | 122.125 | -41.4064
1168.3281 | 122.6669 | -117.5034 | 4.9713 | 0.0069442 | 0.020647 | -0.062873 | 0.018375 | -0.0010512 | 0.023398 | -0.0061807 | 0.05217 | 0.065768 | 0.047302 | 0.0069017 | 0.022421 | 0.060567 | 0.13876 | 0.01906 | 0.12996 | 0.078201 | 0.24727 | 0.10636 | 4.8728 | 4.8813 | 4.7971 | 4.8507 | 5.0135 | 5.0076 | 4.5658 | 117.6097 | -4.8414 | 117.5639 | 117.5224 | -0.087303 | -4.8931 | -4.724 | 122.0691 | -0.12059 | 122.3762 | 122.3004 | 0.23131 | 0.042227 | 0.036272 | 117.6333 | 117.5816 | 117.7506 | 117.6421 | -4.865 | 122.3541 | 122.5169 | 122.5109 | 122.3846 | -0.40554
1170.0781 | 122.731 | -117.3889 | 5.0766 | 0.0069442 | 0.02022 | -0.062659 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.05217 | 0.066195 | 0.046661 | 0.0073291 | 0.022421 | 0.05141 | 0.12961 | 0.037373 | 0.13454 | 0.078201 | 0.24727 | 0.10636 | 5.0376 | 5.0369 | 4.9528 | 5.0064 | 5.1738 | 5.1495 | 4.7169 | 117.4953 | -4.9421 | 117.4403 | 117.4263 | -0.06899 | -4.9984 | -4.8293 | 122.1058 | -0.070209 | 122.4265 | 122.3417 | 0.23589 | 0.097193 | 0.072922 | 117.5235 | 117.4671 | 117.6362 | 117.5185 | -4.9702 | 122.3953 | 122.5627 | 122.5384 | 122.4259 | -0.35973
1171.8281 | 122.6669 | -116.2628 | 6.2393 | -0.00068679 | 0.020434 | -0.0633 | 0.018802 | -0.0012648 | 0.023185 | 0.0090803 | 0.051957 | 0.065982 | 0.046233 | 0.0069017 | 0.022421 | 0.060567 | 0.14334 | 0.023639 | 0.12538 | 0.08278 | 0.24269 | 0.10178 | 6.2556 | 6.2503 | 6.1753 | 6.2014 | 6.3734 | 6.1751 | 5.889 | 116.3646 | -6.1139 | 116.3234 | 116.2865 | -0.078145 | -6.1565 | -5.9966 | 122.1519 | -0.037941 | 122.5184 | 122.4381 | 0.28622 | 0.13407 | -0.064191 | 116.3882 | 116.3456 | 116.5055 | 116.4062 | -6.1375 | 122.4642 | 122.6362 | 122.4379 | 122.5131 | -0.35027
1173.5156 | 122.6898 | -116.2811 | 6.2531 | 0.0069442 | 0.020434 | -0.063086 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.05217 | 0.061709 | 0.050079 | 0.0069017 | 0.022421 | 0.069723 | 0.14792 | 0.023639 | 0.13454 | 0.08278 | 0.25185 | 0.11094 | 6.2098 | 6.2137 | 6.1249 | 6.1602 | 6.3368 | 6.198 | 5.8524 | 116.3921 | -6.1185 | 116.3509 | 116.3048 | -0.087303 | -6.1703 | -6.0012 | 122.1335 | -0.092881 | 122.4909 | 122.406 | 0.27249 | 0.083705 | -0.055031 | 116.4157 | 116.3639 | 116.533 | 116.429 | -6.1421 | 122.4413 | 122.6179 | 122.4791 | 122.4948 | -0.40064
1175.3125 | 122.6486 | -114.4501 | 8.0429 | 0.014575 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | 0.0090803 | 0.050675 | 0.062563 | 0.047302 | 0.0069017 | 0.022421 | 0.065145 | 0.13876 | 0.032795 | 0.12996 | 0.08278 | 0.25185 | 0.10636 | 7.7208 | 7.6605 | 7.6405 | 7.6573 | 7.8156 | 7.6174 | 7.2215 | 114.5564 | -7.9129 | 114.5152 | 114.4829 | -0.073568 | -7.9601 | -7.7911 | 121.6716 | -0.38557 | 122.1708 | 122.0905 | 0.41898 | -0.22726 | -0.42552 | 114.58 | 114.5329 | 114.7019 | 114.5888 | -7.9365 | 122.1074 | 122.2657 | 122.0675 | 122.1106 | -0.82143
1177.0469 | 122.612 | -114.7522 | 7.782 | 0.0069442 | 0.02022 | -0.062659 | 0.018588 | -0.0012648 | 0.023398 | -0.0061807 | 0.05217 | 0.063845 | 0.048156 | 0.0069017 | 0.022421 | 0.065145 | 0.14792 | 0.037373 | 0.13454 | 0.078201 | 0.24269 | 0.10636 | 7.8398 | 7.7887 | 7.7732 | 7.7764 | 7.9484 | 7.8005 | 7.3268 | 114.8586 | -7.6474 | 114.8173 | 114.7896 | -0.06899 | -7.7038 | -7.5393 | 122.079 | -0.005602 | 122.592 | 122.5254 | 0.44645 | 0.16644 | 0.01855 | 114.8867 | 114.8304 | 114.9949 | 114.9001 | -7.6756 | 122.5286 | 122.7006 | 122.5527 | 122.5409 | -0.45519
1178.7969 | 122.6257 | -113.974 | 8.5693 | 0.0069442 | 0.020006 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.053025 | 0.063845 | 0.049652 | 0.0066879 | 0.022421 | 0.074302 | 0.15708 | 0.037373 | 0.13454 | 0.091937 | 0.25185 | 0.11094 | 8.2473 | 8.2008 | 8.1853 | 8.1793 | 8.3422 | 8.1073 | 7.6336 | 114.0849 | -8.4348 | 114.0483 | 114.0114 | -0.073569 | -8.4774 | -8.3175 | 121.6076 | -0.39005 | 122.2213 | 122.1593 | 0.55175 | -0.22715 | -0.46204 | 114.1085 | 114.0659 | 114.2259 | 114.1311 | -8.4584 | 122.1533 | 122.3162 | 122.0813 | 122.1748 | -0.93576
1180.5 | 122.5983 | -113.9648 | 8.5281 | 0.0069442 | 0.020434 | -0.063086 | 0.018375 | -0.0010512 | 0.023185 | -0.0061807 | 0.053025 | 0.065982 | 0.048584 | 0.0066879 | 0.022635 | 0.069723 | 0.15708 | 0.041952 | 0.14369 | 0.08278 | 0.25643 | 0.097205 | 8.4442 | 8.3886 | 8.3776 | 8.3807 | 8.5391 | 8.3683 | 7.7755 | 114.062 | -8.3844 | 114.0346 | 114.0068 | -0.055253 | -8.4454 | -8.2717 | 121.7404 | -0.1474 | 122.409 | 122.3425 | 0.60211 | 0.010927 | -0.15986 | 114.1085 | 114.0476 | 114.2213 | 114.1219 | -8.4309 | 122.3456 | 122.5039 | 122.3331 | 122.3534 | -0.75262
1182.2031 | 122.699 | -113.6398 | 8.8394 | 0.014575 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023398 | 0.0090803 | 0.053239 | 0.065982 | 0.048156 | 0.0069017 | 0.022635 | 0.07888 | 0.17539 | 0.051108 | 0.15285 | 0.096516 | 0.25643 | 0.092626 | 8.6777 | 8.6129 | 8.6111 | 8.5959 | 8.7726 | 8.6018 | 7.922 | 113.7325 | -8.6866 | 113.7187 | 113.6909 | -0.041518 | -8.7429 | -8.583 | 121.5619 | -0.24349 | 122.3175 | 122.251 | 0.68911 | -0.066844 | -0.23763 | 113.7927 | 113.7363 | 113.8963 | 113.8152 | -8.7468 | 122.2358 | 122.4124 | 122.2416 | 122.2527 | -0.91737
1183.875 | 122.6532 | -113.681 | 8.7891 | -0.00068679 | 0.020434 | -0.063086 | 0.018802 | -0.0014786 | 0.023612 | -0.0061807 | 0.053239 | 0.066195 | 0.047729 | 0.0071153 | 0.022421 | 0.07888 | 0.16624 | 0.051108 | 0.14827 | 0.091937 | 0.26559 | 0.092626 | 8.5083 | 8.4572 | 8.4417 | 8.4357 | 8.594 | 8.4415 | 7.8122 | 113.7737 | -8.6408 | 113.7599 | 113.7321 | -0.041518 | -8.6971 | -8.5235 | 121.4932 | -0.35338 | 122.1893 | 122.1228 | 0.62958 | -0.19505 | -0.34753 | 113.8293 | 113.773 | 113.9466 | 113.8473 | -8.6964 | 122.1167 | 122.275 | 122.1226 | 122.1383 | -0.97691
1185.5469 | 122.6532 | -113.4613 | 9.0408 | -0.00068679 | 0.020434 | -0.062873 | 0.018802 | -0.0012648 | 0.023826 | 0.0014498 | 0.053025 | 0.0647 | 0.048584 | 0.0071153 | 0.022207 | 0.07888 | 0.17539 | 0.060265 | 0.15285 | 0.08278 | 0.27017 | 0.097205 | 8.9753 | 8.9288 | 8.9133 | 8.8935 | 9.061 | 8.9727 | 8.0915 | 113.5585 | -8.888 | 113.5402 | 113.5216 | -0.03694 | -8.9581 | -8.7707 | 121.5528 | -0.1473 | 122.4366 | 122.3746 | 0.82188 | 0.020192 | -0.068179 | 113.6142 | 113.5441 | 113.7315 | 113.6367 | -8.9436 | 122.3548 | 122.5223 | 122.434 | 122.3901 | -0.94937
1187.2969 | 122.612 | -113.6353 | 8.876 | 0.0069442 | 0.020647 | -0.062873 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.052811 | 0.0647 | 0.048797 | 0.0069017 | 0.021994 | 0.074302 | 0.17081 | 0.051108 | 0.14827 | 0.087359 | 0.27017 | 0.092626 | 8.6685 | 8.6083 | 8.602 | 8.5822 | 8.7543 | 8.6018 | 7.9175 | 113.7279 | -8.7278 | 113.7096 | 113.6864 | -0.041518 | -8.7887 | -8.6059 | 121.5527 | -0.29384 | 122.3038 | 122.2372 | 0.68452 | -0.12178 | -0.27425 | 113.7835 | 113.7226 | 113.9054 | 113.8061 | -8.7834 | 122.2174 | 122.3895 | 122.237 | 122.2436 | -0.95857
1188.9844 | 122.699 | -113.9923 | 8.4641 | -0.00068679 | 0.020434 | -0.0633 | 0.018375 | -0.0010512 | 0.023612 | 0.0090803 | 0.051529 | 0.062777 | 0.047729 | 0.0069017 | 0.022207 | 0.065145 | 0.16166 | 0.037373 | 0.13912 | 0.078201 | 0.25185 | 0.10636 | 8.4854 | 8.4572 | 8.4509 | 8.4448 | 8.6077 | 8.4599 | 7.8213 | 114.0987 | -8.3249 | 114.0575 | 114.0297 | -0.06899 | -8.3858 | -8.2122 | 121.8136 | -0.01921 | 122.4777 | 122.4432 | 0.62958 | 0.14369 | -0.004199 | 114.1314 | 114.0705 | 114.2442 | 114.154 | -8.3577 | 122.4372 | 122.6001 | 122.4522 | 122.4495 | -0.64274
1190.6719 | 122.5754 | -113.6398 | 8.8577 | -0.0083178 | 0.020006 | -0.062873 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.048539 | 0.061495 | 0.044952 | 0.0071153 | 0.022207 | 0.074302 | 0.15708 | 0.041952 | 0.13912 | 0.087359 | 0.26559 | 0.10178 | 8.7739 | 8.7411 | 8.7394 | 8.7195 | 8.8916 | 8.7071 | 7.9953 | 113.7416 | -8.7186 | 113.7141 | 113.6818 | -0.059832 | -8.7704 | -8.5921 | 121.6351 | -0.13818 | 122.4137 | 122.3792 | 0.74405 | 0.03389 | -0.15063 | 113.7789 | 113.7272 | 113.9054 | 113.7969 | -8.7559 | 122.3594 | 122.5314 | 122.3469 | 122.3809 | -0.86242
1192.3594 | 122.7402 | -113.6902 | 8.725 | -0.0083178 | 0.02022 | -0.062873 | 0.018375 | -0.0012648 | 0.023612 | -0.013811 | 0.052598 | 0.065768 | 0.048156 | 0.0069017 | 0.022635 | 0.069723 | 0.15708 | 0.074 | 0.15285 | 0.087359 | 0.26559 | 0.10636 | 8.5861 | 8.558 | 8.5608 | 8.5318 | 8.7039 | 8.5377 | 7.8854 | 113.7965 | -8.5721 | 113.7599 | 113.7642 | -0.032363 | -8.6376 | -8.4594 | 121.5756 | -0.19314 | 122.2763 | 122.251 | 0.67537 | -0.021082 | -0.18729 | 113.843 | 113.7775 | 113.9558 | 113.8473 | -8.6186 | 122.222 | 122.3941 | 122.2279 | 122.2482 | -0.83956
1194.0781 | 122.5616 | -113.1592 | 9.4025 | -0.00068679 | 0.020434 | -0.063086 | 0.018161 | -0.0012648 | 0.023398 | -0.0061807 | 0.055161 | 0.064273 | 0.051361 | 0.0064743 | 0.022421 | 0.069723 | 0.16166 | 0.074 | 0.14827 | 0.091937 | 0.26101 | 0.097205 | 9.4423 | 9.4188 | 9.417 | 9.388 | 9.5601 | 9.3802 | 8.2792 | 113.2564 | -9.2542 | 113.2289 | 113.2332 | -0.023205 | -9.3105 | -9.1415 | 121.4384 | -0.014456 | 122.6015 | 122.5762 | 1.1378 | 0.15763 | -0.022316 | 113.3075 | 113.2511 | 113.4202 | 113.3208 | -9.3053 | 122.5472 | 122.7193 | 122.5393 | 122.5779 | -1.1233
1195.7656 | 122.6761 | -113.0173 | 9.4986 | -0.00068679 | 0.020434 | -0.063086 | 0.018588 | -0.0012648 | 0.023826 | 0.0090803 | 0.053239 | 0.065768 | 0.049011 | 0.0066879 | 0.022421 | 0.065145 | 0.14792 | 0.064843 | 0.13912 | 0.08278 | 0.25185 | 0.097205 | 9.3508 | 9.3318 | 9.3208 | 9.301 | 9.4639 | 9.2016 | 8.2609 | 113.1145 | -9.3595 | 113.0824 | 113.0821 | -0.032362 | -9.4158 | -9.2467 | 121.2781 | -0.19758 | 122.368 | 122.3381 | 1.06 | -0.034654 | -0.29701 | 113.1564 | 113.1001 | 113.2691 | 113.1652 | -9.4014 | 122.3183 | 122.4812 | 122.2189 | 122.349 | -1.2377
1197.4688 | 122.7173 | -112.674 | 9.7549 | -0.0083178 | 0.020434 | -0.062873 | 0.018802 | -0.0012648 | 0.022971 | -0.0061807 | 0.054734 | 0.064486 | 0.052429 | 0.0066879 | 0.021994 | 0.065145 | 0.16624 | 0.060265 | 0.14369 | 0.087359 | 0.25643 | 0.097205 | 9.6118 | 9.5973 | 9.5452 | 9.5116 | 9.6791 | 9.6778 | 8.325 | 112.7712 | -9.6112 | 112.7391 | 112.7342 | -0.03694 | -9.6676 | -9.4985 | 120.9989 | -0.24331 | 122.2857 | 122.2192 | 1.2202 | -0.075808 | -0.077185 | 112.8176 | 112.7613 | 112.9304 | 112.8402 | -9.6577 | 122.1856 | 122.3531 | 122.3517 | 122.2713 | -1.43
1199.1562 | 122.5525 | -72.7158 | 49.791 | 0.0069442 | 0.020006 | -0.062659 | 0.018375 | -0.0010512 | 0.023612 | 0.0014498 | 0.053025 | 0.063204 | 0.050293 | 0.0071153 | 0.022421 | 0.055988 | 0.14334 | 0.055687 | 0.13912 | 0.08278 | 0.25185 | 0.097205 | 49.6892 | 49.6061 | 49.7692 | 49.5277 | 49.7236 | 49.4658 | 8.4486 | 72.813 | -49.6518 | 72.7717 | 72.7714 | -0.041518 | -49.7082 | -49.5391 | 81.1644 | -0.26328 | 122.405 | 122.4849 | 41.3206 | -0.067361 | -0.32514 | 72.8549 | 72.7985 | 72.9676 | 72.8591 | -49.6938 | 122.2434 | 122.4394 | 122.1816 | 122.3219 | -41.3423
1200.8438 | 122.6624 | -73.3246 | 49.0723 | -0.00068679 | 0.02022 | -0.062873 | 0.018375 | -0.0010512 | 0.023185 | 0.0014498 | 0.052811 | 0.063845 | 0.049225 | 0.0069017 | 0.022421 | 0.065145 | 0.14792 | 0.060265 | 0.14827 | 0.087359 | 0.25643 | 0.092626 | 48.9841 | 48.8918 | 49.0595 | 48.818 | 49.0185 | 48.8294 | 8.4852 | 73.4172 | -48.924 | 73.3897 | 73.3849 | -0.032361 | -48.9849 | -48.8158 | 81.8098 | -0.25426 | 122.3087 | 122.3841 | 40.5742 | -0.053777 | -0.24288 | 73.4729 | 73.4119 | 73.581 | 73.4725 | -48.9796 | 122.1426 | 122.3431 | 122.154 | 122.2164 | -40.587
1202.5312 | 122.5616 | -73.2468 | 49.1776 | -0.0083178 | 0.020006 | -0.063086 | 0.018375 | -0.0012648 | 0.023398 | 0.0090803 | 0.051957 | 0.0647 | 0.048156 | 0.0064743 | 0.022421 | 0.065145 | 0.14792 | 0.064843 | 0.14369 | 0.087359 | 0.26559 | 0.10178 | 49.1581 | 49.0612 | 49.2197 | 48.9783 | 49.1696 | 48.9759 | 8.4807 | 73.3485 | -49.0339 | 73.3119 | 73.3116 | -0.036941 | -49.0902 | -48.912 | 81.7274 | -0.19929 | 122.4048 | 122.4665 | 40.7391 | -0.007968 | -0.20165 | 73.3905 | 73.3341 | 73.5124 | 73.3947 | -49.0758 | 122.225 | 122.4163 | 122.2227 | 122.308 | -40.6969
1204.25 | 122.6395 | -73.4024 | 49.0173 | -0.0083178 | 0.02022 | -0.063086 | 0.018375 | -0.0010512 | 0.023398 | -0.0061807 | 0.053025 | 0.063418 | 0.050293 | 0.0069017 | 0.022421 | 0.055988 | 0.13876 | 0.051108 | 0.13912 | 0.08278 | 0.24727 | 0.10178 | 48.9978 | 48.9056 | 49.0778 | 48.8272 | 49.0231 | 48.8157 | 8.4715 | 73.5042 | -48.8782 | 73.4584 | 73.4535 | -0.050676 | -48.9346 | -48.7701 | 81.8739 | -0.19017 | 122.4002 | 122.4802 | 40.6063 | 0.005734 | -0.20168 | 73.5415 | 73.4852 | 73.6497 | 73.5412 | -48.9155 | 122.2296 | 122.4255 | 122.2181 | 122.308 | -40.5458
1205.9375 | 122.5708 | -73.5672 | 48.8937 | -0.00068679 | 0.020647 | -0.062873 | 0.018802 | -0.0010512 | 0.023398 | 0.0090803 | 0.053025 | 0.063632 | 0.050079 | 0.0071153 | 0.022421 | 0.055988 | 0.14334 | 0.04653 | 0.14369 | 0.078201 | 0.26101 | 0.11094 | 48.7735 | 48.6675 | 48.8351 | 48.5937 | 48.785 | 48.4723 | 8.4669 | 73.6781 | -48.75 | 73.6232 | 73.6137 | -0.064412 | -48.8155 | -48.6327 | 82.0341 | -0.30007 | 122.3407 | 122.4023 | 40.3682 | -0.10876 | -0.42148 | 73.7109 | 73.6454 | 73.8282 | 73.7105 | -48.7828 | 122.1609 | 122.3522 | 122.0395 | 122.2347 | -40.4268
1207.6719 | 122.5845 | -73.5352 | 48.8892 | -0.00068679 | 0.020647 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | -0.013811 | 0.052384 | 0.063204 | 0.049652 | 0.0066879 | 0.022635 | 0.05141 | 0.12961 | 0.041952 | 0.13912 | 0.08278 | 0.24727 | 0.10636 | 48.7735 | 48.6766 | 48.8534 | 48.6074 | 48.7987 | 48.5776 | 8.4807 | 73.6415 | -48.75 | 73.5866 | 73.5771 | -0.064411 | -48.8064 | -48.6419 | 82.0158 | -0.28176 | 122.3086 | 122.3886 | 40.3728 | -0.090444 | -0.31159 | 73.6743 | 73.6179 | 73.7824 | 73.6648 | -48.7828 | 122.1426 | 122.3339 | 122.1127 | 122.2118 | -40.4085
1209.3594 | 122.7219 | -73.9334 | 48.468 | -0.00068679 | 0.02022 | -0.063086 | 0.018588 | -0.00083764 | 0.023185 | -0.0061807 | 0.051957 | 0.064273 | 0.04837 | 0.0066879 | 0.022207 | 0.042253 | 0.12961 | 0.028217 | 0.12996 | 0.078201 | 0.24727 | 0.11094 | 48.5308 | 48.4294 | 48.5924 | 48.3556 | 48.5469 | 48.3624 | 8.4715 | 74.0444 | -48.3381 | 73.9757 | 73.9616 | -0.082725 | -48.3898 | -48.2207 | 82.4049 | -0.11243 | 122.4642 | 122.5259 | 40.1209 | 0.078875 | -0.10565 | 74.0634 | 74.0116 | 74.1807 | 74.063 | -48.3571 | 122.289 | 122.4803 | 122.2958 | 122.3628 | -39.9965
1211.0469 | 122.6578 | -74.501 | 47.9095 | -0.0083178 | 0.02022 | -0.0633 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.051957 | 0.063632 | 0.049011 | 0.0069017 | 0.022207 | 0.042253 | 0.12045 | 0.023639 | 0.12996 | 0.073622 | 0.23812 | 0.10636 | 47.6746 | 47.5686 | 47.7408 | 47.4994 | 47.6861 | 47.4375 | 8.4761 | 74.6074 | -47.7796 | 74.5433 | 74.5247 | -0.082724 | -47.8359 | -47.6714 | 82.9771 | -0.41014 | 122.1756 | 122.2418 | 39.2647 | -0.22343 | -0.47205 | 74.631 | 74.5747 | 74.7392 | 74.6215 | -47.8032 | 122.0004 | 122.1872 | 121.9385 | 122.0696 | -39.4335
1212.7656 | 122.7036 | -74.8352 | 47.5342 | -0.0083178 | 0.020434 | -0.062445 | 0.018161 | -0.00083764 | 0.023398 | -0.0061807 | 0.053239 | 0.062777 | 0.050506 | 0.0066879 | 0.022421 | 0.042253 | 0.12045 | 0.028217 | 0.1208 | 0.073622 | 0.24269 | 0.11094 | 47.3174 | 47.2206 | 47.3791 | 47.1377 | 47.329 | 47.0437 | 8.4578 | 74.9461 | -47.4134 | 74.8775 | 74.8634 | -0.082725 | -47.4606 | -47.2915 | 83.293 | -0.39648 | 122.1526 | 122.2143 | 38.9213 | -0.20519 | -0.49045 | 74.956 | 74.9088 | 75.0779 | 74.9557 | -47.4232 | 121.9729 | 122.1642 | 121.8789 | 122.0558 | -39.0764
1214.4375 | 122.6715 | -82.3059 | 40.0223 | 0.0069442 | 0.020434 | -0.062873 | 0.018375 | -0.0014786 | 0.023398 | 0.0090803 | 0.05217 | 0.063845 | 0.049652 | 0.0066879 | 0.022421 | 0.042253 | 0.12503 | 0.028217 | 0.12996 | 0.073622 | 0.24269 | 0.10636 | 42.084 | 41.9551 | 42.1044 | 41.8587 | 42.0727 | 41.8745 | 8.5493 | 82.4123 | -39.8923 | 82.3482 | 82.3341 | -0.078146 | -39.9487 | -39.7796 | 90.8552 | 1.8364 | 124.3899 | 124.4103 | 33.5551 | 2.0505 | 1.8522 | 82.4359 | 82.3795 | 82.5486 | 82.4309 | -39.9159 | 124.1646 | 124.3787 | 124.1804 | 124.261 | -31.4729
1216.1094 | 122.7264 | -86.2244 | 36.1267 | -0.00068679 | 0.020434 | -0.062659 | 0.018375 | -0.0010512 | 0.023398 | -0.0061807 | 0.053025 | 0.064273 | 0.049652 | 0.0066879 | 0.021994 | 0.05141 | 0.13419 | 0.032795 | 0.13454 | 0.073622 | 0.24727 | 0.10178 | 36.2186 | 36.1035 | 36.2345 | 36.0074 | 36.1847 | 35.785 | 8.5631 | 86.3261 | -35.9922 | 86.2758 | 86.2572 | -0.068989 | -36.0531 | -35.8794 | 94.7874 | -0.11933 | 122.443 | 122.4589 | 27.6714 | 0.057957 | -0.34176 | 86.3589 | 86.298 | 86.4716 | 86.3586 | -36.0249 | 122.2317 | 122.409 | 122.0093 | 122.3279 | -27.5636
1217.8125 | 122.7356 | -118.2129 | 4.2297 | 0.0069442 | 0.020647 | -0.062659 | 0.018375 | -0.0012648 | 0.023826 | 0.0090803 | 0.053452 | 0.066195 | 0.049011 | 0.0069017 | 0.022207 | 0.05141 | 0.13876 | 0.04653 | 0.12996 | 0.08278 | 0.25185 | 0.10636 | 4.0074 | 4.0113 | 3.9225 | 3.9808 | 4.1436 | 4.1239 | 3.7187 | 118.3193 | -4.0998 | 118.2643 | 118.2594 | -0.059833 | -4.147 | -3.9779 | 121.9316 | -0.24893 | 122.2203 | 122.1354 | 0.20386 | -0.08613 | -0.10582 | 118.3429 | 118.2957 | 118.4647 | 118.3517 | -4.1234 | 122.1937 | 122.3565 | 122.3368 | 122.2242 | -0.51105
1219.5469 | 122.6807 | -119.2474 | 3.2318 | 0.0069442 | 0.02022 | -0.063086 | 0.018588 | -0.0010512 | 0.023185 | 0.0014498 | 0.053666 | 0.066409 | 0.049652 | 0.0066879 | 0.022635 | 0.05141 | 0.13876 | 0.032795 | 0.13912 | 0.078201 | 0.25185 | 0.10178 | 3.1787 | 3.178 | 3.0846 | 3.1613 | 3.3103 | 3.3089 | 2.8945 | 119.3492 | -3.0927 | 119.2988 | 119.2802 | -0.068989 | -3.1536 | -2.98 | 122.1419 | -0.070555 | 122.4261 | 122.3321 | 0.19014 | 0.078488 | 0.077111 | 119.3866 | 119.3256 | 119.4993 | 119.3862 | -3.13 | 122.4087 | 122.5577 | 122.5564 | 122.4254 | -0.33731
1221.2188 | 122.6212 | -122.3099 | 0.19226 | -0.00068679 | 0.020647 | -0.062873 | 0.018588 | -0.0012648 | 0.023398 | 0.016711 | 0.029738 | 0.025173 | 0.0238 | 0.0064743 | 0.022421 | 0.060567 | 0.13876 | 0.051108 | 0.14827 | 0.078201 | 0.26101 | 0.10178 | 0.12009 | 0.12856 | 0.016908 | 0.11198 | 0.28384 | 0.255 | -0.16415 | 122.4117 | -0.043987 | 122.3704 | 122.361 | -0.050676 | -0.11406 | 0.068749 | 122.1457 | -0.080282 | 122.43 | 122.3268 | 0.18106 | 0.091583 | 0.062734 | 122.4581 | 122.3881 | 122.5709 | 122.4486 | -0.090477 | 122.4219 | 122.5937 | 122.5649 | 122.4384 | -0.35641
1222.9219 | 122.7768 | -122.3099 | 0.16022 | -0.015949 | 0.020647 | -0.062873 | 0.018375 | -0.0010512 | 0.023185 | 0.0090803 | 0.029952 | 0.024959 | 0.024441 | 0.0069017 | 0.022635 | 0.05141 | 0.13876 | 0.04653 | 0.14827 | 0.087359 | 0.25643 | 0.10178 | 0.074307 | 0.087354 | -0.038036 | 0.066194 | 0.23348 | 0.21379 | -0.18704 | 122.4117 | -0.011943 | 122.3613 | 122.3564 | -0.055254 | -0.072858 | 0.096214 | 122.1228 | -0.094023 | 122.3842 | 122.2718 | 0.14901 | 0.073262 | 0.053571 | 122.4581 | 122.3972 | 122.5663 | 122.4486 | -0.058433 | 122.3761 | 122.5434 | 122.5237 | 122.3972 | -0.34726
1224.7031 | 122.7448 | -122.3602 | 0.19684 | -0.0083178 | 0.020647 | -0.062659 | 0.018588 | -0.0012648 | 0.023185 | 0.0014498 | 0.029525 | 0.025387 | 0.024014 | 0.0069017 | 0.022421 | 0.055988 | 0.13419 | 0.051108 | 0.14369 | 0.091937 | 0.25185 | 0.10178 | 0.069728 | 0.087354 | -0.033458 | 0.061616 | 0.22432 | 0.21379 | -0.17788 | 122.462 | -0.053143 | 122.4162 | 122.4113 | -0.050676 | -0.1049 | 0.055014 | 122.1823 | -0.13522 | 122.43 | 122.3268 | 0.14443 | 0.027484 | 0.01695 | 122.5039 | 122.4522 | 122.6121 | 122.4944 | -0.095054 | 122.4218 | 122.5846 | 122.574 | 122.4476 | -0.37472
1226.4531 | 122.7814 | -122.3419 | 0.16022 | -0.00068679 | 0.020434 | -0.063086 | 0.018802 | -0.0010512 | 0.023826 | -0.0061807 | 0.029525 | 0.0256 | 0.024228 | 0.0066879 | 0.022421 | 0.05141 | 0.13876 | 0.04653 | 0.14827 | 0.091937 | 0.25643 | 0.10178 | 0.069728 | 0.087354 | -0.042615 | 0.061616 | 0.2289 | -0.010564 | -0.18246 | 122.4437 | -0.011943 | 122.3933 | 122.3884 | -0.055254 | -0.06828 | 0.096214 | 122.1595 | -0.098601 | 122.4116 | 122.2993 | 0.13985 | 0.068684 | -0.17078 | 122.4902 | 122.4339 | 122.5984 | 122.4807 | -0.058433 | 122.4035 | 122.5708 | 122.3314 | 122.4293 | -0.34268
1228.2031 | 122.7676 | -122.3557 | 0.16022 | -0.0083178 | 0.020434 | -0.062659 | 0.018588 | -0.0012648 | 0.023612 | -0.013811 | 0.029097 | 0.025173 | 0.024228 | 0.0069017 | 0.022207 | 0.065145 | 0.13876 | 0.051108 | 0.14369 | 0.08278 | 0.25185 | 0.10178 | 0.069728 | 0.06904 | -0.038036 | 0.061616 | 0.22432 | -0.083821 | -0.17788 | 122.4574 | -0.016522 | 122.4208 | 122.4068 | -0.050676 | -0.077437 | 0.091635 | 122.1778 | -0.098601 | 122.4254 | 122.3176 | 0.13985 | 0.064105 | -0.24404 | 122.4993 | 122.4384 | 122.6075 | 122.4944 | -0.058433 | 122.4173 | 122.58 | 122.2718 | 122.4247 | -0.3381
1229.9062 | 122.8088 | -122.3785 | 0.17853 | -0.00068679 | 0.020434 | -0.0633 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.029097 | 0.025387 | 0.024441 | 0.0066879 | 0.022207 | 0.05141 | 0.13419 | 0.037373 | 0.14827 | 0.078201 | 0.26101 | 0.10636 | 0.069728 | 0.073618 | -0.028879 | 0.061616 | 0.21974 | -0.092979 | -0.17331 | 122.4849 | -0.030254 | 122.43 | 122.4159 | -0.06899 | -0.10033 | 0.082482 | 122.2052 | -0.11691 | 122.4483 | 122.3497 | 0.14443 | 0.041216 | -0.27151 | 122.5268 | 122.4567 | 122.6395 | 122.5127 | -0.072165 | 122.4402 | 122.5983 | 122.2856 | 122.4522 | -0.35183
1231.6562 | 122.7036 | -122.4106 | 0.20142 | 0.0069442 | 0.020434 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | 0.016711 | 0.029738 | 0.024746 | 0.024228 | 0.0069017 | 0.022207 | 0.055988 | 0.13876 | 0.04653 | 0.14827 | 0.091937 | 0.26101 | 0.10178 | 0.074307 | 0.06904 | -0.042615 | 0.052459 | 0.22432 | -0.097557 | -0.18246 | 122.5124 | -0.053142 | 122.4666 | 122.4571 | -0.055254 | -0.10948 | 0.059594 | 122.2281 | -0.14896 | 122.4849 | 122.368 | 0.13985 | 0.022906 | -0.29897 | 122.5589 | 122.5025 | 122.6716 | 122.5493 | -0.099632 | 122.463 | 122.6349 | 122.313 | 122.4796 | -0.38388
1233.3906 | 122.6807 | -122.4335 | 0.19684 | -0.00068679 | 0.02022 | -0.0633 | 0.018802 | -0.0014786 | 0.023612 | -0.013811 | 0.029525 | 0.025173 | 0.024655 | 0.0066879 | 0.022635 | 0.046831 | 0.13419 | 0.051108 | 0.13454 | 0.087359 | 0.26101 | 0.10178 | 0.074307 | 0.064461 | -0.028879 | 0.052459 | 0.22432 | -0.060928 | -0.18246 | 122.5353 | -0.062299 | 122.4803 | 122.4846 | -0.050676 | -0.10948 | 0.064172 | 122.251 | -0.14438 | 122.5078 | 122.4046 | 0.15358 | 0.027484 | -0.25777 | 122.568 | 122.5208 | 122.6945 | 122.5677 | -0.095054 | 122.4859 | 122.6578 | 122.3725 | 122.4979 | -0.3793
1235.1406 | 122.7859 | -122.4014 | 0.14648 | -0.00068679 | 0.02022 | -0.063086 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.029952 | 0.025173 | 0.024014 | 0.0069017 | 0.022421 | 0.05141 | 0.12961 | 0.04653 | 0.14369 | 0.087359 | 0.25185 | 0.10636 | 0.069728 | 0.073618 | -0.038036 | 0.057037 | 0.22432 | -0.0884 | -0.18246 | 122.5078 | -0.002789 | 122.4528 | 122.448 | -0.059833 | -0.059125 | 0.10537 | 122.219 | -0.089447 | 122.4712 | 122.3634 | 0.14443 | 0.077838 | -0.23488 | 122.5451 | 122.4888 | 122.6533 | 122.531 | -0.040121 | 122.4585 | 122.6257 | 122.313 | 122.475 | -0.32895
1236.8281 | 122.7814 | -122.374 | 0.14191 | -0.0083178 | 0.020434 | -0.062659 | 0.018375 | -0.0012648 | 0.023612 | 0.0014498 | 0.029525 | 0.025173 | 0.024441 | 0.0071153 | 0.022421 | 0.046831 | 0.13876 | 0.032795 | 0.14827 | 0.078201 | 0.25185 | 0.10178 | 0.06515 | 0.073618 | -0.0243 | 0.057037 | 0.22432 | -0.060928 | -0.17788 | 122.4757 | 0.006367 | 122.4208 | 122.4068 | -0.068989 | -0.063706 | 0.10995 | 122.1961 | -0.08487 | 122.4391 | 122.3497 | 0.15358 | 0.082415 | -0.20284 | 122.5222 | 122.4522 | 122.6258 | 122.5127 | -0.040123 | 122.431 | 122.5983 | 122.313 | 122.4476 | -0.31979
1238.5625 | 122.7859 | -122.4243 | 0.16937 | -0.00068679 | 0.020647 | -0.0633 | 0.018588 | -0.0010512 | 0.023612 | 0.0090803 | 0.029311 | 0.025387 | 0.024441 | 0.0069017 | 0.022421 | 0.05141 | 0.12503 | 0.04653 | 0.14369 | 0.073622 | 0.25185 | 0.10636 | 0.06515 | 0.073618 | -0.038036 | 0.057037 | 0.2289 | -0.12045 | -0.18246 | 122.5307 | -0.025678 | 122.4757 | 122.4708 | -0.059833 | -0.095751 | 0.082479 | 122.2419 | -0.11234 | 122.4895 | 122.3863 | 0.14443 | 0.059528 | -0.28982 | 122.568 | 122.4979 | 122.6762 | 122.5493 | -0.06301 | 122.4814 | 122.6532 | 122.3039 | 122.4979 | -0.35184
1240.3125 | 122.7127 | -122.438 | 0.1831 | 0.0069442 | 0.02022 | -0.062873 | 0.018375 | -0.0012648 | 0.023398 | 0.0090803 | 0.029311 | 0.025387 | 0.024441 | 0.0069017 | 0.022421 | 0.042253 | 0.12961 | 0.037373 | 0.13454 | 0.08278 | 0.24727 | 0.10636 | 0.074307 | 0.064461 | -0.038036 | 0.061616 | 0.22432 | -0.070086 | -0.18704 | 122.5444 | -0.048566 | 122.4803 | 122.4754 | -0.06899 | -0.10032 | 0.064169 | 122.251 | -0.12149 | 122.5124 | 122.4 | 0.14901 | 0.041217 | -0.25319 | 122.5726 | 122.5208 | 122.6853 | 122.5677 | -0.076742 | 122.4997 | 122.6624 | 122.368 | 122.5025 | -0.37015
1242.0938 | 122.7676 | -122.4289 | 0.1831 | -0.00068679 | 0.02022 | -0.062659 | 0.018375 | -0.0012648 | 0.023398 | -0.0061807 | 0.029738 | 0.025387 | 0.024441 | 0.0066879 | 0.022421 | 0.042253 | 0.12961 | 0.037373 | 0.13454 | 0.08278 | 0.25643 | 0.10178 | 0.069728 | 0.059882 | -0.042615 | 0.04788 | 0.22432 | -0.11129 | -0.18704 | 122.5307 | -0.048566 | 122.4711 | 122.4663 | -0.064411 | -0.10032 | 0.073326 | 122.2419 | -0.13522 | 122.4986 | 122.3863 | 0.14443 | 0.041217 | -0.2944 | 122.5634 | 122.5117 | 122.6853 | 122.5585 | -0.081321 | 122.4768 | 122.6532 | 122.3176 | 122.4888 | -0.37015
1243.7969 | 122.8271 | -122.4106 | 0.17853 | 0.0069442 | 0.020434 | -0.062659 | 0.018588 | -0.0010512 | 0.023398 | 0.0014498 | 0.029738 | 0.025173 | 0.025082 | 0.0069017 | 0.022421 | 0.042253 | 0.13419 | 0.051108 | 0.13912 | 0.08278 | 0.24727 | 0.10178 | 0.069728 | 0.06904 | -0.033458 | 0.057037 | 0.21974 | -0.079243 | -0.18704 | 122.5124 | -0.039411 | 122.4528 | 122.4617 | -0.050676 | -0.095748 | 0.068746 | 122.2235 | -0.12149 | 122.4803 | 122.3771 | 0.15358 | 0.041216 | -0.25777 | 122.5497 | 122.4934 | 122.6579 | 122.5448 | -0.076744 | 122.4676 | 122.6303 | 122.3313 | 122.4796 | -0.36557
1245.4844 | 122.7585 | -122.4609 | 0.15564 | -0.00068679 | 0.020434 | -0.063086 | 0.018802 | -0.00083764 | 0.023398 | 0.0090803 | 0.029311 | 0.025814 | 0.025296 | 0.0073291 | 0.022207 | 0.042253 | 0.12503 | 0.032795 | 0.13454 | 0.08278 | 0.25185 | 0.10636 | 0.055992 | 0.064461 | -0.047194 | 0.057037 | 0.21516 | -0.10214 | -0.18704 | 122.5673 | -0.021101 | 122.5032 | 122.4937 | -0.073568 | -0.07286 | 0.096212 | 122.2739 | -0.098603 | 122.5169 | 122.4137 | 0.13985 | 0.059525 | -0.25778 | 122.5955 | 122.5437 | 122.7128 | 122.586 | -0.049277 | 122.518 | 122.6761 | 122.3588 | 122.5254 | -0.34268
1247.1719 | 122.7722 | -122.4564 | 0.17395 | -0.015949 | 0.02022 | -0.062659 | 0.018588 | -0.00083764 | 0.023612 | -0.013811 | 0.029525 | 0.025387 | 0.025082 | 0.0071153 | 0.022207 | 0.042253 | 0.12503 | 0.037373 | 0.12996 | 0.08278 | 0.24727 | 0.10636 | 0.055992 | 0.064461 | -0.038036 | 0.052459 | 0.21516 | -0.079243 | -0.18704 | 122.5627 | -0.04399 | 122.4986 | 122.4937 | -0.06899 | -0.09117 | 0.073324 | 122.2693 | -0.12149 | 122.5124 | 122.4183 | 0.14901 | 0.041215 | -0.25319 | 122.5863 | 122.5391 | 122.7036 | 122.5814 | -0.067587 | 122.5088 | 122.6715 | 122.3771 | 122.5208 | -0.36099
1248.875 | 122.7036 | -122.4701 | 0.19684 | 0.0069442 | 0.020434 | -0.063514 | 0.018802 | -0.0010512 | 0.023398 | 0.0014498 | 0.029738 | 0.024959 | 0.025296 | 0.0066879 | 0.022421 | 0.042253 | 0.12045 | 0.032795 | 0.12996 | 0.064464 | 0.24727 | 0.11094 | 0.060571 | 0.055303 | -0.033458 | 0.052459 | 0.21516 | -0.060928 | -0.18246 | 122.581 | -0.066878 | 122.5123 | 122.5029 | -0.078147 | -0.13237 | 0.050436 | 122.2876 | -0.14438 | 122.5307 | 122.4366 | 0.14901 | 0.018327 | -0.25777 | 122.6001 | 122.5346 | 122.7174 | 122.5905 | -0.085896 | 122.5226 | 122.6853 | 122.4092 | 122.5254 | -0.3793
1250.625 | 122.7402 | -122.4747 | 0.1831 | 0.0069442 | 0.020006 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.029525 | 0.0256 | 0.025082 | 0.0069017 | 0.022848 | 0.042253 | 0.12045 | 0.037373 | 0.12996 | 0.078201 | 0.24269 | 0.10636 | 0.055992 | 0.064461 | -0.038036 | 0.061616 | 0.21059 | -0.074664 | -0.18246 | 122.581 | -0.053145 | 122.5169 | 122.512 | -0.06899 | -0.1049 | 0.05959 | 122.2922 | -0.12149 | 122.5307 | 122.4366 | 0.14443 | 0.027481 | -0.25777 | 122.6046 | 122.5529 | 122.7174 | 122.5951 | -0.076742 | 122.5363 | 122.6853 | 122.4 | 122.5391 | -0.36557
1252.3281 | 122.7173 | -122.4838 | 0.18768 | 0.0069442 | 0.020861 | -0.062873 | 0.018161 | -0.0012648 | 0.023612 | 0.0014498 | 0.029525 | 0.0256 | 0.024869 | 0.0066879 | 0.022421 | 0.033096 | 0.12503 | 0.041952 | 0.12538 | 0.078201 | 0.24269 | 0.10636 | 0.051413 | 0.064461 | -0.028879 | 0.052459 | 0.21059 | -0.13419 | -0.18246 | 122.5902 | -0.062301 | 122.5169 | 122.5258 | -0.064411 | -0.10948 | 0.055012 | 122.3014 | -0.13522 | 122.5352 | 122.4549 | 0.15358 | 0.022903 | -0.32187 | 122.6092 | 122.562 | 122.7265 | 122.6089 | -0.08132 | 122.5363 | 122.6944 | 122.3496 | 122.5483 | -0.37015
1254.0156 | 122.731 | -122.4838 | 0.19226 | -0.00068679 | 0.020434 | -0.062873 | 0.018588 | -0.0012648 | 0.023398 | 0.0090803 | 0.029952 | 0.025387 | 0.025723 | 0.0071153 | 0.022635 | 0.046831 | 0.12503 | 0.032795 | 0.12996 | 0.078201 | 0.24727 | 0.11094 | 0.051413 | 0.06904 | -0.038036 | 0.057037 | 0.21059 | -0.10214 | -0.17788 | 122.5948 | -0.062301 | 122.5307 | 122.5166 | -0.078147 | -0.11406 | 0.055013 | 122.3059 | -0.13522 | 122.5352 | 122.4458 | 0.13985 | 0.018325 | -0.2944 | 122.6138 | 122.562 | 122.7311 | 122.6089 | -0.081319 | 122.5409 | 122.6944 | 122.3817 | 122.5529 | -0.37015
1255.7344 | 122.8226 | -122.4335 | 0.1831 | -0.00068679 | 0.020434 | -0.062659 | 0.018802 | -0.0010512 | 0.023612 | 0.0014498 | 0.029525 | 0.0256 | 0.024869 | 0.0069017 | 0.022207 | 0.042253 | 0.12961 | 0.032795 | 0.12996 | 0.073622 | 0.24727 | 0.10636 | 0.051413 | 0.064461 | -0.042615 | 0.052459 | 0.21059 | -0.092979 | -0.18246 | 122.5398 | -0.053145 | 122.4757 | 122.4663 | -0.073568 | -0.10948 | 0.064169 | 122.251 | -0.13065 | 122.4849 | 122.3909 | 0.13985 | 0.027481 | -0.27608 | 122.5634 | 122.5071 | 122.6807 | 122.5631 | -0.076742 | 122.4859 | 122.6441 | 122.3405 | 122.4979 | -0.36557
1257.4375 | 122.8134 | -122.4152 | 0.13733 | -0.00068679 | 0.02022 | -0.062445 | 0.018375 | -0.00083764 | 0.023398 | 0.0014498 | 0.029952 | 0.0256 | 0.025082 | 0.0069017 | 0.022421 | 0.037675 | 0.12961 | 0.037373 | 0.13912 | 0.073622 | 0.24727 | 0.10178 | 0.042256 | 0.06904 | -0.038036 | 0.052459 | 0.21516 | -0.1525 | -0.17788 | 122.5169 | 0.001788 | 122.4528 | 122.4525 | -0.064411 | -0.063707 | 0.10994 | 122.2373 | -0.08487 | 122.4574 | 122.3771 | 0.13985 | 0.077836 | -0.28983 | 122.5543 | 122.4888 | 122.6624 | 122.5448 | -0.035545 | 122.4676 | 122.6303 | 122.2627 | 122.4842 | -0.31521
1259.125 | 122.731 | -122.4564 | 0.17395 | 0.0069442 | 0.020434 | -0.062873 | 0.018375 | -0.0012648 | 0.023398 | -0.0061807 | 0.029525 | 0.0256 | 0.025082 | 0.0069017 | 0.022635 | 0.042253 | 0.13419 | 0.032795 | 0.13454 | 0.078201 | 0.25643 | 0.10178 | 0.051413 | 0.064461 | -0.038036 | 0.057037 | 0.21974 | -0.14792 | -0.17788 | 122.5581 | -0.039411 | 122.4986 | 122.4892 | -0.068989 | -0.095749 | 0.082481 | 122.2785 | -0.11691 | 122.5078 | 122.4183 | 0.13985 | 0.045794 | -0.32187 | 122.5909 | 122.5346 | 122.7128 | 122.5905 | -0.072166 | 122.5134 | 122.6761 | 122.3084 | 122.5208 | -0.35184
1260.7969 | 122.7127 | -122.4701 | 0.20142 | -0.00068679 | 0.020434 | -0.062445 | 0.019016 | -0.0014786 | 0.023612 | 0.0014498 | 0.029738 | 0.025173 | 0.025296 | 0.0066879 | 0.022635 | 0.042253 | 0.13419 | 0.041952 | 0.14369 | 0.064464 | 0.25185 | 0.11552 | 0.051413 | 0.06904 | -0.038036 | 0.052459 | 0.21516 | -0.14334 | -0.17788 | 122.5856 | -0.057721 | 122.5123 | 122.512 | -0.073569 | -0.13695 | 0.050436 | 122.2922 | -0.14896 | 122.5215 | 122.4321 | 0.13985 | 0.013749 | -0.34476 | 122.6138 | 122.5346 | 122.7219 | 122.6043 | -0.085895 | 122.5226 | 122.6853 | 122.3268 | 122.5391 | -0.3793
1262.5 | 122.6944 | -122.5021 | 0.19226 | -0.0083178 | 0.020434 | -0.063086 | 0.018802 | -0.00062384 | 0.023185 | 0.0090803 | 0.029525 | 0.024959 | 0.025296 | 0.0071153 | 0.022421 | 0.046831 | 0.12961 | 0.032795 | 0.13912 | 0.087359 | 0.25185 | 0.10178 | 0.055992 | 0.064461 | -0.038036 | 0.052459 | 0.21059 | -0.12503 | -0.18246 | 122.6039 | -0.053144 | 122.549 | 122.5349 | -0.068989 | -0.1049 | 0.059591 | 122.3197 | -0.1398 | 122.5581 | 122.4641 | 0.14443 | 0.018325 | -0.31729 | 122.6413 | 122.5895 | 122.754 | 122.6317 | -0.090477 | 122.5546 | 122.7127 | 122.3771 | 122.5666 | -0.37472
1264.1719 | 122.7585 | -122.4701 | 0.17853 | -0.00068679 | 0.020647 | -0.063086 | 0.018375 | -0.0010512 | 0.023612 | -0.0061807 | 0.029525 | 0.024959 | 0.025296 | 0.0069017 | 0.022207 | 0.05141 | 0.12961 | 0.032795 | 0.13912 | 0.087359 | 0.25643 | 0.10636 | 0.051413 | 0.06904 | -0.038036 | 0.052459 | 0.21059 | -0.11587 | -0.18246 | 122.5765 | -0.039411 | 122.5215 | 122.5029 | -0.073568 | -0.091169 | 0.077903 | 122.2876 | -0.12607 | 122.5215 | 122.4321 | 0.14443 | 0.032058 | -0.2944 | 122.6092 | 122.5575 | 122.7265 | 122.5997 | -0.072165 | 122.5226 | 122.6807 | 122.3542 | 122.5391 | -0.36099
1265.8438 | 122.8088 | -122.4518 | 0.16479 | -0.015949 | 0.02022 | -0.062659 | 0.018588 | -0.0010512 | 0.023612 | 0.0014498 | 0.029952 | 0.024532 | 0.024869 | 0.0066879 | 0.022421 | 0.042253 | 0.12503 | 0.037373 | 0.13912 | 0.078201 | 0.25185 | 0.11094 | 0.055992 | 0.064461 | -0.033458 | 0.057037 | 0.21516 | -0.13876 | -0.18246 | 122.5627 | -0.025678 | 122.494 | 122.4892 | -0.073569 | -0.086594 | 0.087057 | 122.2693 | -0.10776 | 122.5078 | 122.4183 | 0.14901 | 0.05037 | -0.30356 | 122.5909 | 122.53 | 122.7036 | 122.5768 | -0.053853 | 122.5088 | 122.6669 | 122.313 | 122.5162 | -0.34726
1267.5312 | 122.7036 | -122.4838 | 0.20142 | -0.00068679 | 0.020434 | -0.062659 | 0.018375 | -0.0012648 | 0.023612 | 0.0090803 | 0.029525 | 0.024746 | 0.025082 | 0.0069017 | 0.022421 | 0.046831 | 0.13419 | 0.041952 | 0.13912 | 0.08278 | 0.25643 | 0.10636 | 0.046835 | 0.06904 | -0.042615 | 0.04788 | 0.21059 | -0.13876 | -0.18246 | 122.5902 | -0.062299 | 122.5307 | 122.5258 | -0.064411 | -0.11864 | 0.055015 | 122.3014 | -0.15354 | 122.5307 | 122.4412 | 0.13985 | 0.00917 | -0.34018 | 122.6229 | 122.5666 | 122.7403 | 122.618 | -0.095053 | 122.5317 | 122.6944 | 122.3451 | 122.5529 | -0.38388
1269.2344 | 122.7173 | -122.5067 | 0.19226 | -0.0083178 | 0.020434 | -0.0633 | 0.018375 | -0.0014786 | 0.023185 | 0.0014498 | 0.029525 | 0.024532 | 0.025296 | 0.0069017 | 0.022421 | 0.042253 | 0.12503 | 0.032795 | 0.13912 | 0.08278 | 0.25643 | 0.10636 | 0.051413 | 0.06904 | -0.033458 | 0.04788 | 0.21059 | -0.14334 | -0.18704 | 122.6131 | -0.053144 | 122.549 | 122.5395 | -0.073568 | -0.10948 | 0.06417 | 122.3197 | -0.14438 | 122.5581 | 122.4733 | 0.15358 | 0.018325 | -0.3356 | 122.6458 | 122.5895 | 122.7631 | 122.6317 | -0.085898 | 122.5546 | 122.7173 | 122.3634 | 122.5758 | -0.3793
1270.9062 | 122.8226 | -122.4472 | 0.16937 | -0.00068679 | 0.020434 | -0.062873 | 0.018375 | -0.0012648 | 0.023185 | -0.0061807 | 0.029525 | 0.024532 | 0.025296 | 0.0069017 | 0.022207 | 0.037675 | 0.12961 | 0.028217 | 0.12996 | 0.08278 | 0.25185 | 0.10636 | 0.055992 | 0.064461 | -0.028879 | 0.052459 | 0.21059 | -0.11587 | -0.18246 | 122.5536 | -0.039413 | 122.4849 | 122.4754 | -0.078146 | -0.086593 | 0.082479 | 122.2647 | -0.11691 | 122.5032 | 122.4183 | 0.15358 | 0.041213 | -0.28524 | 122.5772 | 122.53 | 122.6991 | 122.5768 | -0.06301 | 122.4997 | 122.6578 | 122.3313 | 122.5117 | -0.35184
1272.625 | 122.8088 | -122.4518 | 0.16479 | -0.0083178 | 0.020434 | -0.062873 | 0.018802 | -0.0010512 | 0.023398 | 0.0090803 | 0.029525 | 0.024959 | 0.025296 | 0.0069017 | 0.022421 | 0.037675 | 0.12961 | 0.037373 | 0.13454 | 0.073622 | 0.24727 | 0.11094 | 0.051413 | 0.06904 | -0.033458 | 0.052459 | 0.21059 | -0.15708 | -0.19162 | 122.5627 | -0.030256 | 122.4895 | 122.4892 | -0.073569 | -0.091173 | 0.082479 | 122.2602 | -0.11234 | 122.5032 | 122.4183 | 0.15816 | 0.045791 | -0.32187 | 122.5863 | 122.5254 | 122.6991 | 122.5814 | -0.053853 | 122.5042 | 122.6624 | 122.2947 | 122.5208 | -0.35642
1274.2969 | 122.8867 | -122.4655 | 0.16479 | 0.0069442 | 0.020861 | -0.062873 | 0.018588 | -0.00083764 | 0.023612 | 0.0090803 | 0.029738 | 0.024746 | 0.025296 | 0.0071153 | 0.022421 | 0.028518 | 0.12503 | 0.023639 | 0.13912 | 0.073622 | 0.24269 | 0.11094 | 0.051413 | 0.06904 | -0.038036 | 0.04788 | 0.21516 | -0.097557 | -0.18246 | 122.5765 | -0.025678 | 122.494 | 122.4892 | -0.087303 | -0.091173 | 0.0779 | 122.2831 | -0.11691 | 122.5169 | 122.4275 | 0.14443 | 0.05037 | -0.26235 | 122.6046 | 122.5391 | 122.7082 | 122.5905 | -0.053853 | 122.5134 | 122.6807 | 122.368 | 122.5346 | -0.34726
1275.9688 | 122.818 | -122.4701 | 0.1831 | 0.0069442 | 0.02022 | -0.062873 | 0.018588 | -0.0014786 | 0.023826 | 0.0014498 | 0.029738 | 0.024532 | 0.024869 | 0.0069017 | 0.022421 | 0.028518 | 0.12503 | 0.032795 | 0.12996 | 0.073622 | 0.24727 | 0.11094 | 0.051413 | 0.064461 | -0.042615 | 0.043302 | 0.21059 | -0.13876 | -0.17788 | 122.581 | -0.053145 | 122.4986 | 122.5029 | -0.078147 | -0.10948 | 0.064169 | 122.2922 | -0.1398 | 122.5215 | 122.4275 | 0.13527 | 0.027481 | -0.32187 | 122.6001 | 122.5437 | 122.7174 | 122.5951 | -0.072163 | 122.5134 | 122.6807 | 122.3313 | 122.5346 | -0.36099
1277.6719 | 122.8088 | -122.4472 | 0.17395 | -0.0083178 | 0.02022 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0090803 | 0.029738 | 0.024532 | 0.024869 | 0.0069017 | 0.022635 | 0.046831 | 0.13419 | 0.037373 | 0.14369 | 0.08278 | 0.25643 | 0.11094 | 0.051413 | 0.064461 | -0.033458 | 0.052459 | 0.20601 | -0.097557 | -0.18704 | 122.5581 | -0.030255 | 122.494 | 122.4846 | -0.073569 | -0.09117 | 0.082481 | 122.2602 | -0.12149 | 122.4986 | 122.4137 | 0.15358 | 0.032058 | -0.27151 | 122.5909 | 122.53 | 122.7036 | 122.5814 | -0.063008 | 122.4997 | 122.6532 | 122.3496 | 122.5117 | -0.36099
1279.3594 | 122.8226 | -122.4609 | 0.16022 | -0.00068679 | 0.020647 | -0.062659 | 0.018588 | -0.0012648 | 0.023612 | -0.013811 | 0.029525 | 0.024532 | 0.025296 | 0.0069017 | 0.022421 | 0.046831 | 0.12961 | 0.041952 | 0.14369 | 0.087359 | 0.26559 | 0.11094 | 0.051413 | 0.055303 | -0.033458 | 0.04788 | 0.21059 | -0.12503 | -0.18704 | 122.5719 | -0.016522 | 122.5078 | 122.5029 | -0.06899 | -0.072858 | 0.10537 | 122.2739 | -0.11234 | 122.5123 | 122.4275 | 0.15358 | 0.050369 | -0.28525 | 122.6046 | 122.5483 | 122.7265 | 122.5905 | -0.049275 | 122.5088 | 122.6715 | 122.3359 | 122.5162 | -0.34726
1281.0469 | 122.8775 | -122.4747 | 0.16479 | -0.0083178 | 0.020647 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.029525 | 0.024746 | 0.025296 | 0.0073291 | 0.022421 | 0.055988 | 0.13419 | 0.037373 | 0.14827 | 0.087359 | 0.25643 | 0.11094 | 0.046835 | 0.064461 | -0.038036 | 0.043302 | 0.20143 | -0.14792 | -0.19162 | 122.5856 | -0.016521 | 122.5307 | 122.512 | -0.073569 | -0.077436 | 0.091636 | 122.283 | -0.12149 | 122.5215 | 122.4366 | 0.15359 | 0.036634 | -0.31272 | 122.6229 | 122.562 | 122.7311 | 122.6089 | -0.053853 | 122.518 | 122.6761 | 122.3267 | 122.5391 | -0.35642
1282.7188 | 122.7448 | -122.5067 | 0.19226 | -0.00068679 | 0.02022 | -0.062659 | 0.018802 | -0.00083764 | 0.023398 | 0.0090803 | 0.029738 | 0.024746 | 0.025082 | 0.0071153 | 0.022207 | 0.055988 | 0.13876 | 0.037373 | 0.14369 | 0.091937 | 0.26559 | 0.10636 | 0.046835 | 0.06904 | -0.033458 | 0.057037 | 0.21516 | -0.13876 | -0.18704 | 122.6131 | -0.048566 | 122.5627 | 122.5441 | -0.06899 | -0.10032 | 0.073327 | 122.3197 | -0.13522 | 122.5535 | 122.4733 | 0.15358 | 0.022904 | -0.33103 | 122.6504 | 122.5987 | 122.7723 | 122.6455 | -0.085898 | 122.5638 | 122.7219 | 122.3679 | 122.5758 | -0.3793
1284.3906 | 122.7814 | -122.5388 | 0.19684 | -0.00068679 | 0.020434 | -0.063086 | 0.018161 | -0.00083764 | 0.023826 | -0.0061807 | 0.029525 | 0.025173 | 0.02551 | 0.0071153 | 0.022635 | 0.046831 | 0.12961 | 0.037373 | 0.14827 | 0.087359 | 0.25643 | 0.10636 | 0.055992 | 0.059882 | -0.033458 | 0.057037 | 0.20601 | -0.14792 | -0.18246 | 122.6451 | -0.048564 | 122.5856 | 122.5761 | -0.06899 | -0.10948 | 0.059593 | 122.3563 | -0.1398 | 122.5947 | 122.5053 | 0.14901 | 0.00917 | -0.34476 | 122.687 | 122.6261 | 122.7952 | 122.6684 | -0.090475 | 122.5958 | 122.7448 | 122.3908 | 122.5986 | -0.3793
1286.0625 | 122.7356 | -122.4884 | 0.17395 | -0.0083178 | 0.020647 | -0.062445 | 0.018375 | -0.00062384 | 0.023612 | 0.0090803 | 0.029525 | 0.024746 | 0.025082 | 0.0066879 | 0.022421 | 0.055988 | 0.12961 | 0.037373 | 0.15285 | 0.087359 | 0.26101 | 0.10178 | 0.055992 | 0.073618 | -0.038036 | 0.04788 | 0.20601 | -0.12503 | -0.17788 | 122.5902 | -0.021098 | 122.5444 | 122.5258 | -0.064411 | -0.086591 | 0.08706 | 122.3105 | -0.12607 | 122.5444 | 122.4504 | 0.13985 | 0.032058 | -0.29898 | 122.6413 | 122.5758 | 122.7494 | 122.618 | -0.072166 | 122.5363 | 122.6944 | 122.3634 | 122.562 | -0.35184
1287.7344 | 122.8638 | -122.4747 | 0.16022 | -0.02358 | 0.020647 | -0.062873 | 0.018588 | -0.0012648 | 0.023398 | -0.013811 | 0.029738 | 0.024746 | 0.025296 | 0.0064743 | 0.022635 | 0.046831 | 0.12503 | 0.041952 | 0.14369 | 0.08278 | 0.26101 | 0.10178 | 0.042256 | 0.064461 | -0.033458 | 0.052459 | 0.21516 | -0.11129 | -0.18246 | 122.5765 | -0.016522 | 122.5215 | 122.5166 | -0.059832 | -0.077437 | 0.10079 | 122.2922 | -0.10776 | 122.5169 | 122.4412 | 0.14901 | 0.054948 | -0.27151 | 122.6184 | 122.5575 | 122.7357 | 122.5997 | -0.058433 | 122.5271 | 122.6898 | 122.3634 | 122.5391 | -0.34268
1289.4062 | 122.8546 | -122.4976 | 0.16937 | -0.00068679 | 0.020647 | -0.062873 | 0.018588 | -0.00083764 | 0.023398 | -0.0061807 | 0.029952 | 0.024746 | 0.025082 | 0.0069017 | 0.022207 | 0.060567 | 0.12045 | 0.041952 | 0.14369 | 0.091937 | 0.26101 | 0.10178 | 0.055992 | 0.06904 | -0.033458 | 0.052459 | 0.20601 | -0.1525 | -0.18704 | 122.5993 | -0.025678 | 122.5581 | 122.5395 | -0.059832 | -0.077436 | 0.091637 | 122.3105 | -0.11691 | 122.5536 | 122.4641 | 0.15358 | 0.036635 | -0.32187 | 122.6413 | 122.5895 | 122.7586 | 122.618 | -0.067589 | 122.55 | 122.7036 | 122.3451 | 122.5666 | -0.35642
1291.0781 | 122.8775 | -122.4838 | 0.15106 | -0.0083178 | 0.020434 | -0.062873 | 0.018375 | -0.0012648 | 0.023185 | 0.0014498 | 0.029738 | 0.025387 | 0.025082 | 0.0069017 | 0.022207 | 0.05141 | 0.13876 | 0.041952 | 0.15285 | 0.096516 | 0.26559 | 0.10178 | 0.046835 | 0.064461 | -0.038036 | 0.04788 | 0.21516 | -0.14334 | -0.18246 | 122.5856 | 0.00179 | 122.5352 | 122.5258 | -0.059832 | -0.054546 | 0.11453 | 122.3014 | -0.10318 | 122.5307 | 122.4458 | 0.14443 | 0.064103 | -0.29441 | 122.6367 | 122.5803 | 122.7494 | 122.6226 | -0.049278 | 122.5317 | 122.699 | 122.3405 | 122.5483 | -0.33353
1292.7812 | 122.85 | -122.4655 | 0.15106 | -0.0083178 | 0.020861 | -0.0633 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.029311 | 0.024532 | 0.024869 | 0.0069017 | 0.022421 | 0.060567 | 0.13876 | 0.041952 | 0.14827 | 0.096516 | 0.26559 | 0.10178 | 0.055992 | 0.064461 | -0.033458 | 0.043302 | 0.20601 | -0.14334 | -0.18704 | 122.5673 | -0.002788 | 122.5261 | 122.5075 | -0.059832 | -0.054546 | 0.11453 | 122.2785 | -0.10776 | 122.5215 | 122.4321 | 0.15358 | 0.054946 | -0.29441 | 122.6138 | 122.562 | 122.7311 | 122.6043 | -0.049278 | 122.5088 | 122.6715 | 122.3222 | 122.53 | -0.3381
1294.5 | 122.7951 | -122.4976 | 0.17853 | -0.00068679 | 0.020647 | -0.062659 | 0.018375 | -0.0012648 | 0.023398 | 0.0090803 | 0.029525 | 0.024746 | 0.025296 | 0.0069017 | 0.022421 | 0.05141 | 0.13419 | 0.04653 | 0.15285 | 0.087359 | 0.26101 | 0.10178 | 0.046835 | 0.06904 | -0.038036 | 0.04788 | 0.20601 | -0.14334 | -0.18246 | 122.5993 | -0.025676 | 122.549 | 122.5441 | -0.055254 | -0.091169 | 0.082482 | 122.3151 | -0.13065 | 122.5444 | 122.4595 | 0.14443 | 0.02748 | -0.32187 | 122.6504 | 122.5849 | 122.7586 | 122.6317 | -0.076744 | 122.5454 | 122.7036 | 122.3542 | 122.5666 | -0.36099
1296.1875 | 122.7722 | -122.5296 | 0.17395 | -0.0083178 | 0.020647 | -0.062659 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.029525 | 0.024746 | 0.025082 | 0.0069017 | 0.022421 | 0.046831 | 0.12961 | 0.041952 | 0.15285 | 0.091937 | 0.26559 | 0.10636 | 0.055992 | 0.073618 | -0.028879 | 0.052459 | 0.21516 | -0.11129 | -0.18246 | 122.636 | -0.021098 | 122.5764 | 122.5716 | -0.064411 | -0.082013 | 0.091638 | 122.3471 | -0.12149 | 122.5856 | 122.5007 | 0.15358 | 0.041215 | -0.28524 | 122.6825 | 122.6215 | 122.7952 | 122.6592 | -0.067587 | 122.5821 | 122.7448 | 122.4183 | 122.6032 | -0.35641
1297.9062 | 122.7585 | -122.5433 | 0.21057 | -0.00068679 | 0.020006 | -0.062873 | 0.018588 | -0.0010512 | 0.023398 | 0.0090803 | 0.029525 | 0.024959 | 0.025723 | 0.0073291 | 0.022421 | 0.046831 | 0.13419 | 0.041952 | 0.14827 | 0.091937 | 0.26101 | 0.11094 | 0.051413 | 0.059882 | -0.042615 | 0.043302 | 0.20601 | -0.10214 | -0.18704 | 122.6543 | -0.062297 | 122.5902 | 122.5853 | -0.06899 | -0.11863 | 0.050439 | 122.3563 | -0.16727 | 122.5947 | 122.5007 | 0.14443 | -0.004563 | -0.31271 | 122.6916 | 122.6353 | 122.8043 | 122.6775 | -0.099629 | 122.5866 | 122.7493 | 122.4412 | 122.6032 | -0.39761
1299.625 | 122.7768 | -122.5204 | 0.17853 | 0.014575 | 0.020861 | -0.062659 | 0.018375 | -0.0012648 | 0.023185 | -0.0061807 | 0.029525 | 0.024746 | 0.02551 | 0.0069017 | 0.022635 | 0.042253 | 0.12961 | 0.032795 | 0.13912 | 0.087359 | 0.25185 | 0.11094 | 0.046835 | 0.064461 | -0.038036 | 0.057037 | 0.21059 | -0.083821 | -0.18704 | 122.6314 | -0.039411 | 122.5627 | 122.5532 | -0.078147 | -0.091169 | 0.073324 | 122.3334 | -0.12149 | 122.5673 | 122.4824 | 0.14901 | 0.032058 | -0.26235 | 122.6596 | 122.6078 | 122.7723 | 122.6501 | -0.067586 | 122.5775 | 122.731 | 122.4366 | 122.5849 | -0.36557
1301.3438 | 122.8775 | -122.4747 | 0.16022 | 0.0069442 | 0.019793 | -0.062873 | 0.018588 | -0.00083764 | 0.023612 | -0.0061807 | 0.029525 | 0.024532 | 0.025296 | 0.0071153 | 0.022421 | 0.028518 | 0.12045 | 0.028217 | 0.1208 | 0.069043 | 0.23812 | 0.11552 | 0.060571 | 0.06904 | -0.042615 | 0.043302 | 0.20601 | -0.1525 | -0.18246 | 122.5902 | -0.039413 | 122.5032 | 122.5029 | -0.087304 | -0.091174 | 0.0779 | 122.2922 | -0.11691 | 122.5352 | 122.4321 | 0.13985 | 0.045791 | -0.31272 | 122.5955 | 122.5437 | 122.7128 | 122.5951 | -0.044696 | 122.518 | 122.6807 | 122.3222 | 122.5437 | -0.34268
1303.0625 | 122.7631 | -122.5296 | 0.18768 | -0.00068679 | 0.02022 | -0.062873 | 0.018588 | -0.00062384 | 0.023826 | -0.0061807 | 0.029738 | 0.024746 | 0.024869 | 0.0071153 | 0.022421 | 0.028518 | 0.11587 | 0.023639 | 0.12996 | 0.073622 | 0.23812 | 0.11094 | 0.046835 | 0.064461 | -0.033458 | 0.043302 | 0.20143 | -0.1525 | -0.18246 | 122.6405 | -0.057723 | 122.5581 | 122.5532 | -0.087303 | -0.11406 | 0.050434 | 122.3471 | -0.14438 | 122.5764 | 122.4961 | 0.14901 | 0.013746 | -0.34018 | 122.6596 | 122.6032 | 122.7677 | 122.6455 | -0.076741 | 122.5729 | 122.731 | 122.3771 | 122.5941 | -0.37015
1304.7344 | 122.7539 | -122.5616 | 0.17853 | -0.00068679 | 0.020647 | -0.063086 | 0.018588 | -0.0010512 | 0.023398 | -0.0061807 | 0.029097 | 0.024746 | 0.025082 | 0.0071153 | 0.022421 | 0.028518 | 0.12045 | 0.028217 | 0.12996 | 0.073622 | 0.23812 | 0.1201 | 0.051413 | 0.064461 | -0.038036 | 0.057037 | 0.21059 | -0.12961 | -0.17788 | 122.6817 | -0.048568 | 122.5902 | 122.5899 | -0.091883 | -0.10491 | 0.059589 | 122.3838 | -0.12149 | 122.6131 | 122.5236 | 0.13985 | 0.032058 | -0.30813 | 122.6916 | 122.6353 | 122.7998 | 122.6821 | -0.058428 | 122.6187 | 122.7722 | 122.432 | 122.6261 | -0.35641
1306.4219 | 122.7539 | -122.5204 | 0.1831 | -0.00068679 | 0.020434 | -0.063086 | 0.018588 | -0.0010512 | 0.023185 | 0.0090803 | 0.029738 | 0.024746 | 0.025296 | 0.0071153 | 0.022207 | 0.033096 | 0.11587 | 0.01906 | 0.12538 | 0.073622 | 0.23354 | 0.11094 | 0.055992 | 0.059882 | -0.038036 | 0.052459 | 0.20601 | -0.14334 | -0.18704 | 122.6314 | -0.057723 | 122.5535 | 122.5395 | -0.091882 | -0.10948 | 0.050433 | 122.3334 | -0.13065 | 122.5764 | 122.4824 | 0.14901 | 0.022903 | -0.32645 | 122.6458 | 122.5941 | 122.754 | 122.6363 | -0.072163 | 122.5729 | 122.7265 | 122.3771 | 122.5803 | -0.37015
1308.1094 | 122.7676 | -122.5159 | 0.18768 | 0.0069442 | 0.020647 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | -0.0061807 | 0.029311 | 0.024746 | 0.024869 | 0.0069017 | 0.022635 | 0.023939 | 0.12045 | 0.028217 | 0.13454 | 0.073622 | 0.24727 | 0.11552 | 0.051413 | 0.064461 | -0.028879 | 0.043302 | 0.20601 | -0.1525 | -0.17788 | 122.6314 | -0.053144 | 122.5398 | 122.5441 | -0.087304 | -0.11406 | 0.059591 | 122.338 | -0.14438 | 122.5673 | 122.487 | 0.14901 | 0.018325 | -0.34018 | 122.6504 | 122.5895 | 122.7631 | 122.6363 | -0.072162 | 122.5592 | 122.7219 | 122.3634 | 122.5803 | -0.36557
1309.7812 | 122.7997 | -122.5388 | 0.16937 | -0.00068679 | 0.020434 | -0.062873 | 0.018802 | -0.0014786 | 0.023398 | -0.0061807 | 0.029738 | 0.024746 | 0.024869 | 0.0069017 | 0.022421 | 0.019361 | 0.11587 | 0.023639 | 0.13454 | 0.08278 | 0.23812 | 0.11094 | 0.046835 | 0.06904 | -0.042615 | 0.04788 | 0.20601 | -0.13419 | -0.18246 | 122.6497 | -0.034834 | 122.5581 | 122.5624 | -0.087303 | -0.086593 | 0.068744 | 122.3563 | -0.12149 | 122.5856 | 122.4961 | 0.13985 | 0.036635 | -0.30356 | 122.6733 | 122.6215 | 122.7769 | 122.6546 | -0.058431 | 122.5866 | 122.7448 | 122.4046 | 122.6078 | -0.35184
1311.4688 | 122.7539 | -122.5616 | 0.19684 | -0.00068679 | 0.020647 | -0.062873 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.029738 | 0.024532 | 0.025296 | 0.0071153 | 0.022421 | 0.023939 | 0.11587 | 0.028217 | 0.13912 | 0.073622 | 0.24727 | 0.10636 | 0.051413 | 0.064461 | -0.042615 | 0.04788 | 0.20601 | -0.1525 | -0.18246 | 122.668 | -0.057721 | 122.5856 | 122.5899 | -0.078146 | -0.12322 | 0.050436 | 122.3792 | -0.14896 | 122.6131 | 122.519 | 0.13985 | 0.00917 | -0.34934 | 122.7008 | 122.6353 | 122.8089 | 122.6775 | -0.090475 | 122.6095 | 122.7677 | 122.4091 | 122.6261 | -0.3793
1313.1719 | 122.8638 | -122.4655 | 0.16479 | -0.0083178 | 0.02022 | -0.063086 | 0.018375 | -0.0010512 | 0.023185 | -0.013811 | 0.029311 | 0.024746 | 0.025082 | 0.0069017 | 0.022421 | 0.023939 | 0.11587 | 0.023639 | 0.13454 | 0.078201 | 0.24727 | 0.11552 | 0.055992 | 0.059882 | -0.038036 | 0.04788 | 0.20601 | -0.14792 | -0.19162 | 122.581 | -0.030256 | 122.4895 | 122.4892 | -0.091882 | -0.086594 | 0.082479 | 122.2739 | -0.11691 | 122.5215 | 122.4275 | 0.15359 | 0.041213 | -0.31272 | 122.6001 | 122.5437 | 122.7128 | 122.5814 | -0.049274 | 122.5134 | 122.6715 | 122.3176 | 122.5254 | -0.35642
1314.8438 | 122.905 | -122.4838 | 0.16937 | -0.00068679 | 0.020861 | -0.062873 | 0.018588 | -0.00083764 | 0.023398 | 0.0090803 | 0.029738 | 0.024746 | 0.025082 | 0.0066879 | 0.022421 | 0.023939 | 0.11587 | 0.028217 | 0.12996 | 0.073622 | 0.25185 | 0.11552 | 0.051413 | 0.059882 | -0.028879 | 0.043302 | 0.20601 | -0.13419 | -0.18246 | 122.5993 | -0.039413 | 122.5078 | 122.512 | -0.087304 | -0.095751 | 0.082479 | 122.3014 | -0.12607 | 122.5352 | 122.4549 | 0.15358 | 0.036635 | -0.30356 | 122.6138 | 122.5574 | 122.7357 | 122.5997 | -0.053852 | 122.5271 | 122.6898 | 122.3496 | 122.5437 | -0.35184
1316.5156 | 122.7493 | -122.5479 | 0.18768 | -0.0083178 | 0.020647 | -0.062873 | 0.018375 | -0.0014786 | 0.023398 | -0.0061807 | 0.029311 | 0.024746 | 0.025082 | 0.0069017 | 0.022207 | 0.023939 | 0.12045 | 0.023639 | 0.12996 | 0.073622 | 0.24269 | 0.10636 | 0.042256 | 0.059882 | -0.042615 | 0.04788 | 0.21059 | -0.14334 | -0.17788 | 122.6543 | -0.057723 | 122.5719 | 122.5716 | -0.082724 | -0.11406 | 0.055012 | 122.37 | -0.1398 | 122.5902 | 122.5053 | 0.13527 | 0.022903 | -0.33103 | 122.6779 | 122.6215 | 122.7906 | 122.6684 | -0.08132 | 122.5958 | 122.7585 | 122.4046 | 122.6078 | -0.36557
1318.2031 | 122.8912 | -122.4884 | 0.15106 | -0.0083178 | 0.02022 | -0.062873 | 0.018375 | -0.0010512 | 0.023398 | 0.016711 | 0.029525 | 0.024746 | 0.024869 | 0.0069017 | 0.022635 | 0.019361 | 0.11587 | 0.023639 | 0.13912 | 0.069043 | 0.25185 | 0.11094 | 0.046835 | 0.064461 | -0.042615 | 0.052459 | 0.20601 | -0.10671 | -0.18246 | 122.5993 | -0.011945 | 122.5078 | 122.512 | -0.087303 | -0.082019 | 0.10079 | 122.3059 | -0.098603 | 122.5352 | 122.4458 | 0.13985 | 0.054946 | -0.25778 | 122.6275 | 122.5574 | 122.7403 | 122.6043 | -0.04012 | 122.5409 | 122.6944 | 122.3817 | 122.5529 | -0.33353
1319.9219 | 122.8134 | -122.5021 | 0.1831 | -0.00068679 | 0.020434 | -0.063086 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.029738 | 0.024746 | 0.025082 | 0.0069017 | 0.021994 | 0.019361 | 0.11129 | 0.023639 | 0.1208 | 0.078201 | 0.24269 | 0.11094 | 0.055992 | 0.064461 | -0.038036 | 0.04788 | 0.20143 | -0.12503 | -0.17788 | 122.6131 | -0.062301 | 122.5215 | 122.5258 | -0.087303 | -0.1049 | 0.05959 | 122.3243 | -0.13522 | 122.5581 | 122.4641 | 0.13985 | 0.018324 | -0.30813 | 122.6229 | 122.5803 | 122.7448 | 122.6134 | -0.072163 | 122.55 | 122.7036 | 122.3771 | 122.5666 | -0.36099
1321.5938 | 122.8867 | -122.4884 | 0.14648 | 0.0069442 | 0.020647 | -0.062659 | 0.018375 | -0.0010512 | 0.023612 | -0.0061807 | 0.029525 | 0.024746 | 0.025296 | 0.0071153 | 0.021994 | 0.023939 | 0.11587 | 0.01906 | 0.12996 | 0.078201 | 0.24269 | 0.11094 | 0.055992 | 0.06904 | -0.033458 | 0.04788 | 0.21059 | -0.12503 | -0.17788 | 122.5993 | -0.016524 | 122.5123 | 122.5075 | -0.091882 | -0.068283 | 0.096211 | 122.3105 | -0.098604 | 122.5444 | 122.4549 | 0.14443 | 0.064102 | -0.27151 | 122.6184 | 122.5666 | 122.7311 | 122.6043 | -0.035542 | 122.5363 | 122.699 | 122.3634 | 122.5574 | -0.32437
1323.2656 | 122.7859 | -122.5708 | 0.17853 | -0.0083178 | 0.020434 | -0.063086 | 0.018588 | -0.0012648 | 0.023398 | -0.0061807 | 0.029525 | 0.024532 | 0.024869 | 0.0069017 | 0.022207 | 0.019361 | 0.10671 | 0.032795 | 0.12538 | 0.055306 | 0.24269 | 0.1201 | 0.051413 | 0.06904 | -0.033458 | 0.04788 | 0.21059 | -0.11129 | -0.18704 | 122.6909 | -0.053146 | 122.5902 | 122.6036 | -0.087305 | -0.12322 | 0.064167 | 122.3838 | -0.13065 | 122.6222 | 122.5373 | 0.15358 | 0.032058 | -0.28982 | 122.6962 | 122.6261 | 122.8135 | 122.6775 | -0.058428 | 122.6187 | 122.7814 | 122.4595 | 122.6398 | -0.36557
1324.9531 | 122.8775 | -122.4976 | 0.19226 | 0.0069442 | 0.020434 | -0.062873 | 0.018161 | -0.0010512 | 0.023612 | -0.0061807 | 0.029738 | 0.025173 | 0.025296 | 0.0066879 | 0.022635 | 0.019361 | 0.10671 | 0.023639 | 0.13454 | 0.023254 | 0.24727 | 0.1201 | 0.055992 | 0.06904 | -0.033458 | 0.04788 | 0.21059 | -0.13419 | -0.17788 | 122.6177 | -0.057722 | 122.5169 | 122.5212 | -0.096461 | -0.16901 | 0.055013 | 122.3197 | -0.14438 | 122.5536 | 122.4641 | 0.14443 | 0.018325 | -0.32645 | 122.6321 | 122.5208 | 122.7448 | 122.6043 | -0.072161 | 122.5454 | 122.7081 | 122.3634 | 122.5666 | -0.37015
1326.6562 | 122.8912 | -122.5067 | 0.16479 | -0.0083178 | 0.020434 | -0.063086 | 0.018588 | -0.0010512 | 0.023826 | 0.0014498 | 0.029738 | 0.024532 | 0.024869 | 0.0066879 | 0.022207 | 0.028518 | 0.11129 | 0.028217 | 0.13454 | 0.069043 | 0.24269 | 0.11094 | 0.060571 | 0.073618 | -0.028879 | 0.04788 | 0.20601 | -0.13419 | -0.17788 | 122.6177 | -0.030256 | 122.5352 | 122.5349 | -0.082725 | -0.095752 | 0.0779 | 122.3288 | -0.11691 | 122.5673 | 122.4778 | 0.14901 | 0.041213 | -0.29898 | 122.6413 | 122.5758 | 122.7494 | 122.618 | -0.053853 | 122.5546 | 122.7127 | 122.3725 | 122.5803 | -0.34268
1328.3281 | 122.8729 | -122.5159 | 0.1831 | -0.00068679 | 0.020647 | -0.062659 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.029738 | 0.024532 | 0.02551 | 0.0071153 | 0.022207 | 0.028518 | 0.12045 | 0.032795 | 0.13454 | 0.073622 | 0.24269 | 0.10636 | 0.055992 | 0.073618 | -0.033458 | 0.04788 | 0.20601 | -0.1525 | -0.17331 | 122.6222 | -0.048566 | 122.5444 | 122.5487 | -0.073568 | -0.10948 | 0.05959 | 122.3426 | -0.13522 | 122.5719 | 122.4824 | 0.13985 | 0.022903 | -0.3356 | 122.6504 | 122.5895 | 122.7586 | 122.6363 | -0.076742 | 122.5637 | 122.7219 | 122.3634 | 122.5895 | -0.35641
1330 | 122.8363 | -122.5342 | 0.17853 | -0.0083178 | 0.020434 | -0.062873 | 0.018588 | -0.0012648 | 0.023612 | 0.0014498 | 0.029738 | 0.024532 | 0.025296 | 0.0071153 | 0.022207 | 0.014783 | 0.11587 | 0.023639 | 0.12538 | 0.064464 | 0.24727 | 0.11552 | 0.055992 | 0.06904 | -0.038036 | 0.057037 | 0.20601 | -0.14792 | -0.17788 | 122.6497 | -0.053146 | 122.549 | 122.5578 | -0.091882 | -0.11406 | 0.068746 | 122.3563 | -0.12149 | 122.5902 | 122.4961 | 0.13985 | 0.02748 | -0.32645 | 122.6596 | 122.5986 | 122.7815 | 122.6501 | -0.063007 | 122.5912 | 122.7402 | 122.3863 | 122.6032 | -0.35641
1331.6875 | 122.8134 | -122.525 | 0.16937 | 0.022206 | 0.020647 | -0.062445 | 0.018375 | -0.0012648 | 0.022971 | 0.0014498 | 0.029952 | 0.024959 | 0.024869 | 0.0073291 | 0.022207 | 0.019361 | 0.12045 | 0.028217 | 0.12996 | 0.078201 | 0.24269 | 0.1201 | 0.06515 | 0.06904 | -0.028879 | 0.052459 | 0.20601 | -0.14792 | -0.18246 | 122.6451 | -0.039413 | 122.5444 | 122.5532 | -0.091883 | -0.091172 | 0.073322 | 122.3426 | -0.11691 | 122.5902 | 122.4961 | 0.15358 | 0.036635 | -0.31729 | 122.655 | 122.6032 | 122.7677 | 122.6455 | -0.049273 | 122.5775 | 122.731 | 122.3771 | 122.5941 | -0.35184
1333.3594 | 122.85 | -122.5342 | 0.16937 | -0.0083178 | 0.020434 | -0.062445 | 0.018375 | -0.0012648 | 0.023612 | -0.0061807 | 0.029311 | 0.024959 | 0.025296 | 0.0071153 | 0.022207 | 0.019361 | 0.11129 | 0.028217 | 0.12996 | 0.069043 | 0.24727 | 0.10636 | 0.060571 | 0.06904 | -0.0243 | 0.04788 | 0.21059 | -0.1525 | -0.18246 | 122.6405 | -0.039413 | 122.5535 | 122.5624 | -0.078146 | -0.10033 | 0.077901 | 122.3517 | -0.12149 | 122.5948 | 122.5099 | 0.15816 | 0.041213 | -0.32187 | 122.6641 | 122.6032 | 122.7815 | 122.6455 | -0.06301 | 122.5821 | 122.7448 | 122.3817 | 122.6032 | -0.35184
1335.0469 | 122.9141 | -122.4884 | 0.15564 | -0.0083178 | 0.020647 | -0.062659 | 0.018375 | -0.0010512 | 0.023612 | 0.0090803 | 0.029738 | 0.024746 | 0.025296 | 0.0071153 | 0.022635 | 0.019361 | 0.10671 | 0.028217 | 0.12996 | 0.073622 | 0.24727 | 0.11552 | 0.055992 | 0.064461 | -0.038036 | 0.052459 | 0.21516 | -0.12503 | -0.18246 | 122.6039 | -0.02568 | 122.5078 | 122.5166 | -0.087304 | -0.082018 | 0.091634 | 122.3059 | -0.10318 | 122.5444 | 122.4504 | 0.14443 | 0.059525 | -0.28067 | 122.6184 | 122.562 | 122.7357 | 122.5951 | -0.040119 | 122.5409 | 122.7036 | 122.3634 | 122.5529 | -0.3381
1336.75 | 122.8043 | -122.5159 | 0.19684 | 0.0069442 | 0.020434 | -0.062445 | 0.018588 | -0.00083764 | 0.023185 | 0.0014498 | 0.029525 | 0.024532 | 0.025296 | 0.0069017 | 0.022421 | 0.023939 | 0.11129 | 0.041952 | 0.1208 | 0.069043 | 0.24269 | 0.1201 | 0.060571 | 0.06904 | -0.028879 | 0.052459 | 0.21516 | -0.14792 | -0.18246 | 122.636 | -0.076034 | 122.5398 | 122.5578 | -0.078148 | -0.1278 | 0.045857 | 122.3334 | -0.14438 | 122.5764 | 122.487 | 0.15358 | 0.018327 | -0.34476 | 122.6367 | 122.5849 | 122.7586 | 122.6272 | -0.076738 | 122.5683 | 122.731 | 122.3679 | 122.5849 | -0.3793
1338.4688 | 122.8958 | -122.5296 | 0.17395 | -0.00068679 | 0.020434 | -0.062873 | 0.018375 | -0.0010512 | 0.023398 | 0.0014498 | 0.029525 | 0.024959 | 0.025296 | 0.0073291 | 0.022207 | 0.019361 | 0.11129 | 0.023639 | 0.12538 | 0.069043 | 0.24269 | 0.11552 | 0.060571 | 0.073618 | -0.0243 | 0.04788 | 0.21516 | -0.12045 | -0.18246 | 122.6451 | -0.048568 | 122.549 | 122.5532 | -0.091882 | -0.10491 | 0.068745 | 122.3471 | -0.12607 | 122.5902 | 122.5053 | 0.15816 | 0.041215 | -0.2944 | 122.655 | 122.5986 | 122.7723 | 122.6409 | -0.058429 | 122.5775 | 122.7448 | 122.4092 | 122.6032 | -0.35641
1340.1406 | 122.8958 | -122.525 | 0.15564 | -0.0083178 | 0.02022 | -0.062659 | 0.018588 | -0.0012648 | 0.023398 | 0.0014498 | 0.029738 | 0.024746 | 0.025082 | 0.0071153 | 0.021994 | 0.019361 | 0.11129 | 0.023639 | 0.11165 | 0.055306 | 0.23354 | 0.1201 | 0.055992 | 0.064461 | -0.033458 | 0.052459 | 0.21516 | -0.14334 | -0.17788 | 122.6451 | -0.043993 | 122.5444 | 122.5487 | -0.096461 | -0.10033 | 0.077898 | 122.3471 | -0.10318 | 122.581 | 122.4916 | 0.14443 | 0.059525 | -0.29898 | 122.6367 | 122.5803 | 122.7586 | 122.6363 | -0.03554 | 122.5775 | 122.7402 | 122.3817 | 122.5895 | -0.33352
1341.8438 | 122.9233 | -122.5113 | 0.15564 | -0.00068679 | 0.020647 | -0.062873 | 0.018161 | -0.0010512 | 0.023185 | 0.0090803 | 0.029525 | 0.024746 | 0.025082 | 0.0064743 | 0.021994 | 0.010204 | 0.11129 | 0.023639 | 0.1208 | 0.064464 | 0.23354 | 0.11552 | 0.060571 | 0.064461 | -0.028879 | 0.052459 | 0.21974 | -0.15708 | -0.18246 | 122.6268 | -0.034836 | 122.5215 | 122.5349 | -0.091882 | -0.091176 | 0.077898 | 122.3288 | -0.10318 | 122.5719 | 122.4824 | 0.15358 | 0.064104 | -0.31272 | 122.6321 | 122.5758 | 122.7448 | 122.6226 | -0.040119 | 122.5638 | 122.731 | 122.3542 | 122.5758 | -0.3381
1343.5781 | 122.9095 | -122.4792 | 0.16937 | -0.00068679 | 0.02022 | -0.062659 | 0.018588 | -0.0014786 | 0.023612 | -0.0061807 | 0.029311 | 0.024959 | 0.025082 | 0.0071153 | 0.022421 | 0.014783 | 0.10671 | 0.014482 | 0.11622 | 0.059885 | 0.23354 | 0.1201 | 0.055992 | 0.064461 | -0.028879 | 0.043302 | 0.20601 | -0.1525 | -0.17331 | 122.5993 | -0.053148 | 122.494 | 122.4937 | -0.10562 | -0.10949 | 0.064165 | 122.3059 | -0.12607 | 122.5352 | 122.4504 | 0.14443 | 0.036635 | -0.32187 | 122.5955 | 122.5391 | 122.7128 | 122.586 | -0.049273 | 122.5225 | 122.6853 | 122.3267 | 122.5437 | -0.34268
1345.25 | 122.8546 | -122.5479 | 0.17853 | -0.00068679 | 0.020434 | -0.062873 | 0.018375 | -0.0010512 | 0.023185 | 0.0014498 | 0.029738 | 0.024959 | 0.02551 | 0.0069017 | 0.022207 | 0.005626 | 0.10214 | 0.01906 | 0.1208 | 0.046148 | 0.22896 | 0.11552 | 0.06515 | 0.06904 | -0.0243 | 0.04788 | 0.21516 | -0.14792 | -0.17788 | 122.6634 | -0.057724 | 122.5535 | 122.567 | -0.096461 | -0.13238 | 0.050431 | 122.37 | -0.13065 | 122.6131 | 122.5236 | 0.15358 | 0.036637 | -0.32645 | 122.6687 | 122.5941 | 122.7769 | 122.65 | -0.063007 | 122.5958 | 122.7631 | 122.4 | 122.617 | -0.35641
1346.9375 | 122.7859 | -122.5662 | 0.17853 | 0.0069442 | 0.02022 | -0.062873 | 0.018375 | -0.0014786 | 0.022971 | -0.0061807 | 0.029525 | 0.025173 | 0.025296 | 0.0071153 | 0.022421 | 0.005626 | 0.10671 | 0.014482 | 0.10249 | 0.023254 | 0.22896 | 0.1201 | 0.060571 | 0.06904 | -0.028879 | 0.04788 | 0.21059 | -0.1525 | -0.17788 | 122.6863 | -0.076038 | 122.5718 | 122.5807 | -0.10562 | -0.15527 | 0.050431 | 122.3883 | -0.13065 | 122.6268 | 122.5373 | 0.14901 | 0.032058 | -0.33103 | 122.6687 | 122.5895 | 122.7952 | 122.6729 | -0.058428 | 122.6141 | 122.7768 | 122.4137 | 122.6353 | -0.35641
1348.6875 | 122.7905 | -122.58 | 0.19226 | 0.014575 | 0.020434 | -0.062873 | 0.018161 | -0.0010512 | 0.023185 | 0.0090803 | 0.029525 | 0.024959 | 0.025082 | 0.0073291 | 0.022421 | 0.019361 | 0.11129 | 0.01906 | 0.11165 | 0.03699 | 0.23354 | 0.10636 | 0.055992 | 0.06904 | -0.038036 | 0.038723 | 0.21516 | -0.12503 | -0.17788 | 122.6863 | -0.080614 | 122.5993 | 122.599 | -0.087303 | -0.15527 | 0.041277 | 122.4021 | -0.15354 | 122.6359 | 122.5419 | 0.13985 | 0.022904 | -0.31729 | 122.6916 | 122.6169 | 122.8135 | 122.6912 | -0.085898 | 122.6187 | 122.7951 | 122.4549 | 122.649 | -0.37015
1350.3906 | 122.8958 | -122.5021 | 0.16022 | 0.0069442 | 0.020434 | -0.062659 | 0.018588 | -0.0010512 | 0.023398 | 0.0090803 | 0.029525 | 0.024959 | 0.025082 | 0.0071153 | 0.022421 | 0.028518 | 0.11587 | 0.014482 | 0.10707 | 0.018675 | 0.22438 | 0.1201 | 0.055992 | 0.06904 | -0.028879 | 0.043302 | 0.21059 | -0.14792 | -0.17788 | 122.6222 | -0.053149 | 122.5307 | 122.5166 | -0.10562 | -0.14154 | 0.064164 | 122.3243 | -0.11691 | 122.5581 | 122.4733 | 0.14901 | 0.050369 | -0.30814 | 122.6092 | 122.5208 | 122.7265 | 122.618 | -0.040117 | 122.5454 | 122.7127 | 122.3542 | 122.5712 | -0.3381
1352.1562 | 122.8775 | -122.5204 | 0.15564 | -0.0083178 | 0.02022 | -0.062873 | 0.018588 | -0.00083764 | 0.023398 | 0.0090803 | 0.029525 | 0.024746 | 0.02551 | 0.0071153 | 0.022421 | 0.014783 | 0.11129 | 0.023639 | 0.11165 | -0.008799 | 0.22896 | 0.11552 | 0.06515 | 0.06904 | -0.033458 | 0.04788 | 0.21059 | -0.14334 | -0.17788 | 122.636 | -0.043993 | 122.5352 | 122.5441 | -0.091882 | -0.16444 | 0.073319 | 122.3426 | -0.10776 | 122.5856 | 122.487 | 0.14443 | 0.054946 | -0.29898 | 122.6321 | 122.5116 | 122.7494 | 122.6317 | -0.040119 | 122.5683 | 122.731 | 122.3771 | 122.5895 | -0.33352
1353.9062 | 122.8683 | -122.5342 | 0.15564 | -0.0083178 | 0.020434 | -0.062873 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.029097 | 0.024746 | 0.025082 | 0.0073291 | 0.021994 | 0.019361 | 0.11587 | 0.032795 | 0.11622 | 0.014096 | 0.23354 | 0.11552 | 0.051413 | 0.06904 | -0.028879 | 0.043302 | 0.20601 | -0.1525 | -0.17331 | 122.6497 | -0.039415 | 122.5535 | 122.567 | -0.082726 | -0.14154 | 0.077898 | 122.3609 | -0.11234 | 122.5856 | 122.5053 | 0.14443 | 0.050368 | -0.30814 | 122.6504 | 122.5483 | 122.7677 | 122.6501 | -0.040119 | 122.5775 | 122.7402 | 122.3817 | 122.6032 | -0.32895
1355.5781 | 122.8088 | -122.58 | 0.19684 | 0.0069442 | 0.020647 | -0.062659 | 0.018802 | -0.0010512 | 0.023612 | -0.013811 | 0.029738 | 0.024746 | 0.025296 | 0.0071153 | 0.022421 | 0.019361 | 0.11587 | 0.023639 | 0.11622 | 0.032411 | 0.22896 | 0.11094 | 0.060571 | 0.06904 | -0.033458 | 0.04788 | 0.20601 | -0.11129 | -0.18704 | 122.6909 | -0.080613 | 122.5993 | 122.6036 | -0.087303 | -0.16443 | 0.032121 | 122.3929 | -0.14896 | 122.6405 | 122.5465 | 0.15358 | 0.00917 | -0.30813 | 122.6962 | 122.6124 | 122.8089 | 122.6958 | -0.085896 | 122.6278 | 122.786 | 122.4687 | 122.649 | -0.38388
1357.3125 | 122.8134 | -122.5433 | 0.17853 | -0.00068679 | 0.020861 | -0.062659 | 0.018588 | -0.0010512 | 0.023612 | -0.0061807 | 0.029525 | 0.024532 | 0.025296 | 0.0066879 | 0.022207 | 0.028518 | 0.12045 | 0.023639 | 0.11622 | 0.014096 | 0.23354 | 0.11094 | 0.06515 | 0.06904 | -0.038036 | 0.04788 | 0.21059 | -0.1525 | -0.17788 | 122.6543 | -0.062303 | 122.5719 | 122.567 | -0.087303 | -0.16443 | 0.05501 | 122.3654 | -0.13065 | 122.6085 | 122.5053 | 0.13985 | 0.032058 | -0.33103 | 122.6596 | 122.5574 | 122.7769 | 122.6638 | -0.067586 | 122.5912 | 122.7539 | 122.3908 | 122.6124 | -0.35641
1358.9844 | 122.7676 | -122.5433 | 0.16479 | 0.0069442 | 0.020861 | -0.062873 | 0.018375 | -0.0012648 | 0.023612 | 0.0090803 | 0.029525 | 0.024746 | 0.025082 | 0.0064743 | 0.022421 | 0.019361 | 0.12503 | 0.023639 | 0.11622 | 0.03699 | 0.22438 | 0.11094 | 0.055992 | 0.073618 | -0.0243 | 0.043302 | 0.20601 | -0.14792 | -0.17788 | 122.6543 | -0.04857 | 122.5627 | 122.567 | -0.087303 | -0.12781 | 0.059586 | 122.3654 | -0.12149 | 122.5993 | 122.519 | 0.15358 | 0.041213 | -0.31272 | 122.6596 | 122.5803 | 122.7677 | 122.6684 | -0.053853 | 122.5866 | 122.7493 | 122.3954 | 122.617 | -0.34268
1360.7188 | 122.8271 | -122.5754 | 0.17853 | -0.00068679 | 0.020647 | -0.062659 | 0.018802 | -0.0010512 | 0.023398 | 0.0014498 | 0.029311 | 0.024532 | 0.024869 | 0.0069017 | 0.022421 | 0.014783 | 0.12045 | 0.014482 | 0.10707 | 0.023254 | 0.22438 | 0.11552 | 0.055992 | 0.06904 | -0.028879 | 0.043302 | 0.21059 | -0.11129 | -0.17331 | 122.6909 | -0.07146 | 122.5902 | 122.5899 | -0.10104 | -0.15527 | 0.045853 | 122.4021 | -0.13523 | 122.6314 | 122.5465 | 0.14443 | 0.032058 | -0.28982 | 122.6824 | 122.5986 | 122.7998 | 122.6958 | -0.063007 | 122.6187 | 122.786 | 122.4641 | 122.6444 | -0.35183

## Thermal Data
Fire Time | north top | north mid | north bottom | south top | south mid | south bottom
-0.1521 | 18.2242 | 18.1558 | 17.7366 | 18.0663 | 17.8723 | 17.9888
0.8479 | 18.2463 | 18.1463 | 17.7632 | 18.087 | 17.8593 | 17.9725
1.8479 | 18.7657 | 53.7732 | 18.0188 | 18.1475 | 17.8387 | 17.9795
2.8479 | 19.6845 | 114.248 | 18.3772 | 18.2408 | 17.8369 | 18.0378
3.8479 | 20.5925 | 184.8614 | 18.9654 | 18.5379 | 17.8682 | 18.1251
4.8479 | 22.1628 | 227.2802 | 19.8206 | 19.8252 | 17.9439 | 18.9014
5.8479 | 23.9425 | 301.5167 | 20.84 | 20.2352 | 18.0794 | 19.5109
6.8479 | 25.9472 | 366.969 | 21.9299 | 22.0303 | 18.844 | 20.2747
7.8479 | 27.83 | 416.4108 | 22.988 | 24.6266 | 21.163 | 21.8346
8.8479 | 30.3325 | 461.3779 | 24.216 | 28.0874 | 23.8294 | 24.5954
9.8479 | 32.0636 | 518.8523 | 25.1904 | 32.181 | 26.3666 | 27.1146
10.8479 | 33.4652 | 534.8389 | 26.0511 | 35.1764 | 29.8406 | 29.0368
11.8479 | 34.936 | 550.1456 | 27.2412 | 38.4419 | 32.883 | 33.2438
12.8479 | 36.2334 | 555.5603 | 27.9563 | 41.3097 | 35.937 | 34.8438
13.8479 | 37.1068 | 572.4979 | 28.5262 | 44.3972 | 38.6905 | 37.2313
14.8479 | 37.8426 | 575.6008 | 29.0303 | 48.5706 | 42.0497 | 39.9729
15.8479 | 38.5935 | 567.1843 | 29.4787 | 51.8513 | 45.0538 | 43.4604
16.8479 | 39.2189 | 555.9507 | 29.8463 | 54.268 | 47.488 | 45.7097
17.8479 | 39.8323 | 541.9012 | 30.2157 | 57.8002 | 49.0998 | 48.5365
18.8479 | 40.4836 | 544.1355 | 30.5726 | 60.1406 | 51.5244 | 51.0649
19.8479 | 40.9447 | 523.2871 | 30.9056 | 62.7588 | 53.7961 | 53.2363
20.8479 | 41.1753 | 511.3186 | 31.2557 | 63.7428 | 55.0336 | 54.4128
21.8479 | 41.4759 | 487.7621 | 31.5232 | 63.5551 | 57.0333 | 57.0472
22.8479 | 41.7134 | 477.2798 | 31.6374 | 66.7372 | 58.1072 | 59.3275
23.8479 | 42.0872 | 472.9115 | 31.8817 | 67.8544 | 59.2838 | 60.1448
24.8479 | 42.3229 | 458.2497 | 32.096 | 68.907 | 60.4323 | 61.3714
25.8479 | 42.5511 | 451.2044 | 32.2275 | 69.3583 | 61.8905 | 61.7516
26.8479 | 42.845 | 451.3417 | 32.3944 | 70.4205 | 62.9111 | 62.1599
27.8479 | 43.3048 | 431.7164 | 32.6316 | 71.138 | 63.8929 | 63.2241
28.8479 | 43.3719 | 424.9876 | 32.8307 | 72.5575 | 65.2886 | 64.0657
29.8479 | 43.6165 | 411.5081 | 32.9679 | 73.403 | 66.0429 | 64.6601
30.8479 | 43.8543 | 405.8568 | 33.085 | 74.3241 | 67.026 | 65.3109
31.8479 | 44.0226 | 393.899 | 33.1421 | 75.0246 | 67.891 | 65.7678
32.8479 | 44.2477 | 396.285 | 33.2237 | 75.0052 | 68.7123 | 66.4818
33.8479 | 44.4607 | 390.2703 | 33.2841 | 75.8963 | 69.378 | 66.8383
34.8479 | 44.8014 | 391.9853 | 33.3723 | 76.3822 | 69.6182 | 67.3367
35.8479 | 45.0169 | 381.5361 | 33.4037 | 76.7115 | 70.4319 | 67.6638
36.8479 | 45.3394 | 370.9636 | 33.4293 | 76.8474 | 70.9123 | 68.387
37.8479 | 45.3556 | 372.0999 | 33.5199 | 77.309 | 71.301 | 69.3346
38.8479 | 45.5809 | 381.6576 | 33.5263 | 77.5946 | 71.9764 | 69.8246
39.8479 | 45.8319 | 379.1641 | 33.4654 | 78.0857 | 72.4456 | 70.052
40.8479 | 45.9831 | 385.0951 | 33.539 | 78.5615 | 72.7412 | 70.7179
41.8479 | 46.0891 | 384.0883 | 33.4927 | 78.8449 | 72.881 | 71.1249
42.8479 | 46.2321 | 379.4517 | 33.5109 | 79.0676 | 73.2834 | 71.7012
43.8479 | 46.2779 | 382.8048 | 33.486 | 79.2976 | 73.7315 | 72.3646
44.8479 | 46.3119 | 375.8466 | 33.4205 | 79.9777 | 74.097 | 72.7524
45.8479 | 46.3051 | 385.739 | 33.3722 | 80.5241 | 74.3897 | 73.1928
46.8479 | 46.4369 | 384.14 | 33.3142 | 80.8761 | 74.7723 | 73.7119
47.8479 | 46.3519 | 383.8755 | 33.2184 | 81.3218 | 75.4662 | 74.4084
48.8479 | 46.3702 | 385.6967 | 33.2102 | 81.7565 | 76.0537 | 74.757
49.8479 | 46.4524 | 378.2458 | 33.2739 | 80.5719 | 76.137 | 75.3482
50.8479 | 46.6907 | 376.5542 | 33.2946 | 82.0975 | 76.5154 | 75.5469
51.8479 | 46.7677 | 369.9193 | 33.3576 | 82.4215 | 76.6905 | 75.8454
52.8479 | 46.9304 | 372.1389 | 33.4041 | 82.3829 | 77.0353 | 76.2446
53.8479 | 47.0977 | 376.3231 | 33.5204 | 82.778 | 77.3373 | 76.3535
54.8479 | 47.4027 | 387.7401 | 33.6034 | 83.1306 | 77.6704 | 76.7705
55.8479 | 47.5736 | 385.7012 | 33.7091 | 83.2959 | 77.9082 | 76.9322
56.8479 | 47.6434 | 382.6418 | 33.763 | 83.4253 | 77.9894 | 77.3724
57.8479 | 48.0235 | 397.3167 | 33.8379 | 80.4691 | 78.0577 | 77.7632
58.8479 | 48.1162 | 411.3126 | 33.9076 | 83.2813 | 78.5642 | 78.1486
59.8479 | 48.3098 | 419.4703 | 33.9689 | 83.7592 | 78.7747 | 78.2065
60.8479 | 48.5859 | 425.5783 | 34.1513 | 84.0732 | 79.1334 | 78.2566
61.8479 | 48.9551 | 418.2332 | 34.4263 | 83.7077 | 79.5096 | 78.2705
62.8479 | 49.2544 | 422.837 | 34.559 | 85.4169 | 80.1467 | 78.8148
63.8479 | 49.5842 | 426.5945 | 34.6434 | 86.0045 | 80.0658 | 79.6174
64.8479 | 50.0589 | 441.0233 | 34.9351 | 86.4727 | 80.4555 | 79.7561
65.8479 | 50.4413 | 444.5328 | 35.2232 | 87.1837 | 81.2141 | 80.6288
66.8479 | 50.8675 | 452.2867 | 35.4846 | 88.0194 | 81.5406 | 81.7894
67.8479 | 51.3258 | 451.2028 | 35.7656 | 88.3155 | 81.7106 | 82.0552
68.8479 | 51.6381 | 467.3937 | 36.0268 | 89.1191 | 82.5526 | 82.3987
69.8479 | 52.0871 | 478.701 | 36.4329 | 89.7647 | 83.1854 | 82.7032
70.8479 | 52.6803 | 474.9538 | 36.6917 | 89.7054 | 83.2853 | 83.4799
71.8479 | 53.0283 | 463.2906 | 36.997 | 90.5359 | 83.4227 | 83.6195
72.8479 | 53.4581 | 466.1786 | 37.2208 | 90.7204 | 83.8838 | 83.6204
73.8479 | 53.6951 | 472.8955 | 37.4184 | 91.2438 | 84.7581 | 83.6882
74.8479 | 54.1099 | 471.3131 | 37.5882 | 91.8085 | 85.5152 | 84.5438
75.8479 | 54.4848 | 467.1155 | 37.7103 | 92.3874 | 86.5317 | 85.2913
76.8479 | 54.8167 | 468.2224 | 37.735 | 93.165 | 87.0251 | 85.5348
77.8479 | 55.2118 | 482.742 | 37.856 | 93.6721 | 87.532 | 86.329
78.8479 | 55.5726 | 495.7414 | 37.9805 | 94.3962 | 88.4966 | 87.015
79.8479 | 55.8232 | 508.8117 | 38.3588 | 94.7896 | 88.4937 | 87.5961
80.8479 | 56.2761 | 504.8213 | 38.7652 | 95.453 | 88.7337 | 88.5328
81.8479 | 56.5179 | 503.2117 | 38.9447 | 95.6558 | 89.3655 | 89.2576
82.8635 | 56.969 | 502.7367 | 39.1125 | 96.4035 | 89.6682 | 89.388
83.8479 | 57.3915 | 514.6 | 39.3287 | 97.1924 | 90.0659 | 89.8639
84.8479 | 57.9512 | 516.2984 | 39.5598 | 98.0004 | 90.7551 | 90.1169
85.8479 | 58.276 | 513.8523 | 39.717 | 98.3394 | 91.7949 | 90.6527
86.8479 | 58.6002 | 516.7769 | 40.0063 | 98.7628 | 92.3634 | 90.7728
87.8479 | 59.0882 | 513.6352 | 40.3817 | 99.0371 | 92.7909 | 91.0351
88.8479 | 59.4011 | 522.33 | 40.6409 | 99.4422 | 93.459 | 91.7948
89.8479 | 59.8226 | 522.1788 | 40.9667 | 100.0901 | 93.7353 | 92.3504
90.8479 | 59.7996 | 520.2976 | 41.1916 | 100.4918 | 94.1091 | 92.9782
91.8479 | 60.1015 | 518.4582 | 41.4584 | 100.959 | 94.5704 | 93.2967
92.8479 | 60.4633 | 524.5028 | 41.6616 | 101.2848 | 94.7802 | 94.2574
93.8479 | 60.5914 | 512.0633 | 41.8874 | 101.447 | 95.0599 | 94.918
94.8479 | 60.6301 | 490.9048 | 42.0723 | 101.6109 | 95.5238 | 94.9052
95.8479 | 60.7545 | 490.2624 | 42.3318 | 101.8746 | 96.365 | 95.3941
96.8479 | 60.8094 | 486.9656 | 42.4884 | 102.081 | 97.3107 | 95.946
97.8479 | 60.8286 | 493.213 | 42.9377 | 102.7133 | 98.0485 | 96.3233
98.8479 | 60.8547 | 471.798 | 43.0789 | 103.2432 | 98.5436 | 96.9251
99.8479 | 60.9533 | 490.5949 | 43.304 | 103.7219 | 98.856 | 96.9608
100.8479 | 60.9918 | 497.7889 | 43.6152 | 103.7454 | 99.1886 | 98.0096
101.8479 | 61.2023 | 509.2305 | 43.764 | 103.836 | 99.4196 | 98.4003
102.8479 | 61.2764 | 508.3594 | 43.8962 | 104.1173 | 99.8189 | 98.5527
103.8479 | 61.4407 | 519.8168 | 44.0601 | 104.8391 | 99.6074 | 99.3571
104.8479 | 61.3877 | 508.1043 | 44.2384 | 105.4651 | 99.9951 | 99.7644
105.8479 | 61.603 | 494.2052 | 44.5066 | 105.9518 | 100.4264 | 100.1154
106.8479 | 61.6791 | 499.5623 | 44.8076 | 106.718 | 101.048 | 100.5255
107.8479 | 61.7708 | 511.3242 | 45.0656 | 107.2005 | 101.3822 | 101.4727
108.8479 | 61.8814 | 501.5508 | 45.046 | 107.509 | 101.8063 | 101.5508
109.8479 | 61.9786 | 488.0172 | 45.2798 | 107.6653 | 101.9615 | 101.6955
110.8479 | 61.9524 | 480.6047 | 45.3552 | 107.8143 | 102.2804 | 101.9545
111.8479 | 62.056 | 479.9788 | 45.4073 | 108.2765 | 102.538 | 102.3664
112.8479 | 62.1083 | 480.6969 | 45.5511 | 108.2915 | 102.9807 | 102.4731
113.8479 | 62.3346 | 473.8673 | 45.7384 | 108.2741 | 103.2124 | 102.7741
114.8479 | 62.5678 | 482.114 | 45.9174 | 108.4525 | 103.6694 | 102.8813
115.8479 | 62.7986 | 483.0583 | 46.132 | 108.7486 | 104.4991 | 103.1792
116.8479 | 62.7982 | 478.7314 | 46.463 | 109.0446 | 104.6408 | 103.086
117.8479 | 63.0214 | 482.8834 | 46.7489 | 109.0877 | 104.8186 | 103.2871
118.8479 | 63.2601 | 498.2307 | 46.9984 | 109.4002 | 105.2959 | 103.4999
119.8479 | 63.6523 | 504.7673 | 46.9206 | 109.3487 | 105.3482 | 103.5657
120.8479 | 63.76 | 506.4321 | 46.9951 | 109.5758 | 105.437 | 104.2934
121.8479 | 64.0323 | 523.7841 | 46.8205 | 109.4989 | 105.8217 | 104.6295
122.8479 | 64.2018 | 515.2835 | 46.7087 | 109.6517 | 106.1291 | 104.8662
123.8479 | 64.3034 | 515.3656 | 46.8668 | 109.7979 | 106.4236 | 105.0418
124.8479 | 64.4533 | 517.3986 | 46.9629 | 110.2303 | 106.4476 | 105.2269
125.8479 | 64.4916 | 532.8052 | 47.1343 | 110.5865 | 106.6126 | 105.2662
126.8479 | 64.685 | 529.0086 | 46.9809 | 111.0147 | 106.7616 | 105.4699
127.8479 | 64.8186 | 534.4954 | 47.1264 | 110.9992 | 107.1812 | 105.7444
128.8479 | 64.6936 | 540.202 | 47.1966 | 111.0737 | 107.5635 | 105.8836
129.8479 | 64.6806 | 549.1464 | 47.2594 | 111.2276 | 107.6307 | 105.9533
130.8479 | 64.7713 | 546.5959 | 47.7126 | 111.3736 | 107.998 | 106.4502
131.8479 | 64.7912 | 539.8309 | 47.8789 | 111.6525 | 108.1036 | 106.573
132.8479 | 64.6638 | 542.4169 | 47.9372 | 111.7285 | 108.2756 | 107.2967
133.8479 | 64.7771 | 545.5886 | 47.8325 | 112.2306 | 108.3874 | 107.5862
134.8479 | 64.7181 | 531.0004 | 47.9718 | 112.4998 | 108.2882 | 108.1576
135.8479 | 64.83 | 549.4125 | 47.8631 | 112.9727 | 108.18 | 108.4951
136.8479 | 64.8197 | 540.4532 | 47.8822 | 113.3587 | 108.619 | 109.4306
137.8479 | 64.8643 | 543.1656 | 47.9737 | 113.4825 | 108.9592 | 109.3695
138.8479 | 64.8604 | 546.7477 | 47.8757 | 113.4356 | 109.304 | 109.1523
139.8479 | 65.0813 | 546.3911 | 47.8743 | 113.9959 | 109.9202 | 109.0232
140.8479 | 65.1273 | 533.38 | 47.9877 | 114.3157 | 110.4104 | 109.7174
141.8479 | 65.0981 | 518.1577 | 47.9685 | 114.6879 | 110.4171 | 110.3421
142.8479 | 65.2762 | 530.8438 | 47.9594 | 115.4173 | 110.4454 | 110.3648
143.8479 | 65.2641 | 536.5945 | 47.9796 | 115.5544 | 110.8631 | 110.8311
144.8479 | 65.1609 | 555.6041 | 47.9421 | 115.9791 | 110.7371 | 111.2053
145.8479 | 65.1572 | 558.2329 | 47.7411 | 116.237 | 110.9474 | 111.3751
146.8479 | 65.2239 | 537.3586 | 47.7311 | 116.2626 | 111.2529 | 111.2623
147.8479 | 65.2907 | 519.2706 | 47.8609 | 116.4222 | 111.4675 | 111.5304
148.8479 | 65.4422 | 522.122 | 48.1387 | 116.3345 | 111.5374 | 111.9776
149.8479 | 65.5395 | 529.777 | 48.1257 | 116.1023 | 111.8388 | 111.8757
150.8479 | 65.6842 | 537.5199 | 48.0761 | 116.3682 | 112.2814 | 112.1378
151.8479 | 65.8425 | 539.0945 | 48.1426 | 116.625 | 112.7108 | 112.2064
152.8479 | 66.1035 | 533.0552 | 48.0867 | 117.015 | 113.2608 | 112.1248
153.8479 | 66.4582 | 540.6607 | 48.2372 | 117.0094 | 113.422 | 112.3346
154.8479 | 66.6956 | 545.3243 | 48.4105 | 117.0464 | 113.2541 | 111.9786
155.8479 | 66.7461 | 549.7467 | 48.2499 | 117.2426 | 113.3874 | 111.6994
156.8479 | 66.9299 | 562.0001 | 48.1872 | 117.5277 | 113.5723 | 111.8387
157.8479 | 66.7917 | 583.7266 | 48.1538 | 117.6794 | 114.1308 | 112.0342
158.8479 | 66.8253 | 581.0473 | 48.144 | 117.8633 | 114.2146 | 112.3727
159.8479 | 67.032 | 592.4918 | 48.3969 | 118.1703 | 114.2274 | 112.525
160.8479 | 67.0806 | 576.2729 | 48.4463 | 118.2425 | 114.2696 | 112.5967
161.8479 | 67.1969 | 571.7909 | 48.6705 | 118.2539 | 114.4864 | 113.0693
162.8479 | 67.1115 | 560.9749 | 49.0361 | 118.3666 | 114.8918 | 113.5688
163.8479 | 67.2685 | 569.7383 | 49.2469 | 118.9036 | 115.2249 | 113.8244
164.8479 | 67.6688 | 560.8055 | 49.3711 | 119.0672 | 115.5554 | 113.7315
165.8479 | 67.3656 | 565.0108 | 49.3143 | 118.9605 | 115.9276 | 114.1566
166.8479 | 67.4707 | 556.8605 | 49.2556 | 119.4193 | 115.8206 | 114.6985
167.8479 | 67.6947 | 549.4381 | 49.3625 | 119.3404 | 116.123 | 114.4647
168.8479 | 67.695 | 541.0355 | 49.5494 | 119.6626 | 116.3787 | 114.3125
169.8479 | 67.8477 | 547.1696 | 49.848 | 119.7712 | 116.3538 | 114.214
170.8479 | 67.9625 | 543.6376 | 50.1148 | 120.0136 | 116.6433 | 114.4276
171.8479 | 68.1192 | 548.2724 | 50.2136 | 120.3836 | 116.811 | 114.3036
172.8479 | 68.31 | 546.6685 | 50.4005 | 120.5728 | 116.8 | 114.5743
173.8479 | 68.4436 | 540.7841 | 50.4713 | 120.4833 | 116.7925 | 114.5472
174.8479 | 68.6594 | 543.3222 | 50.3789 | 120.4096 | 116.7825 | 114.7841
175.8479 | 68.7708 | 536.9169 | 50.4098 | 120.6465 | 117.1543 | 115.5176
176.8479 | 68.8621 | 520.7274 | 50.4186 | 120.7742 | 117.4231 | 116.027
177.8479 | 68.8965 | 514.552 | 50.2898 | 121.027 | 117.3874 | 116.2334
178.8479 | 69.0636 | 517.9887 | 50.3783 | 121.4631 | 117.4569 | 117.0761
179.8479 | 69.2623 | 511.5806 | 50.2592 | 121.9173 | 117.6408 | 117.0709
180.8479 | 69.3103 | 500.4506 | 50.0021 | 121.9263 | 118.0969 | 117.4254
181.8479 | 69.4751 | 496.0882 | 50.0484 | 122.0299 | 118.3901 | 117.9343
182.8479 | 69.3898 | 517.2868 | 50.1889 | 122.1762 | 118.3483 | 118.2304
183.8479 | 69.5936 | 524.133 | 50.2703 | 122.0985 | 118.3993 | 118.1284
184.8479 | 69.6587 | 533.6445 | 50.5496 | 121.9446 | 118.4804 | 117.8343
185.8479 | 69.9159 | 531.3926 | 50.5692 | 121.6906 | 118.3096 | 117.8597
186.8479 | 69.8853 | 532.5298 | 50.5759 | 122.0179 | 118.3288 | 117.8658
187.8479 | 69.9667 | 536.0708 | 50.5125 | 122.0738 | 118.3584 | 117.8943
188.8479 | 70.1321 | 541.3337 | 50.3885 | 121.9049 | 118.5479 | 117.9758
189.8479 | 70.1934 | 538.4357 | 50.2069 | 121.7002 | 118.9439 | 117.8255
190.8479 | 70.3262 | 526.614 | 50.1827 | 121.6939 | 118.9928 | 117.8323
191.8479 | 70.1883 | 524.7688 | 50.1546 | 122.0995 | 119.061 | 117.7986
192.8479 | 70.4953 | 522.7274 | 50.095 | 122.1531 | 119.275 | 117.961
193.8479 | 70.5623 | 510.542 | 50.1383 | 122.1127 | 119.1356 | 118.0709
194.8479 | 70.5879 | 517.3998 | 50.1553 | 122.3083 | 118.8468 | 118.5967
195.8479 | 70.892 | 529.9891 | 50.23 | 122.1194 | 118.9284 | 118.7072
196.8479 | 71.0634 | 538.3694 | 50.4405 | 121.9578 | 119.2549 | 119.0361
197.8479 | 71.1746 | 540.9198 | 50.5717 | 122.1787 | 119.3223 | 118.7616
198.8479 | 71.4688 | 557.8313 | 50.6529 | 122.2374 | 119.2832 | 118.6334
199.8479 | 71.7472 | 570.171 | 50.8221 | 122.5311 | 119.5824 | 118.6188
200.8479 | 71.9976 | 566.8024 | 50.9106 | 122.9387 | 119.4463 | 118.3643
201.8479 | 72.1508 | 562.2623 | 50.9899 | 122.7421 | 119.427 | 118.1701
202.8479 | 72.1502 | 562.7783 | 50.9357 | 123.0171 | 120.04 | 117.8519
203.8479 | 72.5778 | 579.1895 | 50.997 | 123.516 | 120.456 | 117.6746
204.8479 | 72.7963 | 585.9437 | 50.9876 | 123.6676 | 120.7764 | 118.6553
205.8479 | 72.6908 | 593.9541 | 51.0547 | 123.8542 | 121.1306 | 118.7444
206.8479 | 73.0466 | 607.2892 | 51.1012 | 124.2007 | 121.2081 | 118.6152
207.8479 | 73.1623 | 599.9878 | 51.0753 | 124.4735 | 121.1904 | 119.0028
208.8479 | 73.0631 | 594.9658 | 51.1188 | 124.8426 | 121.2985 | 119.043
209.8479 | 73.2532 | 606.1619 | 51.0554 | 125.0199 | 121.3469 | 119.7706
210.8479 | 73.3186 | 609.748 | 50.9582 | 125.8039 | 121.4499 | 120.2388
211.8479 | 73.2951 | 615.9198 | 50.8893 | 126.0444 | 121.5102 | 120.4157
212.8479 | 73.3826 | 618.3633 | 50.779 | 126.4384 | 121.4256 | 120.1682
213.8479 | 73.334 | 630.0631 | 50.578 | 126.606 | 121.7942 | 120.2145
214.8479 | 73.3675 | 631.0991 | 50.5799 | 126.7779 | 122.0937 | 120.4091
215.8479 | 73.3448 | 630.3946 | 50.5016 | 127.0186 | 122.4227 | 120.1451
216.8479 | 73.4411 | 633.8419 | 50.5113 | 127.3916 | 122.2459 | 120.2964
217.8479 | 73.5409 | 623.3283 | 50.5849 | 127.6525 | 122.5224 | 120.2663
218.8479 | 73.5471 | 626.8451 | 50.5932 | 128.2358 | 122.8159 | 120.0238
219.8479 | 73.5539 | 631.4347 | 50.6983 | 128.1896 | 123.1428 | 120.0205
220.8479 | 73.495 | 639.8822 | 50.7098 | 128.0924 | 123.4623 | 119.7678
221.8479 | 73.668 | 632.5694 | 50.7315 | 128.3548 | 123.4772 | 119.5366
222.8479 | 73.9444 | 623.4743 | 50.6321 | 128.3201 | 123.3813 | 120.0981
223.8479 | 74.1123 | 629.9663 | 50.5652 | 128.1563 | 123.6332 | 120.4455
224.8479 | 74.249 | 613.7455 | 50.4681 | 127.9472 | 124.0454 | 120.5499
225.8479 | 74.3082 | 614.0868 | 50.5607 | 128.2158 | 124.2467 | 120.702
226.8479 | 74.6001 | 622.8819 | 50.6815 | 128.4275 | 124.5819 | 121.4047
227.8479 | 74.7446 | 609.2618 | 50.7532 | 128.7537 | 124.7164 | 121.5675
228.8479 | 74.9839 | 617.3804 | 50.8465 | 129.0811 | 124.3653 | 121.3729
229.8479 | 75.3081 | 623.3553 | 50.8464 | 129.1133 | 124.1564 | 121.6859
230.8479 | 75.4901 | 623.7283 | 50.8255 | 128.9299 | 124.3318 | 121.8208
231.8479 | 75.5684 | 603.0675 | 51.0184 | 128.6681 | 124.4359 | 121.9229
232.8479 | 75.6846 | 609.6943 | 51.3486 | 128.3991 | 124.3826 | 121.9796
233.8479 | 75.953 | 613.8974 | 51.4434 | 128.3132 | 124.4806 | 122.801
234.8479 | 76.0059 | 605.7459 | 51.5977 | 128.2507 | 124.6362 | 123.1387
235.8479 | 76.1233 | 602.9868 | 51.8275 | 128.3014 | 124.4703 | 123.3026
236.8479 | 76.2426 | 595.6483 | 51.9548 | 128.1616 | 124.7059 | 123.4821
237.8479 | 76.4464 | 589.1031 | 51.7531 | 128.2831 | 124.9765 | 123.7358
238.8479 | 76.5936 | 593.4761 | 51.8748 | 128.1114 | 125.2202 | 123.8618
239.8479 | 76.8837 | 588.7034 | 51.874 | 127.8791 | 125.2718 | 124.0168
240.8479 | 76.9174 | 583.2873 | 52.0975 | 127.8813 | 125.2482 | 124.2751
241.8479 | 77.1068 | 569.293 | 52.4047 | 128.1592 | 125.2623 | 124.9079
242.8479 | 77.2913 | 571.4468 | 52.7079 | 128.1194 | 125.1229 | 125.1352
243.8479 | 77.5342 | 566.1828 | 52.8458 | 127.9389 | 125.2403 | 126.0643
244.8479 | 77.5312 | 558.5293 | 53.0587 | 127.9308 | 125.2661 | 126.324
245.8479 | 77.4225 | 544.0251 | 53.0974 | 127.7622 | 125.2143 | 126.6223
246.8479 | 77.5488 | 550.3803 | 53.2464 | 127.5129 | 125.4991 | 126.7297
247.8479 | 77.7328 | 555.1974 | 53.2915 | 127.4238 | 125.7837 | 127.0224
248.8479 | 77.8126 | 560.7077 | 53.2203 | 128.0482 | 126.0026 | 127.3963
249.8479 | 77.8544 | 558.6734 | 53.3707 | 128.2139 | 126.06 | 127.9748
250.8479 | 77.9475 | 568.701 | 53.5105 | 128.1565 | 125.8971 | 128.2823
251.8479 | 77.9211 | 553.4141 | 53.5165 | 128.4189 | 126.0265 | 128.1312
252.8479 | 77.9743 | 577.8581 | 53.6496 | 128.2057 | 126.141 | 128.1791
253.8479 | 77.9106 | 573.118 | 53.7935 | 127.9649 | 126.0974 | 127.9172
254.8479 | 77.7926 | 567.8665 | 53.963 | 128.0819 | 126.0065 | 128.188
255.8479 | 77.6138 | 589.3282 | 54.1751 | 128.3607 | 126.2368 | 128.3787
256.8479 | 77.7625 | 605.1957 | 54.4396 | 128.467 | 126.5534 | 128.7181
257.8479 | 77.8146 | 605.4896 | 54.5589 | 128.5974 | 126.5551 | 128.6264
258.8479 | 77.5902 | 603.5744 | 54.7377 | 128.6307 | 126.458 | 129.7044
259.8479 | 77.6985 | 600.3667 | 54.8327 | 128.7105 | 126.5781 | 129.8928
260.8479 | 77.5331 | 607.2618 | 55.0146 | 128.9136 | 126.8975 | 130.0987
261.8479 | 77.6987 | 619.0041 | 55.1161 | 129.1922 | 127.2175 | 129.7793
262.8479 | 77.6517 | 605.9731 | 55.1126 | 129.3924 | 127.1318 | 129.6245
263.8479 | 77.5615 | 595.9715 | 55.253 | 129.4677 | 127.011 | 129.7008
264.8479 | 77.8542 | 584.4744 | 55.4371 | 129.5925 | 127.1909 | 129.4901
265.8479 | 77.9587 | 591.1706 | 55.4981 | 129.5416 | 127.455 | 129.397
266.8479 | 78.0548 | 585.3444 | 55.4919 | 129.5404 | 127.2494 | 129.5098
267.8479 | 78.0087 | 586.4024 | 55.3519 | 129.3358 | 127.2546 | 129.469
268.8479 | 77.829 | 593.7051 | 55.2056 | 129.8481 | 127.4552 | 129.341
269.8479 | 77.7781 | 609.6135 | 55.5237 | 129.8284 | 127.4213 | 129.3058
270.8479 | 77.7681 | 598.2315 | 55.7646 | 129.7654 | 127.544 | 129.4866
271.8479 | 77.9837 | 614.8186 | 56.0025 | 129.5791 | 127.6093 | 129.9076
272.8479 | 78.1422 | 632.9897 | 56.2039 | 129.4556 | 127.9029 | 130.1513
273.8479 | 78.269 | 641.9065 | 56.1369 | 129.5737 | 128.1171 | 129.9858
274.8479 | 78.2351 | 673.5118 | 56.0782 | 129.8066 | 128.2767 | 129.9987
275.8479 | 78.4471 | 683.1095 | 55.9891 | 130.2027 | 128.2291 | 130.1014
276.8479 | 78.5957 | 682.8583 | 55.9451 | 130.4232 | 128.6048 | 130.2935
277.8479 | 78.5479 | 703.9934 | 55.8853 | 130.608 | 128.8003 | 130.0249
278.8479 | 78.753 | 709.6289 | 55.8008 | 130.9318 | 128.8563 | 130.1517
279.8479 | 78.9316 | 701.7535 | 55.9194 | 131.373 | 128.9085 | 129.9937
280.8479 | 79.0435 | 704.1757 | 55.9004 | 131.5552 | 129.3137 | 130.3223
281.8479 | 79.1093 | 700.7698 | 55.8345 | 131.6809 | 129.4856 | 130.599
282.8479 | 79.344 | 697.3235 | 55.7939 | 131.7429 | 129.7762 | 130.5304
283.8479 | 79.5932 | 699.2715 | 55.8872 | 131.658 | 129.833 | 130.9942
284.8479 | 79.6927 | 694.857 | 56.4547 | 131.7298 | 129.9601 | 130.7317
285.8479 | 80.0354 | 700.0442 | 56.6322 | 132.065 | 129.9051 | 130.7931
286.8479 | 80.234 | 707.1231 | 56.5319 | 131.9003 | 130.0042 | 131.0338
287.8479 | 80.4143 | 702.4462 | 56.6531 | 131.8295 | 129.7585 | 131.0961
288.8479 | 80.5002 | 698.6783 | 56.9014 | 132.0384 | 129.5861 | 131.4471
289.8479 | 80.6461 | 705.3938 | 57.1514 | 132.0798 | 129.6931 | 132.5107
290.8479 | 80.7876 | 702.492 | 57.5528 | 131.9676 | 129.7658 | 132.6291
291.8479 | 80.9311 | 697.852 | 57.7442 | 131.8847 | 129.8305 | 132.9503
292.8479 | 81.0492 | 694.9413 | 57.845 | 132.1956 | 130.3167 | 132.9966
293.8479 | 81.0422 | 697.9464 | 58.0573 | 132.7956 | 130.8166 | 133.2396
294.8479 | 81.2074 | 697.8789 | 58.1659 | 132.9374 | 130.6234 | 133.0034
295.8479 | 80.9219 | 705.8895 | 58.3672 | 132.967 | 130.5689 | 132.8683
296.8479 | 80.9889 | 714.2817 | 58.5675 | 133.2221 | 130.6846 | 132.6307
297.8479 | 80.8164 | 714.2654 | 58.5564 | 133.089 | 131.0906 | 132.8048
298.8479 | 80.6846 | 712.9332 | 58.6024 | 133.2267 | 130.8607 | 132.7379
299.8479 | 80.8097 | 723.4112 | 58.8693 | 133.4763 | 130.6741 | 132.6623
300.8479 | 81.0124 | 725.225 | 58.9388 | 133.6748 | 130.8196 | 132.5272
301.8479 | 81.1941 | 723.8723 | 59.356 | 134.1117 | 130.8695 | 132.3541
302.8479 | 81.2114 | 719.6146 | 59.4138 | 134.3243 | 130.817 | 132.9191
303.8479 | 81.0927 | 723.2903 | 59.6348 | 134.3272 | 131.0437 | 133.0512
304.8479 | 81.5532 | 728.3159 | 59.7229 | 134.3903 | 131.6209 | 133.3191
305.8479 | 81.6112 | 708.1466 | 59.765 | 134.8331 | 131.9708 | 133.3771
306.8479 | 81.551 | 712.3391 | 59.978 | 134.8904 | 132.2118 | 133.3648
307.8479 | 81.7281 | 714.91 | 60.229 | 135.2279 | 132.5805 | 133.3418
308.8479 | 82.0792 | 701.6848 | 60.5535 | 135.4408 | 132.9505 | 133.7041
309.8479 | 82.1965 | 719.114 | 60.6533 | 135.6682 | 132.8395 | 133.8512
310.8479 | 82.3308 | 718.679 | 60.9308 | 135.5406 | 132.7557 | 133.8138
311.8479 | 82.5525 | 720.5445 | 61.0814 | 135.397 | 132.6349 | 134.4597
312.8479 | 82.5351 | 718.2923 | 60.9861 | 135.2669 | 132.7588 | 134.4534
313.8479 | 82.7448 | 703.6896 | 60.8263 | 135.2863 | 132.8287 | 134.4709
314.8479 | 83.1605 | 715.2463 | 60.7671 | 135.1551 | 133.0852 | 134.88
315.8479 | 83.2548 | 730.6309 | 61.0389 | 135.1679 | 133.3226 | 134.9083
316.8479 | 83.3846 | 671.3464 | 61.2379 | 135.059 | 133.4664 | 134.7066
317.8479 | 83.54 | 755.8549 | 61.1619 | 135.1463 | 133.7616 | 134.5259
318.8479 | 83.5832 | 760.8964 | 61.2475 | 135.4066 | 134.0597 | 134.7752
319.8479 | 83.6571 | 767.1092 | 61.497 | 135.6708 | 134.5443 | 135.0103
320.8479 | 83.8419 | 780.1697 | 61.3995 | 135.6315 | 134.9167 | 135.1466
321.8479 | 83.736 | 783.0736 | 61.5289 | 135.871 | 135.0023 | 135.0815
322.8479 | 83.6954 | 787.5858 | 61.7018 | 135.8176 | 135.0994 | 135.4584
323.8479 | 83.711 | 799.8358 | 61.7683 | 136.0616 | 135.4381 | 135.7642
324.8479 | 83.9167 | 772.0281 | 61.9878 | 136.0557 | 135.9018 | 135.898
325.8479 | 83.9075 | 785.2488 | 62.01 | 136.6419 | 136.2733 | 136.1635
326.8479 | 84.0579 | 785.8895 | 62.1597 | 137.1789 | 136.1687 | 136.0284
327.8479 | 84.0236 | 796.7062 | 62.251 | 137.427 | 136.1611 | 136.0076
328.8479 | 84.4383 | 788.7962 | 62.4539 | 137.6492 | 135.8972 | 136.1254
329.8479 | 84.4551 | 782.9894 | 62.6987 | 137.706 | 135.8083 | 136.5964
330.8479 | 84.6963 | 800.9889 | 63.0629 | 137.4473 | 135.9105 | 136.4349
331.8479 | 84.8323 | 797.6887 | 63.1584 | 137.6481 | 136.1571 | 137.0782
332.8479 | 84.8546 | 785.0144 | 63.2398 | 137.9925 | 136.1267 | 137.4694
333.8479 | 84.5937 | 783.9056 | 63.3452 | 138.2071 | 136.1079 | 137.5594
334.8479 | 84.7594 | 789.8103 | 63.2195 | 138.5507 | 136.4045 | 137.8418
335.8479 | 84.8938 | 420.4721 | 63.0273 | 138.7149 | 136.539 | 138.3188
336.8479 | 85.0474 | 159.3102 | 63.0492 | 138.7353 | 136.7491 | 138.4553
337.8479 | 87.379 | 651.1855 | 63.0454 | 138.736 | 137.1485 | 138.5553
338.8479 | 86.7358 | 775.9779 | 63.1596 | 139.0981 | 137.4393 | 138.512
339.8479 | 86.743 | 344.4306 | 63.1304 | 139.4081 | 137.5022 | 138.651
340.8479 | 86.5559 | 50.1405 | 63.3687 | 139.799 | 137.355 | 138.8566
341.8479 | 86.4352 | 87.5893 | 63.4661 | 140.2537 | 137.6589 | 139.1889
342.8479 | 86.3676 | 455.6598 | 63.3728 | 140.376 | 137.8467 | 139.3247
343.8479 | 86.4128 | 52.5462 | 63.3166 | 140.3423 | 137.5919 | 139.1709
344.8479 | 86.5254 | 613.022 | 63.448 | 140.1962 | 137.4328 | 139.7536
345.8479 | 86.3913 | 50.6161 | 63.7351 | 140.4289 | 137.5482 | 139.853
346.8479 | 86.3994 | 739.6281 | 64.0406 | 140.7759 | 137.8458 | 140.6223
347.8479 | 86.6749 | 183.2833 | 64.1513 | 140.7863 | 138.1674 | 140.9612
348.8479 | 86.8894 | 734.4734 | 64.327 | 140.9306 | 138.1442 | 141.0562
349.8479 | 86.8384 | 750.9866 | 64.5086 | 141.0074 | 138.0582 | 141.0827
350.8479 | 86.77 | 735.1826 | 64.559 | 140.9966 | 138.0877 | 140.8701
351.8479 | 86.9301 | 731.6145 | 64.7036 | 141.1725 | 138.2654 | 140.723
352.8479 | 86.946 | 719.1246 | 64.3615 | 141.2285 | 138.2968 | 140.3741
353.8479 | 87.2831 | 713.4637 | 64.3042 | 141.251 | 138.0238 | 140.145
354.8479 | 87.1707 | 716.0354 | 63.9699 | 140.9962 | 138.2404 | 140.1658
355.8479 | 87.0617 | 703.7268 | 63.7964 | 140.9967 | 138.1311 | 140.7692
356.8479 | 86.7549 | 701.5259 | 63.8028 | 141.1927 | 137.9928 | 141.1
357.8479 | 86.7284 | 703.1466 | 63.7318 | 141.3031 | 137.943 | 140.7507
358.8479 | 86.7809 | 698.0854 | 63.585 | 141.3051 | 138.0668 | 140.4075
359.8479 | 86.7064 | 699.0849 | 63.7203 | 141.6587 | 138.1536 | 140.2315
360.8479 | 86.7609 | 699.688 | 63.5297 | 141.488 | 138.0298 | 140.1547
361.8479 | 87.0989 | 701.8481 | 63.7297 | 141.6861 | 138.0415 | 139.8713
362.8479 | 87.0376 | 694.9487 | 63.8526 | 142.0155 | 138.2534 | 139.6336
363.8479 | 87.0167 | 703.9408 | 64.2165 | 142.2232 | 138.4758 | 139.7385
364.8479 | 86.983 | 706.3554 | 64.1137 | 142.1206 | 138.8552 | 140.0257
365.8479 | 86.9761 | 693.6736 | 64.3654 | 142.146 | 139.0241 | 139.8837
366.8479 | 86.9097 | 682.7745 | 64.3695 | 142.0679 | 138.8825 | 140.1513
367.8479 | 86.9553 | 681.8568 | 64.4635 | 141.84 | 138.8937 | 140.419
368.8479 | 86.7616 | 699.6673 | 65.0585 | 141.8969 | 139.037 | 140.6991
369.8479 | 86.8256 | 701.0006 | 65.3862 | 142.1384 | 138.75 | 140.6708
370.8479 | 86.9181 | 693.2971 | 65.5506 | 142.3524 | 138.7179 | 140.8115
371.8479 | 87.0431 | 690.9745 | 65.4764 | 142.638 | 139.1532 | 140.9308
372.8479 | 87.3268 | 694.6566 | 65.2185 | 142.7492 | 139.1431 | 140.868
373.8479 | 87.7174 | 687.2995 | 65.0054 | 142.7525 | 139.2697 | 141.2732
374.8479 | 87.8259 | 677.8889 | 64.9387 | 143.0766 | 139.2656 | 141.6461
375.8479 | 87.7562 | 669.2099 | 65.1992 | 143.5368 | 139.1417 | 141.5202
376.8479 | 87.7166 | 660.6955 | 65.4497 | 143.5396 | 139.3219 | 141.8674
377.8479 | 87.653 | 669.0383 | 65.7625 | 143.8164 | 139.4847 | 141.8357
378.8479 | 87.4287 | 657.5759 | 66.107 | 143.8425 | 139.2671 | 142.123
379.8479 | 87.5867 | 651.3634 | 66.3069 | 143.708 | 139.5466 | 142.5484
380.8479 | 87.4011 | 643.8911 | 66.4796 | 143.7923 | 139.6333 | 143.1303
381.8479 | 87.4661 | 637.6563 | 66.7155 | 143.658 | 139.651 | 143.3601
382.8479 | 87.5104 | 645.236 | 66.6275 | 143.5162 | 139.5496 | 143.5661
383.8479 | 87.8395 | 635.1945 | 66.9092 | 143.349 | 139.8057 | 143.4512
384.8479 | 88.0555 | 636.4575 | 67.0948 | 144.3689 | 140.1959 | 143.7348
385.8479 | 88.0045 | 629.0897 | 67.2337 | 144.5047 | 140.3435 | 143.7081
386.8479 | 87.9075 | 621.829 | 66.8249 | 144.7267 | 140.4735 | 143.7225
387.8479 | 87.9864 | 634.6575 | 66.6218 | 145.0015 | 140.3654 | 143.9761
388.8479 | 88.2371 | 649.4601 | 66.411 | 145.2785 | 140.4761 | 144.1312
389.8479 | 88.1607 | 647.6159 | 66.3241 | 145.4453 | 140.5336 | 144.0323
390.8479 | 88.1991 | 651.0042 | 66.6932 | 145.2208 | 140.569 | 144.0915
391.8479 | 88.3977 | 641.1914 | 66.9351 | 145.1545 | 140.6222 | 144.0097
392.8479 | 88.3356 | 639.2669 | 67.0879 | 145.1832 | 140.261 | 143.8586
393.8479 | 88.2558 | 626.394 | 67.0473 | 145.3008 | 140.4923 | 144.2423
394.8479 | 88.2016 | 617.8626 | 67.012 | 145.6617 | 140.7426 | 144.3988
395.8479 | 87.8602 | 618.2134 | 66.8011 | 145.7466 | 140.3125 | 144.9621
396.8479 | 88.1521 | 604.217 | 66.5119 | 145.5537 | 140.1281 | 145.6928
397.8479 | 87.8261 | 611.5087 | 66.4127 | 145.4876 | 140.3109 | 145.7872
398.8479 | 87.5118 | 613.3552 | 66.3576 | 145.4692 | 140.4855 | 145.6532
399.8479 | 87.343 | 610.6768 | 66.3527 | 145.3452 | 140.3017 | 145.5163
400.8479 | 86.9387 | 626.6339 | 66.6128 | 145.1057 | 140.1118 | 145.564
401.8479 | 86.8924 | 629.8965 | 66.6666 | 144.9879 | 139.9476 | 145.7428
402.8479 | 86.7369 | 620.276 | 66.4956 | 145.0093 | 140.2809 | 145.7188
403.8479 | 86.6557 | 622.3762 | 66.7938 | 145.1594 | 140.5095 | 145.5771
404.8479 | 86.4976 | 629.4175 | 66.7886 | 144.921 | 140.8475 | 145.3611
405.8479 | 86.2569 | 621.3645 | 66.7763 | 144.7729 | 140.9908 | 145.6219
406.8479 | 85.9381 | 610.4922 | 66.6534 | 144.9549 | 140.9604 | 145.7491
407.8479 | 85.7489 | 607.399 | 66.8345 | 144.9763 | 140.5836 | 145.6835
408.8479 | 85.8111 | 619.0906 | 67.1132 | 145.1839 | 140.428 | 145.8525
409.8479 | 85.9085 | 610.9815 | 67.4398 | 145.1449 | 140.7651 | 145.9469
410.8479 | 85.8986 | 615.6891 | 67.7506 | 145.113 | 140.6433 | 146.1759
411.8479 | 85.9194 | 603.2831 | 67.7512 | 145.0015 | 140.7611 | 146.1167
412.8479 | 86.08 | 602.0604 | 68.1016 | 145.1679 | 140.7255 | 146.5593
413.8479 | 86.233 | 608.456 | 68.4156 | 145.318 | 140.866 | 146.477
414.8479 | 86.0925 | 591.3288 | 68.3096 | 145.4704 | 140.965 | 146.7382
415.8479 | 86.2119 | 598.8503 | 68.0912 | 145.723 | 141.0567 | 146.7518
416.8479 | 86.3238 | 612.3189 | 68.0346 | 145.7245 | 141.4311 | 146.8202
417.8479 | 86.6251 | 599.035 | 68.1538 | 145.6383 | 141.2902 | 147.0599
418.8479 | 86.6547 | 592.9672 | 68.2951 | 145.6455 | 141.1475 | 146.9294
419.8479 | 86.6107 | 582.4422 | 67.8045 | 145.6252 | 141.1549 | 146.9068
420.8479 | 86.8179 | 578.9712 | 67.9068 | 145.9571 | 141.4391 | 147.0615
421.8479 | 86.7132 | 578.9066 | 68.1125 | 145.9868 | 141.7767 | 147.3602
422.8479 | 86.8114 | 576.4223 | 68.2282 | 145.7605 | 142.0141 | 147.5584
423.8479 | 86.8157 | 561.1605 | 68.4693 | 145.7353 | 141.9944 | 147.5385
424.8479 | 86.7583 | 589.9988 | 68.614 | 145.6878 | 142.0645 | 147.7855
425.8479 | 86.831 | 611.149 | 68.7806 | 146.2362 | 142.2054 | 147.6553
426.8479 | 87.0753 | 588.572 | 68.8423 | 146.2844 | 142.4153 | 147.4455
427.8479 | 87.3084 | 593.5163 | 68.8057 | 146.0783 | 142.4982 | 147.2689
428.8479 | 87.3457 | 593.8938 | 68.6174 | 146.0748 | 142.6426 | 147.4232
429.8479 | 87.5313 | 612.8853 | 68.8371 | 146.2516 | 143.0632 | 147.1397
430.8479 | 87.7041 | 615.5462 | 69.1201 | 146.76 | 143.0172 | 147.1509
431.8479 | 87.8327 | 617.7668 | 69.3938 | 147.0395 | 142.7847 | 146.8168
432.8479 | 87.8372 | 621.2734 | 69.0769 | 147.1196 | 142.7308 | 146.8313
433.8479 | 87.6945 | 615.6438 | 69.3194 | 147.4834 | 142.517 | 146.9526
434.8479 | 87.7677 | 607.0823 | 69.4195 | 148.1945 | 142.8949 | 146.6891
435.8479 | 87.7245 | 621.5732 | 69.1907 | 148.4251 | 143.3542 | 147.3054
436.8479 | 87.6905 | 620.8001 | 68.907 | 148.2283 | 143.5294 | 147.8858
437.8479 | 87.7442 | 612.5117 | 68.8605 | 148.2079 | 143.6945 | 148.6021
438.8479 | 87.9062 | 616.3212 | 68.9517 | 148.0493 | 143.4998 | 148.9071
439.8479 | 87.551 | 631.7363 | 68.9796 | 147.7695 | 143.3696 | 149.4211
440.8479 | 87.735 | 628.541 | 69.235 | 147.4243 | 143.4302 | 149.8172
441.8479 | 87.5261 | 626.4139 | 69.5002 | 147.1814 | 143.6046 | 149.6779
442.8479 | 87.5409 | 632.5505 | 69.3583 | 147.0092 | 143.9793 | 149.7251
443.8479 | 87.4853 | 619.8665 | 69.2217 | 147.3274 | 144.2717 | 149.5235
444.8479 | 87.7427 | 619.5823 | 69.281 | 147.5428 | 143.9767 | 149.4603
445.8479 | 88.0076 | 615.9186 | 69.3069 | 147.4229 | 144.0099 | 149.1984
446.8479 | 88.0286 | 603.1647 | 69.1896 | 147.4799 | 144.0261 | 149.2085
447.8479 | 88.4366 | 591.286 | 69.5043 | 147.3307 | 144.1193 | 149.4922
448.8479 | 88.6695 | 586.3058 | 69.5391 | 147.2405 | 144.107 | 149.8959
449.8479 | 88.6029 | 591.4477 | 69.333 | 147.1882 | 144.081 | 150.192
450.8479 | 88.5785 | 600.0051 | 68.9158 | 147.0489 | 144.2781 | 149.909
451.8479 | 88.5709 | 589.6189 | 68.8484 | 146.9171 | 144.1949 | 149.9753
452.8479 | 88.7504 | 586.9016 | 69.0353 | 146.7764 | 144.074 | 149.7935
453.8479 | 88.6438 | 604.3 | 69.1925 | 146.7944 | 144.1555 | 149.7939
454.8479 | 88.73 | 593.0732 | 69.1841 | 146.915 | 144.3712 | 150.0819
455.8479 | 88.7508 | 610.4394 | 69.4641 | 147.1404 | 144.4926 | 150.2353
456.8479 | 88.8324 | 617.0689 | 69.6506 | 147.093 | 144.6137 | 150.4343
457.8479 | 88.7328 | 596.2942 | 69.6557 | 146.8475 | 144.6998 | 150.5254
458.8479 | 88.7342 | 604.9679 | 69.7085 | 146.7815 | 144.8487 | 150.3615
459.8479 | 88.9632 | 618.7064 | 69.8208 | 146.7907 | 144.5654 | 150.7298
460.8479 | 89.2845 | 614.068 | 70.1058 | 146.6998 | 144.6208 | 150.7548
461.8479 | 89.9743 | 631.1403 | 70.152 | 146.7808 | 144.5113 | 151.1281
462.8479 | 90.6408 | 629.96 | 70.3001 | 147.0073 | 144.4813 | 152.258
463.8479 | 91.3188 | 641.4207 | 70.4635 | 147.1674 | 144.8457 | 153.4923
464.8479 | 91.7262 | 655.1785 | 70.4042 | 147.9051 | 145.0887 | 154.4531
465.8479 | 92.3564 | 669.2883 | 70.9629 | 148.2887 | 145.4217 | 155.2035
466.8479 | 92.9625 | 674.5167 | 71.2852 | 148.4121 | 145.7482 | 155.5462
467.8479 | 93.6752 | 664.8272 | 71.6436 | 148.4022 | 146.3378 | 155.798
468.8479 | 94.3786 | 664.0826 | 72.2626 | 149.3875 | 147.0247 | 155.9416
469.8479 | 94.9569 | 675.2451 | 72.4566 | 149.9354 | 147.5574 | 157.0366
470.8479 | 95.6767 | 694.8839 | 72.7686 | 150.2232 | 148.2614 | 158.0425
471.8479 | 96.0595 | 707.02 | 73.07 | 150.9308 | 149.1142 | 159.1194
472.8479 | 96.7747 | 724.324 | 73.439 | 151.947 | 149.6385 | 159.2582
473.8479 | 97.1602 | 702.2662 | 73.9424 | 152.6145 | 150.4072 | 160.7242
474.8479 | 97.5746 | 716.4572 | 74.3568 | 153.079 | 151.2367 | 162.5343
475.8479 | 98.5052 | 715.3633 | 74.7455 | 153.605 | 152.1595 | 162.9894
476.8479 | 98.6892 | 712.0387 | 75.1441 | 153.9802 | 152.8585 | 163.4503
477.8479 | 99.187 | 709.505 | 75.3126 | 154.7788 | 154.0699 | 163.9105
478.8479 | 99.7486 | 705.2423 | 75.6413 | 155.9597 | 155.1915 | 164.3016
479.8479 | 100.2217 | 713.8443 | 75.6951 | 156.9629 | 155.7274 | 164.7632
480.8479 | 100.6786 | 710.912 | 75.6046 | 157.6086 | 156.1944 | 165.6814
481.8479 | 101.2716 | 715.1398 | 75.5231 | 158.4863 | 156.9933 | 166.6013
482.8479 | 101.3955 | 703.9933 | 75.8487 | 158.7843 | 158.4542 | 167.5876
483.8479 | 101.7526 | 690.7241 | 75.9361 | 159.4262 | 159.6538 | 168.2845
484.8479 | 102.0621 | 692.1654 | 76.1852 | 160.377 | 160.9641 | 169.3482
485.8479 | 102.6992 | 691.5915 | 76.2458 | 161.2177 | 161.8205 | 170.1189
486.8479 | 103.4578 | 690.2162 | 76.6131 | 162.2087 | 162.3118 | 171.4477
487.8479 | 103.6833 | 689.0772 | 76.5238 | 163.704 | 163.0884 | 171.9928
488.8479 | 104.4188 | 689.9803 | 76.7755 | 164.8208 | 164.072 | 173.0078
489.8479 | 105.0697 | 691.9984 | 76.9645 | 165.6754 | 165.0474 | 173.8052
490.8479 | 105.7722 | 684.7011 | 76.8629 | 166.3121 | 165.8642 | 174.141
491.8479 | 106.5992 | 699.4175 | 76.7356 | 167.3178 | 166.4372 | 174.5889
492.8479 | 106.9507 | 693.7282 | 76.881 | 168.419 | 167.5788 | 174.9268
493.8479 | 107.4586 | 687.6983 | 77.0248 | 169.5789 | 168.4997 | 175.4687
494.8479 | 108.0663 | 698.5007 | 77.3252 | 170.8786 | 169.823 | 176.2874
495.8479 | 108.6249 | 687.8395 | 77.371 | 172.8428 | 171.4523 | 177.1709
496.8479 | 109.1017 | 692.1221 | 77.1067 | 174.0062 | 172.5755 | 178.2362
497.8479 | 109.6947 | 685.4938 | 77.1626 | 175.1126 | 173.3821 | 178.7085
498.8479 | 110.1098 | 675.53 | 77.2503 | 177.1883 | 174.108 | 179.1534
499.8479 | 110.4742 | 686.5328 | 77.597 | 177.906 | 175.0388 | 179.8641
500.8479 | 110.8374 | 693.5187 | 77.8327 | 178.5974 | 175.9555 | 181.3436
501.8479 | 110.9261 | 688.0306 | 78.2744 | 179.6987 | 177.4647 | 181.8227
502.8479 | 111.0326 | 701.5588 | 78.6165 | 180.434 | 178.967 | 182.691
503.8479 | 111.4326 | 708.4287 | 79.0345 | 181.7948 | 179.3979 | 184.2513
504.8479 | 111.769 | 693.2134 | 78.9422 | 182.6454 | 180.2785 | 184.3712
505.8479 | 112.0042 | 692.7571 | 78.9252 | 184.3231 | 181.6986 | 184.1731
506.8479 | 112.3445 | 704.7957 | 79.0331 | 185.0029 | 183.1767 | 184.8715
507.8479 | 112.5617 | 699.5269 | 79.3505 | 185.6984 | 184.1693 | 187.604
508.8479 | 113.0635 | 696.735 | 79.3298 | 187.1753 | 185.2158 | 189.1749
509.8479 | 113.3251 | 680.3035 | 79.0809 | 187.747 | 186.5187 | 189.6647
510.8479 | 113.7081 | 676.3242 | 79.2066 | 188.9322 | 187.3078 | 189.447
511.8479 | 113.8813 | 670.8659 | 79.3315 | 189.6074 | 189.1207 | 190.2083
512.8479 | 114.3737 | 679.1568 | 79.4948 | 190.1523 | 189.7174 | 190.5541
513.8479 | 114.313 | 671.1623 | 80.1413 | 190.5564 | 190.8125 | 191.4759
514.8479 | 114.4345 | 678.8855 | 80.2892 | 192.36 | 191.6109 | 192.0386
515.8479 | 114.3601 | 680.9206 | 80.6175 | 192.2756 | 192.1142 | 193.5549
516.8479 | 114.4792 | 660.4248 | 80.7516 | 193.0132 | 193.222 | 193.6133
517.8479 | 114.7399 | 662.7783 | 81.1154 | 193.2817 | 194.2163 | 194.9157
518.8479 | 114.6668 | 654.359 | 81.1087 | 194.8652 | 195.1304 | 195.2574
519.8479 | 115.0706 | 646.694 | 81.276 | 195.1718 | 196.1234 | 195.527
520.8479 | 114.7407 | 646.13 | 81.1304 | 196.0325 | 197.3628 | 195.104
521.8479 | 114.7897 | 649.678 | 81.3679 | 197.386 | 198.6963 | 194.5516
522.8479 | 114.6682 | 662.1958 | 81.0874 | 198.9341 | 198.9537 | 196.4279
523.8479 | 115.1312 | 656.0374 | 80.9063 | 199.8725 | 200.0383 | 197.2958
524.8479 | 114.9312 | 653.282 | 80.8352 | 201.1744 | 200.7256 | 199.0131
525.8479 | 114.9381 | 643.4259 | 80.9156 | 201.437 | 201.3977 | 200.0501
526.8479 | 115.2052 | 643.2545 | 80.863 | 201.6145 | 202.2311 | 200.7222
527.8479 | 115.706 | 649.2597 | 81.2162 | 202.2318 | 203.3106 | 201.4421
528.8479 | 115.8853 | 639.1022 | 81.7975 | 203.5013 | 203.9641 | 201.8581
529.8479 | 116.0157 | 630.0438 | 81.7341 | 204.5789 | 204.5385 | 201.7073
530.8479 | 116.4002 | 627.9418 | 81.8182 | 204.5708 | 205.7329 | 202.1534
531.8479 | 116.7086 | 646.6036 | 81.6931 | 205.4551 | 206.4909 | 204.7999
532.8479 | 116.6746 | 644.4997 | 81.737 | 206.5387 | 207.0902 | 205.9605
533.8479 | 116.9819 | 652.1161 | 81.9223 | 206.5528 | 207.9352 | 206.6298
534.8479 | 117.4217 | 659.908 | 81.8014 | 206.8406 | 208.7622 | 207.25
535.8479 | 117.5517 | 647.1223 | 81.7526 | 206.8581 | 209.398 | 207.2987
536.8479 | 117.7781 | 638.8047 | 81.7189 | 207.2038 | 209.966 | 207.8087
537.8479 | 117.7154 | 638.3107 | 81.6822 | 207.8079 | 210.1897 | 208.161
538.8479 | 117.8261 | 627.3099 | 81.6786 | 207.9748 | 210.6179 | 208.3756
539.8479 | 117.8346 | 624.8022 | 81.8873 | 208.1787 | 211.0588 | 208.879
540.8479 | 117.7164 | 619.7401 | 81.7387 | 209.1672 | 212.0599 | 209.5394
541.8479 | 117.79 | 629.8593 | 81.7935 | 209.8688 | 212.2007 | 210.1522
542.8479 | 117.8339 | 607.7297 | 81.6814 | 210.8963 | 212.5075 | 210.8416
543.8479 | 117.783 | 606.4195 | 81.7322 | 212.116 | 213.2502 | 211.2225
544.8479 | 117.998 | 604.5835 | 81.6285 | 213.0867 | 214.0657 | 211.6165
545.8479 | 118.3595 | 606.0078 | 81.7078 | 213.5565 | 214.3585 | 212.9545
546.8479 | 118.3323 | 585.4799 | 81.8137 | 214.2228 | 214.2896 | 213.6803
547.8479 | 118.2516 | 582.0904 | 82.1025 | 214.9472 | 214.7513 | 214.7215
548.8479 | 118.1376 | 589.8852 | 81.9679 | 215.493 | 215.0906 | 216.2009
549.8479 | 117.6791 | 596.8466 | 81.9903 | 215.4661 | 215.5349 | 215.7874
550.8479 | 117.5434 | 599.6732 | 82.3073 | 215.8381 | 215.812 | 217.2923
551.8479 | 117.4655 | 593.7954 | 82.1613 | 215.3294 | 216.4623 | 217.4904
552.8479 | 117.2999 | 590.9889 | 82.2383 | 215.218 | 217.1073 | 219.2191
553.8479 | 117.176 | 598.5321 | 82.4994 | 215.419 | 217.6722 | 220.2627
554.8479 | 116.8717 | 618.5043 | 82.5962 | 216.0941 | 217.5002 | 221.0013
555.8479 | 117.01 | 616.1782 | 82.8122 | 216.3435 | 217.535 | 222.2443
556.8479 | 117.3283 | 618.4355 | 82.9883 | 216.4435 | 217.6321 | 223.611
557.8479 | 117.4487 | 628.9116 | 83.1027 | 216.5697 | 217.668 | 224.4215
558.8479 | 117.6266 | 634.0096 | 83.1522 | 216.3311 | 217.9301 | 224.0817
559.8479 | 117.8382 | 629.7165 | 83.4809 | 215.9998 | 218.6789 | 222.7656
560.8479 | 117.9828 | 637.1689 | 83.4297 | 215.7576 | 219.0074 | 221.5558
561.8479 | 118.1781 | 631.9782 | 83.8391 | 216.9313 | 219.57 | 220.3513
562.8479 | 118.4408 | 641.7844 | 83.8326 | 217.3012 | 219.712 | 220.622
563.8479 | 118.4317 | 653.9224 | 84.0876 | 217.8502 | 220.2257 | 220.5252
564.8479 | 118.4358 | 648.6934 | 83.9253 | 218.6309 | 220.6283 | 221.6782
565.8479 | 118.4716 | 658.6977 | 84.2106 | 218.8771 | 221.3556 | 221.7697
566.8479 | 118.6438 | 665.884 | 84.5876 | 218.8892 | 221.4167 | 220.917
567.8479 | 118.7756 | 664.1654 | 84.729 | 218.3979 | 221.752 | 220.384
568.8479 | 118.8845 | 677.1766 | 85.0431 | 218.0841 | 221.9258 | 220.9805
569.8479 | 119.2511 | 673.6893 | 85.2292 | 218.0716 | 221.9798 | 220.9882
570.8479 | 119.5543 | 677.4488 | 85.408 | 217.8623 | 221.9526 | 220.8522
571.8479 | 120.0192 | 683.0072 | 85.8021 | 217.6722 | 222.4822 | 220.5934
572.8479 | 120.0993 | 697.1532 | 85.7439 | 217.5341 | 222.6518 | 220.7853
573.8479 | 120.1539 | 695.1444 | 86.1081 | 217.2555 | 222.8377 | 220.4759
574.8479 | 120.0789 | 707.3502 | 86.151 | 217.9096 | 223.0359 | 220.2795
575.8479 | 120.3629 | 700.1377 | 86.1004 | 218.8337 | 223.3686 | 220.6394
576.8479 | 120.4817 | 696.5766 | 85.9903 | 218.6655 | 223.5987 | 220.1924
577.8479 | 120.5446 | 698.4088 | 85.8647 | 218.5678 | 223.5167 | 221.7866
578.8479 | 120.487 | 702.7444 | 86.0557 | 218.7735 | 223.8251 | 222.1036
579.8479 | 120.4727 | 711.0682 | 86.0566 | 219.3486 | 224.0933 | 222.0799
580.8479 | 120.3969 | 711.957 | 85.9737 | 219.5182 | 224.4205 | 222.1709
581.8479 | 120.6419 | 704.3456 | 86.0095 | 219.4902 | 224.5522 | 221.2847
582.8479 | 120.7651 | 710.173 | 86.2133 | 219.997 | 225.0118 | 221.3931
583.8479 | 121.3078 | 701.6484 | 86.4896 | 220.711 | 224.8169 | 220.9886
584.8479 | 121.6448 | 684.1588 | 86.7085 | 221.3115 | 224.5354 | 220.7274
585.8479 | 121.8758 | 670.9616 | 86.9057 | 221.1532 | 224.8619 | 220.9049
586.8479 | 122.0748 | 670.3217 | 86.9107 | 221.5061 | 225.0808 | 220.6957
587.8479 | 122.0048 | 653.1505 | 87.2748 | 221.9798 | 225.5326 | 220.2112
588.8479 | 121.9676 | 661.4001 | 87.4914 | 222.7215 | 226.1693 | 221.3031
589.8479 | 122.0912 | 672.7231 | 87.5158 | 223.3459 | 227.2704 | 221.8572
590.8479 | 122.2686 | 668.0831 | 87.7464 | 223.5971 | 228.0556 | 222.2371
591.8479 | 122.4047 | 675.6067 | 87.6617 | 223.3877 | 227.7867 | 222.165
592.8479 | 122.346 | 660.3767 | 87.733 | 223.5313 | 228.3959 | 222.1953
593.8479 | 122.4991 | 649.3842 | 87.9356 | 224.2133 | 228.8841 | 222.5756
594.8479 | 122.4259 | 659.688 | 87.9697 | 225.3014 | 228.8665 | 223.1723
595.8479 | 122.5816 | 677.1365 | 88.4035 | 226.5508 | 228.9059 | 223.3921
596.8479 | 123.0702 | 675.5398 | 88.7401 | 226.8368 | 229.4518 | 223.9543
597.8479 | 123.1166 | 675.7104 | 88.6299 | 227.5308 | 229.3511 | 224.1481
598.8479 | 123.286 | 665.8351 | 88.8434 | 227.4737 | 229.5738 | 224.5607
599.8479 | 123.2337 | 654.7015 | 88.7564 | 227.1921 | 230.0683 | 224.3599
600.8479 | 123.3812 | 642.2012 | 88.8816 | 227.516 | 231.0823 | 224.174
601.8479 | 123.6064 | 634.7845 | 89.2604 | 228.0477 | 231.7805 | 226.9829
602.8479 | 123.5788 | 627.8925 | 89.3603 | 228.4381 | 231.9788 | 227.3713
603.8479 | 123.5506 | 630.083 | 89.5227 | 228.3939 | 232.311 | 227.022
604.8479 | 123.6567 | 629.6832 | 89.5406 | 228.1592 | 232.2404 | 226.5608
605.8479 | 123.7247 | 633.561 | 89.748 | 228.8919 | 232.7903 | 227.0104
606.8479 | 124.0631 | 635.5564 | 90.0159 | 229.2748 | 233.2611 | 227.5306
607.8479 | 124.2862 | 633.195 | 90.5373 | 229.2905 | 233.187 | 228.1934
608.8479 | 124.4233 | 626.8951 | 90.7613 | 230.175 | 233.1259 | 229.4048
609.8479 | 124.6212 | 628.9145 | 90.9681 | 230.6815 | 233.4603 | 230.9637
610.8479 | 124.8632 | 614.6751 | 91.0496 | 230.3719 | 234.0966 | 232.1015
611.8479 | 124.7399 | 592.285 | 91.077 | 230.3611 | 234.868 | 233.3004
612.8479 | 125.0065 | 587.5283 | 91.3042 | 230.8488 | 235.3843 | 236.5218
613.8479 | 125.0519 | 571.738 | 91.281 | 230.7906 | 235.3791 | 237.1786
614.8479 | 125.0871 | 586.1211 | 91.6936 | 230.8312 | 235.8212 | 238.1766
615.8479 | 125.0476 | 587.8946 | 91.5353 | 230.8298 | 236.4876 | 238.4759
616.8479 | 125.3944 | 584.7459 | 91.7218 | 230.9601 | 236.8716 | 239.3657
617.8479 | 125.4379 | 588.7602 | 91.7082 | 231.2235 | 237.3939 | 240.2354
618.8479 | 125.5636 | 581.8085 | 91.8098 | 231.647 | 237.8677 | 239.7081
619.8479 | 125.7245 | 573.2442 | 92.2804 | 231.7598 | 238.1934 | 239.7617
620.8479 | 125.5853 | 560.027 | 92.4826 | 232.6077 | 237.904 | 240.018
621.8479 | 125.2666 | 574.3201 | 93.0647 | 233.3328 | 238.2368 | 241.1585
622.8479 | 125.0894 | 551.0839 | 93.1301 | 233.5256 | 239.8544 | 241.3608
623.8479 | 124.9223 | 544.4163 | 93.0241 | 233.9121 | 239.6826 | 241.7951
624.8479 | 125.0646 | 552.9643 | 93.4632 | 234.2022 | 239.3155 | 242.1589
625.8479 | 125.201 | 582.9476 | 93.8167 | 234.0499 | 238.1898 | 243.6568
626.8479 | 125.5343 | 585.6442 | 94.1251 | 234.9051 | 238.2109 | 243.9445
627.8479 | 126.0679 | 592.7192 | 94.3247 | 234.7422 | 237.6287 | 244.6556
628.8479 | 125.8616 | 592.2331 | 94.4894 | 235.3956 | 236.8896 | 244.3825
629.8479 | 125.6272 | 595.7285 | 94.7193 | 235.6838 | 232.3504 | 243.6125
630.8479 | 125.5532 | 604.7926 | 94.8566 | 235.6729 | 229.459 | 245.2162
631.8479 | 125.4555 | 578.888 | 94.9813 | 236.2999 | 226.8945 | 245.7109
632.8479 | 125.5701 | 566.4444 | 94.7888 | 236.8102 | 224.8479 | 245.6979
633.8479 | 125.6136 | 567.8795 | 95.0329 | 236.5678 | 222.9621 | 247.0625
634.8479 | 125.9377 | 578.2212 | 95.3502 | 237.4101 | 221.3658 | 248.0138
635.8479 | 125.8322 | 568.4709 | 95.2826 | 237.8503 | 220.265 | 247.7866
636.8479 | 125.8231 | 566.883 | 95.1818 | 237.7804 | 219.8099 | 247.1099
637.8479 | 125.9018 | 560.9199 | 95.3594 | 237.5166 | 219.0993 | 247.0558
638.8479 | 125.9602 | 568.591 | 95.7144 | 237.267 | 218.0489 | 247.9586
639.8479 | 126.3791 | 561.231 | 95.6637 | 237.5022 | 216.8387 | 247.7419
640.8479 | 126.5999 | 557.7563 | 95.5654 | 237.3009 | 215.9356 | 248.487
641.8635 | 126.7415 | 544.8978 | 95.9807 | 237.764 | 215.9988 | 248.2749
642.8479 | 127.0077 | 552.5141 | 96.3197 | 238.069 | 216.1824 | 247.6764
643.8479 | 127.295 | 552.257 | 96.5603 | 239.3872 | 215.9685 | 248.1468
644.8479 | 127.625 | 545.6819 | 96.6519 | 239.9452 | 215.6394 | 249.1673
645.8479 | 128.0794 | 553.4116 | 96.6974 | 241.3641 | 215.084 | 250.8294
646.8479 | 128.5087 | 583.3619 | 96.7102 | 241.4935 | 214.62 | 251.4325
647.8479 | 128.6784 | 578.3708 | 96.7475 | 241.5027 | 214.2074 | 251.5218
648.8479 | 128.6483 | 564.9104 | 96.6571 | 241.9533 | 214.325 | 252.1855
649.8479 | 128.4542 | 555.7895 | 96.7207 | 242.2736 | 214.2744 | 253.096
650.8479 | 128.4761 | 553.5256 | 96.8322 | 242.0659 | 213.9391 | 255.3546
651.8479 | 128.7079 | 554.0228 | 96.8578 | 242.121 | 213.8813 | 255.3345
652.8479 | 129.4238 | 552.5608 | 96.8376 | 242.7001 | 213.928 | 255.5949
653.8479 | 129.9533 | 563.7508 | 97.182 | 243.4791 | 214.0738 | 255.2855
654.8479 | 129.9029 | 552.7661 | 97.7012 | 242.9195 | 214.1587 | 256.596
655.8479 | 129.8115 | 544.0496 | 97.7721 | 243.0822 | 214.2895 | 256.4174
656.8479 | 129.6642 | 569.1323 | 97.8789 | 242.6274 | 214.3429 | 257.0708
657.8479 | 129.6258 | 549.7571 | 97.6691 | 242.5329 | 214.3102 | 258.0485
658.8479 | 129.7306 | 547.1343 | 98.1366 | 242.4618 | 214.155 | 258.4415
659.8479 | 129.5398 | 570.1144 | 98.2073 | 242.3506 | 214.2269 | 258.3087
660.8479 | 129.7876 | 581.1193 | 98.6404 | 242.3825 | 214.0283 | 258.9119
661.8479 | 130.4217 | 575.2319 | 99.3017 | 242.4914 | 213.6696 | 258.9799
662.8479 | 130.6522 | 579.121 | 99.5902 | 243.2954 | 213.3023 | 259.7882
663.8479 | 131.1347 | 584.8426 | 99.512 | 243.4484 | 213.1182 | 259.2223
664.8479 | 131.4679 | 571.07 | 99.6502 | 243.5913 | 213.1088 | 258.8851
665.8479 | 131.4251 | 556.5464 | 99.4898 | 243.5738 | 213.0243 | 258.6547
666.8479 | 131.6269 | 538.2806 | 99.6136 | 243.8771 | 212.9506 | 260.292
667.8479 | 131.5264 | 536.0632 | 99.7538 | 244.1696 | 212.6205 | 260.8816
668.8479 | 131.5914 | 543.5021 | 100.0769 | 244.6236 | 212.0969 | 261.4505
669.8479 | 131.7373 | 539.1706 | 100.3214 | 245.3713 | 211.5577 | 263.1037
670.8479 | 132.0283 | 541.4898 | 100.6165 | 245.4019 | 211.2636 | 264.0229
671.8479 | 132.1446 | 544.9485 | 100.7384 | 245.6511 | 211.0365 | 264.4944
672.8479 | 132.5306 | 545.2712 | 100.6762 | 245.5144 | 210.7197 | 263.7643
673.8479 | 132.8233 | 555.4897 | 100.7458 | 245.3454 | 210.4175 | 265.2716
674.8479 | 132.894 | 552.6394 | 100.689 | 245.6262 | 210.2169 | 264.8672
675.8479 | 133.0319 | 559.1303 | 100.7439 | 246.3456 | 209.7079 | 264.097
676.8479 | 133.3141 | 555.6256 | 101.0401 | 246.0857 | 209.1346 | 263.3607
677.8479 | 133.7716 | 554.4891 | 101.0771 | 246.1263 | 208.9155 | 263.5435
678.8479 | 133.9941 | 555.296 | 101.1254 | 245.4803 | 209.2868 | 264.4907
679.8479 | 134.147 | 579.5535 | 101.3359 | 245.5091 | 209.328 | 264.5602
680.8479 | 134.1921 | 583.4112 | 101.4134 | 245.1152 | 209.3497 | 264.3508
681.8479 | 134.052 | 572.7746 | 101.6353 | 243.6956 | 209.3074 | 265.4255
682.8479 | 133.8739 | 560.102 | 102.1564 | 240.9767 | 209.2675 | 265.8167
683.8479 | 134.1326 | 569.7519 | 102.3684 | 238.6067 | 209.0922 | 266.0156
684.8479 | 134.4294 | 588.0313 | 102.4906 | 235.475 | 208.8802 | 267.2004
685.8479 | 134.7277 | 571.224 | 102.8038 | 232.5302 | 208.6991 | 267.6647
686.8479 | 134.708 | 588.8358 | 102.9314 | 229.8471 | 208.7033 | 267.2509
687.8479 | 135.1649 | 607.1254 | 102.9065 | 227.499 | 208.7674 | 267.0254
688.8479 | 135.3462 | 632.2984 | 102.8938 | 225.4285 | 209.2047 | 266.2131
689.8479 | 135.653 | 642.9464 | 102.6609 | 223.2636 | 209.7603 | 264.9777
690.8479 | 135.6554 | 644.1809 | 102.5933 | 222.4496 | 210.0823 | 264.1694
691.8479 | 135.5961 | 624.2311 | 102.8224 | 221.3094 | 210.2411 | 263.6315
692.8479 | 135.5134 | 598.7085 | 102.8285 | 220.2849 | 210.7746 | 263.4722
693.8479 | 135.4054 | 580.1278 | 102.6359 | 218.8421 | 211.1628 | 263.8449
694.8479 | 135.0989 | 573.5993 | 102.8916 | 217.6448 | 211.5869 | 264.3409
695.8479 | 135.0858 | 557.518 | 102.9947 | 216.6673 | 211.0984 | 264.7356
696.8479 | 135.1142 | 570.3833 | 103.3702 | 215.5804 | 211.6291 | 264.9411
697.8479 | 135.3601 | 580.2853 | 103.5814 | 214.6306 | 212.5754 | 266.8307
698.8479 | 136.127 | 596.4252 | 103.9074 | 213.4704 | 213.5537 | 266.5348
699.8479 | 136.1407 | 590.0641 | 103.9462 | 212.9334 | 214.6191 | 266.708
700.8479 | 136.6142 | 602.1196 | 103.8622 | 214.0623 | 218.8127 | 267.1152
701.8479 | 137.1507 | 594.8469 | 103.8672 | 217.111 | 224.0039 | 266.562
702.8479 | 137.4207 | 596.1224 | 104.3163 | 220.178 | 227.9495 | 266.935
703.8479 | 137.6955 | 576.8063 | 104.4748 | 223.7681 | 231.2905 | 267.1326
704.8479 | 137.5878 | 580.2407 | 104.9028 | 226.8434 | 234.4743 | 267.1041
705.8479 | 137.8078 | 569.563 | 104.7413 | 229.4947 | 236.646 | 267.7656
706.8479 | 138.125 | 571.6576 | 104.8692 | 231.9726 | 238.4991 | 268.5913
707.8479 | 138.2855 | 576.1738 | 105.2398 | 234.2948 | 240.4089 | 268.2915
708.8479 | 138.3322 | 571.893 | 105.0739 | 235.9757 | 242.206 | 267.7194
709.8479 | 138.8319 | 573.9788 | 105.0937 | 237.3892 | 243.7879 | 267.3531
710.8479 | 139.2247 | 571.7005 | 105.0575 | 238.9811 | 245.0321 | 267.0471
711.8479 | 139.4006 | 573.5339 | 104.7964 | 240.6325 | 246.4755 | 267.2192
712.8479 | 139.4978 | 545.0401 | 104.7069 | 242.0629 | 247.7846 | 266.925
713.8479 | 139.942 | 533.885 | 104.7825 | 243.527 | 249.0766 | 266.6613
714.8479 | 139.7924 | 530.1935 | 104.7306 | 245.3163 | 250.413 | 266.4859
715.8479 | 139.8557 | 545.7618 | 105.2546 | 246.7308 | 251.1279 | 266.258
716.8479 | 139.9162 | 539.5637 | 105.4613 | 248.0377 | 251.8368 | 266.6104
717.8479 | 139.9275 | 539.5578 | 105.7668 | 249.9004 | 252.5214 | 267.4281
718.8479 | 139.9628 | 546.4908 | 105.7761 | 250.9853 | 253.564 | 267.7791
719.8479 | 140.1646 | 551.2872 | 105.6338 | 251.4892 | 254.5934 | 267.5394
720.8479 | 140.1472 | 562.9344 | 105.8732 | 251.8898 | 255.2913 | 267.4086
721.8479 | 140.1174 | 561.2052 | 106.252 | 252.4598 | 255.8911 | 267.2351
722.8479 | 140.0257 | 560.5072 | 106.3396 | 252.9944 | 256.2339 | 267.1524
723.8479 | 140.045 | 543.9329 | 106.2167 | 254.2172 | 256.6239 | 268.3669
724.8479 | 139.837 | 536.1419 | 106.3971 | 254.7779 | 256.9609 | 268.2823
725.8479 | 139.5124 | 544.0454 | 106.7657 | 255.0083 | 257.196 | 269.2326
726.8479 | 139.4849 | 536.8532 | 106.8641 | 255.1994 | 257.01 | 270.9176
727.8479 | 139.2269 | 545.2409 | 106.7622 | 255.8468 | 256.9959 | 271.9617
728.8479 | 139.2935 | 562.0536 | 106.8734 | 256.3173 | 256.9829 | 273.3022
729.8479 | 139.2421 | 562.0865 | 106.7808 | 256.5407 | 257.5683 | 274.4959
730.8479 | 139.7157 | 572.7101 | 106.6876 | 256.828 | 257.797 | 274.5078
731.8479 | 139.9427 | 544.3743 | 106.8387 | 257.1214 | 257.8353 | 274.0533
732.8479 | 139.9944 | 539.5208 | 107.1634 | 258.1054 | 257.4692 | 274.8723
733.8479 | 139.9423 | 523.9196 | 107.4683 | 258.6194 | 257.9513 | 274.2103
734.8479 | 140.3587 | 528.2148 | 107.3803 | 258.7319 | 258.5929 | 273.5127
735.8479 | 140.9159 | 519.4514 | 107.408 | 259.4851 | 258.4321 | 272.9404
736.8479 | 141.1619 | 536.546 | 107.3912 | 259.577 | 258.7668 | 272.8146
737.8479 | 141.5198 | 553.6375 | 107.9132 | 259.9705 | 258.9793 | 272.8032
738.8479 | 141.722 | 536.4307 | 108.4278 | 260.2324 | 259.5945 | 272.2076
739.8479 | 141.6877 | 526.7371 | 108.7802 | 260.671 | 260.0792 | 271.4606
740.8479 | 142.0605 | 518.6998 | 108.8609 | 260.6807 | 260.628 | 271.0718
741.8479 | 142.4999 | 535.6944 | 109.0453 | 261.1004 | 260.9366 | 272.3388
742.8479 | 142.504 | 529.8042 | 109.1346 | 261.0771 | 261.2527 | 273.4293
743.8479 | 142.517 | 535.4866 | 109.3485 | 261.2821 | 261.5272 | 274.6944
744.8479 | 142.6111 | 539.1489 | 109.2881 | 261.3777 | 262.277 | 275.2673
745.8479 | 142.5936 | 536.5828 | 109.4325 | 261.2904 | 262.7636 | 275.0523
746.8479 | 142.4471 | 532.0706 | 109.2285 | 261.2508 | 262.6813 | 275.7049
747.8479 | 142.3223 | 517.1608 | 109.3987 | 261.0246 | 262.6454 | 275.7111
748.8479 | 142.0261 | 543.3452 | 109.615 | 261.2114 | 262.5498 | 275.6057
749.8479 | 142.0266 | 553.7697 | 109.5059 | 261.1523 | 262.3361 | 275.3143
750.8479 | 142.0958 | 573.2513 | 109.4885 | 261.3678 | 262.304 | 274.3095
751.8479 | 141.8934 | 562.0895 | 109.4652 | 261.2493 | 262.3225 | 273.9673
752.8479 | 141.7753 | 560.1343 | 109.8347 | 260.9683 | 261.9865 | 273.5002
753.8479 | 141.7779 | 555.0722 | 110.2114 | 261.2129 | 262.1774 | 273.8287
754.8479 | 141.691 | 545.51 | 110.3984 | 261.3678 | 262.9102 | 273.9356
755.8479 | 141.4094 | 540.1396 | 110.4674 | 261.8167 | 263.3764 | 273.3774
756.8479 | 141.154 | 539.2233 | 110.7405 | 262.0635 | 263.3025 | 274.4578
757.8479 | 140.9312 | 552.3586 | 111.3053 | 261.8763 | 263.4013 | 274.25
758.8479 | 140.9802 | 541.2638 | 111.4581 | 261.6454 | 263.6654 | 273.9311
759.8479 | 141.0524 | 543.4037 | 111.2748 | 261.5787 | 263.7416 | 274.6282
760.8479 | 140.876 | 559.8012 | 111.2572 | 261.3306 | 263.706 | 273.9158
761.8479 | 140.5938 | 554.1618 | 111.6011 | 261.2434 | 263.7182 | 273.6419
762.8479 | 140.7877 | 560.1248 | 111.8509 | 260.983 | 264.0134 | 274.0051
763.8479 | 140.8622 | 574.9787 | 111.875 | 260.5763 | 264.1209 | 274.2863
764.8479 | 140.7229 | 579.3433 | 111.7385 | 260.8118 | 264.1907 | 274.1366
765.8479 | 140.5883 | 577.7749 | 111.7556 | 260.612 | 264.3804 | 274.8586
766.8479 | 140.6348 | 590.2169 | 111.9006 | 260.4815 | 264.5847 | 274.2009
767.8479 | 140.8826 | 584.8861 | 111.7649 | 260.2198 | 265.0773 | 274.7074
768.8479 | 141.1689 | 575.5901 | 111.9209 | 260.2831 | 265.1537 | 274.5668
769.8479 | 141.7542 | 570.3658 | 112.1537 | 260.561 | 265.4646 | 274.2074
770.8479 | 141.9189 | 554.4756 | 112.213 | 260.8007 | 265.4833 | 273.5205
771.8479 | 142.1257 | 550.7189 | 111.8626 | 261.413 | 264.7561 | 272.95
772.8479 | 142.3988 | 546.5454 | 112.0839 | 262.2297 | 264.6309 | 272.6966
773.8479 | 142.6658 | 540.3364 | 112.1298 | 262.1207 | 264.7164 | 272.9053
774.8479 | 142.6054 | 527.5498 | 112.5006 | 262.2567 | 265.2575 | 272.4969
775.8479 | 142.6703 | 552.6056 | 112.6653 | 262.2933 | 264.9396 | 272.7346
776.8479 | 142.8528 | 554.0025 | 112.7482 | 262.2258 | 264.7955 | 273.8812
777.8479 | 143.2139 | 562.5806 | 112.8078 | 261.8543 | 264.6846 | 274.3611
778.8479 | 143.2835 | 559.8684 | 113.1275 | 261.8757 | 264.7765 | 274.1039
779.8479 | 143.2516 | 537.9261 | 113.2626 | 261.8633 | 264.4397 | 274.0141
780.8479 | 143.2112 | 529.1691 | 113.3637 | 261.9457 | 264.5193 | 273.6098
781.8479 | 143.1041 | 533.459 | 113.3813 | 262.0959 | 264.436 | 274.5192
782.8479 | 143.0047 | 527.5667 | 113.1509 | 262.0329 | 264.6012 | 274.2484
783.8479 | 143.4551 | 532.7498 | 113.0714 | 261.841 | 265.0465 | 274.7194
784.8479 | 143.9281 | 522.4619 | 112.9448 | 261.4786 | 265.5605 | 274.7949
785.8479 | 143.8591 | 547.6013 | 112.705 | 261.2653 | 266.2746 | 274.3799
786.8479 | 143.4307 | 554.2814 | 113.089 | 261.3016 | 266.4397 | 274.2984
787.8479 | 143.6294 | 542.6755 | 112.8667 | 261.1585 | 266.6856 | 275.4026
788.8479 | 143.3964 | 535.0452 | 112.9224 | 261.2303 | 266.9758 | 275.3877
789.8479 | 143.1237 | 547.3729 | 112.5833 | 261.1794 | 266.6461 | 275.2607
790.8479 | 142.6596 | 545.3357 | 112.8943 | 261.2896 | 265.967 | 274.7269
791.8479 | 142.2021 | 541.2644 | 113.2155 | 261.4927 | 266.0691 | 274.3434
792.8479 | 142.4183 | 529.4127 | 113.2388 | 262.1995 | 266.7707 | 274.519
793.8479 | 142.2473 | 541.4632 | 113.8007 | 262.4078 | 266.7928 | 274.8582
794.8479 | 141.8831 | 542.3033 | 113.9455 | 262.3507 | 266.4866 | 274.7095
795.8479 | 141.9127 | 543.8231 | 114.4129 | 262.5705 | 266.7009 | 275.3258
796.8479 | 142.2366 | 533.7766 | 114.4069 | 262.1946 | 266.5391 | 275.9631
797.8479 | 142.5723 | 540.4467 | 114.3216 | 262.1445 | 266.5234 | 275.7129
798.8479 | 142.7512 | 543.808 | 114.2018 | 261.9523 | 266.6651 | 275.1899
799.8479 | 143.2059 | 549.7685 | 114.2541 | 261.8343 | 266.9323 | 274.6427
800.8479 | 143.4054 | 563.7324 | 114.4773 | 261.5368 | 266.7514 | 273.9705
801.8479 | 143.5986 | 577.1946 | 115.0363 | 261.671 | 266.8832 | 273.2306
802.8479 | 143.9708 | 592.6333 | 115.0922 | 261.7982 | 267.0353 | 272.8007
803.8479 | 144.4055 | 602.4028 | 114.6943 | 261.9559 | 267.2373 | 272.3073
804.8479 | 144.9187 | 617.7002 | 114.9345 | 261.9648 | 267.1907 | 272.2474
805.8479 | 145.3488 | 625.3702 | 115.1726 | 262.1718 | 267.5693 | 272.0969
806.8479 | 145.6841 | 626.1046 | 115.59 | 262.9085 | 267.4748 | 272.2876
807.8479 | 146.3591 | 618.4543 | 115.805 | 263.935 | 267.6369 | 272.7915
808.8479 | 146.8127 | 602.2684 | 116.0008 | 264.3216 | 267.6336 | 272.7793
809.8479 | 146.9318 | 601.8668 | 115.7631 | 264.8825 | 268.1603 | 273.7073
810.8479 | 147.3546 | 600.5805 | 116.2362 | 265.2658 | 268.6708 | 273.9257
811.8479 | 147.9748 | 602.374 | 116.8913 | 265.7339 | 268.8534 | 274.1074
812.8479 | 148.1617 | 606.5363 | 117.2762 | 266.1163 | 268.768 | 274.9907
813.8479 | 148.1516 | 588.6397 | 117.3253 | 265.9474 | 269.1413 | 275.8082
814.8479 | 148.3205 | 588.8146 | 117.4309 | 266.2376 | 269.8443 | 276.177
815.8479 | 148.2877 | 590.3669 | 117.4327 | 266.2877 | 269.9644 | 276.5294
816.8479 | 148.4403 | 602.0227 | 117.3737 | 266.3974 | 270.0902 | 276.473
817.8479 | 148.2934 | 595.3442 | 117.1973 | 266.9999 | 270.3495 | 276.516
818.8479 | 148.3593 | 596.1767 | 117.6777 | 267.2831 | 270.4079 | 276.1223
819.8479 | 148.1679 | 576.1221 | 117.6506 | 267.6759 | 270.5733 | 275.6852
820.8479 | 147.9583 | 573.0362 | 117.7372 | 268.1005 | 271.0526 | 275.5305
821.8479 | 147.8135 | 567.6527 | 117.6136 | 268.4787 | 271.6614 | 275.4867
822.8479 | 147.5941 | 564.4781 | 117.8054 | 268.9017 | 271.9955 | 275.5883
823.8479 | 147.48 | 560.3202 | 117.7297 | 268.8805 | 272.2447 | 277.2097
824.8479 | 147.2943 | 552.9479 | 117.9091 | 269.0832 | 272.3062 | 278.2613
825.8479 | 147.3789 | 548.9533 | 118.1037 | 269.0133 | 272.6745 | 279.2818
826.8479 | 147.1111 | 542.352 | 118.1306 | 269.3096 | 272.8955 | 280.5
827.8479 | 147.0821 | 534.7708 | 118.4668 | 269.4244 | 273.1401 | 281.8873
828.8479 | 146.9067 | 548.2279 | 118.7114 | 269.439 | 273.1907 | 282.6632
829.8479 | 147.1973 | 562.3416 | 118.5071 | 269.1731 | 273.3078 | 282.3303
830.8479 | 147.1904 | 549.9151 | 118.7696 | 268.7249 | 273.238 | 281.8865
831.8479 | 147.2886 | 553.5754 | 118.477 | 268.9471 | 272.8464 | 281.7137
832.8479 | 147.2989 | 549.3958 | 118.9829 | 268.9117 | 272.8222 | 281.7957
833.8479 | 147.232 | 556.1697 | 119.1223 | 268.884 | 273.3822 | 281.6912
834.8479 | 147.3554 | 552.2514 | 118.9076 | 268.5179 | 274.5559 | 281.3997
835.8479 | 147.3549 | 562.2447 | 119.4552 | 268.2644 | 275.0364 | 281.703
836.8479 | 147.2838 | 553.1588 | 120.0736 | 268.02 | 274.8259 | 281.5118
837.8479 | 146.9675 | 554.7337 | 120.55 | 267.8793 | 274.4753 | 281.2511
838.8479 | 147.0209 | 556.4437 | 120.2058 | 268.1545 | 273.9466 | 281.8929
839.8479 | 147.0847 | 545.4558 | 120.2106 | 268.5521 | 273.415 | 281.601
840.8479 | 147.0229 | 539.529 | 120.3102 | 268.6294 | 273.3331 | 282.3481
841.8479 | 147.1302 | 542.0847 | 120.4073 | 268.5222 | 273.0814 | 281.9917
842.8479 | 146.9752 | 546.1907 | 120.3504 | 268.4356 | 272.9128 | 283.2632
843.8479 | 146.9946 | 562.1211 | 120.7849 | 268.2713 | 273.7086 | 283.478
844.8479 | 147.2529 | 576.8831 | 121.4057 | 268.0418 | 274.4454 | 283.9363
845.8479 | 147.2824 | 564.3127 | 121.7232 | 267.9145 | 274.4151 | 283.6106
846.8479 | 147.5638 | 577.2593 | 121.8939 | 267.8646 | 273.8912 | 284.096
847.8479 | 147.5446 | 563.4113 | 122.2939 | 267.6932 | 273.6225 | 284.3053
848.8479 | 147.4715 | 551.8154 | 122.1164 | 267.6851 | 273.503 | 284.3997
849.8479 | 147.3315 | 558.8448 | 121.9967 | 267.8977 | 273.4796 | 284.016
850.8479 | 147.142 | 565.3392 | 122.4637 | 268.0619 | 273.41 | 284.3033
851.8479 | 147.021 | 578.4426 | 122.7378 | 268.1123 | 273.0667 | 285.0858
852.8479 | 146.9013 | 586.2284 | 122.9996 | 267.9894 | 272.8878 | 284.3265
853.8479 | 146.9437 | 596.3622 | 122.9515 | 267.9112 | 272.9877 | 283.7261
854.8479 | 146.8314 | 612.1242 | 123.0125 | 267.817 | 273.3719 | 284.3516
855.8479 | 146.9327 | 611.4717 | 123.0978 | 267.5403 | 273.4986 | 283.8402
856.8479 | 146.6371 | 601.7023 | 122.7724 | 267.3561 | 273.5863 | 283.3988
857.8479 | 146.4597 | 591.1392 | 123.2653 | 267.609 | 274.7022 | 283.149
858.8479 | 146.304 | 589.2579 | 123.2021 | 267.8535 | 274.6469 | 282.8053
859.8479 | 146.718 | 592.8198 | 123.034 | 268.2076 | 274.5722 | 282.5958
860.8479 | 146.6929 | 579.684 | 122.8847 | 268.662 | 274.6872 | 282.1628
861.8479 | 146.7913 | 572.7228 | 122.6453 | 268.735 | 274.6756 | 282.2519
862.8479 | 146.7683 | 574.1515 | 122.6315 | 268.8352 | 274.7273 | 282.5109
863.8479 | 146.7259 | 563.2593 | 122.3228 | 268.9818 | 274.8779 | 282.5625
864.8479 | 146.5875 | 564.7251 | 122.2004 | 269.0535 | 274.8789 | 283.0302
865.8479 | 146.5432 | 577.8047 | 122.3675 | 269.2597 | 275.0558 | 282.9233
866.8479 | 146.4107 | 572.5386 | 122.2724 | 269.5842 | 275.4918 | 282.6882
867.8479 | 146.3139 | 576.5179 | 123.0866 | 269.7161 | 275.6916 | 282.3517
868.8479 | 146.0647 | 577.1418 | 123.3707 | 269.7762 | 275.7163 | 282.141
869.8479 | 145.9722 | 585.6724 | 123.2674 | 270.2949 | 275.4726 | 282.7808
870.8479 | 145.9919 | 601.6882 | 123.3009 | 270.5494 | 275.2386 | 282.6204
871.8479 | 146.0902 | 613.5025 | 123.712 | 270.9332 | 275.2578 | 283.0729
872.8479 | 146.3446 | 608.3812 | 123.9676 | 271.2713 | 275.2226 | 282.5191
873.8479 | 146.4355 | 618.6117 | 124.3533 | 270.9782 | 275.3665 | 282.5363
874.8479 | 146.4091 | 611.8829 | 124.5214 | 270.9501 | 275.6605 | 283.6053
875.8479 | 146.3921 | 598.9055 | 124.8113 | 271.0782 | 275.9127 | 284.3976
876.8479 | 146.5901 | 606.1998 | 124.9124 | 271.5724 | 276.5861 | 284.2407
877.8479 | 146.689 | 605.9204 | 124.6998 | 271.9307 | 276.6338 | 283.7112
878.8479 | 146.8326 | 620.6934 | 124.6293 | 271.8448 | 276.5764 | 283.4153
879.8479 | 147.1931 | 628.423 | 124.9251 | 271.8061 | 276.6641 | 283.9497
880.8479 | 147.237 | 628.6058 | 125.0936 | 271.723 | 276.7635 | 283.8608
881.8479 | 147.2695 | 630.4504 | 124.5867 | 271.585 | 277.2303 | 283.8787
882.8479 | 147.3487 | 614.9156 | 124.6648 | 271.7474 | 277.6346 | 283.6541
883.8479 | 147.756 | 628.0544 | 124.9004 | 272.2822 | 277.4597 | 283.8293
884.8479 | 147.8645 | 637.8396 | 125.0211 | 272.31 | 277.477 | 283.7445
885.8479 | 148.1172 | 626.4133 | 124.8714 | 272.3473 | 277.7312 | 283.5218
886.8479 | 148.3968 | 636.859 | 124.8013 | 272.341 | 277.5967 | 283.4046
887.8479 | 148.7629 | 646.225 | 124.3404 | 272.4128 | 277.5874 | 283.4654
888.8479 | 148.636 | 625.9242 | 124.6163 | 272.7441 | 277.6554 | 283.3347
889.8479 | 148.599 | 632.4528 | 125.0306 | 273.1798 | 277.6544 | 283.8799
890.8479 | 148.4195 | 630.2282 | 125.2978 | 273.1723 | 277.5248 | 283.9647
891.8479 | 148.592 | 625.5616 | 125.6758 | 273.4027 | 277.189 | 284.0077
892.8479 | 148.8766 | 617.7138 | 126.3072 | 273.8342 | 277.6333 | 284.0288
893.8479 | 149.2961 | 617.5956 | 126.4145 | 274.7859 | 277.7793 | 283.8895
894.8479 | 149.4316 | 618.2845 | 126.7897 | 275.2182 | 278.2722 | 283.7716
895.8479 | 149.2849 | 604.0702 | 126.6934 | 275.5468 | 278.2087 | 283.5685
896.8479 | 149.2844 | 605.1045 | 126.8867 | 275.3885 | 278.3412 | 283.4607
897.8479 | 148.9568 | 582.1934 | 127.1501 | 275.7207 | 278.2904 | 284.0024
898.8479 | 148.5321 | 571.4277 | 127.4279 | 275.568 | 278.5302 | 284.0893
899.8479 | 148.7721 | 560.52 | 127.8138 | 275.5024 | 278.556 | 284.2334
900.8479 | 149.4171 | 571.2701 | 127.6396 | 275.2465 | 278.8369 | 284.788
901.8479 | 149.8046 | 565.2986 | 127.28 | 274.9566 | 279.2435 | 284.3178
902.8479 | 149.7756 | 568.2376 | 127.46 | 274.8943 | 279.1305 | 284.2201
903.8479 | 149.9016 | 570.2072 | 127.4249 | 274.739 | 279.3142 | 283.9457
904.8479 | 149.7216 | 564.9152 | 127.5732 | 274.556 | 280.1702 | 283.5802
905.8479 | 149.7529 | 576.0184 | 128.4943 | 274.4141 | 280.0213 | 283.4845
906.8479 | 149.8332 | 593.2322 | 128.3736 | 274.3746 | 279.6161 | 283.3822
907.8479 | 150.0999 | 592.6162 | 128.3923 | 274.4435 | 279.4271 | 283.3302
908.8479 | 150.7911 | 604.8102 | 128.518 | 274.4931 | 279.2667 | 283.05
909.8479 | 151.0899 | 584.5313 | 128.3195 | 274.6031 | 278.8229 | 282.7453
910.8479 | 151.4364 | 593.0182 | 129.0215 | 274.1366 | 278.2419 | 282.9543
911.8479 | 151.4839 | 601.9255 | 129.1674 | 273.8971 | 277.86 | 283.0629
912.8479 | 151.4912 | 583.8302 | 128.9182 | 273.9275 | 277.5545 | 282.9658
913.8479 | 151.3983 | 584.3428 | 128.6429 | 274.1901 | 277.1972 | 283.0169
914.8479 | 151.2322 | 575.524 | 128.342 | 274.0204 | 276.7694 | 283.2709
915.8479 | 151.1822 | 571.7237 | 128.4185 | 274.0063 | 276.8525 | 283.6229
916.8479 | 151.106 | 569.8609 | 129.2344 | 274.0852 | 277.1029 | 283.352
917.8479 | 150.8839 | 571.3458 | 129.0727 | 274.038 | 277.3588 | 284.0482
918.8479 | 150.8751 | 549.504 | 129.8826 | 273.9191 | 277.3093 | 284.2067
919.8479 | 150.9794 | 565.6536 | 130.3669 | 273.5399 | 277.0121 | 284.3697
920.8479 | 150.9089 | 595.8365 | 130.6298 | 273.3508 | 276.5033 | 284.3583
921.8479 | 150.965 | 584.6693 | 130.4674 | 273.2711 | 276.0055 | 284.7866
922.8479 | 151.0217 | 581.7933 | 130.3811 | 273.034 | 275.4795 | 284.5466
923.8479 | 151.1483 | 603.0189 | 130.1827 | 272.6714 | 275.0793 | 284.0385
924.8479 | 151.245 | 594.2305 | 129.9902 | 272.4712 | 274.96 | 283.3387
925.8479 | 151.2195 | 585.7206 | 129.9096 | 272.294 | 274.98 | 282.7628
926.8479 | 151.2327 | 586.7199 | 129.6591 | 272.276 | 274.8192 | 283.215
927.8479 | 151.5616 | 590.0054 | 129.5527 | 272.2606 | 274.5684 | 283.1316
928.8479 | 151.6402 | 579.8826 | 129.0779 | 271.96 | 274.6093 | 282.6693
929.8479 | 151.5913 | 577.3915 | 128.5808 | 271.6242 | 274.6727 | 282.261
930.8479 | 151.7771 | 571.2013 | 128.8514 | 271.2862 | 274.7241 | 281.8317
931.8479 | 151.4482 | 567.619 | 128.5181 | 271.0518 | 275.2279 | 281.9922
932.8479 | 151.3448 | 557.9417 | 128.6376 | 271.0385 | 275.2464 | 281.7847
933.8479 | 151.2316 | 555.4007 | 128.5575 | 271.166 | 274.9933 | 282.1288
934.8479 | 151.2305 | 543.457 | 128.6387 | 271.1538 | 274.8199 | 282.6013
935.8479 | 150.9776 | 534.7171 | 128.7924 | 271.4241 | 274.5332 | 282.6151
936.8479 | 151.0529 | 536.4711 | 128.6358 | 271.4949 | 274.7986 | 282.2651
937.8479 | 151.1451 | 532.5844 | 128.4716 | 271.4626 | 274.8713 | 282.2533
938.8479 | 151.348 | 520.7121 | 128.5405 | 271.4064 | 274.8808 | 281.8662
939.8479 | 151.4266 | 506.2575 | 128.4579 | 271.3337 | 275.513 | 281.4709
940.8479 | 151.2649 | 506.6816 | 128.6884 | 271.0061 | 275.2032 | 282.0336
941.8479 | 151.2161 | 501.7276 | 128.3074 | 270.9539 | 275.2259 | 282.3258
942.8479 | 150.9839 | 492.9164 | 128.2607 | 270.9303 | 275.4052 | 282.0256
943.8479 | 151.0167 | 503.3783 | 128.0249 | 270.6026 | 275.3782 | 281.8022
944.8479 | 151.2086 | 508.8931 | 127.7549 | 270.3992 | 275.2694 | 281.2592
945.8479 | 151.9941 | 500.992 | 128.0248 | 270.456 | 275.6544 | 281.0748
946.8479 | 151.9172 | 501.9734 | 127.9493 | 270.8366 | 275.605 | 280.8053
947.8479 | 152.1941 | 497.8253 | 128.3159 | 270.7065 | 275.607 | 280.6545
948.8479 | 152.2096 | 486.8748 | 128.282 | 270.525 | 276.1638 | 280.3627
949.8479 | 152.276 | 489.1236 | 128.4704 | 270.5402 | 276.4405 | 279.964
950.8479 | 152.1246 | 490.4173 | 128.6008 | 270.9009 | 276.532 | 280.1748
951.8479 | 151.6901 | 490.2841 | 129.0912 | 271.1688 | 276.6362 | 280.1113
952.8479 | 151.4408 | 499.4745 | 128.9619 | 271.5163 | 276.9612 | 279.9852
953.8479 | 151.3656 | 511.8086 | 129.1341 | 271.573 | 277.1453 | 279.9064
954.8479 | 151.4112 | 519.9449 | 129.1509 | 271.9261 | 277.3937 | 280.5611
955.8479 | 151.3414 | 522.828 | 128.8657 | 272.1723 | 277.4474 | 280.9045
956.8479 | 151.1642 | 540.9277 | 128.7925 | 271.9601 | 277.4844 | 280.53
957.8479 | 151.0098 | 552.9827 | 128.8814 | 271.959 | 277.6678 | 280.3887
958.8479 | 150.9421 | 534.6585 | 128.7602 | 271.5968 | 277.6188 | 280.3369
959.8479 | 151.197 | 532.352 | 128.8202 | 271.1355 | 277.6552 | 279.9964
960.8479 | 151.4585 | 545.7935 | 128.6808 | 270.9198 | 277.5549 | 279.8086
961.8479 | 151.5112 | 568.2449 | 128.6021 | 270.7881 | 277.3296 | 279.6816
962.8479 | 151.9839 | 566.1197 | 128.7124 | 270.6839 | 277.3025 | 279.4902
963.8479 | 152.0772 | 564.4042 | 129.0749 | 270.6535 | 277.1929 | 279.2115
964.8479 | 151.9069 | 561.1036 | 129.3786 | 270.5584 | 277.0662 | 279.0829
965.8479 | 152.0043 | 585.1901 | 129.5715 | 270.7785 | 276.9423 | 279.3304
966.8479 | 151.8642 | 569.7749 | 129.7781 | 270.6525 | 277.1541 | 279.9288
967.8479 | 151.7119 | 573.2867 | 129.9061 | 270.8336 | 277.3629 | 279.75
968.8479 | 151.8066 | 571.1981 | 130.5908 | 271.2111 | 277.589 | 279.6273
969.8479 | 151.7348 | 569.8699 | 130.9402 | 271.204 | 277.4674 | 279.4725
970.8479 | 151.7661 | 589.0453 | 131.4313 | 271.0415 | 277.379 | 279.2237
971.8479 | 152.1286 | 590.5835 | 131.9607 | 270.972 | 277.0329 | 278.9606
972.8479 | 152.4086 | 612.4864 | 131.7091 | 271.1527 | 276.8438 | 278.929
973.8479 | 152.7437 | 614.904 | 131.6415 | 270.8001 | 276.8048 | 278.7017
974.8479 | 153.1899 | 624.9037 | 131.6772 | 270.5434 | 276.642 | 278.6317
975.8479 | 153.3517 | 611.3505 | 132.2089 | 270.8447 | 276.5121 | 278.4679
976.8479 | 153.2871 | 603.3868 | 131.8466 | 270.7695 | 276.2852 | 278.4765
977.8479 | 153.1161 | 613.4038 | 132.0089 | 270.7935 | 276.5409 | 278.4538
978.8479 | 153.028 | 612.6287 | 132.442 | 271.019 | 276.3808 | 278.4468
979.8479 | 153.1023 | 598.3942 | 132.6436 | 271.2489 | 276.0883 | 278.3414
980.8479 | 152.9775 | 591.8636 | 133.1216 | 271.2103 | 276.3064 | 278.0557
981.8479 | 153.0439 | 575.2196 | 133.4319 | 271.1096 | 276.185 | 277.9884
982.8479 | 152.931 | 566.9436 | 133.7059 | 271.0948 | 275.8635 | 278.1843
983.8479 | 152.6927 | 568.4761 | 134.2284 | 271.0546 | 275.6487 | 278.2571
984.8479 | 152.6856 | 563.3669 | 134.2141 | 271.1098 | 275.6474 | 279.9233
985.8479 | 153.0131 | 571.3393 | 134.3161 | 270.8349 | 275.7821 | 280.1867
986.8479 | 153.2579 | 556.508 | 134.1317 | 270.6426 | 276.1298 | 280.345
987.8479 | 153.2299 | 553.8945 | 134.6541 | 270.6033 | 276.522 | 280.2538
988.8479 | 153.3392 | 579.5964 | 134.5501 | 270.5232 | 276.7689 | 281.4872
989.8479 | 153.256 | 563.3319 | 134.542 | 270.5619 | 277.1194 | 281.1732
990.8479 | 153.5931 | 575.5478 | 134.659 | 270.6091 | 277.3183 | 280.8906
991.8479 | 153.6695 | 586.4977 | 134.9158 | 270.5382 | 277.363 | 280.5677
992.8479 | 153.5735 | 577.6264 | 134.4707 | 270.3406 | 277.2608 | 280.5314
993.8479 | 153.3087 | 583.8766 | 135.0277 | 270.4989 | 277.3487 | 280.2339
994.8479 | 153.3745 | 586.8732 | 135.049 | 270.5437 | 277.6479 | 279.8957
995.8479 | 153.0647 | 583.0124 | 135.554 | 270.7692 | 277.8642 | 280.7047
996.8479 | 152.9413 | 566.126 | 135.9998 | 270.8378 | 277.72 | 280.5942
997.8479 | 153.0725 | 546.4564 | 135.9838 | 271.2532 | 277.8326 | 280.718
998.8479 | 152.8325 | 533.4344 | 136.4065 | 271.2228 | 277.9644 | 281.6826
999.8479 | 152.7045 | 539.8811 | 136.2663 | 271.0302 | 278.1348 | 282.9249
1000.8479 | 153.0255 | 539.1478 | 136.1598 | 270.9186 | 278.3307 | 282.4702
1001.8479 | 153.4515 | 541.7884 | 135.9802 | 270.9444 | 278.2266 | 282.7531
1002.8479 | 153.3938 | 535.4965 | 135.9074 | 270.8051 | 277.9182 | 282.3202
1003.8479 | 153.1471 | 538.33 | 135.7722 | 270.824 | 277.8747 | 282.5403
1004.8479 | 153.159 | 546.7106 | 135.8879 | 270.7581 | 277.7558 | 282.6945
1005.8479 | 152.794 | 533.4489 | 135.1226 | 270.4649 | 277.7399 | 282.866
1006.8479 | 152.6685 | 534.256 | 135.359 | 270.475 | 277.9281 | 282.7228
1007.8479 | 152.5259 | 535.9657 | 135.6416 | 270.9574 | 278.0722 | 283.6504
1008.8479 | 152.4738 | 543.8386 | 135.421 | 270.6341 | 278.4048 | 283.8084
1009.8479 | 152.2939 | 556.8038 | 135.089 | 270.3521 | 278.3901 | 284.214
1010.8479 | 152.3726 | 549.0947 | 134.6213 | 270.7452 | 278.4718 | 283.7254
1011.8479 | 152.565 | 545.7905 | 134.9621 | 270.5712 | 278.2101 | 284.6761
1012.8479 | 152.6973 | 553.0357 | 134.457 | 270.2691 | 278.0373 | 284.9199
1013.8479 | 152.7433 | 538.7937 | 134.2252 | 270.0687 | 278.0204 | 284.6111
1014.8479 | 152.7531 | 534.5589 | 134.4154 | 269.6254 | 278.6722 | 283.9382
1015.8479 | 153.0633 | 539.4099 | 134.1129 | 269.2174 | 278.4235 | 283.2123
1016.8479 | 153.2115 | 547.0771 | 134.0796 | 268.9902 | 277.8562 | 284.3112
1017.8479 | 153.3175 | 548.4092 | 133.9424 | 269.0028 | 277.2595 | 284.9619
1018.8479 | 152.977 | 540.6964 | 133.8041 | 268.9571 | 276.6271 | 285.5324
1019.8479 | 152.6896 | 536.5381 | 134.2984 | 269.0449 | 276.4585 | 286.378
1020.8479 | 152.3806 | 539.212 | 134.1739 | 268.8886 | 276.2148 | 285.9969
1021.8479 | 151.974 | 552.0306 | 134.1605 | 268.7995 | 276.2292 | 285.3848
1022.8479 | 151.9168 | 548.1212 | 134.5099 | 268.491 | 276.3904 | 284.8954
1023.8479 | 151.9762 | 552.7964 | 134.1799 | 268.6819 | 277.3035 | 284.3705
1024.8479 | 152.0908 | 556.3333 | 134.1061 | 268.4541 | 277.5244 | 284.4431
1025.8479 | 151.9734 | 556.332 | 134.2113 | 268.2009 | 277.4733 | 284.0002
1026.8479 | 151.8018 | 559.6296 | 134.0731 | 267.9827 | 277.3421 | 284.1875
1027.8479 | 151.7954 | 553.7644 | 134.4524 | 268.0269 | 277.1471 | 284.1334
1028.8479 | 151.5711 | 541.4464 | 134.2854 | 267.7683 | 276.7497 | 283.7441
1029.8479 | 151.4741 | 530.9089 | 134.574 | 267.5846 | 276.6784 | 283.5091
1030.8479 | 151.6599 | 523.8751 | 135.1364 | 267.5035 | 277.1206 | 283.4804
1031.8479 | 151.6452 | 517.7953 | 135.5988 | 267.2854 | 277.6216 | 283.5468
1032.8479 | 151.3384 | 500.0513 | 136.2834 | 267.087 | 277.995 | 283.3291
1033.8479 | 151.3785 | 492.5461 | 136.3854 | 267.2682 | 278.065 | 283.627
1034.8479 | 151.3592 | 499.1255 | 136.1984 | 267.0592 | 277.9541 | 283.6868
1035.8479 | 151.2593 | 496.5206 | 136.0096 | 267.196 | 277.9531 | 283.276
1036.8479 | 151.4454 | 496.6922 | 136.1 | 267.4235 | 278.1596 | 282.9802
1037.8479 | 151.4214 | 503.9061 | 135.4462 | 267.5576 | 278.1721 | 282.7059
1038.8479 | 151.8496 | 503.302 | 135.3027 | 267.3685 | 278.0961 | 282.4019
1039.8479 | 152.0192 | 518.4528 | 134.8914 | 267.5787 | 277.8842 | 281.9376
1040.8479 | 152.4829 | 535.5547 | 135.0691 | 267.72 | 277.721 | 282.0615
1041.8479 | 152.6805 | 555.4264 | 134.707 | 268.0612 | 277.8747 | 282.8097
1042.8479 | 152.9838 | 561.8845 | 135.033 | 268.2587 | 277.8484 | 282.6449
1043.8479 | 152.9651 | 573.3264 | 135.1243 | 268.4971 | 277.8633 | 282.5101
1044.8479 | 153.1417 | 575.0503 | 134.8093 | 268.7833 | 277.7762 | 282.0093
1045.8479 | 153.5377 | 596.2087 | 134.6438 | 269.1419 | 277.6817 | 282.0906
1046.8479 | 153.6289 | 586.8195 | 134.2612 | 269.4942 | 277.6602 | 281.6654
1047.8479 | 153.5751 | 578.4803 | 134.1839 | 269.744 | 277.5633 | 281.5354
1048.8479 | 153.5372 | 565.3988 | 134.3977 | 269.6407 | 277.5083 | 281.0122
1049.8479 | 153.5359 | 570.5615 | 134.2781 | 269.6084 | 277.5023 | 280.6301
1050.8479 | 153.8456 | 574.2145 | 134.8004 | 269.2847 | 277.5829 | 280.5946
1051.8479 | 153.918 | 576.8229 | 134.8048 | 268.9743 | 277.5119 | 280.4174
1052.8479 | 153.8193 | 580.8617 | 135.2307 | 268.8541 | 277.5908 | 280.273
1053.8479 | 153.606 | 571.9236 | 135.8948 | 268.6263 | 277.3511 | 279.9343
1054.8479 | 153.3449 | 574.7744 | 136.2408 | 268.3695 | 277.2148 | 280.3944
1055.8479 | 153.2766 | 578.6722 | 136.0048 | 268.0743 | 277.0354 | 281.2672
1056.8479 | 153.5271 | 576.4674 | 136.0725 | 267.8025 | 276.9192 | 281.4168
1057.8479 | 153.5677 | 566.3755 | 135.8118 | 267.7239 | 277.5375 | 281.745
1058.8479 | 153.6565 | 566.2686 | 136.3809 | 267.717 | 277.5914 | 281.6773
1059.8479 | 153.6083 | 559.516 | 136.6409 | 268.2211 | 277.4699 | 281.2612
1060.8479 | 153.5985 | 559.5759 | 136.5288 | 268.4763 | 277.3681 | 281.2833
1061.8479 | 153.2515 | 542.6217 | 136.5553 | 268.371 | 277.422 | 280.7925
1062.8479 | 153.2599 | 540.268 | 136.4445 | 268.4421 | 277.4114 | 281.1541
1063.8479 | 153.3902 | 531.3098 | 136.4479 | 268.3056 | 277.3324 | 280.7501
1064.8479 | 153.1894 | 532.9736 | 136.6923 | 268.6275 | 277.246 | 281.3825
1065.8479 | 152.945 | 530.0036 | 137.0568 | 268.5299 | 277.3823 | 281.2553
1066.8479 | 152.7011 | 528.732 | 137.5769 | 268.5426 | 277.4392 | 280.6773
1067.8479 | 152.2706 | 530.7907 | 137.6103 | 268.6831 | 277.5097 | 281.131
1068.8479 | 152.1292 | 528.1011 | 137.61 | 268.664 | 277.3778 | 281.2381
1069.8479 | 151.8951 | 538.3807 | 137.8499 | 268.6793 | 277.4676 | 282.1254
1070.8479 | 151.6282 | 529.4809 | 138.0752 | 268.5177 | 277.3583 | 281.8738
1071.8479 | 151.5766 | 521.0948 | 137.9299 | 268.5138 | 277.496 | 281.7877
1072.8479 | 151.2044 | 527.9306 | 137.8925 | 268.5173 | 277.5937 | 282.4999
1073.8479 | 151.1057 | 522.8352 | 137.7849 | 268.1872 | 277.7917 | 282.6804
1074.8479 | 151.1274 | 514.7839 | 137.6631 | 267.8075 | 277.9061 | 282.9077
1075.8479 | 150.9702 | 508.3356 | 137.724 | 267.7748 | 277.7886 | 282.8697
1076.8479 | 151.1344 | 509.5083 | 137.0764 | 267.6418 | 277.8868 | 282.831
1077.8479 | 151.44 | 513.9681 | 137.4176 | 267.6002 | 277.8437 | 283.0163
1078.8479 | 151.6626 | 525.9726 | 137.5455 | 267.5057 | 278.0614 | 282.8757
1079.8479 | 151.9629 | 541.7151 | 137.3829 | 267.3666 | 278.0177 | 282.6346
1080.8479 | 152.3132 | 562.5471 | 137.0456 | 267.1378 | 278.1191 | 282.0024
1081.8479 | 152.5435 | 579.4117 | 136.6558 | 266.8105 | 278.0431 | 281.7275
1082.8479 | 152.6987 | 574.6878 | 136.9918 | 266.6962 | 277.736 | 281.4321
1083.8479 | 152.6652 | 570.7807 | 136.9809 | 267.1434 | 277.4696 | 281.7912
1084.8479 | 152.7107 | 583.0799 | 136.4972 | 267.7098 | 277.1999 | 282.2643
1085.8479 | 152.8144 | 601.461 | 135.9807 | 268.2135 | 277.1839 | 282.4015
1086.8479 | 153.0607 | 583.7133 | 135.8031 | 268.251 | 277.1425 | 282.6336
1087.8479 | 153.2154 | 589.3294 | 136.5571 | 268.364 | 276.9839 | 282.9214
1088.8479 | 152.9436 | 585.7299 | 136.6374 | 268.1974 | 276.8731 | 282.5277
1089.8479 | 152.8801 | 592.9714 | 136.8712 | 268.0701 | 276.8296 | 283.6747
1090.8479 | 153.1806 | 605.8953 | 136.8902 | 267.9049 | 276.9611 | 283.1023
1091.8479 | 153.4254 | 617.8581 | 136.298 | 267.5757 | 276.833 | 282.9788
1092.8479 | 153.9988 | 635.0597 | 136.2655 | 267.455 | 276.6159 | 283.2197
1093.8479 | 154.2267 | 651.4042 | 136.7064 | 267.9269 | 277.0735 | 283.2417
1094.8479 | 154.317 | 644.7468 | 137.5717 | 267.5113 | 277.3989 | 282.9102
1095.8479 | 154.2313 | 638.6724 | 136.7637 | 267.065 | 277.2069 | 282.1304
1096.8479 | 154.2976 | 626.2751 | 136.9419 | 267.072 | 277.1383 | 281.9626
1097.8479 | 154.3873 | 617.1216 | 136.4222 | 267.1179 | 277.2709 | 282.1741
1098.8479 | 154.2791 | 605.1569 | 136.2093 | 267.422 | 276.9821 | 281.9239
1099.8479 | 154.436 | 605.7757 | 135.7592 | 267.2861 | 277.1261 | 282.4352
1100.8479 | 154.6139 | 610.7503 | 135.8431 | 267.6065 | 277.3592 | 282.2627
1101.8479 | 154.7211 | 598.2624 | 135.5687 | 267.7135 | 277.6265 | 281.8314
1102.8479 | 154.8327 | 605.699 | 135.8804 | 267.7266 | 277.6719 | 281.6803
1103.8479 | 154.8979 | 603.8566 | 135.699 | 267.8864 | 277.7087 | 281.0721
1104.8479 | 154.851 | 603.575 | 135.43 | 268.058 | 277.4918 | 280.5858
1105.8479 | 155.1516 | 607.7879 | 135.2278 | 268.2329 | 277.6011 | 280.1564
1106.8479 | 155.0691 | 607.8542 | 135.3198 | 268.448 | 277.8054 | 279.8786
1107.8479 | 155.0485 | 602.3224 | 135.0817 | 268.8907 | 278.0644 | 279.479
1108.8479 | 155.467 | 572.2943 | 135.9006 | 269.1721 | 278.1695 | 279.1686
1109.8479 | 155.8533 | 565.1099 | 136.3743 | 269.1795 | 278.4085 | 278.9106
1110.8479 | 156.1312 | 563.2051 | 137.0487 | 269.0524 | 278.2264 | 278.8103
1111.8479 | 156.423 | 540.739 | 137.1319 | 269.3642 | 278.3472 | 278.6534
1112.8479 | 156.4104 | 543.1212 | 137.5553 | 269.2356 | 278.6539 | 278.4926
1113.8479 | 156.3085 | 544.3644 | 137.9142 | 269.0769 | 278.6594 | 279.3738
1114.8479 | 156.2979 | 537.2564 | 137.8994 | 268.8408 | 278.58 | 279.8926
1115.8479 | 156.1178 | 541.4665 | 137.3972 | 268.699 | 278.4876 | 280.7435
1116.8479 | 156.0938 | 545.5016 | 137.3417 | 268.568 | 278.3141 | 281.4198
1117.8479 | 156.342 | 545.5359 | 137.6806 | 268.4636 | 278.4768 | 282.313
1118.8479 | 156.3538 | 534.823 | 137.6988 | 268.2631 | 278.4778 | 282.4794
1119.8479 | 156.4101 | 538.4027 | 137.6652 | 268.1717 | 278.3182 | 283.9348
1120.8479 | 156.6368 | 533.2699 | 137.9474 | 267.8985 | 278.245 | 284.1157
1121.8479 | 156.5106 | 557.8273 | 138.141 | 267.6978 | 278.1428 | 284.9372
1122.8479 | 156.7129 | 573.1343 | 137.8092 | 267.5916 | 277.9545 | 284.6782
1123.8479 | 156.8032 | 573.4327 | 137.8955 | 267.4471 | 277.8097 | 284.7629
1124.8479 | 156.7626 | 595.9805 | 138.2163 | 267.3351 | 277.6973 | 284.6305
1125.8479 | 156.5652 | 587.656 | 138.3522 | 267.0766 | 277.5273 | 285.2422
1126.8479 | 156.3095 | 576.9584 | 137.9849 | 266.7494 | 277.6582 | 284.7914
1127.8479 | 156.1711 | 574.896 | 137.7242 | 266.574 | 277.4542 | 284.3197
1128.8479 | 155.9456 | 566.8254 | 137.5117 | 266.5392 | 277.3966 | 283.7402
1129.8479 | 155.7867 | 550.3263 | 137.4407 | 265.9492 | 277.1106 | 283.0098
1130.8479 | 155.5628 | 556.6371 | 137.5321 | 265.72 | 276.7207 | 282.739
1131.8479 | 155.3669 | 560.8566 | 137.4363 | 265.3579 | 276.2387 | 282.9238
1132.8479 | 155.1132 | 574.5915 | 137.7825 | 265.1289 | 275.9576 | 283.3524
1133.8479 | 154.907 | 584.3474 | 137.6307 | 264.8088 | 275.9302 | 283.3861
1134.8479 | 154.7346 | 601.9022 | 138.0027 | 264.6162 | 275.751 | 283.8907
1135.8479 | 154.5301 | 602.54 | 137.525 | 264.5128 | 275.5177 | 283.5128
1136.8479 | 154.2754 | 598.782 | 137.7166 | 264.3256 | 275.3061 | 282.6809
1137.8479 | 153.9311 | 590.8099 | 137.5518 | 264.0314 | 275.2469 | 282.0184
1138.8479 | 154.0165 | 594.6913 | 137.8337 | 263.9216 | 275.132 | 281.357
1139.8479 | 153.9296 | 583.2301 | 137.8249 | 263.7518 | 274.9296 | 280.7049
1140.8479 | 154.0029 | 566.7921 | 137.9504 | 263.7221 | 274.5747 | 280.5299
1141.8479 | 153.9872 | 551.3526 | 138.4451 | 263.7254 | 274.474 | 281.2347
1142.8479 | 153.8416 | 543.3698 | 138.5792 | 263.6907 | 274.4905 | 281.1158
1143.8479 | 153.6557 | 533.3867 | 138.4632 | 263.4015 | 274.5587 | 281.9245
1144.8479 | 153.5378 | 521.9866 | 138.288 | 263.1422 | 274.8477 | 281.4837
1145.8479 | 153.3662 | 513.874 | 138.4012 | 263.4881 | 275.1202 | 281.7254
1146.8479 | 153.1205 | 511.1529 | 138.5761 | 263.6172 | 274.8549 | 281.313
1147.8479 | 152.863 | 508.5493 | 138.1199 | 263.5278 | 274.6899 | 280.989
1148.8479 | 152.5973 | 502.4037 | 137.3337 | 263.4841 | 274.6207 | 280.8811
1149.8479 | 152.3893 | 502.9806 | 136.6637 | 263.4556 | 274.452 | 281.3303
1150.8479 | 152.4163 | 518.7596 | 136.714 | 263.4749 | 274.2857 | 280.8259
1151.8479 | 152.2692 | 522.6647 | 136.7872 | 263.2511 | 274.1253 | 280.3495
1152.8479 | 152.2644 | 515.4363 | 136.6395 | 263.0651 | 273.8197 | 280.2871
1153.8479 | 152.2778 | 525.0664 | 137.2625 | 262.7337 | 273.7908 | 280.947
1154.8479 | 152.2544 | 536.0506 | 137.0901 | 262.5269 | 273.734 | 280.5855
1155.8479 | 152.5195 | 534.9975 | 137.1197 | 262.518 | 273.8004 | 280.6466
1156.8479 | 152.7458 | 553.9418 | 137.3446 | 262.4698 | 273.9061 | 280.7235
1157.8479 | 152.9631 | 568.1933 | 136.9877 | 262.3064 | 273.6643 | 281.3047
1158.8479 | 153.3134 | 574.5481 | 136.6919 | 262.1351 | 273.5797 | 281.3381
1159.8479 | 153.4863 | 569.9267 | 136.6644 | 261.888 | 273.5628 | 280.5736
1160.8479 | 153.5395 | 574.8886 | 136.2036 | 261.5928 | 273.596 | 281.3504
1161.8479 | 153.5394 | 579.1728 | 136.3036 | 261.4487 | 273.4747 | 280.574
1162.8479 | 153.4597 | 568.2032 | 135.9781 | 261.6464 | 273.3177 | 279.9908
1163.8479 | 153.4829 | 575.4274 | 136.2122 | 261.7348 | 273.0364 | 279.9562
1164.8479 | 153.5459 | 582.4979 | 136.7343 | 261.5571 | 273.204 | 279.7072
1165.8479 | 153.5912 | 592.5072 | 136.2878 | 261.5585 | 273.3183 | 279.7767
1166.8479 | 153.8535 | 577.0432 | 135.9578 | 261.9658 | 273.2341 | 279.6332
1167.8479 | 154.0051 | 581.9171 | 135.9049 | 262.2565 | 272.9192 | 278.9171
1168.8479 | 154.1181 | 586.0012 | 135.8668 | 262.1861 | 272.5686 | 278.3916
1169.8479 | 154.1664 | 606.1577 | 136.1704 | 262.1505 | 272.3567 | 277.8139
1170.8479 | 154.3981 | 611.0344 | 136.2936 | 262.0311 | 272.4562 | 277.9987
1171.8479 | 154.4483 | 627.5352 | 136.4972 | 262.0916 | 272.4189 | 278.6561
1172.8479 | 154.3439 | 636.4364 | 136.4417 | 262.2987 | 272.5056 | 278.6897
1173.8479 | 154.2274 | 640.4234 | 136.4286 | 262.2112 | 272.3818 | 278.227
1174.8479 | 153.952 | 628.2313 | 136.7709 | 262.1665 | 272.2697 | 277.6944
1175.8479 | 153.8103 | 648.2858 | 137.1338 | 262.1053 | 272.1802 | 277.0477
1176.8479 | 153.9759 | 663.3658 | 137.3802 | 262.4213 | 271.9616 | 276.3668
1177.8479 | 154.0225 | 651.2652 | 137.3004 | 262.7094 | 271.809 | 275.8045
1178.8479 | 154.0126 | 641.272 | 137.846 | 262.6341 | 271.5734 | 276.1373
1179.8479 | 154.0646 | 640.3461 | 137.3403 | 262.2588 | 271.3181 | 275.9695
1180.8479 | 154.207 | 640.843 | 138.1634 | 262.1867 | 271.0571 | 276.3039
1181.8479 | 154.2239 | 649.4267 | 138.5276 | 261.8698 | 270.8563 | 276.3025
1182.8479 | 154.4556 | 659.6517 | 139.1544 | 261.6534 | 270.7947 | 275.8476
1183.8479 | 154.3969 | 658.5116 | 138.6968 | 261.6111 | 270.6218 | 275.4011
1184.8479 | 154.2977 | 660.8346 | 139.0043 | 261.4407 | 270.6782 | 274.818
1185.8479 | 154.3312 | 652.7672 | 139.6419 | 261.142 | 270.6369 | 274.3578
1186.8479 | 154.3987 | 656.5717 | 140.3726 | 261.1563 | 270.5602 | 274.0993
1187.8479 | 154.6547 | 666.0093 | 140.6421 | 260.9284 | 270.4476 | 274.1122
1188.8479 | 154.7999 | 657.2337 | 140.8486 | 260.7693 | 270.402 | 274.1121
1189.8479 | 154.993 | 668.7296 | 140.9624 | 260.8199 | 270.2264 | 274.3627
1190.8479 | 154.9294 | 644.3407 | 141.2231 | 260.7766 | 270.2496 | 276.1173
1191.8479 | 154.8128 | 620.0459 | 141.7435 | 260.6967 | 270.1061 | 276.0064
1192.8479 | 154.4882 | 605.3321 | 142.1755 | 260.5941 | 270.1755 | 275.7718
1193.8479 | 154.1356 | 603.0651 | 142.549 | 260.6979 | 270.2114 | 276.9807
1194.8479 | 153.7725 | 590.4437 | 142.5903 | 260.7597 | 270.3183 | 277.6459
1195.8479 | 153.9518 | 576.6541 | 141.8925 | 260.8353 | 270.5998 | 277.0436
1196.8479 | 154.0754 | 568.4855 | 141.5458 | 260.8502 | 270.8914 | 276.9184
1197.8479 | 154.0207 | 546.037 | 141.8015 | 260.6598 | 270.943 | 277.2503
1198.8479 | 153.8148 | 538.8797 | 141.4368 | 260.6452 | 271.0446 | 277.2654
1199.8479 | 153.6009 | 554.6161 | 141.7646 | 260.8183 | 271.1277 | 277.8088
1200.8479 | 153.7128 | 561.9245 | 142.2575 | 260.9463 | 271.2821 | 278.7716
1201.8479 | 153.6138 | 568.5647 | 142.3201 | 260.7631 | 271.1792 | 279.0018
1202.8479 | 153.4835 | 556.285 | 142.2104 | 260.5463 | 271.0486 | 279.5052
1203.8479 | 153.2033 | 543.7861 | 142.4923 | 260.5631 | 271.0757 | 280.0794
1204.8479 | 153.1173 | 535.6852 | 142.7625 | 260.6718 | 271.2801 | 279.8655
1205.8479 | 152.9804 | 553.5212 | 143.6621 | 260.7182 | 271.2751 | 279.9997
1206.8479 | 152.8185 | 578.6308 | 143.1637 | 260.6777 | 271.4286 | 280.5073
1207.8479 | 152.5914 | 568.3378 | 143.127 | 260.6974 | 271.5101 | 281.1324
1208.8479 | 152.4634 | 569.2166 | 142.7042 | 260.5752 | 271.4716 | 282.2345
1209.8479 | 152.3008 | 551.519 | 142.3931 | 260.5663 | 271.5441 | 282.7159
1210.8479 | 151.9842 | 539.6641 | 142.0315 | 260.5458 | 271.6952 | 282.7168
1211.8479 | 151.5504 | 525.9204 | 141.8563 | 260.608 | 271.8663 | 282.6695
1212.8479 | 151.2925 | 521.5043 | 142.0767 | 261.6892 | 272.0594 | 282.6806
1213.8479 | 150.9502 | 511.7833 | 142.5252 | 262.4175 | 272.2662 | 283.3941
1214.8479 | 150.6137 | 504.6323 | 142.4298 | 262.6389 | 272.3473 | 283.9914
1215.8479 | 150.614 | 496.2279 | 142.2477 | 262.6537 | 272.1643 | 284.2486
1216.8479 | 150.386 | 487.9793 | 141.5159 | 263.0945 | 272.0168 | 284.1376
1217.8479 | 150.2023 | 479.4584 | 140.493 | 263.1474 | 272.0178 | 285.5524
1218.8479 | 150.1294 | 483.2096 | 140.6733 | 263.0197 | 272.1643 | 285.4419
1219.8479 | 150.0703 | 486.8879 | 140.6255 | 262.8058 | 272.264 | 285.6372
1220.8479 | 150.2219 | 479.3719 | 140.7828 | 262.5905 | 272.5349 | 284.7902
1221.8479 | 150.5016 | 495.2252 | 140.3989 | 262.3622 | 272.5779 | 284.472
1222.8479 | 150.6745 | 500.7298 | 140.4287 | 262.5609 | 272.4496 | 283.6666
1223.8479 | 150.8167 | 508.8438 | 140.3175 | 263.0918 | 272.1767 | 283.3732
1224.8479 | 150.6012 | 526.1193 | 140.1514 | 263.0974 | 272.0242 | 282.6622
1225.8479 | 150.655 | 537.5964 | 140.0604 | 264.0093 | 271.8128 | 282.0103
1226.8479 | 150.5128 | 549.8106 | 139.6237 | 263.8696 | 271.7365 | 282.4669
1227.8479 | 150.4456 | 543.2583 | 139.4499 | 263.5556 | 271.6755 | 281.9909
1228.8479 | 150.2225 | 545.5537 | 139.8713 | 263.2251 | 271.6679 | 281.8101
1229.8479 | 150.3766 | 561.6014 | 139.6107 | 262.9022 | 271.5356 | 281.1139
1230.8479 | 150.5289 | 556.6813 | 139.6247 | 262.7798 | 271.3665 | 280.6844
1231.8479 | 150.4938 | 558.6646 | 139.1318 | 262.8127 | 271.3537 | 280.3931
1232.8479 | 150.4062 | 551.0627 | 139.1277 | 262.6411 | 271.1563 | 280.0087
1233.8479 | 150.3715 | 571.2253 | 139.1709 | 262.4513 | 270.8719 | 280.135
1234.8479 | 150.3733 | 560.6383 | 138.3529 | 262.2445 | 270.9336 | 279.9929
1235.8479 | 150.5453 | 564.7726 | 138.5683 | 262.2443 | 271.2004 | 280.2914
1236.8479 | 150.4695 | 560.5796 | 138.5188 | 262.1019 | 271.4653 | 280.0105
1237.8479 | 150.4819 | 558.6758 | 138.4416 | 262.0834 | 271.4499 | 280.6642
1238.8479 | 150.4932 | 560.9204 | 138.1914 | 262.0952 | 271.6116 | 280.5989
1239.8479 | 150.6295 | 552.5165 | 137.8446 | 261.8772 | 271.7538 | 280.2992
1240.8479 | 150.66 | 541.0558 | 137.7735 | 261.6103 | 271.8363 | 280.0976
1241.8479 | 150.5849 | 536.7219 | 137.6927 | 261.744 | 271.7459 | 280.3055
1242.8479 | 150.5885 | 532.5889 | 137.7039 | 261.7441 | 271.5902 | 281.216
1243.8479 | 150.7419 | 536.2213 | 138.2588 | 261.6298 | 271.6454 | 281.0334
1244.8479 | 150.9937 | 544.9032 | 138.273 | 261.5906 | 271.9977 | 281.5864
1245.8479 | 151.3525 | 537.1362 | 138.4273 | 261.9416 | 271.9876 | 282.5092
1246.8479 | 151.3799 | 545.0478 | 138.1714 | 261.9268 | 272.0752 | 282.9186
1247.8479 | 151.4737 | 559.3125 | 138.6973 | 261.7756 | 272.2685 | 283.5105
1248.8479 | 151.6583 | 568.3801 | 139.0634 | 261.5383 | 272.0634 | 283.1895
1249.8479 | 151.8481 | 591.3257 | 139.1844 | 261.48 | 272.0981 | 282.3124
1250.8479 | 151.8772 | 611.9162 | 139.5467 | 262.0991 | 272.1742 | 282.2687
1251.8479 | 151.9309 | 633.1492 | 139.8037 | 262.4118 | 272.021 | 281.1853
1252.8479 | 152.0547 | 645.78 | 140.1437 | 262.4347 | 271.8818 | 280.2273
1253.8479 | 151.9178 | 674.3354 | 140.8056 | 262.1577 | 271.6032 | 279.5523
1254.8479 | 151.9988 | 673.4749 | 140.8076 | 261.5628 | 271.2916 | 278.9319
1255.8479 | 151.9754 | 663.0864 | 141.2427 | 261.0218 | 270.9006 | 278.5115
1256.8479 | 152.0345 | 654.9847 | 140.7869 | 260.8607 | 270.5288 | 278.2636
1257.8479 | 152.1279 | 634.283 | 140.737 | 260.7408 | 270.3083 | 277.7698
1258.8479 | 152.2353 | 610.5864 | 141.3184 | 260.5775 | 269.9515 | 277.3623
1259.8479 | 152.2429 | 622.4235 | 141.6447 | 260.6585 | 269.4952 | 276.7102
1260.8479 | 152.2304 | 603.6919 | 141.8821 | 260.5194 | 269.2696 | 276.4719
1261.8479 | 152.3797 | 593.1244 | 141.623 | 260.2352 | 269.1112 | 276.8681
1262.8479 | 152.28 | 584.389 | 141.7444 | 259.936 | 269.0206 | 276.9438
1263.8479 | 151.992 | 564.398 | 142.1407 | 259.6511 | 268.979 | 276.9937
1264.8479 | 151.7404 | 547.7576 | 142.1641 | 259.6457 | 269.0658 | 278.0198
1265.8479 | 151.647 | 547.063 | 142.6426 | 260.2614 | 269.214 | 278.9046
1266.8479 | 151.3079 | 533.5684 | 142.4503 | 260.4287 | 269.1685 | 278.9216
1267.8479 | 151.0321 | 538.8202 | 142.2716 | 260.4923 | 269.3076 | 278.4719
1268.8479 | 151.0558 | 517.9334 | 142.7597 | 260.443 | 269.5638 | 277.9966
1269.8479 | 150.8199 | 509.3166 | 142.175 | 260.6188 | 269.5726 | 277.8515
1270.8479 | 150.7362 | 502.4745 | 142.0852 | 260.6907 | 269.4891 | 277.7495
1271.8479 | 150.717 | 500.426 | 141.8638 | 260.5567 | 269.2567 | 277.8292
1272.8479 | 150.5866 | 509.7406 | 141.9536 | 260.4741 | 268.9386 | 278.2041
1273.8479 | 150.5102 | 524.436 | 141.6345 | 260.3414 | 268.7799 | 279.2483
1274.8479 | 150.4427 | 524.6969 | 141.6629 | 260.7613 | 268.6075 | 279.561
1275.8479 | 150.1493 | 517.9548 | 142.5771 | 260.9202 | 268.5523 | 279.7765
1276.8479 | 149.9679 | 507.4205 | 142.5294 | 260.8104 | 268.5283 | 280.622
1277.8479 | 149.8773 | 492.5081 | 142.7302 | 260.7573 | 268.7229 | 281.0934
1278.8479 | 149.7422 | 488.3832 | 142.1501 | 261.0221 | 268.9676 | 281.0627
1279.8479 | 149.6377 | 474.337 | 142.0023 | 260.9848 | 269.5798 | 280.8954
1280.8479 | 149.6332 | 476.0902 | 142.575 | 261.0154 | 269.8823 | 280.6963
1281.8479 | 149.7652 | 497.3395 | 142.1185 | 261.1314 | 270.0477 | 280.7475
1282.8479 | 149.9469 | 528.7918 | 142.2209 | 261.035 | 270.0686 | 281.1044
1283.8479 | 150.1284 | 514.0997 | 141.5029 | 261.4426 | 269.9138 | 280.9719
1284.8479 | 150.1687 | 514.1288 | 141.065 | 261.4359 | 269.7722 | 280.5594
1285.8479 | 150.0346 | 496.2768 | 141.4696 | 261.3759 | 269.7092 | 280.8582
1286.8479 | 149.9341 | 500.6114 | 141.333 | 261.2402 | 269.6254 | 280.4614
1287.8479 | 149.7663 | 515.7102 | 142.075 | 260.9156 | 269.5202 | 280.174
1288.8479 | 149.671 | 535.4091 | 142.9517 | 261.0604 | 269.4581 | 279.3714
1289.8479 | 149.5581 | 542.4266 | 143.4883 | 261.2318 | 269.4777 | 278.7743
1290.8479 | 149.0555 | 540.2923 | 143.8724 | 261.3249 | 269.3418 | 278.5644
1291.8479 | 148.9776 | 541.008 | 144.3243 | 261.3809 | 269.4314 | 278.4819
1292.8479 | 148.8451 | 533.8928 | 144.5281 | 261.2611 | 269.2722 | 277.8805
1293.8479 | 148.6963 | 522.1289 | 143.9898 | 261.1158 | 269.0704 | 277.7222
1294.8479 | 148.4451 | 514.9163 | 144.1293 | 260.8537 | 268.8674 | 278.4591
1295.8479 | 148.198 | 518.013 | 144.2059 | 260.8475 | 268.6872 | 278.7296
1296.8479 | 148.0488 | 504.4291 | 143.1819 | 260.7594 | 268.708 | 278.5847
1297.8479 | 147.7636 | 498.3477 | 142.8948 | 260.7062 | 268.765 | 278.9595
1298.8479 | 147.3898 | 490.072 | 142.5812 | 260.7911 | 268.7531 | 278.052
1299.8479 | 147.2964 | 502.2787 | 142.0995 | 260.6798 | 268.6802 | 277.1781
1300.8479 | 147.3868 | 493.0619 | 141.4661 | 260.5269 | 268.6369 | 276.5431
1301.8479 | 147.4547 | 502.1951 | 141.1823 | 260.4029 | 268.743 | 276.6785
1302.8479 | 147.5619 | 514.8946 | 141.3797 | 260.4402 | 268.712 | 277.0093
1303.8479 | 147.7277 | 530.0101 | 141.5493 | 261.2992 | 268.6898 | 278.2667
1304.8479 | 147.9215 | 549.1674 | 141.1423 | 261.2955 | 268.6195 | 278.6434
1305.8479 | 147.8323 | 539.3037 | 141.3439 | 261.1222 | 268.7155 | 278.7545
1306.8479 | 147.8346 | 554.2839 | 142.1401 | 260.9075 | 268.8961 | 279.0258
1307.8479 | 147.9874 | 559.8254 | 142.7126 | 260.7157 | 269.1155 | 279.4206
1308.8479 | 148.0819 | 568.0883 | 143.0501 | 260.6223 | 269.407 | 279.4634
1309.8479 | 148.1211 | 554.5035 | 143.7218 | 260.3368 | 269.5948 | 279.099
1310.8479 | 148.1586 | 553.005 | 143.6159 | 260.2905 | 269.7924 | 279.8157
1311.8479 | 148.3647 | 551.6969 | 143.4623 | 260.0279 | 270.293 | 279.7408
1312.8479 | 148.1216 | 530.6914 | 142.9931 | 259.9506 | 270.2962 | 279.1447
1313.8479 | 148.2265 | 520.1768 | 142.3578 | 260.1468 | 270.3062 | 278.4395
1314.8479 | 148.3698 | 504.5392 | 142.9452 | 260.2067 | 270.2152 | 278.3038
1315.8479 | 148.4709 | 500.2065 | 142.4287 | 260.0995 | 270.0601 | 278.3875
1316.8479 | 148.4481 | 499.0447 | 142.5386 | 259.9263 | 269.7574 | 278.9114
1317.8479 | 148.4264 | 509.1493 | 142.6034 | 259.6674 | 269.7408 | 278.7361
1318.8479 | 148.4506 | 506.5541 | 142.1571 | 259.7387 | 270.035 | 278.3
1319.8479 | 148.1602 | 507.7267 | 142.043 | 259.6709 | 270.4988 | 279.056
1320.8479 | 147.845 | 496.2804 | 141.4093 | 259.4059 | 270.4331 | 279.6046
1321.8479 | 147.6887 | 493.8039 | 141.5472 | 259.1661 | 270.456 | 279.5658
1322.8479 | 147.6349 | 498.6785 | 142.1211 | 259.0306 | 270.3744 | 279.9344
1323.8479 | 147.4666 | 507.1709 | 142.379 | 259.4045 | 270.3531 | 279.7255
1324.8479 | 147.3934 | 503.0966 | 141.9926 | 259.6369 | 270.9835 | 279.2979
1325.8479 | 147.3015 | 510.8196 | 141.8466 | 260.1994 | 271.5338 | 279.5218
1326.8479 | 147.1728 | 517.164 | 141.081 | 260.4936 | 271.35 | 279.434
1327.8479 | 147.4062 | 516.2542 | 141.1564 | 260.561 | 271.123 | 280.1219
1328.8479 | 147.283 | 519.7116 | 141.4427 | 260.477 | 270.8189 | 280.0365
1329.8479 | 147.1408 | 520.5577 | 141.1924 | 260.2574 | 270.5804 | 280.5929
1330.8479 | 147.1462 | 523.4447 | 141.0534 | 260.2522 | 270.459 | 281.5136
1331.8479 | 147.0987 | 519.0816 | 140.7353 | 260.3179 | 270.3875 | 281.2603
1332.8479 | 147.0038 | 528.5033 | 139.9874 | 260.2842 | 270.6429 | 281.5768
1333.8479 | 147.1417 | 521.9643 | 139.4342 | 260.1553 | 270.8865 | 281.0206
1334.8479 | 147.0754 | 515.5693 | 139.188 | 260.0162 | 271.2499 | 281.6306
1335.8479 | 147.0278 | 512.1001 | 139.4232 | 260.0991 | 271.3633 | 281.5762
1336.8479 | 146.6337 | 507.5255 | 139.4706 | 260.6671 | 271.5463 | 281.959
1337.8479 | 146.3164 | 504.9599 | 139.2391 | 260.9012 | 271.662 | 281.8298
1338.8479 | 146.0567 | 498.2012 | 139.209 | 261.1253 | 271.8033 | 282.8258
1339.8479 | 146.0789 | 496.2395 | 139.4071 | 261.3346 | 271.9807 | 282.9386
1340.8479 | 146.1506 | 505.0079 | 139.8187 | 261.6119 | 272.2872 | 282.166
1341.8479 | 146.1716 | 511.5023 | 139.0513 | 261.6791 | 272.3597 | 281.5767
1342.8479 | 146.3986 | 526.9769 | 139.2499 | 261.5983 | 272.2495 | 282.0919
1343.8479 | 146.7899 | 536.0853 | 139.4651 | 261.4725 | 272.204 | 281.8281
1344.8479 | 147.0607 | 539.996 | 139.3113 | 261.3928 | 272.0733 | 280.9849
1345.8479 | 146.9931 | 559.0675 | 139.1937 | 261.106 | 271.8379 | 281.2023
1346.8479 | 146.8661 | 555.967 | 139.0366 | 261.0642 | 271.6983 | 280.4866
1347.8479 | 146.5407 | 555.3463 | 138.8853 | 260.8515 | 271.6632 | 280.582
1348.8479 | 146.6395 | 560.485 | 138.6151 | 260.8351 | 271.546 | 281.0842
1349.8479 | 146.3934 | 555.4229 | 138.6896 | 260.8213 | 271.5641 | 280.8768
1350.8479 | 146.3674 | 554.8316 | 138.6014 | 260.5142 | 271.779 | 280.4716
1351.8479 | 146.3904 | 563.1606 | 138.4375 | 260.2432 | 271.8627 | 280.433
1352.8479 | 146.4256 | 576.3201 | 138.5324 | 259.9139 | 271.8597 | 280.4626
1353.8479 | 146.6726 | 588.2496 | 138.5433 | 260.1309 | 271.823 | 280.5384
1354.8479 | 146.6677 | 593.9557 | 139.3266 | 260.2668 | 271.7666 | 280.4412
1355.8479 | 146.5483 | 585.5313 | 139.7396 | 260.1466 | 271.5326 | 279.924
1356.8479 | 146.6174 | 581.0818 | 140.0348 | 259.9414 | 271.2424 | 280.2285
1357.8479 | 146.8515 | 581.0505 | 140.4681 | 259.8121 | 271.0073 | 279.5149
1358.8479 | 147.1942 | 582.2038 | 141.2434 | 259.6182 | 270.7125 | 278.6975
1359.8479 | 147.3885 | 577.3301 | 141.2404 | 259.5115 | 270.7442 | 278.3222
1360.8479 | 147.7933 | 576.1331 | 141.6595 | 259.6805 | 270.8582 | 277.8712