## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 1 - Circuit Simulator Data Only
Test Date: | 2010-02-23
DCSim DAQ Start Time | 12:09
DCSim Time for Synchronization | 13:03
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:01
Heat Source Start Time | 13:56
DCSim Offset | 1:47 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 6420 | seconds
Heat Source Offset | 0:55 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3299 | seconds
Heat Source Stop Time | 15:09
Test Duration | 1:13 | hour:minutes:seconds
| 4380 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-1.2188 | 123.3078 | -61.6653 | 61.4685 | 0.0096895 | 0.0012902 | 0.012249 | 0.029978 | 0.040789 | -0.034054 | 0.059276 | -61.7111 | 61.496 | -61.7844 | -61.6104 | 61.2213 | 0.18768 | -0.013733 | 0.17395 | 61.5784 | -61.8439 | -0.11902 | 0.027466 | -0.045777 | 0.054931 | -0.24719 | -0.17853 | 0.10986 | 0.073242 | 61.6516 | 61.8393 | 122.8867 | 123.1613 | -0.045777 | 123.2437 | 61.853 | -0.17853 | 123.1613 | -0.045777 | 61.853 | 122.8867 | 123.2437 | -123.2529 | -123.3124
0.53125 | 123.2941 | -61.6425 | 61.5738 | 0.00206 | 0.00086298 | 0.010754 | 0.021646 | 0.037585 | -0.030849 | 0.059703 | -61.6287 | 61.5097 | -61.7111 | -61.5097 | 61.3541 | 0.28381 | -0.10986 | 0.29297 | 61.5463 | -61.7661 | -0.068665 | -0.064087 | 0.013733 | 0.13275 | -0.21973 | -0.1236 | -0.027466 | 0.082398 | 61.5326 | 61.9354 | 122.9965 | 123.1522 | 0.013733 | 123.1888 | 61.9263 | -0.1236 | 123.1522 | 0.013733 | 61.9263 | 122.9965 | 123.1888 | -123.2849 | -123.3398
2.2188 | 123.3902 | -61.647 | 61.4868 | -0.0055695 | 0.0010766 | 0.0075495 | 0.028696 | 0.041003 | -0.035763 | 0.059917 | -61.7844 | 61.4594 | -61.8118 | -61.647 | 61.1938 | 0.13275 | -0.19684 | 0.10986 | 61.5005 | -61.8576 | -0.1648 | -0.027465 | -0.13733 | 0 | -0.29297 | -0.21057 | 0.013733 | 0.027466 | 61.4502 | 61.7569 | 122.8409 | 123.1064 | -0.13733 | 123.1476 | 61.7798 | -0.21057 | 123.1064 | -0.13733 | 61.7798 | 122.8409 | 123.1476 | -123.2986 | -123.3444
3.9844 | 123.3444 | -61.6425 | 61.5143 | 0.00206 | 0.0057764 | 0.013958 | 0.028482 | 0.040148 | -0.030849 | 0.05949 | -61.7203 | 61.5784 | -61.734 | -61.6379 | 61.2213 | 0.17853 | 0.13275 | 0.17853 | 61.647 | -61.8073 | -0.091553 | 0.064087 | -0.07782 | 0.004578 | -0.29297 | -0.16479 | 0.13275 | 0.013733 | 61.7752 | 61.821 | 122.8638 | 123.2208 | -0.07782 | 123.2895 | 61.821 | -0.16479 | 123.2208 | -0.07782 | 61.821 | 122.8638 | 123.2895 | -123.2483 | -123.3215
5.6562 | 123.2941 | -61.615 | 61.5829 | 0.0096895 | -0.00084602 | 0.014385 | 0.023142 | 0.040789 | -0.028286 | 0.056499 | -61.6287 | 61.496 | -61.6928 | -61.5189 | 61.3358 | 0.30212 | -0.13733 | 0.29297 | 61.5692 | -61.7615 | -0.07782 | -0.086975 | -0.013733 | 0.09613 | -0.24719 | -0.14648 | -0.013733 | 0.064087 | 61.4777 | 61.908 | 122.9507 | 123.111 | -0.013733 | 123.1842 | 61.9171 | -0.14648 | 123.111 | -0.013733 | 61.9171 | 122.9507 | 123.1842 | -123.2758 | -123.3444
7.4062 | 123.4085 | -61.5967 | 61.5234 | 0.0096895 | 0.0017176 | 0.012463 | 0.024851 | 0.041003 | -0.02914 | 0.058635 | -61.7294 | 61.4502 | -61.7798 | -61.6058 | 61.235 | 0.16937 | -0.18768 | 0.14648 | 61.528 | -61.8301 | -0.1831 | -0.073242 | -0.13275 | -0.009155 | -0.28839 | -0.23346 | 0.004578 | 0.050354 | 61.409 | 61.7432 | 122.8317 | 123.0469 | -0.13275 | 123.1247 | 61.7661 | -0.23346 | 123.0469 | -0.13275 | 61.7661 | 122.8317 | 123.1247 | -123.3032 | -123.3536
9.1562 | 123.3444 | -61.6516 | 61.496 | 0.00206 | 0.0034266 | 0.013104 | 0.027201 | 0.040362 | -0.030849 | 0.060131 | -61.7157 | 61.4182 | -61.8073 | -61.6058 | 61.2396 | 0.19226 | -0.27924 | 0.16479 | 61.4685 | -61.8073 | -0.15564 | -0.07782 | -0.064087 | 0.045776 | -0.25635 | -0.15564 | -0.027466 | 0.091553 | 61.3724 | 61.8164 | 122.8912 | 123.0698 | -0.064087 | 123.1201 | 61.8439 | -0.15564 | 123.0698 | -0.064087 | 61.8439 | 122.8912 | 123.1201 | -123.3032 | -123.3032
10.9062 | 123.2574 | -61.6745 | 61.5234 | 0.0096895 | 0.0053492 | 0.013104 | 0.031687 | 0.041644 | -0.030208 | 0.059703 | -61.702 | 61.5509 | -61.7615 | -61.6013 | 61.2442 | 0.20142 | -0.013733 | 0.19684 | 61.5875 | -61.8347 | -0.086975 | 0.027466 | -0.027465 | 0.073243 | -0.27923 | -0.16022 | 0.064087 | 0.05951 | 61.6608 | 61.8713 | 122.9187 | 123.2254 | -0.027465 | 123.262 | 61.8759 | -0.16022 | 123.2254 | -0.027465 | 61.8759 | 122.9187 | 123.262 | -123.2849 | -123.3582
12.6094 | 123.3536 | -61.6287 | 61.4914 | 0.0096895 | -0.0010596 | 0.0092585 | 0.027201 | 0.039935 | -0.029995 | 0.060344 | -61.6974 | 61.4273 | -61.7889 | -61.6058 | 61.235 | 0.19684 | -0.25635 | 0.14648 | 61.4548 | -61.8118 | -0.16022 | -0.064087 | -0.068665 | 0.022888 | -0.25635 | -0.18311 | -0.036621 | 0.091552 | 61.3724 | 61.7752 | 122.8638 | 123.056 | -0.068665 | 123.0835 | 61.8256 | -0.18311 | 123.056 | -0.068665 | 61.8256 | 122.8638 | 123.0835 | -123.2803 | -123.3032
14.3438 | 123.3032 | -61.6379 | 61.5005 | -0.0055695 | 0.00064938 | 0.010754 | 0.028482 | 0.040362 | -0.031704 | 0.058208 | -61.7432 | 61.5692 | -61.7706 | -61.6287 | 61.1984 | 0.17395 | 0.10529 | 0.17395 | 61.6379 | -61.7706 | -0.13275 | 0.068665 | -0.10529 | 0.009155 | -0.30212 | -0.13275 | 0.13733 | 0.027466 | 61.7432 | 61.8118 | 122.8363 | 123.2071 | -0.10529 | 123.2758 | 61.8118 | -0.13275 | 123.2071 | -0.10529 | 61.8118 | 122.8363 | 123.2758 | -123.2712 | -123.2712
16.0469 | 123.3582 | -61.6196 | 61.5097 | 0.00206 | 0.0044946 | 0.011181 | 0.026346 | 0.040362 | -0.029568 | 0.062267 | -61.6974 | 61.4502 | -61.7661 | -61.5967 | 61.2488 | 0.19226 | -0.25635 | 0.14648 | 61.4731 | -61.821 | -0.14648 | -0.05951 | -0.07782 | 0.022888 | -0.26093 | -0.20142 | -0.036622 | 0.068664 | 61.3632 | 61.7661 | 122.8683 | 123.0698 | -0.07782 | 123.0927 | 61.8118 | -0.20142 | 123.0698 | -0.07782 | 61.8118 | 122.8683 | 123.0927 | -123.2758 | -123.3307
17.8125 | 123.3124 | -61.6791 | 61.4594 | -0.0055695 | 0.0019312 | 0.01289 | 0.027841 | 0.041216 | -0.032558 | 0.059917 | -61.7752 | 61.4777 | -61.8027 | -61.6974 | 61.1343 | 0.09613 | -0.022888 | 0.068665 | 61.5372 | -61.8439 | -0.1236 | 0.01831 | -0.096131 | -0.018311 | -0.32501 | -0.16479 | 0.077819 | 0.027465 | 61.6562 | 61.7477 | 122.8134 | 123.1567 | -0.096131 | 123.2162 | 61.7752 | -0.16479 | 123.1567 | -0.096131 | 61.7752 | 122.8134 | 123.2162 | -123.262 | -123.3032
19.5781 | 123.3536 | -61.6516 | 61.441 | 0.00206 | 0.0010766 | 0.0096857 | 0.025919 | 0.042712 | -0.032558 | 0.061199 | -61.7615 | 61.4319 | -61.7935 | -61.6379 | 61.1938 | 0.15564 | -0.23346 | 0.091553 | 61.5051 | -61.8393 | -0.14191 | -0.009155 | -0.10986 | 0.013733 | -0.24719 | -0.18768 | 0.064087 | 0.032043 | 61.4182 | 61.7432 | 122.8455 | 123.0835 | -0.10986 | 123.1567 | 61.8073 | -0.18768 | 123.0835 | -0.10986 | 61.8073 | 122.8455 | 123.1567 | -123.2346 | -123.2803
21.3281 | 123.3353 | -61.5738 | 61.528 | 0.0096895 | 0.0019312 | 0.012249 | 0.023142 | 0.04143 | -0.032345 | 0.058849 | -61.6516 | 61.5234 | -61.702 | -61.5463 | 61.3083 | 0.2655 | -0.13733 | 0.25177 | 61.5509 | -61.7798 | -0.12817 | -0.004578 | -0.077819 | 0.027466 | -0.21973 | -0.20599 | 0.022888 | 0.050354 | 61.4365 | 61.8256 | 122.8821 | 123.0972 | -0.077819 | 123.1247 | 61.8393 | -0.20599 | 123.0972 | -0.077819 | 61.8393 | 122.8821 | 123.1247 | -123.23 | -123.3078
23.0938 | 123.3765 | -61.6241 | 61.4456 | 0.0096895 | 0.0064172 | 0.011395 | 0.029123 | 0.040362 | -0.033199 | 0.060985 | -61.7935 | 61.4868 | -61.8164 | -61.7065 | 61.1069 | 0.086975 | -0.064087 | 0.032043 | 61.5372 | -61.8851 | -0.19226 | 0.041198 | -0.16937 | -0.082397 | -0.33875 | -0.26093 | 0.091552 | 0.022888 | 61.5601 | 61.6562 | 122.731 | 123.111 | -0.16937 | 123.1613 | 61.7111 | -0.26093 | 123.111 | -0.16937 | 61.7111 | 122.731 | 123.1613 | -123.262 | -123.3307
24.8438 | 123.2849 | -61.5967 | 61.5417 | 0.0096895 | 0.0012902 | 0.013104 | 0.024851 | 0.041644 | -0.032558 | 0.059703 | -61.6562 | 61.5234 | -61.7203 | -61.5372 | 61.2808 | 0.25177 | 0.027466 | 0.2655 | 61.5967 | -61.7661 | -0.1236 | -0.018311 | -0.059509 | 0.05951 | -0.26093 | -0.16937 | 0.054932 | 0.064087 | 61.6241 | 61.8622 | 122.8775 | 123.1201 | -0.059509 | 123.1934 | 61.8484 | -0.16937 | 123.1201 | -0.059509 | 61.8484 | 122.8775 | 123.1934 | -123.262 | -123.3078
26.5312 | 123.317 | -61.6013 | 61.496 | 0.00206 | 0.0036402 | 0.013744 | 0.027201 | 0.04143 | -0.031277 | 0.060344 | -61.6928 | 61.4548 | -61.7889 | -61.5921 | 61.2167 | 0.18768 | -0.27924 | 0.14191 | 61.4685 | -61.8301 | -0.18768 | -0.041199 | -0.091553 | 0.009155 | -0.27924 | -0.22888 | -0.027466 | 0.09613 | 61.322 | 61.7432 | 122.818 | 123.056 | -0.091553 | 123.0698 | 61.7889 | -0.22888 | 123.056 | -0.091553 | 61.7889 | 122.818 | 123.0698 | -123.2849 | -123.3261
28.2969 | 123.317 | -61.6287 | 61.4868 | 0.00206 | 0.0019312 | 0.012249 | 0.027414 | 0.041216 | -0.031704 | 0.058422 | -61.6974 | 61.4182 | -61.7844 | -61.5875 | 61.2167 | 0.1831 | -0.2655 | 0.15564 | 61.4731 | -61.8027 | -0.15564 | -0.068664 | -0.068665 | 0.041199 | -0.27008 | -0.17395 | -0.013733 | 0.086975 | 61.3632 | 61.7844 | 122.8455 | 123.0469 | -0.068665 | 123.1018 | 61.8118 | -0.17395 | 123.0469 | -0.068665 | 61.8118 | 122.8455 | 123.1018 | -123.2712 | -123.2895
30.0625 | 123.2574 | -61.6653 | 61.5005 | 0.0096895 | 0.0029992 | 0.013317 | 0.028269 | 0.042712 | -0.031277 | 0.062053 | -61.702 | 61.4868 | -61.7889 | -61.5875 | 61.2213 | 0.19226 | -0.009155 | 0.19226 | 61.5463 | -61.8118 | -0.1236 | -0.013733 | -0.036621 | 0.07782 | -0.27924 | -0.14649 | 0.045777 | 0.086975 | 61.6562 | 61.8576 | 122.8867 | 123.1522 | -0.036621 | 123.2117 | 61.8576 | -0.14649 | 123.1522 | -0.036621 | 61.8576 | 122.8867 | 123.2117 | -123.2895 | -123.3124
31.75 | 123.3856 | -61.6241 | 61.4273 | 0.0096895 | 0.001504 | 0.01524 | 0.028055 | 0.042712 | -0.032772 | 0.059276 | -61.821 | 61.4685 | -61.8164 | -61.7065 | 61.1069 | 0.082397 | -0.045776 | 0.018311 | 61.5189 | -61.8301 | -0.19226 | 0.041199 | -0.19684 | -0.082397 | -0.32043 | -0.20599 | 0.091553 | -0.004578 | 61.5784 | 61.6425 | 122.731 | 123.0927 | -0.19684 | 123.143 | 61.7065 | -0.20599 | 123.0927 | -0.19684 | 61.7065 | 122.731 | 123.143 | -123.2437 | -123.2574
33.5156 | 123.2986 | -61.6196 | 61.4731 | -0.0055695 | 0.001504 | 0.01524 | 0.026346 | 0.041857 | -0.031063 | 0.058422 | -61.6928 | 61.4044 | -61.7477 | -61.5967 | 61.2076 | 0.18768 | -0.28839 | 0.14191 | 61.4777 | -61.821 | -0.12817 | -0.068664 | -0.073242 | 0.022888 | -0.2655 | -0.20142 | 0.004578 | 0.054932 | 61.3312 | 61.7615 | 122.8271 | 123.024 | -0.073242 | 123.0972 | 61.8073 | -0.20142 | 123.024 | -0.073242 | 61.8073 | 122.8271 | 123.0972 | -123.2208 | -123.2941
35.2188 | 123.23 | -61.6974 | 61.4868 | 0.0096895 | 0.0010766 | 0.011608 | 0.032114 | 0.042925 | -0.032345 | 0.058422 | -61.7111 | 61.4777 | -61.7569 | -61.5921 | 61.203 | 0.18768 | -0.022888 | 0.18768 | 61.5692 | -61.7844 | -0.059509 | -0.009155 | -0.013733 | 0.10529 | -0.28381 | -0.086975 | 0.082398 | 0.045776 | 61.6745 | 61.8851 | 122.9004 | 123.175 | -0.013733 | 123.2666 | 61.8851 | -0.086975 | 123.175 | -0.013733 | 61.8851 | 122.9004 | 123.2666 | -123.2437 | -123.2712
36.9844 | 123.3215 | -61.6241 | 61.4502 | 0.0096895 | 0.00064938 | 0.013531 | 0.025705 | 0.04143 | -0.030636 | 0.061412 | -61.7523 | 61.4502 | -61.7889 | -61.6333 | 61.1984 | 0.15106 | -0.21973 | 0.10986 | 61.4822 | -61.8118 | -0.16479 | 0 | -0.12817 | -0.009155 | -0.25177 | -0.18768 | 0.032044 | 0.036621 | 61.4044 | 61.734 | 122.8226 | 123.0743 | -0.12817 | 123.1064 | 61.7752 | -0.18768 | 123.0743 | -0.12817 | 61.7752 | 122.8226 | 123.1064 | -123.2391 | -123.262
38.7344 | 123.3398 | -61.6379 | 61.4182 | 0.00206 | 0.0010766 | 0.011181 | 0.024851 | 0.043139 | -0.033413 | 0.05949 | -61.7752 | 61.4319 | -61.8027 | -61.6653 | 61.1389 | 0.10071 | -0.13733 | 0.073242 | 61.528 | -61.821 | -0.16479 | 0.013733 | -0.13733 | -0.027466 | -0.27924 | -0.18311 | 0.10986 | 0.027465 | 61.5005 | 61.7111 | 122.7768 | 123.0698 | -0.13733 | 123.1659 | 61.7386 | -0.18311 | 123.0698 | -0.13733 | 61.7386 | 122.7768 | 123.1659 | -123.2208 | -123.2391
40.4219 | 123.3307 | -61.6196 | 61.4227 | 0.0096895 | 0.0023584 | 0.011822 | 0.028696 | 0.04378 | -0.032985 | 0.063335 | -61.8073 | 61.4227 | -61.7889 | -61.7157 | 61.0977 | 0.059509 | -0.036621 | 0.050354 | 61.5326 | -61.8347 | -0.16937 | 0 | -0.18768 | -0.09613 | -0.32501 | -0.21515 | 0.10986 | -0.018311 | 61.5829 | 61.6699 | 122.7173 | 123.0423 | -0.18768 | 123.1522 | 61.6791 | -0.21515 | 123.0423 | -0.18768 | 61.6791 | 122.7173 | 123.1522 | -123.2117 | -123.2574
42.1875 | 123.3398 | -61.6287 | 61.4731 | -0.0055695 | 0.0027856 | 0.014813 | 0.023355 | 0.039507 | -0.032345 | 0.060985 | -61.7523 | 61.4182 | -61.7935 | -61.6287 | 61.1755 | 0.14648 | -0.22888 | 0.11444 | 61.4868 | -61.8118 | -0.16479 | -0.054931 | -0.1236 | 0 | -0.29755 | -0.18311 | 0.013733 | 0.041199 | 61.3998 | 61.7432 | 122.8043 | 123.0469 | -0.1236 | 123.1155 | 61.7752 | -0.18311 | 123.0469 | -0.1236 | 61.7752 | 122.8043 | 123.1155 | -123.2666 | -123.2849
43.9531 | 123.3032 | -61.6196 | 61.4685 | 0.0096895 | -0.00041862 | 0.012249 | 0.02421 | 0.041644 | -0.030422 | 0.060344 | -61.6974 | 61.3724 | -61.7661 | -61.6058 | 61.2076 | 0.17853 | -0.28381 | 0.15564 | 61.4685 | -61.8027 | -0.14648 | -0.096131 | -0.07782 | 0.013733 | -0.26093 | -0.1831 | 0 | 0.068664 | 61.3358 | 61.7752 | 122.8271 | 122.9919 | -0.07782 | 123.0881 | 61.7981 | -0.1831 | 122.9919 | -0.07782 | 61.7981 | 122.8271 | 123.0881 | -123.2346 | -123.2712
45.7031 | 123.23 | -61.615 | 61.5326 | 0.00206 | -0.0010596 | 0.011608 | 0.025492 | 0.040362 | -0.032772 | 0.055644 | -61.6104 | 61.4777 | -61.6928 | -61.4731 | 61.3174 | 0.29297 | -0.11444 | 0.3067 | 61.5601 | -61.7432 | -0.07782 | -0.054932 | 0.004577 | 0.14191 | -0.21515 | -0.12817 | 0.027466 | 0.082397 | 61.5005 | 61.9217 | 122.9324 | 123.0927 | 0.004577 | 123.175 | 61.908 | -0.12817 | 123.0927 | 0.004577 | 61.908 | 122.9324 | 123.175 | -123.2254 | -123.2758
47.4062 | 123.2666 | -61.6196 | 61.5143 | 0.0096895 | 0.002572 | 0.013317 | 0.025492 | 0.038866 | -0.033413 | 0.058208 | -61.7111 | 61.5143 | -61.7203 | -61.6058 | 61.1938 | 0.1831 | 0.11444 | 0.18768 | 61.6013 | -61.7661 | -0.10071 | 0 | -0.091553 | 0.013733 | -0.32043 | -0.14648 | 0.086975 | 0.009155 | 61.734 | 61.8073 | 122.8134 | 123.1338 | -0.091553 | 123.2208 | 61.8027 | -0.14648 | 123.1338 | -0.091553 | 61.8027 | 122.8134 | 123.2208 | -123.2346 | -123.2803
49.1719 | 123.3398 | -61.5967 | 61.4822 | -0.0055695 | 0.00064938 | 0.010754 | 0.024423 | 0.042712 | -0.029995 | 0.059276 | -61.6791 | 61.409 | -61.7249 | -61.5921 | 61.1938 | 0.16022 | -0.19226 | 0.15564 | 61.5234 | -61.8027 | -0.12817 | -0.073242 | -0.082397 | 0.004578 | -0.28839 | -0.20599 | 0.041198 | 0.045777 | 61.4044 | 61.7523 | 122.7905 | 123.0057 | -0.082397 | 123.1201 | 61.7569 | -0.20599 | 123.0057 | -0.082397 | 61.7569 | 122.7905 | 123.1201 | -123.2071 | -123.2849
50.9219 | 123.23 | -61.5921 | 61.5784 | 0.00206 | -0.0014868 | 0.0081903 | 0.028269 | 0.041644 | -0.031917 | 0.058849 | -61.6241 | 61.4822 | -61.7111 | -61.4822 | 61.3037 | 0.28839 | -0.10529 | 0.29297 | 61.5463 | -61.7203 | -0.11902 | -0.09613 | -0.032044 | 0.10986 | -0.27466 | -0.12817 | -0.032043 | 0.086975 | 61.4868 | 61.8851 | 122.8958 | 123.0743 | -0.032044 | 123.1384 | 61.8805 | -0.12817 | 123.0743 | -0.032044 | 61.8805 | 122.8958 | 123.1384 | -123.2895 | -123.2986
52.625 | 123.2849 | -61.5921 | 61.5051 | 0.0096895 | 0.0021448 | 0.011181 | 0.027201 | 0.038439 | -0.03149 | 0.058635 | -61.6928 | 61.5372 | -61.6974 | -61.5738 | 61.2076 | 0.18768 | 0.086975 | 0.20142 | 61.5738 | -61.7706 | -0.10529 | 0.032043 | -0.10071 | 0.01831 | -0.29755 | -0.17853 | 0.068665 | 0.004578 | 61.6791 | 61.7935 | 122.7997 | 123.1293 | -0.10071 | 123.1659 | 61.7798 | -0.17853 | 123.1293 | -0.10071 | 61.7798 | 122.7997 | 123.1659 | -123.2025 | -123.2758
54.375 | 123.3032 | -61.5967 | 61.4639 | -0.0055695 | 0.001504 | 0.011608 | 0.031259 | 0.042498 | -0.033626 | 0.060985 | -61.7386 | 61.4227 | -61.7889 | -61.6058 | 61.1572 | 0.13733 | -0.2243 | 0.10986 | 61.5005 | -61.7523 | -0.19226 | -0.041199 | -0.14191 | -0.009155 | -0.3067 | -0.15564 | 0.036621 | 0.050354 | 61.3724 | 61.7065 | 122.7539 | 123.0194 | -0.14191 | 123.0972 | 61.734 | -0.15564 | 123.0194 | -0.14191 | 61.734 | 122.7539 | 123.0972 | -123.2529 | -123.2162
56.125 | 123.349 | -61.5555 | 61.5097 | 0.00206 | 0.002572 | 0.011608 | 0.023355 | 0.041644 | -0.031704 | 0.058849 | -61.7065 | 61.4502 | -61.7203 | -61.5784 | 61.2167 | 0.19226 | -0.11902 | 0.17853 | 61.5372 | -61.7661 | -0.16479 | -0.05951 | -0.15106 | -0.022888 | -0.29297 | -0.21057 | 0.027465 | 0.013733 | 61.4365 | 61.734 | 122.7722 | 123.0057 | -0.15106 | 123.0927 | 61.7477 | -0.21057 | 123.0057 | -0.15106 | 61.7477 | 122.7722 | 123.0927 | -123.23 | -123.2758
57.8906 | 123.1888 | -61.6562 | 61.4868 | 0.017319 | 0.0021448 | 0.0092585 | 0.029764 | 0.042071 | -0.033413 | 0.060131 | -61.6928 | 61.4868 | -61.7523 | -61.5601 | 61.203 | 0.19684 | 0 | 0.20142 | 61.5234 | -61.7706 | -0.09613 | 0 | -0.036621 | 0.09613 | -0.28381 | -0.11444 | 0.036621 | 0.059509 | 61.6562 | 61.8576 | 122.8592 | 123.143 | -0.036621 | 123.1796 | 61.853 | -0.11444 | 123.143 | -0.036621 | 61.853 | 122.8592 | 123.1796 | -123.2391 | -123.2574
59.5781 | 123.3398 | -61.5784 | 61.4639 | 0.00206 | -0.0017004 | 0.012676 | 0.022287 | 0.04143 | -0.032345 | 0.058208 | -61.7111 | 61.4273 | -61.7203 | -61.5967 | 61.1847 | 0.17853 | -0.15106 | 0.14191 | 61.528 | -61.7432 | -0.14191 | -0.036621 | -0.13275 | -0.018311 | -0.27924 | -0.16479 | 0.064087 | 0.009155 | 61.4273 | 61.7203 | 122.7631 | 123.0057 | -0.13275 | 123.1064 | 61.7569 | -0.16479 | 123.0057 | -0.13275 | 61.7569 | 122.7631 | 123.1064 | -123.1842 | -123.2071
61.3281 | 123.2025 | -61.6562 | 61.4594 | 0.00206 | 0.0012902 | 0.01289 | 0.028055 | 0.04143 | -0.03384 | 0.058422 | -61.6699 | 61.4594 | -61.7661 | -61.5829 | 61.1938 | 0.1831 | -0.027466 | 0.17395 | 61.5601 | -61.7752 | -0.10986 | 0 | -0.013733 | 0.073242 | -0.2655 | -0.11902 | 0.10071 | 0.09613 | 61.6287 | 61.8301 | 122.85 | 123.1155 | -0.013733 | 123.2162 | 61.8393 | -0.11902 | 123.1155 | -0.013733 | 61.8393 | 122.85 | 123.2162 | -123.2254 | -123.2346
63.1094 | 123.3444 | -61.5417 | 61.5051 | 0.017319 | 0.001504 | 0.011395 | 0.022928 | 0.040362 | -0.030636 | 0.060344 | -61.6791 | 61.4548 | -61.6745 | -61.5738 | 61.2213 | 0.21057 | -0.13275 | 0.17853 | 61.5738 | -61.7432 | -0.13275 | -0.050354 | -0.13733 | -0.032044 | -0.28381 | -0.20142 | 0.068665 | -0.004577 | 61.409 | 61.7203 | 122.7631 | 122.9965 | -0.13733 | 123.1155 | 61.7523 | -0.20142 | 122.9965 | -0.13733 | 61.7523 | 122.7631 | 123.1155 | -123.1796 | -123.2483
64.7969 | 123.2254 | -61.5646 | 61.5143 | -0.0055695 | 0.0010766 | 0.01289 | 0.025705 | 0.040362 | -0.032558 | 0.060344 | -61.5967 | 61.5097 | -61.6791 | -61.496 | 61.2946 | 0.28381 | -0.14648 | 0.27924 | 61.5463 | -61.7294 | -0.11444 | -0.004577 | -0.032044 | 0.068664 | -0.21973 | -0.16479 | 0.032044 | 0.082397 | 61.4182 | 61.8439 | 122.8592 | 123.0743 | -0.032044 | 123.111 | 61.8484 | -0.16479 | 123.0743 | -0.032044 | 61.8484 | 122.8592 | 123.111 | -123.1934 | -123.2437
66.5469 | 123.3398 | -61.5417 | 61.4868 | -0.0055695 | 0.0023584 | 0.011608 | 0.024637 | 0.040362 | -0.031063 | 0.058422 | -61.6837 | 61.4548 | -61.7157 | -61.5692 | 61.1984 | 0.20142 | -0.13733 | 0.16022 | 61.5372 | -61.7798 | -0.17395 | -0.032043 | -0.14191 | -0.027466 | -0.28839 | -0.23804 | 0.050354 | 0.032043 | 61.4044 | 61.702 | 122.7402 | 122.9965 | -0.14191 | 123.0789 | 61.7432 | -0.23804 | 122.9965 | -0.14191 | 61.7432 | 122.7402 | 123.0789 | -123.2025 | -123.2666
68.25 | 123.3353 | -61.5463 | 61.4868 | -0.013199 | 0.0019312 | 0.011608 | 0.02656 | 0.040362 | -0.032558 | 0.059062 | -61.6882 | 61.4548 | -61.7249 | -61.5784 | 61.1847 | 0.16022 | -0.12817 | 0.14191 | 61.5234 | -61.7706 | -0.17853 | -0.032043 | -0.14191 | -0.032043 | -0.30212 | -0.2243 | 0.036621 | 0.036622 | 61.4182 | 61.6882 | 122.731 | 123.0011 | -0.14191 | 123.0698 | 61.7065 | -0.2243 | 123.0011 | -0.14191 | 61.7065 | 122.731 | 123.0698 | -123.2117 | -123.2574
70 | 123.3307 | -61.5463 | 61.4822 | 0.00206 | -0.00063242 | 0.0092585 | 0.026987 | 0.039507 | -0.03384 | 0.060344 | -61.7111 | 61.4319 | -61.7386 | -61.5738 | 61.1984 | 0.16937 | -0.15106 | 0.13733 | 61.496 | -61.7752 | -0.19226 | -0.050354 | -0.16479 | -0.027466 | -0.28381 | -0.22888 | 0.013733 | 0.027465 | 61.3953 | 61.6837 | 122.7448 | 122.9782 | -0.16479 | 123.0423 | 61.7157 | -0.22888 | 122.9782 | -0.16479 | 61.7157 | 122.7448 | 123.0423 | -123.2208 | -123.2574
71.6719 | 123.3307 | -61.6287 | 61.3861 | -0.0055695 | 0.0010766 | 0.011822 | 0.032968 | 0.042712 | -0.035335 | 0.058635 | -61.7798 | 61.4319 | -61.7798 | -61.6653 | 61.0886 | 0.068665 | -0.068665 | 0.032043 | 61.5051 | -61.8073 | -0.15106 | 0.045777 | -0.15106 | -0.036621 | -0.29755 | -0.17853 | 0.11902 | 0 | 61.5601 | 61.6608 | 122.7173 | 123.0606 | -0.15106 | 123.1338 | 61.6974 | -0.17853 | 123.0606 | -0.15106 | 61.6974 | 122.7173 | 123.1338 | -123.1659 | -123.1934
73.4375 | 123.2117 | -61.6333 | 61.4502 | -0.0055695 | 0.0029992 | 0.012676 | 0.0319 | 0.041644 | -0.03384 | 0.060131 | -61.7065 | 61.4594 | -61.7569 | -61.6013 | 61.1526 | 0.1236 | -0.041199 | 0.11902 | 61.5143 | -61.7844 | -0.1236 | 0.009156 | -0.073242 | 0.032044 | -0.29755 | -0.15106 | 0.064087 | 0.050354 | 61.5921 | 61.7523 | 122.7859 | 123.0927 | -0.073242 | 123.1476 | 61.7569 | -0.15106 | 123.0927 | -0.073242 | 61.7569 | 122.7859 | 123.1476 | -123.2071 | -123.2346
75.1875 | 123.2025 | -61.647 | 61.4502 | 0.0096895 | 0.0010766 | 0.012463 | 0.027414 | 0.042498 | -0.035335 | 0.05949 | -61.6974 | 61.5051 | -61.7203 | -61.5646 | 61.1847 | 0.19226 | 0.082397 | 0.19226 | 61.5829 | -61.7477 | -0.073242 | 0.054932 | -0.050354 | 0.082398 | -0.2655 | -0.10071 | 0.13275 | 0.022888 | 61.7294 | 61.8393 | 122.8317 | 123.1522 | -0.050354 | 123.23 | 61.8393 | -0.10071 | 123.1522 | -0.050354 | 61.8393 | 122.8317 | 123.23 | -123.1705 | -123.1979
76.875 | 123.1705 | -61.6699 | 61.4777 | 0.00206 | 0.00064938 | 0.0086175 | 0.02891 | 0.043139 | -0.030636 | 0.059703 | -61.6791 | 61.4639 | -61.7294 | -61.5646 | 61.1893 | 0.1831 | -0.009155 | 0.18768 | 61.5234 | -61.7889 | -0.059509 | -0.013733 | -0.009155 | 0.10529 | -0.28839 | -0.11902 | 0.045776 | 0.050354 | 61.6608 | 61.8576 | 122.8592 | 123.1338 | -0.009155 | 123.1934 | 61.853 | -0.11902 | 123.1338 | -0.009155 | 61.853 | 122.8592 | 123.1934 | -123.2071 | -123.2666
78.6406 | 123.2712 | -61.6013 | 61.4548 | 0.017319 | 0.00043578 | 0.013744 | 0.028269 | 0.042284 | -0.033199 | 0.060771 | -61.6516 | 61.3861 | -61.7477 | -61.5738 | 61.203 | 0.18768 | -0.27924 | 0.14191 | 61.4502 | -61.7706 | -0.14649 | -0.068665 | -0.050354 | 0.027465 | -0.25177 | -0.16937 | -0.004578 | 0.096131 | 61.322 | 61.7432 | 122.8043 | 122.9874 | -0.050354 | 123.0515 | 61.7889 | -0.16937 | 122.9874 | -0.050354 | 61.7889 | 122.8043 | 123.0515 | -123.2025 | -123.2254
80.3906 | 123.2666 | -61.5417 | 61.5097 | 0.00206 | 0.001504 | 0.012249 | 0.02421 | 0.03908 | -0.031917 | 0.057781 | -61.615 | 61.4777 | -61.6745 | -61.5097 | 61.2762 | 0.27924 | -0.14648 | 0.27466 | 61.5143 | -61.7386 | -0.13275 | -0.032044 | -0.073242 | 0.032043 | -0.23346 | -0.19684 | 0.004577 | 0.05951 | 61.3953 | 61.8164 | 122.818 | 123.0194 | -0.073242 | 123.056 | 61.821 | -0.19684 | 123.0194 | -0.073242 | 61.821 | 122.818 | 123.056 | -123.1842 | -123.2483
82.1562 | 123.3215 | -61.5692 | 61.4685 | 0.0096895 | 0.00022218 | 0.0077631 | 0.023996 | 0.040148 | -0.032131 | 0.059917 | -61.6837 | 61.4227 | -61.7294 | -61.5784 | 61.171 | 0.16937 | -0.17853 | 0.13275 | 61.4822 | -61.7661 | -0.16022 | -0.045777 | -0.11444 | -0.009155 | -0.29755 | -0.19684 | 0.013733 | 0.045776 | 61.3907 | 61.702 | 122.7402 | 122.9919 | -0.11444 | 123.0515 | 61.7386 | -0.19684 | 122.9919 | -0.11444 | 61.7386 | 122.7402 | 123.0515 | -123.1979 | -123.2346
83.9219 | 123.1888 | -61.6287 | 61.4456 | 0.00206 | 0.004281 | 0.014172 | 0.030832 | 0.041003 | -0.030422 | 0.058635 | -61.6379 | 61.5097 | -61.7249 | -61.5509 | 61.1938 | 0.19684 | 0.013733 | 0.21057 | 61.5189 | -61.7752 | -0.096131 | 0.064087 | -0.009155 | 0.07782 | -0.25177 | -0.14648 | 0.073242 | 0.086976 | 61.6425 | 61.8393 | 122.8226 | 123.1384 | -0.009155 | 123.1476 | 61.8256 | -0.14648 | 123.1384 | -0.009155 | 61.8256 | 122.8226 | 123.1476 | -123.1705 | -123.2208
85.6875 | 123.2483 | -61.6104 | 61.3953 | 0.00206 | 0.0040674 | 0.01054 | 0.02955 | 0.042071 | -0.033413 | 0.059062 | -61.7477 | 61.4731 | -61.7615 | -61.6425 | 61.0886 | 0.082397 | 0 | 0.073242 | 61.528 | -61.821 | -0.15106 | 0.077819 | -0.13733 | -0.032043 | -0.3067 | -0.21057 | 0.13275 | 0.013733 | 61.6104 | 61.6837 | 122.699 | 123.0835 | -0.13733 | 123.1384 | 61.6928 | -0.21057 | 123.0835 | -0.13733 | 61.6928 | 122.699 | 123.1384 | -123.1567 | -123.2162
87.3906 | 123.2758 | -61.5829 | 61.4044 | 0.0096895 | 0.002572 | 0.010754 | 0.029123 | 0.043566 | -0.030849 | 0.060131 | -61.7294 | 61.4182 | -61.7706 | -61.6013 | 61.1389 | 0.12817 | -0.19226 | 0.10071 | 61.4731 | -61.7798 | -0.18768 | 0.013733 | -0.14648 | -0.01831 | -0.2655 | -0.19684 | 0.068664 | 0.041199 | 61.3907 | 61.6837 | 122.7219 | 123.0011 | -0.14648 | 123.056 | 61.7111 | -0.19684 | 123.0011 | -0.14648 | 61.7111 | 122.7219 | 123.056 | -123.175 | -123.1842
89.1406 | 123.1979 | -61.6516 | 61.4456 | 0.00206 | 0.0036402 | 0.012035 | 0.027841 | 0.041857 | -0.030849 | 0.059062 | -61.6882 | 61.4731 | -61.7386 | -61.5875 | 61.1618 | 0.16479 | -0.018311 | 0.16022 | 61.5143 | -61.7844 | -0.086975 | 0.027465 | -0.036621 | 0.064087 | -0.28381 | -0.13275 | 0.068664 | 0.050354 | 61.6333 | 61.8118 | 122.8134 | 123.1247 | -0.036621 | 123.1659 | 61.8164 | -0.13275 | 123.1247 | -0.036621 | 61.8164 | 122.8134 | 123.1659 | -123.1842 | -123.23
90.9062 | 123.2712 | -61.5509 | 61.4594 | -0.013199 | -0.00063242 | 0.014172 | 0.022714 | 0.039721 | -0.032345 | 0.058422 | -61.6608 | 61.3861 | -61.6974 | -61.5646 | 61.1984 | 0.1831 | -0.25177 | 0.14191 | 61.4319 | -61.7889 | -0.14648 | -0.073243 | -0.10986 | -0.013733 | -0.26093 | -0.23804 | -0.027466 | 0.036621 | 61.2991 | 61.6928 | 122.7493 | 122.937 | -0.10986 | 122.9828 | 61.734 | -0.23804 | 122.937 | -0.10986 | 61.734 | 122.7493 | 122.9828 | -123.1567 | -123.2483
92.6094 | 123.2986 | -61.5601 | 61.4685 | 0.00206 | 0.0012902 | 0.0092585 | 0.02186 | 0.040362 | -0.030849 | 0.058849 | -61.6653 | 61.409 | -61.7203 | -61.5784 | 61.1755 | 0.17853 | -0.19226 | 0.14648 | 61.4777 | -61.7432 | -0.16022 | -0.059509 | -0.10528 | -0.01831 | -0.29297 | -0.1831 | 0.009155 | 0.054932 | 61.3678 | 61.7065 | 122.7356 | 122.9691 | -0.10528 | 123.0377 | 61.7386 | -0.1831 | 122.9691 | -0.10528 | 61.7386 | 122.7356 | 123.0377 | -123.1888 | -123.2117
94.3594 | 123.2254 | -61.5921 | 61.4548 | 0.00206 | 0.00086298 | 0.013317 | 0.028269 | 0.038439 | -0.029781 | 0.057567 | -61.6791 | 61.528 | -61.6837 | -61.5646 | 61.1801 | 0.18768 | 0.10986 | 0.18768 | 61.5646 | -61.7615 | -0.091553 | 0.073242 | -0.086975 | 0.027466 | -0.27466 | -0.16937 | 0.10986 | 0.004578 | 61.702 | 61.7798 | 122.7722 | 123.1201 | -0.086975 | 123.1567 | 61.7798 | -0.16937 | 123.1201 | -0.086975 | 61.7798 | 122.7722 | 123.1567 | -123.1384 | -123.2162
96.1094 | 123.2162 | -61.5372 | 61.4822 | 0.0096895 | 0.002572 | 0.01524 | 0.02656 | 0.038653 | -0.030208 | 0.05714 | -61.647 | 61.5051 | -61.6791 | -61.5738 | 61.1893 | 0.20142 | 0.07782 | 0.20599 | 61.5738 | -61.7569 | -0.14191 | 0.022888 | -0.10986 | -0.036622 | -0.29297 | -0.21973 | 0.091553 | 0.032043 | 61.615 | 61.7432 | 122.7264 | 123.0423 | -0.10986 | 123.111 | 61.7386 | -0.21973 | 123.0423 | -0.10986 | 61.7386 | 122.7264 | 123.111 | -123.1613 | -123.2391
97.8594 | 123.2529 | -61.5829 | 61.4319 | 0.00206 | 0.0017176 | 0.013104 | 0.026773 | 0.041003 | -0.034481 | 0.058849 | -61.647 | 61.3907 | -61.7294 | -61.5601 | 61.1801 | 0.18768 | -0.2655 | 0.16479 | 61.4273 | -61.8027 | -0.14648 | -0.041199 | -0.064087 | 0.022888 | -0.25177 | -0.21973 | -0.004578 | 0.082397 | 61.3174 | 61.7477 | 122.7631 | 122.9736 | -0.064087 | 123.0103 | 61.7706 | -0.21973 | 122.9736 | -0.064087 | 61.7706 | 122.7631 | 123.0103 | -123.1613 | -123.2346
99.6094 | 123.2483 | -61.5829 | 61.4365 | 0.0096895 | -0.00084602 | 0.011181 | 0.030618 | 0.042712 | -0.032345 | 0.060131 | -61.6791 | 61.3586 | -61.7386 | -61.5509 | 61.1847 | 0.20142 | -0.27466 | 0.17395 | 61.4273 | -61.7432 | -0.15564 | -0.077819 | -0.09613 | 0.032044 | -0.25177 | -0.16022 | -0.009155 | 0.059509 | 61.3083 | 61.7569 | 122.7676 | 122.9416 | -0.09613 | 123.0103 | 61.7844 | -0.16022 | 122.9416 | -0.09613 | 61.7844 | 122.7676 | 123.0103 | -123.175 | -123.1796
101.375 | 123.1659 | -61.5829 | 61.5234 | 0.00206 | 0.0012902 | 0.0088311 | 0.025705 | 0.041216 | -0.03149 | 0.057567 | -61.5875 | 61.4639 | -61.6379 | -61.4639 | 61.2671 | 0.29755 | -0.10071 | 0.3067 | 61.5326 | -61.7111 | -0.054931 | -0.059509 | -0.004577 | 0.11902 | -0.25635 | -0.12817 | 0.009156 | 0.050354 | 61.4822 | 61.8896 | 122.85 | 123.0469 | -0.004577 | 123.1155 | 61.8805 | -0.12817 | 123.0469 | -0.004577 | 61.8805 | 122.85 | 123.1155 | -123.1613 | -123.2346
103.0781 | 123.2208 | -61.5829 | 61.4685 | 0.0096895 | 0.00064938 | 0.013958 | 0.028269 | 0.040789 | -0.031704 | 0.060131 | -61.6837 | 61.5326 | -61.6928 | -61.5738 | 61.1481 | 0.16479 | 0.10986 | 0.17853 | 61.5738 | -61.7615 | -0.10986 | 0.064087 | -0.10071 | 0.009155 | -0.32043 | -0.17853 | 0.10529 | 0.009155 | 61.6928 | 61.7615 | 122.731 | 123.1155 | -0.10071 | 123.1567 | 61.7477 | -0.17853 | 123.1155 | -0.10071 | 61.7477 | 122.731 | 123.1567 | -123.1613 | -123.23
104.8125 | 123.2895 | -61.5921 | 61.3998 | 0.0096895 | 0.00086298 | 0.0092585 | 0.028482 | 0.041644 | -0.032345 | 0.059276 | -61.7661 | 61.3998 | -61.7844 | -61.6745 | 61.0748 | 0.068665 | -0.059509 | 0.036621 | 61.496 | -61.7889 | -0.19226 | 0 | -0.17395 | -0.082398 | -0.32501 | -0.19684 | 0.096131 | 0.018311 | 61.5326 | 61.6287 | 122.6669 | 122.9919 | -0.17395 | 123.0881 | 61.6608 | -0.19684 | 122.9919 | -0.17395 | 61.6608 | 122.6669 | 123.0881 | -123.1842 | -123.1888
106.5625 | 123.1796 | -61.5601 | 61.4914 | -0.0055695 | 0.0023584 | 0.010754 | 0.026132 | 0.040575 | -0.034481 | 0.058422 | -61.6196 | 61.4822 | -61.6653 | -61.528 | 61.2122 | 0.2243 | 0.045776 | 0.24261 | 61.5601 | -61.7065 | -0.10528 | -0.009155 | -0.059509 | 0.032044 | -0.27924 | -0.14648 | 0.068665 | 0.045776 | 61.6058 | 61.8027 | 122.7722 | 123.0423 | -0.059509 | 123.1201 | 61.7844 | -0.14648 | 123.0423 | -0.059509 | 61.7844 | 122.7722 | 123.1201 | -123.1567 | -123.1979
108.2812 | 123.2895 | -61.5784 | 61.3678 | 0.0096895 | 0.0027856 | 0.010326 | 0.030832 | 0.042712 | -0.03384 | 0.060344 | -61.7661 | 61.4319 | -61.7889 | -61.6608 | 61.0474 | 0.068665 | -0.041199 | 0.022888 | 61.5189 | -61.7935 | -0.21057 | 0.064087 | -0.18768 | -0.082398 | -0.32044 | -0.21515 | 0.15106 | 0.022888 | 61.5372 | 61.6013 | 122.6257 | 123.0103 | -0.18768 | 123.0972 | 61.647 | -0.21515 | 123.0103 | -0.18768 | 61.647 | 122.6257 | 123.0972 | -123.1567 | -123.1613
110.0312 | 123.2071 | -61.5829 | 61.4456 | 0.00206 | 0.0027856 | 0.013958 | 0.025919 | 0.041003 | -0.033626 | 0.059703 | -61.6745 | 61.5005 | -61.6882 | -61.5784 | 61.1526 | 0.17853 | 0.13275 | 0.18768 | 61.5784 | -61.7203 | -0.10529 | 0.054931 | -0.091553 | 0.004578 | -0.29297 | -0.13733 | 0.13275 | 0.013732 | 61.7157 | 61.7706 | 122.7356 | 123.0835 | -0.091553 | 123.1613 | 61.7615 | -0.13733 | 123.0835 | -0.091553 | 61.7615 | 122.7356 | 123.1613 | -123.1338 | -123.1659
111.7969 | 123.2986 | -61.5234 | 61.4365 | 0.00206 | 0.0021448 | 0.0098993 | 0.025705 | 0.040575 | -0.031704 | 0.058208 | -61.6608 | 61.4456 | -61.6882 | -61.5646 | 61.1664 | 0.18768 | -0.14191 | 0.14191 | 61.4731 | -61.7569 | -0.16479 | 0.009156 | -0.13733 | -0.041199 | -0.27008 | -0.23346 | 0.036621 | 0.027465 | 61.3815 | 61.6653 | 122.6898 | 122.9691 | -0.13733 | 122.9965 | 61.7111 | -0.23346 | 122.9691 | -0.13733 | 61.7111 | 122.6898 | 122.9965 | -123.1247 | -123.1934
113.4844 | 123.1293 | -61.5555 | 61.5143 | 0.00206 | 0.00022218 | 0.010754 | 0.025278 | 0.03908 | -0.031277 | 0.058635 | -61.5509 | 61.4777 | -61.6608 | -61.4456 | 61.2762 | 0.31586 | -0.10986 | 0.31586 | 61.4914 | -61.7111 | -0.10529 | -0.036621 | 0.004578 | 0.10986 | -0.23804 | -0.15564 | -0.022888 | 0.10986 | 61.4456 | 61.8713 | 122.8317 | 123.0331 | 0.004578 | 123.0469 | 61.8713 | -0.15564 | 123.0331 | 0.004578 | 61.8713 | 122.8317 | 123.0469 | -123.175 | -123.2254
115.25 | 123.1476 | -61.5417 | 61.5463 | 0.00206 | 0.00064938 | 0.011608 | 0.02421 | 0.037371 | -0.030849 | 0.057353 | -61.5463 | 61.4456 | -61.647 | -61.4365 | 61.2991 | 0.28381 | -0.11444 | 0.30212 | 61.5097 | -61.7249 | -0.10529 | -0.10071 | -0.004578 | 0.10529 | -0.24719 | -0.18311 | -0.036621 | 0.10071 | 61.4273 | 61.8439 | 122.8409 | 122.9874 | -0.004578 | 123.0515 | 61.8256 | -0.18311 | 122.9874 | -0.004578 | 61.8256 | 122.8409 | 123.0515 | -123.1934 | -123.2712
117.0156 | 123.1476 | -61.5601 | 61.5143 | 0.00206 | 0.002572 | 0.0088311 | 0.025705 | 0.038866 | -0.032772 | 0.059917 | -61.5692 | 61.4365 | -61.6745 | -61.441 | 61.2762 | 0.28839 | -0.15106 | 0.31128 | 61.5234 | -61.6974 | -0.11444 | -0.07782 | -0.009155 | 0.11902 | -0.23804 | -0.13733 | 0.009155 | 0.10529 | 61.409 | 61.8713 | 122.8363 | 122.9965 | -0.009155 | 123.0835 | 61.8484 | -0.13733 | 122.9965 | -0.009155 | 61.8484 | 122.8363 | 123.0835 | -123.1888 | -123.2117
118.7812 | 123.2666 | -61.5234 | 61.441 | 0.00206 | 0.0029992 | 0.01054 | 0.027414 | 0.039721 | -0.031704 | 0.058635 | -61.6608 | 61.4044 | -61.6974 | -61.5417 | 61.1526 | 0.16937 | -0.19226 | 0.16022 | 61.4731 | -61.7523 | -0.17395 | -0.036621 | -0.13733 | -0.018311 | -0.28839 | -0.22888 | 0.032043 | 0.036621 | 61.3312 | 61.6837 | 122.6761 | 122.9279 | -0.13733 | 122.9965 | 61.6928 | -0.22888 | 122.9279 | -0.13733 | 61.6928 | 122.6761 | 122.9965 | -123.1384 | -123.1934
120.4688 | 123.2162 | -61.5555 | 61.4227 | 0.00206 | 0.0027856 | 0.013317 | 0.026132 | 0.040575 | -0.032131 | 0.059917 | -61.6425 | 61.3358 | -61.7523 | -61.5372 | 61.1664 | 0.17853 | -0.29755 | 0.15106 | 61.4227 | -61.7432 | -0.19684 | -0.086975 | -0.086975 | 0.018311 | -0.25635 | -0.18768 | 0 | 0.10986 | 61.2579 | 61.7065 | 122.7219 | 122.8912 | -0.086975 | 122.9782 | 61.734 | -0.18768 | 122.8912 | -0.086975 | 61.734 | 122.7219 | 122.9782 | -123.175 | -123.1659
122.1562 | 123.1705 | -61.5463 | 61.496 | -0.0055695 | 0.0010766 | 0.010754 | 0.027628 | 0.03908 | -0.030422 | 0.057994 | -61.5921 | 61.4456 | -61.6608 | -61.4731 | 61.2122 | 0.26093 | 0.022888 | 0.2655 | 61.5509 | -61.6974 | -0.11444 | -0.050354 | -0.045776 | 0.073243 | -0.28381 | -0.15106 | 0.054931 | 0.068665 | 61.5692 | 61.8118 | 122.7585 | 122.9919 | -0.045776 | 123.0972 | 61.8073 | -0.15106 | 122.9919 | -0.045776 | 61.8073 | 122.7585 | 123.0972 | -123.1567 | -123.1934
123.8594 | 123.1338 | -61.6333 | 61.3998 | 0.0096895 | 0.0012902 | 0.013104 | 0.029123 | 0.041003 | -0.033199 | 0.057994 | -61.647 | 61.4502 | -61.7249 | -61.5234 | 61.1572 | 0.18768 | -0.022888 | 0.20142 | 61.5326 | -61.7249 | -0.091553 | 0.050354 | -0.013733 | 0.10986 | -0.24261 | -0.091553 | 0.13275 | 0.07782 | 61.6104 | 61.8347 | 122.7905 | 123.0835 | -0.013733 | 123.1659 | 61.821 | -0.091553 | 123.0835 | -0.013733 | 61.821 | 122.7905 | 123.1659 | -123.1247 | -123.1247
125.625 | 123.1522 | -61.6058 | 61.4136 | -0.0055695 | 0.0023584 | 0.011181 | 0.029978 | 0.042071 | -0.034054 | 0.059276 | -61.6653 | 61.4365 | -61.7523 | -61.5829 | 61.1069 | 0.13275 | -0.032043 | 0.11902 | 61.4731 | -61.7661 | -0.14648 | 0.022888 | -0.059509 | 0.022888 | -0.3067 | -0.16022 | 0.059509 | 0.086975 | 61.5738 | 61.7249 | 122.7127 | 123.0423 | -0.059509 | 123.0789 | 61.7386 | -0.16022 | 123.0423 | -0.059509 | 61.7386 | 122.7127 | 123.0789 | -123.1659 | -123.1796
127.3438 | 123.1522 | -61.5921 | 61.4044 | 0.0096895 | 8.578e-06 | 0.0092585 | 0.027201 | 0.042284 | -0.035549 | 0.058849 | -61.6241 | 61.4182 | -61.7386 | -61.5601 | 61.1389 | 0.16937 | -0.027466 | 0.14648 | 61.5143 | -61.7523 | -0.14648 | 0.013733 | -0.032044 | 0.032043 | -0.2655 | -0.16022 | 0.10986 | 0.11444 | 61.5646 | 61.7386 | 122.731 | 123.0103 | -0.032044 | 123.1064 | 61.7615 | -0.16022 | 123.0103 | -0.032044 | 61.7615 | 122.731 | 123.1064 | -123.143 | -123.1567
129.1094 | 123.1705 | -61.5555 | 61.4685 | 0.00206 | 0.0010766 | 0.015453 | 0.025919 | 0.04143 | -0.032772 | 0.05949 | -61.647 | 61.5051 | -61.6882 | -61.5463 | 61.1572 | 0.18768 | 0.10529 | 0.19684 | 61.5829 | -61.7157 | -0.13275 | 0.036621 | -0.091553 | 0.009155 | -0.31128 | -0.16022 | 0.11444 | 0.041198 | 61.6608 | 61.7523 | 122.7127 | 123.0606 | -0.091553 | 123.1384 | 61.7432 | -0.16022 | 123.0606 | -0.091553 | 61.7432 | 122.7127 | 123.1384 | -123.1567 | -123.1842
130.7969 | 123.2574 | -61.5692 | 61.3678 | 0.00206 | 0.00022218 | 0.0096857 | 0.028055 | 0.041216 | -0.031917 | 0.060344 | -61.7294 | 61.409 | -61.7615 | -61.647 | 61.0748 | 0.086975 | -0.13733 | 0.041199 | 61.4777 | -61.7844 | -0.19226 | 0.041199 | -0.16022 | -0.07782 | -0.29297 | -0.21515 | 0.10986 | 0.032044 | 61.4319 | 61.6104 | 122.644 | 122.9782 | -0.16022 | 123.0469 | 61.6562 | -0.21515 | 122.9782 | -0.16022 | 61.6562 | 122.644 | 123.0469 | -123.1293 | -123.1522
132.7344 | 123.23 | -61.5829 | 61.377 | 0.0096895 | 0.00043578 | 0.015026 | 0.027201 | 0.041216 | -0.033626 | 0.059703 | -61.7386 | 61.4136 | -61.7569 | -61.647 | 61.0428 | 0.073242 | -0.013733 | 0.036621 | 61.5189 | -61.7752 | -0.17395 | 0.036621 | -0.15564 | -0.064087 | -0.33417 | -0.19226 | 0.14191 | 0.018311 | 61.5692 | 61.6196 | 122.6257 | 122.9965 | -0.15564 | 123.1018 | 61.6562 | -0.19226 | 122.9965 | -0.15564 | 61.6562 | 122.6257 | 123.1018 | -123.1338 | -123.1522
134.5469 | 123.2025 | -61.5372 | 61.441 | 0.0096895 | 0.001504 | 0.013744 | 0.023783 | 0.040148 | -0.029995 | 0.060131 | -61.6241 | 61.3861 | -61.6837 | -61.5417 | 61.1755 | 0.20142 | -0.27008 | 0.15106 | 61.4273 | -61.7752 | -0.14648 | -0.054932 | -0.086976 | -0.004578 | -0.2655 | -0.23804 | -0.013733 | 0.059509 | 61.2671 | 61.6882 | 122.7127 | 122.9233 | -0.086976 | 122.9645 | 61.7386 | -0.23804 | 122.9233 | -0.086976 | 61.7386 | 122.7127 | 122.9645 | -123.1247 | -123.2162
136.25 | 123.2483 | -61.5005 | 61.4365 | -0.0055695 | 0.00022218 | 0.012676 | 0.022287 | 0.037798 | -0.030636 | 0.057353 | -61.6562 | 61.4365 | -61.6699 | -61.5372 | 61.1938 | 0.21057 | -0.13275 | 0.19226 | 61.4914 | -61.7386 | -0.16937 | 0 | -0.15564 | -0.036621 | -0.24261 | -0.23804 | 0.054932 | 0.013733 | 61.3678 | 61.6928 | 122.6944 | 122.937 | -0.15564 | 122.9919 | 61.7111 | -0.23804 | 122.937 | -0.15564 | 61.7111 | 122.6944 | 122.9919 | -123.1064 | -123.175
137.9844 | 123.1155 | -61.5463 | 61.496 | 0.00206 | -0.00020502 | 0.013531 | 0.028055 | 0.040148 | -0.029995 | 0.059062 | -61.5555 | 61.4594 | -61.6333 | -61.4319 | 61.2579 | 0.29755 | -0.10529 | 0.31128 | 61.5234 | -61.702 | -0.086975 | -0.036621 | -0.009155 | 0.11444 | -0.23804 | -0.15564 | 0.027465 | 0.07782 | 61.441 | 61.8576 | 122.8043 | 123.0057 | -0.009155 | 123.0698 | 61.8439 | -0.15564 | 123.0057 | -0.009155 | 61.8439 | 122.8043 | 123.0698 | -123.1293 | -123.1979
139.7188 | 123.1476 | -61.5692 | 61.4227 | 0.0096895 | 0.001504 | 0.011181 | 0.030191 | 0.040148 | -0.032772 | 0.062053 | -61.6608 | 61.5051 | -61.6653 | -61.5646 | 61.1389 | 0.17853 | 0.091553 | 0.19226 | 61.5555 | -61.7203 | -0.09613 | 0.082398 | -0.091553 | 0.004578 | -0.28381 | -0.15106 | 0.13275 | 0.004577 | 61.6608 | 61.7615 | 122.7081 | 123.0743 | -0.091553 | 123.1247 | 61.7477 | -0.15106 | 123.0743 | -0.091553 | 61.7477 | 122.7081 | 123.1247 | -123.0881 | -123.143
141.4062 | 123.1705 | -61.528 | 61.4731 | 0.00206 | 8.578e-06 | 0.0066949 | 0.024423 | 0.03908 | -0.031704 | 0.060131 | -61.5738 | 61.4319 | -61.6333 | -61.4456 | 61.2625 | 0.28839 | -0.14191 | 0.28381 | 61.4777 | -61.702 | -0.10529 | -0.041198 | -0.045777 | 0.082397 | -0.21057 | -0.17395 | 0.004578 | 0.059509 | 61.3861 | 61.8118 | 122.7905 | 122.9599 | -0.045777 | 123.0057 | 61.8164 | -0.17395 | 122.9599 | -0.045777 | 61.8164 | 122.7905 | 123.0057 | -123.1064 | -123.175
143.0781 | 123.1659 | -61.5601 | 61.4227 | 0.00206 | -0.00020502 | 0.014813 | 0.028482 | 0.038226 | -0.03149 | 0.057994 | -61.6562 | 61.496 | -61.6928 | -61.5463 | 61.1298 | 0.16937 | 0.12817 | 0.19684 | 61.5784 | -61.7111 | -0.13275 | 0.073243 | -0.09613 | 0.013733 | -0.29297 | -0.15106 | 0.15564 | 0.036621 | 61.6882 | 61.7569 | 122.6898 | 123.056 | -0.09613 | 123.1384 | 61.7294 | -0.15106 | 123.056 | -0.09613 | 61.7294 | 122.6898 | 123.1384 | -123.1155 | -123.1338
144.75 | 123.1293 | -61.5967 | 61.3815 | -0.0055695 | -0.00020502 | 0.014385 | 0.031687 | 0.042925 | -0.032985 | 0.060558 | -61.6608 | 61.4227 | -61.7249 | -61.5921 | 61.0748 | 0.11902 | -0.027466 | 0.11444 | 61.4822 | -61.7432 | -0.12817 | 0.041198 | -0.064087 | 0.004578 | -0.3067 | -0.14648 | 0.10071 | 0.064087 | 61.5692 | 61.7111 | 122.6715 | 123.0194 | -0.064087 | 123.0789 | 61.7157 | -0.14648 | 123.0194 | -0.064087 | 61.7157 | 122.6715 | 123.0789 | -123.1064 | -123.1247
146.4375 | 123.23 | -61.528 | 61.4594 | 0.00206 | 0.0010766 | 0.01289 | 0.02421 | 0.040362 | -0.030636 | 0.060771 | -61.6104 | 61.4182 | -61.6699 | -61.5097 | 61.2122 | 0.24261 | -0.11444 | 0.23804 | 61.496 | -61.7111 | -0.14191 | -0.041199 | -0.082398 | 0.01831 | -0.24719 | -0.18311 | 0.036621 | 0.059509 | 61.4136 | 61.7661 | 122.7402 | 122.9462 | -0.082398 | 123.024 | 61.7706 | -0.18311 | 122.9462 | -0.082398 | 61.7706 | 122.7402 | 123.024 | -123.1293 | -123.1705
148.1562 | 123.2758 | -61.4868 | 61.4365 | 0.00206 | -0.0014868 | 0.010113 | 0.024637 | 0.037585 | -0.030636 | 0.058635 | -61.6516 | 61.3998 | -61.6745 | -61.5463 | 61.1481 | 0.19226 | -0.15106 | 0.13733 | 61.4273 | -61.7111 | -0.18768 | -0.036621 | -0.1648 | -0.05951 | -0.28839 | -0.22431 | -0.009155 | 0.022889 | 61.3358 | 61.6241 | 122.6349 | 122.8867 | -0.1648 | 122.9141 | 61.6791 | -0.22431 | 122.8867 | -0.1648 | 61.6791 | 122.6349 | 122.9141 | -123.111 | -123.1476
149.875 | 123.1155 | -61.5646 | 61.4777 | 0.00206 | 0.0021448 | 0.0086175 | 0.026773 | 0.039294 | -0.031277 | 0.058422 | -61.5692 | 61.4319 | -61.615 | -61.4365 | 61.2488 | 0.27008 | -0.07782 | 0.29755 | 61.496 | -61.7203 | -0.050354 | -0.045776 | -0.004578 | 0.12817 | -0.22888 | -0.15564 | 0.018311 | 0.045776 | 61.4868 | 61.8622 | 122.8134 | 122.9965 | -0.004578 | 123.0606 | 61.8347 | -0.15564 | 122.9965 | -0.004578 | 61.8347 | 122.8134 | 123.0606 | -123.0927 | -123.1979
151.5625 | 123.143 | -61.6058 | 61.3678 | 0.00206 | 0.0029992 | 0.0094721 | 0.0319 | 0.041216 | -0.032131 | 0.056072 | -61.6837 | 61.4319 | -61.7523 | -61.6013 | 61.0565 | 0.091553 | -0.032043 | 0.086975 | 61.5005 | -61.7615 | -0.14648 | 0.064087 | -0.07782 | 0.004578 | -0.31128 | -0.15564 | 0.13275 | 0.068664 | 61.5738 | 61.6928 | 122.6624 | 123.0377 | -0.07782 | 123.1064 | 61.6974 | -0.15564 | 123.0377 | -0.07782 | 61.6974 | 122.6624 | 123.1064 | -123.1201 | -123.1293
153.2344 | 123.175 | -61.5646 | 61.3632 | 0.00206 | 0.0012902 | 0.01054 | 0.029337 | 0.039935 | -0.032131 | 0.060771 | -61.6974 | 61.3861 | -61.7477 | -61.5829 | 61.0748 | 0.11444 | -0.17395 | 0.091553 | 61.4273 | -61.7432 | -0.18311 | 0.022888 | -0.13275 | -0.018311 | -0.28839 | -0.17853 | 0.064087 | 0.050354 | 61.3907 | 61.6562 | 122.6395 | 122.9507 | -0.13275 | 122.9919 | 61.6791 | -0.17853 | 122.9507 | -0.13275 | 61.6791 | 122.6395 | 122.9919 | -123.111 | -123.1064
154.9062 | 123.262 | -61.4914 | 61.4227 | 0.0096895 | -0.00084602 | 0.014172 | 0.023142 | 0.040362 | -0.030636 | 0.059703 | -61.647 | 61.4273 | -61.6699 | -61.5463 | 61.1435 | 0.17853 | -0.14191 | 0.14191 | 61.4548 | -61.7477 | -0.17853 | 0.004578 | -0.15564 | -0.054932 | -0.27923 | -0.25635 | 0.032044 | 0.022888 | 61.3495 | 61.6333 | 122.6349 | 122.9187 | -0.15564 | 122.9462 | 61.6699 | -0.25635 | 122.9187 | -0.15564 | 61.6699 | 122.6349 | 122.9462 | -123.0927 | -123.1705
156.5938 | 123.111 | -61.5555 | 61.3815 | 0.0096895 | 0.00022218 | 0.014385 | 0.032114 | 0.041644 | -0.031704 | 0.060344 | -61.6516 | 61.4685 | -61.7157 | -61.5143 | 61.1389 | 0.18768 | 0.082397 | 0.20142 | 61.5509 | -61.7157 | -0.16022 | 0.086975 | -0.09613 | 0.041199 | -0.24262 | -0.16022 | 0.16937 | 0.064087 | 61.6379 | 61.7569 | 122.6944 | 123.024 | -0.09613 | 123.1064 | 61.7432 | -0.16022 | 123.024 | -0.09613 | 61.7432 | 122.6944 | 123.1064 | -123.0972 | -123.0972
158.3281 | 123.143 | -61.5372 | 61.4319 | 0.0096895 | 0.001504 | 0.010326 | 0.025705 | 0.042498 | -0.032558 | 0.059276 | -61.647 | 61.4731 | -61.6699 | -61.5463 | 61.1343 | 0.16479 | 0.11902 | 0.1831 | 61.5692 | -61.6974 | -0.13275 | 0.041198 | -0.10986 | -0.009156 | -0.29755 | -0.16022 | 0.13733 | 0.022888 | 61.6562 | 61.7203 | 122.6715 | 123.0103 | -0.10986 | 123.1064 | 61.702 | -0.16022 | 123.0103 | -0.10986 | 61.702 | 122.6715 | 123.1064 | -123.1018 | -123.1293
160.0156 | 123.2346 | -61.5601 | 61.3495 | 0.00206 | 0.0049218 | 0.0098993 | 0.028055 | 0.044421 | -0.034481 | 0.057567 | -61.734 | 61.3815 | -61.734 | -61.6425 | 61.0382 | 0.068665 | -0.045776 | 0.036621 | 61.4868 | -61.7569 | -0.17395 | 0.032044 | -0.17395 | -0.082397 | -0.31128 | -0.19684 | 0.13733 | 0 | 61.5143 | 61.5967 | 122.5983 | 122.9416 | -0.17395 | 123.0469 | 61.6287 | -0.19684 | 122.9416 | -0.17395 | 61.6287 | 122.5983 | 123.0469 | -123.0835 | -123.1064
161.6875 | 123.1613 | -61.5234 | 61.3953 | -0.0055695 | -0.00020502 | 0.011822 | 0.026773 | 0.041857 | -0.031063 | 0.058422 | -61.6287 | 61.3403 | -61.7157 | -61.5234 | 61.1389 | 0.1831 | -0.28839 | 0.15564 | 61.3998 | -61.7203 | -0.19226 | -0.054932 | -0.10529 | 0 | -0.25635 | -0.19684 | 0.004577 | 0.086975 | 61.235 | 61.6791 | 122.6624 | 122.8638 | -0.10529 | 122.9233 | 61.7065 | -0.19684 | 122.8638 | -0.10529 | 61.7065 | 122.6624 | 122.9233 | -123.111 | -123.1155
163.4219 | 123.1659 | -61.528 | 61.4182 | 0.00206 | -0.0021276 | 0.012676 | 0.026773 | 0.041857 | -0.033199 | 0.061199 | -61.615 | 61.3586 | -61.702 | -61.5234 | 61.1435 | 0.1831 | -0.28381 | 0.15564 | 61.3907 | -61.7477 | -0.17395 | -0.059509 | -0.086975 | 0.004578 | -0.27466 | -0.21973 | -0.027466 | 0.086975 | 61.2442 | 61.6837 | 122.6715 | 122.8867 | -0.086975 | 122.9187 | 61.7111 | -0.21973 | 122.8867 | -0.086975 | 61.7111 | 122.6715 | 122.9187 | -123.1201 | -123.1659
165.1562 | 123.1659 | -61.5555 | 61.3907 | 0.0096895 | 0.00064938 | 0.011822 | 0.027841 | 0.042284 | -0.031917 | 0.060558 | -61.6699 | 61.3358 | -61.7294 | -61.528 | 61.1298 | 0.17395 | -0.23804 | 0.12817 | 61.4136 | -61.7111 | -0.17395 | -0.054932 | -0.11444 | 0.027466 | -0.26093 | -0.15564 | 0.022888 | 0.059509 | 61.3174 | 61.6837 | 122.6852 | 122.8912 | -0.11444 | 122.9691 | 61.7294 | -0.15564 | 122.8912 | -0.11444 | 61.7294 | 122.6852 | 122.9691 | -123.1201 | -123.1018
166.9375 | 123.23 | -61.5051 | 61.4227 | 0.017319 | -0.0021276 | 0.010967 | 0.023783 | 0.039935 | -0.032772 | 0.059703 | -61.6425 | 61.3632 | -61.6653 | -61.5417 | 61.1343 | 0.16479 | -0.15564 | 0.13733 | 61.4548 | -61.6928 | -0.16022 | -0.059509 | -0.13733 | -0.036621 | -0.28839 | -0.18768 | 0.032044 | 0.022888 | 61.3495 | 61.6425 | 122.6395 | 122.8683 | -0.13733 | 122.9599 | 61.6699 | -0.18768 | 122.8683 | -0.13733 | 61.6699 | 122.6395 | 122.9599 | -123.0881 | -123.1155
168.8281 | 123.0972 | -61.5234 | 61.4731 | 0.0096895 | 0.0019312 | 0.011395 | 0.02656 | 0.038653 | -0.03149 | 0.056926 | -61.5463 | 61.4502 | -61.5875 | -61.4365 | 61.2122 | 0.27924 | 0 | 0.28381 | 61.5097 | -61.6608 | -0.064087 | -0.022888 | -0.022889 | 0.086975 | -0.26093 | -0.13733 | 0.036622 | 0.041198 | 61.5234 | 61.8073 | 122.7356 | 122.9736 | -0.022889 | 123.0331 | 61.8027 | -0.13733 | 122.9736 | -0.022889 | 61.8027 | 122.7356 | 123.0331 | -123.0606 | -123.1338
170.8281 | 123.1659 | -61.4914 | 61.4594 | -0.0055695 | 0.0021448 | 0.01289 | 0.026132 | 0.039721 | -0.030636 | 0.05949 | -61.5509 | 61.4136 | -61.6516 | -61.4319 | 61.2259 | 0.27466 | -0.14191 | 0.2655 | 61.4685 | -61.6745 | -0.16022 | -0.045777 | -0.059509 | 0.059509 | -0.23346 | -0.18311 | 0.009155 | 0.10071 | 61.3495 | 61.7569 | 122.7173 | 122.905 | -0.059509 | 122.9599 | 61.7661 | -0.18311 | 122.905 | -0.059509 | 61.7661 | 122.7173 | 122.9599 | -123.111 | -123.1339
173.0156 | 123.1796 | -61.5326 | 61.409 | 0.00206 | 0.002572 | 0.013104 | 0.028482 | 0.041644 | -0.033413 | 0.058635 | -61.6013 | 61.3861 | -61.6699 | -61.5051 | 61.1435 | 0.17853 | -0.25177 | 0.16479 | 61.4365 | -61.7203 | -0.13733 | -0.022889 | -0.068664 | 0.027466 | -0.2655 | -0.18768 | 0.027465 | 0.068665 | 61.2808 | 61.6974 | 122.6761 | 122.9187 | -0.068664 | 122.9691 | 61.7111 | -0.18768 | 122.9187 | -0.068664 | 61.7111 | 122.6761 | 122.9691 | -123.0789 | -123.1293
174.7656 | 123.1384 | -61.5509 | 61.4319 | 0.00206 | 0.0019312 | 0.0090447 | 0.030832 | 0.040575 | -0.033413 | 0.059062 | -61.6241 | 61.5051 | -61.6516 | -61.5097 | 61.1252 | 0.1831 | 0.13275 | 0.20142 | 61.5738 | -61.6837 | -0.10071 | 0.073242 | -0.073243 | 0.041198 | -0.3067 | -0.13275 | 0.14191 | 0.027465 | 61.6837 | 61.7523 | 122.6761 | 123.056 | -0.073243 | 123.1247 | 61.734 | -0.13275 | 123.056 | -0.073243 | 61.734 | 122.6761 | 123.1247 | -123.0835 | -123.1155
176.7656 | 123.143 | -61.5417 | 61.3724 | 0.0096895 | -0.0014868 | 0.013531 | 0.027201 | 0.040575 | -0.030422 | 0.059062 | -61.6104 | 61.322 | -61.7111 | -61.496 | 61.1435 | 0.18768 | -0.28381 | 0.17395 | 61.4044 | -61.7249 | -0.16937 | -0.050354 | -0.068665 | 0.045776 | -0.22888 | -0.18311 | 0.032044 | 0.10071 | 61.2579 | 61.7157 | 122.6852 | 122.8638 | -0.068665 | 122.9462 | 61.7294 | -0.18311 | 122.8638 | -0.068665 | 61.7294 | 122.6852 | 122.9462 | -123.0835 | -123.0972
179.6094 | 123.0789 | -61.5738 | 61.3815 | 0.017319 | 0.0017176 | 0.0098993 | 0.028696 | 0.039507 | -0.032985 | 0.060985 | -61.6333 | 61.4548 | -61.6699 | -61.5143 | 61.1298 | 0.19684 | 0.059509 | 0.21057 | 61.5372 | -61.7065 | -0.09613 | 0.073242 | -0.059509 | 0.05951 | -0.25177 | -0.13275 | 0.15564 | 0.036621 | 61.6333 | 61.7844 | 122.7036 | 123.0286 | -0.059509 | 123.111 | 61.7706 | -0.13275 | 123.0286 | -0.059509 | 61.7706 | 122.7036 | 123.111 | -123.0515 | -123.0881
181.3125 | 123.1201 | -61.5372 | 61.4227 | 0.017319 | 0.0021448 | 0.0098993 | 0.028055 | 0.040789 | -0.033199 | 0.060131 | -61.6287 | 61.5097 | -61.6745 | -61.5234 | 61.1252 | 0.17395 | 0.13275 | 0.18768 | 61.528 | -61.6882 | -0.13733 | 0.086976 | -0.091553 | 0.013733 | -0.29755 | -0.15106 | 0.10529 | 0.045777 | 61.6699 | 61.7249 | 122.6624 | 123.0469 | -0.091553 | 123.0652 | 61.7111 | -0.15106 | 123.0469 | -0.091553 | 61.7111 | 122.6624 | 123.0652 | -123.0972 | -123.111
183 | 123.0606 | -61.5005 | 61.4502 | -0.0055695 | 0.0019312 | 0.011608 | 0.024851 | 0.039935 | -0.030849 | 0.057994 | -61.5143 | 61.441 | -61.6333 | -61.4136 | 61.2305 | 0.29755 | -0.09613 | 0.31128 | 61.4639 | -61.6745 | -0.13275 | -0.009155 | -0.013733 | 0.086975 | -0.21973 | -0.17395 | 0.013733 | 0.11902 | 61.4044 | 61.8118 | 122.731 | 122.9416 | -0.013733 | 122.9645 | 61.7981 | -0.17395 | 122.9416 | -0.013733 | 61.7981 | 122.731 | 122.9645 | -123.0835 | -123.1247
184.7188 | 123.1155 | -61.528 | 61.4365 | 0.00206 | 0.0021448 | 0.012035 | 0.025919 | 0.040362 | -0.030208 | 0.05714 | -61.615 | 61.4822 | -61.6379 | -61.5143 | 61.1343 | 0.1831 | 0.11902 | 0.20599 | 61.5326 | -61.6928 | -0.10986 | 0.045777 | -0.086975 | 0.013733 | -0.30212 | -0.16479 | 0.096131 | 0.022888 | 61.647 | 61.734 | 122.6624 | 123.0103 | -0.086975 | 123.0606 | 61.7111 | -0.16479 | 123.0103 | -0.086975 | 61.7111 | 122.6624 | 123.0606 | -123.0743 | -123.1293
186.4062 | 123.0789 | -61.5143 | 61.4456 | 0.017319 | -0.00063242 | 0.01054 | 0.02421 | 0.042071 | -0.034267 | 0.058422 | -61.5555 | 61.4319 | -61.6287 | -61.4227 | 61.2122 | 0.25635 | -0.009155 | 0.27924 | 61.4914 | -61.6653 | -0.11444 | -0.013733 | -0.041199 | 0.091553 | -0.23346 | -0.15106 | 0.045776 | 0.073242 | 61.5051 | 61.7935 | 122.7264 | 122.9462 | -0.041199 | 123.0057 | 61.7706 | -0.15106 | 122.9462 | -0.041199 | 61.7706 | 122.7264 | 123.0057 | -123.0743 | -123.111
188.0938 | 123.1979 | -61.4685 | 61.4136 | 0.0096895 | -0.00020502 | 0.0096857 | 0.026132 | 0.042071 | -0.031277 | 0.061626 | -61.6241 | 61.4136 | -61.6653 | -61.5189 | 61.1252 | 0.17395 | -0.16479 | 0.15106 | 61.4639 | -61.6882 | -0.19684 | 0 | -0.15564 | -0.050354 | -0.28839 | -0.21973 | 0.050354 | 0.041198 | 61.3037 | 61.6196 | 122.5937 | 122.8821 | -0.15564 | 122.9324 | 61.6425 | -0.21973 | 122.8821 | -0.15564 | 61.6425 | 122.5937 | 122.9324 | -123.0789 | -123.1018
189.7812 | 123.0606 | -61.5051 | 61.4731 | -0.0055695 | 0.00043578 | 0.0092585 | 0.025278 | 0.038866 | -0.030849 | 0.059703 | -61.5189 | 61.4136 | -61.6241 | -61.4044 | 61.235 | 0.3067 | -0.10529 | 0.3067 | 61.4868 | -61.6562 | -0.11902 | -0.059509 | -0.013733 | 0.10071 | -0.23804 | -0.15106 | 0.013733 | 0.10529 | 61.3998 | 61.8118 | 122.7402 | 122.9187 | -0.013733 | 122.9919 | 61.8118 | -0.15106 | 122.9187 | -0.013733 | 61.8118 | 122.7402 | 122.9919 | -123.0972 | -123.1293
191.4531 | 123.1293 | -61.5234 | 61.3998 | -0.0055695 | 0.0023584 | 0.011822 | 0.029337 | 0.040575 | -0.03149 | 0.058849 | -61.6333 | 61.4777 | -61.6608 | -61.5097 | 61.1206 | 0.19226 | 0.12817 | 0.20142 | 61.5326 | -61.6745 | -0.13733 | 0.07782 | -0.10986 | 0.013732 | -0.27924 | -0.15106 | 0.13275 | 0.027466 | 61.6516 | 61.7249 | 122.644 | 123.0011 | -0.10986 | 123.056 | 61.7157 | -0.15106 | 123.0011 | -0.10986 | 61.7157 | 122.644 | 123.056 | -123.0606 | -123.0743
193.1406 | 123.0743 | -61.5005 | 61.4731 | 0.00206 | 0.001504 | 0.012676 | 0.026773 | 0.041003 | -0.031917 | 0.055644 | -61.528 | 61.4182 | -61.6058 | -61.4273 | 61.1893 | 0.26093 | 0.004578 | 0.29297 | 61.528 | -61.6562 | -0.10529 | -0.054931 | -0.027466 | 0.073242 | -0.28381 | -0.15564 | 0.054932 | 0.07782 | 61.5051 | 61.7935 | 122.6898 | 122.9187 | -0.027466 | 123.0286 | 61.7615 | -0.15564 | 122.9187 | -0.027466 | 61.7615 | 122.6898 | 123.0286 | -123.0789 | -123.1293
194.875 | 123.1567 | -61.4868 | 61.4365 | -0.0055695 | 8.578e-06 | 0.0094721 | 0.023996 | 0.040148 | -0.030422 | 0.05714 | -61.5829 | 61.3998 | -61.6196 | -61.4456 | 61.1893 | 0.23804 | -0.12817 | 0.25177 | 61.4868 | -61.6745 | -0.13275 | -0.036621 | -0.096131 | 0.041198 | -0.24719 | -0.18768 | 0.050354 | 0.036621 | 61.3586 | 61.7386 | 122.6761 | 122.8867 | -0.096131 | 122.9736 | 61.7249 | -0.18768 | 122.8867 | -0.096131 | 61.7249 | 122.6761 | 122.9736 | -123.056 | -123.111
196.5625 | 123.1384 | -61.5143 | 61.4044 | 0.00206 | 0.0017176 | 0.013958 | 0.02891 | 0.043353 | -0.032131 | 0.060558 | -61.5829 | 61.3403 | -61.7249 | -61.4914 | 61.1343 | 0.16937 | -0.29755 | 0.16022 | 61.377 | -61.7157 | -0.21057 | -0.064087 | -0.068665 | 0.022888 | -0.27008 | -0.20142 | -0.027466 | 0.14191 | 61.2167 | 61.6745 | 122.6486 | 122.8546 | -0.068665 | 122.8912 | 61.6837 | -0.20142 | 122.8546 | -0.068665 | 61.6837 | 122.6486 | 122.8912 | -123.1293 | -123.1201
198.2344 | 123.0606 | -61.496 | 61.4639 | 0.017319 | 0.0010766 | 0.010967 | 0.025919 | 0.037371 | -0.031704 | 0.057781 | -61.5189 | 61.441 | -61.5738 | -61.3815 | 61.235 | 0.29755 | -0.09613 | 0.31586 | 61.4594 | -61.6791 | -0.07782 | -0.022888 | -0.022888 | 0.11444 | -0.22888 | -0.1831 | -0.004577 | 0.054932 | 61.3998 | 61.8118 | 122.731 | 122.937 | -0.022888 | 122.9553 | 61.7935 | -0.1831 | 122.937 | -0.022888 | 61.7935 | 122.731 | 122.9553 | -123.0377 | -123.143
199.9219 | 123.1476 | -61.5005 | 61.377 | 0.00206 | 0.00064938 | 0.012249 | 0.029123 | 0.040148 | -0.032131 | 0.060131 | -61.5921 | 61.322 | -61.7065 | -61.4777 | 61.1298 | 0.18768 | -0.28839 | 0.16479 | 61.3953 | -61.7111 | -0.20599 | -0.054932 | -0.091553 | 0.022888 | -0.24719 | -0.21057 | 0.018311 | 0.11444 | 61.2122 | 61.6653 | 122.6303 | 122.8226 | -0.091553 | 122.8958 | 61.6882 | -0.21057 | 122.8226 | -0.091553 | 61.6882 | 122.6303 | 122.8958 | -123.0835 | -123.0881
201.625 | 123.1293 | -61.4594 | 61.4319 | -0.0055695 | 0.0012902 | 0.012249 | 0.026987 | 0.037585 | -0.029568 | 0.05949 | -61.5509 | 61.4273 | -61.5967 | -61.4227 | 61.2122 | 0.26093 | -0.13733 | 0.2655 | 61.4548 | -61.6928 | -0.13733 | -0.004578 | -0.091552 | 0.036622 | -0.21973 | -0.23346 | 0.022888 | 0.045777 | 61.322 | 61.7249 | 122.6715 | 122.8867 | -0.091552 | 122.9141 | 61.7203 | -0.23346 | 122.8867 | -0.091552 | 61.7203 | 122.6715 | 122.9141 | -123.0286 | -123.1247
203.3281 | 123.0286 | -61.5463 | 61.3953 | 0.00206 | 0.001504 | 0.011822 | 0.030618 | 0.039935 | -0.03384 | 0.059062 | -61.6058 | 61.3998 | -61.6974 | -61.4868 | 61.116 | 0.19226 | 0 | 0.20599 | 61.4868 | -61.6928 | -0.15106 | 0.004577 | -0.059509 | 0.05951 | -0.27924 | -0.14648 | 0.091552 | 0.091553 | 61.5463 | 61.7523 | 122.6624 | 122.9462 | -0.059509 | 123.0331 | 61.7386 | -0.14648 | 122.9462 | -0.059509 | 61.7386 | 122.6624 | 123.0331 | -123.0927 | -123.0881
205.0156 | 123.143 | -61.5234 | 61.3266 | -0.0055695 | 0.002572 | 0.0084039 | 0.02891 | 0.040575 | -0.032558 | 0.058422 | -61.647 | 61.3586 | -61.7203 | -61.5555 | 61.0703 | 0.13733 | -0.17853 | 0.11444 | 61.4182 | -61.7294 | -0.19684 | 0.032044 | -0.1236 | -0.032044 | -0.25635 | -0.20599 | 0.091553 | 0.073242 | 61.3449 | 61.6379 | 122.5937 | 122.8821 | -0.1236 | 122.9416 | 61.6608 | -0.20599 | 122.8821 | -0.1236 | 61.6608 | 122.5937 | 122.9416 | -123.0469 | -123.056
206.7188 | 123.1705 | -61.5326 | 61.3632 | -0.0055695 | 0.0012902 | 0.011181 | 0.029978 | 0.041216 | -0.031063 | 0.060131 | -61.7111 | 61.3998 | -61.7294 | -61.6013 | 61.0245 | 0.07782 | -0.041199 | 0.041199 | 61.441 | -61.7294 | -0.19684 | 0.036621 | -0.17853 | -0.068664 | -0.33874 | -0.19684 | 0.07782 | 0.01831 | 61.4914 | 61.5738 | 122.5571 | 122.9324 | -0.17853 | 122.9736 | 61.6104 | -0.19684 | 122.9324 | -0.17853 | 61.6104 | 122.5571 | 122.9736 | -123.0927 | -123.0927
208.4688 | 123.056 | -61.5784 | 61.3907 | 0.0096895 | 0.0023584 | 0.012463 | 0.031687 | 0.042712 | -0.033413 | 0.05949 | -61.5967 | 61.409 | -61.6882 | -61.5051 | 61.0886 | 0.17395 | -0.018311 | 0.16937 | 61.4777 | -61.6882 | -0.10986 | 0.018311 | -0.018311 | 0.073242 | -0.30212 | -0.10986 | 0.086975 | 0.091552 | 61.5601 | 61.7477 | 122.6669 | 122.9874 | -0.018311 | 123.056 | 61.7523 | -0.10986 | 122.9874 | -0.018311 | 61.7523 | 122.6669 | 123.056 | -123.0789 | -123.0789
210.1719 | 123.056 | -61.5875 | 61.3632 | 0.0096895 | 0.002572 | 0.011608 | 0.026773 | 0.043353 | -0.035549 | 0.058849 | -61.615 | 61.3815 | -61.6745 | -61.5143 | 61.0931 | 0.15564 | -0.022888 | 0.16022 | 61.4548 | -61.6882 | -0.086976 | 0.018311 | -0.027466 | 0.073242 | -0.27008 | -0.10071 | 0.091553 | 0.05951 | 61.5646 | 61.7477 | 122.6807 | 122.9691 | -0.027466 | 123.0423 | 61.7432 | -0.10071 | 122.9691 | -0.027466 | 61.7432 | 122.6807 | 123.0423 | -123.0377 | -123.0515
211.9062 | 123.0881 | -61.5005 | 61.409 | 0.0096895 | 0.0027856 | 0.010754 | 0.025492 | 0.039721 | -0.032345 | 0.058849 | -61.6196 | 61.4822 | -61.6241 | -61.5189 | 61.1023 | 0.19226 | 0.11902 | 0.18768 | 61.5417 | -61.6699 | -0.1236 | 0.073242 | -0.11902 | -0.018311 | -0.3067 | -0.16937 | 0.13275 | 0.004578 | 61.6196 | 61.6882 | 122.6028 | 122.9828 | -0.11902 | 123.0423 | 61.6928 | -0.16937 | 122.9828 | -0.11902 | 61.6928 | 122.6028 | 123.0423 | -123.0331 | -123.0789
213.5781 | 123.1522 | -61.4731 | 61.3907 | 0.00206 | 0.00022218 | 0.012676 | 0.021005 | 0.039507 | -0.032131 | 0.057994 | -61.6196 | 61.3312 | -61.6653 | -61.5143 | 61.116 | 0.1831 | -0.19684 | 0.15564 | 61.4456 | -61.6974 | -0.19226 | -0.059509 | -0.14648 | -0.041199 | -0.27466 | -0.2243 | 0.054932 | 0.045776 | 61.2762 | 61.6287 | 122.5891 | 122.8043 | -0.14648 | 122.9187 | 61.6562 | -0.2243 | 122.8043 | -0.14648 | 61.6562 | 122.5891 | 122.9187 | -123.056 | -123.0881
215.2812 | 123.0835 | -61.5051 | 61.4319 | 0.0096895 | 0.0027856 | 0.010967 | 0.02656 | 0.04143 | -0.032772 | 0.060985 | -61.5738 | 61.4594 | -61.6196 | -61.4914 | 61.1114 | 0.19684 | 0.09613 | 0.21057 | 61.5646 | -61.6791 | -0.11444 | 0.027466 | -0.068665 | 0.013733 | -0.32044 | -0.17395 | 0.13275 | 0.045776 | 61.6013 | 61.7157 | 122.6166 | 122.9645 | -0.068665 | 123.0698 | 61.702 | -0.17395 | 122.9645 | -0.068665 | 61.702 | 122.6166 | 123.0698 | -123.0515 | -123.111
217.0156 | 123.0515 | -61.5097 | 61.4502 | 0.0096895 | -0.0010596 | 0.0090447 | 0.025919 | 0.041003 | -0.031917 | 0.058422 | -61.5234 | 61.3861 | -61.615 | -61.4044 | 61.1984 | 0.27466 | -0.059509 | 0.29755 | 61.5005 | -61.6287 | -0.10529 | -0.064087 | -0.013732 | 0.10529 | -0.25177 | -0.11902 | 0.050354 | 0.091553 | 61.4502 | 61.8073 | 122.7081 | 122.8958 | -0.013732 | 123.0103 | 61.7844 | -0.11902 | 122.8958 | -0.013732 | 61.7844 | 122.7081 | 123.0103 | -123.0652 | -123.0789
218.7031 | 123.1659 | -61.5143 | 61.3037 | -0.0055695 | 0.0021448 | 0.012035 | 0.02891 | 0.042925 | -0.032558 | 0.05714 | -61.6791 | 61.377 | -61.7294 | -61.6013 | 61.0062 | 0.073242 | -0.054932 | 0.054932 | 61.4731 | -61.7294 | -0.21515 | 0.073242 | -0.16479 | -0.086975 | -0.29755 | -0.21515 | 0.16937 | 0.050354 | 61.4594 | 61.5692 | 122.5204 | 122.8912 | -0.16479 | 122.9874 | 61.5875 | -0.21515 | 122.8912 | -0.16479 | 61.5875 | 122.5204 | 122.9874 | -123.0331 | -123.0331
220.4062 | 123.0743 | -61.5509 | 61.3449 | -0.0055695 | 0.0027856 | 0.012676 | 0.029123 | 0.041644 | -0.03384 | 0.058422 | -61.6608 | 61.3724 | -61.6928 | -61.5692 | 61.0291 | 0.10529 | -0.027466 | 0.091553 | 61.4822 | -61.7294 | -0.14191 | 0.027465 | -0.10986 | -0.018311 | -0.31586 | -0.17853 | 0.13733 | 0.032043 | 61.5234 | 61.6425 | 122.58 | 122.9233 | -0.10986 | 123.0331 | 61.6562 | -0.17853 | 122.9233 | -0.10986 | 61.6562 | 122.58 | 123.0331 | -123.0377 | -123.0743
222.0938 | 123.1522 | -61.4685 | 61.4136 | 0.0096895 | -0.00020502 | 0.011181 | 0.02186 | 0.038866 | -0.030636 | 0.059062 | -61.5784 | 61.3907 | -61.6196 | -61.4685 | 61.1435 | 0.23346 | -0.13275 | 0.20142 | 61.4777 | -61.6837 | -0.15106 | -0.022888 | -0.10986 | 0 | -0.27008 | -0.21515 | 0.064087 | 0.041199 | 61.3358 | 61.6699 | 122.612 | 122.8592 | -0.10986 | 122.9462 | 61.702 | -0.21515 | 122.8592 | -0.10986 | 61.702 | 122.612 | 122.9462 | -123.0331 | -123.0972
223.7969 | 123.0515 | -61.5143 | 61.3953 | 0.00206 | 0.0029992 | 0.010754 | 0.028696 | 0.039935 | -0.033199 | 0.059917 | -61.615 | 61.4273 | -61.6608 | -61.4868 | 61.1023 | 0.18768 | 0.091553 | 0.20142 | 61.5143 | -61.6791 | -0.14648 | 0.032043 | -0.10071 | 0.027466 | -0.29297 | -0.16479 | 0.11902 | 0.045777 | 61.6058 | 61.7157 | 122.6166 | 122.9416 | -0.10071 | 123.0286 | 61.702 | -0.16479 | 122.9416 | -0.10071 | 61.702 | 122.6166 | 123.0286 | -123.056 | -123.0743
225.4688 | 123.0881 | -61.4548 | 61.4319 | 0.0096895 | 0.0017176 | 0.011608 | 0.023142 | 0.038866 | -0.031277 | 0.059276 | -61.5372 | 61.409 | -61.6013 | -61.4182 | 61.203 | 0.29297 | -0.13275 | 0.27466 | 61.441 | -61.6516 | -0.14648 | -0.022888 | -0.082397 | 0.036621 | -0.22888 | -0.19684 | 0.009155 | 0.064087 | 61.322 | 61.7294 | 122.6578 | 122.8638 | -0.082397 | 122.8958 | 61.7477 | -0.19684 | 122.8638 | -0.082397 | 61.7477 | 122.6578 | 122.8958 | -123.0331 | -123.0835
227.2031 | 123.1155 | -61.4548 | 61.4044 | 0.00206 | 0.00043578 | 0.011181 | 0.024851 | 0.040789 | -0.02914 | 0.060558 | -61.5784 | 61.322 | -61.6653 | -61.5097 | 61.0886 | 0.18768 | -0.23804 | 0.16937 | 61.4319 | -61.7111 | -0.21057 | -0.082398 | -0.1236 | -0.054932 | -0.31586 | -0.25635 | 0.027466 | 0.086975 | 61.2167 | 61.6241 | 122.5433 | 122.7768 | -0.1236 | 122.8867 | 61.6425 | -0.25635 | 122.7768 | -0.1236 | 61.6425 | 122.5433 | 122.8867 | -123.0698 | -123.1155
228.9375 | 123.0331 | -61.5326 | 61.3724 | 0.00206 | 0.00064938 | 0.012463 | 0.02891 | 0.043139 | -0.034908 | 0.059703 | -61.5921 | 61.3907 | -61.6516 | -61.4548 | 61.1114 | 0.20599 | -0.013733 | 0.21515 | 61.4777 | -61.6791 | -0.11902 | 0.018311 | -0.059509 | 0.07782 | -0.26093 | -0.14648 | 0.10529 | 0.059509 | 61.5189 | 61.7477 | 122.644 | 122.9233 | -0.059509 | 123.0103 | 61.7386 | -0.14648 | 122.9233 | -0.059509 | 61.7386 | 122.644 | 123.0103 | -123.024 | -123.0515
230.6562 | 123.0606 | -61.5005 | 61.4182 | -0.0055695 | 0.00064938 | 0.0075495 | 0.026346 | 0.040148 | -0.031277 | 0.059276 | -61.5921 | 61.4227 | -61.6241 | -61.5005 | 61.1069 | 0.18768 | 0.086975 | 0.2243 | 61.5463 | -61.6516 | -0.1236 | 0.004577 | -0.091553 | 0 | -0.31128 | -0.15106 | 0.12817 | 0.032044 | 61.5875 | 61.7249 | 122.6074 | 122.9233 | -0.091553 | 123.0469 | 61.6882 | -0.15106 | 122.9233 | -0.091553 | 61.6882 | 122.6074 | 123.0469 | -123.0423 | -123.0698
232.3438 | 123.0698 | -61.5234 | 61.4136 | 0.00206 | 0.0017176 | 0.01289 | 0.023569 | 0.041857 | -0.034054 | 0.058208 | -61.5646 | 61.4548 | -61.5921 | -61.4731 | 61.1206 | 0.21057 | 0.07782 | 0.2243 | 61.5143 | -61.6699 | -0.068665 | 0.041199 | -0.041199 | 0.050354 | -0.29297 | -0.14648 | 0.10071 | 0.027466 | 61.6013 | 61.7477 | 122.644 | 122.9782 | -0.041199 | 123.0377 | 61.734 | -0.14648 | 122.9782 | -0.041199 | 61.734 | 122.644 | 123.0377 | -123.0057 | -123.0835
234.0312 | 123.0469 | -61.5189 | 61.4182 | 0.00206 | 0.0027856 | 0.013104 | 0.025064 | 0.03908 | -0.030422 | 0.060344 | -61.5601 | 61.4456 | -61.6333 | -61.4639 | 61.116 | 0.20599 | 0.086975 | 0.21973 | 61.5189 | -61.6882 | -0.11444 | 0.027466 | -0.041199 | 0.054932 | -0.30212 | -0.16937 | 0.10071 | 0.073242 | 61.6058 | 61.7386 | 122.6349 | 122.9645 | -0.041199 | 123.0377 | 61.7249 | -0.16937 | 122.9645 | -0.041199 | 61.7249 | 122.6349 | 123.0377 | -123.0515 | -123.1064
235.7031 | 123.111 | -61.4822 | 61.3998 | 0.00206 | 0.0038538 | 0.014813 | 0.026132 | 0.039507 | -0.031277 | 0.060344 | -61.5692 | 61.322 | -61.6653 | -61.4914 | 61.116 | 0.19226 | -0.23804 | 0.16022 | 61.3998 | -61.702 | -0.1831 | -0.07782 | -0.086975 | -0.009155 | -0.28381 | -0.21973 | 0 | 0.09613 | 61.2442 | 61.6425 | 122.5983 | 122.8043 | -0.086975 | 122.8821 | 61.6745 | -0.21973 | 122.8043 | -0.086975 | 61.6745 | 122.5983 | 122.8821 | -123.0652 | -123.1018
237.4062 | 123.1338 | -61.528 | 61.3083 | 0.017319 | 0.0010766 | 0.011395 | 0.02955 | 0.038653 | -0.031704 | 0.059276 | -61.6699 | 61.3632 | -61.7203 | -61.5692 | 61.0016 | 0.09613 | -0.15106 | 0.064087 | 61.4182 | -61.7477 | -0.19226 | 0.054931 | -0.14191 | -0.041199 | -0.3067 | -0.21973 | 0.10986 | 0.050354 | 61.377 | 61.5921 | 122.5296 | 122.8912 | -0.14191 | 122.9462 | 61.6241 | -0.21973 | 122.8912 | -0.14191 | 61.6241 | 122.5296 | 122.9462 | -123.0286 | -123.056
239.0938 | 123.1293 | -61.4868 | 61.377 | -0.0055695 | 0.0012902 | 0.011395 | 0.027841 | 0.040575 | -0.031277 | 0.059062 | -61.5784 | 61.322 | -61.647 | -61.4822 | 61.0886 | 0.1831 | -0.23804 | 0.16479 | 61.409 | -61.702 | -0.16022 | -0.054932 | -0.091553 | 0.004577 | -0.28839 | -0.21515 | 0.032044 | 0.068665 | 61.2488 | 61.6516 | 122.5754 | 122.8088 | -0.091553 | 122.8958 | 61.6699 | -0.21515 | 122.8088 | -0.091553 | 61.6699 | 122.5754 | 122.8958 | -123.024 | -123.0789
240.7969 | 123.1338 | -61.5143 | 61.3403 | 0.0096895 | 0.0012902 | 0.015453 | 0.031046 | 0.040362 | -0.034267 | 0.062267 | -61.6653 | 61.3678 | -61.7203 | -61.5829 | 60.997 | 0.086975 | -0.07782 | 0.045776 | 61.4777 | -61.7477 | -0.20599 | 0.027466 | -0.15106 | -0.068665 | -0.34332 | -0.23346 | 0.13733 | 0.054932 | 61.4365 | 61.5601 | 122.5113 | 122.8821 | -0.15106 | 122.9919 | 61.6013 | -0.23346 | 122.8821 | -0.15106 | 61.6013 | 122.5113 | 122.9919 | -123.0606 | -123.0881
242.5 | 123.143 | -61.4456 | 61.3815 | -0.0055695 | 0.00086298 | 0.01289 | 0.025492 | 0.039721 | -0.029995 | 0.060985 | -61.5921 | 61.377 | -61.615 | -61.496 | 61.1069 | 0.17853 | -0.14191 | 0.15106 | 61.4548 | -61.7111 | -0.16937 | -0.004578 | -0.14648 | -0.050354 | -0.27466 | -0.2655 | 0.073242 | 0.022888 | 61.3037 | 61.5967 | 122.5525 | 122.8226 | -0.14648 | 122.9004 | 61.6241 | -0.2655 | 122.8226 | -0.14648 | 61.6241 | 122.5525 | 122.9004 | -122.9965 | -123.0927
244.1875 | 123.0835 | -61.5097 | 61.3678 | -0.0055695 | 0.0010766 | 0.01289 | 0.028269 | 0.041003 | -0.030636 | 0.060558 | -61.5738 | 61.3037 | -61.6653 | -61.4685 | 61.1069 | 0.19684 | -0.28839 | 0.16937 | 61.377 | -61.7111 | -0.15564 | -0.064087 | -0.064087 | 0.041199 | -0.26093 | -0.20142 | 0.009155 | 0.091552 | 61.2213 | 61.6791 | 122.6166 | 122.8134 | -0.064087 | 122.8867 | 61.7065 | -0.20142 | 122.8134 | -0.064087 | 61.7065 | 122.6166 | 122.8867 | -123.0331 | -123.0789
245.9219 | 123.143 | -61.5051 | 61.3174 | 0.0096895 | 0.00022218 | 0.010113 | 0.029123 | 0.040148 | -0.032985 | 0.059917 | -61.6882 | 61.3632 | -61.7203 | -61.5967 | 60.9833 | 0.064087 | -0.059509 | 0.041199 | 61.4227 | -61.7432 | -0.21515 | 0.045776 | -0.1831 | -0.091553 | -0.33417 | -0.23804 | 0.10528 | 0.032044 | 61.4456 | 61.5463 | 122.4884 | 122.8683 | -0.1831 | 122.9279 | 61.5692 | -0.23804 | 122.8683 | -0.1831 | 61.5692 | 122.4884 | 122.9279 | -123.0377 | -123.0606
247.6094 | 123.143 | -61.441 | 61.3861 | 0.00206 | 0.00064938 | 0.012249 | 0.020792 | 0.03908 | -0.03149 | 0.05949 | -61.6058 | 61.3907 | -61.6013 | -61.4868 | 61.1023 | 0.18768 | -0.13275 | 0.16937 | 61.4273 | -61.6699 | -0.16022 | 0.004578 | -0.16479 | -0.045776 | -0.28381 | -0.22888 | 0.041199 | -0.004578 | 61.3083 | 61.6104 | 122.5433 | 122.8317 | -0.16479 | 122.8683 | 61.6287 | -0.22888 | 122.8317 | -0.16479 | 61.6287 | 122.5433 | 122.8683 | -122.9874 | -123.056
249.3125 | 122.9874 | -61.5372 | 61.3815 | -0.0055695 | 0.0012902 | 0.011395 | 0.02955 | 0.038012 | -0.031917 | 0.05949 | -61.5829 | 61.3724 | -61.6791 | -61.4594 | 61.1023 | 0.20142 | -0.004578 | 0.21515 | 61.4548 | -61.6699 | -0.14191 | -0.009156 | -0.045777 | 0.077819 | -0.27924 | -0.13275 | 0.073242 | 0.09613 | 61.5326 | 61.7523 | 122.6395 | 122.9095 | -0.045777 | 122.9919 | 61.7386 | -0.13275 | 122.9095 | -0.045777 | 61.7386 | 122.6395 | 122.9919 | -123.0606 | -123.0515
251.0156 | 122.9965 | -61.5189 | 61.322 | 0.017319 | 0.0047082 | 0.012035 | 0.028055 | 0.03908 | -0.031917 | 0.058635 | -61.5829 | 61.4319 | -61.6653 | -61.4731 | 61.084 | 0.19226 | 0.032043 | 0.20142 | 61.4731 | -61.6791 | -0.14648 | 0.10986 | -0.064087 | 0.045777 | -0.23804 | -0.16022 | 0.15106 | 0.082397 | 61.5509 | 61.7203 | 122.6028 | 122.9507 | -0.064087 | 122.9919 | 61.7111 | -0.16022 | 122.9507 | -0.064087 | 61.7111 | 122.6028 | 122.9919 | -122.9874 | -123.0011
252.7031 | 123.1201 | -61.4227 | 61.3998 | -0.013199 | -0.00020502 | 0.012249 | 0.021646 | 0.037798 | -0.029354 | 0.059062 | -61.5921 | 61.3678 | -61.6287 | -61.4822 | 61.1114 | 0.19226 | -0.14191 | 0.18768 | 61.4182 | -61.6837 | -0.20599 | -0.032043 | -0.16937 | -0.05951 | -0.28839 | -0.26093 | 0.018311 | 0.036621 | 61.2808 | 61.6104 | 122.5342 | 122.7905 | -0.16937 | 122.8409 | 61.615 | -0.26093 | 122.7905 | -0.16937 | 61.615 | 122.5342 | 122.8409 | -123.0286 | -123.0835
254.4062 | 123.0698 | -61.4685 | 61.3586 | 0.0096895 | 0.0023584 | 0.014813 | 0.02891 | 0.040148 | -0.031917 | 0.057781 | -61.5646 | 61.3174 | -61.6653 | -61.4548 | 61.0886 | 0.1831 | -0.27924 | 0.15564 | 61.3678 | -61.7249 | -0.19684 | -0.041199 | -0.09613 | 0.013733 | -0.27008 | -0.25635 | 0.009155 | 0.10071 | 61.1893 | 61.6241 | 122.5571 | 122.7859 | -0.09613 | 122.8363 | 61.6516 | -0.25635 | 122.7859 | -0.09613 | 61.6516 | 122.5571 | 122.8363 | -123.024 | -123.0835
256.0938 | 122.9828 | -61.5646 | 61.3632 | 0.00206 | 0.0010766 | 0.0098993 | 0.029764 | 0.039507 | -0.032345 | 0.059276 | -61.5875 | 61.377 | -61.6287 | -61.4685 | 61.084 | 0.19684 | -0.013733 | 0.20142 | 61.4594 | -61.6928 | -0.064087 | 0.013733 | -0.022888 | 0.09613 | -0.27924 | -0.12817 | 0.096131 | 0.041199 | 61.5509 | 61.7661 | 122.6486 | 122.9416 | -0.022888 | 123.024 | 61.7615 | -0.12817 | 122.9416 | -0.022888 | 61.7615 | 122.6486 | 123.024 | -122.9919 | -123.056
257.8594 | 123.0789 | -61.5051 | 61.3312 | 0.0096895 | 0.001504 | 0.010754 | 0.029764 | 0.041003 | -0.035335 | 0.058422 | -61.6562 | 61.3632 | -61.6745 | -61.5738 | 60.9924 | 0.082397 | -0.004578 | 0.068665 | 61.4594 | -61.7203 | -0.16937 | 0.032043 | -0.15106 | -0.068665 | -0.33874 | -0.21515 | 0.12817 | 0.018311 | 61.5005 | 61.5738 | 122.4976 | 122.8683 | -0.15106 | 122.9645 | 61.5875 | -0.21515 | 122.8683 | -0.15106 | 61.5875 | 122.4976 | 122.9645 | -123.0057 | -123.0515
259.5469 | 123.0515 | -61.4822 | 61.3861 | 0.00206 | 0.0017176 | 0.0094721 | 0.025919 | 0.039294 | -0.033199 | 0.059917 | -61.6104 | 61.4273 | -61.6241 | -61.4914 | 61.084 | 0.19684 | 0.1236 | 0.20142 | 61.5097 | -61.6562 | -0.14191 | 0.041199 | -0.12817 | -0.009155 | -0.30212 | -0.17395 | 0.1236 | 0.013733 | 61.6058 | 61.6837 | 122.5662 | 122.9095 | -0.12817 | 122.9919 | 61.6791 | -0.17395 | 122.9095 | -0.12817 | 61.6791 | 122.5662 | 122.9919 | -123.0103 | -123.0423
261.2812 | 122.9874 | -61.5372 | 61.3174 | 0.0096895 | 0.0027856 | 0.013958 | 0.0319 | 0.042284 | -0.030422 | 0.058635 | -61.5463 | 61.3861 | -61.6516 | -61.4639 | 61.0748 | 0.17853 | -0.018311 | 0.20599 | 61.4548 | -61.6974 | -0.11444 | 0.068664 | -0.009156 | 0.073242 | -0.24262 | -0.16022 | 0.13733 | 0.10529 | 61.5189 | 61.7432 | 122.612 | 122.9233 | -0.009156 | 122.9919 | 61.7157 | -0.16022 | 122.9233 | -0.009156 | 61.7157 | 122.612 | 122.9919 | -122.9691 | -123.0148
262.9844 | 123.1247 | -61.4914 | 61.2991 | 0.00206 | 0.0049218 | 0.011181 | 0.026773 | 0.042071 | -0.02914 | 0.059062 | -61.6699 | 61.3358 | -61.7157 | -61.5784 | 60.9741 | 0.073242 | -0.059509 | 0.045776 | 61.441 | -61.7477 | -0.2243 | 0.036621 | -0.17853 | -0.086975 | -0.32501 | -0.25635 | 0.14191 | 0.045776 | 61.4319 | 61.5372 | 122.4655 | 122.8271 | -0.17853 | 122.9324 | 61.5646 | -0.25635 | 122.8271 | -0.17853 | 61.5646 | 122.4655 | 122.9324 | -123.0148 | -123.0469
264.6875 | 123.0743 | -61.5051 | 61.3312 | -0.0055695 | 0.001504 | 0.012676 | 0.026132 | 0.040362 | -0.031917 | 0.060131 | -61.6333 | 61.3358 | -61.6928 | -61.5189 | 61.0336 | 0.13733 | -0.19684 | 0.11902 | 61.377 | -61.734 | -0.18768 | 0.004577 | -0.12817 | -0.013733 | -0.29755 | -0.22888 | 0.045776 | 0.059509 | 61.3083 | 61.6241 | 122.5388 | 122.8409 | -0.12817 | 122.8821 | 61.6425 | -0.22888 | 122.8409 | -0.12817 | 61.6425 | 122.5388 | 122.8821 | -123.024 | -123.0652
266.375 | 123.111 | -61.5005 | 61.3129 | -0.0055695 | 0.00086298 | 0.015667 | 0.02656 | 0.040575 | -0.031277 | 0.059276 | -61.6837 | 61.3541 | -61.6928 | -61.5738 | 60.9879 | 0.091553 | -0.07782 | 0.059509 | 61.4227 | -61.7203 | -0.19226 | 0.041199 | -0.18311 | -0.073243 | -0.32501 | -0.21973 | 0.10986 | 0.009155 | 61.4227 | 61.5601 | 122.4884 | 122.8546 | -0.18311 | 122.9233 | 61.5921 | -0.21973 | 122.8546 | -0.18311 | 61.5921 | 122.4884 | 122.9233 | -123.0057 | -123.0331
268.0625 | 123.0743 | -61.4594 | 61.3861 | 0.00206 | -0.00084602 | 0.012035 | 0.021005 | 0.040362 | -0.029781 | 0.058208 | -61.5509 | 61.322 | -61.6333 | -61.4685 | 61.084 | 0.1831 | -0.26093 | 0.17395 | 61.3815 | -61.7157 | -0.17395 | -0.064087 | -0.091552 | -0.009155 | -0.30212 | -0.25635 | -0.004577 | 0.082398 | 61.1984 | 61.6333 | 122.5433 | 122.7814 | -0.091552 | 122.8409 | 61.6425 | -0.25635 | 122.7814 | -0.091552 | 61.6425 | 122.5433 | 122.8409 | -123.0194 | -123.1018
269.75 | 122.9874 | -61.4594 | 61.4273 | 0.0096895 | 0.00086298 | 0.010754 | 0.023783 | 0.038653 | -0.030849 | 0.059062 | -61.4822 | 61.3678 | -61.5738 | -61.3632 | 61.1801 | 0.30212 | -0.10529 | 0.32044 | 61.4548 | -61.6058 | -0.11444 | -0.059509 | -0.022888 | 0.096131 | -0.24719 | -0.14648 | 0.027466 | 0.091553 | 61.3541 | 61.7798 | 122.6395 | 122.8271 | -0.022888 | 122.9141 | 61.7615 | -0.14648 | 122.8271 | -0.022888 | 61.7615 | 122.6395 | 122.9141 | -123.0011 | -123.0331
271.4531 | 123.1064 | -61.5189 | 61.3129 | 0.00206 | 0.0027856 | 0.012676 | 0.029123 | 0.042071 | -0.03384 | 0.058208 | -61.6745 | 61.3495 | -61.6974 | -61.5646 | 60.9695 | 0.07782 | -0.045776 | 0.041199 | 61.4502 | -61.7111 | -0.17853 | 0.036621 | -0.15564 | -0.045776 | -0.34332 | -0.19226 | 0.13733 | 0.022888 | 61.4731 | 61.5601 | 122.4884 | 122.8683 | -0.15564 | 122.9691 | 61.5967 | -0.19226 | 122.8683 | -0.15564 | 61.5967 | 122.4884 | 122.9691 | -123.0103 | -123.024
273.1562 | 123.1064 | -61.4456 | 61.3678 | 0.00206 | 0.0021448 | 0.010326 | 0.022714 | 0.040148 | -0.030636 | 0.060771 | -61.5875 | 61.3403 | -61.5875 | -61.4777 | 61.084 | 0.1831 | -0.13733 | 0.15106 | 61.4227 | -61.6837 | -0.14191 | -0.027466 | -0.14191 | -0.032043 | -0.28381 | -0.23804 | 0.054931 | 0 | 61.3083 | 61.5967 | 122.5296 | 122.7859 | -0.14191 | 122.8683 | 61.6287 | -0.23804 | 122.7859 | -0.14191 | 61.6287 | 122.5296 | 122.8683 | -122.9553 | -123.0515
274.9062 | 123.0927 | -61.5097 | 61.3129 | 0.0096895 | 0.0023584 | 0.011822 | 0.031259 | 0.042071 | -0.032772 | 0.060131 | -61.6699 | 61.3403 | -61.7203 | -61.5646 | 60.9741 | 0.086975 | -0.018311 | 0.045776 | 61.441 | -61.7065 | -0.21057 | 0.027466 | -0.16022 | -0.054931 | -0.33875 | -0.19684 | 0.12817 | 0.050354 | 61.4914 | 61.5555 | 122.4838 | 122.85 | -0.16022 | 122.9507 | 61.5967 | -0.19684 | 122.85 | -0.16022 | 61.5967 | 122.4838 | 122.9507 | -123.0331 | -123.0194
276.5938 | 123.0927 | -61.5143 | 61.3129 | 0.0096895 | 0.0012902 | 0.012035 | 0.031259 | 0.042712 | -0.03149 | 0.060985 | -61.6745 | 61.3724 | -61.702 | -61.6013 | 60.965 | 0.07782 | -0.036621 | 0.054932 | 61.4594 | -61.7111 | -0.18768 | 0.059509 | -0.16022 | -0.086975 | -0.3479 | -0.19684 | 0.14648 | 0.027465 | 61.4777 | 61.5692 | 122.4792 | 122.8867 | -0.16022 | 122.9736 | 61.5921 | -0.19684 | 122.8867 | -0.16022 | 61.5921 | 122.4792 | 122.9736 | -123.0148 | -123.024
278.2812 | 123.0881 | -61.4182 | 61.377 | -0.0055695 | 0.00043578 | 0.0049859 | 0.023569 | 0.039935 | -0.030636 | 0.059703 | -61.5784 | 61.3678 | -61.6196 | -61.4777 | 61.0657 | 0.17395 | -0.13275 | 0.16937 | 61.4136 | -61.6791 | -0.20142 | -0.009155 | -0.16022 | -0.059509 | -0.31128 | -0.26093 | 0.036621 | 0.041199 | 61.2854 | 61.5875 | 122.4838 | 122.7859 | -0.16022 | 122.8317 | 61.5921 | -0.26093 | 122.7859 | -0.16022 | 61.5921 | 122.4838 | 122.8317 | -122.9965 | -123.056
279.9688 | 123.024 | -61.4731 | 61.3998 | 0.00206 | 0.0023584 | 0.0075495 | 0.028055 | 0.038439 | -0.031917 | 0.057994 | -61.5372 | 61.4319 | -61.5829 | -61.4365 | 61.0931 | 0.19684 | 0.082397 | 0.22888 | 61.4868 | -61.6562 | -0.10986 | 0.032044 | -0.064087 | 0.036621 | -0.3067 | -0.18311 | 0.086975 | 0.045777 | 61.5555 | 61.702 | 122.5662 | 122.905 | -0.064087 | 122.9599 | 61.6699 | -0.18311 | 122.905 | -0.064087 | 61.6699 | 122.5662 | 122.9599 | -122.9828 | -123.056
281.6562 | 123.0881 | -61.4273 | 61.3586 | 0.0096895 | -0.00020502 | 0.0090447 | 0.023569 | 0.037585 | -0.032772 | 0.059703 | -61.5738 | 61.3586 | -61.6196 | -61.4548 | 61.0794 | 0.19226 | -0.12817 | 0.17395 | 61.441 | -61.6516 | -0.19226 | 0 | -0.14648 | -0.027466 | -0.27924 | -0.2243 | 0.082397 | 0.045776 | 61.2991 | 61.6013 | 122.5067 | 122.7859 | -0.14648 | 122.8683 | 61.6196 | -0.2243 | 122.7859 | -0.14648 | 61.6196 | 122.5067 | 122.8683 | -122.9782 | -123.0103
283.3594 | 123.0652 | -61.4044 | 61.3586 | 0.00206 | 0.0017176 | 0.01054 | 0.02421 | 0.038653 | -0.032131 | 0.059276 | -61.5326 | 61.3861 | -61.5967 | -61.3998 | 61.1298 | 0.25177 | -0.11902 | 0.23346 | 61.4319 | -61.6333 | -0.19226 | 0.027465 | -0.12817 | 0.004578 | -0.22888 | -0.22888 | 0.073242 | 0.064087 | 61.2854 | 61.6379 | 122.5342 | 122.7905 | -0.12817 | 122.8363 | 61.6562 | -0.22888 | 122.7905 | -0.12817 | 61.6562 | 122.5342 | 122.8363 | -122.9553 | -122.9919
285.0625 | 123.111 | -61.441 | 61.3541 | 0.0096895 | 0.0012902 | 0.0075495 | 0.026346 | 0.040789 | -0.030422 | 0.059276 | -61.5601 | 61.3815 | -61.6104 | -61.4639 | 61.0657 | 0.17853 | -0.15564 | 0.15564 | 61.4136 | -61.6791 | -0.16937 | 0.027466 | -0.11902 | -0.022888 | -0.28839 | -0.23804 | 0.059509 | 0.050354 | 61.2854 | 61.5967 | 122.5067 | 122.8226 | -0.11902 | 122.8546 | 61.6196 | -0.23804 | 122.8226 | -0.11902 | 61.6196 | 122.5067 | 122.8546 | -122.9645 | -123.0331
286.7656 | 123.111 | -61.4365 | 61.3449 | 0.00206 | -0.00084602 | 0.010113 | 0.025064 | 0.037157 | -0.032131 | 0.056713 | -61.5601 | 61.3358 | -61.6104 | -61.4685 | 61.0703 | 0.16937 | -0.15106 | 0.15564 | 61.4227 | -61.6653 | -0.17395 | -0.009156 | -0.1236 | -0.032044 | -0.27466 | -0.22888 | 0.077819 | 0.050354 | 61.2854 | 61.5921 | 122.5067 | 122.7722 | -0.1236 | 122.8592 | 61.6058 | -0.22888 | 122.7722 | -0.1236 | 61.6058 | 122.5067 | 122.8592 | -122.9553 | -123.0103
288.4531 | 122.9599 | -61.5372 | 61.3632 | -0.0055695 | 0.0027856 | 0.010754 | 0.031046 | 0.040148 | -0.034267 | 0.057353 | -61.5646 | 61.3815 | -61.6333 | -61.4319 | 61.0657 | 0.20142 | 0.018311 | 0.21515 | 61.4822 | -61.6745 | -0.096131 | 0.018311 | -0.027466 | 0.10529 | -0.29755 | -0.13733 | 0.11902 | 0.068665 | 61.5555 | 61.7523 | 122.6028 | 122.9187 | -0.027466 | 123.0194 | 61.7386 | -0.13733 | 122.9187 | -0.027466 | 61.7386 | 122.6028 | 123.0194 | -122.9965 | -123.0377
290.1719 | 122.9645 | -61.5326 | 61.322 | -0.0055695 | 0.0053492 | 0.011181 | 0.030405 | 0.042284 | -0.034054 | 0.061626 | -61.5921 | 61.3495 | -61.6516 | -61.5143 | 61.0062 | 0.11444 | -0.036621 | 0.12817 | 61.4502 | -61.6791 | -0.11902 | 0.027466 | -0.059509 | 0.018311 | -0.31586 | -0.14648 | 0.12817 | 0.059509 | 61.496 | 61.6608 | 122.5388 | 122.8821 | -0.059509 | 122.9828 | 61.647 | -0.14648 | 122.8821 | -0.059509 | 61.647 | 122.5388 | 122.9828 | -122.9736 | -123.0011
291.9219 | 123.0331 | -61.4731 | 61.3449 | 0.0096895 | 0.0029992 | 0.0094721 | 0.023783 | 0.04143 | -0.032131 | 0.059276 | -61.5372 | 61.2991 | -61.6333 | -61.4456 | 61.0931 | 0.1831 | -0.27466 | 0.16937 | 61.3724 | -61.6882 | -0.16022 | -0.045777 | -0.064087 | 0.027465 | -0.25177 | -0.21515 | 0.027465 | 0.096131 | 61.1984 | 61.6425 | 122.5662 | 122.7722 | -0.064087 | 122.8455 | 61.6562 | -0.21515 | 122.7722 | -0.064087 | 61.6562 | 122.5662 | 122.8455 | -122.9782 | -123.0331
293.6562 | 122.9599 | -61.4685 | 61.4044 | -0.0055695 | 0.0032128 | 0.0094721 | 0.024851 | 0.039507 | -0.031704 | 0.05949 | -61.4868 | 61.377 | -61.5692 | -61.3541 | 61.171 | 0.29297 | -0.045776 | 0.32044 | 61.4548 | -61.5921 | -0.10071 | -0.027466 | -0.01831 | 0.11444 | -0.23346 | -0.1236 | 0.050354 | 0.082398 | 61.4227 | 61.7889 | 122.6395 | 122.8455 | -0.01831 | 122.9233 | 61.7615 | -0.1236 | 122.8455 | -0.01831 | 61.7615 | 122.6395 | 122.9233 | -122.9736 | -122.9965
295.3438 | 123.024 | -61.4685 | 61.3129 | 0.0096895 | 0.0010766 | 0.0086175 | 0.027841 | 0.043139 | -0.033413 | 0.060558 | -61.5784 | 61.2717 | -61.6516 | -61.4594 | 61.0565 | 0.1831 | -0.25177 | 0.16022 | 61.3953 | -61.6562 | -0.18311 | -0.041199 | -0.10986 | 0.009155 | -0.25635 | -0.18768 | 0.082398 | 0.073242 | 61.2167 | 61.6287 | 122.525 | 122.7402 | -0.10986 | 122.8638 | 61.6516 | -0.18768 | 122.7402 | -0.10986 | 61.6516 | 122.525 | 122.8638 | -122.9645 | -122.9691
297.0312 | 123.0606 | -61.4319 | 61.3541 | 0.0096895 | -0.00020502 | 0.0071221 | 0.024851 | 0.040575 | -0.032345 | 0.059062 | -61.5372 | 61.3724 | -61.6058 | -61.4136 | 61.1114 | 0.22888 | -0.12817 | 0.21515 | 61.4227 | -61.6608 | -0.17395 | 0.01831 | -0.10529 | 0.018311 | -0.24262 | -0.22888 | 0.068664 | 0.068665 | 61.3037 | 61.647 | 122.5433 | 122.8043 | -0.10529 | 122.8546 | 61.6608 | -0.22888 | 122.8043 | -0.10529 | 61.6608 | 122.5433 | 122.8546 | -122.9599 | -123.0148
298.75 | 122.9965 | -61.5417 | 61.3129 | -0.0055695 | 0.00022218 | 0.0098993 | 0.02955 | 0.041003 | -0.034054 | 0.05949 | -61.6196 | 61.322 | -61.7111 | -61.5189 | 60.9833 | 0.09613 | -0.027466 | 0.10071 | 61.4227 | -61.702 | -0.16937 | 0.009155 | -0.07782 | 0.022888 | -0.32959 | -0.16022 | 0.10986 | 0.091553 | 61.5143 | 61.6425 | 122.525 | 122.8638 | -0.07782 | 122.9645 | 61.6379 | -0.16022 | 122.8638 | -0.07782 | 61.6379 | 122.525 | 122.9645 | -123.024 | -123.0148
300.4531 | 123.0469 | -61.4822 | 61.3037 | 0.0096895 | 0.002572 | 0.01289 | 0.028055 | 0.040789 | -0.031063 | 0.059276 | -61.6333 | 61.3174 | -61.6882 | -61.5005 | 60.997 | 0.12817 | -0.16479 | 0.10529 | 61.3998 | -61.6882 | -0.20599 | 0.013733 | -0.15106 | -0.01831 | -0.3067 | -0.20599 | 0.09613 | 0.054931 | 61.3174 | 61.5875 | 122.4792 | 122.7997 | -0.15106 | 122.8821 | 61.6104 | -0.20599 | 122.7997 | -0.15106 | 61.6104 | 122.4792 | 122.8821 | -122.9919 | -122.9919
302.1562 | 123.0194 | -61.4685 | 61.2946 | 0.0096895 | 0.0053492 | 0.0092585 | 0.026132 | 0.041644 | -0.030208 | 0.059062 | -61.5738 | 61.3174 | -61.6516 | -61.4685 | 61.0474 | 0.16022 | -0.22888 | 0.15564 | 61.3266 | -61.7249 | -0.18311 | 0.022888 | -0.10529 | 0 | -0.24719 | -0.25635 | 0.032043 | 0.077819 | 61.2396 | 61.6241 | 122.5159 | 122.7859 | -0.10529 | 122.7951 | 61.6287 | -0.25635 | 122.7859 | -0.10529 | 61.6287 | 122.5159 | 122.7951 | -122.9462 | -123.0194
303.9062 | 122.9416 | -61.4456 | 61.3953 | -0.0055695 | -0.0014868 | 0.0086175 | 0.025492 | 0.038653 | -0.030636 | 0.056926 | -61.4868 | 61.3586 | -61.5601 | -61.3632 | 61.171 | 0.29755 | -0.082397 | 0.31586 | 61.4227 | -61.6287 | -0.11444 | -0.036621 | -0.041198 | 0.082398 | -0.2243 | -0.1831 | 0.027465 | 0.073243 | 61.3632 | 61.7615 | 122.6166 | 122.8043 | -0.041198 | 122.8683 | 61.7432 | -0.1831 | 122.8043 | -0.041198 | 61.7432 | 122.6166 | 122.8683 | -122.9553 | -123.024
305.5938 | 122.9553 | -61.4548 | 61.4136 | 0.0096895 | -0.00041862 | 0.0081903 | 0.02421 | 0.039935 | -0.033413 | 0.059062 | -61.4685 | 61.3449 | -61.5417 | -61.3449 | 61.1847 | 0.31128 | -0.10529 | 0.32044 | 61.409 | -61.5921 | -0.086975 | -0.068664 | -0.013733 | 0.10986 | -0.22888 | -0.13733 | -0.004577 | 0.073242 | 61.3495 | 61.7752 | 122.6395 | 122.7997 | -0.013733 | 122.8638 | 61.7661 | -0.13733 | 122.7997 | -0.013733 | 61.7661 | 122.6395 | 122.8638 | -122.9553 | -123.0057
307.2969 | 122.9553 | -61.4273 | 61.3953 | 0.0096895 | -0.00084602 | 0.010754 | 0.025705 | 0.040362 | -0.033626 | 0.057567 | -61.4548 | 61.3632 | -61.5509 | -61.3403 | 61.171 | 0.29297 | -0.14191 | 0.31128 | 61.4456 | -61.5921 | -0.1236 | -0.032044 | -0.027466 | 0.086975 | -0.2243 | -0.16479 | 0.050354 | 0.09613 | 61.2854 | 61.7386 | 122.5983 | 122.7905 | -0.027466 | 122.8729 | 61.7203 | -0.16479 | 122.7905 | -0.027466 | 61.7203 | 122.5983 | 122.8729 | -122.9462 | -122.9874
308.9844 | 122.9553 | -61.4273 | 61.3861 | -0.0055695 | 0.00022218 | 0.0086175 | 0.027414 | 0.039294 | -0.033199 | 0.058208 | -61.4914 | 61.3815 | -61.5829 | -61.377 | 61.1206 | 0.26093 | 0.009155 | 0.28381 | 61.4639 | -61.6013 | -0.15564 | -0.004577 | -0.064087 | 0.050354 | -0.2655 | -0.17395 | 0.07782 | 0.091553 | 61.4365 | 61.7111 | 122.5479 | 122.8088 | -0.064087 | 122.8912 | 61.6882 | -0.17395 | 122.8088 | -0.064087 | 61.6882 | 122.5479 | 122.8912 | -122.9691 | -122.9874
310.6875 | 122.9324 | -61.5051 | 61.3358 | 0.0096895 | -0.00063242 | 0.011181 | 0.031473 | 0.041857 | -0.032985 | 0.058635 | -61.5555 | 61.3586 | -61.6241 | -61.4182 | 61.0748 | 0.20599 | 0.013733 | 0.21057 | 61.441 | -61.6287 | -0.11902 | 0.022889 | -0.050354 | 0.086975 | -0.26093 | -0.1236 | 0.10529 | 0.068665 | 61.5189 | 61.7157 | 122.58 | 122.8638 | -0.050354 | 122.9462 | 61.7111 | -0.1236 | 122.8638 | -0.050354 | 61.7111 | 122.58 | 122.9462 | -122.9599 | -122.9645
312.3906 | 122.9691 | -61.5189 | 61.2671 | 0.017319 | 0.0019312 | 0.014813 | 0.02955 | 0.041644 | -0.032558 | 0.059276 | -61.5875 | 61.3266 | -61.6653 | -61.5097 | 60.9879 | 0.11902 | -0.018311 | 0.10986 | 61.4182 | -61.6745 | -0.14648 | 0.059509 | -0.068664 | 0.009155 | -0.27924 | -0.15564 | 0.15106 | 0.07782 | 61.5005 | 61.6287 | 122.5067 | 122.8455 | -0.068664 | 122.937 | 61.6379 | -0.15564 | 122.8455 | -0.068664 | 61.6379 | 122.5067 | 122.937 | -122.9324 | -122.9416
314.0781 | 123.0698 | -61.4731 | 61.2671 | 0.0096895 | 0.00064938 | 0.012676 | 0.027414 | 0.041216 | -0.033413 | 0.058422 | -61.6425 | 61.3174 | -61.6653 | -61.5646 | 60.9512 | 0.064087 | -0.050354 | 0.036621 | 61.4182 | -61.6882 | -0.19226 | 0.050354 | -0.16937 | -0.091553 | -0.31586 | -0.21515 | 0.15106 | 0.022888 | 61.4227 | 61.5097 | 122.4243 | 122.7905 | -0.16937 | 122.8912 | 61.5372 | -0.21515 | 122.7905 | -0.16937 | 61.5372 | 122.4243 | 122.8912 | -122.9324 | -122.9553
315.7656 | 123.0011 | -61.441 | 61.322 | 0.0096895 | -0.00041862 | 0.011181 | 0.026987 | 0.043566 | -0.034267 | 0.059062 | -61.5417 | 61.2488 | -61.6379 | -61.4456 | 61.0703 | 0.20142 | -0.2655 | 0.16022 | 61.3586 | -61.6745 | -0.19684 | -0.073242 | -0.10071 | -0.004578 | -0.25177 | -0.23346 | 0.036622 | 0.09613 | 61.1755 | 61.6013 | 122.5113 | 122.6898 | -0.10071 | 122.7997 | 61.6425 | -0.23346 | 122.6898 | -0.10071 | 61.6425 | 122.5113 | 122.7997 | -122.9599 | -122.9965
317.4531 | 123.0606 | -61.409 | 61.3678 | 0.0096895 | 0.00064938 | 0.010967 | 0.02186 | 0.037585 | -0.031063 | 0.059062 | -61.5555 | 61.3541 | -61.5875 | -61.4548 | 61.0657 | 0.20142 | -0.12817 | 0.17853 | 61.3861 | -61.6562 | -0.17853 | -0.013733 | -0.14648 | -0.045776 | -0.30212 | -0.24719 | 0.01831 | 0.032043 | 61.2808 | 61.5875 | 122.4747 | 122.7631 | -0.14648 | 122.7951 | 61.6104 | -0.24719 | 122.7631 | -0.14648 | 61.6104 | 122.4747 | 122.7951 | -122.9553 | -123.024
319.1406 | 122.9233 | -61.4456 | 61.3861 | 0.00206 | 0.0012902 | 0.0090447 | 0.025705 | 0.039721 | -0.029995 | 0.057994 | -61.4639 | 61.3449 | -61.5555 | -61.3449 | 61.1755 | 0.31128 | -0.11902 | 0.31586 | 61.4182 | -61.5967 | -0.10986 | -0.041198 | -0.01831 | 0.10071 | -0.21057 | -0.15106 | 0.032044 | 0.091553 | 61.3266 | 61.7615 | 122.6212 | 122.7905 | -0.01831 | 122.8638 | 61.7569 | -0.15106 | 122.7905 | -0.01831 | 61.7569 | 122.6212 | 122.8638 | -122.9416 | -122.9828
320.8281 | 122.9645 | -61.4594 | 61.3495 | 0.0096895 | 0.0010766 | 0.011608 | 0.028055 | 0.038012 | -0.034054 | 0.058635 | -61.5646 | 61.409 | -61.5784 | -61.4456 | 61.0519 | 0.19226 | 0.10529 | 0.21515 | 61.5143 | -61.615 | -0.11902 | 0.05951 | -0.10529 | 0.013733 | -0.29755 | -0.15564 | 0.16479 | 0.013733 | 61.5646 | 61.6745 | 122.5113 | 122.8683 | -0.10529 | 122.9736 | 61.6516 | -0.15564 | 122.8683 | -0.10529 | 61.6516 | 122.5113 | 122.9736 | -122.9279 | -122.9645
322.5625 | 123.056 | -61.4777 | 61.2579 | -0.0055695 | 0.0023584 | 0.013104 | 0.030405 | 0.042284 | -0.033413 | 0.060558 | -61.6287 | 61.3449 | -61.6791 | -61.5326 | 60.9695 | 0.086975 | -0.09613 | 0.064087 | 61.409 | -61.702 | -0.20142 | 0.086975 | -0.15106 | -0.054932 | -0.28839 | -0.2243 | 0.15106 | 0.050354 | 61.3815 | 61.5417 | 122.4472 | 122.8226 | -0.15106 | 122.8867 | 61.5646 | -0.2243 | 122.8226 | -0.15106 | 61.5646 | 122.4472 | 122.8867 | -122.937 | -122.9599
324.2656 | 123.0148 | -61.4502 | 61.2946 | 0.0096895 | 0.00086298 | 0.012035 | 0.02891 | 0.042284 | -0.032985 | 0.059917 | -61.5646 | 61.2946 | -61.647 | -61.4502 | 61.0519 | 0.1831 | -0.23804 | 0.15564 | 61.3495 | -61.6516 | -0.19684 | 0 | -0.11444 | 0 | -0.24262 | -0.20142 | 0.054931 | 0.082398 | 61.2122 | 61.6058 | 122.5021 | 122.7448 | -0.11444 | 122.7997 | 61.6333 | -0.20142 | 122.7448 | -0.11444 | 61.6333 | 122.5021 | 122.7997 | -122.9416 | -122.9462
325.9844 | 122.9416 | -61.4136 | 61.3953 | 0.00206 | 0.0023584 | 0.0079767 | 0.022928 | 0.040148 | -0.030849 | 0.058635 | -61.4639 | 61.377 | -61.5555 | -61.3403 | 61.1664 | 0.29297 | -0.13733 | 0.31128 | 61.3998 | -61.6104 | -0.14191 | -0.018311 | -0.050354 | 0.073242 | -0.22888 | -0.19684 | 0.004577 | 0.091553 | 61.2762 | 61.7249 | 122.58 | 122.7905 | -0.050354 | 122.8134 | 61.7065 | -0.19684 | 122.7905 | -0.050354 | 61.7065 | 122.58 | 122.8134 | -122.9507 | -123.0057
327.6719 | 123.0148 | -61.4639 | 61.2488 | -0.013199 | 0.00086298 | 0.0090447 | 0.026987 | 0.039294 | -0.032131 | 0.060558 | -61.615 | 61.3083 | -61.6699 | -61.5189 | 60.9741 | 0.13275 | -0.17395 | 0.086975 | 61.3541 | -61.6562 | -0.20599 | 0.05951 | -0.15106 | -0.054932 | -0.27466 | -0.19226 | 0.10529 | 0.054932 | 61.29 | 61.5509 | 122.438 | 122.7722 | -0.15106 | 122.818 | 61.5967 | -0.19226 | 122.7722 | -0.15106 | 61.5967 | 122.438 | 122.818 | -122.9187 | -122.905
329.375 | 122.9691 | -61.4868 | 61.3586 | 0.0096895 | 0.0010766 | 0.010113 | 0.028482 | 0.040362 | -0.034054 | 0.05714 | -61.5555 | 61.4044 | -61.5784 | -61.4548 | 61.0199 | 0.18768 | 0.11444 | 0.19226 | 61.4914 | -61.6425 | -0.091553 | 0.045776 | -0.068665 | 0.032043 | -0.33875 | -0.15564 | 0.13275 | 0.022888 | 61.6013 | 61.6791 | 122.5067 | 122.8912 | -0.068665 | 122.9782 | 61.6745 | -0.15564 | 122.8912 | -0.068665 | 61.6745 | 122.5067 | 122.9782 | -122.937 | -123.0011
331.0781 | 122.9324 | -61.5005 | 61.3266 | 0.0096895 | 0.004281 | 0.012676 | 0.031259 | 0.042712 | -0.034694 | 0.058635 | -61.5601 | 61.322 | -61.6425 | -61.4548 | 61.0153 | 0.16937 | -0.027466 | 0.16479 | 61.3953 | -61.6653 | -0.14191 | -0.004578 | -0.05951 | 0.045776 | -0.31128 | -0.16479 | 0.068665 | 0.082397 | 61.4731 | 61.6653 | 122.5159 | 122.8226 | -0.05951 | 122.8958 | 61.6699 | -0.16479 | 122.8226 | -0.05951 | 61.6699 | 122.5159 | 122.8958 | -122.9691 | -122.9919
332.7812 | 123.0194 | -61.4731 | 61.3083 | 0.00206 | 0.00022218 | 0.0098993 | 0.028696 | 0.042712 | -0.031277 | 0.061412 | -61.6196 | 61.2991 | -61.6699 | -61.5143 | 60.9787 | 0.10986 | -0.15106 | 0.082397 | 61.3678 | -61.6974 | -0.19684 | -0.009156 | -0.14648 | -0.041199 | -0.32959 | -0.2243 | 0.059509 | 0.050354 | 61.322 | 61.5555 | 122.4518 | 122.7722 | -0.14648 | 122.8409 | 61.5829 | -0.2243 | 122.7722 | -0.14648 | 61.5829 | 122.4518 | 122.8409 | -122.9782 | -123.0057
334.5 | 123.0194 | -61.4319 | 61.3495 | -0.013199 | 0.001504 | 0.013958 | 0.024423 | 0.039507 | -0.030636 | 0.060131 | -61.528 | 61.29 | -61.5875 | -61.4227 | 61.0565 | 0.1831 | -0.25635 | 0.17395 | 61.322 | -61.6791 | -0.15564 | -0.059509 | -0.09613 | 0.009156 | -0.29297 | -0.24719 | -0.027466 | 0.059509 | 61.1755 | 61.6058 | 122.4884 | 122.7219 | -0.09613 | 122.7539 | 61.615 | -0.24719 | 122.7219 | -0.09613 | 61.615 | 122.4884 | 122.7539 | -122.937 | -123.0286
336.2188 | 122.9691 | -61.4456 | 61.3449 | -0.0055695 | 0.0051356 | 0.013744 | 0.024851 | 0.039507 | -0.029781 | 0.058635 | -61.5097 | 61.3998 | -61.5875 | -61.4273 | 61.0657 | 0.21057 | 0.07782 | 0.21973 | 61.4548 | -61.647 | -0.14191 | 0.054931 | -0.064087 | 0.018311 | -0.27924 | -0.20142 | 0.10986 | 0.077819 | 61.5234 | 61.6653 | 122.5113 | 122.8455 | -0.064087 | 122.9004 | 61.6562 | -0.20142 | 122.8455 | -0.064087 | 61.6562 | 122.5113 | 122.9004 | -122.9324 | -122.9919
337.9062 | 123.0423 | -61.4456 | 61.2671 | 0.017319 | 0.0027856 | 0.013317 | 0.027841 | 0.042925 | -0.034054 | 0.060131 | -61.6608 | 61.3312 | -61.6837 | -61.5646 | 60.9238 | 0.082397 | -0.027466 | 0.054932 | 61.409 | -61.6837 | -0.23804 | 0.064087 | -0.21515 | -0.11902 | -0.34332 | -0.23804 | 0.14191 | 0.022888 | 61.4182 | 61.5006 | 122.3694 | 122.7768 | -0.21515 | 122.8546 | 61.528 | -0.23804 | 122.7768 | -0.21515 | 61.528 | 122.3694 | 122.8546 | -122.9507 | -122.9507
339.5938 | 123.0423 | -61.3724 | 61.3449 | 0.00206 | 0.001504 | 0.0092585 | 0.022287 | 0.039507 | -0.032558 | 0.060344 | -61.5555 | 61.3403 | -61.5784 | -61.4594 | 61.0474 | 0.18768 | -0.13733 | 0.16479 | 61.3541 | -61.6562 | -0.20599 | -0.004578 | -0.18311 | -0.086976 | -0.29755 | -0.28381 | 0.009155 | 0.022888 | 61.235 | 61.5372 | 122.4197 | 122.7127 | -0.18311 | 122.7264 | 61.5601 | -0.28381 | 122.7127 | -0.18311 | 61.5601 | 122.4197 | 122.7264 | -122.9233 | -123.0011
341.2812 | 122.9553 | -61.4594 | 61.3403 | 0.00206 | 0.0010766 | 0.013958 | 0.025705 | 0.039294 | -0.030208 | 0.056926 | -61.5555 | 61.4227 | -61.6013 | -61.4365 | 61.0382 | 0.19226 | 0.11902 | 0.21057 | 61.4731 | -61.6104 | -0.14191 | 0.082397 | -0.09613 | 0.022889 | -0.30212 | -0.15106 | 0.13275 | 0.045776 | 61.5784 | 61.6699 | 122.4976 | 122.8821 | -0.09613 | 122.9324 | 61.6516 | -0.15106 | 122.8821 | -0.09613 | 61.6516 | 122.4976 | 122.9324 | -122.9416 | -122.9507
343 | 122.9095 | -61.4868 | 61.2991 | 0.0096895 | 0.002572 | 0.012249 | 0.028269 | 0.040789 | -0.033626 | 0.059703 | -61.5234 | 61.3449 | -61.6287 | -61.4227 | 61.0199 | 0.20599 | -0.022888 | 0.19226 | 61.3907 | -61.647 | -0.14191 | 0.045777 | -0.036621 | 0.064087 | -0.27924 | -0.16022 | 0.091553 | 0.10529 | 61.4639 | 61.6791 | 122.5067 | 122.8317 | -0.036621 | 122.8775 | 61.6928 | -0.16022 | 122.8317 | -0.036621 | 61.6928 | 122.5067 | 122.8775 | -122.9279 | -122.9462
344.6875 | 122.8912 | -61.5189 | 61.2991 | -0.0055695 | 0.0017176 | 0.01289 | 0.029123 | 0.039294 | -0.032772 | 0.060344 | -61.5234 | 61.3358 | -61.6333 | -61.4182 | 61.0428 | 0.18768 | -0.018311 | 0.21515 | 61.4319 | -61.6425 | -0.11444 | 0.036621 | -0.004577 | 0.10071 | -0.25635 | -0.1236 | 0.13275 | 0.10986 | 61.5005 | 61.734 | 122.5616 | 122.8546 | -0.004577 | 122.9507 | 61.7065 | -0.1236 | 122.8546 | -0.004577 | 61.7065 | 122.5616 | 122.9507 | -122.9324 | -122.9416
346.375 | 123.024 | -61.4731 | 61.2625 | 0.00206 | 0.0010766 | 0.015026 | 0.028696 | 0.041644 | -0.032345 | 0.058635 | -61.6104 | 61.3266 | -61.647 | -61.5463 | 60.9238 | 0.073242 | -0.009155 | 0.045776 | 61.3815 | -61.6791 | -0.17395 | 0.064087 | -0.13733 | -0.073243 | -0.33875 | -0.20599 | 0.11902 | 0.036621 | 61.4639 | 61.5189 | 122.3969 | 122.7997 | -0.13733 | 122.8546 | 61.5463 | -0.20599 | 122.7997 | -0.13733 | 61.5463 | 122.3969 | 122.8546 | -122.9095 | -122.9416
348.0625 | 122.9736 | -61.4685 | 61.3083 | -0.0055695 | 0.0012902 | 0.011181 | 0.02656 | 0.042071 | -0.032131 | 0.060558 | -61.528 | 61.2488 | -61.6379 | -61.4456 | 61.0382 | 0.18768 | -0.2655 | 0.15106 | 61.3403 | -61.6333 | -0.16937 | -0.05951 | -0.059509 | 0.022888 | -0.27008 | -0.1648 | 0.032043 | 0.10986 | 61.203 | 61.6196 | 122.5067 | 122.7173 | -0.059509 | 122.8088 | 61.6562 | -0.1648 | 122.7173 | -0.059509 | 61.6562 | 122.5067 | 122.8088 | -122.9462 | -122.9416
349.75 | 123.0057 | -61.4777 | 61.2717 | 0.00206 | 0.0051356 | 0.013744 | 0.026346 | 0.040575 | -0.034267 | 0.059703 | -61.6104 | 61.3541 | -61.6516 | -61.5509 | 60.9421 | 0.091553 | -0.022888 | 0.045776 | 61.3907 | -61.6837 | -0.17395 | 0.082398 | -0.13275 | -0.073242 | -0.32959 | -0.20599 | 0.11902 | 0.041198 | 61.4548 | 61.5234 | 122.4197 | 122.8317 | -0.13275 | 122.8683 | 61.5692 | -0.20599 | 122.8317 | -0.13275 | 61.5692 | 122.4197 | 122.8683 | -122.9233 | -122.9553
351.4844 | 122.9919 | -61.377 | 61.3495 | 0.00206 | 0.001504 | 0.010113 | 0.020365 | 0.039721 | -0.02914 | 0.059917 | -61.5097 | 61.3403 | -61.5509 | -61.3815 | 61.0931 | 0.2655 | -0.13275 | 0.25635 | 61.3678 | -61.6013 | -0.17395 | -0.009155 | -0.13275 | -0.004578 | -0.25635 | -0.2243 | 0.018311 | 0.041198 | 61.2442 | 61.6333 | 122.4701 | 122.7173 | -0.13275 | 122.7448 | 61.6425 | -0.2243 | 122.7173 | -0.13275 | 61.6425 | 122.4701 | 122.7448 | -122.9004 | -122.9507
353.2969 | 122.9828 | -61.4639 | 61.3037 | 0.0096895 | 0.0010766 | 0.01289 | 0.029123 | 0.04143 | -0.032772 | 0.061412 | -61.5372 | 61.2534 | -61.6425 | -61.4365 | 61.0245 | 0.17853 | -0.26093 | 0.16479 | 61.3403 | -61.6425 | -0.17853 | -0.050354 | -0.073242 | 0.027466 | -0.27924 | -0.17853 | 0.036621 | 0.10529 | 61.203 | 61.6287 | 122.4884 | 122.7173 | -0.073242 | 122.8043 | 61.6425 | -0.17853 | 122.7173 | -0.073242 | 61.6425 | 122.4884 | 122.8043 | -122.9462 | -122.9462
355.0938 | 123.0011 | -61.4502 | 61.2808 | 0.00206 | 0.001504 | 0.01289 | 0.026987 | 0.041216 | -0.032558 | 0.060344 | -61.6058 | 61.29 | -61.6562 | -61.4731 | 60.9741 | 0.14191 | -0.19226 | 0.10071 | 61.3449 | -61.6562 | -0.20599 | 0.009155 | -0.15564 | -0.022888 | -0.3067 | -0.20599 | 0.064087 | 0.050354 | 61.2579 | 61.5509 | 122.4243 | 122.7402 | -0.15564 | 122.7951 | 61.5921 | -0.20599 | 122.7402 | -0.15564 | 61.5921 | 122.4243 | 122.7951 | -122.937 | -122.937
356.7969 | 122.937 | -61.441 | 61.3358 | 0.017319 | -0.00063242 | 0.012676 | 0.026987 | 0.039721 | -0.032985 | 0.059062 | -61.5509 | 61.3953 | -61.5875 | -61.4273 | 61.0291 | 0.18768 | 0.11902 | 0.19684 | 61.496 | -61.6013 | -0.14648 | 0.05951 | -0.10986 | 0.013733 | -0.3067 | -0.16022 | 0.16022 | 0.036621 | 61.5601 | 61.6379 | 122.4701 | 122.8363 | -0.10986 | 122.937 | 61.6287 | -0.16022 | 122.8363 | -0.10986 | 61.6287 | 122.4701 | 122.937 | -122.9233 | -122.937
358.5469 | 122.8867 | -61.4319 | 61.3724 | 0.0096895 | 0.0019312 | 0.0092585 | 0.026132 | 0.037798 | -0.033199 | 0.057994 | -61.4502 | 61.3403 | -61.5005 | -61.3312 | 61.1298 | 0.29755 | -0.086975 | 0.3067 | 61.4044 | -61.5692 | -0.068664 | -0.032043 | -0.01831 | 0.10071 | -0.24261 | -0.13733 | 0.032044 | 0.050354 | 61.3449 | 61.7386 | 122.5616 | 122.7722 | -0.01831 | 122.8363 | 61.7294 | -0.13733 | 122.7722 | -0.01831 | 61.7294 | 122.5616 | 122.8363 | -122.8729 | -122.9416
360.2656 | 122.9462 | -61.4548 | 61.3266 | 0.00206 | -0.00063242 | 0.0098993 | 0.026346 | 0.038866 | -0.032345 | 0.061626 | -61.5417 | 61.4044 | -61.5692 | -61.4227 | 61.0428 | 0.18768 | 0.13275 | 0.21515 | 61.4914 | -61.5921 | -0.11444 | 0.07782 | -0.086975 | 0.032044 | -0.28381 | -0.13733 | 0.16479 | 0.027466 | 61.5875 | 61.6699 | 122.4976 | 122.8592 | -0.086975 | 122.9462 | 61.6425 | -0.13733 | 122.8592 | -0.086975 | 61.6425 | 122.4976 | 122.9462 | -122.8958 | -122.9187
362.0312 | 122.9599 | -61.3815 | 61.3678 | 0.00206 | 0.0021448 | 0.011822 | 0.022714 | 0.038866 | -0.028713 | 0.059703 | -61.4594 | 61.3495 | -61.5509 | -61.3449 | 61.1252 | 0.27924 | -0.14191 | 0.27008 | 61.3998 | -61.5829 | -0.16937 | -0.018311 | -0.07782 | 0.036621 | -0.24262 | -0.20142 | 0.032043 | 0.091552 | 61.2396 | 61.6516 | 122.5067 | 122.731 | -0.07782 | 122.7814 | 61.6608 | -0.20142 | 122.731 | -0.07782 | 61.6608 | 122.5067 | 122.7814 | -122.9187 | -122.9507
363.7344 | 123.0103 | -61.377 | 61.3174 | 0.0096895 | -0.002555 | 0.0088311 | 0.023783 | 0.038012 | -0.02914 | 0.059062 | -61.528 | 61.2625 | -61.6333 | -61.4136 | 61.0062 | 0.17853 | -0.21515 | 0.16022 | 61.3312 | -61.6241 | -0.25635 | -0.054932 | -0.15106 | -0.036621 | -0.31128 | -0.24719 | 0.013733 | 0.10529 | 61.1618 | 61.5372 | 122.3831 | 122.6395 | -0.15106 | 122.7081 | 61.5555 | -0.24719 | 122.6395 | -0.15106 | 61.5555 | 122.3831 | 122.7081 | -122.9507 | -122.9416
365.5 | 122.8638 | -61.4777 | 61.2854 | 0.0096895 | 0.0012902 | 0.011395 | 0.032114 | 0.039294 | -0.037258 | 0.057781 | -61.5326 | 61.3403 | -61.6241 | -61.3953 | 61.0199 | 0.21057 | 0.004578 | 0.23804 | 61.4456 | -61.6013 | -0.14649 | 0.054932 | -0.054932 | 0.082397 | -0.2655 | -0.1236 | 0.16022 | 0.091553 | 61.4822 | 61.7157 | 122.4976 | 122.818 | -0.054932 | 122.9233 | 61.6882 | -0.1236 | 122.818 | -0.054932 | 61.6882 | 122.4976 | 122.9233 | -122.9095 | -122.8867
367.2188 | 122.9279 | -61.4273 | 61.3358 | 0.017319 | 0.00086298 | 0.01524 | 0.026987 | 0.037585 | -0.032345 | 0.060344 | -61.5051 | 61.3678 | -61.5555 | -61.4227 | 61.0611 | 0.19684 | 0.091553 | 0.2243 | 61.4227 | -61.5967 | -0.12817 | 0.032044 | -0.07782 | 0.004578 | -0.27466 | -0.16937 | 0.086975 | 0.050354 | 61.5189 | 61.6516 | 122.4884 | 122.7951 | -0.07782 | 122.85 | 61.6241 | -0.16937 | 122.7951 | -0.07782 | 61.6241 | 122.4884 | 122.85 | -122.8912 | -122.9324
368.9219 | 122.9919 | -61.4273 | 61.2396 | 0.0096895 | 0.0032128 | 0.014172 | 0.030405 | 0.041216 | -0.032345 | 0.059276 | -61.6058 | 61.3403 | -61.6196 | -61.5051 | 60.9329 | 0.09613 | -0.091553 | 0.068665 | 61.3678 | -61.6791 | -0.19226 | 0.10071 | -0.17853 | -0.07782 | -0.3067 | -0.25177 | 0.12817 | 0.013733 | 61.3358 | 61.496 | 122.3602 | 122.7676 | -0.17853 | 122.7951 | 61.5234 | -0.25177 | 122.7676 | -0.17853 | 61.5234 | 122.3602 | 122.7951 | -122.8592 | -122.9187
370.7031 | 122.9507 | -61.4182 | 61.2717 | 0.0096895 | 0.00022218 | 0.01289 | 0.027628 | 0.041003 | -0.032772 | 0.059276 | -61.528 | 61.2442 | -61.6196 | -61.409 | 61.0153 | 0.19684 | -0.27466 | 0.15106 | 61.3083 | -61.6562 | -0.20142 | -0.027465 | -0.10986 | 0.009155 | -0.25635 | -0.23804 | 0.036622 | 0.091553 | 61.1435 | 61.5692 | 122.4335 | 122.6624 | -0.10986 | 122.7264 | 61.615 | -0.23804 | 122.6624 | -0.10986 | 61.615 | 122.4335 | 122.7264 | -122.8912 | -122.9279
372.4688 | 122.9645 | -61.409 | 61.2671 | 0.0096895 | -0.0014868 | 0.01054 | 0.026346 | 0.040575 | -0.03384 | 0.058635 | -61.528 | 61.2488 | -61.6104 | -61.409 | 61.0336 | 0.17853 | -0.29755 | 0.16022 | 61.2991 | -61.6379 | -0.20142 | -0.018311 | -0.11902 | 0 | -0.23346 | -0.22888 | 0.032043 | 0.082398 | 61.1115 | 61.5692 | 122.4426 | 122.6578 | -0.11902 | 122.7081 | 61.5875 | -0.22888 | 122.6578 | -0.11902 | 61.5875 | 122.4426 | 122.7081 | -122.8775 | -122.905
374.1875 | 122.9599 | -61.4273 | 61.2991 | 0.00206 | 0.0023584 | 0.010967 | 0.026773 | 0.041644 | -0.032558 | 0.059062 | -61.5097 | 61.2671 | -61.6058 | -61.4182 | 61.0336 | 0.18768 | -0.27466 | 0.16022 | 61.3037 | -61.6104 | -0.17853 | -0.032043 | -0.082398 | 0.009155 | -0.2655 | -0.18311 | 0.004578 | 0.09613 | 61.1526 | 61.5875 | 122.4609 | 122.6944 | -0.082398 | 122.731 | 61.615 | -0.18311 | 122.6944 | -0.082398 | 61.615 | 122.4609 | 122.731 | -122.905 | -122.9095
375.875 | 122.9141 | -61.4044 | 61.377 | 0.00206 | -0.00020502 | 0.0098993 | 0.023783 | 0.039294 | -0.032558 | 0.059703 | -61.4548 | 61.3129 | -61.5417 | -61.3266 | 61.1298 | 0.28839 | -0.14191 | 0.28381 | 61.3861 | -61.5829 | -0.13733 | -0.064087 | -0.050354 | 0.07782 | -0.24719 | -0.17853 | 0.009155 | 0.086975 | 61.2625 | 61.6882 | 122.5342 | 122.7173 | -0.050354 | 122.7905 | 61.6928 | -0.17853 | 122.7173 | -0.050354 | 61.6928 | 122.5342 | 122.7905 | -122.9187 | -122.9599
377.5938 | 122.9965 | -61.377 | 61.3312 | 0.0096895 | 0.001504 | 0.014813 | 0.026132 | 0.040148 | -0.033199 | 0.058849 | -61.5097 | 61.2762 | -61.5738 | -61.4227 | 61.0199 | 0.16937 | -0.21057 | 0.16479 | 61.3403 | -61.6562 | -0.19684 | -0.054932 | -0.13275 | -0.045776 | -0.31128 | -0.27924 | 0.009155 | 0.064087 | 61.1664 | 61.5417 | 122.3969 | 122.6532 | -0.13275 | 122.7173 | 61.5463 | -0.27924 | 122.6532 | -0.13275 | 61.5463 | 122.3969 | 122.7173 | -122.905 | -122.9874
379.375 | 122.9141 | -61.4319 | 61.3129 | 0.00206 | 0.0029992 | 0.0051995 | 0.027628 | 0.040148 | -0.032558 | 0.061412 | -61.5417 | 61.3907 | -61.5738 | -61.4136 | 61.0153 | 0.19684 | 0.10529 | 0.21057 | 61.4685 | -61.5784 | -0.14191 | 0.07782 | -0.10986 | 0.018311 | -0.29755 | -0.14648 | 0.15564 | 0.032044 | 61.5372 | 61.6425 | 122.4472 | 122.8226 | -0.10986 | 122.9004 | 61.6287 | -0.14648 | 122.8226 | -0.10986 | 61.6287 | 122.4472 | 122.9004 | -122.8867 | -122.8912
381.0781 | 122.8409 | -61.4868 | 61.2946 | -0.0055695 | 0.0012902 | 0.0094721 | 0.031473 | 0.041644 | -0.035122 | 0.057781 | -61.5234 | 61.322 | -61.5829 | -61.4044 | 61.0245 | 0.20599 | 0.018311 | 0.21973 | 61.3953 | -61.6058 | -0.096131 | 0.027465 | -0.036621 | 0.082397 | -0.27008 | -0.11902 | 0.10071 | 0.05951 | 61.5051 | 61.7065 | 122.5113 | 122.8088 | -0.036621 | 122.8821 | 61.6928 | -0.11902 | 122.8088 | -0.036621 | 61.6928 | 122.5113 | 122.8821 | -122.8775 | -122.9004
382.8594 | 122.9965 | -61.377 | 61.3129 | 0.00206 | 0.0012902 | 0.0088311 | 0.022074 | 0.040575 | -0.032772 | 0.05949 | -61.5417 | 61.2946 | -61.5875 | -61.4136 | 61.0382 | 0.20599 | -0.14648 | 0.17395 | 61.3495 | -61.615 | -0.21057 | -0.01831 | -0.16479 | -0.036621 | -0.27466 | -0.23804 | 0.036621 | 0.045776 | 61.2305 | 61.5509 | 122.4152 | 122.6715 | -0.16479 | 122.7264 | 61.5829 | -0.23804 | 122.6715 | -0.16479 | 61.5829 | 122.4152 | 122.7264 | -122.9004 | -122.9279
384.625 | 122.8729 | -61.3998 | 61.3907 | 0.017319 | 0.0010766 | 0.010967 | 0.026346 | 0.040148 | -0.032772 | 0.057781 | -61.4319 | 61.3449 | -61.5143 | -61.2991 | 61.1114 | 0.30212 | -0.10071 | 0.31128 | 61.4044 | -61.5601 | -0.11444 | -0.045776 | -0.032044 | 0.10071 | -0.27924 | -0.16022 | 0.013733 | 0.082397 | 61.2991 | 61.7111 | 122.5113 | 122.7448 | -0.032044 | 122.8043 | 61.702 | -0.16022 | 122.7448 | -0.032044 | 61.702 | 122.5113 | 122.8043 | -122.905 | -122.9507
386.3438 | 122.9919 | -61.4502 | 61.2488 | -0.0055695 | 0.0019312 | 0.015881 | 0.029337 | 0.041216 | -0.032985 | 0.057994 | -61.6013 | 61.2991 | -61.6653 | -61.5189 | 60.9146 | 0.082397 | -0.045776 | 0.059509 | 61.3632 | -61.6837 | -0.21515 | 0.050354 | -0.15106 | -0.068665 | -0.33417 | -0.23346 | 0.11444 | 0.064087 | 61.4044 | 61.5097 | 122.3648 | 122.7493 | -0.15106 | 122.8134 | 61.5326 | -0.23346 | 122.7493 | -0.15106 | 61.5326 | 122.3648 | 122.8134 | -122.9141 | -122.9324
388.125 | 122.85 | -61.3998 | 61.377 | 0.00206 | 0.0017176 | 0.012676 | 0.026346 | 0.039294 | -0.031704 | 0.058208 | -61.4319 | 61.3312 | -61.5005 | -61.3083 | 61.1252 | 0.3067 | -0.082397 | 0.32501 | 61.3632 | -61.5875 | -0.10071 | -0.045776 | -0.032044 | 0.091552 | -0.25177 | -0.18768 | -0.013733 | 0.068664 | 61.3174 | 61.7249 | 122.525 | 122.731 | -0.032044 | 122.7631 | 61.7065 | -0.18768 | 122.731 | -0.032044 | 61.7065 | 122.525 | 122.7631 | -122.8775 | -122.9645
389.8281 | 122.8363 | -61.4868 | 61.2946 | 0.017319 | 0.0021448 | 0.01054 | 0.029123 | 0.041003 | -0.034481 | 0.05949 | -61.4914 | 61.322 | -61.6058 | -61.3861 | 61.0291 | 0.21973 | -0.004578 | 0.21973 | 61.3861 | -61.6013 | -0.11902 | 0.027465 | -0.004578 | 0.10071 | -0.2655 | -0.11444 | 0.091552 | 0.11444 | 61.4822 | 61.7065 | 122.5159 | 122.8088 | -0.004578 | 122.8729 | 61.7065 | -0.11444 | 122.8088 | -0.004578 | 61.7065 | 122.5159 | 122.8729 | -122.9004 | -122.8958
391.5625 | 122.8821 | -61.4594 | 61.2808 | 0.017319 | 0.002572 | 0.0094721 | 0.029978 | 0.040789 | -0.033626 | 0.059062 | -61.5372 | 61.3037 | -61.6104 | -61.4594 | 60.9375 | 0.12817 | -0.022888 | 0.1236 | 61.3953 | -61.6241 | -0.15106 | 0.022888 | -0.077819 | 0 | -0.34332 | -0.1648 | 0.11444 | 0.073243 | 61.4365 | 61.5829 | 122.3969 | 122.7631 | -0.077819 | 122.8546 | 61.5875 | -0.1648 | 122.7631 | -0.077819 | 61.5875 | 122.3969 | 122.8546 | -122.8912 | -122.905
393.2812 | 122.8683 | -61.4319 | 61.3037 | 0.00206 | 0.0023584 | 0.0049859 | 0.025278 | 0.041003 | -0.032985 | 0.060344 | -61.5372 | 61.3724 | -61.5555 | -61.4044 | 61.0382 | 0.19684 | 0.10529 | 0.21515 | 61.4456 | -61.5875 | -0.1236 | 0.068664 | -0.10529 | 0.027466 | -0.2655 | -0.15564 | 0.14191 | 0.018311 | 61.5372 | 61.647 | 122.4701 | 122.8043 | -0.10529 | 122.8775 | 61.6287 | -0.15564 | 122.8043 | -0.10529 | 61.6287 | 122.4701 | 122.8775 | -122.8592 | -122.8912
395.0469 | 122.905 | -61.4273 | 61.322 | 0.0096895 | 0.0032128 | 0.010754 | 0.025705 | 0.040362 | -0.032345 | 0.058635 | -61.5234 | 61.3724 | -61.5326 | -61.4273 | 61.0199 | 0.20142 | 0.14191 | 0.20142 | 61.4365 | -61.5921 | -0.10529 | 0.050354 | -0.09613 | 0 | -0.30212 | -0.16479 | 0.11444 | 0.009156 | 61.5692 | 61.6287 | 122.4472 | 122.7997 | -0.09613 | 122.8638 | 61.6287 | -0.16479 | 122.7997 | -0.09613 | 61.6287 | 122.4472 | 122.8638 | -122.8546 | -122.9141
396.75 | 122.9233 | -61.4182 | 61.2854 | 0.00206 | 0.001504 | 0.012035 | 0.026987 | 0.042071 | -0.032345 | 0.060344 | -61.5005 | 61.2762 | -61.5784 | -61.409 | 61.0291 | 0.1831 | -0.27466 | 0.14648 | 61.3083 | -61.6287 | -0.16022 | -0.009155 | -0.082397 | 0.009155 | -0.25635 | -0.21057 | 0.022889 | 0.07782 | 61.1435 | 61.5646 | 122.4472 | 122.6944 | -0.082397 | 122.7264 | 61.6013 | -0.21057 | 122.6944 | -0.082397 | 61.6013 | 122.4472 | 122.7264 | -122.8638 | -122.9141
398.5312 | 122.9828 | -61.4227 | 61.235 | 0.00206 | 0.00064938 | 0.012463 | 0.02891 | 0.039721 | -0.031704 | 0.059276 | -61.5921 | 61.2671 | -61.647 | -61.496 | 60.91 | 0.10529 | -0.11902 | 0.054932 | 61.3495 | -61.647 | -0.22431 | 0.032044 | -0.16937 | -0.073243 | -0.32501 | -0.22431 | 0.11444 | 0.054932 | 61.3037 | 61.4777 | 122.3328 | 122.6898 | -0.16937 | 122.7722 | 61.528 | -0.22431 | 122.6898 | -0.16937 | 61.528 | 122.3328 | 122.7722 | -122.8821 | -122.8821
400.25 | 122.9828 | -61.441 | 61.2305 | 0.0096895 | 0.0010766 | 0.01054 | 0.026987 | 0.042498 | -0.032131 | 0.060771 | -61.6104 | 61.2579 | -61.6425 | -61.5234 | 60.9055 | 0.082397 | -0.045776 | 0.050354 | 61.3541 | -61.6608 | -0.20142 | 0.027466 | -0.16937 | -0.082397 | -0.32501 | -0.21973 | 0.1236 | 0.032043 | 61.3953 | 61.4914 | 122.3465 | 122.699 | -0.16937 | 122.7951 | 61.5234 | -0.21973 | 122.699 | -0.16937 | 61.5234 | 122.3465 | 122.7951 | -122.8729 | -122.8912
401.9531 | 122.9233 | -61.4273 | 61.2854 | 0.00206 | 8.578e-06 | 0.013744 | 0.025064 | 0.040362 | -0.032345 | 0.060131 | -61.5051 | 61.2442 | -61.5692 | -61.4044 | 61.0336 | 0.20142 | -0.28381 | 0.17395 | 61.3266 | -61.6104 | -0.14191 | -0.041198 | -0.07782 | 0.022888 | -0.25177 | -0.18311 | 0.041199 | 0.064087 | 61.1435 | 61.6013 | 122.4609 | 122.6715 | -0.07782 | 122.7539 | 61.6287 | -0.18311 | 122.6715 | -0.07782 | 61.6287 | 122.4609 | 122.7539 | -122.8546 | -122.8958
403.7344 | 122.9279 | -61.4227 | 61.2991 | -0.0055695 | 0.00043578 | 0.013104 | 0.027201 | 0.042498 | -0.029995 | 0.05714 | -61.496 | 61.2442 | -61.5784 | -61.4044 | 61.0199 | 0.19684 | -0.29297 | 0.16022 | 61.3083 | -61.6379 | -0.15564 | -0.054931 | -0.073243 | 0.01831 | -0.27924 | -0.21515 | 0.009156 | 0.082397 | 61.1298 | 61.5829 | 122.4426 | 122.6669 | -0.073243 | 122.731 | 61.6196 | -0.21515 | 122.6669 | -0.073243 | 61.6196 | 122.4426 | 122.731 | -122.8775 | -122.937
405.5 | 122.9462 | -61.4502 | 61.2259 | 0.00206 | 0.0029992 | 0.011822 | 0.028696 | 0.041003 | -0.033626 | 0.060344 | -61.6013 | 61.3037 | -61.6379 | -61.4822 | 60.9192 | 0.091553 | 0.009155 | 0.086975 | 61.3815 | -61.6241 | -0.18768 | 0.07782 | -0.15106 | -0.032044 | -0.3067 | -0.17395 | 0.15564 | 0.036621 | 61.4594 | 61.5372 | 122.3694 | 122.7539 | -0.15106 | 122.8317 | 61.5417 | -0.17395 | 122.7539 | -0.15106 | 61.5417 | 122.3694 | 122.8317 | -122.8638 | -122.85
407.2344 | 122.937 | -61.3541 | 61.3266 | 0.00206 | 0.0012902 | 0.0092585 | 0.021433 | 0.038439 | -0.029995 | 0.057781 | -61.4639 | 61.3358 | -61.5372 | -61.3358 | 61.084 | 0.27466 | -0.12817 | 0.25635 | 61.3678 | -61.5921 | -0.18311 | 0.009155 | -0.10986 | 0.018311 | -0.24262 | -0.23804 | 0.041199 | 0.073242 | 61.2259 | 61.6104 | 122.438 | 122.6898 | -0.10986 | 122.7219 | 61.6287 | -0.23804 | 122.6898 | -0.10986 | 61.6287 | 122.438 | 122.7219 | -122.8638 | -122.9187
409.0156 | 122.8317 | -61.4182 | 61.3724 | 0.00206 | -0.00063242 | 0.0086175 | 0.024851 | 0.040148 | -0.030422 | 0.059276 | -61.4136 | 61.322 | -61.5189 | -61.2946 | 61.1206 | 0.3067 | -0.10529 | 0.33417 | 61.3678 | -61.5646 | -0.10071 | -0.050354 | 0.004578 | 0.1236 | -0.25177 | -0.14648 | -0.004577 | 0.10529 | 61.3129 | 61.7523 | 122.5388 | 122.7402 | 0.004578 | 122.7859 | 61.7249 | -0.14648 | 122.7402 | 0.004578 | 61.7249 | 122.5388 | 122.7859 | -122.8912 | -122.937
410.7969 | 122.905 | -61.4182 | 61.2946 | -0.0055695 | 0.00086298 | 0.0071221 | 0.027201 | 0.039294 | -0.033199 | 0.056285 | -61.4822 | 61.2396 | -61.6013 | -61.377 | 61.0291 | 0.20142 | -0.2655 | 0.17395 | 61.2854 | -61.6333 | -0.1831 | -0.054932 | -0.064087 | 0.041199 | -0.2655 | -0.21515 | -0.009156 | 0.11902 | 61.1526 | 61.5921 | 122.4472 | 122.6578 | -0.064087 | 122.7036 | 61.6196 | -0.21515 | 122.6578 | -0.064087 | 61.6196 | 122.4472 | 122.7036 | -122.8958 | -122.9279
412.5938 | 122.9782 | -61.4182 | 61.2076 | -0.0055695 | 0.0036402 | 0.010754 | 0.029337 | 0.041003 | -0.034054 | 0.058422 | -61.5921 | 61.2991 | -61.6653 | -61.5097 | 60.9009 | 0.073242 | -0.073242 | 0.041199 | 61.3907 | -61.6287 | -0.24719 | 0.091552 | -0.17395 | -0.091553 | -0.3067 | -0.21057 | 0.18311 | 0.073242 | 61.3449 | 61.4594 | 122.319 | 122.7173 | -0.17395 | 122.8088 | 61.4914 | -0.21057 | 122.7173 | -0.17395 | 61.4914 | 122.319 | 122.8088 | -122.8729 | -122.8363
414.3125 | 122.9599 | -61.4456 | 61.2396 | 0.00206 | 0.00022218 | 0.013744 | 0.028696 | 0.040148 | -0.032772 | 0.05949 | -61.615 | 61.29 | -61.6333 | -61.5051 | 60.9055 | 0.07782 | -0.050354 | 0.045776 | 61.3495 | -61.6516 | -0.18768 | 0.050354 | -0.16937 | -0.059509 | -0.33417 | -0.20599 | 0.10986 | 0.018311 | 61.3953 | 61.4914 | 122.3511 | 122.7356 | -0.16937 | 122.7951 | 61.5234 | -0.20599 | 122.7356 | -0.16937 | 61.5234 | 122.3511 | 122.7951 | -122.8729 | -122.8912
416.0781 | 122.9507 | -61.4456 | 61.2396 | 0.00206 | 0.00086298 | 0.01289 | 0.031259 | 0.041857 | -0.034267 | 0.059276 | -61.5784 | 61.29 | -61.6196 | -61.496 | 60.9055 | 0.09613 | -0.018311 | 0.064087 | 61.3632 | -61.6425 | -0.17395 | 0.050354 | -0.13275 | -0.050354 | -0.33417 | -0.19684 | 0.1236 | 0.041199 | 61.4273 | 61.5097 | 122.3511 | 122.7356 | -0.13275 | 122.8088 | 61.5417 | -0.19684 | 122.7356 | -0.13275 | 61.5417 | 122.3511 | 122.8088 | -122.8592 | -122.8821
417.8438 | 122.9187 | -61.409 | 61.2671 | 0.0096895 | 0.001504 | 0.01054 | 0.025492 | 0.042071 | -0.032131 | 0.058849 | -61.4868 | 61.2442 | -61.5784 | -61.3998 | 61.0153 | 0.19226 | -0.28839 | 0.14648 | 61.2579 | -61.6608 | -0.16937 | -0.022888 | -0.077819 | 0.009156 | -0.25177 | -0.25177 | -0.009155 | 0.091553 | 61.1206 | 61.5555 | 122.4243 | 122.6532 | -0.077819 | 122.6669 | 61.6013 | -0.25177 | 122.6532 | -0.077819 | 61.6013 | 122.4243 | 122.6669 | -122.8455 | -122.9279
419.6406 | 122.9507 | -61.3632 | 61.3083 | 0.00206 | 0.00022218 | 0.011181 | 0.023783 | 0.038439 | -0.028499 | 0.059276 | -61.4822 | 61.2991 | -61.5372 | -61.377 | 61.0565 | 0.23804 | -0.12817 | 0.23346 | 61.3541 | -61.5646 | -0.17395 | -0.009156 | -0.11902 | -0.013733 | -0.25177 | -0.20142 | 0.045776 | 0.054931 | 61.235 | 61.5967 | 122.4197 | 122.6624 | -0.11902 | 122.7173 | 61.6013 | -0.20142 | 122.6624 | -0.11902 | 61.6013 | 122.4197 | 122.7173 | -122.8455 | -122.8729
421.3438 | 122.8912 | -61.4685 | 61.2579 | 0.00206 | 0.0010766 | 0.01054 | 0.02891 | 0.039721 | -0.032558 | 0.060131 | -61.5829 | 61.2946 | -61.6379 | -61.4731 | 60.9238 | 0.10071 | -0.018311 | 0.082397 | 61.377 | -61.6333 | -0.16937 | 0.036621 | -0.11444 | -0.004577 | -0.33417 | -0.1648 | 0.11902 | 0.054931 | 61.4502 | 61.5509 | 122.3923 | 122.7631 | -0.11444 | 122.8455 | 61.5692 | -0.1648 | 122.7631 | -0.11444 | 61.5692 | 122.3923 | 122.8455 | -122.8958 | -122.8912
423.125 | 122.9462 | -61.441 | 61.2305 | 0.0096895 | 0.0029992 | 0.01289 | 0.028055 | 0.041857 | -0.03149 | 0.060344 | -61.5967 | 61.2946 | -61.6196 | -61.5143 | 60.8963 | 0.07782 | -0.036621 | 0.068665 | 61.377 | -61.6516 | -0.17853 | 0.064087 | -0.15564 | -0.073242 | -0.33417 | -0.21057 | 0.14648 | 0.022888 | 61.4044 | 61.5097 | 122.3373 | 122.7356 | -0.15564 | 122.818 | 61.5189 | -0.21057 | 122.7356 | -0.15564 | 61.5189 | 122.3373 | 122.818 | -122.85 | -122.8821
424.8906 | 122.8775 | -61.409 | 61.322 | 0.017319 | 0.0010766 | 0.011395 | 0.024851 | 0.039935 | -0.031277 | 0.058208 | -61.5051 | 61.3632 | -61.5463 | -61.4044 | 61.0062 | 0.19684 | 0.12817 | 0.20142 | 61.4456 | -61.5692 | -0.13733 | 0.041199 | -0.09613 | 0.004578 | -0.31586 | -0.16022 | 0.1236 | 0.041199 | 61.5372 | 61.6104 | 122.4152 | 122.7722 | -0.09613 | 122.8546 | 61.6058 | -0.16022 | 122.7722 | -0.09613 | 61.6058 | 122.4152 | 122.8546 | -122.8683 | -122.8912
426.6719 | 122.9187 | -61.441 | 61.235 | 0.00206 | 0.0032128 | 0.014172 | 0.030618 | 0.039507 | -0.033199 | 0.060771 | -61.5784 | 61.29 | -61.6104 | -61.4914 | 60.9329 | 0.10071 | -0.009155 | 0.086975 | 61.3632 | -61.6516 | -0.16937 | 0.054932 | -0.13733 | -0.050354 | -0.30212 | -0.21057 | 0.12817 | 0.032044 | 61.4319 | 61.528 | 122.374 | 122.731 | -0.13733 | 122.8043 | 61.5417 | -0.21057 | 122.731 | -0.13733 | 61.5417 | 122.374 | 122.8043 | -122.8455 | -122.8867
428.3906 | 122.9233 | -61.4365 | 61.2305 | 0.00206 | 0.0051356 | 0.010967 | 0.027841 | 0.040789 | -0.031063 | 0.059062 | -61.5646 | 61.3312 | -61.6058 | -61.4777 | 60.9192 | 0.10071 | -0.004578 | 0.073242 | 61.377 | -61.6608 | -0.16937 | 0.10071 | -0.12817 | -0.041199 | -0.31128 | -0.22431 | 0.14648 | 0.041199 | 61.4319 | 61.5097 | 122.3557 | 122.7676 | -0.12817 | 122.8134 | 61.5372 | -0.22431 | 122.7676 | -0.12817 | 61.5372 | 122.3557 | 122.8134 | -122.8363 | -122.8912
430.1094 | 122.8867 | -61.4136 | 61.2808 | 0.00206 | 0.0038538 | 0.015881 | 0.020578 | 0.042284 | -0.031063 | 0.058208 | -61.4914 | 61.2259 | -61.5967 | -61.3907 | 61.0107 | 0.20142 | -0.27008 | 0.17853 | 61.2717 | -61.6287 | -0.18311 | -0.054932 | -0.07782 | 0.022888 | -0.27008 | -0.21515 | -0.009156 | 0.10529 | 61.1435 | 61.5921 | 122.4243 | 122.6395 | -0.07782 | 122.6852 | 61.615 | -0.21515 | 122.6395 | -0.07782 | 61.615 | 122.4243 | 122.6852 | -122.8775 | -122.9095
431.875 | 122.9279 | -61.3495 | 61.3174 | 0.00206 | 0.00043578 | 0.0088311 | 0.023996 | 0.03673 | -0.031063 | 0.058849 | -61.4502 | 61.2991 | -61.5189 | -61.3403 | 61.084 | 0.25635 | -0.13733 | 0.2655 | 61.377 | -61.5555 | -0.16937 | -0.018311 | -0.10071 | 0.009155 | -0.23346 | -0.20599 | 0.059509 | 0.068665 | 61.2122 | 61.615 | 122.4335 | 122.6486 | -0.10071 | 122.7264 | 61.6058 | -0.20599 | 122.6486 | -0.10071 | 61.6058 | 122.4335 | 122.7264 | -122.8363 | -122.8729
433.6719 | 122.8134 | -61.4319 | 61.2671 | 0.0096895 | 0.0010766 | 0.012676 | 0.030832 | 0.040362 | -0.033626 | 0.058849 | -61.4914 | 61.322 | -61.5921 | -61.3815 | 61.0016 | 0.2243 | 0.004578 | 0.2243 | 61.4136 | -61.5738 | -0.16022 | 0.054931 | -0.059509 | 0.050354 | -0.2655 | -0.14191 | 0.14648 | 0.10071 | 61.4365 | 61.6562 | 122.4335 | 122.7539 | -0.059509 | 122.8455 | 61.6562 | -0.14191 | 122.7539 | -0.059509 | 61.6562 | 122.4335 | 122.8455 | -122.8592 | -122.8409
435.3906 | 122.9553 | -61.4273 | 61.1984 | 0.0096895 | 0.0038538 | 0.010967 | 0.029764 | 0.041857 | -0.033413 | 0.059917 | -61.5829 | 61.2579 | -61.6333 | -61.5051 | 60.9055 | 0.086975 | -0.064087 | 0.064087 | 61.3632 | -61.6241 | -0.20599 | 0.05951 | -0.15564 | -0.07782 | -0.29297 | -0.19684 | 0.16479 | 0.050354 | 61.3632 | 61.4914 | 122.3328 | 122.6852 | -0.15564 | 122.7905 | 61.5143 | -0.19684 | 122.6852 | -0.15564 | 61.5143 | 122.3328 | 122.7905 | -122.8317 | -122.8226
437.1719 | 122.8134 | -61.441 | 61.2534 | 0.0096895 | 0.0010766 | 0.012249 | 0.029978 | 0.040789 | -0.034054 | 0.060771 | -61.4822 | 61.3129 | -61.5921 | -61.3907 | 61.0199 | 0.21515 | 0.009155 | 0.21515 | 61.377 | -61.5784 | -0.15106 | 0.059509 | -0.041199 | 0.050354 | -0.23346 | -0.13733 | 0.1236 | 0.10986 | 61.4502 | 61.6562 | 122.4609 | 122.7539 | -0.041199 | 122.818 | 61.6562 | -0.13733 | 122.7539 | -0.041199 | 61.6562 | 122.4609 | 122.818 | -122.8455 | -122.8317
438.9531 | 122.8592 | -61.3861 | 61.2991 | -0.0055695 | 0.0049218 | 0.0086175 | 0.024637 | 0.03908 | -0.028927 | 0.059276 | -61.4914 | 61.3586 | -61.5234 | -61.409 | 61.0016 | 0.19226 | 0.10071 | 0.2243 | 61.4227 | -61.6058 | -0.13733 | 0.05951 | -0.10529 | -0.022889 | -0.29755 | -0.21973 | 0.1236 | 0.032043 | 61.4868 | 61.6104 | 122.3877 | 122.7448 | -0.10529 | 122.8088 | 61.5784 | -0.21973 | 122.7448 | -0.10529 | 61.5784 | 122.3877 | 122.8088 | -122.8226 | -122.905
440.6719 | 122.8912 | -61.409 | 61.2717 | -0.0055695 | 0.00064938 | 0.011181 | 0.025064 | 0.040362 | -0.030849 | 0.060344 | -61.4868 | 61.2488 | -61.6013 | -61.3907 | 61.0245 | 0.20599 | -0.27466 | 0.17395 | 61.29 | -61.6104 | -0.19226 | -0.022888 | -0.077819 | 0.018311 | -0.24719 | -0.20142 | 0.018311 | 0.11444 | 61.1343 | 61.5829 | 122.4335 | 122.6578 | -0.077819 | 122.699 | 61.615 | -0.20142 | 122.6578 | -0.077819 | 61.615 | 122.4335 | 122.699 | -122.8729 | -122.8821
442.375 | 122.8409 | -61.3907 | 61.3312 | 0.0096895 | 0.0017176 | 0.013958 | 0.024851 | 0.040362 | -0.031917 | 0.059703 | -61.4273 | 61.3403 | -61.5143 | -61.3358 | 61.0565 | 0.25177 | 0.027466 | 0.25635 | 61.4273 | -61.5921 | -0.1236 | 0.009155 | -0.036621 | 0.054932 | -0.27466 | -0.20142 | 0.09613 | 0.086975 | 61.4182 | 61.647 | 122.4472 | 122.731 | -0.036621 | 122.818 | 61.6425 | -0.20142 | 122.731 | -0.036621 | 61.6425 | 122.4472 | 122.818 | -122.8455 | -122.9233
444.1406 | 122.8134 | -61.3861 | 61.3495 | 0.0096895 | 0.0010766 | 0.0096857 | 0.023569 | 0.038866 | -0.029568 | 0.059917 | -61.3907 | 61.322 | -61.4868 | -61.2762 | 61.1114 | 0.30212 | -0.091553 | 0.32044 | 61.3861 | -61.5417 | -0.10071 | -0.027466 | -0.004578 | 0.10986 | -0.23804 | -0.15564 | 0.036621 | 0.09613 | 61.2946 | 61.7065 | 122.4976 | 122.7081 | -0.004578 | 122.7722 | 61.6882 | -0.15564 | 122.7081 | -0.004578 | 61.6882 | 122.4976 | 122.7722 | -122.8363 | -122.8912
445.9062 | 122.9279 | -61.3174 | 61.2991 | 0.00206 | -0.0010596 | 0.0088311 | 0.025705 | 0.038012 | -0.03149 | 0.060344 | -61.4685 | 61.2946 | -61.5143 | -61.3449 | 61.0519 | 0.24261 | -0.1236 | 0.23346 | 61.3541 | -61.5555 | -0.19684 | -0.004577 | -0.15106 | -0.027466 | -0.24719 | -0.23804 | 0.054932 | 0.045776 | 61.1938 | 61.5509 | 122.3694 | 122.612 | -0.15106 | 122.6715 | 61.5601 | -0.23804 | 122.612 | -0.15106 | 61.5601 | 122.3694 | 122.6715 | -122.8134 | -122.8546
447.6719 | 122.9416 | -61.3358 | 61.2762 | 0.00206 | 0.00022218 | 0.011395 | 0.026132 | 0.038439 | -0.032772 | 0.059276 | -61.5005 | 61.235 | -61.5692 | -61.3998 | 60.9924 | 0.17853 | -0.20142 | 0.15564 | 61.322 | -61.5784 | -0.23346 | -0.041199 | -0.16479 | -0.064087 | -0.28381 | -0.24262 | 0.045776 | 0.068665 | 61.1343 | 61.4914 | 122.3282 | 122.5708 | -0.16479 | 122.6578 | 61.5143 | -0.24262 | 122.5708 | -0.16479 | 61.5143 | 122.3282 | 122.6578 | -122.8455 | -122.8546
449.4531 | 122.85 | -61.3724 | 61.2991 | 0.0096895 | 0.0019312 | 0.010113 | 0.027841 | 0.03908 | -0.031704 | 0.057781 | -61.5234 | 61.3449 | -61.5692 | -61.3998 | 60.9787 | 0.18768 | 0.10071 | 0.20142 | 61.4044 | -61.5738 | -0.19684 | 0.045777 | -0.15106 | -0.027466 | -0.32043 | -0.20142 | 0.10529 | 0.045777 | 61.4731 | 61.5738 | 122.3511 | 122.7173 | -0.15106 | 122.7768 | 61.5601 | -0.20142 | 122.7173 | -0.15106 | 61.5601 | 122.3511 | 122.7768 | -122.8683 | -122.8729
451.1719 | 122.8775 | -61.441 | 61.2305 | 0.00206 | 0.00064938 | 0.012463 | 0.027841 | 0.040789 | -0.03384 | 0.059703 | -61.5555 | 61.2671 | -61.6058 | -61.4822 | 60.9009 | 0.09613 | -0.013733 | 0.086975 | 61.3586 | -61.6287 | -0.16479 | 0.036621 | -0.11444 | -0.041199 | -0.32959 | -0.18768 | 0.12817 | 0.050354 | 61.4273 | 61.528 | 122.3419 | 122.7081 | -0.11444 | 122.7997 | 61.5372 | -0.18768 | 122.7081 | -0.11444 | 61.5372 | 122.3419 | 122.7997 | -122.8363 | -122.8592
452.9375 | 122.937 | -61.3358 | 61.29 | 0.00206 | -0.0010596 | 0.013317 | 0.01951 | 0.038226 | -0.030849 | 0.059703 | -61.5005 | 61.2671 | -61.5417 | -61.3678 | 61.0336 | 0.22888 | -0.13733 | 0.21057 | 61.3312 | -61.5646 | -0.20599 | -0.022888 | -0.16479 | -0.032044 | -0.25635 | -0.22888 | 0.041199 | 0.041199 | 61.1984 | 61.5463 | 122.3694 | 122.6028 | -0.16479 | 122.6669 | 61.5646 | -0.22888 | 122.6028 | -0.16479 | 61.5646 | 122.3694 | 122.6669 | -122.8317 | -122.8546
454.6562 | 122.9095 | -61.3358 | 61.2854 | 0.0096895 | 0.001504 | 0.0073359 | 0.023996 | 0.039294 | -0.030849 | 0.056713 | -61.5005 | 61.2579 | -61.528 | -61.3861 | 61.0107 | 0.19226 | -0.13733 | 0.18768 | 61.3312 | -61.5875 | -0.19226 | -0.027465 | -0.16479 | -0.050354 | -0.27466 | -0.25177 | 0.045777 | 0.027466 | 61.1984 | 61.5234 | 122.3465 | 122.5937 | -0.16479 | 122.6669 | 61.528 | -0.25177 | 122.5937 | -0.16479 | 61.528 | 122.3465 | 122.6669 | -122.8134 | -122.8729
456.3594 | 122.9187 | -61.3358 | 61.3037 | 0.0096895 | -0.00041862 | 0.0084039 | 0.023783 | 0.038866 | -0.032131 | 0.059276 | -61.4868 | 61.2671 | -61.5463 | -61.3678 | 61.0107 | 0.22888 | -0.13275 | 0.21515 | 61.3358 | -61.5646 | -0.21057 | -0.036621 | -0.15106 | -0.032044 | -0.29297 | -0.22888 | 0.032043 | 0.05951 | 61.203 | 61.5509 | 122.3465 | 122.6028 | -0.15106 | 122.6715 | 61.5646 | -0.22888 | 122.6028 | -0.15106 | 61.5646 | 122.3465 | 122.6715 | -122.85 | -122.8683
458.125 | 122.8088 | -61.3724 | 61.3174 | -0.0055695 | 0.00064938 | 0.010113 | 0.026773 | 0.039935 | -0.032558 | 0.059062 | -61.3861 | 61.2991 | -61.5143 | -61.2579 | 61.0977 | 0.31128 | -0.1236 | 0.31586 | 61.3495 | -61.5234 | -0.14191 | -0.018311 | -0.013733 | 0.11444 | -0.21973 | -0.15106 | 0.032043 | 0.12817 | 61.2488 | 61.6882 | 122.4701 | 122.6715 | -0.013733 | 122.7219 | 61.6837 | -0.15106 | 122.6715 | -0.013733 | 61.6837 | 122.4701 | 122.7219 | -122.8317 | -122.8409
459.8281 | 122.8088 | -61.3632 | 61.322 | 0.00206 | 0.0019312 | 0.0092585 | 0.027414 | 0.038012 | -0.034267 | 0.059062 | -61.377 | 61.2991 | -61.5143 | -61.2534 | 61.0977 | 0.30212 | -0.11902 | 0.32501 | 61.3632 | -61.5234 | -0.15106 | -0.022888 | -0.013733 | 0.10986 | -0.2243 | -0.16022 | 0.041199 | 0.13733 | 61.2442 | 61.6882 | 122.4609 | 122.6624 | -0.013733 | 122.7264 | 61.6653 | -0.16022 | 122.6624 | -0.013733 | 61.6653 | 122.4609 | 122.7264 | -122.8363 | -122.8455
461.5938 | 122.9141 | -61.3541 | 61.2808 | 0.00206 | 0.00064938 | 0.0077631 | 0.026346 | 0.038226 | -0.031704 | 0.060131 | -61.4685 | 61.2762 | -61.5417 | -61.322 | 61.0474 | 0.2655 | -0.13733 | 0.25177 | 61.3312 | -61.5738 | -0.18768 | -0.004578 | -0.11444 | 0.032044 | -0.23346 | -0.21973 | 0.050354 | 0.073242 | 61.2167 | 61.6058 | 122.4014 | 122.6303 | -0.11444 | 122.6852 | 61.6196 | -0.21973 | 122.6303 | -0.11444 | 61.6196 | 122.4014 | 122.6852 | -122.8226 | -122.8546
463.3125 | 122.8958 | -61.3724 | 61.2213 | 0.0096895 | 0.004281 | 0.012035 | 0.02891 | 0.039507 | -0.033413 | 0.058208 | -61.5509 | 61.235 | -61.6379 | -61.4319 | 60.9238 | 0.12817 | -0.17853 | 0.10529 | 61.3037 | -61.6379 | -0.2655 | 0.013733 | -0.17853 | -0.05951 | -0.29755 | -0.2655 | 0.082398 | 0.086975 | 61.1938 | 61.4777 | 122.2961 | 122.6074 | -0.17853 | 122.6761 | 61.5005 | -0.2655 | 122.6074 | -0.17853 | 61.5005 | 122.2961 | 122.6761 | -122.8592 | -122.8592
465.0938 | 122.7997 | -61.3632 | 61.3037 | 0.0096895 | -0.001914 | 0.0075495 | 0.023783 | 0.038226 | -0.031917 | 0.059917 | -61.3998 | 61.2625 | -61.5463 | -61.2625 | 61.0931 | 0.31128 | -0.15564 | 0.32501 | 61.3495 | -61.5326 | -0.18311 | -0.041199 | -0.036621 | 0.10071 | -0.21057 | -0.16937 | 0.045776 | 0.14648 | 61.2076 | 61.6882 | 122.4564 | 122.6257 | -0.036621 | 122.7127 | 61.6745 | -0.16937 | 122.6257 | -0.036621 | 61.6745 | 122.4564 | 122.7127 | -122.85 | -122.8363
466.7969 | 122.9187 | -61.3953 | 61.2167 | -0.0055695 | 0.0044946 | 0.013531 | 0.028696 | 0.040789 | -0.032985 | 0.059276 | -61.5509 | 61.235 | -61.5875 | -61.4456 | 60.9055 | 0.10529 | -0.16479 | 0.068665 | 61.2808 | -61.6241 | -0.19226 | 0.01831 | -0.15564 | -0.050354 | -0.31128 | -0.22888 | 0.064087 | 0.036621 | 61.2305 | 61.4639 | 122.3007 | 122.6303 | -0.15564 | 122.6761 | 61.5005 | -0.22888 | 122.6303 | -0.15564 | 61.5005 | 122.3007 | 122.6761 | -122.8043 | -122.8409
468.5625 | 122.8317 | -61.3678 | 61.2991 | 0.00206 | 0.0021448 | 0.0096857 | 0.02656 | 0.038653 | -0.031704 | 0.060771 | -61.4594 | 61.3174 | -61.5189 | -61.3403 | 61.0016 | 0.21515 | 0.086975 | 0.22888 | 61.4044 | -61.5784 | -0.15106 | 0.018311 | -0.091553 | 0.027466 | -0.29755 | -0.21057 | 0.10529 | 0.059509 | 61.4548 | 61.5967 | 122.3694 | 122.6852 | -0.091553 | 122.7722 | 61.5829 | -0.21057 | 122.6852 | -0.091553 | 61.5829 | 122.3694 | 122.7722 | -122.818 | -122.8775
470.2812 | 122.8592 | -61.4136 | 61.2946 | 0.0096895 | -0.00041862 | 0.010113 | 0.028482 | 0.038866 | -0.034267 | 0.059276 | -61.4914 | 61.3495 | -61.5555 | -61.3586 | 60.9924 | 0.19684 | 0.1236 | 0.21515 | 61.4044 | -61.5463 | -0.14191 | 0.054931 | -0.07782 | 0.054931 | -0.30212 | -0.13275 | 0.10986 | 0.064087 | 61.5372 | 61.6287 | 122.406 | 122.7631 | -0.07782 | 122.818 | 61.6104 | -0.13275 | 122.7631 | -0.07782 | 61.6104 | 122.406 | 122.818 | -122.85 | -122.8409
472.0469 | 122.905 | -61.3495 | 61.2534 | 0.0096895 | 8.578e-06 | 0.014599 | 0.024851 | 0.038866 | -0.031917 | 0.059062 | -61.4777 | 61.2167 | -61.5829 | -61.3861 | 60.9833 | 0.18768 | -0.23804 | 0.16479 | 61.2808 | -61.5784 | -0.23346 | -0.036621 | -0.12817 | -0.036621 | -0.27008 | -0.22888 | 0.027466 | 0.10529 | 61.1115 | 61.5143 | 122.3328 | 122.5662 | -0.12817 | 122.6303 | 61.5372 | -0.22888 | 122.5662 | -0.12817 | 61.5372 | 122.3328 | 122.6303 | -122.8363 | -122.8317
473.8281 | 122.7905 | -61.3953 | 61.3358 | 0.00206 | 0.0017176 | 0.0096857 | 0.02421 | 0.038439 | -0.033199 | 0.057781 | -61.3998 | 61.2854 | -61.4731 | -61.2671 | 61.0886 | 0.28839 | -0.082397 | 0.32044 | 61.3403 | -61.5097 | -0.077819 | -0.050354 | -0.004577 | 0.12817 | -0.24719 | -0.11444 | 0.004578 | 0.073242 | 61.3129 | 61.7157 | 122.4838 | 122.6807 | -0.004577 | 122.7356 | 61.6837 | -0.11444 | 122.6807 | -0.004577 | 61.6837 | 122.4838 | 122.7356 | -122.8088 | -122.8455
475.625 | 122.9233 | -61.322 | 61.2442 | 0.00206 | 0.0023584 | 0.0088311 | 0.025919 | 0.040575 | -0.032345 | 0.057353 | -61.4868 | 61.2488 | -61.5372 | -61.3815 | 60.9833 | 0.19226 | -0.15564 | 0.16022 | 61.3174 | -61.5875 | -0.21515 | 0.004577 | -0.16479 | -0.05951 | -0.26093 | -0.2655 | 0.073242 | 0.050354 | 61.1664 | 61.4822 | 122.3053 | 122.5708 | -0.16479 | 122.6395 | 61.5143 | -0.2655 | 122.5708 | -0.16479 | 61.5143 | 122.3053 | 122.6395 | -122.7814 | -122.8317
477.4062 | 122.8638 | -61.3724 | 61.235 | 0.00206 | 0.0023584 | 0.013317 | 0.029978 | 0.042071 | -0.033413 | 0.060771 | -61.4639 | 61.2076 | -61.5829 | -61.3724 | 60.9879 | 0.19684 | -0.27924 | 0.16937 | 61.2717 | -61.5921 | -0.21057 | -0.027465 | -0.091553 | 0 | -0.24719 | -0.21973 | 0.036621 | 0.11902 | 61.0931 | 61.5417 | 122.3602 | 122.58 | -0.091553 | 122.644 | 61.5692 | -0.21973 | 122.58 | -0.091553 | 61.5692 | 122.3602 | 122.644 | -122.818 | -122.8271
479.125 | 122.7631 | -61.4456 | 61.2579 | 0.017319 | 0.0023584 | 0.010326 | 0.02955 | 0.041003 | -0.033626 | 0.058422 | -61.4685 | 61.3037 | -61.5784 | -61.3495 | 60.9879 | 0.22888 | -0.009155 | 0.2243 | 61.3632 | -61.5509 | -0.13275 | 0.045776 | -0.022888 | 0.096131 | -0.27008 | -0.10528 | 0.10528 | 0.10986 | 61.4365 | 61.6699 | 122.4335 | 122.7493 | -0.022888 | 122.8088 | 61.6745 | -0.10528 | 122.7493 | -0.022888 | 61.6745 | 122.4335 | 122.8088 | -122.8363 | -122.8088
480.875 | 122.8592 | -61.3998 | 61.2442 | 0.00206 | 0.0010766 | 0.016308 | 0.025278 | 0.041216 | -0.030636 | 0.060985 | -61.4548 | 61.2076 | -61.5738 | -61.3586 | 60.997 | 0.20599 | -0.29297 | 0.16479 | 61.2625 | -61.5784 | -0.17395 | -0.036621 | -0.054932 | 0.041198 | -0.24719 | -0.17853 | 0.01831 | 0.11902 | 61.1069 | 61.5646 | 122.3969 | 122.6074 | -0.054932 | 122.6624 | 61.6058 | -0.17853 | 122.6074 | -0.054932 | 61.6058 | 122.3969 | 122.6624 | -122.818 | -122.8226
482.5938 | 122.8775 | -61.3724 | 61.2671 | 0.00206 | 0.001504 | 0.012463 | 0.023996 | 0.041216 | -0.032558 | 0.05949 | -61.4548 | 61.1847 | -61.5509 | -61.3632 | 60.997 | 0.21057 | -0.27924 | 0.17853 | 61.2808 | -61.5875 | -0.17853 | -0.082398 | -0.082398 | 0.009155 | -0.27008 | -0.21515 | 0.013733 | 0.09613 | 61.0931 | 61.5509 | 122.3694 | 122.5571 | -0.082398 | 122.6532 | 61.5829 | -0.21515 | 122.5571 | -0.082398 | 61.5829 | 122.3694 | 122.6532 | -122.818 | -122.8546
484.3125 | 122.7951 | -61.4136 | 61.2396 | 0.0096895 | -0.00063242 | 0.012463 | 0.028055 | 0.038866 | -0.035549 | 0.060771 | -61.4868 | 61.3312 | -61.5417 | -61.3449 | 60.9924 | 0.20142 | 0.086975 | 0.21515 | 61.409 | -61.5097 | -0.12817 | 0.091553 | -0.073242 | 0.068664 | -0.24719 | -0.096131 | 0.16937 | 0.054932 | 61.5005 | 61.6287 | 122.406 | 122.7448 | -0.073242 | 122.8226 | 61.615 | -0.096131 | 122.7448 | -0.073242 | 61.615 | 122.406 | 122.8226 | -122.7814 | -122.7493
486.0938 | 122.8088 | -61.3541 | 61.322 | 0.00206 | 0.0010766 | 0.0088311 | 0.022287 | 0.042284 | -0.031917 | 0.05949 | -61.3907 | 61.2717 | -61.4868 | -61.2579 | 61.116 | 0.30212 | -0.13733 | 0.31586 | 61.3678 | -61.4731 | -0.13275 | -0.050354 | -0.036621 | 0.09613 | -0.20599 | -0.11902 | 0.045777 | 0.09613 | 61.2167 | 61.6699 | 122.4701 | 122.6257 | -0.036621 | 122.7219 | 61.6562 | -0.11902 | 122.6257 | -0.036621 | 61.6562 | 122.4701 | 122.7219 | -122.8088 | -122.7951
487.8594 | 122.7676 | -61.3403 | 61.2991 | -0.013199 | 0.00043578 | 0.0088311 | 0.024423 | 0.039935 | -0.03149 | 0.058635 | -61.3724 | 61.2625 | -61.4868 | -61.2488 | 61.084 | 0.31586 | -0.13733 | 0.3067 | 61.3541 | -61.528 | -0.14648 | -0.036621 | -0.032043 | 0.091553 | -0.21515 | -0.18768 | 0.054932 | 0.11444 | 61.203 | 61.647 | 122.4243 | 122.6028 | -0.032043 | 122.6944 | 61.6562 | -0.18768 | 122.6028 | -0.032043 | 61.6562 | 122.4243 | 122.6944 | -122.7859 | -122.8271
489.5781 | 122.9141 | -61.3312 | 61.2671 | 0.017319 | 8.578e-06 | 0.013958 | 0.022928 | 0.039721 | -0.029781 | 0.058422 | -61.4914 | 61.235 | -61.528 | -61.3678 | 60.9787 | 0.19226 | -0.16479 | 0.13733 | 61.3037 | -61.6013 | -0.19684 | -0.032044 | -0.16022 | -0.036621 | -0.28839 | -0.27008 | 0.036621 | 0.036621 | 61.1664 | 61.4685 | 122.3099 | 122.5662 | -0.16022 | 122.6349 | 61.5234 | -0.27008 | 122.5662 | -0.16022 | 61.5234 | 122.3099 | 122.6349 | -122.7951 | -122.8683
491.2969 | 122.8271 | -61.3632 | 61.2854 | 0.00206 | 0.001504 | 0.0056269 | 0.029978 | 0.036944 | -0.03149 | 0.059276 | -61.496 | 61.3495 | -61.5143 | -61.3586 | 60.9879 | 0.20142 | 0.14648 | 0.21515 | 61.3998 | -61.5555 | -0.15106 | 0.064087 | -0.13275 | 0.004577 | -0.29755 | -0.19226 | 0.11444 | 0.01831 | 61.5097 | 61.5784 | 122.3511 | 122.7127 | -0.13275 | 122.7631 | 61.5646 | -0.19226 | 122.7127 | -0.13275 | 61.5646 | 122.3511 | 122.7631 | -122.7997 | -122.8409
493.0625 | 122.7631 | -61.4136 | 61.2762 | 0.0096895 | 0.0057764 | 0.010754 | 0.031046 | 0.041216 | -0.033626 | 0.057781 | -61.4365 | 61.2991 | -61.528 | -61.3449 | 60.9741 | 0.21515 | 0 | 0.21973 | 61.3312 | -61.6196 | -0.11444 | 0.022888 | -0.022888 | 0.068664 | -0.30212 | -0.20599 | 0.054932 | 0.091553 | 61.4136 | 61.6333 | 122.3877 | 122.7127 | -0.022888 | 122.7448 | 61.6287 | -0.20599 | 122.7127 | -0.022888 | 61.6287 | 122.3877 | 122.7448 | -122.8043 | -122.8958
494.8594 | 122.8958 | -61.3403 | 61.2671 | -0.0055695 | 0.001504 | 0.012249 | 0.023569 | 0.037798 | -0.030849 | 0.058422 | -61.4639 | 61.2259 | -61.5326 | -61.3815 | 60.9787 | 0.19226 | -0.20599 | 0.16022 | 61.2808 | -61.5784 | -0.19226 | -0.041199 | -0.1236 | -0.041199 | -0.28839 | -0.23804 | 0.013733 | 0.068665 | 61.1343 | 61.5005 | 122.319 | 122.5662 | -0.1236 | 122.6212 | 61.5326 | -0.23804 | 122.5662 | -0.1236 | 61.5326 | 122.319 | 122.6212 | -122.7997 | -122.8455
496.6406 | 122.7905 | -61.4136 | 61.2671 | 0.00206 | 0.002572 | 0.011181 | 0.030618 | 0.039294 | -0.032985 | 0.060985 | -61.4594 | 61.3403 | -61.5555 | -61.3541 | 60.9787 | 0.21515 | 0.045776 | 0.22888 | 61.3678 | -61.5509 | -0.14191 | 0.073242 | -0.045777 | 0.059509 | -0.28839 | -0.13733 | 0.10071 | 0.09613 | 61.4593 | 61.6425 | 122.3923 | 122.7539 | -0.045777 | 122.7814 | 61.6287 | -0.13733 | 122.7539 | -0.045777 | 61.6287 | 122.3923 | 122.7814 | -122.8226 | -122.818
498.3438 | 122.9141 | -61.3266 | 61.2625 | -0.0055695 | 0.0019312 | 0.011822 | 0.023355 | 0.038012 | -0.029354 | 0.057567 | -61.4822 | 61.2305 | -61.5417 | -61.3815 | 60.965 | 0.20142 | -0.17395 | 0.15564 | 61.2946 | -61.5921 | -0.21515 | -0.032043 | -0.15564 | -0.054932 | -0.29755 | -0.2655 | 0.032044 | 0.059509 | 61.1526 | 61.4822 | 122.2916 | 122.5571 | -0.15564 | 122.6212 | 61.528 | -0.2655 | 122.5571 | -0.15564 | 61.528 | 122.2916 | 122.6212 | -122.8043 | -122.8546
500.125 | 122.8912 | -61.377 | 61.1893 | 0.00206 | 0.0036402 | 0.011181 | 0.031259 | 0.039935 | -0.032131 | 0.061626 | -61.5555 | 61.2717 | -61.6058 | -61.4639 | 60.8551 | 0.07782 | -0.064087 | 0.054932 | 61.3174 | -61.6425 | -0.22888 | 0.082397 | -0.17853 | -0.086975 | -0.33417 | -0.2655 | 0.12817 | 0.050354 | 61.3129 | 61.4319 | 122.2321 | 122.6486 | -0.17853 | 122.6944 | 61.4548 | -0.2655 | 122.6486 | -0.17853 | 61.4548 | 122.2321 | 122.6944 | -122.7951 | -122.8317
501.8906 | 122.7448 | -61.3998 | 61.2671 | 0.00206 | 0.00022218 | 0.0084039 | 0.030405 | 0.041644 | -0.031063 | 0.058422 | -61.4777 | 61.3083 | -61.5372 | -61.3449 | 60.9924 | 0.20599 | 0.032043 | 0.23346 | 61.3403 | -61.5189 | -0.13733 | 0.041199 | -0.07782 | 0.054931 | -0.27466 | -0.11902 | 0.073242 | 0.059509 | 61.4319 | 61.6333 | 122.3923 | 122.7081 | -0.07782 | 122.7402 | 61.6058 | -0.11902 | 122.7081 | -0.07782 | 61.6058 | 122.3923 | 122.7402 | -122.8043 | -122.7859
503.6719 | 122.7951 | -61.3678 | 61.2717 | 0.00206 | 0.0032128 | 0.0088311 | 0.027414 | 0.041216 | -0.029995 | 0.059703 | -61.496 | 61.3174 | -61.5372 | -61.3541 | 60.9741 | 0.21515 | 0.10529 | 0.21057 | 61.3632 | -61.5692 | -0.16937 | 0.045777 | -0.12817 | 0.013733 | -0.29755 | -0.20142 | 0.091553 | 0.041198 | 61.4731 | 61.5784 | 122.3419 | 122.6852 | -0.12817 | 122.731 | 61.5829 | -0.20142 | 122.6852 | -0.12817 | 61.5829 | 122.3419 | 122.731 | -122.8088 | -122.8409
505.3906 | 122.8088 | -61.3449 | 61.2762 | 0.0096895 | -0.0017004 | 0.011822 | 0.01951 | 0.039507 | -0.030849 | 0.058422 | -61.3907 | 61.2671 | -61.4868 | -61.2717 | 61.0748 | 0.30212 | -0.13733 | 0.28839 | 61.3449 | -61.5463 | -0.14191 | -0.009155 | -0.045776 | 0.073243 | -0.20142 | -0.20142 | 0.068665 | 0.09613 | 61.2076 | 61.6333 | 122.4197 | 122.612 | -0.045776 | 122.6898 | 61.647 | -0.20142 | 122.612 | -0.045776 | 61.647 | 122.4197 | 122.6898 | -122.7631 | -122.8226
507.1094 | 122.8226 | -61.3724 | 61.2854 | 0.0096895 | 0.0034266 | 0.013104 | 0.026773 | 0.038226 | -0.032558 | 0.057567 | -61.4365 | 61.3449 | -61.5051 | -61.3632 | 60.9879 | 0.21515 | 0.091553 | 0.2243 | 61.377 | -61.5509 | -0.13275 | 0.05951 | -0.064087 | 0.009155 | -0.29755 | -0.17853 | 0.091553 | 0.068665 | 61.4639 | 61.5967 | 122.3602 | 122.7173 | -0.064087 | 122.7493 | 61.5875 | -0.17853 | 122.7173 | -0.064087 | 61.5875 | 122.3602 | 122.7493 | -122.7905 | -122.8363
508.8906 | 122.7722 | -61.3403 | 61.3083 | 0.00206 | -0.00020502 | 0.0079767 | 0.025064 | 0.038866 | -0.030208 | 0.056926 | -61.3907 | 61.2717 | -61.496 | -61.2671 | 61.0748 | 0.3067 | -0.13275 | 0.31128 | 61.3037 | -61.5143 | -0.15564 | -0.036622 | -0.050354 | 0.073242 | -0.23346 | -0.17395 | -0.004578 | 0.10529 | 61.2076 | 61.6516 | 122.4152 | 122.612 | -0.050354 | 122.644 | 61.647 | -0.17395 | 122.612 | -0.050354 | 61.647 | 122.4152 | 122.644 | -122.8043 | -122.8226
510.6875 | 122.8592 | -61.3678 | 61.2213 | -0.020828 | 0.0021448 | 0.0090447 | 0.029978 | 0.039721 | -0.034054 | 0.058849 | -61.5463 | 61.2488 | -61.5829 | -61.4365 | 60.8871 | 0.10529 | -0.15106 | 0.059509 | 61.2717 | -61.6104 | -0.21515 | 0.027466 | -0.17853 | -0.068664 | -0.33417 | -0.24262 | 0.050354 | 0.036621 | 61.2167 | 61.4273 | 122.2549 | 122.6166 | -0.17853 | 122.6395 | 61.4731 | -0.24262 | 122.6166 | -0.17853 | 61.4731 | 122.2549 | 122.6395 | -122.8043 | -122.8317
512.4688 | 122.7585 | -61.3632 | 61.3266 | 0.00206 | 0.002572 | 0.011181 | 0.024423 | 0.038012 | -0.033413 | 0.059062 | -61.3632 | 61.2854 | -61.4777 | -61.235 | 61.0886 | 0.31586 | -0.11444 | 0.31128 | 61.3266 | -61.528 | -0.11444 | -0.041199 | 0 | 0.12817 | -0.23804 | -0.1648 | 0 | 0.11444 | 61.2488 | 61.6745 | 122.4518 | 122.6486 | 0 | 122.6898 | 61.6791 | -0.1648 | 122.6486 | 0 | 61.6791 | 122.4518 | 122.6898 | -122.8043 | -122.8546
514.1719 | 122.7402 | -61.4182 | 61.2442 | 0.00206 | 0.0027856 | 0.011181 | 0.031046 | 0.039935 | -0.032985 | 0.060344 | -61.4594 | 61.2671 | -61.5463 | -61.3403 | 60.9741 | 0.21057 | -0.009155 | 0.2243 | 61.3678 | -61.5509 | -0.12817 | 0.022888 | -0.041199 | 0.07782 | -0.27008 | -0.13275 | 0.1236 | 0.086975 | 61.409 | 61.6425 | 122.3923 | 122.6852 | -0.041199 | 122.7859 | 61.6287 | -0.13275 | 122.6852 | -0.041199 | 61.6287 | 122.3923 | 122.7859 | -122.7905 | -122.7951
515.9375 | 122.7859 | -61.3678 | 61.2488 | -0.0055695 | 0.0062036 | 0.015026 | 0.027628 | 0.041003 | -0.033413 | 0.058849 | -61.4685 | 61.3449 | -61.5005 | -61.3449 | 60.9741 | 0.20599 | 0.10071 | 0.21515 | 61.409 | -61.5463 | -0.13275 | 0.096131 | -0.10071 | 0.022888 | -0.27466 | -0.17853 | 0.16022 | 0.032043 | 61.4685 | 61.5829 | 122.3419 | 122.7127 | -0.10071 | 122.7768 | 61.5738 | -0.17853 | 122.7127 | -0.10071 | 61.5738 | 122.3419 | 122.7768 | -122.7493 | -122.7951
517.6875 | 122.7631 | -61.409 | 61.2579 | -0.0055695 | 0.0032128 | 0.011608 | 0.029123 | 0.039294 | -0.033413 | 0.058849 | -61.4456 | 61.3083 | -61.5189 | -61.3358 | 60.9741 | 0.21057 | 0.050354 | 0.2243 | 61.3815 | -61.5372 | -0.10986 | 0.050354 | -0.036621 | 0.073243 | -0.28381 | -0.12817 | 0.1236 | 0.073242 | 61.4594 | 61.6333 | 122.3831 | 122.7173 | -0.036621 | 122.7905 | 61.6196 | -0.12817 | 122.7173 | -0.036621 | 61.6196 | 122.3831 | 122.7905 | -122.7768 | -122.7951
519.4688 | 122.8775 | -61.3907 | 61.1572 | 0.017319 | 0.0012902 | 0.010754 | 0.027414 | 0.041644 | -0.031917 | 0.059703 | -61.5463 | 61.2625 | -61.5921 | -61.4594 | 60.8734 | 0.10071 | -0.050354 | 0.054932 | 61.3266 | -61.5921 | -0.20142 | 0.10529 | -0.15564 | -0.068665 | -0.28381 | -0.20142 | 0.16937 | 0.045776 | 61.3403 | 61.4456 | 122.2641 | 122.6532 | -0.15564 | 122.7173 | 61.4914 | -0.20142 | 122.6532 | -0.15564 | 61.4914 | 122.2641 | 122.7173 | -122.7493 | -122.7493
521.1875 | 122.7951 | -61.3815 | 61.2488 | 0.0096895 | 0.002572 | 0.0096857 | 0.025278 | 0.038012 | -0.032772 | 0.060344 | -61.441 | 61.3174 | -61.4868 | -61.3495 | 60.9787 | 0.20599 | 0.086975 | 0.21057 | 61.3678 | -61.5372 | -0.10528 | 0.068665 | -0.059509 | 0.032044 | -0.27008 | -0.15564 | 0.11902 | 0.045776 | 61.4685 | 61.5921 | 122.3602 | 122.699 | -0.059509 | 122.7493 | 61.5875 | -0.15564 | 122.699 | -0.059509 | 61.5875 | 122.3602 | 122.7493 | -122.7356 | -122.7859
522.9531 | 122.8638 | -61.3632 | 61.1755 | 0.0096895 | 0.00043578 | 0.0081903 | 0.02656 | 0.04143 | -0.033199 | 0.05949 | -61.5326 | 61.2167 | -61.6013 | -61.4319 | 60.8871 | 0.11902 | -0.16022 | 0.082397 | 61.3083 | -61.5875 | -0.23804 | 0.041199 | -0.16937 | -0.068665 | -0.28839 | -0.2243 | 0.13275 | 0.068664 | 61.203 | 61.4456 | 122.2504 | 122.58 | -0.16937 | 122.6715 | 61.4822 | -0.2243 | 122.58 | -0.16937 | 61.4822 | 122.2504 | 122.6715 | -122.7768 | -122.7631
524.6719 | 122.7997 | -61.3174 | 61.2762 | -0.0055695 | 8.578e-06 | 0.0086175 | 0.021219 | 0.038439 | -0.031063 | 0.058635 | -61.3861 | 61.2534 | -61.4777 | -61.2717 | 61.0474 | 0.30212 | -0.15564 | 0.3067 | 61.3449 | -61.5051 | -0.16022 | -0.022888 | -0.068664 | 0.045777 | -0.22888 | -0.18768 | 0.068665 | 0.091553 | 61.1618 | 61.6241 | 122.3648 | 122.5708 | -0.068664 | 122.6624 | 61.6196 | -0.18768 | 122.5708 | -0.068664 | 61.6196 | 122.3648 | 122.6624 | -122.7539 | -122.7814
526.3906 | 122.8821 | -61.3861 | 61.1801 | 0.017319 | 0.0053492 | 0.014172 | 0.029764 | 0.04143 | -0.032772 | 0.058849 | -61.5326 | 61.2442 | -61.5784 | -61.4594 | 60.8505 | 0.091553 | -0.068665 | 0.064087 | 61.3312 | -61.6013 | -0.19226 | 0.064087 | -0.14648 | -0.073243 | -0.32959 | -0.21515 | 0.15106 | 0.045776 | 61.3174 | 61.4502 | 122.2366 | 122.6303 | -0.14648 | 122.7173 | 61.4777 | -0.21515 | 122.6303 | -0.14648 | 61.4777 | 122.2366 | 122.7173 | -122.7585 | -122.7814
528.1719 | 122.7448 | -61.4182 | 61.2488 | -0.0055695 | 0.00043578 | 0.0088311 | 0.02891 | 0.042284 | -0.035122 | 0.059276 | -61.4502 | 61.2488 | -61.5555 | -61.3724 | 60.9421 | 0.17395 | -0.013733 | 0.16022 | 61.3586 | -61.5463 | -0.13733 | 0 | -0.032043 | 0.045777 | -0.3067 | -0.12817 | 0.10986 | 0.10529 | 61.4044 | 61.5784 | 122.3602 | 122.6669 | -0.032043 | 122.7768 | 61.5921 | -0.12817 | 122.6669 | -0.032043 | 61.5921 | 122.3602 | 122.7768 | -122.8043 | -122.7951
529.9688 | 122.8546 | -61.3678 | 61.1984 | 0.017319 | 0.0066308 | 0.012463 | 0.026773 | 0.039507 | -0.031277 | 0.059703 | -61.5143 | 61.2762 | -61.5646 | -61.4319 | 60.8826 | 0.091553 | -0.09613 | 0.082397 | 61.3083 | -61.615 | -0.19684 | 0.07782 | -0.14648 | -0.064087 | -0.31586 | -0.24719 | 0.10986 | 0.050354 | 61.2717 | 61.4502 | 122.2504 | 122.644 | -0.14648 | 122.6761 | 61.4594 | -0.24719 | 122.644 | -0.14648 | 61.4594 | 122.2504 | 122.6761 | -122.7631 | -122.8134
531.7344 | 122.8592 | -61.3586 | 61.171 | 0.00206 | 0.00022218 | 0.0071221 | 0.026987 | 0.042498 | -0.034054 | 0.05949 | -61.5509 | 61.2534 | -61.5921 | -61.4822 | 60.8459 | 0.073242 | -0.004578 | 0.054932 | 61.3449 | -61.5967 | -0.23346 | 0.082398 | -0.19226 | -0.1236 | -0.32501 | -0.23804 | 0.17395 | 0.041199 | 61.3541 | 61.4136 | 122.2046 | 122.612 | -0.19226 | 122.7036 | 61.4319 | -0.23804 | 122.612 | -0.19226 | 61.4319 | 122.2046 | 122.7036 | -122.7631 | -122.7676
533.4531 | 122.7264 | -61.3861 | 61.2625 | 0.0096895 | 0.0019312 | 0.0081903 | 0.027841 | 0.041003 | -0.03384 | 0.059917 | -61.4548 | 61.2808 | -61.5601 | -61.3403 | 60.9695 | 0.21057 | 0.018311 | 0.23804 | 61.3586 | -61.5417 | -0.17395 | 0.018311 | -0.068665 | 0.045776 | -0.29297 | -0.15564 | 0.096131 | 0.10529 | 61.4044 | 61.6241 | 122.3557 | 122.6669 | -0.068665 | 122.7448 | 61.5967 | -0.15564 | 122.6669 | -0.068665 | 61.5967 | 122.3557 | 122.7448 | -122.8226 | -122.8043
535.1875 | 122.8226 | -61.3449 | 61.235 | 0.0096895 | -0.0029822 | 0.015881 | 0.024423 | 0.04143 | -0.032558 | 0.059703 | -61.4594 | 61.1618 | -61.5601 | -61.3586 | 60.9741 | 0.21515 | -0.29297 | 0.18768 | 61.2671 | -61.5372 | -0.21515 | -0.073242 | -0.11444 | -0.013733 | -0.26093 | -0.19226 | 0.032044 | 0.10071 | 61.0519 | 61.5326 | 122.319 | 122.5067 | -0.11444 | 122.612 | 61.5601 | -0.19226 | 122.5067 | -0.11444 | 61.5601 | 122.319 | 122.612 | -122.7951 | -122.7722
536.9375 | 122.8455 | -61.2762 | 61.2671 | 0.00206 | 0.00086298 | 0.0088311 | 0.019937 | 0.039294 | -0.030636 | 0.060131 | -61.4594 | 61.235 | -61.5143 | -61.3495 | 60.9787 | 0.20142 | -0.15106 | 0.19226 | 61.2991 | -61.5234 | -0.23804 | -0.032044 | -0.18311 | -0.073242 | -0.28839 | -0.24719 | 0.032043 | 0.054931 | 61.1252 | 61.4685 | 122.2549 | 122.5113 | -0.18311 | 122.5754 | 61.4777 | -0.24719 | 122.5113 | -0.18311 | 61.4777 | 122.2549 | 122.5754 | -122.7814 | -122.7905
538.7188 | 122.8546 | -61.3815 | 61.1618 | 0.0096895 | -0.00041862 | 0.013317 | 0.028482 | 0.039507 | -0.035763 | 0.059276 | -61.5555 | 61.2579 | -61.5829 | -61.4685 | 60.8414 | 0.091553 | -0.059509 | 0.068665 | 61.2762 | -61.5921 | -0.20142 | 0.096131 | -0.17395 | -0.086975 | -0.32043 | -0.21057 | 0.11444 | 0.027466 | 61.322 | 61.4502 | 122.2229 | 122.6395 | -0.17395 | 122.6578 | 61.4731 | -0.21057 | 122.6395 | -0.17395 | 61.4731 | 122.2229 | 122.6578 | -122.7448 | -122.7539
540.5 | 122.8683 | -61.2854 | 61.2579 | 0.00206 | 0.0012902 | 0.0084039 | 0.022287 | 0.039935 | -0.031063 | 0.060558 | -61.4639 | 61.235 | -61.5326 | -61.3495 | 60.9741 | 0.20142 | -0.13275 | 0.16937 | 61.3129 | -61.5555 | -0.24719 | -0.022889 | -0.17853 | -0.064087 | -0.28381 | -0.27008 | 0.054931 | 0.068665 | 61.1526 | 61.4548 | 122.2595 | 122.5204 | -0.17853 | 122.5983 | 61.4868 | -0.27008 | 122.5204 | -0.17853 | 61.4868 | 122.2595 | 122.5983 | -122.7905 | -122.8134
542.2188 | 122.7814 | -61.3449 | 61.2808 | 0.00206 | 0.00086298 | 0.010113 | 0.026987 | 0.038866 | -0.031917 | 0.058422 | -61.4456 | 61.3083 | -61.4731 | -61.3312 | 60.9558 | 0.21515 | 0.091553 | 0.22888 | 61.3815 | -61.5463 | -0.12817 | 0.027466 | -0.10071 | 0.013733 | -0.32501 | -0.20142 | 0.10071 | 0.027465 | 61.4365 | 61.5738 | 122.3007 | 122.6532 | -0.10071 | 122.7264 | 61.5601 | -0.20142 | 122.6532 | -0.10071 | 61.5601 | 122.3007 | 122.7264 | -122.7539 | -122.8271
544 | 122.8134 | -61.3861 | 61.1847 | 0.00206 | 0.0017176 | 0.012249 | 0.02955 | 0.041216 | -0.032772 | 0.06184 | -61.5234 | 61.2579 | -61.5601 | -61.441 | 60.8597 | 0.10986 | -0.013733 | 0.082397 | 61.322 | -61.5784 | -0.17395 | 0.073243 | -0.13733 | -0.054932 | -0.32501 | -0.19226 | 0.13733 | 0.036622 | 61.3724 | 61.4685 | 122.2458 | 122.644 | -0.13733 | 122.7081 | 61.496 | -0.19226 | 122.644 | -0.13733 | 61.496 | 122.2458 | 122.7081 | -122.7448 | -122.7631
545.7031 | 122.8409 | -61.3266 | 61.2534 | 0.00206 | 0.00022218 | 0.013744 | 0.024851 | 0.040362 | -0.03149 | 0.059917 | -61.4319 | 61.1938 | -61.5372 | -61.3541 | 60.9604 | 0.18768 | -0.23804 | 0.17395 | 61.2808 | -61.5509 | -0.21057 | -0.059509 | -0.10529 | -0.027466 | -0.29297 | -0.2243 | 0.027466 | 0.10529 | 61.0886 | 61.5005 | 122.287 | 122.5204 | -0.10529 | 122.6074 | 61.5143 | -0.2243 | 122.5204 | -0.10529 | 61.5143 | 122.287 | 122.6074 | -122.7905 | -122.8043
547.4844 | 122.8271 | -61.3632 | 61.1984 | -0.0055695 | 0.0019312 | 0.010113 | 0.029337 | 0.040575 | -0.033626 | 0.05949 | -61.4868 | 61.2213 | -61.5646 | -61.3861 | 60.9055 | 0.15106 | -0.20599 | 0.11902 | 61.2808 | -61.5829 | -0.20142 | 0.022888 | -0.1236 | -0.022888 | -0.29297 | -0.21973 | 0.082398 | 0.07782 | 61.1572 | 61.4822 | 122.2687 | 122.5845 | -0.1236 | 122.644 | 61.5143 | -0.21973 | 122.5845 | -0.1236 | 61.5143 | 122.2687 | 122.644 | -122.7631 | -122.7814
549.2031 | 122.85 | -61.2854 | 61.2762 | 0.0096895 | 0.0021448 | 0.0073359 | 0.021433 | 0.03908 | -0.030636 | 0.061199 | -61.409 | 61.2579 | -61.4685 | -61.2808 | 61.0245 | 0.25177 | -0.12817 | 0.26093 | 61.3541 | -61.5143 | -0.18311 | -0.01831 | -0.1236 | 0.004577 | -0.25177 | -0.22888 | 0.07782 | 0.059509 | 61.1572 | 61.5463 | 122.3099 | 122.5433 | -0.1236 | 122.6395 | 61.5372 | -0.22888 | 122.5433 | -0.1236 | 61.5372 | 122.3099 | 122.6395 | -122.7448 | -122.7905
550.9844 | 122.7676 | -61.3632 | 61.2396 | 0.00206 | 0.0036402 | 0.010113 | 0.028482 | 0.041216 | -0.034054 | 0.059062 | -61.4777 | 61.2991 | -61.5143 | -61.3495 | 60.9558 | 0.1831 | 0.09613 | 0.20142 | 61.3907 | -61.528 | -0.15106 | 0.059509 | -0.11444 | 0.013733 | -0.28381 | -0.1648 | 0.15106 | 0.036621 | 61.4594 | 61.5646 | 122.319 | 122.6624 | -0.11444 | 122.7539 | 61.5463 | -0.1648 | 122.6624 | -0.11444 | 61.5463 | 122.319 | 122.7539 | -122.7539 | -122.7676
552.75 | 122.8409 | -61.3129 | 61.2625 | 0.00206 | 0.00043578 | 0.0094721 | 0.026132 | 0.039294 | -0.030422 | 0.060131 | -61.4456 | 61.203 | -61.5234 | -61.3586 | 60.9512 | 0.17853 | -0.19684 | 0.16022 | 61.2717 | -61.5555 | -0.21057 | -0.059509 | -0.13275 | -0.045777 | -0.31128 | -0.24262 | 0.009155 | 0.077819 | 61.116 | 61.4731 | 122.2641 | 122.5159 | -0.13275 | 122.5845 | 61.4914 | -0.24262 | 122.5159 | -0.13275 | 61.4914 | 122.2641 | 122.5845 | -122.7859 | -122.818
554.5312 | 122.7402 | -61.3953 | 61.2076 | 0.0096895 | 0.0017176 | 0.010754 | 0.031259 | 0.042498 | -0.035122 | 0.059703 | -61.441 | 61.2396 | -61.5234 | -61.3403 | 60.9283 | 0.19226 | -0.018311 | 0.19226 | 61.3403 | -61.5372 | -0.12817 | 0.032043 | -0.045776 | 0.054932 | -0.27924 | -0.14191 | 0.13275 | 0.082397 | 61.377 | 61.5875 | 122.3236 | 122.6349 | -0.045776 | 122.7356 | 61.5875 | -0.14191 | 122.6349 | -0.045776 | 61.5875 | 122.3236 | 122.7356 | -122.731 | -122.7448
556.25 | 122.7676 | -61.3174 | 61.2671 | 0.0096895 | 0.0040674 | 0.013104 | 0.023996 | 0.039294 | -0.032558 | 0.059062 | -61.3724 | 61.29 | -61.4777 | -61.29 | 61.0107 | 0.26093 | 0.032043 | 0.25635 | 61.4044 | -61.5051 | -0.16022 | 0.022888 | -0.054931 | 0.027466 | -0.25635 | -0.18768 | 0.13733 | 0.10529 | 61.3495 | 61.5738 | 122.3282 | 122.6074 | -0.054931 | 122.7219 | 61.5784 | -0.18768 | 122.6074 | -0.054931 | 61.5784 | 122.3282 | 122.7219 | -122.7448 | -122.7722
558.0156 | 122.7585 | -61.3403 | 61.2808 | 0.00206 | 0.0034266 | 0.0081903 | 0.025919 | 0.037798 | -0.031277 | 0.057567 | -61.409 | 61.3174 | -61.4822 | -61.322 | 60.9558 | 0.2243 | 0.073242 | 0.23346 | 61.3815 | -61.5234 | -0.14191 | 0.036621 | -0.068665 | 0.018311 | -0.32501 | -0.18311 | 0.10071 | 0.073242 | 61.4136 | 61.5738 | 122.2961 | 122.6578 | -0.068665 | 122.7219 | 61.5646 | -0.18311 | 122.6578 | -0.068665 | 61.5646 | 122.2961 | 122.7219 | -122.7631 | -122.8043
559.7812 | 122.7997 | -61.3632 | 61.1664 | 0.0096895 | 0.00043578 | 0.010754 | 0.027628 | 0.043566 | -0.035763 | 0.060344 | -61.5097 | 61.1893 | -61.5555 | -61.377 | 60.9009 | 0.14191 | -0.18768 | 0.11444 | 61.2762 | -61.5601 | -0.19226 | 0.022888 | -0.14648 | -0.013733 | -0.2655 | -0.19684 | 0.10986 | 0.045776 | 61.1755 | 61.4777 | 122.2641 | 122.5525 | -0.14648 | 122.6395 | 61.5051 | -0.19684 | 122.5525 | -0.14648 | 61.5051 | 122.2641 | 122.6395 | -122.7219 | -122.7264
561.5 | 122.7127 | -61.3907 | 61.2305 | -0.0055695 | 0.00086298 | 0.012676 | 0.028055 | 0.040362 | -0.033626 | 0.059276 | -61.4639 | 61.2717 | -61.5372 | -61.3358 | 60.9558 | 0.21973 | 0.027466 | 0.23804 | 61.3449 | -61.528 | -0.14648 | 0.041198 | -0.073242 | 0.054932 | -0.27466 | -0.13733 | 0.11444 | 0.073242 | 61.4182 | 61.6287 | 122.3465 | 122.6624 | -0.073242 | 122.7356 | 61.6104 | -0.13733 | 122.6624 | -0.073242 | 61.6104 | 122.3465 | 122.7356 | -122.7676 | -122.7585
563.2656 | 122.7127 | -61.3266 | 61.3174 | 0.0096895 | 8.578e-06 | 0.0094721 | 0.02421 | 0.040789 | -0.032772 | 0.060344 | -61.322 | 61.2808 | -61.4777 | -61.2259 | 61.0703 | 0.31586 | -0.10071 | 0.32959 | 61.3129 | -61.4685 | -0.15106 | -0.036621 | 0.004578 | 0.10071 | -0.24719 | -0.14191 | -0.004578 | 0.15564 | 61.2259 | 61.6562 | 122.3969 | 122.6074 | 0.004578 | 122.6395 | 61.6425 | -0.14191 | 122.6074 | 0.004578 | 61.6425 | 122.3969 | 122.6395 | -122.7951 | -122.7859
565.0312 | 122.8409 | -61.2991 | 61.2488 | 0.00206 | 0.00022218 | 0.013317 | 0.024423 | 0.038226 | -0.032131 | 0.058849 | -61.4639 | 61.2488 | -61.5097 | -61.3541 | 60.9467 | 0.19226 | -0.15564 | 0.1831 | 61.2991 | -61.5234 | -0.21057 | 0 | -0.1648 | -0.054932 | -0.30212 | -0.2243 | 0.050354 | 0.045777 | 61.1435 | 61.4822 | 122.2458 | 122.5479 | -0.1648 | 122.5983 | 61.4914 | -0.2243 | 122.5479 | -0.1648 | 61.4914 | 122.2458 | 122.5983 | -122.7585 | -122.7722
566.7969 | 122.8363 | -61.2991 | 61.2305 | 0.00206 | 0.0019312 | 0.012035 | 0.025064 | 0.039721 | -0.032345 | 0.057994 | -61.4456 | 61.2076 | -61.528 | -61.3586 | 60.9375 | 0.18768 | -0.19226 | 0.15564 | 61.2717 | -61.5463 | -0.22888 | -0.022888 | -0.14649 | -0.05951 | -0.29297 | -0.24719 | 0.041198 | 0.082397 | 61.1069 | 61.4548 | 122.2366 | 122.5067 | -0.14649 | 122.5708 | 61.4868 | -0.24719 | 122.5067 | -0.14649 | 61.4868 | 122.2366 | 122.5708 | -122.7585 | -122.7768
568.5156 | 122.731 | -61.3495 | 61.2122 | 0.0096895 | 0.0029992 | 0.010754 | 0.029764 | 0.040789 | -0.034908 | 0.05714 | -61.4548 | 61.2717 | -61.5097 | -61.3266 | 60.9512 | 0.21057 | 0.091553 | 0.2243 | 61.3907 | -61.5005 | -0.16022 | 0.059509 | -0.10529 | 0.022888 | -0.26093 | -0.15106 | 0.17853 | 0.054932 | 61.441 | 61.5738 | 122.3007 | 122.6212 | -0.10529 | 122.7402 | 61.5601 | -0.15106 | 122.6212 | -0.10529 | 61.5601 | 122.3007 | 122.7402 | -122.7219 | -122.7127
570.2344 | 122.85 | -61.3174 | 61.2213 | -0.0055695 | 0.00086298 | 0.0096857 | 0.025064 | 0.039935 | -0.02914 | 0.060344 | -61.4548 | 61.2167 | -61.5051 | -61.3449 | 60.9421 | 0.18768 | -0.16022 | 0.15564 | 61.2808 | -61.5417 | -0.18768 | -0.004577 | -0.13733 | -0.027466 | -0.27923 | -0.2243 | 0.05951 | 0.050354 | 61.1572 | 61.4731 | 122.2595 | 122.5342 | -0.13733 | 122.5983 | 61.5051 | -0.2243 | 122.5342 | -0.13733 | 61.5051 | 122.2595 | 122.5983 | -122.7264 | -122.7631
572 | 122.6898 | -61.377 | 61.2122 | 0.017319 | 0.0036402 | 0.012035 | 0.030191 | 0.038439 | -0.034481 | 0.060985 | -61.4227 | 61.2442 | -61.5463 | -61.322 | 60.9467 | 0.21057 | -0.004578 | 0.22888 | 61.322 | -61.5372 | -0.16937 | 0.032044 | -0.045776 | 0.054932 | -0.2655 | -0.16022 | 0.10986 | 0.1236 | 61.3724 | 61.6058 | 122.3236 | 122.6212 | -0.045776 | 122.699 | 61.5875 | -0.16022 | 122.6212 | -0.045776 | 61.5875 | 122.3236 | 122.699 | -122.7585 | -122.7493
573.7188 | 122.7402 | -61.3449 | 61.2534 | 0.00206 | -0.00084602 | 0.0086175 | 0.026773 | 0.037798 | -0.031704 | 0.059917 | -61.3998 | 61.2808 | -61.4868 | -61.3174 | 60.9787 | 0.23346 | 0.073242 | 0.24261 | 61.377 | -61.496 | -0.14191 | 0.027466 | -0.054931 | 0.027466 | -0.27466 | -0.15106 | 0.1236 | 0.086975 | 61.4182 | 61.5875 | 122.3236 | 122.6257 | -0.054931 | 122.7219 | 61.5784 | -0.15106 | 122.6257 | -0.054931 | 61.5784 | 122.3236 | 122.7219 | -122.7402 | -122.7493
575.5 | 122.7493 | -61.3449 | 61.2534 | 0.00206 | 0.00022218 | 0.01524 | 0.027414 | 0.037585 | -0.032558 | 0.059062 | -61.4548 | 61.3083 | -61.5005 | -61.3403 | 60.9421 | 0.23346 | 0.14191 | 0.21973 | 61.3907 | -61.5189 | -0.15564 | 0.054932 | -0.10986 | 0.004578 | -0.31128 | -0.17395 | 0.13733 | 0.045776 | 61.4868 | 61.5646 | 122.287 | 122.6532 | -0.10986 | 122.7356 | 61.5784 | -0.17395 | 122.6532 | -0.10986 | 61.5784 | 122.287 | 122.7356 | -122.7539 | -122.7722
577.2031 | 122.7127 | -61.3358 | 61.2671 | 0.00206 | 0.0010766 | 0.010326 | 0.022501 | 0.03908 | -0.033199 | 0.059703 | -61.3495 | 61.2625 | -61.4456 | -61.2442 | 61.0382 | 0.31128 | -0.054932 | 0.32044 | 61.3174 | -61.4868 | -0.10986 | -0.004578 | -0.013733 | 0.091552 | -0.22888 | -0.15106 | 0.050354 | 0.096131 | 61.2808 | 61.6562 | 122.374 | 122.5983 | -0.013733 | 122.6532 | 61.647 | -0.15106 | 122.5983 | -0.013733 | 61.647 | 122.374 | 122.6532 | -122.7127 | -122.7539
578.9688 | 122.8455 | -61.3037 | 61.235 | 0.017319 | 0.00043578 | 0.0081903 | 0.023783 | 0.038012 | -0.030849 | 0.056713 | -61.4594 | 61.2167 | -61.5005 | -61.3449 | 60.9421 | 0.20142 | -0.17395 | 0.15564 | 61.2625 | -61.5601 | -0.19684 | -0.01831 | -0.15564 | -0.041199 | -0.29297 | -0.25635 | 0.027466 | 0.041198 | 61.1298 | 61.4594 | 122.2458 | 122.5204 | -0.15564 | 122.5662 | 61.5051 | -0.25635 | 122.5204 | -0.15564 | 61.5051 | 122.2458 | 122.5662 | -122.7356 | -122.7951
580.75 | 122.8134 | -61.2808 | 61.2488 | 0.00206 | 0.0019312 | 0.010967 | 0.023355 | 0.03673 | -0.03149 | 0.058635 | -61.4044 | 61.2579 | -61.4822 | -61.2671 | 61.0199 | 0.27008 | -0.1236 | 0.24719 | 61.3037 | -61.5097 | -0.20142 | 0.009156 | -0.1236 | 0.013733 | -0.22888 | -0.22888 | 0.054932 | 0.07782 | 61.1572 | 61.528 | 122.3007 | 122.5388 | -0.1236 | 122.5845 | 61.5509 | -0.22888 | 122.5388 | -0.1236 | 61.5509 | 122.3007 | 122.5845 | -122.731 | -122.7585
582.5312 | 122.8409 | -61.29 | 61.2167 | 0.0096895 | -0.00041862 | 0.0094721 | 0.027414 | 0.039294 | -0.029781 | 0.05714 | -61.4365 | 61.2259 | -61.5097 | -61.3403 | 60.9421 | 0.19226 | -0.15106 | 0.15106 | 61.2762 | -61.5372 | -0.21973 | 0.009155 | -0.14648 | -0.050354 | -0.27466 | -0.24719 | 0.059509 | 0.073243 | 61.1389 | 61.441 | 122.2321 | 122.5159 | -0.14648 | 122.5662 | 61.4822 | -0.24719 | 122.5159 | -0.14648 | 61.4822 | 122.2321 | 122.5662 | -122.7264 | -122.7539
584.25 | 122.7036 | -61.3953 | 61.2213 | 0.00206 | 0.001504 | 0.012035 | 0.030832 | 0.04143 | -0.03384 | 0.059276 | -61.409 | 61.2671 | -61.5143 | -61.2946 | 60.9467 | 0.23346 | 0.032043 | 0.23346 | 61.3449 | -61.5097 | -0.11902 | 0.045777 | -0.013733 | 0.10071 | -0.27466 | -0.11444 | 0.1236 | 0.10529 | 61.4273 | 61.6287 | 122.3419 | 122.6624 | -0.013733 | 122.7402 | 61.6287 | -0.11444 | 122.6624 | -0.013733 | 61.6287 | 122.3419 | 122.7402 | -122.7356 | -122.731
586.0156 | 122.6898 | -61.3266 | 61.2808 | 0.00206 | 0.00086298 | 0.0077631 | 0.025492 | 0.038012 | -0.032345 | 0.058208 | -61.3495 | 61.2808 | -61.4731 | -61.2167 | 61.0428 | 0.30212 | -0.10071 | 0.32959 | 61.3358 | -61.5005 | -0.14648 | 0 | -0.022888 | 0.10986 | -0.23804 | -0.17395 | 0.054931 | 0.1236 | 61.2259 | 61.6562 | 122.3694 | 122.6074 | -0.022888 | 122.6624 | 61.6287 | -0.17395 | 122.6074 | -0.022888 | 61.6287 | 122.3694 | 122.6624 | -122.7539 | -122.7814
587.7812 | 122.8043 | -61.3403 | 61.171 | 0.00206 | 0.002572 | 0.010967 | 0.032114 | 0.04143 | -0.035122 | 0.060344 | -61.528 | 61.2213 | -61.5601 | -61.441 | 60.8322 | 0.10071 | -0.050354 | 0.07782 | 61.3174 | -61.5601 | -0.21973 | 0.050354 | -0.18768 | -0.10071 | -0.33875 | -0.21973 | 0.14648 | 0.032044 | 61.29 | 61.4182 | 122.1725 | 122.5616 | -0.18768 | 122.6578 | 61.441 | -0.21973 | 122.5616 | -0.18768 | 61.441 | 122.1725 | 122.6578 | -122.731 | -122.731
589.5 | 122.818 | -61.2946 | 61.2167 | 0.00206 | 0.002572 | 0.0069085 | 0.024851 | 0.041003 | -0.031704 | 0.059703 | -61.4273 | 61.1618 | -61.5189 | -61.3358 | 60.9421 | 0.19684 | -0.19226 | 0.16479 | 61.2579 | -61.528 | -0.2243 | -0.054932 | -0.13275 | -0.041198 | -0.27466 | -0.23346 | 0.041199 | 0.091553 | 61.1023 | 61.4594 | 122.2366 | 122.4564 | -0.13275 | 122.5525 | 61.4914 | -0.23346 | 122.4564 | -0.13275 | 61.4914 | 122.2366 | 122.5525 | -122.7356 | -122.7448
591.2188 | 122.7905 | -61.3358 | 61.1572 | 0.0096895 | 0.002572 | 0.013104 | 0.029123 | 0.040789 | -0.035335 | 0.060771 | -61.5051 | 61.2305 | -61.5738 | -61.4044 | 60.8643 | 0.11902 | -0.15106 | 0.082397 | 61.2717 | -61.5509 | -0.23804 | 0.073242 | -0.16937 | -0.068665 | -0.29297 | -0.21515 | 0.11444 | 0.068665 | 61.1847 | 61.4182 | 122.2 | 122.5662 | -0.16937 | 122.6074 | 61.4548 | -0.21515 | 122.5662 | -0.16937 | 61.4548 | 122.2 | 122.6074 | -122.731 | -122.7081
593 | 122.731 | -61.3266 | 61.2076 | 0.00206 | 0.00064938 | 0.010754 | 0.02955 | 0.040789 | -0.034481 | 0.059062 | -61.441 | 61.2991 | -61.5051 | -61.3312 | 60.9375 | 0.1831 | 0.091553 | 0.21057 | 61.3586 | -61.5189 | -0.17853 | 0.091552 | -0.11444 | -0.004578 | -0.27008 | -0.19226 | 0.15106 | 0.064087 | 61.4182 | 61.5372 | 122.2641 | 122.6257 | -0.11444 | 122.6852 | 61.5097 | -0.19226 | 122.6257 | -0.11444 | 61.5097 | 122.2641 | 122.6852 | -122.7127 | -122.7264
594.7656 | 122.818 | -61.2625 | 61.2259 | 0.017319 | 0.0021448 | 0.0086175 | 0.025492 | 0.038653 | -0.029995 | 0.059703 | -61.441 | 61.2076 | -61.4822 | -61.322 | 60.9604 | 0.20142 | -0.14648 | 0.18768 | 61.29 | -61.5143 | -0.21973 | -0.01831 | -0.17853 | -0.059509 | -0.2655 | -0.25177 | 0.064087 | 0.041199 | 61.116 | 61.4502 | 122.2229 | 122.4701 | -0.17853 | 122.5525 | 61.4639 | -0.25177 | 122.4701 | -0.17853 | 61.4639 | 122.2229 | 122.5525 | -122.7081 | -122.7402
596.5625 | 122.7127 | -61.3678 | 61.1893 | 0.00206 | 0.0040674 | 0.012035 | 0.032755 | 0.038439 | -0.034481 | 0.059917 | -61.4731 | 61.2213 | -61.5601 | -61.3815 | 60.8734 | 0.14191 | -0.032043 | 0.1236 | 61.2762 | -61.5555 | -0.19226 | 0.032043 | -0.10529 | -0.013733 | -0.31586 | -0.18768 | 0.086975 | 0.086976 | 61.3358 | 61.4914 | 122.2412 | 122.5891 | -0.10529 | 122.644 | 61.5097 | -0.18768 | 122.5891 | -0.10529 | 61.5097 | 122.2412 | 122.644 | -122.7493 | -122.7448
598.2812 | 122.7997 | -61.2671 | 61.2396 | -0.0055695 | 0.0019312 | 0.0090447 | 0.022501 | 0.038653 | -0.029995 | 0.059917 | -61.4319 | 61.1801 | -61.5051 | -61.3358 | 60.9421 | 0.20599 | -0.18768 | 0.16022 | 61.2396 | -61.5509 | -0.23804 | -0.059509 | -0.16479 | -0.068664 | -0.29755 | -0.28381 | 0 | 0.073242 | 61.0794 | 61.4273 | 122.2092 | 122.4472 | -0.16479 | 122.5067 | 61.4731 | -0.28381 | 122.4472 | -0.16479 | 61.4731 | 122.2092 | 122.5067 | -122.7448 | -122.7905
600.0469 | 122.7219 | -61.3449 | 61.2122 | 0.00206 | 0.0021448 | 0.011395 | 0.031473 | 0.037371 | -0.032345 | 0.059917 | -61.4456 | 61.3037 | -61.496 | -61.3403 | 60.9283 | 0.20142 | 0.10071 | 0.21515 | 61.3312 | -61.5189 | -0.15106 | 0.091553 | -0.10071 | 0.004578 | -0.28381 | -0.17395 | 0.11902 | 0.050354 | 61.4456 | 61.5601 | 122.2733 | 122.6486 | -0.10071 | 122.6761 | 61.5463 | -0.17395 | 122.6486 | -0.10071 | 61.5463 | 122.2733 | 122.6761 | -122.7081 | -122.731
601.8281 | 122.7173 | -61.3815 | 61.1893 | 0.00206 | 0.0021448 | 0.0094721 | 0.029978 | 0.039935 | -0.034908 | 0.059276 | -61.4502 | 61.2396 | -61.5234 | -61.3678 | 60.8688 | 0.14648 | -0.027466 | 0.13733 | 61.2991 | -61.528 | -0.14191 | 0.050354 | -0.068664 | 0.013733 | -0.32044 | -0.14648 | 0.10986 | 0.073242 | 61.3541 | 61.5189 | 122.2504 | 122.6212 | -0.068664 | 122.6807 | 61.528 | -0.14648 | 122.6212 | -0.068664 | 61.528 | 122.2504 | 122.6807 | -122.7127 | -122.7173
603.6094 | 122.7493 | -61.3083 | 61.2442 | -0.0055695 | 0.0019312 | 0.0086175 | 0.021646 | 0.038012 | -0.031063 | 0.059062 | -61.3632 | 61.2442 | -61.4456 | -61.2396 | 61.0291 | 0.3067 | -0.13733 | 0.28839 | 61.2671 | -61.4868 | -0.13733 | 0 | -0.054931 | 0.068665 | -0.21515 | -0.17853 | 0.022888 | 0.082398 | 61.171 | 61.5967 | 122.3373 | 122.5525 | -0.054931 | 122.5754 | 61.615 | -0.17853 | 122.5525 | -0.054931 | 61.615 | 122.3373 | 122.5754 | -122.6898 | -122.731
605.3281 | 122.6715 | -61.3724 | 61.2259 | -0.0055695 | 0.002572 | 0.011395 | 0.030618 | 0.038653 | -0.032131 | 0.058422 | -61.4227 | 61.2305 | -61.5143 | -61.3129 | 60.9375 | 0.22888 | -0.004578 | 0.21973 | 61.3174 | -61.528 | -0.14191 | 0.004578 | -0.050354 | 0.059509 | -0.28839 | -0.15564 | 0.091553 | 0.091553 | 61.3678 | 61.5921 | 122.3099 | 122.6028 | -0.050354 | 122.6898 | 61.6013 | -0.15564 | 122.6028 | -0.050354 | 61.6013 | 122.3099 | 122.6898 | -122.7402 | -122.7539
607.0938 | 122.7173 | -61.3266 | 61.2579 | 0.0096895 | 0.004281 | 0.0090447 | 0.02421 | 0.038439 | -0.030636 | 0.058422 | -61.3724 | 61.2854 | -61.4685 | -61.2671 | 60.9833 | 0.27008 | 0.050354 | 0.2655 | 61.3632 | -61.5097 | -0.14191 | 0.027465 | -0.045776 | 0.059509 | -0.27466 | -0.18311 | 0.10528 | 0.096131 | 61.377 | 61.5921 | 122.3099 | 122.612 | -0.045776 | 122.6898 | 61.5967 | -0.18311 | 122.612 | -0.045776 | 61.5967 | 122.3099 | 122.6898 | -122.7264 | -122.7676
608.8594 | 122.6761 | -61.2946 | 61.2762 | 0.0096895 | 0.00043578 | 0.01054 | 0.024637 | 0.038653 | -0.030422 | 0.057567 | -61.3358 | 61.2534 | -61.4273 | -61.2122 | 61.0519 | 0.33417 | -0.10529 | 0.32044 | 61.29 | -61.496 | -0.13275 | -0.022888 | -0.041198 | 0.082398 | -0.2243 | -0.20142 | 0.013733 | 0.091553 | 61.1893 | 61.615 | 122.3465 | 122.5479 | -0.041198 | 122.5845 | 61.6287 | -0.20142 | 122.5479 | -0.041198 | 61.6287 | 122.3465 | 122.5845 | -122.7036 | -122.7722
610.6562 | 122.8043 | -61.2808 | 61.2259 | 0.00206 | -0.00063242 | 0.011822 | 0.023355 | 0.037157 | -0.031063 | 0.057353 | -61.4227 | 61.235 | -61.4822 | -61.3083 | 60.9558 | 0.22888 | -0.14191 | 0.21973 | 61.2808 | -61.528 | -0.20142 | 0.009155 | -0.14191 | -0.027466 | -0.27008 | -0.24719 | 0.054932 | 0.05951 | 61.1389 | 61.5005 | 122.2366 | 122.5159 | -0.14191 | 122.5616 | 61.5097 | -0.24719 | 122.5159 | -0.14191 | 61.5097 | 122.2366 | 122.5616 | -122.7081 | -122.7539
612.375 | 122.7264 | -61.3495 | 61.2259 | 0.00206 | 0.00064938 | 0.0081903 | 0.028482 | 0.040362 | -0.034054 | 0.060771 | -61.4365 | 61.2717 | -61.5143 | -61.322 | 60.9329 | 0.21973 | 0.11902 | 0.22888 | 61.3449 | -61.4822 | -0.16479 | 0.045776 | -0.086975 | 0.027466 | -0.29297 | -0.13275 | 0.11902 | 0.07782 | 61.4685 | 61.5784 | 122.2824 | 122.6212 | -0.086975 | 122.6944 | 61.5692 | -0.13275 | 122.6212 | -0.086975 | 61.5692 | 122.2824 | 122.6944 | -122.7402 | -122.7081
614.1562 | 122.7219 | -61.3129 | 61.2396 | 0.00206 | 0.0023584 | 0.0098993 | 0.025064 | 0.039294 | -0.034267 | 0.059062 | -61.3998 | 61.2671 | -61.4456 | -61.3174 | 60.9375 | 0.23346 | 0.10071 | 0.2243 | 61.3724 | -61.4914 | -0.13275 | 0.027466 | -0.086975 | -0.004578 | -0.30212 | -0.17853 | 0.13275 | 0.045777 | 61.4136 | 61.5372 | 122.2504 | 122.58 | -0.086975 | 122.6852 | 61.5463 | -0.17853 | 122.58 | -0.086975 | 61.5463 | 122.2504 | 122.6852 | -122.6852 | -122.731
615.9531 | 122.699 | -61.3129 | 61.2625 | 0.00206 | -0.00041862 | 0.010326 | 0.023783 | 0.039294 | -0.032345 | 0.060344 | -61.3724 | 61.2305 | -61.4731 | -61.2625 | 60.9833 | 0.27008 | 0.036621 | 0.27466 | 61.3358 | -61.4685 | -0.16022 | -0.032043 | -0.059509 | 0.050354 | -0.27924 | -0.15564 | 0.073242 | 0.10071 | 61.3495 | 61.5875 | 122.2961 | 122.5433 | -0.059509 | 122.6486 | 61.5829 | -0.15564 | 122.5433 | -0.059509 | 61.5829 | 122.2961 | 122.6486 | -122.7356 | -122.731
617.7344 | 122.7173 | -61.2946 | 61.29 | 0.00206 | 0.001504 | 0.01054 | 0.027414 | 0.038439 | -0.03149 | 0.05949 | -61.3403 | 61.2579 | -61.4594 | -61.2625 | 60.9833 | 0.27924 | 0.027466 | 0.28839 | 61.3403 | -61.4914 | -0.16479 | -0.032043 | -0.045776 | 0.032044 | -0.3067 | -0.19684 | 0.050354 | 0.11902 | 61.322 | 61.5829 | 122.2778 | 122.5525 | -0.045776 | 122.6349 | 61.5738 | -0.19684 | 122.5525 | -0.045776 | 61.5738 | 122.2778 | 122.6349 | -122.7493 | -122.7814
619.5 | 122.7448 | -61.3495 | 61.1618 | -0.0055695 | -0.0017004 | 0.014172 | 0.031046 | 0.039294 | -0.03384 | 0.060131 | -61.4914 | 61.1984 | -61.5692 | -61.3861 | 60.8459 | 0.10529 | -0.018311 | 0.09613 | 61.2946 | -61.5189 | -0.21973 | 0.036621 | -0.14191 | -0.036621 | -0.31586 | -0.16937 | 0.13275 | 0.07782 | 61.3312 | 61.4456 | 122.1954 | 122.5479 | -0.14191 | 122.644 | 61.4548 | -0.16937 | 122.5479 | -0.14191 | 61.4548 | 122.1954 | 122.644 | -122.731 | -122.6807
621.2812 | 122.6532 | -61.3541 | 61.1893 | 0.0096895 | 0.00599 | 0.012249 | 0.02891 | 0.040575 | -0.034267 | 0.057567 | -61.4136 | 61.2717 | -61.4868 | -61.3129 | 60.9467 | 0.21973 | 0.045776 | 0.22888 | 61.3358 | -61.496 | -0.13275 | 0.082397 | -0.059509 | 0.041199 | -0.24262 | -0.14191 | 0.14648 | 0.073242 | 61.3998 | 61.5829 | 122.3007 | 122.6257 | -0.059509 | 122.6898 | 61.5738 | -0.14191 | 122.6257 | -0.059509 | 61.5738 | 122.3007 | 122.6898 | -122.6761 | -122.6852
622.9844 | 122.6807 | -61.377 | 61.1938 | -0.0055695 | 0.0040674 | 0.012676 | 0.02891 | 0.03908 | -0.031704 | 0.057781 | -61.3953 | 61.2717 | -61.4868 | -61.2854 | 60.9192 | 0.20599 | -0.013733 | 0.21057 | 61.2808 | -61.5417 | -0.10986 | 0.077819 | -0.018311 | 0.091553 | -0.27466 | -0.16479 | 0.086975 | 0.091552 | 61.3632 | 61.5875 | 122.2961 | 122.6486 | -0.018311 | 122.6578 | 61.5829 | -0.16479 | 122.6486 | -0.018311 | 61.5829 | 122.2961 | 122.6578 | -122.6807 | -122.7356
624.75 | 122.7173 | -61.3129 | 61.2625 | 0.00206 | 0.0021448 | 0.0075495 | 0.022928 | 0.040362 | -0.032772 | 0.059062 | -61.3724 | 61.29 | -61.4502 | -61.2808 | 60.9695 | 0.24719 | 0.068665 | 0.24261 | 61.3312 | -61.5143 | -0.13733 | 0.027466 | -0.059509 | 0.032043 | -0.29297 | -0.20142 | 0.068665 | 0.07782 | 61.3815 | 61.5555 | 122.2824 | 122.6028 | -0.059509 | 122.644 | 61.5601 | -0.20142 | 122.6028 | -0.059509 | 61.5601 | 122.2824 | 122.644 | -122.7127 | -122.7768
626.4531 | 122.7264 | -61.3586 | 61.1618 | 0.0096895 | 0.0027856 | 0.011181 | 0.029123 | 0.04143 | -0.032772 | 0.060131 | -61.4777 | 61.2167 | -61.5509 | -61.3953 | 60.8459 | 0.12817 | -0.018311 | 0.10529 | 61.2991 | -61.5372 | -0.19226 | 0.054932 | -0.11902 | -0.036621 | -0.31586 | -0.17853 | 0.13733 | 0.073242 | 61.3403 | 61.4639 | 122.2046 | 122.5754 | -0.11902 | 122.6578 | 61.4868 | -0.17853 | 122.5754 | -0.11902 | 61.4868 | 122.2046 | 122.6578 | -122.7127 | -122.699
628.1562 | 122.7036 | -61.2991 | 61.2488 | 0.0096895 | 0.004281 | 0.010113 | 0.025064 | 0.038866 | -0.030636 | 0.059917 | -61.377 | 61.2488 | -61.4365 | -61.2854 | 60.9558 | 0.22888 | 0.091553 | 0.25635 | 61.3449 | -61.4914 | -0.13733 | 0 | -0.07782 | 0.013733 | -0.29297 | -0.19226 | 0.096131 | 0.059509 | 61.3907 | 61.5555 | 122.2549 | 122.5479 | -0.07782 | 122.644 | 61.528 | -0.19226 | 122.5479 | -0.07782 | 61.528 | 122.2549 | 122.644 | -122.6852 | -122.7402
629.9531 | 122.7631 | -61.3403 | 61.1664 | -0.0055695 | 0.00043578 | 0.0081903 | 0.027628 | 0.040789 | -0.03384 | 0.060344 | -61.5051 | 61.1618 | -61.5601 | -61.3541 | 60.8826 | 0.16022 | -0.19226 | 0.11902 | 61.2625 | -61.5143 | -0.21973 | -0.004578 | -0.1648 | -0.013733 | -0.28381 | -0.17395 | 0.09613 | 0.054932 | 61.1481 | 61.4594 | 122.2229 | 122.5021 | -0.1648 | 122.6028 | 61.5005 | -0.17395 | 122.5021 | -0.1648 | 61.5005 | 122.2229 | 122.6028 | -122.7264 | -122.6807
631.7344 | 122.7356 | -61.2808 | 61.2488 | 0.0096895 | 0.002572 | 0.012676 | 0.023355 | 0.038439 | -0.032772 | 0.05949 | -61.3449 | 61.2122 | -61.409 | -61.2442 | 61.0153 | 0.3067 | -0.14191 | 0.28839 | 61.29 | -61.496 | -0.12817 | -0.036621 | -0.064087 | 0.036621 | -0.23346 | -0.21515 | 0.041199 | 0.064087 | 61.1389 | 61.5692 | 122.2961 | 122.493 | -0.064087 | 122.5708 | 61.5875 | -0.21515 | 122.493 | -0.064087 | 61.5875 | 122.2961 | 122.5708 | -122.6578 | -122.7448
633.4375 | 122.6624 | -61.377 | 61.2122 | 0.0096895 | 0.00086298 | 0.013317 | 0.028482 | 0.040575 | -0.035335 | 0.059917 | -61.4044 | 61.2396 | -61.5143 | -61.3037 | 60.9192 | 0.22888 | 0.004578 | 0.22888 | 61.3358 | -61.5143 | -0.13733 | 0.027466 | -0.027466 | 0.073242 | -0.29297 | -0.13733 | 0.1236 | 0.10986 | 61.3815 | 61.6058 | 122.2961 | 122.6166 | -0.027466 | 122.7127 | 61.6058 | -0.13733 | 122.6166 | -0.027466 | 61.6058 | 122.2961 | 122.7127 | -122.7264 | -122.7264
635.1406 | 122.6669 | -61.3632 | 61.1984 | 0.017319 | 0.0019312 | 0.0094721 | 0.028055 | 0.041857 | -0.035122 | 0.058635 | -61.4044 | 61.2534 | -61.5051 | -61.29 | 60.9283 | 0.22888 | 0.032043 | 0.23346 | 61.3083 | -61.5234 | -0.14191 | 0.054932 | -0.041199 | 0.073242 | -0.27008 | -0.16022 | 0.10986 | 0.10071 | 61.3953 | 61.5967 | 122.2916 | 122.6166 | -0.041199 | 122.6715 | 61.5921 | -0.16022 | 122.6166 | -0.041199 | 61.5921 | 122.2916 | 122.6715 | -122.7036 | -122.7219
636.9062 | 122.7402 | -61.3129 | 61.2167 | 0.00206 | -0.0012732 | 0.0081903 | 0.02421 | 0.039721 | -0.033199 | 0.058422 | -61.4136 | 61.1252 | -61.5234 | -61.3129 | 60.9329 | 0.20142 | -0.28381 | 0.17853 | 61.2076 | -61.5463 | -0.21057 | -0.091553 | -0.10071 | 0 | -0.28381 | -0.23346 | -0.009155 | 0.10986 | 61.0291 | 61.4914 | 122.2458 | 122.438 | -0.10071 | 122.5204 | 61.5143 | -0.23346 | 122.438 | -0.10071 | 61.5143 | 122.2458 | 122.5204 | -122.7402 | -122.7631
638.6875 | 122.6624 | -61.3678 | 61.1801 | -0.0055695 | 0.002572 | 0.011395 | 0.027628 | 0.038653 | -0.034908 | 0.061412 | -61.3953 | 61.2305 | -61.496 | -61.3083 | 60.9055 | 0.17395 | 0 | 0.19226 | 61.322 | -61.5051 | -0.12817 | 0.050354 | -0.027466 | 0.059509 | -0.27466 | -0.13733 | 0.14191 | 0.10071 | 61.3678 | 61.5601 | 122.2733 | 122.5983 | -0.027466 | 122.6898 | 61.5417 | -0.13733 | 122.5983 | -0.027466 | 61.5417 | 122.2733 | 122.6898 | -122.6761 | -122.6852
640.4844 | 122.7951 | -61.2671 | 61.203 | 0.00206 | -0.00041862 | 0.0088311 | 0.022074 | 0.039721 | -0.032558 | 0.05949 | -61.4273 | 61.1847 | -61.4639 | -61.3449 | 60.9283 | 0.21057 | -0.17395 | 0.15564 | 61.2671 | -61.5097 | -0.19684 | -0.018311 | -0.16022 | -0.07782 | -0.27466 | -0.24261 | 0.064087 | 0.036621 | 61.0931 | 61.4227 | 122.1954 | 122.4518 | -0.16022 | 122.5342 | 61.4777 | -0.24261 | 122.4518 | -0.16022 | 61.4777 | 122.1954 | 122.5342 | -122.6669 | -122.7127
642.1875 | 122.699 | -61.3174 | 61.2396 | 0.017319 | 0.002572 | 0.013958 | 0.025492 | 0.039935 | -0.032985 | 0.059917 | -61.3815 | 61.2762 | -61.4319 | -61.2625 | 60.9558 | 0.25177 | 0.059509 | 0.25635 | 61.3541 | -61.4822 | -0.11444 | 0.036621 | -0.064087 | 0.054932 | -0.28381 | -0.16479 | 0.11444 | 0.050354 | 61.377 | 61.5738 | 122.2733 | 122.5937 | -0.064087 | 122.6715 | 61.5692 | -0.16479 | 122.5937 | -0.064087 | 61.5692 | 122.2733 | 122.6715 | -122.6715 | -122.7219
643.8906 | 122.6852 | -61.3312 | 61.235 | -0.0055695 | 0.0032128 | 0.0094721 | 0.02955 | 0.038012 | -0.031277 | 0.059062 | -61.4182 | 61.2717 | -61.4914 | -61.2991 | 60.9238 | 0.2243 | 0.10071 | 0.2243 | 61.322 | -61.5051 | -0.16022 | 0.036621 | -0.086975 | 0.032044 | -0.31128 | -0.17395 | 0.086975 | 0.073242 | 61.4319 | 61.5555 | 122.2549 | 122.6028 | -0.086975 | 122.6532 | 61.5555 | -0.17395 | 122.6028 | -0.086975 | 61.5555 | 122.2549 | 122.6532 | -122.7264 | -122.7402
645.6094 | 122.6578 | -61.3037 | 61.2717 | 0.00206 | 0.00043578 | 0.0092585 | 0.023996 | 0.038653 | -0.030849 | 0.062053 | -61.3266 | 61.2305 | -61.4319 | -61.1984 | 61.0474 | 0.31128 | -0.10986 | 0.31586 | 61.2717 | -61.4731 | -0.12817 | -0.041198 | -0.022888 | 0.10529 | -0.2243 | -0.16937 | 0 | 0.10529 | 61.1938 | 61.6196 | 122.3511 | 122.5342 | -0.022888 | 122.5754 | 61.615 | -0.16937 | 122.5342 | -0.022888 | 61.615 | 122.3511 | 122.5754 | -122.7036 | -122.7448
647.3281 | 122.644 | -61.3586 | 61.1847 | 0.00206 | 0.001504 | 0.0094721 | 0.029978 | 0.037798 | -0.034054 | 0.060771 | -61.3953 | 61.2625 | -61.4914 | -61.2808 | 60.9283 | 0.22888 | 0.009155 | 0.23346 | 61.29 | -61.5051 | -0.13275 | 0.07782 | -0.036621 | 0.07782 | -0.25635 | -0.14648 | 0.10529 | 0.09613 | 61.3678 | 61.5921 | 122.287 | 122.6212 | -0.036621 | 122.6486 | 61.5875 | -0.14648 | 122.6212 | -0.036621 | 61.5875 | 122.287 | 122.6486 | -122.6761 | -122.6898
649.0938 | 122.6532 | -61.3632 | 61.1938 | 0.0096895 | 0.0019312 | 0.010326 | 0.030405 | 0.039935 | -0.03149 | 0.059276 | -61.3861 | 61.2488 | -61.5005 | -61.2854 | 60.9283 | 0.21057 | -0.004578 | 0.21973 | 61.2946 | -61.5097 | -0.13733 | 0.054931 | -0.022888 | 0.07782 | -0.2655 | -0.14648 | 0.10071 | 0.11444 | 61.3586 | 61.5829 | 122.2916 | 122.612 | -0.022888 | 122.6578 | 61.5738 | -0.14648 | 122.612 | -0.022888 | 61.5738 | 122.2916 | 122.6578 | -122.6944 | -122.7036
650.875 | 122.7448 | -61.3129 | 61.1847 | 0.00206 | 0.00064938 | 0.0092585 | 0.025919 | 0.040575 | -0.032558 | 0.057781 | -61.3953 | 61.1526 | -61.5143 | -61.2946 | 60.9238 | 0.19226 | -0.27466 | 0.16937 | 61.1984 | -61.5509 | -0.20142 | -0.032043 | -0.082398 | 0.01831 | -0.26093 | -0.23804 | 0.013733 | 0.11902 | 61.0382 | 61.4822 | 122.2366 | 122.4655 | -0.082398 | 122.5113 | 61.5051 | -0.23804 | 122.4655 | -0.082398 | 61.5051 | 122.2366 | 122.5113 | -122.699 | -122.7356
652.6875 | 122.6715 | -61.3129 | 61.2534 | 0.00206 | 0.00043578 | 0.0094721 | 0.022714 | 0.036303 | -0.03149 | 0.05949 | -61.3312 | 61.2396 | -61.4273 | -61.2442 | 60.9924 | 0.27008 | 0.004578 | 0.28839 | 61.3174 | -61.4685 | -0.11444 | -0.013733 | -0.018311 | 0.068664 | -0.26093 | -0.15564 | 0.064087 | 0.09613 | 61.3174 | 61.6013 | 122.3053 | 122.5525 | -0.018311 | 122.6303 | 61.5829 | -0.15564 | 122.5525 | -0.018311 | 61.5829 | 122.3053 | 122.6303 | -122.6807 | -122.7219
654.4688 | 122.7173 | -61.2991 | 61.1893 | 0.00206 | -0.0012732 | 0.012035 | 0.028055 | 0.040148 | -0.033626 | 0.05949 | -61.3998 | 61.1526 | -61.528 | -61.3037 | 60.9283 | 0.21515 | -0.27008 | 0.16937 | 61.2488 | -61.5463 | -0.22888 | -0.036621 | -0.10071 | -0.004578 | -0.26093 | -0.24719 | 0.059509 | 0.12817 | 61.0291 | 61.4685 | 122.2275 | 122.4518 | -0.10071 | 122.5479 | 61.5143 | -0.24719 | 122.4518 | -0.10071 | 61.5143 | 122.2275 | 122.5479 | -122.7173 | -122.7356
656.1875 | 122.6486 | -61.3724 | 61.171 | 0.017319 | 0.0019312 | 0.012676 | 0.030191 | 0.039721 | -0.033413 | 0.059703 | -61.3998 | 61.2396 | -61.4822 | -61.29 | 60.9238 | 0.21515 | -0.013733 | 0.2243 | 61.3129 | -61.4639 | -0.10986 | 0.068665 | -0.027466 | 0.082397 | -0.24719 | -0.091553 | 0.14191 | 0.082398 | 61.3586 | 61.5967 | 122.2961 | 122.612 | -0.027466 | 122.6852 | 61.5875 | -0.091553 | 122.612 | -0.027466 | 61.5875 | 122.2961 | 122.6852 | -122.6532 | -122.6349
657.9688 | 122.7219 | -61.3037 | 61.203 | 0.00206 | -0.00020502 | 0.0092585 | 0.024637 | 0.040148 | -0.031917 | 0.059703 | -61.3861 | 61.1435 | -61.4822 | -61.3083 | 60.9283 | 0.21057 | -0.30212 | 0.19226 | 61.2076 | -61.5326 | -0.17853 | -0.059509 | -0.082397 | -0.004578 | -0.27466 | -0.22888 | 0.004578 | 0.096131 | 61.0016 | 61.496 | 122.2321 | 122.4472 | -0.082397 | 122.5113 | 61.5143 | -0.22888 | 122.4472 | -0.082397 | 61.5143 | 122.2321 | 122.5113 | -122.6852 | -122.7356
659.6719 | 122.7173 | -61.3174 | 61.1664 | 0.0096895 | 8.578e-06 | 0.014385 | 0.025492 | 0.042498 | -0.030849 | 0.059917 | -61.409 | 61.1389 | -61.4868 | -61.2991 | 60.9192 | 0.21057 | -0.25635 | 0.16937 | 61.2076 | -61.5005 | -0.16937 | -0.027466 | -0.091553 | 0.018311 | -0.24719 | -0.1831 | 0.041199 | 0.077819 | 61.0611 | 61.4868 | 122.2366 | 122.4564 | -0.091553 | 122.525 | 61.528 | -0.1831 | 122.4564 | -0.091553 | 61.528 | 122.2366 | 122.525 | -122.6532 | -122.6669
661.375 | 122.7951 | -61.2396 | 61.1938 | 0.0096895 | 8.578e-06 | 0.014385 | 0.023142 | 0.038012 | -0.032131 | 0.059276 | -61.4044 | 61.2396 | -61.4868 | -61.3129 | 60.91 | 0.20599 | -0.15106 | 0.15106 | 61.2762 | -61.5051 | -0.24719 | 0.045776 | -0.16479 | -0.073242 | -0.28381 | -0.2655 | 0.082397 | 0.082397 | 61.0886 | 61.3907 | 122.1497 | 122.4792 | -0.16479 | 122.5159 | 61.4456 | -0.2655 | 122.4792 | -0.16479 | 61.4456 | 122.1497 | 122.5159 | -122.6807 | -122.699
663.1562 | 122.6669 | -61.3495 | 61.1435 | 0.00206 | 0.00043578 | 0.01054 | 0.029337 | 0.040575 | -0.036831 | 0.060558 | -61.4685 | 61.203 | -61.5372 | -61.3541 | 60.8231 | 0.13733 | -0.018311 | 0.1236 | 61.2808 | -61.5143 | -0.18768 | 0.059509 | -0.11902 | -0.004578 | -0.32043 | -0.16479 | 0.13733 | 0.068664 | 61.3312 | 61.4731 | 122.1725 | 122.5525 | -0.11902 | 122.6303 | 61.4868 | -0.16479 | 122.5525 | -0.11902 | 61.4868 | 122.1725 | 122.6303 | -122.6807 | -122.6578
664.9375 | 122.7081 | -61.3129 | 61.1938 | 0.00206 | -0.0040502 | 0.013958 | 0.023142 | 0.040575 | -0.033626 | 0.059703 | -61.4136 | 61.1206 | -61.5051 | -61.2946 | 60.9238 | 0.2243 | -0.27466 | 0.18768 | 61.1938 | -61.5143 | -0.19226 | -0.073243 | -0.10071 | 0.01831 | -0.27008 | -0.20142 | 0 | 0.091553 | 61.0382 | 61.5005 | 122.2366 | 122.4335 | -0.10071 | 122.5067 | 61.5372 | -0.20142 | 122.4335 | -0.10071 | 61.5372 | 122.2366 | 122.5067 | -122.699 | -122.7081
666.6406 | 122.6944 | -61.3312 | 61.1801 | 0.00206 | 0.00086298 | 0.013104 | 0.031046 | 0.037798 | -0.03149 | 0.056926 | -61.4639 | 61.1938 | -61.5234 | -61.3724 | 60.8368 | 0.13275 | -0.018311 | 0.11444 | 61.2717 | -61.5189 | -0.19226 | 0.013733 | -0.13275 | -0.041198 | -0.34332 | -0.18768 | 0.091552 | 0.059509 | 61.3129 | 61.4456 | 122.168 | 122.525 | -0.13275 | 122.6028 | 61.4639 | -0.18768 | 122.525 | -0.13275 | 61.4639 | 122.168 | 122.6028 | -122.7036 | -122.699
668.375 | 122.6852 | -61.2991 | 61.1755 | 0.017319 | 0.00086298 | 0.010113 | 0.026346 | 0.038226 | -0.034908 | 0.05949 | -61.4182 | 61.2671 | -61.4502 | -61.2991 | 60.9055 | 0.20599 | 0.13275 | 0.21057 | 61.3312 | -61.4731 | -0.15106 | 0.091553 | -0.11902 | 0 | -0.27008 | -0.17395 | 0.15564 | 0.032043 | 61.4319 | 61.5097 | 122.2046 | 122.5662 | -0.11902 | 122.6303 | 61.5051 | -0.17395 | 122.5662 | -0.11902 | 61.5051 | 122.2046 | 122.6303 | -122.6257 | -122.6486
670.1406 | 122.644 | -61.3449 | 61.1801 | 0.0096895 | 8.578e-06 | 0.0071221 | 0.026773 | 0.039507 | -0.033626 | 0.058422 | -61.4136 | 61.2534 | -61.4914 | -61.3083 | 60.9238 | 0.21515 | 0.10529 | 0.21057 | 61.3495 | -61.4639 | -0.14648 | 0.073242 | -0.068664 | 0.036621 | -0.25635 | -0.11902 | 0.16937 | 0.07782 | 61.4502 | 61.5555 | 122.2687 | 122.5983 | -0.068664 | 122.6944 | 61.5601 | -0.11902 | 122.5983 | -0.068664 | 61.5601 | 122.2687 | 122.6944 | -122.6715 | -122.644
671.9375 | 122.6532 | -61.2808 | 61.2625 | 0.00206 | 0.002572 | 0.0092585 | 0.023142 | 0.038653 | -0.031704 | 0.058635 | -61.3174 | 61.235 | -61.3998 | -61.2259 | 60.997 | 0.28839 | 0 | 0.31586 | 61.3174 | -61.5005 | -0.11902 | -0.027466 | -0.036621 | 0.054932 | -0.2655 | -0.21973 | 0.054932 | 0.082397 | 61.2808 | 61.5967 | 122.2778 | 122.5159 | -0.036621 | 122.5983 | 61.5692 | -0.21973 | 122.5159 | -0.036621 | 61.5692 | 122.2778 | 122.5983 | -122.6624 | -122.7631
673.7344 | 122.7859 | -61.2579 | 61.203 | -0.0055695 | 0.00022218 | 0.010754 | 0.023783 | 0.037798 | -0.031704 | 0.059703 | -61.4182 | 61.171 | -61.4777 | -61.3037 | 60.9192 | 0.19226 | -0.16479 | 0.16937 | 61.2259 | -61.5372 | -0.21973 | -0.032044 | -0.16022 | -0.045776 | -0.28381 | -0.27923 | 0.022888 | 0.059509 | 61.0931 | 61.4273 | 122.1771 | 122.4289 | -0.16022 | 122.4838 | 61.4502 | -0.27923 | 122.4289 | -0.16022 | 61.4502 | 122.1771 | 122.4838 | -122.6807 | -122.7402
675.5312 | 122.7768 | -61.3312 | 61.1023 | 0.00206 | 0.0057764 | 0.01054 | 0.030405 | 0.040575 | -0.032345 | 0.059062 | -61.4914 | 61.2076 | -61.5692 | -61.3998 | 60.791 | 0.082397 | -0.068665 | 0.068665 | 61.2625 | -61.5463 | -0.23804 | 0.10529 | -0.16022 | -0.068664 | -0.31128 | -0.21515 | 0.16022 | 0.07782 | 61.2625 | 61.3998 | 122.1222 | 122.5388 | -0.16022 | 122.5937 | 61.4136 | -0.21515 | 122.5388 | -0.16022 | 61.4136 | 122.1222 | 122.5937 | -122.6715 | -122.6486
677.25 | 122.7402 | -61.2946 | 61.1206 | -0.0055695 | 0.0027856 | 0.011608 | 0.026132 | 0.041857 | -0.032345 | 0.05949 | -61.4731 | 61.1938 | -61.5326 | -61.3953 | 60.8139 | 0.11902 | -0.1236 | 0.07782 | 61.2579 | -61.5601 | -0.23804 | 0.073243 | -0.17853 | -0.10071 | -0.3067 | -0.2655 | 0.13733 | 0.05951 | 61.171 | 61.3724 | 122.1085 | 122.4884 | -0.17853 | 122.5525 | 61.4136 | -0.2655 | 122.4884 | -0.17853 | 61.4136 | 122.1085 | 122.5525 | -122.6532 | -122.6807
678.9688 | 122.7539 | -61.3129 | 61.1252 | 0.00206 | 0.0017176 | 0.0066949 | 0.027414 | 0.041003 | -0.032558 | 0.060131 | -61.4731 | 61.1938 | -61.5372 | -61.3815 | 60.8185 | 0.11902 | -0.091553 | 0.07782 | 61.2671 | -61.5097 | -0.2243 | 0.068665 | -0.16022 | -0.068665 | -0.3067 | -0.19684 | 0.14191 | 0.064087 | 61.2213 | 61.3907 | 122.1313 | 122.5067 | -0.16022 | 122.58 | 61.4319 | -0.19684 | 122.5067 | -0.16022 | 61.4319 | 122.1313 | 122.58 | -122.6624 | -122.6349
680.75 | 122.7539 | -61.3312 | 61.1206 | 0.0096895 | 0.002572 | 0.015026 | 0.027841 | 0.041216 | -0.034267 | 0.059917 | -61.4639 | 61.2167 | -61.5097 | -61.3907 | 60.8276 | 0.10986 | -0.086975 | 0.068665 | 61.2671 | -61.5463 | -0.17853 | 0.096131 | -0.13275 | -0.059509 | -0.29297 | -0.21515 | 0.14649 | 0.045777 | 61.2442 | 61.3998 | 122.1588 | 122.5479 | -0.13275 | 122.5983 | 61.441 | -0.21515 | 122.5479 | -0.13275 | 61.441 | 122.1588 | 122.5983 | -122.6303 | -122.6669
682.5469 | 122.6349 | -61.3174 | 61.1801 | 0.017319 | 0.0010766 | 0.015026 | 0.026132 | 0.03908 | -0.033626 | 0.05949 | -61.3998 | 61.2305 | -61.4868 | -61.2762 | 60.9192 | 0.22888 | 0.045776 | 0.23346 | 61.2854 | -61.4777 | -0.16937 | 0.050354 | -0.082397 | 0.041199 | -0.26093 | -0.16022 | 0.10529 | 0.086975 | 61.3632 | 61.5509 | 122.2366 | 122.5479 | -0.082397 | 122.6028 | 61.5463 | -0.16022 | 122.5479 | -0.082397 | 61.5463 | 122.2366 | 122.6028 | -122.6669 | -122.6578
684.2656 | 122.6395 | -61.3403 | 61.1618 | 0.0096895 | 0.00086298 | 0.0098993 | 0.026987 | 0.039507 | -0.034908 | 0.05949 | -61.409 | 61.2076 | -61.4777 | -61.3129 | 60.8871 | 0.19684 | -0.004578 | 0.19226 | 61.2762 | -61.5189 | -0.13733 | 0.045777 | -0.068665 | 0.027466 | -0.27466 | -0.17853 | 0.11444 | 0.068664 | 61.3358 | 61.5326 | 122.2275 | 122.5479 | -0.068665 | 122.6166 | 61.5372 | -0.17853 | 122.5479 | -0.068665 | 61.5372 | 122.2275 | 122.6166 | -122.6395 | -122.6807
686.0312 | 122.6669 | -61.2854 | 61.2213 | -0.0055695 | 0.0017176 | 0.013744 | 0.023783 | 0.038439 | -0.028286 | 0.05949 | -61.3953 | 61.2625 | -61.441 | -61.2854 | 60.9146 | 0.21973 | 0.10986 | 0.23346 | 61.3174 | -61.4822 | -0.15564 | 0.041199 | -0.10986 | 0 | -0.3067 | -0.19684 | 0.096131 | 0.045776 | 61.3953 | 61.5189 | 122.2 | 122.5479 | -0.10986 | 122.6028 | 61.5051 | -0.19684 | 122.5479 | -0.10986 | 61.5051 | 122.2 | 122.6028 | -122.6624 | -122.7036
687.8125 | 122.7493 | -61.2579 | 61.203 | 0.00206 | 0.00043578 | 0.014599 | 0.022501 | 0.040362 | -0.031917 | 0.059917 | -61.409 | 61.1618 | -61.4548 | -61.322 | 60.9055 | 0.20142 | -0.1831 | 0.13733 | 61.2488 | -61.4731 | -0.19684 | -0.041199 | -0.15106 | -0.064086 | -0.29755 | -0.21515 | 0.045776 | 0.045776 | 61.0748 | 61.3953 | 122.1634 | 122.4197 | -0.15106 | 122.5067 | 61.4594 | -0.21515 | 122.4197 | -0.15106 | 61.4594 | 122.1634 | 122.5067 | -122.6578 | -122.6761
689.5781 | 122.644 | -61.2991 | 61.2534 | 0.0096895 | 8.578e-06 | 0.010326 | 0.026773 | 0.037798 | -0.029781 | 0.058422 | -61.3129 | 61.2579 | -61.3998 | -61.203 | 60.9924 | 0.30212 | 0.004578 | 0.31586 | 61.3129 | -61.4731 | -0.10071 | 0.004578 | -0.013733 | 0.09613 | -0.26093 | -0.17395 | 0.059509 | 0.086975 | 61.3037 | 61.615 | 122.2916 | 122.5571 | -0.013733 | 122.612 | 61.6013 | -0.17395 | 122.5571 | -0.013733 | 61.6013 | 122.2916 | 122.612 | -122.6532 | -122.7264
691.2812 | 122.7219 | -61.2991 | 61.1664 | 0.00206 | -0.0014868 | 0.012676 | 0.028482 | 0.039507 | -0.03149 | 0.060985 | -61.3953 | 61.1206 | -61.4914 | -61.2854 | 60.9146 | 0.21515 | -0.28381 | 0.16479 | 61.1893 | -61.4914 | -0.19226 | -0.045777 | -0.096131 | 0.013733 | -0.25177 | -0.19226 | 0.022888 | 0.09613 | 61.0153 | 61.4639 | 122.2137 | 122.4197 | -0.096131 | 122.4884 | 61.5143 | -0.19226 | 122.4197 | -0.096131 | 61.5143 | 122.2137 | 122.4884 | -122.6578 | -122.6578
693.0781 | 122.6395 | -61.2625 | 61.2717 | 0.00206 | 0.0023584 | 0.010326 | 0.02421 | 0.038653 | -0.032131 | 0.060344 | -61.3037 | 61.2305 | -61.4044 | -61.1893 | 61.0199 | 0.32959 | -0.09613 | 0.33875 | 61.2762 | -61.4456 | -0.14191 | -0.041198 | -0.041199 | 0.073242 | -0.25177 | -0.18311 | 0.004578 | 0.10071 | 61.1664 | 61.6013 | 122.2824 | 122.493 | -0.041199 | 122.5388 | 61.5921 | -0.18311 | 122.493 | -0.041199 | 61.5921 | 122.2824 | 122.5388 | -122.6761 | -122.7173
694.8594 | 122.6761 | -61.2946 | 61.2076 | 0.00206 | 0.0010766 | 0.0069085 | 0.027841 | 0.038226 | -0.033199 | 0.058635 | -61.4136 | 61.2854 | -61.4594 | -61.2991 | 60.8688 | 0.19684 | 0.10529 | 0.19684 | 61.3083 | -61.4822 | -0.16479 | 0.077819 | -0.11902 | -0.004577 | -0.33875 | -0.18768 | 0.10071 | 0.045777 | 61.3998 | 61.4914 | 122.1634 | 122.58 | -0.11902 | 122.6028 | 61.4914 | -0.18768 | 122.58 | -0.11902 | 61.4914 | 122.1634 | 122.6028 | -122.6669 | -122.6898
696.5781 | 122.7448 | -61.2534 | 61.1801 | -0.0055695 | 0.0019312 | 0.0096857 | 0.024851 | 0.037585 | -0.030422 | 0.059917 | -61.3998 | 61.1572 | -61.4456 | -61.3037 | 60.8963 | 0.20599 | -0.17395 | 0.16022 | 61.2167 | -61.5143 | -0.19226 | -0.022888 | -0.14648 | -0.050354 | -0.28381 | -0.26093 | 0.036621 | 0.045777 | 61.0794 | 61.4136 | 122.1497 | 122.4106 | -0.14648 | 122.4701 | 61.4594 | -0.26093 | 122.4106 | -0.14648 | 61.4594 | 122.1497 | 122.4701 | -122.6257 | -122.6944
698.3594 | 122.7539 | -61.2259 | 61.203 | 0.0096895 | 0.0027856 | 0.012035 | 0.023783 | 0.037585 | -0.030849 | 0.058849 | -61.3815 | 61.203 | -61.4502 | -61.2808 | 60.9192 | 0.21515 | -0.14648 | 0.20599 | 61.2534 | -61.4822 | -0.2243 | 0 | -0.15564 | -0.054932 | -0.28381 | -0.25635 | 0.050354 | 0.068664 | 61.0794 | 61.4319 | 122.1451 | 122.4289 | -0.15564 | 122.4792 | 61.441 | -0.25635 | 122.4289 | -0.15564 | 61.441 | 122.1451 | 122.4792 | -122.6532 | -122.6852
700.0781 | 122.612 | -61.2625 | 61.2488 | -0.0055695 | -0.0017004 | 0.012035 | 0.027841 | 0.037157 | -0.03384 | 0.057994 | -61.3037 | 61.203 | -61.4273 | -61.1893 | 60.9879 | 0.30212 | -0.07782 | 0.31586 | 61.3083 | -61.4548 | -0.16479 | -0.045776 | -0.041199 | 0.073242 | -0.26093 | -0.19226 | 0.05951 | 0.1236 | 61.1847 | 61.5784 | 122.2504 | 122.4655 | -0.041199 | 122.5708 | 61.5646 | -0.19226 | 122.4655 | -0.041199 | 61.5646 | 122.2504 | 122.5708 | -122.6761 | -122.7036
701.8438 | 122.7448 | -61.2808 | 61.1252 | 0.0096895 | 0.00086298 | 0.0098993 | 0.029764 | 0.042284 | -0.034908 | 0.057994 | -61.4731 | 61.1801 | -61.5463 | -61.3586 | 60.8002 | 0.1236 | -0.14191 | 0.073242 | 61.2442 | -61.5234 | -0.2655 | 0.054932 | -0.19226 | -0.07782 | -0.32501 | -0.24261 | 0.11902 | 0.073243 | 61.1389 | 61.3541 | 122.081 | 122.4609 | -0.19226 | 122.525 | 61.4044 | -0.24261 | 122.4609 | -0.19226 | 61.4044 | 122.081 | 122.525 | -122.6715 | -122.6486
703.6406 | 122.7448 | -61.235 | 61.1984 | -0.0055695 | 8.578e-06 | 0.012676 | 0.026773 | 0.038226 | -0.033199 | 0.060771 | -61.3815 | 61.171 | -61.4456 | -61.2808 | 60.8963 | 0.18768 | -0.17395 | 0.15106 | 61.2305 | -61.496 | -0.21057 | -0.027466 | -0.14649 | -0.045777 | -0.30212 | -0.26093 | 0.032044 | 0.064087 | 61.0611 | 61.3861 | 122.1313 | 122.406 | -0.14649 | 122.4655 | 61.4227 | -0.26093 | 122.406 | -0.14649 | 61.4227 | 122.1313 | 122.4655 | -122.644 | -122.6944
705.3438 | 122.6715 | -61.29 | 61.2259 | 0.00206 | 0.0044946 | 0.011181 | 0.02955 | 0.038653 | -0.033413 | 0.060771 | -61.3678 | 61.29 | -61.4319 | -61.2579 | 60.91 | 0.2243 | 0.091553 | 0.23804 | 61.3312 | -61.4914 | -0.14191 | 0.064087 | -0.07782 | 0.032043 | -0.31586 | -0.20142 | 0.10529 | 0.064087 | 61.3815 | 61.528 | 122.2 | 122.58 | -0.07782 | 122.6212 | 61.5143 | -0.20142 | 122.58 | -0.07782 | 61.5143 | 122.2 | 122.6212 | -122.6578 | -122.7173
707.1094 | 122.7036 | -61.2808 | 61.1572 | 0.00206 | -0.00084602 | 0.014385 | 0.026987 | 0.040575 | -0.033413 | 0.058208 | -61.3724 | 61.1298 | -61.496 | -61.2534 | 60.9055 | 0.21973 | -0.26093 | 0.19684 | 61.2213 | -61.4868 | -0.21515 | -0.027466 | -0.091552 | 0.027466 | -0.25177 | -0.20599 | 0.064086 | 0.1236 | 61.0199 | 61.4777 | 122.1863 | 122.4106 | -0.091552 | 122.5021 | 61.5005 | -0.20599 | 122.4106 | -0.091552 | 61.5005 | 122.1863 | 122.5021 | -122.6532 | -122.644
708.8906 | 122.7402 | -61.2854 | 61.1252 | 0.0096895 | 0.0017176 | 0.0084039 | 0.028482 | 0.039935 | -0.033199 | 0.062267 | -61.4777 | 61.1755 | -61.5463 | -61.3586 | 60.8093 | 0.10986 | -0.082397 | 0.073242 | 61.2488 | -61.496 | -0.26093 | 0.050354 | -0.19226 | -0.073243 | -0.31586 | -0.21057 | 0.1236 | 0.068665 | 61.203 | 61.3586 | 122.0947 | 122.4609 | -0.19226 | 122.5342 | 61.3953 | -0.21057 | 122.4609 | -0.19226 | 61.3953 | 122.0947 | 122.5342 | -122.6715 | -122.6212
710.6094 | 122.6624 | -61.29 | 61.1893 | 0.0096895 | 0.001504 | 0.0081903 | 0.026987 | 0.039294 | -0.036831 | 0.05949 | -61.409 | 61.2671 | -61.4456 | -61.2808 | 60.9146 | 0.22888 | 0.12817 | 0.2243 | 61.3586 | -61.4502 | -0.15564 | 0.07782 | -0.11902 | 0.009155 | -0.27466 | -0.16022 | 0.16937 | 0.036621 | 61.4182 | 61.5143 | 122.2046 | 122.5571 | -0.11902 | 122.6486 | 61.5189 | -0.16022 | 122.5571 | -0.11902 | 61.5189 | 122.2046 | 122.6486 | -122.6349 | -122.6395
712.3281 | 122.6166 | -61.3037 | 61.171 | 0.00206 | 0.0049218 | 0.012035 | 0.030405 | 0.040362 | -0.031917 | 0.061412 | -61.3678 | 61.2579 | -61.4365 | -61.2534 | 60.9146 | 0.24261 | 0.027466 | 0.23804 | 61.3083 | -61.4822 | -0.13275 | 0.086976 | -0.064087 | 0.050354 | -0.25635 | -0.17853 | 0.13733 | 0.068664 | 61.3312 | 61.5417 | 122.2183 | 122.5616 | -0.064087 | 122.612 | 61.5463 | -0.17853 | 122.5616 | -0.064087 | 61.5463 | 122.2183 | 122.612 | -122.6074 | -122.6532
714.1094 | 122.7722 | -61.2396 | 61.1664 | 0.00206 | 0.0027856 | 0.014385 | 0.022928 | 0.038012 | -0.031063 | 0.059703 | -61.3953 | 61.1984 | -61.4502 | -61.2854 | 60.9009 | 0.20599 | -0.17395 | 0.14191 | 61.2259 | -61.4822 | -0.21057 | 0.032043 | -0.15564 | -0.045776 | -0.2655 | -0.24262 | 0.059509 | 0.054931 | 61.0657 | 61.3815 | 122.1405 | 122.438 | -0.15564 | 122.4655 | 61.4456 | -0.24262 | 122.438 | -0.15564 | 61.4456 | 122.1405 | 122.4655 | -122.6166 | -122.6486
715.875 | 122.6898 | -61.2808 | 61.1389 | 0.00206 | 0.0010766 | 0.014813 | 0.028269 | 0.041003 | -0.031704 | 0.057994 | -61.4182 | 61.1343 | -61.528 | -61.3037 | 60.8643 | 0.20142 | -0.23346 | 0.16022 | 61.2259 | -61.496 | -0.24719 | -0.004578 | -0.13733 | -0.022888 | -0.27466 | -0.21515 | 0.086975 | 0.10986 | 61.0474 | 61.441 | 122.1451 | 122.4152 | -0.13733 | 122.5067 | 61.4822 | -0.21515 | 122.4152 | -0.13733 | 61.4822 | 122.1451 | 122.5067 | -122.6669 | -122.6349
717.6562 | 122.6944 | -61.2213 | 61.1938 | -0.013199 | 0.00022218 | 0.0066949 | 0.024423 | 0.038439 | -0.034054 | 0.058208 | -61.3312 | 61.1984 | -61.4182 | -61.203 | 60.9787 | 0.30212 | -0.14191 | 0.27008 | 61.2762 | -61.4319 | -0.19684 | 0.004577 | -0.10986 | 0.01831 | -0.21515 | -0.21057 | 0.082397 | 0.086975 | 61.0794 | 61.4914 | 122.2 | 122.4197 | -0.10986 | 122.4976 | 61.5234 | -0.21057 | 122.4197 | -0.10986 | 61.5234 | 122.2 | 122.4976 | -122.612 | -122.6257
719.375 | 122.731 | -61.2854 | 61.0977 | -0.0055695 | 0.00086298 | 0.010113 | 0.029337 | 0.040362 | -0.032985 | 0.059703 | -61.4868 | 61.171 | -61.5189 | -61.3907 | 60.7864 | 0.10529 | -0.041199 | 0.064087 | 61.2396 | -61.5189 | -0.23346 | 0.073242 | -0.20142 | -0.10529 | -0.31128 | -0.23346 | 0.14191 | 0.032044 | 61.2442 | 61.3495 | 122.0718 | 122.4564 | -0.20142 | 122.525 | 61.3907 | -0.23346 | 122.4564 | -0.20142 | 61.3907 | 122.0718 | 122.525 | -122.6166 | -122.6166
721.1406 | 122.5845 | -61.3358 | 61.1572 | 0.017319 | 0.00064938 | 0.0092585 | 0.029123 | 0.041003 | -0.03384 | 0.059703 | -61.3632 | 61.1893 | -61.4456 | -61.2625 | 60.8917 | 0.2243 | -0.009155 | 0.21515 | 61.29 | -61.4639 | -0.10986 | 0.032043 | -0.027466 | 0.073242 | -0.2655 | -0.12817 | 0.13275 | 0.082398 | 61.3266 | 61.5509 | 122.2275 | 122.525 | -0.027466 | 122.6257 | 61.5601 | -0.12817 | 122.525 | -0.027466 | 61.5601 | 122.2275 | 122.6257 | -122.6028 | -122.6212
722.9219 | 122.5754 | -61.3358 | 61.1755 | -0.0055695 | 0.0032128 | 0.013744 | 0.029764 | 0.041857 | -0.032985 | 0.060131 | -61.3358 | 61.2213 | -61.4319 | -61.2625 | 60.9009 | 0.24261 | -0.004578 | 0.22888 | 61.2717 | -61.5005 | -0.096131 | 0.045776 | 0 | 0.073242 | -0.27466 | -0.16479 | 0.09613 | 0.096131 | 61.3312 | 61.5646 | 122.2366 | 122.5571 | 0 | 122.6074 | 61.5784 | -0.16479 | 122.5571 | 0 | 61.5784 | 122.2366 | 122.6074 | -122.6074 | -122.6761
724.7031 | 122.6578 | -61.3312 | 61.1298 | 0.00206 | 0.0038538 | 0.012035 | 0.027628 | 0.040362 | -0.033626 | 0.061199 | -61.441 | 61.1984 | -61.4914 | -61.3586 | 60.8185 | 0.11902 | -0.018311 | 0.09613 | 61.2534 | -61.5143 | -0.16022 | 0.068664 | -0.10986 | -0.027466 | -0.31128 | -0.18311 | 0.1236 | 0.050354 | 61.3129 | 61.4273 | 122.1497 | 122.5296 | -0.10986 | 122.5845 | 61.4502 | -0.18311 | 122.5296 | -0.10986 | 61.4502 | 122.1497 | 122.5845 | -122.6212 | -122.644
726.4844 | 122.7264 | -61.2122 | 61.1755 | 0.0096895 | 0.0017176 | 0.010326 | 0.021005 | 0.039935 | -0.029781 | 0.057567 | -61.409 | 61.1984 | -61.4639 | -61.2991 | 60.8917 | 0.21057 | -0.14648 | 0.16479 | 61.2259 | -61.5051 | -0.25177 | 0.022888 | -0.19684 | -0.086975 | -0.28381 | -0.29297 | 0.050354 | 0.054931 | 61.0657 | 61.377 | 122.1039 | 122.4106 | -0.19684 | 122.438 | 61.4227 | -0.29297 | 122.4106 | -0.19684 | 61.4227 | 122.1039 | 122.438 | -122.6395 | -122.6807
728.1875 | 122.5662 | -61.3312 | 61.1938 | -0.0055695 | 0.0012902 | 0.014172 | 0.028269 | 0.039721 | -0.034694 | 0.060344 | -61.3678 | 61.235 | -61.4548 | -61.2762 | 60.8963 | 0.24261 | 0.009155 | 0.2243 | 61.2991 | -61.4594 | -0.1236 | 0.041198 | -0.036621 | 0.054932 | -0.29755 | -0.12817 | 0.10528 | 0.086975 | 61.3403 | 61.5555 | 122.2275 | 122.5662 | -0.036621 | 122.6303 | 61.5738 | -0.12817 | 122.5662 | -0.036621 | 61.5738 | 122.2275 | 122.6303 | -122.6486 | -122.6532
729.9688 | 122.6624 | -61.2808 | 61.1893 | -0.013199 | 0.0029992 | 0.011181 | 0.026346 | 0.04143 | -0.032131 | 0.058208 | -61.3815 | 61.2717 | -61.441 | -61.2946 | 60.8917 | 0.22888 | 0.14648 | 0.21057 | 61.3083 | -61.4868 | -0.16022 | 0.082397 | -0.10071 | -0.013733 | -0.29755 | -0.20599 | 0.11902 | 0.059509 | 61.4273 | 61.4914 | 122.1725 | 122.5525 | -0.10071 | 122.5891 | 61.5097 | -0.20599 | 122.5525 | -0.10071 | 61.5097 | 122.1725 | 122.5891 | -122.6303 | -122.6761
731.7344 | 122.5891 | -61.2442 | 61.2488 | 0.0096895 | -0.00020502 | 0.011395 | 0.023996 | 0.038653 | -0.034267 | 0.057994 | -61.3083 | 61.2122 | -61.377 | -61.1938 | 60.9879 | 0.32959 | -0.054932 | 0.32044 | 61.2396 | -61.4456 | -0.13275 | -0.036621 | -0.064087 | 0.050354 | -0.26093 | -0.20142 | -0.009155 | 0.068664 | 61.1893 | 61.5646 | 122.2321 | 122.4564 | -0.064087 | 122.4838 | 61.5738 | -0.20142 | 122.4564 | -0.064087 | 61.5738 | 122.2321 | 122.4838 | -122.6257 | -122.6944
733.5156 | 122.6761 | -61.2488 | 61.171 | 0.0096895 | 0.0017176 | 0.010754 | 0.024637 | 0.041003 | -0.031917 | 0.059276 | -61.3632 | 61.1435 | -61.4685 | -61.2671 | 60.8963 | 0.21515 | -0.25635 | 0.16937 | 61.1893 | -61.4822 | -0.21973 | -0.027465 | -0.11444 | -0.018311 | -0.27466 | -0.23346 | 0.018311 | 0.10529 | 60.9924 | 61.4182 | 122.1451 | 122.3923 | -0.11444 | 122.438 | 61.4639 | -0.23346 | 122.3923 | -0.11444 | 61.4639 | 122.1451 | 122.438 | -122.6395 | -122.6532
735.2188 | 122.6486 | -61.235 | 61.1435 | 0.0096895 | 0.0027856 | 0.0098993 | 0.026346 | 0.039721 | -0.033199 | 0.058422 | -61.3495 | 61.1206 | -61.4548 | -61.2625 | 60.8871 | 0.22888 | -0.28381 | 0.17395 | 61.1984 | -61.4914 | -0.21973 | -0.022889 | -0.11444 | -0.027466 | -0.25635 | -0.25635 | 0.054931 | 0.10529 | 60.9512 | 61.409 | 122.1222 | 122.3557 | -0.11444 | 122.4335 | 61.4639 | -0.25635 | 122.3557 | -0.11444 | 61.4639 | 122.1222 | 122.4335 | -122.5983 | -122.6349
737 | 122.7219 | -61.2122 | 61.1847 | 0.00206 | 0.0023584 | 0.01289 | 0.023142 | 0.038439 | -0.031277 | 0.059062 | -61.3998 | 61.2076 | -61.4365 | -61.2762 | 60.9009 | 0.21515 | -0.14191 | 0.1831 | 61.2671 | -61.4777 | -0.2243 | 0.022889 | -0.18768 | -0.064087 | -0.28381 | -0.2655 | 0.082398 | 0.036621 | 61.0703 | 61.3953 | 122.113 | 122.4197 | -0.18768 | 122.4792 | 61.4273 | -0.2655 | 122.4197 | -0.18768 | 61.4273 | 122.113 | 122.4792 | -122.6212 | -122.6624
738.7812 | 122.6212 | -61.2762 | 61.1847 | 0.00206 | -0.00041862 | 0.0066949 | 0.026773 | 0.040362 | -0.032772 | 0.058635 | -61.3861 | 61.2442 | -61.4639 | -61.2625 | 60.9009 | 0.21973 | 0.11902 | 0.22888 | 61.3312 | -61.4365 | -0.18768 | 0.05951 | -0.10986 | 0.013733 | -0.28381 | -0.16022 | 0.14648 | 0.07782 | 61.3953 | 61.5051 | 122.1771 | 122.5204 | -0.10986 | 122.6074 | 61.496 | -0.16022 | 122.5204 | -0.10986 | 61.496 | 122.1771 | 122.6074 | -122.6486 | -122.6212
740.5625 | 122.6761 | -61.2762 | 61.1481 | 0.0096895 | -0.00084602 | 0.01054 | 0.028055 | 0.040148 | -0.032131 | 0.059062 | -61.3632 | 61.1343 | -61.4777 | -61.2808 | 60.878 | 0.21515 | -0.27924 | 0.16937 | 61.1618 | -61.5189 | -0.20142 | -0.013733 | -0.086975 | -0.004578 | -0.27008 | -0.24261 | 0.013733 | 0.11444 | 60.997 | 61.4456 | 122.1542 | 122.4106 | -0.086975 | 122.438 | 61.4914 | -0.24261 | 122.4106 | -0.086975 | 61.4914 | 122.1542 | 122.438 | -122.6257 | -122.6669
742.2656 | 122.7127 | -61.2396 | 61.1481 | -0.0055695 | -0.00020502 | 0.0086175 | 0.023996 | 0.039294 | -0.03149 | 0.060344 | -61.3724 | 61.1252 | -61.4639 | -61.2762 | 60.9055 | 0.21057 | -0.19684 | 0.16937 | 61.1938 | -61.4822 | -0.2243 | -0.022888 | -0.13275 | -0.036621 | -0.24261 | -0.24262 | 0.045777 | 0.091553 | 61.0428 | 61.409 | 122.1451 | 122.3648 | -0.13275 | 122.4335 | 61.4502 | -0.24262 | 122.3648 | -0.13275 | 61.4502 | 122.1451 | 122.4335 | -122.612 | -122.6303
744.0469 | 122.5891 | -61.2625 | 61.235 | 0.0096895 | 0.0019312 | 0.0062677 | 0.025278 | 0.037371 | -0.030636 | 0.056926 | -61.2808 | 61.2076 | -61.4044 | -61.1801 | 60.9879 | 0.32501 | -0.086975 | 0.32044 | 61.2762 | -61.3907 | -0.14191 | -0.027465 | -0.018311 | 0.082397 | -0.24719 | -0.12817 | 0.041199 | 0.1236 | 61.1755 | 61.5829 | 122.2504 | 122.4701 | -0.018311 | 122.5388 | 61.5875 | -0.12817 | 122.4701 | -0.018311 | 61.5875 | 122.2504 | 122.5388 | -122.6395 | -122.6257
745.8125 | 122.5937 | -61.2305 | 61.2442 | -0.0055695 | 0.0023584 | 0.0077631 | 0.025064 | 0.036944 | -0.032558 | 0.057994 | -61.2854 | 61.1801 | -61.3953 | -61.1481 | 61.0107 | 0.32959 | -0.11444 | 0.33417 | 61.29 | -61.4594 | -0.16479 | -0.064087 | -0.054931 | 0.082398 | -0.23346 | -0.22888 | 0.045776 | 0.10986 | 61.116 | 61.5646 | 122.2412 | 122.4106 | -0.054931 | 122.5204 | 61.5601 | -0.22888 | 122.4106 | -0.054931 | 61.5601 | 122.2412 | 122.5204 | -122.6395 | -122.7036
747.5938 | 122.6257 | -61.2625 | 61.2122 | 0.00206 | -0.00041862 | 0.0096857 | 0.026346 | 0.038439 | -0.032558 | 0.059062 | -61.3907 | 61.2671 | -61.4227 | -61.2579 | 60.8963 | 0.22888 | 0.13733 | 0.23346 | 61.3403 | -61.4319 | -0.16022 | 0.054932 | -0.12817 | 0.004577 | -0.31586 | -0.16937 | 0.12817 | 0.032043 | 61.3998 | 61.496 | 122.1588 | 122.5296 | -0.12817 | 122.6028 | 61.4914 | -0.16937 | 122.5296 | -0.12817 | 61.4914 | 122.1588 | 122.6028 | -122.6349 | -122.644
749.3125 | 122.6807 | -61.2854 | 61.116 | 0.0096895 | 0.0017176 | 0.012249 | 0.02955 | 0.040148 | -0.035976 | 0.059917 | -61.4456 | 61.1526 | -61.5189 | -61.3449 | 60.8093 | 0.1236 | -0.16937 | 0.09613 | 61.2213 | -61.4777 | -0.23346 | 0.036621 | -0.16022 | -0.05951 | -0.3067 | -0.19226 | 0.10529 | 0.073242 | 61.116 | 61.3815 | 122.0947 | 122.438 | -0.16022 | 122.5067 | 61.409 | -0.19226 | 122.438 | -0.16022 | 61.409 | 122.0947 | 122.5067 | -122.6349 | -122.5937
751.0938 | 122.5937 | -61.2305 | 61.2305 | 0.0096895 | -0.00020502 | 0.011608 | 0.02421 | 0.03908 | -0.033199 | 0.057353 | -61.2671 | 61.2167 | -61.409 | -61.1664 | 60.9833 | 0.32501 | -0.10986 | 0.33417 | 61.2579 | -61.4273 | -0.17853 | -0.013733 | -0.036621 | 0.064087 | -0.24719 | -0.19684 | 0.027466 | 0.14191 | 61.1206 | 61.5646 | 122.2137 | 122.4472 | -0.036621 | 122.4884 | 61.5555 | -0.19684 | 122.4472 | -0.036621 | 61.5555 | 122.2137 | 122.4884 | -122.6395 | -122.6578
752.7969 | 122.5845 | -61.2579 | 61.2442 | -0.0055695 | 0.0019312 | 0.010113 | 0.02421 | 0.037157 | -0.031063 | 0.060344 | -61.2625 | 61.1938 | -61.3861 | -61.1526 | 61.0016 | 0.33875 | -0.10071 | 0.35248 | 61.2442 | -61.4365 | -0.12817 | -0.050354 | -0.004577 | 0.10529 | -0.24262 | -0.17853 | 0 | 0.1236 | 61.1572 | 61.6104 | 122.2595 | 122.4518 | -0.004577 | 122.5021 | 61.5967 | -0.17853 | 122.4518 | -0.004577 | 61.5967 | 122.2595 | 122.5021 | -122.6303 | -122.6807
754.5156 | 122.7173 | -61.203 | 61.1664 | 0.00206 | 0.0012902 | 0.011608 | 0.023569 | 0.036303 | -0.031063 | 0.061199 | -61.3861 | 61.1618 | -61.4456 | -61.2808 | 60.8826 | 0.21057 | -0.15564 | 0.16022 | 61.2167 | -61.4639 | -0.24262 | -0.004578 | -0.1831 | -0.07782 | -0.28381 | -0.26093 | 0.050354 | 0.05951 | 61.0474 | 61.3632 | 122.0856 | 122.3648 | -0.1831 | 122.4197 | 61.4136 | -0.26093 | 122.3648 | -0.1831 | 61.4136 | 122.0856 | 122.4197 | -122.612 | -122.6303
756.2656 | 122.6532 | -61.2762 | 61.1343 | -0.0055695 | 0.0055628 | 0.012249 | 0.029123 | 0.041644 | -0.033626 | 0.059703 | -61.4044 | 61.235 | -61.5005 | -61.3312 | 60.791 | 0.13275 | -0.013733 | 0.09613 | 61.2579 | -61.5097 | -0.2243 | 0.10071 | -0.12817 | -0.054932 | -0.34332 | -0.23346 | 0.1236 | 0.09613 | 61.2625 | 61.3724 | 122.0673 | 122.5113 | -0.12817 | 122.5342 | 61.409 | -0.23346 | 122.5113 | -0.12817 | 61.409 | 122.0673 | 122.5342 | -122.6349 | -122.644
757.9844 | 122.612 | -61.2717 | 61.1389 | 0.0096895 | 0.0036402 | 0.010754 | 0.030405 | 0.040362 | -0.03384 | 0.057781 | -61.3586 | 61.2625 | -61.4319 | -61.2488 | 60.878 | 0.21515 | 0.10529 | 0.23346 | 61.3083 | -61.4594 | -0.16022 | 0.1236 | -0.086976 | 0.022888 | -0.26093 | -0.18768 | 0.16937 | 0.073242 | 61.377 | 61.5051 | 122.1497 | 122.5342 | -0.086976 | 122.58 | 61.4868 | -0.18768 | 122.5342 | -0.086976 | 61.4868 | 122.1497 | 122.58 | -122.5708 | -122.5983
759.6875 | 122.7081 | -61.2991 | 61.0565 | 0.00206 | -0.00041862 | 0.011181 | 0.026987 | 0.041644 | -0.032985 | 0.062267 | -61.4594 | 61.1801 | -61.5234 | -61.3586 | 60.7956 | 0.10529 | -0.059509 | 0.068665 | 61.2396 | -61.5005 | -0.2243 | 0.1236 | -0.16022 | -0.05951 | -0.26093 | -0.20142 | 0.1831 | 0.064086 | 61.2396 | 61.3678 | 122.0947 | 122.4792 | -0.16022 | 122.5388 | 61.4044 | -0.20142 | 122.4792 | -0.16022 | 61.4044 | 122.0947 | 122.5388 | -122.58 | -122.5571
761.4688 | 122.6212 | -61.2671 | 61.1755 | 0.017319 | 0.0023584 | 0.013958 | 0.026346 | 0.041216 | -0.033199 | 0.060558 | -61.377 | 61.2534 | -61.4273 | -61.2717 | 60.878 | 0.21515 | 0.09613 | 0.21973 | 61.3403 | -61.4594 | -0.16022 | 0.07782 | -0.10986 | -0.004577 | -0.29755 | -0.19226 | 0.16479 | 0.050354 | 61.3632 | 61.4868 | 122.1451 | 122.5204 | -0.10986 | 122.6074 | 61.4822 | -0.19226 | 122.5204 | -0.10986 | 61.4822 | 122.1451 | 122.6074 | -122.6028 | -122.6349
763.1875 | 122.7036 | -61.2167 | 61.1664 | 0.017319 | -0.001914 | 0.0092585 | 0.023142 | 0.039935 | -0.033199 | 0.060771 | -61.3907 | 61.0886 | -61.4594 | -61.2854 | 60.8734 | 0.21057 | -0.20599 | 0.17395 | 61.1801 | -61.4685 | -0.24262 | -0.07782 | -0.17395 | -0.068664 | -0.29297 | -0.25177 | 0.013733 | 0.068665 | 61.0107 | 61.3907 | 122.0901 | 122.3053 | -0.17395 | 122.3969 | 61.4273 | -0.25177 | 122.3053 | -0.17395 | 61.4273 | 122.0901 | 122.3969 | -122.6257 | -122.6349
764.8906 | 122.7081 | -61.203 | 61.1755 | -0.0055695 | -0.00041862 | 0.011395 | 0.023569 | 0.040148 | -0.029781 | 0.058849 | -61.3724 | 61.1755 | -61.4044 | -61.2671 | 60.8871 | 0.21973 | -0.14191 | 0.17853 | 61.2442 | -61.4548 | -0.20142 | 0 | -0.16937 | -0.064087 | -0.28839 | -0.25177 | 0.068665 | 0.032044 | 61.0611 | 61.3815 | 122.0901 | 122.3785 | -0.16937 | 122.4472 | 61.4227 | -0.25177 | 122.3785 | -0.16937 | 61.4227 | 122.0901 | 122.4472 | -122.58 | -122.6303
766.6719 | 122.58 | -61.3083 | 61.1389 | 0.0096895 | 0.00086298 | 0.0094721 | 0.029978 | 0.040575 | -0.034694 | 0.060344 | -61.3541 | 61.203 | -61.4639 | -61.2305 | 60.878 | 0.24261 | -0.018311 | 0.24261 | 61.2717 | -61.4319 | -0.15564 | 0.064087 | -0.045776 | 0.07782 | -0.26093 | -0.1236 | 0.13275 | 0.10986 | 61.29 | 61.5509 | 122.1863 | 122.5113 | -0.045776 | 122.58 | 61.5509 | -0.1236 | 122.5113 | -0.045776 | 61.5509 | 122.1863 | 122.58 | -122.6028 | -122.5708
768.3906 | 122.6715 | -61.2671 | 61.1023 | 0.017319 | 0.001504 | 0.014385 | 0.027841 | 0.040575 | -0.031704 | 0.061412 | -61.4319 | 61.1526 | -61.4777 | -61.3312 | 60.8231 | 0.14648 | -0.17853 | 0.10529 | 61.1847 | -61.5005 | -0.21057 | 0.050354 | -0.16479 | -0.064087 | -0.27924 | -0.23346 | 0.082397 | 0.045776 | 61.0886 | 61.3724 | 122.0901 | 122.4197 | -0.16479 | 122.4518 | 61.4136 | -0.23346 | 122.4197 | -0.16479 | 61.4136 | 122.0901 | 122.4518 | -122.58 | -122.6028
770.1562 | 122.5433 | -61.2991 | 61.1572 | 0.0096895 | -0.00041862 | 0.0081903 | 0.029764 | 0.038439 | -0.034481 | 0.058422 | -61.3541 | 61.1938 | -61.4639 | -61.235 | 60.878 | 0.23804 | -0.004578 | 0.24261 | 61.2488 | -61.4548 | -0.1648 | 0.036621 | -0.054932 | 0.064087 | -0.27924 | -0.15564 | 0.091552 | 0.10986 | 61.2946 | 61.5417 | 122.1771 | 122.493 | -0.054932 | 122.5479 | 61.5372 | -0.15564 | 122.493 | -0.054932 | 61.5372 | 122.1771 | 122.5479 | -122.6212 | -122.612
771.9219 | 122.58 | -61.2946 | 61.171 | 0.00206 | 0.0055628 | 0.01054 | 0.028055 | 0.038653 | -0.031277 | 0.059062 | -61.3495 | 61.2579 | -61.4136 | -61.2396 | 60.91 | 0.24719 | 0.045776 | 0.21973 | 61.2717 | -61.4777 | -0.11902 | 0.086976 | -0.054931 | 0.054932 | -0.26093 | -0.1831 | 0.10071 | 0.064087 | 61.3403 | 61.5143 | 122.2046 | 122.5525 | -0.054931 | 122.5662 | 61.5417 | -0.1831 | 122.5525 | -0.054931 | 61.5417 | 122.2046 | 122.5662 | -122.5845 | -122.6486
773.7188 | 122.644 | -61.2808 | 61.1389 | 0.00206 | 0.0040674 | 0.011822 | 0.02421 | 0.039935 | -0.032131 | 0.059917 | -61.3632 | 61.1206 | -61.4594 | -61.2625 | 60.8963 | 0.22888 | -0.25177 | 0.17853 | 61.1572 | -61.5051 | -0.17853 | -0.018311 | -0.082397 | 0.018311 | -0.24262 | -0.2243 | 0.018311 | 0.096131 | 61.0291 | 61.4594 | 122.1771 | 122.4014 | -0.082397 | 122.4381 | 61.5097 | -0.2243 | 122.4014 | -0.082397 | 61.5097 | 122.1771 | 122.4381 | -122.5983 | -122.644
775.5 | 122.612 | -61.2213 | 61.1847 | 0.00206 | 0.00086298 | 0.0092585 | 0.025705 | 0.040362 | -0.032558 | 0.057781 | -61.3724 | 61.2762 | -61.3907 | -61.2717 | 60.8734 | 0.22888 | 0.1236 | 0.24261 | 61.3541 | -61.4182 | -0.16937 | 0.091553 | -0.15106 | -0.050354 | -0.31128 | -0.19684 | 0.16937 | 0.018311 | 61.3449 | 61.4639 | 122.0947 | 122.4976 | -0.15106 | 122.5754 | 61.4502 | -0.19684 | 122.4976 | -0.15106 | 61.4502 | 122.0947 | 122.5754 | -122.5754 | -122.6028
777.2031 | 122.5754 | -61.3083 | 61.1526 | 0.0096895 | 0.0019312 | 0.013104 | 0.030405 | 0.040362 | -0.034481 | 0.058422 | -61.3541 | 61.1893 | -61.4594 | -61.2396 | 60.8917 | 0.23346 | -0.018311 | 0.2243 | 61.2671 | -61.4365 | -0.15106 | 0.036621 | -0.045776 | 0.068665 | -0.26092 | -0.12817 | 0.11444 | 0.10529 | 61.29 | 61.5326 | 122.2 | 122.4976 | -0.045776 | 122.5754 | 61.5417 | -0.12817 | 122.4976 | -0.045776 | 61.5417 | 122.2 | 122.5754 | -122.612 | -122.5891
778.9844 | 122.7036 | -61.1847 | 61.1755 | -0.0055695 | 0.00064938 | 0.0090447 | 0.021433 | 0.036303 | -0.032131 | 0.059276 | -61.3861 | 61.1755 | -61.4227 | -61.2625 | 60.9055 | 0.23804 | -0.13733 | 0.20142 | 61.2167 | -61.4594 | -0.23804 | 0 | -0.20142 | -0.07782 | -0.27008 | -0.27466 | 0.041199 | 0.036621 | 61.0474 | 61.3861 | 122.0901 | 122.3602 | -0.20142 | 122.4014 | 61.4227 | -0.27466 | 122.3602 | -0.20142 | 61.4227 | 122.0901 | 122.4014 | -122.5983 | -122.6349
780.7656 | 122.5754 | -61.2946 | 61.1389 | 0.0096895 | 0.0034266 | 0.0098993 | 0.030618 | 0.041216 | -0.032985 | 0.059062 | -61.3678 | 61.1984 | -61.4594 | -61.2808 | 60.8368 | 0.19684 | -0.009155 | 0.16937 | 61.2259 | -61.4914 | -0.16479 | 0.059509 | -0.073242 | 0.013733 | -0.30212 | -0.19684 | 0.086975 | 0.091553 | 61.2854 | 61.4639 | 122.1313 | 122.493 | -0.073242 | 122.5204 | 61.4914 | -0.19684 | 122.493 | -0.073242 | 61.4914 | 122.1313 | 122.5204 | -122.5983 | -122.6303
782.5625 | 122.5754 | -61.235 | 61.2305 | -0.0055695 | 0.00086298 | 0.010113 | 0.022287 | 0.03673 | -0.032772 | 0.057994 | -61.2717 | 61.171 | -61.3953 | -61.1526 | 60.9924 | 0.33417 | -0.11444 | 0.32044 | 61.2534 | -61.4365 | -0.16022 | -0.05951 | -0.036621 | 0.082397 | -0.23804 | -0.20142 | 0.022888 | 0.1236 | 61.1206 | 61.5555 | 122.2275 | 122.406 | -0.036621 | 122.4884 | 61.5692 | -0.20142 | 122.406 | -0.036621 | 61.5692 | 122.2275 | 122.4884 | -122.6257 | -122.6669
784.2812 | 122.6807 | -61.2213 | 61.171 | 0.0096895 | 0.0019312 | 0.0081903 | 0.025064 | 0.039294 | -0.031063 | 0.058849 | -61.3678 | 61.1069 | -61.4365 | -61.2808 | 60.8688 | 0.21515 | -0.20142 | 0.17853 | 61.2076 | -61.4639 | -0.21515 | -0.064086 | -0.14648 | -0.05951 | -0.30212 | -0.24262 | 0.036622 | 0.068664 | 61.0199 | 61.3998 | 122.0901 | 122.3282 | -0.14648 | 122.4289 | 61.4365 | -0.24262 | 122.3282 | -0.14648 | 61.4365 | 122.0901 | 122.4289 | -122.6074 | -122.6349
786.0625 | 122.6669 | -61.2259 | 61.171 | 0.0096895 | 0.00064938 | 0.013531 | 0.02421 | 0.037371 | -0.032772 | 0.059062 | -61.3358 | 61.1023 | -61.4731 | -61.2808 | 60.8688 | 0.21057 | -0.23804 | 0.1831 | 61.1664 | -61.4685 | -0.24719 | -0.068664 | -0.10986 | -0.054932 | -0.30212 | -0.24262 | -0.004577 | 0.13733 | 60.9879 | 61.409 | 122.0947 | 122.3282 | -0.10986 | 122.3923 | 61.4365 | -0.24262 | 122.3282 | -0.10986 | 61.4365 | 122.0947 | 122.3923 | -122.644 | -122.6395
787.8281 | 122.6852 | -61.2991 | 61.0886 | 0.00206 | 0.00043578 | 0.010754 | 0.028696 | 0.038866 | -0.031704 | 0.060131 | -61.4456 | 61.1526 | -61.5234 | -61.3495 | 60.7636 | 0.10986 | -0.054932 | 0.082397 | 61.2579 | -61.4822 | -0.2243 | 0.064087 | -0.14649 | -0.050354 | -0.32501 | -0.18311 | 0.16937 | 0.077819 | 61.2442 | 61.3815 | 122.0627 | 122.4518 | -0.14649 | 122.5571 | 61.409 | -0.18311 | 122.4518 | -0.14649 | 61.409 | 122.0627 | 122.5571 | -122.612 | -122.5708
789.6094 | 122.7081 | -61.1984 | 61.1572 | -0.013199 | 0.002572 | 0.013744 | 0.025064 | 0.040148 | -0.032345 | 0.058635 | -61.3403 | 61.1664 | -61.4182 | -61.2534 | 60.8826 | 0.21057 | -0.14648 | 0.16479 | 61.235 | -61.4685 | -0.21973 | 0.009155 | -0.14191 | -0.054932 | -0.27466 | -0.27008 | 0.077819 | 0.07782 | 61.0519 | 61.3632 | 122.081 | 122.3648 | -0.14191 | 122.4335 | 61.409 | -0.27008 | 122.3648 | -0.14191 | 61.409 | 122.081 | 122.4335 | -122.5754 | -122.6257
791.3281 | 122.6624 | -61.1847 | 61.1938 | -0.0055695 | 0.0032128 | 0.011395 | 0.023142 | 0.038653 | -0.033199 | 0.059062 | -61.3312 | 61.1847 | -61.4044 | -61.2076 | 60.9375 | 0.27924 | -0.10986 | 0.25177 | 61.2579 | -61.4365 | -0.21973 | -0.009156 | -0.14648 | -0.022889 | -0.25635 | -0.25177 | 0.064087 | 0.073242 | 61.0748 | 61.4365 | 122.1222 | 122.3694 | -0.14648 | 122.4426 | 61.4639 | -0.25177 | 122.3694 | -0.14648 | 61.4639 | 122.1222 | 122.4426 | -122.5983 | -122.6303
793.1094 | 122.5891 | -61.2991 | 61.1298 | -0.013199 | 0.0036402 | 0.01289 | 0.031259 | 0.039294 | -0.035976 | 0.060558 | -61.377 | 61.1664 | -61.4685 | -61.2946 | 60.8139 | 0.16022 | -0.018311 | 0.14648 | 61.2488 | -61.4594 | -0.16937 | 0.036621 | -0.07782 | 0.004577 | -0.31586 | -0.16022 | 0.11902 | 0.091553 | 61.2808 | 61.4456 | 122.113 | 122.4655 | -0.07782 | 122.5479 | 61.4594 | -0.16022 | 122.4655 | -0.07782 | 61.4594 | 122.113 | 122.5479 | -122.5983 | -122.5891
794.8906 | 122.5616 | -61.2442 | 61.1664 | 0.00206 | 0.0029992 | 0.010967 | 0.027628 | 0.042071 | -0.033199 | 0.057781 | -61.3541 | 61.2259 | -61.4227 | -61.2579 | 60.8643 | 0.21057 | 0.11444 | 0.21057 | 61.3174 | -61.4548 | -0.17853 | 0.059509 | -0.10986 | -0.013733 | -0.30212 | -0.21057 | 0.15106 | 0.068664 | 61.3586 | 61.4548 | 122.1085 | 122.4701 | -0.10986 | 122.5616 | 61.4548 | -0.21057 | 122.4701 | -0.10986 | 61.4548 | 122.1085 | 122.5616 | -122.5891 | -122.6212
796.6562 | 122.5616 | -61.2717 | 61.2213 | -0.0055695 | 0.0023584 | 0.011395 | 0.023996 | 0.038653 | -0.031917 | 0.059917 | -61.2717 | 61.2122 | -61.3678 | -61.1526 | 60.9604 | 0.32501 | -0.054932 | 0.32959 | 61.2442 | -61.3907 | -0.096131 | -0.009155 | 0 | 0.11902 | -0.26093 | -0.11902 | 0.022889 | 0.096131 | 61.2167 | 61.6013 | 122.2321 | 122.4838 | 0 | 122.5159 | 61.5967 | -0.11902 | 122.4838 | 0 | 61.5967 | 122.2321 | 122.5159 | -122.5891 | -122.612
798.4219 | 122.5616 | -61.2259 | 61.235 | 0.0096895 | 0.0017176 | 0.012249 | 0.023996 | 0.041216 | -0.033413 | 0.05714 | -61.2579 | 61.2076 | -61.3724 | -61.1618 | 60.9879 | 0.33875 | -0.10071 | 0.32501 | 61.2625 | -61.4273 | -0.14648 | -0.027465 | -0.032044 | 0.064087 | -0.24719 | -0.20142 | 0.027466 | 0.11444 | 61.1252 | 61.5509 | 122.2137 | 122.4335 | -0.032044 | 122.4884 | 61.5646 | -0.20142 | 122.4335 | -0.032044 | 61.5646 | 122.2137 | 122.4884 | -122.6074 | -122.6624
800.1406 | 122.6715 | -61.2854 | 61.0931 | 0.00206 | 0.0023584 | 0.012676 | 0.028482 | 0.040575 | -0.03384 | 0.057353 | -61.4502 | 61.1664 | -61.496 | -61.3586 | 60.759 | 0.10986 | -0.036621 | 0.086975 | 61.2488 | -61.5005 | -0.21057 | 0.073242 | -0.16479 | -0.073243 | -0.33417 | -0.21515 | 0.15564 | 0.045777 | 61.2488 | 61.3724 | 122.0444 | 122.4518 | -0.16479 | 122.5342 | 61.3953 | -0.21515 | 122.4518 | -0.16479 | 61.3953 | 122.0444 | 122.5342 | -122.5891 | -122.5937
801.9219 | 122.5479 | -61.2259 | 61.2122 | 0.0096895 | -0.0012732 | 0.010113 | 0.022501 | 0.039721 | -0.033626 | 0.056926 | -61.2762 | 61.1893 | -61.3678 | -61.1572 | 60.9695 | 0.32959 | -0.073242 | 0.33417 | 61.2396 | -61.409 | -0.14191 | -0.022888 | -0.050354 | 0.068664 | -0.24262 | -0.18311 | 0.027466 | 0.091553 | 61.1526 | 61.5601 | 122.1954 | 122.4152 | -0.050354 | 122.4655 | 61.5555 | -0.18311 | 122.4152 | -0.050354 | 61.5555 | 122.1954 | 122.4655 | -122.58 | -122.6212
803.7031 | 122.6715 | -61.2122 | 61.1618 | 0.00206 | 0.0010766 | 0.0084039 | 0.025919 | 0.03908 | -0.032131 | 0.059703 | -61.3541 | 61.1572 | -61.4319 | -61.2625 | 60.8826 | 0.21057 | -0.16479 | 0.17395 | 61.2488 | -61.4594 | -0.21973 | -0.004577 | -0.14191 | -0.050354 | -0.27924 | -0.24719 | 0.086975 | 0.07782 | 61.0474 | 61.3861 | 122.0947 | 122.3694 | -0.14191 | 122.4609 | 61.4227 | -0.24719 | 122.3694 | -0.14191 | 61.4227 | 122.0947 | 122.4609 | -122.5937 | -122.6212
805.4844 | 122.6028 | -61.3312 | 61.1114 | 0.0096895 | 0.0019312 | 0.015026 | 0.030832 | 0.04143 | -0.033626 | 0.058635 | -61.409 | 61.1801 | -61.5051 | -61.322 | 60.7819 | 0.15106 | -0.013733 | 0.11902 | 61.2167 | -61.4777 | -0.17395 | 0.068665 | -0.07782 | 0.009156 | -0.32959 | -0.14648 | 0.10529 | 0.09613 | 61.3174 | 61.4502 | 122.113 | 122.5113 | -0.07782 | 122.5479 | 61.4822 | -0.14648 | 122.5113 | -0.07782 | 61.4822 | 122.113 | 122.5479 | -122.6166 | -122.5891
807.1875 | 122.6807 | -61.2442 | 61.0977 | 0.00206 | 0.00043578 | 0.0098993 | 0.027414 | 0.040575 | -0.031063 | 0.05949 | -61.4456 | 61.1298 | -61.5005 | -61.3541 | 60.759 | 0.11444 | -0.050354 | 0.064087 | 61.235 | -61.5051 | -0.25635 | 0.032044 | -0.20142 | -0.10986 | -0.33875 | -0.26093 | 0.13733 | 0.054931 | 61.1938 | 61.3083 | 122.0032 | 122.374 | -0.20142 | 122.4792 | 61.3586 | -0.26093 | 122.374 | -0.20142 | 61.3586 | 122.0032 | 122.4792 | -122.5983 | -122.6028
808.9531 | 122.6715 | -61.203 | 61.1481 | 0.0096895 | 0.0032128 | 0.010326 | 0.022928 | 0.038653 | -0.030636 | 0.05714 | -61.3724 | 61.1343 | -61.4365 | -61.2579 | 60.878 | 0.21057 | -0.16479 | 0.16022 | 61.1847 | -61.4639 | -0.23346 | -0.013733 | -0.16937 | -0.054932 | -0.27008 | -0.26093 | 0.036621 | 0.064087 | 61.0382 | 61.3632 | 122.081 | 122.3373 | -0.16937 | 122.3877 | 61.4136 | -0.26093 | 122.3373 | -0.16937 | 61.4136 | 122.081 | 122.3877 | -122.5845 | -122.612
810.6719 | 122.6532 | -61.2213 | 61.1618 | 0.0096895 | -0.0014868 | 0.013104 | 0.025278 | 0.03908 | -0.031917 | 0.059917 | -61.3312 | 61.1298 | -61.4639 | -61.2488 | 60.8643 | 0.20599 | -0.25177 | 0.1831 | 61.1755 | -61.4456 | -0.24262 | -0.032043 | -0.10986 | -0.027466 | -0.29755 | -0.22431 | 0.013733 | 0.13275 | 60.9695 | 61.4044 | 122.0856 | 122.3511 | -0.10986 | 122.3969 | 61.4273 | -0.22431 | 122.3511 | -0.10986 | 61.4273 | 122.0856 | 122.3969 | -122.6257 | -122.6074
812.375 | 122.6624 | -61.2579 | 61.0748 | 0.00206 | 0.0040674 | 0.013958 | 0.029123 | 0.040362 | -0.034694 | 0.059276 | -61.4456 | 61.1389 | -61.4914 | -61.3358 | 60.7681 | 0.10986 | -0.041199 | 0.059509 | 61.2534 | -61.496 | -0.23346 | 0.064087 | -0.18768 | -0.077819 | -0.3067 | -0.23804 | 0.17853 | 0.045776 | 61.2167 | 61.3174 | 122.0261 | 122.3969 | -0.18768 | 122.5113 | 61.3678 | -0.23804 | 122.3969 | -0.18768 | 61.3678 | 122.0261 | 122.5113 | -122.5662 | -122.5708
814.1094 | 122.6807 | -61.2717 | 61.0748 | 0.00206 | 0.0017176 | 0.0098993 | 0.029123 | 0.040789 | -0.032772 | 0.058208 | -61.4365 | 61.171 | -61.4685 | -61.3449 | 60.7681 | 0.11902 | -0.050354 | 0.059509 | 61.2488 | -61.5005 | -0.19684 | 0.09613 | -0.16479 | -0.073243 | -0.3067 | -0.22888 | 0.17395 | 0.032044 | 61.2213 | 61.3312 | 122.0398 | 122.4426 | -0.16479 | 122.5204 | 61.3907 | -0.22888 | 122.4426 | -0.16479 | 61.3907 | 122.0398 | 122.5204 | -122.5433 | -122.5754
815.8281 | 122.6303 | -61.2579 | 61.1069 | 0.0096895 | 0.0019312 | 0.012249 | 0.027841 | 0.04143 | -0.031277 | 0.062053 | -61.4182 | 61.1389 | -61.4868 | -61.322 | 60.8002 | 0.15564 | -0.15564 | 0.10986 | 61.2167 | -61.4777 | -0.22888 | 0.032043 | -0.16022 | -0.064086 | -0.3067 | -0.21973 | 0.10986 | 0.068664 | 61.1023 | 61.3678 | 122.0581 | 122.3969 | -0.16022 | 122.4747 | 61.4136 | -0.21973 | 122.3969 | -0.16022 | 61.4136 | 122.0581 | 122.4747 | -122.5937 | -122.5845
817.5469 | 122.6807 | -61.1938 | 61.1481 | -0.0055695 | 0.0034266 | 0.012463 | 0.021219 | 0.039721 | -0.032985 | 0.058422 | -61.3586 | 61.1481 | -61.4044 | -61.2579 | 60.8688 | 0.21515 | -0.14648 | 0.16022 | 61.2396 | -61.4548 | -0.21057 | 0 | -0.16479 | -0.064087 | -0.27924 | -0.26093 | 0.091553 | 0.045776 | 61.0474 | 61.3541 | 122.0627 | 122.3419 | -0.16479 | 122.4335 | 61.409 | -0.26093 | 122.3419 | -0.16479 | 61.409 | 122.0627 | 122.4335 | -122.5525 | -122.6028
819.2656 | 122.6761 | -61.2762 | 61.0657 | 0.00206 | 0.0012902 | 0.011181 | 0.031046 | 0.038012 | -0.032131 | 0.058422 | -61.4365 | 61.1343 | -61.4868 | -61.3312 | 60.7681 | 0.11444 | -0.054932 | 0.059509 | 61.2442 | -61.4685 | -0.21057 | 0.068664 | -0.16022 | -0.054932 | -0.29755 | -0.19226 | 0.17853 | 0.050354 | 61.2213 | 61.3358 | 122.0444 | 122.4106 | -0.16022 | 122.5204 | 61.3907 | -0.19226 | 122.4106 | -0.16022 | 61.3907 | 122.0444 | 122.5204 | -122.5525 | -122.5342
821.0469 | 122.5754 | -61.2305 | 61.1618 | 0.0096895 | 0.0029992 | 0.0077631 | 0.026987 | 0.038653 | -0.030422 | 0.058208 | -61.3358 | 61.2396 | -61.3907 | -61.2396 | 60.8734 | 0.21973 | 0.091553 | 0.23346 | 61.2854 | -61.4456 | -0.16022 | 0.07782 | -0.10529 | -0.009155 | -0.28839 | -0.21515 | 0.1236 | 0.054932 | 61.322 | 61.4639 | 122.1039 | 122.4701 | -0.10529 | 122.5159 | 61.4502 | -0.21515 | 122.4701 | -0.10529 | 61.4502 | 122.1039 | 122.5159 | -122.5525 | -122.6074
822.8125 | 122.5525 | -61.2213 | 61.1755 | 0.00206 | 0.0029992 | 0.012463 | 0.026346 | 0.038866 | -0.03149 | 0.057994 | -61.2808 | 61.2167 | -61.3815 | -61.1664 | 60.9512 | 0.32044 | -0.013733 | 0.33417 | 61.2534 | -61.4365 | -0.16022 | 0.041199 | -0.05951 | 0.054931 | -0.2243 | -0.21515 | 0.07782 | 0.10071 | 61.2076 | 61.5555 | 122.1725 | 122.438 | -0.05951 | 122.4747 | 61.5417 | -0.21515 | 122.438 | -0.05951 | 61.5417 | 122.1725 | 122.4747 | -122.5571 | -122.612
824.5938 | 122.612 | -61.2167 | 61.1389 | 0.0096895 | 0.001504 | 0.013531 | 0.026987 | 0.038226 | -0.032772 | 0.059276 | -61.3312 | 61.116 | -61.4639 | -61.2579 | 60.8505 | 0.21057 | -0.25635 | 0.17853 | 61.1664 | -61.4548 | -0.24719 | -0.022888 | -0.11444 | -0.041199 | -0.28839 | -0.23804 | 0.027466 | 0.13275 | 60.9604 | 61.3953 | 122.0673 | 122.3328 | -0.11444 | 122.3831 | 61.4273 | -0.23804 | 122.3328 | -0.11444 | 61.4273 | 122.0673 | 122.3831 | -122.6028 | -122.5937
826.375 | 122.5433 | -61.2762 | 61.1526 | 0.00206 | 0.0012902 | 0.0090447 | 0.030832 | 0.039294 | -0.034694 | 0.05949 | -61.3358 | 61.1801 | -61.441 | -61.2259 | 60.8734 | 0.25635 | 0.022888 | 0.23346 | 61.2579 | -61.4182 | -0.16479 | 0.027466 | -0.059509 | 0.050354 | -0.27924 | -0.14191 | 0.10529 | 0.10529 | 61.2991 | 61.5097 | 122.1497 | 122.4564 | -0.059509 | 122.5342 | 61.5326 | -0.14191 | 122.4564 | -0.059509 | 61.5326 | 122.1497 | 122.5342 | -122.5937 | -122.5708
828.0938 | 122.5845 | -61.2396 | 61.1664 | -0.0055695 | 0.00043578 | 0.011608 | 0.02656 | 0.038012 | -0.033626 | 0.059062 | -61.3449 | 61.2534 | -61.3724 | -61.2442 | 60.8734 | 0.22888 | 0.15106 | 0.25177 | 61.3266 | -61.4227 | -0.13275 | 0.086975 | -0.10529 | -0.004578 | -0.29297 | -0.1831 | 0.16022 | 0.027465 | 61.3907 | 61.4914 | 122.113 | 122.493 | -0.10529 | 122.5662 | 61.4685 | -0.1831 | 122.493 | -0.10529 | 61.4685 | 122.113 | 122.5662 | -122.5388 | -122.5891
829.8594 | 122.5204 | -61.2076 | 61.2259 | 0.00206 | -0.00020502 | 0.01289 | 0.020578 | 0.038653 | -0.032558 | 0.059276 | -61.2625 | 61.2076 | -61.3586 | -61.1389 | 60.9695 | 0.33417 | -0.091553 | 0.33875 | 61.2259 | -61.409 | -0.15106 | -0.01831 | -0.054931 | 0.068665 | -0.25635 | -0.20142 | 0 | 0.096131 | 61.116 | 61.5463 | 122.1771 | 122.4152 | -0.054931 | 122.4335 | 61.5417 | -0.20142 | 122.4152 | -0.054931 | 61.5417 | 122.1771 | 122.4335 | -122.5845 | -122.6349
831.6406 | 122.6349 | -61.2213 | 61.1526 | 0.0096895 | 0.0012902 | 0.012463 | 0.023996 | 0.03908 | -0.031917 | 0.05949 | -61.3266 | 61.1114 | -61.4456 | -61.235 | 60.8597 | 0.21973 | -0.25635 | 0.17395 | 61.1572 | -61.4731 | -0.22431 | -0.041199 | -0.10529 | -0.013733 | -0.29297 | -0.25177 | 0.004578 | 0.11902 | 60.965 | 61.3953 | 122.081 | 122.3328 | -0.10529 | 122.3785 | 61.441 | -0.25177 | 122.3328 | -0.10529 | 61.441 | 122.081 | 122.3785 | -122.5983 | -122.6257
833.4062 | 122.6578 | -61.2442 | 61.0886 | 0.0096895 | 0.0027856 | 0.014385 | 0.02891 | 0.041216 | -0.035122 | 0.060131 | -61.4182 | 61.1481 | -61.4914 | -61.3129 | 60.759 | 0.10986 | -0.082397 | 0.082397 | 61.235 | -61.4685 | -0.24719 | 0.059509 | -0.17395 | -0.068664 | -0.32959 | -0.2243 | 0.14648 | 0.073242 | 61.1618 | 61.3266 | 122.0032 | 122.3923 | -0.17395 | 122.4792 | 61.3541 | -0.2243 | 122.3923 | -0.17395 | 61.3541 | 122.0032 | 122.4792 | -122.58 | -122.5571
835.1094 | 122.5708 | -61.2442 | 61.1847 | -0.0055695 | 0.0019312 | 0.010326 | 0.026346 | 0.039507 | -0.032131 | 0.056926 | -61.2946 | 61.235 | -61.3678 | -61.2213 | 60.9055 | 0.24719 | 0.07782 | 0.25635 | 61.2991 | -61.4365 | -0.1236 | 0.050354 | -0.050354 | 0.022889 | -0.27923 | -0.19226 | 0.11444 | 0.073242 | 61.322 | 61.5006 | 122.1497 | 122.4792 | -0.050354 | 122.5433 | 61.4914 | -0.19226 | 122.4792 | -0.050354 | 61.4914 | 122.1497 | 122.5433 | -122.5525 | -122.6212
836.8906 | 122.6852 | -61.1801 | 61.1481 | 0.00206 | 0.00043578 | 0.013744 | 0.021433 | 0.038012 | -0.032772 | 0.059062 | -61.3541 | 61.1526 | -61.4044 | -61.2442 | 60.8597 | 0.21973 | -0.15564 | 0.15106 | 61.1984 | -61.4319 | -0.2243 | 0.004578 | -0.17395 | -0.064087 | -0.28839 | -0.25177 | 0.050354 | 0.050354 | 61.0245 | 61.3312 | 122.0398 | 122.3328 | -0.17395 | 122.3785 | 61.3998 | -0.25177 | 122.3328 | -0.17395 | 61.3998 | 122.0398 | 122.3785 | -122.5525 | -122.58
838.6094 | 122.6761 | -61.1984 | 61.1252 | 0.0096895 | 8.578e-06 | 0.0096857 | 0.024851 | 0.038012 | -0.032131 | 0.060131 | -61.3586 | 61.1343 | -61.4227 | -61.2488 | 60.8551 | 0.2243 | -0.17395 | 0.16479 | 61.2259 | -61.4548 | -0.2243 | 0.009155 | -0.16022 | -0.050354 | -0.27008 | -0.25635 | 0.10071 | 0.064086 | 61.0245 | 61.3632 | 122.0535 | 122.3328 | -0.16022 | 122.4243 | 61.4227 | -0.25635 | 122.3328 | -0.16022 | 61.4227 | 122.0535 | 122.4243 | -122.5479 | -122.58
840.3125 | 122.5662 | -61.2305 | 61.1526 | 0.017319 | 0.0034266 | 0.012676 | 0.02955 | 0.039721 | -0.034694 | 0.058635 | -61.3449 | 61.2396 | -61.4182 | -61.2396 | 60.8688 | 0.24261 | 0.10529 | 0.2243 | 61.29 | -61.441 | -0.18768 | 0.086975 | -0.11444 | -0.009155 | -0.28381 | -0.21057 | 0.13733 | 0.073242 | 61.3358 | 61.4548 | 122.0993 | 122.4701 | -0.11444 | 122.5204 | 61.4731 | -0.21057 | 122.4701 | -0.11444 | 61.4731 | 122.0993 | 122.5204 | -122.5708 | -122.5937
842.0312 | 122.5983 | -61.2534 | 61.1389 | -0.0055695 | 0.0017176 | 0.010754 | 0.026346 | 0.03908 | -0.031063 | 0.057567 | -61.3312 | 61.0794 | -61.441 | -61.235 | 60.8643 | 0.23804 | -0.28381 | 0.19684 | 61.1572 | -61.4548 | -0.18768 | -0.059509 | -0.07782 | 0.018311 | -0.27466 | -0.20142 | 0.018311 | 0.10986 | 60.9695 | 61.4502 | 122.1176 | 122.3328 | -0.07782 | 122.4106 | 61.4914 | -0.20142 | 122.3328 | -0.07782 | 61.4914 | 122.1176 | 122.4106 | -122.58 | -122.5937
843.8125 | 122.5845 | -61.2808 | 61.1023 | 0.017319 | 0.0023584 | 0.014813 | 0.030832 | 0.040575 | -0.034694 | 0.060771 | -61.3953 | 61.171 | -61.4868 | -61.2991 | 60.7864 | 0.13733 | -0.018311 | 0.11444 | 61.2396 | -61.4639 | -0.20599 | 0.068664 | -0.11444 | -0.01831 | -0.31586 | -0.18311 | 0.13733 | 0.091552 | 61.2625 | 61.3953 | 122.0673 | 122.4518 | -0.11444 | 122.5204 | 61.4182 | -0.18311 | 122.4518 | -0.11444 | 61.4182 | 122.0673 | 122.5204 | -122.5891 | -122.5662
845.6094 | 122.6486 | -61.2625 | 61.0565 | 0.00206 | 0.0029992 | 0.01289 | 0.028696 | 0.040362 | -0.034054 | 0.058635 | -61.4502 | 61.1526 | -61.5051 | -61.3449 | 60.7498 | 0.11444 | -0.041199 | 0.07782 | 61.2076 | -61.4777 | -0.24262 | 0.09613 | -0.18768 | -0.082398 | -0.3067 | -0.21515 | 0.15106 | 0.054932 | 61.2213 | 61.3403 | 122.0123 | 122.4152 | -0.18768 | 122.4701 | 61.377 | -0.21515 | 122.4152 | -0.18768 | 61.377 | 122.0123 | 122.4701 | -122.5616 | -122.5342
847.3125 | 122.6486 | -61.1893 | 61.1435 | 0.0096895 | 0.0023584 | 0.010326 | 0.020151 | 0.03908 | -0.032558 | 0.058635 | -61.3495 | 61.1343 | -61.4044 | -61.2442 | 60.8734 | 0.21057 | -0.16937 | 0.17853 | 61.2167 | -61.4227 | -0.21515 | -0.009156 | -0.16022 | -0.054932 | -0.27008 | -0.23346 | 0.073242 | 0.054932 | 61.0199 | 61.3678 | 122.0627 | 122.3236 | -0.16022 | 122.406 | 61.3998 | -0.23346 | 122.3236 | -0.16022 | 61.3998 | 122.0627 | 122.406 | -122.5479 | -122.5662
849.0938 | 122.5479 | -61.2122 | 61.1664 | 0.0096895 | 0.00022218 | 0.0096857 | 0.025278 | 0.03908 | -0.032131 | 0.058635 | -61.2671 | 61.203 | -61.3678 | -61.1572 | 60.91 | 0.28381 | 0.018311 | 0.28381 | 61.2808 | -61.3953 | -0.15564 | 0.036621 | -0.054932 | 0.054931 | -0.25635 | -0.18311 | 0.11444 | 0.10071 | 61.2305 | 61.496 | 122.1222 | 122.4152 | -0.054932 | 122.493 | 61.496 | -0.18311 | 122.4152 | -0.054932 | 61.496 | 122.1222 | 122.493 | -122.5342 | -122.5616
850.875 | 122.6212 | -61.203 | 61.1023 | 0.00206 | -0.00084602 | 0.0094721 | 0.024637 | 0.040789 | -0.03384 | 0.057994 | -61.3083 | 61.0794 | -61.4182 | -61.2213 | 60.878 | 0.24261 | -0.2655 | 0.19684 | 61.1893 | -61.4182 | -0.21515 | -0.022888 | -0.10529 | -0.01831 | -0.2243 | -0.21515 | 0.086975 | 0.10986 | 60.9375 | 61.3998 | 122.081 | 122.2824 | -0.10529 | 122.3923 | 61.4456 | -0.21515 | 122.2824 | -0.10529 | 61.4456 | 122.081 | 122.3923 | -122.5204 | -122.5204
852.6406 | 122.5937 | -61.2396 | 61.1206 | 0.0096895 | 0.00064938 | 0.013958 | 0.026773 | 0.042925 | -0.035763 | 0.060985 | -61.3358 | 61.0794 | -61.4594 | -61.2305 | 60.8734 | 0.23346 | -0.28381 | 0.21057 | 61.1664 | -61.4273 | -0.21973 | -0.041198 | -0.09613 | 0.009155 | -0.24719 | -0.18768 | 0.045777 | 0.1236 | 60.9558 | 61.4502 | 122.113 | 122.319 | -0.09613 | 122.406 | 61.4731 | -0.18768 | 122.319 | -0.09613 | 61.4731 | 122.113 | 122.406 | -122.58 | -122.5479
854.3594 | 122.5754 | -61.203 | 61.1801 | 0.00206 | 0.00064938 | 0.010754 | 0.026346 | 0.040148 | -0.033626 | 0.060131 | -61.3358 | 61.2167 | -61.3907 | -61.2213 | 60.8643 | 0.2243 | 0.10529 | 0.23804 | 61.3358 | -61.377 | -0.18768 | 0.036621 | -0.13275 | -0.01831 | -0.31586 | -0.17395 | 0.15564 | 0.054932 | 61.3083 | 61.441 | 122.0673 | 122.4197 | -0.13275 | 122.5388 | 61.4273 | -0.17395 | 122.4197 | -0.13275 | 61.4273 | 122.0673 | 122.5388 | -122.5708 | -122.5571
856.1719 | 122.525 | -61.2717 | 61.1526 | 0.0096895 | 8.578e-06 | 0.011181 | 0.029337 | 0.038653 | -0.034481 | 0.057781 | -61.3266 | 61.2122 | -61.3953 | -61.2076 | 60.8597 | 0.24261 | 0.041199 | 0.22888 | 61.2396 | -61.4227 | -0.1236 | 0.059509 | -0.054932 | 0.064086 | -0.29297 | -0.15106 | 0.086975 | 0.068665 | 61.3129 | 61.5005 | 122.1313 | 122.4838 | -0.054932 | 122.5113 | 61.5143 | -0.15106 | 122.4838 | -0.054932 | 61.5143 | 122.1313 | 122.5113 | -122.5479 | -122.5754
857.875 | 122.5113 | -61.2671 | 61.1389 | 0.0096895 | 0.0019312 | 0.0056269 | 0.027841 | 0.037585 | -0.034267 | 0.059703 | -61.3358 | 61.2076 | -61.4182 | -61.2167 | 60.8688 | 0.25177 | 0.041199 | 0.24261 | 61.2625 | -61.4273 | -0.15106 | 0.068665 | -0.068664 | 0.050354 | -0.27008 | -0.16022 | 0.1236 | 0.082398 | 61.3083 | 61.5097 | 122.1359 | 122.4747 | -0.068664 | 122.5296 | 61.5189 | -0.16022 | 122.4747 | -0.068664 | 61.5189 | 122.1359 | 122.5296 | -122.5571 | -122.5662
859.6406 | 122.644 | -61.2534 | 61.0611 | 0.00206 | 0.0032128 | 0.011608 | 0.026346 | 0.040789 | -0.032772 | 0.060771 | -61.4182 | 61.116 | -61.4731 | -61.322 | 60.7773 | 0.12817 | -0.082397 | 0.086975 | 61.2122 | -61.4639 | -0.21973 | 0.054932 | -0.16479 | -0.068664 | -0.28381 | -0.21057 | 0.15106 | 0.054931 | 61.171 | 61.3403 | 122.0306 | 122.3694 | -0.16479 | 122.4655 | 61.3815 | -0.21057 | 122.3694 | -0.16479 | 61.3815 | 122.0306 | 122.4655 | -122.5342 | -122.525
861.3594 | 122.5204 | -61.2579 | 61.1206 | 0.0096895 | 0.0019312 | 0.0098993 | 0.027414 | 0.039721 | -0.034481 | 0.060558 | -61.3449 | 61.1755 | -61.4227 | -61.2534 | 60.8231 | 0.21057 | -0.018311 | 0.17395 | 61.2167 | -61.4777 | -0.16479 | 0.054932 | -0.086975 | 0.004578 | -0.29755 | -0.21973 | 0.096131 | 0.077819 | 61.2396 | 61.4319 | 122.081 | 122.4335 | -0.086975 | 122.4747 | 61.4685 | -0.21973 | 122.4335 | -0.086975 | 61.4685 | 122.081 | 122.4747 | -122.5433 | -122.5983
863.125 | 122.5616 | -61.2625 | 61.1114 | 0.0096895 | 0.004281 | 0.014385 | 0.027628 | 0.039721 | -0.032772 | 0.060558 | -61.3724 | 61.1343 | -61.4594 | -61.2991 | 60.7864 | 0.15106 | -0.009155 | 0.11902 | 61.2259 | -61.4639 | -0.19684 | 0.022888 | -0.10986 | -0.036621 | -0.32501 | -0.20142 | 0.11444 | 0.086976 | 61.2534 | 61.3815 | 122.0489 | 122.3969 | -0.10986 | 122.4884 | 61.4136 | -0.20142 | 122.3969 | -0.10986 | 61.4136 | 122.0489 | 122.4884 | -122.5708 | -122.5754
864.9062 | 122.5159 | -61.2305 | 61.1938 | 0.00206 | 0.0034266 | 0.0079767 | 0.021646 | 0.039507 | -0.031063 | 0.05949 | -61.235 | 61.1755 | -61.322 | -61.1343 | 60.9787 | 0.36163 | -0.1236 | 0.33417 | 61.2442 | -61.3632 | -0.091552 | -0.018311 | -0.004577 | 0.096131 | -0.21515 | -0.13275 | 0.050354 | 0.086975 | 61.1069 | 61.5646 | 122.2092 | 122.406 | -0.004577 | 122.4747 | 61.5921 | -0.13275 | 122.406 | -0.004577 | 61.5921 | 122.2092 | 122.4747 | -122.5159 | -122.5571
866.625 | 122.5296 | -61.2946 | 61.116 | 0.0096895 | 0.0027856 | 0.015667 | 0.028696 | 0.041003 | -0.035976 | 0.058422 | -61.3266 | 61.1664 | -61.4319 | -61.235 | 60.8368 | 0.2243 | -0.032043 | 0.19226 | 61.2671 | -61.4273 | -0.13733 | 0.050354 | -0.032043 | 0.05951 | -0.27924 | -0.13275 | 0.15106 | 0.10529 | 61.2625 | 61.4868 | 122.1313 | 122.4609 | -0.032043 | 122.5616 | 61.5189 | -0.13275 | 122.4609 | -0.032043 | 61.5189 | 122.1313 | 122.5616 | -122.5479 | -122.5433
868.3281 | 122.5021 | -61.2671 | 61.1481 | 0.017319 | 0.00086298 | 0.015026 | 0.026773 | 0.040148 | -0.031063 | 0.05949 | -61.3358 | 61.1847 | -61.4044 | -61.2076 | 60.8734 | 0.24719 | 0.004578 | 0.23804 | 61.2396 | -61.4319 | -0.13733 | 0.036621 | -0.068664 | 0.059509 | -0.27466 | -0.16479 | 0.091553 | 0.068665 | 61.2717 | 61.5051 | 122.1405 | 122.4518 | -0.068664 | 122.5067 | 61.5143 | -0.16479 | 122.4518 | -0.068664 | 61.5143 | 122.1405 | 122.5067 | -122.5525 | -122.58
870.1094 | 122.5845 | -61.2167 | 61.1206 | 0.0096895 | 0.0036402 | 0.013531 | 0.026346 | 0.039935 | -0.02914 | 0.060131 | -61.3266 | 61.1206 | -61.3998 | -61.2259 | 60.8551 | 0.20142 | -0.24261 | 0.17395 | 61.1893 | -61.4456 | -0.18311 | 0 | -0.10986 | -0.009155 | -0.2655 | -0.22888 | 0.068665 | 0.073242 | 60.9741 | 61.3907 | 122.0718 | 122.3373 | -0.10986 | 122.406 | 61.4182 | -0.22888 | 122.3373 | -0.10986 | 61.4182 | 122.0718 | 122.406 | -122.5204 | -122.5662
871.8906 | 122.6028 | -61.2259 | 61.116 | 0.0096895 | 0.0032128 | 0.01054 | 0.023996 | 0.039935 | -0.032772 | 0.058849 | -61.3403 | 61.1114 | -61.4365 | -61.2442 | 60.8231 | 0.21973 | -0.24261 | 0.16937 | 61.171 | -61.441 | -0.21057 | -0.004578 | -0.11444 | -0.018311 | -0.29297 | -0.21515 | 0.054931 | 0.09613 | 60.9833 | 61.3953 | 122.0489 | 122.3373 | -0.11444 | 122.3969 | 61.4456 | -0.21515 | 122.3373 | -0.11444 | 61.4456 | 122.0489 | 122.3969 | -122.5525 | -122.5571
873.6875 | 122.4838 | -61.2762 | 61.1298 | 0.00206 | 0.0012902 | 0.014172 | 0.026773 | 0.039935 | -0.035763 | 0.059703 | -61.3266 | 61.1526 | -61.4182 | -61.2122 | 60.8688 | 0.24261 | 0 | 0.23346 | 61.2762 | -61.409 | -0.14191 | 0.022888 | -0.050354 | 0.064087 | -0.26093 | -0.13275 | 0.14648 | 0.091553 | 61.2762 | 61.5097 | 122.1451 | 122.4289 | -0.050354 | 122.5525 | 61.5189 | -0.13275 | 122.4289 | -0.050354 | 61.5189 | 122.1451 | 122.5525 | -122.5479 | -122.5388
875.4062 | 122.5845 | -61.2213 | 61.1206 | 0.00206 | -0.00063242 | 0.0090447 | 0.023569 | 0.038866 | -0.032558 | 0.058208 | -61.322 | 61.0886 | -61.4319 | -61.2122 | 60.8826 | 0.23346 | -0.27466 | 0.18768 | 61.1252 | -61.4365 | -0.21057 | -0.032043 | -0.10071 | 0.009155 | -0.23804 | -0.21515 | 0.004578 | 0.10986 | 60.9467 | 61.409 | 122.1039 | 122.3099 | -0.10071 | 122.3465 | 61.4548 | -0.21515 | 122.3099 | -0.10071 | 61.4548 | 122.1039 | 122.3465 | -122.5525 | -122.5571
877.125 | 122.6303 | -61.2488 | 61.0565 | 0.00206 | 0.0040674 | 0.0090447 | 0.027414 | 0.040148 | -0.031917 | 0.060985 | -61.4136 | 61.1526 | -61.4685 | -61.322 | 60.7544 | 0.10071 | -0.054932 | 0.073242 | 61.2213 | -61.4731 | -0.21973 | 0.09613 | -0.16479 | -0.073242 | -0.30212 | -0.2243 | 0.16479 | 0.054932 | 61.1938 | 61.322 | 122.0032 | 122.4014 | -0.16479 | 122.4701 | 61.3495 | -0.2243 | 122.4014 | -0.16479 | 61.3495 | 122.0032 | 122.4701 | -122.525 | -122.5296
878.9062 | 122.6028 | -61.2122 | 61.0748 | 0.017319 | 0.00064938 | 0.011395 | 0.022928 | 0.038653 | -0.035122 | 0.060344 | -61.4044 | 61.1069 | -61.4594 | -61.3037 | 60.7819 | 0.15564 | -0.16937 | 0.10986 | 61.2076 | -61.4456 | -0.24719 | 0.032044 | -0.19226 | -0.091553 | -0.29297 | -0.23346 | 0.13275 | 0.054932 | 61.0428 | 61.322 | 121.994 | 122.319 | -0.19226 | 122.4197 | 61.3678 | -0.23346 | 122.319 | -0.19226 | 61.3678 | 121.994 | 122.4197 | -122.5342 | -122.5204
880.6406 | 122.5021 | -61.2259 | 61.116 | 0.017319 | 0.0012902 | 0.0058405 | 0.028696 | 0.040789 | -0.034267 | 0.060344 | -61.3403 | 61.1572 | -61.4502 | -61.2534 | 60.7956 | 0.17853 | -0.022888 | 0.13275 | 61.2442 | -61.4319 | -0.2243 | 0.041199 | -0.11444 | -0.027466 | -0.32044 | -0.20599 | 0.12817 | 0.10986 | 61.203 | 61.3586 | 122.0215 | 122.3831 | -0.11444 | 122.4701 | 61.4044 | -0.20599 | 122.3831 | -0.11444 | 61.4044 | 122.0215 | 122.4701 | -122.5662 | -122.5479
882.4062 | 122.5067 | -61.1938 | 61.2213 | 0.00206 | -0.00020502 | 0.012676 | 0.019937 | 0.037371 | -0.032558 | 0.060131 | -61.2305 | 61.1893 | -61.3358 | -61.1114 | 60.9695 | 0.32959 | -0.086975 | 0.3479 | 61.2213 | -61.3724 | -0.14191 | -0.032043 | -0.036621 | 0.082398 | -0.25177 | -0.17853 | 0 | 0.10529 | 61.1069 | 61.5417 | 122.1634 | 122.3831 | -0.036621 | 122.4152 | 61.5234 | -0.17853 | 122.3831 | -0.036621 | 61.5234 | 122.1634 | 122.4152 | -122.5571 | -122.5937
884.125 | 122.5388 | -61.2808 | 61.1298 | 0.00206 | 0.0010766 | 0.0094721 | 0.029337 | 0.042284 | -0.035122 | 0.058849 | -61.3724 | 61.1481 | -61.4319 | -61.2808 | 60.7773 | 0.15106 | -0.009155 | 0.13275 | 61.2579 | -61.4594 | -0.15106 | 0.01831 | -0.091552 | 0 | -0.35248 | -0.17853 | 0.12817 | 0.05951 | 61.2717 | 61.4136 | 122.0581 | 122.4289 | -0.091552 | 122.5388 | 61.4319 | -0.17853 | 122.4289 | -0.091552 | 61.4319 | 122.0581 | 122.5388 | -122.5616 | -122.5891
885.8438 | 122.5525 | -61.2213 | 61.1984 | 0.017319 | 0.0021448 | 0.0079767 | 0.022074 | 0.040789 | -0.032558 | 0.058208 | -61.2717 | 61.2167 | -61.3403 | -61.1938 | 60.9009 | 0.26093 | 0.082397 | 0.25635 | 61.3037 | -61.3861 | -0.11902 | 0.018311 | -0.050354 | 0.027465 | -0.29755 | -0.16479 | 0.10529 | 0.068665 | 61.3037 | 61.4777 | 122.1222 | 122.438 | -0.050354 | 122.525 | 61.4822 | -0.16479 | 122.438 | -0.050354 | 61.4822 | 122.1222 | 122.525 | -122.5388 | -122.5845
887.625 | 122.5616 | -61.2167 | 61.1206 | 0.00206 | 0.00064938 | 0.013317 | 0.02421 | 0.03908 | -0.030849 | 0.059703 | -61.3174 | 61.0748 | -61.4548 | -61.203 | 60.8734 | 0.21515 | -0.28381 | 0.20142 | 61.1618 | -61.4456 | -0.23804 | -0.045776 | -0.10071 | 0.013733 | -0.24719 | -0.22888 | 0.041199 | 0.13733 | 60.9329 | 61.4182 | 122.0901 | 122.2916 | -0.10071 | 122.3785 | 61.4319 | -0.22888 | 122.2916 | -0.10071 | 61.4319 | 122.0901 | 122.3785 | -122.5754 | -122.5662
889.3281 | 122.5937 | -61.2213 | 61.116 | -0.0055695 | 0.0055628 | 0.0092585 | 0.025064 | 0.03908 | -0.033626 | 0.061626 | -61.3403 | 61.0886 | -61.4365 | -61.2259 | 60.8276 | 0.20142 | -0.22888 | 0.16022 | 61.1938 | -61.441 | -0.21515 | -0.027466 | -0.11902 | -0.004578 | -0.28839 | -0.21973 | 0.07782 | 0.09613 | 60.9924 | 61.3815 | 122.049 | 122.3099 | -0.11902 | 122.4152 | 61.4227 | -0.21973 | 122.3099 | -0.11902 | 61.4227 | 122.049 | 122.4152 | -122.5525 | -122.5571
891.125 | 122.58 | -61.2076 | 61.1389 | 0.00206 | 8.578e-06 | 0.011822 | 0.026132 | 0.04143 | -0.034481 | 0.059917 | -61.322 | 61.0611 | -61.4136 | -61.2076 | 60.8551 | 0.21973 | -0.28381 | 0.17853 | 61.1481 | -61.4594 | -0.20599 | -0.07782 | -0.11444 | 0 | -0.28381 | -0.25177 | 0.009155 | 0.091553 | 60.9238 | 61.3861 | 122.0627 | 122.2687 | -0.11444 | 122.3557 | 61.4273 | -0.25177 | 122.2687 | -0.11444 | 61.4273 | 122.0627 | 122.3557 | -122.5525 | -122.5983
892.8906 | 122.6166 | -61.1938 | 61.1343 | 0.00206 | 0.00086298 | 0.0094721 | 0.025492 | 0.039721 | -0.033199 | 0.060985 | -61.3037 | 61.0931 | -61.4365 | -61.2076 | 60.8734 | 0.2243 | -0.24719 | 0.1831 | 61.1664 | -61.4502 | -0.24261 | -0.041198 | -0.10986 | -0.013733 | -0.26093 | -0.25635 | 0.032044 | 0.13275 | 60.9467 | 61.377 | 122.0673 | 122.287 | -0.10986 | 122.3602 | 61.4182 | -0.25635 | 122.287 | -0.10986 | 61.4182 | 122.0673 | 122.3602 | -122.5708 | -122.5845
894.5938 | 122.5113 | -61.1984 | 61.1801 | 0.0096895 | 0.00064938 | 0.0060541 | 0.024423 | 0.038866 | -0.032558 | 0.058208 | -61.235 | 61.1664 | -61.3449 | -61.1206 | 60.9467 | 0.32959 | -0.004578 | 0.32959 | 61.2991 | -61.3632 | -0.14648 | -0.013733 | -0.036621 | 0.07782 | -0.23346 | -0.16479 | 0.11902 | 0.10986 | 61.1938 | 61.528 | 122.1451 | 122.3648 | -0.036621 | 122.4976 | 61.528 | -0.16479 | 122.3648 | -0.036621 | 61.528 | 122.1451 | 122.4976 | -122.525 | -122.5433
896.3125 | 122.5708 | -61.2213 | 61.1252 | -0.0055695 | 0.00043578 | 0.010967 | 0.027414 | 0.040148 | -0.032985 | 0.05949 | -61.2946 | 61.0886 | -61.4365 | -61.203 | 60.8597 | 0.21973 | -0.29297 | 0.17395 | 61.1435 | -61.441 | -0.21515 | -0.036621 | -0.073243 | 0.01831 | -0.2655 | -0.21973 | 0.018311 | 0.14191 | 60.9283 | 61.3953 | 122.081 | 122.3099 | -0.073243 | 122.3648 | 61.441 | -0.21973 | 122.3099 | -0.073243 | 61.441 | 122.081 | 122.3648 | -122.5616 | -122.5662
898.1094 | 122.5754 | -61.1801 | 61.1343 | 0.00206 | 0.0021448 | 0.0092585 | 0.027414 | 0.038866 | -0.031917 | 0.060771 | -61.3083 | 61.084 | -61.409 | -61.1984 | 60.8597 | 0.23346 | -0.29297 | 0.20142 | 61.1618 | -61.4456 | -0.22888 | -0.050354 | -0.12817 | -0.01831 | -0.27466 | -0.2655 | 0.027466 | 0.10071 | 60.8871 | 61.3815 | 122.0398 | 122.2641 | -0.12817 | 122.3419 | 61.4136 | -0.2655 | 122.2641 | -0.12817 | 61.4136 | 122.0398 | 122.3419 | -122.5433 | -122.58
899.875 | 122.4884 | -61.2579 | 61.1069 | 0.0096895 | 0.0023584 | 0.011181 | 0.030405 | 0.040575 | -0.034908 | 0.060985 | -61.2854 | 61.1481 | -61.4136 | -61.1801 | 60.8643 | 0.24261 | 0 | 0.24261 | 61.2488 | -61.3953 | -0.15564 | 0.041198 | -0.027465 | 0.07782 | -0.24262 | -0.13733 | 0.14191 | 0.12817 | 61.2579 | 61.5006 | 122.1222 | 122.406 | -0.027465 | 122.5067 | 61.5006 | -0.13733 | 122.406 | -0.027465 | 61.5006 | 122.1222 | 122.5067 | -122.5204 | -122.5021
901.6094 | 122.4792 | -61.2854 | 61.1343 | 0.0096895 | 0.00022218 | 0.0069085 | 0.02955 | 0.039294 | -0.033199 | 0.058849 | -61.2946 | 61.1572 | -61.4273 | -61.1847 | 60.8551 | 0.24719 | -0.009155 | 0.22888 | 61.2625 | -61.3861 | -0.14191 | 0.022889 | -0.009156 | 0.10071 | -0.27923 | -0.10071 | 0.12817 | 0.13275 | 61.2762 | 61.5143 | 122.1405 | 122.4426 | -0.009156 | 122.5479 | 61.5326 | -0.10071 | 122.4426 | -0.009156 | 61.5326 | 122.1405 | 122.5479 | -122.5616 | -122.5204
903.3281 | 122.5204 | -61.2259 | 61.1343 | 0.00206 | 0.0027856 | 0.0073359 | 0.025064 | 0.040148 | -0.033626 | 0.061199 | -61.3312 | 61.2167 | -61.4044 | -61.2122 | 60.8551 | 0.23346 | 0.09613 | 0.22888 | 61.29 | -61.4182 | -0.17853 | 0.082398 | -0.10529 | 0.013733 | -0.27923 | -0.19226 | 0.15564 | 0.073242 | 61.322 | 61.4548 | 122.081 | 122.4426 | -0.10529 | 122.5159 | 61.4594 | -0.19226 | 122.4426 | -0.10529 | 61.4594 | 122.081 | 122.5159 | -122.5388 | -122.5525
905.1094 | 122.5845 | -61.2213 | 61.1206 | 0.00206 | -0.00041862 | 0.012249 | 0.022501 | 0.040789 | -0.032772 | 0.060131 | -61.3037 | 61.0886 | -61.441 | -61.203 | 60.8734 | 0.23804 | -0.2655 | 0.17853 | 61.1847 | -61.4365 | -0.21973 | -0.032043 | -0.082398 | 0.01831 | -0.24719 | -0.21515 | 0.064087 | 0.13733 | 60.9558 | 61.3998 | 122.0947 | 122.3099 | -0.082398 | 122.406 | 61.4594 | -0.21515 | 122.3099 | -0.082398 | 61.4594 | 122.0947 | 122.406 | -122.5616 | -122.5571
906.875 | 122.493 | -61.1801 | 61.2213 | 0.00206 | 0.00064938 | 0.013531 | 0.02421 | 0.040789 | -0.030849 | 0.060558 | -61.2167 | 61.1847 | -61.3083 | -61.1023 | 60.9787 | 0.35248 | -0.10986 | 0.33875 | 61.2213 | -61.377 | -0.12817 | -0.036621 | -0.036621 | 0.07782 | -0.24261 | -0.19684 | 0 | 0.091553 | 61.0703 | 61.5189 | 122.1588 | 122.3648 | -0.036621 | 122.4014 | 61.5326 | -0.19684 | 122.3648 | -0.036621 | 61.5326 | 122.1588 | 122.4014 | -122.5296 | -122.5983
908.5938 | 122.612 | -61.1526 | 61.1526 | 0.024948 | 0.0019312 | 0.011608 | 0.022287 | 0.039507 | -0.031917 | 0.057994 | -61.3083 | 61.1572 | -61.377 | -61.1893 | 60.8917 | 0.25177 | -0.14648 | 0.23346 | 61.2259 | -61.3861 | -0.2243 | 0.004578 | -0.15564 | -0.036621 | -0.26092 | -0.23346 | 0.073242 | 0.068664 | 61.0062 | 61.3861 | 122.0444 | 122.3099 | -0.15564 | 122.3785 | 61.4044 | -0.23346 | 122.3099 | -0.15564 | 61.4044 | 122.0444 | 122.3785 | -122.5296 | -122.5388
910.375 | 122.493 | -61.2717 | 61.1435 | 0.017319 | 0.002572 | 0.012035 | 0.029764 | 0.039935 | -0.034694 | 0.05949 | -61.3083 | 61.1343 | -61.441 | -61.203 | 60.8322 | 0.20142 | -0.004578 | 0.19684 | 61.2488 | -61.4227 | -0.16937 | -0.009156 | -0.036622 | 0.068664 | -0.31128 | -0.15106 | 0.10529 | 0.13275 | 61.2671 | 61.4685 | 122.1039 | 122.406 | -0.036622 | 122.5204 | 61.4731 | -0.15106 | 122.406 | -0.036622 | 61.4731 | 122.1039 | 122.5204 | -122.5845 | -122.5662
912.1094 | 122.5388 | -61.2122 | 61.1343 | 0.00206 | -0.00020502 | 0.0056269 | 0.025492 | 0.038226 | -0.035763 | 0.061199 | -61.3312 | 61.2076 | -61.3724 | -61.2076 | 60.8459 | 0.2243 | 0.10529 | 0.22888 | 61.29 | -61.3953 | -0.16022 | 0.073243 | -0.11902 | 0.004577 | -0.28839 | -0.18311 | 0.15564 | 0.041198 | 61.3174 | 61.441 | 122.0581 | 122.4197 | -0.11902 | 122.5021 | 61.4365 | -0.18311 | 122.4197 | -0.11902 | 61.4365 | 122.0581 | 122.5021 | -122.5067 | -122.5296
913.875 | 122.6166 | -61.1572 | 61.1389 | 0.0096895 | 8.578e-06 | 0.010967 | 0.022928 | 0.037371 | -0.032985 | 0.058635 | -61.322 | 61.1343 | -61.3724 | -61.2076 | 60.8597 | 0.22888 | -0.16022 | 0.16937 | 61.2259 | -61.4227 | -0.21515 | -0.004578 | -0.16479 | -0.050354 | -0.27924 | -0.2655 | 0.086975 | 0.050354 | 60.997 | 61.3266 | 122.0169 | 122.2916 | -0.16479 | 122.3831 | 61.3861 | -0.2655 | 122.2916 | -0.16479 | 61.3861 | 122.0169 | 122.3831 | -122.5113 | -122.5616
915.5938 | 122.525 | -61.2122 | 61.1755 | 0.017319 | 0.0023584 | 0.011395 | 0.026346 | 0.040575 | -0.034694 | 0.057781 | -61.3266 | 61.2305 | -61.3815 | -61.1984 | 60.8505 | 0.21973 | 0.10071 | 0.21973 | 61.322 | -61.3815 | -0.16937 | 0.054932 | -0.11444 | 0.013733 | -0.32501 | -0.16937 | 0.14648 | 0.054932 | 61.3129 | 61.4319 | 122.0627 | 122.4426 | -0.11444 | 122.5342 | 61.4319 | -0.16937 | 122.4426 | -0.11444 | 61.4319 | 122.0627 | 122.5342 | -122.5571 | -122.5571
917.3594 | 122.5021 | -61.1755 | 61.2076 | 0.00206 | 0.0027856 | 0.0096857 | 0.023142 | 0.03908 | -0.031704 | 0.060558 | -61.2076 | 61.1526 | -61.3174 | -61.0703 | 60.9787 | 0.3479 | -0.15564 | 0.33417 | 61.2396 | -61.3632 | -0.14191 | -0.054932 | -0.032044 | 0.10529 | -0.22888 | -0.18768 | 0.032043 | 0.10986 | 61.0199 | 61.5097 | 122.1542 | 122.3282 | -0.032044 | 122.4152 | 61.5234 | -0.18768 | 122.3282 | -0.032044 | 61.5234 | 122.1542 | 122.4152 | -122.525 | -122.5708
919.0781 | 122.4609 | -61.2671 | 61.1343 | 0.00206 | 0.0021448 | 0.012249 | 0.030405 | 0.039294 | -0.035763 | 0.057567 | -61.29 | 61.1801 | -61.4044 | -61.1801 | 60.8459 | 0.24719 | -0.009155 | 0.23804 | 61.2671 | -61.4136 | -0.13733 | 0.045777 | -0.022888 | 0.086975 | -0.28839 | -0.14648 | 0.13275 | 0.11444 | 61.2579 | 61.5051 | 122.113 | 122.4472 | -0.022888 | 122.5342 | 61.5143 | -0.14648 | 122.4472 | -0.022888 | 61.5143 | 122.113 | 122.5342 | -122.5388 | -122.5479
920.8594 | 122.4884 | -61.1938 | 61.2122 | -0.0055695 | 0.0012902 | 0.013317 | 0.023783 | 0.035876 | -0.02914 | 0.059917 | -61.2122 | 61.171 | -61.3358 | -61.0703 | 60.9741 | 0.33875 | -0.11444 | 0.35248 | 61.2305 | -61.3586 | -0.14191 | -0.041199 | -0.01831 | 0.1236 | -0.23804 | -0.16479 | 0.018311 | 0.1236 | 61.0794 | 61.5463 | 122.168 | 122.3648 | -0.01831 | 122.4243 | 61.5326 | -0.16479 | 122.3648 | -0.01831 | 61.5326 | 122.168 | 122.4243 | -122.5479 | -122.5708
922.5781 | 122.5708 | -61.1618 | 61.1618 | 0.0096895 | -0.00041862 | 0.013317 | 0.026346 | 0.037798 | -0.030636 | 0.059276 | -61.2991 | 61.1023 | -61.3998 | -61.203 | 60.8505 | 0.22888 | -0.23804 | 0.18768 | 61.1755 | -61.4227 | -0.23804 | -0.059509 | -0.13733 | -0.041199 | -0.31128 | -0.26093 | 0.013733 | 0.10071 | 60.9238 | 61.3495 | 122.0123 | 122.2641 | -0.13733 | 122.3373 | 61.3907 | -0.26093 | 122.2641 | -0.13733 | 61.3907 | 122.0123 | 122.3373 | -122.5616 | -122.5845
924.2812 | 122.4976 | -61.1618 | 61.2167 | -0.0055695 | 0.0034266 | 0.0086175 | 0.024423 | 0.037585 | -0.032345 | 0.057994 | -61.2076 | 61.1618 | -61.3266 | -61.0931 | 60.9695 | 0.34332 | -0.14648 | 0.35248 | 61.2579 | -61.3724 | -0.1648 | -0.054932 | -0.045777 | 0.068664 | -0.24719 | -0.21057 | 0.041199 | 0.11902 | 61.0153 | 61.5143 | 122.1313 | 122.3236 | -0.045777 | 122.4197 | 61.5051 | -0.21057 | 122.3236 | -0.045777 | 61.5051 | 122.1313 | 122.4197 | -122.5433 | -122.5891
926.0469 | 122.4976 | -61.1847 | 61.1984 | -0.0055695 | -0.00084602 | 0.014172 | 0.023142 | 0.036303 | -0.032131 | 0.059276 | -61.2122 | 61.1526 | -61.3129 | -61.0657 | 60.965 | 0.3479 | -0.15106 | 0.33875 | 61.2305 | -61.3724 | -0.12817 | -0.045776 | -0.027466 | 0.11902 | -0.23346 | -0.18768 | 0.032044 | 0.10071 | 61.0336 | 61.5234 | 122.1497 | 122.3373 | -0.027466 | 122.4152 | 61.5326 | -0.18768 | 122.3373 | -0.027466 | 61.5326 | 122.1497 | 122.4152 | -122.5113 | -122.5708
927.8125 | 122.6166 | -61.1343 | 61.1664 | 0.00206 | 0.00086298 | 0.0098993 | 0.027201 | 0.038012 | -0.030849 | 0.058849 | -61.3129 | 61.1481 | -61.377 | -61.1984 | 60.8551 | 0.21515 | -0.13275 | 0.17395 | 61.203 | -61.4044 | -0.24262 | -0.018311 | -0.17853 | -0.064087 | -0.31128 | -0.27008 | 0.036621 | 0.064087 | 61.0016 | 61.3083 | 121.9894 | 122.2824 | -0.17853 | 122.3373 | 61.3495 | -0.27008 | 122.2824 | -0.17853 | 61.3495 | 121.9894 | 122.3373 | -122.5433 | -122.5708
929.5781 | 122.5845 | -61.1481 | 61.1847 | 0.017319 | -0.00063242 | 0.0086175 | 0.025278 | 0.037371 | -0.031917 | 0.058849 | -61.2625 | 61.1435 | -61.3724 | -61.116 | 60.9421 | 0.31586 | -0.13733 | 0.28839 | 61.2076 | -61.3678 | -0.2243 | -0.041198 | -0.11444 | 0.032043 | -0.24261 | -0.21973 | 0.022889 | 0.10986 | 61.0107 | 61.4365 | 122.0901 | 122.2916 | -0.11444 | 122.3557 | 61.4639 | -0.21973 | 122.2916 | -0.11444 | 61.4639 | 122.0901 | 122.3557 | -122.5571 | -122.5525
931.2969 | 122.5754 | -61.2213 | 61.0703 | 0.0096895 | 0.0019312 | 0.015667 | 0.033182 | 0.039721 | -0.035122 | 0.059703 | -61.3724 | 61.1618 | -61.4319 | -61.2488 | 60.7544 | 0.1236 | -0.013733 | 0.07782 | 61.2396 | -61.4456 | -0.21057 | 0.091553 | -0.15106 | -0.027466 | -0.31586 | -0.22431 | 0.16937 | 0.05951 | 61.2076 | 61.2991 | 121.9757 | 122.3831 | -0.15106 | 122.4609 | 61.3449 | -0.22431 | 122.3831 | -0.15106 | 61.3449 | 121.9757 | 122.4609 | -122.5021 | -122.5159
933.0781 | 122.6166 | -61.1298 | 61.1435 | -0.0055695 | 0.00043578 | 0.011822 | 0.022501 | 0.038866 | -0.032558 | 0.058208 | -61.2991 | 61.0977 | -61.377 | -61.1893 | 60.8734 | 0.21057 | -0.19226 | 0.17853 | 61.1847 | -61.409 | -0.24719 | -0.045777 | -0.16937 | -0.059509 | -0.27008 | -0.27924 | 0.041198 | 0.07782 | 60.9375 | 61.3083 | 122.0032 | 122.2275 | -0.16937 | 122.3145 | 61.3403 | -0.27924 | 122.2275 | -0.16937 | 61.3403 | 122.0032 | 122.3145 | -122.5204 | -122.5525
934.8438 | 122.6212 | -61.1755 | 61.1435 | -0.0055695 | 0.00064938 | 0.01054 | 0.025278 | 0.039507 | -0.031917 | 0.058635 | -61.2854 | 61.0977 | -61.3632 | -61.171 | 60.8459 | 0.2243 | -0.17395 | 0.17395 | 61.2122 | -61.4044 | -0.18768 | -0.045777 | -0.10986 | 0.004578 | -0.29755 | -0.22888 | 0.068664 | 0.07782 | 61.0016 | 61.3495 | 122.0215 | 122.2733 | -0.10986 | 122.3877 | 61.3998 | -0.22888 | 122.2733 | -0.10986 | 61.3998 | 122.0215 | 122.3877 | -122.5067 | -122.5479
936.625 | 122.4701 | -61.2534 | 61.116 | 0.0096895 | 0.00064938 | 0.0096857 | 0.030191 | 0.039294 | -0.035335 | 0.060131 | -61.2579 | 61.1664 | -61.3907 | -61.1526 | 60.8688 | 0.24719 | -0.018311 | 0.24261 | 61.2717 | -61.3907 | -0.13733 | 0.050354 | -0.004578 | 0.10071 | -0.24719 | -0.13733 | 0.15564 | 0.13275 | 61.235 | 61.496 | 122.1222 | 122.4197 | -0.004578 | 122.525 | 61.5005 | -0.13733 | 122.4197 | -0.004578 | 61.5005 | 122.1222 | 122.525 | -122.5067 | -122.5067
938.4062 | 122.5662 | -61.2213 | 61.084 | -0.0055695 | 0.00086298 | 0.010326 | 0.029764 | 0.040789 | -0.032345 | 0.059917 | -61.3861 | 61.1252 | -61.4456 | -61.2625 | 60.759 | 0.1236 | -0.027466 | 0.086975 | 61.2213 | -61.441 | -0.22431 | 0.041199 | -0.16479 | -0.041199 | -0.32501 | -0.21973 | 0.13733 | 0.05951 | 61.1938 | 61.3083 | 121.9803 | 122.3465 | -0.16479 | 122.4426 | 61.3449 | -0.21973 | 122.3465 | -0.16479 | 61.3449 | 121.9803 | 122.4426 | -122.5296 | -122.525
940.1094 | 122.4792 | -61.2442 | 61.1664 | 0.00206 | 0.0019312 | 0.013317 | 0.02656 | 0.041216 | -0.031917 | 0.05949 | -61.29 | 61.203 | -61.377 | -61.171 | 60.8597 | 0.24261 | 0.032043 | 0.23804 | 61.2717 | -61.409 | -0.13275 | 0.036621 | -0.045776 | 0.073243 | -0.3067 | -0.16479 | 0.10529 | 0.086975 | 61.2762 | 61.4822 | 122.1039 | 122.4472 | -0.045776 | 122.5159 | 61.4868 | -0.16479 | 122.4472 | -0.045776 | 61.4868 | 122.1039 | 122.5159 | -122.5433 | -122.5754
941.8906 | 122.5021 | -61.2213 | 61.1526 | 0.0096895 | 0.0027856 | 0.013958 | 0.025919 | 0.039935 | -0.033199 | 0.05949 | -61.3174 | 61.1893 | -61.3495 | -61.1893 | 60.8459 | 0.23804 | 0.10986 | 0.22888 | 61.2671 | -61.3678 | -0.12817 | 0.036621 | -0.096131 | 0.032043 | -0.3067 | -0.14648 | 0.11444 | 0.032043 | 61.3312 | 61.4502 | 122.0673 | 122.4106 | -0.096131 | 122.4884 | 61.4594 | -0.14648 | 122.4106 | -0.096131 | 61.4594 | 122.0673 | 122.4884 | -122.5021 | -122.5204
943.6875 | 122.4747 | -61.2396 | 61.1343 | 0.00206 | -0.001914 | 0.01289 | 0.028482 | 0.037157 | -0.034481 | 0.061199 | -61.2717 | 61.1664 | -61.377 | -61.1526 | 60.8643 | 0.24719 | -0.004578 | 0.21515 | 61.2488 | -61.3678 | -0.13733 | 0.032044 | -0.032043 | 0.086975 | -0.27008 | -0.12817 | 0.11444 | 0.10529 | 61.235 | 61.4548 | 122.1039 | 122.406 | -0.032043 | 122.4884 | 61.4868 | -0.12817 | 122.406 | -0.032043 | 61.4868 | 122.1039 | 122.4884 | -122.5113 | -122.5021
945.4531 | 122.5067 | -61.2122 | 61.1389 | 0.017319 | 0.0040674 | 0.0088311 | 0.025064 | 0.040362 | -0.033413 | 0.05949 | -61.3083 | 61.2442 | -61.3495 | -61.1984 | 60.8643 | 0.23804 | 0.10986 | 0.2243 | 61.3037 | -61.3632 | -0.13733 | 0.10529 | -0.096131 | 0.013733 | -0.27466 | -0.15106 | 0.16479 | 0.041198 | 61.322 | 61.4365 | 122.0764 | 122.4564 | -0.096131 | 122.5159 | 61.4502 | -0.15106 | 122.4564 | -0.096131 | 61.4502 | 122.0764 | 122.5159 | -122.4884 | -122.5021
947.1875 | 122.5433 | -61.1664 | 61.1481 | 0.0096895 | -0.00020502 | 0.0094721 | 0.022714 | 0.040575 | -0.030422 | 0.060344 | -61.2671 | 61.1298 | -61.3907 | -61.1664 | 60.8871 | 0.23346 | -0.2655 | 0.19226 | 61.1847 | -61.409 | -0.2243 | -0.01831 | -0.10071 | 0 | -0.26093 | -0.24262 | 0.036621 | 0.1236 | 60.9009 | 61.3586 | 122.0535 | 122.2961 | -0.10071 | 122.3511 | 61.3998 | -0.24262 | 122.2961 | -0.10071 | 61.3998 | 122.0535 | 122.3511 | -122.5388 | -122.5571
948.9688 | 122.5204 | -61.1572 | 61.1755 | 0.0096895 | 0.0029992 | 0.0081903 | 0.024851 | 0.039294 | -0.032345 | 0.057781 | -61.2991 | 61.2488 | -61.3495 | -61.171 | 60.8871 | 0.23804 | 0.14648 | 0.24261 | 61.3174 | -61.3358 | -0.19226 | 0.073242 | -0.14191 | -0.013732 | -0.28839 | -0.17853 | 0.14191 | 0.050354 | 61.3037 | 61.3998 | 122.0444 | 122.406 | -0.14191 | 122.4747 | 61.3953 | -0.17853 | 122.406 | -0.14191 | 61.3953 | 122.0444 | 122.4747 | -122.525 | -122.5113
950.7344 | 122.4701 | -61.203 | 61.1664 | 0.00206 | 0.002572 | 0.01289 | 0.026773 | 0.042498 | -0.031704 | 0.058422 | -61.2717 | 61.203 | -61.3861 | -61.1572 | 60.878 | 0.23804 | 0.041199 | 0.25177 | 61.2854 | -61.3815 | -0.1831 | 0.036621 | -0.068664 | 0.045776 | -0.28839 | -0.17853 | 0.11902 | 0.11444 | 61.2442 | 61.4548 | 122.081 | 122.406 | -0.068664 | 122.4884 | 61.441 | -0.17853 | 122.406 | -0.068664 | 61.441 | 122.081 | 122.4884 | -122.5525 | -122.5479
952.5 | 122.4884 | -61.2076 | 61.1481 | -0.0055695 | 0.0019312 | 0.0081903 | 0.026132 | 0.039507 | -0.034054 | 0.058422 | -61.2717 | 61.2305 | -61.3403 | -61.1572 | 60.8688 | 0.25635 | 0.064087 | 0.2243 | 61.2717 | -61.3678 | -0.13275 | 0.082398 | -0.064086 | 0.050354 | -0.27924 | -0.16022 | 0.1236 | 0.068665 | 61.2717 | 61.4319 | 122.0764 | 122.4381 | -0.064086 | 122.4792 | 61.4639 | -0.16022 | 122.4381 | -0.064086 | 61.4639 | 122.0764 | 122.4792 | -122.4884 | -122.5159
954.2188 | 122.4792 | -61.1984 | 61.1526 | 0.017319 | 0.0027856 | 0.012676 | 0.026346 | 0.039507 | -0.032985 | 0.059703 | -61.29 | 61.2213 | -61.3541 | -61.1801 | 60.8688 | 0.25635 | 0.10529 | 0.21973 | 61.29 | -61.3541 | -0.15564 | 0.068664 | -0.091553 | 0.01831 | -0.28381 | -0.15564 | 0.13733 | 0.064087 | 61.3037 | 61.4182 | 122.0673 | 122.4197 | -0.091553 | 122.4884 | 61.4548 | -0.15564 | 122.4197 | -0.091553 | 61.4548 | 122.0673 | 122.4884 | -122.5067 | -122.5067
956 | 122.5891 | -61.203 | 61.0886 | 0.00206 | 0.00064938 | 0.010326 | 0.029123 | 0.043566 | -0.034054 | 0.059276 | -61.3678 | 61.1481 | -61.4182 | -61.29 | 60.7727 | 0.1236 | -0.022888 | 0.073242 | 61.2625 | -61.3953 | -0.21515 | 0.059509 | -0.16479 | -0.086975 | -0.31586 | -0.19226 | 0.17395 | 0.050354 | 61.1801 | 61.2762 | 121.9757 | 122.3511 | -0.16479 | 122.4655 | 61.3266 | -0.19226 | 122.3511 | -0.16479 | 61.3266 | 121.9757 | 122.4655 | -122.5067 | -122.4838
957.7031 | 122.4335 | -61.2305 | 61.1618 | 0.0096895 | 0.00043578 | 0.0084039 | 0.026346 | 0.038226 | -0.032985 | 0.05949 | -61.2717 | 61.203 | -61.3953 | -61.1389 | 60.8826 | 0.24261 | 0.004578 | 0.24261 | 61.2534 | -61.3632 | -0.16479 | 0.041199 | -0.041198 | 0.091553 | -0.27924 | -0.13275 | 0.091553 | 0.1236 | 61.235 | 61.4731 | 122.113 | 122.4335 | -0.041198 | 122.4838 | 61.4731 | -0.13275 | 122.4335 | -0.041198 | 61.4731 | 122.113 | 122.4838 | -122.5571 | -122.525
959.4844 | 122.4792 | -61.2167 | 61.1114 | 0.00206 | 0.002572 | 0.011822 | 0.026773 | 0.040148 | -0.03384 | 0.058635 | -61.2534 | 61.1801 | -61.3541 | -61.1572 | 60.8734 | 0.25635 | -0.004578 | 0.23804 | 61.2991 | -61.3678 | -0.13733 | 0.068665 | -0.036621 | 0.059509 | -0.23804 | -0.15106 | 0.18768 | 0.10071 | 61.2122 | 61.4548 | 122.0901 | 122.3969 | -0.036621 | 122.5159 | 61.4731 | -0.15106 | 122.3969 | -0.036621 | 61.4731 | 122.0901 | 122.5159 | -122.4655 | -122.4792
961.2188 | 122.4701 | -61.1526 | 61.1893 | 0.00206 | 0.0017176 | 0.0081903 | 0.022714 | 0.038439 | -0.030208 | 0.058849 | -61.1938 | 61.1938 | -61.29 | -61.0748 | 60.9695 | 0.33875 | -0.068665 | 0.33875 | 61.2534 | -61.3266 | -0.13733 | 0.004578 | -0.041199 | 0.07782 | -0.21973 | -0.17395 | 0.064087 | 0.09613 | 61.084 | 61.4914 | 122.1222 | 122.3465 | -0.041199 | 122.406 | 61.4914 | -0.17395 | 122.3465 | -0.041199 | 61.4914 | 122.1222 | 122.406 | -122.4792 | -122.5159
963 | 122.4747 | -61.1984 | 61.1389 | 0.00206 | 0.001504 | 0.014385 | 0.029978 | 0.039721 | -0.035122 | 0.05949 | -61.2946 | 61.1847 | -61.3953 | -61.2122 | 60.8139 | 0.17853 | -0.009155 | 0.15564 | 61.2396 | -61.3861 | -0.19684 | 0.045776 | -0.096131 | -0.013733 | -0.32501 | -0.18768 | 0.10071 | 0.10071 | 61.1893 | 61.3541 | 122.0123 | 122.3831 | -0.096131 | 122.438 | 61.377 | -0.18768 | 122.3831 | -0.096131 | 61.377 | 122.0123 | 122.438 | -122.5342 | -122.525
964.7188 | 122.4472 | -61.2076 | 61.116 | 0.00206 | 0.0021448 | 0.010967 | 0.026987 | 0.040575 | -0.034267 | 0.061626 | -61.2534 | 61.1801 | -61.377 | -61.1481 | 60.8643 | 0.25177 | 0.004578 | 0.23804 | 61.2854 | -61.3541 | -0.16937 | 0.064087 | -0.045776 | 0.05951 | -0.25177 | -0.14648 | 0.16937 | 0.1236 | 61.2122 | 61.4456 | 122.0718 | 122.3877 | -0.045776 | 122.493 | 61.4594 | -0.14648 | 122.3877 | -0.045776 | 61.4594 | 122.0718 | 122.493 | -122.493 | -122.4701
966.4375 | 122.4747 | -61.1526 | 61.2213 | 0.00206 | 0.0027856 | 0.011608 | 0.02186 | 0.03908 | -0.032131 | 0.058849 | -61.1984 | 61.1938 | -61.2762 | -61.1023 | 60.9512 | 0.33417 | -0.036621 | 0.33875 | 61.2717 | -61.3312 | -0.1236 | -0.027465 | -0.045776 | 0.050354 | -0.27008 | -0.17853 | 0.050354 | 0.07782 | 61.116 | 61.4914 | 122.1039 | 122.3465 | -0.045776 | 122.4243 | 61.4868 | -0.17853 | 122.3465 | -0.045776 | 61.4868 | 122.1039 | 122.4243 | -122.4976 | -122.5525
968.1406 | 122.5159 | -61.1572 | 61.1801 | -0.0055695 | 0.0040674 | 0.013744 | 0.026987 | 0.037585 | -0.032985 | 0.061412 | -61.2717 | 61.2534 | -61.322 | -61.1755 | 60.8505 | 0.21057 | 0.10529 | 0.21973 | 61.3174 | -61.3632 | -0.16479 | 0.073242 | -0.11444 | -0.01831 | -0.32959 | -0.20599 | 0.13733 | 0.050354 | 61.2625 | 61.377 | 122.0078 | 122.4106 | -0.11444 | 122.4747 | 61.3678 | -0.20599 | 122.4106 | -0.11444 | 61.3678 | 122.0078 | 122.4747 | -122.5021 | -122.5433
969.8906 | 122.5983 | -61.1893 | 61.0703 | 0.00206 | 0.0038538 | 0.012676 | 0.029337 | 0.039507 | -0.034054 | 0.060344 | -61.3541 | 61.1618 | -61.4182 | -61.2579 | 60.7727 | 0.11444 | -0.064087 | 0.082397 | 61.2579 | -61.3953 | -0.22888 | 0.091553 | -0.16479 | -0.068665 | -0.29755 | -0.20599 | 0.18768 | 0.064087 | 61.1252 | 61.2717 | 121.962 | 122.3511 | -0.16479 | 122.4472 | 61.3037 | -0.20599 | 122.3511 | -0.16479 | 61.3037 | 121.962 | 122.4472 | -122.4884 | -122.4655
971.6094 | 122.5891 | -61.1847 | 61.116 | 0.017319 | 0.0038538 | 0.012249 | 0.026987 | 0.042498 | -0.034481 | 0.060344 | -61.3586 | 61.1481 | -61.377 | -61.2671 | 60.7727 | 0.11444 | -0.036621 | 0.073242 | 61.2579 | -61.3998 | -0.19226 | 0.032043 | -0.17395 | -0.082398 | -0.34332 | -0.21515 | 0.14191 | 0.01831 | 61.1481 | 61.2579 | 121.9574 | 122.3328 | -0.17395 | 122.4426 | 61.2991 | -0.21515 | 122.3328 | -0.17395 | 61.2991 | 121.9574 | 122.4426 | -122.493 | -122.5159
973.3125 | 122.5845 | -61.1206 | 61.1481 | -0.0055695 | -0.00063242 | 0.011822 | 0.020578 | 0.040575 | -0.031917 | 0.060558 | -61.2762 | 61.1206 | -61.3586 | -61.171 | 60.8643 | 0.2243 | -0.20142 | 0.19226 | 61.2259 | -61.3586 | -0.23804 | -0.027466 | -0.15564 | -0.050354 | -0.28381 | -0.23804 | 0.07782 | 0.082398 | 60.9192 | 61.3129 | 121.9849 | 122.2412 | -0.15564 | 122.3465 | 61.3449 | -0.23804 | 122.2412 | -0.15564 | 61.3449 | 121.9849 | 122.3465 | -122.5067 | -122.5067
975.0781 | 122.5433 | -61.1572 | 61.1298 | -0.0055695 | 0.0017176 | 0.010326 | 0.025919 | 0.039721 | -0.032345 | 0.059276 | -61.29 | 61.1114 | -61.3907 | -61.171 | 60.8551 | 0.21057 | -0.24261 | 0.16022 | 61.1847 | -61.377 | -0.23346 | -0.018311 | -0.13275 | -0.013732 | -0.27466 | -0.21973 | 0.054931 | 0.10071 | 60.9146 | 61.3174 | 122.0123 | 122.2687 | -0.13275 | 122.3419 | 61.3678 | -0.21973 | 122.2687 | -0.13275 | 61.3678 | 122.0123 | 122.3419 | -122.5204 | -122.5067
976.7969 | 122.4701 | -61.1069 | 61.2076 | 0.00206 | 0.00064938 | 0.0094721 | 0.022074 | 0.037798 | -0.031277 | 0.057994 | -61.1801 | 61.1664 | -61.2991 | -61.0565 | 60.9787 | 0.33417 | -0.13733 | 0.31586 | 61.2762 | -61.3174 | -0.19226 | -0.041199 | -0.073242 | 0.050354 | -0.22888 | -0.21057 | 0.068664 | 0.11902 | 60.9695 | 61.4227 | 122.0856 | 122.2733 | -0.073242 | 122.3831 | 61.441 | -0.21057 | 122.2733 | -0.073242 | 61.441 | 122.0856 | 122.3831 | -122.5067 | -122.525
978.5781 | 122.4655 | -61.1893 | 61.1526 | 0.017319 | 0.0055628 | 0.014172 | 0.030618 | 0.039721 | -0.034054 | 0.059062 | -61.2122 | 61.1984 | -61.3266 | -61.1206 | 60.8826 | 0.23346 | -0.018311 | 0.2243 | 61.29 | -61.3541 | -0.13733 | 0.045776 | -0.022888 | 0.068665 | -0.27008 | -0.16479 | 0.13733 | 0.11444 | 61.171 | 61.4136 | 122.0718 | 122.3877 | -0.022888 | 122.4792 | 61.4227 | -0.16479 | 122.3877 | -0.022888 | 61.4227 | 122.0718 | 122.4792 | -122.4792 | -122.5067
980.2969 | 122.4701 | -61.1206 | 61.2534 | 0.0096895 | 0.00022218 | 0.012463 | 0.025064 | 0.039507 | -0.032558 | 0.058849 | -61.1664 | 61.1847 | -61.2854 | -61.0519 | 60.965 | 0.33875 | -0.068665 | 0.32959 | 61.2717 | -61.3312 | -0.1648 | -0.068665 | -0.045777 | 0.068664 | -0.28839 | -0.21057 | 0.01831 | 0.11902 | 61.0519 | 61.4502 | 122.0856 | 122.3053 | -0.045777 | 122.3923 | 61.4594 | -0.21057 | 122.3053 | -0.045777 | 61.4594 | 122.0856 | 122.3923 | -122.5388 | -122.5845
982.0938 | 122.5388 | -61.1435 | 61.1526 | -0.013199 | 0.00086298 | 0.010754 | 0.02656 | 0.040362 | -0.032772 | 0.058635 | -61.235 | 61.1252 | -61.3907 | -61.1343 | 60.8734 | 0.22888 | -0.26093 | 0.18768 | 61.1847 | -61.3815 | -0.24719 | -0.027466 | -0.091552 | 0.009156 | -0.27924 | -0.23804 | 0.032043 | 0.15564 | 60.8826 | 61.3312 | 122.0169 | 122.2687 | -0.091552 | 122.3282 | 61.3724 | -0.23804 | 122.2687 | -0.091552 | 61.3724 | 122.0169 | 122.3282 | -122.5433 | -122.5342
983.7969 | 122.5845 | -61.1481 | 61.1114 | 0.0096895 | 0.0019312 | 0.013317 | 0.029123 | 0.039935 | -0.035549 | 0.059703 | -61.3266 | 61.1801 | -61.4136 | -61.2122 | 60.7864 | 0.14191 | -0.064087 | 0.091553 | 61.2854 | -61.3953 | -0.2655 | 0.068665 | -0.17853 | -0.064087 | -0.32501 | -0.24719 | 0.17395 | 0.086975 | 61.084 | 61.2396 | 121.9345 | 122.3282 | -0.17853 | 122.4335 | 61.29 | -0.24719 | 122.3282 | -0.17853 | 61.29 | 121.9345 | 122.4335 | -122.525 | -122.5067
985.5625 | 122.4838 | -61.1847 | 61.1481 | 0.00206 | 0.0032128 | 0.012676 | 0.026987 | 0.040789 | -0.033626 | 0.061626 | -61.2671 | 61.1847 | -61.3495 | -61.171 | 60.8322 | 0.18768 | -0.036621 | 0.14648 | 61.2579 | -61.3449 | -0.1648 | 0.036621 | -0.082398 | 0.013733 | -0.31586 | -0.16022 | 0.10986 | 0.082397 | 61.1481 | 61.3312 | 122.0169 | 122.3694 | -0.082398 | 122.4426 | 61.3724 | -0.16022 | 122.3694 | -0.082398 | 61.3724 | 122.0169 | 122.4426 | -122.4976 | -122.493
987.2812 | 122.5113 | -61.1618 | 61.0977 | 0.0096895 | 0.0019312 | 0.014172 | 0.025919 | 0.041644 | -0.034054 | 0.056499 | -61.3083 | 61.171 | -61.3632 | -61.2076 | 60.8047 | 0.15564 | -0.009155 | 0.10986 | 61.2671 | -61.3632 | -0.20142 | 0.073242 | -0.14649 | -0.045777 | -0.29297 | -0.20142 | 0.16937 | 0.054931 | 61.1526 | 61.2717 | 121.9666 | 122.3328 | -0.14649 | 122.4289 | 61.3174 | -0.20142 | 122.3328 | -0.14649 | 61.3174 | 121.9666 | 122.4289 | -122.4609 | -122.4609
988.9844 | 122.5571 | -61.1343 | 61.1572 | 0.024948 | -0.00041862 | 0.013317 | 0.023569 | 0.040789 | -0.031277 | 0.059276 | -61.2534 | 61.1252 | -61.3632 | -61.1343 | 60.878 | 0.22888 | -0.24719 | 0.17395 | 61.1801 | -61.3632 | -0.22888 | -0.032044 | -0.11902 | 0 | -0.27924 | -0.22888 | 0.022888 | 0.10986 | 60.8871 | 61.3083 | 122.0123 | 122.2595 | -0.11902 | 122.3145 | 61.3632 | -0.22888 | 122.2595 | -0.11902 | 61.3632 | 122.0123 | 122.3145 | -122.5204 | -122.5204
990.75 | 122.5296 | -61.1435 | 61.171 | 0.0096895 | 0.0010766 | 0.013317 | 0.022287 | 0.039935 | -0.031063 | 0.059703 | -61.2122 | 61.1206 | -61.322 | -61.1114 | 60.9055 | 0.22888 | -0.25635 | 0.18768 | 61.2122 | -61.3495 | -0.17853 | -0.050354 | -0.068664 | 0.032044 | -0.2655 | -0.20599 | 0.041199 | 0.10986 | 60.8871 | 61.3312 | 122.049 | 122.2641 | -0.068664 | 122.3557 | 61.3724 | -0.20599 | 122.2641 | -0.068664 | 61.3724 | 122.049 | 122.3557 | -122.493 | -122.5204
992.4688 | 122.4747 | -61.1298 | 61.235 | 0.00206 | 0.00086298 | 0.0084039 | 0.023783 | 0.038653 | -0.033413 | 0.058849 | -61.1755 | 61.2076 | -61.2671 | -61.0931 | 60.9329 | 0.28381 | 0.045776 | 0.28839 | 61.3266 | -61.2991 | -0.13733 | -0.027465 | -0.045776 | 0.036621 | -0.30212 | -0.16937 | 0.091553 | 0.091553 | 61.1755 | 61.4182 | 122.0627 | 122.3373 | -0.045776 | 122.4564 | 61.4136 | -0.16937 | 122.3373 | -0.045776 | 61.4136 | 122.0627 | 122.4564 | -122.5021 | -122.5342
994.1875 | 122.5342 | -61.1114 | 61.1801 | 0.0096895 | -0.0014868 | 0.0077631 | 0.02656 | 0.039507 | -0.034481 | 0.057781 | -61.2213 | 61.1069 | -61.3266 | -61.1206 | 60.878 | 0.24261 | -0.26093 | 0.16937 | 61.2167 | -61.3266 | -0.21515 | -0.073242 | -0.10986 | -0.009155 | -0.30212 | -0.21515 | 0.036621 | 0.10529 | 60.8505 | 61.2808 | 121.9894 | 122.2183 | -0.10986 | 122.3282 | 61.3541 | -0.21515 | 122.2183 | -0.10986 | 61.3541 | 121.9894 | 122.3282 | -122.5067 | -122.5067
995.9531 | 122.58 | -61.1343 | 61.1114 | 0.00206 | 0.0027856 | 0.014813 | 0.028055 | 0.03908 | -0.031277 | 0.060558 | -61.3174 | 61.1847 | -61.3632 | -61.1938 | 60.791 | 0.13733 | -0.082397 | 0.082397 | 61.2534 | -61.3678 | -0.22888 | 0.073242 | -0.18311 | -0.05951 | -0.32043 | -0.23346 | 0.14191 | 0.045776 | 61.0519 | 61.2167 | 121.9254 | 122.319 | -0.18311 | 122.3877 | 61.2717 | -0.23346 | 122.319 | -0.18311 | 61.2717 | 121.9254 | 122.3877 | -122.4747 | -122.4792
997.7188 | 122.5342 | -61.1481 | 61.116 | 0.00206 | 0.002572 | 0.0092585 | 0.027628 | 0.041857 | -0.033413 | 0.058208 | -61.2991 | 61.1618 | -61.3724 | -61.1801 | 60.8276 | 0.17395 | -0.16479 | 0.1236 | 61.2396 | -61.3266 | -0.2243 | 0.045776 | -0.15106 | -0.032044 | -0.28839 | -0.17853 | 0.1236 | 0.073242 | 60.9833 | 61.2717 | 121.9757 | 122.3099 | -0.15106 | 122.3877 | 61.322 | -0.17853 | 122.3099 | -0.15106 | 61.322 | 121.9757 | 122.3877 | -122.4884 | -122.4426
999.4844 | 122.4243 | -61.171 | 61.1618 | 0.0096895 | 0.0019312 | 0.010967 | 0.02891 | 0.040575 | -0.034267 | 0.060131 | -61.203 | 61.2122 | -61.3174 | -61.0977 | 60.8917 | 0.25177 | -0.018311 | 0.24719 | 61.2991 | -61.2991 | -0.14648 | 0.050354 | -0.032044 | 0.073242 | -0.27008 | -0.12817 | 0.13733 | 0.11444 | 61.1526 | 61.4182 | 122.0627 | 122.3831 | -0.032044 | 122.4701 | 61.4227 | -0.12817 | 122.3831 | -0.032044 | 61.4227 | 122.0627 | 122.4701 | -122.4792 | -122.4609
1001.2188 | 122.4335 | -61.1114 | 61.2488 | 0.0096895 | 8.578e-06 | 0.01054 | 0.021646 | 0.037798 | -0.031917 | 0.059276 | -61.116 | 61.2259 | -61.2167 | -60.997 | 61.0062 | 0.36163 | -0.10986 | 0.3479 | 61.2808 | -61.2762 | -0.10529 | -0.022888 | -0.004578 | 0.11444 | -0.24261 | -0.1648 | 0.032044 | 0.10071 | 61.0016 | 61.4594 | 122.1176 | 122.3373 | -0.004578 | 122.3923 | 61.4731 | -0.1648 | 122.3373 | -0.004578 | 61.4731 | 122.1176 | 122.3923 | -122.4655 | -122.525
1002.9844 | 122.5204 | -61.1114 | 61.1572 | 0.00206 | -0.001914 | 0.011181 | 0.023569 | 0.040362 | -0.032345 | 0.058635 | -61.203 | 61.0794 | -61.2946 | -61.0886 | 60.9146 | 0.24261 | -0.2655 | 0.1831 | 61.2259 | -61.2946 | -0.18311 | -0.07782 | -0.091553 | 0.022888 | -0.24262 | -0.18311 | 0.068664 | 0.091553 | 60.8459 | 61.2946 | 122.0261 | 122.1909 | -0.091553 | 122.3373 | 61.3541 | -0.18311 | 122.1909 | -0.091553 | 61.3541 | 122.0261 | 122.3373 | -122.4518 | -122.4518
1004.7656 | 122.5708 | -61.1298 | 61.116 | 0.0096895 | 0.0053492 | 0.011608 | 0.028482 | 0.04143 | -0.035122 | 0.059917 | -61.2991 | 61.1938 | -61.3586 | -61.1984 | 60.7956 | 0.14191 | -0.027466 | 0.082397 | 61.2991 | -61.3495 | -0.22888 | 0.07782 | -0.16937 | -0.068664 | -0.32044 | -0.21973 | 0.1831 | 0.05951 | 61.1023 | 61.2122 | 121.9254 | 122.3236 | -0.16937 | 122.4289 | 61.2717 | -0.21973 | 122.3236 | -0.16937 | 61.2717 | 121.9254 | 122.4289 | -122.4747 | -122.4655
1006.5312 | 122.4472 | -61.1664 | 61.1618 | 0.017319 | 0.0010766 | 0.015667 | 0.030191 | 0.041857 | -0.032985 | 0.059703 | -61.1984 | 61.2213 | -61.2946 | -61.0703 | 60.91 | 0.26093 | -0.013733 | 0.25177 | 61.3083 | -61.3312 | -0.12817 | 0.059509 | -0.032043 | 0.096131 | -0.25177 | -0.16479 | 0.14649 | 0.096131 | 61.1526 | 61.4182 | 122.0764 | 122.3877 | -0.032043 | 122.4747 | 61.4273 | -0.16479 | 122.3877 | -0.032043 | 61.4273 | 122.0764 | 122.4747 | -122.4564 | -122.493
1008.3281 | 122.4426 | -61.1435 | 61.2122 | 0.0096895 | 0.0051356 | 0.010326 | 0.028055 | 0.042284 | -0.032558 | 0.058635 | -61.1755 | 61.2579 | -61.2946 | -61.0794 | 60.9192 | 0.25177 | -0.009155 | 0.2243 | 61.3129 | -61.3037 | -0.15106 | 0.045777 | -0.032043 | 0.064087 | -0.29297 | -0.16022 | 0.10071 | 0.11902 | 61.1343 | 61.3678 | 122.0627 | 122.4014 | -0.032043 | 122.4564 | 61.3953 | -0.16022 | 122.4014 | -0.032043 | 61.3953 | 122.0627 | 122.4564 | -122.5067 | -122.5159
1010.0469 | 122.5754 | -61.0519 | 61.203 | -0.0055695 | 0.0010766 | 0.0073359 | 0.021433 | 0.037798 | -0.029781 | 0.059276 | -61.2213 | 61.203 | -61.2625 | -61.1114 | 60.9329 | 0.22888 | -0.1236 | 0.18768 | 61.2854 | -61.3266 | -0.21057 | 0 | -0.16937 | -0.059509 | -0.27008 | -0.27466 | 0.082397 | 0.041199 | 60.9283 | 61.2396 | 121.9849 | 122.2549 | -0.16937 | 122.3373 | 61.2808 | -0.27466 | 122.2549 | -0.16937 | 61.2808 | 121.9849 | 122.3373 | -122.4655 | -122.5296
1011.8125 | 122.438 | -61.0931 | 61.2534 | 0.017319 | 0.0012902 | 0.0098993 | 0.024637 | 0.038012 | -0.034481 | 0.059276 | -61.1206 | 61.235 | -61.2305 | -60.9879 | 61.0199 | 0.32959 | -0.064087 | 0.33875 | 61.3358 | -61.2534 | -0.13733 | -0.018311 | -0.027465 | 0.10529 | -0.23346 | -0.16022 | 0.082397 | 0.10986 | 61.0291 | 61.4319 | 122.113 | 122.3282 | -0.027465 | 122.4289 | 61.4227 | -0.16022 | 122.3282 | -0.027465 | 61.4227 | 122.113 | 122.4289 | -122.4838 | -122.5067
1013.5312 | 122.4884 | -61.0977 | 61.235 | 0.0096895 | 0.0010766 | 0.012463 | 0.027414 | 0.040148 | -0.033413 | 0.05949 | -61.2167 | 61.2854 | -61.2625 | -61.0977 | 60.91 | 0.23346 | 0.13275 | 0.2243 | 61.377 | -61.2762 | -0.16479 | 0.050354 | -0.11902 | 0 | -0.32501 | -0.17853 | 0.14191 | 0.045776 | 61.2305 | 61.322 | 122.0078 | 122.3831 | -0.11902 | 122.4747 | 61.3312 | -0.17853 | 122.3831 | -0.11902 | 61.3312 | 122.0078 | 122.4747 | -122.4976 | -122.5113
1015.25 | 122.4426 | -61.0748 | 61.2717 | -0.0055695 | 0.0021448 | 0.010113 | 0.022287 | 0.040362 | -0.031704 | 0.059703 | -61.0931 | 61.2396 | -61.2305 | -60.9741 | 61.0245 | 0.32501 | -0.10986 | 0.32501 | 61.2854 | -61.29 | -0.15564 | -0.032043 | -0.018311 | 0.10071 | -0.24719 | -0.21515 | 0.013733 | 0.13733 | 60.965 | 61.3998 | 122.0993 | 122.3145 | -0.018311 | 122.3602 | 61.3998 | -0.21515 | 122.3145 | -0.018311 | 61.3998 | 122.0993 | 122.3602 | -122.5021 | -122.5616
1017.0312 | 122.4426 | -61.116 | 61.1938 | 0.00206 | 0.0036402 | 0.012676 | 0.029978 | 0.039721 | -0.035122 | 0.059703 | -61.1893 | 61.2762 | -61.2808 | -61.0519 | 60.9283 | 0.24719 | 0.068665 | 0.25177 | 61.3678 | -61.2717 | -0.16479 | 0.082397 | -0.073242 | 0.064087 | -0.2655 | -0.15564 | 0.17395 | 0.091553 | 61.1847 | 61.3678 | 122.0444 | 122.3923 | -0.073242 | 122.4838 | 61.3632 | -0.15564 | 122.3923 | -0.073242 | 61.3632 | 122.0444 | 122.4838 | -122.4747 | -122.4655
1018.8125 | 122.4884 | -61.0931 | 61.235 | 0.0096895 | 0.00064938 | 0.0096857 | 0.023783 | 0.03908 | -0.031063 | 0.060344 | -61.171 | 61.29 | -61.2442 | -61.0703 | 60.9558 | 0.26093 | 0.091553 | 0.24261 | 61.3586 | -61.2717 | -0.15106 | 0.054932 | -0.077819 | 0.022889 | -0.27923 | -0.17853 | 0.1236 | 0.073243 | 61.1847 | 61.3358 | 122.049 | 122.3831 | -0.077819 | 122.4518 | 61.3541 | -0.17853 | 122.3831 | -0.077819 | 61.3541 | 122.049 | 122.4518 | -122.4792 | -122.5067
1020.5469 | 122.438 | -61.0565 | 61.3037 | 0.00206 | 0.0032128 | 0.013958 | 0.024423 | 0.038653 | -0.032985 | 0.057994 | -61.084 | 61.235 | -61.2122 | -60.965 | 61.0474 | 0.35248 | -0.11444 | 0.34332 | 61.3174 | -61.2488 | -0.15564 | -0.068665 | -0.027465 | 0.091553 | -0.25635 | -0.19226 | 0.013733 | 0.12817 | 60.9421 | 61.3998 | 122.1039 | 122.2916 | -0.027465 | 122.374 | 61.409 | -0.19226 | 122.2916 | -0.027465 | 61.409 | 122.1039 | 122.374 | -122.5159 | -122.5525
1022.2812 | 122.4609 | -61.0657 | 61.2762 | 0.017319 | 0.00086298 | 0.010326 | 0.023783 | 0.038653 | -0.032131 | 0.058422 | -61.1023 | 61.2488 | -61.1801 | -61.0199 | 60.9924 | 0.29755 | 0.027466 | 0.3067 | 61.3495 | -61.235 | -0.11444 | -0.027466 | -0.036621 | 0.045777 | -0.28381 | -0.16937 | 0.073242 | 0.07782 | 61.0931 | 61.3724 | 122.0581 | 122.3145 | -0.036621 | 122.4152 | 61.3632 | -0.16937 | 122.3145 | -0.036621 | 61.3632 | 122.0581 | 122.4152 | -122.4564 | -122.5113
1024.0625 | 122.525 | -61.084 | 61.1847 | -0.0055695 | 0.0017176 | 0.010326 | 0.025919 | 0.041003 | -0.031917 | 0.059276 | -61.2259 | 61.1801 | -61.3129 | -61.0977 | 60.8963 | 0.1831 | -0.19684 | 0.15106 | 61.2854 | -61.3037 | -0.22888 | -0.004577 | -0.14191 | -0.013733 | -0.28839 | -0.21973 | 0.10071 | 0.086975 | 60.8871 | 61.235 | 121.9803 | 122.2641 | -0.14191 | 122.3694 | 61.2671 | -0.21973 | 122.2641 | -0.14191 | 61.2671 | 121.9803 | 122.3694 | -122.4976 | -122.4884
1025.8438 | 122.5845 | -61.0107 | 61.235 | -0.0055695 | -0.00084602 | 0.0092585 | 0.023569 | 0.037798 | -0.030636 | 0.058635 | -61.1572 | 61.203 | -61.235 | -61.0794 | 60.9375 | 0.24261 | -0.14191 | 0.16937 | 61.2808 | -61.2762 | -0.2243 | -0.032043 | -0.14648 | -0.068665 | -0.29755 | -0.2655 | 0.045777 | 0.077819 | 60.8688 | 61.1801 | 121.9482 | 122.2137 | -0.14648 | 122.2916 | 61.2534 | -0.2655 | 122.2137 | -0.14648 | 61.2534 | 121.9482 | 122.2916 | -122.4701 | -122.5113
1027.6406 | 122.438 | -61.0291 | 61.2717 | 0.0096895 | -0.0031958 | 0.0090447 | 0.024423 | 0.038439 | -0.031917 | 0.059276 | -61.1023 | 61.2213 | -61.235 | -60.9741 | 61.0291 | 0.32501 | -0.018311 | 0.34332 | 61.3449 | -61.2259 | -0.20599 | -0.050354 | -0.073242 | 0.054932 | -0.24261 | -0.19684 | 0.073243 | 0.13275 | 61.0107 | 61.3724 | 122.0581 | 122.2504 | -0.073242 | 122.374 | 61.3541 | -0.19684 | 122.2504 | -0.073242 | 61.3541 | 122.0581 | 122.374 | -122.5067 | -122.4976
1029.3438 | 122.5754 | -61.0199 | 61.2625 | -0.0055695 | 0.0036402 | 0.0096857 | 0.025492 | 0.038866 | -0.03384 | 0.057781 | -61.171 | 61.2442 | -61.235 | -61.0382 | 60.9512 | 0.24719 | -0.13733 | 0.21057 | 61.3129 | -61.2625 | -0.21515 | -0.01831 | -0.15106 | -0.018311 | -0.31128 | -0.24262 | 0.050354 | 0.064087 | 60.8826 | 61.2305 | 121.9711 | 122.2641 | -0.15106 | 122.3328 | 61.2671 | -0.24262 | 122.2641 | -0.15106 | 61.2671 | 121.9711 | 122.3328 | -122.4976 | -122.525
1031.125 | 122.4426 | -61.1114 | 61.2076 | 0.00206 | 0.0027856 | 0.011181 | 0.033182 | 0.043139 | -0.035122 | 0.058635 | -61.1618 | 61.2625 | -61.2762 | -61.0611 | 60.9055 | 0.18768 | -0.013733 | 0.1831 | 61.3586 | -61.2488 | -0.1648 | 0.054931 | -0.050354 | 0.050354 | -0.30212 | -0.13733 | 0.15106 | 0.11444 | 61.0977 | 61.2946 | 122.0169 | 122.374 | -0.050354 | 122.4701 | 61.2991 | -0.13733 | 122.374 | -0.050354 | 61.2991 | 122.0169 | 122.4701 | -122.4838 | -122.4564
1032.8438 | 122.5571 | -60.9741 | 61.2671 | 0.0096895 | 0.00022218 | 0.0092585 | 0.022501 | 0.039721 | -0.031277 | 0.058635 | -61.1664 | 61.2305 | -61.2396 | -61.0428 | 60.9558 | 0.24719 | -0.13275 | 0.20599 | 61.3129 | -61.2717 | -0.2655 | -0.036621 | -0.19226 | -0.068665 | -0.31128 | -0.29755 | 0.045776 | 0.073242 | 60.8414 | 61.1801 | 121.9299 | 122.2046 | -0.19226 | 122.287 | 61.2213 | -0.29755 | 122.2046 | -0.19226 | 61.2213 | 121.9299 | 122.287 | -122.5067 | -122.5388
1034.625 | 122.4701 | -61.0703 | 61.2488 | 0.00206 | 0.0027856 | 0.010326 | 0.028482 | 0.038226 | -0.035763 | 0.059917 | -61.1618 | 61.3312 | -61.2534 | -61.0382 | 60.9375 | 0.24261 | 0.09613 | 0.21973 | 61.3953 | -61.2122 | -0.18311 | 0.082398 | -0.091553 | 0.032043 | -0.31128 | -0.14191 | 0.14648 | 0.091553 | 61.1664 | 61.29 | 122.0078 | 122.4014 | -0.091553 | 122.4655 | 61.3129 | -0.14191 | 122.4014 | -0.091553 | 61.3129 | 122.0078 | 122.4655 | -122.5021 | -122.4609
1036.3438 | 122.4701 | -61.0611 | 61.2762 | 0.017319 | 0.0010766 | 0.010754 | 0.027628 | 0.039935 | -0.031063 | 0.061199 | -61.1526 | 61.3358 | -61.2305 | -61.0428 | 60.9375 | 0.23804 | 0.09613 | 0.23346 | 61.3815 | -61.2259 | -0.16937 | 0.059509 | -0.091553 | 0.01831 | -0.33875 | -0.16479 | 0.10529 | 0.07782 | 61.1572 | 61.2946 | 121.9986 | 122.3969 | -0.091553 | 122.4426 | 61.2991 | -0.16479 | 122.3969 | -0.091553 | 61.2991 | 121.9986 | 122.4426 | -122.5067 | -122.5021
1038.125 | 122.4976 | -61.0153 | 61.2671 | 0.00206 | 0.0021448 | 0.0090447 | 0.025064 | 0.039294 | -0.032558 | 0.058635 | -61.1389 | 61.3358 | -61.2167 | -61.0382 | 60.965 | 0.25177 | 0.13733 | 0.21515 | 61.4182 | -61.2167 | -0.20142 | 0.068664 | -0.1236 | -0.022888 | -0.30212 | -0.20142 | 0.15106 | 0.07782 | 61.1526 | 61.2305 | 121.9803 | 122.3511 | -0.1236 | 122.4335 | 61.2671 | -0.20142 | 122.3511 | -0.1236 | 61.2671 | 121.9803 | 122.4335 | -122.4838 | -122.4838
1039.9062 | 122.5571 | -61.0657 | 61.1664 | 0.00206 | 0.00064938 | 0.013958 | 0.027201 | 0.041216 | -0.034481 | 0.05949 | -61.2259 | 61.2259 | -61.2946 | -61.1114 | 60.8688 | 0.14191 | -0.11902 | 0.073242 | 61.3037 | -61.2762 | -0.22888 | 0.059509 | -0.16022 | -0.045776 | -0.29755 | -0.21057 | 0.13733 | 0.068665 | 60.9467 | 61.1389 | 121.9345 | 122.2916 | -0.16022 | 122.3694 | 61.2076 | -0.21057 | 122.2916 | -0.16022 | 61.2076 | 121.9345 | 122.3694 | -122.4609 | -122.4426
1041.6875 | 122.5525 | -61.0336 | 61.1893 | 0.017319 | 0.0044946 | 0.01289 | 0.027414 | 0.040148 | -0.032772 | 0.05949 | -61.2213 | 61.2534 | -61.2625 | -61.1252 | 60.8871 | 0.15106 | -0.045776 | 0.091553 | 61.3586 | -61.2991 | -0.22888 | 0.064087 | -0.18768 | -0.091553 | -0.30212 | -0.2655 | 0.16937 | 0.041199 | 60.9879 | 61.1252 | 121.9208 | 122.287 | -0.18768 | 122.3923 | 61.1847 | -0.2655 | 122.287 | -0.18768 | 61.1847 | 121.9208 | 122.3923 | -122.4518 | -122.4884
1043.4688 | 122.4243 | -61.1023 | 61.2305 | 0.0096895 | 0.0032128 | 0.011822 | 0.026987 | 0.042498 | -0.034267 | 0.05949 | -61.1206 | 61.2808 | -61.235 | -61.0291 | 60.9512 | 0.22888 | 0.004578 | 0.21515 | 61.3724 | -61.2305 | -0.13275 | 0.050354 | -0.01831 | 0.073242 | -0.27924 | -0.12817 | 0.14191 | 0.11444 | 61.1069 | 61.3174 | 122.0535 | 122.3831 | -0.01831 | 122.4747 | 61.3312 | -0.12817 | 122.3831 | -0.01831 | 61.3312 | 122.0535 | 122.4747 | -122.4655 | -122.4609
1045.1875 | 122.4518 | -61.0474 | 61.2625 | 0.00206 | 0.0021448 | 0.0096857 | 0.025492 | 0.041003 | -0.033413 | 0.05949 | -61.116 | 61.3358 | -61.1893 | -61.0153 | 60.9787 | 0.26093 | 0.064087 | 0.24261 | 61.4044 | -61.2076 | -0.14191 | 0.073242 | -0.068665 | 0.032043 | -0.28381 | -0.16022 | 0.14191 | 0.073242 | 61.1114 | 61.29 | 122.0261 | 122.3831 | -0.068665 | 122.4518 | 61.3083 | -0.16022 | 122.3831 | -0.068665 | 61.3083 | 122.0261 | 122.4518 | -122.4518 | -122.4701
1046.9688 | 122.5067 | -61.0382 | 61.235 | 0.00206 | -0.0021276 | 0.011395 | 0.022287 | 0.040148 | -0.033626 | 0.061626 | -61.1435 | 61.171 | -61.2167 | -61.0107 | 60.9741 | 0.24719 | -0.28839 | 0.18768 | 61.2854 | -61.2167 | -0.17853 | -0.064087 | -0.10529 | 0.027466 | -0.26093 | -0.17853 | 0.050354 | 0.073242 | 60.7498 | 61.2259 | 122.0123 | 122.2092 | -0.10529 | 122.3236 | 61.2854 | -0.17853 | 122.2092 | -0.10529 | 61.2854 | 122.0123 | 122.3236 | -122.4518 | -122.4518
1048.75 | 122.4152 | -60.9695 | 61.3495 | 0.00206 | 0.00064938 | 0.0081903 | 0.022501 | 0.039507 | -0.03149 | 0.059062 | -61.0107 | 61.322 | -61.1343 | -60.9055 | 61.0931 | 0.36621 | -0.091553 | 0.34332 | 61.3815 | -61.1481 | -0.16479 | -0.027466 | -0.041199 | 0.064086 | -0.25635 | -0.17853 | 0.032044 | 0.1236 | 60.878 | 61.3129 | 122.0627 | 122.2916 | -0.041199 | 122.3511 | 61.3358 | -0.17853 | 122.2916 | -0.041199 | 61.3358 | 122.0627 | 122.3511 | -122.4838 | -122.4976
1050.5312 | 122.5525 | -60.9695 | 61.2991 | 0.00206 | 0.00086298 | 0.012249 | 0.022501 | 0.038439 | -0.032345 | 0.059062 | -61.1206 | 61.2717 | -61.1572 | -61.0428 | 60.9695 | 0.22888 | -0.12817 | 0.19226 | 61.3586 | -61.1893 | -0.18768 | -0.027466 | -0.15106 | -0.073243 | -0.32959 | -0.21973 | 0.05951 | 0.036622 | 60.8414 | 61.1618 | 121.9391 | 122.2412 | -0.15106 | 122.3282 | 61.1984 | -0.21973 | 122.2412 | -0.15106 | 61.1984 | 121.9391 | 122.3282 | -122.4564 | -122.4884
1052.3125 | 122.5067 | -60.9833 | 61.2671 | 0.0096895 | 0.00064938 | 0.010754 | 0.025278 | 0.040575 | -0.032558 | 0.058849 | -61.1023 | 61.1755 | -61.2305 | -60.9833 | 61.0016 | 0.24719 | -0.27466 | 0.19226 | 61.3037 | -61.2167 | -0.24719 | -0.091553 | -0.11902 | 0 | -0.2655 | -0.23346 | 0.036621 | 0.12817 | 60.7086 | 61.1755 | 121.9849 | 122.1588 | -0.11902 | 122.287 | 61.2305 | -0.23346 | 122.1588 | -0.11902 | 61.2305 | 121.9849 | 122.287 | -122.4976 | -122.4838
1054.0312 | 122.5845 | -60.965 | 61.2854 | 0.0096895 | 0.002572 | 0.0079767 | 0.025064 | 0.037585 | -0.031063 | 0.059703 | -61.116 | 61.2991 | -61.171 | -61.0016 | 60.9924 | 0.25177 | -0.15106 | 0.17395 | 61.3678 | -61.2122 | -0.20599 | 0.013733 | -0.15106 | -0.036621 | -0.29297 | -0.24719 | 0.082398 | 0.054931 | 60.8139 | 61.1389 | 121.9574 | 122.2641 | -0.15106 | 122.3328 | 61.2167 | -0.24719 | 122.2641 | -0.15106 | 61.2167 | 121.9574 | 122.3328 | -122.4564 | -122.4976
1055.7344 | 122.4976 | -60.9833 | 61.2534 | -0.0055695 | 0.0012902 | 0.014385 | 0.026987 | 0.04143 | -0.033626 | 0.059276 | -61.084 | 61.2167 | -61.2076 | -60.965 | 61.0016 | 0.24719 | -0.27924 | 0.19226 | 61.3083 | -61.2167 | -0.22431 | -0.036621 | -0.10071 | 0.01831 | -0.25177 | -0.23346 | 0.054932 | 0.1236 | 60.704 | 61.1755 | 121.9849 | 122.2 | -0.10071 | 122.2916 | 61.2305 | -0.23346 | 122.2 | -0.10071 | 61.2305 | 121.9849 | 122.2916 | -122.4609 | -122.4701
1057.5 | 122.5433 | -60.9467 | 61.2854 | 0.00206 | 0.0021448 | 0.0079767 | 0.02421 | 0.040362 | -0.034267 | 0.057353 | -61.0977 | 61.29 | -61.1755 | -60.9741 | 61.0153 | 0.24719 | -0.14191 | 0.21973 | 61.3586 | -61.203 | -0.22888 | 0.004578 | -0.15106 | -0.027466 | -0.27008 | -0.25635 | 0.073243 | 0.07782 | 60.8047 | 61.1664 | 121.962 | 122.2366 | -0.15106 | 122.3053 | 61.1938 | -0.25635 | 122.2366 | -0.15106 | 61.1938 | 121.962 | 122.3053 | -122.4609 | -122.4884
1059.2188 | 122.406 | -61.0519 | 61.2854 | 0.017319 | 0.0012902 | 0.0090447 | 0.029123 | 0.040789 | -0.035122 | 0.059917 | -61.0748 | 61.3174 | -61.1893 | -60.9787 | 60.9741 | 0.25635 | -0.022888 | 0.2243 | 61.3861 | -61.1847 | -0.13733 | 0.032044 | -0.022888 | 0.073242 | -0.31128 | -0.13275 | 0.10071 | 0.11444 | 61.0291 | 61.2762 | 122.0261 | 122.3694 | -0.022888 | 122.438 | 61.3083 | -0.13275 | 122.3694 | -0.022888 | 61.3083 | 122.0261 | 122.438 | -122.4747 | -122.4701
1061 | 122.525 | -60.9833 | 61.2625 | -0.0055695 | 0.0017176 | 0.010967 | 0.028055 | 0.040575 | -0.031917 | 0.060985 | -61.1206 | 61.2671 | -61.203 | -61.0107 | 60.9695 | 0.21515 | -0.20599 | 0.14648 | 61.3083 | -61.2167 | -0.21973 | 0.004578 | -0.13733 | -0.027466 | -0.29297 | -0.23346 | 0.045777 | 0.082398 | 60.7773 | 61.1298 | 121.9528 | 122.2504 | -0.13733 | 122.2916 | 61.1984 | -0.23346 | 122.2504 | -0.13733 | 61.1984 | 121.9528 | 122.2916 | -122.4655 | -122.4792
1062.7656 | 122.5616 | -60.9604 | 61.2946 | -0.0055695 | 0.0012902 | 0.0090447 | 0.024637 | 0.041216 | -0.030636 | 0.058849 | -61.0794 | 61.2854 | -61.1526 | -61.0016 | 61.0107 | 0.22888 | -0.16479 | 0.17395 | 61.377 | -61.1893 | -0.19226 | -0.009156 | -0.11902 | -0.041199 | -0.28381 | -0.22888 | 0.082397 | 0.073242 | 60.7956 | 61.1343 | 121.9711 | 122.2458 | -0.11902 | 122.3373 | 61.1893 | -0.22888 | 122.2458 | -0.11902 | 61.1893 | 121.9711 | 122.3373 | -122.4472 | -122.4838
1064.4688 | 122.4152 | -60.9604 | 61.3678 | 0.00206 | 0.0049218 | 0.0084039 | 0.023142 | 0.038439 | -0.03384 | 0.058635 | -60.997 | 61.3358 | -61.116 | -60.8688 | 61.0931 | 0.34332 | 0 | 0.35248 | 61.4685 | -61.1343 | -0.15564 | -0.032044 | -0.036621 | 0.091553 | -0.27466 | -0.17395 | 0.10071 | 0.11902 | 60.9604 | 61.3129 | 122.0535 | 122.2961 | -0.036621 | 122.4289 | 61.3037 | -0.17395 | 122.2961 | -0.036621 | 61.3037 | 122.0535 | 122.4289 | -122.4838 | -122.5021
1066.1875 | 122.406 | -60.9467 | 61.3724 | 0.00206 | 0.002572 | 0.010113 | 0.02421 | 0.038653 | -0.032985 | 0.058422 | -60.9833 | 61.3495 | -61.1114 | -60.8505 | 61.1343 | 0.37079 | -0.10529 | 0.35248 | 61.4182 | -61.116 | -0.16479 | -0.022888 | -0.036621 | 0.09613 | -0.23804 | -0.16937 | 0.045777 | 0.12817 | 60.8414 | 61.2991 | 122.081 | 122.2961 | -0.036621 | 122.3648 | 61.3174 | -0.16937 | 122.2961 | -0.036621 | 61.3174 | 122.081 | 122.3648 | -122.4838 | -122.4884
1067.8906 | 122.4518 | -60.9879 | 61.3266 | 0.0096895 | 0.0023584 | 0.013744 | 0.029764 | 0.039294 | -0.03384 | 0.059917 | -61.0703 | 61.4136 | -61.1618 | -60.9421 | 61.0245 | 0.25177 | 0.10986 | 0.25177 | 61.4731 | -61.1298 | -0.17395 | 0.086975 | -0.082397 | 0.045776 | -0.30212 | -0.14191 | 0.14648 | 0.091553 | 61.0977 | 61.2396 | 122.0123 | 122.4014 | -0.082397 | 122.4609 | 61.2396 | -0.14191 | 122.4014 | -0.082397 | 61.2396 | 122.0123 | 122.4609 | -122.4884 | -122.4564
1069.6094 | 122.4518 | -61.0291 | 61.2854 | 0.00206 | 0.004281 | 0.0075495 | 0.028696 | 0.039294 | -0.034267 | 0.059276 | -61.0977 | 61.3312 | -61.203 | -60.997 | 60.9512 | 0.16479 | -0.018311 | 0.13733 | 61.4227 | -61.2259 | -0.17395 | 0.045777 | -0.068664 | 0.032044 | -0.33417 | -0.19684 | 0.13733 | 0.10529 | 61.0107 | 61.1664 | 121.9803 | 122.3602 | -0.068664 | 122.4518 | 61.1938 | -0.19684 | 122.3602 | -0.068664 | 61.1938 | 121.9803 | 122.4518 | -122.4884 | -122.5113
1071.3438 | 122.5525 | -60.9009 | 61.3129 | -0.0055695 | 0.0010766 | 0.015881 | 0.023142 | 0.039721 | -0.031277 | 0.058422 | -61.0565 | 61.3266 | -61.116 | -60.9512 | 61.0245 | 0.22888 | -0.16022 | 0.19226 | 61.4044 | -61.1526 | -0.21515 | 0.013733 | -0.15564 | -0.050354 | -0.28839 | -0.25177 | 0.091553 | 0.059509 | 60.7407 | 61.0931 | 121.9254 | 122.2275 | -0.15564 | 122.3053 | 61.1298 | -0.25177 | 122.2275 | -0.15564 | 61.1298 | 121.9254 | 122.3053 | -122.4289 | -122.4655
1073.1406 | 122.406 | -60.9375 | 61.3678 | 0.017319 | 0.00086298 | 0.011395 | 0.025705 | 0.03908 | -0.031277 | 0.058208 | -60.9375 | 61.377 | -61.0657 | -60.8276 | 61.1389 | 0.36621 | -0.10529 | 0.34332 | 61.4456 | -61.1069 | -0.12817 | 0.009155 | 0 | 0.10986 | -0.22888 | -0.16937 | 0.07782 | 0.12817 | 60.8322 | 61.2808 | 122.0764 | 122.3145 | 0 | 122.3831 | 61.3037 | -0.16937 | 122.3145 | 0 | 61.3037 | 122.0764 | 122.3831 | -122.4335 | -122.4747
1074.9219 | 122.4609 | -60.9833 | 61.2762 | 0.00206 | 0.0021448 | 0.012676 | 0.029337 | 0.040789 | -0.033199 | 0.062267 | -61.0977 | 61.3403 | -61.1893 | -61.0062 | 60.9604 | 0.16937 | -0.009155 | 0.12817 | 61.4365 | -61.1664 | -0.20599 | 0.064087 | -0.11444 | -0.022889 | -0.31586 | -0.18311 | 0.16022 | 0.091553 | 60.9741 | 61.1114 | 121.9437 | 122.3236 | -0.11444 | 122.4197 | 61.1526 | -0.18311 | 122.3236 | -0.11444 | 61.1526 | 121.9437 | 122.4197 | -122.4655 | -122.4426
1076.6875 | 122.5433 | -60.9604 | 61.2534 | 0.00206 | 0.0034266 | 0.012249 | 0.026987 | 0.04143 | -0.031063 | 0.059276 | -61.1298 | 61.3998 | -61.1435 | -61.0199 | 60.9467 | 0.14191 | -0.036621 | 0.073242 | 61.4273 | -61.1984 | -0.18311 | 0.14648 | -0.16937 | -0.059509 | -0.3067 | -0.23804 | 0.17395 | 0.013733 | 60.9238 | 61.0336 | 121.907 | 122.3602 | -0.16937 | 122.3877 | 61.1023 | -0.23804 | 122.3602 | -0.16937 | 61.1023 | 121.907 | 122.3877 | -122.3969 | -122.4518
1078.4219 | 122.4884 | -60.9604 | 61.2991 | 0.0096895 | 0.00086298 | 0.0098993 | 0.027628 | 0.043566 | -0.032985 | 0.060344 | -61.1023 | 61.3632 | -61.1664 | -60.9879 | 60.9833 | 0.15564 | -0.009155 | 0.10529 | 61.4548 | -61.1618 | -0.20599 | 0.064087 | -0.14191 | -0.027466 | -0.31586 | -0.20142 | 0.15564 | 0.064087 | 60.9512 | 61.0657 | 121.9437 | 122.3236 | -0.14191 | 122.4152 | 61.116 | -0.20142 | 122.3236 | -0.14191 | 61.116 | 121.9437 | 122.4152 | -122.4655 | -122.4609
1080.1406 | 122.493 | -60.9238 | 61.3403 | 0.0096895 | 0.0019312 | 0.013104 | 0.023783 | 0.040575 | -0.030422 | 0.060985 | -61.0199 | 61.2991 | -61.1343 | -60.91 | 61.0703 | 0.25635 | -0.27466 | 0.20142 | 61.377 | -61.171 | -0.21057 | -0.041199 | -0.09613 | 0.013733 | -0.27008 | -0.24719 | 0.036621 | 0.11444 | 60.6491 | 61.1252 | 121.994 | 122.2229 | -0.09613 | 122.3007 | 61.1801 | -0.24719 | 122.2229 | -0.09613 | 61.1801 | 121.994 | 122.3007 | -122.4747 | -122.5113
1081.9219 | 122.4197 | -60.8917 | 61.4319 | 0.00206 | 8.578e-06 | 0.011822 | 0.020578 | 0.039294 | -0.032985 | 0.059703 | -60.9421 | 61.377 | -61.0565 | -60.8002 | 61.1801 | 0.35706 | -0.13275 | 0.3479 | 61.4456 | -61.0565 | -0.16479 | -0.054932 | -0.050354 | 0.091553 | -0.25177 | -0.16479 | 0.013733 | 0.11444 | 60.759 | 61.2396 | 122.0718 | 122.2687 | -0.050354 | 122.3373 | 61.2488 | -0.16479 | 122.2687 | -0.050354 | 61.2488 | 122.0718 | 122.3373 | -122.4884 | -122.4884
1083.6406 | 122.4152 | -60.91 | 61.4273 | 0.00206 | 0.0019312 | 0.011395 | 0.025278 | 0.039721 | -0.034694 | 0.056713 | -60.9329 | 61.4044 | -61.0291 | -60.8093 | 61.1755 | 0.35248 | -0.009155 | 0.3479 | 61.4639 | -61.0657 | -0.11902 | -0.022888 | -0.022888 | 0.10071 | -0.25177 | -0.15564 | 0.036621 | 0.096131 | 60.9009 | 61.2579 | 122.0856 | 122.3145 | -0.022888 | 122.374 | 61.2625 | -0.15564 | 122.3145 | -0.022888 | 61.2625 | 122.0856 | 122.374 | -122.4564 | -122.493
1085.4219 | 122.4472 | -60.9009 | 61.3953 | 0.0096895 | 0.001504 | 0.0037043 | 0.025705 | 0.038226 | -0.030208 | 0.059276 | -60.965 | 61.4639 | -61.0336 | -60.8963 | 61.1069 | 0.2655 | 0.09613 | 0.25635 | 61.5143 | -61.0748 | -0.13275 | 0.068664 | -0.064087 | 0.004578 | -0.28839 | -0.17395 | 0.11902 | 0.068664 | 60.997 | 61.1572 | 122.0078 | 122.3648 | -0.064087 | 122.4152 | 61.1664 | -0.17395 | 122.3648 | -0.064087 | 61.1664 | 122.0078 | 122.4152 | -122.4289 | -122.4701
1087.1406 | 122.5296 | -60.91 | 61.3174 | 0.0096895 | 0.0027856 | 0.0086175 | 0.028482 | 0.039294 | -0.032131 | 0.057994 | -61.0794 | 61.3861 | -61.1389 | -60.9879 | 60.9787 | 0.13733 | -0.045776 | 0.086975 | 61.4502 | -61.171 | -0.22888 | 0.068664 | -0.16937 | -0.07782 | -0.33875 | -0.26093 | 0.13275 | 0.059509 | 60.8643 | 60.997 | 121.8887 | 122.2961 | -0.16937 | 122.3602 | 61.0474 | -0.26093 | 122.2961 | -0.16937 | 61.0474 | 121.8887 | 122.3602 | -122.4564 | -122.4884
1088.9375 | 122.4609 | -60.8963 | 61.3998 | 0.00206 | 0.0057764 | 0.0098993 | 0.025278 | 0.036944 | -0.030849 | 0.058635 | -60.9695 | 61.496 | -61.0565 | -60.878 | 61.1069 | 0.24719 | 0.1236 | 0.24261 | 61.5372 | -61.1023 | -0.16022 | 0.096131 | -0.073242 | 0.01831 | -0.29297 | -0.20599 | 0.13733 | 0.086976 | 61.0199 | 61.1389 | 122.0032 | 122.3923 | -0.073242 | 122.4335 | 61.1435 | -0.20599 | 122.3923 | -0.073242 | 61.1435 | 122.0032 | 122.4335 | -122.4564 | -122.5021
1090.7188 | 122.5021 | -60.9055 | 61.3312 | 0.0096895 | 0.0027856 | 0.016949 | 0.029123 | 0.040362 | -0.032558 | 0.059062 | -61.0336 | 61.441 | -61.1343 | -60.9512 | 61.0016 | 0.16479 | 0.004578 | 0.10986 | 61.4822 | -61.1114 | -0.22888 | 0.10986 | -0.12817 | -0.045776 | -0.32959 | -0.20599 | 0.15106 | 0.10071 | 60.91 | 61.0153 | 121.907 | 122.3465 | -0.12817 | 122.3877 | 61.0703 | -0.20599 | 122.3465 | -0.12817 | 61.0703 | 121.907 | 122.3877 | -122.4655 | -122.4426
1092.4844 | 122.5479 | -60.8871 | 61.3358 | 0.017319 | 0.0017176 | 0.013104 | 0.026132 | 0.03908 | -0.031704 | 0.059917 | -61.0519 | 61.4227 | -61.1206 | -60.9741 | 61.0016 | 0.13733 | -0.054932 | 0.068665 | 61.5189 | -61.1069 | -0.23346 | 0.086975 | -0.16479 | -0.086975 | -0.33417 | -0.21973 | 0.18311 | 0.068664 | 60.8322 | 60.9558 | 121.8887 | 122.3099 | -0.16479 | 122.406 | 61.0245 | -0.21973 | 122.3099 | -0.16479 | 61.0245 | 121.8887 | 122.406 | -122.4564 | -122.4426
1094.2031 | 122.4472 | -60.8322 | 61.4456 | 0.0096895 | 0.0010766 | 0.011822 | 0.022501 | 0.038866 | -0.03149 | 0.057567 | -60.9421 | 61.4914 | -61.0382 | -60.8505 | 61.1343 | 0.27008 | 0.10529 | 0.24261 | 61.5829 | -61.0245 | -0.20599 | 0.045776 | -0.10986 | -0.018311 | -0.31128 | -0.19226 | 0.13733 | 0.09613 | 60.9375 | 61.0748 | 121.9666 | 122.3236 | -0.10986 | 122.4152 | 61.1023 | -0.19226 | 122.3236 | -0.10986 | 61.1023 | 121.9666 | 122.4152 | -122.4838 | -122.4701
1095.9844 | 122.4472 | -60.8871 | 61.3907 | 0.00206 | 0.0053492 | 0.010967 | 0.028696 | 0.041644 | -0.032985 | 0.05949 | -61.0016 | 61.4594 | -61.0611 | -60.9146 | 61.0382 | 0.17395 | -0.013733 | 0.1236 | 61.5189 | -61.0886 | -0.17395 | 0.068665 | -0.11444 | -0.027466 | -0.35248 | -0.20142 | 0.12817 | 0.059509 | 60.8734 | 61.0107 | 121.9254 | 122.3465 | -0.11444 | 122.406 | 61.0611 | -0.20142 | 122.3465 | -0.11444 | 61.0611 | 121.9254 | 122.406 | -122.4518 | -122.4792
1097.6875 | 122.438 | -60.8414 | 61.4182 | 0.00206 | 0.0040674 | 0.0094721 | 0.026132 | 0.040362 | -0.031277 | 0.061626 | -60.9467 | 61.5005 | -61.0107 | -60.8368 | 61.1298 | 0.26093 | 0.10986 | 0.21515 | 61.5967 | -60.9924 | -0.16937 | 0.082397 | -0.10529 | 0.004578 | -0.28839 | -0.15106 | 0.17853 | 0.064087 | 60.9512 | 61.0565 | 121.9711 | 122.3419 | -0.10529 | 122.4381 | 61.1023 | -0.15106 | 122.3419 | -0.10529 | 61.1023 | 121.9711 | 122.4381 | -122.4289 | -122.4106
1099.4688 | 122.525 | -60.7681 | 61.4456 | 0.00206 | 0.0029992 | 0.012676 | 0.020578 | 0.039721 | -0.03149 | 0.059917 | -60.9558 | 61.4502 | -61.0062 | -60.8505 | 61.1618 | 0.24261 | -0.1236 | 0.19226 | 61.5326 | -61.0336 | -0.23804 | 0.004577 | -0.18768 | -0.082398 | -0.28381 | -0.2655 | 0.086975 | 0.050354 | 60.6445 | 60.9604 | 121.9299 | 122.2183 | -0.18768 | 122.3007 | 61.0107 | -0.2655 | 122.2183 | -0.18768 | 61.0107 | 121.9299 | 122.3007 | -122.4518 | -122.4792
1101.1875 | 122.4106 | -60.8826 | 61.4319 | 0.00206 | 0.00064938 | 0.011608 | 0.030618 | 0.043139 | -0.034267 | 0.058635 | -60.91 | 61.4685 | -61.0382 | -60.8276 | 61.1343 | 0.24719 | -0.004578 | 0.21973 | 61.5875 | -61.0016 | -0.15564 | 0.036621 | -0.027466 | 0.054931 | -0.29755 | -0.11902 | 0.15564 | 0.12817 | 60.878 | 61.1023 | 122.0169 | 122.3511 | -0.027466 | 122.4701 | 61.1298 | -0.11902 | 122.3511 | -0.027466 | 61.1298 | 122.0169 | 122.4701 | -122.4701 | -122.4335
1102.9688 | 122.3969 | -60.8643 | 61.4227 | 0.00206 | 0.002572 | 0.014172 | 0.027841 | 0.04143 | -0.034481 | 0.059276 | -60.8917 | 61.4914 | -61.0291 | -60.8002 | 61.1618 | 0.28381 | 0 | 0.24719 | 61.5875 | -61.0062 | -0.16479 | 0.068665 | -0.027466 | 0.064087 | -0.26093 | -0.14191 | 0.1648 | 0.13733 | 60.8643 | 61.1114 | 122.0261 | 122.3557 | -0.027466 | 122.4518 | 61.1481 | -0.14191 | 122.3557 | -0.027466 | 61.1481 | 122.0261 | 122.4518 | -122.4518 | -122.4289
1104.75 | 122.3877 | -60.8688 | 61.4548 | -0.0055695 | 0.0034266 | 0.013744 | 0.02891 | 0.040575 | -0.031917 | 0.059062 | -60.878 | 61.5051 | -60.9741 | -60.8002 | 61.1618 | 0.27466 | 0 | 0.25177 | 61.5967 | -61.0474 | -0.10529 | 0.050354 | -0.009156 | 0.068664 | -0.29297 | -0.17853 | 0.14191 | 0.09613 | 60.8688 | 61.1206 | 122.0306 | 122.374 | -0.009156 | 122.4655 | 61.1435 | -0.17853 | 122.374 | -0.009156 | 61.1435 | 122.0306 | 122.4655 | -122.4289 | -122.5021
1106.5312 | 122.4426 | -60.7864 | 61.5005 | 0.0096895 | -0.0010596 | 0.01054 | 0.024851 | 0.038439 | -0.034481 | 0.058635 | -60.8643 | 61.5097 | -60.9512 | -60.7727 | 61.2259 | 0.29297 | 0.068665 | 0.28381 | 61.6333 | -60.9695 | -0.1648 | 0.009156 | -0.07782 | 0.013733 | -0.27466 | -0.18311 | 0.13275 | 0.086975 | 60.8551 | 61.0703 | 122.0123 | 122.2961 | -0.07782 | 122.4197 | 61.0794 | -0.18311 | 122.2961 | -0.07782 | 61.0794 | 122.0123 | 122.4197 | -122.4518 | -122.4701
1108.2656 | 122.3969 | -60.8139 | 61.5005 | 0.00206 | 0.001504 | 0.0096857 | 0.028696 | 0.041857 | -0.032985 | 0.05949 | -60.8643 | 61.5463 | -60.9604 | -60.759 | 61.2076 | 0.27008 | 0.018311 | 0.23804 | 61.6104 | -60.965 | -0.14648 | 0.045777 | -0.050354 | 0.054932 | -0.29297 | -0.15106 | 0.10986 | 0.09613 | 60.8322 | 61.0519 | 122.0215 | 122.3602 | -0.050354 | 122.4243 | 61.084 | -0.15106 | 122.3602 | -0.050354 | 61.084 | 122.0215 | 122.4243 | -122.4609 | -122.4655
1110.0469 | 122.4976 | -60.7544 | 61.5005 | 0.0096895 | 0.0010766 | 0.0092585 | 0.023142 | 0.040148 | -0.033199 | 0.058849 | -60.8551 | 61.4548 | -60.9558 | -60.7452 | 61.2167 | 0.27008 | -0.24719 | 0.18768 | 61.5189 | -60.9879 | -0.20142 | -0.045776 | -0.10071 | 0.009156 | -0.28381 | -0.23346 | 0.018311 | 0.10071 | 60.5072 | 60.9421 | 121.9711 | 122.2092 | -0.10071 | 122.2733 | 61.0245 | -0.23346 | 122.2092 | -0.10071 | 61.0245 | 121.9711 | 122.2733 | -122.4564 | -122.4884
1111.8125 | 122.4884 | -60.7407 | 61.4685 | 0.0096895 | 0.0034266 | 0.0090447 | 0.027201 | 0.041644 | -0.03384 | 0.061412 | -60.8963 | 61.496 | -60.9604 | -60.7956 | 61.1847 | 0.20599 | -0.19226 | 0.15564 | 61.5829 | -60.965 | -0.21973 | 0.027466 | -0.15564 | -0.054931 | -0.28381 | -0.2243 | 0.11444 | 0.064087 | 60.5484 | 60.8963 | 121.9254 | 122.2366 | -0.15564 | 122.3236 | 60.9467 | -0.2243 | 122.2366 | -0.15564 | 60.9467 | 121.9254 | 122.3236 | -122.4289 | -122.4335
1113.5938 | 122.4564 | -60.7681 | 61.4594 | 0.017319 | 0.0034266 | 0.01289 | 0.028269 | 0.041216 | -0.035122 | 0.058208 | -60.9055 | 61.5189 | -60.9924 | -60.8185 | 61.1389 | 0.16022 | -0.009155 | 0.10529 | 61.6379 | -60.9879 | -0.22431 | 0.059509 | -0.13733 | -0.050354 | -0.32043 | -0.21973 | 0.17853 | 0.086975 | 60.759 | 60.8734 | 121.907 | 122.287 | -0.13733 | 122.406 | 60.9283 | -0.21973 | 122.287 | -0.13733 | 60.9283 | 121.907 | 122.406 | -122.4518 | -122.4472
1115.3125 | 122.4838 | -60.7361 | 61.5189 | 0.0096895 | 0.0010766 | 0.0047723 | 0.024637 | 0.041644 | -0.033413 | 0.060344 | -60.8368 | 61.4822 | -60.9467 | -60.7407 | 61.2442 | 0.25177 | -0.24719 | 0.17395 | 61.5555 | -60.965 | -0.21057 | -0.036621 | -0.10071 | -0.004578 | -0.27466 | -0.22888 | 0.036621 | 0.10986 | 60.4889 | 60.91 | 121.9803 | 122.2183 | -0.10071 | 122.2916 | 60.9879 | -0.22888 | 122.2183 | -0.10071 | 60.9879 | 121.9803 | 122.2916 | -122.4655 | -122.4838
1117.1094 | 122.4014 | -60.7315 | 61.528 | -0.0055695 | 0.002572 | 0.01054 | 0.02656 | 0.041216 | -0.033626 | 0.058849 | -60.8139 | 61.5921 | -60.9055 | -60.6995 | 61.2534 | 0.27008 | 0.064087 | 0.24719 | 61.6974 | -60.9055 | -0.17395 | 0.064087 | -0.082398 | 0.032043 | -0.27466 | -0.17395 | 0.16937 | 0.091553 | 60.7956 | 60.9787 | 121.9849 | 122.3236 | -0.082398 | 122.4289 | 61.0016 | -0.17395 | 122.3236 | -0.082398 | 61.0016 | 121.9849 | 122.4289 | -122.4335 | -122.4335
1118.9062 | 122.3969 | -60.6857 | 61.6241 | 0.00206 | -0.0017004 | 0.0084039 | 0.021219 | 0.036517 | -0.032345 | 0.059703 | -60.7086 | 61.5738 | -60.8139 | -60.5988 | 61.3815 | 0.35706 | -0.082397 | 0.36163 | 61.6425 | -60.8963 | -0.12817 | -0.050354 | -0.022888 | 0.086975 | -0.24262 | -0.21057 | 0.01831 | 0.10529 | 60.6033 | 61.0474 | 122.0673 | 122.2595 | -0.022888 | 122.3282 | 61.0428 | -0.21057 | 122.2595 | -0.022888 | 61.0428 | 122.0673 | 122.3282 | -122.4381 | -122.5204
1120.6719 | 122.525 | -60.6583 | 61.5646 | 0.0096895 | 0.00086298 | 0.010967 | 0.02421 | 0.037798 | -0.035335 | 0.059703 | -60.8093 | 61.528 | -60.8643 | -60.7086 | 61.2625 | 0.2243 | -0.17395 | 0.17395 | 61.6562 | -60.8826 | -0.20599 | -0.036621 | -0.15106 | -0.050354 | -0.30212 | -0.2243 | 0.091553 | 0.054932 | 60.4843 | 60.8322 | 121.9208 | 122.1863 | -0.15106 | 122.3145 | 60.8826 | -0.2243 | 122.1863 | -0.15106 | 60.8826 | 121.9208 | 122.3145 | -122.4289 | -122.4472
1122.3906 | 122.5021 | -60.6491 | 61.5967 | 0.00206 | 8.578e-06 | 0.010326 | 0.024637 | 0.041216 | -0.034481 | 0.059276 | -60.7636 | 61.528 | -60.8688 | -60.6903 | 61.2671 | 0.24719 | -0.23346 | 0.1831 | 61.6425 | -60.8963 | -0.21973 | -0.068665 | -0.11444 | -0.041199 | -0.32959 | -0.24719 | 0.045776 | 0.10528 | 60.4156 | 60.8322 | 121.9162 | 122.1771 | -0.11444 | 122.2916 | 60.8963 | -0.24719 | 122.1771 | -0.11444 | 60.8963 | 121.9162 | 122.2916 | -122.4655 | -122.493
1124.1719 | 122.4701 | -60.672 | 61.5601 | 0.00206 | 0.00043578 | 0.0092585 | 0.027414 | 0.04143 | -0.033626 | 0.060131 | -60.8047 | 61.5555 | -60.8826 | -60.6766 | 61.2808 | 0.23804 | -0.24261 | 0.18768 | 61.6287 | -60.8871 | -0.21057 | -0.004578 | -0.13275 | -0.004578 | -0.27924 | -0.21515 | 0.068664 | 0.077819 | 60.4294 | 60.8597 | 121.9528 | 122.2275 | -0.13275 | 122.3007 | 60.91 | -0.21515 | 122.2275 | -0.13275 | 60.91 | 121.9528 | 122.3007 | -122.4426 | -122.4472
1125.875 | 122.5479 | -60.64 | 61.6104 | 0.0096895 | 0.0029992 | 0.014172 | 0.023996 | 0.040575 | -0.032131 | 0.058635 | -60.7681 | 61.5829 | -60.8185 | -60.672 | 61.2991 | 0.24719 | -0.15106 | 0.17853 | 61.6837 | -60.8688 | -0.17853 | -0.027466 | -0.12817 | -0.032043 | -0.31128 | -0.22888 | 0.073242 | 0.050354 | 60.4889 | 60.8185 | 121.9391 | 122.2229 | -0.12817 | 122.3236 | 60.8871 | -0.22888 | 122.2229 | -0.12817 | 60.8871 | 121.9391 | 122.3236 | -122.4289 | -122.4792
1127.6562 | 122.4335 | -60.6354 | 61.6562 | 0.0096895 | 0.00022218 | 0.012249 | 0.027841 | 0.039294 | -0.032985 | 0.059276 | -60.7315 | 61.6745 | -60.8047 | -60.6125 | 61.3312 | 0.25635 | 0.09613 | 0.24719 | 61.7661 | -60.8185 | -0.16937 | 0.018311 | -0.09613 | 0.022888 | -0.32501 | -0.1831 | 0.10986 | 0.073243 | 60.7315 | 60.8826 | 121.9666 | 122.3099 | -0.09613 | 122.4014 | 60.8917 | -0.1831 | 122.3099 | -0.09613 | 60.8917 | 121.9666 | 122.4014 | -122.4609 | -122.4747
1129.4531 | 122.493 | -60.5804 | 61.6608 | -0.0055695 | -0.00041862 | 0.0084039 | 0.023783 | 0.039507 | -0.032985 | 0.059917 | -60.6628 | 61.6608 | -60.7544 | -60.5484 | 61.4182 | 0.33875 | -0.1236 | 0.3067 | 61.7432 | -60.7956 | -0.17395 | 0 | -0.082398 | 0.032043 | -0.24262 | -0.21515 | 0.082397 | 0.091553 | 60.4568 | 60.8871 | 121.9986 | 122.2412 | -0.082398 | 122.3236 | 60.9192 | -0.21515 | 122.2412 | -0.082398 | 60.9192 | 121.9986 | 122.3236 | -122.4152 | -122.4564
1131.1875 | 122.5159 | -60.5621 | 61.6653 | 0.00206 | 0.0012902 | 0.0071221 | 0.02421 | 0.036517 | -0.02914 | 0.057994 | -60.6903 | 61.647 | -60.7819 | -60.5804 | 61.3861 | 0.28839 | -0.14191 | 0.23804 | 61.7249 | -60.8139 | -0.21973 | -0.01831 | -0.12817 | -0.01831 | -0.27924 | -0.25177 | 0.05951 | 0.091552 | 60.4202 | 60.8002 | 121.9482 | 122.2092 | -0.12817 | 122.287 | 60.8505 | -0.25177 | 122.2092 | -0.12817 | 60.8505 | 121.9482 | 122.287 | -122.4472 | -122.4792
1132.9688 | 122.3602 | -60.6354 | 61.6653 | 0.0096895 | 0.0049218 | 0.014813 | 0.030618 | 0.036517 | -0.03384 | 0.059703 | -60.6674 | 61.7157 | -60.8002 | -60.553 | 61.3678 | 0.27008 | -0.004578 | 0.24719 | 61.7844 | -60.8231 | -0.16479 | 0.050354 | -0.032043 | 0.082397 | -0.29755 | -0.18768 | 0.11902 | 0.13275 | 60.6308 | 60.8826 | 122.0032 | 122.3511 | -0.032043 | 122.4197 | 60.9055 | -0.18768 | 122.3511 | -0.032043 | 60.9055 | 122.0032 | 122.4197 | -122.4655 | -122.4884
1134.75 | 122.525 | -60.553 | 61.6837 | 0.0096895 | 0.00086298 | 0.012676 | 0.025064 | 0.039721 | -0.033413 | 0.058849 | -60.6812 | 61.6516 | -60.7544 | -60.5713 | 61.3861 | 0.24719 | -0.18768 | 0.16937 | 61.7249 | -60.7773 | -0.20142 | -0.032044 | -0.12817 | -0.01831 | -0.29755 | -0.2243 | 0.041199 | 0.073243 | 60.3653 | 60.7224 | 121.9391 | 122.2046 | -0.12817 | 122.2778 | 60.8002 | -0.2243 | 122.2046 | -0.12817 | 60.8002 | 121.9391 | 122.2778 | -122.4381 | -122.4609
1136.4844 | 122.3785 | -60.585 | 61.6882 | 0.00206 | 0.0027856 | 0.013958 | 0.029764 | 0.037585 | -0.034694 | 0.059703 | -60.6445 | 61.7432 | -60.7636 | -60.5209 | 61.3953 | 0.27008 | 0.036621 | 0.26093 | 61.8484 | -60.7407 | -0.17853 | 0.054932 | -0.059509 | 0.064087 | -0.29297 | -0.15564 | 0.16022 | 0.11902 | 60.6216 | 60.8459 | 121.9803 | 122.3282 | -0.059509 | 122.4335 | 60.8551 | -0.15564 | 122.3282 | -0.059509 | 60.8551 | 121.9803 | 122.4335 | -122.4518 | -122.4289
1138.1875 | 122.4747 | -60.5621 | 61.6562 | 0.00206 | 0.0017176 | 0.012463 | 0.02955 | 0.040148 | -0.031917 | 0.060771 | -60.7224 | 61.7203 | -60.791 | -60.6033 | 61.322 | 0.17395 | 0 | 0.11902 | 61.821 | -60.7819 | -0.22888 | 0.064087 | -0.16022 | -0.041199 | -0.33417 | -0.21973 | 0.1648 | 0.068665 | 60.5621 | 60.6812 | 121.8842 | 122.2824 | -0.16022 | 122.3831 | 60.7361 | -0.21973 | 122.2824 | -0.16022 | 60.7361 | 121.8842 | 122.3831 | -122.4472 | -122.438
1139.9531 | 122.4747 | -60.4889 | 61.734 | 0.0096895 | 0.0017176 | 0.011608 | 0.023355 | 0.038439 | -0.032131 | 0.059276 | -60.6079 | 61.6745 | -60.7086 | -60.498 | 61.4502 | 0.24719 | -0.28381 | 0.18768 | 61.7569 | -60.7315 | -0.21973 | -0.059509 | -0.11902 | -0.009155 | -0.28381 | -0.24261 | 0.022888 | 0.10071 | 60.2051 | 60.6766 | 121.9391 | 122.1634 | -0.11902 | 122.2458 | 60.7361 | -0.24261 | 122.1634 | -0.11902 | 60.7361 | 121.9391 | 122.2458 | -122.4426 | -122.4655
1141.7188 | 122.4197 | -60.5118 | 61.7523 | 0.0096895 | 0.0036402 | 0.013104 | 0.028696 | 0.042284 | -0.031917 | 0.05949 | -60.5713 | 61.8622 | -60.6766 | -60.4568 | 61.496 | 0.27008 | 0.054932 | 0.24261 | 61.9308 | -60.6628 | -0.16479 | 0.10986 | -0.059509 | 0.054932 | -0.25635 | -0.15106 | 0.17853 | 0.10529 | 60.5667 | 60.7544 | 122.0078 | 122.374 | -0.059509 | 122.4426 | 60.7819 | -0.15106 | 122.374 | -0.059509 | 60.7819 | 122.0078 | 122.4426 | -122.4289 | -122.4152
1143.4375 | 122.5204 | -60.4202 | 61.8027 | 0.017319 | 0.00086298 | 0.0086175 | 0.020578 | 0.037798 | -0.031704 | 0.058849 | -60.5667 | 61.7752 | -60.6033 | -60.4568 | 61.5005 | 0.25177 | -0.19684 | 0.18768 | 61.853 | -60.6766 | -0.18311 | -0.027465 | -0.14648 | -0.036621 | -0.30212 | -0.25635 | 0.050354 | 0.036622 | 60.2234 | 60.6079 | 121.9208 | 122.1954 | -0.14648 | 122.2733 | 60.672 | -0.25635 | 122.1954 | -0.14648 | 60.672 | 121.9208 | 122.2733 | -122.406 | -122.4792
1145.1562 | 122.4747 | -60.4111 | 61.8256 | 0.0096895 | 8.578e-06 | 0.0096857 | 0.026346 | 0.037371 | -0.030422 | 0.058849 | -60.5118 | 61.7844 | -60.6125 | -60.4019 | 61.5417 | 0.27008 | -0.2655 | 0.20142 | 61.8576 | -60.6308 | -0.20142 | -0.041199 | -0.10071 | 0.009155 | -0.28381 | -0.21973 | 0.032043 | 0.10071 | 60.1456 | 60.6125 | 121.9528 | 122.1954 | -0.10071 | 122.2687 | 60.6812 | -0.21973 | 122.1954 | -0.10071 | 60.6812 | 121.9528 | 122.2687 | -122.4381 | -122.4564
1146.9219 | 122.4701 | -60.4111 | 61.821 | 0.0096895 | 8.578e-06 | 0.0084039 | 0.026987 | 0.039507 | -0.033626 | 0.060558 | -60.4935 | 61.7889 | -60.6262 | -60.4019 | 61.5463 | 0.26093 | -0.27466 | 0.17395 | 61.8668 | -60.6125 | -0.21515 | -0.032044 | -0.082397 | 0.009155 | -0.27466 | -0.20142 | 0.045776 | 0.13275 | 60.1364 | 60.585 | 121.9574 | 122.2 | -0.082397 | 122.2778 | 60.672 | -0.20142 | 122.2 | -0.082397 | 60.672 | 121.9574 | 122.2778 | -122.4472 | -122.4335
1148.6875 | 122.5204 | -60.2966 | 61.8896 | 0.00206 | 0.00086298 | 0.012463 | 0.023355 | 0.037585 | -0.029995 | 0.05949 | -60.4752 | 61.8668 | -60.5301 | -60.3699 | 61.5921 | 0.25177 | -0.17853 | 0.17395 | 61.9308 | -60.5942 | -0.23346 | -0.022888 | -0.17853 | -0.073242 | -0.29755 | -0.29755 | 0.041199 | 0.054931 | 60.1181 | 60.4706 | 121.8887 | 122.1634 | -0.17853 | 122.2275 | 60.5484 | -0.29755 | 122.1634 | -0.17853 | 60.5484 | 121.8887 | 122.2275 | -122.4197 | -122.4838
1150.4844 | 122.5204 | -60.2737 | 61.9354 | -0.013199 | 0.0010766 | 0.011395 | 0.022501 | 0.03908 | -0.03149 | 0.058635 | -60.4385 | 61.9629 | -60.4935 | -60.3287 | 61.6196 | 0.25635 | -0.14191 | 0.1831 | 61.9904 | -60.5759 | -0.21973 | 0.027466 | -0.16479 | -0.054931 | -0.31586 | -0.30212 | 0.054931 | 0.054931 | 60.1318 | 60.4568 | 121.8933 | 122.2366 | -0.16479 | 122.2641 | 60.5301 | -0.30212 | 122.2366 | -0.16479 | 60.5301 | 121.8933 | 122.2641 | -122.4289 | -122.5113
1152.2031 | 122.5113 | -60.2737 | 61.8942 | 0.0096895 | 0.0010766 | 0.011181 | 0.030405 | 0.040148 | -0.034267 | 0.061199 | -60.4614 | 61.9446 | -60.5255 | -60.3653 | 61.5555 | 0.15564 | -0.050354 | 0.086975 | 62.0865 | -60.5118 | -0.25177 | 0.050354 | -0.18768 | -0.091552 | -0.33875 | -0.23804 | 0.19226 | 0.064087 | 60.2234 | 60.3607 | 121.8292 | 122.2183 | -0.18768 | 122.3602 | 60.4294 | -0.23804 | 122.2183 | -0.18768 | 60.4294 | 121.8292 | 122.3602 | -122.4197 | -122.406
1153.9844 | 122.374 | -60.3241 | 61.9583 | 0.0096895 | 0.0049218 | 0.012035 | 0.029764 | 0.040575 | -0.033626 | 0.058635 | -60.347 | 62.0361 | -60.4477 | -60.2325 | 61.6791 | 0.28839 | -0.027466 | 0.25177 | 62.1048 | -60.4797 | -0.1236 | 0.07782 | -0.022888 | 0.091553 | -0.27924 | -0.15564 | 0.14648 | 0.10071 | 60.2966 | 60.5759 | 122.0032 | 122.3602 | -0.022888 | 122.4289 | 60.6125 | -0.15564 | 122.3602 | -0.022888 | 60.6125 | 122.0032 | 122.4289 | -122.406 | -122.438
1155.6875 | 122.5204 | -60.141 | 62.0407 | 0.00206 | 0.0017176 | 0.0084039 | 0.022074 | 0.040148 | -0.029781 | 0.058208 | -60.3333 | 62.059 | -60.3561 | -60.2097 | 61.7477 | 0.26093 | -0.15564 | 0.17853 | 62.114 | -60.4202 | -0.21515 | 0.018311 | -0.19226 | -0.068665 | -0.29297 | -0.27924 | 0.073243 | 0.022888 | 59.9854 | 60.3195 | 121.8887 | 122.2 | -0.19226 | 122.2549 | 60.4019 | -0.27924 | 122.2 | -0.19226 | 60.4019 | 121.8887 | 122.2549 | -122.3969 | -122.4609
1157.4844 | 122.5067 | -60.1639 | 62.0178 | -0.0055695 | 0.0038538 | 0.0077631 | 0.029764 | 0.04143 | -0.034908 | 0.059703 | -60.3424 | 62.114 | -60.4248 | -60.2417 | 61.702 | 0.17853 | -0.050354 | 0.068665 | 62.1597 | -60.4156 | -0.26093 | 0.096131 | -0.17853 | -0.07782 | -0.31586 | -0.25177 | 0.14191 | 0.082398 | 60.1135 | 60.2325 | 121.8658 | 122.2778 | -0.17853 | 122.3236 | 60.3424 | -0.25177 | 122.2778 | -0.17853 | 60.3424 | 121.8658 | 122.3236 | -122.4426 | -122.4335
1159.2031 | 122.3831 | -60.1181 | 62.1552 | 0.00206 | 0.00064938 | 0.014599 | 0.029764 | 0.039935 | -0.033199 | 0.060344 | -60.1822 | 62.178 | -60.2921 | -60.0906 | 61.8484 | 0.23804 | -0.018311 | 0.17395 | 62.3108 | -60.2966 | -0.17395 | 0.022889 | -0.064087 | 0.027466 | -0.3067 | -0.17853 | 0.15564 | 0.10986 | 60.0998 | 60.2921 | 121.9666 | 122.2961 | -0.064087 | 122.4289 | 60.3561 | -0.17853 | 122.2961 | -0.064087 | 60.3561 | 121.9666 | 122.4289 | -122.4472 | -122.4518
1160.9844 | 122.493 | -60.0403 | 62.1597 | -0.0055695 | 0.0047082 | 0.016308 | 0.027414 | 0.041003 | -0.030849 | 0.061199 | -60.1959 | 62.233 | -60.2646 | -60.0906 | 61.8393 | 0.19684 | -0.15106 | 0.10986 | 62.2742 | -60.2554 | -0.2243 | 0.073242 | -0.15564 | -0.050354 | -0.32043 | -0.21515 | 0.11444 | 0.068664 | 59.8892 | 60.1501 | 121.8796 | 122.2733 | -0.15564 | 122.3145 | 60.2371 | -0.21515 | 122.2733 | -0.15564 | 60.2371 | 121.8796 | 122.3145 | -122.4243 | -122.4152
1162.75 | 122.3419 | -60.0815 | 62.2009 | 0.0096895 | 0.0032128 | 0.014385 | 0.027201 | 0.040575 | -0.035122 | 0.060131 | -60.0998 | 62.2421 | -60.2325 | -60.0174 | 61.9263 | 0.28839 | -0.009155 | 0.23804 | 62.352 | -60.2005 | -0.15106 | 0.041198 | -0.01831 | 0.064087 | -0.27466 | -0.11902 | 0.15106 | 0.13275 | 60.0723 | 60.3195 | 122.0078 | 122.3236 | -0.01831 | 122.4335 | 60.3699 | -0.11902 | 122.3236 | -0.01831 | 60.3699 | 122.0078 | 122.4335 | -122.4335 | -122.4014
1164.5312 | 122.4426 | -59.967 | 62.2833 | -0.0055695 | 0.0029992 | 0.013104 | 0.02421 | 0.041216 | -0.032131 | 0.059917 | -60.0357 | 62.2696 | -60.1456 | -59.9258 | 62.027 | 0.28381 | -0.27466 | 0.21057 | 62.3245 | -60.1868 | -0.17853 | -0.013733 | -0.068665 | 0.041199 | -0.25635 | -0.21973 | 0.041199 | 0.10986 | 59.6924 | 60.1776 | 121.994 | 122.2366 | -0.068665 | 122.2916 | 60.2509 | -0.21973 | 122.2366 | -0.068665 | 60.2509 | 121.994 | 122.2916 | -122.4289 | -122.4701
1166.2656 | 122.4747 | -59.9442 | 62.2467 | 0.00206 | 0.001504 | 0.012463 | 0.025492 | 0.042071 | -0.031917 | 0.059917 | -60.0769 | 62.233 | -60.1913 | -59.967 | 61.9949 | 0.28839 | -0.25177 | 0.17395 | 62.3154 | -60.1822 | -0.24719 | -0.013733 | -0.13275 | -0.022888 | -0.25177 | -0.23804 | 0.068665 | 0.11444 | 59.6924 | 60.1181 | 121.9391 | 122.1771 | -0.13275 | 122.2595 | 60.2325 | -0.23804 | 122.1771 | -0.13275 | 60.2325 | 121.9391 | 122.2595 | -122.438 | -122.4289
1168.0469 | 122.4792 | -59.8755 | 62.352 | 0.00206 | 0.0029992 | 0.0049859 | 0.024637 | 0.037585 | -0.031277 | 0.060344 | -60.0037 | 62.3016 | -60.0998 | -59.9121 | 62.0316 | 0.28381 | -0.23346 | 0.18768 | 62.3611 | -60.1227 | -0.2243 | -0.050354 | -0.12817 | -0.036621 | -0.32044 | -0.24719 | 0.009155 | 0.09613 | 59.642 | 60.0632 | 121.907 | 122.1771 | -0.12817 | 122.2366 | 60.1593 | -0.24719 | 122.1771 | -0.12817 | 60.1593 | 121.907 | 122.2366 | -122.4518 | -122.4747
1169.7656 | 122.5204 | -59.8251 | 62.3795 | 0.00206 | 0.002572 | 0.0094721 | 0.023142 | 0.037585 | -0.031063 | 0.058849 | -60.0037 | 62.3566 | -60.0494 | -59.8755 | 62.0819 | 0.29755 | -0.13275 | 0.21057 | 62.4344 | -60.0677 | -0.2243 | -0.022889 | -0.17853 | -0.050354 | -0.29755 | -0.24262 | 0.054931 | 0.045776 | 59.6924 | 60.0357 | 121.907 | 122.1817 | -0.17853 | 122.2595 | 60.1227 | -0.24262 | 122.1817 | -0.17853 | 60.1227 | 121.907 | 122.2595 | -122.4289 | -122.4472
1171.5 | 122.374 | -59.8251 | 62.4847 | 0.0096895 | 0.002572 | 0.010967 | 0.025064 | 0.037585 | -0.032772 | 0.058635 | -59.8343 | 62.4435 | -59.967 | -59.7198 | 62.2009 | 0.39825 | -0.091553 | 0.35248 | 62.5259 | -59.9899 | -0.14191 | -0.041199 | -0.009156 | 0.10528 | -0.28381 | -0.16479 | 0.041199 | 0.13275 | 59.7336 | 60.1776 | 122.0261 | 122.2687 | -0.009156 | 122.3511 | 60.2234 | -0.16479 | 122.2687 | -0.009156 | 60.2234 | 122.0261 | 122.3511 | -122.4518 | -122.4747
1173.2188 | 122.4609 | -59.7656 | 62.4664 | 0.00206 | -0.00084602 | 0.0086175 | 0.026773 | 0.038012 | -0.031704 | 0.059276 | -59.8755 | 62.384 | -59.9808 | -59.7519 | 62.1643 | 0.27466 | -0.27924 | 0.19684 | 62.4939 | -60.0082 | -0.21515 | -0.082398 | -0.10986 | 0.013733 | -0.30212 | -0.24262 | 0.027465 | 0.10529 | 59.4864 | 59.9625 | 121.9299 | 122.1497 | -0.10986 | 122.2595 | 60.0403 | -0.24262 | 122.1497 | -0.10986 | 60.0403 | 121.9299 | 122.2595 | -122.4472 | -122.4747
1175 | 122.4243 | -59.7427 | 62.5168 | 0.00206 | 0.0038538 | 0.0094721 | 0.026132 | 0.038866 | -0.035763 | 0.059276 | -59.8572 | 62.59 | -59.9533 | -59.7382 | 62.1689 | 0.28839 | 0.10986 | 0.23804 | 62.6633 | -59.9396 | -0.21057 | 0.073242 | -0.11444 | 0.004578 | -0.3479 | -0.19684 | 0.14648 | 0.09613 | 59.8526 | 59.9808 | 121.9116 | 122.3328 | -0.11444 | 122.406 | 60.0311 | -0.19684 | 122.3328 | -0.11444 | 60.0311 | 121.9116 | 122.406 | -122.4701 | -122.4564
1176.7656 | 122.4014 | -59.6466 | 62.6221 | 0.0096895 | 0.0019312 | 0.0077631 | 0.025064 | 0.039721 | -0.031704 | 0.057994 | -59.7015 | 62.5809 | -59.8114 | -59.5642 | 62.3566 | 0.42114 | -0.13733 | 0.3479 | 62.6495 | -59.8709 | -0.16479 | -0.041198 | -0.054932 | 0.082397 | -0.2655 | -0.22431 | 0.027466 | 0.10986 | 59.5093 | 59.9945 | 122.0032 | 122.2275 | -0.054932 | 122.2961 | 60.0677 | -0.22431 | 122.2275 | -0.054932 | 60.0677 | 122.0032 | 122.2961 | -122.4335 | -122.493
1178.5469 | 122.4518 | -59.5963 | 62.5992 | 0.00206 | 0.0017176 | 0.015453 | 0.024851 | 0.038653 | -0.033199 | 0.058422 | -59.6878 | 62.5763 | -59.8389 | -59.5871 | 62.3199 | 0.30212 | -0.28381 | 0.19226 | 62.6633 | -59.8343 | -0.24262 | -0.022888 | -0.091553 | 0.009155 | -0.27924 | -0.23804 | 0.064087 | 0.15106 | 59.3124 | 59.7885 | 121.9162 | 122.1725 | -0.091553 | 122.2595 | 59.8984 | -0.23804 | 122.1725 | -0.091553 | 59.8984 | 121.9162 | 122.2595 | -122.438 | -122.4335
1180.2656 | 122.3648 | -59.5963 | 62.6816 | 0.00206 | 0.0012902 | 0.011822 | 0.029123 | 0.03908 | -0.034267 | 0.059276 | -59.642 | 62.677 | -59.7794 | -59.5459 | 62.3795 | 0.3067 | 0.013733 | 0.25177 | 62.8372 | -59.7336 | -0.18311 | -0.004578 | -0.045777 | 0.050354 | -0.30212 | -0.13733 | 0.15564 | 0.13733 | 59.61 | 59.848 | 121.9757 | 122.2733 | -0.045777 | 122.4335 | 59.903 | -0.13733 | 122.2733 | -0.045777 | 59.903 | 121.9757 | 122.4335 | -122.4609 | -122.4152
1182.0469 | 122.4472 | -59.5322 | 62.6816 | 0.00206 | 0.00086298 | 0.013744 | 0.023355 | 0.041644 | -0.03384 | 0.059917 | -59.6237 | 62.645 | -59.7565 | -59.5139 | 62.4115 | 0.32044 | -0.27466 | 0.18768 | 62.7548 | -59.729 | -0.2243 | -0.036622 | -0.091552 | 0.018311 | -0.27008 | -0.19684 | 0.073242 | 0.13275 | 59.2575 | 59.7198 | 121.9437 | 122.1771 | -0.091552 | 122.287 | 59.8526 | -0.19684 | 122.1771 | -0.091552 | 59.8526 | 121.9437 | 122.287 | -122.4381 | -122.4106
1183.7344 | 122.3694 | -59.5001 | 62.7869 | 0.00206 | 0.0032128 | 0.013744 | 0.027414 | 0.039935 | -0.034908 | 0.058635 | -59.5642 | 62.8281 | -59.6558 | -59.4406 | 62.4802 | 0.32501 | 0.027466 | 0.24261 | 62.8922 | -59.6466 | -0.15564 | 0.041199 | -0.064087 | 0.059509 | -0.3067 | -0.14648 | 0.10529 | 0.091553 | 59.5276 | 59.7427 | 121.9803 | 122.3282 | -0.064087 | 122.3923 | 59.8251 | -0.14648 | 122.3282 | -0.064087 | 59.8251 | 121.9803 | 122.3923 | -122.4426 | -122.4335
1185.5156 | 122.5067 | -59.3079 | 62.8738 | 0.0096895 | 0.0017176 | 0.0084039 | 0.020151 | 0.039721 | -0.032131 | 0.058635 | -59.4727 | 62.883 | -59.5184 | -59.3582 | 62.5809 | 0.3067 | -0.16022 | 0.1831 | 62.9562 | -59.5505 | -0.21057 | 0.009156 | -0.16479 | -0.050354 | -0.29297 | -0.24262 | 0.082398 | 0.045777 | 59.1476 | 59.491 | 121.8887 | 122.1909 | -0.16479 | 122.2641 | 59.6146 | -0.24262 | 122.1909 | -0.16479 | 59.6146 | 121.8887 | 122.2641 | -122.3923 | -122.4243
1187.2344 | 122.4197 | -59.2896 | 62.9242 | 0.0096895 | 0.00086298 | 0.010967 | 0.026987 | 0.038866 | -0.033626 | 0.059062 | -59.3948 | 63.0386 | -59.4498 | -59.3033 | 62.6404 | 0.32501 | 0.13275 | 0.24719 | 63.1485 | -59.4543 | -0.16022 | 0.11444 | -0.10528 | -0.013733 | -0.28381 | -0.16479 | 0.22431 | 0.054932 | 59.4223 | 59.5367 | 121.9299 | 122.3282 | -0.10528 | 122.4381 | 59.6146 | -0.16479 | 122.3282 | -0.10528 | 59.6146 | 121.9299 | 122.4381 | -122.374 | -122.3785
1188.9531 | 122.3877 | -59.2941 | 62.9471 | 0.0096895 | 0.0047082 | 0.0094721 | 0.031046 | 0.039721 | -0.034694 | 0.057994 | -59.3719 | 63.0157 | -59.4406 | -59.2987 | 62.6129 | 0.26093 | -0.036621 | 0.16479 | 63.089 | -59.4589 | -0.14648 | 0.068664 | -0.07782 | -0.004578 | -0.33417 | -0.16479 | 0.14191 | 0.068665 | 59.2575 | 59.4589 | 121.907 | 122.3099 | -0.07782 | 122.3831 | 59.5551 | -0.16479 | 122.3099 | -0.07782 | 59.5551 | 121.907 | 122.3831 | -122.3877 | -122.406
1190.6719 | 122.438 | -59.1843 | 63.0341 | 0.00206 | 0.0017176 | 0.013531 | 0.026132 | 0.041003 | -0.034267 | 0.060344 | -59.3079 | 63.0798 | -59.3994 | -59.1888 | 62.7411 | 0.3067 | -0.24261 | 0.16022 | 63.1531 | -59.3857 | -0.21515 | 0.045776 | -0.1236 | -0.004578 | -0.29297 | -0.20142 | 0.11902 | 0.091553 | 58.9417 | 59.3445 | 121.9254 | 122.2641 | -0.1236 | 122.3373 | 59.491 | -0.20142 | 122.2641 | -0.1236 | 59.491 | 121.9254 | 122.3373 | -122.4335 | -122.4197
1192.4531 | 122.4518 | -59.0836 | 63.0936 | 0.00206 | 0.0019312 | 0.012463 | 0.025492 | 0.041644 | -0.033626 | 0.05949 | -59.2117 | 63.1668 | -59.3216 | -59.1019 | 62.8281 | 0.28381 | -0.20142 | 0.17395 | 63.2126 | -59.3216 | -0.23804 | 0.073242 | -0.12817 | -0.018311 | -0.2655 | -0.23804 | 0.11902 | 0.10986 | 58.8821 | 59.2575 | 121.9116 | 122.2504 | -0.12817 | 122.2961 | 59.3674 | -0.23804 | 122.2504 | -0.12817 | 59.3674 | 121.9116 | 122.2961 | -122.4152 | -122.4152
1194.1875 | 122.438 | -59.0378 | 63.1622 | -0.0055695 | 0.0019312 | 0.010754 | 0.024851 | 0.040575 | -0.031917 | 0.058849 | -59.1248 | 63.1668 | -59.2346 | -59.024 | 62.8876 | 0.32044 | -0.27466 | 0.19684 | 63.2172 | -59.2712 | -0.19684 | 0.004578 | -0.086975 | 0.013733 | -0.27466 | -0.23346 | 0.054932 | 0.10986 | 58.7631 | 59.2346 | 121.9254 | 122.2046 | -0.086975 | 122.2549 | 59.3582 | -0.23346 | 122.2046 | -0.086975 | 59.3582 | 121.9254 | 122.2549 | -122.3969 | -122.4335
1195.9688 | 122.4976 | -58.8181 | 63.3591 | 0.0096895 | -0.002555 | 0.0088311 | 0.021646 | 0.039935 | -0.029781 | 0.060131 | -58.9417 | 63.2996 | -59.0607 | -58.8089 | 63.1073 | 0.35706 | -0.16937 | 0.21973 | 63.4918 | -59.0332 | -0.24262 | -0.059509 | -0.1236 | 0.009155 | -0.25177 | -0.21515 | 0.13275 | 0.11902 | 58.6487 | 59.0378 | 121.9254 | 122.1176 | -0.1236 | 122.3099 | 59.1751 | -0.21515 | 122.1176 | -0.1236 | 59.1751 | 121.9254 | 122.3099 | -122.4197 | -122.3923
1197.7344 | 122.4152 | -58.7082 | 63.5422 | 0.0096895 | 0.0021448 | 0.0084039 | 0.025492 | 0.036944 | -0.033626 | 0.058208 | -58.8181 | 63.6063 | -58.8776 | -58.7036 | 63.2217 | 0.33875 | 0.14648 | 0.25177 | 63.7207 | -58.8684 | -0.16937 | 0.064087 | -0.10986 | 0.004578 | -0.32043 | -0.16022 | 0.17853 | 0.059509 | 58.8547 | 58.96 | 121.9299 | 122.3145 | -0.10986 | 122.4289 | 59.0469 | -0.16022 | 122.3145 | -0.10986 | 59.0469 | 121.9299 | 122.4289 | -122.4197 | -122.4106
1199.4688 | 122.406 | -58.5526 | 63.6932 | 0.017319 | 0.0036402 | 0.0092585 | 0.027628 | 0.038866 | -0.034054 | 0.058635 | -58.6624 | 63.7894 | -58.7402 | -58.548 | 63.3591 | 0.35248 | 0.15106 | 0.26093 | 63.858 | -58.7585 | -0.18768 | 0.096131 | -0.10986 | 0.004577 | -0.33417 | -0.20599 | 0.16479 | 0.077819 | 58.7036 | 58.8135 | 121.9116 | 122.3419 | -0.10986 | 122.4106 | 58.905 | -0.20599 | 122.3419 | -0.10986 | 58.905 | 121.9116 | 122.4106 | -122.4335 | -122.4518
1201.25 | 122.4518 | -58.5342 | 63.6475 | 0.00206 | -0.00041862 | 0.01524 | 0.023355 | 0.037798 | -0.031917 | 0.059276 | -58.6533 | 63.6429 | -58.754 | -58.5617 | 63.3728 | 0.31128 | -0.25177 | 0.1831 | 63.707 | -58.7952 | -0.21973 | -0.004578 | -0.11902 | -0.027466 | -0.27466 | -0.26093 | 0.059509 | 0.10071 | 58.2825 | 58.7173 | 121.907 | 122.1771 | -0.11902 | 122.2412 | 58.8455 | -0.26093 | 122.1771 | -0.11902 | 58.8455 | 121.907 | 122.2412 | -122.4014 | -122.4426
1203.0312 | 122.3602 | -58.5022 | 63.7665 | 0.0096895 | 0.00086298 | 0.013317 | 0.02891 | 0.041003 | -0.034267 | 0.061199 | -58.5571 | 63.7894 | -58.6807 | -58.4702 | 63.4186 | 0.32959 | 0 | 0.21057 | 63.8763 | -58.6945 | -0.17853 | 0.022889 | -0.054932 | 0.032043 | -0.3479 | -0.19226 | 0.10986 | 0.1236 | 58.5022 | 58.7128 | 121.9208 | 122.2916 | -0.054932 | 122.3785 | 58.8318 | -0.19226 | 122.2916 | -0.054932 | 58.8318 | 121.9208 | 122.3785 | -122.4472 | -122.4609
1204.7344 | 122.4792 | -58.4198 | 63.7527 | -0.0055695 | 0.0023584 | 0.010113 | 0.026773 | 0.039721 | -0.034267 | 0.058635 | -58.5892 | 63.8626 | -58.6258 | -58.4885 | 63.4277 | 0.21973 | 0.009155 | 0.10529 | 63.9267 | -58.6121 | -0.20599 | 0.10986 | -0.16937 | -0.068664 | -0.32501 | -0.19226 | 0.17395 | 0.036621 | 58.429 | 58.5251 | 121.8475 | 122.2824 | -0.16937 | 122.3465 | 58.6395 | -0.19226 | 122.2824 | -0.16937 | 58.6395 | 121.8475 | 122.3465 | -122.3785 | -122.3648
1206.5156 | 122.493 | -58.3145 | 63.8535 | 0.017319 | 0.0023584 | 0.011395 | 0.027628 | 0.040362 | -0.032985 | 0.058849 | -58.5114 | 63.9175 | -58.5388 | -58.4335 | 63.4964 | 0.23804 | -0.027466 | 0.082397 | 63.9954 | -58.5159 | -0.2243 | 0.064087 | -0.19684 | -0.11902 | -0.35706 | -0.20142 | 0.14191 | 0.027465 | 58.287 | 58.3969 | 121.8109 | 122.2321 | -0.19684 | 122.3099 | 58.5526 | -0.20142 | 122.2321 | -0.19684 | 58.5526 | 121.8109 | 122.3099 | -122.3923 | -122.3694
1208.2969 | 122.3648 | -58.2367 | 64.0411 | 0.017319 | -0.0014868 | 0.0090447 | 0.018442 | 0.039507 | -0.031704 | 0.059062 | -58.2642 | 64.0182 | -58.3649 | -58.1268 | 63.8031 | 0.44861 | -0.07782 | 0.35248 | 64.1281 | -58.3694 | -0.12817 | -0.022888 | -0.027466 | 0.10986 | -0.23804 | -0.13275 | 0.086975 | 0.10071 | 58.1589 | 58.5892 | 122.0398 | 122.2549 | -0.027466 | 122.3648 | 58.6853 | -0.13275 | 122.2549 | -0.027466 | 58.6853 | 122.0398 | 122.3648 | -122.406 | -122.4106
1210.0312 | 122.5159 | -58.1039 | 64.064 | 0.00206 | 0.0029992 | 0.01289 | 0.023996 | 0.039507 | -0.033199 | 0.058422 | -58.2779 | 64.0686 | -58.3191 | -58.1543 | 63.7848 | 0.35706 | -0.14191 | 0.20142 | 64.1785 | -58.3603 | -0.21515 | 0.004578 | -0.17395 | -0.050354 | -0.27924 | -0.25635 | 0.11444 | 0.041199 | 57.962 | 58.3054 | 121.8887 | 122.1725 | -0.17395 | 122.2824 | 58.461 | -0.25635 | 122.1725 | -0.17395 | 58.461 | 121.8887 | 122.2824 | -122.3831 | -122.4243
1211.7969 | 122.3602 | -58.0719 | 64.2517 | -0.0055695 | -0.00041862 | 0.0075495 | 0.02656 | 0.037798 | -0.032131 | 0.060771 | -58.0902 | 64.2014 | -58.1955 | -57.9758 | 63.9587 | 0.45319 | -0.082397 | 0.37537 | 64.2563 | -58.2321 | -0.1236 | -0.050354 | -0.018311 | 0.09613 | -0.29297 | -0.16022 | 0.004578 | 0.10529 | 57.9895 | 58.4473 | 122.0306 | 122.2733 | -0.018311 | 122.3282 | 58.5251 | -0.16022 | 122.2733 | -0.018311 | 58.5251 | 122.0306 | 122.3282 | -122.4472 | -122.4838
1213.5938 | 122.374 | -58.0307 | 64.2288 | 0.017319 | 0.0021448 | 0.010326 | 0.030191 | 0.040575 | -0.032985 | 0.060131 | -58.0811 | 64.2563 | -58.1955 | -57.9987 | 63.8901 | 0.30212 | -0.004578 | 0.17853 | 64.3707 | -58.2184 | -0.16479 | 0.027466 | -0.050354 | 0.032044 | -0.33874 | -0.18768 | 0.14191 | 0.11444 | 58.0261 | 58.2092 | 121.9208 | 122.287 | -0.050354 | 122.4014 | 58.3328 | -0.18768 | 122.287 | -0.050354 | 58.3328 | 121.9208 | 122.4014 | -122.4243 | -122.4472
1215.3125 | 122.4197 | -57.8751 | 64.357 | 0.00206 | 0.0036402 | 0.014385 | 0.02656 | 0.040789 | -0.032985 | 0.060131 | -58.0032 | 64.4257 | -58.0948 | -57.8979 | 63.9999 | 0.36163 | 0.12817 | 0.23804 | 64.4897 | -58.0948 | -0.21973 | 0.068664 | -0.12817 | -0.022888 | -0.35706 | -0.21973 | 0.13275 | 0.091553 | 58.0032 | 58.1131 | 121.875 | 122.3007 | -0.12817 | 122.3648 | 58.2367 | -0.21973 | 122.3007 | -0.12817 | 58.2367 | 121.875 | 122.3648 | -122.4518 | -122.4518
1217.0781 | 122.406 | -57.8384 | 64.389 | 0.017319 | 0.0036402 | 0.0073359 | 0.025492 | 0.040148 | -0.031277 | 0.057567 | -57.9712 | 64.4852 | -58.0032 | -57.8567 | 64.064 | 0.33875 | 0.14648 | 0.22888 | 64.563 | -58.0261 | -0.16479 | 0.09613 | -0.13275 | -0.01831 | -0.32501 | -0.18768 | 0.17395 | 0.032044 | 57.9849 | 58.0673 | 121.9025 | 122.3236 | -0.13275 | 122.4014 | 58.1772 | -0.18768 | 122.3236 | -0.13275 | 58.1772 | 121.9025 | 122.4014 | -122.3923 | -122.4152
1218.8438 | 122.3557 | -57.7103 | 64.5538 | 0.00206 | 0.001504 | 0.010967 | 0.023569 | 0.03908 | -0.03384 | 0.061412 | -57.8064 | 64.5264 | -57.8751 | -57.6736 | 64.2426 | 0.41657 | -0.064087 | 0.34332 | 64.5721 | -57.93 | -0.1648 | -0.027466 | -0.09613 | 0.036621 | -0.31128 | -0.21973 | 0.018311 | 0.068665 | 57.6462 | 58.0536 | 121.9528 | 122.2366 | -0.09613 | 122.2824 | 58.1268 | -0.21973 | 122.2366 | -0.09613 | 58.1268 | 121.9528 | 122.2824 | -122.4289 | -122.4838
1220.5781 | 122.3785 | -57.6965 | 64.5264 | -0.013199 | 0.0019312 | 0.010326 | 0.027841 | 0.039721 | -0.033199 | 0.059917 | -57.811 | 64.563 | -57.9117 | -57.7286 | 64.1785 | 0.2655 | -0.013733 | 0.13733 | 64.6957 | -57.8934 | -0.21515 | 0.036621 | -0.11444 | -0.032044 | -0.3479 | -0.19684 | 0.16937 | 0.10071 | 57.6828 | 57.8339 | 121.875 | 122.2595 | -0.11444 | 122.3923 | 57.962 | -0.19684 | 122.2595 | -0.11444 | 57.962 | 121.875 | 122.3923 | -122.438 | -122.4197
1222.3594 | 122.4747 | -57.5226 | 64.6225 | 0.0096895 | 0.0027856 | 0.010967 | 0.022287 | 0.038226 | -0.028286 | 0.061199 | -57.7148 | 64.6408 | -57.756 | -57.5821 | 64.3524 | 0.36163 | -0.13733 | 0.23346 | 64.7232 | -57.7972 | -0.23346 | 0.01831 | -0.19226 | -0.059509 | -0.27008 | -0.27466 | 0.10071 | 0.041198 | 57.3853 | 57.756 | 121.875 | 122.1634 | -0.19226 | 122.2458 | 57.8842 | -0.27466 | 122.1634 | -0.19226 | 57.8842 | 121.875 | 122.2458 | -122.3785 | -122.4197
1224.1406 | 122.374 | -57.5226 | 64.7461 | 0.00206 | 8.578e-06 | 0.012676 | 0.023783 | 0.038012 | -0.033199 | 0.058849 | -57.5775 | 64.7324 | -57.6691 | -57.4585 | 64.4623 | 0.43945 | 0.027466 | 0.31128 | 64.8468 | -57.6874 | -0.14648 | -0.013733 | -0.054932 | 0.064087 | -0.28381 | -0.1648 | 0.10071 | 0.091552 | 57.55 | 57.8339 | 121.9849 | 122.2549 | -0.054932 | 122.3694 | 57.962 | -0.1648 | 122.2549 | -0.054932 | 57.962 | 121.9849 | 122.3694 | -122.4152 | -122.4335
1225.9219 | 122.3602 | -57.4493 | 64.8056 | -0.0055695 | 0.0053492 | 0.012249 | 0.029764 | 0.04143 | -0.033413 | 0.057781 | -57.4951 | 64.888 | -57.605 | -57.4219 | 64.4669 | 0.32501 | -0.013733 | 0.16937 | 64.9704 | -57.6187 | -0.15564 | 0.082397 | -0.045776 | 0.027466 | -0.33875 | -0.16937 | 0.16479 | 0.10986 | 57.4356 | 57.6187 | 121.9162 | 122.3373 | -0.045776 | 122.4197 | 57.7744 | -0.16937 | 122.3373 | -0.045776 | 57.7744 | 121.9162 | 122.4197 | -122.4106 | -122.4243
1227.7031 | 122.3877 | -56.8588 | 65.3229 | 0.0096895 | 0.0027856 | 0.013744 | 0.026132 | 0.038866 | -0.033413 | 0.059917 | -56.8497 | 65.5746 | -56.9183 | -56.7307 | 65.1901 | 0.56763 | 0.14191 | 0.27466 | 65.6845 | -56.9138 | -0.059509 | 0.25177 | 0.009156 | 0.12817 | -0.13275 | -0.054931 | 0.36163 | 0.068665 | 57.0007 | 57.1335 | 122.049 | 122.4335 | 0.009156 | 122.5433 | 57.4265 | -0.054931 | 122.4335 | 0.009156 | 57.4265 | 122.049 | 122.5433 | -122.2412 | -122.2366
1229.4219 | 122.3373 | -56.6711 | 65.5701 | 0.017319 | 8.578e-06 | 0.0086175 | 0.026773 | 0.038866 | -0.033413 | 0.05949 | -56.7078 | 65.6662 | -56.7947 | -56.575 | 65.3183 | 0.46234 | 0.032043 | 0.25635 | 65.7532 | -56.813 | -0.1236 | 0.096131 | -0.036621 | 0.096131 | -0.25177 | -0.14191 | 0.18311 | 0.086975 | 56.7032 | 56.9275 | 121.9894 | 122.3373 | -0.036621 | 122.4243 | 57.1335 | -0.14191 | 122.3373 | -0.036621 | 57.1335 | 121.9894 | 122.4243 | -122.3648 | -122.3831
1231.2188 | 122.3969 | -56.5063 | 65.744 | 0.00206 | 0.002572 | 0.0094721 | 0.022074 | 0.038866 | -0.031704 | 0.058849 | -56.575 | 65.7623 | -56.6483 | -56.4697 | 65.4556 | 0.44403 | 0.041199 | 0.29755 | 65.8768 | -56.6666 | -0.14191 | 0.01831 | -0.068664 | 0.036621 | -0.28839 | -0.16022 | 0.13275 | 0.073242 | 56.5475 | 56.8039 | 121.962 | 122.2687 | -0.068664 | 122.3831 | 56.9504 | -0.16022 | 122.2687 | -0.068664 | 56.9504 | 121.962 | 122.3831 | -122.3923 | -122.4106
1233 | 122.5067 | -56.1493 | 66.0095 | 0.017319 | 0.00064938 | 0.0090447 | 0.022074 | 0.037798 | -0.033199 | 0.059917 | -56.3416 | 66.0187 | -56.3644 | -56.2454 | 65.6845 | 0.41199 | -0.15106 | 0.19684 | 66.0965 | -56.4011 | -0.21515 | 0.009156 | -0.19226 | -0.09613 | -0.32501 | -0.25177 | 0.086976 | 0.022888 | 55.9982 | 56.3461 | 121.8338 | 122.168 | -0.19226 | 122.2458 | 56.5613 | -0.25177 | 122.168 | -0.19226 | 56.5613 | 121.8338 | 122.2458 | -122.374 | -122.4106
1234.7656 | 122.3648 | -56.1081 | 66.1606 | 0.017319 | 0.001504 | 0.013531 | 0.029337 | 0.041644 | -0.033413 | 0.059062 | -56.1813 | 66.1789 | -56.2408 | -56.0852 | 65.8173 | 0.3891 | 0.004578 | 0.18768 | 66.3162 | -56.2546 | -0.13275 | 0.018311 | -0.073242 | 0.022888 | -0.34332 | -0.14649 | 0.15564 | 0.05951 | 56.1127 | 56.2958 | 121.9254 | 122.287 | -0.073242 | 122.4243 | 56.4972 | -0.14649 | 122.287 | -0.073242 | 56.4972 | 121.9254 | 122.4243 | -122.4014 | -122.4152
1236.5625 | 122.4289 | -56.044 | 66.1606 | 0.017319 | 0.0038538 | 0.012676 | 0.025919 | 0.04143 | -0.032131 | 0.059703 | -56.1218 | 66.1652 | -56.2134 | -56.0349 | 65.8768 | 0.43945 | -0.2655 | 0.21057 | 66.2521 | -56.2637 | -0.16937 | 0.004578 | -0.07782 | 0.009155 | -0.28381 | -0.21973 | 0.091553 | 0.091553 | 55.7785 | 56.2546 | 121.9208 | 122.2092 | -0.07782 | 122.2961 | 56.4835 | -0.21973 | 122.2092 | -0.07782 | 56.4835 | 121.9208 | 122.2961 | -122.374 | -122.4243
1238.2969 | 122.493 | -55.9845 | 66.1972 | 0.00206 | 0.0023584 | 0.0090447 | 0.028269 | 0.042284 | -0.03384 | 0.059062 | -56.1813 | 66.2567 | -56.2134 | -56.0898 | 65.8218 | 0.28839 | -0.036621 | 0.07782 | 66.362 | -56.218 | -0.22888 | 0.059509 | -0.19684 | -0.10529 | -0.37537 | -0.23346 | 0.16479 | 0.032044 | 55.9479 | 56.0623 | 121.8063 | 122.2412 | -0.19684 | 122.3465 | 56.2729 | -0.23346 | 122.2412 | -0.19684 | 56.2729 | 121.8063 | 122.3465 | -122.4106 | -122.4152
1240.0781 | 122.493 | -55.9387 | 66.2384 | 0.00206 | 0.00043578 | 0.0066949 | 0.019937 | 0.03908 | -0.032345 | 0.061199 | -56.1172 | 66.2659 | -56.1264 | -56.0028 | 65.9271 | 0.39825 | -0.1236 | 0.19226 | 66.3712 | -56.1996 | -0.18768 | 0.027466 | -0.17853 | -0.064087 | -0.31128 | -0.26093 | 0.13275 | 0.009155 | 55.8151 | 56.131 | 121.8658 | 122.2046 | -0.17853 | 122.3099 | 56.337 | -0.26093 | 122.2046 | -0.17853 | 56.337 | 121.8658 | 122.3099 | -122.3648 | -122.438
1241.7812 | 122.5113 | -55.9296 | 66.2704 | -0.0055695 | -0.0010596 | 0.012035 | 0.022287 | 0.038439 | -0.030422 | 0.05949 | -56.0944 | 66.2476 | -56.1676 | -55.9753 | 65.9271 | 0.40741 | -0.13733 | 0.1831 | 66.3345 | -56.1813 | -0.23804 | -0.022888 | -0.1648 | -0.045777 | -0.34332 | -0.25177 | 0.064087 | 0.073243 | 55.7922 | 56.1127 | 121.8567 | 122.1771 | -0.1648 | 122.2641 | 56.337 | -0.25177 | 122.1771 | -0.1648 | 56.337 | 121.8567 | 122.2641 | -122.4381 | -122.4518
1243.5781 | 122.3648 | -55.8563 | 66.394 | -0.0055695 | 0.0023584 | 0.01289 | 0.025064 | 0.037798 | -0.030849 | 0.059276 | -55.925 | 66.3757 | -56.0074 | -55.8151 | 66.0873 | 0.48065 | 0.022888 | 0.32959 | 66.5131 | -56.0486 | -0.15106 | -0.018311 | -0.068665 | 0.041198 | -0.3067 | -0.19226 | 0.11902 | 0.082397 | 55.8792 | 56.1859 | 121.9437 | 122.2321 | -0.068665 | 122.3694 | 56.337 | -0.19226 | 122.2321 | -0.068665 | 56.337 | 121.9437 | 122.3694 | -122.4014 | -122.4426
1245.2969 | 122.4426 | -55.8701 | 66.3345 | 0.00206 | 0.001504 | 0.010754 | 0.025919 | 0.040148 | -0.032131 | 0.058208 | -55.9753 | 66.3437 | -56.0669 | -55.8563 | 66.0278 | 0.43488 | -0.23804 | 0.21515 | 66.3986 | -56.0989 | -0.19684 | 0.009155 | -0.10529 | 0.013733 | -0.3067 | -0.22888 | 0.064087 | 0.091553 | 55.632 | 56.0852 | 121.8979 | 122.2137 | -0.10529 | 122.2687 | 56.3049 | -0.22888 | 122.2137 | -0.10529 | 56.3049 | 121.8979 | 122.2687 | -122.4014 | -122.4335
1247.0781 | 122.3419 | -56.044 | 66.2384 | 0.0096895 | 0.0040674 | 0.0079767 | 0.030618 | 0.039294 | -0.032985 | 0.060985 | -56.0852 | 66.2704 | -56.1905 | -55.9753 | 65.9042 | 0.42572 | 0 | 0.24719 | 66.3712 | -56.1859 | -0.14648 | 0.032044 | -0.041199 | 0.068664 | -0.33417 | -0.14191 | 0.13275 | 0.10529 | 56.044 | 56.2912 | 121.9482 | 122.3145 | -0.041199 | 122.4152 | 56.4697 | -0.14191 | 122.3145 | -0.041199 | 56.4697 | 121.9482 | 122.4152 | -122.4289 | -122.4243
1248.7812 | 122.319 | -55.8517 | 66.3803 | -0.0055695 | 0.001504 | 0.0084039 | 0.028269 | 0.03908 | -0.031277 | 0.058422 | -55.9067 | 66.4764 | -55.9799 | -55.7785 | 66.1057 | 0.43945 | 0.018311 | 0.26093 | 66.5588 | -55.9891 | -0.12817 | 0.09613 | -0.054931 | 0.073243 | -0.27466 | -0.13733 | 0.17853 | 0.073242 | 55.8701 | 56.1127 | 121.9574 | 122.3282 | -0.054931 | 122.4106 | 56.2912 | -0.13733 | 122.3282 | -0.054931 | 56.2912 | 121.9574 | 122.4106 | -122.3602 | -122.3694
1250.5781 | 122.4701 | -52.977 | 69.191 | 0.00206 | 0.001504 | 0.01054 | 0.019083 | 0.040362 | -0.029781 | 0.05949 | -53.1738 | 69.2047 | -53.2013 | -53.0502 | 68.866 | 0.54474 | -0.1236 | 0.22888 | 69.2734 | -53.2516 | -0.2243 | 0.013733 | -0.19684 | -0.073242 | -0.32501 | -0.27466 | 0.082397 | 0.027466 | 52.8534 | 53.2059 | 121.843 | 122.1817 | -0.19684 | 122.2504 | 53.5217 | -0.27466 | 122.1817 | -0.19684 | 53.5217 | 121.843 | 122.2504 | -122.3923 | -122.4426
1252.2812 | 122.3328 | -51.9928 | 70.2942 | 0.017319 | 0.0012902 | 0.012035 | 0.029123 | 0.041216 | -0.034694 | 0.057994 | -52.0569 | 70.3171 | -52.1255 | -51.9333 | 69.9371 | 0.56305 | 0.027466 | 0.27466 | 70.4498 | -52.1118 | -0.13275 | 0.022889 | -0.064087 | 0.059509 | -0.35706 | -0.11902 | 0.15564 | 0.068664 | 52.0203 | 52.2675 | 121.9299 | 122.3099 | -0.064087 | 122.4426 | 52.5558 | -0.11902 | 122.3099 | -0.064087 | 52.5558 | 121.9299 | 122.4426 | -122.4197 | -122.406
1254.0625 | 122.3602 | -51.2558 | 71.022 | 0.0096895 | 0.0017176 | 0.0090447 | 0.022287 | 0.038653 | -0.031917 | 0.059062 | -51.3245 | 70.9991 | -51.3702 | -51.1871 | 70.697 | 0.66376 | 0.013733 | 0.36163 | 71.1273 | -51.416 | -0.11444 | -0.022888 | -0.068665 | 0.068664 | -0.32501 | -0.16022 | 0.10528 | 0.045776 | 51.2695 | 51.6174 | 121.9528 | 122.2549 | -0.068665 | 122.3831 | 51.9196 | -0.16022 | 122.2549 | -0.068665 | 51.9196 | 121.9528 | 122.3831 | -122.3923 | -122.4381
1255.8281 | 122.3328 | -49.8734 | 72.4182 | -0.013199 | 0.0023584 | 0.014385 | 0.023783 | 0.038226 | -0.031704 | 0.058422 | -49.8962 | 72.3953 | -49.9832 | -49.7864 | 72.0978 | 0.75989 | -0.064087 | 0.3891 | 72.4594 | -50.0244 | -0.10986 | -0.022888 | -0.022888 | 0.086975 | -0.32043 | -0.15106 | 0.041199 | 0.086975 | 49.8093 | 50.2625 | 121.9711 | 122.2687 | -0.022888 | 122.3328 | 50.6332 | -0.15106 | 122.2687 | -0.022888 | 50.6332 | 121.9711 | 122.3328 | -122.4014 | -122.4426
1257.5469 | 122.4838 | -49.4705 | 72.7112 | 0.00206 | 0.00022218 | 0.0094721 | 0.022287 | 0.038226 | -0.031063 | 0.059703 | -49.6674 | 72.7203 | -49.6719 | -49.53 | 72.3495 | 0.63171 | -0.15106 | 0.19226 | 72.7844 | -49.7131 | -0.20142 | 0.009155 | -0.19684 | -0.059509 | -0.36163 | -0.24262 | 0.073242 | 0.004578 | 49.3195 | 49.6628 | 121.8201 | 122.1909 | -0.19684 | 122.2549 | 50.1022 | -0.24262 | 122.1909 | -0.19684 | 50.1022 | 121.8201 | 122.2549 | -122.3831 | -122.4243
1259.3125 | 122.438 | -48.4085 | 73.7869 | 0.0096895 | -0.0012732 | 0.0051995 | 0.024851 | 0.037371 | -0.034054 | 0.060344 | -48.5641 | 73.7503 | -48.6282 | -48.4222 | 73.439 | 0.6958 | -0.2243 | 0.21515 | 73.819 | -48.6282 | -0.21973 | -0.036621 | -0.15564 | -0.013733 | -0.3479 | -0.21973 | 0.032044 | 0.064087 | 48.1842 | 48.6237 | 121.8475 | 122.1588 | -0.15564 | 122.2275 | 49.1043 | -0.21973 | 122.1588 | -0.15564 | 49.1043 | 121.8475 | 122.2275 | -122.4152 | -122.4152
1261.0938 | 122.3373 | -47.6028 | 74.6704 | 0.00206 | 0.00086298 | 0.0079767 | 0.030405 | 0.038012 | -0.035549 | 0.059703 | -47.7264 | 74.7253 | -47.7585 | -47.4838 | 74.3362 | 0.69122 | 0.041199 | 0.24719 | 74.8581 | -47.7356 | -0.15564 | 0.054932 | -0.1236 | 0.11902 | -0.33417 | -0.13275 | 0.18768 | 0.032044 | 47.644 | 47.85 | 121.9391 | 122.3282 | -0.1236 | 122.4609 | 48.2941 | -0.13275 | 122.3282 | -0.1236 | 48.2941 | 121.9391 | 122.4609 | -122.4289 | -122.406
1262.8125 | 122.3419 | -46.5729 | 75.6775 | 0.00206 | 0.0032128 | 0.015453 | 0.027841 | 0.04143 | -0.033626 | 0.060344 | -46.6553 | 75.7187 | -46.7148 | -46.5591 | 75.2884 | 0.71869 | 0.018311 | 0.23346 | 75.8102 | -46.7194 | -0.14191 | 0.041199 | -0.082397 | 0.013733 | -0.3891 | -0.14648 | 0.13275 | 0.05951 | 46.5912 | 46.8063 | 121.8613 | 122.2916 | -0.082397 | 122.3831 | 47.2916 | -0.14648 | 122.2916 | -0.082397 | 47.2916 | 121.8613 | 122.3831 | -122.3923 | -122.3969
1264.6094 | 122.374 | -46.4264 | 75.8194 | 0.00206 | 0.0012902 | 0.0086175 | 0.023996 | 0.039294 | -0.034908 | 0.059917 | -46.5683 | 75.8011 | -46.5958 | -46.4447 | 75.4166 | 0.7782 | 0.082397 | 0.31586 | 75.9521 | -46.6003 | -0.16937 | -0.018311 | -0.14191 | -0.01831 | -0.40283 | -0.17395 | 0.13275 | 0.027466 | 46.5088 | 46.7422 | 121.843 | 122.2275 | -0.14191 | 122.3785 | 47.2046 | -0.17395 | 122.2275 | -0.14191 | 47.2046 | 121.843 | 122.3785 | -122.4152 | -122.4197
1266.3438 | 122.4472 | -45.9961 | 76.1581 | 0.0096895 | 0.0029992 | 0.012676 | 0.028055 | 0.039721 | -0.034267 | 0.060985 | -46.2387 | 76.2314 | -46.2341 | -46.1151 | 75.7507 | 0.6546 | 0 | 0.12817 | 76.3596 | -46.225 | -0.23804 | 0.073242 | -0.24261 | -0.11902 | -0.40741 | -0.22888 | 0.20142 | -0.004577 | 45.9961 | 46.1243 | 121.7468 | 122.2275 | -0.24261 | 122.3557 | 46.6507 | -0.22888 | 122.2275 | -0.24261 | 46.6507 | 121.7468 | 122.3557 | -122.3923 | -122.3831
1268.1094 | 122.4518 | -45.3964 | 76.7899 | 0.00206 | 0.0023584 | 0.012463 | 0.027201 | 0.041857 | -0.033626 | 0.060771 | -45.6116 | 76.8631 | -45.5887 | -45.5154 | 76.355 | 0.71869 | 0.050354 | 0.14191 | 76.9913 | -45.5795 | -0.19226 | 0.073242 | -0.21515 | -0.11902 | -0.43488 | -0.18311 | 0.20142 | -0.022888 | 45.4468 | 45.5383 | 121.7514 | 122.2595 | -0.21515 | 122.3877 | 46.1151 | -0.18311 | 122.2595 | -0.21515 | 46.1151 | 121.7514 | 122.3877 | -122.3785 | -122.3694
1269.7969 | 122.4655 | -45.1355 | 77.0691 | -0.0055695 | 0.00022218 | 0.0090447 | 0.021005 | 0.039935 | -0.033626 | 0.059703 | -45.6161 | 76.767 | -45.5933 | -45.4742 | 76.4191 | 0.78735 | -0.1236 | 0.24719 | 76.8814 | -45.6619 | -0.45776 | -0.30212 | -0.48065 | -0.33875 | -0.65002 | -0.52643 | -0.18768 | -0.022888 | 45.0119 | 45.3827 | 121.5546 | 121.9025 | -0.48065 | 122.0169 | 45.9229 | -0.52643 | 121.9025 | -0.48065 | 45.9229 | 121.5546 | 122.0169 | -122.6624 | -122.731
1271.5781 | 122.4655 | -44.014 | 78.1631 | 0.00206 | 8.578e-06 | 0.0079767 | 0.02421 | 0.037798 | -0.029354 | 0.059703 | -44.1559 | 78.2822 | -44.133 | -44.0277 | 77.8656 | 0.82855 | -0.13275 | 0.18768 | 78.2959 | -44.2108 | -0.11902 | 0.11902 | -0.14191 | -0.013733 | -0.29755 | -0.19684 | 0.13275 | -0.022888 | 43.8812 | 44.2017 | 121.8796 | 122.2961 | -0.14191 | 122.3099 | 44.8425 | -0.19684 | 122.2961 | -0.14191 | 44.8425 | 121.8796 | 122.3099 | -122.2961 | -122.374
1273.3594 | 122.3419 | -43.428 | 78.8498 | 0.00206 | 0.001504 | 0.0071221 | 0.023355 | 0.038653 | -0.030208 | 0.05949 | -43.4601 | 78.8635 | -43.5104 | -43.3319 | 78.5294 | 0.94757 | -0.091553 | 0.37537 | 78.9642 | -43.5333 | -0.082397 | 0.013733 | -0.032043 | 0.096131 | -0.32043 | -0.10528 | 0.11444 | 0.050354 | 43.3365 | 43.8034 | 121.9574 | 122.2916 | -0.032043 | 122.3923 | 44.3756 | -0.10528 | 122.2916 | -0.032043 | 44.3756 | 121.9574 | 122.3923 | -122.3602 | -122.3831
1275.0625 | 122.4609 | -42.9474 | 79.2709 | -0.0055695 | 0.0021448 | 0.0079767 | 0.02421 | 0.038012 | -0.032131 | 0.056713 | -43.2953 | 79.1336 | -43.2907 | -43.1717 | 78.6896 | 0.84228 | -0.1236 | 0.2243 | 79.1931 | -43.3548 | -0.34332 | -0.13733 | -0.3479 | -0.2243 | -0.58136 | -0.40741 | -0.07782 | -0.004578 | 42.8238 | 43.1717 | 121.637 | 122.081 | -0.3479 | 122.1405 | 43.7897 | -0.40741 | 122.081 | -0.3479 | 43.7897 | 121.637 | 122.1405 | -122.5616 | -122.6257
1276.8281 | 122.4609 | -43.396 | 78.7903 | -0.0055695 | 0.0010766 | 0.013104 | 0.025705 | 0.037157 | -0.03384 | 0.060131 | -43.5974 | 78.772 | -43.6157 | -43.483 | 78.3691 | 0.8194 | -0.12817 | 0.21515 | 78.8498 | -43.6523 | -0.21973 | -0.01831 | -0.20142 | -0.086975 | -0.42114 | -0.25635 | 0.059509 | 0.018311 | 43.2678 | 43.6111 | 121.7651 | 122.168 | -0.20142 | 122.2458 | 44.2154 | -0.25635 | 122.168 | -0.20142 | 44.2154 | 121.7651 | 122.2458 | -122.406 | -122.4426
1278.625 | 122.4014 | -42.8375 | 79.3304 | 0.0096895 | 0.0027856 | 0.01524 | 0.029123 | 0.039294 | -0.034267 | 0.059062 | -43.0023 | 79.3945 | -43.0527 | -42.8604 | 78.9688 | 0.87891 | -0.18768 | 0.23804 | 79.4586 | -43.0573 | -0.21515 | 0.064087 | -0.16479 | -0.022889 | -0.36163 | -0.21973 | 0.12817 | 0.050354 | 42.6498 | 43.0756 | 121.8063 | 122.2321 | -0.16479 | 122.2961 | 43.7164 | -0.21973 | 122.2321 | -0.16479 | 43.7164 | 121.8063 | 122.2961 | -122.3831 | -122.3877
1280.4062 | 122.4014 | -43.9362 | 78.2913 | 0.0096895 | 0.0038538 | 0.010967 | 0.026132 | 0.037798 | -0.032558 | 0.058208 | -44.1238 | 78.3646 | -44.1101 | -43.9682 | 77.8656 | 0.85144 | 0.1831 | 0.27924 | 78.4882 | -44.1147 | -0.17395 | 0.073242 | -0.18768 | -0.032044 | -0.42572 | -0.17853 | 0.19684 | -0.013733 | 44.1193 | 44.2154 | 121.8018 | 122.3007 | -0.18768 | 122.4243 | 44.7876 | -0.17853 | 122.3007 | -0.18768 | 44.7876 | 121.8018 | 122.4243 | -122.4014 | -122.406
1282.125 | 122.3785 | -43.2129 | 78.9871 | 0.017319 | 0.0023584 | 0.0079767 | 0.025492 | 0.039294 | -0.034481 | 0.05949 | -43.3868 | 79.1107 | -43.3914 | -43.277 | 78.566 | 0.91553 | 0.15106 | 0.29755 | 79.1885 | -43.3823 | -0.17853 | 0.1236 | -0.17395 | -0.064087 | -0.42114 | -0.16937 | 0.20142 | 0.004577 | 43.364 | 43.5104 | 121.7789 | 122.3236 | -0.17395 | 122.4014 | 44.1284 | -0.16937 | 122.3236 | -0.17395 | 44.1284 | 121.7789 | 122.4014 | -122.3785 | -122.3694
1283.8906 | 122.4564 | -42.8009 | 79.3625 | 0.0096895 | 0.002572 | 0.0066949 | 0.025705 | 0.042498 | -0.03619 | 0.060344 | -42.9977 | 79.4678 | -42.984 | -42.9062 | 78.9276 | 0.85144 | 0.050354 | 0.14648 | 79.6051 | -42.9932 | -0.18311 | 0.10528 | -0.19684 | -0.10529 | -0.43488 | -0.19226 | 0.24262 | -0.013733 | 42.8513 | 42.9474 | 121.7285 | 122.2687 | -0.19684 | 122.406 | 43.6523 | -0.19226 | 122.2687 | -0.19684 | 43.6523 | 121.7285 | 122.406 | -122.3465 | -122.3557
1285.6719 | 122.3236 | -42.5583 | 79.6555 | 0.0096895 | 0.00064938 | 0.014385 | 0.025064 | 0.041003 | -0.034267 | 0.059917 | -42.7094 | 79.7287 | -42.7094 | -42.5583 | 79.2892 | 0.91095 | 0.073242 | 0.29297 | 79.8065 | -42.7322 | -0.15106 | 0.073242 | -0.15106 | 0 | -0.36621 | -0.17395 | 0.15106 | 0 | 42.6315 | 42.8513 | 121.8475 | 122.287 | -0.15106 | 122.3648 | 43.4692 | -0.17395 | 122.287 | -0.15106 | 43.4692 | 121.8475 | 122.3648 | -122.3648 | -122.3877
1287.4062 | 122.3236 | -42.2928 | 79.9622 | 0.0096895 | 0.0023584 | 0.011181 | 0.026987 | 0.04143 | -0.035763 | 0.05949 | -42.4164 | 80.0125 | -42.4347 | -42.2745 | 79.5547 | 0.94757 | 0.022888 | 0.28839 | 80.1178 | -42.4301 | -0.14191 | 0.050354 | -0.1236 | 0.018311 | -0.40741 | -0.13733 | 0.15564 | 0.01831 | 42.3157 | 42.5812 | 121.8475 | 122.3053 | -0.1236 | 122.4106 | 43.2404 | -0.13733 | 122.3053 | -0.1236 | 43.2404 | 121.8475 | 122.4106 | -122.3969 | -122.3923
1289.1875 | 122.3007 | -41.8442 | 80.4199 | 0.0096895 | -0.00063242 | 0.0079767 | 0.027414 | 0.040148 | -0.034481 | 0.057781 | -41.9815 | 80.4382 | -41.9769 | -41.8533 | 80.0125 | 0.94299 | 0.041199 | 0.28839 | 80.5435 | -41.9907 | -0.13275 | 0.01831 | -0.13733 | -0.009156 | -0.40741 | -0.14648 | 0.1236 | -0.004577 | 41.8854 | 42.1326 | 121.8567 | 122.2824 | -0.13733 | 122.3877 | 42.7872 | -0.14648 | 122.2824 | -0.13733 | 42.7872 | 121.8567 | 122.3877 | -122.3969 | -122.4106
1290.9688 | 122.319 | -41.153 | 81.134 | 0.0096895 | 0.0036402 | 0.010967 | 0.028482 | 0.039721 | -0.031917 | 0.058635 | -41.2491 | 81.1981 | -41.2582 | -41.1255 | 80.7175 | 1.0071 | 0.059509 | 0.29297 | 81.2714 | -41.2949 | -0.10529 | 0.064087 | -0.09613 | 0.027466 | -0.41657 | -0.14191 | 0.13733 | 0.009156 | 41.2125 | 41.4459 | 121.8704 | 122.3511 | -0.09613 | 122.4243 | 42.16 | -0.14191 | 122.3511 | -0.09613 | 42.16 | 121.8704 | 122.4243 | -122.3923 | -122.4289
1292.6875 | 122.3785 | -41.2857 | 80.9601 | 0.00206 | 0.0019312 | 0.012463 | 0.022501 | 0.039294 | -0.032558 | 0.059917 | -41.5237 | 80.9967 | -41.4551 | -41.3818 | 80.4886 | 0.96588 | 0.19226 | 0.27924 | 81.0699 | -41.4642 | -0.16937 | 0.036621 | -0.23804 | -0.09613 | -0.4715 | -0.17853 | 0.10986 | -0.068665 | 41.478 | 41.5649 | 121.7743 | 122.2824 | -0.23804 | 122.3557 | 42.2516 | -0.17853 | 122.2824 | -0.23804 | 42.2516 | 121.7743 | 122.3557 | -122.4152 | -122.4243
1294.4688 | 122.4014 | -35.463 | 86.7783 | 0.00206 | 0.00022218 | 0.011181 | 0.021005 | 0.035662 | -0.030422 | 0.05949 | -35.6094 | 86.7966 | -35.5591 | -35.4538 | 86.4029 | 1.3138 | -0.082397 | 0.3479 | 86.8744 | -35.6277 | -0.09613 | 0.018311 | -0.14648 | 0.009156 | -0.37537 | -0.16479 | 0.096131 | -0.050354 | 35.3806 | 35.8109 | 121.8658 | 122.2595 | -0.14648 | 122.3373 | 36.7767 | -0.16479 | 122.2595 | -0.14648 | 36.7767 | 121.8658 | 122.3373 | -122.3373 | -122.406
1296.2031 | 122.374 | -35.3531 | 86.8835 | 0.00206 | 0.0017176 | 0.0096857 | 0.02186 | 0.038653 | -0.030636 | 0.059276 | -35.5087 | 86.8698 | -35.5225 | -35.3668 | 86.467 | 1.3046 | -0.086975 | 0.36163 | 86.998 | -35.5453 | -0.16937 | -0.013733 | -0.15564 | -0.013733 | -0.41656 | -0.19226 | 0.11444 | 0.013733 | 35.2661 | 35.7147 | 121.8201 | 122.2229 | -0.15564 | 122.3511 | 36.6577 | -0.19226 | 122.2229 | -0.15564 | 36.6577 | 121.8201 | 122.3511 | -122.406 | -122.4289
1297.9688 | 122.4426 | -35.0739 | 87.1033 | 0.017319 | -0.0027686 | 0.0073359 | 0.023569 | 0.038439 | -0.03149 | 0.058849 | -35.3485 | 87.0712 | -35.3027 | -35.1837 | 86.6592 | 1.2131 | -0.091553 | 0.27924 | 87.2314 | -35.2798 | -0.22888 | -0.032043 | -0.27466 | -0.10986 | -0.44403 | -0.20599 | 0.12817 | -0.045777 | 34.9823 | 35.3531 | 121.7331 | 122.1451 | -0.27466 | 122.3053 | 36.2869 | -0.20599 | 122.1451 | -0.27466 | 36.2869 | 121.7331 | 122.3053 | -122.406 | -122.3831
1299.6719 | 122.4152 | -34.8267 | 87.3734 | 0.024948 | 0.0012902 | 0.010967 | 0.022714 | 0.039507 | -0.032345 | 0.058849 | -35.0281 | 87.3962 | -35.0143 | -34.8541 | 86.9522 | 1.2909 | -0.086975 | 0.33875 | 87.5061 | -35.0281 | -0.18768 | 0.022888 | -0.20142 | -0.027466 | -0.42114 | -0.20142 | 0.13275 | -0.013733 | 34.7397 | 35.1654 | 121.7789 | 122.2229 | -0.20142 | 122.3328 | 36.1176 | -0.20142 | 122.2229 | -0.20142 | 36.1176 | 121.7789 | 122.3328 | -122.3877 | -122.4014
1301.4688 | 122.3328 | -34.584 | 87.6663 | 0.0096895 | 0.0010766 | 0.010326 | 0.026987 | 0.038012 | -0.031277 | 0.057994 | -34.7443 | 87.6709 | -34.7397 | -34.5795 | 87.2131 | 1.3046 | 0.082397 | 0.36621 | 87.8037 | -34.758 | -0.15564 | 0.004577 | -0.16022 | 0.004577 | -0.45319 | -0.17395 | 0.13733 | -0.004578 | 34.6664 | 34.9503 | 121.7972 | 122.2549 | -0.16022 | 122.3877 | 35.8887 | -0.17395 | 122.2549 | -0.16022 | 35.8887 | 121.7972 | 122.3877 | -122.406 | -122.4243
1303.1875 | 122.3282 | -33.522 | 88.7741 | 0.00206 | -0.00020502 | 0.0081903 | 0.023996 | 0.035021 | -0.032985 | 0.057781 | -33.6502 | 88.7283 | -33.6639 | -33.5266 | 88.2843 | 1.3367 | -0.027466 | 0.42114 | 88.8153 | -33.6868 | -0.14191 | -0.045776 | -0.12817 | -0.004577 | -0.48981 | -0.1648 | 0.041199 | 0.013732 | 33.4946 | 33.9432 | 121.8063 | 122.2504 | -0.12817 | 122.3373 | 34.8587 | -0.1648 | 122.2504 | -0.12817 | 34.8587 | 121.8063 | 122.3373 | -122.438 | -122.4609
1304.9531 | 122.4518 | -32.9453 | 89.2227 | 0.00206 | -0.0017004 | 0.0073359 | 0.024637 | 0.040362 | -0.032558 | 0.060985 | -33.1924 | 89.241 | -33.165 | -33.0551 | 88.7558 | 1.3275 | -0.073242 | 0.24719 | 89.36 | -33.1696 | -0.21973 | 0.018311 | -0.24719 | -0.10986 | -0.46692 | -0.22431 | 0.13733 | -0.027466 | 32.872 | 33.1924 | 121.701 | 122.1863 | -0.24719 | 122.3053 | 34.2728 | -0.22431 | 122.1863 | -0.24719 | 34.2728 | 121.701 | 122.3053 | -122.3877 | -122.3923
1306.7344 | 122.4106 | -33.3252 | 88.8657 | 0.00206 | -0.00063242 | 0.011608 | 0.02891 | 0.039294 | -0.034481 | 0.059062 | -33.5312 | 88.8931 | -33.5037 | -33.371 | 88.4171 | 1.2405 | -0.13275 | 0.21973 | 89.0167 | -33.4946 | -0.17853 | 0.027465 | -0.20599 | -0.045777 | -0.44861 | -0.16937 | 0.15106 | -0.027466 | 33.1924 | 33.5449 | 121.7422 | 122.2183 | -0.20599 | 122.3419 | 34.5657 | -0.16937 | 122.2183 | -0.20599 | 34.5657 | 121.7422 | 122.3419 | -122.3694 | -122.3602
1308.4531 | 122.374 | -32.8949 | 89.3417 | 0.00206 | 0.0034266 | 0.011822 | 0.02656 | 0.039507 | -0.036617 | 0.058422 | -33.1375 | 89.4012 | -33.0872 | -32.9681 | 88.8153 | 1.3138 | 0.20142 | 0.28839 | 89.5294 | -33.046 | -0.19226 | 0.059509 | -0.24262 | -0.073243 | -0.52643 | -0.15106 | 0.18768 | -0.050354 | 33.0963 | 33.1833 | 121.7102 | 122.2961 | -0.24262 | 122.4243 | 34.2087 | -0.15106 | 122.2961 | -0.24262 | 34.2087 | 121.7102 | 122.4243 | -122.4289 | -122.3877
1310.2344 | 122.4197 | -32.9544 | 89.2456 | 0.00206 | 0.0029992 | 0.011181 | 0.028055 | 0.040148 | -0.032345 | 0.059062 | -33.2565 | 89.2044 | -33.2108 | -33.0414 | 88.797 | 1.3916 | -0.086975 | 0.27924 | 89.3692 | -33.1055 | -0.25635 | -0.041198 | -0.30212 | -0.086975 | -0.44861 | -0.15106 | 0.1236 | -0.045777 | 32.8674 | 33.2336 | 121.7514 | 122.1588 | -0.30212 | 122.3236 | 34.346 | -0.15106 | 122.1588 | -0.30212 | 34.346 | 121.7514 | 122.3236 | -122.4564 | -122.3511
1312.0312 | 122.4564 | -34.1309 | 88.06 | 0.017319 | -0.0012732 | 0.014599 | 0.022928 | 0.038439 | -0.032772 | 0.059276 | -34.3781 | 88.0142 | -34.3369 | -34.2224 | 87.5885 | 1.236 | -0.14191 | 0.23346 | 88.1561 | -34.3735 | -0.20599 | -0.045777 | -0.24719 | -0.091553 | -0.4715 | -0.24262 | 0.09613 | -0.041199 | 33.989 | 34.3643 | 121.7194 | 122.1451 | -0.24719 | 122.287 | 35.3668 | -0.24262 | 122.1451 | -0.24719 | 35.3668 | 121.7194 | 122.287 | -122.3969 | -122.4335
1313.8125 | 122.3969 | -34.8267 | 87.3505 | 0.00206 | 0.00064938 | 0.011181 | 0.026987 | 0.041857 | -0.033199 | 0.058208 | -34.996 | 87.323 | -35.0098 | -34.8862 | 86.9293 | 1.2177 | -0.21515 | 0.25635 | 87.4695 | -35.0464 | -0.18311 | -0.027466 | -0.16937 | -0.059509 | -0.42114 | -0.21973 | 0.11902 | 0.013733 | 34.6115 | 35.083 | 121.756 | 122.1497 | -0.16937 | 122.2961 | 36.0443 | -0.21973 | 122.1497 | -0.16937 | 36.0443 | 121.756 | 122.2961 | -122.3602 | -122.3969
1315.6094 | 122.2961 | -34.8083 | 87.4283 | 0.0096895 | 0.0027856 | 0.010113 | 0.027841 | 0.039721 | -0.036403 | 0.057353 | -34.9869 | 87.4329 | -35.0052 | -34.8358 | 86.9568 | 1.2634 | 0.068665 | 0.32044 | 87.5885 | -34.964 | -0.19684 | 0.004577 | -0.17853 | -0.027465 | -0.4715 | -0.15564 | 0.16022 | 0.018311 | 34.877 | 35.1288 | 121.7651 | 122.2412 | -0.17853 | 122.3969 | 36.0718 | -0.15564 | 122.2412 | -0.17853 | 36.0718 | 121.7651 | 122.3969 | -122.4335 | -122.3923
1317.3281 | 122.3648 | -34.0576 | 88.147 | 0.00206 | 0.0034266 | 0.013317 | 0.022287 | 0.040789 | -0.035549 | 0.059062 | -34.1858 | 88.1927 | -34.1812 | -34.0256 | 87.7899 | 1.3779 | -0.073242 | 0.37537 | 88.3072 | -34.1949 | -0.1236 | 0.045776 | -0.12817 | 0.032043 | -0.35706 | -0.13733 | 0.16022 | -0.004578 | 33.9844 | 34.433 | 121.8475 | 122.2504 | -0.12817 | 122.3648 | 35.4355 | -0.13733 | 122.2504 | -0.12817 | 35.4355 | 121.8475 | 122.3648 | -122.3282 | -122.3419
1319.0938 | 122.4609 | -34.2453 | 87.9272 | 0.017319 | 0.0017176 | 0.0073359 | 0.025492 | 0.040789 | -0.032772 | 0.058635 | -34.4879 | 88.0142 | -34.4238 | -34.3643 | 87.4557 | 1.1673 | 0.013733 | 0.14191 | 88.1561 | -34.4238 | -0.17853 | 0.086975 | -0.24262 | -0.11902 | -0.4715 | -0.17853 | 0.22888 | -0.064087 | 34.259 | 34.3872 | 121.701 | 122.2595 | -0.24262 | 122.4014 | 35.4126 | -0.17853 | 122.2595 | -0.24262 | 35.4126 | 121.701 | 122.4014 | -122.3511 | -122.3511
1320.8594 | 122.4243 | -33.9844 | 88.1927 | 0.0096895 | 0.0023584 | 0.011608 | 0.025705 | 0.037585 | -0.033413 | 0.059703 | -34.1858 | 88.1744 | -34.1995 | -34.0485 | 87.7716 | 1.2726 | -0.1831 | 0.26093 | 88.3026 | -34.1949 | -0.21515 | -0.018311 | -0.20142 | -0.064087 | -0.42114 | -0.21057 | 0.10986 | 0.013733 | 33.8013 | 34.2453 | 121.756 | 122.1588 | -0.20142 | 122.287 | 35.257 | -0.21057 | 122.1588 | -0.20142 | 35.257 | 121.756 | 122.287 | -122.3923 | -122.3877
1322.6406 | 122.3053 | -34.4879 | 87.7213 | 0.00206 | 0.00064938 | 0.012463 | 0.023569 | 0.038012 | -0.032345 | 0.057781 | -34.5612 | 87.8128 | -34.5703 | -34.4192 | 87.3962 | 1.355 | -0.041199 | 0.40283 | 87.8906 | -34.6115 | -0.082397 | 0.091553 | -0.073242 | 0.068665 | -0.32501 | -0.1236 | 0.16937 | 0.009155 | 34.4467 | 34.8907 | 121.8842 | 122.3007 | -0.073242 | 122.3785 | 35.8429 | -0.1236 | 122.3007 | -0.073242 | 35.8429 | 121.8842 | 122.3785 | -122.2916 | -122.3328
1324.3594 | 122.4243 | -34.0988 | 88.0234 | 0.00206 | 0.00043578 | 0.0086175 | 0.02186 | 0.037371 | -0.032985 | 0.059703 | -34.3552 | 88.0875 | -34.314 | -34.1995 | 87.6068 | 1.2955 | -0.068665 | 0.28381 | 88.2065 | -34.3048 | -0.21515 | 0.064087 | -0.25635 | -0.10071 | -0.41656 | -0.20599 | 0.18311 | -0.041199 | 34.0302 | 34.3826 | 121.7056 | 122.1863 | -0.25635 | 122.3053 | 35.3943 | -0.20599 | 122.1863 | -0.25635 | 35.3943 | 121.7056 | 122.3053 | -122.3373 | -122.3282
1326.125 | 122.3282 | -34.4604 | 87.7991 | 0.00206 | 0.0012902 | 0.011822 | 0.025492 | 0.038226 | -0.03384 | 0.057994 | -34.5703 | 87.8082 | -34.5612 | -34.4009 | 87.4008 | 1.3687 | -0.022888 | 0.40741 | 87.8998 | -34.5978 | -0.10071 | 0.009156 | -0.10986 | 0.059509 | -0.39825 | -0.13733 | 0.10071 | -0.009155 | 34.4376 | 34.8679 | 121.8613 | 122.2687 | -0.10986 | 122.3602 | 35.8292 | -0.13733 | 122.2687 | -0.10986 | 35.8292 | 121.8613 | 122.3602 | -122.3602 | -122.3969
1327.8281 | 122.3282 | -36.5891 | 85.6796 | 0.00206 | 0.0019312 | 0.0086175 | 0.023783 | 0.038866 | -0.033626 | 0.059062 | -36.8179 | 85.5331 | -36.8362 | -36.6531 | 85.1761 | 0.59967 | -0.48523 | -0.027466 | 85.6247 | -36.8637 | -0.24719 | -0.14648 | -0.22888 | -0.064087 | -0.50354 | -0.27466 | -0.054931 | 0.018311 | 36.1038 | 36.5616 | 121.7651 | 122.1222 | -0.22888 | 122.2137 | 37.1887 | -0.27466 | 122.1222 | -0.22888 | 37.1887 | 121.7651 | 122.2137 | -122.5159 | -122.5433
1329.6094 | 122.406 | -36.5479 | 85.6384 | 0.0096895 | 0.0010766 | 0.010113 | 0.026773 | 0.041644 | -0.035335 | 0.05949 | -36.7172 | 85.6567 | -36.731 | -36.5707 | 85.2493 | 1.2405 | -0.13275 | 0.27008 | 85.7803 | -36.7081 | -0.1831 | 0.01831 | -0.16937 | -0.022888 | -0.3891 | -0.16022 | 0.14191 | 0.013733 | 36.4151 | 36.8179 | 121.7972 | 122.2046 | -0.16937 | 122.3282 | 37.7884 | -0.16022 | 122.2046 | -0.16937 | 37.7884 | 121.7972 | 122.3282 | -122.3694 | -122.3465
1331.3281 | 122.319 | -37.2391 | 84.9792 | 0.0096895 | 0.0019312 | 0.0064813 | 0.028696 | 0.041216 | -0.036617 | 0.057781 | -37.3581 | 85.112 | -37.3535 | -37.207 | 84.6085 | 1.1719 | 0.12817 | 0.3067 | 85.2173 | -37.3398 | -0.11444 | 0.13275 | -0.11902 | 0.032044 | -0.37079 | -0.10071 | 0.23804 | -0.004577 | 37.3672 | 37.5458 | 121.8475 | 122.3511 | -0.11902 | 122.4564 | 38.4109 | -0.10071 | 122.3511 | -0.11902 | 38.4109 | 121.8475 | 122.4564 | -122.3328 | -122.319
1333.125 | 122.3145 | -37.1017 | 85.1486 | 0.0096895 | -0.00041862 | 0.0086175 | 0.023996 | 0.039294 | -0.034481 | 0.057994 | -37.175 | 85.1715 | -37.1887 | -37.056 | 84.7687 | 1.2589 | -0.059509 | 0.37994 | 85.2585 | -37.2574 | -0.086975 | 0.022888 | -0.073242 | 0.045777 | -0.37994 | -0.15564 | 0.10986 | 0.013733 | 37.0422 | 37.4817 | 121.8704 | 122.2733 | -0.073242 | 122.3602 | 38.3606 | -0.15564 | 122.2733 | -0.073242 | 38.3606 | 121.8704 | 122.3602 | -122.3373 | -122.406
1334.8438 | 122.3557 | -36.3831 | 85.8582 | 0.0096895 | 0.0021448 | 0.0094721 | 0.024423 | 0.038653 | -0.035122 | 0.059703 | -36.5662 | 85.8948 | -36.5341 | -36.4197 | 85.4004 | 1.181 | 0.16022 | 0.29297 | 86.0367 | -36.5158 | -0.15106 | 0.036621 | -0.1831 | -0.036621 | -0.45776 | -0.13275 | 0.17853 | -0.032043 | 36.5433 | 36.676 | 121.7834 | 122.2778 | -0.1831 | 122.4197 | 37.5641 | -0.13275 | 122.2778 | -0.1831 | 37.5641 | 121.7834 | 122.4197 | -122.3923 | -122.374
1336.625 | 122.4518 | -35.6277 | 86.5173 | 0.024948 | 0.001504 | 0.0086175 | 0.022714 | 0.037585 | -0.030422 | 0.05949 | -35.8612 | 86.5585 | -35.8154 | -35.7101 | 86.1053 | 1.236 | -0.07782 | 0.23346 | 86.6547 | -35.8429 | -0.18768 | 0.041199 | -0.23346 | -0.082397 | -0.41199 | -0.21515 | 0.13733 | -0.045776 | 35.5499 | 35.8612 | 121.7331 | 122.1863 | -0.23346 | 122.2824 | 36.8637 | -0.21515 | 122.1863 | -0.23346 | 36.8637 | 121.7331 | 122.2824 | -122.3328 | -122.3602
1338.3594 | 122.3328 | -34.9045 | 87.3459 | 0.00206 | 0.0010766 | 0.0098993 | 0.026987 | 0.036944 | -0.032985 | 0.060558 | -35.0922 | 87.2955 | -35.0555 | -34.7855 | 87.0666 | 1.5335 | 0.37537 | 0.54932 | 87.7213 | -34.8312 | -0.15106 | -0.050354 | -0.18768 | 0.11902 | -0.27924 | 0.073242 | 0.37537 | -0.036621 | 35.2798 | 35.4538 | 121.9711 | 122.2 | -0.18768 | 122.6257 | 36.438 | 0.073242 | 122.2 | -0.18768 | 36.438 | 121.9711 | 122.6257 | -122.4014 | -122.1771
1340.1406 | 122.2778 | -32.6111 | 89.653 | 0.0096895 | 0.002572 | 0.010967 | 0.028482 | 0.041003 | -0.035122 | 0.057781 | -32.7667 | 89.6896 | -32.7576 | -32.6157 | 89.1541 | 1.3824 | 0.073242 | 0.33417 | 89.7995 | -32.7301 | -0.14648 | 0.036621 | -0.15564 | -0.004578 | -0.49896 | -0.11902 | 0.14648 | -0.009156 | 32.6843 | 32.9453 | 121.7651 | 122.3007 | -0.15564 | 122.4106 | 33.9935 | -0.11902 | 122.3007 | -0.15564 | 33.9935 | 121.7651 | 122.4106 | -122.4106 | -122.3831
1341.8438 | 122.406 | -32.0206 | 90.1794 | -0.0055695 | 0.00064938 | 0.013317 | 0.024637 | 0.039507 | -0.03149 | 0.058849 | -32.2174 | 90.1703 | -32.1716 | -32.0801 | 89.7263 | 1.4282 | -0.09613 | 0.2655 | 90.3076 | -32.1899 | -0.15106 | -0.009155 | -0.19684 | -0.059509 | -0.45319 | -0.16937 | 0.12817 | -0.045776 | 31.9244 | 32.2861 | 121.7468 | 122.1909 | -0.19684 | 122.3282 | 33.4488 | -0.16937 | 122.1909 | -0.19684 | 33.4488 | 121.7468 | 122.3282 | -122.3511 | -122.3694
1343.625 | 122.3923 | -29.6402 | 92.5323 | 0.0096895 | 0.0021448 | 0.0096857 | 0.027201 | 0.040148 | -0.030208 | 0.06184 | -29.9423 | 92.4957 | -29.9103 | -29.7821 | 92.0013 | 1.6754 | 0.09613 | 0.36163 | 92.6605 | -29.8645 | -0.27008 | -0.036621 | -0.30212 | -0.14191 | -0.53101 | -0.2243 | 0.12817 | -0.032044 | 29.7363 | 30.0018 | 121.6415 | 122.1359 | -0.30212 | 122.3007 | 31.3156 | -0.2243 | 122.1359 | -0.30212 | 31.3156 | 121.6415 | 122.3007 | -122.4426 | -122.3969
1345.3438 | 122.4152 | -27.5116 | 94.6335 | 0.0096895 | 0.0012902 | 0.012463 | 0.027841 | 0.041644 | -0.035763 | 0.058422 | -27.8412 | 94.6747 | -27.7771 | -27.713 | 94.043 | 1.5335 | 0.059509 | 0.1831 | 94.8166 | -27.7542 | -0.2655 | 0.041199 | -0.32959 | -0.20142 | -0.59051 | -0.24261 | 0.1831 | -0.064087 | 27.5711 | 27.6947 | 121.5546 | 122.1863 | -0.32959 | 122.3282 | 29.0451 | -0.24261 | 122.1863 | -0.32959 | 29.0451 | 121.5546 | 122.3282 | -122.4106 | -122.3877
1347.125 | 122.2916 | -25.7263 | 96.5561 | 0.00206 | 0.00022218 | 0.0092585 | 0.021219 | 0.038439 | -0.032131 | 0.058635 | -25.8499 | 96.5149 | -25.8362 | -25.6622 | 96.0617 | 1.7807 | -0.022888 | 0.37079 | 96.6064 | -25.8774 | -0.10986 | -0.041198 | -0.1236 | 0.064087 | -0.49438 | -0.15106 | 0.050354 | -0.013733 | 25.7034 | 26.0971 | 121.788 | 122.2412 | -0.1236 | 122.3328 | 27.507 | -0.15106 | 122.2412 | -0.1236 | 27.507 | 121.788 | 122.3328 | -122.3923 | -122.4335
1348.8438 | 122.3099 | -24.5636 | 97.6364 | 0.0096895 | 0.00064938 | 0.0069085 | 0.023142 | 0.038439 | -0.030849 | 0.061199 | -24.7284 | 97.6639 | -24.6963 | -24.5453 | 97.1787 | 1.8127 | -0.054932 | 0.39825 | 97.7509 | -24.7375 | -0.13275 | 0.027465 | -0.1648 | 0.018311 | -0.45776 | -0.17395 | 0.11444 | -0.032044 | 24.5087 | 24.9619 | 121.7422 | 122.2275 | -0.1648 | 122.3145 | 26.3763 | -0.17395 | 122.2275 | -0.1648 | 26.3763 | 121.7422 | 122.3145 | -122.3328 | -122.374
1350.6406 | 122.3648 | -27.5162 | 94.6381 | 0.0096895 | 0.00043578 | 0.010967 | 0.026346 | 0.04143 | -0.032345 | 0.058422 | -27.681 | 94.6793 | -27.6581 | -27.5162 | 94.2169 | 1.6022 | -0.19226 | 0.27466 | 94.78 | -27.7084 | -0.14191 | 0.041198 | -0.1648 | 0 | -0.42114 | -0.19226 | 0.14191 | -0.022888 | 27.3239 | 27.7908 | 121.7331 | 122.1954 | -0.1648 | 122.2961 | 29.1183 | -0.19226 | 122.1954 | -0.1648 | 29.1183 | 121.7331 | 122.2961 | -122.2961 | -122.3465
1352.3594 | 122.287 | -29.0176 | 93.2236 | 0.00206 | 0.0032128 | 0.01054 | 0.029764 | 0.038866 | -0.034694 | 0.059917 | -29.1687 | 93.2785 | -29.1458 | -28.9902 | 92.7338 | 1.593 | 0.14191 | 0.3479 | 93.3929 | -29.1183 | -0.12817 | 0.054931 | -0.15106 | 0.027466 | -0.48981 | -0.10071 | 0.16937 | -0.022888 | 29.1595 | 29.3655 | 121.7514 | 122.2961 | -0.15106 | 122.4106 | 30.6107 | -0.10071 | 122.2961 | -0.15106 | 30.6107 | 121.7514 | 122.4106 | -122.3694 | -122.3419
1354.125 | 122.2824 | -31.2607 | 90.9348 | 0.0096895 | 0.0012902 | 0.011181 | 0.028055 | 0.040148 | -0.034481 | 0.061412 | -31.4987 | 90.976 | -31.4529 | -31.3385 | 90.4221 | 1.4145 | 0.12817 | 0.32044 | 91.1041 | -31.4529 | -0.19226 | 0.041199 | -0.23804 | -0.07782 | -0.51269 | -0.19226 | 0.16937 | -0.045776 | 31.3889 | 31.5811 | 121.6827 | 122.2366 | -0.23804 | 122.3648 | 32.6752 | -0.19226 | 122.2366 | -0.23804 | 32.6752 | 121.6827 | 122.3648 | -122.3877 | -122.3877
1355.8906 | 122.3785 | -54.1397 | 67.9825 | 0.0096895 | 0.00022218 | 0.0079767 | 0.025064 | 0.039507 | -0.033626 | 0.058849 | -54.2084 | 68.129 | -54.2267 | -54.1306 | 67.6712 | -0.14648 | -0.013733 | 0.13275 | 68.2251 | -54.3045 | -0.086976 | 0.14648 | -0.068665 | 0.009155 | -0.31128 | -0.16479 | 0.24262 | 0.018311 | 54.126 | 54.2725 | 121.8109 | 122.2687 | -0.068665 | 122.3648 | 53.9932 | -0.16479 | 122.2687 | -0.068665 | 53.9932 | 121.8109 | 122.3648 | -122.2092 | -122.287
1357.6094 | 122.3877 | -80.0766 | 41.9861 | 0.017319 | 0.0012902 | 0.012035 | 0.026346 | 0.042498 | -0.032131 | 0.059276 | -80.5344 | 41.7206 | -80.6808 | -80.4428 | 41.4459 | -0.40741 | 0.52643 | 0.59052 | 41.8213 | -80.6259 | -0.60425 | -0.2655 | -0.45776 | -0.36621 | -0.54016 | -0.54932 | -0.16479 | 0.14648 | 80.603 | 80.6671 | 121.5225 | 121.7972 | -0.45776 | 121.8979 | 79.6692 | -0.54932 | 121.7972 | -0.45776 | 79.6692 | 121.5225 | 121.8979 | -122.6669 | -122.612
1359.4062 | 122.287 | -45.3827 | 76.7578 | 0.00206 | -0.00020502 | 0.016521 | 0.02656 | 0.039294 | -0.031704 | 0.058422 | -45.4788 | 76.8127 | -45.52 | -45.433 | 76.3596 | 0.23804 | 0.082397 | 0.29297 | 76.8906 | -45.5795 | -0.13733 | 0.054932 | -0.096131 | -0.050354 | -0.39825 | -0.19684 | 0.13275 | 0.041199 | 45.4651 | 45.6757 | 121.7422 | 122.1954 | -0.096131 | 122.2733 | 45.6207 | -0.19684 | 122.1954 | -0.096131 | 45.6207 | 121.7422 | 122.2733 | -122.2778 | -122.3373
1361.1875 | 122.287 | -105.5603 | 16.5024 | 0.00206 | 0.001504 | 0.0077631 | 0.025492 | 0.037798 | -0.031277 | 0.05949 | -105.4092 | 16.8182 | -105.574 | -105.3452 | 16.5665 | -2.6733 | -0.27008 | -0.12817 | 16.8137 | -105.6793 | -0.013733 | 0.31586 | 0.15106 | 0.21515 | 0.064087 | -0.11902 | 0.31128 | 0.1648 | 105.2902 | 105.4321 | 122.1268 | 122.3785 | 0.15106 | 122.374 | 102.887 | -0.11902 | 122.3785 | 0.15106 | 102.887 | 122.1268 | 122.374 | -122.0764 | -122.1817
1362.9219 | 122.3236 | -114.0381 | 8.0521 | 0.0096895 | -0.0017004 | 0.014813 | 0.022714 | 0.040575 | -0.031917 | 0.058422 | -113.9648 | 8.0658 | -114.1891 | -113.8596 | 8.0109 | -2.1332 | -0.36621 | 0.036621 | 8.1573 | -114.1846 | -0.15106 | 0.013733 | 0.073242 | 0.17853 | -0.041199 | -0.14648 | 0.10529 | 0.2243 | 113.6719 | 114.0747 | 122.049 | 122.1039 | 0.073242 | 122.1954 | 111.9049 | -0.14648 | 122.1039 | 0.073242 | 111.9049 | 122.049 | 122.1954 | -122.2412 | -122.2366
1364.7031 | 122.1817 | -115.6631 | 6.4178 | 0.00206 | 0.0036402 | 0.012463 | 0.027841 | 0.038439 | -0.034054 | 0.062694 | -115.5807 | 6.4316 | -115.8463 | -115.5121 | 6.2805 | -2.1652 | -0.21057 | 0.041199 | 6.5186 | -115.8783 | -0.18311 | 0.013733 | 0.082397 | 0.15106 | -0.13733 | -0.21515 | 0.10071 | 0.2655 | 115.4526 | 115.7043 | 121.9437 | 122.0947 | 0.082397 | 122.1817 | 113.4979 | -0.21515 | 122.0947 | 0.082397 | 113.4979 | 121.9437 | 122.1817 | -122.2641 | -122.2961
1366.5 | 122.2366 | -116.3773 | 5.6625 | 0.0096895 | 0.0019312 | 0.0081903 | 0.020151 | 0.038866 | -0.029354 | 0.060985 | -116.2903 | 5.6717 | -116.5192 | -116.1758 | 5.6168 | -2.124 | -0.35706 | 0.073242 | 5.7587 | -116.597 | -0.14191 | 0.009155 | 0.086975 | 0.20142 | -0.045777 | -0.21973 | 0.09613 | 0.22888 | 116.0202 | 116.4505 | 121.994 | 122.0489 | 0.086975 | 122.1359 | 114.2532 | -0.21973 | 122.0489 | 0.086975 | 114.2532 | 121.994 | 122.1359 | -122.1817 | -122.2595
1368.2188 | 122.1313 | -116.8808 | 5.1865 | 0.00206 | 0.0019312 | 0.011822 | 0.022501 | 0.037585 | -0.032345 | 0.056926 | -116.7572 | 5.1224 | -116.9998 | -116.6428 | 5.1315 | -2.1103 | -0.33417 | 0.16022 | 5.1956 | -117.0776 | -0.11902 | -0.064087 | 0.1236 | 0.23804 | -0.054931 | -0.19684 | 0.009156 | 0.24261 | 116.5466 | 117.041 | 122.0123 | 122.0032 | 0.1236 | 122.0764 | 114.7705 | -0.19684 | 122.0032 | 0.1236 | 114.7705 | 122.0123 | 122.0764 | -122.1863 | -122.2641
1370 | 122.1176 | -117.0593 | 4.9805 | 0.00206 | 0.00086298 | 0.0081903 | 0.024637 | 0.036517 | -0.032558 | 0.060344 | -116.9586 | 4.921 | -117.2012 | -116.8533 | 4.8752 | -2.1011 | -0.21515 | 0.15564 | 5.0171 | -117.2974 | -0.14191 | -0.05951 | 0.10071 | 0.20599 | -0.10529 | -0.23804 | 0.036621 | 0.24262 | 116.8442 | 117.215 | 121.9345 | 121.9803 | 0.10071 | 122.0764 | 114.9582 | -0.23804 | 121.9803 | 0.10071 | 114.9582 | 121.9345 | 122.0764 | -122.1817 | -122.2778
1371.7188 | 122.1451 | -116.4047 | 5.2734 | 0.0096895 | 0.0010766 | 0.012676 | 0.026987 | 0.038653 | -0.032558 | 0.064403 | -117.0364 | 4.8203 | -117.3386 | -116.8442 | 4.7882 | -2.1606 | -0.40283 | 0.004578 | 4.9347 | -117.3248 | -0.93384 | -0.45319 | -0.63171 | -0.43945 | -0.48523 | -0.9201 | -0.33875 | 0.30212 | 116.0019 | 116.4093 | 121.1929 | 121.225 | -0.63171 | 121.3394 | 114.2441 | -0.9201 | 121.225 | -0.63171 | 114.2441 | 121.1929 | 121.3394 | -122.612 | -122.5983
1373.5 | 122.2321 | -117.1555 | 4.7607 | 0.017319 | 0.001504 | 0.0092585 | 0.025919 | 0.035876 | -0.032558 | 0.061626 | -117.4072 | 4.6188 | -117.6041 | -117.334 | 4.4083 | -2.3209 | -0.30212 | -0.11444 | 4.7058 | -117.6178 | -0.44861 | -0.14191 | -0.25177 | -0.17853 | -0.35248 | -0.46234 | -0.054931 | 0.19684 | 116.8533 | 117.041 | 121.5637 | 121.7743 | -0.25177 | 121.8613 | 114.8346 | -0.46234 | 121.7743 | -0.25177 | 114.8346 | 121.5637 | 121.8613 | -122.3648 | -122.3785
1375.2188 | 122.1405 | -87.8311 | 34.0805 | 0.00206 | 0.0019312 | 0.01289 | 0.025064 | 0.039294 | -0.034267 | 0.05949 | -88.504 | 33.49 | -88.6551 | -88.3667 | 33.3252 | 0.45319 | 0.31586 | 0.45319 | 33.6548 | -88.5498 | -0.82397 | -0.59052 | -0.67291 | -0.53558 | -0.75531 | -0.71869 | -0.42572 | 0.15106 | 88.147 | 88.2843 | 121.1563 | 121.3211 | -0.67291 | 121.4859 | 88.2843 | -0.71869 | 121.3211 | -0.67291 | 88.2843 | 121.1563 | 121.4859 | -122.7356 | -122.6303
1376.9844 | 122.0856 | -93.8736 | 28.0655 | 0.017319 | 0.00022218 | 0.011395 | 0.025705 | 0.041216 | -0.032558 | 0.060131 | -92.6743 | 29.2923 | -92.8757 | -92.807 | 28.9352 | -9.256 | -3.4882 | -3.067 | 29.1962 | -93.0771 | 0.99793 | 1.2268 | 1.1993 | 1.0666 | 0.86975 | 0.79651 | 1.1307 | 0.20142 | 90.3854 | 90.8066 | 122.8088 | 123.1659 | 1.1993 | 123.0698 | 84.6176 | 0.79651 | 123.1659 | 1.1993 | 84.6176 | 122.8088 | 123.0698 | -120.9412 | -121.1426
1378.7656 | 122.049 | -79.6326 | 42.3386 | 0.0096895 | 0.0040674 | 0.010754 | 0.02421 | 0.041216 | -0.033413 | 0.058422 | -79.8706 | 42.1326 | -80.0308 | -79.715 | 41.9357 | 0.13733 | 0.064087 | 0.32501 | 42.247 | -80.0034 | -0.39825 | -0.20599 | -0.23804 | -0.082398 | -0.40283 | -0.37079 | -0.091553 | 0.16022 | 79.6967 | 79.9576 | 121.5683 | 121.7651 | -0.23804 | 121.8796 | 79.7699 | -0.37079 | 121.7651 | -0.23804 | 79.7699 | 121.5683 | 121.8796 | -122.3694 | -122.3419
1380.5469 | 122.1909 | -76.7395 | 45.1263 | 0.00206 | 0.004281 | 0.013744 | 0.023783 | 0.041857 | -0.033626 | 0.058635 | -77.0737 | 45.0165 | -77.1515 | -76.9821 | 44.6915 | 0.073242 | 0 | 0.11902 | 45.0897 | -77.2018 | -0.41199 | -0.10986 | -0.33417 | -0.24262 | -0.43488 | -0.46234 | -0.036621 | 0.07782 | 76.7395 | 76.8585 | 121.431 | 121.756 | -0.33417 | 121.8292 | 76.8127 | -0.46234 | 121.756 | -0.33417 | 76.8127 | 121.431 | 121.8292 | -122.2778 | -122.3282
1382.2812 | 122.2046 | -84.5993 | 37.2574 | 0.0096895 | 0.002572 | 0.010113 | 0.02421 | 0.041644 | -0.030208 | 0.060558 | -85.5652 | 36.1496 | -85.8307 | -85.5377 | 36.264 | -0.6546 | -0.13275 | 0.045776 | 36.7401 | -85.4507 | -1.2314 | -1.1078 | -0.96588 | -0.93842 | -0.99335 | -0.85144 | -0.51727 | 0.2655 | 84.4666 | 84.6451 | 120.8633 | 120.7489 | -0.96588 | 121.3394 | 83.9447 | -0.85144 | 120.7489 | -0.96588 | 83.9447 | 120.8633 | 121.3394 | -123.0881 | -122.7081
1384.0625 | 122.0856 | -95.7092 | 26.1749 | 0.00206 | 0.0066308 | 0.013531 | 0.026346 | 0.040575 | -0.03149 | 0.059276 | -96.0159 | 25.9003 | -96.2494 | -95.9793 | 25.7126 | -3.3554 | -0.2243 | 0.045776 | 25.9415 | -96.3455 | -0.54016 | -0.27466 | -0.3067 | -0.27008 | -0.46234 | -0.63629 | -0.23346 | 0.23346 | 95.4849 | 95.755 | 121.4218 | 121.6095 | -0.3067 | 121.6507 | 92.3538 | -0.63629 | 121.6095 | -0.3067 | 92.3538 | 121.4218 | 121.6507 | -122.4243 | -122.5204
1385.8281 | 121.9437 | -84.4666 | 37.4222 | 0.00206 | 0.0017176 | 0.012463 | 0.021646 | 0.039507 | -0.029995 | 0.058849 | -83.4915 | 38.2141 | -83.7891 | -83.8669 | 37.8525 | -2.4399 | -0.92926 | -0.44861 | 38.0081 | -84.1965 | 0.67749 | 0.79193 | 0.97504 | 0.59967 | 0.4303 | 0.27008 | 0.58594 | 0.29755 | 83.5373 | 84.0179 | 122.319 | 122.6807 | 0.97504 | 122.4747 | 82.0267 | 0.27008 | 122.6807 | 0.97504 | 82.0267 | 122.319 | 122.4747 | -121.2112 | -121.6187
1387.6094 | 121.9345 | -68.7424 | 53.0365 | 0.017319 | 0.0019312 | 0.010754 | 0.025278 | 0.040148 | -0.030636 | 0.058422 | -67.3782 | 54.744 | -67.3096 | -66.4627 | 54.7394 | 2.6367 | 1.1902 | 1.8585 | 55.7053 | -66.2933 | 1.4328 | 1.7075 | 1.3641 | 2.2797 | 1.7029 | 2.449 | 2.6688 | -0.068665 | 69.9326 | 70.6009 | 123.4818 | 123.4863 | 1.3641 | 124.4476 | 71.3791 | 2.449 | 123.4863 | 1.3641 | 71.3791 | 123.4818 | 124.4476 | -120.3461 | -119.3298
1389.3281 | 121.8201 | -87.2635 | 34.3231 | 0.00206 | 0.001504 | 0.012035 | 0.026773 | 0.038866 | -0.035976 | 0.057781 | -88.5498 | 33.0002 | -88.7787 | -88.385 | 33.0139 | -0.96588 | 0.45319 | 0.40283 | 33.6182 | -88.2477 | -1.5152 | -1.3229 | -1.2863 | -1.1215 | -1.3092 | -0.98419 | -0.70496 | 0.22888 | 87.7167 | 87.6663 | 120.2774 | 120.2637 | -1.2863 | 120.8817 | 86.2976 | -0.98419 | 120.2637 | -1.2863 | 86.2976 | 120.2774 | 120.8817 | -123.1018 | -122.5708
1391.1094 | 121.7651 | -83.876 | 37.5412 | 0.017319 | -0.0010596 | 0.012035 | 0.020365 | 0.038012 | -0.033199 | 0.057994 | -82.8735 | 38.6124 | -83.0978 | -83.3679 | 37.8067 | -1.4694 | -1.0941 | -0.66834 | 38.2004 | -83.5648 | 0.7782 | 1.0712 | 1.0025 | 0.50812 | 0.2655 | 0.31128 | 0.65918 | 0.2243 | 82.782 | 83.2077 | 121.6827 | 122.4884 | 1.0025 | 122.0764 | 82.4066 | 0.31128 | 122.4884 | 1.0025 | 82.4066 | 121.6827 | 122.0764 | -120.639 | -121.106
1392.8125 | 121.9208 | -71.3928 | 49.8459 | 0.017319 | -0.00063242 | 0.0081903 | 0.024851 | 0.037157 | -0.034694 | 0.06483 | -70.1202 | 51.3611 | -70.2484 | -70.2347 | 52.121 | 0.10529 | -0.54474 | -0.10071 | 52.3224 | -69.4885 | 1.1444 | 1.5152 | 1.2726 | 1.1581 | 2.2751 | 1.9043 | 2.4765 | 0.12817 | 70.8481 | 71.2921 | 123.5138 | 122.7539 | 1.2726 | 123.7152 | 71.4981 | 1.9043 | 122.7539 | 1.2726 | 71.4981 | 123.5138 | 123.7152 | -120.0943 | -119.3344
1394.5938 | 121.907 | -54.5792 | 67.2775 | 0.00206 | 0.0012902 | 0.01054 | 0.026987 | 0.040362 | -0.034481 | 0.058208 | -59.8618 | 63.1622 | -58.8547 | -58.905 | 63.1485 | 2.3026 | -0.32044 | 0.11444 | 63.8672 | -58.0261 | -4.2755 | -4.1153 | -5.2826 | -4.3259 | -4.129 | -3.447 | -3.4103 | -1.0071 | 54.2587 | 54.6936 | 117.7277 | 117.7414 | -5.2826 | 118.4463 | 56.8817 | -3.447 | 117.7414 | -5.2826 | 56.8817 | 117.7277 | 118.4463 | -126.1322 | -125.3037
1396.3125 | 121.9757 | -120.1813 | 1.4694 | 0.0096895 | 0.00086298 | 0.01289 | 0.030405 | 0.038866 | -0.033199 | 0.062053 | -120.2499 | 1.5289 | -120.5109 | -120.1721 | 1.3321 | -2.861 | -0.32501 | -0.14648 | 1.6113 | -120.4926 | -0.32959 | 0.05951 | -0.068665 | 0.009155 | -0.13733 | -0.31128 | 0.14191 | 0.26093 | 119.8563 | 120.0348 | 121.5134 | 121.7102 | -0.068665 | 121.7926 | 117.3203 | -0.31128 | 121.7102 | -0.068665 | 117.3203 | 121.5134 | 121.7926 | -121.9803 | -121.962
1398.0938 | 122.0261 | -120.5566 | 1.3458 | 0.00206 | -0.0029822 | 0.011181 | 0.022928 | 0.038012 | -0.034054 | 0.057994 | -120.488 | 1.3 | -120.7626 | -120.369 | 1.3092 | -2.4261 | -0.39368 | 0.086975 | 1.3962 | -120.7581 | -0.20599 | -0.045776 | 0.068665 | 0.18768 | -0.036621 | -0.20142 | 0.050354 | 0.27466 | 120.163 | 120.6436 | 121.8658 | 121.8567 | 0.068665 | 121.9528 | 118.1305 | -0.20142 | 121.8567 | 0.068665 | 118.1305 | 121.8658 | 121.9528 | -122.1085 | -122.1039
1399.8594 | 122.0993 | -120.6619 | 1.2909 | 0.00206 | 0.0032128 | 0.012035 | 0.028482 | 0.040575 | -0.032772 | 0.060131 | -120.6665 | 1.2772 | -120.9137 | -120.5933 | 1.1124 | -2.5497 | -0.21057 | -0.082397 | 1.3824 | -120.9045 | -0.25177 | -0.013733 | -0.004578 | 0.068664 | -0.17853 | -0.24262 | 0.091552 | 0.24719 | 120.4514 | 120.5795 | 121.7743 | 121.9391 | -0.004578 | 122.0444 | 118.1122 | -0.24262 | 121.9391 | -0.004578 | 118.1122 | 121.7743 | 122.0444 | -122.2046 | -122.1954
1401.5781 | 122.1313 | -120.7672 | 1.1719 | 0.017319 | 0.0023584 | 0.014172 | 0.026773 | 0.040789 | -0.033199 | 0.060985 | -120.7535 | 1.2085 | -120.9961 | -120.6528 | 1.1078 | -2.4719 | -0.41199 | -0.036621 | 1.2772 | -120.9869 | -0.22888 | 0.036621 | 0.013733 | 0.11444 | -0.064087 | -0.21973 | 0.10529 | 0.24262 | 120.3552 | 120.7306 | 121.875 | 121.9757 | 0.013733 | 122.0444 | 118.2953 | -0.21973 | 121.9757 | 0.013733 | 118.2953 | 121.875 | 122.0444 | -122.168 | -122.1588
1403.3594 | 122.2 | -120.7626 | 1.1948 | 0.0096895 | 0.00022218 | 0.012676 | 0.028055 | 0.04143 | -0.034908 | 0.060344 | -120.7993 | 1.2131 | -121.019 | -120.7123 | 1.0483 | -2.5314 | -0.25635 | -0.10071 | 1.3275 | -121.019 | -0.25635 | 0.018311 | -0.036621 | 0.050354 | -0.14648 | -0.25635 | 0.13275 | 0.21973 | 120.5063 | 120.6619 | 121.8109 | 121.9757 | -0.036621 | 122.0901 | 118.2312 | -0.25635 | 121.9757 | -0.036621 | 118.2312 | 121.8109 | 122.0901 | -122.2137 | -122.2137
1405.0625 | 122.1405 | -120.8221 | 1.149 | 0.00206 | 0.00022218 | 0.012249 | 0.023996 | 0.041216 | -0.03149 | 0.058849 | -120.7535 | 1.1398 | -121.0327 | -120.6665 | 1.1353 | -2.417 | -0.50354 | 0.004578 | 1.2131 | -121.0556 | -0.21057 | -0.009155 | 0.068665 | 0.15564 | -0.013733 | -0.23346 | 0.064087 | 0.27924 | 120.3186 | 120.8267 | 121.9574 | 121.962 | 0.068665 | 122.0352 | 118.4052 | -0.23346 | 121.962 | 0.068665 | 118.4052 | 121.9574 | 122.0352 | -122.1817 | -122.2046
1406.8281 | 122.2046 | -120.8038 | 1.1581 | 0.0096895 | -0.00063242 | 0.0073359 | 0.028055 | 0.043353 | -0.032772 | 0.060558 | -120.8817 | 1.1765 | -121.0739 | -120.8176 | 1.0071 | -2.5314 | -0.23804 | -0.082397 | 1.268 | -121.1014 | -0.27008 | 0.018311 | -0.07782 | -0.013733 | -0.15106 | -0.29755 | 0.10986 | 0.19226 | 120.5658 | 120.7214 | 121.8109 | 121.9803 | -0.07782 | 122.0718 | 118.2724 | -0.29755 | 121.9803 | -0.07782 | 118.2724 | 121.8109 | 122.0718 | -122.2321 | -122.2595
1408.6094 | 122.113 | -120.9778 | 1.0574 | 0.00206 | 0.00086298 | 0.011181 | 0.027841 | 0.040148 | -0.035763 | 0.060558 | -120.9274 | 1.0574 | -121.1929 | -120.8542 | 0.93842 | -2.4673 | -0.21515 | 0.032043 | 1.1627 | -121.2204 | -0.21515 | 0 | 0.050354 | 0.1236 | -0.11902 | -0.24262 | 0.10529 | 0.2655 | 120.7626 | 121.0098 | 121.9162 | 122.0352 | 0.050354 | 122.1405 | 118.5104 | -0.24262 | 122.0352 | 0.050354 | 118.5104 | 121.9162 | 122.1405 | -122.2504 | -122.2778
1410.3125 | 122.1954 | -121.0373 | 0.98419 | 0.0096895 | -0.00041862 | 0.011822 | 0.021219 | 0.038866 | -0.032345 | 0.060558 | -120.9595 | 0.94757 | -121.2158 | -120.8771 | 0.96588 | -2.4582 | -0.47607 | 0.009155 | 1.0391 | -121.2524 | -0.17853 | -0.036621 | 0.077819 | 0.16022 | -0.018311 | -0.21515 | 0.054932 | 0.25635 | 120.5612 | 121.0464 | 122.0032 | 121.9849 | 0.077819 | 122.0764 | 118.5791 | -0.21515 | 121.9849 | 0.077819 | 118.5791 | 122.0032 | 122.0764 | -122.2 | -122.2366
1412.0938 | 122.1222 | -121.0648 | 1.0117 | 0.0096895 | 0.0023584 | 0.010967 | 0.022501 | 0.038012 | -0.031704 | 0.058208 | -120.9595 | 1.0071 | -121.225 | -120.8771 | 0.95673 | -2.4216 | -0.26093 | 0.14648 | 1.0757 | -121.3165 | -0.16022 | -0.004578 | 0.10528 | 0.18768 | -0.054932 | -0.25177 | 0.064087 | 0.2655 | 120.8038 | 121.2112 | 122.0215 | 122.0718 | 0.10528 | 122.1405 | 118.6432 | -0.25177 | 122.0718 | 0.10528 | 118.6432 | 122.0215 | 122.1405 | -122.2366 | -122.3282
1413.8906 | 122.1268 | -121.0739 | 1.0117 | 0.0096895 | 0.00022218 | 0.010967 | 0.026132 | 0.038226 | -0.033199 | 0.060771 | -121.0373 | 1.0117 | -121.2753 | -120.9503 | 0.90179 | -2.4765 | -0.14648 | 0.064087 | 1.1078 | -121.2982 | -0.20142 | 0 | 0.036622 | 0.1236 | -0.10986 | -0.2243 | 0.09613 | 0.23804 | 120.9274 | 121.138 | 121.9757 | 122.0856 | 0.036622 | 122.1817 | 118.5974 | -0.2243 | 122.0856 | 0.036622 | 118.5974 | 121.9757 | 122.1817 | -122.287 | -122.3099
1415.6094 | 122.1222 | -121.1884 | 0.90179 | 0.0096895 | -0.00063242 | 0.01289 | 0.029123 | 0.041644 | -0.035122 | 0.059276 | -121.106 | 0.89264 | -121.4081 | -121.0236 | 0.80566 | -2.504 | -0.21057 | 0.054932 | 0.99335 | -121.3898 | -0.21973 | -0.009155 | 0.082397 | 0.16479 | -0.09613 | -0.20142 | 0.091553 | 0.30212 | 120.9778 | 121.2433 | 121.994 | 122.081 | 0.082397 | 122.1817 | 118.6844 | -0.20142 | 122.081 | 0.082397 | 118.6844 | 121.994 | 122.1817 | -122.3099 | -122.2916
1417.375 | 122.1634 | -121.7148 | 0.3891 | 0.017319 | 0.0027856 | 0.013531 | 0.025705 | 0.038866 | -0.031704 | 0.060131 | -121.7194 | 0.40283 | -121.9437 | -121.6324 | 0.26093 | -2.5726 | -0.1236 | 0.027466 | 0.48065 | -121.9574 | -0.22888 | 0.013733 | -0.004577 | 0.082398 | -0.12817 | -0.24261 | 0.091553 | 0.22431 | 121.5912 | 121.7422 | 121.9757 | 122.1176 | -0.004577 | 122.1954 | 119.1422 | -0.24261 | 122.1176 | -0.004577 | 119.1422 | 121.9757 | 122.1954 | -122.3328 | -122.3465
1419.1562 | 122.168 | -121.8018 | 0.28839 | 0.00206 | 0.0010766 | 0.0084039 | 0.027414 | 0.040575 | -0.031917 | 0.061412 | -121.7697 | 0.31128 | -122.0032 | -121.6873 | 0.1831 | -2.5681 | -0.2243 | -0.018311 | 0.3891 | -122.0398 | -0.20142 | 0.022888 | 0.032044 | 0.11444 | -0.10529 | -0.23804 | 0.10071 | 0.23346 | 121.5775 | 121.7834 | 121.9849 | 122.113 | 0.032044 | 122.1909 | 119.2337 | -0.23804 | 122.113 | 0.032044 | 119.2337 | 121.9849 | 122.1909 | -122.2916 | -122.3282
1420.9219 | 122.1405 | -121.8246 | 0.29755 | 0.017319 | 0.001504 | 0.01054 | 0.027841 | 0.040789 | -0.032558 | 0.059062 | -121.7514 | 0.27924 | -122.0123 | -121.6827 | 0.16479 | -2.5452 | -0.20599 | 0.018311 | 0.3891 | -122.0398 | -0.18768 | -0.01831 | 0.073242 | 0.14191 | -0.13275 | -0.21515 | 0.091553 | 0.26093 | 121.6187 | 121.843 | 121.9894 | 122.1039 | 0.073242 | 122.2137 | 119.2795 | -0.21515 | 122.1039 | 0.073242 | 119.2795 | 121.9894 | 122.2137 | -122.3099 | -122.3373
1422.7031 | 122.2366 | -121.8063 | 0.26093 | 0.0096895 | 0.0019312 | 0.012463 | 0.025705 | 0.039935 | -0.032345 | 0.06184 | -121.8246 | 0.28839 | -122.0581 | -121.7697 | 0.1236 | -2.6184 | -0.20599 | -0.07782 | 0.37537 | -122.0627 | -0.25177 | 0.027466 | -0.018311 | 0.036621 | -0.13733 | -0.25635 | 0.11444 | 0.23346 | 121.6003 | 121.7285 | 121.9299 | 122.0947 | -0.018311 | 122.1817 | 119.1879 | -0.25635 | 122.0947 | -0.018311 | 119.1879 | 121.9299 | 122.1817 | -122.319 | -122.3236
1424.5156 | 122.2549 | -121.7926 | 0.24261 | 0.00206 | -0.00020502 | 0.0071221 | 0.019724 | 0.039294 | -0.031917 | 0.05949 | -121.7926 | 0.27008 | -121.962 | -121.669 | 0.23804 | -2.5223 | -0.38452 | 0.036621 | 0.34332 | -122.0581 | -0.16937 | 0.027466 | 0 | 0.1236 | -0.004578 | -0.2655 | 0.10071 | 0.16937 | 121.4081 | 121.8292 | 122.0306 | 122.0627 | 0 | 122.1359 | 119.2703 | -0.2655 | 122.0627 | 0 | 119.2703 | 122.0306 | 122.1359 | -122.2046 | -122.3007
1426.2812 | 122.1954 | -121.8109 | 0.27924 | 0.024948 | 8.578e-06 | 0.011608 | 0.024423 | 0.03908 | -0.034267 | 0.05949 | -121.8384 | 0.30212 | -122.0535 | -121.7285 | 0.14191 | -2.6047 | -0.09613 | 0.018311 | 0.41199 | -122.0352 | -0.24262 | 0.022888 | -0.027466 | 0.082397 | -0.13733 | -0.2243 | 0.13275 | 0.21515 | 121.7148 | 121.8292 | 121.9528 | 122.113 | -0.027466 | 122.2229 | 119.2062 | -0.2243 | 122.113 | -0.027466 | 119.2062 | 121.9528 | 122.2229 | -122.3328 | -122.3145
1428 | 122.2595 | -121.7926 | 0.2655 | 0.00206 | 0.0023584 | 0.013744 | 0.025492 | 0.042284 | -0.033626 | 0.061626 | -121.843 | 0.29755 | -122.049 | -121.7697 | 0.1236 | -2.6413 | -0.24261 | -0.082397 | 0.37994 | -122.0627 | -0.25635 | 0.032043 | -0.050354 | 0.022889 | -0.14191 | -0.27008 | 0.11444 | 0.20599 | 121.55 | 121.7102 | 121.9162 | 122.0901 | -0.050354 | 122.1725 | 119.1513 | -0.27008 | 122.0901 | -0.050354 | 119.1513 | 121.9162 | 122.1725 | -122.3145 | -122.3282
1429.7188 | 122.1771 | -121.8292 | 0.29755 | 0.0096895 | -0.00063242 | 0.0092585 | 0.020792 | 0.039507 | -0.034267 | 0.059062 | -121.7377 | 0.25635 | -121.9849 | -121.6553 | 0.25177 | -2.5314 | -0.23346 | 0.09613 | 0.35706 | -122.0306 | -0.15564 | -0.041198 | 0.091553 | 0.17395 | -0.045776 | -0.20142 | 0.05951 | 0.24719 | 121.5958 | 121.9254 | 122.081 | 122.0856 | 0.091553 | 122.1863 | 119.2978 | -0.20142 | 122.0856 | 0.091553 | 119.2978 | 122.081 | 122.1863 | -122.2824 | -122.3282
1431.5156 | 122.1497 | -121.8063 | 0.31586 | -0.0055695 | 0.00022218 | 0.0098993 | 0.022714 | 0.036303 | -0.032772 | 0.057567 | -121.6736 | 0.27466 | -121.9437 | -121.5912 | 0.3067 | -2.4948 | -0.35706 | 0.1236 | 0.37537 | -122.0535 | -0.13733 | -0.041199 | 0.13275 | 0.21515 | -0.009155 | -0.24719 | 0.059509 | 0.27008 | 121.4493 | 121.9299 | 122.113 | 122.081 | 0.13275 | 122.1817 | 119.3115 | -0.24719 | 122.081 | 0.13275 | 119.3115 | 122.113 | 122.1817 | -122.2595 | -122.3694
1433.2344 | 122.2366 | -121.7972 | 0.3067 | 0.00206 | 0.00022218 | 0.010326 | 0.021433 | 0.037585 | -0.029568 | 0.058849 | -121.7148 | 0.28381 | -121.9803 | -121.6278 | 0.27924 | -2.5223 | -0.39825 | 0.073242 | 0.35706 | -122.0444 | -0.18311 | -0.022889 | 0.082397 | 0.16937 | -0.027466 | -0.24719 | 0.050354 | 0.2655 | 121.3989 | 121.8704 | 122.0764 | 122.081 | 0.082397 | 122.1542 | 119.2749 | -0.24719 | 122.081 | 0.082397 | 119.2749 | 122.0764 | 122.1542 | -122.287 | -122.3511
1434.9375 | 122.1588 | -121.8018 | 0.32501 | -0.0055695 | 0.0023584 | 0.011395 | 0.023783 | 0.036089 | -0.032772 | 0.057781 | -121.6965 | 0.27008 | -121.9528 | -121.582 | 0.30212 | -2.504 | -0.33417 | 0.12817 | 0.36163 | -122.049 | -0.15106 | -0.054931 | 0.10529 | 0.21973 | -0.022888 | -0.24719 | 0.036621 | 0.25635 | 121.4676 | 121.9299 | 122.1039 | 122.0718 | 0.10529 | 122.1634 | 119.2978 | -0.24719 | 122.0718 | 0.10529 | 119.2978 | 122.1039 | 122.1634 | -122.2778 | -122.374
1436.7188 | 122.2824 | -121.7606 | 0.28381 | 0.0096895 | 0.0010766 | 0.012463 | 0.029123 | 0.039935 | -0.03619 | 0.060558 | -121.8246 | 0.32044 | -122.049 | -121.7331 | 0.16479 | -2.6688 | -0.3067 | -0.10071 | 0.41657 | -122.0169 | -0.28839 | 0.036622 | -0.064087 | 0.027466 | -0.11902 | -0.25635 | 0.13275 | 0.2243 | 121.4539 | 121.6599 | 121.9254 | 122.081 | -0.064087 | 122.1771 | 119.0918 | -0.25635 | 122.081 | -0.064087 | 119.0918 | 121.9254 | 122.1771 | -122.3328 | -122.3007
1438.5 | 122.168 | -121.8155 | 0.31586 | 0.0096895 | 0.00064938 | 0.0098993 | 0.022928 | 0.037157 | -0.03149 | 0.058208 | -121.6873 | 0.28839 | -121.9574 | -121.5775 | 0.29297 | -2.5131 | -0.37079 | 0.11444 | 0.37079 | -122.0306 | -0.14191 | -0.027466 | 0.12817 | 0.23804 | -0.022888 | -0.21515 | 0.054932 | 0.27008 | 121.4447 | 121.9299 | 122.1085 | 122.1039 | 0.12817 | 122.1863 | 119.3024 | -0.21515 | 122.1039 | 0.12817 | 119.3024 | 122.1085 | 122.1863 | -122.2733 | -122.3465
1440.2812 | 122.0947 | -121.2479 | 0.87433 | 0.00206 | -0.00063242 | 0.0098993 | 0.02186 | 0.038653 | -0.034481 | 0.058849 | -121.138 | 0.79651 | -121.4767 | -121.0419 | 0.82398 | -2.3621 | -0.32959 | 0.16022 | 0.87891 | -121.4951 | -0.22888 | -0.07782 | 0.10986 | 0.20599 | -0.050354 | -0.24719 | 0.004577 | 0.33875 | 120.9183 | 121.4081 | 122.0718 | 122.0444 | 0.10986 | 122.1268 | 118.8858 | -0.24719 | 122.0444 | 0.10986 | 118.8858 | 122.0718 | 122.1268 | -122.3511 | -122.3694
1442.0469 | 122.1451 | -119.87 | 2.0782 | 0.017319 | 0.00086298 | 0.01289 | 0.028055 | 0.041644 | -0.033199 | 0.060771 | -119.8746 | 2.1103 | -120.1126 | -119.8105 | 1.9455 | -2.5864 | -0.2655 | -0.11444 | 2.1973 | -120.1355 | -0.24262 | 0.032044 | -0.004578 | 0.059509 | -0.13275 | -0.2655 | 0.11902 | 0.23804 | 119.6045 | 119.7556 | 121.8155 | 121.9803 | -0.004578 | 122.0673 | 117.2836 | -0.2655 | 121.9803 | -0.004578 | 117.2836 | 121.8155 | 122.0673 | -122.1909 | -122.2137
1443.7656 | 122.1588 | -121.2021 | 0.75531 | -0.0055695 | 0.0010766 | 0.0098993 | 0.023142 | 0.038866 | -0.029995 | 0.05949 | -121.1105 | 0.78278 | -121.3852 | -121.0373 | 0.75531 | -2.6321 | -0.48523 | -0.036621 | 0.84228 | -121.431 | -0.18311 | 0.027466 | 0.091552 | 0.1648 | 0 | -0.22888 | 0.086975 | 0.27466 | 120.7169 | 121.1655 | 121.9574 | 121.9849 | 0.091552 | 122.0444 | 118.5699 | -0.22888 | 121.9849 | 0.091552 | 118.5699 | 121.9574 | 122.0444 | -122.1405 | -122.1863
1445.5469 | 121.9299 | -118.9453 | 2.8702 | 0.00206 | -0.00084602 | 0.011395 | 0.023996 | 0.040362 | -0.031917 | 0.058849 | -118.8217 | 2.8336 | -119.1284 | -118.7531 | 2.829 | -2.4261 | -0.5127 | 0.009155 | 2.9297 | -119.1696 | -0.18311 | -0.036621 | 0.1236 | 0.19226 | -0.041199 | -0.22431 | 0.059509 | 0.3067 | 118.4326 | 118.9545 | 121.7743 | 121.7789 | 0.1236 | 121.875 | 116.5192 | -0.22431 | 121.7789 | 0.1236 | 116.5192 | 121.7743 | 121.875 | -121.9986 | -122.0398
1447.3281 | 121.8292 | -119.0826 | 2.6871 | 0.00206 | 0.0021448 | 0.01054 | 0.023783 | 0.037798 | -0.034481 | 0.05949 | -118.9499 | 2.6688 | -119.2474 | -118.8446 | 2.6688 | -2.4216 | -0.37079 | 0.10071 | 2.742 | -119.3024 | -0.16479 | -0.018311 | 0.13275 | 0.23804 | -0.018311 | -0.21973 | 0.054931 | 0.29755 | 118.7119 | 119.1834 | 121.7514 | 121.7514 | 0.13275 | 121.8246 | 116.6611 | -0.21973 | 121.7514 | 0.13275 | 116.6611 | 121.7514 | 121.8246 | -121.9345 | -121.9894
1449.0469 | 121.907 | -119.1467 | 2.5269 | 0.0096895 | 0.001504 | 0.014385 | 0.023355 | 0.038866 | -0.031704 | 0.058208 | -119.1696 | 2.5085 | -119.3939 | -119.0552 | 2.4353 | -2.449 | -0.3891 | -0.009155 | 2.5772 | -119.4763 | -0.24719 | -0.01831 | -0.022888 | 0.091553 | -0.091552 | -0.32959 | 0.050354 | 0.2243 | 118.7576 | 119.1376 | 121.582 | 121.6553 | -0.022888 | 121.7239 | 116.6977 | -0.32959 | 121.6553 | -0.022888 | 116.6977 | 121.582 | 121.7239 | -121.9208 | -122.0032
1450.8281 | 121.6049 | -117.9977 | 3.6484 | 0.0096895 | -0.00063242 | 0.011395 | 0.026132 | 0.037157 | -0.03384 | 0.05949 | -118.071 | 3.4836 | -118.2449 | -117.6865 | 3.4561 | -2.536 | -0.36163 | 0.26093 | 3.5934 | -118.2541 | -0.24719 | -0.16479 | -0.073242 | 0.31128 | -0.19226 | -0.25635 | -0.054931 | 0.17395 | 117.6361 | 118.2587 | 121.4539 | 121.4813 | -0.073242 | 121.5912 | 115.4617 | -0.25635 | 121.4813 | -0.073242 | 115.4617 | 121.4539 | 121.5912 | -121.8933 | -121.9025
1452.5938 | 121.7056 | -118.9819 | 2.6642 | 0.00206 | -0.0010596 | 0.012676 | 0.028055 | 0.040362 | -0.036617 | 0.058422 | -118.9316 | 2.6688 | -119.2017 | -118.8171 | 2.5543 | -2.4582 | -0.19226 | 0.050354 | 2.7695 | -119.1834 | -0.21973 | 0.004577 | 0.050354 | 0.16479 | -0.10986 | -0.20142 | 0.10529 | 0.27008 | 118.7897 | 119.0323 | 121.5363 | 121.6507 | 0.050354 | 121.7514 | 116.5237 | -0.20142 | 121.6507 | 0.050354 | 116.5237 | 121.5363 | 121.7514 | -121.8658 | -121.8475
1454.375 | 121.7377 | -118.9453 | 2.6688 | 0.00206 | 0.002572 | 0.012676 | 0.027201 | 0.040362 | -0.032558 | 0.059276 | -118.9728 | 2.6688 | -119.1925 | -118.8858 | 2.5177 | -2.5085 | -0.11444 | 0.009155 | 2.7466 | -119.2429 | -0.24719 | 0 | -0.027466 | 0.059509 | -0.15106 | -0.29755 | 0.07782 | 0.21973 | 118.8309 | 118.9545 | 121.463 | 121.6141 | -0.027466 | 121.6919 | 116.4368 | -0.29755 | 121.6141 | -0.027466 | 116.4368 | 121.463 | 121.6919 | -121.8613 | -121.9116
1456.1562 | 121.6919 | -118.9453 | 2.5955 | 0.0096895 | -0.0012732 | 0.011608 | 0.027841 | 0.039935 | -0.032985 | 0.058635 | -118.9133 | 2.6184 | -119.1742 | -118.7897 | 2.6001 | -1.7624 | -0.38452 | 0.059509 | 2.7008 | -119.1467 | -0.22888 | 0.022888 | 0.032043 | 0.15564 | 0.004578 | -0.20142 | 0.10529 | 0.26093 | 118.5608 | 119.0048 | 121.5454 | 121.5637 | 0.032043 | 121.6461 | 117.1829 | -0.20142 | 121.5637 | 0.032043 | 117.1829 | 121.5454 | 121.6461 | -121.7697 | -121.7422
1457.9219 | 121.7514 | -119.0964 | 2.4261 | 0.0096895 | -0.0010596 | 0.01054 | 0.028055 | 0.041857 | -0.034267 | 0.060558 | -119.1467 | 2.4628 | -119.2841 | -119.0186 | 2.3712 | -2.5589 | -0.23804 | -0.1236 | 2.6138 | -119.3573 | -0.18768 | 0.036622 | -0.050354 | 0.07782 | -0.054931 | -0.26093 | 0.18768 | 0.13733 | 118.8583 | 118.9728 | 121.4676 | 121.5591 | -0.050354 | 121.7102 | 116.5375 | -0.26093 | 121.5591 | -0.050354 | 116.5375 | 121.4676 | 121.7102 | -121.7102 | -121.7834
1459.7031 | 121.637 | -119.6274 | 1.9089 | 0.0096895 | -0.00063242 | 0.0090447 | 0.022287 | 0.038226 | -0.033626 | 0.057567 | -119.6182 | 1.886 | -119.8563 | -119.5267 | 1.7853 | -2.5818 | -0.16937 | 0.027466 | 2.0096 | -119.8608 | -0.22888 | -0.022889 | 0.009155 | 0.10071 | -0.1236 | -0.23346 | 0.10071 | 0.23804 | 119.458 | 119.6548 | 121.4127 | 121.5134 | 0.009155 | 121.637 | 117.0456 | -0.23346 | 121.5134 | 0.009155 | 117.0456 | 121.4127 | 121.637 | -121.7651 | -121.7697
1461.4375 | 121.4859 | -119.8196 | 1.6754 | 0.0096895 | 0.0017176 | 0.012676 | 0.022928 | 0.037798 | -0.030422 | 0.05714 | -119.6182 | 1.5976 | -120.0119 | -119.632 | 1.6159 | -2.3758 | -0.33417 | 0.018311 | 1.6891 | -120.2774 | -0.19226 | -0.07782 | 0.20142 | 0.18768 | -0.059509 | -0.45776 | 0.013733 | 0.39368 | 119.4855 | 119.838 | 121.4355 | 121.4172 | 0.20142 | 121.5088 | 117.4438 | -0.45776 | 121.4172 | 0.20142 | 117.4438 | 121.4355 | 121.5088 | -121.6873 | -121.9528
1463.2188 | 121.344 | -120.4697 | 0.86975 | 0.00206 | 0.0040674 | 0.012249 | 0.028696 | 0.041216 | -0.035763 | 0.058849 | -120.4605 | 0.91095 | -120.7535 | -120.282 | 0.79193 | -2.5818 | -0.29297 | 0.022888 | 0.92926 | -120.6985 | -0.28381 | 0.041199 | 0.009156 | 0.18768 | -0.07782 | -0.22888 | 0.059509 | 0.29297 | 120.1767 | 120.4926 | 121.2616 | 121.3806 | 0.009156 | 121.3989 | 117.8879 | -0.22888 | 121.3806 | 0.009156 | 117.8879 | 121.2616 | 121.3989 | -121.6232 | -121.5683
1465 | 121.3623 | -118.8675 | 2.3117 | -0.013199 | 0.0012902 | 0.011395 | 0.02656 | 0.03908 | -0.033626 | 0.061412 | -118.8126 | 2.3254 | -119.0781 | -118.7347 | 2.2797 | -2.4994 | -0.45776 | -0.036621 | 2.3895 | -119.1055 | -0.21057 | 0.013732 | 0.054932 | 0.13275 | -0.032044 | -0.23804 | 0.077819 | 0.2655 | 118.4097 | 118.8309 | 121.1472 | 121.1929 | 0.054932 | 121.257 | 116.3681 | -0.23804 | 121.1929 | 0.054932 | 116.3681 | 121.1472 | 121.257 | -121.3898 | -121.4172
1466.7188 | 121.701 | -121.4401 | 0.13275 | 0.00206 | 8.578e-06 | 0.0098993 | 0.019724 | 0.037371 | -0.032345 | 0.060558 | -121.3806 | 0.11902 | -121.5958 | -121.2753 | 0.091553 | -2.6505 | -0.40741 | -0.013733 | 0.21515 | -121.6644 | -0.15564 | -0.013732 | 0.05951 | 0.16479 | -0.041198 | -0.2243 | 0.082398 | 0.21515 | 121.0327 | 121.4264 | 121.5317 | 121.5591 | 0.05951 | 121.6553 | 118.7897 | -0.2243 | 121.5591 | 0.05951 | 118.7897 | 121.5317 | 121.6553 | -121.7285 | -121.7972
1468.5 | 121.7239 | -121.5454 | 0.16937 | -0.0055695 | 0.00086298 | 0.012249 | 0.024851 | 0.036089 | -0.032772 | 0.057994 | -121.4722 | 0.13275 | -121.7239 | -121.3852 | 0.082397 | -2.6138 | -0.24261 | 0.059509 | 0.20142 | -121.7972 | -0.17853 | -0.036622 | 0.073242 | 0.16022 | -0.086976 | -0.25177 | 0.032043 | 0.25177 | 121.3028 | 121.6049 | 121.6278 | 121.6782 | 0.073242 | 121.7468 | 118.9316 | -0.25177 | 121.6782 | 0.073242 | 118.9316 | 121.6278 | 121.7468 | -121.8933 | -121.9666
1470.2812 | 121.8109 | -121.582 | 0.13733 | 0.00206 | 0.0012902 | 0.011181 | 0.030191 | 0.039294 | -0.034267 | 0.060344 | -121.5866 | 0.14191 | -121.8475 | -121.4951 | 0.022888 | -2.7191 | -0.24261 | -0.086975 | 0.23346 | -121.8384 | -0.2655 | 0.004578 | -0.004578 | 0.086975 | -0.11444 | -0.25635 | 0.09613 | 0.26093 | 121.3394 | 121.4951 | 121.6049 | 121.7239 | -0.004578 | 121.8155 | 118.8629 | -0.25635 | 121.7239 | -0.004578 | 118.8629 | 121.6049 | 121.8155 | -121.9849 | -121.9757
1472 | 121.8704 | -121.5271 | 0.21515 | 0.0096895 | -0.001914 | 0.011181 | 0.023783 | 0.041216 | -0.033413 | 0.061199 | -121.4493 | 0.19226 | -121.7148 | -121.3486 | 0.21515 | -2.6276 | -0.50812 | -0.022888 | 0.2655 | -121.756 | -0.18768 | -0.022888 | 0.07782 | 0.17853 | 0 | -0.22888 | 0.050354 | 0.2655 | 121.019 | 121.5042 | 121.7422 | 121.7194 | 0.07782 | 121.7926 | 118.8995 | -0.22888 | 121.7194 | 0.07782 | 118.8995 | 121.7422 | 121.7926 | -121.9299 | -121.9711
1473.7812 | 121.8979 | -121.55 | 0.19226 | -0.0055695 | 0.0027856 | 0.011822 | 0.025919 | 0.039721 | -0.033199 | 0.059703 | -121.4905 | 0.16937 | -121.7606 | -121.4127 | 0.17395 | -2.6321 | -0.5127 | -0.036621 | 0.25635 | -121.8246 | -0.21057 | -0.022888 | 0.059509 | 0.13733 | -0.018311 | -0.27466 | 0.064087 | 0.27008 | 121.0373 | 121.5134 | 121.7239 | 121.7194 | 0.059509 | 121.8063 | 118.9178 | -0.27466 | 121.7194 | 0.059509 | 118.9178 | 121.7239 | 121.8063 | -121.9528 | -122.0169
1475.5 | 121.875 | -121.3028 | 0.49439 | 0.00206 | 0.002572 | 0.010754 | 0.02656 | 0.039507 | -0.031063 | 0.057994 | -121.312 | 0.50354 | -121.5225 | -121.2067 | 0.35706 | -2.6688 | -0.14191 | 0.004578 | 0.59052 | -121.55 | -0.21973 | 0.009155 | -0.009156 | 0.09613 | -0.13733 | -0.24719 | 0.09613 | 0.21057 | 121.1609 | 121.3074 | 121.6599 | 121.8063 | -0.009156 | 121.8933 | 118.634 | -0.24719 | 121.8063 | -0.009156 | 118.634 | 121.6599 | 121.8933 | -122.0169 | -122.0444
1477.2656 | 121.8704 | -121.1197 | 0.6546 | 0.00206 | 0.00064938 | 0.012035 | 0.025064 | 0.03908 | -0.034054 | 0.05949 | -121.1472 | 0.67291 | -121.3531 | -121.051 | 0.52185 | -2.6779 | -0.14191 | -0.009155 | 0.75531 | -121.3989 | -0.23346 | 0.018311 | -0.027466 | 0.068665 | -0.13275 | -0.27924 | 0.10071 | 0.20599 | 120.9778 | 121.1105 | 121.6415 | 121.7926 | -0.027466 | 121.875 | 118.4418 | -0.27924 | 121.7926 | -0.027466 | 118.4418 | 121.6415 | 121.875 | -122.0078 | -122.0535
1479.0469 | 121.8384 | -121.0327 | 0.74158 | -0.0055695 | -0.0010596 | 0.012676 | 0.026987 | 0.039507 | -0.03619 | 0.05949 | -120.9961 | 0.75073 | -121.2845 | -120.9183 | 0.61798 | -2.6505 | -0.2655 | -0.041199 | 0.82398 | -121.2799 | -0.25177 | 0.009155 | 0.036621 | 0.11444 | -0.1236 | -0.24719 | 0.082398 | 0.28839 | 120.7672 | 120.9915 | 121.6507 | 121.7834 | 0.036621 | 121.8567 | 118.3823 | -0.24719 | 121.7834 | 0.036621 | 118.3823 | 121.6507 | 121.8567 | -122.0261 | -122.0215
1480.7656 | 121.9574 | -120.9641 | 0.7782 | 0.00206 | 0.00022218 | 0.0075495 | 0.021005 | 0.03908 | -0.033626 | 0.060131 | -120.9091 | 0.76446 | -121.1517 | -120.8542 | 0.74158 | -2.6459 | -0.48065 | -0.068665 | 0.85144 | -121.225 | -0.18768 | -0.013733 | 0.054931 | 0.10986 | -0.036621 | -0.26093 | 0.073242 | 0.24261 | 120.4834 | 120.8954 | 121.7056 | 121.7285 | 0.054931 | 121.8155 | 118.3182 | -0.26093 | 121.7285 | 0.054931 | 118.3182 | 121.7056 | 121.8155 | -121.9299 | -122.0032
1482.5469 | 121.843 | -120.9732 | 0.80109 | 0.0096895 | 0.00064938 | 0.011822 | 0.022287 | 0.037585 | -0.034267 | 0.059276 | -120.9137 | 0.79193 | -121.17 | -120.8221 | 0.737 | -2.6321 | -0.24261 | 0.022888 | 0.89264 | -121.2158 | -0.19684 | -0.009155 | 0.05951 | 0.15106 | -0.064086 | -0.24261 | 0.091553 | 0.25635 | 120.7306 | 120.9961 | 121.7102 | 121.7651 | 0.05951 | 121.8658 | 118.3411 | -0.24261 | 121.7651 | 0.05951 | 118.3411 | 121.7102 | 121.8658 | -121.9711 | -122.0169
1484.2656 | 121.8796 | -120.9732 | 0.80109 | 0.00206 | 0.0036402 | 0.0088311 | 0.020365 | 0.037371 | -0.029995 | 0.05949 | -120.8725 | 0.7782 | -121.1288 | -120.7718 | 0.81024 | -2.5864 | -0.4303 | 0.068665 | 0.86975 | -121.2112 | -0.15564 | -0.022888 | 0.10071 | 0.20142 | 0.009156 | -0.23804 | 0.068665 | 0.25635 | 120.5429 | 121.0419 | 121.7834 | 121.7514 | 0.10071 | 121.843 | 118.3868 | -0.23804 | 121.7514 | 0.10071 | 118.3868 | 121.7834 | 121.843 | -121.9299 | -122.0123
1486.0312 | 121.8475 | -120.9732 | 0.8194 | -0.0055695 | 0.00086298 | 0.0073359 | 0.023355 | 0.037585 | -0.034481 | 0.058635 | -120.8542 | 0.77362 | -121.1288 | -120.7626 | 0.80109 | -2.5909 | -0.45319 | 0.073242 | 0.88348 | -121.2021 | -0.15564 | -0.045776 | 0.11902 | 0.21057 | -0.018311 | -0.22888 | 0.064087 | 0.27466 | 120.52 | 121.0464 | 121.7743 | 121.7468 | 0.11902 | 121.8567 | 118.3823 | -0.22888 | 121.7468 | 0.11902 | 118.3823 | 121.7743 | 121.8567 | -121.9482 | -122.0215
1487.75 | 121.8613 | -120.9412 | 0.85144 | -0.0055695 | -0.0014868 | 0.010967 | 0.024637 | 0.037371 | -0.035122 | 0.059276 | -120.8542 | 0.82855 | -121.1472 | -120.7901 | 0.76446 | -2.6505 | -0.24261 | 0.036621 | 0.9201 | -121.1884 | -0.20599 | -0.022888 | 0.086975 | 0.15106 | -0.086975 | -0.24719 | 0.068665 | 0.29297 | 120.6985 | 120.9778 | 121.7056 | 121.7697 | 0.086975 | 121.8613 | 118.2907 | -0.24719 | 121.7697 | 0.086975 | 118.2907 | 121.7056 | 121.8613 | -121.9986 | -122.0398
1489.5469 | 121.8201 | -120.9412 | 0.85602 | 0.00206 | -0.001914 | 0.0086175 | 0.022928 | 0.037798 | -0.033626 | 0.05949 | -120.845 | 0.82855 | -121.1288 | -120.7169 | 0.83771 | -2.5864 | -0.3891 | 0.082397 | 0.89722 | -121.1517 | -0.18768 | -0.027466 | 0.09613 | 0.2243 | -0.01831 | -0.21057 | 0.041199 | 0.28381 | 120.5521 | 121.0236 | 121.7789 | 121.7697 | 0.09613 | 121.8384 | 118.3548 | -0.21057 | 121.7697 | 0.09613 | 118.3548 | 121.7789 | 121.8384 | -121.9849 | -122.0078
1491.3281 | 121.8658 | -120.932 | 0.87891 | 0.00206 | 0.0021448 | 0.0073359 | 0.026773 | 0.039294 | -0.032985 | 0.058208 | -120.9091 | 0.87433 | -121.1426 | -120.8221 | 0.71869 | -2.7054 | -0.15564 | -0.013733 | 0.95673 | -121.1746 | -0.21057 | -0.004577 | 0.022888 | 0.10986 | -0.16022 | -0.24262 | 0.07782 | 0.23346 | 120.7764 | 120.9183 | 121.6507 | 121.8063 | 0.022888 | 121.8887 | 118.2266 | -0.24262 | 121.8063 | 0.022888 | 118.2266 | 121.6507 | 121.8887 | -122.0215 | -122.0535
1493.0312 | 121.9345 | -120.9045 | 0.82855 | 0.00206 | 0.00022218 | 0.0088311 | 0.028269 | 0.038653 | -0.032772 | 0.060131 | -120.9366 | 0.85602 | -121.1746 | -120.8588 | 0.67749 | -2.7512 | -0.2655 | -0.15106 | 0.92926 | -121.1838 | -0.27008 | 0.027466 | -0.032043 | 0.045776 | -0.15106 | -0.27924 | 0.10071 | 0.23804 | 120.639 | 120.7535 | 121.582 | 121.7606 | -0.032043 | 121.8338 | 118.1534 | -0.27924 | 121.7606 | -0.032043 | 118.1534 | 121.582 | 121.8338 | -122.0032 | -122.0123
1494.8125 | 121.962 | -120.8908 | 0.81482 | 0.00206 | 0.0019312 | 0.01054 | 0.027628 | 0.042071 | -0.031917 | 0.060771 | -120.9457 | 0.8606 | -121.1838 | -120.8542 | 0.70496 | -2.7466 | -0.3067 | -0.14648 | 0.94757 | -121.1746 | -0.29297 | 0.045777 | -0.054932 | 0.036621 | -0.10986 | -0.28381 | 0.13275 | 0.23804 | 120.5841 | 120.7443 | 121.5958 | 121.7514 | -0.054932 | 121.8384 | 118.1442 | -0.28381 | 121.7514 | -0.054932 | 118.1442 | 121.5958 | 121.8384 | -121.9986 | -121.9894
1496.6094 | 121.8338 | -120.9229 | 0.84686 | 0.0096895 | 0.0019312 | 0.0075495 | 0.027841 | 0.040148 | -0.034694 | 0.059703 | -120.8771 | 0.84686 | -121.17 | -120.8038 | 0.74158 | -2.6871 | -0.30212 | -0.041199 | 0.94299 | -121.17 | -0.24719 | 0 | 0.045777 | 0.11902 | -0.10529 | -0.24719 | 0.09613 | 0.29297 | 120.6207 | 120.8817 | 121.6644 | 121.7697 | 0.045777 | 121.8658 | 118.2358 | -0.24719 | 121.7697 | 0.045777 | 118.2358 | 121.6644 | 121.8658 | -122.0169 | -122.0169
1498.3906 | 121.907 | -120.9457 | 0.83313 | -0.0055695 | 0.0012902 | 0.0086175 | 0.022074 | 0.041644 | -0.033199 | 0.059062 | -120.8313 | 0.80109 | -121.1105 | -120.7397 | 0.83771 | -2.655 | -0.54932 | -0.036621 | 0.87433 | -121.1472 | -0.16479 | -0.032044 | 0.11444 | 0.20599 | 0.004578 | -0.20142 | 0.041199 | 0.27924 | 120.3964 | 120.9091 | 121.7834 | 121.7468 | 0.11444 | 121.8201 | 118.2907 | -0.20142 | 121.7468 | 0.11444 | 118.2907 | 121.7834 | 121.8201 | -121.9437 | -121.9803
1500.1562 | 121.9574 | -120.8817 | 0.83313 | 0.00206 | -0.0012732 | 0.0069085 | 0.019724 | 0.038012 | -0.032131 | 0.058849 | -120.8862 | 0.8194 | -121.1151 | -120.8038 | 0.76904 | -2.71 | -0.4303 | -0.086975 | 0.91095 | -121.1609 | -0.23346 | -0.013733 | -0.004577 | 0.07782 | -0.064087 | -0.27924 | 0.07782 | 0.22888 | 120.4514 | 120.7947 | 121.6507 | 121.701 | -0.004577 | 121.7926 | 118.1717 | -0.27924 | 121.701 | -0.004577 | 118.1717 | 121.6507 | 121.7926 | -121.9482 | -121.994
1501.8594 | 121.8155 | -120.9229 | 0.87433 | -0.0055695 | -0.00041862 | 0.0064813 | 0.022074 | 0.039507 | -0.032772 | 0.060131 | -120.7993 | 0.81482 | -121.0831 | -120.6985 | 0.84686 | -2.623 | -0.43488 | 0.054932 | 0.91095 | -121.1197 | -0.16022 | -0.05951 | 0.1236 | 0.22431 | -0.027466 | -0.19684 | 0.036621 | 0.28381 | 120.488 | 120.9778 | 121.7697 | 121.7377 | 0.1236 | 121.8338 | 118.2999 | -0.19684 | 121.7377 | 0.1236 | 118.2999 | 121.7697 | 121.8338 | -121.9574 | -121.994
1503.6406 | 121.907 | -120.9 | 0.83771 | 0.0096895 | -0.0023412 | 0.010967 | 0.024423 | 0.040148 | -0.032985 | 0.059917 | -120.8176 | 0.80566 | -121.0922 | -120.7489 | 0.8194 | -2.6962 | -0.55389 | -0.07782 | 0.88806 | -121.1288 | -0.19226 | -0.032044 | 0.082397 | 0.15106 | -0.018311 | -0.22888 | 0.050354 | 0.27466 | 120.3461 | 120.8221 | 121.7194 | 121.7056 | 0.082397 | 121.788 | 118.2037 | -0.22888 | 121.7056 | 0.082397 | 118.2037 | 121.7194 | 121.788 | -121.9299 | -121.9666
1505.4219 | 121.8613 | -120.932 | 0.85144 | 0.0096895 | -0.00020502 | 0.0077631 | 0.025705 | 0.040148 | -0.035335 | 0.058422 | -120.9137 | 0.84228 | -121.1655 | -120.8267 | 0.71411 | -2.7512 | -0.18768 | -0.045776 | 0.95673 | -121.1792 | -0.23346 | -0.009155 | 0.018311 | 0.10529 | -0.13733 | -0.24719 | 0.10529 | 0.25177 | 120.7443 | 120.8862 | 121.6461 | 121.7743 | 0.018311 | 121.8887 | 118.1808 | -0.24719 | 121.7743 | 0.018311 | 118.1808 | 121.6461 | 121.8887 | -122.0169 | -122.0306
1507.1875 | 121.8933 | -120.8817 | 0.85602 | 0.0096895 | -0.0014868 | 0.014385 | 0.023142 | 0.038012 | -0.033413 | 0.059062 | -120.8176 | 0.83313 | -121.1014 | -120.7214 | 0.84228 | -2.6688 | -0.46692 | 0.013733 | 0.92926 | -121.138 | -0.21973 | -0.022888 | 0.064087 | 0.16022 | -0.013733 | -0.25635 | 0.073242 | 0.28381 | 120.4147 | 120.8954 | 121.7239 | 121.7148 | 0.064087 | 121.8109 | 118.2129 | -0.25635 | 121.7148 | 0.064087 | 118.2129 | 121.7239 | 121.8109 | -121.9574 | -121.994
1508.9844 | 121.9666 | -120.8405 | 0.84686 | 0.0096895 | 0.0012902 | 0.014172 | 0.023996 | 0.037585 | -0.034054 | 0.059917 | -120.8405 | 0.83313 | -121.1014 | -120.7672 | 0.79651 | -2.742 | -0.45776 | -0.09613 | 0.93384 | -121.1334 | -0.26093 | -0.013733 | 0 | 0.073242 | -0.050354 | -0.29297 | 0.086975 | 0.26093 | 120.3827 | 120.7443 | 121.637 | 121.6736 | 0 | 121.7743 | 118.0984 | -0.29297 | 121.6736 | 0 | 118.0984 | 121.637 | 121.7743 | -121.9482 | -121.9803
1510.7656 | 121.8658 | -120.8725 | 0.87433 | 0.0096895 | 0.0019312 | 0.0081903 | 0.02891 | 0.03908 | -0.034694 | 0.059062 | -120.9091 | 0.87433 | -121.1288 | -120.7993 | 0.72784 | -2.7649 | -0.19684 | -0.068665 | 0.95673 | -121.1746 | -0.25635 | 0 | -0.036621 | 0.073243 | -0.14648 | -0.30212 | 0.082397 | 0.21973 | 120.6757 | 120.8038 | 121.6003 | 121.7468 | -0.036621 | 121.8292 | 118.1076 | -0.30212 | 121.7468 | -0.036621 | 118.1076 | 121.6003 | 121.8292 | -122.0032 | -122.049
1512.5469 | 121.8979 | -120.8633 | 0.84228 | -0.0055695 | 0.0038538 | 0.014813 | 0.025705 | 0.040148 | -0.031063 | 0.059276 | -120.8267 | 0.86975 | -121.0968 | -120.7352 | 0.8194 | -2.7237 | -0.50812 | -0.091553 | 0.91095 | -121.1334 | -0.23346 | 0.027466 | 0.036621 | 0.12817 | -0.022888 | -0.27008 | 0.068665 | 0.27008 | 120.3552 | 120.7718 | 121.6827 | 121.7331 | 0.036621 | 121.7743 | 118.1396 | -0.27008 | 121.7331 | 0.036621 | 118.1396 | 121.6827 | 121.7743 | -121.9391 | -121.9757
1514.2656 | 121.8018 | -120.9091 | 0.90179 | 0.00206 | -0.00020502 | 0.013317 | 0.024851 | 0.038653 | -0.031277 | 0.060344 | -120.7626 | 0.8606 | -121.019 | -120.6619 | 0.89722 | -2.6596 | -0.42114 | 0.054932 | 0.95673 | -121.1197 | -0.10986 | -0.041198 | 0.14648 | 0.24719 | -0.004577 | -0.21057 | 0.054932 | 0.25635 | 120.488 | 120.9641 | 121.8063 | 121.7697 | 0.14648 | 121.8658 | 118.2495 | -0.21057 | 121.7697 | 0.14648 | 118.2495 | 121.8063 | 121.8658 | -121.9208 | -122.0215
1516.0312 | 121.8842 | -121.5317 | 0.27924 | 0.017319 | -0.00041862 | 0.012676 | 0.025492 | 0.038866 | -0.034694 | 0.05949 | -121.5134 | 0.2655 | -121.7834 | -121.4264 | 0.16022 | -2.8152 | -0.23804 | -0.068665 | 0.36163 | -121.8109 | -0.25177 | -0.013733 | 0.01831 | 0.10528 | -0.11902 | -0.27924 | 0.082397 | 0.27008 | 121.2936 | 121.463 | 121.6919 | 121.7972 | 0.01831 | 121.8933 | 118.7164 | -0.27924 | 121.7972 | 0.01831 | 118.7164 | 121.6919 | 121.8933 | -122.0627 | -122.0901
1517.7969 | 121.875 | -121.5363 | 0.30212 | 0.017319 | -0.00084602 | 0.012035 | 0.023355 | 0.038439 | -0.032558 | 0.059917 | -121.4355 | 0.24719 | -121.6965 | -121.3394 | 0.28381 | -2.71 | -0.44403 | 0.022888 | 0.33875 | -121.7926 | -0.16022 | -0.054932 | 0.10071 | 0.19684 | -0.018311 | -0.25635 | 0.036621 | 0.26093 | 121.0922 | 121.5591 | 121.8201 | 121.7834 | 0.10071 | 121.875 | 118.8263 | -0.25635 | 121.7834 | 0.10071 | 118.8263 | 121.8201 | 121.875 | -121.9986 | -122.0947
1519.5156 | 122.0078 | -121.5134 | 0.2655 | 0.0096895 | 0.0044946 | 0.0079767 | 0.027841 | 0.038866 | -0.033199 | 0.061199 | -121.5408 | 0.31586 | -121.788 | -121.463 | 0.16479 | -2.861 | -0.42572 | -0.19226 | 0.37079 | -121.8201 | -0.27466 | 0.050354 | -0.027466 | 0.050354 | -0.10071 | -0.3067 | 0.10529 | 0.24719 | 121.0876 | 121.3211 | 121.6782 | 121.8292 | -0.027466 | 121.8842 | 118.6523 | -0.3067 | 121.8292 | -0.027466 | 118.6523 | 121.6782 | 121.8842 | -122.0535 | -122.0856
1521.2969 | 121.8933 | -121.5866 | 0.30212 | -0.0055695 | 0.0029992 | 0.01289 | 0.021433 | 0.036303 | -0.03149 | 0.058635 | -121.4447 | 0.25635 | -121.7468 | -121.3486 | 0.3067 | -2.7145 | -0.4303 | 0.036621 | 0.32959 | -121.8338 | -0.16022 | -0.045776 | 0.14191 | 0.23804 | 0.004578 | -0.24719 | 0.027466 | 0.30212 | 121.1563 | 121.6232 | 121.8933 | 121.843 | 0.14191 | 121.9162 | 118.8721 | -0.24719 | 121.843 | 0.14191 | 118.8721 | 121.8933 | 121.9162 | -122.049 | -122.1359
1523.0625 | 122.0444 | -121.5225 | 0.30212 | 0.017319 | 0.00022218 | 0.01289 | 0.021219 | 0.038226 | -0.032985 | 0.059917 | -121.4951 | 0.27466 | -121.7331 | -121.431 | 0.24261 | -2.8152 | -0.48981 | -0.14191 | 0.35248 | -121.8018 | -0.21057 | -0.027466 | 0.027466 | 0.091553 | -0.059509 | -0.27924 | 0.050354 | 0.23804 | 121.0327 | 121.3806 | 121.7651 | 121.7972 | 0.027466 | 121.875 | 118.7073 | -0.27924 | 121.7972 | 0.027466 | 118.7073 | 121.7651 | 121.875 | -122.0352 | -122.1039
1524.8438 | 122.0261 | -121.5225 | 0.28381 | 0.0096895 | 0.0019312 | 0.014599 | 0.027201 | 0.039935 | -0.036617 | 0.057567 | -121.5729 | 0.3067 | -121.843 | -121.4859 | 0.13733 | -2.9114 | -0.33417 | -0.17853 | 0.39368 | -121.8063 | -0.32044 | 0.022889 | -0.050354 | 0.036621 | -0.14648 | -0.28381 | 0.10986 | 0.27008 | 121.1884 | 121.344 | 121.6599 | 121.8292 | -0.050354 | 121.9162 | 118.6111 | -0.28381 | 121.8292 | -0.050354 | 118.6111 | 121.6599 | 121.9162 | -122.1268 | -122.0901
1526.5625 | 121.9894 | -121.5454 | 0.28839 | 0.0096895 | 8.578e-06 | 0.010967 | 0.025919 | 0.04143 | -0.036831 | 0.061199 | -121.4676 | 0.29297 | -121.7514 | -121.3806 | 0.28839 | -2.7924 | -0.58594 | -0.10529 | 0.35706 | -121.7789 | -0.20599 | 0.004578 | 0.07782 | 0.16479 | 0 | -0.23346 | 0.068665 | 0.28381 | 120.9595 | 121.4401 | 121.8338 | 121.8384 | 0.07782 | 121.9025 | 118.7531 | -0.23346 | 121.8384 | 0.07782 | 118.7531 | 121.8338 | 121.9025 | -122.0398 | -122.0673
1528.3281 | 122.0627 | -121.5179 | 0.28381 | 0.0096895 | -0.00041862 | 0.0088311 | 0.023355 | 0.040148 | -0.031704 | 0.059062 | -121.5042 | 0.3067 | -121.7468 | -121.4127 | 0.24261 | -2.8336 | -0.49439 | -0.13275 | 0.38452 | -121.8292 | -0.22888 | 0.022889 | 0.013733 | 0.10528 | -0.041198 | -0.31128 | 0.10071 | 0.24262 | 121.0236 | 121.3852 | 121.7606 | 121.8246 | 0.013733 | 121.9025 | 118.6844 | -0.31128 | 121.8246 | 0.013733 | 118.6844 | 121.7606 | 121.9025 | -122.0306 | -122.113
1530.0469 | 122.0535 | -121.5546 | 0.28381 | -0.0055695 | 8.578e-06 | 0.0098993 | 0.025919 | 0.041857 | -0.035122 | 0.060131 | -121.5637 | 0.31128 | -121.8384 | -121.4767 | 0.18768 | -2.9022 | -0.44403 | -0.20599 | 0.41199 | -121.8338 | -0.28381 | 0.027466 | -0.009156 | 0.077819 | -0.09613 | -0.27924 | 0.12817 | 0.27466 | 121.1105 | 121.3486 | 121.7422 | 121.8658 | -0.009156 | 121.9666 | 118.6523 | -0.27924 | 121.8658 | -0.009156 | 118.6523 | 121.7422 | 121.9666 | -122.1222 | -122.1176
1531.8125 | 122.0673 | -121.5317 | 0.3067 | 0.00206 | -0.00084602 | 0.012463 | 0.027628 | 0.039721 | -0.034908 | 0.05949 | -121.582 | 0.31128 | -121.7972 | -121.4996 | 0.17853 | -2.9297 | -0.37079 | -0.23346 | 0.4303 | -121.8201 | -0.2655 | 0.004577 | -0.050354 | 0.032043 | -0.12817 | -0.28839 | 0.1236 | 0.21515 | 121.1609 | 121.2982 | 121.7102 | 121.843 | -0.050354 | 121.962 | 118.602 | -0.28839 | 121.843 | -0.050354 | 118.602 | 121.7102 | 121.962 | -122.1039 | -122.1268
1533.5938 | 122.0627 | -121.5546 | 0.3067 | 0.00206 | 0.00086298 | 0.011181 | 0.021005 | 0.039507 | -0.032131 | 0.060131 | -121.5317 | 0.29755 | -121.756 | -121.4264 | 0.27466 | -2.8564 | -0.49896 | -0.12817 | 0.37994 | -121.8338 | -0.20142 | -0.009156 | 0.022888 | 0.12817 | -0.032044 | -0.27924 | 0.073242 | 0.2243 | 121.0556 | 121.4264 | 121.8292 | 121.8521 | 0.022888 | 121.9345 | 118.6981 | -0.27924 | 121.8521 | 0.022888 | 118.6981 | 121.8292 | 121.9345 | -122.0627 | -122.1405
1535.375 | 122.0856 | -121.5271 | 0.29755 | 0.0096895 | -0.00063242 | 0.01054 | 0.027628 | 0.040362 | -0.034908 | 0.061412 | -121.5866 | 0.31128 | -121.8384 | -121.4996 | 0.1831 | -2.948 | -0.3891 | -0.23346 | 0.42114 | -121.8338 | -0.31128 | 0.013733 | -0.059509 | 0.027466 | -0.11444 | -0.3067 | 0.1236 | 0.25177 | 121.138 | 121.2936 | 121.7102 | 121.8384 | -0.059509 | 121.9482 | 118.5791 | -0.3067 | 121.8384 | -0.059509 | 118.5791 | 121.7102 | 121.9482 | -122.1359 | -122.1313
1537.1406 | 121.9528 | -121.5683 | 0.32959 | 0.0096895 | 0.0010766 | 0.010326 | 0.027201 | 0.040575 | -0.035763 | 0.060131 | -121.5317 | 0.31586 | -121.8063 | -121.4447 | 0.22888 | -2.8702 | -0.33875 | -0.11902 | 0.40741 | -121.8384 | -0.23804 | -0.013733 | 0.036621 | 0.1236 | -0.10071 | -0.27008 | 0.07782 | 0.27466 | 121.2296 | 121.4493 | 121.7972 | 121.8842 | 0.036621 | 121.9757 | 118.6981 | -0.27008 | 121.8842 | 0.036621 | 118.6981 | 121.7972 | 121.9757 | -122.1359 | -122.168
1538.8594 | 122.0901 | -121.5591 | 0.28381 | -0.0055695 | -0.00020502 | 0.0092585 | 0.02656 | 0.043566 | -0.034908 | 0.061412 | -121.6278 | 0.30212 | -121.8338 | -121.5317 | 0.16022 | -2.9434 | -0.36621 | -0.23346 | 0.39825 | -121.8567 | -0.27466 | 0.018311 | -0.068665 | 0.027466 | -0.1236 | -0.29755 | 0.11444 | 0.20599 | 121.1929 | 121.3257 | 121.7194 | 121.8613 | -0.068665 | 121.9574 | 118.6157 | -0.29755 | 121.8613 | -0.068665 | 118.6157 | 121.7194 | 121.9574 | -122.1176 | -122.1405
1540.6406 | 122.0627 | -121.6003 | 0.29297 | 0.0096895 | 0.0021448 | 0.011395 | 0.021219 | 0.037585 | -0.032345 | 0.05949 | -121.5088 | 0.27924 | -121.7743 | -121.4447 | 0.27924 | -2.861 | -0.60425 | -0.17853 | 0.37537 | -121.8887 | -0.17395 | -0.013733 | 0.091553 | 0.15564 | -0.013733 | -0.28839 | 0.082397 | 0.2655 | 120.9961 | 121.4218 | 121.8796 | 121.8796 | 0.091553 | 121.9757 | 118.7393 | -0.28839 | 121.8796 | 0.091553 | 118.7393 | 121.8796 | 121.9757 | -122.0673 | -122.1817
1542.4219 | 121.994 | -121.6324 | 0.32501 | 0.00206 | 0.00043578 | 0.012249 | 0.023569 | 0.038439 | -0.030208 | 0.058422 | -121.5225 | 0.27466 | -121.7972 | -121.4539 | 0.2655 | -2.8519 | -0.36621 | -0.086975 | 0.40283 | -121.8887 | -0.16479 | -0.050354 | 0.10986 | 0.17853 | -0.059509 | -0.25635 | 0.07782 | 0.27466 | 121.2662 | 121.5454 | 121.8979 | 121.907 | 0.10986 | 122.0352 | 118.7805 | -0.25635 | 121.907 | 0.10986 | 118.7805 | 121.8979 | 122.0352 | -122.1222 | -122.2137
1544.1875 | 121.9528 | -121.6599 | 0.29297 | 0.00206 | 0.0017176 | 0.01054 | 0.028482 | 0.038866 | -0.035976 | 0.060344 | -121.5866 | 0.27008 | -121.875 | -121.4859 | 0.19684 | -2.8839 | -0.37994 | -0.12817 | 0.38452 | -121.8842 | -0.21515 | -0.022888 | 0.073242 | 0.17395 | -0.096131 | -0.2243 | 0.091552 | 0.28839 | 121.2799 | 121.5317 | 121.8567 | 121.9299 | 0.073242 | 122.0444 | 118.7759 | -0.2243 | 121.9299 | 0.073242 | 118.7759 | 121.8567 | 122.0444 | -122.168 | -122.1771
1545.9844 | 122.1085 | -121.6003 | 0.24719 | 0.0096895 | -0.002555 | 0.010967 | 0.02186 | 0.037798 | -0.030422 | 0.060985 | -121.6049 | 0.25177 | -121.8475 | -121.5225 | 0.21057 | -2.9297 | -0.54932 | -0.2243 | 0.33417 | -121.8887 | -0.24719 | 0.004578 | -0.004577 | 0.07782 | -0.036621 | -0.28839 | 0.086975 | 0.24262 | 121.051 | 121.376 | 121.8109 | 121.8521 | -0.004577 | 121.9345 | 118.6707 | -0.28839 | 121.8521 | -0.004577 | 118.6707 | 121.8109 | 121.9345 | -122.0947 | -122.1359
1547.7656 | 121.9666 | -121.669 | 0.27008 | 0.00206 | 0.00022218 | 0.0098993 | 0.021646 | 0.038653 | -0.034481 | 0.05949 | -121.5408 | 0.21973 | -121.8567 | -121.4584 | 0.24719 | -2.8381 | -0.4715 | -0.07782 | 0.34332 | -121.9025 | -0.18768 | -0.050354 | 0.12817 | 0.21057 | -0.022889 | -0.23346 | 0.073242 | 0.31586 | 121.1975 | 121.5912 | 121.9162 | 121.8887 | 0.12817 | 122.0123 | 118.8309 | -0.23346 | 121.8887 | 0.12817 | 118.8309 | 121.9162 | 122.0123 | -122.1268 | -122.1725
1549.5625 | 121.9757 | -121.6736 | 0.27924 | 0.00206 | -0.00041862 | 0.011822 | 0.022074 | 0.036089 | -0.029568 | 0.059703 | -121.55 | 0.23346 | -121.8613 | -121.4539 | 0.2655 | -2.8656 | -0.56763 | -0.086975 | 0.31128 | -121.907 | -0.18768 | -0.045777 | 0.1236 | 0.21973 | -0.013733 | -0.23346 | 0.032043 | 0.31128 | 121.106 | 121.5866 | 121.9391 | 121.907 | 0.1236 | 121.9849 | 118.808 | -0.23346 | 121.907 | 0.1236 | 118.808 | 121.9391 | 121.9849 | -122.1405 | -122.1863
1551.2969 | 122.0078 | -121.7651 | 0.16022 | 0.0096895 | 0.0010766 | 0.013104 | 0.028055 | 0.039294 | -0.035549 | 0.061199 | -121.788 | 0.14648 | -122.0123 | -121.6873 | 0.027466 | -2.9938 | -0.30212 | -0.20142 | 0.26093 | -122.049 | -0.24719 | -0.013733 | -0.022888 | 0.07782 | -0.13275 | -0.28381 | 0.10071 | 0.2243 | 121.463 | 121.5637 | 121.7926 | 121.9116 | -0.022888 | 122.0261 | 118.7714 | -0.28381 | 121.9116 | -0.022888 | 118.7714 | 121.7926 | 122.0261 | -122.1725 | -122.2092
1553.0781 | 121.9849 | -121.788 | 0.15106 | -0.0055695 | 0.0019312 | 0.010113 | 0.027841 | 0.03908 | -0.034908 | 0.059062 | -121.7651 | 0.13275 | -122.049 | -121.6599 | 0.045776 | -2.9526 | -0.37079 | -0.17395 | 0.23804 | -122.0673 | -0.26093 | -0.018311 | 0.022888 | 0.12817 | -0.10529 | -0.27924 | 0.086975 | 0.28381 | 121.4172 | 121.6141 | 121.8338 | 121.9208 | 0.022888 | 122.0261 | 118.8354 | -0.27924 | 121.9208 | 0.022888 | 118.8354 | 121.8338 | 122.0261 | -122.2 | -122.2183
1554.7812 | 122.081 | -121.7514 | 0.10986 | -0.0055695 | 8.578e-06 | 0.011822 | 0.017801 | 0.040148 | -0.032131 | 0.059062 | -121.7239 | 0.11902 | -121.9757 | -121.6415 | 0.073242 | -2.9846 | -0.62256 | -0.27924 | 0.18768 | -122.0352 | -0.2243 | 0.009156 | 0.027466 | 0.10986 | -0.036621 | -0.28381 | 0.07782 | 0.25177 | 121.1288 | 121.4722 | 121.8246 | 121.8704 | 0.027466 | 121.9391 | 118.7668 | -0.28381 | 121.8704 | 0.027466 | 118.7668 | 121.8246 | 121.9391 | -122.0856 | -122.1451
1556.5781 | 122.1085 | -121.7651 | 0.11902 | 0.0096895 | 0.0019312 | 0.013958 | 0.028269 | 0.038012 | -0.033413 | 0.05949 | -121.788 | 0.12817 | -122.0398 | -121.7194 | 0.009155 | -3.0579 | -0.52185 | -0.33875 | 0.23804 | -122.0764 | -0.27466 | 0.009155 | -0.022888 | 0.045777 | -0.10986 | -0.31128 | 0.11902 | 0.25177 | 121.2433 | 121.4264 | 121.7743 | 121.8933 | -0.022888 | 122.0032 | 118.7073 | -0.31128 | 121.8933 | -0.022888 | 118.7073 | 121.7743 | 122.0032 | -122.1588 | -122.1954
1558.3594 | 121.9574 | -120.163 | 1.6937 | 0.0096895 | -0.0023412 | 0.0096857 | 0.024637 | 0.038226 | -0.032345 | 0.059703 | -120.0943 | 1.6663 | -120.4102 | -120.0348 | 1.6113 | -2.8427 | -0.55389 | -0.45776 | 1.7166 | -120.7489 | -0.24719 | -0.027466 | 0.068665 | 0.12817 | -0.082398 | -0.58594 | 0.022888 | 0.31586 | 119.6091 | 119.7052 | 121.7743 | 121.8292 | 0.068665 | 121.8796 | 117.3203 | -0.58594 | 121.8292 | 0.068665 | 117.3203 | 121.7743 | 121.8796 | -122.1039 | -122.4426
1560.1406 | 122.0581 | -121.7743 | 0.09613 | 0.017319 | 0.0021448 | 0.013104 | 0.028482 | 0.040575 | -0.031277 | 0.060131 | -121.8063 | 0.11444 | -122.0352 | -121.7194 | -0.032043 | -3.0899 | -0.49439 | -0.37079 | 0.20599 | -122.0581 | -0.26093 | 0.018311 | -0.032043 | 0.054932 | -0.12817 | -0.28381 | 0.10986 | 0.22888 | 121.2799 | 121.4035 | 121.7422 | 121.8887 | -0.032043 | 121.9803 | 118.6844 | -0.28381 | 121.8887 | -0.032043 | 118.6844 | 121.7422 | 121.9803 | -122.1313 | -122.1542
1561.8594 | 122.0123 | -121.8384 | 0.10986 | -0.0055695 | 0.00064938 | 0.010967 | 0.023996 | 0.03908 | -0.035763 | 0.059703 | -121.8338 | 0.1236 | -122.0764 | -121.7422 | -0.009155 | -3.0487 | -0.31586 | -0.24719 | 0.20599 | -122.1222 | -0.23804 | 0.013733 | 0.004578 | 0.09613 | -0.11902 | -0.28381 | 0.096131 | 0.24262 | 121.5225 | 121.5912 | 121.8292 | 121.962 | 0.004578 | 122.0444 | 118.7897 | -0.28381 | 121.962 | 0.004578 | 118.7897 | 121.8292 | 122.0444 | -122.1863 | -122.2321
1563.6406 | 121.962 | -121.8658 | 0.1236 | 0.0096895 | 0.0023584 | 0.011822 | 0.026987 | 0.040789 | -0.032985 | 0.060985 | -121.788 | 0.10071 | -122.081 | -121.6965 | 0.041199 | -3.0212 | -0.42114 | -0.22888 | 0.19684 | -122.113 | -0.21515 | -0.022888 | 0.07782 | 0.16937 | -0.082397 | -0.24719 | 0.073242 | 0.29297 | 121.4447 | 121.637 | 121.907 | 121.9666 | 0.07782 | 122.0627 | 118.8446 | -0.24719 | 121.9666 | 0.07782 | 118.8446 | 121.907 | 122.0627 | -122.2046 | -122.2366
1565.4219 | 122.0581 | -121.8521 | 0.086975 | -0.0055695 | 0.0019312 | 0.0088311 | 0.022501 | 0.038866 | -0.033413 | 0.059917 | -121.8613 | 0.1236 | -122.1085 | -121.7789 | -0.013733 | -3.067 | -0.32501 | -0.29755 | 0.21515 | -122.1588 | -0.25635 | 0.036621 | -0.009155 | 0.073242 | -0.10071 | -0.3067 | 0.12817 | 0.24719 | 121.5271 | 121.5546 | 121.8384 | 121.9757 | -0.009155 | 122.0673 | 118.7851 | -0.3067 | 121.9757 | -0.009155 | 118.7851 | 121.8384 | 122.0673 | -122.1954 | -122.2458
1567.2031 | 122.0673 | -121.8567 | 0.11444 | -0.0055695 | -0.00041862 | 0.010754 | 0.023142 | 0.037371 | -0.032558 | 0.06184 | -121.8796 | 0.1236 | -122.1039 | -121.7789 | -0.004578 | -3.0808 | -0.3479 | -0.3067 | 0.21973 | -122.1451 | -0.24719 | 0.009155 | -0.022889 | 0.077819 | -0.11902 | -0.28839 | 0.10529 | 0.2243 | 121.5088 | 121.55 | 121.8521 | 121.9803 | -0.022889 | 122.0764 | 118.7759 | -0.28839 | 121.9803 | -0.022889 | 118.7759 | 121.8521 | 122.0764 | -122.2183 | -122.2595
1569.0156 | 122.049 | -121.8613 | 0.10529 | 0.00206 | -0.00084602 | 0.0096857 | 0.022714 | 0.038866 | -0.03384 | 0.058635 | -121.8613 | 0.10529 | -122.0993 | -121.7743 | -0.004578 | -3.1128 | -0.40283 | -0.31128 | 0.20142 | -122.1497 | -0.23804 | 0 | 0 | 0.086975 | -0.10986 | -0.28839 | 0.09613 | 0.23804 | 121.4584 | 121.55 | 121.8567 | 121.9666 | 0 | 122.0627 | 118.7485 | -0.28839 | 121.9666 | 0 | 118.7485 | 121.8567 | 122.0627 | -122.2046 | -122.2549
1570.8125 | 122.0215 | -121.8658 | 0.14191 | 0.017319 | 0.0012902 | 0.010113 | 0.026773 | 0.039721 | -0.034054 | 0.059917 | -121.8338 | 0.11444 | -122.1085 | -121.7422 | 0.032043 | -3.0899 | -0.46692 | -0.29755 | 0.1831 | -122.1542 | -0.24261 | -0.027466 | 0.032044 | 0.1236 | -0.10986 | -0.28839 | 0.041198 | 0.27466 | 121.3989 | 121.5683 | 121.8979 | 121.9803 | 0.032044 | 122.0489 | 118.7759 | -0.28839 | 121.9803 | 0.032044 | 118.7759 | 121.8979 | 122.0489 | -122.2504 | -122.2961
1572.5156 | 122.1497 | -121.8887 | 0.09613 | 0.00206 | -0.0023412 | 0.0071221 | 0.021433 | 0.039507 | -0.030636 | 0.059703 | -121.8109 | 0.073242 | -122.049 | -121.7468 | 0.064087 | -3.0808 | -0.6958 | -0.34332 | 0.16479 | -122.1451 | -0.16022 | -0.022888 | 0.07782 | 0.14191 | -0.032043 | -0.25635 | 0.068665 | 0.23804 | 121.1929 | 121.5454 | 121.9528 | 121.962 | 0.07782 | 122.0535 | 118.808 | -0.25635 | 121.962 | 0.07782 | 118.808 | 121.9528 | 122.0535 | -122.1451 | -122.2412
1574.2969 | 122.1039 | -121.8933 | 0.10986 | -0.0055695 | 0.001504 | 0.0092585 | 0.022501 | 0.038226 | -0.032558 | 0.060344 | -121.8018 | 0.07782 | -122.0718 | -121.7056 | 0.091553 | -3.0487 | -0.6134 | -0.26093 | 0.16022 | -122.1451 | -0.17853 | -0.032043 | 0.091553 | 0.18768 | -0.01831 | -0.25177 | 0.050354 | 0.27008 | 121.2799 | 121.6324 | 121.9849 | 121.9711 | 0.091553 | 122.0535 | 118.8446 | -0.25177 | 121.9711 | 0.091553 | 118.8446 | 121.9849 | 122.0535 | -122.1817 | -122.2549
1576.0312 | 122.1268 | -121.8887 | 0.086975 | -0.0055695 | 0.00022218 | 0.015453 | 0.02656 | 0.042925 | -0.032772 | 0.060344 | -121.7743 | 0.082397 | -122.0947 | -121.7056 | 0.07782 | -3.0853 | -0.74616 | -0.36163 | 0.16937 | -122.1268 | -0.20599 | -0.004578 | 0.11444 | 0.18311 | -0.009155 | -0.23804 | 0.082398 | 0.32044 | 121.1426 | 121.5271 | 121.9666 | 121.9711 | 0.11444 | 122.0581 | 118.8034 | -0.23804 | 121.9711 | 0.11444 | 118.8034 | 121.9666 | 122.0581 | -122.1817 | -122.2137
1577.8125 | 122.1542 | -121.8704 | 0.082397 | 0.00206 | 0.0010766 | 0.016094 | 0.028482 | 0.038866 | -0.032772 | 0.062053 | -121.8887 | 0.086975 | -122.1313 | -121.8063 | -0.004578 | -3.1723 | -0.64087 | -0.45319 | 0.16937 | -122.1542 | -0.26093 | 0.004578 | -0.018311 | 0.064087 | -0.086975 | -0.28381 | 0.086976 | 0.24262 | 121.2296 | 121.4172 | 121.8658 | 121.9574 | -0.018311 | 122.0398 | 118.6981 | -0.28381 | 121.9574 | -0.018311 | 118.6981 | 121.8658 | 122.0398 | -122.2137 | -122.2366
1579.6094 | 122.1863 | -121.8704 | 0.082397 | 0.00206 | 0.0019312 | 0.010754 | 0.02891 | 0.039507 | -0.033199 | 0.058849 | -121.9025 | 0.10071 | -122.1863 | -121.843 | -0.027466 | -3.2272 | -0.5722 | -0.49896 | 0.20599 | -122.2092 | -0.31586 | 0.018311 | -0.032044 | 0.027465 | -0.10986 | -0.33874 | 0.1236 | 0.28381 | 121.2982 | 121.3715 | 121.843 | 121.9711 | -0.032044 | 122.0764 | 118.6432 | -0.33874 | 121.9711 | -0.032044 | 118.6432 | 121.843 | 122.0764 | -122.2687 | -122.2916
1581.3438 | 122.1176 | -121.9208 | 0.10529 | 0.0096895 | 0.002572 | 0.013531 | 0.023783 | 0.040148 | -0.031704 | 0.060558 | -121.9208 | 0.11902 | -122.1634 | -121.843 | -0.018311 | -3.186 | -0.39825 | -0.3891 | 0.19684 | -122.2275 | -0.24262 | 0.013733 | 0 | 0.077819 | -0.1236 | -0.3067 | 0.091552 | 0.24262 | 121.5225 | 121.5317 | 121.9025 | 122.0398 | 0 | 122.1176 | 118.7347 | -0.3067 | 122.0398 | 0 | 118.7347 | 121.9025 | 122.1176 | -122.2687 | -122.3328
1583.1094 | 122.113 | -121.907 | 0.091553 | 0.00206 | -0.00063242 | 0.014172 | 0.025064 | 0.03908 | -0.03149 | 0.060558 | -121.9299 | 0.10986 | -122.1405 | -121.8338 | -0.009155 | -3.2135 | -0.41199 | -0.41657 | 0.19226 | -122.2137 | -0.23346 | 0.01831 | -0.022889 | 0.073242 | -0.10071 | -0.3067 | 0.10071 | 0.21057 | 121.4951 | 121.4905 | 121.8979 | 122.0169 | -0.022889 | 122.0993 | 118.6935 | -0.3067 | 122.0169 | -0.022889 | 118.6935 | 121.8979 | 122.0993 | -122.2321 | -122.3053
1584.8281 | 122.0581 | -121.9299 | 0.10986 | 0.00206 | -0.00084602 | 0.012249 | 0.026346 | 0.038653 | -0.034481 | 0.06184 | -121.8521 | 0.091553 | -122.1405 | -121.7926 | 0.022888 | -3.2043 | -0.54016 | -0.42572 | 0.19226 | -122.1817 | -0.21057 | -0.01831 | 0.07782 | 0.13733 | -0.086975 | -0.25177 | 0.082398 | 0.28839 | 121.3898 | 121.5042 | 121.9528 | 122.0215 | 0.07782 | 122.1222 | 118.7256 | -0.25177 | 122.0215 | 0.07782 | 118.7256 | 121.9528 | 122.1222 | -122.2504 | -122.2916
1586.625 | 122.2 | -121.9254 | 0.086975 | 0.00206 | -0.00020502 | 0.0098993 | 0.021433 | 0.040789 | -0.030636 | 0.059917 | -121.8521 | 0.07782 | -122.113 | -121.8018 | 0.054932 | -3.2593 | -0.78735 | -0.52643 | 0.15106 | -122.1634 | -0.18768 | -0.009155 | 0.073242 | 0.1236 | -0.032043 | -0.23804 | 0.064087 | 0.26093 | 121.138 | 121.3989 | 121.9803 | 122.0032 | 0.073242 | 122.0764 | 118.6661 | -0.23804 | 122.0032 | 0.073242 | 118.6661 | 121.9803 | 122.0764 | -122.2 | -122.2504
1588.4062 | 122.2 | -121.8933 | 0.09613 | 0.00206 | 0.0032128 | 0.010754 | 0.02656 | 0.042284 | -0.033199 | 0.060558 | -121.9299 | 0.11444 | -122.1909 | -121.8521 | -0.022888 | -3.3371 | -0.67749 | -0.60883 | 0.19684 | -122.1817 | -0.29755 | 0.018311 | -0.036621 | 0.041199 | -0.11902 | -0.28839 | 0.10071 | 0.26093 | 121.2158 | 121.2845 | 121.8704 | 122.0078 | -0.036621 | 122.0901 | 118.5562 | -0.28839 | 122.0078 | -0.036621 | 118.5562 | 121.8704 | 122.0901 | -122.287 | -122.2778
1590.1094 | 122.1725 | -121.9345 | 0.091553 | 0.00206 | -0.00063242 | 0.01289 | 0.024423 | 0.041003 | -0.031063 | 0.060558 | -121.8292 | 0.064087 | -122.1222 | -121.7606 | 0.091553 | -3.2684 | -0.8606 | -0.53101 | 0.14648 | -122.1954 | -0.18768 | -0.027466 | 0.10529 | 0.17395 | 0 | -0.26093 | 0.054931 | 0.29297 | 121.0739 | 121.4035 | 122.0261 | 121.9986 | 0.10529 | 122.081 | 118.6661 | -0.26093 | 121.9986 | 0.10529 | 118.6661 | 122.0261 | 122.081 | -122.2137 | -122.287
1591.8906 | 122.1497 | -121.9391 | 0.086975 | 0.017319 | -0.0017004 | 0.0088311 | 0.021219 | 0.038439 | -0.034054 | 0.058849 | -121.8475 | 0.068665 | -122.1451 | -121.7468 | 0.10986 | -3.2318 | -0.77362 | -0.43945 | 0.15564 | -122.1817 | -0.20599 | -0.01831 | 0.091553 | 0.19226 | 0.022888 | -0.24262 | 0.068665 | 0.29755 | 121.1655 | 121.4996 | 122.049 | 122.0078 | 0.091553 | 122.0947 | 118.7073 | -0.24262 | 122.0078 | 0.091553 | 118.7073 | 122.049 | 122.0947 | -122.2321 | -122.2687
1593.6875 | 122.081 | -121.9711 | 0.12817 | 0.0096895 | 0.00064938 | 0.010754 | 0.021433 | 0.038653 | -0.03149 | 0.059703 | -121.8201 | 0.068665 | -122.1405 | -121.7514 | 0.09613 | -3.2455 | -0.75989 | -0.45319 | 0.14648 | -122.1909 | -0.16937 | -0.059509 | 0.15106 | 0.21973 | -0.032044 | -0.21973 | 0.01831 | 0.32043 | 121.2112 | 121.5179 | 122.0673 | 122.0398 | 0.15106 | 122.1176 | 118.7256 | -0.21973 | 122.0398 | 0.15106 | 118.7256 | 122.0673 | 122.1176 | -122.2687 | -122.319
1595.4062 | 122.2229 | -121.9116 | 0.068665 | 0.00206 | 0.00022218 | 0.013744 | 0.029337 | 0.040362 | -0.034694 | 0.060131 | -121.962 | 0.10071 | -122.2137 | -121.8796 | -0.050354 | -3.4561 | -0.71869 | -0.73242 | 0.17853 | -122.2275 | -0.30212 | 0.032043 | -0.050354 | 0.032043 | -0.11902 | -0.31586 | 0.10986 | 0.25177 | 121.1929 | 121.1792 | 121.8613 | 122.0123 | -0.050354 | 122.0901 | 118.4555 | -0.31586 | 122.0123 | -0.050354 | 118.4555 | 121.8613 | 122.0901 | -122.2824 | -122.2961
1597.125 | 122.0947 | -122.0032 | 0.12817 | -0.0055695 | -0.00063242 | 0.0094721 | 0.022928 | 0.036944 | -0.032345 | 0.059917 | -121.8658 | 0.064087 | -122.1588 | -121.7651 | 0.10071 | -3.3508 | -0.80566 | -0.57678 | 0.16937 | -122.2229 | -0.15564 | -0.064087 | 0.13733 | 0.23804 | -0.027466 | -0.21973 | 0.041199 | 0.29297 | 121.1975 | 121.4264 | 122.1039 | 122.0673 | 0.13733 | 122.1725 | 118.6523 | -0.21973 | 122.0673 | 0.13733 | 118.6523 | 122.1039 | 122.1725 | -122.287 | -122.3511
1598.9219 | 122.1176 | -121.994 | 0.11444 | 0.0096895 | 0.0012902 | 0.010113 | 0.023142 | 0.03908 | -0.033413 | 0.05949 | -121.8613 | 0.082397 | -122.1497 | -121.7468 | 0.10529 | -3.3508 | -0.86517 | -0.58594 | 0.14648 | -122.2229 | -0.15564 | -0.032044 | 0.13275 | 0.24719 | -0.009155 | -0.22888 | 0.032043 | 0.28839 | 121.1288 | 121.4081 | 122.0993 | 122.0764 | 0.13275 | 122.1405 | 118.6432 | -0.22888 | 122.0764 | 0.13275 | 118.6432 | 122.0993 | 122.1405 | -122.2641 | -122.3373
1600.7031 | 122.2275 | -121.9574 | 0.091553 | 0.0096895 | 0.00086298 | 0.011608 | 0.023996 | 0.038866 | -0.03149 | 0.060985 | -121.875 | 0.082397 | -122.1725 | -121.7926 | 0.054932 | -3.4607 | -0.94299 | -0.75989 | 0.16022 | -122.2321 | -0.21515 | -0.009156 | 0.082397 | 0.16479 | -0.036621 | -0.27466 | 0.068664 | 0.29755 | 121.0144 | 121.1975 | 122.0123 | 122.0398 | 0.082397 | 122.1176 | 118.4967 | -0.27466 | 122.0398 | 0.082397 | 118.4967 | 122.0123 | 122.1176 | -122.2641 | -122.3236
1602.4375 | 122.2366 | -121.9574 | 0.082397 | 0.0096895 | 0.001504 | 0.012249 | 0.027628 | 0.041003 | -0.032772 | 0.058208 | -121.9574 | 0.09613 | -122.2092 | -121.8842 | -0.036621 | -3.5522 | -0.84228 | -0.84686 | 0.19684 | -122.2321 | -0.25177 | 0.013733 | 0 | 0.073242 | -0.11902 | -0.27466 | 0.11444 | 0.25177 | 121.1151 | 121.1105 | 121.9208 | 122.0535 | 0 | 122.1542 | 118.4052 | -0.27466 | 122.0535 | 0 | 118.4052 | 121.9208 | 122.1542 | -122.2916 | -122.3145
1604.2188 | 122.1725 | -121.9849 | 0.11444 | 0.0096895 | 0.0010766 | 0.010754 | 0.023569 | 0.037157 | -0.032772 | 0.061199 | -121.9208 | 0.10529 | -122.2046 | -121.8613 | 0.022888 | -3.5294 | -0.71869 | -0.74158 | 0.19684 | -122.2687 | -0.21973 | -0.009155 | 0.064087 | 0.1236 | -0.091553 | -0.28381 | 0.082397 | 0.28381 | 121.2662 | 121.2433 | 122.0078 | 122.0901 | 0.064087 | 122.1817 | 118.4555 | -0.28381 | 122.0901 | 0.064087 | 118.4555 | 122.0078 | 122.1817 | -122.319 | -122.3831
1606.0156 | 122.2504 | -121.9482 | 0.091553 | 0.00206 | -0.0010596 | 0.011822 | 0.020578 | 0.037798 | -0.033413 | 0.059276 | -121.9345 | 0.068665 | -122.2 | -121.8292 | 0.054932 | -3.566 | -0.95215 | -0.82855 | 0.16937 | -122.2641 | -0.25177 | -0.022888 | 0.013733 | 0.11902 | -0.036621 | -0.31586 | 0.07782 | 0.2655 | 120.9961 | 121.1197 | 122.0032 | 122.0169 | 0.013733 | 122.1176 | 118.3823 | -0.31586 | 122.0169 | 0.013733 | 118.3823 | 122.0032 | 122.1176 | -122.2916 | -122.3557
1607.7812 | 122.2687 | -121.9437 | 0.064087 | 0.017319 | 0.00043578 | 0.010326 | 0.022501 | 0.038226 | -0.03149 | 0.059062 | -121.9254 | 0.086975 | -122.1817 | -121.8521 | 0.041199 | -3.6118 | -0.99335 | -0.91095 | 0.16479 | -122.2595 | -0.23804 | 0.022888 | 0.018311 | 0.091553 | -0.022888 | -0.31586 | 0.10071 | 0.25635 | 120.9503 | 121.0327 | 121.9849 | 122.0306 | 0.018311 | 122.1085 | 118.3319 | -0.31586 | 122.0306 | 0.018311 | 118.3319 | 121.9849 | 122.1085 | -122.2458 | -122.3236
1609.5 | 122.2549 | -121.9528 | 0.082397 | 0.0096895 | -0.001914 | 0.0096857 | 0.030832 | 0.039935 | -0.034481 | 0.061626 | -121.9711 | 0.10529 | -122.2549 | -121.8887 | -0.032043 | -3.685 | -0.95673 | -1.0071 | 0.17395 | -122.2458 | -0.30212 | 0.022889 | -0.01831 | 0.064087 | -0.11444 | -0.29297 | 0.091553 | 0.28381 | 120.9961 | 120.9457 | 121.9208 | 122.0581 | -0.01831 | 122.1268 | 118.2678 | -0.29297 | 122.0581 | -0.01831 | 118.2678 | 121.9208 | 122.1268 | -122.3373 | -122.3282
1611.2812 | 122.168 | -122.0078 | 0.10071 | -0.013199 | 0.0021448 | 0.0077631 | 0.025278 | 0.038653 | -0.031704 | 0.058849 | -121.9803 | 0.11902 | -122.2412 | -121.9025 | -0.013733 | -3.6942 | -0.78735 | -0.94299 | 0.20599 | -122.2961 | -0.23346 | 0.018311 | 0.027465 | 0.10528 | -0.11444 | -0.28839 | 0.10529 | 0.26093 | 121.2204 | 121.0648 | 121.994 | 122.1268 | 0.027465 | 122.2137 | 118.3136 | -0.28839 | 122.1268 | 0.027465 | 118.3136 | 121.994 | 122.2137 | -122.3419 | -122.3969
1613.0781 | 122.2321 | -121.9711 | 0.09613 | 0.00206 | 0.00086298 | 0.0096857 | 0.025705 | 0.042071 | -0.032558 | 0.060558 | -121.8704 | 0.068665 | -122.1817 | -121.788 | 0.073242 | -3.653 | -1.1948 | -0.97961 | 0.15106 | -122.2595 | -0.21057 | -0.027465 | 0.10071 | 0.1831 | -0.022888 | -0.28839 | 0.054932 | 0.31128 | 120.7764 | 120.9915 | 122.0444 | 122.0398 | 0.10071 | 122.1222 | 118.3182 | -0.28839 | 122.0398 | 0.10071 | 118.3182 | 122.0444 | 122.1222 | -122.2778 | -122.3557
1614.7969 | 122.1451 | -122.0123 | 0.1236 | 0.00206 | -0.00084602 | 0.0073359 | 0.020578 | 0.037371 | -0.033199 | 0.059062 | -121.9025 | 0.068665 | -122.2 | -121.8155 | 0.091553 | -3.6713 | -0.99792 | -0.90179 | 0.16479 | -122.2595 | -0.18768 | -0.054931 | 0.10986 | 0.19684 | -0.032043 | -0.24719 | 0.041199 | 0.29755 | 121.0144 | 121.1105 | 122.1039 | 122.081 | 0.10986 | 122.1771 | 118.3411 | -0.24719 | 122.081 | 0.10986 | 118.3411 | 122.1039 | 122.1771 | -122.3236 | -122.3831
1616.5938 | 122.1497 | -122.0261 | 0.10986 | 0.0096895 | 0.0019312 | 0.011608 | 0.031046 | 0.041644 | -0.03619 | 0.060344 | -121.9254 | 0.09613 | -122.2687 | -121.8521 | 0.018311 | -3.7674 | -0.99335 | -1.0437 | 0.20142 | -122.2504 | -0.24262 | -0.013733 | 0.10071 | 0.17395 | -0.091552 | -0.2243 | 0.091553 | 0.34332 | 121.0327 | 120.9824 | 122.0444 | 122.1222 | 0.10071 | 122.2275 | 118.2587 | -0.2243 | 122.1222 | 0.10071 | 118.2587 | 122.0444 | 122.2275 | -122.3785 | -122.3602
1618.375 | 122.1497 | -122.0306 | 0.10986 | 0.0096895 | -0.00020502 | 0.012035 | 0.02186 | 0.038439 | -0.029995 | 0.059703 | -121.9116 | 0.054932 | -122.2092 | -121.8155 | 0.073242 | -3.7491 | -1.0666 | -1.0162 | 0.14648 | -122.2778 | -0.17853 | -0.054931 | 0.11902 | 0.21515 | -0.036621 | -0.24719 | 0.036621 | 0.29755 | 120.9641 | 121.0144 | 122.1039 | 122.0856 | 0.11902 | 122.1771 | 118.2816 | -0.24719 | 122.0856 | 0.11902 | 118.2816 | 122.1039 | 122.1771 | -122.319 | -122.3877
1620.1562 | 122.1405 | -122.0078 | 0.10986 | 0.0096895 | -0.00084602 | 0.010967 | 0.027841 | 0.042071 | -0.035335 | 0.05949 | -121.9528 | 0.07782 | -122.2641 | -121.8567 | 0.018311 | -3.8269 | -1.0391 | -1.1398 | 0.18768 | -122.2687 | -0.25635 | -0.032043 | 0.054931 | 0.15106 | -0.091552 | -0.26093 | 0.07782 | 0.31128 | 120.9686 | 120.8679 | 122.0261 | 122.0856 | 0.054931 | 122.1954 | 118.1808 | -0.26093 | 122.0856 | 0.054931 | 118.1808 | 122.0261 | 122.1954 | -122.374 | -122.3785
1621.9375 | 122.1725 | -122.0535 | 0.11444 | 0.0096895 | -0.00020502 | 0.011822 | 0.022287 | 0.03673 | -0.034908 | 0.060344 | -121.9437 | 0.086975 | -122.2 | -121.8658 | 0.064087 | -3.8635 | -1.0941 | -1.1673 | 0.1831 | -122.2824 | -0.14648 | -0.027466 | 0.10986 | 0.18768 | -0.050354 | -0.22888 | 0.068664 | 0.25635 | 120.9595 | 120.8862 | 122.1176 | 122.1405 | 0.10986 | 122.2366 | 118.19 | -0.22888 | 122.1405 | 0.10986 | 118.19 | 122.1176 | 122.2366 | -122.3145 | -122.3969
1623.7188 | 122.2641 | -121.9894 | 0.082397 | 0.00206 | 0.00086298 | 0.013317 | 0.023783 | 0.039721 | -0.03149 | 0.060771 | -121.9254 | 0.054932 | -122.2137 | -121.8567 | 0.064087 | -3.9093 | -1.3687 | -1.3275 | 0.15106 | -122.2916 | -0.2243 | -0.027465 | 0.064087 | 0.13275 | -0.01831 | -0.30212 | 0.068665 | 0.28839 | 120.6207 | 120.6619 | 122.0535 | 122.0444 | 0.064087 | 122.1405 | 118.0801 | -0.30212 | 122.0444 | 0.064087 | 118.0801 | 122.0535 | 122.1405 | -122.2961 | -122.374
1625.4375 | 122.1771 | -122.0352 | 0.10071 | 0.00206 | 0.001504 | 0.01289 | 0.029337 | 0.041216 | -0.033626 | 0.06248 | -121.9528 | 0.10071 | -122.2687 | -121.8796 | 0 | -4.0009 | -1.1719 | -1.3641 | 0.19226 | -122.2595 | -0.23346 | 0 | 0.082397 | 0.15564 | -0.10071 | -0.2243 | 0.091553 | 0.31586 | 120.8633 | 120.6711 | 122.0352 | 122.1359 | 0.082397 | 122.2275 | 118.0344 | -0.2243 | 122.1359 | 0.082397 | 118.0344 | 122.0352 | 122.2275 | -122.3694 | -122.3602
1627.2344 | 122.2412 | -122.0398 | 0.09613 | 0.0096895 | -0.00084602 | 0.011822 | 0.019296 | 0.038226 | -0.032985 | 0.059276 | -121.9254 | 0.073242 | -122.2092 | -121.8338 | 0.10529 | -3.9597 | -1.355 | -1.3458 | 0.15564 | -122.2824 | -0.16937 | -0.022888 | 0.11444 | 0.20599 | 0.009156 | -0.24262 | 0.05951 | 0.28381 | 120.6848 | 120.694 | 122.1451 | 122.113 | 0.11444 | 122.1954 | 118.0801 | -0.24262 | 122.113 | 0.11444 | 118.0801 | 122.1451 | 122.1954 | -122.3053 | -122.3785
1629.0312 | 122.3007 | -121.9803 | 0.068665 | -0.0055695 | 0.0012902 | 0.011395 | 0.022074 | 0.039507 | -0.033199 | 0.059703 | -121.9528 | 0.07782 | -122.2275 | -121.875 | 0.036621 | -4.0924 | -1.442 | -1.5701 | 0.17395 | -122.2916 | -0.24719 | 0.009155 | 0.027466 | 0.10529 | -0.032044 | -0.31128 | 0.10528 | 0.27466 | 120.5383 | 120.4102 | 122.0169 | 122.0581 | 0.027466 | 122.1542 | 117.8879 | -0.31128 | 122.0581 | 0.027466 | 117.8879 | 122.0169 | 122.1542 | -122.2961 | -122.3602
1630.8125 | 122.3053 | -121.994 | 0.068665 | 0.00206 | -0.00020502 | 0.010754 | 0.025492 | 0.041003 | -0.032558 | 0.060771 | -121.9666 | 0.064087 | -122.2229 | -121.8887 | 0.041199 | -4.1245 | -1.474 | -1.6342 | 0.14191 | -122.2961 | -0.22888 | -0.004578 | 0.027466 | 0.10529 | -0.027466 | -0.30212 | 0.073242 | 0.25635 | 120.52 | 120.3598 | 122.0352 | 122.0581 | 0.027466 | 122.1359 | 117.8696 | -0.30212 | 122.0581 | 0.027466 | 117.8696 | 122.0352 | 122.1359 | -122.2916 | -122.3648
1632.5469 | 122.2916 | -121.9849 | 0.091553 | 0.0096895 | -0.00084602 | 0.01289 | 0.023569 | 0.041003 | -0.032558 | 0.060985 | -121.9254 | 0.073242 | -122.2046 | -121.8613 | 0.054932 | -4.1519 | -1.5701 | -1.6891 | 0.15564 | -122.3053 | -0.21973 | -0.018311 | 0.059509 | 0.1236 | -0.036621 | -0.32043 | 0.064087 | 0.27924 | 120.4147 | 120.2957 | 122.0398 | 122.0581 | 0.059509 | 122.1405 | 117.8329 | -0.32043 | 122.0581 | 0.059509 | 117.8329 | 122.0398 | 122.1405 | -122.2961 | -122.3969
1634.3281 | 122.2641 | -122.0078 | 0.086975 | 0.00206 | -0.0012732 | 0.012035 | 0.028269 | 0.037798 | -0.032985 | 0.060985 | -121.9711 | 0.07782 | -122.2824 | -121.8658 | 0.064087 | -4.216 | -1.5793 | -1.7807 | 0.15564 | -122.2549 | -0.27466 | -0.009155 | 0.036621 | 0.14191 | -0.022888 | -0.24719 | 0.068665 | 0.31128 | 120.4285 | 120.2271 | 122.0718 | 122.0856 | 0.036621 | 122.1634 | 117.7917 | -0.24719 | 122.0856 | 0.036621 | 117.7917 | 122.0718 | 122.1634 | -122.3694 | -122.3419
1636.1094 | 122.1634 | -122.0444 | 0.11902 | 0.00206 | -0.00020502 | 0.011181 | 0.029978 | 0.039507 | -0.03619 | 0.058635 | -121.9711 | 0.086975 | -122.3099 | -121.8842 | 0.018311 | -4.248 | -1.4053 | -1.7761 | 0.18768 | -122.2824 | -0.2655 | -0.032044 | 0.073243 | 0.16022 | -0.10071 | -0.23804 | 0.068664 | 0.33875 | 120.639 | 120.2682 | 122.0627 | 122.1313 | 0.073243 | 122.2321 | 117.7963 | -0.23804 | 122.1313 | 0.073243 | 117.7963 | 122.0627 | 122.2321 | -122.4289 | -122.4014
1637.9062 | 122.2733 | -122.0215 | 0.082397 | 0.0096895 | 0.0051356 | 0.010754 | 0.027414 | 0.043566 | -0.037258 | 0.060344 | -122.0169 | 0.11444 | -122.3053 | -121.9757 | -0.045776 | -4.3945 | -1.4511 | -2.0096 | 0.19684 | -122.3099 | -0.28381 | 0.032044 | 0.004577 | 0.045776 | -0.12817 | -0.28839 | 0.11444 | 0.28839 | 120.5704 | 120.0119 | 121.9757 | 122.1359 | 0.004577 | 122.2183 | 117.627 | -0.28839 | 122.1359 | 0.004577 | 117.627 | 121.9757 | 122.2183 | -122.3877 | -122.3923
1639.7031 | 122.3145 | -122.0215 | 0.086975 | -0.0055695 | -0.0012732 | 0.010113 | 0.020151 | 0.038012 | -0.030849 | 0.060344 | -122.0078 | 0.082397 | -122.2366 | -121.9116 | 0.045776 | -4.3304 | -1.6388 | -1.9455 | 0.16022 | -122.3007 | -0.21515 | -0.004578 | 0.013733 | 0.10986 | -0.041199 | -0.27924 | 0.073242 | 0.22888 | 120.3827 | 120.076 | 122.0673 | 122.1039 | 0.013733 | 122.1817 | 117.691 | -0.27924 | 122.1039 | 0.013733 | 117.691 | 122.0673 | 122.1817 | -122.3236 | -122.3877
1641.4219 | 122.319 | -122.0398 | 0.082397 | 0.017319 | -0.0034094 | 0.0086175 | 0.020365 | 0.040148 | -0.034694 | 0.05949 | -122.0261 | 0.082397 | -122.2504 | -121.9208 | 0.041199 | -4.3259 | -1.6388 | -2.0096 | 0.17395 | -122.2824 | -0.21057 | 0 | 0.013733 | 0.11902 | -0.041198 | -0.24262 | 0.091553 | 0.2243 | 120.401 | 120.0302 | 122.081 | 122.1222 | 0.013733 | 122.2137 | 117.7139 | -0.24262 | 122.1222 | 0.013733 | 117.7139 | 122.081 | 122.2137 | -122.3328 | -122.3648
1643.2031 | 122.2733 | -122.0764 | 0.091553 | 0.00206 | 0.001504 | 0.0090447 | 0.023355 | 0.039721 | -0.03149 | 0.061626 | -121.9574 | 0.068665 | -122.2366 | -121.8567 | 0.082397 | -4.303 | -1.6846 | -1.9638 | 0.17395 | -122.3007 | -0.16022 | -0.022888 | 0.11902 | 0.21973 | -0.009156 | -0.2243 | 0.082397 | 0.27924 | 120.3918 | 120.1126 | 122.1588 | 122.1451 | 0.11902 | 122.2504 | 117.7734 | -0.2243 | 122.1451 | 0.11902 | 117.7734 | 122.1588 | 122.2504 | -122.3282 | -122.3923
1645 | 122.2092 | -122.0535 | 0.10529 | 0.00206 | -0.00041862 | 0.012035 | 0.023355 | 0.038653 | -0.032131 | 0.061626 | -121.9482 | 0.059509 | -122.2458 | -121.843 | 0.10986 | -4.3488 | -1.7441 | -2.0233 | 0.15106 | -122.3007 | -0.19226 | -0.045777 | 0.10529 | 0.21057 | 0.004577 | -0.24719 | 0.045776 | 0.29755 | 120.3094 | 120.0302 | 122.1634 | 122.113 | 0.10529 | 122.2046 | 117.7048 | -0.24719 | 122.113 | 0.10529 | 117.7048 | 122.1634 | 122.2046 | -122.3511 | -122.406
1646.7969 | 122.2778 | -122.0444 | 0.073242 | 0.00206 | 0.00043578 | 0.013104 | 0.026773 | 0.040362 | -0.034054 | 0.059276 | -121.962 | 0.073242 | -122.287 | -121.8704 | 0.059509 | -4.4678 | -1.8768 | -2.2339 | 0.15106 | -122.3099 | -0.24261 | 0 | 0.082398 | 0.17395 | -0.013733 | -0.2655 | 0.07782 | 0.32501 | 120.1675 | 119.8105 | 122.1039 | 122.1176 | 0.082398 | 122.1954 | 117.5766 | -0.2655 | 122.1176 | 0.082398 | 117.5766 | 122.1039 | 122.1954 | -122.3602 | -122.3831
1648.5156 | 122.2549 | -122.049 | 0.10071 | 0.00206 | 0.0027856 | 0.011181 | 0.024851 | 0.038439 | -0.032345 | 0.062053 | -122.0535 | 0.10071 | -122.2961 | -121.9574 | -0.027466 | -4.5959 | -1.6022 | -2.298 | 0.19226 | -122.3557 | -0.24719 | 0 | -0.004578 | 0.091553 | -0.12817 | -0.3067 | 0.091553 | 0.24262 | 120.4468 | 119.751 | 122.0215 | 122.1497 | -0.004578 | 122.2412 | 117.453 | -0.3067 | 122.1497 | -0.004578 | 117.453 | 122.0215 | 122.2412 | -122.3969 | -122.4564
1650.2812 | 122.3511 | -122.0581 | 0.068665 | 0.0096895 | 0.0023584 | 0.0092585 | 0.022501 | 0.039507 | -0.032131 | 0.05949 | -122.0032 | 0.068665 | -122.2595 | -121.9345 | 0.032043 | -4.6371 | -1.918 | -2.4124 | 0.15106 | -122.3236 | -0.20142 | 0 | 0.054931 | 0.1236 | -0.036622 | -0.2655 | 0.082397 | 0.25635 | 120.1401 | 119.6457 | 122.0901 | 122.1268 | 0.054931 | 122.2092 | 117.421 | -0.2655 | 122.1268 | 0.054931 | 117.421 | 122.0901 | 122.2092 | -122.3282 | -122.3923
1652.0781 | 122.2046 | -122.0673 | 0.10071 | -0.0055695 | -0.00084602 | 0.0086175 | 0.029764 | 0.039507 | -0.035122 | 0.062053 | -122.0261 | 0.10071 | -122.3419 | -121.9254 | 0.013733 | -4.6692 | -1.7578 | -2.4399 | 0.19226 | -122.3419 | -0.27466 | 0 | 0.041199 | 0.14191 | -0.086975 | -0.27466 | 0.091553 | 0.31586 | 120.3094 | 119.6274 | 122.081 | 122.168 | 0.041199 | 122.2595 | 117.3981 | -0.27466 | 122.168 | 0.041199 | 117.3981 | 122.081 | 122.2595 | -122.4426 | -122.4426
1653.7969 | 122.3465 | -122.0535 | 0.086975 | 0.00206 | 0.00086298 | 0.0062677 | 0.021219 | 0.038226 | -0.028286 | 0.058208 | -122.0123 | 0.068665 | -122.2549 | -121.9391 | 0.018311 | -4.7424 | -2.0004 | -2.5909 | 0.16479 | -122.3465 | -0.20142 | -0.01831 | 0.041199 | 0.11444 | -0.068664 | -0.29297 | 0.07782 | 0.24262 | 120.0531 | 119.4626 | 122.0718 | 122.1222 | 0.041199 | 122.2183 | 117.3111 | -0.29297 | 122.1222 | 0.041199 | 117.3111 | 122.0718 | 122.2183 | -122.3419 | -122.4335
1655.5781 | 122.2687 | -122.0581 | 0.082397 | 0.00206 | 0.0034266 | 0.010113 | 0.029337 | 0.041003 | -0.035763 | 0.060558 | -122.0535 | 0.10529 | -122.3328 | -121.9986 | -0.054932 | -4.866 | -1.8997 | -2.7374 | 0.20599 | -122.3373 | -0.27466 | 0.022889 | 0.004577 | 0.059509 | -0.13733 | -0.27924 | 0.1236 | 0.27924 | 120.1584 | 119.3207 | 122.0032 | 122.1634 | 0.004577 | 122.2641 | 117.1921 | -0.27924 | 122.1634 | 0.004577 | 117.1921 | 122.0032 | 122.2641 | -122.4152 | -122.4197
1657.3594 | 122.2961 | -122.0444 | 0.082397 | 0.0096895 | -0.00020502 | 0.010326 | 0.021433 | 0.03908 | -0.033413 | 0.060131 | -121.9666 | 0.036621 | -122.2916 | -121.8887 | 0.073242 | -4.8386 | -2.1973 | -2.7374 | 0.13733 | -122.3373 | -0.24719 | -0.045776 | 0.07782 | 0.15564 | -0.009155 | -0.29297 | 0.054932 | 0.32501 | 119.8471 | 119.3069 | 122.1176 | 122.081 | 0.07782 | 122.1817 | 117.2058 | -0.29297 | 122.081 | 0.07782 | 117.2058 | 122.1176 | 122.1817 | -122.374 | -122.4197
1659.0781 | 122.3648 | -122.0352 | 0.10529 | 0.00206 | 0.0017176 | 0.0088311 | 0.021646 | 0.037798 | -0.031917 | 0.060344 | -122.0215 | 0.086975 | -122.2687 | -121.9437 | 0.032043 | -4.9667 | -2.1652 | -2.8793 | 0.16022 | -122.3373 | -0.23346 | -0.018311 | 0.013733 | 0.091552 | -0.073243 | -0.30212 | 0.054931 | 0.24719 | 119.87 | 119.1559 | 122.0673 | 122.1222 | 0.013733 | 122.1954 | 117.0685 | -0.30212 | 122.1222 | 0.013733 | 117.0685 | 122.0673 | 122.1954 | -122.374 | -122.4426
1660.8594 | 122.2229 | -122.1039 | 0.11902 | -0.0055695 | -0.0010596 | 0.012249 | 0.02186 | 0.039507 | -0.031917 | 0.060558 | -121.962 | 0.059509 | -122.287 | -121.8567 | 0.11444 | -4.9393 | -2.211 | -2.861 | 0.13733 | -122.3419 | -0.1831 | -0.05951 | 0.14191 | 0.24719 | -0.004578 | -0.23804 | 0.01831 | 0.32501 | 119.8929 | 119.2429 | 122.2183 | 122.1634 | 0.14191 | 122.2412 | 117.1646 | -0.23804 | 122.1634 | 0.14191 | 117.1646 | 122.2183 | 122.2412 | -122.406 | -122.4609
1662.6562 | 122.3877 | -122.0947 | 0.086975 | 0.00206 | 0.00064938 | 0.012676 | 0.022714 | 0.038653 | -0.031063 | 0.058422 | -122.0032 | 0.054932 | -122.2733 | -121.9528 | 0.022888 | -5.1224 | -2.3071 | -3.0991 | 0.15564 | -122.3648 | -0.17853 | -0.032043 | 0.091553 | 0.14191 | -0.064087 | -0.27008 | 0.068665 | 0.27008 | 119.7876 | 118.9957 | 122.1176 | 122.1497 | 0.091553 | 122.2504 | 116.9724 | -0.27008 | 122.1497 | 0.091553 | 116.9724 | 122.1176 | 122.2504 | -122.3602 | -122.4518
1664.375 | 122.2961 | -122.0627 | 0.10071 | 0.017319 | 0.002572 | 0.014599 | 0.031046 | 0.039721 | -0.034694 | 0.060344 | -122.0581 | 0.10986 | -122.3648 | -122.0032 | -0.054932 | -5.2643 | -2.2064 | -3.2593 | 0.20599 | -122.3831 | -0.30212 | 0.009155 | 0.004578 | 0.059509 | -0.15564 | -0.32043 | 0.10529 | 0.3067 | 119.8563 | 118.8034 | 122.0078 | 122.1725 | 0.004578 | 122.2687 | 116.7984 | -0.32043 | 122.1725 | 0.004578 | 116.7984 | 122.0078 | 122.2687 | -122.4655 | -122.4838
1666.1406 | 122.3465 | -122.081 | 0.082397 | 0.00206 | 0.0034266 | 0.011181 | 0.022074 | 0.041216 | -0.033413 | 0.058849 | -122.0078 | 0.068665 | -122.3099 | -121.9345 | 0.07782 | -5.2505 | -2.4307 | -3.2639 | 0.16022 | -122.3602 | -0.22888 | -0.013732 | 0.073243 | 0.14648 | -0.004577 | -0.27923 | 0.07782 | 0.30212 | 119.6503 | 118.8171 | 122.1588 | 122.1497 | 0.073243 | 122.2412 | 116.8304 | -0.27923 | 122.1497 | 0.073243 | 116.8304 | 122.1588 | 122.2412 | -122.3923 | -122.4426
1667.8594 | 122.2549 | -122.0947 | 0.09613 | 0.017319 | 0.0012902 | 0.015453 | 0.030405 | 0.042712 | -0.035763 | 0.061199 | -122.0718 | 0.086975 | -122.3419 | -121.9849 | -0.027466 | -5.4428 | -2.3712 | -3.4973 | 0.18768 | -122.3557 | -0.24719 | -0.009155 | 0.022889 | 0.10986 | -0.1236 | -0.26093 | 0.091553 | 0.27008 | 119.7235 | 118.5974 | 122.0673 | 122.1817 | 0.022889 | 122.2824 | 116.6519 | -0.26093 | 122.1817 | 0.022889 | 116.6519 | 122.0673 | 122.2824 | -122.438 | -122.4518
1669.6406 | 122.3648 | -122.0627 | 0.091553 | -0.0055695 | -0.0021276 | 0.0060541 | 0.022928 | 0.038012 | -0.031917 | 0.060771 | -122.0306 | 0.064087 | -122.3053 | -121.9254 | 0.068665 | -5.4108 | -2.5589 | -3.5019 | 0.15106 | -122.3648 | -0.24261 | -0.027466 | 0.032043 | 0.13733 | -0.022888 | -0.30212 | 0.059509 | 0.27466 | 119.5038 | 118.5608 | 122.1313 | 122.1268 | 0.032043 | 122.2137 | 116.6519 | -0.30212 | 122.1268 | 0.032043 | 116.6519 | 122.1313 | 122.2137 | -122.3969 | -122.4564
1671.3594 | 122.3282 | -122.0673 | 0.07782 | 0.0096895 | -0.0027686 | 0.0088311 | 0.023996 | 0.040789 | -0.034054 | 0.06184 | -121.9894 | 0.018311 | -122.3145 | -121.8979 | 0.07782 | -5.4932 | -2.7557 | -3.653 | 0.15564 | -122.319 | -0.24719 | -0.059509 | 0.07782 | 0.16937 | 0 | -0.25177 | 0.07782 | 0.32501 | 119.3115 | 118.4143 | 122.1451 | 122.0856 | 0.07782 | 122.2229 | 116.5741 | -0.25177 | 122.0856 | 0.07782 | 116.5741 | 122.1451 | 122.2229 | -122.3923 | -122.3969
1673.1406 | 122.2458 | -122.1039 | 0.11902 | 0.0096895 | -0.0010596 | 0.0098993 | 0.023355 | 0.038439 | -0.03384 | 0.058635 | -121.994 | 0.068665 | -122.3007 | -121.9162 | 0.07782 | -5.4886 | -2.6459 | -3.6118 | 0.15564 | -122.3465 | -0.19684 | -0.050354 | 0.10986 | 0.18768 | -0.041199 | -0.24262 | 0.036621 | 0.3067 | 119.458 | 118.4921 | 122.1817 | 122.1725 | 0.10986 | 122.2595 | 116.6153 | -0.24262 | 122.1725 | 0.10986 | 116.6153 | 122.1817 | 122.2595 | -122.4197 | -122.4655
1674.8594 | 122.3923 | -122.0764 | 0.064087 | 0.0096895 | 0.0017176 | 0.0094721 | 0.022928 | 0.039294 | -0.034908 | 0.059703 | -122.0398 | 0.059509 | -122.2824 | -121.9391 | 0.032043 | -5.6671 | -2.7924 | -3.8956 | 0.16479 | -122.374 | -0.20599 | -0.004578 | 0.036621 | 0.13733 | -0.032044 | -0.29755 | 0.10071 | 0.24262 | 119.2841 | 118.1808 | 122.1085 | 122.1359 | 0.036621 | 122.2412 | 116.4093 | -0.29755 | 122.1359 | 0.036621 | 116.4093 | 122.1085 | 122.2412 | -122.3465 | -122.438
1676.6406 | 122.3328 | -122.0947 | 0.086975 | -0.013199 | 0.00086298 | 0.014385 | 0.028055 | 0.041003 | -0.036403 | 0.061199 | -122.0947 | 0.082397 | -122.3831 | -122.0261 | -0.064087 | -5.8411 | -2.6733 | -4.0741 | 0.16022 | -122.3877 | -0.28839 | -0.004578 | 0 | 0.068665 | -0.15106 | -0.29297 | 0.073242 | 0.28839 | 119.4214 | 118.0206 | 122.0306 | 122.1771 | 0 | 122.2549 | 116.2537 | -0.29297 | 122.1771 | 0 | 116.2537 | 122.0306 | 122.2549 | -122.4701 | -122.4747
1678.4375 | 122.3923 | -122.0764 | 0.082397 | 0.0096895 | 0.00086298 | 0.010754 | 0.022287 | 0.039935 | -0.034267 | 0.060985 | -122.0535 | 0.073242 | -122.3053 | -121.9711 | 0.027466 | -5.8456 | -2.8702 | -4.097 | 0.16022 | -122.3877 | -0.22888 | -0.009155 | 0.022888 | 0.10529 | -0.054931 | -0.31128 | 0.07782 | 0.25177 | 119.2062 | 117.9794 | 122.1039 | 122.1497 | 0.022888 | 122.2366 | 116.2308 | -0.31128 | 122.1497 | 0.022888 | 116.2308 | 122.1039 | 122.2366 | -122.3877 | -122.4701
1680.2188 | 122.3328 | -122.113 | 0.091553 | 0.00206 | 0.002572 | 0.011608 | 0.024637 | 0.039935 | -0.032772 | 0.059917 | -121.9803 | 0.036621 | -122.3328 | -121.9116 | 0.068665 | -5.9052 | -3.0808 | -4.1977 | 0.15106 | -122.3557 | -0.21973 | -0.054932 | 0.13275 | 0.20142 | -0.022888 | -0.24262 | 0.059509 | 0.35248 | 119.0323 | 117.9153 | 122.1817 | 122.1497 | 0.13275 | 122.2641 | 116.2079 | -0.24262 | 122.1497 | 0.13275 | 116.2079 | 122.1817 | 122.2641 | -122.4243 | -122.4472
1682.0156 | 122.2412 | -122.1313 | 0.10986 | 0.0096895 | 0.0027856 | 0.011181 | 0.028055 | 0.040789 | -0.032131 | 0.058635 | -122.0261 | 0.10529 | -122.3602 | -121.9482 | 0.009155 | -5.983 | -2.8793 | -4.2755 | 0.17395 | -122.4243 | -0.22888 | -0.004577 | 0.10529 | 0.18311 | -0.10071 | -0.29297 | 0.064087 | 0.33417 | 119.252 | 117.8558 | 122.1405 | 122.2366 | 0.10529 | 122.3053 | 116.1484 | -0.29297 | 122.2366 | 0.10529 | 116.1484 | 122.1405 | 122.3053 | -122.4701 | -122.5342
1683.7344 | 122.3923 | -122.0764 | 0.073242 | 0.0096895 | 8.578e-06 | 0.0098993 | 0.02186 | 0.038012 | -0.029568 | 0.059703 | -122.0627 | 0.068665 | -122.319 | -121.9757 | 0.018311 | -6.0516 | -3.0716 | -4.4128 | 0.15106 | -122.4106 | -0.24262 | -0.004577 | 0.013733 | 0.10071 | -0.054931 | -0.33417 | 0.07782 | 0.25635 | 119.0048 | 117.6636 | 122.0947 | 122.1451 | 0.013733 | 122.2275 | 116.0248 | -0.33417 | 122.1451 | 0.013733 | 116.0248 | 122.0947 | 122.2275 | -122.3923 | -122.4838
1685.5 | 122.3007 | -122.1039 | 0.10071 | 0.00206 | 0.0027856 | 0.0079767 | 0.027414 | 0.03908 | -0.032131 | 0.059917 | -122.1222 | 0.11902 | -122.3831 | -122.0352 | -0.041199 | -6.1707 | -2.9205 | -4.509 | 0.1831 | -122.406 | -0.27924 | 0.018311 | -0.01831 | 0.068665 | -0.14191 | -0.30212 | 0.082397 | 0.26093 | 119.1834 | 117.5949 | 122.0627 | 122.2229 | -0.01831 | 122.287 | 115.9332 | -0.30212 | 122.2229 | -0.01831 | 115.9332 | 122.0627 | 122.287 | -122.4838 | -122.5067
1687.2812 | 122.3465 | -122.1176 | 0.082397 | 0.017319 | 0.00086298 | 0.011608 | 0.025705 | 0.039721 | -0.032985 | 0.060985 | -122.0581 | 0.073242 | -122.3648 | -121.962 | 0.027466 | -6.2668 | -3.3234 | -4.6921 | 0.15106 | -122.3557 | -0.24719 | -0.009155 | 0.05951 | 0.15564 | -0.054931 | -0.23804 | 0.068665 | 0.3067 | 118.7943 | 117.4255 | 122.1451 | 122.1909 | 0.05951 | 122.2687 | 115.8508 | -0.23804 | 122.1909 | 0.05951 | 115.8508 | 122.1451 | 122.2687 | -122.4472 | -122.438
1689.0625 | 122.2641 | -122.1451 | 0.10986 | 0.00206 | -0.00020502 | 0.012035 | 0.02186 | 0.039294 | -0.033199 | 0.059703 | -122.0123 | 0.064087 | -122.3328 | -121.9162 | 0.07782 | -6.2851 | -3.3005 | -4.6509 | 0.14191 | -122.3923 | -0.18768 | -0.045776 | 0.13275 | 0.22888 | -0.032043 | -0.24719 | 0.032044 | 0.32044 | 118.8446 | 117.4942 | 122.2229 | 122.2092 | 0.13275 | 122.287 | 115.86 | -0.24719 | 122.2092 | 0.13275 | 115.86 | 122.2229 | 122.287 | -122.4426 | -122.5021
1690.8438 | 122.3328 | -122.1085 | 0.10071 | 0.0096895 | 0.00043578 | 0.010967 | 0.027414 | 0.040789 | -0.03384 | 0.062053 | -122.113 | 0.09613 | -122.4243 | -122.0398 | -0.054932 | -6.5323 | -3.2959 | -4.985 | 0.19226 | -122.4289 | -0.31586 | -0.004578 | -0.004578 | 0.068664 | -0.15564 | -0.32044 | 0.091553 | 0.31128 | 118.8126 | 117.1234 | 122.0535 | 122.2046 | -0.004578 | 122.3007 | 115.5762 | -0.32044 | 122.2046 | -0.004578 | 115.5762 | 122.0535 | 122.3007 | -122.525 | -122.5296
1692.5625 | 122.3465 | -122.1222 | 0.082397 | 0.00206 | 0.00043578 | 0.012676 | 0.024423 | 0.039721 | -0.032131 | 0.05949 | -122.0261 | 0.054932 | -122.3145 | -121.9437 | 0.050354 | -6.4819 | -3.6346 | -4.9942 | 0.12817 | -122.406 | -0.19226 | -0.027465 | 0.09613 | 0.17853 | -0.032043 | -0.28381 | 0.045777 | 0.28839 | 118.4875 | 117.128 | 122.1725 | 122.1771 | 0.09613 | 122.2504 | 115.6403 | -0.28381 | 122.1771 | 0.09613 | 115.6403 | 122.1725 | 122.2504 | -122.3969 | -122.4884
1694.3281 | 122.3648 | -122.1085 | 0.091553 | 0.00206 | 0.0010766 | 0.011608 | 0.025492 | 0.038653 | -0.03384 | 0.060771 | -122.0169 | 0.045776 | -122.3373 | -121.9574 | 0.059509 | -6.6101 | -3.7262 | -5.1453 | 0.14648 | -122.3923 | -0.22888 | -0.045777 | 0.091552 | 0.15106 | -0.032044 | -0.28381 | 0.054931 | 0.32043 | 118.3823 | 116.9632 | 122.168 | 122.1542 | 0.091552 | 122.2549 | 115.4984 | -0.28381 | 122.1542 | 0.091552 | 115.4984 | 122.168 | 122.2549 | -122.4289 | -122.4838
1696.1094 | 122.2549 | -122.168 | 0.11444 | 0.00206 | 0.0017176 | 0.012463 | 0.028482 | 0.038866 | -0.034694 | 0.060771 | -122.0673 | 0.086975 | -122.3877 | -122.0032 | -0.013733 | -6.7017 | -3.5706 | -5.2368 | 0.1831 | -122.4289 | -0.21973 | -0.027466 | 0.10071 | 0.16479 | -0.12817 | -0.26093 | 0.068664 | 0.32043 | 118.5974 | 116.9312 | 122.1542 | 122.2549 | 0.10071 | 122.3511 | 115.4663 | -0.26093 | 122.2549 | 0.10071 | 115.4663 | 122.1542 | 122.3511 | -122.5021 | -122.5433
1697.8906 | 122.3236 | -122.1359 | 0.068665 | 0.0096895 | 0.0010766 | 0.011395 | 0.026132 | 0.040148 | -0.035335 | 0.060558 | -122.113 | 0.086975 | -122.4289 | -122.049 | -0.064087 | -6.9214 | -3.6987 | -5.4611 | 0.17395 | -122.4197 | -0.29297 | 0.01831 | 0.022888 | 0.086975 | -0.13275 | -0.28381 | 0.10528 | 0.31586 | 118.4372 | 116.6748 | 122.0718 | 122.2229 | 0.022888 | 122.3099 | 115.2145 | -0.28381 | 122.2229 | 0.022888 | 115.2145 | 122.0718 | 122.3099 | -122.4976 | -122.4884
1699.6719 | 122.3969 | -122.1222 | 0.086975 | 0.0096895 | 0.0017176 | 0.013958 | 0.022928 | 0.041003 | -0.030208 | 0.060344 | -122.049 | 0.073242 | -122.3099 | -121.9849 | 0.036621 | -6.9534 | -4.0466 | -5.5435 | 0.15564 | -122.4289 | -0.18768 | -0.013733 | 0.073242 | 0.13733 | -0.050354 | -0.3067 | 0.068665 | 0.26093 | 118.0756 | 116.5787 | 122.1588 | 122.1954 | 0.073242 | 122.2778 | 115.1688 | -0.3067 | 122.1954 | 0.073242 | 115.1688 | 122.1588 | 122.2778 | -122.3969 | -122.5159
1701.4531 | 122.319 | -122.1451 | 0.091553 | 0.0096895 | 0.0012902 | 0.0090447 | 0.025919 | 0.040362 | -0.032558 | 0.059703 | -122.1313 | 0.10071 | -122.3969 | -122.0398 | -0.045776 | -7.0953 | -3.8361 | -5.6488 | 0.20142 | -122.4152 | -0.25177 | 0.009155 | 0.013733 | 0.10529 | -0.13733 | -0.27008 | 0.10986 | 0.2655 | 118.309 | 116.4963 | 122.0993 | 122.2458 | 0.013733 | 122.3465 | 115.0497 | -0.27008 | 122.2458 | 0.013733 | 115.0497 | 122.0993 | 122.3465 | -122.4884 | -122.5067
1703.1719 | 122.3785 | -122.1405 | 0.09613 | 0.00206 | 8.578e-06 | 0.0094721 | 0.021433 | 0.042071 | -0.033413 | 0.060771 | -122.0535 | 0.07782 | -122.3099 | -121.9437 | 0.059509 | -7.132 | -4.2343 | -5.7083 | 0.14191 | -122.406 | -0.16937 | -0.01831 | 0.086975 | 0.19684 | -0.036621 | -0.2655 | 0.045777 | 0.25635 | 117.9062 | 116.4322 | 122.2 | 122.2183 | 0.086975 | 122.2824 | 115.0085 | -0.2655 | 122.2183 | 0.086975 | 115.0085 | 122.2 | 122.2824 | -122.406 | -122.5021
1704.9375 | 122.287 | -122.1817 | 0.1236 | 0.00206 | -0.00063242 | 0.012676 | 0.022501 | 0.039507 | -0.032985 | 0.057567 | -122.0306 | 0.059509 | -122.3465 | -121.9299 | 0.07782 | -7.2006 | -4.2664 | -5.7449 | 0.14191 | -122.4014 | -0.16479 | -0.064087 | 0.15106 | 0.25177 | -0.045776 | -0.21973 | 0.018311 | 0.31586 | 117.9153 | 116.4368 | 122.2595 | 122.2412 | 0.15106 | 122.3236 | 114.9811 | -0.21973 | 122.2412 | 0.15106 | 114.9811 | 122.2595 | 122.3236 | -122.4701 | -122.525
1706.7188 | 122.4152 | -122.1405 | 0.086975 | -0.0055695 | 0.0012902 | 0.011608 | 0.022074 | 0.038866 | -0.033413 | 0.060131 | -122.0993 | 0.073242 | -122.3785 | -122.0123 | -0.004578 | -7.4341 | -4.4586 | -6.0425 | 0.16022 | -122.4197 | -0.23804 | -0.013733 | 0.041199 | 0.12817 | -0.091553 | -0.27924 | 0.073242 | 0.27924 | 117.6819 | 116.098 | 122.1359 | 122.2137 | 0.041199 | 122.3007 | 114.7064 | -0.27924 | 122.2137 | 0.041199 | 114.7064 | 122.1359 | 122.3007 | -122.4655 | -122.5067
1708.5 | 122.4106 | -122.1268 | 0.09613 | 0.00206 | 8.578e-06 | 0.0079767 | 0.024423 | 0.03908 | -0.030849 | 0.061626 | -122.0581 | 0.064087 | -122.3511 | -121.9986 | 0.022888 | -7.4753 | -4.628 | -6.0745 | 0.15106 | -122.4426 | -0.2243 | -0.032043 | 0.068665 | 0.12817 | -0.073242 | -0.31586 | 0.054932 | 0.29297 | 117.4988 | 116.0522 | 122.1497 | 122.1909 | 0.068665 | 122.2778 | 114.6515 | -0.31586 | 122.1909 | 0.068665 | 114.6515 | 122.1497 | 122.2778 | -122.4472 | -122.5388
1710.2031 | 122.2916 | -122.168 | 0.10071 | 0.0096895 | 0.0010766 | 0.010754 | 0.022714 | 0.037371 | -0.032345 | 0.058635 | -122.0306 | 0.07782 | -122.3831 | -121.9574 | 0.073242 | -7.4799 | -4.6097 | -6.0196 | 0.13275 | -122.4106 | -0.21515 | -0.022888 | 0.13733 | 0.21057 | -0.027466 | -0.24261 | 0.032043 | 0.35248 | 117.5583 | 116.1484 | 122.2412 | 122.2458 | 0.13733 | 122.3007 | 114.6881 | -0.24261 | 122.2458 | 0.13733 | 114.6881 | 122.2412 | 122.3007 | -122.4838 | -122.5113
1711.9688 | 122.3053 | -122.168 | 0.11444 | 0.00206 | -0.002555 | 0.0094721 | 0.023142 | 0.038439 | -0.03384 | 0.05949 | -122.0169 | 0.068665 | -122.406 | -121.9345 | 0.07782 | -7.6126 | -4.7882 | -6.1661 | 0.13733 | -122.3969 | -0.23804 | -0.045776 | 0.15106 | 0.23346 | -0.036621 | -0.22888 | 0.022888 | 0.3891 | 117.3798 | 116.0019 | 122.2458 | 122.2366 | 0.15106 | 122.3053 | 114.5554 | -0.22888 | 122.2366 | 0.15106 | 114.5554 | 122.2458 | 122.3053 | -122.5204 | -122.5113
1713.7344 | 122.374 | -122.1542 | 0.091553 | 0.0096895 | -0.0014868 | 0.012463 | 0.027201 | 0.040148 | -0.032985 | 0.059917 | -122.0444 | 0.041199 | -122.4014 | -121.962 | 0.032043 | -7.7362 | -5.04 | -6.3721 | 0.16022 | -122.406 | -0.24719 | -0.050354 | 0.10986 | 0.19226 | -0.05951 | -0.25177 | 0.068664 | 0.35706 | 117.1143 | 115.7822 | 122.1863 | 122.1954 | 0.10986 | 122.3145 | 114.418 | -0.25177 | 122.1954 | 0.10986 | 114.418 | 122.1863 | 122.3145 | -122.493 | -122.4976
1715.5156 | 122.4197 | -122.1313 | 0.073242 | 0.0096895 | 0.00043578 | 0.0088311 | 0.022501 | 0.03908 | -0.032131 | 0.060985 | -122.113 | 0.091553 | -122.3602 | -122.0261 | 0.013733 | -7.8506 | -5.0491 | -6.5323 | 0.16479 | -122.438 | -0.22888 | 0.018311 | 0.018311 | 0.10529 | -0.059509 | -0.3067 | 0.091553 | 0.24719 | 117.0822 | 115.5991 | 122.1451 | 122.2229 | 0.018311 | 122.2961 | 114.2807 | -0.3067 | 122.2229 | 0.018311 | 114.2807 | 122.1451 | 122.2961 | -122.4335 | -122.5113
1717.2344 | 122.3053 | -122.168 | 0.11902 | 0.00206 | 0.0019312 | 0.011608 | 0.028696 | 0.038866 | -0.033413 | 0.058635 | -122.1039 | 0.09613 | -122.4289 | -122.0032 | -0.004578 | -7.9468 | -5.0217 | -6.6467 | 0.17395 | -122.4289 | -0.26093 | -0.022889 | 0.064087 | 0.16479 | -0.1236 | -0.26093 | 0.054931 | 0.32501 | 117.1463 | 115.5212 | 122.1634 | 122.2641 | 0.064087 | 122.3419 | 114.2212 | -0.26093 | 122.2641 | 0.064087 | 114.2212 | 122.1634 | 122.3419 | -122.5479 | -122.5479
1719.0312 | 122.438 | -122.1497 | 0.086975 | -0.0055695 | 8.578e-06 | 0.013958 | 0.021005 | 0.036944 | -0.030849 | 0.060344 | -122.113 | 0.07782 | -122.3648 | -122.0078 | 0.013733 | -8.0521 | -5.3329 | -6.7886 | 0.14191 | -122.4701 | -0.21515 | -0.009155 | 0.036621 | 0.14191 | -0.073242 | -0.32044 | 0.054932 | 0.25177 | 116.8167 | 115.361 | 122.1634 | 122.2275 | 0.036621 | 122.2916 | 114.0976 | -0.32044 | 122.2275 | 0.036621 | 114.0976 | 122.1634 | 122.2916 | -122.4518 | -122.5571
1720.8125 | 122.3007 | -122.1725 | 0.10529 | 0.0096895 | 0.0027856 | 0.0094721 | 0.030618 | 0.040789 | -0.033413 | 0.059062 | -122.1222 | 0.091553 | -122.4472 | -122.0306 | -0.009155 | -8.1345 | -5.3192 | -6.8665 | 0.19684 | -122.438 | -0.27466 | -0.013733 | 0.050354 | 0.14191 | -0.11444 | -0.2655 | 0.091552 | 0.32501 | 116.8533 | 115.3061 | 122.1634 | 122.2641 | 0.050354 | 122.3694 | 114.0381 | -0.2655 | 122.2641 | 0.050354 | 114.0381 | 122.1634 | 122.3694 | -122.5525 | -122.5433
1722.5312 | 122.4609 | -122.1405 | 0.073242 | -0.0055695 | 0.0010766 | 0.010967 | 0.023142 | 0.03908 | -0.030636 | 0.058422 | -122.1039 | 0.073242 | -122.3511 | -122.0306 | 0.018311 | -8.5785 | -5.9189 | -7.4753 | 0.15564 | -122.4472 | -0.21057 | 0 | 0.036621 | 0.10986 | -0.054931 | -0.3067 | 0.082398 | 0.24719 | 116.2216 | 114.6652 | 122.1588 | 122.2137 | 0.036621 | 122.2961 | 113.562 | -0.3067 | 122.2137 | 0.036621 | 113.562 | 122.1588 | 122.2961 | -122.4243 | -122.5204
1724.3125 | 122.2916 | -122.1909 | 0.091553 | -0.0055695 | -0.00063242 | 0.0079767 | 0.031473 | 0.039507 | -0.035122 | 0.060344 | -122.0993 | 0.068665 | -122.4197 | -122.0306 | -0.018311 | -9.0408 | -6.1981 | -8.02 | 0.1831 | -122.4197 | -0.22888 | -0.022888 | 0.091553 | 0.16022 | -0.10986 | -0.22888 | 0.091552 | 0.32044 | 115.9927 | 114.1708 | 122.1725 | 122.2595 | 0.091553 | 122.374 | 113.15 | -0.22888 | 122.2595 | 0.091553 | 113.15 | 122.1725 | 122.374 | -122.5113 | -122.5113
1726.0312 | 122.3923 | -122.1588 | 0.09613 | 0.00206 | 0.001504 | 0.011822 | 0.02421 | 0.040362 | -0.034054 | 0.061412 | -122.0535 | 0.050354 | -122.3648 | -121.9757 | 0.050354 | -9.1644 | -6.5964 | -8.2031 | 0.1236 | -122.4335 | -0.20599 | -0.045776 | 0.10528 | 0.1831 | -0.045776 | -0.27466 | 0.027466 | 0.31128 | 115.5624 | 113.9557 | 122.2092 | 122.2092 | 0.10528 | 122.2824 | 112.9944 | -0.27466 | 122.2092 | 0.10528 | 112.9944 | 122.2092 | 122.2824 | -122.4609 | -122.5296
1727.8125 | 122.3282 | -122.2137 | 0.10529 | 0.017319 | 0.0010766 | 0.014599 | 0.021646 | 0.036517 | -0.031704 | 0.058208 | -122.081 | 0.068665 | -122.3877 | -122.0078 | 0.036621 | -9.2834 | -6.5323 | -8.2489 | 0.16937 | -122.4609 | -0.17395 | -0.036621 | 0.13275 | 0.20599 | -0.068665 | -0.24719 | 0.064087 | 0.3067 | 115.6815 | 113.9648 | 122.2504 | 122.2824 | 0.13275 | 122.3831 | 112.9303 | -0.24719 | 122.2824 | 0.13275 | 112.9303 | 122.2504 | 122.3831 | -122.493 | -122.5662
1729.5938 | 122.4472 | -122.1634 | 0.086975 | 0.00206 | 0.0010766 | 0.010326 | 0.026987 | 0.042498 | -0.032345 | 0.060558 | -122.1817 | 0.10071 | -122.4335 | -122.1039 | -0.10071 | -9.5032 | -6.6605 | -8.6105 | 0.19684 | -122.4884 | -0.27008 | 0.013733 | -0.018311 | 0.059509 | -0.18768 | -0.32501 | 0.10986 | 0.25177 | 115.5029 | 113.5529 | 122.0627 | 122.2641 | -0.018311 | 122.3602 | 112.6602 | -0.32501 | 122.2641 | -0.018311 | 112.6602 | 122.0627 | 122.3602 | -122.5204 | -122.5754
1731.375 | 122.3145 | -122.1909 | 0.11902 | 0.017319 | 0.0012902 | 0.0084039 | 0.020792 | 0.040575 | -0.032345 | 0.057994 | -122.0627 | 0.059509 | -122.3694 | -121.9803 | 0.068665 | -9.4849 | -6.9305 | -8.5556 | 0.14191 | -122.4518 | -0.17853 | -0.05951 | 0.12817 | 0.21057 | -0.050354 | -0.26093 | 0.022888 | 0.3067 | 115.2603 | 113.6353 | 122.2595 | 122.2504 | 0.12817 | 122.3328 | 112.706 | -0.26093 | 122.2504 | 0.12817 | 112.706 | 122.2595 | 122.3328 | -122.4884 | -122.5708
1733.1094 | 122.374 | -122.2 | 0.10986 | 0.0096895 | 0.0012902 | 0.013104 | 0.02421 | 0.040575 | -0.033626 | 0.061626 | -122.1817 | 0.10071 | -122.4426 | -122.0947 | -0.082397 | -9.6725 | -6.8665 | -8.8348 | 0.18768 | -122.4655 | -0.24262 | -0.009155 | 0.01831 | 0.10528 | -0.19226 | -0.2655 | 0.07782 | 0.26093 | 115.3336 | 113.3652 | 122.1176 | 122.3007 | 0.01831 | 122.3877 | 112.5275 | -0.2655 | 122.3007 | 0.01831 | 112.5275 | 122.1176 | 122.3877 | -122.5525 | -122.5754
1734.8906 | 122.3236 | -122.168 | 0.091553 | 0.017319 | 0.00043578 | 0.014172 | 0.026132 | 0.041216 | -0.034694 | 0.063121 | -122.1313 | 0.082397 | -122.4426 | -122.0581 | -0.041199 | -9.7641 | -7.0267 | -8.9127 | 0.16937 | -122.4518 | -0.27466 | -0.009156 | 0.036621 | 0.10986 | -0.13275 | -0.28381 | 0.07782 | 0.31128 | 115.1413 | 113.2553 | 122.1268 | 122.2504 | 0.036621 | 122.3373 | 112.4039 | -0.28381 | 122.2504 | 0.036621 | 112.4039 | 122.1268 | 122.3373 | -122.5342 | -122.5433
1736.6719 | 122.3053 | -122.2046 | 0.11902 | 0.0096895 | 0.0017176 | 0.013958 | 0.025705 | 0.041003 | -0.037472 | 0.061199 | -122.1222 | 0.082397 | -122.4335 | -122.049 | -0.022888 | -9.9289 | -7.2784 | -9.1553 | 0.17853 | -122.4655 | -0.22888 | -0.036622 | 0.082398 | 0.15564 | -0.14191 | -0.26093 | 0.059509 | 0.31128 | 114.9261 | 113.0493 | 122.1817 | 122.287 | 0.082398 | 122.3831 | 112.2757 | -0.26093 | 122.287 | 0.082398 | 112.2757 | 122.1817 | 122.3831 | -122.5525 | -122.5845
1738.4531 | 122.4243 | -122.1634 | 0.054932 | 0.00206 | 0.0021448 | 0.011395 | 0.023783 | 0.04143 | -0.035976 | 0.062053 | -122.1268 | 0.068665 | -122.4152 | -122.049 | 0 | -10.025 | -7.6035 | -9.3338 | 0.16022 | -122.4335 | -0.25177 | 0.013733 | 0.036621 | 0.11444 | -0.054932 | -0.27008 | 0.10528 | 0.28839 | 114.5599 | 112.8296 | 122.1634 | 122.2321 | 0.036621 | 122.3236 | 112.1384 | -0.27008 | 122.2321 | 0.036621 | 112.1384 | 122.1634 | 122.3236 | -122.4701 | -122.4884
1740.2188 | 122.4106 | -122.1817 | 0.091553 | 0.0096895 | -0.00041862 | 0.01054 | 0.021219 | 0.041644 | -0.030849 | 0.061199 | -122.0856 | 0.054932 | -122.3465 | -122.0123 | 0.032043 | -10.0754 | -7.7637 | -9.4482 | 0.14648 | -122.438 | -0.16479 | -0.036621 | 0.096131 | 0.16937 | -0.05951 | -0.25635 | 0.054931 | 0.26093 | 114.418 | 112.7335 | 122.2137 | 122.2366 | 0.096131 | 122.3282 | 112.1063 | -0.25635 | 122.2366 | 0.096131 | 112.1063 | 122.2137 | 122.3282 | -122.4381 | -122.5296
1742 | 122.3282 | -122.2137 | 0.10986 | 0.00206 | 0.0040674 | 0.013317 | 0.02891 | 0.040362 | -0.03384 | 0.059276 | -122.1085 | 0.091553 | -122.4197 | -122.0398 | -0.032043 | -10.2676 | -7.7179 | -9.6313 | 0.18768 | -122.4792 | -0.20599 | -0.01831 | 0.10529 | 0.17395 | -0.14191 | -0.2655 | 0.07782 | 0.31128 | 114.4958 | 112.5824 | 122.1817 | 122.3053 | 0.10529 | 122.4014 | 111.9461 | -0.2655 | 122.3053 | 0.10529 | 111.9461 | 122.1817 | 122.4014 | -122.5296 | -122.5891
1743.7188 | 122.4426 | -122.1451 | 0.086975 | 0.00206 | -0.00063242 | 0.0075495 | 0.021433 | 0.040148 | -0.031063 | 0.061412 | -122.113 | 0.07782 | -122.3877 | -122.0261 | 0.018311 | -10.3683 | -8.075 | -9.8511 | 0.16022 | -122.4884 | -0.24261 | -0.009155 | 0.032044 | 0.11902 | -0.068664 | -0.34332 | 0.073242 | 0.27466 | 114.0701 | 112.294 | 122.1634 | 122.2229 | 0.032044 | 122.3053 | 111.7767 | -0.34332 | 122.2229 | 0.032044 | 111.7767 | 122.1634 | 122.3053 | -122.4747 | -122.5754
1745.5156 | 122.4106 | -122.1954 | 0.068665 | 0.00206 | 0.001504 | 0.013958 | 0.026132 | 0.038866 | -0.032772 | 0.062053 | -122.0718 | 0.059509 | -122.3923 | -122.0169 | 0.022888 | -10.5423 | -8.2947 | -10.0388 | 0.14648 | -122.4792 | -0.19684 | -0.009156 | 0.1236 | 0.17853 | -0.045777 | -0.28381 | 0.077819 | 0.32044 | 113.9008 | 112.1567 | 122.2183 | 122.2549 | 0.1236 | 122.3419 | 111.6531 | -0.28381 | 122.2549 | 0.1236 | 111.6531 | 122.2183 | 122.3419 | -122.4609 | -122.5479
1747.2344 | 122.3831 | -122.2137 | 0.10071 | 0.00206 | 0.00064938 | 0.0090447 | 0.024851 | 0.038226 | -0.034481 | 0.057781 | -122.1817 | 0.091553 | -122.4289 | -122.113 | -0.086975 | -10.7437 | -8.1161 | -10.1715 | 0.20599 | -122.525 | -0.21515 | -0.009155 | 0.032043 | 0.10071 | -0.18768 | -0.31128 | 0.10529 | 0.24719 | 114.0976 | 112.0422 | 122.1268 | 122.3053 | 0.032043 | 122.4197 | 111.47 | -0.31128 | 122.3053 | 0.032043 | 111.47 | 122.1268 | 122.4197 | -122.5296 | -122.6257
1749.0156 | 122.3923 | -122.2092 | 0.09613 | 0.0096895 | 0.0012902 | 0.0084039 | 0.024423 | 0.039507 | -0.03149 | 0.058208 | -122.1817 | 0.082397 | -122.4609 | -122.1085 | -0.07782 | -10.9634 | -8.345 | -10.4141 | 0.19226 | -122.5067 | -0.25177 | -0.013733 | 0.027465 | 0.10071 | -0.17395 | -0.29755 | 0.096131 | 0.27923 | 113.8641 | 111.795 | 122.1313 | 122.2916 | 0.027465 | 122.4014 | 111.2457 | -0.29755 | 122.2916 | 0.027465 | 111.2457 | 122.1313 | 122.4014 | -122.5571 | -122.6028
1750.7188 | 122.438 | -122.1588 | 0.07782 | -0.0055695 | 8.578e-06 | 0.01054 | 0.02955 | 0.040148 | -0.034481 | 0.060131 | -122.2 | 0.09613 | -122.4976 | -122.1359 | -0.1236 | -11.1237 | -8.5464 | -10.6659 | 0.1831 | -122.5067 | -0.33875 | 0.01831 | -0.041199 | 0.022888 | -0.20142 | -0.3479 | 0.10528 | 0.29755 | 113.6124 | 111.4929 | 122.0352 | 122.2549 | -0.041199 | 122.3419 | 111.0352 | -0.3479 | 122.2549 | -0.041199 | 111.0352 | 122.0352 | 122.3419 | -122.5754 | -122.5845
1752.5 | 122.438 | -122.1817 | 0.07782 | 0.024948 | 0.00043578 | 0.014172 | 0.025492 | 0.039721 | -0.033199 | 0.062694 | -122.1725 | 0.086975 | -122.4472 | -122.0947 | -0.059509 | -10.8444 | -8.6197 | -10.5606 | 0.15564 | -122.4655 | -0.2655 | 0.009155 | 0.009156 | 0.086975 | -0.13733 | -0.28381 | 0.07782 | 0.27466 | 113.562 | 111.6211 | 122.1222 | 122.2687 | 0.009156 | 122.3373 | 111.3373 | -0.28381 | 122.2687 | 0.009156 | 111.3373 | 122.1222 | 122.3373 | -122.525 | -122.5433
1754.2812 | 122.3511 | -122.2183 | 0.11902 | 0.0096895 | 0.0017176 | 0.0079767 | 0.02186 | 0.040148 | -0.034908 | 0.059917 | -122.0673 | 0.050354 | -122.3831 | -121.9803 | 0.054932 | -10.8673 | -8.7112 | -10.4736 | 0.14648 | -122.4838 | -0.16479 | -0.068665 | 0.15106 | 0.23804 | -0.064087 | -0.2655 | 0.027465 | 0.31586 | 113.5071 | 111.7447 | 122.2733 | 122.2687 | 0.15106 | 122.3648 | 111.351 | -0.2655 | 122.2687 | 0.15106 | 111.351 | 122.2733 | 122.3648 | -122.5021 | -122.6028
1756 | 122.3557 | -122.2137 | 0.10986 | 0.00206 | -0.0061866 | 0.010967 | 0.022074 | 0.038866 | -0.032985 | 0.059276 | -122.0993 | 0.050354 | -122.4426 | -121.9986 | 0.036621 | -10.968 | -8.876 | -10.643 | 0.15106 | -122.4609 | -0.22888 | -0.059509 | 0.11444 | 0.21515 | -0.073242 | -0.24719 | 0.041199 | 0.34332 | 113.3377 | 111.5707 | 122.2504 | 122.2641 | 0.11444 | 122.3648 | 111.2457 | -0.24719 | 122.2641 | 0.11444 | 111.2457 | 122.2504 | 122.3648 | -122.5525 | -122.5708
1757.7656 | 122.3831 | -122.2412 | 0.10529 | 0.00206 | 0.0017176 | 0.011181 | 0.021219 | 0.038653 | -0.032772 | 0.061412 | -122.0856 | 0.041199 | -122.4243 | -122.0078 | 0.027466 | -11.1099 | -9.0317 | -10.7254 | 0.14648 | -122.4747 | -0.1831 | -0.064087 | 0.15564 | 0.23346 | -0.07782 | -0.23346 | 0.041198 | 0.33875 | 113.2095 | 111.5158 | 122.2687 | 122.2824 | 0.15564 | 122.3877 | 111.1313 | -0.23346 | 122.2824 | 0.15564 | 111.1313 | 122.2687 | 122.3877 | -122.5296 | -122.58
1759.5469 | 122.4792 | -122.1771 | 0.068665 | 0.0096895 | 0.00022218 | 0.014599 | 0.023569 | 0.039507 | -0.032131 | 0.059703 | -122.1451 | 0.068665 | -122.4197 | -122.081 | -0.032043 | -11.3937 | -9.256 | -11.0687 | 0.14191 | -122.4976 | -0.24262 | 0 | 0.032043 | 0.09613 | -0.10071 | -0.32043 | 0.073242 | 0.27466 | 112.9211 | 111.1084 | 122.1451 | 122.2458 | 0.032043 | 122.319 | 110.7834 | -0.32043 | 122.2458 | 0.032043 | 110.7834 | 122.1451 | 122.319 | -122.4884 | -122.5662
1761.3281 | 122.374 | -122.2321 | 0.10986 | -0.0055695 | -0.0027686 | 0.011822 | 0.023355 | 0.038439 | -0.031917 | 0.059276 | -122.0993 | 0.032043 | -122.438 | -122.0032 | 0.009155 | -11.4075 | -9.3567 | -11.0779 | 0.14191 | -122.4747 | -0.20599 | -0.07782 | 0.13275 | 0.22888 | -0.10071 | -0.24261 | 0.032044 | 0.33875 | 112.8754 | 111.1542 | 122.2412 | 122.2641 | 0.13275 | 122.374 | 110.8246 | -0.24261 | 122.2641 | 0.13275 | 110.8246 | 122.2412 | 122.374 | -122.5479 | -122.5845
1763.0469 | 122.3602 | -122.2137 | 0.10529 | 0.0096895 | 0.0021448 | 0.012676 | 0.030405 | 0.039294 | -0.033626 | 0.062053 | -122.1359 | 0.086975 | -122.4838 | -122.081 | -0.07782 | -11.6913 | -9.3613 | -11.4075 | 0.16937 | -122.5067 | -0.27008 | -0.018311 | 0.07782 | 0.13275 | -0.18311 | -0.29297 | 0.064087 | 0.3479 | 112.8525 | 110.8063 | 122.1359 | 122.3007 | 0.07782 | 122.3831 | 110.5225 | -0.29297 | 122.3007 | 0.07782 | 110.5225 | 122.1359 | 122.3831 | -122.5891 | -122.612
1764.8281 | 122.3831 | -122.2504 | 0.10071 | 0.0096895 | 0.00043578 | 0.013317 | 0.022074 | 0.039507 | -0.032345 | 0.060985 | -122.0947 | 0.050354 | -122.3969 | -122.0032 | 0.036621 | -11.7783 | -9.6817 | -11.5265 | 0.15564 | -122.4884 | -0.14648 | -0.050354 | 0.15564 | 0.24719 | -0.064087 | -0.23804 | 0.054932 | 0.30212 | 112.5687 | 110.7239 | 122.287 | 122.3007 | 0.15564 | 122.406 | 110.4721 | -0.23804 | 122.3007 | 0.15564 | 110.4721 | 122.287 | 122.406 | -122.4976 | -122.5891
1766.6094 | 122.4106 | -122.2183 | 0.10529 | 0.017319 | 8.578e-06 | 0.01524 | 0.027628 | 0.037798 | -0.035335 | 0.061626 | -122.2229 | 0.09613 | -122.4976 | -122.1039 | -0.09613 | -11.9705 | -9.8694 | -11.7737 | 0.17853 | -122.5433 | -0.27924 | -0.009156 | -0.004577 | 0.11444 | -0.20142 | -0.32501 | 0.073242 | 0.27466 | 112.3489 | 110.4446 | 122.1222 | 122.3145 | -0.004577 | 122.3969 | 110.2478 | -0.32501 | 122.3145 | -0.004577 | 110.2478 | 122.1222 | 122.3969 | -122.6028 | -122.6486
1768.3906 | 122.4838 | -122.1725 | 0.082397 | 0.0096895 | 0.0017176 | 0.0086175 | 0.028055 | 0.040789 | -0.031704 | 0.062053 | -122.2275 | 0.09613 | -122.4701 | -122.1634 | -0.12817 | -12.2635 | -9.8831 | -12.149 | 0.1831 | -122.5296 | -0.29755 | 0.013733 | -0.054932 | 0.009155 | -0.21057 | -0.35706 | 0.10071 | 0.24262 | 112.2894 | 110.0235 | 122.0444 | 122.2687 | -0.054932 | 122.3557 | 109.9091 | -0.35706 | 122.2687 | -0.054932 | 109.9091 | 122.0444 | 122.3557 | -122.5525 | -122.612
1770.1094 | 122.4838 | -122.2229 | 0.09613 | 0.017319 | 0.0012902 | 0.012249 | 0.01951 | 0.039294 | -0.032345 | 0.061412 | -122.1634 | 0.068665 | -122.4518 | -122.0901 | -0.050354 | -12.2269 | -10.0937 | -12.1078 | 0.13733 | -122.5067 | -0.22888 | -0.027465 | 0.059509 | 0.13275 | -0.14648 | -0.28381 | 0.041199 | 0.28839 | 112.1292 | 110.1151 | 122.1725 | 122.2916 | 0.059509 | 122.3602 | 109.996 | -0.28381 | 122.2916 | 0.059509 | 109.996 | 122.1725 | 122.3602 | -122.5479 | -122.6028
1771.875 | 122.4655 | -122.2 | 0.086975 | 0.0096895 | 0.0021448 | 0.013744 | 0.025492 | 0.039294 | -0.032131 | 0.058849 | -122.1085 | 0.050354 | -122.438 | -122.0535 | -0.027466 | -12.41 | -10.3683 | -12.4008 | 0.14191 | -122.5067 | -0.23804 | -0.036621 | 0.091553 | 0.14648 | -0.11444 | -0.3067 | 0.054932 | 0.32959 | 111.8317 | 109.7992 | 122.1725 | 122.2504 | 0.091553 | 122.3419 | 109.79 | -0.3067 | 122.2504 | 0.091553 | 109.79 | 122.1725 | 122.3419 | -122.525 | -122.5937
1773.5938 | 122.493 | -122.2092 | 0.082397 | 0.00206 | 0.0021448 | 0.010326 | 0.021005 | 0.039507 | -0.032131 | 0.059703 | -122.1497 | 0.054932 | -122.4197 | -122.1039 | -0.050354 | -12.6022 | -10.4599 | -12.6846 | 0.15564 | -122.4976 | -0.21057 | -0.027465 | 0.059509 | 0.10528 | -0.13275 | -0.28839 | 0.073243 | 0.27008 | 111.7493 | 109.5245 | 122.1588 | 122.2641 | 0.059509 | 122.3648 | 109.6069 | -0.28839 | 122.2641 | 0.059509 | 109.6069 | 122.1588 | 122.3648 | -122.5021 | -122.58
1775.375 | 122.4884 | -122.1909 | 0.09613 | 0.00206 | 0.0032128 | 0.0094721 | 0.023996 | 0.038226 | -0.031917 | 0.060558 | -122.1451 | 0.073242 | -122.438 | -122.0444 | -0.022888 | -12.7213 | -10.6476 | -12.7487 | 0.16937 | -122.5067 | -0.24719 | -0.022888 | 0.045776 | 0.14648 | -0.11902 | -0.31586 | 0.073243 | 0.29297 | 111.5433 | 109.4421 | 122.168 | 122.2641 | 0.045776 | 122.3602 | 109.4696 | -0.31586 | 122.2641 | 0.045776 | 109.4696 | 122.168 | 122.3602 | -122.5342 | -122.6028
1777.1562 | 122.4335 | -122.2229 | 0.091553 | 0.017319 | 0.00064938 | 0.013531 | 0.028269 | 0.044421 | -0.035335 | 0.061199 | -122.1954 | 0.086975 | -122.5204 | -122.1405 | -0.13275 | -12.9868 | -10.6796 | -13.1012 | 0.1831 | -122.5067 | -0.29755 | -0.004578 | 0.027465 | 0.082397 | -0.2243 | -0.28381 | 0.091552 | 0.32501 | 111.5433 | 109.1217 | 122.0901 | 122.3099 | 0.027465 | 122.406 | 109.2361 | -0.28381 | 122.3099 | 0.027465 | 109.2361 | 122.0901 | 122.406 | -122.612 | -122.5983
1778.875 | 122.3602 | -122.2366 | 0.12817 | -0.0055695 | 0.002572 | 0.013958 | 0.026987 | 0.041216 | -0.033413 | 0.061626 | -122.1588 | 0.082397 | -122.4884 | -122.0901 | -0.07782 | -13.0463 | -10.7803 | -13.1653 | 0.19684 | -122.5204 | -0.25177 | -0.045777 | 0.07782 | 0.14648 | -0.20599 | -0.28381 | 0.068664 | 0.32959 | 111.4563 | 109.0713 | 122.1588 | 122.319 | 0.07782 | 122.4335 | 109.1904 | -0.28381 | 122.319 | 0.07782 | 109.1904 | 122.1588 | 122.4335 | -122.6166 | -122.6486
1780.6406 | 122.4655 | -122.2321 | 0.091553 | 0.017319 | 0.00086298 | 0.016094 | 0.027414 | 0.041003 | -0.032985 | 0.062908 | -122.2229 | 0.082397 | -122.5204 | -122.1634 | -0.14648 | -13.147 | -10.8536 | -13.4125 | 0.19684 | -122.5388 | -0.28839 | -0.009156 | 0.009156 | 0.068665 | -0.23804 | -0.3067 | 0.10529 | 0.29755 | 111.3785 | 108.8196 | 122.0856 | 122.3145 | 0.009156 | 122.4289 | 109.0851 | -0.3067 | 122.3145 | 0.009156 | 109.0851 | 122.0856 | 122.4289 | -122.612 | -122.6303
1782.4062 | 122.5113 | -122.2 | 0.07782 | 0.0096895 | 8.578e-06 | 0.015026 | 0.025919 | 0.041644 | -0.032131 | 0.059276 | -122.2458 | 0.09613 | -122.4884 | -122.2 | -0.13275 | -13.1607 | -10.9863 | -13.678 | 0.17853 | -122.5113 | -0.28839 | 0.01831 | -0.045777 | 0 | -0.21057 | -0.31128 | 0.10071 | 0.24261 | 111.2137 | 108.522 | 122.0673 | 122.2961 | -0.045777 | 122.3785 | 109.0393 | -0.31128 | 122.2961 | -0.045777 | 109.0393 | 122.0673 | 122.3785 | -122.5662 | -122.5891
1784.1406 | 122.3648 | -122.2641 | 0.1236 | 0.00206 | 0.0044946 | 0.016735 | 0.024851 | 0.039935 | -0.032345 | 0.058635 | -122.1725 | 0.086975 | -122.4792 | -122.1039 | -0.059509 | -13.1699 | -11.1237 | -13.7009 | 0.16937 | -122.5525 | -0.21515 | -0.036621 | 0.091553 | 0.16022 | -0.1831 | -0.28839 | 0.045777 | 0.3067 | 111.1404 | 108.5632 | 122.2046 | 122.3511 | 0.091553 | 122.4335 | 109.0942 | -0.28839 | 122.3511 | 0.091553 | 109.0942 | 122.2046 | 122.4335 | -122.6028 | -122.6761
1785.9062 | 122.3831 | -122.2549 | 0.10529 | 0.00206 | 0.0012902 | 0.0088311 | 0.01951 | 0.039294 | -0.031917 | 0.059062 | -122.1222 | 0.050354 | -122.4106 | -122.0261 | 0 | -13.1836 | -11.348 | -13.7421 | 0.14648 | -122.5067 | -0.15564 | -0.054932 | 0.13275 | 0.22888 | -0.10529 | -0.25177 | 0.041198 | 0.28839 | 110.907 | 108.5129 | 122.2549 | 122.3053 | 0.13275 | 122.4014 | 109.0713 | -0.25177 | 122.3053 | 0.13275 | 109.0713 | 122.2549 | 122.4014 | -122.5159 | -122.612
1787.6094 | 122.4747 | -122.2183 | 0.082397 | 0.0096895 | -0.00063242 | 0.019085 | 0.026132 | 0.042498 | -0.034694 | 0.061199 | -122.2092 | 0.082397 | -122.4838 | -122.1222 | -0.091553 | -13.5956 | -11.6592 | -14.2548 | 0.17853 | -122.525 | -0.2655 | 0 | 0.009156 | 0.096131 | -0.17395 | -0.3067 | 0.096131 | 0.27466 | 110.5591 | 107.9636 | 122.1268 | 122.3007 | 0.009156 | 122.3969 | 108.6227 | -0.3067 | 122.3007 | 0.009156 | 108.6227 | 122.1268 | 122.3969 | -122.5662 | -122.6074
1789.3906 | 122.3694 | -122.2824 | 0.09613 | -0.0055695 | 0.0032128 | 0.012676 | 0.027201 | 0.043353 | -0.032985 | 0.062267 | -122.168 | 0.07782 | -122.5204 | -122.113 | -0.086975 | -13.7329 | -11.7874 | -14.5065 | 0.17853 | -122.5479 | -0.23804 | -0.01831 | 0.11444 | 0.16937 | -0.1831 | -0.2655 | 0.082398 | 0.35248 | 110.495 | 107.7759 | 122.1954 | 122.3602 | 0.11444 | 122.4609 | 108.5495 | -0.2655 | 122.3602 | 0.11444 | 108.5495 | 122.1954 | 122.4609 | -122.6166 | -122.644
1791.1094 | 122.4243 | -122.2641 | 0.086975 | 0.017319 | 0.0021448 | 0.01524 | 0.026132 | 0.041644 | -0.03149 | 0.062053 | -122.2137 | 0.082397 | -122.493 | -122.1725 | -0.14191 | -13.9572 | -11.9064 | -14.74 | 0.20599 | -122.5616 | -0.22888 | -0.004578 | 0.050354 | 0.091553 | -0.22888 | -0.29755 | 0.11902 | 0.27924 | 110.3577 | 107.5241 | 122.1222 | 122.3465 | 0.050354 | 122.4701 | 108.3069 | -0.29755 | 122.3465 | 0.050354 | 108.3069 | 122.1222 | 122.4701 | -122.58 | -122.6486
1792.875 | 122.4197 | -122.2504 | 0.10986 | 0.0096895 | 0.0010766 | 0.010967 | 0.018442 | 0.039721 | -0.032772 | 0.060131 | -122.1588 | 0.068665 | -122.4564 | -122.113 | -0.073242 | -13.9572 | -12.0117 | -14.772 | 0.16937 | -122.5616 | -0.20599 | -0.041198 | 0.091553 | 0.13733 | -0.18311 | -0.31128 | 0.05951 | 0.29755 | 110.2386 | 107.4783 | 122.1771 | 122.319 | 0.091553 | 122.4197 | 108.2932 | -0.31128 | 122.319 | 0.091553 | 108.2932 | 122.1771 | 122.4197 | -122.5662 | -122.6715
1794.6562 | 122.406 | -122.2595 | 0.10529 | 0.0096895 | 0.0029992 | 0.014172 | 0.023783 | 0.037585 | -0.032772 | 0.05949 | -122.2092 | 0.09613 | -122.5204 | -122.1176 | -0.10071 | -14.1312 | -12.1765 | -15.0284 | 0.17853 | -122.5616 | -0.26093 | -0.009156 | 0.050354 | 0.14191 | -0.20599 | -0.30212 | 0.073242 | 0.31128 | 110.083 | 107.2311 | 122.1588 | 122.3557 | 0.050354 | 122.438 | 108.1284 | -0.30212 | 122.3557 | 0.050354 | 108.1284 | 122.1588 | 122.438 | -122.6257 | -122.6669
1796.4375 | 122.3877 | -122.2687 | 0.10986 | 0.00206 | -0.0012732 | 0.010326 | 0.020578 | 0.038012 | -0.032345 | 0.060985 | -122.1451 | 0.064087 | -122.4426 | -122.0718 | -0.050354 | -14.3463 | -12.5793 | -15.2664 | 0.14648 | -122.58 | -0.17395 | -0.045776 | 0.1236 | 0.19684 | -0.16022 | -0.31128 | 0.036621 | 0.29755 | 109.6893 | 107.0023 | 122.2183 | 122.3328 | 0.1236 | 122.4152 | 107.9224 | -0.31128 | 122.3328 | 0.1236 | 107.9224 | 122.2183 | 122.4152 | -122.5525 | -122.6898
1798.2188 | 122.4701 | -122.2549 | 0.082397 | -0.0055695 | -0.00084602 | 0.012463 | 0.022074 | 0.039294 | -0.03149 | 0.058849 | -122.1222 | 0.050354 | -122.4701 | -122.081 | -0.050354 | -14.5386 | -12.9776 | -15.5548 | 0.14648 | -122.5204 | -0.21515 | -0.032043 | 0.13275 | 0.17395 | -0.13275 | -0.2655 | 0.064087 | 0.3479 | 109.2773 | 106.7001 | 122.2046 | 122.3053 | 0.13275 | 122.4014 | 107.7164 | -0.2655 | 122.3053 | 0.13275 | 107.7164 | 122.2046 | 122.4014 | -122.5525 | -122.6028
1800 | 122.374 | -122.2549 | 0.10529 | 0.00206 | 0.0062036 | 0.010754 | 0.027201 | 0.038226 | -0.030849 | 0.060131 | -122.1634 | 0.10071 | -122.493 | -122.113 | -0.10986 | -14.7354 | -12.8769 | -15.7974 | 0.17853 | -122.5937 | -0.23804 | -0.004578 | 0.091553 | 0.14191 | -0.21515 | -0.33875 | 0.073242 | 0.32959 | 109.3781 | 106.4575 | 122.1451 | 122.3557 | 0.091553 | 122.4335 | 107.5195 | -0.33875 | 122.3557 | 0.091553 | 107.5195 | 122.1451 | 122.4335 | -122.5983 | -122.699
1801.7656 | 122.3969 | -122.2687 | 0.10071 | 0.00206 | 0.0012902 | 0.010967 | 0.027201 | 0.040362 | -0.033626 | 0.061626 | -122.1909 | 0.068665 | -122.5204 | -122.1222 | -0.12817 | -15.0192 | -13.2248 | -16.1865 | 0.17395 | -122.5571 | -0.25177 | -0.032043 | 0.07782 | 0.14648 | -0.22888 | -0.28839 | 0.073242 | 0.32959 | 109.0439 | 106.0822 | 122.1405 | 122.3373 | 0.07782 | 122.4426 | 107.2495 | -0.28839 | 122.3373 | 0.07782 | 107.2495 | 122.1405 | 122.4426 | -122.6212 | -122.6578
1803.5469 | 122.406 | -122.2778 | 0.11902 | 0.0096895 | -0.0010596 | 0.01289 | 0.01951 | 0.038226 | -0.033199 | 0.059062 | -122.1497 | 0.045776 | -122.4747 | -122.0673 | -0.045776 | -14.946 | -13.4399 | -16.2415 | 0.14191 | -122.5159 | -0.19684 | -0.073243 | 0.12817 | 0.21057 | -0.16479 | -0.23804 | 0.022888 | 0.32501 | 108.8379 | 106.0364 | 122.2321 | 122.3236 | 0.12817 | 122.4197 | 107.3318 | -0.23804 | 122.3236 | 0.12817 | 107.3318 | 122.2321 | 122.4197 | -122.5937 | -122.6349
1805.25 | 122.4884 | -122.2321 | 0.091553 | 0.017319 | 0.0010766 | 0.013104 | 0.024637 | 0.040789 | -0.033626 | 0.05949 | -122.1451 | 0.068665 | -122.4792 | -122.0856 | -0.07782 | -15.4221 | -13.8382 | -16.6855 | 0.14191 | -122.525 | -0.24719 | -0.022888 | 0.086975 | 0.14648 | -0.16937 | -0.29297 | 0.050354 | 0.33417 | 108.3939 | 105.5466 | 122.1542 | 122.3007 | 0.086975 | 122.374 | 106.81 | -0.29297 | 122.3007 | 0.086975 | 106.81 | 122.1542 | 122.374 | -122.5708 | -122.6166
1807.0312 | 122.4106 | -122.2778 | 0.12817 | -0.013199 | 0.0023584 | 0.013317 | 0.022287 | 0.038653 | -0.032131 | 0.059062 | -122.1497 | 0.059509 | -122.4747 | -122.081 | -0.07782 | -15.4312 | -13.8657 | -16.7953 | 0.15564 | -122.5525 | -0.19684 | -0.068665 | 0.12817 | 0.19684 | -0.20599 | -0.27466 | 0.027466 | 0.32501 | 108.4122 | 105.4825 | 122.2 | 122.3373 | 0.12817 | 122.4335 | 106.8466 | -0.27466 | 122.3373 | 0.12817 | 106.8466 | 122.2 | 122.4335 | -122.6028 | -122.6807
1808.8125 | 122.3831 | -122.2778 | 0.091553 | 0.00206 | 0.0017176 | 0.015453 | 0.027628 | 0.039935 | -0.035763 | 0.060771 | -122.1817 | 0.10071 | -122.5388 | -122.1176 | -0.13275 | -15.564 | -13.9572 | -17.0242 | 0.17853 | -122.5754 | -0.26093 | 0.009155 | 0.09613 | 0.16022 | -0.2243 | -0.29755 | 0.086975 | 0.35706 | 108.3206 | 105.2536 | 122.1451 | 122.3785 | 0.09613 | 122.4564 | 106.7139 | -0.29755 | 122.3785 | 0.09613 | 106.7139 | 122.1451 | 122.4564 | -122.6303 | -122.6669
1810.5312 | 122.4289 | -122.287 | 0.1236 | 0.00206 | 0.0049218 | 0.017162 | 0.028269 | 0.043566 | -0.034054 | 0.059917 | -122.2 | 0.091553 | -122.493 | -122.168 | -0.18768 | -15.6967 | -14.0671 | -17.2577 | 0.17395 | -122.5708 | -0.20599 | -0.032043 | 0.086975 | 0.11902 | -0.31128 | -0.28381 | 0.050354 | 0.29297 | 108.2199 | 105.0293 | 122.0993 | 122.3785 | 0.086975 | 122.4609 | 106.5903 | -0.28381 | 122.3785 | 0.086975 | 106.5903 | 122.0993 | 122.4609 | -122.6166 | -122.6944
1812.3125 | 122.374 | -122.2916 | 0.10529 | 0.00206 | -0.00063242 | 0.0079767 | 0.025919 | 0.039721 | -0.034054 | 0.059703 | -122.2092 | 0.091553 | -122.5388 | -122.1268 | -0.13733 | -15.7059 | -14.1769 | -17.3584 | 0.1831 | -122.5479 | -0.24719 | -0.013733 | 0.082398 | 0.1648 | -0.24262 | -0.25635 | 0.077819 | 0.32959 | 108.1146 | 104.9332 | 122.1542 | 122.3831 | 0.082398 | 122.4747 | 106.5857 | -0.25635 | 122.3831 | 0.082398 | 106.5857 | 122.1542 | 122.4747 | -122.644 | -122.6532
1814.0938 | 122.4014 | -122.3053 | 0.13275 | 0.00206 | -0.00084602 | 0.010967 | 0.018442 | 0.040789 | -0.033199 | 0.061412 | -122.1359 | 0.059509 | -122.4792 | -122.081 | -0.068665 | -15.6097 | -14.4196 | -17.4454 | 0.15106 | -122.525 | -0.17395 | -0.073242 | 0.16937 | 0.2243 | -0.20142 | -0.21973 | 0.018311 | 0.34332 | 107.8857 | 104.8599 | 122.2366 | 122.3648 | 0.16937 | 122.4564 | 106.6956 | -0.21973 | 122.3648 | 0.16937 | 106.6956 | 122.2366 | 122.4564 | -122.612 | -122.6578
1815.7969 | 122.4518 | -122.2687 | 0.10986 | -0.0055695 | -0.00063242 | 0.011608 | 0.022928 | 0.041216 | -0.032772 | 0.060985 | -122.2183 | 0.073242 | -122.4838 | -122.1634 | -0.16022 | -15.9576 | -14.534 | -17.8848 | 0.17395 | -122.5891 | -0.21515 | -0.036621 | 0.050354 | 0.10529 | -0.27008 | -0.32043 | 0.064087 | 0.2655 | 107.7347 | 104.3838 | 122.1085 | 122.3419 | 0.050354 | 122.4426 | 106.311 | -0.32043 | 122.3419 | 0.050354 | 106.311 | 122.1085 | 122.4426 | -122.5937 | -122.699
1817.5781 | 122.4609 | -122.2641 | 0.10529 | 0.0096895 | 0.00086298 | 0.0079767 | 0.023569 | 0.040789 | -0.036403 | 0.057567 | -122.2641 | 0.082397 | -122.5388 | -122.1817 | -0.19684 | -16.1819 | -14.74 | -18.1778 | 0.20142 | -122.5891 | -0.27466 | -0.022889 | 0 | 0.082397 | -0.30212 | -0.32501 | 0.09613 | 0.27466 | 107.5241 | 104.0863 | 122.0673 | 122.3465 | 0 | 122.4655 | 106.0822 | -0.32501 | 122.3465 | 0 | 106.0822 | 122.0673 | 122.4655 | -122.644 | -122.6944
1819.3594 | 122.493 | -122.2412 | 0.09613 | 0.0096895 | 0.00022218 | 0.01289 | 0.024423 | 0.040575 | -0.034481 | 0.06184 | -122.1542 | 0.045776 | -122.4792 | -122.0901 | -0.11444 | -16.1682 | -15.1886 | -18.2693 | 0.13733 | -122.5616 | -0.23804 | -0.050354 | 0.086975 | 0.15106 | -0.21057 | -0.32043 | 0.041199 | 0.32501 | 107.0526 | 103.9719 | 122.1268 | 122.287 | 0.086975 | 122.3785 | 106.073 | -0.32043 | 122.287 | 0.086975 | 106.073 | 122.1268 | 122.3785 | -122.5754 | -122.6578
1821.1406 | 122.406 | -122.2961 | 0.13733 | 0.017319 | 0.0032128 | 0.010754 | 0.029123 | 0.040148 | -0.034481 | 0.060558 | -122.1954 | 0.07782 | -122.5433 | -122.1405 | -0.15564 | -16.4291 | -15.2206 | -18.5669 | 0.17395 | -122.5662 | -0.24719 | -0.059509 | 0.10071 | 0.15564 | -0.29297 | -0.27008 | 0.036621 | 0.3479 | 107.0755 | 103.7292 | 122.1405 | 122.374 | 0.10071 | 122.4701 | 105.867 | -0.27008 | 122.374 | 0.10071 | 105.867 | 122.1405 | 122.4701 | -122.6807 | -122.7036
1822.8594 | 122.5342 | -122.2778 | 0.068665 | 0.0096895 | 0.0027856 | 0.016094 | 0.021005 | 0.039294 | -0.030849 | 0.060985 | -122.1634 | 0.064087 | -122.4701 | -122.1313 | -0.14191 | -16.6992 | -15.6509 | -18.8324 | 0.16022 | -122.5433 | -0.19226 | -0.004578 | 0.11444 | 0.14648 | -0.21057 | -0.2655 | 0.091552 | 0.3067 | 106.6269 | 103.4454 | 122.1359 | 122.3419 | 0.11444 | 122.438 | 105.5786 | -0.2655 | 122.3419 | 0.11444 | 105.5786 | 122.1359 | 122.438 | -122.5388 | -122.612
1824.6406 | 122.3831 | -122.2916 | 0.10986 | 0.00206 | 0.0019312 | 0.013317 | 0.030618 | 0.039721 | -0.032345 | 0.060771 | -122.1954 | 0.09613 | -122.5433 | -122.1405 | -0.17395 | -16.8732 | -15.6692 | -19.0292 | 0.17853 | -122.5754 | -0.25177 | -0.013733 | 0.09613 | 0.15106 | -0.28381 | -0.28381 | 0.068665 | 0.3479 | 106.6223 | 103.2623 | 122.1176 | 122.3877 | 0.09613 | 122.4701 | 105.4184 | -0.28381 | 122.3877 | 0.09613 | 105.4184 | 122.1176 | 122.4701 | -122.6532 | -122.6852
1826.4219 | 122.4197 | -122.287 | 0.10529 | 0.00206 | 0.001504 | 0.013744 | 0.027841 | 0.040575 | -0.031063 | 0.060131 | -122.2092 | 0.086975 | -122.5433 | -122.1405 | -0.16937 | -17.1387 | -15.9164 | -19.313 | 0.1831 | -122.58 | -0.25635 | -0.018311 | 0.07782 | 0.14648 | -0.27466 | -0.29297 | 0.077819 | 0.33417 | 106.3705 | 102.9739 | 122.1176 | 122.374 | 0.07782 | 122.4701 | 105.1483 | -0.29297 | 122.374 | 0.07782 | 105.1483 | 122.1176 | 122.4701 | -122.6486 | -122.6852
1828.2031 | 122.4243 | -122.2961 | 0.09613 | 0.00206 | 0.0036402 | 0.014599 | 0.021219 | 0.039507 | -0.03149 | 0.058208 | -122.1497 | 0.064087 | -122.4701 | -122.0947 | -0.10529 | -16.9922 | -16.1911 | -19.4412 | 0.14648 | -122.58 | -0.17395 | -0.032043 | 0.14648 | 0.20142 | -0.20142 | -0.28381 | 0.050354 | 0.32044 | 106.105 | 102.8549 | 122.1909 | 122.3602 | 0.14648 | 122.4426 | 105.304 | -0.28381 | 122.3602 | 0.14648 | 105.304 | 122.1909 | 122.4426 | -122.5662 | -122.6761
1830 | 122.4289 | -122.2961 | 0.11902 | -0.0055695 | 0.0012902 | 0.014172 | 0.022074 | 0.03908 | -0.031063 | 0.061199 | -122.1451 | 0.059509 | -122.493 | -122.0901 | -0.11444 | -17.3218 | -16.5024 | -19.7937 | 0.14648 | -122.58 | -0.19684 | -0.05951 | 0.15106 | 0.20599 | -0.23346 | -0.28381 | 0.027465 | 0.3479 | 105.7938 | 102.5024 | 122.1817 | 122.3557 | 0.15106 | 122.4426 | 104.9744 | -0.28381 | 122.3557 | 0.15106 | 104.9744 | 122.1817 | 122.4426 | -122.612 | -122.699
1831.7812 | 122.4609 | -122.2733 | 0.10529 | 0.00206 | 8.578e-06 | 0.015453 | 0.022287 | 0.038439 | -0.032131 | 0.060131 | -122.2733 | 0.10071 | -122.5525 | -122.1954 | -0.23346 | -17.6422 | -16.5436 | -20.1691 | 0.1831 | -122.6028 | -0.27924 | -0.004578 | 0 | 0.077819 | -0.33875 | -0.32959 | 0.077819 | 0.27924 | 105.7297 | 102.1042 | 122.0398 | 122.374 | 0 | 122.4564 | 104.631 | -0.32959 | 122.374 | 0 | 104.631 | 122.0398 | 122.4564 | -122.6578 | -122.7081
1833.5625 | 122.5342 | -122.2321 | 0.068665 | 0.017319 | 0.00064938 | 0.014385 | 0.026346 | 0.042925 | -0.032772 | 0.063335 | -122.2366 | 0.068665 | -122.5296 | -122.1359 | -0.17853 | -17.7063 | -17.0105 | -20.3888 | 0.13733 | -122.5845 | -0.29755 | 0 | -0.004577 | 0.096131 | -0.24719 | -0.35248 | 0.068664 | 0.29297 | 105.2216 | 101.8433 | 122.0535 | 122.3007 | -0.004577 | 122.3694 | 104.5258 | -0.35248 | 122.3007 | -0.004577 | 104.5258 | 122.0535 | 122.3694 | -122.5983 | -122.6532
1835.3438 | 122.4518 | -122.2824 | 0.10986 | 0.0096895 | 0.0038538 | 0.013317 | 0.027201 | 0.038653 | -0.031917 | 0.060985 | -122.2549 | 0.09613 | -122.5571 | -122.1863 | -0.25177 | -17.9626 | -17.0563 | -20.7459 | 0.16937 | -122.5983 | -0.27466 | -0.013733 | 0.027466 | 0.096131 | -0.36163 | -0.31586 | 0.05951 | 0.30212 | 105.2261 | 101.5366 | 122.0306 | 122.3785 | 0.027466 | 122.4518 | 104.3198 | -0.31586 | 122.3785 | 0.027466 | 104.3198 | 122.0306 | 122.4518 | -122.6669 | -122.7081
1837.0625 | 122.438 | -122.2824 | 0.10529 | -0.0055695 | 0.00086298 | 0.014599 | 0.019937 | 0.037157 | -0.030208 | 0.057994 | -122.1451 | 0.064087 | -122.4792 | -122.0673 | -0.11902 | -18.0679 | -17.5552 | -20.9198 | 0.16022 | -122.5845 | -0.19684 | -0.041199 | 0.13733 | 0.21515 | -0.22431 | -0.30212 | 0.054931 | 0.33417 | 104.7272 | 101.3626 | 122.1634 | 122.3465 | 0.13733 | 122.4426 | 104.2145 | -0.30212 | 122.3465 | 0.13733 | 104.2145 | 122.1634 | 122.4426 | -122.5845 | -122.6898
1838.8594 | 122.5479 | -122.2687 | 0.086975 | 0.0096895 | 0.001504 | 0.012676 | 0.028482 | 0.042071 | -0.034481 | 0.061199 | -122.2641 | 0.10529 | -122.5571 | -122.2183 | -0.28839 | -18.512 | -17.7475 | -21.4645 | 0.19226 | -122.5891 | -0.28839 | 0.018311 | 0.004578 | 0.050354 | -0.37537 | -0.32043 | 0.10529 | 0.29297 | 104.5212 | 100.8041 | 121.9803 | 122.374 | 0.004578 | 122.4609 | 103.7567 | -0.32043 | 122.374 | 0.004578 | 103.7567 | 121.9803 | 122.4609 | -122.644 | -122.6761
1840.6406 | 122.4884 | -122.3053 | 0.10986 | -0.0055695 | 0.00064938 | 0.016949 | 0.023355 | 0.042284 | -0.032345 | 0.058422 | -122.2595 | 0.10071 | -122.5342 | -122.2 | -0.26093 | -18.5715 | -17.807 | -21.5332 | 0.19226 | -122.6212 | -0.22888 | -0.009155 | 0.045777 | 0.10529 | -0.37079 | -0.31586 | 0.082398 | 0.27466 | 104.4983 | 100.7721 | 122.0444 | 122.406 | 0.045777 | 122.4976 | 103.7338 | -0.31586 | 122.406 | 0.045777 | 103.7338 | 122.0444 | 122.4976 | -122.644 | -122.731
1842.4219 | 122.5616 | -122.2733 | 0.086975 | 0.017319 | 8.578e-06 | 0.012249 | 0.020792 | 0.038866 | -0.031277 | 0.060985 | -122.1817 | 0.059509 | -122.4976 | -122.1359 | -0.17395 | -18.8004 | -18.4616 | -21.8536 | 0.14191 | -122.5754 | -0.22431 | -0.027466 | 0.091552 | 0.13733 | -0.26092 | -0.30212 | 0.054932 | 0.31586 | 103.8116 | 100.4196 | 122.0993 | 122.3328 | 0.091552 | 122.4152 | 103.4729 | -0.30212 | 122.3328 | 0.091552 | 103.4729 | 122.0993 | 122.4152 | -122.5845 | -122.6624
1844.1406 | 122.5296 | -122.2824 | 0.10071 | 0.00206 | 0.0019312 | 0.01524 | 0.023355 | 0.039507 | -0.031917 | 0.058422 | -122.1588 | 0.050354 | -122.525 | -122.1222 | -0.17853 | -19.0063 | -18.8095 | -22.1787 | 0.13275 | -122.5616 | -0.24261 | -0.050354 | 0.1236 | 0.16022 | -0.27924 | -0.27924 | 0.032043 | 0.36621 | 103.4729 | 100.1038 | 122.1039 | 122.3328 | 0.1236 | 122.4152 | 103.2761 | -0.27924 | 122.3328 | 0.1236 | 103.2761 | 122.1039 | 122.4152 | -122.6257 | -122.6624
1845.9062 | 122.5708 | -122.2641 | 0.091553 | 0.0096895 | -0.00020502 | 0.011608 | 0.023142 | 0.03908 | -0.032345 | 0.060131 | -122.2046 | 0.068665 | -122.5067 | -122.1405 | -0.20142 | -19.313 | -19.0384 | -22.4991 | 0.13733 | -122.58 | -0.24262 | -0.022888 | 0.059509 | 0.1236 | -0.29297 | -0.31586 | 0.045776 | 0.30212 | 103.2257 | 99.765 | 122.0627 | 122.3328 | 0.059509 | 122.4014 | 102.9511 | -0.31586 | 122.3328 | 0.059509 | 102.9511 | 122.0627 | 122.4014 | -122.5983 | -122.6715
1847.6875 | 122.5616 | -122.2733 | 0.054932 | 0.017319 | 0.0029992 | 0.016949 | 0.027414 | 0.038866 | -0.03619 | 0.060558 | -122.2824 | 0.09613 | -122.612 | -122.2549 | -0.31586 | -19.7433 | -19.2581 | -23.0026 | 0.17853 | -122.5937 | -0.33875 | 0.041198 | -0.009156 | 0.01831 | -0.37079 | -0.32044 | 0.1236 | 0.32959 | 103.0151 | 99.2706 | 121.9574 | 122.3694 | -0.009156 | 122.4518 | 102.5299 | -0.32044 | 122.3694 | -0.009156 | 102.5299 | 121.9574 | 122.4518 | -122.6669 | -122.6486
1849.3906 | 122.5067 | -122.2778 | 0.09613 | 0.0096895 | 0.0021448 | 0.0069085 | 0.021219 | 0.040362 | -0.033626 | 0.061199 | -122.1725 | 0.059509 | -122.5021 | -122.0947 | -0.17853 | -19.5786 | -19.5007 | -22.9065 | 0.12817 | -122.5845 | -0.2243 | -0.036621 | 0.10529 | 0.1831 | -0.27466 | -0.3067 | 0.032044 | 0.32959 | 102.7771 | 99.3713 | 122.0993 | 122.3373 | 0.10529 | 122.406 | 102.6993 | -0.3067 | 122.3373 | 0.10529 | 102.6993 | 122.0993 | 122.406 | -122.5983 | -122.6807
1851.1875 | 122.4426 | -122.3236 | 0.11902 | -0.013199 | 0.0010766 | 0.013317 | 0.025064 | 0.038439 | -0.033626 | 0.061199 | -122.1588 | 0.050354 | -122.5067 | -122.1085 | -0.16937 | -19.8349 | -19.8349 | -23.2269 | 0.13275 | -122.5708 | -0.18311 | -0.068665 | 0.16479 | 0.21515 | -0.28839 | -0.24719 | 0.013732 | 0.3479 | 102.4887 | 99.0967 | 122.1542 | 122.374 | 0.16479 | 122.4564 | 102.4887 | -0.24719 | 122.374 | 0.16479 | 102.4887 | 122.1542 | 122.4564 | -122.6257 | -122.6898
1852.9688 | 122.5159 | -122.2961 | 0.07782 | 0.0096895 | 0.00043578 | 0.016949 | 0.025919 | 0.038653 | -0.031704 | 0.060344 | -122.1771 | 0.041199 | -122.5388 | -122.1039 | -0.20142 | -20.0821 | -20.2194 | -23.6206 | 0.14191 | -122.5845 | -0.24261 | -0.036621 | 0.11902 | 0.19226 | -0.27924 | -0.28839 | 0.064087 | 0.36163 | 102.0767 | 98.6755 | 122.0947 | 122.3373 | 0.11902 | 122.4381 | 102.2141 | -0.28839 | 122.3373 | 0.11902 | 102.2141 | 122.0947 | 122.4381 | -122.6166 | -122.6624
1854.75 | 122.5891 | -122.2916 | 0.07782 | 0.00206 | 8.578e-06 | 0.011822 | 0.021646 | 0.038866 | -0.035122 | 0.061626 | -122.2366 | 0.068665 | -122.5204 | -122.168 | -0.25177 | -20.3796 | -20.4987 | -24.0051 | 0.15564 | -122.5616 | -0.22888 | -0.009155 | 0.054932 | 0.1236 | -0.32959 | -0.27008 | 0.07782 | 0.28381 | 101.7929 | 98.2864 | 122.0398 | 122.3602 | 0.054932 | 122.4472 | 101.9119 | -0.27008 | 122.3602 | 0.054932 | 101.9119 | 122.0398 | 122.4472 | -122.5983 | -122.6395
1856.4688 | 122.5662 | -122.2595 | 0.082397 | 0.0096895 | 0.0032128 | 0.012035 | 0.030405 | 0.041857 | -0.035976 | 0.060985 | -122.2733 | 0.10071 | -122.6028 | -122.2366 | -0.35706 | -20.7275 | -20.6451 | -24.3759 | 0.1831 | -122.5891 | -0.34332 | 0.018311 | -0.013733 | 0.022888 | -0.43945 | -0.32959 | 0.10071 | 0.32959 | 101.6144 | 97.8836 | 121.9025 | 122.3602 | -0.013733 | 122.4426 | 101.532 | -0.32959 | 122.3602 | -0.013733 | 101.532 | 121.9025 | 122.4426 | -122.6852 | -122.6715
1858.25 | 122.4518 | -122.3373 | 0.10529 | 0.00206 | -0.00041862 | 0.010113 | 0.021646 | 0.039507 | -0.034481 | 0.060558 | -122.168 | 0.059509 | -122.5296 | -122.0947 | -0.20599 | -20.723 | -20.9518 | -24.3668 | 0.14191 | -122.6028 | -0.19226 | -0.045777 | 0.16937 | 0.24261 | -0.31128 | -0.2655 | 0.036621 | 0.36163 | 101.3855 | 97.9706 | 122.1313 | 122.3969 | 0.16937 | 122.4792 | 101.6144 | -0.2655 | 122.3969 | 0.16937 | 101.6144 | 122.1313 | 122.4792 | -122.6349 | -122.7081
1860.0469 | 122.5754 | -122.287 | 0.068665 | 0.00206 | 0.0029992 | 0.014813 | 0.029764 | 0.041003 | -0.035976 | 0.060131 | -122.2641 | 0.10529 | -122.5571 | -122.2504 | -0.36163 | -21.2082 | -21.2265 | -24.9435 | 0.20142 | -122.612 | -0.27008 | 0.036621 | 0.022888 | 0.036621 | -0.4303 | -0.32501 | 0.13275 | 0.29297 | 101.0605 | 97.3434 | 121.9254 | 122.3923 | 0.022888 | 122.4884 | 101.0788 | -0.32501 | 122.3923 | 0.022888 | 101.0788 | 121.9254 | 122.4884 | -122.6257 | -122.6807
1861.7656 | 122.5388 | -122.2961 | 0.054932 | 0.0096895 | 0.0044946 | 0.010967 | 0.025064 | 0.041216 | -0.034054 | 0.060771 | -122.2458 | 0.10071 | -122.5662 | -122.1954 | -0.3067 | -21.3959 | -21.8307 | -25.383 | 0.17395 | -122.6166 | -0.27008 | 0.045776 | 0.050354 | 0.10071 | -0.36163 | -0.32043 | 0.11902 | 0.32043 | 100.4654 | 96.9131 | 121.9894 | 122.3969 | 0.050354 | 122.4701 | 100.9003 | -0.32043 | 122.3969 | 0.050354 | 100.9003 | 121.9894 | 122.4701 | -122.6212 | -122.6715
1863.5469 | 122.58 | -122.2916 | 0.068665 | 0.0096895 | 0.0019312 | 0.014385 | 0.026773 | 0.040148 | -0.031917 | 0.061199 | -122.2733 | 0.10986 | -122.5708 | -122.2366 | -0.36621 | -21.7117 | -22.2153 | -25.9598 | 0.17395 | -122.6669 | -0.27924 | 0.041198 | 0.018311 | 0.054932 | -0.43488 | -0.37537 | 0.10528 | 0.29755 | 100.0763 | 96.3318 | 121.9254 | 122.4014 | 0.018311 | 122.4655 | 100.5798 | -0.37537 | 122.4014 | 0.018311 | 100.5798 | 121.9254 | 122.4655 | -122.6395 | -122.7356
1865.3438 | 122.5754 | -122.3007 | 0.068665 | 0.0096895 | 0.0040674 | 0.014172 | 0.023569 | 0.04378 | -0.035549 | 0.063549 | -122.2595 | 0.10529 | -122.5708 | -122.2412 | -0.35248 | -22.023 | -22.6456 | -26.3031 | 0.17853 | -122.5845 | -0.27008 | 0.036621 | 0.041199 | 0.059509 | -0.42114 | -0.28381 | 0.10986 | 0.31128 | 99.6552 | 95.9976 | 121.9482 | 122.406 | 0.041199 | 122.4792 | 100.2777 | -0.28381 | 122.406 | 0.041199 | 100.2777 | 121.9482 | 122.4792 | -122.6395 | -122.6532
1867.0625 | 122.4976 | -122.3282 | 0.10986 | 0.00206 | 0.0027856 | 0.013531 | 0.024851 | 0.041216 | -0.03384 | 0.061412 | -122.2046 | 0.091553 | -122.5296 | -122.1909 | -0.29755 | -22.0688 | -22.8378 | -26.4084 | 0.15564 | -122.612 | -0.20142 | -0.01831 | 0.1236 | 0.13733 | -0.40741 | -0.28381 | 0.045777 | 0.32501 | 99.4904 | 95.9198 | 122.0306 | 122.4197 | 0.1236 | 122.4838 | 100.2594 | -0.28381 | 122.4197 | 0.1236 | 100.2594 | 122.0306 | 122.4838 | -122.6395 | -122.7219
1868.8438 | 122.4243 | -122.3328 | 0.086975 | 0.00206 | 0.0032128 | 0.012035 | 0.025278 | 0.041216 | -0.034267 | 0.060985 | -122.2275 | 0.068665 | -122.6028 | -122.1634 | -0.31128 | -22.3022 | -23.2132 | -26.7563 | 0.17853 | -122.5708 | -0.27008 | -0.01831 | 0.10529 | 0.16937 | -0.39825 | -0.23804 | 0.091553 | 0.37537 | 99.1196 | 95.5765 | 122.0215 | 122.4014 | 0.10529 | 122.5113 | 100.0305 | -0.23804 | 122.4014 | 0.10529 | 100.0305 | 122.0215 | 122.5113 | -122.6898 | -122.6578
1870.625 | 122.5296 | -122.3007 | 0.086975 | 0.0096895 | 0.0010766 | 0.015881 | 0.020151 | 0.04143 | -0.033626 | 0.062053 | -122.1817 | 0.027466 | -122.5067 | -122.1405 | -0.27924 | -22.3938 | -23.6755 | -27.0767 | 0.13733 | -122.5616 | -0.20599 | -0.059509 | 0.11902 | 0.16022 | -0.36621 | -0.26093 | 0.050354 | 0.32501 | 98.6252 | 95.224 | 122.0215 | 122.3282 | 0.11902 | 122.438 | 99.9069 | -0.26093 | 122.3282 | 0.11902 | 99.9069 | 122.0215 | 122.438 | -122.5937 | -122.6486
1872.3906 | 122.5937 | -122.2504 | 0.064087 | 0.017319 | 0.0012902 | 0.014385 | 0.020792 | 0.039294 | -0.032558 | 0.059276 | -122.2275 | 0.064087 | -122.5296 | -122.1909 | -0.32959 | -22.5677 | -23.8907 | -27.4933 | 0.13733 | -122.5983 | -0.27924 | 0 | 0.022888 | 0.059509 | -0.39368 | -0.3479 | 0.073242 | 0.30212 | 98.3597 | 94.7571 | 121.9208 | 122.3145 | 0.022888 | 122.3877 | 99.6826 | -0.3479 | 122.3145 | 0.022888 | 99.6826 | 121.9208 | 122.3877 | -122.5937 | -122.6624
1874.1719 | 122.5296 | -122.287 | 0.068665 | 0.0096895 | 0.00064938 | 0.012035 | 0.02656 | 0.041003 | -0.034267 | 0.062267 | -122.168 | 0.054932 | -122.5662 | -122.1313 | -0.28381 | -22.8333 | -24.3896 | -27.9465 | 0.12817 | -122.5433 | -0.27924 | -0.013733 | 0.11902 | 0.15564 | -0.35248 | -0.25635 | 0.059509 | 0.39825 | 97.8973 | 94.3405 | 122.0032 | 122.3419 | 0.11902 | 122.4152 | 99.4537 | -0.25635 | 122.3419 | 0.11902 | 99.4537 | 122.0032 | 122.4152 | -122.6349 | -122.612
1875.8906 | 122.6028 | -122.2916 | 0.082397 | 0.0096895 | 0.0012902 | 0.014385 | 0.021433 | 0.042498 | -0.032345 | 0.05949 | -122.2275 | 0.059509 | -122.5159 | -122.1863 | -0.33875 | -22.8836 | -24.5407 | -28.2623 | 0.15564 | -122.612 | -0.2243 | -0.022888 | 0.064087 | 0.10529 | -0.42114 | -0.32043 | 0.073243 | 0.28839 | 97.7509 | 94.0292 | 121.9528 | 122.3511 | 0.064087 | 122.4472 | 99.408 | -0.32043 | 122.3511 | 0.064087 | 99.408 | 121.9528 | 122.4472 | -122.5983 | -122.6944
1877.6719 | 122.4655 | -122.3328 | 0.11444 | 0.00206 | 0.00064938 | 0.014813 | 0.028055 | 0.040362 | -0.034481 | 0.061412 | -122.2137 | 0.082397 | -122.5662 | -122.1817 | -0.36621 | -23.172 | -24.8611 | -28.6514 | 0.16022 | -122.5983 | -0.23346 | -0.032044 | 0.11902 | 0.15106 | -0.48065 | -0.2655 | 0.045776 | 0.35248 | 97.4716 | 93.6813 | 121.9666 | 122.4152 | 0.11902 | 122.493 | 99.1608 | -0.2655 | 122.4152 | 0.11902 | 99.1608 | 121.9666 | 122.493 | -122.6807 | -122.7127
1879.4531 | 122.5433 | -122.2778 | 0.082397 | 0.0096895 | 0.0051356 | 0.010754 | 0.026132 | 0.041644 | -0.031277 | 0.061412 | -122.1771 | 0.054932 | -122.5342 | -122.1222 | -0.30212 | -23.2178 | -25.3052 | -28.8345 | 0.14648 | -122.5891 | -0.25635 | -0.027465 | 0.10071 | 0.15564 | -0.38452 | -0.31128 | 0.064087 | 0.35706 | 96.9727 | 93.4433 | 121.9757 | 122.3328 | 0.10071 | 122.4243 | 99.0601 | -0.31128 | 122.3328 | 0.10071 | 99.0601 | 121.9757 | 122.4243 | -122.6166 | -122.6715
1881.25 | 122.612 | -122.3099 | 0.073242 | -0.0055695 | 0.0047082 | 0.015026 | 0.020151 | 0.040362 | -0.029354 | 0.061199 | -122.2229 | 0.050354 | -122.5296 | -122.1954 | -0.36163 | -23.3505 | -25.4608 | -29.1 | 0.14648 | -122.6349 | -0.21973 | -0.022888 | 0.086975 | 0.11444 | -0.43488 | -0.32501 | 0.073242 | 0.3067 | 96.8491 | 93.2098 | 121.9482 | 122.3602 | 0.086975 | 122.4564 | 98.9594 | -0.32501 | 122.3602 | 0.086975 | 98.9594 | 121.9482 | 122.4564 | -122.6028 | -122.7081
1883.0312 | 122.4335 | -122.3557 | 0.1236 | 0.017319 | 0.0047082 | 0.015881 | 0.028696 | 0.041216 | -0.036403 | 0.06184 | -122.2275 | 0.10071 | -122.6212 | -122.1771 | -0.37537 | -23.5748 | -25.6851 | -29.4113 | 0.15564 | -122.5662 | -0.2655 | -0.022888 | 0.12817 | 0.17853 | -0.49896 | -0.21057 | 0.032044 | 0.39368 | 96.6705 | 92.9443 | 121.9803 | 122.4564 | 0.12817 | 122.5113 | 98.7808 | -0.21057 | 122.4564 | 0.12817 | 98.7808 | 121.9803 | 122.5113 | -122.7448 | -122.6898
1884.8125 | 122.525 | -122.3007 | 0.068665 | 0.0096895 | 0.00064938 | 0.012676 | 0.024851 | 0.042284 | -0.032985 | 0.060344 | -122.168 | 0.032043 | -122.5342 | -122.1313 | -0.33875 | -23.7717 | -26.2344 | -29.686 | 0.13733 | -122.5845 | -0.23346 | -0.036622 | 0.13275 | 0.16937 | -0.40741 | -0.28381 | 0.068664 | 0.36621 | 96.0663 | 92.6147 | 121.962 | 122.3328 | 0.13275 | 122.438 | 98.5291 | -0.28381 | 122.3328 | 0.13275 | 98.5291 | 121.962 | 122.438 | -122.6028 | -122.6532
1886.6094 | 122.5983 | -122.2687 | 0.059509 | 0.0096895 | 0.0021448 | 0.016949 | 0.026773 | 0.040362 | -0.032772 | 0.060771 | -122.2778 | 0.086975 | -122.5845 | -122.2366 | -0.45319 | -24.0829 | -26.2848 | -30.0659 | 0.17395 | -122.6532 | -0.31586 | 0.027466 | -0.009155 | 0.032044 | -0.5127 | -0.38452 | 0.11444 | 0.3067 | 95.9839 | 92.2028 | 121.8155 | 122.3557 | -0.009155 | 122.4426 | 98.1857 | -0.38452 | 122.3557 | -0.009155 | 98.1857 | 121.8155 | 122.4426 | -122.644 | -122.7127
1888.3281 | 122.5571 | -122.3099 | 0.073242 | -0.0055695 | 0.0040674 | 0.016094 | 0.023783 | 0.041216 | -0.033199 | 0.065044 | -122.2229 | 0.059509 | -122.5525 | -122.1405 | -0.36163 | -24.2157 | -26.8112 | -30.3177 | 0.13733 | -122.612 | -0.24262 | -0.013733 | 0.086975 | 0.16937 | -0.43488 | -0.30212 | 0.064087 | 0.32959 | 95.4987 | 91.9922 | 121.9482 | 122.3694 | 0.086975 | 122.4472 | 98.0942 | -0.30212 | 122.3694 | 0.086975 | 98.0942 | 121.9482 | 122.4472 | -122.6257 | -122.6852
1890.1094 | 122.5525 | -122.3373 | 0.10071 | 0.00206 | 0.002572 | 0.015026 | 0.022287 | 0.040362 | -0.031917 | 0.062694 | -122.1725 | 0.050354 | -122.5204 | -122.1405 | -0.37079 | -24.3347 | -27.063 | -30.4916 | 0.1236 | -122.6028 | -0.18311 | -0.050354 | 0.16479 | 0.19684 | -0.4715 | -0.2655 | 0.022888 | 0.3479 | 95.2744 | 91.8457 | 121.9666 | 122.3877 | 0.16479 | 122.4609 | 98.0026 | -0.2655 | 122.3877 | 0.16479 | 98.0026 | 121.9666 | 122.4609 | -122.6212 | -122.7036
1891.9062 | 122.5067 | -122.3099 | 0.10986 | 0.0096895 | 0.00086298 | 0.018444 | 0.027414 | 0.038653 | -0.033413 | 0.061412 | -122.3053 | 0.10071 | -122.5983 | -122.2321 | -0.46692 | -24.6185 | -27.0447 | -30.8212 | 0.16022 | -122.6669 | -0.28839 | -0.009155 | 0.004577 | 0.077819 | -0.57678 | -0.35706 | 0.050354 | 0.29297 | 95.2652 | 91.4886 | 121.843 | 122.4106 | 0.004577 | 122.4701 | 97.6913 | -0.35706 | 122.4106 | 0.004577 | 97.6913 | 121.843 | 122.4701 | -122.7081 | -122.7768
1893.625 | 122.58 | -122.3099 | 0.086975 | 0.0096895 | 0.0019312 | 0.010754 | 0.019937 | 0.037157 | -0.031917 | 0.063976 | -122.2504 | 0.064087 | -122.5616 | -122.168 | -0.40283 | -24.7742 | -27.562 | -31.0867 | 0.13733 | -122.612 | -0.25177 | -0.022888 | 0.059509 | 0.14191 | -0.48981 | -0.30212 | 0.050354 | 0.31128 | 94.7479 | 91.2231 | 121.907 | 122.374 | 0.059509 | 122.4472 | 97.5357 | -0.30212 | 122.374 | 0.059509 | 97.5357 | 121.907 | 122.4472 | -122.6486 | -122.699
1895.4062 | 122.5525 | -122.3145 | 0.073242 | 0.0096895 | 0.0019312 | 0.017162 | 0.024637 | 0.040148 | -0.034694 | 0.059276 | -122.1634 | 0.050354 | -122.5388 | -122.1588 | -0.38452 | -24.9939 | -28.0106 | -31.3843 | 0.13733 | -122.58 | -0.2243 | -0.022888 | 0.15106 | 0.15564 | -0.45776 | -0.2655 | 0.064087 | 0.37537 | 94.3039 | 90.9302 | 121.9299 | 122.3648 | 0.15106 | 122.4518 | 97.3206 | -0.2655 | 122.3648 | 0.15106 | 97.3206 | 121.9299 | 122.4518 | -122.612 | -122.6532
1897.1875 | 122.5021 | -122.3373 | 0.10529 | 0.017319 | 0.0021448 | 0.013317 | 0.023783 | 0.039721 | -0.032345 | 0.059276 | -122.2092 | 0.054932 | -122.5479 | -122.1771 | -0.43488 | -25.2182 | -28.1296 | -31.636 | 0.14191 | -122.6166 | -0.21057 | -0.050354 | 0.12817 | 0.16022 | -0.54016 | -0.27924 | 0.036621 | 0.33875 | 94.2078 | 90.7013 | 121.9025 | 122.3923 | 0.12817 | 122.4792 | 97.1191 | -0.27924 | 122.3923 | 0.12817 | 97.1191 | 121.9025 | 122.4792 | -122.6532 | -122.7219
1898.9062 | 122.5571 | -122.3557 | 0.091553 | 0.00206 | 0.001504 | 0.015453 | 0.023783 | 0.039507 | -0.031704 | 0.063762 | -122.1725 | 0.027466 | -122.5525 | -122.1542 | -0.42114 | -25.4471 | -28.6194 | -31.9107 | 0.13275 | -122.6074 | -0.19684 | -0.064087 | 0.18311 | 0.20142 | -0.5127 | -0.25177 | 0.041198 | 0.37994 | 93.7363 | 90.4449 | 121.9345 | 122.3831 | 0.18311 | 122.4884 | 96.9086 | -0.25177 | 122.3831 | 0.18311 | 96.9086 | 121.9345 | 122.4884 | -122.644 | -122.699
1900.6875 | 122.5067 | -122.3282 | 0.091553 | 0.00206 | 0.0019312 | 0.013531 | 0.026773 | 0.038866 | -0.037472 | 0.060131 | -122.287 | 0.09613 | -122.5754 | -122.2412 | -0.53558 | -25.6302 | -28.5782 | -32.2357 | 0.1831 | -122.6303 | -0.24719 | 0.004577 | 0.041199 | 0.086975 | -0.62714 | -0.30212 | 0.091552 | 0.28839 | 93.75 | 90.0925 | 121.7926 | 122.4243 | 0.041199 | 122.5113 | 96.698 | -0.30212 | 122.4243 | 0.041199 | 96.698 | 121.7926 | 122.5113 | -122.6669 | -122.7219
1902.4688 | 122.5754 | -122.3236 | 0.068665 | 0.00206 | 0.0027856 | 0.011822 | 0.023996 | 0.040362 | -0.033626 | 0.062267 | -122.1817 | 0.045776 | -122.5571 | -122.1359 | -0.45776 | -25.7126 | -29.2099 | -32.4829 | 0.1236 | -122.5937 | -0.23346 | -0.022889 | 0.14191 | 0.18768 | -0.52643 | -0.27008 | 0.054931 | 0.37537 | 93.1137 | 89.8407 | 121.8658 | 122.3694 | 0.14191 | 122.4472 | 96.611 | -0.27008 | 122.3694 | 0.14191 | 96.611 | 121.8658 | 122.4472 | -122.6257 | -122.6624
1904.1875 | 122.5662 | -122.3145 | 0.07782 | 0.017319 | 0.0072718 | 0.01289 | 0.025064 | 0.040575 | -0.032985 | 0.061412 | -122.1771 | 0.050354 | -122.5296 | -122.1542 | -0.45319 | -26.0056 | -29.6356 | -32.8949 | 0.14191 | -122.6166 | -0.21515 | -0.027466 | 0.13733 | 0.16022 | -0.53101 | -0.30212 | 0.064087 | 0.35248 | 92.6788 | 89.4196 | 121.8613 | 122.3648 | 0.13733 | 122.4564 | 96.3089 | -0.30212 | 122.3648 | 0.13733 | 96.3089 | 121.8613 | 122.4564 | -122.6074 | -122.6944
1905.9688 | 122.5891 | -122.3236 | 0.07782 | -0.0055695 | 0.0027856 | 0.016735 | 0.020365 | 0.039294 | -0.034054 | 0.059917 | -122.2 | 0.059509 | -122.5159 | -122.1954 | -0.48065 | -26.2848 | -29.9561 | -33.2977 | 0.15106 | -122.612 | -0.19226 | -0.018311 | 0.1236 | 0.12817 | -0.55847 | -0.28839 | 0.073242 | 0.31586 | 92.3676 | 89.0259 | 121.843 | 122.3831 | 0.1236 | 122.4747 | 96.0388 | -0.28839 | 122.3831 | 0.1236 | 96.0388 | 121.843 | 122.4747 | -122.5937 | -122.6898
1907.75 | 122.612 | -122.3053 | 0.073242 | 0.00206 | 0.0062036 | 0.016521 | 0.02955 | 0.04378 | -0.034054 | 0.061412 | -122.2733 | 0.10071 | -122.6257 | -122.2549 | -0.57678 | -26.6144 | -30.2078 | -33.7738 | 0.16022 | -122.6257 | -0.32043 | 0.027466 | 0.032044 | 0.050354 | -0.65002 | -0.32043 | 0.086975 | 0.35248 | 92.0975 | 88.5315 | 121.7285 | 122.406 | 0.032044 | 122.4655 | 95.6909 | -0.32043 | 122.406 | 0.032044 | 95.6909 | 121.7285 | 122.4655 | -122.699 | -122.699
1909.4688 | 122.5479 | -122.3328 | 0.07782 | 0.0096895 | 0.0047082 | 0.018017 | 0.02421 | 0.039721 | -0.032345 | 0.058635 | -122.1542 | 0.032043 | -122.525 | -122.1451 | -0.48981 | -26.7334 | -30.748 | -33.9798 | 0.12817 | -122.5983 | -0.19226 | -0.045777 | 0.17853 | 0.18768 | -0.56763 | -0.2655 | 0.050354 | 0.37079 | 91.5848 | 88.353 | 121.843 | 122.3648 | 0.17853 | 122.4609 | 95.5994 | -0.2655 | 122.3648 | 0.17853 | 95.5994 | 121.843 | 122.4609 | -122.6028 | -122.6761
1911.2656 | 122.6166 | -122.319 | 0.07782 | 0.0096895 | 0.0047082 | 0.016949 | 0.02186 | 0.038866 | -0.031063 | 0.059917 | -122.2458 | 0.059509 | -122.5525 | -122.2137 | -0.54016 | -27.0309 | -30.9769 | -34.3872 | 0.15564 | -122.6257 | -0.23346 | -0.018311 | 0.073242 | 0.10529 | -0.61798 | -0.3067 | 0.07782 | 0.3067 | 91.3422 | 87.9318 | 121.7789 | 122.3785 | 0.073242 | 122.4747 | 95.2881 | -0.3067 | 122.3785 | 0.073242 | 95.2881 | 121.7789 | 122.4747 | -122.6303 | -122.7036
1912.9688 | 122.4747 | -122.3557 | 0.11444 | 0.017319 | 0.0044946 | 0.015881 | 0.027841 | 0.040148 | -0.035763 | 0.060985 | -122.2275 | 0.10071 | -122.6257 | -122.2 | -0.58136 | -27.2278 | -31.1462 | -34.6619 | 0.17395 | -122.6395 | -0.27008 | -0.013733 | 0.12817 | 0.15564 | -0.6958 | -0.28381 | 0.059509 | 0.39825 | 91.2094 | 87.6938 | 121.7743 | 122.4564 | 0.12817 | 122.5296 | 95.1279 | -0.28381 | 122.4564 | 0.12817 | 95.1279 | 121.7743 | 122.5296 | -122.7402 | -122.7539
1914.75 | 122.6074 | -122.2961 | 0.082397 | 0.00206 | 0.00599 | 0.016521 | 0.02656 | 0.041644 | -0.030208 | 0.060131 | -122.287 | 0.091553 | -122.6166 | -122.2641 | -0.62714 | -27.4658 | -31.5079 | -35.1151 | 0.17853 | -122.644 | -0.32043 | 0.009156 | 0.009156 | 0.032044 | -0.70953 | -0.3479 | 0.096131 | 0.32959 | 90.7883 | 87.1811 | 121.669 | 122.3877 | 0.009156 | 122.4747 | 94.8303 | -0.3479 | 122.3877 | 0.009156 | 94.8303 | 121.669 | 122.4747 | -122.699 | -122.7264
1916.5469 | 122.5616 | -122.3282 | 0.064087 | 0.00206 | 0.0038538 | 0.020367 | 0.024851 | 0.043139 | -0.033626 | 0.06248 | -122.1817 | 0.032043 | -122.5708 | -122.1634 | -0.54016 | -27.5345 | -31.9839 | -35.289 | 0.13275 | -122.5937 | -0.24262 | -0.032044 | 0.14648 | 0.16479 | -0.60425 | -0.2655 | 0.068664 | 0.3891 | 90.3442 | 87.0392 | 121.788 | 122.3602 | 0.14648 | 122.4609 | 94.7937 | -0.2655 | 122.3602 | 0.14648 | 94.7937 | 121.788 | 122.4609 | -122.6349 | -122.6578
1918.2656 | 122.5937 | -122.3282 | 0.073242 | 0.00206 | 0.00599 | 0.016735 | 0.023355 | 0.038653 | -0.030208 | 0.059062 | -122.2412 | 0.045776 | -122.5571 | -122.2137 | -0.58594 | -27.8275 | -32.2311 | -35.6735 | 0.11444 | -122.6486 | -0.22888 | -0.027466 | 0.086975 | 0.11444 | -0.65918 | -0.32044 | 0.041199 | 0.31586 | 90.097 | 86.6547 | 121.7422 | 122.374 | 0.086975 | 122.4426 | 94.5007 | -0.32044 | 122.374 | 0.086975 | 94.5007 | 121.7422 | 122.4426 | -122.6303 | -122.7219
1920.0469 | 122.5479 | -122.319 | 0.10986 | 0.00206 | 0.0032128 | 0.01524 | 0.021433 | 0.035876 | -0.030208 | 0.062267 | -122.1863 | 0.054932 | -122.5708 | -122.1542 | -0.55389 | -27.9282 | -32.5974 | -35.9024 | 0.12817 | -122.6395 | -0.25177 | -0.054931 | 0.13275 | 0.16479 | -0.66376 | -0.32043 | 0.018311 | 0.38452 | 89.7217 | 86.4166 | 121.7651 | 122.374 | 0.13275 | 122.4472 | 94.3909 | -0.32043 | 122.374 | 0.13275 | 94.3909 | 121.7651 | 122.4472 | -122.6807 | -122.7493
1921.8281 | 122.6212 | -122.3282 | 0.064087 | 0.0096895 | 0.0053492 | 0.01759 | 0.028269 | 0.038439 | -0.034054 | 0.06248 | -122.2916 | 0.10529 | -122.612 | -122.2778 | -0.71869 | -28.3859 | -32.8903 | -36.5524 | 0.16022 | -122.6166 | -0.28381 | 0.041199 | 0.036621 | 0.050354 | -0.78278 | -0.28839 | 0.09613 | 0.32043 | 89.4379 | 85.7758 | 121.6095 | 122.4335 | 0.036621 | 122.4884 | 93.9423 | -0.28839 | 122.4335 | 0.036621 | 93.9423 | 121.6095 | 122.4884 | -122.6761 | -122.6807
1923.5469 | 122.6028 | -122.3419 | 0.086975 | -0.0055695 | 0.0027856 | 0.014813 | 0.01951 | 0.039935 | -0.032131 | 0.059703 | -122.2229 | 0.059509 | -122.5571 | -122.1817 | -0.61798 | -28.4958 | -33.3664 | -36.7493 | 0.13275 | -122.6395 | -0.21515 | -0.027466 | 0.11902 | 0.16022 | -0.70496 | -0.29755 | 0.045776 | 0.33417 | 88.9755 | 85.5927 | 121.7239 | 122.4014 | 0.11902 | 122.4747 | 93.8461 | -0.29755 | 122.4014 | 0.11902 | 93.8461 | 121.7239 | 122.4747 | -122.644 | -122.7264
1925.3281 | 122.5937 | -122.3145 | 0.054932 | 0.0096895 | 0.002572 | 0.014813 | 0.026987 | 0.041216 | -0.035335 | 0.061199 | -122.2412 | 0.091553 | -122.6212 | -122.2321 | -0.67291 | -28.7659 | -33.6731 | -37.1246 | 0.14648 | -122.6395 | -0.3067 | 0.036621 | 0.073242 | 0.082397 | -0.72784 | -0.32501 | 0.091552 | 0.37994 | 88.6414 | 85.1898 | 121.6415 | 122.406 | 0.073242 | 122.4609 | 93.5486 | -0.32501 | 122.406 | 0.073242 | 93.5486 | 121.6415 | 122.4609 | -122.6761 | -122.6944
1927.125 | 122.5204 | -122.3602 | 0.11902 | 0.00206 | 0.0072718 | 0.017162 | 0.02656 | 0.039721 | -0.034908 | 0.058849 | -122.2641 | 0.086975 | -122.6212 | -122.2595 | -0.737 | -28.9536 | -33.9203 | -37.5412 | 0.16937 | -122.6303 | -0.26093 | -0.032044 | 0.09613 | 0.10071 | -0.85602 | -0.27008 | 0.050354 | 0.35706 | 88.4399 | 84.819 | 121.6232 | 122.4472 | 0.09613 | 122.5296 | 93.4067 | -0.27008 | 122.4472 | 0.09613 | 93.4067 | 121.6232 | 122.5296 | -122.7402 | -122.7493
1928.8438 | 122.6303 | -122.3282 | 0.064087 | -0.0055695 | 0.0051356 | 0.020153 | 0.021433 | 0.040148 | -0.032558 | 0.061412 | -122.2321 | 0.059509 | -122.5296 | -122.2275 | -0.67749 | -29.1046 | -34.4147 | -37.9211 | 0.13733 | -122.6624 | -0.20142 | -0.004578 | 0.09613 | 0.10071 | -0.74158 | -0.33417 | 0.073242 | 0.29755 | 87.9135 | 84.407 | 121.6507 | 122.3877 | 0.09613 | 122.4655 | 93.2236 | -0.33417 | 122.3877 | 0.09613 | 93.2236 | 121.6507 | 122.4655 | -122.5937 | -122.7264
1930.625 | 122.4884 | -122.3328 | 0.10986 | 0.0096895 | 0.0047082 | 0.019939 | 0.026132 | 0.040789 | -0.033626 | 0.061199 | -122.2412 | 0.082397 | -122.644 | -122.2275 | -0.71869 | -29.2877 | -34.5428 | -38.1775 | 0.17853 | -122.6486 | -0.31128 | -0.027466 | 0.091553 | 0.10529 | -0.82855 | -0.31586 | 0.068665 | 0.40283 | 87.7899 | 84.1553 | 121.6141 | 122.4152 | 0.091553 | 122.5113 | 93.045 | -0.31586 | 122.4152 | 0.091553 | 93.045 | 121.6141 | 122.5113 | -122.7539 | -122.7585
1932.3594 | 122.6028 | -122.3236 | 0.059509 | 0.00206 | 0.0091944 | 0.016308 | 0.026132 | 0.042498 | -0.033199 | 0.060985 | -122.2733 | 0.064087 | -122.6074 | -122.2504 | -0.7782 | -29.5761 | -34.9869 | -38.5986 | 0.17395 | -122.6349 | -0.28381 | 0.004578 | 0.050354 | 0.073242 | -0.83771 | -0.31128 | 0.11444 | 0.33417 | 87.3367 | 83.725 | 121.5454 | 122.3877 | 0.050354 | 122.4976 | 92.7475 | -0.31128 | 122.3877 | 0.050354 | 92.7475 | 121.5454 | 122.4976 | -122.6669 | -122.6944
1934.1406 | 122.5571 | -122.3557 | 0.10529 | 0.0096895 | 0.00599 | 0.015026 | 0.023996 | 0.038653 | -0.032558 | 0.063335 | -122.3053 | 0.10986 | -122.6349 | -122.2961 | -0.79651 | -29.8141 | -35.2432 | -38.9145 | 0.17853 | -122.6624 | -0.27924 | 0.004577 | 0.050354 | 0.059509 | -0.9018 | -0.3067 | 0.073242 | 0.32959 | 87.1124 | 83.4412 | 121.5591 | 122.4655 | 0.050354 | 122.5342 | 92.5415 | -0.3067 | 122.4655 | 0.050354 | 92.5415 | 121.5591 | 122.5342 | -122.7402 | -122.7676
1935.9062 | 122.5388 | -122.3785 | 0.10529 | 0.00206 | 0.0023584 | 0.018871 | 0.023142 | 0.039507 | -0.032345 | 0.06184 | -122.2275 | 0.064087 | -122.5937 | -122.2641 | -0.78278 | -30.0888 | -35.7468 | -39.2715 | 0.15106 | -122.6898 | -0.21515 | -0.041199 | 0.15106 | 0.11444 | -0.88806 | -0.31128 | 0.045776 | 0.36621 | 86.6318 | 83.107 | 121.5958 | 122.4426 | 0.15106 | 122.5296 | 92.2897 | -0.31128 | 122.4426 | 0.15106 | 92.2897 | 121.5958 | 122.5296 | -122.699 | -122.7951
1937.6406 | 122.5983 | -122.3236 | 0.082397 | 0.00206 | 0.0079126 | 0.018444 | 0.026987 | 0.041644 | -0.033626 | 0.06248 | -122.3007 | 0.10529 | -122.644 | -122.2961 | -0.84686 | -30.3726 | -36.0855 | -39.6652 | 0.17853 | -122.6898 | -0.32044 | 0.022889 | 0.022888 | 0.027465 | -0.92926 | -0.36621 | 0.096131 | 0.34332 | 86.2381 | 82.6584 | 121.4767 | 122.4289 | 0.022888 | 122.5021 | 91.951 | -0.36621 | 122.4289 | 0.022888 | 91.951 | 121.4767 | 122.5021 | -122.7264 | -122.7722
1939.4375 | 122.5479 | -122.3694 | 0.091553 | 0.017319 | 0.0034266 | 0.016735 | 0.021219 | 0.040362 | -0.034694 | 0.063335 | -122.2961 | 0.10071 | -122.6486 | -122.2916 | -0.85144 | -30.5191 | -36.351 | -39.9033 | 0.1831 | -122.6486 | -0.27924 | 0.009155 | 0.073242 | 0.07782 | -0.94299 | -0.27924 | 0.091552 | 0.35248 | 86.0184 | 82.4661 | 121.5179 | 122.4701 | 0.073242 | 122.5525 | 91.8503 | -0.27924 | 122.4701 | 0.073242 | 91.8503 | 121.5179 | 122.5525 | -122.7402 | -122.7402
1941.1719 | 122.5388 | -122.3877 | 0.10529 | -0.0055695 | 0.0036402 | 0.01823 | 0.02421 | 0.039507 | -0.032985 | 0.060771 | -122.2549 | 0.07782 | -122.6028 | -122.2778 | -0.85144 | -30.6564 | -36.7264 | -40.1596 | 0.16479 | -122.6578 | -0.21515 | -0.027466 | 0.13275 | 0.10986 | -0.95673 | -0.27008 | 0.059509 | 0.3479 | 85.6613 | 82.2281 | 121.5363 | 122.4655 | 0.13275 | 122.5525 | 91.7313 | -0.27008 | 122.4655 | 0.13275 | 91.7313 | 121.5363 | 122.5525 | -122.7081 | -122.7631
1942.9688 | 122.6303 | -122.3419 | 0.09613 | 0.00206 | 0.0057764 | 0.014599 | 0.021646 | 0.039294 | -0.03149 | 0.060771 | -122.2321 | 0.068665 | -122.5342 | -122.2229 | -0.79193 | -30.8395 | -37.2482 | -40.4388 | 0.14191 | -122.6578 | -0.19226 | -0.027465 | 0.10986 | 0.11902 | -0.88806 | -0.31586 | 0.045777 | 0.30212 | 85.0937 | 81.9031 | 121.55 | 122.4106 | 0.10986 | 122.4838 | 91.5024 | -0.31586 | 122.4106 | 0.10986 | 91.5024 | 121.55 | 122.4838 | -122.6303 | -122.7539
1944.6875 | 122.6166 | -122.3282 | 0.068665 | 0.017319 | 0.00599 | 0.015026 | 0.027414 | 0.042284 | -0.032131 | 0.062053 | -122.2824 | 0.09613 | -122.5937 | -122.2961 | -0.91095 | -31.16 | -37.468 | -40.8966 | 0.17395 | -122.6578 | -0.2655 | 0.027465 | 0.045776 | 0.032043 | -0.97962 | -0.32959 | 0.10528 | 0.31128 | 84.8602 | 81.4316 | 121.4172 | 122.4243 | 0.045776 | 122.5021 | 91.1682 | -0.32959 | 122.4243 | 0.045776 | 91.1682 | 121.4172 | 122.5021 | -122.6624 | -122.7264
1946.4688 | 122.5479 | -122.3694 | 0.11444 | 0.0096895 | 0.00599 | 0.016735 | 0.026346 | 0.04143 | -0.033199 | 0.063121 | -122.2687 | 0.07782 | -122.6532 | -122.2824 | -0.91553 | -31.3751 | -37.8708 | -41.2399 | 0.16937 | -122.6624 | -0.28381 | -0.036621 | 0.10071 | 0.086975 | -1.03 | -0.29297 | 0.054932 | 0.38452 | 84.4986 | 81.1295 | 121.4539 | 122.4472 | 0.10071 | 122.5388 | 90.9943 | -0.29297 | 122.4472 | 0.10071 | 90.9943 | 121.4539 | 122.5388 | -122.7676 | -122.7768
1948.1875 | 122.5388 | -122.3648 | 0.10529 | 0.0096895 | 0.0036402 | 0.018017 | 0.023142 | 0.039507 | -0.030636 | 0.062694 | -122.2458 | 0.082397 | -122.6074 | -122.2641 | -0.88348 | -31.485 | -38.063 | -41.4276 | 0.16479 | -122.6715 | -0.24262 | -0.022889 | 0.11902 | 0.10071 | -0.98877 | -0.3067 | 0.059509 | 0.36163 | 84.3018 | 80.9372 | 121.4813 | 122.4472 | 0.11902 | 122.5296 | 90.8798 | -0.3067 | 122.4472 | 0.11902 | 90.8798 | 121.4813 | 122.5296 | -122.7127 | -122.7768
1949.9688 | 122.5021 | -122.374 | 0.09613 | 0.00206 | 0.004281 | 0.016949 | 0.019296 | 0.038866 | -0.031917 | 0.063121 | -122.1588 | 0.050354 | -122.5845 | -122.1588 | -0.81024 | -31.5308 | -38.5529 | -41.5329 | 0.1236 | -122.6532 | -0.21057 | -0.045776 | 0.21515 | 0.21515 | -0.90637 | -0.27924 | 0.027466 | 0.42572 | 83.8211 | 80.8411 | 121.5637 | 122.4243 | 0.21515 | 122.4976 | 90.8432 | -0.27924 | 122.4243 | 0.21515 | 90.8432 | 121.5637 | 122.4976 | -122.6807 | -122.7493
1951.75 | 122.4976 | -122.3969 | 0.10986 | -0.0055695 | 0.0051356 | 0.017803 | 0.023142 | 0.038439 | -0.030636 | 0.062694 | -122.2 | 0.050354 | -122.5754 | -122.2092 | -0.86517 | -31.8329 | -38.9282 | -41.9907 | 0.14191 | -122.6761 | -0.17853 | -0.059509 | 0.19684 | 0.18768 | -0.97504 | -0.27923 | 0.032044 | 0.37537 | 83.4686 | 80.4062 | 121.5317 | 122.4472 | 0.19684 | 122.5388 | 90.564 | -0.27923 | 122.4472 | 0.19684 | 90.564 | 121.5317 | 122.5388 | -122.6852 | -122.7859
1953.5156 | 122.5479 | -122.3831 | 0.10529 | 0.0096895 | 0.007699 | 0.01759 | 0.023783 | 0.041857 | -0.031917 | 0.062267 | -122.2275 | 0.064087 | -122.6028 | -122.2137 | -0.92926 | -32.1121 | -39.267 | -42.3889 | 0.16022 | -122.6578 | -0.21973 | -0.041199 | 0.15564 | 0.16937 | -1.0345 | -0.27466 | 0.054931 | 0.37537 | 83.1162 | 79.9942 | 121.4539 | 122.4472 | 0.15564 | 122.5433 | 90.271 | -0.27466 | 122.4472 | 0.15564 | 90.271 | 121.4539 | 122.5433 | -122.7081 | -122.7631
1955.2969 | 122.525 | -122.3969 | 0.10529 | 0.0096895 | 0.0062036 | 0.016094 | 0.02421 | 0.039721 | -0.032131 | 0.061199 | -122.1954 | 0.045776 | -122.5845 | -122.1863 | -0.91553 | -32.2311 | -39.6194 | -42.6544 | 0.15564 | -122.6624 | -0.18768 | -0.05951 | 0.20142 | 0.21057 | -1.0208 | -0.2655 | 0.050354 | 0.3891 | 82.7774 | 79.7424 | 121.4813 | 122.4426 | 0.20142 | 122.5525 | 90.1657 | -0.2655 | 122.4426 | 0.20142 | 90.1657 | 121.4813 | 122.5525 | -122.6898 | -122.7676
1957.0781 | 122.5113 | -122.3877 | 0.10986 | -0.0055695 | 0.0066308 | 0.018871 | 0.023996 | 0.039294 | -0.032345 | 0.057353 | -122.1863 | 0.050354 | -122.5754 | -122.1725 | -0.9201 | -32.4326 | -40.1093 | -43.0161 | 0.13733 | -122.6486 | -0.18768 | -0.059509 | 0.20142 | 0.21515 | -1.03 | -0.26093 | 0.027466 | 0.3891 | 82.2784 | 79.3716 | 121.4676 | 122.438 | 0.20142 | 122.525 | 89.9551 | -0.26093 | 122.438 | 0.20142 | 89.9551 | 121.4676 | 122.525 | -122.6852 | -122.7585
1958.8438 | 122.6349 | -122.374 | 0.073242 | 0.0096895 | 0.0068444 | 0.01759 | 0.021433 | 0.039507 | -0.030208 | 0.061626 | -122.2412 | 0.050354 | -122.5937 | -122.2183 | -0.97504 | -32.7347 | -40.535 | -43.4189 | 0.13275 | -122.6669 | -0.21973 | -0.022888 | 0.13275 | 0.15564 | -1.0483 | -0.29297 | 0.059509 | 0.35248 | 81.839 | 78.9551 | 121.3989 | 122.4243 | 0.13275 | 122.5067 | 89.6393 | -0.29297 | 122.4243 | 0.13275 | 89.6393 | 121.3989 | 122.5067 | -122.6669 | -122.7402
1960.5625 | 122.58 | -122.3557 | 0.086975 | 0.017319 | 0.0070582 | 0.017162 | 0.02891 | 0.040575 | -0.033199 | 0.062908 | -122.2412 | 0.073242 | -122.6303 | -122.2092 | -1.0254 | -33.0093 | -41.011 | -43.8766 | 0.15106 | -122.6257 | -0.27466 | -0.013733 | 0.11444 | 0.14649 | -1.1124 | -0.27008 | 0.064087 | 0.3891 | 81.3446 | 78.479 | 121.3303 | 122.4289 | 0.11444 | 122.5067 | 89.3463 | -0.27008 | 122.4289 | 0.11444 | 89.3463 | 121.3303 | 122.5067 | -122.7173 | -122.7127
1962.3438 | 122.5708 | -122.3785 | 0.10986 | 0.00206 | 0.00599 | 0.018444 | 0.02421 | 0.039721 | -0.031277 | 0.062053 | -122.2641 | 0.082397 | -122.6486 | -122.2641 | -1.0712 | -33.2291 | -41.1301 | -44.133 | 0.16937 | -122.6715 | -0.27008 | -0.027466 | 0.11444 | 0.11444 | -1.181 | -0.29297 | 0.05951 | 0.38452 | 81.2485 | 78.2455 | 121.3074 | 122.4609 | 0.11444 | 122.5479 | 89.1495 | -0.29297 | 122.4609 | 0.11444 | 89.1495 | 121.3074 | 122.5479 | -122.7585 | -122.7814
1964.0781 | 122.5616 | -122.3694 | 0.091553 | 0.017319 | 0.0053492 | 0.016308 | 0.026132 | 0.04143 | -0.034054 | 0.06184 | -122.3007 | 0.07782 | -122.6669 | -122.2961 | -1.1169 | -33.4671 | -41.4642 | -44.5358 | 0.16479 | -122.6807 | -0.29755 | -0.013733 | 0.068665 | 0.073242 | -1.2085 | -0.31128 | 0.073242 | 0.36621 | 80.9052 | 77.8336 | 121.2524 | 122.4472 | 0.068665 | 122.5342 | 88.9023 | -0.31128 | 122.4472 | 0.068665 | 88.9023 | 121.2524 | 122.5342 | -122.7585 | -122.7722
1965.8594 | 122.6349 | -122.3282 | 0.064087 | 0.00206 | 0.0074854 | 0.014172 | 0.020365 | 0.040148 | -0.030636 | 0.063335 | -122.2321 | 0.050354 | -122.6028 | -122.2229 | -1.0437 | -33.6182 | -42.0319 | -44.7464 | 0.12817 | -122.6669 | -0.27466 | -0.013733 | 0.09613 | 0.10529 | -1.1078 | -0.33875 | 0.064087 | 0.37079 | 80.2963 | 77.5818 | 121.2845 | 122.3785 | 0.09613 | 122.4564 | 88.71 | -0.33875 | 122.3785 | 0.09613 | 88.71 | 121.2845 | 122.4564 | -122.6669 | -122.731
1967.6562 | 122.6166 | -122.3648 | 0.07782 | -0.0055695 | 0.0036402 | 0.024212 | 0.029764 | 0.040362 | -0.033199 | 0.06184 | -122.287 | 0.086975 | -122.6578 | -122.3053 | -1.1902 | -33.9569 | -42.2333 | -45.2271 | 0.16022 | -122.6807 | -0.29297 | 0.009155 | 0.07782 | 0.059509 | -1.268 | -0.31586 | 0.082397 | 0.37079 | 80.1315 | 77.1378 | 121.1746 | 122.4518 | 0.07782 | 122.525 | 88.4079 | -0.31586 | 122.4518 | 0.07782 | 88.4079 | 121.1746 | 122.525 | -122.7356 | -122.7585
1969.3906 | 122.5525 | -122.3969 | 0.09613 | 0.0096895 | 0.00599 | 0.01823 | 0.021219 | 0.039507 | -0.032131 | 0.063976 | -122.2 | 0.041199 | -122.6074 | -122.2092 | -1.0986 | -34.053 | -42.6773 | -45.3918 | 0.15106 | -122.7127 | -0.21057 | -0.054931 | 0.19684 | 0.18768 | -1.1948 | -0.31586 | 0.054932 | 0.40741 | 79.7195 | 77.005 | 121.2982 | 122.4381 | 0.19684 | 122.5479 | 88.3438 | -0.31586 | 122.4381 | 0.19684 | 88.3438 | 121.2982 | 122.5479 | -122.7036 | -122.8088
1971.1562 | 122.5159 | -122.374 | 0.091553 | 0.017319 | 0.007699 | 0.021221 | 0.028482 | 0.041216 | -0.034267 | 0.063335 | -122.2366 | 0.086975 | -122.6715 | -122.2321 | -1.1856 | -34.3964 | -43.0161 | -45.8038 | 0.16022 | -122.6852 | -0.29755 | -0.004578 | 0.13733 | 0.14191 | -1.2772 | -0.31128 | 0.068664 | 0.43488 | 79.3579 | 76.5701 | 121.1884 | 122.4609 | 0.13733 | 122.5342 | 87.9776 | -0.31128 | 122.4609 | 0.13733 | 87.9776 | 121.1884 | 122.5342 | -122.7631 | -122.7768
1972.9375 | 122.5342 | -122.3923 | 0.086975 | 0.00206 | 0.0074854 | 0.021221 | 0.021005 | 0.040362 | -0.033199 | 0.061626 | -122.1725 | 0.054932 | -122.5662 | -122.1909 | -1.1169 | -34.4788 | -43.5287 | -46.0144 | 0.12817 | -122.6624 | -0.17395 | -0.032043 | 0.21973 | 0.20142 | -1.2039 | -0.27008 | 0.041199 | 0.39368 | 78.8635 | 76.3779 | 121.2753 | 122.4472 | 0.21973 | 122.5204 | 87.9135 | -0.27008 | 122.4472 | 0.21973 | 87.9135 | 121.2753 | 122.5204 | -122.6532 | -122.7493
1974.7188 | 122.612 | -122.3602 | 0.091553 | 0.0096895 | 0.0017176 | 0.02058 | 0.023783 | 0.042071 | -0.035335 | 0.063121 | -122.2137 | 0.050354 | -122.6166 | -122.2137 | -1.1673 | -34.726 | -43.9178 | -46.3577 | 0.13275 | -122.6303 | -0.25635 | -0.041199 | 0.14648 | 0.14648 | -1.2589 | -0.27008 | 0.041198 | 0.40283 | 78.4424 | 76.0025 | 121.1929 | 122.4106 | 0.14648 | 122.493 | 87.6343 | -0.27008 | 122.4106 | 0.14648 | 87.6343 | 121.1929 | 122.493 | -122.7081 | -122.7219
1976.4375 | 122.5204 | -122.4014 | 0.091553 | 0.0096895 | 0.00599 | 0.022717 | 0.02891 | 0.042284 | -0.03149 | 0.062908 | -122.2183 | 0.091553 | -122.644 | -122.2275 | -1.2634 | -34.9365 | -44.046 | -46.6232 | 0.16022 | -122.6578 | -0.24262 | 0 | 0.1831 | 0.17395 | -1.355 | -0.25635 | 0.068664 | 0.42572 | 78.3554 | 75.7782 | 121.138 | 122.493 | 0.1831 | 122.5616 | 87.4649 | -0.25635 | 122.493 | 0.1831 | 87.4649 | 121.138 | 122.5616 | -122.7356 | -122.7493
1978.2344 | 122.6395 | -122.3465 | 0.064087 | 0.0096895 | 0.0070582 | 0.021008 | 0.027414 | 0.040789 | -0.034054 | 0.061412 | -122.3053 | 0.086975 | -122.6532 | -122.3419 | -1.355 | -35.2386 | -44.3619 | -47.0078 | 0.16479 | -122.6807 | -0.3067 | 0.022888 | 0.041199 | 0.004578 | -1.4191 | -0.33417 | 0.10071 | 0.3479 | 77.9846 | 75.3387 | 120.9915 | 122.4335 | 0.041199 | 122.5113 | 87.1078 | -0.33417 | 122.4335 | 0.041199 | 87.1078 | 120.9915 | 122.5113 | -122.7173 | -122.7448
1980 | 122.6257 | -122.3511 | 0.086975 | 0.017319 | 0.0049218 | 0.019939 | 0.021433 | 0.039935 | -0.032131 | 0.062694 | -122.2137 | 0.045776 | -122.5983 | -122.2275 | -1.2543 | -35.2478 | -44.8746 | -47.1634 | 0.1236 | -122.6349 | -0.24719 | -0.041199 | 0.13733 | 0.1236 | -1.3412 | -0.28381 | 0.036621 | 0.38452 | 77.4765 | 75.1877 | 121.0968 | 122.3969 | 0.13733 | 122.4747 | 87.1033 | -0.28381 | 122.3969 | 0.13733 | 87.1033 | 121.0968 | 122.4747 | -122.6852 | -122.7219
1981.7656 | 122.6532 | -122.3557 | 0.054932 | 0.0096895 | 0.0089808 | 0.021008 | 0.027628 | 0.041857 | -0.033413 | 0.061626 | -122.2778 | 0.082397 | -122.6303 | -122.3053 | -1.3962 | -35.5316 | -45.0485 | -47.5388 | 0.16479 | -122.6532 | -0.27466 | 0.027465 | 0.07782 | 0.050354 | -1.4511 | -0.29755 | 0.10986 | 0.35248 | 77.3071 | 74.8169 | 120.9595 | 122.438 | 0.07782 | 122.5204 | 86.824 | -0.29755 | 122.438 | 0.07782 | 86.824 | 120.9595 | 122.5204 | -122.6852 | -122.7081
1983.5625 | 122.5388 | -122.3969 | 0.11444 | 0.0096895 | 0.0070582 | 0.018444 | 0.020365 | 0.038439 | -0.031917 | 0.062908 | -122.168 | 0.045776 | -122.5708 | -122.1817 | -1.3 | -35.6598 | -45.4788 | -47.6852 | 0.1236 | -122.6624 | -0.17395 | -0.068665 | 0.22888 | 0.21515 | -1.4145 | -0.2655 | 0.009155 | 0.40283 | 76.918 | 74.7116 | 121.0968 | 122.4426 | 0.22888 | 122.5204 | 86.7371 | -0.2655 | 122.4426 | 0.22888 | 86.7371 | 121.0968 | 122.5204 | -122.6852 | -122.7768
1985.2812 | 122.6486 | -122.3648 | 0.064087 | 0.00206 | 0.0066308 | 0.021862 | 0.027414 | 0.042712 | -0.030849 | 0.065044 | -122.2641 | 0.086975 | -122.6349 | -122.3007 | -1.4511 | -35.9665 | -45.5933 | -48.0789 | 0.16479 | -122.6578 | -0.27008 | 0.022888 | 0.10071 | 0.064087 | -1.5152 | -0.29297 | 0.10071 | 0.37079 | 76.7715 | 74.2859 | 120.9137 | 122.4518 | 0.10071 | 122.5296 | 86.3983 | -0.29297 | 122.4518 | 0.10071 | 86.3983 | 120.9137 | 122.5296 | -122.699 | -122.7219
1987.0781 | 122.6669 | -122.3694 | 0.064087 | 0.00206 | 0.0079126 | 0.01823 | 0.021219 | 0.041003 | -0.030849 | 0.063762 | -122.2275 | 0.022888 | -122.6212 | -122.2458 | -1.4099 | -36.0992 | -46.0098 | -48.317 | 0.12817 | -122.644 | -0.25177 | -0.041199 | 0.14191 | 0.1236 | -1.474 | -0.27466 | 0.064087 | 0.39368 | 76.3596 | 74.0524 | 120.9595 | 122.3923 | 0.14191 | 122.4976 | 86.2701 | -0.27466 | 122.3923 | 0.14191 | 86.2701 | 120.9595 | 122.4976 | -122.6852 | -122.7081
1988.7812 | 122.5296 | -122.3923 | 0.11444 | 0.00206 | 0.0083398 | 0.017376 | 0.023996 | 0.042071 | -0.03384 | 0.060985 | -122.1909 | 0.059509 | -122.5891 | -122.2046 | -1.4145 | -36.2274 | -46.1105 | -48.4634 | 0.14191 | -122.6852 | -0.19684 | -0.054932 | 0.20142 | 0.18768 | -1.5289 | -0.29297 | 0.027466 | 0.39825 | 76.2817 | 73.9288 | 120.9778 | 122.4518 | 0.20142 | 122.5342 | 86.1649 | -0.29297 | 122.4518 | 0.20142 | 86.1649 | 120.9778 | 122.5342 | -122.7036 | -122.7997
1990.5625 | 122.5891 | -122.3831 | 0.091553 | 0.00206 | 0.0066308 | 0.020153 | 0.022928 | 0.038012 | -0.030208 | 0.063335 | -122.1954 | 0.064087 | -122.5983 | -122.1863 | -1.4328 | -36.3647 | -46.4996 | -48.7427 | 0.14191 | -122.6761 | -0.21515 | -0.027466 | 0.18768 | 0.19684 | -1.5244 | -0.29297 | 0.050354 | 0.40283 | 75.8835 | 73.6404 | 120.9503 | 122.4472 | 0.18768 | 122.525 | 86.0184 | -0.29297 | 122.4472 | 0.18768 | 86.0184 | 120.9503 | 122.525 | -122.6898 | -122.7676
1992.2812 | 122.5616 | -122.3923 | 0.10071 | -0.0055695 | 0.0070582 | 0.022076 | 0.023569 | 0.038012 | -0.031277 | 0.063335 | -122.1634 | 0.054932 | -122.6303 | -122.168 | -1.4603 | -36.4883 | -46.7239 | -48.9899 | 0.13275 | -122.6761 | -0.23804 | -0.045776 | 0.22888 | 0.2243 | -1.561 | -0.28381 | 0.032043 | 0.46692 | 75.6683 | 73.4024 | 120.932 | 122.4472 | 0.22888 | 122.525 | 85.9039 | -0.28381 | 122.4472 | 0.22888 | 85.9039 | 120.932 | 122.525 | -122.731 | -122.7768
1994.0625 | 122.6486 | -122.374 | 0.086975 | -0.013199 | 0.0051356 | 0.019726 | 0.025705 | 0.039507 | -0.029568 | 0.066112 | -122.2092 | 0.036621 | -122.6257 | -122.2366 | -1.5472 | -36.7493 | -46.9391 | -49.3286 | 0.14191 | -122.6532 | -0.25177 | -0.050354 | 0.1648 | 0.13733 | -1.6342 | -0.27924 | 0.054932 | 0.41657 | 75.4349 | 73.0453 | 120.8267 | 122.4106 | 0.1648 | 122.5159 | 85.6247 | -0.27924 | 122.4106 | 0.1648 | 85.6247 | 120.8267 | 122.5159 | -122.7127 | -122.7402
1995.8281 | 122.6532 | -122.3923 | 0.082397 | 0.0096895 | 0.0062036 | 0.019085 | 0.026132 | 0.03908 | -0.030636 | 0.060558 | -122.2137 | 0.045776 | -122.6166 | -122.2504 | -1.593 | -36.8088 | -47.1542 | -49.6262 | 0.13275 | -122.6669 | -0.2243 | -0.036621 | 0.17853 | 0.14191 | -1.6754 | -0.27466 | 0.050354 | 0.40283 | 75.238 | 72.7661 | 120.7993 | 122.438 | 0.17853 | 122.525 | 85.5835 | -0.27466 | 122.438 | 0.17853 | 85.5835 | 120.7993 | 122.525 | -122.699 | -122.7493
1997.5469 | 122.6349 | -122.3602 | 0.07782 | 0.00206 | 0.010903 | 0.019299 | 0.02421 | 0.039935 | -0.03149 | 0.064403 | -122.2 | 0.059509 | -122.612 | -122.2321 | -1.6113 | -36.9553 | -47.319 | -49.704 | 0.1236 | -122.6486 | -0.25177 | -0.018311 | 0.16022 | 0.12817 | -1.6891 | -0.28839 | 0.045776 | 0.41199 | 75.0412 | 72.6562 | 120.7489 | 122.4197 | 0.16022 | 122.4838 | 85.405 | -0.28839 | 122.4197 | 0.16022 | 85.405 | 120.7489 | 122.4838 | -122.6898 | -122.7264
1999.3281 | 122.5433 | -122.3969 | 0.1236 | 0.0096895 | 0.0074854 | 0.020367 | 0.022714 | 0.039507 | -0.033199 | 0.061412 | -122.1634 | 0.054932 | -122.6349 | -122.2 | -1.6067 | -37.0926 | -47.4701 | -49.8367 | 0.13733 | -122.6624 | -0.23804 | -0.068664 | 0.23346 | 0.19684 | -1.7303 | -0.2655 | 0.013733 | 0.4715 | 74.9268 | 72.5601 | 120.7901 | 122.4518 | 0.23346 | 122.5342 | 85.3043 | -0.2655 | 122.4518 | 0.23346 | 85.3043 | 120.7901 | 122.5342 | -122.7585 | -122.7859
2001.0469 | 122.6212 | -122.3923 | 0.07782 | 0.00206 | 0.0072718 | 0.024426 | 0.02656 | 0.040148 | -0.033199 | 0.063549 | -122.1771 | 0.032043 | -122.6074 | -122.1954 | -1.6479 | -37.1613 | -47.6852 | -50.0336 | 0.10529 | -122.6486 | -0.21515 | -0.045777 | 0.21515 | 0.19684 | -1.7258 | -0.25635 | 0.027466 | 0.4303 | 74.707 | 72.3587 | 120.7443 | 122.4243 | 0.21515 | 122.4976 | 85.231 | -0.25635 | 122.4243 | 0.21515 | 85.231 | 120.7443 | 122.4976 | -122.6852 | -122.7264
2002.8281 | 122.5616 | -122.406 | 0.09613 | 0.0096895 | 0.0040674 | 0.023357 | 0.025278 | 0.039721 | -0.03149 | 0.064189 | -122.1817 | 0.050354 | -122.612 | -122.1863 | -1.6571 | -37.1933 | -47.7997 | -50.0931 | 0.1236 | -122.6624 | -0.20599 | -0.045776 | 0.2243 | 0.21973 | -1.7532 | -0.25635 | 0.027466 | 0.4303 | 74.6063 | 72.3129 | 120.7489 | 122.4564 | 0.2243 | 122.5296 | 85.2127 | -0.25635 | 122.4564 | 0.2243 | 85.2127 | 120.7489 | 122.5296 | -122.7081 | -122.7585
2004.6094 | 122.6624 | -122.3648 | 0.073242 | 0.0096895 | 0.0079126 | 0.022503 | 0.026987 | 0.038653 | -0.030636 | 0.06184 | -122.2 | 0.050354 | -122.6166 | -122.2366 | -1.7578 | -37.1979 | -47.7814 | -50.1297 | 0.11444 | -122.6852 | -0.25177 | -0.022888 | 0.16479 | 0.12817 | -1.8311 | -0.32044 | 0.041199 | 0.41657 | 74.5834 | 72.2351 | 120.607 | 122.4152 | 0.16479 | 122.4792 | 85.1669 | -0.32044 | 122.4152 | 0.16479 | 85.1669 | 120.607 | 122.4792 | -122.6898 | -122.7585
2006.3906 | 122.5388 | -122.406 | 0.11444 | 0.0096895 | 0.0091944 | 0.02528 | 0.031687 | 0.041644 | -0.033413 | 0.06248 | -122.1954 | 0.068665 | -122.6715 | -122.2275 | -1.8036 | -37.1841 | -47.7905 | -50.1846 | 0.16479 | -122.6807 | -0.2655 | -0.045776 | 0.21057 | 0.17853 | -1.918 | -0.27466 | 0.050354 | 0.47607 | 74.6155 | 72.2214 | 120.6024 | 122.4747 | 0.21057 | 122.5708 | 85.2219 | -0.27466 | 122.4747 | 0.21057 | 85.2219 | 120.6024 | 122.5708 | -122.7859 | -122.7951
2008.1719 | 122.6166 | -122.3831 | 0.054932 | 0.0096895 | 0.007699 | 0.021648 | 0.026132 | 0.041644 | -0.030636 | 0.063976 | -122.1725 | 0.036621 | -122.612 | -122.2 | -1.7807 | -37.2528 | -48.0469 | -50.1205 | 0.11902 | -122.6807 | -0.22888 | -0.018311 | 0.21057 | 0.18311 | -1.8356 | -0.29755 | 0.064087 | 0.43945 | 74.3362 | 72.2626 | 120.6024 | 122.4197 | 0.21057 | 122.5021 | 85.1303 | -0.29755 | 122.4197 | 0.21057 | 85.1303 | 120.6024 | 122.5021 | -122.6669 | -122.7356
2009.9531 | 122.5708 | -122.3785 | 0.09613 | 0.024948 | 0.0081262 | 0.024212 | 0.024851 | 0.040789 | -0.031063 | 0.062053 | -122.2687 | 0.10071 | -122.6761 | -122.2824 | -1.9089 | -37.2986 | -47.8363 | -50.2258 | 0.16479 | -122.6852 | -0.29755 | 0.004578 | 0.10986 | 0.09613 | -2.005 | -0.3067 | 0.068665 | 0.40741 | 74.5422 | 72.1527 | 120.4697 | 122.4792 | 0.10986 | 122.5433 | 85.08 | -0.3067 | 122.4792 | 0.10986 | 85.08 | 120.4697 | 122.5433 | -122.7722 | -122.7814
2011.6719 | 122.6669 | -122.374 | 0.059509 | 0.0096895 | 0.0089808 | 0.025066 | 0.026346 | 0.04143 | -0.032345 | 0.063121 | -122.287 | 0.086975 | -122.6578 | -122.319 | -1.973 | -37.3123 | -47.9736 | -50.1801 | 0.16022 | -122.699 | -0.28381 | 0.027466 | 0.086975 | 0.054931 | -2.0325 | -0.32501 | 0.10071 | 0.37079 | 74.4003 | 72.1939 | 120.401 | 122.4609 | 0.086975 | 122.5342 | 85.0616 | -0.32501 | 122.4609 | 0.086975 | 85.0616 | 120.401 | 122.5342 | -122.7173 | -122.7585
2013.4688 | 122.5342 | -122.4197 | 0.11444 | 0.00206 | 0.0089808 | 0.021435 | 0.020365 | 0.038653 | -0.031063 | 0.065471 | -122.1542 | 0.045776 | -122.58 | -122.1771 | -1.8585 | -37.2162 | -48.2346 | -50.116 | 0.13733 | -122.6852 | -0.16022 | -0.068665 | 0.2655 | 0.24262 | -1.973 | -0.2655 | 0.022888 | 0.42572 | 74.1852 | 72.3038 | 120.5612 | 122.4655 | 0.2655 | 122.5571 | 85.2036 | -0.2655 | 122.4655 | 0.2655 | 85.2036 | 120.5612 | 122.5571 | -122.6944 | -122.7997
2015.1875 | 122.6761 | -122.3694 | 0.059509 | 0.00206 | 0.0081262 | 0.020367 | 0.021005 | 0.037798 | -0.029568 | 0.06483 | -122.2321 | 0.054932 | -122.6303 | -122.2641 | -1.9775 | -37.2986 | -48.317 | -50.2167 | 0.13275 | -122.6852 | -0.26093 | -0.004577 | 0.13733 | 0.10529 | -2.037 | -0.31586 | 0.073242 | 0.39825 | 74.0524 | 72.1527 | 120.3918 | 122.4243 | 0.13733 | 122.5021 | 85.0708 | -0.31586 | 122.4243 | 0.13733 | 85.0708 | 120.3918 | 122.5021 | -122.6898 | -122.7448
2016.9531 | 122.5937 | -122.4197 | 0.10529 | 0.00206 | 0.011117 | 0.02058 | 0.028055 | 0.039721 | -0.031277 | 0.062267 | -122.2412 | 0.091553 | -122.6486 | -122.3007 | -2.0599 | -37.3398 | -48.2025 | -50.235 | 0.16022 | -122.7448 | -0.22888 | -0.013733 | 0.17853 | 0.11902 | -2.1652 | -0.32501 | 0.054931 | 0.40741 | 74.2172 | 72.1848 | 120.3598 | 122.5113 | 0.17853 | 122.58 | 85.08 | -0.32501 | 122.5113 | 0.17853 | 85.08 | 120.3598 | 122.58 | -122.7539 | -122.85
2018.7344 | 122.6761 | -122.374 | 0.068665 | 0.0096895 | 0.0053492 | 0.022503 | 0.023355 | 0.039507 | -0.032345 | 0.06248 | -122.2137 | 0.054932 | -122.5891 | -122.2595 | -2.0508 | -37.4954 | -48.5413 | -50.2716 | 0.13733 | -122.6486 | -0.21515 | -0.013733 | 0.16022 | 0.11444 | -2.1194 | -0.27466 | 0.068664 | 0.37537 | 73.8327 | 72.1024 | 120.3232 | 122.4289 | 0.16022 | 122.5113 | 84.8785 | -0.27466 | 122.4289 | 0.16022 | 84.8785 | 120.3232 | 122.5113 | -122.6578 | -122.7173
2020.5156 | 122.612 | -122.374 | 0.086975 | 0.017319 | 0.0083398 | 0.023357 | 0.028482 | 0.043993 | -0.032985 | 0.064617 | -122.1634 | 0.032043 | -122.6532 | -122.1954 | -2.037 | -37.3947 | -48.5641 | -50.1205 | 0.13275 | -122.6624 | -0.27924 | -0.054932 | 0.21057 | 0.17853 | -2.124 | -0.28839 | 0.045776 | 0.48981 | 73.8098 | 72.2534 | 120.3369 | 122.406 | 0.21057 | 122.5067 | 84.9792 | -0.28839 | 122.406 | 0.21057 | 84.9792 | 120.3369 | 122.5067 | -122.7402 | -122.7493
2022.2344 | 122.6257 | -122.3923 | 0.07782 | 0.00206 | 0.0085534 | 0.022289 | 0.029123 | 0.042925 | -0.034267 | 0.066112 | -122.1634 | 0.041199 | -122.6257 | -122.2137 | -2.0874 | -37.413 | -48.6694 | -50.2029 | 0.13275 | -122.6486 | -0.23346 | -0.036621 | 0.22888 | 0.17853 | -2.1652 | -0.25635 | 0.054931 | 0.46234 | 73.7228 | 72.1893 | 120.3049 | 122.4335 | 0.22888 | 122.525 | 84.9792 | -0.25635 | 122.4335 | 0.22888 | 84.9792 | 120.3049 | 122.525 | -122.7036 | -122.7264
2024.0312 | 122.6761 | -122.3557 | 0.068665 | -0.0055695 | 0.0070582 | 0.022076 | 0.023569 | 0.041216 | -0.031063 | 0.063762 | -122.1909 | 0.064087 | -122.6303 | -122.2641 | -2.179 | -37.3398 | -48.4817 | -50.1389 | 0.1236 | -122.6807 | -0.27466 | -0.004578 | 0.1648 | 0.091553 | -2.2476 | -0.32501 | 0.054931 | 0.43945 | 73.8739 | 72.2168 | 120.1767 | 122.4197 | 0.1648 | 122.4792 | 85.0159 | -0.32501 | 122.4197 | 0.1648 | 85.0159 | 120.1767 | 122.4792 | -122.699 | -122.7493
2025.7344 | 122.6166 | -122.374 | 0.068665 | 0.0096895 | 0.0091944 | 0.024853 | 0.028269 | 0.04143 | -0.032558 | 0.063762 | -122.1405 | 0.050354 | -122.6303 | -122.2092 | -2.1561 | -37.2711 | -48.5092 | -49.9832 | 0.12817 | -122.6532 | -0.25635 | -0.018311 | 0.23346 | 0.1648 | -2.2247 | -0.27924 | 0.059509 | 0.48981 | 73.8647 | 72.3907 | 120.2179 | 122.4243 | 0.23346 | 122.5021 | 85.1028 | -0.27924 | 122.4243 | 0.23346 | 85.1028 | 120.2179 | 122.5021 | -122.699 | -122.7219
2027.5156 | 122.58 | -122.4243 | 0.10529 | 0.0096895 | 0.010476 | 0.01823 | 0.024637 | 0.039294 | -0.032345 | 0.063762 | -122.2229 | 0.086975 | -122.6761 | -122.3007 | -2.2705 | -37.3764 | -48.2803 | -50.0061 | 0.17853 | -122.7081 | -0.25177 | -0.018311 | 0.20142 | 0.1236 | -2.3758 | -0.28381 | 0.073242 | 0.45319 | 74.144 | 72.4182 | 120.1538 | 122.5113 | 0.20142 | 122.6028 | 85.0479 | -0.28381 | 122.5113 | 0.20142 | 85.0479 | 120.1538 | 122.6028 | -122.7814 | -122.8134
2029.3281 | 122.6624 | -122.3648 | 0.059509 | 0.00206 | 0.011544 | 0.025707 | 0.029123 | 0.041003 | -0.03149 | 0.065044 | -122.2778 | 0.073242 | -122.6761 | -122.3099 | -2.3483 | -37.3169 | -48.2758 | -49.9558 | 0.15564 | -122.7219 | -0.31128 | 0.013733 | 0.086975 | 0.054932 | -2.4078 | -0.35706 | 0.096131 | 0.39825 | 74.0891 | 72.4091 | 120.0165 | 122.438 | 0.086975 | 122.5204 | 85.0479 | -0.35706 | 122.438 | 0.086975 | 85.0479 | 120.0165 | 122.5204 | -122.7356 | -122.7814
2031.0469 | 122.5296 | -122.4243 | 0.10529 | 0.00206 | 0.0091944 | 0.024853 | 0.029337 | 0.042284 | -0.034908 | 0.064617 | -122.1863 | 0.086975 | -122.6578 | -122.2687 | -2.3163 | -37.2345 | -48.3765 | -49.704 | 0.16022 | -122.7173 | -0.23346 | -0.018311 | 0.23804 | 0.15564 | -2.4216 | -0.29297 | 0.054931 | 0.4715 | 74.0479 | 72.7203 | 120.108 | 122.5113 | 0.23804 | 122.5845 | 85.1898 | -0.29297 | 122.5113 | 0.23804 | 85.1898 | 120.108 | 122.5845 | -122.7631 | -122.8226
2032.8281 | 122.5433 | -122.4197 | 0.10529 | -0.013199 | 0.008767 | 0.023571 | 0.021433 | 0.037585 | -0.030636 | 0.063121 | -122.1313 | 0.050354 | -122.612 | -122.2092 | -2.2614 | -37.2574 | -48.5779 | -49.5575 | 0.12817 | -122.7219 | -0.19226 | -0.054932 | 0.28839 | 0.21057 | -2.3666 | -0.30212 | 0.022888 | 0.48065 | 73.8419 | 72.8622 | 120.1584 | 122.4701 | 0.28839 | 122.5479 | 85.1624 | -0.30212 | 122.4701 | 0.28839 | 85.1624 | 120.1584 | 122.5479 | -122.7173 | -122.8271
2034.5938 | 122.5433 | -122.4335 | 0.09613 | 0.00206 | 0.011331 | 0.022717 | 0.028055 | 0.041003 | -0.033199 | 0.065898 | -122.1954 | 0.07782 | -122.6944 | -122.2549 | -2.3849 | -37.3627 | -48.5092 | -49.6307 | 0.16937 | -122.6944 | -0.26093 | -0.01831 | 0.23804 | 0.17853 | -2.4811 | -0.26093 | 0.073243 | 0.49896 | 73.9243 | 72.8027 | 120.0485 | 122.5113 | 0.23804 | 122.6028 | 85.0708 | -0.26093 | 122.5113 | 0.23804 | 85.0708 | 120.0485 | 122.6028 | -122.7905 | -122.7905
2036.3125 | 122.5433 | -122.438 | 0.1236 | 0.017319 | 0.010903 | 0.021435 | 0.031259 | 0.04143 | -0.032985 | 0.066326 | -122.2092 | 0.07782 | -122.6578 | -122.287 | -2.4307 | -37.3032 | -48.3124 | -49.379 | 0.15106 | -122.6852 | -0.21973 | -0.045776 | 0.22888 | 0.15106 | -2.5543 | -0.24719 | 0.027466 | 0.44861 | 74.1257 | 73.0591 | 120.0073 | 122.5159 | 0.22888 | 122.5891 | 85.1349 | -0.24719 | 122.5159 | 0.22888 | 85.1349 | 120.0073 | 122.5891 | -122.7814 | -122.8088
2038.0938 | 122.612 | -122.3969 | 0.091553 | 0.00206 | 0.0091944 | 0.02293 | 0.025492 | 0.042071 | -0.032558 | 0.066753 | -122.1268 | 0.041199 | -122.5983 | -122.2321 | -2.4078 | -37.175 | -48.4451 | -49.0952 | 0.1236 | -122.7081 | -0.20142 | -0.050354 | 0.27008 | 0.16479 | -2.4994 | -0.31128 | 0.032043 | 0.4715 | 73.9517 | 73.3017 | 119.989 | 122.4381 | 0.27008 | 122.5204 | 85.2219 | -0.31128 | 122.4381 | 0.27008 | 85.2219 | 119.989 | 122.5204 | -122.6898 | -122.7997
2039.8125 | 122.5525 | -122.4335 | 0.1236 | 0.0096895 | 0.0079126 | 0.024426 | 0.022928 | 0.039721 | -0.02914 | 0.064617 | -122.1634 | 0.045776 | -122.5983 | -122.2092 | -2.4261 | -37.1567 | -48.4222 | -49.0677 | 0.14191 | -122.6761 | -0.1648 | -0.07782 | 0.27008 | 0.22431 | -2.5497 | -0.24261 | 0.018311 | 0.43488 | 74.0112 | 73.3658 | 120.0073 | 122.4792 | 0.27008 | 122.5754 | 85.2768 | -0.24261 | 122.4792 | 0.27008 | 85.2768 | 120.0073 | 122.5754 | -122.7219 | -122.7997
2041.6094 | 122.5525 | -122.4289 | 0.082397 | 0.00206 | 0.01069 | 0.02763 | 0.028055 | 0.040362 | -0.032985 | 0.065257 | -122.2183 | 0.086975 | -122.7081 | -122.2687 | -2.5543 | -37.2757 | -48.3765 | -49.1364 | 0.16937 | -122.7081 | -0.27924 | 0.004578 | 0.21057 | 0.16022 | -2.6367 | -0.27924 | 0.086976 | 0.48981 | 74.0524 | 73.2925 | 119.8746 | 122.5159 | 0.21057 | 122.5983 | 85.1532 | -0.27924 | 122.5159 | 0.21057 | 85.1532 | 119.8746 | 122.5983 | -122.7905 | -122.7905
2043.3438 | 122.5342 | -122.4243 | 0.11444 | 0.0096895 | 0.013467 | 0.028271 | 0.02891 | 0.041216 | -0.032985 | 0.065898 | -122.1909 | 0.07782 | -122.6944 | -122.2824 | -2.5726 | -37.2025 | -48.2849 | -48.8754 | 0.16479 | -122.6944 | -0.27008 | -0.036621 | 0.23346 | 0.14191 | -2.6871 | -0.27008 | 0.050354 | 0.50354 | 74.1394 | 73.5489 | 119.8517 | 122.5021 | 0.23346 | 122.5891 | 85.2219 | -0.27008 | 122.5021 | 0.23346 | 85.2219 | 119.8517 | 122.5891 | -122.8088 | -122.8088
2045.1406 | 122.5937 | -122.4289 | 0.091553 | 0.0096895 | 0.009408 | 0.023998 | 0.025064 | 0.040575 | -0.030636 | 0.066112 | -122.2504 | 0.09613 | -122.6624 | -122.3419 | -2.6596 | -37.0697 | -47.905 | -48.6694 | 0.14191 | -122.6944 | -0.23346 | 0.004577 | 0.17853 | 0.086975 | -2.7512 | -0.2655 | 0.050354 | 0.41199 | 74.5239 | 73.7595 | 119.7693 | 122.525 | 0.17853 | 122.5708 | 85.3592 | -0.2655 | 122.525 | 0.17853 | 85.3592 | 119.7693 | 122.5708 | -122.7539 | -122.7859
2046.9219 | 122.6807 | -122.3602 | 0.073242 | 0.017319 | 0.0079126 | 0.021862 | 0.021433 | 0.041003 | -0.03149 | 0.069103 | -122.2137 | 0.036621 | -122.6349 | -122.3007 | -2.6276 | -36.8912 | -48.1293 | -48.6786 | 0.12817 | -122.6852 | -0.27466 | -0.036621 | 0.14648 | 0.059509 | -2.7008 | -0.32501 | 0.054932 | 0.42114 | 74.231 | 73.6816 | 119.7327 | 122.3969 | 0.14648 | 122.4884 | 85.4691 | -0.32501 | 122.3969 | 0.14648 | 85.4691 | 119.7327 | 122.4884 | -122.7081 | -122.7585
2048.6875 | 122.6761 | -122.3694 | 0.064087 | 0.0096895 | 0.010262 | 0.026989 | 0.02421 | 0.041003 | -0.02914 | 0.066326 | -122.1817 | 0.041199 | -122.5983 | -122.2687 | -2.6733 | -36.7401 | -48.2208 | -48.6099 | 0.13733 | -122.6898 | -0.22888 | -0.022888 | 0.18768 | 0.10071 | -2.7374 | -0.32043 | 0.073242 | 0.41657 | 74.1486 | 73.7595 | 119.696 | 122.4106 | 0.18768 | 122.5067 | 85.6293 | -0.32043 | 122.4106 | 0.18768 | 85.6293 | 119.696 | 122.5067 | -122.6624 | -122.7539
2050.4844 | 122.6486 | -122.4106 | 0.073242 | -0.0055695 | 0.009408 | 0.023357 | 0.025492 | 0.041216 | -0.032345 | 0.06483 | -122.1359 | 0.045776 | -122.6303 | -122.2549 | -2.6962 | -36.557 | -48.0515 | -48.3948 | 0.1236 | -122.6807 | -0.21973 | -0.027466 | 0.27466 | 0.15564 | -2.7695 | -0.27008 | 0.050354 | 0.49438 | 74.3591 | 74.0158 | 119.7144 | 122.4564 | 0.27466 | 122.5342 | 85.8536 | -0.27008 | 122.4564 | 0.27466 | 85.8536 | 119.7144 | 122.5342 | -122.7036 | -122.7539
2052.2031 | 122.5296 | -122.4426 | 0.10529 | 0.0096895 | 0.011544 | 0.028484 | 0.031687 | 0.040148 | -0.034054 | 0.06718 | -122.1725 | 0.050354 | -122.7036 | -122.2641 | -2.7832 | -36.4471 | -47.7402 | -48.2346 | 0.16479 | -122.6852 | -0.26093 | -0.054932 | 0.27008 | 0.17853 | -2.8885 | -0.24262 | 0.059509 | 0.53101 | 74.7025 | 74.2081 | 119.6594 | 122.493 | 0.27008 | 122.6074 | 85.9955 | -0.24262 | 122.493 | 0.27008 | 85.9955 | 119.6594 | 122.6074 | -122.8088 | -122.7905
2053.9844 | 122.5983 | -122.4106 | 0.10529 | 0.00206 | 0.013894 | 0.023785 | 0.028696 | 0.039507 | -0.031917 | 0.064403 | -122.2458 | 0.10529 | -122.6715 | -122.3282 | -2.8564 | -36.4563 | -47.6578 | -48.2254 | 0.1831 | -122.7676 | -0.26093 | 0 | 0.16479 | 0.082397 | -2.9617 | -0.35706 | 0.077819 | 0.42572 | 74.7528 | 74.1852 | 119.5541 | 122.5159 | 0.16479 | 122.5937 | 85.9543 | -0.35706 | 122.5159 | 0.16479 | 85.9543 | 119.5541 | 122.5937 | -122.7768 | -122.8729
2055.7344 | 122.6486 | -122.3831 | 0.086975 | 0.0096895 | 0.0098352 | 0.024853 | 0.027201 | 0.042284 | -0.034481 | 0.065898 | -122.1817 | 0.068665 | -122.6715 | -122.2549 | -2.8336 | -36.6257 | -48.1979 | -48.4177 | 0.14648 | -122.6669 | -0.28839 | -0.01831 | 0.20142 | 0.12817 | -2.9205 | -0.28381 | 0.059509 | 0.48981 | 74.1852 | 73.9655 | 119.5496 | 122.4518 | 0.20142 | 122.5296 | 85.7574 | -0.28381 | 122.4518 | 0.20142 | 85.7574 | 119.5496 | 122.5296 | -122.7585 | -122.7539
2057.4531 | 122.58 | -122.4289 | 0.11444 | 0.00206 | 0.010903 | 0.02998 | 0.031259 | 0.043566 | -0.035549 | 0.068248 | -122.1909 | 0.086975 | -122.6761 | -122.3236 | -2.9388 | -36.6211 | -48.0011 | -48.3765 | 0.15564 | -122.6944 | -0.24719 | -0.027466 | 0.23804 | 0.10529 | -3.0533 | -0.2655 | 0.041199 | 0.48523 | 74.4278 | 74.0524 | 119.4901 | 122.5159 | 0.23804 | 122.5845 | 85.8078 | -0.2655 | 122.5159 | 0.23804 | 85.8078 | 119.4901 | 122.5845 | -122.7905 | -122.8088
2059.25 | 122.5708 | -122.4335 | 0.10986 | 0.0096895 | 0.010049 | 0.032757 | 0.023569 | 0.039935 | -0.028927 | 0.065685 | -122.1497 | 0.059509 | -122.6028 | -122.2458 | -2.8931 | -36.4197 | -47.85 | -48.0148 | 0.15564 | -122.7219 | -0.16937 | -0.050354 | 0.28381 | 0.18768 | -3.0029 | -0.28839 | 0.045777 | 0.45319 | 74.5834 | 74.4186 | 119.5404 | 122.493 | 0.28381 | 122.5891 | 86.0138 | -0.28839 | 122.493 | 0.28381 | 86.0138 | 119.5404 | 122.5891 | -122.7127 | -122.8317
2061.0312 | 122.5525 | -122.4518 | 0.10529 | 0.0096895 | 0.011117 | 0.02293 | 0.024423 | 0.038226 | -0.030422 | 0.069744 | -122.1176 | 0.041199 | -122.6303 | -122.2275 | -2.9022 | -36.319 | -47.7997 | -47.8226 | 0.13275 | -122.7127 | -0.17853 | -0.064087 | 0.33417 | 0.2243 | -3.0075 | -0.26093 | 0.027465 | 0.51269 | 74.6521 | 74.6292 | 119.5496 | 122.493 | 0.33417 | 122.5845 | 86.1328 | -0.26093 | 122.493 | 0.33417 | 86.1328 | 119.5496 | 122.5845 | -122.7356 | -122.818
2062.7344 | 122.699 | -122.4014 | 0.064087 | 0.0096895 | 0.011331 | 0.027416 | 0.023783 | 0.040148 | -0.030636 | 0.066966 | -122.1863 | 0.064087 | -122.6486 | -122.2778 | -3.0075 | -36.3831 | -47.7859 | -47.85 | 0.1236 | -122.699 | -0.24719 | 0 | 0.21515 | 0.1236 | -3.0716 | -0.29755 | 0.059509 | 0.46234 | 74.6155 | 74.5514 | 119.3939 | 122.4655 | 0.21515 | 122.525 | 86.0184 | -0.29755 | 122.4655 | 0.21515 | 86.0184 | 119.3939 | 122.525 | -122.7127 | -122.7631
2064.5469 | 122.6395 | -122.3969 | 0.064087 | 0.00206 | 0.013467 | 0.03233 | 0.029764 | 0.042284 | -0.031277 | 0.065685 | -122.1268 | 0.059509 | -122.6395 | -122.2366 | -3.0304 | -36.2091 | -47.6486 | -47.5616 | 0.1236 | -122.6852 | -0.24261 | -0.004578 | 0.27008 | 0.16022 | -3.0945 | -0.28839 | 0.059509 | 0.5127 | 74.7482 | 74.8352 | 119.3665 | 122.4564 | 0.27008 | 122.5204 | 86.1877 | -0.28839 | 122.4564 | 0.27008 | 86.1877 | 119.3665 | 122.5204 | -122.7036 | -122.7493
2066.2812 | 122.6166 | -122.3923 | 0.082397 | 0.00206 | 0.01304 | 0.029553 | 0.030191 | 0.042925 | -0.031277 | 0.068248 | -122.1039 | 0.036621 | -122.6578 | -122.2183 | -3.0533 | -36.2732 | -47.6715 | -47.4564 | 0.13275 | -122.6944 | -0.2655 | -0.045776 | 0.28839 | 0.17395 | -3.1357 | -0.30212 | 0.050354 | 0.55389 | 74.7208 | 74.9359 | 119.339 | 122.4289 | 0.28839 | 122.525 | 86.1191 | -0.30212 | 122.4289 | 0.28839 | 86.1191 | 119.339 | 122.525 | -122.7402 | -122.7768
2068.0781 | 122.6166 | -122.4426 | 0.10986 | 0.00206 | 0.012399 | 0.026135 | 0.027628 | 0.038653 | -0.031277 | 0.066326 | -122.2458 | 0.10529 | -122.731 | -122.3282 | -3.2227 | -36.4975 | -47.4884 | -47.6028 | 0.17395 | -122.731 | -0.28839 | -0.004577 | 0.19684 | 0.11444 | -3.3325 | -0.28839 | 0.064087 | 0.48523 | 74.9542 | 74.8398 | 119.22 | 122.5479 | 0.19684 | 122.6166 | 85.9451 | -0.28839 | 122.5479 | 0.19684 | 85.9451 | 119.22 | 122.6166 | -122.8409 | -122.8409
2069.7812 | 122.5891 | -122.4106 | 0.091553 | 0.0096895 | 0.012612 | 0.025494 | 0.031473 | 0.039507 | -0.030636 | 0.069316 | -122.2229 | 0.082397 | -122.6898 | -122.3236 | -3.2501 | -36.5616 | -47.4884 | -47.4976 | 0.17395 | -122.7402 | -0.27924 | -0.009156 | 0.18768 | 0.086975 | -3.3417 | -0.32959 | 0.082397 | 0.46692 | 74.9222 | 74.913 | 119.1605 | 122.493 | 0.18768 | 122.5845 | 85.849 | -0.32959 | 122.493 | 0.18768 | 85.849 | 119.1605 | 122.5845 | -122.7814 | -122.8317
2071.5781 | 122.6624 | -122.4106 | 0.068665 | 0.0096895 | 0.01368 | 0.026989 | 0.028269 | 0.041216 | -0.034054 | 0.068248 | -122.1085 | 0.041199 | -122.6578 | -122.2275 | -3.1952 | -36.5662 | -47.7768 | -47.374 | 0.1236 | -122.6852 | -0.24719 | -0.027466 | 0.30212 | 0.1831 | -3.2639 | -0.27466 | 0.054931 | 0.54932 | 74.6338 | 75.0366 | 119.2154 | 122.4518 | 0.30212 | 122.5342 | 85.8444 | -0.27466 | 122.4518 | 0.30212 | 85.8444 | 119.2154 | 122.5342 | -122.7264 | -122.7539
2073.3594 | 122.6898 | -122.374 | 0.07782 | 0.0096895 | 0.012185 | 0.027844 | 0.031046 | 0.041216 | -0.031704 | 0.066966 | -122.2229 | 0.07782 | -122.7127 | -122.3648 | -3.3829 | -36.8088 | -47.5296 | -47.4701 | 0.1831 | -122.7219 | -0.33875 | 0 | 0.15106 | 0.009155 | -3.4607 | -0.3479 | 0.10528 | 0.48981 | 74.8444 | 74.9039 | 118.9911 | 122.4518 | 0.15106 | 122.5571 | 85.5652 | -0.3479 | 122.4518 | 0.15106 | 85.5652 | 118.9911 | 122.5571 | -122.7905 | -122.7997
2075.0781 | 122.5616 | -122.4289 | 0.09613 | 0.0096895 | 0.013467 | 0.029553 | 0.030618 | 0.044848 | -0.035335 | 0.068889 | -122.1542 | 0.064087 | -122.6486 | -122.2961 | -3.3737 | -36.7996 | -47.5159 | -47.287 | 0.16479 | -122.6761 | -0.21973 | -0.032043 | 0.27466 | 0.13275 | -3.4698 | -0.24719 | 0.068665 | 0.49439 | 74.913 | 75.1419 | 119.0552 | 122.493 | 0.27466 | 122.5937 | 85.6293 | -0.24719 | 122.493 | 0.27466 | 85.6293 | 119.0552 | 122.5937 | -122.7448 | -122.7722
2076.8594 | 122.5754 | -122.4335 | 0.11444 | 0.0096895 | 0.011971 | 0.029125 | 0.020365 | 0.039935 | -0.028499 | 0.068889 | -122.0947 | 0.041199 | -122.6303 | -122.2321 | -3.3279 | -36.6989 | -47.5067 | -47.0764 | 0.13733 | -122.6944 | -0.19684 | -0.073242 | 0.33874 | 0.20142 | -3.4424 | -0.26093 | 0.022888 | 0.53558 | 74.9268 | 75.3571 | 119.1055 | 122.4747 | 0.33874 | 122.5708 | 85.7346 | -0.26093 | 122.4747 | 0.33874 | 85.7346 | 119.1055 | 122.5708 | -122.7448 | -122.8088
2078.6406 | 122.612 | -122.4289 | 0.10986 | 0.017319 | 0.013467 | 0.026135 | 0.028482 | 0.039721 | -0.032772 | 0.069103 | -122.1863 | 0.059509 | -122.6807 | -122.3282 | -3.4744 | -36.8866 | -47.3785 | -47.2229 | 0.16937 | -122.7081 | -0.25177 | -0.050354 | 0.24262 | 0.10071 | -3.5843 | -0.27924 | 0.05951 | 0.49438 | 75.0504 | 75.206 | 118.9545 | 122.4884 | 0.24262 | 122.5983 | 85.5423 | -0.27924 | 122.4884 | 0.24262 | 85.5423 | 118.9545 | 122.5983 | -122.7905 | -122.818
2080.375 | 122.5754 | -122.4564 | 0.10071 | 0.00206 | 0.011544 | 0.02998 | 0.02656 | 0.038439 | -0.029781 | 0.068462 | -122.1176 | 0.032043 | -122.6303 | -122.2458 | -3.4332 | -36.8088 | -47.3648 | -47.0718 | 0.15106 | -122.7448 | -0.17395 | -0.068665 | 0.33875 | 0.21057 | -3.5339 | -0.28839 | 0.050354 | 0.51269 | 75.0916 | 75.3845 | 119.0231 | 122.4884 | 0.33875 | 122.6074 | 85.6476 | -0.28839 | 122.4884 | 0.33875 | 85.6476 | 119.0231 | 122.6074 | -122.731 | -122.8455
2082.1562 | 122.6715 | -122.4106 | 0.064087 | 0.0096895 | 0.014535 | 0.031902 | 0.032114 | 0.041857 | -0.031063 | 0.070171 | -122.1817 | 0.068665 | -122.7081 | -122.3053 | -3.5751 | -37.0148 | -47.3969 | -47.1359 | 0.15564 | -122.699 | -0.29755 | 0.004578 | 0.22888 | 0.10529 | -3.6392 | -0.28839 | 0.091553 | 0.52643 | 75.0137 | 75.2747 | 118.8354 | 122.4792 | 0.22888 | 122.5662 | 85.3958 | -0.28839 | 122.4792 | 0.22888 | 85.3958 | 118.8354 | 122.5662 | -122.7722 | -122.7631
2083.9531 | 122.6028 | -122.4243 | 0.086975 | 0.00206 | 0.016244 | 0.03532 | 0.033609 | 0.042071 | -0.033626 | 0.069103 | -122.1634 | 0.064087 | -122.6807 | -122.3328 | -3.6713 | -37.1658 | -47.3694 | -47.168 | 0.15106 | -122.7264 | -0.25635 | -0.022888 | 0.26093 | 0.091552 | -3.7582 | -0.30212 | 0.064087 | 0.51727 | 75.0549 | 75.2563 | 118.7531 | 122.4884 | 0.26093 | 122.5754 | 85.2585 | -0.30212 | 122.4884 | 0.26093 | 85.2585 | 118.7531 | 122.5754 | -122.7676 | -122.8134
2085.6562 | 122.6212 | -122.4197 | 0.086975 | 0.017319 | 0.013253 | 0.030193 | 0.030191 | 0.040575 | -0.033413 | 0.067394 | -122.1863 | 0.086975 | -122.7127 | -122.3511 | -3.7354 | -37.2803 | -47.1771 | -47.0352 | 0.16937 | -122.7173 | -0.29297 | 0 | 0.23346 | 0.068665 | -3.8223 | -0.29755 | 0.082398 | 0.52643 | 75.2426 | 75.3845 | 118.6844 | 122.5067 | 0.23346 | 122.5891 | 85.1395 | -0.29755 | 122.5067 | 0.23346 | 85.1395 | 118.6844 | 122.5891 | -122.7997 | -122.8043
2087.4375 | 122.5479 | -122.438 | 0.091553 | 0.0096895 | 0.016458 | 0.03297 | 0.031046 | 0.040362 | -0.031917 | 0.070171 | -122.1359 | 0.082397 | -122.6761 | -122.2824 | -3.7125 | -37.3261 | -47.1359 | -46.907 | 0.15106 | -122.7081 | -0.23804 | -0.009156 | 0.30212 | 0.15564 | -3.804 | -0.27008 | 0.059509 | 0.54016 | 75.3021 | 75.531 | 118.7256 | 122.5204 | 0.30212 | 122.5891 | 85.112 | -0.27008 | 122.5204 | 0.30212 | 85.112 | 118.7256 | 122.5891 | -122.7676 | -122.7997
2089.1719 | 122.6852 | -122.4152 | 0.07782 | 0.0096895 | 0.01368 | 0.029553 | 0.023996 | 0.040148 | -0.028499 | 0.069957 | -122.1359 | 0.068665 | -122.6257 | -122.2916 | -3.7445 | -37.3489 | -47.2458 | -46.8567 | 0.15564 | -122.7127 | -0.21057 | -0.009155 | 0.27924 | 0.1236 | -3.8223 | -0.29755 | 0.07782 | 0.48981 | 75.1694 | 75.5585 | 118.6707 | 122.4838 | 0.27924 | 122.5708 | 85.0662 | -0.29755 | 122.4838 | 0.27924 | 85.0662 | 118.6707 | 122.5708 | -122.7036 | -122.7905
2090.9531 | 122.58 | -122.4243 | 0.09613 | 0.0096895 | 0.017953 | 0.034679 | 0.029337 | 0.041644 | -0.03149 | 0.068889 | -122.1542 | 0.10529 | -122.6624 | -122.319 | -3.8544 | -37.3444 | -46.8842 | -46.7194 | 0.16479 | -122.7402 | -0.23804 | 0.009156 | 0.27008 | 0.10529 | -3.9505 | -0.31586 | 0.068665 | 0.50812 | 75.5402 | 75.705 | 118.5699 | 122.5296 | 0.27008 | 122.5891 | 85.08 | -0.31586 | 122.5296 | 0.27008 | 85.08 | 118.5699 | 122.5891 | -122.7585 | -122.8363
2092.7344 | 122.6166 | -122.4335 | 0.091553 | 0.0096895 | 0.015389 | 0.03297 | 0.028696 | 0.040789 | -0.032985 | 0.070171 | -122.1863 | 0.082397 | -122.7127 | -122.3282 | -3.9322 | -37.3352 | -46.7102 | -46.6141 | 0.16937 | -122.7448 | -0.27924 | -0.009156 | 0.24719 | 0.10529 | -4.0237 | -0.31128 | 0.07782 | 0.52643 | 75.7233 | 75.8194 | 118.5013 | 122.5159 | 0.24719 | 122.6028 | 85.0983 | -0.31128 | 122.5159 | 0.24719 | 85.0983 | 118.5013 | 122.6028 | -122.8043 | -122.8363
2094.5312 | 122.6532 | -122.438 | 0.082397 | 0.0096895 | 0.01368 | 0.030834 | 0.026987 | 0.041003 | -0.028713 | 0.069316 | -122.0718 | 0.041199 | -122.6532 | -122.2504 | -3.8956 | -37.4222 | -46.994 | -46.5775 | 0.10529 | -122.6898 | -0.21515 | -0.041198 | 0.36621 | 0.18768 | -3.978 | -0.25177 | 0.022889 | 0.58136 | 75.444 | 75.8606 | 118.5425 | 122.4792 | 0.36621 | 122.5433 | 85.0159 | -0.25177 | 122.4792 | 0.36621 | 85.0159 | 118.5425 | 122.5433 | -122.7356 | -122.7722
2096.25 | 122.7036 | -122.3969 | 0.07782 | 0.00206 | 0.015603 | 0.026775 | 0.02656 | 0.039721 | -0.030208 | 0.069744 | -122.1451 | 0.054932 | -122.644 | -122.2961 | -4.0649 | -37.6968 | -47.0398 | -46.7972 | 0.13275 | -122.7219 | -0.24719 | -0.022888 | 0.25177 | 0.10071 | -4.1428 | -0.32501 | 0.054931 | 0.49896 | 75.3571 | 75.5997 | 118.3319 | 122.4518 | 0.25177 | 122.5296 | 84.7 | -0.32501 | 122.4518 | 0.25177 | 84.7 | 118.3319 | 122.5296 | -122.7219 | -122.7997
2098.0312 | 122.699 | -122.3969 | 0.064087 | 0.0096895 | 0.016244 | 0.033825 | 0.032968 | 0.041216 | -0.031277 | 0.070384 | -122.2046 | 0.07782 | -122.7264 | -122.3557 | -4.1336 | -37.4771 | -46.788 | -46.788 | 0.16022 | -122.731 | -0.32959 | 0.013733 | 0.19226 | 0.041199 | -4.1977 | -0.33417 | 0.09613 | 0.52185 | 75.6088 | 75.6088 | 118.2632 | 122.4747 | 0.19226 | 122.5571 | 84.9197 | -0.33417 | 122.4747 | 0.19226 | 84.9197 | 118.2632 | 122.5571 | -122.7905 | -122.7951
2099.7344 | 122.6349 | -122.406 | 0.082397 | 0.0096895 | 0.015176 | 0.031048 | 0.024637 | 0.03908 | -0.030849 | 0.070812 | -122.0901 | 0.059509 | -122.6486 | -122.2229 | -4.0604 | -37.5504 | -47.0398 | -46.6965 | 0.12817 | -122.6944 | -0.24262 | -0.022888 | 0.31586 | 0.18311 | -4.1428 | -0.28839 | 0.045777 | 0.55847 | 75.3662 | 75.7095 | 118.3456 | 122.4655 | 0.31586 | 122.5342 | 84.8557 | -0.28839 | 122.4655 | 0.31586 | 84.8557 | 118.3456 | 122.5342 | -122.731 | -122.7768
2101.5312 | 122.6807 | -122.4014 | 0.064087 | 0.024948 | 0.017739 | 0.036175 | 0.033609 | 0.041003 | -0.032558 | 0.073375 | -122.1909 | 0.091553 | -122.699 | -122.3328 | -4.2938 | -37.793 | -46.9162 | -46.9528 | 0.15106 | -122.7356 | -0.29755 | 0.027466 | 0.21057 | 0.068664 | -4.3579 | -0.33417 | 0.086975 | 0.50812 | 75.4852 | 75.4486 | 118.1076 | 122.493 | 0.21057 | 122.5525 | 84.6085 | -0.33417 | 122.493 | 0.21057 | 84.6085 | 118.1076 | 122.5525 | -122.7631 | -122.7997
2103.3125 | 122.699 | -122.4197 | 0.068665 | 0.0096895 | 0.01368 | 0.035748 | 0.024851 | 0.040575 | -0.031917 | 0.070384 | -122.1039 | 0.059509 | -122.6624 | -122.287 | -4.2664 | -37.7747 | -46.9574 | -46.843 | 0.14191 | -122.6898 | -0.24261 | -0.009156 | 0.31586 | 0.13275 | -4.335 | -0.27008 | 0.073242 | 0.55847 | 75.4623 | 75.5768 | 118.1534 | 122.4792 | 0.31586 | 122.5616 | 84.6451 | -0.27008 | 122.4792 | 0.31586 | 84.6451 | 118.1534 | 122.5616 | -122.731 | -122.7585
2105.0469 | 122.5983 | -122.4472 | 0.07782 | 0.0096895 | 0.017739 | 0.031475 | 0.032327 | 0.038866 | -0.03149 | 0.071025 | -122.168 | 0.073242 | -122.7036 | -122.3145 | -4.3762 | -37.944 | -46.8613 | -46.8887 | 0.16022 | -122.7402 | -0.25635 | -0.004578 | 0.27924 | 0.13275 | -4.454 | -0.29297 | 0.082397 | 0.53558 | 75.5859 | 75.5585 | 118.071 | 122.5204 | 0.27924 | 122.6074 | 84.5032 | -0.29297 | 122.5204 | 0.27924 | 84.5032 | 118.071 | 122.6074 | -122.7814 | -122.818
2106.8125 | 122.699 | -122.4106 | 0.068665 | 0.00206 | 0.013894 | 0.035748 | 0.025919 | 0.037585 | -0.03149 | 0.072307 | -122.1268 | 0.064087 | -122.6715 | -122.2824 | -4.4083 | -38.0493 | -47.1497 | -46.9345 | 0.14648 | -122.7081 | -0.26093 | -0.004578 | 0.28381 | 0.12817 | -4.4769 | -0.29755 | 0.077819 | 0.54474 | 75.2609 | 75.4761 | 118.0023 | 122.4747 | 0.28381 | 122.5571 | 84.3613 | -0.29755 | 122.4747 | 0.28381 | 84.3613 | 118.0023 | 122.5571 | -122.7402 | -122.7768
2108.5469 | 122.644 | -122.4197 | 0.07782 | 0.017319 | 0.016671 | 0.038738 | 0.032114 | 0.041644 | -0.030849 | 0.068035 | -122.0581 | 0.041199 | -122.6395 | -122.2229 | -4.4449 | -38.0264 | -47.3007 | -47.0123 | 0.10071 | -122.7036 | -0.21973 | -0.036621 | 0.36163 | 0.19684 | -4.5227 | -0.28381 | 0.022888 | 0.58136 | 75.119 | 75.4074 | 117.9749 | 122.4609 | 0.36163 | 122.5204 | 84.3933 | -0.28381 | 122.4609 | 0.36163 | 84.3933 | 117.9749 | 122.5204 | -122.7173 | -122.7814
2110.3281 | 122.6303 | -122.4289 | 0.11902 | 0.017319 | 0.016458 | 0.035107 | 0.031046 | 0.039935 | -0.028927 | 0.071239 | -122.168 | 0.091553 | -122.7081 | -122.3419 | -4.6188 | -38.1638 | -46.9299 | -46.9803 | 0.17853 | -122.7631 | -0.27924 | -0.027466 | 0.26093 | 0.086975 | -4.7379 | -0.33417 | 0.059509 | 0.54016 | 75.499 | 75.4486 | 117.8101 | 122.5204 | 0.26093 | 122.6074 | 84.2651 | -0.33417 | 122.5204 | 0.26093 | 84.2651 | 117.8101 | 122.6074 | -122.8271 | -122.8821
2112.1094 | 122.7127 | -122.3785 | 0.059509 | 0.00206 | 0.017526 | 0.038097 | 0.034036 | 0.042712 | -0.032345 | 0.068889 | -122.1542 | 0.086975 | -122.7127 | -122.3648 | -4.7333 | -38.5162 | -47.1954 | -47.2412 | 0.16479 | -122.7264 | -0.33417 | 0.027466 | 0.2243 | 0.013733 | -4.7928 | -0.3479 | 0.10529 | 0.55847 | 75.1831 | 75.1373 | 117.6453 | 122.4655 | 0.2243 | 122.5433 | 83.8623 | -0.3479 | 122.4655 | 0.2243 | 83.8623 | 117.6453 | 122.5433 | -122.7722 | -122.7859
2113.8125 | 122.644 | -122.4426 | 0.07782 | 0.017319 | 0.01838 | 0.031261 | 0.033609 | 0.042498 | -0.030422 | 0.071239 | -122.1634 | 0.064087 | -122.7402 | -122.3557 | -4.7974 | -38.4567 | -47.0123 | -47.0764 | 0.15564 | -122.7356 | -0.29755 | -0.013733 | 0.27924 | 0.086975 | -4.8752 | -0.29297 | 0.07782 | 0.57678 | 75.4303 | 75.3662 | 117.6453 | 122.5067 | 0.27924 | 122.5983 | 83.9859 | -0.29297 | 122.5067 | 0.27924 | 83.9859 | 117.6453 | 122.5983 | -122.818 | -122.8134
2115.5938 | 122.5708 | -122.4335 | 0.091553 | 0.0096895 | 0.019448 | 0.037029 | 0.029764 | 0.040575 | -0.03149 | 0.071239 | -122.113 | 0.082397 | -122.6715 | -122.2916 | -4.8203 | -38.9282 | -48.2391 | -47.9416 | 0.16479 | -122.7081 | -0.23804 | -0.009156 | 0.32043 | 0.14191 | -4.9118 | -0.27466 | 0.073242 | 0.55847 | 74.1943 | 74.4919 | 117.6132 | 122.5159 | 0.32043 | 122.5983 | 83.5052 | -0.27466 | 122.5159 | 0.32043 | 83.5052 | 117.6132 | 122.5983 | -122.7631 | -122.7997
2117.375 | 122.6212 | -122.438 | 0.10071 | 0.0096895 | 0.019448 | 0.035748 | 0.02955 | 0.042284 | -0.027218 | 0.072093 | -122.1451 | 0.082397 | -122.699 | -122.3465 | -4.9347 | -39.1388 | -48.4222 | -48.1613 | 0.16479 | -122.7448 | -0.26093 | -0.018311 | 0.29297 | 0.091552 | -5.0354 | -0.3067 | 0.064087 | 0.55389 | 74.0158 | 74.2767 | 117.5034 | 122.5204 | 0.29297 | 122.6028 | 83.2993 | -0.3067 | 122.5204 | 0.29297 | 83.2993 | 117.5034 | 122.6028 | -122.7997 | -122.8455
2119.1719 | 122.6486 | -122.4335 | 0.10986 | 0.0096895 | 0.016458 | 0.038738 | 0.027841 | 0.039294 | -0.029995 | 0.072521 | -122.0444 | 0.045776 | -122.6669 | -122.2321 | -4.9438 | -39.1571 | -48.9944 | -48.3078 | 0.11444 | -122.7173 | -0.23346 | -0.064087 | 0.3891 | 0.20142 | -5.0537 | -0.28381 | 0.004578 | 0.62256 | 73.439 | 74.1257 | 117.4896 | 122.4792 | 0.3891 | 122.5479 | 83.2764 | -0.28381 | 122.4792 | 0.3891 | 83.2764 | 117.4896 | 122.5479 | -122.7768 | -122.8271
2120.9375 | 122.6166 | -122.4289 | 0.091553 | 0.0096895 | 0.016458 | 0.034039 | 0.032114 | 0.03908 | -0.030422 | 0.071666 | -122.1451 | 0.091553 | -122.6898 | -122.3602 | -5.1819 | -39.5874 | -49.4156 | -48.9075 | 0.18768 | -122.7081 | -0.26093 | 0 | 0.28381 | 0.068665 | -5.2734 | -0.27924 | 0.09613 | 0.54474 | 73.0133 | 73.5214 | 117.247 | 122.5204 | 0.28381 | 122.6166 | 82.8415 | -0.27924 | 122.5204 | 0.28381 | 82.8415 | 117.247 | 122.6166 | -122.7814 | -122.7997
2122.6562 | 122.644 | -122.4197 | 0.054932 | -0.0055695 | 0.016885 | 0.037884 | 0.029337 | 0.041857 | -0.030849 | 0.073802 | -122.0123 | 0.054932 | -122.6624 | -122.2366 | -5.1453 | -39.1434 | -49.0402 | -48.381 | 0.13275 | -122.7127 | -0.24261 | 0 | 0.40741 | 0.18311 | -5.2002 | -0.29297 | 0.077819 | 0.65002 | 73.3795 | 74.0387 | 117.2745 | 122.4747 | 0.40741 | 122.5525 | 83.2764 | -0.29297 | 122.4747 | 0.40741 | 83.2764 | 117.2745 | 122.5525 | -122.7173 | -122.7676
2124.4531 | 122.6028 | -122.4518 | 0.10986 | 0.0096895 | 0.015817 | 0.038525 | 0.028482 | 0.038226 | -0.028927 | 0.07188 | -122.0169 | 0.045776 | -122.6486 | -122.2137 | -5.2689 | -39.299 | -49.2554 | -48.587 | 0.11444 | -122.7264 | -0.19684 | -0.064087 | 0.43487 | 0.23804 | -5.3787 | -0.27466 | 0.004578 | 0.63171 | 73.1964 | 73.8647 | 117.1829 | 122.4976 | 0.43487 | 122.5662 | 83.1528 | -0.27466 | 122.4976 | 0.43487 | 83.1528 | 117.1829 | 122.5662 | -122.7585 | -122.8363
2126.2344 | 122.5571 | -122.4335 | 0.10529 | 0.0096895 | 0.019448 | 0.038097 | 0.033182 | 0.03908 | -0.03149 | 0.075511 | -122.0535 | 0.068665 | -122.6944 | -122.2824 | -5.4886 | -39.4501 | -49.1455 | -48.7061 | 0.17395 | -122.731 | -0.26093 | -0.036621 | 0.37994 | 0.15106 | -5.5939 | -0.29755 | 0.068664 | 0.64087 | 73.288 | 73.7274 | 116.9449 | 122.5021 | 0.37994 | 122.6074 | 82.9834 | -0.29755 | 122.5021 | 0.37994 | 82.9834 | 116.9449 | 122.6074 | -122.7997 | -122.8363
2127.9375 | 122.6761 | -122.4152 | 0.082397 | 0.017319 | 0.015603 | 0.036175 | 0.025919 | 0.037798 | -0.027431 | 0.071666 | -122.0718 | 0.036621 | -122.6486 | -122.2687 | -5.5984 | -39.5142 | -49.8138 | -49.0448 | 0.13275 | -122.7219 | -0.23346 | -0.045776 | 0.34332 | 0.14648 | -5.6808 | -0.3067 | 0.050354 | 0.57678 | 72.6013 | 73.3704 | 116.8167 | 122.4518 | 0.34332 | 122.5479 | 82.901 | -0.3067 | 122.4518 | 0.34332 | 82.901 | 116.8167 | 122.5479 | -122.731 | -122.8043
2129.7344 | 122.699 | -122.3831 | 0.068665 | 0.017319 | 0.017739 | 0.038097 | 0.026773 | 0.038866 | -0.027218 | 0.072948 | -122.0535 | 0.045776 | -122.6257 | -122.3099 | -5.809 | -39.592 | -49.8962 | -49.1821 | 0.15106 | -122.7264 | -0.24261 | -0.022889 | 0.32959 | 0.073243 | -5.8777 | -0.34332 | 0.082397 | 0.5722 | 72.4869 | 73.201 | 116.5741 | 122.4289 | 0.32959 | 122.5342 | 82.7911 | -0.34332 | 122.4289 | 0.32959 | 82.7911 | 116.5741 | 122.5342 | -122.6944 | -122.7951
2131.5156 | 122.7036 | -122.3877 | 0.07782 | 0.0096895 | 0.019021 | 0.040234 | 0.035959 | 0.039507 | -0.028499 | 0.075511 | -122.0993 | 0.068665 | -122.7081 | -122.3465 | -6.0608 | -39.8392 | -50.0656 | -49.4339 | 0.16937 | -122.7402 | -0.32044 | -0.009155 | 0.28839 | 0.041198 | -6.1386 | -0.35248 | 0.091553 | 0.60883 | 72.3221 | 72.9538 | 116.3269 | 122.4564 | 0.28839 | 122.5571 | 82.5485 | -0.35248 | 122.4564 | 0.28839 | 82.5485 | 116.3269 | 122.5571 | -122.7859 | -122.818
2133.25 | 122.6486 | -122.4289 | 0.07782 | 0.0096895 | 0.019021 | 0.041943 | 0.032968 | 0.041003 | -0.02914 | 0.075084 | -121.9894 | 0.045776 | -122.6532 | -122.2458 | -6.1203 | -39.679 | -50.5554 | -49.6033 | 0.11902 | -122.699 | -0.2243 | -0.032044 | 0.43945 | 0.1831 | -6.1981 | -0.27008 | 0.041199 | 0.66376 | 71.8735 | 72.8256 | 116.3086 | 122.4747 | 0.43945 | 122.5479 | 82.7499 | -0.27008 | 122.4747 | 0.43945 | 82.7499 | 116.3086 | 122.5479 | -122.731 | -122.7768
2135.0312 | 122.6028 | -122.4564 | 0.09613 | 0.0096895 | 0.017953 | 0.040234 | 0.035318 | 0.041857 | -0.031917 | 0.075725 | -122.0581 | 0.07782 | -122.7356 | -122.3236 | -6.3538 | -39.8254 | -50.3998 | -49.8047 | 0.17395 | -122.7127 | -0.27924 | -0.01831 | 0.39826 | 0.13275 | -6.4499 | -0.25635 | 0.07782 | 0.67749 | 72.0566 | 72.6517 | 116.1026 | 122.5342 | 0.39826 | 122.6303 | 82.6309 | -0.25635 | 122.5342 | 0.39826 | 82.6309 | 116.1026 | 122.6303 | -122.8317 | -122.8088
2136.7344 | 122.6624 | -122.4106 | 0.07782 | 0.017319 | 0.021371 | 0.043011 | 0.030618 | 0.04143 | -0.028927 | 0.074871 | -122.0627 | 0.059509 | -122.6898 | -122.2961 | -6.4545 | -39.8163 | -51.1047 | -50.4593 | 0.15564 | -122.699 | -0.27924 | -0.018311 | 0.3479 | 0.11444 | -6.5323 | -0.28839 | 0.07782 | 0.62714 | 71.3058 | 71.9513 | 115.9561 | 122.4701 | 0.3479 | 122.5662 | 82.5943 | -0.28839 | 122.4701 | 0.3479 | 82.5943 | 115.9561 | 122.5662 | -122.7676 | -122.7768
2138.5156 | 122.644 | -122.4106 | 0.09613 | -0.0055695 | 0.017739 | 0.039593 | 0.033396 | 0.043566 | -0.030636 | 0.076366 | -122.081 | 0.082397 | -122.699 | -122.3465 | -6.6879 | -39.6057 | -50.4684 | -50.6516 | 0.16479 | -122.731 | -0.28839 | -0.013733 | 0.32959 | 0.064086 | -6.7841 | -0.32044 | 0.068665 | 0.61798 | 71.9421 | 71.759 | 115.7227 | 122.493 | 0.32959 | 122.5754 | 82.8049 | -0.32044 | 122.493 | 0.32959 | 82.8049 | 115.7227 | 122.5754 | -122.7951 | -122.8271
2140.2969 | 122.6028 | -122.438 | 0.10071 | 0.00206 | 0.017312 | 0.042797 | 0.027628 | 0.040362 | -0.028927 | 0.076152 | -122.0352 | 0.059509 | -122.6852 | -122.2916 | -6.8253 | -39.6927 | -50.9674 | -51.0315 | 0.14648 | -122.7036 | -0.24719 | -0.041199 | 0.40283 | 0.14648 | -6.926 | -0.2655 | 0.045776 | 0.65002 | 71.4706 | 71.4066 | 115.6128 | 122.4976 | 0.40283 | 122.5845 | 82.7454 | -0.2655 | 122.4976 | 0.40283 | 82.7454 | 115.6128 | 122.5845 | -122.7859 | -122.8043
2142.0156 | 122.6898 | -122.4014 | 0.07782 | -0.0055695 | 0.019875 | 0.042584 | 0.027841 | 0.038866 | -0.028927 | 0.075511 | -121.9894 | 0.050354 | -122.6166 | -122.2824 | -6.9717 | -39.9445 | -51.9287 | -51.4938 | 0.12817 | -122.7219 | -0.21515 | -0.027466 | 0.41199 | 0.11902 | -7.0496 | -0.32044 | 0.050354 | 0.62714 | 70.4727 | 70.9076 | 115.4297 | 122.4518 | 0.41199 | 122.5296 | 82.457 | -0.32044 | 122.4518 | 0.41199 | 82.457 | 115.4297 | 122.5296 | -122.6944 | -122.7997
2143.7812 | 122.6166 | -122.4243 | 0.10529 | 0.0096895 | 0.022439 | 0.045788 | 0.034464 | 0.037798 | -0.028286 | 0.075725 | -122.0764 | 0.09613 | -122.7219 | -122.319 | -7.1869 | -40.0085 | -51.9287 | -51.9104 | 0.16022 | -122.7585 | -0.29755 | -0.009156 | 0.3479 | 0.10529 | -7.2922 | -0.33417 | 0.054931 | 0.64545 | 70.4956 | 70.5139 | 115.2374 | 122.5204 | 0.3479 | 122.5845 | 82.4158 | -0.33417 | 122.5204 | 0.3479 | 82.4158 | 115.2374 | 122.5845 | -122.8271 | -122.8638
2145.5 | 122.6257 | -122.438 | 0.10529 | 0.00206 | 0.022225 | 0.048992 | 0.0319 | 0.038439 | -0.029568 | 0.075298 | -122.0764 | 0.086975 | -122.699 | -122.3145 | -7.3242 | -40.1184 | -52.2583 | -52.2308 | 0.1831 | -122.7402 | -0.26093 | -0.018311 | 0.36163 | 0.1236 | -7.4295 | -0.30212 | 0.077819 | 0.62256 | 70.1797 | 70.2072 | 115.1138 | 122.525 | 0.36163 | 122.6212 | 82.3196 | -0.30212 | 122.525 | 0.36163 | 82.3196 | 115.1138 | 122.6212 | -122.8043 | -122.8455
2147.2812 | 122.6898 | -122.3923 | 0.07782 | -0.0055695 | 0.02308 | 0.04707 | 0.03425 | 0.041644 | -0.02914 | 0.078288 | -122.0581 | 0.10071 | -122.6715 | -122.3465 | -7.5302 | -40.1733 | -52.7435 | -52.4963 | 0.16022 | -122.7264 | -0.27924 | 0.022888 | 0.33417 | 0.045776 | -7.608 | -0.33417 | 0.082397 | 0.6134 | 69.6487 | 69.8959 | 114.8621 | 122.493 | 0.33417 | 122.5525 | 82.2189 | -0.33417 | 122.493 | 0.33417 | 82.2189 | 114.8621 | 122.5525 | -122.7493 | -122.8043
2149 | 122.6349 | -122.4335 | 0.10529 | 0.0096895 | 0.022225 | 0.042797 | 0.032968 | 0.039935 | -0.028072 | 0.078929 | -122.0444 | 0.091553 | -122.6761 | -122.3328 | -7.6767 | -40.2695 | -53.5309 | -53.0502 | 0.17395 | -122.7402 | -0.24261 | -0.013733 | 0.3891 | 0.10071 | -7.782 | -0.3067 | 0.068664 | 0.63171 | 68.9026 | 69.3832 | 114.7568 | 122.525 | 0.3891 | 122.6074 | 82.164 | -0.3067 | 122.525 | 0.3891 | 82.164 | 114.7568 | 122.6074 | -122.7814 | -122.8455
2150.7656 | 122.5479 | -122.4335 | 0.10986 | 0.0096895 | 0.021157 | 0.050488 | 0.035105 | 0.040148 | -0.028499 | 0.079784 | -122.0123 | 0.068665 | -122.699 | -122.2733 | -7.7774 | -40.2008 | -53.1601 | -52.858 | 0.15106 | -122.7127 | -0.2655 | -0.041198 | 0.42114 | 0.16022 | -7.8873 | -0.27924 | 0.041199 | 0.68665 | 69.2734 | 69.5755 | 114.6561 | 122.5021 | 0.42114 | 122.5845 | 82.2327 | -0.27924 | 122.5021 | 0.42114 | 82.2327 | 114.6561 | 122.5845 | -122.8088 | -122.8226
2152.5469 | 122.6074 | -122.4472 | 0.11444 | 0.00206 | 0.022225 | 0.048565 | 0.028482 | 0.03908 | -0.027859 | 0.077648 | -121.9894 | 0.07782 | -122.6578 | -122.2778 | -7.9788 | -40.3381 | -53.421 | -53.1326 | 0.17395 | -122.7402 | -0.21057 | -0.036621 | 0.45776 | 0.16937 | -8.0933 | -0.29297 | 0.059509 | 0.66833 | 69.0262 | 69.3146 | 114.4684 | 122.525 | 0.45776 | 122.6212 | 82.1091 | -0.29297 | 122.525 | 0.45776 | 82.1091 | 114.4684 | 122.6212 | -122.7722 | -122.8546
2154.2656 | 122.5891 | -122.4609 | 0.1236 | 0.0096895 | 0.021157 | 0.046215 | 0.029764 | 0.039721 | -0.02914 | 0.077648 | -121.9574 | 0.041199 | -122.6578 | -122.2412 | -8.1253 | -40.4846 | -54.245 | -53.7369 | 0.16022 | -122.7356 | -0.19684 | -0.082397 | 0.50354 | 0.21973 | -8.2489 | -0.27466 | 0.036621 | 0.70038 | 68.2159 | 68.7241 | 114.3356 | 122.5021 | 0.50354 | 122.6212 | 81.9763 | -0.27466 | 122.5021 | 0.50354 | 81.9763 | 114.3356 | 122.6212 | -122.7814 | -122.8592
2156.0469 | 122.5983 | -122.4289 | 0.11444 | 0.0096895 | 0.022653 | 0.046856 | 0.037882 | 0.040575 | -0.031063 | 0.078929 | -122.0078 | 0.07782 | -122.7127 | -122.2916 | -8.3176 | -40.6265 | -55.0049 | -54.2725 | 0.15564 | -122.7264 | -0.28381 | -0.036621 | 0.42114 | 0.13733 | -8.432 | -0.29755 | 0.041199 | 0.70496 | 67.424 | 68.1564 | 114.1113 | 122.5067 | 0.42114 | 122.5845 | 81.8024 | -0.29755 | 122.5067 | 0.42114 | 81.8024 | 114.1113 | 122.5845 | -122.8271 | -122.8409
2157.8281 | 122.6166 | -122.4426 | 0.09613 | -0.013199 | 0.02073 | 0.049419 | 0.0319 | 0.038653 | -0.028072 | 0.078929 | -122.0444 | 0.073242 | -122.6898 | -122.3419 | -8.4778 | -40.7593 | -55.6824 | -56.6574 | 0.16937 | -122.7448 | -0.24719 | -0.022888 | 0.39825 | 0.10071 | -8.5739 | -0.30212 | 0.073243 | 0.64545 | 66.7603 | 65.7852 | 113.9648 | 122.5159 | 0.39825 | 122.612 | 81.6834 | -0.30212 | 122.5159 | 0.39825 | 81.6834 | 113.9648 | 122.612 | -122.7859 | -122.8409
2159.6406 | 122.6028 | -122.4472 | 0.09613 | 0.0096895 | 0.023293 | 0.048992 | 0.030405 | 0.037371 | -0.02615 | 0.078288 | -121.9849 | 0.073242 | -122.6669 | -122.3053 | -8.6197 | -40.7684 | -54.8584 | -56.543 | 0.17395 | -122.731 | -0.21973 | -0.022888 | 0.46234 | 0.14191 | -8.7158 | -0.28381 | 0.07782 | 0.68207 | 67.5888 | 65.9042 | 113.8275 | 122.5204 | 0.46234 | 122.6212 | 81.6788 | -0.28381 | 122.5204 | 0.46234 | 81.6788 | 113.8275 | 122.6212 | -122.7631 | -122.8271
2161.4375 | 122.6303 | -122.406 | 0.091553 | 0.017319 | 0.02543 | 0.048992 | 0.029764 | 0.037585 | -0.02615 | 0.080852 | -121.9437 | 0.054932 | -122.6395 | -122.2229 | -8.7021 | -40.9378 | -55.7602 | -56.9138 | 0.13733 | -122.731 | -0.23346 | -0.036621 | 0.46234 | 0.18311 | -8.7936 | -0.32501 | 0.045776 | 0.6958 | 66.6458 | 65.4922 | 113.7039 | 122.4609 | 0.46234 | 122.5433 | 81.4682 | -0.32501 | 122.4609 | 0.46234 | 81.4682 | 113.7039 | 122.5433 | -122.731 | -122.8226
2163.1719 | 122.6532 | -122.4106 | 0.091553 | 0.0096895 | 0.021798 | 0.051342 | 0.032327 | 0.036944 | -0.024441 | 0.081493 | -121.9345 | 0.054932 | -122.6486 | -122.2321 | -8.9035 | -40.9241 | -56.7169 | -57.5867 | 0.1236 | -122.7402 | -0.23804 | -0.036621 | 0.47607 | 0.17853 | -8.9951 | -0.32959 | 0.032043 | 0.71411 | 65.6937 | 64.8239 | 113.5071 | 122.4655 | 0.47607 | 122.5342 | 81.4865 | -0.32959 | 122.4655 | 0.47607 | 81.4865 | 113.5071 | 122.5342 | -122.7402 | -122.8317
2164.9688 | 122.5708 | -122.4335 | 0.11902 | 0.0096895 | 0.018594 | 0.046856 | 0.033396 | 0.038866 | -0.028713 | 0.079997 | -121.9162 | 0.045776 | -122.6715 | -122.2092 | -9.0683 | -41.2857 | -56.9504 | -57.8018 | 0.14648 | -122.6852 | -0.23804 | -0.073243 | 0.51727 | 0.22431 | -9.1873 | -0.25177 | 0.027465 | 0.75531 | 65.4831 | 64.6317 | 113.3652 | 122.4792 | 0.51727 | 122.58 | 81.1478 | -0.25177 | 122.4792 | 0.51727 | 81.1478 | 113.3652 | 122.58 | -122.7905 | -122.8043
2166.6875 | 122.7173 | -122.3831 | 0.07782 | 0.0096895 | 0.024789 | 0.050701 | 0.0366 | 0.040148 | -0.025936 | 0.080425 | -122.0078 | 0.10071 | -122.699 | -122.3328 | -9.4482 | -41.7801 | -57.518 | -58.5754 | 0.19226 | -122.7264 | -0.31586 | 0.022888 | 0.37537 | 0.050354 | -9.5261 | -0.34332 | 0.11444 | 0.69122 | 64.8651 | 63.8077 | 112.9349 | 122.4838 | 0.37537 | 122.5754 | 80.603 | -0.34332 | 122.4838 | 0.37537 | 80.603 | 112.9349 | 122.5754 | -122.7768 | -122.8043
2168.4844 | 122.699 | -122.3694 | 0.10071 | 0.0096895 | 0.027993 | 0.058392 | 0.037241 | 0.042712 | -0.028927 | 0.083415 | -121.9986 | 0.09613 | -122.6852 | -122.3236 | -9.5856 | -41.7206 | -57.9071 | -59.0378 | 0.15564 | -122.7173 | -0.31586 | -0.004578 | 0.37079 | 0.045777 | -9.6863 | -0.3479 | 0.054932 | 0.68665 | 64.4623 | 63.3316 | 112.7838 | 122.4655 | 0.37079 | 122.525 | 80.6488 | -0.3479 | 122.4655 | 0.37079 | 80.6488 | 112.7838 | 122.525 | -122.7859 | -122.818
2170.2344 | 122.6898 | -122.3969 | 0.073242 | 0.00206 | 0.022653 | 0.056683 | 0.031259 | 0.038439 | -0.024868 | 0.080211 | -121.9482 | 0.068665 | -122.6578 | -122.2504 | -9.7366 | -41.8121 | -58.6029 | -59.2438 | 0.13275 | -122.699 | -0.26093 | -0.004577 | 0.44861 | 0.14648 | -9.8099 | -0.30212 | 0.059509 | 0.70953 | 63.7939 | 63.1531 | 112.6602 | 122.4655 | 0.44861 | 122.5296 | 80.5847 | -0.30212 | 122.4655 | 0.44861 | 80.5847 | 112.6602 | 122.5296 | -122.731 | -122.7722
2172.0156 | 122.5708 | -122.4564 | 0.11902 | 0.017319 | 0.02778 | 0.058819 | 0.039591 | 0.040148 | -0.027859 | 0.081066 | -121.9299 | 0.07782 | -122.7264 | -122.2595 | -9.9564 | -41.922 | -59.0012 | -59.8526 | 0.16937 | -122.699 | -0.27008 | -0.041199 | 0.52643 | 0.19684 | -10.0754 | -0.24262 | 0.050354 | 0.79651 | 63.4552 | 62.6038 | 112.5 | 122.5342 | 0.52643 | 122.6257 | 80.5344 | -0.24262 | 122.5342 | 0.52643 | 80.5344 | 112.5 | 122.6257 | -122.8455 | -122.818
2173.7812 | 122.5845 | -122.4289 | 0.10529 | 0.017319 | 0.025643 | 0.057323 | 0.031046 | 0.039721 | -0.027004 | 0.083843 | -121.8567 | 0.054932 | -122.6303 | -122.2092 | -9.9747 | -41.6107 | -58.9828 | -59.7153 | 0.13275 | -122.7036 | -0.20142 | -0.050354 | 0.5722 | 0.21973 | -10.08 | -0.27466 | 0.027465 | 0.77362 | 63.446 | 62.7136 | 112.4542 | 122.4838 | 0.5722 | 122.5616 | 80.8182 | -0.27466 | 122.4838 | 0.5722 | 80.8182 | 112.4542 | 122.5616 | -122.7356 | -122.8088
2175.5 | 122.6074 | -122.4518 | 0.10529 | -0.0055695 | 0.023507 | 0.057537 | 0.031046 | 0.03908 | -0.025722 | 0.083415 | -121.8796 | 0.050354 | -122.6257 | -122.1954 | -10.1395 | -41.8304 | -59.1248 | -60.0906 | 0.12817 | -122.7081 | -0.17395 | -0.054932 | 0.5722 | 0.25635 | -10.2448 | -0.25635 | 0.022888 | 0.74615 | 63.327 | 62.3611 | 112.3123 | 122.5021 | 0.5722 | 122.58 | 80.6213 | -0.25635 | 122.5021 | 0.5722 | 80.6213 | 112.3123 | 122.58 | -122.731 | -122.8134
2177.2188 | 122.6944 | -122.3602 | 0.059509 | 0.0096895 | 0.027139 | 0.063091 | 0.039377 | 0.042925 | -0.028072 | 0.083843 | -121.9757 | 0.10529 | -122.6761 | -122.3419 | -10.6339 | -42.128 | -60.3104 | -61.1938 | 0.19684 | -122.7036 | -0.31586 | 0.045777 | 0.38452 | 0.01831 | -10.6934 | -0.34332 | 0.13733 | 0.70038 | 62.0499 | 61.1664 | 111.7264 | 122.4655 | 0.38452 | 122.5571 | 80.2322 | -0.34332 | 122.4655 | 0.38452 | 80.2322 | 111.7264 | 122.5571 | -122.7356 | -122.7631
2179 | 122.5983 | -122.4289 | 0.10529 | 0.00206 | 0.027993 | 0.061169 | 0.037027 | 0.040575 | -0.028499 | 0.084911 | -121.994 | 0.086975 | -122.7081 | -122.3053 | -10.7025 | -42.3569 | -59.729 | -60.8093 | 0.18768 | -122.7448 | -0.27924 | -0.018311 | 0.43488 | 0.1236 | -10.8078 | -0.31586 | 0.082397 | 0.71411 | 62.6999 | 61.6196 | 111.7264 | 122.5159 | 0.43488 | 122.6166 | 80.072 | -0.31586 | 122.5159 | 0.43488 | 80.072 | 111.7264 | 122.6166 | -122.8134 | -122.85
2180.7812 | 122.6624 | -122.4289 | 0.07782 | 0.00206 | 0.024789 | 0.062023 | 0.034677 | 0.039721 | -0.024868 | 0.086193 | -121.8796 | 0.050354 | -122.6395 | -122.2504 | -10.9131 | -42.952 | -60.7224 | -61.3541 | 0.13275 | -122.699 | -0.21057 | -0.027466 | 0.54932 | 0.17853 | -10.9909 | -0.27008 | 0.054931 | 0.75989 | 61.7065 | 61.0748 | 111.5158 | 122.4792 | 0.54932 | 122.5616 | 79.4769 | -0.27008 | 122.4792 | 0.54932 | 79.4769 | 111.5158 | 122.5616 | -122.7173 | -122.7768
2182.4844 | 122.5937 | -122.4106 | 0.11902 | 0.017319 | 0.027566 | 0.064159 | 0.037668 | 0.038866 | -0.027645 | 0.084697 | -121.9391 | 0.09613 | -122.7219 | -122.2778 | -11.2427 | -43.364 | -61.3495 | -62.0361 | 0.1831 | -122.6944 | -0.31128 | -0.022889 | 0.4715 | 0.13275 | -11.3617 | -0.28381 | 0.064086 | 0.78278 | 61.0611 | 60.3745 | 111.1679 | 122.5067 | 0.4715 | 122.5937 | 79.0466 | -0.28381 | 122.5067 | 0.4715 | 79.0466 | 111.1679 | 122.5937 | -122.8409 | -122.8134
2184.2188 | 122.7081 | -122.3969 | 0.064087 | 0.00206 | 0.026498 | 0.065655 | 0.032541 | 0.039507 | -0.027859 | 0.084484 | -121.8704 | 0.059509 | -122.6074 | -122.2778 | -11.5036 | -43.364 | -61.9537 | -62.2742 | 0.14648 | -122.7081 | -0.21057 | -0.004578 | 0.52643 | 0.11902 | -11.5677 | -0.31128 | 0.082397 | 0.737 | 60.4431 | 60.1227 | 110.8932 | 122.4564 | 0.52643 | 122.5433 | 79.0329 | -0.31128 | 122.4564 | 0.52643 | 79.0329 | 110.8932 | 122.5433 | -122.6715 | -122.7722
2185.9688 | 122.6715 | -122.3785 | 0.10071 | 0.00206 | 0.02842 | 0.067577 | 0.041513 | 0.04143 | -0.025722 | 0.087474 | -121.8201 | 0.11902 | -122.6624 | -122.319 | -11.6913 | -43.4097 | -61.9904 | -62.4481 | 0.15564 | -122.7448 | -0.28381 | 0.018311 | 0.55847 | 0.059509 | -11.792 | -0.36621 | 0.054932 | 0.84229 | 60.3882 | 59.9304 | 110.6873 | 122.4976 | 0.55847 | 122.5342 | 78.9688 | -0.36621 | 122.4976 | 0.55847 | 78.9688 | 110.6873 | 122.5342 | -122.7631 | -122.8455
2187.6875 | 122.6532 | -122.4152 | 0.09613 | 0.0096895 | 0.025002 | 0.072491 | 0.035959 | 0.040789 | -0.027004 | 0.08662 | -121.8384 | 0.041199 | -122.6257 | -122.2137 | -11.7188 | -43.5333 | -61.9034 | -62.4527 | 0.11902 | -122.6532 | -0.21057 | -0.054931 | 0.57678 | 0.20142 | -11.8149 | -0.23804 | 0.022889 | 0.78735 | 60.5118 | 59.9625 | 110.6964 | 122.4564 | 0.57678 | 122.5342 | 78.8818 | -0.23804 | 122.4564 | 0.57678 | 78.8818 | 110.6964 | 122.5342 | -122.7219 | -122.7493
2189.4062 | 122.5937 | -122.4014 | 0.082397 | 0.0096895 | 0.029275 | 0.070355 | 0.038736 | 0.041644 | -0.028072 | 0.087047 | -121.8933 | 0.09613 | -122.699 | -122.319 | -12.204 | -43.5562 | -62.3566 | -62.8052 | 0.17853 | -122.7219 | -0.29755 | 0.013733 | 0.50812 | 0.082397 | -12.2864 | -0.32044 | 0.096131 | 0.80566 | 60.0449 | 59.5963 | 110.1974 | 122.4976 | 0.50812 | 122.58 | 78.8452 | -0.32044 | 122.4976 | 0.50812 | 78.8452 | 110.1974 | 122.58 | -122.7814 | -122.8043
2191.1094 | 122.6074 | -122.4243 | 0.11902 | 0.0096895 | 0.026498 | 0.0742 | 0.03425 | 0.041003 | -0.026363 | 0.088329 | -121.9162 | 0.11444 | -122.6395 | -122.319 | -12.3642 | -43.2953 | -62.796 | -62.9562 | 0.17853 | -122.7448 | -0.21515 | -0.004578 | 0.50812 | 0.10529 | -12.4832 | -0.32043 | 0.059509 | 0.72327 | 59.6283 | 59.4681 | 110.0601 | 122.5388 | 0.50812 | 122.6028 | 79.129 | -0.32043 | 122.5388 | 0.50812 | 79.129 | 110.0601 | 122.6028 | -122.7585 | -122.8638
2192.8438 | 122.58 | -122.4472 | 0.11444 | 0.0096895 | 0.027139 | 0.075909 | 0.040659 | 0.040789 | -0.02679 | 0.087474 | -121.875 | 0.086975 | -122.6898 | -122.2778 | -12.5015 | -43.4738 | -62.6404 | -62.9425 | 0.17395 | -122.7219 | -0.24261 | -0.027466 | 0.5722 | 0.16937 | -12.616 | -0.27466 | 0.059509 | 0.81482 | 59.8068 | 59.5047 | 109.9457 | 122.5342 | 0.5722 | 122.6212 | 78.9734 | -0.27466 | 122.5342 | 0.5722 | 78.9734 | 109.9457 | 122.6212 | -122.8043 | -122.8363
2194.5469 | 122.5433 | -122.4243 | 0.13733 | 0.0096895 | 0.026498 | 0.081463 | 0.035745 | 0.041644 | -0.027004 | 0.090038 | -121.8475 | 0.082397 | -122.6807 | -122.2687 | -12.6343 | -43.1534 | -63.1393 | -63.0753 | 0.16479 | -122.6898 | -0.25635 | -0.054932 | 0.57678 | 0.15564 | -12.7716 | -0.2655 | 0.027466 | 0.83313 | 59.285 | 59.3491 | 109.79 | 122.5067 | 0.57678 | 122.5891 | 79.2709 | -0.2655 | 122.5067 | 0.57678 | 79.2709 | 109.79 | 122.5891 | -122.818 | -122.8271
2196.25 | 121.907 | -121.6095 | 0.10529 | 0.0096895 | 0.00064938 | 0.0011407 | 0.026346 | 0.038226 | -0.02615 | 0.088115 | -0.022888 | 0.10986 | -0.33875 | -121.431 | -12.1902 | -41.7755 | -59.4452 | -58.5526 | 0.14191 | -121.9391 | 121.2708 | 0.004577 | 121.5866 | 0.17853 | -12.2955 | -0.32959 | 0.036621 | 0.31586 | 62.1643 | 63.0569 | 109.4193 | 121.7194 | 121.5866 | 121.7514 | 79.834 | -0.32959 | 121.7194 | 121.5866 | 79.834 | 109.4193 | 121.7514 | -0.44403 | -122.0444
2197.9531 | 122.4609 | -122.2641 | 0.12817 | 0.00206 | 0.0021448 | 0.012035 | 0.038309 | 0.04143 | -0.027645 | 0.089824 | -0.027466 | 0.13733 | -0.36163 | -122.1085 | -12.442 | -41.7847 | -59.0286 | -58.5159 | 0.17395 | -122.5433 | 121.9025 | 0.009155 | 122.2366 | 0.15564 | -12.5702 | -0.27924 | 0.045776 | 0.33417 | 63.2355 | 63.7482 | 109.8221 | 122.4014 | 122.2366 | 122.438 | 80.4794 | -0.27924 | 122.4014 | 122.2366 | 80.4794 | 109.8221 | 122.438 | -0.48981 | -122.6715
2199.6875 | 122.5296 | -122.2778 | 0.10986 | 0.017319 | 0.0029992 | 0.0037043 | 0.034891 | 0.038866 | -0.025295 | 0.091533 | -0.12817 | 0.13733 | -0.35706 | -122.2137 | -12.7029 | -42.0181 | -59.1522 | -58.8776 | 0.18768 | -122.6349 | 121.9208 | 0.027466 | 122.1497 | 0.064087 | -12.8128 | -0.35706 | 0.07782 | 0.22888 | 63.1256 | 63.4003 | 109.5749 | 122.4152 | 122.1497 | 122.4655 | 80.2597 | -0.35706 | 122.4152 | 122.1497 | 80.2597 | 109.5749 | 122.4655 | -0.46692 | -122.7448
2201.3906 | 122.4976 | -122.3328 | 0.1236 | 0.0096895 | 0.00043578 | 0.0075495 | 0.032968 | 0.038866 | -0.024227 | 0.091747 | 0.004578 | 0.09613 | -0.31128 | -122.0856 | -12.8357 | -41.8442 | -59.3079 | -58.5342 | 0.14648 | -122.6166 | 122.0215 | -0.027466 | 122.3373 | 0.24719 | -12.9593 | -0.28381 | 0.022888 | 0.31586 | 63.0249 | 63.7985 | 109.4971 | 122.4289 | 122.3373 | 122.4792 | 80.4886 | -0.28381 | 122.4289 | 122.3373 | 80.4886 | 109.4971 | 122.4792 | -0.43487 | -122.7402
2203.0938 | 122.5342 | -122.3328 | 0.11444 | 0.017319 | 0.0019312 | 0.0081903 | 0.036386 | 0.039294 | -0.028713 | 0.091747 | -0.10071 | 0.13275 | -0.34332 | -122.2092 | -13.2202 | -41.7709 | -59.0286 | -58.9783 | 0.19226 | -122.6303 | 121.9894 | 0.01831 | 122.2321 | 0.1236 | -13.3347 | -0.29755 | 0.07782 | 0.24261 | 63.3041 | 63.3545 | 109.1125 | 122.4655 | 122.2321 | 122.525 | 80.5618 | -0.29755 | 122.4655 | 122.2321 | 80.5618 | 109.1125 | 122.525 | -0.45776 | -122.7448
2204.8125 | 122.5571 | -122.3282 | 0.10986 | -0.0055695 | 0.0019312 | 0.0090447 | 0.040232 | 0.040148 | -0.025722 | 0.092601 | -0.1236 | 0.14648 | -0.37079 | -122.2366 | -13.3026 | -40.9195 | -58.5297 | -58.4885 | 0.16937 | -122.6349 | 121.9574 | 0.036621 | 122.2046 | 0.091553 | -13.4125 | -0.3067 | 0.05951 | 0.24719 | 63.7985 | 63.8397 | 109.0256 | 122.4747 | 122.2046 | 122.4976 | 81.4087 | -0.3067 | 122.4747 | 122.2046 | 81.4087 | 109.0256 | 122.4976 | -0.48065 | -122.7448
2206.6094 | 122.6303 | -122.3328 | 0.082397 | 0.00206 | 0.001504 | 0.012676 | 0.039377 | 0.042712 | -0.028286 | 0.09431 | -0.13275 | 0.13275 | -0.37079 | -122.2595 | -13.5727 | -40.3061 | -59.1614 | -59.3719 | 0.17853 | -122.612 | 121.962 | 0.050354 | 122.2 | 0.073243 | -13.6551 | -0.27924 | 0.096131 | 0.23804 | 63.1714 | 62.9608 | 108.7601 | 122.4655 | 122.2 | 122.5113 | 82.0267 | -0.27924 | 122.4655 | 122.2 | 82.0267 | 108.7601 | 122.5113 | -0.45319 | -122.6944
2208.4219 | 122.5204 | -122.3648 | 0.12817 | 0.00206 | -0.00020502 | 0.0071221 | 0.040872 | 0.04143 | -0.027431 | 0.096019 | -0.073242 | 0.12817 | -0.34332 | -122.1954 | -13.765 | -41.7252 | -58.6945 | -58.9645 | 0.17853 | -122.6212 | 122.0215 | 0 | 122.2916 | 0.16937 | -13.8931 | -0.25635 | 0.050354 | 0.27008 | 63.6703 | 63.4003 | 108.5999 | 122.493 | 122.2916 | 122.5433 | 80.6396 | -0.25635 | 122.493 | 122.2916 | 80.6396 | 108.5999 | 122.5433 | -0.4715 | -122.7493
2210.2344 | 122.5616 | -122.374 | 0.10529 | 0.00206 | -0.00084602 | 0.0028497 | 0.039804 | 0.041003 | -0.028286 | 0.094737 | -0.13275 | 0.13275 | -0.35706 | -122.2458 | -13.9114 | -41.8808 | -58.8638 | -58.9783 | 0.17853 | -122.6395 | 122.0169 | 0.027465 | 122.2412 | 0.12817 | -14.0167 | -0.2655 | 0.073242 | 0.2243 | 63.5101 | 63.3957 | 108.4625 | 122.5067 | 122.2412 | 122.5525 | 80.4932 | -0.2655 | 122.5067 | 122.2412 | 80.4932 | 108.4625 | 122.5525 | -0.46234 | -122.7448
2212.0312 | 122.612 | -122.3648 | 0.091553 | 0.017319 | 0.001504 | 0.012035 | 0.0366 | 0.039294 | -0.022518 | 0.097942 | -0.018311 | 0.10071 | -0.3067 | -122.168 | -13.8428 | -38.7772 | -59.1431 | -59.166 | 0.11444 | -122.644 | 122.0581 | 0.009155 | 122.3465 | 0.19684 | -13.9343 | -0.27924 | 0.022888 | 0.28839 | 63.2217 | 63.1989 | 108.522 | 122.4655 | 122.3465 | 122.4792 | 83.5876 | -0.27924 | 122.4655 | 122.3465 | 83.5876 | 108.522 | 122.4792 | -0.39825 | -122.7356
2213.8125 | 122.6257 | -122.3373 | 0.091553 | 0.0096895 | 0.0032128 | 0.0077631 | 0.042154 | 0.042925 | -0.024654 | 0.099437 | -0.07782 | 0.10529 | -0.31586 | -122.2 | -15.1566 | -38.8962 | -59.491 | -59.0149 | 0.13733 | -122.6486 | 122.0215 | 0.013733 | 122.2595 | 0.13733 | -15.2481 | -0.31128 | 0.045776 | 0.23804 | 62.8464 | 63.3224 | 107.1808 | 122.4426 | 122.2595 | 122.4747 | 83.4412 | -0.31128 | 122.4426 | 122.2595 | 83.4412 | 107.1808 | 122.4747 | -0.40741 | -122.7402
2215.625 | 122.5388 | -122.3785 | 0.13733 | 0.017319 | 0.00043578 | 0.010967 | 0.041941 | 0.042071 | -0.026577 | 0.10072 | -0.068665 | 0.13275 | -0.35248 | -122.2137 | -14.8911 | -38.9923 | -59.4727 | -59.5413 | 0.1831 | -122.644 | 122.0261 | -0.004578 | 122.3099 | 0.16479 | -15.0284 | -0.2655 | 0.045776 | 0.28381 | 62.9059 | 62.8372 | 107.4875 | 122.5113 | 122.3099 | 122.5616 | 83.3862 | -0.2655 | 122.5113 | 122.3099 | 83.3862 | 107.4875 | 122.5616 | -0.48981 | -122.7814
2217.3594 | 122.5433 | -122.3877 | 0.10529 | 0.0096895 | 0.0017176 | 0.0054131 | 0.040232 | 0.040789 | -0.0238 | 0.098796 | -0.13733 | 0.13733 | -0.37079 | -122.2321 | -16.1911 | -39.1159 | -59.6329 | -59.7977 | 0.19684 | -122.6624 | 122.0169 | 0.032043 | 122.2504 | 0.15564 | -16.2964 | -0.27466 | 0.091552 | 0.23346 | 62.7548 | 62.59 | 106.1966 | 122.525 | 122.2504 | 122.5845 | 83.2718 | -0.27466 | 122.525 | 122.2504 | 83.2718 | 106.1966 | 122.5845 | -0.47607 | -122.7676
2219.1406 | 122.5388 | -122.3969 | 0.1236 | 0.017319 | 8.578e-06 | 0.0041315 | 0.0366 | 0.040148 | -0.021236 | 0.099864 | -0.036621 | 0.09613 | -0.3067 | -122.1497 | -15.7196 | -39.3265 | -60.4935 | -60.4568 | 0.14648 | -122.6624 | 122.0901 | -0.027466 | 122.3602 | 0.24719 | -15.8432 | -0.2655 | 0.022888 | 0.27008 | 61.9034 | 61.94 | 106.6772 | 122.493 | 122.3602 | 122.5433 | 83.0704 | -0.2655 | 122.493 | 122.3602 | 83.0704 | 106.6772 | 122.5433 | -0.4303 | -122.7859
2220.9219 | 122.5388 | -122.406 | 0.10529 | 0.017319 | 0.0062036 | 0.013958 | 0.044504 | 0.03908 | -0.024868 | 0.10115 | -0.10071 | 0.15106 | -0.36621 | -122.2137 | -15.7104 | -39.1525 | -59.3445 | -59.7382 | 0.17853 | -122.7036 | 122.0398 | 0.045776 | 122.3053 | 0.19226 | -15.8157 | -0.29755 | 0.073242 | 0.2655 | 63.0615 | 62.6678 | 106.6956 | 122.5571 | 122.3053 | 122.5845 | 83.2535 | -0.29755 | 122.5571 | 122.3053 | 83.2535 | 106.6956 | 122.5845 | -0.4715 | -122.8088
2222.7031 | 122.6578 | -122.3602 | 0.09613 | 0.0096895 | -0.00063242 | 0.0094721 | 0.03895 | 0.04143 | -0.025722 | 0.10072 | -0.045776 | 0.10071 | -0.30212 | -122.1954 | -16.3376 | -40.8875 | -59.7153 | -60.3699 | 0.12817 | -122.6578 | 122.0581 | 0.004578 | 122.3145 | 0.16479 | -16.4337 | -0.29755 | 0.032044 | 0.25635 | 62.645 | 61.9904 | 106.0226 | 122.4609 | 122.3145 | 122.4884 | 81.4728 | -0.29755 | 122.4609 | 122.3145 | 81.4728 | 106.0226 | 122.4884 | -0.39825 | -122.7539
2224.4844 | 122.6074 | -122.3831 | 0.11902 | 0.0096895 | -0.003623 | 0.0092585 | 0.041513 | 0.039721 | -0.025295 | 0.10264 | -0.086975 | 0.1236 | -0.33417 | -122.2321 | -16.4612 | -40.1093 | -61.2259 | -61.9034 | 0.17853 | -122.6486 | 122.049 | 0.004577 | 122.2961 | 0.15106 | -16.5802 | -0.2655 | 0.059509 | 0.24719 | 61.1572 | 60.4797 | 105.9219 | 122.5067 | 122.2961 | 122.5616 | 82.2739 | -0.2655 | 122.5067 | 122.2961 | 82.2739 | 105.9219 | 122.5616 | -0.45319 | -122.7676
2226.2188 | 122.644 | -122.3694 | 0.09613 | 0.00206 | 0.00043578 | 0.010326 | 0.044718 | 0.041857 | -0.024868 | 0.10414 | -0.13733 | 0.13275 | -0.36163 | -122.2458 | -16.713 | -41.8945 | -59.7015 | -61.1801 | 0.16022 | -122.6578 | 122.0078 | 0.036621 | 122.2321 | 0.1236 | -16.8091 | -0.28839 | 0.064087 | 0.2243 | 62.6678 | 61.1893 | 105.6564 | 122.5021 | 122.2321 | 122.5296 | 80.4749 | -0.28839 | 122.5021 | 122.2321 | 80.4749 | 105.6564 | 122.5296 | -0.45776 | -122.7539
2227.9219 | 122.6486 | -122.3877 | 0.086975 | 0.017319 | -0.001914 | 0.0064813 | 0.040232 | 0.04143 | -0.024227 | 0.10478 | -0.064087 | 0.10529 | -0.33417 | -122.1817 | -16.5573 | -42.1738 | -60.0586 | -61.3586 | 0.13275 | -122.6532 | 122.0535 | 0.018311 | 122.3236 | 0.20599 | -16.6443 | -0.2655 | 0.045776 | 0.27008 | 62.3291 | 61.0291 | 105.8304 | 122.493 | 122.3236 | 122.5204 | 80.2139 | -0.2655 | 122.493 | 122.3236 | 80.2139 | 105.8304 | 122.5204 | -0.42114 | -122.7402
2229.6406 | 122.5845 | -122.3831 | 0.11902 | 0.0096895 | 0.0021448 | 0.0064813 | 0.040445 | 0.039721 | -0.02145 | 0.10713 | -0.068665 | 0.10529 | -0.3479 | -122.1497 | -17.9718 | -42.1143 | -64.0091 | -68.5455 | 0.14191 | -122.6486 | 122.0352 | -0.013733 | 122.3145 | 0.23346 | -18.0908 | -0.2655 | 0.022888 | 0.27924 | 58.374 | 53.8376 | 104.4113 | 122.4884 | 122.3145 | 122.525 | 80.2689 | -0.2655 | 122.4884 | 122.3145 | 80.2689 | 104.4113 | 122.525 | -0.46692 | -122.7676
2231.3594 | 122.6532 | -122.3694 | 0.10071 | 0.00206 | 0.0023584 | 0.0051995 | 0.040872 | 0.038653 | -0.023372 | 0.10585 | -0.11444 | 0.1236 | -0.3479 | -122.2092 | -18.3151 | -42.1921 | -60.3058 | -63.0936 | 0.1236 | -122.7173 | 122.0215 | 0.022888 | 122.2549 | 0.16022 | -18.4158 | -0.3479 | 0.022888 | 0.23346 | 62.0636 | 59.2758 | 104.0543 | 122.493 | 122.2549 | 122.493 | 80.1773 | -0.3479 | 122.493 | 122.2549 | 80.1773 | 104.0543 | 122.493 | -0.44861 | -122.818
2233.1406 | 122.644 | -122.3511 | 0.10071 | 0.024948 | 0.0023584 | 0.0045587 | 0.047922 | 0.040362 | -0.021023 | 0.11012 | -0.17853 | 0.1236 | -0.3891 | -122.2824 | -19.3451 | -42.9703 | -61.5875 | -66.1011 | 0.17395 | -122.6578 | 121.962 | 0.022888 | 122.1725 | 0.068664 | -19.4458 | -0.3067 | 0.073242 | 0.21057 | 60.7635 | 56.25 | 103.006 | 122.4747 | 122.1725 | 122.525 | 79.3808 | -0.3067 | 122.4747 | 122.1725 | 79.3808 | 103.006 | 122.525 | -0.48981 | -122.7585
2234.9219 | 122.5754 | -122.406 | 0.11444 | 0.00206 | 0.00043578 | 0.0066949 | 0.04429 | 0.038653 | -0.022091 | 0.11076 | -0.11444 | 0.13733 | -0.37079 | -122.2321 | -20.2972 | -44.3436 | -64.8926 | -70.697 | 0.16937 | -122.6944 | 122.0352 | 0.022888 | 122.2916 | 0.17395 | -20.4117 | -0.28839 | 0.054932 | 0.25635 | 57.5134 | 51.709 | 102.1088 | 122.5433 | 122.2916 | 122.5754 | 78.0624 | -0.28839 | 122.5433 | 122.2916 | 78.0624 | 102.1088 | 122.5754 | -0.48523 | -122.8088
2236.7188 | 122.6669 | -122.3557 | 0.10071 | 0.00206 | 0.00064938 | 0.0092585 | 0.042368 | 0.039294 | -0.019314 | 0.11225 | -0.13275 | 0.11902 | -0.37994 | -122.1725 | -20.8282 | -44.5724 | -66.9022 | -74.263 | 0.15106 | -122.6898 | 121.9757 | 0.018311 | 122.2229 | 0.18311 | -20.929 | -0.33417 | 0.050354 | 0.24719 | 55.4535 | 48.0927 | 101.5274 | 122.4747 | 122.2229 | 122.5067 | 77.7832 | -0.33417 | 122.4747 | 122.2229 | 77.7832 | 101.5274 | 122.5067 | -0.48065 | -122.7905
2238.5156 | 122.6486 | -122.3694 | 0.09613 | 0.017319 | 0.0010766 | 0.0094721 | 0.050699 | 0.04143 | -0.024013 | 0.11482 | -0.1831 | 0.15106 | -0.42572 | -122.2321 | -22.0276 | -46.843 | -67.9459 | -76.1169 | 0.15564 | -122.6532 | 121.9437 | 0.054932 | 122.1863 | 0.13733 | -22.1237 | -0.28381 | 0.05951 | 0.24261 | 54.4235 | 46.2524 | 100.3418 | 122.5204 | 122.1863 | 122.525 | 75.5264 | -0.28381 | 122.5204 | 122.1863 | 75.5264 | 100.3418 | 122.525 | -0.52185 | -122.7493
2240.25 | 122.6715 | -122.3465 | 0.09613 | 0.0096895 | 0.0057764 | 0.0092585 | 0.048776 | 0.041003 | -0.018673 | 0.11546 | -0.21515 | 0.15106 | -0.42114 | -122.2687 | -23.0942 | -47.5388 | -68.573 | -77.916 | 0.18768 | -122.6807 | 121.9254 | 0.054932 | 122.1313 | 0.07782 | -23.1903 | -0.33417 | 0.091553 | 0.20599 | 53.7735 | 44.4305 | 99.2523 | 122.4976 | 122.1313 | 122.5342 | 74.8077 | -0.33417 | 122.4976 | 122.1313 | 74.8077 | 99.2523 | 122.5342 | -0.51727 | -122.7768
2242.0312 | 122.5937 | -122.406 | 0.11902 | 0.00206 | 0.0032128 | 0.0045587 | 0.047708 | 0.03908 | -0.014828 | 0.12315 | -0.19684 | 0.14648 | -0.42114 | -122.2595 | -34.8175 | -49.5529 | -68.2846 | -77.8839 | 0.17395 | -122.731 | 121.9849 | 0.027465 | 122.2092 | 0.14648 | -34.9365 | -0.32501 | 0.054931 | 0.2243 | 54.1214 | 44.5221 | 87.5885 | 122.5525 | 122.2092 | 122.58 | 72.8531 | -0.32501 | 122.5525 | 122.2092 | 72.8531 | 87.5885 | 122.58 | -0.54016 | -122.85
2243.7969 | 122.6532 | -122.3465 | 0.10986 | 0.017319 | -0.00020502 | 0.0079767 | 0.046213 | 0.040148 | -0.0092734 | 0.12849 | -0.13733 | 0.11444 | -0.37994 | -122.1863 | -38.9145 | -50.0244 | -66.1148 | -71.8323 | 0.14191 | -122.6944 | 121.9666 | 0.004578 | 122.2092 | 0.16022 | -39.0244 | -0.3479 | 0.032044 | 0.24261 | 56.2317 | 50.5142 | 83.432 | 122.4609 | 122.2092 | 122.4884 | 72.3221 | -0.3479 | 122.4609 | 122.2092 | 72.3221 | 83.432 | 122.4884 | -0.48981 | -122.8043
2245.5312 | 122.6303 | -122.3694 | 0.09613 | 0.00206 | 0.0019312 | 0.010967 | 0.050913 | 0.042071 | -0.0071372 | 0.13682 | -0.13733 | 0.11444 | -0.40741 | -122.1405 | -48.7747 | -53.7872 | -67.0715 | -72.3724 | 0.14191 | -122.6303 | 121.962 | 0.018311 | 122.2321 | 0.22888 | -48.8708 | -0.26093 | 0.045777 | 0.27008 | 55.2979 | 49.9969 | 73.5947 | 122.4838 | 122.2321 | 122.5113 | 68.5822 | -0.26093 | 122.4838 | 122.2321 | 68.5822 | 73.5947 | 122.5113 | -0.50354 | -122.7264
2247.3125 | 122.5891 | -122.3694 | 0.13733 | 0.0096895 | 0.0021448 | 0.0066949 | 0.053476 | 0.040575 | 0.0097392 | 0.15947 | -0.28381 | 0.16022 | -0.46692 | -122.2504 | -80.2551 | -64.3799 | -68.6325 | -76.6525 | 0.1831 | -122.6944 | 121.9025 | 0.022888 | 122.0856 | 0.11902 | -80.3925 | -0.32501 | 0.045776 | 0.18311 | 53.7369 | 45.7169 | 42.1143 | 122.5296 | 122.0856 | 122.5525 | 57.9895 | -0.32501 | 122.5296 | 122.0856 | 57.9895 | 42.1143 | 122.5525 | -0.60425 | -122.8317
2249.0938 | 122.612 | -122.3785 | 0.11902 | 0.017319 | 0.0034266 | 0.0075495 | 0.057321 | 0.042925 | 0.020207 | 0.17399 | -0.27466 | 0.14648 | -0.4715 | -122.2458 | -98.1262 | -69.548 | -69.1406 | -77.916 | 0.17853 | -122.6349 | 121.907 | 0.027465 | 122.1039 | 0.13275 | -98.2452 | -0.25635 | 0.059509 | 0.19684 | 53.2379 | 44.4626 | 24.2523 | 122.525 | 122.1039 | 122.5571 | 52.8305 | -0.25635 | 122.525 | 122.1039 | 52.8305 | 24.2523 | 122.5571 | -0.59052 | -122.7539
2250.875 | 122.5525 | -122.3969 | 0.14648 | 0.0096895 | 0.0057764 | 0.01054 | 0.051126 | 0.041216 | 0.023625 | 0.17997 | -0.091553 | 0.10529 | -0.35706 | -122.1405 | -102.1133 | -69.3924 | -68.0008 | -76.2726 | 0.16022 | -122.6486 | 122.0398 | -0.041198 | 122.3053 | 0.25635 | -102.2598 | -0.25177 | 0.013733 | 0.2655 | 54.3961 | 46.1243 | 20.2835 | 122.5021 | 122.3053 | 122.5571 | 53.0045 | -0.25177 | 122.5021 | 122.3053 | 53.0045 | 20.2835 | 122.5571 | -0.50354 | -122.7951
2252.6562 | 122.5891 | -122.3602 | 0.15106 | 0.017319 | 0.0064172 | 0.0058405 | 0.054117 | 0.039721 | 0.024479 | 0.18275 | -0.11902 | 0.15106 | -0.32501 | -122.2321 | -104.1092 | -84.9472 | -69.0308 | -77.0599 | 0.21057 | -122.6532 | 122.0352 | 0 | 122.2412 | 0.12817 | -104.2603 | -0.29297 | 0.059509 | 0.20599 | 53.3295 | 45.3003 | 18.251 | 122.5113 | 122.2412 | 122.5708 | 37.413 | -0.29297 | 122.5113 | 122.2412 | 37.413 | 18.251 | 122.5708 | -0.47607 | -122.8043
2254.3906 | 122.5616 | -122.3648 | 0.14648 | 0.0096895 | 0.0066308 | 0.0051995 | 0.054972 | 0.037157 | 0.025761 | 0.18489 | 0.073242 | 0.12817 | -0.16937 | -122.1588 | -104.9011 | -88.9618 | -69.0537 | -79.1611 | 0.14191 | -122.6578 | 122.1954 | -0.01831 | 122.438 | 0.20599 | -105.0476 | -0.29297 | -0.004577 | 0.24261 | 53.3112 | 43.2037 | 17.4637 | 122.493 | 122.438 | 122.5067 | 33.403 | -0.29297 | 122.493 | 122.438 | 33.403 | 17.4637 | 122.5067 | -0.31586 | -122.8043
2256.1875 | 122.5891 | -122.3694 | 0.11902 | -0.0055695 | 0.0072718 | 0.0071221 | 0.054544 | 0.040362 | 0.025761 | 0.19151 | 0.11902 | 0.10986 | -0.15564 | -122.113 | -105.7205 | -87.1765 | -69.0308 | -78.8132 | 0.14648 | -122.6303 | 122.2137 | -0.009156 | 122.4884 | 0.25635 | -105.8395 | -0.26093 | 0.027465 | 0.27466 | 53.3386 | 43.5562 | 16.6489 | 122.4792 | 122.4884 | 122.5159 | 35.1929 | -0.26093 | 122.4792 | 122.4884 | 35.1929 | 16.6489 | 122.5159 | -0.27466 | -122.7493
2257.9688 | 122.6669 | -122.3511 | 0.10071 | 0.00206 | 0.0064172 | 0.0073359 | 0.058389 | 0.037798 | 0.026829 | 0.19236 | 0.07782 | 0.11444 | -0.13733 | -122.1634 | -106.3477 | -85.3912 | -69.3329 | -80.0949 | 0.15564 | -122.6028 | 122.2137 | 0.013733 | 122.4289 | 0.18768 | -106.4484 | -0.25177 | 0.054932 | 0.21515 | 53.0182 | 42.2562 | 16.0034 | 122.4655 | 122.4289 | 122.5067 | 36.9598 | -0.25177 | 122.4655 | 122.4289 | 36.9598 | 16.0034 | 122.5067 | -0.23804 | -122.7036
2259.6875 | 122.5937 | -122.3465 | 0.13275 | 0.0096895 | 0.0085534 | 0.0007135 | 0.060098 | 0.039721 | 0.019993 | 0.19471 | 0.018311 | 0.13275 | -0.16937 | -122.2046 | -106.6727 | -86.293 | -69.5023 | -79.0329 | 0.19684 | -122.6669 | 122.1771 | 0 | 122.3648 | 0.14191 | -106.8054 | -0.32043 | 0.064087 | 0.18768 | 52.8442 | 43.3136 | 15.6738 | 122.4792 | 122.3648 | 122.5433 | 36.0535 | -0.32043 | 122.4792 | 122.3648 | 36.0535 | 15.6738 | 122.5433 | -0.30212 | -122.7997
2261.4844 | 122.6166 | -122.3511 | 0.11902 | 0.0096895 | 0.011971 | 0.0092585 | 0.062021 | 0.040789 | 0.025974 | 0.1977 | 0.054932 | 0.15564 | -0.15106 | -122.168 | -106.8008 | -82.045 | -70.4453 | -84.6771 | 0.15106 | -122.6257 | 122.2 | 0.036621 | 122.406 | 0.1831 | -106.9199 | -0.27466 | 0.032043 | 0.20599 | 51.9058 | 37.6739 | 15.5502 | 122.5067 | 122.406 | 122.5021 | 40.3061 | -0.27466 | 122.5067 | 122.406 | 40.3061 | 15.5502 | 122.5021 | -0.27008 | -122.7448
2263.2031 | 122.5708 | -122.3328 | 0.1236 | 0.0096895 | 0.009408 | 0.0081903 | 0.063516 | 0.04143 | 0.02277 | 0.21714 | 0.064087 | 0.16937 | -0.15564 | -122.1497 | -106.7825 | -58.8547 | -70.0836 | -83.0658 | 0.19684 | -122.6303 | 122.1771 | 0.045777 | 122.3969 | 0.18311 | -106.9061 | -0.29755 | 0.073242 | 0.21973 | 52.2491 | 39.267 | 15.5502 | 122.5021 | 122.3969 | 122.5296 | 63.4781 | -0.29755 | 122.5021 | 122.3969 | 63.4781 | 15.5502 | 122.5296 | -0.27924 | -122.7539
2264.9844 | 122.5983 | -122.3099 | 0.15564 | 0.0096895 | 0.011544 | 0.0056269 | 0.05604 | 0.041857 | 0.025974 | 0.24086 | 0.16937 | 0.17395 | -0.091553 | -122.0444 | -106.0226 | -6.9122 | -69.8914 | -78.9825 | 0.15106 | -122.5891 | 122.2183 | 0.01831 | 122.4792 | 0.2655 | -106.1783 | -0.27924 | -0.004578 | 0.26093 | 52.4185 | 43.3273 | 16.2872 | 122.4838 | 122.4792 | 122.4609 | 115.3976 | -0.27924 | 122.4838 | 122.4792 | 115.3976 | 16.2872 | 122.4609 | -0.24719 | -122.7448
2266.7656 | 122.5525 | -121.9528 | 0.4303 | 0.0096895 | 0.031198 | 0.010754 | 0.05903 | 0.041216 | 0.028538 | 0.63841 | 0.52643 | 0.45776 | 0.21973 | -121.431 | -107.222 | -51.3107 | -74.7208 | -78.3691 | 0.53101 | -122.168 | 122.1725 | 0.027466 | 122.4792 | 0.52185 | -107.6523 | -0.21515 | 0.10071 | 0.3067 | 47.2321 | 43.5837 | 14.7308 | 122.4106 | 122.4792 | 122.4838 | 70.6421 | -0.21515 | 122.4106 | 122.4792 | 70.6421 | 14.7308 | 122.4838 | -0.21057 | -122.5983
2268.5625 | 120.3781 | -91.1728 | 28.5919 | 0.017319 | 3.4707 | 0.0086175 | 0.047067 | -0.010267 | 0.019566 | 7.0123 | 29.4754 | 29.6722 | 8.8394 | -2.179 | -63.3316 | -4.4174 | -16.0538 | -35.701 | 30.3635 | -86.2244 | 100.0122 | 1.0803 | 120.6482 | 88.9938 | -91.9235 | 4.9484 | 1.7715 | 20.636 | 75.119 | 55.4718 | 27.8412 | 120.845 | 120.6482 | 121.5363 | 86.7554 | 4.9484 | 120.845 | 120.6482 | 86.7554 | 27.8412 | 121.5363 | -19.7525 | -114.8163
2270.3438 | 119.6548 | -104.686 | 14.6942 | 0.0096895 | 4.0559 | 0.0090447 | 2.85 | -0.020307 | 0.013371 | 7.0123 | 15.6876 | 16.2872 | 8.8394 | 0.027466 | -75.2014 | 3.5797 | -4.1794 | -41.6931 | 15.6784 | -99.9527 | 113.5254 | 1.593 | 120.3735 | 104.7134 | -89.8956 | 4.7333 | 0.98419 | 6.8481 | 100.5066 | 62.9929 | 29.4846 | 120.9732 | 120.3735 | 120.3644 | 108.2657 | 4.7333 | 120.9732 | 120.3735 | 108.2657 | 29.4846 | 120.3644 | -5.8548 | -114.6469
2272.0625 | 119.9066 | -91.0217 | 28.8071 | 0.00206 | 0.97178 | 0.0049859 | 0.1699 | -0.0066351 | 0.027256 | 7.0123 | 30.3268 | 30.368 | 8.8348 | -2.2339 | -65.3183 | -0.39825 | -9.3109 | -35.0967 | 32.254 | -85.7574 | 99.8566 | 1.561 | 121.3486 | 88.7878 | -94.1254 | 5.2643 | 3.447 | 21.492 | 81.7108 | 55.925 | 25.7034 | 121.3898 | 121.3486 | 123.2758 | 90.6235 | 5.2643 | 121.3898 | 121.3486 | 90.6235 | 25.7034 | 123.2758 | -19.9722 | -114.5645
2273.8438 | 121.0831 | -120.7764 | 0.14191 | 0.00206 | 0.1504 | 0.0056269 | 0.15196 | -0.024793 | 0.025547 | 0.74073 | 0.21057 | 0.22888 | -0.054932 | -0.20142 | -104.9698 | 0.10071 | -1.4282 | -59.2712 | 0.21515 | -121.0373 | 120.7214 | 0.086975 | 120.9869 | 120.575 | -105.1117 | -0.26093 | 0.073242 | 0.2655 | 119.3481 | 61.5051 | 15.8066 | 121.0052 | 120.9869 | 120.9915 | 120.8771 | -0.26093 | 121.0052 | 120.9869 | 120.8771 | 15.8066 | 120.9915 | -0.19684 | -121.1792
2275.625 | 121.4172 | -120.9274 | 0.25635 | 0.0096895 | 0.1583 | 0.0062677 | 0.1182 | -0.026075 | 0.024906 | 0.80226 | 0.25635 | 0.22888 | -0.032043 | 0.15106 | -106.0913 | 0.14648 | -0.29755 | -60.8139 | 0.28839 | -121.1838 | 120.8954 | -0.027466 | 121.1838 | 121.0785 | -106.3477 | -0.25635 | 0.032043 | 0.28839 | 120.6299 | 60.1135 | 14.8361 | 121.1563 | 121.1838 | 121.2158 | 121.0739 | -0.25635 | 121.1563 | 121.1838 | 121.0739 | 14.8361 | 121.2158 | -0.28839 | -121.4401
2277.4062 | 121.2341 | -120.5933 | 0.60425 | 0.0096895 | 0.38133 | 0.0086175 | 0.98765 | -0.025648 | -0.027645 | 2.7101 | 0.52185 | 0.52643 | 0.21973 | -1.4099 | -5.809 | -0.07782 | -6.8893 | -28.299 | 0.54016 | -120.7077 | 120.813 | -0.07782 | 121.1151 | 119.1833 | -6.4133 | -0.11444 | -0.064087 | 0.30212 | 113.7039 | 92.2943 | 114.7842 | 121.1197 | 121.1151 | 121.1334 | 120.5154 | -0.11444 | 121.1197 | 121.1151 | 120.5154 | 114.7842 | 121.1334 | -0.38452 | -121.312
2279.1875 | 121.4767 | -121.0968 | 0.23804 | 0.0096895 | 0.12455 | 0.0079767 | 0.31324 | -0.027784 | -0.030849 | 0.85801 | 0.12817 | 0.2655 | -0.082397 | -0.21057 | -4.6555 | -0.027466 | -1.7441 | -24.2889 | 0.3067 | -121.3028 | 121.0144 | 0.027466 | 121.225 | 120.8862 | -4.8935 | -0.20599 | 0.068665 | 0.21057 | 119.3527 | 96.8079 | 116.4413 | 121.3623 | 121.225 | 121.4035 | 121.0693 | -0.20599 | 121.3623 | 121.225 | 121.0693 | 116.4413 | 121.4035 | -0.32043 | -121.5408
2280.8906 | 120.4102 | -119.8791 | 0.46234 | 0.0096895 | 0.24696 | 0.0069085 | 6.9721 | -0.02757 | -0.023586 | 7.0123 | 0.41199 | 0.40283 | 0.1236 | -0.46234 | -13.9572 | -0.29755 | -39.3082 | -72.084 | -0.11444 | -119.4626 | 120.0027 | -0.059509 | 120.2911 | 119.4168 | -14.4196 | 0.41656 | -0.57678 | 0.28839 | 80.571 | 47.7951 | 105.9219 | 120.282 | 120.2911 | 119.7647 | 119.5816 | 0.41656 | 120.282 | 120.2911 | 119.5816 | 105.9219 | 119.7647 | -0.33875 | -119.9249
2282.6875 | 120.9915 | -120.6299 | 0.091553 | 0.00206 | 0.032052 | 0.0075495 | 0.21668 | -0.026289 | 0.022556 | 0.37138 | 0.10529 | 0.11444 | -0.11902 | 0.059509 | -95.1691 | 0.013733 | -0.33417 | -63.0753 | 0.14191 | -120.9229 | 120.5109 | 0.022888 | 120.7352 | 120.6894 | -95.2606 | -0.29297 | 0.050354 | 0.22431 | 120.2957 | 57.5546 | 25.4608 | 120.7443 | 120.7352 | 120.7718 | 120.6436 | -0.29297 | 120.7443 | 120.7352 | 120.6436 | 25.4608 | 120.7718 | -0.21057 | -121.0144
2284.4688 | 119.5358 | -117.9291 | 1.5381 | 0.017319 | 0.85706 | 0.0062677 | 6.9721 | -0.01988 | -0.040462 | 7.0123 | 1.3412 | 1.6296 | 1.1536 | -2.1515 | -8.8486 | -2.2659 | -36.1771 | -66.2842 | -0.42572 | -115.2008 | 119.0826 | 0.091553 | 119.2703 | 115.7776 | -10.3867 | 2.7283 | -1.9638 | 0.18768 | 81.752 | 51.6449 | 109.0805 | 119.5587 | 119.2703 | 117.5034 | 115.6631 | 2.7283 | 119.5587 | 119.2703 | 115.6631 | 109.0805 | 117.5034 | -0.38452 | -116.7389
2286.25 | 120.9732 | -120.0119 | 0.77362 | 0.00206 | 0.69898 | 0.0071221 | 0.95945 | -0.025434 | 0.0056802 | 3.8731 | 0.58594 | 0.65002 | 0.30212 | 0.013733 | -64.5493 | -0.17853 | -2.5085 | -33.1696 | 0.737 | -120.1859 | 120.314 | -0.1236 | 120.5978 | 120.0256 | -65.3229 | -0.17395 | -0.036621 | 0.28381 | 117.5034 | 86.8423 | 55.4626 | 120.6619 | 120.5978 | 120.7489 | 119.8334 | -0.17395 | 120.6619 | 120.5978 | 119.8334 | 55.4626 | 120.7489 | -0.4715 | -120.9595
2288.0469 | 120.6482 | -119.9799 | 0.41657 | 0.0096895 | 0.43943 | 0.0077631 | 0.34742 | -0.023298 | -0.015041 | 1.6978 | 0.32501 | 0.4715 | 0.10986 | 0.13733 | -26.4404 | -0.44861 | -29.274 | -31.3751 | 0.54932 | -120.1401 | 120.0897 | 0.054932 | 120.3049 | 120.1172 | -26.857 | -0.16022 | 0.13275 | 0.21515 | 90.7059 | 88.6047 | 93.5394 | 120.4514 | 120.3049 | 120.5292 | 119.5312 | -0.16022 | 120.4514 | 120.3049 | 119.5312 | 93.5394 | 120.5292 | -0.3067 | -120.5566
2289.7656 | 115.3198 | -113.7405 | 1.442 | 0.017319 | 1.3858 | 0.0041315 | 6.9721 | -0.035261 | -0.029995 | 7.0123 | 1.1856 | 1.3641 | 0.87891 | -2.5864 | -19.4183 | -18.4662 | -38.6902 | -38.3331 | -8.6792 | -101.6281 | 114.6194 | -0.07782 | 114.9261 | 111.1542 | -20.8603 | 12.1124 | -10.1212 | 0.3067 | 75.0504 | 75.4074 | 94.3222 | 115.1047 | 114.9261 | 105.0613 | 95.2744 | 12.1124 | 115.1047 | 114.9261 | 95.2744 | 94.3222 | 105.0613 | -0.56305 | -103.0701
2291.5469 | 117.2104 | -78.7308 | 38.8824 | 0.024948 | 7.0002 | 0.011181 | 6.6602 | -0.0032171 | -0.0028646 | 7.0123 | 32.1854 | 35.9573 | 8.812 | -0.53558 | -23.3551 | -23.0118 | 6.8207 | 35.7605 | 36.85 | -74.7025 | 87.5427 | -2.9251 | 110.9161 | 78.1952 | -62.2375 | 4.0283 | -2.0325 | 23.3734 | 85.5515 | 114.4913 | 55.3757 | 114.6881 | 110.9161 | 115.5807 | 55.719 | 4.0283 | 114.6881 | 110.9161 | 55.719 | 55.3757 | 115.5807 | -30.0705 | -113.5849
2293.2656 | 118.3411 | -78.7857 | 39.1891 | 0.00206 | 1.6447 | 0.0071221 | 6.9721 | -0.0053535 | 0.023838 | 7.0123 | 39.3723 | 39.4272 | 8.8348 | 1.3779 | -70.5963 | 0.53101 | 32.6248 | 32.8079 | 35.6873 | -77.7924 | 87.6205 | 0.23804 | 118.158 | 80.1636 | -109.7855 | 0.99335 | -3.5019 | 30.5374 | 111.4105 | 111.5936 | 8.1894 | 118.2129 | 118.158 | 114.473 | 79.3167 | 0.99335 | 118.2129 | 118.158 | 79.3167 | 8.1894 | 114.473 | -30.3543 | -116.9815
2295.0469 | 119.9799 | -119.8975 | 0.11902 | 0.032577 | 0.0010766 | 0.0032769 | 0.063516 | -0.025007 | -0.030849 | 0.011638 | 0.068665 | 0.10986 | -0.21057 | 0.13275 | -0.032043 | 0.11902 | -0.027466 | -0.15564 | 0.16479 | -120.1675 | 119.6869 | -0.009156 | 119.9661 | 120.0302 | -0.15106 | -0.27008 | 0.045776 | 0.27924 | 119.87 | 119.7418 | 119.8654 | 120.0073 | 119.9661 | 120.0623 | 120.0165 | -0.27008 | 120.0073 | 119.9661 | 120.0165 | 119.8654 | 120.0623 | -0.32959 | -120.2866
2296.8438 | 120.3598 | -120.0851 | 0.068665 | 0.00206 | 0.0032128 | 0.0066949 | 0.061594 | -0.024793 | -0.02914 | 0.012493 | -0.009155 | 0.10529 | -0.1831 | 0.07782 | -0.11444 | 0.086975 | -0.027466 | -0.23804 | 0.16937 | -120.4239 | 119.902 | 0.036621 | 120.076 | 120.163 | -0.18311 | -0.33875 | 0.10071 | 0.17395 | 120.0577 | 119.8471 | 119.9707 | 120.1904 | 120.076 | 120.2545 | 120.1721 | -0.33875 | 120.1904 | 120.076 | 120.1721 | 119.9707 | 120.2545 | -0.25177 | -120.4926
2298.6406 | 120.4926 | -120.1767 | 0.054932 | 0.00206 | -0.00041862 | 0.0092585 | 0.053903 | -0.025648 | -0.029568 | 0.012279 | 0.050354 | 0.068665 | -0.15564 | 0.14648 | -0.064087 | 0.16479 | -0.10071 | -0.19684 | 0.1236 | -120.5109 | 120.0211 | 0.013733 | 120.2271 | 120.3232 | -0.11902 | -0.33417 | 0.068664 | 0.20599 | 120.076 | 119.9799 | 120.1126 | 120.2454 | 120.2271 | 120.3003 | 120.3415 | -0.33417 | 120.2454 | 120.2271 | 120.3415 | 120.1126 | 120.3003 | -0.21057 | -120.5658
2300.3594 | 120.5063 | -120.2774 | 0.054932 | 0.017319 | 0.00043578 | 0.0045587 | 0.05903 | -0.026075 | -0.031277 | 0.014415 | 0.10529 | 0.054932 | -0.16022 | 0.19226 | -0.027466 | 0.20599 | -0.1831 | -0.16479 | 0.14191 | -120.5841 | 120.1172 | 0 | 120.3827 | 120.4697 | -0.082398 | -0.3067 | 0.086975 | 0.2655 | 120.0943 | 120.1126 | 120.2499 | 120.3323 | 120.3827 | 120.4193 | 120.4834 | -0.3067 | 120.3323 | 120.3827 | 120.4834 | 120.2499 | 120.4193 | -0.21515 | -120.639
2302.1406 | 120.4742 | -120.3461 | 0.073242 | 0.00206 | 0.0019312 | 0.0092585 | 0.066507 | -0.026716 | -0.032772 | 0.020824 | 0.059509 | 0.09613 | -0.18768 | 0.17395 | -0.086975 | 0.11902 | -0.032043 | -0.48523 | 0.16937 | -120.639 | 120.1584 | 0.022888 | 120.4056 | 120.52 | -0.16022 | -0.29297 | 0.096131 | 0.24719 | 120.314 | 119.8608 | 120.2591 | 120.4422 | 120.4056 | 120.5154 | 120.4651 | -0.29297 | 120.4422 | 120.4056 | 120.4651 | 120.2591 | 120.5154 | -0.26092 | -120.7123
2303.8438 | 120.5109 | -120.2225 | 0.21973 | 0.0096895 | 0.06025 | 0.0062677 | 0.18592 | -0.026075 | -0.024654 | 0.51365 | 0.11902 | 0.23804 | -0.091553 | 0.15564 | -6.4224 | 0.086975 | 0.12817 | -2.9434 | 0.30212 | -120.5475 | 120.1309 | 0.01831 | 120.3415 | 120.3781 | -6.6422 | -0.32501 | 0.082397 | 0.21057 | 120.3506 | 117.2791 | 113.8 | 120.4605 | 120.3415 | 120.5246 | 120.3094 | -0.32501 | 120.4605 | 120.3415 | 120.3094 | 113.8 | 120.5246 | -0.31128 | -120.7672
2305.6406 | 120.5475 | -120.2728 | 0.25177 | 0.0096895 | 0.051705 | 0.0073359 | 0.15602 | -0.026929 | -0.031277 | 0.39701 | 0.15106 | 0.2243 | -0.09613 | 0.15564 | -4.0192 | 0.10071 | 0.073242 | -0.62256 | 0.25635 | -120.5521 | 120.1767 | -0.027466 | 120.4239 | 120.4285 | -4.2709 | -0.27924 | 0.004578 | 0.24719 | 120.3461 | 119.6503 | 116.2537 | 120.4971 | 120.4239 | 120.5292 | 120.3735 | -0.27924 | 120.4971 | 120.4239 | 120.3735 | 116.2537 | 120.5292 | -0.3479 | -120.8038
2307.3594 | 120.6573 | -120.4605 | 0.068665 | 0.017319 | 0.0038538 | 0.0090447 | 0.058176 | -0.025648 | -0.029995 | 0.030437 | 0.11902 | 0.07782 | -0.13275 | 0.20142 | 0.07782 | 0.22888 | -0.19684 | -0.74158 | 0.1236 | -120.7397 | 120.3278 | 0.009155 | 120.5795 | 120.6619 | 0.009155 | -0.27924 | 0.054931 | 0.25177 | 120.2637 | 119.7189 | 120.5383 | 120.5383 | 120.5795 | 120.5841 | 120.6894 | -0.27924 | 120.5383 | 120.5795 | 120.6894 | 120.5383 | 120.5841 | -0.20142 | -120.8084
2309.1406 | 120.6162 | -120.3461 | 0.21515 | 0.0096895 | 0.061532 | 0.0086175 | 0.184 | -0.024793 | -0.034054 | 0.47734 | 0.16479 | 0.22888 | -0.10071 | 0.17853 | -0.041199 | 0.13733 | 0.07782 | -5.5069 | 0.28381 | -120.607 | 120.2454 | 0.013733 | 120.5109 | 120.5246 | -0.25635 | -0.26093 | 0.068664 | 0.2655 | 120.4239 | 114.8392 | 120.3049 | 120.575 | 120.5109 | 120.6299 | 120.4834 | -0.26093 | 120.575 | 120.5109 | 120.4834 | 120.3049 | 120.6299 | -0.31586 | -120.8221
2310.9219 | 120.7306 | -120.4926 | 0.054932 | 0.017319 | 0.0049218 | 0.0064813 | 0.066507 | -0.02458 | -0.031917 | 0.038982 | 0.11444 | 0.07782 | -0.16022 | 0.20142 | 0.068665 | 0.21973 | -0.17853 | -114.0152 | 0.086975 | -120.7993 | 120.3323 | 0.022888 | 120.607 | 120.694 | 0.013733 | -0.3067 | 0.032043 | 0.27466 | 120.314 | 6.4774 | 120.5612 | 120.5704 | 120.607 | 120.5795 | 120.7123 | -0.3067 | 120.5704 | 120.607 | 120.7123 | 120.5612 | 120.5795 | -0.21515 | -120.8542
2312.6406 | 120.7809 | -120.5521 | 0.068665 | 0.00206 | 0.0019312 | 0.0039179 | 0.056253 | -0.027143 | -0.030849 | 0.035564 | 0.10071 | 0.082397 | -0.15564 | 0.21057 | 0.082397 | 0.21515 | -0.13275 | -7.5623 | 0.12817 | -120.8679 | 120.3964 | 0.013732 | 120.6528 | 120.7626 | 0.013732 | -0.31586 | 0.059509 | 0.25635 | 120.4193 | 112.9898 | 120.6345 | 120.6345 | 120.6528 | 120.6802 | 120.7672 | -0.31586 | 120.6345 | 120.6528 | 120.7672 | 120.6345 | 120.6802 | -0.22431 | -120.9366
2314.4375 | 120.8633 | -120.5933 | 0.07782 | 0.00206 | 0.0019312 | 0.0096857 | 0.07377 | -0.026929 | -0.031063 | 0.053295 | 0.07782 | 0.086975 | -0.16479 | 0.17395 | 0.018311 | 0.16479 | -0.10986 | -13.6093 | 0.12817 | -120.8633 | 120.4285 | 0.009155 | 120.6711 | 120.7672 | -0.059509 | -0.27008 | 0.050354 | 0.24261 | 120.4834 | 106.9839 | 120.6116 | 120.6802 | 120.6711 | 120.7214 | 120.7581 | -0.27008 | 120.6802 | 120.6711 | 120.7581 | 120.6116 | 120.7214 | -0.24261 | -120.9412
2316.1562 | 120.8908 | -120.5841 | 0.064087 | 0.017319 | 0.0038538 | 0.0081903 | 0.072061 | -0.02458 | -0.035976 | 0.038982 | 0.009155 | 0.11444 | -0.19226 | 0.10071 | -0.059509 | 0.073242 | -0.004578 | -3.0212 | 0.17395 | -120.9229 | 120.3918 | 0.050354 | 120.5933 | 120.6848 | -0.1236 | -0.33875 | 0.10986 | 0.20142 | 120.5795 | 117.5629 | 120.5246 | 120.6985 | 120.5933 | 120.7581 | 120.6573 | -0.33875 | 120.6985 | 120.5933 | 120.6573 | 120.5246 | 120.7581 | -0.25635 | -120.9869
2317.9219 | 120.7169 | -120.0027 | 0.5722 | 0.00206 | 0.24781 | 0.0088311 | 0.48799 | -0.027143 | -0.031704 | 1.9851 | 0.56763 | 0.55847 | 0.19684 | 0.37537 | -1.4648 | 0.37537 | 0.27466 | -114.5966 | 0.6134 | -120.0714 | 120.1996 | -0.013733 | 120.5704 | 120.3781 | -2.037 | -0.068664 | 0.041198 | 0.37079 | 120.2774 | 5.4062 | 118.5379 | 120.5612 | 120.5704 | 120.6162 | 120.3781 | -0.068664 | 120.5612 | 120.5704 | 120.3781 | 118.5379 | 120.6162 | -0.37537 | -120.6436
2319.7031 | 120.845 | -120.6619 | 0.09613 | 0.0096895 | 0.002572 | 0.0079767 | 0.066507 | -0.027143 | -0.032772 | 0.0377 | 0.036621 | 0.11902 | -0.19226 | 0.11902 | -0.022888 | 0.09613 | 0.045776 | -116.3773 | 0.15106 | -120.9732 | 120.4697 | 0.022889 | 120.6985 | 120.7809 | -0.11902 | -0.31128 | 0.054932 | 0.22888 | 120.7077 | 4.2847 | 120.639 | 120.7809 | 120.6985 | 120.813 | 120.7581 | -0.31128 | 120.7809 | 120.6985 | 120.7581 | 120.639 | 120.813 | -0.28839 | -121.0693
2321.4844 | 120.8496 | -120.694 | 0.10986 | 0.0096895 | 0.0044946 | 0.0098993 | 0.068216 | -0.027357 | -0.029995 | 0.044322 | 0.12817 | 0.086975 | -0.15564 | 0.22888 | 0.091553 | 0.2243 | -0.14191 | -116.4734 | 0.091553 | -121.0052 | 120.5383 | -0.022888 | 120.8221 | 120.9229 | -0.01831 | -0.31128 | -0.01831 | 0.28381 | 120.5521 | 4.2206 | 120.7855 | 120.7809 | 120.8221 | 120.7855 | 120.9183 | -0.31128 | 120.7809 | 120.8221 | 120.9183 | 120.7855 | 120.7855 | -0.2655 | -121.1151
2323.25 | 120.845 | -120.7581 | 0.086975 | 0.017319 | 0.0049218 | 0.0066949 | 0.076975 | -0.027143 | -0.034054 | 0.063121 | 0.10986 | 0.068665 | -0.16479 | 0.22888 | 0.086975 | 0.21515 | -0.11902 | -118.7668 | 0.10529 | -120.9686 | 120.5933 | -0.01831 | 120.8679 | 120.9869 | 0 | -0.21057 | 0.018311 | 0.27466 | 120.639 | 1.9913 | 120.845 | 120.8267 | 120.8679 | 120.8633 | 120.9732 | -0.21057 | 120.8267 | 120.8679 | 120.9732 | 120.845 | 120.8633 | -0.25177 | -121.0556
2324.9844 | 121.0144 | -120.7306 | 0.064087 | -0.0055695 | 0.0047082 | 0.0066949 | 0.069498 | -0.028852 | -0.030636 | 0.051372 | 0.073242 | 0.07782 | -0.16022 | 0.15564 | 0.027466 | 0.14648 | -0.091553 | -119.0048 | 0.11444 | -121.0693 | 120.5704 | 0.013733 | 120.8038 | 120.8862 | -0.036621 | -0.33875 | 0.050354 | 0.23346 | 120.639 | 1.7258 | 120.7581 | 120.8084 | 120.8038 | 120.845 | 120.8771 | -0.33875 | 120.8084 | 120.8038 | 120.8771 | 120.7581 | 120.845 | -0.2243 | -121.1334
2326.7656 | 120.9503 | -120.7809 | 0.091553 | 0.017319 | 0.0055628 | 0.0056269 | 0.07847 | -0.02757 | -0.034908 | 0.052226 | 0.018311 | 0.11902 | -0.21515 | 0.10529 | -0.032043 | 0.07782 | 0.041199 | -119.7281 | 0.14191 | -121.0602 | 120.5658 | 0.027466 | 120.7993 | 120.8862 | -0.1236 | -0.27924 | 0.050354 | 0.23346 | 120.8221 | 1.0529 | 120.7489 | 120.9 | 120.7993 | 120.9229 | 120.8588 | -0.27924 | 120.9 | 120.7993 | 120.8588 | 120.7489 | 120.9229 | -0.3067 | -121.1517
2328.5625 | 121.0464 | -120.7397 | 0.086975 | 0.017319 | 0.0064172 | 0.0088311 | 0.075266 | -0.02757 | -0.03149 | 0.060771 | 0.086975 | 0.086975 | -0.15106 | 0.19684 | 0.059509 | 0.17395 | -0.10986 | -119.1284 | 0.11902 | -121.0693 | 120.5887 | 0 | 120.8267 | 120.9366 | -0.027466 | -0.32959 | 0.032044 | 0.23804 | 120.6299 | 1.6113 | 120.7993 | 120.8267 | 120.8267 | 120.8588 | 120.9137 | -0.32959 | 120.8267 | 120.8267 | 120.9137 | 120.7993 | 120.8588 | -0.23804 | -121.1563
2330.2969 | 120.9961 | -120.8038 | 0.10071 | 0.00206 | 0.0070582 | 0.012035 | 0.20194 | -0.026289 | -0.032558 | 0.21821 | 0.11902 | 0.091553 | -0.16022 | 0.22888 | 0.086975 | 0.20599 | -0.16022 | -118.6249 | 0.10071 | -121.0327 | 120.6436 | -0.009155 | 120.9229 | 121.0327 | -0.013733 | -0.22888 | 0 | 0.27924 | 120.6436 | 2.179 | 120.8908 | 120.8954 | 120.9229 | 120.9045 | 121.0098 | -0.22888 | 120.8954 | 120.9229 | 121.0098 | 120.8908 | 120.9045 | -0.26093 | -121.1334
2332.0781 | 120.9824 | -120.8038 | 0.068665 | 0.0096895 | 0.0040674 | 0.0084039 | 0.066721 | -0.027357 | -0.034054 | 0.032146 | 0.032043 | 0.086975 | -0.19684 | 0.10986 | -0.032043 | 0.073242 | -0.004578 | -3.3325 | 0.16479 | -121.1014 | 120.607 | 0.01831 | 120.8359 | 120.9137 | -0.10071 | -0.29755 | 0.09613 | 0.22888 | 120.7993 | 117.4713 | 120.7718 | 120.8908 | 120.8359 | 120.9686 | 120.8771 | -0.29755 | 120.8908 | 120.8359 | 120.8771 | 120.7718 | 120.9686 | -0.2655 | -121.17
2333.8594 | 121.0144 | -120.8496 | 0.086975 | 0.00206 | 0.0055628 | 0.0058405 | 0.067789 | -0.025434 | -0.034054 | 0.041545 | 0.018311 | 0.10986 | -0.18768 | 0.10986 | -0.045776 | 0.086975 | 0.064087 | -8.0338 | 0.1831 | -121.1746 | 120.6619 | 0.022888 | 120.8679 | 120.9595 | -0.13275 | -0.32501 | 0.09613 | 0.20599 | 120.9137 | 112.8159 | 120.8038 | 120.9595 | 120.8679 | 121.0327 | 120.9366 | -0.32501 | 120.9595 | 120.8679 | 120.9366 | 120.8038 | 121.0327 | -0.27466 | -121.2616
2335.5781 | 121.1197 | -120.8221 | 0.068665 | 0.00206 | 0.0023584 | 0.011395 | 0.093424 | -0.027784 | -0.033199 | 0.12635 | 0.09613 | 0.064087 | -0.13733 | 0.19226 | 0.073242 | 0.21057 | -0.16937 | -85.9634 | 0.1236 | -121.1243 | 120.6848 | -0.004578 | 120.9183 | 121.0144 | 0.004577 | -0.30212 | 0.054931 | 0.23346 | 120.6528 | 34.8587 | 120.8954 | 120.8862 | 120.9183 | 120.9457 | 121.0327 | -0.30212 | 120.8862 | 120.9183 | 121.0327 | 120.8954 | 120.9457 | -0.20599 | -121.1929
2337.3594 | 120.5383 | -120.9183 | 0.10529 | 0.00206 | 0.0040674 | 0.0054131 | 0.073557 | -0.026075 | -0.032345 | 0.05244 | 0.054932 | 0.12817 | -0.1831 | 0.13733 | -0.17853 | 0.10529 | 0.004578 | -14.7354 | 0.17395 | -120.1309 | 120.7352 | 0.022888 | 120.9732 | 121.0556 | -0.28381 | 0.78735 | 0.068664 | 0.23804 | 120.9229 | 106.1829 | 120.7397 | 121.0464 | 120.9732 | 121.0922 | 121.0236 | 0.78735 | 121.0464 | 120.9732 | 121.0236 | 120.7397 | 121.0922 | -0.28839 | -120.2362
2339.1406 | 121.1151 | -120.8771 | 0.07782 | -0.0055695 | 0.039102 | 0.0092585 | 0.11585 | -0.025861 | -0.032131 | 0.032146 | 0.036621 | 0.11902 | -0.10986 | 0.1236 | -0.013733 | 0.086975 | 0.013733 | -68.2068 | 0.17395 | -116.6061 | 120.7672 | 0.041199 | 120.9137 | 121.0007 | -0.091553 | 4.2709 | 0.09613 | 0.14648 | 120.8908 | 52.6703 | 120.8633 | 120.9961 | 120.9137 | 121.051 | 120.9641 | 4.2709 | 120.9961 | 120.9137 | 120.9641 | 120.8633 | 121.051 | -0.18768 | -116.684
2340.8594 | 121.1288 | -120.8908 | 0.082397 | 0.00206 | 0.0040674 | 0.0088311 | 0.063516 | -0.026289 | -0.033413 | 0.033855 | 0.018311 | 0.10986 | -0.19684 | 0.10071 | -0.064087 | 0.073242 | 0.050354 | -9.7092 | 0.17395 | -121.2296 | 120.694 | 0.027466 | 120.9091 | 120.9915 | -0.14648 | -0.33874 | 0.091553 | 0.21515 | 120.9412 | 111.1816 | 120.8267 | 121.0007 | 120.9091 | 121.0648 | 120.9641 | -0.33874 | 121.0007 | 120.9091 | 120.9641 | 120.8267 | 121.0648 | -0.27924 | -121.3119
2342.6406 | 121.0693 | -120.9457 | 0.073242 | 0.024948 | 0.0066308 | 0.0090447 | 0.064371 | -0.023725 | -0.032558 | 0.031932 | 0.059509 | 0.086975 | -0.18768 | 0.13733 | -0.045776 | 0.11444 | -0.027466 | -4.8477 | 0.17395 | -121.2433 | 120.7581 | 0.013733 | 121.0052 | 121.0831 | -0.11902 | -0.29755 | 0.10071 | 0.24719 | 120.9183 | 116.098 | 120.9 | 121.0327 | 121.0052 | 121.1197 | 121.0602 | -0.29755 | 121.0327 | 121.0052 | 121.0602 | 120.9 | 121.1197 | -0.26092 | -121.3165
2344.4219 | 121.1838 | -120.9503 | 0.045776 | 0.017319 | 0.0040674 | 0.0060541 | 0.05604 | -0.025007 | -0.030422 | 0.030864 | 0.11444 | 0.091553 | -0.13733 | 0.19684 | 0.07782 | 0.21057 | -0.17853 | -3.1448 | 0.13733 | -121.257 | 120.813 | 0.045777 | 121.0648 | 121.1472 | 0.032044 | -0.3067 | 0.091553 | 0.25177 | 120.7718 | 117.8055 | 121.0281 | 121.0419 | 121.0648 | 121.0876 | 121.1609 | -0.3067 | 121.0419 | 121.0648 | 121.1609 | 121.0281 | 121.0876 | -0.18311 | -121.3028
2346.1406 | 121.0785 | -120.7626 | 0.24261 | 0.0096895 | 0.055337 | 0.0092585 | 1.809 | -0.024152 | -0.030422 | 2.0534 | 0.17395 | 0.24719 | -0.059509 | 0.018311 | -0.07782 | -0.013733 | -0.23346 | -58.2687 | 0.10529 | -120.9641 | 120.7031 | 0.004577 | 120.9366 | 120.7809 | -0.32044 | -0.20142 | -0.13733 | 0.23346 | 120.5292 | 62.4939 | 120.6848 | 121.0098 | 120.9366 | 120.8679 | 120.7489 | -0.20142 | 121.0098 | 120.9366 | 120.7489 | 120.6848 | 120.8679 | -0.30212 | -121.2067
2347.9219 | 121.2753 | -120.9778 | 0.068665 | 0.017319 | 0.0068444 | 0.0090447 | 0.068857 | -0.023511 | -0.033199 | 0.040904 | 0 | 0.11902 | -0.20599 | 0.068665 | -0.086975 | 0.068665 | 0.004578 | -0.050354 | 0.16479 | -121.2845 | 120.7718 | 0.050354 | 120.9778 | 121.0464 | -0.15564 | -0.3067 | 0.09613 | 0.20599 | 120.9824 | 120.9274 | 120.8908 | 121.0968 | 120.9778 | 121.1426 | 121.0464 | -0.3067 | 121.0968 | 120.9778 | 121.0464 | 120.8908 | 121.1426 | -0.27466 | -121.3531
2349.7031 | 121.1563 | -121.0373 | 0.10986 | 0.0096895 | 0.0021448 | 0.0075495 | 0.06373 | -0.025648 | -0.029995 | 0.045818 | 0.10986 | 0.064087 | -0.14191 | 0.21973 | 0.050354 | 0.20599 | -0.082397 | 0.10986 | 0.16022 | -121.2936 | 120.8954 | -0.045776 | 121.1472 | 121.257 | -0.059509 | -0.25635 | 0.050354 | 0.25177 | 120.9549 | 121.1472 | 121.0876 | 121.1014 | 121.1472 | 121.1975 | 121.2433 | -0.25635 | 121.1014 | 121.1472 | 121.2433 | 121.0876 | 121.1975 | -0.25177 | -121.4035
2351.4219 | 121.2158 | -121.0602 | 0.086975 | 0.0096895 | 0.002572 | 0.0081903 | 0.057749 | -0.025648 | -0.032772 | 0.03535 | 0.050354 | 0.091553 | -0.16022 | 0.11444 | -0.027466 | 0.10529 | 0.041199 | 0.12817 | 0.16479 | -121.3577 | 120.9 | 0.004578 | 121.1105 | 121.1746 | -0.11444 | -0.29755 | 0.07782 | 0.21057 | 121.1014 | 121.1884 | 121.0327 | 121.1517 | 121.1105 | 121.225 | 121.1655 | -0.29755 | 121.1517 | 121.1105 | 121.1655 | 121.0327 | 121.225 | -0.24719 | -121.4447
2353.2031 | 121.2341 | -121.0602 | 0.091553 | 0.00206 | 0.00064938 | 0.0077631 | 0.1135 | -0.027998 | -0.030422 | 0.15028 | 0.10529 | 0.086975 | -0.15564 | 0.20142 | 0.027466 | 0.20599 | -0.10986 | -0.93384 | 0.15564 | -121.3623 | 120.9045 | -0.004578 | 121.1655 | 121.2616 | -0.064087 | -0.30212 | 0.064087 | 0.26093 | 120.9503 | 120.1263 | 121.0876 | 121.1472 | 121.1655 | 121.2158 | 121.2662 | -0.30212 | 121.1472 | 121.1655 | 121.2662 | 121.0876 | 121.2158 | -0.24719 | -121.4539
2354.9062 | 121.2112 | -121.0739 | 0.068665 | 0.0096895 | 0.0047082 | 0.0069085 | 0.063944 | -0.027998 | -0.033199 | 0.033641 | 0.004578 | 0.10529 | -0.20142 | 0.11902 | -0.027466 | 0.10529 | 0.036621 | 0.15106 | 0.18768 | -121.3623 | 120.8725 | 0.036621 | 121.0785 | 121.1929 | -0.096131 | -0.28839 | 0.11902 | 0.20599 | 121.1105 | 121.225 | 121.0464 | 121.1792 | 121.0785 | 121.2616 | 121.1792 | -0.28839 | 121.1792 | 121.0785 | 121.1792 | 121.0464 | 121.2616 | -0.27008 | -121.431
2356.6875 | 121.3715 | -121.051 | 0.054932 | 0.00206 | 0.0040674 | 0.0011407 | 0.060312 | -0.026929 | -0.03149 | 0.038341 | 0.064087 | 0.082397 | -0.16022 | 0.16022 | -0.045776 | 0.16479 | -0.10071 | 0.1831 | 0.13275 | -121.3715 | 120.8908 | 0.027465 | 121.1151 | 121.2112 | -0.10071 | -0.32044 | 0.077819 | 0.2243 | 120.9503 | 121.2341 | 121.0052 | 121.1334 | 121.1151 | 121.1838 | 121.2158 | -0.32044 | 121.1334 | 121.1151 | 121.2158 | 121.0052 | 121.1838 | -0.21515 | -121.4264
2358.4844 | 121.2387 | -121.1105 | 0.091553 | 0.0096895 | 0.0021448 | 0.0064813 | 0.064798 | -0.027784 | -0.030849 | 0.044963 | 0.12817 | 0.054932 | -0.15564 | 0.2243 | 0.054932 | 0.24719 | -0.14191 | 0.16022 | 0.13733 | -121.376 | 120.9549 | -0.036621 | 121.2387 | 121.3348 | -0.036621 | -0.2655 | 0.045776 | 0.28381 | 120.9686 | 121.2708 | 121.1655 | 121.1655 | 121.2387 | 121.2479 | 121.3577 | -0.2655 | 121.1655 | 121.2387 | 121.3577 | 121.1655 | 121.2479 | -0.24719 | -121.4676
2360.2031 | 121.344 | -121.0419 | 0.07782 | 0.0096895 | 0.0047082 | 0.0060541 | 0.071634 | -0.024152 | -0.033199 | 0.057994 | 0.068665 | 0.068665 | -0.15564 | 0.21515 | -0.11902 | 0.19226 | -0.10071 | 0.17395 | 0.13275 | -121.3898 | 120.8862 | -0.009155 | 121.1105 | 121.257 | -0.19684 | -0.3479 | 0.054931 | 0.22431 | 120.9412 | 121.2158 | 120.9229 | 121.1105 | 121.1105 | 121.1746 | 121.2341 | -0.3479 | 121.1105 | 121.1105 | 121.2341 | 120.9229 | 121.1746 | -0.23346 | -121.4676
2361.9844 | 121.3074 | -121.1197 | 0.09613 | 0.00206 | 0.0047082 | 0.0062677 | 0.083383 | -0.028211 | -0.032772 | 0.04774 | 0.027466 | 0.1236 | -0.1831 | 0.10529 | -0.068665 | 0.073242 | 0.073242 | -0.66834 | 0.17853 | -121.431 | 120.9366 | 0.027466 | 121.1472 | 121.225 | -0.16479 | -0.31128 | 0.082398 | 0.21057 | 121.1929 | 120.4514 | 121.051 | 121.2433 | 121.1472 | 121.2982 | 121.1929 | -0.31128 | 121.2433 | 121.1472 | 121.1929 | 121.051 | 121.2982 | -0.27924 | -121.5271
2363.7656 | 121.4081 | -121.0831 | 0.068665 | 0.00206 | 0.0049218 | 0.0086175 | 0.09556 | -0.028211 | -0.03149 | 0.080852 | 0.064087 | 0.086975 | -0.15106 | 0.1831 | 0.041199 | 0.16937 | -0.11444 | -0.50812 | 0.15106 | -121.4172 | 120.932 | 0.01831 | 121.1472 | 121.2662 | -0.027466 | -0.33417 | 0.082397 | 0.21515 | 120.9686 | 120.575 | 121.1243 | 121.17 | 121.1472 | 121.2341 | 121.2524 | -0.33417 | 121.17 | 121.1472 | 121.2524 | 121.1243 | 121.2341 | -0.21973 | -121.4859
2365.5469 | 121.2799 | -121.0236 | 0.11444 | 0.00206 | 0.016885 | 0.0090447 | 0.58198 | -0.026075 | -0.032131 | 0.66597 | 0.15564 | 0.10071 | -0.10071 | 0.20599 | 0.027466 | 0.1831 | -0.24719 | -4.7287 | 0.13275 | -121.2845 | 120.9229 | -0.013733 | 121.1792 | 121.2296 | -0.086975 | -0.26093 | 0.01831 | 0.25635 | 120.7764 | 116.2949 | 121.051 | 121.1243 | 121.1792 | 121.1563 | 121.2067 | -0.26093 | 121.1243 | 121.1792 | 121.2067 | 121.051 | 121.1563 | -0.21515 | -121.3989
2367.3281 | 119.902 | -119.6732 | 0.064087 | 0.00206 | -0.033317 | 0.010326 | 0.046213 | -0.020948 | -0.034908 | 0.02296 | -0.009155 | 0.10071 | -0.19684 | 0.091553 | -0.059509 | 0.059509 | -0.009155 | 0.13733 | 0.17853 | -119.9203 | 119.4763 | 0.036621 | 119.664 | 119.7647 | -0.1236 | -0.24719 | 0.11444 | 0.18768 | 119.664 | 119.8105 | 119.6136 | 119.7739 | 119.664 | 119.8517 | 119.7327 | -0.24719 | 119.7739 | 119.664 | 119.7327 | 119.6136 | 119.8517 | -0.26093 | -119.9844
2369.0469 | 120.8405 | -120.7672 | 0.10071 | 0.0096895 | -0.031608 | 0.0077631 | 0.048136 | -0.023939 | -0.033413 | 0.033855 | 0.059509 | 0.10071 | -0.17853 | 0.15106 | 0.018311 | 0.11902 | -0.054932 | -107.1854 | 0.1236 | -120.9915 | 120.5887 | 0 | 120.8267 | 120.9183 | -0.082397 | -0.2243 | 0.022888 | 0.23804 | 120.7123 | 13.5818 | 120.7855 | 120.8679 | 120.8267 | 120.8908 | 120.8862 | -0.2243 | 120.8679 | 120.8267 | 120.8862 | 120.7855 | 120.8908 | -0.27924 | -121.0922
2370.8438 | 121.0739 | -120.8038 | 0.068665 | 0.0096895 | -0.032035 | 0.0086175 | 0.048563 | -0.024366 | -0.029995 | 0.032146 | 0.004578 | 0.10529 | -0.19226 | 0.091553 | -0.050354 | 0.086975 | -0.050354 | -113.6353 | 0.11902 | -121.1563 | 120.6116 | 0.036621 | 120.8084 | 120.8954 | -0.11902 | -0.35248 | 0.050354 | 0.19684 | 120.7535 | 7.1686 | 120.7535 | 120.9091 | 120.8084 | 120.9229 | 120.8908 | -0.35248 | 120.9091 | 120.8084 | 120.8908 | 120.7535 | 120.9229 | -0.26093 | -121.225
2372.625 | 121.106 | -120.8633 | 0.073242 | 0.00206 | -0.029685 | 0.0051995 | 0.055826 | -0.022657 | -0.030849 | 0.045391 | -0.013733 | 0.12817 | -0.16937 | 0.082397 | -0.064087 | 0.054932 | 0.004578 | -113.6444 | 0.14191 | -121.2021 | 120.694 | 0.054932 | 120.8496 | 120.9457 | -0.13733 | -0.33875 | 0.068665 | 0.15564 | 120.8679 | 7.2189 | 120.7993 | 120.9915 | 120.8496 | 121.0052 | 120.9183 | -0.33875 | 120.9915 | 120.8496 | 120.9183 | 120.7993 | 121.0052 | -0.24261 | -121.2753
2374.3594 | 121.1563 | -120.9045 | 0.082397 | 0.017319 | -0.029044 | 0.0062677 | 0.048349 | -0.02223 | -0.031704 | 0.039836 | 0.10986 | 0.07782 | -0.12817 | 0.20142 | 0.068665 | 0.20142 | -0.19684 | -111.9095 | 0.11444 | -121.1746 | 120.7764 | -0.004577 | 121.0144 | 121.106 | -0.013732 | -0.27008 | 0.032044 | 0.23804 | 120.7077 | 8.9951 | 120.9732 | 120.9824 | 121.0144 | 121.019 | 121.106 | -0.27008 | 120.9824 | 121.0144 | 121.106 | 120.9732 | 121.019 | -0.21057 | -121.257
2376.1406 | 121.2708 | -120.9274 | 0.07782 | 0.0096895 | -0.027976 | 0.0069085 | 0.05134 | -0.028211 | -0.029995 | 0.060771 | 0.045776 | 0.10071 | -0.14191 | 0.14191 | 0.018311 | 0.15106 | -0.11444 | -112.8799 | 0.10529 | -121.257 | 120.7855 | 0.022888 | 120.9732 | 121.0693 | -0.059509 | -0.32959 | 0.027466 | 0.18768 | 120.813 | 8.0475 | 120.9457 | 121.0281 | 120.9732 | 121.0327 | 121.0785 | -0.32959 | 121.0281 | 120.9732 | 121.0785 | 120.9457 | 121.0327 | -0.21973 | -121.3348
2377.9219 | 121.1655 | -120.9869 | 0.082397 | 0.0096895 | -0.027762 | 0.0069085 | 0.053903 | -0.025007 | -0.033413 | 0.043041 | 0.013733 | 0.10529 | -0.17853 | 0.09613 | -0.054932 | 0.068665 | -0.009155 | -116.6016 | 0.13733 | -121.2982 | 120.8084 | 0.022889 | 121.0007 | 121.0831 | -0.13733 | -0.31128 | 0.054932 | 0.19226 | 120.9778 | 4.3854 | 120.932 | 121.0922 | 121.0007 | 121.1243 | 121.0556 | -0.31128 | 121.0922 | 121.0007 | 121.0556 | 120.932 | 121.1243 | -0.26092 | -121.3806
2379.7188 | 121.3165 | -121.0098 | 0.11444 | 0.00206 | -0.020499 | 0.0077631 | 0.04899 | -0.023084 | -0.034908 | 0.066326 | -0.013733 | 0.10529 | -0.19684 | 0.086975 | -0.050354 | 0.054932 | 0.032043 | -119.4855 | 0.17395 | -121.3211 | 120.813 | -0.009155 | 120.9961 | 121.0968 | -0.16479 | -0.31128 | 0.059509 | 0.18311 | 121.0419 | 1.5244 | 120.9595 | 121.1151 | 120.9961 | 121.1838 | 121.0648 | -0.31128 | 121.1151 | 120.9961 | 121.0648 | 120.9595 | 121.1838 | -0.31128 | -121.4355
2381.4375 | 121.1655 | -121.0831 | 0.091553 | 0.0096895 | -0.024772 | 0.0056269 | 0.045786 | -0.028638 | -0.031704 | 0.03236 | 0.11902 | 0.07782 | -0.14648 | 0.21515 | 0.091553 | 0.21515 | -0.14191 | -3.4607 | 0.12817 | -121.3669 | 120.9366 | -0.013733 | 121.2021 | 121.2982 | 0 | -0.28381 | 0.036621 | 0.2655 | 120.9412 | 117.6224 | 121.1746 | 121.1609 | 121.2021 | 121.2112 | 121.2982 | -0.28381 | 121.1609 | 121.2021 | 121.2982 | 121.1746 | 121.2112 | -0.23804 | -121.4584
2383.2188 | 121.2982 | -121.0876 | 0.082397 | 0.0096895 | -0.015159 | 0.01054 | 0.047495 | -0.026929 | -0.030422 | 0.044109 | 0.10529 | 0.07782 | -0.12817 | 0.19684 | 0.059509 | 0.20142 | -0.18768 | -2.7557 | 0.12817 | -121.344 | 120.9595 | -0.004577 | 121.1929 | 121.2845 | -0.022888 | -0.25635 | 0.045777 | 0.23346 | 120.9 | 118.3319 | 121.1472 | 121.1655 | 121.1929 | 121.2158 | 121.2891 | -0.25635 | 121.1655 | 121.1929 | 121.2891 | 121.1472 | 121.2158 | -0.21057 | -121.4264
2384.9219 | 121.2387 | -121.0922 | 0.082397 | 0.0096895 | -0.017295 | 0.0092585 | 0.055826 | -0.026502 | -0.034267 | 0.0377 | 0.073242 | 0.11444 | -0.16479 | 0.12817 | -0.032043 | 0.082397 | -0.027466 | -0.52643 | 0.16022 | -121.4127 | 120.9274 | 0.032044 | 121.1655 | 121.2204 | -0.11444 | -0.32044 | 0.07782 | 0.23804 | 121.0648 | 120.5658 | 121.0602 | 121.2067 | 121.1655 | 121.2524 | 121.1746 | -0.32044 | 121.2067 | 121.1655 | 121.1746 | 121.0602 | 121.2524 | -0.24719 | -121.4951
2386.7031 | 121.2891 | -121.0648 | 0.09613 | 0.0096895 | 0.019662 | 0.0075495 | 0.051126 | -0.026075 | -0.031704 | 0.11589 | 0.10986 | 0.10529 | -0.10529 | 0.16479 | -0.32501 | 0.17395 | -0.20142 | -110.527 | 0.11444 | -121.3669 | 120.9595 | 0.009156 | 121.1746 | 121.2296 | -0.42114 | -0.30212 | 0.018311 | 0.21515 | 120.8633 | 10.5377 | 120.7397 | 121.17 | 121.1746 | 121.1792 | 121.2387 | -0.30212 | 121.17 | 121.1746 | 121.2387 | 120.7397 | 121.1792 | -0.20142 | -121.463
2388.5 | 120.4468 | -120.4056 | 0.10529 | 0.017319 | -0.042716 | 0.0062677 | 0.039804 | -0.02522 | -0.029995 | 0.016551 | 0.10986 | 0.068665 | -0.14648 | 0.21057 | 0.036621 | 0.18768 | -0.086975 | 0.24261 | 0.14191 | -120.6299 | 120.2591 | -0.036621 | 120.5154 | 120.6162 | -0.068665 | -0.2243 | 0.036621 | 0.25635 | 120.3186 | 120.6482 | 120.4422 | 120.4742 | 120.5154 | 120.5475 | 120.5933 | -0.2243 | 120.4742 | 120.5154 | 120.5933 | 120.4422 | 120.5475 | -0.25177 | -120.7352
2390.2969 | 121.051 | -120.9091 | 0.091553 | 0.00206 | -0.043357 | 0.0079767 | 0.042368 | -0.027357 | -0.029781 | 0.01527 | 0.018311 | 0.11902 | -0.17395 | 0.10986 | -0.045776 | 0.082397 | 0.032043 | 0.13733 | 0.19684 | -121.225 | 120.7352 | 0.027466 | 120.9274 | 121.019 | -0.13733 | -0.31586 | 0.10529 | 0.19226 | 120.9412 | 121.0464 | 120.8633 | 121.0281 | 120.9274 | 121.106 | 120.9915 | -0.31586 | 121.0281 | 120.9274 | 120.9915 | 120.8633 | 121.106 | -0.2655 | -121.3165
2392.0625 | 121.1014 | -120.9778 | 0.10071 | 0.024948 | -0.044852 | 0.011395 | 0.047708 | -0.02223 | -0.034054 | 0.015483 | 0.041199 | 0.091553 | -0.18768 | 0.11444 | -0.036621 | 0.068665 | -0.013733 | 0.09613 | 0.1831 | -121.2387 | 120.7901 | -0.009155 | 121.019 | 121.0922 | -0.13733 | -0.26093 | 0.082397 | 0.22888 | 120.9641 | 121.0739 | 120.9412 | 121.0693 | 121.019 | 121.1609 | 121.0464 | -0.26093 | 121.0693 | 121.019 | 121.0464 | 120.9412 | 121.1609 | -0.28839 | -121.3394
2393.8594 | 121.2479 | -120.932 | 0.086975 | 0.0096895 | -0.018363 | 0.0081903 | 0.04664 | -0.023511 | -0.031277 | 0.055858 | 0.027466 | 0.10529 | -0.15106 | 0.086975 | -0.050354 | 0.054932 | -0.059509 | -0.71869 | 0.17395 | -121.2936 | 120.7809 | 0.018311 | 120.9595 | 121.019 | -0.13733 | -0.36163 | 0.086975 | 0.17853 | 120.8725 | 120.2133 | 120.8817 | 121.0373 | 120.9595 | 121.106 | 120.9869 | -0.36163 | 121.0373 | 120.9595 | 120.9869 | 120.8817 | 121.106 | -0.23804 | -121.3806
2395.5938 | 121.1746 | -121.0236 | 0.10986 | 0.017319 | -0.039298 | 0.0030633 | 0.03895 | -0.025861 | -0.029781 | 0.019756 | 0.10529 | 0.050354 | -0.13733 | 0.2243 | 0.11902 | 0.21973 | -0.13733 | 0.25635 | 0.13275 | -121.3165 | 120.8862 | -0.059509 | 121.1288 | 121.2479 | 0.009156 | -0.29297 | 0.022888 | 0.24262 | 120.8862 | 121.2799 | 121.1426 | 121.0739 | 121.1288 | 121.1563 | 121.2433 | -0.29297 | 121.0739 | 121.1288 | 121.2433 | 121.1426 | 121.1563 | -0.24719 | -121.4264
2397.375 | 121.2067 | -121.0693 | 0.086975 | 0.00206 | -0.039512 | 0.0073359 | 0.045358 | -0.024152 | -0.035335 | 0.024028 | 0.022888 | 0.10986 | -0.19226 | 0.12817 | 0.013733 | 0.09613 | -0.004578 | -0.086975 | 0.18768 | -121.3394 | 120.8771 | 0.022888 | 121.0922 | 121.1975 | -0.073242 | -0.27008 | 0.10071 | 0.21515 | 121.0648 | 120.9824 | 121.0831 | 121.1792 | 121.0922 | 121.257 | 121.1655 | -0.27008 | 121.1792 | 121.0922 | 121.1655 | 121.0831 | 121.257 | -0.27924 | -121.4264
2399.1719 | 121.2021 | -120.9869 | 0.1831 | 0.017319 | 0.034615 | 0.0064813 | 0.042795 | -0.025434 | -0.032345 | 0.25752 | 0.16022 | 0.13275 | -0.091553 | 0.14191 | 0.027466 | 0.13733 | -0.2655 | -4.3442 | 0.20142 | -121.2799 | 120.8954 | -0.050354 | 121.1472 | 121.1288 | -0.15564 | -0.29297 | 0.018311 | 0.25177 | 120.7214 | 116.6428 | 121.0144 | 121.1197 | 121.1472 | 121.1884 | 121.1243 | -0.29297 | 121.1197 | 121.1472 | 121.1243 | 121.0144 | 121.1884 | -0.27466 | -121.463
2400.9062 | 121.2387 | -121.1105 | 0.07782 | 0.0096895 | -0.034598 | 0.0051995 | 0.050058 | -0.026075 | -0.032985 | 0.025096 | 0.036621 | 0.13275 | -0.16479 | 0.14191 | 0.022888 | 0.10529 | 0.013733 | 0.11444 | 0.16937 | -121.4218 | 120.9457 | 0.054931 | 121.1472 | 121.2524 | -0.054932 | -0.31128 | 0.091553 | 0.20142 | 121.1243 | 121.225 | 121.1334 | 121.2433 | 121.1472 | 121.2799 | 121.2158 | -0.31128 | 121.2433 | 121.1472 | 121.2158 | 121.1334 | 121.2799 | -0.24261 | -121.4996
2402.6875 | 121.3715 | -121.0602 | 0.050354 | 0.017319 | -0.039298 | 0.01054 | 0.050699 | -0.022443 | -0.032558 | 0.024242 | -0.009155 | 0.09613 | -0.19226 | 0.09613 | -0.013733 | 0.07782 | -0.045776 | 0.091553 | 0.16479 | -121.3898 | 120.8679 | 0.045776 | 121.051 | 121.1563 | -0.064087 | -0.32959 | 0.11444 | 0.18311 | 121.0144 | 121.1517 | 121.0464 | 121.1563 | 121.051 | 121.225 | 121.138 | -0.32959 | 121.1563 | 121.051 | 121.138 | 121.0464 | 121.225 | -0.24261 | -121.4401
2404.4844 | 121.3989 | -121.1288 | 0.073242 | 0.00206 | -0.036094 | 0.011822 | 0.043009 | -0.026289 | -0.030208 | 0.024669 | 0.07782 | 0.068665 | -0.14648 | 0.14648 | 0.068665 | 0.17395 | -0.11902 | -0.37079 | 0.12817 | -121.431 | 120.9824 | -0.004577 | 121.2067 | 121.2753 | -0.004577 | -0.30212 | 0.054932 | 0.2243 | 121.0098 | 120.7581 | 121.1975 | 121.1975 | 121.2067 | 121.257 | 121.3028 | -0.30212 | 121.1975 | 121.2067 | 121.3028 | 121.1975 | 121.257 | -0.21973 | -121.5042
2406.2031 | 121.2662 | -121.1426 | 0.086975 | 0.00206 | -0.03353 | 0.0056269 | 0.050058 | -0.02458 | -0.034481 | 0.027233 | 0.082397 | 0.11444 | -0.16022 | 0.16022 | 0.027466 | 0.1236 | -0.050354 | 0.004578 | 0.19226 | -121.4722 | 120.9824 | 0.027466 | 121.225 | 121.3028 | -0.059509 | -0.32959 | 0.10529 | 0.24261 | 121.0922 | 121.1472 | 121.17 | 121.257 | 121.225 | 121.3348 | 121.2662 | -0.32959 | 121.257 | 121.225 | 121.2662 | 121.17 | 121.3348 | -0.24719 | -121.5591
2407.9688 | 121.3623 | -121.1334 | 0.07782 | 0.017319 | -0.03588 | 0.0064813 | 0.045786 | -0.025434 | -0.030636 | 0.033428 | 0.11444 | 0.068665 | -0.13733 | 0.2243 | 0.091553 | 0.20599 | -0.20599 | -0.073242 | 0.13733 | -121.431 | 120.9961 | -0.009155 | 121.2479 | 121.3577 | 0.013733 | -0.29755 | 0.059509 | 0.25177 | 120.9274 | 121.0602 | 121.225 | 121.2021 | 121.2479 | 121.2708 | 121.3394 | -0.29755 | 121.2021 | 121.2479 | 121.3394 | 121.225 | 121.2708 | -0.21515 | -121.5088
2409.6875 | 121.344 | -121.1792 | 0.073242 | 0.017319 | -0.036948 | 0.0032769 | 0.045786 | -0.025861 | -0.03384 | 0.025524 | -0.009155 | 0.10529 | -0.17395 | 0.09613 | -0.004578 | 0.068665 | 0.027466 | -0.22888 | 0.17853 | -121.5179 | 121.0052 | 0.032044 | 121.17 | 121.2753 | -0.07782 | -0.33875 | 0.10529 | 0.16479 | 121.2067 | 120.9503 | 121.1746 | 121.2845 | 121.17 | 121.3577 | 121.2479 | -0.33875 | 121.2845 | 121.17 | 121.2479 | 121.1746 | 121.3577 | -0.24719 | -121.5912
2411.4844 | 121.4722 | -121.1563 | 0.064087 | 0.017319 | -0.036521 | 0.0047723 | 0.041727 | -0.026075 | -0.031063 | 0.027233 | 0.059509 | 0.082397 | -0.15106 | 0.14648 | 0.032043 | 0.16937 | -0.09613 | 0.13733 | 0.14648 | -121.4905 | 121.0052 | 0.01831 | 121.2158 | 121.3028 | -0.032044 | -0.33417 | 0.082397 | 0.21057 | 121.0602 | 121.2936 | 121.1884 | 121.2387 | 121.2158 | 121.3028 | 121.3257 | -0.33417 | 121.2387 | 121.2158 | 121.3257 | 121.1884 | 121.3028 | -0.21515 | -121.5546
2413.2656 | 121.344 | -121.2112 | 0.082397 | 0.00206 | -0.033744 | 0.0096857 | 0.048349 | -0.023084 | -0.034054 | 0.024669 | 0.064087 | 0.10529 | -0.17853 | 0.13733 | 0.022888 | 0.10986 | -0.036621 | 0.036621 | 0.17395 | -121.4951 | 121.0327 | 0.022889 | 121.2753 | 121.3486 | -0.059509 | -0.28381 | 0.091553 | 0.24261 | 121.1746 | 121.2479 | 121.2341 | 121.3165 | 121.2753 | 121.3852 | 121.3211 | -0.28381 | 121.3165 | 121.2753 | 121.3211 | 121.2341 | 121.3852 | -0.26092 | -121.5775
2415.0469 | 121.3394 | -121.2341 | 0.10071 | -0.0055695 | -0.018149 | 0.0069085 | 0.042368 | -0.028852 | -0.030208 | 0.09901 | 0.10529 | 0.091553 | -0.1236 | 0.19226 | -0.009155 | 0.17395 | -0.15106 | 0.16937 | 0.16022 | -121.4905 | 121.1105 | -0.009155 | 121.3394 | 121.4264 | -0.10986 | -0.25635 | 0.059509 | 0.22888 | 121.0831 | 121.4035 | 121.225 | 121.3257 | 121.3394 | 121.3943 | 121.4081 | -0.25635 | 121.3257 | 121.3394 | 121.4081 | 121.225 | 121.3943 | -0.2243 | -121.5912
2416.75 | 121.4996 | -121.2021 | 0.059509 | 0.0096895 | -0.034171 | 0.010326 | 0.049204 | -0.026929 | -0.032985 | 0.025737 | 0.009155 | 0.11444 | -0.16937 | 0.10986 | -0.013733 | 0.07782 | -0.045776 | -0.10529 | 0.17853 | -121.5317 | 121.0327 | 0.054932 | 121.2112 | 121.312 | -0.073242 | -0.32959 | 0.11902 | 0.17853 | 121.1563 | 121.0968 | 121.1884 | 121.3165 | 121.2112 | 121.3806 | 121.2799 | -0.32959 | 121.3165 | 121.2112 | 121.2799 | 121.1884 | 121.3806 | -0.22888 | -121.5912
2418.5469 | 121.4355 | -121.2387 | 0.086975 | 0.017319 | -0.036948 | 0.0075495 | 0.043649 | -0.026716 | -0.031063 | 0.02296 | 0.10529 | 0.086975 | -0.14191 | 0.21057 | 0.11444 | 0.21973 | -0.14648 | -0.62714 | 0.15564 | -121.55 | 121.0968 | 0 | 121.344 | 121.4493 | 0.027466 | -0.31128 | 0.068665 | 0.24719 | 121.0922 | 120.6116 | 121.3531 | 121.3257 | 121.344 | 121.3943 | 121.4584 | -0.31128 | 121.3257 | 121.344 | 121.4584 | 121.3531 | 121.3943 | -0.22888 | -121.637
2420.3281 | 121.5134 | -121.2296 | 0.07782 | 0.0096895 | -0.036948 | 0.0058405 | 0.0413 | -0.02757 | -0.032772 | 0.029369 | 0.054932 | 0.07782 | -0.14191 | 0.19684 | 0.07782 | 0.20599 | -0.13275 | -0.75073 | 0.12817 | -121.5591 | 121.0876 | 0 | 121.2845 | 121.4264 | 0 | -0.32959 | 0.050354 | 0.19684 | 121.0968 | 120.4788 | 121.3074 | 121.3074 | 121.2845 | 121.3577 | 121.4355 | -0.32959 | 121.3074 | 121.2845 | 121.4355 | 121.3074 | 121.3577 | -0.21973 | -121.637
2422.0469 | 121.5179 | -121.2296 | 0.059509 | 0.0096895 | -0.035666 | 0.0064813 | 0.049204 | -0.023511 | -0.032131 | 0.030864 | -0.009155 | 0.1236 | -0.18768 | 0.07782 | -0.041199 | 0.064087 | -0.013733 | -0.92926 | 0.17395 | -121.5775 | 121.0419 | 0.064087 | 121.2204 | 121.3074 | -0.10071 | -0.3479 | 0.11444 | 0.17853 | 121.2158 | 120.3003 | 121.1884 | 121.3531 | 121.2204 | 121.4035 | 121.2936 | -0.3479 | 121.3531 | 121.2204 | 121.2936 | 121.1884 | 121.4035 | -0.24719 | -121.637
2423.8281 | 121.4676 | -121.2708 | 0.10529 | 0.017319 | -0.035453 | 0.0045587 | 0.04664 | -0.02757 | -0.033413 | 0.027446 | -0.018311 | 0.1236 | -0.20142 | 0.10071 | -0.013733 | 0.068665 | 0.050354 | -2.6001 | 0.17853 | -121.5775 | 121.0693 | 0.01831 | 121.2524 | 121.3715 | -0.11902 | -0.3067 | 0.073242 | 0.18311 | 121.3211 | 118.6707 | 121.257 | 121.3943 | 121.2524 | 121.4493 | 121.3394 | -0.3067 | 121.3943 | 121.2524 | 121.3394 | 121.257 | 121.4493 | -0.3067 | -121.6827
2425.5625 | 121.4355 | -121.2982 | 0.10071 | 0.0096895 | -0.035239 | 0.0064813 | 0.042581 | -0.025007 | -0.029995 | 0.02531 | 0.10071 | 0.07782 | -0.13275 | 0.21973 | 0.09613 | 0.21057 | -0.13733 | -1.3229 | 0.14191 | -121.6232 | 121.1655 | -0.022888 | 121.3989 | 121.5179 | -0.004578 | -0.32501 | 0.041199 | 0.23346 | 121.1609 | 119.9753 | 121.3943 | 121.376 | 121.3989 | 121.4401 | 121.5088 | -0.32501 | 121.376 | 121.3989 | 121.5088 | 121.3943 | 121.4401 | -0.23346 | -121.7239
2427.3438 | 121.4127 | -121.3028 | 0.091553 | 0.0096895 | -0.034812 | 0.0058405 | 0.049417 | -0.024152 | -0.035335 | 0.028728 | 0.059509 | 0.09613 | -0.16937 | 0.16022 | 0.013733 | 0.11444 | -0.041199 | -2.3346 | 0.1831 | -121.5683 | 121.1334 | 0.004577 | 121.3623 | 121.463 | -0.07782 | -0.2655 | 0.091552 | 0.22888 | 121.2616 | 118.9682 | 121.3165 | 121.3989 | 121.3623 | 121.4859 | 121.4172 | -0.2655 | 121.3989 | 121.3623 | 121.4172 | 121.3165 | 121.4859 | -0.26093 | -121.6599
2429.1406 | 121.5179 | -121.2982 | 0.10071 | 0.0096895 | -0.034385 | 0.0079767 | 0.046213 | -0.026075 | -0.032345 | 0.02766 | -0.004578 | 0.11902 | -0.18768 | 0.10071 | -0.013733 | 0.07782 | 0.050354 | -34.1034 | 0.17395 | -121.6141 | 121.1105 | 0.018311 | 121.2936 | 121.3989 | -0.11444 | -0.31586 | 0.073242 | 0.1831 | 121.3486 | 87.1948 | 121.2845 | 121.4172 | 121.2936 | 121.4722 | 121.376 | -0.31586 | 121.4172 | 121.2936 | 121.376 | 121.2845 | 121.4722 | -0.28839 | -121.7148
2430.9531 | 121.5042 | -121.3348 | 0.086975 | 0.0096895 | -0.033958 | 0.0084039 | 0.049417 | -0.023939 | -0.031917 | 0.02296 | 0.032043 | 0.11902 | -0.16479 | 0.10071 | -0.013733 | 0.064087 | -0.009155 | -34.227 | 0.15564 | -121.669 | 121.17 | 0.032044 | 121.3669 | 121.4355 | -0.10071 | -0.33417 | 0.068665 | 0.19684 | 121.3257 | 87.1078 | 121.3211 | 121.4539 | 121.3669 | 121.4905 | 121.3989 | -0.33417 | 121.4539 | 121.3669 | 121.3989 | 121.3211 | 121.4905 | -0.25177 | -121.756
2432.6719 | 121.5042 | -121.3531 | 0.09613 | 0.0096895 | -0.036948 | 0.0007135 | 0.042154 | -0.026502 | -0.03149 | 0.025096 | 0.082397 | 0.091553 | -0.16022 | 0.16937 | 0.059509 | 0.16479 | -0.045776 | -33.5449 | 0.14648 | -121.6461 | 121.1929 | -0.004577 | 121.4355 | 121.5225 | -0.036621 | -0.29297 | 0.050354 | 0.24261 | 121.3074 | 87.8082 | 121.4127 | 121.4447 | 121.4355 | 121.4996 | 121.5179 | -0.29297 | 121.4447 | 121.4355 | 121.5179 | 121.4127 | 121.4996 | -0.25635 | -121.7422
2434.4688 | 121.55 | -121.3348 | 0.09613 | -0.0055695 | -0.03588 | 0.0073359 | 0.041727 | -0.027357 | -0.032345 | 0.021892 | 0.10071 | 0.068665 | -0.13733 | 0.21057 | 0.10986 | 0.20142 | -0.14648 | -33.3664 | 0.12817 | -121.637 | 121.1975 | -0.027465 | 121.4355 | 121.5454 | 0.013733 | -0.30212 | 0.032044 | 0.23804 | 121.1884 | 87.9684 | 121.4447 | 121.4035 | 121.4355 | 121.463 | 121.5363 | -0.30212 | 121.4035 | 121.4355 | 121.5363 | 121.4447 | 121.463 | -0.23346 | -121.7331
2436.2656 | 121.5683 | -121.3394 | 0.082397 | 0.0096895 | -0.037803 | 0.0043451 | 0.045786 | -0.023939 | -0.03384 | 0.023387 | 0.11444 | 0.036621 | -0.13733 | 0.20599 | 0.10986 | 0.2243 | -0.20142 | -33.3572 | 0.1236 | -121.5958 | 121.2021 | -0.045776 | 121.4539 | 121.5454 | 0.027466 | -0.25635 | 0.041199 | 0.25177 | 121.138 | 87.9822 | 121.4493 | 121.376 | 121.4539 | 121.463 | 121.5637 | -0.25635 | 121.376 | 121.4539 | 121.5637 | 121.4493 | 121.463 | -0.21973 | -121.6782
2438.0625 | 121.6095 | -121.3211 | 0.059509 | 0.00206 | -0.03118 | 0.010967 | 0.049631 | -0.022657 | -0.03384 | 0.027233 | 0 | 0.11902 | -0.18768 | 0.073242 | -0.068665 | 0.054932 | 0.004578 | -33.2291 | 0.15564 | -121.6736 | 121.1334 | 0.05951 | 121.3211 | 121.3943 | -0.12817 | -0.35248 | 0.096131 | 0.18768 | 121.3257 | 88.092 | 121.2524 | 121.4401 | 121.3211 | 121.4767 | 121.376 | -0.35248 | 121.4401 | 121.3211 | 121.376 | 121.2524 | 121.4767 | -0.24719 | -121.7331
2439.8594 | 121.6324 | -121.3577 | 0.073242 | 0.00206 | -0.036521 | 0.0069085 | 0.043436 | -0.026075 | -0.031704 | 0.029796 | 0.041199 | 0.091553 | -0.13733 | 0.13275 | 0.022888 | 0.15564 | -0.10071 | -33.403 | 0.14191 | -121.6919 | 121.2204 | 0.018311 | 121.3989 | 121.4905 | -0.050354 | -0.33417 | 0.068665 | 0.17853 | 121.257 | 87.9547 | 121.3806 | 121.4493 | 121.3989 | 121.4996 | 121.5134 | -0.33417 | 121.4493 | 121.3989 | 121.5134 | 121.3806 | 121.4996 | -0.21057 | -121.7651
2441.5781 | 121.5775 | -121.3943 | 0.10071 | 0.017319 | -0.033317 | 0.0069085 | 0.047495 | -0.026502 | -0.030849 | 0.02531 | -0.004578 | 0.11444 | -0.18768 | 0.09613 | -0.009155 | 0.068665 | 0.045776 | -33.2977 | 0.16479 | -121.7194 | 121.2067 | 0.013733 | 121.3898 | 121.4905 | -0.10986 | -0.32501 | 0.064087 | 0.1831 | 121.4401 | 88.0966 | 121.3852 | 121.5088 | 121.3898 | 121.5591 | 121.463 | -0.32501 | 121.5088 | 121.3898 | 121.463 | 121.3852 | 121.5591 | -0.28839 | -121.8201
2443.3594 | 121.5637 | -121.3943 | 0.091553 | 0.017319 | -0.035453 | 0.0039179 | 0.049631 | -0.027784 | -0.032131 | 0.021892 | -0.004578 | 0.10986 | -0.17395 | 0.09613 | 0 | 0.082397 | 0.027466 | -33.3252 | 0.17395 | -121.7285 | 121.2204 | 0.01831 | 121.3898 | 121.4905 | -0.091553 | -0.33417 | 0.082397 | 0.16937 | 121.4218 | 88.0692 | 121.3943 | 121.5042 | 121.3898 | 121.5683 | 121.4767 | -0.33417 | 121.5042 | 121.3898 | 121.4767 | 121.3943 | 121.5683 | -0.2655 | -121.8201
2445.0938 | 121.5683 | -121.4172 | 0.091553 | 0.00206 | -0.036521 | 0.0084039 | 0.049631 | -0.026716 | -0.034481 | 0.023174 | 0.027466 | 0.11902 | -0.16937 | 0.10986 | -0.022888 | 0.07782 | -0.032043 | -33.4122 | 0.17395 | -121.7056 | 121.2479 | 0.027466 | 121.4447 | 121.5271 | -0.11444 | -0.28839 | 0.082397 | 0.19684 | 121.3852 | 88.0051 | 121.3943 | 121.5363 | 121.4447 | 121.5912 | 121.4951 | -0.28839 | 121.5363 | 121.4447 | 121.4951 | 121.3943 | 121.5912 | -0.26093 | -121.7972
2446.8906 | 121.6187 | -121.4035 | 0.073242 | 0.00206 | -0.038657 | 0.0092585 | 0.04664 | -0.02458 | -0.034694 | 0.023387 | -0.004578 | 0.10529 | -0.18768 | 0.09613 | -0.027466 | 0.073242 | 0.045776 | -33.815 | 0.1831 | -121.7331 | 121.2158 | 0.032044 | 121.3989 | 121.4996 | -0.10071 | -0.32959 | 0.10986 | 0.1831 | 121.4493 | 87.5885 | 121.376 | 121.5088 | 121.3989 | 121.5866 | 121.4767 | -0.32959 | 121.5088 | 121.3989 | 121.4767 | 121.376 | 121.5866 | -0.26092 | -121.8063
2448.6875 | 121.7148 | -121.4127 | 0.091553 | -0.0055695 | -0.012809 | 0.0075495 | 0.042795 | -0.026502 | -0.032558 | 0.043041 | 0.082397 | 0.07782 | -0.1236 | 0.19226 | 0.032043 | 0.20142 | -0.13733 | -34.3231 | 0.15106 | -121.6736 | 121.2891 | -0.013733 | 121.4951 | 121.6049 | -0.05951 | -0.26093 | 0.059509 | 0.20599 | 121.2753 | 87.0895 | 121.4447 | 121.4905 | 121.4951 | 121.5637 | 121.6141 | -0.26093 | 121.4905 | 121.4951 | 121.6141 | 121.4447 | 121.5637 | -0.21515 | -121.7651
2450.5 | 121.701 | -121.3898 | 0.054932 | 0.00206 | -0.027762 | 0.0088311 | 0.051126 | -0.026289 | -0.03149 | 0.053081 | 0.013733 | 0.10529 | -0.14648 | 0.07782 | -0.09613 | 0.086975 | -0.045776 | -118.5562 | 0.14648 | -121.7422 | 121.2433 | 0.050354 | 121.4035 | 121.4676 | -0.15106 | -0.35248 | 0.091552 | 0.16022 | 121.344 | 2.8336 | 121.2936 | 121.4951 | 121.4035 | 121.5363 | 121.4767 | -0.35248 | 121.4951 | 121.4035 | 121.4767 | 121.2936 | 121.5363 | -0.20142 | -121.7972
2452.2969 | 121.5363 | -121.4676 | 0.086975 | 0.0096895 | -0.018363 | 0.0051995 | 0.053049 | -0.025434 | -0.033199 | 0.048381 | 0.054932 | 0.10071 | -0.16479 | 0.15106 | -0.009155 | 0.12817 | -0.050354 | -119.1559 | 0.15106 | -121.7422 | 121.3028 | 0.013733 | 121.5225 | 121.6187 | -0.09613 | -0.27466 | 0.064087 | 0.21973 | 121.4172 | 2.3117 | 121.4584 | 121.5683 | 121.5225 | 121.6187 | 121.5958 | -0.27466 | 121.5683 | 121.5225 | 121.5958 | 121.4584 | 121.6187 | -0.25177 | -121.8292
2454.0938 | 121.6049 | -121.4447 | 0.086975 | 0.00206 | -0.019645 | 0.0045587 | 0.046213 | -0.025861 | -0.032558 | 0.056285 | 0.11444 | 0.086975 | -0.12817 | 0.20599 | 0.032043 | 0.2243 | -0.15564 | -118.4418 | 0.07782 | -121.7514 | 121.3165 | 0 | 121.5591 | 121.6507 | -0.054932 | -0.3067 | -0.009155 | 0.24262 | 121.2891 | 3.0029 | 121.4767 | 121.5317 | 121.5591 | 121.5225 | 121.669 | -0.3067 | 121.5317 | 121.5591 | 121.669 | 121.4767 | 121.5225 | -0.21515 | -121.8384
2455.8125 | 114.9078 | -105.0705 | 9.9014 | 0.0096895 | 7.0002 | 0.0047723 | 6.9721 | -0.023725 | -0.040462 | 7.0123 | 4.8798 | 8.4183 | 4.4678 | -15.6189 | -22.9477 | -22.3206 | -18.0908 | -30.0476 | -0.97961 | -94.574 | 109.5383 | -1.4832 | 109.9503 | 89.4516 | -32.8491 | 10.4965 | -10.881 | 0.41199 | 86.9797 | 75.0229 | 82.1228 | 113.4888 | 109.9503 | 104.0909 | 82.7499 | 10.4965 | 113.4888 | 109.9503 | 82.7499 | 82.1228 | 104.0909 | -5.4337 | -104.4754
2457.5938 | 121.2662 | -120.9595 | 0.059509 | 0.0096895 | -0.018363 | 0.010113 | 0.067789 | -0.024366 | -0.030422 | 0.023174 | 0.018311 | 0.10071 | -0.16937 | 0.09613 | -0.15106 | 0.068665 | -0.022888 | 0.11444 | 0.15106 | -121.3165 | 120.7901 | 0.041199 | 120.9778 | 121.0556 | -0.21057 | -0.35706 | 0.091553 | 0.18768 | 120.9366 | 121.0739 | 120.8084 | 121.0602 | 120.9778 | 121.1105 | 121.0281 | -0.35706 | 121.0602 | 120.9778 | 121.0281 | 120.8084 | 121.1105 | -0.22888 | -121.376
2459.3125 | 121.257 | -121.0876 | 0.09613 | -0.0055695 | -0.015159 | 0.0086175 | 0.064585 | -0.022871 | -0.035122 | 0.032787 | 0.036621 | 0.11444 | -0.17853 | 0.12817 | -0.17853 | 0.086975 | 0.004578 | 0.16022 | 0.16937 | -121.4081 | 120.9091 | 0.018311 | 121.1243 | 121.2158 | -0.27466 | -0.32043 | 0.073243 | 0.21515 | 121.0922 | 121.2479 | 120.9091 | 121.2021 | 121.1243 | 121.257 | 121.1746 | -0.32043 | 121.2021 | 121.1243 | 121.1746 | 120.9091 | 121.257 | -0.27466 | -121.5042
2461.1094 | 115.7547 | -109.1583 | 6.3904 | 0.017319 | 7.0002 | 0.0064813 | 6.9721 | -0.021589 | -0.02145 | 7.0123 | 4.2435 | 7.7042 | 3.5843 | -18.7408 | -26.4587 | -26.3535 | -21.5515 | -22.0825 | -1.0529 | -92.0013 | 112.7426 | 1.3138 | 113.4018 | 90.4175 | -32.8491 | 17.157 | -7.4432 | 0.65918 | 87.6068 | 87.0758 | 82.6996 | 116.8625 | 113.4018 | 108.1055 | 82.8049 | 17.157 | 116.8625 | 113.4018 | 82.8049 | 82.6996 | 108.1055 | -2.8061 | -98.3917
2462.8281 | 121.0098 | -120.8679 | 0.10071 | 0.00206 | -0.021995 | 0.0054131 | 0.013742 | -0.023939 | -0.032772 | 0.043254 | 0.032043 | 0.11444 | -0.16479 | 0.068665 | -0.036621 | 0.059509 | -0.013733 | 0.059509 | 0.19226 | -121.1655 | 120.7031 | 0.013733 | 120.9 | 120.9366 | -0.13733 | -0.29755 | 0.091553 | 0.19684 | 120.8542 | 120.9274 | 120.8313 | 120.9824 | 120.9 | 121.0602 | 120.9274 | -0.29755 | 120.9824 | 120.9 | 120.9274 | 120.8313 | 121.0602 | -0.2655 | -121.2662
2464.625 | 121.1426 | -120.9915 | 0.091553 | 0.0096895 | -0.024344 | 0.0071221 | 0.010538 | -0.02458 | -0.034267 | 0.037914 | 0.004578 | 0.1236 | -0.17853 | 0.064087 | -0.022888 | 0.045776 | 0.050354 | 0.11444 | 0.19684 | -121.2799 | 120.813 | 0.032043 | 120.9961 | 121.0556 | -0.11444 | -0.28839 | 0.10529 | 0.18311 | 121.0419 | 121.106 | 120.9686 | 121.1151 | 120.9961 | 121.1884 | 121.0373 | -0.28839 | 121.1151 | 120.9961 | 121.0373 | 120.9686 | 121.1884 | -0.27008 | -121.3715
2466.4219 | 121.1517 | -121.0556 | 0.11902 | 0.0096895 | -0.021567 | 0.0069085 | 0.0094699 | -0.02757 | -0.030636 | 0.042613 | 0.091553 | 0.073242 | -0.11444 | 0.19684 | 0.10071 | 0.20142 | -0.14191 | 0.24261 | 0.14191 | -121.3486 | 120.9412 | -0.045777 | 121.1472 | 121.2524 | -0.018311 | -0.29297 | 0.022888 | 0.20599 | 120.9137 | 121.2982 | 121.1563 | 121.1288 | 121.1472 | 121.1975 | 121.257 | -0.29297 | 121.1288 | 121.1472 | 121.257 | 121.1563 | 121.1975 | -0.23346 | -121.4676
2468.1562 | 121.3257 | -121.019 | 0.082397 | 0.0096895 | -0.019004 | 0.0058405 | 0.010324 | -0.026502 | -0.032772 | 0.044963 | 0.054932 | 0.086975 | -0.14191 | 0.13275 | -0.013733 | 0.14191 | -0.11902 | 0.14191 | 0.16022 | -121.3531 | 120.8771 | 0.004578 | 121.0739 | 121.1517 | -0.09613 | -0.33417 | 0.07782 | 0.19684 | 120.9 | 121.1609 | 121.0052 | 121.106 | 121.0739 | 121.1792 | 121.1609 | -0.33417 | 121.106 | 121.0739 | 121.1609 | 121.0052 | 121.1792 | -0.2243 | -121.4355
2469.9531 | 121.3028 | -121.0556 | 0.07782 | 0.0096895 | 0.031838 | 0.0077631 | 0.016092 | -0.02522 | -0.03149 | 0.16886 | 0.073242 | 0.10071 | -0.12817 | 0.1236 | -0.20599 | 0.10529 | -0.18768 | 0.13275 | 0.17395 | -121.3074 | 120.9274 | 0.022888 | 121.1288 | 121.1792 | -0.28381 | -0.25177 | 0.09613 | 0.20142 | 120.8679 | 121.1884 | 120.8496 | 121.1563 | 121.1288 | 121.2296 | 121.1609 | -0.25177 | 121.1563 | 121.1288 | 121.1609 | 120.8496 | 121.2296 | -0.20599 | -121.3852
2471.75 | 120.9824 | -120.6024 | 0.10071 | 0.017319 | 0.078835 | 0.0096857 | 0.04899 | -0.023298 | 0.006962 | 0.25175 | 0 | 0.13733 | -0.15564 | 0.009155 | -75.4349 | -0.050354 | -0.041199 | -0.036621 | 0.2243 | -120.9641 | 120.4468 | 0.036621 | 120.6024 | 120.6116 | -75.5356 | -0.36163 | 0.1236 | 0.15564 | 120.5612 | 120.5658 | 45.1675 | 120.7397 | 120.6024 | 120.8267 | 120.5521 | -0.36163 | 120.7397 | 120.6024 | 120.5521 | 45.1675 | 120.8267 | -0.25635 | -121.0648
2473.5469 | 121.2204 | -120.8862 | 0.082397 | 0.0096895 | 0.0055628 | 0.0077631 | 0.042581 | -0.02522 | -0.032558 | 0.044963 | 0.064087 | 0.064087 | -0.1236 | 0.13275 | -1.4786 | 0.15564 | -0.12817 | 0.14648 | 0.15106 | -121.2341 | 120.7626 | -0.01831 | 120.9503 | 121.019 | -1.561 | -0.3479 | 0.068665 | 0.18768 | 120.7581 | 121.0327 | 119.4077 | 120.9503 | 120.9503 | 121.0373 | 121.0419 | -0.3479 | 120.9503 | 120.9503 | 121.0419 | 119.4077 | 121.0373 | -0.20599 | -121.3165
2475.3281 | 121.0648 | -120.8679 | 0.19684 | -0.0055695 | 0.24973 | 0.0064813 | 0.054117 | -0.026716 | 0.0039712 | 0.61406 | 0.073242 | 0.22888 | -0.12817 | -0.086975 | -70.8481 | -0.20142 | -0.14191 | -0.11444 | 0.27466 | -121.138 | 120.7397 | 0.032044 | 120.9412 | 120.7809 | -71.0449 | -0.27008 | 0.07782 | 0.20142 | 120.726 | 120.7535 | 50.0198 | 121.0968 | 120.9412 | 121.1426 | 120.6665 | -0.27008 | 121.0968 | 120.9412 | 120.6665 | 50.0198 | 121.1426 | -0.32501 | -121.3348
2477.0469 | 121.1014 | -120.0668 | 0.78278 | 0.00206 | 1.0162 | 0.0011407 | 0.050058 | -0.026716 | -0.02615 | 2.4734 | 0.31586 | 0.50812 | 0.10071 | -0.75073 | -9.2056 | -1.03 | -0.97961 | -0.90179 | 0.65002 | -120.4285 | 120.1675 | -0.27466 | 120.3827 | 119.3161 | -9.9884 | -0.36163 | -0.13275 | 0.21515 | 119.0872 | 119.165 | 110.8612 | 120.575 | 120.3827 | 120.7169 | 119.0369 | -0.36163 | 120.575 | 120.3827 | 119.0369 | 110.8612 | 120.7169 | -0.68207 | -121.2112
2478.8281 | 121.3257 | -121.0144 | 0.068665 | 0.00206 | 0.010262 | 0.0051995 | 0.045999 | -0.027998 | -0.030208 | 0.051158 | 0.045776 | 0.086975 | -0.13733 | 0.14648 | -0.19226 | 0.13733 | -0.11902 | 0.073242 | 0.15106 | -121.3669 | 120.8771 | 0.01831 | 121.0602 | 121.1609 | -0.26093 | -0.35248 | 0.082397 | 0.18311 | 120.8954 | 121.0876 | 120.8221 | 121.1014 | 121.0602 | 121.1655 | 121.1517 | -0.35248 | 121.1014 | 121.0602 | 121.1517 | 120.8221 | 121.1655 | -0.20599 | -121.4355
2480.625 | 120.8954 | -119.6503 | 1.2726 | -0.0055695 | 2.3776 | 0.0028497 | 0.051554 | -0.026929 | -0.016964 | 5.8322 | 0.71869 | 1.0757 | 0.36163 | -1.7807 | -26.5274 | -2.6001 | -2.1606 | -1.7578 | 1.2543 | -119.4763 | 120.0119 | -0.19684 | 120.369 | 117.8696 | -27.8 | 0.17395 | -0.018311 | 0.35706 | 117.4896 | 117.8925 | 93.1229 | 120.726 | 120.369 | 120.9045 | 117.0502 | 0.17395 | 120.726 | 120.369 | 117.0502 | 93.1229 | 120.9045 | -0.91095 | -120.7489
2482.3438 | 121.2479 | -120.9595 | 0.15564 | 0.0096895 | 0.15339 | 0.0043451 | 0.057962 | -0.024366 | -0.0090598 | 0.38697 | 0.15564 | 0.1236 | -0.10529 | 0.086975 | -17.9077 | 0.036621 | -0.33875 | 0.11444 | 0.19684 | -121.2479 | 120.8542 | -0.032044 | 121.1151 | 121.0464 | -18.0634 | -0.28839 | 0.041198 | 0.26093 | 120.6207 | 121.0739 | 103.0518 | 121.0831 | 121.1151 | 121.1563 | 120.9961 | -0.28839 | 121.0831 | 121.1151 | 120.9961 | 103.0518 | 121.1563 | -0.26093 | -121.4035
2484.125 | 116.6702 | -116.4001 | 0.22888 | 0.024948 | 2.3392 | 0.0062677 | 6.9721 | -0.032484 | -0.020595 | 7.0123 | 0.5127 | 1.2039 | 0.37994 | -1.1124 | -46.2982 | -1.6205 | -1.3092 | -1.3275 | -7.8094 | -106.5811 | 116.7801 | 0.97504 | 116.9128 | 115.2878 | -46.5271 | 9.819 | -8.0383 | 0.13275 | 115.0909 | 115.0726 | 70.1019 | 117.6041 | 116.9128 | 108.5907 | 114.7797 | 9.819 | 117.6041 | 116.9128 | 114.7797 | 70.1019 | 108.5907 | 0.15106 | -106.81
2485.8594 | 120.3323 | -118.7073 | 1.7303 | 0.0096895 | 3.2558 | 0.0086175 | 1.9015 | -0.020948 | 0.011875 | 7.0123 | 0.86517 | 1.4145 | 0.50354 | -2.6642 | -82.196 | -3.7949 | -2.6001 | -2.3529 | 1.6113 | -118.1396 | 119.2108 | -0.31586 | 119.5724 | 116.0431 | -83.9264 | 0.56763 | -0.11902 | 0.36163 | 116.1072 | 116.3544 | 36.5112 | 120.1218 | 119.5724 | 120.3186 | 114.9124 | 0.56763 | 120.1218 | 119.5724 | 114.9124 | 36.5112 | 120.3186 | -1.2268 | -119.87
2487.6406 | 120.9 | -120.1721 | 0.55847 | 0.0096895 | 0.97605 | 0.0047723 | 0.52473 | -0.02522 | 0.01508 | 2.9663 | 0.32959 | 0.48981 | 0.068665 | -0.66834 | -80.3787 | -1.0071 | -0.89722 | -0.59052 | 0.58594 | -120.2774 | 120.2408 | -0.068665 | 120.5017 | 119.5038 | -80.9372 | -0.10529 | 0.027465 | 0.26092 | 119.2749 | 119.5816 | 39.7934 | 120.6619 | 120.5017 | 120.7581 | 119.165 | -0.10529 | 120.6619 | 120.5017 | 119.165 | 39.7934 | 120.7581 | -0.48981 | -120.8359
2489.4375 | 121.0739 | -120.7169 | 0.16479 | 0.0096895 | 0.21961 | 0.0056269 | 0.09791 | -0.027784 | 0.01273 | 0.6602 | 0.10071 | 0.17395 | -0.082397 | -0.022888 | -75.9064 | -0.07782 | -0.26093 | 0.059509 | 0.24261 | -120.9869 | 120.6345 | 0.009155 | 120.8176 | 120.694 | -76.0712 | -0.27008 | 0.07782 | 0.18311 | 120.4559 | 120.7764 | 44.8105 | 120.8908 | 120.8176 | 120.9595 | 120.639 | -0.27008 | 120.8908 | 120.8176 | 120.639 | 44.8105 | 120.9595 | -0.24719 | -121.1517
2491.1719 | 120.3049 | -120.0485 | 0.11902 | 0.017319 | 0.051492 | 0.0028497 | 0.33012 | -0.025007 | -0.013332 | 0.44807 | 0.10529 | 0.091553 | -0.11444 | 0.16937 | -33.6456 | 0.16937 | -0.16022 | 0.24719 | 0.14191 | -120.2866 | 119.9341 | -0.027466 | 120.1538 | 120.2179 | -33.7646 | -0.23804 | 0.022888 | 0.21973 | 119.8883 | 120.2957 | 86.4029 | 120.1401 | 120.1538 | 120.1904 | 120.2179 | -0.23804 | 120.1401 | 120.1538 | 120.2179 | 86.4029 | 120.1904 | -0.23346 | -120.4056
2492.9531 | 120.9732 | -120.6894 | 0.068665 | 0.0096895 | 0.0079126 | 0.0056269 | 0.082529 | -0.026289 | -0.012905 | 0.092174 | 0.041199 | 0.064087 | -0.13733 | 0.14648 | -39.7934 | 0.14648 | -0.09613 | 0.20599 | 0.14648 | -121.0144 | 120.5521 | -0.004578 | 120.7306 | 120.8359 | -39.8621 | -0.32501 | 0.077819 | 0.17853 | 120.5933 | 120.8954 | 80.896 | 120.7535 | 120.7306 | 120.8359 | 120.8359 | -0.32501 | 120.7535 | 120.7306 | 120.8359 | 80.896 | 120.8359 | -0.20599 | -121.0831
2494.6719 | 121.0327 | -120.7489 | 0.09613 | 0.017319 | 0.041665 | 0.0073359 | 0.29722 | -0.023939 | -0.0022238 | 0.42543 | 0.12817 | 0.082397 | -0.1236 | 0.19226 | -52.9266 | 0.15106 | -0.21515 | 0.21515 | 0.12817 | -120.9732 | 120.6253 | -0.013733 | 120.8771 | 120.9412 | -53.0228 | -0.22431 | 0.032044 | 0.25177 | 120.5338 | 120.9641 | 67.8223 | 120.8313 | 120.8771 | 120.8771 | 120.9 | -0.22431 | 120.8313 | 120.8771 | 120.9 | 67.8223 | 120.8771 | -0.21973 | -121.0693
2496.4531 | 120.6711 | -120.1401 | 0.35248 | 0.0096895 | 0.55885 | 0.0032769 | 0.21925 | -0.023939 | -0.02679 | 1.6463 | 0.27008 | 0.32044 | 0.009155 | -0.21057 | -8.6655 | -0.37994 | -0.53558 | -0.10986 | 0.40741 | -120.2911 | 120.1492 | -0.032043 | 120.4102 | 119.9295 | -9.0179 | -0.15106 | 0.054932 | 0.26093 | 119.6045 | 120.0302 | 111.4746 | 120.4605 | 120.4102 | 120.5475 | 119.7601 | -0.15106 | 120.4605 | 120.4102 | 119.7601 | 111.4746 | 120.5475 | -0.34332 | -120.6436
2498.25 | 120.8771 | -120.4605 | 0.22888 | 0.024948 | 0.22175 | 0.0066949 | 0.055826 | -0.021802 | -0.028713 | 0.73133 | 0.15564 | 0.20142 | -0.064087 | 0 | -4.129 | -0.045776 | -0.32501 | 0.068665 | 0.26093 | -120.8313 | 120.3964 | -0.027466 | 120.6162 | 120.4605 | -4.3579 | -0.37079 | 0.032043 | 0.21973 | 120.1355 | 120.5292 | 116.3315 | 120.6619 | 120.6162 | 120.7214 | 120.4147 | -0.37079 | 120.6619 | 120.6162 | 120.4147 | 116.3315 | 120.7214 | -0.29297 | -121.0602
2500.0469 | 120.5521 | -120.2225 | 0.09613 | 0.0096895 | 0.2194 | 0.0088311 | 0.047708 | -0.02223 | -0.029781 | 0.57966 | 0.20142 | 0.16479 | -0.064087 | -0.004578 | -1.2177 | -0.027466 | -0.4303 | -1.6067 | 0.22888 | -120.4239 | 120.1584 | 0.068665 | 120.4239 | 120.2179 | -1.3138 | -0.20142 | 0.13275 | 0.2655 | 119.7922 | 118.6157 | 119.0048 | 120.3873 | 120.4239 | 120.4514 | 120.195 | -0.20142 | 120.3873 | 120.4239 | 120.195 | 119.0048 | 120.4514 | -0.16022 | -120.52
2501.7812 | 120.8221 | -120.5429 | 0.09613 | 0.0096895 | 0.075417 | 0.0092585 | 0.045145 | -0.023084 | -0.029995 | 0.19471 | 0.12817 | 0.082397 | -0.10071 | 0.14648 | -0.25635 | 0.13275 | -0.25177 | -1.3321 | 0.17395 | -120.8267 | 120.4422 | -0.013733 | 120.6711 | 120.6894 | -0.35248 | -0.28381 | 0.07782 | 0.22888 | 120.2911 | 119.2108 | 120.2866 | 120.6253 | 120.6711 | 120.7169 | 120.6757 | -0.28381 | 120.6253 | 120.6711 | 120.6757 | 120.2866 | 120.7169 | -0.19684 | -120.9229
2503.5781 | 120.6985 | -120.1401 | 0.52643 | 0.017319 | 0.51527 | 0.0022089 | 0.045786 | -0.026289 | -0.030422 | 1.319 | 0.2655 | 0.27924 | 0.009155 | -0.33417 | -2.211 | -0.42572 | -0.72327 | -3.3234 | 0.3891 | -120.5109 | 120.1492 | -0.24719 | 120.4056 | 119.8059 | -2.7374 | -0.37079 | -0.13733 | 0.25635 | 119.4168 | 116.8167 | 117.9291 | 120.4193 | 120.4056 | 120.5292 | 119.7144 | -0.37079 | 120.4193 | 120.4056 | 119.7144 | 117.9291 | 120.5292 | -0.51727 | -121.0373
2505.3594 | 120.639 | -120.5292 | 0.09613 | 0.017319 | 0.014749 | 0.0084039 | 0.045999 | -0.025648 | -0.033626 | 0.034923 | 0.10529 | 0.059509 | -0.1236 | 0.23346 | 0.09613 | 0.19684 | -0.14648 | 0.25635 | 0.12817 | -120.7352 | 120.4056 | -0.036621 | 120.6345 | 120.7626 | 0 | -0.20599 | 0.032044 | 0.22888 | 120.3827 | 120.7855 | 120.6253 | 120.5887 | 120.6345 | 120.6573 | 120.726 | -0.20599 | 120.5887 | 120.6345 | 120.726 | 120.6253 | 120.6573 | -0.21973 | -120.8313
2507.1406 | 120.8496 | -120.6482 | 0.073242 | 0.024948 | 0.017953 | 0.0075495 | 0.051554 | -0.024366 | -0.031277 | 0.036205 | 0 | 0.091553 | -0.17853 | 0.10529 | -0.041199 | 0.059509 | 0.050354 | 0.07782 | 0.17853 | -120.932 | 120.4697 | 0.018311 | 120.6482 | 120.7535 | -0.11444 | -0.28381 | 0.10529 | 0.17853 | 120.6985 | 120.726 | 120.607 | 120.7397 | 120.6482 | 120.8267 | 120.7077 | -0.28381 | 120.7397 | 120.6482 | 120.7077 | 120.607 | 120.8267 | -0.25177 | -121.0052
2508.9375 | 120.7123 | -120.5704 | 0.1236 | 0.0096895 | 0.17368 | 0.0084039 | 0.057749 | -0.023939 | -0.029781 | 0.26008 | 0.082397 | 0.15564 | -0.13733 | 0.027466 | -0.46692 | -0.041199 | -0.11444 | -0.62256 | 0.21057 | -120.8954 | 120.433 | 0.032044 | 120.6528 | 120.5978 | -0.59052 | -0.32501 | 0.086975 | 0.21973 | 120.4559 | 119.9478 | 120.1035 | 120.726 | 120.6528 | 120.7809 | 120.5292 | -0.32501 | 120.726 | 120.6528 | 120.5292 | 120.1035 | 120.7809 | -0.26093 | -121.019
2510.6562 | 121.0236 | -120.7214 | 0.068665 | -0.0055695 | 0.021584 | 0.0075495 | 0.054544 | -0.025861 | -0.032985 | 0.040264 | 0.004578 | 0.091553 | -0.15564 | 0.086975 | -0.050354 | 0.064087 | -0.022888 | 0.036621 | 0.16022 | -121.0693 | 120.5658 | 0.022888 | 120.726 | 120.8084 | -0.11902 | -0.3479 | 0.091552 | 0.16022 | 120.6985 | 120.7581 | 120.6711 | 120.813 | 120.726 | 120.8817 | 120.7855 | -0.3479 | 120.813 | 120.726 | 120.7855 | 120.6711 | 120.8817 | -0.22431 | -121.138
2512.4375 | 115.9195 | -115.0864 | 0.48981 | 0.0096895 | 1.1869 | 0.0086175 | 6.9721 | -0.030775 | -0.038112 | 7.0123 | 0.28381 | 0.58594 | 0.054932 | -1.2177 | -3.0533 | -1.4145 | -1.4145 | -61.4639 | -7.2327 | -107.9453 | 115.1413 | 0.09613 | 115.3702 | 113.8687 | -3.5431 | 7.1411 | -7.7225 | 0.22888 | 113.6719 | 53.6224 | 112.0331 | 115.6723 | 115.3702 | 107.8537 | 113.6719 | 7.1411 | 115.6723 | 115.3702 | 113.6719 | 112.0331 | 107.8537 | -0.43488 | -108.4351
2514.1562 | 120.8359 | -120.4971 | 0.041199 | 0.00206 | 0.0012902 | 0.0073359 | 0.041941 | -0.025434 | -0.031063 | 0.032573 | 0.050354 | 0.059509 | -0.13733 | 0.13275 | 0.022888 | 0.16022 | -0.10986 | 0.14648 | 0.16022 | -120.8496 | 120.3598 | 0.01831 | 120.5475 | 120.6299 | -0.018311 | -0.35248 | 0.11902 | 0.18768 | 120.3873 | 120.6436 | 120.52 | 120.5566 | 120.5475 | 120.6573 | 120.6573 | -0.35248 | 120.5566 | 120.5475 | 120.6573 | 120.52 | 120.6573 | -0.17853 | -120.8908
2515.9531 | 120.8633 | -120.5795 | 0.10529 | 0.0096895 | 0.082467 | 0.0069085 | 0.04664 | -0.026075 | -0.032345 | 0.23658 | 0.14648 | 0.091553 | -0.09613 | 0.091553 | -0.16937 | 0.09613 | -0.3067 | -0.9613 | 0.17395 | -120.8862 | 120.4834 | -0.013733 | 120.726 | 120.6711 | -0.27466 | -0.3067 | 0.068664 | 0.24261 | 120.2728 | 119.6182 | 120.4102 | 120.6711 | 120.726 | 120.7535 | 120.6757 | -0.3067 | 120.6711 | 120.726 | 120.6757 | 120.4102 | 120.7535 | -0.20142 | -120.9915
2517.7344 | 120.8588 | -120.5566 | 0.21057 | 0.017319 | 0.22645 | 0.0062677 | 0.049417 | -0.025434 | -0.032558 | 0.58607 | 0.086975 | 0.21515 | -0.13733 | -0.10986 | -0.94299 | -0.20142 | -0.2655 | -3.0624 | 0.28381 | -120.8313 | 120.4193 | 0.004578 | 120.6436 | 120.4468 | -1.1536 | -0.27466 | 0.073242 | 0.2243 | 120.2911 | 117.4942 | 119.6136 | 120.7718 | 120.6436 | 120.8405 | 120.3552 | -0.27466 | 120.7718 | 120.6436 | 120.3552 | 119.6136 | 120.8405 | -0.3479 | -121.0419
2519.5156 | 120.5841 | -120.3598 | 0.064087 | 0.0096895 | 0.010476 | 0.0051995 | 0.042795 | -0.023725 | -0.030636 | 0.023601 | 0.059509 | 0.086975 | -0.15106 | 0.16937 | 0.045776 | 0.17395 | -0.16479 | 0.19226 | 0.15106 | -120.6436 | 120.2087 | 0.022888 | 120.4193 | 120.5292 | -0.018311 | -0.28381 | 0.086975 | 0.21057 | 120.195 | 120.5521 | 120.4056 | 120.4468 | 120.4193 | 120.5109 | 120.5338 | -0.28381 | 120.4468 | 120.4193 | 120.5338 | 120.4056 | 120.5109 | -0.21515 | -120.7077
2521.2969 | 120.7947 | -120.5338 | 0.059509 | 0.017319 | 0.011117 | 0.0049859 | 0.04429 | -0.023939 | -0.029781 | 0.02296 | 0.018311 | 0.11902 | -0.16022 | 0.091553 | -0.036621 | 0.086975 | -0.045776 | 0.068665 | 0.16479 | -120.8588 | 120.3735 | 0.05951 | 120.5521 | 120.6253 | -0.09613 | -0.32501 | 0.10529 | 0.17853 | 120.488 | 120.6024 | 120.4971 | 120.6528 | 120.5521 | 120.6985 | 120.6207 | -0.32501 | 120.6528 | 120.5521 | 120.6207 | 120.4971 | 120.6985 | -0.21973 | -120.9183
2523.0781 | 120.8542 | -120.5978 | 0.07782 | 0.0096895 | 0.010903 | 0.0084039 | 0.042154 | -0.025434 | -0.029995 | 0.026378 | 0.09613 | 0.068665 | -0.11902 | 0.19684 | 0.086975 | 0.21515 | -0.17395 | 0.18768 | 0.11444 | -120.9183 | 120.4788 | -0.009155 | 120.694 | 120.7947 | 0.009155 | -0.32044 | 0.036621 | 0.21515 | 120.4239 | 120.7855 | 120.6848 | 120.6665 | 120.694 | 120.7123 | 120.813 | -0.32044 | 120.6665 | 120.694 | 120.813 | 120.6848 | 120.7123 | -0.19684 | -120.9961
2524.8594 | 120.8542 | -120.694 | 0.11444 | 0.00206 | 0.014108 | 0.0022089 | 0.041513 | -0.028852 | -0.033199 | 0.025737 | 0.082397 | 0.091553 | -0.13275 | 0.17395 | 0.041199 | 0.15106 | -0.027466 | 0.14648 | 0.14648 | -120.9915 | 120.5612 | -0.022888 | 120.7764 | 120.8679 | -0.073242 | -0.29755 | 0.032043 | 0.21515 | 120.6665 | 120.8405 | 120.7352 | 120.7855 | 120.7764 | 120.8405 | 120.845 | -0.29755 | 120.7855 | 120.7764 | 120.845 | 120.7352 | 120.8405 | -0.24719 | -121.106
2526.6562 | 120.9503 | -120.7214 | 0.07782 | 0.0096895 | 0.015817 | 0.0096857 | 0.045145 | -0.02458 | -0.033199 | 0.025524 | 0.11444 | 0.07782 | -0.12817 | 0.21057 | 0.068665 | 0.21057 | -0.17853 | 0.15106 | 0.13275 | -120.9869 | 120.5933 | 0 | 120.8359 | 120.932 | -0.009155 | -0.2655 | 0.054931 | 0.24262 | 120.5429 | 120.8725 | 120.7901 | 120.7993 | 120.8359 | 120.8542 | 120.932 | -0.2655 | 120.7993 | 120.8359 | 120.932 | 120.7901 | 120.8542 | -0.20599 | -121.0648
2528.4375 | 120.8817 | -120.7489 | 0.11902 | 0.00206 | 0.014535 | 0.012035 | 0.048563 | -0.02522 | -0.03384 | 0.026805 | 0.059509 | 0.10071 | -0.16479 | 0.17395 | 0.004578 | 0.12817 | -0.036621 | 0.11902 | 0.17395 | -121.0602 | 120.5841 | -0.018311 | 120.8084 | 120.9229 | -0.11444 | -0.31128 | 0.054931 | 0.2243 | 120.7123 | 120.8679 | 120.7535 | 120.8496 | 120.8084 | 120.9229 | 120.8771 | -0.31128 | 120.8496 | 120.8084 | 120.8771 | 120.7535 | 120.9229 | -0.28381 | -121.1792
2530.1562 | 120.9503 | -120.8176 | 0.082397 | 0.0096895 | 0.015176 | 0.0047723 | 0.041941 | -0.028211 | -0.029995 | 0.023387 | 0.13275 | 0.07782 | -0.10071 | 0.22888 | 0.11444 | 0.23346 | -0.16022 | 0.21057 | 0.12817 | -121.0876 | 120.7169 | -0.004577 | 120.9503 | 121.0464 | 0.032044 | -0.27008 | 0.045777 | 0.23346 | 120.6573 | 121.0281 | 120.932 | 120.8954 | 120.9503 | 120.9457 | 121.051 | -0.27008 | 120.8954 | 120.9503 | 121.051 | 120.932 | 120.9457 | -0.18311 | -121.17
2531.9531 | 121.0419 | -120.8038 | 0.086975 | 0.00206 | 0.014962 | 0.0066949 | 0.045999 | -0.022871 | -0.033413 | 0.026592 | 0.07782 | 0.07782 | -0.12817 | 0.20142 | 0.050354 | 0.20599 | -0.15106 | 0.14191 | 0.14191 | -121.0739 | 120.6757 | -0.009155 | 120.8817 | 121.0052 | -0.036621 | -0.27008 | 0.054932 | 0.20599 | 120.6528 | 120.9457 | 120.8542 | 120.8817 | 120.8817 | 120.9457 | 121.0098 | -0.27008 | 120.8817 | 120.8817 | 121.0098 | 120.8542 | 120.9457 | -0.21515 | -121.1609
2533.7344 | 121.051 | -120.8267 | 0.064087 | 0.0096895 | 0.018594 | 0.0096857 | 0.044931 | -0.024366 | -0.032345 | 0.025524 | 0.13275 | 0.086975 | -0.11902 | 0.21973 | 0.073242 | 0.21057 | -0.19226 | 0.16937 | 0.14191 | -121.1472 | 120.7077 | 0.022888 | 120.9595 | 121.0464 | 0.009155 | -0.32043 | 0.07782 | 0.25177 | 120.6345 | 120.9961 | 120.9 | 120.9137 | 120.9595 | 120.9686 | 121.0373 | -0.32043 | 120.9137 | 120.9595 | 121.0373 | 120.9 | 120.9686 | -0.18311 | -121.2112
2535.5312 | 121.0968 | -120.845 | 0.086975 | 0.00206 | 0.017098 | 0.0026361 | 0.046427 | -0.025861 | -0.035122 | 0.027019 | 0.12817 | 0.054932 | -0.11444 | 0.2243 | 0.059509 | 0.21515 | -0.18768 | 0.16479 | 0.13733 | -121.1472 | 120.7306 | -0.032043 | 120.9732 | 121.0693 | -0.027466 | -0.30212 | 0.050354 | 0.24262 | 120.6573 | 121.0098 | 120.9045 | 120.9 | 120.9732 | 120.9824 | 121.0602 | -0.30212 | 120.9 | 120.9732 | 121.0602 | 120.9045 | 120.9824 | -0.20142 | -121.2341
2537.3125 | 121.0373 | -120.8954 | 0.09613 | 0.0096895 | 0.016458 | 0.0030633 | 0.049417 | -0.028211 | -0.033626 | 0.025096 | 0.027466 | 0.10986 | -0.16479 | 0.14191 | -0.013733 | 0.10529 | 0.013733 | 0.064087 | 0.1831 | -121.1975 | 120.7306 | 0.013733 | 120.9229 | 121.0373 | -0.10986 | -0.30212 | 0.086975 | 0.19226 | 120.9091 | 120.9595 | 120.8817 | 121.0052 | 120.9229 | 121.0785 | 121.0007 | -0.30212 | 121.0052 | 120.9229 | 121.0007 | 120.8817 | 121.0785 | -0.26092 | -121.2936
2539.0469 | 121.1792 | -120.8542 | 0.073242 | 0.00206 | 0.018167 | 0.0062677 | 0.049417 | -0.026716 | -0.032772 | 0.025737 | -0.004578 | 0.10071 | -0.16022 | 0.07782 | -0.050354 | 0.07782 | -0.013733 | 0 | 0.17853 | -121.2296 | 120.694 | 0.027466 | 120.8496 | 120.932 | -0.1236 | -0.37537 | 0.10529 | 0.15564 | 120.8405 | 120.8542 | 120.8038 | 120.9549 | 120.8496 | 121.0327 | 120.932 | -0.37537 | 120.9549 | 120.8496 | 120.932 | 120.8038 | 121.0327 | -0.23346 | -121.3028
2540.8281 | 121.0693 | -120.9366 | 0.09613 | -0.0055695 | 0.016885 | 0.0034905 | 0.0413 | -0.027357 | -0.032558 | 0.027873 | 0.10986 | 0.086975 | -0.11444 | 0.2243 | 0.082397 | 0.21973 | -0.13275 | 0.21057 | 0.15106 | -121.2753 | 120.8221 | -0.009155 | 121.0464 | 121.1609 | -0.013733 | -0.33875 | 0.054932 | 0.2243 | 120.8038 | 121.1472 | 121.019 | 121.0236 | 121.0464 | 121.0876 | 121.1563 | -0.33875 | 121.0236 | 121.0464 | 121.1563 | 121.019 | 121.0876 | -0.21057 | -121.3715
2542.6094 | 121.0739 | -120.9549 | 0.11444 | 0.017319 | 0.017312 | 0.0069085 | 0.050485 | -0.026289 | -0.034908 | 0.027233 | 0.073242 | 0.09613 | -0.16479 | 0.16022 | -0.004578 | 0.14191 | -0.045776 | 0.068665 | 0.16937 | -121.2341 | 120.7901 | -0.018311 | 121.0281 | 121.1151 | -0.11902 | -0.27924 | 0.054932 | 0.23804 | 120.9091 | 121.0236 | 120.9503 | 121.051 | 121.0281 | 121.1243 | 121.0968 | -0.27924 | 121.051 | 121.0281 | 121.0968 | 120.9503 | 121.1243 | -0.27924 | -121.3486
2544.3906 | 121.1975 | -120.9274 | 0.064087 | 0.00206 | 0.019662 | 0.0049859 | 0.048563 | -0.025007 | -0.034481 | 0.027873 | 0.050354 | 0.11902 | -0.13733 | 0.16022 | 0.004578 | 0.15106 | -0.11902 | 0.064087 | 0.15106 | -121.2524 | 120.7901 | 0.054932 | 120.9778 | 121.0876 | -0.059509 | -0.32501 | 0.086975 | 0.18768 | 120.8084 | 120.9915 | 120.932 | 121.0464 | 120.9778 | 121.0785 | 121.0785 | -0.32501 | 121.0464 | 120.9778 | 121.0785 | 120.932 | 121.0785 | -0.20142 | -121.3165
2546.1719 | 121.1838 | -120.9869 | 0.09613 | -0.0055695 | 0.01838 | 0.0086175 | 0.041941 | -0.02757 | -0.032558 | 0.026805 | 0.050354 | 0.10071 | -0.14648 | 0.13275 | -0.036621 | 0.09613 | 0.022888 | 0.073242 | 0.1831 | -121.3257 | 120.8405 | 0.004578 | 121.0373 | 121.1197 | -0.13275 | -0.33875 | 0.086975 | 0.19684 | 121.0098 | 121.0602 | 120.9503 | 121.0876 | 121.0373 | 121.17 | 121.0831 | -0.33875 | 121.0876 | 121.0373 | 121.0831 | 120.9503 | 121.17 | -0.24261 | -121.4218
2547.8906 | 121.2891 | -120.9641 | 0.073242 | 0.00206 | 0.019235 | 0.0081903 | 0.048136 | -0.02757 | -0.031704 | 0.025951 | 0.013733 | 0.1236 | -0.14191 | 0.07782 | -0.07782 | 0.064087 | -0.004578 | -0.050354 | 0.16937 | -121.3531 | 120.8221 | 0.050354 | 120.9778 | 121.0419 | -0.15106 | -0.3891 | 0.096131 | 0.15564 | 120.9595 | 120.9137 | 120.8862 | 121.0876 | 120.9778 | 121.1334 | 121.0281 | -0.3891 | 121.0876 | 120.9778 | 121.0281 | 120.8862 | 121.1334 | -0.21515 | -121.4264
2549.6719 | 121.257 | -121.019 | 0.07782 | 0.0096895 | 0.020516 | 0.0075495 | 0.0413 | -0.026075 | -0.031917 | 0.025524 | 0.10071 | 0.086975 | -0.1236 | 0.21057 | 0.050354 | 0.19684 | -0.1236 | 0.036621 | 0.15106 | -121.3669 | 120.8954 | 0.009155 | 121.1197 | 121.2296 | -0.027466 | -0.3479 | 0.073242 | 0.2243 | 120.8954 | 121.0556 | 121.0693 | 121.106 | 121.1197 | 121.17 | 121.2158 | -0.3479 | 121.106 | 121.1197 | 121.2158 | 121.0693 | 121.17 | -0.20142 | -121.4447
2551.3906 | 121.2296 | -121.0464 | 0.073242 | 0.0096895 | 0.017953 | 0.0081903 | 0.04664 | -0.027998 | -0.031704 | 0.026805 | 0 | 0.12817 | -0.16937 | 0.10529 | -0.054932 | 0.068665 | 0.068665 | -0.082397 | 0.18768 | -121.4127 | 120.8771 | 0.054932 | 121.0464 | 121.1517 | -0.12817 | -0.36621 | 0.11444 | 0.16937 | 121.1151 | 120.9641 | 120.9915 | 121.1746 | 121.0464 | 121.2341 | 121.1151 | -0.36621 | 121.1746 | 121.0464 | 121.1151 | 120.9915 | 121.2341 | -0.24261 | -121.4859
2553.1719 | 121.2479 | -121.0602 | 0.082397 | 0.024948 | 0.020303 | 0.0062677 | 0.047922 | -0.023298 | -0.033413 | 0.028942 | 0.018311 | 0.10529 | -0.16022 | 0.09613 | -0.07782 | 0.073242 | 0.004578 | -0.086975 | 0.18768 | -121.3669 | 120.9 | 0.022889 | 121.0785 | 121.1563 | -0.16022 | -0.3067 | 0.10529 | 0.17853 | 121.0648 | 120.9732 | 120.9824 | 121.1655 | 121.0785 | 121.2479 | 121.1334 | -0.3067 | 121.1655 | 121.0785 | 121.1334 | 120.9824 | 121.2479 | -0.24261 | -121.4493
2554.9688 | 121.2387 | -121.1105 | 0.11444 | 0.0096895 | 0.02073 | 0.0051995 | 0.044718 | -0.028211 | -0.032345 | 0.024669 | 0.10071 | 0.086975 | -0.12817 | 0.16479 | 0.018311 | 0.13733 | -0.018311 | 0.022888 | 0.15564 | -121.431 | 120.9824 | -0.027466 | 121.2112 | 121.2753 | -0.09613 | -0.32043 | 0.041199 | 0.22888 | 121.0922 | 121.1334 | 121.1288 | 121.1975 | 121.2112 | 121.2662 | 121.2479 | -0.32043 | 121.1975 | 121.2112 | 121.2479 | 121.1288 | 121.2662 | -0.24262 | -121.5454
2556.75 | 121.3669 | -121.0693 | 0.082397 | 0.0096895 | 0.019875 | 0.0079767 | 0.041727 | -0.027143 | -0.031917 | 0.026378 | 0.07782 | 0.091553 | -0.11444 | 0.15106 | 0.004578 | 0.17395 | -0.1236 | 0.022888 | 0.14648 | -121.4035 | 120.9549 | 0.009156 | 121.1472 | 121.2204 | -0.077819 | -0.33417 | 0.064087 | 0.19226 | 120.9457 | 121.0922 | 121.0739 | 121.1609 | 121.1472 | 121.2158 | 121.2433 | -0.33417 | 121.1609 | 121.1472 | 121.2433 | 121.0739 | 121.2158 | -0.19684 | -121.4859
2558.4688 | 121.3348 | -121.0693 | 0.073242 | 0.0096895 | 0.020944 | 0.010754 | 0.047495 | -0.024152 | -0.033413 | 0.026592 | 0.09613 | 0.091553 | -0.11902 | 0.18768 | 0.018311 | 0.19684 | -0.17395 | 0.027466 | 0.1236 | -121.3898 | 120.9503 | 0.018311 | 121.1655 | 121.257 | -0.054931 | -0.32043 | 0.050354 | 0.21515 | 120.8954 | 121.0968 | 121.0876 | 121.1609 | 121.1655 | 121.1929 | 121.2662 | -0.32043 | 121.1609 | 121.1655 | 121.2662 | 121.0876 | 121.1929 | -0.19226 | -121.463
2560.2344 | 121.2936 | -121.1151 | 0.07782 | 0.0096895 | 0.020303 | 0.0056269 | 0.048136 | -0.026716 | -0.032558 | 0.026805 | 0.022888 | 0.10986 | -0.16937 | 0.1236 | -0.064087 | 0.091553 | 0.022888 | -0.059509 | 0.17853 | -121.4264 | 120.9457 | 0.032043 | 121.138 | 121.2387 | -0.14191 | -0.31128 | 0.10071 | 0.19226 | 121.138 | 121.0556 | 121.051 | 121.225 | 121.138 | 121.2936 | 121.2067 | -0.31128 | 121.225 | 121.138 | 121.2067 | 121.051 | 121.2936 | -0.24719 | -121.5042
2562.0312 | 121.2616 | -121.1243 | 0.10529 | 0.017319 | 0.02073 | 0.0088311 | 0.048349 | -0.023511 | -0.032131 | 0.025737 | 0.064087 | 0.091553 | -0.15106 | 0.15106 | -0.027466 | 0.10986 | -0.013733 | -0.050354 | 0.16479 | -121.4218 | 120.9732 | -0.013733 | 121.1884 | 121.2753 | -0.13275 | -0.29755 | 0.059509 | 0.21515 | 121.1105 | 121.0739 | 121.0968 | 121.2158 | 121.1884 | 121.2891 | 121.2341 | -0.29755 | 121.2158 | 121.1884 | 121.2341 | 121.0968 | 121.2891 | -0.25635 | -121.5271
2563.7969 | 121.3531 | -121.1288 | 0.073242 | 0.0096895 | 0.020516 | 0.0062677 | 0.047495 | -0.02522 | -0.030849 | 0.028942 | 0.022888 | 0.10529 | -0.15106 | 0.07782 | -0.082397 | 0.064087 | 0.004578 | -0.10529 | 0.19226 | -121.4676 | 120.9778 | 0.032044 | 121.1517 | 121.2067 | -0.15564 | -0.33875 | 0.11902 | 0.17395 | 121.1334 | 121.0236 | 121.0464 | 121.2341 | 121.1517 | 121.3211 | 121.1929 | -0.33875 | 121.2341 | 121.1517 | 121.1929 | 121.0464 | 121.3211 | -0.2243 | -121.5408
2565.5312 | 121.3898 | -121.1517 | 0.082397 | 0.00206 | 0.019448 | 0.0037043 | 0.042581 | -0.024793 | -0.03149 | 0.027873 | 0.11902 | 0.07782 | -0.10986 | 0.18768 | 0.036621 | 0.20599 | -0.16479 | 0.064087 | 0.15106 | -121.4447 | 121.0419 | -0.004577 | 121.2708 | 121.3394 | -0.045776 | -0.29297 | 0.068665 | 0.22888 | 120.9869 | 121.2158 | 121.1884 | 121.2296 | 121.2708 | 121.3028 | 121.3577 | -0.29297 | 121.2296 | 121.2708 | 121.3577 | 121.1884 | 121.3028 | -0.19226 | -121.5271
2567.3125 | 121.3623 | -121.1838 | 0.09613 | 0.017319 | 0.022866 | 0.0079767 | 0.047922 | -0.026502 | -0.032131 | 0.027873 | 0 | 0.11444 | -0.17395 | 0.082397 | -0.086975 | 0.07782 | 0.07782 | -0.14648 | 0.20142 | -121.4813 | 121.0098 | 0.018311 | 121.1838 | 121.2662 | -0.1831 | -0.29755 | 0.10529 | 0.17395 | 121.2616 | 121.0373 | 121.0968 | 121.2982 | 121.1838 | 121.3852 | 121.2616 | -0.29755 | 121.2982 | 121.1838 | 121.2616 | 121.0968 | 121.3852 | -0.27008 | -121.5775
2569.0938 | 121.3303 | -121.17 | 0.10529 | 0.017319 | 0.023293 | 0.0077631 | 0.047922 | -0.023939 | -0.034481 | 0.025524 | 0.073242 | 0.11902 | -0.14191 | 0.15106 | -0.022888 | 0.1236 | -0.036621 | -0.018311 | 0.17853 | -121.4676 | 121.0281 | 0.013733 | 121.2433 | 121.3211 | -0.12817 | -0.29755 | 0.073242 | 0.21515 | 121.1334 | 121.1517 | 121.1472 | 121.2891 | 121.2433 | 121.3486 | 121.2936 | -0.29755 | 121.2891 | 121.2433 | 121.2936 | 121.1472 | 121.3486 | -0.24719 | -121.5729
2570.8125 | 121.3943 | -121.1884 | 0.082397 | 0.0096895 | 0.022439 | 0.0069085 | 0.043863 | -0.026929 | -0.030849 | 0.028301 | 0.004578 | 0.1236 | -0.15106 | 0.091553 | -0.086975 | 0.073242 | 0.064087 | -0.11444 | 0.18768 | -121.55 | 121.0373 | 0.041199 | 121.1929 | 121.2799 | -0.16937 | -0.36163 | 0.10529 | 0.15564 | 121.2524 | 121.0739 | 121.1014 | 121.312 | 121.1929 | 121.376 | 121.2616 | -0.36163 | 121.312 | 121.1929 | 121.2616 | 121.1014 | 121.376 | -0.23346 | -121.6324
2572.5938 | 121.3531 | -121.2296 | 0.11444 | 0.00206 | 0.020303 | 0.0056269 | 0.041941 | -0.028425 | -0.030636 | 0.028087 | 0.1236 | 0.064087 | -0.11444 | 0.20599 | 0.004578 | 0.1831 | -0.10071 | 0.068665 | 0.14191 | -121.5454 | 121.1151 | -0.050354 | 121.3531 | 121.4355 | -0.10986 | -0.31586 | 0.027466 | 0.23804 | 121.1288 | 121.2982 | 121.2341 | 121.2936 | 121.3531 | 121.3715 | 121.4127 | -0.31586 | 121.2936 | 121.3531 | 121.4127 | 121.2341 | 121.3715 | -0.22888 | -121.6599
2574.375 | 121.463 | -121.1929 | 0.068665 | 0.0096895 | 0.020089 | 0.0062677 | 0.042581 | -0.027143 | -0.034054 | 0.028087 | 0.07782 | 0.073242 | -0.1236 | 0.19684 | 0.009155 | 0.20599 | -0.13275 | 0.041199 | 0.15106 | -121.4859 | 121.0693 | 0.004577 | 121.2708 | 121.3898 | -0.05951 | -0.29297 | 0.082397 | 0.20142 | 121.0602 | 121.2341 | 121.2021 | 121.2662 | 121.2708 | 121.344 | 121.3989 | -0.29297 | 121.2662 | 121.2708 | 121.3989 | 121.2021 | 121.344 | -0.19226 | -121.5546
2576.1562 | 121.4081 | -121.2433 | 0.10529 | 0.017319 | 0.021157 | 0.0030633 | 0.04429 | -0.02757 | -0.032772 | 0.030437 | 0.07782 | 0.082397 | -0.1236 | 0.16022 | -0.10071 | 0.14191 | -0.013733 | -0.022888 | 0.16479 | -121.5546 | 121.1197 | -0.022889 | 121.3211 | 121.4035 | -0.20599 | -0.31128 | 0.059509 | 0.20142 | 121.2296 | 121.2204 | 121.1426 | 121.3257 | 121.3211 | 121.4081 | 121.3852 | -0.31128 | 121.3257 | 121.3211 | 121.3852 | 121.1426 | 121.4081 | -0.22888 | -121.6599
2577.875 | 121.5408 | -121.1838 | 0.091553 | 0.0096895 | 0.021371 | 0.0084039 | 0.043009 | -0.028852 | -0.032131 | 0.027446 | 0.068665 | 0.086975 | -0.1236 | 0.15106 | -0.022888 | 0.15106 | -0.11444 | -0.09613 | 0.12817 | -121.5454 | 121.0602 | -0.004578 | 121.2524 | 121.3348 | -0.11444 | -0.36163 | 0.036621 | 0.19226 | 121.0693 | 121.0876 | 121.1609 | 121.2708 | 121.2524 | 121.312 | 121.3348 | -0.36163 | 121.2708 | 121.2524 | 121.3348 | 121.1609 | 121.312 | -0.21515 | -121.637
2579.6562 | 121.5134 | -121.1975 | 0.073242 | 0.017319 | 0.021584 | 0.0073359 | 0.053049 | -0.026716 | -0.030636 | 0.030651 | 0.009155 | 0.11902 | -0.14191 | 0.091553 | -0.10071 | 0.068665 | -0.009155 | -0.19226 | 0.1831 | -121.5729 | 121.0556 | 0.045777 | 121.2067 | 121.2891 | -0.17395 | -0.37537 | 0.10986 | 0.15106 | 121.1884 | 121.0052 | 121.0968 | 121.3165 | 121.2067 | 121.3806 | 121.2662 | -0.37537 | 121.3165 | 121.2067 | 121.2662 | 121.0968 | 121.3806 | -0.21515 | -121.6461
2581.4375 | 121.4127 | -121.2845 | 0.10071 | 0.0096895 | 0.021371 | 0.0054131 | 0.045572 | -0.027998 | -0.031704 | 0.026805 | 0.13275 | 0.073242 | -0.11444 | 0.21973 | 0.045776 | 0.21057 | -0.13733 | -0.064087 | 0.14191 | -121.5866 | 121.17 | -0.027466 | 121.4172 | 121.5042 | -0.054932 | -0.30212 | 0.041199 | 0.24719 | 121.1472 | 121.2204 | 121.3303 | 121.3577 | 121.4172 | 121.4264 | 121.4951 | -0.30212 | 121.3577 | 121.4172 | 121.4951 | 121.3303 | 121.4264 | -0.21515 | -121.6873
2583.2344 | 121.4401 | -121.2708 | 0.10071 | 0.017319 | 0.023293 | 0.0090447 | 0.051981 | -0.026289 | -0.035763 | 0.028942 | 0.050354 | 0.11902 | -0.13733 | 0.09613 | -0.082397 | 0.068665 | -0.022888 | -0.2655 | 0.19226 | -121.5775 | 121.1334 | 0.018311 | 121.3211 | 121.3669 | -0.18311 | -0.3067 | 0.091553 | 0.18768 | 121.2479 | 121.0052 | 121.1884 | 121.3898 | 121.3211 | 121.463 | 121.3394 | -0.3067 | 121.3898 | 121.3211 | 121.3394 | 121.1884 | 121.463 | -0.23804 | -121.6782
2585.0312 | 121.55 | -121.2387 | 0.068665 | 0.017319 | 0.023721 | 0.0064813 | 0.049417 | -0.026929 | -0.032345 | 0.029582 | -0.009155 | 0.10986 | -0.15564 | 0.091553 | -0.086975 | 0.073242 | -0.009155 | -0.39368 | 0.18768 | -121.6095 | 121.0831 | 0.041198 | 121.2296 | 121.3303 | -0.15564 | -0.37079 | 0.11902 | 0.14649 | 121.2296 | 120.845 | 121.1517 | 121.3486 | 121.2296 | 121.4264 | 121.3119 | -0.37079 | 121.3486 | 121.2296 | 121.3119 | 121.1517 | 121.4264 | -0.22431 | -121.6782
2586.8281 | 121.4813 | -121.3028 | 0.091553 | 0.0096895 | 0.021371 | 0.0079767 | 0.047067 | -0.026502 | -0.032772 | 0.027233 | 0.013733 | 0.11444 | -0.16479 | 0.10071 | -0.07782 | 0.073242 | 0.045776 | -0.35706 | 0.20142 | -121.6278 | 121.138 | 0.022888 | 121.3165 | 121.4035 | -0.16937 | -0.32501 | 0.10986 | 0.17853 | 121.3486 | 120.9457 | 121.225 | 121.4172 | 121.3165 | 121.5042 | 121.376 | -0.32501 | 121.4172 | 121.3165 | 121.376 | 121.225 | 121.5042 | -0.25635 | -121.7194
2588.5625 | 121.5729 | -121.2799 | 0.068665 | 0.0096895 | 0.024148 | 0.0071221 | 0.042795 | -0.028425 | -0.028499 | 0.028728 | 0.045776 | 0.086975 | -0.11902 | 0.15106 | -0.004578 | 0.13733 | -0.091553 | -0.32959 | 0.15564 | -121.6324 | 121.1609 | 0.01831 | 121.3257 | 121.431 | -0.073243 | -0.35248 | 0.086975 | 0.16479 | 121.1884 | 120.9503 | 121.2753 | 121.3669 | 121.3257 | 121.4355 | 121.4172 | -0.35248 | 121.3669 | 121.3257 | 121.4172 | 121.2753 | 121.4355 | -0.18768 | -121.701
2590.3281 | 121.5591 | -121.312 | 0.07782 | 0.0096895 | 0.02543 | 0.012035 | 0.048136 | -0.026929 | -0.032558 | 0.030437 | 0.10529 | 0.07782 | -0.12817 | 0.2243 | 0.013733 | 0.20599 | -0.18768 | -0.27008 | 0.13733 | -121.5958 | 121.1838 | 0 | 121.4172 | 121.5363 | -0.064087 | -0.28381 | 0.059509 | 0.23346 | 121.1243 | 121.0419 | 121.3257 | 121.3898 | 121.4172 | 121.4493 | 121.5179 | -0.28381 | 121.3898 | 121.4172 | 121.5179 | 121.3257 | 121.4493 | -0.20599 | -121.6736
2592.1094 | 121.5775 | -121.2982 | 0.068665 | 0.017319 | 0.025216 | 0.0088311 | 0.047922 | -0.029279 | -0.034481 | 0.033428 | 0.10071 | 0.07782 | -0.10986 | 0.17853 | 0.004578 | 0.17853 | -0.15106 | -0.23804 | 0.13275 | -121.6278 | 121.1884 | 0.009155 | 121.3989 | 121.4767 | -0.064087 | -0.32959 | 0.064086 | 0.21057 | 121.1472 | 121.0602 | 121.3028 | 121.376 | 121.3989 | 121.431 | 121.4767 | -0.32959 | 121.376 | 121.3989 | 121.4767 | 121.3028 | 121.431 | -0.17853 | -121.6965
2593.8125 | 121.5179 | -121.3394 | 0.086975 | 0.00206 | 0.026498 | 0.0069085 | 0.046213 | -0.030134 | -0.03149 | 0.030864 | 0.11902 | 0.068665 | -0.11902 | 0.22888 | 0.054932 | 0.21973 | -0.14191 | -0.17395 | 0.14191 | -121.6095 | 121.2204 | -0.01831 | 121.4584 | 121.5683 | -0.032043 | -0.27008 | 0.054932 | 0.23804 | 121.1975 | 121.1655 | 121.3943 | 121.4081 | 121.4584 | 121.4813 | 121.5591 | -0.27008 | 121.4081 | 121.4584 | 121.5591 | 121.3943 | 121.4813 | -0.20599 | -121.6965
2595.5938 | 121.6415 | -121.3211 | 0.073242 | 0.017319 | 0.02543 | 0.0047723 | 0.048136 | -0.026075 | -0.03149 | 0.027446 | 0.059509 | 0.07782 | -0.10071 | 0.16479 | -0.013733 | 0.15106 | -0.10071 | -0.21973 | 0.16479 | -121.637 | 121.2204 | 0.004578 | 121.3806 | 121.4859 | -0.086975 | -0.31586 | 0.091553 | 0.16022 | 121.2204 | 121.1014 | 121.3074 | 121.3989 | 121.3806 | 121.4859 | 121.4722 | -0.31586 | 121.3989 | 121.3806 | 121.4722 | 121.3074 | 121.4859 | -0.17395 | -121.7102
2597.3125 | 121.6278 | -121.3165 | 0.068665 | 0.0096895 | 0.024789 | 0.0064813 | 0.051554 | -0.025434 | -0.035335 | 0.031719 | 0.018311 | 0.10986 | -0.15564 | 0.09613 | -0.10529 | 0.07782 | -0.004578 | -0.42572 | 0.18768 | -121.6599 | 121.1609 | 0.041198 | 121.3348 | 121.4127 | -0.17395 | -0.34332 | 0.11902 | 0.17395 | 121.312 | 120.8908 | 121.2112 | 121.4264 | 121.3348 | 121.5042 | 121.3943 | -0.34332 | 121.4264 | 121.3348 | 121.3943 | 121.2112 | 121.5042 | -0.22431 | -121.7285
2599.0938 | 121.5042 | -121.3806 | 0.09613 | 0.0096895 | 0.025216 | 0.0054131 | 0.043863 | -0.028638 | -0.031704 | 0.031505 | 0.11444 | 0.07782 | -0.10529 | 0.23346 | 0.045776 | 0.20142 | -0.14191 | -0.21057 | 0.12817 | -121.6919 | 121.2753 | -0.01831 | 121.4951 | 121.6141 | -0.050354 | -0.31128 | 0.032044 | 0.21973 | 121.2387 | 121.17 | 121.4264 | 121.4584 | 121.4951 | 121.5088 | 121.582 | -0.31128 | 121.4584 | 121.4951 | 121.582 | 121.4264 | 121.5088 | -0.20142 | -121.788
2600.8281 | 121.6644 | -121.3257 | 0.064087 | 0.00206 | 0.029489 | 0.0086175 | 0.045572 | -0.026716 | -0.029354 | 0.033641 | 0.07782 | 0.07782 | -0.11444 | 0.16937 | -0.036621 | 0.14648 | -0.10986 | -0.34332 | 0.13733 | -121.6873 | 121.2112 | 0.013733 | 121.4035 | 121.4951 | -0.10071 | -0.36163 | 0.073242 | 0.19226 | 121.2158 | 120.9824 | 121.2891 | 121.4035 | 121.4035 | 121.463 | 121.4722 | -0.36163 | 121.4035 | 121.4035 | 121.4722 | 121.2891 | 121.463 | -0.17853 | -121.7514
2602.6094 | 121.6507 | -121.3623 | 0.07782 | -0.0055695 | 0.029916 | 0.0081903 | 0.051554 | -0.023939 | -0.033413 | 0.033855 | 0.018311 | 0.11444 | -0.15564 | 0.10529 | -0.10529 | 0.086975 | -0.059509 | -0.45319 | 0.1831 | -121.6965 | 121.2067 | 0.036621 | 121.3806 | 121.4676 | -0.18311 | -0.33417 | 0.10528 | 0.17395 | 121.3028 | 120.9091 | 121.257 | 121.4767 | 121.3806 | 121.5454 | 121.4493 | -0.33417 | 121.4767 | 121.3806 | 121.4493 | 121.257 | 121.5454 | -0.23346 | -121.7743
2604.4062 | 121.6232 | -121.3577 | 0.082397 | 0.0096895 | 0.02778 | 0.010967 | 0.050058 | -0.024366 | -0.033413 | 0.037059 | 0.082397 | 0.091553 | -0.11902 | 0.1831 | -0.027466 | 0.16022 | -0.16022 | -0.31586 | 0.15106 | -121.6553 | 121.2387 | 0.009156 | 121.4401 | 121.5408 | -0.10986 | -0.29755 | 0.068665 | 0.20142 | 121.1975 | 121.0419 | 121.3303 | 121.4493 | 121.4401 | 121.5088 | 121.5179 | -0.29755 | 121.4493 | 121.4401 | 121.5179 | 121.3303 | 121.5088 | -0.20142 | -121.7377
2606.1406 | 121.6232 | -121.3852 | 0.091553 | 0.00206 | 0.027352 | 0.0037043 | 0.047067 | -0.025648 | -0.029995 | 0.03535 | 0.11444 | 0.073242 | -0.10529 | 0.21973 | -0.013733 | 0.17853 | -0.1831 | -0.31586 | 0.14648 | -121.7148 | 121.2799 | -0.018311 | 121.4996 | 121.6049 | -0.10529 | -0.32959 | 0.054931 | 0.21973 | 121.2021 | 121.0693 | 121.3715 | 121.4584 | 121.4996 | 121.5317 | 121.5637 | -0.32959 | 121.4584 | 121.4996 | 121.5637 | 121.3715 | 121.5317 | -0.19684 | -121.8063
2607.9219 | 121.5775 | -121.4218 | 0.11444 | 0.0096895 | 0.030343 | 0.0094721 | 0.045572 | -0.028425 | -0.03149 | 0.035991 | 0.13275 | 0.082397 | -0.12817 | 0.23346 | 0.022888 | 0.2243 | -0.16022 | -0.29297 | 0.1236 | -121.7331 | 121.2936 | -0.032044 | 121.5546 | 121.6553 | -0.091553 | -0.31128 | 0.009155 | 0.26093 | 121.2616 | 121.1288 | 121.4447 | 121.5042 | 121.5546 | 121.5454 | 121.6461 | -0.31128 | 121.5042 | 121.5546 | 121.6461 | 121.4447 | 121.5454 | -0.24262 | -121.8475
2609.7031 | 121.6003 | -121.3943 | 0.11444 | 0.0096895 | 0.030984 | 0.0066949 | 0.050272 | -0.027143 | -0.034694 | 0.041118 | 0.013733 | 0.10986 | -0.15106 | 0.13275 | -0.11902 | 0.082397 | 0.018311 | -0.74158 | 0.1831 | -121.7056 | 121.2433 | -0.004578 | 121.4081 | 121.5271 | -0.23346 | -0.31128 | 0.068664 | 0.16479 | 121.4127 | 120.6528 | 121.2753 | 121.5042 | 121.4081 | 121.5775 | 121.4767 | -0.31128 | 121.5042 | 121.4081 | 121.4767 | 121.2753 | 121.5775 | -0.2655 | -121.8201
2611.4844 | 121.5683 | -121.3852 | 0.07782 | 0.0096895 | 0.059823 | 0.0075495 | 0.052408 | -0.026716 | -0.034267 | 0.11717 | 0.036621 | 0.10986 | -0.15564 | 0.064087 | -0.25177 | 0.027466 | -0.032043 | -43.0939 | 0.18768 | -121.6507 | 121.2296 | 0.032043 | 121.4218 | 121.4493 | -0.32959 | -0.2655 | 0.10986 | 0.19226 | 121.3531 | 78.2913 | 121.1334 | 121.4951 | 121.4218 | 121.5729 | 121.4127 | -0.2655 | 121.4951 | 121.4218 | 121.4127 | 121.1334 | 121.5729 | -0.23346 | -121.7285
2613.2656 | 121.6873 | -121.3806 | 0.07782 | 0.00206 | 0.034188 | 0.0077631 | 0.047922 | -0.023298 | -0.033413 | 0.039409 | 0.004578 | 0.11902 | -0.14191 | 0.091553 | -0.14191 | 0.068665 | -0.013733 | -0.14191 | 0.19226 | -121.7377 | 121.2387 | 0.041199 | 121.3852 | 121.4722 | -0.21973 | -0.35706 | 0.11444 | 0.14649 | 121.3669 | 121.2387 | 121.2387 | 121.4996 | 121.3852 | 121.5729 | 121.4493 | -0.35706 | 121.4996 | 121.3852 | 121.4493 | 121.2387 | 121.5729 | -0.21973 | -121.8155
2615.0469 | 121.6232 | -121.431 | 0.10986 | 0.0096895 | 0.035043 | 0.0058405 | 0.04664 | -0.026075 | -0.032558 | 0.041118 | 0.009155 | 0.13275 | -0.13733 | 0.10071 | -0.11444 | 0.07782 | 0.041199 | -0.13275 | 0.19684 | -121.7743 | 121.2936 | 0.022888 | 121.4401 | 121.5317 | -0.2243 | -0.34332 | 0.086975 | 0.14648 | 121.4722 | 121.2982 | 121.3165 | 121.5637 | 121.4401 | 121.6278 | 121.5088 | -0.34332 | 121.5637 | 121.4401 | 121.5088 | 121.3165 | 121.6278 | -0.24719 | -121.8842
2616.7656 | 121.5683 | -121.3989 | 0.10529 | 0.0096895 | 0.036324 | 0.0034905 | 0.041513 | -0.026289 | -0.030636 | 0.049449 | 0.11902 | 0.068665 | -0.091553 | 0.21515 | -0.013733 | 0.2243 | -0.15564 | -0.16479 | 0.16479 | -121.7285 | 121.3074 | -0.036621 | 121.5179 | 121.6141 | -0.11902 | -0.32959 | 0.059509 | 0.21057 | 121.2433 | 121.2341 | 121.3852 | 121.4676 | 121.5179 | 121.5637 | 121.6232 | -0.32959 | 121.4676 | 121.5179 | 121.6232 | 121.3852 | 121.5637 | -0.19684 | -121.8338
2618.5625 | 121.4859 | -121.3669 | 0.11902 | 0.0096895 | 0.058328 | 0.0096857 | 0.051126 | -0.023298 | -0.034694 | 0.099864 | 0.082397 | 0.10071 | -0.13275 | 0.13733 | -0.66376 | 0.10529 | -0.073242 | -0.60883 | 0.19226 | -121.6187 | 121.2341 | -0.018311 | 121.4493 | 121.5042 | -0.78278 | -0.25177 | 0.073242 | 0.21515 | 121.2936 | 120.7581 | 120.7031 | 121.4676 | 121.4493 | 121.5591 | 121.4722 | -0.25177 | 121.4676 | 121.4493 | 121.4722 | 120.7031 | 121.5591 | -0.25177 | -121.7377
2620.2812 | 121.4081 | -121.2433 | 0.21057 | 0.00206 | 0.21854 | 0.0081903 | 0.045572 | -0.025861 | -0.029354 | 0.50532 | 0.18768 | 0.16479 | -0.054932 | 0.054932 | -0.84686 | 0.041199 | -0.3067 | -43.1213 | 0.22888 | -121.5363 | 121.1884 | -0.045776 | 121.431 | 121.2982 | -1.0574 | -0.29297 | 0.018311 | 0.24261 | 120.9366 | 78.1219 | 120.3964 | 121.4081 | 121.431 | 121.4722 | 121.2845 | -0.29297 | 121.4081 | 121.431 | 121.2845 | 120.3964 | 121.4722 | -0.2655 | -121.7468
2622.0625 | 115.448 | -111.4197 | 4.1382 | 0.017319 | 7.0002 | 0.0090447 | 6.9721 | -0.029493 | -0.035122 | 7.0123 | 1.9409 | 3.4653 | 1.5701 | -5.6122 | -10.9589 | -5.7953 | -7.9147 | -28.0975 | -5.5893 | -99.7604 | 112.9898 | -0.67291 | 113.3606 | 105.8075 | -15.097 | 11.6592 | -9.7275 | 0.37079 | 103.5049 | 83.3221 | 100.4608 | 114.8849 | 113.3606 | 105.8304 | 105.6244 | 11.6592 | 114.8849 | 113.3606 | 105.6244 | 100.4608 | 105.8304 | -2.5681 | -103.8986
2623.8438 | 121.0281 | -120.7993 | 0.073242 | 0.017319 | -0.010459 | 0.011822 | 0.00049769 | -0.026716 | -0.031063 | 0.016979 | 0.082397 | 0.10529 | -0.11444 | 0.15106 | 0.064087 | 0.18768 | -0.10986 | 0.27466 | 0.14191 | -121.1014 | 120.6848 | 0.032044 | 120.8817 | 120.9503 | -0.009155 | -0.30212 | 0.068665 | 0.19684 | 120.6894 | 121.0739 | 120.8633 | 120.9045 | 120.8817 | 120.9412 | 120.9869 | -0.30212 | 120.9045 | 120.8817 | 120.9869 | 120.8633 | 120.9412 | -0.18768 | -121.1746
2625.6406 | 121.1838 | -120.8817 | 0.07782 | 0.024948 | -0.00875 | 0.0081903 | 0.0028475 | -0.026289 | -0.030636 | 0.014842 | 0.068665 | 0.082397 | -0.12817 | 0.14648 | 0.036621 | 0.14648 | -0.10071 | 0.22888 | 0.15106 | -121.2387 | 120.7535 | 0.004577 | 120.9503 | 121.0281 | -0.041199 | -0.35706 | 0.073242 | 0.19684 | 120.7809 | 121.1105 | 120.9183 | 120.9641 | 120.9503 | 121.0327 | 121.0281 | -0.35706 | 120.9641 | 120.9503 | 121.0281 | 120.9183 | 121.0327 | -0.20599 | -121.3165
2627.3594 | 121.2341 | -120.9503 | 0.082397 | 0.00206 | -0.0083228 | 0.0045587 | 0.0028475 | -0.02522 | -0.030208 | 0.017406 | 0.086975 | 0.086975 | -0.09613 | 0.16937 | 0.032043 | 0.16022 | -0.11902 | 0.23804 | 0.16479 | -121.257 | 120.8542 | 0.004578 | 121.0373 | 121.1197 | -0.050354 | -0.3067 | 0.082398 | 0.1831 | 120.8313 | 121.1884 | 120.9824 | 121.0373 | 121.0373 | 121.1151 | 121.1105 | -0.3067 | 121.0373 | 121.0373 | 121.1105 | 120.9824 | 121.1151 | -0.17853 | -121.3394
2629.1406 | 121.2753 | -120.9457 | 0.073242 | 0.0096895 | -0.007041 | 0.0077631 | 0.011392 | -0.02522 | -0.033626 | 0.021465 | 0.013733 | 0.10986 | -0.15564 | 0.09613 | -0.054932 | 0.064087 | -0.013733 | 0.13733 | 0.17853 | -121.2891 | 120.7901 | 0.036621 | 120.9595 | 121.0419 | -0.12817 | -0.34332 | 0.10529 | 0.16937 | 120.932 | 121.0831 | 120.8908 | 121.0556 | 120.9595 | 121.1243 | 121.0098 | -0.34332 | 121.0556 | 120.9595 | 121.0098 | 120.8908 | 121.1243 | -0.22888 | -121.3623
2630.8594 | 121.1929 | -121.0144 | 0.11444 | 0.017319 | -0.0064002 | 0.010326 | 0.0096835 | -0.023298 | -0.035122 | 0.019115 | 0.054932 | 0.10529 | -0.14648 | 0.10986 | -0.032043 | 0.07782 | -0.027466 | 0.15564 | 0.17395 | -121.3074 | 120.8679 | -0.009155 | 121.0693 | 121.1243 | -0.14648 | -0.29297 | 0.059509 | 0.20142 | 120.9869 | 121.17 | 120.9824 | 121.1197 | 121.0693 | 121.1884 | 121.0922 | -0.29297 | 121.1197 | 121.0693 | 121.0922 | 120.9824 | 121.1884 | -0.26093 | -121.4218
2632.6406 | 121.2845 | -121.0052 | 0.09613 | 0.00206 | 0.0021448 | 0.0064813 | 0.0077609 | -0.022443 | -0.033199 | 0.032146 | 0.10529 | 0.082397 | -0.09613 | 0.18768 | 0.054932 | 0.19226 | -0.17853 | 0.26093 | 0.15106 | -121.344 | 120.9091 | -0.013733 | 121.1105 | 121.1929 | -0.041198 | -0.33874 | 0.054932 | 0.20142 | 120.8267 | 121.2662 | 121.0602 | 121.0876 | 121.1105 | 121.1563 | 121.1975 | -0.33874 | 121.0876 | 121.1105 | 121.1975 | 121.0602 | 121.1563 | -0.19226 | -121.4401
2634.4219 | 121.3028 | -121.0281 | 0.07782 | 0.0096895 | -0.0055456 | 0.0092585 | 0.0092563 | -0.023725 | -0.031917 | 0.022747 | 0.050354 | 0.10071 | -0.14191 | 0.14191 | 0.027466 | 0.14648 | -0.13733 | 0.2243 | 0.16022 | -121.3669 | 120.8862 | 0.022888 | 121.0785 | 121.17 | -0.050354 | -0.33875 | 0.082397 | 0.19226 | 120.8908 | 121.2524 | 121.0556 | 121.1288 | 121.0785 | 121.1884 | 121.1746 | -0.33875 | 121.1288 | 121.0785 | 121.1746 | 121.0556 | 121.1884 | -0.21973 | -121.4447
2636.1719 | 121.3623 | -121.0602 | 0.082397 | 0.0096895 | -0.0010596 | 0.0062677 | 0.0094699 | -0.02522 | -0.032131 | 0.02061 | 0.032043 | 0.10986 | -0.15106 | 0.07782 | -0.022888 | 0.086975 | -0.018311 | 0.12817 | 0.17853 | -121.4218 | 120.9091 | 0.027466 | 121.0922 | 121.138 | -0.10528 | -0.36163 | 0.096131 | 0.18311 | 121.0419 | 121.1884 | 121.0373 | 121.17 | 121.0922 | 121.2387 | 121.1472 | -0.36163 | 121.17 | 121.0922 | 121.1472 | 121.0373 | 121.2387 | -0.23346 | -121.5042
2637.9531 | 121.3623 | -121.0602 | 0.082397 | 0.0096895 | 0.0023584 | 0.010754 | 0.0086155 | -0.024152 | -0.032985 | 0.023174 | 0.032043 | 0.11902 | -0.1236 | 0.10529 | -0.013733 | 0.10071 | -0.068665 | 0.15564 | 0.18768 | -121.4539 | 120.9366 | 0.036622 | 121.0922 | 121.1655 | -0.09613 | -0.39368 | 0.10529 | 0.15564 | 120.9915 | 121.2158 | 121.0464 | 121.1792 | 121.0922 | 121.2479 | 121.1609 | -0.39368 | 121.1792 | 121.0922 | 121.1609 | 121.0464 | 121.2479 | -0.20599 | -121.5363
2639.7344 | 121.3806 | -121.1197 | 0.068665 | 0.00206 | -0.0012732 | 0.0077631 | 0.0071201 | -0.027998 | -0.031277 | 0.034709 | 0.082397 | 0.064087 | -0.10986 | 0.15106 | 0.045776 | 0.16937 | -0.12817 | 0.24719 | 0.15564 | -121.4218 | 121.0098 | -0.004578 | 121.2021 | 121.2708 | -0.022889 | -0.30212 | 0.086975 | 0.19226 | 120.9915 | 121.3669 | 121.1655 | 121.1838 | 121.2021 | 121.2753 | 121.2891 | -0.30212 | 121.1838 | 121.2021 | 121.2891 | 121.1655 | 121.2753 | -0.17853 | -121.4905
2641.5156 | 121.1288 | -120.6665 | 0.49896 | 0.017319 | 1.0536 | 0.0056269 | 0.025278 | -0.027357 | -0.028927 | 0.073802 | 0.39368 | 0.50812 | 0.15564 | 0.20599 | 0.091553 | 0.21057 | -0.16937 | 0.31128 | 0.48523 | -120.932 | 120.8221 | 0.009156 | 121.0602 | 120.8725 | -0.40741 | -0.2655 | -0.013733 | 0.23804 | 120.4971 | 120.9778 | 120.7581 | 121.1746 | 121.0602 | 121.1517 | 120.8771 | -0.2655 | 121.1746 | 121.0602 | 120.8771 | 120.7581 | 121.1517 | -0.34332 | -121.431
2643.3125 | 121.1746 | -120.8954 | 0.2655 | 0.00206 | 0.36701 | 0.0092585 | 0.031259 | -0.025861 | -0.034908 | 0.039836 | 0.1236 | 0.25177 | -0.054932 | 0.14648 | 0.013733 | 0.10071 | -0.013733 | 0.20599 | 0.36621 | -121.1884 | 120.8405 | -0.013733 | 121.019 | 121.0419 | -0.25177 | -0.29297 | 0.10071 | 0.17853 | 120.8817 | 121.1014 | 120.9091 | 121.1472 | 121.019 | 121.2616 | 120.9961 | -0.29297 | 121.1472 | 121.019 | 120.9961 | 120.9091 | 121.2616 | -0.32043 | -121.4539
2645.0938 | 121.2753 | -120.7718 | 0.27924 | 0.017319 | 0.48151 | 0.0071221 | 0.15623 | -0.025861 | -0.031063 | 0.03001 | 0.18768 | 0.27466 | -0.004578 | 0.19226 | 0.073242 | 0.19226 | -0.054932 | 0.2655 | 0.37994 | -121.1105 | 120.7672 | -0.004578 | 120.9595 | 120.9641 | -0.20599 | -0.33875 | 0.10071 | 0.19226 | 120.7169 | 121.0373 | 120.845 | 121.0464 | 120.9595 | 121.1517 | 120.9641 | -0.33875 | 121.0464 | 120.9595 | 120.9641 | 120.845 | 121.1517 | -0.28381 | -121.3898
2646.875 | 121.0831 | -120.2545 | 0.68207 | 0.0096895 | 1.2461 | 0.0060541 | 0.551 | -0.025434 | -0.032345 | 0.033641 | 0.28381 | 0.60883 | 0.10986 | 0.2655 | 0.10071 | 0.22888 | 0.18768 | 0.30212 | 0.737 | -120.6711 | 120.3644 | -0.073242 | 120.5383 | 120.52 | -0.58136 | -0.41656 | 0.054932 | 0.17395 | 120.4422 | 120.5566 | 120.3552 | 120.8633 | 120.5383 | 120.9915 | 120.4834 | -0.41656 | 120.8633 | 120.5383 | 120.4834 | 120.3552 | 120.9915 | -0.5722 | -121.3531
2648.6719 | 121.3211 | -121.0739 | 0.082397 | 0.00206 | -0.0031958 | 0.0064813 | 0.010324 | -0.02522 | -0.031917 | 0.033 | 0.068665 | 0.073242 | -0.10071 | 0.16022 | 0.041199 | 0.15564 | -0.13275 | 0.23804 | 0.14191 | -121.4172 | 120.9732 | -0.009155 | 121.1426 | 121.2341 | -0.041198 | -0.34332 | 0.05951 | 0.16937 | 120.9412 | 121.312 | 121.1151 | 121.1472 | 121.1426 | 121.2158 | 121.2296 | -0.34332 | 121.1472 | 121.1426 | 121.2296 | 121.1151 | 121.2158 | -0.18311 | -121.4996
2650.3906 | 121.2204 | -121.17 | 0.086975 | 0.0096895 | -0.0031958 | 0.0084039 | 0.020151 | -0.023939 | -0.034908 | 0.025951 | 0.064087 | 0.091553 | -0.15564 | 0.15564 | 0.018311 | 0.11902 | -0.032043 | 0.21057 | 0.14191 | -121.4401 | 121.0144 | 0.004578 | 121.2341 | 121.3257 | -0.068664 | -0.27008 | 0.054932 | 0.21973 | 121.138 | 121.3806 | 121.1884 | 121.2616 | 121.2341 | 121.312 | 121.2891 | -0.27008 | 121.2616 | 121.2341 | 121.2891 | 121.1884 | 121.312 | -0.24261 | -121.5271
2652.1875 | 121.3303 | -121.1334 | 0.10071 | 0.0096895 | 0.0079126 | 0.0026361 | 0.07612 | -0.025648 | -0.032772 | 0.11503 | -0.004578 | 0.10529 | -0.15106 | 0.091553 | -0.027466 | 0.054932 | 0.032043 | 0.14648 | 0.16479 | -121.4493 | 120.9824 | 0.004578 | 121.1288 | 121.225 | -0.12817 | -0.31586 | 0.064087 | 0.14648 | 121.1655 | 121.2799 | 121.106 | 121.2387 | 121.1288 | 121.2982 | 121.1884 | -0.31586 | 121.2387 | 121.1288 | 121.1884 | 121.106 | 121.2982 | -0.25177 | -121.55
2653.9844 | 121.3806 | -121.1105 | 0.050354 | 0.0096895 | -0.0111 | 0.0092585 | 0.029337 | -0.025434 | -0.032558 | 0.03236 | 0.004578 | 0.09613 | -0.15106 | 0.10986 | -0.022888 | 0.10529 | -0.068665 | 0.15564 | 0.16479 | -121.4813 | 120.9595 | 0.045776 | 121.1151 | 121.2204 | -0.073242 | -0.37079 | 0.11444 | 0.15564 | 121.0419 | 121.2662 | 121.0876 | 121.2067 | 121.1151 | 121.2753 | 121.2158 | -0.37079 | 121.2067 | 121.1151 | 121.2158 | 121.0876 | 121.2753 | -0.20142 | -121.5317
2655.7031 | 121.3989 | -121.1151 | 0.073242 | 0.0096895 | 0.00022218 | 0.011181 | 0.081034 | -0.026289 | -0.030849 | 0.11802 | 0.07782 | 0.068665 | -0.10986 | 0.19226 | 0.064087 | 0.19226 | -0.14648 | 0.27008 | 0.14191 | -121.4264 | 121.0052 | -0.004577 | 121.1929 | 121.3074 | -0.009155 | -0.31128 | 0.068665 | 0.18768 | 120.9686 | 121.3852 | 121.1792 | 121.1838 | 121.1929 | 121.257 | 121.3074 | -0.31128 | 121.1838 | 121.1929 | 121.3074 | 121.1792 | 121.257 | -0.18311 | -121.4996
2657.4844 | 121.3623 | -121.1563 | 0.068665 | 0.017319 | -0.0085364 | 0.01054 | 0.030191 | -0.023939 | -0.034054 | 0.029796 | 0.018311 | 0.11902 | -0.14191 | 0.10071 | -0.041199 | 0.064087 | 0.004578 | 0.14648 | 0.16937 | -121.4813 | 121.0144 | 0.050354 | 121.1746 | 121.257 | -0.10986 | -0.32501 | 0.10071 | 0.16022 | 121.1609 | 121.3028 | 121.1151 | 121.2753 | 121.1746 | 121.3257 | 121.2204 | -0.32501 | 121.2753 | 121.1746 | 121.2204 | 121.1151 | 121.3257 | -0.21057 | -121.55
2659.2656 | 121.4127 | -121.1426 | 0.054932 | 0.017319 | -0.0111 | 0.010113 | 0.031046 | -0.025861 | -0.031063 | 0.033214 | 0.018311 | 0.09613 | -0.14191 | 0.10529 | -0.018311 | 0.09613 | -0.068665 | 0.14648 | 0.14648 | -121.4996 | 121.0007 | 0.041198 | 121.1609 | 121.2479 | -0.073243 | -0.35706 | 0.091552 | 0.16022 | 121.0739 | 121.2891 | 121.1243 | 121.2387 | 121.1609 | 121.2891 | 121.2387 | -0.35706 | 121.2387 | 121.1609 | 121.2387 | 121.1243 | 121.2891 | -0.19684 | -121.5546
2661.0625 | 121.4264 | -121.1517 | 0.050354 | 0.0096895 | -0.0074682 | 0.012249 | 0.037668 | -0.025434 | -0.031277 | 0.041973 | -0.009155 | 0.11444 | -0.15564 | 0.082397 | -0.036621 | 0.073242 | -0.032043 | 0.14191 | 0.17395 | -121.5225 | 120.9961 | 0.064087 | 121.1426 | 121.2341 | -0.086975 | -0.37079 | 0.1236 | 0.14649 | 121.1197 | 121.2936 | 121.1151 | 121.2662 | 121.1426 | 121.3257 | 121.225 | -0.37079 | 121.2662 | 121.1426 | 121.225 | 121.1151 | 121.3257 | -0.20599 | -121.5729
2662.7812 | 121.4264 | -121.1746 | 0.050354 | 0.00206 | -0.0158 | 0.0069085 | 0.022714 | -0.024793 | -0.030849 | 0.035564 | 0.064087 | 0.064087 | -0.11902 | 0.14648 | 0.050354 | 0.17395 | -0.11902 | 0.2655 | 0.13275 | -121.5317 | 121.0556 | 0.013733 | 121.2387 | 121.3211 | 0 | -0.35706 | 0.082397 | 0.18311 | 121.0556 | 121.4401 | 121.225 | 121.2387 | 121.2387 | 121.3074 | 121.3486 | -0.35706 | 121.2387 | 121.2387 | 121.3486 | 121.225 | 121.3074 | -0.16937 | -121.582
2664.5781 | 121.3898 | -121.3165 | 0.086975 | 0.00206 | -0.014518 | 0.0071221 | 0.024423 | -0.025648 | -0.032131 | 0.032146 | 0.11444 | 0.050354 | -0.10071 | 0.23346 | 0.09613 | 0.20599 | -0.13733 | 0.3067 | 0.12817 | -121.5912 | 121.2158 | -0.036621 | 121.431 | 121.55 | 0.009155 | -0.27466 | 0.041199 | 0.21515 | 121.1792 | 121.6232 | 121.4127 | 121.3669 | 121.431 | 121.4447 | 121.5225 | -0.27466 | 121.3669 | 121.431 | 121.5225 | 121.4127 | 121.4447 | -0.18768 | -121.6782
2666.2969 | 121.582 | -121.2799 | 0.073242 | 0.017319 | -0.012382 | 0.0043451 | 0.027841 | -0.025861 | -0.031063 | 0.037486 | 0.059509 | 0.068665 | -0.1236 | 0.15106 | 0.018311 | 0.13733 | -0.10529 | 0.22888 | 0.12817 | -121.6095 | 121.1563 | -0.004577 | 121.3394 | 121.431 | -0.054931 | -0.32959 | 0.054932 | 0.1831 | 121.1746 | 121.5088 | 121.2982 | 121.3486 | 121.3394 | 121.4081 | 121.4172 | -0.32959 | 121.3486 | 121.3394 | 121.4172 | 121.2982 | 121.4081 | -0.19684 | -121.6827
2668.1094 | 121.5088 | -121.3165 | 0.064087 | 0.00206 | -0.012595 | 0.0056269 | 0.025492 | -0.025434 | -0.032772 | 0.030437 | -0.004578 | 0.09613 | -0.16479 | 0.091553 | -0.041199 | 0.054932 | 0.054932 | 0.17395 | 0.17853 | -121.6736 | 121.1517 | 0.032043 | 121.312 | 121.4081 | -0.10529 | -0.35706 | 0.11444 | 0.16022 | 121.3715 | 121.4905 | 121.2753 | 121.4127 | 121.312 | 121.4951 | 121.3715 | -0.35706 | 121.4127 | 121.312 | 121.3715 | 121.2753 | 121.4951 | -0.22888 | -121.7377
2669.8281 | 121.5546 | -121.3394 | 0.059509 | 0.00206 | -0.012809 | 0.0092585 | 0.028482 | -0.027357 | -0.031917 | 0.030437 | 0.032043 | 0.091553 | -0.14191 | 0.15564 | 0 | 0.13275 | -0.11444 | 0.20599 | 0.14191 | -121.6736 | 121.1975 | 0.032044 | 121.3715 | 121.4951 | -0.059509 | -0.33417 | 0.082398 | 0.17395 | 121.225 | 121.5454 | 121.3394 | 121.431 | 121.3715 | 121.4813 | 121.4722 | -0.33417 | 121.431 | 121.3715 | 121.4722 | 121.3394 | 121.4813 | -0.20142 | -121.7331
2671.6094 | 121.5134 | -121.3211 | 0.09613 | 0.0096895 | -0.013022 | 0.0079767 | 0.042795 | -0.026502 | -0.032985 | 0.039623 | 0.032043 | 0.09613 | -0.16022 | 0.12817 | -0.018311 | 0.082397 | 0.022888 | 0.18768 | 0.16022 | -121.7194 | 121.1609 | 0 | 121.3531 | 121.4493 | -0.11444 | -0.39825 | 0.064087 | 0.19226 | 121.344 | 121.5088 | 121.3028 | 121.4172 | 121.3531 | 121.4813 | 121.4035 | -0.39825 | 121.4172 | 121.3531 | 121.4035 | 121.3028 | 121.4813 | -0.25635 | -121.8155
2673.4062 | 121.4813 | -121.3806 | 0.091553 | 0.00206 | -0.013663 | 0.0066949 | 0.031687 | -0.026075 | -0.033626 | 0.038341 | 0.045776 | 0.086975 | -0.17395 | 0.14648 | 0.009155 | 0.10529 | -0.018311 | 0.21057 | 0.15564 | -121.6644 | 121.2067 | -0.004578 | 121.4264 | 121.5271 | -0.082398 | -0.28381 | 0.064087 | 0.21973 | 121.3623 | 121.5912 | 121.3898 | 121.4676 | 121.4264 | 121.5363 | 121.4859 | -0.28381 | 121.4676 | 121.4264 | 121.4859 | 121.3898 | 121.5363 | -0.2655 | -121.756
2675.1406 | 121.4813 | -121.3806 | 0.07782 | 0.0096895 | -0.013022 | 0.0047723 | 0.042581 | -0.026502 | -0.032772 | 0.057353 | 0.059509 | 0.086975 | -0.15106 | 0.15106 | 0.013733 | 0.1236 | -0.045776 | 0.21515 | 0.15106 | -121.6873 | 121.2296 | 0.009155 | 121.4401 | 121.5317 | -0.064087 | -0.3067 | 0.073242 | 0.21057 | 121.3348 | 121.5958 | 121.3943 | 121.4676 | 121.4401 | 121.5317 | 121.5042 | -0.3067 | 121.4676 | 121.4401 | 121.5042 | 121.3943 | 121.5317 | -0.22888 | -121.7651
2676.9375 | 121.5363 | -121.4218 | 0.091553 | 0.0096895 | -0.011313 | 0.0077631 | 0.025278 | -0.027998 | -0.030636 | 0.042613 | 0.11444 | 0.064087 | -0.091553 | 0.20599 | 0.09613 | 0.21515 | -0.12817 | 0.31586 | 0.11902 | -121.7239 | 121.3303 | -0.027466 | 121.5363 | 121.6278 | 0.004577 | -0.30212 | 0.027466 | 0.20599 | 121.2936 | 121.7377 | 121.5179 | 121.4859 | 121.5363 | 121.5408 | 121.637 | -0.30212 | 121.4859 | 121.5363 | 121.637 | 121.5179 | 121.5408 | -0.18311 | -121.8155
2678.7344 | 121.6507 | -121.344 | 0.07782 | 0.017319 | 0.02842 | 0.0090447 | 0.18144 | -0.023511 | -0.035549 | 0.28721 | -0.004578 | 0.11902 | -0.16479 | 0.050354 | -0.10071 | 0.027466 | -0.045776 | 0.059509 | 0.1831 | -121.669 | 121.1792 | 0.041199 | 121.3394 | 121.3943 | -0.17853 | -0.32501 | 0.10528 | 0.16022 | 121.2982 | 121.4035 | 121.2433 | 121.463 | 121.3394 | 121.5271 | 121.3715 | -0.32501 | 121.463 | 121.3394 | 121.3715 | 121.2433 | 121.5271 | -0.24261 | -121.7468
2680.5156 | 121.6919 | -121.4127 | 0.073242 | 0.017319 | -0.010673 | 0.014172 | 0.028696 | -0.023725 | -0.029995 | 0.036205 | 0.018311 | 0.10529 | -0.15106 | 0.086975 | -0.036621 | 0.086975 | -0.041199 | 0.14648 | 0.16937 | -121.7743 | 121.2616 | 0.032044 | 121.431 | 121.4996 | -0.10986 | -0.36163 | 0.096131 | 0.16937 | 121.3715 | 121.5591 | 121.376 | 121.5179 | 121.431 | 121.582 | 121.4996 | -0.36163 | 121.5179 | 121.431 | 121.4996 | 121.376 | 121.582 | -0.2243 | -121.8475
2682.25 | 121.6599 | -121.431 | 0.036621 | 0.0096895 | -0.016013 | 0.0060541 | 0.02421 | -0.02458 | -0.03384 | 0.028301 | 0.10529 | 0.068665 | -0.10529 | 0.1831 | 0.086975 | 0.20599 | -0.1831 | 0.27008 | 0.1236 | -121.7377 | 121.3257 | 0.032044 | 121.5363 | 121.6141 | 0.050354 | -0.3067 | 0.086975 | 0.21057 | 121.2479 | 121.7011 | 121.5179 | 121.4996 | 121.5363 | 121.5546 | 121.637 | -0.3067 | 121.4996 | 121.5363 | 121.637 | 121.5179 | 121.5546 | -0.14191 | -121.7743
2684.0469 | 121.7285 | -121.4035 | 0.041199 | 0.00206 | -0.01345 | 0.0088311 | 0.032755 | -0.02458 | -0.032558 | 0.032787 | -0.009155 | 0.10529 | -0.15564 | 0.073242 | -0.064087 | 0.064087 | -0.009155 | 0.11444 | 0.16022 | -121.7514 | 121.2479 | 0.064087 | 121.3943 | 121.4767 | -0.10529 | -0.3479 | 0.11902 | 0.14649 | 121.3943 | 121.5179 | 121.3394 | 121.5088 | 121.3943 | 121.5637 | 121.4676 | -0.3479 | 121.5088 | 121.3943 | 121.4676 | 121.3394 | 121.5637 | -0.19684 | -121.7926
2685.7656 | 121.6415 | -121.4767 | 0.086975 | 0.0096895 | -0.013877 | 0.0079767 | 0.027841 | -0.026502 | -0.03149 | 0.035778 | -0.013733 | 0.11902 | -0.16022 | 0.086975 | -0.022888 | 0.073242 | 0.045776 | 0.17853 | 0.15564 | -121.8109 | 121.3165 | 0.032044 | 121.463 | 121.5637 | -0.10986 | -0.33417 | 0.068665 | 0.14648 | 121.5225 | 121.6553 | 121.4539 | 121.5958 | 121.463 | 121.6324 | 121.55 | -0.33417 | 121.5958 | 121.463 | 121.55 | 121.4539 | 121.6324 | -0.24719 | -121.8979
2687.5469 | 121.7514 | -121.431 | 0.045776 | 0.0096895 | -0.012382 | 0.0069085 | 0.048349 | -0.024793 | -0.032772 | 0.068248 | -0.004578 | 0.10071 | -0.15564 | 0.068665 | -0.059509 | 0.082397 | -0.027466 | 0.12817 | 0.17853 | -121.7697 | 121.2753 | 0.054932 | 121.4264 | 121.4996 | -0.10528 | -0.33874 | 0.13275 | 0.15106 | 121.4035 | 121.5591 | 121.3715 | 121.5317 | 121.4264 | 121.6095 | 121.5134 | -0.33874 | 121.5317 | 121.4264 | 121.5134 | 121.3715 | 121.6095 | -0.20142 | -121.8155
2689.3438 | 120.9869 | -120.9229 | 0.086975 | 0.0096895 | 0.0017176 | 0.0064813 | 0.052622 | -0.023084 | -0.034054 | 0.029796 | 0.054932 | 0.086975 | -0.14191 | 0.13733 | -0.018311 | 0.1236 | -0.041199 | 0.20142 | 0.14191 | -121.17 | 120.7809 | 0 | 120.9778 | 121.0602 | -0.10529 | -0.24719 | 0.054932 | 0.19684 | 120.8817 | 121.1243 | 120.9045 | 121.0098 | 120.9778 | 121.0648 | 121.0464 | -0.24719 | 121.0098 | 120.9778 | 121.0464 | 120.9045 | 121.0648 | -0.22888 | -121.257
2691.0781 | 121.3806 | -121.1151 | 0.068665 | 0.00206 | 8.578e-06 | 0.0037043 | 0.048349 | -0.023298 | -0.029781 | 0.035137 | 0.064087 | 0.059509 | -0.11902 | 0.14648 | 0.041199 | 0.16937 | -0.12817 | 0.24261 | 0.11902 | -121.4172 | 120.9961 | -0.009156 | 121.1792 | 121.2616 | -0.027466 | -0.30212 | 0.050354 | 0.18311 | 120.9869 | 121.3577 | 121.1563 | 121.1746 | 121.1792 | 121.2341 | 121.2845 | -0.30212 | 121.1746 | 121.1792 | 121.2845 | 121.1563 | 121.2341 | -0.18768 | -121.4859
2692.8438 | 121.3303 | -121.2387 | 0.091553 | 0.00206 | 0.00043578 | 0.0058405 | 0.049631 | -0.026289 | -0.03149 | 0.028087 | 0.09613 | 0.050354 | -0.086975 | 0.19684 | 0.09613 | 0.19226 | -0.10529 | 0.3067 | 0.13733 | -121.5317 | 121.1517 | -0.041199 | 121.3348 | 121.4355 | 0.004577 | -0.29297 | 0.045776 | 0.1831 | 121.1334 | 121.5454 | 121.3348 | 121.2891 | 121.3348 | 121.376 | 121.431 | -0.29297 | 121.2891 | 121.3348 | 121.431 | 121.3348 | 121.376 | -0.17853 | -121.6232
2694.5781 | 121.4951 | -121.2067 | 0.041199 | 0.0096895 | -0.0014868 | 0.0051995 | 0.051767 | -0.027143 | -0.031917 | 0.031291 | 0.045776 | 0.059509 | -0.13275 | 0.16479 | 0.036621 | 0.16022 | -0.10529 | 0.25177 | 0.14191 | -121.5775 | 121.0739 | 0.01831 | 121.2524 | 121.3715 | -0.004578 | -0.37079 | 0.10071 | 0.17853 | 121.1014 | 121.4584 | 121.2433 | 121.2662 | 121.2524 | 121.3486 | 121.3669 | -0.37079 | 121.2662 | 121.2524 | 121.3669 | 121.2433 | 121.3486 | -0.17395 | -121.6187
2696.3594 | 121.0602 | -120.932 | 0.073242 | 0.017319 | -0.020499 | 0.0049859 | 0.046854 | -0.023298 | -0.030849 | 0.023815 | 0.10986 | 0.054932 | -0.11444 | 0.20142 | 0.091553 | 0.19684 | -0.14191 | 0.29297 | 0.13733 | -121.2112 | 120.8176 | -0.01831 | 121.0419 | 121.1334 | 0.018311 | -0.27924 | 0.064087 | 0.2243 | 120.7901 | 121.225 | 121.0236 | 120.9869 | 121.0419 | 121.0693 | 121.1288 | -0.27924 | 120.9869 | 121.0419 | 121.1288 | 121.0236 | 121.0693 | -0.18768 | -121.2845
2698.0781 | 121.2021 | -121.1472 | 0.10071 | 0.00206 | -0.021995 | 0.0062677 | 0.052622 | -0.02522 | -0.032345 | 0.024669 | 0.1236 | 0.054932 | -0.11444 | 0.23346 | 0.10071 | 0.19226 | -0.14648 | 0.31586 | 0.12817 | -121.3943 | 121.0327 | -0.045776 | 121.2708 | 121.3806 | 0 | -0.24719 | 0.027466 | 0.23804 | 121.0007 | 121.463 | 121.2479 | 121.2021 | 121.2708 | 121.2753 | 121.3394 | -0.24719 | 121.2021 | 121.2708 | 121.3394 | 121.2479 | 121.2753 | -0.21515 | -121.4951
2699.8594 | 121.3028 | -121.1838 | 0.082397 | 0.0096895 | -0.021567 | 0.0069085 | 0.056467 | -0.02522 | -0.033199 | 0.02766 | 0.013733 | 0.10529 | -0.16479 | 0.14191 | 0.004578 | 0.086975 | -0.004578 | 0.20599 | 0.16479 | -121.4584 | 121.019 | 0.022889 | 121.1975 | 121.3257 | -0.077819 | -0.27466 | 0.082398 | 0.17853 | 121.1792 | 121.3898 | 121.1884 | 121.2891 | 121.1975 | 121.3486 | 121.2708 | -0.27466 | 121.2891 | 121.1975 | 121.2708 | 121.1884 | 121.3486 | -0.24719 | -121.5408
2701.6562 | 121.4172 | -121.1792 | 0.050354 | 0.00206 | -0.0085364 | 0.0077631 | 0.044077 | -0.026289 | -0.030208 | 0.038555 | 0.073242 | 0.086975 | -0.10529 | 0.14191 | 0.018311 | 0.12817 | -0.1236 | 0.23346 | 0.11902 | -121.463 | 121.0739 | 0.036621 | 121.2524 | 121.3211 | -0.032043 | -0.28381 | 0.068665 | 0.17853 | 121.0556 | 121.4127 | 121.1975 | 121.2662 | 121.2524 | 121.2982 | 121.3074 | -0.28381 | 121.2662 | 121.2524 | 121.3074 | 121.1975 | 121.2982 | -0.15564 | -121.5134
2703.4375 | 120.9961 | -120.9 | 0.064087 | 0.017319 | -0.023704 | 0.0043451 | 0.055185 | -0.020948 | -0.031917 | 0.022319 | 0.027466 | 0.09613 | -0.15106 | 0.091553 | -0.027466 | 0.064087 | -0.022888 | 0.14648 | 0.16479 | -121.1426 | 120.7489 | 0.032043 | 120.9274 | 120.9915 | -0.091553 | -0.24262 | 0.10071 | 0.17853 | 120.8771 | 121.0464 | 120.8725 | 120.9961 | 120.9274 | 121.0648 | 120.9641 | -0.24262 | 120.9961 | 120.9274 | 120.9641 | 120.8725 | 121.0648 | -0.21515 | -121.2067
2705.2344 | 121.1929 | -120.9778 | 0.068665 | 0.017319 | -0.023276 | 0.0077631 | 0.049845 | -0.023725 | -0.031063 | 0.021678 | 0.11444 | 0.064087 | -0.10071 | 0.17853 | 0.073242 | 0.16937 | -0.17395 | 0.25177 | 0.11444 | -121.312 | 120.8771 | -0.004578 | 121.0922 | 121.1563 | 0.004577 | -0.33417 | 0.045776 | 0.21515 | 120.8038 | 121.2296 | 121.051 | 121.0419 | 121.0922 | 121.0922 | 121.1472 | -0.33417 | 121.0419 | 121.0922 | 121.1472 | 121.051 | 121.0922 | -0.16937 | -121.3806
2707.0312 | 121.2067 | -121.0968 | 0.09613 | 0.0096895 | -0.024558 | 0.0090447 | 0.053476 | -0.027998 | -0.029995 | 0.038341 | 0.091553 | 0.068665 | -0.10529 | 0.17853 | 0.054932 | 0.12817 | -0.041199 | 0.24719 | 0.16022 | -121.3943 | 120.9915 | -0.027465 | 121.1884 | 121.2753 | -0.041198 | -0.29755 | 0.064087 | 0.19684 | 121.0556 | 121.344 | 121.1517 | 121.1655 | 121.1884 | 121.257 | 121.225 | -0.29755 | 121.1655 | 121.1884 | 121.225 | 121.1517 | 121.257 | -0.20142 | -121.4905
2708.75 | 121.3394 | -121.0648 | 0.059509 | 0.0096895 | -0.024131 | 0.0066949 | 0.055399 | -0.023939 | -0.028499 | 0.029155 | 0.10071 | 0.068665 | -0.11444 | 0.1831 | 0.064087 | 0.17395 | -0.15564 | 0.24261 | 0.13275 | -121.4035 | 120.9503 | 0.009156 | 121.1655 | 121.2479 | 0.004578 | -0.33875 | 0.073242 | 0.21515 | 120.9091 | 121.3074 | 121.1288 | 121.1334 | 121.1655 | 121.1975 | 121.2387 | -0.33875 | 121.1334 | 121.1655 | 121.2387 | 121.1288 | 121.1975 | -0.17395 | -121.463
2710.5312 | 121.4264 | -121.1014 | 0.041199 | 0.00206 | -0.016868 | 0.010967 | 0.066721 | -0.027143 | -0.033626 | 0.062908 | 0.059509 | 0.073242 | -0.11902 | 0.17395 | 0.054932 | 0.1831 | -0.16937 | 0.25177 | 0.12817 | -121.4081 | 120.9824 | 0.032043 | 121.1609 | 121.2753 | 0.013733 | -0.3067 | 0.086975 | 0.17853 | 120.932 | 121.3531 | 121.1563 | 121.1746 | 121.1609 | 121.2296 | 121.2845 | -0.3067 | 121.1746 | 121.1609 | 121.2845 | 121.1563 | 121.2296 | -0.16022 | -121.4493
2712.25 | 120.726 | -120.4971 | 0.11902 | 0.017319 | 0.10297 | 0.0062677 | 0.06373 | -0.023725 | -0.0013692 | 0.35984 | 0.12817 | 0.10529 | -0.091553 | 0.086975 | -51.21 | 0.073242 | -0.20599 | 0.17395 | 0.18768 | -120.7306 | 120.4056 | -0.013733 | 120.6253 | 120.5841 | -51.329 | -0.23346 | 0.068664 | 0.21973 | 120.2911 | 120.6711 | 69.2871 | 120.6024 | 120.6253 | 120.6848 | 120.5704 | -0.23346 | 120.6024 | 120.6253 | 120.5704 | 69.2871 | 120.6848 | -0.21057 | -120.8496
2714.0312 | 120.9824 | -120.7718 | 0.082397 | -0.0055695 | -0.013022 | 0.0056269 | 0.044931 | -0.02522 | -0.025081 | 0.03535 | 0.086975 | 0.050354 | -0.10071 | 0.20142 | -9.9976 | 0.18768 | -0.14648 | 0.29755 | 0.14191 | -121.0648 | 120.6711 | -0.032043 | 120.8588 | 120.9732 | -10.08 | -0.29297 | 0.05951 | 0.18768 | 120.6253 | 121.0693 | 110.7742 | 120.8221 | 120.8588 | 120.9137 | 120.9595 | -0.29297 | 120.8221 | 120.8588 | 120.9595 | 110.7742 | 120.9137 | -0.18311 | -121.1472
2715.8281 | 121.1105 | -120.6665 | 0.1831 | 0.0096895 | 0.30164 | 0.0088311 | 0.056894 | -0.025007 | 0.015507 | 0.92787 | 0.064087 | 0.21515 | -0.10071 | -0.16479 | -85.5652 | -0.21973 | -0.23346 | -0.073242 | 0.33417 | -120.9366 | 120.5658 | 0.032044 | 120.7306 | 120.5017 | -85.7483 | -0.27008 | 0.15106 | 0.1648 | 120.433 | 120.5933 | 35.1013 | 120.8817 | 120.7306 | 121.0007 | 120.4468 | -0.27008 | 120.8817 | 120.7306 | 120.4468 | 35.1013 | 121.0007 | -0.28381 | -121.1197
2717.5938 | 121.1243 | -120.7306 | 0.15564 | 0.0096895 | 0.18009 | 0.0073359 | 0.055185 | -0.026716 | 0.008671 | 0.54527 | 0.041199 | 0.17853 | -0.11902 | -0.068665 | -79.1977 | -0.10529 | -0.12817 | 0.009155 | 0.25635 | -121.0648 | 120.6116 | 0.022888 | 120.7718 | 120.6619 | -79.3533 | -0.33417 | 0.10071 | 0.16022 | 120.6024 | 120.7397 | 41.5329 | 120.9091 | 120.7718 | 120.9869 | 120.6253 | -0.33417 | 120.9091 | 120.7718 | 120.6253 | 41.5329 | 120.9869 | -0.27466 | -121.2204
2719.3125 | 121.1151 | -120.813 | 0.16022 | 0.0096895 | 0.17198 | 0.0084039 | 0.055612 | -0.023084 | 0.031529 | 0.54527 | 0.15564 | 0.13275 | -0.064087 | 0.09613 | -112.7014 | 0.073242 | -0.34332 | 0.14191 | 0.21057 | -121.0922 | 120.7489 | -0.027466 | 120.9686 | 120.9091 | -112.8616 | -0.27924 | 0.050354 | 0.21973 | 120.4697 | 120.9549 | 8.1116 | 120.9457 | 120.9686 | 121.0236 | 120.8862 | -0.27924 | 120.9457 | 120.9686 | 120.8862 | 8.1116 | 121.0236 | -0.2243 | -121.2524
2721.0469 | 121.1792 | -120.9503 | 0.064087 | 0.024948 | -0.014091 | 0.0069085 | 0.055399 | -0.02757 | 0.033451 | 0.10841 | 0.11444 | 0.050354 | -0.091553 | 0.20599 | -119.3161 | 0.20599 | -0.21057 | 0.2655 | 0.10529 | -121.2524 | 120.8588 | -0.013733 | 121.0648 | 121.1563 | -119.3802 | -0.30212 | 0.041199 | 0.20599 | 120.7397 | 121.2158 | 1.6342 | 121.0007 | 121.0648 | 121.0556 | 121.1563 | -0.30212 | 121.0007 | 121.0648 | 121.1563 | 1.6342 | 121.0556 | -0.15564 | -121.3165
2722.7656 | 121.2067 | -120.9641 | 0.086975 | 0.0096895 | 0.018807 | 0.0073359 | 0.056467 | -0.028852 | 0.034092 | 0.1866 | 0.1236 | 0.064087 | -0.086975 | 0.18768 | -118.7805 | 0.15564 | -0.20599 | 0.26093 | 0.13733 | -121.2708 | 120.8771 | -0.022888 | 121.0876 | 121.1517 | -118.8675 | -0.3067 | 0.050354 | 0.21057 | 120.7581 | 121.225 | 2.1835 | 121.0281 | 121.0876 | 121.1014 | 121.1197 | -0.3067 | 121.0281 | 121.0876 | 121.1197 | 2.1835 | 121.1014 | -0.17395 | -121.3577
2724.4688 | 121.1426 | -120.9457 | 0.11444 | 0.017319 | 0.077767 | 0.0066949 | 0.072061 | -0.025434 | 0.029179 | 0.31349 | 0.018311 | 0.13275 | -0.13275 | 0.036621 | -114.386 | -0.004578 | -0.07782 | 0.09613 | 0.20142 | -121.2753 | 120.813 | 0.01831 | 120.9641 | 120.9824 | -114.5004 | -0.32959 | 0.086975 | 0.15106 | 120.8679 | 121.0419 | 6.5598 | 121.0785 | 120.9641 | 121.1472 | 120.9412 | -0.32959 | 121.0785 | 120.9641 | 120.9412 | 6.5598 | 121.1472 | -0.24719 | -121.3898
2726.1719 | 121.2845 | -120.7993 | 0.22888 | -0.0055695 | 0.41657 | 0.011181 | 0.068216 | -0.026075 | 0.031101 | 1.1379 | 0.15106 | 0.22888 | -0.027466 | -0.13275 | -113.6948 | -0.20599 | -0.35706 | 0.004578 | 0.32959 | -121.0373 | 120.7718 | 0 | 120.9503 | 120.6665 | -113.9236 | -0.23804 | 0.10071 | 0.17853 | 120.4422 | 120.8038 | 7.1045 | 121.0281 | 120.9503 | 121.1288 | 120.5933 | -0.23804 | 121.0281 | 120.9503 | 120.5933 | 7.1045 | 121.1288 | -0.25635 | -121.2662
2727.875 | 121.0098 | -120.4697 | 0.48523 | 0.0096895 | 0.7353 | 0.010113 | 0.072702 | -0.025861 | 0.030033 | 1.5877 | 0.17853 | 0.37994 | -0.018311 | -0.26093 | -114.5233 | -0.44861 | -0.3479 | -0.16937 | 0.40741 | -120.8908 | 120.4514 | -0.10529 | 120.6482 | 120.2087 | -115.0085 | -0.42114 | -0.077819 | 0.19684 | 120.1218 | 120.3003 | 5.9464 | 120.8496 | 120.6482 | 120.8771 | 120.0211 | -0.42114 | 120.8496 | 120.6482 | 120.0211 | 5.9464 | 120.8771 | -0.50354 | -121.376
2729.6094 | 121.0556 | -120.3735 | 0.50812 | 0.017319 | 0.94337 | 0.0086175 | 0.074198 | -0.024366 | 0.029179 | 2.3668 | 0.24719 | 0.44403 | 0.027466 | -0.49439 | -116.1163 | -0.69122 | -0.52643 | -0.38452 | 0.58594 | -120.5566 | 120.401 | -0.064087 | 120.6207 | 119.8792 | -116.6245 | -0.18311 | 0.077819 | 0.21973 | 119.8471 | 119.989 | 4.2572 | 120.8176 | 120.6207 | 120.9595 | 119.6823 | -0.18311 | 120.8176 | 120.6207 | 119.6823 | 4.2572 | 120.9595 | -0.48065 | -121.0648
2731.3438 | 121.2067 | -120.8954 | 0.17853 | 0.0096895 | 0.19099 | 0.0037043 | 0.073557 | -0.025861 | 0.032597 | 0.59996 | 0.15564 | 0.13733 | -0.064087 | 0.086975 | -118.0344 | 0.068665 | -0.25635 | 0.20599 | 0.22888 | -121.17 | 120.8313 | -0.041199 | 121.051 | 120.9824 | -118.2129 | -0.27466 | 0.050354 | 0.21973 | 120.639 | 121.1014 | 2.861 | 121.0327 | 121.051 | 121.1243 | 120.9641 | -0.27466 | 121.0327 | 121.051 | 120.9641 | 2.861 | 121.1243 | -0.24261 | -121.3486
2733.0625 | 121.312 | -121.0556 | 0.059509 | 0.00206 | -0.0057592 | 0.0041315 | 0.069712 | -0.025007 | 0.03281 | 0.12657 | 0.059509 | 0.064087 | -0.10986 | 0.1831 | -117.5217 | 0.19226 | -0.1236 | 0.2655 | 0.11902 | -121.3715 | 120.9457 | 0.004578 | 121.1151 | 121.2387 | -117.5812 | -0.31586 | 0.05951 | 0.16937 | 120.932 | 121.3211 | 3.5339 | 121.1197 | 121.1151 | 121.1746 | 121.2479 | -0.31586 | 121.1197 | 121.1151 | 121.2479 | 3.5339 | 121.1746 | -0.16937 | -121.431
2734.7812 | 121.3898 | -121.0831 | 0.059509 | 0.017319 | -0.0061866 | 0.0084039 | 0.066294 | -0.026716 | 0.034947 | 0.1161 | 0.064087 | 0.07782 | -0.10529 | 0.15564 | -119.1696 | 0.15564 | -0.10529 | 0.22888 | 0.14191 | -121.4127 | 120.9778 | 0.018311 | 121.1472 | 121.2387 | -119.2291 | -0.32959 | 0.082398 | 0.16937 | 120.9778 | 121.312 | 1.9135 | 121.1609 | 121.1472 | 121.225 | 121.2387 | -0.32959 | 121.1609 | 121.1472 | 121.2387 | 1.9135 | 121.225 | -0.16479 | -121.4722
2736.5156 | 121.344 | -121.106 | 0.068665 | 0.0096895 | -0.0064002 | 0.0064813 | 0.067148 | -0.028425 | 0.034306 | 0.11418 | 0.09613 | 0.045776 | -0.09613 | 0.20599 | -118.5654 | 0.20142 | -0.12817 | 0.3067 | 0.10529 | -121.4355 | 121.0098 | -0.022889 | 121.2021 | 121.312 | -118.634 | -0.32959 | 0.036621 | 0.19226 | 120.9778 | 121.4127 | 2.5406 | 121.1517 | 121.2021 | 121.2112 | 121.3074 | -0.32959 | 121.1517 | 121.2021 | 121.3074 | 2.5406 | 121.2112 | -0.16479 | -121.5042
2738.25 | 121.3623 | -121.1334 | 0.073242 | 0.0096895 | -0.0051184 | 0.011608 | 0.069498 | -0.025007 | 0.033451 | 0.11268 | 0.13275 | 0.059509 | -0.09613 | 0.21973 | -117.421 | 0.20599 | -0.19684 | 0.27924 | 0.10986 | -121.4355 | 121.0373 | -0.013733 | 121.2662 | 121.3531 | -117.4942 | -0.30212 | 0.036621 | 0.22888 | 120.9366 | 121.4127 | 3.7125 | 121.1929 | 121.2662 | 121.2433 | 121.3394 | -0.30212 | 121.1929 | 121.2662 | 121.3394 | 3.7125 | 121.2433 | -0.16937 | -121.5088
2740 | 121.2799 | -121.1792 | 0.09613 | 0.0096895 | -0.0046912 | 0.0084039 | 0.072489 | -0.026289 | 0.031956 | 0.11525 | 0.07782 | 0.091553 | -0.13733 | 0.16937 | -117.7505 | 0.11902 | -0.054932 | 0.21057 | 0.16022 | -121.5042 | 121.0419 | -0.004577 | 121.257 | 121.3486 | -117.8467 | -0.32501 | 0.064087 | 0.21515 | 121.1243 | 121.3898 | 3.4286 | 121.2708 | 121.257 | 121.3394 | 121.2982 | -0.32501 | 121.2708 | 121.257 | 121.2982 | 3.4286 | 121.3394 | -0.23346 | -121.6003
2741.6875 | 121.3211 | -121.1746 | 0.09613 | 0.00206 | -0.0068274 | 0.0073359 | 0.075052 | -0.027357 | 0.030674 | 0.13768 | 0.10986 | 0.059509 | -0.10529 | 0.23804 | -117.5537 | 0.20142 | -0.14648 | 0.32501 | 0.10986 | -121.4767 | 121.0693 | -0.036621 | 121.2845 | 121.4127 | -117.6498 | -0.30212 | 0.013733 | 0.21515 | 121.0281 | 121.4996 | 3.6209 | 121.2341 | 121.2845 | 121.2845 | 121.376 | -0.30212 | 121.2341 | 121.2845 | 121.376 | 3.6209 | 121.2845 | -0.20142 | -121.5729
2743.3906 | 121.3165 | -121.2021 | 0.09613 | 0.00206 | -0.0074682 | 0.0058405 | 0.067789 | -0.02522 | 0.033024 | 0.12913 | 0.09613 | 0.064087 | -0.11902 | 0.21515 | -117.5446 | 0.18768 | -0.1236 | 0.30212 | 0.1236 | -121.4813 | 121.0831 | -0.032043 | 121.2982 | 121.4172 | -117.6407 | -0.27924 | 0.027466 | 0.21515 | 121.0785 | 121.5042 | 3.6575 | 121.2662 | 121.2982 | 121.3257 | 121.3898 | -0.27924 | 121.2662 | 121.2982 | 121.3898 | 3.6575 | 121.3257 | -0.21515 | -121.5775
2745.0938 | 121.3898 | -121.2021 | 0.10071 | 0.017319 | -0.007041 | 0.0092585 | 0.067789 | -0.026502 | 0.03217 | 0.11503 | 0.022888 | 0.082397 | -0.15564 | 0.10986 | -117.4759 | 0.07782 | 0.041199 | 0.1831 | 0.17853 | -121.5179 | 121.0464 | -0.018311 | 121.225 | 121.312 | -117.5766 | -0.31586 | 0.07782 | 0.17853 | 121.2433 | 121.3852 | 3.7262 | 121.2845 | 121.225 | 121.3806 | 121.2799 | -0.31586 | 121.2845 | 121.225 | 121.2799 | 3.7262 | 121.3806 | -0.25635 | -121.6187
2746.8125 | 121.4172 | -121.2387 | 0.068665 | 0.017319 | -0.0055456 | 0.0049859 | 0.075266 | -0.025434 | 0.031742 | 0.12443 | -0.004578 | 0.091553 | -0.15564 | 0.086975 | -117.4255 | 0.059509 | 0.041199 | 0.16479 | 0.16022 | -121.5454 | 121.0831 | 0.022888 | 121.2341 | 121.3257 | -117.4942 | -0.3067 | 0.091552 | 0.15106 | 121.2799 | 121.4035 | 3.8132 | 121.3303 | 121.2341 | 121.3989 | 121.2982 | -0.3067 | 121.3303 | 121.2341 | 121.2982 | 3.8132 | 121.3989 | -0.22431 | -121.6141
2748.5156 | 121.4127 | -121.257 | 0.073242 | 0.024948 | -0.0078954 | 0.0075495 | 0.061807 | -0.026075 | 0.03217 | 0.11396 | 0.11444 | 0.059509 | -0.10529 | 0.21515 | -116.0751 | 0.22888 | -0.16022 | 0.31128 | 0.1236 | -121.5317 | 121.1517 | -0.013733 | 121.3715 | 121.4722 | -116.1484 | -0.27466 | 0.050354 | 0.21973 | 121.0968 | 121.5683 | 5.1819 | 121.3165 | 121.3715 | 121.3806 | 121.4859 | -0.27466 | 121.3165 | 121.3715 | 121.4859 | 5.1819 | 121.3806 | -0.17853 | -121.6049
2750.2344 | 121.4218 | -121.2296 | 0.073242 | 0.0096895 | -0.0081092 | 0.0069085 | 0.068857 | -0.027143 | 0.033238 | 0.11866 | 0 | 0.086975 | -0.14191 | 0.10529 | -119.5267 | 0.086975 | 0.027466 | 0.19684 | 0.16479 | -121.5775 | 121.0876 | 0.013733 | 121.2296 | 121.3348 | -119.5999 | -0.3479 | 0.091553 | 0.14191 | 121.257 | 121.4264 | 1.7029 | 121.3165 | 121.2296 | 121.3943 | 121.3165 | -0.3479 | 121.3165 | 121.2296 | 121.3165 | 1.7029 | 121.3943 | -0.21515 | -121.6507
2751.9844 | 121.4859 | -121.2341 | 0.059509 | 0.0096895 | -0.0031958 | 0.0069085 | 0.072916 | -0.02522 | 0.033024 | 0.11589 | 0.013733 | 0.10529 | -0.13275 | 0.082397 | -119.5587 | 0.064087 | 0.004578 | 0.13275 | 0.17853 | -121.5958 | 121.1014 | 0.045777 | 121.2479 | 121.3165 | -119.6182 | -0.36163 | 0.11902 | 0.14648 | 121.2387 | 121.3669 | 1.6754 | 121.3394 | 121.2479 | 121.4127 | 121.2982 | -0.36163 | 121.3394 | 121.2479 | 121.2982 | 1.6754 | 121.4127 | -0.19226 | -121.6553
2753.6875 | 121.4539 | -121.2708 | 0.09613 | 0.0096895 | -0.0044776 | 0.0066949 | 0.064157 | -0.025007 | 0.034092 | 0.12101 | 0.086975 | 0.064087 | -0.1236 | 0.16022 | -119.3115 | 0.15564 | -0.041199 | 0.25177 | 0.14191 | -121.5775 | 121.1472 | -0.032043 | 121.3577 | 121.431 | -119.4077 | -0.3067 | 0.045777 | 0.21057 | 121.2296 | 121.5225 | 1.9592 | 121.3348 | 121.3577 | 121.4127 | 121.4264 | -0.3067 | 121.3348 | 121.3577 | 121.4264 | 1.9592 | 121.4127 | -0.21973 | -121.6736
2755.3906 | 121.4584 | -121.3028 | 0.086975 | 0.0096895 | -0.0044776 | 0.0051995 | 0.066294 | -0.024793 | 0.033665 | 0.11738 | 0.041199 | 0.086975 | -0.13733 | 0.11444 | -119.4077 | 0.086975 | 0.027466 | 0.20599 | 0.16022 | -121.6049 | 121.1655 | 0 | 121.344 | 121.4172 | -119.4946 | -0.30212 | 0.073242 | 0.17853 | 121.3303 | 121.5088 | 1.8951 | 121.3898 | 121.344 | 121.463 | 121.3898 | -0.30212 | 121.3898 | 121.344 | 121.3898 | 1.8951 | 121.463 | -0.2243 | -121.6919
2757.125 | 121.4584 | -121.3211 | 0.086975 | 0.0096895 | -0.0055456 | 0.0079767 | 0.063089 | -0.026075 | 0.031956 | 0.11695 | 0.11444 | 0.064087 | -0.11444 | 0.23346 | -119.252 | 0.21973 | -0.12817 | 0.31586 | 0.11444 | -121.5912 | 121.2067 | -0.022888 | 121.4355 | 121.5546 | -119.339 | -0.27008 | 0.027466 | 0.22888 | 121.1929 | 121.637 | 2.0691 | 121.3852 | 121.4355 | 121.4355 | 121.5408 | -0.27008 | 121.3852 | 121.4355 | 121.5408 | 2.0691 | 121.4355 | -0.20142 | -121.6782
2758.875 | 121.4401 | -121.3577 | 0.082397 | 0.0096895 | -0.00875 | 0.0086175 | 0.065866 | -0.025861 | 0.033451 | 0.11888 | 0.11444 | 0.032043 | -0.11444 | 0.21973 | -119.3481 | 0.20142 | -0.13275 | 0.32044 | 0.13275 | -121.6141 | 121.2433 | -0.050354 | 121.4722 | 121.5775 | -119.4305 | -0.25635 | 0.050354 | 0.22888 | 121.225 | 121.6782 | 2.0096 | 121.3898 | 121.4722 | 121.4905 | 121.5591 | -0.25635 | 121.3898 | 121.4722 | 121.5591 | 2.0096 | 121.4905 | -0.19684 | -121.6965
2760.5781 | 121.5271 | -121.3394 | 0.064087 | 0.0096895 | -0.0051184 | 0.0081903 | 0.07612 | -0.026716 | 0.030674 | 0.12229 | -0.004578 | 0.10529 | -0.15106 | 0.09613 | -119.4901 | 0.059509 | 0.059509 | 0.17395 | 0.16022 | -121.6507 | 121.1884 | 0.041199 | 121.3348 | 121.4355 | -119.5541 | -0.31128 | 0.09613 | 0.14648 | 121.3989 | 121.5134 | 1.8494 | 121.4447 | 121.3348 | 121.4996 | 121.3989 | -0.31128 | 121.4447 | 121.3348 | 121.3989 | 1.8494 | 121.4996 | -0.21515 | -121.7148
2762.2812 | 121.55 | -121.3394 | 0.068665 | 0.017319 | -0.0064002 | 0.0079767 | 0.069071 | -0.025648 | 0.03217 | 0.11589 | 0.009155 | 0.091553 | -0.15564 | 0.10529 | -119.5175 | 0.064087 | -0.004578 | 0.13275 | 0.16022 | -121.6415 | 121.1838 | 0.022888 | 121.3486 | 121.4447 | -119.5862 | -0.30212 | 0.091552 | 0.16479 | 121.3348 | 121.4722 | 1.8219 | 121.431 | 121.3486 | 121.4996 | 121.4035 | -0.30212 | 121.431 | 121.3486 | 121.4035 | 1.8219 | 121.4996 | -0.22431 | -121.7102
2764.0156 | 121.5729 | -121.3303 | 0.07782 | 0.0096895 | -0.0049048 | 0.0075495 | 0.069498 | -0.025007 | 0.034733 | 0.1208 | 0.11902 | 0.059509 | -0.10071 | 0.21057 | -119.1422 | 0.21057 | -0.21057 | 0.27008 | 0.09613 | -121.6782 | 121.2296 | -0.018311 | 121.4493 | 121.5408 | -119.22 | -0.3479 | 0.01831 | 0.21973 | 121.1197 | 121.6003 | 2.1881 | 121.3898 | 121.4493 | 121.4264 | 121.5408 | -0.3479 | 121.3898 | 121.4493 | 121.5408 | 2.1881 | 121.4264 | -0.17853 | -121.756
2765.75 | 121.6324 | -121.3486 | 0.045776 | 0.017319 | -0.0044776 | 0.0049859 | 0.066721 | -0.022871 | 0.034306 | 0.11546 | 0.009155 | 0.10071 | -0.15564 | 0.07782 | -119.1879 | 0.059509 | -0.013733 | 0.11902 | 0.16937 | -121.6919 | 121.1929 | 0.054932 | 121.3577 | 121.4264 | -119.2337 | -0.34332 | 0.1236 | 0.16479 | 121.3348 | 121.4676 | 2.1606 | 121.4493 | 121.3577 | 121.5179 | 121.4081 | -0.34332 | 121.4493 | 121.3577 | 121.4081 | 2.1606 | 121.5179 | -0.20142 | -121.7377
2767.4531 | 121.5317 | -121.3898 | 0.073242 | 0.024948 | -0.0046912 | 0.0069085 | 0.067789 | -0.025648 | 0.031529 | 0.11695 | 0.036621 | 0.086975 | -0.15106 | 0.10529 | -119.1696 | 0.082397 | -0.032043 | 0.15564 | 0.14191 | -121.7056 | 121.2387 | 0.013733 | 121.4264 | 121.4951 | -119.2429 | -0.31586 | 0.068665 | 0.18768 | 121.3577 | 121.5454 | 2.2202 | 121.4767 | 121.4264 | 121.5317 | 121.4722 | -0.31586 | 121.4767 | 121.4264 | 121.4722 | 2.2202 | 121.5317 | -0.2243 | -121.7789
2769.1562 | 121.5546 | -121.3943 | 0.086975 | 0.017319 | -0.002555 | 0.0094721 | 0.073984 | -0.028211 | 0.031956 | 0.13469 | -0.004578 | 0.10986 | -0.16022 | 0.086975 | -118.8492 | 0.068665 | 0.041199 | 0.16479 | 0.16937 | -121.7056 | 121.2341 | 0.022888 | 121.3898 | 121.4813 | -118.9362 | -0.31128 | 0.082398 | 0.15564 | 121.4355 | 121.5591 | 2.5452 | 121.5042 | 121.3898 | 121.5637 | 121.463 | -0.31128 | 121.5042 | 121.3898 | 121.463 | 2.5452 | 121.5637 | -0.24719 | -121.7926
2770.9219 | 121.6232 | -121.3806 | 0.059509 | 0.017319 | -0.0049048 | 0.0092585 | 0.06608 | -0.02757 | 0.03516 | 0.11674 | 0.10529 | 0.045776 | -0.10071 | 0.19226 | -118.7485 | 0.18768 | -0.19226 | 0.26093 | 0.13275 | -121.669 | 121.2799 | -0.013733 | 121.4859 | 121.5729 | -118.808 | -0.28839 | 0.073242 | 0.20599 | 121.1884 | 121.6415 | 2.6321 | 121.4264 | 121.4859 | 121.5134 | 121.5683 | -0.28839 | 121.4264 | 121.4859 | 121.5683 | 2.6321 | 121.5134 | -0.16022 | -121.7285
2772.6562 | 121.6278 | -121.3989 | 0.082397 | 0.0096895 | -0.0091772 | 0.0094721 | 0.064157 | -0.027998 | 0.035801 | 0.12059 | 0.09613 | 0.036621 | -0.10986 | 0.19226 | -119.426 | 0.19684 | -0.17853 | 0.28839 | 0.12817 | -121.7194 | 121.2891 | -0.045776 | 121.4951 | 121.5912 | -119.5084 | -0.32043 | 0.045777 | 0.20599 | 121.2204 | 121.6873 | 1.973 | 121.4355 | 121.4951 | 121.5271 | 121.5958 | -0.32043 | 121.4355 | 121.4951 | 121.5958 | 1.973 | 121.5271 | -0.19226 | -121.8018
2774.3594 | 121.6782 | -121.4172 | 0.068665 | 0.017319 | -0.001914 | 0.0077631 | 0.064798 | -0.028211 | 0.033238 | 0.12251 | 0.045776 | 0.07782 | -0.11902 | 0.14648 | -118.689 | 0.14648 | -0.10529 | 0.24261 | 0.12817 | -121.7377 | 121.2982 | 0.009155 | 121.463 | 121.5637 | -118.7576 | -0.32044 | 0.059509 | 0.16479 | 121.3119 | 121.6599 | 2.7283 | 121.4951 | 121.463 | 121.5454 | 121.5637 | -0.32044 | 121.4951 | 121.463 | 121.5637 | 2.7283 | 121.5454 | -0.18768 | -121.8063
2776.0781 | 121.6553 | -121.4264 | 0.073242 | 0.017319 | -0.0040502 | 0.0086175 | 0.066934 | -0.025434 | 0.031742 | 0.11781 | 0.10529 | 0.050354 | -0.10071 | 0.20142 | -118.4738 | 0.21057 | -0.20599 | 0.27466 | 0.11444 | -121.7422 | 121.3257 | -0.022888 | 121.5317 | 121.6278 | -118.5471 | -0.31586 | 0.041199 | 0.20599 | 121.2204 | 121.7011 | 2.9526 | 121.4767 | 121.5317 | 121.5408 | 121.637 | -0.31586 | 121.4767 | 121.5317 | 121.637 | 2.9526 | 121.5408 | -0.17395 | -121.8155
2777.7812 | 121.5683 | -121.4264 | 0.09613 | 0.0096895 | -0.0046912 | 0.0071221 | 0.079538 | -0.024152 | 0.03217 | 0.13191 | 0.041199 | 0.091553 | -0.15564 | 0.14191 | -118.2083 | 0.10986 | -0.018311 | 0.20142 | 0.15564 | -121.7468 | 121.2708 | -0.004577 | 121.4676 | 121.5683 | -118.3044 | -0.32043 | 0.05951 | 0.19684 | 121.4081 | 121.6278 | 3.2181 | 121.5179 | 121.4676 | 121.582 | 121.5363 | -0.32043 | 121.5179 | 121.4676 | 121.5363 | 3.2181 | 121.582 | -0.25177 | -121.843
2779.5 | 121.669 | -121.4081 | 0.064087 | 0.00206 | 0.00022218 | 0.0073359 | 0.068857 | -0.025861 | 0.034306 | 0.11952 | 0.064087 | 0.086975 | -0.11902 | 0.17395 | -118.4006 | 0.17853 | -0.16479 | 0.22888 | 0.11902 | -121.7468 | 121.2891 | 0.022888 | 121.4722 | 121.582 | -118.4647 | -0.33875 | 0.054932 | 0.18311 | 121.2433 | 121.637 | 3.0075 | 121.4951 | 121.4722 | 121.5271 | 121.5866 | -0.33875 | 121.4951 | 121.4722 | 121.5866 | 3.0075 | 121.5271 | -0.18311 | -121.8109
2781.2188 | 121.3211 | -121.0602 | 0.054932 | 0.00206 | -0.027335 | 0.0069085 | 0.062235 | -0.02522 | -0.028713 | 0.039409 | 0.082397 | 0.059509 | -0.10529 | 0.14191 | -0.94757 | 0.16022 | -0.13275 | 0.23346 | 0.1236 | -121.3669 | 120.9549 | 0.004577 | 121.1426 | 121.2021 | -1.0025 | -0.3067 | 0.068664 | 0.18768 | 120.9274 | 121.2936 | 120.1126 | 121.1197 | 121.1426 | 121.1838 | 121.2204 | -0.3067 | 121.1197 | 121.1426 | 121.2204 | 120.1126 | 121.1838 | -0.16022 | -121.4218
2782.9844 | 121.4172 | -121.2112 | 0.068665 | 0.0096895 | -0.024558 | 0.0062677 | 0.063303 | -0.023725 | -0.031917 | 0.034923 | 0 | 0.09613 | -0.16479 | 0.086975 | -0.18768 | 0.07782 | 0.045776 | 0.16937 | 0.1831 | -121.582 | 121.0464 | 0.027465 | 121.2112 | 121.2982 | -0.25635 | -0.37079 | 0.11444 | 0.16479 | 121.257 | 121.3806 | 121.0236 | 121.3074 | 121.2112 | 121.3943 | 121.2891 | -0.37079 | 121.3074 | 121.2112 | 121.2891 | 121.0236 | 121.3943 | -0.23346 | -121.6507
2784.6875 | 121.4035 | -121.3165 | 0.07782 | 0.0096895 | -0.024344 | 0.0066949 | 0.064798 | -0.023939 | -0.032558 | 0.034709 | 0.036621 | 0.09613 | -0.13733 | 0.14191 | -0.12817 | 0.11902 | -0.027466 | 0.21973 | 0.17395 | -121.6141 | 121.1792 | 0.01831 | 121.3531 | 121.4584 | -0.20599 | -0.29755 | 0.09613 | 0.17395 | 121.2891 | 121.5363 | 121.1884 | 121.4127 | 121.3531 | 121.4905 | 121.4355 | -0.29755 | 121.4127 | 121.3531 | 121.4355 | 121.1884 | 121.4905 | -0.21515 | -121.6919
2786.3906 | 121.5866 | -121.2982 | 0.041199 | 0.00206 | -0.019004 | 0.0066949 | 0.058817 | -0.026075 | -0.031704 | 0.039409 | 0.073242 | 0.068665 | -0.091553 | 0.15106 | -0.068665 | 0.16022 | -0.11444 | 0.22888 | 0.13733 | -121.6141 | 121.2067 | 0.027466 | 121.3715 | 121.4493 | -0.10986 | -0.31586 | 0.09613 | 0.16479 | 121.1838 | 121.5271 | 121.2296 | 121.3669 | 121.3715 | 121.4355 | 121.4584 | -0.31586 | 121.3669 | 121.3715 | 121.4584 | 121.2296 | 121.4355 | -0.13275 | -121.6553
2788.1094 | 121.2982 | -121.0373 | 0.059509 | 0.00206 | -0.02114 | 0.0071221 | 0.058389 | -0.026289 | -0.030208 | 0.029369 | 0.064087 | 0.064087 | -0.10986 | 0.14648 | 0.050354 | 0.16479 | -0.10986 | 0.2655 | 0.12817 | -121.3577 | 120.9274 | 0.004578 | 121.1014 | 121.1838 | -0.009155 | -0.32044 | 0.068665 | 0.17395 | 120.9274 | 121.3028 | 121.0876 | 121.1014 | 121.1014 | 121.1655 | 121.2021 | -0.32044 | 121.1014 | 121.1014 | 121.2021 | 121.0876 | 121.1655 | -0.16937 | -121.4172
2789.8125 | 121.4127 | -121.17 | 0.054932 | 0.00206 | -0.022635 | 0.0060541 | 0.066294 | -0.026075 | -0.030636 | 0.032573 | 0.059509 | 0.073242 | -0.11902 | 0.16937 | 0.050354 | 0.15564 | -0.15106 | 0.23804 | 0.1236 | -121.4859 | 121.051 | 0.01831 | 121.2296 | 121.3394 | -0.004578 | -0.31586 | 0.068664 | 0.17853 | 121.019 | 121.4081 | 121.2204 | 121.2433 | 121.2296 | 121.2936 | 121.3257 | -0.31586 | 121.2433 | 121.2296 | 121.3257 | 121.2204 | 121.2936 | -0.17395 | -121.5408
2791.5156 | 121.4035 | -121.2662 | 0.07782 | 0.0096895 | -0.021567 | 0.0047723 | 0.06373 | -0.026716 | -0.029354 | 0.030651 | 0.059509 | 0.07782 | -0.1236 | 0.13733 | 0.018311 | 0.11902 | -0.004578 | 0.21057 | 0.14648 | -121.5729 | 121.1426 | 0 | 121.3257 | 121.4035 | -0.059509 | -0.3067 | 0.068664 | 0.1831 | 121.2616 | 121.4767 | 121.2845 | 121.344 | 121.3257 | 121.4127 | 121.3852 | -0.3067 | 121.344 | 121.3257 | 121.3852 | 121.2845 | 121.4127 | -0.20142 | -121.6507
2793.2188 | 121.4172 | -121.2845 | 0.10529 | 0.00206 | -0.019431 | 0.0075495 | 0.062448 | -0.026929 | -0.030422 | 0.029796 | 0.10071 | 0.050354 | -0.10986 | 0.20142 | 0.086975 | 0.1831 | -0.091553 | 0.30212 | 0.12817 | -121.55 | 121.1746 | -0.054932 | 121.3852 | 121.4859 | -0.018311 | -0.2655 | 0.022888 | 0.21057 | 121.1929 | 121.5866 | 121.3715 | 121.3348 | 121.3852 | 121.4127 | 121.4676 | -0.2655 | 121.3348 | 121.3852 | 121.4676 | 121.3715 | 121.4127 | -0.21515 | -121.6553
2794.9844 | 121.55 | -121.2891 | 0.041199 | 0.017319 | -0.018149 | 0.0041315 | 0.067575 | -0.023511 | -0.033413 | 0.030437 | 0.018311 | 0.086975 | -0.15564 | 0.11444 | -0.013733 | 0.086975 | -0.082397 | 0.17853 | 0.17853 | -121.6095 | 121.1334 | 0.045776 | 121.3074 | 121.4035 | -0.054932 | -0.32044 | 0.13733 | 0.17395 | 121.2067 | 121.4676 | 121.2753 | 121.376 | 121.3074 | 121.4676 | 121.376 | -0.32044 | 121.376 | 121.3074 | 121.376 | 121.2753 | 121.4676 | -0.19684 | -121.6507
2796.7188 | 121.5637 | -121.3074 | 0.045776 | 0.00206 | -0.016654 | 0.0071221 | 0.065866 | -0.024366 | -0.032558 | 0.031932 | 0.009155 | 0.09613 | -0.14648 | 0.10986 | -0.009155 | 0.09613 | -0.09613 | 0.16937 | 0.12817 | -121.6599 | 121.1609 | 0.050354 | 121.3165 | 121.4172 | -0.054931 | -0.35248 | 0.082398 | 0.15564 | 121.2112 | 121.4767 | 121.2982 | 121.4035 | 121.3165 | 121.4355 | 121.4035 | -0.35248 | 121.4035 | 121.3165 | 121.4035 | 121.2982 | 121.4355 | -0.19226 | -121.7056
2798.4375 | 121.5271 | -121.344 | 0.068665 | 0.00206 | -0.019004 | 0.0079767 | 0.067148 | -0.024152 | -0.032131 | 0.032787 | 0.018311 | 0.09613 | -0.16022 | 0.09613 | -0.041199 | 0.054932 | -0.004578 | 0.13733 | 0.16022 | -121.6873 | 121.1838 | 0.027465 | 121.3623 | 121.4401 | -0.10986 | -0.34332 | 0.091552 | 0.17853 | 121.3394 | 121.4813 | 121.3028 | 121.4401 | 121.3623 | 121.5042 | 121.3989 | -0.34332 | 121.4401 | 121.3623 | 121.3989 | 121.3028 | 121.5042 | -0.22888 | -121.756
2800.1406 | 121.5042 | -121.3531 | 0.073242 | 0.017319 | -0.020072 | 0.010326 | 0.06843 | -0.02458 | -0.031704 | 0.033214 | 0.045776 | 0.09613 | -0.14648 | 0.1236 | -0.004578 | 0.10529 | -0.036621 | 0.16937 | 0.15564 | -121.6782 | 121.2067 | 0.022888 | 121.3989 | 121.4767 | -0.07782 | -0.32501 | 0.082398 | 0.19226 | 121.3165 | 121.5225 | 121.3486 | 121.4493 | 121.3989 | 121.5088 | 121.4584 | -0.32501 | 121.4493 | 121.3989 | 121.4584 | 121.3486 | 121.5088 | -0.21973 | -121.7514
2801.9062 | 121.5729 | -121.3577 | 0.045776 | 0.00206 | -0.018363 | 0.0088311 | 0.065439 | -0.023298 | -0.03384 | 0.034496 | 0.009155 | 0.091553 | -0.15564 | 0.073242 | -0.036621 | 0.059509 | -0.004578 | 0.12817 | 0.15564 | -121.6919 | 121.2021 | 0.045777 | 121.3669 | 121.431 | -0.082397 | -0.33417 | 0.10986 | 0.16479 | 121.3531 | 121.4859 | 121.3211 | 121.4493 | 121.3669 | 121.5134 | 121.4172 | -0.33417 | 121.4493 | 121.3669 | 121.4172 | 121.3211 | 121.5134 | -0.20142 | -121.7377
2803.6094 | 121.5408 | -121.4172 | 0.073242 | 0.017319 | -0.017295 | 0.0077631 | 0.067148 | -0.02458 | -0.033626 | 0.033641 | 0.068665 | 0.082397 | -0.14191 | 0.13733 | 0.027466 | 0.14191 | -0.041199 | 0.20599 | 0.14191 | -121.6919 | 121.2753 | 0.009155 | 121.4859 | 121.5546 | -0.045776 | -0.27466 | 0.068665 | 0.21057 | 121.376 | 121.6232 | 121.4447 | 121.4996 | 121.4859 | 121.5591 | 121.5591 | -0.27466 | 121.4996 | 121.4859 | 121.5591 | 121.4447 | 121.5591 | -0.21515 | -121.7651
2805.3125 | 121.6553 | -121.3806 | 0.050354 | 0.0096895 | -0.018149 | 0.0077631 | 0.062662 | -0.024793 | -0.032345 | 0.036632 | 0.086975 | 0.073242 | -0.091553 | 0.17395 | 0.059509 | 0.19226 | -0.15564 | 0.26093 | 0.11444 | -121.7102 | 121.2891 | 0.022888 | 121.4676 | 121.5546 | 0.009155 | -0.32959 | 0.064087 | 0.17853 | 121.225 | 121.6415 | 121.4401 | 121.4539 | 121.4676 | 121.4951 | 121.5729 | -0.32959 | 121.4539 | 121.4676 | 121.5729 | 121.4401 | 121.4951 | -0.14191 | -121.7606
2807.0156 | 120.7077 | -120.314 | 0.15564 | 0.0096895 | 0.23777 | 0.0039179 | 0.043436 | -0.023298 | -0.018032 | 0.60487 | 0.10986 | 0.15564 | -0.07782 | -0.009155 | -23.8953 | -0.045776 | -0.23346 | -37.2894 | 0.23804 | -120.5978 | 120.2362 | 0 | 120.4239 | 120.3049 | -24.0509 | -0.28381 | 0.082397 | 0.18768 | 120.0806 | 83.0246 | 96.4188 | 120.4697 | 120.4239 | 120.5521 | 120.2682 | -0.28381 | 120.4697 | 120.4239 | 120.2682 | 96.4188 | 120.5521 | -0.23346 | -120.7535
2808.7188 | 120.9457 | -120.6665 | 0.064087 | 0.00206 | 0.0085534 | 0.0079767 | 0.051126 | -0.024793 | 0.029606 | 0.094524 | 0.091553 | 0.045776 | -0.10986 | 0.15106 | -106.0822 | 0.16022 | -0.15106 | -39.0701 | 0.10986 | -121.019 | 120.5566 | -0.018311 | 120.7581 | 120.8176 | -106.1462 | -0.35248 | 0.045776 | 0.20142 | 120.5154 | 81.5964 | 14.5844 | 120.7123 | 120.7581 | 120.7764 | 120.8267 | -0.35248 | 120.7123 | 120.7581 | 120.8267 | 14.5844 | 120.7764 | -0.17395 | -121.0831
2810.4219 | 121.0602 | -120.7947 | 0.045776 | 0.00206 | 0.013894 | 0.0049859 | 0.057321 | -0.025007 | 0.027043 | 0.090038 | 0.022888 | 0.086975 | -0.15106 | 0.10529 | -103.5141 | 0.086975 | -0.068665 | -38.6032 | 0.12817 | -121.1288 | 120.6436 | 0.041199 | 120.8176 | 120.9 | -103.5599 | -0.33417 | 0.082398 | 0.17395 | 120.726 | 82.1915 | 17.2806 | 120.8817 | 120.8176 | 120.9229 | 120.8817 | -0.33417 | 120.8817 | 120.8176 | 120.8817 | 17.2806 | 120.9229 | -0.19684 | -121.1746
2812.1406 | 121.138 | -120.8588 | 0.050354 | 0.00206 | 0.009408 | 0.0081903 | 0.054972 | -0.023939 | -0.00030125 | 0.059917 | 0 | 0.09613 | -0.15106 | 0.082397 | -57.0007 | 0.054932 | -0.013733 | -37.5412 | 0.14648 | -121.2021 | 120.7077 | 0.045776 | 120.8588 | 120.9412 | -57.0511 | -0.34332 | 0.09613 | 0.15106 | 120.845 | 83.3176 | 63.858 | 120.9549 | 120.8588 | 121.0052 | 120.9137 | -0.34332 | 120.9549 | 120.8588 | 120.9137 | 63.858 | 121.0052 | -0.20142 | -121.2524
2813.9062 | 121.1929 | -120.9045 | 0.050354 | 0.017319 | 0.010476 | 0.0098993 | 0.05903 | -0.023511 | 0.010807 | 0.07722 | 0.009155 | 0.10986 | -0.13733 | 0.086975 | -78.3829 | 0.064087 | -0.032043 | -6.72 | 0.15564 | -121.2479 | 120.7672 | 0.059509 | 120.9137 | 120.9915 | -78.4332 | -0.34332 | 0.10529 | 0.14648 | 120.8725 | 114.1846 | 42.5217 | 121.0144 | 120.9137 | 121.0602 | 120.9686 | -0.34332 | 121.0144 | 120.9137 | 120.9686 | 42.5217 | 121.0602 | -0.18768 | -121.2982
2815.625 | 121.1884 | -120.9503 | 0.045776 | 0.017319 | 0.0091944 | 0.010967 | 0.058603 | -0.025434 | 0.013157 | 0.080211 | 0.045776 | 0.086975 | -0.13275 | 0.15106 | -81.7017 | 0.15564 | -0.13733 | 0.17853 | 0.1236 | -121.2936 | 120.8176 | 0.041199 | 120.9961 | 121.1014 | -81.7474 | -0.34332 | 0.07782 | 0.17853 | 120.813 | 121.1288 | 39.2487 | 121.0373 | 120.9961 | 121.0739 | 121.106 | -0.34332 | 121.0373 | 120.9961 | 121.106 | 39.2487 | 121.0739 | -0.17853 | -121.3394
2817.3438 | 121.1517 | -121.0052 | 0.073242 | 0.0096895 | 0.0089808 | 0.010326 | 0.060953 | -0.02522 | 0.013798 | 0.076366 | 0 | 0.09613 | -0.14648 | 0.10529 | -81.5002 | 0.073242 | 0.041199 | 0.15106 | 0.15106 | -121.3394 | 120.8588 | 0.022888 | 121.0052 | 121.1105 | -81.5735 | -0.33417 | 0.07782 | 0.14648 | 121.0464 | 121.1563 | 39.505 | 121.1014 | 121.0052 | 121.1563 | 121.0785 | -0.33417 | 121.1014 | 121.0052 | 121.0785 | 39.505 | 121.1563 | -0.21973 | -121.4127
2819.0781 | 121.2524 | -121.019 | 0.050354 | 0.0096895 | 0.0098352 | 0.011395 | 0.061807 | -0.02458 | 0.015293 | 0.082988 | 0.036621 | 0.07782 | -0.11444 | 0.14648 | -85.2081 | 0.14191 | -0.14191 | 0.19684 | 0.12817 | -121.344 | 120.9045 | 0.027466 | 121.0556 | 121.1655 | -85.2585 | -0.32501 | 0.07782 | 0.15106 | 120.8771 | 121.2158 | 35.8109 | 121.0968 | 121.0556 | 121.1472 | 121.1609 | -0.32501 | 121.0968 | 121.0556 | 121.1609 | 35.8109 | 121.1472 | -0.16479 | -121.3943
2820.7812 | 121.2982 | -121.0098 | 0.032043 | 0.017319 | 0.011117 | 0.0069085 | 0.063516 | -0.026929 | 0.02747 | 0.099224 | 0 | 0.10071 | -0.13733 | 0.086975 | -105.5099 | 0.086975 | -0.073242 | 0.10986 | 0.13275 | -121.3806 | 120.8725 | 0.068665 | 121.0098 | 121.0968 | -105.542 | -0.37079 | 0.10071 | 0.13733 | 120.9366 | 121.1197 | 15.4999 | 121.1105 | 121.0098 | 121.1426 | 121.0968 | -0.37079 | 121.1105 | 121.0098 | 121.0968 | 15.4999 | 121.1426 | -0.16937 | -121.4127
2822.4844 | 121.3303 | -121.0327 | 0.054932 | 0.00206 | 0.008767 | 0.0056269 | 0.048136 | -0.028852 | -0.025722 | 0.036418 | 0.041199 | 0.068665 | -0.10071 | 0.14191 | -2.7283 | 0.14648 | -0.10529 | 0.21515 | 0.13275 | -121.3806 | 120.932 | 0.013733 | 121.0739 | 121.1746 | -2.7832 | -0.3479 | 0.077819 | 0.14191 | 120.9274 | 121.2479 | 118.3044 | 121.1014 | 121.0739 | 121.1655 | 121.1792 | -0.3479 | 121.1014 | 121.0739 | 121.1792 | 118.3044 | 121.1655 | -0.15564 | -121.4355
2824.1875 | 121.3165 | -121.0968 | 0.054932 | 0.017319 | 0.0089808 | 0.0086175 | 0.054331 | -0.026289 | -0.030422 | 0.034282 | 0.1236 | 0.045776 | -0.09613 | 0.19684 | -0.19684 | 0.20599 | -0.19226 | 0.27008 | 0.10529 | -121.4035 | 121.0007 | -0.009156 | 121.2204 | 121.2936 | -0.25177 | -0.3067 | 0.050354 | 0.21973 | 120.9045 | 121.3669 | 120.9 | 121.1426 | 121.2204 | 121.2021 | 121.3028 | -0.3067 | 121.1426 | 121.2204 | 121.3028 | 120.9 | 121.2021 | -0.15106 | -121.4584
2825.9375 | 121.376 | -121.1014 | 0.054932 | 0.0096895 | 0.0098352 | 0.0060541 | 0.05369 | -0.027357 | -0.032772 | 0.035564 | 0.082397 | 0.059509 | -0.11444 | 0.14648 | -0.65918 | 0.16022 | -0.11902 | 0.22888 | 0.12817 | -121.463 | 120.9869 | 0.004577 | 121.1838 | 121.2479 | -0.71411 | -0.36163 | 0.073242 | 0.19684 | 120.9824 | 121.3303 | 120.4422 | 121.1609 | 121.1838 | 121.2296 | 121.2616 | -0.36163 | 121.1609 | 121.1838 | 121.2616 | 120.4422 | 121.2296 | -0.16937 | -121.5179
2827.6406 | 121.3852 | -121.1243 | 0.050354 | 0.0096895 | 0.011117 | 0.0032769 | 0.058603 | -0.026289 | -0.032772 | 0.037273 | 0.036621 | 0.086975 | -0.1236 | 0.13733 | -2.7603 | 0.11902 | -0.11444 | 0.18768 | 0.14191 | -121.4767 | 121.0007 | 0.036621 | 121.1609 | 121.2616 | -2.8107 | -0.35248 | 0.091553 | 0.16022 | 121.0098 | 121.312 | 118.364 | 121.2112 | 121.1609 | 121.2662 | 121.2433 | -0.35248 | 121.2112 | 121.1609 | 121.2433 | 118.364 | 121.2662 | -0.17395 | -121.5271
2829.3594 | 121.2845 | -121.2112 | 0.10529 | -0.013199 | 0.008767 | 0.0071221 | 0.055612 | -0.026929 | -0.031917 | 0.031505 | 0.10529 | 0.059509 | -0.086975 | 0.19684 | -0.51727 | 0.18768 | -0.12817 | 0.29755 | 0.12817 | -121.4951 | 121.1243 | -0.045777 | 121.3165 | 121.4081 | -0.62256 | -0.28381 | 0.022888 | 0.19226 | 121.0831 | 121.5088 | 120.694 | 121.2708 | 121.3165 | 121.3394 | 121.3989 | -0.28381 | 121.2708 | 121.3165 | 121.3989 | 120.694 | 121.3394 | -0.19226 | -121.6003
2831.0625 | 121.4447 | -121.1792 | 0.054932 | 0.00206 | 0.0066308 | 0.0079767 | 0.056253 | -0.026075 | -0.031277 | 0.031505 | 0.054932 | 0.073242 | -0.10529 | 0.15564 | -1.0986 | 0.13275 | -0.10529 | 0.23804 | 0.11902 | -121.4996 | 121.0739 | 0.01831 | 121.2341 | 121.3348 | -1.1536 | -0.32044 | 0.064087 | 0.16022 | 121.0739 | 121.4172 | 120.0806 | 121.2524 | 121.2341 | 121.2982 | 121.3119 | -0.32044 | 121.2524 | 121.2341 | 121.3119 | 120.0806 | 121.2982 | -0.16022 | -121.5546
2832.8125 | 121.463 | -121.1975 | 0.045776 | 0.00206 | 0.0066308 | 0.0066949 | 0.056894 | -0.026929 | -0.02914 | 0.031719 | 0.10529 | 0.068665 | -0.10529 | 0.16937 | -1.9821 | 0.16022 | -0.14191 | 0.24261 | 0.11902 | -121.5179 | 121.0922 | 0.022889 | 121.3028 | 121.3669 | -2.0279 | -0.32043 | 0.073243 | 0.21057 | 121.0556 | 121.4401 | 119.2154 | 121.2662 | 121.3028 | 121.3165 | 121.3577 | -0.32043 | 121.2662 | 121.3028 | 121.3577 | 119.2154 | 121.3165 | -0.15106 | -121.5637
2834.5156 | 121.4401 | -121.2021 | 0.073242 | 0.0096895 | 0.0064172 | 0.0069085 | 0.059244 | -0.026502 | -0.025936 | 0.034923 | 0.11444 | 0.036621 | -0.09613 | 0.21057 | -9.2926 | 0.19684 | -0.20599 | 0.27008 | 0.10986 | -121.5179 | 121.106 | -0.036621 | 121.3165 | 121.4127 | -9.3658 | -0.31586 | 0.036621 | 0.21057 | 120.9961 | 121.4722 | 111.9095 | 121.2387 | 121.3165 | 121.312 | 121.3989 | -0.31586 | 121.2387 | 121.3165 | 121.3989 | 111.9095 | 121.312 | -0.16937 | -121.5912
2836.2188 | 121.4996 | -121.225 | 0.054932 | -0.0055695 | 0.007699 | 0.0079767 | 0.057962 | -0.026502 | -0.02679 | 0.043254 | 0.091553 | 0.059509 | -0.09613 | 0.15106 | -2.8519 | 0.16479 | -0.13275 | 0.2243 | 0.14191 | -121.5408 | 121.1288 | 0.004577 | 121.3165 | 121.376 | -2.9068 | -0.31586 | 0.086975 | 0.18768 | 121.0922 | 121.4493 | 118.3731 | 121.2845 | 121.3165 | 121.3669 | 121.3898 | -0.31586 | 121.2845 | 121.3165 | 121.3898 | 118.3731 | 121.3669 | -0.15106 | -121.5958
2837.9844 | 121.4447 | -121.2662 | 0.059509 | 0.0096895 | 0.0066308 | 0.0092585 | 0.066507 | -0.02757 | -0.032131 | 0.065044 | 0.10529 | 0.045776 | -0.10529 | 0.21515 | -0.35248 | 0.20142 | -0.20142 | 0.27008 | 0.11902 | -121.5179 | 121.1609 | -0.013733 | 121.3715 | 121.4813 | -0.41199 | -0.25177 | 0.05951 | 0.21057 | 121.0648 | 121.5363 | 120.9137 | 121.312 | 121.3715 | 121.3852 | 121.4676 | -0.25177 | 121.312 | 121.3715 | 121.4676 | 120.9137 | 121.3852 | -0.16479 | -121.5775
2839.6875 | 120.5704 | -120.4559 | 0.082397 | 0.024948 | -0.012595 | 0.0077631 | 0.073343 | -0.022871 | -0.031917 | 0.028514 | 0.050354 | 0.082397 | -0.13733 | 0.13733 | 0.009155 | 0.10986 | -0.018311 | -3.1403 | 0.15564 | -120.7581 | 120.3186 | 0 | 120.5063 | 120.5933 | -0.073242 | -0.30212 | 0.073243 | 0.18768 | 120.4376 | 117.3157 | 120.4651 | 120.5383 | 120.5063 | 120.6116 | 120.5658 | -0.30212 | 120.5383 | 120.5063 | 120.5658 | 120.4651 | 120.6116 | -0.21973 | -120.8405
2841.4219 | 120.8221 | -120.6894 | 0.091553 | 0.017319 | -0.015159 | 0.0069085 | 0.069284 | -0.026289 | -0.03149 | 0.028514 | 0.050354 | 0.064087 | -0.11902 | 0.12817 | 0.022888 | 0.091553 | -0.004578 | -3.1174 | 0.15106 | -121.0052 | 120.5704 | -0.027466 | 120.7397 | 120.8176 | -0.068665 | -0.31586 | 0.059509 | 0.16937 | 120.6848 | 117.572 | 120.7123 | 120.7535 | 120.7397 | 120.8405 | 120.7809 | -0.31586 | 120.7535 | 120.7397 | 120.7809 | 120.7123 | 120.8405 | -0.21057 | -121.0968
2843.1406 | 121.0007 | -120.726 | 0.054932 | 0.00206 | -0.013236 | 0.0096857 | 0.074625 | -0.02522 | -0.031917 | 0.029369 | 0 | 0.10986 | -0.15564 | 0.068665 | -0.041199 | 0.041199 | 0.018311 | -3.3279 | 0.16022 | -121.1151 | 120.5704 | 0.054931 | 120.726 | 120.7947 | -0.096131 | -0.3891 | 0.10528 | 0.15564 | 120.7443 | 117.3981 | 120.6848 | 120.8359 | 120.726 | 120.8862 | 120.7672 | -0.3891 | 120.8359 | 120.726 | 120.7672 | 120.6848 | 120.8862 | -0.21057 | -121.17
2844.9062 | 121.0785 | -120.7993 | 0.045776 | 0.0096895 | -0.016013 | 0.0066949 | 0.067362 | -0.026502 | -0.029354 | 0.030651 | 0.054932 | 0.059509 | -0.11902 | 0.14648 | 0.059509 | 0.15564 | -0.12817 | -2.4536 | 0.11902 | -121.17 | 120.6802 | 0.013733 | 120.8542 | 120.9457 | 0.013733 | -0.37079 | 0.073243 | 0.17395 | 120.6711 | 118.3456 | 120.8588 | 120.8588 | 120.8542 | 120.9183 | 120.9549 | -0.37079 | 120.8588 | 120.8542 | 120.9549 | 120.8588 | 120.9183 | -0.16479 | -121.2158
2846.6094 | 121.0281 | -120.8771 | 0.068665 | 0.0096895 | -0.012382 | 0.0060541 | 0.078897 | -0.024366 | -0.032558 | 0.031932 | 0.032043 | 0.09613 | -0.13733 | 0.09613 | -0.027466 | 0.064087 | -0.004578 | -2.4353 | 0.14191 | -121.2112 | 120.7397 | 0.027465 | 120.9091 | 120.9732 | -0.096131 | -0.33417 | 0.073242 | 0.16937 | 120.8725 | 118.4418 | 120.8496 | 120.9732 | 120.9091 | 121.019 | 120.9412 | -0.33417 | 120.9732 | 120.9091 | 120.9412 | 120.8496 | 121.019 | -0.20599 | -121.2799
2848.3594 | 121.1655 | -120.8862 | 0.064087 | 0.00206 | -0.011527 | 0.0069085 | 0.077188 | -0.025648 | -0.032772 | 0.029155 | -0.004578 | 0.091553 | -0.12817 | 0.059509 | -0.027466 | 0.068665 | -0.009155 | -2.1149 | 0.16479 | -121.2433 | 120.7581 | 0.027466 | 120.8817 | 120.9457 | -0.091553 | -0.35706 | 0.10071 | 0.1236 | 120.8771 | 118.7714 | 120.8588 | 120.9778 | 120.8817 | 121.051 | 120.9549 | -0.35706 | 120.9778 | 120.8817 | 120.9549 | 120.8588 | 121.051 | -0.19226 | -121.3074
2850.0781 | 121.1151 | -120.9366 | 0.07782 | 0.0096895 | -0.01345 | 0.0092585 | 0.077616 | -0.023084 | -0.034054 | 0.031719 | 0.022888 | 0.082397 | -0.14191 | 0.10071 | -0.022888 | 0.054932 | -0.013733 | -3.1174 | 0.16022 | -121.257 | 120.7947 | 0.004577 | 120.9595 | 121.0373 | -0.10071 | -0.32044 | 0.082397 | 0.16479 | 120.9229 | 117.8192 | 120.9137 | 121.019 | 120.9595 | 121.0968 | 120.9915 | -0.32044 | 121.019 | 120.9595 | 120.9915 | 120.9137 | 121.0968 | -0.21973 | -121.3348
2851.7812 | 121.1655 | -120.9824 | 0.07782 | 0.017319 | -0.012382 | 0.0047723 | 0.07612 | -0.026502 | -0.032985 | 0.032787 | -0.004578 | 0.10071 | -0.15564 | 0.086975 | 0.004578 | 0.073242 | 0.064087 | -2.6505 | 0.17853 | -121.312 | 120.8267 | 0.022888 | 120.9778 | 121.0693 | -0.073242 | -0.32959 | 0.10071 | 0.15106 | 121.0464 | 118.3319 | 120.9869 | 121.0831 | 120.9778 | 121.1609 | 121.0556 | -0.32959 | 121.0831 | 120.9778 | 121.0556 | 120.9869 | 121.1609 | -0.23346 | -121.3898
2853.4844 | 121.0693 | -120.9686 | 0.045776 | 0.0096895 | -0.012382 | 0.0079767 | 0.082529 | -0.02458 | -0.034694 | 0.040904 | 0.013733 | 0.082397 | -0.13733 | 0.091553 | -0.036621 | 0.059509 | 0.018311 | -0.54474 | 0.16479 | -121.2982 | 120.8313 | 0.036621 | 120.9824 | 121.0602 | -0.082397 | -0.32959 | 0.11902 | 0.15106 | 120.9869 | 120.4239 | 120.932 | 121.051 | 120.9824 | 121.1334 | 121.0281 | -0.32959 | 121.051 | 120.9824 | 121.0281 | 120.932 | 121.1334 | -0.18311 | -121.344
2855.1875 | 121.1929 | -121.019 | 0.082397 | 0.017319 | -0.011954 | 0.0086175 | 0.081674 | -0.025007 | -0.032772 | 0.042186 | 0.013733 | 0.091553 | -0.13733 | 0.086975 | -0.013733 | 0.073242 | 0 | -0.80109 | 0.14648 | -121.3577 | 120.8817 | 0.009156 | 121.0327 | 121.106 | -0.09613 | -0.33875 | 0.064087 | 0.15106 | 121.019 | 120.2179 | 121.0052 | 121.1105 | 121.0327 | 121.1655 | 121.0922 | -0.33875 | 121.1105 | 121.0327 | 121.0922 | 121.0052 | 121.1655 | -0.21973 | -121.4401
2856.9219 | 121.312 | -121.0144 | 0.045776 | 0.00206 | -0.010673 | 0.0060541 | 0.082529 | -0.025007 | -0.031704 | 0.043895 | 0 | 0.10071 | -0.14191 | 0.054932 | -0.036621 | 0.068665 | 0.004578 | -0.9201 | 0.16022 | -121.3898 | 120.8725 | 0.054932 | 121.0144 | 121.0693 | -0.082397 | -0.37537 | 0.11444 | 0.14191 | 121.019 | 120.0943 | 120.9778 | 121.1151 | 121.0144 | 121.1746 | 121.0831 | -0.37537 | 121.1151 | 121.0144 | 121.0831 | 120.9778 | 121.1746 | -0.18768 | -121.4355
2858.625 | 120.3552 | -120.2225 | 0.059509 | 0.017319 | -0.0089636 | 0.0047723 | 0.060312 | -0.026929 | 0.033451 | 0.11503 | 0.11902 | 0.050354 | -0.091553 | 0.17853 | -118.2999 | -3.4103 | -0.19226 | 0.2655 | 0.11902 | -120.4788 | 120.1309 | -0.009155 | 120.3415 | 120.401 | -118.3594 | -0.25635 | 0.05951 | 0.21057 | 120.0302 | 120.488 | 1.9226 | 120.2728 | 120.3415 | 120.3415 | 116.8121 | -0.25635 | 120.2728 | 120.3415 | 116.8121 | 1.9226 | 120.3415 | -0.15106 | -120.5383
2860.3594 | 120.8176 | -120.7581 | 0.10986 | 0.0096895 | -0.0078954 | 0.0075495 | 0.059458 | -0.027784 | 0.035374 | 0.11824 | 0.14191 | 0.059509 | -0.09613 | 0.19684 | -119.8929 | -3.8544 | -0.14648 | 0.32044 | 0.11902 | -121.0144 | 120.6619 | -0.050354 | 120.9 | 120.9549 | -120.0027 | -0.25635 | 0.009156 | 0.23804 | 120.6116 | 121.0785 | 0.86517 | 120.8176 | 120.9 | 120.8771 | 116.9037 | -0.25635 | 120.8176 | 120.9 | 116.9037 | 0.86517 | 120.8771 | -0.20599 | -121.1243
2862.0625 | 121.0236 | -120.7581 | 0.068665 | -0.013199 | -0.0074682 | 0.0066949 | 0.060953 | -0.027357 | 0.036442 | 0.11845 | 0.073242 | 0.07782 | -0.10071 | 0.17853 | -120.3369 | -3.8864 | -0.13275 | 0.27466 | 0.12817 | -121.1288 | 120.6573 | 0.009155 | 120.8313 | 120.9366 | -120.4056 | -0.37079 | 0.059509 | 0.17395 | 120.6253 | 121.0327 | 0.42114 | 120.8359 | 120.8313 | 120.8862 | 116.8716 | -0.37079 | 120.8359 | 120.8313 | 116.8716 | 0.42114 | 120.8862 | -0.16937 | -121.1975
2863.7656 | 121.0922 | -120.8221 | 0.068665 | 0.00206 | -0.0085364 | 0.013531 | 0.067148 | -0.026502 | 0.035374 | 0.12165 | 0 | 0.10071 | -0.13275 | 0.086975 | -120.6207 | -3.9963 | -0.036621 | 0.13275 | 0.15106 | -121.17 | 120.6894 | 0.032043 | 120.8221 | 120.9091 | -120.6894 | -0.3479 | 0.082397 | 0.13275 | 120.7855 | 120.9549 | 0.20142 | 120.9229 | 120.8221 | 120.9732 | 116.8259 | -0.3479 | 120.9229 | 120.8221 | 116.8259 | 0.20142 | 120.9732 | -0.20142 | -121.2387
2865.5 | 121.0648 | -120.8862 | 0.086975 | 0.0096895 | -0.0085364 | 0.0056269 | 0.066294 | -0.027998 | 0.034306 | 0.12336 | 0.009155 | 0.091553 | -0.15106 | 0.10071 | -120.6665 | -3.6758 | 0.045776 | 0.17395 | 0.16022 | -121.225 | 120.7352 | 0.004578 | 120.8954 | 120.9869 | -120.7535 | -0.33875 | 0.073242 | 0.16022 | 120.932 | 121.0602 | 0.21973 | 120.9778 | 120.8954 | 121.0464 | 117.2104 | -0.33875 | 120.9778 | 120.8954 | 117.2104 | 0.21973 | 121.0464 | -0.23804 | -121.312
2867.2031 | 121.17 | -120.9137 | 0.059509 | 0.00206 | -0.011954 | 0.0039179 | 0.068857 | -0.024793 | 0.03516 | 0.12101 | 0.064087 | 0.068665 | -0.10529 | 0.1831 | -120.6299 | -1.5015 | -0.12817 | 0.2655 | 0.13733 | -121.2296 | 120.8084 | 0.009156 | 120.9778 | 121.0968 | -120.6894 | -0.31586 | 0.07782 | 0.16937 | 120.7855 | 121.1792 | 0.28381 | 120.9824 | 120.9778 | 121.051 | 119.4122 | -0.31586 | 120.9824 | 120.9778 | 119.4122 | 0.28381 | 121.051 | -0.16479 | -121.2891
2868.9062 | 121.2021 | -120.9183 | 0.054932 | 0.00206 | -0.0091772 | 0.0081903 | 0.079538 | -0.025007 | 0.033879 | 0.13639 | 0.068665 | 0.068665 | -0.09613 | 0.16022 | -120.7077 | 0.036621 | -0.1236 | 0.23346 | 0.11444 | -121.2708 | 120.8221 | 0.013733 | 120.9869 | 121.0785 | -120.7626 | -0.35248 | 0.059509 | 0.16479 | 120.7947 | 121.1517 | 0.21057 | 120.9869 | 120.9869 | 121.0327 | 120.9549 | -0.35248 | 120.9869 | 120.9869 | 120.9549 | 0.21057 | 121.0327 | -0.15106 | -121.3257
2870.625 | 121.1472 | -120.9915 | 0.082397 | 0.00206 | -0.010886 | 0.0075495 | 0.095133 | -0.028425 | 0.033665 | 0.14772 | 0.091553 | 0.054932 | -0.10986 | 0.16022 | -120.7214 | 0.082397 | -0.027466 | 0.23804 | 0.15564 | -121.3028 | 120.8817 | -0.027465 | 121.0831 | 121.1517 | -120.8038 | -0.31128 | 0.073243 | 0.20142 | 120.9641 | 121.2296 | 0.27008 | 121.0464 | 121.0831 | 121.1472 | 121.0739 | -0.31128 | 121.0464 | 121.0831 | 121.0739 | 0.27008 | 121.1472 | -0.19226 | -121.3852
2872.3438 | 119.1605 | -119.133 | 0.091553 | 0.0096895 | 0.01603 | 0.010113 | 0.24104 | -0.021162 | -0.03149 | 0.27055 | 0.082397 | 0.09613 | -0.15106 | 0.10529 | -5.7953 | 0.086975 | -0.068665 | 0.15564 | 0.15564 | -119.3024 | 118.9819 | 0.004577 | 119.2154 | 119.2383 | -5.8868 | -0.16937 | 0.064087 | 0.23346 | 119.0643 | 119.2886 | 113.3377 | 119.2291 | 119.2154 | 119.2886 | 119.22 | -0.16937 | 119.2291 | 119.2154 | 119.22 | 113.3377 | 119.2886 | -0.24261 | -119.3939
2874.0625 | 119.5404 | -119.5312 | 0.09613 | 0.0096895 | -0.063224 | 0.010326 | 0.033396 | -0.023511 | -0.03384 | 0.028087 | 0.07782 | 0.082397 | -0.10529 | 0.14191 | -0.027466 | 0.11444 | -0.050354 | 0.19684 | 0.16022 | -119.7464 | 119.426 | -0.013733 | 119.6091 | 119.6732 | -0.1236 | -0.21515 | 0.064087 | 0.18311 | 119.4809 | 119.7281 | 119.5038 | 119.6136 | 119.6091 | 119.6915 | 119.6457 | -0.21515 | 119.6136 | 119.6091 | 119.6457 | 119.5038 | 119.6915 | -0.20142 | -119.8425
2875.7656 | 120.4697 | -120.3918 | 0.10986 | 0.0096895 | -0.063651 | 0.0060541 | 0.02891 | -0.026289 | -0.031277 | 0.028087 | 0.073242 | 0.064087 | -0.10986 | 0.15106 | 0.004578 | 0.14648 | -0.027466 | 0.22888 | 0.14191 | -120.6711 | 120.282 | -0.045776 | 120.4651 | 120.5429 | -0.10529 | -0.27924 | 0.032044 | 0.18311 | 120.3644 | 120.6207 | 120.3964 | 120.4559 | 120.4651 | 120.5338 | 120.5383 | -0.27924 | 120.4559 | 120.4651 | 120.5383 | 120.3964 | 120.5338 | -0.21973 | -120.7809
2877.4844 | 120.639 | -120.4514 | 0.059509 | 0.0096895 | -0.064078 | 0.010754 | 0.064798 | -0.024152 | -0.031063 | 0.062908 | 0.1236 | 0.059509 | -0.086975 | 0.19226 | -0.23804 | 0.20599 | -0.20142 | 0.26093 | 0.10071 | -120.7352 | 120.3644 | 0 | 120.575 | 120.6436 | -0.29755 | -0.28381 | 0.041199 | 0.21057 | 120.2499 | 120.7123 | 120.2133 | 120.5109 | 120.575 | 120.5521 | 120.6573 | -0.28381 | 120.5109 | 120.575 | 120.6573 | 120.2133 | 120.5521 | -0.14648 | -120.7947
2879.2031 | 120.7947 | -120.52 | 0.064087 | 0.0096895 | -0.058951 | 0.0069085 | 0.037027 | -0.027143 | -0.029568 | 0.032146 | 0.045776 | 0.07782 | -0.10529 | 0.13275 | -1.5884 | 0.13275 | -0.10986 | 0.20599 | 0.1236 | -120.8725 | 120.4147 | 0.013733 | 120.5658 | 120.6528 | -1.6525 | -0.35248 | 0.059509 | 0.15106 | 120.4102 | 120.726 | 118.9316 | 120.5978 | 120.5658 | 120.6436 | 120.6528 | -0.35248 | 120.5978 | 120.5658 | 120.6528 | 118.9316 | 120.6436 | -0.16937 | -120.9366
2880.9062 | 120.813 | -120.5887 | 0.068665 | 0.00206 | -0.062369 | 0.0056269 | 0.038095 | -0.026929 | -0.029781 | 0.031505 | 0.10529 | 0.050354 | -0.09613 | 0.20599 | -0.89722 | 0.19226 | -0.1831 | 0.24719 | 0.1236 | -120.8908 | 120.4926 | -0.018311 | 120.694 | 120.7947 | -0.96588 | -0.30212 | 0.054931 | 0.20142 | 120.4056 | 120.8359 | 119.6915 | 120.639 | 120.694 | 120.7123 | 120.7809 | -0.30212 | 120.639 | 120.694 | 120.7809 | 119.6915 | 120.7123 | -0.16479 | -120.9595
2882.625 | 120.8359 | -120.5978 | 0.054932 | 0.0096895 | -0.06066 | 0.011395 | 0.044504 | -0.026075 | -0.034267 | 0.032146 | 0.032043 | 0.082397 | -0.1236 | 0.16022 | -1.2543 | 0.14191 | -0.13733 | 0.19684 | 0.13733 | -120.9457 | 120.4742 | 0.027465 | 120.6299 | 120.7581 | -1.3092 | -0.3479 | 0.082397 | 0.15564 | 120.4605 | 120.7947 | 119.3436 | 120.6802 | 120.6299 | 120.7352 | 120.7397 | -0.3479 | 120.6802 | 120.6299 | 120.7397 | 119.3436 | 120.7352 | -0.17853 | -121.0007
2884.3906 | 120.8221 | -120.7077 | 0.09613 | 0.00206 | -0.06002 | 0.0084039 | 0.035105 | -0.028638 | -0.032345 | 0.033641 | 0.10071 | 0.041199 | -0.09613 | 0.21057 | -0.1236 | 0.17853 | -0.10071 | 0.27924 | 0.11902 | -120.9778 | 120.6116 | -0.054931 | 120.8084 | 120.9183 | -0.21973 | -0.27008 | 0.022889 | 0.19684 | 120.607 | 120.9869 | 120.5841 | 120.7489 | 120.8084 | 120.8267 | 120.8862 | -0.27008 | 120.7489 | 120.8084 | 120.8862 | 120.5841 | 120.8267 | -0.19226 | -121.0739
2886.0938 | 120.9503 | -120.6894 | 0.068665 | 0.00206 | -0.058524 | 0.0096857 | 0.038523 | -0.02757 | -0.029568 | 0.036418 | 0.073242 | 0.064087 | -0.09613 | 0.17395 | -0.082397 | 0.16479 | -0.11902 | 0.24261 | 0.10529 | -121.0556 | 120.5933 | -0.004578 | 120.7626 | 120.8633 | -0.15106 | -0.36621 | 0.036621 | 0.16937 | 120.5704 | 120.932 | 120.607 | 120.7535 | 120.7626 | 120.7947 | 120.8542 | -0.36621 | 120.7535 | 120.7626 | 120.8542 | 120.607 | 120.7947 | -0.16479 | -121.1243
2887.8281 | 120.8679 | -120.7855 | 0.10529 | 0.00206 | -0.062369 | 0.0019953 | 0.041727 | -0.025007 | -0.032772 | 0.033641 | 0.1236 | 0.054932 | -0.086975 | 0.23346 | -0.091553 | 0.18768 | -0.13275 | 0.23804 | 0.11902 | -121.0464 | 120.6985 | -0.050354 | 120.9091 | 121.019 | -0.19684 | -0.26093 | 0.013733 | 0.21057 | 120.6528 | 121.0236 | 120.694 | 120.8405 | 120.9091 | 120.9045 | 120.9732 | -0.26093 | 120.8405 | 120.9091 | 120.9732 | 120.694 | 120.9045 | -0.19226 | -121.1517
2889.5469 | 120.9183 | -120.7855 | 0.082397 | 0.00206 | -0.064506 | 0.0060541 | 0.051126 | -0.02757 | -0.031063 | 0.034496 | 0.10529 | 0.050354 | -0.10986 | 0.21973 | -1.1536 | 0.16937 | -0.09613 | 0.16479 | 0.13733 | -121.1151 | 120.6757 | -0.032043 | 120.8908 | 121.0052 | -1.236 | -0.32959 | 0.054932 | 0.21515 | 120.6894 | 120.9503 | 119.632 | 120.8359 | 120.8908 | 120.9229 | 120.9549 | -0.32959 | 120.8359 | 120.8908 | 120.9549 | 119.632 | 120.9229 | -0.19226 | -121.1975
2891.25 | 120.9961 | -120.813 | 0.086975 | 0.0096895 | -0.064078 | 0.0062677 | 0.063944 | -0.027357 | -0.032985 | 0.038127 | 0.009155 | 0.086975 | -0.11902 | 0.10529 | -2.861 | 0.064087 | 0.036621 | 0.19684 | 0.15106 | -121.1472 | 120.694 | 0 | 120.8221 | 120.9183 | -2.948 | -0.33417 | 0.064087 | 0.12817 | 120.8496 | 121.0098 | 117.952 | 120.9 | 120.8221 | 120.9641 | 120.8771 | -0.33417 | 120.9 | 120.8221 | 120.8771 | 117.952 | 120.9641 | -0.20599 | -121.2341
2892.9531 | 121.0098 | -120.8542 | 0.068665 | 0.0096895 | -0.063651 | 0.0066949 | 0.061167 | -0.026502 | -0.03149 | 0.039195 | -0.013733 | 0.09613 | -0.15564 | 0.10529 | -3.2227 | 0.059509 | 0.041199 | 0.17853 | 0.16022 | -121.1563 | 120.6985 | 0.027465 | 120.8405 | 120.9595 | -3.2913 | -0.30212 | 0.091552 | 0.14191 | 120.8954 | 121.0327 | 117.6315 | 120.9503 | 120.8405 | 121.0144 | 120.9137 | -0.30212 | 120.9503 | 120.8405 | 120.9137 | 117.6315 | 121.0144 | -0.22431 | -121.225
2894.6719 | 121.0739 | -120.8588 | 0.07782 | 0.0096895 | -0.064078 | 0.0098993 | 0.067575 | -0.024793 | -0.031063 | 0.040264 | 0.13275 | 0.045776 | -0.086975 | 0.21057 | -3.1128 | 0.21515 | -0.19684 | 0.27924 | 0.11902 | -121.1655 | 120.7718 | -0.032044 | 120.9915 | 121.0693 | -3.1906 | -0.3067 | 0.041199 | 0.21973 | 120.6619 | 121.138 | 117.746 | 120.9045 | 120.9915 | 120.9778 | 121.0739 | -0.3067 | 120.9045 | 120.9915 | 121.0739 | 117.746 | 120.9778 | -0.16479 | -121.2433
2896.375 | 121.138 | -120.8862 | 0.045776 | 0.0096895 | -0.064078 | 0.0084039 | 0.067362 | -0.024152 | -0.032558 | 0.040904 | 0.004578 | 0.086975 | -0.14648 | 0.09613 | -1.1948 | 0.082397 | -0.041199 | 0.12817 | 0.14648 | -121.1929 | 120.7397 | 0.041199 | 120.8908 | 120.9824 | -1.2405 | -0.3067 | 0.10071 | 0.15106 | 120.845 | 121.0144 | 119.6915 | 120.9732 | 120.8908 | 121.0327 | 120.9686 | -0.3067 | 120.9732 | 120.8908 | 120.9686 | 119.6915 | 121.0327 | -0.19226 | -121.2387
2898.0781 | 121.1014 | -120.8862 | 0.041199 | 0.00206 | -0.062156 | 0.0026361 | 0.066934 | -0.02522 | 0.032597 | 0.11525 | 0.082397 | 0.082397 | -0.10986 | 0.19226 | -120.4376 | 0.12817 | -0.16937 | 0.24261 | 0.10986 | -121.1929 | 120.7764 | 0.041198 | 120.9686 | 121.0785 | -120.4788 | -0.3067 | 0.068664 | 0.19226 | 120.7169 | 121.1288 | 0.44861 | 120.9686 | 120.9686 | 120.9961 | 121.0144 | -0.3067 | 120.9686 | 120.9686 | 121.0144 | 0.44861 | 120.9961 | -0.15106 | -121.2341
2899.7812 | 120.6848 | -120.5704 | 0.07782 | 0.017319 | -0.014945 | 0.0081903 | 0.076761 | -0.027143 | 0.023197 | 0.11332 | 0.009155 | 0.09613 | -0.14191 | 0.091553 | -98.5107 | 0.018311 | 0.022888 | 0.18768 | 0.15564 | -120.845 | 120.4285 | 0.01831 | 120.5795 | 120.6619 | -98.5886 | -0.27466 | 0.07782 | 0.15106 | 120.5933 | 120.7581 | 22.0596 | 120.6665 | 120.5795 | 120.726 | 120.5887 | -0.27466 | 120.6665 | 120.5795 | 120.5887 | 22.0596 | 120.726 | -0.21973 | -120.9229
2901.5 | 120.4056 | -120.163 | 0.050354 | 0.00206 | -0.025413 | 0.013531 | 0.050699 | -0.022657 | -0.029995 | 0.041973 | 0.11444 | 0.068665 | -0.086975 | 0.18768 | -1.9135 | 0.21057 | -0.21515 | -111.0672 | 0.09613 | -120.4605 | 120.076 | 0.018311 | 120.2774 | 120.3506 | -1.9638 | -0.29755 | 0.045776 | 0.20142 | 119.9478 | 9.0958 | 118.2495 | 120.2316 | 120.2774 | 120.2591 | 120.3735 | -0.29755 | 120.2316 | 120.2774 | 120.3735 | 118.2495 | 120.2591 | -0.13733 | -120.5109
2903.2188 | 120.5704 | -120.3323 | 0.15564 | 0.00206 | -0.022422 | 0.011608 | 0.060739 | -0.02458 | -0.012691 | 0.073802 | 0.07782 | 0.086975 | -0.13275 | 0.10986 | -24.0005 | 0.10986 | -0.050354 | -115.2008 | 0.11902 | -120.726 | 120.1996 | -0.068665 | 120.4102 | 120.4422 | -24.1562 | -0.39368 | -0.036621 | 0.21057 | 120.282 | 5.1315 | 96.3318 | 120.4193 | 120.4102 | 120.4514 | 120.4422 | -0.39368 | 120.4193 | 120.4102 | 120.4422 | 96.3318 | 120.4514 | -0.28839 | -120.8817
2904.9844 | 120.7764 | -120.488 | 0.073242 | 0.0096895 | -0.0057592 | 0.0090447 | 0.06843 | -0.025434 | 0.03281 | 0.15113 | 0.091553 | 0.07782 | -0.09613 | 0.16022 | -115.0177 | 0.14191 | -0.16937 | -115.5762 | 0.086975 | -120.7947 | 120.3918 | 0.004578 | 120.5795 | 120.6482 | -115.0909 | -0.3067 | 0.013733 | 0.18768 | 120.3186 | 4.9118 | 5.4703 | 120.5658 | 120.5795 | 120.575 | 120.6299 | -0.3067 | 120.5658 | 120.5795 | 120.6299 | 5.4703 | 120.575 | -0.16937 | -120.8679
2906.6875 | 119.3985 | -119.133 | 0.086975 | 0.00206 | 0.045938 | 0.0054131 | 0.055399 | -0.025648 | -0.0075644 | 0.21223 | 0.032043 | 0.10529 | -0.11902 | 0.013733 | -45.8221 | -0.068665 | -0.12817 | -97.8333 | 0.14648 | -119.4351 | 119.014 | 0.018311 | 119.165 | 119.1467 | -45.9091 | -0.30212 | 0.059509 | 0.15106 | 119.0048 | 21.2997 | 73.3109 | 119.2383 | 119.165 | 119.2795 | 119.0643 | -0.30212 | 119.2383 | 119.165 | 119.0643 | 73.3109 | 119.2795 | -0.20599 | -119.5221
2908.4219 | 120.5933 | -120.3781 | 0.050354 | 0.0096895 | -0.01879 | 0.0094721 | 0.048776 | -0.024152 | -0.029781 | 0.089183 | 0.10071 | 0.064087 | -0.07782 | 0.19226 | -1.2177 | 0.19226 | -0.16937 | -33.252 | 0.10529 | -120.6757 | 120.3003 | 0.013733 | 120.4788 | 120.5704 | -1.268 | -0.29755 | 0.054932 | 0.17853 | 120.2087 | 87.1262 | 119.1605 | 120.4422 | 120.4788 | 120.4834 | 120.5704 | -0.29755 | 120.4422 | 120.4788 | 120.5704 | 119.1605 | 120.4834 | -0.12817 | -120.726
2910.1562 | 120.6985 | -120.4559 | 0.068665 | 0.017319 | -0.0064002 | 0.0084039 | 0.055612 | -0.024793 | 0.0071756 | 0.096446 | 0.11444 | 0.054932 | -0.091553 | 0.20599 | -63.1119 | 0.19684 | -0.18768 | -109.5016 | 0.07782 | -120.8084 | 120.3644 | -0.013733 | 120.5704 | 120.6619 | -63.1805 | -0.35248 | 0.009155 | 0.20599 | 120.2682 | 10.9543 | 57.3441 | 120.5109 | 120.5704 | 120.5338 | 120.6528 | -0.35248 | 120.5109 | 120.5704 | 120.6528 | 57.3441 | 120.5338 | -0.16022 | -120.8771
2911.9219 | 120.2179 | -120.0714 | 0.09613 | 0.0096895 | -0.027122 | 0.0075495 | 0.043222 | -0.025861 | -0.028499 | 0.030223 | 0.064087 | 0.082397 | -0.10529 | 0.12817 | -0.8194 | 0.10986 | -0.022888 | -3.3737 | 0.13733 | -120.3827 | 119.9661 | -0.013733 | 120.1355 | 120.1996 | -0.91553 | -0.31128 | 0.041199 | 0.16937 | 120.0485 | 116.6977 | 119.252 | 120.1538 | 120.1355 | 120.2087 | 120.1813 | -0.31128 | 120.1538 | 120.1355 | 120.1813 | 119.252 | 120.2087 | -0.20142 | -120.4788
2913.625 | 120.3552 | -120.2591 | 0.10071 | 0.0096895 | -0.01879 | 0.0092585 | 0.056253 | -0.026502 | -0.030422 | 0.052654 | 0.09613 | 0.045776 | -0.09613 | 0.16937 | -0.11902 | 0.15564 | -0.068665 | -118.0069 | 0.091553 | -120.5109 | 120.163 | -0.054932 | 120.3552 | 120.4285 | -0.21973 | -0.25177 | -0.009155 | 0.19226 | 120.1904 | 2.2522 | 120.1401 | 120.3049 | 120.3552 | 120.3506 | 120.4147 | -0.25177 | 120.3049 | 120.3552 | 120.4147 | 120.1401 | 120.3506 | -0.19684 | -120.6116
2915.3438 | 120.4559 | -120.2133 | 0.032043 | 0.024948 | -0.011954 | 0.0051995 | 0.04899 | -0.025007 | -0.029568 | 0.033214 | -0.009155 | 0.091553 | -0.14648 | 0.054932 | -1.4694 | 0.054932 | -0.022888 | -14.3143 | 0.15106 | -120.5338 | 120.0668 | 0.05951 | 120.2042 | 120.2682 | -1.5015 | -0.32043 | 0.11902 | 0.13733 | 120.1904 | 105.899 | 118.7439 | 120.3049 | 120.2042 | 120.3644 | 120.2682 | -0.32043 | 120.3049 | 120.2042 | 120.2682 | 118.7439 | 120.3644 | -0.17853 | -120.5658
2917.0469 | 120.4788 | -120.3461 | 0.059509 | 0.0096895 | -0.014945 | 0.0090447 | 0.049631 | -0.022016 | -0.032772 | 0.034709 | 0.022888 | 0.091553 | -0.11902 | 0.086975 | -0.6134 | 0.082397 | -0.022888 | -30.9906 | 0.13275 | -120.6482 | 120.2271 | 0.032044 | 120.369 | 120.433 | -0.67291 | -0.30212 | 0.073242 | 0.14191 | 120.3232 | 89.3555 | 119.7327 | 120.4376 | 120.369 | 120.4788 | 120.4285 | -0.30212 | 120.4376 | 120.369 | 120.4285 | 119.7327 | 120.4788 | -0.17853 | -120.7077
2918.75 | 120.6848 | -120.3644 | 0.045776 | 0.0096895 | -0.014731 | 0.0073359 | 0.041941 | -0.026502 | -0.028713 | 0.033641 | 0.041199 | 0.045776 | -0.09613 | 0.14191 | -0.37079 | 0.15106 | -0.11902 | -19.4092 | 0.12817 | -120.7214 | 120.2682 | 0 | 120.4056 | 120.5063 | -0.41656 | -0.35706 | 0.082398 | 0.13733 | 120.2454 | 100.9552 | 119.9936 | 120.4102 | 120.4056 | 120.4926 | 120.5154 | -0.35706 | 120.4102 | 120.4056 | 120.5154 | 119.9936 | 120.4926 | -0.14191 | -120.7672
2920.4531 | 120.726 | -120.4193 | 0.054932 | 0.0096895 | -0.014304 | 0.01054 | 0.046427 | -0.027357 | -0.028286 | 0.034923 | 0.059509 | 0.054932 | -0.086975 | 0.15106 | -0.25635 | 0.16479 | -0.13275 | -27.3422 | 0.1236 | -120.7672 | 120.3323 | 0 | 120.4788 | 120.5704 | -0.31128 | -0.3479 | 0.068664 | 0.14648 | 120.2866 | 93.0771 | 120.163 | 120.4742 | 120.4788 | 120.5429 | 120.5841 | -0.3479 | 120.4742 | 120.4788 | 120.5841 | 120.163 | 120.5429 | -0.14191 | -120.8221
2922.1719 | 120.6802 | -120.4971 | 0.082397 | 0.0096895 | -0.015586 | 0.0071221 | 0.058603 | -0.02757 | -0.033626 | 0.0424 | -0.018311 | 0.11444 | -0.13733 | 0.086975 | -0.45776 | 0.059509 | 0.050354 | -0.11902 | 0.15564 | -120.8267 | 120.3598 | 0.032044 | 120.4788 | 120.5841 | -0.54016 | -0.32959 | 0.073243 | 0.11902 | 120.5475 | 120.3781 | 120.0394 | 120.6116 | 120.4788 | 120.6528 | 120.5566 | -0.32959 | 120.6116 | 120.4788 | 120.5566 | 120.0394 | 120.6528 | -0.21973 | -120.9091
2923.9375 | 120.726 | -120.52 | 0.073242 | 0.017319 | -0.0085364 | 0.0028497 | 0.060526 | -0.023298 | -0.033626 | 0.048595 | 0.032043 | 0.086975 | -0.12817 | 0.07782 | -0.28381 | 0.064087 | -0.013733 | 0.068665 | 0.16479 | -120.8359 | 120.3918 | 0.013733 | 120.5521 | 120.5978 | -0.35706 | -0.31586 | 0.091553 | 0.16022 | 120.5063 | 120.5887 | 120.2362 | 120.607 | 120.5521 | 120.6848 | 120.5841 | -0.31586 | 120.607 | 120.5521 | 120.5841 | 120.2362 | 120.6848 | -0.20142 | -120.9091
2925.6562 | 120.1584 | -119.8929 | 0.041199 | 0.0096895 | -0.021995 | 0.0075495 | 0.047067 | -0.024366 | -0.030849 | 0.024028 | 0.009155 | 0.091553 | -0.15106 | 0.050354 | -0.036621 | 0.064087 | -0.013733 | 0.013733 | 0.16022 | -120.2499 | 119.7418 | 0.050354 | 119.902 | 119.9432 | -0.07782 | -0.35706 | 0.11902 | 0.16022 | 119.8791 | 119.9066 | 119.8563 | 119.9844 | 119.902 | 120.0531 | 119.957 | -0.35706 | 119.9844 | 119.902 | 119.957 | 119.8563 | 120.0531 | -0.19226 | -120.2911
2927.3906 | 120.4193 | -120.282 | 0.09613 | 0.024948 | -0.023276 | 0.0060541 | 0.040445 | -0.023511 | -0.030208 | 0.026592 | 0.11902 | 0.050354 | -0.091553 | 0.19684 | 0.11902 | 0.20599 | -0.14648 | 0.23346 | 0.11902 | -120.5933 | 120.1904 | -0.045776 | 120.401 | 120.4788 | 0.022889 | -0.31128 | 0.022889 | 0.21057 | 120.1355 | 120.5154 | 120.401 | 120.3323 | 120.401 | 120.401 | 120.488 | -0.31128 | 120.3323 | 120.401 | 120.488 | 120.401 | 120.401 | -0.18768 | -120.6894
2929.1094 | 120.4559 | -120.401 | 0.10529 | 0.00206 | -0.01345 | 0.0054131 | 0.049417 | -0.027998 | -0.032772 | 0.053295 | 0.064087 | 0.091553 | -0.14191 | 0.13275 | 0.018311 | 0.10071 | -0.050354 | -0.027466 | 0.13733 | -120.6848 | 120.2591 | -0.013733 | 120.4651 | 120.5338 | -0.086975 | -0.28381 | 0.032043 | 0.20599 | 120.3506 | 120.3735 | 120.4193 | 120.4926 | 120.4651 | 120.5383 | 120.5017 | -0.28381 | 120.4926 | 120.4651 | 120.5017 | 120.4193 | 120.5383 | -0.24719 | -120.7901
2930.8125 | 120.6528 | -120.4742 | 0.073242 | 0.017319 | -0.023063 | 0.0064813 | 0.045572 | -0.024152 | -0.031917 | 0.02531 | -0.009155 | 0.09613 | -0.13275 | 0.07782 | -0.018311 | 0.059509 | 0.041199 | 0.10529 | 0.16479 | -120.7855 | 120.3415 | 0.022888 | 120.4651 | 120.5521 | -0.091553 | -0.31128 | 0.091553 | 0.1236 | 120.5154 | 120.5795 | 120.4559 | 120.5704 | 120.4651 | 120.639 | 120.5338 | -0.31128 | 120.5704 | 120.4651 | 120.5338 | 120.4559 | 120.639 | -0.20599 | -120.8588
2932.5156 | 120.8176 | -120.1767 | 0.48523 | 0.00206 | 0.27665 | 0.0077631 | 0.10603 | -0.02522 | -0.032345 | 0.87574 | 0.16479 | 0.19226 | -0.050354 | -0.17853 | -0.27924 | -0.09613 | -0.51727 | -2.4536 | 0.26093 | -120.5292 | 120.1263 | -0.29297 | 120.3415 | 119.9982 | -0.76446 | -0.35248 | -0.2243 | 0.21515 | 119.6594 | 117.7231 | 119.8975 | 120.369 | 120.3415 | 120.4376 | 120.0806 | -0.35248 | 120.369 | 120.3415 | 120.0806 | 119.8975 | 120.4376 | -0.53558 | -121.0144
2934.2188 | 119.7372 | -8.6838 | 111.1084 | 0.0096895 | -0.0021276 | 0.0071221 | 0.16541 | 0.035235 | 0.030888 | 0.26649 | 0.013733 | 0.022888 | -0.15106 | 0.1831 | 0.1236 | 0.21515 | -0.082397 | 0.28381 | 109.9457 | -10.2219 | 8.5327 | -111.0855 | 8.6975 | 8.8669 | -110.9848 | -1.5381 | -1.1627 | 0.16479 | 8.6014 | 8.9676 | 8.8074 | 8.7067 | 8.6975 | 118.6295 | 8.8989 | -1.5381 | 8.7067 | 8.6975 | 8.8989 | 8.8074 | 118.6295 | -111.2595 | -121.3303
2935.9844 | 120.2591 | -44.1422 | 75.7324 | 0.0096895 | -0.0017004 | 0.0051995 | 0.080179 | 0.020709 | 0.01508 | 0.14387 | 0.036621 | 0.041199 | -0.14191 | 0.18768 | 0.091553 | 0.21515 | -0.16022 | 0.26093 | 84.0408 | -36.2137 | 44.0002 | -75.6912 | 44.1788 | 44.3298 | -75.6409 | 7.9285 | 8.3084 | 0.17853 | 43.9819 | 44.4031 | 44.2337 | 44.1833 | 44.1788 | 128.183 | 44.3573 | 7.9285 | 44.1833 | 44.1788 | 44.3573 | 44.2337 | 128.183 | -75.8743 | -111.9461
2937.6875 | 120.1675 | -76.5015 | 43.9407 | 0.017319 | 0.00064938 | 0.0039179 | 0.10816 | 0.0053277 | -8.7646e-05 | 0.13469 | 0.009155 | 0.073242 | -0.11902 | 0.15564 | 0.045776 | 0.11444 | 0.068665 | 0.21973 | 57.8979 | -63.1302 | 76.3824 | -43.8675 | 76.5106 | 76.6571 | -43.895 | 13.3713 | 13.9572 | 0.12817 | 76.5701 | 76.7212 | 76.5472 | 76.5747 | 76.5106 | 134.3994 | 76.6159 | 13.3713 | 76.5747 | 76.5106 | 76.6159 | 76.5472 | 134.3994 | -44.0598 | -107.0709
2939.4219 | 120.3598 | -119.9799 | 0.073242 | 0.017319 | -0.0012732 | 0.0030633 | 0.082956 | -0.024366 | -0.029995 | 0.024028 | -0.009155 | 0.07782 | -0.14648 | 0.10071 | -0.009155 | 0.082397 | 0.036621 | 0.18768 | 0.16937 | -120.369 | 119.8334 | 0.004578 | 119.9707 | 120.0806 | -0.082397 | -0.3891 | 0.096131 | 0.13733 | 120.0165 | 120.1675 | 119.9707 | 120.0577 | 119.9707 | 120.1492 | 120.0623 | -0.3891 | 120.0577 | 119.9707 | 120.0623 | 119.9707 | 120.1492 | -0.21973 | -120.4422
2941.125 | 120.282 | -119.8791 | 0.1236 | 0.017319 | 0.00022218 | 0.0079767 | 0.23783 | -0.026075 | -0.032985 | 0.19065 | -0.018311 | 0.10986 | -0.14191 | 0.082397 | -0.009155 | 0.068665 | 0.050354 | 0.16479 | 0.21057 | -120.2316 | 119.7372 | -0.013733 | 119.8608 | 119.9615 | -0.13275 | -0.35248 | 0.086975 | 0.1236 | 119.9295 | 120.0439 | 119.87 | 119.989 | 119.8608 | 120.0897 | 119.9478 | -0.35248 | 119.989 | 119.8608 | 119.9478 | 119.87 | 120.0897 | -0.2655 | -120.3552
2942.8906 | 120.3873 | -120.1126 | 0.13275 | 0.00206 | -0.0010596 | 0.0077631 | 0.31089 | -0.026075 | -0.030636 | 0.25111 | 0.050354 | 0.059509 | -0.10071 | 0.15106 | 0.045776 | 0.14191 | -0.022888 | 0.22888 | 0.20142 | -120.3552 | 120.0119 | -0.073242 | 120.163 | 120.2637 | -0.086975 | -0.24262 | 0.068665 | 0.15106 | 120.0897 | 120.3415 | 120.1584 | 120.1721 | 120.163 | 120.314 | 120.2545 | -0.24262 | 120.1721 | 120.163 | 120.2545 | 120.1584 | 120.314 | -0.23346 | -120.488
2944.5938 | 120.2225 | -119.9982 | 0.14648 | 0.017319 | 0.00022218 | 0.0051995 | 0.2295 | -0.02522 | -0.029568 | 0.17549 | 0.12817 | 0.045776 | -0.10071 | 0.19226 | 0.1236 | 0.21057 | -0.13275 | -3.2455 | 0.13733 | -120.2316 | 119.8975 | -0.10071 | 120.1263 | 120.1904 | -0.022888 | -0.23346 | -0.009155 | 0.22888 | 119.8654 | 116.7526 | 120.1218 | 120.0439 | 120.1263 | 120.1355 | 120.2087 | -0.23346 | 120.0439 | 120.1263 | 120.2087 | 120.1218 | 120.1355 | -0.24719 | -120.3781
2946.3125 | 120.3964 | -120.1309 | 0.10529 | -0.0055695 | 0.00064938 | 0.0071221 | 0.16477 | -0.025434 | -0.031704 | 0.10414 | 0.018311 | 0.07782 | -0.14191 | 0.09613 | -0.022888 | 0.068665 | 0 | -8.0978 | 0.16479 | -120.4514 | 119.989 | -0.027466 | 120.1492 | 120.2271 | -0.12817 | -0.32044 | 0.059509 | 0.16022 | 120.1309 | 112.0331 | 120.108 | 120.2087 | 120.1492 | 120.2957 | 120.1996 | -0.32044 | 120.2087 | 120.1492 | 120.1996 | 120.108 | 120.2957 | -0.24719 | -120.5566
2948.0312 | 120.5017 | -119.9432 | 0.28839 | 0.0096895 | 0.0021448 | 0.0090447 | 0.94001 | -0.02223 | -0.031704 | 0.83921 | -0.013733 | 0.09613 | -0.15564 | 0.054932 | -0.022888 | 0.07782 | -0.013733 | -72.1115 | 0.28381 | -120.2774 | 119.7876 | -0.19226 | 119.9295 | 119.9982 | -0.31128 | -0.33417 | -0.004578 | 0.14191 | 119.9295 | 47.8317 | 119.9203 | 120.0394 | 119.9295 | 120.227 | 120.0211 | -0.33417 | 120.0394 | 119.9295 | 120.0211 | 119.9203 | 120.227 | -0.44403 | -120.5658
2949.75 | 120.314 | -119.5633 | 0.65918 | 0.017319 | -0.0012732 | 0.0058405 | 1.6749 | -0.026075 | -0.031917 | 1.6595 | 0.022888 | 0.082397 | -0.14648 | 0.13733 | 0.041199 | 0.10529 | 0.004578 | -17.4088 | 0.43945 | -119.9066 | 119.4168 | -0.57678 | 119.5862 | 119.7006 | -0.61798 | -0.34332 | -0.21973 | 0.16937 | 119.5679 | 102.1545 | 119.6045 | 119.6457 | 119.5862 | 120.0027 | 119.6686 | -0.34332 | 119.6457 | 119.5862 | 119.6686 | 119.6045 | 120.0027 | -0.80566 | -120.5658
2951.5 | 120.3049 | -119.7968 | 0.032043 | 0.00206 | 0.001504 | 0.0084039 | 0.089792 | -0.023298 | -0.030849 | 0.032787 | 0.013733 | 0.10071 | -0.16479 | 0.059509 | -0.041199 | 0.054932 | -0.013733 | 0.07782 | 0.15564 | -120.2499 | 119.632 | 0.068665 | 119.8105 | 119.8563 | -0.073242 | -0.45319 | 0.1236 | 0.17853 | 119.783 | 119.8746 | 119.7556 | 119.8975 | 119.8105 | 119.9524 | 119.8517 | -0.45319 | 119.8975 | 119.8105 | 119.8517 | 119.7556 | 119.9524 | -0.19684 | -120.282
2953.25 | 120.4376 | -120.2179 | 0.10071 | 0.032577 | -0.00084602 | 0.0034905 | 0.088938 | -0.024366 | -0.030208 | 0.031719 | 0.10529 | 0.054932 | -0.09613 | 0.20142 | 0.10986 | 0.17853 | -0.11444 | 0.24261 | 0.13275 | -120.5154 | 120.1218 | -0.045776 | 120.3232 | 120.4193 | 0.009155 | -0.29755 | 0.032043 | 0.20142 | 120.1035 | 120.4605 | 120.3278 | 120.2728 | 120.3232 | 120.3506 | 120.3964 | -0.29755 | 120.2728 | 120.3232 | 120.3964 | 120.3278 | 120.3506 | -0.19684 | -120.6161
2955.0312 | 120.4971 | -120.3461 | 0.09613 | 0.0096895 | 0.00022218 | 0.0092585 | 0.097269 | -0.025434 | -0.031704 | 0.037059 | 0.054932 | 0.073242 | -0.13733 | 0.15564 | 0.041199 | 0.13275 | -0.041199 | 0.13733 | 0.16022 | -120.6116 | 120.2087 | -0.022888 | 120.401 | 120.5017 | -0.054931 | -0.2655 | 0.064087 | 0.19226 | 120.3049 | 120.4834 | 120.3873 | 120.4193 | 120.401 | 120.5063 | 120.4788 | -0.2655 | 120.4193 | 120.401 | 120.4788 | 120.3873 | 120.5063 | -0.23346 | -120.7077
2956.7344 | 120.5292 | -120.3964 | 0.082397 | 0.00206 | -0.0010596 | 0.0086175 | 0.1024 | -0.022871 | -0.030849 | 0.0424 | 0.059509 | 0.073242 | -0.1236 | 0.14648 | 0.041199 | 0.10529 | -0.041199 | 0.1236 | 0.15106 | -120.6619 | 120.2728 | -0.009155 | 120.4559 | 120.5429 | -0.041198 | -0.2655 | 0.068665 | 0.1831 | 120.3552 | 120.52 | 120.4376 | 120.4697 | 120.4559 | 120.5475 | 120.5017 | -0.2655 | 120.4697 | 120.4559 | 120.5017 | 120.4376 | 120.5475 | -0.20599 | -120.7443
2958.5 | 120.6665 | -120.314 | 0.12817 | 0.0096895 | -0.0023412 | 0.011395 | 0.18208 | -0.025648 | -0.028713 | 0.13447 | 0.09613 | 0.041199 | -0.09613 | 0.15564 | 0.07782 | 0.15564 | -0.15106 | 0.14648 | 0.14191 | -120.6528 | 120.2179 | -0.086975 | 120.4102 | 120.4697 | -0.050354 | -0.33875 | 0.013733 | 0.19226 | 120.163 | 120.4605 | 120.3918 | 120.3552 | 120.4102 | 120.4559 | 120.4697 | -0.33875 | 120.3552 | 120.4102 | 120.4697 | 120.3918 | 120.4559 | -0.2243 | -120.7809
2960.2188 | 120.7352 | -120.401 | 0.045776 | 0.0096895 | -0.0031958 | 0.0049859 | 0.093637 | -0.026716 | -0.030422 | 0.03535 | 0.041199 | 0.068665 | -0.11902 | 0.15564 | 0.045776 | 0.16022 | -0.11444 | 0.14191 | 0.12817 | -120.7352 | 120.282 | 0.022889 | 120.4422 | 120.5566 | 0 | -0.33417 | 0.082398 | 0.16022 | 120.2866 | 120.5429 | 120.4468 | 120.4697 | 120.4422 | 120.5292 | 120.5612 | -0.33417 | 120.4697 | 120.4422 | 120.5612 | 120.4468 | 120.5292 | -0.16479 | -120.7809
2962.0156 | 120.6299 | -120.4742 | 0.09613 | 0.0096895 | -0.0010596 | 0.010113 | 0.098978 | -0.024152 | -0.034054 | 0.035137 | 0.032043 | 0.073242 | -0.15106 | 0.1236 | 0.004578 | 0.091553 | -0.018311 | 0.068665 | 0.16022 | -120.7443 | 120.3232 | -0.022888 | 120.5063 | 120.5978 | -0.091552 | -0.27008 | 0.064087 | 0.18311 | 120.4559 | 120.5429 | 120.4788 | 120.5475 | 120.5063 | 120.6345 | 120.5658 | -0.27008 | 120.5475 | 120.5063 | 120.5658 | 120.4788 | 120.6345 | -0.24719 | -120.8405
2963.7188 | 115.361 | -12.8586 | 92.3538 | 0.024948 | -0.0014868 | 0.0066949 | 0.076334 | 0.034167 | 0.026829 | 0.16929 | -0.004578 | 0.032043 | -0.16937 | 0.07782 | -0.041199 | 0.036621 | -0.045776 | 0.13275 | 107.7576 | -12.8311 | 12.6892 | -92.3218 | 12.854 | 12.9364 | -92.395 | 0.027466 | 15.4037 | 0.16479 | 12.8128 | 12.9913 | 12.8174 | 12.8906 | 12.854 | 120.6162 | 12.8952 | 0.027466 | 12.8906 | 12.854 | 12.8952 | 12.8174 | 120.6162 | -92.5232 | -105.1849
2965.4375 | 96.9452 | -0.10529 | 96.0434 | 0.017319 | 8.578e-06 | 0.0064813 | 0.081461 | 0.037157 | 0.034733 | 0.18852 | -0.050354 | 0.054932 | -0.17853 | 0.059509 | -0.027466 | 0.027466 | 0.027466 | -1.474 | 117.2562 | -3.566 | -0.073242 | -95.9885 | 0.054932 | 0.16479 | -96.0709 | -3.4607 | 21.2128 | 0.12817 | 0.13275 | -1.3687 | 0.07782 | 0.16022 | 0.054932 | 117.3615 | 0.13275 | -3.4607 | 0.16022 | 0.054932 | 0.13275 | 0.07782 | 117.3615 | -96.2219 | -99.6094
2967.1562 | 120.5704 | -2.861 | 116.8716 | 0.0096895 | 0.00043578 | 0.0096857 | 0.11222 | 0.04143 | 0.033238 | 0.22633 | -0.032043 | 0.054932 | -0.17853 | 0.068665 | -0.050354 | 0.059509 | -0.068665 | -2.3666 | 116.9861 | -3.7537 | 2.6825 | -116.8167 | 2.829 | 2.9297 | -116.922 | -0.89264 | 0.11444 | 0.14648 | 2.7924 | 0.49438 | 2.8107 | 2.916 | 2.829 | 119.8471 | 2.9205 | -0.89264 | 2.916 | 2.829 | 2.9205 | 2.8107 | 119.8471 | -117.0502 | -120.6253
2968.9375 | 120.694 | -4.0604 | 116.1667 | 0.0096895 | 8.578e-06 | 0.0062677 | 0.090433 | 0.039721 | 0.034947 | 0.1977 | 0 | 0.027466 | -0.16022 | 0.1236 | 0.022888 | 0.11902 | -0.1831 | -2.536 | 116.5878 | -4.2389 | 3.9001 | -116.1392 | 4.0604 | 4.184 | -116.1438 | -0.17853 | 0.42114 | 0.16022 | 3.8773 | 1.5244 | 4.0833 | 4.0878 | 4.0604 | 120.6482 | 4.1794 | -0.17853 | 4.0878 | 4.0604 | 4.1794 | 4.0833 | 120.6482 | -116.3269 | -120.4056
2970.6875 | 115.9927 | -60.6995 | 54.8126 | 0.00206 | -0.0027686 | 0.0049859 | 6.9721 | -0.0087713 | -0.013546 | 7.0123 | -0.009155 | 0.059509 | -0.15106 | 0.091553 | -0.018311 | 0.073242 | 0.013733 | -0.55389 | 46.3669 | -41.5421 | 60.5484 | -54.7531 | 60.6903 | 60.791 | -54.8309 | 19.1574 | -8.4457 | 0.14191 | 60.7132 | 60.1456 | 60.6812 | 60.759 | 60.6903 | 107.0663 | 60.7727 | 19.1574 | 60.759 | 60.6903 | 60.7727 | 60.6812 | 107.0663 | -54.9637 | -96.3547
2972.3906 | 120.5566 | -91.2415 | 25.3372 | 0.0096895 | -0.00020502 | 0.0084039 | 0.063516 | 0.016863 | 0.0037576 | 0.054363 | -0.013733 | 0.054932 | -0.12817 | 0.086975 | -0.018311 | 0.059509 | -0.009155 | -0.23804 | 78.1998 | -41.2674 | 91.1133 | -25.2823 | 91.2277 | 91.3284 | -25.3555 | 49.9741 | 52.8625 | 0.11444 | 91.2323 | 91.0034 | 91.2231 | 91.2964 | 91.2277 | 169.4412 | 91.301 | 49.9741 | 91.2964 | 91.2277 | 91.301 | 91.2231 | 169.4412 | -25.4654 | -66.6046
2974.0938 | 120.5017 | -14.9826 | 104.8782 | 0.0096895 | -0.0014868 | 0.0045587 | 0.071634 | 0.033099 | 0.026615 | 0.1663 | 0.027466 | 0.036621 | -0.16479 | 0.12817 | 0.032043 | 0.13275 | -0.19226 | -0.30212 | 105.4733 | -15.2115 | 14.8178 | -104.8416 | 15.0101 | 15.1108 | -104.8462 | -0.22888 | 0.59509 | 0.19226 | 14.7903 | 14.6805 | 15.0146 | 15.0192 | 15.0101 | 120.4559 | 15.1154 | -0.22888 | 15.0192 | 15.0101 | 15.1154 | 15.0146 | 120.4559 | -105.043 | -120.0897
2975.7969 | 119.8975 | -12.4786 | 107.1625 | 0.00206 | -0.00041862 | 0.0090447 | 0.082956 | 0.031817 | 0.02747 | 0.17463 | -0.018311 | 0.041199 | -0.16937 | 0.050354 | -0.045776 | 0.036621 | -0.059509 | -0.68207 | 107.8629 | -12.9181 | 12.3093 | -107.1213 | 12.4603 | 12.529 | -107.2083 | -0.43945 | 0.70038 | 0.15106 | 12.4191 | 11.7966 | 12.4329 | 12.5198 | 12.4603 | 120.3415 | 12.5153 | -0.43945 | 12.5198 | 12.4603 | 12.5153 | 12.4329 | 120.3415 | -107.3318 | -120.0806
2977.5 | 92.6651 | -0.13275 | 94.693 | 0.024948 | -0.0021276 | 0.0041315 | 0.069712 | 0.035235 | 0.031315 | 0.17613 | -0.054932 | 0.036621 | -0.19684 | 0.050354 | -0.036621 | 0.027466 | -0.013733 | -0.3479 | 113.3652 | -7.37 | -0.064087 | -94.6564 | 0.077819 | 0.18311 | -94.7296 | -7.2372 | 18.6722 | 0.14191 | 0.11902 | -0.21515 | 0.09613 | 0.16937 | 0.077819 | 113.4979 | 0.16022 | -7.2372 | 0.16937 | 0.077819 | 0.16022 | 0.09613 | 113.4979 | -94.8898 | -102.063
2979.2188 | 99.8062 | -2.6642 | 86.6455 | 0.0096895 | -0.0012732 | 0.0037043 | 0.076334 | 0.035876 | 0.031529 | 0.18681 | 0.004578 | 0.032043 | -0.16937 | 0.10986 | -0.004578 | 0.082397 | -0.041199 | 0.18768 | 117.0502 | -3.6438 | 2.4948 | -86.6135 | 2.6688 | 2.774 | -86.6501 | -0.97961 | 30.4047 | 0.17395 | 2.623 | 2.8519 | 2.6596 | 2.6962 | 2.6688 | 119.7144 | 2.7466 | -0.97961 | 2.6962 | 2.6688 | 2.7466 | 2.6596 | 119.7144 | -86.8149 | -90.2893
2980.9844 | 120.6528 | -3.9642 | 115.9103 | 0.0096895 | -0.002555 | 0.0084039 | 0.16093 | 0.039721 | 0.03217 | 0.2667 | -0.022888 | 0.054932 | -0.17853 | 0.082397 | -0.018311 | 0.086975 | -0.12817 | 0.16937 | 116.6153 | -4.2206 | 3.7857 | -115.8554 | 3.9413 | 4.0466 | -115.9286 | -0.25635 | 0.70496 | 0.15564 | 3.8361 | 4.1336 | 3.9459 | 4.0192 | 3.9413 | 120.5795 | 4.0512 | -0.25635 | 4.0192 | 3.9413 | 4.0512 | 3.9459 | 120.5795 | -116.0889 | -120.1309
2982.6875 | 119.6548 | -106.5445 | 12.6892 | 0.0096895 | 0.0036402 | 0.0043451 | 0.062876 | -0.015394 | -0.023586 | 0.017833 | -0.022888 | 0.07782 | -0.13733 | 0.068665 | -0.036621 | 0.050354 | 0 | 0.11902 | 13.1241 | -106.6452 | 106.4072 | -12.6114 | 106.5216 | 106.6132 | -12.7258 | -0.10071 | 0.43487 | 0.11444 | 106.5445 | 106.6635 | 106.5079 | 106.6223 | 106.5216 | 119.6686 | 106.5948 | -0.10071 | 106.6223 | 106.5216 | 106.5948 | 106.5079 | 119.6686 | -12.8265 | -119.3344
2984.4688 | 120.6253 | -106.4117 | 13.7238 | 0.0096895 | -0.001914 | 0.0084039 | 0.089578 | -0.014753 | -0.024654 | 0.043682 | 0 | 0.059509 | -0.14648 | 0.068665 | -0.027466 | 0.064087 | 0.004578 | 0.12817 | 13.0875 | -107.4692 | 106.2653 | -13.6642 | 106.4117 | 106.4804 | -13.7512 | -1.0574 | -0.63629 | 0.14648 | 106.4163 | 106.5399 | 106.3843 | 106.4713 | 106.4117 | 119.4992 | 106.4758 | -1.0574 | 106.4713 | 106.4117 | 106.4758 | 106.3843 | 119.4992 | -13.8702 | -121.1929
2986.1719 | 120.5109 | -105.7663 | 14.1495 | 0.0096895 | 0.00043578 | 0.0041315 | 0.055185 | -0.014112 | -0.024868 | 0.013774 | -0.027466 | 0.064087 | -0.15106 | 0.054932 | -0.036621 | 0.032043 | 0.013733 | 0.09613 | 13.884 | -106.6589 | 105.6152 | -14.0854 | 105.7388 | 105.8212 | -14.1861 | -0.89264 | -0.2655 | 0.1236 | 105.78 | 105.8624 | 105.7297 | 105.8304 | 105.7388 | 119.6503 | 105.7983 | -0.89264 | 105.8304 | 105.7388 | 105.7983 | 105.7297 | 119.6503 | -14.3005 | -120.8084
2987.9375 | 115.2969 | -47.9233 | 66.5451 | 0.0096895 | -0.0027686 | 0.0064813 | 6.9721 | -0.0006537 | 0.013584 | 7.0123 | 0.073242 | 0.013733 | -0.1236 | 0.60425 | 0.004578 | 0.45319 | -0.018311 | 0.26093 | 59.0286 | -32.1808 | 47.7997 | -66.5314 | 47.9965 | 48.5275 | -66.5405 | 15.7425 | -7.5165 | 0.19684 | 47.905 | 48.1842 | 47.9279 | 47.937 | 47.9965 | 106.9519 | 48.3765 | 15.7425 | 47.937 | 47.9965 | 48.3765 | 47.9279 | 106.9519 | -66.6687 | -98.7259
2989.6406 | 120.4102 | -0.38452 | 119.3115 | 0.017319 | -0.0040502 | 0.0069085 | 0.068003 | 0.041003 | 0.034306 | 0.18318 | 0.068665 | 0.004578 | -0.13275 | 0.1831 | 0.073242 | 0.16022 | -0.21973 | 0.3067 | 119.9661 | -0.55847 | 0.25177 | -119.3069 | 0.45319 | 0.56763 | -119.2383 | -0.17395 | 0.6546 | 0.20142 | 0.16479 | 0.69122 | 0.45776 | 0.3891 | 0.45319 | 120.3506 | 0.54474 | -0.17395 | 0.3891 | 0.45319 | 0.54474 | 0.45776 | 120.3506 | -119.4443 | -119.87
2991.3438 | 119.8196 | -0.737 | 118.309 | 0.0096895 | -0.002555 | 0.0060541 | 0.052835 | 0.041003 | 0.035374 | 0.17271 | 0.059509 | -0.004578 | -0.14191 | 0.17395 | 0.086975 | 0.18768 | -0.16937 | 0.35248 | 119.0689 | -0.9201 | 0.59509 | -118.3136 | 0.79651 | 0.91095 | -118.222 | -0.1831 | 0.75989 | 0.20142 | 0.56763 | 1.0895 | 0.82398 | 0.73242 | 0.79651 | 119.8059 | 0.92468 | -0.1831 | 0.73242 | 0.79651 | 0.92468 | 0.82398 | 119.8059 | -118.4509 | -119.2291
2993.0781 | 120.4193 | -0.54932 | 119.3619 | 0.0096895 | -0.00063242 | 0.0073359 | 0.12226 | 0.041216 | 0.034733 | 0.23487 | -0.041199 | 0.054932 | -0.18768 | 0.050354 | -0.073242 | 0.022888 | -0.054932 | 0.43945 | 119.8791 | -0.80109 | 0.36163 | -119.3069 | 0.50812 | 0.59967 | -119.4351 | -0.25177 | 0.51727 | 0.14648 | 0.49438 | 0.98877 | 0.47607 | 0.60425 | 0.50812 | 120.4285 | 0.5722 | -0.25177 | 0.60425 | 0.50812 | 0.5722 | 0.47607 | 120.4285 | -119.5496 | -120.163
2994.7812 | 120.1584 | -1.2955 | 118.8538 | 0.00206 | 0.00043578 | 0.0077631 | 0.065866 | 0.042071 | 0.033665 | 0.17399 | 0 | 0.027466 | -0.17395 | 0.10071 | -0.027466 | 0.036621 | -0.050354 | 0.12817 | 118.9499 | -1.4511 | 1.1215 | -118.8263 | 1.2955 | 1.3962 | -118.8812 | -0.15564 | 0.09613 | 0.17395 | 1.2451 | 1.4236 | 1.268 | 1.3229 | 1.2955 | 120.2454 | 1.3321 | -0.15564 | 1.3229 | 1.2955 | 1.3321 | 1.268 | 120.2454 | -119.0277 | -120.3049
2996.5156 | 120.3918 | -1.3824 | 119.0689 | 0.0096895 | 0.00043578 | 0.0069085 | 0.19212 | 0.03908 | 0.033879 | 0.27546 | 0.059509 | 0.004578 | -0.13733 | 0.18768 | 0.091553 | 0.15564 | -0.15564 | 0.27008 | 119.1193 | -1.355 | 1.2451 | -119.0643 | 1.442 | 1.5701 | -118.9774 | 0.027466 | 0.050354 | 0.19684 | 1.2268 | 1.6525 | 1.474 | 1.387 | 1.442 | 120.5017 | 1.5381 | 0.027466 | 1.387 | 1.442 | 1.5381 | 1.474 | 120.5017 | -119.2062 | -120.4239
2998.25 | 120.4468 | -0.58136 | 119.3298 | 0.0096895 | -0.00084602 | 0.0058405 | 0.081461 | 0.043139 | 0.03217 | 0.19984 | -0.050354 | 0.032043 | -0.16937 | 0.073242 | -0.041199 | 0.013733 | -0.027466 | 0.086975 | 119.9341 | -0.76446 | 0.41199 | -119.2978 | 0.53101 | 0.6546 | -119.371 | -0.1831 | 0.60425 | 0.11902 | 0.55389 | 0.66834 | 0.54016 | 0.6134 | 0.53101 | 120.5154 | 0.59509 | -0.1831 | 0.6134 | 0.53101 | 0.59509 | 0.54016 | 120.5154 | -119.4992 | -120.0943
3000 | 120.5841 | -0.74158 | 119.5358 | 0.017319 | -0.0038366 | 0.0007135 | 0.1323 | 0.039721 | 0.034092 | 0.27418 | -0.009155 | 0 | -0.1236 | 0.13275 | 0.036621 | 0.10071 | -0.13275 | 0.18768 | 119.8563 | -0.77362 | 0.61798 | -119.5358 | 0.73242 | 0.87433 | -119.4992 | -0.032044 | 0.32043 | 0.11444 | 0.60883 | 0.92926 | 0.7782 | 0.74158 | 0.73242 | 120.5978 | 0.84229 | -0.032044 | 0.74158 | 0.73242 | 0.84229 | 0.7782 | 120.5978 | -119.6594 | -120.3094
3001.7031 | 120.6116 | -0.82855 | 119.5587 | 0.017319 | 0.00064938 | 0.0071221 | 0.097696 | 0.042071 | 0.03281 | 0.23936 | -0.022888 | 0.027466 | -0.16937 | 0.12817 | 0.004578 | 0.10986 | -0.16022 | 0.1831 | 119.7281 | -1.0254 | 0.65918 | -119.5312 | 0.80566 | 0.95673 | -119.5541 | -0.19684 | 0.16937 | 0.14649 | 0.66833 | 1.0117 | 0.83313 | 0.85602 | 0.80566 | 120.5566 | 0.93841 | -0.19684 | 0.85602 | 0.80566 | 0.93841 | 0.83313 | 120.5566 | -119.7281 | -120.5841
3003.4062 | 119.6411 | -1.0757 | 119.0872 | 0.0096895 | -0.0031958 | 0.0073359 | 0.055185 | 0.04143 | 0.036015 | 0.16716 | -0.045776 | 0.036621 | -0.19684 | 0.064087 | -0.050354 | 0.045776 | -0.091553 | 0.11902 | 119.2337 | -1.3092 | 0.87891 | -119.0506 | 1.03 | 1.1398 | -119.1376 | -0.23346 | 0.14648 | 0.15106 | 0.98419 | 1.1948 | 1.0254 | 1.1124 | 1.03 | 120.3094 | 1.1215 | -0.23346 | 1.1124 | 1.03 | 1.1215 | 1.0254 | 120.3094 | -119.2841 | -120.3964
3005.1406 | 120.2087 | -1.1261 | 119.2017 | 0.017319 | -0.00041862 | 0.0071221 | 0.05134 | 0.040362 | 0.036228 | 0.16459 | 0.045776 | 0.004578 | -0.1236 | 0.15106 | 0.045776 | 0.13275 | -0.21057 | 0.2243 | 119.2978 | -1.2909 | 1.0025 | -119.1971 | 1.1719 | 1.2772 | -119.1559 | -0.1648 | 0.096131 | 0.16937 | 0.91553 | 1.3504 | 1.1719 | 1.1307 | 1.1719 | 120.4239 | 1.2589 | -0.1648 | 1.1307 | 1.1719 | 1.2589 | 1.1719 | 120.4239 | -119.3253 | -120.4926
3006.8438 | 119.5679 | -102.4475 | 16.4429 | 0.017319 | -0.0034094 | 0.0049859 | 0.041727 | -0.0085577 | -0.015255 | 0.03001 | 0.059509 | 0.045776 | -0.11444 | 0.15106 | 0.041199 | 0.14191 | -0.14648 | 0.23804 | 30.8578 | -87.8174 | 102.3331 | -16.3971 | 102.507 | 102.5986 | -16.4017 | 14.6301 | 14.415 | 0.17395 | 102.301 | 102.6855 | 102.4887 | 102.4933 | 102.507 | 133.3054 | 102.5894 | 14.6301 | 102.4933 | 102.507 | 102.5894 | 102.4887 | 133.3054 | -16.5573 | -104.2603
3008.5469 | 120.4468 | -2.7191 | 117.5262 | 0.017319 | -0.00020502 | 0.0092585 | 0.075479 | 0.037371 | 0.036015 | 0.17891 | 0.041199 | 0 | -0.14648 | 0.14648 | 0.041199 | 0.13275 | -0.19226 | 0.21515 | 117.6544 | -2.9068 | 2.5726 | -117.5262 | 2.7603 | 2.8656 | -117.485 | -0.18768 | 0.12817 | 0.18768 | 2.5269 | 2.9343 | 2.7603 | 2.7191 | 2.7603 | 120.3735 | 2.8519 | -0.18768 | 2.7191 | 2.7603 | 2.8519 | 2.7603 | 120.3735 | -117.6727 | -120.433
3010.2812 | 88.4857 | -0.11902 | 86.2976 | 0.00206 | 0.00064938 | 0.0079767 | 0.060526 | 0.038226 | 0.037296 | 0.1725 | 0.009155 | 0.032043 | -0.17395 | 0.073242 | -0.022888 | 0.036621 | -0.009155 | 0.15564 | 116.8808 | -3.1403 | -0.054931 | -86.2656 | 0.12817 | 0.19226 | -86.3205 | -3.0212 | 30.5832 | 0.1831 | 0.10986 | 0.27466 | 0.096131 | 0.15106 | 0.12817 | 116.9998 | 0.15564 | -3.0212 | 0.15106 | 0.12817 | 0.15564 | 0.096131 | 116.9998 | -86.4716 | -89.4379
3011.9844 | 111.7355 | -2.4765 | 89.6027 | 0.00206 | 0.0044946 | 0.0090447 | 0.065225 | 0.040148 | 0.033238 | 0.17079 | 0.013733 | 0.045776 | -0.17395 | 0.14191 | 0 | 0.064087 | -0.064087 | 0.17853 | 118.0435 | -2.504 | 2.3026 | -89.5569 | 2.4902 | 2.6184 | -89.6027 | -0.027466 | 28.4409 | 0.18768 | 2.4124 | 2.655 | 2.4765 | 2.5223 | 2.4902 | 120.52 | 2.5406 | -0.027466 | 2.5223 | 2.4902 | 2.5406 | 2.4765 | 120.52 | -89.7766 | -92.1066
3013.7031 | 120.3369 | -81.4133 | 40.3427 | -0.0055695 | -0.0029822 | 0.0049859 | 0.044077 | -1.2902e-05 | -0.0032918 | 0.056926 | 0.036621 | 0.054932 | -0.10986 | 0.14191 | 0.045776 | 0.14648 | -0.13275 | 0.23346 | 47.3465 | -71.5897 | 81.3034 | -40.2878 | 81.4499 | 81.5552 | -40.2969 | 9.8236 | 7.0038 | 0.14648 | 81.2805 | 81.6467 | 81.459 | 81.4682 | 81.4499 | 128.7598 | 81.5598 | 9.8236 | 81.4682 | 81.4499 | 81.5598 | 81.459 | 128.7598 | -40.4526 | -111.9324
3015.4219 | 120.5612 | -108.6411 | 11.2793 | 0.017319 | 0.00043578 | 0.0077631 | 0.077188 | -0.01753 | -0.019954 | 0.04475 | 0.054932 | 0.041199 | -0.11444 | 0.14648 | 0.045776 | 0.14191 | -0.1236 | 0.23346 | 15.7562 | -104.5944 | 108.5266 | -11.2381 | 108.696 | 108.7875 | -11.2335 | 4.0466 | 4.4769 | 0.16937 | 108.5175 | 108.8745 | 108.6868 | 108.6823 | 108.696 | 124.3973 | 108.783 | 4.0466 | 108.6823 | 108.696 | 108.783 | 108.6868 | 124.3973 | -11.3937 | -115.8737
3017.125 | 119.9432 | -0.14648 | 119.8883 | 0.017319 | -0.002555 | 0.0037043 | 0.050485 | 0.042071 | 0.036228 | 0.1663 | 0.027466 | 0 | -0.14648 | 0.11902 | 0.027466 | 0.1236 | -0.15564 | 0.19684 | 120.0531 | -0.3479 | 0 | -119.8883 | 0.17395 | 0.2655 | -119.8608 | -0.20142 | 0.16479 | 0.17395 | -0.009156 | 0.34332 | 0.17395 | 0.14648 | 0.17395 | 120.1996 | 0.27008 | -0.20142 | 0.14648 | 0.17395 | 0.27008 | 0.17395 | 120.1996 | -120.0348 | -120.2362
3018.875 | 119.9615 | -0.16479 | 119.4168 | 0.024948 | -0.003623 | 0.0073359 | 0.055612 | 0.043139 | 0.036228 | 0.16886 | 0.068665 | 0 | -0.14648 | 0.19226 | 0.054932 | 0.15106 | -0.23804 | 0.24719 | 120.2225 | -0.32501 | 0.018311 | -119.4168 | 0.23346 | 0.35706 | -119.3619 | -0.16022 | 0.80566 | 0.21515 | -0.073242 | 0.41199 | 0.21973 | 0.16479 | 0.23346 | 120.3873 | 0.31586 | -0.16022 | 0.16479 | 0.23346 | 0.31586 | 0.21973 | 120.3873 | -119.5633 | -119.7418
3020.5938 | 119.8471 | -0.022888 | 116.1575 | 0.0096895 | -0.001914 | 0.0043451 | 0.056894 | 0.041003 | 0.036228 | 0.17079 | -0.064087 | 0.041199 | -0.18768 | 0.073242 | -0.07782 | 0.009155 | -0.036621 | 0.086975 | 120.3506 | -0.3479 | -0.16479 | -116.1163 | -0.041199 | 0.09613 | -116.2354 | -0.32501 | 4.1931 | 0.1236 | -0.013733 | 0.10986 | -0.054932 | 0.064087 | -0.041199 | 120.3735 | 0.032043 | -0.32501 | 0.064087 | -0.041199 | 0.032043 | -0.054932 | 120.3735 | -116.3452 | -116.5054
3022.2969 | 120.4834 | -0.17395 | 119.7739 | 0.017319 | -0.00063242 | 0.0071221 | 0.065866 | 0.041857 | 0.033665 | 0.17228 | -0.027466 | 0.027466 | -0.17853 | 0.07782 | -0.050354 | 0.022888 | -0.050354 | 0.10071 | 120.4056 | -0.34332 | -0.004578 | -119.7464 | 0.14648 | 0.25177 | -119.8242 | -0.16937 | 0.63171 | 0.15106 | 0.1236 | 0.27466 | 0.1236 | 0.20142 | 0.14648 | 120.5795 | 0.19684 | -0.16937 | 0.20142 | 0.14648 | 0.19684 | 0.1236 | 120.5795 | -119.9524 | -120.1172
3024.0156 | 119.9844 | -0.15106 | 119.1879 | 0.00206 | -0.0023412 | 0.0060541 | 0.050485 | 0.042071 | 0.036869 | 0.16651 | 0.045776 | 0.027466 | -0.14191 | 0.13733 | 0.036621 | 0.13275 | -0.19226 | 0.2243 | 119.7556 | -0.32044 | 0.009155 | -119.1605 | 0.19684 | 0.28839 | -119.1513 | -0.16937 | 0.56763 | 0.18768 | -0.041199 | 0.37537 | 0.18768 | 0.17853 | 0.19684 | 119.9066 | 0.28381 | -0.16937 | 0.17853 | 0.19684 | 0.28381 | 0.18768 | 119.9066 | -119.3298 | -119.5084
3025.7188 | 89.8773 | -46.376 | 72.3495 | 0.017319 | 0.00064938 | 0.0088311 | 0.053476 | 0.012591 | 0.005253 | 0.09666 | -0.009155 | 0.054932 | -0.16479 | 0.064087 | -0.032043 | 0.041199 | -0.027466 | 0.10529 | 70.2713 | -49.7314 | 46.2112 | -72.2946 | 46.3669 | 46.4401 | -72.3816 | -3.3554 | -2.0782 | 0.15564 | 46.3486 | 46.4813 | 46.344 | 46.431 | 46.3669 | 116.6473 | 46.4172 | -3.3554 | 46.431 | 46.3669 | 46.4172 | 46.344 | 116.6473 | -72.5143 | -122.081
3027.4531 | 119.5038 | -3.6255 | 87.6709 | 0.0096895 | -0.0012732 | 0.0028497 | 0.061807 | 0.038012 | 0.034519 | 0.17057 | -0.050354 | 0.041199 | -0.17395 | 0.086975 | -0.018311 | 0.027466 | 0.009155 | 0.15106 | 116.5192 | -3.9551 | 3.4515 | -87.6297 | 3.5751 | 3.7125 | -87.6892 | -0.32959 | 28.8483 | 0.1236 | 3.6346 | 3.7765 | 3.6072 | 3.6667 | 3.5751 | 120.1447 | 3.653 | -0.32959 | 3.6667 | 3.5751 | 3.653 | 3.6072 | 120.1447 | -87.8448 | -91.626
3029.1719 | 111.3785 | -21.0571 | 97.8882 | 0.017319 | -0.00063242 | 0.0077631 | 0.055399 | 0.032458 | 0.026402 | 0.14323 | -0.050354 | 0.036621 | -0.17395 | 0.050354 | -0.041199 | 0.022888 | -0.032043 | 0.082397 | 102.1912 | -18.0313 | 20.8832 | -97.8516 | 21.0068 | 21.1075 | -97.9294 | 3.0258 | 4.303 | 0.1236 | 21.0251 | 21.1395 | 21.0159 | 21.0938 | 21.0068 | 123.2483 | 21.08 | 3.0258 | 21.0938 | 21.0068 | 21.08 | 21.0159 | 123.2483 | -98.0621 | -115.9195
3030.9375 | 120.3094 | -117.3615 | 2.623 | 0.0096895 | -0.004264 | 0.0054131 | 0.090433 | -0.024793 | -0.028499 | 0.039836 | 0.09613 | 0.050354 | -0.086975 | 0.23346 | 0.12817 | 0.23804 | -0.14648 | 0.32044 | 2.6779 | -117.7094 | 117.2745 | -2.5726 | 117.4576 | 117.5949 | -2.4948 | -0.3479 | 0.054931 | 0.1831 | 117.215 | 117.6819 | 117.4896 | 117.4118 | 117.4576 | 120.0394 | 117.5995 | -0.3479 | 117.4118 | 117.4576 | 117.5995 | 117.4896 | 120.0394 | -2.71 | -120.3323
3032.6406 | 118.634 | -6.8024 | 95.3384 | 0.024948 | -0.00020502 | 0.0079767 | 0.059885 | 0.037157 | 0.029606 | 0.15583 | 0 | 0.041199 | -0.1831 | 0.07782 | -0.92468 | 0.045776 | -0.054932 | 0.11902 | 109.9365 | -9.6451 | 6.6193 | -95.2972 | 6.8024 | 6.8802 | -96.2631 | -2.8427 | 14.5981 | 0.1831 | 6.7474 | 6.9214 | 5.8777 | 6.8436 | 6.8024 | 116.7389 | 6.8481 | -2.8427 | 6.8436 | 6.8024 | 6.8481 | 5.8777 | 116.7389 | -95.5215 | -104.9835
3034.3594 | 94.6335 | -0.32959 | 85.5606 | 0.00206 | -0.00041862 | 0.0043451 | 0.05903 | 0.038866 | 0.034092 | 0.1663 | -0.041199 | 0.041199 | -0.17395 | 0.068665 | -1.7532 | 0.027466 | 0.018311 | 0.15564 | 116.011 | -4.4083 | 0.15564 | -85.5194 | 0.28839 | 0.39826 | -87.3138 | -4.0787 | 30.4504 | 0.13275 | 0.3479 | 0.48523 | -1.4236 | 0.37079 | 0.28839 | 116.3406 | 0.35706 | -4.0787 | 0.37079 | 0.28839 | 0.35706 | -1.4236 | 116.3406 | -85.7346 | -89.9689
3036.0781 | 120.0989 | -7.4249 | 111.9141 | 0.00206 | 0.00086298 | 0.0073359 | 0.047922 | 0.037798 | 0.034092 | 0.15327 | 0.086975 | 0.018311 | -0.1236 | 0.17395 | -1.6891 | 0.16937 | -0.23804 | 0.2243 | 112.5961 | -7.5851 | 7.3013 | -111.8958 | 7.5119 | 7.5989 | -113.6032 | -0.16022 | 0.68207 | 0.21057 | 7.1869 | 7.6492 | 5.7358 | 7.4432 | 7.5119 | 120.0211 | 7.5943 | -0.16022 | 7.4432 | 7.5119 | 7.5943 | 5.7358 | 120.0211 | -112.0377 | -119.4992
3037.7812 | 120.5933 | -6.752 | 112.9074 | 0.0096895 | 0.00064938 | 0.010754 | 0.054117 | 0.037798 | 0.03217 | 0.15647 | -0.027466 | 0.045776 | -0.17853 | 0.073242 | -0.98877 | 0.018311 | -0.036621 | 0.10986 | 113.5391 | -6.8573 | 6.5735 | -112.8616 | 6.7245 | 6.8253 | -113.8962 | -0.10529 | 0.63171 | 0.15106 | 6.7154 | 6.8619 | 5.7632 | 6.7978 | 6.7245 | 120.2911 | 6.7703 | -0.10529 | 6.7978 | 6.7245 | 6.7703 | 5.7632 | 120.2911 | -113.0859 | -119.7647
3039.5 | 119.5862 | -35.0601 | 84.3658 | 0.017319 | -0.001914 | 0.0094721 | 0.046854 | 0.023058 | 0.015934 | 0.11183 | 0.07782 | 0.009155 | -0.13733 | 0.1831 | -0.47607 | 0.15564 | -0.11444 | 0.27924 | 85.0891 | -34.552 | 34.9228 | -84.3567 | 35.1379 | 35.2432 | -84.8419 | 0.50812 | 0.72327 | 0.21515 | 34.9457 | 35.3394 | 34.584 | 35.0693 | 35.1379 | 120.1492 | 35.2158 | 0.50812 | 35.0693 | 35.1379 | 35.2158 | 34.584 | 120.1492 | -84.5032 | -118.9178
3041.2344 | 120.2774 | -20.1828 | 99.8016 | 0.0096895 | -0.00020502 | 0.0077631 | 0.04899 | 0.027117 | 0.024265 | 0.13575 | 0.009155 | 0.018311 | -0.1236 | 0.14191 | 0.37079 | 0.11902 | -0.16022 | 0.16022 | 99.9115 | -20.3659 | 20.0592 | -99.7833 | 20.192 | 20.3247 | -99.4308 | -0.18311 | 0.10986 | 0.13275 | 20.0226 | 20.343 | 20.5536 | 20.2011 | 20.192 | 120.0943 | 20.3018 | -0.18311 | 20.2011 | 20.192 | 20.3018 | 20.5536 | 120.0943 | -99.9252 | -120.1675
3042.9844 | 120.3506 | -39.6194 | 80.3696 | 0.0096895 | -0.002555 | 0.0049859 | 0.056894 | 0.018786 | 0.01273 | 0.11268 | 0.050354 | 0.036621 | -0.13275 | 0.1831 | 0.050354 | 0.16479 | -0.19684 | 0.23346 | 80.6259 | -39.7247 | 39.4867 | -80.3329 | 39.6698 | 39.8026 | -80.3192 | -0.10528 | 0.25635 | 0.18311 | 39.4226 | 39.8529 | 39.6698 | 39.6561 | 39.6698 | 120.2454 | 39.7842 | -0.10528 | 39.6561 | 39.6698 | 39.7842 | 39.6698 | 120.2454 | -80.5023 | -120.0943
3044.6875 | 115.0726 | -24.4492 | 95.7916 | 0.0096895 | 8.578e-06 | 0.0032769 | 0.053476 | 0.024126 | 0.021275 | 0.13041 | 0.068665 | 0.009155 | -0.12817 | 0.21057 | 0.45319 | 0.16937 | -0.17395 | 0.30212 | 95.8603 | -24.5956 | 24.321 | -95.7825 | 24.5178 | 24.6597 | -95.3384 | -0.14648 | 0.068665 | 0.19684 | 24.2752 | 24.7513 | 24.9023 | 24.4583 | 24.5178 | 120.3094 | 24.6185 | -0.14648 | 24.4583 | 24.5178 | 24.6185 | 24.9023 | 120.3094 | -95.9198 | -120.3873
3046.4062 | 105.8441 | -22.9477 | 97.1512 | 0.0096895 | -0.0010596 | 0.010326 | 0.062876 | 0.030108 | 0.02042 | 0.13618 | -0.018311 | 0.032043 | -0.1831 | 0.11444 | 0.3067 | 0.073242 | -0.041199 | 0.16937 | 97.4167 | -23.1308 | 22.7646 | -97.1191 | 22.9294 | 23.0621 | -96.8445 | -0.1831 | 0.2655 | 0.16479 | 22.9065 | 23.1171 | 23.2544 | 22.9797 | 22.9294 | 120.3644 | 23.0209 | -0.1831 | 22.9797 | 22.9294 | 23.0209 | 23.2544 | 120.3644 | -97.3343 | -120.282
3048.1094 | 120.1996 | -6.4178 | 113.1088 | 0.0096895 | -0.0031958 | 0.0045587 | 0.12547 | 0.038439 | 0.028538 | 0.22782 | 0 | 0.041199 | -0.17395 | 0.13275 | 0.59967 | 0.07782 | -0.041199 | 0.17395 | 113.942 | -6.6925 | 6.2439 | -113.0676 | 6.4178 | 6.5506 | -112.5092 | -0.27466 | 0.83313 | 0.17395 | 6.3766 | 6.5918 | 7.0175 | 6.459 | 6.4178 | 120.3598 | 6.4957 | -0.27466 | 6.459 | 6.4178 | 6.4957 | 7.0175 | 120.3598 | -113.2828 | -119.8013
3049.875 | 120.5063 | -5.983 | 114.1205 | 0.017319 | -0.002555 | 0.0058405 | 0.06138 | 0.037157 | 0.031315 | 0.17186 | 0.013733 | 0.018311 | -0.13733 | 0.15106 | 0.54016 | 0.1236 | -0.15106 | 0.23346 | 114.5096 | -6.1523 | 5.8456 | -114.1022 | 5.9967 | 6.134 | -113.5803 | -0.16937 | 0.3891 | 0.15106 | 5.8319 | 6.2164 | 6.5231 | 6.0013 | 5.9967 | 120.4926 | 6.1066 | -0.16937 | 6.0013 | 5.9967 | 6.1066 | 6.5231 | 120.4926 | -114.2578 | -120.2728
3051.5781 | 119.9799 | -6.4407 | 113.9053 | 0.00206 | 8.578e-06 | 0.0045587 | 0.12547 | 0.037798 | 0.02982 | 0.22911 | -0.054932 | 0.045776 | -0.1831 | 0.073242 | 0.48981 | 0.036621 | 0.013733 | 0.15106 | 114.093 | -6.633 | 6.2576 | -113.8596 | 6.3858 | 6.514 | -113.4155 | -0.19226 | 0.18768 | 0.12817 | 6.4545 | 6.5918 | 6.9305 | 6.4865 | 6.3858 | 120.5338 | 6.4774 | -0.19226 | 6.4865 | 6.3858 | 6.4774 | 6.9305 | 120.5338 | -114.0884 | -120.5383
3053.2969 | 120.5933 | -4.7012 | 115.2054 | 0.024948 | 0.001504 | 0.0081903 | 0.14918 | 0.040362 | 0.030247 | 0.18788 | -0.041199 | 0.041199 | -0.17395 | 0.07782 | 0.6546 | 0.045776 | -0.041199 | 0.091553 | 115.654 | -5.0949 | 4.5273 | -115.1642 | 4.66 | 4.7791 | -114.5508 | -0.39368 | 0.44861 | 0.13275 | 4.66 | 4.7928 | 5.3558 | 4.7424 | 4.66 | 120.3552 | 4.747 | -0.39368 | 4.7424 | 4.66 | 4.747 | 5.3558 | 120.3552 | -115.3793 | -120.3003
3055.0156 | 120.6253 | -38.7589 | 81.3812 | 0.017319 | -0.0044776 | 0.0069085 | 0.75501 | 0.03139 | 0.027683 | 0.86036 | 0 | 0.022888 | -0.1236 | 0.14648 | 0.72784 | 0.11444 | -0.12817 | 0.24261 | 107.9819 | -12.9044 | 38.6353 | -81.3583 | 38.7589 | 38.9053 | -80.6534 | 25.8545 | 26.6006 | 0.1236 | 38.6307 | 39.0015 | 39.4867 | 38.7817 | 38.7589 | 146.7407 | 38.8733 | 25.8545 | 38.7817 | 38.7589 | 38.8733 | 39.4867 | 146.7407 | -81.5048 | -94.2856
3056.7344 | 120.5978 | -3.4607 | 117.009 | 0.017319 | -0.0017004 | 0.0096857 | 0.17738 | 0.039935 | 0.030033 | 0.29255 | -0.022888 | 0.032043 | -0.1831 | 0.091553 | 0.68207 | 0.041199 | -0.036621 | 0.13275 | 117.4026 | -3.447 | 3.2776 | -116.9769 | 3.4378 | 3.5522 | -116.3269 | 0.013733 | 0.39368 | 0.16022 | 3.4241 | 3.5934 | 4.1428 | 3.4927 | 3.4378 | 120.8633 | 3.5019 | 0.013733 | 3.4927 | 3.4378 | 3.5019 | 4.1428 | 120.8633 | -117.1921 | -120.4559
3058.4844 | 120.0623 | -119.6457 | 0.064087 | 0.0096895 | -0.0014868 | 0.0096857 | 0.089792 | -0.019666 | -0.029354 | 0.03001 | -0.004578 | 0.073242 | -0.14191 | 0.07782 | -0.027466 | 0.091553 | -0.032043 | 0.15564 | 0.20142 | -119.957 | 119.5038 | 0.009155 | 119.6411 | 119.7235 | -0.091553 | -0.31128 | 0.13733 | 0.13733 | 119.6136 | 119.8013 | 119.6182 | 119.7189 | 119.6411 | 119.8471 | 119.7372 | -0.31128 | 119.7189 | 119.6411 | 119.7372 | 119.6182 | 119.8471 | -0.20599 | -120.0211
3060.1875 | 120.4422 | -120.0531 | 0.064087 | 0.00206 | -0.0012732 | 0.0081903 | 0.090006 | -0.025007 | -0.032131 | 0.02766 | -0.013733 | 0.086975 | -0.14191 | 0.086975 | -0.027466 | 0.09613 | -0.027466 | 0.15106 | 0.20142 | -120.369 | 119.9112 | 0.022888 | 120.0394 | 120.1401 | -0.091553 | -0.31586 | 0.13733 | 0.12817 | 120.0256 | 120.2042 | 120.0256 | 120.1401 | 120.0394 | 120.2545 | 120.1492 | -0.31586 | 120.1401 | 120.0394 | 120.1492 | 120.0256 | 120.2545 | -0.20599 | -120.433
3061.9375 | 120.5246 | -120.2042 | 0.10071 | 0.0096895 | -0.0023412 | 0.0073359 | 0.10539 | -0.025648 | -0.030208 | 0.04475 | 0.10071 | 0.036621 | -0.086975 | 0.16937 | 0.027466 | 0.21057 | -0.17395 | 0.27008 | 0.17853 | -120.4788 | 120.1172 | -0.064087 | 120.3049 | 120.3735 | -0.073242 | -0.27466 | 0.07782 | 0.18768 | 120.0302 | 120.4742 | 120.2316 | 120.2408 | 120.3049 | 120.3827 | 120.4147 | -0.27466 | 120.2408 | 120.3049 | 120.4147 | 120.2316 | 120.3827 | -0.18768 | -120.5795
3063.6875 | 120.4193 | -120.195 | 0.21515 | -0.0055695 | -0.0012732 | 0.0079767 | 0.57899 | -0.026716 | -0.030849 | 0.56471 | 0.11902 | 0.050354 | -0.07782 | 0.23804 | -1.0208 | 0.21973 | -0.091553 | 0.37079 | 0.28381 | -120.2866 | 120.1172 | -0.16479 | 120.314 | 120.433 | -1.236 | -0.091553 | 0.068664 | 0.19684 | 120.1035 | 120.5658 | 119.1742 | 120.2454 | 120.314 | 120.4788 | 120.4147 | -0.091553 | 120.2454 | 120.314 | 120.4147 | 119.1742 | 120.4788 | -0.29297 | -120.5017
3065.4062 | 119.9158 | -119.4122 | 0.10529 | 0.017319 | -0.002555 | 0.0064813 | 0.18849 | -0.02522 | -0.02914 | 0.11119 | 0.059509 | 0.068665 | -0.10071 | 0.16479 | 0.07782 | 0.1831 | -0.10986 | 0.27466 | 0.17395 | -119.7556 | 119.3115 | -0.036621 | 119.4717 | 119.577 | -0.027466 | -0.34332 | 0.068664 | 0.16022 | 119.3024 | 119.6869 | 119.4901 | 119.4809 | 119.4717 | 119.5862 | 119.5953 | -0.34332 | 119.4809 | 119.4717 | 119.5953 | 119.4901 | 119.5862 | -0.20599 | -119.8608
3067.1094 | 120.0714 | -119.6503 | 0.20142 | 0.0096895 | -0.004264 | 0.0047723 | 0.46534 | -0.026716 | -0.031277 | 0.39338 | 0.059509 | 0.050354 | -0.09613 | 0.19684 | 0.07782 | 0.19684 | -0.10986 | 0.29297 | 0.22888 | -119.9432 | 119.5541 | -0.15106 | 119.7098 | 119.8471 | -0.1236 | -0.29297 | 0.027466 | 0.15564 | 119.5404 | 119.9432 | 119.7281 | 119.7006 | 119.7098 | 119.8792 | 119.8471 | -0.29297 | 119.7006 | 119.7098 | 119.8471 | 119.7281 | 119.8792 | -0.29755 | -120.1447
3068.875 | 119.8975 | -119.4901 | 0.068665 | 0.017319 | -0.0017004 | 0.0056269 | 0.085092 | -0.021802 | -0.031704 | 0.023815 | 0.036621 | 0.068665 | -0.11902 | 0.12817 | 0.018311 | 0.11444 | -0.10071 | 0.19684 | 0.17853 | -119.7876 | 119.371 | 0 | 119.5267 | 119.6182 | -0.050354 | -0.29755 | 0.10986 | 0.15564 | 119.3893 | 119.6869 | 119.5084 | 119.5587 | 119.5267 | 119.6686 | 119.6045 | -0.29755 | 119.5587 | 119.5267 | 119.6045 | 119.5084 | 119.6686 | -0.18768 | -119.8563
3070.5781 | 120.2911 | -119.9341 | 0.091553 | 0.017319 | -0.0021276 | 0.0002863 | 0.23036 | -0.026929 | -0.029354 | 0.13661 | 0.068665 | 0.059509 | -0.09613 | 0.19226 | 0.068665 | 0.17853 | -0.11902 | 0.28381 | 0.17395 | -120.2042 | 119.838 | -0.032044 | 120.0027 | 120.1263 | -0.022888 | -0.27008 | 0.082397 | 0.16479 | 119.8151 | 120.2179 | 120.0027 | 119.9936 | 120.0027 | 120.108 | 120.1126 | -0.27008 | 119.9936 | 120.0027 | 120.1126 | 120.0027 | 120.108 | -0.18768 | -120.2957
3072.2812 | 120.2866 | -120.0485 | 0.15106 | 0.0096895 | -0.001914 | 0.0084039 | 0.19596 | -0.027784 | -0.029995 | 0.17805 | 0.091553 | 0.054932 | -0.11902 | 0.19226 | 0 | 0.14648 | -0.036621 | 0.27466 | 0.20599 | -120.3049 | 119.9295 | -0.09613 | 120.1401 | 120.2408 | -0.15106 | -0.25635 | 0.054932 | 0.21057 | 120.0119 | 120.3232 | 120.0485 | 120.1035 | 120.1401 | 120.2545 | 120.195 | -0.25635 | 120.1035 | 120.1401 | 120.195 | 120.0485 | 120.2545 | -0.27008 | -120.4559
3074 | 120.3781 | -120.0668 | 0.059509 | 0.00206 | -0.0010596 | 0.0043451 | 0.10389 | -0.026075 | -0.031917 | 0.033 | -0.009155 | 0.091553 | -0.16022 | 0.082397 | -0.050354 | 0.050354 | 0.013733 | 0.11902 | 0.19684 | -120.3964 | 119.9066 | 0.032044 | 120.0577 | 120.1492 | -0.10986 | -0.32959 | 0.13733 | 0.15106 | 120.0806 | 120.1859 | 120.0165 | 120.1584 | 120.0577 | 120.2637 | 120.1172 | -0.32959 | 120.1584 | 120.0577 | 120.1172 | 120.0165 | 120.2637 | -0.21973 | -120.4559
3075.7344 | 120.4285 | -119.8837 | 0.27924 | 0.00206 | -0.00020502 | 0.010326 | 0.86973 | -0.025648 | -0.032772 | 0.81037 | -0.004578 | 0.082397 | -0.14191 | 0.091553 | -0.76904 | 0.059509 | 0.004578 | 0.14648 | 0.33417 | -120.1263 | 119.7418 | -0.19684 | 119.8792 | 119.9753 | -1.0483 | -0.24262 | 0.054931 | 0.13733 | 119.8883 | 120.0302 | 119.1147 | 119.9661 | 119.8792 | 120.2179 | 119.9432 | -0.24262 | 119.9661 | 119.8792 | 119.9432 | 119.1147 | 120.2179 | -0.42114 | -120.4056
3077.6562 | 119.165 | -118.6615 | 0.19684 | 0.00206 | 0.0012902 | 0.0043451 | 0.81867 | -0.022657 | -0.030849 | 0.65593 | 0.036621 | 0.082397 | -0.11902 | 0.13733 | -0.39368 | 0.13733 | -0.10986 | 0.20142 | 0.29755 | -118.9362 | 118.5425 | -0.11444 | 118.6981 | 118.7988 | -0.59052 | -0.27466 | 0.10071 | 0.15564 | 118.5516 | 118.8629 | 118.2678 | 118.7439 | 118.6981 | 118.959 | 118.7988 | -0.27466 | 118.7439 | 118.6981 | 118.7988 | 118.2678 | 118.959 | -0.31586 | -119.133
3079.5 | 120.3415 | -120.0943 | 0.091553 | -0.0055695 | -0.0040502 | 0.0026361 | 0.078043 | -0.027998 | -0.030849 | 0.020183 | 0.036621 | 0.068665 | -0.10986 | 0.11444 | 0.009155 | 0.09613 | 0.027466 | 0.20142 | 0.17853 | -120.4056 | 119.9844 | -0.022888 | 120.1309 | 120.2087 | -0.082398 | -0.31128 | 0.086975 | 0.14648 | 120.1218 | 120.2957 | 120.1035 | 120.163 | 120.1309 | 120.2728 | 120.1904 | -0.31128 | 120.163 | 120.1309 | 120.1904 | 120.1035 | 120.2728 | -0.20142 | -120.4971
3081.2344 | 120.488 | -120.1538 | 0.07782 | 0.017319 | -0.0021276 | 0.0079767 | 0.081888 | -0.023725 | -0.031917 | 0.018688 | -0.004578 | 0.082397 | -0.13275 | 0.086975 | -0.027466 | 0.059509 | -0.018311 | 0.12817 | 0.17853 | -120.4834 | 120.0211 | 0.004577 | 120.1492 | 120.2408 | -0.10529 | -0.32959 | 0.10071 | 0.12817 | 120.1355 | 120.282 | 120.1263 | 120.2362 | 120.1492 | 120.3323 | 120.2133 | -0.32959 | 120.2362 | 120.1492 | 120.2133 | 120.1263 | 120.3323 | -0.21057 | -120.5612
3083.0156 | 120.5109 | -120.2179 | 0.091553 | 0.0096895 | -0.0017004 | 0.0069085 | 0.084238 | -0.024152 | -0.031063 | 0.019969 | 0.11444 | 0.045776 | -0.10986 | 0.21057 | 0.10986 | 0.21057 | -0.21973 | 0.27008 | 0.13275 | -120.52 | 120.108 | -0.045777 | 120.3323 | 120.4285 | 0.01831 | -0.30212 | 0.041198 | 0.2243 | 119.9982 | 120.488 | 120.3278 | 120.2637 | 120.3323 | 120.3506 | 120.4285 | -0.30212 | 120.2637 | 120.3323 | 120.4285 | 120.3278 | 120.3506 | -0.20142 | -120.6116
3084.8125 | 120.4376 | -120.2957 | 0.10529 | 0.00206 | -0.0021276 | 0.0075495 | 0.08552 | -0.028425 | -0.033199 | 0.021465 | -0.018311 | 0.073242 | -0.13275 | 0.086975 | 0 | 0.082397 | 0.036621 | 0.17395 | 0.1831 | -120.5841 | 120.163 | -0.032044 | 120.2774 | 120.3827 | -0.10529 | -0.28839 | 0.077819 | 0.11444 | 120.3323 | 120.4697 | 120.2957 | 120.369 | 120.2774 | 120.4788 | 120.3781 | -0.28839 | 120.369 | 120.2774 | 120.3781 | 120.2957 | 120.4788 | -0.23804 | -120.6894
3086.625 | 120.5475 | -120.3186 | 0.07782 | 0.00206 | -0.00020502 | 0.0073359 | 0.091501 | -0.026075 | -0.035122 | 0.023601 | 0.009155 | 0.091553 | -0.1236 | 0.086975 | -0.027466 | 0.054932 | 0.013733 | 0.13275 | 0.19226 | -120.607 | 120.195 | 0.013733 | 120.3278 | 120.4056 | -0.10529 | -0.28839 | 0.11444 | 0.13275 | 120.3323 | 120.4514 | 120.2911 | 120.4102 | 120.3278 | 120.5109 | 120.3735 | -0.28839 | 120.4102 | 120.3278 | 120.3735 | 120.2911 | 120.5109 | -0.20142 | -120.6848
3088.3438 | 120.6299 | -120.3278 | 0.050354 | 0.0096895 | 0.0019312 | 0.0019953 | 0.093851 | -0.026929 | -0.031277 | 0.032573 | -0.018311 | 0.082397 | -0.13275 | 0.073242 | -0.022888 | 0.073242 | -0.013733 | 0.13733 | 0.16937 | -120.6253 | 120.195 | 0.032043 | 120.3094 | 120.401 | -0.073242 | -0.29755 | 0.11902 | 0.11444 | 120.314 | 120.4651 | 120.3049 | 120.4102 | 120.3094 | 120.4971 | 120.401 | -0.29755 | 120.4102 | 120.3094 | 120.401 | 120.3049 | 120.4971 | -0.18311 | -120.6757
3090.125 | 120.5841 | -120.3918 | 0.09613 | 0.0096895 | 8.578e-06 | 0.0047723 | 0.078043 | -0.02522 | -0.030636 | 0.016338 | -0.004578 | 0.09613 | -0.1236 | 0.091553 | -0.004578 | 0.059509 | 0.041199 | 0.16479 | 0.19226 | -120.7306 | 120.2682 | 0 | 120.3873 | 120.4834 | -0.10071 | -0.33875 | 0.096131 | 0.11902 | 120.433 | 120.5566 | 120.3873 | 120.488 | 120.3873 | 120.5841 | 120.4514 | -0.33875 | 120.488 | 120.3873 | 120.4514 | 120.3873 | 120.5841 | -0.21973 | -120.8267
3091.9062 | 120.6162 | -120.433 | 0.068665 | 0.00206 | -0.0023412 | 0.0081903 | 0.076547 | -0.028425 | -0.031063 | 0.016338 | 0.091553 | 0.059509 | -0.10529 | 0.21515 | 0.11444 | 0.21973 | -0.15106 | 0.31128 | 0.14191 | -120.6802 | 120.3278 | -0.009156 | 120.5246 | 120.6482 | 0.045776 | -0.24719 | 0.073242 | 0.19684 | 120.282 | 120.7443 | 120.5475 | 120.4926 | 120.5246 | 120.575 | 120.6528 | -0.24719 | 120.4926 | 120.5246 | 120.6528 | 120.5475 | 120.575 | -0.17395 | -120.7489
3093.6406 | 120.5841 | -120.4422 | 0.07782 | 0.0096895 | 0.00064938 | 0.0092585 | 0.087229 | -0.023725 | -0.035335 | 0.020183 | 0.036621 | 0.068665 | -0.13733 | 0.12817 | 0 | 0.10071 | -0.036621 | 0.16479 | 0.16479 | -120.7306 | 120.3049 | -0.009155 | 120.4788 | 120.5704 | -0.07782 | -0.28839 | 0.086975 | 0.17395 | 120.4056 | 120.607 | 120.4422 | 120.5109 | 120.4788 | 120.607 | 120.5429 | -0.28839 | 120.5109 | 120.4788 | 120.5429 | 120.4422 | 120.607 | -0.21515 | -120.8084
3095.3906 | 120.6024 | -120.488 | 0.10529 | 0.0096895 | 0.0017176 | 0.010967 | 0.082315 | -0.02458 | -0.033413 | 0.015483 | 0.07782 | 0.10071 | -0.13275 | 0.15106 | 0.041199 | 0.13275 | -0.045776 | 0.21057 | 0.17853 | -120.7764 | 120.3552 | -0.004578 | 120.5658 | 120.639 | -0.064087 | -0.28839 | 0.073242 | 0.21057 | 120.4422 | 120.6985 | 120.5292 | 120.5887 | 120.5658 | 120.6665 | 120.6207 | -0.28839 | 120.5887 | 120.5658 | 120.6207 | 120.5292 | 120.6665 | -0.23804 | -120.8817
3097.1875 | 120.6162 | -120.5154 | 0.10986 | 0.0096895 | -0.0034094 | 0.0077631 | 0.078043 | -0.028638 | -0.032558 | 0.017406 | 0.10529 | 0.036621 | -0.091553 | 0.2243 | 0.16022 | 0.24261 | -0.15106 | 0.31586 | 0.13733 | -120.7718 | 120.4239 | -0.073242 | 120.6207 | 120.7397 | 0.050354 | -0.25635 | 0.027466 | 0.19684 | 120.3644 | 120.8313 | 120.6757 | 120.5521 | 120.6207 | 120.6528 | 120.7581 | -0.25635 | 120.5521 | 120.6207 | 120.7581 | 120.6757 | 120.6528 | -0.20142 | -120.8817
3098.9688 | 120.7535 | -120.4834 | 0.082397 | 0.017319 | -0.0029822 | 0.0096857 | 0.079111 | -0.027143 | -0.03149 | 0.017833 | 0.07782 | 0.054932 | -0.086975 | 0.15106 | 0.073242 | 0.17395 | -0.13733 | 0.23804 | 0.14648 | -120.8176 | 120.3964 | -0.027465 | 120.5612 | 120.6345 | -0.009155 | -0.33417 | 0.064087 | 0.16479 | 120.3461 | 120.7214 | 120.5566 | 120.5383 | 120.5612 | 120.6299 | 120.6573 | -0.33417 | 120.5383 | 120.5612 | 120.6573 | 120.5566 | 120.6299 | -0.16937 | -120.9
3100.7031 | 120.7993 | -120.5109 | 0.073242 | 0.0096895 | -0.0029822 | 0.0056269 | 0.08082 | -0.028425 | -0.031277 | 0.019756 | 0.036621 | 0.050354 | -0.10071 | 0.14191 | 0.054932 | 0.17395 | -0.086975 | 0.24719 | 0.15564 | -120.8267 | 120.4102 | -0.022888 | 120.5475 | 120.6528 | -0.01831 | -0.31586 | 0.082398 | 0.13733 | 120.4239 | 120.7581 | 120.5658 | 120.5612 | 120.5475 | 120.6665 | 120.6848 | -0.31586 | 120.5612 | 120.5475 | 120.6848 | 120.5658 | 120.6665 | -0.17395 | -120.9
3102.5156 | 120.8084 | -120.5063 | 0.064087 | -0.0055695 | -0.0023412 | 0.0092585 | 0.084238 | -0.026716 | -0.03149 | 0.020183 | 0.064087 | 0.064087 | -0.086975 | 0.15564 | 0.068665 | 0.16022 | -0.11444 | 0.23804 | 0.13733 | -120.8405 | 120.4193 | 0 | 120.5704 | 120.6619 | 0.004578 | -0.33417 | 0.073242 | 0.15106 | 120.3918 | 120.7443 | 120.575 | 120.5704 | 120.5704 | 120.6436 | 120.6665 | -0.33417 | 120.5704 | 120.5704 | 120.6665 | 120.575 | 120.6436 | -0.15106 | -120.9045
3104.25 | 120.7214 | -120.575 | 0.10529 | 0.017319 | -0.0038366 | -0.0003547 | 0.083811 | -0.027357 | -0.032558 | 0.021038 | 0.10529 | 0.054932 | -0.086975 | 0.21973 | 0.10529 | 0.19226 | -0.086975 | 0.32044 | 0.14648 | -120.8679 | 120.488 | -0.050354 | 120.6802 | 120.7947 | 0 | -0.29297 | 0.041198 | 0.19226 | 120.488 | 120.8954 | 120.6802 | 120.6299 | 120.6802 | 120.7214 | 120.7672 | -0.29297 | 120.6299 | 120.6802 | 120.7672 | 120.6802 | 120.7214 | -0.19226 | -120.9732
3105.9688 | 120.7031 | -120.5933 | 0.09613 | 0.0096895 | 0.0040674 | 0.0094721 | 0.087656 | -0.025007 | -0.034694 | 0.041759 | 0.054932 | 0.086975 | -0.11444 | 0.16479 | 0.041199 | 0.1236 | -0.045776 | 0.2243 | 0.16937 | -120.9091 | 120.4788 | -0.009155 | 120.6482 | 120.7581 | -0.054931 | -0.31586 | 0.073243 | 0.16937 | 120.5475 | 120.8176 | 120.6345 | 120.6802 | 120.6482 | 120.7626 | 120.7169 | -0.31586 | 120.6802 | 120.6482 | 120.7169 | 120.6345 | 120.7626 | -0.21057 | -121.0052
3107.75 | 120.8633 | -120.5658 | 0.07782 | 0.00206 | 0.00022218 | 0.0086175 | 0.091928 | -0.025648 | -0.030636 | 0.02766 | 0.027466 | 0.07782 | -0.13275 | 0.13275 | 0.036621 | 0.11902 | -0.09613 | 0.1831 | 0.16022 | -120.9 | 120.433 | 0 | 120.5933 | 120.6985 | -0.041199 | -0.33417 | 0.082397 | 0.16022 | 120.4697 | 120.7489 | 120.6024 | 120.6436 | 120.5933 | 120.726 | 120.6848 | -0.33417 | 120.6436 | 120.5933 | 120.6848 | 120.6024 | 120.726 | -0.21057 | -120.9778
3109.5469 | 120.8084 | -120.6436 | 0.082397 | 0.0096895 | -0.0023412 | 0.0062677 | 0.087015 | -0.026502 | -0.031917 | 0.024028 | 0.045776 | 0.054932 | -0.11902 | 0.13733 | 0.041199 | 0.10529 | 0.004578 | 0.20599 | 0.1831 | -120.9229 | 120.5246 | -0.027465 | 120.6894 | 120.7809 | -0.041198 | -0.27924 | 0.10071 | 0.16479 | 120.6482 | 120.8496 | 120.6848 | 120.6985 | 120.6894 | 120.8267 | 120.7489 | -0.27924 | 120.6985 | 120.6894 | 120.7489 | 120.6848 | 120.8267 | -0.20142 | -121.0052
3111.2812 | 115.5579 | -77.8152 | 37.587 | 0.017319 | -0.00020502 | 0.0081903 | 6.9721 | -0.014539 | -0.022304 | 7.0123 | -0.013733 | 0.068665 | -0.15106 | 0.082397 | 0.2655 | 0.022888 | 0.009155 | -0.27008 | 25.7812 | -66.774 | 77.6642 | -37.5183 | 77.8015 | 77.8976 | -37.3215 | 11.0413 | -11.8057 | 0.13733 | 77.8244 | 77.5452 | 78.0807 | 77.8839 | 77.8015 | 103.5965 | 77.8381 | 11.0413 | 77.8839 | 77.8015 | 77.8381 | 78.0807 | 103.5965 | -37.738 | -104.361
3113.0781 | 120.6299 | -120.2728 | 0.082397 | 0.00206 | -0.003623 | 0.0090447 | 0.072702 | -0.025861 | -0.029995 | 0.017192 | 0.07782 | 0.054932 | -0.09613 | 0.17395 | 0.10529 | 0.21057 | -0.14191 | 0.29297 | 0.11444 | -120.6665 | 120.1767 | -0.027465 | 120.3506 | 120.4468 | 0.022889 | -0.39368 | 0.032044 | 0.17395 | 120.1309 | 120.5658 | 120.3781 | 120.3278 | 120.3506 | 120.3873 | 120.4834 | -0.39368 | 120.3278 | 120.3506 | 120.4834 | 120.3781 | 120.3873 | -0.17853 | -120.7489
3114.8125 | 120.726 | -120.4056 | 0.073242 | 0.0096895 | -0.0027686 | 0.0041315 | 0.08082 | -0.026929 | -0.029995 | 0.01826 | 0.059509 | 0.064087 | -0.086975 | 0.15564 | 0.068665 | 0.19684 | -0.17853 | 0.25177 | 0.13275 | -120.7397 | 120.3186 | -0.009155 | 120.4651 | 120.5612 | -0.004577 | -0.33417 | 0.059509 | 0.14648 | 120.2271 | 120.6573 | 120.4742 | 120.4697 | 120.4651 | 120.5383 | 120.6024 | -0.33417 | 120.4697 | 120.4651 | 120.6024 | 120.4742 | 120.5383 | -0.16022 | -120.813
3116.5938 | 120.7626 | -120.488 | 0.041199 | 0.00206 | -0.0017004 | 0.0043451 | 0.084024 | -0.02458 | -0.03149 | 0.020824 | 0.050354 | 0.064087 | -0.09613 | 0.17853 | 0.091553 | 0.17853 | -0.17853 | 0.24719 | 0.14191 | -120.8084 | 120.3918 | 0.022888 | 120.5383 | 120.6665 | 0.050354 | -0.32044 | 0.10071 | 0.14648 | 120.3094 | 120.7352 | 120.5795 | 120.5521 | 120.5383 | 120.6299 | 120.6665 | -0.32044 | 120.5521 | 120.5383 | 120.6665 | 120.5795 | 120.6299 | -0.13733 | -120.8496
3118.3906 | 120.7993 | -120.5566 | 0.082397 | -0.0055695 | -0.0021276 | 0.0049859 | 0.081461 | -0.025861 | -0.029781 | 0.022533 | 0.10529 | 0.045776 | -0.086975 | 0.21057 | 0.1236 | 0.21973 | -0.13733 | 0.29755 | 0.12817 | -120.8542 | 120.4697 | -0.036621 | 120.6619 | 120.7672 | 0.041199 | -0.29755 | 0.045777 | 0.19226 | 120.4193 | 120.8542 | 120.6802 | 120.6024 | 120.6619 | 120.6848 | 120.7764 | -0.29755 | 120.6024 | 120.6619 | 120.7764 | 120.6802 | 120.6848 | -0.16937 | -120.9366
3120.1875 | 120.8771 | -120.5612 | 0.059509 | 0.0096895 | -0.0017004 | 0.0073359 | 0.086588 | -0.027357 | -0.03149 | 0.021678 | -0.018311 | 0.091553 | -0.13733 | 0.082397 | -0.032043 | 0.073242 | -0.022888 | 0.13275 | 0.17853 | -120.9091 | 120.4239 | 0.032044 | 120.5429 | 120.6436 | -0.091552 | -0.3479 | 0.11902 | 0.11902 | 120.5383 | 120.694 | 120.5292 | 120.6528 | 120.5429 | 120.7397 | 120.6345 | -0.3479 | 120.6528 | 120.5429 | 120.6345 | 120.5292 | 120.7397 | -0.19684 | -120.9686
3121.9062 | 120.7718 | -120.6116 | 0.11902 | -0.0055695 | -0.00063242 | 0.011608 | 0.091928 | -0.026929 | -0.032985 | 0.032146 | 0.07782 | 0.050354 | -0.07782 | 0.17853 | 0.091553 | 0.15564 | -0.041199 | 0.27008 | 0.14648 | -120.9137 | 120.5338 | -0.068665 | 120.6894 | 120.7901 | -0.027466 | -0.30212 | 0.027465 | 0.15564 | 120.5704 | 120.8817 | 120.7031 | 120.6619 | 120.6894 | 120.7581 | 120.7672 | -0.30212 | 120.6619 | 120.6894 | 120.7672 | 120.7031 | 120.7581 | -0.19684 | -121.0327
3123.6875 | 120.7901 | -120.6665 | 0.11902 | 0.017319 | -0.002555 | 0.0043451 | 0.1605 | -0.026502 | -0.02914 | 0.10264 | 0.11444 | 0.050354 | -0.10071 | 0.2243 | 0.10529 | 0.19226 | -0.14191 | 0.31128 | 0.13275 | -120.9595 | 120.5658 | -0.068665 | 120.7809 | 120.8908 | -0.013733 | -0.29297 | 0.013732 | 0.21515 | 120.5246 | 120.9778 | 120.7718 | 120.7169 | 120.7809 | 120.7993 | 120.8588 | -0.29297 | 120.7169 | 120.7809 | 120.8588 | 120.7718 | 120.7993 | -0.21973 | -121.0785
3125.4688 | 120.2087 | -119.9615 | 0.068665 | 0.00206 | -0.00063242 | 0.0026361 | 0.072702 | -0.024152 | -0.030849 | 0.01292 | 0.10529 | 0.054932 | -0.10071 | 0.21515 | 0.12817 | 0.21515 | -0.16479 | -95.5399 | 0.10071 | -120.2728 | 119.8608 | -0.013733 | 120.0668 | 120.1767 | 0.059509 | -0.31128 | 0.032043 | 0.20599 | 119.7968 | 24.4217 | 120.0897 | 120.0165 | 120.0668 | 120.0623 | 120.1767 | -0.31128 | 120.0165 | 120.0668 | 120.1767 | 120.0897 | 120.0623 | -0.16937 | -120.3415
3127.2656 | 120.575 | -120.3232 | 0.091553 | 0.0096895 | -0.002555 | 0.0019953 | 0.080393 | -0.025434 | -0.032985 | 0.013347 | 0 | 0.09613 | -0.15106 | 0.11444 | 0 | 0.07782 | 0.036621 | -97.142 | 0.13733 | -120.6848 | 120.1721 | 0.004577 | 120.3232 | 120.4376 | -0.091553 | -0.36163 | 0.045776 | 0.15106 | 120.3598 | 23.1812 | 120.3232 | 120.4193 | 120.3232 | 120.4605 | 120.401 | -0.36163 | 120.4193 | 120.3232 | 120.401 | 120.3232 | 120.4605 | -0.24261 | -120.7764
3129.0469 | 120.6757 | -120.4422 | 0.082397 | 0.0096895 | -0.0023412 | 0.0056269 | 0.079325 | -0.025434 | -0.031704 | 0.014842 | -0.022888 | 0.082397 | -0.13733 | 0.10071 | -0.004578 | 0.064087 | 0.054932 | -101.4267 | 0.13733 | -120.7764 | 120.3049 | 0 | 120.4193 | 120.5429 | -0.086975 | -0.33417 | 0.054932 | 0.11444 | 120.4971 | 19.0155 | 120.4376 | 120.5246 | 120.4193 | 120.5795 | 120.5063 | -0.33417 | 120.5246 | 120.4193 | 120.5063 | 120.4376 | 120.5795 | -0.21973 | -120.8588
3130.7812 | 120.7993 | -120.488 | 0.054932 | 0.017319 | -0.0010596 | 0.0071221 | 0.084024 | -0.02522 | -0.031917 | 0.017406 | 0.004578 | 0.086975 | -0.13275 | 0.082397 | -0.018311 | 0.064087 | 0 | -104.1 | 0.14191 | -120.8084 | 120.3552 | 0.032043 | 120.4926 | 120.5704 | -0.073243 | -0.32044 | 0.086975 | 0.13733 | 120.488 | 16.3879 | 120.4697 | 120.575 | 120.4926 | 120.6299 | 120.5521 | -0.32044 | 120.575 | 120.4926 | 120.5521 | 120.4697 | 120.6299 | -0.18768 | -120.8633
3132.5781 | 120.7489 | -120.5658 | 0.059509 | 0.017319 | -0.001914 | 0.0045587 | 0.084024 | -0.02458 | -0.033626 | 0.016551 | 0.013733 | 0.086975 | -0.13275 | 0.10071 | -0.022888 | 0.068665 | 0 | -109.964 | 0.13733 | -120.8588 | 120.433 | 0.027466 | 120.5795 | 120.6665 | -0.082397 | -0.29297 | 0.07782 | 0.14648 | 120.5658 | 10.6018 | 120.5429 | 120.6528 | 120.5795 | 120.7031 | 120.6345 | -0.29297 | 120.6528 | 120.5795 | 120.6345 | 120.5429 | 120.7031 | -0.19226 | -120.9183
3134.375 | 120.8359 | -120.5658 | 0.059509 | 0.00206 | 0.00022218 | 0.0032769 | 0.089365 | -0.02458 | -0.028927 | 0.027873 | 0.073242 | 0.050354 | -0.10529 | 0.17395 | 0.082397 | 0.17853 | -0.15564 | -109.639 | 0.091553 | -120.8908 | 120.4605 | -0.009155 | 120.639 | 120.7397 | 0.022888 | -0.32501 | 0.032044 | 0.17853 | 120.4102 | 10.9268 | 120.6482 | 120.6162 | 120.639 | 120.6573 | 120.7443 | -0.32501 | 120.6162 | 120.639 | 120.7443 | 120.6482 | 120.6573 | -0.16479 | -120.9503
3136.1719 | 120.8221 | -120.5704 | 0.13733 | 0.00206 | -0.0034094 | 0.0054131 | 0.23057 | -0.026929 | -0.03149 | 0.17036 | 0.082397 | 0.027466 | -0.091553 | 0.21515 | 0.12817 | 0.21057 | -0.14648 | -112.4084 | 0.10529 | -120.8359 | 120.4788 | -0.10986 | 120.6528 | 120.7855 | -0.009155 | -0.2655 | -0.032043 | 0.17395 | 120.4239 | 8.1619 | 120.6985 | 120.5978 | 120.6528 | 120.6757 | 120.7809 | -0.2655 | 120.5978 | 120.6528 | 120.7809 | 120.6985 | 120.6757 | -0.22888 | -120.9732
3137.875 | 120.7672 | -120.6528 | 0.082397 | 0.017319 | -0.0017004 | 0.0047723 | 0.094492 | -0.023939 | -0.036617 | 0.025737 | 0.064087 | 0.068665 | -0.11444 | 0.13733 | 0.041199 | 0.1236 | -0.041199 | -0.6958 | 0.16937 | -120.9183 | 120.5383 | -0.013732 | 120.7169 | 120.7901 | -0.041198 | -0.2655 | 0.086976 | 0.17853 | 120.6116 | 119.957 | 120.694 | 120.7214 | 120.7169 | 120.8221 | 120.7764 | -0.2655 | 120.7214 | 120.7169 | 120.7764 | 120.694 | 120.8221 | -0.19684 | -121.0007
3139.6562 | 120.7993 | -120.5658 | 0.16022 | 0.0096895 | 0.00022218 | 0.0058405 | 0.38267 | -0.024152 | -0.035763 | 0.262 | 0.045776 | 0.086975 | -0.11902 | 0.15106 | 0.041199 | 0.10986 | -0.022888 | -6.6284 | 0.19226 | -120.8405 | 120.4468 | -0.073242 | 120.6116 | 120.7169 | -0.11902 | -0.27466 | 0.032044 | 0.16479 | 120.5429 | 113.9374 | 120.607 | 120.6528 | 120.6116 | 120.7581 | 120.6757 | -0.27466 | 120.6528 | 120.6116 | 120.6757 | 120.607 | 120.7581 | -0.27924 | -121.0007
3141.4531 | 120.8862 | -120.6573 | 0.11902 | 0.017319 | 0.00086298 | 0.0077631 | 0.20942 | -0.029279 | -0.031063 | 0.14408 | 0.07782 | 0.064087 | -0.10071 | 0.15106 | 0.068665 | 0.13275 | -0.032043 | -28.8666 | 0.16937 | -120.9412 | 120.5566 | -0.054932 | 120.7352 | 120.8084 | -0.050354 | -0.28381 | 0.050354 | 0.17853 | 120.6253 | 91.7908 | 120.726 | 120.7214 | 120.7352 | 120.8267 | 120.7901 | -0.28381 | 120.7214 | 120.7352 | 120.7901 | 120.726 | 120.8267 | -0.21973 | -121.0602
3143.2344 | 120.845 | -120.7169 | 0.10986 | 0.0096895 | -0.0023412 | 0.0060541 | 0.26774 | -0.026929 | -0.032772 | 0.20198 | 0.10986 | 0.036621 | -0.07782 | 0.21515 | 0.11444 | 0.21973 | -0.1236 | -118.9865 | 0.1236 | -120.932 | 120.639 | -0.073242 | 120.8267 | 120.932 | 0.004578 | -0.21515 | 0.013733 | 0.18768 | 120.5933 | 1.7303 | 120.8313 | 120.7535 | 120.8267 | 120.8405 | 120.9366 | -0.21515 | 120.7535 | 120.8267 | 120.9366 | 120.8313 | 120.8405 | -0.18768 | -121.0419
3145.0156 | 120.6116 | -120.2774 | 0.050354 | 0.0096895 | 0.00043578 | 0.0069085 | 0.069925 | -0.023725 | -0.030636 | 0.0092883 | 0.082397 | 0.050354 | -0.09613 | 0.13733 | 0.059509 | 0.16479 | -0.11444 | 0.13275 | 0.13733 | -120.607 | 120.1813 | 0 | 120.3598 | 120.4147 | 0.009155 | -0.32959 | 0.086975 | 0.17853 | 120.163 | 120.4102 | 120.3369 | 120.3278 | 120.3598 | 120.4147 | 120.4422 | -0.32959 | 120.3278 | 120.3598 | 120.4422 | 120.3369 | 120.4147 | -0.14648 | -120.6573
3146.8125 | 120.8084 | -120.5566 | 0.064087 | 0.0096895 | -0.0017004 | 0.0069085 | 0.078043 | -0.026716 | -0.032345 | 0.014415 | 0.10986 | 0.027466 | -0.082397 | 0.19684 | 0.10529 | 0.19684 | -0.19226 | 0.23346 | 0.11902 | -120.8588 | 120.4742 | -0.036621 | 120.6665 | 120.7535 | 0.041199 | -0.30212 | 0.054932 | 0.19226 | 120.3644 | 120.7901 | 120.6619 | 120.5841 | 120.6665 | 120.6757 | 120.7535 | -0.30212 | 120.5841 | 120.6665 | 120.7535 | 120.6619 | 120.6757 | -0.14648 | -120.9229
3148.5469 | 120.7993 | -120.6573 | 0.082397 | 0.0096895 | 8.578e-06 | 0.0024225 | 0.090647 | -0.023939 | -0.030636 | 0.027873 | 0.10071 | 0.041199 | -0.10529 | 0.24261 | 0.12817 | 0.23346 | -0.16022 | -120.1401 | 0.10071 | -120.9045 | 120.5521 | -0.041198 | 120.7581 | 120.9 | 0.045777 | -0.24719 | 0.018311 | 0.20599 | 120.4971 | 0.51727 | 120.7855 | 120.6985 | 120.7581 | 120.7581 | 120.8908 | -0.24719 | 120.6985 | 120.7581 | 120.8908 | 120.7855 | 120.7581 | -0.18768 | -120.9869
3150.3438 | 120.8633 | -120.6757 | 0.10071 | 0.017319 | -0.0012732 | 0.0077631 | 0.11158 | -0.027784 | -0.032985 | 0.045391 | 0.050354 | 0.068665 | -0.10986 | 0.13733 | 0.032043 | 0.10071 | 0.018311 | -116.6656 | 0.14191 | -120.9869 | 120.5658 | -0.032043 | 120.726 | 120.813 | -0.068665 | -0.31128 | 0.041199 | 0.16022 | 120.694 | 4.01 | 120.7077 | 120.7443 | 120.726 | 120.8176 | 120.7764 | -0.31128 | 120.7443 | 120.726 | 120.7764 | 120.7077 | 120.8176 | -0.21057 | -121.0876
3152.125 | 120.8588 | -120.7169 | 0.10529 | 0.017319 | -0.0023412 | 0.0081903 | 0.084879 | -0.026502 | -0.033199 | 0.01527 | 0.068665 | 0.082397 | -0.14191 | 0.14191 | 0.036621 | 0.10071 | -0.036621 | -6.8298 | 0.15564 | -121.0236 | 120.575 | -0.022889 | 120.7855 | 120.8588 | -0.068665 | -0.3067 | 0.050354 | 0.21057 | 120.6802 | 113.887 | 120.7535 | 120.7993 | 120.7855 | 120.8725 | 120.8176 | -0.3067 | 120.7993 | 120.7855 | 120.8176 | 120.7535 | 120.8725 | -0.24719 | -121.1288
3153.8438 | 120.8633 | -120.7077 | 0.086975 | 0.017319 | -0.00063242 | 0.0054131 | 0.085733 | -0.025007 | -0.032131 | 0.018901 | 0.050354 | 0.064087 | -0.14191 | 0.14648 | 0.022888 | 0.10986 | -0.041199 | -22.6273 | 0.14191 | -121.0556 | 120.5658 | -0.022888 | 120.7581 | 120.8542 | -0.064087 | -0.3479 | 0.054932 | 0.19226 | 120.6665 | 98.0804 | 120.7306 | 120.7718 | 120.7581 | 120.8496 | 120.8176 | -0.3479 | 120.7718 | 120.7581 | 120.8176 | 120.7306 | 120.8496 | -0.22888 | -121.1426
3155.625 | 121.0098 | -120.7535 | 0.064087 | 0.0096895 | -0.001914 | 0.0077631 | 0.080179 | -0.02522 | -0.030208 | 0.01762 | 0.082397 | 0.068665 | -0.07782 | 0.16937 | 0.073242 | 0.17395 | -0.14648 | -6.7978 | 0.11444 | -121.0831 | 120.6757 | 0.004578 | 120.8359 | 120.9229 | 0.009155 | -0.32959 | 0.050354 | 0.16022 | 120.607 | 113.9557 | 120.8267 | 120.8221 | 120.8359 | 120.8679 | 120.9274 | -0.32959 | 120.8221 | 120.8359 | 120.9274 | 120.8267 | 120.8679 | -0.14191 | -121.1472
3157.4375 | 120.9183 | -120.7764 | 0.091553 | 0.017319 | 0.0017176 | 0.0064813 | 0.10688 | -0.025434 | -0.032345 | 0.029369 | 0.041199 | 0.082397 | -0.11902 | 0.12817 | 0.032043 | 0.091553 | -0.027466 | -120.5475 | 0.10529 | -121.0876 | 120.6573 | -0.009156 | 120.8176 | 120.9045 | -0.05951 | -0.31128 | 0.013733 | 0.16022 | 120.7489 | 0.22888 | 120.8084 | 120.8588 | 120.8176 | 120.8817 | 120.8679 | -0.31128 | 120.8588 | 120.8176 | 120.8679 | 120.8084 | 120.8817 | -0.21057 | -121.1792
3159.1719 | 120.9183 | -120.6207 | 0.27466 | 0.00206 | 8.578e-06 | 0.0094721 | 0.6121 | -0.025007 | -0.034054 | 0.54954 | 0.027466 | 0.086975 | -0.10529 | 0.10986 | 0.018311 | 0.082397 | -0.009155 | -117.9245 | 0.19684 | -120.8954 | 120.5154 | -0.18768 | 120.6482 | 120.7306 | -0.25635 | -0.27466 | -0.07782 | 0.13275 | 120.6116 | 2.6962 | 120.639 | 120.7077 | 120.6482 | 120.8176 | 120.7031 | -0.27466 | 120.7077 | 120.6482 | 120.7031 | 120.639 | 120.8176 | -0.37994 | -121.17
3160.9531 | 121.138 | -120.7581 | 0.064087 | 0.017319 | -0.0023412 | 0.0047723 | 0.10966 | -0.027357 | -0.032131 | 0.040477 | 0.032043 | 0.045776 | -0.10529 | 0.14191 | 0.073242 | 0.16022 | -0.10986 | -120.5246 | 0.086975 | -121.0785 | 120.6528 | -0.018311 | 120.7901 | 120.9 | 0.009155 | -0.32043 | 0.022888 | 0.13733 | 120.6482 | 0.23346 | 120.8313 | 120.8038 | 120.7901 | 120.845 | 120.9183 | -0.32043 | 120.8038 | 120.7901 | 120.9183 | 120.8313 | 120.845 | -0.16937 | -121.1426
3162.6875 | 120.9229 | -120.6619 | 0.21515 | 0.0096895 | -0.00084602 | 0.0043451 | 0.60121 | -0.027357 | -0.031063 | 0.52775 | -0.027466 | 0.082397 | -0.13733 | 0.082397 | -0.009155 | 0.059509 | 0.064087 | -65.3458 | 0.21973 | -120.9778 | 120.5246 | -0.13275 | 120.6345 | 120.7443 | -0.2243 | -0.31586 | 0.004578 | 0.10986 | 120.726 | 55.3162 | 120.6528 | 120.7443 | 120.6345 | 120.8817 | 120.7214 | -0.31586 | 120.7443 | 120.6345 | 120.7214 | 120.6528 | 120.8817 | -0.35248 | -121.1929
3164.4844 | 121.0648 | -120.7031 | 0.073242 | -0.0055695 | -0.0031958 | 0.0077631 | 0.42646 | -0.026929 | -0.030208 | 0.3701 | 0.09613 | 0.041199 | -0.086975 | 0.16479 | 0.10529 | 0.19226 | -0.19684 | -11.1786 | 0.16022 | -121.0464 | 120.6162 | -0.032043 | 120.7993 | 120.8679 | 0.032044 | -0.34332 | 0.086975 | 0.1831 | 120.5063 | 109.5245 | 120.8084 | 120.7443 | 120.7993 | 120.8633 | 120.8954 | -0.34332 | 120.7443 | 120.7993 | 120.8954 | 120.8084 | 120.8633 | -0.16022 | -121.1197
3166.2188 | 121.0144 | -120.8542 | 0.10529 | 0.00206 | -0.0031958 | 0.0092585 | 0.10325 | -0.028211 | -0.032131 | 0.033214 | 0.10529 | 0.036621 | -0.09613 | 0.20599 | 0.10986 | 0.20599 | -0.13733 | -1.7944 | 0.1236 | -121.1243 | 120.7581 | -0.068665 | 120.9595 | 121.0602 | 0.004577 | -0.27008 | 0.01831 | 0.20142 | 120.7169 | 119.0598 | 120.9641 | 120.8908 | 120.9595 | 120.9778 | 121.0602 | -0.27008 | 120.8908 | 120.9595 | 121.0602 | 120.9641 | 120.9778 | -0.20142 | -121.2296
3168.0156 | 120.8725 | -120.0211 | 0.073242 | 0.00206 | 0.00086298 | 0.0077631 | 0.063944 | -0.025648 | -0.033626 | 0.22526 | 0.11902 | 0.032043 | 0.29297 | 0.2243 | -15.4221 | 0.19226 | -0.091553 | 0.004578 | 0.1236 | -108.2153 | 120.314 | -0.041199 | 120.1401 | 120.2454 | -15.4953 | 11.8057 | 0.050354 | -0.17395 | 119.9295 | 120.0256 | 104.599 | 120.0531 | 120.1401 | 120.1447 | 120.2133 | 11.8057 | 120.0531 | 120.1401 | 120.2133 | 104.599 | 120.1447 | 0.21973 | -108.2886
3169.7344 | 121.0281 | -120.6894 | 0.054932 | 0.00206 | -0.0017004 | 0.0079767 | 0.07377 | -0.025648 | -0.031277 | 0.011211 | 0.059509 | 0.059509 | -0.10529 | 0.13733 | -0.032043 | 0.15106 | -0.10986 | 0.21057 | 0.12817 | -121.0327 | 120.5841 | 0.004577 | 120.7489 | 120.8267 | -0.086975 | -0.34332 | 0.073242 | 0.16479 | 120.5795 | 120.9 | 120.6573 | 120.7489 | 120.7489 | 120.8176 | 120.8405 | -0.34332 | 120.7489 | 120.7489 | 120.8405 | 120.6573 | 120.8176 | -0.16022 | -121.0876
3171.5312 | 121.0281 | -120.7764 | 0.059509 | 0.00206 | 0.0010766 | 0.0084039 | 0.08082 | -0.025434 | -0.03384 | 0.015056 | 0.036621 | 0.073242 | -0.1236 | 0.13275 | -0.064087 | 0.1236 | -0.11444 | -0.15106 | 0.15564 | -121.0785 | 120.6528 | 0.013733 | 120.813 | 120.9091 | -0.1236 | -0.30212 | 0.096131 | 0.16022 | 120.6619 | 120.6253 | 120.7123 | 120.8496 | 120.813 | 120.932 | 120.9 | -0.30212 | 120.8496 | 120.813 | 120.9 | 120.7123 | 120.932 | -0.1831 | -121.138
3173.3281 | 121.0236 | -120.7947 | 0.082397 | 0.017319 | -0.0023412 | 0.011608 | 0.10368 | -0.027143 | -0.030849 | 0.037059 | 0.10071 | 0.041199 | -0.091553 | 0.20599 | -0.073242 | 0.19684 | -0.17853 | -13.3209 | 0.1236 | -121.0785 | 120.7031 | -0.041198 | 120.8954 | 121.0007 | -0.15564 | -0.28381 | 0.041199 | 0.19226 | 120.6162 | 107.4738 | 120.7214 | 120.8359 | 120.8954 | 120.9183 | 120.9915 | -0.28381 | 120.8359 | 120.8954 | 120.9915 | 120.7214 | 120.9183 | -0.17395 | -121.1609
3175.125 | 121.1151 | -120.7855 | 0.064087 | 0.0096895 | -0.0021276 | 0.0045587 | 0.10923 | -0.027357 | -0.02914 | 0.038555 | 0.041199 | 0.059509 | -0.09613 | 0.15106 | -0.21973 | 0.15564 | -0.09613 | -2.9205 | 0.13275 | -121.1197 | 120.6894 | -0.004578 | 120.8267 | 120.9366 | -0.28381 | -0.33417 | 0.068664 | 0.13733 | 120.6894 | 117.865 | 120.5658 | 120.845 | 120.8267 | 120.9183 | 120.9412 | -0.33417 | 120.845 | 120.8267 | 120.9412 | 120.5658 | 120.9183 | -0.16022 | -121.1838
3176.9531 | 121.1426 | -120.8405 | 0.068665 | 0.00206 | -0.0017004 | 0.0096857 | 0.088083 | -0.027357 | -0.032131 | 0.019756 | -0.009155 | 0.10986 | -0.15564 | 0.10071 | -0.13275 | 0.073242 | -0.027466 | 0.018311 | 0.15564 | -121.1792 | 120.6848 | 0.041198 | 120.8313 | 120.9412 | -0.20142 | -0.33875 | 0.086975 | 0.14649 | 120.813 | 120.8588 | 120.7077 | 120.9503 | 120.8313 | 120.9961 | 120.9137 | -0.33875 | 120.9503 | 120.8313 | 120.9137 | 120.7077 | 120.9961 | -0.22431 | -121.2479
3178.6875 | 121.0739 | -120.8817 | 0.064087 | 0.017319 | -0.00041862 | 0.0037043 | 0.10603 | -0.022443 | -0.032985 | 0.037273 | 0.11444 | 0.027466 | -0.086975 | 0.20599 | -0.07782 | 0.21515 | -0.21515 | -0.56305 | 0.10529 | -121.1426 | 120.7947 | -0.036621 | 120.9961 | 121.0876 | -0.14191 | -0.26093 | 0.041199 | 0.20142 | 120.6665 | 120.3186 | 120.8038 | 120.9091 | 120.9961 | 120.9869 | 121.0968 | -0.26093 | 120.9091 | 120.9961 | 121.0968 | 120.8038 | 120.9869 | -0.15106 | -121.2067
3180.4219 | 121.138 | -120.8633 | 0.073242 | 0.0096895 | -0.002555 | 0.0037043 | 0.087656 | -0.026502 | -0.033626 | 0.021892 | 0.09613 | 0.041199 | -0.10071 | 0.20142 | 0.022888 | 0.19684 | -0.17395 | 0.073242 | 0.12817 | -121.1517 | 120.7626 | -0.032043 | 120.9595 | 121.0648 | -0.050354 | -0.28839 | 0.054932 | 0.19684 | 120.6894 | 120.9366 | 120.8862 | 120.9045 | 120.9595 | 120.9915 | 121.0602 | -0.28839 | 120.9045 | 120.9595 | 121.0602 | 120.8862 | 120.9915 | -0.17395 | -121.225
3182.1562 | 121.1884 | -120.8908 | 0.082397 | 0.0096895 | -0.0031958 | 0.0066949 | 0.081247 | -0.026502 | -0.031917 | 0.020397 | 0.045776 | 0.054932 | -0.09613 | 0.14648 | -0.027466 | 0.15106 | -0.10071 | 0.073242 | 0.14191 | -121.2112 | 120.7947 | -0.027465 | 120.9366 | 121.0373 | -0.10986 | -0.32043 | 0.05951 | 0.14191 | 120.7901 | 120.9641 | 120.8633 | 120.9457 | 120.9366 | 121.0327 | 121.0419 | -0.32043 | 120.9457 | 120.9366 | 121.0419 | 120.8633 | 121.0327 | -0.17853 | -121.2936
3183.9531 | 121.2387 | -120.8908 | 0.059509 | 0.0096895 | -0.0010596 | 0.0081903 | 0.097055 | -0.028425 | -0.030422 | 0.034069 | 0.050354 | 0.041199 | -0.10529 | 0.16937 | -0.13275 | 0.15106 | -0.1236 | -0.67291 | 0.13275 | -121.2433 | 120.7855 | -0.01831 | 120.9412 | 121.0602 | -0.19226 | -0.35248 | 0.073242 | 0.15564 | 120.7672 | 120.2179 | 120.7581 | 120.932 | 120.9412 | 121.0236 | 121.0419 | -0.35248 | 120.932 | 120.9412 | 121.0419 | 120.7581 | 121.0236 | -0.16479 | -121.3028
3185.6719 | 121.1563 | -120.9091 | 0.054932 | 0.0096895 | -0.0014868 | 0.0047723 | 0.098978 | -0.026289 | -0.033413 | 0.017833 | 0.1236 | 0.036621 | -0.082397 | 0.22888 | 0.054932 | 0.21515 | -0.20142 | -0.009155 | 0.1236 | -121.225 | 120.8267 | -0.018311 | 121.0327 | 121.138 | 0 | -0.31586 | 0.068664 | 0.20599 | 120.7077 | 120.9 | 120.9641 | 120.9457 | 121.0327 | 121.0327 | 121.1243 | -0.31586 | 120.9457 | 121.0327 | 121.1243 | 120.9641 | 121.0327 | -0.13733 | -121.2799
3187.4531 | 121.2296 | -120.8954 | 0.054932 | 0.017319 | -0.00063242 | 0.0090447 | 0.087869 | -0.026289 | -0.033199 | 0.016979 | -0.009155 | 0.091553 | -0.14648 | 0.086975 | -0.086975 | 0.064087 | -0.009155 | -0.013733 | 0.16937 | -121.3028 | 120.7489 | 0.036621 | 120.8862 | 120.9824 | -0.14191 | -0.40741 | 0.11444 | 0.13733 | 120.8862 | 120.8817 | 120.8084 | 120.9869 | 120.8862 | 121.0648 | 120.9595 | -0.40741 | 120.9869 | 120.8862 | 120.9595 | 120.8084 | 121.0648 | -0.20142 | -121.3577
3189.1562 | 121.2524 | -120.9366 | 0.050354 | 0.0096895 | -0.0012732 | 0.0062677 | 0.11457 | -0.026929 | -0.032772 | 0.041973 | 0.036621 | 0.064087 | -0.11902 | 0.16479 | -0.004578 | 0.14191 | -0.1236 | 0.09613 | 0.13275 | -121.2753 | 120.8176 | 0.013733 | 120.9732 | 121.1014 | -0.054932 | -0.33875 | 0.082397 | 0.15564 | 120.813 | 121.0327 | 120.932 | 121.0007 | 120.9732 | 121.0693 | 121.0785 | -0.33875 | 121.0007 | 120.9732 | 121.0785 | 120.932 | 121.0693 | -0.16937 | -121.3257
3190.875 | 121.0922 | -120.9915 | 0.07782 | 0.017319 | -0.0029822 | 0.0077631 | 0.10197 | -0.025648 | -0.033626 | 0.031505 | 0.054932 | 0.064087 | -0.11902 | 0.15564 | -0.004578 | 0.13733 | -0.032043 | 0.17853 | 0.14191 | -121.2891 | 120.8725 | -0.013733 | 121.0464 | 121.1472 | -0.082398 | -0.29755 | 0.064087 | 0.17395 | 120.9595 | 121.17 | 120.9869 | 121.0556 | 121.0464 | 121.1334 | 121.1288 | -0.29755 | 121.0556 | 121.0464 | 121.1288 | 120.9869 | 121.1334 | -0.19684 | -121.3669
3192.5938 | 121.1746 | -121.0052 | 0.10986 | 0.00206 | -0.002555 | 0.0058405 | 0.092142 | -0.024793 | -0.031917 | 0.026378 | 0.09613 | 0.050354 | -0.082397 | 0.19684 | -0.027466 | 0.1831 | -0.064087 | 0.25177 | 0.12817 | -121.2845 | 120.9229 | -0.059509 | 121.1014 | 121.2021 | -0.13733 | -0.27924 | 0.018311 | 0.17853 | 120.9412 | 121.257 | 120.9778 | 121.0556 | 121.1014 | 121.1334 | 121.1884 | -0.27924 | 121.0556 | 121.1014 | 121.1884 | 120.9778 | 121.1334 | -0.19226 | -121.3943
3194.3281 | 121.2662 | -120.9686 | 0.086975 | 0.0096895 | -0.0017004 | 0.0060541 | 0.11329 | -0.025861 | -0.03149 | 0.0471 | 0.10529 | 0.045776 | -0.10529 | 0.18768 | 0.013733 | 0.20142 | -0.19684 | -0.29297 | 0.1236 | -121.312 | 120.8633 | -0.041199 | 121.0739 | 121.1563 | -0.073242 | -0.34332 | 0.036621 | 0.21057 | 120.7718 | 120.6757 | 120.9824 | 121.0144 | 121.0739 | 121.0922 | 121.17 | -0.34332 | 121.0144 | 121.0739 | 121.17 | 120.9824 | 121.0922 | -0.19226 | -121.3989
3196.0469 | 121.1792 | -120.9732 | 0.13733 | 0.0096895 | -0.001914 | 0.0098993 | 0.18614 | -0.027784 | -0.034908 | 0.11055 | -0.013733 | 0.086975 | -0.14648 | 0.086975 | -0.20142 | 0.068665 | 0.045776 | -10.7758 | 0.16937 | -121.2936 | 120.8267 | -0.050354 | 120.9595 | 121.0602 | -0.33875 | -0.32043 | 0.032044 | 0.13275 | 121.019 | 110.1974 | 120.7718 | 121.0602 | 120.9595 | 121.1426 | 121.0419 | -0.32043 | 121.0602 | 120.9595 | 121.0419 | 120.7718 | 121.1426 | -0.28381 | -121.431
3197.75 | 121.225 | -121.0236 | 0.073242 | 0.0096895 | -0.00041862 | 0.0034905 | 0.11543 | -0.025434 | -0.034694 | 0.043682 | 0.004578 | 0.073242 | -0.15106 | 0.11902 | -0.10986 | 0.10529 | 0.032043 | -0.3479 | 0.15106 | -121.2982 | 120.8725 | 0 | 121.0281 | 121.1426 | -0.18311 | -0.27466 | 0.07782 | 0.15564 | 121.0556 | 120.6757 | 120.9137 | 121.0968 | 121.0281 | 121.1746 | 121.1288 | -0.27466 | 121.0968 | 121.0281 | 121.1288 | 120.9137 | 121.1746 | -0.2243 | -121.3715
3199.4688 | 121.225 | -121.0098 | 0.059509 | 0.00206 | 0.001504 | 0.0060541 | 0.10581 | -0.025861 | -0.034054 | 0.053081 | 0.11444 | 0.036621 | -0.064087 | 0.19684 | -0.054932 | 0.21973 | -0.21057 | -0.073242 | 0.13733 | -121.2936 | 120.9457 | -0.022888 | 121.1243 | 121.2067 | -0.11444 | -0.28381 | 0.07782 | 0.17853 | 120.7993 | 120.9366 | 120.9549 | 121.0464 | 121.1243 | 121.1472 | 121.2296 | -0.28381 | 121.0464 | 121.1243 | 121.2296 | 120.9549 | 121.1472 | -0.1236 | -121.3531
3201.2031 | 121.1975 | -121.051 | 0.091553 | 0.0096895 | -0.001914 | 0.0062677 | 0.090433 | -0.023725 | -0.031917 | 0.023815 | 0.041199 | 0.082397 | -0.10529 | 0.14191 | -0.013733 | 0.086975 | -0.018311 | 0.018311 | 0.16937 | -121.3303 | 120.9457 | -0.009156 | 121.0922 | 121.1929 | -0.10529 | -0.27924 | 0.07782 | 0.14649 | 121.0327 | 121.0693 | 121.0373 | 121.1334 | 121.0922 | 121.2204 | 121.138 | -0.27924 | 121.1334 | 121.0922 | 121.138 | 121.0373 | 121.2204 | -0.19684 | -121.4218
3202.9688 | 121.2433 | -121.0602 | 0.064087 | 0.0096895 | -0.001914 | 0.0060541 | 0.080606 | -0.027784 | -0.03149 | 0.018901 | 0.10529 | 0.041199 | -0.091553 | 0.21515 | 0.091553 | 0.22888 | -0.14648 | 0.27924 | 0.13275 | -121.3623 | 120.9686 | -0.022888 | 121.1655 | 121.2753 | 0.027466 | -0.30212 | 0.068664 | 0.19684 | 120.9137 | 121.3394 | 121.1517 | 121.1014 | 121.1655 | 121.1929 | 121.2891 | -0.30212 | 121.1014 | 121.1655 | 121.2891 | 121.1517 | 121.1929 | -0.15564 | -121.4264
3204.6875 | 121.3165 | -120.9824 | 0.059509 | 0.00206 | 0.00043578 | 0.0045587 | 0.095133 | -0.02757 | -0.03149 | 0.028514 | 0.045776 | 0.073242 | -0.10071 | 0.13733 | 0.018311 | 0.15106 | -0.09613 | -0.17395 | 0.13275 | -121.3486 | 120.8817 | 0.013733 | 121.0281 | 121.1197 | -0.041198 | -0.36621 | 0.073242 | 0.14648 | 120.8862 | 120.8084 | 121.0007 | 121.0556 | 121.0281 | 121.1151 | 121.1334 | -0.36621 | 121.0556 | 121.0281 | 121.1334 | 121.0007 | 121.1151 | -0.16022 | -121.4081
3206.4062 | 121.3806 | -120.9961 | 0.086975 | 0.00206 | -0.001914 | 0.0081903 | 0.25086 | -0.028638 | -0.030422 | 0.064189 | 0.054932 | 0.073242 | -0.082397 | 0.14648 | -0.19226 | 0.15106 | -0.10071 | 0.013733 | 0.13733 | -121.376 | 120.9137 | -0.013733 | 121.051 | 121.1426 | -0.27924 | -0.37994 | 0.050354 | 0.13733 | 120.8954 | 121.0098 | 120.8038 | 121.0693 | 121.051 | 121.1334 | 121.1472 | -0.37994 | 121.0693 | 121.051 | 121.1472 | 120.8038 | 121.1334 | -0.16937 | -121.463
3208.125 | 121.4035 | -121.0373 | 0.07782 | 0.0096895 | -0.0023412 | 0.0028497 | 0.14341 | -0.02992 | -0.030636 | 0.075939 | 0.054932 | 0.041199 | -0.09613 | 0.14191 | -0.27008 | 0.16479 | -0.10529 | -0.11902 | 0.14191 | -121.4081 | 120.9412 | -0.036621 | 121.0922 | 121.1792 | -0.3479 | -0.37079 | 0.064087 | 0.15106 | 120.932 | 120.9183 | 120.7672 | 121.0785 | 121.0922 | 121.1792 | 121.2021 | -0.37079 | 121.0785 | 121.0922 | 121.2021 | 120.7672 | 121.1792 | -0.17395 | -121.4859
3209.8906 | 121.3211 | -121.0419 | 0.068665 | 0.00206 | -0.0017004 | 0.0017817 | 0.13828 | -0.027784 | -0.030422 | 0.08192 | 0.09613 | 0.050354 | -0.073242 | 0.19684 | -0.07782 | 0.16937 | -0.17853 | -68.9575 | 0.10071 | -121.8018 | 120.9686 | -0.018311 | 121.138 | 121.2387 | -0.14649 | -0.75989 | 0.032043 | 0.16937 | 120.8633 | 52.0844 | 120.9641 | 121.0922 | 121.138 | 121.1426 | 121.2112 | -0.75989 | 121.0922 | 121.138 | 121.2112 | 120.9641 | 121.1426 | -0.14191 | -121.8704
3211.6094 | 121.2616 | -121.0968 | 0.086975 | 0.00206 | -0.0021276 | 0.0032769 | 0.14598 | -0.028211 | -0.031277 | 0.076793 | 0.10986 | 0.054932 | -0.10071 | 0.21057 | -0.21515 | 0.1831 | -0.082397 | -116.5558 | 0.10986 | -121.3806 | 120.9961 | -0.032043 | 121.2067 | 121.3074 | -0.30212 | -0.28381 | 0.022888 | 0.21057 | 121.0144 | 4.541 | 120.8817 | 121.1517 | 121.2067 | 121.2067 | 121.2799 | -0.28381 | 121.1517 | 121.2067 | 121.2799 | 120.8817 | 121.2067 | -0.18768 | -121.4676
3213.3125 | 121.2799 | -121.138 | 0.10071 | 0.0096895 | 0.001504 | 0.0058405 | 0.15815 | -0.025861 | -0.034694 | 0.10093 | 0.022888 | 0.082397 | -0.15106 | 0.1236 | -0.027466 | 0.07782 | 0.041199 | -117.8009 | 0.13733 | -121.3989 | 120.9869 | -0.018311 | 121.1609 | 121.2616 | -0.12817 | -0.26093 | 0.036621 | 0.17395 | 121.1792 | 3.3371 | 121.1105 | 121.2204 | 121.1609 | 121.2753 | 121.2158 | -0.26093 | 121.2204 | 121.1609 | 121.2158 | 121.1105 | 121.2753 | -0.25177 | -121.4996
3215.0312 | 121.2433 | -121.0922 | 0.12817 | 0.00206 | -0.0021276 | 0.0047723 | 0.22074 | -0.025007 | -0.03149 | 0.13917 | 0.009155 | 0.10071 | -0.12817 | 0.09613 | -0.17853 | 0.059509 | 0.059509 | -118.5059 | 0.16937 | -121.3989 | 120.9641 | -0.027466 | 121.1014 | 121.1884 | -0.3067 | -0.3067 | 0.041199 | 0.13733 | 121.1517 | 2.5864 | 120.9137 | 121.1929 | 121.1014 | 121.2616 | 121.1517 | -0.3067 | 121.1929 | 121.1014 | 121.1517 | 120.9137 | 121.2616 | -0.25635 | -121.5271
3216.7344 | 121.3211 | -121.0327 | 0.10986 | 0.0096895 | -0.0023412 | 0.0039179 | 0.25791 | -0.024366 | -0.032985 | 0.20198 | 0.10529 | 0.041199 | -0.10071 | 0.19684 | 0.059509 | 0.19684 | -0.19226 | -118.3136 | 0.09613 | -121.344 | 120.932 | -0.068664 | 121.138 | 121.2296 | -0.050354 | -0.31128 | -0.013733 | 0.20599 | 120.8405 | 2.7191 | 121.0922 | 121.0739 | 121.138 | 121.1288 | 121.2296 | -0.31128 | 121.0739 | 121.138 | 121.2296 | 121.0922 | 121.1288 | -0.21057 | -121.4539
3218.5 | 120.3323 | -8.6517 | 112.0651 | 0.0096895 | -0.0031958 | 0.0045587 | 0.056253 | 0.034808 | 0.032383 | 0.1569 | 0.013733 | 0.022888 | -0.15564 | 0.09613 | -1.6754 | 0.068665 | -0.036621 | -1.0391 | 111.969 | -9.3338 | 8.4961 | -112.0422 | 8.6655 | 8.7479 | -113.7405 | -0.68207 | -0.096131 | 0.16937 | 8.6151 | 7.6126 | 6.9763 | 8.6746 | 8.6655 | 120.6207 | 8.7204 | -0.68207 | 8.6746 | 8.6655 | 8.7204 | 6.9763 | 120.6207 | -112.2208 | -121.3989
3220.2031 | 120.3873 | -9.2148 | 111.1816 | 0.017319 | -0.00084602 | 0.0064813 | 0.057108 | 0.033526 | 0.028965 | 0.1584 | -0.036621 | 0.041199 | -0.17853 | 0.068665 | -3.4378 | 0.032043 | 0 | -8.0246 | 111.5158 | -9.9014 | 9.0363 | -111.1404 | 9.1782 | 9.2834 | -114.6194 | -0.68664 | 0.33417 | 0.14191 | 9.2148 | 1.1902 | 5.777 | 9.256 | 9.1782 | 120.7306 | 9.2468 | -0.68664 | 9.256 | 9.1782 | 9.2468 | 5.777 | 120.7306 | -111.3602 | -121.0831
3221.9062 | 121.2433 | -6.2164 | 114.8392 | 0.017319 | -0.0010596 | 0.0079767 | 0.063303 | 0.039294 | 0.030674 | 0.16673 | -0.050354 | 0.027466 | -0.1831 | 0.036621 | -2.243 | 0.013733 | -0.027466 | -2.8152 | 114.9124 | -6.5689 | 6.0333 | -114.8117 | 6.1661 | 6.2531 | -117.0822 | -0.35248 | 0.073243 | 0.13275 | 6.189 | 3.4012 | 3.9734 | 6.2439 | 6.1661 | 121.1288 | 6.2302 | -0.35248 | 6.2439 | 6.1661 | 6.2302 | 3.9734 | 121.1288 | -115.0223 | -121.4081
3223.6094 | 121.2479 | -4.7012 | 116.423 | 0.0096895 | -0.0034094 | 0.0064813 | 0.075266 | 0.035448 | 0.035374 | 0.17826 | 0.027466 | 0.018311 | -0.13733 | 0.16479 | -1.8356 | 0.15564 | -0.17853 | -2.1515 | 116.478 | -4.9438 | 4.5639 | -116.4047 | 4.7287 | 4.866 | -118.2587 | -0.24261 | 0.054931 | 0.16479 | 4.5227 | 2.5497 | 2.8656 | 4.7195 | 4.7287 | 121.1792 | 4.8569 | -0.24261 | 4.7195 | 4.7287 | 4.8569 | 2.8656 | 121.1792 | -116.5604 | -121.3669
3225.3906 | 121.1609 | -5.9143 | 114.592 | 0.00206 | -0.0023412 | 0.0030633 | 0.31367 | 0.035662 | 0.030888 | 0.37864 | 0.054932 | 0 | -0.12817 | 0.19684 | -2.7008 | 0.16022 | -0.16937 | -6.5277 | 113.2965 | -8.2947 | 5.7861 | -114.592 | 5.9692 | 6.1111 | -117.2928 | -2.3804 | -1.2955 | 0.18311 | 5.7449 | -0.6134 | 3.2135 | 5.9143 | 5.9692 | 119.2108 | 6.0745 | -2.3804 | 5.9143 | 5.9692 | 6.0745 | 3.2135 | 119.2108 | -114.7202 | -122.8867
3227.1094 | 121.2021 | -3.3142 | 117.7368 | 0.0096895 | -0.0034094 | 0.0084039 | 0.07847 | 0.038866 | 0.030247 | 0.1945 | 0.050354 | -0.009155 | -0.12817 | 0.16937 | -0.67291 | 0.12817 | -0.09613 | -0.42114 | 118.2404 | -3.2639 | 3.186 | -117.746 | 3.3646 | 3.4836 | -118.4097 | 0.050354 | 0.50354 | 0.17853 | 3.2181 | 2.8931 | 2.6413 | 3.3051 | 3.3646 | 121.5546 | 3.4424 | 0.050354 | 3.3051 | 3.3646 | 3.4424 | 2.6413 | 121.5546 | -117.865 | -121.0007
3228.8438 | 121.2112 | -3.1174 | 118.1259 | 0.0096895 | -0.002555 | 0.0060541 | 0.091928 | 0.040575 | 0.03281 | 0.18937 | 0 | 0.027466 | -0.16022 | 0.13275 | -0.58136 | 0.073242 | -0.073242 | -0.28381 | 118.1717 | -3.3875 | 2.9572 | -118.0984 | 3.1174 | 3.2501 | -118.7073 | -0.27008 | 0.045776 | 0.16022 | 3.0441 | 2.8336 | 2.536 | 3.1448 | 3.1174 | 121.2891 | 3.1906 | -0.27008 | 3.1448 | 3.1174 | 3.1906 | 2.536 | 121.2891 | -118.2861 | -121.5134
3230.5625 | 121.3303 | -3.7765 | 117.5079 | 0.00206 | -0.0031958 | 0.0054131 | 0.073129 | 0.040362 | 0.032597 | 0.19236 | 0.073242 | 0.004578 | -0.1236 | 0.16937 | -0.77362 | 0.16479 | -0.24261 | -0.20142 | 117.6682 | -3.8315 | 3.653 | -117.5034 | 3.8498 | 3.9459 | -118.2816 | -0.054932 | 0.16022 | 0.19684 | 3.5339 | 3.5751 | 3.0029 | 3.7811 | 3.8498 | 121.4447 | 3.9413 | -0.054932 | 3.7811 | 3.8498 | 3.9413 | 3.0029 | 121.4447 | -117.6315 | -121.3394
3232.2812 | 121.3028 | -9.1782 | 111.9232 | -0.0055695 | -0.0017004 | 0.0056269 | 0.49781 | 0.033526 | 0.027683 | 0.57817 | 0.073242 | 0 | -0.12817 | 0.18768 | 1.1261 | 0.17395 | -0.25177 | -0.8194 | 112.2437 | -9.0958 | 9.05 | -111.9232 | 9.2514 | 9.3658 | -110.7971 | 0.082398 | 0.32043 | 0.20142 | 8.9264 | 8.3588 | 10.3043 | 9.1782 | 9.2514 | 121.4218 | 9.3521 | 0.082398 | 9.1782 | 9.2514 | 9.3521 | 10.3043 | 121.4218 | -112.0514 | -121.019
3234.0156 | 121.1517 | -5.0629 | 115.6494 | 0.017319 | 0.00022218 | 0.0058405 | 0.055185 | 0.041003 | 0.033238 | 0.16374 | 0.045776 | 0.013733 | -0.13733 | 0.15106 | 1.03 | 0.15106 | -0.20599 | -0.39825 | 116.0889 | -5.2689 | 4.9255 | -115.6357 | 5.1086 | 5.2139 | -114.6194 | -0.20599 | 0.43945 | 0.18311 | 4.8569 | 4.6646 | 6.0928 | 5.0766 | 5.1086 | 121.1517 | 5.2139 | -0.20599 | 5.0766 | 5.1086 | 5.2139 | 6.0928 | 121.1517 | -115.7867 | -120.9183
3235.7344 | 121.3303 | -4.3488 | 116.89 | 0.024948 | 0.0010766 | 0.0081903 | 0.063516 | 0.039507 | 0.031315 | 0.18531 | -0.045776 | 0.041199 | -0.17395 | 0.045776 | 0.59052 | 0.027466 | -0.054932 | -0.44861 | 117.6407 | -3.8727 | 4.1748 | -116.8488 | 4.303 | 4.3945 | -116.2994 | 0.47607 | 0.75073 | 0.12817 | 4.2938 | 3.9001 | 4.9393 | 4.39 | 4.303 | 121.9894 | 4.3762 | 0.47607 | 4.39 | 4.303 | 4.3762 | 4.9393 | 121.9894 | -117.0639 | -120.7626
3237.4531 | 121.376 | -4.9942 | 115.535 | 0.0096895 | 0.001504 | 0.0079767 | 0.10731 | 0.038866 | 0.032597 | 0.21522 | -0.050354 | 0.027466 | -0.17395 | 0.045776 | 0.45319 | 0.022888 | -0.059509 | -0.60883 | 117.2653 | -4.2938 | 4.8203 | -115.5075 | 4.9438 | 5.04 | -115.0818 | 0.70038 | 1.7303 | 0.1236 | 4.9347 | 4.3854 | 5.4474 | 5.0217 | 4.9438 | 122.2595 | 5.0171 | 0.70038 | 5.0217 | 4.9438 | 5.0171 | 5.4474 | 122.2595 | -115.7089 | -119.8288
3239.1875 | 121.4539 | -113.4567 | 7.4615 | 0.00206 | -0.00020502 | 0.0051995 | 0.30747 | -0.023511 | -0.02679 | 0.24748 | 0.068665 | 0.045776 | -0.086975 | 0.17395 | 0.082397 | 0.1831 | -0.15564 | -0.23346 | 5.8868 | -115.5716 | 113.3698 | -7.4158 | 113.5254 | 113.6307 | -7.3792 | -2.1149 | -1.5747 | 0.15564 | 113.3011 | 113.2233 | 113.5391 | 113.5025 | 113.5254 | 119.3436 | 113.6398 | -2.1149 | 113.5025 | 113.5254 | 113.6398 | 113.5391 | 119.3436 | -7.5485 | -123.0331
3240.9688 | 121.4584 | -120.9732 | 0.16479 | -0.0055695 | -0.0014868 | 0.0084039 | 0.092783 | -0.025434 | -0.032345 | 0.028301 | 0.10529 | 0.054932 | -0.086975 | 0.19226 | 0.091553 | 0.20142 | -0.18768 | 0.25635 | 0.24261 | -121.3348 | 120.8862 | -0.10986 | 121.0785 | 121.1655 | -0.073242 | -0.36163 | 0.07782 | 0.19226 | 120.7855 | 121.2296 | 121.0648 | 121.0281 | 121.0785 | 121.2158 | 121.1746 | -0.36163 | 121.0281 | 121.0785 | 121.1746 | 121.0648 | 121.2158 | -0.25177 | -121.4996
3242.6875 | 121.4447 | -120.8496 | 0.30212 | 0.0096895 | -0.00084602 | 0.0045587 | 0.21583 | -0.026929 | -0.032772 | 0.15391 | 0.050354 | 0.054932 | -0.10986 | 0.17853 | 0.07782 | 0.19684 | -0.15564 | -0.16479 | 0.36163 | -121.17 | 120.7397 | -0.24719 | 120.9 | 121.0281 | -0.2243 | -0.32044 | 0.059509 | 0.16022 | 120.694 | 120.6848 | 120.9274 | 120.9045 | 120.9 | 121.2112 | 121.0464 | -0.32044 | 120.9045 | 120.9 | 121.0464 | 120.9274 | 121.2112 | -0.41199 | -121.4722
3244.4688 | 121.4035 | -120.5704 | 0.6546 | 0.00206 | -0.0027686 | 0.0019953 | 0.4914 | -0.02458 | -0.033199 | 0.44529 | -0.022888 | 0.086975 | -0.14191 | 0.10071 | -0.022888 | 0.073242 | 0.054932 | -1.6067 | 0.69122 | -120.8405 | 120.4285 | -0.56763 | 120.5475 | 120.6711 | -0.67749 | -0.27008 | 0.036621 | 0.11902 | 120.6253 | 118.9636 | 120.5475 | 120.6573 | 120.5475 | 121.2616 | 120.6436 | -0.27008 | 120.6573 | 120.5475 | 120.6436 | 120.5475 | 121.2616 | -0.79651 | -121.4951
3246.1719 | 121.344 | -120.8176 | 0.41199 | 0.0096895 | -0.00041862 | 0.0062677 | 0.47389 | -0.02522 | -0.031277 | 0.4077 | 0 | 0.091553 | -0.13275 | 0.091553 | -0.004578 | 0.07782 | 0.032043 | -0.91553 | 0.50812 | -121.019 | 120.6848 | -0.32043 | 120.8176 | 120.9091 | -0.41657 | -0.20142 | 0.096131 | 0.13275 | 120.8496 | 119.902 | 120.813 | 120.9091 | 120.8176 | 121.3257 | 120.8954 | -0.20142 | 120.9091 | 120.8176 | 120.8954 | 120.813 | 121.3257 | -0.54474 | -121.431
3247.9375 | 121.4401 | -120.8771 | 0.36621 | 0.0096895 | -0.00063242 | 0.0032769 | 0.36238 | -0.026289 | -0.031063 | 0.30046 | 0.073242 | 0.054932 | -0.091553 | 0.17853 | 0.082397 | 0.20142 | -0.1236 | -0.79193 | 0.41657 | -121.1334 | 120.7855 | -0.31128 | 120.9503 | 121.0556 | -0.28381 | -0.25635 | 0.050354 | 0.16479 | 120.7535 | 120.0851 | 120.9595 | 120.932 | 120.9503 | 121.2936 | 121.0785 | -0.25635 | 120.932 | 120.9503 | 121.0785 | 120.9595 | 121.2936 | -0.45776 | -121.4996
3249.6406 | 121.3394 | -120.8221 | 0.44861 | 0.00206 | 0.0029992 | 0.0075495 | 0.45381 | -0.024793 | -0.035122 | 0.38356 | 0.050354 | 0.073242 | -0.13733 | 0.16022 | 0.022888 | 0.13275 | -0.054932 | -1.2909 | 0.48981 | -121.0602 | 120.6848 | -0.37537 | 120.8725 | 120.9824 | -0.42572 | -0.23804 | 0.041199 | 0.18768 | 120.7672 | 119.5312 | 120.845 | 120.8954 | 120.8725 | 121.312 | 120.9549 | -0.23804 | 120.8954 | 120.8725 | 120.9549 | 120.845 | 121.312 | -0.58594 | -121.5088
3251.3438 | 121.4539 | -120.9595 | 0.27008 | 0.0096895 | -0.0017004 | 0.0047723 | 0.34422 | -0.026716 | -0.034481 | 0.30152 | -0.009155 | 0.091553 | -0.10986 | 0.091553 | -0.022888 | 0.068665 | 0 | -0.81024 | 0.35706 | -121.2479 | 120.8496 | -0.17853 | 120.9503 | 121.051 | -0.29297 | -0.28839 | 0.086975 | 0.10071 | 120.9595 | 120.1492 | 120.9366 | 121.051 | 120.9503 | 121.3165 | 121.0281 | -0.28839 | 121.051 | 120.9503 | 121.0281 | 120.9366 | 121.3165 | -0.37994 | -121.5179
3253.0781 | 121.4722 | -120.9366 | 0.32959 | 0.0096895 | -0.0027686 | 0.0064813 | 0.39997 | -0.024793 | -0.03149 | 0.33763 | 0.064087 | 0.054932 | -0.07782 | 0.15564 | 0.027466 | 0.17853 | -0.1236 | -1.0254 | 0.37537 | -121.2387 | 120.8588 | -0.27466 | 121.0007 | 121.0922 | -0.30212 | -0.30212 | 0.045776 | 0.14191 | 120.813 | 119.9112 | 120.9641 | 120.9915 | 121.0007 | 121.3119 | 121.1151 | -0.30212 | 120.9915 | 121.0007 | 121.1151 | 120.9641 | 121.3119 | -0.40741 | -121.5683
3254.7969 | 121.4355 | -120.8542 | 0.36621 | -0.0055695 | -0.0029822 | 0.0043451 | 0.44569 | -0.027784 | -0.031277 | 0.37309 | 0.041199 | 0.064087 | -0.10529 | 0.16479 | 0.013733 | 0.17395 | -0.10986 | -1.1353 | 0.36621 | -121.1746 | 120.7489 | -0.30212 | 120.8954 | 121.019 | -0.35248 | -0.32044 | 0 | 0.14649 | 120.7443 | 119.7189 | 120.8679 | 120.9183 | 120.8954 | 121.2204 | 121.0281 | -0.32044 | 120.9183 | 120.8954 | 121.0281 | 120.8679 | 121.2204 | -0.4715 | -121.5408
3256.5156 | 121.4859 | -120.9503 | 0.32044 | 0.00206 | -0.0010596 | 0.0026361 | 0.40083 | -0.026716 | -0.033413 | 0.34062 | 0.073242 | 0.064087 | -0.086975 | 0.19684 | 0.059509 | 0.19226 | -0.12817 | -0.95673 | 0.35706 | -121.2021 | 120.8633 | -0.25635 | 121.0236 | 121.1472 | -0.26093 | -0.25177 | 0.036621 | 0.16022 | 120.8221 | 119.9936 | 121.0098 | 121.0144 | 121.0236 | 121.3074 | 121.1426 | -0.25177 | 121.0144 | 121.0236 | 121.1426 | 121.0098 | 121.3074 | -0.40741 | -121.5225
3258.2188 | 121.312 | -119.3939 | 1.918 | 0.0096895 | 8.578e-06 | 0.0037043 | 1.3433 | -0.028425 | -0.030849 | 1.3023 | 0.091553 | 0.045776 | -0.10071 | 0.2243 | 0.032043 | 0.19684 | -0.09613 | -3.8498 | 1.9592 | -119.4443 | 119.2932 | -1.8723 | 119.4855 | 119.6182 | -1.886 | -0.050354 | 0.041199 | 0.19226 | 119.2978 | 115.5441 | 119.426 | 119.4397 | 119.4855 | 121.3531 | 119.5908 | -0.050354 | 119.4397 | 119.4855 | 119.5908 | 119.426 | 121.3531 | -2.0187 | -121.3623
3260 | 121.4355 | -121.138 | 0.2243 | -0.0055695 | -0.00041862 | 0.0013543 | 0.099405 | -0.02757 | -0.031704 | 0.040477 | 0.050354 | 0.073242 | -0.12817 | 0.1236 | 0.036621 | 0.10071 | 0.009155 | 0.19226 | 0.29755 | -121.463 | 121.0098 | -0.15106 | 121.1884 | 121.2616 | -0.18768 | -0.32501 | 0.073242 | 0.17853 | 121.1472 | 121.3303 | 121.1746 | 121.2112 | 121.1884 | 121.4355 | 121.2387 | -0.32501 | 121.2112 | 121.1884 | 121.2387 | 121.1746 | 121.4355 | -0.35248 | -121.6873
3261.7031 | 121.4218 | -119.7464 | 1.6113 | 0.00206 | -0.002555 | 0.0058405 | 0.29786 | -0.02522 | -0.030849 | 0.23765 | 0.11444 | 0.041199 | -0.091553 | 0.23804 | 0.10071 | 0.21973 | -0.16479 | -0.36163 | 1.6296 | -119.9936 | 119.6548 | -1.5701 | 119.8608 | 119.9844 | -1.5106 | -0.24719 | 0.018311 | 0.20599 | 119.5816 | 119.3848 | 119.8471 | 119.7876 | 119.8608 | 121.376 | 119.9661 | -0.24719 | 119.7876 | 119.8608 | 119.9661 | 119.8471 | 121.376 | -1.7029 | -121.6049
3263.4688 | 121.1563 | -117.2699 | 4.0833 | -0.0055695 | -0.003623 | 0.0039179 | 0.57194 | -0.022657 | -0.031063 | 0.51451 | 0.10529 | 0.045776 | -0.091553 | 0.21973 | 0.10529 | 0.19684 | -0.12817 | -1.2589 | 4.0924 | -117.4118 | 117.1783 | -4.0375 | 117.3752 | 117.4896 | -3.978 | -0.14191 | 0.009155 | 0.19684 | 117.1417 | 116.011 | 117.3752 | 117.3157 | 117.3752 | 121.3623 | 117.4667 | -0.14191 | 117.3157 | 117.3752 | 117.4667 | 117.3752 | 121.3623 | -4.1748 | -121.4951
3265.1875 | 121.4539 | -119.9066 | 1.4053 | 0.017319 | -0.0029822 | 0.0026361 | 0.41813 | -0.026289 | -0.032772 | 0.35066 | -0.004578 | 0.091553 | -0.13733 | 0.10071 | -0.036621 | 0.073242 | 0.036621 | -0.87433 | 1.4786 | -120.195 | 119.7693 | -1.3138 | 119.902 | 120.0073 | -1.442 | -0.28839 | 0.073243 | 0.13275 | 119.9432 | 119.0323 | 119.87 | 119.9982 | 119.902 | 121.3852 | 119.9799 | -0.28839 | 119.9982 | 119.902 | 119.9799 | 119.87 | 121.3852 | -1.5427 | -121.6003
3266.9531 | 121.3303 | -118.7805 | 2.4857 | 0.017319 | -0.0021276 | 0.0060541 | 0.89921 | -0.02522 | -0.031277 | 0.83216 | 0.11902 | 0.045776 | -0.091553 | 0.22888 | 0.004578 | 0.22888 | -0.15106 | -2.2202 | 2.4033 | -119.0414 | 118.689 | -2.4399 | 118.8995 | 119.0094 | -2.4811 | -0.26093 | -0.082398 | 0.21057 | 118.6295 | 116.5604 | 118.7851 | 118.8263 | 118.8995 | 121.1838 | 119.0094 | -0.26093 | 118.8263 | 118.8995 | 119.0094 | 118.7851 | 121.1838 | -2.5772 | -121.5271
3268.6719 | 121.4859 | -121.0693 | 0.26093 | 0.017319 | 0.00022218 | 0.0058405 | 0.13316 | -0.026716 | -0.032131 | 0.070171 | -0.009155 | 0.10071 | -0.1236 | 0.09613 | -0.004578 | 0.068665 | 0.064087 | 0.11444 | 0.31586 | -121.4172 | 120.9457 | -0.16022 | 121.0602 | 121.1655 | -0.2655 | -0.3479 | 0.054932 | 0.11444 | 121.1334 | 121.1838 | 121.0648 | 121.17 | 121.0602 | 121.3852 | 121.138 | -0.3479 | 121.17 | 121.0602 | 121.138 | 121.0648 | 121.3852 | -0.38452 | -121.6782
3270.3906 | 120.163 | -119.8929 | 0.10071 | 0.017319 | -0.0027686 | 0.0034905 | 0.072916 | -0.021589 | -0.033199 | 0.0037341 | 0.050354 | 0.068665 | -0.13733 | 0.12817 | 0.018311 | 0.09613 | -0.004578 | 0.21515 | 0.15106 | -120.2225 | 119.7556 | -0.032043 | 119.9432 | 120.0211 | -0.082397 | -0.32959 | 0.050354 | 0.18768 | 119.8883 | 120.108 | 119.9112 | 119.9615 | 119.9432 | 120.0439 | 119.989 | -0.32959 | 119.9615 | 119.9432 | 119.989 | 119.9112 | 120.0439 | -0.23804 | -120.3232
3272.1094 | 120.0256 | -120.6345 | 0.10071 | 0.017319 | 0.0012902 | 0.0094721 | 0.073129 | -0.02223 | -0.033413 | 0.0041615 | 0.009155 | 0.082397 | -0.13275 | 0.07782 | -0.004578 | 0.068665 | -0.013733 | 0.15106 | 0.17395 | -120.9091 | 120.5017 | -0.018311 | 120.6436 | 120.7123 | -0.10529 | -0.27466 | 0.073242 | 0.14191 | 120.6207 | 120.7855 | 120.6299 | 120.7169 | 120.6436 | 120.8084 | 120.7031 | -0.27466 | 120.7169 | 120.6436 | 120.7031 | 120.6299 | 120.8084 | -0.23346 | -121.0098
3273.875 | 120.7947 | -120.3598 | 0.32501 | 0.0096895 | -0.0029822 | 0.0069085 | 0.91075 | -0.026075 | -0.031704 | 0.86613 | 0.10071 | 0.036621 | -0.073242 | 0.21973 | 0.12817 | 0.21057 | -0.13275 | 0.32959 | 0.27924 | -120.6162 | 120.2866 | -0.28839 | 120.4605 | 120.5795 | -0.19684 | -0.25635 | -0.045776 | 0.17395 | 120.2271 | 120.6894 | 120.488 | 120.3964 | 120.4605 | 120.639 | 120.5704 | -0.25635 | 120.3964 | 120.4605 | 120.5704 | 120.488 | 120.639 | -0.39825 | -120.9412
3275.5781 | 121.0327 | -120.6802 | 0.10986 | 0.0096895 | -0.0014868 | 0.0039179 | 0.18891 | -0.02458 | -0.032558 | 0.1193 | 0.082397 | 0.036621 | -0.082397 | 0.17853 | 0.09613 | 0.18768 | -0.15106 | 0.064087 | 0.14191 | -120.9869 | 120.5978 | -0.073242 | 120.7626 | 120.8588 | -0.013733 | -0.3067 | 0.032044 | 0.16479 | 120.5292 | 120.7443 | 120.7764 | 120.7169 | 120.7626 | 120.8221 | 120.8679 | -0.3067 | 120.7169 | 120.7626 | 120.8679 | 120.7764 | 120.8221 | -0.19226 | -121.0968
3277.2969 | 121.0373 | -120.7947 | 0.091553 | 0.00206 | 0.00043578 | 0.0062677 | 0.081461 | -0.027143 | -0.031704 | 0.01527 | 0.004578 | 0.07782 | -0.1236 | 0.10529 | 0.013733 | 0.073242 | 0.032043 | 0.1831 | 0.18768 | -121.1288 | 120.6711 | -0.013733 | 120.7993 | 120.9 | -0.07782 | -0.33417 | 0.09613 | 0.12817 | 120.8267 | 120.9778 | 120.8084 | 120.8725 | 120.7993 | 120.9824 | 120.8679 | -0.33417 | 120.8725 | 120.7993 | 120.8679 | 120.8084 | 120.9824 | -0.21515 | -121.2204
3279 | 121.0693 | -120.6207 | 0.23804 | 0.0096895 | -0.0012732 | 0.0041315 | 0.67747 | -0.025648 | -0.035549 | 0.6352 | 0.027466 | 0.07782 | -0.13275 | 0.11902 | 0.036621 | 0.1236 | -0.07782 | -1.9775 | 0.24719 | -120.8817 | 120.488 | -0.16022 | 120.6482 | 120.7397 | -0.20142 | -0.26093 | 0.009155 | 0.16022 | 120.5429 | 118.6432 | 120.6573 | 120.6985 | 120.6482 | 120.8679 | 120.7443 | -0.26093 | 120.6985 | 120.6482 | 120.7443 | 120.6573 | 120.8679 | -0.37079 | -121.1197
3280.7188 | 121.1746 | -120.8176 | 0.054932 | 0.0096895 | -0.0014868 | 0.01054 | 0.087442 | -0.026289 | -0.036617 | 0.016979 | -0.018311 | 0.091553 | -0.13275 | 0.07782 | -0.013733 | 0.07782 | -0.013733 | 0.13275 | 0.17853 | -121.1929 | 120.6848 | 0.036621 | 120.7993 | 120.8954 | -0.068665 | -0.37537 | 0.1236 | 0.11444 | 120.8038 | 120.9503 | 120.8038 | 120.9091 | 120.7993 | 120.9961 | 120.8954 | -0.37537 | 120.9091 | 120.7993 | 120.8954 | 120.8038 | 120.9961 | -0.18768 | -121.2479
3282.4531 | 121.0785 | -120.9183 | 0.09613 | 0.032577 | -0.00020502 | 0.0043451 | 0.090219 | -0.02458 | -0.032558 | 0.022106 | 0.045776 | 0.068665 | -0.11902 | 0.13275 | 0.013733 | 0.086975 | -0.022888 | 0.15106 | 0.16937 | -121.1929 | 120.7993 | -0.027465 | 120.9641 | 121.051 | -0.082397 | -0.27466 | 0.073243 | 0.16479 | 120.8954 | 121.0693 | 120.932 | 120.9869 | 120.9641 | 121.0876 | 121.0052 | -0.27466 | 120.9869 | 120.9641 | 121.0052 | 120.932 | 121.0876 | -0.21515 | -121.2891
3284.1562 | 121.2204 | -120.6894 | 0.24261 | 0.0096895 | -0.00041862 | 0.0069085 | 0.2263 | -0.023725 | -0.031704 | 0.15605 | -0.004578 | 0.073242 | -0.11902 | 0.091553 | -0.004578 | 0.07782 | -0.032043 | 0.14191 | 0.19684 | -121.1884 | 120.5704 | -0.16937 | 120.6848 | 120.7809 | -0.24719 | -0.49896 | -0.045777 | 0.11444 | 120.6573 | 120.8313 | 120.6848 | 120.7626 | 120.6848 | 120.8862 | 120.7672 | -0.49896 | 120.7626 | 120.6848 | 120.7672 | 120.6848 | 120.8862 | -0.36163 | -121.431
3285.9062 | 121.2845 | -120.9229 | 0.054932 | 0.032577 | -0.0034094 | 0.0022089 | 0.077402 | -0.026929 | -0.031704 | 0.016765 | 0.050354 | 0.064087 | -0.09613 | 0.15106 | 0.068665 | 0.17395 | -0.10986 | 0.21515 | 0.1236 | -121.2616 | 120.8267 | 0.009155 | 120.9732 | 121.0739 | 0.013733 | -0.33874 | 0.068664 | 0.14648 | 120.813 | 121.138 | 120.9915 | 120.9869 | 120.9732 | 121.0464 | 121.0968 | -0.33874 | 120.9869 | 120.9732 | 121.0968 | 120.9915 | 121.0464 | -0.15106 | -121.3165
3287.625 | 121.1746 | -121.0007 | 0.068665 | 0.0096895 | -0.0038366 | 0.0054131 | 0.082743 | -0.026289 | -0.032558 | 0.015911 | -0.009155 | 0.086975 | -0.14191 | 0.10986 | 0.004578 | 0.082397 | 0.041199 | 0.14648 | 0.16937 | -121.312 | 120.8588 | 0.01831 | 120.9915 | 121.1105 | -0.064087 | -0.31128 | 0.10071 | 0.13275 | 121.0419 | 121.1472 | 121.0052 | 121.0876 | 120.9915 | 121.17 | 121.0831 | -0.31128 | 121.0876 | 120.9915 | 121.0831 | 121.0052 | 121.17 | -0.21057 | -121.3806
3289.4062 | 121.1746 | -121.019 | 0.10071 | 0.0096895 | -0.0040502 | 0.0039179 | 0.08082 | -0.027784 | -0.032345 | 0.016338 | 0.10529 | 0.032043 | -0.086975 | 0.21515 | 0.1236 | 0.21515 | -0.10986 | 0.29755 | 0.10529 | -121.2936 | 120.932 | -0.068665 | 121.1243 | 121.2341 | 0.022888 | -0.27466 | 0.004578 | 0.19226 | 120.9091 | 121.3165 | 121.1426 | 121.051 | 121.1243 | 121.1243 | 121.2341 | -0.27466 | 121.051 | 121.1243 | 121.2341 | 121.1426 | 121.1243 | -0.18768 | -121.3943
3291.125 | 121.2296 | -121.0327 | 0.09613 | 0.017319 | -0.002555 | 0.0090447 | 0.084879 | -0.027998 | -0.034481 | 0.01762 | -0.018311 | 0.07782 | -0.14191 | 0.086975 | 0.013733 | 0.073242 | 0.054932 | 0.14191 | 0.1831 | -121.3257 | 120.8908 | -0.01831 | 121.0144 | 121.1197 | -0.082397 | -0.29297 | 0.086975 | 0.1236 | 121.0876 | 121.1746 | 121.0464 | 121.1105 | 121.0144 | 121.2158 | 121.106 | -0.29297 | 121.1105 | 121.0144 | 121.106 | 121.0464 | 121.2158 | -0.23804 | -121.4218
3292.8438 | 121.3028 | -121.0556 | 0.068665 | 0.0096895 | -0.00063242 | 0.0028497 | 0.085733 | -0.025648 | -0.032772 | 0.018688 | 0.10986 | 0.045776 | -0.086975 | 0.19684 | 0.091553 | 0.20142 | -0.17853 | 0.2655 | 0.14191 | -121.3394 | 120.9686 | -0.022889 | 121.1655 | 121.2524 | 0.022888 | -0.28381 | 0.073242 | 0.19684 | 120.8771 | 121.3211 | 121.1472 | 121.1014 | 121.1655 | 121.1975 | 121.257 | -0.28381 | 121.1014 | 121.1655 | 121.257 | 121.1472 | 121.1975 | -0.15564 | -121.4081
3294.5469 | 121.2753 | -121.0556 | 0.086975 | 0.0096895 | -0.00020502 | 0.0013543 | 0.090006 | -0.029066 | -0.034267 | 0.021251 | -0.027466 | 0.09613 | -0.11902 | 0.091553 | 0.004578 | 0.07782 | 0.068665 | 0.14191 | 0.1831 | -121.3943 | 120.9366 | 0.009155 | 121.0281 | 121.1472 | -0.082397 | -0.33874 | 0.09613 | 0.091553 | 121.1243 | 121.1975 | 121.0602 | 121.1517 | 121.0281 | 121.2387 | 121.1334 | -0.33874 | 121.1517 | 121.0281 | 121.1334 | 121.0602 | 121.2387 | -0.20599 | -121.4813
3296.2812 | 121.2479 | -121.0602 | 0.07782 | 0.00206 | -0.0029822 | 0.0084039 | 0.085733 | -0.027357 | -0.034694 | 0.018901 | 0.009155 | 0.091553 | -0.14191 | 0.10529 | 0.018311 | 0.07782 | 0.036621 | 0.15564 | 0.17853 | -121.4035 | 120.9183 | 0.013733 | 121.0693 | 121.1655 | -0.059509 | -0.34332 | 0.10071 | 0.15106 | 121.0968 | 121.2158 | 121.0785 | 121.1517 | 121.0693 | 121.2387 | 121.138 | -0.34332 | 121.1517 | 121.0693 | 121.138 | 121.0785 | 121.2387 | -0.21973 | -121.4813
3297.9844 | 121.3669 | -121.0648 | 0.059509 | 0.00206 | 8.578e-06 | 0.0084039 | 0.089365 | -0.024793 | -0.032985 | 0.016551 | 0 | 0.086975 | -0.11902 | 0.082397 | -0.009155 | 0.054932 | -0.004578 | 0.086975 | 0.16022 | -121.4355 | 120.9457 | 0.027466 | 121.0648 | 121.1472 | -0.068664 | -0.37079 | 0.10071 | 0.11902 | 121.0602 | 121.1517 | 121.0556 | 121.1517 | 121.0648 | 121.225 | 121.1197 | -0.37079 | 121.1517 | 121.0648 | 121.1197 | 121.0556 | 121.225 | -0.17853 | -121.4951
3299.7031 | 121.3531 | -121.0831 | 0.064087 | 0.00206 | -0.0031958 | 0.0047723 | 0.091501 | -0.023298 | -0.035549 | 0.025951 | 0.004578 | 0.07782 | -0.10529 | 0.082397 | -0.013733 | 0.07782 | -0.027466 | -0.064087 | 0.16022 | -121.431 | 120.9778 | 0.013733 | 121.0876 | 121.1655 | -0.07782 | -0.3479 | 0.09613 | 0.10986 | 121.0556 | 121.019 | 121.0693 | 121.1609 | 121.0876 | 121.2433 | 121.1609 | -0.3479 | 121.1609 | 121.0876 | 121.1609 | 121.0693 | 121.2433 | -0.16937 | -121.4951
3301.4688 | 121.3806 | -121.0968 | 0.07782 | 0.00206 | -0.00063242 | -0.0007819 | 0.081247 | -0.025648 | -0.030849 | 0.017192 | 0.091553 | 0.059509 | -0.054932 | 0.15106 | 0.082397 | 0.18768 | -0.14191 | 0.1831 | 0.12817 | -121.4493 | 121.0419 | -0.018311 | 121.1884 | 121.2479 | 0.004577 | -0.35248 | 0.050354 | 0.14649 | 120.9549 | 121.2799 | 121.1792 | 121.1563 | 121.1884 | 121.225 | 121.2845 | -0.35248 | 121.1563 | 121.1884 | 121.2845 | 121.1792 | 121.225 | -0.13275 | -121.5271
3303.1875 | 121.4218 | -121.0968 | 0.054932 | -0.0055695 | -0.0017004 | 0.0022089 | 0.083597 | -0.025648 | -0.031277 | 0.020183 | 0.045776 | 0.054932 | -0.10986 | 0.14191 | 0.073242 | 0.16937 | -0.10071 | 0.1831 | 0.12817 | -121.4676 | 120.9869 | 0 | 121.1426 | 121.2387 | 0.01831 | -0.37079 | 0.073242 | 0.15564 | 120.9961 | 121.2799 | 121.17 | 121.1517 | 121.1426 | 121.225 | 121.2662 | -0.37079 | 121.1517 | 121.1426 | 121.2662 | 121.17 | 121.225 | -0.16479 | -121.5225
3304.9531 | 121.3623 | -121.1563 | 0.10071 | 0.017319 | -0.0010596 | 0.0073359 | 0.09556 | -0.026075 | -0.035335 | 0.026164 | 0.018311 | 0.073242 | -0.14191 | 0.10071 | -0.004578 | 0.073242 | -0.004578 | 0.004578 | 0.16479 | -121.4447 | 121.0144 | -0.027466 | 121.1746 | 121.257 | -0.10529 | -0.28839 | 0.064087 | 0.16022 | 121.1517 | 121.1609 | 121.1517 | 121.2296 | 121.1746 | 121.3211 | 121.2296 | -0.28839 | 121.2296 | 121.1746 | 121.2296 | 121.1517 | 121.3211 | -0.24262 | -121.5454
3306.6562 | 121.4172 | -121.1426 | 0.082397 | 0.017319 | -0.0012732 | 0.0092585 | 0.10581 | -0.024152 | -0.033626 | 0.037914 | 0.004578 | 0.086975 | -0.13275 | 0.059509 | -0.032043 | 0.050354 | 0.022888 | -0.2655 | 0.16022 | -121.4722 | 121.0098 | 0.004578 | 121.1472 | 121.2021 | -0.11444 | -0.32959 | 0.07782 | 0.13733 | 121.1655 | 120.8771 | 121.1105 | 121.2296 | 121.1472 | 121.3028 | 121.1929 | -0.32959 | 121.2296 | 121.1472 | 121.1929 | 121.1105 | 121.3028 | -0.21515 | -121.5546
3308.3594 | 121.3531 | -121.1838 | 0.054932 | 0.0096895 | -0.0014868 | 0.0051995 | 0.090647 | -0.025434 | -0.033626 | 0.028942 | 0.091553 | 0.059509 | -0.09613 | 0.17853 | 0.091553 | 0.19684 | -0.16022 | 0.10986 | 0.1236 | -121.4401 | 121.0876 | 0.004577 | 121.2753 | 121.3623 | 0.036621 | -0.25635 | 0.068664 | 0.18768 | 121.0236 | 121.2936 | 121.2753 | 121.2433 | 121.2753 | 121.3074 | 121.3806 | -0.25635 | 121.2433 | 121.2753 | 121.3806 | 121.2753 | 121.3074 | -0.15106 | -121.4951
3310.0938 | 121.2982 | -121.2021 | 0.12817 | 0.0096895 | -0.001914 | 0.0086175 | 0.092142 | -0.027143 | -0.030636 | 0.030651 | 0.11444 | 0.050354 | -0.082397 | 0.20599 | 0.13275 | 0.20599 | -0.13275 | 0.086975 | 0.13275 | -121.4813 | 121.1197 | -0.07782 | 121.3165 | 121.4081 | 0.004577 | -0.27924 | 0.004577 | 0.19684 | 121.0693 | 121.2891 | 121.3348 | 121.2524 | 121.3165 | 121.3348 | 121.4081 | -0.27924 | 121.2524 | 121.3165 | 121.4081 | 121.3348 | 121.3348 | -0.21057 | -121.6095
3311.7969 | 121.4264 | -121.1517 | 0.11444 | 0.00206 | -0.0014868 | 0.0041315 | 0.094065 | -0.02757 | -0.03149 | 0.022106 | 0.07782 | 0.050354 | -0.082397 | 0.19684 | 0.11902 | 0.19684 | -0.13275 | 0.23346 | 0.12817 | -121.4996 | 121.0693 | -0.064087 | 121.2296 | 121.3486 | 0.004578 | -0.3479 | 0.013733 | 0.16022 | 121.019 | 121.3852 | 121.2708 | 121.2021 | 121.2296 | 121.2799 | 121.3486 | -0.3479 | 121.2021 | 121.2296 | 121.3486 | 121.2708 | 121.2799 | -0.19684 | -121.6141
3313.5 | 121.4172 | -121.1838 | 0.09613 | 0.00206 | -0.00041862 | 0.0077631 | 0.11415 | -0.026289 | -0.031277 | 0.046031 | 0.004578 | 0.068665 | -0.13733 | 0.09613 | 0.004578 | 0.07782 | 0.041199 | -0.20142 | 0.1831 | -121.5363 | 121.0464 | -0.027465 | 121.1884 | 121.2799 | -0.091552 | -0.35248 | 0.086975 | 0.14191 | 121.225 | 120.9824 | 121.1884 | 121.2524 | 121.1884 | 121.3669 | 121.2616 | -0.35248 | 121.2524 | 121.1884 | 121.2616 | 121.1884 | 121.3669 | -0.23346 | -121.6324
3315.2188 | 121.3898 | -121.2112 | 0.10986 | 0.017319 | -0.001914 | 0.0043451 | 0.08317 | -0.028211 | -0.035122 | 0.016551 | 0.09613 | 0.059509 | -0.09613 | 0.18768 | 0.086975 | 0.16479 | -0.045776 | 0.25635 | 0.14191 | -121.5225 | 121.1151 | -0.050354 | 121.3074 | 121.3989 | -0.022888 | -0.31128 | 0.032044 | 0.19226 | 121.1655 | 121.4676 | 121.2982 | 121.2708 | 121.3074 | 121.3531 | 121.376 | -0.31128 | 121.2708 | 121.3074 | 121.376 | 121.2982 | 121.3531 | -0.20599 | -121.6324
3316.9844 | 115.3519 | -72.7341 | 42.6773 | 0.017319 | -0.00020502 | 0.0090447 | 6.9721 | -0.013898 | -0.019314 | 7.0123 | 0.009155 | 0.050354 | -0.15106 | 0.45319 | -0.6958 | 0.42114 | 0.35248 | 0.21057 | 29.2648 | -60.2509 | 72.583 | -42.627 | 72.7432 | 73.1873 | -43.3731 | 12.4832 | -13.4125 | 0.16022 | 73.0865 | 72.9446 | 72.0383 | 72.7844 | 72.7432 | 101.9989 | 73.1552 | 12.4832 | 72.7844 | 72.7432 | 73.1552 | 72.0383 | 101.9989 | -42.8284 | -102.9282
3318.7031 | 120.7855 | -120.2545 | 0.068665 | 0.0096895 | -0.0017004 | 0.0034905 | 0.14811 | -0.023939 | 0.03516 | 0.14686 | 0.064087 | 0.054932 | -0.086975 | 0.13275 | -120.1859 | 0.15564 | -0.11444 | 0.23346 | 0.13275 | -120.7077 | 120.1675 | -0.013733 | 120.3186 | 120.3873 | -120.2545 | -0.45319 | 0.064086 | 0.15106 | 120.1401 | 120.488 | 0.068665 | 120.3094 | 120.3186 | 120.3873 | 120.4102 | -0.45319 | 120.3094 | 120.3186 | 120.4102 | 0.068665 | 120.3873 | -0.15564 | -120.7764
3320.4688 | 120.5109 | -119.87 | 0.17395 | 0.0096895 | -0.00063242 | 0.0058405 | 0.21049 | -0.023298 | 0.003544 | 0.15776 | 0.022888 | 0.091553 | -0.11444 | 0.082397 | -62.5946 | 0.12817 | -0.07782 | -2.5635 | 0.19684 | -120.433 | 119.7556 | -0.082397 | 119.8929 | 119.9524 | -62.7686 | -0.56305 | 0.022888 | 0.13733 | 119.7922 | 117.3065 | 57.2754 | 119.9615 | 119.8929 | 120.0668 | 119.9982 | -0.56305 | 119.9615 | 119.8929 | 119.9982 | 57.2754 | 120.0668 | -0.28839 | -120.607
3322.1875 | 120.7672 | -120.4376 | 0.07782 | 0.017319 | -0.0017004 | 0.0054131 | 0.087229 | -0.023725 | -0.029995 | 0.020824 | 0.11444 | 0.045776 | -0.086975 | 0.20142 | -1.9547 | 0.19684 | -0.21057 | 0.27008 | 0.11902 | -120.7718 | 120.3506 | -0.032044 | 120.5521 | 120.639 | -2.0325 | -0.33417 | 0.041199 | 0.20142 | 120.2271 | 120.7077 | 118.483 | 120.4834 | 120.5521 | 120.5566 | 120.6345 | -0.33417 | 120.4834 | 120.5521 | 120.6345 | 118.483 | 120.5566 | -0.16479 | -120.8496
3323.9531 | 120.8359 | -120.0806 | 0.36621 | 0.0096895 | 0.0019312 | 0.0060541 | 1.4801 | -0.026502 | 0.028538 | 1.4194 | -0.022888 | 0.086975 | -0.1236 | 0.064087 | -111.2137 | 0.050354 | 0.009155 | -0.09613 | 0.40283 | -120.3186 | 119.957 | -0.27924 | 120.0577 | 120.1447 | -111.5799 | -0.23804 | 0.036621 | 0.10071 | 120.0897 | 119.9844 | 8.8669 | 120.1675 | 120.0577 | 120.4834 | 120.1309 | -0.23804 | 120.1675 | 120.0577 | 120.1309 | 8.8669 | 120.4834 | -0.48981 | -120.6848
3325.6562 | 120.5063 | -118.7714 | 1.561 | 0.024948 | -0.0027686 | 0.0064813 | 6.3152 | -0.02522 | 0.030033 | 6.311 | -0.009155 | 0.091553 | -0.13733 | 0.10529 | -110.582 | 0.09613 | 0.013733 | -0.59052 | 1.2726 | -118.4601 | 118.634 | -1.4694 | 118.7622 | 118.8766 | -112.1429 | 0.31128 | -0.28839 | 0.12817 | 118.7851 | 118.1808 | 8.1894 | 118.8629 | 118.7622 | 120.0439 | 118.8675 | 0.31128 | 118.8629 | 118.7622 | 118.8675 | 8.1894 | 120.0439 | -1.6983 | -120.0211
3327.3906 | 120.9045 | -120.5109 | 0.1236 | -0.0055695 | 0.0012902 | 0.0062677 | 0.38011 | -0.027357 | 0.036656 | 0.39018 | 0.091553 | 0.045776 | -0.086975 | 0.16022 | -119.751 | 0.17853 | -0.14191 | 0.086975 | 0.16022 | -120.8084 | 120.4239 | -0.07782 | 120.6024 | 120.6711 | -119.8746 | -0.29755 | 0.036621 | 0.17853 | 120.369 | 120.5978 | 0.75989 | 120.5566 | 120.6024 | 120.6711 | 120.6894 | -0.29755 | 120.5566 | 120.6024 | 120.6894 | 0.75989 | 120.6711 | -0.21057 | -120.932
3329.0938 | 120.8908 | -120.6345 | 0.07782 | 0.0096895 | -0.0031958 | 0.0032769 | 0.20365 | -0.027784 | 0.034306 | 0.1522 | 0.032043 | 0.054932 | -0.10529 | 0.1236 | -120.0851 | 0.14648 | -0.09613 | -0.004578 | 0.14648 | -120.932 | 120.5292 | -0.022888 | 120.6665 | 120.7581 | -120.163 | -0.29755 | 0.068664 | 0.13733 | 120.5383 | 120.6299 | 0.54932 | 120.6894 | 120.6665 | 120.7809 | 120.7809 | -0.29755 | 120.6894 | 120.6665 | 120.7809 | 0.54932 | 120.7809 | -0.18311 | -121.0098
3330.8125 | 120.607 | -120.1035 | 0.39368 | 0.0096895 | -0.0023412 | 0.0060541 | 1.3109 | -0.024366 | -0.00051485 | 1.2791 | 0.004578 | 0.07782 | -0.15564 | 0.082397 | -59.1019 | 0.064087 | 0.050354 | -2.916 | 0.39825 | -120.2682 | 119.9478 | -0.31586 | 120.108 | 120.1859 | -59.4955 | -0.16479 | 0.004577 | 0.16022 | 120.1538 | 117.1875 | 61.0016 | 120.1813 | 120.108 | 120.5017 | 120.1675 | -0.16479 | 120.1813 | 120.108 | 120.1675 | 61.0016 | 120.5017 | -0.54932 | -120.6619
3332.5469 | 120.607 | -120.1859 | 0.37537 | 0.0096895 | -0.00084602 | 0.0056269 | 1.4783 | -0.024366 | 0.031101 | 1.4779 | 0.10529 | 0.041199 | -0.068665 | 0.21973 | -116.4871 | 0.22888 | -0.20142 | 0.24719 | 0.37994 | -120.2911 | 120.1172 | -0.33417 | 120.2911 | 120.4056 | -116.8625 | -0.10529 | 0.004578 | 0.17395 | 119.9844 | 120.433 | 3.6987 | 120.2271 | 120.2911 | 120.5658 | 120.4147 | -0.10529 | 120.2271 | 120.2911 | 120.4147 | 3.6987 | 120.5658 | -0.44403 | -120.6665
3334.25 | 120.7855 | -120.6116 | 0.1236 | 0.0096895 | -0.0023412 | 0.012035 | 0.093424 | -0.026716 | 0.034947 | 0.092388 | 0.09613 | 0.050354 | -0.082397 | 0.20599 | -117.5034 | 0.20142 | -0.1236 | 0.3067 | 0.10986 | -120.8862 | 120.5292 | -0.073242 | 120.7077 | 120.8176 | -117.627 | -0.27466 | -0.013733 | 0.17853 | 120.488 | 120.9183 | 3.1082 | 120.6619 | 120.7077 | 120.7214 | 120.813 | -0.27466 | 120.6619 | 120.7077 | 120.813 | 3.1082 | 120.7214 | -0.20599 | -121.0098
3335.9844 | 120.7901 | -120.1172 | 0.4303 | 0.0096895 | 0.0029992 | 0.0077631 | 1.1372 | -0.024366 | -0.0191 | 1.1092 | 0.013733 | 0.09613 | -0.13275 | 0.10071 | -19.1483 | 0.073242 | 0.045776 | 0.17853 | 0.3479 | -120.5063 | 119.9844 | -0.33417 | 120.1309 | 120.2179 | -19.5786 | -0.3891 | -0.082398 | 0.14648 | 120.163 | 120.2957 | 100.9689 | 120.2133 | 120.1309 | 120.4651 | 120.1904 | -0.3891 | 120.2133 | 120.1309 | 120.1904 | 100.9689 | 120.4651 | -0.56305 | -120.9366
3337.6875 | 120.6619 | -119.9661 | 0.67749 | 0.0096895 | -0.0021276 | 0.0004999 | 2.2482 | -0.023511 | -0.018886 | 2.2489 | 0.054932 | 0.073242 | -0.10986 | 0.16479 | -27.301 | 0.13275 | -0.032043 | 0.20599 | 0.55389 | -120.1355 | 119.8563 | -0.60425 | 120.0211 | 120.1309 | -27.9785 | -0.16937 | -0.1236 | 0.16479 | 119.9341 | 120.1721 | 92.6651 | 120.0394 | 120.0211 | 120.52 | 120.0989 | -0.16937 | 120.0394 | 120.0211 | 120.0989 | 92.6651 | 120.52 | -0.78735 | -120.813
3339.4375 | 120.9503 | -120.5841 | 0.068665 | 0.0096895 | 8.578e-06 | 0.0024225 | 0.091928 | -0.026075 | 0.010166 | 0.068889 | 0.059509 | 0.064087 | -0.086975 | 0.14648 | -78.6072 | 0.15564 | -0.10986 | 0.21973 | 0.1236 | -120.8267 | 120.4971 | -0.004578 | 120.6436 | 120.7306 | -78.6758 | -0.24262 | 0.054931 | 0.14648 | 120.4742 | 120.8038 | 41.9769 | 120.6482 | 120.6436 | 120.7077 | 120.7397 | -0.24262 | 120.6482 | 120.6436 | 120.7397 | 41.9769 | 120.7077 | -0.15564 | -120.8954
3341.1562 | 120.845 | -120.4742 | 0.27466 | 0.0096895 | -0.0021276 | 0.0002863 | 1.1682 | -0.026502 | -0.016323 | 1.1334 | 0.059509 | 0.064087 | -0.11444 | 0.12817 | -31.4026 | 0.10986 | 0.004578 | 0.20142 | 0.34332 | -120.5704 | 120.3598 | -0.21057 | 120.5338 | 120.6024 | -31.6772 | -0.096131 | 0.068665 | 0.17395 | 120.4788 | 120.6757 | 89.0717 | 120.5383 | 120.5338 | 120.8176 | 120.5841 | -0.096131 | 120.5383 | 120.5338 | 120.5841 | 89.0717 | 120.8176 | -0.3891 | -120.845
3342.9219 | 120.9869 | -120.7169 | 0.059509 | 0.00206 | -0.0017004 | 0.0066949 | 0.10688 | -0.02522 | 0.017643 | 0.088329 | 0.10986 | 0.045776 | -0.1236 | 0.20142 | -88.2797 | 0.19226 | -0.19684 | 0.27924 | 0.10986 | -120.9778 | 120.5933 | -0.013733 | 120.8267 | 120.9183 | -88.3392 | -0.26093 | 0.050354 | 0.23346 | 120.52 | 120.9961 | 32.4371 | 120.7626 | 120.8267 | 120.8267 | 120.9091 | -0.26093 | 120.7626 | 120.8267 | 120.9091 | 32.4371 | 120.8267 | -0.1831 | -121.0373
3344.6406 | 120.9137 | -120.7672 | 0.068665 | 0.0096895 | -0.0017004 | 0.0086175 | 0.072916 | -0.026716 | 0.0073892 | 0.10136 | 0.054932 | 0.064087 | -0.068665 | 0.16022 | -73.0041 | 0.16022 | -0.10529 | 0.24261 | 0.11444 | -119.9432 | 120.6985 | -0.004578 | 120.8221 | 120.9274 | -73.0728 | 0.82398 | 0.045776 | 0.1236 | 120.6619 | 121.0098 | 47.7631 | 120.8313 | 120.8221 | 120.8817 | 120.9274 | 0.82398 | 120.8313 | 120.8221 | 120.9274 | 47.7631 | 120.8817 | -0.13733 | -120.0119
3346.3594 | 120.8954 | -120.0485 | 0.65918 | 0.024948 | -0.0017004 | 0.0049859 | 2.2749 | -0.027784 | 0.010594 | 2.256 | 0.07782 | 0.041199 | -1.8127 | 0.22888 | -74.8169 | 0.2243 | -0.14648 | 0.3067 | 0.5127 | -120.2179 | 118.2358 | -0.61798 | 120.1263 | 120.2774 | -75.4761 | -0.16937 | -0.14648 | 1.8906 | 119.902 | 120.3552 | 45.2316 | 120.0897 | 120.1263 | 120.5612 | 120.2728 | -0.16937 | 120.0897 | 120.1263 | 120.2728 | 45.2316 | 120.5612 | -2.4719 | -120.8771
3348.0938 | 120.7535 | -120.7764 | 0.073242 | 0.00206 | -0.0014868 | 0.0073359 | 0.15132 | -0.027784 | -0.028499 | 0.021465 | 0.059509 | 0.068665 | -0.073242 | 0.17853 | -25.177 | 0.1831 | -0.10071 | 0.27466 | 0.14648 | -120.6757 | 120.7031 | -0.004577 | 120.8359 | 120.9549 | -25.2502 | 0.10071 | 0.073242 | 0.13275 | 120.6757 | 121.051 | 95.5994 | 120.845 | 120.8359 | 120.9229 | 120.9595 | 0.10071 | 120.845 | 120.8359 | 120.9595 | 95.5994 | 120.9229 | -0.14648 | -120.7489
3349.8125 | 116.2628 | -82.8964 | 33.0368 | 0.017319 | -0.0044776 | 0.0060541 | 6.9721 | -0.019453 | -0.0032918 | 7.0123 | -0.29755 | -0.31586 | -1.9547 | 0.71411 | -29.6082 | 0.86517 | 0.41199 | 0.86975 | 22.8973 | -73.0728 | 80.9418 | -33.3527 | 82.5989 | 83.6105 | -62.645 | 9.8236 | -10.1395 | 1.6571 | 83.3084 | 83.7662 | 53.2883 | 82.5806 | 82.5989 | 105.7938 | 83.7616 | 9.8236 | 82.5806 | 82.5989 | 83.7616 | 53.2883 | 105.7938 | -34.9915 | -106.1096
3351.5312 | 120.6848 | -120.1492 | 0.24261 | 0.00206 | 8.578e-06 | 0.0026361 | 0.70802 | -0.024152 | 0.0037576 | 0.70228 | 0.054932 | 0.082397 | -0.89722 | 0.15564 | -64.2014 | 0.1236 | -0.054932 | 0.2243 | 0.27008 | -120.4147 | 119.252 | -0.16022 | 120.2042 | 120.3049 | -64.444 | -0.2655 | 0.027466 | 0.95215 | 120.0943 | 120.3735 | 55.9479 | 120.2316 | 120.2042 | 120.4193 | 120.2728 | -0.2655 | 120.2316 | 120.2042 | 120.2728 | 55.9479 | 120.4193 | -1.1398 | -120.6573
3353.25 | 120.163 | -119.8654 | 0.10529 | 0.0096895 | -0.0021276 | 0.0081903 | 0.1746 | -0.022016 | -0.018459 | 0.13533 | 0.032043 | 0.082397 | -0.14648 | 0.10071 | -25.676 | 0.07782 | -0.022888 | 0.15564 | 0.17395 | -120.1859 | 119.7189 | -0.022889 | 119.8975 | 119.9661 | -25.7812 | -0.32044 | 0.068664 | 0.17853 | 119.8425 | 120.0211 | 94.1895 | 119.9478 | 119.8975 | 120.0394 | 119.9432 | -0.32044 | 119.9478 | 119.8975 | 119.9432 | 94.1895 | 120.0394 | -0.25177 | -120.2911
3355 | 120.5566 | -120.1721 | 0.086975 | 0.0096895 | -0.0031958 | 0.0081903 | 0.23292 | -0.02522 | -0.010555 | 0.18681 | 0.041199 | 0.059509 | -0.086975 | 0.14648 | -34.14 | 0.15106 | -0.11444 | 0.2243 | 0.15564 | -120.4468 | 120.0851 | -0.027466 | 120.2133 | 120.3186 | -34.227 | -0.27466 | 0.068665 | 0.12817 | 120.0577 | 120.3964 | 86.0321 | 120.2316 | 120.2133 | 120.3278 | 120.3232 | -0.27466 | 120.2316 | 120.2133 | 120.3232 | 86.0321 | 120.3278 | -0.17395 | -120.5338
3356.7031 | 120.639 | -120.4422 | 0.07782 | 0.0096895 | -0.0010596 | 0.0009271 | 0.091715 | -0.025861 | 0.0043986 | 0.066112 | 0.10529 | 0.041199 | -0.068665 | 0.2243 | -62.4619 | 0.21515 | -0.14648 | 0.32044 | 0.12817 | -120.7031 | 120.3735 | -0.036621 | 120.5475 | 120.6665 | -62.5397 | -0.26093 | 0.050354 | 0.17395 | 120.2957 | 120.7626 | 57.9803 | 120.4834 | 120.5475 | 120.5704 | 120.6573 | -0.26093 | 120.4834 | 120.5475 | 120.6573 | 57.9803 | 120.5704 | -0.14649 | -120.7809
3358.4062 | 120.6665 | -120.4605 | 0.068665 | 0.00206 | -0.00020502 | 0.0081903 | 0.091715 | -0.026502 | -0.028713 | 0.022533 | -0.013733 | 0.091553 | -0.1236 | 0.10071 | -3.1357 | 0.073242 | 0.041199 | 0.17853 | 0.16479 | -120.7947 | 120.3369 | 0.022888 | 120.4468 | 120.5612 | -3.2043 | -0.33417 | 0.09613 | 0.10986 | 120.5017 | 120.639 | 117.3248 | 120.5521 | 120.4468 | 120.6253 | 120.5338 | -0.33417 | 120.5521 | 120.4468 | 120.5338 | 117.3248 | 120.6253 | -0.19226 | -120.8633
3360.125 | 120.7626 | -120.5017 | 0.073242 | 0.0096895 | 0.0019312 | 0.0064813 | 0.089365 | -0.02522 | -0.032345 | 0.022747 | 0.10529 | 0.036621 | -0.09613 | 0.18768 | -0.059509 | 0.17853 | -0.17853 | 0.26093 | 0.13275 | -120.7947 | 120.4056 | -0.036621 | 120.607 | 120.6894 | -0.13275 | -0.29297 | 0.059509 | 0.20142 | 120.3232 | 120.7626 | 120.4422 | 120.5383 | 120.607 | 120.6345 | 120.6802 | -0.29297 | 120.5383 | 120.607 | 120.6802 | 120.4422 | 120.6345 | -0.16937 | -120.8679
3361.8281 | 120.7901 | -120.5292 | 0.086975 | 0.0096895 | -0.0010596 | 0.0077631 | 0.087656 | -0.026929 | -0.032558 | 0.019115 | 0.10071 | 0.036621 | -0.07782 | 0.20142 | 0.09613 | 0.20599 | -0.19226 | 0.27466 | 0.11444 | -120.8221 | 120.4514 | -0.050354 | 120.6299 | 120.7306 | 0.009155 | -0.29297 | 0.027466 | 0.17853 | 120.3369 | 120.8038 | 120.6253 | 120.5658 | 120.6299 | 120.6436 | 120.7352 | -0.29297 | 120.5658 | 120.6299 | 120.7352 | 120.6253 | 120.6436 | -0.16479 | -120.9091
3363.5469 | 120.7123 | -120.2866 | 0.33417 | 0.017319 | -0.0017004 | 0.0051995 | 1.2959 | -0.025648 | -0.015682 | 1.2237 | 0.004578 | 0.073242 | -0.12817 | 0.1236 | -30.9036 | 0.10071 | 0.036621 | 0.18768 | 0.36163 | -120.4056 | 120.1584 | -0.26092 | 120.2911 | 120.4102 | -31.2378 | -0.11902 | 0.027466 | 0.13275 | 120.3232 | 120.4742 | 89.3829 | 120.3598 | 120.2911 | 120.6482 | 120.3873 | -0.11902 | 120.3598 | 120.2911 | 120.3873 | 89.3829 | 120.6482 | -0.46234 | -120.7397
3365.2812 | 119.7784 | -119.2474 | 0.21515 | 0.00206 | -0.0038366 | 0.0043451 | 0.66401 | -0.024366 | -0.030422 | 0.59782 | 0.10986 | 0.027466 | -0.07782 | 0.18768 | -1.2909 | 0.21515 | -0.1831 | -101.2161 | 0.18768 | -119.5587 | 119.1696 | -0.18768 | 119.3573 | 119.4351 | -1.506 | -0.31128 | -0.027466 | 0.18768 | 119.0643 | 18.0313 | 117.9565 | 119.2749 | 119.3573 | 119.4351 | 119.4626 | -0.31128 | 119.2749 | 119.3573 | 119.4626 | 117.9565 | 119.4351 | -0.29297 | -119.7739
3366.9844 | 120.1492 | -119.8151 | 0.18768 | 0.00206 | -0.0012732 | 0.0054131 | 0.53733 | -0.026289 | -0.027859 | 0.51429 | 0.082397 | 0.068665 | -0.082397 | 0.19684 | -3.6255 | 0.21057 | -0.1236 | -119.1284 | 0.16479 | -120.0302 | 119.7327 | -0.11902 | 119.8975 | 120.0119 | -3.8132 | -0.21515 | -0.022888 | 0.16479 | 119.6915 | 0.68664 | 116.1896 | 119.8837 | 119.8975 | 119.9799 | 120.0256 | -0.21515 | 119.8837 | 119.8975 | 120.0256 | 116.1896 | 119.9799 | -0.27008 | -120.2179
3368.7188 | 120.2362 | -120.0073 | 0.14191 | 0.017319 | -0.0014868 | 0.0017817 | 0.26304 | -0.026716 | -0.030636 | 0.19236 | -0.009155 | 0.091553 | -0.14191 | 0.09613 | -1.973 | 0.054932 | 0.045776 | -119.783 | 0.15106 | -120.2682 | 119.8654 | -0.050354 | 119.9982 | 120.1035 | -2.1149 | -0.26093 | 0.009155 | 0.13275 | 120.0531 | 0.2243 | 118.0344 | 120.0989 | 119.9982 | 120.1584 | 120.0623 | -0.26093 | 120.0989 | 119.9982 | 120.0623 | 118.0344 | 120.1584 | -0.28381 | -120.4102
3370.4531 | 120.2499 | -119.9295 | 0.27008 | 0.017319 | -0.0017004 | 0.0022089 | 0.79667 | -0.024366 | -0.032985 | 0.7277 | 0.009155 | 0.054932 | -0.32044 | 0.13733 | -4.6555 | 0.086975 | 0.032043 | -119.5679 | 0.27008 | -120.1538 | 119.6091 | -0.21515 | 119.9387 | 120.0668 | -4.9255 | -0.22431 | 0 | 0.32959 | 119.9615 | 0.36163 | 115.274 | 119.9844 | 119.9387 | 120.1996 | 120.0165 | -0.22431 | 119.9844 | 119.9387 | 120.0165 | 115.274 | 120.1996 | -0.59052 | -120.4239
3372.1719 | 120.1584 | -119.5358 | 0.45319 | 0.017319 | -0.0017004 | 0.0019953 | 1.4081 | -0.024152 | -0.031917 | 1.2771 | 0.013733 | 0.086975 | -0.14648 | 0.11902 | -7.4524 | 0.09613 | 0.032043 | -116.1301 | 0.35706 | -119.87 | 119.3893 | -0.36621 | 119.5496 | 119.6548 | -7.9056 | -0.33417 | -0.09613 | 0.16022 | 119.5679 | 3.4058 | 112.0834 | 119.6228 | 119.5496 | 119.8929 | 119.632 | -0.33417 | 119.6228 | 119.5496 | 119.632 | 112.0834 | 119.8929 | -0.59967 | -120.3232
3373.875 | 120.3506 | -119.8929 | 0.32501 | 0.024948 | -0.0017004 | 0.0084039 | 1.0041 | -0.022657 | -0.029995 | 0.95158 | 0 | 0.086975 | -0.18768 | 0.10071 | -5.7495 | 0.086975 | 0.041199 | -70.1431 | 0.31586 | -120.1447 | 119.7052 | -0.23804 | 119.8929 | 119.9936 | -6.0745 | -0.25177 | -0.009155 | 0.18768 | 119.9341 | 49.7498 | 114.1434 | 119.9799 | 119.8929 | 120.2087 | 119.9799 | -0.25177 | 119.9799 | 119.8929 | 119.9799 | 114.1434 | 120.2087 | -0.5127 | -120.4697
3375.6094 | 120.488 | -120.1859 | 0.068665 | 0.00206 | -0.0010596 | 0.0045587 | 0.1041 | -0.025434 | -0.031063 | 0.024455 | 0.11902 | 0.045776 | -0.073242 | 0.19226 | -0.022888 | 0.2243 | -0.19226 | -0.47607 | 0.10529 | -120.5154 | 120.1126 | -0.022889 | 120.3049 | 120.3781 | -0.091553 | -0.32959 | 0.036621 | 0.19226 | 119.9936 | 119.7098 | 120.163 | 120.2316 | 120.3049 | 120.2911 | 120.4102 | -0.32959 | 120.2316 | 120.3049 | 120.4102 | 120.163 | 120.2911 | -0.14191 | -120.5841
3377.3281 | 120.3918 | -120.0531 | 0.28839 | 0.017319 | -0.0046912 | 0.0026361 | 0.83128 | -0.025648 | -0.02914 | 0.76957 | 0.10529 | 0.027466 | -0.11444 | 0.23346 | -7.045 | 0.2243 | -0.12817 | -57.193 | 0.24261 | -120.2316 | 119.9387 | -0.26093 | 120.1584 | 120.2866 | -7.3334 | -0.17853 | -0.045776 | 0.21973 | 119.9249 | 62.8601 | 113.0081 | 120.0806 | 120.1584 | 120.2957 | 120.2774 | -0.17853 | 120.0806 | 120.1584 | 120.2774 | 113.0081 | 120.2957 | -0.40283 | -120.52
3379.0469 | 120.5933 | -120.3186 | 0.050354 | 0.0096895 | -0.00020502 | 0.0066949 | 0.083811 | -0.026502 | -0.029995 | 0.018474 | 0.10986 | 0.064087 | -0.073242 | 0.1831 | 0.027466 | 0.18768 | -0.14648 | 0.09613 | 0.13733 | -120.575 | 120.2454 | 0.013733 | 120.4285 | 120.5017 | -0.022888 | -0.25635 | 0.086975 | 0.18311 | 120.1721 | 120.4147 | 120.3461 | 120.3827 | 120.4285 | 120.4559 | 120.5063 | -0.25635 | 120.3827 | 120.4285 | 120.5063 | 120.3461 | 120.4559 | -0.1236 | -120.6253
3380.75 | 120.5246 | -120.1355 | 0.068665 | 0.00206 | -0.0010596 | 0.0024225 | 0.14063 | -0.02522 | -0.028499 | 0.078075 | 0.032043 | 0.050354 | -0.091553 | 0.15564 | -0.68665 | 0.15106 | -0.09613 | -1.2268 | 0.13733 | -120.4651 | 120.0439 | -0.018311 | 120.1675 | 120.2911 | -0.75531 | -0.32959 | 0.068664 | 0.1236 | 120.0394 | 118.9087 | 119.4489 | 120.1859 | 120.1675 | 120.2728 | 120.2866 | -0.32959 | 120.1859 | 120.1675 | 120.2866 | 119.4489 | 120.2728 | -0.16022 | -120.5338
3382.4531 | 120.5383 | -120.3964 | 0.09613 | 0.0096895 | -0.0010596 | 0.0041315 | 0.073984 | -0.026075 | -0.029781 | 0.0062977 | 0.10529 | 0.032043 | -0.091553 | 0.23346 | 0.10529 | 0.20142 | -0.13275 | 0.3067 | 0.13275 | -120.6711 | 120.3049 | -0.064087 | 120.5017 | 120.6299 | 0.009156 | -0.27466 | 0.036621 | 0.19684 | 120.2637 | 120.7031 | 120.5017 | 120.4285 | 120.5017 | 120.5292 | 120.5978 | -0.27466 | 120.4285 | 120.5017 | 120.5978 | 120.5017 | 120.5292 | -0.18768 | -120.7672
3384.1719 | 120.6573 | -120.369 | 0.054932 | 0.0096895 | -0.0010596 | 0.0066949 | 0.079752 | -0.024152 | -0.032772 | 0.0095019 | 0.036621 | 0.059509 | -0.10071 | 0.16022 | -0.004578 | 0.14191 | -0.13733 | 0.16479 | 0.13275 | -120.7123 | 120.2683 | 0.004577 | 120.4056 | 120.5292 | -0.05951 | -0.34332 | 0.077819 | 0.13733 | 120.2316 | 120.5338 | 120.3644 | 120.4285 | 120.4056 | 120.5017 | 120.5109 | -0.34332 | 120.4285 | 120.4056 | 120.5109 | 120.3644 | 120.5017 | -0.15564 | -120.7672
3385.8906 | 120.6345 | -120.4193 | 0.07782 | 0.0096895 | -0.0023412 | 0.0004999 | 0.086374 | -0.026716 | -0.033626 | 0.014629 | -0.013733 | 0.091553 | -0.14191 | 0.10986 | -0.086975 | 0.059509 | 0.07782 | 0.068665 | 0.15564 | -120.7397 | 120.2774 | 0.013733 | 120.4056 | 120.5292 | -0.16479 | -0.32043 | 0.07782 | 0.12817 | 120.4971 | 120.488 | 120.3323 | 120.5109 | 120.4056 | 120.575 | 120.4788 | -0.32043 | 120.5109 | 120.4056 | 120.4788 | 120.3323 | 120.575 | -0.21973 | -120.8176
3387.625 | 120.6436 | -120.4468 | 0.07782 | 0.017319 | -0.00063242 | 0.0043451 | 0.092996 | -0.023511 | -0.034694 | 0.021465 | 0.032043 | 0.073242 | -0.1236 | 0.11902 | -0.10529 | 0.068665 | -0.022888 | 0.004578 | 0.15564 | -120.7443 | 120.3232 | -0.004578 | 120.4788 | 120.5658 | -0.18311 | -0.29755 | 0.07782 | 0.15564 | 120.4239 | 120.4514 | 120.3415 | 120.52 | 120.4788 | 120.6024 | 120.5154 | -0.29755 | 120.52 | 120.4788 | 120.5154 | 120.3415 | 120.6024 | -0.20142 | -120.8221
3389.3906 | 120.5292 | -119.8196 | 0.5127 | 0.00206 | -0.00041862 | 0.0054131 | 1.8917 | -0.023084 | -0.025081 | 1.8422 | -0.009155 | 0.09613 | -0.13733 | 0.10071 | -14.3463 | 0.064087 | 0.022888 | -55.9891 | 0.46234 | -120.0211 | 119.6823 | -0.41657 | 119.8105 | 119.9203 | -14.859 | -0.20142 | -0.050354 | 0.12817 | 119.8425 | 63.8306 | 105.4733 | 119.9158 | 119.8105 | 120.282 | 119.8837 | -0.20142 | 119.9158 | 119.8105 | 119.8837 | 105.4733 | 120.282 | -0.65002 | -120.5338
3391.1094 | 120.5109 | -119.5312 | 0.85144 | 0.0096895 | 0.00022218 | 0.0041315 | 3.0856 | -0.023939 | -0.0054282 | 3.0566 | -0.004578 | 0.068665 | -0.15564 | 0.10529 | -50.5508 | 0.073242 | 0.022888 | -86.4349 | 0.66834 | -119.5908 | 119.3756 | -0.78277 | 119.5267 | 119.6365 | -51.4023 | -0.059509 | -0.1831 | 0.15106 | 119.5541 | 33.0963 | 68.9804 | 119.5999 | 119.5267 | 120.1996 | 119.6045 | -0.059509 | 119.5999 | 119.5267 | 119.6045 | 68.9804 | 120.1996 | -1.0071 | -120.4422
3392.8281 | 120.7581 | -120.433 | 0.091553 | 0.017319 | -0.0010596 | 0.011395 | 0.099191 | -0.026502 | 0.002476 | 0.063976 | 0.11444 | 0.032043 | -0.082397 | 0.21057 | -60.2783 | 0.21057 | -0.21057 | 0.082397 | 0.10529 | -120.7809 | 120.3506 | -0.05951 | 120.5475 | 120.6436 | -60.3699 | -0.3479 | 0.013733 | 0.19684 | 120.2225 | 120.5154 | 60.1547 | 120.4651 | 120.5475 | 120.5383 | 120.6436 | -0.3479 | 120.4651 | 120.5475 | 120.6436 | 60.1547 | 120.5383 | -0.17395 | -120.8725
3394.5469 | 120.5383 | -119.4168 | 0.88806 | 0.0096895 | 0.00064938 | 0.0039179 | 3.3576 | -0.025434 | 0.008671 | 3.3403 | -0.036621 | 0.059509 | -0.16022 | 0.086975 | -79.6738 | 0.082397 | 0.036621 | -35.8933 | 0.74616 | -119.4763 | 119.2566 | -0.82855 | 119.3802 | 119.5038 | -80.5618 | -0.059509 | -0.14191 | 0.1236 | 119.4534 | 83.5236 | 39.743 | 119.4763 | 119.3802 | 120.163 | 119.4992 | -0.059509 | 119.4763 | 119.3802 | 119.4992 | 39.743 | 120.163 | -1.0483 | -120.3644
3396.3125 | 120.7031 | -120.4056 | 0.082397 | 0.017319 | -0.001914 | 0.0032769 | 0.1699 | -0.024793 | -0.034054 | 0.1067 | 0 | 0.082397 | -0.15106 | 0.064087 | -1.1444 | 0.068665 | 0.013733 | -2.3209 | 0.17853 | -120.7352 | 120.2545 | 0 | 120.4056 | 120.4697 | -1.2268 | -0.32959 | 0.096131 | 0.15106 | 120.4193 | 118.0847 | 119.2612 | 120.488 | 120.4056 | 120.5841 | 120.4742 | -0.32959 | 120.488 | 120.4056 | 120.4742 | 119.2612 | 120.5841 | -0.23346 | -120.8176
3398.0938 | 120.5521 | -119.8837 | 0.70953 | -0.0055695 | -0.0014868 | 0.0028497 | 2.1006 | -0.027143 | 0.010807 | 2.0054 | 0.082397 | 0.045776 | -0.10529 | 0.20142 | -76.6846 | 0.20142 | -0.10986 | -84.819 | 0.46234 | -120.0623 | 119.7784 | -0.66376 | 119.9661 | 120.0851 | -77.3941 | -0.17853 | -0.24719 | 0.18768 | 119.7739 | 35.0647 | 43.1992 | 119.9295 | 119.9661 | 120.3461 | 120.0851 | -0.17853 | 119.9295 | 119.9661 | 120.0851 | 43.1992 | 120.3461 | -0.81482 | -120.7718
3399.8438 | 120.8267 | -120.4788 | 0.10529 | 0.017319 | -0.0031958 | 0.0032769 | 0.21967 | -0.02522 | -0.029354 | 0.15477 | 0.045776 | 0.045776 | -0.10071 | 0.17395 | -2.7466 | 0.19226 | -0.10986 | -21.3409 | 0.13733 | -120.8176 | 120.3781 | -0.05951 | 120.5246 | 120.6528 | -2.8519 | -0.33875 | 0.032043 | 0.14648 | 120.369 | 99.1379 | 117.7322 | 120.5246 | 120.5246 | 120.6161 | 120.6711 | -0.33875 | 120.5246 | 120.5246 | 120.6711 | 117.7322 | 120.6161 | -0.20599 | -120.9229
3401.6406 | 120.7718 | -120.5566 | 0.082397 | 0.0096895 | -0.0017004 | 0.0039179 | 0.092142 | -0.028852 | -0.028072 | 0.031078 | -0.027466 | 0.064087 | -0.13275 | 0.091553 | -9.0729 | 0.07782 | 0.064087 | -15.8432 | 0.16479 | -120.8908 | 120.4239 | -0.01831 | 120.5292 | 120.6482 | -9.1553 | -0.33417 | 0.082398 | 0.10529 | 120.6207 | 104.7134 | 111.4838 | 120.6207 | 120.5292 | 120.7214 | 120.6345 | -0.33417 | 120.6207 | 120.5292 | 120.6345 | 111.4838 | 120.7214 | -0.21515 | -120.9732
3403.4375 | 120.7947 | -120.6207 | 0.091553 | 0.0096895 | -0.0029822 | 0.0058405 | 0.094919 | -0.02757 | -0.0064962 | 0.052867 | 0.11444 | 0.041199 | -0.07782 | 0.21515 | -45.3598 | 0.21515 | -0.15106 | -46.6141 | 0.086975 | -120.8954 | 120.5429 | -0.050354 | 120.7352 | 120.8359 | -45.4514 | -0.27466 | -0.004578 | 0.19226 | 120.4697 | 74.0067 | 75.2609 | 120.6619 | 120.7352 | 120.7077 | 120.8359 | -0.27466 | 120.6619 | 120.7352 | 120.8359 | 75.2609 | 120.7077 | -0.16937 | -120.9869
3405.1875 | 120.7764 | -120.6619 | 0.086975 | 0.017319 | -0.0031958 | 0.0062677 | 0.091074 | -0.029066 | 0.00033955 | 0.055217 | 0.09613 | 0.045776 | -0.068665 | 0.21057 | -57.4677 | 0.19226 | -0.11902 | -58.9188 | 0.10071 | -120.9274 | 120.5933 | -0.041199 | 120.7581 | 120.8725 | -57.5546 | -0.2655 | 0.013733 | 0.16479 | 120.5429 | 61.7432 | 63.1943 | 120.7077 | 120.7581 | 120.7626 | 120.8542 | -0.2655 | 120.7077 | 120.7581 | 120.8542 | 63.1943 | 120.7626 | -0.15564 | -121.0144
3406.9844 | 120.7535 | -120.3506 | 0.32501 | 0.00206 | 0.00022218 | 0.0062677 | 0.89558 | -0.028211 | -0.030849 | 0.83302 | 0.10529 | 0.036621 | -0.10529 | 0.20599 | -1.0941 | 0.1831 | -0.054932 | -117.9337 | 0.23346 | -120.6436 | 120.2454 | -0.28839 | 120.4559 | 120.5566 | -1.4191 | -0.29297 | -0.091553 | 0.21057 | 120.2957 | 2.417 | 119.2566 | 120.3873 | 120.4559 | 120.5841 | 120.5338 | -0.29297 | 120.3873 | 120.4559 | 120.5338 | 119.2566 | 120.5841 | -0.4303 | -120.9686
3408.7812 | 120.9595 | -120.6116 | 0.082397 | 0.00206 | -0.0023412 | 0.0092585 | 0.11692 | -0.028211 | -0.031277 | 0.044536 | 0.041199 | 0.054932 | -0.10071 | 0.15564 | 0.022888 | 0.15564 | -0.10986 | -120.3964 | 0.091553 | -120.9686 | 120.5109 | -0.027465 | 120.6528 | 120.7672 | -0.059509 | -0.35706 | 0.009156 | 0.14191 | 120.5017 | 0.21515 | 120.6345 | 120.6665 | 120.6528 | 120.7031 | 120.7672 | -0.35706 | 120.6665 | 120.6528 | 120.7672 | 120.6345 | 120.7031 | -0.18311 | -121.051
3410.5781 | 120.8588 | -120.6573 | 0.10986 | 0.017319 | 0.001504 | 0.010967 | 0.10774 | -0.026716 | 0.030461 | 0.090251 | 0.086975 | 0.07782 | -0.10071 | 0.16937 | -111.6028 | 0.11902 | -0.041199 | -120.3964 | 0.1236 | -120.9732 | 120.5566 | -0.032043 | 120.7443 | 120.8267 | -111.7126 | -0.31586 | 0.013733 | 0.18768 | 120.6161 | 0.26093 | 9.0546 | 120.7352 | 120.7443 | 120.7809 | 120.7764 | -0.31586 | 120.7352 | 120.7443 | 120.7764 | 9.0546 | 120.7809 | -0.21057 | -121.0831
3412.3125 | 120.9457 | -120.5612 | 0.14191 | 0.0096895 | -0.0027686 | 0.0056269 | 0.44718 | -0.027357 | 0.027897 | 0.47392 | -0.018311 | 0.082397 | -0.1236 | 0.082397 | -113.887 | 0.059509 | -0.004578 | -118.5104 | 0.18768 | -120.8176 | 120.4376 | -0.05951 | 120.5429 | 120.6436 | -114.0289 | -0.25635 | 0.045776 | 0.10528 | 120.5566 | 2.0508 | 6.6742 | 120.6436 | 120.5429 | 120.7489 | 120.6207 | -0.25635 | 120.6436 | 120.5429 | 120.6207 | 6.6742 | 120.7489 | -0.2655 | -120.9595
3414.0938 | 120.8633 | -120.7031 | 0.09613 | 0.017319 | -0.00041862 | 0.0056269 | 0.16221 | -0.023511 | 0.027043 | 0.15284 | 0.004578 | 0.09613 | -0.14191 | 0.10071 | -110.1746 | 0.059509 | 0.045776 | -120.2408 | 0.13275 | -120.9869 | 120.5612 | 0 | 120.7077 | 120.8038 | -110.2707 | -0.28381 | 0.036621 | 0.14649 | 120.7489 | 0.46234 | 10.5286 | 120.7993 | 120.7077 | 120.8359 | 120.7626 | -0.28381 | 120.7993 | 120.7077 | 120.7626 | 10.5286 | 120.8359 | -0.23804 | -121.0831
3415.8125 | 120.8405 | -120.7031 | 0.11902 | 0.0096895 | -0.0023412 | 0.0049859 | 0.28462 | -0.023511 | -0.032345 | 0.21458 | 0.045776 | 0.082397 | -0.11902 | 0.12817 | -1.3779 | 0.1236 | -0.036621 | -119.902 | 0.15564 | -120.9457 | 120.5841 | -0.036622 | 120.7489 | 120.8313 | -1.4969 | -0.24262 | 0.036621 | 0.16479 | 120.6665 | 0.80109 | 119.3253 | 120.7855 | 120.7489 | 120.8588 | 120.8267 | -0.24262 | 120.7855 | 120.7489 | 120.8267 | 119.3253 | 120.8588 | -0.23804 | -121.0648
3417.625 | 120.9137 | -120.7581 | 0.10529 | 0.0096895 | -0.001914 | 0.0081903 | 0.092783 | -0.023939 | -0.030636 | 0.021892 | 0.009155 | 0.086975 | -0.1236 | 0.12817 | -0.34332 | 0.10986 | 0 | -120.5658 | 0.13275 | -121.0739 | 120.6345 | -0.018311 | 120.7672 | 120.8862 | -0.44861 | -0.31586 | 0.027465 | 0.13275 | 120.7581 | 0.19226 | 120.4147 | 120.845 | 120.7672 | 120.8908 | 120.8679 | -0.31586 | 120.845 | 120.7672 | 120.8679 | 120.4147 | 120.8908 | -0.22888 | -121.1792
3419.4219 | 121.0007 | -120.7626 | 0.054932 | 0.00206 | -0.0010596 | 0.0039179 | 0.085733 | -0.024366 | -0.034267 | 0.019756 | 0.10529 | 0.050354 | -0.07782 | 0.19226 | -0.054932 | 0.20599 | -0.1831 | -120.52 | 0.059509 | -121.0098 | 120.6848 | -0.004578 | 120.8679 | 120.9549 | -0.10986 | -0.24719 | 0.004577 | 0.18311 | 120.5795 | 0.24261 | 120.7077 | 120.813 | 120.8679 | 120.8221 | 120.9686 | -0.24719 | 120.813 | 120.8679 | 120.9686 | 120.7077 | 120.8221 | -0.13275 | -121.0648
3421.2188 | 119.8471 | -77.3666 | 42.3614 | 0.017319 | 0.001504 | 0.0079767 | 0.51618 | 0.0044733 | -0.006069 | 0.51899 | 0.050354 | 0.054932 | -0.13275 | 0.11444 | -1.1581 | 0.10529 | -0.054932 | -2.4811 | 47.8638 | -72.1161 | 77.2339 | -42.3065 | 77.417 | 77.4811 | -43.5196 | 5.2505 | 5.5023 | 0.18311 | 77.3117 | 74.8856 | 76.2085 | 77.4216 | 77.417 | 125.2304 | 77.4719 | 5.2505 | 77.4216 | 77.417 | 77.4719 | 76.2085 | 125.2304 | -42.4942 | -114.4775
3422.9375 | 120.7169 | -118.2266 | 2.0462 | 0.00206 | -0.0023412 | 0.0056269 | 0.077402 | -0.022443 | -0.031277 | 0.017833 | 0.032043 | 0.064087 | -0.11444 | 0.14648 | 0.059509 | 0.15564 | -0.13275 | 0.2243 | 2.1469 | -118.6752 | 118.1122 | -1.9821 | 118.2587 | 118.3731 | -1.9867 | -0.44861 | 0.10071 | 0.14648 | 118.0939 | 118.4509 | 118.2861 | 118.2907 | 118.2587 | 120.3735 | 118.3823 | -0.44861 | 118.2907 | 118.2587 | 118.3823 | 118.2861 | 120.3735 | -2.1606 | -120.7214
3424.7188 | 121.7606 | -67.5339 | 50.6516 | 0.0096895 | -0.0021276 | 0.0039179 | 0.18165 | -0.0051397 | -0.0092734 | 0.16545 | -0.013733 | 0.073242 | -0.13733 | 0.10071 | -0.19226 | 0.086975 | -0.004578 | -0.32959 | 39.711 | -80.8685 | 67.3965 | -50.5783 | 67.5201 | 67.6346 | -50.8438 | -13.3347 | -10.9406 | 0.1236 | 67.5293 | 67.2043 | 67.3416 | 67.6071 | 67.5201 | 107.2449 | 67.6208 | -13.3347 | 67.6071 | 67.5201 | 67.6208 | 67.3416 | 107.2449 | -50.7889 | -131.5201
3426.4375 | 120.8588 | -119.3985 | 1.0941 | 0.017319 | -0.0031958 | 0.0086175 | 0.09321 | -0.023939 | -0.031063 | 0.040477 | 0.036621 | 0.07782 | -0.13733 | 0.14648 | -0.036621 | 0.16937 | -0.13733 | 0.23804 | 1.387 | -119.6182 | 119.2612 | -1.0162 | 119.4351 | 119.545 | -1.1307 | -0.21973 | 0.29297 | 0.17395 | 119.2612 | 119.6365 | 119.3619 | 119.4763 | 119.4351 | 120.7855 | 119.5679 | -0.21973 | 119.4763 | 119.4351 | 119.5679 | 119.3619 | 120.7855 | -1.2314 | -120.7123
3428.2188 | 120.8771 | -114.6652 | 4.3625 | 0.0096895 | -0.0027686 | 0.0045587 | 0.34785 | -0.021162 | -0.027218 | 0.31477 | 0.09613 | 0.027466 | -0.086975 | 0.19684 | -0.92468 | 0.21515 | -0.20142 | -0.13733 | 6.9031 | -113.8275 | 114.5782 | -4.335 | 114.7614 | 114.8621 | -5.2872 | 0.83771 | 2.5406 | 0.1831 | 114.4638 | 114.5279 | 113.7405 | 114.6927 | 114.7614 | 121.5683 | 114.8804 | 0.83771 | 114.6927 | 114.7614 | 114.8804 | 113.7405 | 121.5683 | -4.4495 | -118.19
3430.0156 | 120.8313 | -119.8929 | 0.84228 | 0.017319 | -0.0021276 | 0.0096857 | 0.092569 | -0.024152 | -0.034481 | 0.024028 | 0.041199 | 0.086975 | -0.13275 | 0.14648 | 0.036621 | 0.10986 | -0.027466 | 0.2243 | 0.88806 | -120.1813 | 119.7601 | -0.75531 | 119.9341 | 120.0394 | -0.80566 | -0.28839 | 0.045777 | 0.17395 | 119.8654 | 120.1172 | 119.9295 | 119.9799 | 119.9341 | 120.7809 | 120.0027 | -0.28839 | 119.9799 | 119.9341 | 120.0027 | 119.9295 | 120.7809 | -0.97504 | -121.0236
3431.7344 | 120.9457 | -119.8425 | 0.85144 | 0.00206 | -0.001914 | 0.0060541 | 0.092996 | -0.023084 | -0.031704 | 0.024883 | 0.022888 | 0.073242 | -0.1236 | 0.13733 | 0.032043 | 0.1236 | -0.10529 | -0.95673 | 0.94757 | -120.0851 | 119.7189 | -0.7782 | 119.8654 | 119.9799 | -0.8194 | -0.24262 | 0.096131 | 0.14648 | 119.7372 | 118.8858 | 119.8746 | 119.9158 | 119.8654 | 120.7901 | 119.9661 | -0.24262 | 119.9158 | 119.8654 | 119.9661 | 119.8746 | 120.7901 | -0.97504 | -120.9366
3433.5156 | 120.8817 | -120.0073 | 0.81482 | 0.0096895 | -0.0017004 | 0.0058405 | 0.090006 | -0.026289 | -0.032131 | 0.021465 | 0.091553 | 0.059509 | -0.082397 | 0.18768 | 0.10529 | 0.18768 | -0.07782 | 0.33417 | 0.8606 | -120.2774 | 119.9249 | -0.75531 | 120.0989 | 120.195 | -0.70953 | -0.27008 | 0.045777 | 0.17395 | 119.9295 | 120.3415 | 120.1126 | 120.0668 | 120.0989 | 120.8679 | 120.195 | -0.27008 | 120.0668 | 120.0989 | 120.195 | 120.1126 | 120.8679 | -0.89722 | -121.0922
3435.3125 | 120.9961 | -120.1035 | 0.63629 | 0.00206 | -0.0021276 | 0.0022089 | 0.092569 | -0.027784 | -0.029995 | 0.026164 | 0.045776 | 0.059509 | -0.086975 | 0.16022 | 0.041199 | 0.17395 | -0.11444 | 0.23804 | 0.68665 | -120.4788 | 120.0165 | -0.57678 | 120.1492 | 120.2637 | -0.59509 | -0.37537 | 0.050354 | 0.13275 | 119.989 | 120.3415 | 120.1447 | 120.163 | 120.1492 | 120.7901 | 120.2774 | -0.37537 | 120.163 | 120.1492 | 120.2774 | 120.1447 | 120.7901 | -0.72327 | -121.1151
3437.0469 | 121.051 | -120.1401 | 0.61798 | 0.0096895 | -0.0014868 | 0.0034905 | 0.10603 | -0.026502 | -0.032985 | 0.025737 | -0.004578 | 0.082397 | -0.13275 | 0.091553 | -0.004578 | 0.064087 | -0.027466 | 0.14191 | 0.70953 | -120.5017 | 120.0073 | -0.53558 | 120.1355 | 120.2316 | -0.62256 | -0.36163 | 0.091553 | 0.12817 | 120.1126 | 120.282 | 120.1355 | 120.2225 | 120.1355 | 120.8496 | 120.2042 | -0.36163 | 120.2225 | 120.1355 | 120.2042 | 120.1355 | 120.8496 | -0.75073 | -121.1197
3438.8281 | 121.0556 | -119.4946 | 1.2817 | -0.0055695 | -0.0010596 | 0.0028497 | 0.13999 | -0.026929 | -0.031704 | 0.066966 | 0.045776 | 0.045776 | -0.10071 | 0.16479 | 0.064087 | 0.16937 | -0.11444 | 0.26093 | 0.99335 | -120.1996 | 119.3939 | -1.236 | 119.5404 | 119.6594 | -1.2177 | -0.70496 | -0.28839 | 0.14648 | 119.3802 | 119.7556 | 119.5587 | 119.5404 | 119.5404 | 120.488 | 119.664 | -0.70496 | 119.5404 | 119.5404 | 119.664 | 119.5587 | 120.488 | -1.3824 | -121.4813
3440.5469 | 120.9961 | -120.3598 | 0.50812 | 0.024948 | -0.0031958 | 0.0043451 | 0.086374 | -0.02757 | -0.031917 | 0.015697 | -0.022888 | 0.086975 | -0.12817 | 0.091553 | 0.009155 | 0.064087 | 0.050354 | 0.15106 | 0.6134 | -120.6665 | 120.2316 | -0.42114 | 120.3369 | 120.4514 | -0.49896 | -0.3067 | 0.10529 | 0.10529 | 120.4102 | 120.5109 | 120.369 | 120.4468 | 120.3369 | 120.9732 | 120.4239 | -0.3067 | 120.4468 | 120.3369 | 120.4239 | 120.369 | 120.9732 | -0.63629 | -121.1746
3442.2812 | 120.9549 | -119.0598 | 1.7212 | -0.013199 | -0.0014868 | 0.0043451 | 0.096201 | -0.027143 | -0.031277 | 0.030864 | 0.10529 | 0.050354 | -0.073242 | 0.21515 | 0.091553 | 0.21515 | -0.15106 | 0.33417 | 0.78735 | -120.401 | 118.9865 | -1.6708 | 119.165 | 119.2749 | -1.6296 | -1.3412 | -0.93384 | 0.17853 | 118.9087 | 119.3939 | 119.1513 | 119.1101 | 119.165 | 119.8471 | 119.2749 | -1.3412 | 119.1101 | 119.165 | 119.2749 | 119.1513 | 119.8471 | -1.7944 | -122.1222
3444.0625 | 120.9824 | -120.4651 | 0.44861 | 0.00206 | -0.0010596 | 0.0041315 | 0.098337 | -0.027357 | -0.032345 | 0.029369 | 0.07782 | 0.045776 | -0.082397 | 0.19684 | 0.09613 | 0.17395 | -0.045776 | 0.27466 | 0.57678 | -120.6848 | 120.3827 | -0.40283 | 120.5429 | 120.6619 | -0.35248 | -0.21973 | 0.12817 | 0.16022 | 120.4193 | 120.7397 | 120.5612 | 120.5109 | 120.5429 | 121.0419 | 120.639 | -0.21973 | 120.5109 | 120.5429 | 120.639 | 120.5612 | 121.0419 | -0.531 | -121.1334
3445.8438 | 120.9366 | -118.5196 | 2.4124 | 0.0096895 | -0.001914 | 0.0092585 | 0.28932 | -0.024152 | -0.032985 | 0.2227 | 0.050354 | 0.073242 | -0.10986 | 0.15106 | -0.14648 | 0.10986 | -0.036621 | 0.20142 | 1.767 | -119.3619 | 118.4097 | -2.3392 | 118.5699 | 118.6707 | -2.5589 | -0.84229 | -0.64545 | 0.16022 | 118.483 | 118.721 | 118.3731 | 118.5928 | 118.5699 | 120.2866 | 118.6295 | -0.84229 | 118.5928 | 118.5699 | 118.6295 | 118.3731 | 120.2866 | -2.5223 | -121.7743
3447.5938 | 121.1014 | -119.8654 | 1.0666 | 0.00206 | -0.0031958 | 0.0051995 | 0.25065 | -0.025434 | -0.032772 | 0.1757 | 0.082397 | 0.050354 | -0.073242 | 0.19684 | 0.009155 | 0.20599 | -0.13733 | 0.30212 | 1.4374 | -119.783 | 119.7922 | -1.0162 | 119.9478 | 120.0623 | -1.0574 | 0.082397 | 0.37079 | 0.15564 | 119.7281 | 120.1675 | 119.8746 | 119.9158 | 119.9478 | 121.3028 | 120.0714 | 0.082397 | 119.9158 | 119.9478 | 120.0714 | 119.8746 | 121.3028 | -1.1398 | -120.8496
3449.375 | 121.1197 | -120.3049 | 0.60883 | -0.0055695 | -0.002555 | 0.0022089 | 0.11585 | -0.026075 | -0.030422 | 0.050518 | 0.091553 | 0.050354 | -0.091553 | 0.16937 | 0.064087 | 0.17395 | -0.13275 | 0.082397 | 0.66376 | -120.6024 | 120.2133 | -0.55847 | 120.3964 | 120.4742 | -0.54474 | -0.29755 | 0.054931 | 0.18311 | 120.1721 | 120.3873 | 120.369 | 120.3552 | 120.3964 | 120.9686 | 120.4788 | -0.29755 | 120.3552 | 120.3964 | 120.4788 | 120.369 | 120.9686 | -0.70038 | -121.2112
3451.1719 | 121.0648 | -120.1172 | 0.82398 | 0.00206 | 0.00043578 | 0.01054 | 0.11778 | -0.026929 | -0.03149 | 0.053935 | 0.11444 | 0.050354 | -0.09613 | 0.24719 | 0 | 0.21515 | -0.14191 | 0.22888 | 0.95215 | -120.3461 | 120.0211 | -0.77362 | 120.2316 | 120.3644 | -0.82398 | -0.22888 | 0.12817 | 0.21057 | 119.9753 | 120.3461 | 120.1172 | 120.1675 | 120.2316 | 121.0693 | 120.3323 | -0.22888 | 120.1675 | 120.2316 | 120.3323 | 120.1172 | 121.0693 | -0.9201 | -121.17
3452.9062 | 121.0876 | -120.0302 | 0.94299 | 0.0096895 | -0.0040502 | 0.0030633 | 0.12504 | -0.027784 | -0.032131 | 0.05244 | -0.004578 | 0.10529 | -0.12817 | 0.091553 | -0.050354 | 0.07782 | 0.068665 | 0.13733 | 0.91553 | -120.4056 | 119.902 | -0.83771 | 120.0256 | 120.1218 | -0.99335 | -0.37537 | -0.027466 | 0.1236 | 120.0989 | 120.1675 | 119.9799 | 120.1355 | 120.0256 | 120.9457 | 120.108 | -0.37537 | 120.1355 | 120.0256 | 120.108 | 119.9799 | 120.9457 | -1.0712 | -121.3486
3454.7031 | 121.1884 | -120.0394 | 0.90637 | 0.0096895 | 8.578e-06 | 0.0043451 | 0.18806 | -0.025861 | -0.031063 | 0.13404 | 0.059509 | 0.059509 | -0.09613 | 0.17853 | -0.07782 | 0.17395 | -0.11902 | 0.3067 | 1.3275 | -119.9982 | 119.9432 | -0.84686 | 120.0989 | 120.2179 | -0.98419 | 0.041199 | 0.42114 | 0.15564 | 119.9203 | 120.3461 | 119.9615 | 120.0989 | 120.0989 | 121.3669 | 120.2133 | 0.041199 | 120.0989 | 120.0989 | 120.2133 | 119.9615 | 121.3669 | -1.0025 | -120.9045
3456.4375 | 121.17 | -120.4605 | 0.41657 | 0.00206 | -0.00063242 | 0.0090447 | 0.13337 | -0.025434 | -0.034267 | 0.054149 | 0.064087 | 0.054932 | -0.11444 | 0.20599 | 0.054932 | 0.18768 | -0.16937 | 0.2655 | 0.55389 | -120.726 | 120.3461 | -0.36163 | 120.5246 | 120.6665 | -0.36163 | -0.2655 | 0.13733 | 0.17853 | 120.2911 | 120.726 | 120.5154 | 120.5154 | 120.5246 | 121.0144 | 120.6482 | -0.2655 | 120.5154 | 120.5246 | 120.6482 | 120.5154 | 121.0144 | -0.53101 | -121.1426
3458.25 | 121.0693 | -120.5429 | 0.47607 | 0.017319 | 0.00064938 | 0.0092585 | 0.11949 | -0.023725 | -0.037472 | 0.045391 | 0.064087 | 0.068665 | -0.11444 | 0.15106 | 0.036621 | 0.10529 | -0.050354 | 0.20599 | 0.48523 | -121.0281 | 120.4285 | -0.40741 | 120.607 | 120.694 | -0.43945 | -0.48523 | 0.009155 | 0.17853 | 120.4926 | 120.7489 | 120.5795 | 120.6116 | 120.607 | 121.0281 | 120.6482 | -0.48523 | 120.6116 | 120.607 | 120.6482 | 120.5795 | 121.0281 | -0.59052 | -121.5042
3460.0469 | 121.0602 | -120.6024 | 0.43488 | 0.024948 | -0.0010596 | 0.0037043 | 0.11244 | -0.024366 | -0.033199 | 0.049236 | 0.045776 | 0.059509 | -0.11902 | 0.14648 | 0.009155 | 0.10071 | -0.036621 | 0.19684 | 0.54932 | -120.8542 | 120.4834 | -0.37537 | 120.6482 | 120.7489 | -0.42572 | -0.25177 | 0.11444 | 0.16479 | 120.5658 | 120.7993 | 120.6116 | 120.6619 | 120.6482 | 121.1517 | 120.7031 | -0.25177 | 120.6619 | 120.6482 | 120.7031 | 120.6116 | 121.1517 | -0.55389 | -121.2891
3461.7812 | 121.1838 | -120.52 | 0.45776 | 0.0096895 | -0.0023412 | 0.0069085 | 0.097483 | -0.028638 | -0.031704 | 0.023387 | 0.10071 | 0.027466 | -0.091553 | 0.17853 | 0.11444 | 0.20142 | -0.17395 | 0.27924 | 0.44861 | -120.9091 | 120.4285 | -0.4303 | 120.6207 | 120.6985 | -0.34332 | -0.3891 | -0.009156 | 0.19226 | 120.3461 | 120.7993 | 120.6345 | 120.5475 | 120.6207 | 120.9686 | 120.7214 | -0.3891 | 120.5475 | 120.6207 | 120.7214 | 120.6345 | 120.9686 | -0.54932 | -121.3669
3463.5625 | 121.1105 | -120.4971 | 0.50812 | 0.0096895 | -0.00041862 | 0.0088311 | 0.098978 | -0.024152 | -0.034054 | 0.026805 | 0.041199 | 0.073242 | -0.10529 | 0.10986 | 0.032043 | 0.09613 | -0.013733 | 0.17853 | 0.60425 | -120.8267 | 120.3918 | -0.43488 | 120.5383 | 120.607 | -0.47607 | -0.32959 | 0.09613 | 0.14649 | 120.4834 | 120.6757 | 120.5292 | 120.5704 | 120.5383 | 121.1014 | 120.5933 | -0.32959 | 120.5704 | 120.5383 | 120.5933 | 120.5292 | 121.1014 | -0.6134 | -121.3348
3465.375 | 121.1746 | -120.5566 | 0.52185 | 0.00206 | -0.0029822 | 0.0056269 | 0.099619 | -0.026502 | -0.032131 | 0.032146 | 0.086975 | 0.064087 | -0.07782 | 0.15564 | 0.10071 | 0.15564 | -0.036621 | 0.2655 | 0.60883 | -120.8496 | 120.4788 | -0.45776 | 120.6436 | 120.7123 | -0.42114 | -0.29297 | 0.086975 | 0.16479 | 120.52 | 120.8221 | 120.6573 | 120.6207 | 120.6436 | 121.1655 | 120.7123 | -0.29297 | 120.6207 | 120.6436 | 120.7123 | 120.6573 | 121.1655 | -0.59967 | -121.3715
3467.125 | 121.1746 | -120.4834 | 0.55847 | 0.0096895 | -0.00041862 | 0.0028497 | 0.09791 | -0.027998 | -0.030422 | 0.022747 | 0.10986 | 0.041199 | -0.07782 | 0.20599 | 0.13733 | 0.20599 | -0.19684 | 0.29297 | 0.5127 | -120.8908 | 120.4056 | -0.51727 | 120.5933 | 120.6894 | -0.42114 | -0.40741 | -0.045777 | 0.18768 | 120.2866 | 120.7764 | 120.6207 | 120.5246 | 120.5933 | 120.9961 | 120.6894 | -0.40741 | 120.5246 | 120.5933 | 120.6894 | 120.6207 | 120.9961 | -0.63629 | -121.4493
3468.9062 | 121.2021 | -120.5795 | 0.46234 | 0.00206 | -0.0029822 | 0.0056269 | 0.090433 | -0.028425 | -0.031277 | 0.019756 | 0.10529 | 0.054932 | -0.082397 | 0.20599 | 0.15106 | 0.19684 | -0.10986 | 0.32044 | 0.48065 | -120.9503 | 120.4971 | -0.40741 | 120.6848 | 120.7855 | -0.31128 | -0.37079 | 0.018311 | 0.18768 | 120.4697 | 120.9 | 120.7306 | 120.6345 | 120.6848 | 121.0602 | 120.7764 | -0.37079 | 120.6345 | 120.6848 | 120.7764 | 120.7306 | 121.0602 | -0.54474 | -121.4127
3470.6875 | 121.1014 | -120.0806 | 0.86517 | 0.0096895 | -0.00020502 | 0.0084039 | 0.12205 | -0.027357 | -0.033199 | 0.056285 | 0.050354 | 0.068665 | -0.11902 | 0.13733 | 0.027466 | 0.10529 | -0.022888 | 0.16022 | 0.99335 | -120.4193 | 119.9615 | -0.79651 | 120.1309 | 120.2179 | -0.83771 | -0.33875 | 0.12817 | 0.16937 | 120.0577 | 120.2408 | 120.108 | 120.1492 | 120.1309 | 121.0739 | 120.1859 | -0.33875 | 120.1492 | 120.1309 | 120.1859 | 120.108 | 121.0739 | -0.98419 | -121.2845
3472.4844 | 121.2158 | -120.4376 | 0.72327 | 0.0096895 | -0.0017004 | 0.0079767 | 0.13807 | -0.02757 | -0.030636 | 0.073589 | 0.10986 | 0.054932 | -0.091553 | 0.22888 | 0.16479 | 0.2243 | -0.13733 | 0.33875 | 0.737 | -120.7626 | 120.3461 | -0.66834 | 120.5475 | 120.6665 | -0.55847 | -0.32501 | 0.013733 | 0.20142 | 120.3003 | 120.7764 | 120.6024 | 120.4926 | 120.5475 | 121.1746 | 120.6619 | -0.32501 | 120.4926 | 120.5475 | 120.6619 | 120.6024 | 121.1746 | -0.81482 | -121.4859
3474.2188 | 121.3394 | -120.5017 | 0.57678 | 0.0096895 | -0.0027686 | 0.0069085 | 0.10859 | -0.028638 | -0.030422 | 0.045177 | 0.050354 | 0.064087 | -0.073242 | 0.14191 | 0.064087 | 0.14648 | -0.10071 | 0.23804 | 0.59967 | -120.8679 | 120.4285 | -0.5127 | 120.5521 | 120.6436 | -0.5127 | -0.36621 | 0.022888 | 0.1236 | 120.401 | 120.7397 | 120.5658 | 120.5658 | 120.5521 | 121.1014 | 120.6482 | -0.36621 | 120.5658 | 120.5521 | 120.6482 | 120.5658 | 121.1014 | -0.65002 | -121.4447
3476.0156 | 121.1975 | -120.6482 | 0.47607 | 0.024948 | -0.0014868 | 0.0075495 | 0.11564 | -0.027357 | -0.035335 | 0.037486 | -0.009155 | 0.086975 | -0.12817 | 0.10529 | 0.018311 | 0.064087 | 0.068665 | 0.19684 | 0.58594 | -120.9274 | 120.52 | -0.3891 | 120.639 | 120.7535 | -0.45776 | -0.27924 | 0.10986 | 0.11902 | 120.7169 | 120.845 | 120.6665 | 120.7352 | 120.639 | 121.2341 | 120.7123 | -0.27924 | 120.7352 | 120.639 | 120.7123 | 120.6665 | 121.2341 | -0.60425 | -121.4035
3477.75 | 119.632 | -9.8923 | 109.5886 | 0.0096895 | -0.0034094 | 0.0056269 | 0.041513 | 0.035662 | 0.028111 | 0.14451 | 0.086975 | -0.004578 | -0.1236 | 0.16022 | 0 | 0.17853 | -0.23804 | 0.20142 | 109.6161 | -10.1166 | 9.7687 | -109.5932 | 9.9792 | 10.0525 | -109.5886 | -0.2243 | 0.027466 | 0.21057 | 9.6542 | 10.0937 | 9.8923 | 9.8877 | 9.9792 | 119.5084 | 10.0708 | -0.2243 | 9.8877 | 9.9792 | 10.0708 | 9.8923 | 119.5084 | -109.7122 | -119.7052
3479.5312 | 120.6619 | -13.9389 | 106.7459 | 0.0096895 | -0.0031958 | 0.0060541 | 0.051981 | 0.033953 | 0.026402 | 0.14878 | 0.009155 | 0.022888 | -0.14191 | 0.12817 | -0.032043 | 0.13275 | -0.17395 | 0.082397 | 107.0572 | -14.1129 | 13.797 | -106.723 | 13.9481 | 14.0671 | -106.778 | -0.17395 | 0.31128 | 0.15106 | 13.765 | 14.0213 | 13.9069 | 13.9618 | 13.9481 | 120.9961 | 14.0717 | -0.17395 | 13.9618 | 13.9481 | 14.0717 | 13.9069 | 120.9961 | -106.8878 | -120.8588
3481.2656 | 108.6502 | -54.6753 | 66.0233 | 0.00206 | -0.003623 | 0.0075495 | 0.058176 | 0.0070367 | 0.0014078 | 0.085765 | -0.032043 | 0.050354 | -0.14648 | 0.091553 | -0.036621 | 0.059509 | 0.022888 | 0.10071 | 64.4577 | -56.813 | 54.5288 | -65.9729 | 54.6433 | 54.7668 | -66.0599 | -2.1378 | -1.5656 | 0.11444 | 54.6982 | 54.776 | 54.6387 | 54.7256 | 54.6433 | 119.133 | 54.7348 | -2.1378 | 54.7256 | 54.6433 | 54.7348 | 54.6387 | 119.133 | -66.1697 | -122.8363
3483.0625 | 121.3486 | -117.6041 | 3.392 | 0.0096895 | -0.0040502 | 0.0026361 | 0.56553 | -0.0032171 | -0.0064962 | 0.55488 | 0.041199 | 0.027466 | -0.09613 | 0.1831 | -0.064087 | 0.16479 | -0.12817 | 1.5656 | 41.8167 | -81.0425 | 117.5079 | -3.3646 | 117.6453 | 117.7872 | -3.4561 | 36.5616 | 38.4247 | 0.13733 | 117.4759 | 119.1696 | 117.54 | 117.6315 | 117.6453 | 159.4208 | 117.7689 | 36.5616 | 117.6315 | 117.6453 | 117.7689 | 117.54 | 159.4208 | -3.4882 | -84.4345
3484.8594 | 121.2753 | -118.8309 | 2.0416 | 0.0096895 | -0.00041862 | 0.0096857 | 0.089365 | -0.023084 | -0.029995 | 0.010997 | 0.1236 | 0.036621 | -0.064087 | 0.20142 | 0.11902 | 0.20142 | -0.19226 | 0.4303 | 1.9318 | -119.4031 | 118.7668 | -2.005 | 118.9545 | 119.0323 | -1.9226 | -0.5722 | -0.10986 | 0.18768 | 118.6386 | 119.2612 | 118.9499 | 118.8675 | 118.9545 | 120.7626 | 119.0323 | -0.5722 | 118.8675 | 118.9545 | 119.0323 | 118.9499 | 120.7626 | -2.1057 | -121.4447
3486.6562 | 121.2158 | -119.1605 | 1.8082 | 0.0096895 | -0.00020502 | 0.0064813 | 0.11607 | -0.023298 | -0.031917 | 0.041759 | 0.036621 | 0.07782 | -0.11444 | 0.13733 | 0.032043 | 0.10071 | -0.018311 | 0.41199 | 1.9135 | -119.4672 | 119.046 | -1.7303 | 119.1971 | 119.2978 | -1.7761 | -0.3067 | 0.10528 | 0.15106 | 119.1422 | 119.5724 | 119.1925 | 119.2383 | 119.1971 | 121.0739 | 119.2612 | -0.3067 | 119.2383 | 119.1971 | 119.2612 | 119.1925 | 121.0739 | -1.9226 | -121.2753
3488.3906 | 121.3165 | -120.3827 | 0.54016 | 0.017319 | -0.00020502 | 0.0081903 | 0.087015 | -0.023939 | -0.034908 | 0.015697 | 0.09613 | 0.041199 | -0.07782 | 0.20142 | 0.10529 | 0.20142 | -0.1831 | 0.40283 | 0.60883 | -120.7443 | 120.3049 | -0.49896 | 120.4788 | 120.5841 | -0.43488 | -0.36163 | 0.068665 | 0.17395 | 120.1996 | 120.7855 | 120.488 | 120.4239 | 120.4788 | 120.9915 | 120.5841 | -0.36163 | 120.4239 | 120.4788 | 120.5841 | 120.488 | 120.9915 | -0.61798 | -121.2845
3490.1875 | 121.3486 | -120.0806 | 0.91095 | 0.00206 | -0.0010596 | 0.0058405 | 0.41685 | -0.027357 | -0.031277 | 0.33827 | 0.036621 | 0.050354 | -0.082397 | 0.15564 | 0.07782 | 0.15564 | -0.10529 | 0.3891 | 1.0803 | -120.3232 | 119.9982 | -0.8606 | 120.1172 | 120.2362 | -0.83313 | -0.24262 | 0.16937 | 0.11902 | 119.9753 | 120.4697 | 120.1584 | 120.1309 | 120.1172 | 121.1609 | 120.2362 | -0.24262 | 120.1309 | 120.1172 | 120.2362 | 120.1584 | 121.1609 | -0.99335 | -121.2341
3491.9688 | 121.3348 | -103.7521 | 17.0929 | 0.017319 | -0.0066138 | 0.0060541 | 0.20686 | -0.0098395 | -0.015255 | 0.1851 | 0.027466 | 0.041199 | -0.09613 | 0.14648 | -0.036621 | 0.15106 | -0.1236 | 0.25177 | 34.9869 | -85.7071 | 103.656 | -17.0517 | 103.7796 | 103.8986 | -17.1295 | 18.045 | 17.894 | 0.1236 | 103.6285 | 104.0039 | 103.7155 | 103.7933 | 103.7796 | 138.739 | 103.9032 | 18.045 | 103.7933 | 103.7796 | 103.9032 | 103.7155 | 138.739 | -17.189 | -102.8
3493.75 | 121.4447 | -119.9295 | 1.0345 | 0.017319 | 0.00064938 | 0.0041315 | 0.12846 | -0.024366 | -0.033626 | 0.043895 | -0.004578 | 0.09613 | -0.13733 | 0.073242 | -0.004578 | 0.064087 | -0.009155 | 0.16937 | 1.1444 | -120.3506 | 119.7922 | -0.93842 | 119.9249 | 120.0027 | -1.0391 | -0.42114 | 0.10986 | 0.13275 | 119.9203 | 120.0989 | 119.9249 | 120.0256 | 119.9249 | 121.0739 | 119.9936 | -0.42114 | 120.0256 | 119.9249 | 119.9936 | 119.9249 | 121.0739 | -1.1719 | -121.3852
3495.4688 | 121.3943 | -119.5633 | 1.5289 | 0.0096895 | -0.0021276 | 0.0051995 | 0.089792 | -0.023298 | -0.030208 | 0.029582 | 0.10986 | 0.022888 | -0.064087 | 0.20142 | 0.10071 | 0.21515 | -0.19684 | 0.28839 | 1.6067 | -119.8288 | 119.4992 | -1.506 | 119.6732 | 119.7647 | -1.4282 | -0.2655 | 0.077819 | 0.17395 | 119.3665 | 119.8517 | 119.664 | 119.5862 | 119.6732 | 121.17 | 119.7784 | -0.2655 | 119.5862 | 119.6732 | 119.7784 | 119.664 | 121.17 | -1.593 | -121.3577
3497.25 | 121.344 | -119.6182 | 1.4648 | 0.017319 | -0.00063242 | 0.0066949 | 0.09791 | -0.022443 | -0.033413 | 0.026164 | 0.041199 | 0.068665 | -0.1236 | 0.11444 | 0.004578 | 0.086975 | -0.027466 | 0.1236 | 1.4099 | -120.0851 | 119.4946 | -1.3962 | 119.6594 | 119.7327 | -1.4603 | -0.46692 | -0.054932 | 0.16479 | 119.5908 | 119.7418 | 119.6228 | 119.6869 | 119.6594 | 121.0281 | 119.7052 | -0.46692 | 119.6869 | 119.6594 | 119.7052 | 119.6228 | 121.0281 | -1.5884 | -121.55
3499.0312 | 120.2042 | -120.0073 | 0.13733 | 0.017319 | -0.00020502 | 0.0039179 | 0.072061 | -0.026929 | -0.032772 | 0.0018115 | 0.1236 | 0.050354 | -0.091553 | 0.21057 | 0.13275 | 0.21973 | -0.13275 | 0.32044 | 0.11902 | -120.2957 | 119.9158 | -0.086975 | 120.1309 | 120.2179 | -0.004578 | -0.28839 | -0.01831 | 0.21515 | 119.8746 | 120.3278 | 120.1401 | 120.0577 | 120.1309 | 120.1263 | 120.2271 | -0.28839 | 120.0577 | 120.1309 | 120.2271 | 120.1401 | 120.1263 | -0.22888 | -120.433
3500.8281 | 120.9824 | -120.6573 | 0.059509 | 0.0096895 | -0.00020502 | 0.0060541 | 0.077402 | -0.023298 | -0.028286 | 0.0020251 | 0.032043 | 0.07782 | -0.12817 | 0.11444 | -0.51727 | 0.1236 | -0.091553 | 0.1831 | 0.14191 | -120.9915 | 120.5292 | 0.018311 | 120.6894 | 120.7718 | -0.57678 | -0.33417 | 0.082398 | 0.16022 | 120.5658 | 120.8405 | 120.1401 | 120.7352 | 120.6894 | 120.7993 | 120.7809 | -0.33417 | 120.7352 | 120.6894 | 120.7809 | 120.1401 | 120.7993 | -0.18768 | -121.051
3502.6406 | 121.0968 | -120.7489 | 0.059509 | 0.017319 | -0.0049048 | 0.0002863 | 0.076761 | -0.027784 | -0.030636 | 0.0097157 | 0.018311 | 0.045776 | -0.10071 | 0.14191 | -0.4303 | 0.16022 | -0.086975 | 0.24261 | 0.13733 | -121.051 | 120.6482 | -0.013733 | 120.7672 | 120.8908 | -0.48981 | -0.30212 | 0.07782 | 0.11902 | 120.6619 | 120.9915 | 120.3186 | 120.7947 | 120.7672 | 120.8862 | 120.9091 | -0.30212 | 120.7947 | 120.7672 | 120.9091 | 120.3186 | 120.8862 | -0.16022 | -121.1105
3504.4219 | 121.051 | -120.8542 | 0.086975 | 0.0096895 | -0.0010596 | 0.0047723 | 0.079111 | -0.027998 | -0.030636 | 0.0077929 | 0.09613 | 0.045776 | -0.073242 | 0.21973 | -0.41199 | 0.21515 | -0.14648 | 0.32501 | 0.1236 | -121.1288 | 120.7809 | -0.041199 | 120.9503 | 121.0739 | -0.49896 | -0.27466 | 0.036621 | 0.16937 | 120.7077 | 121.1792 | 120.4422 | 120.9 | 120.9503 | 120.9778 | 121.0693 | -0.27466 | 120.9 | 120.9503 | 121.0693 | 120.4422 | 120.9778 | -0.16022 | -121.2158
3506.1562 | 121.1884 | -120.8359 | 0.07782 | 0.017319 | 8.578e-06 | 0.0043451 | 0.086801 | -0.02522 | -0.034694 | 0.0095019 | -0.004578 | 0.082397 | -0.1236 | 0.068665 | -0.59967 | 0.064087 | -0.004578 | 0.11902 | 0.16937 | -121.1929 | 120.7123 | 0.004577 | 120.8313 | 120.9045 | -0.67749 | -0.35706 | 0.091553 | 0.11902 | 120.8313 | 120.9549 | 120.2362 | 120.9183 | 120.8313 | 121.0052 | 120.9 | -0.35706 | 120.9183 | 120.8313 | 120.9 | 120.2362 | 121.0052 | -0.20142 | -121.2708
3507.9531 | 120.8633 | -120.9091 | 0.1236 | 0.0096895 | -0.00020502 | 0.010967 | 0.087229 | -0.022016 | -0.03384 | 0.010356 | 0.054932 | 0.073242 | -0.1236 | 0.16022 | -0.47607 | 0.11902 | -0.050354 | 0.21057 | 0.16479 | -121.2296 | 120.7855 | -0.050354 | 120.9641 | 121.0693 | -0.59967 | -0.32043 | 0.041199 | 0.17853 | 120.8588 | 121.1197 | 120.433 | 120.9824 | 120.9641 | 121.0739 | 121.0281 | -0.32043 | 120.9824 | 120.9641 | 121.0281 | 120.433 | 121.0739 | -0.24719 | -121.3531
3509.7344 | 121.2341 | -120.8954 | 0.073242 | 0.017319 | -0.00063242 | 0.0062677 | 0.08851 | -0.024366 | -0.029781 | 0.012065 | 0 | 0.07782 | -0.12817 | 0.091553 | -2.9068 | 0.07782 | -0.022888 | 0.11902 | 0.16022 | -121.2296 | 120.7672 | 0.004578 | 120.8954 | 120.9869 | -2.98 | -0.33417 | 0.086975 | 0.12817 | 120.8725 | 121.0144 | 117.9886 | 120.9732 | 120.8954 | 121.0556 | 120.9732 | -0.33417 | 120.9732 | 120.8954 | 120.9732 | 117.9886 | 121.0556 | -0.20142 | -121.3028
3511.4531 | 121.2296 | -120.9091 | 0.064087 | 0.0096895 | -0.0023412 | 0.0060541 | 0.083811 | -0.021802 | -0.033626 | 0.012065 | 0 | 0.068665 | -0.12817 | 0.09613 | -0.55389 | 0.073242 | -0.041199 | 0.13733 | 0.16937 | -121.2616 | 120.7809 | 0.004578 | 120.9091 | 121.0052 | -0.61798 | -0.35248 | 0.10529 | 0.12817 | 120.8679 | 121.0464 | 120.3552 | 120.9778 | 120.9091 | 121.0785 | 120.9824 | -0.35248 | 120.9778 | 120.9091 | 120.9824 | 120.3552 | 121.0785 | -0.19226 | -121.3257
3513.25 | 121.2524 | -120.9595 | 0.059509 | 0.0096895 | -0.0012732 | 0.0056269 | 0.085947 | -0.023725 | -0.033626 | 0.0088611 | -0.018311 | 0.082397 | -0.13275 | 0.054932 | -0.43945 | 0.059509 | 0.022888 | 0.14191 | 0.16479 | -121.2845 | 120.8267 | 0.022888 | 120.9412 | 121.0144 | -0.49896 | -0.32501 | 0.10529 | 0.11444 | 120.9824 | 121.1014 | 120.52 | 121.0419 | 120.9412 | 121.1243 | 121.019 | -0.32501 | 121.0419 | 120.9412 | 121.019 | 120.52 | 121.1243 | -0.19226 | -121.344
3515.0469 | 121.2387 | -120.9778 | 0.054932 | -0.0055695 | -0.0014868 | 0.0064813 | 0.08082 | -0.024366 | -0.032131 | 0.010784 | 0.07782 | 0.045776 | -0.068665 | 0.1831 | -0.29297 | 0.19684 | -0.17395 | 0.28381 | 0.10529 | -121.2708 | 120.9091 | -0.009156 | 121.0556 | 121.1609 | -0.3479 | -0.29297 | 0.050354 | 0.14649 | 120.8038 | 121.2616 | 120.6848 | 121.0236 | 121.0556 | 121.0831 | 121.1746 | -0.29297 | 121.0236 | 121.0556 | 121.1746 | 120.6848 | 121.0831 | -0.1236 | -121.3257
3516.7656 | 121.2845 | -121.0007 | 0.054932 | 0.017319 | -0.00084602 | 0.0056269 | 0.081461 | -0.02458 | -0.033413 | 0.010997 | 0 | 0.073242 | -0.13275 | 0.09613 | -0.40283 | 0.09613 | -0.059509 | 0.16022 | 0.14648 | -121.3074 | 120.8679 | 0.01831 | 121.0007 | 121.0968 | -0.45776 | -0.3067 | 0.091552 | 0.13275 | 120.9412 | 121.1609 | 120.5978 | 121.0739 | 121.0007 | 121.1472 | 121.0968 | -0.3067 | 121.0739 | 121.0007 | 121.0968 | 120.5978 | 121.1472 | -0.18768 | -121.3623
3518.5625 | 121.2616 | -121.0236 | 0.082397 | 0.00206 | -0.00020502 | 0.0079767 | 0.081247 | -0.023939 | -0.031917 | 0.0073657 | 0.1236 | 0.032043 | -0.068665 | 0.21515 | -0.33417 | 0.21057 | -0.18768 | 0.27008 | 0.10529 | -121.3348 | 120.9549 | -0.050354 | 121.1472 | 121.2387 | -0.41656 | -0.31128 | 0.022889 | 0.19226 | 120.8359 | 121.2936 | 120.6894 | 121.0556 | 121.1472 | 121.1288 | 121.2341 | -0.31128 | 121.0556 | 121.1472 | 121.2341 | 120.6894 | 121.1288 | -0.15106 | -121.4172
3520.3125 | 121.2753 | -121.0373 | 0.073242 | 0.017319 | 8.578e-06 | 0.0051995 | 0.084238 | -0.023084 | -0.031917 | 0.0088611 | 0.10071 | 0.064087 | -0.07782 | 0.19684 | -0.35248 | 0.19684 | -0.17395 | 0.25635 | 0.13275 | -121.344 | 120.9595 | -0.009155 | 121.138 | 121.2341 | -0.42572 | -0.3067 | 0.059509 | 0.17853 | 120.8633 | 121.2936 | 120.6848 | 121.1014 | 121.138 | 121.17 | 121.2341 | -0.3067 | 121.1014 | 121.138 | 121.2341 | 120.6848 | 121.17 | -0.15106 | -121.4172
3522.0469 | 120.9549 | -121.019 | 0.10529 | -0.0055695 | -0.00084602 | 0.0058405 | 0.079965 | -0.025648 | -0.035335 | 0.0073657 | 0.10529 | 0.054932 | -0.064087 | 0.21057 | -0.35248 | 0.19684 | -0.10986 | 0.3067 | 0.11444 | -121.3531 | 120.9549 | -0.050354 | 121.1243 | 121.2296 | -0.45776 | -0.33417 | 0.009155 | 0.16937 | 120.9091 | 121.3257 | 120.6665 | 121.0739 | 121.1243 | 121.1334 | 121.2158 | -0.33417 | 121.0739 | 121.1243 | 121.2158 | 120.6665 | 121.1334 | -0.16937 | -121.4584
3523.8281 | 121.3348 | -121.0831 | 0.059509 | 0.0096895 | -0.0012732 | 0.0049859 | 0.08082 | -0.026075 | -0.031277 | 0.0075793 | 0.086975 | 0.064087 | -0.068665 | 0.16022 | -0.41657 | 0.16479 | -0.13275 | 0.23804 | 0.1236 | -121.3943 | 121.0144 | 0.004578 | 121.17 | 121.2433 | -0.47607 | -0.31128 | 0.064087 | 0.15564 | 120.9503 | 121.3211 | 120.6665 | 121.1472 | 121.17 | 121.2067 | 121.2479 | -0.31128 | 121.1472 | 121.17 | 121.2479 | 120.6665 | 121.2067 | -0.12817 | -121.4539
3525.625 | 120.8267 | -120.5978 | 0.082397 | 0.0096895 | -0.0014868 | 0.0069085 | 0.084238 | -0.027357 | -0.034694 | 0.0077929 | -0.009155 | 0.10071 | -0.13275 | 0.086975 | -0.53101 | 0.073242 | 0.064087 | 0.16022 | 0.16937 | -121.4172 | 120.4651 | 0.018311 | 120.5887 | 120.6848 | -0.6134 | -0.8194 | 0.086976 | 0.1236 | 120.6619 | 120.7581 | 120.0668 | 120.6985 | 120.5887 | 120.7672 | 120.6711 | -0.8194 | 120.6985 | 120.5887 | 120.6711 | 120.0668 | 120.7672 | -0.21515 | -121.4996
3527.4531 | 121.2891 | -121.1105 | 0.10071 | 0.0096895 | -0.0010596 | 0.0037043 | 0.079538 | -0.028638 | -0.02914 | 0.0056567 | 0.09613 | 0.041199 | -0.086975 | 0.22888 | -0.46692 | 0.21057 | -0.14191 | 0.32044 | 0.10071 | -121.4218 | 121.0236 | -0.059509 | 121.2067 | 121.3394 | -0.56763 | -0.31128 | 0 | 0.1831 | 120.9686 | 121.431 | 120.6436 | 121.1517 | 121.2067 | 121.2112 | 121.3211 | -0.31128 | 121.1517 | 121.2067 | 121.3211 | 120.6436 | 121.2112 | -0.18768 | -121.5225
3529.2344 | 121.2067 | -121.0922 | 0.10986 | -0.0055695 | -0.0021276 | 0.0071221 | 0.081674 | -0.027143 | -0.032345 | 0.0069385 | 0.10986 | 0.036621 | -0.082397 | 0.22888 | -0.33417 | 0.19684 | -0.11444 | 0.33417 | 0.11444 | -121.4172 | 121.0098 | -0.073242 | 121.2021 | 121.3211 | -0.44403 | -0.32501 | 0.004578 | 0.19226 | 120.9778 | 121.4264 | 120.7581 | 121.1288 | 121.2021 | 121.2067 | 121.2891 | -0.32501 | 121.1288 | 121.2021 | 121.2891 | 120.7581 | 121.2067 | -0.19226 | -121.5271
3530.9844 | 121.3715 | -121.0876 | 0.07782 | 0.00206 | -0.002555 | 0.0037043 | 0.080179 | -0.027998 | -0.030636 | 0.0065113 | 0.07782 | 0.045776 | -0.073242 | 0.17853 | -0.49896 | 0.18768 | -0.11444 | 0.28839 | 0.11444 | -121.4355 | 121.0144 | -0.032044 | 121.1655 | 121.2662 | -0.57678 | -0.3479 | 0.036621 | 0.15106 | 120.9732 | 121.376 | 120.5887 | 121.1334 | 121.1655 | 121.2021 | 121.2753 | -0.3479 | 121.1334 | 121.1655 | 121.2753 | 120.5887 | 121.2021 | -0.15106 | -121.5134
3532.7812 | 121.4172 | -121.0602 | 0.068665 | 0.0096895 | 8.578e-06 | 0.0039179 | 0.095346 | -0.026289 | -0.03384 | 0.01292 | -0.013733 | 0.086975 | -0.13733 | 0.10986 | -0.49439 | 0.059509 | -0.004578 | 0.13733 | 0.16937 | -121.4401 | 120.9229 | 0.01831 | 121.0464 | 121.17 | -0.56305 | -0.37994 | 0.10071 | 0.1236 | 121.0556 | 121.1975 | 120.5658 | 121.1472 | 121.0464 | 121.2296 | 121.1197 | -0.37994 | 121.1472 | 121.0464 | 121.1197 | 120.5658 | 121.2296 | -0.20599 | -121.5088
3534.5781 | 121.4127 | -121.1334 | 0.082397 | 0.0096895 | -0.0034094 | 0.0032769 | 0.088083 | -0.026502 | -0.030208 | 0.014842 | 0.059509 | 0.041199 | -0.07782 | 0.16022 | -0.29297 | 0.16479 | -0.13275 | 0.23804 | 0.11444 | -121.4584 | 121.0556 | -0.041198 | 121.1929 | 121.2936 | -0.37537 | -0.32501 | 0.032044 | 0.13733 | 121.0007 | 121.3715 | 120.8405 | 121.1746 | 121.1929 | 121.2479 | 121.2982 | -0.32501 | 121.1746 | 121.1929 | 121.2982 | 120.8405 | 121.2479 | -0.16022 | -121.5408
3536.3594 | 121.4264 | -121.1243 | 0.064087 | 0.0096895 | -0.0027686 | 0.0049859 | 0.088297 | -0.026289 | -0.032558 | 0.015056 | 0.10986 | 0.032043 | -0.07782 | 0.17853 | -0.30212 | 0.16937 | -0.16479 | 0.2655 | 0.11444 | -121.4584 | 121.0464 | -0.032044 | 121.2341 | 121.3028 | -0.36621 | -0.33417 | 0.050354 | 0.18768 | 120.9595 | 121.3898 | 120.8221 | 121.1563 | 121.2341 | 121.2387 | 121.2936 | -0.33417 | 121.1563 | 121.2341 | 121.2936 | 120.8221 | 121.2387 | -0.14191 | -121.5225
3538.0938 | 116.2445 | -77.2659 | 38.7039 | 0.48271 | -0.0091772 | 0.0047723 | 6.9721 | -0.014753 | -0.032985 | 7.0123 | 0.09613 | 0.022888 | -0.10529 | 0.2243 | 21.9955 | 0.14648 | -0.23804 | -4.9576 | 26.1017 | -67.0349 | 77.1606 | -38.681 | 77.3621 | 77.4902 | -16.7084 | 10.231 | -12.6022 | 0.20142 | 77.0279 | 72.3083 | 99.2615 | 77.2888 | 77.3621 | 103.3676 | 77.4124 | 10.231 | 77.2888 | 77.3621 | 77.4124 | 99.2615 | 103.3676 | -38.8092 | -105.7388
3539.875 | 121.1014 | -5.3329 | 114.6698 | 0.024948 | -0.00084602 | 0.0019953 | 0.057108 | 0.037157 | 0.010166 | 0.15242 | 0.086975 | 0.013733 | -0.11902 | 0.18768 | 44.3985 | 0.16937 | -0.19226 | 0.28381 | 115.7959 | -5.4794 | 5.2139 | -114.6561 | 5.4199 | 5.5206 | -70.2713 | -0.14648 | 1.1261 | 0.20599 | 5.1407 | 5.6168 | 49.7314 | 5.3467 | 5.4199 | 121.1288 | 5.5023 | -0.14648 | 5.3467 | 5.4199 | 5.5023 | 49.7314 | 121.1288 | -114.7888 | -120.1492
3541.6094 | 121.0831 | -3.9597 | 116.3361 | 0.0096895 | -0.0014868 | 0.0066949 | 0.064157 | 0.037157 | -0.029354 | 0.12187 | 0.009155 | 0.009155 | -0.13733 | 0.1236 | 114.8483 | 0.1236 | -0.14648 | 0.022888 | 117.3706 | -3.9688 | 3.8223 | -116.3269 | 3.9688 | 4.0833 | -1.4877 | -0.009155 | 1.0345 | 0.14648 | 3.8132 | 3.9825 | 118.808 | 3.9688 | 3.9688 | 121.3303 | 4.0833 | -0.009155 | 3.9688 | 3.9688 | 4.0833 | 118.808 | 121.3303 | -116.4734 | -120.3049
3543.4062 | 121.1792 | -4.0009 | 108.2565 | 0.0096895 | -0.0014868 | 0.0043451 | 0.07078 | 0.035662 | -0.030849 | 0.12721 | 0.068665 | -0.004578 | -0.11902 | 0.18768 | 114.4043 | 0.15106 | -0.16022 | 0.13275 | 117.0456 | -4.0512 | 3.8818 | -108.2611 | 4.0695 | 4.1885 | 6.1478 | -0.050354 | 8.7891 | 0.18768 | 3.8406 | 4.1336 | 118.4052 | 3.9963 | 4.0695 | 121.0464 | 4.1519 | -0.050354 | 3.9963 | 4.0695 | 4.1519 | 118.4052 | 121.0464 | -108.3755 | -112.3077
3545.2031 | 120.8862 | -2.9755 | 111.3693 | 0.0096895 | -0.002555 | 0.0011407 | 0.072702 | 0.037157 | -0.029568 | 0.12336 | -0.050354 | 0.050354 | -0.18768 | 0.073242 | 115.9836 | 0.036621 | 0 | 0.009155 | 118.2907 | -3.1815 | 2.7878 | -111.319 | 2.9251 | 3.0487 | 4.6143 | -0.20599 | 6.9214 | 0.13733 | 2.9755 | 2.9846 | 118.959 | 3.0258 | 2.9251 | 121.2662 | 3.0121 | -0.20599 | 3.0258 | 2.9251 | 3.0121 | 118.959 | 121.2662 | -111.557 | -114.5508
3546.9219 | 121.3211 | -3.7674 | 116.8304 | 0.0096895 | 8.578e-06 | 0.0045587 | 0.25492 | 0.035876 | -0.029781 | 0.31263 | -0.018311 | 0.054932 | -0.15564 | 0.10071 | 111.5753 | 0.068665 | -0.13275 | -0.12817 | 114.1617 | -7.2647 | 3.6118 | -116.7755 | 3.7491 | 3.8681 | -5.2551 | -3.4973 | -2.6688 | 0.13733 | 3.6346 | 3.6392 | 115.3427 | 3.8223 | 3.7491 | 117.9291 | 3.8361 | -3.4973 | 3.8223 | 3.7491 | 3.8361 | 115.3427 | 117.9291 | -116.9861 | -124.0952
3548.7188 | 121.2341 | -4.129 | 117.0731 | 0.017319 | -0.0010596 | 0.0028497 | 0.19425 | 0.037585 | -0.028072 | 0.26329 | 0.018311 | 0.041199 | -0.14191 | 0.11444 | 106.6269 | 0.059509 | -0.059509 | -0.073242 | 114.7751 | -6.5506 | 3.9871 | -117.0319 | 4.1473 | 4.2435 | -10.4462 | -2.4216 | -2.298 | 0.16022 | 4.0695 | 4.0558 | 110.7559 | 4.1702 | 4.1473 | 118.9041 | 4.1885 | -2.4216 | 4.1702 | 4.1473 | 4.1885 | 110.7559 | 118.9041 | -117.215 | -123.6237
3550.5156 | 102.5116 | -45.6619 | 75.4623 | 0.017319 | -0.0010596 | 0.0015679 | 0.48499 | 0.011095 | -0.028713 | 0.52092 | -0.050354 | 0.064087 | -0.15106 | 0.082397 | 67.9688 | 0.032043 | 0.009155 | -1.2909 | 69.5892 | -51.8829 | 45.5109 | -75.3983 | 45.6116 | 45.7443 | -7.4936 | -6.221 | -5.8731 | 0.10071 | 45.6711 | 44.371 | 113.6307 | 45.726 | 45.6116 | 115.2512 | 45.694 | -6.221 | 45.726 | 45.6116 | 45.694 | 113.6307 | 115.2512 | -75.6134 | -127.3453
3552.25 | 120.9595 | -115.7822 | 4.7424 | 0.00206 | -0.0021276 | 0.0045587 | 0.1714 | -0.020521 | 0.03281 | 0.16972 | 0.10529 | 0.036621 | -0.07782 | 0.19226 | -114.0518 | 0.19226 | -0.19226 | 0.23804 | 4.6921 | -116.2674 | 115.7043 | -4.7058 | 115.8875 | 115.9744 | -118.7943 | -0.48523 | -0.050354 | 0.18311 | 115.5899 | 116.0202 | 1.7303 | 115.8188 | 115.8875 | 120.4742 | 115.9744 | -0.48523 | 115.8188 | 115.8875 | 115.9744 | 1.7303 | 120.4742 | -4.8203 | -121.0098
3554.0469 | 121.2708 | -113.5941 | 7.251 | 0.0096895 | -0.00063242 | 0.0045587 | 0.47453 | -0.02223 | 0.034519 | 0.47734 | 0.041199 | 0.045776 | -0.082397 | 0.13733 | -111.8637 | 0.13275 | -0.11444 | -0.36163 | 7.2601 | -113.9191 | 113.5117 | -7.2052 | 113.6353 | 113.7314 | -119.1147 | -0.32501 | 0.009155 | 0.1236 | 113.4796 | 113.2324 | 1.7303 | 113.6398 | 113.6353 | 120.8542 | 113.7268 | -0.32501 | 113.6398 | 113.6353 | 113.7268 | 1.7303 | 120.8542 | -7.3334 | -121.17
3555.7656 | 121.3028 | -97.4167 | 23.2681 | 0.0096895 | -0.0014868 | 0.0056269 | 0.598 | -0.011121 | 0.032383 | 0.61427 | 0.032043 | 0.054932 | -0.1236 | 0.14648 | -95.8466 | 0.11902 | -0.13275 | -0.69122 | 23.3871 | -97.7829 | 97.2931 | -23.2132 | 97.4487 | 97.5632 | -119.1147 | -0.36621 | 0.11902 | 0.15564 | 97.2839 | 96.7255 | 1.5701 | 97.4716 | 97.4487 | 120.8038 | 97.5357 | -0.36621 | 97.4716 | 97.4487 | 97.5357 | 1.5701 | 120.8038 | -23.3917 | -121.051
3557.5469 | 120.5429 | -115.3839 | 4.9072 | 0.00206 | -0.00020502 | 0.0064813 | 0.70631 | -0.022443 | -0.023159 | 0.66191 | 0.059509 | 0.054932 | -0.11444 | 0.15106 | -11.9476 | 0.12817 | -0.032043 | 0.2243 | 4.8386 | -115.9378 | 115.2695 | -4.8523 | 115.4434 | 115.535 | -16.8549 | -0.55389 | -0.068665 | 0.17395 | 115.3519 | 115.6082 | 103.4363 | 115.4388 | 115.4434 | 120.2225 | 115.5121 | -0.55389 | 115.4388 | 115.4434 | 115.5121 | 103.4363 | 120.2225 | -5.0217 | -120.845
3559.3438 | 120.9229 | -115.3976 | 5.2551 | 0.017319 | -0.0010596 | 0.0088311 | 0.98167 | -0.023725 | 0.021916 | 0.96952 | -0.009155 | 0.10529 | -0.11444 | 0.082397 | -92.1799 | 0.068665 | 0.036621 | 0.16937 | 5.191 | -115.7867 | 115.2832 | -5.1498 | 115.3885 | 115.48 | -97.435 | -0.3891 | -0.064087 | 0.10529 | 115.4343 | 115.567 | 23.2178 | 115.5029 | 115.3885 | 120.5887 | 115.4663 | -0.3891 | 115.5029 | 115.3885 | 115.4663 | 23.2178 | 120.5887 | -5.3696 | -121.0419
3561.125 | 121.0098 | -114.2807 | 6.2942 | 0.00206 | -0.003623 | 0.0028497 | 2.1032 | -0.021802 | 0.010166 | 2.2587 | 0.050354 | 0.059509 | -0.09613 | 0.17853 | -59.1568 | 0.20142 | -0.13275 | 0.27008 | 6.5689 | -114.18 | 114.1846 | -6.2347 | 114.3311 | 114.4592 | -65.451 | 0.10071 | 0.27466 | 0.14648 | 114.1479 | 114.5508 | 55.1239 | 114.3402 | 114.3311 | 120.8496 | 114.4821 | 0.10071 | 114.3402 | 114.3311 | 114.4821 | 55.1239 | 120.8496 | -6.3904 | -120.4742
3562.9062 | 120.9366 | -116.2903 | 4.5044 | 0.0096895 | 0.001504 | 0.0058405 | 1.6369 | -0.026075 | -0.025936 | 1.57 | 0.09613 | 0.036621 | -0.068665 | 0.21515 | -4.8935 | 0.20599 | -0.14648 | 0.33875 | 4.5227 | -116.3269 | 116.2216 | -4.4678 | 116.3864 | 116.5054 | -9.3979 | -0.036621 | 0.01831 | 0.16479 | 116.1438 | 116.629 | 111.3968 | 116.3269 | 116.3864 | 120.813 | 116.4963 | -0.036621 | 116.3269 | 116.3864 | 116.4963 | 111.3968 | 120.813 | -4.5731 | -120.8313
3564.6406 | 121.019 | -118.4967 | 2.3666 | 0.024948 | -0.001914 | 0.0066949 | 0.82124 | -0.024793 | -0.033626 | 0.73432 | 0.054932 | 0.09613 | -0.11444 | 0.15564 | 1.6571 | 0.11902 | -0.036621 | 0.21515 | 2.1149 | -118.895 | 118.3823 | -2.2705 | 118.5516 | 118.6523 | -0.70953 | -0.39825 | -0.25177 | 0.16937 | 118.4601 | 118.7119 | 120.1538 | 118.5928 | 118.5516 | 120.6116 | 118.6157 | -0.39825 | 118.5928 | 118.5516 | 118.6157 | 120.1538 | 120.6116 | -2.4811 | -121.2616
3566.4531 | 121.1105 | -117.3889 | 3.3188 | 0.0096895 | -0.0034094 | 0.0056269 | 0.82936 | -0.022016 | 0.031956 | 0.82768 | 0.10071 | 0.041199 | -0.068665 | 0.19684 | -112.2162 | 0.19684 | -0.19226 | 0.27008 | 3.3051 | -117.6956 | 117.3203 | -3.2776 | 117.4896 | 117.5858 | -115.535 | -0.3067 | -0.013733 | 0.16937 | 117.1967 | 117.659 | 5.1727 | 117.4301 | 117.4896 | 120.694 | 117.5858 | -0.3067 | 117.4301 | 117.4896 | 117.5858 | 5.1727 | 120.694 | -3.3875 | -121.0144
3568.25 | 121.1288 | -114.7751 | 6.0379 | 0.0096895 | 0.0017176 | 0.010967 | 1.3196 | -0.020948 | 0.031101 | 1.3156 | 0.10529 | 0.045776 | -0.086975 | 0.19684 | -105.7114 | 0.20142 | -0.21057 | 0.29297 | 6.1203 | -114.8117 | 114.6881 | -5.9921 | 114.8804 | 114.9719 | -111.7493 | -0.036622 | 0.082397 | 0.19226 | 114.5645 | 115.0681 | 9.0637 | 114.8209 | 114.8804 | 120.8954 | 114.9765 | -0.036622 | 114.8209 | 114.8804 | 114.9765 | 9.0637 | 120.8954 | -6.1249 | -120.8496
3570.0469 | 120.9961 | -114.4226 | 6.3538 | 0.017319 | 0.00022218 | 0.0098993 | 2.1337 | -0.023725 | -0.032131 | 2.0737 | -0.018311 | 0.11444 | -0.11444 | 0.10529 | 3.3142 | 0.064087 | 0.059509 | 0.18768 | 6.3721 | -114.5187 | 114.3082 | -6.2393 | 114.4043 | 114.5279 | -3.0396 | -0.096131 | 0.01831 | 0.09613 | 114.4821 | 114.6103 | 117.7368 | 114.537 | 114.4043 | 120.7947 | 114.4867 | -0.096131 | 114.537 | 114.4043 | 114.4867 | 117.7368 | 120.7947 | -6.4682 | -120.8725
3571.8281 | 121.0052 | -116.5878 | 4.3121 | 0.024948 | -0.001914 | 0.0051995 | 1.2023 | -0.026716 | -0.030422 | 1.1056 | 0.086975 | 0.050354 | -0.073242 | 0.23346 | 2.4994 | 0.20599 | -0.11444 | 0.31128 | 4.2343 | -116.7709 | 116.5146 | -4.2618 | 116.6748 | 116.8213 | -1.8127 | -0.1831 | -0.07782 | 0.16022 | 116.4734 | 116.8991 | 119.0872 | 116.6382 | 116.6748 | 120.8221 | 116.7938 | -0.1831 | 116.6382 | 116.6748 | 116.7938 | 119.0872 | 120.8221 | -4.3854 | -121.0831
3573.625 | 121.0281 | -117.6682 | 3.2593 | 0.0096895 | -0.0010596 | 0.0041315 | 0.76335 | -0.02458 | -0.032772 | 0.69374 | 0.059509 | 0.086975 | -0.13275 | 0.16022 | -1.0666 | 0.13733 | -0.041199 | 0.21515 | 3.392 | -117.778 | 117.5354 | -3.1723 | 117.7277 | 117.8284 | -4.3259 | -0.10986 | 0.13275 | 0.19226 | 117.627 | 117.8833 | 116.6016 | 117.7551 | 117.7277 | 121.0602 | 117.8055 | -0.10986 | 117.7551 | 117.7277 | 117.8055 | 116.6016 | 121.0602 | -3.392 | -121.0373
3575.375 | 121.0602 | -116.6519 | 4.2892 | 0.024948 | -0.0031958 | 0.0051995 | 1.0473 | -0.024152 | -0.025722 | 1.0362 | 0.032043 | 0.059509 | -0.11902 | 0.14191 | -9.1507 | 0.10529 | 0.013733 | 0.20599 | 4.7333 | -116.4917 | 116.5329 | -4.2297 | 116.684 | 116.7938 | -13.4399 | 0.16022 | 0.44403 | 0.15106 | 116.6656 | 116.8579 | 107.5012 | 116.7114 | 116.684 | 121.3852 | 116.7572 | 0.16022 | 116.7114 | 116.684 | 116.7572 | 107.5012 | 121.3852 | -4.4083 | -120.7809
3577.1719 | 121.1334 | -117.7231 | 3.1357 | 0.0096895 | -0.0038366 | 0.0054131 | 1.0863 | -0.026716 | -0.025081 | 1.0073 | 0.082397 | 0.036621 | -0.091553 | 0.16937 | -5.1498 | 0.18768 | -0.12817 | 0.26093 | 3.2867 | -117.7826 | 117.6315 | -3.0991 | 117.8055 | 117.8925 | -8.2855 | -0.05951 | 0.15106 | 0.17395 | 117.5949 | 117.984 | 112.5732 | 117.7597 | 117.8055 | 121.0098 | 117.9108 | -0.05951 | 117.7597 | 117.8055 | 117.9108 | 112.5732 | 121.0098 | -3.2272 | -120.9183
3578.9062 | 121.1014 | -115.416 | 5.4474 | 0.00206 | -0.0034094 | 0.0039179 | 1.6691 | -0.023725 | -0.032985 | 1.6065 | 0.07782 | 0.045776 | -0.091553 | 0.18768 | 4.3304 | 0.1831 | -0.16937 | 0.25635 | 5.3741 | -115.5807 | 115.3244 | -5.4016 | 115.4938 | 115.6036 | -1.1169 | -0.16479 | -0.073242 | 0.16937 | 115.2466 | 115.6723 | 119.7464 | 115.4617 | 115.4938 | 120.7901 | 115.5991 | -0.16479 | 115.4617 | 115.4938 | 115.5991 | 119.7464 | 120.7901 | -5.5389 | -121.0281
3580.7031 | 121.1243 | -117.9108 | 2.9617 | 0.0096895 | 0.00022218 | 0.0071221 | 0.85862 | -0.023939 | 0.031101 | 0.81059 | 0.086975 | 0.045776 | -0.086975 | 0.18768 | -113.6398 | 0.18768 | -0.17853 | 0.26093 | 2.8473 | -118.2907 | 117.8238 | -2.916 | 117.9977 | 118.0985 | -116.6016 | -0.37994 | -0.11444 | 0.17395 | 117.7322 | 118.1717 | 4.2709 | 117.9565 | 117.9977 | 120.7581 | 118.0985 | -0.37994 | 117.9565 | 117.9977 | 118.0985 | 4.2709 | 120.7581 | -3.0487 | -121.2524
3582.5156 | 121.2799 | -116.4368 | 4.4312 | 0.0096895 | 0.00043578 | 0.0084039 | 0.322 | -0.022871 | 0.03217 | 0.30729 | 0.10071 | 0.022888 | -0.091553 | 0.21057 | -110.5637 | 0.19684 | -0.19226 | 0.27466 | 4.5273 | -116.748 | 116.3452 | -4.4083 | 116.5375 | 116.6473 | -114.9948 | -0.31128 | 0.096131 | 0.19226 | 116.2445 | 116.7114 | 5.8731 | 116.4597 | 116.5375 | 120.9641 | 116.6336 | -0.31128 | 116.4597 | 116.5375 | 116.6336 | 5.8731 | 120.9641 | -4.5227 | -121.1792
3584.2656 | 121.3486 | -120.1675 | 0.80109 | 0.00206 | -0.0021276 | 0.0071221 | 0.11714 | -0.027998 | -0.030849 | 0.046245 | 0.054932 | 0.064087 | -0.10529 | 0.15564 | -2.3849 | 0.16937 | -0.091553 | 0.24719 | 0.92926 | -120.5017 | 120.0623 | -0.737 | 120.2225 | 120.3232 | -3.186 | -0.33417 | 0.12817 | 0.16022 | 120.076 | 120.4147 | 117.7826 | 120.2316 | 120.2225 | 121.0968 | 120.3369 | -0.33417 | 120.2316 | 120.2225 | 120.3369 | 117.7826 | 121.0968 | -0.90637 | -121.3028
3586.0625 | 121.1838 | -120.1355 | 0.96588 | 0.0096895 | -0.0012732 | 0.0019953 | 0.10838 | -0.025434 | -0.032131 | 0.03535 | 0.12817 | 0.045776 | -0.073242 | 0.23804 | -0.11902 | 0.23804 | -0.12817 | 0.32044 | 0.98419 | -120.4147 | 120.0623 | -0.9201 | 120.2637 | 120.3735 | -1.0849 | -0.27924 | 0.018311 | 0.20142 | 120.0073 | 120.4559 | 120.0165 | 120.1813 | 120.2637 | 121.1197 | 120.3735 | -0.27924 | 120.1813 | 120.2637 | 120.3735 | 120.0165 | 121.1197 | -1.0391 | -121.3806
3587.7812 | 121.3257 | -120.3094 | 0.7782 | 0.00206 | -0.0010596 | 0.0060541 | 0.11714 | -0.02522 | -0.032985 | 0.040691 | 0.054932 | 0.050354 | -0.086975 | 0.15564 | 0.21515 | 0.16022 | -0.10071 | 0.25177 | 0.84228 | -120.6162 | 120.2225 | -0.72784 | 120.3644 | 120.4651 | -0.56305 | -0.3067 | 0.064087 | 0.14191 | 120.2087 | 120.5612 | 120.5246 | 120.3598 | 120.3644 | 121.1517 | 120.4697 | -0.3067 | 120.3598 | 120.3644 | 120.4697 | 120.5246 | 121.1517 | -0.86517 | -121.3943
3589.5938 | 121.2433 | -119.4489 | 1.6663 | 0.017319 | -0.004264 | 0.0060541 | 0.3173 | -0.02522 | -0.031917 | 0.25132 | 0.059509 | 0.073242 | -0.10529 | 0.15106 | -0.77362 | 0.10986 | 0 | 0.22888 | 1.9913 | -119.4534 | 119.3436 | -1.593 | 119.5084 | 119.5999 | -2.4399 | -0.004577 | 0.32501 | 0.16479 | 119.4489 | 119.6777 | 118.6752 | 119.5221 | 119.5084 | 121.4401 | 119.5587 | -0.004577 | 119.5221 | 119.5084 | 119.5587 | 118.6752 | 121.4401 | -1.7715 | -121.1197
3591.3438 | 121.3486 | -120.5887 | 0.52185 | 0.00206 | -0.0029822 | 0.0019953 | 0.10859 | -0.027357 | -0.032345 | 0.0424 | 0.064087 | 0.045776 | -0.086975 | 0.16479 | 0.3479 | 0.16479 | -0.1236 | 0.25177 | 0.58594 | -120.8725 | 120.5017 | -0.47607 | 120.6528 | 120.7535 | -0.17395 | -0.28381 | 0.064086 | 0.15106 | 120.4651 | 120.8405 | 120.9366 | 120.6345 | 120.6528 | 121.1746 | 120.7535 | -0.28381 | 120.6345 | 120.6528 | 120.7535 | 120.9366 | 121.1746 | -0.60883 | -121.3943
3593.1406 | 121.2982 | -120.2179 | 0.86975 | 0.017319 | 0.0012902 | 0.0054131 | 0.43052 | -0.025007 | -0.029568 | 0.37181 | 0.07782 | 0.073242 | -0.086975 | 0.19684 | -4.8523 | 0.19226 | -0.16022 | 0.25177 | 0.81024 | -120.5658 | 120.1309 | -0.79651 | 120.2957 | 120.4147 | -5.722 | -0.3479 | -0.059509 | 0.16479 | 120.0577 | 120.4697 | 115.3656 | 120.2911 | 120.2957 | 121.0281 | 120.4102 | -0.3479 | 120.2911 | 120.2957 | 120.4102 | 115.3656 | 121.0281 | -0.95673 | -121.4355
3594.9531 | 121.2524 | -120.7489 | 0.40283 | 0.0096895 | -0.00084602 | 0.0071221 | 0.1103 | -0.02757 | -0.033199 | 0.040904 | 0.004578 | 0.086975 | -0.11444 | 0.09613 | 0.19684 | 0.07782 | 0.068665 | 0.17395 | 0.48523 | -121.1014 | 120.6345 | -0.31586 | 120.7535 | 120.845 | -0.20599 | -0.35248 | 0.082397 | 0.11902 | 120.8176 | 120.9229 | 120.9457 | 120.8359 | 120.7535 | 121.2341 | 120.8267 | -0.35248 | 120.8359 | 120.7535 | 120.8267 | 120.9457 | 121.2341 | -0.51727 | -121.5042
3596.7344 | 121.3394 | -120.7443 | 0.4303 | 0.00206 | -0.0012732 | 0.0084039 | 0.16221 | -0.027998 | -0.033199 | 0.089824 | 0.09613 | 0.022888 | -0.07782 | 0.19684 | 0.24261 | 0.20599 | -0.18768 | 0.27924 | 0.4303 | -121.0373 | 120.6665 | -0.40741 | 120.8405 | 120.9412 | -0.18768 | -0.29297 | 0 | 0.17395 | 120.5566 | 121.0236 | 120.9869 | 120.7672 | 120.8405 | 121.1746 | 120.9503 | -0.29297 | 120.7672 | 120.8405 | 120.9503 | 120.9869 | 121.1746 | -0.50812 | -121.4676
3598.4688 | 121.3806 | -120.6848 | 0.47607 | 0.017319 | -0.0012732 | 0.0043451 | 0.28803 | -0.023939 | -0.033199 | 0.21949 | 0.091553 | 0.050354 | -0.082397 | 0.16479 | 0.22888 | 0.16022 | -0.14191 | 0.25177 | 0.48065 | -120.9778 | 120.6024 | -0.42572 | 120.7764 | 120.8496 | -0.24719 | -0.29297 | 0.004578 | 0.17395 | 120.5429 | 120.9366 | 120.9137 | 120.7352 | 120.7764 | 121.1655 | 120.845 | -0.29297 | 120.7352 | 120.7764 | 120.845 | 120.9137 | 121.1655 | -0.55847 | -121.4539
3600.2656 | 121.2982 | -118.0847 | 3.1082 | 0.0096895 | -0.00041862 | 0.0079767 | 0.46876 | -0.02522 | 0.018284 | 0.46067 | 0.11902 | 0.027466 | -0.091553 | 0.21057 | -90.683 | 0.20599 | -0.19684 | 0.29297 | 3.1769 | -118.3456 | 117.9932 | -3.0807 | 118.2037 | 118.2953 | -93.7912 | -0.26093 | 0.068665 | 0.21057 | 117.8879 | 118.3777 | 27.4017 | 118.1122 | 118.2037 | 121.2616 | 118.2907 | -0.26093 | 118.1122 | 118.2037 | 118.2907 | 27.4017 | 121.2616 | -3.1998 | -121.4539
3602.0625 | 121.3852 | -120.7809 | 0.37994 | 0.00206 | -0.0014868 | 0.0075495 | 0.098123 | -0.027784 | 0.033879 | 0.090679 | 0.064087 | 0.045776 | -0.068665 | 0.18768 | -119.7372 | 0.17853 | -0.12817 | 0.27008 | 0.39825 | -121.1288 | 120.7123 | -0.33417 | 120.845 | 120.9686 | -120.1172 | -0.3479 | 0.01831 | 0.13275 | 120.6528 | 121.051 | 1.0437 | 120.8267 | 120.845 | 121.1792 | 120.9595 | -0.3479 | 120.8267 | 120.845 | 120.9595 | 1.0437 | 121.1792 | -0.44861 | -121.5088
3603.7812 | 121.3943 | -120.7352 | 0.39368 | 0.00206 | -0.00084602 | 0.0066949 | 0.3878 | -0.024793 | 0.030674 | 0.35002 | 0.032043 | 0.086975 | -0.12817 | 0.11444 | -119.5724 | 0.09613 | -0.07782 | 0.16937 | 0.50812 | -121.0144 | 120.607 | -0.3067 | 120.7672 | 120.8496 | -119.9661 | -0.27924 | 0.11444 | 0.16022 | 120.6573 | 120.9045 | 1.1627 | 120.8221 | 120.7672 | 121.2433 | 120.8313 | -0.27924 | 120.8221 | 120.7672 | 120.8313 | 1.1627 | 121.2433 | -0.52185 | -121.4081
3605.5781 | 119.87 | -116.629 | 2.8839 | 0.017319 | 0.0017176 | 0.0049859 | 0.2122 | -0.01988 | -0.030208 | 0.14515 | 0.12817 | 0.045776 | -0.073242 | 0.18768 | -1.2451 | 0.20599 | -0.19684 | 0.27924 | 3.2822 | -116.6199 | 116.5558 | -2.8381 | 116.7572 | 116.8167 | -4.129 | 0.009155 | 0.39826 | 0.20142 | 116.4322 | 116.9083 | 115.3839 | 116.6748 | 116.7572 | 119.9112 | 116.835 | 0.009155 | 116.6748 | 116.7572 | 116.835 | 115.3839 | 119.9112 | -2.9572 | -119.5038
3607.3906 | 120.8496 | -119.3527 | 1.2222 | 0.00206 | -0.0023412 | 0.0019953 | 0.087869 | -0.023725 | -0.032131 | 0.014202 | 0.013733 | 0.07782 | -0.14191 | 0.13275 | 0.25635 | 0.091553 | -0.004578 | 0.21057 | 1.3092 | -119.7464 | 119.2108 | -1.1444 | 119.3665 | 119.4855 | -0.96588 | -0.39368 | 0.086975 | 0.15564 | 119.3481 | 119.5633 | 119.6091 | 119.4305 | 119.3665 | 120.6619 | 119.4443 | -0.39368 | 119.4305 | 119.3665 | 119.4443 | 119.6091 | 120.6619 | -1.3641 | -120.9686
3609.1719 | 121.0327 | -119.7144 | 0.96588 | 0.0096895 | -0.0012732 | 0.0060541 | 0.081247 | -0.026289 | -0.028713 | 0.014415 | 0.064087 | 0.059509 | -0.086975 | 0.16022 | 0.44861 | 0.17395 | -0.11444 | 0.28839 | 1.0345 | -120.108 | 119.6274 | -0.90637 | 119.7784 | 119.8746 | -0.51727 | -0.39368 | 0.068665 | 0.15106 | 119.5999 | 120.0027 | 120.163 | 119.7739 | 119.7784 | 120.7489 | 119.8883 | -0.39368 | 119.7739 | 119.7784 | 119.8883 | 120.163 | 120.7489 | -1.0529 | -121.0739
3610.9688 | 120.9686 | -120.195 | 0.6546 | 0.00206 | 8.578e-06 | 0.0069085 | 0.10133 | -0.024793 | -0.033413 | 0.013133 | 0.041199 | 0.068665 | -0.11902 | 0.13275 | 0.27466 | 0.10986 | -0.041199 | 0.17395 | 0.72327 | -120.488 | 120.076 | -0.58594 | 120.2362 | 120.3278 | -0.37994 | -0.29297 | 0.068665 | 0.16022 | 120.1538 | 120.369 | 120.4697 | 120.2637 | 120.2362 | 120.9183 | 120.3049 | -0.29297 | 120.2637 | 120.2362 | 120.3049 | 120.4697 | 120.9183 | -0.77362 | -121.1426
3612.75 | 121.019 | -120.314 | 0.5722 | 0.0096895 | 0.0038538 | 0.0041315 | 0.094065 | -0.026289 | -0.031063 | 0.016765 | 0.054932 | 0.082397 | -0.10986 | 0.1236 | 0.24261 | 0.09613 | -0.032043 | 0.17853 | 0.65002 | -120.6345 | 120.2042 | -0.48981 | 120.369 | 120.4376 | -0.32959 | -0.32043 | 0.077819 | 0.16479 | 120.282 | 120.4926 | 120.5566 | 120.3964 | 120.369 | 120.9641 | 120.4102 | -0.32043 | 120.3964 | 120.369 | 120.4102 | 120.5566 | 120.9641 | -0.68207 | -121.2067
3614.5469 | 121.0556 | -120.488 | 0.46234 | 0.0096895 | -0.0014868 | 0.0069085 | 0.092142 | -0.024793 | -0.032558 | 0.013774 | 0.022888 | 0.086975 | -0.12817 | 0.091553 | 0.16479 | 0.086975 | -0.022888 | 0.14191 | 0.53101 | -120.7718 | 120.3598 | -0.37537 | 120.5109 | 120.5795 | -0.29755 | -0.28381 | 0.068665 | 0.15106 | 120.4651 | 120.6299 | 120.6528 | 120.575 | 120.5109 | 121.019 | 120.575 | -0.28381 | 120.575 | 120.5109 | 120.575 | 120.6528 | 121.019 | -0.59052 | -121.2341
3616.2812 | 121.1609 | -120.4147 | 0.49439 | 0.0096895 | -0.0010596 | 0.0069085 | 0.091287 | -0.024366 | -0.029781 | 0.01527 | -0.018311 | 0.073242 | -0.11902 | 0.07782 | 0.16022 | 0.082397 | -0.013733 | 0.14648 | 0.5722 | -120.7672 | 120.2957 | -0.42114 | 120.3964 | 120.4926 | -0.33417 | -0.35248 | 0.07782 | 0.10071 | 120.401 | 120.5612 | 120.575 | 120.488 | 120.3964 | 120.9869 | 120.4971 | -0.35248 | 120.488 | 120.3964 | 120.4971 | 120.575 | 120.9869 | -0.6134 | -121.2616
3618.0781 | 121.1792 | -120.4926 | 0.43945 | 0.0096895 | 0.0012902 | 0.0054131 | 0.10432 | -0.022443 | -0.03149 | 0.024883 | -0.013733 | 0.086975 | -0.11444 | 0.07782 | 0.10071 | 0.11444 | -0.068665 | 0.16022 | 0.54932 | -120.845 | 120.3781 | -0.35248 | 120.4788 | 120.5704 | -0.33874 | -0.35248 | 0.10986 | 0.10071 | 120.4239 | 120.6528 | 120.5933 | 120.5795 | 120.4788 | 121.0419 | 120.607 | -0.35248 | 120.5795 | 120.4788 | 120.607 | 120.5933 | 121.0419 | -0.55389 | -121.2845
3619.875 | 121.1609 | -120.5246 | 0.43945 | 0.00206 | -0.001914 | 0.0043451 | 0.099405 | -0.024793 | -0.033199 | 0.022747 | 0.10529 | 0.054932 | -0.073242 | 0.19684 | 0.19684 | 0.21973 | -0.20142 | 0.28839 | 0.48065 | -120.8038 | 120.4514 | -0.38452 | 120.6299 | 120.7214 | -0.24261 | -0.27924 | 0.041199 | 0.17853 | 120.3232 | 120.813 | 120.7214 | 120.5795 | 120.6299 | 121.0052 | 120.7443 | -0.27924 | 120.5795 | 120.6299 | 120.7443 | 120.7214 | 121.0052 | -0.5127 | -121.2433
3621.6562 | 121.2021 | -120.5246 | 0.45319 | 0.017319 | -0.0017004 | 0.0043451 | 0.11201 | -0.023298 | -0.034694 | 0.030651 | -0.009155 | 0.073242 | -0.11902 | 0.10071 | 0.12817 | 0.073242 | -0.041199 | 0.15564 | 0.54474 | -120.8496 | 120.4056 | -0.37994 | 120.5154 | 120.6253 | -0.32501 | -0.32501 | 0.091553 | 0.10986 | 120.4834 | 120.6802 | 120.6528 | 120.5978 | 120.5154 | 121.0693 | 120.5978 | -0.32501 | 120.5978 | 120.5154 | 120.5978 | 120.6528 | 121.0693 | -0.5722 | -121.3028
3623.4531 | 121.1746 | -120.7397 | 0.29297 | 0.00206 | 0.0017176 | 0.0071221 | 0.097696 | -0.025434 | -0.032772 | 0.023387 | 0.13275 | 0.041199 | -0.073242 | 0.20142 | 0.17395 | 0.2243 | -0.18768 | 0.27466 | 0.33875 | -121.0098 | 120.6665 | -0.25177 | 120.8725 | 120.9412 | -0.11902 | -0.27008 | 0.045776 | 0.20599 | 120.5521 | 121.0144 | 120.9137 | 120.7809 | 120.8725 | 121.0785 | 120.9641 | -0.27008 | 120.7809 | 120.8725 | 120.9641 | 120.9137 | 121.0785 | -0.36621 | -121.3028
3625.1875 | 121.1792 | -120.7535 | 0.3067 | 0.0096895 | 0.00043578 | 0.0045587 | 0.096842 | -0.024152 | -0.034481 | 0.019329 | 0.004578 | 0.064087 | -0.1236 | 0.09613 | 0.068665 | 0.064087 | -0.004578 | 0.13733 | 0.39825 | -121.0648 | 120.6299 | -0.24261 | 120.7581 | 120.8496 | -0.23804 | -0.31128 | 0.091552 | 0.12817 | 120.7489 | 120.8908 | 120.8221 | 120.8176 | 120.7581 | 121.1517 | 120.8176 | -0.31128 | 120.8176 | 120.7581 | 120.8176 | 120.8221 | 121.1517 | -0.4303 | -121.3715
3626.9688 | 121.1792 | -120.6253 | 0.44403 | 0.017319 | -0.0014868 | 0.0022089 | 0.10197 | -0.023725 | -0.035763 | 0.022533 | 0.013733 | 0.068665 | -0.11902 | 0.086975 | 0.064087 | 0.073242 | -0.004578 | 0.13733 | 0.38452 | -121.0281 | 120.5063 | -0.37537 | 120.639 | 120.7123 | -0.37994 | -0.40283 | -0.05951 | 0.13275 | 120.6207 | 120.7626 | 120.6894 | 120.694 | 120.639 | 121.0098 | 120.6985 | -0.40283 | 120.694 | 120.639 | 120.6985 | 120.6894 | 121.0098 | -0.56305 | -121.4722
3628.75 | 121.2982 | -120.7077 | 0.34332 | 0.0096895 | -0.0010596 | 0.0096857 | 0.11329 | -0.023084 | -0.034481 | 0.0424 | -0.004578 | 0.082397 | -0.12817 | 0.07782 | 0.10071 | 0.09613 | -0.036621 | 0.15564 | 0.44403 | -121.0419 | 120.5795 | -0.26093 | 120.7031 | 120.7855 | -0.24261 | -0.33417 | 0.10071 | 0.1236 | 120.6711 | 120.8633 | 120.8084 | 120.7901 | 120.7031 | 121.1517 | 120.8038 | -0.33417 | 120.7901 | 120.7031 | 120.8038 | 120.8084 | 121.1517 | -0.4715 | -121.3852
3630.4844 | 121.2662 | -120.7306 | 0.39368 | 0.017319 | 0.00022218 | 0.0054131 | 0.12867 | -0.021589 | -0.034908 | 0.059917 | 0.004578 | 0.073242 | -0.11902 | 0.073242 | 0.09613 | 0.073242 | 0.004578 | 0.14648 | 0.4715 | -121.0236 | 120.6116 | -0.32044 | 120.7352 | 120.8038 | -0.29755 | -0.29297 | 0.07782 | 0.1236 | 120.7352 | 120.8771 | 120.8267 | 120.8038 | 120.7352 | 121.2021 | 120.8038 | -0.29297 | 120.8038 | 120.7352 | 120.8038 | 120.8267 | 121.2021 | -0.5127 | -121.4172
3632.2812 | 121.2936 | -120.7947 | 0.29755 | 0.017319 | -0.00020502 | 0.0073359 | 0.12226 | -0.023298 | -0.032131 | 0.044963 | 0 | 0.082397 | -0.11444 | 0.068665 | 0.068665 | 0.082397 | 0 | 0.13733 | 0.42572 | -121.0785 | 120.6802 | -0.21515 | 120.7947 | 120.8633 | -0.22888 | -0.28381 | 0.12817 | 0.11444 | 120.7947 | 120.932 | 120.8633 | 120.8771 | 120.7947 | 121.2204 | 120.8771 | -0.28381 | 120.8771 | 120.7947 | 120.8771 | 120.8633 | 121.2204 | -0.41199 | -121.376
3634.0781 | 121.3165 | -120.6757 | 0.40741 | 0.0096895 | -0.0023412 | 0.0062677 | 0.13358 | -0.026716 | -0.031277 | 0.069744 | 0.064087 | 0.045776 | -0.07782 | 0.16022 | 0.1831 | 0.17853 | -0.11902 | 0.28381 | 0.38452 | -121.0968 | 120.5978 | -0.36163 | 120.7397 | 120.8359 | -0.22431 | -0.42114 | -0.022889 | 0.14191 | 120.5566 | 120.9595 | 120.8588 | 120.7214 | 120.7397 | 121.0602 | 120.8542 | -0.42114 | 120.7214 | 120.7397 | 120.8542 | 120.8588 | 121.0602 | -0.48523 | -121.5042
3635.7969 | 121.3806 | -120.8313 | 0.49896 | -0.0055695 | -0.00084602 | 0.0037043 | 0.098123 | -0.02757 | -0.030636 | 0.02296 | 0.082397 | 0.032043 | -0.068665 | 0.19226 | 0.10071 | 0.19684 | -0.086975 | 0.3067 | 0.2243 | -121.2387 | 120.7626 | -0.46692 | 120.9137 | 121.0236 | -0.39825 | -0.40741 | -0.27466 | 0.15106 | 120.7443 | 121.138 | 120.932 | 120.8633 | 120.9137 | 121.0556 | 121.0281 | -0.40741 | 120.8633 | 120.9137 | 121.0281 | 120.932 | 121.0556 | -0.56763 | -121.7377
3637.5938 | 121.2296 | -121.0007 | 0.17395 | 0.00206 | -0.001914 | 0.0062677 | 0.10496 | -0.027784 | -0.032345 | 0.026164 | 0.027466 | 0.082397 | -0.11444 | 0.1236 | 0.032043 | 0.10529 | -0.009155 | 0.21057 | 0.21515 | -121.3211 | 120.8862 | -0.091553 | 121.0281 | 121.1243 | -0.14191 | -0.32044 | 0.041199 | 0.14191 | 120.9915 | 121.2112 | 121.0327 | 121.0831 | 121.0281 | 121.2158 | 121.106 | -0.32044 | 121.0831 | 121.0281 | 121.106 | 121.0327 | 121.2158 | -0.28839 | -121.4951
3639.3281 | 121.3028 | -120.9641 | 0.13733 | 0.024948 | -0.0034094 | 0.0039179 | 0.22117 | -0.02522 | -0.031704 | 0.025096 | 0.036621 | 0.050354 | -0.11444 | 0.16022 | 0.054932 | 0.19226 | -0.14648 | 0.24719 | 0.18768 | -121.3028 | 120.8496 | -0.086975 | 121.0007 | 121.1243 | -0.082397 | -0.33875 | 0.050354 | 0.15106 | 120.8176 | 121.2112 | 121.019 | 121.0144 | 121.0007 | 121.1517 | 121.1563 | -0.33875 | 121.0144 | 121.0007 | 121.1563 | 121.019 | 121.1517 | -0.25177 | -121.4401
3641.125 | 121.2799 | -120.7214 | 0.46692 | 0.024948 | -0.0010596 | 0.0032769 | 0.30064 | -0.026075 | -0.035335 | 0.23594 | 0.054932 | 0.07782 | -0.11902 | 0.15106 | 0.068665 | 0.12817 | -0.032043 | 0.22888 | 0.37079 | -121.1334 | 120.6024 | -0.3891 | 120.7764 | 120.8725 | -0.39825 | -0.41199 | -0.09613 | 0.17395 | 120.6894 | 120.9503 | 120.7901 | 120.7993 | 120.7764 | 121.0922 | 120.8496 | -0.41199 | 120.7993 | 120.7764 | 120.8496 | 120.7901 | 121.0922 | -0.58594 | -121.6003
3642.8438 | 120.5383 | -15.303 | 98.7579 | 0.00206 | -0.0012732 | 0.0039179 | 0.08082 | 0.034594 | 0.021916 | 0.1851 | -0.018311 | 0.022888 | -0.15564 | 0.059509 | 8.107 | 0.041199 | -0.041199 | 0.11444 | 106.9473 | -14.0854 | 15.1474 | -98.735 | 15.2847 | 15.3625 | -90.6509 | 1.2177 | 8.1894 | 0.13733 | 15.2618 | 15.4175 | 23.41 | 15.3259 | 15.2847 | 122.2504 | 15.3442 | 1.2177 | 15.3259 | 15.2847 | 15.3442 | 23.41 | 122.2504 | -98.9136 | -112.8433
3644.6406 | 121.1746 | -95.723 | 24.9023 | 0.017319 | -0.0017004 | 0.0037043 | 0.037027 | -0.012617 | -0.016964 | 0.0035205 | 0.11902 | 0.027466 | -0.082397 | 0.18768 | 2.0737 | 0.20142 | -0.19684 | 0.27466 | 24.9527 | -96.1761 | 95.6406 | -24.8749 | 95.842 | 95.9106 | -22.8287 | -0.45319 | 0.050354 | 0.20142 | 95.5261 | 95.9976 | 97.7966 | 95.7504 | 95.842 | 120.6757 | 95.9244 | -0.45319 | 95.7504 | 95.842 | 95.9244 | 97.7966 | 120.6757 | -24.9847 | -121.0785
3646.3906 | 121.2616 | -95.8008 | 24.9527 | 0.00206 | -0.002555 | 0.0060541 | 0.057321 | -0.010694 | -0.019954 | 0.02061 | 0.10071 | 0.013733 | -0.07782 | 0.18768 | 2.0645 | 0.20142 | -0.20599 | 0.28381 | 24.9939 | -96.2219 | 95.723 | -24.939 | 95.9015 | 95.9885 | -22.8882 | -0.42114 | 0.041198 | 0.17853 | 95.5948 | 96.0846 | 97.8653 | 95.8145 | 95.9015 | 120.7947 | 96.0022 | -0.42114 | 95.8145 | 95.9015 | 96.0022 | 97.8653 | 120.7947 | -25.0305 | -121.1746
3648.1875 | 121.2296 | -95.8786 | 25.0122 | 0.00206 | -0.0023412 | 0.0026361 | 0.050058 | -0.013044 | -0.019741 | 0.010356 | -0.013733 | 0.09613 | -0.13275 | 0.086975 | 1.9226 | 0.054932 | 0.059509 | 0.16022 | 25.1312 | -96.2219 | 95.7459 | -24.9161 | 95.8649 | 95.9656 | -23.0896 | -0.34332 | 0.11902 | 0.11902 | 95.9381 | 96.0388 | 97.8012 | 95.9747 | 95.8649 | 121.0098 | 95.9335 | -0.34332 | 95.9747 | 95.8649 | 95.9335 | 97.8012 | 121.0098 | -25.145 | -121.2341
3649.9062 | 121.1838 | -95.9747 | 25.0214 | 0.0096895 | -0.00041862 | 0.0058405 | 0.054544 | -0.011976 | -0.019527 | 0.013561 | 0.041199 | 0.073242 | -0.13275 | 0.12817 | 1.9089 | 0.11902 | -0.018311 | 0.21515 | 25.0763 | -96.254 | 95.842 | -24.9481 | 96.0159 | 96.1029 | -23.1125 | -0.27924 | 0.054932 | 0.17395 | 95.9564 | 96.1899 | 97.8836 | 96.048 | 96.0159 | 121.051 | 96.0938 | -0.27924 | 96.048 | 96.0159 | 96.0938 | 97.8836 | 121.051 | -25.1541 | -121.2753
3651.6875 | 121.17 | -95.929 | 25.1129 | 0.017319 | -0.0017004 | 0.0034905 | 0.056681 | -0.0098395 | -0.024227 | 0.014202 | 0.032043 | 0.059509 | -0.13275 | 0.13733 | 1.9272 | 0.1236 | -0.054932 | 0.2243 | 25.1587 | -96.1899 | 95.7962 | -25.0534 | 95.961 | 96.0663 | -23.1857 | -0.26093 | 0.045776 | 0.16479 | 95.874 | 96.1533 | 97.8561 | 95.9885 | 95.961 | 121.0876 | 96.0526 | -0.26093 | 95.9885 | 95.961 | 96.0526 | 97.8561 | 121.0876 | -25.2457 | -121.3028
3653.4844 | 121.3028 | -96.4188 | 24.5728 | 0.0096895 | -0.004264 | 0.0049859 | 0.041513 | -0.013258 | -0.018246 | 0.0075793 | 0.086975 | 0.032043 | -0.07782 | 0.15564 | 1.9318 | 0.1831 | -0.17853 | 0.25635 | 24.5316 | -96.8491 | 96.3409 | -24.5407 | 96.5057 | 96.5744 | -22.641 | -0.4303 | -0.041199 | 0.16479 | 96.2402 | 96.6751 | 98.3505 | 96.4508 | 96.5057 | 120.9503 | 96.6019 | -0.4303 | 96.4508 | 96.5057 | 96.6019 | 98.3505 | 120.9503 | -24.6506 | -121.4218
3655.2656 | 121.2341 | -96.9818 | 24.1104 | 0.017319 | -0.004264 | 0.0030633 | 0.078043 | -0.013044 | -0.021236 | 0.048168 | 0.091553 | 0.022888 | -0.082397 | 0.21057 | 2.1927 | 0.20142 | -0.13275 | 0.32501 | 24.147 | -97.1512 | 96.8994 | -24.0875 | 97.0734 | 97.1924 | -21.9177 | -0.16937 | 0.036621 | 0.17395 | 96.8491 | 97.3068 | 99.1745 | 97.0047 | 97.0734 | 121.1288 | 97.1832 | -0.16937 | 97.0047 | 97.0734 | 97.1832 | 99.1745 | 121.1288 | -24.1928 | -121.2616
3657 | 121.3486 | -21.7575 | 99.1882 | 0.017319 | -0.00063242 | 0.0051995 | 0.32243 | 0.027758 | 0.0050394 | 0.39039 | -0.018311 | 0.050354 | -0.10529 | 0.082397 | 31.1417 | 0.068665 | -0.091553 | 0.1236 | 97.554 | -23.7991 | 21.6522 | -99.1379 | 21.7392 | 21.8399 | -68.0466 | -2.0416 | -1.6342 | 0.086975 | 21.666 | 21.8811 | 52.8992 | 21.8079 | 21.7392 | 119.3115 | 21.8262 | -2.0416 | 21.8079 | 21.7392 | 21.8262 | 52.8992 | 119.3115 | -99.2935 | -122.9874
3658.7812 | 121.2616 | -3.804 | 117.1326 | 0.017319 | -0.002555 | 0.0039179 | 0.058176 | 0.036944 | -0.01675 | 0.13276 | 0.041199 | 0.004578 | -0.11902 | 0.17853 | 89.2639 | 0.16022 | -0.16937 | 0.27466 | 117.4484 | -3.717 | 3.685 | -117.128 | 3.8452 | 3.9825 | -27.8687 | 0.086975 | 0.31586 | 0.16022 | 3.6346 | 4.0787 | 93.0679 | 3.8086 | 3.8452 | 121.2524 | 3.9642 | 0.086975 | 3.8086 | 3.8452 | 3.9642 | 93.0679 | 121.2524 | -117.2516 | -120.8496
3660.5781 | 121.2845 | -4.7562 | 116.0843 | 0.017319 | 0.00064938 | 0.0081903 | 0.081674 | 0.037585 | 0.026615 | 0.19386 | 0.013733 | 0.050354 | -0.15106 | 0.11444 | 7.6813 | 0.073242 | -0.045776 | 0.16022 | 116.6931 | -4.8203 | 4.6051 | -116.0339 | 4.7699 | 4.8706 | -108.403 | -0.064086 | 0.60883 | 0.16479 | 4.7104 | 4.9164 | 12.4374 | 4.8065 | 4.7699 | 121.4493 | 4.8294 | -0.064086 | 4.8065 | 4.7699 | 4.8294 | 12.4374 | 121.4493 | -116.2354 | -120.9045
3662.3125 | 121.2296 | -5.7037 | 115.0314 | 0.017319 | -0.0012732 | 0.0049859 | 0.18614 | 0.035235 | 0.022984 | 0.26222 | 0 | 0.027466 | -0.13733 | 0.14191 | 11.1191 | 0.082397 | -0.073242 | 0.19226 | 115.1505 | -6.3858 | 5.5664 | -115.004 | 5.7037 | 5.8456 | -103.9124 | -0.68207 | 0.11902 | 0.13733 | 5.6305 | 5.896 | 16.8228 | 5.7312 | 5.7037 | 120.8542 | 5.7861 | -0.68207 | 5.7312 | 5.7037 | 5.7861 | 16.8228 | 120.8542 | -115.1688 | -121.4172
3664.1094 | 121.2708 | -4.1748 | 117.1371 | 0.00206 | 0.00086298 | 0.0058405 | 0.96714 | 0.03908 | -0.0058554 | 1.0206 | 0.10986 | 0.036621 | 0 | 0.18768 | 61.2854 | 0.16937 | -0.2243 | 0.24719 | 109.8129 | -11.4578 | 4.1748 | -117.1005 | 4.2847 | 4.3625 | -55.8517 | -7.283 | -7.3242 | 0.10986 | 3.9505 | 4.422 | 65.4602 | 4.2114 | 4.2847 | 113.9877 | 4.3442 | -7.283 | 4.2114 | 4.2847 | 4.3442 | 65.4602 | 113.9877 | -117.1371 | -128.595
3665.9062 | 121.431 | -4.8203 | 116.7206 | 0.017319 | 0.001504 | 0.0047723 | 0.45701 | 0.038226 | 0.027897 | 0.46238 | 0.009155 | 0.009155 | -0.10071 | 0.13275 | 7.8598 | 0.13275 | -0.14191 | 0.18768 | 115.8508 | -5.4794 | 4.7195 | -116.7114 | 4.8294 | 4.953 | -108.8608 | -0.65918 | -0.86975 | 0.10986 | 4.6783 | 5.0079 | 12.6801 | 4.8294 | 4.8294 | 120.6711 | 4.953 | -0.65918 | 4.8294 | 4.8294 | 4.953 | 12.6801 | 120.6711 | -116.8213 | -122.2
3667.6875 | 121.3989 | -112.9028 | 8.1894 | 0.0096895 | 8.578e-06 | 0.0028497 | 0.076334 | -0.019666 | -0.031277 | 0.011211 | 0.09613 | 0.018311 | -0.054932 | 0.2243 | 2.4124 | 0.22888 | -0.13733 | 0.32501 | 8.2535 | -113.2645 | 112.8479 | -8.1711 | 112.999 | 113.1271 | -5.777 | -0.36163 | 0.064087 | 0.15106 | 112.7655 | 113.2278 | 115.3152 | 112.9211 | 112.999 | 121.1563 | 113.1317 | -0.36163 | 112.9211 | 112.999 | 113.1317 | 115.3152 | 121.1563 | -8.2443 | -121.4539
3669.4844 | 121.5088 | -114.2212 | 6.839 | 0.00206 | 0.00022218 | 0.0073359 | 0.084451 | -0.02223 | -0.030849 | 0.011424 | -0.022888 | 0.091553 | -0.12817 | 0.082397 | 2.3254 | 0.068665 | -0.018311 | 0.13733 | 6.9717 | -114.6011 | 114.093 | -6.7474 | 114.1983 | 114.3036 | -4.5136 | -0.37994 | 0.13275 | 0.10529 | 114.2029 | 114.3585 | 116.5466 | 114.3127 | 114.1983 | 121.1929 | 114.2899 | -0.37994 | 114.3127 | 114.1983 | 114.2899 | 116.5466 | 121.1929 | -6.9672 | -121.4401
3671.2656 | 121.4951 | -114.5599 | 6.6055 | 0.0096895 | -0.0012732 | 0.0058405 | 0.084024 | -0.020521 | -0.031063 | 0.013133 | 0.018311 | 0.086975 | -0.10529 | 0.10529 | 1.6113 | 0.09613 | -0.086975 | 0.18768 | 6.6788 | -114.9078 | 114.4547 | -6.5186 | 114.5782 | 114.6652 | -4.9942 | -0.3479 | 0.073242 | 0.1236 | 114.473 | 114.7476 | 116.1713 | 114.6469 | 114.5782 | 121.2387 | 114.6561 | -0.3479 | 114.6469 | 114.5782 | 114.6561 | 116.1713 | 121.2387 | -6.7108 | -121.5134
3673 | 121.4951 | -114.8163 | 6.3675 | 0.017319 | -0.0017004 | 0.0045587 | 0.082529 | -0.022871 | -0.030208 | 0.013133 | -0.009155 | 0.091553 | -0.086975 | 0.068665 | 1.6388 | 0.073242 | -0.013733 | 0.12817 | 6.459 | -115.1688 | 114.7293 | -6.2759 | 114.8071 | 114.8849 | -4.7287 | -0.35248 | 0.091552 | 0.07782 | 114.8026 | 114.9445 | 116.4551 | 114.9078 | 114.8071 | 121.2753 | 114.8895 | -0.35248 | 114.9078 | 114.8071 | 114.8895 | 116.4551 | 121.2753 | -6.4545 | -121.5363
3674.7812 | 121.4081 | -116.0522 | 5.2231 | 0.0096895 | -0.00041862 | 0.0013543 | 0.079538 | -0.024793 | -0.02914 | 0.01057 | 0.10986 | 0.041199 | -0.050354 | 0.19684 | 1.6022 | 0.22888 | -0.16022 | 0.33875 | 5.2322 | -116.3086 | 116.0019 | -5.1819 | 116.1621 | 116.2491 | -3.6209 | -0.25635 | 0.009156 | 0.16022 | 115.892 | 116.391 | 117.6544 | 116.0934 | 116.1621 | 121.2845 | 116.2811 | -0.25635 | 116.0934 | 116.1621 | 116.2811 | 117.6544 | 121.2845 | -5.2734 | -121.5317
3676.5938 | 121.4218 | -116.0019 | 5.3238 | 0.0096895 | -0.0029822 | 0.0045587 | 0.084024 | -0.025861 | -0.032345 | 0.011211 | 0.073242 | 0.059509 | -0.036621 | 0.13733 | 1.6342 | 0.15106 | -0.022888 | 0.24719 | 5.3421 | -116.2903 | 115.9653 | -5.2643 | 116.0751 | 116.1392 | -3.6896 | -0.28839 | 0.01831 | 0.10986 | 115.979 | 116.2491 | 117.6361 | 116.0614 | 116.0751 | 121.344 | 116.153 | -0.28839 | 116.0614 | 116.0751 | 116.153 | 117.6361 | 121.344 | -5.3604 | -121.6141
3678.3281 | 121.3806 | -115.5533 | 5.7724 | 0.017319 | -0.0027686 | 0.010326 | 0.079752 | -0.024793 | -0.027645 | 0.010356 | 0.10071 | 0.036621 | -0.036621 | 0.21973 | 1.8082 | 0.20599 | -0.13733 | 0.33875 | 5.8685 | -115.7272 | 115.5167 | -5.7358 | 115.654 | 115.773 | -3.9642 | -0.17395 | 0.09613 | 0.13733 | 115.416 | 115.892 | 117.3615 | 115.5899 | 115.654 | 121.4218 | 115.7593 | -0.17395 | 115.5899 | 115.654 | 115.7593 | 117.3615 | 121.4218 | -5.809 | -121.4996
3680.1094 | 121.3852 | -116.4825 | 4.8111 | -0.0055695 | -0.002555 | 0.0039179 | 0.084451 | -0.023725 | -0.03149 | 0.011638 | 0.091553 | 0.054932 | -0.036621 | 0.19226 | 1.8219 | 0.1831 | -0.10529 | 0.30212 | 4.8614 | -116.7618 | 116.4459 | -4.7562 | 116.5741 | 116.6748 | -2.9892 | -0.27924 | 0.050354 | 0.12817 | 116.3773 | 116.7847 | 118.3044 | 116.5375 | 116.5741 | 121.344 | 116.6656 | -0.27924 | 116.5375 | 116.5741 | 116.6656 | 118.3044 | 121.344 | -4.8477 | -121.5729
3681.9062 | 121.3852 | -117.3615 | 3.9734 | 0.017319 | -0.0051184 | 0.0073359 | 0.089792 | -0.022443 | -0.032558 | 0.011638 | 0.045776 | 0.07782 | -0.11902 | 0.15564 | 1.6937 | 0.11902 | -0.032043 | 0.21973 | 4.0237 | -117.6361 | 117.2424 | -3.8956 | 117.4072 | 117.5171 | -2.2797 | -0.27466 | 0.050354 | 0.16479 | 117.3294 | 117.5812 | 119.0552 | 117.4393 | 117.4072 | 121.3852 | 117.4805 | -0.27466 | 117.4393 | 117.4072 | 117.4805 | 119.0552 | 121.3852 | -4.0924 | -121.6095
3683.7031 | 121.4035 | -117.6178 | 3.7354 | 0.00206 | -0.0012732 | 0.0062677 | 0.082529 | -0.024366 | -0.029995 | 0.012065 | 0.11444 | 0.050354 | -0.050354 | 0.21057 | 1.9135 | 0.2243 | -0.15106 | 0.31586 | 3.7857 | -117.8329 | 117.5674 | -3.685 | 117.7322 | 117.8284 | -1.8219 | -0.21515 | 0.050354 | 0.16479 | 117.4667 | 117.9337 | 119.5312 | 117.6682 | 117.7322 | 121.4035 | 117.8421 | -0.21515 | 117.6682 | 117.7322 | 117.8421 | 119.5312 | 121.4035 | -3.7857 | -121.5683
3685.5 | 121.5363 | -118.1168 | 3.1265 | 0.017319 | -0.0068274 | 0.0028497 | 0.084238 | -0.026716 | -0.03149 | 0.012493 | 0.027466 | 0.054932 | -0.073242 | 0.13275 | 1.6937 | 0.13733 | -0.10529 | 0.25177 | 3.1723 | -118.4692 | 118.0435 | -3.0716 | 118.1442 | 118.2495 | -1.4328 | -0.35248 | 0.045776 | 0.10071 | 118.0115 | 118.3685 | 119.8105 | 118.1717 | 118.1442 | 121.2891 | 118.2541 | -0.35248 | 118.1717 | 118.1442 | 118.2541 | 119.8105 | 121.2891 | -3.1998 | -121.5958
3687.2344 | 121.4493 | -118.3548 | 3.0075 | 0.0096895 | -0.002555 | 0.0084039 | 0.092996 | -0.02458 | -0.033413 | 0.012065 | 0.027466 | 0.068665 | -0.10529 | 0.11444 | 1.7075 | 0.082397 | -0.018311 | 0.15564 | 3.035 | -118.6752 | 118.2495 | -2.9388 | 118.3823 | 118.4692 | -1.3 | -0.32043 | 0.027466 | 0.13275 | 118.3365 | 118.5104 | 120.0623 | 118.4235 | 118.3823 | 121.3898 | 118.4372 | -0.32043 | 118.4235 | 118.3823 | 118.4372 | 120.0623 | 121.3898 | -3.1128 | -121.6827
3689.0312 | 121.4127 | -118.4463 | 2.9114 | 0.0096895 | 0.001504 | 0.0071221 | 0.090433 | -0.023511 | -0.033626 | 0.013561 | 0.064087 | 0.054932 | -0.10529 | 0.13733 | 1.8127 | 0.10986 | -0.041199 | 0.19226 | 2.9572 | -118.7485 | 118.3411 | -2.8564 | 118.5104 | 118.5837 | -1.0986 | -0.30212 | 0.045776 | 0.16937 | 118.4052 | 118.6386 | 120.2591 | 118.5013 | 118.5104 | 121.4035 | 118.5562 | -0.30212 | 118.5013 | 118.5104 | 118.5562 | 120.2591 | 121.4035 | -3.0167 | -121.6599
3690.8281 | 121.4905 | -118.5837 | 2.6962 | 0.00206 | -0.0051184 | 0.0051995 | 0.087869 | -0.023725 | -0.033626 | 0.013133 | 0.10071 | 0.013733 | -0.050354 | 0.20599 | 1.8814 | 0.20142 | -0.20599 | 0.29755 | 2.7557 | -118.8721 | 118.5333 | -2.6825 | 118.6844 | 118.7897 | -0.81482 | -0.28839 | 0.059509 | 0.15106 | 118.3777 | 118.8812 | 120.4651 | 118.5974 | 118.6844 | 121.3394 | 118.7851 | -0.28839 | 118.5974 | 118.6844 | 118.7851 | 120.4651 | 121.3394 | -2.7466 | -121.5683
3692.625 | 121.4996 | -118.634 | 2.6733 | 0.017319 | -0.0023412 | 0.0073359 | 0.088938 | -0.023725 | -0.032131 | 0.011211 | 0.10529 | 0.041199 | -0.022888 | 0.20599 | 1.9547 | 0.19684 | -0.18768 | 0.29755 | 2.7374 | -118.9316 | 118.6111 | -2.6321 | 118.7393 | 118.84 | -0.71869 | -0.29755 | 0.064087 | 0.12817 | 118.4463 | 118.9316 | 120.5887 | 118.6752 | 118.7393 | 121.3715 | 118.8309 | -0.29755 | 118.6752 | 118.7393 | 118.8309 | 120.5887 | 121.3715 | -2.6962 | -121.6049
3694.3594 | 121.4722 | -118.6935 | 2.6642 | 0.0096895 | -0.0017004 | 0.0037043 | 0.086588 | -0.025648 | -0.030636 | 0.011852 | -0.032043 | 0.091553 | -0.09613 | 0.086975 | 1.8951 | 0.064087 | 0.073242 | 0.1831 | 2.7466 | -119.0186 | 118.5974 | -2.5726 | 118.6615 | 118.7805 | -0.76904 | -0.32501 | 0.082397 | 0.064087 | 118.7668 | 118.8766 | 120.5887 | 118.7851 | 118.6615 | 121.4401 | 118.7576 | -0.32501 | 118.7851 | 118.6615 | 118.7576 | 120.5887 | 121.4401 | -2.7603 | -121.6827
3696.1562 | 121.55 | -118.7164 | 2.5955 | 0.017319 | -0.0034094 | 0.0075495 | 0.090647 | -0.023084 | -0.032985 | 0.012706 | -0.018311 | 0.07782 | -0.09613 | 0.059509 | 1.9272 | 0.041199 | 0.018311 | 0.10529 | 2.6962 | -119.0369 | 118.6203 | -2.5177 | 118.6981 | 118.7759 | -0.66834 | -0.32043 | 0.10071 | 0.077819 | 118.7347 | 118.8217 | 120.6436 | 118.7943 | 118.6981 | 121.4127 | 118.7576 | -0.32043 | 118.7943 | 118.6981 | 118.7576 | 120.6436 | 121.4127 | -2.6917 | -121.6324
3697.9375 | 121.4401 | -119.0323 | 2.3712 | 0.0096895 | -0.00041862 | 0.0064813 | 0.093424 | -0.023939 | -0.031917 | 0.013561 | 0.07782 | 0.059509 | -0.07782 | 0.15106 | 1.8402 | 0.1236 | -0.050354 | 0.21515 | 2.4216 | -119.3436 | 118.9545 | -2.3117 | 119.1101 | 119.1833 | -0.53101 | -0.31128 | 0.050354 | 0.15564 | 118.9819 | 119.2474 | 120.8725 | 119.0918 | 119.1101 | 121.4539 | 119.1559 | -0.31128 | 119.0918 | 119.1101 | 119.1559 | 120.8725 | 121.4539 | -2.449 | -121.7148
3699.7188 | 121.4447 | -119.0231 | 2.3987 | 0.017319 | -0.0012732 | 0.0037043 | 0.093851 | -0.023298 | -0.032345 | 0.015056 | 0.054932 | 0.068665 | -0.082397 | 0.13275 | 1.918 | 0.11902 | -0.041199 | 0.21057 | 2.417 | -119.339 | 118.9407 | -2.33 | 119.0781 | 119.1559 | -0.48065 | -0.31586 | 0.01831 | 0.13733 | 118.9819 | 119.2337 | 120.9412 | 119.0918 | 119.0781 | 121.4401 | 119.1422 | -0.31586 | 119.0918 | 119.0781 | 119.1422 | 120.9412 | 121.4401 | -2.4811 | -121.7377
3701.5312 | 121.4996 | -119.0002 | 2.3758 | 0.017319 | -0.001914 | 0.0090447 | 0.086374 | -0.025648 | -0.032558 | 0.013133 | -0.013733 | 0.10529 | -0.086975 | 0.073242 | 1.9226 | 0.082397 | 0.073242 | 0.17395 | 2.4261 | -119.3481 | 118.9133 | -2.2705 | 118.9865 | 119.0735 | -0.45319 | -0.3479 | 0.050354 | 0.073242 | 119.0735 | 119.1742 | 120.9229 | 119.1055 | 118.9865 | 121.4264 | 119.0826 | -0.3479 | 119.1055 | 118.9865 | 119.0826 | 120.9229 | 121.4264 | -2.4628 | -121.7239
3703.2656 | 121.4996 | -119.0323 | 2.3529 | 0.0096895 | -0.0023412 | 0.0071221 | 0.088724 | -0.025007 | -0.03384 | 0.0099293 | -0.004578 | 0.091553 | -0.07782 | 0.073242 | 1.9318 | 0.073242 | 0.059509 | 0.16937 | 2.3987 | -119.3893 | 118.9545 | -2.2614 | 119.0277 | 119.1055 | -0.42114 | -0.35706 | 0.045777 | 0.073242 | 119.0918 | 119.2017 | 120.9641 | 119.1238 | 119.0277 | 121.431 | 119.1055 | -0.35706 | 119.1238 | 119.0277 | 119.1055 | 120.9641 | 121.431 | -2.4307 | -121.7422
3705.0625 | 121.4905 | -119.0872 | 2.3254 | 0.00206 | -0.0017004 | 0.0060541 | 0.086801 | -0.025861 | -0.030849 | 0.012493 | 0.11444 | 0.054932 | -0.064087 | 0.19684 | 2.0554 | 0.21057 | -0.11902 | 0.3067 | 2.3392 | -119.4214 | 119.0231 | -2.2705 | 119.2017 | 119.2841 | -0.27008 | -0.33417 | 0.013733 | 0.17853 | 118.9682 | 119.3939 | 121.1426 | 119.1422 | 119.2017 | 121.4264 | 119.2978 | -0.33417 | 119.1422 | 119.2017 | 119.2978 | 121.1426 | 121.4264 | -2.3895 | -121.7468
3706.8594 | 121.5454 | -119.101 | 2.3071 | 0.017319 | -0.00063242 | 0.0047723 | 0.091287 | -0.02458 | -0.034694 | 0.013774 | 0.004578 | 0.086975 | -0.09613 | 0.07782 | 1.9272 | 0.073242 | 0.041199 | 0.15564 | 2.3804 | -119.4534 | 119.0048 | -2.2202 | 119.1055 | 119.1788 | -0.37994 | -0.35248 | 0.073242 | 0.10071 | 119.1422 | 119.2566 | 121.0281 | 119.1879 | 119.1055 | 121.4813 | 119.1742 | -0.35248 | 119.1879 | 119.1055 | 119.1742 | 121.0281 | 121.4813 | -2.4033 | -121.7606
3708.6562 | 121.5408 | -119.1284 | 2.2705 | 0.0096895 | -0.00063242 | 0.0077631 | 0.094705 | -0.023511 | -0.033413 | 0.013561 | 0.004578 | 0.082397 | -0.082397 | 0.07782 | 1.9226 | 0.07782 | 0.013733 | 0.13733 | 2.33 | -119.4763 | 119.046 | -2.1881 | 119.133 | 119.2062 | -0.3479 | -0.3479 | 0.059509 | 0.086975 | 119.1422 | 119.2657 | 121.051 | 119.2108 | 119.133 | 121.4584 | 119.2062 | -0.3479 | 119.2108 | 119.133 | 119.2062 | 121.051 | 121.4584 | -2.3529 | -121.7468
3710.3906 | 121.6324 | -119.1788 | 2.2247 | 0.00206 | 0.00022218 | 0.0060541 | 0.084665 | -0.025434 | -0.030636 | 0.011852 | 0.059509 | 0.064087 | -0.064087 | 0.15106 | 1.9363 | 0.16022 | -0.10071 | 0.22888 | 2.2476 | -119.5358 | 119.1147 | -2.1606 | 119.2383 | 119.3298 | -0.28839 | -0.35706 | 0.022889 | 0.1236 | 119.0781 | 119.4077 | 121.1151 | 119.2429 | 119.2383 | 121.4264 | 119.339 | -0.35706 | 119.2429 | 119.2383 | 119.339 | 121.1151 | 121.4264 | -2.2888 | -121.7606
3712.1875 | 121.4722 | -119.2383 | 2.2247 | 0.0096895 | -0.00063242 | 0.0088311 | 0.09321 | -0.022871 | -0.034481 | 0.010784 | 0.059509 | 0.07782 | -0.10529 | 0.15564 | 1.9135 | 0.13733 | -0.045776 | 0.2243 | 2.2842 | -119.5267 | 119.133 | -2.1469 | 119.2978 | 119.3939 | -0.31128 | -0.28839 | 0.05951 | 0.16479 | 119.1925 | 119.4626 | 121.1517 | 119.3161 | 119.2978 | 121.5225 | 119.3756 | -0.28839 | 119.3161 | 119.2978 | 119.3756 | 121.1517 | 121.5225 | -2.33 | -121.7514
3713.9688 | 121.637 | -119.2062 | 2.1606 | 0.0096895 | 0.0029992 | 0.010113 | 0.094705 | -0.02223 | -0.032558 | 0.014842 | 0.022888 | 0.10529 | -0.082397 | 0.059509 | 1.8448 | 0.073242 | -0.004578 | 0.13275 | 2.2751 | -119.6365 | 119.1238 | -2.0554 | 119.2291 | 119.2657 | -0.31586 | -0.4303 | 0.11444 | 0.10528 | 119.2017 | 119.339 | 121.051 | 119.3115 | 119.2291 | 121.4813 | 119.2795 | -0.4303 | 119.3115 | 119.2291 | 119.2795 | 121.051 | 121.4813 | -2.243 | -121.7972
3715.75 | 121.5958 | -119.2703 | 2.1652 | 0.0096895 | -0.0010596 | 0.010113 | 0.09086 | -0.022016 | -0.033199 | 0.01292 | 0.10529 | 0.045776 | -0.045776 | 0.18768 | 1.9409 | 0.20142 | -0.20142 | 0.29297 | 2.1835 | -119.5587 | 119.2245 | -2.1194 | 119.3756 | 119.458 | -0.2243 | -0.28839 | 0.018311 | 0.15106 | 119.0689 | 119.5633 | 121.2112 | 119.3161 | 119.3756 | 121.4539 | 119.4717 | -0.28839 | 119.3161 | 119.3756 | 119.4717 | 121.2112 | 121.4539 | -2.211 | -121.7239
3717.5625 | 121.669 | -119.3939 | 2.0462 | 0.00206 | -0.00084602 | 0.0043451 | 0.088297 | -0.025861 | -0.03149 | 0.012493 | 0.036621 | 0.068665 | -0.054932 | 0.14648 | 1.7807 | 0.15564 | -0.09613 | 0.23346 | 2.1057 | -119.7144 | 119.339 | -1.9775 | 119.4305 | 119.5404 | -0.2655 | -0.32043 | 0.059509 | 0.091553 | 119.2978 | 119.6274 | 121.1746 | 119.4626 | 119.4305 | 121.4996 | 119.5496 | -0.32043 | 119.4626 | 119.4305 | 119.5496 | 121.1746 | 121.4996 | -2.1011 | -121.7606
3719.2969 | 121.6141 | -119.4168 | 2.0142 | 0.017319 | -0.0027686 | 0.0026361 | 0.093637 | -0.024793 | -0.030849 | 0.013347 | 0.09613 | 0.050354 | -0.054932 | 0.17853 | 1.7487 | 0.19684 | -0.18768 | 0.27466 | 2.0279 | -119.7327 | 119.3619 | -1.9638 | 119.5129 | 119.5953 | -0.2655 | -0.31586 | 0.013733 | 0.15106 | 119.2291 | 119.6915 | 121.1655 | 119.4672 | 119.5129 | 121.4447 | 119.6136 | -0.31586 | 119.4672 | 119.5129 | 119.6136 | 121.1655 | 121.4447 | -2.0691 | -121.7468
3721.0781 | 121.6644 | -119.4992 | 1.9089 | 0.017319 | -0.0021276 | 0.0056269 | 0.096414 | -0.022871 | -0.034054 | 0.013561 | -0.013733 | 0.068665 | -0.082397 | 0.073242 | 1.5427 | 0.073242 | -0.009155 | 0.13275 | 2.0004 | -119.8608 | 119.4168 | -1.8402 | 119.4855 | 119.5724 | -0.36621 | -0.36163 | 0.091552 | 0.068664 | 119.4901 | 119.632 | 121.0419 | 119.5679 | 119.4855 | 121.4996 | 119.5724 | -0.36163 | 119.5679 | 119.4855 | 119.5724 | 121.0419 | 121.4996 | -1.9913 | -121.7697
3722.7969 | 121.637 | -119.6411 | 1.8082 | 0.017319 | -0.0021276 | 0.010113 | 0.091074 | -0.023511 | -0.031277 | 0.012279 | 0.082397 | 0.064087 | -0.059509 | 0.1831 | 1.5015 | 0.18768 | -0.16479 | 0.2655 | 1.8539 | -119.957 | 119.5816 | -1.7441 | 119.7235 | 119.8242 | -0.3067 | -0.31586 | 0.045776 | 0.14191 | 119.4763 | 119.9066 | 121.1426 | 119.7052 | 119.7235 | 121.4951 | 119.8288 | -0.31586 | 119.7052 | 119.7235 | 119.8288 | 121.1426 | 121.4951 | -1.8677 | -121.7651
3724.5938 | 121.55 | -119.7372 | 1.7807 | 0.00206 | -0.00041862 | 0.0071221 | 0.094919 | -0.024793 | -0.033199 | 0.014202 | 0.050354 | 0.059509 | -0.064087 | 0.14648 | 1.387 | 0.11444 | -0.004578 | 0.23346 | 1.8356 | -120.0394 | 119.6732 | -1.7212 | 119.7876 | 119.8837 | -0.39368 | -0.30212 | 0.054931 | 0.11444 | 119.7327 | 119.9707 | 121.1243 | 119.7968 | 119.7876 | 121.5729 | 119.8517 | -0.30212 | 119.7968 | 119.7876 | 119.8517 | 121.1243 | 121.5729 | -1.8448 | -121.8201
3726.3281 | 121.6095 | -119.8425 | 1.6434 | 0.0096895 | -0.0012732 | 0.0034905 | 0.092783 | -0.026502 | -0.031917 | 0.012706 | 0.013733 | 0.086975 | -0.073242 | 0.10529 | 1.2314 | 0.082397 | 0.041199 | 0.19226 | 1.7441 | -120.1767 | 119.7693 | -1.5564 | 119.8563 | 119.9478 | -0.41199 | -0.33417 | 0.10071 | 0.086975 | 119.8837 | 120.0348 | 121.0739 | 119.9295 | 119.8563 | 121.5866 | 119.9249 | -0.33417 | 119.9295 | 119.8563 | 119.9249 | 121.0739 | 121.5866 | -1.7166 | -121.8201
3728.1094 | 121.5591 | -119.9524 | 1.5747 | 0.00206 | -0.0021276 | 0.0047723 | 0.093851 | -0.023511 | -0.034267 | 0.01292 | 0.068665 | 0.068665 | -0.036621 | 0.14648 | 1.1765 | 0.13275 | -0.032043 | 0.21515 | 1.6205 | -120.2271 | 119.9158 | -1.506 | 120.0211 | 120.0989 | -0.39825 | -0.27466 | 0.045776 | 0.10529 | 119.9203 | 120.1675 | 121.1288 | 120.0211 | 120.0211 | 121.5729 | 120.0851 | -0.27466 | 120.0211 | 120.0211 | 120.0851 | 121.1288 | 121.5729 | -1.6113 | -121.8018
3729.8906 | 121.6187 | -120.0302 | 1.506 | 0.0096895 | 0.002572 | 0.0043451 | 0.091074 | -0.025007 | -0.033199 | 0.013347 | -0.004578 | 0.086975 | -0.050354 | 0.086975 | 1.0345 | 0.054932 | 0.064087 | 0.16022 | 1.5381 | -120.3964 | 119.9799 | -1.4191 | 120.0256 | 120.1172 | -0.4715 | -0.36621 | 0.032044 | 0.045776 | 120.0943 | 120.1904 | 121.0648 | 120.1172 | 120.0256 | 121.5683 | 120.0851 | -0.36621 | 120.1172 | 120.0256 | 120.0851 | 121.0648 | 121.5683 | -1.5564 | -121.9025
3731.7031 | 121.6873 | -120.1309 | 1.3458 | 0.00206 | -0.0017004 | 0.0073359 | 0.092356 | -0.023084 | -0.033413 | 0.013774 | 0.082397 | 0.045776 | -0.013733 | 0.17395 | 1.062 | 0.20142 | -0.16479 | 0.2655 | 1.387 | -120.4193 | 120.1172 | -1.3 | 120.2133 | 120.3049 | -0.28381 | -0.28839 | 0.041199 | 0.09613 | 119.9661 | 120.3964 | 121.1929 | 120.1767 | 120.2133 | 121.5179 | 120.3323 | -0.28839 | 120.1767 | 120.2133 | 120.3323 | 121.1929 | 121.5179 | -1.3596 | -121.7651
3733.5 | 121.6324 | -120.2866 | 1.2497 | 0.0096895 | -0.0021276 | 0.0056269 | 0.092569 | -0.026502 | -0.032345 | 0.01292 | -0.013733 | 0.091553 | -0.059509 | 0.091553 | 0.86517 | 0.07782 | 0.041199 | 0.1831 | 1.2955 | -120.6116 | 120.2271 | -1.1581 | 120.2728 | 120.3781 | -0.38452 | -0.32501 | 0.045776 | 0.045776 | 120.3278 | 120.4697 | 121.1517 | 120.3781 | 120.2728 | 121.582 | 120.3644 | -0.32501 | 120.3781 | 120.2728 | 120.3644 | 121.1517 | 121.582 | -1.3092 | -121.8613
3735.2344 | 121.7422 | -120.3552 | 1.1215 | 0.0096895 | -0.0014868 | 0.0041315 | 0.090647 | -0.026502 | -0.034054 | 0.015697 | 0.036621 | 0.045776 | -0.022888 | 0.1236 | 0.82855 | 0.16022 | -0.13733 | 0.24719 | 1.2039 | -120.7077 | 120.3323 | -1.0757 | 120.3918 | 120.4788 | -0.29297 | -0.35248 | 0.082397 | 0.059509 | 120.2179 | 120.6024 | 121.1838 | 120.401 | 120.3918 | 121.5591 | 120.5154 | -0.35248 | 120.401 | 120.3918 | 120.5154 | 121.1838 | 121.5591 | -1.1444 | -121.8292
3737.0469 | 121.7285 | -120.4742 | 1.062 | 0.0096895 | -0.001914 | 0.0019953 | 0.092783 | -0.027357 | -0.032985 | 0.012706 | 0.054932 | 0.050354 | -0.022888 | 0.12817 | 0.75531 | 0.15106 | -0.10529 | 0.23346 | 1.1169 | -120.7764 | 120.4514 | -1.0117 | 120.5292 | 120.6024 | -0.3067 | -0.30212 | 0.054931 | 0.07782 | 120.369 | 120.7077 | 121.2296 | 120.5246 | 120.5292 | 121.5912 | 120.6253 | -0.30212 | 120.5246 | 120.5292 | 120.6253 | 121.2296 | 121.5912 | -1.0849 | -121.8384
3738.8438 | 121.7331 | -120.4376 | 1.0529 | -0.0055695 | 0.00022218 | 0.0064813 | 0.09791 | -0.02522 | -0.034054 | 0.014415 | -0.013733 | 0.086975 | -0.086975 | 0.082397 | 0.65918 | 0.073242 | -0.013733 | 0.14191 | 1.1444 | -120.7764 | 120.3506 | -0.96588 | 120.4239 | 120.52 | -0.39368 | -0.33874 | 0.091553 | 0.073242 | 120.4239 | 120.5795 | 121.0968 | 120.5246 | 120.4239 | 121.582 | 120.5109 | -0.33874 | 120.5246 | 120.4239 | 120.5109 | 121.0968 | 121.582 | -1.1398 | -121.8292
3740.6406 | 121.6553 | -120.5063 | 1.0483 | 0.0096895 | -0.001914 | 0.0007135 | 0.094278 | -0.026716 | -0.031277 | 0.013988 | 0.07782 | 0.064087 | -0.027466 | 0.16479 | 0.737 | 0.14648 | -0.041199 | 0.27008 | 1.0803 | -120.8633 | 120.4788 | -0.98419 | 120.5841 | 120.6711 | -0.31128 | -0.35706 | 0.032043 | 0.10529 | 120.4651 | 120.7764 | 121.2433 | 120.5704 | 120.5841 | 121.5866 | 120.6528 | -0.35706 | 120.5704 | 120.5841 | 120.6528 | 121.2433 | 121.5866 | -1.0757 | -121.9116
3742.3906 | 121.6187 | -120.3094 | 1.2405 | -0.0055695 | -0.001914 | 0.0028497 | 0.098978 | -0.023511 | -0.032345 | 0.011424 | 0.018311 | 0.073242 | -0.073242 | 0.13275 | 0.84228 | 0.10529 | -0.004578 | 0.19684 | 1.3092 | -120.6299 | 120.2362 | -1.1673 | 120.3278 | 120.4422 | -0.39826 | -0.32044 | 0.068664 | 0.091553 | 120.3049 | 120.5063 | 121.1517 | 120.3827 | 120.3278 | 121.6187 | 120.4147 | -0.32044 | 120.3827 | 120.3278 | 120.4147 | 121.1517 | 121.6187 | -1.3138 | -121.8704
3744.1875 | 121.6141 | -120.2545 | 1.3367 | 0.0096895 | -0.001914 | 0.0096857 | 0.09791 | -0.023725 | -0.035549 | 0.014629 | 0.045776 | 0.064087 | -0.036621 | 0.14648 | 0.80109 | 0.13275 | -0.041199 | 0.21057 | 1.4008 | -120.5246 | 120.2179 | -1.2726 | 120.3003 | 120.401 | -0.53558 | -0.27008 | 0.064087 | 0.082397 | 120.2133 | 120.4651 | 121.0556 | 120.3186 | 120.3003 | 121.6553 | 120.3873 | -0.27008 | 120.3186 | 120.3003 | 120.3873 | 121.0556 | 121.6553 | -1.3733 | -121.8613
3745.9844 | 121.7148 | -120.2454 | 1.3412 | 0.017319 | -0.003623 | 0.0077631 | 0.093851 | -0.023725 | -0.030636 | 0.014202 | 0.091553 | 0.036621 | 0.004578 | 0.17395 | 0.8606 | 0.19684 | -0.17395 | 0.27466 | 1.3596 | -120.5063 | 120.2499 | -1.3046 | 120.3369 | 120.4193 | -0.48065 | -0.26093 | 0.01831 | 0.086975 | 120.0714 | 120.52 | 121.106 | 120.282 | 120.3369 | 121.6049 | 120.4422 | -0.26093 | 120.282 | 120.3369 | 120.4422 | 121.106 | 121.6049 | -1.3367 | -121.8475
3747.7656 | 121.6644 | -120.1447 | 1.4557 | 0.00206 | -0.002555 | 0.0056269 | 0.097055 | -0.025648 | -0.035122 | 0.014415 | -0.004578 | 0.082397 | -0.045776 | 0.086975 | 0.84228 | 0.068665 | 0.045776 | 0.16022 | 1.5106 | -120.4514 | 120.0989 | -1.3733 | 120.1401 | 120.2316 | -0.6134 | -0.3067 | 0.054932 | 0.041198 | 120.1904 | 120.3049 | 120.9869 | 120.2271 | 120.1401 | 121.6553 | 120.2133 | -0.3067 | 120.2271 | 120.1401 | 120.2133 | 120.9869 | 121.6553 | -1.5015 | -121.907
3749.5625 | 121.6873 | -120.0577 | 1.4877 | 0.017319 | 0.0012902 | 0.0066949 | 0.096842 | -0.024366 | -0.032131 | 0.015483 | 0.013733 | 0.082397 | -0.032043 | 0.09613 | 0.87891 | 0.068665 | -0.009155 | 0.16022 | 1.5747 | -120.3918 | 120.0256 | -1.4053 | 120.0714 | 120.1538 | -0.60883 | -0.33417 | 0.086975 | 0.045776 | 120.0485 | 120.2179 | 120.9366 | 120.1401 | 120.0714 | 121.6324 | 120.1263 | -0.33417 | 120.1401 | 120.0714 | 120.1263 | 120.9366 | 121.6324 | -1.5198 | -121.8796
3751.3438 | 121.6553 | -119.9478 | 1.6388 | 0.00206 | -0.001914 | 0.0024225 | 0.095346 | -0.023939 | -0.033199 | 0.015697 | 0.045776 | 0.073242 | -0.036621 | 0.1236 | 0.99335 | 0.10529 | -0.004578 | 0.20599 | 1.712 | -120.2454 | 119.9112 | -1.5656 | 119.9936 | 120.0714 | -0.64545 | -0.29755 | 0.073242 | 0.082397 | 119.9432 | 120.1538 | 120.9412 | 120.0211 | 119.9936 | 121.6599 | 120.0531 | -0.29755 | 120.0211 | 119.9936 | 120.0531 | 120.9412 | 121.6599 | -1.6754 | -121.8842
3753.0781 | 121.7148 | -120.0531 | 1.5381 | 0.017319 | -0.0014868 | 0.0049859 | 0.095987 | -0.02458 | -0.032985 | 0.014202 | -0.004578 | 0.091553 | -0.050354 | 0.07782 | 0.88348 | 0.064087 | 0.059509 | 0.18768 | 1.6205 | -120.3598 | 120.0027 | -1.4465 | 120.0485 | 120.1309 | -0.6546 | -0.3067 | 0.082397 | 0.045776 | 120.1126 | 120.2408 | 120.9366 | 120.1447 | 120.0485 | 121.6736 | 120.1172 | -0.3067 | 120.1447 | 120.0485 | 120.1172 | 120.9366 | 121.6736 | -1.5884 | -121.8979
3754.8438 | 121.7697 | -120.0623 | 1.4969 | 0.017319 | -0.00063242 | 0.0047723 | 0.096842 | -0.021589 | -0.035122 | 0.016765 | -0.022888 | 0.073242 | -0.032043 | 0.059509 | 0.79651 | 0.059509 | -0.004578 | 0.1236 | 1.5839 | -120.3873 | 120.0302 | -1.4236 | 120.0394 | 120.1218 | -0.70038 | -0.32501 | 0.086975 | 0.009155 | 120.0577 | 120.1859 | 120.8588 | 120.1355 | 120.0394 | 121.6461 | 120.1218 | -0.32501 | 120.1355 | 120.0394 | 120.1218 | 120.8588 | 121.6461 | -1.5289 | -121.8842
3756.6562 | 121.7926 | -120.1126 | 1.4465 | 0.017319 | -0.0029822 | 0.0064813 | 0.091074 | -0.028211 | -0.030422 | 0.015056 | 0.054932 | 0.050354 | -0.022888 | 0.14191 | 0.82855 | 0.14648 | -0.09613 | 0.22888 | 1.5015 | -120.4697 | 120.0897 | -1.3962 | 120.1675 | 120.2545 | -0.61798 | -0.35706 | 0.054932 | 0.07782 | 120.0165 | 120.3415 | 120.9412 | 120.163 | 120.1675 | 121.6141 | 120.2591 | -0.35706 | 120.163 | 120.1675 | 120.2591 | 120.9412 | 121.6141 | -1.4694 | -121.9162
3758.4531 | 121.8018 | -120.1401 | 1.4008 | -0.0055695 | 8.578e-06 | -0.0020637 | 0.09791 | -0.025434 | -0.03384 | 0.014842 | -0.022888 | 0.068665 | -0.059509 | 0.07782 | 0.72784 | 0.073242 | -0.018311 | 0.1236 | 1.4603 | -120.52 | 120.0806 | -1.3321 | 120.1172 | 120.2179 | -0.67291 | -0.37994 | 0.059509 | 0.036621 | 120.1218 | 120.2637 | 120.8679 | 120.2087 | 120.1172 | 121.6003 | 120.2133 | -0.37994 | 120.2087 | 120.1172 | 120.2133 | 120.8679 | 121.6003 | -1.4603 | -121.9208
3760.2031 | 121.669 | -120.2316 | 1.3916 | 0.00206 | -0.0023412 | 0.0056269 | 0.094919 | -0.024793 | -0.031704 | 0.015483 | 0.09613 | 0.027466 | -0.041199 | 0.20599 | 0.85144 | 0.19226 | -0.10529 | 0.3067 | 1.4191 | -120.5383 | 120.1904 | -1.3641 | 120.3278 | 120.4376 | -0.54016 | -0.3067 | 0.027465 | 0.13733 | 120.1263 | 120.5383 | 121.0831 | 120.2591 | 120.3278 | 121.6507 | 120.4239 | -0.3067 | 120.2591 | 120.3278 | 120.4239 | 121.0831 | 121.6507 | -1.4328 | -121.9299
3762 | 121.7285 | -120.2957 | 1.3412 | 0.00206 | -0.00084602 | 0.0028497 | 0.095774 | -0.025648 | -0.034481 | 0.015911 | 0.073242 | 0.054932 | -0.045776 | 0.16937 | 0.78278 | 0.13733 | -0.027466 | 0.25177 | 1.3824 | -120.5933 | 120.2499 | -1.2863 | 120.369 | 120.4651 | -0.55847 | -0.29755 | 0.041198 | 0.11902 | 120.2682 | 120.5475 | 121.0785 | 120.3506 | 120.369 | 121.6782 | 120.433 | -0.29755 | 120.3506 | 120.369 | 120.433 | 121.0785 | 121.6782 | -1.387 | -121.9345
3763.7812 | 121.8063 | -120.3049 | 1.2543 | 0.00206 | -0.00020502 | 0.010754 | 0.10133 | -0.02522 | -0.032131 | 0.017833 | 0.004578 | 0.064087 | -0.09613 | 0.086975 | 0.68207 | 0.091553 | -0.082397 | 0.17395 | 1.3367 | -120.6482 | 120.2087 | -1.1902 | 120.3094 | 120.3918 | -0.5722 | -0.34332 | 0.082398 | 0.10071 | 120.2225 | 120.4788 | 120.9869 | 120.369 | 120.3094 | 121.6415 | 120.3964 | -0.34332 | 120.369 | 120.3094 | 120.3964 | 120.9869 | 121.6415 | -1.3504 | -121.9025
3765.5156 | 121.7468 | -120.3506 | 1.2726 | 0.0096895 | -0.0034094 | 0.0041315 | 0.095987 | -0.026502 | -0.031277 | 0.016979 | 0.013733 | 0.082397 | -0.07782 | 0.091553 | 0.67749 | 0.086975 | 0.027466 | 0.19226 | 1.3504 | -120.6619 | 120.2728 | -1.1902 | 120.3644 | 120.4422 | -0.59509 | -0.31128 | 0.07782 | 0.091553 | 120.3781 | 120.5429 | 121.0281 | 120.433 | 120.3644 | 121.701 | 120.4376 | -0.31128 | 120.433 | 120.3644 | 120.4376 | 121.0281 | 121.701 | -1.3504 | -121.9345
3768.625 | 121.8201 | -120.3827 | 1.2131 | 0.0096895 | -0.0057592 | 0.0041315 | 0.096414 | -0.027357 | -0.030636 | 0.016765 | 0.073242 | 0.027466 | -0.059509 | 0.16479 | 0.69122 | 0.17395 | -0.15564 | 0.26093 | 1.2634 | -120.6802 | 120.3232 | -1.1856 | 120.4559 | 120.5475 | -0.52185 | -0.29755 | 0.050354 | 0.13275 | 120.227 | 120.6436 | 121.0739 | 120.4102 | 120.4559 | 121.6461 | 120.5566 | -0.29755 | 120.4102 | 120.4559 | 120.5566 | 121.0739 | 121.6461 | -1.2726 | -121.8933
3772.7188 | 121.6873 | -118.7576 | 2.8976 | 0.017319 | 0.00064938 | 0.0096857 | 0.33674 | -0.024152 | -0.034267 | 0.25431 | 0.041199 | 0.09613 | -0.11902 | 0.14191 | 0.1236 | 0.1236 | -0.004578 | 0.22888 | 3.0441 | -118.9545 | 118.6386 | -2.8015 | 118.7988 | 118.8995 | -2.774 | -0.19684 | 0.14648 | 0.16022 | 118.7531 | 118.9865 | 118.8812 | 118.8538 | 118.7988 | 121.8018 | 118.8812 | -0.19684 | 118.8538 | 118.7988 | 118.8812 | 118.8812 | 121.8018 | -3.0167 | -121.8521
3778.875 | 121.8155 | -118.1305 | 3.4058 | 0.017319 | -0.0055456 | 0.0015679 | 0.43287 | -0.023511 | -0.029781 | 0.36027 | 0.073242 | 0.027466 | -0.091553 | 0.17395 | 0.59052 | 0.16937 | -0.16022 | 0.27008 | 3.4195 | -118.4189 | 118.0389 | -3.3783 | 118.2037 | 118.3044 | -2.8152 | -0.28839 | 0.013733 | 0.16479 | 117.9703 | 118.4006 | 118.721 | 118.158 | 118.2037 | 121.55 | 118.2999 | -0.28839 | 118.158 | 118.2037 | 118.2999 | 118.721 | 121.55 | -3.4973 | -121.8246
3780.8281 | 121.6782 | -118.6066 | 3.0533 | 0.0096895 | -0.0017004 | 0.0079767 | 0.5666 | -0.024793 | -0.032345 | 0.48866 | 0.036621 | 0.073242 | -0.17853 | 0.15564 | -2.8244 | 0.11902 | -0.032043 | 0.21973 | 3.0167 | -118.8629 | 118.428 | -2.98 | 118.6432 | 118.7622 | -5.8777 | -0.25635 | -0.036621 | 0.21515 | 118.5745 | 118.8263 | 115.7822 | 118.6798 | 118.6432 | 121.6232 | 118.7256 | -0.25635 | 118.6798 | 118.6432 | 118.7256 | 115.7822 | 121.6232 | -3.2318 | -121.9162
3782.6562 | 121.6873 | -119.2474 | 2.3529 | 0.024948 | -0.0014868 | 0.0084039 | 0.64051 | -0.02458 | -0.030422 | 0.55894 | 0.054932 | 0.045776 | -0.14191 | 0.15564 | -2.9984 | 0.12817 | -0.054932 | 0.20599 | 2.3346 | -119.5404 | 119.1055 | -2.3071 | 119.3024 | 119.4031 | -5.3513 | -0.29297 | -0.01831 | 0.19684 | 119.1925 | 119.4534 | 116.2491 | 119.2932 | 119.3024 | 121.582 | 119.3756 | -0.29297 | 119.2932 | 119.3024 | 119.3756 | 116.2491 | 121.582 | -2.4948 | -121.8933
3784.4531 | 121.7651 | -118.7256 | 2.8061 | 0.00206 | -0.00084602 | 0.0064813 | 1.2523 | -0.024366 | -0.02914 | 1.1838 | 0.032043 | 0.041199 | -0.10529 | 0.13733 | -2.8244 | 0.15564 | -0.09613 | 0.24719 | 2.7695 | -118.9499 | 118.6203 | -2.7649 | 118.7576 | 118.8629 | -5.6305 | -0.2243 | -0.036621 | 0.13733 | 118.6295 | 118.9728 | 115.9012 | 118.7668 | 118.7576 | 121.4951 | 118.8812 | -0.2243 | 118.7668 | 118.7576 | 118.8812 | 115.9012 | 121.4951 | -2.9114 | -121.756
3786.1875 | 121.6507 | -119.8883 | 1.7715 | 0.0096895 | -0.0012732 | 0.0043451 | 0.44612 | -0.025434 | -0.033626 | 0.36924 | -0.013733 | 0.07782 | -0.13733 | 0.10986 | -0.036621 | 0.073242 | 0.036621 | 0.18768 | 1.8082 | -120.1538 | 119.751 | -1.6937 | 119.8746 | 119.9982 | -1.8082 | -0.2655 | 0.036622 | 0.1236 | 119.9249 | 120.076 | 119.8517 | 119.9661 | 119.8746 | 121.6965 | 119.9615 | -0.2655 | 119.9661 | 119.8746 | 119.9615 | 119.8517 | 121.6965 | -1.9089 | -121.9254
3787.9688 | 121.7377 | -120.282 | 1.3596 | 0.0096895 | -0.0038366 | 0.0039179 | 0.28868 | -0.025648 | -0.035763 | 0.20774 | 0.018311 | 0.068665 | -0.10529 | 0.11902 | 0.35706 | 0.09613 | 0 | 0.21515 | 1.3824 | -120.5887 | 120.1767 | -1.2909 | 120.3003 | 120.401 | -1.0025 | -0.3067 | 0.022888 | 0.1236 | 120.282 | 120.4971 | 120.639 | 120.3506 | 120.3003 | 121.6644 | 120.3781 | -0.3067 | 120.3506 | 120.3003 | 120.3781 | 120.639 | 121.6644 | -1.4648 | -121.9482
3789.7656 | 121.8475 | -120.6757 | 0.93842 | 0.0096895 | -0.0029822 | 0.0079767 | 0.14875 | -0.027357 | -0.03149 | 0.065685 | 0.059509 | 0.050354 | -0.073242 | 0.14648 | 0.68207 | 0.15564 | -0.13275 | 0.24261 | 0.98419 | -121.0144 | 120.6024 | -0.88806 | 120.7352 | 120.8221 | -0.25635 | -0.33875 | 0.045776 | 0.13275 | 120.5429 | 120.9183 | 121.3577 | 120.726 | 120.7352 | 121.6599 | 120.8313 | -0.33875 | 120.726 | 120.7352 | 120.8313 | 121.3577 | 121.6599 | -1.0117 | -121.9528
3791.5 | 121.7834 | -120.3964 | 1.2451 | 0.0096895 | -0.00041862 | 0.0084039 | 0.19981 | -0.023939 | -0.034481 | 0.11012 | 0.004578 | 0.07782 | -0.1236 | 0.09613 | 0.71411 | 0.064087 | -0.004578 | 0.13733 | 1.3092 | -120.7443 | 120.2728 | -1.1673 | 120.401 | 120.4926 | -0.53101 | -0.3479 | 0.064087 | 0.12817 | 120.3918 | 120.5338 | 121.1105 | 120.4742 | 120.401 | 121.7056 | 120.4605 | -0.3479 | 120.4742 | 120.401 | 120.4605 | 121.1105 | 121.7056 | -1.3687 | -121.9894
3793.2344 | 121.7331 | -119.4443 | 2.2018 | 0.00206 | -0.0014868 | 0.0019953 | 0.58241 | -0.024793 | -0.032131 | 0.50404 | 0.064087 | 0.045776 | -0.10986 | 0.14191 | -0.17395 | 0.12817 | -0.009155 | 0.22888 | 2.2247 | -119.7006 | 119.3344 | -2.1561 | 119.5084 | 119.5862 | -2.3758 | -0.25635 | 0.022888 | 0.17395 | 119.4351 | 119.6732 | 119.2703 | 119.4901 | 119.5084 | 121.669 | 119.5724 | -0.25635 | 119.4901 | 119.5084 | 119.5724 | 119.2703 | 121.669 | -2.3117 | -121.9025
3794.9688 | 121.8063 | -118.9224 | 2.6276 | 0.00206 | 0.0017176 | 0.011395 | 0.80885 | -0.023511 | -0.030849 | 0.72578 | -0.004578 | 0.073242 | -0.1236 | 0.068665 | -0.66376 | 0.064087 | -0.004578 | 0.12817 | 2.655 | -119.2383 | 118.7988 | -2.5543 | 118.9178 | 118.9911 | -3.2913 | -0.31586 | 0.027466 | 0.11902 | 118.9178 | 119.0506 | 118.2587 | 118.9957 | 118.9178 | 121.5775 | 118.9865 | -0.31586 | 118.9957 | 118.9178 | 118.9865 | 118.2587 | 121.5775 | -2.7512 | -121.8658
3796.75 | 121.6278 | -118.5471 | 3.0762 | 0.017319 | -0.001914 | 0.0045587 | 0.85478 | -0.023298 | -0.03384 | 0.80268 | 0.050354 | 0.050354 | -0.11902 | 0.14648 | -0.28839 | 0.11902 | -0.050354 | 0.2243 | 3.0579 | -118.7622 | 118.428 | -3.0258 | 118.5974 | 118.6935 | -3.3646 | -0.21515 | -0.018311 | 0.16937 | 118.4967 | 118.7714 | 118.2587 | 118.5974 | 118.5974 | 121.6049 | 118.6661 | -0.21515 | 118.5974 | 118.5974 | 118.6661 | 118.2587 | 121.6049 | -3.1952 | -121.8384
3798.4844 | 121.6873 | -117.4988 | 4.0146 | 0.00206 | -0.00084602 | 0.0024225 | 1.4578 | -0.025434 | -0.029781 | 1.3961 | 0.064087 | 0.032043 | -0.10986 | 0.21973 | -0.39368 | 0.21057 | -0.13275 | 0.31586 | 3.9276 | -117.7231 | 117.3889 | -3.9825 | 117.5629 | 117.7185 | -4.4083 | -0.2243 | -0.086975 | 0.17395 | 117.366 | 117.8146 | 117.1051 | 117.5308 | 117.5629 | 121.4264 | 117.7094 | -0.2243 | 117.5308 | 117.5629 | 117.7094 | 117.1051 | 121.4264 | -4.1244 | -121.7377
3800.2344 | 121.8338 | -118.7119 | 2.861 | 0.017319 | 0.001504 | 0.0034905 | 0.49803 | -0.027143 | -0.024441 | 0.42884 | 0.059509 | 0.032043 | -1.3 | 0.16022 | -9.5947 | 0.16022 | -0.12817 | 0.24261 | 2.5772 | -119.2612 | 117.4118 | -2.829 | 118.7714 | 118.8721 | -12.4558 | -0.54932 | -0.28381 | 1.3596 | 118.5837 | 118.9545 | 109.1171 | 118.7439 | 118.7714 | 121.2891 | 118.8721 | -0.54932 | 118.7439 | 118.7714 | 118.8721 | 109.1171 | 121.2891 | -4.1611 | -122.1222
3801.9688 | 121.6782 | -119.3481 | 2.1744 | 0.017319 | -0.004264 | 0.0039179 | 1.1427 | -0.026502 | -0.031063 | 1.0011 | 0.09613 | 0.018311 | -0.26093 | 0.21057 | -2.536 | 0.2243 | -0.15564 | 0.32959 | 2.3575 | -119.3665 | 119.0872 | -2.1561 | 119.4443 | 119.5587 | -4.7104 | -0.01831 | 0.18311 | 0.35706 | 119.1925 | 119.6777 | 116.8121 | 119.3665 | 119.4443 | 121.7056 | 119.5724 | -0.01831 | 119.3665 | 119.4443 | 119.5724 | 116.8121 | 121.7056 | -2.4353 | -121.5408
3803.7656 | 121.8063 | -118.9224 | 2.5406 | 0.017319 | -0.00041862 | 0.0075495 | 0.60056 | -0.023511 | -0.035763 | 0.55168 | 0 | 0.07782 | -0.086975 | 0.10071 | 1.1673 | 0.10986 | -0.073242 | 0.17395 | 2.6138 | -119.2154 | 118.8354 | -2.4628 | 118.9224 | 119.0231 | -1.3733 | -0.29297 | 0.073243 | 0.086975 | 118.8492 | 119.0964 | 120.0897 | 119.0002 | 118.9224 | 121.5363 | 119.0323 | -0.29297 | 119.0002 | 118.9224 | 119.0323 | 120.0897 | 121.5363 | -2.6276 | -121.756
3805.5625 | 121.7606 | -121.312 | 0.3891 | 0.0096895 | -0.0010596 | 0.0043451 | 0.10603 | -0.024366 | -0.032345 | 0.021892 | 0.11444 | 0.054932 | -0.064087 | 0.18768 | 0.32959 | 0.1831 | -0.09613 | 0.31128 | 0.41657 | -121.6095 | 121.2479 | -0.33417 | 121.4264 | 121.4996 | -0.059509 | -0.29755 | 0.027466 | 0.17853 | 121.2158 | 121.6232 | 121.6415 | 121.3669 | 121.4264 | 121.7285 | 121.4951 | -0.29755 | 121.3669 | 121.4264 | 121.4951 | 121.6415 | 121.7285 | -0.45319 | -121.9986
3807.3594 | 121.8018 | -121.2891 | 0.3891 | 0.0096895 | -0.003623 | -0.0020637 | 0.10966 | -0.026929 | -0.033626 | 0.022106 | -0.018311 | 0.07782 | -0.12817 | 0.091553 | 0.22888 | 0.064087 | 0.032043 | 0.16937 | 0.45319 | -121.6049 | 121.1609 | -0.31128 | 121.2708 | 121.3806 | -0.16022 | -0.31586 | 0.064087 | 0.10986 | 121.3211 | 121.4584 | 121.5179 | 121.3669 | 121.2708 | 121.7422 | 121.3531 | -0.31586 | 121.3669 | 121.2708 | 121.3531 | 121.5179 | 121.7422 | -0.51727 | -121.994
3809.1719 | 121.8109 | -121.2936 | 0.39368 | 0.017319 | -0.004264 | 0.0034905 | 0.10517 | -0.025434 | -0.031704 | 0.019969 | 0 | 0.068665 | -0.10986 | 0.09613 | 0.24261 | 0.082397 | 0.036621 | 0.17853 | 0.48065 | -121.6461 | 121.1838 | -0.32501 | 121.2936 | 121.3898 | -0.15106 | -0.35248 | 0.086975 | 0.10986 | 121.3303 | 121.4722 | 121.5363 | 121.3623 | 121.2936 | 121.7743 | 121.376 | -0.35248 | 121.3623 | 121.2936 | 121.376 | 121.5363 | 121.7743 | -0.50354 | -122.0398
3810.9688 | 121.8796 | -121.2753 | 0.3479 | 0.0096895 | 0.0012902 | 0.0069085 | 0.11009 | -0.025648 | -0.030208 | 0.02061 | 0.022888 | 0.068665 | -0.10529 | 0.10986 | 0.25177 | 0.10529 | -0.091553 | 0.16479 | 0.44861 | -121.6049 | 121.17 | -0.27924 | 121.2982 | 121.3852 | -0.09613 | -0.32959 | 0.10071 | 0.12817 | 121.1838 | 121.4401 | 121.5271 | 121.344 | 121.2982 | 121.7239 | 121.3806 | -0.32959 | 121.344 | 121.2982 | 121.3806 | 121.5271 | 121.7239 | -0.45319 | -121.9528
3812.75 | 121.8887 | -121.2753 | 0.37079 | 0.017319 | -0.0017004 | 0.0047723 | 0.10859 | -0.027143 | -0.032772 | 0.020824 | -0.009155 | 0.082397 | -0.13275 | 0.068665 | 0.21515 | 0.050354 | 0.022888 | 0.12817 | 0.48065 | -121.6415 | 121.1426 | -0.28839 | 121.2662 | 121.344 | -0.15564 | -0.36621 | 0.10986 | 0.1236 | 121.2982 | 121.4035 | 121.4905 | 121.3577 | 121.2662 | 121.756 | 121.3257 | -0.36621 | 121.3577 | 121.2662 | 121.3257 | 121.4905 | 121.756 | -0.50354 | -122.0123
3814.5469 | 121.8613 | -121.2845 | 0.40741 | 0.024948 | -0.00063242 | 0.0039179 | 0.10624 | -0.021589 | -0.029354 | 0.019756 | 0.11902 | 0.036621 | -0.068665 | 0.20599 | 0.36621 | 0.21057 | -0.20599 | 0.28839 | 0.44861 | -121.582 | 121.2158 | -0.37079 | 121.4035 | 121.4905 | -0.041199 | -0.29755 | 0.041198 | 0.18768 | 121.0785 | 121.5729 | 121.6507 | 121.3211 | 121.4035 | 121.7331 | 121.4951 | -0.29755 | 121.3211 | 121.4035 | 121.4951 | 121.6507 | 121.7331 | -0.47608 | -121.9894
3816.2812 | 121.9208 | -121.2936 | 0.37994 | 0.00206 | -0.00041862 | 0.0073359 | 0.10368 | -0.026502 | -0.034267 | 0.017406 | 0.050354 | 0.064087 | -0.091553 | 0.13275 | 0.33417 | 0.16022 | -0.11902 | 0.22888 | 0.46692 | -121.6141 | 121.2021 | -0.31586 | 121.344 | 121.4264 | -0.045777 | -0.32044 | 0.086975 | 0.14191 | 121.1746 | 121.5225 | 121.6278 | 121.3577 | 121.344 | 121.7606 | 121.4539 | -0.32044 | 121.3577 | 121.344 | 121.4539 | 121.6278 | 121.7606 | -0.4715 | -121.994
3818.0156 | 121.875 | -121.2982 | 0.41657 | 0.00206 | -0.0031958 | 0.0077631 | 0.10731 | -0.023725 | -0.032131 | 0.019969 | 0.091553 | 0.027466 | -0.054932 | 0.21057 | 0.36163 | 0.20599 | -0.20142 | 0.28839 | 0.46234 | -121.5591 | 121.2433 | -0.3891 | 121.3898 | 121.5088 | -0.054932 | -0.26093 | 0.045776 | 0.14649 | 121.0968 | 121.5866 | 121.6599 | 121.3257 | 121.3898 | 121.7606 | 121.5042 | -0.26093 | 121.3257 | 121.3898 | 121.5042 | 121.6599 | 121.7606 | -0.4715 | -121.9757
3819.75 | 121.9025 | -121.2708 | 0.40283 | 0.0096895 | 0.0017176 | 0.0069085 | 0.10859 | -0.025861 | -0.033413 | 0.022533 | 0.036621 | 0.073242 | -0.10529 | 0.12817 | 0.29297 | 0.10986 | -0.09613 | 0.17395 | 0.49896 | -121.6141 | 121.1655 | -0.32959 | 121.3074 | 121.3989 | -0.10986 | -0.34332 | 0.09613 | 0.14191 | 121.1746 | 121.4447 | 121.5637 | 121.344 | 121.3074 | 121.7697 | 121.3806 | -0.34332 | 121.344 | 121.3074 | 121.3806 | 121.5637 | 121.7697 | -0.50812 | -122.0169
3821.4844 | 121.7102 | -118.1259 | 3.5431 | 0.0096895 | -0.0010596 | 0.0075495 | 1.2295 | -0.02223 | -0.030636 | 1.1364 | 0.022888 | 0.064087 | -0.17395 | 0.15564 | -1.0483 | 0.10529 | -0.013733 | 0.2243 | 3.6575 | -118.2083 | 117.952 | -3.479 | 118.1488 | 118.2816 | -4.5914 | -0.082397 | 0.11444 | 0.19684 | 118.1122 | 118.3502 | 117.0776 | 118.19 | 118.1488 | 121.7834 | 118.2312 | -0.082397 | 118.19 | 118.1488 | 118.2312 | 117.0776 | 121.7834 | -3.717 | -121.7514
3823.2812 | 121.788 | -118.0573 | 3.598 | 0.0096895 | -0.0027686 | 0.0064813 | 0.95069 | -0.02522 | -0.028499 | 0.87532 | 0.068665 | 0.018311 | -0.082397 | 0.21973 | 1.8402 | 0.21057 | -0.15564 | 0.32501 | 3.5843 | -118.2678 | 117.9749 | -3.5797 | 118.1259 | 118.277 | -1.7578 | -0.21057 | -0.013732 | 0.15106 | 117.9016 | 118.3823 | 119.8975 | 118.0756 | 118.1259 | 121.6415 | 118.2678 | -0.21057 | 118.0756 | 118.1259 | 118.2678 | 119.8975 | 121.6415 | -3.6804 | -121.8658
3825 | 121.7926 | -121.3989 | 0.28839 | 0.0096895 | 0.001504 | 0.0056269 | 0.11329 | -0.025861 | -0.03149 | 0.021038 | 0.013733 | 0.09613 | -0.11902 | 0.10986 | 0.16937 | 0.07782 | 0.036621 | 0.18768 | 0.3479 | -121.7697 | 121.2799 | -0.19226 | 121.4127 | 121.5088 | -0.11902 | -0.37079 | 0.059509 | 0.13275 | 121.4355 | 121.5866 | 121.5683 | 121.4951 | 121.4127 | 121.7468 | 121.4767 | -0.37079 | 121.4951 | 121.4127 | 121.4767 | 121.5683 | 121.7468 | -0.40741 | -122.0581
3826.7812 | 121.7834 | -121.4401 | 0.31128 | 0.0096895 | -0.00020502 | 0.0081903 | 0.11094 | -0.023939 | -0.034267 | 0.020824 | 0.054932 | 0.073242 | -0.13275 | 0.14648 | 0.20142 | 0.11444 | -0.027466 | 0.2243 | 0.37537 | -121.7285 | 121.3074 | -0.23804 | 121.4951 | 121.5866 | -0.10986 | -0.28839 | 0.064087 | 0.18768 | 121.4127 | 121.6644 | 121.6415 | 121.5134 | 121.4951 | 121.8155 | 121.5546 | -0.28839 | 121.5134 | 121.4951 | 121.5546 | 121.6415 | 121.8155 | -0.44403 | -122.0398
3828.5781 | 121.8842 | -121.4035 | 0.25635 | 0.0096895 | -0.0014868 | 0.0045587 | 0.1088 | -0.024793 | -0.029995 | 0.023815 | 0.013733 | 0.050354 | -0.10529 | 0.12817 | 0.19684 | 0.1236 | -0.11444 | 0.20599 | 0.33875 | -121.7743 | 121.2982 | -0.20599 | 121.4172 | 121.5317 | -0.05951 | -0.37079 | 0.082397 | 0.11902 | 121.2891 | 121.6095 | 121.6003 | 121.4539 | 121.4172 | 121.7422 | 121.5271 | -0.37079 | 121.4539 | 121.4172 | 121.5271 | 121.6003 | 121.7422 | -0.36163 | -122.0306
3830.375 | 121.843 | -121.4584 | 0.31128 | 0.0096895 | -0.0034094 | 0.0045587 | 0.10304 | -0.02458 | -0.03384 | 0.020824 | 0.064087 | 0.059509 | -0.10071 | 0.15564 | 0.21057 | 0.14191 | -0.013733 | 0.24719 | 0.32959 | -121.7651 | 121.3577 | -0.25177 | 121.5225 | 121.6141 | -0.10071 | -0.3067 | 0.018311 | 0.1648 | 121.4447 | 121.7056 | 121.669 | 121.5179 | 121.5225 | 121.788 | 121.6003 | -0.3067 | 121.5179 | 121.5225 | 121.6003 | 121.669 | 121.788 | -0.41199 | -122.0764
3832.1094 | 121.9391 | -121.4355 | 0.2655 | 0.00206 | -0.0021276 | 0.0049859 | 0.11201 | -0.026289 | -0.033413 | 0.022747 | -0.009155 | 0.064087 | -0.11902 | 0.082397 | 0.13275 | 0.059509 | 0.009155 | 0.13275 | 0.33417 | -121.7972 | 121.3165 | -0.20142 | 121.4264 | 121.5179 | -0.13275 | -0.36163 | 0.068664 | 0.10986 | 121.4447 | 121.5683 | 121.5683 | 121.4996 | 121.4264 | 121.7697 | 121.4951 | -0.36163 | 121.4996 | 121.4264 | 121.4951 | 121.5683 | 121.7697 | -0.38452 | -122.0627
3833.8906 | 121.9528 | -121.4447 | 0.25635 | 0.00206 | 0.00043578 | 0.0071221 | 0.10539 | -0.025434 | -0.031063 | 0.02061 | 0.045776 | 0.045776 | -0.07782 | 0.13733 | 0.2243 | 0.16479 | -0.11444 | 0.24261 | 0.3067 | -121.8063 | 121.3669 | -0.21057 | 121.4905 | 121.582 | -0.032044 | -0.36163 | 0.050354 | 0.1236 | 121.3303 | 121.6873 | 121.669 | 121.4905 | 121.4905 | 121.7514 | 121.6095 | -0.36163 | 121.4905 | 121.4905 | 121.6095 | 121.669 | 121.7514 | -0.33417 | -122.0627
3835.6406 | 121.9528 | -121.4493 | 0.25635 | -0.0055695 | 0.00064938 | 0.0051995 | 0.11286 | -0.024152 | -0.031917 | 0.023815 | -0.018311 | 0.07782 | -0.10986 | 0.073242 | 0.11902 | 0.068665 | -0.018311 | 0.13275 | 0.35248 | -121.788 | 121.3394 | -0.17853 | 121.431 | 121.5225 | -0.13733 | -0.33875 | 0.09613 | 0.091552 | 121.431 | 121.582 | 121.5683 | 121.5271 | 121.431 | 121.8018 | 121.5179 | -0.33875 | 121.5271 | 121.431 | 121.5179 | 121.5683 | 121.8018 | -0.36621 | -122.0444
3837.4375 | 121.8887 | -121.4859 | 0.28839 | 0.0096895 | 0.00064938 | 0.0086175 | 0.10902 | -0.025434 | -0.034908 | 0.021038 | -0.004578 | 0.086975 | -0.11902 | 0.07782 | 0.15106 | 0.059509 | 0.064087 | 0.16479 | 0.36163 | -121.8246 | 121.3669 | -0.20142 | 121.4813 | 121.5637 | -0.13733 | -0.33875 | 0.073242 | 0.11444 | 121.55 | 121.6507 | 121.637 | 121.5729 | 121.4813 | 121.8475 | 121.5454 | -0.33875 | 121.5729 | 121.4813 | 121.5454 | 121.637 | 121.8475 | -0.40741 | -122.113
3839.2344 | 121.9116 | -121.4722 | 0.25635 | 0.00206 | -0.00041862 | 0.0062677 | 0.11094 | -0.024793 | -0.032131 | 0.02296 | 0.10071 | 0.050354 | -0.086975 | 0.20599 | 0.21973 | 0.20599 | -0.1831 | 0.25635 | 0.32044 | -121.7651 | 121.3852 | -0.20599 | 121.5729 | 121.6782 | -0.036621 | -0.29297 | 0.064087 | 0.18768 | 121.2891 | 121.7285 | 121.6919 | 121.5225 | 121.5729 | 121.7926 | 121.6782 | -0.29297 | 121.5225 | 121.5729 | 121.6782 | 121.6919 | 121.7926 | -0.34332 | -122.0215
3841.0312 | 121.9437 | -121.4401 | 0.28381 | 0.00206 | -0.0010596 | 0.0049859 | 0.1024 | -0.026929 | -0.032772 | 0.021678 | 0.050354 | 0.064087 | -0.07782 | 0.15564 | 0.21515 | 0.16479 | -0.11902 | 0.26093 | 0.33417 | -121.788 | 121.3623 | -0.21973 | 121.4905 | 121.5958 | -0.068664 | -0.3479 | 0.050354 | 0.12817 | 121.3211 | 121.701 | 121.6553 | 121.5042 | 121.4905 | 121.7743 | 121.6049 | -0.3479 | 121.5042 | 121.4905 | 121.6049 | 121.6553 | 121.7743 | -0.36163 | -122.0718
3842.8125 | 121.9574 | -121.4035 | 0.31128 | 0.0096895 | 0.00022218 | 0.0049859 | 0.11436 | -0.022016 | -0.031917 | 0.021678 | 0 | 0.082397 | -0.11902 | 0.082397 | 0.13275 | 0.059509 | -0.018311 | 0.12817 | 0.41199 | -121.7468 | 121.2845 | -0.22888 | 121.4035 | 121.4859 | -0.17853 | -0.34332 | 0.10071 | 0.11902 | 121.3852 | 121.5317 | 121.5363 | 121.4859 | 121.4035 | 121.8155 | 121.463 | -0.34332 | 121.4859 | 121.4035 | 121.463 | 121.5363 | 121.8155 | -0.4303 | -122.0581
3844.5469 | 121.9299 | -121.4127 | 0.32501 | 0.0096895 | -0.0012732 | 0.0017817 | 0.11158 | -0.024152 | -0.032772 | 0.021251 | 0.004578 | 0.068665 | -0.10529 | 0.11444 | 0.20142 | 0.11902 | -0.10529 | 0.18768 | 0.40283 | -121.7148 | 121.3074 | -0.25635 | 121.4172 | 121.5271 | -0.1236 | -0.30212 | 0.07782 | 0.10986 | 121.3074 | 121.6003 | 121.6141 | 121.4813 | 121.4172 | 121.8155 | 121.5317 | -0.30212 | 121.4813 | 121.4172 | 121.5317 | 121.6141 | 121.8155 | -0.4303 | -122.0398
3846.3438 | 121.8521 | -121.4447 | 0.37994 | 0.024948 | -0.002555 | 0.0043451 | 0.1118 | -0.022871 | -0.035549 | 0.023174 | 0.07782 | 0.068665 | -0.11444 | 0.14648 | 0.21973 | 0.1236 | -0.050354 | 0.21515 | 0.41657 | -121.7514 | 121.3303 | -0.31128 | 121.5225 | 121.5912 | -0.16022 | -0.3067 | 0.036621 | 0.19226 | 121.3943 | 121.6599 | 121.6644 | 121.5134 | 121.5225 | 121.8613 | 121.5683 | -0.3067 | 121.5134 | 121.5225 | 121.5683 | 121.6644 | 121.8613 | -0.49439 | -122.1313
3848.1406 | 121.9803 | -121.3989 | 0.33417 | 0.017319 | -0.0017004 | 0.0037043 | 0.10603 | -0.025648 | -0.032345 | 0.02296 | 0.041199 | 0.050354 | -0.068665 | 0.13275 | 0.25177 | 0.16022 | -0.11902 | 0.24261 | 0.40283 | -121.756 | 121.3303 | -0.28381 | 121.4401 | 121.5317 | -0.082397 | -0.35706 | 0.068665 | 0.10986 | 121.2799 | 121.6415 | 121.6507 | 121.4493 | 121.4401 | 121.8018 | 121.5591 | -0.35706 | 121.4493 | 121.4401 | 121.5591 | 121.6507 | 121.8018 | -0.40283 | -122.0901
3849.9375 | 121.9528 | -121.4218 | 0.35706 | 0.00206 | -0.003623 | 0.0051995 | 0.11051 | -0.024366 | -0.032772 | 0.02296 | 0.091553 | 0.059509 | -0.091553 | 0.18768 | 0.27466 | 0.19684 | -0.1831 | 0.28381 | 0.39825 | -121.6873 | 121.3303 | -0.29755 | 121.5134 | 121.6095 | -0.082398 | -0.2655 | 0.041198 | 0.18311 | 121.2387 | 121.7056 | 121.6965 | 121.4813 | 121.5134 | 121.8201 | 121.6187 | -0.2655 | 121.4813 | 121.5134 | 121.6187 | 121.6965 | 121.8201 | -0.44861 | -122.0444
3851.6719 | 121.8613 | -121.4493 | 0.40741 | 0.017319 | -0.001914 | 0.0051995 | 0.10923 | -0.026716 | -0.032772 | 0.022319 | 0.10529 | 0.027466 | -0.082397 | 0.20599 | 0.31586 | 0.21057 | -0.11902 | 0.31128 | 0.41657 | -121.7102 | 121.3669 | -0.37994 | 121.5546 | 121.6553 | -0.091553 | -0.26093 | 0.009155 | 0.18768 | 121.3303 | 121.7606 | 121.7651 | 121.4767 | 121.5546 | 121.8658 | 121.6599 | -0.26093 | 121.4767 | 121.5546 | 121.6599 | 121.7651 | 121.8658 | -0.48981 | -122.1176
3853.4688 | 121.9757 | -121.3943 | 0.37079 | 0.017319 | -0.002555 | 0.0064813 | 0.10859 | -0.02757 | -0.030208 | 0.022533 | 0.09613 | 0.032043 | -0.068665 | 0.15564 | 0.26093 | 0.17395 | -0.14191 | 0.24261 | 0.41657 | -121.7285 | 121.3257 | -0.33875 | 121.4905 | 121.55 | -0.10986 | -0.33417 | 0.045776 | 0.16479 | 121.2524 | 121.637 | 121.6553 | 121.4264 | 121.4905 | 121.8109 | 121.5683 | -0.33417 | 121.4264 | 121.4905 | 121.5683 | 121.6553 | 121.8109 | -0.43945 | -122.0993
3855.2031 | 121.8613 | -121.4355 | 0.3891 | 0.0096895 | -0.0027686 | 0.0077631 | 0.11671 | -0.025434 | -0.034054 | 0.023601 | 0.041199 | 0.068665 | -0.12817 | 0.15564 | 0.2243 | 0.1236 | -0.036621 | 0.2243 | 0.45776 | -121.7422 | 121.3074 | -0.32043 | 121.4767 | 121.5912 | -0.16479 | -0.3067 | 0.068665 | 0.16937 | 121.3989 | 121.6599 | 121.6599 | 121.5042 | 121.4767 | 121.8933 | 121.5591 | -0.3067 | 121.5042 | 121.4767 | 121.5591 | 121.6599 | 121.8933 | -0.51727 | -122.1313
3857 | 121.9208 | -121.4447 | 0.3891 | 0.0096895 | 0.0010766 | 0.0026361 | 0.11799 | -0.025434 | -0.034481 | 0.025951 | -0.009155 | 0.07782 | -0.12817 | 0.10529 | 0.1831 | 0.068665 | 0.068665 | 0.18768 | 0.45319 | -121.8018 | 121.3165 | -0.31128 | 121.4355 | 121.55 | -0.20599 | -0.35706 | 0.064087 | 0.11902 | 121.5134 | 121.6324 | 121.6278 | 121.5225 | 121.4355 | 121.8979 | 121.5134 | -0.35706 | 121.5225 | 121.4355 | 121.5134 | 121.6278 | 121.8979 | -0.51727 | -122.1909
3858.7969 | 121.9345 | -121.4447 | 0.37079 | 0.00206 | -0.001914 | 0.0028497 | 0.10752 | -0.028211 | -0.03149 | 0.019969 | 0.07782 | 0.054932 | -0.082397 | 0.21515 | 0.32501 | 0.21973 | -0.13733 | 0.31128 | 0.41199 | -121.7239 | 121.3623 | -0.31586 | 121.5225 | 121.6599 | -0.045777 | -0.27924 | 0.041198 | 0.16022 | 121.3074 | 121.756 | 121.7697 | 121.4996 | 121.5225 | 121.8567 | 121.6644 | -0.27924 | 121.4996 | 121.5225 | 121.6644 | 121.7697 | 121.8567 | -0.45319 | -122.0947
3860.5625 | 121.9574 | -121.4401 | 0.39825 | 0.00206 | -0.0023412 | 0.0049859 | 0.11265 | -0.02522 | -0.030849 | 0.023601 | 0.11444 | 0.027466 | -0.068665 | 0.20142 | 0.30212 | 0.19684 | -0.18768 | 0.29297 | 0.41657 | -121.756 | 121.3715 | -0.37079 | 121.5546 | 121.6415 | -0.09613 | -0.31586 | 0.018311 | 0.18311 | 121.2524 | 121.7331 | 121.7422 | 121.4676 | 121.5546 | 121.8567 | 121.637 | -0.31586 | 121.4676 | 121.5546 | 121.637 | 121.7422 | 121.8567 | -0.46692 | -122.1542
3862.3594 | 121.9208 | -121.4218 | 0.39825 | 0.017319 | 0.0012902 | 0.0086175 | 0.11073 | -0.026716 | -0.032985 | 0.020397 | 0.064087 | 0.064087 | -0.10071 | 0.11902 | 0.23346 | 0.091553 | 0.018311 | 0.20142 | 0.45319 | -121.7651 | 121.3211 | -0.33417 | 121.4859 | 121.5408 | -0.16479 | -0.34332 | 0.054932 | 0.1648 | 121.4401 | 121.6232 | 121.6553 | 121.4859 | 121.4859 | 121.875 | 121.5134 | -0.34332 | 121.4859 | 121.4859 | 121.5134 | 121.6553 | 121.875 | -0.49896 | -122.1634
3864.0781 | 121.9986 | -121.4081 | 0.38452 | 0.00206 | -0.0010596 | 0.0086175 | 0.11393 | -0.02458 | -0.03384 | 0.023387 | 0.018311 | 0.07782 | -0.10529 | 0.11902 | 0.22888 | 0.10986 | -0.10071 | 0.17853 | 0.44861 | -121.7377 | 121.3028 | -0.3067 | 121.4264 | 121.5271 | -0.15564 | -0.32959 | 0.064087 | 0.1236 | 121.3074 | 121.5866 | 121.637 | 121.4859 | 121.4264 | 121.8567 | 121.5179 | -0.32959 | 121.4859 | 121.4264 | 121.5179 | 121.637 | 121.8567 | -0.48981 | -122.1222
3865.8594 | 121.9345 | -121.4539 | 0.40283 | 0.0096895 | -0.0010596 | 0.0077631 | 0.1118 | -0.02757 | -0.030849 | 0.022319 | 0.054932 | 0.050354 | -0.10071 | 0.12817 | 0.26093 | 0.10986 | 0.009155 | 0.2243 | 0.45319 | -121.7789 | 121.3531 | -0.35248 | 121.5088 | 121.582 | -0.14191 | -0.32501 | 0.050354 | 0.15564 | 121.463 | 121.6782 | 121.7148 | 121.5042 | 121.5088 | 121.907 | 121.5637 | -0.32501 | 121.5042 | 121.5088 | 121.5637 | 121.7148 | 121.907 | -0.50354 | -122.1817
3867.6562 | 121.9894 | -121.431 | 0.37994 | 0.0096895 | -0.00063242 | 0.0081903 | 0.11265 | -0.024366 | -0.033199 | 0.023815 | 0.059509 | 0.07782 | -0.10986 | 0.15564 | 0.27924 | 0.15106 | -0.14191 | 0.24261 | 0.4303 | -121.7514 | 121.3211 | -0.30212 | 121.4905 | 121.5866 | -0.10071 | -0.32043 | 0.050354 | 0.16937 | 121.2891 | 121.6736 | 121.7102 | 121.5088 | 121.4905 | 121.8613 | 121.582 | -0.32043 | 121.5088 | 121.4905 | 121.582 | 121.7102 | 121.8613 | -0.48981 | -122.1313
3869.3906 | 121.9574 | -121.4264 | 0.39825 | 0.00206 | -0.00020502 | 0.0056269 | 0.11094 | -0.026502 | -0.030849 | 0.021678 | -0.013733 | 0.09613 | -0.12817 | 0.086975 | 0.21515 | 0.068665 | 0.059509 | 0.16937 | 0.47607 | -121.8018 | 121.2982 | -0.30212 | 121.4127 | 121.5134 | -0.1831 | -0.37537 | 0.07782 | 0.11444 | 121.4859 | 121.5958 | 121.6415 | 121.5225 | 121.4127 | 121.9025 | 121.4951 | -0.37537 | 121.5225 | 121.4127 | 121.4951 | 121.6415 | 121.9025 | -0.52643 | -122.2
3871.1875 | 121.9666 | -121.431 | 0.36621 | 0.017319 | -0.00063242 | 0.0041315 | 0.11457 | -0.026502 | -0.032345 | 0.024028 | 0.004578 | 0.086975 | -0.13733 | 0.09613 | 0.19226 | 0.064087 | 0.004578 | 0.15106 | 0.46234 | -121.7834 | 121.2936 | -0.27924 | 121.4355 | 121.5271 | -0.17395 | -0.35248 | 0.09613 | 0.14191 | 121.4355 | 121.582 | 121.6232 | 121.5179 | 121.4355 | 121.8933 | 121.4951 | -0.35248 | 121.5179 | 121.4355 | 121.4951 | 121.6232 | 121.8933 | -0.50354 | -122.1497
3872.9844 | 122.0306 | -121.4127 | 0.37079 | 0.017319 | 0.00086298 | 0.0045587 | 0.11372 | -0.024366 | -0.031917 | 0.023601 | 0 | 0.068665 | -0.11902 | 0.09613 | 0.21515 | 0.086975 | -0.064087 | 0.14191 | 0.48523 | -121.7926 | 121.2936 | -0.30212 | 121.4127 | 121.5088 | -0.15564 | -0.37994 | 0.11444 | 0.11902 | 121.3486 | 121.5546 | 121.6278 | 121.4813 | 121.4127 | 121.8979 | 121.4996 | -0.37994 | 121.4813 | 121.4127 | 121.4996 | 121.6278 | 121.8979 | -0.48981 | -122.1634
3874.7031 | 122.0535 | -121.431 | 0.36163 | 0.00206 | -0.0017004 | 0.0032769 | 0.11009 | -0.027357 | -0.029354 | 0.022747 | 0.054932 | 0.041199 | -0.073242 | 0.14191 | 0.27466 | 0.14648 | -0.086975 | 0.23804 | 0.44403 | -121.7697 | 121.3577 | -0.32043 | 121.4859 | 121.5729 | -0.086975 | -0.33874 | 0.082398 | 0.12817 | 121.344 | 121.669 | 121.7056 | 121.4722 | 121.4859 | 121.875 | 121.5775 | -0.33874 | 121.4722 | 121.4859 | 121.5775 | 121.7056 | 121.875 | -0.43488 | -122.1313
3876.5 | 121.9208 | -121.4813 | 0.39368 | 0.0096895 | -0.0014868 | 0.0051995 | 0.11714 | -0.02522 | -0.036831 | 0.021038 | 0.059509 | 0.068665 | -0.10071 | 0.11902 | 0.23804 | 0.11444 | -0.036621 | 0.20599 | 0.4715 | -121.7789 | 121.3806 | -0.32501 | 121.5408 | 121.6003 | -0.15564 | -0.29755 | 0.07782 | 0.16022 | 121.4447 | 121.6873 | 121.7194 | 121.55 | 121.5408 | 121.9528 | 121.5958 | -0.29755 | 121.55 | 121.5408 | 121.5958 | 121.7194 | 121.9528 | -0.49439 | -122.1725
3878.2969 | 122.0352 | -121.4172 | 0.37537 | 0.0096895 | 0.00022218 | 0.0058405 | 0.1165 | -0.024152 | -0.032772 | 0.023174 | 0.013733 | 0.086975 | -0.1236 | 0.09613 | 0.21515 | 0.10529 | -0.082397 | 0.15564 | 0.4715 | -121.7789 | 121.2936 | -0.28839 | 121.431 | 121.5134 | -0.16022 | -0.36163 | 0.096131 | 0.13733 | 121.3348 | 121.5729 | 121.6324 | 121.5042 | 121.431 | 121.8887 | 121.5225 | -0.36163 | 121.5042 | 121.431 | 121.5225 | 121.6324 | 121.8887 | -0.49896 | -122.1542
3880.0156 | 122.0444 | -121.4355 | 0.3891 | 0.0096895 | -0.0012732 | 0.0058405 | 0.11521 | -0.024152 | -0.031917 | 0.02296 | -0.018311 | 0.091553 | -0.10986 | 0.064087 | 0.21515 | 0.059509 | 0 | 0.13733 | 0.4715 | -121.8063 | 121.3257 | -0.29755 | 121.4172 | 121.4996 | -0.17395 | -0.37079 | 0.082398 | 0.091552 | 121.4355 | 121.5729 | 121.6507 | 121.5271 | 121.4172 | 121.907 | 121.4951 | -0.37079 | 121.5271 | 121.4172 | 121.4951 | 121.6507 | 121.907 | -0.49896 | -122.1954
3881.7969 | 121.9299 | -121.4584 | 0.41199 | 0.017319 | -0.00041862 | 0.0071221 | 0.11628 | -0.02458 | -0.034054 | 0.024669 | 0.068665 | 0.068665 | -0.1236 | 0.16479 | 0.28381 | 0.13733 | -0.041199 | 0.2243 | 0.48523 | -121.756 | 121.3348 | -0.34332 | 121.5271 | 121.6232 | -0.12817 | -0.29755 | 0.073242 | 0.19226 | 121.4172 | 121.6827 | 121.7422 | 121.5271 | 121.5271 | 121.9437 | 121.5958 | -0.29755 | 121.5271 | 121.5271 | 121.5958 | 121.7422 | 121.9437 | -0.53558 | -122.168
3883.5938 | 121.8567 | -119.6182 | 2.2202 | 0.00206 | -0.002555 | 0.0086175 | 0.96394 | -0.022443 | -0.029995 | 0.87489 | 0.041199 | 0.041199 | -0.1236 | 0.15106 | -6.0928 | 0.13275 | -0.027466 | 0.21973 | 3.067 | -118.9133 | 119.4946 | -2.179 | 119.6594 | 119.7693 | -8.313 | 0.70496 | 0.84686 | 0.16479 | 119.5908 | 119.838 | 113.5254 | 119.6594 | 119.6594 | 122.6852 | 119.751 | 0.70496 | 119.6594 | 119.6594 | 119.751 | 113.5254 | 122.6852 | -2.3438 | -121.1334
3885.4062 | 121.9894 | -116.2079 | 5.5527 | 0.0096895 | -0.001914 | 0.0034905 | 0.099832 | -0.024366 | -0.028927 | 0.023387 | 0.09613 | 0.027466 | -0.054932 | 0.21057 | 0.58594 | 0.21057 | -0.13275 | 0.32501 | 5.5756 | -116.597 | 116.153 | -5.5252 | 116.304 | 116.4185 | -4.9667 | -0.3891 | 0.022889 | 0.15106 | 116.0751 | 116.5329 | 116.7938 | 116.2354 | 116.304 | 121.7834 | 116.4185 | -0.3891 | 116.2354 | 116.304 | 116.4185 | 116.7938 | 121.7834 | -5.6076 | -122.1497
3887.1406 | 122.0261 | -116.2811 | 5.5115 | 0.0096895 | -0.0017004 | 0.0037043 | 0.10261 | -0.023939 | -0.027859 | 0.021465 | -0.018311 | 0.059509 | -0.12817 | 0.082397 | 0.46692 | 0.059509 | 0.050354 | 0.17853 | 5.5939 | -116.6656 | 116.153 | -5.452 | 116.2628 | 116.3635 | -5.0446 | -0.38452 | 0.082397 | 0.10986 | 116.3315 | 116.4597 | 116.748 | 116.3406 | 116.2628 | 121.875 | 116.3406 | -0.38452 | 116.3406 | 116.2628 | 116.3406 | 116.748 | 121.875 | -5.6396 | -122.1771
3888.9219 | 122.0078 | -118.4463 | 3.3966 | 0.017319 | -0.0034094 | 0.0015679 | 0.10688 | -0.026716 | -0.030422 | 0.021465 | 0.10986 | 0.027466 | -0.064087 | 0.20142 | 0.70038 | 0.21515 | -0.11902 | 0.33417 | 3.3875 | -118.483 | 118.3823 | -3.3691 | 118.5562 | 118.6478 | -2.6962 | -0.036621 | -0.009155 | 0.17395 | 118.3273 | 118.7805 | 119.1467 | 118.4738 | 118.5562 | 121.8338 | 118.6615 | -0.036621 | 118.4738 | 118.5562 | 118.6615 | 119.1467 | 121.8338 | -3.4607 | -121.8796
3890.7188 | 121.9574 | -118.5928 | 3.2867 | 0.00206 | -0.0010596 | 0.0064813 | 0.11073 | -0.023725 | -0.032345 | 0.019756 | 0.045776 | 0.073242 | -0.10529 | 0.16022 | 0.59052 | 0.1236 | -0.045776 | 0.21515 | 3.3508 | -118.8858 | 118.4875 | -3.2135 | 118.6386 | 118.7531 | -2.6962 | -0.29297 | 0.064087 | 0.15106 | 118.5471 | 118.808 | 119.1833 | 118.6661 | 118.6386 | 121.9437 | 118.7164 | -0.29297 | 118.6661 | 118.6386 | 118.7164 | 119.1833 | 121.9437 | -3.392 | -122.1725
3892.5156 | 122.0993 | -119.5679 | 2.2385 | 0.00206 | -0.00084602 | 0.0077631 | 0.11158 | -0.022016 | -0.03149 | 0.023174 | 0.022888 | 0.086975 | -0.11902 | 0.10529 | 0.83313 | 0.09613 | -0.073242 | 0.16022 | 2.33 | -119.9341 | 119.4489 | -2.1515 | 119.5908 | 119.6732 | -1.4053 | -0.36621 | 0.091553 | 0.14191 | 119.4946 | 119.7281 | 120.401 | 119.6548 | 119.5908 | 121.8979 | 119.664 | -0.36621 | 119.6548 | 119.5908 | 119.664 | 120.401 | 121.8979 | -2.3575 | -122.1725
3894.2344 | 122.1313 | -119.5541 | 2.2751 | 0.00206 | -0.003623 | 0.0013543 | 0.11073 | -0.024793 | -0.032772 | 0.023815 | -0.013733 | 0.073242 | -0.1236 | 0.073242 | 0.80566 | 0.082397 | -0.032043 | 0.13275 | 2.3575 | -119.9066 | 119.4305 | -2.2018 | 119.5404 | 119.6274 | -1.4694 | -0.35248 | 0.082398 | 0.10986 | 119.5221 | 119.6869 | 120.3598 | 119.6274 | 119.5404 | 121.9116 | 119.6365 | -0.35248 | 119.6274 | 119.5404 | 119.6365 | 120.3598 | 121.9116 | -2.3987 | -122.1817
3896.0312 | 122.081 | -119.664 | 2.1606 | 0.0096895 | 8.578e-06 | 0.0058405 | 0.11094 | -0.023939 | -0.030208 | 0.024242 | 0 | 0.07782 | -0.10529 | 0.082397 | 0.86975 | 0.086975 | -0.045776 | 0.14191 | 2.2476 | -120.0119 | 119.5587 | -2.0828 | 119.664 | 119.7464 | -1.2909 | -0.3479 | 0.086975 | 0.10529 | 119.6182 | 119.8059 | 120.5338 | 119.7418 | 119.664 | 121.9116 | 119.751 | -0.3479 | 119.7418 | 119.664 | 119.751 | 120.5338 | 121.9116 | -2.2659 | -122.1725
3897.7656 | 122.0352 | -119.7784 | 2.1057 | 0.0096895 | 0.00043578 | 0.0062677 | 0.11009 | -0.024366 | -0.03149 | 0.023174 | -0.018311 | 0.091553 | -0.15106 | 0.07782 | 0.88806 | 0.068665 | 0.050354 | 0.16479 | 2.179 | -120.1218 | 119.6274 | -2.0142 | 119.7601 | 119.8563 | -1.2177 | -0.34332 | 0.073242 | 0.13275 | 119.8288 | 119.9432 | 120.6665 | 119.87 | 119.7601 | 121.9574 | 119.8471 | -0.34332 | 119.87 | 119.7601 | 119.8471 | 120.6665 | 121.9574 | -2.2568 | -122.2275
3899.5625 | 122.0718 | -119.7006 | 2.179 | 0.00206 | -0.001914 | 0.0058405 | 0.10987 | -0.026075 | -0.029568 | 0.022106 | 0.091553 | 0.032043 | -0.059509 | 0.18768 | 1.0025 | 0.19226 | -0.17395 | 0.2655 | 2.2293 | -120.0394 | 119.6411 | -2.1469 | 119.7922 | 119.8883 | -1.1765 | -0.33875 | 0.050354 | 0.15106 | 119.5267 | 119.9661 | 120.7031 | 119.7327 | 119.7922 | 121.9299 | 119.8929 | -0.33875 | 119.7327 | 119.7922 | 119.8929 | 120.7031 | 121.9299 | -2.2385 | -122.2183
3901.3438 | 122.0764 | -119.6686 | 2.211 | 0.017319 | -0.0010596 | 0.0043451 | 0.10816 | -0.027998 | -0.028927 | 0.021465 | 0.086975 | 0.054932 | -0.064087 | 0.20599 | 1.0483 | 0.1831 | -0.13275 | 0.3067 | 2.2614 | -120.0073 | 119.6045 | -2.1561 | 119.7556 | 119.8746 | -1.1627 | -0.33875 | 0.050354 | 0.15106 | 119.5358 | 119.9753 | 120.7169 | 119.7235 | 119.7556 | 121.9299 | 119.8517 | -0.33875 | 119.7235 | 119.7556 | 119.8517 | 120.7169 | 121.9299 | -2.2751 | -122.2183
3903.0781 | 121.9803 | -119.8288 | 2.1149 | 0.017319 | 0.00043578 | 0.0056269 | 0.11585 | -0.025007 | -0.032558 | 0.022533 | 0.054932 | 0.07782 | -0.1236 | 0.13275 | 0.96588 | 0.10529 | -0.022888 | 0.21973 | 2.1378 | -120.1675 | 119.7052 | -2.037 | 119.8837 | 119.9615 | -1.149 | -0.33875 | 0.022888 | 0.17853 | 119.8059 | 120.0485 | 120.7947 | 119.9066 | 119.8837 | 121.9666 | 119.9341 | -0.33875 | 119.9066 | 119.8837 | 119.9341 | 120.7947 | 121.9666 | -2.2385 | -122.2824
3904.8594 | 122.0673 | -119.6732 | 2.2568 | 0.00206 | -0.0023412 | 0.0060541 | 0.1165 | -0.023939 | -0.030422 | 0.02296 | 0.10071 | 0.054932 | -0.054932 | 0.19226 | 1.0666 | 0.19684 | -0.19226 | 0.28381 | 2.243 | -119.9936 | 119.6182 | -2.2018 | 119.7739 | 119.8654 | -1.1902 | -0.32043 | -0.013733 | 0.15564 | 119.4809 | 119.957 | 120.7397 | 119.7281 | 119.7739 | 121.9162 | 119.87 | -0.32043 | 119.7281 | 119.7739 | 119.87 | 120.7397 | 121.9162 | -2.3117 | -122.2504
3906.6562 | 122.0581 | -119.5999 | 2.2751 | 0.017319 | 0.00043578 | 0.0049859 | 0.12248 | -0.022871 | -0.03384 | 0.026164 | 0.013733 | 0.073242 | -0.091553 | 0.091553 | 1.0208 | 0.050354 | -0.004578 | 0.14191 | 2.3621 | -119.9661 | 119.5084 | -2.2018 | 119.6136 | 119.6915 | -1.2543 | -0.36621 | 0.086976 | 0.10529 | 119.5953 | 119.7418 | 120.6207 | 119.6732 | 119.6136 | 121.962 | 119.6503 | -0.36621 | 119.6732 | 119.6136 | 119.6503 | 120.6207 | 121.962 | -2.3666 | -122.2412
3908.3906 | 122.1497 | -119.8883 | 1.9638 | 0.0096895 | -0.0027686 | 0.0060541 | 0.10816 | -0.026716 | -0.030849 | 0.023387 | 0.045776 | 0.059509 | -0.041199 | 0.13275 | 0.98877 | 0.14648 | -0.10071 | 0.2243 | 1.9958 | -120.2637 | 119.8471 | -1.9043 | 119.9341 | 120.0211 | -0.97504 | -0.37537 | 0.032044 | 0.086975 | 119.7876 | 120.1126 | 120.8771 | 119.9478 | 119.9341 | 121.8842 | 120.0348 | -0.37537 | 119.9478 | 119.9341 | 120.0348 | 120.8771 | 121.8842 | -2.005 | -122.2275
3910.1719 | 122.1268 | -120.0027 | 1.8448 | 0.024948 | 8.578e-06 | 0.0017817 | 0.11906 | -0.024793 | -0.035122 | 0.024242 | -0.013733 | 0.07782 | -0.09613 | 0.07782 | 0.92468 | 0.059509 | -0.013733 | 0.15106 | 1.9318 | -120.3827 | 119.9066 | -1.767 | 119.989 | 120.0806 | -0.92011 | -0.37994 | 0.086975 | 0.082397 | 119.989 | 120.1538 | 120.9274 | 120.0806 | 119.989 | 121.9345 | 120.0623 | -0.37994 | 120.0806 | 119.989 | 120.0623 | 120.9274 | 121.9345 | -1.9409 | -122.2275
3911.8906 | 122.1359 | -120.1126 | 1.767 | 0.017319 | -0.002555 | 0.0084039 | 0.11564 | -0.023511 | -0.033626 | 0.024028 | 0.009155 | 0.068665 | -0.11444 | 0.086975 | 0.91553 | 0.068665 | -0.018311 | 0.13733 | 1.8585 | -120.4559 | 119.9982 | -1.6983 | 120.1218 | 120.1996 | -0.85144 | -0.34332 | 0.091553 | 0.1236 | 120.0943 | 120.2499 | 121.0281 | 120.1813 | 120.1218 | 121.9711 | 120.1813 | -0.34332 | 120.1813 | 120.1218 | 120.1813 | 121.0281 | 121.9711 | -1.8814 | -122.2229
3913.6875 | 122.113 | -120.0989 | 1.7715 | 0.00206 | 0.00043578 | 0.0034905 | 0.11393 | -0.022657 | -0.032985 | 0.02531 | 0.013733 | 0.086975 | -0.10986 | 0.10529 | 0.97504 | 0.10071 | -0.091553 | 0.17395 | 1.8356 | -120.4239 | 119.989 | -1.6846 | 120.1126 | 120.2042 | -0.79651 | -0.32501 | 0.064087 | 0.1236 | 120.0073 | 120.2728 | 121.0739 | 120.1859 | 120.1126 | 121.9345 | 120.1996 | -0.32501 | 120.1859 | 120.1126 | 120.1996 | 121.0739 | 121.9345 | -1.8814 | -122.1954
3915.4844 | 122.1039 | -120.0394 | 1.8631 | 0.0096895 | -0.0017004 | 0.0066949 | 0.11009 | -0.02458 | -0.032131 | 0.024883 | 0.09613 | 0.050354 | -0.027466 | 0.18768 | 1.0437 | 0.18768 | -0.16479 | 0.2655 | 1.8997 | -120.3552 | 120.0119 | -1.8127 | 120.1355 | 120.2271 | -0.8194 | -0.31586 | 0.036621 | 0.1236 | 119.8746 | 120.3049 | 121.0831 | 120.0897 | 120.1355 | 121.9391 | 120.2271 | -0.31586 | 120.0897 | 120.1355 | 120.2271 | 121.0831 | 121.9391 | -1.8906 | -122.2183
3917.2969 | 121.9803 | -120.0989 | 1.8951 | 0.0096895 | -0.0023412 | 0.0054131 | 0.11457 | -0.025648 | -0.031277 | 0.023174 | 0.10071 | 0.059509 | -0.050354 | 0.21515 | 1.0849 | 0.21515 | -0.13275 | 0.32959 | 1.8997 | -120.3506 | 120.0485 | -1.8356 | 120.1996 | 120.314 | -0.81024 | -0.25177 | 0.004577 | 0.15106 | 119.9661 | 120.4285 | 121.1838 | 120.1584 | 120.1996 | 121.9986 | 120.314 | -0.25177 | 120.1584 | 120.1996 | 120.314 | 121.1838 | 121.9986 | -1.9455 | -122.2458
3919.0156 | 122.0444 | -120.1401 | 1.8539 | 0.0096895 | -0.003623 | 0.0060541 | 0.11863 | -0.027357 | -0.03149 | 0.024455 | 0.059509 | 0.068665 | -0.054932 | 0.15106 | 1.0941 | 0.1236 | -0.018311 | 0.2243 | 2.0096 | -120.4193 | 120.0851 | -1.7853 | 120.1996 | 120.2911 | -0.75989 | -0.27924 | 0.15564 | 0.11444 | 120.1218 | 120.3644 | 121.2341 | 120.2087 | 120.1996 | 122.1497 | 120.2637 | -0.27924 | 120.2087 | 120.1996 | 120.2637 | 121.2341 | 122.1497 | -1.9089 | -122.2733
3920.7969 | 122.0535 | -119.957 | 2.0004 | 0.0096895 | -0.0010596 | 0.0086175 | 0.12611 | -0.028211 | -0.031277 | 0.024455 | 0.10071 | 0.027466 | -0.013733 | 0.21057 | 1.2085 | 0.21057 | -0.14648 | 0.32959 | 2.0187 | -120.2408 | 119.9432 | -1.973 | 120.0577 | 120.1675 | -0.79193 | -0.28381 | 0.018311 | 0.11444 | 119.8105 | 120.2866 | 121.1655 | 119.9844 | 120.0577 | 121.9757 | 120.1675 | -0.28381 | 119.9844 | 120.0577 | 120.1675 | 121.1655 | 121.9757 | -2.0142 | -122.2412
3922.5469 | 122.0856 | -119.7739 | 2.1378 | 0.0096895 | -0.0010596 | 0.0075495 | 0.12098 | -0.024366 | -0.033413 | 0.027873 | -0.018311 | 0.086975 | -0.10986 | 0.091553 | 1.1719 | 0.050354 | -0.018311 | 0.13733 | 2.1561 | -120.282 | 119.664 | -2.0508 | 119.7556 | 119.8654 | -0.96588 | -0.50812 | 0.018311 | 0.091552 | 119.7556 | 119.9112 | 120.9457 | 119.8608 | 119.7556 | 121.9299 | 119.8242 | -0.50812 | 119.8608 | 119.7556 | 119.8242 | 120.9457 | 121.9299 | -2.2476 | -122.4197
3924.3438 | 122.1359 | -119.9799 | 1.9043 | 0.00206 | -0.0012732 | 0.0058405 | 0.11244 | -0.026289 | -0.03149 | 0.028087 | 0.059509 | 0.036621 | -0.027466 | 0.14648 | 1.1169 | 0.14191 | -0.10529 | 0.22888 | 1.9821 | -120.3598 | 119.9524 | -1.8677 | 120.0394 | 120.1263 | -0.78735 | -0.37994 | 0.07782 | 0.086975 | 119.8746 | 120.2087 | 121.0968 | 120.0165 | 120.0394 | 121.962 | 120.1218 | -0.37994 | 120.0165 | 120.0394 | 120.1218 | 121.0968 | 121.962 | -1.9318 | -122.2641
3926.0625 | 122.0764 | -119.8746 | 2.0554 | 0.0096895 | -0.0038366 | 0.0062677 | 0.11692 | -0.026075 | -0.031917 | 0.02531 | 0.10071 | 0.041199 | -0.045776 | 0.21973 | 1.2543 | 0.20599 | -0.15106 | 0.31128 | 2.037 | -120.2408 | 119.8288 | -2.0142 | 119.9753 | 120.0943 | -0.80109 | -0.36621 | -0.018311 | 0.14648 | 119.7235 | 120.1859 | 121.1288 | 119.9158 | 119.9753 | 121.9116 | 120.0806 | -0.36621 | 119.9158 | 119.9753 | 120.0806 | 121.1288 | 121.9116 | -2.1011 | -122.2961
3927.8438 | 122.3648 | -119.6136 | 2.3163 | 0.0096895 | -0.00063242 | 0.0034905 | 0.14256 | -0.02223 | -0.03619 | 0.02766 | 0.036621 | 0.07782 | -0.073242 | 0.15106 | 1.3367 | 0.14648 | -0.10986 | 0.21973 | 2.2614 | -119.9936 | 119.5404 | -2.2385 | 119.6503 | 119.7647 | -0.97961 | -0.37994 | -0.054931 | 0.10986 | 119.5038 | 119.8334 | 120.9503 | 119.6915 | 119.6503 | 121.875 | 119.7601 | -0.37994 | 119.6915 | 119.6503 | 119.7601 | 120.9503 | 121.875 | -2.3895 | -122.3099
3929.5625 | 121.962 | -119.9661 | 2.0233 | 0.00206 | -0.00020502 | 0.0041315 | 0.11842 | -0.023298 | -0.033626 | 0.029369 | 0.1236 | 0.041199 | -0.032043 | 0.22888 | 1.2817 | 0.18768 | -0.14191 | 0.33417 | 2.092 | -120.163 | 119.9341 | -1.9821 | 120.0897 | 120.195 | -0.74158 | -0.19684 | 0.068665 | 0.15564 | 119.8242 | 120.3003 | 121.2479 | 120.0073 | 120.0897 | 122.0581 | 120.1538 | -0.19684 | 120.0073 | 120.0897 | 120.1538 | 121.2479 | 122.0581 | -2.0554 | -122.1863
3931.3594 | 122.1725 | -119.5908 | 2.3346 | -0.0055695 | -0.0012732 | 0.0066949 | 0.13423 | -0.023298 | -0.03149 | 0.037486 | 0.086975 | 0.045776 | -0.041199 | 0.16937 | 1.3412 | 0.17395 | -0.15106 | 0.24719 | 2.3758 | -119.8929 | 119.5496 | -2.2888 | 119.6777 | 119.7601 | -0.99335 | -0.30212 | 0.041198 | 0.12817 | 119.4397 | 119.838 | 120.932 | 119.6365 | 119.6777 | 121.9666 | 119.7647 | -0.30212 | 119.6365 | 119.6777 | 119.7647 | 120.932 | 121.9666 | -2.3758 | -122.2275
3933.0781 | 122.0078 | -114.3677 | 7.489 | 0.024948 | 0.00086298 | 0.0045587 | 1.0332 | -0.021375 | -0.0090598 | 0.80247 | -0.004578 | 0.050354 | -0.16022 | 0.1236 | -35.9619 | 0.068665 | 0.036621 | 0.20142 | 7.8827 | -114.2029 | 114.2075 | -7.4387 | 114.3631 | 114.4913 | -43.4509 | 0.16479 | 0.39368 | 0.15564 | 114.4043 | 114.5691 | 78.4058 | 114.418 | 114.3631 | 122.2504 | 114.4363 | 0.16479 | 114.418 | 114.3631 | 114.4363 | 78.4058 | 122.2504 | -7.6492 | -121.6919
3934.8594 | 121.5729 | -13.4445 | 108.3252 | 0.0096895 | -0.0012732 | 0.0019953 | 0.06138 | 0.032458 | 0.021488 | 0.054149 | -0.036621 | 0.036621 | -0.15564 | 0.059509 | 0.84686 | 0.036621 | -0.032043 | 0.10071 | 104.6082 | -17.6514 | 13.2889 | -108.2886 | 13.4079 | 13.504 | -107.4783 | -4.2068 | -3.717 | 0.11902 | 13.4125 | 13.5452 | 14.2914 | 13.4811 | 13.4079 | 118.0527 | 13.4811 | -4.2068 | 13.4811 | 13.4079 | 13.4811 | 14.2914 | 118.0527 | -108.4808 | -125.9766
3936.6562 | 121.9849 | -84.2056 | 37.3627 | 0.0096895 | -0.003623 | 0.0060541 | 1.0314 | -0.0038581 | -0.011837 | 0.92253 | 0.041199 | 0.064087 | -0.10529 | 0.13275 | 4.4861 | 0.11444 | -0.050354 | 0.19226 | 39.1113 | -82.869 | 84.1003 | -37.2986 | 84.2468 | 84.3384 | -32.8766 | 1.3367 | 1.7487 | 0.14649 | 84.1553 | 84.3979 | 88.6917 | 84.2697 | 84.2468 | 123.317 | 84.3201 | 1.3367 | 84.2697 | 84.2468 | 84.3201 | 88.6917 | 123.317 | -37.468 | -120.2316
3938.4375 | 121.7331 | -5.4108 | 116.5192 | 0.017319 | -0.00084602 | 0.0047723 | 0.094919 | 0.039507 | 0.028538 | 0.17057 | -0.022888 | 0.050354 | -0.15106 | 0.068665 | 0.60883 | 0.045776 | -0.050354 | 0.10529 | 116.7938 | -5.5252 | 5.2597 | -116.4688 | 5.3879 | 5.4794 | -115.9103 | -0.11444 | 0.27466 | 0.12817 | 5.3604 | 5.5161 | 6.0196 | 5.4611 | 5.3879 | 122.2046 | 5.4565 | -0.11444 | 5.4611 | 5.3879 | 5.4565 | 6.0196 | 122.2046 | -116.6702 | -122.0444
3940.2344 | 122.0352 | -4.6005 | 117.3248 | 0.00206 | -0.0027686 | 0.0086175 | 0.060098 | 0.037157 | 0.033451 | 0.16224 | 0.059509 | 0.004578 | -0.10529 | 0.16022 | 0.65002 | 0.16479 | -0.23346 | 0.22888 | 117.4026 | -4.7974 | 4.4952 | -117.3203 | 4.66 | 4.7607 | -116.6748 | -0.19684 | 0.07782 | 0.16479 | 4.3671 | 4.8294 | 5.2505 | 4.6051 | 4.66 | 122.0032 | 4.7653 | -0.19684 | 4.6051 | 4.66 | 4.7653 | 5.2505 | 122.0032 | -117.4301 | -122.1222
3941.9688 | 121.9528 | -4.3442 | 117.691 | 0.00206 | -0.0031958 | 0.0062677 | 0.057749 | 0.03673 | 0.032383 | 0.16587 | 0.054932 | 0.004578 | -0.11902 | 0.17395 | 0.66834 | 0.15106 | -0.14191 | 0.26093 | 117.7826 | -4.509 | 4.2252 | -117.6865 | 4.3991 | 4.5181 | -117.0227 | -0.16479 | 0.091553 | 0.17395 | 4.2023 | 4.6051 | 5.0125 | 4.3488 | 4.3991 | 122.1268 | 4.4952 | -0.16479 | 4.3488 | 4.3991 | 4.4952 | 5.0125 | 122.1268 | -117.8101 | -122.2
3943.75 | 121.9528 | -4.1656 | 117.865 | 0.00206 | -0.0031958 | 0.0017817 | 0.058389 | 0.036303 | 0.031956 | 0.16651 | 0.082397 | -0.009155 | -0.11444 | 0.1831 | 0.64545 | 0.16937 | -0.17395 | 0.28839 | 117.9474 | -4.2984 | 4.0512 | -117.8741 | 4.248 | 4.3488 | -117.2195 | -0.13275 | 0.082398 | 0.19684 | 3.9917 | 4.454 | 4.8111 | 4.1565 | 4.248 | 122.113 | 4.335 | -0.13275 | 4.1565 | 4.248 | 4.335 | 4.8111 | 122.113 | -117.9794 | -122.1634
3945.5625 | 122.0306 | -3.9322 | 118.1168 | 0.00206 | -0.0034094 | 0.0017817 | 0.062021 | 0.037157 | 0.033879 | 0.15498 | -0.018311 | 0.018311 | -0.14191 | 0.09613 | 0.54474 | 0.054932 | -0.018311 | 0.14648 | 118.2404 | -4.1336 | 3.7903 | -118.0984 | 3.9139 | 4.0283 | -117.572 | -0.20142 | 0.1236 | 0.1236 | 3.9139 | 4.0787 | 4.4769 | 3.9505 | 3.9139 | 122.1725 | 3.9871 | -0.20142 | 3.9505 | 3.9139 | 3.9871 | 4.4769 | 122.1725 | -118.2587 | -122.2504
3947.375 | 121.9803 | -3.7857 | 118.2587 | 0.024948 | -0.00063242 | 0.0062677 | 0.065439 | 0.037585 | 0.02982 | 0.16032 | 0.027466 | 0.041199 | -0.15564 | 0.1236 | 0.61798 | 0.082397 | -0.082397 | 0.1831 | 118.3594 | -3.9642 | 3.6301 | -118.2175 | 3.8132 | 3.9093 | -117.6407 | -0.17853 | 0.10071 | 0.18311 | 3.7033 | 3.9688 | 4.4037 | 3.8269 | 3.8132 | 122.1451 | 3.8681 | -0.17853 | 3.8269 | 3.8132 | 3.8681 | 4.4037 | 122.1451 | -118.4143 | -122.2229
3949.1562 | 122.0123 | -3.7308 | 118.3136 | 0.0096895 | 0.00086298 | 0.0054131 | 0.063303 | 0.039507 | 0.030888 | 0.15904 | -0.041199 | 0.036621 | -0.15106 | 0.059509 | 0.57678 | 0.027466 | 0.009155 | 0.14191 | 118.4326 | -3.9322 | 3.5797 | -118.277 | 3.6896 | 3.7903 | -117.7368 | -0.20142 | 0.11902 | 0.10986 | 3.7399 | 3.8727 | 4.3076 | 3.7674 | 3.6896 | 122.1634 | 3.7582 | -0.20142 | 3.7674 | 3.6896 | 3.7582 | 4.3076 | 122.1634 | -118.4647 | -122.2458
3950.875 | 122.0078 | -3.6896 | 118.3319 | 0.0096895 | -0.00084602 | 0.0096857 | 0.065225 | 0.040575 | 0.031529 | 0.15904 | 0.009155 | 0.032043 | -0.14648 | 0.091553 | 0.62256 | 0.064087 | -0.068665 | 0.15106 | 118.4738 | -3.891 | 3.5431 | -118.2999 | 3.6987 | 3.7811 | -117.7094 | -0.20142 | 0.14191 | 0.15564 | 3.6209 | 3.8406 | 4.3121 | 3.7216 | 3.6987 | 122.1634 | 3.7537 | -0.20142 | 3.7216 | 3.6987 | 3.7537 | 4.3121 | 122.1634 | -118.4784 | -122.2229
3952.6719 | 122.049 | -3.6255 | 118.4052 | 0.00206 | -0.00020502 | 0.0069085 | 0.060098 | 0.037157 | 0.032597 | 0.15776 | 0.009155 | 0.018311 | -0.1236 | 0.10071 | 0.63171 | 0.082397 | -0.045776 | 0.17395 | 118.5104 | -3.8315 | 3.5019 | -118.3868 | 3.6346 | 3.7262 | -117.7734 | -0.20599 | 0.10529 | 0.13275 | 3.5797 | 3.7994 | 4.2572 | 3.6438 | 3.6346 | 122.1359 | 3.7079 | -0.20599 | 3.6438 | 3.6346 | 3.7079 | 4.2572 | 122.1359 | -118.5287 | -122.2366
3954.4688 | 122.1268 | -3.4836 | 118.4555 | 0.017319 | 0.00022218 | 0.0086175 | 0.063089 | 0.041216 | 0.031742 | 0.1569 | -0.032043 | 0.041199 | -0.15106 | 0.064087 | 0.63629 | 0.059509 | -0.07782 | 0.10071 | 118.6203 | -3.7491 | 3.3325 | -118.4143 | 3.4515 | 3.5477 | -117.8192 | -0.2655 | 0.16479 | 0.11902 | 3.4058 | 3.5843 | 4.1199 | 3.5248 | 3.4515 | 122.1039 | 3.5431 | -0.2655 | 3.5248 | 3.4515 | 3.5431 | 4.1199 | 122.1039 | -118.6066 | -122.2046
3956.2031 | 121.9894 | -41.803 | 79.8843 | 0.00206 | -0.0017004 | 0.0015679 | 0.28889 | 0.01665 | 0.0097392 | 0.15071 | 0.082397 | 0.036621 | 0.036621 | 0.19684 | 5.4703 | 0.20599 | -0.14648 | 0.3067 | 79.0009 | -43.3044 | 41.8396 | -79.8477 | 41.8854 | 41.9998 | -74.4141 | -1.5015 | -0.88348 | 0.045776 | 41.6565 | 42.1097 | 47.2733 | 41.8396 | 41.8854 | 120.8038 | 42.009 | -1.5015 | 41.8396 | 41.8854 | 42.009 | 47.2733 | 120.8038 | -79.8477 | -123.1888
3958 | 121.8292 | -5.0583 | 117.0181 | 0.017319 | -0.00020502 | 0.0069085 | 0.06608 | 0.039721 | 0.032383 | 0.078288 | 0.022888 | 0.036621 | -0.10529 | 0.13733 | 1.1993 | 0.07782 | -0.086975 | 0.16022 | 117.0914 | -5.2322 | 4.953 | -116.9815 | 5.0812 | 5.1956 | -115.8188 | -0.17395 | 0.073243 | 0.12817 | 4.9713 | 5.2185 | 6.2576 | 5.0949 | 5.0812 | 122.1497 | 5.1361 | -0.17395 | 5.0949 | 5.0812 | 5.1361 | 6.2576 | 122.1497 | -117.1234 | -122.2504
3959.7969 | 122.0078 | -4.7333 | 117.3203 | 0.0096895 | -0.003623 | 0.0028497 | 0.056681 | 0.036944 | 0.033024 | 0.087474 | 0.073242 | 0.009155 | -0.086975 | 0.20142 | 1.1993 | 0.1831 | -0.19684 | 0.31128 | 117.3843 | -4.8935 | 4.6463 | -117.3111 | 4.8065 | 4.9347 | -116.1209 | -0.16022 | 0.064087 | 0.16022 | 4.5364 | 5.0446 | 5.9326 | 4.7424 | 4.8065 | 122.1176 | 4.9164 | -0.16022 | 4.7424 | 4.8065 | 4.9164 | 5.9326 | 122.1176 | -117.4072 | -122.2137
3961.5469 | 122.0169 | -4.9576 | 117.1051 | 0.017319 | -0.002555 | 0.0007135 | 0.057535 | 0.03673 | 0.031529 | 0.096019 | 0.054932 | 0.004578 | -0.10071 | 0.19226 | 1.149 | 0.1831 | -0.17853 | 0.29755 | 117.1921 | -5.0812 | 4.8569 | -117.1005 | 5.0125 | 5.1498 | -115.9561 | -0.1236 | 0.086975 | 0.15564 | 4.7791 | 5.2551 | 6.1066 | 4.9622 | 5.0125 | 122.1497 | 5.1407 | -0.1236 | 4.9622 | 5.0125 | 5.1407 | 6.1066 | 122.1497 | -117.2058 | -122.1863
3963.3594 | 122.1634 | -5.0034 | 116.9128 | 0.00206 | -0.0017004 | 0.0043451 | 0.058817 | 0.036517 | 0.03217 | 0.10286 | 0.032043 | 0.009155 | -0.11444 | 0.11902 | 1.03 | 0.11902 | -0.14648 | 0.20142 | 117.0959 | -5.2048 | 4.8889 | -116.9037 | 5.0354 | 5.1224 | -115.8829 | -0.20142 | 0.1831 | 0.14648 | 4.8569 | 5.2048 | 6.0333 | 5.0125 | 5.0354 | 122.0993 | 5.1224 | -0.20142 | 5.0125 | 5.0354 | 5.1224 | 6.0333 | 122.0993 | -117.0273 | -122.1176
3965.1562 | 122.0032 | -4.4312 | 117.6224 | 0.017319 | 0.002572 | 0.0039179 | 0.068216 | 0.037371 | 0.031742 | 0.092601 | 0.050354 | 0.036621 | -0.13275 | 0.1236 | 1.062 | 0.073242 | -0.07782 | 0.19226 | 117.7872 | -4.5959 | 4.2984 | -117.5858 | 4.4815 | 4.5547 | -116.5604 | -0.16479 | 0.16479 | 0.18311 | 4.3533 | 4.6234 | 5.4932 | 4.4678 | 4.4815 | 122.2183 | 4.5044 | -0.16479 | 4.4678 | 4.4815 | 4.5044 | 5.4932 | 122.2183 | -117.7551 | -122.2183
3966.9531 | 122.0718 | -4.3625 | 117.7094 | 0.00206 | -0.001914 | 0.0032769 | 0.063089 | 0.038653 | 0.031315 | 0.09431 | 0.004578 | 0.027466 | -0.10529 | 0.091553 | 1.0345 | 0.032043 | -0.013733 | 0.15564 | 117.8146 | -4.5685 | 4.2572 | -117.6819 | 4.3671 | 4.454 | -116.6748 | -0.20599 | 0.10528 | 0.10986 | 4.3488 | 4.5181 | 5.397 | 4.39 | 4.3671 | 122.1771 | 4.3945 | -0.20599 | 4.39 | 4.3671 | 4.3945 | 5.397 | 122.1771 | -117.8146 | -122.2778
3968.6719 | 122.0352 | -4.248 | 117.8101 | 0.00206 | -0.0014868 | 0.0037043 | 0.063944 | 0.040575 | 0.031742 | 0.097728 | 0.018311 | 0.036621 | -0.1236 | 0.11444 | 1.0483 | 0.07782 | -0.068665 | 0.16937 | 117.9245 | -4.4266 | 4.1245 | -117.7734 | 4.2664 | 4.3625 | -116.7618 | -0.17853 | 0.11444 | 0.14191 | 4.1794 | 4.4174 | 5.2963 | 4.2847 | 4.2664 | 122.1725 | 4.3259 | -0.17853 | 4.2847 | 4.2664 | 4.3259 | 5.2963 | 122.1725 | -117.9337 | -122.2366
3970.4688 | 122.1771 | -4.2572 | 117.746 | 0.00206 | -0.0017004 | 0.0037043 | 0.057108 | 0.040362 | 0.031101 | 0.10157 | 0.009155 | 0.032043 | -0.10529 | 0.10986 | 1.0666 | 0.11444 | -0.14191 | 0.19684 | 117.8833 | -4.4678 | 4.1519 | -117.7139 | 4.2664 | 4.3671 | -116.6794 | -0.21057 | 0.13733 | 0.11444 | 4.1153 | 4.454 | 5.3238 | 4.2892 | 4.2664 | 122.1405 | 4.3716 | -0.21057 | 4.2892 | 4.2664 | 4.3716 | 5.3238 | 122.1405 | -117.8513 | -122.2137
3972.2656 | 122.0535 | -4.0192 | 118.0847 | 0.017319 | -0.00020502 | 0.0086175 | 0.064371 | 0.041857 | 0.028538 | 0.096019 | 0.004578 | 0.018311 | -0.13275 | 0.086975 | 1.0986 | 0.054932 | -0.045776 | 0.12817 | 118.2495 | -4.1794 | 3.8864 | -118.0664 | 4.0237 | 4.1061 | -116.9861 | -0.16022 | 0.16479 | 0.13733 | 3.9734 | 4.1473 | 5.1178 | 4.0375 | 4.0237 | 122.2687 | 4.0741 | -0.16022 | 4.0375 | 4.0237 | 4.0741 | 5.1178 | 122.2687 | -118.2175 | -122.2641
3974 | 122.1817 | -4.0649 | 117.8787 | 0.0096895 | -0.00084602 | 0.0011407 | 0.065225 | 0.04143 | 0.031956 | 0.10008 | -0.045776 | 0.022888 | -0.13733 | 0.041199 | 1.0666 | 0.022888 | -0.050354 | 0.086975 | 118.0939 | -4.3121 | 3.9276 | -117.8558 | 4.0192 | 4.1061 | -116.8121 | -0.24719 | 0.21515 | 0.091553 | 4.0146 | 4.1519 | 5.1315 | 4.0878 | 4.0192 | 122.1588 | 4.0878 | -0.24719 | 4.0878 | 4.0192 | 4.0878 | 5.1315 | 122.1588 | -118.0161 | -122.1909
3975.7969 | 122.0627 | -4.1245 | 117.952 | 0.0096895 | 0.00022218 | 0.0066949 | 0.062021 | 0.038012 | 0.02747 | 0.10286 | -0.032043 | 0.027466 | -0.12817 | 0.10071 | 1.0895 | 0.059509 | -0.036621 | 0.16022 | 118.0573 | -4.3167 | 3.9963 | -117.9245 | 4.0924 | 4.2252 | -116.8625 | -0.19226 | 0.10529 | 0.096131 | 4.0878 | 4.2847 | 5.2139 | 4.1519 | 4.0924 | 122.1817 | 4.184 | -0.19226 | 4.1519 | 4.0924 | 4.184 | 5.2139 | 122.1817 | -118.0801 | -122.2687
3977.6094 | 122.0627 | -4.0558 | 118.0115 | 0.0096895 | 0.00043578 | 0.0054131 | 0.06373 | 0.03908 | 0.031956 | 0.099651 | -0.022888 | 0.041199 | -0.13275 | 0.086975 | 1.0986 | 0.059509 | -0.036621 | 0.16479 | 118.1534 | -4.2572 | 3.923 | -117.9703 | 4.0329 | 4.1428 | -116.9128 | -0.20142 | 0.14191 | 0.10986 | 4.0192 | 4.2206 | 5.1544 | 4.097 | 4.0329 | 122.2092 | 4.1153 | -0.20142 | 4.097 | 4.0329 | 4.1153 | 5.1544 | 122.2092 | -118.1442 | -122.2687
3979.4062 | 122.0215 | -4.0466 | 118.0252 | 0.00206 | -0.0034094 | 0.0030633 | 0.061594 | 0.041216 | 0.030674 | 0.10243 | 0.018311 | 0.018311 | -0.11444 | 0.10986 | 1.1261 | 0.07782 | -0.073242 | 0.19226 | 118.1717 | -4.2114 | 3.9322 | -118.0069 | 4.0649 | 4.1565 | -116.8991 | -0.1648 | 0.14648 | 0.13275 | 3.9734 | 4.2389 | 5.1727 | 4.0649 | 4.0649 | 122.2183 | 4.1245 | -0.1648 | 4.0649 | 4.0649 | 4.1245 | 5.1727 | 122.2183 | -118.1396 | -122.2366
3981.125 | 122.168 | -4.01 | 118.0161 | 0.00206 | -0.0014868 | 0.0011407 | 0.060953 | 0.040575 | 0.031315 | 0.10264 | -0.054932 | 0.050354 | -0.13275 | 0.045776 | 1.0712 | 0.022888 | -0.027466 | 0.07782 | 118.1808 | -4.216 | 3.8773 | -117.9657 | 3.9551 | 4.0558 | -116.9449 | -0.20599 | 0.16479 | 0.077819 | 3.9825 | 4.0878 | 5.0812 | 4.0604 | 3.9551 | 122.1909 | 4.0329 | -0.20599 | 4.0604 | 3.9551 | 4.0329 | 5.0812 | 122.1909 | -118.1488 | -122.2321
3982.9219 | 122.1085 | -3.9322 | 118.1168 | -0.0055695 | 0.00022218 | 0.0071221 | 0.060739 | 0.036089 | 0.033024 | 0.10136 | -0.032043 | 0.041199 | -0.10529 | 0.036621 | 1.1169 | 0.036621 | 0.022888 | 0.13275 | 118.2449 | -4.1245 | 3.8269 | -118.0756 | 3.9001 | 3.9688 | -116.9998 | -0.19226 | 0.12817 | 0.073243 | 3.9551 | 4.0649 | 5.0491 | 3.9734 | 3.9001 | 122.1771 | 3.9688 | -0.19226 | 3.9734 | 3.9001 | 3.9688 | 5.0491 | 122.1771 | -118.222 | -122.2412
3984.6875 | 122.1863 | -3.8269 | 118.1808 | 0.0096895 | -0.0023412 | 0.0037043 | 0.062662 | 0.043566 | 0.030674 | 0.10563 | -0.045776 | 0.041199 | -0.11902 | 0.032043 | 1.0895 | 0.032043 | -0.045776 | 0.10071 | 118.3411 | -4.0558 | 3.7079 | -118.1396 | 3.7811 | 3.8589 | -117.0914 | -0.22888 | 0.16022 | 0.073243 | 3.7811 | 3.9276 | 4.9164 | 3.8681 | 3.7811 | 122.168 | 3.8589 | -0.22888 | 3.8681 | 3.7811 | 3.8589 | 4.9164 | 122.168 | -118.2999 | -122.2366
3986.5 | 122.0718 | -3.9917 | 118.071 | 0.0096895 | 0.00064938 | 0.0043451 | 0.057108 | 0.038012 | 0.030888 | 0.098369 | 0.073242 | 0.018311 | -0.068665 | 0.17853 | 1.3 | 0.17853 | -0.17853 | 0.3067 | 118.1946 | -4.1656 | 3.923 | -118.0527 | 4.0649 | 4.1702 | -116.7709 | -0.17395 | 0.1236 | 0.14191 | 3.8132 | 4.2984 | 5.2917 | 4.01 | 4.0649 | 122.1863 | 4.1702 | -0.17395 | 4.01 | 4.0649 | 4.1702 | 5.2917 | 122.1863 | -118.1396 | -122.2366
3988.2188 | 122.1588 | -3.9047 | 118.103 | 0.0096895 | -0.0017004 | 0.0060541 | 0.064157 | 0.040575 | 0.030461 | 0.10179 | 0.073242 | 0.018311 | -0.050354 | 0.16937 | 1.3184 | 0.16022 | -0.22888 | 0.25177 | 118.2632 | -4.0833 | 3.8544 | -118.0847 | 3.978 | 4.0741 | -116.7847 | -0.17853 | 0.16022 | 0.1236 | 3.6758 | 4.1565 | 5.2231 | 3.923 | 3.978 | 122.168 | 4.0649 | -0.17853 | 3.923 | 3.978 | 4.0649 | 5.2231 | 122.168 | -118.1534 | -122.1863
3990 | 122.081 | -4.1702 | 117.9337 | 0.0096895 | -0.00084602 | 0.0086175 | 0.060739 | 0.038653 | 0.03217 | 0.10777 | 0.07782 | -0.004578 | -0.064087 | 0.19684 | 1.3504 | 0.16937 | -0.17395 | 0.29297 | 117.9977 | -4.335 | 4.1061 | -117.9382 | 4.248 | 4.3671 | -116.5833 | -0.1648 | 0.064087 | 0.14191 | 3.9963 | 4.4632 | 5.5206 | 4.1656 | 4.248 | 122.168 | 4.3396 | -0.1648 | 4.1656 | 4.248 | 4.3396 | 5.5206 | 122.168 | -117.9977 | -122.2687
3991.7031 | 122.0627 | -4.1611 | 117.9108 | 0.0096895 | -0.00020502 | 0.0071221 | 0.064798 | 0.038866 | 0.032597 | 0.10606 | -0.004578 | 0.036621 | -0.09613 | 0.1236 | 1.2497 | 0.064087 | -0.054932 | 0.17853 | 118.0664 | -4.3625 | 4.0649 | -117.8741 | 4.1565 | 4.2847 | -116.6611 | -0.20142 | 0.15564 | 0.091552 | 4.1061 | 4.3396 | 5.4108 | 4.1977 | 4.1565 | 122.2275 | 4.2252 | -0.20142 | 4.1977 | 4.1565 | 4.2252 | 5.4108 | 122.2275 | -118.0069 | -122.2733
3993.4688 | 122.081 | -4.216 | 117.9245 | 0.00206 | -0.0023412 | 0.0041315 | 0.061594 | 0.036944 | 0.034306 | 0.10521 | 0.050354 | 0.004578 | -0.073242 | 0.16022 | 1.3275 | 0.13733 | -0.11444 | 0.24261 | 117.9794 | -4.3625 | 4.1428 | -117.9199 | 4.2664 | 4.3762 | -116.597 | -0.14649 | 0.054931 | 0.1236 | 4.1016 | 4.4586 | 5.5435 | 4.2206 | 4.2664 | 122.1954 | 4.3533 | -0.14649 | 4.2206 | 4.2664 | 4.3533 | 5.5435 | 122.1954 | -117.9977 | -122.287
3995.1719 | 122.1451 | -4.1611 | 117.9062 | 0.0096895 | -0.0027686 | 0.0017817 | 0.061594 | 0.039721 | 0.02982 | 0.10777 | 0.073242 | -0.013733 | -0.050354 | 0.17853 | 1.3138 | 0.16937 | -0.23804 | 0.24719 | 118.0344 | -4.2938 | 4.1107 | -117.9199 | 4.2343 | 4.3396 | -116.5924 | -0.13275 | 0.12817 | 0.1236 | 3.923 | 4.4083 | 5.4749 | 4.1473 | 4.2343 | 122.1954 | 4.3304 | -0.13275 | 4.1473 | 4.2343 | 4.3304 | 5.4749 | 122.1954 | -117.9565 | -122.2
3996.9531 | 122.168 | -4.0237 | 117.9749 | 0.0096895 | 8.578e-06 | 0.0086175 | 0.06373 | 0.039721 | 0.030247 | 0.10734 | 0.018311 | 0.018311 | -0.073242 | 0.13275 | 1.3046 | 0.1236 | -0.20142 | 0.20599 | 118.1168 | -4.2343 | 3.9505 | -117.9565 | 4.0421 | 4.1565 | -116.6702 | -0.21057 | 0.14191 | 0.091553 | 3.8223 | 4.2297 | 5.3284 | 4.0421 | 4.0421 | 122.1405 | 4.1473 | -0.21057 | 4.0421 | 4.0421 | 4.1473 | 5.3284 | 122.1405 | -118.0481 | -122.2092
3998.6719 | 122.168 | -4.1931 | 117.8192 | 0.017319 | -0.0023412 | 0.0019953 | 0.062876 | 0.039721 | 0.031956 | 0.10884 | 0.064087 | -0.009155 | -0.07782 | 0.16479 | 1.3229 | 0.15564 | -0.21973 | 0.23804 | 117.9428 | -4.3671 | 4.1153 | -117.8284 | 4.2572 | 4.3579 | -116.4963 | -0.17395 | 0.1236 | 0.14191 | 3.9734 | 4.4312 | 5.5161 | 4.184 | 4.2572 | 122.1359 | 4.3488 | -0.17395 | 4.184 | 4.2572 | 4.3488 | 5.5161 | 122.1359 | -117.897 | -122.1863
4000.3906 | 122.1039 | -4.1199 | 117.9749 | 0.017319 | -0.0014868 | 0.0056269 | 0.05903 | 0.036944 | 0.033665 | 0.10627 | 0.068665 | -0.018311 | -0.059509 | 0.1831 | 1.3641 | 0.18768 | -0.19226 | 0.30212 | 118.0573 | -4.2709 | 4.0604 | -117.9932 | 4.1885 | 4.303 | -116.6107 | -0.15106 | 0.082397 | 0.12817 | 3.9276 | 4.422 | 5.484 | 4.1016 | 4.1885 | 122.1771 | 4.3076 | -0.15106 | 4.1016 | 4.1885 | 4.3076 | 5.484 | 122.1771 | -118.0344 | -122.2458
4002.1562 | 122.0856 | -4.0512 | 118.0801 | 0.00206 | -0.002555 | 0.0019953 | 0.068857 | 0.036944 | 0.031529 | 0.11845 | 0.07782 | 0.004578 | -0.050354 | 0.18768 | 1.3596 | 0.15564 | -0.15564 | 0.28381 | 118.1717 | -4.1656 | 4.0009 | -118.0756 | 4.129 | 4.2389 | -116.7206 | -0.11444 | 0.091553 | 0.12817 | 3.8956 | 4.335 | 5.4108 | 4.0558 | 4.129 | 122.2229 | 4.2068 | -0.11444 | 4.0558 | 4.129 | 4.2068 | 5.4108 | 122.2229 | -118.1305 | -122.2458
4004.0156 | 122.0627 | -5.983 | 116.1209 | 0.00206 | -0.003623 | 0.0041315 | 0.06843 | 0.036517 | 0.030674 | 0.074657 | -0.013733 | 0.036621 | -0.1236 | 0.12817 | 1.1627 | 0.068665 | -0.073242 | 0.17853 | 116.2354 | -6.1432 | 5.8594 | -116.0843 | 5.9692 | 6.1111 | -114.9582 | -0.16022 | 0.11444 | 0.10986 | 5.9097 | 6.1615 | 7.1457 | 6.0196 | 5.9692 | 122.2183 | 6.0516 | -0.16022 | 6.0196 | 5.9692 | 6.0516 | 7.1457 | 122.2183 | -116.2445 | -122.2641
4005.7188 | 122.1405 | -6.6925 | 115.3473 | 0.00206 | -0.00084602 | 0.0060541 | 0.059885 | 0.037798 | 0.029392 | 0.072521 | -0.013733 | 0.036621 | -0.13275 | 0.082397 | 0.8606 | 0.059509 | -0.11902 | 0.15106 | 115.4984 | -6.8893 | 6.5598 | -115.3107 | 6.6788 | 6.7749 | -114.4867 | -0.19684 | 0.15106 | 0.11902 | 6.5735 | 6.8436 | 7.5531 | 6.7291 | 6.6788 | 122.1909 | 6.752 | -0.19684 | 6.7291 | 6.6788 | 6.752 | 7.5531 | 122.1909 | -115.48 | -122.2366
4007.4219 | 122.1222 | -5.7449 | 116.2903 | 0.017319 | -0.0029822 | 0.0051995 | 0.078897 | 0.039294 | 0.031529 | 0.054576 | 0.068665 | -0.004578 | -0.082397 | 0.16937 | 1.3687 | 0.16937 | -0.24261 | 0.24261 | 116.4322 | -5.9052 | 5.6625 | -116.2949 | 5.8136 | 5.9143 | -114.9216 | -0.16022 | 0.14191 | 0.15106 | 5.5023 | 5.9875 | 7.1136 | 5.7404 | 5.8136 | 122.1771 | 5.9143 | -0.16022 | 5.7404 | 5.8136 | 5.9143 | 7.1136 | 122.1771 | -116.3727 | -122.1954
4009.1406 | 121.3943 | -4.248 | 117.8833 | 0.0096895 | -0.004264 | 0.0071221 | 0.06138 | 0.039507 | 0.030461 | 0.055644 | 0.022888 | 0.013733 | -0.10071 | 0.1236 | 1.1398 | 0.064087 | -0.07782 | 0.17853 | 118.0252 | -4.3854 | 4.1473 | -117.8696 | 4.2709 | 4.3716 | -116.7435 | -0.13733 | 0.14191 | 0.1236 | 4.1702 | 4.4266 | 5.3879 | 4.2618 | 4.2709 | 122.2733 | 4.3121 | -0.13733 | 4.2618 | 4.2709 | 4.3121 | 5.3879 | 122.2733 | -117.984 | -122.2687
4010.8594 | 121.7056 | -5.0583 | 117.0639 | 0.0096895 | -0.00063242 | 0.0058405 | 0.054544 | 0.036517 | 0.035587 | 0.050518 | 0.064087 | 0.004578 | -0.064087 | 0.19226 | 1.3092 | 0.17853 | -0.19684 | 0.28839 | 117.1143 | -5.2139 | 4.9942 | -117.0593 | 5.1224 | 5.2506 | -115.7547 | -0.15564 | 0.050354 | 0.12817 | 4.8615 | 5.3467 | 6.3675 | 5.0629 | 5.1224 | 122.1725 | 5.2368 | -0.15564 | 5.0629 | 5.1224 | 5.2368 | 6.3675 | 122.1725 | -117.128 | -122.2778
4012.5781 | 121.5775 | -6.514 | 115.6265 | 0.0096895 | -0.0034094 | 0.0069085 | 0.062021 | 0.036944 | 0.029392 | 0.064617 | 0.004578 | 0.018311 | -0.12817 | 0.12817 | 1.1124 | 0.086975 | -0.07782 | 0.1831 | 114.4959 | -7.8827 | 6.3858 | -115.6082 | 6.5186 | 6.6422 | -114.5142 | -1.3687 | -1.1307 | 0.13275 | 6.4362 | 6.6971 | 7.6263 | 6.5323 | 6.5186 | 121.0098 | 6.601 | -1.3687 | 6.5323 | 6.5186 | 6.601 | 7.6263 | 121.0098 | -115.7547 | -123.5092
4014.2969 | 122.1451 | -4.2297 | 117.8421 | 0.00206 | 0.00022218 | 0.0066949 | 0.067362 | 0.040362 | 0.031742 | 0.054363 | 0.068665 | 0.013733 | -0.07782 | 0.16022 | 1.2085 | 0.16479 | -0.23346 | 0.22888 | 117.9016 | -4.4403 | 4.1519 | -117.8284 | 4.2984 | 4.39 | -116.6336 | -0.21057 | 0.059509 | 0.14649 | 3.9963 | 4.4586 | 5.4382 | 4.2435 | 4.2984 | 122.1313 | 4.3945 | -0.21057 | 4.2435 | 4.2984 | 4.3945 | 5.4382 | 122.1313 | -117.9199 | -122.2824
4016.0156 | 122.0764 | -4.7562 | 117.3706 | 0.0096895 | -0.0023412 | 0.0060541 | 0.086801 | 0.037798 | 0.032597 | 0.052013 | 0.045776 | 0.004578 | -0.059509 | 0.17853 | 1.3687 | 0.13275 | -0.14191 | 0.27008 | 117.7048 | -4.6463 | 4.6967 | -117.366 | 4.8019 | 4.9347 | -116.0019 | 0.10986 | 0.33417 | 0.10528 | 4.6143 | 5.0262 | 6.1249 | 4.7607 | 4.8019 | 122.4609 | 4.8889 | 0.10986 | 4.7607 | 4.8019 | 4.8889 | 6.1249 | 122.4609 | -117.4301 | -122.0169
4017.7188 | 122.1817 | -4.8294 | 117.1509 | 0.00206 | -0.0014868 | 0.0022089 | 0.066507 | 0.03908 | 0.032383 | 0.070598 | 0.027466 | -0.004578 | -0.082397 | 0.14191 | 1.0117 | 0.10071 | -0.17395 | 0.21515 | 117.3569 | -5.0171 | 4.747 | -117.1555 | 4.8569 | 4.9713 | -116.1392 | -0.18768 | 0.20599 | 0.10986 | 4.6555 | 5.0446 | 5.8411 | 4.8248 | 4.8569 | 122.1863 | 4.9301 | -0.18768 | 4.8248 | 4.8569 | 4.9301 | 5.8411 | 122.1863 | -117.2333 | -122.168
4019.4844 | 121.7789 | -4.303 | 117.5446 | 0.0096895 | -0.001914 | 0.0032769 | 0.06373 | 0.039507 | 0.030888 | 0.048381 | -0.004578 | 0.036621 | -0.09613 | 0.11444 | 1.5106 | 0.068665 | -0.07782 | 0.18768 | 117.9794 | -4.4586 | 4.2068 | -117.5079 | 4.2984 | 4.4174 | -116.0339 | -0.15564 | 0.43488 | 0.091552 | 4.2252 | 4.4907 | 5.8136 | 4.3396 | 4.2984 | 122.2824 | 4.3716 | -0.15564 | 4.3396 | 4.2984 | 4.3716 | 5.8136 | 122.2824 | -117.6407 | -122.0032
4021.1875 | 122.0993 | -4.628 | 117.54 | 0.0096895 | -0.0014868 | 0.0015679 | 0.13273 | 0.038439 | 0.029392 | 0.05949 | -0.022888 | 0.036621 | -0.10529 | 0.091553 | 1.1673 | 0.050354 | -0.036621 | 0.16937 | 117.4988 | -4.8981 | 4.5227 | -117.5034 | 4.6051 | 4.7195 | -116.3727 | -0.27008 | -0.041199 | 0.082398 | 4.5914 | 4.7974 | 5.7953 | 4.6646 | 4.6051 | 122.1268 | 4.6783 | -0.27008 | 4.6646 | 4.6051 | 4.6783 | 5.7953 | 122.1268 | -117.6453 | -122.438
4022.9688 | 121.701 | -3.0167 | 119.1696 | 0.017319 | -0.0031958 | 0.0026361 | 0.069712 | 0.03673 | 0.03217 | 0.048168 | 0.064087 | 0.009155 | -0.050354 | 0.1831 | 1.4465 | 0.15564 | -0.16937 | 0.2655 | 119.22 | -3.1174 | 2.9663 | -119.1605 | 3.0808 | 3.1998 | -117.7231 | -0.10071 | 0.050354 | 0.11444 | 2.8473 | 3.2822 | 4.4632 | 3.0258 | 3.0808 | 122.2366 | 3.1723 | -0.10071 | 3.0258 | 3.0808 | 3.1723 | 4.4632 | 122.2366 | -119.22 | -122.287
4024.6875 | 122.1268 | -4.9026 | 117.1967 | 0.00206 | -0.0029822 | 0.0030633 | 0.07377 | 0.037371 | 0.034092 | 0.060131 | 0.059509 | -0.013733 | -0.054932 | 0.16937 | 1.3321 | 0.14191 | -0.16937 | 0.26093 | 117.3248 | -5.0491 | 4.8477 | -117.2104 | 4.9622 | 5.072 | -115.8646 | -0.14648 | 0.12817 | 0.11444 | 4.7333 | 5.1636 | 6.2347 | 4.8889 | 4.9622 | 122.2275 | 5.0446 | -0.14648 | 4.8889 | 4.9622 | 5.0446 | 6.2347 | 122.2275 | -117.2516 | -122.2458
4026.4531 | 122.168 | -4.0237 | 118.0573 | 0.00206 | -0.0031958 | 0.0060541 | 0.082956 | 0.040148 | 0.032383 | 0.073589 | 0.064087 | 0.004578 | -0.022888 | 0.17853 | 1.1444 | 0.16937 | -0.21973 | 0.2243 | 117.9153 | -4.3716 | 4.0009 | -118.0527 | 4.0878 | 4.2023 | -116.9128 | -0.3479 | -0.14191 | 0.086975 | 3.804 | 4.248 | 5.1682 | 4.0283 | 4.0878 | 121.9391 | 4.1931 | -0.3479 | 4.0283 | 4.0878 | 4.1931 | 5.1682 | 121.9391 | -118.0801 | -122.4289
4028.1562 | 122.287 | -3.7308 | 118.309 | 0.0096895 | -0.0014868 | 0.0028497 | 0.098551 | 0.037371 | 0.032383 | 0.069744 | 0.032043 | 0.018311 | -0.041199 | 0.10529 | 1.1032 | 0.11902 | -0.14648 | 0.19226 | 118.4921 | -3.8818 | 3.6896 | -118.2907 | 3.7628 | 3.8361 | -117.2058 | -0.15106 | 0.1831 | 0.073242 | 3.5843 | 3.923 | 4.834 | 3.7491 | 3.7628 | 122.2229 | 3.8498 | -0.15106 | 3.7491 | 3.7628 | 3.8498 | 4.834 | 122.2229 | -118.3502 | -122.1909
4029.875 | 121.3165 | -120.9869 | 0.10986 | 0.0096895 | -0.0014868 | 0.0058405 | 1.128 | -0.021802 | -0.027004 | 1.0449 | 0.091553 | 0.018311 | -0.10071 | 0.19226 | -10.7117 | 0.1831 | -0.18768 | 0.29297 | 0.33875 | -120.6848 | 120.8862 | -0.091552 | 121.0785 | 121.1792 | -10.8215 | 0.30212 | 0.22888 | 0.19226 | 120.7993 | 121.2799 | 110.2753 | 121.0052 | 121.0785 | 121.3257 | 121.17 | 0.30212 | 121.0052 | 121.0785 | 121.17 | 110.2753 | 121.3257 | -0.21057 | -120.7947
4031.5781 | 121.3303 | -120.1904 | 1.1261 | 0.00206 | -0.0010596 | -0.0003547 | 4.0087 | -0.027143 | -0.014187 | 3.997 | -0.004578 | 0.004578 | -0.18768 | 0.13275 | -30.4733 | 0.11444 | 0 | 0.2243 | 0.85144 | -120.1172 | 120.0027 | -1.1215 | 120.1859 | 120.3232 | -31.5994 | 0.073243 | -0.27466 | 0.1831 | 120.1904 | 120.4147 | 89.7171 | 120.195 | 120.1859 | 121.0419 | 120.3049 | 0.073243 | 120.195 | 120.1859 | 120.3049 | 89.7171 | 121.0419 | -1.3138 | -121.2433
4033.2969 | 121.3852 | -6.3995 | 114.2578 | 0.017319 | -0.00084602 | 0.0045587 | 0.052194 | 0.041003 | 0.03281 | 0.19471 | 0 | 0.018311 | -0.14648 | 0.10529 | 0.85144 | 0.073242 | -0.16022 | -3.6072 | 114.8254 | -6.7062 | 6.2531 | -114.2395 | 6.3995 | 6.5048 | -113.4064 | -0.3067 | 0.56763 | 0.14648 | 6.2393 | 2.7924 | 7.251 | 6.4178 | 6.3995 | 121.225 | 6.4728 | -0.3067 | 6.4178 | 6.3995 | 6.4728 | 7.251 | 121.225 | -114.4043 | -120.9641
4035.0156 | 121.2479 | -8.6517 | 105.8533 | 0.017319 | -0.002555 | 0.0039179 | 0.063944 | 0.037371 | 0.029179 | 0.19429 | 0.009155 | 0.041199 | -0.12817 | 0.11444 | 0.8194 | 0.07782 | -0.07782 | -5.9509 | 112.7747 | -8.757 | 8.5236 | -105.8121 | 8.6609 | 8.7662 | -105.0339 | -0.10529 | 6.9214 | 0.13733 | 8.5739 | 2.7008 | 9.4711 | 8.6929 | 8.6609 | 121.4264 | 8.7296 | -0.10529 | 8.6929 | 8.6609 | 8.7296 | 9.4711 | 121.4264 | -105.9814 | -114.6103
4036.7656 | 121.1151 | -8.8852 | 112.1613 | 0.0096895 | -0.0017004 | 0.0060541 | 0.04899 | 0.034594 | 0.03281 | 0.19407 | 0.022888 | 0.018311 | -0.09613 | 0.15564 | 0.82855 | 0.14648 | -0.15564 | -6.6238 | 112.5549 | -9.1278 | 8.7891 | -112.1429 | 8.9081 | 9.0408 | -111.3327 | -0.24262 | 0.39368 | 0.11902 | 8.7296 | 2.2614 | 9.7137 | 8.9035 | 8.9081 | 121.4401 | 9.0317 | -0.24262 | 8.9035 | 8.9081 | 9.0317 | 9.7137 | 121.4401 | -112.2574 | -121.2891
4038.4844 | 121.3486 | -6.5277 | 114.473 | 0.0096895 | -0.002555 | 0.0013543 | 0.060098 | 0.035235 | 0.032383 | 0.20582 | 0.027466 | 0.018311 | -0.10986 | 0.15564 | 0.75531 | 0.15106 | -0.16937 | -4.3121 | 114.9765 | -6.7383 | 6.4178 | -114.4547 | 6.5552 | 6.6833 | -113.7177 | -0.21057 | 0.50354 | 0.13733 | 6.3583 | 2.2156 | 7.283 | 6.546 | 6.5552 | 121.5042 | 6.6788 | -0.21057 | 6.546 | 6.5552 | 6.6788 | 7.283 | 121.5042 | -114.5828 | -121.2112
4040.2031 | 121.7514 | -107.9269 | 13.3255 | 0.0096895 | -0.0027686 | 0.0051995 | 0.12119 | -0.021589 | -0.020809 | 0.074443 | 0.07782 | 0.027466 | -0.09613 | 0.1831 | -0.15106 | 0.18768 | -0.13733 | -106.8924 | 13.4399 | -108.2565 | 107.8308 | -13.298 | 108.0048 | 108.11 | -13.4766 | -0.32959 | 0.11444 | 0.17395 | 107.7896 | 1.0345 | 107.7759 | 107.9544 | 108.0048 | 121.3669 | 108.1146 | -0.32959 | 107.9544 | 108.0048 | 108.1146 | 107.7759 | 121.3669 | -13.4216 | -121.582
4041.9688 | 121.3394 | -42.3431 | 78.9917 | 0.024948 | -0.00084602 | 0.0022089 | 0.058389 | 0.017504 | 0.010807 | 0.12977 | -0.022888 | 0.064087 | -0.13733 | 0.12817 | -0.4715 | 0.050354 | -0.13275 | -40.2283 | 75.5722 | -45.1172 | 42.2058 | -78.9276 | 42.3203 | 42.4713 | -79.4632 | -2.774 | -3.4195 | 0.11444 | 42.2104 | 2.1149 | 41.8716 | 42.4072 | 42.3203 | 117.9153 | 42.3935 | -2.774 | 42.4072 | 42.3203 | 42.3935 | 41.8716 | 117.9153 | -79.129 | -124.1089
4043.7188 | 121.3943 | -22.0184 | 99.4583 | 0.017319 | -0.0038366 | 0.0045587 | 0.054331 | 0.026904 | 0.024479 | 0.16673 | 0.082397 | 0.009155 | -0.11444 | 0.16937 | -0.19226 | 0.16479 | -0.22888 | -20.4025 | 99.5132 | -22.1741 | 21.904 | -99.4492 | 22.1008 | 22.1878 | -99.6506 | -0.15564 | 0.054932 | 0.19684 | 21.7896 | 1.6159 | 21.8262 | 22.0276 | 22.1008 | 121.5317 | 22.1832 | -0.15564 | 22.0276 | 22.1008 | 22.1832 | 21.8262 | 121.5317 | -99.5728 | -121.6324
4045.4375 | 121.1655 | -13.9755 | 107.1716 | 0.00206 | -0.0027686 | 0.0045587 | 0.050485 | 0.032885 | 0.029179 | 0.17997 | 0.022888 | 0.022888 | -0.1236 | 0.16022 | -0.17853 | 0.13733 | -0.16937 | -12.7121 | 107.634 | -14.1495 | 13.8519 | -107.1487 | 13.9984 | 14.1357 | -107.3502 | -0.17395 | 0.46234 | 0.14648 | 13.8062 | 1.2634 | 13.797 | 13.9984 | 13.9984 | 121.6095 | 14.1129 | -0.17395 | 13.9984 | 13.9984 | 14.1129 | 13.797 | 121.6095 | -107.2952 | -121.3211
4047.1562 | 120.8908 | -7.8369 | 113.0173 | 0.0096895 | -0.00041862 | 0.0081903 | 0.053263 | 0.034594 | 0.030247 | 0.1945 | 0.073242 | -0.013733 | -0.10986 | 0.17853 | 0.2243 | 0.15564 | -0.17395 | -5.4932 | 113.6719 | -8.1528 | 7.7271 | -113.031 | 7.9102 | 8.0154 | -112.793 | -0.31586 | 0.6546 | 0.18311 | 7.663 | 2.3438 | 8.0612 | 7.8232 | 7.9102 | 121.5088 | 7.9926 | -0.31586 | 7.8232 | 7.9102 | 7.9926 | 8.0612 | 121.5088 | -113.1271 | -121.17
4048.9219 | 98.8861 | -8.0933 | 113.5437 | 0.017319 | -0.00041862 | 0.0054131 | 0.057962 | 0.03438 | 0.031101 | 0.20048 | -0.036621 | 0.073242 | -0.15564 | 0.082397 | 0.16937 | 0.009155 | 0.009155 | -6.3492 | 113.6124 | -8.3221 | 7.9376 | -113.4705 | 8.0566 | 8.1757 | -113.3743 | -0.22888 | 0.068665 | 0.11902 | 8.1024 | 1.7441 | 8.2626 | 8.1665 | 8.0566 | 121.7056 | 8.1024 | -0.22888 | 8.1665 | 8.0566 | 8.1024 | 8.2626 | 121.7056 | -113.6993 | -121.8658
4050.6406 | 100.0397 | -21.1533 | 74.5056 | 0.0096895 | -0.002555 | 0.0002863 | 0.056253 | 0.027544 | 0.018711 | 0.17378 | -0.004578 | 0.018311 | -0.16479 | 0.12817 | -0.21057 | 0.073242 | -0.041199 | -19.4366 | 100.9644 | -20.8374 | 20.9885 | -74.4873 | 21.1487 | 21.2814 | -74.7162 | 0.31586 | 26.4587 | 0.16022 | 21.1121 | 1.7166 | 20.9427 | 21.1716 | 21.1487 | 122.1176 | 21.2265 | 0.31586 | 21.1716 | 21.1487 | 21.2265 | 20.9427 | 122.1176 | -74.6704 | -95.343
4052.3594 | 121.1014 | -16.8961 | 103.8483 | 0.017319 | -0.0027686 | 0.0037043 | 0.052622 | 0.028613 | 0.027256 | 0.18339 | 0.022888 | 0.018311 | -0.12817 | 0.15106 | -0.16022 | 0.14191 | -0.15106 | -15.5319 | 104.6402 | -17.1753 | 16.7679 | -103.83 | 16.9189 | 17.0471 | -104.0085 | -0.27924 | 0.79193 | 0.15106 | 16.745 | 1.3641 | 16.7358 | 16.9144 | 16.9189 | 121.5363 | 17.038 | -0.27924 | 16.9144 | 16.9189 | 17.038 | 16.7358 | 121.5363 | -103.9764 | -121.0236
4054.0781 | 111.3235 | -15.9668 | 100.5066 | 0.0096895 | -0.0023412 | 0.0081903 | 0.07847 | 0.030322 | 0.024479 | 0.20454 | 0.013733 | 0.050354 | -0.17395 | 0.14191 | -0.19226 | 0.082397 | -0.091553 | -14.4196 | 105.7617 | -16.1041 | 15.7928 | -100.4562 | 15.9805 | 16.1087 | -100.6989 | -0.13733 | 5.2551 | 0.18768 | 15.8752 | 1.5472 | 15.7745 | 16.0172 | 15.9805 | 121.7285 | 16.0492 | -0.13733 | 16.0172 | 15.9805 | 16.0492 | 15.7745 | 121.7285 | -100.6805 | -116.6107
4055.7812 | 121.0098 | -14.1357 | 106.3477 | 0.017319 | -0.00041862 | 0.0062677 | 0.072275 | 0.033099 | 0.024052 | 0.20689 | -0.050354 | 0.045776 | -0.16022 | 0.054932 | -0.2655 | 0.018311 | -0.045776 | -13.1424 | 107.309 | -14.6072 | 13.9755 | -106.3019 | 14.0854 | 14.1907 | -106.6132 | -0.4715 | 0.9613 | 0.10986 | 14.09 | 0.99335 | 13.8702 | 14.1815 | 14.0854 | 121.4447 | 14.1541 | -0.4715 | 14.1815 | 14.0854 | 14.1541 | 13.8702 | 121.4447 | -106.5079 | -120.9549
4057.4844 | 121.907 | -87.6801 | 33.7234 | -0.0055695 | -0.0010596 | 0.0092585 | 0.80906 | -0.0081305 | -0.0144 | 0.78282 | -0.009155 | 0.036621 | -0.17395 | 0.11444 | -2.2705 | 0.11902 | -0.11902 | -86.8515 | 29.7134 | -91.8823 | 87.5061 | -33.6868 | 87.6709 | 87.7945 | -35.994 | -4.2023 | -4.01 | 0.16479 | 87.561 | 0.82855 | 85.4095 | 87.7167 | 87.6709 | 117.3935 | 87.7991 | -4.2023 | 87.7167 | 87.6709 | 87.7991 | 85.4095 | 117.3935 | -33.8974 | -125.6058
4059.1875 | 121.8338 | -59.9808 | 61.4731 | 0.0096895 | -0.0017004 | 0.0051995 | 0.058389 | 0.0070367 | 0.0063212 | 0.1082 | 0.032043 | 0.009155 | -0.10071 | 0.11902 | -0.009155 | 0.14191 | -0.13733 | -54.4235 | 65.4053 | -55.513 | 59.8801 | -61.4639 | 60.0128 | 60.0998 | -61.4822 | 4.4678 | 3.9322 | 0.13275 | 59.8434 | 5.5573 | 59.9716 | 59.9899 | 60.0128 | 125.386 | 60.1227 | 4.4678 | 59.9899 | 60.0128 | 60.1227 | 59.9716 | 125.386 | -61.5738 | -116.9861
4060.8906 | 112.6923 | -9.343 | 86.2152 | 0.00206 | -0.0017004 | 0.0043451 | 0.067789 | 0.033953 | 0.028324 | 0.20732 | -0.054932 | 0.054932 | -0.17853 | 0.068665 | -0.22888 | 0.027466 | 0.018311 | -8.7387 | 112.0834 | -9.8923 | 9.1644 | -86.1603 | 9.288 | 9.4116 | -86.4441 | -0.54932 | 25.8682 | 0.1236 | 9.3613 | 0.60425 | 9.1141 | 9.3979 | 9.288 | 121.4264 | 9.3704 | -0.54932 | 9.3979 | 9.288 | 9.3704 | 9.1141 | 121.4264 | -86.3937 | -96.1075
4062.625 | 121.8292 | -9.2239 | 111.5524 | 0.0096895 | 0.0019312 | 0.0047723 | 0.076975 | 0.037157 | 0.030033 | 0.20539 | -0.027466 | 0.036621 | -0.14648 | 0.050354 | -0.22888 | 0.036621 | -0.068665 | -8.2764 | 112.5229 | -9.462 | 9.0775 | -111.5158 | 9.1965 | 9.2743 | -111.7813 | -0.23804 | 0.97046 | 0.11902 | 9.1553 | 0.94757 | 8.9951 | 9.2606 | 9.1965 | 121.7468 | 9.2606 | -0.23804 | 9.2606 | 9.1965 | 9.2606 | 8.9951 | 121.7468 | -111.6989 | -121.0144
4064.3281 | 121.431 | -11.5997 | 109.845 | 0.0096895 | -0.00084602 | 0.0060541 | 0.062662 | 0.033953 | 0.028538 | 0.20176 | 0.082397 | 0.004578 | -0.10529 | 0.17395 | -0.11902 | 0.17395 | -0.24261 | -10.4599 | 110.1562 | -11.7096 | 11.4944 | -109.8404 | 11.6821 | 11.7737 | -109.964 | -0.10986 | 0.31128 | 0.18768 | 11.3571 | 1.1398 | 11.4807 | 11.6043 | 11.6821 | 121.756 | 11.7737 | -0.10986 | 11.6043 | 11.6821 | 11.7737 | 11.4807 | 121.756 | -109.9503 | -121.5546
4066.0469 | 121.3577 | -10.0113 | 110.9253 | 0.017319 | 0.00022218 | 0.0084039 | 0.06138 | 0.035876 | 0.030461 | 0.20411 | 0.064087 | -0.013733 | -0.11902 | 0.13733 | -0.1236 | 0.14191 | -0.17853 | -9.3109 | 111.6989 | -10.2081 | 9.8923 | -110.939 | 10.0754 | 10.1486 | -111.0489 | -0.19684 | 0.77362 | 0.18311 | 9.8328 | 0.70038 | 9.8877 | 9.9976 | 10.0754 | 121.7102 | 10.1532 | -0.19684 | 9.9976 | 10.0754 | 10.1532 | 9.8877 | 121.7102 | -111.0443 | -121.1334
4067.75 | 121.8613 | -8.8806 | 111.9736 | 0.00206 | -0.0031958 | 0.0047723 | 0.052194 | 0.03438 | 0.031742 | 0.19984 | 0.050354 | 0.009155 | -0.11902 | 0.14648 | -0.1236 | 0.13275 | -0.1831 | -8.1299 | 112.8296 | -9.0866 | 8.7616 | -111.9644 | 8.931 | 9.0271 | -112.0972 | -0.20599 | 0.85602 | 0.16937 | 8.6975 | 0.75073 | 8.757 | 8.8898 | 8.931 | 121.7102 | 9.0134 | -0.20599 | 8.8898 | 8.931 | 9.0134 | 8.757 | 121.7102 | -112.0926 | -121.0602
4069.4531 | 121.0556 | -10.5377 | 111.1496 | 0.0096895 | -0.0014868 | 0.0045587 | 0.050485 | 0.034594 | 0.031101 | 0.19386 | 0.013733 | 0.004578 | -0.13733 | 0.13733 | -0.12817 | 0.11902 | -0.15106 | -9.8373 | 111.1633 | -10.7666 | 10.4004 | -111.145 | 10.5515 | 10.675 | -111.2778 | -0.22888 | 0.013733 | 0.15106 | 10.3867 | 0.70038 | 10.4095 | 10.5423 | 10.5515 | 121.7011 | 10.6567 | -0.22888 | 10.5423 | 10.5515 | 10.6567 | 10.4095 | 121.7011 | -111.2869 | -121.9162
4071.1562 | 101.3535 | -9.407 | 92.157 | 0.0096895 | -0.0051184 | 0.0045587 | 0.054758 | 0.035876 | 0.030033 | 0.19386 | 0.064087 | 0.004578 | -0.11902 | 0.19226 | -0.082397 | 0.15106 | -0.14648 | -8.8303 | 112.1155 | -9.8236 | 9.288 | -92.1524 | 9.4711 | 9.5993 | -92.2394 | -0.41657 | 19.9585 | 0.18311 | 9.2606 | 0.57678 | 9.3246 | 9.4116 | 9.4711 | 121.5225 | 9.5581 | -0.41657 | 9.4116 | 9.4711 | 9.5581 | 9.3246 | 121.5225 | -92.276 | -101.9806
4072.8906 | 121.4264 | -10.2219 | 110.8704 | -0.0055695 | -0.0014868 | 0.0064813 | 0.054758 | 0.033312 | 0.028538 | 0.19471 | 0.050354 | 0 | -0.11902 | 0.15564 | -0.11902 | 0.13275 | -0.21515 | -9.462 | 111.5158 | -10.4187 | 10.1028 | -110.8704 | 10.2722 | 10.3775 | -110.9894 | -0.19684 | 0.64545 | 0.16937 | 10.0067 | 0.75989 | 10.1028 | 10.2219 | 10.2722 | 121.7377 | 10.3546 | -0.19684 | 10.2219 | 10.2722 | 10.3546 | 10.1028 | 121.7377 | -110.9894 | -121.2891
4074.6562 | 121.4813 | -9.9426 | 111.0489 | 0.0096895 | -0.0017004 | 0.0077631 | 0.057535 | 0.036089 | 0.029179 | 0.19664 | 0.068665 | 0 | -0.1236 | 0.1831 | -0.11902 | 0.16937 | -0.2243 | -9.1553 | 111.8271 | -10.1028 | 9.819 | -111.0489 | 10.0113 | 10.1257 | -111.1679 | -0.16022 | 0.7782 | 0.19226 | 9.7183 | 0.78735 | 9.8236 | 9.9426 | 10.0113 | 121.7697 | 10.112 | -0.16022 | 9.9426 | 10.0113 | 10.112 | 9.8236 | 121.7697 | -111.1725 | -121.1517
4076.375 | 121.257 | -10.6339 | 110.5362 | 0.0096895 | 0.0010766 | 0.0075495 | 0.058389 | 0.03438 | 0.030461 | 0.19471 | 0.004578 | 0.018311 | -0.1236 | 0.12817 | -0.16937 | 0.11444 | -0.16022 | -9.9426 | 111.0901 | -10.8673 | 10.5103 | -110.5179 | 10.6384 | 10.762 | -110.7056 | -0.23346 | 0.55389 | 0.12817 | 10.4736 | 0.69122 | 10.4645 | 10.6522 | 10.6384 | 121.7239 | 10.7483 | -0.23346 | 10.6522 | 10.6384 | 10.7483 | 10.4645 | 121.7239 | -110.6598 | -121.4035
4078.0781 | 121.4401 | -10.2219 | 111.3052 | 0.0096895 | -0.0029822 | 0.0024225 | 0.05369 | 0.034808 | 0.030033 | 0.19664 | 0.027466 | 0.013733 | -0.12817 | 0.1236 | -0.13733 | 0.12817 | -0.17395 | -9.4025 | 111.5616 | -10.405 | 10.0937 | -111.2915 | 10.2493 | 10.3455 | -111.4426 | -0.1831 | 0.25635 | 0.15564 | 10.0479 | 0.8194 | 10.0845 | 10.2356 | 10.2493 | 121.7834 | 10.35 | -0.1831 | 10.2356 | 10.2493 | 10.35 | 10.0845 | 121.7834 | -111.4334 | -121.7102
4079.7812 | 121.4264 | -9.9884 | 111.5433 | 0.0096895 | -0.002555 | 0.0075495 | 0.057749 | 0.036517 | 0.028111 | 0.1977 | 0.050354 | 0 | -0.11902 | 0.1831 | -0.1236 | 0.15564 | -0.23804 | -9.1965 | 111.7996 | -10.1669 | 9.8694 | -111.5433 | 10.0388 | 10.1715 | -111.6669 | -0.17853 | 0.25635 | 0.16937 | 9.7504 | 0.79193 | 9.8648 | 9.9884 | 10.0388 | 121.788 | 10.144 | -0.17853 | 9.9884 | 10.0388 | 10.144 | 9.8648 | 121.788 | -111.6623 | -121.7102
4081.4844 | 121.1792 | -7.7408 | 112.9532 | 0.00206 | -0.0012732 | 0.0058405 | 0.057535 | 0.036089 | 0.031956 | 0.20219 | -0.045776 | 0.041199 | -0.16937 | 0.054932 | -0.20599 | 0.027466 | -0.059509 | -7.3105 | 113.9328 | -8.1161 | 7.5714 | -112.912 | 7.695 | 7.7957 | -113.1592 | -0.37537 | 0.97961 | 0.1236 | 7.6813 | 0.4303 | 7.5348 | 7.782 | 7.695 | 121.6736 | 7.7683 | -0.37537 | 7.782 | 7.695 | 7.7683 | 7.5348 | 121.6736 | -113.1226 | -121.0693
4083.2031 | 121.1746 | -7.7591 | 113.2233 | 0.017319 | -0.00063242 | 0.0088311 | 0.057108 | 0.035876 | 0.031529 | 0.20198 | -0.036621 | 0.054932 | -0.16479 | 0.050354 | -0.21515 | 0.041199 | -0.059509 | -7.2418 | 113.9648 | -8.0704 | 7.5943 | -113.1683 | 7.7225 | 7.8094 | -113.4384 | -0.31128 | 0.74158 | 0.12817 | 7.6996 | 0.51727 | 7.5439 | 7.814 | 7.7225 | 121.7239 | 7.8003 | -0.31128 | 7.814 | 7.7225 | 7.8003 | 7.5439 | 121.7239 | -113.3881 | -121.2936
4084.9688 | 104.4525 | -7.6813 | 113.0676 | 0.017319 | -0.003623 | 0.0086175 | 0.053049 | 0.032885 | 0.030033 | 0.20091 | 0.054932 | 0.018311 | -0.14648 | 0.16479 | -0.10529 | 0.14191 | -0.11444 | -7.1045 | 113.8275 | -8.1161 | 7.5348 | -113.0493 | 7.7362 | 7.8461 | -113.1729 | -0.43488 | 0.75989 | 0.20142 | 7.5668 | 0.57678 | 7.576 | 7.6996 | 7.7362 | 121.5088 | 7.8232 | -0.43488 | 7.6996 | 7.7362 | 7.8232 | 7.576 | 121.5088 | -113.2141 | -121.1838
4086.6719 | 92.1661 | -8.194 | 86.3892 | 0.0096895 | 0.00043578 | 0.0015679 | 0.057321 | 0.037371 | 0.029606 | 0.20411 | -0.036621 | 0.036621 | -0.15106 | 0.054932 | -0.19684 | 0.027466 | 0.027466 | -7.2372 | 113.8687 | -8.1757 | 8.0429 | -86.3525 | 8.1573 | 8.2489 | -86.586 | 0.018311 | 27.4796 | 0.11444 | 8.2214 | 0.95673 | 7.9971 | 8.2306 | 8.1573 | 122.0627 | 8.2214 | 0.018311 | 8.2306 | 8.1573 | 8.2214 | 7.9971 | 122.0627 | -86.5402 | -94.5648
4088.4062 | 103.5507 | -7.9147 | 97.0413 | 0.0096895 | -0.00041862 | 0.0088311 | 0.058176 | 0.038226 | 0.02747 | 0.20069 | 0.004578 | 0.027466 | -0.16937 | 0.12817 | -0.15106 | 0.07782 | -0.07782 | -7.3883 | 113.6719 | -8.3542 | 7.7454 | -97.0139 | 7.9193 | 8.0429 | -97.1924 | -0.43945 | 16.6306 | 0.17395 | 7.8369 | 0.52643 | 7.7637 | 7.9422 | 7.9193 | 121.5866 | 7.9926 | -0.43945 | 7.9422 | 7.9193 | 7.9926 | 7.7637 | 121.5866 | -97.2107 | -105.3955
4090.1094 | 110.8475 | -7.9834 | 113.5345 | 0.0096895 | -0.0034094 | 0.0064813 | 0.057535 | 0.038226 | 0.028752 | 0.20048 | 0.013733 | 0.036621 | -0.15564 | 0.11444 | -0.17853 | 0.07782 | -0.073242 | -7.3471 | 113.7588 | -8.3267 | 7.8278 | -113.4979 | 7.9971 | 8.0978 | -113.7131 | -0.34332 | 0.2243 | 0.16937 | 7.9102 | 0.63629 | 7.8049 | 8.02 | 7.9971 | 121.7422 | 8.0612 | -0.34332 | 8.02 | 7.9971 | 8.0612 | 7.8049 | 121.7422 | -113.6902 | -121.8613
4091.8438 | 121.4996 | -8.5464 | 112.5458 | 0.00206 | -0.00063242 | 0.0039179 | 0.04899 | 0.036089 | 0.031742 | 0.20134 | 0.041199 | -0.004578 | -0.11902 | 0.12817 | -0.086975 | 0.13733 | -0.17853 | -7.869 | 113.2782 | -8.7204 | 8.4274 | -112.5504 | 8.5876 | 8.6746 | -112.6328 | -0.17395 | 0.73242 | 0.16022 | 8.3679 | 0.67749 | 8.4595 | 8.5419 | 8.5876 | 121.8246 | 8.6838 | -0.17395 | 8.5419 | 8.5876 | 8.6838 | 8.4595 | 121.8246 | -112.6648 | -121.2662
4093.5625 | 104.6265 | -8.844 | 94.1071 | 0.00206 | -0.0027686 | 0.0086175 | 0.053903 | 0.035662 | 0.029392 | 0.1992 | 0.054932 | -0.004578 | -0.1236 | 0.16022 | -0.068665 | 0.12817 | -0.11902 | -7.9147 | 113.1592 | -8.8715 | 8.7204 | -94.1116 | 8.8989 | 9.0042 | -94.1757 | -0.027466 | 19.0521 | 0.17853 | 8.725 | 0.92926 | 8.7753 | 8.8394 | 8.8989 | 122.0032 | 8.9722 | -0.027466 | 8.8394 | 8.8989 | 8.9722 | 8.7753 | 122.0032 | -94.2307 | -102.9785
4095.2969 | 121.5454 | -8.7433 | 112.3032 | 0.017319 | -0.002555 | 0.0039179 | 0.050699 | 0.034808 | 0.031956 | 0.20198 | -0.004578 | -0.004578 | -0.10986 | 0.11444 | -0.11902 | 0.12817 | -0.14648 | -8.0017 | 113.0997 | -8.9218 | 8.6334 | -112.3077 | 8.7387 | 8.8577 | -112.4222 | -0.17853 | 0.79651 | 0.10529 | 8.5968 | 0.74158 | 8.6243 | 8.7387 | 8.7387 | 121.843 | 8.8715 | -0.17853 | 8.7387 | 8.7387 | 8.8715 | 8.6243 | 121.843 | -112.413 | -121.225
4097.0312 | 121.5454 | -8.8028 | 112.6648 | -0.0055695 | -0.0010596 | 0.0064813 | 0.051981 | 0.034167 | 0.031315 | 0.20027 | 0.013733 | 0.004578 | -0.12817 | 0.11444 | -0.1236 | 0.10986 | -0.14191 | -8.0338 | 113.031 | -9.0042 | 8.6746 | -112.6602 | 8.8165 | 8.9172 | -112.7884 | -0.20142 | 0.36621 | 0.14191 | 8.6609 | 0.76904 | 8.6792 | 8.8074 | 8.8165 | 121.8338 | 8.9127 | -0.20142 | 8.8074 | 8.8165 | 8.9127 | 8.6792 | 121.8338 | -112.793 | -121.669
4098.7344 | 121.2387 | -15.4175 | 101.8982 | 0.0096895 | -0.0027686 | 0.0015679 | 0.051767 | 0.027758 | 0.024906 | 0.18574 | 0.018311 | 0.027466 | -0.13275 | 0.15106 | 0.064087 | 0.1236 | -0.16022 | -15.2023 | 106.1142 | -15.9073 | 15.2847 | -101.8707 | 15.4358 | 15.5685 | -101.8341 | -0.48981 | 4.216 | 0.15106 | 15.2573 | 0.21515 | 15.4816 | 15.4449 | 15.4358 | 121.5317 | 15.5411 | -0.48981 | 15.4449 | 15.4358 | 15.5411 | 15.4816 | 121.5317 | -102.0309 | -117.8055
4100.4688 | 121.9482 | -8.9081 | 111.8134 | 0.0096895 | -0.0014868 | 0.0045587 | 0.059885 | 0.038012 | 0.028752 | 0.19813 | -0.027466 | 0.022888 | -0.17395 | 0.045776 | -0.19226 | 0.013733 | -0.022888 | -8.6838 | 112.6831 | -9.4299 | 8.7341 | -111.7905 | 8.8806 | 8.9539 | -112.0056 | -0.52185 | 0.86975 | 0.14648 | 8.8852 | 0.2243 | 8.7158 | 8.931 | 8.8806 | 121.5912 | 8.9218 | -0.52185 | 8.931 | 8.8806 | 8.9218 | 8.7158 | 121.5912 | -111.9873 | -121.2433
4102.1719 | 121.9803 | -95.018 | 26.3809 | 0.0096895 | 0.001504 | 0.0073359 | 1.7172 | -0.0091987 | -0.016323 | 1.6792 | -0.022888 | 0.059509 | -0.21973 | 0.09613 | -4.8935 | 0.064087 | -0.054932 | -92.3904 | 25.9094 | -95.7596 | 94.7983 | -26.3214 | 94.9951 | 95.1141 | -31.2744 | -0.74158 | -0.4715 | 0.19684 | 94.9631 | 2.6276 | 90.1245 | 95.0775 | 94.9951 | 120.9274 | 95.0821 | -0.74158 | 95.0775 | 94.9951 | 95.0821 | 90.1245 | 120.9274 | -26.6006 | -122.1405
4103.9375 | 121.5454 | -9.3109 | 112.4359 | 0.00206 | -0.0021276 | 0.0069085 | 0.058176 | 0.036517 | 0.031529 | 0.2039 | 0.041199 | -0.004578 | -0.13275 | 0.16022 | -0.13275 | 0.14191 | -0.21973 | -8.6609 | 112.5687 | -9.4528 | 9.1782 | -112.4405 | 9.3521 | 9.4711 | -112.5687 | -0.14191 | 0.13275 | 0.17395 | 9.0912 | 0.65002 | 9.1782 | 9.3063 | 9.3521 | 121.8796 | 9.4528 | -0.14191 | 9.3063 | 9.3521 | 9.4528 | 9.1782 | 121.8796 | -112.5687 | -121.8887
4105.6562 | 121.9299 | -8.5648 | 112.5137 | 0.00206 | -0.0029822 | 0.0051995 | 0.052622 | 0.034808 | 0.03217 | 0.20155 | 0.054932 | 0.022888 | -0.13275 | 0.16937 | -0.10529 | 0.16022 | -0.16937 | -7.9102 | 113.3011 | -8.757 | 8.432 | -112.4908 | 8.6197 | 8.7341 | -112.619 | -0.19226 | 0.78735 | 0.18768 | 8.3954 | 0.6546 | 8.4595 | 8.5876 | 8.6197 | 121.8658 | 8.725 | -0.19226 | 8.5876 | 8.6197 | 8.725 | 8.4595 | 121.8658 | -112.6465 | -121.2708
4107.375 | 108.2108 | -9.2011 | 102.5253 | 0.0096895 | -0.0029822 | 0.0047723 | 0.060312 | 0.035021 | 0.031101 | 0.21244 | 0.073242 | -0.009155 | -0.11902 | 0.19226 | -0.13275 | 0.16022 | -0.16022 | -8.7845 | 112.2986 | -9.7229 | 9.082 | -102.5345 | 9.2743 | 9.3933 | -102.6581 | -0.52185 | 9.7733 | 0.19226 | 9.0408 | 0.41657 | 9.0683 | 9.1919 | 9.2743 | 121.4996 | 9.3613 | -0.52185 | 9.1919 | 9.2743 | 9.3613 | 9.0683 | 121.4996 | -102.6443 | -112.2482
4109.125 | 121.1792 | -8.3817 | 113.4338 | 0.00206 | -0.00020502 | 0.0058405 | 0.054117 | 0.035021 | 0.030674 | 0.20283 | 0.013733 | 0.004578 | -0.13733 | 0.15106 | -0.1236 | 0.1236 | -0.16479 | -7.7408 | 113.4888 | -8.5556 | 8.2443 | -113.4293 | 8.3954 | 8.5327 | -113.5574 | -0.17395 | 0.054932 | 0.15106 | 8.2169 | 0.64087 | 8.2581 | 8.3862 | 8.3954 | 121.8704 | 8.5052 | -0.17395 | 8.3862 | 8.3954 | 8.5052 | 8.2581 | 121.8704 | -113.5712 | -121.9894
4110.8438 | 100.8774 | -14.1769 | 92.8757 | 0.00206 | -0.0017004 | 0.0028497 | 0.055185 | 0.033099 | 0.023411 | 0.1898 | -0.004578 | 0.032043 | -0.14191 | 0.11444 | -0.17395 | 0.045776 | -0.027466 | -14.1678 | 107.2678 | -14.8178 | 14.035 | -92.8436 | 14.1724 | 14.2914 | -93.0496 | -0.64087 | 14.3921 | 0.13733 | 14.1495 | 0.009155 | 14.003 | 14.209 | 14.1724 | 121.4447 | 14.2227 | -0.64087 | 14.209 | 14.1724 | 14.2227 | 14.003 | 121.4447 | -93.0176 | -107.6935
4112.5781 | 121.2341 | -8.2535 | 113.0264 | 0.00206 | -0.00041862 | -0.0003547 | 0.053049 | 0.036303 | 0.031529 | 0.20347 | 0.022888 | 0.004578 | -0.12817 | 0.14648 | -0.12817 | 0.12817 | -0.15564 | -7.6309 | 113.6078 | -8.4503 | 8.1253 | -113.0219 | 8.2764 | 8.4 | -113.1546 | -0.19684 | 0.58136 | 0.15106 | 8.0978 | 0.62256 | 8.1253 | 8.2581 | 8.2764 | 121.8613 | 8.3817 | -0.19684 | 8.2581 | 8.2764 | 8.3817 | 8.1253 | 121.8613 | -113.1546 | -121.4767
4114.3125 | 115.0177 | -8.0887 | 104.4754 | 0.017319 | -0.0021276 | 0.0013543 | 0.053903 | 0.035876 | 0.030247 | 0.20069 | 0.054932 | 0 | -0.11902 | 0.19684 | -0.09613 | 0.15564 | -0.17395 | -7.457 | 113.6993 | -8.3633 | 7.9697 | -104.4754 | 8.1436 | 8.2855 | -104.5715 | -0.27466 | 9.2239 | 0.17395 | 7.9147 | 0.63171 | 7.9926 | 8.0887 | 8.1436 | 121.788 | 8.2443 | -0.27466 | 8.0887 | 8.1436 | 8.2443 | 7.9926 | 121.788 | -104.5944 | -112.8387
4116.0469 | 121.4905 | -7.7316 | 113.4476 | 0.0096895 | -0.00041862 | 0.0058405 | 0.054117 | 0.03438 | 0.029179 | 0.20176 | 0.082397 | -0.013733 | -0.1236 | 0.20599 | -0.10071 | 0.18768 | -0.21057 | -6.9946 | 114.1708 | -7.9056 | 7.608 | -113.4613 | 7.814 | 7.9376 | -113.5483 | -0.17395 | 0.72327 | 0.20599 | 7.5211 | 0.737 | 7.6309 | 7.7179 | 7.814 | 121.9025 | 7.9193 | -0.17395 | 7.7179 | 7.814 | 7.9193 | 7.6309 | 121.9025 | -113.5712 | -121.3531
4117.75 | 121.6827 | -7.5302 | 111.7264 | 0.0096895 | -0.0027686 | 0.0088311 | 0.053476 | 0.036303 | 0.030888 | 0.20369 | 0.068665 | 0 | -0.13275 | 0.18768 | -0.1236 | 0.13733 | -0.13733 | -6.9397 | 114.2624 | -7.814 | 7.3975 | -111.7264 | 7.5989 | 7.7179 | -111.85 | -0.28381 | 2.536 | 0.20142 | 7.3929 | 0.59051 | 7.4066 | 7.5302 | 7.5989 | 121.7926 | 7.6675 | -0.28381 | 7.5302 | 7.5989 | 7.6675 | 7.4066 | 121.7926 | -111.8591 | -119.5404
4119.4844 | 121.8613 | -7.5577 | 113.6581 | 0.0096895 | -0.0014868 | 0.0069085 | 0.061594 | 0.03673 | 0.030674 | 0.20433 | 0.022888 | 0 | -0.15564 | 0.12817 | -0.21057 | 0.059509 | -0.07782 | -7.0724 | 114.3356 | -7.8278 | 7.402 | -113.6581 | 7.5806 | 7.6859 | -113.8687 | -0.27008 | 0.67749 | 0.17853 | 7.4799 | 0.48523 | 7.3471 | 7.5577 | 7.5806 | 121.8933 | 7.6172 | -0.27008 | 7.5577 | 7.5806 | 7.6172 | 7.3471 | 121.8933 | -113.8138 | -121.4859
4121.2188 | 121.2067 | -119.2429 | 1.6022 | 0.0096895 | -0.0010596 | 0.0069085 | 0.076334 | -0.023939 | -0.029568 | 0.0052295 | 0.073242 | 0.041199 | -0.07782 | 0.14648 | 0.17395 | 0.13733 | -0.027466 | 0.48065 | 1.6251 | -119.664 | 119.165 | -1.561 | 119.3161 | 119.3893 | -1.4282 | -0.42114 | 0.022888 | 0.15106 | 119.2154 | 119.7235 | 119.4168 | 119.2841 | 119.3161 | 120.8679 | 119.3802 | -0.42114 | 119.2841 | 119.3161 | 119.3802 | 119.4168 | 120.8679 | -1.68 | -121.2662
4123 | 121.5637 | -120.0119 | 1.3596 | 0.00206 | -0.001914 | 0.0056269 | 0.079752 | -0.024793 | -0.031917 | 0.0052295 | 0.086975 | 0.041199 | -0.073242 | 0.19684 | 0.23804 | 0.18768 | -0.12817 | 0.59052 | 1.3504 | -120.3552 | 119.9387 | -1.3184 | 120.0989 | 120.2087 | -1.1215 | -0.34332 | -0.009155 | 0.16022 | 119.8837 | 120.6024 | 120.2499 | 120.0531 | 120.0989 | 121.3623 | 120.1996 | -0.34332 | 120.0531 | 120.0989 | 120.1996 | 120.2499 | 121.3623 | -1.4328 | -121.7148
4124.7031 | 121.6095 | -120.163 | 1.3046 | -0.0055695 | -0.0021276 | 0.0049859 | 0.085947 | -0.022871 | -0.034054 | 0.0054431 | 0.013733 | 0.07782 | -0.1236 | 0.12817 | 0.1236 | 0.091553 | -0.009155 | 0.42572 | 1.387 | -120.4056 | 120.0394 | -1.2268 | 120.1767 | 120.2911 | -1.181 | -0.24262 | 0.082398 | 0.13733 | 120.1538 | 120.5887 | 120.2866 | 120.2408 | 120.1767 | 121.55 | 120.2545 | -0.24262 | 120.2408 | 120.1767 | 120.2545 | 120.2866 | 121.55 | -1.4282 | -121.7102
4126.4688 | 121.756 | -120.6573 | 0.82398 | 0.00206 | -0.0012732 | 0.0066949 | 0.087229 | -0.02522 | -0.033413 | 0.010784 | 0.054932 | 0.054932 | -0.07782 | 0.15564 | 0.1236 | 0.16022 | -0.13733 | 0.38452 | 0.90179 | -120.9457 | 120.5795 | -0.76904 | 120.7123 | 120.813 | -0.70038 | -0.28839 | 0.077819 | 0.13275 | 120.52 | 121.0419 | 120.7809 | 120.7123 | 120.7123 | 121.5591 | 120.8176 | -0.28839 | 120.7123 | 120.7123 | 120.8176 | 120.7809 | 121.5591 | -0.9018 | -121.7697
4128.1719 | 121.7926 | -120.7169 | 0.80566 | 0.0096895 | -0.00020502 | 0.0047723 | 0.097696 | -0.023939 | -0.030422 | 0.0377 | 0.059509 | 0.036621 | -0.07782 | 0.15106 | 0.086975 | 0.15564 | -0.14648 | 0.32959 | 0.85144 | -121.0052 | 120.639 | -0.76904 | 120.7764 | 120.8679 | -0.71869 | -0.28839 | 0.045776 | 0.13733 | 120.5704 | 121.0464 | 120.8038 | 120.7535 | 120.7764 | 121.5683 | 120.8725 | -0.28839 | 120.7535 | 120.7764 | 120.8725 | 120.8038 | 121.5683 | -0.88348 | -121.8109
4129.9375 | 121.6232 | -120.9824 | 0.6546 | 0.00206 | -0.0031958 | 0.0009271 | 0.093637 | -0.02757 | -0.03149 | 0.01527 | 0.10986 | 0.032043 | -0.091553 | 0.21057 | 0.14648 | 0.21515 | -0.15106 | 0.44861 | 0.68665 | -121.2021 | 120.8908 | -0.62256 | 121.0922 | 121.1929 | -0.50812 | -0.21973 | 0.032044 | 0.20142 | 120.8313 | 121.431 | 121.1288 | 121.0144 | 121.0922 | 121.669 | 121.1975 | -0.21973 | 121.0144 | 121.0922 | 121.1975 | 121.1288 | 121.669 | -0.74616 | -121.8567
4131.6406 | 121.7239 | -120.9503 | 0.62714 | 0.00206 | -0.00084602 | 0.0077631 | 0.12739 | -0.027357 | -0.034054 | 0.046459 | -0.004578 | 0.086975 | -0.1236 | 0.10071 | -0.19226 | 0.073242 | 0.027466 | 0.34332 | 0.83313 | -121.1655 | 120.8267 | -0.54016 | 120.9457 | 121.051 | -0.8194 | -0.21515 | 0.20599 | 0.11902 | 120.9778 | 121.2936 | 120.7581 | 121.0373 | 120.9457 | 121.7834 | 121.0236 | -0.21515 | 121.0373 | 120.9457 | 121.0236 | 120.7581 | 121.7834 | -0.75073 | -121.7926
4133.375 | 121.7834 | -120.9686 | 0.59509 | 0.0096895 | -0.0021276 | 0.0058405 | 0.099191 | -0.02458 | -0.032772 | 0.023815 | -0.009155 | 0.064087 | -0.1236 | 0.07782 | -0.018311 | 0.036621 | 0 | 0.24261 | 0.64545 | -121.2845 | 120.845 | -0.53101 | 120.9595 | 121.0464 | -0.6134 | -0.31586 | 0.050354 | 0.11444 | 120.9686 | 121.2112 | 120.9503 | 121.0327 | 120.9595 | 121.6141 | 121.0052 | -0.31586 | 121.0327 | 120.9595 | 121.0052 | 120.9503 | 121.6141 | -0.71869 | -121.8796
4135.1094 | 121.7377 | -120.9045 | 0.72784 | 0.00206 | -0.00063242 | 0.0037043 | 0.1118 | -0.025861 | -0.031917 | 0.031719 | -0.009155 | 0.091553 | -0.13275 | 0.086975 | -0.032043 | 0.041199 | 0.036621 | 0.27466 | 0.76446 | -121.225 | 120.7718 | -0.63629 | 120.8954 | 120.9915 | -0.75989 | -0.32044 | 0.036621 | 0.1236 | 120.9412 | 121.1792 | 120.8725 | 120.9961 | 120.8954 | 121.669 | 120.9457 | -0.32044 | 120.9961 | 120.8954 | 120.9457 | 120.8725 | 121.669 | -0.86059 | -121.9528
4136.8125 | 121.6736 | -121.0236 | 0.63171 | 0.0096895 | 0.00043578 | 0.0073359 | 0.11308 | -0.025434 | -0.034054 | 0.036846 | 0.059509 | 0.059509 | -0.091553 | 0.16022 | 0.004578 | 0.1236 | -0.032043 | 0.33417 | 0.70496 | -121.2341 | 120.932 | -0.5722 | 121.0831 | 121.1838 | -0.62714 | -0.21057 | 0.073242 | 0.15106 | 120.9915 | 121.3577 | 121.0281 | 121.0831 | 121.0831 | 121.7285 | 121.1472 | -0.21057 | 121.0831 | 121.0831 | 121.1472 | 121.0281 | 121.7285 | -0.72327 | -121.8658
4138.5938 | 121.8109 | -120.9549 | 0.62256 | 0.0096895 | 0.00086298 | 0.0094721 | 0.11991 | -0.025648 | -0.030849 | 0.038768 | 0.086975 | 0.082397 | -0.082397 | 0.17395 | 0.032043 | 0.17395 | -0.1831 | 0.36163 | 0.70496 | -121.2387 | 120.8725 | -0.54016 | 121.0419 | 121.1288 | -0.59052 | -0.28381 | 0.082397 | 0.16937 | 120.7718 | 121.3165 | 120.9869 | 121.0373 | 121.0419 | 121.6599 | 121.1288 | -0.28381 | 121.0373 | 121.0419 | 121.1288 | 120.9869 | 121.6599 | -0.70496 | -121.8613
4140.3281 | 121.8201 | -120.8542 | 0.737 | 0.0096895 | -0.0034094 | 0.0058405 | 0.11735 | -0.021802 | -0.032985 | 0.038127 | -0.013733 | 0.050354 | -0.1236 | 0.068665 | -0.086975 | 0.041199 | 0.013733 | 0.22888 | 0.8194 | -121.1884 | 120.7306 | -0.68665 | 120.8405 | 120.9229 | -0.82398 | -0.33417 | 0.082397 | 0.10986 | 120.8679 | 121.0831 | 120.7672 | 120.9045 | 120.8405 | 121.6736 | 120.8954 | -0.33417 | 120.9045 | 120.8405 | 120.8954 | 120.7672 | 121.6736 | -0.8606 | -121.9254
4142.0625 | 121.7972 | -120.3278 | 1.2451 | 0.017319 | -0.0012732 | 0.0073359 | 0.34892 | -0.024152 | -0.029354 | 0.27482 | -0.036621 | 0.082397 | -0.1236 | 0.073242 | -0.064087 | 0.054932 | -0.013733 | 0.07782 | 1.4511 | -120.4788 | 120.2042 | -1.1627 | 120.2911 | 120.401 | -1.3092 | -0.15106 | 0.20599 | 0.086975 | 120.314 | 120.4056 | 120.2637 | 120.4102 | 120.2911 | 121.7789 | 120.3827 | -0.15106 | 120.4102 | 120.2911 | 120.3827 | 120.2637 | 121.7789 | -1.3687 | -121.7239
4143.7812 | 121.9574 | -120.9183 | 0.68207 | 0.017319 | -0.0029822 | 0.0034905 | 0.17524 | -0.027784 | -0.031277 | 0.14323 | 0.041199 | 0.064087 | -0.082397 | 0.13275 | 0.022888 | 0.14191 | -0.10529 | 0.25177 | 0.79193 | -121.1655 | 120.8359 | -0.61798 | 120.9595 | 121.051 | -0.65918 | -0.24719 | 0.10986 | 0.1236 | 120.813 | 121.17 | 120.9412 | 120.9824 | 120.9595 | 121.7102 | 121.0602 | -0.24719 | 120.9824 | 120.9595 | 121.0602 | 120.9412 | 121.7102 | -0.76446 | -121.8475
4145.5 | 117.1097 | -67.6254 | 48.0927 | 0.0096895 | -0.00041862 | 0.0022089 | 6.9721 | -0.0072761 | -0.013119 | 7.0123 | 0.041199 | 0.018311 | -0.11902 | 0.19226 | -2.8519 | 0.21515 | -0.036621 | -1.9409 | 35.4858 | -58.5022 | 67.5064 | -48.0743 | 67.6666 | 67.8177 | -50.9445 | 9.1232 | -12.6068 | 0.16022 | 67.5888 | 65.6845 | 64.7736 | 67.6437 | 67.6666 | 103.1113 | 67.8406 | 9.1232 | 67.6437 | 67.6666 | 67.8406 | 64.7736 | 103.1113 | -48.2117 | -106.5948
4147.2031 | 116.2445 | -66.0278 | 51.1459 | -0.013199 | -0.0027686 | 0.0049859 | 6.9721 | 0.0036187 | 0.0084574 | 7.0123 | 0.064087 | 0.032043 | -0.13733 | 0.17395 | -9.6817 | 0.041199 | -0.091553 | -30.0385 | 54.6249 | -61.6058 | 65.8905 | -51.1139 | 66.0919 | 66.2018 | -60.8276 | 4.422 | 3.479 | 0.20142 | 65.9363 | 35.9894 | 56.3461 | 66.0599 | 66.0919 | 120.6528 | 66.069 | 4.422 | 66.0599 | 66.0919 | 66.069 | 56.3461 | 120.6528 | -51.2833 | -112.7518
4148.9375 | 120.9183 | -98.1445 | 22.3755 | 0.0096895 | 0.0023584 | 0.0041315 | 0.084665 | -0.020948 | -0.032772 | 0.0028797 | 0.018311 | 0.068665 | -0.11444 | 0.068665 | 0.46234 | 0.059509 | -0.027466 | 0.21057 | 1.2726 | -119.664 | 98.0301 | -22.3068 | 98.1628 | 98.2132 | -21.9131 | -21.5195 | -21.1029 | 0.13275 | 98.1171 | 98.3551 | 98.6069 | 98.2132 | 98.1628 | 99.4171 | 98.204 | -21.5195 | 98.2132 | 98.1628 | 98.204 | 98.6069 | 99.4171 | -22.4899 | -142.0395
4150.7188 | 121.1243 | -119.7052 | 1.0025 | 0.017319 | -0.002555 | 0.0051995 | 0.087229 | -0.023084 | -0.031704 | 0.011638 | -0.022888 | 0.09613 | -0.13275 | 0.082397 | 0.091553 | 0.054932 | 0.036621 | 0.27466 | 1.1765 | -120.0348 | 119.5724 | -0.90637 | 119.6823 | 119.7876 | -0.91095 | -0.32959 | 0.17395 | 0.10986 | 119.7418 | 119.9799 | 119.7968 | 119.8013 | 119.6823 | 120.8817 | 119.7601 | -0.32959 | 119.8013 | 119.6823 | 119.7601 | 119.7968 | 120.8817 | -1.1353 | -121.0373
4152.4844 | 120.4788 | -105.2719 | 14.0762 | -0.013199 | -0.0031958 | 0.0086175 | 6.9721 | -0.01048 | -0.006069 | 7.0123 | 0.041199 | 0.045776 | -0.086975 | 0.24261 | -0.75073 | -0.018311 | -0.51727 | -0.37537 | 40.361 | -75.3159 | 105.1849 | -14.0305 | 105.3131 | 105.5145 | -14.827 | 29.9561 | 26.2848 | 0.12817 | 104.7546 | 104.8965 | 104.5212 | 105.3177 | 105.3131 | 145.6329 | 105.2536 | 29.9561 | 105.3177 | 105.3131 | 105.2536 | 104.5212 | 145.6329 | -14.1632 | -89.3921
4154.2188 | 120.6802 | -119.2703 | 0.91095 | 0.0096895 | -0.0017004 | 0.0094721 | 0.096842 | -0.025434 | -0.030208 | 0.024455 | 0.064087 | 0.045776 | -0.068665 | 0.16937 | 0.082397 | 0.16937 | -0.10986 | 0.32044 | 0.85602 | -119.7876 | 119.2017 | -0.86517 | 119.3344 | 119.4397 | -0.82855 | -0.51727 | -0.054932 | 0.13275 | 119.1605 | 119.5908 | 119.3527 | 119.3161 | 119.3344 | 120.1263 | 119.4397 | -0.51727 | 119.3161 | 119.3344 | 119.4397 | 119.3527 | 120.1263 | -0.97962 | -120.6985
4155.9844 | 120.2316 | -46.55 | 72.8027 | -0.0055695 | -0.0038366 | 0.0075495 | 0.038523 | 0.013445 | 0.0084574 | 0.10926 | 0.036621 | 0.013733 | -0.10071 | 0.12817 | 0.12817 | 0.13733 | -0.16937 | 0.086975 | 72.0016 | -48.3582 | 46.4493 | -72.789 | 46.5866 | 46.6782 | -72.6746 | -1.8082 | -0.80109 | 0.13733 | 46.3806 | 46.637 | 46.6782 | 46.5637 | 46.5866 | 118.5516 | 46.6873 | -1.8082 | 46.5637 | 46.5866 | 46.6873 | 46.6782 | 118.5516 | -72.9034 | -121.1609
4157.6875 | 120.5063 | -119.3893 | 0.59509 | 0.017319 | -0.0017004 | 0.0034905 | 0.093851 | -0.026289 | -0.029781 | 0.016979 | -0.009155 | 0.073242 | -0.12817 | 0.073242 | 0.18768 | 0.054932 | -0.032043 | 0.13275 | 0.66834 | -119.9387 | 119.2612 | -0.52185 | 119.3802 | 119.4626 | -0.40741 | -0.54932 | 0.073242 | 0.11902 | 119.3573 | 119.5221 | 119.577 | 119.4626 | 119.3802 | 120.0577 | 119.4443 | -0.54932 | 119.4626 | 119.3802 | 119.4443 | 119.577 | 120.0577 | -0.72327 | -120.5338
4159.4062 | 120.6711 | -119.3802 | 0.82398 | 0.0096895 | -0.00041862 | 0.0071221 | 0.087229 | -0.021162 | -0.029781 | 0.014629 | 0.07782 | 0.050354 | -0.091553 | 0.18768 | 0.091553 | 0.17853 | -0.18768 | 0.31128 | 1.0025 | -119.7098 | 119.2886 | -0.77362 | 119.458 | 119.5679 | -0.73242 | -0.32959 | 0.17853 | 0.16937 | 119.1925 | 119.6915 | 119.4717 | 119.4305 | 119.458 | 120.3827 | 119.5587 | -0.32959 | 119.4305 | 119.458 | 119.5587 | 119.4717 | 120.3827 | -0.91553 | -120.5338
4161.1406 | 120.7718 | -120.0485 | 0.5127 | 0.00206 | -0.001914 | 0.0075495 | 0.093851 | -0.022871 | -0.031917 | 0.012493 | 0.050354 | 0.059509 | -0.10986 | 0.14191 | 0.064087 | 0.1236 | -0.059509 | 0.23804 | 0.55847 | -120.3873 | 119.9387 | -0.45319 | 120.0989 | 120.1904 | -0.44861 | -0.33875 | 0.045777 | 0.16022 | 119.989 | 120.2866 | 120.1126 | 120.108 | 120.0989 | 120.607 | 120.1721 | -0.33875 | 120.108 | 120.0989 | 120.1721 | 120.1126 | 120.607 | -0.62256 | -120.9
4162.9531 | 116.8396 | -70.6467 | 45.7718 | 0.017319 | -0.0010596 | 0.0060541 | 6.9721 | -0.0070623 | -0.025722 | 7.0123 | -0.009155 | 0.064087 | -0.13275 | -0.086975 | 0.032043 | -0.091553 | -0.009155 | 0.091553 | 33.4579 | -62.8738 | 70.5139 | -45.7077 | 70.6375 | 70.5597 | -45.7397 | 7.7728 | -12.3138 | 0.1236 | 70.6375 | 70.7382 | 70.6787 | 70.7108 | 70.6375 | 104.1046 | 70.5551 | 7.7728 | 70.7108 | 70.6375 | 70.5551 | 70.6787 | 104.1046 | -45.9045 | -108.6456
4164.6875 | 119.8242 | -96.4188 | 22.9431 | -0.0055695 | -0.0029822 | 0.0060541 | 0.038736 | -0.012617 | -0.021877 | 0.01292 | 0.041199 | 0.059509 | -0.10071 | 0.12817 | 0.059509 | 0.11444 | -0.054932 | 0.19226 | 23.2407 | -96.6339 | 96.3181 | -22.8836 | 96.46 | 96.5469 | -22.8836 | -0.21515 | 0.29755 | 0.14191 | 96.3638 | 96.611 | 96.4783 | 96.4783 | 96.46 | 119.6594 | 96.5332 | -0.21515 | 96.4783 | 96.46 | 96.5332 | 96.4783 | 119.6594 | -23.0438 | -119.577
4166.4219 | 120.7214 | -119.87 | 0.56305 | 0.0096895 | -0.0027686 | 0.0034905 | 0.084024 | -0.024152 | -0.030636 | 0.0086475 | 0.054932 | 0.036621 | -0.086975 | 0.13275 | 0.086975 | 0.14648 | -0.032043 | 0.24719 | 0.63171 | -120.2316 | 119.783 | -0.52643 | 119.9249 | 120.0027 | -0.47607 | -0.36163 | 0.068665 | 0.14191 | 119.838 | 120.1172 | 119.957 | 119.9066 | 119.9249 | 120.5017 | 120.0165 | -0.36163 | 119.9066 | 119.9249 | 120.0165 | 119.957 | 120.5017 | -0.65002 | -120.7947
4168.1562 | 120.7672 | -120.0577 | 0.54932 | 0.0096895 | -0.002555 | 0.0054131 | 0.094278 | -0.023511 | -0.032558 | 0.010997 | 0.027466 | 0.054932 | -0.10986 | 0.10529 | 0.022888 | 0.082397 | -0.022888 | 0.17853 | 0.58594 | -120.3781 | 119.9478 | -0.49438 | 120.0851 | 120.163 | -0.52643 | -0.32044 | 0.036621 | 0.13733 | 120.0348 | 120.2362 | 120.0806 | 120.1126 | 120.0851 | 120.6436 | 120.1401 | -0.32044 | 120.1126 | 120.0851 | 120.1401 | 120.0806 | 120.6436 | -0.65918 | -120.9274
4169.9219 | 120.1218 | -119.1101 | 0.60883 | 0.00206 | -0.004264 | 0.0047723 | 0.090219 | -0.023298 | -0.033626 | 0.01292 | 0.10986 | 0.027466 | -0.073242 | 0.19226 | 0.11902 | 0.19684 | -0.21057 | 0.2655 | 0.60883 | -119.5496 | 119.0369 | -0.58136 | 119.22 | 119.3024 | -0.48981 | -0.43945 | 0 | 0.18311 | 118.8995 | 119.3756 | 119.2291 | 119.1376 | 119.22 | 119.7189 | 119.3069 | -0.43945 | 119.1376 | 119.22 | 119.3069 | 119.2291 | 119.7189 | -0.68207 | -120.1584
4171.625 | 120.2866 | -117.9474 | 1.8356 | 0.017319 | -0.0023412 | 0.0045587 | 0.083383 | -0.024152 | -0.029995 | 0.016338 | 0.041199 | 0.054932 | -0.091553 | 0.1236 | 0.068665 | 0.15564 | -0.11902 | 0.23804 | 1.4877 | -118.84 | 117.8558 | -1.7807 | 117.9886 | 118.071 | -1.767 | -0.89264 | -0.3479 | 0.13275 | 117.8284 | 118.1854 | 118.0161 | 118.0023 | 117.9886 | 119.4351 | 118.103 | -0.89264 | 118.0023 | 117.9886 | 118.103 | 118.0161 | 119.4351 | -1.9272 | -120.6757
4173.3438 | 120.6436 | -115.8646 | 4.4312 | -0.0055695 | 8.578e-06 | 0.0022089 | 0.074198 | -0.024793 | -0.026363 | 0.012065 | 0.11444 | 0.009155 | -0.064087 | 0.21057 | 0.13275 | 0.21973 | -0.16937 | 0.35248 | 4.3762 | -116.2994 | 115.8005 | -4.422 | 115.979 | 116.0751 | -4.2984 | -0.43487 | -0.054931 | 0.17853 | 115.6952 | 116.217 | 115.9973 | 115.8737 | 115.979 | 120.2408 | 116.0843 | -0.43487 | 115.8737 | 115.979 | 116.0843 | 115.9973 | 120.2408 | -4.4952 | -120.7306
4175.0625 | 120.7626 | -116.3361 | 4.0924 | 0.0096895 | 0.00022218 | 0.0084039 | 0.075052 | -0.022871 | -0.028713 | 0.017406 | 0.013733 | 0.068665 | -0.10529 | 0.09613 | 0.009155 | 0.059509 | -0.018311 | 0.14648 | 4.0604 | -116.803 | 116.2308 | -4.0237 | 116.3498 | 116.4322 | -4.0833 | -0.46692 | -0.032043 | 0.11902 | 116.3177 | 116.4825 | 116.3452 | 116.4047 | 116.3498 | 120.3964 | 116.3956 | -0.46692 | 116.4047 | 116.3498 | 116.3956 | 116.3452 | 120.3964 | -4.1977 | -120.8954
4176.7812 | 120.8542 | -118.0664 | 2.4353 | 0.00206 | 0.001504 | 0.0062677 | 0.082529 | -0.022016 | -0.030636 | 0.02296 | 0.004578 | 0.086975 | -0.10986 | 0.1236 | 0.050354 | 0.11902 | -0.10071 | 0.17853 | 2.6001 | -118.364 | 117.9565 | -2.3483 | 118.071 | 118.19 | -2.3849 | -0.29755 | 0.16479 | 0.11444 | 117.9657 | 118.2449 | 118.1168 | 118.1534 | 118.071 | 120.6665 | 118.1854 | -0.29755 | 118.1534 | 118.071 | 118.1854 | 118.1168 | 120.6665 | -2.5452 | -120.7993
4178.5 | 120.8954 | -118.0481 | 2.4353 | 0.00206 | 0.001504 | 0.0084039 | 0.07377 | -0.021589 | -0.031063 | 0.016979 | 0.059509 | 0.050354 | -0.09613 | 0.16022 | 0.091553 | 0.17395 | -0.16022 | 0.23346 | 2.5085 | -118.364 | 117.952 | -2.3849 | 118.1076 | 118.2083 | -2.3438 | -0.31586 | 0.073242 | 0.15564 | 117.8879 | 118.2816 | 118.1396 | 118.0984 | 118.1076 | 120.5566 | 118.222 | -0.31586 | 118.0984 | 118.1076 | 118.222 | 118.1396 | 120.5566 | -2.5314 | -120.7993
4180.2188 | 120.9915 | -118.3502 | 2.2156 | 0.017319 | -0.00084602 | 0.0051995 | 0.085306 | -0.022657 | -0.028713 | 0.036632 | -0.018311 | 0.082397 | -0.12817 | 0.064087 | 0.004578 | 0.064087 | -0.013733 | 0.1236 | 2.5681 | -118.4921 | 118.222 | -2.1332 | 118.3319 | 118.4143 | -2.211 | -0.14191 | 0.35248 | 0.10986 | 118.3365 | 118.4738 | 118.3548 | 118.4326 | 118.3319 | 120.9183 | 118.4143 | -0.14191 | 118.4326 | 118.3319 | 118.4143 | 118.3548 | 120.9183 | -2.3438 | -120.7077
4181.9844 | 120.8817 | -118.5699 | 2.092 | 0.0096895 | -0.0034094 | 0.0058405 | 0.090647 | -0.02522 | -0.030636 | 0.025524 | 0 | 0.082397 | -0.11444 | 0.086975 | 0.027466 | 0.082397 | -0.009155 | 0.14648 | 2.2064 | -118.8263 | 118.4555 | -2.0096 | 118.5699 | 118.6569 | -2.0645 | -0.25635 | 0.11444 | 0.11444 | 118.5608 | 118.7164 | 118.5974 | 118.6523 | 118.5699 | 120.7764 | 118.6523 | -0.25635 | 118.6523 | 118.5699 | 118.6523 | 118.5974 | 120.7764 | -2.2064 | -120.9183
4183.6875 | 120.9091 | -118.959 | 1.7349 | 0.00206 | -0.0049048 | 0.0034905 | 0.087656 | -0.023511 | -0.031277 | 0.031932 | 0.032043 | 0.050354 | -0.09613 | 0.11444 | 0.073242 | 0.086975 | 0.013733 | 0.19684 | 2.0737 | -119.2657 | 118.8629 | -1.6846 | 118.9911 | 119.0735 | -1.6617 | -0.3067 | 0.33875 | 0.12817 | 118.9728 | 119.1559 | 119.0323 | 119.0094 | 118.9911 | 121.0327 | 119.046 | -0.3067 | 119.0094 | 118.9911 | 119.046 | 119.0323 | 121.0327 | -1.8311 | -121.0007
4185.4531 | 120.9137 | -118.5104 | 2.1423 | 0.00206 | -0.0021276 | 0.0086175 | 0.13999 | -0.023084 | -0.034908 | 0.082561 | 0.045776 | 0.073242 | -0.10986 | 0.13275 | 0.091553 | 0.11444 | -0.041199 | 0.19226 | 2.0508 | -119.1147 | 118.4006 | -2.0691 | 118.5562 | 118.6432 | -2.0508 | -0.60425 | -0.091553 | 0.15564 | 118.4692 | 118.7027 | 118.602 | 118.5837 | 118.5562 | 120.5612 | 118.6249 | -0.60425 | 118.5837 | 118.5562 | 118.6249 | 118.602 | 120.5612 | -2.2522 | -121.257
4187.2344 | 120.9961 | -119.4077 | 1.3458 | -0.0055695 | -0.0014868 | 0.0043451 | 0.077829 | -0.025648 | -0.031063 | 0.020397 | 0.09613 | 0.041199 | -0.064087 | 0.23346 | 0.16937 | 0.21973 | -0.15106 | 0.32044 | 1.3641 | -119.7189 | 119.3436 | -1.3046 | 119.5038 | 119.6411 | -1.1765 | -0.31128 | 0.018311 | 0.16022 | 119.2566 | 119.7281 | 119.577 | 119.4489 | 119.5038 | 120.7718 | 119.6274 | -0.31128 | 119.4489 | 119.5038 | 119.6274 | 119.577 | 120.7718 | -1.4099 | -121.0648
4188.9688 | 120.7809 | -118.4189 | 2.0966 | 0.0096895 | -0.002555 | 0.0064813 | 0.089151 | -0.020948 | -0.031277 | 0.013133 | 0.073242 | 0.045776 | -0.086975 | 0.16022 | 0.086975 | 0.1831 | -0.16937 | 0.24261 | 1.3138 | -119.458 | 118.3319 | -2.0508 | 118.4921 | 118.5791 | -2.0096 | -1.0391 | -0.78278 | 0.16022 | 118.2495 | 118.6615 | 118.5059 | 118.4647 | 118.4921 | 119.7327 | 118.602 | -1.0391 | 118.4647 | 118.4921 | 118.602 | 118.5059 | 119.7327 | -2.1835 | -121.5546
4190.75 | 120.8405 | -117.778 | 2.9709 | 0.0096895 | -0.0023412 | 0.0024225 | 0.084665 | -0.024152 | -0.028927 | 0.013347 | 0.10529 | 0.032043 | -0.09613 | 0.20599 | 0.1236 | 0.21515 | -0.13275 | 0.32959 | 2.2064 | -118.6615 | 117.6819 | -2.9388 | 117.8833 | 117.984 | -2.8473 | -0.88348 | -0.76446 | 0.20142 | 117.6453 | 118.1076 | 117.9016 | 117.8101 | 117.8833 | 119.9844 | 117.9932 | -0.88348 | 117.8101 | 117.8833 | 117.9932 | 117.9016 | 119.9844 | -3.067 | -121.6324
4192.4844 | 120.9366 | -118.8858 | 1.7578 | 0.017319 | -0.0029822 | 0.0039179 | 0.09791 | -0.024366 | -0.031063 | 0.020397 | 0.091553 | 0.045776 | -0.086975 | 0.14191 | 0.073242 | 0.13733 | -0.041199 | 0.27008 | 1.9043 | -119.2245 | 118.7988 | -1.712 | 118.9774 | 119.0277 | -1.6846 | -0.33875 | 0.14648 | 0.17853 | 118.8446 | 119.1559 | 118.959 | 118.9316 | 118.9774 | 120.7901 | 119.0231 | -0.33875 | 118.9316 | 118.9774 | 119.0231 | 118.959 | 120.7901 | -1.8448 | -120.9824
4194.25 | 120.9549 | -119.1101 | 1.6067 | 0.00206 | -0.001914 | 0.0051995 | 0.091715 | -0.026929 | -0.030849 | 0.021465 | 0.004578 | 0.068665 | -0.10986 | 0.10071 | -0.009155 | 0.07782 | 0.036621 | 0.20142 | 1.6525 | -119.4534 | 119.0002 | -1.5381 | 119.1147 | 119.2108 | -1.6159 | -0.34332 | 0.045777 | 0.11444 | 119.1467 | 119.3115 | 119.101 | 119.1788 | 119.1147 | 120.7626 | 119.1879 | -0.34332 | 119.1788 | 119.1147 | 119.1879 | 119.101 | 120.7626 | -1.7166 | -121.0602
4196.0156 | 120.9595 | -114.7156 | 3.8315 | 0.0096895 | -0.0012732 | 0.0017817 | 0.16242 | -0.023939 | -0.031277 | 0.098583 | 0.059509 | 0.064087 | -0.11902 | 0.14191 | -0.082397 | 0.11902 | -0.050354 | 0.19684 | 4.3808 | -116.0843 | 114.5966 | -3.7674 | 114.7751 | 114.8575 | -3.9139 | -1.3687 | 0.54932 | 0.17853 | 114.6652 | 114.9124 | 114.6332 | 114.7797 | 114.7751 | 119.0964 | 114.8346 | -1.3687 | 114.7797 | 114.7751 | 114.8346 | 114.6332 | 119.0964 | -3.9505 | -119.9158
4197.7188 | 121.0373 | -119.2932 | 1.4191 | 0.00206 | -0.0023412 | 0.0037043 | 0.090647 | -0.02522 | -0.031917 | 0.016551 | -0.009155 | 0.086975 | -0.11902 | 0.10071 | 0.018311 | 0.068665 | 0.032043 | 0.17853 | 1.5106 | -119.6503 | 119.1742 | -1.3321 | 119.2841 | 119.3939 | -1.4008 | -0.35706 | 0.091553 | 0.10986 | 119.3253 | 119.4717 | 119.3115 | 119.3802 | 119.2841 | 120.8038 | 119.3619 | -0.35706 | 119.3802 | 119.2841 | 119.3619 | 119.3115 | 120.8038 | -1.5381 | -121.0693
4199.4844 | 121.0831 | -117.6132 | 3.1036 | 0.017319 | -0.00063242 | 0.0049859 | 0.29658 | -0.021375 | -0.029781 | 0.23658 | -0.009155 | 0.064087 | -0.11902 | 0.064087 | -0.27008 | 0.054932 | -0.004578 | 0.17395 | 5.5527 | -115.3976 | 117.4942 | -3.0396 | 117.6041 | 117.6773 | -3.3737 | 2.2156 | 2.449 | 0.10986 | 117.6086 | 117.7872 | 117.3431 | 117.6773 | 117.6041 | 123.1659 | 117.6682 | 2.2156 | 117.6773 | 117.6041 | 117.6682 | 117.3431 | 123.1659 | -3.2227 | -118.5013
4201.2031 | 121.0831 | -119.4077 | 1.3687 | 0.00206 | 0.001504 | 0.0064813 | 0.14747 | -0.025648 | -0.031277 | 0.07722 | 0 | 0.07782 | -0.13275 | 0.086975 | 0.018311 | 0.07782 | -0.018311 | 0.14648 | 1.5289 | -119.6823 | 119.2749 | -1.2909 | 119.4077 | 119.4946 | -1.3504 | -0.27466 | 0.16022 | 0.13275 | 119.3893 | 119.5541 | 119.426 | 119.4855 | 119.4077 | 120.9366 | 119.4855 | -0.27466 | 119.4855 | 119.4077 | 119.4855 | 119.426 | 120.9366 | -1.5015 | -121.051
4203 | 120.9732 | -119.2383 | 1.6113 | 0.0096895 | 8.578e-06 | 0.0054131 | 0.099619 | -0.024793 | -0.032985 | 0.034069 | 0.027466 | 0.050354 | -0.10529 | 0.14648 | 0.07782 | 0.1236 | -0.045776 | 0.2243 | 1.4603 | -119.7144 | 119.133 | -1.561 | 119.2657 | 119.3848 | -1.5335 | -0.47607 | -0.15106 | 0.13275 | 119.1925 | 119.4626 | 119.3161 | 119.2886 | 119.2657 | 120.6985 | 119.3619 | -0.47607 | 119.2886 | 119.2657 | 119.3619 | 119.3161 | 120.6985 | -1.7166 | -121.3257
4204.75 | 121.0693 | -119.8013 | 1.062 | 0.0096895 | -0.00084602 | 0.0098993 | 0.088724 | -0.023939 | -0.031063 | 0.021251 | 0.11902 | 0.041199 | -0.064087 | 0.1831 | 0.11902 | 0.21515 | -0.18768 | 0.2655 | 1.1124 | -120.0806 | 119.7372 | -1.0208 | 119.9203 | 119.9844 | -0.94299 | -0.27923 | 0.050354 | 0.18311 | 119.6136 | 120.0668 | 119.9203 | 119.8425 | 119.9203 | 120.9137 | 120.0165 | -0.27923 | 119.8425 | 119.9203 | 120.0165 | 119.9203 | 120.9137 | -1.1261 | -121.1426
4206.5 | 120.9686 | -119.902 | 1.0117 | 0.017319 | -0.0031958 | 0.0049859 | 0.13166 | -0.025007 | -0.032558 | 0.057781 | 0.004578 | 0.068665 | -0.12817 | 0.11902 | 0.059509 | 0.11902 | -0.009155 | 0.20599 | 1.1444 | -120.0943 | 119.7739 | -0.94299 | 119.9066 | 120.0211 | -0.95215 | -0.19226 | 0.13275 | 0.13275 | 119.8929 | 120.108 | 119.9615 | 119.9707 | 119.9066 | 121.0464 | 120.0211 | -0.19226 | 119.9707 | 119.9066 | 120.0211 | 119.9615 | 121.0464 | -1.1398 | -121.106
4208.2656 | 121.0144 | -119.0323 | 1.9363 | 0.00206 | -0.0014868 | 0.0045587 | 0.20365 | -0.026716 | -0.030636 | 0.15733 | 0.09613 | 0.050354 | -0.073242 | 0.17853 | 0.045776 | 0.16937 | -0.059509 | 0.27924 | 1.9913 | -119.2154 | 118.959 | -1.886 | 119.1284 | 119.2108 | -1.8906 | -0.18311 | 0.054932 | 0.16937 | 118.9728 | 119.3115 | 119.0781 | 119.0826 | 119.1284 | 121.0236 | 119.2017 | -0.18311 | 119.0826 | 119.1284 | 119.2017 | 119.0781 | 121.0236 | -2.0096 | -121.1517
4210.0156 | 121.0098 | -119.7235 | 1.2634 | -0.013199 | -0.0034094 | 0.0096857 | 0.11692 | -0.026716 | -0.029995 | 0.047313 | 0.10986 | 0.050354 | -0.068665 | 0.20142 | 0.13275 | 0.18768 | -0.1236 | 0.32959 | 1.2131 | -120.0119 | 119.6548 | -1.2131 | 119.8334 | 119.9249 | -1.1307 | -0.28839 | -0.050354 | 0.17853 | 119.5999 | 120.0531 | 119.8563 | 119.7739 | 119.8334 | 120.9366 | 119.9112 | -0.28839 | 119.7739 | 119.8334 | 119.9112 | 119.8563 | 120.9366 | -1.3321 | -121.2753
4211.7656 | 121.1243 | -119.7739 | 1.1536 | 0.00206 | -0.0031958 | 0.0047723 | 0.10453 | -0.026716 | -0.032345 | 0.038768 | 0.086975 | 0.041199 | -0.068665 | 0.14648 | 0.10071 | 0.16937 | -0.14191 | 0.23804 | 1.062 | -120.1996 | 119.7052 | -1.1124 | 119.8608 | 119.9203 | -1.0529 | -0.42572 | -0.091552 | 0.15564 | 119.632 | 120.0119 | 119.8746 | 119.8151 | 119.8608 | 120.8359 | 119.9432 | -0.42572 | 119.8151 | 119.8608 | 119.9432 | 119.8746 | 120.8359 | -1.2222 | -121.3531
4213.4844 | 121.0419 | -119.902 | 1.0162 | 0.0096895 | -0.0017004 | 0.0075495 | 0.10496 | -0.026929 | -0.034481 | 0.027446 | 0 | 0.07782 | -0.11902 | 0.10529 | 0.036621 | 0.086975 | 0.032043 | 0.19684 | 1.0071 | -120.3323 | 119.783 | -0.93841 | 119.902 | 120.0073 | -0.97961 | -0.4303 | -0.009155 | 0.11902 | 119.9341 | 120.0989 | 119.9387 | 119.9799 | 119.902 | 120.9091 | 119.989 | -0.4303 | 119.9799 | 119.902 | 119.989 | 119.9387 | 120.9091 | -1.1353 | -121.3486
4215.2344 | 121.0922 | -120.1218 | 0.82398 | 0.00206 | -0.0010596 | 0.0066949 | 0.09556 | -0.023725 | -0.033626 | 0.016765 | 0.11444 | 0.041199 | -0.068665 | 0.20142 | 0.15106 | 0.20142 | -0.20599 | 0.29755 | 0.89722 | -120.3735 | 120.0531 | -0.78278 | 120.2362 | 120.3232 | -0.67291 | -0.25177 | 0.073242 | 0.18311 | 119.9158 | 120.4193 | 120.2728 | 120.163 | 120.2362 | 121.019 | 120.3232 | -0.25177 | 120.163 | 120.2362 | 120.3232 | 120.2728 | 121.019 | -0.89264 | -121.1975
4217 | 121.1517 | -119.8929 | 1.0574 | 0.017319 | 8.578e-06 | 0.0049859 | 0.19084 | -0.026289 | -0.03384 | 0.1208 | -0.013733 | 0.073242 | -0.11902 | 0.073242 | 0.013733 | 0.059509 | -0.004578 | 0.13733 | 0.86517 | -120.4834 | 119.7739 | -0.98419 | 119.8791 | 119.9661 | -1.0437 | -0.59051 | -0.19226 | 0.10529 | 119.8883 | 120.0302 | 119.9066 | 119.9661 | 119.8791 | 120.7581 | 119.9524 | -0.59051 | 119.9661 | 119.8791 | 119.9524 | 119.9066 | 120.7581 | -1.1765 | -121.5408
4218.7812 | 121.1288 | -120.3644 | 0.61798 | 0.0096895 | 0.0012902 | 0.0028497 | 0.12226 | -0.026716 | -0.033626 | 0.060558 | -0.018311 | 0.09613 | -0.11444 | 0.082397 | 0.045776 | 0.064087 | 0.059509 | 0.16937 | 0.70953 | -120.6985 | 120.2499 | -0.52185 | 120.3461 | 120.4468 | -0.5722 | -0.33417 | 0.091553 | 0.09613 | 120.4239 | 120.5338 | 120.4102 | 120.4605 | 120.3461 | 121.0739 | 120.4285 | -0.33417 | 120.4605 | 120.3461 | 120.4285 | 120.4102 | 121.0739 | -0.73242 | -121.3165
4220.5625 | 121.051 | -120.4742 | 0.57678 | 0.017319 | -0.0044776 | 0.0037043 | 0.10026 | -0.026716 | -0.03149 | 0.03236 | 0.09613 | 0.045776 | -0.082397 | 0.21057 | 0.18768 | 0.18768 | -0.12817 | 0.33417 | 0.6134 | -120.726 | 120.3918 | -0.53101 | 120.5704 | 120.6848 | -0.3891 | -0.25177 | 0.036621 | 0.17853 | 120.3461 | 120.8084 | 120.6619 | 120.52 | 120.5704 | 121.0876 | 120.6619 | -0.25177 | 120.52 | 120.5704 | 120.6619 | 120.6619 | 121.0876 | -0.65918 | -121.3028
4222.3438 | 121.2524 | -120.1675 | 0.72784 | 0.024948 | -0.00063242 | 0.0049859 | 0.68516 | -0.028211 | -0.029568 | 0.61854 | 0.036621 | 0.045776 | -0.091553 | 0.11902 | 0.10529 | 0.16022 | -0.12817 | 0.2243 | 1.1536 | -120.0577 | 120.076 | -0.68207 | 120.2042 | 120.2866 | -0.62256 | 0.10986 | 0.42572 | 0.12817 | 120.0394 | 120.3918 | 120.2728 | 120.2133 | 120.2042 | 121.3211 | 120.3278 | 0.10986 | 120.2133 | 120.2042 | 120.3278 | 120.2728 | 121.3211 | -0.8194 | -120.7855
4224.125 | 121.1243 | -120.3918 | 0.66834 | 0.00206 | -0.0031958 | 0.0037043 | 0.12034 | -0.026075 | -0.034908 | 0.049449 | 0.10529 | 0.027466 | -0.07782 | 0.19684 | 0.17395 | 0.1831 | -0.10986 | 0.3067 | 0.6958 | -120.6848 | 120.314 | -0.64087 | 120.4971 | 120.5887 | -0.49439 | -0.29297 | 0.027466 | 0.18311 | 120.282 | 120.6985 | 120.5658 | 120.4193 | 120.4971 | 121.0876 | 120.575 | -0.29297 | 120.4193 | 120.4971 | 120.575 | 120.5658 | 121.0876 | -0.74616 | -121.3531
4225.8594 | 121.2112 | -120.2911 | 0.70496 | -0.0055695 | -0.0017004 | 0.0077631 | 0.1464 | -0.024793 | -0.034694 | 0.066326 | 0.009155 | 0.073242 | -0.11902 | 0.082397 | 0.018311 | 0.068665 | -0.013733 | 0.13275 | 0.79651 | -120.6482 | 120.1721 | -0.63171 | 120.3003 | 120.3735 | -0.68665 | -0.35706 | 0.091553 | 0.12817 | 120.2774 | 120.4239 | 120.3094 | 120.3644 | 120.3003 | 121.0876 | 120.3598 | -0.35706 | 120.3644 | 120.3003 | 120.3598 | 120.3094 | 121.0876 | -0.82398 | -121.3531
4227.625 | 121.2616 | -119.2383 | 1.6617 | 0.00206 | -0.002555 | 0.0056269 | 0.11585 | -0.024152 | -0.033413 | 0.032573 | 0.10986 | 0.036621 | -0.086975 | 0.1831 | 0.12817 | 0.20142 | -0.19226 | 0.27466 | 1.5106 | -119.5496 | 119.1513 | -1.6251 | 119.3481 | 119.4214 | -1.5335 | -0.31128 | -0.15106 | 0.19684 | 119.046 | 119.5129 | 119.3665 | 119.2749 | 119.3481 | 120.7489 | 119.4397 | -0.31128 | 119.2749 | 119.3481 | 119.4397 | 119.3665 | 120.7489 | -1.7487 | -121.2112
4229.3906 | 121.1563 | -119.2062 | 1.8951 | 0.0096895 | -0.0017004 | 0.0019953 | 0.2592 | -0.024152 | -0.032772 | 0.16075 | -0.013733 | 0.07782 | -0.10071 | 0.10071 | -0.15106 | 0.064087 | 0.050354 | 0.19684 | 2.0096 | -119.6045 | 119.1055 | -1.8173 | 119.1925 | 119.3069 | -2.0462 | -0.39825 | 0.11444 | 0.086975 | 119.2566 | 119.4031 | 119.0552 | 119.2841 | 119.1925 | 121.2158 | 119.2703 | -0.39825 | 119.2841 | 119.1925 | 119.2703 | 119.0552 | 121.2158 | -1.9959 | -121.4996
4231.125 | 120.0485 | -74.9222 | 44.8105 | 0.017319 | 0.00086298 | -0.0005683 | 0.97483 | 0.0029779 | -0.0054282 | 0.96354 | -0.022888 | 0.045776 | -0.13733 | 0.032043 | -0.21973 | 0.013733 | 0.009155 | 0.14648 | 50.9857 | -68.9255 | 74.7849 | -44.7647 | 74.8993 | 74.9542 | -45.0302 | 5.9967 | 6.1752 | 0.11444 | 74.9313 | 75.0687 | 74.7025 | 74.968 | 74.8993 | 125.9079 | 74.9359 | 5.9967 | 74.968 | 74.8993 | 74.9359 | 74.7025 | 125.9079 | -44.9478 | -113.736
4232.875 | 104.7043 | -5.4291 | 90.8478 | 0.00206 | -0.0040502 | 0.0024225 | 0.041513 | 0.038012 | 0.031742 | 0.19236 | 0.050354 | -0.009155 | -0.13275 | 0.14648 | -0.19226 | 0.16479 | -0.2243 | 0.21515 | 114.537 | -4.7195 | 5.2963 | -90.8569 | 5.4794 | 5.5756 | -91.04 | 0.70953 | 23.6893 | 0.18311 | 5.2048 | 5.6442 | 5.2368 | 5.4199 | 5.4794 | 119.9661 | 5.5939 | 0.70953 | 5.4199 | 5.4794 | 5.5939 | 5.2368 | 119.9661 | -90.9805 | -95.5673
4234.625 | 120.2682 | -96.0938 | 23.8586 | 0.0096895 | -0.0049048 | 0.0032769 | 0.031687 | -0.014753 | -0.018246 | 0.0018115 | 0.10071 | 0.027466 | -0.07782 | 0.22888 | 0.16022 | 0.20599 | -0.16022 | 0.31128 | 23.909 | -96.3867 | 96.0159 | -23.8312 | 96.1945 | 96.3226 | -23.6984 | -0.29297 | 0.050354 | 0.17853 | 95.9335 | 96.405 | 96.254 | 96.1212 | 96.1945 | 120.0027 | 96.2997 | -0.29297 | 96.1212 | 96.1945 | 96.2997 | 96.254 | 120.0027 | -23.9365 | -120.2454
4236.375 | 120.4285 | -95.9244 | 24.1699 | 0.0096895 | -0.00041862 | 0.0054131 | 0.041941 | -0.010053 | -0.018886 | 0.0065113 | 0.054932 | 0.059509 | -0.11444 | 0.1236 | 0.050354 | 0.10071 | -0.050354 | 0.20599 | 24.2249 | -96.286 | 95.8099 | -24.1104 | 95.9793 | 96.048 | -24.1196 | -0.36163 | 0.054932 | 0.16937 | 95.874 | 96.1304 | 95.9747 | 95.9839 | 95.9793 | 120.1492 | 96.0251 | -0.36163 | 95.9839 | 95.9793 | 96.0251 | 95.9747 | 120.1492 | -24.2844 | -120.4559
4238.1406 | 120.2911 | -95.842 | 23.9273 | 0.017319 | -0.0040502 | 0.0030633 | 0.040445 | -0.0096259 | -0.017391 | 0.0039477 | -0.009155 | 0.064087 | -0.1236 | 0.07782 | 0.004578 | 0.054932 | 0 | 0.14648 | 24.0372 | -96.2448 | 95.7184 | -23.8632 | 95.8328 | 95.9198 | -23.9227 | -0.40283 | 0.10986 | 0.11444 | 95.842 | 95.9885 | 95.8466 | 95.9061 | 95.8328 | 119.8792 | 95.8969 | -0.40283 | 95.9061 | 95.8328 | 95.8969 | 95.8466 | 119.8792 | -24.0509 | -120.1721
4239.8594 | 117.2104 | -68.2709 | 45.7306 | -0.0055695 | -0.0029822 | 0.0015679 | 6.9721 | -0.0098395 | -0.007778 | 7.0123 | 0.07782 | 0.009155 | -0.086975 | 0.24719 | 0.10986 | 0.21973 | -0.09613 | 0.26093 | 40.7639 | -52.4826 | 68.1839 | -45.7214 | 68.3487 | 68.5181 | -45.6207 | 15.7883 | -4.9667 | 0.16479 | 68.1747 | 68.5318 | 68.3807 | 68.28 | 68.3487 | 109.0347 | 68.4906 | 15.7883 | 68.28 | 68.3487 | 68.4906 | 68.3807 | 109.0347 | -45.8176 | -98.2132
4241.6094 | 104.3701 | -63.5742 | 55.5267 | 0.0096895 | -0.0010596 | 0.0034905 | 0.043222 | 0.0036187 | -0.0041464 | 0.063121 | -0.009155 | 0.059509 | -0.13275 | 0.059509 | -0.10071 | 0.036621 | -0.036621 | 0.10529 | 50.8347 | -69.3375 | 63.4415 | -55.4672 | 63.5651 | 63.6337 | -55.6274 | -5.7632 | -4.6921 | 0.1236 | 63.5376 | 63.6795 | 63.4735 | 63.6337 | 63.5651 | 114.4089 | 63.6108 | -5.7632 | 63.6337 | 63.5651 | 63.6108 | 63.4735 | 114.4089 | -55.6595 | -124.8642
4243.3281 | 120.2774 | -105.0751 | 16.8091 | 0.017319 | -0.002555 | 0.0004999 | 0.045786 | -0.021802 | -0.028286 | 0.021251 | -0.022888 | 0.068665 | -0.1236 | 0.07782 | 0 | 0.064087 | 0.050354 | 0.16479 | 6.2393 | -114.4547 | 104.9515 | -16.7404 | 105.0522 | 105.1529 | -16.8091 | -9.3796 | -10.5698 | 0.10071 | 105.1254 | 105.2399 | 105.0751 | 105.1437 | 105.0522 | 111.3144 | 105.1392 | -9.3796 | 105.1437 | 105.0522 | 105.1392 | 105.0751 | 111.3144 | -16.9327 | -131.2637
4245.0625 | 120.5612 | -25.3738 | 89.1769 | 0.00206 | -0.001914 | 0.0081903 | 0.047708 | 0.025622 | 0.01807 | 0.16651 | -0.027466 | 0.045776 | -0.14648 | 0.059509 | -0.35248 | 0.027466 | 0 | 0.15106 | 95.1187 | -25.6165 | 25.2274 | -89.1312 | 25.3464 | 25.4333 | -89.5294 | -0.24261 | 5.9418 | 0.11902 | 25.3738 | 25.5249 | 25.0214 | 25.4196 | 25.3464 | 120.4926 | 25.4013 | -0.24261 | 25.4196 | 25.3464 | 25.4013 | 25.0214 | 120.4926 | -89.3234 | -114.7934
4246.7812 | 89.5615 | -0.10986 | 82.8415 | 0.017319 | -0.0021276 | 0.0054131 | 0.049631 | 0.039507 | 0.029179 | 0.19877 | -0.027466 | 0.027466 | -0.15564 | 0.064087 | 0.064087 | 0.050354 | 0 | 0.032043 | 113.3835 | -7.4478 | -0.045777 | -82.814 | 0.082397 | 0.17395 | -82.7774 | -7.338 | 30.542 | 0.12817 | 0.10986 | 0.14191 | 0.17395 | 0.13733 | 0.082397 | 113.4933 | 0.16022 | -7.338 | 0.13733 | 0.082397 | 0.16022 | 0.17395 | 113.4933 | -82.9971 | -90.2893
4248.5 | 110.6461 | -7.8461 | 88.2385 | 0.0096895 | -0.002555 | 0.0051995 | 0.054972 | 0.038439 | 0.029606 | 0.20582 | -0.004578 | 0.022888 | -0.12817 | 0.11902 | 0.09613 | 0.07782 | -0.082397 | 0.068665 | 113.2004 | -7.6904 | 7.7179 | -88.2156 | 7.8415 | 7.9651 | -88.1424 | 0.15564 | 24.9619 | 0.1236 | 7.7637 | 7.9147 | 7.9422 | 7.869 | 7.8415 | 121.0464 | 7.9239 | 0.15564 | 7.869 | 7.8415 | 7.9239 | 7.9422 | 121.0464 | -88.3667 | -95.929
4250.3281 | 120.1767 | -10.5835 | 109.4421 | 0.017319 | -0.0034094 | 0.0024225 | 0.2357 | 0.03374 | 0.031315 | 0.28807 | 0.041199 | 0.004578 | -0.09613 | 0.13733 | 0.059509 | 0.13733 | -0.20599 | 0.11444 | 110.9024 | -9.9472 | 10.4874 | -109.4376 | 10.6247 | 10.7208 | -109.3826 | 0.63629 | 1.4603 | 0.13733 | 10.3775 | 10.6979 | 10.643 | 10.5881 | 10.6247 | 121.4859 | 10.7208 | 0.63629 | 10.5881 | 10.6247 | 10.7208 | 10.643 | 121.4859 | -109.5383 | -119.3893
4252.1094 | 119.8837 | -117.1555 | 2.211 | -0.0055695 | -0.00063242 | 0.0060541 | 0.093637 | -0.023511 | -0.029781 | 0.021251 | 0.059509 | 0.032043 | -0.09613 | 0.11902 | 0.059509 | 0.14648 | -0.10529 | 0.22888 | 2.3621 | -117.5446 | 117.0593 | -2.179 | 117.215 | 117.2745 | -2.1515 | -0.3891 | 0.15106 | 0.15564 | 117.0502 | 117.3843 | 117.215 | 117.1875 | 117.215 | 119.5175 | 117.3019 | -0.3891 | 117.1875 | 117.215 | 117.3019 | 117.215 | 119.5175 | -2.3071 | -119.7556
4253.8906 | 120.2637 | -119.0277 | 0.78278 | 0.0096895 | -0.0023412 | 0.0056269 | 0.098123 | -0.023298 | -0.029995 | 0.019756 | 0.082397 | 0.050354 | -0.064087 | 0.16937 | 0.17395 | 0.17395 | -0.16022 | 0.25635 | 0.82855 | -119.4397 | 118.9636 | -0.73242 | 119.1101 | 119.1971 | -0.60883 | -0.41199 | 0.045776 | 0.14648 | 118.8675 | 119.2841 | 119.2017 | 119.0781 | 119.1101 | 119.8563 | 119.2017 | -0.41199 | 119.0781 | 119.1101 | 119.2017 | 119.2017 | 119.8563 | -0.84686 | -120.2225
4255.6094 | 120.6665 | -119.6091 | 0.70953 | 0.00206 | -0.0023412 | 0.0066949 | 0.10304 | -0.026075 | -0.03149 | 0.024669 | 0.027466 | 0.059509 | -0.11444 | 0.10986 | 0.07782 | 0.07782 | 0.004578 | 0.21057 | 0.5722 | -120.2133 | 119.4946 | -0.65002 | 119.6365 | 119.7189 | -0.63171 | -0.60425 | -0.13733 | 0.14191 | 119.6136 | 119.8196 | 119.6869 | 119.6686 | 119.6365 | 120.1813 | 119.6869 | -0.60425 | 119.6686 | 119.6365 | 119.6869 | 119.6869 | 120.1813 | -0.82398 | -120.9229
4257.3906 | 120.488 | -119.5908 | 0.66376 | 0.0096895 | 0.00043578 | 0.0075495 | 0.10304 | -0.023511 | -0.030636 | 0.020824 | 0.12817 | 0.022888 | -0.064087 | 0.19684 | 0.1236 | 0.20142 | -0.20599 | 0.31128 | 0.71411 | -119.8013 | 119.5267 | -0.64087 | 119.7189 | 119.7876 | -0.54016 | -0.21057 | 0.050354 | 0.19226 | 119.3848 | 119.902 | 119.7144 | 119.6136 | 119.7189 | 120.3049 | 119.7922 | -0.21057 | 119.6136 | 119.7189 | 119.7922 | 119.7144 | 120.3049 | -0.72784 | -120.4651
4259.1406 | 119.8105 | -119.101 | 0.32044 | 0.024948 | -0.0023412 | 0.0028497 | 0.1041 | -0.021802 | -0.033199 | 0.020183 | 0.022888 | 0.068665 | -0.12817 | 0.10071 | 0.009155 | 0.064087 | -0.018311 | 0.19226 | 0.37994 | -119.545 | 118.9728 | -0.25177 | 119.1238 | 119.2017 | -0.31128 | -0.44403 | 0.059509 | 0.15106 | 119.0826 | 119.2932 | 119.1101 | 119.1696 | 119.1238 | 119.4809 | 119.165 | -0.44403 | 119.1696 | 119.1238 | 119.165 | 119.1101 | 119.4809 | -0.44861 | -119.8654
4260.8438 | 120.4971 | -119.7418 | 0.37994 | 0.017319 | -0.0014868 | 0.0071221 | 0.087656 | -0.027784 | -0.031917 | 0.010356 | 0.045776 | 0.068665 | -0.086975 | 0.16022 | 0.10986 | 0.15564 | -0.1236 | 0.28381 | 0.43945 | -120.1492 | 119.6548 | -0.31128 | 119.7876 | 119.902 | -0.27008 | -0.40741 | 0.059509 | 0.13275 | 119.6182 | 120.0256 | 119.8517 | 119.8105 | 119.7876 | 120.1813 | 119.8975 | -0.40741 | 119.8105 | 119.7876 | 119.8975 | 119.8517 | 120.1813 | -0.46692 | -120.5292
4262.5625 | 120.5338 | -120.0119 | 0.33417 | 0.00206 | 0.00043578 | 0.0034905 | 0.091715 | -0.027784 | -0.028713 | 0.011638 | 0.082397 | 0.041199 | -0.073242 | 0.21057 | 0.13733 | 0.21973 | -0.16022 | 0.3479 | 0.37537 | -120.3415 | 119.9387 | -0.29297 | 120.0943 | 120.2225 | -0.19684 | -0.32959 | 0.041199 | 0.15564 | 119.8517 | 120.3598 | 120.1492 | 120.0531 | 120.0943 | 120.3873 | 120.2316 | -0.32959 | 120.0531 | 120.0943 | 120.2316 | 120.1492 | 120.3873 | -0.40741 | -120.6757
4264.2969 | 120.639 | -120.108 | 0.27466 | 0.00206 | -0.002555 | 0.0049859 | 0.09791 | -0.025648 | -0.032131 | 0.015911 | 0.10071 | 0.032043 | -0.064087 | 0.1831 | 0.11444 | 0.16937 | -0.18768 | 0.27924 | 0.33417 | -120.4056 | 120.0439 | -0.24262 | 120.2087 | 120.2911 | -0.16022 | -0.29755 | 0.059509 | 0.1648 | 119.9203 | 120.3873 | 120.2225 | 120.1401 | 120.2087 | 120.4422 | 120.2774 | -0.29755 | 120.1401 | 120.2087 | 120.2774 | 120.2225 | 120.4422 | -0.33875 | -120.6802
4266 | 120.6345 | -120.1904 | 0.29755 | 0.017319 | -0.00020502 | 0.0069085 | 0.10902 | -0.026502 | -0.032131 | 0.019969 | 0.004578 | 0.10986 | -0.11444 | 0.10071 | 0.027466 | 0.059509 | 0.050354 | 0.19684 | 0.36621 | -120.5063 | 120.076 | -0.18768 | 120.195 | 120.2911 | -0.27008 | -0.31586 | 0.068665 | 0.11902 | 120.2408 | 120.3873 | 120.2179 | 120.3003 | 120.195 | 120.5566 | 120.2499 | -0.31586 | 120.3003 | 120.195 | 120.2499 | 120.2179 | 120.5566 | -0.41199 | -120.8038
4267.7656 | 120.6116 | -120.3049 | 0.31586 | 0.0096895 | -0.0017004 | 0.0017817 | 0.10005 | -0.02757 | -0.03384 | 0.017833 | 0.10986 | 0.041199 | -0.073242 | 0.21515 | 0.14648 | 0.1831 | -0.10986 | 0.32044 | 0.32959 | -120.5063 | 120.2316 | -0.27466 | 120.4147 | 120.52 | -0.16937 | -0.20142 | 0.013733 | 0.18311 | 120.195 | 120.6253 | 120.4514 | 120.3461 | 120.4147 | 120.6345 | 120.488 | -0.20142 | 120.3461 | 120.4147 | 120.488 | 120.4514 | 120.6345 | -0.3891 | -120.8221
4269.4844 | 120.6757 | -120.1996 | 0.33875 | 0.00206 | -0.0021276 | 0.0034905 | 0.11521 | -0.029493 | -0.031917 | 0.034496 | 0.068665 | 0.045776 | -0.091553 | 0.16022 | 0.07782 | 0.10986 | -0.013733 | 0.24261 | 0.36163 | -120.5475 | 120.108 | -0.29297 | 120.2682 | 120.3598 | -0.26093 | -0.3479 | 0.022888 | 0.16022 | 120.1859 | 120.4422 | 120.2774 | 120.2454 | 120.2682 | 120.5612 | 120.3094 | -0.3479 | 120.2454 | 120.2682 | 120.3094 | 120.2774 | 120.5612 | -0.4303 | -120.8862
4271.2031 | 120.6573 | -120.2499 | 0.35248 | 0.0096895 | -0.00063242 | 0.0045587 | 0.11991 | -0.025434 | -0.033199 | 0.025951 | 0.054932 | 0.059509 | -0.12817 | 0.16022 | 0.073242 | 0.13275 | -0.045776 | 0.23346 | 0.37994 | -120.5338 | 120.1218 | -0.29297 | 120.3049 | 120.4102 | -0.27924 | -0.28381 | 0.027466 | 0.18311 | 120.2042 | 120.4834 | 120.3232 | 120.3094 | 120.3049 | 120.6299 | 120.3827 | -0.28381 | 120.3094 | 120.3049 | 120.3827 | 120.3232 | 120.6299 | -0.48065 | -120.8862
4272.9219 | 120.7214 | -120.1904 | 0.42572 | 0.0096895 | -0.0023412 | 0.0056269 | 0.23506 | -0.024366 | -0.03384 | 0.15242 | 0.041199 | 0.068665 | -0.10986 | 0.13733 | 0.004578 | 0.09613 | -0.022888 | 0.17395 | 0.49439 | -120.4468 | 120.0806 | -0.35706 | 120.2316 | 120.3278 | -0.42114 | -0.25635 | 0.068665 | 0.15106 | 120.1675 | 120.3644 | 120.195 | 120.2591 | 120.2316 | 120.6848 | 120.2866 | -0.25635 | 120.2591 | 120.2316 | 120.2866 | 120.195 | 120.6848 | -0.53558 | -120.8725
4274.6406 | 120.7031 | -120.3003 | 0.35248 | 0.00206 | -0.0014868 | 0.0013543 | 0.13743 | -0.025007 | -0.034267 | 0.056072 | 0 | 0.09613 | -0.1236 | 0.10529 | 0.041199 | 0.07782 | 0.032043 | 0.1831 | 0.46234 | -120.5338 | 120.1767 | -0.25635 | 120.3003 | 120.4056 | -0.31128 | -0.23346 | 0.10986 | 0.1236 | 120.3323 | 120.4834 | 120.3415 | 120.3964 | 120.3003 | 120.7626 | 120.3781 | -0.23346 | 120.3964 | 120.3003 | 120.3781 | 120.3415 | 120.7626 | -0.47607 | -120.8862
4276.4219 | 120.7947 | -120.2866 | 0.36163 | 0.0096895 | -0.00084602 | 0.0043451 | 0.12141 | -0.026929 | -0.032985 | 0.032573 | -0.018311 | 0.07782 | -0.11902 | 0.09613 | 0.022888 | 0.068665 | 0.041199 | 0.1831 | 0.36621 | -120.6528 | 120.1675 | -0.28381 | 120.2682 | 120.3827 | -0.33874 | -0.36621 | 0.004578 | 0.10071 | 120.3278 | 120.4697 | 120.3094 | 120.3644 | 120.2682 | 120.6528 | 120.3552 | -0.36621 | 120.3644 | 120.2682 | 120.3552 | 120.3094 | 120.6528 | -0.48065 | -121.0144
4278.1562 | 120.7535 | -120.4285 | 0.29755 | 0.00206 | -0.0023412 | 0.0032769 | 0.14341 | -0.028211 | -0.030422 | 0.060344 | 0.11902 | 0.041199 | -0.07782 | 0.20142 | 0.14648 | 0.21515 | -0.13733 | 0.33875 | 0.31128 | -120.6573 | 120.3506 | -0.25635 | 120.5475 | 120.6299 | -0.15106 | -0.22888 | 0.013733 | 0.19684 | 120.2911 | 120.7672 | 120.575 | 120.4697 | 120.5475 | 120.7397 | 120.6436 | -0.22888 | 120.4697 | 120.5475 | 120.6436 | 120.575 | 120.7397 | -0.37537 | -120.9549
4279.875 | 120.8359 | -120.3735 | 0.30212 | 0.00206 | -0.001914 | 0.0056269 | 0.11158 | -0.027143 | -0.03149 | 0.028728 | 0.091553 | 0.032043 | -0.086975 | 0.20142 | 0.15106 | 0.21973 | -0.13733 | 0.34332 | 0.31586 | -120.6802 | 120.2866 | -0.27008 | 120.4651 | 120.575 | -0.15106 | -0.3067 | 0.013733 | 0.17853 | 120.2362 | 120.7169 | 120.5246 | 120.4056 | 120.4651 | 120.6894 | 120.5933 | -0.3067 | 120.4056 | 120.4651 | 120.5933 | 120.5246 | 120.6894 | -0.3891 | -120.9824
4281.6406 | 120.8633 | -120.3232 | 0.36621 | 0.0096895 | -0.0031958 | 0.0073359 | 0.37263 | -0.028852 | -0.03149 | 0.287 | 0.10529 | 0.045776 | -0.07782 | 0.21057 | 0.14191 | 0.20142 | -0.13733 | 0.32959 | 0.35248 | -120.6024 | 120.2454 | -0.32044 | 120.4285 | 120.5338 | -0.2243 | -0.27924 | -0.013733 | 0.18311 | 120.1859 | 120.6528 | 120.4651 | 120.369 | 120.4285 | 120.6757 | 120.5246 | -0.27924 | 120.369 | 120.4285 | 120.5246 | 120.4651 | 120.6757 | -0.44403 | -120.9686
4283.3906 | 120.9091 | -120.4285 | 0.2655 | 0.00206 | 0.00022218 | 0.0081903 | 0.12205 | -0.026929 | -0.030849 | 0.041759 | 0.11902 | 0.027466 | -0.068665 | 0.1831 | 0.11902 | 0.20142 | -0.16937 | 0.28381 | 0.3067 | -120.7077 | 120.3598 | -0.23804 | 120.5475 | 120.6116 | -0.14648 | -0.27924 | 0.041199 | 0.18768 | 120.2591 | 120.7123 | 120.5475 | 120.4559 | 120.5475 | 120.7352 | 120.6299 | -0.27924 | 120.4559 | 120.5475 | 120.6299 | 120.5475 | 120.7352 | -0.33417 | -120.9732
4285.125 | 120.845 | -120.5017 | 0.29297 | 0.017319 | -0.0010596 | 0.0088311 | 0.14021 | -0.02522 | -0.032985 | 0.094524 | 0.045776 | 0.073242 | -0.11444 | 0.15564 | 0.082397 | 0.11902 | -0.054932 | 0.25177 | 0.37079 | -120.7672 | 120.3873 | -0.21973 | 120.5475 | 120.6573 | -0.21057 | -0.2655 | 0.07782 | 0.16022 | 120.4468 | 120.7535 | 120.5841 | 120.575 | 120.5475 | 120.8725 | 120.6207 | -0.2655 | 120.575 | 120.5475 | 120.6207 | 120.5841 | 120.8725 | -0.40741 | -121.0602
4286.875 | 120.9503 | -120.4559 | 0.27924 | 0.00206 | -0.0029822 | 0.0022089 | 0.12589 | -0.026929 | -0.029568 | 0.048168 | 0.086975 | 0.036621 | -0.073242 | 0.17395 | 0.10529 | 0.16479 | -0.14648 | 0.2655 | 0.32501 | -120.7764 | 120.3827 | -0.24261 | 120.5429 | 120.6299 | -0.17395 | -0.32043 | 0.045776 | 0.16022 | 120.3094 | 120.7214 | 120.5612 | 120.4926 | 120.5429 | 120.7809 | 120.6207 | -0.32043 | 120.4926 | 120.5429 | 120.6207 | 120.5612 | 120.7809 | -0.35248 | -121.0556
4288.6406 | 120.9091 | -120.4971 | 0.28839 | 0.017319 | -0.0023412 | 0.0028497 | 0.12931 | -0.02757 | -0.031704 | 0.043468 | 0.10529 | 0.018311 | -0.064087 | 0.20599 | 0.11444 | 0.21515 | -0.1831 | 0.29755 | 0.31128 | -120.7443 | 120.433 | -0.27008 | 120.6024 | 120.7031 | -0.17395 | -0.24719 | 0.022888 | 0.16937 | 120.314 | 120.7947 | 120.6116 | 120.5154 | 120.6024 | 120.8084 | 120.7123 | -0.24719 | 120.5154 | 120.6024 | 120.7123 | 120.6116 | 120.8084 | -0.35248 | -121.0327
4290.3594 | 121.0602 | -120.3644 | 0.40283 | 0.0096895 | -0.002555 | 0.0015679 | 0.23463 | -0.026502 | -0.032985 | 0.10392 | 0.082397 | 0.045776 | -0.086975 | 0.16937 | 0.10529 | 0.16479 | -0.14191 | 0.27008 | 0.32959 | -120.7443 | 120.2774 | -0.35706 | 120.4468 | 120.5338 | -0.29755 | -0.37994 | -0.073242 | 0.16937 | 120.2225 | 120.6345 | 120.4697 | 120.4102 | 120.4468 | 120.694 | 120.5292 | -0.37994 | 120.4102 | 120.4468 | 120.5292 | 120.4697 | 120.694 | -0.48981 | -121.1472
4292.0938 | 120.9412 | -120.5109 | 0.28839 | 0.017319 | -0.0031958 | 0.0009271 | 0.12654 | -0.028425 | -0.033626 | 0.043468 | 0.082397 | 0.036621 | -0.064087 | 0.1831 | 0.10071 | 0.15564 | -0.054932 | 0.28381 | 0.32959 | -120.8176 | 120.4468 | -0.25177 | 120.5933 | 120.694 | -0.18768 | -0.3067 | 0.041199 | 0.14648 | 120.4559 | 120.7947 | 120.6116 | 120.5475 | 120.5933 | 120.8405 | 120.6665 | -0.3067 | 120.5475 | 120.5933 | 120.6665 | 120.6116 | 120.8405 | -0.35248 | -121.106
4293.8125 | 120.9274 | -120.5521 | 0.27008 | 0.0096895 | -0.0021276 | 0.0058405 | 0.11884 | -0.027357 | -0.031704 | 0.034709 | 0.10986 | 0.022888 | -0.054932 | 0.2243 | 0.16479 | 0.21973 | -0.14191 | 0.35248 | 0.29755 | -120.7947 | 120.4971 | -0.24719 | 120.6619 | 120.7764 | -0.10529 | -0.24262 | 0.027465 | 0.16479 | 120.4102 | 120.9045 | 120.7169 | 120.575 | 120.6619 | 120.8496 | 120.7718 | -0.24262 | 120.575 | 120.6619 | 120.7718 | 120.7169 | 120.8496 | -0.32501 | -121.0648
4295.5469 | 120.8588 | -118.8629 | 1.6617 | 0.017319 | -0.001914 | 0.0049859 | 0.29231 | -0.026075 | -0.029781 | 0.29896 | 0.082397 | 0.054932 | -0.07782 | 0.17395 | 0.13275 | 0.19684 | -0.12817 | 0.31586 | 0.48981 | -120.4742 | 118.7851 | -1.6068 | 118.9453 | 119.0369 | -1.5289 | -1.6113 | -1.1719 | 0.16022 | 118.7347 | 119.1788 | 118.9957 | 118.9178 | 118.9453 | 119.3527 | 119.0598 | -1.6113 | 118.9178 | 118.9453 | 119.0598 | 118.9957 | 119.3527 | -1.7395 | -122.1359
4297.2812 | 120.2591 | -94.3405 | 25.3738 | 0.0096895 | -0.00041862 | 0.0047723 | 0.6341 | -0.011976 | -0.018032 | 0.59098 | 0.086975 | 0.027466 | -0.09613 | 0.19226 | 0.11444 | 0.17853 | -0.15106 | 0.31128 | 25.4334 | -94.725 | 94.2444 | -25.3464 | 94.4275 | 94.5328 | -25.2594 | -0.38452 | 0.05951 | 0.1831 | 94.1895 | 94.6518 | 94.455 | 94.368 | 94.4275 | 119.7739 | 94.519 | -0.38452 | 94.368 | 94.4275 | 94.519 | 94.455 | 119.7739 | -25.47 | -120.0989
4299 | 120.7626 | -113.887 | 6.3583 | 0.017319 | -0.0031958 | 0.0064813 | 0.10902 | -0.019666 | -0.027859 | 0.092601 | 0.050354 | 0.032043 | -0.09613 | 0.14648 | 0.059509 | 0.14191 | -0.11902 | 0.23804 | 6.4407 | -114.2715 | 113.7909 | -6.3263 | 113.9374 | 114.0335 | -6.2988 | -0.38452 | 0.082398 | 0.14648 | 113.768 | 114.1251 | 113.9465 | 113.9191 | 113.9374 | 120.3278 | 114.0289 | -0.38452 | 113.9191 | 113.9374 | 114.0289 | 113.9465 | 120.3278 | -6.4545 | -120.6299
4300.7188 | 120.8038 | -109.8633 | 10.4965 | 0.0096895 | -0.0029822 | 0.0034905 | 0.041727 | -0.016889 | -0.025081 | 0.0095019 | 0.11902 | 0.032043 | -0.082397 | 0.20142 | 0.11902 | 0.18768 | -0.19684 | 0.28839 | 10.5331 | -110.2341 | 109.7809 | -10.4645 | 109.9823 | 110.0647 | -10.3775 | -0.37079 | 0.036621 | 0.20142 | 109.6664 | 110.1517 | 109.9823 | 109.8953 | 109.9823 | 120.3964 | 110.051 | -0.37079 | 109.8953 | 109.9823 | 110.051 | 109.9823 | 120.3964 | -10.5789 | -120.7306
4302.4531 | 116.7709 | -93.2281 | 23.5336 | 0.00206 | -0.0010596 | 0.012035 | 6.9721 | -0.017744 | -0.036617 | 7.0123 | 0.11444 | 0.032043 | -0.073242 | 0.10529 | -0.004578 | 0.086975 | -0.26093 | 0.23804 | 7.457 | -94.899 | 93.1549 | -23.5016 | 93.3426 | 93.3334 | -23.5382 | -1.6708 | -16.0767 | 0.18768 | 92.9672 | 93.4662 | 93.2236 | 93.2602 | 93.3426 | 100.6851 | 93.3151 | -1.6708 | 93.2602 | 93.3426 | 93.3151 | 93.2236 | 100.6851 | -23.6069 | -118.4326
4304.1875 | 120.4788 | -94.6609 | 25.1541 | 0.00206 | -0.00041862 | 0.0049859 | 0.039377 | -0.010053 | -0.018032 | 0.0033069 | -0.009155 | 0.082397 | -0.11902 | 0.086975 | -0.009155 | 0.054932 | -0.045776 | 0.12817 | 25.383 | -95.0226 | 94.5419 | -25.0717 | 94.6518 | 94.7479 | -25.1633 | -0.36163 | 0.22888 | 0.10986 | 94.6152 | 94.7891 | 94.6518 | 94.7433 | 94.6518 | 120.0439 | 94.7159 | -0.36163 | 94.7433 | 94.6518 | 94.7159 | 94.6518 | 120.0439 | -25.2731 | -120.1767
4305.9062 | 120.6162 | -94.4824 | 25.7767 | 0.0096895 | -0.00020502 | 0.0039179 | 0.043863 | -0.010908 | -0.019314 | 0.085765 | 0.032043 | 0.068665 | -0.11444 | 0.13733 | 0.041199 | 0.10529 | -0.027466 | 0.20142 | 25.8453 | -94.812 | 94.368 | -25.708 | 94.5145 | 94.6198 | -25.7355 | -0.32959 | 0.068665 | 0.14648 | 94.455 | 94.6838 | 94.5236 | 94.5511 | 94.5145 | 120.3278 | 94.5877 | -0.32959 | 94.5511 | 94.5145 | 94.5877 | 94.5236 | 120.3278 | -25.8911 | -120.5887
4307.6406 | 120.8038 | -111.763 | 8.4961 | 0.0096895 | 0.00043578 | 0.012035 | 0.039591 | -0.019453 | -0.026577 | 0.0097157 | 0.036621 | 0.068665 | -0.10529 | 0.12817 | 0.059509 | 0.11902 | -0.12817 | 0.21057 | 8.5922 | -112.1841 | 111.6577 | -8.4274 | 111.7996 | 111.8912 | -8.4366 | -0.42114 | 0.09613 | 0.14191 | 111.6348 | 111.9736 | 111.8225 | 111.8317 | 111.7996 | 120.3552 | 111.882 | -0.42114 | 111.8317 | 111.7996 | 111.882 | 111.8225 | 120.3552 | -8.6014 | -120.6802
4309.3906 | 120.8588 | -111.8454 | 8.551 | 0.00206 | -0.00041862 | 0.0037043 | 0.037241 | -0.022016 | -0.024868 | 0.010143 | 0.045776 | 0.059509 | -0.073242 | 0.15564 | 0.082397 | 0.15106 | -0.12817 | 0.23346 | 8.4457 | -112.413 | 111.7722 | -8.4915 | 111.8912 | 112.001 | -8.4686 | -0.56763 | -0.10528 | 0.11902 | 111.7172 | 112.0789 | 111.9278 | 111.9049 | 111.8912 | 120.2911 | 111.9965 | -0.56763 | 111.9049 | 111.8912 | 111.9965 | 111.9278 | 120.2911 | -8.6243 | -120.9641
4311.125 | 120.932 | -112.9257 | 7.4524 | 0.017319 | -0.0021276 | 0.0054131 | 0.043436 | -0.023084 | -0.027004 | 0.011638 | 0.027466 | 0.041199 | -0.091553 | 0.15564 | 0.064087 | 0.13733 | -0.10071 | 0.24261 | 7.5577 | -113.3057 | 112.8342 | -7.4112 | 112.9532 | 113.0814 | -7.3883 | -0.37994 | 0.10529 | 0.11902 | 112.825 | 113.1683 | 112.9898 | 112.9669 | 112.9532 | 120.4834 | 113.063 | -0.37994 | 112.9669 | 112.9532 | 113.063 | 112.9898 | 120.4834 | -7.5439 | -120.7581
4312.8594 | 120.9274 | -113.7634 | 6.7062 | 0.017319 | 0.00086298 | 0.0062677 | 0.051126 | -0.022443 | -0.029354 | 0.014629 | 0.009155 | 0.068665 | -0.12817 | 0.091553 | -0.018311 | 0.068665 | -0.022888 | 0.14191 | 6.8298 | -114.1479 | 113.6353 | -6.6376 | 113.7726 | 113.855 | -6.7245 | -0.38452 | 0.1236 | 0.13733 | 113.7405 | 113.9053 | 113.7451 | 113.8321 | 113.7726 | 120.5933 | 113.8321 | -0.38452 | 113.8321 | 113.7726 | 113.8321 | 113.7451 | 120.5933 | -6.8344 | -120.8542
4314.625 | 120.9778 | -114.2395 | 6.2622 | 0.00206 | 0.00022218 | 0.0058405 | 0.040872 | -0.023298 | -0.028072 | 0.012279 | 0.036621 | 0.041199 | -0.082397 | 0.16022 | 0.068665 | 0.13733 | -0.1236 | 0.25635 | 6.4041 | -114.5462 | 114.1571 | -6.221 | 114.2761 | 114.3997 | -6.1935 | -0.3067 | 0.14191 | 0.11902 | 114.1159 | 114.4959 | 114.3082 | 114.2807 | 114.2761 | 120.6436 | 114.3768 | -0.3067 | 114.2807 | 114.2761 | 114.3768 | 114.3082 | 120.6436 | -6.3446 | -120.8084
4316.3594 | 120.4056 | -117.4301 | 2.623 | 0.00206 | 0.0012902 | 0.0049859 | 0.055826 | -0.020948 | -0.030422 | 0.021892 | 0.022888 | 0.086975 | -0.11902 | 0.10071 | 0 | 0.09613 | -0.086975 | 0.15564 | 2.7054 | -117.8009 | 117.3111 | -2.536 | 117.453 | 117.5308 | -2.623 | -0.37079 | 0.082397 | 0.14191 | 117.3431 | 117.5858 | 117.4301 | 117.5171 | 117.453 | 120.1355 | 117.5262 | -0.37079 | 117.5171 | 117.453 | 117.5262 | 117.4301 | 120.1355 | -2.742 | -120.4239
4318.0938 | 120.9641 | -116.2903 | 4.2526 | 0.017319 | -0.0031958 | 0.0094721 | 0.043222 | -0.023298 | -0.025509 | 0.011852 | 0.11902 | 0.027466 | -0.073242 | 0.16937 | 0.091553 | 0.19226 | -0.1831 | 0.26093 | 4.3167 | -116.6336 | 116.217 | -4.2252 | 116.4093 | 116.4597 | -4.1611 | -0.34332 | 0.064086 | 0.19226 | 116.1072 | 116.5512 | 116.3818 | 116.3177 | 116.4093 | 120.607 | 116.4825 | -0.34332 | 116.3177 | 116.4093 | 116.4825 | 116.3818 | 120.607 | -4.3259 | -120.8862
4319.8125 | 120.726 | -118.895 | 1.5793 | 0.0096895 | -0.00041862 | 0.0028497 | 0.042795 | -0.023725 | -0.031277 | 0.014415 | 0.059509 | 0.054932 | -0.11902 | 0.14648 | 0.050354 | 0.1236 | -0.050354 | 0.21057 | 1.6525 | -119.2337 | 118.7759 | -1.5244 | 118.9545 | 119.0414 | -1.5289 | -0.33875 | 0.073242 | 0.17853 | 118.8446 | 119.1055 | 118.9453 | 118.9499 | 118.9545 | 120.5475 | 119.0186 | -0.33875 | 118.9499 | 118.9545 | 119.0186 | 118.9453 | 120.5475 | -1.6983 | -120.813
4321.5312 | 120.6802 | -117.865 | 2.5955 | 0.0096895 | -0.0038366 | 0.0004999 | 0.040018 | -0.024152 | -0.028499 | 0.06483 | 0.050354 | 0.073242 | -0.11444 | 0.1236 | 0.004578 | 0.11902 | -0.041199 | 0.18768 | 2.6413 | -118.1534 | 117.7505 | -2.5223 | 117.9153 | 117.9886 | -2.5909 | -0.28839 | 0.045776 | 0.16479 | 117.8238 | 118.0527 | 117.8696 | 117.9382 | 117.9153 | 120.5063 | 117.984 | -0.28839 | 117.9382 | 117.9153 | 117.984 | 117.8696 | 120.5063 | -2.71 | -120.7489
4323.25 | 120.7855 | -119.0277 | 1.4511 | 0.0096895 | 0.00043578 | 0.0047723 | 0.035532 | -0.023084 | -0.030636 | 0.0056567 | 0.09613 | 0.032043 | -0.064087 | 0.17853 | 0.10071 | 0.19226 | -0.19684 | 0.26093 | 1.3733 | -119.4397 | 118.9636 | -1.4191 | 119.1238 | 119.2062 | -1.3504 | -0.41199 | -0.07782 | 0.16022 | 118.8309 | 119.2886 | 119.1284 | 119.0598 | 119.1238 | 120.401 | 119.22 | -0.41199 | 119.0598 | 119.1238 | 119.22 | 119.1284 | 120.401 | -1.5152 | -120.8908
4325 | 120.8679 | -114.9811 | 5.5893 | 0.00206 | 8.578e-06 | 0.0028497 | 0.039804 | -0.024152 | -0.028499 | 0.22483 | -0.018311 | 0.073242 | -0.13275 | 0.082397 | -0.14191 | 0.068665 | 0.050354 | 0.15106 | 5.6717 | -115.274 | 114.8483 | -5.5161 | 114.9628 | 115.0635 | -5.7312 | -0.29297 | 0.082398 | 0.11444 | 115.0314 | 115.1321 | 114.8392 | 115.0543 | 114.9628 | 120.6528 | 115.0497 | -0.29297 | 115.0543 | 114.9628 | 115.0497 | 114.8392 | 120.6528 | -5.722 | -120.8633
4326.7344 | 120.0027 | -118.4509 | 1.3046 | 0.017319 | -0.004264 | 0.0030633 | 0.036173 | -0.02458 | -0.028927 | 0.033428 | 0.1236 | 0.027466 | -0.082397 | 0.19684 | 0.10986 | 0.2243 | -0.13733 | 0.32501 | 1.3596 | -118.7256 | 118.3685 | -1.2772 | 118.5745 | 118.6478 | -1.1948 | -0.27466 | 0.054932 | 0.20599 | 118.3136 | 118.7759 | 118.5608 | 118.4784 | 118.5745 | 119.8105 | 118.6752 | -0.27466 | 118.4784 | 118.5745 | 118.6752 | 118.5608 | 119.8105 | -1.387 | -120.0302
4328.4531 | 120.0119 | -112.2437 | 7.1823 | 0.017319 | -0.0010596 | 0.0060541 | 0.029978 | -0.021802 | -0.025509 | -0.00011114 | 0.045776 | 0.045776 | -0.086975 | 0.1236 | 0.064087 | 0.13733 | -0.10071 | 0.23346 | 7.4799 | -112.468 | 112.1567 | -7.1365 | 112.2894 | 112.3672 | -7.1182 | -0.22431 | 0.29755 | 0.13275 | 112.1429 | 112.4771 | 112.3077 | 112.2894 | 112.2894 | 119.7235 | 112.381 | -0.22431 | 112.2894 | 112.2894 | 112.381 | 112.3077 | 119.7235 | -7.2693 | -119.6503
4330.1875 | 119.7464 | -114.1434 | 5.3192 | 0.017319 | -0.0027686 | 0.0013543 | 0.039591 | -0.020521 | -0.028713 | 0.0045887 | 0.004578 | 0.059509 | -0.12817 | 0.1236 | 0.032043 | 0.086975 | -0.009155 | 0.19684 | 5.3192 | -114.4913 | 114.0152 | -5.2597 | 114.1479 | 114.267 | -5.2872 | -0.3479 | 0 | 0.13275 | 114.1342 | 114.3402 | 114.1754 | 114.2029 | 114.1479 | 119.4626 | 114.2303 | -0.3479 | 114.2029 | 114.1479 | 114.2303 | 114.1754 | 119.4626 | -5.4474 | -119.8105
4331.9688 | 118.3594 | -65.7669 | 49.8688 | 0.00206 | 0.00022218 | 0.0045587 | 6.9721 | -0.024152 | -0.03619 | 7.0123 | -0.018311 | 0.064087 | -0.14191 | 0.10986 | -0.091553 | 0.068665 | -0.013733 | 0.11444 | 8.4915 | -96.9955 | 65.625 | -49.8047 | 65.7486 | 65.8768 | -49.9603 | -31.2286 | -41.3773 | 0.1236 | 65.7532 | 65.8813 | 65.6754 | 65.831 | 65.7486 | 74.2584 | 65.8356 | -31.2286 | 65.831 | 65.7486 | 65.8356 | 65.6754 | 74.2584 | -50.0107 | -146.8643
4333.6875 | 118.2953 | -116.8625 | 2.4536 | 0.00206 | -0.0010596 | 0.0039179 | 0.041727 | -0.025007 | -0.029354 | 0.0062977 | 0.10071 | 0.050354 | -0.073242 | 0.19226 | 0.09613 | 0.19684 | -0.21057 | 0.2655 | 1.8906 | -118.2541 | 116.7892 | -2.4033 | 116.9632 | 117.0547 | -2.3575 | -1.3916 | -0.56305 | 0.17395 | 116.6519 | 117.128 | 116.9586 | 116.9128 | 116.9632 | 118.7531 | 117.0593 | -1.3916 | 116.9128 | 116.9632 | 117.0593 | 116.9586 | 118.7531 | -2.5269 | -120.7077
4335.4688 | 119.989 | -117.8833 | 1.7212 | 0.00206 | -0.003623 | 0.0054131 | 0.043009 | -0.025007 | -0.029995 | 0.0026661 | 0.004578 | 0.054932 | -0.13275 | 0.11902 | 0.036621 | 0.10071 | -0.013733 | 0.20142 | 1.7899 | -118.2861 | 117.7506 | -1.6663 | 117.8879 | 118.0023 | -1.6846 | -0.40283 | 0.068665 | 0.13733 | 117.8696 | 118.0847 | 117.9199 | 117.9382 | 117.8879 | 119.6732 | 117.984 | -0.40283 | 117.9382 | 117.8879 | 117.984 | 117.9199 | 119.6732 | -1.8539 | -120.0073
4337.1875 | 116.4688 | -86.5997 | 29.393 | 0.017319 | 0.00022218 | 0.0024225 | 6.9721 | -0.025648 | -0.024868 | 7.0123 | -0.13275 | 0.018311 | -0.13275 | -0.10986 | -1.3412 | 0.064087 | 0.009155 | 0.022888 | 17.8116 | -79.6555 | 86.467 | -29.3747 | 86.467 | 86.4899 | -30.7343 | 6.9443 | -11.5814 | 0 | 86.6089 | 86.6226 | 85.2585 | 86.618 | 86.467 | 104.4113 | 86.6638 | 6.9443 | 86.618 | 86.467 | 86.6638 | 85.2585 | 104.4113 | -29.5258 | -109.0485
4338.9688 | 119.6182 | -118.8171 | 0.60883 | 0.00206 | -0.00084602 | 0.010113 | 0.043649 | -0.02458 | -0.034267 | 0.0086475 | 0.036621 | 0.050354 | -0.10071 | 0.086975 | 0.009155 | 0.073242 | -0.027466 | 0.15564 | 0.66834 | -119.1238 | 118.7164 | -0.55847 | 118.8538 | 118.9041 | -0.59967 | -0.3067 | 0.059509 | 0.13733 | 118.7897 | 118.9728 | 118.8263 | 118.8675 | 118.8538 | 119.4855 | 118.8904 | -0.3067 | 118.8675 | 118.8538 | 118.8904 | 118.8263 | 119.4855 | -0.70953 | -119.7327
4340.7031 | 120.1218 | -119.577 | 0.21515 | 0.0096895 | -0.001914 | 0.0037043 | 0.079965 | -0.023298 | -0.029995 | 0.0062977 | 0.073242 | 0.036621 | -0.086975 | 0.14648 | 0.10986 | 0.16937 | -0.13733 | 0.25635 | 0.28381 | -119.902 | 119.4901 | -0.17853 | 119.6503 | 119.7235 | -0.10529 | -0.32501 | 0.068664 | 0.16022 | 119.4397 | 119.8334 | 119.6869 | 119.6136 | 119.6503 | 119.8608 | 119.7464 | -0.32501 | 119.6136 | 119.6503 | 119.7464 | 119.6869 | 119.8608 | -0.30212 | -120.1172
4342.4531 | 120.2408 | -119.696 | 0.21515 | 0.0096895 | -0.0034094 | 7.2696e-05 | 0.079965 | -0.021802 | -0.032985 | 0.0035205 | 0.11902 | 0.022888 | -0.068665 | 0.18768 | 0.13275 | 0.20599 | -0.21057 | 0.27466 | 0.2655 | -120.0348 | 119.6274 | -0.19226 | 119.8151 | 119.8837 | -0.082398 | -0.33875 | 0.050354 | 0.18768 | 119.4855 | 119.9707 | 119.8288 | 119.7189 | 119.8151 | 119.9615 | 119.902 | -0.33875 | 119.7189 | 119.8151 | 119.902 | 119.8288 | 119.9615 | -0.28381 | -120.2499
4344.3438 | 120.3873 | -119.8471 | 0.21973 | 0.0096895 | -0.0029822 | 0.0047723 | 0.077829 | -0.024152 | -0.030636 | 0.0056567 | 0.036621 | 0.050354 | -0.091553 | 0.13275 | 0.10071 | 0.15106 | -0.10071 | 0.24261 | 0.28839 | -120.1675 | 119.7556 | -0.16937 | 119.8837 | 119.9799 | -0.11902 | -0.32044 | 0.068664 | 0.12817 | 119.7464 | 120.0897 | 119.9478 | 119.8975 | 119.8837 | 120.1355 | 119.9982 | -0.32044 | 119.8975 | 119.8837 | 119.9982 | 119.9478 | 120.1355 | -0.31128 | -120.3873
4346.1562 | 119.989 | -119.4534 | 0.25177 | 0.00206 | -0.0038366 | 0.0071221 | 0.067575 | -0.024793 | -0.032131 | 0.0050159 | 0.004578 | 0.086975 | -0.13275 | 0.082397 | 0.032043 | 0.073242 | 0.032043 | 0.19684 | 0.33417 | -119.8242 | 119.3207 | -0.16479 | 119.458 | 119.5358 | -0.21973 | -0.37079 | 0.082397 | 0.13733 | 119.4855 | 119.6503 | 119.4855 | 119.5404 | 119.458 | 119.7876 | 119.5267 | -0.37079 | 119.5404 | 119.458 | 119.5267 | 119.4855 | 119.7876 | -0.38452 | -120.076
4347.9688 | 120.3644 | -119.8151 | 0.1831 | 0.00206 | 0.0012902 | 0.0073359 | 0.074411 | -0.024793 | -0.031704 | 0.0062977 | 0.009155 | 0.09613 | -0.10986 | 0.073242 | 0 | 0.064087 | -0.009155 | 0.14191 | 0.31128 | -120.1904 | 119.7052 | -0.086975 | 119.8242 | 119.8883 | -0.1831 | -0.37537 | 0.12817 | 0.11902 | 119.8059 | 119.957 | 119.8151 | 119.9112 | 119.8242 | 120.1263 | 119.8791 | -0.37537 | 119.9112 | 119.8242 | 119.8791 | 119.8151 | 120.1263 | -0.29297 | -120.3735
4349.7812 | 120.4468 | -119.8746 | 0.20599 | 0.00206 | -0.0021276 | 0.0071221 | 0.078043 | -0.023298 | -0.031917 | 0.016551 | -0.004578 | 0.086975 | -0.1236 | 0.073242 | -0.009155 | 0.050354 | -0.013733 | 0.11444 | 0.32501 | -120.2408 | 119.751 | -0.11902 | 119.87 | 119.9478 | -0.21515 | -0.36621 | 0.11902 | 0.11902 | 119.8608 | 119.989 | 119.8654 | 119.9615 | 119.87 | 120.1996 | 119.9249 | -0.36621 | 119.9615 | 119.87 | 119.9249 | 119.8654 | 120.1996 | -0.32959 | -120.4468
4351.6094 | 120.3735 | -119.9936 | 0.31586 | 0.0096895 | -0.0010596 | 0.0069085 | 0.074838 | -0.02757 | -0.031704 | 0.02766 | 0.068665 | 0.064087 | -0.082397 | 0.16022 | 0.073242 | 0.1236 | -0.032043 | 0.24719 | 0.3479 | -120.2408 | 119.9112 | -0.25177 | 120.0623 | 120.1538 | -0.24261 | -0.24719 | 0.032043 | 0.15106 | 119.9615 | 120.2408 | 120.0668 | 120.0577 | 120.0623 | 120.3415 | 120.1172 | -0.24719 | 120.0577 | 120.0623 | 120.1172 | 120.0668 | 120.3415 | -0.39825 | -120.5566
4353.4219 | 120.3918 | -119.9753 | 0.37079 | 0.017319 | -0.00063242 | 0.0051995 | 0.069712 | -0.02522 | -0.032985 | 0.023601 | 0.045776 | 0.064087 | -0.1236 | 0.13733 | 0.045776 | 0.11444 | -0.022888 | 0.21515 | 0.3891 | -120.2866 | 119.8517 | -0.3067 | 120.0211 | 120.1126 | -0.32501 | -0.31128 | 0.01831 | 0.16937 | 119.9524 | 120.1904 | 120.0211 | 120.0394 | 120.0211 | 120.3644 | 120.0897 | -0.31128 | 120.0394 | 120.0211 | 120.0897 | 120.0211 | 120.3644 | -0.49438 | -120.6573
4355.1562 | 120.4834 | -120.0897 | 0.25177 | 0.00206 | -0.0029822 | 0.0004999 | 0.080393 | -0.025861 | -0.032772 | 0.018047 | 0.091553 | 0.032043 | -0.082397 | 0.19226 | 0.12817 | 0.19684 | -0.20599 | 0.28839 | 0.28839 | -120.3278 | 120.0073 | -0.21973 | 120.1813 | 120.282 | -0.1236 | -0.23804 | 0.036621 | 0.17395 | 119.8837 | 120.3781 | 120.2179 | 120.1218 | 120.1813 | 120.3781 | 120.2866 | -0.23804 | 120.1218 | 120.1813 | 120.2866 | 120.2179 | 120.3781 | -0.33417 | -120.5795
4356.9531 | 120.5521 | -120.0623 | 0.26093 | 0.017319 | -0.0029822 | 0.0039179 | 0.082315 | -0.02757 | -0.031063 | 0.023815 | 0.022888 | 0.050354 | -0.082397 | 0.16022 | 0.09613 | 0.14191 | -0.10071 | 0.27008 | 0.31128 | -120.4056 | 119.9799 | -0.21057 | 120.0851 | 120.2225 | -0.1648 | -0.34332 | 0.050354 | 0.10528 | 119.9615 | 120.3323 | 120.1584 | 120.1126 | 120.0851 | 120.3735 | 120.2042 | -0.34332 | 120.1126 | 120.0851 | 120.2042 | 120.1584 | 120.3735 | -0.34332 | -120.6665
4358.75 | 120.2682 | -119.783 | 0.24261 | 0.017319 | -0.0017004 | 0.0043451 | 0.061594 | -0.024793 | -0.031063 | 0.0037341 | 0.004578 | 0.082397 | -0.13275 | 0.10529 | 0.032043 | 0.07782 | 0.032043 | 0.18768 | 0.33417 | -120.163 | 119.6503 | -0.16022 | 119.7876 | 119.8883 | -0.21057 | -0.37994 | 0.091552 | 0.13733 | 119.8151 | 119.9707 | 119.8151 | 119.8654 | 119.7876 | 120.1172 | 119.8608 | -0.37994 | 119.8654 | 119.7876 | 119.8608 | 119.8151 | 120.1172 | -0.37537 | -120.4056
4360.5781 | 120.4376 | -120.0668 | 0.27466 | 0.024948 | -0.0017004 | 0.0041315 | 0.056467 | -0.023511 | -0.031917 | 0.0069385 | 0.091553 | 0.045776 | -0.068665 | 0.20599 | 0.14191 | 0.19226 | -0.13275 | 0.33875 | 0.27008 | -120.3369 | 119.9982 | -0.22888 | 120.1584 | 120.2728 | -0.13275 | -0.27008 | -0.004577 | 0.16022 | 119.9341 | 120.4056 | 120.2087 | 120.1126 | 120.1584 | 120.3369 | 120.2591 | -0.27008 | 120.1126 | 120.1584 | 120.2591 | 120.2087 | 120.3369 | -0.34332 | -120.6116
4362.375 | 120.575 | -120.1218 | 0.23804 | 0.0096895 | -0.0014868 | 0.0009271 | 0.060098 | -0.025007 | -0.032772 | 0.0069385 | 0.086975 | 0.027466 | -0.068665 | 0.17853 | 0.10986 | 0.1831 | -0.17395 | 0.27008 | 0.30212 | -120.4147 | 120.0531 | -0.21057 | 120.2087 | 120.3003 | -0.12817 | -0.29297 | 0.064087 | 0.15564 | 119.9478 | 120.3918 | 120.2316 | 120.1492 | 120.2087 | 120.4239 | 120.3049 | -0.29297 | 120.1492 | 120.2087 | 120.3049 | 120.2316 | 120.4239 | -0.3067 | -120.6528
4364.1719 | 120.4926 | -120.2042 | 0.27466 | 0.0096895 | 0.00043578 | 0.0047723 | 0.076547 | -0.026289 | -0.03384 | 0.02061 | 0.045776 | 0.050354 | -0.13733 | 0.15106 | 0.054932 | 0.11902 | -0.045776 | 0.21057 | 0.31586 | -120.4514 | 120.0668 | -0.2243 | 120.2499 | 120.3552 | -0.21973 | -0.24719 | 0.041199 | 0.18311 | 120.1584 | 120.4147 | 120.2591 | 120.2545 | 120.2499 | 120.52 | 120.3232 | -0.24719 | 120.2545 | 120.2499 | 120.3232 | 120.2591 | 120.52 | -0.41199 | -120.726
4365.9219 | 120.5658 | -120.1904 | 0.24261 | 0.0096895 | -0.00063242 | 0.0019953 | 0.072489 | -0.02757 | -0.032131 | 0.017406 | -0.009155 | 0.09613 | -0.14191 | 0.091553 | 0.032043 | 0.07782 | 0.054932 | 0.17853 | 0.33875 | -120.4971 | 120.0485 | -0.14649 | 120.1813 | 120.282 | -0.21057 | -0.3067 | 0.09613 | 0.13275 | 120.2454 | 120.369 | 120.2225 | 120.2866 | 120.1813 | 120.5292 | 120.2683 | -0.3067 | 120.2866 | 120.1813 | 120.2683 | 120.2225 | 120.5292 | -0.38452 | -120.7397
4367.7188 | 120.5933 | -120.2179 | 0.27008 | 0.0096895 | -0.0029822 | 0.0030633 | 0.076975 | -0.026502 | -0.034054 | 0.022106 | -0.009155 | 0.09613 | -0.11902 | 0.10071 | 0.018311 | 0.059509 | 0.059509 | 0.17395 | 0.33417 | -120.5109 | 120.0989 | -0.17395 | 120.2087 | 120.3186 | -0.25177 | -0.29297 | 0.064086 | 0.10986 | 120.2774 | 120.3918 | 120.2362 | 120.314 | 120.2087 | 120.5521 | 120.2774 | -0.29297 | 120.314 | 120.2087 | 120.2774 | 120.2362 | 120.5521 | -0.3891 | -120.7809
4369.5156 | 120.5429 | -120.2591 | 0.28839 | 0.00206 | -0.0010596 | 0.0064813 | 0.063089 | -0.026716 | -0.031063 | 0.0073657 | 0.10986 | 0.054932 | -0.059509 | 0.20142 | 0.15564 | 0.19684 | -0.1236 | 0.32044 | 0.29755 | -120.5154 | 120.1996 | -0.23346 | 120.369 | 120.4605 | -0.13275 | -0.25635 | 0.009155 | 0.16937 | 120.1355 | 120.5795 | 120.4147 | 120.314 | 120.369 | 120.5566 | 120.4559 | -0.25635 | 120.314 | 120.369 | 120.4559 | 120.4147 | 120.5566 | -0.3479 | -120.8038
4371.2656 | 120.5704 | -120.3094 | 0.25635 | 0.0096895 | -0.002555 | 0.0041315 | 0.081034 | -0.025007 | -0.033626 | 0.013133 | 0.073242 | 0.068665 | -0.11444 | 0.14191 | 0.073242 | 0.10529 | -0.027466 | 0.21515 | 0.31586 | -120.5566 | 120.195 | -0.18768 | 120.3827 | 120.4514 | -0.18311 | -0.24719 | 0.059509 | 0.18768 | 120.282 | 120.5246 | 120.3827 | 120.3781 | 120.3827 | 120.6253 | 120.4147 | -0.24719 | 120.3781 | 120.3827 | 120.4147 | 120.3827 | 120.6253 | -0.37079 | -120.813
4373.0625 | 120.6436 | -120.2866 | 0.26093 | 0.0096895 | 0.004281 | 0.0066949 | 0.072061 | -0.026502 | -0.030208 | 0.016979 | -0.009155 | 0.07782 | -0.10071 | 0.091553 | 0.022888 | 0.07782 | 0.059509 | 0.1831 | 0.32044 | -120.6345 | 120.1859 | -0.18311 | 120.2774 | 120.3781 | -0.23804 | -0.3479 | 0.05951 | 0.091553 | 120.3461 | 120.4697 | 120.3094 | 120.3644 | 120.2774 | 120.607 | 120.3644 | -0.3479 | 120.3644 | 120.2774 | 120.3644 | 120.3094 | 120.607 | -0.36163 | -120.8954
4374.7969 | 120.607 | -120.3232 | 0.2655 | 0.00206 | -0.0029822 | -0.0005683 | 0.07612 | -0.027998 | -0.03384 | 0.015911 | 0.09613 | 0.027466 | -0.10071 | 0.21973 | 0.17395 | 0.21973 | -0.14648 | 0.32959 | 0.29297 | -120.5795 | 120.2225 | -0.23804 | 120.4193 | 120.5429 | -0.091553 | -0.25635 | 0.027466 | 0.19684 | 120.1767 | 120.6528 | 120.4971 | 120.3506 | 120.4193 | 120.6162 | 120.5429 | -0.25635 | 120.3506 | 120.4193 | 120.5429 | 120.4971 | 120.6162 | -0.36621 | -120.845
4376.5938 | 120.7489 | -120.3369 | 0.25177 | 0.00206 | -0.0031958 | 0.0073359 | 0.071634 | -0.025648 | -0.031704 | 0.0095019 | 0.091553 | 0.054932 | -0.07782 | 0.17395 | 0.12817 | 0.17853 | -0.18768 | 0.27008 | 0.3067 | -120.607 | 120.2591 | -0.19684 | 120.4285 | 120.5109 | -0.1236 | -0.27008 | 0.054932 | 0.16937 | 120.1492 | 120.607 | 120.4651 | 120.3918 | 120.4285 | 120.6436 | 120.5154 | -0.27008 | 120.3918 | 120.4285 | 120.5154 | 120.4651 | 120.6436 | -0.32959 | -120.8588
4378.3906 | 120.6573 | -120.3781 | 0.27008 | 0.024948 | -0.001914 | 0.0022089 | 0.075907 | -0.02992 | -0.03149 | 0.013133 | 0.10071 | 0.036621 | -0.082397 | 0.21973 | 0.14648 | 0.20599 | -0.12817 | 0.32959 | 0.27924 | -120.6299 | 120.2957 | -0.23346 | 120.4788 | 120.5978 | -0.1236 | -0.25177 | 0.009155 | 0.18311 | 120.2499 | 120.7077 | 120.5246 | 120.4147 | 120.4788 | 120.6573 | 120.5841 | -0.25177 | 120.4147 | 120.4788 | 120.5841 | 120.5246 | 120.6573 | -0.35248 | -120.9
4380.2188 | 120.7169 | -120.3644 | 0.23804 | 0.0096895 | -0.0017004 | 0.0094721 | 0.099619 | -0.027357 | -0.034908 | 0.023815 | 0.013733 | 0.064087 | -0.11902 | 0.086975 | 0.018311 | 0.073242 | -0.004578 | 0.16022 | 0.31128 | -120.6665 | 120.2454 | -0.17395 | 120.3781 | 120.4514 | -0.21973 | -0.30212 | 0.073242 | 0.13275 | 120.3598 | 120.5246 | 120.3827 | 120.4285 | 120.3781 | 120.6757 | 120.4376 | -0.30212 | 120.4285 | 120.3781 | 120.4376 | 120.3827 | 120.6757 | -0.35706 | -120.9045

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.9646 | 6.6406 | 6.8873 | 6.9225
0.0354 | 6.6387 | 6.8852 | 6.9306
1.0354 | 6.6379 | 6.8832 | 6.9253
2.0354 | 6.6441 | 6.9001 | 6.9315
3.0354 | 6.6506 | 6.8945 | 6.9297
4.0354 | 6.6617 | 6.9011 | 6.9327
5.0354 | 6.6592 | 6.906 | 6.9225
6.0354 | 6.6616 | 6.9052 | 6.9407
7.0354 | 6.6622 | 6.9248 | 6.9446
8.0354 | 6.6896 | 7.2115 | 6.9584
9.0354 | 6.8573 | 7.6941 | 7.5834
10.0354 | 7.7673 | 8.5786 | 8.7952
11.0354 | 8.6993 | 10.3667 | 10.4745
12.0354 | 10.7566 | 13.223 | 12.185
13.0354 | 13.0535 | 16.4711 | 13.8645
14.0354 | 15.6463 | 20.9416 | 17.2234
15.0354 | 17.6273 | 25.7265 | 19.5288
16.0354 | 20.8978 | 30.6265 | 21.9667
17.0354 | 23.7355 | 34.3161 | 23.7792
18.0354 | 26.3768 | 37.9511 | 27.2212
19.0354 | 29.9889 | 43.0952 | 31.0688
20.0354 | 33.3845 | 49.7825 | 34.1204
21.0354 | 37.6394 | 55.2711 | 37.6197
22.0354 | 39.668 | 56.6639 | 40.8542
23.0354 | 41.6608 | 59.7382 | 43.7539
24.0354 | 45.1685 | 66.1676 | 48.6474
25.0354 | 48.8339 | 68.6845 | 53.0789
26.0354 | 52.4955 | 72.3989 | 56.1847
27.0354 | 55.6501 | 76.4267 | 59.3524
28.0354 | 57.132 | 80.9033 | 61.4627
29.0354 | 59.1813 | 84.1895 | 63.7638
30.0354 | 61.8994 | 87.3122 | 66.494
31.0354 | 64.1896 | 89.3774 | 69.5733
32.0354 | 66.8049 | 91.7391 | 72.1596
33.0354 | 68.5093 | 94.4608 | 74.8498
34.0354 | 69.0819 | 97.8568 | 78.5564
35.0354 | 71.5216 | 101.7058 | 81.6432
36.0354 | 72.786 | 104.8127 | 83.9866
37.0354 | 74.15 | 108.1631 | 86.6115
38.0354 | 75.5625 | 115.0107 | 90.5184
39.0354 | 76.937 | 119.5597 | 92.835
40.0354 | 77.9703 | 124.2813 | 95.6698
41.0354 | 79.204 | 127.241 | 98.3208
42.0354 | 79.9542 | 129.7016 | 99.2463
43.0354 | 81.0335 | 132.1673 | 99.8557
44.0354 | 82.5745 | 135.0679 | 101.0471
45.0354 | 83.5097 | 137.4888 | 102.1073
46.0354 | 83.8989 | 139.1049 | 103.529
47.0354 | 85.675 | 140.6698 | 105.9531
48.0354 | 87.2573 | 142.1176 | 106.8191
49.0354 | 88.2669 | 143.2206 | 107.5446
50.0354 | 90.0882 | 145.5203 | 108.2561
51.0354 | 92.3929 | 147.2506 | 109.0673
52.0354 | 94.984 | 148.4193 | 110.7018
53.0354 | 96.7564 | 149.2397 | 111.8971
54.0354 | 99.1983 | 150.1836 | 113.2497
55.0354 | 103.0808 | 152.3962 | 114.1984
56.0354 | 103.91 | 153.281 | 114.7736
57.0354 | 106.1408 | 154.5556 | 115.5808
58.0354 | 107.9727 | 155.0706 | 116.2853
59.0354 | 109.8962 | 155.1095 | 117.1107
60.0354 | 111.6456 | 155.6642 | 117.7899
61.0354 | 112.773 | 155.3412 | 118.7349
62.0354 | 113.8198 | 155.1456 | 119.352
63.0354 | 116.1148 | 156.0492 | 120.0664
64.0354 | 116.923 | 156.3055 | 120.3129
65.0354 | 118.7625 | 156.4227 | 121.564
66.0354 | 118.8118 | 155.1654 | 121.5178
67.0354 | 118.1134 | 154.031 | 121.4551
68.0354 | 118.2802 | 153.0397 | 121.3322
69.0354 | 118.0166 | 152.8527 | 121.8865
70.0354 | 118.6526 | 152.5555 | 122.5459
71.0354 | 118.8767 | 151.508 | 122.2704
72.0354 | 119.959 | 151.7918 | 122.9499
73.0354 | 120.7999 | 152.5694 | 123.8428
74.0354 | 121.7127 | 151.7278 | 123.9243
75.0354 | 121.5756 | 152.0565 | 124.6186
76.0354 | 121.6919 | 150.8031 | 124.8104
77.0354 | 121.0974 | 150.4274 | 125.0473
78.0354 | 121.8482 | 149.7226 | 125.1214
79.0354 | 121.7992 | 149.6002 | 125.6948
80.0354 | 121.4769 | 148.5581 | 125.669
81.0354 | 121.7229 | 148.3424 | 125.7402
82.0354 | 122.2324 | 148.1598 | 126.4242
83.0354 | 121.5856 | 147.3278 | 126.2036
84.0354 | 121.1197 | 146.3124 | 125.8741
85.0354 | 121.0334 | 146.2005 | 126.2947
86.0354 | 121.0986 | 145.0417 | 126.1607
87.0354 | 120.5365 | 144.5322 | 126.266
88.0354 | 120.4979 | 143.9743 | 125.9722
89.0354 | 120.2015 | 142.8059 | 125.5985
90.0354 | 119.7275 | 142.8005 | 125.8265
91.0354 | 119.1505 | 142.3252 | 125.8776
92.0354 | 119.1358 | 141.6487 | 125.9798
93.0354 | 118.9928 | 140.8524 | 125.9574
94.0354 | 119.3597 | 140.9177 | 126.6253
95.0354 | 120.3073 | 141.7089 | 127.9551
96.0354 | 121.3989 | 142.2943 | 128.8064
97.0354 | 121.6569 | 142.6566 | 129.3784
98.0354 | 121.3906 | 142.1619 | 129.4735
99.0354 | 121.2136 | 141.5926 | 129.5976
100.0354 | 121.1587 | 141.6146 | 130.5706
101.0354 | 121.3776 | 141.7564 | 131.1033
102.0354 | 122.6043 | 143.1658 | 132.0495
103.0354 | 123.244 | 144.0078 | 133.1281
104.0354 | 123.4901 | 144.5693 | 134.3391
105.0354 | 124.6001 | 145.4526 | 134.9397
106.0354 | 125.374 | 146.4598 | 135.9752
107.0354 | 125.9384 | 148.0295 | 136.9262
108.0354 | 126.6679 | 149.2235 | 138.378
109.0354 | 126.7537 | 150.0611 | 139.6296
110.0354 | 126.4464 | 150.307 | 140.0874
111.0354 | 127.4611 | 151.1274 | 140.9334
112.0354 | 127.7731 | 151.6648 | 142.1332
113.0354 | 128.3702 | 152.5512 | 143.8544
114.0354 | 130.3483 | 154.7512 | 145.2339
115.0354 | 131.3761 | 155.6034 | 146.1584
116.0354 | 132.3285 | 156.8147 | 147.1132
117.0354 | 133.0043 | 157.2093 | 148.1837
118.0354 | 134.8416 | 157.5577 | 149.1548
119.0354 | 136.8956 | 159.6625 | 150.9335
120.0354 | 138.34 | 161.9577 | 153.6491
121.0354 | 139.7477 | 163.314 | 155.9977
122.0354 | 140.1515 | 165.1343 | 157.6187
123.0354 | 140.6838 | 166.3326 | 158.6602
124.0354 | 140.7592 | 168.1703 | 160.9483
125.0354 | 141.1284 | 169.4103 | 161.6821
126.0354 | 140.7707 | 170.184 | 162.2349
127.0354 | 142.5953 | 170.8134 | 162.168
128.0354 | 141.9947 | 170.0774 | 161.9378
129.0354 | 143.2442 | 171.2145 | 163.0423
130.0354 | 143.3987 | 173.5689 | 163.9196
131.0354 | 144.4052 | 174.525 | 164.0421
132.0354 | 145.1447 | 175.6234 | 165.4852
133.0354 | 146.2599 | 177.4566 | 167.2562
134.0354 | 146.4459 | 177.5959 | 167.9878
135.0354 | 146.4309 | 177.7202 | 168.4335
136.0354 | 145.4599 | 175.8987 | 168.1782
137.0354 | 144.1124 | 175.1189 | 167.1453
138.0354 | 144.7489 | 175.3204 | 168.073
139.0354 | 145.4561 | 177.9898 | 169.6111
140.0354 | 146.208 | 178.6218 | 169.2084
141.0354 | 147.256 | 179.5595 | 169.6753
142.0354 | 147.7632 | 180.2167 | 169.92
143.0354 | 147.7082 | 181.1713 | 171.5309
144.0354 | 147.1667 | 182.2883 | 172.9241
145.0354 | 147.7442 | 184.1316 | 174.6967
146.0354 | 148.1677 | 185.246 | 175.7451
147.0354 | 148.9586 | 184.3199 | 175.8264
148.0354 | 147.6743 | 183.6959 | 175.273
149.0354 | 148.3936 | 183.3361 | 174.1013
150.0354 | 148.6178 | 182.3068 | 173.2482
151.0354 | 148.0704 | 181.368 | 171.8656
152.0354 | 147.7076 | 180.5677 | 171.0848
153.0354 | 147.568 | 180.741 | 170.2975
154.0354 | 149.1838 | 180.9584 | 170.2062
155.0354 | 150.3254 | 181.6668 | 170.7433
156.0354 | 151.2087 | 181.8096 | 170.7144
157.0354 | 150.5062 | 181.0779 | 170.6637
158.0354 | 150.0638 | 180.584 | 171.3723
159.0354 | 149.1538 | 179.5617 | 171.7342
160.0354 | 148.7632 | 180.1021 | 171.9968
161.0354 | 147.7114 | 180.7389 | 172.1669
162.0354 | 146.9688 | 180.7956 | 172.187
163.0354 | 146.8617 | 180.5175 | 171.869
164.0354 | 147.4479 | 180.6759 | 171.6257
165.0354 | 147.9612 | 180.7256 | 172.1033
166.0354 | 148.3741 | 181.0608 | 172.7418
167.0354 | 148.2329 | 180.4741 | 172.5025
168.0354 | 148.6334 | 182.0649 | 173.178
169.0354 | 148.2656 | 181.1758 | 172.3715
170.0354 | 147.4242 | 180.731 | 172.893
171.0354 | 147.7251 | 179.9355 | 172.5287
172.0354 | 147.702 | 179.4745 | 172.0017
173.0354 | 147.2906 | 179.41 | 172.0873
174.0354 | 147.1801 | 178.1071 | 171.7067
175.0354 | 147.1949 | 178.1801 | 172.3837
176.0354 | 147.9436 | 178.5538 | 172.9522
177.0354 | 147.9001 | 178.4911 | 172.809
178.0354 | 147.7023 | 179.5492 | 172.9308
179.0354 | 147.7173 | 179.324 | 173.7214
180.0354 | 148.4509 | 180.8268 | 174.8089
181.0354 | 148.4173 | 180.0956 | 175.2919
182.0354 | 148.0889 | 180.5984 | 176.0135
183.0354 | 148.5507 | 181.1499 | 176.6512
184.0354 | 149.1011 | 180.623 | 177.5645
185.0354 | 148.5028 | 179.8312 | 177.2432
186.0354 | 148.3925 | 179.7369 | 177.3417
187.0354 | 148.6122 | 179.2724 | 176.8806
188.0354 | 149.3615 | 179.0178 | 176.3571
189.0354 | 149.2885 | 179.0161 | 176.4286
190.0354 | 149.9471 | 180.2343 | 176.5375
191.0354 | 149.6117 | 181.4184 | 178.4429
192.0354 | 149.4117 | 179.9228 | 177.147
193.0354 | 148.7137 | 179.4137 | 176.726
194.0354 | 149.7542 | 179.673 | 176.7867
195.0354 | 149.4974 | 178.6923 | 176.4206
196.0354 | 149.3494 | 178.423 | 176.2627
197.0354 | 150.455 | 178.5345 | 176.2443
198.0354 | 151.0169 | 178.8094 | 176.1673
199.0354 | 150.7553 | 179.2901 | 175.8514
200.0354 | 151.9015 | 179.348 | 176.5497
201.0354 | 151.435 | 179.5827 | 175.8545
202.0354 | 152.289 | 180.0971 | 177.0776
203.0354 | 153.4834 | 179.7227 | 177.8448
204.0354 | 153.6061 | 179.7973 | 178.1331
205.0354 | 152.3516 | 177.9739 | 177.2675
206.0354 | 151.5161 | 177.8137 | 177.1763
207.0354 | 152.2213 | 177.6873 | 177.1261
208.0354 | 152.2344 | 176.9046 | 176.0263
209.0354 | 151.9362 | 176.6401 | 175.1707
210.0354 | 151.9618 | 176.73 | 175.1124
211.0354 | 152.3939 | 176.8816 | 175.6226
212.0354 | 153.7778 | 177.621 | 176.1757
213.0354 | 154.8256 | 177.8279 | 176.707
214.0354 | 154.5764 | 177.2572 | 176.0882
215.0354 | 154.4035 | 177.6854 | 176.1562
216.0354 | 154.7132 | 177.824 | 176.5151
217.0354 | 156.0709 | 178.835 | 177.6184
218.0354 | 156.8658 | 180.2224 | 178.3372
219.0354 | 157.2629 | 180.3915 | 178.8971
220.0354 | 155.9247 | 180.7706 | 178.9486
221.0354 | 156.1331 | 179.9573 | 179.2762
222.0354 | 156.6581 | 180.6566 | 179.5691
223.0354 | 156.4778 | 181.6169 | 180.0264
224.0354 | 156.5841 | 181.9643 | 180.0405
225.0354 | 156.6267 | 180.6508 | 178.8367
226.0354 | 156.5931 | 180.42 | 178.1919
227.0354 | 158.3498 | 181.0118 | 178.8652
228.0354 | 159.1784 | 182.0571 | 178.6733
229.0354 | 161.1986 | 182.951 | 180.1533
230.0354 | 161.0116 | 183.2999 | 179.9066
231.0354 | 160.8297 | 182.9128 | 180.345
232.0354 | 161.6795 | 183.751 | 180.9648
233.0354 | 161.0426 | 183.5296 | 181.14
234.0354 | 160.3133 | 183.6619 | 180.6331
235.0354 | 160.4709 | 183.9351 | 180.8927
236.0354 | 160.521 | 183.9551 | 180.6701
237.0354 | 160.8499 | 184.0123 | 180.5834
238.0354 | 160.7991 | 183.9038 | 181.6991
239.0354 | 159.6189 | 184.2171 | 180.925
240.0354 | 160.4193 | 184.4751 | 181.1734
241.0354 | 160.9236 | 185.0237 | 181.9314
242.0354 | 161.8229 | 185.1109 | 182.6701
243.0354 | 162.6029 | 185.5333 | 182.246
244.0354 | 163.555 | 185.9125 | 182.6759
245.0354 | 165.4331 | 187.4437 | 183.3995
246.0354 | 164.3764 | 186.4938 | 183.0887
247.0354 | 164.8947 | 186.5087 | 183.35
248.0354 | 164.8412 | 187.3429 | 183.5391
249.0354 | 165.058 | 187.5845 | 183.0689
250.0354 | 165.7491 | 187.6756 | 183.8387
251.0354 | 165.5536 | 186.6008 | 184.03
252.0354 | 164.8457 | 187.2913 | 184.8065
253.0354 | 164.4735 | 187.9388 | 185.4044
254.0354 | 163.2326 | 187.5576 | 185.0763
255.0354 | 162.9356 | 187.6909 | 184.5855
256.0354 | 164.6966 | 189.1432 | 185.5754
257.0354 | 165.3317 | 188.7785 | 186.1756
258.0354 | 164.5963 | 189.1491 | 186.442
259.0354 | 163.636 | 189.7703 | 187.6959
260.0354 | 163.2825 | 190.731 | 187.4861
261.0354 | 162.5636 | 190.4627 | 186.7909
262.0354 | 162.3911 | 189.6224 | 186.7161
263.0354 | 161.8353 | 188.3238 | 185.6415
264.0354 | 162.5228 | 188.6936 | 186.2614
265.0354 | 163.7512 | 189.9454 | 187.7127
266.0354 | 164.3471 | 190.7233 | 187.1872
267.0354 | 164.4456 | 191.9308 | 187.3963
268.0354 | 165.8023 | 192.3567 | 188.3498
269.0354 | 164.6409 | 191.9804 | 188.3535
270.0354 | 165.2922 | 191.1746 | 187.9336
271.0354 | 164.6663 | 190.836 | 187.2489
272.0354 | 163.4228 | 189.7085 | 186.1582
273.0354 | 162.7537 | 189.3791 | 185.3687
274.0354 | 163.0372 | 188.9228 | 184.5052
275.0354 | 162.5218 | 188.005 | 183.9321
276.0354 | 163.2003 | 189.2542 | 183.5828
277.0354 | 162.654 | 188.8652 | 183.2674
278.0354 | 161.8174 | 187.3372 | 182.5613
279.0354 | 162.0746 | 187.5979 | 182.8896
280.0354 | 162.4805 | 189.1299 | 183.4673
281.0354 | 162.3571 | 188.5689 | 184.3254
282.0354 | 161.4942 | 188.6558 | 183.9726
283.0354 | 162.7858 | 189.4903 | 184.6214
284.0354 | 162.1571 | 188.2876 | 184.991
285.0354 | 162.17 | 188.5374 | 185.4903
286.0354 | 161.8146 | 187.482 | 186.2105
287.0354 | 161.1093 | 186.9408 | 186.4085
288.0354 | 160.5989 | 186.535 | 186.32
289.0354 | 160.3689 | 186.0938 | 186.517
290.0354 | 161.925 | 188.4745 | 188.0874
291.0354 | 163.4738 | 189.5094 | 188.6429
292.0354 | 163.8879 | 189.7013 | 188.9872
293.0354 | 164.2294 | 188.611 | 188.9871
294.0354 | 163.058 | 187.871 | 189.2514
295.0354 | 162.9365 | 187.6905 | 189.2213
296.0354 | 162.7354 | 187.9783 | 189.0494
297.0354 | 161.9611 | 187.8857 | 188.5547
298.0354 | 161.8899 | 188.0676 | 189.3007
299.0354 | 161.554 | 187.146 | 189.048
300.0354 | 160.6572 | 185.4494 | 188.7893
301.0354 | 160.36 | 186.3014 | 188.9736
302.0354 | 160.6603 | 186.4331 | 189.6575
303.0354 | 160.445 | 185.6586 | 189.0946
304.0354 | 160.449 | 185.2058 | 188.9597
305.0354 | 159.8314 | 184.0685 | 188.4861
306.0354 | 159.2149 | 184.1345 | 188.2454
307.0354 | 159.3561 | 184.1181 | 189.1388
308.0354 | 159.5099 | 184.3502 | 188.75
309.0354 | 159.0496 | 184.8237 | 188.7541
310.0354 | 158.8589 | 185.6308 | 189.0286
311.0354 | 158.6118 | 184.4245 | 188.799
312.0354 | 157.6943 | 184.1176 | 188.6208
313.0354 | 157.0416 | 183.8067 | 188.1416
314.0354 | 157.1381 | 183.6152 | 188.1191
315.0354 | 157.2326 | 183.2558 | 188.2498
316.0354 | 156.7942 | 183.3603 | 187.9653
317.0354 | 156.3918 | 182.7541 | 187.2724
318.0354 | 156.4176 | 182.2177 | 188.0219
319.0354 | 156.3748 | 182.371 | 187.9625
320.0354 | 155.8253 | 182.398 | 187.7923
321.0354 | 155.2747 | 183.3997 | 188.0058
322.0354 | 154.8715 | 182.7596 | 188.0025
323.0354 | 154.8704 | 182.2618 | 187.4646
324.0354 | 154.6206 | 183.5865 | 187.3937
325.0354 | 155.273 | 182.6963 | 187.0612
326.0354 | 155.2119 | 183.1286 | 187.0406
327.0354 | 155.3416 | 182.5751 | 186.2672
328.0354 | 155.2649 | 182.5297 | 185.8695
329.0354 | 154.7005 | 182.3088 | 185.7597
330.0354 | 154.748 | 181.7586 | 184.7944
331.0354 | 155.114 | 181.0595 | 184.1132
332.0354 | 155.6884 | 181.9697 | 183.8701
333.0354 | 156.365 | 181.9536 | 184.0803
334.0354 | 156.681 | 183.728 | 184.4526
335.0354 | 157.4408 | 184.9493 | 184.4963
336.0354 | 157.8608 | 185.9048 | 184.4779
337.0354 | 159.9269 | 187.7109 | 184.4982
338.0354 | 162.2393 | 189.7468 | 186.2411
339.0354 | 164.9634 | 190.8446 | 187.7956
340.0354 | 164.8574 | 192.1209 | 188.0949
341.0354 | 164.9358 | 191.6837 | 188.3817
342.0354 | 165.6994 | 191.8483 | 188.2675
343.0354 | 165.7668 | 191.4346 | 188.2002
344.0354 | 165.2641 | 190.6656 | 187.7083
345.0354 | 165.8995 | 191.1287 | 188.1053
346.0354 | 166.2562 | 191.33 | 188.256
347.0354 | 166.5667 | 192.4554 | 189.3752
348.0354 | 166.8178 | 193.0134 | 189.8958
349.0354 | 166.4357 | 193.6056 | 190.0974
350.0354 | 165.3149 | 192.7572 | 189.5452
351.0354 | 165.2841 | 192.7972 | 189.5462
352.0354 | 166.9141 | 193.4906 | 191.1215
353.0354 | 166.508 | 193.6354 | 191.886
354.0354 | 166.5705 | 193.4667 | 191.9075
355.0354 | 167.1965 | 194.6328 | 192.1586
356.0354 | 166.5412 | 194.4427 | 192.4055
357.0354 | 167.7071 | 195.6712 | 192.6428
358.0354 | 167.5928 | 196.9044 | 193.2073
359.0354 | 168.313 | 198.7623 | 193.7939
360.0354 | 170.8372 | 200.2734 | 195.0183
361.0354 | 172.3067 | 200.8358 | 196.2397
362.0354 | 173.0881 | 200.3449 | 195.6346
363.0354 | 172.2375 | 199.041 | 194.8759
364.0354 | 171.2595 | 198.4972 | 194.1171
365.0354 | 170.6023 | 196.9674 | 193.2506
366.0354 | 169.7693 | 195.8487 | 192.0078
367.0354 | 168.9771 | 195.283 | 191.4594
368.0354 | 168.995 | 194.6704 | 191.4305
369.0354 | 168.5226 | 193.4826 | 190.8823
370.0354 | 168.2289 | 193.1387 | 190.4503
371.0354 | 167.8429 | 192.2951 | 189.6244
372.0354 | 167.0053 | 190.9091 | 188.5626
373.0354 | 166.574 | 190.7988 | 187.8299
374.0354 | 166.0657 | 190.0095 | 187.097
375.0354 | 166.8746 | 190.0498 | 186.927
376.0354 | 167.3701 | 189.6657 | 186.384
377.0354 | 168.416 | 188.9166 | 186.0923
378.0354 | 169.2067 | 189.1811 | 185.7457
379.0354 | 169.4801 | 189.691 | 186.1852
380.0354 | 169.9004 | 190.2277 | 186.5404
381.0354 | 170.0225 | 191.136 | 186.8598
382.0354 | 170.7622 | 191.8458 | 187.6203
383.0354 | 171.5952 | 192.3628 | 188.9816
384.0354 | 175.174 | 193.7436 | 189.3271
385.0354 | 178.7123 | 195.2653 | 190.1511
386.0354 | 180.6983 | 197.9424 | 192.3213
387.0354 | 180.5465 | 199.3532 | 193.991
388.0354 | 179.4453 | 199.6339 | 194.9908
389.0354 | 180.6021 | 199.9812 | 195.0309
390.0354 | 181.2725 | 200.8631 | 195.9901
391.0354 | 183.0282 | 200.9669 | 196.2844
392.0354 | 184.2597 | 200.5896 | 195.9708
393.0354 | 184.5414 | 200.2085 | 195.9194
394.0354 | 184.3687 | 199.9605 | 196.4481
395.0354 | 184.7378 | 198.965 | 195.8297
396.0354 | 185.4254 | 198.8634 | 195.3595
397.0354 | 186.6275 | 200.0636 | 196.157
398.0354 | 185.7952 | 200.6903 | 196.8774
399.0354 | 187.8906 | 201.3385 | 195.8516
400.0354 | 188.803 | 201.4789 | 196.2105
401.0354 | 188.4541 | 201.0992 | 195.1456
402.0354 | 187.5799 | 200.9674 | 194.5774
403.0354 | 187.6258 | 201.5472 | 193.6723
404.0354 | 187.8597 | 201.0313 | 192.5162
405.0354 | 187.6814 | 201.6986 | 192.7136
406.0354 | 189.1924 | 203.6387 | 195.6443
407.0354 | 189.8948 | 204.8961 | 196.7703
408.0354 | 191.2407 | 205.9334 | 197.6751
409.0354 | 191.3467 | 207.5264 | 198.6108
410.0354 | 191.6332 | 207.74 | 198.4082
411.0354 | 192.6821 | 209.0507 | 198.7883
412.0354 | 193.1793 | 209.5907 | 199.5077
413.0354 | 193.5784 | 210.5738 | 199.1339
414.0354 | 195.0074 | 211.4637 | 199.0126
415.0354 | 194.8804 | 212.578 | 198.1947
416.0354 | 195.9759 | 213.5847 | 198.6766
417.0354 | 196.0593 | 213.2685 | 198.909
418.0354 | 196.2549 | 212.7553 | 198.8933
419.0354 | 195.7623 | 211.8262 | 198.2131
420.0354 | 194.3622 | 210.9544 | 197.52
421.0354 | 193.2618 | 209.6418 | 196.7206
422.0354 | 192.6644 | 209.6844 | 197.0675
423.0354 | 192.1983 | 210.5911 | 198.0886
424.0354 | 193.1216 | 211.2271 | 197.6771
425.0198 | 192.3688 | 210.7074 | 197.11
426.0198 | 192.2497 | 210.6655 | 197.3694
427.0198 | 191.595 | 209.7147 | 197.63
428.0354 | 190.1829 | 208.1723 | 196.9665
429.0354 | 189.338 | 206.9855 | 196.2054
430.0354 | 188.001 | 207.4109 | 195.897
431.0354 | 188.7248 | 206.9762 | 195.1594
432.0354 | 188.7178 | 206.891 | 195.5345
433.0354 | 188.2536 | 206.8919 | 195.7493
434.0354 | 190.4288 | 208.0434 | 197.3416
435.0354 | 191.0744 | 208.6011 | 197.7256
436.0354 | 191.1352 | 209.2406 | 198.4563
437.0354 | 192.0296 | 210.2031 | 200.1037
438.0198 | 193.426 | 211.9916 | 201.2552
439.0198 | 193.6115 | 213.2486 | 203.2828
440.0198 | 194.1347 | 212.3276 | 202.7315
441.0198 | 195.1603 | 212.4073 | 202.1822
442.0198 | 195.5672 | 212.7404 | 201.8176
443.0198 | 195.135 | 211.3419 | 201.5285
444.0198 | 194.466 | 211.331 | 201.7017
445.0354 | 194.0348 | 211.938 | 201.8634
446.0354 | 193.9755 | 212.3168 | 202.1294
447.0354 | 194.558 | 212.2888 | 202.5487
448.0354 | 194.0014 | 212.4939 | 202.2877
449.0354 | 194.3589 | 214.1595 | 202.7816
450.0354 | 194.9467 | 215.2102 | 203.3819
451.0354 | 196.5675 | 216.819 | 203.9629
452.0354 | 198.3674 | 217.7144 | 204.8824
453.0354 | 199.0895 | 217.9595 | 204.314
454.0354 | 199.1824 | 218.2188 | 204.8576
455.0354 | 199.8656 | 219.6418 | 205.9847
456.0354 | 199.691 | 219.1368 | 206.1132
457.0354 | 199.4943 | 218.7046 | 206.3289
458.0354 | 199.7939 | 218.804 | 206.6949
459.0354 | 198.9572 | 218.1794 | 205.6765
460.0354 | 198.9577 | 217.4086 | 205.269
461.0354 | 198.844 | 215.4273 | 204.2649
462.0354 | 197.9796 | 214.2779 | 203.2846
463.0354 | 196.8273 | 213.272 | 202.3572
464.0354 | 196.3135 | 212.5457 | 201.5698
465.0354 | 196.2354 | 212.2344 | 200.7597
466.0354 | 195.8221 | 212.2841 | 200.4738
467.0354 | 195.0152 | 213.0005 | 200.068
468.0354 | 195.6014 | 211.9412 | 199.4639
469.0354 | 197.0863 | 213.0157 | 199.2988
470.0354 | 199.9233 | 215.4465 | 201.0702
471.0354 | 201.6332 | 216.4893 | 202.3097
472.0354 | 203.5744 | 218.0252 | 203.5591
473.0354 | 205.3548 | 219.6867 | 205.5017
474.0354 | 205.7814 | 221.2274 | 206.83
475.0354 | 206.3437 | 221.4005 | 207.3556
476.0354 | 208.0201 | 223.2121 | 207.6024
477.0354 | 209.5959 | 224.3492 | 208.8519
478.0354 | 208.9608 | 225.0843 | 209.7455
479.0354 | 208.7796 | 225.5764 | 211.322
480.0354 | 208.6104 | 225.8161 | 211.4274
481.0354 | 211.1875 | 225.6221 | 211.3035
482.0354 | 211.7293 | 225.1844 | 210.4858
483.0354 | 210.0882 | 224.0881 | 209.4692
484.0354 | 209.6189 | 224.2857 | 209.518
485.0354 | 209.9762 | 224.6078 | 210.4177
486.0354 | 211.3156 | 226.3315 | 212.4685
487.0354 | 211.2101 | 227.4878 | 213.3667
488.0354 | 211.3397 | 228.558 | 215.4867
489.0354 | 210.8819 | 228.8394 | 216.3809
490.0354 | 209.2036 | 227.808 | 216.6219
491.0354 | 208.7832 | 227.7318 | 215.8307
492.0354 | 210.3756 | 229.36 | 216.1733
493.0354 | 211.1047 | 231.4829 | 216.3599
494.0354 | 211.7207 | 232.774 | 216.9311
495.0354 | 212.8609 | 233.9266 | 217.4717
496.0354 | 212.5323 | 234.2793 | 216.7815
497.0354 | 212.3419 | 234.1249 | 216.2752
498.0354 | 212.6202 | 236.0487 | 216.5397
499.0354 | 213.9755 | 237.9308 | 217.5916
500.0354 | 214.6461 | 238.2532 | 218.4566
501.0354 | 215.7193 | 239.5324 | 220.3579
502.0354 | 215.4094 | 238.3534 | 220.9781
503.0354 | 215.0638 | 237.579 | 220.7653
504.0354 | 215.631 | 238.1091 | 221.3282
505.051 | 217.0722 | 239.2632 | 222.7166
506.0354 | 218.9172 | 239.6752 | 222.5765
507.0354 | 220.7726 | 241.6067 | 223.2893
508.0354 | 220.3271 | 241.6267 | 223.4336
509.0354 | 220.9569 | 242.1128 | 224.2889
510.0354 | 223.0919 | 242.3844 | 224.5247
511.0354 | 226.5017 | 244.0331 | 225.9462
512.0354 | 226.8636 | 245.6396 | 225.5749
513.0354 | 226.9954 | 245.8709 | 224.9832
514.0354 | 228.577 | 247.4122 | 226.344
515.0354 | 228.4604 | 247.923 | 227.4389
516.0354 | 230.0471 | 248.2171 | 227.7759
517.0354 | 228.8278 | 247.7254 | 226.6005
518.0354 | 228.685 | 248.7137 | 225.9089
519.0354 | 227.9766 | 247.8659 | 225.2859
520.0354 | 228.6858 | 248.2445 | 225.4119
521.0354 | 228.5423 | 248.87 | 224.4245
522.0354 | 228.283 | 248.8628 | 224.924
523.0354 | 228.1941 | 248.8744 | 225.7206
524.0354 | 228.9104 | 248.7407 | 225.2908
525.0354 | 228.1583 | 249.0601 | 225.3156
526.0354 | 227.3886 | 248.5461 | 224.3392
527.0354 | 227.9312 | 249.2086 | 224.5826
528.0354 | 229.9236 | 249.1053 | 225.3278
529.0354 | 230.1061 | 247.3995 | 224.2812
530.0354 | 232.2972 | 247.8211 | 224.4779
531.0354 | 233.0453 | 248.4987 | 224.5648
532.0354 | 233.5714 | 248.9831 | 225.1744
533.0354 | 233.821 | 248.7461 | 225.1065
534.0354 | 233.8447 | 249.7396 | 225.4964
535.0354 | 233.1744 | 248.486 | 224.4074
536.0354 | 234.2647 | 248.854 | 224.5038
537.0354 | 233.9253 | 249.1637 | 225.3479
538.0354 | 233.4963 | 250.9448 | 225.7397
539.0354 | 232.953 | 251.9111 | 226.0175
540.0354 | 233.4243 | 253.4292 | 226.7756
541.0354 | 234.413 | 253.73 | 226.3674
542.0354 | 234.5141 | 254.3262 | 227.3712
543.0354 | 235.2419 | 255.4735 | 227.0934
544.0354 | 234.354 | 255.7551 | 228.5136
545.0354 | 234.4431 | 256.4512 | 228.8103
546.0354 | 234.3308 | 256.4795 | 228.6355
547.0354 | 233.7955 | 257.5423 | 229.8251
548.0354 | 235.7529 | 257.8508 | 229.7989
549.0354 | 236.0423 | 259.1617 | 230.5274
550.0354 | 235.944 | 259.2819 | 231.0472
551.0354 | 236.2949 | 260.0254 | 230.3206
552.0354 | 238.3009 | 262.23 | 232.3263
553.0354 | 237.4592 | 263.1478 | 233.6012
554.0354 | 237.2523 | 263.8861 | 235.0091
555.0354 | 236.6423 | 264.1882 | 235.6505
556.0354 | 238.0456 | 264.5607 | 237.4929
557.0354 | 240.1486 | 265.9641 | 239.6694
558.0354 | 239.3681 | 264.665 | 239.3138
559.0354 | 239.6729 | 264.0773 | 239.422
560.0354 | 238.8363 | 263.4836 | 238.6393
561.0354 | 238.8183 | 264.2257 | 239.8979
562.0354 | 238.5795 | 264.6215 | 240.4223
563.0354 | 240.2653 | 265.3094 | 241.0599
564.0354 | 239.8491 | 265.7217 | 242.097
565.0354 | 239.99 | 266.9753 | 242.8794
566.0354 | 240.7033 | 266.4737 | 243.1882
567.0354 | 241.0542 | 266.0469 | 243.6414
568.0354 | 240.5223 | 265.954 | 243.0911
569.0354 | 241.0753 | 264.5954 | 242.7741
570.0354 | 240.4801 | 265.5211 | 243.6709
571.0354 | 240.6364 | 264.8854 | 243.6143
572.0354 | 240.8387 | 264.733 | 243.7225
573.0354 | 239.9469 | 265.1158 | 243.7395
574.0354 | 239.5232 | 264.3093 | 242.3309
575.0354 | 239.3719 | 263.0401 | 240.9831
576.0354 | 240.0946 | 262.5833 | 240.9033
577.0354 | 240.8377 | 261.6993 | 239.331
578.0354 | 240.3058 | 261.5476 | 237.7717
579.0354 | 241.7143 | 261.3341 | 238.5029
580.0354 | 240.5869 | 260.5225 | 238.0548
581.0354 | 240.4491 | 259.2885 | 237.2063
582.0354 | 240.2464 | 258.4912 | 236.6539
583.0354 | 239.9537 | 258.1295 | 236.1105
584.0354 | 240.0475 | 259.0467 | 236.1917
585.0354 | 240.1282 | 259.7483 | 235.7868
586.0354 | 239.3193 | 259.738 | 235.7172
587.0354 | 239.3363 | 260.7673 | 236.0056
588.0354 | 239.2137 | 260.9376 | 235.7313
589.0354 | 239.9599 | 261.4449 | 235.2199
590.0354 | 239.4908 | 260.8079 | 234.1061
591.0354 | 240.634 | 261.3651 | 233.2568
592.0354 | 240.8934 | 262.8479 | 234.9458
593.0354 | 240.6138 | 262.157 | 234.5559
594.0354 | 240.5093 | 261.2255 | 234.1029
595.0354 | 240.3775 | 260.1784 | 232.8682
596.0354 | 239.5022 | 259.4101 | 232.2981
597.0354 | 240.4599 | 258.857 | 230.7671
598.0354 | 241.9708 | 259.7305 | 230.7186
599.0354 | 243.1726 | 260.8443 | 231.272
600.0354 | 242.9068 | 260.2658 | 231.1149
601.0354 | 244.3847 | 262.5984 | 232.182
602.0354 | 245.3271 | 262.3621 | 232.9404
603.0354 | 243.8792 | 261.8782 | 233.6604
604.0354 | 244.064 | 261.4256 | 233.1931
605.0354 | 244.4089 | 261.6781 | 234.2987
606.0354 | 244.0414 | 260.7145 | 233.1888
607.0354 | 244.3138 | 259.9816 | 231.7341
608.0354 | 244.3396 | 260.1298 | 232.9457
609.0354 | 243.3832 | 260.4701 | 233.5318
610.0354 | 243.9158 | 261.4933 | 234.8233
611.0354 | 246.1541 | 262.2965 | 235.8452
612.0354 | 245.3193 | 262.0302 | 236.955
613.0354 | 245.3051 | 262.7428 | 235.9159
614.0354 | 246.9504 | 263.472 | 237.1901
615.0354 | 247.2286 | 263.2896 | 237.3775
616.0354 | 245.3505 | 263.2102 | 236.6052
617.0354 | 245.4685 | 262.2148 | 236.0813
618.0354 | 245.5538 | 261.8006 | 235.1537
619.0354 | 245.6563 | 260.3426 | 233.9908
620.0354 | 246.908 | 260.1888 | 233.4283
621.0354 | 248.3406 | 261.133 | 233.6524
622.0354 | 250.1418 | 262.0416 | 234.3016
623.0354 | 251.5739 | 262.5975 | 236.1627
624.0354 | 252.9165 | 263.023 | 236.0376
625.0354 | 253.9998 | 263.7265 | 236.4744
626.0354 | 252.2151 | 263.2907 | 235.7347
627.0354 | 253.5848 | 263.1042 | 235.9652
628.0354 | 253.499 | 263.274 | 235.2908
629.0354 | 253.2333 | 264.3028 | 236.6409
630.0354 | 252.6612 | 264.393 | 236.7713
631.0354 | 252.2406 | 264.3254 | 236.5581
632.0354 | 251.7531 | 264.9857 | 236.2331
633.0354 | 250.3881 | 265.6707 | 235.8002
634.0354 | 249.6896 | 265.4707 | 234.8714
635.0354 | 251.6681 | 266.7019 | 236.5455
636.0354 | 252.2172 | 266.7081 | 237.1517
637.0354 | 250.6293 | 265.4113 | 236.6371
638.0354 | 249.7965 | 264.4981 | 235.5153
639.0354 | 249.17 | 263.192 | 234.797
640.0354 | 249.0002 | 262.6432 | 234.7325
641.0354 | 249.6726 | 263.6868 | 235.5245
642.0354 | 248.3338 | 263.5007 | 235.3097
643.0354 | 249.7567 | 264.401 | 235.321
644.0354 | 250.5759 | 266.2345 | 235.805
645.0354 | 250.9442 | 266.9881 | 235.947
646.0354 | 251.062 | 266.8858 | 237.7527
647.0354 | 250.0497 | 266.9398 | 237.8655
648.0354 | 251.082 | 267.664 | 238.8567
649.0354 | 250.3086 | 267.1059 | 239.458
650.0354 | 249.5621 | 266.771 | 239.4982
651.0354 | 250.4723 | 267.6492 | 240.7268
652.0354 | 252.5623 | 269.3316 | 241.8959
653.0354 | 252.244 | 269.3342 | 242.3329
654.0354 | 251.8191 | 268.4501 | 241.5708
655.0354 | 251.1258 | 267.7885 | 241.4832
656.0354 | 250.3036 | 267.1631 | 241.3172
657.0354 | 251.3381 | 268.3789 | 241.0282
658.0354 | 251.1948 | 268.7417 | 241.2366
659.0354 | 250.6314 | 269.1918 | 240.6347
660.0354 | 250.4276 | 268.3611 | 239.9192
661.0354 | 251.4765 | 267.6815 | 240.4748
662.0354 | 252.7272 | 268.3809 | 241.6078
663.0354 | 251.4822 | 267.9573 | 242.3749
664.0354 | 251.8036 | 267.5442 | 241.7107
665.0354 | 250.1022 | 266.9966 | 241.32
666.0354 | 249.2987 | 266.058 | 240.2019
667.0354 | 248.3114 | 265.1153 | 239.8453
668.0354 | 247.1126 | 264.9507 | 238.7458
669.0354 | 247.4647 | 264.1894 | 238.3116
670.0354 | 247.5376 | 263.8172 | 237.1629
671.0354 | 247.1457 | 263.1918 | 237.3596
672.0354 | 245.9848 | 260.9219 | 236.0783
673.0354 | 245.0041 | 260.5026 | 235.7725
674.0354 | 243.7367 | 260.5686 | 235.2723
675.0354 | 243.3414 | 260.2647 | 235.0406
676.0354 | 243.0793 | 259.7438 | 234.6324
677.0354 | 244.4199 | 259.9621 | 234.9565
678.0354 | 246.0208 | 260.6568 | 235.2064
679.0354 | 247.024 | 261.6655 | 236.3315
680.0354 | 246.4786 | 261.3681 | 235.2402
681.0354 | 246.5382 | 260.6684 | 234.875
682.0354 | 247.3148 | 260.9598 | 234.1983
683.0354 | 247.9135 | 260.9187 | 233.2245
684.0354 | 248.126 | 261.0444 | 232.7307
685.0354 | 248.2663 | 260.7407 | 232.6108
686.0354 | 247.8457 | 260.2402 | 231.9725
687.0354 | 247.5339 | 259.8995 | 232.0743
688.0354 | 247.9764 | 259.6566 | 231.5079
689.0354 | 247.4889 | 259.3917 | 230.9337
690.0354 | 247.4807 | 259.6943 | 230.3502
691.0354 | 246.8429 | 259.5239 | 230.193
692.0354 | 246.5738 | 258.8696 | 229.8417
693.0354 | 246.7974 | 258.9421 | 229.5477
694.0354 | 246.667 | 258.4079 | 228.7979
695.0354 | 246.1394 | 258.5571 | 228.863
696.0354 | 246.1018 | 257.5571 | 228.183
697.0354 | 245.5619 | 258.578 | 228.613
698.0354 | 245.0755 | 259.2277 | 229.0338
699.0354 | 245.3832 | 260.6382 | 229.4287
700.0354 | 246.0325 | 262.1204 | 230.0266
701.0354 | 248.5839 | 262.4188 | 231.9094
702.0354 | 249.8579 | 262.8234 | 233.4679
703.0354 | 249.7221 | 263.1451 | 233.775
704.0354 | 249.0603 | 263.9959 | 233.551
705.0354 | 248.9245 | 263.9693 | 233.5078
706.0354 | 250.1116 | 265.2674 | 234.6997
707.0354 | 251.6097 | 266.1101 | 235.9293
708.0354 | 251.6403 | 266.5902 | 236.7816
709.0354 | 251.2518 | 267.0235 | 238.3035
710.0354 | 251.6759 | 265.8052 | 237.7441
711.0354 | 251.9711 | 265.3703 | 238.1099
712.0354 | 253.1806 | 265.3571 | 238.4642
713.0354 | 253.4001 | 265.2027 | 238.7947
714.0354 | 251.9978 | 264.6369 | 238.5
715.0354 | 250.8101 | 263.8846 | 237.1824
716.0354 | 250.0766 | 263.1146 | 235.9313
717.0354 | 250.5627 | 263.2614 | 236.0547
718.0354 | 249.727 | 262.6067 | 236.6434
719.0354 | 250.0054 | 262.3057 | 235.6909
720.0354 | 249.3142 | 262.6407 | 236.6752
721.0354 | 250.0595 | 261.856 | 236.0909
722.0354 | 250.3429 | 262.5571 | 236.8735
723.0354 | 250.1014 | 263.6716 | 236.157
724.0354 | 249.6852 | 263.5661 | 236.8478
725.0354 | 250.3479 | 264.8432 | 236.4691
726.0354 | 250.193 | 264.4068 | 235.8785
727.0354 | 249.6133 | 264.6452 | 235.1012
728.0354 | 250.6471 | 264.4306 | 236.8977
729.0354 | 252.2287 | 265.7243 | 238.3701
730.0354 | 252.3701 | 264.6144 | 237.7307
731.0354 | 251.8096 | 263.4151 | 236.6234
732.0354 | 250.9169 | 262.6553 | 235.3632
733.0354 | 250.6728 | 263.001 | 235.7076
734.0354 | 250.1634 | 262.8062 | 235.6296
735.0354 | 251.5809 | 263.3826 | 237.0301
736.0354 | 253.2078 | 265.936 | 239.321
737.0354 | 252.3758 | 266.6933 | 240.7792
738.0354 | 252.151 | 265.9529 | 240.7458
739.0354 | 251.5562 | 264.9317 | 240.562
740.0354 | 251.2966 | 264.4349 | 239.5274
741.0354 | 251.6216 | 264.1231 | 238.3078
742.0354 | 252.1276 | 264.3497 | 238.2731
743.0354 | 252.5321 | 263.8699 | 237.6081
744.0354 | 252.6939 | 263.8786 | 237.1974
745.0354 | 252.2729 | 263.7768 | 237.0405
746.0354 | 251.5625 | 263.3228 | 236.0337
747.0354 | 251.521 | 262.3754 | 234.9676
748.0354 | 250.9808 | 261.2913 | 233.9784
749.0354 | 251.8621 | 261.6576 | 233.6211
750.0354 | 251.7992 | 263.1656 | 234.7877
751.0354 | 252.1717 | 265.4154 | 237.2098
752.0354 | 251.6676 | 266.8322 | 239.4865
753.0354 | 250.6834 | 268.6319 | 241.4231
754.0354 | 250.8958 | 269.3334 | 242.0551
755.0354 | 251.0025 | 269.7332 | 242.2851
756.0354 | 250.9474 | 269.1019 | 243.0781
757.0354 | 251.8185 | 269.6046 | 243.4829
758.0354 | 250.8594 | 267.8459 | 242.7001
759.0354 | 250.0977 | 266.7486 | 241.6674
760.0354 | 248.6716 | 265.7295 | 240.4838
761.0354 | 248.687 | 264.2419 | 239.9856
762.0354 | 248.4829 | 263.7055 | 238.9884
763.0354 | 247.1911 | 262.2213 | 237.8951
764.0354 | 247.3488 | 261.5884 | 236.6902
765.0354 | 246.5012 | 261.3433 | 235.5888
766.0354 | 247.3186 | 262.0071 | 234.9959
767.0354 | 245.914 | 260.3332 | 234.0933
768.0354 | 246.723 | 259.154 | 233.086
769.0354 | 247.7881 | 257.7986 | 232.0318
770.0354 | 247.4546 | 257.3788 | 230.9381
771.0354 | 248.6085 | 258.216 | 230.8464
772.0354 | 248.3231 | 258.5603 | 231.3509
773.0354 | 248.889 | 259.1518 | 231.2684
774.0354 | 250.3528 | 259.4061 | 231.8293
775.0354 | 250.2993 | 258.0939 | 231.6874
776.0354 | 250.5457 | 257.802 | 231.8171
777.0354 | 251.0813 | 258.6505 | 231.3991
778.0354 | 250.3721 | 257.1518 | 231.2113
779.0354 | 250.0388 | 256.8426 | 231.4286
780.0354 | 249.4802 | 256.4081 | 231.0027
781.0354 | 249.1117 | 255.3168 | 230.4292
782.0354 | 249.1052 | 255.3799 | 230.6007
783.0354 | 248.7025 | 256.6081 | 231.4507
784.0354 | 248.1821 | 258.0263 | 232.6277
785.0354 | 248.2075 | 259.0395 | 232.928
786.0354 | 248.1391 | 259.2776 | 232.4225
787.0354 | 248.4258 | 260.5052 | 233.4185
788.0354 | 248.174 | 259.6371 | 233.8283
789.0354 | 248.3921 | 259.9914 | 234.5723
790.0354 | 247.2957 | 259.6055 | 235.7723
791.0354 | 247.9296 | 261.2417 | 236.5713
792.0354 | 247.7823 | 261.7873 | 237.4895
793.0354 | 248.6912 | 262.2517 | 237.4173
794.0354 | 247.8259 | 262.2746 | 237.3881
795.0354 | 247.5695 | 262.668 | 237.1353
796.0354 | 247.5666 | 263.1618 | 237.2693
797.0354 | 248.6227 | 261.6742 | 236.9153
798.0354 | 248.1002 | 261.7045 | 236.7518
799.0354 | 249.7366 | 262.1662 | 236.6129
800.0354 | 249.9393 | 261.7982 | 237.1528
801.0354 | 249.9803 | 262.7435 | 237.009
802.0354 | 249.5322 | 262.7033 | 237.1252
803.0354 | 249.4309 | 262.8389 | 237.5138
804.0354 | 249.2419 | 262.5522 | 236.8902
805.0354 | 250.1324 | 262.9599 | 237.0765
806.0354 | 249.3901 | 262.842 | 237.2252
807.0354 | 249.7774 | 263.2963 | 239.0952
808.0354 | 250.7903 | 264.6606 | 239.7259
809.0354 | 249.6656 | 265.1252 | 241.0074
810.0354 | 249.8978 | 265.9187 | 240.815
811.0354 | 251.0909 | 265.5447 | 240.957
812.0354 | 251.0489 | 265.0238 | 241.2201
813.0354 | 249.7662 | 265.636 | 241.1545
814.0354 | 249.4128 | 265.086 | 240.6112
815.0354 | 248.9711 | 264.681 | 239.7103
816.0354 | 248.6636 | 263.7555 | 238.5714
817.0354 | 248.364 | 263.533 | 238.2804
818.0354 | 249.8027 | 264.0567 | 238.0363
819.0354 | 249.5816 | 263.8954 | 239.1227
820.0354 | 249.7145 | 263.928 | 238.5878
821.0354 | 249.383 | 264.5954 | 240.1493
822.0354 | 251.2766 | 265.0103 | 241.0107
823.0354 | 252.8731 | 264.183 | 240.4016
824.0354 | 253.1197 | 263.4279 | 240.7812
825.0354 | 253.5438 | 263.653 | 239.5939
826.0354 | 255.0923 | 264.0419 | 239.9127
827.0354 | 256.7535 | 264.4911 | 241.0098
828.0354 | 256.9773 | 264.1497 | 241.8754
829.0354 | 256.1085 | 263.2957 | 241.5539
830.0354 | 256.2119 | 263.114 | 241.4224
831.0354 | 254.8591 | 263.0618 | 241.6793
832.0354 | 254.4116 | 262.5845 | 240.8727
833.0354 | 253.7609 | 261.5417 | 240.135
834.0354 | 253.3012 | 261.4972 | 239.1295
835.0354 | 251.8519 | 260.3436 | 238.0153
836.0354 | 250.8608 | 259.0634 | 237.4343
837.0354 | 250.1756 | 258.4542 | 236.3446
838.0354 | 249.679 | 258.1971 | 235.8818
839.0354 | 250.3871 | 259.0012 | 236.1403
840.0354 | 249.579 | 257.9721 | 235.1078
841.0354 | 249.0298 | 256.996 | 234.1919
842.0354 | 248.8294 | 256.9164 | 233.0322
843.0354 | 249.3137 | 257.7857 | 234.0309
844.0354 | 248.7462 | 257.6841 | 234.5807
845.0354 | 249.8812 | 257.7365 | 233.8435
846.0354 | 249.1894 | 257.3757 | 233.4095
847.0354 | 249.2917 | 257.8704 | 232.7787
848.0354 | 248.658 | 259.0578 | 234.0967
849.0354 | 248.1891 | 258.618 | 233.4704
850.0354 | 247.6193 | 259.7961 | 233.218
851.0354 | 247.7012 | 259.8826 | 233.6192
852.0354 | 247.8101 | 259.8917 | 233.5756
853.0354 | 247.7218 | 260.221 | 233.8529
854.0354 | 247.8014 | 261.1059 | 233.6206
855.0354 | 247.5785 | 261.4387 | 233.8847
856.0354 | 248.904 | 261.7704 | 234.6303
857.0354 | 250.2388 | 261.9401 | 234.6898
858.0354 | 251.2397 | 261.2421 | 234.4455
859.0354 | 251.1317 | 261.0992 | 235.4019
860.0354 | 250.62 | 259.9562 | 234.7482
861.0354 | 250.5683 | 259.799 | 234.0228
862.0354 | 250.2748 | 259.6237 | 233.9465
863.0354 | 249.2661 | 259.1777 | 234.004
864.0354 | 249.3844 | 259.4697 | 234.5166
865.0354 | 249.3991 | 259.4171 | 234.7783
866.0354 | 249.5653 | 260.3242 | 235.2198
867.0354 | 248.4026 | 259.6414 | 234.5359
868.0354 | 247.5419 | 259.5529 | 234.5978
869.0354 | 247.3965 | 259.5636 | 234.7844
870.0354 | 247.6096 | 260.7542 | 235.5535
871.0354 | 247.9162 | 261.3294 | 235.2525
872.0354 | 249.0857 | 262.3142 | 236.0192
873.0354 | 249.0221 | 261.8105 | 236.152
874.0354 | 250.0937 | 262.7919 | 236.8167
875.0354 | 249.7366 | 262.6942 | 236.6194
876.0354 | 248.8858 | 261.7267 | 235.8696
877.0354 | 249.3752 | 261.0679 | 235.8364
878.0354 | 248.0313 | 260.5895 | 236.4532
879.0354 | 247.8281 | 260.2891 | 236.851
880.0354 | 247.2996 | 260.0671 | 237.4244
881.0354 | 248.222 | 260.2898 | 237.8157
882.0354 | 247.276 | 260.7137 | 238.9369
883.0354 | 247.1865 | 261.0037 | 238.9058
884.0354 | 246.6952 | 260.4377 | 238.755
885.0354 | 245.7584 | 260.7437 | 238.8065
886.0354 | 245.6215 | 260.054 | 238.8574
887.0354 | 245.2851 | 259.7542 | 238.5166
888.0354 | 244.3366 | 259.1279 | 238.485
889.0354 | 243.6011 | 259.2759 | 238.1626
890.0354 | 244.2523 | 259.1913 | 236.9777
891.0354 | 244.2633 | 258.5488 | 235.5499
892.0354 | 243.4986 | 258.8333 | 235.6672
893.0354 | 243.2926 | 257.8256 | 235.7533
894.0354 | 242.6997 | 257.1956 | 235.488
895.0354 | 242.7991 | 256.7471 | 234.7163
896.0354 | 241.966 | 255.5884 | 234.5536
897.0354 | 241.6761 | 254.7688 | 234.9243
898.0354 | 241.8226 | 254.8371 | 236.3486
899.0354 | 240.3661 | 255.3997 | 237.1807
900.0354 | 240.2684 | 256.969 | 239.289
901.0354 | 240.9491 | 257.704 | 238.9496
902.0354 | 241.6292 | 257.952 | 238.5367
903.0354 | 242.2816 | 258.2961 | 238.5709
904.0354 | 241.8688 | 259.9364 | 240.4431
905.0354 | 243.1455 | 260.9636 | 240.192
906.0354 | 243.3791 | 261.8933 | 240.8836
907.0354 | 244.453 | 262.9685 | 240.5929
908.0354 | 245.745 | 264.9626 | 242.8123
909.0354 | 248.7262 | 267.1838 | 244.7108
910.0354 | 251.802 | 267.6697 | 245.8993
911.0354 | 253.9432 | 267.9764 | 246.8484
912.0354 | 255.2461 | 268.367 | 247.1912
913.0354 | 257.6089 | 269.8033 | 248.8509
914.0354 | 259.3198 | 270.245 | 248.972
915.0354 | 260.2405 | 271.8351 | 250.1624
916.0354 | 262.2142 | 273.1371 | 251.1392
917.0354 | 263.1488 | 273.9347 | 251.5289
918.0354 | 264.4641 | 274.8757 | 252.0307
919.0354 | 264.0842 | 275.4826 | 253.2125
920.0354 | 264.2035 | 276.7419 | 253.248
921.0354 | 263.8723 | 279.0534 | 254.4506
922.0354 | 264.927 | 279.954 | 255.3296
923.0354 | 266.4054 | 281.3408 | 255.1487
924.0354 | 267.1983 | 280.8857 | 254.6659
925.0354 | 267.6989 | 281.2088 | 253.7813
926.0354 | 268.3965 | 281.2563 | 254.0752
927.0354 | 268.6313 | 281.5447 | 254.5006
928.0354 | 268.2583 | 282.5494 | 255.0601
929.0354 | 270.5318 | 284.1956 | 257.8103
930.0354 | 271.729 | 285.0592 | 257.8572
931.0354 | 272.266 | 285.6277 | 259.5289
932.0354 | 271.2413 | 286.6032 | 259.6454
933.0354 | 271.5626 | 287.9284 | 260.4307
934.0354 | 271.7975 | 287.376 | 260.5745
935.0354 | 271.4429 | 287.1128 | 260.6774
936.0354 | 271.8968 | 286.8767 | 260.7455
937.0354 | 275.7612 | 288.8994 | 262.1105
938.0354 | 277.9934 | 290.9237 | 263.6722
939.0354 | 277.2387 | 291.5205 | 265.0219
940.0354 | 277.7334 | 292.0077 | 265.7727
941.0354 | 277.7254 | 292.7962 | 265.8743
942.0354 | 277.3298 | 292.6213 | 266.2139
943.0354 | 277.0179 | 292.4616 | 265.897
944.0354 | 276.3123 | 293.8292 | 267.1703
945.0354 | 274.9884 | 294.7373 | 267.3673
946.0354 | 277.3069 | 295.6932 | 266.9531
947.0354 | 277.3393 | 294.9164 | 265.4392
948.0354 | 277.0511 | 293.5502 | 264.6332
949.0354 | 276.8491 | 293.4798 | 263.4106
950.0354 | 277.5642 | 294.1459 | 263.1711
951.0354 | 277.7125 | 295.2017 | 263.0519
952.0354 | 278.0878 | 294.4086 | 262.7845
953.0354 | 278.5672 | 293.3637 | 262.7838
954.0354 | 278.255 | 293.8288 | 262.2539
955.0354 | 278.0063 | 292.7927 | 262.8328
956.0354 | 278.9173 | 292.2143 | 262.3673
957.0354 | 280.873 | 292.7524 | 263.248
958.0354 | 279.6072 | 291.8271 | 261.8987
959.0354 | 278.8539 | 291.7666 | 261.6716
960.0354 | 278.1761 | 291.5284 | 261.3413
961.0354 | 277.3387 | 291.4514 | 260.8703
962.0354 | 277.6951 | 291.0134 | 259.5748
963.0354 | 277.08 | 290.4948 | 259.3042
964.0354 | 279.4108 | 291.5311 | 259.8316
965.0354 | 280.5347 | 292.8215 | 260.3928
966.0354 | 280.9188 | 293.2917 | 260.6671
967.0354 | 281.4775 | 293.9394 | 261.4931
968.0354 | 282.1288 | 293.8857 | 260.6258
969.0354 | 282.2954 | 293.4165 | 260.9572
970.0198 | 281.6586 | 292.9462 | 260.4394
971.0354 | 282.9965 | 293.5568 | 261.6046
972.0354 | 283.7751 | 295.291 | 263.6599
973.0354 | 285.0521 | 297.0688 | 265.6342
974.0354 | 285.1024 | 297.2807 | 265.6942
975.0354 | 285.6617 | 297.2904 | 267.6205
976.0354 | 284.094 | 296.5589 | 266.784
977.0354 | 285.2415 | 297.0871 | 267.1098
978.0354 | 286.9939 | 297.6331 | 268.3592
979.0354 | 287.456 | 296.9586 | 267.0535
980.0354 | 288.1693 | 297.042 | 266.749
981.0354 | 287.8483 | 295.7059 | 265.0982
982.0354 | 287.1617 | 296.8459 | 264.2259
983.0354 | 287.4324 | 298.1265 | 264.2211
984.0354 | 289.0884 | 299.6903 | 264.7091
985.0354 | 289.1126 | 299.5793 | 266.0257
986.0354 | 289.6979 | 300.385 | 265.699
987.0354 | 289.9507 | 301.8879 | 266.5612
988.0354 | 289.7328 | 303.0619 | 266.7779
989.0354 | 290.1565 | 303.0215 | 267.1731
990.0354 | 291.181 | 303.6247 | 267.4976
991.0354 | 292.1873 | 303.4376 | 266.903
992.0354 | 293.2566 | 305.221 | 269.5781
993.0354 | 291.958 | 305.8688 | 269.8688
994.0354 | 291.7787 | 306.1 | 270.3457
995.0354 | 291.1724 | 306.6222 | 270.3468
996.0354 | 290.7356 | 306.8847 | 270.155
997.0354 | 290.1715 | 307.1293 | 270.2883
998.0354 | 290.154 | 307.0541 | 271.657
999.0354 | 291.1888 | 308.0117 | 272.1655
1000.0354 | 291.9602 | 307.2851 | 272.0171
1001.0354 | 290.7685 | 306.8472 | 271.3505
1002.0354 | 291.7087 | 306.7976 | 272.0974
1003.0354 | 293.1201 | 307.2289 | 272.998
1004.0354 | 293.4934 | 307.3122 | 273.1389
1005.0354 | 294.4406 | 309.0257 | 275.6505
1006.0354 | 294.1177 | 309.1443 | 274.6776
1007.0354 | 296.6047 | 311.4623 | 277.0207
1008.0354 | 297.362 | 310.7733 | 277.4119
1009.0354 | 298.6038 | 310.5747 | 277.9933
1010.0354 | 298.8611 | 310.5823 | 277.69
1011.0354 | 298.7235 | 309.4117 | 277.6286
1012.0198 | 297.2761 | 308.5167 | 276.8385
1013.0354 | 297.1067 | 309.1256 | 277.6101
1014.0354 | 296.2975 | 308.9412 | 276.7436
1015.0354 | 296.4032 | 308.9454 | 277.1677
1016.0354 | 295.7026 | 308.124 | 277.1079
1017.0354 | 295.4191 | 306.9733 | 276.5142
1018.0354 | 296.3715 | 305.9097 | 276.1184
1019.0354 | 296.904 | 305.8529 | 276.1085
1020.0354 | 297.3593 | 304.3216 | 274.5212
1021.0354 | 297.5189 | 304.4723 | 275.6394
1022.0354 | 298.4482 | 304.997 | 275.7182
1023.0354 | 297.5839 | 306.1637 | 274.8438
1024.0354 | 297.6999 | 306.2044 | 274.7733
1025.0354 | 297.2022 | 306.28 | 273.7652
1026.0354 | 297.0773 | 307.0199 | 274.377
1027.0354 | 297.1635 | 307.2907 | 274.9478
1028.0354 | 296.2349 | 306.6438 | 274.1582
1029.0354 | 296.5139 | 306.5667 | 273.392
1030.0354 | 296.3556 | 305.2442 | 272.0365
1031.0354 | 296.8403 | 304.977 | 271.3998
1032.0354 | 296.3035 | 303.5491 | 270.6983
1033.0354 | 295.8316 | 303.6384 | 271.5084
1034.0354 | 295.6959 | 304.1681 | 270.1693
1035.0354 | 298.8857 | 305.7572 | 271.6189
1036.0354 | 297.8193 | 307.6879 | 272.447
1037.0354 | 299.203 | 308.4759 | 273.8259
1038.0354 | 298.7393 | 307.4786 | 273.4232
1039.0354 | 298.129 | 308.366 | 273.4171
1040.0354 | 299.2227 | 309.9048 | 275.5947
1041.0354 | 299.1499 | 309.4242 | 275.8684
1042.0354 | 298.6409 | 310.0776 | 276.9652
1043.0354 | 299.5685 | 310.4426 | 277.0266
1044.0354 | 299.5297 | 312.5374 | 277.8147
1045.0354 | 299.916 | 311.9914 | 277.6962
1046.0354 | 300.2771 | 312.3965 | 277.4441
1047.0354 | 299.8987 | 311.4602 | 276.6758
1048.0354 | 300.4512 | 311.6868 | 276.7421
1049.0354 | 300.8549 | 311.7181 | 276.4241
1050.0354 | 299.7704 | 311.445 | 276.8585
1051.0354 | 299.716 | 311.5619 | 277.0949
1052.0354 | 299.9745 | 311.2924 | 276.9959
1053.0354 | 299.8635 | 310.4802 | 276.8207
1054.0354 | 298.7733 | 310.3427 | 276.9248
1055.0354 | 298.9902 | 310.5338 | 277.56
1056.0354 | 298.3093 | 310.2982 | 277.7437
1057.0354 | 297.881 | 310.3371 | 278.6479
1058.0354 | 297.8782 | 311.0831 | 279.2987
1059.0354 | 298.3876 | 312.282 | 279.5109
1060.0354 | 298.8224 | 311.582 | 279.0807
1061.0354 | 299.0949 | 310.8952 | 278.5111
1062.0354 | 300.0757 | 311.4422 | 278.123
1063.0354 | 299.2489 | 311.986 | 277.8292
1064.0354 | 298.991 | 312.6692 | 277.8726
1065.0354 | 299.1521 | 312.9706 | 277.4861
1066.0354 | 299.6961 | 311.8625 | 276.2968
1067.0354 | 299.2561 | 310.9821 | 275.8039
1068.0354 | 299.9444 | 311.0277 | 276.0736
1069.0354 | 300.1861 | 310.7435 | 275.4728
1070.0354 | 301.4419 | 310.7295 | 275.926
1071.0354 | 302.5361 | 310.5414 | 275.2763
1072.0354 | 302.2593 | 309.7919 | 275.5262
1073.0354 | 301.5918 | 311.8447 | 276.7244
1074.0354 | 302.319 | 314.5494 | 278.3023
1075.0354 | 304.5422 | 316.7136 | 280.7911
1076.0354 | 305.2433 | 317.961 | 282.5104
1077.0354 | 305.3429 | 318.1593 | 282.4518
1078.0354 | 308.2476 | 318.0017 | 282.3694
1079.0354 | 310.181 | 320.3106 | 284.2565
1080.0354 | 310.6841 | 319.7883 | 284.8038
1081.0354 | 311.5246 | 319.6614 | 284.8543
1082.0354 | 312.081 | 319.2588 | 283.9069
1083.0354 | 311.8868 | 318.1462 | 283.4112
1084.0354 | 311.555 | 317.4984 | 282.6225
1085.0354 | 310.8706 | 317.0698 | 283.1153
1086.0354 | 310.8101 | 317.6586 | 282.5811
1087.0354 | 311.2209 | 317.4589 | 281.7013
1088.0354 | 311.95 | 317.7413 | 280.7672
1089.0354 | 312.1876 | 318.2015 | 280.3593
1090.0354 | 311.3074 | 317.456 | 280.0962
1091.0354 | 311.9063 | 317.5918 | 279.7766
1092.0354 | 311.6387 | 319.174 | 281.0802
1093.0354 | 311.4498 | 318.7888 | 280.3292
1094.0354 | 311.2063 | 317.9094 | 281.0511
1095.0354 | 310.7523 | 316.9534 | 279.6857
1096.0354 | 309.5506 | 316.1229 | 279.0817
1097.0354 | 309.3798 | 315.7223 | 278.6633
1098.0354 | 308.1174 | 315.9492 | 278.8417
1099.0354 | 308.1202 | 315.7692 | 279.4608
1100.0354 | 308.0383 | 316.5027 | 280.8988
1101.0354 | 307.0358 | 316.5946 | 280.8832
1102.0354 | 307.2334 | 317.244 | 281.1401
1103.0354 | 307.7573 | 317.873 | 282.1725
1104.0354 | 308.0018 | 318.4376 | 283.5186
1105.0354 | 308.3948 | 318.1136 | 282.887
1106.0354 | 308.4415 | 319.0493 | 282.4907
1107.0354 | 308.184 | 319.041 | 282.8097
1108.0354 | 308.9416 | 318.5301 | 283.3644
1109.0354 | 309.6874 | 319.2898 | 285.1463
1110.0354 | 308.461 | 319.4676 | 285.9607
1111.0354 | 308.2529 | 319.7951 | 286.0854
1112.0354 | 307.2452 | 320.7757 | 287.0294
1113.0354 | 306.8441 | 320.3178 | 286.8283
1114.0354 | 306.3391 | 320.6578 | 287.204
1115.0354 | 306.3321 | 320.7865 | 288.4652
1116.0354 | 306.6399 | 320.8191 | 289.1036
1117.0354 | 306.7961 | 321.3099 | 290.4607
1118.0354 | 307.0778 | 320.6774 | 290.7017
1119.0354 | 306.322 | 322.4269 | 292.4101
1120.0354 | 306.4491 | 323.1373 | 293.1649
1121.0354 | 305.8983 | 324.9969 | 293.6141
1122.0354 | 306.351 | 325.7798 | 293.6578
1123.0354 | 307.7755 | 326.0667 | 293.7909
1124.0354 | 309.1757 | 327.0019 | 295.2475
1125.0354 | 308.5298 | 327.8125 | 296.3136
1126.0354 | 308.6005 | 328.3786 | 296.4371
1127.0354 | 308.3025 | 329.0268 | 297.9633
1128.0354 | 309.2635 | 328.9215 | 299.2385
1129.0354 | 311.1286 | 330.1728 | 300.4115
1130.0354 | 311.6098 | 331.9864 | 302.9369
1131.0354 | 311.8539 | 332.1295 | 304.2131
1132.0354 | 311.4951 | 332.9304 | 304.8971
1133.0354 | 311.1425 | 332.7289 | 305.8278
1134.0354 | 311.4016 | 333.2008 | 306.1944
1135.0354 | 311.1868 | 333.0793 | 305.5188
1136.0354 | 311.8237 | 333.5846 | 306.3106
1137.0354 | 311.3344 | 333.7391 | 305.8603
1138.0354 | 310.4274 | 332.8538 | 304.2763
1139.0354 | 311.1046 | 333.1807 | 304.6608
1140.0354 | 311.8123 | 334.1954 | 303.9137
1141.0354 | 312.0843 | 336.5913 | 304.825
1142.0354 | 312.5311 | 337.775 | 306.2674
1143.0354 | 311.34 | 337.7241 | 306.5096
1144.0354 | 310.0823 | 336.6952 | 304.8855
1145.0354 | 310.3997 | 336.4934 | 304.1287
1146.0354 | 310.846 | 335.1247 | 302.4583
1147.0354 | 310.8155 | 334.5127 | 300.8962
1148.0354 | 311.4129 | 333.9815 | 299.8141
1149.0354 | 312.678 | 335.1003 | 299.3482
1150.0354 | 312.6233 | 336.3573 | 300.2883
1151.0354 | 312.9534 | 338.6975 | 302.4595
1152.0354 | 313.9548 | 340.7281 | 303.3125
1153.0354 | 315.51 | 341.6581 | 303.8951
1154.0354 | 315.361 | 342.7307 | 303.7212
1155.0354 | 316.9687 | 342.7004 | 304.417
1156.0354 | 317.1582 | 343.8986 | 304.3008
1157.0354 | 318.8574 | 345.1574 | 305.4249
1158.0354 | 318.5848 | 346.4647 | 306.1053
1159.0354 | 320.8917 | 348.9097 | 307.8464
1160.0354 | 323.5149 | 352.3875 | 310.4545
1161.0354 | 326.2443 | 354.0824 | 311.5992
1162.0354 | 326.7134 | 355.8603 | 313.6771
1163.0354 | 327.1766 | 358.208 | 317.2405
1164.0354 | 329.1565 | 358.6219 | 318.4018
1165.0354 | 329.572 | 358.3516 | 318.195
1166.0354 | 330.4866 | 360.3204 | 320.3051
1167.0354 | 332.345 | 361.5226 | 321.3105
1168.0354 | 332.4315 | 362.1975 | 321.9406
1169.0354 | 331.4502 | 361.0719 | 322.6514
1170.0354 | 330.9909 | 360.6806 | 322.8199
1171.0354 | 332.8234 | 361.7109 | 323.9976
1172.0354 | 332.3273 | 362.2449 | 323.1109
1173.0354 | 333.9291 | 364.025 | 324.3174
1174.0354 | 333.7207 | 362.819 | 323.0962
1175.0354 | 333.6135 | 361.9995 | 322.3818
1176.0354 | 333.5548 | 361.9952 | 321.4178
1177.0354 | 334.1285 | 362.5282 | 321.1912
1178.0354 | 334.7434 | 361.7666 | 319.9619
1179.0354 | 334.4985 | 360.3589 | 318.9979
1180.0354 | 334.4024 | 361.3626 | 318.6296
1181.0354 | 336.0167 | 362.6743 | 320.2447
1182.0354 | 336.0735 | 361.4792 | 319.5605
1183.0354 | 336.0593 | 363.9376 | 319.7657
1184.0354 | 336.6952 | 365.7615 | 320.7847
1185.0354 | 336.2243 | 366.3506 | 321.2068
1186.0354 | 336.8389 | 367.0403 | 321.7462
1187.0354 | 336.7234 | 367.7085 | 323.0901
1188.0354 | 336.8643 | 367.4532 | 322.6913
1189.0354 | 338.5991 | 369.1633 | 324.4581
1190.0354 | 339.3137 | 370.3729 | 325.7314
1191.0354 | 339.6266 | 372.2975 | 325.2751
1192.0354 | 340.3242 | 372.5863 | 325.0855
1193.0354 | 340.2227 | 373.9566 | 326.5028
1194.0354 | 342.1199 | 373.8575 | 327.6566
1195.0354 | 341.7617 | 373.1841 | 326.7628
1196.0354 | 342.8621 | 373.5442 | 328.5413
1197.0354 | 345.3822 | 373.2002 | 329.2178
1198.0354 | 346.8458 | 376.539 | 330.2885
1199.0354 | 347.3017 | 377.1931 | 332.6344
1200.0354 | 346.2345 | 377.2735 | 332.889
1201.0354 | 345.4562 | 377.7833 | 333.3077
1202.0354 | 345.3078 | 377.1728 | 333.0159
1203.0354 | 346.024 | 377.9187 | 333.9005
1204.0354 | 346.9845 | 379.9744 | 335.4449
1205.0354 | 346.6546 | 380.9173 | 334.1705
1206.0354 | 346.8326 | 382.1886 | 334.4969
1207.0354 | 348.0436 | 382.363 | 334.8147
1208.0354 | 350.1708 | 383.1735 | 336.8367
1209.0354 | 351.9109 | 384.0315 | 338.5055
1210.0354 | 352.4034 | 384.8067 | 337.2338
1211.0354 | 354.2527 | 386.1106 | 338.3795
1212.0354 | 355.21 | 386.8055 | 339.0038
1213.0354 | 354.0849 | 386.8607 | 338.1304
1214.0354 | 353.5546 | 387.4963 | 340.044
1215.0354 | 353.7349 | 388.1748 | 340.8857
1216.0354 | 354.6892 | 390.7276 | 340.7011
1217.0354 | 357.1741 | 391.1272 | 341.748
1218.0354 | 358.804 | 391.4915 | 342.2267
1219.0354 | 359.8224 | 392.706 | 344.5455
1220.0354 | 359.6992 | 394.962 | 345.2703
1221.0354 | 361.0846 | 395.5925 | 345.4024
1222.0354 | 361.3967 | 396.6876 | 344.6569
1223.0354 | 362.4799 | 395.533 | 343.9466
1224.0354 | 362.9946 | 396.3963 | 342.868
1225.0354 | 364.1284 | 399.6576 | 343.0598
1226.0354 | 364.2287 | 402.3756 | 344.2401
1227.0354 | 364.5073 | 404.3274 | 344.2521
1228.0354 | 364.2424 | 405.0486 | 344.8062
1229.0354 | 367.1705 | 406.5375 | 345.8611
1230.0354 | 369.1713 | 406.8699 | 346.427
1231.0354 | 370.7022 | 407.1506 | 346.5988
1232.0354 | 372.9133 | 409.2343 | 345.9613
1233.0354 | 373.8363 | 410.6062 | 346.9393
1234.0354 | 374.5247 | 409.9822 | 347.431
1235.0354 | 374.4617 | 410.0519 | 347.6419
1236.0354 | 376.0451 | 409.9884 | 348.4994
1237.0354 | 375.1344 | 410.5409 | 348.0521
1238.0354 | 375.2531 | 410.3791 | 347.811
1239.0354 | 374.7972 | 409.6263 | 346.649
1240.0354 | 375.4299 | 409.9752 | 346.4516
1241.0354 | 375.196 | 409.9996 | 347.1736
1242.0354 | 374.7596 | 410.3321 | 348.0521
1243.0354 | 375.4641 | 410.9346 | 348.6548
1244.0354 | 376.1427 | 412.0856 | 349.8839
1245.0354 | 376.2247 | 411.6328 | 349.7577
1246.0354 | 375.9862 | 409.8993 | 348.8291
1247.0354 | 376.9042 | 410.324 | 348.8685
1248.0354 | 376.7458 | 410.3872 | 348.6181
1249.0354 | 376.7016 | 411.2846 | 349.0951
1250.0354 | 377.3847 | 412.3249 | 350.5287
1251.0354 | 378.2502 | 413.8543 | 353.4297
1252.0354 | 379.4589 | 414.6647 | 355.3099
1253.0354 | 380.6865 | 416.0175 | 356.834
1254.0354 | 381.8397 | 417.5903 | 357.8065
1255.0354 | 382.2747 | 418.0901 | 359.0204
1256.0354 | 381.3042 | 420.8906 | 361.1588
1257.0354 | 380.9767 | 421.6848 | 361.9856
1258.0354 | 383.6683 | 422.386 | 363.0814
1259.0354 | 383.682 | 423.5363 | 363.4266
1260.0354 | 383.8816 | 423.9946 | 362.642
1261.0354 | 383.5972 | 423.9676 | 362.2794
1262.0354 | 384.4023 | 425.699 | 363.1752
1263.0354 | 386.2807 | 427.0138 | 364.6509
1264.0354 | 385.4844 | 425.5239 | 366.0099
1265.0354 | 384.0547 | 425.0285 | 365.798
1266.0354 | 385.322 | 425.6381 | 367.1511
1267.0354 | 385.7339 | 428.2863 | 367.9258
1268.0354 | 385.6861 | 429.2337 | 368.8561
1269.0354 | 386.9444 | 429.0742 | 370.5229
1270.0354 | 388.5873 | 427.7617 | 370.6373
1271.0354 | 389.287 | 427.5803 | 370.0736
1272.0354 | 391.1601 | 428.7022 | 369.8835
1273.0354 | 392.1379 | 428.9848 | 370.8614
1274.0354 | 393.4572 | 428.8772 | 371.4267
1275.0354 | 392.5657 | 427.6249 | 371.4711
1276.0354 | 391.8254 | 426.5826 | 370.7534
1277.0354 | 391.1454 | 427.4042 | 370.6703
1278.0354 | 391.3532 | 427.8426 | 370.0886
1279.0354 | 391.8582 | 425.5741 | 368.4448
1280.0354 | 390.5695 | 424.3395 | 368.4057
1281.0354 | 390.9438 | 424.6351 | 367.7254
1282.0354 | 390.0415 | 423.3406 | 366.9099
1283.0354 | 391.0892 | 422.9604 | 365.6844
1284.0354 | 390.0132 | 421.0593 | 363.578
1285.0354 | 392.0183 | 422.4857 | 362.6858
1286.0354 | 392.9322 | 422.3534 | 362.3172
1287.0354 | 393.836 | 421.9303 | 361.1709
1288.0354 | 394.2788 | 422.2763 | 361.9494
1289.0354 | 394.5753 | 420.5948 | 362.4118
1290.0354 | 394.2737 | 418.6202 | 361.0738
1291.0354 | 392.9514 | 417.805 | 359.4053
1292.0354 | 391.848 | 416.189 | 358.5613
1293.0354 | 392.625 | 415.5054 | 358.4426
1294.0354 | 393.8951 | 415.5755 | 359.1127
1295.0354 | 393.6606 | 415.4403 | 359.7763
1296.0354 | 392.7778 | 413.9032 | 358.3474
1297.0354 | 392.8443 | 414.311 | 359.2904
1298.0354 | 393.5974 | 413.3654 | 358.9643
1299.0354 | 394.3282 | 413.4505 | 358.6075
1300.0354 | 395.4127 | 413.005 | 357.3936
1301.0354 | 395.2782 | 413.7613 | 357.9895
1302.0354 | 395.224 | 414.1186 | 358.8712
1303.0354 | 396.2301 | 413.4613 | 358.9553
1304.0354 | 398.1629 | 415.002 | 359.333
1305.0354 | 397.3735 | 414.5554 | 359.5273
1306.0354 | 396.9431 | 416.271 | 360.158
1307.0354 | 395.7353 | 416.8029 | 360.7704
1308.0354 | 394.3866 | 417.6677 | 361.1371
1309.0354 | 395.0729 | 419.0674 | 362.7442
1310.0354 | 395.4584 | 417.6719 | 363.1034
1311.0354 | 395.5909 | 417.717 | 362.9253
1312.0354 | 394.758 | 418.2031 | 362.6181
1313.0354 | 394.6545 | 419.5062 | 363.2107
1314.0354 | 393.8043 | 421.5008 | 363.975
1315.0354 | 392.7887 | 423.2637 | 363.4143
1316.0354 | 392.4952 | 424.2327 | 364.944
1317.0354 | 392.0171 | 424.6381 | 364.8044
1318.0354 | 391.9883 | 425.4954 | 363.5853
1319.0354 | 392.8703 | 423.4652 | 362.2389
1320.0354 | 392.403 | 422.1915 | 361.1492
1321.0354 | 392.457 | 422.2285 | 361.3756
1322.0354 | 393.1369 | 420.699 | 360.896
1323.0354 | 394.2803 | 420.6588 | 361.999
1324.0354 | 394.0281 | 419.7771 | 362.4908
1325.0354 | 394.5094 | 419.5645 | 362.762
1326.0354 | 393.7956 | 419.1578 | 362.2412
1327.0354 | 393.7869 | 418.559 | 362.2818
1328.0354 | 394.2665 | 418.9002 | 363.1827
1329.0354 | 396.0449 | 419.8265 | 363.4382
1330.0354 | 394.9373 | 420.9362 | 363.24
1331.0354 | 395.1096 | 420.8682 | 363.1489
1332.0354 | 396.3539 | 421.1243 | 363.4569
1333.0354 | 395.3641 | 420.7764 | 362.2654
1334.0354 | 395.464 | 420.4405 | 363.438
1335.0354 | 394.3609 | 420.1033 | 364.3064
1336.0354 | 393.2986 | 419.1292 | 364.7518
1337.0354 | 393.2258 | 419.2027 | 365.0682
1338.0354 | 392.7123 | 418.3466 | 363.95
1339.0354 | 393.6766 | 418.6327 | 363.7181
1340.0354 | 393.6491 | 419.3888 | 364.6525
1341.0354 | 393.3966 | 418.6574 | 364.3476
1342.0354 | 393.877 | 418.516 | 364.6026
1343.0354 | 393.5132 | 418.3628 | 363.7385
1344.0354 | 395.1916 | 417.5733 | 364.1917
1345.0354 | 394.3929 | 416.4179 | 363.956
1346.0354 | 394.7265 | 415.8053 | 363.793
1347.0354 | 393.3656 | 415.3791 | 363.2287
1348.0354 | 393.5607 | 416.6856 | 363.1319
1349.0354 | 392.5967 | 417.0434 | 363.0951
1350.0354 | 392.7418 | 417.3336 | 363.4102
1351.0354 | 392.1695 | 416.4886 | 363.3187
1352.0354 | 393.5202 | 419.0929 | 364.5657
1353.0354 | 393.9101 | 419.8206 | 363.9271
1354.0354 | 394.1576 | 420.1123 | 363.0555
1355.0354 | 393.7946 | 420.6725 | 363.1513
1356.0354 | 393.2615 | 420.7118 | 363.0039
1357.0354 | 392.7461 | 420.1601 | 364.1121
1358.0354 | 392.1401 | 418.9957 | 364.6678
1359.0354 | 391.4807 | 417.6954 | 364.2396
1360.0354 | 391.9044 | 416.9893 | 363.947
1361.0354 | 391.3741 | 416.2799 | 364.1518
1362.0354 | 390.7813 | 415.8458 | 364.1394
1363.0354 | 390.3178 | 415.0618 | 363.387
1364.0354 | 390.5394 | 415.5078 | 363.7752
1365.0354 | 390.2023 | 414.9754 | 364.2366
1366.0354 | 391.67 | 415.1407 | 365.3634
1367.0354 | 390.7082 | 415.612 | 365.0048
1368.0354 | 391.1697 | 415.9145 | 365.6916
1369.0354 | 392.12 | 415.5291 | 366.4019
1370.0354 | 392.3145 | 416.3227 | 366.6891
1371.0354 | 391.301 | 416.4107 | 366.7023
1372.0354 | 391.8093 | 416.1205 | 366.9616
1373.0354 | 392.171 | 416.3172 | 367.6489
1374.0354 | 391.7346 | 415.5495 | 366.6242
1375.0354 | 391.9899 | 414.0981 | 365.2231
1376.0354 | 392.4111 | 414.8363 | 365.4106
1377.0354 | 393.1619 | 415.8076 | 366.9201
1378.0354 | 393.2357 | 418.4486 | 367.1813
1379.0354 | 393.3643 | 418.0819 | 368.237
1380.0354 | 392.8043 | 416.2934 | 365.4569
1381.0354 | 392.5895 | 415.5866 | 366.0649
1382.0354 | 392.5075 | 415.8487 | 366.51
1383.0354 | 392.0005 | 416.443 | 368.0993
1384.0354 | 391.3412 | 418.0509 | 368.3559
1385.0354 | 391.1673 | 419.2638 | 367.6269
1386.0354 | 391.2113 | 419.3591 | 366.3804
1387.0354 | 391.3456 | 419.1615 | 367.1481
1388.0354 | 390.483 | 418.2276 | 367.3649
1389.0354 | 390.248 | 417.3095 | 366.5244
1390.0354 | 391.2355 | 416.549 | 366.5871
1391.0354 | 390.5252 | 415.8871 | 365.0696
1392.0354 | 390.6907 | 416.2285 | 363.9496
1393.0354 | 391.35 | 416.1496 | 364.104
1394.0354 | 391.738 | 416.4165 | 364.902
1395.0354 | 391.5913 | 416.0647 | 365.4109
1396.0354 | 391.6473 | 416.2988 | 366.4007
1397.0354 | 390.1614 | 416.8722 | 367.2128
1398.0354 | 388.6577 | 416.295 | 367.779
1399.0354 | 387.7451 | 414.8083 | 367.7132
1400.0354 | 387.3256 | 414.479 | 367.232
1401.0354 | 387.0018 | 413.5986 | 367.2067
1402.0354 | 387.2782 | 412.936 | 367.0527
1403.0354 | 386.1438 | 411.472 | 366.367
1404.0354 | 385.6135 | 410.9445 | 366.2262
1405.0354 | 385.6008 | 410.5423 | 365.4494
1406.0354 | 386.4133 | 410.8242 | 366.141
1407.0354 | 385.3851 | 410.949 | 366.4222
1408.0354 | 384.9885 | 412.3873 | 366.2701
1409.0354 | 384.1801 | 412.335 | 365.6538
1410.0354 | 383.4633 | 411.2173 | 364.7642
1411.0354 | 383.2144 | 409.8476 | 362.8574
1412.0354 | 382.6696 | 409.1644 | 362.5536
1413.0354 | 382.8294 | 408.9919 | 362.8779
1414.0354 | 381.8998 | 409.2437 | 363.1435
1415.0354 | 381.3135 | 409.4543 | 363.1435
1416.0354 | 381.5347 | 410.9737 | 363.034
1417.0354 | 380.6361 | 412.1206 | 363.5099
1418.0354 | 380.3514 | 412.6056 | 363.625
1419.0354 | 379.8483 | 412.4489 | 363.2803
1420.0354 | 379.1497 | 411.3672 | 361.833
1421.0354 | 379.5102 | 411.7688 | 360.5931
1422.0354 | 380.2829 | 412.7554 | 360.5946
1423.0354 | 379.7378 | 412.0197 | 359.8212
1424.0354 | 379.7451 | 411.4874 | 359.4372
1425.0354 | 378.7975 | 411.2079 | 359.5237
1426.0354 | 378.1467 | 411.4203 | 359.5158
1427.0354 | 378.4686 | 410.6006 | 359.5852
1428.0354 | 377.9645 | 409.8686 | 359.8388
1429.0354 | 377.824 | 408.5225 | 358.9774
1430.0354 | 378.99 | 408.2801 | 359.2108
1431.0354 | 378.8166 | 406.9619 | 359.6911
1432.0354 | 378.9461 | 405.8854 | 359.2649
1433.0354 | 377.7954 | 404.5927 | 357.536
1434.0354 | 377.0885 | 403.3599 | 356.7864
1435.0354 | 376.4949 | 401.8736 | 355.8851
1436.0354 | 375.6462 | 400.7207 | 354.552
1437.0354 | 376.9661 | 399.383 | 353.8142
1438.0354 | 377.4907 | 397.9377 | 351.9275
1439.0354 | 376.9277 | 397.8716 | 350.7629
1440.0354 | 377.4555 | 397.8527 | 350.1057
1441.0354 | 379.0386 | 398.4107 | 351.1237
1442.0354 | 379.393 | 398.9613 | 351.4993
1443.0354 | 380.5794 | 399.0658 | 352.8086
1444.0354 | 379.6288 | 398.7114 | 353.013
1445.0354 | 378.9533 | 398.1141 | 352.9614
1446.0354 | 379.0439 | 397.5474 | 352.3133
1447.0354 | 379.4942 | 397.4276 | 352.5914
1448.0354 | 380.4146 | 397.6504 | 351.9202
1449.0354 | 380.6329 | 395.9451 | 350.7422
1450.0354 | 381.1928 | 395.0476 | 349.7379
1451.0354 | 380.8492 | 395.09 | 349.0464
1452.0354 | 380.8045 | 394.5004 | 348.2147
1453.0354 | 382.0675 | 394.7287 | 347.9873
1454.0354 | 383.3113 | 395.1538 | 348.7976
1455.0354 | 382.6692 | 396.2541 | 349.954
1456.0354 | 381.6285 | 396.3292 | 349.1959
1457.0354 | 381.0261 | 395.7332 | 348.6097
1458.0354 | 380.977 | 395.0545 | 348.2335
1459.0354 | 380.6223 | 396.0019 | 349.2238
1460.0354 | 381.9458 | 398.065 | 351.3993
1461.0354 | 381.2883 | 399.8945 | 354.0407
1462.0354 | 381.9078 | 401.1016 | 355.9064
1463.0354 | 381.8013 | 401.6122 | 356.7573
1464.0354 | 382.2416 | 402.7051 | 357.3445
1465.0354 | 383.2523 | 403.0568 | 358.5863
1466.0354 | 382.9789 | 403.2304 | 359.1264
1467.0354 | 383.1849 | 403.3476 | 358.9285
1468.0354 | 383.1561 | 403.6659 | 358.7266
1469.0354 | 383.1837 | 403.7535 | 358.6372
1470.0354 | 383.6737 | 404.2368 | 359.5675
1471.0354 | 383.8069 | 403.5465 | 358.8366
1472.0354 | 383.1575 | 403.6892 | 358.8667
1473.0354 | 383.9412 | 404.5851 | 359.8738
1474.0354 | 385.5246 | 405.8107 | 360.548
1475.0354 | 384.7284 | 407.0538 | 361.2395
1476.0354 | 385.4403 | 407.6075 | 361.2232
1477.0354 | 387.6443 | 407.7308 | 361.5144
1478.0354 | 387.7891 | 408.1371 | 360.9596
1479.0354 | 388.2966 | 408.7733 | 361.532
1480.0354 | 387.3238 | 410.3246 | 361.5973
1481.0354 | 387.0104 | 410.3821 | 360.8236
1482.0354 | 387.0919 | 410.1906 | 360.0279
1483.0354 | 387.2733 | 409.3322 | 359.2375
1484.0354 | 386.7966 | 408.9779 | 359.8723
1485.0354 | 386.574 | 408.4469 | 360.79
1486.0354 | 385.6773 | 408.2943 | 361.6267
1487.0354 | 384.6686 | 408.0065 | 361.1534
1488.0354 | 384.75 | 408.3149 | 360.1039
1489.0354 | 384.787 | 407.3599 | 359.326
1490.0354 | 384.8647 | 407.1672 | 359.7241
1491.0354 | 384.8039 | 407.5881 | 359.7809
1492.0354 | 384.2865 | 408.2697 | 359.8865
1493.0354 | 384.5132 | 408.1375 | 359.1245
1494.0354 | 385.887 | 407.2901 | 358.0178
1495.0354 | 386.2255 | 406.8404 | 357.9099
1496.0354 | 385.9158 | 405.5287 | 357.816
1497.0354 | 385.6385 | 404.0428 | 357.1739
1498.0354 | 385.3703 | 403.3699 | 356.6517
1499.0354 | 385.4826 | 404.3076 | 357.3816
1500.0354 | 385.1974 | 403.2022 | 357.8073
1501.0354 | 384.6402 | 403.014 | 356.411
1502.0354 | 384.6699 | 402.8769 | 356.202
1503.0354 | 384.3888 | 402.4085 | 356.0664
1504.0354 | 383.869 | 402.3121 | 356.2541
1505.0354 | 383.9888 | 402.1182 | 356.3105
1506.0354 | 383.8714 | 402.5728 | 356.3166
1507.0354 | 383.6776 | 402.827 | 356.7933
1508.0354 | 383.5945 | 402.4478 | 356.8963
1509.0354 | 383.2703 | 401.6399 | 356.5476
1510.0354 | 382.9912 | 402.3928 | 357.1317
1511.0354 | 382.3812 | 402.1341 | 357.3995
1512.0354 | 382.1245 | 402.631 | 357.963
1513.0354 | 381.4936 | 401.7916 | 357.0635
1514.0354 | 381.2522 | 401.7416 | 357.4616
1515.0354 | 381.2644 | 401.2857 | 357.364
1516.0354 | 381.1116 | 402.0517 | 356.4491
1517.0354 | 381.803 | 402.5409 | 356.732
1518.0354 | 381.3951 | 400.7985 | 355.6139
1519.0354 | 380.7986 | 398.0863 | 353.5679
1520.0354 | 380.5573 | 396.2442 | 352.6085
1521.0354 | 380.8131 | 396.168 | 352.3384
1522.0354 | 380.8603 | 396.586 | 353.2906
1523.0354 | 380.1256 | 396.3514 | 353.7096
1524.0354 | 380.3779 | 396.4274 | 353.8216
1525.0354 | 380.8104 | 396.3012 | 354.3645
1526.0354 | 381.5797 | 396.1711 | 354.3149
1527.0354 | 381.0792 | 396.1589 | 353.5583
1528.0354 | 380.8299 | 396.7465 | 353.9676
1529.0354 | 380.7746 | 396.87 | 353.2227
1530.0354 | 381.3608 | 398.0975 | 353.0845
1531.0354 | 381.3799 | 398.3097 | 353.5019
1532.0354 | 381.088 | 397.1498 | 353.5657
1533.0354 | 380.8283 | 396.9127 | 353.4084
1534.0354 | 380.7629 | 397.4673 | 352.8978
1535.0354 | 380.6427 | 396.741 | 352.6109
1536.0354 | 380.2315 | 397.1312 | 352.8505
1537.0354 | 380.1278 | 396.5828 | 353.3482
1538.0354 | 379.6287 | 396.2473 | 353.4539
1539.0354 | 379.2767 | 397.1654 | 354.6253
1540.0354 | 379.0866 | 396.7663 | 354.6194
1541.0354 | 379.0015 | 396.5489 | 355.7222
1542.0354 | 378.5009 | 396.9447 | 355.866
1543.0354 | 378.6944 | 397.0579 | 356.1013
1544.0354 | 378.799 | 398.145 | 355.4896
1545.0354 | 378.2977 | 398.9641 | 355.6727
1546.0354 | 378.3871 | 398.9733 | 356.2519
1547.0354 | 378.0822 | 398.0985 | 355.5891
1548.0354 | 378.9173 | 398.942 | 356.7022
1549.0354 | 379.1187 | 398.4484 | 356.4304
1550.0354 | 379.8687 | 398.0505 | 355.6343
1551.0354 | 380.8108 | 398.0403 | 356.0557
1552.0354 | 380.8947 | 399.014 | 357.4389
1553.0354 | 380.6548 | 398.8368 | 358.0714
1554.0354 | 380.1096 | 398.3717 | 357.3688
1555.0354 | 379.7196 | 397.1752 | 356.2752
1556.0354 | 379.7571 | 396.9264 | 356.1391
1557.0354 | 378.9629 | 397.8554 | 356.4888
1558.0354 | 378.7168 | 398.9387 | 356.7739
1559.0354 | 379.0013 | 400.7895 | 356.2198
1560.0354 | 378.9647 | 402.899 | 356.6966
1561.0354 | 378.9691 | 403.617 | 357.4154
1562.0354 | 378.6242 | 403.3096 | 357.6394
1563.0354 | 378.3253 | 402.7688 | 357.3882
1564.0354 | 377.7296 | 402.2358 | 356.7885
1565.0354 | 377.4672 | 401.8253 | 357.2618
1566.0354 | 377.2628 | 401.2114 | 357.7517
1567.0354 | 377.3435 | 402.656 | 358.3562
1568.0354 | 378.7556 | 403.0123 | 358.3567
1569.0354 | 381.1233 | 403.608 | 358.2864
1570.0354 | 381.6771 | 403.5542 | 357.3378
1571.0354 | 382.4916 | 404.0994 | 356.809
1572.0354 | 383.0843 | 404.2356 | 356.2335
1573.0354 | 383.1246 | 403.6965 | 355.6776
1574.0354 | 383.5554 | 402.999 | 355.8553
1575.0354 | 384.5483 | 403.4462 | 355.6111
1576.0354 | 383.7846 | 403.0388 | 355.3623
1577.0354 | 382.9429 | 403.805 | 355.5314
1578.0354 | 383.4251 | 403.1331 | 354.6661
1579.0354 | 383.0462 | 403.1117 | 354.6287
1580.0354 | 381.8732 | 403.3634 | 355.2749
1581.0354 | 380.8045 | 403.7677 | 355.2819
1582.0354 | 380.5946 | 403.5081 | 356.4544
1583.0354 | 381.0531 | 403.1316 | 356.1852
1584.0354 | 381.0955 | 403.206 | 357.0449
1585.0354 | 380.7295 | 403.9669 | 356.7723
1586.0354 | 380.6759 | 405.4539 | 356.4937
1587.0354 | 381.3573 | 406.9305 | 356.4879
1588.0354 | 382.3568 | 407.1515 | 355.7862
1589.0354 | 383.7541 | 407.7541 | 356.3039
1590.0354 | 383.7084 | 407.8674 | 357.2939
1591.0354 | 383.7807 | 408.5341 | 358.023
1592.0354 | 383.6296 | 408.6663 | 358.1552
1593.0354 | 384.6325 | 409.0238 | 357.816
1594.0354 | 383.9168 | 409.3775 | 357.5971
1595.0354 | 383.4822 | 408.6338 | 357.4104
1596.0354 | 384.3193 | 408.9615 | 357.6614
1597.0354 | 384.5259 | 409.2342 | 358.9248
1598.0354 | 384.716 | 409.6714 | 360.2728
1599.0354 | 385.1589 | 410.2904 | 361.5
1600.0354 | 385.9315 | 412.4974 | 362.3818
1601.0354 | 386.419 | 412.7104 | 363.1576
1602.0354 | 385.7032 | 411.9477 | 362.3413
1603.0354 | 385.4318 | 412.5142 | 362.9216
1604.0354 | 385.3218 | 413.4084 | 364.1553
1605.0354 | 385.8835 | 414.1571 | 365.1189
1606.0354 | 385.705 | 414.2966 | 365.4317
1607.0354 | 385.4273 | 415.0557 | 365.5896
1608.0354 | 385.4684 | 415.884 | 365.2788
1609.0354 | 385.4292 | 416.6004 | 363.9272
1610.0354 | 386.3037 | 416.9766 | 363.7895
1611.0354 | 386.9314 | 417.2787 | 364.1291
1612.0354 | 387.7514 | 417.5769 | 365.524
1613.0354 | 388.1394 | 417.9205 | 366.6003
1614.0354 | 388.0235 | 419.0549 | 367.2998
1615.0354 | 387.8993 | 419.4565 | 367.1578
1616.0354 | 388.0267 | 418.828 | 366.912
1617.0354 | 389.0152 | 417.9842 | 366.985
1618.0354 | 389.0242 | 418.3354 | 366.6963
1619.0354 | 389.5606 | 417.8193 | 366.5511
1620.0354 | 389.1179 | 418.7426 | 367.2742
1621.0354 | 388.5163 | 420.9391 | 367.076
1622.0354 | 388.4346 | 422.1015 | 368.0195
1623.0354 | 388.2799 | 421.1771 | 367.9856
1624.0354 | 388.0701 | 421.2861 | 367.6109
1625.0354 | 387.7426 | 422.0259 | 368.0223
1626.0354 | 386.3132 | 422.1606 | 367.4256
1627.0354 | 385.6869 | 422.521 | 367.7613
1628.0354 | 385.8904 | 423.4283 | 368.1802
1629.0354 | 385.7151 | 424.2629 | 368.2216
1630.0354 | 386.5168 | 424.2197 | 368.6151
1631.0354 | 386.6528 | 424.6946 | 368.7969
1632.0354 | 387.5574 | 423.9582 | 367.9981
1633.0354 | 387.7798 | 423.402 | 368.5179
1634.0354 | 387.5023 | 423.7322 | 368.9132
1635.0354 | 387.5663 | 424.63 | 368.569
1636.0354 | 388.5427 | 423.5046 | 368.5741
1637.0354 | 388.7899 | 423.2112 | 368.1178
1638.0354 | 388.4667 | 422.1947 | 367.8551
1639.0354 | 387.6027 | 425.0933 | 369.1103
1640.0354 | 387.0407 | 426.5719 | 370.3435
1641.0354 | 387.2463 | 426.9427 | 371.7105
1642.0354 | 387.046 | 426.9385 | 371.5085
1643.0354 | 386.7706 | 427.7613 | 370.7697
1644.0354 | 387.3245 | 428.4662 | 369.5482
1645.0354 | 387.6078 | 428.3918 | 369.9556
1646.0354 | 387.6115 | 429.9145 | 370.0905
1647.0354 | 387.3744 | 428.9388 | 369.8999
1648.0354 | 387.4017 | 427.9405 | 369.3065
1649.0354 | 387.0576 | 428.8456 | 369.2131
1650.0354 | 386.9035 | 429.6422 | 369.1945
1651.0354 | 386.3322 | 430.1843 | 369.1401
1652.0354 | 385.6514 | 429.9039 | 370.0421
1653.0354 | 385.1017 | 429.6092 | 369.9119
1654.0354 | 384.2544 | 428.3557 | 370.2793
1655.0354 | 384.3647 | 428.8654 | 372.1107
1656.0354 | 383.9887 | 427.9249 | 371.8655
1657.0354 | 383.5884 | 426.8786 | 371.6701
1658.0354 | 383.2895 | 426.1503 | 371.3655
1659.0354 | 383.8957 | 426.0557 | 371.7358
1660.0354 | 384.4334 | 426.0577 | 371.6438
1661.0354 | 385.0967 | 426.2153 | 371.0572
1662.0354 | 384.5322 | 425.9888 | 371.5769
1663.0354 | 384.0673 | 426.073 | 370.9479
1664.0354 | 383.7307 | 425.167 | 370.2724
1665.0354 | 383.8373 | 423.5214 | 369.4658
1666.0354 | 384.1362 | 422.0472 | 368.6701
1667.0354 | 384.6387 | 420.1468 | 367.1561
1668.0354 | 385.3325 | 419.2832 | 366.0854
1669.0354 | 386.055 | 420.3759 | 367.4586
1670.0354 | 386.9833 | 420.1327 | 368.0001
1671.0354 | 386.3376 | 419.9174 | 367.7727
1672.0354 | 387.0971 | 420.4546 | 367.6652
1673.0354 | 387.1781 | 420.0842 | 368.393
1674.0354 | 387.2782 | 420.235 | 368.616
1675.0354 | 387.0979 | 419.435 | 369.3968
1676.0354 | 387.2491 | 418.884 | 369.5452
1677.0354 | 386.9163 | 417.6247 | 369.4335
1678.0354 | 387.5439 | 418.8611 | 370.2047
1679.0354 | 387.1339 | 418.9007 | 369.3112
1680.0354 | 387.8248 | 419.4495 | 370.1489
1681.0354 | 387.8583 | 419.641 | 369.4502
1682.0354 | 387.7173 | 421.1641 | 369.0764
1683.0354 | 387.5505 | 420.4439 | 368.1799
1684.0354 | 387.9409 | 421.6268 | 368.7291
1685.0354 | 387.9622 | 422.5936 | 368.6242
1686.0354 | 387.9678 | 420.8725 | 367.9576
1687.0354 | 388.0723 | 419.8936 | 367.3761
1688.0354 | 387.8839 | 418.7764 | 367.4018
1689.0354 | 387.8089 | 417.5219 | 367.3781
1690.0354 | 388.1692 | 417.4703 | 368.1137
1691.0354 | 387.5462 | 415.8507 | 368.0598
1692.0354 | 386.9192 | 415.0784 | 367.8873
1693.0354 | 387.1446 | 415.9192 | 366.4717
1694.0354 | 386.5031 | 414.053 | 365.2855
1695.0354 | 386.6846 | 414.0277 | 365.7136
1696.0354 | 386.9116 | 413.3941 | 365.2976
1697.0354 | 387.2311 | 412.5932 | 365.2505
1698.0354 | 387.712 | 412.1858 | 365.2539
1699.0354 | 387.2481 | 412.5299 | 365.7756
1700.0354 | 386.9288 | 412.4343 | 365.6197
1701.0354 | 386.8606 | 412.1553 | 365.1452
1702.0354 | 386.1828 | 411.6968 | 365.2158
1703.0354 | 385.8102 | 412.1653 | 365.3843
1704.0354 | 386.0799 | 413.0097 | 366.1951
1705.0354 | 386.4149 | 412.2473 | 366.3959
1706.0354 | 386.4026 | 413.3268 | 366.9488
1707.0354 | 386.288 | 413.043 | 366.981
1708.0354 | 386.2137 | 413.2231 | 367.5102
1709.0354 | 385.9521 | 413.5591 | 366.9195
1710.0354 | 385.596 | 412.8452 | 367.0607
1711.0354 | 385.6159 | 412.1473 | 367.3263
1712.0354 | 385.9394 | 413.5539 | 368.2765
1713.0354 | 385.7079 | 413.3489 | 368.3141
1714.0354 | 385.4931 | 412.2469 | 367.4203
1715.0354 | 386.425 | 412.0993 | 367.508
1716.0354 | 387.1573 | 412.0361 | 366.9349
1717.0354 | 387.3358 | 412.1068 | 366.3908
1718.0354 | 388.4465 | 413.4037 | 367.5326
1719.0354 | 388.9782 | 413.3011 | 368.3263
1720.0354 | 389.0527 | 412.6678 | 367.5074
1721.0354 | 389.2181 | 413.3365 | 367.4267
1722.0354 | 389.2326 | 414.9661 | 368.3547
1723.0354 | 389.6584 | 416.3326 | 368.9783
1724.0354 | 390.0116 | 416.7092 | 368.2837
1725.0354 | 390.0275 | 417.9535 | 368.4236
1726.0354 | 390.3521 | 417.5048 | 368.8507
1727.0354 | 390.2566 | 417.4011 | 368.7924
1728.0354 | 390.0997 | 417.5045 | 369.1058
1729.0354 | 390.285 | 418.5451 | 369.0341
1730.0354 | 390.7272 | 418.9763 | 369.552
1731.0354 | 391.672 | 419.3357 | 370.3044
1732.0354 | 392.1091 | 419.4098 | 370.6763
1733.0354 | 392.3669 | 419.8399 | 370.8691
1734.0354 | 392.4145 | 420.7419 | 371.3928
1735.0354 | 393.0631 | 421.4499 | 371.6741
1736.0354 | 394.0545 | 423.6071 | 372.5882
1737.0354 | 394.2604 | 425.9275 | 373.8809
1738.0354 | 394.3865 | 427.5152 | 374.8807
1739.0354 | 394.5494 | 430.9946 | 376.6123
1740.0354 | 394.7947 | 434.5619 | 378.2684
1741.0354 | 395.0213 | 434.6233 | 378.5758
1742.0354 | 395.5751 | 435.1325 | 378.0227
1743.0354 | 396.1196 | 434.6072 | 377.6058
1744.0354 | 396.2189 | 433.774 | 377.4802
1745.0354 | 396.6824 | 434.6393 | 377.7195
1746.0354 | 397.9041 | 435.4449 | 377.5935
1747.0354 | 398.0266 | 436.5056 | 377.4503
1748.0354 | 398.5306 | 436.1313 | 377.5388
1749.0354 | 399.0689 | 436.1038 | 377.9449
1750.0354 | 399.8567 | 434.9028 | 377.6939
1751.0354 | 399.9803 | 434.6396 | 377.4351
1752.0354 | 400.0338 | 432.9853 | 377.7871
1753.0354 | 399.8942 | 431.0523 | 377.5103
1754.0354 | 400.2984 | 430.638 | 376.9111
1755.0354 | 400.469 | 430.8461 | 375.798
1756.0354 | 400.6987 | 430.1781 | 375.1976
1757.0354 | 400.1415 | 427.5925 | 373.8424
1758.0354 | 399.9836 | 427.6154 | 374.5764
1759.0354 | 399.8478 | 428.8986 | 374.4974
1760.0354 | 400.1502 | 432.1617 | 376.0541
1761.0354 | 400.1948 | 432.8532 | 376.1059
1762.0354 | 399.9092 | 432.0238 | 376.3131
1763.0354 | 400.3885 | 433.0817 | 376.9422
1764.0354 | 401.3582 | 434.2026 | 377.0743
1765.0354 | 402.1386 | 434.0966 | 377.0348
1766.0354 | 402.6634 | 433.1662 | 376.3357
1767.0354 | 403.4629 | 433.9278 | 376.5577
1768.0354 | 403.8244 | 433.023 | 376.4798
1769.0354 | 403.0703 | 430.3364 | 375.1154
1770.0354 | 402.6819 | 430.1923 | 375.0439
1771.0354 | 403.0299 | 431.5018 | 375.6034
1772.0354 | 403.8622 | 431.9407 | 375.5317
1773.0354 | 403.3947 | 431.4568 | 375.4656
1774.0354 | 402.8685 | 431.838 | 376.5365
1775.0354 | 402.5059 | 430.5226 | 376.6274
1776.0354 | 402.7354 | 430.9604 | 376.9871
1777.0354 | 403.4738 | 433.7046 | 377.4032
1778.0354 | 404.1622 | 438.1999 | 379.4326
1779.0354 | 404.9958 | 438.9913 | 380.5664
1780.0354 | 405.3301 | 439.6336 | 381.9206
1781.0354 | 405.1007 | 439.426 | 383.1338
1782.0354 | 404.4132 | 438.8124 | 383.7925
1783.0354 | 404.6772 | 440.0794 | 384.7218
1784.0354 | 405.1658 | 440.1773 | 385.4315
1785.0354 | 405.4772 | 439.7372 | 385.2881
1786.0354 | 405.8242 | 441.0146 | 386.0052
1787.0354 | 406.5346 | 442.2098 | 386.192
1788.0354 | 407.7513 | 450.2046 | 389.0177
1789.0354 | 409.0286 | 454.7626 | 390.5601
1790.0354 | 410.1369 | 458.0665 | 390.0609
1791.0354 | 410.8195 | 459.6484 | 390.0892
1792.0354 | 411.6609 | 459.9942 | 389.8405
1793.0354 | 412.5927 | 460.1856 | 390.8
1794.0354 | 413.2208 | 457.9058 | 390.6125
1795.0354 | 413.7324 | 456.5068 | 390.1739
1796.0354 | 413.7818 | 454.4706 | 390.0011
1797.0354 | 413.696 | 452.6305 | 389.4317
1798.0354 | 413.3865 | 452.0828 | 389.6559
1799.0354 | 413.2814 | 451.9828 | 390.1547
1800.0354 | 412.7229 | 450.7219 | 389.9337
1801.0354 | 412.5572 | 449.2214 | 389.9115
1802.0354 | 412.6871 | 448.3161 | 390.0247
1803.0354 | 412.4063 | 446.9391 | 388.665
1804.0354 | 412.3815 | 445.9721 | 388.1331
1805.0354 | 412.1979 | 445.6 | 388.9592
1806.0354 | 412.4744 | 446.6796 | 390.3258
1807.0354 | 412.2755 | 445.9777 | 390.0616
1808.0354 | 412.0465 | 445.1469 | 389.6969
1809.0354 | 411.3563 | 444.6738 | 389.7859
1810.0354 | 410.6279 | 444.4947 | 390.9198
1811.0354 | 410.156 | 444.9596 | 392.5053
1812.0354 | 409.6839 | 444.6542 | 391.9259
1813.0354 | 409.5646 | 443.4163 | 391.3146
1814.0354 | 409.2987 | 442.943 | 390.6125
1815.0354 | 409.368 | 442.4451 | 389.5684
1816.0354 | 410.2945 | 445.538 | 390.3922
1817.0354 | 411.245 | 448.2041 | 390.982
1818.0354 | 412.0402 | 452.1489 | 392.3517
1819.0354 | 413.1654 | 456.7286 | 392.8451
1820.0354 | 414.66 | 458.7535 | 392.8579
1821.0354 | 416.2138 | 458.9848 | 393.0931
1822.0354 | 417.3009 | 458.0741 | 392.1592
1823.0354 | 418.827 | 457.8604 | 392.4614
1824.0354 | 419.2568 | 457.0267 | 391.9063
1825.0354 | 419.7548 | 457.9447 | 392.0979
1826.0354 | 419.3253 | 456.7704 | 391.9959
1827.0354 | 420.467 | 459.6104 | 392.8788
1828.0354 | 420.8143 | 460.8485 | 395.0869
1829.0354 | 420.913 | 461.391 | 396.059
1830.0354 | 421.1592 | 460.8591 | 396.8452
1831.0354 | 420.7669 | 460.731 | 397.1683
1832.0354 | 420.9805 | 460.5308 | 397.7321
1833.0354 | 420.6751 | 459.654 | 397.6991
1834.0354 | 420.621 | 459.0539 | 397.8358
1835.0354 | 420.0914 | 458.4241 | 398.2654
1836.0354 | 419.7385 | 456.8419 | 397.7103
1837.0354 | 420.0682 | 455.9011 | 397.007
1838.0354 | 419.9235 | 456.0704 | 397.6563
1839.0354 | 420.2303 | 456.1062 | 398.1239
1840.0354 | 420.6088 | 457.3253 | 397.4628
1841.0354 | 420.9082 | 458.7593 | 397.9287
1842.0354 | 420.9331 | 457.8659 | 396.759
1843.0354 | 420.7838 | 456.4703 | 395.6407
1844.0354 | 420.3046 | 457.493 | 395.5957
1845.0354 | 420.1709 | 456.7476 | 395.4265
1846.0354 | 419.5383 | 454.671 | 393.8302
1847.0354 | 419.2271 | 452.7193 | 392.5538
1848.0354 | 419.5463 | 452.3937 | 392.1729
1849.0354 | 420.7189 | 451.6774 | 392.1793
1850.0354 | 420.8142 | 451.1647 | 391.5995
1851.0354 | 420.7203 | 452.1271 | 390.8904
1852.0354 | 420.6329 | 452.3225 | 391.2709
1853.0354 | 419.8465 | 451.967 | 391.4644
1854.0354 | 419.5095 | 451.6073 | 390.4452
1855.0354 | 418.8463 | 450.8896 | 389.2738
1856.0354 | 418.5648 | 449.5152 | 388.464
1857.0354 | 418.8379 | 450.4686 | 388.4764
1858.0354 | 420.9705 | 452.1899 | 388.3182
1859.0354 | 422.5449 | 452.0889 | 387.6018
1860.0354 | 422.6003 | 450.5382 | 387.0244
1861.0354 | 423.0378 | 449.3554 | 386.1538
1862.0198 | 423.7583 | 447.9606 | 385.6002
1863.0354 | 424.327 | 445.9122 | 384.5354
1864.0354 | 424.1199 | 444.7481 | 383.8605
1865.0354 | 424.0118 | 443.7191 | 383.7957
1866.0354 | 424.0738 | 442.9248 | 383.702
1867.0354 | 425.1227 | 443.2341 | 383.8117
1868.0354 | 425.3173 | 441.8835 | 383.4841
1869.0354 | 425.3768 | 440.5762 | 382.3302
1870.0354 | 424.8965 | 438.4519 | 381.5173
1871.0354 | 424.374 | 437.612 | 381.1597
1872.0354 | 423.4554 | 436.9132 | 380.927
1873.0354 | 422.8022 | 436.7452 | 381.2274
1874.0354 | 422.4234 | 436.0201 | 380.6747
1875.0354 | 421.7502 | 434.1831 | 379.5565
1876.0354 | 421.0975 | 432.5569 | 378.7685
1877.0354 | 421.0151 | 432.3704 | 378.3559
1878.0354 | 420.7176 | 432.9875 | 378.0248
1879.0354 | 420.8242 | 433.4386 | 378.2984
1880.0354 | 420.6417 | 432.4595 | 377.8527
1881.0354 | 421.1546 | 432.0603 | 377.4456
1882.0354 | 421.5325 | 431.7712 | 377.2219
1883.0354 | 421.1263 | 431.7139 | 377.5159
1884.0354 | 420.945 | 432.0262 | 378.5146
1885.0354 | 420.8189 | 433.0311 | 378.5607
1886.0354 | 420.033 | 434.1464 | 379.7341
1887.0354 | 419.7917 | 434.4357 | 380.9633
1888.0354 | 419.6356 | 434.5465 | 381.6106
1889.0354 | 420.3474 | 435.4537 | 382.9801
1890.0354 | 420.3408 | 437.194 | 383.4831
1891.0354 | 420.2954 | 438.6255 | 384.5499
1892.0354 | 419.8047 | 438.3102 | 385.4495
1893.0354 | 419.1651 | 439.0095 | 385.3567
1894.0354 | 419.6963 | 441.6258 | 386.6601
1895.0354 | 420.2085 | 445.4193 | 388.1433
1896.0354 | 420.7946 | 445.8038 | 389.2138
1897.0354 | 420.9308 | 445.1739 | 389.113
1898.0354 | 421.0793 | 448.1801 | 390.3678
1899.0354 | 421.078 | 450.989 | 391.5766
1900.0354 | 421.3279 | 449.8783 | 391.4454
1901.0354 | 422.1398 | 449.2647 | 391.3274
1902.0354 | 422.4218 | 449.0396 | 391.0625
1903.0354 | 422.8123 | 448.985 | 392.0692
1904.0354 | 423.1268 | 449.0862 | 393.0203
1905.0354 | 423.1911 | 449.738 | 394.1602
1906.0354 | 423.0563 | 450.2699 | 395.5287
1907.0354 | 423.0085 | 451.5938 | 397.023
1908.0354 | 423.0124 | 455.8809 | 397.3616
1909.0354 | 423.279 | 455.021 | 397.3918
1910.0354 | 423.5422 | 453.7383 | 396.7484
1911.0354 | 423.4017 | 452.5295 | 395.2474
1912.0354 | 423.782 | 452.067 | 394.7349
1913.0354 | 423.8744 | 451.0134 | 394.138
1914.0354 | 423.6749 | 450.3066 | 393.5777
1915.0354 | 423.4815 | 450.1702 | 394.0623
1916.0354 | 423.419 | 450.0683 | 394.0271
1917.0354 | 423.9882 | 449.7175 | 394.5762
1918.0354 | 423.7679 | 448.5294 | 393.927
1919.0354 | 423.3354 | 447.769 | 393.3098
1920.0354 | 423.8003 | 448.7624 | 394.1993
1921.0354 | 423.3769 | 449.626 | 394.6854
1922.0354 | 424.2991 | 450.4169 | 396.7193
1923.0354 | 424.5237 | 449.5945 | 397.0595
1924.0354 | 424.5014 | 450.1256 | 397.3975
1925.0354 | 425.5488 | 448.8555 | 397.8027
1926.0354 | 425.2068 | 447.3788 | 396.3632
1927.0354 | 425.8317 | 448.4225 | 395.4287
1928.0354 | 425.4169 | 448.591 | 395.0141
1929.0354 | 425.2855 | 448.5764 | 394.7872
1930.0354 | 424.7401 | 448.7921 | 394.5849
1931.0354 | 424.1136 | 447.8362 | 394.5491
1932.0354 | 423.6169 | 447.4001 | 394.5201
1933.0354 | 423.7991 | 446.4825 | 394.9798
1934.0354 | 423.2199 | 444.9299 | 393.6205
1935.0354 | 423.1966 | 444.812 | 393.9816
1936.0354 | 423.7689 | 445.4523 | 394.3578
1937.0354 | 423.8003 | 445.0837 | 394.6189
1938.0354 | 423.4837 | 444.1353 | 394.4953
1939.0354 | 424.0477 | 443.8897 | 394.638
1940.0354 | 423.5137 | 442.719 | 394.1344
1941.0354 | 422.5865 | 442.5625 | 393.8349
1942.0354 | 422.3181 | 441.7547 | 394.0383
1943.0354 | 422.379 | 440.9163 | 394.4792
1944.0354 | 421.8648 | 441.4986 | 394.9095
1945.0354 | 421.8925 | 441.8227 | 395.8777
1946.0354 | 421.1906 | 441.134 | 395.9525
1947.0354 | 420.2638 | 441.116 | 395.9029
1948.0354 | 420.3373 | 442.5568 | 395.8019
1949.0354 | 420.5603 | 441.7917 | 394.7172
1950.0354 | 422.5785 | 442.4293 | 393.9498
1951.0354 | 422.5181 | 442.7176 | 393.5536
1952.0354 | 423.2589 | 442.591 | 392.6398
1953.0354 | 423.4959 | 443.3366 | 391.9531
1954.0354 | 424.3814 | 443.7763 | 391.6454
1955.0354 | 424.6105 | 444.9171 | 391.6351
1956.0354 | 424.8586 | 446.7688 | 392.5174
1957.0354 | 425.1447 | 447.912 | 392.5638
1958.0354 | 426.4705 | 449.5309 | 393.5722
1959.0354 | 425.8545 | 448.9797 | 393.5168
1960.0354 | 425.6582 | 447.8739 | 393.516
1961.0354 | 425.3523 | 445.5889 | 392.3842
1962.0354 | 425.157 | 444.5055 | 392.2129
1963.0354 | 426.6434 | 445.7688 | 392.0326
1964.0354 | 427.4717 | 447.0235 | 392.1078
1965.0354 | 427.0516 | 445.0204 | 391.314
1966.0354 | 426.4524 | 444.5466 | 390.7199
1967.0354 | 426.836 | 445.2997 | 392.588
1968.0354 | 426.3838 | 445.1108 | 393.0451
1969.0354 | 426.3357 | 444.8036 | 393.5991
1970.0354 | 426.033 | 445.0563 | 393.902
1971.0354 | 425.7577 | 445.8807 | 395.2478
1972.0354 | 426.316 | 446.2585 | 396.1008
1973.0354 | 426.5768 | 446.8499 | 396.9158
1974.0354 | 426.0345 | 447.0841 | 396.5801
1975.0354 | 427.2122 | 447.2877 | 397.0214
1976.0354 | 428.1941 | 446.9052 | 397.219
1977.0354 | 428.0632 | 446.6399 | 397.0945
1978.0354 | 427.9959 | 446.7441 | 396.9118
1979.0354 | 427.4596 | 446.2457 | 396.7575
1980.0354 | 427.3191 | 446.0404 | 396.2853
1981.0354 | 427.8204 | 445.8211 | 396.893
1982.0354 | 427.5094 | 448.5705 | 398.0372
1983.0354 | 427.2714 | 450.8795 | 398.8743
1984.0354 | 427.2686 | 450.4573 | 398.4269
1985.0354 | 428.2502 | 450.7772 | 398.6296
1986.0354 | 429.457 | 449.1804 | 397.2522
1987.0354 | 431.9111 | 449.6154 | 396.8305
1988.0354 | 432.8936 | 449.2052 | 396.329
1989.0354 | 433.2629 | 448.4472 | 395.4006
1990.0354 | 433.3099 | 448.1684 | 395.4766
1991.0354 | 432.969 | 447.5786 | 395.1647
1992.0354 | 432.8425 | 448.5842 | 396.4781
1993.0354 | 432.6046 | 448.3247 | 396.8796
1994.0354 | 432.9793 | 449.3616 | 397.2783
1995.0354 | 432.3203 | 450.115 | 397.5717
1996.0354 | 432.8111 | 450.3692 | 398.3365
1997.0354 | 433.1068 | 449.3142 | 398.8055
1998.0354 | 432.5684 | 448.8997 | 399.1038
1999.0354 | 432.4467 | 448.2588 | 398.828
2000.0354 | 431.7505 | 449.1755 | 399.491
2001.0354 | 432.139 | 451.9952 | 401.4019
2002.0354 | 431.8884 | 453.4276 | 402.2029
2003.0354 | 432.3112 | 453.1113 | 401.8202
2004.0354 | 433.5293 | 451.8654 | 400.7958
2005.0354 | 433.2012 | 451.6222 | 400.9337
2006.0354 | 432.9405 | 450.0911 | 400.7358
2007.0354 | 432.8344 | 449.3352 | 400.2833
2008.0354 | 432.7581 | 450.4638 | 400.5091
2009.0354 | 432.8688 | 453.1696 | 401.5631
2010.0354 | 433.3208 | 455.0036 | 402.1423
2011.0354 | 434.0298 | 454.5197 | 401.7962
2012.0354 | 434.4509 | 455.0213 | 402.4834
2013.0354 | 435.0021 | 456.5676 | 402.2489
2014.0354 | 436.5424 | 457.1046 | 401.3961
2015.0354 | 439.0659 | 458.5848 | 401.5222
2016.0354 | 439.9328 | 457.8909 | 401.1601
2017.0354 | 440.3766 | 458.9733 | 401.4645
2018.0354 | 442.3152 | 462.333 | 401.5995
2019.0354 | 442.9461 | 463.2729 | 402.3578
2020.0354 | 444.0973 | 462.4083 | 402.6824
2021.0354 | 442.7938 | 461.8555 | 402.8324
2022.0354 | 441.8313 | 461.9317 | 403.2898
2023.0354 | 442.0022 | 461.6728 | 404.226
2024.0354 | 441.8365 | 460.477 | 403.8864
2025.0354 | 441.4763 | 459.6702 | 403.4733
2026.0354 | 441.7235 | 458.6876 | 403.2851
2027.0354 | 441.7341 | 457.6584 | 403.6803
2028.0354 | 441.7243 | 456.8143 | 404.8023
2029.0354 | 442.4452 | 457.7158 | 405.1556
2030.0354 | 442.5977 | 457.3573 | 404.6255
2031.0354 | 442.9629 | 457.0446 | 404.6017
2032.0354 | 444.0884 | 463.3283 | 405.6437
2033.0354 | 444.6902 | 467.819 | 406.3181
2034.0354 | 445.2835 | 467.2444 | 406.3411
2035.0354 | 445.3941 | 465.9186 | 405.8594
2036.0354 | 444.7025 | 465.4023 | 406.0635
2037.0354 | 444.2234 | 463.6971 | 404.7868
2038.0354 | 444.1293 | 461.6254 | 403.4174
2039.0354 | 444.1449 | 462.8968 | 403.517
2040.0354 | 445.9966 | 465.5413 | 404.2224
2041.0354 | 447.6974 | 469.357 | 404.9251
2042.0354 | 447.4522 | 469.3891 | 403.8689
2043.0354 | 446.893 | 468.0341 | 403.3028
2044.0354 | 446.3414 | 466.7181 | 403.0384
2045.0354 | 445.8121 | 465.5738 | 402.7573
2046.0354 | 446.0996 | 464.7298 | 403.0165
2047.0354 | 445.9249 | 465.0168 | 403.5042
2048.0354 | 445.7422 | 465.0931 | 404.5963
2049.0354 | 445.422 | 464.3045 | 404.3194
2050.0354 | 445.6978 | 463.6119 | 404.7761
2051.0354 | 445.158 | 463.4072 | 404.5304
2052.0354 | 446.2525 | 463.9591 | 404.724
2053.0354 | 446.1335 | 462.9647 | 404.682
2054.0354 | 446.7055 | 464.5267 | 405.2933
2055.0354 | 446.7455 | 465.3097 | 405.3863
2056.0354 | 445.8812 | 465.221 | 405.8749
2057.0354 | 445.9954 | 465.6786 | 406.57
2058.0354 | 446.6745 | 470.9155 | 408.6083
2059.0354 | 448.9171 | 476.7478 | 410.3888
2060.0354 | 451.7079 | 481.2613 | 412.6098
2061.0354 | 453.2878 | 481.4132 | 412.6931
2062.0354 | 453.2914 | 480.1137 | 412.3995
2063.0354 | 454.7267 | 480.4132 | 411.654
2064.0354 | 454.0116 | 479.4126 | 411.1261
2065.0354 | 453.6697 | 477.8749 | 409.3294
2066.0354 | 453.5652 | 477.5413 | 409.5851
2067.0354 | 452.9482 | 478.1527 | 409.5207
2068.0354 | 451.9254 | 476.6733 | 409.5114
2069.0354 | 451.895 | 476.1399 | 409.5801
2070.051 | 454.165 | 480.3202 | 410.0652
2071.0354 | 457.6633 | 485.7536 | 411.8577
2072.0354 | 459.088 | 492.4214 | 414.0191
2073.0354 | 459.9607 | 498.6543 | 415.861
2074.0354 | 458.6587 | 499.5594 | 414.9934
2075.0354 | 459.4659 | 502.0672 | 414.1146
2076.0354 | 462.5004 | 504.6012 | 414.7123
2077.0354 | 463.3666 | 504.6184 | 416.1571
2078.0354 | 462.9915 | 503.3271 | 416.408
2079.0354 | 464.521 | 505.4105 | 417.0558
2080.0354 | 464.5475 | 504.0476 | 416.4161
2081.0354 | 463.1199 | 502.4343 | 416.7137
2082.0354 | 463.8796 | 512.9676 | 418.7786
2083.0354 | 465.0419 | 517.0151 | 421.2795
2084.0354 | 465.4669 | 517.2303 | 421.916
2085.0354 | 464.3348 | 517.3953 | 422.0951
2086.0354 | 463.5168 | 519.9138 | 422.5244
2087.0354 | 463.2259 | 521.6964 | 423.587
2088.0354 | 461.5721 | 521.7981 | 423.8782
2089.0354 | 460.7903 | 519.5358 | 423.9317
2090.0354 | 461.1785 | 525.9129 | 425.4913
2091.0354 | 462.9147 | 532.2573 | 428.1647
2092.0354 | 463.6307 | 531.8993 | 427.9133
2093.0354 | 464.5875 | 534.1522 | 428.5784
2094.0354 | 465.5109 | 534.4957 | 429.3433
2095.0354 | 468.7001 | 536.9435 | 428.9151
2096.0354 | 468.2906 | 552.8695 | 427.7715
2097.0354 | 469.2235 | 564.7416 | 427.9764
2098.0354 | 469.4726 | 566.4947 | 431.9749
2099.0354 | 469.9137 | 561.5097 | 433.895
2100.0354 | 469.1797 | 556.0243 | 435.3924
2101.0354 | 468.8085 | 552.7873 | 437.1792
2102.0354 | 469.356 | 546.4471 | 437.5154
2103.0354 | 468.7911 | 543.1158 | 437.9394
2104.0354 | 468.2789 | 538.7295 | 438.1764
2105.0354 | 469.2433 | 536.0068 | 437.5247
2106.0354 | 468.4652 | 530.3762 | 435.8403
2107.0354 | 470.8763 | 530.9893 | 436.7469
2108.0354 | 471.5688 | 530.2406 | 437.905
2109.0354 | 471.1441 | 528.9058 | 437.7488
2110.0354 | 470.8373 | 531.022 | 438.1068
2111.0354 | 471.1555 | 526.7578 | 437.9285
2112.0354 | 470.5519 | 524.5142 | 437.7362
2113.0354 | 469.5792 | 525.0354 | 436.7221
2114.0354 | 469.6186 | 523.1705 | 436.7847
2115.0354 | 469.8561 | 518.098 | 435.3383
2116.0354 | 468.9592 | 514.87 | 434.9969
2117.0354 | 467.4084 | 512.0063 | 435.0774
2118.0354 | 467.7556 | 516.0948 | 438.0371
2119.0354 | 467.6807 | 514.396 | 439.4631
2120.0354 | 467.8845 | 512.3163 | 440.2325
2121.0354 | 468.6898 | 513.3097 | 440.5633
2122.0354 | 469.4775 | 515.5826 | 441.0569
2123.0354 | 470.105 | 518.5913 | 440.8098
2124.0354 | 469.9627 | 521.3983 | 441.3047
2125.0354 | 469.6661 | 519.5555 | 439.6883
2126.0354 | 470.4516 | 519.7413 | 439.8166
2127.0354 | 469.214 | 517.0259 | 438.784
2128.0354 | 469.2569 | 520.7761 | 438.0544
2129.0354 | 472.0048 | 527.9508 | 438.9106
2130.0354 | 472.5593 | 530.3065 | 439.0197
2131.0354 | 473.4548 | 534.2038 | 439.5032
2132.0354 | 474.7317 | 536.2131 | 441.3992
2133.0354 | 475.102 | 535.934 | 444.3196
2134.0354 | 476.0781 | 536.0226 | 445.0286
2135.0354 | 476.6232 | 537.5483 | 446.5709
2136.0354 | 476.7833 | 537.5182 | 446.8728
2137.0354 | 476.8695 | 539.347 | 447.6559
2138.0354 | 477.2142 | 541.8212 | 449.4304
2139.0354 | 479.351 | 542.9718 | 449.8915
2140.0354 | 481.5173 | 543.0181 | 450.2323
2141.0354 | 483.5598 | 544.5761 | 450.8308
2142.0354 | 485.1563 | 549.003 | 452.8151
2143.0354 | 486.361 | 547.6497 | 453.539
2144.0354 | 487.183 | 549.9243 | 452.2914
2145.0354 | 488.9156 | 549.399 | 453.5358
2146.0354 | 489.0153 | 550.875 | 452.8741
2147.0354 | 490.4334 | 550.988 | 454.0291
2148.0354 | 491.7969 | 548.5257 | 453.0601
2149.0354 | 493.8254 | 547.1705 | 452.4811
2150.0354 | 497.4519 | 545.7178 | 451.4561
2151.0354 | 498.9101 | 546.079 | 450.4122
2152.0354 | 499.7211 | 542.3657 | 450.8763
2153.0354 | 500.0202 | 539.2136 | 450.5466
2154.0354 | 498.9834 | 540.2526 | 449.1372
2155.0354 | 499.2852 | 538.9259 | 447.26
2156.0354 | 500.0156 | 536.0534 | 448.5485
2157.0354 | 498.9499 | 536.6286 | 447.7981
2158.0354 | 499.7725 | 540.577 | 448.2159
2159.0354 | 502.6943 | 568.5244 | 449.3886
2160.0354 | 503.1425 | 575.7268 | 449.9371
2161.0354 | 503.7145 | 585.8448 | 450.3178
2162.0354 | 503.5197 | 581.2748 | 449.9452
2163.0354 | 503.332 | 575.7026 | 450.4532
2164.0354 | 502.7525 | 571.5696 | 452.1398
2165.0354 | 501.519 | 564.6969 | 453.0538
2166.0354 | 500.5303 | 559.323 | 453.0368
2167.0354 | 499.5328 | 553.5615 | 452.9587
2168.0354 | 497.9332 | 548.8926 | 451.894
2169.0354 | 496.8449 | 543.73 | 452.365
2170.0354 | 495.4484 | 538.8896 | 452.2858
2171.0354 | 494.245 | 532.9359 | 452.1344
2172.0354 | 493.0404 | 528.1997 | 451.2655
2173.0354 | 492.0137 | 525.5372 | 449.9979
2174.0354 | 491.7539 | 523.29 | 450.1894
2175.0354 | 491.4764 | 523.2267 | 450.6238
2176.0354 | 491.2367 | 522.2189 | 451.5299
2177.0354 | 491.155 | 521.6066 | 450.0151
2178.0354 | 491.3842 | 528.0165 | 451.7269
2179.0354 | 492.5504 | 528.7161 | 454.5725
2180.0354 | 492.4085 | 525.8526 | 454.911
2181.0354 | 493.4002 | 527.3125 | 455.0128
2182.0354 | 493.3851 | 525.5525 | 453.5954
2183.0354 | 492.9857 | 522.4954 | 453.0315
2184.0354 | 492.7031 | 520.3116 | 452.0473
2185.0354 | 492.1191 | 518.7279 | 452.05
2186.0354 | 492.0561 | 520.3757 | 452.507
2187.0354 | 491.845 | 519.818 | 453.755
2188.0354 | 490.6065 | 517.5083 | 451.3575
2189.0354 | 490.5921 | 518.3992 | 450.0808
2190.0354 | 490.433 | 521.2637 | 450.7144
2191.0354 | 491.6433 | 522.9525 | 451.2843
2192.0354 | 491.9936 | 524.0346 | 453.0062
2193.0354 | 491.986 | 525.9569 | 455.1751
2194.0354 | 491.5282 | 526.6058 | 455.7006
2195.0354 | 491.3998 | 528.6375 | 457.4961
2196.0354 | 490.9145 | 525.136 | 457.5903
2197.0354 | 492.2363 | 530.902 | 458.1657
2198.0354 | 493.3074 | 533.227 | 458.9592
2199.0354 | 494.307 | 535.0619 | 459.114
2200.0354 | 495.8106 | 538.0034 | 460.957
2201.0354 | 496.0001 | 541.414 | 462.5678
2202.0354 | 496.0379 | 540.1399 | 462.2336
2203.0354 | 497.1223 | 541.639 | 461.975
2204.0354 | 498.1562 | 543.9156 | 463.5304
2205.0354 | 499.5178 | 547.2437 | 464.5941
2206.0354 | 500.322 | 551.6521 | 464.5217
2207.0354 | 500.6502 | 552.2507 | 465.1832
2208.0354 | 502.2434 | 553.3547 | 467.3929
2209.0354 | 504.1373 | 554.8503 | 466.8984
2210.0354 | 506.2456 | 552.3032 | 466.9246
2211.0354 | 508.3435 | 552.2617 | 466.4535
2212.0354 | 510.4632 | 553.2436 | 466.8964
2213.0354 | 512.0801 | 554.3819 | 466.4152
2214.0354 | 513.984 | 554.2869 | 465.3676
2215.0354 | 516.74 | 555.1401 | 465.7542
2216.0354 | 517.2572 | 556.1461 | 464.9413
2217.0354 | 518.1129 | 554.0358 | 465.5926
2218.0354 | 519.861 | 552.9873 | 464.3107
2219.0354 | 522.5018 | 553.1502 | 462.8818
2220.0354 | 523.7231 | 553.3018 | 463.18
2221.0354 | 525.0724 | 554.4583 | 463.5081
2222.0354 | 526.9306 | 552.4002 | 463.9418
2223.0354 | 528.3123 | 552.5078 | 465.2967
2224.0354 | 529.3209 | 550.5115 | 465.0357
2225.0354 | 531.7331 | 550.1663 | 465.4916
2226.0354 | 533.5064 | 551.1257 | 466.0464
2227.0354 | 533.5034 | 550.5334 | 467.0825
2228.0354 | 534.921 | 553.4107 | 468.8257
2229.0354 | 536.0284 | 554.0045 | 468.8339
2230.0354 | 536.852 | 549.4769 | 466.9115
2231.0354 | 538.7685 | 550.4786 | 465.1989
2232.0354 | 542.5571 | 554.1802 | 467.4782
2233.0354 | 544.4488 | 555.455 | 467.8509
2234.0354 | 547.143 | 556.0507 | 469.3749
2235.0354 | 547.7237 | 553.3005 | 470.4601
2236.0354 | 547.2487 | 553.3979 | 469.5321
2237.0354 | 548.4969 | 552.2652 | 470.6107
2238.0354 | 549.5433 | 563.433 | 474.018
2239.0354 | 551.6028 | 565.6665 | 477.3585
2240.0354 | 551.9345 | 563.0124 | 476.9336
2241.0354 | 552.9308 | 557.6601 | 475.7135
2242.0354 | 556.4845 | 554.3332 | 477.3777
2243.0354 | 558.1661 | 554.27 | 478.3328
2244.0354 | 558.1517 | 550.5795 | 481.6538
2245.0354 | 558.548 | 549.2898 | 488.3192
2246.0354 | 558.9872 | 555.3234 | 497.6632
2247.0354 | 561.1384 | 554.3756 | 504.5947
2248.0354 | 564.4587 | 548.7757 | 506.824
2249.0354 | 565.3954 | 551.5312 | 507.538
2250.0354 | 567.8147 | 549.8517 | 506.7364
2251.0354 | 568.3608 | 551.2969 | 503.233
2252.0354 | 567.8852 | 552.0469 | 500.474
2253.0354 | 568.5405 | 553.2801 | 498.424
2254.0354 | 568.8453 | 558.4205 | 496.723
2255.0354 | 569.027 | 558.6056 | 494.3517
2256.0354 | 568.3193 | 560.2077 | 496.8113
2257.0354 | 565.771 | 560.0042 | 496.0771
2258.0354 | 563.7194 | 560.6362 | 496.3546
2259.0354 | 563.25 | 559.7801 | 496.0465
2260.0354 | 561.8209 | 556.4052 | 495.9532
2261.0354 | 562.0186 | 552.7365 | 494.1691
2262.0354 | 562.0898 | 550.93 | 491.6621
2263.0354 | 562.3925 | 551.7693 | 491.3348
2264.0354 | 561.8942 | 549.5848 | 489.138
2265.0354 | 564.7733 | 545.7203 | 488.9913
2266.0354 | 566.2358 | 543.3092 | 488.4803
2267.0354 | 565.9984 | 546.0409 | 489.2765
2268.0354 | 564.2906 | 549.3974 | 491.2246
2269.0354 | 562.6775 | 548.9502 | 490.3362
2270.0354 | 562.0482 | 549.6981 | 489.7334
2271.0354 | 562.4691 | 555.0948 | 489.7997
2272.0354 | 562.5893 | 555.3252 | 491.2155
2273.0354 | 561.8934 | 554.9048 | 489.8863
2274.0354 | 561.6785 | 555.2589 | 491.1331
2275.0354 | 561.864 | 554.2257 | 492.8515
2276.0354 | 561.2253 | 553.2006 | 492.6797
2277.0354 | 559.8771 | 556.3231 | 491.4763
2278.0354 | 560.6552 | 567.5007 | 494.3699
2279.0354 | 561.9907 | 571.7945 | 498.3479
2280.0354 | 562.3155 | 571.2767 | 499.6957
2281.0354 | 562.0501 | 570.0977 | 503.6913
2282.0354 | 562.633 | 572.0501 | 508.5619
2283.0354 | 560.8248 | 575.8719 | 508.4135
2284.0354 | 557.4011 | 576.7898 | 508.1723
2285.0354 | 558.7799 | 576.84 | 507.5944
2286.0354 | 558.6783 | 571.8358 | 505.1598
2287.0354 | 558.1006 | 570.3109 | 502.6159
2288.0354 | 556.8671 | 571.0838 | 502.2496
2289.0354 | 556.7641 | 567.1931 | 499.7509
2290.0354 | 557.9339 | 567.2179 | 499.3724
2291.0354 | 555.4918 | 563.94 | 498.9843
2292.0354 | 554.7496 | 566.9772 | 499.3442
2293.0354 | 552.1823 | 572.0471 | 499.2623
2294.0354 | 550.1056 | 566.9414 | 500.2989
2295.0354 | 548.5908 | 567.6488 | 499.2015
2296.0354 | 548.2829 | 569.2567 | 499.6284
2297.0354 | 548.9433 | 571.9037 | 501.6113
2298.0354 | 549.8215 | 571.876 | 503.206
2299.0354 | 549.6493 | 575.4839 | 505.1023
2300.0354 | 548.197 | 574.6284 | 505.7567
2301.0354 | 546.1476 | 576.816 | 508.0183
2302.0354 | 546.0117 | 578.5367 | 508.9807
2303.0354 | 546.5329 | 575.5036 | 508.8128
2304.0354 | 548.9142 | 572.0465 | 507.9503
2305.0354 | 550.9256 | 569.9112 | 508.3161
2306.0354 | 550.6112 | 568.7057 | 506.8976
2307.0354 | 549.3269 | 565.1914 | 506.3401
2308.0354 | 549.4093 | 565.5013 | 503.2581
2309.0354 | 550.4976 | 567.4599 | 505.1272
2310.0354 | 551.3564 | 568.1541 | 508.32
2311.0354 | 552.3477 | 566.7578 | 507.7149
2312.0354 | 553.2535 | 567.171 | 510.0675
2313.0354 | 552.987 | 563.7331 | 509.4487
2314.0354 | 551.7335 | 559.2228 | 508.4835
2315.0354 | 551.3528 | 562.499 | 509.4145
2316.0354 | 551.0019 | 563.7924 | 511.1966
2317.0354 | 550.8216 | 566.4584 | 513.0812
2318.0354 | 550.8891 | 566.6223 | 510.0545
2319.0354 | 552.115 | 567.0647 | 513.6878
2320.0354 | 553.2227 | 568.5165 | 514.3361
2321.0354 | 551.6331 | 567.2212 | 513.1911
2322.0354 | 551.7727 | 566.0833 | 512.9184
2323.0354 | 550.1929 | 571.6697 | 515.3602
2324.0354 | 548.9652 | 576.2248 | 515.2746
2325.0354 | 546.487 | 576.2433 | 516.8624
2326.0354 | 545.8264 | 573.6565 | 515.1222
2327.0354 | 546.6717 | 574.6158 | 514.5068
2328.0354 | 547.4509 | 571.9753 | 514.0071
2329.0354 | 549.5612 | 576.5764 | 514.5677
2330.0354 | 550.4434 | 573.274 | 514.2645
2331.0354 | 553.3016 | 570.8176 | 514.57
2332.0354 | 554.4391 | 575.3933 | 511.4046
2333.0354 | 554.463 | 577.0388 | 516.6638
2334.0354 | 555.5094 | 574.5621 | 515.2137
2335.0354 | 553.8921 | 567.1431 | 512.8545
2336.0354 | 553.2133 | 570.7556 | 512.937
2337.0354 | 554.8219 | 568.5899 | 512.325
2338.0354 | 557.0255 | 566.6972 | 508.558
2339.0354 | 556.402 | 565.6318 | 509.4973
2340.0354 | 557.6654 | 567.5324 | 510.5705
2341.0354 | 561.0185 | 573.0231 | 511.6113
2342.0354 | 561.4969 | 571.8957 | 512.6184
2343.0354 | 560.4311 | 570.6262 | 514.7435
2344.0354 | 561.301 | 570.379 | 515.1475
2345.0354 | 562.319 | 568.2479 | 514.4849
2346.0354 | 562.6561 | 565.6676 | 512.7249
2347.0354 | 564.6542 | 564.8582 | 510.3228
2348.0354 | 565.6756 | 564.6572 | 509.8261
2349.0354 | 563.5962 | 563.8481 | 514.2822
2350.0354 | 564.0674 | 562.7919 | 512.8718
2351.0354 | 564.917 | 563.1435 | 513.0286
2352.0354 | 564.5702 | 564.5373 | 513.7958
2353.0354 | 565.6475 | 566.8488 | 515.0284
2354.0354 | 564.9508 | 565.9369 | 517.9033
2355.0354 | 565.1989 | 565.7373 | 518.7822
2356.0354 | 566.8194 | 561.664 | 516.7091
2357.0354 | 568.6051 | 561.5385 | 517.8544
2358.0354 | 568.9543 | 560.142 | 518.241
2359.0354 | 567.9649 | 562.1555 | 518.8115
2360.0354 | 567.7584 | 564.832 | 519.0143
2361.0354 | 565.7886 | 566.9277 | 518.7118
2362.0354 | 563.6089 | 567.895 | 519.6952
2363.0354 | 562.0349 | 569.1911 | 516.625
2364.0354 | 560.56 | 569.0076 | 517.8072
2365.0354 | 558.8425 | 566.6727 | 516.18
2366.0354 | 559.3357 | 562.4952 | 514.1894
2367.0354 | 559.224 | 559.3947 | 512.1281
2368.0354 | 559.9001 | 559.4154 | 511.4929
2369.0354 | 560.0638 | 557.5402 | 509.0645
2370.0354 | 562.0242 | 561.0516 | 512.3573
2371.0354 | 562.3978 | 560.2714 | 512.0088
2372.0354 | 560.6034 | 566.2851 | 513.8509
2373.0354 | 560.6086 | 568.2704 | 513.7272
2374.0354 | 557.336 | 569.448 | 511.9976
2375.0354 | 557.9844 | 567.7071 | 512.1782
2376.0823 | 557.8259 | 563.9486 | 509.4733
2377.0354 | 557.6752 | 562.3711 | 508.5685
2378.0354 | 558.8416 | 564.5439 | 508.9654
2379.0354 | 559.524 | 563.7794 | 508.3496
2380.0354 | 559.0506 | 561.4889 | 505.498
2381.0354 | 560.3449 | 560.3218 | 503.669
2382.0354 | 560.5502 | 558.3336 | 507.8299
2383.0354 | 562.4449 | 556.2209 | 507.4648
2384.0354 | 563.99 | 558.2462 | 508.5068
2385.0354 | 564.0767 | 558.7743 | 508.8082
2386.0354 | 563.8717 | 556.7865 | 509.8349
2387.0354 | 562.0342 | 557.5323 | 509.3136
2388.0354 | 560.8468 | 557.4105 | 512.402
2389.0354 | 560.0119 | 557.4472 | 513.4866
2390.0354 | 557.9224 | 561.4382 | 516.8688
2391.0354 | 556.2429 | 562.8643 | 516.8774
2392.0354 | 554.7586 | 564.1788 | 516.2826
2393.0354 | 553.8713 | 561.8637 | 514.8168
2394.0354 | 553.7013 | 562.9072 | 514.6967
2395.0354 | 553.9955 | 566.9623 | 516.8648
2396.0354 | 554.5047 | 566.4086 | 516.6317
2397.0354 | 555.0391 | 567.8667 | 515.8192
2398.0354 | 553.9817 | 566.0119 | 516.8676
2399.0354 | 555.2637 | 565.3212 | 516.7977
2400.0354 | 557.5198 | 566.5278 | 515.8596
2401.0354 | 558.7661 | 564.2326 | 516.8814
2402.0354 | 558.1507 | 564.6 | 518.9287
2403.0354 | 557.1247 | 564.6283 | 519.0801
2404.0354 | 556.2253 | 567.4104 | 520.3595
2405.0354 | 556.3454 | 569.2526 | 519.0055
2406.0354 | 555.6709 | 573.81 | 519.1572
2407.0354 | 554.4182 | 577.016 | 520.8631
2408.0354 | 554.6435 | 578.14 | 522.4067
2409.0354 | 552.5192 | 576.5855 | 519.698
2410.0354 | 552.6546 | 573.6416 | 520.8843
2411.0354 | 553.6986 | 571.8173 | 519.5149
2412.0354 | 554.3492 | 570.8768 | 521.701
2413.0354 | 554.3516 | 568.8093 | 520.1941
2414.0354 | 553.5724 | 566.2897 | 520.2596
2415.0354 | 553.4641 | 563.7597 | 518.272
2416.0354 | 552.7365 | 564.9373 | 519.5112
2417.0354 | 551.9628 | 562.7057 | 519.457
2418.0354 | 551.4411 | 558.4335 | 517.6785
2419.0354 | 549.8099 | 557.7246 | 521.1895
2420.0354 | 549.0297 | 558.227 | 522.5391
2421.0354 | 549.8983 | 558.2853 | 523.2487
2422.0354 | 550.2143 | 559.3041 | 521.1203
2423.0354 | 549.5141 | 557.1819 | 520.0609
2424.0354 | 549.5532 | 557.9353 | 520.0855
2425.0354 | 547.8531 | 558.0442 | 522.9966
2426.0354 | 547.1691 | 557.8583 | 523.9291
2427.0354 | 548.0913 | 557.0286 | 522.7184
2428.0354 | 548.5512 | 560.2306 | 524.3772
2429.0354 | 547.4075 | 561.6851 | 524.7361
2430.0354 | 548.0112 | 559.6795 | 524.6949
2431.0354 | 549.5679 | 559.0899 | 525.0493
2432.0354 | 551.5728 | 559.0653 | 524.9056
2433.0354 | 551.5422 | 558.6168 | 525.2494
2434.0354 | 550.6699 | 557.1933 | 524.8758
2435.0354 | 550.0911 | 555.5226 | 523.5742
2436.0354 | 549.6843 | 555.5347 | 522.7487
2437.0354 | 548.3912 | 556.6001 | 525.033
2438.0354 | 546.8084 | 557.216 | 526.2327
2439.0354 | 546.5266 | 554.8503 | 526.6113
2440.0354 | 545.2684 | 551.1089 | 523.7991
2441.0354 | 544.7447 | 550.0195 | 522.6333
2442.0354 | 544.6065 | 548.177 | 521.4263
2443.0354 | 544.2191 | 548.8265 | 521.4189
2444.0354 | 544.9676 | 549.6581 | 522.8397
2445.0354 | 544.012 | 549.4323 | 520.3416
2446.0354 | 543.8078 | 550.3389 | 521.6027
2447.0354 | 542.8549 | 548.6861 | 521.9427
2448.0354 | 541.4533 | 550.3826 | 523.2406
2449.0354 | 540.4004 | 550.3823 | 525.9095
2450.0354 | 540.0587 | 553.1422 | 527.3013
2451.0354 | 540.307 | 556.3299 | 528.5938
2452.0354 | 539.3625 | 558.9282 | 528.6435
2453.0354 | 539.3579 | 562.8616 | 529.4861
2454.0354 | 539.59 | 566.81 | 531.147
2455.0354 | 540.7289 | 569.7475 | 532.0993
2456.0354 | 540.6701 | 573.6161 | 530.9047
2457.0354 | 541.0235 | 571.346 | 530.7213
2458.0354 | 541.3527 | 570.9969 | 531.7417
2459.0354 | 542.1191 | 571.8599 | 532.7226
2460.0354 | 542.2099 | 574.4389 | 531.652
2461.0354 | 542.9293 | 578.9087 | 533.3097
2462.0354 | 543.2105 | 574.9733 | 533.4872
2463.0354 | 543.3258 | 571.0625 | 532.4691
2464.0354 | 543.9701 | 566.8297 | 531.092
2465.0354 | 545.2832 | 570.6538 | 532.1452
2466.0354 | 545.7515 | 572.1591 | 533.9321
2467.0354 | 546.0373 | 573.7208 | 533.1767
2468.0354 | 547.7193 | 572.6227 | 531.1929
2469.0354 | 550.4488 | 570.922 | 530.0737
2470.0354 | 551.1923 | 569.1303 | 530.2799
2471.0354 | 551.5157 | 569.3208 | 532.2683
2472.0354 | 551.8182 | 567.4011 | 533.6551
2473.0354 | 553.2488 | 567.028 | 532.8712
2474.0354 | 554.7506 | 569.0764 | 534.308
2475.0354 | 555.1536 | 568.5574 | 533.9941
2476.0354 | 554.1223 | 568.4383 | 533.1925
2477.0354 | 556.1795 | 572.9562 | 535.6979
2478.0354 | 557.9892 | 571.3826 | 536.3509
2479.0354 | 559.242 | 571.7467 | 536.9838
2480.0354 | 562.0464 | 569.1859 | 536.3331
2481.0354 | 563.7696 | 567.5548 | 535.6354
2482.0354 | 568.3695 | 565.5001 | 535.5096
2483.0354 | 568.6433 | 565.9664 | 536.991
2484.0354 | 568.4158 | 565.6034 | 539.2317
2485.0354 | 567.0857 | 563.2699 | 539.1987
2486.0354 | 568.31 | 565.0424 | 540.0865
2487.0354 | 570.2162 | 565.7889 | 540.8499
2488.0354 | 574.7328 | 568.536 | 543.3031
2489.0354 | 576.4526 | 569.4815 | 543.2213
2490.0354 | 580.7932 | 567.3843 | 546.1863
2491.0354 | 584.6964 | 569.6609 | 551.8695
2492.0354 | 587.3578 | 568.6674 | 553.0251
2493.0354 | 591.8977 | 568.3972 | 554.4608
2494.0354 | 596.0211 | 566.4991 | 553.8951
2495.0354 | 596.2454 | 568.9437 | 553.1791
2496.0354 | 595.2571 | 572.8455 | 553.8466
2497.0354 | 596.4068 | 571.8369 | 552.5123
2498.0354 | 597.1976 | 574.3032 | 550.45
2499.0354 | 597.8641 | 571.9818 | 551.0607
2500.0354 | 597.1979 | 569.2178 | 548.3118
2501.0354 | 597.3683 | 567.1096 | 548.0342
2502.0354 | 596.4982 | 569.6121 | 548.9193
2503.0354 | 596.7981 | 570.8074 | 549.5178
2504.0354 | 597.967 | 572.0383 | 549.1992
2505.0354 | 597.6599 | 575.8304 | 546.7397
2506.0354 | 598.3927 | 579.7763 | 549.7023
2507.0354 | 600.6132 | 582.1181 | 548.2645
2508.0354 | 597.706 | 579.7368 | 547.3704
2509.0354 | 598.2794 | 577.4402 | 546.9803
2510.0354 | 600.1198 | 574.8322 | 548.4044
2511.0354 | 600.7829 | 578.2226 | 550.2055
2512.0354 | 599.7488 | 577.6609 | 549.8722
2513.0354 | 601.0112 | 577.1214 | 549.34
2514.0354 | 599.5441 | 574.5449 | 548.8611
2515.0354 | 599.8277 | 572.331 | 547.484
2516.0354 | 598.7273 | 570.4479 | 546.3955
2517.0354 | 597.3176 | 570.2248 | 545.8911
2518.0354 | 595.6262 | 567.5394 | 543.4202
2519.0354 | 593.404 | 566.7648 | 552.62
2520.0354 | 592.6366 | 566.2625 | 551.5191
2521.0354 | 592.8201 | 568.166 | 550.9338
2522.0354 | 593.5824 | 567.5417 | 550.1755
2523.0354 | 592.446 | 565.7929 | 548.1477
2524.0354 | 593.1312 | 562.8072 | 547.4591
2525.0354 | 590.4859 | 562.8894 | 548.4408
2526.0354 | 587.7271 | 560.4148 | 549.1709
2527.0354 | 585.1234 | 558.4074 | 551.6525
2528.0354 | 583.1939 | 557.7663 | 552.0419
2529.0354 | 581.266 | 560.0373 | 551.9382
2530.0354 | 581.5141 | 562.8881 | 551.8826
2531.0354 | 580.383 | 562.9307 | 549.1792
2532.0354 | 580.1355 | 564.3036 | 549.0909
2533.0354 | 577.1809 | 565.6254 | 549.5274
2534.0354 | 574.8934 | 566.9475 | 550.06
2535.0354 | 573.0648 | 567.4411 | 549.8861
2536.0354 | 572.7069 | 564.8648 | 549.3441
2537.0354 | 573.4754 | 562.6083 | 547.2401
2538.0354 | 572.5182 | 566.1993 | 546.8889
2539.0354 | 571.6679 | 565.9954 | 546.1356
2540.0354 | 571.6692 | 564.0375 | 544.064
2541.0354 | 570.4398 | 565.7868 | 542.9076
2542.0354 | 568.7802 | 565.3821 | 543.5628
2543.0354 | 569.6071 | 565.0576 | 543.4789
2544.0354 | 569.0176 | 560.5036 | 541.9306
2545.0354 | 572.0217 | 559.8032 | 541.7569
2546.0354 | 572.6825 | 560.114 | 542.197
2547.0354 | 571.2377 | 561.3268 | 539.8382
2548.0354 | 577.5519 | 558.8599 | 539.2548
2549.0354 | 576.4753 | 563.1402 | 541.4666
2550.0354 | 571.7748 | 563.2758 | 541.0055
2551.0354 | 569.0694 | 560.8189 | 538.8241
2552.0354 | 566.4256 | 561.5386 | 536.6968
2553.0354 | 567.3562 | 561.5948 | 536.7881
2554.0354 | 567.2842 | 560.2993 | 536.1174
2555.0354 | 568.5102 | 558.6186 | 534.1505
2556.0354 | 568.6618 | 561.7132 | 534.7746
2557.0354 | 568.8897 | 565.4418 | 538.0899
2558.0354 | 565.8273 | 573.1131 | 540.8255
2559.0354 | 562.3473 | 573.9468 | 540.9952
2560.0354 | 563.2753 | 573.1135 | 545.399
2561.0354 | 562.5335 | 571.993 | 544.0693
2562.0354 | 561.4203 | 568.1294 | 543.774
2563.0354 | 560.7079 | 568.2575 | 541.7266
2564.0354 | 559.6236 | 567.2946 | 542.1604
2565.0354 | 559.3832 | 568.6658 | 543.7103
2566.0354 | 559.0958 | 569.2891 | 545.4482
2567.0354 | 558.5588 | 568.8235 | 547.3491
2568.0354 | 558.1702 | 566.1347 | 548.0083
2569.0354 | 556.3685 | 563.0288 | 545.2745
2570.0354 | 555.8814 | 561.4065 | 543.0661
2571.0354 | 553.522 | 561.8724 | 543.4262
2572.0354 | 552.0588 | 561.4314 | 543.6823
2573.0354 | 551.0027 | 562.0197 | 546.1953
2574.0354 | 549.6081 | 561.2328 | 546.6714
2575.0354 | 550.4072 | 560.3097 | 546.3554
2576.0354 | 549.3542 | 559.6214 | 547.0948
2577.0354 | 551.9384 | 559.8896 | 546.3769
2578.0354 | 554.2432 | 559.4209 | 547.1293
2579.0354 | 555.6981 | 559.3682 | 545.5609
2580.0354 | 560.5063 | 560.6799 | 544.2944
2581.0354 | 562.0552 | 560.4113 | 543.7829
2582.0354 | 563.0761 | 559.2751 | 542.3099
2583.0354 | 564.3123 | 556.9955 | 541.0427
2584.0354 | 564.4617 | 556.0106 | 539.5346
2585.0354 | 563.2723 | 553.9477 | 538.1788
2586.0354 | 560.9953 | 551.4814 | 537.0999
2587.0354 | 558.1007 | 552.0633 | 537.4719
2588.0354 | 556.0631 | 551.853 | 537.6054
2589.0354 | 554.444 | 553.0033 | 537.7495
2590.0354 | 552.2533 | 553.2096 | 537.1073
2591.0354 | 550.8568 | 555.3067 | 537.8595
2592.0354 | 548.1951 | 555.105 | 537.9429
2593.0354 | 546.6343 | 555.0262 | 536.6351
2594.0354 | 545.5378 | 554.7269 | 535.8721
2595.0354 | 545.1166 | 556.1011 | 535.4975
2596.0354 | 544.2787 | 554.4823 | 533.2116
2597.0354 | 544.6179 | 554.1375 | 531.552
2598.0354 | 544.7386 | 552.8505 | 530.6608
2599.0354 | 544.4889 | 551.7752 | 530.4064
2600.0354 | 544.2467 | 554.7895 | 530.9079
2601.0354 | 543.0709 | 552.9826 | 532.2844
2602.0354 | 542.7924 | 552.6699 | 533.5361
2603.0354 | 542.4943 | 551.9028 | 533.19
2604.0354 | 541.7014 | 553.555 | 531.8534
2605.0354 | 541.9948 | 557.044 | 534.6965
2606.0354 | 541.3337 | 559.723 | 533.9088
2607.0354 | 540.1633 | 560.7365 | 532.9903
2608.0354 | 539.4514 | 559.5003 | 534.2834
2609.0354 | 539.033 | 559.8263 | 534.681
2610.0354 | 540.2031 | 560.1572 | 534.5361
2611.0354 | 540.7012 | 559.9396 | 534.675
2612.0354 | 540.0307 | 561.6804 | 535.3038
2613.0354 | 539.3996 | 561.7316 | 537.1001
2614.0354 | 539.5535 | 560.9021 | 537.2156
2615.0354 | 539.0613 | 559.3123 | 536.8036
2616.0354 | 538.3928 | 558.2392 | 537.0401
2617.0354 | 537.9465 | 560.4848 | 542.7912
2618.0354 | 537.6565 | 560.6578 | 543.0443
2619.0354 | 538.9429 | 563.0774 | 545.3516
2620.0354 | 539.3153 | 560.3569 | 544.5494
2621.0354 | 539.6998 | 557.0327 | 541.6085
2622.0354 | 540.2903 | 561.2132 | 542.8256
2623.0354 | 539.8405 | 563.9418 | 544.5362
2624.0354 | 539.6727 | 565.2967 | 547.9247
2625.0354 | 539.44 | 564.4844 | 550.1214
2626.0354 | 539.0248 | 565.6813 | 550.89
2627.0354 | 539.966 | 565.8819 | 550.0788
2628.0354 | 540.5087 | 566.2647 | 552.3054
2629.0354 | 540.7339 | 564.8902 | 551.4756
2630.0354 | 539.337 | 564.9443 | 553.1134
2631.0354 | 540.713 | 563.3331 | 550.4599
2632.0354 | 540.7395 | 562.9159 | 549.9093
2633.0354 | 540.5335 | 559.0153 | 548.2008
2634.0354 | 539.606 | 560.6252 | 546.8555
2635.0354 | 538.4633 | 558.6831 | 545.0434
2636.0354 | 537.8017 | 559.3529 | 543.5791
2637.0354 | 537.0537 | 558.2084 | 542.4697
2638.0354 | 536.4026 | 556.1965 | 540.8155
2639.0354 | 536.851 | 554.5074 | 538.2917
2640.0354 | 537.4571 | 556.1004 | 536.9682
2641.0354 | 536.7248 | 558.2129 | 536.6859
2642.0354 | 537.9619 | 557.0915 | 535.4313
2643.0354 | 538.1104 | 555.4681 | 533.703
2644.0354 | 537.7129 | 553.2643 | 533.079
2645.0354 | 537.706 | 551.5602 | 531.4688
2646.0354 | 536.0915 | 553.833 | 530.3798
2647.0354 | 534.0303 | 554.9051 | 531.8899
2648.0354 | 532.6269 | 556.7593 | 533.4353
2649.0354 | 532.7009 | 556.5965 | 532.9878
2650.0354 | 533.815 | 557.7184 | 533.6502
2651.0354 | 533.497 | 555.3856 | 533.5012
2652.0354 | 534.0746 | 554.7832 | 532.1803
2653.0354 | 535.7543 | 556.1102 | 534.012
2654.0354 | 538.0924 | 557.5479 | 533.8946
2655.0354 | 540.003 | 559.8342 | 535.2052
2656.0354 | 539.0279 | 560.8431 | 534.7394
2657.0354 | 538.5116 | 558.7039 | 534.2433
2658.0354 | 539.7046 | 559.4401 | 535.4008
2659.0354 | 540.5995 | 559.3725 | 536.534
2660.0354 | 540.3497 | 556.0932 | 535.8772
2661.0354 | 541.7725 | 555.8153 | 535.2511
2662.0354 | 543.3029 | 555.9831 | 536.1028
2663.0354 | 543.081 | 554.0171 | 535.6098
2664.0354 | 542.6798 | 551.4275 | 535.0759
2665.0354 | 542.1059 | 549.7752 | 535.4497
2666.0354 | 542.4465 | 550.3063 | 535.2912
2667.0354 | 541.1606 | 548.2996 | 533.7211
2668.0354 | 541.7906 | 550.5209 | 536.8217
2669.0354 | 540.5411 | 551.7973 | 539.6802
2670.0354 | 539.6744 | 550.1027 | 540.2296
2671.0354 | 539.225 | 550.3021 | 539.1124
2672.0354 | 540.5604 | 551.9058 | 540.3371
2673.0354 | 540.6905 | 551.3787 | 539.2232
2674.0354 | 541.4874 | 553.7501 | 539.2838
2675.0354 | 541.0568 | 553.5606 | 539.2527
2676.0354 | 540.1169 | 553.1725 | 537.7845
2677.0354 | 540.7979 | 552.4513 | 537.7681
2678.0354 | 541.3281 | 553.314 | 536.717
2679.0354 | 541.8665 | 552.8259 | 536.046
2680.0354 | 540.8164 | 553.3648 | 538.3445
2681.0354 | 541.5815 | 554.767 | 538.9963
2682.0354 | 541.0673 | 552.9696 | 538.9442
2683.0354 | 540.369 | 551.6433 | 537.4355
2684.0354 | 540.1857 | 550.1523 | 537.1455
2685.0354 | 541.0345 | 550.6508 | 536.163
2686.0354 | 541.5809 | 549.7691 | 535.0724
2687.0354 | 541.6335 | 550.9715 | 536.2287
2688.0354 | 542.5035 | 551.3322 | 534.827
2689.0354 | 543.526 | 552.5879 | 534.9098
2690.0354 | 544.4806 | 551.8442 | 534.4812
2691.0354 | 544.8999 | 550.6814 | 534.8358
2692.0354 | 545.8413 | 550.2514 | 533.5426
2693.0354 | 545.8469 | 551.5307 | 533.3769
2694.0354 | 545.453 | 552.1182 | 534.4521
2695.0354 | 546.5794 | 552.9639 | 534.9384
2696.0354 | 546.5935 | 555.0277 | 533.534
2697.0354 | 545.2585 | 552.7647 | 531.8074
2698.0354 | 549.8499 | 551.7183 | 531.7556
2699.0354 | 551.4268 | 549.6405 | 531.6986
2700.0354 | 552.831 | 549.2193 | 531.9538
2701.0354 | 552.8701 | 553.7955 | 534.6597
2702.0354 | 559.8344 | 555.2043 | 534.9505
2703.0354 | 559.0208 | 553.0006 | 535.151
2704.0354 | 557.8783 | 553.3865 | 535.5838
2705.0354 | 561.1741 | 551.8899 | 534.8179
2706.0354 | 562.2138 | 548.8522 | 531.8566
2707.0354 | 562.039 | 548.5153 | 530.6749
2708.0354 | 567.8769 | 551.6819 | 530.9895
2709.0354 | 571.9681 | 554.7066 | 531.9168
2710.0354 | 571.2376 | 555.0882 | 533.0222
2711.0354 | 577.1145 | 552.649 | 532.4919
2712.0354 | 575.1362 | 554.0793 | 531.2919
2713.0354 | 575.8263 | 557.6916 | 534.3694
2714.0354 | 574.9802 | 562.6711 | 536.9701
2715.0354 | 573.8984 | 563.346 | 537.9015
2716.0354 | 571.7402 | 562.5306 | 536.4445
2717.0354 | 569.1439 | 560.2916 | 535.2673
2718.0354 | 566.6528 | 557.671 | 533.1892
2719.0354 | 565.2754 | 556.5823 | 534.2999
2720.0354 | 566.1047 | 556.6573 | 536.3723
2721.0354 | 569.8402 | 559.3301 | 540.1826
2722.0354 | 573.7379 | 560.2362 | 541.9058
2723.0354 | 581.5989 | 558.0044 | 542.3013
2724.0354 | 583.0156 | 557.8932 | 543.6369
2725.0354 | 584.6945 | 560.1762 | 546.9603
2726.0354 | 591.4879 | 564.8952 | 549.2677
2727.0354 | 593.5919 | 570.6807 | 550.3814
2728.0354 | 593.6295 | 568.2647 | 547.7802
2729.0354 | 591.925 | 568.5571 | 546.2949
2730.0354 | 588.0179 | 567.1957 | 546.4313
2731.0354 | 585.9784 | 566.4006 | 546.051
2732.0354 | 590.5782 | 570.0615 | 547.1149
2733.0354 | 591.6105 | 571.903 | 547.6011
2734.0354 | 592.4743 | 570.3928 | 546.4544
2735.0354 | 591.6706 | 567.6387 | 544.3154
2736.0354 | 589.7267 | 564.9115 | 542.5681
2737.0354 | 586.5375 | 564.2606 | 540.4752
2738.0354 | 585.7897 | 567.5269 | 541.1218
2739.0354 | 587.7738 | 565.781 | 540.4452
2740.0354 | 587.9669 | 565.4535 | 539.9422
2741.0354 | 585.9434 | 566.2491 | 539.806
2742.0354 | 583.3467 | 566.5719 | 538.9087
2743.0354 | 583.6378 | 566.6553 | 537.8993
2744.0354 | 581.3527 | 566.104 | 539.5849
2745.0354 | 577.9447 | 568.6859 | 540.615
2746.0354 | 574.7429 | 569.319 | 542.0471
2747.0354 | 573.7006 | 570.447 | 542.4156
2748.0354 | 576.3565 | 571.5572 | 539.9131
2749.0354 | 577.5866 | 569.7166 | 537.9824
2750.0354 | 576.311 | 567.9255 | 540.1175
2751.0354 | 576.1016 | 568.583 | 540.8482
2752.0354 | 577.4346 | 570.4982 | 541.3624
2753.0354 | 578.8219 | 571.3114 | 539.8156
2754.0354 | 579.6343 | 569.4055 | 539.8561
2755.0354 | 578.186 | 569.094 | 539.4459
2756.0354 | 576.6723 | 567.207 | 538.2656
2757.0354 | 576.7078 | 565.3167 | 536.8904
2758.0354 | 575.3175 | 565.4222 | 536.6202
2759.0354 | 578.0862 | 567.9608 | 537.1816
2760.0354 | 578.4255 | 567.7891 | 537.5213
2761.0354 | 577.7082 | 566.4238 | 536.8368
2762.0354 | 577.8311 | 565.1584 | 534.782
2763.0354 | 580.2329 | 568.352 | 536.2537
2764.0354 | 581.6287 | 568.2651 | 536.5643
2765.0354 | 582.1568 | 567.4151 | 535.9556
2766.0354 | 581.7897 | 564.867 | 534.6077
2767.0354 | 581.2055 | 564.868 | 533.4183
2768.0354 | 584.7423 | 564.9376 | 535.3573
2769.0354 | 586.9287 | 567.0836 | 536.6722
2770.0354 | 588.6532 | 567.8876 | 536.6859
2771.0354 | 590.2848 | 568.2617 | 536.8032
2772.0354 | 592.0957 | 569.3378 | 536.6344
2773.0354 | 592.0669 | 567.7032 | 536.2986
2774.0354 | 589.4303 | 568.3014 | 534.7377
2775.0354 | 588.7817 | 568.6963 | 535.248
2776.0354 | 587.7153 | 567.9772 | 535.2311
2777.0354 | 587.9774 | 567.7715 | 533.8286
2778.0354 | 587.5027 | 565.7777 | 533.9927
2779.0354 | 587.5342 | 563.9763 | 533.7396
2780.0354 | 585.9665 | 561.8287 | 531.4307
2781.0354 | 584.0954 | 561.2384 | 530.9056
2782.0354 | 582.6875 | 562.5483 | 530.9163
2783.0354 | 583.5002 | 562.1485 | 531.5721
2784.0354 | 584.0111 | 562.2422 | 532.3624
2785.0354 | 584.1144 | 561.1146 | 532.3239
2786.0354 | 581.9922 | 559.793 | 531.5256
2787.0354 | 581.1337 | 558.3639 | 530.3117
2788.0354 | 580.2585 | 557.716 | 528.2178
2789.0354 | 582.1887 | 558.3377 | 528.0388
2790.0354 | 583.1456 | 557.8667 | 528.1397
2791.0354 | 582.1501 | 556.5325 | 528.2809
2792.0354 | 581.5643 | 555.6536 | 527.6938
2793.0354 | 582.2146 | 554.1419 | 526.4947
2794.0354 | 581.2109 | 553.3856 | 526.3642
2795.0354 | 579.5527 | 553.6164 | 527.5504
2796.0354 | 578.6672 | 554.8468 | 528.6338
2797.0354 | 578.4166 | 554.4475 | 529.744
2798.0354 | 579.137 | 554.0254 | 529.5895
2799.0354 | 576.9401 | 552.5456 | 528.5743
2800.0354 | 576.4618 | 554.3388 | 528.9173
2801.0354 | 577.2494 | 555.8997 | 530.2984
2802.0354 | 576.8564 | 556.2536 | 530.4763
2803.0354 | 581.1368 | 555.1947 | 528.5403
2804.0354 | 581.4071 | 560.1359 | 531.3956
2805.0354 | 582.1373 | 561.0449 | 532.4693
2806.0354 | 583.602 | 561.4697 | 533.4501
2807.0354 | 583.5801 | 560.9049 | 533.636
2808.0354 | 584.0249 | 560.6877 | 533.2028
2809.0354 | 583.3264 | 562.2986 | 534.8152
2810.0354 | 582.8456 | 562.9132 | 536.3512
2811.0354 | 581.3481 | 561.9365 | 536.5293
2812.0354 | 581.3443 | 563.0732 | 536.335
2813.0354 | 580.3886 | 562.7641 | 536.1374
2814.0354 | 578.5946 | 562.7754 | 535.8088
2815.0354 | 578.8348 | 563.7542 | 534.7543
2816.0354 | 579.2318 | 567.0025 | 537.2125
2817.0354 | 579.5271 | 569.3591 | 539.4197
2818.0354 | 588.0551 | 567.2058 | 539.4337
2819.0354 | 587.95 | 566.7967 | 538.987
2820.0354 | 585.6922 | 567.7722 | 538.96
2821.0354 | 583.7814 | 566.7257 | 538.5332
2822.0354 | 582.0147 | 564.4934 | 536.8606
2823.0354 | 583.464 | 565.2593 | 537.1801
2824.0354 | 584.1483 | 568.3335 | 537.7327
2825.0354 | 583.7113 | 570.8059 | 539.2132
2826.0354 | 583.1633 | 571.6901 | 540.5865
2827.0354 | 581.4117 | 572.9107 | 541.3395
2828.0354 | 581.6941 | 574.522 | 541.7802
2829.0354 | 580.9742 | 572.8264 | 541.1405
2830.0354 | 579.4401 | 569.671 | 539.0196
2831.0354 | 578.5722 | 567.5669 | 537.3905
2832.0354 | 578.9855 | 565.6208 | 536.7658
2833.0354 | 578.9663 | 563.6726 | 535.1689
2834.0354 | 581.3197 | 564.8891 | 535.0498
2835.0354 | 583.041 | 567.7573 | 535.8158
2836.0354 | 583.0549 | 567.9342 | 536.2872
2837.0354 | 583.8878 | 568.7236 | 536.2896
2838.0354 | 583.7124 | 571.4739 | 538.0032
2839.0354 | 584.8587 | 570.0721 | 537.2418
2840.0354 | 583.8055 | 569.2232 | 536.7706
2841.0354 | 583.7952 | 567.5685 | 535.4713
2842.0354 | 585.6055 | 570.1757 | 537.1859
2843.0354 | 585.5792 | 568.8766 | 537.0708
2844.0354 | 585.4671 | 567.5602 | 536.9621
2845.0354 | 584.9251 | 568.0328 | 537.235
2846.0354 | 586.1807 | 566.5455 | 536.0537
2847.0354 | 585.4589 | 567.9036 | 536.3181
2848.0354 | 587.526 | 568.2161 | 536.8567
2849.0354 | 588.7853 | 566.6321 | 535.9451
2850.0354 | 589.7184 | 565.8443 | 535.7226
2851.0354 | 589.2946 | 566.9851 | 535.9925
2852.0354 | 589.4157 | 567.8541 | 537.5037
2853.0354 | 588.3197 | 568.3824 | 538.2015
2854.0354 | 587.5684 | 568.8273 | 538.9667
2855.0354 | 586.9986 | 569.7265 | 539.2575
2856.0354 | 586.5953 | 569.4427 | 539.179
2857.0354 | 587.8276 | 570.972 | 539.9697
2858.0354 | 589.3736 | 572.0451 | 540.6214
2859.0354 | 589.4074 | 572.5963 | 540.4272
2860.0354 | 590.7742 | 571.6424 | 540.048
2861.0354 | 592.7308 | 569.4374 | 538.886
2862.0354 | 593.5914 | 567.6357 | 537.3916
2863.0354 | 594.107 | 567.1336 | 536.8351
2864.0354 | 593.3546 | 566.4763 | 536.3439
2865.0354 | 595.981 | 565.7333 | 535.9175
2866.0354 | 596.4852 | 566.4495 | 536.7488
2867.0354 | 595.4668 | 567.4096 | 537.129
2868.0354 | 595.0182 | 567.1353 | 536.5094
2869.0354 | 594.2056 | 565.4824 | 535.0419
2870.0354 | 593.6037 | 564.3705 | 534.56
2871.0354 | 593.4532 | 564.213 | 534.3739
2872.0354 | 592.4094 | 564.3758 | 534.6752
2873.0354 | 594.0141 | 566.0265 | 535.3276
2874.0354 | 594.4003 | 568.1125 | 537.056
2875.0354 | 597.2944 | 570.4569 | 539.4844
2876.0354 | 597.3928 | 572.4361 | 541.265
2877.0354 | 597.0537 | 573.4444 | 541.6234
2878.0354 | 596.2466 | 573.8149 | 542.9643
2879.0354 | 595.7485 | 573.1983 | 542.8002
2880.0354 | 593.9593 | 575.1809 | 543.0216
2881.0354 | 596.2822 | 574.5431 | 543.0357
2882.0354 | 597.9261 | 575.529 | 542.4205
2883.0354 | 599.2341 | 575.8229 | 543.7117
2884.0354 | 598.5736 | 575.8871 | 544.8187
2885.0354 | 601.0445 | 577.8111 | 545.4664
2886.0354 | 601.2096 | 575.4737 | 543.9554
2887.0354 | 602.1543 | 573.0665 | 542.8354
2888.0354 | 601.4603 | 571.8871 | 541.1899
2889.0354 | 601.3548 | 570.8132 | 540.932
2890.0354 | 600.8856 | 572.5142 | 542.4578
2891.0354 | 601.9838 | 573.9697 | 543.5761
2892.0354 | 600.0932 | 573.8711 | 542.6081
2893.0354 | 600.2124 | 574.943 | 542.4463
2894.0354 | 598.2502 | 573.3601 | 541.5889
2895.0354 | 597.5287 | 571.7792 | 539.8031
2896.0354 | 597.1813 | 570.9674 | 539.7245
2897.0354 | 597.0423 | 571.7757 | 540.6059
2898.0354 | 598.6884 | 570.7043 | 541.7855
2899.0354 | 600.4969 | 570.1936 | 541.92
2900.0354 | 599.4506 | 570.8594 | 542.3417
2901.0354 | 600.2294 | 572.1824 | 542.0848
2902.0354 | 602.0643 | 573.4191 | 542.9217
2903.0354 | 601.6438 | 573.1434 | 542.6842
2904.0354 | 601.1025 | 573.6911 | 543.327
2905.0354 | 602.0759 | 574.6219 | 542.4815
2906.0354 | 602.4241 | 575.5072 | 543.3232
2907.0354 | 602.6557 | 575.4856 | 542.3357
2908.0354 | 603.2239 | 573.6981 | 541.1865
2909.0354 | 603.2599 | 573.6745 | 540.3692
2910.0354 | 602.593 | 573.9672 | 540.5872
2911.0354 | 601.627 | 574.0867 | 540.3563
2912.0354 | 602.0724 | 574.5855 | 540.2626
2913.0354 | 602.2435 | 576.3993 | 540.3358
2914.0354 | 602.4742 | 574.7617 | 540.1344
2915.0354 | 602.4453 | 574.3589 | 539.9641
2916.0354 | 601.304 | 574.7661 | 539.4365
2917.0354 | 600.2416 | 574.246 | 537.8042
2918.0354 | 600.5358 | 573.072 | 537.1153
2919.0354 | 600.1699 | 574.0407 | 537.8455
2920.0354 | 599.2833 | 575.8956 | 539.3624
2921.0354 | 598.5185 | 575.6876 | 539.245
2922.0354 | 599.3979 | 576.526 | 540.1747
2923.0354 | 599.3061 | 576.7895 | 540.1929
2924.0354 | 600.8101 | 576.1727 | 540.7776
2925.0354 | 602.5522 | 576.7416 | 542.75
2926.0354 | 603.9081 | 576.1838 | 543.2271
2927.0354 | 605.2905 | 577.0614 | 544.7855
2928.0354 | 605.3506 | 577.0405 | 544.866
2929.0354 | 604.6944 | 576.8035 | 545.4539
2930.0354 | 603.0146 | 576.5916 | 545.3966
2931.0354 | 603.7014 | 576.9648 | 544.5545
2932.0354 | 604.9168 | 576.2495 | 543.1508
2933.0354 | 604.2594 | 575.7069 | 542.2787
2934.0354 | 603.0786 | 574.7166 | 542.3097
2935.0354 | 601.1165 | 575.2604 | 543.3838
2936.0354 | 600.2681 | 575.0652 | 542.8359
2937.0354 | 601.0991 | 579.1136 | 545.1719
2938.0354 | 600.5476 | 579.1712 | 545.007
2939.0354 | 600.5851 | 576.9305 | 543.9593
2940.0354 | 599.4727 | 575.2387 | 543.0894
2941.0354 | 597.9345 | 574.7105 | 542.4347
2942.0354 | 599.5116 | 576.2618 | 542.4644
2943.0354 | 599.1862 | 578.382 | 544.2621
2944.0354 | 598.2818 | 578.1274 | 544.1194
2945.0354 | 598.8342 | 581.1735 | 544.8726
2946.0354 | 599.5481 | 582.3892 | 544.8738
2947.0354 | 599.4189 | 581.1005 | 543.7834
2948.0354 | 601.1036 | 581.2593 | 542.8414
2949.0354 | 602.6421 | 581.5779 | 542.5161
2950.0354 | 601.7248 | 581.7001 | 542.1215
2951.0354 | 601.7651 | 582.6314 | 542.346
2952.0354 | 600.3499 | 582.4527 | 541.7106
2953.0354 | 600.3831 | 581.1494 | 541.6787
2954.0354 | 601.7897 | 578.1437 | 539.068
2955.0354 | 602.2694 | 576.3932 | 538.7654
2956.0354 | 600.5632 | 574.4382 | 537.4141
2957.0354 | 601.1946 | 574.7594 | 538.1506
2958.0354 | 602.0189 | 575.3665 | 538.4453
2959.0354 | 602.4146 | 577.6481 | 539.9353
2960.0354 | 601.1321 | 578.4477 | 540.0148
2961.0354 | 600.8202 | 580.7459 | 542.8643
2962.0354 | 598.8251 | 579.9508 | 543.7002
2963.0354 | 598.3575 | 579.846 | 543.6743
2964.0354 | 600.5142 | 582.0257 | 543.87
2965.0354 | 601.6437 | 579.824 | 544.6471
2966.0354 | 600.9353 | 577.8453 | 545.2585
2967.0354 | 603.5599 | 576.5882 | 547.9855
2968.0354 | 605.8713 | 574.9615 | 547.4404
2969.0354 | 607.614 | 574.1673 | 546.0831
2970.0354 | 608.1575 | 575.0042 | 546.4028
2971.0354 | 607.3518 | 576.2726 | 546.0193
2972.0354 | 605.3801 | 575.8647 | 545.6566
2973.0354 | 604.0919 | 574.4036 | 544.7294
2974.0354 | 603.708 | 574.9944 | 544.2674
2975.0354 | 603.3183 | 575.277 | 545.3248
2976.0354 | 601.6398 | 575.2743 | 545.0462
2977.0354 | 601.1819 | 575.99 | 544.0718
2978.0354 | 601.7156 | 575.4125 | 544.925
2979.0354 | 600.5669 | 573.5536 | 543.9494
2980.0354 | 601.776 | 572.9201 | 542.5087
2981.0354 | 602.514 | 572.2447 | 541.6616
2982.0354 | 601.9488 | 574.1621 | 541.5948
2983.0354 | 602.1821 | 575.9584 | 541.2597
2984.0354 | 603.4866 | 576.1024 | 541.1949
2985.0354 | 603.3761 | 576.1025 | 541.6834
2986.0354 | 602.9517 | 577.2847 | 542.5655
2987.0354 | 603.0974 | 578.6949 | 542.7339
2988.0354 | 603.7948 | 580.5905 | 543.5534
2989.0354 | 603.0238 | 585.418 | 546.1839
2990.0354 | 602.6824 | 585.0077 | 545.1119
2991.0354 | 600.6464 | 583.8762 | 545.4743
2992.0354 | 601.21 | 584.3773 | 544.6446
2993.0354 | 606.648 | 586.1133 | 542.1793
2994.0354 | 603.3337 | 587.5258 | 545.8572
2995.0354 | 603.1854 | 590.4843 | 547.9946
2996.0354 | 602.0409 | 590.0481 | 548.9922
2997.0354 | 602.5497 | 590.966 | 549.926
2998.0354 | 602.5225 | 588.7133 | 549.4296
2999.0354 | 601.4606 | 586.6182 | 548.5627
3000.0354 | 600.3398 | 584.6367 | 548.0177
3001.0354 | 600.2776 | 583.8116 | 546.5909
3002.0354 | 600.4039 | 582.269 | 546.0554
3003.0354 | 601.0633 | 581.7058 | 546.0226
3004.0354 | 602.6754 | 581.7025 | 545.7958
3005.0354 | 604.7894 | 583.9409 | 547.4384
3006.0354 | 604.2778 | 584.4726 | 548.1114
3007.0354 | 603.6667 | 585.3636 | 548.1093
3008.0354 | 601.5512 | 584.1749 | 548.0992
3009.0354 | 601.2943 | 583.0019 | 545.9564
3010.0354 | 601.6151 | 580.9816 | 544.9515
3011.0354 | 601.8555 | 579.9659 | 544.5976
3012.0354 | 603.2377 | 576.8887 | 543.4675
3013.0354 | 604.6087 | 575.0851 | 541.9302
3014.0354 | 605.1488 | 575.9224 | 541.7883
3015.0354 | 605.4735 | 578.3507 | 542.7004
3016.0354 | 606.3269 | 580.1783 | 543.6915
3017.0354 | 604.8182 | 580.2866 | 544.0184
3018.0354 | 604.1814 | 582.1063 | 544.9032
3019.0354 | 603.76 | 583.2041 | 546.7459
3020.0354 | 604.0927 | 583.8258 | 546.2614
3021.0354 | 603.2296 | 582.3367 | 546.383
3022.0354 | 602.0398 | 580.4168 | 545.8484
3023.0354 | 601.1619 | 580.301 | 546.1001
3024.0354 | 601.4411 | 580.1573 | 545.5265
3025.0354 | 603.8528 | 582.0114 | 545.4769
3026.0354 | 603.5569 | 581.5469 | 544.6594
3027.0354 | 603.8155 | 579.1158 | 544.1936
3028.0354 | 605.1478 | 578.6334 | 543.5012
3029.0354 | 604.2337 | 577.0106 | 543.662
3030.0354 | 603.5486 | 576.7018 | 543.2078
3031.0354 | 604.3365 | 578.6446 | 545.1973
3032.0354 | 604.271 | 578.0411 | 545.4067
3033.0354 | 602.8222 | 576.4919 | 544.799
3034.0354 | 601.3935 | 576.3563 | 545.1795
3035.0354 | 601.2434 | 575.1514 | 544.6388
3036.0354 | 600.3217 | 575.4118 | 544.7301
3037.0354 | 600.243 | 576.3907 | 545.0196
3038.0354 | 600.78 | 577.5531 | 545.7492
3039.0354 | 601.3453 | 579.4068 | 545.8813
3040.0354 | 601.3061 | 579.9005 | 546.397
3041.0354 | 600.8495 | 579.7725 | 546.239
3042.0354 | 600.9326 | 580.4025 | 546.0012
3043.0354 | 600.9168 | 579.7721 | 545.079
3044.0354 | 600.3355 | 578.8686 | 544.0394
3045.0354 | 600.283 | 578.6974 | 543.8189
3046.0354 | 600.0618 | 577.1215 | 543.2451
3047.0354 | 599.1404 | 575.1319 | 542.8621
3048.0354 | 599.0912 | 574.7734 | 542.1414
3049.0354 | 597.6289 | 572.4185 | 541.3991
3050.0354 | 596.769 | 571.6824 | 541.1697
3051.0354 | 595.7874 | 571.1361 | 541.022
3052.0354 | 595.0153 | 572.044 | 540.9948
3053.0354 | 595.6323 | 573.1658 | 540.9168
3054.0354 | 596.2153 | 572.5559 | 540.7301
3055.0354 | 597.4952 | 572.2122 | 540.5806
3056.0354 | 596.665 | 573.4556 | 541.1947
3057.0354 | 597.691 | 574.2558 | 542.3134
3058.0354 | 599.5009 | 575.5609 | 542.8652
3059.0354 | 599.6285 | 576.7197 | 544.0982
3060.0354 | 598.531 | 577.844 | 544.9872
3061.0354 | 597.4292 | 583.1418 | 548.6105
3062.0354 | 596.7608 | 581.4383 | 547.9816
3063.0354 | 594.5979 | 579.1955 | 547.305
3064.0354 | 592.9333 | 577.4243 | 545.9975
3065.0354 | 592.5803 | 576.9966 | 546.5654
3066.0354 | 592.3362 | 576.8079 | 547.4736
3067.0354 | 593.0727 | 576.6985 | 547.8525
3068.0354 | 592.7682 | 576.2675 | 547.6744
3069.0354 | 592.9069 | 574.3679 | 546.6092
3070.0354 | 592.7676 | 573.9798 | 545.745
3071.0354 | 592.2068 | 572.5155 | 545.177
3072.0354 | 593.5168 | 576.4353 | 546.4862
3073.0354 | 593.9117 | 578.9743 | 548.3562
3074.0354 | 594.3222 | 578.5514 | 548.173
3075.0354 | 592.4405 | 576.8316 | 547.3346
3076.0354 | 592.3104 | 576.4312 | 546.3798
3077.0354 | 592.3982 | 576.9747 | 546.5089
3078.0354 | 592.1729 | 577.696 | 547.7332
3079.0354 | 591.7373 | 579.5222 | 549.4589
3080.0354 | 590.7961 | 578.204 | 549.4559
3081.0354 | 589.4959 | 578.1712 | 550.2744
3082.0354 | 588.6714 | 575.7688 | 549.4581
3083.0354 | 587.2861 | 575.0568 | 548.8309
3084.0354 | 586.2216 | 574.1128 | 548.6261
3085.0354 | 586.6592 | 573.1587 | 548.2234
3086.0354 | 585.866 | 572.0458 | 547.4135
3087.0354 | 586.9614 | 572.3711 | 547.7797
3088.0354 | 589.0766 | 574.4399 | 548.3367
3089.0354 | 591.7921 | 575.8334 | 548.2232
3090.0354 | 592.512 | 574.9348 | 547.2295
3091.0354 | 593.1108 | 573.873 | 545.9213
3092.0354 | 594.3264 | 574.6774 | 545.4454
3093.0354 | 594.1072 | 574.2698 | 546.0322
3094.0354 | 592.2989 | 572.1191 | 545.4571
3095.0354 | 591.8291 | 573.6315 | 545.154
3096.0354 | 594.2412 | 577.294 | 545.9765
3097.0354 | 595.5884 | 578.7475 | 547.8532
3098.0354 | 595.1824 | 579.2379 | 549.864
3099.0354 | 594.0975 | 579.2138 | 550.678
3100.0354 | 594.163 | 578.3182 | 549.8667
3101.0354 | 593.4851 | 577.4215 | 550.2006
3102.0354 | 593.3569 | 577.7343 | 549.2403
3103.0354 | 594.6896 | 577.4254 | 549.3431
3104.0354 | 594.2499 | 575.7693 | 547.8348
3105.0354 | 593.6098 | 573.82 | 546.1522
3106.0354 | 592.4993 | 573.1295 | 545.6404
3107.0354 | 591.017 | 572.3349 | 545.5494
3108.0354 | 592.1961 | 571.3039 | 545.2228
3109.0354 | 592.6184 | 570.8599 | 544.2183
3110.0354 | 592.0008 | 570.6229 | 544.1033
3111.0354 | 592.3114 | 569.8219 | 544.6395
3112.0354 | 592.8038 | 570.0374 | 544.4591
3113.0354 | 593.3997 | 571.1813 | 545.0233
3114.0354 | 593.9083 | 570.4022 | 544.3238
3115.0354 | 597.0185 | 573.1504 | 544.5948
3116.0354 | 598.2492 | 573.9186 | 545.0784
3117.0354 | 598.0915 | 573.5907 | 544.9546
3118.0354 | 597.1956 | 573.1545 | 544.9362
3119.0354 | 595.8327 | 573.1233 | 545.1917
3120.0354 | 595.1224 | 573.0257 | 545.5085
3121.0354 | 594.4835 | 572.6874 | 545.9453
3122.0354 | 593.1812 | 572.5958 | 546.3737
3123.0354 | 591.1498 | 572.7854 | 547.4484
3124.0354 | 588.6166 | 572.6352 | 549.0172
3125.0354 | 586.4393 | 573.0336 | 549.7425
3126.0354 | 585.1964 | 572.1405 | 548.9587
3127.0354 | 583.7991 | 571.2934 | 548.7338
3128.0354 | 582.5307 | 571.6283 | 548.1364
3129.0354 | 584.0652 | 574.1209 | 548.6646
3130.0354 | 583.9669 | 573.2229 | 548.5687
3131.0354 | 583.7383 | 573.3742 | 548.8996
3132.0354 | 582.9018 | 572.5437 | 548.903
3133.0354 | 583.2057 | 573.5788 | 549.1868
3134.0354 | 584.3255 | 574.2143 | 549.4716
3135.0354 | 583.7236 | 573.7356 | 549.2966
3136.0354 | 583.074 | 573.1364 | 549.6301
3137.0354 | 582.8406 | 573.2427 | 549.9233
3138.0354 | 582.5568 | 575.8527 | 550.3316
3139.0354 | 582.9251 | 577.032 | 552.1767
3140.0354 | 582.6493 | 576.4626 | 551.5544
3141.0354 | 582.3727 | 575.7537 | 551.0124
3142.0354 | 582.6328 | 576.5065 | 551.4105
3143.0354 | 583.4084 | 577.059 | 552.9744
3144.0354 | 583.5652 | 576.6397 | 553.3698
3145.0354 | 583.2177 | 575.9797 | 553.0297
3146.0354 | 582.2092 | 575.3469 | 553.5544
3147.0354 | 581.7051 | 574.6275 | 553.614
3148.0354 | 579.8653 | 573.741 | 553.7698
3149.0354 | 580.1653 | 575.4571 | 554.1376
3150.0354 | 581.1816 | 573.7558 | 553.2455
3151.0354 | 580.6063 | 572.1946 | 551.6341
3152.0354 | 578.8882 | 570.3363 | 551.7518
3153.0354 | 577.9912 | 569.3643 | 551.3902
3154.0354 | 576.7398 | 568.8621 | 551.6418
3155.0354 | 577.9345 | 574.3055 | 553.7548
3156.0354 | 579.2335 | 576.1165 | 554.3718
3157.0354 | 579.9552 | 575.8531 | 554.2581
3158.0354 | 580.6552 | 574.3957 | 553.5572
3159.0354 | 580.3165 | 573.8982 | 553.4621
3160.0354 | 580.1985 | 573.8126 | 553.0794
3161.0354 | 580.4003 | 574.3551 | 553.8302
3162.0354 | 580.2354 | 574.2362 | 553.627
3163.0354 | 579.2647 | 574.0283 | 552.9723
3164.0354 | 579.2095 | 573.0152 | 552.4137
3165.0354 | 579.539 | 573.4245 | 551.924
3166.0354 | 579.7176 | 572.7936 | 551.5351
3167.0354 | 579.9979 | 573.0839 | 551.3859
3168.0354 | 580.397 | 573.1007 | 551.2051
3169.0354 | 581.6584 | 573.3031 | 551.4183
3170.0354 | 582.2964 | 575.3492 | 552.6737
3171.0354 | 583.2312 | 578.3896 | 554.4878
3172.0354 | 584.4647 | 580.7318 | 554.9835
3173.0354 | 585.2078 | 581.3066 | 555.5504
3174.0354 | 584.5466 | 581.0922 | 555.6618
3175.0354 | 583.9288 | 580.8509 | 555.2783
3176.0354 | 583.7121 | 581.6191 | 557.538
3177.0354 | 582.3471 | 582.6159 | 558.957
3178.0354 | 581.6472 | 580.8851 | 559.4422
3179.0354 | 580.7528 | 580.7497 | 560.6095
3180.0354 | 580.6761 | 580.9731 | 559.5981
3181.0354 | 579.5207 | 580.0185 | 558.7272
3182.0354 | 579.1007 | 579.3206 | 558.9466
3183.0354 | 579.8452 | 579.5317 | 558.6103
3184.0354 | 578.3257 | 577.654 | 557.2033
3185.0354 | 577.3785 | 576.0975 | 557.7156
3186.0354 | 577.7731 | 574.7007 | 557.554
3187.0354 | 576.8327 | 573.4614 | 556.4586
3188.0354 | 576.8477 | 573.0904 | 556.2635
3189.0354 | 578.2258 | 572.824 | 555.5084
3190.0354 | 579.3127 | 570.3854 | 553.2294
3191.0354 | 578.053 | 567.6039 | 550.8971
3192.0354 | 577.3029 | 566.2083 | 549.3601
3193.0354 | 577.4252 | 566.499 | 549.3566
3194.0354 | 577.8236 | 566.0405 | 548.8172
3195.0354 | 576.4209 | 566.6789 | 548.7979
3196.0354 | 576.0776 | 570.037 | 550.1002
3197.0354 | 576.4797 | 574.0022 | 552.5808
3198.0354 | 576.6041 | 575.2949 | 553.566
3199.0354 | 576.6042 | 575.0466 | 553.5775
3200.0354 | 577.168 | 576.5143 | 556.6436
3201.0354 | 577.4174 | 575.008 | 558.0199
3202.0354 | 576.8153 | 574.3997 | 558.8393
3203.0354 | 576.6867 | 575.926 | 559.8028
3204.0354 | 576.1129 | 576.2035 | 560.4204
3205.0354 | 575.719 | 575.2335 | 558.7434
3206.0354 | 575.9474 | 574.348 | 558.0166
3207.0354 | 575.8935 | 575.8124 | 557.8986
3208.0354 | 576.5842 | 577.7302 | 559.1833
3209.0354 | 579.3984 | 583.1777 | 561.8936
3210.0354 | 579.5779 | 583.0773 | 561.454
3211.0354 | 580.1116 | 584.8442 | 561.674
3212.0354 | 579.6176 | 585.4636 | 564.1223
3213.0354 | 578.5833 | 584.8462 | 563.2238
3214.0354 | 577.3304 | 584.8784 | 563.3388
3215.0354 | 578.711 | 584.7783 | 561.7012
3216.0354 | 577.9382 | 583.1964 | 561.3037
3217.0354 | 577.556 | 581.8357 | 560.8333
3218.0354 | 578.0445 | 581.1647 | 559.9405
3219.0354 | 578.3618 | 581.2949 | 560.1856
3220.0354 | 578.7308 | 582.1538 | 560.9794
3221.0354 | 578.4394 | 581.0023 | 559.9542
3222.0354 | 577.4891 | 580.1062 | 559.6404
3223.0354 | 576.9297 | 578.8029 | 558.1308
3224.0354 | 576.9928 | 576.6175 | 557.776
3225.0354 | 576.6584 | 576.2499 | 557.1343
3226.0354 | 577.1343 | 577.7214 | 558.0476
3227.0354 | 577.2176 | 577.448 | 558.8725
3228.0354 | 576.1139 | 576.6524 | 558.0556
3229.0354 | 576.1513 | 577.1229 | 558.2037
3230.0354 | 575.944 | 577.5811 | 558.9686
3231.0354 | 574.8517 | 576.4828 | 559.7358
3232.0354 | 574.4332 | 576 | 559.2389
3233.0354 | 573.9014 | 575.1204 | 558.2179
3234.0354 | 573.8701 | 573.5765 | 556.8606
3235.0354 | 573.9937 | 572.811 | 555.6543
3236.0354 | 574.4959 | 573.8527 | 555.3738
3237.0354 | 574.9822 | 575.1269 | 556.4021
3238.0354 | 575.9294 | 575.2378 | 557.7217
3239.0354 | 574.8821 | 575.7691 | 558.7337
3240.0354 | 575.0611 | 575.7291 | 560.5369
3241.0354 | 575.2908 | 575.7716 | 562.5073
3242.0354 | 574.6005 | 576.5352 | 564.8803
3243.0354 | 573.5917 | 574.8175 | 566.1718
3244.0354 | 574.2656 | 574.9508 | 566.1353
3245.0354 | 574.822 | 574.3422 | 565.3873
3246.0354 | 574.3329 | 574.2225 | 563.934
3247.0354 | 574.2357 | 575.102 | 563.1609
3248.0354 | 574.1012 | 573.7576 | 561.3282
3249.0354 | 573.6907 | 572.4278 | 558.8274
3250.0354 | 575.118 | 572.4449 | 563.3457
3251.0354 | 575.7409 | 573.4114 | 564.6637
3252.0354 | 576.6001 | 574.9005 | 564.6202
3253.0354 | 576.4863 | 575.4294 | 565.4326
3254.0354 | 575.6464 | 573.5345 | 564.7063
3255.0354 | 574.8185 | 573.3582 | 563.8958
3256.0354 | 573.7769 | 573.4961 | 563.6638
3257.0354 | 573.7505 | 575.1658 | 563.547
3258.0354 | 573.6429 | 574.3389 | 563.3085
3259.0354 | 573.773 | 573.8157 | 562.0233
3260.0354 | 573.2885 | 573.2546 | 561.2895
3261.0354 | 573.3379 | 573.5892 | 560.6429
3262.0354 | 573.325 | 573.3219 | 559.6507
3263.0354 | 573.2001 | 573.5892 | 559.3397
3264.0354 | 572.5803 | 572.8868 | 558.6298
3265.0354 | 571.9078 | 573.6714 | 559.1132
3266.0354 | 572.1973 | 572.9594 | 558.6169
3267.0354 | 572.7869 | 571.3137 | 557.2383
3268.0354 | 573.217 | 569.3464 | 555.7727
3269.0354 | 572.0092 | 568.365 | 554.0978
3270.0354 | 571.5497 | 569.9235 | 554.7706
3271.0354 | 571.3821 | 571.9408 | 555.5453
3272.0354 | 571.8622 | 573.1608 | 555.7777
3273.0354 | 572.063 | 572.3595 | 555.054
3274.0354 | 571.7914 | 570.2323 | 553.8946
3275.0354 | 571.4284 | 568.0087 | 552.8039
3276.0354 | 571.242 | 567.669 | 553.2264
3277.0354 | 571.7199 | 568.8349 | 553.8121
3278.0354 | 571.2961 | 567.4407 | 553.1329
3279.0354 | 571.142 | 568.593 | 553.9288
3280.0354 | 570.3059 | 567.188 | 554.7436
3281.0354 | 570.1353 | 566.6972 | 554.3784
3282.0354 | 569.6738 | 566.2366 | 553.665
3283.0354 | 569.191 | 566.5768 | 554.4471
3284.0354 | 568.9622 | 567.049 | 556.3882
3285.0354 | 568.3537 | 567.6051 | 557.2073
3286.0354 | 569.4392 | 569.5974 | 556.822
3287.0354 | 570.7408 | 572.1647 | 558.664
3288.0354 | 572.2657 | 574.0522 | 559.7226
3289.0354 | 572.2796 | 573.5194 | 560.609
3290.0354 | 572.5318 | 573.8484 | 560.5421
3291.0354 | 572.6118 | 573.8727 | 560.4794
3292.0354 | 572.46 | 573.0665 | 559.7517
3293.0354 | 572.44 | 571.8678 | 558.273
3294.0354 | 572.5108 | 569.5378 | 556.2973
3295.0354 | 572.8028 | 566.9769 | 553.9516
3296.0354 | 571.8389 | 565.6945 | 553.2071
3297.0354 | 571.9718 | 565.9349 | 553.2621
3298.0354 | 571.5098 | 565.9431 | 552.883
3299.0354 | 571.737 | 566.3386 | 552.3392
3300.0354 | 573.4461 | 566.655 | 551.5159
3301.0354 | 573.3236 | 566.3014 | 551.3382
3302.0354 | 573.4335 | 565.2656 | 551.0796
3303.0354 | 573.0049 | 564.8933 | 551.4415
3304.0354 | 572.4062 | 563.9967 | 551.6121
3305.0354 | 571.8382 | 563.2803 | 550.5878
3306.0354 | 570.9537 | 563.4417 | 550.2724
3307.0354 | 571.0087 | 564.091 | 551.6242
3308.0354 | 571.2279 | 565.1934 | 551.6269
3309.0354 | 571.1918 | 564.5802 | 551.2196
3310.0354 | 571.8118 | 563.5292 | 549.7829
3311.0354 | 571.4795 | 562.9839 | 548.9861
3312.0354 | 570.4249 | 563.1309 | 549.0986
3313.0354 | 569.8623 | 561.4505 | 548.2025
3314.0354 | 569.3732 | 561.9903 | 547.6665
3315.0354 | 568.9154 | 563.5793 | 551.0819
3316.0198 | 569.1921 | 566.9262 | 555.0712
3317.0354 | 568.6919 | 567.6893 | 557.0321
3318.0354 | 568.0295 | 568.1055 | 556.2983
3319.0354 | 567.5395 | 567.3011 | 555.0176
3320.0354 | 567.4177 | 565.9668 | 554.1298
3321.0354 | 566.8429 | 565.1877 | 552.7257
3322.0354 | 566.5297 | 564.0448 | 551.0904
3323.0354 | 566.7145 | 562.9856 | 552.9792
3324.0354 | 567.1187 | 561.8714 | 551.7804
3325.0354 | 567.0071 | 560.1945 | 550.629
3326.0354 | 566.8698 | 559.7871 | 549.5801
3327.0354 | 567.4296 | 559.9686 | 549.37
3328.0354 | 567.0968 | 561.187 | 551.4615
3329.0354 | 567.1976 | 561.7626 | 551.3645
3330.0354 | 567.7713 | 561.1984 | 550.7538
3331.0354 | 567.7783 | 560.5744 | 549.8415
3332.0354 | 567.4509 | 560.0335 | 549.2318
3333.0354 | 568.1352 | 560.6199 | 548.6223
3334.0354 | 567.6269 | 560.0364 | 548.9158
3335.0354 | 566.8195 | 558.7675 | 548.2612
3336.0354 | 566.4831 | 560.1067 | 549.8179
3337.0354 | 566.3119 | 562.0265 | 553.6867
3338.0354 | 567.7638 | 563.8002 | 554.914
3339.0354 | 567.8805 | 563.6844 | 554.5376
3340.0354 | 567.1448 | 562.9301 | 554.0758
3341.0354 | 566.9538 | 564.3377 | 555.3309
3342.0354 | 566.047 | 563.8559 | 555.8248
3343.0354 | 565.5095 | 565.2599 | 558.1607
3344.0354 | 565.1871 | 566.0803 | 559.295
3345.0354 | 565.4613 | 566.125 | 558.2067
3346.0354 | 565.6243 | 565.8156 | 557.6073
3347.0354 | 565.8439 | 566.278 | 557.2434
3348.0354 | 565.7603 | 566.2367 | 559.5112
3349.0354 | 566.3969 | 566.8824 | 558.9308
3350.0354 | 567.7266 | 569.4116 | 561.2707
3351.0354 | 566.4253 | 567.7525 | 563.5485
3352.0354 | 565.8202 | 566.4174 | 563.7385
3353.0354 | 566.1519 | 565.919 | 564.3486
3354.0354 | 564.839 | 565.4842 | 565.0142
3355.0354 | 564.5933 | 565.1213 | 563.8508
3356.0354 | 563.9124 | 564.6353 | 561.9762
3357.0354 | 564.9162 | 565.3835 | 560.0106
3358.0354 | 563.4915 | 565.112 | 561.3369
3359.0354 | 564.1345 | 565.5274 | 560.2407
3360.0354 | 564.2484 | 565.0096 | 558.9807
3361.0354 | 564.5389 | 564.964 | 558.1827
3362.0354 | 564.7988 | 566.0312 | 557.6149
3363.0354 | 564.5892 | 566.0727 | 557.2748
3364.0354 | 564.512 | 565.7659 | 557.5873
3365.0354 | 563.4612 | 564.1675 | 556.8754
3366.0354 | 562.5555 | 562.9746 | 556.6415
3367.0354 | 561.9505 | 563.5858 | 556.8137
3368.0354 | 562.144 | 565.1811 | 557.0139
3369.0354 | 562.2084 | 564.3947 | 555.9174
3370.0354 | 561.5282 | 563.2324 | 554.3617
3371.0354 | 561.2082 | 562.3783 | 553.4045
3372.0354 | 562.0451 | 562.7336 | 553.0017
3373.0354 | 563.3894 | 565.4058 | 554.4867
3374.0354 | 564.6271 | 565.2253 | 553.6054
3375.0354 | 565.8863 | 565.4791 | 555.4099
3376.0354 | 565.2227 | 563.5235 | 555.7977
3377.0354 | 563.9645 | 562.545 | 554.6967
3378.0354 | 563.0464 | 561.9082 | 554.1783
3379.0354 | 562.2211 | 560.8585 | 553.132
3380.0354 | 561.2595 | 559.8357 | 551.3139
3381.0354 | 561.3637 | 559.5553 | 553.2774
3382.0354 | 561.5386 | 559.2414 | 552.3587
3383.0354 | 561.562 | 557.7734 | 550.9572
3384.0354 | 561.9946 | 556.7286 | 551.7052
3385.0354 | 561.2136 | 554.8926 | 552.6694
3386.0354 | 559.4414 | 552.9893 | 552.2562
3387.0354 | 557.9323 | 552.8669 | 551.1157
3388.0354 | 557.4434 | 553.467 | 551.0634
3389.0354 | 557.3916 | 554.8628 | 551.9734
3390.0354 | 557.4731 | 555.6975 | 551.7223
3391.0354 | 557.5746 | 555.8111 | 550.9232
3392.0354 | 557.7744 | 556.308 | 549.9593
3393.0354 | 557.8894 | 556.4511 | 549.7752
3394.0354 | 557.2236 | 556.3223 | 549.7257
3395.0354 | 556.9295 | 556.2101 | 549.0612
3396.0354 | 556.7014 | 555.7151 | 549.1579
3397.0354 | 556.4473 | 556.3704 | 548.7973
3398.0354 | 557.0742 | 557.613 | 549.9422
3399.0354 | 558.2377 | 558.329 | 549.4666
3400.0354 | 559.2098 | 559.2948 | 552.968
3401.0354 | 560.1691 | 560.0778 | 558.1766
3402.0354 | 560.2079 | 558.7066 | 556.7417
3403.0354 | 560.428 | 558.0224 | 555.8093
3404.0354 | 559.4798 | 556.754 | 554.6978
3405.0354 | 557.5697 | 554.648 | 552.8739
3406.0354 | 556.7406 | 554.2183 | 551.2352
3407.0354 | 557.3673 | 555.5513 | 551.3452
3408.0354 | 557.8896 | 554.8514 | 551.0208
3409.0354 | 557.9881 | 554.2227 | 549.8214
3410.0354 | 557.4663 | 553.0318 | 549.0957
3411.0354 | 556.8378 | 552.2964 | 548.7872
3412.0354 | 556.0341 | 552.7441 | 548.7906
3413.0354 | 555.7531 | 553.8094 | 549.5065
3414.0354 | 555.9602 | 554.1187 | 550.0719
3415.0354 | 556.2442 | 554.7838 | 550.3554
3416.0354 | 556.1534 | 555.0943 | 550.0758
3417.0354 | 557.7861 | 557.226 | 551.94
3418.0354 | 557.8492 | 558.1697 | 554.7981
3419.0354 | 556.1457 | 556.3468 | 553.9143
3420.0354 | 556.1575 | 555.7282 | 552.863
3421.0354 | 555.4712 | 556.2671 | 552.5996
3422.0354 | 556.1488 | 557.1624 | 552.3391
3423.0354 | 556.7214 | 560.4047 | 554.2116
3424.0354 | 557.6961 | 561.0033 | 553.7842
3425.0354 | 558.9323 | 562.18 | 554.1043
3426.0354 | 559.9946 | 563.8629 | 553.6308
3427.0354 | 559.4479 | 563.4559 | 553.7804
3428.0354 | 559.519 | 564.5362 | 553.9764
3429.0354 | 559.9468 | 563.6606 | 553.7284
3430.0354 | 559.4701 | 562.5799 | 552.4787
3431.0354 | 558.9481 | 561.4899 | 551.2903
3432.0354 | 558.0108 | 560.7544 | 550.247
3433.0354 | 557.83 | 559.6601 | 549.3146
3434.0354 | 557.6085 | 558.8042 | 548.3656
3435.0354 | 558.1217 | 558.5263 | 548.0104
3436.0354 | 558.7414 | 558.0962 | 546.8821
3437.0354 | 558.1184 | 557.0328 | 546.2307
3438.0354 | 557.4836 | 555.9488 | 545.3861
3439.0354 | 556.6958 | 554.4443 | 543.9515
3440.0354 | 556.4762 | 554.6648 | 543.522
3441.0354 | 556.1446 | 555.0038 | 543.9351
3442.0354 | 556.0765 | 555.0811 | 544.1583
3443.0354 | 556.0208 | 555.813 | 545.6298
3444.0354 | 555.4342 | 556.0417 | 547.0666
3445.0354 | 554.6153 | 555.4204 | 548.1852
3446.0354 | 554.4975 | 556.2491 | 549.0263
3447.0354 | 554.1418 | 557.4226 | 549.8219
3448.0354 | 555.2275 | 558.0509 | 550.0848
3449.0354 | 555.8776 | 558.2699 | 550.6078
3450.0354 | 556.3642 | 557.9975 | 551.5173
3451.0354 | 556.5844 | 558.5712 | 552.6622
3452.0354 | 556.6852 | 558.8136 | 553.943
3453.0354 | 556.7447 | 558.6441 | 554.2805
3454.0354 | 556.3075 | 557.7943 | 553.4145
3455.0354 | 556.2738 | 557.5527 | 552.812
3456.0354 | 556.187 | 557.6673 | 552.7728
3457.0354 | 555.3545 | 556.1014 | 554.0229
3458.0354 | 554.4598 | 554.7563 | 554.693
3459.0354 | 553.446 | 554.3685 | 553.9782
3460.0354 | 552.6867 | 554.2967 | 554.0416
3461.0354 | 553.1839 | 555.6237 | 554.9282
3462.0354 | 552.6984 | 556.6564 | 554.9656
3463.0354 | 552.4767 | 556.5861 | 554.981
3464.0354 | 552.4068 | 558.0253 | 555.9518
3465.0354 | 552.8389 | 560.247 | 558.6368
3466.0354 | 553.5066 | 561.7143 | 561.6364
3467.0354 | 552.7078 | 562.4335 | 562.3425
3468.0354 | 552.177 | 562.5763 | 564.0266
3469.0354 | 551.7799 | 561.8803 | 563.1001
3470.0354 | 551.736 | 562.3959 | 565.4972
3471.0354 | 550.3664 | 560.7904 | 565.5676
3472.0354 | 550.194 | 559.6793 | 563.2629
3473.0354 | 551.4708 | 559.1919 | 562.0749
3474.0354 | 551.971 | 559.235 | 560.0551
3475.0354 | 552.9746 | 560.2453 | 559.2689
3476.0354 | 553.4336 | 560.4733 | 558.6837
3477.0354 | 553.433 | 559.4719 | 558.3327
3478.0354 | 552.8928 | 558.9564 | 557.4207
3479.0354 | 552.7689 | 558.4121 | 557.0112
3480.0354 | 553.4593 | 557.5468 | 555.5894
3481.0354 | 553.8082 | 556.5404 | 554.0517
3482.0354 | 554.2005 | 557.5608 | 554.2374
3483.0354 | 555.1338 | 558.2694 | 554.1803
3484.0354 | 556.164 | 559.4037 | 553.8469
3485.0354 | 556.2125 | 558.3197 | 552.2963
3486.0354 | 555.3864 | 556.8928 | 551.7962
3487.0354 | 554.8499 | 556.8076 | 550.9884
3488.0354 | 554.669 | 555.9415 | 550.1092
3489.0354 | 554.7236 | 556.2353 | 549.2743
3490.0354 | 554.526 | 557.4669 | 555.0932
3491.0354 | 553.5362 | 558.4695 | 555.4423
3492.0354 | 552.9209 | 558.594 | 554.132
3493.0354 | 551.8603 | 557.9433 | 556.543
3494.0354 | 551.4521 | 557.8594 | 555.0168
3495.0354 | 551.8144 | 557.2817 | 554.4866
3496.0354 | 551.7952 | 556.3188 | 552.8449
3497.0354 | 552.4096 | 555.5541 | 551.5623
3498.0354 | 552.6454 | 555.5774 | 550.225
3499.0354 | 552.8571 | 554.4348 | 550.3591
3500.0354 | 552.872 | 554.0135 | 549.6966
3501.0354 | 553.0186 | 553.3294 | 548.4613
3502.0354 | 552.8351 | 552.3597 | 547.2191
3503.0354 | 552.6286 | 551.7896 | 546.4881
3504.0354 | 553.4834 | 551.7989 | 546.4023
3505.0354 | 553.1707 | 551.3552 | 548.094
3506.0354 | 553.0836 | 550.649 | 548.2939
3507.0354 | 553.0186 | 549.4798 | 548.5007
3508.0354 | 551.6659 | 547.7856 | 548.1327
3509.0354 | 550.7474 | 545.626 | 546.6839
3510.0354 | 549.7921 | 544.8466 | 545.1755
3511.0354 | 549.5543 | 545.2642 | 544.6756
3512.0354 | 549.9747 | 545.1216 | 544.1412
3513.0354 | 551.1266 | 545.9138 | 543.2515
3514.0354 | 551.693 | 546.1782 | 543.2735
3515.0354 | 551.4121 | 545.0788 | 542.373
3516.0354 | 551.6601 | 544.3341 | 543.3426
3517.0354 | 551.7337 | 544.454 | 542.854
3518.0354 | 552.9204 | 545.3909 | 542.8763
3519.0354 | 552.8245 | 546.8209 | 543.5343
3520.0354 | 553.0773 | 548.3165 | 543.9394
3521.0354 | 553.8477 | 548.6237 | 543.6432
3522.0354 | 553.8371 | 548.3609 | 543.3497
3523.0354 | 554.1996 | 548.8047 | 542.8822
3524.0354 | 554.2018 | 548.2833 | 541.9531
3525.0354 | 553.9787 | 548.3179 | 541.4368
3526.0354 | 554.0421 | 548.4203 | 541.2843
3527.0354 | 553.8642 | 548.6017 | 542.0114
3528.0354 | 553.5828 | 548.0738 | 541.3062
3529.0354 | 554.2638 | 547.4347 | 541.6802
3530.0354 | 554.154 | 545.9296 | 541.6939
3531.0354 | 553.3766 | 544.9199 | 541.5314
3532.0354 | 553.2473 | 543.7712 | 541.4039
3533.0354 | 552.7822 | 544.0106 | 542.27
3534.0354 | 552.432 | 544.7786 | 543.0144
3535.0354 | 552.6736 | 545.7384 | 542.1267
3536.0354 | 552.2266 | 545.0791 | 540.2922
3537.0354 | 551.5112 | 544.4266 | 539.1296
3538.0354 | 551.1604 | 544.5319 | 538.7523
3539.0354 | 550.5143 | 544.8332 | 539.1898
3540.0354 | 550.1602 | 544.9811 | 538.889
3541.0354 | 549.5855 | 544.1424 | 538.0299
3542.0354 | 549.1152 | 543.962 | 538.2455
3543.0354 | 548.4008 | 543.8525 | 538.2723
3544.0354 | 547.2053 | 543.857 | 538.315
3545.0354 | 546.6538 | 544.5784 | 538.8449
3546.0354 | 545.6301 | 546.4902 | 540.1581
3547.0354 | 544.853 | 545.8482 | 541.2014
3548.0354 | 544.3562 | 544.8222 | 540.955
3549.0354 | 543.723 | 544.8198 | 540.8864
3550.0354 | 543.2095 | 544.6126 | 539.9142
3551.0354 | 543.9921 | 544.79 | 539.613
3552.0354 | 544.9454 | 545.585 | 539.1153
3553.0354 | 544.9635 | 545.3711 | 538.6412
3554.0354 | 543.9605 | 543.3387 | 537.0888
3555.0354 | 543.4166 | 542.3219 | 536.4226
3556.0354 | 543.1457 | 541.1951 | 534.8881
3557.0354 | 543.351 | 540.0235 | 533.4913
3558.0354 | 543.6973 | 538.5827 | 531.8952
3559.0354 | 544.1495 | 537.1038 | 530.1485
3560.0354 | 543.673 | 536.3323 | 528.9443
3561.0354 | 544.9043 | 537.527 | 534.754
3562.0354 | 545.1967 | 537.3578 | 534.6827
3563.0354 | 545.4543 | 537.6056 | 533.6509
3564.0354 | 546.328 | 537.557 | 532.6589
3565.0354 | 546.3561 | 538.0161 | 532.2613
3566.0354 | 547.604 | 539.173 | 532.3496
3567.0354 | 548.255 | 538.5571 | 531.9043
3568.0354 | 548.1199 | 537.6446 | 531.2874
3569.0354 | 547.447 | 537.5324 | 531.2036
3570.0354 | 546.996 | 537.8889 | 531.1511
3571.0354 | 547.8557 | 538.1724 | 530.9565
3572.0354 | 547.5946 | 537.5082 | 529.7971
3573.0354 | 547.1184 | 537.8577 | 529.1278
3574.0354 | 547.8025 | 539.9759 | 529.7704
3575.0354 | 548.4941 | 540.4903 | 529.1389
3576.0354 | 550.657 | 543.7022 | 530.7147
3577.0354 | 550.2143 | 544.8753 | 532.6024
3578.0354 | 550.1102 | 546.3893 | 533.898
3579.0354 | 549.1537 | 545.2981 | 533.3901
3580.0354 | 549.0015 | 545.7147 | 533.1634
3581.0354 | 549.2536 | 546.11 | 533.7271
3582.0354 | 549.708 | 544.9402 | 534.3422
3583.0354 | 550.9216 | 544.6866 | 533.9163
3584.0354 | 551.615 | 543.4393 | 533.105
3585.0354 | 551.4174 | 542.4843 | 531.9813
3586.0354 | 551.5943 | 542.2325 | 531.9572
3587.0354 | 550.6344 | 541.2485 | 531.3521
3588.0354 | 549.3097 | 540.4387 | 530.0324
3589.0354 | 549.0947 | 540.4136 | 529.3819
3590.0354 | 549.4918 | 540.6122 | 528.8442
3591.0354 | 549.2683 | 540.4854 | 528.1378
3592.0354 | 549.3738 | 541.0562 | 527.3461
3593.0354 | 549.342 | 542.3945 | 527.863
3594.0354 | 549.0644 | 542.8955 | 528.5302
3595.0354 | 549.3557 | 543.1554 | 528.5741
3596.0354 | 549.1269 | 541.9915 | 527.7218
3597.0354 | 548.7186 | 540.7468 | 526.8179
3598.0354 | 549.2643 | 541.0422 | 526.9304
3599.0354 | 549.5507 | 541.8526 | 527.409
3600.0354 | 548.8163 | 541.1664 | 526.6501
3601.0354 | 547.8729 | 541.5163 | 526.7581
3602.0354 | 547.5446 | 543.4002 | 528.4296
3603.0354 | 545.9742 | 542.5658 | 527.8626
3604.0354 | 545.7548 | 542.6215 | 527.2487
3605.0354 | 545.5166 | 542.0505 | 526.7143
3606.0354 | 546.4531 | 541.5176 | 526.2022
3607.0354 | 547.2563 | 541.2503 | 525.856
3608.0354 | 547.2907 | 541.5164 | 525.8885
3609.0354 | 547.9694 | 542.7776 | 526.4324
3610.0354 | 547.5977 | 542.3198 | 526.0791
3611.0354 | 547.5604 | 542.0867 | 524.9511
3612.0354 | 548.6563 | 542.4407 | 524.6991
3613.0354 | 548.4751 | 540.4375 | 523.6741
3614.0354 | 548.1995 | 539.9184 | 523.2811
3615.0354 | 547.9699 | 539.905 | 523.3951
3616.0354 | 548.1523 | 541.2198 | 523.866
3617.0354 | 547.7936 | 540.9617 | 524.1811
3618.0354 | 547.7347 | 541.158 | 524.1252
3619.0354 | 547.2785 | 541.1565 | 524.5305
3620.0354 | 547.5923 | 542.241 | 524.6664
3621.0354 | 547.4346 | 542.5703 | 524.682
3622.0354 | 547.137 | 542.2194 | 524.4941
3623.0354 | 546.9425 | 542.0555 | 524.1997
3624.0354 | 546.7705 | 541.3806 | 523.3539
3625.0354 | 546.9208 | 541.0116 | 522.5444
3626.0354 | 547.3474 | 540.6775 | 521.8137
3627.0354 | 547.8059 | 539.7577 | 521.2461
3628.0354 | 547.7973 | 539.9055 | 521.5125
3629.0354 | 546.8893 | 539.4465 | 521.5794
3630.0354 | 545.7539 | 539.6717 | 521.7829
3631.0354 | 545.3891 | 541.4688 | 523.168
3632.0354 | 545.4896 | 542.9208 | 524.7826
3633.0354 | 546.5192 | 543.5015 | 526.0725
3634.0354 | 547.1241 | 542.8818 | 525.7131
3635.0354 | 547.2877 | 542.5582 | 525.4054
3636.0354 | 547.0683 | 542.0743 | 524.9949
3637.0354 | 547.1142 | 540.5695 | 524.4302
3638.0354 | 547.3844 | 540.7629 | 523.8258
3639.0354 | 547.9854 | 542.3663 | 524.1076
3640.0354 | 548.1641 | 542.9775 | 523.4138
3641.0354 | 548.9 | 542.861 | 523.3459
3642.0354 | 550.5572 | 542.2671 | 523.0255
3643.0354 | 550.8151 | 540.7375 | 521.2882
3644.0354 | 550.5958 | 540.5723 | 520.987
3645.0354 | 550.5114 | 540.6677 | 520.9017
3646.0354 | 551.3319 | 540.3168 | 520.8272
3647.0354 | 551.5141 | 540.2088 | 520.7686
3648.0354 | 551.1271 | 540.8485 | 520.7903
3649.0354 | 550.4135 | 541.0767 | 520.9936
3650.0354 | 549.8575 | 541.8953 | 521.534
3651.0354 | 550.1308 | 541.4069 | 520.8471
3652.0354 | 550.2856 | 541.8906 | 520.5992
3653.0354 | 551.4421 | 542.8394 | 520.6325
3654.0354 | 552.2782 | 543.8077 | 521.5338
3655.0354 | 552.9492 | 544.5648 | 521.4358
3656.0354 | 552.6686 | 544.6306 | 520.9802
3657.0354 | 552.8183 | 543.4558 | 520.5585
3658.0354 | 552.4329 | 542.5267 | 519.766
3659.0354 | 553.2615 | 542.1606 | 518.8651
3660.0354 | 554.2626 | 542.6495 | 518.4865
3661.0354 | 554.8013 | 542.5884 | 517.5939
3662.0354 | 555.6347 | 541.4547 | 517.1013
3663.0354 | 556.295 | 540.5395 | 515.9693
3664.0354 | 556.0382 | 539.6078 | 515.1262
3665.0354 | 556.0644 | 540.501 | 515.8824
3666.0354 | 555.7276 | 541.0772 | 515.9595
3667.0354 | 555.7307 | 541.8627 | 516.6882
3668.0354 | 555.7638 | 542.8354 | 516.2745
3669.0354 | 555.1599 | 542.2358 | 515.7481
3670.0354 | 554.9091 | 541.9622 | 515.6049
3671.0354 | 554.8267 | 540.1903 | 514.516
3672.0354 | 554.5377 | 538.9108 | 514.1834
3673.0354 | 553.8409 | 537.713 | 514.0885
3674.0354 | 553.3958 | 535.995 | 513.1175
3675.0354 | 552.4719 | 535.3989 | 512.5926
3676.0354 | 551.7151 | 534.76 | 512.3988
3677.0354 | 550.4588 | 533.4493 | 512.0432
3678.0354 | 550.5533 | 535.158 | 512.6007
3679.0354 | 550.6099 | 535.5919 | 513.6331
3680.0354 | 550.3627 | 536.5167 | 514.3315
3681.0354 | 550.3589 | 537.9738 | 515.0381
3682.0354 | 551.1214 | 539.5324 | 515.436
3683.0354 | 552.0007 | 538.8573 | 514.6958
3684.0354 | 552.4972 | 538.4104 | 514.1991
3685.0354 | 553.0624 | 537.624 | 514.1357
3686.0354 | 552.4104 | 537.3784 | 512.9522
3687.0354 | 552.1536 | 538.5243 | 514.0663
3688.0354 | 551.4367 | 538.4797 | 513.6525
3689.0354 | 551.3482 | 538.0048 | 513.7611
3690.0354 | 551.4659 | 538.6632 | 513.9683
3691.0354 | 551.0916 | 538.4252 | 513.9765
3692.0354 | 550.8977 | 539.0448 | 514.0987
3693.0354 | 551.2328 | 539.9248 | 514.4241
3694.0354 | 553.5852 | 541.1467 | 515.2046
3695.0354 | 555.861 | 540.9338 | 515.2006
3696.0354 | 556.2913 | 541.0251 | 514.9522
3697.0354 | 555.5872 | 540.9593 | 514.3982
3698.0354 | 554.1281 | 540.1569 | 513.7486
3699.0354 | 552.8409 | 540.8381 | 515.2992
3700.0354 | 552.6817 | 542.5146 | 515.6123
3701.0354 | 552.4903 | 544.3405 | 515.7596
3702.0354 | 552.8486 | 545.606 | 516.4063
3703.0354 | 553.2381 | 545.7434 | 516.8934
3704.0354 | 553.1066 | 545.9089 | 517.3419
3705.0354 | 553.2999 | 546.2982 | 517.454
3706.0354 | 553.6042 | 546.4687 | 517.6708
3707.0354 | 554.1906 | 545.9997 | 517.6447
3708.0354 | 554.6225 | 545.7386 | 517.5141
3709.0354 | 555.6003 | 545.3495 | 517.0231
3710.0354 | 555.2704 | 544.205 | 516.7901
3711.0354 | 554.5997 | 544.2249 | 517.4279
3712.0354 | 554.8669 | 544.362 | 518.9607
3713.0354 | 553.9301 | 544.2871 | 518.9676
3714.0354 | 554.0383 | 544.9165 | 519.1299
3715.0354 | 553.9645 | 544.024 | 518.5004
3716.0354 | 553.5116 | 543.3591 | 518.1684
3717.0354 | 553.1256 | 542.3911 | 517.5165
3718.0354 | 553.0522 | 542.4432 | 517.1869
3719.0354 | 553.3341 | 542.8177 | 517.7054
3720.0354 | 553.7211 | 543.6057 | 517.5827
3721.0354 | 553.7963 | 543.1344 | 516.9975
3722.0354 | 554.0424 | 542.9208 | 517.1203
3723.0354 | 553.738 | 542.4514 | 516.5563
3724.0354 | 553.3414 | 541.9135 | 515.9439
3725.0354 | 553.7111 | 542.1524 | 515.875
3726.0354 | 555.0168 | 543.6343 | 516.8435
3727.0354 | 555.7502 | 542.8798 | 516.83
3728.0354 | 555.1451 | 541.9488 | 516.1663
3729.0354 | 554.8712 | 543.169 | 516.8423
3730.0354 | 554.887 | 542.9285 | 516.9711
3731.0354 | 555.1686 | 542.1444 | 517.0229
3732.0354 | 556.3838 | 542.8227 | 517.1981
3733.0354 | 557.3917 | 543.2645 | 517.1578
3734.0354 | 557.5211 | 543.5852 | 517.0687
3735.0354 | 557.8711 | 542.8557 | 516.7896
3736.0354 | 557.747 | 541.9812 | 516.5765
3737.0354 | 556.7965 | 541.2335 | 516.0675
3738.0354 | 556.2651 | 541.8835 | 516.1421
3739.0354 | 556.8613 | 543.5962 | 515.6726
3740.0354 | 558.051 | 544.3093 | 515.8819
3741.0354 | 558.7632 | 545.0943 | 515.3591
3742.0354 | 558.9439 | 545.0273 | 515.4397
3743.0354 | 558.1664 | 544.1636 | 514.5513
3744.0354 | 557.3031 | 542.7944 | 513.6705
3745.0354 | 557.0909 | 542.4008 | 513.4875
3746.0354 | 557.78 | 542.2094 | 512.6529
3747.0354 | 559.3081 | 543.872 | 512.4111
3748.0354 | 560.2959 | 543.0651 | 511.4306
3749.0354 | 560.4924 | 541.686 | 510.226
3750.0354 | 559.2216 | 540.1284 | 509.3875
3751.0354 | 558.6144 | 540.4734 | 509.1582
3752.0354 | 558.6419 | 541.4883 | 510.3562
3753.0354 | 557.8589 | 541.1128 | 510.446
3754.0354 | 557.0866 | 540.5874 | 510.3287
3755.0354 | 555.998 | 540.5879 | 510.7387
3756.0354 | 555.3664 | 540.4301 | 511.2434
3757.0354 | 554.8452 | 539.8051 | 510.8332
3758.0354 | 554.9542 | 539.5788 | 510.5688
3759.0354 | 554.6308 | 539.2141 | 510.5286
3760.0354 | 553.9562 | 540.0287 | 511.4318
3761.0354 | 553.5992 | 542.5679 | 512.9484
3762.0354 | 553.2274 | 543.9937 | 513.8427
3763.0354 | 553.2356 | 544.3612 | 514.1734
3764.0354 | 554.0775 | 544.0991 | 513.904
3765.0354 | 554.7256 | 543.7884 | 513.7345
3766.0354 | 554.4723 | 543.4659 | 513.2561
3767.0354 | 554.8622 | 544.5233 | 513.0674
3768.0354 | 555.1647 | 545.1723 | 512.8745
3769.0354 | 554.3425 | 543.0296 | 511.4947
3770.0354 | 554.5894 | 542.2605 | 510.7282
3771.0354 | 554.9393 | 541.8521 | 510.122
3772.0354 | 554.8539 | 541.0313 | 509.3495
3773.0354 | 553.8039 | 540.7321 | 509.4292
3774.0354 | 552.984 | 541.908 | 510.3762
3775.0354 | 552.865 | 542.177 | 510.6696
3776.0354 | 553.1992 | 540.8416 | 509.4982
3777.0354 | 554.3351 | 539.5992 | 508.7762
3778.0354 | 554.4719 | 539.0715 | 507.7911
3779.0354 | 554.3247 | 537.6334 | 507.3701
3780.0354 | 553.8201 | 536.88 | 507.0585
3781.0354 | 553.4152 | 537.0705 | 507.6551
3782.0354 | 553.1608 | 538.7386 | 508.9253
3783.0354 | 552.867 | 540.6356 | 509.6533
3784.0354 | 552.6509 | 541.0463 | 509.1435
3785.0354 | 553.1549 | 540.7711 | 508.6951
3786.0354 | 553.3175 | 540.0398 | 508.3147
3787.0354 | 553.3145 | 539.1754 | 507.4765
3788.0354 | 552.9762 | 538.5915 | 506.7604
3789.0354 | 552.7787 | 539.1775 | 507.6996
3790.0354 | 552.3381 | 538.951 | 507.3335
3791.0354 | 552.3179 | 538.1489 | 506.7337
3792.0354 | 551.6597 | 537.9841 | 506.3386
3793.0354 | 551.8445 | 538.2066 | 506.7748
3794.0354 | 552.8642 | 539.1957 | 506.2802
3795.0354 | 553.911 | 538.0901 | 505.4424
3796.0354 | 553.898 | 537.0113 | 504.5135
3797.0354 | 554.915 | 537.0887 | 503.9195
3798.0354 | 555.4246 | 536.4037 | 503.6113
3799.0354 | 555.3252 | 535.8448 | 503.3897
3800.0354 | 556.1573 | 534.9887 | 502.6707
3801.0354 | 555.891 | 533.7165 | 502.1057
3802.0354 | 555.5391 | 532.612 | 501.6499
3803.0354 | 554.9305 | 533.0955 | 501.9794
3804.0354 | 555.1144 | 534.1804 | 502.311
3805.0354 | 555.8269 | 535.4455 | 502.7555
3806.0354 | 556.6555 | 536.5661 | 503.0782
3807.0354 | 556.8627 | 537.125 | 503.1556
3808.0354 | 557.499 | 537.2116 | 503.5326
3809.0354 | 558.7377 | 536.8845 | 503.0679
3810.0354 | 558.4534 | 536.2048 | 502.5782
3811.0354 | 557.3517 | 535.1974 | 501.9835
3812.0354 | 556.803 | 534.9957 | 501.9929
3813.0354 | 556.6913 | 535.6398 | 501.8115
3814.0354 | 556.9139 | 535.2272 | 501.5296
3815.0354 | 556.7247 | 535.0973 | 501.3038
3816.0354 | 557.1571 | 535.2745 | 501.514
3817.0354 | 558.0081 | 535.5474 | 501.9633
3818.0354 | 558.8494 | 536.5822 | 501.9103
3819.0354 | 559.0265 | 537.7435 | 502.641
3820.0354 | 559.3679 | 537.755 | 502.9311
3821.0354 | 558.9547 | 538.7745 | 503.2957
3822.0354 | 558.9623 | 540.109 | 504.4239
3823.0354 | 560.3974 | 540.5854 | 504.9586
3824.0354 | 561.5724 | 540.4327 | 505.1519
3825.0354 | 561.0806 | 539.0389 | 504.6857
3826.0354 | 560.2762 | 538.4568 | 504.7917
3827.0354 | 560.4129 | 538.7573 | 505.5956
3828.0354 | 561.3593 | 538.4037 | 505.8221
3829.0354 | 561.21 | 536.4875 | 504.3763
3830.0354 | 560.9249 | 535.8288 | 503.8657
3831.0354 | 559.8229 | 536.2975 | 503.5728
3832.0354 | 559.337 | 537.6093 | 504.8119
3833.0354 | 558.7274 | 537.5532 | 504.7703
3834.0354 | 558.54 | 537.0001 | 504.7816
3835.0354 | 558.1984 | 536.4316 | 504.881
3836.0354 | 557.5125 | 537.5405 | 506.0833
3837.0354 | 557.5511 | 538.492 | 507.8579
3838.0354 | 557.3709 | 538.6879 | 509.9129
3839.0354 | 556.9617 | 539.4154 | 513.1175
3840.0354 | 556.7295 | 540.9228 | 515.9237
3841.0354 | 556.0733 | 540.434 | 518.3811
3842.0354 | 556.5141 | 540.404 | 520.7307
3843.0354 | 557.4652 | 539.7315 | 522.1439
3844.0354 | 557.2369 | 538.2321 | 524.7378
3845.0354 | 556.4431 | 537.1888 | 526.6876
3846.0354 | 557.8233 | 537.8353 | 529.4902
3847.0354 | 559.6479 | 537.9564 | 532.0656
3848.0354 | 560.9707 | 538.1677 | 535.2285
3849.0354 | 561.8187 | 538.196 | 537.3006
3850.0354 | 561.9994 | 539.2232 | 541.8946
3851.0354 | 562.6738 | 540.1634 | 547.7231
3852.0354 | 562.8884 | 541.791 | 553.5122
3853.0354 | 562.5951 | 542.195 | 560.4891
3854.0354 | 562.6503 | 542.3435 | 566.646
3855.0354 | 562.6551 | 540.9008 | 572.5764
3856.0354 | 562.0538 | 540.281 | 579.8924
3857.0354 | 560.9107 | 539.8155 | 585.2619
3858.0354 | 560.6738 | 540.1923 | 593.5266
3859.0354 | 560.5962 | 539.9612 | 600.9217
3860.0354 | 560.5673 | 540.4261 | 607.4614
3861.0354 | 559.7545 | 539.6304 | 612.0852
3862.0354 | 559.6273 | 539.7012 | 618.3417
3863.0354 | 560.2153 | 540.2524 | 624.3541
3864.0354 | 561.0647 | 541.0871 | 629.6275
3865.0354 | 560.482 | 539.9898 | 633.1278
3866.0354 | 559.6913 | 539.6784 | 636.299
3867.0354 | 559.8439 | 540.9598 | 636.5085
3868.0354 | 560.0264 | 543.1858 | 639.789
3869.0354 | 560.3658 | 543.5485 | 645.0839
3870.0354 | 561.4635 | 543.9933 | 649.3449
3871.0354 | 561.2949 | 543.4291 | 652.3008
3872.0354 | 560.4617 | 543.3436 | 654.9162
3873.0354 | 560.829 | 544.4347 | 655.0811
3874.0354 | 561.1422 | 544.5628 | 651.2302
3875.0354 | 560.545 | 543.9577 | 650.7104
3876.0354 | 560.85 | 543.8501 | 648.2439
3877.0354 | 561.4461 | 543.8322 | 642.4883
3878.0354 | 561.2455 | 542.9459 | 635.4993
3879.0354 | 560.5327 | 542.1006 | 626.3547
3880.0354 | 559.2166 | 541.1206 | 621.4967
3881.0354 | 559.121 | 541.5921 | 608.2421
3882.0354 | 558.9274 | 543.0767 | 598.0197
3883.0354 | 559.3954 | 545.1749 | 587.3699
3884.0354 | 559.9403 | 545.4798 | 582.3598
3885.0354 | 560.658 | 545.4432 | 578.5064
3886.0354 | 561.0017 | 545.314 | 576.675
3887.0354 | 561.7377 | 545.3866 | 576.4365
3888.0354 | 562.8964 | 545.761 | 577.1734
3889.0354 | 562.7399 | 546.3959 | 577.2472
3890.0354 | 561.4279 | 546.3969 | 578.0737
3891.0354 | 560.0838 | 546.3081 | 577.3504
3892.0354 | 558.8784 | 546.3533 | 577.868
3893.0354 | 558.4153 | 546.4438 | 578.8872
3894.0354 | 558.1237 | 547.6473 | 581.7136
3895.0354 | 558.7268 | 548.1568 | 581.6936
3896.0354 | 559.0148 | 547.6556 | 582.1642
3897.0354 | 559.835 | 547.0965 | 581.8056
3898.0354 | 560.3301 | 547.4834 | 583.4099
3899.0354 | 562.0137 | 551.7378 | 585.1583
3900.0354 | 562.9599 | 555.3925 | 586.6809
3901.0354 | 563.3071 | 554.1032 | 587.4625
3902.0354 | 562.725 | 552.624 | 588.7728
3903.0354 | 562.2215 | 551.2274 | 587.831
3904.0354 | 561.485 | 551.2114 | 588.3029
3905.0354 | 560.8264 | 550.4632 | 585.7297
3906.0354 | 560.6455 | 550.0194 | 587.1695
3907.0354 | 560.9927 | 548.3522 | 587.6778
3908.0354 | 561.1063 | 546.8457 | 588.2261
3909.0354 | 560.807 | 545.7096 | 589.2147
3910.0354 | 560.7347 | 545.3152 | 591.471
3911.0354 | 559.7438 | 543.8636 | 591.3589
3912.0354 | 559.6765 | 542.4596 | 591.4665
3913.0354 | 560.1638 | 541.8289 | 592.4526
3914.0354 | 559.207 | 541.2339 | 594.7773
3915.0354 | 559.0014 | 541.1109 | 595.5902
3916.0354 | 559.6176 | 542.1493 | 595.4909
3917.051 | 559.6541 | 543.1206 | 595.8991
3918.0354 | 559.5704 | 542.9842 | 595.4259
3919.0354 | 559.4042 | 542.4478 | 597.0481
3920.0354 | 559.0262 | 542.4414 | 597.2583
3921.0354 | 559.6514 | 542.1336 | 598.3994
3922.0354 | 559.5942 | 541.4045 | 598.6448
3923.0354 | 560.4954 | 542.8294 | 598.9905
3924.0354 | 561.4947 | 544.5592 | 599.8073
3925.0354 | 561.7903 | 544.5003 | 600.1631
3926.0354 | 561.8819 | 544.2036 | 601.2284
3927.0354 | 563.5246 | 543.5167 | 600.5458
3928.0354 | 563.7214 | 543.9597 | 602.0761
3929.0354 | 563.5263 | 543.3428 | 602.7762
3930.0354 | 563.4652 | 541.9097 | 604.335
3931.0354 | 562.9087 | 540.297 | 604.8968
3932.0354 | 562.5369 | 539.4233 | 604.9873
3933.0354 | 562.6429 | 539.6261 | 605.7101
3934.0354 | 563.0436 | 540.3875 | 606.3503
3935.0354 | 563.4395 | 540.3298 | 606.2248
3936.0354 | 563.6386 | 539.385 | 607.3259
3937.0354 | 563.6508 | 538.9817 | 608.0204
3938.0354 | 562.6305 | 538.5524 | 607.942
3939.0198 | 563.2538 | 538.1276 | 608.0856
3940.0354 | 562.6446 | 536.8935 | 608.1171
3941.0354 | 561.6241 | 536.3929 | 610.2505
3942.0354 | 561.2733 | 536.7101 | 611.5181
3943.0354 | 560.7243 | 536.4807 | 610.299
3944.0354 | 559.3837 | 536.743 | 611.5927
3945.0354 | 558.747 | 540.3343 | 611.6278
3946.0354 | 560.7506 | 543.1924 | 607.2625
3947.0354 | 560.3932 | 543.2937 | 610.1138
3948.0354 | 560.9537 | 542.8412 | 609.7905
3949.0354 | 562.5555 | 542.7401 | 609.4574
3950.0354 | 562.795 | 541.4396 | 609.7547
3951.0354 | 562.2103 | 539.7783 | 607.536
3952.0354 | 561.5286 | 538.0941 | 606.4127
3953.0354 | 561.5132 | 536.1875 | 605.3935
3954.0354 | 560.8219 | 535.9149 | 603.7054
3955.0354 | 560.3217 | 536.5918 | 601.8866
3956.0354 | 560.5992 | 540.3004 | 597.0014
3957.0354 | 562.2635 | 542.153 | 599.7248
3958.0354 | 562.3457 | 541.3507 | 602.2885
3959.0354 | 561.3798 | 540.9088 | 603.3653
3960.0354 | 561.2599 | 539.8296 | 602.7528
3961.0354 | 561.46 | 539.549 | 601.1364
3962.0354 | 562.7302 | 539.9062 | 599.9955
3963.0354 | 562.0965 | 539.6358 | 597.5648
3964.0354 | 562.0982 | 540.35 | 593.4678
3965.0354 | 563.89 | 544.8482 | 591.9959
3966.0354 | 564.5801 | 544.9263 | 589.409
3967.0354 | 564.9037 | 543.2849 | 586.2758
3968.0354 | 565.478 | 541.9768 | 582.8778
3969.0354 | 565.1277 | 540.2741 | 581.5909
3970.0354 | 565.0057 | 539.4465 | 580.0351
3971.0354 | 565.0402 | 539.3446 | 579.3215
3972.0354 | 564.5225 | 539.5436 | 577.4679
3973.0354 | 563.9725 | 540.2121 | 577.1071
3974.0354 | 563.8893 | 539.5007 | 575.3668
3975.0354 | 563.527 | 538.4809 | 575.5917
3976.0354 | 562.6665 | 537.086 | 574.0756
3977.0354 | 562.0072 | 537.3504 | 573.4349
3978.0354 | 562.2706 | 537.4353 | 573.2879
3979.0354 | 562.769 | 536.5971 | 570.9932
3980.0354 | 562.4347 | 535.4768 | 568.1566
3981.0354 | 562.667 | 536.3811 | 564.2834
3982.0354 | 563.278 | 536.1394 | 562.5611
3983.0354 | 563.4583 | 536.9979 | 562.4376
3984.0354 | 564.1502 | 537.1247 | 562.4884
3985.0354 | 564.5398 | 536.3968 | 563.1618
3986.0354 | 564.8328 | 536.2751 | 563.2975
3987.0354 | 566.5284 | 536.8674 | 562.734
3988.0354 | 565.9459 | 535.2295 | 563.2717
3989.0354 | 565.0539 | 534.8509 | 563.5039
3990.0354 | 564.6899 | 535.7234 | 564.5627
3991.0354 | 563.8202 | 535.1744 | 564.0846
3992.0354 | 563.8444 | 535.4042 | 563.1234
3993.0354 | 563.3182 | 535.3455 | 562.3778
3994.0354 | 563.5166 | 536.7653 | 562.596
3995.0354 | 565.6773 | 538.0919 | 563.1767
3996.0354 | 566.6925 | 538.4333 | 562.5858
3997.0354 | 566.6988 | 540.2391 | 563.9077
3998.0354 | 566.0036 | 539.7898 | 563.5259
3999.0354 | 565.1331 | 539.7892 | 563.9492
4000.0354 | 564.8533 | 540.145 | 563.9716
4001.0354 | 564.6896 | 541.7026 | 563.4629
4002.0198 | 564.524 | 542.6809 | 564.9488
4003.0354 | 565.3861 | 542.9273 | 564.5798
4004.0354 | 565.8774 | 540.6791 | 564.6986
4005.0354 | 565.9736 | 539.7895 | 565.5847
4006.0354 | 566.4607 | 540.0869 | 566.1677
4007.0354 | 566.0274 | 539.7397 | 567.0496
4008.0354 | 566.196 | 539.8562 | 567.2399
4009.0354 | 565.7008 | 539.8467 | 569.3655
4010.0354 | 565.2611 | 540.4953 | 570.7798
4011.0354 | 564.8637 | 540.3714 | 570.3967
4012.0354 | 564.3183 | 540.694 | 571.1559
4013.0354 | 564.7916 | 540.5119 | 571.968
4014.0354 | 565.9217 | 540.5248 | 571.7755
4015.0354 | 565.498 | 539.4987 | 569.5475
4016.0354 | 564.3925 | 540.3832 | 568.6153
4017.0354 | 562.8645 | 540.3393 | 567.4076
4018.0354 | 562.7894 | 541.3564 | 567.6232
4019.0354 | 562.4561 | 540.6961 | 567.8166
4020.0354 | 562.3038 | 540.6515 | 566.6699
4021.0354 | 562.3582 | 541.3199 | 564.9315
4022.0354 | 562.6304 | 540.5728 | 565.1862
4023.0354 | 563.734 | 539.5177 | 564.3441
4024.0354 | 564.3615 | 539.2394 | 564.9826
4025.0354 | 565.4558 | 541.8779 | 564.2917
4026.0354 | 566.8135 | 542.7624 | 563.7007
4027.0354 | 567.635 | 541.7917 | 562.9646
4028.0354 | 568.1611 | 541.0093 | 562.432
4029.0354 | 569.0725 | 540.3626 | 561.73
4030.0354 | 569.8267 | 539.7907 | 561.8109
4031.0354 | 570.0744 | 539.006 | 561.7464
4032.0354 | 569.7293 | 539.124 | 561.0576
4033.0354 | 569.8486 | 539.8751 | 560.0918
4034.0354 | 572.3106 | 540.703 | 560.6709
4035.0354 | 574.0846 | 544.0125 | 560.49
4036.0354 | 573.9158 | 542.3203 | 557.7944
4037.0354 | 573.0108 | 539.9748 | 557.5639
4038.0354 | 572.4915 | 538.9358 | 556.638
4039.0354 | 571.1264 | 538.1304 | 556.5439
4040.0354 | 572.2548 | 538.8026 | 555.9083
4041.0354 | 573.1897 | 537.7036 | 555.7559
4042.0354 | 572.766 | 536.0107 | 555.6885
4043.0354 | 573.739 | 535.1836 | 555.814
4044.0354 | 574.2369 | 533.6029 | 555.4829
4045.0354 | 573.657 | 532.6847 | 554.9125
4046.0354 | 573.0788 | 531.8223 | 555.1875
4047.0354 | 571.8954 | 531.39 | 556.5877
4048.0354 | 573.4042 | 530.502 | 556.1845
4049.0354 | 575.2245 | 530.4935 | 555.6091
4050.0354 | 578.5698 | 530.5975 | 556.0995
4051.0354 | 577.801 | 529.2037 | 553.8221
4052.0354 | 576.6893 | 528.7228 | 552.9998
4053.0354 | 577.6076 | 529.1647 | 553.3687
4054.0354 | 579.0446 | 529.4019 | 554.6532
4055.0354 | 579.1046 | 529.7228 | 554.7677
4056.0354 | 577.7277 | 528.9263 | 554.8441
4057.0354 | 577.0094 | 528.9233 | 555.9839
4058.0354 | 575.5998 | 528.9069 | 556.7921
4059.0354 | 574.8745 | 530.1169 | 556.8224
4060.0354 | 574.1498 | 531.2226 | 558.762
4061.0354 | 576.8067 | 532.3404 | 550.2697
4062.0354 | 575.5411 | 531.8539 | 558.9177
4063.0354 | 575.1369 | 531.1039 | 559.1025
4064.0354 | 574.8509 | 531.2381 | 560.1319
4065.0354 | 575.5366 | 531.0336 | 559.9477
4066.0354 | 575.0693 | 530.1329 | 560.3726
4067.0354 | 574.3424 | 528.2149 | 560.0099
4068.0354 | 573.1906 | 527.2868 | 559.198
4069.0354 | 572.6667 | 528.3353 | 559.5505
4070.0354 | 572.9565 | 529.185 | 559.8024
4071.0354 | 572.8006 | 528.7583 | 559.5725
4072.0354 | 572.2274 | 528.0685 | 558.6584
4073.0354 | 571.3862 | 528.1052 | 559.6034
4074.0354 | 571.1369 | 528.1927 | 558.9529
4075.0354 | 570.5611 | 528.7534 | 559.3504
4076.0354 | 569.962 | 528.5974 | 559.4637
4077.0354 | 569.4235 | 528.5889 | 559.2382
4078.0354 | 569.8386 | 528.4078 | 559.177
4079.0354 | 570.0305 | 528.9598 | 558.7313
4080.0354 | 570.8555 | 530.9821 | 559.3448
4081.0354 | 569.6068 | 532.8805 | 560.0674
4082.0354 | 569.1359 | 532.325 | 560.0939
4083.0354 | 568.1645 | 531.6544 | 560.1514
4084.0354 | 567.9544 | 533.6369 | 561.1124
4085.0354 | 565.844 | 535.4128 | 562.1504
4086.0354 | 566.7779 | 537.7642 | 562.9213
4087.0354 | 566.1335 | 538.6529 | 563.3175
4088.0354 | 566.4451 | 539.4449 | 563.8149
4089.0354 | 566.0481 | 537.978 | 562.7056
4090.0354 | 566.0225 | 537.1474 | 562.7849
4091.0354 | 565.6744 | 536.0367 | 561.8686
4092.0354 | 564.4211 | 535.6183 | 561.5334
4093.0354 | 564.0192 | 537.0267 | 562.2032
4094.0354 | 563.486 | 537.8224 | 562.548
4095.0354 | 563.0407 | 539.3483 | 562.4647
4096.0354 | 562.8996 | 538.589 | 562.5487
4097.0354 | 562.5633 | 538.1985 | 561.3999
4098.0354 | 561.8833 | 538.7812 | 561.4412
4099.0354 | 561.5014 | 539.6581 | 561.8252
4100.0354 | 560.1848 | 540.1802 | 562.4319
4101.0354 | 561.059 | 540.2403 | 561.2065
4102.0354 | 561.992 | 539.3245 | 559.5972
4103.0354 | 562.3709 | 536.9748 | 558.004
4104.0354 | 561.9149 | 535.1483 | 556.8105
4105.0354 | 561.9532 | 533.4424 | 555.1266
4106.0354 | 562.135 | 533.0716 | 554.1943
4107.0354 | 561.6862 | 532.9468 | 554.2841
4108.0354 | 562.0865 | 532.2595 | 555.7494
4109.0354 | 563.4042 | 532.1213 | 555.8261
4110.0354 | 563.6775 | 531.7329 | 554.3016
4111.0354 | 565.8236 | 532.6836 | 552.5341
4112.0354 | 566.0653 | 531.9851 | 552.6745
4113.0354 | 567.7345 | 533.1242 | 551.2519
4114.0354 | 567.7619 | 532.7839 | 550.0732
4115.0354 | 567.2572 | 531.9707 | 548.8376
4116.0354 | 566.7535 | 530.8783 | 547.8916
4117.0354 | 566.9115 | 531.2973 | 547.4082
4118.0354 | 566.4141 | 531.3908 | 547.0349
4119.0354 | 566.2377 | 531.3327 | 546.6695
4120.0354 | 566.0507 | 530.6782 | 546.6953
4121.0354 | 565.9656 | 529.7404 | 546.4322
4122.0354 | 566.7213 | 529.6994 | 545.8492
4123.0354 | 567.9985 | 529.4661 | 545.5548
4124.0354 | 568.7006 | 529.1745 | 544.6158
4125.0354 | 568.7727 | 528.9963 | 543.5518
4126.0354 | 568.4824 | 527.6101 | 541.8912
4127.0354 | 568.4865 | 526.7799 | 540.4392
4128.0354 | 568.7225 | 527.443 | 538.9073
4129.0354 | 568.7736 | 528.5226 | 538.7639
4130.0354 | 569.0496 | 529.5612 | 538.7868
4131.0354 | 568.8693 | 529.476 | 538.5287
4132.0354 | 568.2868 | 529.0886 | 537.327
4133.0354 | 568.3755 | 530.0963 | 537.3353
4134.0354 | 567.317 | 530.3876 | 538.2912
4135.0354 | 566.2957 | 530.7891 | 539.1692
4136.0354 | 566.2522 | 531.0635 | 539.9071
4137.0354 | 565.5079 | 530.8237 | 540.5564
4138.0354 | 565.8458 | 531.0091 | 540.9404
4139.0354 | 565.8295 | 532.1639 | 540.4773
4140.0354 | 566.6338 | 533.0489 | 539.5262
4141.0354 | 567.7969 | 532.9379 | 539.4481
4142.0354 | 567.7617 | 531.4086 | 538.7366
4143.0354 | 567.6247 | 530.3657 | 538.415
4144.0354 | 567.387 | 529.7919 | 538.9815
4145.0354 | 567.246 | 530.7603 | 539.5198
4146.0354 | 567.8602 | 531.5858 | 539.6474
4147.0354 | 567.3267 | 531.4955 | 538.9758
4148.0354 | 566.8255 | 530.6529 | 537.9483
4149.0354 | 567.0605 | 530.4109 | 537.1014
4150.0354 | 566.8379 | 530.1749 | 536.1218
4151.0354 | 566.6645 | 529.0578 | 535.2796
4152.0354 | 566.9054 | 529.5008 | 534.208
4153.0354 | 566.9133 | 529.8979 | 534.091
4154.0354 | 567.5117 | 530.8796 | 533.9882
4155.0354 | 567.3781 | 532.583 | 534.111
4156.0354 | 568.0736 | 533.2844 | 534.1005
4157.0354 | 567.5439 | 532.7041 | 533.5204
4158.0354 | 567.5191 | 531.5093 | 532.6193
4159.0354 | 566.4778 | 531.5231 | 532.6785
4160.0354 | 565.6967 | 534.0457 | 533.6444
4161.0354 | 565.8888 | 533.3525 | 532.8975
4162.0354 | 566.2335 | 533.2499 | 532.401
4163.0354 | 566.0933 | 532.9405 | 531.4435
4164.0354 | 565.6679 | 532.2143 | 531.0011
4165.0354 | 565.7121 | 533.293 | 530.7649
4166.0354 | 566.4864 | 533.9756 | 530.6771
4167.0354 | 567.4422 | 534.5274 | 530.8227
4168.0354 | 567.5874 | 533.4035 | 530.2794
4169.0354 | 567.4535 | 532.5778 | 529.6287
4170.0354 | 568.1132 | 531.9841 | 528.7324
4171.0354 | 568.177 | 530.8903 | 528.096
4172.0354 | 568.5319 | 530.7014 | 528.8422
4173.0354 | 568.9801 | 530.5975 | 528.6351
4174.0354 | 569.3824 | 532.8271 | 529.2788
4175.0354 | 571.2016 | 536.3519 | 529.936
4176.0354 | 570.3744 | 535.9442 | 529.131
4177.0354 | 570.1402 | 537.9494 | 528.6094
4178.0354 | 570.5151 | 537.4853 | 528.6105
4179.0354 | 571.3883 | 537.6473 | 527.9012
4180.0354 | 570.7683 | 536.2472 | 526.5753
4181.0354 | 569.7191 | 535.0825 | 525.618
4182.0354 | 568.3943 | 534.1962 | 525.5941
4183.0354 | 568.0387 | 533.4986 | 525.9127
4184.0354 | 568.1065 | 532.8579 | 525.0448
4185.0354 | 567.2001 | 530.9029 | 523.5638
4186.0354 | 566.6476 | 530.0498 | 523.4412
4187.0354 | 565.8561 | 528.197 | 522.3543
4188.0354 | 565.47 | 527.5742 | 522.4149
4189.0354 | 564.488 | 526.8117 | 521.8941
4190.0354 | 563.9321 | 527.1083 | 522.175
4191.0354 | 563.296 | 528.4017 | 521.862
4192.0354 | 563.6603 | 528.8826 | 521.0018
4193.0354 | 563.9244 | 528.5607 | 521.0644
4194.0354 | 563.8773 | 528.9178 | 521.3
4195.0354 | 564.8312 | 529.6339 | 521.1793
4196.0354 | 564.7166 | 529.1587 | 521.2804
4197.0354 | 565.6517 | 529.5979 | 521.9969
4198.0354 | 566.5396 | 529.559 | 522.1148
4199.0354 | 567.4458 | 528.9663 | 522.0712
4200.0354 | 566.4364 | 528.6729 | 520.9807
4201.0354 | 566.4141 | 529.1906 | 521.624
4202.0354 | 566.8993 | 529.7775 | 521.0981
4203.0354 | 567.6099 | 531.2755 | 520.3742
4204.0354 | 568.1895 | 532.3722 | 520.6462
4205.0354 | 568.2833 | 532.8485 | 520.2317
4206.0354 | 568.0182 | 532.7757 | 519.7985
4207.0354 | 568.3797 | 533.7591 | 521.1917
4208.0354 | 568.5105 | 534.0289 | 522.6858
4209.0354 | 568.8432 | 535.4613 | 522.8412
4210.0354 | 568.8728 | 536.2045 | 522.8409
4211.0354 | 568.883 | 535.3753 | 522.4784
4212.0354 | 567.7071 | 534.162 | 520.7761
4213.0354 | 566.1997 | 531.9595 | 518.8747
4214.0354 | 564.5881 | 530.222 | 518.1538
4215.0354 | 564.2467 | 529.5172 | 517.6499
4216.0667 | 564.6999 | 530.8657 | 518.5001
4217.0354 | 565.4096 | 534.0326 | 519.416
4218.0354 | 566.4095 | 535.937 | 519.5419
4219.0354 | 567.4065 | 535.1157 | 519.3133
4220.0354 | 566.1432 | 533.2222 | 518.7209
4221.0354 | 565.4984 | 532.7627 | 518.786
4222.0354 | 564.8695 | 533.4785 | 518.9121
4223.0354 | 564.41 | 533.6018 | 518.9351
4224.0354 | 565.5135 | 534.1118 | 519.0509
4225.0354 | 566.692 | 534.2824 | 518.3932
4226.0354 | 567.1626 | 534.5393 | 518.9729
4227.0354 | 566.7518 | 533.2377 | 518.1777
4228.0354 | 566.5879 | 533.7524 | 518.3801
4229.0354 | 567.3612 | 535.1022 | 518.5259
4230.0354 | 566.8131 | 534.0884 | 518.4748
4231.0354 | 566.1614 | 532.5597 | 517.608
4232.0354 | 566.6015 | 531.9319 | 517.3318
4233.0354 | 566.3983 | 531.1663 | 517.7939
4234.0354 | 566.7038 | 530.9792 | 517.3845
4235.0354 | 567.0749 | 530.0237 | 516.9976
4236.0354 | 566.869 | 528.7335 | 517.2658
4237.0354 | 566.7188 | 529.2454 | 516.5427
4238.0354 | 566.6493 | 529.6909 | 516.4293
4239.0354 | 565.7918 | 529.0072 | 520.0935
4240.0354 | 565.3108 | 529.0455 | 521.7249
4241.0354 | 564.025 | 529.1574 | 525.0138
4242.0354 | 562.9642 | 529.2201 | 524.9264
4243.0354 | 562.9869 | 530.3102 | 523.0518
4244.0354 | 564.6778 | 530.7804 | 524.0899
4245.0354 | 564.866 | 529.6921 | 524.5197
4246.0354 | 564.6294 | 529.1178 | 525.1361
4247.0354 | 563.7302 | 529.3937 | 525.5382
4248.0354 | 562.2506 | 528.869 | 525.0516
4249.0354 | 561.1595 | 528.5771 | 525.7168
4250.0354 | 560.1632 | 527.5592 | 524.999
4251.0354 | 559.3475 | 526.8387 | 526.9334
4252.0354 | 558.5787 | 526.1562 | 525.109
4253.0354 | 557.2243 | 525.3342 | 532.9505
4254.0354 | 556.4996 | 525.1577 | 531.6579
4255.0354 | 556.2299 | 525.4538 | 535.8128
4256.0354 | 555.6896 | 524.7537 | 537.4956
4257.0354 | 555.3686 | 524.4617 | 538.483
4258.0354 | 555.9298 | 524.1676 | 538.7833
4259.0354 | 557.1911 | 525.4902 | 539.5005
4260.0354 | 557.3015 | 526.1346 | 532.4606
4261.0354 | 556.5533 | 526.1366 | 528.6023
4262.0354 | 556.6701 | 527.6409 | 530.4443
4263.0354 | 556.2295 | 528.8432 | 530.5889
4264.0354 | 556.0975 | 529.915 | 531.7076
4265.0354 | 556.0607 | 530.224 | 532.0368
4266.0354 | 555.7996 | 531.1619 | 532.6414
4267.0354 | 554.9582 | 532.1034 | 533.7857
4268.0354 | 555.1771 | 533.3366 | 533.7856
4269.0354 | 555.14 | 533.752 | 532.8799
4270.0354 | 554.5803 | 532.0936 | 532.0442
4271.0354 | 553.5065 | 531.0221 | 532.232
4272.0354 | 552.958 | 529.7433 | 532.0927
4273.0354 | 554.2422 | 528.9363 | 532.6274
4274.0354 | 553.0609 | 527.1431 | 533.9193
4275.0354 | 551.9675 | 526.4723 | 534.8233
4276.0354 | 552.0519 | 526.3129 | 534.6227
4277.0354 | 551.8282 | 525.8813 | 533.176
4278.0354 | 551.8837 | 526.2861 | 533.8602
4279.0354 | 551.5595 | 525.4359 | 533.912
4280.0354 | 551.7904 | 525.5215 | 532.7898
4281.0354 | 552.1612 | 525.7285 | 532.996
4282.0354 | 551.7425 | 526.5411 | 534.5205
4283.0354 | 551.7533 | 526.3996 | 534.8915
4284.0354 | 551.1326 | 526.5777 | 534.7887
4285.0354 | 551.1521 | 527.8627 | 535.026
4286.0354 | 551.8203 | 528.6913 | 533.6779
4287.0354 | 551.8844 | 528.5671 | 533.0205
4288.0354 | 551.4243 | 527.7929 | 533.2033
4289.0354 | 551.3956 | 527.7253 | 534.2715
4290.0354 | 552.1474 | 526.8337 | 534.7964
4291.0354 | 552.0326 | 526.6094 | 536.199
4292.0354 | 551.4039 | 525.6926 | 538.3234
4293.0354 | 551.3063 | 525.7356 | 539.3804
4294.0354 | 552.0177 | 526.0767 | 540.5931
4295.0354 | 551.8443 | 525.2509 | 539.6837
4296.0354 | 551.7347 | 525.6059 | 540.2262
4297.0354 | 551.1829 | 525.5837 | 540.5196
4298.0354 | 551.1497 | 526.4196 | 539.7074
4299.0354 | 551.7764 | 526.9614 | 538.7804
4300.0354 | 552.2696 | 526.8562 | 538.8939
4301.0354 | 552.0088 | 526.9753 | 538.8165
4302.0354 | 551.9056 | 527.7506 | 537.9944
4303.0354 | 552.9822 | 527.8169 | 537.5404
4304.0354 | 553.2657 | 527.3065 | 536.0623
4305.0354 | 553.5256 | 528.3027 | 535.3882
4306.0354 | 553.8392 | 529.0018 | 535.346
4307.0354 | 553.37 | 528.3459 | 533.8784
4308.0354 | 552.6549 | 528.62 | 532.3517
4309.0354 | 552.4881 | 530.5166 | 532.3067
4310.0354 | 551.8296 | 531.4754 | 530.9117
4311.0354 | 551.1142 | 531.1719 | 529.4417
4312.0354 | 550.0993 | 530.2642 | 526.6555
4313.0354 | 549.3781 | 530.1514 | 524.7423
4314.0354 | 549.3889 | 530.7272 | 521.9413
4315.0354 | 549.7698 | 532.144 | 522.9425
4316.0354 | 550.2654 | 531.8735 | 518.2809
4317.0354 | 550.1526 | 530.0819 | 515.4335
4318.0354 | 549.2177 | 528.9078 | 513.281
4319.0354 | 548.2754 | 529.3183 | 512.6046
4320.0354 | 547.2796 | 528.7275 | 511.5016
4321.0354 | 547.2622 | 529.291 | 510.0678
4322.0354 | 548.144 | 530.1992 | 508.9211
4323.0354 | 550.0535 | 530.4189 | 508.0212
4324.0354 | 550.5293 | 529.0016 | 507.2477
4325.0354 | 550.2879 | 527.604 | 506.5084
4326.0354 | 549.8278 | 528.2844 | 507.2598
4327.0354 | 549.3377 | 528.3354 | 508.2983
4328.0354 | 548.776 | 528.9157 | 507.9583
4329.0354 | 548.9914 | 528.6026 | 507.6216
4330.0354 | 549.3017 | 529.0196 | 508.229
4331.0354 | 550.0118 | 528.27 | 507.8828
4332.0354 | 549.9131 | 527.1949 | 505.3307
4333.0354 | 550.096 | 526.8059 | 504.9386
4334.0354 | 549.6259 | 527.3882 | 505.1141
4335.0354 | 550.7111 | 529.5017 | 504.9192
4336.0354 | 551.0231 | 529.9305 | 505.9063
4337.0354 | 551.5109 | 529.7184 | 504.0923
4338.0354 | 552.288 | 528.9598 | 502.8994
4339.0354 | 552.6015 | 528.9003 | 504.3568
4340.0354 | 552.9981 | 529.4267 | 505.7542
4341.0354 | 553.4721 | 529.9271 | 507.3176
4342.0354 | 554.2722 | 530.9532 | 508.1082
4343.0354 | 555.0688 | 531.4827 | 508.2893
4344.0354 | 555.0129 | 530.3939 | 507.3585
4345.0354 | 554.4564 | 529.1781 | 506.4568
4346.0354 | 554.4678 | 530.0063 | 506.8025
4347.0354 | 554.5702 | 529.6674 | 506.7827
4348.0354 | 555.0635 | 529.612 | 506.6727
4349.0354 | 555.2932 | 529.6597 | 506.0053
4350.0354 | 555.0719 | 529.1181 | 505.8601
4351.0354 | 555.3895 | 529.4013 | 505.613
4352.0354 | 555.269 | 530.6874 | 504.9567
4353.0354 | 555.3682 | 531.9206 | 504.6422
4354.0354 | 555.6405 | 532.2669 | 504.2255
4355.0354 | 555.4182 | 531.9871 | 503.4973
4356.0354 | 554.6762 | 531.3669 | 502.7003
4357.0354 | 553.821 | 531.4301 | 502.7116
4358.0354 | 553.7848 | 531.6516 | 502.41
4359.0354 | 553.9886 | 530.2693 | 501.2029
4360.0354 | 553.6199 | 529.3179 | 500.2034
4361.0354 | 552.7554 | 528.1147 | 499.4427
4362.0354 | 552.9963 | 528.454 | 500.2453
4363.0354 | 554.33 | 529.604 | 501.8122
4364.0354 | 554.3571 | 528.7143 | 501.9543
4365.0354 | 554.996 | 529.5871 | 501.3964
4366.0354 | 554.8296 | 528.3214 | 500.5738
4367.0354 | 554.4014 | 527.2797 | 500.0679
4368.0354 | 554.1033 | 527.5353 | 499.8692
4369.0354 | 553.8896 | 528.8229 | 500.3138
4370.0354 | 553.5163 | 529.6318 | 500.7374
4371.0354 | 554.4635 | 530.524 | 501.7566
4372.0354 | 554.0268 | 530.3884 | 501.9651
4373.0354 | 553.9952 | 530.4134 | 501.5855
4374.0354 | 553.6885 | 529.1415 | 499.8132
4375.0354 | 554.0449 | 528.4225 | 498.7162
4376.0354 | 554.4473 | 529.0188 | 498.1253
4377.0354 | 553.8826 | 528.262 | 497.4674
4378.0354 | 553.8918 | 528.4082 | 497.3372
4379.0354 | 553.9293 | 527.3952 | 496.4052
4380.0354 | 553.6099 | 527.7648 | 496.2142