## Test Conditions
DESIREE-FIRE Intermediate Scale Test 1 - Circuit Data Only
Test Date: | 2010-02-23
DCSim DAQ Start Time | 12:09
DCSim Time for Synchronization | 13:03
Heat Source Synchronization | 0:02 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:01
Fire Time | 13:56
Offset | 1:47 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 6420 | seconds
Heat Source Offset | 0:55 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3299 | seconds
Heat Source Stop Time | 15:09
Test Duration | 1:13 | hours:minutes:seconds
| 4380 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Tray - Middle" in the temperature data file.
Large Coil | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Tray - Middle" in the temperature data file.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-1.2188 | 123.3078 | -61.6653 | 61.4685 | -0.0022127 | -0.036243 | 0.11252 | 0.025656 | 0.052869 | -0.020322 | -0.019933 | -0.0079343 | -0.0026511 | 0.041321 | 0.059853 | -0.015518 | -0.01254 | 61.5372 | -61.5509 | -0.018311 | -61.734 | 61.4456 | -61.6882 | -61.6608 | -62.0682 | -0.022888 | -62.0316 | 61.377 | 61.4548 | -61.5601 | -61.7477 | -0.022888 | 0.004577 | -0.022888 | 0.11444 | -0.068665 | -0.073242 | 0.068664 | 0.10528 | -0.082398 | -0.091553 | -0.40283 | -0.36621 | -0.28381 | -0.013733 | 123.111 | 123.2025 | 61.647 | -123.1293 | 123.0423 | 123.1201 | 61.6425 | -123.2162
0.53125 | 123.2941 | -61.6425 | 61.5738 | -0.0022127 | -0.03368 | 0.11466 | 0.029929 | 0.054792 | -0.026517 | -0.022283 | 0.0073242 | -0.0050009 | 0.041962 | 0.059853 | -0.020645 | -0.014249 | 61.6562 | -61.3632 | 0.17853 | -61.5921 | 61.4685 | -61.6058 | -61.528 | -61.9217 | 0.16479 | -61.821 | 61.409 | 61.496 | -61.4456 | -61.6608 | 0.036621 | 0.11444 | -0.10529 | 0.27924 | 0.050354 | -0.064087 | 0.082397 | 0.19684 | -0.018311 | -0.16479 | -0.27924 | -0.17853 | -0.16022 | -0.07782 | 123.111 | 123.2986 | 61.821 | -123.1018 | 123.0515 | 123.1384 | 61.8073 | -123.2346
2.2188 | 123.3902 | -61.647 | 61.4868 | 0.013046 | -0.035816 | 0.11445 | 0.023306 | 0.052869 | -0.025235 | -0.02271 | -0.0003053 | -0.0069235 | 0.041535 | 0.060494 | -0.01744 | -0.014462 | 61.615 | -61.4365 | 0.059509 | -61.6608 | 61.4044 | -61.7065 | -61.5875 | -61.9446 | 0.064087 | -61.8759 | 61.3174 | 61.3495 | -61.528 | -61.702 | -0.059509 | 0.05951 | -0.082397 | 0.21057 | -0.013733 | -0.073243 | 0.12817 | 0.11902 | -0.054931 | -0.16937 | -0.29755 | -0.22888 | -0.17395 | -0.13733 | 123.0515 | 123.262 | 61.7065 | -123.0743 | 122.9645 | 122.9965 | 61.7111 | -123.1888
3.9844 | 123.3444 | -61.6425 | 61.5143 | 0.0054168 | -0.030262 | 0.11295 | 0.026511 | 0.055219 | -0.020108 | -0.021856 | -0.0003053 | -0.0035055 | 0.04303 | 0.060067 | -0.016799 | -0.01318 | 61.6104 | -61.4639 | 0.073242 | -61.6425 | 61.5143 | -61.6791 | -61.5921 | -61.9858 | 0.091553 | -61.9263 | 61.4136 | 61.4456 | -61.5143 | -61.7432 | -0.036621 | 0.050354 | 0 | 0.17853 | 0 | -0.050354 | 0.096131 | 0.12817 | -0.10071 | -0.10071 | -0.34332 | -0.28381 | -0.18311 | -0.068664 | 123.1567 | 123.2529 | 61.7157 | -123.1064 | 123.056 | 123.0881 | 61.734 | -123.2574
5.6562 | 123.2941 | -61.615 | 61.5829 | 0.0054168 | -0.036671 | 0.11487 | 0.026297 | 0.053083 | -0.026944 | -0.023778 | 0.0073242 | -0.0069235 | 0.041535 | 0.059853 | -0.020004 | -0.013821 | 61.6791 | -61.3358 | 0.1831 | -61.5784 | 61.4685 | -61.6196 | -61.5417 | -61.9125 | 0.16479 | -61.8118 | 61.3907 | 61.4777 | -61.4456 | -61.6653 | -0.004578 | 0.073242 | -0.11444 | 0.27924 | 0.036621 | -0.036621 | 0.09613 | 0.16937 | -0.050354 | -0.19226 | -0.29755 | -0.19684 | -0.14649 | -0.10529 | 123.0835 | 123.2941 | 61.7981 | -123.1247 | 123.0057 | 123.0927 | 61.7798 | -123.2483
7.4062 | 123.4085 | -61.5967 | 61.5234 | -0.0022127 | -0.039875 | 0.11658 | 0.025656 | 0.051588 | -0.026731 | -0.02271 | 0.014954 | -0.0052145 | 0.04068 | 0.058571 | -0.018295 | -0.01318 | 61.5829 | -61.4639 | 0.041199 | -61.647 | 61.4639 | -61.6425 | -61.5692 | -61.9858 | 0.041199 | -61.8851 | 61.3678 | 61.4365 | -61.4822 | -61.6974 | -0.045776 | 0.027466 | -0.059509 | 0.13275 | -0.050354 | -0.07782 | 0.05951 | 0.11444 | -0.10071 | -0.15564 | -0.3891 | -0.28839 | -0.18768 | -0.086975 | 123.0606 | 123.1796 | 61.6379 | -123.0927 | 122.9645 | 123.0331 | 61.6379 | -123.2208
9.1562 | 123.3444 | -61.6516 | 61.496 | 0.0054168 | -0.040943 | 0.11616 | 0.024588 | 0.052229 | -0.025662 | -0.02506 | 0.0073242 | -0.0058555 | 0.03769 | 0.058999 | -0.016372 | -0.014676 | 61.6104 | -61.4273 | 0.054932 | -61.6699 | 61.4365 | -61.6699 | -61.5829 | -61.9858 | 0.036621 | -61.8805 | 61.3266 | 61.3678 | -61.496 | -61.7249 | -0.018311 | 0.068664 | -0.05951 | 0.2243 | -0.018311 | -0.086975 | 0.11444 | 0.15564 | -0.073243 | -0.16937 | -0.33417 | -0.22888 | -0.15564 | -0.12817 | 123.0881 | 123.262 | 61.7065 | -123.0789 | 122.9782 | 123.0194 | 61.6882 | -123.2208
10.9062 | 123.2574 | -61.6745 | 61.5234 | -0.0022127 | -0.02898 | 0.11381 | 0.027792 | 0.053938 | -0.01904 | -0.02271 | -0.0003053 | -0.00030125 | 0.044525 | 0.060067 | -0.014877 | -0.01318 | 61.5829 | -61.5051 | 0.018311 | -61.6928 | 61.5051 | -61.6837 | -61.6058 | -62.0316 | -0.004578 | -62.0132 | 61.377 | 61.4319 | -61.5234 | -61.7432 | -0.009155 | 0.068665 | -0.01831 | 0.16937 | -0.01831 | -0.086975 | 0.05951 | 0.15106 | -0.068664 | -0.14648 | -0.35705 | -0.33874 | -0.27008 | -0.091552 | 123.1796 | 123.2574 | 61.6928 | -123.1293 | 123.0515 | 123.1064 | 61.6699 | -123.2666
12.6094 | 123.3536 | -61.6287 | 61.4914 | -0.0022127 | -0.037311 | 0.11573 | 0.024588 | 0.052015 | -0.028867 | -0.021856 | 0.0073242 | -0.0056419 | 0.040467 | 0.059853 | -0.017227 | -0.011899 | 61.5967 | -61.4365 | 0.041199 | -61.6608 | 61.4044 | -61.647 | -61.5875 | -61.9766 | 0.032043 | -61.8988 | 61.3449 | 61.409 | -61.4914 | -61.7111 | -0.018311 | 0.041199 | -0.086975 | 0.19226 | -0.032044 | -0.073243 | 0.10529 | 0.13733 | -0.082398 | -0.14648 | -0.3479 | -0.27008 | -0.18768 | -0.082397 | 123.0331 | 123.2254 | 61.6699 | -123.0789 | 122.9736 | 123.0377 | 61.6608 | -123.2025
14.3438 | 123.3032 | -61.6379 | 61.5005 | -0.0022127 | -0.033253 | 0.1121 | 0.029288 | 0.052656 | -0.022672 | -0.022069 | 0.014954 | -0.0022239 | 0.042176 | 0.061776 | -0.015304 | -0.015103 | 61.6333 | -61.4548 | 0.07782 | -61.6425 | 61.5143 | -61.6791 | -61.5509 | -61.9492 | 0.10529 | -61.908 | 61.3953 | 61.4548 | -61.5051 | -61.7111 | -0.041199 | 0.086975 | 0.013733 | 0.1831 | -0.004578 | -0.091553 | 0.13275 | 0.13275 | -0.073243 | -0.10529 | -0.31128 | -0.27008 | -0.19684 | -0.045776 | 123.1522 | 123.2712 | 61.7157 | -123.0515 | 123.0331 | 123.0927 | 61.7432 | -123.2117
16.0469 | 123.3582 | -61.6196 | 61.5097 | -0.0022127 | -0.037098 | 0.1153 | 0.027792 | 0.055433 | -0.02844 | -0.024633 | 0.0073242 | -0.0041465 | 0.04068 | 0.06028 | -0.017013 | -0.012326 | 61.6013 | -61.4319 | 0.054932 | -61.6562 | 61.4502 | -61.6653 | -61.5601 | -61.9904 | 0.036621 | -61.8988 | 61.3495 | 61.4319 | -61.5051 | -61.6974 | -0.045776 | 0.059509 | -0.05951 | 0.18768 | -0.036621 | -0.09613 | 0.091552 | 0.11444 | -0.07782 | -0.16022 | -0.37079 | -0.27924 | -0.20142 | -0.07782 | 123.0698 | 123.2208 | 61.6745 | -123.0698 | 122.9691 | 123.0515 | 61.6562 | -123.2071
17.8125 | 123.3124 | -61.6791 | 61.4594 | -0.0022127 | -0.034107 | 0.11188 | 0.026083 | 0.053938 | -0.020963 | -0.019506 | 0.0073242 | -0.0017965 | 0.041962 | 0.060921 | -0.015518 | -0.012967 | 61.528 | -61.5738 | -0.068665 | -61.734 | 61.4456 | -61.7065 | -61.6425 | -62.0636 | -0.054932 | -62.0087 | 61.3586 | 61.4227 | -61.5555 | -61.7386 | -0.027466 | 0.036621 | -0.013733 | 0.10529 | -0.054932 | -0.091553 | 0.068664 | 0.1236 | -0.059509 | -0.10071 | -0.38452 | -0.32959 | -0.27008 | -0.036622 | 123.1247 | 123.2071 | 61.6104 | -123.1018 | 123.0377 | 123.1018 | 61.6241 | -123.1979
19.5781 | 123.3536 | -61.6516 | 61.441 | -0.0022127 | -0.037739 | 0.1153 | 0.024161 | 0.050306 | -0.026944 | -0.020788 | 0.0073242 | -0.0058555 | 0.040039 | 0.060707 | -0.014236 | -0.013394 | 61.6013 | -61.4044 | 0.054932 | -61.6562 | 61.3724 | -61.6653 | -61.5921 | -61.94 | 0.068665 | -61.8713 | 61.322 | 61.3495 | -61.5372 | -61.7157 | -0.013733 | 0.059509 | -0.068665 | 0.24719 | -0.004578 | -0.064087 | 0.16022 | 0.11444 | -0.064087 | -0.11902 | -0.28839 | -0.21973 | -0.15564 | -0.091553 | 123.024 | 123.2529 | 61.7065 | -123.0331 | 122.9736 | 123.0011 | 61.7203 | -123.1567
21.3281 | 123.3353 | -61.5738 | 61.528 | 0.013046 | -0.037952 | 0.11658 | 0.027792 | 0.052442 | -0.027158 | -0.023565 | -0.0079343 | -0.0052145 | 0.040467 | 0.058358 | -0.018295 | -0.013394 | 61.6882 | -61.322 | 0.1831 | -61.5601 | 61.4456 | -61.5875 | -61.5051 | -61.8805 | 0.1831 | -61.7889 | 61.377 | 61.441 | -61.441 | -61.6379 | -0.013732 | 0.068665 | -0.082397 | 0.25177 | 0.013733 | -0.054932 | 0.16022 | 0.13275 | -0.064086 | -0.15106 | -0.3067 | -0.21515 | -0.15106 | -0.086975 | 123.0194 | 123.262 | 61.7569 | -123.0331 | 122.9507 | 123.0148 | 61.7569 | -123.1659
23.0938 | 123.3765 | -61.6241 | 61.4456 | 0.0054168 | -0.039234 | 0.11637 | 0.022879 | 0.05052 | -0.022031 | -0.023778 | 0.0073242 | -0.0032919 | 0.039826 | 0.061135 | -0.013595 | -0.011685 | 61.5784 | -61.4777 | 0 | -61.6974 | 61.4044 | -61.6745 | -61.5967 | -61.9675 | 0.054932 | -61.908 | 61.322 | 61.3724 | -61.5005 | -61.7157 | -0.050354 | 0.027466 | -0.041199 | 0.14649 | -0.073242 | -0.10071 | 0.13275 | 0.1236 | -0.091552 | -0.1236 | -0.34332 | -0.28381 | -0.19226 | -0.073243 | 123.0286 | 123.2025 | 61.6241 | -123.0423 | 122.9462 | 122.9965 | 61.6791 | -123.1613
24.8438 | 123.2849 | -61.5967 | 61.5417 | -0.0022127 | -0.036243 | 0.11381 | 0.029288 | 0.054792 | -0.023313 | -0.022283 | 0.0073242 | -0.0026511 | 0.042176 | 0.06028 | -0.018722 | -0.014035 | 61.5875 | -61.4456 | 0.07782 | -61.6516 | 61.5326 | -61.6516 | -61.528 | -61.9812 | 0.064087 | -61.908 | 61.4273 | 61.4822 | -61.4685 | -61.6837 | -0.054931 | 0.068665 | -0.009155 | 0.15106 | -0.054931 | -0.1236 | 0.045776 | 0.12817 | -0.086975 | -0.11444 | -0.38452 | -0.31128 | -0.2243 | -0.059509 | 123.1293 | 123.1842 | 61.6745 | -123.0698 | 123.024 | 123.0789 | 61.6608 | -123.2254
26.5312 | 123.317 | -61.6013 | 61.496 | -0.0022127 | -0.035389 | 0.11466 | 0.025229 | 0.054578 | -0.027158 | -0.022924 | -0.0079343 | -0.0064963 | 0.042816 | 0.06028 | -0.016586 | -0.014249 | 61.6104 | -61.3907 | 0.07782 | -61.6608 | 61.3998 | -61.6425 | -61.5509 | -61.9675 | 0.045776 | -61.8805 | 61.3266 | 61.3724 | -61.5005 | -61.7203 | -0.041199 | 0.050354 | -0.096131 | 0.21057 | -0.05951 | -0.10986 | 0.11444 | 0.10071 | -0.11902 | -0.16937 | -0.36621 | -0.27924 | -0.16022 | -0.1236 | 123.0011 | 123.2117 | 61.6791 | -123.0469 | 122.9279 | 122.9736 | 61.647 | -123.2162
28.2969 | 123.317 | -61.6287 | 61.4868 | -0.0022127 | -0.036457 | 0.11551 | 0.025443 | 0.054792 | -0.025022 | -0.024206 | -0.0003053 | -0.0056419 | 0.040253 | 0.061562 | -0.018295 | -0.01318 | 61.6196 | -61.3861 | 0.068665 | -61.6562 | 61.3861 | -61.647 | -61.5692 | -61.9629 | 0.059509 | -61.8576 | 61.3174 | 61.3861 | -61.4777 | -61.6882 | -0.018311 | 0.059509 | -0.10071 | 0.24262 | -0.027466 | -0.086975 | 0.13275 | 0.15106 | -0.059509 | -0.16937 | -0.33417 | -0.22888 | -0.16937 | -0.10071 | 123.0148 | 123.2483 | 61.6974 | -123.056 | 122.9462 | 123.0148 | 61.6882 | -123.175
30.0625 | 123.2574 | -61.6653 | 61.5005 | -0.0098417 | -0.035175 | 0.11466 | 0.022665 | 0.050306 | -0.020108 | -0.021856 | -0.0079343 | -0.0043601 | 0.040467 | 0.061562 | -0.014877 | -0.012967 | 61.5555 | -61.528 | -0.018311 | -61.702 | 61.4639 | -61.6882 | -61.6104 | -62.027 | -0.009155 | -62.0178 | 61.3632 | 61.4273 | -61.5005 | -61.7294 | -0.022888 | 0.054931 | -0.036621 | 0.13733 | -0.036621 | -0.091552 | 0.054932 | 0.16479 | -0.064087 | -0.13733 | -0.36163 | -0.35248 | -0.28839 | -0.073242 | 123.1293 | 123.2208 | 61.647 | -123.111 | 123.0286 | 123.0927 | 61.6562 | -123.23
31.75 | 123.3856 | -61.6241 | 61.4273 | -0.0022127 | -0.038593 | 0.11295 | 0.023947 | 0.051161 | -0.022458 | -0.020574 | 0.0073242 | -0.0028647 | 0.038971 | 0.060707 | -0.014663 | -0.011899 | 61.528 | -61.528 | -0.050354 | -61.7111 | 61.4365 | -61.6928 | -61.6196 | -62.0132 | -0.009155 | -61.94 | 61.3403 | 61.409 | -61.5234 | -61.7157 | -0.068664 | 0.004578 | 0.009155 | 0.096131 | -0.086975 | -0.091553 | 0.10071 | 0.10071 | -0.091552 | -0.086975 | -0.3891 | -0.31586 | -0.2243 | -0.01831 | 123.0606 | 123.1522 | 61.5738 | -123.0469 | 122.9645 | 123.0331 | 61.615 | -123.143
33.5156 | 123.2986 | -61.6196 | 61.4731 | -0.0022127 | -0.037311 | 0.1153 | 0.027152 | 0.049879 | -0.02908 | -0.022069 | -0.0003053 | -0.0086325 | 0.042389 | 0.060494 | -0.019149 | -0.012112 | 61.5829 | -61.4182 | 0.059509 | -61.6516 | 61.3861 | -61.647 | -61.5646 | -61.9675 | 0.032043 | -61.8851 | 61.3174 | 61.3632 | -61.4914 | -61.6928 | -0.027466 | 0.054932 | -0.086975 | 0.20142 | -0.032043 | -0.086975 | 0.10986 | 0.12817 | -0.073242 | -0.15564 | -0.3479 | -0.2655 | -0.19226 | -0.10986 | 123.0057 | 123.2025 | 61.6791 | -123.0377 | 122.937 | 122.9828 | 61.6516 | -123.1659
35.2188 | 123.23 | -61.6974 | 61.4868 | -0.0022127 | -0.035175 | 0.11124 | 0.026297 | 0.049238 | -0.018826 | -0.020788 | 0.0073242 | -0.0020103 | 0.04538 | 0.063271 | -0.01274 | -0.01318 | 61.5234 | -61.5326 | -0.036621 | -61.7111 | 61.4319 | -61.6745 | -61.6013 | -62.0499 | -0.027466 | -62.0224 | 61.3449 | 61.4182 | -61.5417 | -61.734 | 0.022888 | 0.096131 | -0.054931 | 0.16479 | -0.013733 | -0.10986 | 0.036621 | 0.15564 | -0.036621 | -0.14191 | -0.35248 | -0.32501 | -0.28839 | -0.068664 | 123.1293 | 123.2208 | 61.6608 | -123.0881 | 123.0423 | 123.1155 | 61.6699 | -123.2208
36.9844 | 123.3215 | -61.6241 | 61.4502 | 0.0054168 | -0.037098 | 0.11466 | 0.026511 | 0.053083 | -0.025449 | -0.023778 | -0.0003053 | -0.0060691 | 0.043671 | 0.061348 | -0.017867 | -0.01254 | 61.5692 | -61.409 | 0.054932 | -61.6516 | 61.3724 | -61.6653 | -61.5829 | -61.9308 | 0.082397 | -61.8576 | 61.29 | 61.3403 | -61.5189 | -61.7065 | -0.041198 | 0.041199 | -0.07782 | 0.21515 | -0.027465 | -0.068664 | 0.11902 | 0.10529 | -0.082397 | -0.16022 | -0.3067 | -0.23346 | -0.15106 | -0.10986 | 122.9965 | 123.1934 | 61.6791 | -123.0331 | 122.9141 | 122.9645 | 61.7065 | -123.1567
38.7344 | 123.3398 | -61.6379 | 61.4182 | -0.0022127 | -0.03902 | 0.11359 | 0.026511 | 0.053724 | -0.023526 | -0.022069 | -0.0079343 | -0.0056419 | 0.041535 | 0.06028 | -0.017227 | -0.01318 | 61.5829 | -61.4044 | 0.054932 | -61.6379 | 61.3907 | -61.6653 | -61.5921 | -61.9263 | 0.073242 | -61.8759 | 61.2762 | 61.3312 | -61.5417 | -61.702 | -0.027466 | 0.045776 | -0.027466 | 0.23346 | 0 | -0.045776 | 0.16479 | 0.09613 | -0.064087 | -0.14191 | -0.28839 | -0.23804 | -0.17395 | -0.086975 | 123.0286 | 123.2208 | 61.6928 | -123.0103 | 122.9141 | 122.9691 | 61.7111 | -123.1201
40.4219 | 123.3307 | -61.6196 | 61.4227 | 0.013046 | -0.037952 | 0.11381 | 0.02822 | 0.052229 | -0.020963 | -0.022497 | -0.0003053 | -0.0043601 | 0.039612 | 0.060067 | -0.015518 | -0.013608 | 61.5234 | -61.5234 | -0.050354 | -61.7203 | 61.4044 | -61.6608 | -61.615 | -62.0224 | -0.022888 | -61.9537 | 61.3449 | 61.3907 | -61.5417 | -61.7477 | -0.041199 | 0.004578 | -0.01831 | 0.096131 | -0.10071 | -0.10529 | 0.10071 | 0.07782 | -0.12817 | -0.077819 | -0.40283 | -0.33417 | -0.20599 | -0.032043 | 123.024 | 123.143 | 61.5692 | -123.0377 | 122.9645 | 123.0103 | 61.5967 | -123.1705
42.1875 | 123.3398 | -61.6287 | 61.4731 | 0.013046 | -0.036671 | 0.11466 | 0.024374 | 0.051374 | -0.025876 | -0.020574 | -0.0079343 | -0.0064963 | 0.03833 | 0.058999 | -0.017227 | -0.012967 | 61.5875 | -61.3998 | 0.059509 | -61.6379 | 61.3724 | -61.6379 | -61.5738 | -61.9354 | 0.068665 | -61.8622 | 61.29 | 61.3724 | -61.4777 | -61.6928 | -0.009155 | 0.054931 | -0.10071 | 0.22888 | -0.009155 | -0.064086 | 0.11444 | 0.15106 | -0.064087 | -0.18311 | -0.3067 | -0.23346 | -0.16937 | -0.10071 | 123.0011 | 123.2162 | 61.6882 | -123.0469 | 122.9187 | 123.0011 | 61.6974 | -123.1659
43.9531 | 123.3032 | -61.6196 | 61.4685 | 0.0054168 | -0.039234 | 0.11509 | 0.025443 | 0.05351 | -0.026303 | -0.025915 | 0.0073242 | -0.0058555 | 0.039185 | 0.058785 | -0.017654 | -0.01254 | 61.5875 | -61.3998 | 0.050354 | -61.6516 | 61.3815 | -61.647 | -61.5601 | -61.9629 | 0.054932 | -61.8713 | 61.3037 | 61.3632 | -61.4777 | -61.6882 | -0.027466 | 0.059509 | -0.086975 | 0.21973 | -0.032043 | -0.091552 | 0.11902 | 0.14191 | -0.068664 | -0.16479 | -0.34332 | -0.25177 | -0.18311 | -0.10529 | 123.0011 | 123.2071 | 61.6699 | -123.0286 | 122.9233 | 122.9828 | 61.6745 | -123.1567
45.7031 | 123.23 | -61.615 | 61.5326 | -0.0022127 | -0.033253 | 0.11338 | 0.028433 | 0.05052 | -0.024381 | -0.022069 | -0.0003053 | -0.0043601 | 0.043244 | 0.061135 | -0.018936 | -0.015317 | 61.6608 | -61.3403 | 0.17853 | -61.5646 | 61.4502 | -61.5967 | -61.5005 | -61.9125 | 0.12817 | -61.821 | 61.377 | 61.4365 | -61.4502 | -61.6379 | 0.01831 | 0.11444 | -0.082398 | 0.27466 | 0.050354 | -0.064087 | 0.12817 | 0.16479 | -0.022888 | -0.15564 | -0.29755 | -0.20599 | -0.18311 | -0.096131 | 123.0652 | 123.2758 | 61.7935 | -123.0331 | 122.9919 | 123.0515 | 61.7432 | -123.1705
47.4062 | 123.2666 | -61.6196 | 61.5143 | -0.0022127 | -0.036671 | 0.11594 | 0.025656 | 0.052442 | -0.020749 | -0.022497 | 0.0073242 | -0.0020103 | 0.04068 | 0.060067 | -0.014449 | -0.01254 | 61.5646 | -61.4502 | 0.064087 | -61.6241 | 61.4914 | -61.6013 | -61.5509 | -61.9629 | 0.073242 | -61.9034 | 61.4136 | 61.496 | -61.4639 | -61.6425 | 0.018311 | 0.068665 | -0.022888 | 0.16937 | -0.004578 | -0.073243 | 0.050354 | 0.15564 | -0.022888 | -0.10071 | -0.34332 | -0.28381 | -0.26093 | -0.01831 | 123.111 | 123.1842 | 61.6837 | -123.0652 | 123.0331 | 123.1155 | 61.6928 | -123.1567
49.1719 | 123.3398 | -61.5967 | 61.4822 | -0.0022127 | -0.038807 | 0.11616 | 0.028433 | 0.050733 | -0.027371 | -0.022924 | 0.0073242 | -0.0073507 | 0.043457 | 0.057503 | -0.018722 | -0.011471 | 61.5601 | -61.4182 | 0.045776 | -61.6287 | 61.4182 | -61.6241 | -61.5326 | -61.9675 | 0.036621 | -61.8576 | 61.3541 | 61.3953 | -61.4594 | -61.6928 | -0.027466 | 0.064087 | -0.064087 | 0.17853 | -0.032043 | -0.09613 | 0.07782 | 0.13733 | -0.09613 | -0.12817 | -0.37079 | -0.26093 | -0.16479 | -0.086975 | 123.0148 | 123.1567 | 61.6425 | -123.0148 | 122.9507 | 122.9919 | 61.6333 | -123.175
50.9219 | 123.23 | -61.5921 | 61.5784 | -0.0098417 | -0.038807 | 0.11551 | 0.02822 | 0.05351 | -0.025449 | -0.02036 | 0.0073242 | -0.0058555 | 0.040894 | 0.062416 | -0.017654 | -0.012967 | 61.5875 | -61.3953 | 0.10529 | -61.6104 | 61.4822 | -61.5967 | -61.5005 | -61.9537 | 0.054932 | -61.8805 | 61.4227 | 61.4822 | -61.4731 | -61.6562 | -0.004578 | 0.091553 | -0.09613 | 0.19684 | -0.018311 | -0.10986 | 0.009155 | 0.11902 | -0.064087 | -0.15564 | -0.36163 | -0.28839 | -0.2243 | -0.09613 | 123.0743 | 123.1796 | 61.6974 | -123.0789 | 123.0148 | 123.0743 | 61.647 | -123.2346
52.625 | 123.2849 | -61.5921 | 61.5051 | 0.0054168 | -0.036884 | 0.11381 | 0.026297 | 0.052869 | -0.021817 | -0.02271 | 0.0073242 | -0.0020103 | 0.042389 | 0.060921 | -0.015945 | -0.013608 | 61.5875 | -61.4456 | 0.059509 | -61.615 | 61.5051 | -61.6104 | -61.5463 | -61.972 | 0.054932 | -61.9034 | 61.4044 | 61.4731 | -61.4731 | -61.6653 | -0.018311 | 0.045776 | 0 | 0.14648 | -0.022888 | -0.068664 | 0.082397 | 0.11902 | -0.073242 | -0.10071 | -0.37994 | -0.31128 | -0.23804 | -0.032044 | 123.0972 | 123.1796 | 61.6516 | -123.0515 | 122.9965 | 123.0652 | 61.647 | -123.1705
54.375 | 123.3032 | -61.5967 | 61.4639 | 0.0054168 | -0.040302 | 0.11338 | 0.023734 | 0.053724 | -0.025022 | -0.024206 | -0.0003053 | -0.0067099 | 0.038971 | 0.06028 | -0.015731 | -0.012753 | 61.5784 | -61.3815 | 0.041199 | -61.6241 | 61.3815 | -61.6425 | -61.5555 | -61.9217 | 0.073242 | -61.8484 | 61.2717 | 61.3266 | -61.496 | -61.7203 | -0.045776 | 0.041199 | -0.082397 | 0.21515 | -0.027466 | -0.068665 | 0.11444 | 0.10071 | -0.1236 | -0.19226 | -0.32501 | -0.25177 | -0.12817 | -0.13733 | 122.9782 | 123.175 | 61.6379 | -123.0194 | 122.8683 | 122.9233 | 61.6699 | -123.1842
56.125 | 123.349 | -61.5555 | 61.5097 | 0.0054168 | -0.036671 | 0.11616 | 0.029929 | 0.052015 | -0.027585 | -0.023351 | -0.0079343 | -0.0062827 | 0.039612 | 0.059853 | -0.016586 | -0.013394 | 61.647 | -61.2854 | 0.15564 | -61.5509 | 61.4502 | -61.6058 | -61.5005 | -61.853 | 0.17395 | -61.7477 | 61.3586 | 61.3907 | -61.441 | -61.6379 | -0.050354 | 0.054932 | -0.05951 | 0.27008 | 0.004578 | -0.050354 | 0.13733 | 0.11444 | -0.082397 | -0.15106 | -0.29755 | -0.19226 | -0.10986 | -0.11902 | 123.0057 | 123.2025 | 61.7111 | -123.0103 | 122.9141 | 122.9462 | 61.7294 | -123.1476
57.8906 | 123.1888 | -61.6562 | 61.4868 | -0.0098417 | -0.033893 | 0.11381 | 0.023947 | 0.053297 | -0.018613 | -0.023778 | -0.0003053 | -0.0017965 | 0.041321 | 0.063485 | -0.0121 | -0.01318 | 61.5692 | -61.4456 | 0.045776 | -61.647 | 61.4456 | -61.6516 | -61.5829 | -61.9812 | 0.032043 | -61.9629 | 61.3724 | 61.4044 | -61.5051 | -61.7111 | 0.004578 | 0.073242 | -0.041198 | 0.21057 | 0.009155 | -0.064087 | 0.082398 | 0.15106 | -0.054932 | -0.11444 | -0.32501 | -0.3067 | -0.25177 | -0.082397 | 123.1018 | 123.2254 | 61.702 | -123.0698 | 123.0286 | 123.0606 | 61.6882 | -123.1979
59.5781 | 123.3398 | -61.5784 | 61.4639 | 0.0054168 | -0.04137 | 0.0093439 | 0.024588 | 0.05052 | -0.028867 | -0.025274 | -0.0079343 | -0.0079917 | 0.03833 | 0.058571 | -0.016799 | -0.010617 | 61.5692 | -61.3815 | 0.064087 | -61.6104 | 61.4319 | -61.615 | -61.5326 | -61.9308 | 0.073242 | -61.8027 | 61.322 | 61.4227 | -61.4456 | -61.647 | -0.036621 | 0.045776 | -0.032043 | 0.19684 | -0.032044 | -0.07782 | 0.10529 | 0.13275 | -0.068665 | -0.14191 | -0.35248 | -0.2243 | -0.15564 | -0.041199 | 123.0103 | 123.1476 | 61.6425 | -122.9965 | 122.9004 | 123.0011 | 61.6516 | -123.111
61.3281 | 123.2025 | -61.6562 | 61.4594 | 0.013046 | -0.034534 | 0.11466 | 0.025656 | 0.053083 | -0.020108 | -0.020788 | -0.0079343 | -0.0037191 | 0.04303 | 0.059426 | -0.014236 | -0.013821 | 61.5051 | -61.5189 | -0.027466 | -61.6882 | 61.4273 | -61.6699 | -61.5784 | -62.0224 | -0.018311 | -61.9995 | 61.377 | 61.3586 | -61.5189 | -61.7477 | -0.013733 | 0.07782 | -0.032044 | 0.13733 | -0.032043 | -0.10986 | 0.045776 | 0.13733 | -0.091553 | -0.082398 | -0.36621 | -0.34332 | -0.25177 | -0.10071 | 123.0835 | 123.1613 | 61.6287 | -123.0377 | 123.0331 | 123.0148 | 61.6379 | -123.2071
63.1094 | 123.3444 | -61.5417 | 61.5051 | -0.0022127 | -0.037311 | 0.11765 | 0.030783 | 0.053724 | -0.028226 | -0.021856 | -0.0079343 | -0.0075645 | 0.042603 | 0.059426 | -0.020858 | -0.013394 | 61.6379 | -61.2762 | 0.16479 | -61.5555 | 61.4273 | -61.5692 | -61.496 | -61.8484 | 0.16479 | -61.7523 | 61.3403 | 61.3998 | -61.4182 | -61.6241 | -0.027466 | 0.045776 | -0.07782 | 0.2655 | -0.013733 | -0.059509 | 0.13275 | 0.1236 | -0.082398 | -0.1648 | -0.3067 | -0.21057 | -0.12817 | -0.10529 | 122.9691 | 123.1796 | 61.7065 | -123.0011 | 122.8821 | 122.9416 | 61.7065 | -123.1293
64.7969 | 123.2254 | -61.5646 | 61.5143 | 0.0054168 | -0.035816 | 0.11637 | 0.027365 | 0.053938 | -0.02609 | -0.020147 | 0.0073242 | -0.0060691 | 0.041107 | 0.06028 | -0.016372 | -0.01318 | 61.6425 | -61.2946 | 0.1831 | -61.528 | 61.441 | -61.5646 | -61.5005 | -61.8668 | 0.16937 | -61.7615 | 61.3449 | 61.4136 | -61.3953 | -61.647 | 0 | 0.064087 | -0.073242 | 0.27008 | 0.036621 | -0.027466 | 0.12817 | 0.16937 | -0.082398 | -0.16937 | -0.30212 | -0.19684 | -0.11444 | -0.10071 | 123.0057 | 123.2071 | 61.7477 | -123.0148 | 122.9095 | 122.9782 | 61.734 | -123.1613
66.5469 | 123.3398 | -61.5417 | 61.4868 | 0.0054168 | -0.036243 | 0.11573 | 0.026297 | 0.051161 | -0.027158 | -0.023138 | 0.0073242 | -0.0056419 | 0.039612 | 0.059212 | -0.018508 | -0.014462 | 61.6425 | -61.29 | 0.14191 | -61.5417 | 61.4227 | -61.5875 | -61.4685 | -61.8439 | 0.15564 | -61.7386 | 61.3403 | 61.3907 | -61.4044 | -61.6196 | -0.045776 | 0.073242 | -0.064087 | 0.25177 | 0 | -0.073242 | 0.15564 | 0.13733 | -0.07782 | -0.14648 | -0.30212 | -0.19684 | -0.11902 | -0.09613 | 122.9645 | 123.1842 | 61.6837 | -122.9553 | 122.8821 | 122.9324 | 61.6974 | -123.1064
68.25 | 123.3353 | -61.5463 | 61.4868 | -0.0022127 | -0.039234 | 0.1153 | 0.027365 | 0.052229 | -0.027585 | -0.022283 | -0.0003053 | -0.0067099 | 0.041321 | 0.061776 | -0.018508 | -0.016385 | 61.6516 | -61.322 | 0.11902 | -61.5646 | 61.4319 | -61.5784 | -61.496 | -61.8668 | 0.13733 | -61.7386 | 61.3358 | 61.3815 | -61.4273 | -61.6333 | -0.032043 | 0.050354 | -0.054931 | 0.22431 | -0.01831 | -0.068664 | 0.1648 | 0.11902 | -0.086975 | -0.15106 | -0.32043 | -0.19226 | -0.10528 | -0.10528 | 122.9782 | 123.1979 | 61.6653 | -122.9828 | 122.8821 | 122.9279 | 61.6837 | -123.1201
70 | 123.3307 | -61.5463 | 61.4822 | 0.013046 | -0.041157 | 0.11316 | 0.027152 | 0.051588 | -0.025876 | -0.025274 | 0.0073242 | -0.0035055 | 0.040253 | 0.059639 | -0.018936 | -0.012112 | 61.6058 | -61.3678 | 0.091553 | -61.5738 | 61.4273 | -61.6241 | -61.5051 | -61.8805 | 0.1236 | -61.7752 | 61.3495 | 61.4273 | -61.4273 | -61.6287 | -0.07782 | 0.041199 | -0.054932 | 0.17853 | -0.027466 | -0.068665 | 0.1236 | 0.11902 | -0.082397 | -0.13275 | -0.33417 | -0.22888 | -0.14648 | -0.054932 | 122.9736 | 123.1522 | 61.6379 | -122.9874 | 122.8958 | 122.9736 | 61.6699 | -123.111
71.6719 | 123.3307 | -61.6287 | 61.3861 | -0.0022127 | -0.038593 | 0.11338 | 0.024161 | 0.052015 | -0.02139 | -0.023565 | 0.0073242 | -0.0024375 | 0.041535 | 0.059853 | -0.014449 | -0.014889 | 61.5555 | -61.4319 | 0.009155 | -61.6425 | 61.409 | -61.6516 | -61.5692 | -61.9308 | 0.054932 | -61.8713 | 61.3083 | 61.3174 | -61.496 | -61.6928 | -0.022888 | 0.059509 | 0.022889 | 0.19684 | -0.013733 | -0.073242 | 0.16937 | 0.13275 | -0.064087 | -0.077819 | -0.30212 | -0.24262 | -0.17853 | -0.068664 | 123.0377 | 123.1842 | 61.6379 | -122.9553 | 122.937 | 122.9462 | 61.6837 | -123.0789
73.4375 | 123.2117 | -61.6333 | 61.4502 | -0.0022127 | -0.035816 | 0.11423 | 0.025229 | 0.053083 | -0.017758 | -0.022069 | -0.0079343 | 0.00076695 | 0.04068 | 0.060494 | -0.014663 | -0.01318 | 61.4731 | -61.5372 | -0.082397 | -61.6791 | 61.3953 | -61.6516 | -61.6104 | -62.0132 | -0.054932 | -61.9995 | 61.3495 | 61.4227 | -61.5051 | -61.7203 | -0.01831 | 0.022888 | -0.054931 | 0.096131 | -0.045776 | -0.068664 | 0.022888 | 0.12817 | -0.086975 | -0.10071 | -0.37994 | -0.36621 | -0.27924 | -0.027466 | 123.0286 | 123.1064 | 61.5509 | -123.0606 | 122.9828 | 123.056 | 61.5784 | -123.1705
75.1875 | 123.2025 | -61.647 | 61.4502 | 0.0054168 | -0.034748 | 0.11274 | 0.027152 | 0.051588 | -0.020749 | -0.022069 | -0.0003053 | -0.0030783 | 0.043244 | 0.060707 | -0.015731 | -0.012967 | 61.5692 | -61.3998 | 0.073242 | -61.615 | 61.4273 | -61.6013 | -61.5463 | -61.9034 | 0.10529 | -61.8851 | 61.3403 | 61.409 | -61.4685 | -61.6745 | 0.045777 | 0.10071 | -0.022888 | 0.24719 | 0.032044 | -0.068664 | 0.11902 | 0.17853 | -0.027466 | -0.10986 | -0.25635 | -0.23804 | -0.21057 | -0.041198 | 123.0743 | 123.2162 | 61.7203 | -122.9965 | 122.9874 | 123.056 | 61.7523 | -123.1247
76.875 | 123.1705 | -61.6699 | 61.4777 | -0.0022127 | -0.033893 | 0.11295 | 0.025229 | 0.052229 | -0.023526 | -0.020574 | -0.0003053 | -0.0024375 | 0.041321 | 0.06263 | -0.016372 | -0.01254 | 61.5417 | -61.4273 | 0.027466 | -61.6516 | 61.4273 | -61.6425 | -61.5555 | -61.9904 | 0.032043 | -61.9308 | 61.3266 | 61.3998 | -61.4914 | -61.7157 | 0.027466 | 0.11444 | -0.050354 | 0.24262 | 0.018311 | -0.09613 | 0.064087 | 0.17853 | -0.045776 | -0.15106 | -0.32043 | -0.26093 | -0.21515 | -0.07782 | 123.0972 | 123.2117 | 61.6974 | -123.0331 | 122.9965 | 123.0698 | 61.702 | -123.1934
78.6406 | 123.2712 | -61.6013 | 61.4548 | -0.0022127 | -0.037311 | 0.11509 | 0.027365 | 0.054578 | -0.028226 | -0.022497 | 0.0073242 | -0.0088461 | 0.041962 | 0.058999 | -0.018081 | -0.010831 | 61.5692 | -61.3632 | 0.054932 | -61.6241 | 61.3541 | -61.6287 | -61.5234 | -61.9446 | 0.059509 | -61.8439 | 61.2946 | 61.3586 | -61.4731 | -61.6562 | -0.027466 | 0.07782 | -0.10071 | 0.23804 | -0.022889 | -0.10071 | 0.11444 | 0.12817 | -0.054932 | -0.16022 | -0.34332 | -0.24262 | -0.18768 | -0.09613 | 122.9553 | 123.1705 | 61.6562 | -122.9782 | 122.8958 | 122.9599 | 61.6608 | -123.111
80.3906 | 123.2666 | -61.5417 | 61.5097 | -0.0098417 | -0.036243 | 0.1153 | 0.026083 | 0.054792 | -0.027799 | -0.024206 | -0.0003053 | -0.0054281 | 0.040039 | 0.058999 | -0.017654 | -0.013394 | 61.615 | -61.2808 | 0.19226 | -61.528 | 61.441 | -61.5555 | -61.4777 | -61.853 | 0.17395 | -61.7477 | 61.3403 | 61.4227 | -61.4319 | -61.6058 | -0.013733 | 0.064087 | -0.068665 | 0.26093 | 0.013733 | -0.050354 | 0.10529 | 0.10986 | -0.064087 | -0.16937 | -0.31128 | -0.20599 | -0.14191 | -0.086976 | 122.9828 | 123.1567 | 61.734 | -122.9874 | 122.8821 | 122.9645 | 61.7157 | -123.1155
82.1562 | 123.3215 | -61.5692 | 61.4685 | -0.0022127 | -0.037098 | 0.1153 | 0.029501 | 0.05351 | -0.026517 | -0.022924 | 0.0073242 | -0.0054281 | 0.042603 | 0.059853 | -0.019363 | -0.014462 | 61.528 | -61.3907 | 0.068665 | -61.6058 | 61.4365 | -61.6104 | -61.5372 | -61.9217 | 0.064087 | -61.8073 | 61.3312 | 61.3953 | -61.4594 | -61.6653 | -0.041199 | 0.032044 | -0.032044 | 0.17853 | -0.036621 | -0.068665 | 0.059509 | 0.10986 | -0.09613 | -0.13733 | -0.35248 | -0.23804 | -0.14191 | -0.073242 | 123.0057 | 123.0972 | 61.6379 | -123.0057 | 122.9004 | 122.9645 | 61.6333 | -123.1338
83.9219 | 123.1888 | -61.6287 | 61.4456 | -0.0022127 | -0.030903 | 0.11509 | 0.026938 | 0.052869 | -0.020108 | -0.022497 | -0.0003053 | -0.0013693 | 0.041962 | 0.06028 | -0.01509 | -0.014889 | 61.5829 | -61.3953 | 0.064087 | -61.6104 | 61.4319 | -61.615 | -61.5372 | -61.9446 | 0.073242 | -61.8988 | 61.3312 | 61.3815 | -61.4685 | -61.702 | 0.013733 | 0.091553 | -0.013733 | 0.23346 | 0.01831 | -0.073243 | 0.13733 | 0.16022 | -0.073242 | -0.11444 | -0.31586 | -0.27008 | -0.19684 | -0.064087 | 123.0606 | 123.2117 | 61.6928 | -122.9828 | 122.9599 | 123.0103 | 61.702 | -123.1476
85.6875 | 123.2483 | -61.6104 | 61.3953 | -0.0022127 | -0.038593 | 0.11487 | 0.02352 | 0.056287 | -0.023313 | -0.022283 | -0.0079343 | -0.0030783 | 0.039185 | 0.061348 | -0.015518 | -0.014889 | 61.4822 | -61.5143 | -0.073242 | -61.6653 | 61.4136 | -61.6562 | -61.5555 | -62.0178 | -0.041199 | -61.9629 | 61.3266 | 61.3998 | -61.5051 | -61.7065 | -0.045776 | 0.054932 | 0.01831 | 0.096131 | -0.054931 | -0.10986 | 0.086975 | 0.10529 | -0.09613 | -0.068665 | -0.40741 | -0.35248 | -0.25635 | 0.004577 | 123.024 | 123.0927 | 61.5372 | -122.9507 | 122.937 | 123.0103 | 61.5692 | -123.1018
87.3906 | 123.2758 | -61.5829 | 61.4044 | 0.0054168 | -0.03603 | 0.11274 | 0.025015 | 0.053083 | -0.025022 | -0.021429 | -0.0079343 | -0.0067099 | 0.040253 | 0.059212 | -0.017227 | -0.01318 | 61.5555 | -61.3815 | 0.041199 | -61.615 | 61.3495 | -61.6333 | -61.5692 | -61.9217 | 0.073242 | -61.8301 | 61.2442 | 61.3174 | -61.4822 | -61.6699 | -0.050354 | 0.013733 | -0.054932 | 0.20142 | -0.032043 | -0.045776 | 0.15106 | 0.10071 | -0.086975 | -0.16022 | -0.33875 | -0.24719 | -0.16022 | -0.086975 | 122.9324 | 123.1384 | 61.6241 | -122.9736 | 122.8271 | 122.9004 | 61.6562 | -123.0743
89.1406 | 123.1979 | -61.6516 | 61.4456 | 0.013046 | -0.034321 | 0.11274 | 0.02587 | 0.052015 | -0.022244 | -0.023565 | 0.0073242 | -0.0035055 | 0.040467 | 0.060921 | -0.01509 | -0.014035 | 61.4777 | -61.528 | -0.036621 | -61.6699 | 61.4227 | -61.6562 | -61.5601 | -62.0361 | -0.013733 | -61.9904 | 61.322 | 61.4044 | -61.496 | -61.6928 | -0.004578 | 0.091552 | -0.022889 | 0.1236 | -0.018311 | -0.10986 | 0.032043 | 0.15564 | -0.041199 | -0.1236 | -0.38452 | -0.33874 | -0.29755 | -0.041199 | 123.0743 | 123.1293 | 61.615 | -123.0057 | 122.9736 | 123.056 | 61.6379 | -123.1384
90.9062 | 123.2712 | -61.5509 | 61.4594 | 0.0054168 | -0.040089 | 0.11466 | 0.02822 | 0.052442 | -0.029294 | -0.025274 | 0.0073242 | -0.0062827 | 0.041535 | 0.059639 | -0.018936 | -0.011471 | 61.5234 | -61.4044 | 0.050354 | -61.6058 | 61.4136 | -61.5875 | -61.5234 | -61.9629 | 0.041199 | -61.8622 | 61.3037 | 61.3724 | -61.441 | -61.647 | -0.036621 | 0.027466 | -0.045777 | 0.14648 | -0.054932 | -0.082398 | 0.064086 | 0.10986 | -0.096131 | -0.15564 | -0.41199 | -0.31128 | -0.21515 | -0.086976 | 122.9645 | 123.0743 | 61.6013 | -122.9828 | 122.8546 | 122.9233 | 61.5921 | -123.1064
92.6094 | 123.2986 | -61.5601 | 61.4685 | -0.0022127 | -0.040729 | 0.1168 | 0.024374 | 0.052015 | -0.026517 | -0.023138 | -0.0003053 | -0.0064963 | 0.040253 | 0.060067 | -0.01744 | -0.01318 | 61.528 | -61.3953 | 0.032043 | -61.5875 | 61.3998 | -61.6058 | -61.5143 | -61.94 | 0.050354 | -61.8393 | 61.3129 | 61.3815 | -61.4502 | -61.6379 | -0.045776 | 0.045777 | -0.068665 | 0.1648 | -0.027465 | -0.073242 | 0.059509 | 0.10986 | -0.077819 | -0.15564 | -0.37994 | -0.27923 | -0.20142 | -0.086975 | 122.9599 | 123.0881 | 61.5921 | -122.9828 | 122.8729 | 122.9416 | 61.6104 | -123.1064
94.3594 | 123.2254 | -61.5921 | 61.4548 | -0.0098417 | -0.035602 | 0.11466 | 0.027152 | 0.051374 | -0.019681 | -0.024633 | 0.0073242 | -0.0026511 | 0.043671 | 0.059426 | -0.014236 | -0.015103 | 61.5463 | -61.4273 | 0.059509 | -61.5967 | 61.4685 | -61.5829 | -61.5143 | -61.9354 | 0.064087 | -61.8713 | 61.3953 | 61.4227 | -61.4319 | -61.6425 | 0.009155 | 0.07782 | 0.013733 | 0.16479 | -0.004578 | -0.082398 | 0.091553 | 0.16022 | -0.050354 | -0.059509 | -0.34332 | -0.27924 | -0.22888 | -0.032044 | 123.0606 | 123.1384 | 61.6516 | -122.9691 | 122.9874 | 123.0148 | 61.6562 | -123.0972
96.1094 | 123.2162 | -61.5372 | 61.4822 | -0.0022127 | -0.034107 | 0.11295 | 0.028006 | 0.055006 | -0.022458 | -0.026342 | 0.0073242 | -0.0022239 | 0.042389 | 0.061562 | -0.017013 | -0.015103 | 61.5555 | -61.4227 | 0.07782 | -61.5921 | 61.4822 | -61.5829 | -61.528 | -61.9537 | 0.068665 | -61.8805 | 61.4044 | 61.4502 | -61.4502 | -61.6287 | -0.045777 | 0.009155 | 0 | 0.11444 | -0.054932 | -0.064087 | 0.073242 | 0.086975 | -0.091553 | -0.07782 | -0.41656 | -0.34332 | -0.25177 | -0.032044 | 123.0194 | 123.0927 | 61.615 | -123.0103 | 122.9416 | 122.9874 | 61.6058 | -123.111
97.8594 | 123.2529 | -61.5829 | 61.4319 | 0.0054168 | -0.037311 | 0.11381 | 0.023306 | 0.051588 | -0.025662 | -0.024419 | 0.014954 | -0.0037191 | 0.04068 | 0.059426 | -0.015518 | -0.012967 | 61.5738 | -61.3449 | 0.064087 | -61.6013 | 61.3403 | -61.5921 | -61.5234 | -61.9171 | 0.050354 | -61.821 | 61.2625 | 61.3495 | -61.4777 | -61.6791 | -0.009155 | 0.05951 | -0.091553 | 0.23804 | -0.01831 | -0.07782 | 0.14191 | 0.10529 | -0.09613 | -0.16937 | -0.33417 | -0.23804 | -0.14191 | -0.082398 | 122.9233 | 123.1567 | 61.647 | -122.9553 | 122.8455 | 122.9324 | 61.6333 | -123.111
99.6094 | 123.2483 | -61.5829 | 61.4365 | -0.0098417 | -0.042011 | 0.11594 | 0.025015 | 0.052442 | -0.026731 | -0.023138 | -0.0003053 | -0.0067099 | 0.039826 | 0.058144 | -0.014022 | -0.012326 | 61.5417 | -61.3541 | 0.050354 | -61.615 | 61.3678 | -61.5692 | -61.5143 | -61.9171 | 0.032043 | -61.8347 | 61.2808 | 61.3632 | -61.4639 | -61.6562 | 0.013733 | 0.068665 | -0.068664 | 0.22888 | -0.032043 | -0.10071 | 0.10529 | 0.11902 | -0.073242 | -0.15564 | -0.33417 | -0.25177 | -0.17853 | -0.073242 | 122.9507 | 123.1247 | 61.6333 | -122.9507 | 122.8638 | 122.9462 | 61.615 | -123.0927
101.375 | 123.1659 | -61.5829 | 61.5234 | 0.0054168 | -0.036457 | 0.11381 | 0.029074 | 0.05052 | -0.025449 | -0.023992 | 0.0073242 | -0.0017965 | 0.043244 | 0.059853 | -0.018722 | -0.014249 | 61.5601 | -61.3632 | 0.1236 | -61.5875 | 61.4594 | -61.5646 | -61.496 | -61.9308 | 0.059509 | -61.853 | 61.3861 | 61.4273 | -61.4594 | -61.6287 | 0.018311 | 0.086975 | -0.064086 | 0.21973 | -0.004577 | -0.091552 | 0.036622 | 0.1236 | -0.045776 | -0.13733 | -0.3479 | -0.27008 | -0.2243 | -0.09613 | 123.0423 | 123.143 | 61.7065 | -123.0194 | 122.9691 | 123.0103 | 61.6425 | -123.1522
103.0781 | 123.2208 | -61.5829 | 61.4685 | 0.0054168 | -0.035175 | 0.11359 | 0.024802 | 0.053297 | -0.021176 | -0.021001 | -0.0003053 | -0.0022239 | 0.041321 | 0.061776 | -0.014663 | -0.012967 | 61.5692 | -61.4044 | 0.068665 | -61.5784 | 61.4594 | -61.6379 | -61.5326 | -61.9125 | 0.086975 | -61.8668 | 61.3632 | 61.4319 | -61.441 | -61.6333 | -0.054931 | 0.050354 | -0.009155 | 0.17853 | 0.004578 | -0.045776 | 0.10071 | 0.14191 | -0.050354 | -0.10529 | -0.32959 | -0.28381 | -0.23346 | -0.036621 | 123.0423 | 123.1522 | 61.6516 | -123.0011 | 122.9462 | 123.0148 | 61.6699 | -123.1018
104.8125 | 123.2895 | -61.5921 | 61.3998 | 0.013046 | -0.038166 | 0.11487 | 0.02587 | 0.050947 | -0.024594 | -0.023351 | 0.0073242 | -0.0041465 | 0.039826 | 0.061135 | -0.016372 | -0.01254 | 61.5326 | -61.4136 | -0.004578 | -61.6379 | 61.3541 | -61.647 | -61.5555 | -61.9171 | 0.041199 | -61.8439 | 61.2534 | 61.3083 | -61.4777 | -61.6791 | -0.054932 | 0.036621 | -0.045776 | 0.17853 | -0.045776 | -0.082397 | 0.13275 | 0.11444 | -0.086975 | -0.14648 | -0.32501 | -0.25177 | -0.16479 | -0.091552 | 122.9462 | 123.1247 | 61.5875 | -122.9553 | 122.8455 | 122.9004 | 61.6333 | -123.0789
106.5625 | 123.1796 | -61.5601 | 61.4914 | 0.0054168 | -0.036457 | 0.11594 | 0.029715 | 0.052229 | -0.024594 | -0.022497 | -0.0003053 | -0.0028647 | 0.04303 | 0.061348 | -0.018508 | -0.011685 | 61.5372 | -61.3907 | 0.054932 | -61.5784 | 61.496 | -61.5875 | -61.4914 | -61.9446 | 0.064087 | -61.8759 | 61.3678 | 61.4502 | -61.4273 | -61.6516 | -0.027465 | 0.068665 | 0.004578 | 0.16937 | -0.01831 | -0.086975 | 0.045776 | 0.13275 | -0.091552 | -0.1236 | -0.38452 | -0.31586 | -0.2243 | -0.041199 | 123.056 | 123.0972 | 61.615 | -122.9828 | 122.9279 | 123.0103 | 61.6241 | -123.143
108.2812 | 123.2895 | -61.5784 | 61.3678 | -0.0098417 | -0.039234 | 0.11551 | 0.024802 | 0.052869 | -0.022031 | -0.022497 | 0.0073242 | -0.0026511 | 0.040039 | 0.061989 | -0.014877 | -0.011685 | 61.4731 | -61.4639 | -0.050354 | -61.6653 | 61.3861 | -61.6653 | -61.5417 | -61.9583 | -0.004578 | -61.9034 | 61.2671 | 61.3449 | -61.4822 | -61.7111 | -0.086975 | 0.036621 | 0.01831 | 0.11444 | -0.086975 | -0.1236 | 0.10529 | 0.09613 | -0.13275 | -0.10071 | -0.37994 | -0.32501 | -0.19226 | -0.022888 | 122.9645 | 123.0515 | 61.528 | -122.9095 | 122.8455 | 122.9233 | 61.5738 | -123.0789
110.0312 | 123.2071 | -61.5829 | 61.4456 | -0.0022127 | -0.037739 | 0.11402 | 0.027152 | 0.056074 | -0.021817 | -0.023778 | -0.0003053 | -0.0026511 | 0.040039 | 0.059639 | -0.015518 | -0.012967 | 61.5234 | -61.3861 | 0.059509 | -61.5921 | 61.4548 | -61.6013 | -61.5097 | -61.9125 | 0.09613 | -61.8393 | 61.3266 | 61.3815 | -61.4502 | -61.6608 | -0.01831 | 0.073242 | 0.009155 | 0.19684 | -0.009155 | -0.082397 | 0.077819 | 0.13275 | -0.07782 | -0.11902 | -0.32959 | -0.25635 | -0.17853 | -0.064087 | 123.0377 | 123.1064 | 61.6425 | -122.9553 | 122.9095 | 122.9645 | 61.6791 | -123.1064
111.7969 | 123.2986 | -61.5234 | 61.4365 | 0.0054168 | -0.037739 | 0.11594 | 0.028647 | 0.050733 | -0.031003 | -0.023351 | 0.014954 | -0.0067099 | 0.040253 | 0.058999 | -0.020004 | -0.011899 | 61.5326 | -61.3586 | 0.086975 | -61.5601 | 61.3953 | -61.5784 | -61.4777 | -61.8805 | 0.11444 | -61.7523 | 61.322 | 61.3953 | -61.3907 | -61.6104 | -0.054932 | 0.045776 | -0.041198 | 0.16479 | -0.036622 | -0.082398 | 0.096131 | 0.13275 | -0.086976 | -0.11444 | -0.35706 | -0.22888 | -0.14191 | -0.041198 | 122.9187 | 123.056 | 61.6104 | -122.9141 | 122.8455 | 122.9187 | 61.6379 | -123.0469
113.4844 | 123.1293 | -61.5555 | 61.5143 | 0.0054168 | -0.037525 | 0.11423 | 0.027792 | 0.053297 | -0.028012 | -0.022497 | -0.0003053 | -0.0058555 | 0.039826 | 0.061989 | -0.017227 | -0.013394 | 61.615 | -61.2946 | 0.17395 | -61.5097 | 61.4227 | -61.5784 | -61.4639 | -61.8896 | 0.12817 | -61.7844 | 61.3403 | 61.4227 | -61.3861 | -61.615 | -0.022888 | 0.091553 | -0.091553 | 0.26093 | 0.045776 | -0.045777 | 0.10071 | 0.16937 | -0.059509 | -0.17395 | -0.33417 | -0.22888 | -0.16937 | -0.091553 | 122.9782 | 123.1705 | 61.7294 | -122.9782 | 122.8958 | 122.9782 | 61.6837 | -123.1293
115.25 | 123.1476 | -61.5417 | 61.5463 | -0.0098417 | -0.035602 | 0.11637 | 0.02587 | 0.052869 | -0.025235 | -0.022283 | 0.0073242 | -0.0041465 | 0.041535 | 0.062203 | -0.018508 | -0.011685 | 61.6241 | -61.29 | 0.17395 | -61.5189 | 61.4227 | -61.5601 | -61.4594 | -61.8668 | 0.14648 | -61.7569 | 61.3495 | 61.4044 | -61.3907 | -61.5921 | -0.018311 | 0.082397 | -0.1236 | 0.25177 | 0.022888 | -0.059509 | 0.07782 | 0.15106 | -0.050354 | -0.19684 | -0.32501 | -0.21515 | -0.1648 | -0.14191 | 122.9645 | 123.1659 | 61.7157 | -123.0057 | 122.8912 | 122.9462 | 61.6882 | -123.1384
117.0156 | 123.1476 | -61.5601 | 61.5143 | -0.0022127 | -0.034107 | 0.11551 | 0.026938 | 0.055219 | -0.025876 | -0.02506 | -0.0003053 | -0.0032919 | 0.040253 | 0.058999 | -0.017227 | -0.015103 | 61.6104 | -61.2762 | 0.1831 | -61.5097 | 61.4044 | -61.5646 | -61.4548 | -61.8393 | 0.15564 | -61.7432 | 61.3312 | 61.3998 | -61.3907 | -61.5601 | -0.004577 | 0.10529 | -0.10986 | 0.28381 | 0.050354 | -0.054932 | 0.096131 | 0.16937 | 0 | -0.18311 | -0.27923 | -0.1831 | -0.1831 | -0.11444 | 122.9645 | 123.1705 | 61.7432 | -122.9691 | 122.8912 | 122.9599 | 61.7157 | -123.0743
118.7812 | 123.2666 | -61.5234 | 61.441 | -0.0022127 | -0.039234 | 0.11808 | 0.027792 | 0.052442 | -0.026303 | -0.024206 | -0.0003053 | -0.0069235 | 0.041107 | 0.060067 | -0.01979 | -0.012967 | 61.5189 | -61.3815 | 0.050354 | -61.5875 | 61.3953 | -61.5738 | -61.496 | -61.908 | 0.054932 | -61.8164 | 61.2854 | 61.3724 | -61.3953 | -61.647 | -0.050355 | 0.027465 | -0.045776 | 0.14191 | -0.064087 | -0.091552 | 0.07782 | 0.12817 | -0.1236 | -0.15564 | -0.38452 | -0.29297 | -0.16937 | -0.068665 | 122.9187 | 123.0423 | 61.5738 | -122.937 | 122.8088 | 122.8958 | 61.5784 | -123.0881
120.4688 | 123.2162 | -61.5555 | 61.4227 | -0.0022127 | -0.037739 | 0.11509 | 0.023947 | 0.051374 | -0.022885 | -0.022924 | 0.0073242 | -0.0062827 | 0.040894 | 0.061776 | -0.017227 | -0.014249 | 61.5555 | -61.3403 | 0.059509 | -61.5967 | 61.3449 | -61.5967 | -61.5143 | -61.908 | 0.041199 | -61.8347 | 61.2717 | 61.3266 | -61.4548 | -61.647 | -0.041199 | 0.041199 | -0.077819 | 0.21515 | -0.041199 | -0.082398 | 0.13275 | 0.10071 | -0.091553 | -0.15106 | -0.35248 | -0.27924 | -0.18768 | -0.09613 | 122.9004 | 123.111 | 61.615 | -122.937 | 122.8271 | 122.8821 | 61.5967 | -123.0698
122.1562 | 123.1705 | -61.5463 | 61.496 | 0.013046 | -0.033253 | 0.11402 | 0.029501 | 0.052442 | -0.022031 | -0.023992 | -0.0003053 | -0.0041465 | 0.041107 | 0.061348 | -0.015731 | -0.014889 | 61.5417 | -61.3724 | 0.07782 | -61.5784 | 61.4731 | -61.5692 | -61.4685 | -61.9263 | 0.045776 | -61.8576 | 61.377 | 61.4136 | -61.4182 | -61.5875 | -0.022888 | 0.07782 | -0.022889 | 0.17395 | -0.032043 | -0.10986 | 0.045776 | 0.12817 | -0.041198 | -0.11902 | -0.37994 | -0.31128 | -0.27008 | -0.082398 | 123.0194 | 123.0881 | 61.6241 | -122.9645 | 122.9233 | 122.9599 | 61.5921 | -123.0835
123.8594 | 123.1338 | -61.6333 | 61.3998 | 0.0054168 | -0.034107 | 0.11231 | 0.023734 | 0.052869 | -0.018613 | -0.022283 | 0.0073242 | -0.0030783 | 0.043671 | 0.06028 | -0.013809 | -0.013821 | 61.4731 | -61.4731 | -0.018311 | -61.6516 | 61.4136 | -61.6013 | -61.5601 | -61.9858 | -0.013733 | -61.9537 | 61.3174 | 61.3678 | -61.4594 | -61.6928 | 0.032044 | 0.073242 | 0.013733 | 0.16022 | -0.01831 | -0.091552 | 0.073242 | 0.17395 | -0.059509 | -0.082397 | -0.35248 | -0.32043 | -0.26093 | -0.032043 | 123.0469 | 123.1064 | 61.615 | -122.9599 | 122.9507 | 123.0011 | 61.6196 | -123.0927
125.625 | 123.1522 | -61.6058 | 61.4136 | 0.013046 | -0.038166 | 0.11381 | 0.024802 | 0.052656 | -0.020749 | -0.022283 | 0.0073242 | -0.0037191 | 0.041321 | 0.059853 | -0.015518 | -0.01254 | 61.4136 | -61.496 | -0.082397 | -61.6699 | 61.409 | -61.6425 | -61.5738 | -61.9858 | -0.059509 | -61.9583 | 61.2991 | 61.3403 | -61.5097 | -61.6974 | -0.036621 | 0.032043 | -0.004577 | 0.10986 | -0.064087 | -0.09613 | 0 | 0.09613 | -0.091553 | -0.11444 | -0.37994 | -0.35248 | -0.26093 | -0.073242 | 123.0148 | 123.0194 | 61.5234 | -122.9874 | 122.905 | 122.9462 | 61.5463 | -123.111
127.3438 | 123.1522 | -61.5921 | 61.4044 | 0.0054168 | -0.034748 | 0.11338 | 0.025656 | 0.049665 | -0.022672 | -0.022924 | 0.0073242 | -0.0035055 | 0.041962 | 0.059853 | -0.01509 | -0.012112 | 61.4227 | -61.4822 | -0.045776 | -61.6745 | 61.409 | -61.647 | -61.5463 | -62.0132 | -0.032043 | -61.9492 | 61.2808 | 61.3403 | -61.496 | -61.7065 | -0.054932 | 0.045776 | 0.004578 | 0.10986 | -0.082398 | -0.12817 | 0.01831 | 0.09613 | -0.11444 | -0.1236 | -0.42114 | -0.35706 | -0.24261 | -0.064087 | 123.0011 | 123.0148 | 61.5463 | -122.9507 | 122.8729 | 122.9324 | 61.5601 | -123.111
129.1094 | 123.1705 | -61.5555 | 61.4685 | -0.0022127 | -0.035816 | 0.11594 | 0.029501 | 0.05351 | -0.024808 | -0.023351 | 0.0073242 | -0.0030783 | 0.04068 | 0.058999 | -0.016586 | -0.014035 | 61.4731 | -61.3861 | 0.059509 | -61.5921 | 61.4227 | -61.5692 | -61.4914 | -61.9308 | 0.07782 | -61.8622 | 61.3724 | 61.3998 | -61.4456 | -61.6379 | -0.013733 | 0.064087 | -0.045777 | 0.16937 | -0.036621 | -0.10071 | 0.004577 | 0.10986 | -0.082397 | -0.096131 | -0.37537 | -0.3067 | -0.22431 | -0.068665 | 122.9782 | 123.0286 | 61.615 | -122.9599 | 122.9279 | 122.9553 | 61.6333 | -123.1064
130.7969 | 123.2574 | -61.5692 | 61.3678 | 0.020676 | -0.036457 | 0.1153 | 0.025015 | 0.052229 | -0.027158 | -0.022283 | 0.0073242 | -0.0064963 | 0.040894 | 0.061135 | -0.018081 | -0.013608 | 61.5097 | -61.3495 | 0.045776 | -61.5692 | 61.3495 | -61.6241 | -61.5097 | -61.8942 | 0.064087 | -61.8118 | 61.2213 | 61.29 | -61.4594 | -61.6516 | -0.054932 | 0.059509 | -0.018311 | 0.21973 | 0 | -0.059509 | 0.14191 | 0.10986 | -0.082397 | -0.14648 | -0.32501 | -0.24262 | -0.16022 | -0.07782 | 122.9187 | 123.0789 | 61.615 | -122.8775 | 122.7905 | 122.8592 | 61.6333 | -123.0194
132.7344 | 123.23 | -61.5829 | 61.377 | -0.0098417 | -0.036671 | 0.11423 | 0.025015 | 0.052869 | -0.022458 | -0.022069 | -0.0003053 | -0.0015829 | 0.040894 | 0.061562 | -0.016586 | -0.01254 | 61.4319 | -61.4502 | -0.050354 | -61.6608 | 61.3953 | -61.6196 | -61.5692 | -61.9904 | -0.032043 | -61.9125 | 61.29 | 61.3403 | -61.4685 | -61.6699 | -0.036621 | 0.013733 | 0.018311 | 0.13275 | -0.07782 | -0.091553 | 0.054932 | 0.11444 | -0.086975 | -0.086975 | -0.40741 | -0.32959 | -0.24262 | -0.036621 | 122.9782 | 123.0148 | 61.5326 | -122.9462 | 122.8729 | 122.9233 | 61.5509 | -123.0469
134.5469 | 123.2025 | -61.5372 | 61.441 | -0.0022127 | -0.037952 | 0.11616 | 0.028647 | 0.052656 | -0.028012 | -0.024206 | -0.0003053 | -0.0058555 | 0.040039 | 0.057503 | -0.019149 | -0.01254 | 61.496 | -61.3495 | 0.032043 | -61.5875 | 61.3632 | -61.5646 | -61.4777 | -61.9263 | 0.036621 | -61.8256 | 61.2534 | 61.3632 | -61.4044 | -61.6104 | -0.027466 | 0.059509 | -0.07782 | 0.18768 | -0.050354 | -0.10986 | 0.054932 | 0.13275 | -0.073243 | -0.18768 | -0.3891 | -0.28839 | -0.21515 | -0.07782 | 122.9004 | 123.0331 | 61.5692 | -122.9187 | 122.7905 | 122.9004 | 61.5738 | -123.0515
136.25 | 123.2483 | -61.5005 | 61.4365 | 0.0054168 | -0.037311 | 0.11402 | 0.029288 | 0.05052 | -0.028867 | -0.024206 | -0.0003053 | -0.0062827 | 0.042176 | 0.060067 | -0.018936 | -0.01553 | 61.615 | -61.2534 | 0.15564 | -61.5234 | 61.3998 | -61.5326 | -61.4456 | -61.7981 | 0.16937 | -61.6928 | 61.3037 | 61.3632 | -61.3953 | -61.5829 | -0.032044 | 0.054931 | -0.036621 | 0.24719 | -0.022888 | -0.077819 | 0.17853 | 0.10529 | -0.082398 | -0.13275 | -0.29755 | -0.19226 | -0.10986 | -0.073242 | 122.9004 | 123.1155 | 61.6562 | -122.8821 | 122.8043 | 122.8638 | 61.6699 | -123.0194
137.9844 | 123.1155 | -61.5463 | 61.496 | -0.0098417 | -0.034321 | 0.11487 | 0.030997 | 0.051374 | -0.025662 | -0.024206 | -0.0003053 | -0.0041465 | 0.042176 | 0.061348 | -0.018295 | -0.015103 | 61.5601 | -61.3312 | 0.13275 | -61.5372 | 61.4365 | -61.5555 | -61.4456 | -61.8988 | 0.086975 | -61.821 | 61.3632 | 61.4273 | -61.3998 | -61.5875 | -0.009155 | 0.10071 | -0.05951 | 0.21515 | 0.009156 | -0.091552 | 0.064087 | 0.14648 | -0.041198 | -0.13275 | -0.35248 | -0.27466 | -0.23346 | -0.068665 | 122.9828 | 123.1064 | 61.6791 | -122.9416 | 122.9095 | 122.9736 | 61.6333 | -123.0835
139.7188 | 123.1476 | -61.5692 | 61.4227 | -0.0022127 | -0.031544 | 0.11359 | 0.02587 | 0.052656 | -0.021176 | -0.024419 | 0.0073242 | -0.00072845 | 0.042816 | 0.060921 | -0.014663 | -0.014035 | 61.5326 | -61.3632 | 0.07782 | -61.5646 | 61.4136 | -61.5829 | -61.5051 | -61.8759 | 0.086975 | -61.8301 | 61.3174 | 61.3861 | -61.4365 | -61.647 | -0.013733 | 0.064087 | -0.009155 | 0.20599 | 0.004578 | -0.059509 | 0.10986 | 0.13275 | -0.07782 | -0.10528 | -0.3067 | -0.26093 | -0.18311 | -0.036621 | 122.9828 | 123.1018 | 61.647 | -122.9279 | 122.8867 | 122.9553 | 61.6562 | -123.0698
141.4062 | 123.1705 | -61.528 | 61.4731 | 0.0054168 | -0.035389 | 0.11487 | 0.028647 | 0.052656 | -0.02609 | -0.02506 | -0.0079343 | -0.0069235 | 0.040894 | 0.061562 | -0.018295 | -0.012967 | 61.5921 | -61.2488 | 0.19684 | -61.5005 | 61.3998 | -61.5189 | -61.4182 | -61.8073 | 0.16022 | -61.7249 | 61.3174 | 61.3907 | -61.3724 | -61.5738 | 0.009155 | 0.10986 | -0.073242 | 0.27924 | 0.027466 | -0.082397 | 0.11902 | 0.15564 | -0.045777 | -0.15564 | -0.27924 | -0.19684 | -0.15106 | -0.082397 | 122.9279 | 123.1201 | 61.7249 | -122.8912 | 122.8455 | 122.9187 | 61.6882 | -123.0469
143.0781 | 123.1659 | -61.5601 | 61.4227 | -0.0098417 | -0.033466 | 0.11103 | 0.025443 | 0.052015 | -0.020963 | -0.022497 | 0.0073242 | -0.0028647 | 0.044739 | 0.06028 | -0.01509 | -0.015317 | 61.5326 | -61.3678 | 0.059509 | -61.5646 | 61.441 | -61.5784 | -61.5005 | -61.8988 | 0.10071 | -61.8393 | 61.3403 | 61.377 | -61.4365 | -61.6333 | -0.01831 | 0.05951 | 0.018311 | 0.19226 | -0.004577 | -0.064087 | 0.10986 | 0.1236 | -0.073242 | -0.082397 | -0.33874 | -0.27923 | -0.20599 | -0.045776 | 123.0011 | 123.0927 | 61.6196 | -122.9233 | 122.9004 | 122.937 | 61.6608 | -123.056
144.75 | 123.1293 | -61.5967 | 61.3815 | 0.013046 | -0.03902 | 0.11316 | 0.024588 | 0.05351 | -0.022031 | -0.022924 | -0.0003053 | -0.0017965 | 0.040894 | 0.059639 | -0.013595 | -0.014889 | 61.3998 | -61.4868 | -0.050354 | -61.6699 | 61.3861 | -61.6196 | -61.5463 | -61.9949 | -0.054932 | -61.9446 | 61.2854 | 61.3174 | -61.4685 | -61.6791 | -0.022888 | 0.050354 | 0.004577 | 0.10986 | -0.073242 | -0.1236 | 0.01831 | 0.12817 | -0.082397 | -0.096131 | -0.39825 | -0.3479 | -0.2655 | -0.064087 | 122.9828 | 122.9965 | 61.5463 | -122.9279 | 122.8821 | 122.9141 | 61.5417 | -123.0606
146.4375 | 123.23 | -61.528 | 61.4594 | -0.0022127 | -0.035602 | 0.11658 | 0.026297 | 0.052442 | -0.027585 | -0.024847 | -0.0003053 | -0.0060691 | 0.041321 | 0.059212 | -0.017227 | -0.012967 | 61.6013 | -61.2122 | 0.20599 | -61.4868 | 61.3815 | -61.5234 | -61.4548 | -61.8073 | 0.17853 | -61.6928 | 61.3037 | 61.3907 | -61.3724 | -61.5601 | 0.004578 | 0.073242 | -0.07782 | 0.31586 | 0.041199 | -0.032043 | 0.14191 | 0.15564 | -0.032044 | -0.15564 | -0.27924 | -0.16479 | -0.13275 | -0.068665 | 122.9095 | 123.1293 | 61.734 | -122.9141 | 122.8317 | 122.9187 | 61.7065 | -123.0194
148.1562 | 123.2758 | -61.4868 | 61.4365 | -0.0022127 | -0.038166 | 0.11445 | 0.02822 | 0.051801 | -0.030789 | -0.025274 | 0.0073242 | -0.0058555 | 0.043457 | 0.060067 | -0.018722 | -0.01254 | 61.5417 | -61.2991 | 0.10529 | -61.5143 | 61.4044 | -61.5417 | -61.4594 | -61.853 | 0.13733 | -61.7249 | 61.322 | 61.3678 | -61.3907 | -61.5692 | -0.054932 | 0.027465 | -0.032043 | 0.18768 | -0.027466 | -0.054931 | 0.10529 | 0.09613 | -0.082398 | -0.11444 | -0.36621 | -0.23804 | -0.15564 | -0.068664 | 122.8912 | 123.0286 | 61.5921 | -122.8958 | 122.8088 | 122.8546 | 61.6241 | -123.0057
149.875 | 123.1155 | -61.5646 | 61.4777 | 0.0054168 | -0.03368 | 0.11146 | 0.027792 | 0.052015 | -0.025876 | -0.023992 | 0.0073242 | -0.0047873 | 0.041107 | 0.060707 | -0.018081 | -0.013821 | 61.5234 | -61.3724 | 0.09613 | -61.5646 | 61.4319 | -61.5555 | -61.4914 | -61.8942 | 0.050354 | -61.8393 | 61.3861 | 61.441 | -61.3998 | -61.6058 | 0.009155 | 0.073242 | -0.045776 | 0.19226 | 0 | -0.073242 | 0.045776 | 0.16479 | -0.041199 | -0.091553 | -0.32959 | -0.27466 | -0.23346 | -0.036621 | 122.9965 | 123.0881 | 61.6608 | -122.9691 | 122.9507 | 123.0057 | 61.615 | -123.0835
151.5625 | 123.143 | -61.6058 | 61.3678 | 0.0054168 | -0.035175 | 0.11487 | 0.022238 | 0.054578 | -0.020108 | -0.022497 | -0.0003053 | -0.0011557 | 0.039612 | 0.060921 | -0.01274 | -0.014249 | 61.4136 | -61.4731 | -0.068665 | -61.6516 | 61.3815 | -61.6241 | -61.5372 | -61.9949 | -0.054932 | -61.9217 | 61.3037 | 61.3541 | -61.4685 | -61.6882 | -0.018311 | 0.068665 | 0.013733 | 0.13275 | -0.045776 | -0.11444 | 0.045776 | 0.13733 | -0.082397 | -0.064087 | -0.3891 | -0.31586 | -0.23346 | -0.013733 | 122.9874 | 123.0194 | 61.5372 | -122.905 | 122.9095 | 122.9599 | 61.5509 | -123.056
153.2344 | 123.175 | -61.5646 | 61.3632 | 0.0054168 | -0.037952 | 0.11423 | 0.024161 | 0.055433 | -0.024381 | -0.024206 | 0.0073242 | -0.0047873 | 0.038117 | 0.06028 | -0.01509 | -0.011899 | 61.5143 | -61.3358 | 0.050354 | -61.5692 | 61.2946 | -61.5738 | -61.5234 | -61.8622 | 0.082397 | -61.7844 | 61.2259 | 61.2854 | -61.4822 | -61.647 | -0.009156 | 0.041199 | -0.068664 | 0.22888 | -0.004578 | -0.045777 | 0.15106 | 0.082397 | -0.082398 | -0.13733 | -0.29755 | -0.21973 | -0.13733 | -0.07782 | 122.8592 | 123.0789 | 61.615 | -122.8867 | 122.7905 | 122.85 | 61.647 | -123.0103
154.9062 | 123.262 | -61.4914 | 61.4227 | -0.0022127 | -0.038166 | 0.11594 | 0.027365 | 0.052442 | -0.028867 | -0.026342 | 0.014954 | -0.0075645 | 0.040894 | 0.061135 | -0.019363 | -0.013394 | 61.5417 | -61.3083 | 0.10986 | -61.5326 | 61.3861 | -61.5509 | -61.4456 | -61.8484 | 0.10986 | -61.7294 | 61.2808 | 61.3815 | -61.3907 | -61.5967 | -0.059509 | 0.045776 | -0.036621 | 0.1831 | -0.041199 | -0.086975 | 0.11902 | 0.10071 | -0.10529 | -0.14191 | -0.35706 | -0.23804 | -0.13275 | -0.041198 | 122.8775 | 123.0331 | 61.6013 | -122.8683 | 122.7722 | 122.8729 | 61.6013 | -123.0194
156.5938 | 123.111 | -61.5555 | 61.3815 | -0.017471 | -0.037739 | 0.11338 | 0.022665 | 0.053297 | -0.020749 | -0.019933 | 0.0073242 | -0.0020103 | 0.040894 | 0.059853 | -0.01509 | -0.013821 | 61.5326 | -61.3632 | 0.073242 | -61.5738 | 61.3953 | -61.5738 | -61.4868 | -61.8668 | 0.10071 | -61.8347 | 61.2991 | 61.3449 | -61.4273 | -61.647 | -0.018311 | 0.068665 | 0.013733 | 0.19226 | -0.018311 | -0.086976 | 0.15106 | 0.12817 | -0.091553 | -0.082398 | -0.31128 | -0.27924 | -0.18768 | -0.036621 | 122.9507 | 123.0881 | 61.6287 | -122.8683 | 122.8546 | 122.9004 | 61.6562 | -123.0286
158.3281 | 123.143 | -61.5372 | 61.4319 | 0.0054168 | -0.036243 | 0.11423 | 0.02587 | 0.052015 | -0.02139 | -0.022924 | -0.0003053 | -0.0041465 | 0.042389 | 0.060494 | -0.013168 | -0.012112 | 61.5005 | -61.3632 | 0.073242 | -61.5601 | 61.4227 | -61.5738 | -61.5097 | -61.8851 | 0.09613 | -61.8256 | 61.322 | 61.3541 | -61.441 | -61.6379 | -0.036622 | 0.027465 | -0.009156 | 0.17395 | -0.022889 | -0.050354 | 0.068664 | 0.09613 | -0.10071 | -0.10986 | -0.3479 | -0.28839 | -0.18768 | -0.07782 | 122.9599 | 123.0377 | 61.6104 | -122.9416 | 122.8592 | 122.8912 | 61.6333 | -123.0698
160.0156 | 123.2346 | -61.5601 | 61.3495 | -0.0022127 | -0.03603 | 0.11402 | 0.026297 | 0.049665 | -0.021604 | -0.022069 | 0.0073242 | -0.0047873 | 0.04303 | 0.059639 | -0.01509 | -0.011899 | 61.4365 | -61.4365 | -0.045776 | -61.6379 | 61.3495 | -61.6333 | -61.5189 | -61.9217 | 0 | -61.8484 | 61.2396 | 61.3174 | -61.441 | -61.6653 | -0.073242 | 0.041199 | 0 | 0.1236 | -0.077819 | -0.11902 | 0.086975 | 0.11902 | -0.10528 | -0.10986 | -0.36163 | -0.28839 | -0.18311 | -0.032043 | 122.9095 | 122.9965 | 61.5143 | -122.8683 | 122.7997 | 122.8775 | 61.5601 | -123.0148
161.6875 | 123.1613 | -61.5234 | 61.3953 | 0.0054168 | -0.038807 | 0.11722 | 0.022879 | 0.052442 | -0.028012 | -0.023778 | -0.0003053 | -0.0069235 | 0.038544 | 0.059853 | -0.017867 | -0.010617 | 61.5051 | -61.3174 | 0.054932 | -61.5784 | 61.3174 | -61.5921 | -61.4914 | -61.8988 | 0.045776 | -61.7889 | 61.2305 | 61.3129 | -61.4182 | -61.6058 | -0.068665 | 0.032043 | -0.07782 | 0.20599 | -0.054932 | -0.086975 | 0.10986 | 0.10529 | -0.082398 | -0.16479 | -0.37537 | -0.2655 | -0.1831 | -0.082398 | 122.8409 | 123.0286 | 61.5784 | -122.8867 | 122.7539 | 122.8363 | 61.5692 | -123.0011
163.4219 | 123.1659 | -61.528 | 61.4182 | 0.0054168 | -0.039875 | 0.11509 | 0.02587 | 0.053938 | -0.026731 | -0.024206 | -0.0003053 | -0.0050009 | 0.038758 | 0.06028 | -0.016799 | -0.011899 | 61.5005 | -61.3312 | 0.059509 | -61.5784 | 61.3129 | -61.5601 | -61.4868 | -61.8942 | 0.050354 | -61.7981 | 61.2305 | 61.3037 | -61.409 | -61.615 | -0.032044 | 0.041199 | -0.10529 | 0.19684 | -0.050354 | -0.091553 | 0.082397 | 0.11902 | -0.086975 | -0.18768 | -0.36621 | -0.27008 | -0.18311 | -0.11444 | 122.8409 | 123.0286 | 61.5875 | -122.905 | 122.7585 | 122.8317 | 61.5784 | -123.0331
165.1562 | 123.1659 | -61.5555 | 61.3907 | 0.013046 | -0.040302 | 0.11466 | 0.026724 | 0.05052 | -0.026517 | -0.024847 | -0.0003053 | -0.0045737 | 0.038544 | 0.060707 | -0.01509 | -0.014462 | 61.5234 | -61.3266 | 0.064087 | -61.5646 | 61.3083 | -61.5829 | -61.496 | -61.8622 | 0.082397 | -61.7798 | 61.2259 | 61.2946 | -61.4182 | -61.647 | -0.027466 | 0.059509 | -0.082397 | 0.22888 | -0.009155 | -0.068664 | 0.13275 | 0.13733 | -0.091553 | -0.1648 | -0.3067 | -0.2243 | -0.13275 | -0.09613 | 122.8638 | 123.0789 | 61.6196 | -122.8867 | 122.7814 | 122.85 | 61.6379 | -123.0377
166.9375 | 123.23 | -61.5051 | 61.4227 | 0.0054168 | -0.043079 | 0.11573 | 0.022452 | 0.05052 | -0.026517 | -0.023565 | 0.0073242 | -0.0067099 | 0.038544 | 0.059426 | -0.018508 | -0.014249 | 61.528 | -61.2808 | 0.091553 | -61.528 | 61.3907 | -61.5417 | -61.4594 | -61.853 | 0.11444 | -61.7249 | 61.2991 | 61.3403 | -61.377 | -61.5646 | -0.036621 | 0.045776 | -0.032043 | 0.2243 | -0.022888 | -0.068664 | 0.10529 | 0.12817 | -0.059509 | -0.1236 | -0.3479 | -0.21973 | -0.16022 | -0.082397 | 122.8958 | 123.0331 | 61.5967 | -122.8821 | 122.8043 | 122.8455 | 61.6196 | -122.9874
168.8281 | 123.0972 | -61.5234 | 61.4731 | 0.0054168 | -0.033253 | 0.11487 | 0.030356 | 0.052656 | -0.022885 | -0.023778 | 0.014954 | -0.0015829 | 0.039398 | 0.059639 | -0.016158 | -0.011899 | 61.5143 | -61.377 | 0.073242 | -61.5646 | 61.4456 | -61.5417 | -61.4594 | -61.908 | 0.059509 | -61.821 | 61.3861 | 61.4273 | -61.3953 | -61.6058 | -0.018311 | 0.064086 | -0.027465 | 0.14648 | -0.041199 | -0.10529 | 0.041199 | 0.12817 | -0.082398 | -0.086975 | -0.38452 | -0.29755 | -0.21515 | -0.045776 | 122.9691 | 123.0377 | 61.5967 | -122.9324 | 122.9095 | 122.9507 | 61.5829 | -123.0789
170.8281 | 123.1659 | -61.4914 | 61.4594 | 0.0054168 | -0.038166 | 0.11445 | 0.02886 | 0.053297 | -0.024808 | -0.023992 | 0.0073242 | -0.0073507 | 0.04068 | 0.06028 | -0.020645 | -0.015317 | 61.5967 | -61.2259 | 0.19684 | -61.4685 | 61.3861 | -61.5005 | -61.4227 | -61.7889 | 0.17395 | -61.7065 | 61.2854 | 61.3678 | -61.3632 | -61.5372 | -0.009155 | 0.068665 | -0.073243 | 0.2655 | 0.022888 | -0.045777 | 0.13733 | 0.12817 | -0.045776 | -0.17395 | -0.29755 | -0.21515 | -0.16937 | -0.091553 | 122.8775 | 123.0881 | 61.6882 | -122.8821 | 122.7768 | 122.8592 | 61.6653 | -122.9965
173.0156 | 123.1796 | -61.5326 | 61.409 | -0.0022127 | -0.037952 | 0.11744 | 0.025015 | 0.050733 | -0.026944 | -0.023778 | 0.0073242 | -0.0054281 | 0.04068 | 0.058785 | -0.016372 | -0.012753 | 61.496 | -61.3266 | 0.059509 | -61.5646 | 61.3541 | -61.5509 | -61.4548 | -61.8896 | 0.036621 | -61.8027 | 61.2625 | 61.3174 | -61.3998 | -61.5921 | -0.01831 | 0.07782 | -0.054932 | 0.20599 | -0.032043 | -0.10986 | 0.086975 | 0.13275 | -0.059509 | -0.14648 | -0.35706 | -0.27008 | -0.21057 | -0.091553 | 122.8867 | 123.0286 | 61.5921 | -122.8638 | 122.7951 | 122.85 | 61.5692 | -123.0011
174.7656 | 123.1384 | -61.5509 | 61.4319 | 0.0054168 | -0.033039 | 0.11381 | 0.028433 | 0.051374 | -0.019681 | -0.021001 | -0.0003053 | -0.0017965 | 0.041962 | 0.059426 | -0.013595 | -0.014676 | 61.5234 | -61.3403 | 0.073242 | -61.5372 | 61.4227 | -61.5509 | -61.496 | -61.8622 | 0.086975 | -61.8164 | 61.322 | 61.3541 | -61.4273 | -61.615 | 0 | 0.054931 | -0.009156 | 0.21057 | 0.013733 | -0.041198 | 0.091552 | 0.1236 | -0.064087 | -0.10986 | -0.31128 | -0.2655 | -0.20142 | -0.07782 | 122.9736 | 123.0743 | 61.6241 | -122.9279 | 122.8729 | 122.905 | 61.6379 | -123.0469
176.7656 | 123.143 | -61.5417 | 61.3724 | 0.0054168 | -0.035816 | 0.11573 | 0.026083 | 0.052869 | -0.027799 | -0.022924 | 0.0073242 | -0.0069235 | 0.04068 | 0.058571 | -0.016799 | -0.012326 | 61.5051 | -61.3174 | 0.054932 | -61.5646 | 61.3541 | -61.5784 | -61.4685 | -61.8805 | 0.032043 | -61.7981 | 61.2534 | 61.322 | -61.4044 | -61.615 | -0.036621 | 0.073242 | -0.01831 | 0.2243 | -0.022888 | -0.09613 | 0.13275 | 0.13733 | -0.073242 | -0.11902 | -0.33875 | -0.25635 | -0.18311 | -0.050354 | 122.8958 | 123.0469 | 61.5967 | -122.8409 | 122.7951 | 122.8638 | 61.5738 | -122.9874
179.6094 | 123.0789 | -61.5738 | 61.3815 | 0.0054168 | -0.032398 | 0.11316 | 0.028647 | 0.052442 | -0.019467 | -0.021642 | -0.0003053 | -0.0017965 | 0.043244 | 0.061562 | -0.017013 | -0.01254 | 61.5051 | -61.322 | 0.091553 | -61.5463 | 61.409 | -61.5829 | -61.5143 | -61.8439 | 0.10071 | -61.8256 | 61.3129 | 61.322 | -61.4273 | -61.6241 | -0.009155 | 0.05951 | 0.027466 | 0.25177 | 0.027466 | -0.032044 | 0.1236 | 0.14648 | -0.050354 | -0.068665 | -0.27008 | -0.25177 | -0.20142 | -0.05951 | 122.9828 | 123.0789 | 61.6653 | -122.8958 | 122.8867 | 122.8958 | 61.6745 | -123.0057
181.3125 | 123.1201 | -61.5372 | 61.4227 | -0.0098417 | -0.032612 | 0.11188 | 0.02822 | 0.052869 | -0.020749 | -0.021856 | 0.0073242 | -0.0020103 | 0.043244 | 0.060494 | -0.014877 | -0.014035 | 61.5097 | -61.3312 | 0.082397 | -61.5326 | 61.409 | -61.5738 | -61.4822 | -61.8622 | 0.10529 | -61.8164 | 61.3174 | 61.3724 | -61.3998 | -61.6058 | -0.036622 | 0.054931 | -0.013732 | 0.20599 | 0.004577 | -0.050354 | 0.086976 | 0.13733 | -0.068665 | -0.10528 | -0.32501 | -0.27924 | -0.21057 | -0.050354 | 122.9462 | 123.0469 | 61.6196 | -122.905 | 122.8546 | 122.9095 | 61.6425 | -123.0286
183 | 123.0606 | -61.5005 | 61.4502 | 0.0054168 | -0.035602 | 0.11252 | 0.029501 | 0.053938 | -0.025662 | -0.023351 | 0.014954 | -0.0043601 | 0.042603 | 0.06028 | -0.018081 | -0.014249 | 61.5097 | -61.29 | 0.14191 | -61.5051 | 61.409 | -61.5051 | -61.4365 | -61.8851 | 0.082397 | -61.7844 | 61.322 | 61.409 | -61.409 | -61.5601 | -0.004578 | 0.064087 | -0.041198 | 0.21057 | -0.004578 | -0.068665 | 0.05951 | 0.091552 | -0.05951 | -0.12817 | -0.38452 | -0.28381 | -0.2243 | -0.041198 | 122.9095 | 123.0103 | 61.6425 | -122.8867 | 122.8226 | 122.9095 | 61.5829 | -123.0103
184.7188 | 123.1155 | -61.528 | 61.4365 | -0.0098417 | -0.032184 | 0.11359 | 0.028006 | 0.052229 | -0.020749 | -0.022283 | 0.014954 | -0.0045737 | 0.042176 | 0.059853 | -0.017227 | -0.01318 | 61.4731 | -61.3541 | 0.059509 | -61.5555 | 61.4273 | -61.5555 | -61.4594 | -61.8668 | 0.082397 | -61.821 | 61.322 | 61.3724 | -61.3861 | -61.6104 | -0.027466 | 0.068664 | -0.009155 | 0.17395 | -0.027466 | -0.09613 | 0.036621 | 0.14191 | -0.082398 | -0.11444 | -0.33874 | -0.29297 | -0.21057 | -0.064087 | 122.9553 | 123.0011 | 61.5875 | -122.8958 | 122.85 | 122.9004 | 61.6104 | -123.0469
186.4062 | 123.0789 | -61.5143 | 61.4456 | -0.0022127 | -0.036884 | 0.11402 | 0.023947 | 0.056074 | -0.025235 | -0.024206 | 0.0073242 | -0.0028647 | 0.040039 | 0.059426 | -0.018508 | -0.011471 | 61.4594 | -61.3449 | 0.082397 | -61.5555 | 61.4182 | -61.5372 | -61.4365 | -61.9034 | 0.082397 | -61.821 | 61.3586 | 61.4136 | -61.3953 | -61.5875 | -0.022888 | 0.07782 | -0.027466 | 0.16937 | -0.041199 | -0.11902 | 0.013733 | 0.11902 | -0.073242 | -0.086975 | -0.3891 | -0.3067 | -0.23346 | -0.032044 | 122.9324 | 122.9736 | 61.5967 | -122.8821 | 122.8729 | 122.9279 | 61.5967 | -123.0331
188.0938 | 123.1979 | -61.4685 | 61.4136 | 0.0054168 | -0.039875 | 0.11722 | 0.027579 | 0.052869 | -0.030149 | -0.024633 | -0.0003053 | -0.0062827 | 0.040039 | 0.058785 | -0.019149 | -0.012967 | 61.4502 | -61.2946 | 0.059509 | -61.5326 | 61.3907 | -61.5326 | -61.4456 | -61.8622 | 0.10071 | -61.7477 | 61.2625 | 61.3495 | -61.3815 | -61.5784 | -0.064087 | 0.022888 | -0.022888 | 0.17395 | -0.064087 | -0.086975 | 0.036621 | 0.086975 | -0.10986 | -0.15106 | -0.39368 | -0.27924 | -0.16937 | -0.064087 | 122.8592 | 122.9187 | 61.528 | -122.8592 | 122.731 | 122.818 | 61.5692 | -122.9919
189.7812 | 123.0606 | -61.5051 | 61.4731 | 0.0054168 | -0.036671 | 0.11487 | 0.029074 | 0.052656 | -0.026303 | -0.025274 | 0.0073242 | -0.0045737 | 0.041321 | 0.06028 | -0.018081 | -0.012326 | 61.5601 | -61.2259 | 0.16937 | -61.4594 | 61.4044 | -61.5005 | -61.4319 | -61.8301 | 0.14648 | -61.7294 | 61.322 | 61.3907 | -61.3678 | -61.5784 | 0.004578 | 0.073242 | -0.068664 | 0.27924 | 0.045776 | -0.027466 | 0.086976 | 0.13733 | -0.073242 | -0.15106 | -0.32501 | -0.2243 | -0.15106 | -0.082397 | 122.9095 | 123.0652 | 61.6745 | -122.905 | 122.8271 | 122.8958 | 61.6516 | -123.0515
191.4531 | 123.1293 | -61.5234 | 61.3998 | 0.0054168 | -0.035175 | 0.11274 | 0.026724 | 0.053083 | -0.020963 | -0.022283 | -0.0003053 | -0.0035055 | 0.041748 | 0.061348 | -0.017227 | -0.015317 | 61.4868 | -61.3358 | 0.068665 | -61.5372 | 61.4273 | -61.5234 | -61.4731 | -61.8668 | 0.07782 | -61.8256 | 61.3495 | 61.3724 | -61.4136 | -61.5967 | 0 | 0.050354 | 0.027466 | 0.18768 | -0.013733 | -0.064087 | 0.086975 | 0.10986 | -0.073243 | -0.050354 | -0.34332 | -0.30212 | -0.22888 | -0.027466 | 122.9507 | 123.0103 | 61.5921 | -122.8729 | 122.8729 | 122.8958 | 61.6013 | -122.9965
193.1406 | 123.0743 | -61.5005 | 61.4731 | -0.0022127 | -0.034748 | 0.11423 | 0.030356 | 0.049879 | -0.024594 | -0.026342 | 0.0073242 | -0.0030783 | 0.043244 | 0.062203 | -0.017867 | -0.013394 | 61.4685 | -61.3312 | 0.073242 | -61.5463 | 61.4273 | -61.5463 | -61.4365 | -61.8805 | 0.059509 | -61.7981 | 61.3678 | 61.3953 | -61.3953 | -61.5967 | -0.045777 | 0.064087 | -0.045776 | 0.16937 | -0.045777 | -0.10986 | -0.004577 | 0.10529 | -0.096131 | -0.10529 | -0.37994 | -0.29755 | -0.20142 | -0.077819 | 122.9279 | 122.9691 | 61.5738 | -122.9095 | 122.8683 | 122.8958 | 61.5601 | -123.0698
194.875 | 123.1567 | -61.4868 | 61.4365 | -0.0022127 | -0.036884 | 0.11445 | 0.02822 | 0.052015 | -0.029721 | -0.023138 | -0.0079343 | -0.0064963 | 0.041535 | 0.057076 | -0.018936 | -0.013394 | 61.5875 | -61.1847 | 0.1831 | -61.4639 | 61.3724 | -61.4868 | -61.4227 | -61.7661 | 0.19226 | -61.6653 | 61.2762 | 61.3358 | -61.3403 | -61.5646 | 0 | 0.064087 | -0.064087 | 0.30212 | 0.022888 | -0.041199 | 0.15106 | 0.14648 | -0.07782 | -0.16022 | -0.27924 | -0.17853 | -0.10071 | -0.10071 | 122.8592 | 123.0743 | 61.6699 | -122.8592 | 122.7631 | 122.8226 | 61.6791 | -123.0011
196.5625 | 123.1384 | -61.5143 | 61.4044 | 0.0054168 | -0.038593 | 0.11616 | 0.023734 | 0.054365 | -0.025662 | -0.024847 | 0.0073242 | -0.0032919 | 0.039398 | 0.05793 | -0.017227 | -0.010831 | 61.4822 | -61.2991 | 0.059509 | -61.5646 | 61.2946 | -61.5417 | -61.4594 | -61.853 | 0.050354 | -61.7706 | 61.2259 | 61.3037 | -61.3815 | -61.6104 | -0.027466 | 0.054931 | -0.10986 | 0.21515 | -0.050354 | -0.10529 | 0.07782 | 0.13275 | -0.096131 | -0.17853 | -0.33874 | -0.25635 | -0.16022 | -0.10071 | 122.8088 | 122.9965 | 61.5738 | -122.8638 | 122.7402 | 122.818 | 61.5646 | -123.0148
198.2344 | 123.0606 | -61.496 | 61.4639 | 0.0054168 | -0.035389 | 0.11487 | 0.027792 | 0.053083 | -0.024594 | -0.024633 | 0.0073242 | -0.0030783 | 0.041535 | 0.058999 | -0.017654 | -0.012967 | 61.5509 | -61.2488 | 0.15106 | -61.4914 | 61.409 | -61.5051 | -61.4365 | -61.8622 | 0.091553 | -61.7615 | 61.3449 | 61.3541 | -61.3632 | -61.5646 | -0.009155 | 0.05951 | -0.054931 | 0.24719 | 0.004578 | -0.054932 | 0.086975 | 0.13275 | -0.068664 | -0.11902 | -0.36621 | -0.2655 | -0.19684 | -0.10986 | 122.905 | 123.0469 | 61.647 | -122.9004 | 122.8409 | 122.85 | 61.5875 | -123.0286
199.9219 | 123.1476 | -61.5005 | 61.377 | -0.0022127 | -0.037525 | 0.1153 | 0.026297 | 0.05351 | -0.025022 | -0.024847 | -0.0003053 | -0.0054281 | 0.037476 | 0.06028 | -0.016158 | -0.012326 | 61.4914 | -61.3037 | 0.059509 | -61.5463 | 61.3129 | -61.5555 | -61.4731 | -61.8713 | 0.054932 | -61.7798 | 61.2488 | 61.2854 | -61.3678 | -61.6013 | -0.054932 | 0.027466 | -0.064087 | 0.19684 | -0.045777 | -0.073243 | 0.11444 | 0.13275 | -0.10071 | -0.12817 | -0.37079 | -0.27924 | -0.17853 | -0.091553 | 122.8134 | 122.9919 | 61.5601 | -122.85 | 122.7493 | 122.7859 | 61.5555 | -122.9782
201.625 | 123.1293 | -61.4594 | 61.4319 | -0.0022127 | -0.037952 | 0.11637 | 0.027792 | 0.052656 | -0.026944 | -0.02271 | 0.0073242 | -0.0039329 | 0.041748 | 0.059639 | -0.015945 | -0.014249 | 61.5784 | -61.1984 | 0.18768 | -61.4594 | 61.3815 | -61.4731 | -61.4182 | -61.7706 | 0.16479 | -61.6837 | 61.2625 | 61.3541 | -61.3266 | -61.5509 | -0.013732 | 0.041199 | -0.050354 | 0.26093 | 0 | -0.041199 | 0.14648 | 0.13275 | -0.091552 | -0.16937 | -0.31128 | -0.2243 | -0.13275 | -0.07782 | 122.8409 | 123.0377 | 61.647 | -122.85 | 122.7219 | 122.8134 | 61.6241 | -122.9828
203.3281 | 123.0286 | -61.5463 | 61.3953 | 0.013046 | -0.035602 | 0.1121 | 0.02352 | 0.050092 | -0.021176 | -0.022924 | -0.0003053 | -0.00072845 | 0.04303 | 0.061135 | -0.014236 | -0.012753 | 61.4868 | -61.322 | 0.054932 | -61.5646 | 61.3815 | -61.5784 | -61.4731 | -61.8759 | 0.045776 | -61.8759 | 61.2762 | 61.3266 | -61.4502 | -61.6379 | -0.032043 | 0.073243 | -0.013733 | 0.22431 | -0.01831 | -0.091553 | 0.091552 | 0.096131 | -0.091552 | -0.11902 | -0.32959 | -0.32959 | -0.23804 | -0.068665 | 122.9279 | 123.0331 | 61.6013 | -122.8683 | 122.8226 | 122.8729 | 61.5921 | -123.0331
205.0156 | 123.143 | -61.5234 | 61.3266 | -0.0022127 | -0.036884 | 0.11359 | 0.024374 | 0.053724 | -0.025876 | -0.024633 | -0.0003053 | -0.0060691 | 0.041107 | 0.059426 | -0.014663 | -0.012967 | 61.4868 | -61.3037 | 0.059509 | -61.5509 | 61.29 | -61.5692 | -61.5005 | -61.8256 | 0.07782 | -61.7569 | 61.1938 | 61.2625 | -61.377 | -61.6196 | -0.045777 | 0.022888 | -0.036621 | 0.21973 | -0.027466 | -0.050354 | 0.16022 | 0.14648 | -0.096131 | -0.13275 | -0.30212 | -0.23346 | -0.13733 | -0.064087 | 122.8134 | 123.0103 | 61.5829 | -122.8271 | 122.7173 | 122.7859 | 61.6013 | -122.9462
206.7188 | 123.1705 | -61.5326 | 61.3632 | -0.0098417 | -0.034534 | 0.11252 | 0.02587 | 0.051588 | -0.023953 | -0.023138 | -0.0003053 | -0.0022239 | 0.039185 | 0.060494 | -0.017867 | -0.013394 | 61.4273 | -61.4136 | -0.050354 | -61.6241 | 61.3403 | -61.5921 | -61.5143 | -61.908 | -0.027466 | -61.8484 | 61.2167 | 61.2762 | -61.4594 | -61.6241 | -0.059509 | 0.018311 | -0.022888 | 0.11902 | -0.091553 | -0.10986 | 0.064087 | 0.073242 | -0.091553 | -0.14648 | -0.37537 | -0.31586 | -0.2243 | -0.086975 | 122.8729 | 122.9599 | 61.4822 | -122.8775 | 122.7493 | 122.8088 | 61.5051 | -122.9874
208.4688 | 123.056 | -61.5784 | 61.3907 | -0.0022127 | -0.035602 | 0.11295 | 0.023947 | 0.05052 | -0.020963 | -0.021001 | 0.014954 | -0.0013693 | 0.039185 | 0.061989 | -0.013595 | -0.011685 | 61.3998 | -61.4273 | -0.036621 | -61.6058 | 61.3632 | -61.5875 | -61.5097 | -61.9629 | -0.036621 | -61.9308 | 61.2671 | 61.29 | -61.4319 | -61.6425 | -0.009155 | 0.068664 | -0.027466 | 0.15106 | -0.027466 | -0.09613 | 0.009155 | 0.14648 | -0.064087 | -0.1236 | -0.38452 | -0.35248 | -0.28839 | -0.10071 | 122.9416 | 122.9782 | 61.5417 | -122.9004 | 122.8455 | 122.8683 | 61.5417 | -123.0331
210.1719 | 123.056 | -61.5875 | 61.3632 | 0.0054168 | -0.037739 | 0.11423 | 0.025656 | 0.054365 | -0.021604 | -0.020788 | 0.0073242 | -0.0047873 | 0.041748 | 0.061135 | -0.01509 | -0.011685 | 61.3907 | -61.4365 | -0.041199 | -61.6196 | 61.3632 | -61.5875 | -61.5143 | -61.972 | -0.032043 | -61.9354 | 61.2534 | 61.3129 | -61.4365 | -61.6196 | 0 | 0.073242 | 0 | 0.15106 | -0.032044 | -0.10529 | 0.027466 | 0.15106 | -0.032044 | -0.10986 | -0.38452 | -0.3479 | -0.31586 | -0.050354 | 122.9507 | 122.9782 | 61.5463 | -122.8775 | 122.8409 | 122.9004 | 61.5555 | -122.9828
211.9062 | 123.0881 | -61.5005 | 61.409 | -0.0022127 | -0.033893 | 0.1121 | 0.02822 | 0.05351 | -0.024381 | -0.021642 | -0.0003053 | -0.0039329 | 0.04303 | 0.061135 | -0.017654 | -0.011471 | 61.4639 | -61.3312 | 0.086975 | -61.5234 | 61.3953 | -61.5555 | -61.4822 | -61.8576 | 0.10071 | -61.7844 | 61.2717 | 61.3083 | -61.3953 | -61.5967 | -0.054932 | 0.01831 | -0.013733 | 0.16937 | -0.022888 | -0.041198 | 0.054931 | 0.10529 | -0.096131 | -0.13733 | -0.35706 | -0.28381 | -0.18768 | -0.10071 | 122.8958 | 122.9645 | 61.5875 | -122.8912 | 122.7722 | 122.8088 | 61.6013 | -123.0057
213.5781 | 123.1522 | -61.4731 | 61.3907 | -0.0022127 | -0.039448 | 0.11466 | 0.027579 | 0.050733 | -0.029294 | -0.023138 | -0.0003053 | -0.0075645 | 0.041535 | 0.060494 | -0.020004 | -0.010617 | 61.4273 | -61.3037 | 0.045776 | -61.5372 | 61.322 | -61.5509 | -61.441 | -61.8988 | 0.027466 | -61.7569 | 61.2442 | 61.3129 | -61.3907 | -61.5875 | -0.07782 | 0.032043 | -0.068665 | 0.16937 | -0.064087 | -0.09613 | 0.036621 | 0.082397 | -0.11444 | -0.14648 | -0.42572 | -0.28381 | -0.16937 | -0.07782 | 122.7951 | 122.9004 | 61.5189 | -122.8317 | 122.7173 | 122.7859 | 61.5005 | -122.9782
215.2812 | 123.0835 | -61.5051 | 61.4319 | -0.0022127 | -0.032612 | 0.11594 | 0.029288 | 0.052442 | -0.023099 | -0.024633 | -0.0003053 | -0.0024375 | 0.040467 | 0.059212 | -0.017227 | -0.015103 | 61.4548 | -61.3403 | 0.068665 | -61.5463 | 61.4136 | -61.5326 | -61.4639 | -61.8851 | 0.059509 | -61.8256 | 61.322 | 61.3632 | -61.3815 | -61.5875 | -0.027466 | 0.041199 | -0.018311 | 0.1648 | -0.041199 | -0.082398 | 0.022888 | 0.1236 | -0.082397 | -0.10986 | -0.37994 | -0.32043 | -0.23804 | -0.068665 | 122.9187 | 122.9599 | 61.5738 | -122.8958 | 122.8271 | 122.8683 | 61.5646 | -123.0194
217.0156 | 123.0515 | -61.5097 | 61.4502 | 0.0054168 | -0.039661 | 0.11381 | 0.02886 | 0.053724 | -0.026303 | -0.024633 | 0.0073242 | -0.0043601 | 0.041107 | 0.060921 | -0.017867 | -0.013394 | 61.4685 | -61.3129 | 0.086975 | -61.528 | 61.4136 | -61.5005 | -61.4365 | -61.8896 | 0.064087 | -61.7798 | 61.3266 | 61.3678 | -61.3632 | -61.5738 | 0.009156 | 0.073243 | -0.036621 | 0.19684 | -0.01831 | -0.091553 | 0.018311 | 0.14648 | -0.064087 | -0.1236 | -0.37994 | -0.27008 | -0.20599 | -0.082397 | 122.9233 | 122.9782 | 61.5967 | -122.8867 | 122.8363 | 122.8775 | 61.5738 | -123.024
218.7031 | 123.1659 | -61.5143 | 61.3037 | 0.013046 | -0.038166 | 0.11551 | 0.025229 | 0.05351 | -0.024594 | -0.023778 | 0.0073242 | -0.0026511 | 0.04303 | 0.061776 | -0.01509 | -0.012967 | 61.4365 | -61.3449 | -0.004578 | -61.5601 | 61.29 | -61.5875 | -61.4594 | -61.8713 | 0.050354 | -61.7798 | 61.1984 | 61.2396 | -61.409 | -61.6379 | -0.073242 | 0.054931 | -0.013733 | 0.16937 | -0.045777 | -0.10071 | 0.13275 | 0.10529 | -0.1236 | -0.10529 | -0.35706 | -0.2655 | -0.14191 | -0.064087 | 122.8043 | 122.9507 | 61.5097 | -122.7631 | 122.7127 | 122.7539 | 61.5646 | -122.9416
220.4062 | 123.0743 | -61.5509 | 61.3449 | -0.0022127 | -0.037739 | 0.11316 | 0.026297 | 0.050947 | -0.022458 | -0.021642 | -0.0003053 | -0.0032919 | 0.040467 | 0.058785 | -0.014877 | -0.014249 | 61.3861 | -61.4319 | -0.064087 | -61.6013 | 61.3266 | -61.5784 | -61.5097 | -61.9537 | -0.050354 | -61.8988 | 61.2259 | 61.3129 | -61.4456 | -61.6562 | -0.027466 | 0.041198 | -0.018311 | 0.11902 | -0.050354 | -0.091552 | 0.041198 | 0.10528 | -0.10529 | -0.11902 | -0.40283 | -0.3479 | -0.24262 | -0.032044 | 122.8775 | 122.937 | 61.4868 | -122.8546 | 122.7768 | 122.8638 | 61.5005 | -123.0011
222.0938 | 123.1522 | -61.4685 | 61.4136 | -0.0098417 | -0.037739 | 0.11445 | 0.030783 | 0.049665 | -0.027585 | -0.024847 | -0.0003053 | -0.0088461 | 0.043457 | 0.059212 | -0.019363 | -0.012112 | 61.5417 | -61.1801 | 0.17395 | -61.4456 | 61.3358 | -61.4868 | -61.3907 | -61.7844 | 0.17853 | -61.6653 | 61.2579 | 61.3266 | -61.3174 | -61.528 | -0.01831 | 0.07782 | -0.07782 | 0.28839 | 0.022888 | -0.054932 | 0.12817 | 0.15106 | -0.059509 | -0.15564 | -0.31586 | -0.19684 | -0.13733 | -0.086975 | 122.8043 | 123.0103 | 61.6425 | -122.8043 | 122.7264 | 122.7951 | 61.647 | -122.9416
223.7969 | 123.0515 | -61.5143 | 61.3953 | -0.0022127 | -0.033466 | 0.11359 | 0.026724 | 0.054151 | -0.020535 | -0.022283 | -0.0003053 | -0.0022239 | 0.04303 | 0.06028 | -0.014877 | -0.012967 | 61.4868 | -61.322 | 0.086975 | -61.528 | 61.3586 | -61.5326 | -61.4548 | -61.8301 | 0.10986 | -61.7935 | 61.2808 | 61.3403 | -61.3724 | -61.6058 | -0.018311 | 0.059509 | -0.036621 | 0.19226 | -0.013733 | -0.073242 | 0.091552 | 0.14191 | -0.091553 | -0.11444 | -0.31586 | -0.27924 | -0.18768 | -0.054932 | 122.8729 | 123.0011 | 61.6013 | -122.85 | 122.7951 | 122.8546 | 61.6241 | -123.0011
225.4688 | 123.0881 | -61.4548 | 61.4319 | -0.0022127 | -0.037525 | 0.11487 | 0.028433 | 0.051161 | -0.029294 | -0.023351 | 0.014954 | -0.0067099 | 0.039185 | 0.061348 | -0.018295 | -0.014462 | 61.5463 | -61.1847 | 0.19226 | -61.4273 | 61.3403 | -61.4868 | -61.3998 | -61.7798 | 0.16022 | -61.6653 | 61.2534 | 61.3083 | -61.3495 | -61.528 | -0.032043 | 0.054932 | -0.091553 | 0.27008 | 0.027466 | -0.027466 | 0.11444 | 0.10529 | -0.073242 | -0.17853 | -0.32501 | -0.21057 | -0.13733 | -0.1236 | 122.7951 | 123.0011 | 61.647 | -122.8317 | 122.7081 | 122.7631 | 61.615 | -122.9599
227.2031 | 123.1155 | -61.4548 | 61.4044 | -0.0022127 | -0.03902 | 0.11744 | 0.027579 | 0.052656 | -0.028653 | -0.025274 | -0.0003053 | -0.0084189 | 0.041535 | 0.058144 | -0.018936 | -0.01318 | 61.4548 | -61.29 | 0.036621 | -61.528 | 61.322 | -61.5189 | -61.4456 | -61.8668 | 0.032043 | -61.7569 | 61.2579 | 61.3037 | -61.3724 | -61.5692 | -0.064087 | 0.009155 | -0.082398 | 0.1648 | -0.073242 | -0.082397 | 0.050354 | 0.082398 | -0.11444 | -0.14648 | -0.41199 | -0.30212 | -0.18768 | -0.10071 | 122.7768 | 122.9095 | 61.4914 | -122.85 | 122.7127 | 122.7585 | 61.4868 | -122.9736
228.9375 | 123.0331 | -61.5326 | 61.3724 | -0.0022127 | -0.035175 | 0.11359 | 0.022879 | 0.051374 | -0.019681 | -0.020788 | 0.014954 | -0.0035055 | 0.040467 | 0.060707 | -0.012954 | -0.014035 | 61.4182 | -61.377 | -0.004578 | -61.5921 | 61.3632 | -61.5692 | -61.4914 | -61.9171 | -0.004578 | -61.8805 | 61.2579 | 61.2991 | -61.4319 | -61.6333 | -0.036621 | 0.041199 | -0.009155 | 0.15564 | -0.059509 | -0.10071 | 0.045777 | 0.10071 | -0.10071 | -0.11444 | -0.38452 | -0.3479 | -0.24719 | -0.073242 | 122.8958 | 122.9507 | 61.528 | -122.8638 | 122.7905 | 122.8317 | 61.528 | -123.0057
230.6562 | 123.0606 | -61.5005 | 61.4182 | 0.0054168 | -0.035175 | 0.11658 | 0.028006 | 0.050306 | -0.022885 | -0.023351 | 0.014954 | -0.0047873 | 0.04303 | 0.060494 | -0.017013 | -0.014889 | 61.4502 | -61.3129 | 0.07782 | -61.528 | 61.4227 | -61.5189 | -61.4319 | -61.8759 | 0.059509 | -61.7981 | 61.3129 | 61.3541 | -61.3815 | -61.5601 | -0.018311 | 0.068664 | 0.004577 | 0.18768 | -0.027466 | -0.09613 | 0.032043 | 0.11902 | -0.05951 | -0.10529 | -0.37537 | -0.29755 | -0.23804 | -0.064087 | 122.9233 | 122.9507 | 61.5784 | -122.85 | 122.8134 | 122.8546 | 61.5601 | -122.9782
232.3438 | 123.0698 | -61.5234 | 61.4136 | -0.0022127 | -0.033893 | 0.11381 | 0.02886 | 0.053938 | -0.026303 | -0.023992 | -0.0003053 | -0.0035055 | 0.042176 | 0.06028 | -0.016372 | -0.013394 | 61.4502 | -61.3266 | 0.073242 | -61.5189 | 61.409 | -61.5143 | -61.4548 | -61.8713 | 0.050354 | -61.8073 | 61.2946 | 61.3541 | -61.3541 | -61.5784 | 0.009155 | 0.068664 | -0.004577 | 0.19684 | 0.004577 | -0.064087 | 0.036621 | 0.16937 | -0.054932 | -0.11902 | -0.3479 | -0.28381 | -0.22888 | -0.059509 | 122.9324 | 122.9736 | 61.5967 | -122.8683 | 122.818 | 122.8775 | 61.5738 | -122.9919
234.0312 | 123.0469 | -61.5189 | 61.4182 | 0.0054168 | -0.032612 | 0.11551 | 0.026724 | 0.050733 | -0.024381 | -0.02506 | 0.0073242 | -0.0043601 | 0.043457 | 0.059426 | -0.017013 | -0.013608 | 61.4456 | -61.3312 | 0.064087 | -61.528 | 61.4182 | -61.5143 | -61.4182 | -61.8896 | 0.059509 | -61.8027 | 61.322 | 61.377 | -61.3907 | -61.5738 | 0.004578 | 0.10071 | 0 | 0.18768 | -0.009155 | -0.10986 | 0.027466 | 0.12817 | -0.054932 | -0.096131 | -0.37079 | -0.28381 | -0.22888 | -0.041199 | 122.937 | 122.9645 | 61.5829 | -122.8363 | 122.8409 | 122.8958 | 61.5784 | -122.9919
235.7031 | 123.111 | -61.4822 | 61.3998 | 0.013046 | -0.039875 | 0.11701 | 0.027792 | 0.050306 | -0.028653 | -0.02506 | 0.0073242 | -0.0073507 | 0.041107 | 0.060067 | -0.019149 | -0.014249 | 61.4365 | -61.29 | 0.036621 | -61.5189 | 61.3266 | -61.528 | -61.4365 | -61.8576 | 0.032043 | -61.7477 | 61.235 | 61.3083 | -61.3861 | -61.5875 | -0.045776 | 0.045777 | -0.073242 | 0.19226 | -0.036621 | -0.082398 | 0.036621 | 0.096131 | -0.10529 | -0.1648 | -0.37537 | -0.2655 | -0.16022 | -0.091552 | 122.8088 | 122.9187 | 61.5189 | -122.8363 | 122.7173 | 122.7905 | 61.5143 | -122.9874
237.4062 | 123.1338 | -61.528 | 61.3083 | 0.013046 | -0.036243 | 0.11509 | 0.024374 | 0.050733 | -0.025876 | -0.023138 | -0.0079343 | -0.0045737 | 0.041107 | 0.060707 | -0.015945 | -0.014889 | 61.4822 | -61.2854 | 0.059509 | -61.5143 | 61.2717 | -61.5692 | -61.4639 | -61.8393 | 0.064087 | -61.7523 | 61.1481 | 61.2488 | -61.409 | -61.5921 | -0.041199 | 0.064087 | -0.036622 | 0.24262 | 0.013733 | -0.050354 | 0.17395 | 0.11902 | -0.064087 | -0.16022 | -0.31128 | -0.2243 | -0.16022 | -0.05951 | 122.7997 | 123.0103 | 61.5875 | -122.7722 | 122.6761 | 122.7768 | 61.5921 | -122.9004
239.0938 | 123.1293 | -61.4868 | 61.377 | -0.0098417 | -0.040089 | 0.11594 | 0.026724 | 0.053938 | -0.026731 | -0.025274 | -0.0003053 | -0.0060691 | 0.04068 | 0.057717 | -0.016799 | -0.012326 | 61.4273 | -61.29 | 0.050354 | -61.5326 | 61.3358 | -61.5143 | -61.4182 | -61.8713 | 0.027466 | -61.7798 | 61.2534 | 61.2854 | -61.3632 | -61.5646 | -0.027466 | 0.068664 | -0.041199 | 0.19684 | -0.045777 | -0.11444 | 0.050354 | 0.1236 | -0.07782 | -0.1236 | -0.38452 | -0.29297 | -0.21515 | -0.091553 | 122.8226 | 122.9141 | 61.5372 | -122.7951 | 122.7402 | 122.7722 | 61.5143 | -122.9416
240.7969 | 123.1338 | -61.5143 | 61.3403 | -0.0022127 | -0.037952 | 0.11445 | 0.024161 | 0.051588 | -0.021604 | -0.022497 | 0.0073242 | -0.0039329 | 0.041107 | 0.058358 | -0.014449 | -0.014676 | 61.4594 | -61.3129 | 0.013733 | -61.5417 | 61.2854 | -61.5601 | -61.4868 | -61.8301 | 0.054932 | -61.7661 | 61.1801 | 61.2396 | -61.3815 | -61.5875 | -0.045777 | 0.027466 | -0.054932 | 0.20142 | -0.027466 | -0.054932 | 0.11902 | 0.13275 | -0.073242 | -0.16022 | -0.31586 | -0.25177 | -0.17853 | -0.10071 | 122.7997 | 122.9736 | 61.528 | -122.8271 | 122.6944 | 122.7539 | 61.5692 | -122.9279
242.5 | 123.143 | -61.4456 | 61.3815 | 0.0054168 | -0.036457 | 0.11616 | 0.02822 | 0.053297 | -0.027158 | -0.024847 | -0.0003053 | -0.0060691 | 0.040894 | 0.057503 | -0.019149 | -0.013821 | 61.5417 | -61.2122 | 0.15564 | -61.4502 | 61.3724 | -61.4868 | -61.4136 | -61.7615 | 0.12817 | -61.6608 | 61.2259 | 61.3037 | -61.3449 | -61.5509 | -0.041198 | 0.032044 | -0.009156 | 0.23346 | -0.004577 | -0.036621 | 0.16022 | 0.10071 | -0.10528 | -0.15564 | -0.31586 | -0.21515 | -0.10986 | -0.07782 | 122.818 | 122.9874 | 61.6013 | -122.7951 | 122.6715 | 122.7493 | 61.5738 | -122.9324
244.1875 | 123.0835 | -61.5097 | 61.3678 | 0.0054168 | -0.040089 | 0.11808 | 0.024374 | 0.052442 | -0.025022 | -0.023992 | 0.0073242 | -0.0047873 | 0.041748 | 0.056862 | -0.015731 | -0.012967 | 61.4777 | -61.2808 | 0.054932 | -61.5234 | 61.2854 | -61.5417 | -61.4502 | -61.8393 | 0.041199 | -61.7615 | 61.2259 | 61.2717 | -61.3724 | -61.5784 | -0.032043 | 0.05951 | -0.082398 | 0.22888 | -0.013732 | -0.073242 | 0.10986 | 0.13733 | -0.068664 | -0.14191 | -0.32959 | -0.25177 | -0.18311 | -0.096131 | 122.7951 | 122.9874 | 61.5646 | -122.818 | 122.7356 | 122.7814 | 61.5509 | -122.9462
245.9219 | 123.143 | -61.5051 | 61.3174 | -0.0022127 | -0.037952 | 0.11616 | 0.023947 | 0.051374 | -0.020963 | -0.021856 | 0.014954 | -0.0024375 | 0.040894 | 0.061348 | -0.014877 | -0.013608 | 61.4136 | -61.3861 | -0.045776 | -61.5921 | 61.322 | -61.5829 | -61.4822 | -61.8713 | 0.009155 | -61.8256 | 61.1984 | 61.2671 | -61.4182 | -61.5875 | -0.07782 | 0.022888 | 0.004577 | 0.11902 | -0.086975 | -0.10986 | 0.09613 | 0.086975 | -0.082397 | -0.11902 | -0.36621 | -0.32043 | -0.23804 | -0.050354 | 122.8271 | 122.9187 | 61.4594 | -122.7997 | 122.7036 | 122.7722 | 61.5143 | -122.905
247.6094 | 123.143 | -61.441 | 61.3861 | -0.017471 | -0.037952 | 0.1153 | 0.030142 | 0.052229 | -0.027799 | -0.022283 | -0.0003053 | -0.0060691 | 0.042816 | 0.056649 | -0.020217 | -0.014035 | 61.5555 | -61.1938 | 0.16479 | -61.441 | 61.3495 | -61.4777 | -61.3953 | -61.7706 | 0.14648 | -61.6379 | 61.2396 | 61.322 | -61.3129 | -61.5189 | -0.036621 | 0.045776 | -0.036621 | 0.24719 | 0 | -0.045776 | 0.16937 | 0.12817 | -0.07782 | -0.14648 | -0.32959 | -0.19684 | -0.11902 | -0.064087 | 122.7905 | 122.9965 | 61.6058 | -122.7814 | 122.6807 | 122.7631 | 61.5875 | -122.905
249.3125 | 122.9874 | -61.5372 | 61.3815 | 0.0054168 | -0.037311 | 0.10932 | 0.023306 | 0.05351 | -0.018186 | -0.022069 | -0.0003053 | -8.7654e-05 | 0.043671 | 0.060921 | -0.013381 | -0.014249 | 61.4822 | -61.3266 | 0.054932 | -61.5417 | 61.3266 | -61.528 | -61.4822 | -61.8713 | -0.004578 | -61.853 | 61.2488 | 61.3129 | -61.4365 | -61.6013 | 0.009155 | 0.054931 | -0.054932 | 0.21057 | -0.004578 | -0.059509 | 0.10071 | 0.10071 | -0.064087 | -0.13275 | -0.33417 | -0.31586 | -0.25177 | -0.068665 | 122.8638 | 123.0194 | 61.5921 | -122.8638 | 122.7859 | 122.85 | 61.5326 | -122.9828
251.0156 | 122.9965 | -61.5189 | 61.322 | 0.013046 | -0.032825 | 0.11252 | 0.028647 | 0.053297 | -0.022031 | -0.021642 | 0.0073242 | -0.0011557 | 0.042176 | 0.061348 | -0.015731 | -0.015317 | 61.5005 | -61.3083 | 0.086975 | -61.5097 | 61.3586 | -61.5234 | -61.4502 | -61.821 | 0.091553 | -61.8027 | 61.235 | 61.322 | -61.3724 | -61.5784 | -0.004577 | 0.068665 | 0.036622 | 0.21057 | 0.009155 | -0.05951 | 0.17853 | 0.14648 | -0.059509 | -0.086975 | -0.30212 | -0.28381 | -0.2243 | 0 | 122.8775 | 123.0194 | 61.6058 | -122.7722 | 122.7539 | 122.8409 | 61.6104 | -122.9004
252.7031 | 123.1201 | -61.4227 | 61.3998 | -0.0022127 | -0.035175 | 0.1153 | 0.027792 | 0.052229 | -0.02908 | -0.023778 | -0.0003053 | -0.0050009 | 0.043885 | 0.060921 | -0.020004 | -0.014889 | 61.5463 | -61.1847 | 0.16022 | -61.441 | 61.322 | -61.496 | -61.3998 | -61.7386 | 0.17395 | -61.6287 | 61.2488 | 61.3449 | -61.3312 | -61.528 | -0.073243 | 0.022888 | -0.07782 | 0.23804 | -0.018311 | -0.041199 | 0.14648 | 0.091552 | -0.10529 | -0.15106 | -0.31586 | -0.20599 | -0.10071 | -0.054931 | 122.7447 | 122.9691 | 61.5829 | -122.7997 | 122.6715 | 122.7676 | 61.5967 | -122.9279
254.4062 | 123.0698 | -61.4685 | 61.3586 | -0.0022127 | -0.037311 | 0.11487 | 0.022025 | 0.055219 | -0.02609 | -0.023565 | 0.0073242 | -0.0054281 | 0.04068 | 0.061348 | -0.018295 | -0.011899 | 61.4731 | -61.2717 | 0.064087 | -61.528 | 61.2991 | -61.528 | -61.4319 | -61.8256 | 0.054932 | -61.7477 | 61.1801 | 61.2854 | -61.3678 | -61.5875 | -0.059509 | 0.036621 | -0.05951 | 0.19684 | -0.059509 | -0.09613 | 0.11444 | 0.10071 | -0.11902 | -0.17853 | -0.35706 | -0.27924 | -0.16022 | -0.073243 | 122.7676 | 122.9416 | 61.5326 | -122.7905 | 122.6486 | 122.7539 | 61.5234 | -122.9462
256.0938 | 122.9828 | -61.5646 | 61.3632 | 0.020676 | -0.034107 | 0.11274 | 0.026083 | 0.053724 | -0.020535 | -0.024206 | -0.0003053 | -0.0011557 | 0.040894 | 0.062203 | -0.01274 | -0.01553 | 61.4731 | -61.3403 | 0.045776 | -61.5326 | 61.3495 | -61.528 | -61.4594 | -61.8805 | 0.013733 | -61.8393 | 61.2305 | 61.3129 | -61.409 | -61.6287 | 0.036621 | 0.10529 | -0.013733 | 0.2243 | 0.032043 | -0.073242 | 0.10986 | 0.15564 | -0.064087 | -0.13275 | -0.31586 | -0.27466 | -0.21057 | -0.050354 | 122.9141 | 123.0377 | 61.6104 | -122.8226 | 122.7951 | 122.8775 | 61.5784 | -122.9919
257.8594 | 123.0789 | -61.5051 | 61.3312 | 0.013046 | -0.035389 | 0.11316 | 0.026511 | 0.052656 | -0.022031 | -0.023138 | 0.0073242 | -0.0045737 | 0.042389 | 0.059853 | -0.015518 | -0.01318 | 61.3815 | -61.409 | -0.059509 | -61.5967 | 61.322 | -61.5784 | -61.4914 | -61.9125 | -0.036621 | -61.8484 | 61.235 | 61.29 | -61.4319 | -61.615 | -0.073242 | 0.013733 | -0.009156 | 0.09613 | -0.091553 | -0.10529 | 0.050354 | 0.073242 | -0.10986 | -0.096131 | -0.40741 | -0.34332 | -0.23346 | -0.041199 | 122.8271 | 122.8867 | 61.4456 | -122.8226 | 122.7402 | 122.7951 | 61.4685 | -122.9462
259.5469 | 123.0515 | -61.4822 | 61.3861 | 0.0054168 | -0.034321 | 0.11316 | 0.027792 | 0.051374 | -0.023953 | -0.021001 | -0.0003053 | -0.0032919 | 0.040467 | 0.060067 | -0.01744 | -0.014676 | 61.4594 | -61.3037 | 0.082397 | -61.4868 | 61.3907 | -61.5143 | -61.4227 | -61.8439 | 0.091553 | -61.7798 | 61.2488 | 61.3495 | -61.377 | -61.5829 | -0.032043 | 0.05951 | 0.004578 | 0.17853 | -0.004577 | -0.064087 | 0.073243 | 0.10529 | -0.10071 | -0.13733 | -0.36163 | -0.29755 | -0.19684 | -0.036621 | 122.8729 | 122.9416 | 61.5646 | -122.8088 | 122.731 | 122.8317 | 61.5738 | -122.9691
261.2812 | 122.9874 | -61.5372 | 61.3174 | -0.0022127 | -0.031544 | 0.10975 | 0.030783 | 0.055006 | -0.023313 | -0.021215 | -0.0003053 | -0.0024375 | 0.044098 | 0.061135 | -0.018295 | -0.012753 | 61.3678 | -61.409 | -0.013733 | -61.5692 | 61.3403 | -61.5601 | -61.4639 | -61.9263 | -0.022888 | -61.8759 | 61.2259 | 61.2808 | -61.3953 | -61.615 | -0.022889 | 0.073242 | 0.022888 | 0.12817 | -0.032044 | -0.10529 | 0.050354 | 0.14191 | -0.07782 | -0.091553 | -0.3891 | -0.33875 | -0.26093 | -0.036621 | 122.8775 | 122.905 | 61.5234 | -122.7814 | 122.7631 | 122.818 | 61.5143 | -122.9324
262.9844 | 123.1247 | -61.4914 | 61.2991 | 0.0054168 | -0.035602 | 0.11423 | 0.024161 | 0.051801 | -0.025235 | -0.022924 | 0.014954 | -0.0037191 | 0.039826 | 0.061562 | -0.015945 | -0.011258 | 61.3678 | -61.3586 | -0.027466 | -61.5601 | 61.2991 | -61.5463 | -61.4868 | -61.8622 | 0.036621 | -61.7935 | 61.1801 | 61.2488 | -61.409 | -61.6013 | -0.054932 | 0.004578 | 0 | 0.13275 | -0.068665 | -0.073243 | 0.068665 | 0.082397 | -0.10986 | -0.11902 | -0.37079 | -0.30212 | -0.19226 | -0.050354 | 122.7905 | 122.8592 | 61.4639 | -122.7859 | 122.6715 | 122.7402 | 61.528 | -122.9004
264.6875 | 123.0743 | -61.5051 | 61.3312 | 0.0054168 | -0.036884 | 0.11338 | 0.023306 | 0.052015 | -0.027371 | -0.022497 | -0.0079343 | -0.0037191 | 0.04068 | 0.059853 | -0.018508 | -0.012967 | 61.4685 | -61.2854 | 0.045776 | -61.5005 | 61.2442 | -61.5326 | -61.4594 | -61.7981 | 0.07782 | -61.7203 | 61.1572 | 61.2442 | -61.3724 | -61.5829 | -0.027466 | 0.045776 | -0.086975 | 0.21973 | 0.004578 | -0.041198 | 0.13733 | 0.13275 | -0.07782 | -0.17395 | -0.29297 | -0.21515 | -0.13733 | -0.086975 | 122.7493 | 122.9736 | 61.5509 | -122.7905 | 122.6624 | 122.7493 | 61.5829 | -122.9141
266.375 | 123.111 | -61.5005 | 61.3129 | 0.013046 | -0.037098 | 0.11381 | 0.024588 | 0.051161 | -0.025235 | -0.022283 | 0.0073242 | -0.0037191 | 0.041321 | 0.061348 | -0.014663 | -0.011899 | 61.4456 | -61.2808 | 0.022888 | -61.5189 | 61.2579 | -61.5417 | -61.441 | -61.8256 | 0.073242 | -61.7523 | 61.171 | 61.2396 | -61.3953 | -61.5875 | -0.041199 | 0.059509 | -0.054931 | 0.21973 | -0.018311 | -0.07782 | 0.13275 | 0.10529 | -0.086975 | -0.14191 | -0.32501 | -0.25177 | -0.16479 | -0.073242 | 122.7585 | 122.9462 | 61.5234 | -122.7539 | 122.6715 | 122.7402 | 61.5738 | -122.9004
268.0625 | 123.0743 | -61.4594 | 61.3861 | 0.0054168 | -0.040516 | 0.11658 | 0.026938 | 0.052442 | -0.029721 | -0.024633 | -0.0003053 | -0.0045737 | 0.039185 | 0.058144 | -0.01744 | -0.011899 | 61.4365 | -61.3037 | 0.045776 | -61.5189 | 61.2991 | -61.5189 | -61.4365 | -61.8576 | 0.027466 | -61.7386 | 61.2076 | 61.2946 | -61.3312 | -61.5555 | -0.059509 | 0.022889 | -0.086975 | 0.15564 | -0.059509 | -0.082398 | 0.050354 | 0.12817 | -0.09613 | -0.17853 | -0.39825 | -0.27923 | -0.1831 | -0.091552 | 122.7585 | 122.8958 | 61.5051 | -122.8226 | 122.6669 | 122.7539 | 61.4868 | -122.9416
269.75 | 122.9874 | -61.4594 | 61.4273 | -0.0098417 | -0.034962 | 0.11658 | 0.028433 | 0.051801 | -0.025022 | -0.025701 | 0.0073242 | -0.0039329 | 0.041535 | 0.060067 | -0.019576 | -0.014249 | 61.5143 | -61.1984 | 0.17853 | -61.4273 | 61.3358 | -61.4685 | -61.3861 | -61.7889 | 0.13733 | -61.6974 | 61.2762 | 61.3358 | -61.3358 | -61.5234 | -0.009155 | 0.073243 | -0.091553 | 0.26093 | 0.032044 | -0.041199 | 0.086975 | 0.1236 | -0.064086 | -0.15106 | -0.32959 | -0.23804 | -0.17395 | -0.091553 | 122.7951 | 122.9736 | 61.6379 | -122.8134 | 122.7356 | 122.7951 | 61.5967 | -122.9507
271.4531 | 123.1064 | -61.5189 | 61.3129 | -0.0022127 | -0.03603 | 0.11381 | 0.02352 | 0.054151 | -0.021817 | -0.025701 | 0.0073242 | -0.0054281 | 0.039826 | 0.060067 | -0.01509 | -0.012967 | 61.3953 | -61.3632 | -0.041199 | -61.5555 | 61.2991 | -61.5646 | -61.4777 | -61.8484 | 0.013733 | -61.7752 | 61.1847 | 61.2167 | -61.3998 | -61.6058 | -0.045776 | 0.041199 | -0.013733 | 0.15564 | -0.036621 | -0.07782 | 0.082398 | 0.11902 | -0.086975 | -0.12817 | -0.32959 | -0.25635 | -0.16937 | -0.09613 | 122.818 | 122.9141 | 61.4777 | -122.7905 | 122.7036 | 122.7356 | 61.5326 | -122.9187
273.1562 | 123.1064 | -61.4456 | 61.3678 | -0.0098417 | -0.037098 | 0.11466 | 0.02886 | 0.05052 | -0.027799 | -0.025915 | -0.0079343 | -0.0052145 | 0.04068 | 0.059212 | -0.020217 | -0.01318 | 61.5051 | -61.2076 | 0.13275 | -61.4456 | 61.322 | -61.4502 | -61.3998 | -61.7661 | 0.1236 | -61.6379 | 61.235 | 61.3129 | -61.3266 | -61.5234 | -0.004577 | 0.045777 | -0.045777 | 0.23804 | 0 | -0.045777 | 0.13733 | 0.11902 | -0.077819 | -0.13275 | -0.32043 | -0.19226 | -0.11444 | -0.054932 | 122.7676 | 122.9507 | 61.5784 | -122.7676 | 122.6807 | 122.7585 | 61.5692 | -122.8912
274.9062 | 123.0927 | -61.5097 | 61.3129 | 0.0054168 | -0.035602 | 0.11466 | 0.025229 | 0.053724 | -0.021817 | -0.022924 | 0.0073242 | -0.0020103 | 0.041107 | 0.060707 | -0.014236 | -0.013608 | 61.377 | -61.3953 | -0.054932 | -61.5967 | 61.3083 | -61.5555 | -61.4731 | -61.8942 | -0.041199 | -61.8439 | 61.2213 | 61.2717 | -61.409 | -61.5967 | -0.045776 | 0.036622 | -0.004577 | 0.11444 | -0.086975 | -0.1236 | 0.064087 | 0.10071 | -0.086975 | -0.091553 | -0.38452 | -0.33417 | -0.24719 | -0.041199 | 122.818 | 122.8867 | 61.4548 | -122.7859 | 122.731 | 122.7814 | 61.4685 | -122.9095
276.5938 | 123.0927 | -61.5143 | 61.3129 | -0.0022127 | -0.037098 | 0.11338 | 0.025229 | 0.052229 | -0.021817 | -0.023351 | 0.014954 | -0.0011557 | 0.040253 | 0.061562 | -0.014236 | -0.014462 | 61.3861 | -61.3861 | -0.045776 | -61.5784 | 61.3266 | -61.5463 | -61.4548 | -61.8851 | -0.050354 | -61.8256 | 61.1938 | 61.2396 | -61.4227 | -61.6196 | -0.032044 | 0.059509 | 0.013733 | 0.12817 | -0.064087 | -0.1236 | 0.073242 | 0.091553 | -0.10529 | -0.11902 | -0.37079 | -0.31128 | -0.20599 | -0.073242 | 122.8409 | 122.9004 | 61.4685 | -122.7676 | 122.7081 | 122.7539 | 61.4639 | -122.9324
278.2812 | 123.0881 | -61.4182 | 61.377 | -0.0022127 | -0.036671 | 0.11744 | 0.027579 | 0.05052 | -0.030576 | -0.023992 | -0.0079343 | -0.0037191 | 0.040894 | 0.057076 | -0.018295 | -0.01318 | 61.496 | -61.1801 | 0.15106 | -61.4456 | 61.3403 | -61.4639 | -61.3724 | -61.7569 | 0.15564 | -61.6379 | 61.2122 | 61.3083 | -61.3037 | -61.5463 | -0.045776 | 0.045777 | -0.036621 | 0.23804 | -0.027466 | -0.073243 | 0.11902 | 0.11444 | -0.12817 | -0.16479 | -0.33875 | -0.21973 | -0.091552 | -0.068664 | 122.7585 | 122.9141 | 61.5692 | -122.7493 | 122.6303 | 122.7264 | 61.5738 | -122.9233
279.9688 | 123.024 | -61.4731 | 61.3998 | 0.0054168 | -0.031971 | 0.11509 | 0.029715 | 0.051801 | -0.022672 | -0.023351 | -0.0003053 | -0.00072845 | 0.042816 | 0.060707 | -0.017227 | -0.016171 | 61.4502 | -61.3266 | 0.068665 | -61.5005 | 61.3724 | -61.5051 | -61.409 | -61.8484 | 0.054932 | -61.7889 | 61.2946 | 61.3586 | -61.3358 | -61.5463 | -0.032044 | 0.064086 | -0.027466 | 0.14648 | -0.027466 | -0.091552 | 0.050354 | 0.13733 | -0.073243 | -0.10529 | -0.37537 | -0.31586 | -0.24261 | -0.041198 | 122.8455 | 122.9233 | 61.5417 | -122.8088 | 122.7676 | 122.8317 | 61.528 | -122.9462
281.6562 | 123.0881 | -61.4273 | 61.3586 | -0.0022127 | -0.038593 | 0.11509 | 0.029715 | 0.052229 | -0.027371 | -0.025915 | 0.0073242 | -0.0060691 | 0.04068 | 0.060921 | -0.018295 | -0.013821 | 61.5143 | -61.1755 | 0.13733 | -61.4273 | 61.3266 | -61.4365 | -61.377 | -61.7615 | 0.16022 | -61.6333 | 61.2122 | 61.2946 | -61.3083 | -61.5005 | -0.009155 | 0.050354 | -0.032044 | 0.25177 | 0 | -0.050354 | 0.15564 | 0.11902 | -0.073242 | -0.14648 | -0.33417 | -0.20599 | -0.13275 | -0.064087 | 122.7539 | 122.9416 | 61.5646 | -122.7356 | 122.6395 | 122.7219 | 61.5875 | -122.8592
283.3594 | 123.0652 | -61.4044 | 61.3586 | 0.013046 | -0.033039 | 0.1153 | 0.027365 | 0.051801 | -0.029721 | -0.024419 | 0.0073242 | -0.0067099 | 0.040253 | 0.060707 | -0.018295 | -0.014249 | 61.5509 | -61.1389 | 0.17853 | -61.4136 | 61.3312 | -61.4502 | -61.3815 | -61.734 | 0.1831 | -61.6379 | 61.2534 | 61.2854 | -61.322 | -61.5005 | -0.045776 | 0.022888 | -0.027466 | 0.2655 | -0.009155 | -0.032043 | 0.19226 | 0.082398 | -0.09613 | -0.10529 | -0.32959 | -0.23346 | -0.13733 | -0.073243 | 122.7356 | 122.9553 | 61.5829 | -122.7402 | 122.6578 | 122.6898 | 61.5875 | -122.8592
285.0625 | 123.111 | -61.441 | 61.3541 | -0.0022127 | -0.037952 | 0.11658 | 0.025443 | 0.057356 | -0.028226 | -0.024633 | -0.0003053 | -0.0058555 | 0.040039 | 0.059639 | -0.018508 | -0.01254 | 61.4914 | -61.1984 | 0.10529 | -61.441 | 61.3403 | -61.4731 | -61.3678 | -61.7523 | 0.13733 | -61.6379 | 61.2396 | 61.2946 | -61.3037 | -61.5097 | -0.032043 | 0.073242 | -0.013733 | 0.24262 | 0 | -0.073242 | 0.13733 | 0.13733 | -0.068665 | -0.11444 | -0.31128 | -0.19684 | -0.12817 | -0.059509 | 122.7814 | 122.9324 | 61.5463 | -122.7219 | 122.6807 | 122.7356 | 61.5784 | -122.8638
286.7656 | 123.111 | -61.4365 | 61.3449 | 0.0054168 | -0.036884 | 0.11616 | 0.026297 | 0.050733 | -0.025876 | -0.024847 | -0.0003053 | -0.0071371 | 0.040467 | 0.058785 | -0.020217 | -0.014889 | 61.4731 | -61.2213 | 0.10529 | -61.4456 | 61.322 | -61.4914 | -61.3724 | -61.7477 | 0.13733 | -61.6745 | 61.235 | 61.2991 | -61.3174 | -61.5097 | -0.054932 | 0.064087 | -0.022889 | 0.21515 | -0.009156 | -0.073243 | 0.12817 | 0.11902 | -0.073243 | -0.10986 | -0.31128 | -0.23804 | -0.1648 | -0.045777 | 122.7585 | 122.9095 | 61.5417 | -122.7173 | 122.6715 | 122.7356 | 61.5738 | -122.8546
288.4531 | 122.9599 | -61.5372 | 61.3632 | 0.013046 | -0.033039 | 0.11252 | 0.025443 | 0.052015 | -0.017972 | -0.023778 | 0.014954 | -0.00051485 | 0.043885 | 0.061348 | -0.016158 | -0.016171 | 61.4594 | -61.2762 | 0.07782 | -61.4914 | 61.3312 | -61.5417 | -61.4365 | -61.8073 | 0.068665 | -61.7889 | 61.2442 | 61.2808 | -61.3907 | -61.5692 | -0.004578 | 0.10071 | -0.032043 | 0.26093 | 0.045776 | -0.054932 | 0.096131 | 0.14648 | -0.032044 | -0.11902 | -0.27008 | -0.25177 | -0.21973 | -0.082397 | 122.8683 | 122.9965 | 61.615 | -122.7997 | 122.7814 | 122.818 | 61.6058 | -122.9324
290.1719 | 122.9645 | -61.5326 | 61.322 | -0.0022127 | -0.037952 | 0.11316 | 0.025229 | 0.052656 | -0.021176 | -0.021856 | 0.014954 | -0.0022239 | 0.042603 | 0.056221 | -0.014663 | -0.012753 | 61.3449 | -61.409 | -0.064087 | -61.5829 | 61.3174 | -61.5463 | -61.4548 | -61.9125 | -0.041199 | -61.8576 | 61.2213 | 61.2488 | -61.3953 | -61.6104 | -0.013733 | 0.07782 | -0.004577 | 0.1236 | -0.050354 | -0.12817 | 0.022889 | 0.13733 | -0.07782 | -0.10071 | -0.37994 | -0.32501 | -0.24719 | -0.073242 | 122.85 | 122.8775 | 61.4685 | -122.7768 | 122.7539 | 122.7814 | 61.4914 | -122.9324
291.9219 | 123.0331 | -61.4731 | 61.3449 | 0.013046 | -0.037739 | 0.11573 | 0.026938 | 0.049879 | -0.026944 | -0.023778 | -0.0079343 | -0.0069235 | 0.041748 | 0.059853 | -0.018508 | -0.010403 | 61.4182 | -61.2396 | 0.059509 | -61.5051 | 61.2762 | -61.5051 | -61.4136 | -61.8301 | 0.032043 | -61.734 | 61.1893 | 61.2534 | -61.3586 | -61.5692 | -0.032044 | 0.059509 | -0.068665 | 0.23346 | -0.032044 | -0.091553 | 0.073242 | 0.11444 | -0.096131 | -0.15564 | -0.35706 | -0.26093 | -0.16479 | -0.091553 | 122.7493 | 122.8912 | 61.5326 | -122.7585 | 122.6624 | 122.7264 | 61.5051 | -122.9141
293.6562 | 122.9599 | -61.4685 | 61.4044 | 0.0054168 | -0.034107 | 0.11466 | 0.030783 | 0.051801 | -0.021176 | -0.023351 | 0.014954 | -0.0024375 | 0.041962 | 0.06028 | -0.019149 | -0.012753 | 61.409 | -61.2717 | 0.07782 | -61.4914 | 61.4044 | -61.4822 | -61.4273 | -61.8347 | 0.064087 | -61.7569 | 61.3037 | 61.3449 | -61.3083 | -61.528 | -0.013733 | 0.041199 | 0 | 0.19684 | -0.022888 | -0.064087 | 0.004578 | 0.16022 | -0.059509 | -0.10071 | -0.36621 | -0.28839 | -0.22888 | -0.059509 | 122.8729 | 122.8775 | 61.5463 | -122.8317 | 122.7722 | 122.8134 | 61.5326 | -122.9324
295.3438 | 123.024 | -61.4685 | 61.3129 | -0.0098417 | -0.038807 | 0.11402 | 0.025229 | 0.052015 | -0.025235 | -0.021429 | 0.0073242 | -0.0050009 | 0.041962 | 0.061562 | -0.016158 | -0.011899 | 61.4365 | -61.2396 | 0.059509 | -61.5005 | 61.2167 | -61.5143 | -61.4319 | -61.7935 | 0.068665 | -61.7065 | 61.1481 | 61.1938 | -61.3586 | -61.5692 | -0.045776 | 0.036621 | -0.09613 | 0.22888 | -0.032043 | -0.068664 | 0.1236 | 0.10986 | -0.10071 | -0.16479 | -0.32501 | -0.23804 | -0.13733 | -0.11902 | 122.6852 | 122.905 | 61.528 | -122.7448 | 122.6166 | 122.6624 | 61.5372 | -122.8821
297.0312 | 123.0606 | -61.4319 | 61.3541 | -0.0022127 | -0.036457 | 0.11381 | 0.02886 | 0.053083 | -0.027158 | -0.026128 | -0.0003053 | -0.0058555 | 0.040894 | 0.061135 | -0.019149 | -0.013394 | 61.528 | -61.1435 | 0.17395 | -61.4182 | 61.3083 | -61.441 | -61.3495 | -61.7157 | 0.16937 | -61.6287 | 61.2259 | 61.2808 | -61.2946 | -61.5097 | -0.009155 | 0.082398 | -0.045776 | 0.28839 | 0.013733 | -0.068665 | 0.17395 | 0.13733 | -0.07782 | -0.12817 | -0.28381 | -0.19684 | -0.11902 | -0.073242 | 122.7402 | 122.9599 | 61.6058 | -122.7036 | 122.6578 | 122.7127 | 61.6013 | -122.8638
298.75 | 122.9965 | -61.5417 | 61.3129 | 0.0054168 | -0.035816 | 0.11509 | 0.023734 | 0.051588 | -0.02139 | -0.022497 | 0.0073242 | -8.7654e-05 | 0.039612 | 0.060921 | -0.014022 | -0.013821 | 61.3541 | -61.3861 | -0.07782 | -61.5646 | 61.3174 | -61.5555 | -61.4777 | -61.8851 | -0.059509 | -61.8576 | 61.2122 | 61.2625 | -61.3998 | -61.6104 | -0.013733 | 0.064087 | 0.004578 | 0.15564 | -0.022888 | -0.086975 | 0.041199 | 0.14191 | -0.068665 | -0.10071 | -0.34332 | -0.31586 | -0.24719 | -0.050354 | 122.8592 | 122.8958 | 61.4639 | -122.7905 | 122.7539 | 122.8043 | 61.4822 | -122.9233
300.4531 | 123.0469 | -61.4822 | 61.3037 | -0.0022127 | -0.038807 | 0.11338 | 0.023947 | 0.051801 | -0.024381 | -0.022069 | 0.014954 | -0.0052145 | 0.040467 | 0.06028 | -0.016586 | -0.011258 | 61.4273 | -61.235 | 0.050354 | -61.4868 | 61.2167 | -61.5097 | -61.441 | -61.7889 | 0.07782 | -61.7111 | 61.1618 | 61.203 | -61.377 | -61.5738 | -0.027466 | 0.041199 | -0.086975 | 0.24719 | -0.004577 | -0.045776 | 0.1236 | 0.10529 | -0.091553 | -0.14191 | -0.3067 | -0.22888 | -0.13733 | -0.10071 | 122.699 | 122.9095 | 61.5326 | -122.7448 | 122.644 | 122.6852 | 61.5601 | -122.8775
302.1562 | 123.0194 | -61.4685 | 61.2946 | 0.0054168 | -0.034962 | 0.11487 | 0.027152 | 0.049879 | -0.024594 | -0.022497 | 0.0073242 | -0.0050009 | 0.041962 | 0.06028 | -0.016799 | -0.013394 | 61.4502 | -61.2259 | 0.059509 | -61.4914 | 61.2442 | -61.5189 | -61.409 | -61.7844 | 0.07782 | -61.7065 | 61.1847 | 61.235 | -61.3678 | -61.5692 | -0.050354 | 0.059509 | -0.050354 | 0.24262 | -0.022888 | -0.082397 | 0.15564 | 0.10071 | -0.10071 | -0.10986 | -0.31586 | -0.23804 | -0.13733 | -0.05951 | 122.7127 | 122.9187 | 61.528 | -122.7036 | 122.6532 | 122.7036 | 61.5463 | -122.8638
303.9062 | 122.9416 | -61.4456 | 61.3953 | 0.0054168 | -0.035602 | 0.11466 | 0.030142 | 0.052229 | -0.023953 | -0.025915 | -0.0003053 | -0.0024375 | 0.042816 | 0.061562 | -0.018081 | -0.013821 | 61.4594 | -61.2442 | 0.10529 | -61.4777 | 61.3998 | -61.4685 | -61.3953 | -61.8347 | 0.086975 | -61.7386 | 61.3083 | 61.3312 | -61.3358 | -61.5143 | -0.022888 | 0.050354 | 0.004577 | 0.20142 | -0.032043 | -0.082397 | 0.064087 | 0.10986 | -0.068664 | -0.086975 | -0.3891 | -0.29297 | -0.2243 | -0.064087 | 122.8455 | 122.905 | 61.5509 | -122.7905 | 122.7539 | 122.7768 | 61.5326 | -122.9095
305.5938 | 122.9553 | -61.4548 | 61.4136 | -0.0022127 | -0.035175 | 0.11551 | 0.02822 | 0.055647 | -0.02609 | -0.023565 | 0.0073242 | -0.0050009 | 0.042603 | 0.059426 | -0.01744 | -0.013821 | 61.4914 | -61.1801 | 0.16022 | -61.4365 | 61.3495 | -61.4273 | -61.3586 | -61.7752 | 0.10986 | -61.6974 | 61.2579 | 61.2991 | -61.322 | -61.5005 | 0.027466 | 0.09613 | -0.064087 | 0.27466 | 0.018311 | -0.077819 | 0.07782 | 0.13275 | -0.045776 | -0.15564 | -0.32043 | -0.24261 | -0.19684 | -0.11444 | 122.8043 | 122.9462 | 61.615 | -122.7722 | 122.7127 | 122.7539 | 61.5646 | -122.9141
307.2969 | 122.9553 | -61.4273 | 61.3953 | 0.0054168 | -0.034534 | 0.11487 | 0.02886 | 0.054365 | -0.026731 | -0.023351 | -0.0079343 | -0.0045737 | 0.041321 | 0.058358 | -0.01744 | -0.013821 | 61.4868 | -61.1526 | 0.1831 | -61.4136 | 61.3449 | -61.4319 | -61.3495 | -61.7294 | 0.16937 | -61.647 | 61.2396 | 61.2762 | -61.322 | -61.5234 | -0.004578 | 0.07782 | -0.050354 | 0.27466 | 0.013733 | -0.064087 | 0.091552 | 0.10529 | -0.09613 | -0.15564 | -0.30212 | -0.21973 | -0.1236 | -0.11902 | 122.7722 | 122.9141 | 61.6104 | -122.7448 | 122.6669 | 122.7036 | 61.5967 | -122.9187
308.9844 | 122.9553 | -61.4273 | 61.3861 | -0.0098417 | -0.033466 | 0.11509 | 0.029929 | 0.049024 | -0.023313 | -0.023138 | -0.0003053 | -0.0030783 | 0.044739 | 0.060494 | -0.017867 | -0.013608 | 61.4365 | -61.2671 | 0.082397 | -61.4639 | 61.3724 | -61.4502 | -61.3861 | -61.8301 | 0.054932 | -61.7523 | 61.2854 | 61.3312 | -61.3449 | -61.528 | -0.022888 | 0.041199 | -0.013733 | 0.16022 | -0.036621 | -0.07782 | 0.050354 | 0.082397 | -0.10071 | -0.10071 | -0.40283 | -0.32501 | -0.2243 | -0.054931 | 122.7997 | 122.8638 | 61.5097 | -122.7722 | 122.7127 | 122.7585 | 61.4822 | -122.9141
310.6875 | 122.9324 | -61.5051 | 61.3358 | -0.0098417 | -0.036243 | 0.11402 | 0.023947 | 0.051374 | -0.020749 | -0.022497 | -0.0079343 | -8.7654e-05 | 0.042816 | 0.061348 | -0.012527 | -0.015103 | 61.4365 | -61.2488 | 0.064087 | -61.4914 | 61.3449 | -61.5005 | -61.4182 | -61.8118 | 0.091553 | -61.7569 | 61.2213 | 61.2579 | -61.3495 | -61.5463 | 0.004578 | 0.086975 | 0.009156 | 0.25635 | 0.013733 | -0.073242 | 0.10071 | 0.15564 | -0.041199 | -0.11444 | -0.3067 | -0.25177 | -0.21057 | -0.077819 | 122.85 | 122.9416 | 61.5692 | -122.7539 | 122.7264 | 122.7631 | 61.5967 | -122.8821
312.3906 | 122.9691 | -61.5189 | 61.2671 | -0.0022127 | -0.034962 | 0.11445 | 0.024588 | 0.050947 | -0.021817 | -0.022497 | -0.0003053 | -0.00072845 | 0.040253 | 0.062203 | -0.015945 | -0.010617 | 61.3174 | -61.3678 | -0.059509 | -61.5646 | 61.322 | -61.5417 | -61.4914 | -61.908 | -0.045776 | -61.8347 | 61.1984 | 61.2717 | -61.3953 | -61.5967 | -0.022888 | 0.027466 | 0.054931 | 0.15106 | -0.045776 | -0.073242 | 0.050354 | 0.1236 | -0.07782 | -0.068665 | -0.3891 | -0.31586 | -0.23804 | 0.004577 | 122.8409 | 122.8363 | 61.4594 | -122.7585 | 122.7173 | 122.7905 | 61.4731 | -122.8638
314.0781 | 123.0698 | -61.4731 | 61.2671 | 0.0054168 | -0.035816 | 0.11551 | 0.024588 | 0.052442 | -0.026303 | -0.023992 | 0.0073242 | -0.0047873 | 0.04303 | 0.059639 | -0.014449 | -0.011471 | 61.3678 | -61.2808 | 0.018311 | -61.528 | 61.2442 | -61.5143 | -61.4456 | -61.8073 | 0.064087 | -61.7432 | 61.1801 | 61.203 | -61.3495 | -61.5646 | -0.041199 | 0.027465 | -0.022888 | 0.19226 | -0.054932 | -0.082397 | 0.10071 | 0.1236 | -0.091553 | -0.086975 | -0.33417 | -0.27008 | -0.17853 | -0.064087 | 122.7173 | 122.8409 | 61.4914 | -122.7127 | 122.6532 | 122.6761 | 61.5372 | -122.8317
315.7656 | 123.0011 | -61.441 | 61.322 | 0.0054168 | -0.037311 | 0.11466 | 0.027152 | 0.054578 | -0.026303 | -0.023138 | 0.0073242 | -0.0075645 | 0.038971 | 0.061562 | -0.015731 | -0.012753 | 61.409 | -61.2122 | 0.073242 | -61.4868 | 61.235 | -61.496 | -61.4227 | -61.7981 | 0.068665 | -61.7157 | 61.1664 | 61.2122 | -61.3495 | -61.5829 | -0.054932 | 0.018311 | -0.086975 | 0.22888 | -0.045776 | -0.064087 | 0.086976 | 0.091553 | -0.14191 | -0.15564 | -0.35706 | -0.27466 | -0.13275 | -0.10986 | 122.6761 | 122.85 | 61.5143 | -122.7447 | 122.6074 | 122.6532 | 61.5097 | -122.905
317.4531 | 123.0606 | -61.409 | 61.3678 | 0.0054168 | -0.035602 | 0.11274 | 0.031424 | 0.052656 | -0.029721 | -0.025701 | -0.0003053 | -0.0054281 | 0.040039 | 0.057717 | -0.020217 | -0.012967 | 61.5005 | -61.1618 | 0.16022 | -61.4182 | 61.3037 | -61.4502 | -61.3724 | -61.7294 | 0.16479 | -61.5921 | 61.203 | 61.2854 | -61.2808 | -61.496 | -0.041198 | 0.036622 | -0.064087 | 0.24719 | -0.009155 | -0.045777 | 0.13275 | 0.12817 | -0.086975 | -0.16479 | -0.32043 | -0.1831 | -0.09613 | -0.082398 | 122.7127 | 122.9095 | 61.5692 | -122.7402 | 122.612 | 122.6944 | 61.5738 | -122.8638
319.1406 | 122.9233 | -61.4456 | 61.3861 | -0.0022127 | -0.034962 | 0.11381 | 0.02822 | 0.053297 | -0.025449 | -0.025274 | -0.0003053 | -0.0035055 | 0.044739 | 0.061135 | -0.019149 | -0.014889 | 61.5005 | -61.1755 | 0.1831 | -61.4136 | 61.3037 | -61.441 | -61.3815 | -61.7249 | 0.16479 | -61.6425 | 61.2396 | 61.3129 | -61.3174 | -61.4914 | 0.004578 | 0.064087 | -0.082397 | 0.27008 | 0.032044 | -0.032043 | 0.11444 | 0.12817 | -0.045776 | -0.14648 | -0.27924 | -0.19684 | -0.15106 | -0.073242 | 122.7493 | 122.9462 | 61.6287 | -122.7676 | 122.6852 | 122.7585 | 61.6104 | -122.8775
320.8281 | 122.9645 | -61.4594 | 61.3495 | 0.0054168 | -0.033253 | 0.11509 | 0.030142 | 0.054578 | -0.020749 | -0.025487 | 0.0073242 | -0.0037191 | 0.042816 | 0.059853 | -0.018936 | -0.016171 | 61.4227 | -61.2946 | 0.054932 | -61.4731 | 61.3541 | -61.4868 | -61.4044 | -61.821 | 0.073242 | -61.7477 | 61.2534 | 61.3083 | -61.3358 | -61.5143 | -0.027465 | 0.054932 | 0.004578 | 0.16479 | -0.013732 | -0.068664 | 0.073242 | 0.1236 | -0.054931 | -0.09613 | -0.36163 | -0.28839 | -0.23346 | -0.041198 | 122.8134 | 122.8821 | 61.5143 | -122.7539 | 122.7127 | 122.7676 | 61.5326 | -122.8638
322.5625 | 123.056 | -61.4777 | 61.2579 | -0.0098417 | -0.036671 | 0.1121 | 0.024802 | 0.053083 | -0.024381 | -0.023351 | -0.0079343 | -0.0052145 | 0.040039 | 0.060494 | -0.014877 | -0.01318 | 61.4319 | -61.2488 | 0.045776 | -61.4639 | 61.2671 | -61.5051 | -61.409 | -61.7706 | 0.059509 | -61.7249 | 61.1343 | 61.203 | -61.3678 | -61.5738 | -0.027466 | 0.068664 | 0.009155 | 0.22888 | 0.013733 | -0.054931 | 0.17395 | 0.10986 | -0.096131 | -0.1236 | -0.29297 | -0.24719 | -0.15106 | -0.054932 | 122.7448 | 122.9095 | 61.5234 | -122.6669 | 122.612 | 122.6807 | 61.5372 | -122.8317
324.2656 | 123.0148 | -61.4502 | 61.2946 | 0.0054168 | -0.040516 | 0.11402 | 0.024588 | 0.050092 | -0.026944 | -0.024633 | -0.0079343 | -0.0062827 | 0.038117 | 0.061135 | -0.01509 | -0.011471 | 61.4182 | -61.2122 | 0.059509 | -61.4822 | 61.2213 | -61.5189 | -61.4182 | -61.7752 | 0.073242 | -61.6882 | 61.1435 | 61.2076 | -61.3495 | -61.5463 | -0.068665 | 0.032043 | -0.073243 | 0.23804 | -0.032044 | -0.064087 | 0.1236 | 0.10071 | -0.096131 | -0.15106 | -0.32501 | -0.23804 | -0.14191 | -0.086975 | 122.6715 | 122.8683 | 61.5097 | -122.7127 | 122.5937 | 122.6578 | 61.5234 | -122.8409
325.9844 | 122.9416 | -61.4136 | 61.3953 | 0.0054168 | -0.034748 | 0.11487 | 0.029715 | 0.053938 | -0.025022 | -0.023778 | -0.0003053 | -0.0037191 | 0.040894 | 0.060921 | -0.016586 | -0.016385 | 61.5005 | -61.1435 | 0.16937 | -61.3815 | 61.322 | -61.4044 | -61.3174 | -61.7294 | 0.16022 | -61.6241 | 61.1938 | 61.2717 | -61.3083 | -61.4777 | 0.009155 | 0.09613 | -0.073243 | 0.27008 | 0.032043 | -0.064087 | 0.10529 | 0.10528 | -0.064087 | -0.20142 | -0.31586 | -0.21057 | -0.14649 | -0.1236 | 122.7356 | 122.9141 | 61.5829 | -122.7127 | 122.6074 | 122.6852 | 61.5738 | -122.8729
327.6719 | 123.0148 | -61.4639 | 61.2488 | -0.0022127 | -0.03902 | 0.11402 | 0.026724 | 0.053297 | -0.023313 | -0.023138 | 0.0073242 | -0.0032919 | 0.038544 | 0.059853 | -0.013381 | -0.013394 | 61.4456 | -61.2442 | 0.032043 | -61.4639 | 61.2396 | -61.5097 | -61.4136 | -61.7706 | 0.059509 | -61.702 | 61.1298 | 61.1984 | -61.3586 | -61.528 | -0.045777 | 0.050354 | -0.009155 | 0.21973 | 0 | -0.050354 | 0.19684 | 0.10529 | -0.064087 | -0.11902 | -0.3067 | -0.23804 | -0.17395 | -0.050354 | 122.7036 | 122.9095 | 61.496 | -122.6624 | 122.5937 | 122.6624 | 61.5234 | -122.7768
329.375 | 122.9691 | -61.4868 | 61.3586 | -0.017471 | -0.034321 | 0.1153 | 0.027579 | 0.052229 | -0.019467 | -0.022069 | -0.0003053 | 0.00012615 | 0.042176 | 0.058358 | -0.014663 | -0.014462 | 61.4273 | -61.2717 | 0.064087 | -61.4639 | 61.3586 | -61.4777 | -61.3953 | -61.7889 | 0.082397 | -61.7386 | 61.2396 | 61.2946 | -61.3266 | -61.5463 | 0.009155 | 0.091552 | 0 | 0.21515 | 0.022888 | -0.068664 | 0.068664 | 0.16022 | -0.05951 | -0.11902 | -0.30212 | -0.25177 | -0.19226 | -0.064087 | 122.8455 | 122.9141 | 61.5509 | -122.7539 | 122.7264 | 122.7814 | 61.5692 | -122.905
331.0781 | 122.9324 | -61.5005 | 61.3266 | 0.013046 | -0.035389 | 0.11573 | 0.024374 | 0.053083 | -0.022458 | -0.021215 | 0.022583 | -0.0011557 | 0.039185 | 0.059853 | -0.011886 | -0.01318 | 61.3312 | -61.3632 | -0.059509 | -61.5463 | 61.322 | -61.5143 | -61.441 | -61.8805 | -0.032043 | -61.8484 | 61.2122 | 61.2534 | -61.3861 | -61.5692 | -0.013733 | 0.059509 | -0.004578 | 0.13733 | -0.045777 | -0.10529 | 0.004578 | 0.11444 | -0.068665 | -0.11444 | -0.37994 | -0.3479 | -0.27924 | -0.073242 | 122.8226 | 122.8317 | 61.441 | -122.7676 | 122.7127 | 122.7539 | 61.4685 | -122.8958
332.7812 | 123.0194 | -61.4731 | 61.3083 | -0.0022127 | -0.036457 | 0.1168 | 0.025015 | 0.051161 | -0.025662 | -0.019292 | 0.0073242 | -0.0050009 | 0.040467 | 0.058999 | -0.016158 | -0.011258 | 61.4273 | -61.2213 | 0.045776 | -61.4639 | 61.2167 | -61.5097 | -61.4182 | -61.7844 | 0.054932 | -61.7111 | 61.1298 | 61.1755 | -61.3907 | -61.5463 | -0.036622 | 0.054931 | -0.091553 | 0.25177 | 0.009155 | -0.045776 | 0.11902 | 0.082397 | -0.073243 | -0.17853 | -0.31128 | -0.23804 | -0.16479 | -0.13275 | 122.6898 | 122.9004 | 61.5189 | -122.7264 | 122.6028 | 122.6486 | 61.528 | -122.8546
334.5 | 123.0194 | -61.4319 | 61.3495 | -0.0022127 | -0.03902 | 0.11316 | 0.02822 | 0.051161 | -0.026731 | -0.026342 | 0.0073242 | -0.0058555 | 0.040467 | 0.061348 | -0.019149 | -0.013394 | 61.4136 | -61.2442 | 0.050354 | -61.4731 | 61.2854 | -61.4639 | -61.3678 | -61.8164 | 0.027466 | -61.7203 | 61.1526 | 61.2396 | -61.322 | -61.5417 | -0.032043 | 0.064087 | -0.064087 | 0.18768 | -0.041198 | -0.10529 | 0.064087 | 0.10986 | -0.10986 | -0.19684 | -0.38452 | -0.28839 | -0.17853 | -0.10986 | 122.7173 | 122.8455 | 61.4822 | -122.7173 | 122.5845 | 122.6715 | 61.4594 | -122.8912
336.2188 | 122.9691 | -61.4456 | 61.3449 | -0.0022127 | -0.031757 | 0.11338 | 0.028433 | 0.051161 | -0.02374 | -0.024847 | 0.0073242 | -0.0026511 | 0.042816 | 0.059853 | -0.016372 | -0.014676 | 61.4227 | -61.2854 | 0.054932 | -61.4639 | 61.3541 | -61.4548 | -61.3953 | -61.8301 | 0.059509 | -61.7477 | 61.2671 | 61.3495 | -61.3083 | -61.5143 | -0.009155 | 0.050354 | 0.009155 | 0.16022 | -0.01831 | -0.068664 | 0.077819 | 0.13733 | -0.068664 | -0.07782 | -0.38452 | -0.30212 | -0.23346 | 0.004577 | 122.7997 | 122.8683 | 61.5006 | -122.7402 | 122.7127 | 122.7951 | 61.5051 | -122.8592
337.9062 | 123.0423 | -61.4456 | 61.2671 | 0.020676 | -0.034534 | 0.11658 | 0.024374 | 0.053938 | -0.024381 | -0.023778 | -0.0079343 | -0.0030783 | 0.038758 | 0.060707 | -0.013595 | -0.012753 | 61.3495 | -61.3403 | -0.050354 | -61.5509 | 61.29 | -61.528 | -61.441 | -61.8576 | -0.032043 | -61.7981 | 61.1755 | 61.2213 | -61.3861 | -61.5784 | -0.082397 | 0.004578 | 0.022888 | 0.10529 | -0.10528 | -0.10986 | 0.082397 | 0.05951 | -0.13275 | -0.091553 | -0.41199 | -0.35248 | -0.21973 | -0.045777 | 122.7356 | 122.7951 | 61.3953 | -122.7081 | 122.6212 | 122.6669 | 61.4136 | -122.8455
339.5938 | 123.0423 | -61.3724 | 61.3449 | -0.0022127 | -0.040943 | 0.11445 | 0.029074 | 0.050947 | -0.030576 | -0.023778 | 0.0073242 | -0.0052145 | 0.040894 | 0.060067 | -0.018936 | -0.012753 | 61.4777 | -61.1664 | 0.14648 | -61.4182 | 61.3037 | -61.4273 | -61.322 | -61.7249 | 0.15106 | -61.6058 | 61.171 | 61.2991 | -61.2717 | -61.496 | -0.054932 | 0.050354 | -0.041199 | 0.20599 | -0.045777 | -0.096131 | 0.13275 | 0.10071 | -0.1236 | -0.17395 | -0.35248 | -0.23346 | -0.10986 | -0.045777 | 122.6761 | 122.85 | 61.5189 | -122.6669 | 122.5433 | 122.6715 | 61.5234 | -122.8409
341.2812 | 122.9553 | -61.4594 | 61.3403 | -0.0022127 | -0.034748 | 0.11509 | 0.029288 | 0.054151 | -0.022244 | -0.024419 | 0.0073242 | -0.0035055 | 0.042603 | 0.059212 | -0.016372 | -0.01553 | 61.409 | -61.2854 | 0.068665 | -61.4685 | 61.3678 | -61.4777 | -61.3815 | -61.7935 | 0.07782 | -61.734 | 61.2717 | 61.3037 | -61.3403 | -61.5143 | -0.01831 | 0.07782 | 0.027466 | 0.17395 | -0.009155 | -0.086975 | 0.068665 | 0.11902 | -0.054931 | -0.068665 | -0.33417 | -0.27466 | -0.21973 | -0.036621 | 122.8271 | 122.8683 | 61.528 | -122.7219 | 122.731 | 122.7631 | 61.5372 | -122.8546
343 | 122.9095 | -61.4868 | 61.2991 | 0.0054168 | -0.036243 | 0.11338 | 0.026511 | 0.053297 | -0.022244 | -0.020147 | 0.0073242 | -0.0026511 | 0.040894 | 0.06263 | -0.014236 | -0.014249 | 61.3312 | -61.3586 | -0.045776 | -61.5463 | 61.2946 | -61.5189 | -61.4273 | -61.853 | -0.032043 | -61.8301 | 61.1847 | 61.2717 | -61.3724 | -61.5738 | -0.032044 | 0.059509 | -0.004577 | 0.12817 | -0.05951 | -0.11902 | 0.032044 | 0.11444 | -0.086976 | -0.11444 | -0.36621 | -0.34332 | -0.25635 | -0.027466 | 122.7814 | 122.818 | 61.441 | -122.7264 | 122.6715 | 122.7585 | 61.4548 | -122.8729
344.6875 | 122.8912 | -61.5189 | 61.2991 | 0.0054168 | -0.035175 | 0.11295 | 0.024161 | 0.049879 | -0.021817 | -0.022283 | 0.014954 | -0.0032919 | 0.040894 | 0.06028 | -0.01509 | -0.011899 | 61.3358 | -61.3541 | -0.018311 | -61.5189 | 61.2808 | -61.5189 | -61.4319 | -61.8668 | -0.018311 | -61.8439 | 61.1984 | 61.2625 | -61.4044 | -61.5646 | 0 | 0.086975 | -0.01831 | 0.16479 | 0 | -0.086975 | 0.036621 | 0.11444 | -0.045776 | -0.10071 | -0.3479 | -0.32501 | -0.27924 | -0.036621 | 122.7997 | 122.8546 | 61.5005 | -122.731 | 122.7173 | 122.7814 | 61.5005 | -122.8638
346.375 | 123.024 | -61.4731 | 61.2625 | 0.0054168 | -0.037525 | 0.11402 | 0.023734 | 0.049879 | -0.02609 | -0.022497 | -0.0079343 | -0.0037191 | 0.041748 | 0.061135 | -0.015731 | -0.010403 | 61.3083 | -61.3449 | -0.059509 | -61.5509 | 61.2854 | -61.5189 | -61.4319 | -61.8713 | -0.036621 | -61.8164 | 61.1801 | 61.235 | -61.3815 | -61.5646 | -0.045777 | 0.041198 | 0.022888 | 0.12817 | -0.07782 | -0.11902 | 0.045777 | 0.091552 | -0.091553 | -0.082397 | -0.39825 | -0.34332 | -0.25177 | -0.027466 | 122.7585 | 122.7814 | 61.4136 | -122.6944 | 122.6532 | 122.7081 | 61.4365 | -122.8271
348.0625 | 122.9736 | -61.4685 | 61.3083 | -0.0098417 | -0.037952 | 0.11402 | 0.026724 | 0.050092 | -0.028012 | -0.023138 | 0.014954 | -0.0043601 | 0.041107 | 0.058144 | -0.018295 | -0.013394 | 61.3861 | -61.2076 | 0.059509 | -61.4594 | 61.2122 | -61.4777 | -61.3861 | -61.7844 | 0.059509 | -61.6974 | 61.116 | 61.2167 | -61.3495 | -61.5372 | -0.009155 | 0.082398 | -0.096131 | 0.26093 | 0.009155 | -0.073243 | 0.077819 | 0.11902 | -0.068664 | -0.19226 | -0.31586 | -0.22888 | -0.16022 | -0.091553 | 122.6807 | 122.8546 | 61.528 | -122.6944 | 122.5845 | 122.6852 | 61.528 | -122.8455
349.75 | 123.0057 | -61.4777 | 61.2717 | 0.0054168 | -0.035389 | 0.11551 | 0.026511 | 0.047743 | -0.024594 | -0.024633 | -0.0079343 | -0.0028647 | 0.041962 | 0.059426 | -0.014236 | -0.015317 | 61.3358 | -61.3495 | -0.045776 | -61.5463 | 61.2671 | -61.528 | -61.4456 | -61.8713 | -0.041199 | -61.821 | 61.1801 | 61.235 | -61.3861 | -61.5692 | -0.050354 | 0.032043 | -0.004577 | 0.12817 | -0.068665 | -0.10071 | 0.064087 | 0.091553 | -0.091553 | -0.091552 | -0.39368 | -0.34332 | -0.25177 | -0.036621 | 122.7448 | 122.8134 | 61.4319 | -122.7173 | 122.6578 | 122.7127 | 61.4365 | -122.8409
351.4844 | 122.9919 | -61.377 | 61.3495 | 0.013046 | -0.035389 | 0.1168 | 0.029288 | 0.05052 | -0.028653 | -0.023138 | -0.0003053 | -0.0058555 | 0.039612 | 0.058999 | -0.020858 | -0.011899 | 61.496 | -61.116 | 0.1831 | -61.3678 | 61.29 | -61.409 | -61.3266 | -61.7111 | 0.1831 | -61.5784 | 61.1893 | 61.2671 | -61.2762 | -61.4548 | -0.032044 | 0.050354 | -0.059509 | 0.26093 | 0.009155 | -0.041199 | 0.14648 | 0.10071 | -0.07782 | -0.16022 | -0.33417 | -0.20142 | -0.1236 | -0.082397 | 122.6669 | 122.8729 | 61.5601 | -122.6761 | 122.5662 | 122.644 | 61.5601 | -122.8043
353.2969 | 122.9828 | -61.4639 | 61.3037 | -0.0022127 | -0.039234 | 0.11466 | 0.02822 | 0.053083 | -0.026944 | -0.022924 | 0.0073242 | -0.0060691 | 0.042816 | 0.058358 | -0.018722 | -0.011685 | 61.4227 | -61.2259 | 0.050354 | -61.4548 | 61.2305 | -61.4822 | -61.4136 | -61.7844 | 0.050354 | -61.6974 | 61.1343 | 61.1938 | -61.3541 | -61.5509 | -0.018311 | 0.050354 | -0.073242 | 0.23804 | 0.009155 | -0.041199 | 0.11902 | 0.10986 | -0.086975 | -0.16937 | -0.32043 | -0.23346 | -0.14648 | -0.10986 | 122.6944 | 122.8867 | 61.5143 | -122.7173 | 122.5983 | 122.6578 | 61.5143 | -122.8546
355.0938 | 123.0011 | -61.4502 | 61.2808 | 0.0054168 | -0.040516 | 0.11316 | 0.026083 | 0.052656 | -0.023953 | -0.023138 | -0.0003053 | -0.0052145 | 0.039398 | 0.058358 | -0.015945 | -0.016171 | 61.4182 | -61.235 | 0.045776 | -61.4685 | 61.2396 | -61.4777 | -61.4044 | -61.7889 | 0.059509 | -61.6882 | 61.116 | 61.171 | -61.3449 | -61.5463 | -0.027466 | 0.045776 | -0.041199 | 0.21515 | -0.018311 | -0.064087 | 0.13733 | 0.10529 | -0.096131 | -0.16479 | -0.33874 | -0.23804 | -0.14191 | -0.10986 | 122.6898 | 122.8683 | 61.496 | -122.6852 | 122.5662 | 122.6212 | 61.5097 | -122.8271
356.7969 | 122.937 | -61.441 | 61.3358 | -0.0022127 | -0.034534 | 0.11466 | 0.026083 | 0.051588 | -0.021176 | -0.023778 | -0.0003053 | -0.0030783 | 0.04303 | 0.060067 | -0.016799 | -0.017026 | 61.4044 | -61.2625 | 0.073242 | -61.4456 | 61.3678 | -61.4502 | -61.3953 | -61.7752 | 0.059509 | -61.7249 | 61.235 | 61.3083 | -61.322 | -61.5143 | -0.009155 | 0.045776 | 0.032044 | 0.17853 | -0.004578 | -0.050354 | 0.068665 | 0.11902 | -0.073242 | -0.10071 | -0.33417 | -0.28381 | -0.21057 | -0.027465 | 122.8088 | 122.8455 | 61.5143 | -122.731 | 122.6761 | 122.7493 | 61.5005 | -122.85
358.5469 | 122.8867 | -61.4319 | 61.3724 | -0.0022127 | -0.035602 | 0.11551 | 0.027152 | 0.052656 | -0.024167 | -0.026556 | -0.0003053 | -0.0043601 | 0.04303 | 0.05793 | -0.017654 | -0.014676 | 61.4182 | -61.2442 | 0.09613 | -61.4502 | 61.3541 | -61.4456 | -61.3586 | -61.8027 | 0.068665 | -61.7111 | 61.2625 | 61.2991 | -61.3266 | -61.4914 | -0.013733 | 0.073242 | -0.01831 | 0.18768 | -0.01831 | -0.091552 | 0.045777 | 0.10529 | -0.059509 | -0.10986 | -0.37079 | -0.27924 | -0.21973 | -0.073242 | 122.7859 | 122.85 | 61.528 | -122.731 | 122.6944 | 122.731 | 61.5006 | -122.8638
360.2656 | 122.9462 | -61.4548 | 61.3266 | -0.0022127 | -0.035602 | 0.11509 | 0.028006 | 0.051588 | -0.023313 | -0.022497 | 0.0073242 | -0.0011557 | 0.040894 | 0.061989 | -0.016158 | -0.012753 | 61.409 | -61.2625 | 0.082397 | -61.4548 | 61.3449 | -61.4548 | -61.3678 | -61.7935 | 0.068665 | -61.7294 | 61.2579 | 61.2946 | -61.3037 | -61.5051 | 0 | 0.086975 | 0.018311 | 0.19226 | 0 | -0.086975 | 0.082398 | 0.15106 | -0.050354 | -0.068664 | -0.33874 | -0.27466 | -0.2243 | -0.032043 | 122.7997 | 122.8638 | 61.5372 | -122.6944 | 122.7127 | 122.7493 | 61.5234 | -122.8317
362.0312 | 122.9599 | -61.3815 | 61.3678 | 0.013046 | -0.037311 | 0.11509 | 0.029715 | 0.050947 | -0.02844 | -0.023992 | -0.0003053 | -0.0060691 | 0.041107 | 0.058785 | -0.019576 | -0.015103 | 61.4868 | -61.1114 | 0.18768 | -61.3815 | 61.3083 | -61.4319 | -61.3358 | -61.6928 | 0.19226 | -61.5921 | 61.171 | 61.2579 | -61.2671 | -61.4731 | -0.050354 | 0.045777 | -0.059509 | 0.27008 | 0 | -0.045777 | 0.11902 | 0.11444 | -0.091552 | -0.19684 | -0.31128 | -0.21057 | -0.11902 | -0.10986 | 122.6898 | 122.8683 | 61.5692 | -122.7036 | 122.5525 | 122.6395 | 61.5738 | -122.8409
363.7344 | 123.0103 | -61.377 | 61.3174 | -0.0022127 | -0.039234 | 0.1168 | 0.025229 | 0.052015 | -0.026731 | -0.02506 | -0.0003053 | -0.0058555 | 0.041748 | 0.061776 | -0.018508 | -0.013394 | 61.3861 | -61.2488 | 0.041199 | -61.4639 | 61.2717 | -61.4639 | -61.3541 | -61.7935 | 0.027466 | -61.6928 | 61.171 | 61.2671 | -61.2946 | -61.5143 | -0.086975 | 0.022888 | -0.045777 | 0.12817 | -0.086975 | -0.10986 | 0.068664 | 0.082397 | -0.13733 | -0.14648 | -0.41656 | -0.31586 | -0.17853 | -0.050354 | 122.6486 | 122.7631 | 61.4182 | -122.6715 | 122.5479 | 122.644 | 61.4044 | -122.8317
365.5 | 122.8638 | -61.4777 | 61.2854 | 0.0054168 | -0.034962 | 0.11295 | 0.026297 | 0.054151 | -0.019895 | -0.023778 | 0.0073242 | -0.00051485 | 0.041107 | 0.061135 | -0.014877 | -0.014035 | 61.3678 | -61.2808 | 0.027466 | -61.496 | 61.3129 | -61.4777 | -61.441 | -61.821 | 0.022888 | -61.8118 | 61.1801 | 61.2259 | -61.3449 | -61.5692 | 0 | 0.036621 | 0.027466 | 0.19684 | -0.018311 | -0.054932 | 0.082398 | 0.13275 | -0.091553 | -0.10529 | -0.34332 | -0.33417 | -0.24262 | -0.059509 | 122.7905 | 122.8455 | 61.5051 | -122.7264 | 122.6578 | 122.7036 | 61.5005 | -122.8546
367.2188 | 122.9279 | -61.4273 | 61.3358 | 0.0054168 | -0.037525 | 0.11381 | 0.027365 | 0.050733 | -0.023526 | -0.021642 | 0.0073242 | -0.00094205 | 0.04068 | 0.059639 | -0.016799 | -0.014462 | 61.3998 | -61.2579 | 0.073242 | -61.441 | 61.3678 | -61.4594 | -61.3724 | -61.7981 | 0.068665 | -61.7249 | 61.2579 | 61.3037 | -61.322 | -61.5005 | -0.032044 | 0.054932 | 0.032044 | 0.16937 | -0.013733 | -0.068665 | 0.064087 | 0.10529 | -0.073242 | -0.077819 | -0.37079 | -0.29755 | -0.22431 | -0.032043 | 122.7951 | 122.8271 | 61.5005 | -122.7081 | 122.6852 | 122.731 | 61.496 | -122.8363
368.9219 | 122.9919 | -61.4273 | 61.2396 | -0.0022127 | -0.031757 | 0.11402 | 0.027152 | 0.051161 | -0.025449 | -0.022497 | -0.0003053 | -0.0037191 | 0.042816 | 0.06028 | -0.018295 | -0.015103 | 61.409 | -61.2488 | 0.036621 | -61.4548 | 61.2076 | -61.496 | -61.4044 | -61.7615 | 0.059509 | -61.702 | 61.1252 | 61.1847 | -61.3403 | -61.5051 | -0.068665 | 0.022888 | -0.032043 | 0.17853 | -0.027466 | -0.050354 | 0.16937 | 0.086975 | -0.07782 | -0.11444 | -0.33417 | -0.27466 | -0.19684 | -0.054932 | 122.6349 | 122.8363 | 61.4639 | -122.644 | 122.5525 | 122.612 | 61.4868 | -122.7448
370.7031 | 122.9507 | -61.4182 | 61.2717 | 0.0054168 | -0.039448 | 0.11402 | 0.026511 | 0.053083 | -0.026303 | -0.022497 | -0.0079343 | -0.0050009 | 0.039612 | 0.061989 | -0.016799 | -0.011685 | 61.4044 | -61.1984 | 0.054932 | -61.4548 | 61.2167 | -61.4914 | -61.3998 | -61.7615 | 0.045776 | -61.6791 | 61.1114 | 61.1893 | -61.3358 | -61.5372 | -0.073242 | 0.018311 | -0.054931 | 0.21973 | -0.036621 | -0.054932 | 0.13275 | 0.082398 | -0.11902 | -0.16022 | -0.34332 | -0.26093 | -0.14191 | -0.082397 | 122.6349 | 122.8226 | 61.4731 | -122.6715 | 122.5296 | 122.6074 | 61.4639 | -122.8088
372.4688 | 122.9645 | -61.409 | 61.2671 | 0.0054168 | -0.039661 | 0.11637 | 0.02587 | 0.052869 | -0.029508 | -0.024419 | 0.0073242 | -0.0039329 | 0.041535 | 0.060494 | -0.018295 | -0.01318 | 61.377 | -61.2213 | 0.027466 | -61.4731 | 61.2167 | -61.4777 | -61.3953 | -61.7844 | 0.054932 | -61.6791 | 61.1389 | 61.1938 | -61.3358 | -61.5143 | -0.068664 | 0.013733 | -0.050354 | 0.18768 | -0.064086 | -0.077819 | 0.10986 | 0.073243 | -0.10529 | -0.12817 | -0.37537 | -0.27008 | -0.16479 | -0.073242 | 122.6257 | 122.7859 | 61.4365 | -122.6624 | 122.5479 | 122.6028 | 61.4639 | -122.7814
374.1875 | 122.9599 | -61.4273 | 61.2991 | -0.0022127 | -0.039234 | 0.11338 | 0.026083 | 0.054151 | -0.025235 | -0.024419 | -0.0003053 | -0.0050009 | 0.041107 | 0.058358 | -0.016586 | -0.011258 | 61.4136 | -61.1984 | 0.050354 | -61.4548 | 61.2122 | -61.4639 | -61.3586 | -61.7706 | 0.045776 | -61.702 | 61.1069 | 61.171 | -61.322 | -61.528 | -0.036621 | 0.068664 | -0.086975 | 0.22888 | -0.027466 | -0.09613 | 0.11444 | 0.10529 | -0.10071 | -0.19226 | -0.34332 | -0.27466 | -0.17395 | -0.12817 | 122.6395 | 122.8409 | 61.4777 | -122.6578 | 122.5342 | 122.5983 | 61.4731 | -122.8271
375.875 | 122.9141 | -61.4044 | 61.377 | -0.0022127 | -0.035389 | 0.11594 | 0.027365 | 0.05351 | -0.025876 | -0.02271 | 0.0073242 | -0.0047873 | 0.040039 | 0.060921 | -0.01744 | -0.014249 | 61.4777 | -61.0977 | 0.18768 | -61.3815 | 61.2854 | -61.409 | -61.3174 | -61.6882 | 0.17395 | -61.6058 | 61.203 | 61.2579 | -61.2534 | -61.4777 | -0.004578 | 0.086975 | -0.091553 | 0.3067 | 0.022888 | -0.064087 | 0.10071 | 0.15106 | -0.073242 | -0.17395 | -0.28381 | -0.20142 | -0.12817 | -0.11902 | 122.6898 | 122.8821 | 61.5921 | -122.6944 | 122.6074 | 122.6624 | 61.5784 | -122.8546
377.5938 | 122.9965 | -61.377 | 61.3312 | 0.013046 | -0.036884 | 0.11765 | 0.028647 | 0.054365 | -0.026303 | -0.025487 | 0.0073242 | -0.0050009 | 0.040894 | 0.060921 | -0.017013 | -0.01553 | 61.3678 | -61.2259 | 0.022888 | -61.441 | 61.29 | -61.4685 | -61.377 | -61.7935 | 0.027466 | -61.6837 | 61.1755 | 61.1984 | -61.3129 | -61.5143 | -0.091553 | 0 | -0.041199 | 0.15106 | -0.064087 | -0.064087 | 0.036621 | 0.064087 | -0.13733 | -0.15564 | -0.41656 | -0.3067 | -0.16937 | -0.13275 | 122.6669 | 122.7448 | 61.3998 | -122.7081 | 122.5525 | 122.5754 | 61.4044 | -122.8455
379.375 | 122.9141 | -61.4319 | 61.3129 | 0.0054168 | -0.032398 | 0.11423 | 0.028433 | 0.052229 | -0.020108 | -0.023138 | -0.0003053 | -0.0047873 | 0.041962 | 0.059212 | -0.014663 | -0.016171 | 61.3998 | -61.2579 | 0.07782 | -61.4273 | 61.3449 | -61.4685 | -61.3586 | -61.7523 | 0.068665 | -61.7157 | 61.2396 | 61.2762 | -61.3129 | -61.4777 | -0.036621 | 0.073242 | 0.032044 | 0.17395 | 0.004578 | -0.068664 | 0.086975 | 0.11902 | -0.045776 | -0.073242 | -0.32043 | -0.28381 | -0.23804 | -0.036621 | 122.7768 | 122.8317 | 61.5097 | -122.6715 | 122.6715 | 122.7081 | 61.5006 | -122.7905
381.0781 | 122.8409 | -61.4868 | 61.2946 | 0.0054168 | -0.031971 | 0.11124 | 0.024588 | 0.052442 | -0.02139 | -0.021001 | -0.0003053 | 0.00098055 | 0.042816 | 0.061135 | -0.011886 | -0.014889 | 61.4227 | -61.2305 | 0.082397 | -61.4594 | 61.2946 | -61.4639 | -61.3907 | -61.7798 | 0.073242 | -61.7523 | 61.1847 | 61.2579 | -61.3174 | -61.5372 | 0.022888 | 0.09613 | 0 | 0.25635 | 0.027465 | -0.068665 | 0.12817 | 0.16937 | -0.050354 | -0.10986 | -0.29297 | -0.2655 | -0.21515 | -0.036621 | 122.7814 | 122.9095 | 61.5692 | -122.6852 | 122.6715 | 122.7448 | 61.5601 | -122.8317
382.8594 | 122.9965 | -61.377 | 61.3129 | -0.0098417 | -0.040516 | 0.11573 | 0.02822 | 0.051161 | -0.02844 | -0.024847 | 0.0073242 | -0.0073507 | 0.04068 | 0.060067 | -0.019363 | -0.01254 | 61.4731 | -61.1114 | 0.15564 | -61.3724 | 61.2534 | -61.4365 | -61.322 | -61.6791 | 0.16022 | -61.5601 | 61.1664 | 61.2442 | -61.2579 | -61.4777 | -0.059509 | 0.054932 | -0.059509 | 0.2655 | 0.004578 | -0.050354 | 0.16022 | 0.11902 | -0.10071 | -0.14648 | -0.30212 | -0.18311 | -0.082398 | -0.068664 | 122.6303 | 122.85 | 61.5326 | -122.6349 | 122.5433 | 122.6212 | 61.5372 | -122.7905
384.625 | 122.8729 | -61.3998 | 61.3907 | -0.0022127 | -0.035602 | 0.11487 | 0.029288 | 0.05052 | -0.025662 | -0.023351 | -0.0079343 | -0.0039329 | 0.042176 | 0.058999 | -0.018508 | -0.014249 | 61.4044 | -61.1801 | 0.10986 | -61.4182 | 61.3358 | -61.4227 | -61.3312 | -61.7706 | 0.073242 | -61.6974 | 61.2488 | 61.3037 | -61.3037 | -61.4639 | -0.022888 | 0.068664 | -0.054932 | 0.21973 | -0.018311 | -0.086975 | 0.013733 | 0.09613 | -0.064087 | -0.14191 | -0.37079 | -0.29755 | -0.23346 | -0.086975 | 122.7356 | 122.8043 | 61.5097 | -122.7219 | 122.6486 | 122.7036 | 61.4731 | -122.8546
386.3438 | 122.9919 | -61.4502 | 61.2488 | 0.0054168 | -0.037098 | 0.11445 | 0.022452 | 0.050733 | -0.022672 | -0.020788 | -0.0003053 | -0.0015829 | 0.042389 | 0.060494 | -0.013809 | -0.013821 | 61.322 | -61.3083 | -0.036621 | -61.528 | 61.2305 | -61.5097 | -61.409 | -61.7981 | 0.004578 | -61.7477 | 61.1389 | 61.2076 | -61.3495 | -61.5646 | -0.05951 | 0.041198 | -0.01831 | 0.14191 | -0.07782 | -0.11902 | 0.073242 | 0.10071 | -0.11444 | -0.10986 | -0.3479 | -0.29755 | -0.18311 | -0.041198 | 122.6807 | 122.7722 | 61.4136 | -122.6578 | 122.5891 | 122.6578 | 61.4548 | -122.8134
388.125 | 122.85 | -61.3998 | 61.377 | 0.0054168 | -0.034534 | 0.11658 | 0.028006 | 0.053083 | -0.02609 | -0.023351 | -0.0003053 | -0.0022239 | 0.04303 | 0.058358 | -0.015945 | -0.013394 | 61.3907 | -61.1984 | 0.11444 | -61.4227 | 61.3266 | -61.4273 | -61.3495 | -61.7935 | 0.068665 | -61.7065 | 61.2305 | 61.322 | -61.2808 | -61.4777 | -0.027466 | 0.050354 | -0.050354 | 0.20142 | -0.022888 | -0.073242 | 0.013733 | 0.11902 | -0.07782 | -0.14648 | -0.39368 | -0.3067 | -0.22888 | -0.054932 | 122.7264 | 122.7905 | 61.5143 | -122.7264 | 122.6303 | 122.7219 | 61.4685 | -122.8546
389.8281 | 122.8363 | -61.4868 | 61.2946 | 0.0054168 | -0.035389 | 0.11381 | 0.026511 | 0.047743 | -0.019254 | -0.021429 | 0.0073242 | -0.0020103 | 0.041107 | 0.059212 | -0.014449 | -0.013821 | 61.3586 | -61.2717 | 0.013733 | -61.4731 | 61.29 | -61.4822 | -61.3953 | -61.8118 | 0.004578 | -61.7844 | 61.1526 | 61.2259 | -61.3449 | -61.5646 | 0.004577 | 0.091552 | -0.004578 | 0.21515 | 0.013733 | -0.077819 | 0.064087 | 0.14191 | -0.07782 | -0.14191 | -0.32501 | -0.29755 | -0.21973 | -0.068665 | 122.7768 | 122.8455 | 61.5005 | -122.6898 | 122.6395 | 122.7127 | 61.4914 | -122.8592
391.5625 | 122.8821 | -61.4594 | 61.2808 | 0.0054168 | -0.03603 | 0.11573 | 0.02587 | 0.05351 | -0.021604 | -0.022497 | 0.014954 | -0.0026511 | 0.04068 | 0.060067 | -0.015518 | -0.012967 | 61.2854 | -61.3815 | -0.050354 | -61.5372 | 61.2808 | -61.5097 | -61.4044 | -61.8759 | -0.032043 | -61.8073 | 61.1664 | 61.2259 | -61.3586 | -61.5692 | -0.050354 | 0.054932 | 0 | 0.07782 | -0.077819 | -0.13275 | 0.004577 | 0.10071 | -0.10986 | -0.11444 | -0.41656 | -0.3479 | -0.23804 | -0.054932 | 122.7402 | 122.7448 | 61.409 | -122.6852 | 122.6257 | 122.6852 | 61.4273 | -122.85
393.2812 | 122.8683 | -61.4319 | 61.3037 | 0.0054168 | -0.035389 | 0.11231 | 0.029501 | 0.050306 | -0.02139 | -0.022497 | -0.0003053 | -0.0024375 | 0.042389 | 0.061135 | -0.016586 | -0.015103 | 61.3907 | -61.2259 | 0.10071 | -61.4273 | 61.2946 | -61.4685 | -61.409 | -61.7615 | 0.10071 | -61.6974 | 61.1893 | 61.2488 | -61.322 | -61.5372 | -0.036621 | 0.022888 | -0.009155 | 0.20599 | 0.004578 | -0.01831 | 0.086975 | 0.10986 | -0.10529 | -0.11444 | -0.32959 | -0.2655 | -0.16022 | -0.054932 | 122.7264 | 122.8226 | 61.5326 | -122.7127 | 122.6212 | 122.6807 | 61.5326 | -122.8409
395.0469 | 122.905 | -61.4273 | 61.322 | 0.0054168 | -0.033466 | 0.11316 | 0.028647 | 0.051374 | -0.024167 | -0.021429 | 0.014954 | -0.0030783 | 0.042603 | 0.059212 | -0.01744 | -0.01318 | 61.3724 | -61.2305 | 0.091553 | -61.4319 | 61.3266 | -61.4594 | -61.3861 | -61.7706 | 0.10986 | -61.702 | 61.203 | 61.2854 | -61.3037 | -61.4777 | -0.032044 | 0.041199 | 0.004578 | 0.19684 | -0.004578 | -0.045777 | 0.050354 | 0.1236 | -0.050354 | -0.11902 | -0.34332 | -0.27466 | -0.2243 | -0.036621 | 122.7539 | 122.7997 | 61.5189 | -122.7081 | 122.6303 | 122.7127 | 61.5372 | -122.7997
396.75 | 122.9233 | -61.4182 | 61.2854 | -0.0098417 | -0.037311 | 0.11466 | 0.026938 | 0.053724 | -0.028653 | -0.022283 | 0.014954 | -0.0037191 | 0.039185 | 0.056649 | -0.018295 | -0.011685 | 61.377 | -61.1893 | 0.059509 | -61.4548 | 61.1801 | -61.4548 | -61.3815 | -61.7889 | 0.054932 | -61.6882 | 61.1114 | 61.1755 | -61.322 | -61.4777 | -0.036621 | 0.036621 | -0.10529 | 0.22888 | -0.036621 | -0.073242 | 0.091553 | 0.096131 | -0.059509 | -0.17395 | -0.37079 | -0.27008 | -0.21057 | -0.10986 | 122.5983 | 122.7951 | 61.4777 | -122.6669 | 122.5296 | 122.5937 | 61.4731 | -122.7631
398.5312 | 122.9828 | -61.4227 | 61.235 | 0.0054168 | -0.03902 | 0.11252 | 0.025656 | 0.051374 | -0.023099 | -0.023778 | -0.0003053 | -0.0043601 | 0.039826 | 0.058358 | -0.014663 | -0.012753 | 61.3953 | -61.2259 | 0.050354 | -61.441 | 61.1893 | -61.4731 | -61.4136 | -61.7569 | 0.064087 | -61.6837 | 61.0794 | 61.1481 | -61.3586 | -61.5143 | -0.050354 | 0.009155 | -0.045776 | 0.19684 | -0.018311 | -0.027466 | 0.16022 | 0.064086 | -0.091553 | -0.15564 | -0.33417 | -0.26093 | -0.16937 | -0.086975 | 122.612 | 122.818 | 61.4731 | -122.6486 | 122.5021 | 122.5708 | 61.4868 | -122.7493
400.25 | 122.9828 | -61.441 | 61.2305 | 0.0054168 | -0.036671 | 0.11445 | 0.025015 | 0.052015 | -0.025235 | -0.022283 | 0.022583 | -0.0041465 | 0.041535 | 0.060494 | -0.01509 | -0.014035 | 61.3312 | -61.2808 | -0.013733 | -61.4822 | 61.2213 | -61.4685 | -61.3998 | -61.7798 | 0.045776 | -61.702 | 61.1023 | 61.1664 | -61.3632 | -61.5372 | -0.027466 | 0.041199 | -0.009156 | 0.16022 | -0.041199 | -0.082398 | 0.10071 | 0.07782 | -0.09613 | -0.12817 | -0.33874 | -0.26093 | -0.16479 | -0.064087 | 122.6624 | 122.7722 | 61.4273 | -122.6303 | 122.5433 | 122.6074 | 61.4868 | -122.7676
401.9531 | 122.9233 | -61.4273 | 61.2854 | -0.0098417 | -0.040729 | 0.11701 | 0.027579 | 0.052656 | -0.02844 | -0.026128 | -0.0003053 | -0.0047873 | 0.038971 | 0.060067 | -0.018722 | -0.01254 | 61.3586 | -61.203 | 0.050354 | -61.4639 | 61.2259 | -61.4502 | -61.3586 | -61.7935 | 0.036621 | -61.6882 | 61.1206 | 61.1938 | -61.3174 | -61.5189 | -0.022888 | 0.068664 | -0.059509 | 0.2243 | -0.036621 | -0.10529 | 0.073243 | 0.10986 | -0.091553 | -0.1648 | -0.36621 | -0.26093 | -0.16937 | -0.091552 | 122.6532 | 122.7859 | 61.4777 | -122.644 | 122.5479 | 122.6212 | 61.4639 | -122.8043
403.7344 | 122.9279 | -61.4227 | 61.2991 | -0.0022127 | -0.037098 | 0.11466 | 0.026724 | 0.052442 | -0.026731 | -0.023351 | 0.0073242 | -0.0064963 | 0.041962 | 0.057503 | -0.017867 | -0.01318 | 61.3541 | -61.1984 | 0.045776 | -61.4639 | 61.2213 | -61.4456 | -61.3495 | -61.7798 | 0.032043 | -61.6608 | 61.1481 | 61.203 | -61.3129 | -61.4914 | -0.022889 | 0.073242 | -0.07782 | 0.2243 | -0.041199 | -0.11444 | 0.054932 | 0.10986 | -0.068665 | -0.15106 | -0.35706 | -0.23804 | -0.16937 | -0.09613 | 122.644 | 122.7768 | 61.4685 | -122.6486 | 122.5708 | 122.6257 | 61.4548 | -122.7905
405.5 | 122.9462 | -61.4502 | 61.2259 | -0.0022127 | -0.037098 | 0.1153 | 0.023947 | 0.052442 | -0.023099 | -0.023992 | 0.0073242 | -0.0035055 | 0.040039 | 0.059853 | -0.014449 | -0.01553 | 61.2946 | -61.3266 | -0.059509 | -61.5051 | 61.2579 | -61.496 | -61.4273 | -61.8393 | -0.032043 | -61.7752 | 61.1755 | 61.1984 | -61.3632 | -61.5417 | -0.045777 | 0.022888 | 0.032044 | 0.1236 | -0.054932 | -0.07782 | 0.068665 | 0.086975 | -0.091553 | -0.050354 | -0.3891 | -0.32501 | -0.23346 | -0.027466 | 122.7081 | 122.7448 | 61.3907 | -122.6532 | 122.6257 | 122.6486 | 61.4182 | -122.7676
407.2344 | 122.937 | -61.3541 | 61.3266 | 0.0054168 | -0.038166 | 0.1153 | 0.02886 | 0.053083 | -0.02844 | -0.024419 | -0.0079343 | -0.0054281 | 0.041107 | 0.056435 | -0.018508 | -0.014249 | 61.4731 | -61.1023 | 0.17395 | -61.3541 | 61.2671 | -61.3907 | -61.3129 | -61.6745 | 0.1831 | -61.5738 | 61.1801 | 61.2625 | -61.2396 | -61.4319 | -0.036621 | 0.041199 | -0.059509 | 0.25177 | 0 | -0.041199 | 0.14648 | 0.11444 | -0.07782 | -0.14648 | -0.32044 | -0.21973 | -0.14191 | -0.064087 | 122.6212 | 122.8271 | 61.528 | -122.6395 | 122.5342 | 122.6166 | 61.5372 | -122.7585
409.0156 | 122.8317 | -61.4182 | 61.3724 | 0.0054168 | -0.036671 | 0.11808 | 0.028006 | 0.051161 | -0.025022 | -0.02271 | 0.0073242 | -0.0022239 | 0.040039 | 0.060921 | -0.016372 | -0.014676 | 61.4548 | -61.1481 | 0.15564 | -61.3907 | 61.2762 | -61.409 | -61.3037 | -61.7523 | 0.10529 | -61.6608 | 61.2259 | 61.3037 | -61.29 | -61.4502 | 0.009155 | 0.11444 | -0.09613 | 0.27008 | 0.027466 | -0.086975 | 0.082398 | 0.12817 | -0.032043 | -0.14648 | -0.33417 | -0.24262 | -0.21057 | -0.068664 | 122.6944 | 122.8729 | 61.5738 | -122.6761 | 122.644 | 122.7219 | 61.5234 | -122.8226
410.7969 | 122.905 | -61.4182 | 61.2946 | 0.0054168 | -0.038593 | 0.11274 | 0.026724 | 0.051161 | -0.026731 | -0.024633 | 0.0073242 | -0.0052145 | 0.04303 | 0.060707 | -0.019363 | -0.013608 | 61.377 | -61.2122 | 0.036621 | -61.4365 | 61.2442 | -61.4502 | -61.3586 | -61.7661 | 0.027466 | -61.6791 | 61.116 | 61.2213 | -61.2854 | -61.496 | -0.032043 | 0.059509 | -0.050354 | 0.20599 | -0.01831 | -0.077819 | 0.082397 | 0.13275 | -0.07782 | -0.17853 | -0.3479 | -0.26093 | -0.1831 | -0.073243 | 122.6624 | 122.7951 | 61.4548 | -122.6532 | 122.5342 | 122.6395 | 61.4456 | -122.7905
412.5938 | 122.9782 | -61.4182 | 61.2076 | 0.013046 | -0.037952 | 0.11551 | 0.024161 | 0.050092 | -0.022031 | -0.024206 | -0.0003053 | -0.0017965 | 0.042389 | 0.060707 | -0.013809 | -0.015958 | 61.3541 | -61.2579 | 0 | -61.4639 | 61.2305 | -61.5005 | -61.3998 | -61.7477 | 0.041199 | -61.702 | 61.0977 | 61.1389 | -61.322 | -61.5143 | -0.082397 | 0.018311 | 0.022888 | 0.16022 | -0.045776 | -0.064087 | 0.14648 | 0.096131 | -0.09613 | -0.10986 | -0.32959 | -0.28381 | -0.18768 | -0.068665 | 122.6486 | 122.7722 | 61.4182 | -122.6074 | 122.5159 | 122.5571 | 61.4594 | -122.7219
414.3125 | 122.9599 | -61.4456 | 61.2396 | 0.0054168 | -0.037098 | 0.11509 | 0.02352 | 0.053938 | -0.021604 | -0.021001 | -0.0003053 | -0.0024375 | 0.040894 | 0.061989 | -0.01274 | -0.014249 | 61.3129 | -61.2946 | -0.041199 | -61.5051 | 61.2305 | -61.4914 | -61.4136 | -61.7889 | 0 | -61.7477 | 61.1435 | 61.1893 | -61.3174 | -61.5417 | -0.045776 | 0.032044 | -0.009155 | 0.15106 | -0.059509 | -0.091553 | 0.073242 | 0.12817 | -0.09613 | -0.09613 | -0.34332 | -0.30212 | -0.20599 | -0.050354 | 122.6761 | 122.7585 | 61.4044 | -122.6532 | 122.5891 | 122.6349 | 61.4456 | -122.7814
416.0781 | 122.9507 | -61.4456 | 61.2396 | 0.0054168 | -0.034962 | 0.11487 | 0.02352 | 0.051161 | -0.02139 | -0.022283 | 0.022583 | -0.0030783 | 0.040039 | 0.059639 | -0.014877 | -0.012967 | 61.3129 | -61.3083 | -0.054932 | -61.5143 | 61.2488 | -61.4731 | -61.3998 | -61.8393 | -0.041199 | -61.7889 | 61.1572 | 61.2076 | -61.3449 | -61.5555 | -0.027465 | 0.045777 | 0.009155 | 0.13733 | -0.068664 | -0.11444 | 0.073242 | 0.10071 | -0.10986 | -0.082397 | -0.39368 | -0.34332 | -0.23346 | -0.032043 | 122.6944 | 122.7585 | 61.3907 | -122.6395 | 122.6028 | 122.6532 | 61.4044 | -122.7951
417.8438 | 122.9187 | -61.409 | 61.2671 | -0.0022127 | -0.037525 | 0.1153 | 0.027792 | 0.052229 | -0.028012 | -0.01972 | -0.0079343 | -0.0067099 | 0.042603 | 0.061562 | -0.01744 | -0.012967 | 61.3678 | -61.203 | 0.036621 | -61.4365 | 61.1755 | -61.4548 | -61.377 | -61.7569 | 0.050354 | -61.6745 | 61.1023 | 61.2076 | -61.3037 | -61.5143 | -0.045776 | 0.032044 | -0.091553 | 0.20599 | -0.027465 | -0.059509 | 0.10071 | 0.10529 | -0.10529 | -0.1648 | -0.3479 | -0.2655 | -0.16022 | -0.059509 | 122.5845 | 122.7768 | 61.4456 | -122.644 | 122.5113 | 122.6166 | 61.4594 | -122.7814
419.6406 | 122.9507 | -61.3632 | 61.3083 | 0.020676 | -0.036884 | 0.11808 | 0.028433 | 0.053938 | -0.027799 | -0.024633 | -0.0003053 | -0.0039329 | 0.041321 | 0.056435 | -0.019576 | -0.014035 | 61.4685 | -61.0657 | 0.1831 | -61.3586 | 61.2579 | -61.4044 | -61.2991 | -61.6699 | 0.16937 | -61.5601 | 61.1664 | 61.2076 | -61.2396 | -61.4502 | -0.041199 | 0.064087 | -0.050354 | 0.29755 | 0.004577 | -0.05951 | 0.16022 | 0.1236 | -0.086975 | -0.14191 | -0.3067 | -0.19684 | -0.10986 | -0.10071 | 122.6212 | 122.8317 | 61.5463 | -122.6074 | 122.5296 | 122.5708 | 61.5326 | -122.7585
421.3438 | 122.8912 | -61.4685 | 61.2579 | -0.0022127 | -0.036243 | 0.11466 | 0.022665 | 0.053083 | -0.020535 | -0.021642 | 0.0073242 | -0.00094205 | 0.040894 | 0.060067 | -0.014663 | -0.014462 | 61.3083 | -61.3403 | -0.054932 | -61.5143 | 61.2534 | -61.4914 | -61.4136 | -61.821 | -0.045776 | -61.7889 | 61.1801 | 61.2259 | -61.3495 | -61.5417 | -0.022888 | 0.054932 | -0.004578 | 0.12817 | -0.045776 | -0.10071 | 0.050354 | 0.11902 | -0.073242 | -0.07782 | -0.35248 | -0.32043 | -0.24719 | -0.032044 | 122.7219 | 122.7768 | 61.4136 | -122.6715 | 122.6486 | 122.6944 | 61.4227 | -122.7997
423.125 | 122.9462 | -61.441 | 61.2305 | 0.013046 | -0.036457 | 0.11423 | 0.027365 | 0.050092 | -0.022458 | -0.021215 | -0.0003053 | -0.0028647 | 0.043671 | 0.061348 | -0.01509 | -0.012967 | 61.3174 | -61.3037 | -0.050354 | -61.4914 | 61.2488 | -61.496 | -61.3998 | -61.8164 | -0.027466 | -61.7752 | 61.1526 | 61.1938 | -61.3358 | -61.5601 | -0.054932 | 0.041199 | 0.01831 | 0.13733 | -0.050354 | -0.091553 | 0.086975 | 0.10529 | -0.11902 | -0.07782 | -0.37537 | -0.33417 | -0.21515 | -0.036621 | 122.6898 | 122.7585 | 61.3907 | -122.6303 | 122.5937 | 122.6349 | 61.4136 | -122.7905
424.8906 | 122.8775 | -61.409 | 61.322 | 0.0054168 | -0.032825 | 0.1121 | 0.028006 | 0.052015 | -0.021176 | -0.021642 | -0.0079343 | -0.0035055 | 0.042816 | 0.062203 | -0.018295 | -0.014462 | 61.377 | -61.2167 | 0.086975 | -61.4044 | 61.2808 | -61.4136 | -61.3541 | -61.7203 | 0.10071 | -61.6791 | 61.1847 | 61.2534 | -61.3037 | -61.496 | -0.004577 | 0.054932 | -0.041198 | 0.19226 | 0.004578 | -0.050354 | 0.054932 | 0.10529 | -0.086975 | -0.13733 | -0.31128 | -0.27008 | -0.1831 | -0.068664 | 122.6898 | 122.7859 | 61.496 | -122.6761 | 122.5937 | 122.6624 | 61.5097 | -122.818
426.6719 | 122.9187 | -61.441 | 61.235 | -0.0022127 | -0.036671 | 0.11551 | 0.026511 | 0.050092 | -0.022458 | -0.021856 | 0.0073242 | -0.0028647 | 0.041535 | 0.058785 | -0.016372 | -0.012112 | 61.2854 | -61.3312 | -0.064087 | -61.496 | 61.2396 | -61.4685 | -61.4136 | -61.8439 | -0.027466 | -61.7615 | 61.1252 | 61.2305 | -61.3403 | -61.5463 | -0.027466 | 0.027466 | 0.004578 | 0.10986 | -0.054932 | -0.082398 | 0.050354 | 0.10071 | -0.10529 | -0.10986 | -0.40283 | -0.32043 | -0.21515 | -0.004577 | 122.6807 | 122.7264 | 61.377 | -122.6486 | 122.5662 | 122.6715 | 61.4136 | -122.7814
428.3906 | 122.9233 | -61.4365 | 61.2305 | 0.0054168 | -0.03133 | 0.11167 | 0.030142 | 0.049024 | -0.024594 | -0.022924 | 0.014954 | -0.0026511 | 0.042816 | 0.059426 | -0.017867 | -0.014035 | 61.2854 | -61.322 | -0.064087 | -61.496 | 61.2488 | -61.4777 | -61.3998 | -61.8301 | -0.036621 | -61.7706 | 61.1481 | 61.2213 | -61.3358 | -61.5326 | -0.041199 | 0.036621 | 0.01831 | 0.11444 | -0.05951 | -0.096131 | 0.054931 | 0.10071 | -0.096131 | -0.082398 | -0.39368 | -0.33417 | -0.23804 | -0.009156 | 122.6852 | 122.7219 | 61.3724 | -122.6303 | 122.5845 | 122.6578 | 61.3998 | -122.7631
430.1094 | 122.8867 | -61.4136 | 61.2808 | 0.0054168 | -0.037739 | 0.11637 | 0.02822 | 0.053297 | -0.029721 | -0.025487 | 0.0073242 | -0.0037191 | 0.040039 | 0.059853 | -0.019149 | -0.01318 | 61.3541 | -61.2076 | 0.041199 | -61.4319 | 61.2076 | -61.4365 | -61.3541 | -61.7569 | 0.036621 | -61.6608 | 61.1114 | 61.2167 | -61.2854 | -61.4777 | -0.022888 | 0.059509 | -0.073242 | 0.20599 | -0.018311 | -0.07782 | 0.073242 | 0.12817 | -0.064087 | -0.16937 | -0.34332 | -0.24719 | -0.18311 | -0.064087 | 122.6212 | 122.7676 | 61.4548 | -122.6349 | 122.525 | 122.6303 | 61.4502 | -122.7585
431.875 | 122.9279 | -61.3495 | 61.3174 | 0.0054168 | -0.035389 | 0.11616 | 0.027152 | 0.051161 | -0.026517 | -0.023565 | 0.014954 | -0.0052145 | 0.043244 | 0.058785 | -0.018295 | -0.013608 | 61.4502 | -61.084 | 0.1831 | -61.3403 | 61.2717 | -61.3815 | -61.3037 | -61.6699 | 0.17395 | -61.5601 | 61.1389 | 61.2259 | -61.2442 | -61.4502 | -0.032044 | 0.045776 | -0.045777 | 0.2655 | 0.009155 | -0.036621 | 0.13275 | 0.10529 | -0.10071 | -0.17853 | -0.32043 | -0.21057 | -0.10986 | -0.091553 | 122.6212 | 122.7997 | 61.5326 | -122.6212 | 122.4884 | 122.5754 | 61.5234 | -122.7676
433.6719 | 122.8134 | -61.4319 | 61.2671 | 0.0054168 | -0.034107 | 0.11338 | 0.025229 | 0.052015 | -0.01904 | -0.023565 | 0.014954 | -0.00030125 | 0.04068 | 0.060921 | -0.012954 | -0.01553 | 61.3815 | -61.2213 | 0.050354 | -61.4502 | 61.2488 | -61.4548 | -61.3815 | -61.7844 | 0.041199 | -61.7569 | 61.1481 | 61.2122 | -61.322 | -61.5326 | -0.022888 | 0.050354 | -0.018311 | 0.21057 | -0.01831 | -0.068664 | 0.11444 | 0.10986 | -0.10071 | -0.11902 | -0.35248 | -0.32501 | -0.2243 | -0.054932 | 122.6807 | 122.8134 | 61.4822 | -122.6486 | 122.58 | 122.644 | 61.4731 | -122.7997
435.3906 | 122.9553 | -61.4273 | 61.1984 | -0.0098417 | -0.038807 | 0.11551 | 0.025015 | 0.051588 | -0.023526 | -0.022924 | 0.014954 | -0.0024375 | 0.041535 | 0.061776 | -0.014022 | -0.015103 | 61.3312 | -61.2259 | 0.022888 | -61.4502 | 61.2076 | -61.4868 | -61.3861 | -61.734 | 0.059509 | -61.6653 | 61.0794 | 61.1435 | -61.3037 | -61.496 | -0.059509 | 0.041199 | 0.009156 | 0.20142 | -0.022888 | -0.064087 | 0.13275 | 0.1236 | -0.068665 | -0.11902 | -0.3067 | -0.23804 | -0.16937 | -0.054931 | 122.6349 | 122.7585 | 61.4502 | -122.5845 | 122.5067 | 122.5708 | 61.4868 | -122.6944
437.1719 | 122.8134 | -61.441 | 61.2534 | -0.0022127 | -0.034748 | 0.11487 | 0.025443 | 0.053083 | -0.020963 | -0.022069 | 0.0073242 | -0.0022239 | 0.041107 | 0.060707 | -0.01274 | -0.014676 | 61.3678 | -61.2213 | 0.064087 | -61.4365 | 61.2671 | -61.4319 | -61.3724 | -61.7798 | 0.045776 | -61.7432 | 61.1526 | 61.2122 | -61.3129 | -61.5143 | 0.009155 | 0.068665 | 0.013733 | 0.21973 | 0.004578 | -0.064087 | 0.11444 | 0.12817 | -0.073242 | -0.10071 | -0.33874 | -0.30212 | -0.22888 | -0.041199 | 122.7081 | 122.8088 | 61.5051 | -122.6257 | 122.5937 | 122.6532 | 61.4868 | -122.7676
438.9531 | 122.8592 | -61.3861 | 61.2991 | -0.0022127 | -0.031544 | 0.11487 | 0.029288 | 0.052869 | -0.025449 | -0.023778 | 0.0073242 | -0.0041465 | 0.041107 | 0.060067 | -0.017654 | -0.013394 | 61.3586 | -61.2213 | 0.059509 | -61.4136 | 61.3174 | -61.4044 | -61.3403 | -61.7615 | 0.07782 | -61.6837 | 61.1984 | 61.29 | -61.2534 | -61.4731 | -0.018311 | 0.045776 | 0.018311 | 0.16479 | -0.027466 | -0.073242 | 0.05951 | 0.13275 | -0.086975 | -0.10071 | -0.37537 | -0.29755 | -0.21057 | -0.009155 | 122.7036 | 122.7448 | 61.4456 | -122.6395 | 122.5845 | 122.6761 | 61.4639 | -122.7722
440.6719 | 122.8912 | -61.409 | 61.2717 | 0.0054168 | -0.041584 | 0.1153 | 0.026511 | 0.050306 | -0.029935 | -0.02506 | -0.0079343 | -0.0082053 | 0.04068 | 0.059639 | -0.018081 | -0.010617 | 61.3358 | -61.1893 | 0.045776 | -61.441 | 61.2259 | -61.3953 | -61.3678 | -61.7844 | 0.041199 | -61.6562 | 61.1252 | 61.1938 | -61.29 | -61.4822 | 0.013733 | 0.041199 | -0.045776 | 0.21973 | -0.032043 | -0.073242 | 0.064087 | 0.11902 | -0.073242 | -0.14648 | -0.37537 | -0.24719 | -0.17395 | -0.077819 | 122.6349 | 122.7448 | 61.4548 | -122.6395 | 122.5342 | 122.6028 | 61.4502 | -122.7539
442.375 | 122.8409 | -61.3907 | 61.3312 | 0.013046 | -0.032825 | 0.11573 | 0.02886 | 0.050092 | -0.024808 | -0.025915 | -0.0079343 | -0.0032919 | 0.044312 | 0.061348 | -0.018722 | -0.014676 | 61.3541 | -61.2122 | 0.091553 | -61.4227 | 61.3174 | -61.4044 | -61.3403 | -61.7661 | 0.059509 | -61.6837 | 61.2305 | 61.2762 | -61.2762 | -61.4502 | -0.013733 | 0.050354 | -0.013733 | 0.17853 | -0.032043 | -0.082397 | 0.022888 | 0.11444 | -0.059509 | -0.10071 | -0.37537 | -0.29297 | -0.23346 | -0.054932 | 122.7081 | 122.7448 | 61.4822 | -122.6715 | 122.6212 | 122.6669 | 61.4502 | -122.7814
444.1406 | 122.8134 | -61.3861 | 61.3495 | 0.0054168 | -0.033893 | 0.11509 | 0.02822 | 0.050306 | -0.026731 | -0.024419 | -0.0003053 | -0.0030783 | 0.041321 | 0.061562 | -0.01744 | -0.014676 | 61.3998 | -61.1526 | 0.12817 | -61.3724 | 61.2854 | -61.3953 | -61.3083 | -61.7477 | 0.086975 | -61.6608 | 61.1847 | 61.2762 | -61.2625 | -61.441 | -0.009156 | 0.077819 | -0.064087 | 0.23346 | 0.013733 | -0.064086 | 0.050354 | 0.1236 | -0.054932 | -0.1648 | -0.36163 | -0.27466 | -0.21973 | -0.073242 | 122.6715 | 122.7859 | 61.5143 | -122.6578 | 122.5708 | 122.6624 | 61.4731 | -122.7905
445.9062 | 122.9279 | -61.3174 | 61.2991 | -0.0022127 | -0.037311 | 0.11658 | 0.02822 | 0.052869 | -0.027799 | -0.025701 | -0.0003053 | -0.0071371 | 0.039612 | 0.058785 | -0.017227 | -0.014889 | 61.4365 | -61.0519 | 0.19684 | -61.3358 | 61.2762 | -61.3953 | -61.2991 | -61.6562 | 0.16022 | -61.5555 | 61.1664 | 61.2167 | -61.2259 | -61.4365 | -0.07782 | 0.018311 | -0.022888 | 0.2655 | -0.01831 | -0.036621 | 0.13733 | 0.091553 | -0.11902 | -0.13275 | -0.33874 | -0.23804 | -0.11902 | -0.082397 | 122.5937 | 122.7539 | 61.5143 | -122.5983 | 122.4838 | 122.5342 | 61.4777 | -122.7356
447.6719 | 122.9416 | -61.3358 | 61.2762 | 0.0054168 | -0.039448 | 0.11445 | 0.027365 | 0.049665 | -0.027158 | -0.026983 | 0.0073242 | -0.0056419 | 0.041107 | 0.059853 | -0.020004 | -0.015958 | 61.3403 | -61.1984 | 0.027466 | -61.4273 | 61.2671 | -61.4044 | -61.3541 | -61.7523 | 0.041199 | -61.6333 | 61.1343 | 61.2122 | -61.2579 | -61.4914 | -0.068665 | -0.018311 | -0.009155 | 0.13733 | -0.091553 | -0.073242 | 0.064087 | 0.077819 | -0.15564 | -0.14191 | -0.41656 | -0.29755 | -0.14191 | -0.064087 | 122.6028 | 122.6761 | 61.3632 | -122.6303 | 122.4701 | 122.5479 | 61.377 | -122.7676
449.4531 | 122.85 | -61.3724 | 61.2991 | 0.0054168 | -0.034534 | 0.11231 | 0.024588 | 0.050947 | -0.020322 | -0.023565 | 0.0073242 | 0.00012615 | 0.041107 | 0.062203 | -0.016158 | -0.015744 | 61.3815 | -61.2076 | 0.07782 | -61.409 | 61.2762 | -61.4502 | -61.3632 | -61.7157 | 0.091553 | -61.6791 | 61.1755 | 61.2213 | -61.2625 | -61.5005 | -0.07782 | 0.009155 | -0.022888 | 0.16479 | -0.036622 | -0.045777 | 0.082398 | 0.10986 | -0.12817 | -0.1236 | -0.34332 | -0.3067 | -0.17853 | -0.07782 | 122.6486 | 122.7539 | 61.4502 | -122.6624 | 122.5479 | 122.5937 | 61.4639 | -122.7997
451.1719 | 122.8775 | -61.441 | 61.2305 | -0.0022127 | -0.037525 | 0.11295 | 0.026938 | 0.050092 | -0.020749 | -0.023778 | 0.0073242 | -8.7654e-05 | 0.040467 | 0.061989 | -0.016586 | -0.012326 | 61.2854 | -61.3083 | -0.054932 | -61.4914 | 61.2396 | -61.4731 | -61.4227 | -61.821 | -0.050354 | -61.7661 | 61.1298 | 61.2259 | -61.3037 | -61.5326 | -0.032043 | 0.018311 | 0.009155 | 0.13275 | -0.050354 | -0.068665 | 0.054931 | 0.13733 | -0.091553 | -0.10071 | -0.37994 | -0.32501 | -0.23346 | -0.004578 | 122.6807 | 122.7264 | 61.3861 | -122.6532 | 122.5708 | 122.6669 | 61.3907 | -122.7631
452.9375 | 122.937 | -61.3358 | 61.29 | -0.0098417 | -0.040943 | 0.11487 | 0.026511 | 0.051374 | -0.028012 | -0.024206 | -0.0079343 | -0.0062827 | 0.039398 | 0.057717 | -0.014022 | -0.014462 | 61.4273 | -61.0748 | 0.14648 | -61.3449 | 61.2579 | -61.3815 | -61.3083 | -61.6608 | 0.16479 | -61.5463 | 61.1526 | 61.2305 | -61.235 | -61.4365 | -0.045777 | 0.027465 | -0.032043 | 0.26093 | -0.009156 | -0.036621 | 0.13733 | 0.10071 | -0.10071 | -0.13733 | -0.32501 | -0.21057 | -0.10986 | -0.059509 | 122.5937 | 122.7631 | 61.4822 | -122.5983 | 122.4884 | 122.5662 | 61.5005 | -122.7264
454.6562 | 122.9095 | -61.3358 | 61.2854 | 0.013046 | -0.038807 | 0.11616 | 0.02886 | 0.050092 | -0.028012 | -0.024419 | -0.0003053 | -0.0058555 | 0.041748 | 0.060067 | -0.018295 | -0.011471 | 61.4456 | -61.0977 | 0.16022 | -61.3403 | 61.2717 | -61.3724 | -61.2946 | -61.6653 | 0.16022 | -61.5417 | 61.1389 | 61.1984 | -61.2259 | -61.4273 | -0.036621 | 0.041198 | -0.013733 | 0.23804 | -0.004578 | -0.045776 | 0.16022 | 0.10986 | -0.091553 | -0.14648 | -0.32959 | -0.20599 | -0.11444 | -0.086975 | 122.6074 | 122.7814 | 61.496 | -122.58 | 122.4747 | 122.5342 | 61.496 | -122.7127
456.3594 | 122.9187 | -61.3358 | 61.3037 | 0.0054168 | -0.03838 | 0.11551 | 0.029715 | 0.052229 | -0.026303 | -0.023992 | 0.014954 | -0.0071371 | 0.04068 | 0.058358 | -0.018508 | -0.014035 | 61.4502 | -61.0611 | 0.16937 | -61.3266 | 61.2534 | -61.3586 | -61.2625 | -61.6562 | 0.16479 | -61.5417 | 61.1572 | 61.203 | -61.2396 | -61.4548 | -0.022889 | 0.073242 | -0.050354 | 0.27466 | 0.009155 | -0.064087 | 0.14648 | 0.09613 | -0.11902 | -0.14648 | -0.32043 | -0.20599 | -0.086975 | -0.10071 | 122.5891 | 122.7859 | 61.5051 | -122.5662 | 122.493 | 122.5388 | 61.5005 | -122.7585
458.125 | 122.8088 | -61.3724 | 61.3174 | -0.0022127 | -0.033893 | 0.11316 | 0.02822 | 0.055219 | -0.024808 | -0.025915 | -0.0003053 | -0.0062827 | 0.042176 | 0.060494 | -0.017867 | -0.014035 | 61.4319 | -61.0977 | 0.16937 | -61.3449 | 61.2488 | -61.377 | -61.3174 | -61.6745 | 0.16479 | -61.5738 | 61.1755 | 61.1938 | -61.2625 | -61.4365 | -0.004578 | 0.054931 | -0.068665 | 0.27466 | 0.027465 | -0.027466 | 0.11444 | 0.10986 | -0.064087 | -0.14191 | -0.30213 | -0.20142 | -0.13733 | -0.1236 | 122.6212 | 122.8043 | 61.5417 | -122.6349 | 122.5479 | 122.5662 | 61.5372 | -122.7539
459.8281 | 122.8088 | -61.3632 | 61.322 | -0.0098417 | -0.036457 | 0.11637 | 0.029929 | 0.052869 | -0.023099 | -0.024633 | 0.014954 | -0.0043601 | 0.040894 | 0.061135 | -0.017227 | -0.016385 | 61.4365 | -61.0886 | 0.17395 | -61.3266 | 61.2671 | -61.3953 | -61.3037 | -61.6928 | 0.13275 | -61.6104 | 61.1938 | 61.2488 | -61.235 | -61.4365 | -0.032044 | 0.059509 | -0.054931 | 0.27466 | 0.036621 | -0.022888 | 0.11444 | 0.12817 | -0.073242 | -0.12817 | -0.32959 | -0.24719 | -0.17395 | -0.073242 | 122.6303 | 122.7997 | 61.5372 | -122.6257 | 122.5571 | 122.612 | 61.496 | -122.7585
461.5938 | 122.9141 | -61.3541 | 61.2808 | 0.0054168 | -0.037098 | 0.11616 | 0.02822 | 0.052229 | -0.026517 | -0.024847 | -0.0079343 | -0.0041465 | 0.042389 | 0.058785 | -0.015945 | -0.01318 | 61.4777 | -61.0611 | 0.16479 | -61.3266 | 61.2579 | -61.377 | -61.3083 | -61.6379 | 0.19226 | -61.5326 | 61.1572 | 61.2305 | -61.2442 | -61.441 | -0.022888 | 0.045776 | -0.022888 | 0.29297 | 0.027466 | -0.01831 | 0.19684 | 0.10986 | -0.086975 | -0.1236 | -0.28381 | -0.17853 | -0.091553 | -0.050354 | 122.612 | 122.8317 | 61.5189 | -122.5891 | 122.5113 | 122.5845 | 61.5463 | -122.7219
463.3125 | 122.8958 | -61.3724 | 61.2213 | -0.0022127 | -0.037098 | 0.11509 | 0.023947 | 0.049238 | -0.021817 | -0.023565 | 0.014954 | -0.0028647 | 0.038117 | 0.059639 | -0.012313 | -0.015103 | 61.377 | -61.1847 | 0.036621 | -61.3998 | 61.171 | -61.4639 | -61.3724 | -61.702 | 0.064087 | -61.6425 | 61.0611 | 61.1389 | -61.2946 | -61.496 | -0.091553 | 0 | -0.050354 | 0.18768 | -0.027466 | -0.027466 | 0.15564 | 0.077819 | -0.1236 | -0.16022 | -0.32959 | -0.27008 | -0.14648 | -0.082397 | 122.5433 | 122.7493 | 61.409 | -122.5937 | 122.4335 | 122.5113 | 61.4365 | -122.7173
465.0938 | 122.7997 | -61.3632 | 61.3037 | -0.0022127 | -0.040729 | 0.11616 | 0.02587 | 0.052656 | -0.023953 | -0.025274 | 0.0073242 | -0.0054281 | 0.041107 | 0.058571 | -0.01744 | -0.014676 | 61.441 | -61.0794 | 0.17395 | -61.3266 | 61.2625 | -61.377 | -61.3037 | -61.6562 | 0.17395 | -61.5921 | 61.1755 | 61.2213 | -61.2305 | -61.4182 | -0.013733 | 0.059509 | -0.041199 | 0.28381 | 0.036621 | -0.022888 | 0.13733 | 0.13275 | -0.054932 | -0.12817 | -0.29297 | -0.22888 | -0.17395 | -0.082398 | 122.6257 | 122.8043 | 61.5372 | -122.6074 | 122.5388 | 122.5845 | 61.5372 | -122.7219
466.7969 | 122.9187 | -61.3953 | 61.2167 | -0.0022127 | -0.036671 | 0.11316 | 0.02352 | 0.052656 | -0.023313 | -0.02036 | 0.0073242 | -0.0013693 | 0.038544 | 0.058358 | -0.011245 | -0.015744 | 61.3632 | -61.1801 | 0.041199 | -61.3953 | 61.1801 | -61.4502 | -61.3724 | -61.7157 | 0.054932 | -61.6425 | 61.0657 | 61.1252 | -61.3312 | -61.5143 | -0.054931 | 0.022889 | -0.036621 | 0.21515 | 0 | -0.022889 | 0.14648 | 0.064087 | -0.11902 | -0.15106 | -0.32043 | -0.24719 | -0.12817 | -0.091553 | 122.5754 | 122.7585 | 61.4365 | -122.5891 | 122.4609 | 122.5204 | 61.4502 | -122.731
468.5625 | 122.8317 | -61.3678 | 61.2991 | -0.0098417 | -0.03368 | 0.1153 | 0.030783 | 0.052869 | -0.022458 | -0.022069 | 0.0073242 | 0.00055335 | 0.042816 | 0.057503 | -0.016799 | -0.014035 | 61.3586 | -61.2122 | 0.068665 | -61.4044 | 61.3037 | -61.4044 | -61.3312 | -61.7569 | 0.054932 | -61.6837 | 61.203 | 61.2488 | -61.2625 | -61.4548 | -0.036621 | 0.036621 | 0.004578 | 0.15564 | -0.036621 | -0.073242 | 0.05951 | 0.10529 | -0.086975 | -0.09613 | -0.3891 | -0.31586 | -0.22888 | -0.050354 | 122.6715 | 122.7264 | 61.4365 | -122.6303 | 122.5708 | 122.6166 | 61.4227 | -122.7539
470.2812 | 122.8592 | -61.4136 | 61.2946 | 0.0054168 | -0.033039 | 0.11402 | 0.028647 | 0.051801 | -0.022458 | -0.021856 | -0.0003053 | -0.00030125 | 0.045166 | 0.06028 | -0.015304 | -0.015744 | 61.3403 | -61.1984 | 0.064087 | -61.409 | 61.3174 | -61.3998 | -61.3495 | -61.7477 | 0.09613 | -61.6562 | 61.2167 | 61.2625 | -61.2762 | -61.4822 | 0.013733 | 0.064087 | 0.022888 | 0.21515 | 0.004577 | -0.05951 | 0.045776 | 0.13733 | -0.068665 | -0.07782 | -0.33417 | -0.24262 | -0.17395 | -0.032044 | 122.731 | 122.7539 | 61.4777 | -122.644 | 122.6303 | 122.6761 | 61.5097 | -122.7768
472.0469 | 122.905 | -61.3495 | 61.2534 | 0.0054168 | -0.040943 | 0.11616 | 0.027365 | 0.05052 | -0.02844 | -0.024419 | 0.0073242 | -0.0064963 | 0.040253 | 0.058785 | -0.017654 | -0.0093353 | 61.3266 | -61.1847 | 0.032043 | -61.4044 | 61.2122 | -61.4044 | -61.3541 | -61.7569 | 0.032043 | -61.6425 | 61.1298 | 61.1938 | -61.2671 | -61.4548 | -0.054932 | -0.004578 | -0.041199 | 0.1648 | -0.054932 | -0.050354 | 0.073242 | 0.082397 | -0.10529 | -0.1236 | -0.40741 | -0.29297 | -0.18768 | -0.059509 | 122.5616 | 122.6761 | 61.3815 | -122.6074 | 122.4792 | 122.5433 | 61.3815 | -122.7081
473.8281 | 122.7905 | -61.3953 | 61.3358 | 0.0054168 | -0.035389 | 0.11402 | 0.028006 | 0.054365 | -0.024594 | -0.02506 | 0.0073242 | -0.0047873 | 0.041748 | 0.058785 | -0.016372 | -0.014035 | 61.3678 | -61.1618 | 0.10529 | -61.3998 | 61.2991 | -61.409 | -61.3174 | -61.7477 | 0.082397 | -61.6425 | 61.1984 | 61.2671 | -61.2534 | -61.4319 | -0.013733 | 0.07782 | -0.036621 | 0.23346 | -0.004577 | -0.082397 | 0.032044 | 0.14191 | -0.036621 | -0.13733 | -0.35248 | -0.24719 | -0.21057 | -0.068664 | 122.6944 | 122.7631 | 61.5005 | -122.6532 | 122.5937 | 122.6624 | 61.4777 | -122.7676
475.625 | 122.9233 | -61.322 | 61.2442 | 0.013046 | -0.035816 | 0.11466 | 0.02886 | 0.053724 | -0.028226 | -0.02506 | 0.0073242 | -0.0039329 | 0.041321 | 0.059212 | -0.016586 | -0.012326 | 61.3541 | -61.1206 | 0.091553 | -61.3632 | 61.2122 | -61.4044 | -61.3037 | -61.6974 | 0.10986 | -61.5555 | 61.116 | 61.1801 | -61.2488 | -61.4685 | -0.082398 | 0.01831 | -0.032044 | 0.20142 | -0.041199 | -0.059509 | 0.10986 | 0.073242 | -0.14648 | -0.12817 | -0.37537 | -0.23346 | -0.086975 | -0.064087 | 122.5342 | 122.6761 | 61.4136 | -122.5479 | 122.438 | 122.5021 | 61.4319 | -122.7127
477.4062 | 122.8638 | -61.3724 | 61.235 | 0.0054168 | -0.038807 | 0.11573 | 0.023947 | 0.052015 | -0.024808 | -0.023351 | -0.0003053 | -0.0032919 | 0.04068 | 0.06028 | -0.015945 | -0.014889 | 61.3632 | -61.1343 | 0.050354 | -61.409 | 61.171 | -61.441 | -61.3403 | -61.7203 | 0.050354 | -61.6241 | 61.084 | 61.1252 | -61.2854 | -61.4868 | -0.068665 | 0.032043 | -0.064087 | 0.23804 | -0.036622 | -0.068665 | 0.12817 | 0.086975 | -0.11444 | -0.15106 | -0.3479 | -0.25177 | -0.13733 | -0.10986 | 122.5433 | 122.7356 | 61.4227 | -122.5754 | 122.4564 | 122.4976 | 61.4227 | -122.7219
479.125 | 122.7631 | -61.4456 | 61.2579 | 0.0054168 | -0.034534 | 0.11295 | 0.026083 | 0.051801 | -0.016904 | -0.02036 | 0.014954 | -0.0022239 | 0.04068 | 0.061135 | -0.014022 | -0.01318 | 61.3266 | -61.2122 | 0.022888 | -61.4548 | 61.2579 | -61.441 | -61.377 | -61.7844 | 0.013733 | -61.7523 | 61.1069 | 61.1664 | -61.3037 | -61.528 | 0.004578 | 0.068665 | 0 | 0.23346 | -0.009155 | -0.07782 | 0.068664 | 0.14191 | -0.082397 | -0.15106 | -0.33874 | -0.3067 | -0.2243 | -0.091553 | 122.7036 | 122.7722 | 61.4685 | -122.6349 | 122.5525 | 122.612 | 61.4594 | -122.786
480.875 | 122.8592 | -61.3998 | 61.2442 | 0.0054168 | -0.039448 | 0.11573 | 0.02352 | 0.049665 | -0.028653 | -0.023138 | -0.0003053 | -0.0069235 | 0.039185 | 0.059639 | -0.01509 | -0.013394 | 61.3449 | -61.1481 | 0.050354 | -61.409 | 61.1664 | -61.4365 | -61.3495 | -61.7523 | 0.045776 | -61.647 | 61.0703 | 61.1252 | -61.2671 | -61.4731 | -0.036621 | 0.050354 | -0.07782 | 0.25177 | -0.009156 | -0.05951 | 0.10071 | 0.13275 | -0.073242 | -0.17395 | -0.35248 | -0.24719 | -0.17395 | -0.11902 | 122.5662 | 122.7448 | 61.4502 | -122.5937 | 122.4701 | 122.525 | 61.4456 | -122.7173
482.5938 | 122.8775 | -61.3724 | 61.2671 | 0.0054168 | -0.040089 | 0.11701 | 0.026938 | 0.052656 | -0.026731 | -0.023992 | 0.0073242 | -0.0047873 | 0.039398 | 0.058571 | -0.015731 | -0.010617 | 61.3266 | -61.1435 | 0.027466 | -61.4182 | 61.1938 | -61.4227 | -61.3403 | -61.7432 | 0.032043 | -61.647 | 61.1206 | 61.1572 | -61.2671 | -61.4594 | -0.050354 | 0.032043 | -0.073242 | 0.22888 | -0.045777 | -0.07782 | 0.059509 | 0.10528 | -0.086976 | -0.14649 | -0.37079 | -0.27466 | -0.18768 | -0.10986 | 122.5662 | 122.699 | 61.3998 | -122.6074 | 122.493 | 122.5296 | 61.4044 | -122.7264
484.3125 | 122.7951 | -61.4136 | 61.2396 | 0.013046 | -0.034321 | 0.11423 | 0.027152 | 0.05351 | -0.019681 | -0.021642 | 0.0073242 | -8.7654e-05 | 0.041748 | 0.061776 | -0.016372 | -0.013608 | 61.3586 | -61.1801 | 0.091553 | -61.4044 | 61.2579 | -61.4182 | -61.3312 | -61.7203 | 0.10986 | -61.6653 | 61.1526 | 61.1893 | -61.2625 | -61.4548 | -0.004578 | 0.082397 | 0.018311 | 0.23346 | 0.009155 | -0.073242 | 0.11902 | 0.15106 | -0.041199 | -0.086975 | -0.3067 | -0.25177 | -0.21057 | -0.050354 | 122.6715 | 122.7722 | 61.5051 | -122.5708 | 122.5662 | 122.6028 | 61.5234 | -122.6944
486.0938 | 122.8088 | -61.3541 | 61.322 | -0.0022127 | -0.037739 | 0.11722 | 0.026511 | 0.049879 | -0.026517 | -0.023565 | -0.0003053 | -0.0071371 | 0.040894 | 0.058999 | -0.016586 | -0.011899 | 61.409 | -61.0428 | 0.18768 | -61.3266 | 61.2396 | -61.3861 | -61.29 | -61.6516 | 0.16479 | -61.5555 | 61.1526 | 61.203 | -61.2122 | -61.4227 | -0.032043 | 0.064087 | -0.082397 | 0.31128 | 0.027466 | -0.036621 | 0.086976 | 0.14191 | -0.068664 | -0.16937 | -0.29755 | -0.20142 | -0.13275 | -0.11902 | 122.5937 | 122.7631 | 61.5417 | -122.612 | 122.5067 | 122.5571 | 61.5189 | -122.7447
487.8594 | 122.7676 | -61.3403 | 61.2991 | -0.0022127 | -0.034962 | 0.11658 | 0.029715 | 0.053938 | -0.027158 | -0.024206 | -0.0003053 | -0.0039329 | 0.039398 | 0.059212 | -0.015945 | -0.012326 | 61.4136 | -61.0565 | 0.1831 | -61.3266 | 61.2442 | -61.3724 | -61.2762 | -61.647 | 0.1831 | -61.5555 | 61.1526 | 61.1755 | -61.2122 | -61.4182 | -0.032043 | 0.064087 | -0.054931 | 0.28381 | 0.013733 | -0.050354 | 0.11444 | 0.12817 | -0.07782 | -0.14648 | -0.3067 | -0.21515 | -0.13733 | -0.1236 | 122.5845 | 122.7539 | 61.5234 | -122.5754 | 122.493 | 122.5159 | 61.5234 | -122.7173
489.5781 | 122.9141 | -61.3312 | 61.2671 | 0.0054168 | -0.039234 | 0.1168 | 0.028433 | 0.053083 | -0.027799 | -0.024847 | 0.0073242 | -0.0030783 | 0.040039 | 0.058999 | -0.016799 | -0.013821 | 61.3266 | -61.1526 | 0.059509 | -61.3861 | 61.2396 | -61.3953 | -61.3174 | -61.7065 | 0.082397 | -61.5921 | 61.1526 | 61.2076 | -61.2305 | -61.4594 | -0.064087 | 0.013733 | -0.027466 | 0.17853 | -0.054931 | -0.068664 | 0.059509 | 0.10071 | -0.12817 | -0.11444 | -0.37537 | -0.26093 | -0.13275 | -0.059509 | 122.5708 | 122.6578 | 61.3907 | -122.5845 | 122.4838 | 122.5388 | 61.4136 | -122.7264
491.2969 | 122.8271 | -61.3632 | 61.2854 | -0.0022127 | -0.036671 | 0.11445 | 0.026938 | 0.055433 | -0.020322 | -0.022497 | 0.014954 | -0.0011557 | 0.039612 | 0.061135 | -0.013595 | -0.014889 | 61.377 | -61.1893 | 0.073242 | -61.3632 | 61.2854 | -61.3907 | -61.322 | -61.7203 | 0.086975 | -61.6562 | 61.171 | 61.2259 | -61.2762 | -61.4548 | -0.027466 | 0.041199 | 0 | 0.17395 | 0 | -0.041199 | 0.091553 | 0.086975 | -0.091553 | -0.11444 | -0.35706 | -0.29297 | -0.20142 | -0.059509 | 122.6486 | 122.7402 | 61.4365 | -122.6074 | 122.5342 | 122.5891 | 61.4502 | -122.7402
493.0625 | 122.7631 | -61.4136 | 61.2762 | -0.0022127 | -0.029835 | 0.11551 | 0.027792 | 0.05052 | -0.021176 | -0.021001 | 0.0073242 | 0.00098055 | 0.043244 | 0.058358 | -0.014449 | -0.013394 | 61.3541 | -61.1984 | 0.059509 | -61.4182 | 61.2396 | -61.4227 | -61.3449 | -61.7615 | 0.018311 | -61.7432 | 61.1206 | 61.1847 | -61.2854 | -61.528 | -0.009155 | 0.068664 | -0.036621 | 0.21515 | -0.004578 | -0.073242 | 0.07782 | 0.12817 | -0.11444 | -0.15564 | -0.3479 | -0.32959 | -0.21515 | -0.091553 | 122.6532 | 122.7676 | 61.4731 | -122.6212 | 122.5342 | 122.5983 | 61.4319 | -122.8043
494.8594 | 122.8958 | -61.3403 | 61.2671 | -0.0022127 | -0.038807 | 0.11722 | 0.028006 | 0.048597 | -0.030362 | -0.02271 | -0.0003053 | -0.0060691 | 0.041321 | 0.058571 | -0.018936 | -0.011899 | 61.322 | -61.1755 | 0.041199 | -61.4044 | 61.203 | -61.4044 | -61.322 | -61.7432 | 0.027466 | -61.6333 | 61.1206 | 61.2259 | -61.2534 | -61.4548 | -0.064087 | 0.018311 | -0.064087 | 0.16479 | -0.064087 | -0.082398 | 0.054931 | 0.086975 | -0.11444 | -0.14649 | -0.40283 | -0.29297 | -0.17853 | -0.041199 | 122.5433 | 122.6624 | 61.3815 | -122.5891 | 122.4609 | 122.5662 | 61.3678 | -122.7219
496.6406 | 122.7905 | -61.4136 | 61.2671 | -0.0022127 | -0.034534 | 0.11316 | 0.02886 | 0.049452 | -0.019681 | -0.022069 | 0.0073242 | -0.0011557 | 0.041962 | 0.060921 | -0.016158 | -0.013821 | 61.377 | -61.1618 | 0.086975 | -61.3953 | 61.2579 | -61.4182 | -61.3403 | -61.7111 | 0.10986 | -61.6562 | 61.1481 | 61.1801 | -61.2808 | -61.4685 | -0.004578 | 0.073242 | -0.009155 | 0.25177 | 0.01831 | -0.054932 | 0.10986 | 0.13275 | -0.054932 | -0.11902 | -0.29755 | -0.24262 | -0.18768 | -0.086975 | 122.6715 | 122.7905 | 61.5005 | -122.6074 | 122.5616 | 122.5937 | 61.5234 | -122.7356
498.3438 | 122.9141 | -61.3266 | 61.2625 | 0.0054168 | -0.037952 | 0.11765 | 0.026938 | 0.051588 | -0.029294 | -0.023778 | 0.014954 | -0.0064963 | 0.039612 | 0.058999 | -0.018295 | -0.012112 | 61.3174 | -61.1526 | 0.041199 | -61.3907 | 61.1984 | -61.3861 | -61.2991 | -61.7111 | 0.064087 | -61.6013 | 61.116 | 61.1847 | -61.2305 | -61.441 | -0.059509 | 0.027466 | -0.064087 | 0.17395 | -0.064087 | -0.091553 | 0.054932 | 0.09613 | -0.11444 | -0.14648 | -0.38452 | -0.27466 | -0.16022 | -0.07782 | 122.525 | 122.644 | 61.3678 | -122.5616 | 122.4426 | 122.5113 | 61.3907 | -122.7036
500.125 | 122.8912 | -61.377 | 61.1893 | 0.013046 | -0.032825 | 0.11274 | 0.025015 | 0.051588 | -0.021176 | -0.024206 | 0.0073242 | -8.7654e-05 | 0.04303 | 0.061989 | -0.015945 | -0.013608 | 61.3037 | -61.2213 | -0.009155 | -61.441 | 61.1938 | -61.441 | -61.3586 | -61.7203 | 0.041199 | -61.6745 | 61.0565 | 61.1252 | -61.3129 | -61.496 | -0.064087 | 0.01831 | 0.004578 | 0.15564 | -0.064087 | -0.082397 | 0.11444 | 0.064087 | -0.11902 | -0.13275 | -0.34332 | -0.29755 | -0.17853 | -0.064087 | 122.5708 | 122.6807 | 61.3678 | -122.5479 | 122.4335 | 122.5021 | 61.4182 | -122.6852
501.8906 | 122.7448 | -61.3998 | 61.2671 | -0.0098417 | -0.033893 | 0.11252 | 0.027152 | 0.054151 | -0.02139 | -0.021642 | 0.0073242 | -0.00094205 | 0.041962 | 0.060707 | -0.015518 | -0.012967 | 61.3724 | -61.1526 | 0.10986 | -61.377 | 61.2396 | -61.4044 | -61.3266 | -61.7157 | 0.082397 | -61.6791 | 61.1526 | 61.203 | -61.2762 | -61.4777 | -0.004578 | 0.073242 | -0.027466 | 0.24719 | 0.022888 | -0.050354 | 0.10528 | 0.1236 | -0.07782 | -0.11444 | -0.31586 | -0.27924 | -0.20142 | -0.064087 | 122.6395 | 122.7722 | 61.5097 | -122.5937 | 122.5525 | 122.6028 | 61.4822 | -122.7448
503.6719 | 122.7951 | -61.3678 | 61.2717 | 0.0054168 | -0.032612 | 0.11402 | 0.026511 | 0.052229 | -0.022672 | -0.024419 | -0.0003053 | -0.0022239 | 0.041107 | 0.061989 | -0.015304 | -0.014035 | 61.3449 | -61.1526 | 0.07782 | -61.3815 | 61.2534 | -61.4044 | -61.3312 | -61.7111 | 0.10986 | -61.647 | 61.1343 | 61.2213 | -61.2762 | -61.4685 | -0.036621 | 0.036621 | -0.01831 | 0.21515 | -0.013733 | -0.050354 | 0.073243 | 0.091553 | -0.10071 | -0.13733 | -0.34332 | -0.27924 | -0.17853 | -0.050354 | 122.6212 | 122.7127 | 61.4456 | -122.6028 | 122.5021 | 122.5891 | 61.4777 | -122.7402
505.3906 | 122.8088 | -61.3449 | 61.2762 | -0.0022127 | -0.03838 | 0.11637 | 0.028433 | 0.052869 | -0.028653 | -0.024847 | 0.0073242 | -0.0058555 | 0.040894 | 0.058999 | -0.01744 | -0.012967 | 61.3953 | -61.0428 | 0.17853 | -61.3129 | 61.2442 | -61.3724 | -61.2671 | -61.647 | 0.1831 | -61.5372 | 61.1206 | 61.1893 | -61.2305 | -61.4182 | -0.027465 | 0.07782 | -0.032043 | 0.30212 | 0.032044 | -0.045776 | 0.11902 | 0.11444 | -0.073242 | -0.15564 | -0.30212 | -0.19226 | -0.11902 | -0.086975 | 122.5891 | 122.7402 | 61.5234 | -122.5433 | 122.4655 | 122.5342 | 61.528 | -122.6944
507.1094 | 122.8226 | -61.3724 | 61.2854 | -0.0098417 | -0.033253 | 0.11551 | 0.029501 | 0.052869 | -0.024167 | -0.02506 | 0.0073242 | -0.0022239 | 0.04303 | 0.059426 | -0.015945 | -0.012967 | 61.3129 | -61.1893 | 0.07782 | -61.377 | 61.29 | -61.3632 | -61.3266 | -61.7386 | 0.068665 | -61.6516 | 61.1984 | 61.2625 | -61.2488 | -61.441 | 0.009155 | 0.045776 | 0.004578 | 0.1831 | -0.004578 | -0.050354 | 0.027466 | 0.1236 | -0.068665 | -0.086975 | -0.36621 | -0.27924 | -0.21057 | -0.022888 | 122.6624 | 122.6852 | 61.4502 | -122.612 | 122.5708 | 122.6349 | 61.441 | -122.7264
508.8906 | 122.7722 | -61.3403 | 61.3083 | 0.0054168 | -0.036671 | 0.11637 | 0.027152 | 0.051161 | -0.029294 | -0.022283 | 0.0073242 | -0.0047873 | 0.04303 | 0.059853 | -0.018295 | -0.01318 | 61.409 | -61.0611 | 0.16937 | -61.3083 | 61.2259 | -61.3495 | -61.2762 | -61.6608 | 0.16937 | -61.5417 | 61.1298 | 61.2122 | -61.1984 | -61.409 | -0.009155 | 0.064087 | -0.082398 | 0.27924 | 0.032043 | -0.032044 | 0.10071 | 0.14191 | -0.068665 | -0.17853 | -0.32044 | -0.20142 | -0.13275 | -0.096131 | 122.5662 | 122.7493 | 61.5097 | -122.5845 | 122.4701 | 122.5525 | 61.5097 | -122.7173
510.6875 | 122.8592 | -61.3678 | 61.2213 | -0.0022127 | -0.03603 | 0.11551 | 0.023947 | 0.050947 | -0.024381 | -0.023565 | -0.0079343 | -0.0035055 | 0.041748 | 0.060707 | -0.015304 | -0.013608 | 61.3541 | -61.1664 | 0.041199 | -61.3861 | 61.1572 | -61.4227 | -61.3632 | -61.6974 | 0.050354 | -61.6287 | 61.0428 | 61.1206 | -61.2946 | -61.4868 | -0.054931 | 0.004578 | -0.064086 | 0.20142 | -0.01831 | -0.022888 | 0.13275 | 0.073242 | -0.11902 | -0.17853 | -0.32959 | -0.26093 | -0.14191 | -0.10071 | 122.525 | 122.7219 | 61.409 | -122.5845 | 122.4106 | 122.4884 | 61.4182 | -122.7081
512.4688 | 122.7585 | -61.3632 | 61.3266 | -0.0022127 | -0.036884 | 0.11551 | 0.029074 | 0.052442 | -0.026517 | -0.024206 | 0.0073242 | -0.0041465 | 0.041321 | 0.060921 | -0.018508 | -0.013394 | 61.409 | -61.0794 | 0.16937 | -61.3083 | 61.2579 | -61.3403 | -61.2808 | -61.647 | 0.16479 | -61.5601 | 61.1526 | 61.2534 | -61.2076 | -61.4273 | 0.022888 | 0.082397 | -0.068664 | 0.28381 | 0.054931 | -0.027466 | 0.082398 | 0.15564 | -0.064087 | -0.17395 | -0.28381 | -0.19684 | -0.13275 | -0.073242 | 122.6212 | 122.7722 | 61.5326 | -122.6074 | 122.5159 | 122.6166 | 61.528 | -122.7539
514.1719 | 122.7402 | -61.4182 | 61.2442 | 0.0054168 | -0.035175 | 0.11423 | 0.024161 | 0.052869 | -0.020963 | -0.024847 | 0.0073242 | -0.00030125 | 0.040894 | 0.061989 | -0.012954 | -0.013608 | 61.3449 | -61.203 | 0.045776 | -61.3953 | 61.2488 | -61.3953 | -61.3083 | -61.7569 | 0.013733 | -61.7157 | 61.1252 | 61.1938 | -61.3129 | -61.496 | 0.022888 | 0.10986 | 0.004577 | 0.21515 | 0.022888 | -0.086975 | 0.10071 | 0.10529 | -0.07782 | -0.11902 | -0.33875 | -0.29755 | -0.21973 | -0.050354 | 122.6669 | 122.7631 | 61.4639 | -122.5525 | 122.5433 | 122.612 | 61.4319 | -122.7402
515.9375 | 122.7859 | -61.3678 | 61.2488 | -0.0098417 | -0.030048 | 0.11316 | 0.031851 | 0.053724 | -0.022244 | -0.021429 | 0.0073242 | -0.0017965 | 0.044739 | 0.062203 | -0.016586 | -0.013394 | 61.3358 | -61.1618 | 0.091553 | -61.3998 | 61.2534 | -61.4044 | -61.3266 | -61.6974 | 0.11902 | -61.6425 | 61.1618 | 61.2076 | -61.2305 | -61.4777 | -0.036621 | 0.041199 | 0.004578 | 0.20599 | -0.032043 | -0.073242 | 0.086975 | 0.13733 | -0.10986 | -0.086975 | -0.32959 | -0.27466 | -0.1648 | -0.041198 | 122.6212 | 122.7036 | 61.4594 | -122.5754 | 122.5296 | 122.5754 | 61.4868 | -122.7264
517.6875 | 122.7631 | -61.409 | 61.2579 | -0.0098417 | -0.03368 | 0.11509 | 0.025015 | 0.053724 | -0.021176 | -0.021001 | -0.0003053 | -0.0026511 | 0.040253 | 0.061135 | -0.014236 | -0.012112 | 61.3586 | -61.1572 | 0.10529 | -61.3953 | 61.2259 | -61.3953 | -61.3495 | -61.702 | 0.11444 | -61.6516 | 61.1481 | 61.203 | -61.235 | -61.4639 | 0.013733 | 0.05951 | -0.032044 | 0.25177 | 0.013733 | -0.045777 | 0.10071 | 0.17395 | -0.054931 | -0.10986 | -0.29297 | -0.24261 | -0.18768 | -0.054932 | 122.6349 | 122.7676 | 61.5143 | -122.6074 | 122.5571 | 122.612 | 61.5234 | -122.7219
519.4688 | 122.8775 | -61.3907 | 61.1572 | -0.0022127 | -0.036243 | 0.11252 | 0.026938 | 0.053083 | -0.025022 | -0.021856 | 0.0073242 | -0.0028647 | 0.041535 | 0.061135 | -0.017013 | -0.012326 | 61.2442 | -61.2442 | -0.036621 | -61.4502 | 61.1755 | -61.4685 | -61.3678 | -61.7569 | 0.022888 | -61.6745 | 61.0428 | 61.1572 | -61.2991 | -61.4731 | -0.07782 | 0.022888 | 0.01831 | 0.14648 | -0.059509 | -0.082397 | 0.086975 | 0.091553 | -0.082397 | -0.11444 | -0.36621 | -0.28381 | -0.20142 | 0 | 122.5662 | 122.6349 | 61.3541 | -122.525 | 122.4335 | 122.5479 | 61.4136 | -122.6303
521.1875 | 122.7951 | -61.3815 | 61.2488 | -0.0022127 | -0.034321 | 0.11381 | 0.027792 | 0.050733 | -0.025235 | -0.021856 | 0.022583 | -0.00072845 | 0.041321 | 0.06028 | -0.017227 | -0.012967 | 61.3037 | -61.203 | 0.068665 | -61.377 | 61.2854 | -61.3815 | -61.3083 | -61.734 | 0.064087 | -61.647 | 61.1893 | 61.2534 | -61.2442 | -61.4365 | 0 | 0.073242 | 0.036621 | 0.17853 | 0.004578 | -0.068664 | 0.054932 | 0.13733 | -0.054931 | -0.059509 | -0.35248 | -0.2655 | -0.21057 | 0.004578 | 122.6669 | 122.6852 | 61.4502 | -122.5571 | 122.5708 | 122.6349 | 61.4456 | -122.6852
522.9531 | 122.8638 | -61.3632 | 61.1755 | 0.0054168 | -0.037525 | 0.11637 | 0.025443 | 0.052015 | -0.026517 | -0.021856 | 0.0073242 | -0.0054281 | 0.040894 | 0.061135 | -0.016158 | -0.01254 | 61.322 | -61.1526 | 0.045776 | -61.3815 | 61.1481 | -61.4227 | -61.3541 | -61.7065 | 0.064087 | -61.6333 | 61.0565 | 61.1023 | -61.29 | -61.4685 | -0.059509 | 0.009155 | -0.027466 | 0.21057 | -0.018311 | -0.027466 | 0.14648 | 0.073242 | -0.10529 | -0.11902 | -0.34332 | -0.27008 | -0.1648 | -0.073242 | 122.5113 | 122.6852 | 61.409 | -122.5296 | 122.4197 | 122.4655 | 61.4273 | -122.644
524.6719 | 122.7997 | -61.3174 | 61.2762 | 0.0054168 | -0.036243 | 0.11487 | 0.02886 | 0.052229 | -0.02844 | -0.025915 | 0.0073242 | -0.0060691 | 0.043885 | 0.059212 | -0.01979 | -0.012967 | 61.3907 | -61.0382 | 0.17853 | -61.2991 | 61.2442 | -61.3358 | -61.2396 | -61.6425 | 0.1831 | -61.5326 | 61.1298 | 61.203 | -61.1984 | -61.4044 | -0.01831 | 0.07782 | -0.032043 | 0.27924 | 0.018311 | -0.059509 | 0.11444 | 0.11902 | -0.086975 | -0.14648 | -0.32501 | -0.21515 | -0.12817 | -0.073242 | 122.5616 | 122.7081 | 61.496 | -122.5159 | 122.4472 | 122.5204 | 61.5005 | -122.6807
526.3906 | 122.8821 | -61.3861 | 61.1801 | 0.020676 | -0.035602 | 0.11423 | 0.024802 | 0.049665 | -0.022885 | -0.023565 | -0.0003053 | -0.0030783 | 0.041748 | 0.060494 | -0.014449 | -0.01254 | 61.2991 | -61.2167 | -0.004578 | -61.4227 | 61.203 | -61.4502 | -61.3541 | -61.7249 | 0.041199 | -61.6333 | 61.0474 | 61.1114 | -61.2671 | -61.4777 | -0.064087 | 0.032043 | 0.022888 | 0.16937 | -0.036621 | -0.068664 | 0.11902 | 0.11902 | -0.091553 | -0.13275 | -0.33875 | -0.24719 | -0.15564 | -0.068665 | 122.5891 | 122.6852 | 61.3815 | -122.5342 | 122.4335 | 122.4976 | 61.4273 | -122.6578
528.1719 | 122.7448 | -61.4182 | 61.2488 | 0.0054168 | -0.034534 | 0.11402 | 0.024588 | 0.050306 | -0.02139 | -0.021215 | 0.0073242 | -0.0013693 | 0.042176 | 0.06028 | -0.015304 | -0.012753 | 61.235 | -61.2717 | -0.045776 | -61.4594 | 61.2305 | -61.4456 | -61.3907 | -61.821 | -0.036621 | -61.7294 | 61.1206 | 61.1572 | -61.2991 | -61.5097 | -0.027466 | 0.027466 | -0.01831 | 0.14648 | -0.041199 | -0.068665 | -0.013733 | 0.11902 | -0.091553 | -0.12817 | -0.40283 | -0.31128 | -0.21973 | -0.091552 | 122.6486 | 122.6532 | 61.3724 | -122.6395 | 122.5388 | 122.5754 | 61.3815 | -122.7585
529.9688 | 122.8546 | -61.3678 | 61.1984 | 0.013046 | -0.038166 | 0.11445 | 0.025656 | 0.052869 | -0.024808 | -0.022924 | -0.0003053 | -0.0030783 | 0.041535 | 0.060494 | -0.015945 | -0.014249 | 61.322 | -61.1526 | 0.041199 | -61.3907 | 61.1572 | -61.4227 | -61.3174 | -61.6974 | 0.059509 | -61.6287 | 61.0428 | 61.1069 | -61.2671 | -61.4685 | -0.054931 | 0.050354 | -0.041198 | 0.21515 | -0.022888 | -0.073242 | 0.1236 | 0.10071 | -0.10071 | -0.15564 | -0.32959 | -0.26093 | -0.16022 | -0.091552 | 122.525 | 122.6898 | 61.409 | -122.5159 | 122.4106 | 122.4747 | 61.4273 | -122.6669
531.7344 | 122.8592 | -61.3586 | 61.171 | -0.0022127 | -0.035816 | 0.1153 | 0.027792 | 0.052015 | -0.024167 | -0.023351 | -0.0003053 | -0.00072845 | 0.042816 | 0.060921 | -0.016586 | -0.013394 | 61.2396 | -61.2534 | -0.050354 | -61.4548 | 61.2259 | -61.4273 | -61.3678 | -61.7798 | -0.041199 | -61.7294 | 61.0931 | 61.1572 | -61.3083 | -61.4822 | -0.068664 | -0.009155 | 0.054932 | 0.10529 | -0.09613 | -0.086975 | 0.068665 | 0.050354 | -0.1236 | -0.077819 | -0.42114 | -0.37079 | -0.24719 | -0.013732 | 122.5845 | 122.5983 | 61.3083 | -122.5388 | 122.4518 | 122.5159 | 61.3174 | -122.6532
533.4531 | 122.7264 | -61.3861 | 61.2625 | 0.013046 | -0.035602 | 0.11509 | 0.024374 | 0.053083 | -0.022885 | -0.023351 | 0.0073242 | -0.00094205 | 0.041535 | 0.058785 | -0.014022 | -0.015317 | 61.3358 | -61.1481 | 0.086975 | -61.3724 | 61.235 | -61.3953 | -61.3358 | -61.7386 | 0.082397 | -61.6562 | 61.1114 | 61.1847 | -61.2671 | -61.4731 | -0.009156 | 0.050354 | -0.027466 | 0.23804 | 0.013733 | -0.036621 | 0.073242 | 0.11902 | -0.086975 | -0.15106 | -0.35248 | -0.27008 | -0.18311 | -0.07782 | 122.6212 | 122.7219 | 61.4731 | -122.5983 | 122.4976 | 122.5708 | 61.4685 | -122.7356
535.1875 | 122.8226 | -61.3449 | 61.235 | 0.0054168 | -0.042225 | 0.11722 | 0.02822 | 0.050306 | -0.028226 | -0.024633 | 0.0073242 | -0.0067099 | 0.040039 | 0.058785 | -0.01979 | -0.011044 | 61.2991 | -61.1435 | 0.036621 | -61.3953 | 61.1389 | -61.4273 | -61.2991 | -61.734 | 0.022888 | -61.6196 | 61.0794 | 61.1572 | -61.2534 | -61.4319 | -0.082397 | 0.045777 | -0.09613 | 0.20142 | -0.050354 | -0.096131 | 0.064087 | 0.091553 | -0.086975 | -0.15564 | -0.3891 | -0.27466 | -0.18768 | -0.077819 | 122.4838 | 122.644 | 61.3815 | -122.5342 | 122.4243 | 122.5021 | 61.3678 | -122.6669
536.9375 | 122.8455 | -61.2762 | 61.2671 | 0.0054168 | -0.042225 | 0.11616 | 0.027152 | 0.052015 | -0.02844 | -0.025274 | 0.0073242 | -0.0069235 | 0.039398 | 0.058785 | -0.016372 | -0.014249 | 61.3998 | -61.0474 | 0.16022 | -61.322 | 61.2122 | -61.3358 | -61.2671 | -61.6241 | 0.16937 | -61.4868 | 61.116 | 61.2213 | -61.1893 | -61.3998 | -0.059509 | 0.009155 | -0.054932 | 0.22888 | -0.045776 | -0.054931 | 0.13275 | 0.086975 | -0.1236 | -0.15106 | -0.3479 | -0.21057 | -0.086975 | -0.045777 | 122.4884 | 122.6761 | 61.4365 | -122.5342 | 122.3923 | 122.4976 | 61.4456 | -122.6669
538.7188 | 122.8546 | -61.3815 | 61.1618 | 0.013046 | -0.037311 | 0.11402 | 0.027792 | 0.052442 | -0.022885 | -0.023992 | 0.0073242 | -0.0015829 | 0.040039 | 0.061776 | -0.014236 | -0.01553 | 61.29 | -61.2442 | -0.032043 | -61.441 | 61.1847 | -61.4273 | -61.3678 | -61.7203 | 0.018311 | -61.6562 | 61.0611 | 61.1389 | -61.2808 | -61.4639 | -0.045776 | 0.013733 | 0.022888 | 0.13733 | -0.059509 | -0.073242 | 0.12817 | 0.10071 | -0.082397 | -0.10071 | -0.33874 | -0.27466 | -0.19226 | -0.022888 | 122.5662 | 122.6715 | 61.3495 | -122.5296 | 122.4426 | 122.5204 | 61.3998 | -122.6257
540.5 | 122.8683 | -61.2854 | 61.2579 | 0.0054168 | -0.034748 | 0.11829 | 0.02886 | 0.049665 | -0.02844 | -0.026342 | 0.0073242 | -0.0052145 | 0.041962 | 0.059426 | -0.02214 | -0.014676 | 61.3907 | -61.0519 | 0.14191 | -61.3129 | 61.1893 | -61.3449 | -61.2717 | -61.6333 | 0.15564 | -61.5189 | 61.1069 | 61.1938 | -61.1938 | -61.409 | -0.05951 | 0.013733 | -0.068665 | 0.23346 | -0.027466 | -0.041199 | 0.13275 | 0.091552 | -0.1236 | -0.15106 | -0.3479 | -0.23346 | -0.10986 | -0.064087 | 122.4747 | 122.6761 | 61.4273 | -122.5296 | 122.3923 | 122.4792 | 61.441 | -122.6669
542.2188 | 122.7814 | -61.3449 | 61.2808 | -0.0022127 | -0.034962 | 0.1153 | 0.028006 | 0.05351 | -0.023526 | -0.023351 | 0.0073242 | -0.0022239 | 0.041748 | 0.058571 | -0.015304 | -0.01553 | 61.3174 | -61.1938 | 0.064087 | -61.3632 | 61.2854 | -61.3678 | -61.3037 | -61.7111 | 0.054932 | -61.6653 | 61.1755 | 61.2259 | -61.2396 | -61.4502 | -0.022888 | 0.041199 | 0.004577 | 0.15106 | -0.01831 | -0.059509 | 0.036621 | 0.10529 | -0.10529 | -0.10529 | -0.36621 | -0.32043 | -0.21515 | -0.054932 | 122.6303 | 122.6624 | 61.409 | -122.5845 | 122.5204 | 122.5708 | 61.3998 | -122.731
544 | 122.8134 | -61.3861 | 61.1847 | 0.0054168 | -0.035175 | 0.11188 | 0.025443 | 0.052229 | -0.021817 | -0.022924 | 0.0073242 | -0.0017965 | 0.040467 | 0.059426 | -0.016586 | -0.015744 | 61.2534 | -61.2717 | -0.054932 | -61.4548 | 61.2213 | -61.4456 | -61.3586 | -61.7798 | -0.045776 | -61.7249 | 61.116 | 61.1664 | -61.29 | -61.4777 | -0.05951 | 0.027465 | 0.036621 | 0.11444 | -0.068665 | -0.09613 | 0.068665 | 0.09613 | -0.091553 | -0.068664 | -0.39368 | -0.33875 | -0.24719 | -0.01831 | 122.6074 | 122.6395 | 61.3312 | -122.5433 | 122.5021 | 122.5525 | 61.3403 | -122.6624
545.7031 | 122.8409 | -61.3266 | 61.2534 | 0.013046 | -0.038166 | 0.11573 | 0.026938 | 0.052656 | -0.029294 | -0.024419 | 0.014954 | -0.0060691 | 0.041748 | 0.05729 | -0.017227 | -0.013394 | 61.3037 | -61.1481 | 0.050354 | -61.3815 | 61.1847 | -61.377 | -61.29 | -61.7294 | 0.022888 | -61.615 | 61.1023 | 61.1801 | -61.2442 | -61.4639 | -0.050354 | 0.036621 | -0.068665 | 0.17853 | -0.054932 | -0.091553 | 0.050354 | 0.082397 | -0.13733 | -0.15106 | -0.40283 | -0.28839 | -0.15106 | -0.073242 | 122.5113 | 122.6303 | 61.377 | -122.5433 | 122.4289 | 122.5067 | 61.3495 | -122.7173
547.4844 | 122.8271 | -61.3632 | 61.1984 | -0.0022127 | -0.03603 | 0.11658 | 0.024588 | 0.053297 | -0.024381 | -0.024206 | 0.0073242 | -0.0050009 | 0.042176 | 0.05793 | -0.016158 | -0.01318 | 61.3174 | -61.1435 | 0.050354 | -61.3861 | 61.1572 | -61.4273 | -61.3358 | -61.6699 | 0.064087 | -61.6058 | 61.0336 | 61.084 | -61.2579 | -61.4639 | -0.064087 | 0.027466 | -0.041198 | 0.21973 | -0.022888 | -0.050354 | 0.11902 | 0.10528 | -0.10071 | -0.16479 | -0.3067 | -0.24262 | -0.14191 | -0.11444 | 122.5204 | 122.6807 | 61.4136 | -122.5342 | 122.3969 | 122.4472 | 61.4273 | -122.6624
549.2031 | 122.85 | -61.2854 | 61.2762 | -0.0022127 | -0.034748 | 0.11744 | 0.030783 | 0.052656 | -0.031217 | -0.024419 | 0.0073242 | -0.0047873 | 0.042603 | 0.059639 | -0.019576 | -0.014676 | 61.4365 | -61.0016 | 0.16937 | -61.2808 | 61.2076 | -61.3449 | -61.2442 | -61.6196 | 0.16937 | -61.5097 | 61.1114 | 61.1755 | -61.1755 | -61.3953 | -0.05951 | 0.041198 | -0.068664 | 0.28381 | 0.004577 | -0.036621 | 0.16022 | 0.10986 | -0.10986 | -0.1648 | -0.33417 | -0.2243 | -0.11444 | -0.10071 | 122.493 | 122.7219 | 61.4548 | -122.5204 | 122.3969 | 122.4609 | 61.4548 | -122.6715
550.9844 | 122.7676 | -61.3632 | 61.2396 | -0.0022127 | -0.032184 | 0.11338 | 0.027365 | 0.055006 | -0.021176 | -0.024847 | 0.0073242 | -0.0020103 | 0.043457 | 0.059853 | -0.016799 | -0.017026 | 61.3586 | -61.1526 | 0.10529 | -61.3586 | 61.2625 | -61.4044 | -61.3037 | -61.6745 | 0.11444 | -61.6241 | 61.1114 | 61.1893 | -61.235 | -61.4594 | -0.041199 | 0.059509 | 0.022888 | 0.21057 | 0.004577 | -0.054932 | 0.11902 | 0.12817 | -0.096131 | -0.12817 | -0.31128 | -0.26093 | -0.1648 | -0.050354 | 122.6257 | 122.7219 | 61.4685 | -122.5433 | 122.4747 | 122.5525 | 61.4777 | -122.699
552.75 | 122.8409 | -61.3129 | 61.2625 | 0.013046 | -0.037098 | 0.11423 | 0.027579 | 0.048597 | -0.026731 | -0.024419 | -0.0079343 | -0.0073507 | 0.042176 | 0.058785 | -0.020217 | -0.014035 | 61.2854 | -61.1572 | 0.045776 | -61.3724 | 61.2076 | -61.3815 | -61.3037 | -61.7065 | 0.036621 | -61.6058 | 61.0794 | 61.1664 | -61.203 | -61.4136 | -0.068665 | 0.009155 | -0.054931 | 0.15564 | -0.059509 | -0.068664 | 0.022888 | 0.10986 | -0.10071 | -0.1831 | -0.39368 | -0.29297 | -0.19226 | -0.09613 | 122.5204 | 122.5983 | 61.3586 | -122.5662 | 122.3923 | 122.4792 | 61.3495 | -122.6761
554.5312 | 122.7402 | -61.3953 | 61.2076 | 0.013046 | -0.036671 | 0.11487 | 0.02587 | 0.053083 | -0.019254 | -0.021642 | -0.0003053 | 0.00012615 | 0.041535 | 0.059426 | -0.012954 | -0.012967 | 61.235 | -61.2671 | -0.022888 | -61.4365 | 61.2122 | -61.4273 | -61.3586 | -61.7844 | -0.041199 | -61.7706 | 61.1114 | 61.1481 | -61.2946 | -61.4868 | -0.032043 | 0.036621 | 0.004577 | 0.12817 | -0.041198 | -0.077819 | 0.027465 | 0.10071 | -0.091552 | -0.096131 | -0.3891 | -0.37537 | -0.28381 | -0.05951 | 122.6074 | 122.6303 | 61.3724 | -122.5662 | 122.5067 | 122.5433 | 61.3541 | -122.6944
556.25 | 122.7676 | -61.3174 | 61.2671 | 0.0054168 | -0.033466 | 0.11658 | 0.030142 | 0.051161 | -0.026303 | -0.023778 | -0.0003053 | -0.00094205 | 0.042816 | 0.058358 | -0.015518 | -0.012753 | 61.3129 | -61.1481 | 0.082397 | -61.3586 | 61.2717 | -61.3541 | -61.2579 | -61.7203 | 0.064087 | -61.647 | 61.1618 | 61.1938 | -61.235 | -61.4136 | -0.036621 | 0.059509 | 0.004577 | 0.16937 | -0.041199 | -0.10071 | 0.045776 | 0.082398 | -0.09613 | -0.10529 | -0.40283 | -0.32959 | -0.23346 | -0.073242 | 122.5891 | 122.6303 | 61.3998 | -122.525 | 122.4792 | 122.5113 | 61.3815 | -122.6807
558.0156 | 122.7585 | -61.3403 | 61.2808 | -0.0022127 | -0.03368 | 0.11487 | 0.028006 | 0.053083 | -0.025449 | -0.023138 | -0.0003053 | -0.0037191 | 0.043457 | 0.058785 | -0.017227 | -0.012753 | 61.3037 | -61.1618 | 0.086975 | -61.3586 | 61.2717 | -61.3632 | -61.29 | -61.7294 | 0.064087 | -61.6425 | 61.1526 | 61.2259 | -61.2213 | -61.409 | -0.022888 | 0.050354 | -0.009156 | 0.17853 | -0.018311 | -0.068665 | 0.022888 | 0.11902 | -0.068665 | -0.12817 | -0.3891 | -0.30212 | -0.23346 | -0.054932 | 122.612 | 122.644 | 61.4273 | -122.5708 | 122.493 | 122.5662 | 61.4044 | -122.6898
559.7812 | 122.7997 | -61.3632 | 61.1664 | 0.0054168 | -0.037311 | 0.11594 | 0.02352 | 0.053938 | -0.026944 | -0.022497 | -0.0079343 | -0.0022239 | 0.042176 | 0.060494 | -0.015304 | -0.013821 | 61.2991 | -61.1069 | 0.054932 | -61.3815 | 61.1435 | -61.4136 | -61.3129 | -61.6699 | 0.073242 | -61.5738 | 61.0107 | 61.0886 | -61.2579 | -61.4594 | -0.050354 | 0.050354 | -0.022888 | 0.25635 | -0.018311 | -0.068665 | 0.13275 | 0.10528 | -0.096131 | -0.15564 | -0.3067 | -0.21057 | -0.11444 | -0.07782 | 122.5067 | 122.6624 | 61.4182 | -122.4792 | 122.374 | 122.4518 | 61.4365 | -122.6257
561.5 | 122.7127 | -61.3907 | 61.2305 | -0.0022127 | -0.03368 | 0.11274 | 0.026297 | 0.052229 | -0.021817 | -0.023778 | -0.0003053 | 0.00012615 | 0.042816 | 0.060921 | -0.015945 | -0.014035 | 61.3358 | -61.1343 | 0.082397 | -61.3724 | 61.2396 | -61.3724 | -61.3129 | -61.702 | 0.091553 | -61.6425 | 61.1069 | 61.1618 | -61.2625 | -61.4594 | 0.018311 | 0.07782 | 0.009155 | 0.25635 | 0.018311 | -0.059509 | 0.10529 | 0.12817 | -0.068665 | -0.1236 | -0.31128 | -0.25177 | -0.18311 | -0.068665 | 122.6303 | 122.7264 | 61.4731 | -122.5433 | 122.4976 | 122.5525 | 61.4822 | -122.6898
563.2656 | 122.7127 | -61.3266 | 61.3174 | -0.0022127 | -0.035816 | 0.11509 | 0.029288 | 0.053083 | -0.028012 | -0.023992 | 0.014954 | -0.0045737 | 0.041748 | 0.056649 | -0.020004 | -0.011258 | 61.3541 | -61.0565 | 0.16022 | -61.2991 | 61.2488 | -61.3174 | -61.2534 | -61.6928 | 0.12817 | -61.5784 | 61.171 | 61.1938 | -61.203 | -61.3998 | 0.009155 | 0.073242 | -0.068665 | 0.27008 | 0.027466 | -0.045776 | 0.036621 | 0.1236 | -0.073242 | -0.14648 | -0.36621 | -0.25177 | -0.17853 | -0.1236 | 122.5754 | 122.6807 | 61.4868 | -122.5708 | 122.4976 | 122.5204 | 61.4548 | -122.7173
565.0312 | 122.8409 | -61.2991 | 61.2488 | 0.0054168 | -0.037739 | 0.11637 | 0.028647 | 0.051588 | -0.029935 | -0.026128 | 0.0073242 | -0.0071371 | 0.04068 | 0.057717 | -0.018936 | -0.014249 | 61.3586 | -61.0336 | 0.14648 | -61.3037 | 61.2167 | -61.3174 | -61.2717 | -61.6241 | 0.16479 | -61.496 | 61.0931 | 61.1435 | -61.1984 | -61.3998 | -0.018311 | 0.027466 | -0.032043 | 0.2655 | -0.004578 | -0.032044 | 0.10986 | 0.10071 | -0.10071 | -0.15564 | -0.32501 | -0.19684 | -0.096131 | -0.10529 | 122.5159 | 122.6578 | 61.4456 | -122.5204 | 122.3923 | 122.4426 | 61.4639 | -122.6486
566.7969 | 122.8363 | -61.2991 | 61.2305 | -0.0022127 | -0.037952 | 0.11637 | 0.027792 | 0.051161 | -0.028012 | -0.026128 | -0.0003053 | -0.0064963 | 0.041535 | 0.05793 | -0.018722 | -0.013821 | 61.2762 | -61.1481 | 0.045776 | -61.3541 | 61.1893 | -61.3632 | -61.2946 | -61.6882 | 0.045776 | -61.5738 | 61.0794 | 61.1664 | -61.2076 | -61.441 | -0.064087 | 0.004577 | -0.041199 | 0.15106 | -0.054932 | -0.059509 | 0.045776 | 0.091552 | -0.14191 | -0.15106 | -0.3891 | -0.27466 | -0.13275 | -0.064087 | 122.4884 | 122.5754 | 61.3449 | -122.525 | 122.3785 | 122.4655 | 61.3449 | -122.6715
568.5156 | 122.731 | -61.3495 | 61.2122 | -0.0022127 | -0.035602 | 0.11359 | 0.027579 | 0.051374 | -0.01904 | -0.023778 | -0.0003053 | 0.00076695 | 0.04068 | 0.061776 | -0.014449 | -0.016385 | 61.3403 | -61.1435 | 0.10071 | -61.3449 | 61.2259 | -61.3953 | -61.2946 | -61.6608 | 0.082397 | -61.6104 | 61.1526 | 61.1938 | -61.2122 | -61.4502 | -0.045777 | 0.054931 | 0.013733 | 0.20599 | 0.004577 | -0.050354 | 0.12817 | 0.13733 | -0.10071 | -0.059509 | -0.31128 | -0.26093 | -0.16022 | -0.01831 | 122.5754 | 122.6898 | 61.4502 | -122.5067 | 122.5021 | 122.5433 | 61.4319 | -122.6624
570.2344 | 122.85 | -61.3174 | 61.2213 | 0.0054168 | -0.037739 | 0.1168 | 0.026297 | 0.050092 | -0.027158 | -0.026342 | 0.014954 | -0.0047873 | 0.041748 | 0.059426 | -0.018722 | -0.013608 | 61.2808 | -61.1298 | 0.054932 | -61.3541 | 61.1938 | -61.3541 | -61.2808 | -61.6699 | 0.082397 | -61.5692 | 61.1023 | 61.1664 | -61.2122 | -61.3861 | -0.036621 | 0.036621 | -0.027465 | 0.18768 | -0.036621 | -0.073242 | 0.05951 | 0.10529 | -0.068664 | -0.11902 | -0.35248 | -0.25177 | -0.18311 | -0.054931 | 122.5113 | 122.5983 | 61.3724 | -122.5021 | 122.4197 | 122.4838 | 61.3998 | -122.6074
572 | 122.6898 | -61.377 | 61.2122 | 0.013046 | -0.034107 | 0.11594 | 0.025229 | 0.054151 | -0.019254 | -0.021856 | -0.0003053 | -0.0013693 | 0.039612 | 0.061562 | -0.01509 | -0.013821 | 61.322 | -61.1435 | 0.059509 | -61.3907 | 61.2259 | -61.3861 | -61.3174 | -61.7111 | 0.027466 | -61.6882 | 61.1252 | 61.1893 | -61.29 | -61.4639 | -0.009155 | 0.059509 | 0.013733 | 0.23346 | -0.013733 | -0.073242 | 0.10986 | 0.086975 | -0.086975 | -0.086975 | -0.33417 | -0.31128 | -0.2243 | -0.022888 | 122.6028 | 122.699 | 61.4365 | -122.5296 | 122.5021 | 122.5662 | 61.4044 | -122.6761
573.7188 | 122.7402 | -61.3449 | 61.2534 | -0.0098417 | -0.037311 | 0.11487 | 0.027365 | 0.051161 | -0.024594 | -0.023138 | -0.0003053 | -0.00072845 | 0.041321 | 0.059426 | -0.017227 | -0.013821 | 61.3129 | -61.1481 | 0.082397 | -61.3541 | 61.3083 | -61.3632 | -61.2762 | -61.7065 | 0.068665 | -61.6241 | 61.1664 | 61.235 | -61.2122 | -61.3998 | -0.01831 | 0.068665 | 0.054932 | 0.19684 | -0.009155 | -0.07782 | 0.059509 | 0.13275 | -0.054931 | -0.086975 | -0.36163 | -0.27924 | -0.22431 | -0.018311 | 122.6532 | 122.6578 | 61.4273 | -122.5296 | 122.5113 | 122.58 | 61.4136 | -122.6532
575.5 | 122.7493 | -61.3449 | 61.2534 | 0.0054168 | -0.037525 | 0.11722 | 0.025229 | 0.049452 | -0.023313 | -0.022497 | -0.0079343 | -0.0028647 | 0.038758 | 0.058571 | -0.016158 | -0.014249 | 61.3083 | -61.1526 | 0.082397 | -61.3541 | 61.2671 | -61.3724 | -61.2717 | -61.6882 | 0.086975 | -61.6333 | 61.1481 | 61.2122 | -61.235 | -61.4227 | -0.027465 | 0.073243 | 0.013733 | 0.19226 | -0.009155 | -0.082398 | 0.054932 | 0.10986 | -0.077819 | -0.10529 | -0.34332 | -0.28839 | -0.21057 | -0.041199 | 122.612 | 122.6532 | 61.4273 | -122.525 | 122.493 | 122.5571 | 61.4319 | -122.6761
577.2031 | 122.7127 | -61.3358 | 61.2671 | 0.013046 | -0.035389 | 0.11573 | 0.027365 | 0.051161 | -0.028226 | -0.023992 | -0.0079343 | -0.0045737 | 0.041107 | 0.059212 | -0.019149 | -0.012326 | 61.3037 | -61.1435 | 0.07782 | -61.3678 | 61.2579 | -61.3403 | -61.2671 | -61.7157 | 0.082397 | -61.6104 | 61.1664 | 61.2534 | -61.2122 | -61.4044 | -0.004578 | 0.068664 | -0.009155 | 0.19226 | -0.032044 | -0.10071 | 0.036621 | 0.1236 | -0.068665 | -0.10071 | -0.37994 | -0.27466 | -0.20599 | -0.013733 | 122.5937 | 122.6395 | 61.4136 | -122.5342 | 122.5021 | 122.5891 | 61.4182 | -122.6715
578.9688 | 122.8455 | -61.3037 | 61.235 | -0.0022127 | -0.040302 | 0.11594 | 0.02587 | 0.051801 | -0.029508 | -0.024633 | 0.0073242 | -0.0054281 | 0.039612 | 0.059853 | -0.018936 | -0.012753 | 61.29 | -61.1252 | 0.045776 | -61.3632 | 61.1664 | -61.3632 | -61.2762 | -61.6882 | 0.068665 | -61.5601 | 61.0794 | 61.1755 | -61.1984 | -61.4044 | -0.059509 | 0.027466 | -0.068664 | 0.17853 | -0.059509 | -0.086975 | 0.054932 | 0.10529 | -0.10071 | -0.15564 | -0.38452 | -0.25635 | -0.15564 | -0.059509 | 122.4701 | 122.5937 | 61.3495 | -122.5113 | 122.3831 | 122.4792 | 61.3724 | -122.6395
580.75 | 122.8134 | -61.2808 | 61.2488 | 0.0054168 | -0.034962 | 0.11701 | 0.027792 | 0.053724 | -0.02908 | -0.02741 | 0.0073242 | -0.0043601 | 0.040039 | 0.059639 | -0.019149 | -0.014249 | 61.4044 | -60.9879 | 0.16479 | -61.2762 | 61.203 | -61.322 | -61.1938 | -61.6104 | 0.17853 | -61.4914 | 61.1114 | 61.1801 | -61.2076 | -61.3586 | -0.041198 | 0.086975 | -0.045776 | 0.29297 | 0.004578 | -0.082397 | 0.15564 | 0.073242 | -0.07782 | -0.13733 | -0.32959 | -0.21057 | -0.13275 | -0.068664 | 122.4838 | 122.6852 | 61.4456 | -122.4426 | 122.3923 | 122.4609 | 61.4594 | -122.6074
582.5312 | 122.8409 | -61.29 | 61.2167 | 0.0054168 | -0.036884 | 0.11487 | 0.029074 | 0.051801 | -0.028012 | -0.025487 | 0.0073242 | -0.0041465 | 0.040467 | 0.058785 | -0.020645 | -0.013608 | 61.3586 | -61.0565 | 0.1236 | -61.3174 | 61.203 | -61.3495 | -61.2488 | -61.6379 | 0.13275 | -61.5051 | 61.084 | 61.1526 | -61.1938 | -61.4044 | -0.059509 | 0.041199 | -0.013733 | 0.23346 | -0.027466 | -0.068665 | 0.14191 | 0.09613 | -0.11444 | -0.13275 | -0.3479 | -0.21515 | -0.10071 | -0.064087 | 122.493 | 122.6486 | 61.4136 | -122.4655 | 122.374 | 122.4426 | 61.4227 | -122.6212
584.25 | 122.7036 | -61.3953 | 61.2213 | 0.0054168 | -0.03133 | 0.11487 | 0.026297 | 0.053297 | -0.018826 | -0.022497 | 0.0073242 | -0.0013693 | 0.04303 | 0.062203 | -0.01509 | -0.014249 | 61.3403 | -61.1298 | 0.09613 | -61.3495 | 61.203 | -61.3678 | -61.2854 | -61.6745 | 0.073242 | -61.6379 | 61.1114 | 61.1389 | -61.2671 | -61.4594 | 0.027466 | 0.10986 | -0.01831 | 0.2655 | 0.045777 | -0.064087 | 0.11902 | 0.12817 | -0.064087 | -0.10986 | -0.27924 | -0.24261 | -0.17853 | -0.082397 | 122.5983 | 122.7356 | 61.4914 | -122.5067 | 122.5067 | 122.5342 | 61.4685 | -122.6807
586.0156 | 122.6898 | -61.3266 | 61.2808 | -0.0022127 | -0.036457 | 0.11594 | 0.030783 | 0.050092 | -0.025662 | -0.025915 | 0.0073242 | -0.0047873 | 0.041962 | 0.060067 | -0.01744 | -0.013394 | 61.29 | -61.0931 | 0.10529 | -61.3312 | 61.235 | -61.3586 | -61.2762 | -61.6974 | 0.068665 | -61.5921 | 61.1389 | 61.2122 | -61.2076 | -61.4136 | -0.032044 | 0.050354 | -0.045777 | 0.23346 | -0.004578 | -0.054932 | 0.009155 | 0.11902 | -0.086975 | -0.14191 | -0.37079 | -0.2655 | -0.17853 | -0.068665 | 122.5616 | 122.6166 | 61.4319 | -122.5571 | 122.4655 | 122.5388 | 61.3953 | -122.6944
587.7812 | 122.8043 | -61.3403 | 61.171 | -0.0022127 | -0.035175 | 0.11487 | 0.025656 | 0.051588 | -0.023313 | -0.021642 | 0.0073242 | -0.0020103 | 0.041535 | 0.060067 | -0.015304 | -0.012112 | 61.2213 | -61.2076 | -0.045776 | -61.4456 | 61.1893 | -61.4182 | -61.3312 | -61.7432 | -0.032043 | -61.6882 | 61.0748 | 61.0977 | -61.2717 | -61.4731 | -0.07782 | 0.009155 | 0.018311 | 0.13275 | -0.10529 | -0.11444 | 0.050354 | 0.068665 | -0.13275 | -0.09613 | -0.40283 | -0.3479 | -0.21515 | -0.073242 | 122.5296 | 122.5616 | 61.2946 | -122.5021 | 122.4152 | 122.438 | 61.3083 | -122.644
589.5 | 122.818 | -61.2946 | 61.2167 | -0.0022127 | -0.036884 | 0.11594 | 0.026511 | 0.050092 | -0.029508 | -0.02506 | 0.0073242 | -0.0054281 | 0.043244 | 0.058785 | -0.018722 | -0.012753 | 61.2579 | -61.1252 | 0.032043 | -61.3586 | 61.1847 | -61.3678 | -61.2671 | -61.7111 | 0.050354 | -61.5784 | 61.0611 | 61.1206 | -61.2213 | -61.4273 | -0.073242 | 0.027466 | -0.032044 | 0.16937 | -0.064087 | -0.091553 | 0.041199 | 0.073243 | -0.13275 | -0.15564 | -0.41656 | -0.28381 | -0.15106 | -0.096131 | 122.4792 | 122.5525 | 61.3266 | -122.4838 | 122.3557 | 122.4152 | 61.3449 | -122.644
591.2188 | 122.7905 | -61.3358 | 61.1572 | 0.0054168 | -0.035175 | 0.1153 | 0.02587 | 0.051588 | -0.023953 | -0.023778 | -0.0079343 | -0.0064963 | 0.041748 | 0.059212 | -0.014663 | -0.015103 | 61.2991 | -61.1069 | 0.054932 | -61.3541 | 61.0977 | -61.3815 | -61.3037 | -61.6699 | 0.045776 | -61.6058 | 61.0245 | 61.0886 | -61.2534 | -61.441 | -0.045777 | 0.032043 | -0.05951 | 0.22888 | -0.018311 | -0.050354 | 0.14191 | 0.082397 | -0.10529 | -0.13275 | -0.33417 | -0.27008 | -0.16479 | -0.068665 | 122.4335 | 122.6349 | 61.3907 | -122.4609 | 122.3602 | 122.4243 | 61.3815 | -122.5983
593 | 122.731 | -61.3266 | 61.2076 | -0.017471 | -0.032398 | 0.11487 | 0.023734 | 0.050092 | -0.021176 | -0.021642 | 0.0073242 | -0.0020103 | 0.041748 | 0.060707 | -0.014022 | -0.014889 | 61.3266 | -61.1206 | 0.09613 | -61.3449 | 61.2488 | -61.3815 | -61.29 | -61.6608 | 0.086975 | -61.6104 | 61.1298 | 61.1618 | -61.2305 | -61.4273 | -0.054932 | 0.036621 | 0.041198 | 0.20599 | -0.018311 | -0.054932 | 0.11902 | 0.09613 | -0.10071 | -0.07782 | -0.33417 | -0.28381 | -0.18311 | -0.045777 | 122.5754 | 122.6532 | 61.4227 | -122.4976 | 122.4564 | 122.4884 | 61.4136 | -122.6349
594.7656 | 122.818 | -61.2625 | 61.2259 | 0.0054168 | -0.036671 | 0.11658 | 0.029074 | 0.050733 | -0.029508 | -0.024206 | 0.0073242 | -0.0052145 | 0.04303 | 0.05729 | -0.020217 | -0.013821 | 61.3586 | -61.0062 | 0.16022 | -61.2946 | 61.1755 | -61.322 | -61.2305 | -61.6058 | 0.16022 | -61.4731 | 61.0703 | 61.1526 | -61.171 | -61.3678 | -0.059509 | 0.032043 | -0.050354 | 0.25635 | -0.032044 | -0.064087 | 0.13275 | 0.091553 | -0.10529 | -0.15564 | -0.34332 | -0.21057 | -0.10529 | -0.073242 | 122.438 | 122.6212 | 61.4227 | -122.4564 | 122.3328 | 122.4152 | 61.4227 | -122.5937
596.5625 | 122.7127 | -61.3678 | 61.1893 | -0.0022127 | -0.037098 | 0.11338 | 0.025656 | 0.054151 | -0.02139 | -0.022497 | 0.022583 | -0.0011557 | 0.041321 | 0.063485 | -0.015304 | -0.013821 | 61.2122 | -61.2488 | -0.050354 | -61.4227 | 61.1755 | -61.4136 | -61.3449 | -61.7752 | -0.050354 | -61.7203 | 61.0931 | 61.1435 | -61.2717 | -61.4685 | -0.045776 | 0.022888 | -0.013733 | 0.11902 | -0.054931 | -0.077819 | 0.022888 | 0.096131 | -0.10071 | -0.09613 | -0.40741 | -0.35248 | -0.25177 | -0.045776 | 122.5433 | 122.58 | 61.3174 | -122.5342 | 122.4609 | 122.5113 | 61.3174 | -122.6578
598.2812 | 122.7997 | -61.2671 | 61.2396 | -0.0098417 | -0.036243 | 0.11701 | 0.029288 | 0.054151 | -0.028226 | -0.023992 | 0.0073242 | -0.0056419 | 0.042389 | 0.061348 | -0.020858 | -0.01318 | 61.2717 | -61.1481 | 0.027466 | -61.3586 | 61.1801 | -61.3632 | -61.29 | -61.7111 | 0.036621 | -61.5646 | 61.0657 | 61.1618 | -61.1938 | -61.3861 | -0.09613 | -0.022888 | -0.059509 | 0.11902 | -0.091553 | -0.068665 | 0.032043 | 0.073242 | -0.11902 | -0.17395 | -0.44403 | -0.29755 | -0.17853 | -0.07782 | 122.4472 | 122.5388 | 61.2946 | -122.5296 | 122.3328 | 122.4289 | 61.3037 | -122.6257
600.0469 | 122.7219 | -61.3449 | 61.2122 | 0.0054168 | -0.032398 | 0.11551 | 0.027152 | 0.053297 | -0.019681 | -0.020788 | -0.015564 | 0.00055335 | 0.041321 | 0.060067 | -0.015518 | -0.014462 | 61.3358 | -61.1298 | 0.086975 | -61.322 | 61.2305 | -61.377 | -61.2854 | -61.647 | 0.10529 | -61.6104 | 61.1206 | 61.1801 | -61.2076 | -61.4044 | -0.032043 | 0.05951 | 0.018311 | 0.21515 | 0.022889 | -0.036621 | 0.1236 | 0.13733 | -0.059509 | -0.091553 | -0.30212 | -0.2655 | -0.20599 | -0.032043 | 122.5754 | 122.6807 | 61.4319 | -122.4976 | 122.4655 | 122.525 | 61.4502 | -122.6166
601.8281 | 122.7173 | -61.3815 | 61.1893 | 0.0054168 | -0.036457 | 0.11188 | 0.023306 | 0.050733 | -0.019681 | -0.02271 | 0.0073242 | -0.0022239 | 0.044953 | 0.063912 | -0.013809 | -0.014676 | 61.1938 | -61.2671 | -0.041199 | -61.441 | 61.1984 | -61.4319 | -61.3312 | -61.7523 | -0.032043 | -61.7294 | 61.0748 | 61.1343 | -61.2854 | -61.4548 | -0.050354 | 0.050354 | 0.009155 | 0.11444 | -0.059509 | -0.10986 | 0.004578 | 0.096131 | -0.073242 | -0.11444 | -0.37079 | -0.3479 | -0.27466 | -0.054932 | 122.58 | 122.5754 | 61.3403 | -122.5204 | 122.4564 | 122.5159 | 61.3495 | -122.644
603.6094 | 122.7493 | -61.3083 | 61.2442 | -0.0022127 | -0.035389 | 0.11466 | 0.028647 | 0.052229 | -0.02908 | -0.023351 | -0.0003053 | -0.0047873 | 0.043457 | 0.060494 | -0.017227 | -0.01318 | 61.3678 | -61.0062 | 0.16937 | -61.2625 | 61.2122 | -61.3037 | -61.235 | -61.615 | 0.1831 | -61.5143 | 61.0748 | 61.171 | -61.1801 | -61.3861 | 0.004578 | 0.073243 | -0.032044 | 0.30212 | 0.045777 | -0.027466 | 0.1236 | 0.12817 | -0.077819 | -0.16937 | -0.3067 | -0.20599 | -0.12817 | -0.073243 | 122.5204 | 122.6761 | 61.4777 | -122.4792 | 122.3831 | 122.4792 | 61.4914 | -122.6303
605.3281 | 122.6715 | -61.3724 | 61.2259 | -0.0022127 | -0.033039 | 0.11402 | 0.024161 | 0.051161 | -0.019467 | -0.021001 | -0.0003053 | -8.7654e-05 | 0.042176 | 0.061776 | -0.013381 | -0.014035 | 61.2442 | -61.2167 | 0.009155 | -61.409 | 61.1938 | -61.409 | -61.2991 | -61.7477 | -0.004578 | -61.7203 | 61.1069 | 61.1481 | -61.2534 | -61.4822 | -0.036622 | 0.073242 | -0.032043 | 0.15564 | -0.036622 | -0.10986 | 0.018311 | 0.11902 | -0.10986 | -0.11902 | -0.37537 | -0.3479 | -0.23804 | -0.07782 | 122.5662 | 122.6166 | 61.3815 | -122.525 | 122.4792 | 122.5204 | 61.3678 | -122.7081
607.0938 | 122.7173 | -61.3266 | 61.2579 | 0.0054168 | -0.034321 | 0.11573 | 0.030142 | 0.051801 | -0.025235 | -0.023565 | 0.0073242 | -0.0011557 | 0.041535 | 0.063698 | -0.017227 | -0.01254 | 61.2671 | -61.1389 | 0.082397 | -61.3495 | 61.2762 | -61.3403 | -61.2488 | -61.7111 | 0.064087 | -61.6241 | 61.1618 | 61.2305 | -61.2259 | -61.3998 | -0.013733 | 0.07782 | 0.01831 | 0.18768 | -0.022888 | -0.10071 | 0.009155 | 0.10071 | -0.073242 | -0.096131 | -0.38452 | -0.29755 | -0.22431 | -0.027466 | 122.6028 | 122.5937 | 61.409 | -122.5067 | 122.4884 | 122.5571 | 61.3907 | -122.6578
608.8594 | 122.6761 | -61.2946 | 61.2762 | 0.0054168 | -0.034321 | 0.11487 | 0.028006 | 0.049879 | -0.028226 | -0.026128 | 0.0073242 | -0.0022239 | 0.042816 | 0.059639 | -0.016372 | -0.012967 | 61.3174 | -61.0977 | 0.1236 | -61.3174 | 61.2213 | -61.3174 | -61.235 | -61.6791 | 0.091553 | -61.5921 | 61.1755 | 61.2122 | -61.1984 | -61.3953 | -0.022888 | 0.05951 | -0.054932 | 0.19684 | -0.022888 | -0.082398 | 0.041199 | 0.096131 | -0.10071 | -0.10071 | -0.38452 | -0.29755 | -0.19684 | -0.064087 | 122.5159 | 122.612 | 61.4182 | -122.5113 | 122.4701 | 122.5067 | 61.3861 | -122.6715
610.6562 | 122.8043 | -61.2808 | 61.2259 | -0.0022127 | -0.03902 | 0.11573 | 0.026724 | 0.050306 | -0.028012 | -0.024847 | 0.0073242 | -0.0071371 | 0.042176 | 0.059426 | -0.020217 | -0.012326 | 61.3678 | -61.0153 | 0.17395 | -61.2717 | 61.1893 | -61.322 | -61.2213 | -61.5829 | 0.1831 | -61.4548 | 61.0794 | 61.1481 | -61.1664 | -61.3678 | -0.041198 | 0.05951 | -0.036621 | 0.2655 | 0.009156 | -0.050354 | 0.14191 | 0.11444 | -0.086975 | -0.14648 | -0.30212 | -0.17395 | -0.086975 | -0.07782 | 122.4701 | 122.6486 | 61.4548 | -122.4472 | 122.3602 | 122.4289 | 61.4639 | -122.5937
612.375 | 122.7264 | -61.3495 | 61.2259 | 0.0054168 | -0.036243 | 0.11316 | 0.023093 | 0.052869 | -0.020749 | -0.023138 | -0.0003053 | -0.0015829 | 0.041321 | 0.060921 | -0.0121 | -0.013821 | 61.3174 | -61.1114 | 0.082397 | -61.3358 | 61.2122 | -61.3632 | -61.2946 | -61.6425 | 0.10986 | -61.6013 | 61.084 | 61.1526 | -61.2167 | -61.4456 | -0.013733 | 0.054931 | -0.013733 | 0.23804 | 0.013733 | -0.041198 | 0.091553 | 0.13275 | -0.096131 | -0.14191 | -0.29297 | -0.25177 | -0.15564 | -0.073242 | 122.5616 | 122.6669 | 61.4319 | -122.5204 | 122.4335 | 122.5021 | 61.4594 | -122.6715
614.1562 | 122.7219 | -61.3129 | 61.2396 | 0.0054168 | -0.036243 | 0.11637 | 0.026938 | 0.051801 | -0.023313 | -0.023138 | 0.0073242 | -0.00094205 | 0.042176 | 0.061989 | -0.01509 | -0.013821 | 61.2991 | -61.1481 | 0.07782 | -61.3266 | 61.2717 | -61.3449 | -61.2488 | -61.6974 | 0.068665 | -61.6287 | 61.1526 | 61.2122 | -61.203 | -61.4044 | -0.032044 | 0.064087 | 0.032043 | 0.16479 | -0.013733 | -0.07782 | 0.059509 | 0.10986 | -0.091553 | -0.086975 | -0.38452 | -0.31586 | -0.2243 | -0.027466 | 122.5845 | 122.612 | 61.3907 | -122.4884 | 122.4655 | 122.525 | 61.3815 | -122.644
615.9531 | 122.699 | -61.3129 | 61.2625 | 0.013046 | -0.03838 | 0.11658 | 0.027792 | 0.051374 | -0.026303 | -0.022497 | 0.014954 | -0.0037191 | 0.040039 | 0.061776 | -0.016158 | -0.012326 | 61.2808 | -61.1298 | 0.091553 | -61.3358 | 61.2534 | -61.322 | -61.2534 | -61.7065 | 0.073242 | -61.615 | 61.1893 | 61.2167 | -61.1755 | -61.3861 | -0.009155 | 0.059509 | -0.009155 | 0.1831 | -0.022888 | -0.082397 | 0.018311 | 0.13733 | -0.073242 | -0.073242 | -0.39368 | -0.30212 | -0.22888 | -0.045776 | 122.5662 | 122.5937 | 61.4044 | -122.5159 | 122.5021 | 122.5296 | 61.3861 | -122.6486
617.7344 | 122.7173 | -61.2946 | 61.29 | -0.0022127 | -0.032398 | 0.11445 | 0.029929 | 0.051374 | -0.026731 | -0.023992 | 0.0073242 | -0.0015829 | 0.042176 | 0.059212 | -0.019149 | -0.013608 | 61.2808 | -61.1481 | 0.068665 | -61.3403 | 61.2717 | -61.3449 | -61.2534 | -61.6928 | 0.082397 | -61.6196 | 61.1618 | 61.2259 | -61.1984 | -61.409 | -0.050354 | 0.041199 | -0.018311 | 0.14648 | -0.045776 | -0.086975 | -0.009155 | 0.096131 | -0.11444 | -0.12817 | -0.39825 | -0.32501 | -0.21057 | -0.064087 | 122.5662 | 122.5754 | 61.3632 | -122.5433 | 122.4564 | 122.5204 | 61.377 | -122.699
619.5 | 122.7448 | -61.3495 | 61.1618 | -0.0022127 | -0.035602 | 0.11231 | 0.025443 | 0.052869 | -0.023526 | -0.02271 | -0.0079343 | -0.0011557 | 0.039612 | 0.063912 | -0.016372 | -0.01318 | 61.1984 | -61.2534 | -0.054932 | -61.4182 | 61.1618 | -61.4044 | -61.322 | -61.7752 | -0.032043 | -61.702 | 61.0611 | 61.171 | -61.2625 | -61.4639 | -0.054932 | 0.027466 | 0 | 0.09613 | -0.068665 | -0.096131 | 0.036621 | 0.086975 | -0.11444 | -0.10071 | -0.42572 | -0.35248 | -0.23804 | 0.009155 | 122.5113 | 122.5479 | 61.2946 | -122.4838 | 122.4106 | 122.5204 | 61.3174 | -122.6257
621.2812 | 122.6532 | -61.3541 | 61.1893 | -0.0098417 | -0.032612 | 0.11359 | 0.028433 | 0.052869 | -0.022244 | -0.023778 | 0.0073242 | -0.0015829 | 0.043885 | 0.06263 | -0.015945 | -0.012112 | 61.3266 | -61.1298 | 0.086975 | -61.3495 | 61.1938 | -61.3495 | -61.2808 | -61.6745 | 0.10529 | -61.615 | 61.1114 | 61.1481 | -61.2259 | -61.4273 | 0.004578 | 0.073242 | 0.004578 | 0.2243 | 0.004578 | -0.068664 | 0.13733 | 0.12817 | -0.073242 | -0.07782 | -0.32044 | -0.26093 | -0.18768 | -0.041199 | 122.5479 | 122.6807 | 61.441 | -122.4701 | 122.4655 | 122.5021 | 61.4594 | -122.6166
622.9844 | 122.6807 | -61.377 | 61.1938 | 0.0054168 | -0.034748 | 0.11445 | 0.027365 | 0.051161 | -0.022672 | -0.021856 | -0.0003053 | -0.0017965 | 0.042176 | 0.061348 | -0.014663 | -0.011471 | 61.2076 | -61.2259 | -0.004578 | -61.4044 | 61.1664 | -61.4182 | -61.3174 | -61.7569 | -0.004578 | -61.7157 | 61.0977 | 61.1526 | -61.2717 | -61.4502 | -0.041199 | 0.059509 | -0.027466 | 0.15106 | -0.027466 | -0.086975 | 0.013733 | 0.10529 | -0.073242 | -0.096131 | -0.37994 | -0.33875 | -0.2655 | -0.041199 | 122.5433 | 122.5845 | 61.3724 | -122.5113 | 122.4747 | 122.5296 | 61.3724 | -122.644
624.75 | 122.7173 | -61.3129 | 61.2625 | 0.020676 | -0.03368 | 0.11466 | 0.029715 | 0.053938 | -0.026517 | -0.023992 | -0.0079343 | -0.0030783 | 0.041535 | 0.057717 | -0.017227 | -0.011471 | 61.2579 | -61.1252 | 0.082397 | -61.3312 | 61.2625 | -61.322 | -61.2442 | -61.7065 | 0.082397 | -61.6013 | 61.1618 | 61.2259 | -61.2076 | -61.4044 | -0.009155 | 0.068664 | 0 | 0.18768 | -0.018311 | -0.086975 | -0.004577 | 0.10529 | -0.091553 | -0.10071 | -0.39368 | -0.28839 | -0.19684 | -0.036621 | 122.5754 | 122.5708 | 61.3953 | -122.5067 | 122.4747 | 122.5388 | 61.3953 | -122.6669
626.4531 | 122.7264 | -61.3586 | 61.1618 | 0.013046 | -0.035816 | 0.1153 | 0.024588 | 0.052015 | -0.024167 | -0.023992 | 0.0073242 | -0.0015829 | 0.041321 | 0.059853 | -0.014663 | -0.01318 | 61.1801 | -61.2442 | -0.059509 | -61.4319 | 61.203 | -61.3998 | -61.3129 | -61.7798 | -0.050354 | -61.6928 | 61.0748 | 61.1481 | -61.2946 | -61.4594 | -0.041198 | 0.045777 | 0.041199 | 0.11444 | -0.073242 | -0.11902 | 0.018311 | 0.064087 | -0.10071 | -0.086975 | -0.42114 | -0.33417 | -0.23346 | -0.013733 | 122.5616 | 122.5388 | 61.2991 | -122.4747 | 122.4335 | 122.5067 | 61.3083 | -122.6212
628.1562 | 122.7036 | -61.2991 | 61.2488 | 0.0054168 | -0.035175 | 0.11637 | 0.027152 | 0.053297 | -0.025235 | -0.023992 | 0.0073242 | -0.00094205 | 0.039185 | 0.059853 | -0.01744 | -0.010403 | 61.2671 | -61.1252 | 0.059509 | -61.3312 | 61.2396 | -61.322 | -61.2579 | -61.7111 | 0.068665 | -61.615 | 61.1572 | 61.2213 | -61.203 | -61.4136 | -0.022888 | 0.041198 | -0.009155 | 0.17395 | -0.032044 | -0.073242 | 0.018311 | 0.09613 | -0.11444 | -0.091552 | -0.41199 | -0.31586 | -0.20142 | -0.027466 | 122.5388 | 122.5662 | 61.3586 | -122.5067 | 122.4564 | 122.5204 | 61.3678 | -122.6624
629.9531 | 122.7631 | -61.3403 | 61.1664 | 0.0054168 | -0.039448 | 0.11359 | 0.026083 | 0.050733 | -0.028226 | -0.023565 | -0.0079343 | -0.0062827 | 0.040253 | 0.060067 | -0.016799 | -0.012326 | 61.2579 | -61.1069 | 0.041199 | -61.3495 | 61.1114 | -61.3724 | -61.2946 | -61.6745 | 0.068665 | -61.5646 | 60.9879 | 61.0886 | -61.2259 | -61.4273 | -0.032043 | 0.045776 | -0.054932 | 0.23346 | -0.009155 | -0.054931 | 0.091553 | 0.11444 | -0.086975 | -0.17853 | -0.33417 | -0.2243 | -0.13733 | -0.07782 | 122.4518 | 122.5983 | 61.3815 | -122.4609 | 122.3282 | 122.4289 | 61.409 | -122.5937
631.7344 | 122.7356 | -61.2808 | 61.2488 | 0.0054168 | -0.033893 | 0.11722 | 0.028006 | 0.050733 | -0.029508 | -0.024633 | 0.014954 | -0.0079917 | 0.040039 | 0.059853 | -0.019576 | -0.01318 | 61.3724 | -60.9787 | 0.17395 | -61.2534 | 61.1938 | -61.2808 | -61.203 | -61.6058 | 0.1831 | -61.4822 | 61.0794 | 61.1526 | -61.1664 | -61.377 | 0 | 0.07782 | -0.054931 | 0.30212 | 0.027466 | -0.050354 | 0.1236 | 0.11444 | -0.09613 | -0.16937 | -0.32501 | -0.20142 | -0.10529 | -0.09613 | 122.4747 | 122.6532 | 61.4548 | -122.4518 | 122.3602 | 122.4335 | 61.4639 | -122.6257
633.4375 | 122.6624 | -61.377 | 61.2122 | 0.0054168 | -0.037311 | 0.11423 | 0.025229 | 0.051161 | -0.021176 | -0.023351 | 0.0073242 | -0.0013693 | 0.041535 | 0.061562 | -0.014236 | -0.012967 | 61.2808 | -61.1618 | 0.050354 | -61.3586 | 61.1938 | -61.3815 | -61.2717 | -61.7249 | 0.013733 | -61.6882 | 61.0703 | 61.1481 | -61.2442 | -61.4502 | -0.004578 | 0.10529 | -0.01831 | 0.21515 | 0.01831 | -0.086976 | 0.068665 | 0.13275 | -0.073242 | -0.14191 | -0.3479 | -0.31128 | -0.23804 | -0.064087 | 122.5708 | 122.6578 | 61.4273 | -122.4838 | 122.4472 | 122.525 | 61.3907 | -122.6624
635.1406 | 122.6669 | -61.3632 | 61.1984 | 0.0054168 | -0.034321 | 0.11039 | 0.026511 | 0.052229 | -0.022885 | -0.022497 | 0.0073242 | -0.0020103 | 0.040467 | 0.060707 | -0.016799 | -0.014035 | 61.3083 | -61.1069 | 0.091553 | -61.3266 | 61.1801 | -61.3266 | -61.2579 | -61.6791 | 0.086975 | -61.6196 | 61.084 | 61.1801 | -61.203 | -61.4182 | 0.036621 | 0.10528 | -0.01831 | 0.25635 | 0.036621 | -0.068664 | 0.10986 | 0.16022 | -0.054932 | -0.11444 | -0.31586 | -0.25635 | -0.20142 | -0.01831 | 122.5433 | 122.6715 | 61.4548 | -122.4564 | 122.4472 | 122.5433 | 61.4502 | -122.6166
636.9062 | 122.7402 | -61.3129 | 61.2167 | 0.0054168 | -0.039875 | 0.11701 | 0.025656 | 0.05052 | -0.030149 | -0.022497 | 0.014954 | -0.0045737 | 0.040253 | 0.059212 | -0.019363 | -0.013394 | 61.2625 | -61.1206 | 0.050354 | -61.3495 | 61.1114 | -61.3495 | -61.2762 | -61.702 | 0.045776 | -61.5738 | 61.0382 | 61.1526 | -61.2167 | -61.4136 | -0.036621 | 0.036621 | -0.10529 | 0.19226 | -0.036621 | -0.073242 | 0.045776 | 0.09613 | -0.10071 | -0.17853 | -0.3891 | -0.26093 | -0.16022 | -0.064087 | 122.4243 | 122.5754 | 61.3632 | -122.493 | 122.3511 | 122.4655 | 61.3586 | -122.6303
638.6875 | 122.6624 | -61.3678 | 61.1801 | 0.013046 | -0.035175 | 0.11466 | 0.027152 | 0.053938 | -0.022031 | -0.020147 | -0.0003053 | 0.0026895 | 0.042816 | 0.06028 | -0.01509 | -0.01318 | 61.2076 | -61.2396 | -0.032043 | -61.4136 | 61.1847 | -61.3861 | -61.2991 | -61.7706 | -0.041199 | -61.734 | 61.0611 | 61.1389 | -61.2534 | -61.4548 | -0.01831 | 0.068665 | 0.004577 | 0.12817 | -0.045776 | -0.11444 | 0.027466 | 0.11444 | -0.086975 | -0.11902 | -0.40283 | -0.36621 | -0.27924 | -0.041199 | 122.5525 | 122.5754 | 61.3358 | -122.4792 | 122.4289 | 122.5067 | 61.3266 | -122.6349
640.4844 | 122.7951 | -61.2671 | 61.203 | 0.013046 | -0.036671 | 0.11466 | 0.02886 | 0.051801 | -0.029508 | -0.02506 | 0.0073242 | -0.0058555 | 0.041535 | 0.062203 | -0.018081 | -0.01318 | 61.2534 | -61.116 | 0.050354 | -61.322 | 61.1618 | -61.3403 | -61.2534 | -61.6699 | 0.059509 | -61.5417 | 61.0519 | 61.1435 | -61.1938 | -61.377 | -0.073242 | 0.013733 | -0.041199 | 0.15106 | -0.054931 | -0.068664 | 0.050354 | 0.073242 | -0.10986 | -0.15106 | -0.40283 | -0.27466 | -0.16479 | -0.059509 | 122.4289 | 122.5204 | 61.3174 | -122.4564 | 122.319 | 122.4106 | 61.3266 | -122.58
642.1875 | 122.699 | -61.3174 | 61.2396 | -0.0022127 | -0.035816 | 0.1153 | 0.026938 | 0.052869 | -0.025662 | -0.023778 | 0.0073242 | -0.0015829 | 0.042176 | 0.060494 | -0.01509 | -0.014249 | 61.29 | -61.1343 | 0.091553 | -61.3312 | 61.2534 | -61.322 | -61.2534 | -61.6745 | 0.064087 | -61.6104 | 61.1481 | 61.1938 | -61.1984 | -61.3861 | -0.004577 | 0.064087 | 0.013733 | 0.18311 | -0.013733 | -0.07782 | 0.050354 | 0.11902 | -0.068664 | -0.091553 | -0.35706 | -0.29297 | -0.22431 | -0.045776 | 122.5708 | 122.6074 | 61.409 | -122.493 | 122.4655 | 122.5113 | 61.3815 | -122.6257
643.8906 | 122.6852 | -61.3312 | 61.235 | -0.0098417 | -0.033039 | 0.11487 | 0.026938 | 0.052442 | -0.020749 | -0.023565 | 0.0073242 | -0.0017965 | 0.042816 | 0.061562 | -0.01509 | -0.014249 | 61.2991 | -61.1114 | 0.09613 | -61.3312 | 61.2213 | -61.3403 | -61.2854 | -61.6516 | 0.10986 | -61.5875 | 61.0748 | 61.1847 | -61.2122 | -61.441 | -0.009155 | 0.045777 | -0.013733 | 0.21973 | 0 | -0.045777 | 0.064087 | 0.11902 | -0.10986 | -0.16022 | -0.32043 | -0.25635 | -0.14648 | -0.050354 | 122.5525 | 122.6303 | 61.4273 | -122.5204 | 122.406 | 122.5159 | 61.441 | -122.6761
645.6094 | 122.6578 | -61.3037 | 61.2717 | 0.013046 | -0.034534 | 0.11487 | 0.027152 | 0.05351 | -0.02844 | -0.023778 | 0.014954 | -0.0041465 | 0.041321 | 0.058571 | -0.019149 | -0.012753 | 61.3495 | -61.0199 | 0.16937 | -61.2534 | 61.1938 | -61.3037 | -61.2076 | -61.6104 | 0.16937 | -61.5143 | 61.1206 | 61.203 | -61.1526 | -61.3358 | 0 | 0.09613 | -0.077819 | 0.28381 | 0.050354 | -0.045776 | 0.07782 | 0.15106 | -0.032043 | -0.15106 | -0.3067 | -0.21057 | -0.17853 | -0.068664 | 122.4976 | 122.6532 | 61.4731 | -122.4792 | 122.4243 | 122.5067 | 61.4731 | -122.6074
647.3281 | 122.644 | -61.3586 | 61.1847 | -0.0022127 | -0.032825 | 0.11103 | 0.02587 | 0.049024 | -0.021604 | -0.02271 | 0.0073242 | 0.0022623 | 0.044312 | 0.061562 | -0.014449 | -0.016385 | 61.3037 | -61.1298 | 0.091553 | -61.3449 | 61.2076 | -61.3541 | -61.2808 | -61.6745 | 0.07782 | -61.6241 | 61.0748 | 61.1618 | -61.2305 | -61.4182 | 0.004578 | 0.07782 | 0.022889 | 0.22888 | 0.013733 | -0.064087 | 0.11902 | 0.12817 | -0.059509 | -0.10986 | -0.31586 | -0.2655 | -0.20599 | -0.022888 | 122.5662 | 122.6624 | 61.4502 | -122.4655 | 122.4335 | 122.5204 | 61.4365 | -122.6028
649.0938 | 122.6532 | -61.3632 | 61.1938 | 0.0054168 | -0.034534 | 0.11338 | 0.026511 | 0.053938 | -0.020322 | -0.020574 | -0.0003053 | -0.0015829 | 0.041962 | 0.061776 | -0.015304 | -0.013821 | 61.2808 | -61.1526 | 0.064087 | -61.3495 | 61.1847 | -61.3815 | -61.2991 | -61.7157 | 0.018311 | -61.6653 | 61.0611 | 61.1755 | -61.2442 | -61.4456 | -0.018311 | 0.064087 | -0.009156 | 0.21057 | 0.013733 | -0.050354 | 0.086975 | 0.11902 | -0.082398 | -0.13275 | -0.35248 | -0.30212 | -0.21973 | -0.018311 | 122.5479 | 122.644 | 61.4273 | -122.493 | 122.4243 | 122.5388 | 61.3815 | -122.6395
650.875 | 122.7448 | -61.3129 | 61.1847 | 0.013046 | -0.038593 | 0.11295 | 0.026938 | 0.052015 | -0.026731 | -0.023351 | -0.0003053 | -0.0041465 | 0.041748 | 0.061135 | -0.019149 | -0.01254 | 61.2625 | -61.0931 | 0.068665 | -61.3449 | 61.0886 | -61.3724 | -61.2671 | -61.6791 | 0.050354 | -61.5509 | 61.0153 | 61.1023 | -61.2122 | -61.4136 | -0.059509 | 0.045776 | -0.09613 | 0.21973 | -0.032044 | -0.07782 | 0.07782 | 0.10071 | -0.10071 | -0.16937 | -0.36621 | -0.23804 | -0.13733 | -0.082397 | 122.4014 | 122.5754 | 61.3815 | -122.4518 | 122.3282 | 122.4152 | 61.3632 | -122.5983
652.6875 | 122.6715 | -61.3129 | 61.2534 | -0.0022127 | -0.036884 | 0.11573 | 0.029501 | 0.052656 | -0.026517 | -0.025274 | 0.0073242 | -0.0043601 | 0.044312 | 0.060494 | -0.018295 | -0.012112 | 61.2625 | -61.1252 | 0.07782 | -61.3174 | 61.2625 | -61.3129 | -61.2442 | -61.6928 | 0.07782 | -61.5921 | 61.1343 | 61.2305 | -61.1664 | -61.3541 | 0 | 0.068664 | 0.009155 | 0.18768 | -0.004578 | -0.073242 | 0.009155 | 0.14648 | -0.041199 | -0.11902 | -0.37994 | -0.27924 | -0.23804 | -0.022888 | 122.5754 | 122.5754 | 61.3907 | -122.4976 | 122.4472 | 122.5433 | 61.3907 | -122.6074
654.4688 | 122.7173 | -61.2991 | 61.1893 | 0.013046 | -0.040943 | 0.11701 | 0.025015 | 0.051801 | -0.027371 | -0.023992 | 0.0073242 | -0.0060691 | 0.038758 | 0.061562 | -0.017867 | -0.011899 | 61.2854 | -61.0931 | 0.059509 | -61.3358 | 61.116 | -61.3632 | -61.2625 | -61.6608 | 0.032043 | -61.5555 | 61.0291 | 61.1069 | -61.2167 | -61.4319 | -0.064087 | 0.036621 | -0.073242 | 0.20599 | -0.036621 | -0.073242 | 0.09613 | 0.082397 | -0.13275 | -0.16022 | -0.36163 | -0.25635 | -0.1236 | -0.082397 | 122.4152 | 122.5845 | 61.3586 | -122.4518 | 122.3282 | 122.406 | 61.3312 | -122.6212
656.1875 | 122.6486 | -61.3724 | 61.171 | -0.0022127 | -0.035389 | 0.11509 | 0.023947 | 0.052869 | -0.020535 | -0.022497 | -0.0003053 | -0.00030125 | 0.044098 | 0.06263 | -0.015518 | -0.014462 | 61.2259 | -61.203 | 0.009155 | -61.3861 | 61.1847 | -61.3724 | -61.3037 | -61.7249 | -0.018311 | -61.702 | 61.0657 | 61.116 | -61.2396 | -61.4456 | 0 | 0.068664 | 0.013733 | 0.16937 | -0.013733 | -0.082397 | 0.054932 | 0.13275 | -0.073243 | -0.10529 | -0.35248 | -0.32959 | -0.25635 | -0.054931 | 122.5571 | 122.5983 | 61.3815 | -122.4747 | 122.438 | 122.4884 | 61.3541 | -122.6166
657.9688 | 122.7219 | -61.3037 | 61.203 | 0.0054168 | -0.037311 | 0.11594 | 0.02886 | 0.052015 | -0.028653 | -0.024633 | -0.0003053 | -0.0077781 | 0.044098 | 0.06028 | -0.016586 | -0.01318 | 61.2488 | -61.0931 | 0.054932 | -61.3449 | 61.1389 | -61.3449 | -61.2671 | -61.6791 | 0.045776 | -61.5692 | 61.0107 | 61.1023 | -61.2213 | -61.3998 | -0.041199 | 0.036621 | -0.064087 | 0.21057 | -0.041199 | -0.07782 | 0.045776 | 0.082398 | -0.09613 | -0.19226 | -0.37537 | -0.2655 | -0.16937 | -0.10071 | 122.4426 | 122.5525 | 61.3586 | -122.4701 | 122.3145 | 122.406 | 61.3495 | -122.6028
659.6719 | 122.7173 | -61.3174 | 61.1664 | 0.013046 | -0.039448 | 0.11445 | 0.026938 | 0.053083 | -0.027371 | -0.022069 | 0.0073242 | -0.0054281 | 0.040467 | 0.059426 | -0.016799 | -0.013608 | 61.2717 | -61.0748 | 0.054932 | -61.3358 | 61.0977 | -61.3495 | -61.2717 | -61.6425 | 0.041199 | -61.5738 | 61.0153 | 61.0703 | -61.2305 | -61.4182 | -0.032043 | 0.045777 | -0.068665 | 0.24262 | -0.01831 | -0.064087 | 0.10529 | 0.086975 | -0.10071 | -0.15106 | -0.32501 | -0.25635 | -0.15564 | -0.096131 | 122.4152 | 122.5891 | 61.3724 | -122.438 | 122.3328 | 122.3877 | 61.3586 | -122.5845
661.375 | 122.7951 | -61.2396 | 61.1938 | 0.013046 | -0.037525 | 0.11594 | 0.029501 | 0.052229 | -0.02844 | -0.025487 | 0.0073242 | -0.0054281 | 0.043244 | 0.060067 | -0.018081 | -0.014462 | 61.3174 | -61.0199 | 0.11902 | -61.2762 | 61.1893 | -61.29 | -61.2167 | -61.6058 | 0.10529 | -61.4777 | 61.0657 | 61.116 | -61.1664 | -61.3586 | -0.050354 | 0.022888 | -0.004578 | 0.21973 | -0.036621 | -0.059509 | 0.1236 | 0.073242 | -0.11902 | -0.12817 | -0.36621 | -0.23804 | -0.11902 | -0.07782 | 122.4289 | 122.5571 | 61.3586 | -122.4106 | 122.3053 | 122.3557 | 61.3449 | -122.5525
663.1562 | 122.6669 | -61.3495 | 61.1435 | 0.0054168 | -0.035389 | 0.11338 | 0.026511 | 0.053083 | -0.020963 | -0.023351 | 0.014954 | -0.00030125 | 0.041107 | 0.061135 | -0.014022 | -0.014676 | 61.2076 | -61.2396 | -0.059509 | -61.409 | 61.1526 | -61.3815 | -61.3037 | -61.7249 | -0.050354 | -61.6928 | 61.0657 | 61.1252 | -61.2442 | -61.4319 | -0.032044 | 0.045776 | 0.009155 | 0.10986 | -0.05951 | -0.10529 | 0.064087 | 0.10529 | -0.082398 | -0.07782 | -0.37537 | -0.34332 | -0.26093 | -0.018311 | 122.5021 | 122.5571 | 61.29 | -122.4472 | 122.4152 | 122.4747 | 61.2991 | -122.5754
664.9375 | 122.7081 | -61.3129 | 61.1938 | -0.0022127 | -0.042652 | 0.11573 | 0.025229 | 0.049879 | -0.029294 | -0.023138 | 0.0073242 | -0.0032919 | 0.039612 | 0.060921 | -0.016799 | -0.011899 | 61.2762 | -61.0886 | 0.036621 | -61.3449 | 61.1206 | -61.3403 | -61.2579 | -61.6653 | 0.018311 | -61.5921 | 61.0565 | 61.1206 | -61.1938 | -61.377 | -0.027466 | 0.054931 | -0.073243 | 0.2243 | -0.032044 | -0.086975 | 0.082397 | 0.11902 | -0.064087 | -0.13733 | -0.35248 | -0.27924 | -0.21515 | -0.073243 | 122.4335 | 122.5891 | 61.3495 | -122.4518 | 122.3694 | 122.4335 | 61.3312 | -122.5708
666.6406 | 122.6944 | -61.3312 | 61.1801 | -0.0022127 | -0.034748 | 0.11658 | 0.026297 | 0.052656 | -0.021176 | -0.023351 | 0.0073242 | -0.0013693 | 0.039826 | 0.060067 | -0.014663 | -0.015103 | 61.2122 | -61.235 | -0.068665 | -61.3953 | 61.171 | -61.3678 | -61.3358 | -61.7294 | -0.045776 | -61.6928 | 61.0657 | 61.1343 | -61.2625 | -61.4136 | -0.036621 | -0.004577 | -0.009156 | 0.096131 | -0.064087 | -0.05951 | 0.032043 | 0.068665 | -0.082397 | -0.11444 | -0.39825 | -0.36163 | -0.27924 | -0.045777 | 122.5021 | 122.5433 | 61.2625 | -122.5159 | 122.3969 | 122.4655 | 61.2854 | -122.5937
668.375 | 122.6852 | -61.2991 | 61.1755 | -0.0022127 | -0.035816 | 0.11573 | 0.024802 | 0.052229 | -0.022244 | -0.02036 | -0.0003053 | 0.00012615 | 0.041107 | 0.059639 | -0.014877 | -0.01318 | 61.2808 | -61.116 | 0.086975 | -61.3083 | 61.2076 | -61.3403 | -61.2671 | -61.6333 | 0.10071 | -61.5784 | 61.1023 | 61.1435 | -61.203 | -61.377 | -0.041199 | 0.032043 | 0.032044 | 0.1831 | -0.009156 | -0.041199 | 0.10529 | 0.09613 | -0.07782 | -0.073242 | -0.33417 | -0.27924 | -0.20142 | -0.032043 | 122.5067 | 122.58 | 61.3861 | -122.4426 | 122.4014 | 122.4426 | 61.3998 | -122.5525
670.1406 | 122.644 | -61.3449 | 61.1801 | 0.0054168 | -0.03368 | 0.11466 | 0.026724 | 0.05351 | -0.022672 | -0.021642 | -0.0079343 | -0.0015829 | 0.040467 | 0.058999 | -0.016372 | -0.013821 | 61.3037 | -61.0977 | 0.10071 | -61.322 | 61.171 | -61.3495 | -61.29 | -61.6287 | 0.11444 | -61.5875 | 61.084 | 61.1572 | -61.2076 | -61.3953 | -0.004577 | 0.054932 | -0.009156 | 0.24719 | 0.022889 | -0.032043 | 0.1236 | 0.13733 | -0.050354 | -0.096131 | -0.28381 | -0.24261 | -0.19226 | -0.022888 | 122.5159 | 122.6486 | 61.4456 | -122.4701 | 122.4289 | 122.5021 | 61.4594 | -122.5754
671.9375 | 122.6532 | -61.2808 | 61.2625 | 0.013046 | -0.035175 | 0.11551 | 0.029715 | 0.053083 | -0.026303 | -0.02271 | 0.0073242 | -0.0041465 | 0.044098 | 0.061135 | -0.018508 | -0.014249 | 61.2717 | -61.1298 | 0.091553 | -61.3174 | 61.2122 | -61.3174 | -61.2396 | -61.6791 | 0.07782 | -61.5692 | 61.1526 | 61.2213 | -61.1618 | -61.3586 | -0.036621 | 0.041199 | -0.050354 | 0.15106 | -0.036621 | -0.07782 | 0.009155 | 0.11902 | -0.07782 | -0.10986 | -0.39825 | -0.28839 | -0.21057 | -0.041199 | 122.493 | 122.5525 | 61.3724 | -122.5021 | 122.4335 | 122.5021 | 61.3586 | -122.6212
673.7344 | 122.7859 | -61.2579 | 61.203 | -0.0022127 | -0.034748 | 0.11957 | 0.027365 | 0.053083 | -0.029508 | -0.025701 | -0.0003053 | -0.0058555 | 0.040894 | 0.058999 | -0.020217 | -0.012326 | 61.2625 | -61.0931 | 0.064087 | -61.3037 | 61.1389 | -61.322 | -61.2442 | -61.6425 | 0.086975 | -61.5143 | 61.0428 | 61.1618 | -61.1572 | -61.3541 | -0.064086 | 0.013733 | -0.064087 | 0.1648 | -0.045776 | -0.059509 | 0.059509 | 0.10071 | -0.09613 | -0.16022 | -0.38452 | -0.25635 | -0.16022 | -0.041199 | 122.3969 | 122.5204 | 61.322 | -122.4472 | 122.3007 | 122.4197 | 61.3449 | -122.5571
675.5312 | 122.7768 | -61.3312 | 61.1023 | 0.0054168 | -0.037311 | 0.11573 | 0.022665 | 0.052229 | -0.024594 | -0.021001 | 0.014954 | -0.0022239 | 0.041107 | 0.058358 | -0.014022 | -0.013394 | 61.2396 | -61.1389 | -0.009155 | -61.3678 | 61.1252 | -61.377 | -61.3083 | -61.6608 | 0.027466 | -61.5829 | 61.0153 | 61.0611 | -61.2534 | -61.4136 | -0.045776 | 0.022888 | 0.022888 | 0.19226 | -0.036621 | -0.059509 | 0.13733 | 0.07782 | -0.082397 | -0.086975 | -0.32959 | -0.25177 | -0.16937 | -0.041199 | 122.4564 | 122.5708 | 61.322 | -122.4106 | 122.3465 | 122.3923 | 61.3586 | -122.5159
677.25 | 122.7402 | -61.2946 | 61.1206 | 0.0054168 | -0.035175 | 0.11487 | 0.025015 | 0.051161 | -0.025876 | -0.023992 | 0.014954 | -0.0043601 | 0.039398 | 0.059639 | -0.016799 | -0.014249 | 61.2671 | -61.0886 | 0.045776 | -61.3174 | 61.0703 | -61.3678 | -61.2808 | -61.6379 | 0.045776 | -61.5692 | 61.0062 | 61.0519 | -61.2442 | -61.441 | -0.073242 | 0.013733 | -0.050354 | 0.20599 | -0.022888 | -0.036621 | 0.14649 | 0.050354 | -0.14648 | -0.11444 | -0.34332 | -0.27466 | -0.12817 | -0.068664 | 122.3648 | 122.5616 | 61.3403 | -122.4014 | 122.3007 | 122.3465 | 61.3403 | -122.5616
678.9688 | 122.7539 | -61.3129 | 61.1252 | -0.0022127 | -0.038807 | 0.11658 | 0.025015 | 0.052015 | -0.025022 | -0.023992 | 0.0073242 | -0.0045737 | 0.040894 | 0.06028 | -0.015518 | -0.01318 | 61.2625 | -61.0931 | 0.045776 | -61.322 | 61.1069 | -61.3632 | -61.2671 | -61.6562 | 0.068665 | -61.5463 | 60.9924 | 61.0428 | -61.2122 | -61.4136 | -0.050354 | 0.045776 | -0.01831 | 0.21973 | -0.009155 | -0.054931 | 0.13733 | 0.10071 | -0.10071 | -0.13275 | -0.34332 | -0.23346 | -0.13275 | -0.082397 | 122.4197 | 122.5754 | 61.3586 | -122.3923 | 122.3053 | 122.3557 | 61.3815 | -122.5388
680.75 | 122.7539 | -61.3312 | 61.1206 | 0.0054168 | -0.034962 | 0.11359 | 0.026297 | 0.052229 | -0.025022 | -0.022497 | -0.0003053 | -0.0054281 | 0.04303 | 0.059639 | -0.015945 | -0.01318 | 61.2762 | -61.0886 | 0.032043 | -61.322 | 61.084 | -61.3586 | -61.2717 | -61.6241 | 0.073242 | -61.5646 | 61.0199 | 61.0428 | -61.2396 | -61.4182 | -0.027466 | 0.05951 | -0.036621 | 0.24261 | 0.009156 | -0.050354 | 0.15564 | 0.091553 | -0.086975 | -0.10071 | -0.29297 | -0.23346 | -0.14648 | -0.077819 | 122.4152 | 122.6074 | 61.3632 | -122.3923 | 122.3511 | 122.374 | 61.4044 | -122.5388
682.5469 | 122.6349 | -61.3174 | 61.1801 | 0.0054168 | -0.034107 | 0.11103 | 0.027152 | 0.056287 | -0.021817 | -0.023565 | -0.0003053 | -0.0028647 | 0.041962 | 0.062203 | -0.015304 | -0.014462 | 61.3174 | -61.084 | 0.091553 | -61.3174 | 61.1893 | -61.322 | -61.2534 | -61.6241 | 0.086975 | -61.6058 | 61.0611 | 61.1664 | -61.1938 | -61.4227 | -0.004577 | 0.064087 | 0.009155 | 0.23346 | 0 | -0.064087 | 0.13733 | 0.1236 | -0.10528 | -0.11902 | -0.3067 | -0.28839 | -0.18311 | -0.013733 | 122.5067 | 122.6349 | 61.409 | -122.4335 | 122.3785 | 122.4838 | 61.4044 | -122.6028
684.2656 | 122.6395 | -61.3403 | 61.1618 | 0.0054168 | -0.035816 | 0.11252 | 0.027579 | 0.051374 | -0.020322 | -0.01972 | 0.0073242 | -0.00094205 | 0.040253 | 0.060921 | -0.01509 | -0.013608 | 61.1801 | -61.2122 | -0.036621 | -61.3907 | 61.1801 | -61.377 | -61.2946 | -61.7523 | -0.013733 | -61.6974 | 61.0565 | 61.1572 | -61.235 | -61.4182 | -0.036621 | 0.045776 | 0.018311 | 0.12817 | -0.050354 | -0.09613 | 0.018311 | 0.10529 | -0.07782 | -0.10528 | -0.41199 | -0.35706 | -0.27924 | -0.004577 | 122.5204 | 122.5204 | 61.3037 | -122.4564 | 122.3969 | 122.4976 | 61.3266 | -122.58
686.0312 | 122.6669 | -61.2854 | 61.2213 | 0.013046 | -0.035175 | 0.11594 | 0.027792 | 0.05052 | -0.023953 | -0.025915 | 0.014954 | -0.0026511 | 0.044525 | 0.059639 | -0.015731 | -0.011471 | 61.2625 | -61.1114 | 0.07782 | -61.3083 | 61.2259 | -61.3174 | -61.2167 | -61.6562 | 0.082397 | -61.5829 | 61.1298 | 61.171 | -61.1847 | -61.3541 | -0.032044 | 0.068664 | 0.004578 | 0.17395 | -0.022889 | -0.091553 | 0.041199 | 0.10071 | -0.068665 | -0.091552 | -0.37079 | -0.29755 | -0.22888 | -0.050354 | 122.5113 | 122.5479 | 61.3632 | -122.438 | 122.4152 | 122.4564 | 61.3678 | -122.5754
687.8125 | 122.7493 | -61.2579 | 61.203 | 0.0054168 | -0.039448 | 0.11551 | 0.029288 | 0.050733 | -0.030576 | -0.025701 | 0.0073242 | -0.0064963 | 0.043244 | 0.057503 | -0.018936 | -0.01318 | 61.2213 | -61.0931 | 0.045776 | -61.3083 | 61.1572 | -61.3312 | -61.235 | -61.6516 | 0.054932 | -61.528 | 61.0474 | 61.1252 | -61.1893 | -61.3678 | -0.073242 | 0.022889 | -0.045776 | 0.1648 | -0.050354 | -0.073243 | 0.01831 | 0.068665 | -0.10986 | -0.15564 | -0.39368 | -0.27008 | -0.16022 | -0.07782 | 122.4152 | 122.4792 | 61.3037 | -122.438 | 122.3053 | 122.3831 | 61.3129 | -122.5708
689.5781 | 122.644 | -61.2991 | 61.2534 | 0.0054168 | -0.033253 | 0.11551 | 0.028006 | 0.053724 | -0.025449 | -0.024206 | 0.0073242 | -0.0011557 | 0.041321 | 0.059639 | -0.017227 | -0.013608 | 61.2534 | -61.1206 | 0.068665 | -61.3037 | 61.2396 | -61.3037 | -61.2396 | -61.6699 | 0.082397 | -61.5738 | 61.1023 | 61.2076 | -61.1847 | -61.3495 | -0.004578 | 0.059509 | -0.013733 | 0.17853 | -0.004578 | -0.064087 | 0 | 0.11444 | -0.050354 | -0.15106 | -0.37079 | -0.27466 | -0.2243 | -0.045776 | 122.5388 | 122.5525 | 61.3678 | -122.493 | 122.4014 | 122.5067 | 61.3815 | -122.6028
691.2812 | 122.7219 | -61.2991 | 61.1664 | 0.013046 | -0.03838 | 0.11445 | 0.024802 | 0.052442 | -0.028012 | -0.02271 | 0.014954 | -0.0050009 | 0.04068 | 0.059853 | -0.019149 | -0.013394 | 61.2717 | -61.0794 | 0.054932 | -61.3174 | 61.1069 | -61.3312 | -61.2671 | -61.647 | 0.050354 | -61.5463 | 61.0153 | 61.0886 | -61.2076 | -61.4182 | -0.032044 | 0.032043 | -0.059509 | 0.21973 | -0.018311 | -0.050354 | 0.10529 | 0.091552 | -0.11902 | -0.15106 | -0.3479 | -0.24719 | -0.12817 | -0.07782 | 122.406 | 122.5708 | 61.3541 | -122.4335 | 122.3145 | 122.3877 | 61.3495 | -122.5845
693.0781 | 122.6395 | -61.2625 | 61.2717 | 0.0054168 | -0.03838 | 0.11551 | 0.027579 | 0.05351 | -0.025662 | -0.023351 | 0.014954 | -0.0017965 | 0.040467 | 0.060921 | -0.017013 | -0.015103 | 61.3358 | -61.0474 | 0.1236 | -61.2717 | 61.2167 | -61.29 | -61.2259 | -61.6241 | 0.082397 | -61.5463 | 61.1298 | 61.203 | -61.1664 | -61.3541 | -0.027466 | 0.036621 | -0.054931 | 0.21515 | -0.009155 | -0.045776 | 0.064087 | 0.09613 | -0.091553 | -0.14191 | -0.36163 | -0.28381 | -0.19226 | -0.068664 | 122.4792 | 122.5983 | 61.3861 | -122.4976 | 122.3923 | 122.4655 | 61.3449 | -122.6257
694.8594 | 122.6761 | -61.2946 | 61.2076 | -0.0022127 | -0.035389 | 0.11338 | 0.025015 | 0.053297 | -0.02139 | -0.022283 | 0.014954 | 0.00012615 | 0.043457 | 0.062416 | -0.014877 | -0.015103 | 61.2946 | -61.0931 | 0.091553 | -61.2991 | 61.1984 | -61.3266 | -61.2625 | -61.6333 | 0.10529 | -61.5646 | 61.0703 | 61.1526 | -61.1801 | -61.3861 | -0.032043 | 0.032044 | -0.009156 | 0.20142 | -0.004577 | -0.036621 | 0.086975 | 0.11444 | -0.091552 | -0.13733 | -0.33875 | -0.27008 | -0.17853 | -0.054932 | 122.493 | 122.5891 | 61.3861 | -122.4701 | 122.3648 | 122.4472 | 61.3998 | -122.5937
696.5781 | 122.7448 | -61.2534 | 61.1801 | 0.013046 | -0.038807 | 0.11573 | 0.028433 | 0.052869 | -0.030789 | -0.025701 | 0.0073242 | -0.0060691 | 0.040253 | 0.059853 | -0.019576 | -0.015103 | 61.2396 | -61.084 | 0.050354 | -61.3083 | 61.1572 | -61.3266 | -61.2122 | -61.6379 | 0.086975 | -61.5097 | 61.0199 | 61.1298 | -61.1755 | -61.377 | -0.073242 | 0.041199 | -0.022888 | 0.16937 | -0.054932 | -0.096131 | 0.059509 | 0.07782 | -0.1236 | -0.16022 | -0.38452 | -0.25635 | -0.13275 | -0.050354 | 122.4106 | 122.493 | 61.3037 | -122.3923 | 122.2733 | 122.3831 | 61.3403 | -122.5571
698.3594 | 122.7539 | -61.2259 | 61.203 | -0.0098417 | -0.03603 | 0.11466 | 0.026297 | 0.050306 | -0.026731 | -0.024847 | 0.0073242 | -0.0071371 | 0.041535 | 0.061348 | -0.016372 | -0.012753 | 61.3449 | -60.9787 | 0.14648 | -61.2396 | 61.1572 | -61.3083 | -61.203 | -61.5555 | 0.16937 | -61.4227 | 61.0474 | 61.1114 | -61.1252 | -61.322 | -0.082398 | 0.022888 | -0.045776 | 0.24719 | -0.013733 | -0.036621 | 0.14191 | 0.10071 | -0.09613 | -0.15564 | -0.32959 | -0.19684 | -0.10071 | -0.091553 | 122.3831 | 122.5708 | 61.3724 | -122.406 | 122.2733 | 122.3373 | 61.3953 | -122.525
700.0781 | 122.612 | -61.2625 | 61.2488 | -0.0022127 | -0.034962 | 0.11658 | 0.026938 | 0.050733 | -0.023953 | -0.024847 | 0.014954 | -0.0037191 | 0.040253 | 0.059212 | -0.015945 | -0.013608 | 61.2579 | -61.084 | 0.091553 | -61.3129 | 61.2259 | -61.2808 | -61.2259 | -61.6516 | 0.068665 | -61.5692 | 61.1481 | 61.1664 | -61.1938 | -61.3403 | -0.018311 | 0.036621 | -0.022888 | 0.17853 | -0.050354 | -0.086975 | 0.009156 | 0.068664 | -0.07782 | -0.10071 | -0.3891 | -0.3067 | -0.22888 | -0.082397 | 122.4884 | 122.5204 | 61.3541 | -122.4747 | 122.4106 | 122.4289 | 61.3312 | -122.5891
701.8438 | 122.7448 | -61.2808 | 61.1252 | -0.0098417 | -0.037311 | 0.11551 | 0.025015 | 0.050733 | -0.020963 | -0.022924 | 0.0073242 | -0.0011557 | 0.040039 | 0.057717 | -0.016372 | -0.013821 | 61.2854 | -61.0748 | 0.036621 | -61.2946 | 61.0794 | -61.3495 | -61.2717 | -61.6241 | 0.064087 | -61.5509 | 61.0062 | 61.0245 | -61.2213 | -61.4136 | -0.068664 | 0.009156 | -0.045776 | 0.20599 | -0.013733 | -0.022889 | 0.16022 | 0.05951 | -0.13275 | -0.11902 | -0.34332 | -0.27008 | -0.13733 | -0.10071 | 122.3602 | 122.5662 | 61.3174 | -122.3969 | 122.287 | 122.3053 | 61.3449 | -122.5388
703.6406 | 122.7448 | -61.235 | 61.1984 | -0.0022127 | -0.03603 | 0.11423 | 0.029501 | 0.053297 | -0.027799 | -0.023351 | -0.0079343 | -0.0035055 | 0.042816 | 0.059426 | -0.018295 | -0.014889 | 61.2305 | -61.0886 | 0.050354 | -61.2991 | 61.1481 | -61.3129 | -61.2442 | -61.6379 | 0.054932 | -61.5097 | 61.0519 | 61.084 | -61.1847 | -61.3907 | -0.07782 | -0.009156 | -0.050354 | 0.14648 | -0.064087 | -0.054931 | 0.032044 | 0.050354 | -0.15564 | -0.14648 | -0.40283 | -0.27466 | -0.11902 | -0.11444 | 122.3831 | 122.4655 | 61.2854 | -122.4426 | 122.287 | 122.319 | 61.29 | -122.5891
705.3438 | 122.6715 | -61.29 | 61.2259 | 0.0054168 | -0.031971 | 0.11786 | 0.025443 | 0.052869 | -0.021817 | -0.023778 | 0.014954 | 0.0018351 | 0.041748 | 0.061348 | -0.015304 | -0.01553 | 61.2625 | -61.0886 | 0.073242 | -61.2991 | 61.2396 | -61.3037 | -61.2488 | -61.6425 | 0.064087 | -61.5738 | 61.1206 | 61.1664 | -61.1755 | -61.3586 | -0.013733 | 0.041199 | 0.013733 | 0.20142 | -0.009155 | -0.050354 | 0.036621 | 0.11444 | -0.068665 | -0.10529 | -0.35248 | -0.28381 | -0.21515 | -0.059509 | 122.5296 | 122.5525 | 61.3632 | -122.4747 | 122.4106 | 122.4564 | 61.3541 | -122.5845
707.1094 | 122.7036 | -61.2808 | 61.1572 | -0.0022127 | -0.040089 | 0.1168 | 0.024374 | 0.049238 | -0.02908 | -0.023351 | -0.0079343 | -0.0052145 | 0.040894 | 0.059212 | -0.015304 | -0.013821 | 61.2534 | -61.0703 | 0.036621 | -61.322 | 61.1069 | -61.3403 | -61.2488 | -61.647 | 0.041199 | -61.5372 | 61.0291 | 61.0611 | -61.1893 | -61.377 | -0.059509 | 0.032044 | -0.050354 | 0.21057 | -0.041198 | -0.073242 | 0.09613 | 0.091553 | -0.09613 | -0.12817 | -0.36621 | -0.25635 | -0.16022 | -0.096131 | 122.3877 | 122.5342 | 61.3174 | -122.406 | 122.3099 | 122.3419 | 61.322 | -122.5342
708.8906 | 122.7402 | -61.2854 | 61.1252 | 0.0054168 | -0.039234 | 0.11402 | 0.026297 | 0.052442 | -0.022885 | -0.023992 | 0.0073242 | -0.00094205 | 0.039826 | 0.061348 | -0.014449 | -0.014035 | 61.2762 | -61.0748 | 0.050354 | -61.2946 | 61.1114 | -61.3449 | -61.2488 | -61.5967 | 0.064087 | -61.5463 | 61.0062 | 61.0382 | -61.2213 | -61.3998 | -0.05951 | 0.036621 | -0.013733 | 0.21057 | -0.009156 | -0.045777 | 0.15106 | 0.064087 | -0.11444 | -0.11902 | -0.31128 | -0.26093 | -0.14648 | -0.086975 | 122.3969 | 122.5616 | 61.3358 | -122.374 | 122.2916 | 122.3236 | 61.3495 | -122.525
710.6094 | 122.6624 | -61.29 | 61.1893 | -0.0098417 | -0.034748 | 0.11551 | 0.027579 | 0.053724 | -0.021604 | -0.021429 | -0.0003053 | -0.00094205 | 0.04068 | 0.060707 | -0.013809 | -0.01553 | 61.2442 | -61.0931 | 0.07782 | -61.2991 | 61.2213 | -61.3174 | -61.2259 | -61.6104 | 0.09613 | -61.5646 | 61.1252 | 61.1572 | -61.1847 | -61.3678 | -0.027466 | 0.064087 | 0.032043 | 0.19684 | -0.009155 | -0.073242 | 0.054932 | 0.10529 | -0.07782 | -0.064087 | -0.32044 | -0.27466 | -0.19684 | -0.032043 | 122.5113 | 122.5342 | 61.3678 | -122.4152 | 122.4152 | 122.4472 | 61.3861 | -122.5571
712.3281 | 122.6166 | -61.3037 | 61.171 | 0.0054168 | -0.031971 | 0.1121 | 0.030997 | 0.053083 | -0.020108 | -0.021429 | 0.0073242 | 0.00055335 | 0.043457 | 0.061348 | -0.014022 | -0.014249 | 61.2946 | -61.0748 | 0.09613 | -61.3129 | 61.1893 | -61.3358 | -61.2488 | -61.6287 | 0.10529 | -61.5784 | 61.0748 | 61.1114 | -61.1664 | -61.4044 | -0.032043 | 0.054932 | 0.018311 | 0.22888 | -0.009155 | -0.064087 | 0.1236 | 0.13733 | -0.10071 | -0.09613 | -0.32501 | -0.27466 | -0.17395 | -0.059509 | 122.493 | 122.5983 | 61.3998 | -122.4197 | 122.3785 | 122.4152 | 61.409 | -122.5754
714.1094 | 122.7722 | -61.2396 | 61.1664 | -0.0022127 | -0.037525 | 0.11487 | 0.028647 | 0.05052 | -0.031644 | -0.026128 | -0.0003053 | -0.0050009 | 0.041321 | 0.059639 | -0.018295 | -0.010831 | 61.2442 | -61.0428 | 0.082397 | -61.2946 | 61.1435 | -61.3266 | -61.2076 | -61.6104 | 0.09613 | -61.4731 | 61.0657 | 61.1252 | -61.1481 | -61.3495 | -0.086975 | 0.032043 | -0.022888 | 0.19684 | -0.054932 | -0.086975 | 0.07782 | 0.091553 | -0.10986 | -0.10071 | -0.37079 | -0.23346 | -0.1236 | -0.041199 | 122.3831 | 122.4838 | 61.322 | -122.374 | 122.3053 | 122.3648 | 61.3358 | -122.5159
715.875 | 122.6898 | -61.2808 | 61.1389 | 0.0054168 | -0.040089 | 0.11445 | 0.023734 | 0.055219 | -0.025235 | -0.02506 | 0.0073242 | -0.0041465 | 0.041535 | 0.059639 | -0.014877 | -0.014676 | 61.2534 | -61.0428 | 0.054932 | -61.3037 | 61.084 | -61.3541 | -61.2259 | -61.6104 | 0.07782 | -61.5143 | 60.9741 | 61.0245 | -61.1938 | -61.3907 | -0.073242 | 0.054932 | -0.054932 | 0.23804 | -0.022888 | -0.07782 | 0.11444 | 0.086975 | -0.10986 | -0.1648 | -0.32959 | -0.23346 | -0.1236 | -0.11444 | 122.3648 | 122.5342 | 61.3358 | -122.3648 | 122.2549 | 122.3053 | 61.3586 | -122.5296
717.6562 | 122.6944 | -61.2213 | 61.1938 | 0.0054168 | -0.034962 | 0.11701 | 0.029074 | 0.051801 | -0.028226 | -0.023565 | 0.0073242 | -0.0052145 | 0.041321 | 0.060067 | -0.017654 | -0.014676 | 61.3403 | -60.9467 | 0.19226 | -61.2213 | 61.1847 | -61.2579 | -61.1938 | -61.5326 | 0.1831 | -61.4502 | 61.0748 | 61.0931 | -61.1206 | -61.3495 | -0.036622 | 0.027465 | -0.009156 | 0.27466 | 0 | -0.027465 | 0.14648 | 0.10071 | -0.12817 | -0.11902 | -0.31128 | -0.22888 | -0.10071 | -0.10071 | 122.406 | 122.5616 | 61.4136 | -122.3877 | 122.2961 | 122.3145 | 61.4044 | -122.5433
719.375 | 122.731 | -61.2854 | 61.0977 | -0.0022127 | -0.035175 | 0.11445 | 0.025656 | 0.052442 | -0.022885 | -0.024419 | -0.0003053 | 0.00012615 | 0.040894 | 0.06263 | -0.01274 | -0.01318 | 61.1984 | -61.1847 | -0.041199 | -61.3861 | 61.1343 | -61.3541 | -61.2854 | -61.6653 | -0.004578 | -61.615 | 61.0428 | 61.084 | -61.2305 | -61.4044 | -0.068665 | 0 | 0.036621 | 0.10071 | -0.10071 | -0.10071 | 0.10071 | 0.054931 | -0.11902 | -0.054931 | -0.37994 | -0.32959 | -0.21057 | -0.013733 | 122.4197 | 122.4838 | 61.2442 | -122.3831 | 122.3282 | 122.3694 | 61.2808 | -122.5021
721.1406 | 122.5845 | -61.3358 | 61.1572 | 0.0054168 | -0.035175 | 0.11316 | 0.026938 | 0.051374 | -0.019895 | -0.022069 | -0.0003053 | -0.00094205 | 0.041321 | 0.062416 | -0.014449 | -0.014249 | 61.1984 | -61.1801 | -0.022888 | -61.3632 | 61.1618 | -61.3586 | -61.2854 | -61.7111 | -0.018311 | -61.6745 | 61.0382 | 61.116 | -61.2122 | -61.4227 | -0.022889 | 0.050354 | 0.004577 | 0.15564 | -0.027466 | -0.07782 | 0.041198 | 0.1236 | -0.086975 | -0.11902 | -0.37537 | -0.33875 | -0.25177 | -0.041199 | 122.4976 | 122.5342 | 61.3129 | -122.4426 | 122.374 | 122.4518 | 61.3174 | -122.58
722.9219 | 122.5754 | -61.3358 | 61.1755 | -0.0022127 | -0.030903 | 0.11316 | 0.030142 | 0.050733 | -0.021817 | -0.021215 | 0.0073242 | -0.00030125 | 0.043671 | 0.061562 | -0.015945 | -0.013394 | 61.2488 | -61.116 | 0.068665 | -61.3174 | 61.1755 | -61.3586 | -61.235 | -61.6608 | 0.022888 | -61.6287 | 61.0611 | 61.1023 | -61.203 | -61.3998 | -0.022889 | 0.10071 | 0 | 0.21973 | 0.01831 | -0.082398 | 0.073242 | 0.13275 | -0.064087 | -0.11444 | -0.32501 | -0.29297 | -0.22888 | -0.073242 | 122.5113 | 122.5845 | 61.4044 | -122.4106 | 122.3969 | 122.438 | 61.3586 | -122.5754
724.7031 | 122.6578 | -61.3312 | 61.1298 | 0.0054168 | -0.036457 | 0.11445 | 0.024374 | 0.052442 | -0.023313 | -0.021642 | -0.0003053 | -0.00094205 | 0.040467 | 0.062416 | -0.015304 | -0.014249 | 61.1664 | -61.1938 | -0.045776 | -61.3861 | 61.1389 | -61.3586 | -61.2946 | -61.734 | -0.022888 | -61.6562 | 61.0565 | 61.0977 | -61.2305 | -61.4319 | -0.027466 | 0.036621 | 0.009155 | 0.13733 | -0.054931 | -0.091552 | 0.036621 | 0.10071 | -0.10071 | -0.073242 | -0.40283 | -0.32501 | -0.2243 | -0.032044 | 122.4701 | 122.4976 | 61.2854 | -122.4243 | 122.3877 | 122.4289 | 61.3083 | -122.5616
726.4844 | 122.7264 | -61.2122 | 61.1755 | 0.0054168 | -0.039448 | 0.11616 | 0.029074 | 0.053938 | -0.028867 | -0.023778 | 0.0073242 | -0.0056419 | 0.041107 | 0.058999 | -0.020217 | -0.012112 | 61.2808 | -60.997 | 0.12817 | -61.2579 | 61.1618 | -61.29 | -61.1893 | -61.5692 | 0.13733 | -61.4456 | 61.0382 | 61.116 | -61.1435 | -61.3174 | -0.07782 | 0.022888 | -0.013733 | 0.21515 | -0.045777 | -0.068665 | 0.10529 | 0.068664 | -0.10529 | -0.13733 | -0.35706 | -0.23346 | -0.12817 | -0.059509 | 122.374 | 122.493 | 61.3403 | -122.3648 | 122.2504 | 122.3282 | 61.3495 | -122.493
728.1875 | 122.5662 | -61.3312 | 61.1938 | 0.0054168 | -0.033466 | 0.11359 | 0.026083 | 0.05052 | -0.021176 | -0.022924 | -0.0079343 | -8.7654e-05 | 0.041962 | 0.062203 | -0.011245 | -0.014249 | 61.2625 | -61.0886 | 0.086975 | -61.2946 | 61.1664 | -61.3129 | -61.2579 | -61.647 | 0.07782 | -61.5829 | 61.0565 | 61.1298 | -61.1801 | -61.4044 | 0.018311 | 0.073242 | -0.027466 | 0.24261 | 0.036621 | -0.036621 | 0.068664 | 0.15106 | -0.073242 | -0.13733 | -0.31586 | -0.25177 | -0.17853 | -0.064087 | 122.4976 | 122.5937 | 61.4182 | -122.4518 | 122.3877 | 122.4609 | 61.409 | -122.5983
729.9688 | 122.6624 | -61.2808 | 61.1893 | 0.013046 | -0.029835 | 0.11551 | 0.02886 | 0.052442 | -0.022244 | -0.023138 | -0.0003053 | -8.7654e-05 | 0.042603 | 0.061135 | -0.015731 | -0.01318 | 61.2396 | -61.1023 | 0.086975 | -61.2854 | 61.1755 | -61.3037 | -61.2579 | -61.6058 | 0.11902 | -61.5646 | 61.0794 | 61.1572 | -61.1755 | -61.3495 | -0.022888 | 0.022888 | -0.013733 | 0.17853 | -0.004577 | -0.027465 | 0.050354 | 0.10529 | -0.068664 | -0.10986 | -0.32501 | -0.28381 | -0.21515 | -0.032043 | 122.4564 | 122.5204 | 61.3678 | -122.4472 | 122.3602 | 122.4381 | 61.3998 | -122.5388
731.7344 | 122.5891 | -61.2442 | 61.2488 | 0.0054168 | -0.035389 | 0.11509 | 0.029288 | 0.052015 | -0.025449 | -0.026983 | 0.014954 | -0.0035055 | 0.043885 | 0.059853 | -0.019576 | -0.012326 | 61.235 | -61.0886 | 0.091553 | -61.29 | 61.2122 | -61.2854 | -61.2167 | -61.6562 | 0.091553 | -61.5509 | 61.1114 | 61.2076 | -61.1526 | -61.3541 | -0.041198 | 0.027466 | -0.036621 | 0.15564 | -0.045776 | -0.073242 | -0.013733 | 0.091553 | -0.10986 | -0.13733 | -0.41199 | -0.3067 | -0.19684 | -0.041198 | 122.4564 | 122.4792 | 61.3358 | -122.4655 | 122.3557 | 122.4518 | 61.3358 | -122.6028
733.5156 | 122.6761 | -61.2488 | 61.171 | 0.0054168 | -0.039448 | 0.11551 | 0.025443 | 0.053297 | -0.030362 | -0.028905 | 0.0073242 | -0.0037191 | 0.039612 | 0.060494 | -0.018081 | -0.013608 | 61.2213 | -61.0748 | 0.036621 | -61.29 | 61.116 | -61.2991 | -61.2259 | -61.647 | 0.036621 | -61.528 | 61.0474 | 61.1114 | -61.1618 | -61.3586 | -0.050354 | 0.022888 | -0.054931 | 0.17395 | -0.041199 | -0.064087 | 0.050354 | 0.086975 | -0.10986 | -0.1236 | -0.39825 | -0.27924 | -0.16937 | -0.059509 | 122.3648 | 122.4701 | 61.2854 | -122.3969 | 122.2961 | 122.3602 | 61.2854 | -122.5296
735.2188 | 122.6486 | -61.235 | 61.1435 | -0.0022127 | -0.036884 | 0.11594 | 0.023734 | 0.050733 | -0.026944 | -0.026342 | 0.0073242 | -0.0039329 | 0.042176 | 0.059426 | -0.016372 | -0.013608 | 61.2625 | -61.0611 | 0.036621 | -61.3174 | 61.1023 | -61.3037 | -61.2579 | -61.6425 | 0.050354 | -61.5326 | 61.0062 | 61.0611 | -61.1572 | -61.377 | -0.068665 | -0.022889 | -0.041199 | 0.17395 | -0.082398 | -0.059509 | 0.11902 | 0.077819 | -0.14191 | -0.13733 | -0.40741 | -0.29755 | -0.15564 | -0.082398 | 122.3373 | 122.4976 | 61.2717 | -122.4014 | 122.2412 | 122.2961 | 61.2854 | -122.5204
737 | 122.7219 | -61.2122 | 61.1847 | 0.0054168 | -0.03603 | 0.11658 | 0.023093 | 0.053297 | -0.029721 | -0.026128 | 0.0073242 | -0.0039329 | 0.040253 | 0.059212 | -0.018722 | -0.014889 | 61.322 | -60.965 | 0.14191 | -61.2259 | 61.1618 | -61.2488 | -61.1481 | -61.5601 | 0.16479 | -61.4227 | 61.0474 | 61.1114 | -61.1298 | -61.322 | -0.036621 | 0.064087 | -0.022888 | 0.24719 | -0.013733 | -0.07782 | 0.13733 | 0.082397 | -0.10986 | -0.13733 | -0.3479 | -0.21057 | -0.10071 | -0.073242 | 122.374 | 122.5342 | 61.3541 | -122.3328 | 122.2595 | 122.3236 | 61.377 | -122.5067
738.7812 | 122.6212 | -61.2762 | 61.1847 | 0.0054168 | -0.036884 | 0.11423 | 0.026511 | 0.051374 | -0.02139 | -0.025701 | 0.0073242 | 0.00012615 | 0.041748 | 0.060921 | -0.015945 | -0.015317 | 61.2671 | -61.1069 | 0.068665 | -61.2946 | 61.2305 | -61.2854 | -61.2488 | -61.6287 | 0.082397 | -61.5738 | 61.1114 | 61.1755 | -61.1664 | -61.3541 | -0.009155 | 0.027466 | 0.045777 | 0.16937 | -0.018311 | -0.045777 | 0.082398 | 0.10986 | -0.07782 | -0.073242 | -0.35248 | -0.29755 | -0.21973 | -0.009155 | 122.5067 | 122.5433 | 61.3449 | -122.4335 | 122.3877 | 122.4518 | 61.3586 | -122.5388
740.5625 | 122.6761 | -61.2762 | 61.1481 | 0.0054168 | -0.038166 | 0.11637 | 0.023734 | 0.05052 | -0.026731 | -0.023992 | 0.0073242 | -0.0047873 | 0.040253 | 0.060921 | -0.017227 | -0.012967 | 61.2762 | -61.0474 | 0.064087 | -61.2946 | 61.0977 | -61.3083 | -61.2396 | -61.6104 | 0.059509 | -61.5143 | 60.9879 | 61.0703 | -61.2076 | -61.3998 | -0.032044 | 0.036621 | -0.050354 | 0.22888 | -0.018311 | -0.054932 | 0.12817 | 0.068664 | -0.1236 | -0.16022 | -0.33417 | -0.23804 | -0.11444 | -0.07782 | 122.374 | 122.5525 | 61.3403 | -122.3877 | 122.2641 | 122.3465 | 61.3358 | -122.5479
742.2656 | 122.7127 | -61.2396 | 61.1481 | -0.0022127 | -0.038593 | 0.1168 | 0.028647 | 0.051801 | -0.028012 | -0.024847 | 0.0073242 | -0.0062827 | 0.041748 | 0.058571 | -0.014877 | -0.01553 | 61.2396 | -61.0703 | 0.041199 | -61.3083 | 61.1023 | -61.3174 | -61.235 | -61.6562 | 0.027466 | -61.5326 | 61.0382 | 61.1069 | -61.1618 | -61.3724 | -0.07782 | 0.004578 | -0.045776 | 0.16937 | -0.068665 | -0.073243 | 0.091553 | 0.07782 | -0.13275 | -0.10986 | -0.41656 | -0.29297 | -0.16022 | -0.041198 | 122.3419 | 122.4792 | 61.2808 | -122.3831 | 122.2778 | 122.3465 | 61.2671 | -122.5204
744.0469 | 122.5891 | -61.2625 | 61.235 | -0.0022127 | -0.03603 | 0.11551 | 0.02886 | 0.051374 | -0.024594 | -0.02741 | -0.0079343 | -0.0022239 | 0.041748 | 0.058999 | -0.016158 | -0.014035 | 61.2625 | -61.0336 | 0.10986 | -61.2717 | 61.2122 | -61.2717 | -61.203 | -61.6379 | 0.073242 | -61.5463 | 61.1298 | 61.1847 | -61.1618 | -61.3358 | -0.009155 | 0.059509 | -0.022888 | 0.22888 | -0.009155 | -0.068664 | 0.027466 | 0.10071 | -0.073242 | -0.10528 | -0.37537 | -0.28381 | -0.21057 | -0.050354 | 122.4747 | 122.525 | 61.3724 | -122.438 | 122.3923 | 122.4472 | 61.3358 | -122.5708
745.8125 | 122.5937 | -61.2305 | 61.2442 | 0.0054168 | -0.036457 | 0.11551 | 0.030142 | 0.05351 | -0.025662 | -0.025487 | 0.0073242 | -0.0035055 | 0.044098 | 0.06028 | -0.018081 | -0.014249 | 61.3083 | -60.9695 | 0.17395 | -61.2213 | 61.2076 | -61.2717 | -61.1801 | -61.5921 | 0.11902 | -61.5189 | 61.0748 | 61.1389 | -61.1389 | -61.3541 | -0.041198 | 0.050354 | -0.036621 | 0.26093 | 0.009156 | -0.041198 | 0.064087 | 0.091553 | -0.1236 | -0.16937 | -0.36163 | -0.28839 | -0.16479 | -0.10529 | 122.4381 | 122.5388 | 61.4044 | -122.4243 | 122.3053 | 122.3694 | 61.3495 | -122.5983
747.5938 | 122.6257 | -61.2625 | 61.2122 | 0.0054168 | -0.035175 | 0.1153 | 0.026297 | 0.050733 | -0.020535 | -0.023565 | 0.0073242 | -0.0026511 | 0.041962 | 0.061348 | -0.014877 | -0.014249 | 61.2625 | -61.0748 | 0.07782 | -61.2854 | 61.2305 | -61.2946 | -61.2213 | -61.6058 | 0.10071 | -61.5555 | 61.0977 | 61.1389 | -61.171 | -61.3724 | -0.032044 | 0.041199 | 0.018311 | 0.18768 | -0.022888 | -0.064087 | 0.050354 | 0.091553 | -0.10986 | -0.11444 | -0.34332 | -0.29297 | -0.18311 | -0.073242 | 122.493 | 122.525 | 61.3403 | -122.4335 | 122.3602 | 122.4014 | 61.3632 | -122.5845
749.3125 | 122.6807 | -61.2854 | 61.116 | 0.0054168 | -0.036243 | 0.11722 | 0.023734 | 0.051588 | -0.025449 | -0.022069 | 0.0073242 | -0.0041465 | 0.040894 | 0.057717 | -0.016372 | -0.014249 | 61.2488 | -61.0382 | 0.054932 | -61.2946 | 61.0703 | -61.3724 | -61.2671 | -61.6058 | 0.054932 | -61.5509 | 60.9604 | 61.0153 | -61.203 | -61.409 | -0.086975 | 0.01831 | -0.045777 | 0.24719 | -0.009156 | -0.027466 | 0.13275 | 0.082397 | -0.1236 | -0.15564 | -0.32043 | -0.2655 | -0.14191 | -0.10071 | 122.3557 | 122.5342 | 61.3403 | -122.3831 | 122.2458 | 122.3007 | 61.3403 | -122.525
751.0938 | 122.5937 | -61.2305 | 61.2305 | -0.0098417 | -0.039875 | 0.11509 | 0.027579 | 0.052229 | -0.026944 | -0.02271 | 0.0073242 | -0.0037191 | 0.042389 | 0.058571 | -0.016586 | -0.014035 | 61.322 | -60.9604 | 0.17853 | -61.2167 | 61.1664 | -61.2579 | -61.171 | -61.5692 | 0.16479 | -61.4777 | 61.0794 | 61.1435 | -61.116 | -61.3449 | -0.027466 | 0.05951 | -0.064087 | 0.27008 | 0.013733 | -0.045777 | 0.091552 | 0.11444 | -0.11444 | -0.15106 | -0.33875 | -0.24719 | -0.13275 | -0.086975 | 122.3969 | 122.5525 | 61.409 | -122.4014 | 122.3099 | 122.374 | 61.3953 | -122.5754
752.7969 | 122.5845 | -61.2579 | 61.2442 | 0.013046 | -0.034748 | 0.11637 | 0.02822 | 0.05351 | -0.025449 | -0.025274 | 0.014954 | -0.0035055 | 0.04303 | 0.063057 | -0.018936 | -0.01254 | 61.322 | -60.9604 | 0.16937 | -61.2167 | 61.1664 | -61.2442 | -61.1893 | -61.5784 | 0.14191 | -61.4777 | 61.0748 | 61.1664 | -61.1526 | -61.3266 | 0.013733 | 0.068665 | -0.07782 | 0.29755 | 0.041199 | -0.027466 | 0.077819 | 0.10529 | -0.068664 | -0.16937 | -0.32043 | -0.21973 | -0.15106 | -0.07782 | 122.4243 | 122.58 | 61.4273 | -122.4335 | 122.3328 | 122.4243 | 61.3998 | -122.5708
754.5156 | 122.7173 | -61.203 | 61.1664 | 0.0054168 | -0.038166 | 0.11594 | 0.028433 | 0.050947 | -0.025876 | -0.025701 | 0.014954 | -0.0047873 | 0.043671 | 0.062203 | -0.019363 | -0.015103 | 61.3083 | -60.9879 | 0.11902 | -61.2305 | 61.1435 | -61.2854 | -61.171 | -61.5463 | 0.14648 | -61.4365 | 61.0199 | 61.1252 | -61.1114 | -61.3174 | -0.082397 | 0.032044 | -0.022888 | 0.21515 | -0.027466 | -0.05951 | 0.14191 | 0.091553 | -0.11444 | -0.14648 | -0.34332 | -0.23346 | -0.11902 | -0.041199 | 122.3465 | 122.5113 | 61.322 | -122.3373 | 122.2229 | 122.3282 | 61.3495 | -122.4838
756.2656 | 122.6532 | -61.2762 | 61.1343 | 0.0054168 | -0.032398 | 0.11359 | 0.027365 | 0.051588 | -0.017972 | -0.02271 | 0.0073242 | -0.0020103 | 0.043244 | 0.062416 | -0.012954 | -0.01553 | 61.1755 | -61.1755 | -0.050354 | -61.3586 | 61.1389 | -61.3449 | -61.2854 | -61.6882 | -0.032043 | -61.6425 | 61.0428 | 61.0611 | -61.2259 | -61.4273 | -0.068665 | -0.009155 | 0.004578 | 0.10071 | -0.082398 | -0.073243 | 0.041199 | 0.050354 | -0.15106 | -0.091552 | -0.41199 | -0.36621 | -0.21515 | -0.073242 | 122.4152 | 122.4518 | 61.2259 | -122.4197 | 122.319 | 122.3373 | 61.2442 | -122.5616
757.9844 | 122.612 | -61.2717 | 61.1389 | 0.0054168 | -0.031757 | 0.11445 | 0.027792 | 0.052015 | -0.02139 | -0.021429 | 0.0073242 | 0.00012615 | 0.042176 | 0.060494 | -0.014236 | -0.016171 | 61.2579 | -61.0611 | 0.09613 | -61.2762 | 61.1572 | -61.3083 | -61.2396 | -61.5967 | 0.11902 | -61.5417 | 61.0565 | 61.1343 | -61.1526 | -61.3724 | -0.036622 | 0.032043 | 0.018311 | 0.21057 | -0.004578 | -0.036621 | 0.11902 | 0.11902 | -0.10071 | -0.082397 | -0.32501 | -0.27008 | -0.16937 | -0.004578 | 122.4289 | 122.5296 | 61.3678 | -122.3785 | 122.3282 | 122.406 | 61.3907 | -122.5113
759.6875 | 122.7081 | -61.2991 | 61.0565 | -0.0022127 | -0.036671 | 0.11509 | 0.02587 | 0.052229 | -0.02374 | -0.021001 | 0.0073242 | -0.0024375 | 0.042603 | 0.061776 | -0.015945 | -0.014035 | 61.2122 | -61.1023 | 0.018311 | -61.3266 | 61.0886 | -61.3586 | -61.2305 | -61.6104 | 0.068665 | -61.5555 | 60.997 | 61.0016 | -61.1938 | -61.3815 | -0.05951 | 0.068664 | 0.032043 | 0.19684 | -0.027466 | -0.09613 | 0.15564 | 0.10528 | -0.082398 | -0.05951 | -0.31128 | -0.25635 | -0.17395 | -0.054932 | 122.3877 | 122.5113 | 61.3174 | -122.287 | 122.2961 | 122.3007 | 61.3678 | -122.4381
761.4688 | 122.6212 | -61.2671 | 61.1755 | 0.0054168 | -0.034107 | 0.11423 | 0.02822 | 0.054365 | -0.022031 | -0.022924 | 0.014954 | -0.0017965 | 0.042603 | 0.058999 | -0.015518 | -0.014462 | 61.2396 | -61.0565 | 0.091553 | -61.2762 | 61.1618 | -61.322 | -61.2305 | -61.5921 | 0.11444 | -61.5463 | 61.0703 | 61.1023 | -61.1664 | -61.3815 | -0.054931 | 0.036621 | -0.013733 | 0.21057 | -0.009155 | -0.045776 | 0.064087 | 0.10071 | -0.11444 | -0.10529 | -0.32501 | -0.27924 | -0.16479 | -0.073242 | 122.4289 | 122.5067 | 61.3586 | -122.406 | 122.3373 | 122.3694 | 61.3815 | -122.5571
763.1875 | 122.7036 | -61.2167 | 61.1664 | -0.0022127 | -0.037311 | 0.11573 | 0.028006 | 0.051161 | -0.030576 | -0.023778 | 0.0073242 | -0.0067099 | 0.041535 | 0.059853 | -0.01979 | -0.011899 | 61.1984 | -61.0703 | 0.041199 | -61.29 | 61.116 | -61.2808 | -61.2167 | -61.647 | 0.027466 | -61.528 | 61.0153 | 61.0977 | -61.1435 | -61.3632 | -0.064087 | 0 | -0.050354 | 0.14648 | -0.073242 | -0.073242 | 0.032043 | 0.073242 | -0.14648 | -0.15106 | -0.4303 | -0.31128 | -0.1648 | -0.068665 | 122.3328 | 122.4152 | 61.2579 | -122.3831 | 122.2321 | 122.3145 | 61.2442 | -122.5296
764.8906 | 122.7081 | -61.203 | 61.1755 | 0.0054168 | -0.035175 | 0.1168 | 0.024588 | 0.05351 | -0.030362 | -0.023565 | -0.0003053 | -0.0062827 | 0.040467 | 0.058358 | -0.018722 | -0.013608 | 61.2991 | -60.9512 | 0.17395 | -61.2122 | 61.1481 | -61.2488 | -61.1755 | -61.5372 | 0.15106 | -61.4182 | 61.0336 | 61.0748 | -61.1252 | -61.3174 | -0.045776 | 0.027466 | -0.027466 | 0.25177 | -0.009155 | -0.036621 | 0.1236 | 0.07782 | -0.11444 | -0.14191 | -0.33417 | -0.21515 | -0.10071 | -0.10071 | 122.3511 | 122.5021 | 61.377 | -122.3511 | 122.2366 | 122.2778 | 61.3541 | -122.493
766.6719 | 122.58 | -61.3083 | 61.1389 | 0.0054168 | -0.033039 | 0.11381 | 0.024802 | 0.053297 | -0.018186 | -0.02271 | -0.0003053 | -8.7654e-05 | 0.042389 | 0.061989 | -0.015304 | -0.015958 | 61.2076 | -61.1481 | 0.013733 | -61.3449 | 61.1618 | -61.3449 | -61.2671 | -61.6699 | 0 | -61.647 | 61.0291 | 61.1023 | -61.2122 | -61.3907 | -0.036621 | 0.041199 | 0.022888 | 0.16022 | -0.036621 | -0.07782 | 0.068665 | 0.096131 | -0.082397 | -0.10986 | -0.36163 | -0.33874 | -0.25635 | -0.036621 | 122.4701 | 122.5159 | 61.322 | -122.406 | 122.3373 | 122.4106 | 61.3083 | -122.5296
768.3906 | 122.6715 | -61.2671 | 61.1023 | 0.0054168 | -0.033466 | 0.11445 | 0.025229 | 0.053938 | -0.024381 | -0.024847 | 0.0073242 | -0.0026511 | 0.040467 | 0.060494 | -0.015304 | -0.01553 | 61.2579 | -61.0428 | 0.059509 | -61.2946 | 61.0565 | -61.3266 | -61.2579 | -61.5921 | 0.068665 | -61.5234 | 60.9558 | 61.0336 | -61.2122 | -61.3861 | -0.059509 | 0.009155 | -0.045776 | 0.2243 | -0.027466 | -0.036621 | 0.15564 | 0.054932 | -0.11902 | -0.14648 | -0.32501 | -0.25635 | -0.13733 | -0.068665 | 122.3236 | 122.525 | 61.3266 | -122.3602 | 122.2229 | 122.3007 | 61.3358 | -122.4884
770.1562 | 122.5433 | -61.2991 | 61.1572 | 0.013046 | -0.035389 | 0.11295 | 0.025656 | 0.054792 | -0.02139 | -0.022497 | -0.0003053 | 0.00012615 | 0.042176 | 0.062203 | -0.013381 | -0.014889 | 61.1938 | -61.1389 | 0.022888 | -61.3266 | 61.1435 | -61.3266 | -61.2854 | -61.6653 | 0.004578 | -61.6379 | 60.997 | 61.1069 | -61.1847 | -61.3724 | -0.027466 | 0.013733 | -0.013733 | 0.16022 | -0.027466 | -0.041199 | 0.036621 | 0.11444 | -0.073242 | -0.16022 | -0.36621 | -0.33875 | -0.2655 | -0.050354 | 122.4426 | 122.493 | 61.322 | -122.4426 | 122.2961 | 122.406 | 61.3037 | -122.5296
771.9219 | 122.58 | -61.2946 | 61.171 | 0.0054168 | -0.029407 | 0.11402 | 0.02886 | 0.051588 | -0.023099 | -0.020574 | -0.0003053 | -0.0022239 | 0.040894 | 0.06028 | -0.014022 | -0.015958 | 61.2671 | -61.0336 | 0.10529 | -61.2808 | 61.1755 | -61.2991 | -61.2305 | -61.5921 | 0.10986 | -61.5417 | 61.0474 | 61.1298 | -61.1481 | -61.3586 | -0.004577 | 0.064087 | 0.004578 | 0.26093 | 0.013733 | -0.050354 | 0.096131 | 0.14648 | -0.064087 | -0.1236 | -0.29755 | -0.24719 | -0.1831 | -0.041198 | 122.4701 | 122.5616 | 61.3998 | -122.4014 | 122.3419 | 122.4243 | 61.4044 | -122.5296
773.7188 | 122.644 | -61.2808 | 61.1389 | 0.013046 | -0.037525 | 0.11487 | 0.026511 | 0.050733 | -0.028867 | -0.021856 | 0.0073242 | -0.0056419 | 0.042389 | 0.059853 | -0.020217 | -0.011471 | 61.235 | -61.0291 | 0.07782 | -61.29 | 61.0657 | -61.2991 | -61.2259 | -61.6196 | 0.064087 | -61.5097 | 60.9604 | 61.0565 | -61.203 | -61.3815 | -0.01831 | 0.054932 | -0.073242 | 0.25177 | -0.009155 | -0.064087 | 0.09613 | 0.07782 | -0.10071 | -0.17853 | -0.33875 | -0.22888 | -0.12817 | -0.082397 | 122.3465 | 122.5159 | 61.3586 | -122.3648 | 122.2412 | 122.3373 | 61.3449 | -122.5204
775.5 | 122.612 | -61.2213 | 61.1847 | 0.0054168 | -0.03368 | 0.11445 | 0.029929 | 0.054792 | -0.02374 | -0.023138 | 0.014954 | -0.0020103 | 0.042176 | 0.061776 | -0.018508 | -0.014249 | 61.2076 | -61.0794 | 0.086975 | -61.2625 | 61.203 | -61.2854 | -61.2259 | -61.6104 | 0.10529 | -61.5417 | 61.0977 | 61.1481 | -61.1664 | -61.3724 | -0.064087 | -0.004578 | 0.018311 | 0.14191 | -0.041199 | -0.036621 | 0.022889 | 0.054931 | -0.15106 | -0.086975 | -0.3891 | -0.32043 | -0.16937 | -0.036621 | 122.4243 | 122.4289 | 61.3083 | -122.4106 | 122.319 | 122.3694 | 61.3266 | -122.5571
777.2031 | 122.5754 | -61.3083 | 61.1526 | -0.0098417 | -0.036671 | 0.11295 | 0.025656 | 0.051801 | -0.021604 | -0.021215 | -0.0003053 | -0.00051485 | 0.04068 | 0.062203 | -0.014877 | -0.01254 | 61.1572 | -61.1481 | -0.018311 | -61.3495 | 61.1481 | -61.3266 | -61.2808 | -61.702 | -0.013733 | -61.6425 | 61.0382 | 61.0977 | -61.2167 | -61.409 | -0.01831 | 0.027466 | -0.004578 | 0.16022 | -0.041198 | -0.068664 | 0.004578 | 0.091553 | -0.10071 | -0.11444 | -0.39368 | -0.33417 | -0.23346 | -0.054932 | 122.4564 | 122.4655 | 61.29 | -122.4335 | 122.3465 | 122.406 | 61.2946 | -122.5616
778.9844 | 122.7036 | -61.1847 | 61.1755 | 0.013046 | -0.037952 | 0.11722 | 0.029501 | 0.053083 | -0.030362 | -0.02506 | 0.0073242 | -0.0062827 | 0.041962 | 0.061562 | -0.020645 | -0.01318 | 61.3037 | -60.9421 | 0.16022 | -61.2122 | 61.1481 | -61.2488 | -61.1572 | -61.5463 | 0.16937 | -61.4044 | 61.0382 | 61.1252 | -61.1343 | -61.29 | -0.064087 | 0.027465 | -0.027466 | 0.24261 | -0.027466 | -0.054931 | 0.12817 | 0.050354 | -0.10529 | -0.13733 | -0.36163 | -0.21973 | -0.11444 | -0.050354 | 122.3328 | 122.4884 | 61.3449 | -122.3328 | 122.2229 | 122.3099 | 61.3541 | -122.4655
780.7656 | 122.5754 | -61.2946 | 61.1389 | 0.020676 | -0.033039 | 0.11338 | 0.02587 | 0.049238 | -0.021817 | -0.022069 | -0.0003053 | 0.0011941 | 0.041962 | 0.061562 | -0.013168 | -0.015103 | 61.1572 | -61.1938 | -0.064087 | -61.377 | 61.1389 | -61.3495 | -61.2762 | -61.6974 | -0.018311 | -61.6379 | 61.0519 | 61.1252 | -61.1984 | -61.4044 | -0.054931 | 0.018311 | 0 | 0.10071 | -0.082397 | -0.10071 | 0.018311 | 0.096131 | -0.10986 | -0.086975 | -0.40283 | -0.34332 | -0.23346 | -0.013733 | 122.4335 | 122.4518 | 61.2305 | -122.4152 | 122.3465 | 122.4197 | 61.2762 | -122.5433
782.5625 | 122.5754 | -61.235 | 61.2305 | -0.0022127 | -0.036243 | 0.11423 | 0.026083 | 0.055006 | -0.027158 | -0.024633 | -0.0003053 | -0.0067099 | 0.041748 | 0.059639 | -0.018508 | -0.011258 | 61.3129 | -60.9512 | 0.1831 | -61.2167 | 61.1298 | -61.2534 | -61.1389 | -61.5463 | 0.18768 | -61.4273 | 61.0657 | 61.171 | -61.1252 | -61.2991 | -0.018311 | 0.09613 | -0.10071 | 0.28381 | 0.01831 | -0.07782 | 0.082397 | 0.10986 | -0.064087 | -0.16479 | -0.31128 | -0.19226 | -0.12817 | -0.05951 | 122.3648 | 122.5479 | 61.4182 | -122.3694 | 122.3007 | 122.406 | 61.4227 | -122.5296
784.2812 | 122.6807 | -61.2213 | 61.171 | 0.0054168 | -0.03838 | 0.11829 | 0.027365 | 0.051588 | -0.029508 | -0.023992 | 0.014954 | -0.0062827 | 0.041962 | 0.059426 | -0.018508 | -0.012753 | 61.1984 | -61.0657 | 0.045776 | -61.29 | 61.1069 | -61.29 | -61.2076 | -61.6425 | 0.036621 | -61.5005 | 61.0199 | 61.084 | -61.1435 | -61.3403 | -0.068665 | 0.013732 | -0.064086 | 0.15564 | -0.068665 | -0.082397 | 0.027466 | 0.077819 | -0.11902 | -0.15106 | -0.42114 | -0.27924 | -0.16022 | -0.086975 | 122.3282 | 122.4197 | 61.2671 | -122.3785 | 122.2412 | 122.3053 | 61.2579 | -122.5113
786.0625 | 122.6669 | -61.2259 | 61.171 | 0.0054168 | -0.040729 | 0.11872 | 0.023734 | 0.052015 | -0.02844 | -0.025487 | 0.0073242 | -0.0037191 | 0.03833 | 0.061562 | -0.017013 | -0.014249 | 61.2259 | -61.0565 | 0.045776 | -61.2854 | 61.1252 | -61.2854 | -61.2167 | -61.6241 | 0.041199 | -61.5143 | 61.0153 | 61.0886 | -61.1481 | -61.3678 | -0.059509 | 0.009155 | -0.045776 | 0.16937 | -0.059509 | -0.068664 | 0.054932 | 0.07782 | -0.14191 | -0.15564 | -0.39826 | -0.28839 | -0.14648 | -0.082397 | 122.3511 | 122.4518 | 61.2717 | -122.3877 | 122.2412 | 122.3145 | 61.2671 | -122.5388
787.8281 | 122.6852 | -61.2991 | 61.0886 | 0.0054168 | -0.036243 | 0.11594 | 0.022025 | 0.052442 | -0.020749 | -0.023778 | 0.0073242 | -0.0026511 | 0.039398 | 0.059212 | -0.016158 | -0.012967 | 61.2305 | -61.0977 | 0.013733 | -61.322 | 61.0748 | -61.3083 | -61.2213 | -61.6058 | 0.050354 | -61.5372 | 60.9833 | 61.0291 | -61.2122 | -61.3815 | -0.009156 | 0.07782 | -0.013733 | 0.20142 | -0.022888 | -0.10071 | 0.14191 | 0.086975 | -0.082398 | -0.10529 | -0.3067 | -0.23804 | -0.15564 | -0.059509 | 122.374 | 122.5296 | 61.3129 | -122.3099 | 122.2824 | 122.3282 | 61.3495 | -122.4701
789.6094 | 122.7081 | -61.1984 | 61.1572 | -0.0098417 | -0.036884 | 0.11808 | 0.029929 | 0.054365 | -0.030789 | -0.024847 | 0.0073242 | -0.0045737 | 0.04303 | 0.059212 | -0.018936 | -0.012326 | 61.2396 | -61.0062 | 0.09613 | -61.2625 | 61.1343 | -61.2808 | -61.2076 | -61.5784 | 0.1236 | -61.441 | 61.0474 | 61.0748 | -61.1298 | -61.3266 | -0.082398 | -0.009156 | -0.022889 | 0.19226 | -0.064087 | -0.054931 | 0.082397 | 0.068664 | -0.12817 | -0.10986 | -0.37994 | -0.24262 | -0.11444 | -0.082398 | 122.3328 | 122.438 | 61.2946 | -122.3648 | 122.2458 | 122.2733 | 61.322 | -122.4838
791.3281 | 122.6624 | -61.1847 | 61.1938 | 0.0054168 | -0.03603 | 0.11701 | 0.027152 | 0.051588 | -0.027371 | -0.026556 | 0.0073242 | -0.0050009 | 0.040894 | 0.058999 | -0.019149 | -0.013608 | 61.322 | -60.91 | 0.18768 | -61.1984 | 61.1572 | -61.235 | -61.1847 | -61.528 | 0.17395 | -61.409 | 61.0336 | 61.084 | -61.116 | -61.3037 | -0.050354 | 0 | -0.036621 | 0.27466 | -0.013733 | -0.013733 | 0.12817 | 0.068664 | -0.11902 | -0.16022 | -0.34332 | -0.22431 | -0.10529 | -0.10986 | 122.3419 | 122.5067 | 61.3724 | -122.3785 | 122.2183 | 122.2687 | 61.3586 | -122.4976
793.1094 | 122.5891 | -61.2991 | 61.1298 | -0.0022127 | -0.036457 | 0.11252 | 0.025015 | 0.052442 | -0.021604 | -0.023778 | 0.014954 | -0.00094205 | 0.041962 | 0.060707 | -0.013595 | -0.013821 | 61.1389 | -61.1847 | -0.036621 | -61.3632 | 61.1298 | -61.3358 | -61.2534 | -61.6745 | -0.041199 | -61.6516 | 61.0382 | 61.0565 | -61.2076 | -61.4227 | -0.036621 | 0.045776 | 0 | 0.11444 | -0.064087 | -0.10986 | 0.009155 | 0.091552 | -0.1236 | -0.091553 | -0.37537 | -0.35248 | -0.22888 | -0.073242 | 122.4289 | 122.438 | 61.2625 | -122.3831 | 122.3373 | 122.3557 | 61.2579 | -122.5525
794.8906 | 122.5616 | -61.2442 | 61.1664 | 0.0054168 | -0.029835 | 0.11445 | 0.026297 | 0.052229 | -0.020535 | -0.022924 | 0.014954 | -0.0022239 | 0.040894 | 0.059853 | -0.01509 | -0.014249 | 61.2534 | -61.0474 | 0.09613 | -61.2625 | 61.1572 | -61.3037 | -61.2442 | -61.5784 | 0.10529 | -61.5463 | 61.0382 | 61.1023 | -61.1343 | -61.3586 | -0.059509 | 0 | -0.009155 | 0.19684 | -0.01831 | -0.01831 | 0.086975 | 0.10986 | -0.11444 | -0.12817 | -0.33417 | -0.30212 | -0.18768 | -0.064087 | 122.4014 | 122.4976 | 61.3403 | -122.4106 | 122.2824 | 122.3465 | 61.3495 | -122.525
796.6562 | 122.5616 | -61.2717 | 61.2213 | -0.0022127 | -0.035175 | 0.11744 | 0.030783 | 0.049879 | -0.024167 | -0.024847 | -0.0003053 | -0.0017965 | 0.04068 | 0.058571 | -0.019149 | -0.012753 | 61.2122 | -61.0519 | 0.10071 | -61.29 | 61.1938 | -61.2717 | -61.1984 | -61.615 | 0.073242 | -61.528 | 61.1114 | 61.1618 | -61.1298 | -61.3129 | 0 | 0.073242 | -0.027465 | 0.21973 | -0.018311 | -0.091553 | -0.009155 | 0.14191 | -0.041199 | -0.10986 | -0.34332 | -0.25635 | -0.21515 | -0.059509 | 122.4655 | 122.4838 | 61.3724 | -122.4197 | 122.3831 | 122.4335 | 61.3449 | -122.5342
798.4219 | 122.5616 | -61.2259 | 61.235 | 0.0054168 | -0.035816 | 0.11616 | 0.02886 | 0.052015 | -0.026944 | -0.024847 | 0.0073242 | -0.0024375 | 0.042816 | 0.061135 | -0.017013 | -0.014249 | 61.2488 | -61.0016 | 0.13733 | -61.235 | 61.1801 | -61.2534 | -61.1801 | -61.6104 | 0.09613 | -61.528 | 61.0794 | 61.1389 | -61.1252 | -61.3449 | -0.027466 | 0.045776 | -0.054931 | 0.2243 | -0.009155 | -0.054931 | 0.013733 | 0.10071 | -0.11902 | -0.15564 | -0.38452 | -0.30212 | -0.18311 | -0.09613 | 122.406 | 122.4747 | 61.3632 | -122.4152 | 122.3053 | 122.3648 | 61.322 | -122.58
800.1406 | 122.6715 | -61.2854 | 61.0931 | 0.013046 | -0.034534 | 0.11338 | 0.02886 | 0.050092 | -0.022244 | -0.021642 | -0.0003053 | -0.0015829 | 0.043671 | 0.061989 | -0.01509 | -0.014676 | 61.1664 | -61.1435 | -0.036621 | -61.3495 | 61.1343 | -61.3449 | -61.2717 | -61.6699 | -0.027466 | -61.6058 | 61.0062 | 61.084 | -61.1938 | -61.4136 | -0.05951 | 0.013733 | 0.041198 | 0.14191 | -0.064087 | -0.07782 | 0.073242 | 0.091552 | -0.12817 | -0.086975 | -0.38452 | -0.32043 | -0.19226 | -0.009156 | 122.4197 | 122.4518 | 61.2488 | -122.3648 | 122.2916 | 122.3694 | 61.2579 | -122.5067
801.9219 | 122.5479 | -61.2259 | 61.2122 | 0.013046 | -0.032612 | 0.11487 | 0.028006 | 0.051801 | -0.02609 | -0.022924 | 0.0073242 | -0.0022239 | 0.041535 | 0.060707 | -0.017654 | -0.014249 | 61.2488 | -61.0153 | 0.10986 | -61.2625 | 61.1938 | -61.2442 | -61.1847 | -61.6241 | 0.07782 | -61.5143 | 61.1069 | 61.1572 | -61.1298 | -61.3174 | -0.018311 | 0.041199 | -0.01831 | 0.21057 | -0.036621 | -0.07782 | 0.036621 | 0.09613 | -0.091553 | -0.10529 | -0.39826 | -0.28839 | -0.19684 | -0.054931 | 122.4197 | 122.4747 | 61.3358 | -122.3969 | 122.3328 | 122.3831 | 61.3037 | -122.5296
803.7031 | 122.6715 | -61.2122 | 61.1618 | 0.0054168 | -0.040729 | 0.11722 | 0.027579 | 0.053083 | -0.028867 | -0.025915 | 0.0073242 | -0.0045737 | 0.040467 | 0.058571 | -0.018081 | -0.011685 | 61.1984 | -61.0199 | 0.07782 | -61.2762 | 61.1389 | -61.29 | -61.2122 | -61.5738 | 0.10071 | -61.4594 | 61.0382 | 61.0748 | -61.1298 | -61.3312 | -0.07782 | 0 | -0.022888 | 0.19226 | -0.064087 | -0.064087 | 0.036621 | 0.082397 | -0.11902 | -0.1236 | -0.36163 | -0.24719 | -0.12817 | -0.086975 | 122.3511 | 122.4106 | 61.29 | -122.374 | 122.2504 | 122.287 | 61.3129 | -122.493
805.4844 | 122.6028 | -61.3312 | 61.1114 | 0.013046 | -0.035389 | 0.11466 | 0.022238 | 0.053297 | -0.021176 | -0.024419 | -0.0003053 | -0.0026511 | 0.041535 | 0.061989 | -0.014236 | -0.012112 | 61.1618 | -61.1801 | -0.041199 | -61.3449 | 61.1252 | -61.3495 | -61.2625 | -61.6699 | -0.041199 | -61.6379 | 61.0382 | 61.0886 | -61.203 | -61.3907 | -0.01831 | 0.068665 | 0.013733 | 0.15106 | -0.013733 | -0.082398 | 0.050354 | 0.12817 | -0.059509 | -0.073242 | -0.33875 | -0.3067 | -0.24719 | -0.022888 | 122.4564 | 122.493 | 61.29 | -122.374 | 122.3694 | 122.4197 | 61.29 | -122.5021
807.1875 | 122.6807 | -61.2442 | 61.0977 | 0.013046 | -0.038166 | 0.11445 | 0.026724 | 0.052656 | -0.024381 | -0.023351 | 0.0073242 | -0.0024375 | 0.042176 | 0.060707 | -0.014663 | -0.014035 | 61.1801 | -61.1023 | -0.009155 | -61.322 | 61.1023 | -61.3449 | -61.2442 | -61.6104 | 0.068665 | -61.5555 | 60.9695 | 61.0291 | -61.1938 | -61.3632 | -0.10071 | 0 | 0.004578 | 0.14191 | -0.077819 | -0.077819 | 0.082398 | 0.050354 | -0.11902 | -0.12817 | -0.36621 | -0.31128 | -0.19226 | -0.068664 | 122.3465 | 122.4243 | 61.235 | -122.3419 | 122.2137 | 122.2733 | 61.3129 | -122.4609
808.9531 | 122.6715 | -61.203 | 61.1481 | 0.0054168 | -0.039875 | 0.11786 | 0.027792 | 0.053083 | -0.029935 | -0.02506 | -0.0003053 | -0.0030783 | 0.039612 | 0.059853 | -0.020858 | -0.0099763 | 61.2305 | -61.0062 | 0.073242 | -61.2442 | 61.1389 | -61.2854 | -61.1893 | -61.5829 | 0.10529 | -61.441 | 61.0062 | 61.1206 | -61.1114 | -61.3083 | -0.082397 | 0.013733 | -0.009155 | 0.19684 | -0.041199 | -0.054932 | 0.082398 | 0.091553 | -0.10529 | -0.14191 | -0.37994 | -0.23804 | -0.13275 | -0.027466 | 122.3419 | 122.4335 | 61.2762 | -122.3373 | 122.2092 | 122.3236 | 61.3083 | -122.4564
810.6719 | 122.6532 | -61.2213 | 61.1618 | -0.0098417 | -0.039661 | 0.1153 | 0.025656 | 0.05351 | -0.029294 | -0.026556 | -0.0003053 | -0.0028647 | 0.040253 | 0.05793 | -0.017654 | -0.011685 | 61.2167 | -61.0474 | 0.050354 | -61.2717 | 61.1069 | -61.2579 | -61.2122 | -61.6287 | 0.036621 | -61.5326 | 61.0199 | 61.0977 | -61.1252 | -61.3358 | -0.036622 | 0.009155 | -0.054931 | 0.17395 | -0.050354 | -0.059509 | 0.054932 | 0.09613 | -0.11444 | -0.14191 | -0.40741 | -0.31128 | -0.19684 | -0.064087 | 122.3282 | 122.438 | 61.2717 | -122.374 | 122.2412 | 122.319 | 61.2579 | -122.4976
812.375 | 122.6624 | -61.2579 | 61.0748 | 0.0054168 | -0.034748 | 0.11487 | 0.027365 | 0.051161 | -0.02139 | -0.02271 | 0.0073242 | -0.00030125 | 0.042603 | 0.061989 | -0.014449 | -0.013821 | 61.1801 | -61.1481 | -0.036621 | -61.3541 | 61.1114 | -61.3403 | -61.2717 | -61.615 | 0.009155 | -61.5692 | 60.9833 | 61.0336 | -61.1755 | -61.4044 | -0.082397 | -0.013732 | 0.036621 | 0.10986 | -0.09613 | -0.082398 | 0.10529 | 0.082398 | -0.14648 | -0.091553 | -0.35705 | -0.31128 | -0.1648 | -0.041199 | 122.3694 | 122.4381 | 61.2213 | -122.3465 | 122.2412 | 122.2916 | 61.2671 | -122.4792
814.1094 | 122.6807 | -61.2717 | 61.0748 | -0.0022127 | -0.035389 | 0.11466 | 0.025656 | 0.052869 | -0.024594 | -0.023351 | 0.0073242 | -0.0030783 | 0.040894 | 0.060921 | -0.014236 | -0.01318 | 61.2076 | -61.0886 | 0 | -61.3129 | 61.0931 | -61.3083 | -61.2579 | -61.5967 | 0.036621 | -61.528 | 60.9741 | 61.0245 | -61.1801 | -61.3861 | -0.036622 | 0.013732 | 0.018311 | 0.1831 | -0.041199 | -0.054931 | 0.13275 | 0.091552 | -0.11444 | -0.10071 | -0.32501 | -0.25635 | -0.14191 | -0.050354 | 122.3648 | 122.4792 | 61.2717 | -122.3328 | 122.2458 | 122.2961 | 61.3083 | -122.4609
815.8281 | 122.6303 | -61.2579 | 61.1069 | 0.013046 | -0.037098 | 0.11316 | 0.026083 | 0.052869 | -0.023526 | -0.022924 | 0.0073242 | -0.0026511 | 0.04068 | 0.061989 | -0.014449 | -0.013608 | 61.2396 | -61.0245 | 0.059509 | -61.2717 | 61.0519 | -61.2808 | -61.2259 | -61.5829 | 0.068665 | -61.5143 | 60.9421 | 61.0016 | -61.1847 | -61.3678 | -0.022888 | 0.032044 | -0.054932 | 0.23346 | -0.013732 | -0.045776 | 0.13275 | 0.073243 | -0.10986 | -0.16479 | -0.32501 | -0.25635 | -0.14648 | -0.10529 | 122.3099 | 122.4976 | 61.3174 | -122.3328 | 122.2 | 122.2595 | 61.3266 | -122.4747
817.5469 | 122.6807 | -61.1938 | 61.1481 | -0.0022127 | -0.038166 | 0.11594 | 0.028647 | 0.053724 | -0.028653 | -0.025487 | -0.0003053 | -0.0062827 | 0.042389 | 0.059639 | -0.017867 | -0.014035 | 61.2488 | -60.9879 | 0.11444 | -61.235 | 61.1023 | -61.2579 | -61.1847 | -61.5417 | 0.12817 | -61.4273 | 61.0291 | 61.0657 | -61.1023 | -61.2991 | -0.064087 | 0.009156 | -0.045776 | 0.20599 | -0.041198 | -0.050354 | 0.10071 | 0.091553 | -0.10528 | -0.11902 | -0.3479 | -0.23346 | -0.12817 | -0.082397 | 122.2961 | 122.4426 | 61.3083 | -122.3328 | 122.2229 | 122.2595 | 61.322 | -122.4472
819.2656 | 122.6761 | -61.2762 | 61.0657 | -0.0022127 | -0.037098 | 0.11274 | 0.024588 | 0.050733 | -0.020535 | -0.023778 | -0.0003053 | -0.0015829 | 0.040467 | 0.061989 | -0.013381 | -0.015317 | 61.203 | -61.0931 | 0.013733 | -61.3129 | 61.0794 | -61.3174 | -61.235 | -61.5784 | 0.054932 | -61.528 | 60.9741 | 61.0153 | -61.1893 | -61.3541 | -0.041199 | 0.041199 | 0.013733 | 0.18311 | -0.036621 | -0.07782 | 0.13733 | 0.086975 | -0.07782 | -0.091553 | -0.30212 | -0.25177 | -0.17395 | -0.050354 | 122.3557 | 122.4792 | 61.29 | -122.3007 | 122.2504 | 122.2916 | 61.3312 | -122.4197
821.0469 | 122.5754 | -61.2305 | 61.1618 | 0.0054168 | -0.03368 | 0.11381 | 0.02886 | 0.05351 | -0.022244 | -0.023778 | 0.0073242 | 0.0018351 | 0.041962 | 0.062203 | -0.018081 | -0.01553 | 61.2305 | -61.0794 | 0.082397 | -61.2625 | 61.2076 | -61.2671 | -61.2122 | -61.615 | 0.073242 | -61.5509 | 61.084 | 61.1481 | -61.1114 | -61.322 | -0.036621 | 0.018311 | 0.045777 | 0.15106 | -0.032043 | -0.050354 | 0.068665 | 0.11902 | -0.091552 | -0.07782 | -0.38452 | -0.32043 | -0.22888 | -0.013733 | 122.4381 | 122.4609 | 61.3129 | -122.374 | 122.3145 | 122.3785 | 61.3037 | -122.4838
822.8125 | 122.5525 | -61.2213 | 61.1755 | 0.0054168 | -0.033466 | 0.11509 | 0.028006 | 0.052015 | -0.025022 | -0.024633 | -0.0003053 | -0.0022239 | 0.04303 | 0.061562 | -0.018936 | -0.014035 | 61.235 | -61.0565 | 0.09613 | -61.2717 | 61.203 | -61.2396 | -61.1664 | -61.6104 | 0.09613 | -61.528 | 61.0931 | 61.1847 | -61.0794 | -61.3358 | -0.018311 | 0.054931 | 0.027466 | 0.16479 | -0.050354 | -0.10529 | 0.059509 | 0.14191 | -0.11444 | -0.082397 | -0.3891 | -0.3067 | -0.19226 | 0.009155 | 122.4243 | 122.4564 | 61.3174 | -122.3419 | 122.3145 | 122.406 | 61.3174 | -122.5113
824.5938 | 122.612 | -61.2167 | 61.1389 | 0.013046 | -0.03603 | 0.11423 | 0.022452 | 0.053724 | -0.027371 | -0.023138 | 0.0073242 | -0.0062827 | 0.042389 | 0.060921 | -0.016158 | -0.013394 | 61.235 | -61.0199 | 0.082397 | -61.2671 | 61.0519 | -61.3037 | -61.1984 | -61.5784 | 0.086975 | -61.4777 | 60.9375 | 61.0519 | -61.1435 | -61.3586 | -0.086975 | 0.018311 | -0.086975 | 0.19684 | -0.050354 | -0.068665 | 0.09613 | 0.073242 | -0.14191 | -0.20142 | -0.36163 | -0.26093 | -0.11902 | -0.086975 | 122.2687 | 122.4518 | 61.2991 | -122.3373 | 122.1542 | 122.2687 | 61.3037 | -122.4976
826.375 | 122.5433 | -61.2762 | 61.1526 | -0.0022127 | -0.037525 | 0.1168 | 0.023093 | 0.053724 | -0.020535 | -0.024419 | 0.0073242 | -0.0011557 | 0.040467 | 0.059426 | -0.012313 | -0.013394 | 61.2534 | -61.0336 | 0.09613 | -61.2625 | 61.1343 | -61.2808 | -61.2076 | -61.5967 | 0.091553 | -61.5555 | 61.0107 | 61.0977 | -61.171 | -61.3495 | -0.004578 | 0.068664 | -0.018311 | 0.24262 | 0.013733 | -0.054931 | 0.10071 | 0.10529 | -0.073242 | -0.14191 | -0.32043 | -0.27924 | -0.20599 | -0.054932 | 122.4106 | 122.5296 | 61.3724 | -122.3602 | 122.287 | 122.374 | 61.3678 | -122.5021
828.0938 | 122.5845 | -61.2396 | 61.1664 | 0.0054168 | -0.034534 | 0.11509 | 0.02886 | 0.052015 | -0.023526 | -0.023992 | 0.0073242 | -0.0020103 | 0.041535 | 0.061989 | -0.016158 | -0.012967 | 61.2122 | -61.0611 | 0.068665 | -61.2396 | 61.1984 | -61.2854 | -61.1847 | -61.5875 | 0.10071 | -61.528 | 61.0794 | 61.1435 | -61.1343 | -61.322 | -0.045776 | 0.054932 | 0.032043 | 0.17853 | 0 | -0.054932 | 0.045776 | 0.10529 | -0.082397 | -0.086975 | -0.3479 | -0.28839 | -0.20599 | -0.022888 | 122.438 | 122.4518 | 61.3083 | -122.3511 | 122.319 | 122.3831 | 61.3403 | -122.4884
829.8594 | 122.5204 | -61.2076 | 61.2259 | -0.0022127 | -0.035602 | 0.11851 | 0.029501 | 0.053083 | -0.028867 | -0.025487 | 0.014954 | -0.0035055 | 0.043244 | 0.058571 | -0.017654 | -0.01318 | 61.2488 | -60.997 | 0.13275 | -61.2488 | 61.171 | -61.2579 | -61.171 | -61.6104 | 0.091553 | -61.5097 | 61.0977 | 61.1618 | -61.1389 | -61.3037 | -0.050354 | 0.036622 | -0.054932 | 0.21057 | -0.041198 | -0.07782 | 0.022888 | 0.068665 | -0.09613 | -0.12817 | -0.40283 | -0.30212 | -0.20599 | -0.064087 | 122.3785 | 122.4564 | 61.3403 | -122.3969 | 122.3053 | 122.3694 | 61.2991 | -122.5296
831.6406 | 122.6349 | -61.2213 | 61.1526 | 0.013046 | -0.040516 | 0.11637 | 0.025656 | 0.051374 | -0.029294 | -0.023778 | 0.0073242 | -0.0028647 | 0.040039 | 0.059212 | -0.018081 | -0.011899 | 61.1893 | -61.0291 | 0.036621 | -61.2717 | 61.0931 | -61.2717 | -61.1893 | -61.6287 | 0.041199 | -61.5005 | 60.997 | 61.0748 | -61.1298 | -61.3449 | -0.050354 | 0.032043 | -0.059509 | 0.19226 | -0.050354 | -0.082397 | 0.036621 | 0.091552 | -0.1236 | -0.15564 | -0.40741 | -0.27924 | -0.15564 | -0.07782 | 122.3145 | 122.4106 | 61.2579 | -122.3419 | 122.2183 | 122.2961 | 61.2625 | -122.4976
833.4062 | 122.6578 | -61.2442 | 61.0886 | 0.013046 | -0.036671 | 0.11487 | 0.024161 | 0.049024 | -0.022458 | -0.024419 | 0.0073242 | -0.00094205 | 0.040253 | 0.059212 | -0.014449 | -0.012967 | 61.2305 | -61.0336 | 0.032043 | -61.2808 | 61.0565 | -61.3083 | -61.2305 | -61.5829 | 0.073242 | -61.5051 | 60.9329 | 61.0016 | -61.1984 | -61.3632 | -0.064087 | 0.013733 | -0.032043 | 0.21057 | -0.036621 | -0.050354 | 0.14191 | 0.045777 | -0.11902 | -0.15564 | -0.33874 | -0.26093 | -0.14191 | -0.086975 | 122.3007 | 122.4747 | 61.2762 | -122.319 | 122.1771 | 122.2458 | 61.3174 | -122.4518
835.1094 | 122.5708 | -61.2442 | 61.1847 | 0.0054168 | -0.034962 | 0.11509 | 0.029501 | 0.052869 | -0.02374 | -0.024633 | 0.014954 | -0.0020103 | 0.043885 | 0.059639 | -0.017227 | -0.013608 | 61.2259 | -61.0565 | 0.086975 | -61.2579 | 61.1984 | -61.2717 | -61.1847 | -61.6196 | 0.07782 | -61.5417 | 61.0748 | 61.1481 | -61.1114 | -61.3358 | -0.027465 | 0.05951 | 0.013733 | 0.18768 | -0.013733 | -0.073243 | 0.041199 | 0.13275 | -0.091552 | -0.10986 | -0.37537 | -0.29755 | -0.20599 | -0.036621 | 122.4426 | 122.4701 | 61.3312 | -122.3694 | 122.319 | 122.3923 | 61.322 | -122.5204
836.8906 | 122.6852 | -61.1801 | 61.1481 | 0.013046 | -0.03902 | 0.11701 | 0.030997 | 0.051588 | -0.029294 | -0.024419 | 0.0073242 | -0.0047873 | 0.043671 | 0.059426 | -0.01979 | -0.014889 | 61.2488 | -60.9879 | 0.10071 | -61.2305 | 61.1389 | -61.2442 | -61.1755 | -61.5417 | 0.13733 | -61.4273 | 61.0336 | 61.1069 | -61.0886 | -61.2854 | -0.064087 | 0.004578 | -0.009155 | 0.19226 | -0.050354 | -0.054932 | 0.10071 | 0.091553 | -0.10529 | -0.11444 | -0.36163 | -0.24719 | -0.14191 | -0.041198 | 122.319 | 122.4289 | 61.2808 | -122.3236 | 122.2137 | 122.287 | 61.3174 | -122.4335
838.6094 | 122.6761 | -61.1984 | 61.1252 | 0.013046 | -0.038166 | 0.11402 | 0.026938 | 0.051588 | -0.029294 | -0.024847 | 0.0073242 | -0.0058555 | 0.039612 | 0.060921 | -0.018722 | -0.012753 | 61.2076 | -61.0245 | 0.082397 | -61.2534 | 61.1206 | -61.2579 | -61.1664 | -61.5829 | 0.091553 | -61.441 | 60.9833 | 61.084 | -61.1252 | -61.2991 | -0.05951 | 0.032043 | -0.004578 | 0.17395 | -0.054932 | -0.086975 | 0.082398 | 0.073242 | -0.10071 | -0.14191 | -0.38452 | -0.24262 | -0.14191 | -0.041199 | 122.319 | 122.406 | 61.2808 | -122.2916 | 122.1817 | 122.2824 | 61.29 | -122.4243
840.3125 | 122.5662 | -61.2305 | 61.1526 | -0.0022127 | -0.032398 | 0.11338 | 0.026511 | 0.052442 | -0.02139 | -0.022283 | -0.0003053 | -0.00072845 | 0.041535 | 0.061989 | -0.013381 | -0.016812 | 61.2534 | -61.0336 | 0.091553 | -61.2442 | 61.1481 | -61.2808 | -61.203 | -61.5555 | 0.10071 | -61.5143 | 61.0565 | 61.0977 | -61.1298 | -61.3358 | -0.050354 | 0.027466 | -0.004578 | 0.19684 | -0.013733 | -0.041199 | 0.10071 | 0.10071 | -0.10529 | -0.09613 | -0.32501 | -0.28381 | -0.17853 | -0.054932 | 122.3785 | 122.4838 | 61.322 | -122.3557 | 122.287 | 122.3282 | 61.3312 | -122.4884
842.0312 | 122.5983 | -61.2534 | 61.1389 | 0.028305 | -0.036671 | 0.11487 | 0.026938 | 0.049665 | -0.026731 | -0.025487 | 0.0073242 | -0.0041465 | 0.040039 | 0.061776 | -0.018508 | -0.013394 | 61.2305 | -61.0153 | 0.064087 | -61.2717 | 61.0748 | -61.2808 | -61.203 | -61.5875 | 0.041199 | -61.5097 | 60.997 | 61.0519 | -61.1618 | -61.3586 | -0.027466 | 0.050354 | -0.064087 | 0.23804 | -0.01831 | -0.068664 | 0.091553 | 0.091553 | -0.10529 | -0.14191 | -0.33417 | -0.25635 | -0.15106 | -0.086975 | 122.3282 | 122.4838 | 61.3174 | -122.3419 | 122.2504 | 122.3053 | 61.2946 | -122.4976
843.8125 | 122.5845 | -61.2808 | 61.1023 | -0.0022127 | -0.033466 | 0.11445 | 0.023947 | 0.053297 | -0.020322 | -0.022497 | -0.0003053 | 0.00012615 | 0.04303 | 0.061989 | -0.014236 | -0.015103 | 61.1389 | -61.1481 | -0.041199 | -61.3358 | 61.1343 | -61.3129 | -61.235 | -61.647 | -0.018311 | -61.6104 | 61.0291 | 61.0657 | -61.2122 | -61.377 | -0.032043 | 0.045777 | 0.032043 | 0.13275 | -0.054931 | -0.10071 | 0.036621 | 0.068665 | -0.09613 | -0.073242 | -0.36621 | -0.32959 | -0.23346 | -0.036621 | 122.4152 | 122.4197 | 61.2396 | -122.3373 | 122.3099 | 122.3465 | 61.2625 | -122.4792
845.6094 | 122.6486 | -61.2625 | 61.0565 | 0.0054168 | -0.034321 | 0.11594 | 0.026083 | 0.051801 | -0.021817 | -0.02036 | 0.022583 | 0.00033975 | 0.039398 | 0.061776 | -0.013595 | -0.012326 | 61.171 | -61.1252 | -0.045776 | -61.3358 | 61.1114 | -61.3312 | -61.2625 | -61.6425 | -0.018311 | -61.5875 | 60.997 | 61.0382 | -61.1801 | -61.3815 | -0.068665 | 0 | 0.054931 | 0.13733 | -0.073242 | -0.073242 | 0.11444 | 0.082397 | -0.11902 | -0.05951 | -0.37994 | -0.32501 | -0.20599 | -0.018311 | 122.374 | 122.4335 | 61.2167 | -122.319 | 122.2595 | 122.3007 | 61.2442 | -122.4381
847.3125 | 122.6486 | -61.1893 | 61.1435 | 0.0054168 | -0.038593 | 0.11872 | 0.025443 | 0.053938 | -0.028653 | -0.023565 | 0.0073242 | -0.0058555 | 0.040039 | 0.058358 | -0.018722 | -0.012112 | 61.1984 | -60.9879 | 0.068665 | -61.2396 | 61.1114 | -61.2396 | -61.1893 | -61.5738 | 0.086975 | -61.4456 | 61.0199 | 61.0611 | -61.116 | -61.2854 | -0.050354 | 0 | -0.032044 | 0.20142 | -0.050354 | -0.050354 | 0.054931 | 0.073242 | -0.09613 | -0.1236 | -0.38452 | -0.25635 | -0.16022 | -0.082398 | 122.3007 | 122.3877 | 61.2579 | -122.3328 | 122.2092 | 122.2504 | 61.2762 | -122.4289
849.0938 | 122.5479 | -61.2122 | 61.1664 | -0.0022127 | -0.035175 | 0.11402 | 0.027579 | 0.051161 | -0.025876 | -0.02506 | -0.0003053 | -0.00051485 | 0.042816 | 0.061348 | -0.017654 | -0.01318 | 61.2259 | -61.0336 | 0.10986 | -61.2534 | 61.1938 | -61.2579 | -61.1526 | -61.6013 | 0.068665 | -61.5143 | 61.1114 | 61.1481 | -61.116 | -61.322 | -0.045777 | 0.059509 | 0.027466 | 0.17853 | -0.041199 | -0.10071 | 0.059509 | 0.09613 | -0.10986 | -0.054932 | -0.3891 | -0.30212 | -0.19226 | -0.018311 | 122.406 | 122.438 | 61.322 | -122.319 | 122.3236 | 122.3602 | 61.2808 | -122.4884
850.875 | 122.6212 | -61.203 | 61.1023 | 0.0054168 | -0.040089 | 0.11765 | 0.026938 | 0.053938 | -0.027158 | -0.023778 | 0.0073242 | -0.0056419 | 0.041321 | 0.059426 | -0.018081 | -0.011685 | 61.203 | -61.0199 | 0.054932 | -61.2717 | 61.1023 | -61.2488 | -61.1938 | -61.6104 | 0.045776 | -61.5051 | 60.997 | 61.0474 | -61.1343 | -61.3312 | -0.045776 | 0.009155 | 0 | 0.18311 | -0.068664 | -0.077819 | 0.10071 | 0.068665 | -0.12817 | -0.10529 | -0.40741 | -0.30212 | -0.17395 | -0.054932 | 122.3053 | 122.406 | 61.2579 | -122.2961 | 122.2 | 122.2504 | 61.2488 | -122.4335
852.6406 | 122.5937 | -61.2396 | 61.1206 | -0.0022127 | -0.042011 | 0.11466 | 0.026083 | 0.052442 | -0.025662 | -0.02271 | 0.0073242 | -0.0047873 | 0.040467 | 0.057717 | -0.014236 | -0.013608 | 61.2167 | -60.9879 | 0.068665 | -61.2671 | 61.0886 | -61.2625 | -61.1938 | -61.6013 | 0.050354 | -61.5005 | 60.9924 | 61.0291 | -61.1298 | -61.3266 | -0.022888 | 0.045776 | -0.032043 | 0.25177 | -0.027466 | -0.073242 | 0.096131 | 0.10986 | -0.086975 | -0.12817 | -0.36163 | -0.26093 | -0.17395 | -0.091552 | 122.3282 | 122.4564 | 61.3083 | -122.3145 | 122.2321 | 122.2687 | 61.29 | -122.4472
854.3594 | 122.5754 | -61.203 | 61.1801 | 0.0054168 | -0.037098 | 0.11423 | 0.02822 | 0.050947 | -0.021604 | -0.025487 | 0.0073242 | -8.7654e-05 | 0.041107 | 0.061989 | -0.014663 | -0.014676 | 61.2076 | -61.0382 | 0.073242 | -61.2579 | 61.1984 | -61.2671 | -61.1893 | -61.6013 | 0.07782 | -61.5372 | 61.0748 | 61.1389 | -61.1343 | -61.3083 | -0.064087 | 0.013733 | 0.01831 | 0.1648 | -0.054932 | -0.068665 | 0.027466 | 0.068665 | -0.10529 | -0.10529 | -0.39825 | -0.33417 | -0.22888 | -0.041199 | 122.4014 | 122.4106 | 61.2762 | -122.3694 | 122.2778 | 122.3419 | 61.2808 | -122.4884
856.1719 | 122.525 | -61.2717 | 61.1526 | -0.0098417 | -0.034748 | 0.11381 | 0.027152 | 0.052869 | -0.020963 | -0.023992 | -0.0003053 | -0.00030125 | 0.041748 | 0.060921 | -0.014449 | -0.014462 | 61.2625 | -61.0107 | 0.10071 | -61.2396 | 61.1664 | -61.2762 | -61.1938 | -61.5555 | 0.09613 | -61.5326 | 61.0062 | 61.0886 | -61.1343 | -61.3266 | -0.004578 | 0.077819 | 0.013733 | 0.26093 | 0.032043 | -0.045776 | 0.10986 | 0.13733 | -0.054932 | -0.14648 | -0.28381 | -0.26093 | -0.20599 | -0.064087 | 122.438 | 122.5342 | 61.3724 | -122.3465 | 122.2778 | 122.3602 | 61.3678 | -122.4792
857.875 | 122.5113 | -61.2671 | 61.1389 | 0.013046 | -0.033039 | 0.11359 | 0.029288 | 0.053938 | -0.021176 | -0.02271 | 0.014954 | -0.00051485 | 0.041748 | 0.062203 | -0.014877 | -0.01254 | 61.235 | -61.0245 | 0.10986 | -61.2442 | 61.1069 | -61.2854 | -61.1938 | -61.5738 | 0.091553 | -61.5417 | 61.0474 | 61.0886 | -61.1389 | -61.3403 | -0.01831 | 0.073242 | -0.032043 | 0.24262 | 0.022888 | -0.050354 | 0.09613 | 0.12817 | -0.073242 | -0.091553 | -0.3067 | -0.27466 | -0.20142 | -0.050354 | 122.374 | 122.5021 | 61.377 | -122.3328 | 122.3145 | 122.3557 | 61.3586 | -122.4792
859.6406 | 122.644 | -61.2534 | 61.0611 | -0.0022127 | -0.037098 | 0.11637 | 0.026297 | 0.054365 | -0.027158 | -0.01972 | -0.0003053 | -0.0020103 | 0.037903 | 0.059639 | -0.016586 | -0.013821 | 61.1847 | -61.0062 | 0.054932 | -61.2717 | 61.0657 | -61.29 | -61.2167 | -61.5692 | 0.068665 | -61.5005 | 60.9467 | 61.0291 | -61.1572 | -61.3266 | -0.036621 | 0.036621 | 0.004578 | 0.24719 | -0.01831 | -0.054931 | 0.1236 | 0.09613 | -0.073242 | -0.11444 | -0.31586 | -0.24719 | -0.17395 | -0.032043 | 122.319 | 122.438 | 61.3083 | -122.2778 | 122.2 | 122.2824 | 61.322 | -122.3877
861.3594 | 122.5204 | -61.2579 | 61.1206 | -0.0022127 | -0.036243 | 0.11231 | 0.025656 | 0.051588 | -0.022885 | -0.024206 | -0.0003053 | 0.00076695 | 0.042603 | 0.062844 | -0.017013 | -0.013821 | 61.1206 | -61.1755 | -0.045776 | -61.3403 | 61.1206 | -61.3083 | -61.2213 | -61.6745 | -0.018311 | -61.6287 | 61.0062 | 61.0931 | -61.1938 | -61.3678 | -0.050354 | 0.036622 | 0 | 0.082398 | -0.082397 | -0.11902 | 0 | 0.064087 | -0.10986 | -0.11444 | -0.41656 | -0.37079 | -0.26093 | -0.027465 | 122.3785 | 122.3785 | 61.2122 | -122.3419 | 122.2641 | 122.3511 | 61.2396 | -122.4884
863.125 | 122.5616 | -61.2625 | 61.1114 | 0.0054168 | -0.035816 | 0.11509 | 0.02352 | 0.053724 | -0.022672 | -0.021001 | 0.0073242 | -0.00072845 | 0.041321 | 0.060921 | -0.015731 | -0.011471 | 61.116 | -61.1526 | -0.036621 | -61.322 | 61.1389 | -61.3083 | -61.2396 | -61.6837 | -0.045776 | -61.615 | 61.0199 | 61.0931 | -61.1664 | -61.409 | -0.045777 | 0.022888 | 0.027466 | 0.10986 | -0.059509 | -0.082397 | 0.004578 | 0.09613 | -0.14648 | -0.091553 | -0.42114 | -0.35248 | -0.20599 | -0.01831 | 122.4014 | 122.3785 | 61.2259 | -122.3511 | 122.2824 | 122.3557 | 61.2167 | -122.5204
864.9062 | 122.5159 | -61.2305 | 61.1938 | -0.0022127 | -0.035389 | 0.1168 | 0.026297 | 0.052442 | -0.027799 | -0.025487 | 0.0073242 | -0.0050009 | 0.040894 | 0.058571 | -0.021072 | -0.014035 | 61.2534 | -60.9238 | 0.1831 | -61.1801 | 61.1298 | -61.2122 | -61.1298 | -61.5463 | 0.16022 | -61.4319 | 61.0611 | 61.1206 | -61.084 | -61.29 | 0.018311 | 0.10071 | -0.064087 | 0.3067 | 0.050354 | -0.050354 | 0.059509 | 0.14648 | -0.059509 | -0.13275 | -0.31586 | -0.20142 | -0.14191 | -0.073243 | 122.3602 | 122.4838 | 61.4136 | -122.3236 | 122.2916 | 122.3511 | 61.3907 | -122.4838
866.625 | 122.5296 | -61.2946 | 61.116 | 0.0054168 | -0.037525 | 0.11338 | 0.026297 | 0.049238 | -0.022458 | -0.023351 | -0.0003053 | -0.0024375 | 0.044953 | 0.061776 | -0.016158 | -0.014035 | 61.1114 | -61.1389 | -0.027466 | -61.3083 | 61.1389 | -61.2854 | -61.2122 | -61.6791 | 0 | -61.6287 | 61.0291 | 61.0519 | -61.1801 | -61.3724 | 0.009156 | 0.082398 | 0.022888 | 0.15564 | -0.013733 | -0.096131 | -0.004578 | 0.11444 | -0.077819 | -0.086975 | -0.38452 | -0.33417 | -0.25635 | -0.064087 | 122.4335 | 122.406 | 61.2671 | -122.3282 | 122.3236 | 122.3465 | 61.2946 | -122.4884
868.3281 | 122.5021 | -61.2671 | 61.1481 | 0.0054168 | -0.034534 | 0.11381 | 0.027792 | 0.048811 | -0.022885 | -0.024633 | -0.0003053 | -0.0013693 | 0.042816 | 0.063698 | -0.017227 | -0.014035 | 61.171 | -61.0931 | 0.018311 | -61.2946 | 61.0977 | -61.29 | -61.2076 | -61.6516 | 0.009155 | -61.5875 | 61.0016 | 61.0794 | -61.1801 | -61.377 | -0.022888 | 0.059509 | -0.050354 | 0.17395 | -0.027466 | -0.086975 | 0.022888 | 0.086975 | -0.10986 | -0.14648 | -0.38452 | -0.32043 | -0.21057 | -0.068664 | 122.3648 | 122.438 | 61.2854 | -122.3557 | 122.2687 | 122.3465 | 61.2762 | -122.525
870.1094 | 122.5845 | -61.2167 | 61.1206 | 0.0054168 | -0.038807 | 0.11594 | 0.026938 | 0.052656 | -0.028226 | -0.022924 | 0.0073242 | -0.0043601 | 0.041107 | 0.061135 | -0.016586 | -0.013821 | 61.2122 | -60.997 | 0.082397 | -61.2671 | 61.0474 | -61.2762 | -61.1847 | -61.5784 | 0.082397 | -61.4731 | 60.9375 | 61.0199 | -61.1343 | -61.3495 | -0.059509 | 0.032044 | -0.073242 | 0.21973 | -0.050354 | -0.082398 | 0.091553 | 0.082398 | -0.13275 | -0.1831 | -0.36163 | -0.25635 | -0.1236 | -0.10071 | 122.2641 | 122.4289 | 61.2991 | -122.3053 | 122.1542 | 122.2366 | 61.2991 | -122.4701
871.8906 | 122.6028 | -61.2259 | 61.116 | -0.0098417 | -0.036243 | 0.11402 | 0.025229 | 0.053938 | -0.027585 | -0.023992 | 0.0073242 | -0.0039329 | 0.041962 | 0.060921 | -0.015518 | -0.012753 | 61.2167 | -61.0062 | 0.068665 | -61.2579 | 61.0382 | -61.2854 | -61.1847 | -61.5738 | 0.07782 | -61.4502 | 60.9604 | 60.997 | -61.1481 | -61.3495 | -0.059509 | 0.041199 | -0.07782 | 0.21973 | -0.032044 | -0.073243 | 0.10071 | 0.07782 | -0.1236 | -0.15564 | -0.3479 | -0.2243 | -0.10071 | -0.11902 | 122.2641 | 122.4426 | 61.2946 | -122.3007 | 122.1863 | 122.2229 | 61.3037 | -122.4655
873.6875 | 122.4838 | -61.2762 | 61.1298 | -0.0022127 | -0.034748 | 0.11509 | 0.026511 | 0.052656 | -0.021176 | -0.024206 | -0.0079343 | 0.00076695 | 0.042603 | 0.061989 | -0.013168 | -0.014889 | 61.1755 | -61.084 | 0.018311 | -61.3129 | 61.1252 | -61.2854 | -61.2213 | -61.6379 | 0.022888 | -61.5967 | 61.0062 | 61.0657 | -61.171 | -61.3678 | -0.009155 | 0.054932 | -0.004578 | 0.19226 | -0.036621 | -0.091553 | 0.045776 | 0.10529 | -0.091553 | -0.1236 | -0.36163 | -0.32043 | -0.22888 | -0.064087 | 122.4014 | 122.4518 | 61.2946 | -122.3511 | 122.2824 | 122.3419 | 61.2991 | -122.4976
875.4062 | 122.5845 | -61.2213 | 61.1206 | 0.0054168 | -0.038166 | 0.11701 | 0.026938 | 0.051374 | -0.02908 | -0.026342 | 0.0073242 | -0.0045737 | 0.041535 | 0.060494 | -0.018936 | -0.012753 | 61.1984 | -61.0245 | 0.054932 | -61.2717 | 61.0703 | -61.2579 | -61.1755 | -61.6013 | 0.050354 | -61.4822 | 60.9741 | 61.0794 | -61.1206 | -61.3266 | -0.036622 | 0.045776 | -0.050354 | 0.19684 | -0.050354 | -0.09613 | 0.07782 | 0.10071 | -0.10529 | -0.14648 | -0.37994 | -0.26093 | -0.15564 | -0.041198 | 122.2916 | 122.4197 | 61.2762 | -122.2961 | 122.1954 | 122.3007 | 61.2717 | -122.4472
877.125 | 122.6303 | -61.2488 | 61.0565 | 0.013046 | -0.036884 | 0.1153 | 0.024802 | 0.052015 | -0.023526 | -0.022924 | 0.0073242 | -0.0024375 | 0.040467 | 0.059853 | -0.015518 | -0.015317 | 61.1801 | -61.0703 | 0 | -61.2991 | 61.0748 | -61.3037 | -61.2167 | -61.5921 | 0.054932 | -61.5097 | 60.9604 | 61.0382 | -61.1618 | -61.3358 | -0.054932 | 0.032043 | 0.01831 | 0.17853 | -0.050354 | -0.082397 | 0.1236 | 0.086975 | -0.086975 | -0.096131 | -0.34332 | -0.26093 | -0.17395 | -0.018311 | 122.3236 | 122.4289 | 61.2488 | -122.2733 | 122.2092 | 122.287 | 61.3037 | -122.3923
878.9062 | 122.6028 | -61.2122 | 61.0748 | 0.020676 | -0.03838 | 0.11274 | 0.023947 | 0.051588 | -0.024594 | -0.022069 | 0.0073242 | -0.0035055 | 0.042816 | 0.059426 | -0.014877 | -0.015958 | 61.2213 | -61.0107 | 0.059509 | -61.2625 | 61.0474 | -61.2991 | -61.2076 | -61.5738 | 0.068665 | -61.4639 | 60.9283 | 60.997 | -61.1893 | -61.3678 | -0.086975 | 0.004577 | -0.027466 | 0.20142 | -0.050354 | -0.054931 | 0.14648 | 0.022888 | -0.15564 | -0.14648 | -0.36163 | -0.25177 | -0.09613 | -0.07782 | 122.2595 | 122.4335 | 61.2717 | -122.2824 | 122.1405 | 122.2092 | 61.2808 | -122.4426
880.6406 | 122.5021 | -61.2259 | 61.116 | -0.0022127 | -0.034748 | 0.11423 | 0.027152 | 0.052869 | -0.020535 | -0.023778 | 0.0073242 | -0.0032919 | 0.043244 | 0.06263 | -0.014236 | -0.012326 | 61.116 | -61.1618 | -0.027466 | -61.3174 | 61.1069 | -61.2991 | -61.2213 | -61.6653 | -0.041199 | -61.6241 | 60.9924 | 61.0611 | -61.171 | -61.377 | -0.073242 | 0.004578 | -0.009155 | 0.064087 | -0.091553 | -0.096131 | 0 | 0.054932 | -0.15106 | -0.1236 | -0.43945 | -0.39826 | -0.24719 | -0.054932 | 122.3328 | 122.3419 | 61.1984 | -122.3373 | 122.2183 | 122.287 | 61.1847 | -122.493
882.4062 | 122.5067 | -61.1938 | 61.2213 | 0.0054168 | -0.032825 | 0.1153 | 0.028006 | 0.053083 | -0.027158 | -0.022924 | 0.0073242 | -0.0022239 | 0.043244 | 0.058358 | -0.018508 | -0.012753 | 61.2442 | -60.9558 | 0.14191 | -61.2076 | 61.1572 | -61.2122 | -61.116 | -61.5738 | 0.10986 | -61.4731 | 61.0748 | 61.1526 | -61.1023 | -61.2854 | -0.01831 | 0.07782 | -0.064086 | 0.23804 | -0.013733 | -0.091553 | 0.022889 | 0.091553 | -0.091552 | -0.14648 | -0.37994 | -0.27923 | -0.18768 | -0.068664 | 122.3511 | 122.4381 | 61.3358 | -122.3373 | 122.2687 | 122.3465 | 61.3037 | -122.5067
884.125 | 122.5388 | -61.2808 | 61.1298 | -0.0098417 | -0.035175 | 0.11316 | 0.026083 | 0.050306 | -0.021604 | -0.02271 | 0.0073242 | -0.0024375 | 0.042816 | 0.062416 | -0.015304 | -0.012967 | 61.1343 | -61.1389 | -0.050354 | -61.3174 | 61.1252 | -61.3037 | -61.2396 | -61.6608 | -0.054932 | -61.5921 | 61.0107 | 61.0428 | -61.1618 | -61.3724 | -0.022888 | 0.041199 | -0.004578 | 0.14191 | -0.036621 | -0.07782 | 0.004577 | 0.11902 | -0.091552 | -0.11902 | -0.37994 | -0.31128 | -0.21973 | -0.086975 | 122.406 | 122.4152 | 61.2305 | -122.3694 | 122.2916 | 122.3236 | 61.2259 | -122.5021
885.8438 | 122.5525 | -61.2213 | 61.1984 | 0.013046 | -0.032184 | 0.11509 | 0.029501 | 0.052229 | -0.025022 | -0.024847 | -0.0079343 | -0.0017965 | 0.043457 | 0.058999 | -0.017013 | -0.012753 | 61.2076 | -61.0016 | 0.082397 | -61.2305 | 61.2076 | -61.2167 | -61.1664 | -61.6058 | 0.068665 | -61.5372 | 61.0703 | 61.1481 | -61.1206 | -61.3083 | 0.004577 | 0.054931 | 0.009156 | 0.21973 | -0.009156 | -0.064087 | 0.009156 | 0.10071 | -0.086976 | -0.12817 | -0.38452 | -0.31586 | -0.22888 | -0.050354 | 122.4289 | 122.4289 | 61.3037 | -122.3648 | 122.2916 | 122.3694 | 61.29 | -122.5067
887.625 | 122.5616 | -61.2167 | 61.1206 | 0.013046 | -0.040089 | 0.11744 | 0.024374 | 0.051588 | -0.02908 | -0.023351 | 0.0073242 | -0.0060691 | 0.039185 | 0.06028 | -0.016799 | -0.012112 | 61.1938 | -60.9787 | 0.050354 | -61.2717 | 61.0611 | -61.235 | -61.1572 | -61.5875 | 0.050354 | -61.4822 | 60.9787 | 61.0565 | -61.1069 | -61.322 | -0.01831 | 0.059509 | -0.059509 | 0.23804 | -0.054931 | -0.11444 | 0.073243 | 0.10986 | -0.10529 | -0.14191 | -0.37079 | -0.2655 | -0.16022 | -0.064086 | 122.2778 | 122.4106 | 61.2671 | -122.2778 | 122.1954 | 122.2733 | 61.2671 | -122.4426
889.3281 | 122.5937 | -61.2213 | 61.116 | -0.0022127 | -0.036243 | 0.11466 | 0.027365 | 0.052229 | -0.025022 | -0.023565 | 0.0073242 | -0.0026511 | 0.041962 | 0.059426 | -0.015304 | -0.017026 | 61.2167 | -60.9924 | 0.068665 | -61.2488 | 61.0565 | -61.2579 | -61.1801 | -61.5601 | 0.086975 | -61.4502 | 60.965 | 61.0016 | -61.1526 | -61.3358 | -0.036622 | 0.041198 | -0.059509 | 0.22888 | -0.027466 | -0.068664 | 0.10071 | 0.068664 | -0.11444 | -0.15106 | -0.33875 | -0.22888 | -0.11444 | -0.11444 | 122.2778 | 122.438 | 61.29 | -122.2961 | 122.1863 | 122.2229 | 61.3083 | -122.4518
891.125 | 122.58 | -61.2076 | 61.1389 | 0.0054168 | -0.039448 | 0.11722 | 0.027579 | 0.052656 | -0.026731 | -0.024419 | 0.014954 | -0.0039329 | 0.042389 | 0.060494 | -0.018508 | -0.014035 | 61.203 | -60.997 | 0.064087 | -61.2625 | 61.0748 | -61.2396 | -61.1755 | -61.5829 | 0.054932 | -61.4685 | 60.9604 | 61.0199 | -61.1206 | -61.3266 | -0.032043 | 0.032044 | -0.064087 | 0.21057 | -0.054931 | -0.086975 | 0.064087 | 0.086976 | -0.11902 | -0.17853 | -0.37537 | -0.26093 | -0.14191 | -0.11902 | 122.2824 | 122.4106 | 61.2717 | -122.3145 | 122.168 | 122.2275 | 61.2625 | -122.4655
892.8906 | 122.6166 | -61.1938 | 61.1343 | 0.013046 | -0.03838 | 0.11658 | 0.025229 | 0.052229 | -0.028226 | -0.025915 | 0.0073242 | -0.0028647 | 0.04303 | 0.060494 | -0.018081 | -0.013394 | 61.1938 | -61.0016 | 0.045776 | -61.2579 | 61.0977 | -61.2305 | -61.1893 | -61.5921 | 0.041199 | -61.4777 | 61.0062 | 61.0611 | -61.1343 | -61.3037 | -0.036621 | 0.004578 | -0.036621 | 0.19226 | -0.064087 | -0.068665 | 0.05951 | 0.05951 | -0.10986 | -0.12817 | -0.39825 | -0.28381 | -0.17395 | -0.073242 | 122.2916 | 122.3877 | 61.2396 | -122.3236 | 122.2 | 122.2549 | 61.235 | -122.438
894.5938 | 122.5113 | -61.1984 | 61.1801 | 0.0054168 | -0.034534 | 0.11573 | 0.03121 | 0.051374 | -0.024594 | -0.024633 | 0.0073242 | -0.0015829 | 0.042176 | 0.061135 | -0.018722 | -0.013821 | 61.2167 | -61.0199 | 0.086975 | -61.2534 | 61.1801 | -61.2213 | -61.1755 | -61.5829 | 0.073242 | -61.4914 | 61.1114 | 61.1481 | -61.116 | -61.2991 | -0.022888 | 0.022888 | 0 | 0.17853 | -0.054932 | -0.07782 | 0.036621 | 0.082397 | -0.10071 | -0.068665 | -0.38452 | -0.29297 | -0.19226 | -0.032044 | 122.3785 | 122.4152 | 61.2854 | -122.3557 | 122.3099 | 122.3465 | 61.2717 | -122.4792
896.3125 | 122.5708 | -61.2213 | 61.1252 | -0.0022127 | -0.036671 | 0.11487 | 0.023947 | 0.051588 | -0.026517 | -0.022497 | 0.0073242 | -0.0039329 | 0.041321 | 0.060494 | -0.020431 | -0.015317 | 61.2167 | -60.9695 | 0.059509 | -61.2534 | 61.0657 | -61.2625 | -61.2076 | -61.5601 | 0.050354 | -61.4822 | 60.9787 | 61.0291 | -61.1069 | -61.3037 | -0.041199 | 0.013732 | -0.059509 | 0.25177 | -0.032044 | -0.045776 | 0.091553 | 0.11444 | -0.082398 | -0.14648 | -0.33875 | -0.26093 | -0.17853 | -0.09613 | 122.287 | 122.438 | 61.2808 | -122.3328 | 122.2 | 122.2504 | 61.2717 | -122.4289
898.1094 | 122.5754 | -61.1801 | 61.1343 | 0.0054168 | -0.041797 | 0.11765 | 0.022452 | 0.050947 | -0.026944 | -0.025274 | 0.014954 | -0.0045737 | 0.039826 | 0.058999 | -0.016799 | -0.013821 | 61.2213 | -60.997 | 0.054932 | -61.2488 | 61.1023 | -61.2808 | -61.1801 | -61.5646 | 0.054932 | -61.4731 | 60.9695 | 61.0519 | -61.1023 | -61.3037 | -0.10071 | 0 | -0.032043 | 0.18311 | -0.068664 | -0.068664 | 0.086975 | 0.07782 | -0.1236 | -0.16479 | -0.38452 | -0.29297 | -0.16937 | -0.082397 | 122.2824 | 122.4014 | 61.235 | -122.3145 | 122.1497 | 122.2321 | 61.235 | -122.438
899.875 | 122.4884 | -61.2579 | 61.1069 | -0.0022127 | -0.03368 | 0.11402 | 0.024802 | 0.052229 | -0.018826 | -0.023138 | 0.0073242 | 0.0022623 | 0.042603 | 0.061135 | -0.013381 | -0.016598 | 61.171 | -61.0886 | 0 | -61.2946 | 61.1389 | -61.2762 | -61.2167 | -61.6241 | 0.022888 | -61.5875 | 61.0062 | 61.0794 | -61.1755 | -61.3403 | -0.01831 | 0.041199 | 0.032043 | 0.16937 | -0.036621 | -0.07782 | 0.064086 | 0.082398 | -0.082397 | -0.10071 | -0.36621 | -0.32959 | -0.24719 | -0.027466 | 122.3969 | 122.4289 | 61.2579 | -122.3236 | 122.2641 | 122.3373 | 61.2808 | -122.4472
901.6094 | 122.4792 | -61.2854 | 61.1343 | 0.0054168 | -0.034534 | 0.11509 | 0.024374 | 0.054578 | -0.020535 | -0.021001 | -0.0079343 | 0.00033975 | 0.040039 | 0.061348 | -0.014877 | -0.013821 | 61.1526 | -61.0931 | 0 | -61.2991 | 61.1343 | -61.2762 | -61.2259 | -61.6379 | 0 | -61.6104 | 61.0519 | 61.0703 | -61.1435 | -61.3632 | 0.009155 | 0.059509 | 0 | 0.19226 | -0.013733 | -0.073242 | 0.018311 | 0.14191 | -0.07782 | -0.082397 | -0.35248 | -0.32501 | -0.24719 | -0.064087 | 122.4197 | 122.438 | 61.2854 | -122.3602 | 122.3373 | 122.3557 | 61.2854 | -122.4976
903.3281 | 122.5204 | -61.2259 | 61.1343 | -0.0098417 | -0.034534 | 0.11616 | 0.027365 | 0.052869 | -0.022458 | -0.021642 | 0.0073242 | 0.00012615 | 0.041535 | 0.060494 | -0.015518 | -0.013394 | 61.2259 | -60.9787 | 0.10529 | -61.2122 | 61.1618 | -61.2534 | -61.1893 | -61.5463 | 0.12817 | -61.5005 | 61.0519 | 61.1069 | -61.1069 | -61.322 | -0.027466 | 0.036621 | 0.027466 | 0.24719 | 0.013733 | -0.022888 | 0.091553 | 0.11902 | -0.09613 | -0.082397 | -0.32044 | -0.27466 | -0.17853 | -0.027465 | 122.3877 | 122.4518 | 61.3312 | -122.3236 | 122.2778 | 122.3328 | 61.3541 | -122.4564
905.1094 | 122.5845 | -61.2213 | 61.1206 | 0.013046 | -0.03838 | 0.11445 | 0.026297 | 0.053938 | -0.027158 | -0.021429 | -0.0003053 | -0.0032919 | 0.04068 | 0.06028 | -0.016799 | -0.012967 | 61.2305 | -60.9695 | 0.07782 | -61.235 | 61.0336 | -61.2534 | -61.1664 | -61.5692 | 0.068665 | -61.4548 | 60.9512 | 61.0199 | -61.1069 | -61.3129 | -0.032044 | 0.054931 | -0.086975 | 0.25177 | -0.013733 | -0.068664 | 0.10986 | 0.11444 | -0.091553 | -0.16937 | -0.3479 | -0.23346 | -0.14191 | -0.10071 | 122.2549 | 122.4518 | 61.2991 | -122.287 | 122.1725 | 122.2412 | 61.29 | -122.4335
906.875 | 122.493 | -61.1801 | 61.2213 | -0.0022127 | -0.035175 | 0.1168 | 0.03121 | 0.052442 | -0.027158 | -0.023138 | 0.022583 | -0.0050009 | 0.040467 | 0.060921 | -0.019149 | -0.015317 | 61.2762 | -60.9146 | 0.16937 | -61.171 | 61.1389 | -61.1893 | -61.1435 | -61.5417 | 0.13733 | -61.4365 | 61.0657 | 61.1389 | -61.0794 | -61.2534 | -0.009155 | 0.036621 | -0.082397 | 0.2655 | 0.009156 | -0.027465 | 0.054932 | 0.10071 | -0.073242 | -0.15564 | -0.36163 | -0.25635 | -0.1831 | -0.082397 | 122.319 | 122.4564 | 61.3495 | -122.3648 | 122.2458 | 122.319 | 61.3174 | -122.4747
908.5938 | 122.612 | -61.1526 | 61.1526 | 0.020676 | -0.03603 | 0.11594 | 0.029074 | 0.054151 | -0.027799 | -0.024206 | -0.0003053 | -0.0041465 | 0.039826 | 0.060921 | -0.017867 | -0.015958 | 61.3037 | -60.878 | 0.16479 | -61.1618 | 61.1023 | -61.1984 | -61.1069 | -61.4639 | 0.17853 | -61.3403 | 61.0062 | 61.0703 | -61.0657 | -61.2671 | -0.045776 | 0.045776 | -0.050354 | 0.27466 | -0.009155 | -0.054931 | 0.15106 | 0.086975 | -0.11444 | -0.14648 | -0.31128 | -0.18768 | -0.073242 | -0.082398 | 122.2549 | 122.4564 | 61.3174 | -122.2595 | 122.1588 | 122.2229 | 61.3312 | -122.4197
910.375 | 122.493 | -61.2717 | 61.1435 | 0.0054168 | -0.035175 | 0.11423 | 0.026724 | 0.050092 | -0.019254 | -0.02271 | 0.022583 | -8.7654e-05 | 0.038758 | 0.062416 | -0.014022 | -0.014889 | 61.1481 | -61.1069 | -0.032043 | -61.3037 | 61.1526 | -61.2762 | -61.203 | -61.6425 | -0.018311 | -61.6104 | 61.0062 | 61.084 | -61.1526 | -61.3678 | -0.004578 | 0.068664 | 0.009155 | 0.16479 | -0.032044 | -0.10071 | 0.004577 | 0.11902 | -0.096131 | -0.13733 | -0.37079 | -0.33875 | -0.24262 | -0.05951 | 122.4243 | 122.4197 | 61.2396 | -122.3465 | 122.2778 | 122.3557 | 61.2534 | -122.5113
912.1094 | 122.5388 | -61.2122 | 61.1343 | 0.0054168 | -0.036671 | 0.11274 | 0.025443 | 0.052656 | -0.022244 | -0.021215 | 0.0073242 | -0.00030125 | 0.041535 | 0.06028 | -0.014663 | -0.013821 | 61.235 | -61.0062 | 0.086975 | -61.2167 | 61.171 | -61.2442 | -61.1664 | -61.5417 | 0.11444 | -61.496 | 61.0382 | 61.084 | -61.1114 | -61.29 | -0.032044 | 0.045776 | 0.036621 | 0.20599 | -0.004578 | -0.050354 | 0.10071 | 0.10071 | -0.07782 | -0.09613 | -0.32959 | -0.28381 | -0.20599 | -0.050354 | 122.3831 | 122.4472 | 61.2991 | -122.3007 | 122.2504 | 122.2961 | 61.3266 | -122.4243
913.875 | 122.6166 | -61.1572 | 61.1389 | -0.0022127 | -0.038593 | 0.11722 | 0.028647 | 0.051588 | -0.031644 | -0.02506 | 0.0073242 | -0.0067099 | 0.039612 | 0.058358 | -0.016586 | -0.01254 | 61.1847 | -60.9741 | 0.064087 | -61.2167 | 61.0931 | -61.2305 | -61.1572 | -61.5463 | 0.09613 | -61.409 | 61.0016 | 61.0794 | -61.0748 | -61.2671 | -0.073242 | 0 | -0.045776 | 0.18311 | -0.059509 | -0.059509 | 0.045776 | 0.082398 | -0.10986 | -0.13733 | -0.3891 | -0.25177 | -0.14191 | -0.059509 | 122.2504 | 122.3419 | 61.2213 | -122.2961 | 122.1588 | 122.2366 | 61.2534 | -122.406
915.5938 | 122.525 | -61.2122 | 61.1755 | 0.013046 | -0.035389 | 0.11359 | 0.025229 | 0.054792 | -0.022244 | -0.022497 | 0.0073242 | 0.00012615 | 0.042176 | 0.06028 | -0.017013 | -0.015317 | 61.2259 | -60.9787 | 0.10071 | -61.2076 | 61.171 | -61.235 | -61.1572 | -61.5463 | 0.11444 | -61.496 | 61.0519 | 61.0657 | -61.1023 | -61.3266 | -0.022888 | 0.054931 | -0.004578 | 0.23346 | 0.004577 | -0.050354 | 0.050354 | 0.10986 | -0.11444 | -0.1236 | -0.33417 | -0.28381 | -0.16937 | -0.10986 | 122.3831 | 122.438 | 61.3129 | -122.3328 | 122.2641 | 122.2778 | 61.3266 | -122.5021
917.3594 | 122.5021 | -61.1755 | 61.2076 | 0.013046 | -0.034962 | 0.11744 | 0.029501 | 0.05351 | -0.026303 | -0.023565 | 0.0073242 | -0.0047873 | 0.042603 | 0.061135 | -0.019363 | -0.014889 | 61.2671 | -60.8917 | 0.1831 | -61.1526 | 61.116 | -61.1938 | -61.116 | -61.4868 | 0.19684 | -61.377 | 61.0336 | 61.116 | -61.0291 | -61.2625 | -0.018311 | 0.059509 | -0.091553 | 0.28381 | 0.022888 | -0.036621 | 0.059509 | 0.14648 | -0.086975 | -0.17395 | -0.31128 | -0.20142 | -0.11444 | -0.091553 | 122.2916 | 122.4426 | 61.3586 | -122.3236 | 122.2092 | 122.2916 | 61.3724 | -122.4701
919.0781 | 122.4609 | -61.2671 | 61.1343 | 0.0054168 | -0.034107 | 0.11252 | 0.024161 | 0.050092 | -0.020108 | -0.022924 | 0.0073242 | -0.00030125 | 0.040894 | 0.063485 | -0.014877 | -0.01318 | 61.1893 | -61.0382 | 0.036621 | -61.2808 | 61.1298 | -61.2717 | -61.203 | -61.6196 | 0.013733 | -61.5692 | 61.0153 | 61.0931 | -61.1206 | -61.3449 | -0.004577 | 0.064087 | -0.004577 | 0.22888 | -0.013733 | -0.07782 | 0.054932 | 0.14649 | -0.07782 | -0.11902 | -0.35248 | -0.30212 | -0.2243 | -0.041198 | 122.3969 | 122.4564 | 61.3037 | -122.3373 | 122.2824 | 122.3602 | 61.2808 | -122.4792
920.8594 | 122.4884 | -61.1938 | 61.2122 | -0.0022127 | -0.034107 | 0.11466 | 0.030356 | 0.051374 | -0.028012 | -0.024206 | 0.0073242 | -0.0050009 | 0.043457 | 0.062203 | -0.018508 | -0.012967 | 61.2808 | -60.8826 | 0.16937 | -61.1389 | 61.1206 | -61.2167 | -61.0977 | -61.5097 | 0.17853 | -61.3953 | 61.0657 | 61.1206 | -61.0657 | -61.2808 | -0.022888 | 0.096131 | -0.091553 | 0.31128 | 0.054932 | -0.041199 | 0.068665 | 0.12817 | -0.086975 | -0.14648 | -0.31586 | -0.20142 | -0.11444 | -0.091553 | 122.3145 | 122.4747 | 61.3632 | -122.3099 | 122.2595 | 122.3145 | 61.3724 | -122.493
922.5781 | 122.5708 | -61.1618 | 61.1618 | -0.0098417 | -0.039661 | 0.11423 | 0.025443 | 0.054578 | -0.028226 | -0.023565 | 0.0073242 | -0.0035055 | 0.041107 | 0.060067 | -0.018295 | -0.013821 | 61.203 | -60.9924 | 0.041199 | -61.235 | 61.1023 | -61.2213 | -61.1435 | -61.5692 | 0.032043 | -61.4548 | 61.0062 | 61.084 | -61.0931 | -61.2991 | -0.059509 | 0.01831 | -0.059509 | 0.16937 | -0.073242 | -0.091552 | 0.041199 | 0.068664 | -0.13733 | -0.15564 | -0.40741 | -0.29297 | -0.15564 | -0.07782 | 122.2641 | 122.3648 | 61.203 | -122.3053 | 122.168 | 122.2458 | 61.1938 | -122.4609
924.2812 | 122.4976 | -61.1618 | 61.2167 | 0.0054168 | -0.037311 | 0.11637 | 0.026724 | 0.052656 | -0.024808 | -0.024206 | 0.0073242 | -0.0039329 | 0.042176 | 0.05793 | -0.015945 | -0.014676 | 61.29 | -60.878 | 0.19226 | -61.1481 | 61.1114 | -61.1847 | -61.1252 | -61.4868 | 0.17853 | -61.3724 | 61.0428 | 61.0657 | -61.0886 | -61.2442 | -0.022888 | 0.036621 | -0.10529 | 0.28381 | 0.013733 | -0.022888 | 0.073242 | 0.073242 | -0.082398 | -0.17395 | -0.32501 | -0.21057 | -0.12817 | -0.15106 | 122.2733 | 122.4518 | 61.3541 | -122.3419 | 122.2046 | 122.2275 | 61.3403 | -122.4609
926.0469 | 122.4976 | -61.1847 | 61.1984 | 0.0054168 | -0.037739 | 0.11423 | 0.026724 | 0.055219 | -0.025662 | -0.026556 | 0.0073242 | -0.0041465 | 0.040467 | 0.061562 | -0.018081 | -0.014676 | 61.3037 | -60.8871 | 0.17853 | -61.1343 | 61.1343 | -61.1755 | -61.1114 | -61.4777 | 0.18768 | -61.3724 | 61.0336 | 61.1023 | -61.0519 | -61.2534 | 0.009155 | 0.073242 | -0.064087 | 0.29755 | 0.050354 | -0.022888 | 0.10529 | 0.13275 | -0.068665 | -0.16479 | -0.29297 | -0.18768 | -0.11902 | -0.09613 | 122.319 | 122.4884 | 61.3632 | -122.3099 | 122.2183 | 122.287 | 61.3724 | -122.4518
927.8125 | 122.6166 | -61.1343 | 61.1664 | 0.013046 | -0.038593 | 0.11744 | 0.028006 | 0.054578 | -0.028226 | -0.026342 | 0.014954 | -0.0054281 | 0.041535 | 0.058785 | -0.018295 | -0.015317 | 61.2808 | -60.8871 | 0.13275 | -61.1572 | 61.1343 | -61.1847 | -61.116 | -61.4639 | 0.17395 | -61.3678 | 61.0199 | 61.0794 | -61.084 | -61.2671 | -0.050354 | 0.01831 | -0.032044 | 0.24719 | -0.022889 | -0.041199 | 0.11444 | 0.050354 | -0.13275 | -0.14648 | -0.32959 | -0.23346 | -0.10071 | -0.086975 | 122.2687 | 122.4152 | 61.2671 | -122.2824 | 122.1542 | 122.2137 | 61.3083 | -122.4335
929.5781 | 122.5845 | -61.1481 | 61.1847 | 0.0054168 | -0.036457 | 0.11744 | 0.028647 | 0.053083 | -0.026303 | -0.026769 | 0.0073242 | -0.0037191 | 0.042176 | 0.059853 | -0.018081 | -0.015744 | 61.3174 | -60.8551 | 0.18768 | -61.1481 | 61.1526 | -61.1984 | -61.1114 | -61.4502 | 0.18768 | -61.3586 | 61.0474 | 61.1023 | -61.0474 | -61.235 | -0.050354 | 0.036621 | -0.032043 | 0.29297 | 0 | -0.036621 | 0.13275 | 0.10071 | -0.086975 | -0.13733 | -0.30212 | -0.21057 | -0.1236 | -0.082397 | 122.3007 | 122.4655 | 61.3358 | -122.2961 | 122.1954 | 122.2504 | 61.3358 | -122.4197
931.2969 | 122.5754 | -61.2213 | 61.0703 | 0.013046 | -0.037311 | 0.11316 | 0.025229 | 0.050733 | -0.020322 | -0.025915 | -0.0003053 | -0.00094205 | 0.040894 | 0.059212 | -0.011459 | -0.012967 | 61.1755 | -61.084 | -0.064087 | -61.2854 | 61.116 | -61.2762 | -61.1938 | -61.6013 | -0.022888 | -61.5692 | 60.997 | 61.0657 | -61.1343 | -61.3541 | -0.054932 | 0.027465 | 0.045777 | 0.13733 | -0.064087 | -0.091552 | 0.10529 | 0.086975 | -0.13275 | -0.073242 | -0.37994 | -0.3479 | -0.21515 | -0.004577 | 122.3373 | 122.3969 | 61.1572 | -122.2641 | 122.2183 | 122.287 | 61.1984 | -122.4243
933.0781 | 122.6166 | -61.1298 | 61.1435 | 0.0054168 | -0.039661 | 0.11509 | 0.027365 | 0.051801 | -0.026731 | -0.022497 | -0.0079343 | -0.0054281 | 0.040039 | 0.060494 | -0.018722 | -0.011899 | 61.1938 | -60.9833 | 0.045776 | -61.2213 | 61.1114 | -61.2259 | -61.1435 | -61.5326 | 0.068665 | -61.4365 | 61.0153 | 61.0703 | -61.0703 | -61.3083 | -0.09613 | -0.013733 | -0.032044 | 0.14649 | -0.091552 | -0.077819 | 0.050354 | 0.05951 | -0.17853 | -0.12817 | -0.40283 | -0.3067 | -0.12817 | -0.073243 | 122.2412 | 122.3236 | 61.1755 | -122.287 | 122.1451 | 122.2 | 61.1984 | -122.4518
934.8438 | 122.6212 | -61.1755 | 61.1435 | -0.0022127 | -0.037952 | 0.11744 | 0.027365 | 0.052869 | -0.029294 | -0.023351 | 0.014954 | -0.0041465 | 0.040039 | 0.059212 | -0.01509 | -0.012967 | 61.1893 | -60.9741 | 0.027466 | -61.2122 | 61.1114 | -61.2213 | -61.1572 | -61.5372 | 0.068665 | -61.4227 | 61.0153 | 61.0703 | -61.084 | -61.2808 | -0.045776 | 0.01831 | -0.032044 | 0.20142 | -0.036621 | -0.054931 | 0.045776 | 0.091553 | -0.10529 | -0.12817 | -0.36163 | -0.24719 | -0.14191 | -0.073243 | 122.287 | 122.3648 | 61.203 | -122.3007 | 122.1909 | 122.2458 | 61.2442 | -122.4243
936.625 | 122.4701 | -61.2534 | 61.116 | 0.0054168 | -0.034748 | 0.11359 | 0.022665 | 0.052442 | -0.019254 | -0.023778 | 0.014954 | 0.0026895 | 0.041962 | 0.063912 | -0.010818 | -0.014462 | 61.1893 | -61.0519 | 0.004578 | -61.2762 | 61.1389 | -61.2534 | -61.1938 | -61.5875 | 0.004578 | -61.5646 | 61.0336 | 61.0657 | -61.1389 | -61.3541 | 0 | 0.059509 | 0.022888 | 0.20142 | -0.022888 | -0.082397 | 0.073242 | 0.11444 | -0.10071 | -0.082398 | -0.33417 | -0.31128 | -0.21057 | -0.050354 | 122.3923 | 122.4426 | 61.2579 | -122.3099 | 122.287 | 122.319 | 61.2579 | -122.4701
938.4062 | 122.5662 | -61.2213 | 61.084 | 0.013046 | -0.034321 | 0.1121 | 0.027792 | 0.052442 | -0.02139 | -0.021215 | 0.014954 | 0.00055335 | 0.041107 | 0.060067 | -0.016586 | -0.014249 | 61.1572 | -61.0703 | -0.050354 | -61.2946 | 61.1114 | -61.2808 | -61.1938 | -61.6013 | -0.004578 | -61.5463 | 61.0199 | 61.0748 | -61.1343 | -61.3403 | -0.05951 | 0.027465 | 0.027466 | 0.15106 | -0.073243 | -0.10071 | 0.073243 | 0.086975 | -0.11902 | -0.064087 | -0.37994 | -0.32501 | -0.20599 | -0.009155 | 122.3328 | 122.3785 | 61.171 | -122.2778 | 122.2412 | 122.2961 | 61.2167 | -122.4243
940.1094 | 122.4792 | -61.2442 | 61.1664 | 0.013046 | -0.03368 | 0.11402 | 0.024374 | 0.051801 | -0.021176 | -0.022283 | 0.0073242 | -0.0013693 | 0.040894 | 0.063271 | -0.013168 | -0.013608 | 61.2534 | -60.9604 | 0.09613 | -61.2076 | 61.1435 | -61.2259 | -61.1435 | -61.5189 | 0.09613 | -61.4822 | 61.0428 | 61.0931 | -61.0886 | -61.2991 | 0.018311 | 0.10071 | -0.022888 | 0.28381 | 0.036621 | -0.064087 | 0.086975 | 0.15564 | -0.054931 | -0.1236 | -0.27466 | -0.23804 | -0.18311 | -0.073242 | 122.3877 | 122.4976 | 61.3403 | -122.3099 | 122.287 | 122.3373 | 61.3403 | -122.4655
941.8906 | 122.5021 | -61.2213 | 61.1526 | 0.0054168 | -0.034962 | 0.1121 | 0.027152 | 0.053083 | -0.022031 | -0.019506 | -0.0003053 | -0.0015829 | 0.043244 | 0.061562 | -0.015518 | -0.01318 | 61.235 | -60.9787 | 0.07782 | -61.1984 | 61.1572 | -61.2213 | -61.1481 | -61.5143 | 0.11444 | -61.4731 | 61.0153 | 61.1343 | -61.0748 | -61.2808 | 0 | 0.073242 | 0.004578 | 0.24261 | 0.022888 | -0.050354 | 0.082397 | 0.14648 | -0.05951 | -0.13733 | -0.29297 | -0.25177 | -0.19226 | -0.018311 | 122.3785 | 122.4564 | 61.2991 | -122.3007 | 122.2366 | 122.3557 | 61.3358 | -122.4335
943.6875 | 122.4747 | -61.2396 | 61.1343 | 0.0054168 | -0.035175 | 0.11381 | 0.029501 | 0.052656 | -0.023953 | -0.022283 | 0.0073242 | -0.0013693 | 0.041962 | 0.061989 | -0.015304 | -0.012753 | 61.1435 | -61.0657 | -0.018311 | -61.2534 | 61.1206 | -61.2671 | -61.1893 | -61.6104 | -0.009155 | -61.5692 | 61.0153 | 61.0931 | -61.1526 | -61.3312 | -0.027466 | 0.050354 | -0.013733 | 0.17395 | -0.013733 | -0.064087 | 0.009156 | 0.086975 | -0.091553 | -0.11902 | -0.37079 | -0.32959 | -0.23804 | -0.041198 | 122.3602 | 122.3831 | 61.2213 | -122.3236 | 122.2549 | 122.3328 | 61.2305 | -122.4655
945.4531 | 122.5067 | -61.2122 | 61.1389 | -0.0022127 | -0.033466 | 0.11359 | 0.02822 | 0.051801 | -0.023953 | -0.02271 | -0.0003053 | -0.0013693 | 0.041748 | 0.061135 | -0.015945 | -0.015744 | 61.2305 | -60.965 | 0.086975 | -61.1984 | 61.1572 | -61.2122 | -61.1618 | -61.5417 | 0.1236 | -61.4548 | 61.0291 | 61.1114 | -61.0703 | -61.2762 | 0 | 0.050354 | 0.018311 | 0.24719 | 0.013733 | -0.036621 | 0.091553 | 0.14191 | -0.064087 | -0.10986 | -0.32959 | -0.24262 | -0.17853 | -0.027466 | 122.3694 | 122.4426 | 61.2991 | -122.3007 | 122.2412 | 122.3236 | 61.3358 | -122.4152
947.1875 | 122.5433 | -61.1664 | 61.1481 | 0.0054168 | -0.038593 | 0.11851 | 0.02822 | 0.050947 | -0.030149 | -0.023565 | 0.0073242 | -0.0052145 | 0.040467 | 0.058358 | -0.019576 | -0.011471 | 61.203 | -60.9558 | 0.032043 | -61.2167 | 61.0703 | -61.2167 | -61.1252 | -61.5692 | 0.050354 | -61.4319 | 60.9924 | 61.0931 | -61.0886 | -61.2717 | -0.050354 | 0.041199 | -0.07782 | 0.21057 | -0.050354 | -0.091553 | 0.054932 | 0.07782 | -0.10529 | -0.15564 | -0.40283 | -0.2655 | -0.16022 | -0.054931 | 122.2366 | 122.3694 | 61.1984 | -122.2733 | 122.1588 | 122.2595 | 61.2167 | -122.4197
948.9688 | 122.5204 | -61.1572 | 61.1755 | 0.0054168 | -0.034107 | 0.11423 | 0.02886 | 0.051374 | -0.022244 | -0.022924 | 0.0073242 | -0.0028647 | 0.041962 | 0.059853 | -0.014663 | -0.013821 | 61.2259 | -60.9741 | 0.054932 | -61.1755 | 61.1755 | -61.2259 | -61.1114 | -61.5509 | 0.10071 | -61.4594 | 61.0519 | 61.1252 | -61.0703 | -61.3083 | -0.068664 | 0.045777 | 0 | 0.18311 | -0.01831 | -0.064087 | 0.050354 | 0.086976 | -0.15106 | -0.1236 | -0.39368 | -0.30212 | -0.15106 | -0.050354 | 122.3328 | 122.3831 | 61.2122 | -122.287 | 122.2092 | 122.2824 | 61.2579 | -122.4838
950.7344 | 122.4701 | -61.203 | 61.1664 | 0.0054168 | -0.032612 | 0.11316 | 0.02886 | 0.052229 | -0.022458 | -0.021001 | 0.022583 | -0.00051485 | 0.044312 | 0.06028 | -0.01509 | -0.015103 | 61.2396 | -60.9512 | 0.082397 | -61.1984 | 61.1664 | -61.2259 | -61.116 | -61.528 | 0.11902 | -61.4685 | 61.0291 | 61.1069 | -61.0931 | -61.3083 | -0.022888 | 0.086975 | 0 | 0.25177 | 0.004578 | -0.082397 | 0.073242 | 0.10986 | -0.10529 | -0.13733 | -0.32501 | -0.2655 | -0.16022 | -0.059509 | 122.3694 | 122.4426 | 61.2854 | -122.2824 | 122.2321 | 122.3099 | 61.322 | -122.4747
952.5 | 122.4884 | -61.2076 | 61.1481 | 0.013046 | -0.033253 | 0.11338 | 0.02822 | 0.051588 | -0.02374 | -0.020788 | -0.0003053 | -0.0015829 | 0.042603 | 0.061562 | -0.014877 | -0.013394 | 61.2305 | -60.9512 | 0.073242 | -61.1893 | 61.1572 | -61.2259 | -61.1252 | -61.5189 | 0.1236 | -61.4594 | 61.0153 | 61.1069 | -61.0794 | -61.2717 | -0.01831 | 0.082398 | 0.009156 | 0.25635 | 0.018311 | -0.064087 | 0.082398 | 0.12817 | -0.064086 | -0.13275 | -0.31128 | -0.25177 | -0.18768 | -0.041198 | 122.3648 | 122.4381 | 61.2808 | -122.2733 | 122.2229 | 122.3145 | 61.3312 | -122.4197
954.2188 | 122.4792 | -61.1984 | 61.1526 | -0.0022127 | -0.03368 | 0.11616 | 0.026297 | 0.052869 | -0.022672 | -0.021856 | 0.0073242 | 0.00012615 | 0.042176 | 0.061348 | -0.015518 | -0.011471 | 61.2122 | -60.965 | 0.059509 | -61.1984 | 61.1298 | -61.2076 | -61.1481 | -61.5189 | 0.13275 | -61.4456 | 61.0382 | 61.116 | -61.0931 | -61.2717 | -0.009156 | 0.050354 | -0.022888 | 0.23346 | 0 | -0.050354 | 0.059509 | 0.10529 | -0.073242 | -0.11444 | -0.32043 | -0.24719 | -0.17395 | -0.036621 | 122.3282 | 122.4106 | 61.2579 | -122.3007 | 122.2366 | 122.3145 | 61.3312 | -122.4243
956 | 122.5891 | -61.203 | 61.0886 | 0.0054168 | -0.034321 | 0.11573 | 0.024588 | 0.049665 | -0.025022 | -0.024206 | -0.0003053 | -0.0015829 | 0.041321 | 0.061562 | -0.016586 | -0.011899 | 61.1389 | -61.0519 | -0.045776 | -61.2717 | 61.1206 | -61.2534 | -61.1984 | -61.6013 | 0 | -61.5143 | 60.9833 | 61.0565 | -61.1298 | -61.3403 | -0.050354 | 0.004578 | 0.032043 | 0.15106 | -0.068664 | -0.073242 | 0.050354 | 0.073242 | -0.13733 | -0.10529 | -0.39825 | -0.31128 | -0.17395 | -0.032043 | 122.3236 | 122.3419 | 61.1572 | -122.287 | 122.1863 | 122.2595 | 61.203 | -122.4289
957.7031 | 122.4335 | -61.2305 | 61.1618 | -0.0022127 | -0.035816 | 0.11487 | 0.028433 | 0.052015 | -0.021604 | -0.022283 | -0.0003053 | 0.00012615 | 0.044525 | 0.061348 | -0.015518 | -0.013821 | 61.1755 | -61.0291 | -0.009155 | -61.2534 | 61.1252 | -61.2305 | -61.1893 | -61.615 | 0.013733 | -61.5463 | 61.0107 | 61.0794 | -61.1206 | -61.3266 | 0 | 0.041199 | -0.036621 | 0.20142 | -0.022888 | -0.064087 | 0.013733 | 0.10986 | -0.09613 | -0.15106 | -0.38452 | -0.31586 | -0.21973 | -0.082397 | 122.3557 | 122.406 | 61.2213 | -122.3511 | 122.2412 | 122.3099 | 61.2442 | -122.4884
959.4844 | 122.4792 | -61.2167 | 61.1114 | -0.0022127 | -0.033253 | 0.11445 | 0.028433 | 0.049879 | -0.022031 | -0.025915 | 0.014954 | -8.7654e-05 | 0.041535 | 0.061776 | -0.014022 | -0.011685 | 61.1481 | -61.0153 | 0 | -61.2534 | 61.1298 | -61.235 | -61.1984 | -61.5967 | 0.018311 | -61.5509 | 60.997 | 61.1114 | -61.1435 | -61.322 | -0.01831 | 0.018311 | 0.018311 | 0.20142 | -0.036621 | -0.054932 | 0.036621 | 0.073242 | -0.10529 | -0.11444 | -0.37994 | -0.33417 | -0.22888 | 0 | 122.3465 | 122.3648 | 61.2167 | -122.3099 | 122.2137 | 122.3282 | 61.235 | -122.4335
961.2188 | 122.4701 | -61.1526 | 61.1893 | 0.0054168 | -0.03368 | 0.11616 | 0.029929 | 0.051374 | -0.026517 | -0.026128 | 0.0073242 | -0.0015829 | 0.043885 | 0.060067 | -0.020431 | -0.012326 | 61.2213 | -60.9467 | 0.073242 | -61.1526 | 61.1801 | -61.1572 | -61.084 | -61.5509 | 0.082397 | -61.4319 | 61.0886 | 61.1755 | -61.0474 | -61.235 | -0.004578 | 0.068665 | -0.009155 | 0.20599 | 0 | -0.068665 | 0.032043 | 0.10529 | -0.082397 | -0.10071 | -0.39825 | -0.27924 | -0.19684 | -0.013733 | 122.3328 | 122.374 | 61.2259 | -122.2733 | 122.2412 | 122.3282 | 61.235 | -122.4243
963 | 122.4747 | -61.1984 | 61.1389 | -0.0022127 | -0.033253 | 0.11423 | 0.025229 | 0.051374 | -0.023099 | -0.023778 | 0.014954 | -8.7654e-05 | 0.041962 | 0.060707 | -0.017013 | -0.012753 | 61.1206 | -61.0931 | -0.07782 | -61.2762 | 61.1343 | -61.2671 | -61.1847 | -61.6379 | -0.036621 | -61.5509 | 61.0062 | 61.0931 | -61.116 | -61.3037 | -0.068665 | 0.013733 | -0.004578 | 0.10529 | -0.07782 | -0.091553 | -0.018311 | 0.082397 | -0.10529 | -0.13275 | -0.43945 | -0.35248 | -0.24719 | -0.045776 | 122.3328 | 122.319 | 61.1206 | -122.3236 | 122.2046 | 122.2916 | 61.1618 | -122.4426
964.7188 | 122.4472 | -61.2076 | 61.116 | 0.0054168 | -0.035602 | 0.11316 | 0.029288 | 0.053724 | -0.023313 | -0.024419 | -0.0003053 | -0.0011557 | 0.042816 | 0.062416 | -0.014877 | -0.013608 | 61.1893 | -60.9879 | 0.018311 | -61.2213 | 61.1481 | -61.2213 | -61.1526 | -61.5692 | 0.036621 | -61.5189 | 61.0199 | 61.1069 | -61.116 | -61.3266 | -0.013732 | 0.054932 | 0.032043 | 0.21973 | -0.013732 | -0.068664 | 0.073242 | 0.091553 | -0.11902 | -0.096131 | -0.36163 | -0.31128 | -0.19226 | -0.009155 | 122.3557 | 122.3969 | 61.2259 | -122.2687 | 122.2275 | 122.3145 | 61.2442 | -122.4426
966.4375 | 122.4747 | -61.1526 | 61.2213 | -0.0022127 | -0.03368 | 0.11722 | 0.029501 | 0.051374 | -0.026944 | -0.023351 | 0.0073242 | -0.0026511 | 0.042816 | 0.061348 | -0.020858 | -0.014249 | 61.1984 | -60.9604 | 0.064087 | -61.1801 | 61.1801 | -61.1755 | -61.1023 | -61.5463 | 0.091553 | -61.441 | 61.0931 | 61.1984 | -61.0428 | -61.2213 | -0.022888 | 0.050354 | -0.041198 | 0.19226 | -0.027466 | -0.07782 | -0.022888 | 0.10986 | -0.068664 | -0.12817 | -0.39368 | -0.28839 | -0.21973 | -0.022888 | 122.3328 | 122.3511 | 61.2167 | -122.3236 | 122.2458 | 122.3511 | 61.2442 | -122.4426
968.1406 | 122.5159 | -61.1572 | 61.1801 | -0.0098417 | -0.031757 | 0.1153 | 0.024802 | 0.051801 | -0.02374 | -0.023778 | 0.014954 | 0.00033975 | 0.042176 | 0.06028 | -0.01509 | -0.014035 | 61.2305 | -60.9512 | 0.086975 | -61.1664 | 61.1801 | -61.203 | -61.1114 | -61.5005 | 0.11902 | -61.4548 | 61.0519 | 61.1252 | -61.0703 | -61.2946 | -0.045776 | 0.045777 | 0 | 0.20599 | -0.009155 | -0.054932 | 0.050354 | 0.086976 | -0.13733 | -0.12817 | -0.34332 | -0.29755 | -0.16022 | -0.054932 | 122.3373 | 122.3877 | 61.2442 | -122.2916 | 122.2092 | 122.2824 | 61.2762 | -122.4747
969.8906 | 122.5983 | -61.1893 | 61.0703 | 0.013046 | -0.035816 | 0.11573 | 0.025656 | 0.053938 | -0.025022 | -0.025487 | 0.0073242 | -0.0043601 | 0.042389 | 0.062844 | -0.015945 | -0.013821 | 61.1664 | -61.0062 | -0.036621 | -61.235 | 61.1069 | -61.235 | -61.1572 | -61.528 | 0.064087 | -61.4639 | 60.9558 | 61.0336 | -61.0977 | -61.29 | -0.045776 | 0.032043 | 0.036622 | 0.1831 | -0.045776 | -0.077819 | 0.096131 | 0.091553 | -0.10071 | -0.11444 | -0.33875 | -0.27466 | -0.17395 | -0.036621 | 122.2961 | 122.3557 | 61.1526 | -122.2275 | 122.1451 | 122.2229 | 61.2534 | -122.3602
971.6094 | 122.5891 | -61.1847 | 61.116 | -0.0022127 | -0.03603 | 0.11466 | 0.026938 | 0.048597 | -0.024381 | -0.023351 | 0.014954 | -0.0045737 | 0.042816 | 0.061776 | -0.014663 | -0.014462 | 61.1572 | -61.0428 | -0.059509 | -61.2625 | 61.1023 | -61.2488 | -61.1572 | -61.5646 | 0.009155 | -61.4639 | 60.9879 | 61.0565 | -61.1206 | -61.322 | -0.064087 | 0.027465 | -0.013733 | 0.14191 | -0.07782 | -0.10529 | 0.041199 | 0.064087 | -0.13733 | -0.12817 | -0.37994 | -0.27924 | -0.14191 | -0.059509 | 122.287 | 122.3419 | 61.1252 | -122.2733 | 122.1725 | 122.2412 | 61.1938 | -122.438
973.3125 | 122.5845 | -61.1206 | 61.1481 | -0.0022127 | -0.037739 | 0.1168 | 0.029074 | 0.053724 | -0.030149 | -0.025701 | 0.0073242 | -0.0043601 | 0.039826 | 0.061348 | -0.019149 | -0.010403 | 61.1893 | -60.9512 | 0.018311 | -61.1893 | 61.1206 | -61.1755 | -61.1114 | -61.5326 | 0.041199 | -61.4227 | 61.0153 | 61.1023 | -61.0382 | -61.2534 | -0.054932 | 0.009155 | -0.027466 | 0.16937 | -0.068665 | -0.07782 | 0.041199 | 0.082397 | -0.13275 | -0.13275 | -0.41199 | -0.30212 | -0.16937 | -0.045776 | 122.2412 | 122.3099 | 61.1389 | -122.2595 | 122.1359 | 122.2229 | 61.1618 | -122.4014
975.0781 | 122.5433 | -61.1572 | 61.1298 | 0.0054168 | -0.03902 | 0.11423 | 0.025443 | 0.05351 | -0.026517 | -0.025701 | 0.014954 | -0.0045737 | 0.04068 | 0.060067 | -0.016372 | -0.014249 | 61.235 | -60.8963 | 0.041199 | -61.1847 | 61.0657 | -61.203 | -61.1252 | -61.4914 | 0.07782 | -61.3907 | 60.9924 | 61.0428 | -61.0657 | -61.2488 | -0.045776 | 0.032044 | -0.064087 | 0.26093 | -0.027465 | -0.059509 | 0.10528 | 0.091553 | -0.091552 | -0.13733 | -0.33417 | -0.23346 | -0.14191 | -0.086975 | 122.2229 | 122.3923 | 61.1984 | -122.2549 | 122.1497 | 122.2 | 61.235 | -122.3785
976.7969 | 122.4701 | -61.1069 | 61.2076 | 0.013046 | -0.035816 | 0.11701 | 0.027152 | 0.053083 | -0.027585 | -0.025701 | 0.0073242 | -0.0043601 | 0.042816 | 0.058144 | -0.017227 | -0.01553 | 61.3083 | -60.8139 | 0.16937 | -61.1023 | 61.1572 | -61.1343 | -61.0519 | -61.4182 | 0.17395 | -61.322 | 61.0519 | 61.1114 | -61.0199 | -61.203 | -0.027465 | 0.054932 | -0.050354 | 0.29297 | 0.004578 | -0.050354 | 0.10071 | 0.086976 | -0.09613 | -0.15564 | -0.31128 | -0.21515 | -0.11902 | -0.096131 | 122.2641 | 122.4152 | 61.2762 | -122.2595 | 122.1588 | 122.2183 | 61.2808 | -122.4106
978.5781 | 122.4655 | -61.1893 | 61.1526 | 0.013046 | -0.030475 | 0.11338 | 0.02822 | 0.05351 | -0.020108 | -0.024206 | -0.0003053 | 0.0022623 | 0.042389 | 0.060494 | -0.014022 | -0.015958 | 61.1801 | -61.0245 | -0.018311 | -61.2396 | 61.1389 | -61.2167 | -61.1526 | -61.5829 | -0.009155 | -61.5189 | 61.0245 | 61.0794 | -61.0977 | -61.2946 | -0.027466 | 0.036621 | -0.013733 | 0.16479 | -0.050354 | -0.086975 | 0.027466 | 0.091553 | -0.10529 | -0.12817 | -0.39368 | -0.32959 | -0.2243 | -0.073242 | 122.3282 | 122.3694 | 61.171 | -122.3053 | 122.2137 | 122.2687 | 61.1801 | -122.4472
980.2969 | 122.4701 | -61.1206 | 61.2534 | -0.0022127 | -0.037311 | 0.11786 | 0.027579 | 0.050733 | -0.025876 | -0.022924 | -0.0003053 | -0.0028647 | 0.042389 | 0.060067 | -0.018295 | -0.011899 | 61.235 | -60.91 | 0.07782 | -61.1572 | 61.2167 | -61.1893 | -61.0886 | -61.528 | 0.07782 | -61.4273 | 61.0977 | 61.1893 | -61.0519 | -61.2259 | -0.068665 | 0.032043 | -0.036621 | 0.21057 | -0.036622 | -0.068665 | -0.018311 | 0.068664 | -0.10529 | -0.15564 | -0.40741 | -0.3067 | -0.20142 | -0.064087 | 122.3373 | 122.3557 | 61.1984 | -122.3419 | 122.2183 | 122.3099 | 61.1984 | -122.4792
982.0938 | 122.5388 | -61.1435 | 61.1526 | -0.0022127 | -0.03838 | 0.11487 | 0.02587 | 0.051588 | -0.028012 | -0.024419 | 0.0073242 | -0.0060691 | 0.044098 | 0.060921 | -0.017013 | -0.01254 | 61.2488 | -60.9009 | 0.059509 | -61.1801 | 61.0977 | -61.1847 | -61.116 | -61.4868 | 0.064087 | -61.409 | 60.9833 | 61.0565 | -61.0657 | -61.2579 | -0.041198 | 0.027466 | -0.054932 | 0.24261 | -0.036621 | -0.064087 | 0.09613 | 0.07782 | -0.11444 | -0.16937 | -0.34332 | -0.2655 | -0.15106 | -0.09613 | 122.2412 | 122.3923 | 61.203 | -122.2687 | 122.1268 | 122.2 | 61.2076 | -122.4106
983.7969 | 122.5845 | -61.1481 | 61.1114 | 0.013046 | -0.037098 | 0.11551 | 0.023734 | 0.052869 | -0.02374 | -0.024633 | 0.0073242 | -0.0026511 | 0.03833 | 0.059853 | -0.016372 | -0.014889 | 61.2396 | -60.9421 | -0.004578 | -61.1664 | 61.0886 | -61.2213 | -61.1298 | -61.496 | 0.068665 | -61.4273 | 60.9512 | 61.0016 | -61.0886 | -61.2579 | -0.073242 | 0.01831 | -0.022888 | 0.20599 | -0.018311 | -0.036621 | 0.12817 | 0.059509 | -0.10986 | -0.16022 | -0.3479 | -0.27924 | -0.16937 | -0.10986 | 122.2366 | 122.3877 | 61.1435 | -122.2412 | 122.0993 | 122.1497 | 61.2167 | -122.3694
985.5625 | 122.4838 | -61.1847 | 61.1481 | 0.0054168 | -0.036671 | 0.11487 | 0.026938 | 0.052656 | -0.022672 | -0.021215 | -0.0079343 | 0.00055335 | 0.041962 | 0.061562 | -0.01509 | -0.011899 | 61.1389 | -61.0748 | -0.073242 | -61.2442 | 61.1618 | -61.2122 | -61.171 | -61.5921 | -0.027466 | -61.5372 | 60.997 | 61.0886 | -61.0931 | -61.2946 | -0.027466 | 0.013733 | 0.013733 | 0.10986 | -0.05951 | -0.073243 | -0.009155 | 0.091552 | -0.10986 | -0.15106 | -0.40741 | -0.35248 | -0.24261 | -0.059509 | 122.3465 | 122.3236 | 61.1114 | -122.319 | 122.1817 | 122.2733 | 61.1572 | -122.4426
987.2812 | 122.5113 | -61.1618 | 61.0977 | 0.013046 | -0.036457 | 0.11573 | 0.025656 | 0.049879 | -0.021176 | -0.021856 | 0.022583 | -0.00094205 | 0.042816 | 0.06263 | -0.014877 | -0.01318 | 61.1526 | -61.0291 | -0.082397 | -61.2442 | 61.1252 | -61.2442 | -61.1664 | -61.5692 | -0.027466 | -61.5234 | 61.0245 | 61.0886 | -61.1114 | -61.3083 | -0.082398 | -0.004578 | 0.027466 | 0.13275 | -0.082398 | -0.07782 | 0.054932 | 0.050354 | -0.14649 | -0.073242 | -0.40741 | -0.36163 | -0.21515 | -0.009155 | 122.287 | 122.3145 | 61.0794 | -122.2641 | 122.1863 | 122.2504 | 61.1343 | -122.406
988.9844 | 122.5571 | -61.1343 | 61.1572 | -0.0022127 | -0.041157 | 0.11445 | 0.026297 | 0.051374 | -0.027799 | -0.022283 | -0.0003053 | -0.0026511 | 0.041107 | 0.061135 | -0.019149 | -0.012967 | 61.2305 | -60.878 | 0.050354 | -61.1664 | 61.0657 | -61.1938 | -61.1526 | -61.4777 | 0.086975 | -61.3815 | 60.9604 | 61.0611 | -61.0565 | -61.2396 | -0.05951 | -0.018311 | -0.091553 | 0.25635 | -0.032044 | -0.013733 | 0.073242 | 0.077819 | -0.10529 | -0.19684 | -0.34332 | -0.24719 | -0.14191 | -0.096131 | 122.2 | 122.3648 | 61.1847 | -122.3099 | 122.0947 | 122.1954 | 61.2213 | -122.3969
990.75 | 122.5296 | -61.1435 | 61.171 | -0.0098417 | -0.041797 | 0.11957 | 0.026297 | 0.053938 | -0.028867 | -0.027624 | 0.0073242 | -0.0054281 | 0.04068 | 0.058571 | -0.01744 | -0.011471 | 61.2259 | -60.8917 | 0.022888 | -61.1801 | 61.1298 | -61.1664 | -61.1069 | -61.5051 | 0.050354 | -61.4044 | 61.0107 | 61.0703 | -61.0428 | -61.2396 | -0.022888 | 0.036621 | -0.041198 | 0.25177 | -0.036621 | -0.073242 | 0.054932 | 0.10071 | -0.09613 | -0.16022 | -0.36163 | -0.26093 | -0.16479 | -0.10071 | 122.2733 | 122.3694 | 61.1664 | -122.2778 | 122.1542 | 122.2137 | 61.1938 | -122.4106
992.4688 | 122.4747 | -61.1298 | 61.235 | -0.0022127 | -0.036243 | 0.1153 | 0.026724 | 0.052442 | -0.02374 | -0.025487 | -0.0003053 | -0.0013693 | 0.042603 | 0.060707 | -0.017013 | -0.015103 | 61.2488 | -60.8871 | 0.068665 | -61.1572 | 61.2122 | -61.1389 | -61.0931 | -61.5051 | 0.064087 | -61.4227 | 61.1206 | 61.1893 | -61.0199 | -61.2305 | -0.009155 | 0.036621 | -0.022888 | 0.24262 | -0.027466 | -0.064087 | 0.013733 | 0.10986 | -0.10071 | -0.11444 | -0.37537 | -0.29297 | -0.19226 | -0.045776 | 122.3419 | 122.3785 | 61.1984 | -122.3282 | 122.2504 | 122.319 | 61.1938 | -122.4655
994.1875 | 122.5342 | -61.1114 | 61.1801 | 0.0054168 | -0.039448 | 0.11509 | 0.027365 | 0.051161 | -0.025449 | -0.02271 | 0.0073242 | -0.0054281 | 0.040253 | 0.060067 | -0.017013 | -0.012967 | 61.2488 | -60.8551 | 0.036621 | -61.1618 | 61.0977 | -61.171 | -61.1023 | -61.4685 | 0.068665 | -61.377 | 60.965 | 61.0565 | -61.0428 | -61.235 | -0.059509 | 0.009155 | -0.082398 | 0.25635 | -0.050354 | -0.059509 | 0.068664 | 0.068664 | -0.1236 | -0.21515 | -0.35706 | -0.2655 | -0.14191 | -0.1236 | 122.2092 | 122.3602 | 61.1481 | -122.2824 | 122.0764 | 122.168 | 61.1801 | -122.4152
995.9531 | 122.58 | -61.1343 | 61.1114 | -0.0022127 | -0.038807 | 0.11701 | 0.023734 | 0.054578 | -0.022885 | -0.023992 | 0.022583 | -0.0037191 | 0.039398 | 0.059426 | -0.014877 | -0.014249 | 61.2671 | -60.878 | 0.022888 | -61.1572 | 61.1114 | -61.2076 | -61.084 | -61.4639 | 0.073242 | -61.3907 | 60.9833 | 61.0291 | -61.0611 | -61.2213 | -0.073243 | 0.050354 | 0 | 0.25635 | -0.022889 | -0.073243 | 0.15564 | 0.073242 | -0.086975 | -0.12817 | -0.32959 | -0.25635 | -0.16937 | -0.082397 | 122.2458 | 122.4014 | 61.1572 | -122.1954 | 122.1176 | 122.1634 | 61.2076 | -122.3328
997.7188 | 122.5342 | -61.1481 | 61.116 | 0.0054168 | -0.038807 | 0.11658 | 0.024374 | 0.052869 | -0.023099 | -0.023565 | 0.0073242 | -0.0035055 | 0.041535 | 0.058571 | -0.014877 | -0.014676 | 61.2579 | -60.8597 | 0.027466 | -61.1526 | 61.1023 | -61.1938 | -61.1206 | -61.4502 | 0.068665 | -61.3907 | 60.9879 | 61.0382 | -61.0565 | -61.2534 | -0.045777 | 0.027466 | -0.013733 | 0.28839 | -0.004578 | -0.032044 | 0.14191 | 0.091552 | -0.10529 | -0.12817 | -0.30212 | -0.24262 | -0.13733 | -0.07782 | 122.2504 | 122.406 | 61.1755 | -122.2366 | 122.1359 | 122.1863 | 61.2167 | -122.3694
999.4844 | 122.4243 | -61.171 | 61.1618 | 0.013046 | -0.032825 | 0.11509 | 0.027792 | 0.051161 | -0.020322 | -0.022497 | -0.0079343 | -0.00072845 | 0.042603 | 0.061348 | -0.014663 | -0.01254 | 61.2488 | -60.9009 | 0.013733 | -61.1618 | 61.1618 | -61.1938 | -61.1114 | -61.5234 | 0.018311 | -61.4868 | 61.0565 | 61.1023 | -61.0611 | -61.2717 | -0.022889 | 0.059509 | 0 | 0.27008 | 0.009155 | -0.050354 | 0.086975 | 0.10986 | -0.10071 | -0.10528 | -0.35248 | -0.31586 | -0.21515 | -0.059509 | 122.3328 | 122.4197 | 61.1847 | -122.2733 | 122.2275 | 122.2733 | 61.1893 | -122.4335
1001.2188 | 122.4335 | -61.1114 | 61.2488 | -0.0022127 | -0.035816 | 0.11359 | 0.029715 | 0.052015 | -0.026944 | -0.022283 | 0.0073242 | -0.0041465 | 0.04303 | 0.062203 | -0.019576 | -0.013821 | 61.3037 | -60.7636 | 0.12817 | -61.0703 | 61.1938 | -61.0977 | -61.0382 | -61.409 | 0.14648 | -61.3358 | 61.0794 | 61.1435 | -61.0016 | -61.1893 | 0.013733 | 0.073242 | -0.054931 | 0.3479 | 0.041199 | -0.032043 | 0.054932 | 0.10986 | -0.07782 | -0.16937 | -0.29755 | -0.2243 | -0.14648 | -0.10529 | 122.3053 | 122.4152 | 61.2396 | -122.287 | 122.1909 | 122.2549 | 61.2579 | -122.438
1002.9844 | 122.5204 | -61.1114 | 61.1572 | 0.0054168 | -0.042225 | 0.11573 | 0.025015 | 0.050092 | -0.030576 | -0.022497 | 0.014954 | -0.0071371 | 0.041748 | 0.060494 | -0.017013 | -0.012326 | 61.235 | -60.8643 | 0.009155 | -61.1526 | 61.1389 | -61.1206 | -61.0703 | -61.4914 | 0.045776 | -61.3724 | 61.0519 | 61.1114 | -61.0245 | -61.2076 | -0.009155 | 0.041199 | -0.018311 | 0.24719 | -0.041199 | -0.082398 | 0.077819 | 0.086975 | -0.096131 | -0.10529 | -0.37994 | -0.26093 | -0.16479 | -0.045777 | 122.2504 | 122.3465 | 61.1206 | -122.2275 | 122.1634 | 122.2229 | 61.1572 | -122.3648
1004.7656 | 122.5708 | -61.1298 | 61.116 | 0.0054168 | -0.036884 | 0.11573 | 0.023734 | 0.054151 | -0.022672 | -0.021001 | 0.0073242 | -0.0020103 | 0.042176 | 0.058999 | -0.015731 | -0.014889 | 61.203 | -60.9558 | -0.086975 | -61.203 | 61.1664 | -61.1893 | -61.1298 | -61.5097 | -0.032043 | -61.4685 | 61.0336 | 61.0794 | -61.0794 | -61.2396 | -0.059509 | 0 | 0.050354 | 0.17395 | -0.073242 | -0.073242 | 0.086975 | 0.050354 | -0.10986 | -0.082398 | -0.37994 | -0.33874 | -0.22888 | -0.036621 | 122.2961 | 122.3328 | 61.0428 | -122.2458 | 122.1634 | 122.2092 | 61.0977 | -122.3557
1006.5312 | 122.4472 | -61.1664 | 61.1618 | -0.017471 | -0.033253 | 0.11338 | 0.026297 | 0.052869 | -0.020108 | -0.021429 | 0.0073242 | 0.00055335 | 0.044953 | 0.062844 | -0.016372 | -0.014889 | 61.2259 | -60.9512 | -0.064087 | -61.1755 | 61.171 | -61.2076 | -61.1069 | -61.5097 | 0.009155 | -61.4822 | 61.0519 | 61.1435 | -61.0474 | -61.2442 | -0.041199 | 0.059509 | 0.009155 | 0.21515 | -0.009155 | -0.068664 | 0.064087 | 0.11902 | -0.07782 | -0.10986 | -0.34332 | -0.31586 | -0.23804 | -0.01831 | 122.3373 | 122.3923 | 61.1023 | -122.2687 | 122.2183 | 122.3099 | 61.1755 | -122.406
1008.3281 | 122.4426 | -61.1435 | 61.2122 | 0.0054168 | -0.033893 | 0.1153 | 0.02587 | 0.051374 | -0.022672 | -0.023138 | -0.0003053 | 0.0011941 | 0.042389 | 0.059853 | -0.013381 | -0.014462 | 61.1938 | -60.9604 | -0.054932 | -61.1893 | 61.1755 | -61.1847 | -61.1069 | -61.528 | -0.013733 | -61.4914 | 61.0565 | 61.1389 | -61.0565 | -61.2717 | -0.041198 | 0.036621 | -0.036621 | 0.18311 | -0.045776 | -0.082397 | -0.01831 | 0.086975 | -0.12817 | -0.15564 | -0.38452 | -0.3479 | -0.21973 | -0.073242 | 122.319 | 122.3373 | 61.0886 | -122.319 | 122.2 | 122.2824 | 61.1298 | -122.4838
1010.0469 | 122.5754 | -61.0519 | 61.203 | 0.013046 | -0.03838 | 0.11786 | 0.029929 | 0.051801 | -0.031003 | -0.025274 | 0.014954 | -0.0050009 | 0.041748 | 0.058358 | -0.021499 | -0.013394 | 61.3129 | -60.759 | 0.073242 | -61.0565 | 61.1801 | -61.1069 | -61.0153 | -61.3907 | 0.15106 | -61.2442 | 61.0703 | 61.1572 | -60.9604 | -61.1618 | -0.054932 | 0.036621 | -0.022888 | 0.29297 | -0.004578 | -0.041199 | 0.10986 | 0.091553 | -0.10986 | -0.13275 | -0.33875 | -0.19226 | -0.082398 | -0.045776 | 122.2321 | 122.3648 | 61.1252 | -122.2183 | 122.1222 | 122.2092 | 61.203 | -122.3648
1011.8125 | 122.438 | -61.0931 | 61.2534 | -0.0022127 | -0.032825 | 0.11445 | 0.029288 | 0.050733 | -0.026303 | -0.025915 | 0.0073242 | -0.0015829 | 0.044953 | 0.060494 | -0.016799 | -0.016171 | 61.2579 | -60.8231 | 0.009155 | -61.116 | 61.2488 | -61.1206 | -61.0291 | -61.4502 | 0.068665 | -61.3861 | 61.1481 | 61.2076 | -60.9741 | -61.1755 | -0.027465 | 0.064087 | -0.004578 | 0.27008 | -0.022888 | -0.086975 | 0.004578 | 0.11902 | -0.082397 | -0.10529 | -0.35706 | -0.29297 | -0.21057 | -0.045776 | 122.3419 | 122.3511 | 61.1023 | -122.2824 | 122.2412 | 122.3007 | 61.1618 | -122.4289
1013.5312 | 122.4884 | -61.0977 | 61.235 | -0.0022127 | -0.034107 | 0.11252 | 0.029074 | 0.052869 | -0.022458 | -0.022924 | 0.0073242 | -0.00072845 | 0.043885 | 0.061989 | -0.015945 | -0.014249 | 61.2991 | -60.8505 | -0.004578 | -61.0794 | 61.2442 | -61.1526 | -61.0565 | -61.4182 | 0.091553 | -61.3724 | 61.1114 | 61.1755 | -60.9924 | -61.1847 | -0.054932 | 0.041198 | 0.009156 | 0.24719 | 0.01831 | -0.022888 | 0.064087 | 0.10529 | -0.086975 | -0.1236 | -0.32043 | -0.27466 | -0.18768 | -0.059509 | 122.3419 | 122.3969 | 61.0931 | -122.2916 | 122.2092 | 122.2733 | 61.1893 | -122.4197
1015.25 | 122.4426 | -61.0748 | 61.2717 | -0.0022127 | -0.03368 | 0.11765 | 0.028006 | 0.052442 | -0.027585 | -0.024206 | 0.014954 | -0.0054281 | 0.041962 | 0.059853 | -0.018936 | -0.013608 | 61.3358 | -60.7315 | 0.086975 | -61.0382 | 61.203 | -61.084 | -61.0199 | -61.3724 | 0.17853 | -61.2717 | 61.1114 | 61.1801 | -60.9467 | -61.1343 | -0.009155 | 0.054932 | -0.068664 | 0.34332 | 0.036621 | -0.018311 | 0.064087 | 0.12817 | -0.059509 | -0.16022 | -0.29755 | -0.19684 | -0.13733 | -0.091552 | 122.2778 | 122.4106 | 61.1618 | -122.2916 | 122.1863 | 122.2549 | 61.2534 | -122.406
1017.0312 | 122.4426 | -61.116 | 61.1938 | -0.0022127 | -0.034748 | 0.11573 | 0.02352 | 0.051588 | -0.020963 | -0.023351 | 0.0073242 | -0.0028647 | 0.041535 | 0.06028 | -0.013809 | -0.014462 | 61.3129 | -60.8047 | -0.004578 | -61.0886 | 61.203 | -61.1206 | -61.0565 | -61.4044 | 0.10071 | -61.3586 | 61.1069 | 61.1755 | -61.0062 | -61.1893 | -0.004577 | 0.059509 | 0.009155 | 0.31128 | 0.027466 | -0.032043 | 0.11902 | 0.10986 | -0.073242 | -0.086975 | -0.28839 | -0.24262 | -0.16937 | -0.018311 | 122.319 | 122.4289 | 61.1114 | -122.2504 | 122.2229 | 122.2916 | 61.2167 | -122.3831
1018.8125 | 122.4884 | -61.0931 | 61.235 | 0.0054168 | -0.034748 | 0.11701 | 0.029501 | 0.050306 | -0.025662 | -0.022924 | -0.0003053 | -0.0011557 | 0.042389 | 0.061989 | -0.015518 | -0.010831 | 61.2762 | -60.8459 | -0.027466 | -61.1023 | 61.2488 | -61.1389 | -61.0199 | -61.4594 | 0.059509 | -61.3861 | 61.1252 | 61.203 | -60.9741 | -61.1664 | -0.045776 | 0.073243 | 0.013733 | 0.24719 | -0.009155 | -0.082398 | 0.041199 | 0.11902 | -0.073242 | -0.10986 | -0.36621 | -0.29297 | -0.21973 | -0.032043 | 122.3419 | 122.3694 | 61.0657 | -122.2549 | 122.2183 | 122.2961 | 61.1526 | -122.4014
1020.5469 | 122.438 | -61.0565 | 61.3037 | 0.020676 | -0.03603 | 0.11658 | 0.027792 | 0.052015 | -0.028653 | -0.02506 | 0.0073242 | -0.0054281 | 0.042176 | 0.056862 | -0.017227 | -0.01318 | 61.3358 | -60.7361 | 0.068665 | -61.0199 | 61.1893 | -61.0703 | -60.9833 | -61.377 | 0.14191 | -61.2717 | 61.116 | 61.203 | -60.9467 | -61.1572 | -0.013732 | 0.073243 | -0.11444 | 0.32044 | 0.036622 | -0.036621 | 0.032043 | 0.10986 | -0.10071 | -0.18768 | -0.32043 | -0.21515 | -0.11444 | -0.10071 | 122.2458 | 122.3923 | 61.1252 | -122.287 | 122.1725 | 122.2595 | 61.1984 | -122.4609
1022.2812 | 122.4609 | -61.0657 | 61.2762 | 0.0054168 | -0.037311 | 0.11722 | 0.02352 | 0.051161 | -0.026731 | -0.024847 | -0.0003053 | -0.0024375 | 0.041962 | 0.060494 | -0.015731 | -0.014035 | 61.2762 | -60.8276 | -0.041199 | -61.1069 | 61.2946 | -61.1069 | -61.0107 | -61.4548 | 0.036621 | -61.3541 | 61.1664 | 61.2442 | -60.9467 | -61.171 | -0.041199 | 0.054932 | 0.018311 | 0.23804 | -0.041199 | -0.096131 | 0 | 0.11902 | -0.10529 | -0.10986 | -0.3891 | -0.28839 | -0.18311 | -0.032043 | 122.3602 | 122.3419 | 61.0245 | -122.287 | 122.2321 | 122.3099 | 61.1023 | -122.4472
1024.0625 | 122.525 | -61.084 | 61.1847 | -0.0022127 | -0.037098 | 0.11616 | 0.025229 | 0.052229 | -0.025876 | -0.020147 | 0.0073242 | -0.0056419 | 0.04068 | 0.058999 | -0.014236 | -0.014462 | 61.2808 | -60.791 | -0.068665 | -61.0931 | 61.1114 | -61.1435 | -61.0611 | -61.3998 | 0.054932 | -61.3266 | 61.0336 | 61.0931 | -61.0199 | -61.1801 | -0.05951 | 0.022888 | -0.073242 | 0.29297 | -0.009156 | -0.032044 | 0.096131 | 0.064087 | -0.096131 | -0.15106 | -0.31586 | -0.24262 | -0.14648 | -0.091552 | 122.1954 | 122.3648 | 61.0153 | -122.2458 | 122.1176 | 122.1771 | 61.1389 | -122.3648
1025.8438 | 122.5845 | -61.0107 | 61.235 | 0.0054168 | -0.037525 | 0.11722 | 0.029288 | 0.050947 | -0.030149 | -0.024633 | 0.0073242 | -0.0050009 | 0.040253 | 0.059853 | -0.018295 | -0.012967 | 61.3449 | -60.7315 | -0.013733 | -61.0291 | 61.2076 | -61.0794 | -60.9833 | -61.3495 | 0.10071 | -61.2259 | 61.1069 | 61.1572 | -60.9329 | -61.116 | -0.068665 | 0.027466 | -0.027465 | 0.27924 | -0.018311 | -0.045777 | 0.10986 | 0.07782 | -0.10529 | -0.12817 | -0.33875 | -0.21515 | -0.10986 | -0.077819 | 122.2183 | 122.3557 | 60.997 | -122.2183 | 122.1176 | 122.168 | 61.1114 | -122.3511
1027.6406 | 122.438 | -61.0291 | 61.2717 | -0.0022127 | -0.038593 | 0.11423 | 0.028433 | 0.050733 | -0.023313 | -0.024847 | -0.0079343 | -0.0011557 | 0.042176 | 0.059853 | -0.017227 | -0.014889 | 61.3037 | -60.8231 | -0.036621 | -61.0794 | 61.2717 | -61.0794 | -61.0245 | -61.4227 | 0.036621 | -61.3541 | 61.2259 | 61.2488 | -60.9375 | -61.1252 | -0.050354 | 0.004578 | 0 | 0.20599 | -0.050354 | -0.054932 | 0.032044 | 0.091553 | -0.09613 | -0.045776 | -0.39368 | -0.32501 | -0.22888 | -0.022888 | 122.3007 | 122.3328 | 60.9924 | -122.2961 | 122.2549 | 122.2778 | 61.0657 | -122.3969
1029.3438 | 122.5754 | -61.0199 | 61.2625 | 0.0054168 | -0.035816 | 0.1168 | 0.027792 | 0.052656 | -0.027371 | -0.026769 | 0.0073242 | -0.0035055 | 0.042176 | 0.058999 | -0.01744 | -0.015103 | 61.3724 | -60.6857 | 0.068665 | -61.0062 | 61.203 | -61.0382 | -61.0062 | -61.3174 | 0.15564 | -61.1893 | 61.0931 | 61.171 | -60.9238 | -61.1206 | -0.018311 | 0.013732 | -0.059509 | 0.33417 | 0.013732 | 0 | 0.10986 | 0.09613 | -0.10071 | -0.16937 | -0.29755 | -0.16937 | -0.068665 | -0.091553 | 122.2229 | 122.3923 | 61.0886 | -122.2687 | 122.113 | 122.1909 | 61.1755 | -122.3831
1031.125 | 122.4426 | -61.1114 | 61.2076 | 0.0054168 | -0.034107 | 0.11573 | 0.022238 | 0.053083 | -0.020108 | -0.022924 | 0.0073242 | 0.00098055 | 0.040467 | 0.058358 | -0.014449 | -0.014676 | 61.2167 | -60.9283 | -0.14191 | -61.1572 | 61.1984 | -61.1481 | -61.0703 | -61.4822 | -0.07782 | -61.4365 | 61.1023 | 61.1572 | -61.0016 | -61.2213 | -0.036621 | 0.041199 | -0.009156 | 0.1831 | -0.045777 | -0.086976 | 0.009155 | 0.10986 | -0.10986 | -0.10529 | -0.37079 | -0.32501 | -0.21515 | -0.050354 | 122.3099 | 122.3282 | 60.9695 | -122.2778 | 122.2137 | 122.2687 | 61.0336 | -122.4289
1032.8438 | 122.5571 | -60.9741 | 61.2671 | -0.0022127 | -0.037311 | 0.11616 | 0.02587 | 0.049879 | -0.029294 | -0.023351 | -0.0003053 | -0.0043601 | 0.041107 | 0.058999 | -0.018936 | -0.013608 | 61.3815 | -60.6583 | 0.068665 | -61.0153 | 61.203 | -61.0611 | -60.9695 | -61.3129 | 0.12817 | -61.2076 | 61.1114 | 61.1801 | -60.9055 | -61.116 | -0.086975 | 0.004578 | -0.064087 | 0.31586 | -0.041199 | -0.045777 | 0.11444 | 0.068664 | -0.14191 | -0.15564 | -0.33875 | -0.23346 | -0.091553 | -0.086975 | 122.1771 | 122.3557 | 61.0428 | -122.2366 | 122.0856 | 122.1542 | 61.1023 | -122.3831
1034.625 | 122.4701 | -61.0703 | 61.2488 | 0.0054168 | -0.032184 | 0.11316 | 0.029288 | 0.053724 | -0.022458 | -0.023778 | -0.0003053 | 0.00076695 | 0.04303 | 0.061348 | -0.01509 | -0.015317 | 61.3358 | -60.7544 | 0.009155 | -61.0565 | 61.2625 | -61.1069 | -61.0245 | -61.377 | 0.054932 | -61.322 | 61.1298 | 61.1847 | -60.965 | -61.1664 | -0.036622 | 0.045776 | 0.013733 | 0.31586 | 0.013732 | -0.032044 | 0.086975 | 0.10529 | -0.096131 | -0.11902 | -0.3067 | -0.25177 | -0.15564 | -0.064087 | 122.3328 | 122.406 | 61.0794 | -122.2733 | 122.2 | 122.2549 | 61.1252 | -122.4152
1036.3438 | 122.4701 | -61.0611 | 61.2762 | -0.0022127 | -0.032825 | 0.11445 | 0.027365 | 0.049665 | -0.021817 | -0.021642 | 0.0073242 | 0.00012615 | 0.041962 | 0.060067 | -0.01509 | -0.014462 | 61.3312 | -60.7452 | 0.032043 | -61.0474 | 61.2442 | -61.0748 | -61.0062 | -61.3724 | 0.059509 | -61.3266 | 61.1481 | 61.1893 | -60.9375 | -61.1435 | -0.013733 | 0.054931 | -0.032043 | 0.31586 | 0.013733 | -0.041198 | 0.054932 | 0.1236 | -0.082398 | -0.12817 | -0.31128 | -0.2655 | -0.18311 | -0.086975 | 122.3053 | 122.3923 | 61.0931 | -122.2824 | 122.2092 | 122.2504 | 61.1206 | -122.4197
1038.125 | 122.4976 | -61.0153 | 61.2671 | -0.0022127 | -0.032184 | 0.11381 | 0.027579 | 0.052229 | -0.024808 | -0.022069 | 0.0073242 | -0.00072845 | 0.042603 | 0.061348 | -0.018081 | -0.012753 | 61.2991 | -60.7681 | 0.022888 | -61.0428 | 61.2854 | -61.0657 | -61.0107 | -61.3678 | 0.073242 | -61.322 | 61.1847 | 61.2122 | -60.9467 | -61.1343 | -0.050354 | 0.004578 | 0.01831 | 0.24719 | -0.027466 | -0.032044 | 0.032043 | 0.068665 | -0.11902 | -0.082398 | -0.35248 | -0.3067 | -0.18768 | -0.054932 | 122.3007 | 122.3145 | 61.0382 | -122.2778 | 122.2 | 122.2275 | 61.0886 | -122.4014
1039.9062 | 122.5571 | -61.0657 | 61.1664 | 0.013046 | -0.03838 | 0.11445 | 0.026083 | 0.053083 | -0.026731 | -0.01972 | 0.0073242 | -0.0052145 | 0.041535 | 0.060921 | -0.015731 | -0.014676 | 61.3129 | -60.7498 | 0.009155 | -61.0611 | 61.1435 | -61.0977 | -61.0245 | -61.3586 | 0.022888 | -61.2991 | 61.0519 | 61.1298 | -60.9787 | -61.1755 | -0.032043 | 0.041199 | -0.022888 | 0.31586 | 0.004578 | -0.036621 | 0.14648 | 0.086975 | -0.10986 | -0.11444 | -0.29297 | -0.23346 | -0.1236 | -0.036621 | 122.2092 | 122.3785 | 61.0748 | -122.1909 | 122.1176 | 122.1954 | 61.0886 | -122.3419
1041.6875 | 122.5525 | -61.0336 | 61.1893 | 0.013046 | -0.036243 | 0.11551 | 0.026297 | 0.052442 | -0.025022 | -0.024419 | 0.014954 | -0.0013693 | 0.041107 | 0.058785 | -0.017227 | -0.014035 | 61.2854 | -60.7819 | -0.009155 | -61.0748 | 61.1664 | -61.0886 | -61.0336 | -61.3724 | 0 | -61.2991 | 61.0611 | 61.1252 | -60.9604 | -61.1664 | -0.054932 | 0 | -0.022888 | 0.25177 | -0.041199 | -0.041199 | 0.09613 | 0.073242 | -0.13275 | -0.12817 | -0.33874 | -0.2655 | -0.13275 | -0.064087 | 122.2 | 122.319 | 61.0245 | -122.2229 | 122.0947 | 122.1588 | 61.0336 | -122.3557
1043.4688 | 122.4243 | -61.1023 | 61.2305 | 0.013046 | -0.03368 | 0.11402 | 0.024374 | 0.051588 | -0.022031 | -0.022283 | 0.014954 | -0.00072845 | 0.043885 | 0.06028 | -0.013595 | -0.011899 | 61.2442 | -60.8597 | -0.068665 | -61.1206 | 61.235 | -61.0748 | -61.0474 | -61.4685 | -0.10071 | -61.4273 | 61.1206 | 61.171 | -60.9741 | -61.1938 | 0.027466 | 0.054932 | 0.004577 | 0.24262 | -0.01831 | -0.073242 | 0.013733 | 0.12817 | -0.091553 | -0.10986 | -0.36621 | -0.32501 | -0.23346 | -0.05951 | 122.3373 | 122.3465 | 61.0336 | -122.2778 | 122.2229 | 122.2733 | 61.0016 | -122.4243
1045.1875 | 122.4518 | -61.0474 | 61.2625 | -0.0098417 | -0.035602 | 0.11381 | 0.026724 | 0.054792 | -0.023526 | -0.022283 | 0.0073242 | -0.0013693 | 0.042816 | 0.06028 | -0.016158 | -0.01254 | 61.3358 | -60.7315 | 0.07782 | -61.0382 | 61.2579 | -61.0657 | -61.0153 | -61.3541 | 0.064087 | -61.2991 | 61.1572 | 61.2259 | -60.91 | -61.1252 | -0.018311 | 0.032043 | -0.004577 | 0.31586 | 0.009155 | -0.022888 | 0.073242 | 0.13733 | -0.07782 | -0.10529 | -0.3067 | -0.25177 | -0.17395 | -0.036621 | 122.3053 | 122.3831 | 61.1252 | -122.2778 | 122.2046 | 122.2733 | 61.1114 | -122.3877
1046.9688 | 122.5067 | -61.0382 | 61.235 | 0.0054168 | -0.040302 | 0.11744 | 0.028433 | 0.051161 | -0.030576 | -0.022283 | 0.0073242 | -0.0064963 | 0.041321 | 0.059639 | -0.018295 | -0.011899 | 61.3129 | -60.7132 | 0.082397 | -61.0703 | 61.1664 | -61.0657 | -60.9787 | -61.3998 | -0.022888 | -61.2854 | 61.0748 | 61.171 | -60.9283 | -61.1114 | -0.027466 | 0.059509 | -0.068664 | 0.32501 | -0.032043 | -0.091552 | 0.07782 | 0.10986 | -0.073242 | -0.16022 | -0.36163 | -0.24719 | -0.17395 | -0.064087 | 122.2046 | 122.3511 | 61.1206 | -122.2137 | 122.113 | 122.2092 | 61.0153 | -122.3465
1048.75 | 122.4152 | -60.9695 | 61.3495 | 0.0054168 | -0.037098 | 0.11594 | 0.032492 | 0.052442 | -0.027371 | -0.023138 | 0.0073242 | -0.00094205 | 0.044098 | 0.061135 | -0.018722 | -0.014889 | 61.3907 | -60.6262 | 0.2243 | -60.9695 | 61.2671 | -60.9787 | -60.9055 | -61.3266 | 0.073242 | -61.2305 | 61.2076 | 61.235 | -60.9146 | -61.0657 | -0.009156 | 0.064086 | -0.082397 | 0.34332 | 0 | -0.064086 | 0.041199 | 0.054931 | -0.096131 | -0.14191 | -0.35706 | -0.26093 | -0.16479 | -0.11444 | 122.2366 | 122.3602 | 61.1938 | -122.2549 | 122.1771 | 122.2046 | 61.0428 | -122.4152
1050.5312 | 122.5525 | -60.9695 | 61.2991 | 0.013046 | -0.036457 | 0.11658 | 0.029929 | 0.051374 | -0.027371 | -0.025274 | 0.0073242 | -0.0069235 | 0.042389 | 0.060067 | -0.018936 | -0.014249 | 61.3907 | -60.6262 | 0.21973 | -60.965 | 61.2579 | -60.9833 | -60.91 | -61.2946 | 0.086975 | -61.1618 | 61.1572 | 61.1984 | -60.8597 | -61.0611 | -0.013733 | 0.059509 | -0.041198 | 0.34332 | 0.004577 | -0.054932 | 0.091553 | 0.10986 | -0.091553 | -0.14191 | -0.32501 | -0.19226 | -0.10071 | -0.10071 | 122.2275 | 122.3602 | 61.1893 | -122.2092 | 122.1268 | 122.168 | 61.0565 | -122.3602
1052.3125 | 122.5067 | -60.9833 | 61.2671 | 0.0054168 | -0.03902 | 0.11551 | 0.027579 | 0.051161 | -0.026731 | -0.025274 | -0.0003053 | -0.0052145 | 0.042176 | 0.05793 | -0.016158 | -0.014676 | 61.3403 | -60.6903 | 0.16022 | -61.0336 | 61.2122 | -61.0428 | -60.9421 | -61.3678 | -0.050354 | -61.2717 | 61.1298 | 61.1572 | -60.9009 | -61.116 | -0.05951 | 0.041198 | -0.054932 | 0.29297 | -0.050354 | -0.091552 | 0.073242 | 0.082397 | -0.13275 | -0.13733 | -0.38452 | -0.28839 | -0.15564 | -0.10986 | 122.1954 | 122.3236 | 61.1435 | -122.2092 | 122.113 | 122.1405 | 60.9329 | -122.3831
1054.0312 | 122.5845 | -60.965 | 61.2854 | -0.0022127 | -0.036671 | 0.11594 | 0.027579 | 0.049238 | -0.026517 | -0.023565 | 0.0073242 | -0.0032919 | 0.042603 | 0.059212 | -0.018295 | -0.013608 | 61.3632 | -60.6674 | 0.20599 | -60.9787 | 61.2762 | -61.0153 | -60.965 | -61.2854 | 0.041199 | -61.1893 | 61.1664 | 61.2076 | -60.8597 | -61.0519 | -0.050354 | 0 | -0.009155 | 0.29755 | -0.013733 | -0.013733 | 0.07782 | 0.10529 | -0.086975 | -0.11902 | -0.32043 | -0.2243 | -0.13733 | -0.077819 | 122.2412 | 122.3282 | 61.171 | -122.2504 | 122.1313 | 122.1725 | 61.0062 | -122.3373
1055.7344 | 122.4976 | -60.9833 | 61.2534 | 0.0054168 | -0.039448 | 0.11786 | 0.023306 | 0.053724 | -0.024381 | -0.025274 | -0.0003053 | -0.0045737 | 0.04068 | 0.059639 | -0.014236 | -0.014035 | 61.3495 | -60.6628 | 0.19226 | -61.0336 | 61.2305 | -61.0336 | -60.9421 | -61.3358 | -0.022888 | -61.2625 | 61.116 | 61.171 | -60.9238 | -61.1023 | -0.050354 | 0.041198 | -0.022888 | 0.32043 | -0.050354 | -0.091552 | 0.09613 | 0.059509 | -0.11902 | -0.13733 | -0.35248 | -0.27924 | -0.16022 | -0.082398 | 122.2137 | 122.3328 | 61.1755 | -122.1954 | 122.0993 | 122.1542 | 60.9604 | -122.3557
1057.5 | 122.5433 | -60.9467 | 61.2854 | 0.020676 | -0.037098 | 0.11765 | 0.028433 | 0.051801 | -0.026303 | -0.025274 | 0.0073242 | -0.0045737 | 0.041962 | 0.058144 | -0.017654 | -0.014249 | 61.4502 | -60.5804 | 0.32044 | -60.9512 | 61.2808 | -61.0016 | -60.9192 | -61.2305 | 0.10071 | -61.1481 | 61.1389 | 61.2305 | -60.8597 | -61.0336 | -0.054932 | 0.027466 | -0.004577 | 0.36621 | -0.004578 | -0.032044 | 0.16479 | 0.086975 | -0.086975 | -0.14648 | -0.28381 | -0.20142 | -0.11444 | -0.054931 | 122.2275 | 122.3969 | 61.2671 | -122.2046 | 122.0856 | 122.1771 | 61.0474 | -122.319
1059.2188 | 122.406 | -61.0519 | 61.2854 | 0.0054168 | -0.036671 | 0.11402 | 0.024588 | 0.049879 | -0.017331 | -0.022497 | 0.0073242 | 0.0026895 | 0.041321 | 0.062416 | -0.011245 | -0.015744 | 61.3129 | -60.7819 | 0.16937 | -61.0703 | 61.2717 | -61.0519 | -61.0153 | -61.377 | -0.10529 | -61.3998 | 61.1755 | 61.2076 | -60.9283 | -61.1435 | 0 | 0.036621 | -0.013733 | 0.27008 | -0.01831 | -0.054931 | 0.027466 | 0.1236 | -0.091553 | -0.10986 | -0.32501 | -0.3479 | -0.25635 | -0.077819 | 122.3236 | 122.3648 | 61.2213 | -122.3007 | 122.2275 | 122.2595 | 60.9467 | -122.4289
1061 | 122.525 | -60.9833 | 61.2625 | 0.0054168 | -0.038807 | 0.11445 | 0.023093 | 0.050947 | -0.024381 | -0.022283 | -0.0003053 | -0.0030783 | 0.041107 | 0.058144 | -0.015518 | -0.012753 | 61.3678 | -60.6445 | 0.26093 | -61.0153 | 61.1801 | -61.0794 | -60.9695 | -61.2717 | -0.009155 | -61.2305 | 61.0886 | 61.1664 | -60.9238 | -61.1114 | -0.096131 | 0.013733 | -0.082397 | 0.33874 | -0.032044 | -0.045777 | 0.10529 | 0.059509 | -0.12817 | -0.17395 | -0.28839 | -0.24719 | -0.11902 | -0.09613 | 122.1634 | 122.3511 | 61.2442 | -122.2321 | 122.0718 | 122.1497 | 60.9741 | -122.374
1062.7656 | 122.5616 | -60.9604 | 61.2946 | 0.0054168 | -0.040729 | 0.11851 | 0.027365 | 0.052656 | -0.027799 | -0.025487 | -0.0003053 | -0.0052145 | 0.040467 | 0.05793 | -0.018508 | -0.01254 | 61.3495 | -60.6354 | 0.28839 | -60.9924 | 61.2808 | -61.0016 | -60.9055 | -61.29 | -0.018311 | -61.2076 | 61.203 | 61.2167 | -60.8826 | -61.0703 | -0.041199 | 0.054931 | -0.013733 | 0.32501 | -0.032044 | -0.086975 | 0.054931 | 0.07782 | -0.10986 | -0.091553 | -0.32959 | -0.24719 | -0.13733 | -0.07782 | 122.2412 | 122.3099 | 61.2488 | -122.2 | 122.1634 | 122.1771 | 60.9421 | -122.3648
1064.4688 | 122.4152 | -60.9604 | 61.3678 | 0.0054168 | -0.034748 | 0.11637 | 0.029929 | 0.051161 | -0.024381 | -0.02506 | 0.014954 | -0.0013693 | 0.042603 | 0.058144 | -0.014449 | -0.013608 | 61.377 | -60.6491 | 0.38452 | -60.9833 | 61.3678 | -60.9879 | -60.9192 | -61.322 | -0.009155 | -61.2534 | 61.2808 | 61.29 | -60.8597 | -61.0474 | -0.027466 | 0.041199 | 0 | 0.31128 | -0.022888 | -0.064087 | 0.009155 | 0.10071 | -0.086975 | -0.086975 | -0.36163 | -0.29297 | -0.20599 | -0.07782 | 122.3282 | 122.3373 | 61.3449 | -122.287 | 122.2412 | 122.2504 | 60.9512 | -122.4152
1066.1875 | 122.406 | -60.9467 | 61.3724 | 0.013046 | -0.034321 | 0.11701 | 0.030356 | 0.053083 | -0.02609 | -0.021856 | 0.0073242 | -0.0013693 | 0.045166 | 0.059639 | -0.015945 | -0.012326 | 61.4227 | -60.5667 | 0.49896 | -60.9329 | 61.3174 | -61.0016 | -60.8917 | -61.2808 | 0.022888 | -61.2305 | 61.235 | 61.2808 | -60.8643 | -61.0428 | -0.054932 | 0.054931 | -0.054931 | 0.37994 | 0.013733 | -0.041198 | 0.050354 | 0.082397 | -0.096131 | -0.13733 | -0.33417 | -0.28381 | -0.18768 | -0.091552 | 122.2641 | 122.3694 | 61.4456 | -122.2641 | 122.1817 | 122.2275 | 60.9695 | -122.4152
1067.8906 | 122.4518 | -60.9879 | 61.3266 | -0.0022127 | -0.033039 | 0.11509 | 0.027152 | 0.050947 | -0.018186 | -0.021856 | 0.014954 | -0.00051485 | 0.043244 | 0.059426 | -0.013809 | -0.013821 | 61.409 | -60.6308 | 0.49439 | -60.9741 | 61.3266 | -60.9924 | -60.9375 | -61.2625 | 0 | -61.2442 | 61.2396 | 61.2442 | -60.8917 | -61.0657 | -0.004578 | 0.050354 | 0 | 0.35706 | 0.013733 | -0.036621 | 0.082398 | 0.09613 | -0.07782 | -0.086975 | -0.27466 | -0.25635 | -0.17853 | -0.082397 | 122.3145 | 122.3969 | 61.4822 | -122.2641 | 122.2275 | 122.2321 | 60.9879 | -122.3923
1069.6094 | 122.4518 | -61.0291 | 61.2854 | 0.0054168 | -0.035816 | 0.11637 | 0.026511 | 0.052656 | -0.022031 | -0.022283 | 0.0073242 | -0.00051485 | 0.042389 | 0.060067 | -0.016158 | -0.012753 | 61.3037 | -60.7452 | 0.3891 | -61.0428 | 61.29 | -61.0428 | -61.0062 | -61.3678 | -0.13733 | -61.3403 | 61.1755 | 61.2396 | -60.91 | -61.1114 | -0.013733 | 0.022888 | 0.004578 | 0.28381 | -0.013733 | -0.036621 | 0.018311 | 0.11902 | -0.082397 | -0.10986 | -0.33875 | -0.31128 | -0.22888 | -0.045776 | 122.319 | 122.3328 | 61.4182 | -122.2916 | 122.2046 | 122.2687 | 60.8917 | -122.3969
1071.3438 | 122.5525 | -60.9009 | 61.3129 | 0.013046 | -0.037098 | 0.11637 | 0.030356 | 0.05052 | -0.02844 | -0.02271 | 0.0073242 | -0.0054281 | 0.042816 | 0.059426 | -0.021926 | -0.011044 | 61.3815 | -60.6033 | 0.5127 | -60.9512 | 61.3083 | -60.965 | -60.91 | -61.2579 | -0.013733 | -61.1664 | 61.1801 | 61.2579 | -60.8185 | -61.0291 | -0.064087 | -0.009155 | -0.004577 | 0.29755 | -0.050354 | -0.041199 | 0.068665 | 0.082398 | -0.12817 | -0.13275 | -0.35706 | -0.2655 | -0.13733 | -0.054931 | 122.2092 | 122.2824 | 61.4136 | -122.2229 | 122.081 | 122.1588 | 60.8871 | -122.3419
1073.1406 | 122.406 | -60.9375 | 61.3678 | 0.0054168 | -0.034321 | 0.11551 | 0.028647 | 0.052869 | -0.024381 | -0.021856 | -0.0003053 | -0.0041465 | 0.041107 | 0.060494 | -0.01979 | -0.014676 | 61.4594 | -60.5026 | 0.62714 | -60.8871 | 61.3495 | -60.9192 | -60.878 | -61.235 | 0.027466 | -61.1572 | 61.2305 | 61.3129 | -60.8047 | -60.997 | 0.018311 | 0.059509 | -0.018311 | 0.43487 | 0.050354 | -0.009155 | 0.091553 | 0.13275 | -0.059509 | -0.13733 | -0.29755 | -0.21973 | -0.16022 | -0.054932 | 122.287 | 122.3969 | 61.5646 | -122.2458 | 122.168 | 122.2504 | 60.965 | -122.3648
1074.9219 | 122.4609 | -60.9833 | 61.2762 | 0.0054168 | -0.035602 | 0.11466 | 0.025229 | 0.054365 | -0.022031 | -0.022924 | 0.0073242 | 0.0014077 | 0.043671 | 0.062416 | -0.014663 | -0.015317 | 61.322 | -60.7224 | 0.43945 | -61.0336 | 61.3083 | -61.0199 | -60.9787 | -61.3449 | -0.15106 | -61.3129 | 61.2259 | 61.2396 | -60.8963 | -61.0748 | -0.036621 | 0.004577 | 0.032044 | 0.26092 | -0.050354 | -0.054931 | 0.045776 | 0.086975 | -0.091553 | -0.050354 | -0.36163 | -0.32959 | -0.23804 | -0.036621 | 122.2916 | 122.3053 | 61.4227 | -122.2549 | 122.2092 | 122.2229 | 60.8322 | -122.3511
1076.6875 | 122.5433 | -60.9604 | 61.2534 | 0.0054168 | -0.032825 | 0.11637 | 0.026724 | 0.051588 | -0.025876 | -0.02271 | 0.014954 | -0.0028647 | 0.043244 | 0.061348 | -0.014449 | -0.012753 | 61.3312 | -60.6766 | 0.50812 | -61.0199 | 61.3037 | -61.0199 | -60.9604 | -61.2946 | -0.10986 | -61.2396 | 61.1938 | 61.2671 | -60.8597 | -61.0748 | -0.059509 | 0 | 0.050354 | 0.28381 | -0.059509 | -0.059509 | 0.07782 | 0.10071 | -0.11444 | -0.059509 | -0.33417 | -0.27924 | -0.16479 | 0.013733 | 122.2641 | 122.2916 | 61.4685 | -122.2137 | 122.1542 | 122.2275 | 60.8505 | -122.3282
1078.4219 | 122.4884 | -60.9604 | 61.2991 | 0.0054168 | -0.035389 | 0.11466 | 0.022452 | 0.049238 | -0.022458 | -0.023565 | 0.014954 | 0.00055335 | 0.039826 | 0.062844 | -0.01509 | -0.013821 | 61.322 | -60.6903 | 0.52643 | -61.0199 | 61.3266 | -61.0016 | -60.9375 | -61.3403 | -0.14648 | -61.2946 | 61.1984 | 61.2762 | -60.8734 | -61.0565 | -0.041199 | 0.022888 | 0.027466 | 0.27008 | -0.059509 | -0.082397 | 0.022888 | 0.086975 | -0.096131 | -0.10071 | -0.37994 | -0.33417 | -0.23804 | -0.022888 | 122.287 | 122.2824 | 61.4868 | -122.2366 | 122.1588 | 122.2366 | 60.8139 | -122.3557
1080.1406 | 122.493 | -60.9238 | 61.3403 | 0.0054168 | -0.037739 | 0.11509 | 0.027579 | 0.049879 | -0.029508 | -0.024633 | 0.0073242 | -0.0052145 | 0.042176 | 0.058144 | -0.020004 | -0.01254 | 61.3907 | -60.5621 | 0.69122 | -60.9512 | 61.2671 | -60.9512 | -60.9055 | -61.2442 | -0.091553 | -61.171 | 61.1938 | 61.2854 | -60.8276 | -61.0428 | -0.027466 | 0.01831 | -0.073242 | 0.36163 | -0.027466 | -0.045776 | 0.050354 | 0.09613 | -0.11902 | -0.14648 | -0.32044 | -0.24719 | -0.12817 | -0.054932 | 122.1909 | 122.3145 | 61.615 | -122.2458 | 122.1176 | 122.2092 | 60.8322 | -122.3831
1081.9219 | 122.4197 | -60.8917 | 61.4319 | -0.0022127 | -0.039661 | 0.11786 | 0.027579 | 0.050733 | -0.026944 | -0.024847 | 0.014954 | -0.0058555 | 0.039185 | 0.06028 | -0.017654 | -0.012753 | 61.4914 | -60.4385 | 0.83771 | -60.8643 | 61.3358 | -60.9055 | -60.8368 | -61.1618 | 0.041199 | -61.0748 | 61.2534 | 61.2991 | -60.7773 | -60.9604 | -0.013733 | 0.054932 | -0.096131 | 0.45319 | 0.027466 | -0.027466 | 0.059509 | 0.11444 | -0.068664 | -0.17853 | -0.27008 | -0.1831 | -0.11444 | -0.13275 | 122.2275 | 122.3831 | 61.7294 | -122.2687 | 122.1451 | 122.1909 | 60.9329 | -122.3923
1083.6406 | 122.4152 | -60.91 | 61.4273 | 0.0054168 | -0.032825 | 0.11466 | 0.02886 | 0.052015 | -0.023953 | -0.023992 | -0.0003053 | -0.0015829 | 0.043457 | 0.060494 | -0.019576 | -0.015744 | 61.4319 | -60.5484 | 0.81024 | -60.9238 | 61.4182 | -60.9238 | -60.8459 | -61.235 | -0.073242 | -61.1938 | 61.3358 | 61.3724 | -60.791 | -60.9695 | -0.013733 | 0.064087 | -0.009155 | 0.36163 | -0.013733 | -0.07782 | 0.004578 | 0.11902 | -0.059509 | -0.091553 | -0.32501 | -0.28381 | -0.22431 | -0.054932 | 122.3282 | 122.3419 | 61.7203 | -122.2733 | 122.2458 | 122.2824 | 60.8368 | -122.3969
1085.4219 | 122.4472 | -60.9009 | 61.3953 | -0.0022127 | -0.034321 | 0.1153 | 0.029929 | 0.049452 | -0.020535 | -0.02271 | -0.0003053 | -0.00094205 | 0.043885 | 0.058999 | -0.017013 | -0.015744 | 61.441 | -60.5667 | 0.80109 | -60.9055 | 61.4319 | -60.8963 | -60.8597 | -61.2396 | -0.10071 | -61.1938 | 61.3174 | 61.3861 | -60.7819 | -60.9787 | 0.004578 | 0.041199 | 0.036621 | 0.33417 | -0.004578 | -0.045777 | 0.045776 | 0.11902 | -0.07782 | -0.07782 | -0.33874 | -0.29297 | -0.21515 | -0.009156 | 122.3328 | 122.3419 | 61.702 | -122.2549 | 122.2183 | 122.287 | 60.8002 | -122.374
1087.1406 | 122.5296 | -60.91 | 61.3174 | 0.013046 | -0.03603 | 0.11359 | 0.026083 | 0.053083 | -0.02374 | -0.021856 | 0.0073242 | -0.0011557 | 0.042603 | 0.061989 | -0.014663 | -0.015317 | 61.3998 | -60.6171 | 0.76904 | -60.9695 | 61.3266 | -60.965 | -60.9146 | -61.2259 | -0.15106 | -61.1938 | 61.2076 | 61.2625 | -60.8322 | -61.0062 | -0.054932 | -0.004578 | 0.009155 | 0.29297 | -0.059509 | -0.054931 | 0.082397 | 0.07782 | -0.096131 | -0.10986 | -0.31586 | -0.28381 | -0.18768 | -0.054932 | 122.2366 | 122.3099 | 61.6791 | -122.2321 | 122.1176 | 122.1725 | 60.759 | -122.3236
1088.9375 | 122.4609 | -60.8963 | 61.3998 | 0.0054168 | -0.033039 | 0.11573 | 0.027579 | 0.052229 | -0.025235 | -0.024633 | 0.014954 | 0.00055335 | 0.04303 | 0.06028 | -0.017013 | -0.013608 | 61.4456 | -60.5438 | 0.89264 | -60.9009 | 61.4136 | -60.8963 | -60.8414 | -61.1984 | -0.10986 | -61.1572 | 61.3174 | 61.4044 | -60.7727 | -60.9558 | 0 | 0.054931 | 0.013733 | 0.35248 | -0.004578 | -0.059509 | 0.045777 | 0.1236 | -0.05951 | -0.082397 | -0.30212 | -0.26093 | -0.20142 | 0.004578 | 122.3099 | 122.3419 | 61.7889 | -122.2412 | 122.2137 | 122.3007 | 60.7864 | -122.3557
1090.7188 | 122.5021 | -60.9055 | 61.3312 | -0.0022127 | -0.034962 | 0.11487 | 0.025015 | 0.054578 | -0.023953 | -0.023565 | 0.0073242 | -0.00072845 | 0.04303 | 0.062203 | -0.014877 | -0.012967 | 61.3998 | -60.6354 | 0.80566 | -60.9695 | 61.3449 | -60.9604 | -60.8871 | -61.2717 | -0.21973 | -61.2396 | 61.2808 | 61.3174 | -60.8276 | -61.0291 | -0.054931 | 0.018311 | 0.013733 | 0.27008 | -0.064086 | -0.082397 | 0.068664 | 0.07782 | -0.1236 | -0.050354 | -0.36621 | -0.33417 | -0.21057 | -0.013733 | 122.2504 | 122.3053 | 61.7111 | -122.2183 | 122.1863 | 122.2229 | 60.6857 | -122.3602
1092.4844 | 122.5479 | -60.8871 | 61.3358 | -0.0022127 | -0.037525 | 0.11594 | 0.023093 | 0.053938 | -0.025022 | -0.022283 | -0.0003053 | -0.0020103 | 0.043671 | 0.058571 | -0.01509 | -0.013821 | 61.4227 | -60.5621 | 0.89264 | -60.9375 | 61.3449 | -60.9558 | -60.8643 | -61.1847 | -0.13733 | -61.1526 | 61.2213 | 61.2717 | -60.8047 | -60.997 | -0.068665 | 0.022888 | 0.009156 | 0.32501 | -0.050354 | -0.073242 | 0.086975 | 0.082397 | -0.10986 | -0.11444 | -0.29755 | -0.2655 | -0.15564 | -0.064087 | 122.2321 | 122.3099 | 61.7798 | -122.2 | 122.1085 | 122.1588 | 60.7498 | -122.3328
1094.2031 | 122.4472 | -60.8322 | 61.4456 | 0.0054168 | -0.035602 | 0.11851 | 0.027792 | 0.050733 | -0.024381 | -0.023992 | -0.0003053 | -0.00051485 | 0.042816 | 0.058144 | -0.014022 | -0.012326 | 61.4594 | -60.498 | 0.9613 | -60.8688 | 61.4227 | -60.878 | -60.8231 | -61.203 | -0.13733 | -61.1389 | 61.3586 | 61.4136 | -60.7498 | -60.9558 | -0.045777 | 0.009155 | -0.022889 | 0.33417 | -0.036621 | -0.045776 | 0.013733 | 0.082397 | -0.1236 | -0.086975 | -0.37079 | -0.3067 | -0.18311 | -0.032044 | 122.2549 | 122.2916 | 61.7935 | -122.2687 | 122.1909 | 122.2458 | 60.6949 | -122.4014
1095.9844 | 122.4472 | -60.8871 | 61.3907 | 0.020676 | -0.032184 | 0.11573 | 0.026511 | 0.053724 | -0.021817 | -0.023992 | 0.0073242 | -0.00072845 | 0.044098 | 0.060707 | -0.014022 | -0.011258 | 61.3861 | -60.6079 | 0.85602 | -60.9329 | 61.377 | -60.9238 | -60.8322 | -61.2579 | -0.27924 | -61.2213 | 61.2854 | 61.3495 | -60.8276 | -60.9924 | -0.036621 | 0.054932 | -0.013733 | 0.27924 | -0.045776 | -0.10071 | -0.004578 | 0.059509 | -0.10529 | -0.10529 | -0.37079 | -0.33417 | -0.22888 | -0.041199 | 122.2641 | 122.2733 | 61.7432 | -122.2229 | 122.1725 | 122.2366 | 60.6079 | -122.3831
1097.6875 | 122.438 | -60.8414 | 61.4182 | 0.0054168 | -0.031544 | 0.11509 | 0.028433 | 0.051801 | -0.022031 | -0.023138 | 0.0073242 | -0.00051485 | 0.045594 | 0.061348 | -0.016158 | -0.014249 | 61.4914 | -60.4523 | 1.03 | -60.8414 | 61.4548 | -60.8505 | -60.7727 | -61.1481 | -0.11444 | -61.1069 | 61.3312 | 61.4044 | -60.7361 | -60.9421 | -0.009155 | 0.068665 | 0.036621 | 0.3891 | 0 | -0.068665 | 0.073242 | 0.10529 | -0.10071 | -0.086975 | -0.3067 | -0.2655 | -0.16479 | -0.013733 | 122.2961 | 122.3328 | 61.8713 | -122.1909 | 122.1725 | 122.2458 | 60.7269 | -122.3602
1099.4688 | 122.525 | -60.7681 | 61.4456 | -0.0022127 | -0.037525 | 0.11829 | 0.032492 | 0.050092 | -0.031644 | -0.025274 | -0.0003053 | -0.0062827 | 0.045594 | 0.059426 | -0.021285 | -0.011899 | 61.5555 | -60.3333 | 1.1078 | -60.7773 | 61.4182 | -60.8093 | -60.7132 | -61.0748 | -0.10529 | -60.9741 | 61.3129 | 61.3815 | -60.704 | -60.8963 | -0.041199 | 0.054931 | -0.027466 | 0.43487 | -0.009156 | -0.064087 | 0.10986 | 0.064086 | -0.12817 | -0.13275 | -0.3067 | -0.20599 | -0.07782 | -0.064087 | 122.1863 | 122.3236 | 61.8759 | -122.1588 | 122.081 | 122.1497 | 60.6628 | -122.3419
1101.1875 | 122.4106 | -60.8826 | 61.4319 | 0.013046 | -0.03368 | 0.11316 | 0.023734 | 0.051374 | -0.020322 | -0.023138 | 0.0073242 | -0.00094205 | 0.042389 | 0.061776 | -0.014877 | -0.014035 | 61.409 | -60.5392 | 0.99335 | -60.9009 | 61.4182 | -60.9055 | -60.8276 | -61.2167 | -0.31128 | -61.235 | 61.3129 | 61.3724 | -60.7681 | -60.9879 | -0.022889 | 0.054931 | -0.013733 | 0.34332 | -0.018311 | -0.073242 | -0.022888 | 0.11444 | -0.10529 | -0.11902 | -0.33417 | -0.35248 | -0.24719 | -0.05951 | 122.3007 | 122.2916 | 61.8759 | -122.2595 | 122.1954 | 122.2549 | 60.5713 | -122.4197
1102.9688 | 122.3969 | -60.8643 | 61.4227 | 0.0054168 | -0.029621 | 0.11466 | 0.029501 | 0.051588 | -0.021604 | -0.023565 | 0.0073242 | 0.0011941 | 0.043671 | 0.06263 | -0.014663 | -0.011685 | 61.4868 | -60.4523 | 1.0849 | -60.8597 | 61.4319 | -60.8597 | -60.8185 | -61.1893 | -0.2655 | -61.1755 | 61.3266 | 61.3998 | -60.759 | -60.9604 | 0.004578 | 0.045777 | 0.009156 | 0.41199 | 0.004578 | -0.041199 | 0.064087 | 0.10529 | -0.09613 | -0.09613 | -0.32501 | -0.31128 | -0.21515 | -0.022888 | 122.2961 | 122.3511 | 61.9492 | -122.2412 | 122.1909 | 122.2641 | 60.5988 | -122.3831
1104.75 | 122.3877 | -60.8688 | 61.4548 | -0.0022127 | -0.030048 | 0.11359 | 0.02886 | 0.052442 | -0.023953 | -0.022283 | 0.0073242 | -0.0020103 | 0.044739 | 0.061348 | -0.01509 | -0.014462 | 61.4548 | -60.4797 | 1.0895 | -60.878 | 61.441 | -60.8597 | -60.8002 | -61.1893 | -0.26093 | -61.1893 | 61.3129 | 61.3861 | -60.7636 | -60.9558 | 0.009155 | 0.068664 | -0.013733 | 0.3891 | -0.009156 | -0.07782 | 0 | 0.10528 | -0.086976 | -0.14191 | -0.32044 | -0.32044 | -0.23346 | -0.068665 | 122.3099 | 122.3236 | 61.9583 | -122.2549 | 122.1817 | 122.2549 | 60.6079 | -122.4106
1106.5312 | 122.4426 | -60.7864 | 61.5005 | 0.0054168 | -0.034962 | 0.11637 | 0.02886 | 0.050092 | -0.02609 | -0.024633 | 0.0073242 | -0.0015829 | 0.043671 | 0.059639 | -0.01744 | -0.01318 | 61.5097 | -60.4065 | 1.2039 | -60.791 | 61.5189 | -60.8276 | -60.7224 | -61.1343 | -0.19226 | -61.084 | 61.409 | 61.4822 | -60.6995 | -60.8734 | -0.041199 | 0.064087 | 0.018311 | 0.37994 | -0.004578 | -0.068665 | 0.009156 | 0.086975 | -0.086975 | -0.091552 | -0.3479 | -0.29755 | -0.21057 | -0.01831 | 122.3053 | 122.2961 | 61.9904 | -122.2229 | 122.1954 | 122.2687 | 60.5942 | -122.374
1108.2656 | 122.3969 | -60.8139 | 61.5005 | 0.013046 | -0.034534 | 0.11402 | 0.026511 | 0.052656 | -0.023313 | -0.021429 | 0.0073242 | -0.0011557 | 0.042816 | 0.062844 | -0.014236 | -0.01254 | 61.5417 | -60.379 | 1.2268 | -60.8093 | 61.4548 | -60.7956 | -60.7315 | -61.1114 | -0.23804 | -61.1023 | 61.3312 | 61.4227 | -60.6949 | -60.9009 | 0.018311 | 0.082398 | -0.045776 | 0.43488 | 0.004578 | -0.07782 | 0.041199 | 0.11902 | -0.086975 | -0.16937 | -0.29755 | -0.28839 | -0.20142 | -0.07782 | 122.2687 | 122.3557 | 62.0407 | -122.2321 | 122.1451 | 122.2366 | 60.5759 | -122.4014
1110.0469 | 122.4976 | -60.7544 | 61.5005 | 0.0054168 | -0.039234 | 0.11765 | 0.027579 | 0.051374 | -0.030149 | -0.024206 | 0.0073242 | -0.0064963 | 0.04068 | 0.059426 | -0.019149 | -0.012326 | 61.5189 | -60.347 | 1.2726 | -60.8002 | 61.441 | -60.7681 | -60.7269 | -61.1069 | -0.24261 | -61.0016 | 61.322 | 61.4227 | -60.6628 | -60.8597 | -0.013732 | 0.027466 | -0.059509 | 0.40741 | -0.045776 | -0.073242 | 0.018311 | 0.091553 | -0.10528 | -0.17853 | -0.35248 | -0.24719 | -0.14191 | -0.07782 | 122.1954 | 122.2733 | 62.027 | -122.2275 | 122.0764 | 122.1771 | 60.5118 | -122.3602
1111.8125 | 122.4884 | -60.7407 | 61.4685 | 0.020676 | -0.038166 | 0.1168 | 0.023306 | 0.05351 | -0.025662 | -0.023778 | -0.0003053 | -0.0054281 | 0.041321 | 0.058358 | -0.016799 | -0.012326 | 61.5646 | -60.3149 | 1.2039 | -60.7636 | 61.4273 | -60.8047 | -60.7224 | -61.0336 | -0.26093 | -60.9833 | 61.3266 | 61.3861 | -60.6857 | -60.8414 | -0.064087 | 0.018311 | -0.041199 | 0.42572 | -0.022888 | -0.041199 | 0.09613 | 0.054932 | -0.10071 | -0.14191 | -0.29297 | -0.24261 | -0.14191 | -0.082398 | 122.168 | 122.3053 | 61.9446 | -122.1909 | 122.0673 | 122.1268 | 60.4797 | -122.3099
1113.5938 | 122.4564 | -60.7681 | 61.4594 | -0.0022127 | -0.037098 | 0.11402 | 0.026083 | 0.053938 | -0.021817 | -0.023778 | 0.0073242 | -0.00094205 | 0.040467 | 0.060494 | -0.014449 | -0.01318 | 61.496 | -60.4294 | 1.1856 | -60.8322 | 61.5372 | -60.8322 | -60.7544 | -61.1389 | -0.3479 | -61.1069 | 61.409 | 61.4319 | -60.7269 | -60.8917 | -0.064087 | 0.013732 | 0.077819 | 0.33875 | -0.064087 | -0.077819 | 0.036621 | 0.041198 | -0.1236 | -0.050354 | -0.37079 | -0.33875 | -0.21515 | -0.027466 | 122.3053 | 122.2641 | 61.9537 | -122.2137 | 122.1771 | 122.2 | 60.4202 | -122.3511
1115.3125 | 122.4838 | -60.7361 | 61.5189 | -0.0098417 | -0.037098 | 0.11701 | 0.026938 | 0.053083 | -0.028226 | -0.023992 | 0.014954 | -0.0039329 | 0.040039 | 0.061776 | -0.017013 | -0.012753 | 61.5875 | -60.2829 | 1.3458 | -60.7681 | 61.441 | -60.7636 | -60.6949 | -61.0291 | -0.25177 | -60.965 | 61.3403 | 61.4182 | -60.6491 | -60.8551 | -0.027466 | 0.041199 | -0.07782 | 0.45319 | -0.032043 | -0.073242 | 0.068664 | 0.086975 | -0.11902 | -0.17853 | -0.29297 | -0.22888 | -0.10986 | -0.10071 | 122.1771 | 122.3236 | 62.0819 | -122.2137 | 122.0764 | 122.1542 | 60.4843 | -122.374
1117.1094 | 122.4014 | -60.7315 | 61.528 | 0.013046 | -0.035602 | 0.1153 | 0.026511 | 0.049879 | -0.023099 | -0.024419 | 0.0073242 | 0.0014077 | 0.042389 | 0.060067 | -0.013809 | -0.015317 | 61.6516 | -60.2875 | 1.3412 | -60.7224 | 61.5326 | -60.7407 | -60.6812 | -61.0107 | -0.26093 | -61.0153 | 61.441 | 61.4868 | -60.6354 | -60.8368 | -0.009156 | 0.050354 | 0.004578 | 0.44403 | 0.009155 | -0.041199 | 0.1236 | 0.09613 | -0.10529 | -0.086975 | -0.27924 | -0.28381 | -0.17853 | -0.041199 | 122.2641 | 122.3831 | 62.0728 | -122.2092 | 122.1725 | 122.2183 | 60.4706 | -122.3648
1118.9062 | 122.3969 | -60.6857 | 61.6241 | 0.0054168 | -0.034321 | 0.11637 | 0.029929 | 0.055433 | -0.02844 | -0.026983 | 0.0073242 | -0.0030783 | 0.041107 | 0.059212 | -0.018936 | -0.011899 | 61.6791 | -60.1822 | 1.4282 | -60.6445 | 61.5509 | -60.7224 | -60.6216 | -60.997 | -0.23804 | -60.9329 | 61.4639 | 61.5601 | -60.5942 | -60.7727 | -0.036621 | 0.064087 | -0.073243 | 0.50354 | 0.041199 | -0.022888 | 0.054931 | 0.091553 | -0.086975 | -0.16022 | -0.31128 | -0.24719 | -0.16022 | -0.064087 | 122.2366 | 122.3648 | 62.114 | -122.2458 | 122.1497 | 122.2458 | 60.4477 | -122.3969
1120.6719 | 122.525 | -60.6583 | 61.5646 | -0.0022127 | -0.039448 | 0.11616 | 0.028006 | 0.054578 | -0.030149 | -0.023138 | 0.0073242 | -0.0050009 | 0.042816 | 0.06028 | -0.018081 | -0.012753 | 61.5829 | -60.2417 | 1.3458 | -60.6995 | 61.5143 | -60.7086 | -60.64 | -60.9924 | -0.28381 | -60.9283 | 61.4227 | 61.496 | -60.5896 | -60.7727 | -0.050354 | 0.01831 | -0.050354 | 0.41657 | -0.041199 | -0.059509 | 0.018311 | 0.068664 | -0.11444 | -0.14191 | -0.33417 | -0.27008 | -0.15564 | -0.068664 | 122.1725 | 122.2412 | 62.0041 | -122.2046 | 122.081 | 122.1542 | 60.3745 | -122.3373
1122.3906 | 122.5021 | -60.6491 | 61.5967 | 0.013046 | -0.039875 | 0.11829 | 0.025656 | 0.055433 | -0.02844 | -0.023565 | -0.0003053 | -0.0047873 | 0.040467 | 0.05793 | -0.017654 | -0.01254 | 61.615 | -60.228 | 1.3779 | -60.6949 | 61.5234 | -60.7086 | -60.6079 | -61.0016 | -0.29755 | -60.9421 | 61.4227 | 61.5097 | -60.5988 | -60.759 | -0.059509 | 0.041199 | -0.073243 | 0.42114 | -0.045776 | -0.086975 | 0.01831 | 0.050354 | -0.10986 | -0.17395 | -0.35248 | -0.29297 | -0.18311 | -0.086975 | 122.1725 | 122.2641 | 62.027 | -122.2046 | 122.0718 | 122.1588 | 60.3516 | -122.3557
1124.1719 | 122.4701 | -60.672 | 61.5601 | 0.0054168 | -0.040089 | 0.11573 | 0.023306 | 0.056074 | -0.026303 | -0.023778 | 0.0073242 | -0.0020103 | 0.042389 | 0.060494 | -0.013809 | -0.015744 | 61.6745 | -60.1822 | 1.4282 | -60.6857 | 61.4822 | -60.7452 | -60.6354 | -60.9558 | -0.24719 | -60.9329 | 61.4136 | 61.4502 | -60.5988 | -60.7681 | -0.073242 | 0.036621 | -0.07782 | 0.48981 | -0.013733 | -0.050354 | 0.11444 | 0.073242 | -0.09613 | -0.14649 | -0.28381 | -0.26093 | -0.16479 | -0.10986 | 122.1542 | 122.3465 | 62.1002 | -122.1954 | 122.0856 | 122.1222 | 60.4248 | -122.3282
1125.875 | 122.5479 | -60.64 | 61.6104 | 0.0054168 | -0.037952 | 0.11573 | 0.026083 | 0.052869 | -0.028867 | -0.025487 | 0.0073242 | -0.0067099 | 0.039185 | 0.059639 | -0.018081 | -0.013608 | 61.6791 | -60.141 | 1.4465 | -60.64 | 61.5692 | -60.6674 | -60.5942 | -60.8917 | -0.20599 | -60.8459 | 61.4731 | 61.5463 | -60.5301 | -60.7132 | -0.027465 | 0.045777 | -0.041199 | 0.49896 | 0 | -0.045777 | 0.068664 | 0.10986 | -0.073242 | -0.13733 | -0.25177 | -0.20599 | -0.13275 | -0.064087 | 122.2092 | 122.319 | 62.0865 | -122.2046 | 122.113 | 122.1863 | 60.434 | -122.3236
1127.6562 | 122.4335 | -60.6354 | 61.6562 | 0.0054168 | -0.035175 | 0.1153 | 0.026511 | 0.053938 | -0.022244 | -0.023778 | 0.0073242 | 0.0022623 | 0.040467 | 0.05793 | -0.014236 | -0.014889 | 61.6837 | -60.1822 | 1.3687 | -60.6445 | 61.6608 | -60.6766 | -60.5713 | -60.9375 | -0.28381 | -60.9421 | 61.5646 | 61.5921 | -60.5301 | -60.6995 | -0.041199 | 0.064087 | 0.004578 | 0.45319 | -0.009155 | -0.073242 | 0.027466 | 0.10529 | -0.064087 | -0.091553 | -0.30212 | -0.3067 | -0.24262 | -0.064087 | 122.2961 | 122.319 | 62.0041 | -122.2275 | 122.2 | 122.2275 | 60.3516 | -122.3557
1129.4531 | 122.493 | -60.5804 | 61.6608 | 0.0054168 | -0.035389 | 0.11445 | 0.030783 | 0.052229 | -0.026517 | -0.025274 | -0.0003053 | -0.0026511 | 0.041535 | 0.059639 | -0.017654 | -0.014676 | 61.7844 | -60.0037 | 1.5244 | -60.5484 | 61.6196 | -60.6033 | -60.5072 | -60.8093 | -0.1236 | -60.7956 | 61.5097 | 61.5692 | -60.4706 | -60.672 | -0.022889 | 0.073242 | -0.041199 | 0.57678 | 0.032043 | -0.041199 | 0.1236 | 0.10986 | -0.091553 | -0.15106 | -0.22888 | -0.21515 | -0.1236 | -0.091553 | 122.2 | 122.3648 | 62.1048 | -122.168 | 122.0901 | 122.1497 | 60.4568 | -122.3328
1131.1875 | 122.5159 | -60.5621 | 61.6653 | 0.0054168 | -0.034321 | 0.11487 | 0.030997 | 0.052869 | -0.028653 | -0.023565 | -0.0003053 | -0.0035055 | 0.04068 | 0.061776 | -0.020431 | -0.016171 | 61.7981 | -59.9945 | 1.5701 | -60.5484 | 61.6379 | -60.5713 | -60.5301 | -60.7819 | -0.10986 | -60.7681 | 61.5189 | 61.5967 | -60.4523 | -60.6583 | -0.009155 | 0.032044 | -0.027466 | 0.56763 | 0.013733 | -0.018311 | 0.13275 | 0.10986 | -0.09613 | -0.14648 | -0.21973 | -0.20599 | -0.10986 | -0.068664 | 122.2 | 122.3602 | 62.1323 | -122.1954 | 122.081 | 122.1588 | 60.4523 | -122.3236
1132.9688 | 122.3602 | -60.6354 | 61.6653 | 0.0054168 | -0.030903 | 0.11381 | 0.027579 | 0.053083 | -0.017758 | -0.023351 | 0.0073242 | 0.0016213 | 0.042389 | 0.061776 | -0.015731 | -0.016598 | 61.7477 | -60.1227 | 1.4374 | -60.6171 | 61.6837 | -60.64 | -60.5804 | -60.8871 | -0.21057 | -60.9604 | 61.5463 | 61.6058 | -60.5255 | -60.7361 | -0.004578 | 0.054932 | 0.018311 | 0.5127 | 0.018311 | -0.036621 | 0.082398 | 0.10986 | -0.10071 | -0.11902 | -0.25177 | -0.32501 | -0.2243 | -0.059509 | 122.319 | 122.3831 | 62.0728 | -122.2458 | 122.1817 | 122.2412 | 60.4248 | -122.4014
1134.75 | 122.525 | -60.553 | 61.6837 | 0.013046 | -0.040729 | 0.1153 | 0.026511 | 0.05052 | -0.029294 | -0.023565 | -0.0003053 | -0.0052145 | 0.040467 | 0.059639 | -0.018081 | -0.012967 | 61.7111 | -60.0677 | 1.4557 | -60.585 | 61.6516 | -60.5804 | -60.5072 | -60.8505 | -0.15564 | -60.8093 | 61.528 | 61.6333 | -60.4706 | -60.6491 | -0.027465 | 0.045777 | -0.032044 | 0.48523 | -0.032043 | -0.07782 | 0.027466 | 0.082398 | -0.09613 | -0.15564 | -0.29755 | -0.25635 | -0.16022 | -0.050354 | 122.2046 | 122.2641 | 62.0087 | -122.1909 | 122.081 | 122.1863 | 60.3973 | -122.3328
1136.4844 | 122.3785 | -60.585 | 61.6882 | 0.013046 | -0.03368 | 0.11445 | 0.026511 | 0.055006 | -0.019895 | -0.023351 | -0.0079343 | -0.00051485 | 0.041962 | 0.061348 | -0.01509 | -0.015958 | 61.8073 | -60.0266 | 1.4786 | -60.5713 | 61.7111 | -60.5896 | -60.5255 | -60.8047 | -0.10986 | -60.8551 | 61.5829 | 61.6379 | -60.4706 | -60.6674 | -0.004578 | 0.059509 | 0.022889 | 0.55847 | 0.013733 | -0.045776 | 0.11902 | 0.11444 | -0.082397 | -0.10529 | -0.21973 | -0.27008 | -0.18768 | -0.050354 | 122.2961 | 122.3923 | 62.0636 | -122.2137 | 122.168 | 122.2229 | 60.4752 | -122.3557
1138.1875 | 122.4747 | -60.5621 | 61.6562 | 0.020676 | -0.034748 | 0.11744 | 0.025443 | 0.051588 | -0.022458 | -0.022924 | 0.0073242 | -8.7654e-05 | 0.041107 | 0.059639 | -0.013168 | -0.012753 | 61.7065 | -60.0861 | 1.3962 | -60.6171 | 61.7157 | -60.6125 | -60.553 | -60.8734 | -0.16937 | -60.8917 | 61.6013 | 61.6379 | -60.4752 | -60.6949 | -0.050354 | 0.009155 | 0.059509 | 0.47607 | -0.054931 | -0.064086 | 0.050354 | 0.086975 | -0.13275 | -0.054932 | -0.31128 | -0.32959 | -0.19684 | -0.018311 | 122.2778 | 122.2687 | 61.9583 | -122.2092 | 122.1634 | 122.2 | 60.3928 | -122.3511
1139.9531 | 122.4747 | -60.4889 | 61.734 | 0.013046 | -0.040943 | 0.11573 | 0.025229 | 0.049452 | -0.027585 | -0.021856 | 0.0073242 | -0.0035055 | 0.04068 | 0.060707 | -0.016799 | -0.012967 | 61.8118 | -59.9304 | 1.5106 | -60.5209 | 61.6379 | -60.5576 | -60.4797 | -60.791 | -0.07782 | -60.7544 | 61.5509 | 61.6653 | -60.4156 | -60.6079 | -0.068664 | 0.009156 | -0.096131 | 0.55847 | -0.032043 | -0.041199 | 0.07782 | 0.073243 | -0.11902 | -0.18311 | -0.30212 | -0.2655 | -0.14649 | -0.068665 | 122.1268 | 122.3007 | 61.9995 | -122.2137 | 122.0398 | 122.1542 | 60.4111 | -122.3419
1141.7188 | 122.4197 | -60.5118 | 61.7523 | -0.0098417 | -0.034534 | 0.11402 | 0.027579 | 0.052229 | -0.023526 | -0.023138 | 0.0073242 | 0.0014077 | 0.043457 | 0.061348 | -0.014022 | -0.014249 | 61.8668 | -59.8984 | 1.4969 | -60.4843 | 61.7615 | -60.5026 | -60.434 | -60.7315 | 0.045776 | -60.7636 | 61.6745 | 61.7294 | -60.3699 | -60.5896 | 0.009155 | 0.07782 | 0.009156 | 0.6134 | 0.027466 | -0.050354 | 0.11444 | 0.14191 | -0.07782 | -0.077819 | -0.21973 | -0.25177 | -0.17395 | -0.022888 | 122.2733 | 122.3785 | 62.0087 | -122.1863 | 122.1863 | 122.2412 | 60.5576 | -122.3419
1143.4375 | 122.5204 | -60.4202 | 61.8027 | 0.0054168 | -0.039661 | 0.11637 | 0.027152 | 0.053724 | -0.029294 | -0.023138 | 0.014954 | -0.0054281 | 0.040039 | 0.058785 | -0.018722 | -0.011258 | 61.8393 | -59.8938 | 1.5518 | -60.466 | 61.7752 | -60.4889 | -60.4065 | -60.7452 | 0.054932 | -60.7132 | 61.647 | 61.7294 | -60.3607 | -60.5713 | -0.068665 | 0.013733 | -0.027465 | 0.52643 | -0.045776 | -0.059509 | 0.036621 | 0.059509 | -0.15106 | -0.15564 | -0.32501 | -0.29297 | -0.14191 | -0.073242 | 122.1954 | 122.2595 | 61.972 | -122.2092 | 122.0673 | 122.1497 | 60.4752 | -122.374
1145.1562 | 122.4747 | -60.4111 | 61.8256 | 0.0054168 | -0.040943 | 0.11829 | 0.026511 | 0.050733 | -0.028653 | -0.023565 | -0.0003053 | -0.0047873 | 0.039398 | 0.060494 | -0.01979 | -0.014035 | 61.8896 | -59.8114 | 1.561 | -60.4431 | 61.7569 | -60.4477 | -60.3653 | -60.6995 | 0.091553 | -60.6674 | 61.6699 | 61.7477 | -60.3058 | -60.4935 | -0.036621 | 0.045777 | -0.068665 | 0.59967 | -0.032043 | -0.07782 | 0.064086 | 0.10529 | -0.082397 | -0.15564 | -0.28839 | -0.25635 | -0.17395 | -0.07782 | 122.168 | 122.3007 | 61.972 | -122.1909 | 122.081 | 122.1588 | 60.5026 | -122.319
1146.9219 | 122.4701 | -60.4111 | 61.821 | -0.0022127 | -0.041157 | 0.11551 | 0.026297 | 0.052229 | -0.02609 | -0.023992 | 0.0073242 | -0.0067099 | 0.038544 | 0.06028 | -0.018508 | -0.012967 | 61.9446 | -59.7656 | 1.5427 | -60.4202 | 61.7798 | -60.466 | -60.3607 | -60.6628 | 0.10529 | -60.6628 | 61.6608 | 61.7615 | -60.3104 | -60.5164 | -0.054931 | 0.050354 | -0.041199 | 0.64545 | -0.009155 | -0.059509 | 0.1236 | 0.10071 | -0.10529 | -0.16022 | -0.25177 | -0.25177 | -0.14648 | -0.059509 | 122.1909 | 122.3557 | 61.9537 | -122.1817 | 122.0718 | 122.1725 | 60.5164 | -122.3373
1148.6875 | 122.5204 | -60.2966 | 61.8896 | -0.0022127 | -0.038593 | 0.11423 | 0.029715 | 0.052869 | -0.02908 | -0.024847 | 0.014954 | -0.0037191 | 0.041748 | 0.061989 | -0.021072 | -0.014676 | 61.9537 | -59.7336 | 1.5198 | -60.3653 | 61.8439 | -60.3882 | -60.3149 | -60.6216 | 0.21973 | -60.5942 | 61.7615 | 61.8393 | -60.2509 | -60.4614 | -0.091553 | -0.01831 | -0.045776 | 0.56305 | -0.068664 | -0.050354 | 0.064087 | 0.045777 | -0.1648 | -0.12817 | -0.32501 | -0.29755 | -0.13275 | -0.050354 | 122.1405 | 122.2504 | 61.8164 | -122.2046 | 122.0581 | 122.1359 | 60.5164 | -122.3511
1150.4844 | 122.5204 | -60.2737 | 61.9354 | -0.0022127 | -0.036457 | 0.11744 | 0.025656 | 0.053297 | -0.028012 | -0.025915 | 0.0073242 | -0.0035055 | 0.039612 | 0.058144 | -0.018295 | -0.015103 | 62.027 | -59.6329 | 1.5381 | -60.2921 | 61.8896 | -60.3241 | -60.2737 | -60.5118 | 0.32501 | -60.4935 | 61.8301 | 61.8805 | -60.1822 | -60.3928 | -0.050354 | 0 | -0.045777 | 0.64087 | -0.01831 | -0.01831 | 0.091553 | 0.091553 | -0.11902 | -0.10529 | -0.23804 | -0.21973 | -0.10071 | -0.054932 | 122.1634 | 122.3007 | 61.8118 | -122.2092 | 122.1039 | 122.1542 | 60.5988 | -122.3282
1152.2031 | 122.5113 | -60.2737 | 61.8942 | 0.0054168 | -0.038166 | 0.11701 | 0.022879 | 0.05052 | -0.018186 | -0.023565 | 0.0073242 | -0.0020103 | 0.039612 | 0.061562 | -0.011245 | -0.014676 | 62.0132 | -59.6603 | 1.3412 | -60.3378 | 61.9217 | -60.3653 | -60.2692 | -60.5347 | 0.13733 | -60.5804 | 61.8027 | 61.8393 | -60.26 | -60.4111 | -0.091552 | 0.004578 | 0.027466 | 0.6134 | -0.064087 | -0.068665 | 0.11902 | 0.013733 | -0.13733 | -0.091553 | -0.26093 | -0.3067 | -0.16937 | -0.054932 | 122.1954 | 122.287 | 61.615 | -122.1634 | 122.0764 | 122.113 | 60.4111 | -122.3053
1153.9844 | 122.374 | -60.3241 | 61.9583 | 0.0054168 | -0.030262 | 0.11509 | 0.029501 | 0.054365 | -0.019467 | -0.022497 | -0.0003053 | 0.00055335 | 0.044312 | 0.059639 | -0.015518 | -0.015103 | 62.0224 | -59.6466 | 1.2772 | -60.3195 | 61.9583 | -60.3241 | -60.2509 | -60.585 | 0.11902 | -60.6445 | 61.8713 | 61.908 | -60.2325 | -60.4202 | 0 | 0.073243 | 0 | 0.67749 | 0.004578 | -0.068665 | 0.064087 | 0.091553 | -0.09613 | -0.086975 | -0.26093 | -0.32043 | -0.2243 | -0.050354 | 122.2824 | 122.3465 | 61.6013 | -122.2092 | 122.1954 | 122.2321 | 60.4431 | -122.3785
1155.6875 | 122.5204 | -60.141 | 62.0407 | -0.0022127 | -0.037952 | 0.11701 | 0.02822 | 0.052229 | -0.031217 | -0.023778 | 0.014954 | -0.0045737 | 0.042603 | 0.061135 | -0.019363 | -0.013608 | 62.1048 | -59.4315 | 1.3733 | -60.1868 | 62.0132 | -60.2188 | -60.1639 | -60.4202 | 0.29297 | -60.4065 | 61.9125 | 62.0041 | -60.0861 | -60.2783 | -0.07782 | -0.022888 | -0.027465 | 0.70953 | -0.045777 | -0.022889 | 0.064087 | 0.054931 | -0.13733 | -0.12817 | -0.27924 | -0.2655 | -0.12817 | -0.036621 | 122.1542 | 122.2458 | 61.5143 | -122.2046 | 122.0535 | 122.1451 | 60.434 | -122.319
1157.4844 | 122.5067 | -60.1639 | 62.0178 | 0.013046 | -0.034748 | 0.11338 | 0.025015 | 0.054151 | -0.022031 | -0.021856 | 0.022583 | -0.00094205 | 0.042176 | 0.06028 | -0.014449 | -0.014249 | 62.146 | -59.4269 | 1.3184 | -60.1913 | 62.0407 | -60.228 | -60.1364 | -60.3973 | 0.37994 | -60.4248 | 61.9171 | 61.9537 | -60.0998 | -60.2371 | -0.064087 | 0.027465 | 0.022888 | 0.737 | -0.027466 | -0.054931 | 0.12817 | 0.064087 | -0.073243 | -0.10071 | -0.23346 | -0.26093 | -0.18768 | -0.064087 | 122.2046 | 122.3099 | 61.4822 | -122.1542 | 122.081 | 122.1176 | 60.5438 | -122.2549
1159.2031 | 122.3831 | -60.1181 | 62.1552 | 0.0054168 | -0.034321 | 0.11509 | 0.024374 | 0.053083 | -0.019467 | -0.02271 | 0.014954 | -8.7654e-05 | 0.041962 | 0.061776 | -0.0121 | -0.013394 | 62.1506 | -59.3719 | 1.2222 | -60.1593 | 62.1643 | -60.1547 | -60.0998 | -60.3745 | 0.35706 | -60.4706 | 62.0407 | 62.1048 | -60.0357 | -60.228 | -0.036621 | 0.018311 | 0.009156 | 0.74615 | -0.041199 | -0.05951 | -0.004577 | 0.082397 | -0.10986 | -0.11444 | -0.25635 | -0.35248 | -0.24262 | -0.050354 | 122.2824 | 122.2687 | 61.3403 | -122.2549 | 122.1588 | 122.2229 | 60.4752 | -122.3831
1160.9844 | 122.493 | -60.0403 | 62.1597 | 0.0054168 | -0.037098 | 0.11295 | 0.02587 | 0.055006 | -0.024167 | -0.021429 | 0.0073242 | -0.0022239 | 0.041748 | 0.059853 | -0.01509 | -0.013394 | 62.2925 | -59.1064 | 1.3687 | -60.0403 | 62.1368 | -60.0815 | -60.0082 | -60.2463 | 0.59509 | -60.2783 | 62.0132 | 62.1002 | -59.9625 | -60.1501 | -0.041199 | 0.032043 | -0.022888 | 0.93384 | 0 | -0.032043 | 0.13275 | 0.07782 | -0.10986 | -0.14648 | -0.20599 | -0.23804 | -0.12817 | -0.059509 | 122.1771 | 122.3328 | 61.409 | -122.168 | 122.0535 | 122.1405 | 60.6354 | -122.3099
1162.75 | 122.3419 | -60.0815 | 62.2009 | 0.013046 | -0.034534 | 0.11616 | 0.025443 | 0.052442 | -0.018186 | -0.021429 | 0.014954 | 0.00055335 | 0.041535 | 0.061562 | -0.012313 | -0.012112 | 62.2696 | -59.2072 | 1.268 | -60.0632 | 62.2147 | -60.0952 | -60.0037 | -60.3104 | 0.60425 | -60.3745 | 62.0773 | 62.146 | -59.9625 | -60.1685 | -0.013733 | 0.07782 | 0.013733 | 0.87433 | 0.018311 | -0.059509 | 0.068664 | 0.11902 | -0.086975 | -0.1236 | -0.22888 | -0.29297 | -0.20599 | -0.054932 | 122.2961 | 122.3511 | 61.3495 | -122.2046 | 122.1588 | 122.2275 | 60.6857 | -122.3694
1164.5312 | 122.4426 | -59.967 | 62.2833 | -0.0022127 | -0.037739 | 0.11658 | 0.029501 | 0.052015 | -0.030149 | -0.023565 | -0.0003053 | -0.0047873 | 0.039398 | 0.060707 | -0.017013 | -0.011471 | 62.3474 | -59.0057 | 1.2634 | -59.9625 | 62.2238 | -59.9991 | -59.8801 | -60.2005 | 0.66376 | -60.2005 | 62.1323 | 62.2375 | -59.8389 | -60.054 | -0.032043 | 0.086975 | -0.059509 | 0.9613 | 0.004578 | -0.082397 | 0.064087 | 0.12817 | -0.086975 | -0.15106 | -0.23346 | -0.23346 | -0.14648 | -0.045776 | 122.1909 | 122.3145 | 61.2305 | -122.1634 | 122.0993 | 122.2046 | 60.6308 | -122.3373
1166.2656 | 122.4747 | -59.9442 | 62.2467 | -0.0022127 | -0.036457 | 0.11594 | 0.026297 | 0.053724 | -0.026303 | -0.024847 | 0.0073242 | -0.0026511 | 0.04068 | 0.059212 | -0.016799 | -0.014462 | 62.3474 | -59.0424 | 1.2543 | -59.967 | 62.1826 | -60.022 | -59.935 | -60.1776 | 0.76446 | -60.2097 | 62.1048 | 62.1597 | -59.8938 | -60.0769 | -0.07782 | 0.009155 | -0.064087 | 0.90179 | -0.022888 | -0.032043 | 0.10071 | 0.050354 | -0.13275 | -0.14191 | -0.23346 | -0.2655 | -0.13275 | -0.086975 | 122.1268 | 122.2916 | 61.1984 | -122.1817 | 122.0489 | 122.1039 | 60.7086 | -122.3236
1168.0469 | 122.4792 | -59.8755 | 62.352 | -0.0022127 | -0.040516 | 0.11851 | 0.029074 | 0.053297 | -0.028653 | -0.026342 | 0.014954 | -0.0039329 | 0.04303 | 0.060921 | -0.020645 | -0.012112 | 62.3932 | -58.992 | 1.1993 | -59.9121 | 62.2925 | -59.9213 | -59.848 | -60.1547 | 0.71869 | -60.1456 | 62.2009 | 62.2833 | -59.7931 | -59.9945 | -0.045777 | 0.027466 | -0.05951 | 0.88348 | -0.036621 | -0.064087 | 0.041198 | 0.082397 | -0.11902 | -0.15106 | -0.27924 | -0.27008 | -0.15106 | -0.068665 | 122.168 | 122.2687 | 61.0748 | -122.2 | 122.0764 | 122.1588 | 60.5942 | -122.3465
1169.7656 | 122.5204 | -59.8251 | 62.3795 | -0.0022127 | -0.037952 | 0.11765 | 0.027365 | 0.054365 | -0.027585 | -0.025274 | 0.0073242 | -0.0022239 | 0.04068 | 0.059426 | -0.017654 | -0.013821 | 62.5031 | -58.8638 | 1.2177 | -59.8389 | 62.3383 | -59.8755 | -59.7794 | -59.9991 | 0.87891 | -60.0082 | 62.233 | 62.3108 | -59.7382 | -59.9533 | -0.050354 | 0.045776 | -0.041199 | 0.9613 | -0.013733 | -0.059509 | 0.1236 | 0.086975 | -0.12817 | -0.14648 | -0.17395 | -0.18311 | -0.054932 | -0.068665 | 122.1634 | 122.3282 | 61.0428 | -122.1588 | 122.0581 | 122.1359 | 60.704 | -122.3328
1171.5 | 122.374 | -59.8251 | 62.4847 | -0.0022127 | -0.032612 | 0.11573 | 0.030569 | 0.053938 | -0.025235 | -0.025274 | -0.0079343 | -0.00094205 | 0.042816 | 0.061776 | -0.015945 | -0.015317 | 62.5122 | -58.8409 | 1.1307 | -59.8068 | 62.4161 | -59.8709 | -59.7519 | -60.054 | 0.79651 | -60.0952 | 62.3657 | 62.4115 | -59.7153 | -59.8709 | -0.045777 | 0.073242 | -0.068664 | 0.98419 | 0.01831 | -0.054932 | 0.027466 | 0.10986 | -0.045777 | -0.11902 | -0.22888 | -0.27008 | -0.2243 | -0.073242 | 122.2412 | 122.3373 | 60.9558 | -122.2366 | 122.1909 | 122.2366 | 60.6216 | -122.3557
1173.2188 | 122.4609 | -59.7656 | 62.4664 | 0.0054168 | -0.036671 | 0.11594 | 0.02587 | 0.050733 | -0.026731 | -0.024419 | 0.014954 | -0.0041465 | 0.041748 | 0.06263 | -0.018081 | -0.01318 | 62.5442 | -58.7814 | 1.0895 | -59.7839 | 62.4069 | -59.816 | -59.7336 | -60.0037 | 0.81482 | -60.0357 | 62.3154 | 62.3657 | -59.6786 | -59.8801 | -0.050354 | 0.032043 | -0.05951 | 0.98419 | -0.018311 | -0.050354 | 0.077819 | 0.086975 | -0.11444 | -0.15106 | -0.23804 | -0.27008 | -0.15564 | -0.10071 | 122.1725 | 122.3099 | 60.8551 | -122.2 | 122.081 | 122.1313 | 60.5804 | -122.3465
1175 | 122.4243 | -59.7427 | 62.5168 | -0.0022127 | -0.031971 | 0.11616 | 0.026938 | 0.055006 | -0.019681 | -0.022924 | 0.014954 | -0.00094205 | 0.042816 | 0.062844 | -0.01509 | -0.017239 | 62.5854 | -58.7448 | 1.0117 | -59.7382 | 62.5031 | -59.7656 | -59.7198 | -59.935 | 0.86517 | -60.022 | 62.4023 | 62.4435 | -59.6558 | -59.8709 | -0.022888 | 0.022888 | -0.013733 | 0.99792 | 0.004578 | -0.01831 | 0.068664 | 0.086975 | -0.12817 | -0.11444 | -0.19226 | -0.27924 | -0.15106 | -0.073243 | 122.2458 | 122.3282 | 60.7544 | -122.2366 | 122.1451 | 122.1863 | 60.6079 | -122.3877
1176.7656 | 122.4014 | -59.6466 | 62.6221 | 0.0054168 | -0.036243 | 0.11359 | 0.027579 | 0.053724 | -0.02609 | -0.02271 | -0.0003053 | -0.0024375 | 0.041535 | 0.060494 | -0.020004 | -0.013608 | 62.6862 | -58.5434 | 1.0254 | -59.6191 | 62.5076 | -59.6695 | -59.6008 | -59.8251 | 0.87433 | -59.8618 | 62.4298 | 62.5076 | -59.5276 | -59.7519 | -0.022889 | 0.045776 | -0.11444 | 1.1032 | 0.027465 | -0.018311 | 0.064087 | 0.11902 | -0.10529 | -0.19226 | -0.17853 | -0.21515 | -0.10986 | -0.11444 | 122.1542 | 122.3328 | 60.672 | -122.2229 | 122.0764 | 122.1542 | 60.5209 | -122.374
1178.5469 | 122.4518 | -59.5963 | 62.5992 | -0.0022127 | -0.040729 | 0.1153 | 0.027365 | 0.052442 | -0.025876 | -0.024419 | -0.0079343 | -0.0015829 | 0.043457 | 0.061135 | -0.014236 | -0.012753 | 62.6816 | -58.5342 | 0.89264 | -59.6329 | 62.558 | -59.6695 | -59.5917 | -59.8297 | 0.75531 | -59.8801 | 62.439 | 62.5259 | -59.5184 | -59.7382 | -0.073243 | 0.004577 | -0.041199 | 1.062 | -0.036622 | -0.041199 | 0.082398 | 0.077819 | -0.14191 | -0.16022 | -0.23346 | -0.28381 | -0.14191 | -0.073242 | 122.1542 | 122.2778 | 60.4889 | -122.1909 | 122.0352 | 122.1222 | 60.3516 | -122.3373
1180.2656 | 122.3648 | -59.5963 | 62.6816 | -0.0022127 | -0.035816 | 0.11637 | 0.024802 | 0.052656 | -0.02139 | -0.021429 | 0.0073242 | -0.0011557 | 0.041321 | 0.061562 | -0.011245 | -0.015317 | 62.7594 | -58.4656 | 0.79651 | -59.5688 | 62.6999 | -59.5871 | -59.5367 | -59.7885 | 0.8194 | -59.8938 | 62.5717 | 62.6129 | -59.4864 | -59.6832 | 0.009155 | 0.059509 | 0.01831 | 1.1307 | 0.027465 | -0.032044 | 0.077819 | 0.10986 | -0.086976 | -0.10986 | -0.19226 | -0.29755 | -0.21057 | -0.068665 | 122.2961 | 122.3557 | 60.3928 | -122.2183 | 122.168 | 122.2092 | 60.4156 | -122.3648
1182.0469 | 122.4472 | -59.5322 | 62.6816 | 0.0054168 | -0.039875 | 0.11594 | 0.025656 | 0.053297 | -0.02844 | -0.022283 | 0.0073242 | -0.0045737 | 0.041535 | 0.058785 | -0.017013 | -0.01318 | 62.7457 | -58.4244 | 0.79651 | -59.5459 | 62.5992 | -59.6146 | -59.5139 | -59.7336 | 0.90179 | -59.7885 | 62.5122 | 62.5763 | -59.4635 | -59.6649 | -0.082397 | 0.018311 | -0.082398 | 1.1078 | -0.013732 | -0.032043 | 0.064087 | 0.068665 | -0.13275 | -0.16937 | -0.20142 | -0.25635 | -0.1236 | -0.10529 | 122.1313 | 122.2778 | 60.3287 | -122.1954 | 122.0444 | 122.1085 | 60.434 | -122.3465
1183.7344 | 122.3694 | -59.5001 | 62.7869 | -0.0098417 | -0.03368 | 0.11509 | 0.02352 | 0.052869 | -0.019467 | -0.021856 | 0.0073242 | 0.0022623 | 0.042603 | 0.06028 | -0.015731 | -0.014249 | 62.8693 | -58.342 | 0.64087 | -59.4635 | 62.7731 | -59.5047 | -59.4406 | -59.6832 | 0.94299 | -59.7748 | 62.645 | 62.6953 | -59.3765 | -59.5917 | -0.004578 | 0.059509 | -0.013733 | 1.1581 | 0.036621 | -0.022888 | 0.082398 | 0.1236 | -0.091553 | -0.14191 | -0.18311 | -0.27466 | -0.1831 | -0.091553 | 122.2733 | 122.3694 | 60.141 | -122.2275 | 122.1451 | 122.1954 | 60.4431 | -122.3785
1185.5156 | 122.5067 | -59.3079 | 62.8738 | -0.0098417 | -0.038593 | 0.11893 | 0.030569 | 0.053938 | -0.02908 | -0.023138 | 0.0073242 | -0.0054281 | 0.040039 | 0.059639 | -0.019149 | -0.011258 | 62.9425 | -58.1177 | 0.62256 | -59.317 | 62.8647 | -59.3903 | -59.3033 | -59.5367 | 1.0391 | -59.5505 | 62.7411 | 62.8464 | -59.2163 | -59.4315 | -0.082398 | 0.004577 | -0.009155 | 1.1902 | -0.009156 | -0.013733 | 0.068665 | 0.091552 | -0.1236 | -0.13275 | -0.22888 | -0.24262 | -0.11902 | -0.027465 | 122.1725 | 122.2504 | 59.9304 | -122.1771 | 122.049 | 122.1542 | 60.347 | -122.3053
1187.2344 | 122.4197 | -59.2896 | 62.9242 | 0.013046 | -0.034962 | 0.1168 | 0.026083 | 0.052229 | -0.022244 | -0.024633 | 0.0073242 | -0.00051485 | 0.040894 | 0.059212 | -0.014877 | -0.014249 | 63.0341 | -58.0307 | 0.53558 | -59.2575 | 63.002 | -59.3262 | -59.2438 | -59.4727 | 1.2772 | -59.5688 | 62.8418 | 62.9013 | -59.2026 | -59.3765 | -0.036621 | 0.045777 | 0.07782 | 1.2589 | 0.032044 | -0.013733 | 0.10986 | 0.086975 | -0.086975 | -0.082397 | -0.1831 | -0.27924 | -0.19226 | -0.022888 | 122.2916 | 122.3236 | 59.8251 | -122.168 | 122.1313 | 122.1909 | 60.5667 | -122.3007
1188.9531 | 122.3877 | -59.2941 | 62.9471 | 0.0054168 | -0.032398 | 0.1121 | 0.028647 | 0.053083 | -0.023313 | -0.022497 | 0.014954 | -0.0015829 | 0.042816 | 0.061989 | -0.015518 | -0.012967 | 62.9608 | -58.1085 | 0.41199 | -59.3262 | 62.9654 | -59.3262 | -59.2575 | -59.5322 | 1.3138 | -59.6283 | 62.8647 | 62.9517 | -59.2117 | -59.3948 | -0.032044 | 0.036621 | 0.01831 | 1.1856 | -0.032044 | -0.068665 | 0.013732 | 0.082397 | -0.10071 | -0.082398 | -0.23804 | -0.33417 | -0.23346 | 0.004577 | 122.2595 | 122.2549 | 59.7061 | -122.2046 | 122.1588 | 122.2458 | 60.6079 | -122.3419
1190.6719 | 122.438 | -59.1843 | 63.0341 | 0.0054168 | -0.036884 | 0.11594 | 0.027152 | 0.052442 | -0.02609 | -0.022497 | -0.0003053 | -0.0045737 | 0.041748 | 0.059212 | -0.014663 | -0.012112 | 63.1119 | -57.8201 | 0.42572 | -59.1797 | 62.9471 | -59.23 | -59.1476 | -59.3445 | 1.442 | -59.4086 | 62.8555 | 62.9425 | -59.0927 | -59.285 | -0.045777 | 0.036621 | -0.086975 | 1.3641 | 0.004578 | -0.032043 | 0.077819 | 0.091553 | -0.10071 | -0.17853 | -0.16022 | -0.2243 | -0.1236 | -0.091553 | 122.1313 | 122.2961 | 59.61 | -122.1817 | 122.0398 | 122.1268 | 60.6262 | -122.319
1192.4531 | 122.4518 | -59.0836 | 63.0936 | 0.0054168 | -0.036457 | 0.11551 | 0.022025 | 0.052442 | -0.024594 | -0.023565 | 0.0073242 | -0.0024375 | 0.040894 | 0.060494 | -0.018295 | -0.012326 | 63.1989 | -57.692 | 0.32501 | -59.0836 | 63.0524 | -59.1614 | -59.0607 | -59.2575 | 1.5472 | -59.3308 | 62.9608 | 62.9929 | -58.9966 | -59.198 | -0.07782 | 0.022888 | -0.041199 | 1.3916 | 0 | -0.022888 | 0.10529 | 0.086975 | -0.11444 | -0.13275 | -0.17395 | -0.24719 | -0.13275 | -0.10071 | 122.1359 | 122.2824 | 59.4086 | -122.1542 | 122.0444 | 122.0764 | 60.6308 | -122.2916
1194.1875 | 122.438 | -59.0378 | 63.1622 | 0.013046 | -0.040302 | 0.1153 | 0.026083 | 0.051801 | -0.025235 | -0.023565 | 0.022583 | -0.0028647 | 0.041535 | 0.058571 | -0.018722 | -0.013608 | 63.2629 | -57.5958 | 0.3067 | -59.0607 | 63.0936 | -59.0698 | -59.0195 | -59.2392 | 1.68 | -59.2987 | 63.0112 | 63.0981 | -58.9554 | -59.1431 | -0.032043 | 0.018311 | -0.068664 | 1.442 | -0.022888 | -0.041199 | 0.10071 | 0.082398 | -0.10528 | -0.15106 | -0.20142 | -0.26093 | -0.15564 | -0.064086 | 122.1313 | 122.3007 | 59.3445 | -122.1817 | 122.049 | 122.1359 | 60.7178 | -122.3053
1195.9688 | 122.4976 | -58.8181 | 63.3591 | -0.0022127 | -0.043934 | 0.11808 | 0.027152 | 0.055219 | -0.028012 | -0.025701 | 0.0073242 | -0.0041465 | 0.042603 | 0.060067 | -0.01744 | -0.01318 | 63.4094 | -57.3166 | 0.33875 | -58.8593 | 63.3453 | -58.873 | -58.7997 | -59.0652 | 1.7715 | -59.1064 | 63.2217 | 63.3041 | -58.7494 | -58.9828 | -0.054932 | 0.01831 | -0.013733 | 1.5015 | -0.041199 | -0.059509 | 0.050354 | 0.068664 | -0.1648 | -0.13733 | -0.24719 | -0.28839 | -0.1236 | -0.054932 | 122.1634 | 122.2275 | 59.1568 | -122.1588 | 122.0398 | 122.1222 | 60.5896 | -122.3419
1197.7344 | 122.4152 | -58.7082 | 63.5422 | 0.013046 | -0.036671 | 0.11616 | 0.027152 | 0.053724 | -0.021604 | -0.023778 | 0.014954 | -0.0011557 | 0.042603 | 0.058144 | -0.014022 | -0.016171 | 63.6063 | -57.0465 | 0.13733 | -58.6853 | 63.5971 | -58.7128 | -58.6578 | -58.8913 | 1.8311 | -58.9874 | 63.4644 | 63.5284 | -58.5983 | -58.8043 | -0.004578 | 0.050354 | 0.054932 | 1.6617 | 0.022888 | -0.027466 | 0.064087 | 0.10986 | -0.09613 | -0.07782 | -0.1831 | -0.27924 | -0.18311 | -0.013733 | 122.3053 | 122.3145 | 58.8455 | -122.2 | 122.1725 | 122.2366 | 60.5392 | -122.3465
1199.4688 | 122.406 | -58.5526 | 63.6932 | -0.0022127 | -0.034962 | 0.11487 | 0.029715 | 0.053297 | -0.022031 | -0.024419 | 0.014954 | -0.00030125 | 0.044525 | 0.060707 | -0.015945 | -0.013394 | 63.739 | -56.7627 | 0.10529 | -58.5297 | 63.739 | -58.5388 | -58.4702 | -58.7219 | 1.9135 | -58.8318 | 63.6246 | 63.6658 | -58.4518 | -58.6349 | 0.013733 | 0.082397 | 0.045777 | 1.7899 | 0.022888 | -0.059509 | 0.045777 | 0.10071 | -0.082398 | -0.068664 | -0.16937 | -0.27924 | -0.19684 | -0.027466 | 122.2916 | 122.2916 | 58.6578 | -122.1634 | 122.1771 | 122.2183 | 60.466 | -122.3282
1201.25 | 122.4518 | -58.5342 | 63.6475 | 0.0054168 | -0.03902 | 0.11573 | 0.029074 | 0.054365 | -0.028867 | -0.026128 | 0.0073242 | -0.0030783 | 0.042603 | 0.061562 | -0.019363 | -0.013608 | 63.7344 | -56.8176 | 0.073242 | -58.548 | 63.6383 | -58.58 | -58.493 | -58.7448 | 1.9226 | -58.8135 | 63.5376 | 63.6154 | -58.4702 | -58.6624 | -0.045776 | 0.041199 | -0.009155 | 1.7166 | -0.013733 | -0.054932 | 0.086975 | 0.064087 | -0.12817 | -0.10986 | -0.21057 | -0.27924 | -0.15106 | -0.032044 | 122.1725 | 122.2687 | 58.6075 | -122.1405 | 122.0718 | 122.1497 | 60.4568 | -122.3099
1203.0312 | 122.3602 | -58.5022 | 63.7665 | -0.0022127 | -0.034534 | 0.11551 | 0.024588 | 0.052015 | -0.021604 | -0.023778 | -0.0003053 | 0.0020487 | 0.041748 | 0.058785 | -0.013381 | -0.014462 | 63.7619 | -56.7719 | -0.17853 | -58.5114 | 63.7573 | -58.5297 | -58.4747 | -58.7265 | 1.8631 | -58.8547 | 63.6429 | 63.707 | -58.4198 | -58.6304 | -0.027466 | 0.027466 | -0.009155 | 1.7303 | -0.009156 | -0.036622 | -0.004577 | 0.082397 | -0.12817 | -0.1236 | -0.2243 | -0.35248 | -0.2243 | -0.059509 | 122.2595 | 122.2641 | 58.3237 | -122.2412 | 122.1451 | 122.2092 | 60.3653 | -122.3969
1204.7344 | 122.4792 | -58.4198 | 63.7527 | 0.013046 | -0.035175 | 0.11701 | 0.025443 | 0.05351 | -0.022885 | -0.02506 | 0.014954 | -0.0017965 | 0.039612 | 0.063698 | -0.01744 | -0.013608 | 63.8306 | -56.6895 | -0.19684 | -58.4564 | 63.8123 | -58.4839 | -58.3786 | -58.6212 | 2.0187 | -58.7677 | 63.6795 | 63.7573 | -58.374 | -58.5388 | -0.064087 | 0.041199 | 0.059509 | 1.7303 | -0.036621 | -0.07782 | 0.077819 | 0.045777 | -0.11902 | -0.073243 | -0.20142 | -0.3479 | -0.22888 | 0.004577 | 122.2321 | 122.2504 | 58.223 | -122.1313 | 122.0993 | 122.1771 | 60.4385 | -122.2916
1206.5156 | 122.493 | -58.3145 | 63.8535 | -0.0022127 | -0.036243 | 0.1153 | 0.02886 | 0.050733 | -0.023313 | -0.022497 | 0.014954 | -0.00051485 | 0.040253 | 0.060921 | -0.015518 | -0.013821 | 63.9038 | -56.5155 | -0.27466 | -58.374 | 63.8626 | -58.3878 | -58.3282 | -58.5297 | 2.0874 | -58.6441 | 63.7619 | 63.826 | -58.2733 | -58.4702 | -0.073242 | -0.013733 | 0.009155 | 1.799 | -0.059509 | -0.045776 | 0.050354 | 0.041199 | -0.15564 | -0.091553 | -0.21515 | -0.32959 | -0.17395 | -0.027466 | 122.1771 | 122.2183 | 58.0399 | -122.1817 | 122.0764 | 122.1405 | 60.4019 | -122.3236
1208.2969 | 122.3648 | -58.2367 | 64.0411 | -0.0022127 | -0.037952 | 0.12 | 0.027579 | 0.052442 | -0.028226 | -0.024847 | 0.0073242 | -0.0022239 | 0.044312 | 0.059212 | -0.014449 | -0.011258 | 64.0686 | -56.2454 | -0.32959 | -58.1772 | 64.0228 | -58.2275 | -58.1543 | -58.4152 | 2.243 | -58.5022 | 63.9359 | 63.9954 | -58.0948 | -58.3099 | 0.009155 | 0.082397 | -0.018311 | 1.9913 | 0.059509 | -0.022888 | 0.027466 | 0.14191 | -0.073243 | -0.10529 | -0.17853 | -0.2655 | -0.19226 | -0.045777 | 122.2595 | 122.3053 | 57.9071 | -122.1954 | 122.1725 | 122.2321 | 60.4797 | -122.3511
1210.0312 | 122.5159 | -58.1039 | 64.064 | 0.013046 | -0.036457 | 0.11765 | 0.031851 | 0.053083 | -0.032285 | -0.025274 | -0.0003053 | -0.0047873 | 0.04303 | 0.058571 | -0.01979 | -0.012753 | 64.1876 | -56.1264 | -0.2655 | -58.0994 | 64.0366 | -58.1406 | -58.1039 | -58.255 | 2.3346 | -58.3145 | 63.913 | 63.9954 | -57.9895 | -58.223 | -0.036621 | 0 | -0.027466 | 1.9775 | 0.004578 | 0.004578 | 0.1236 | 0.11444 | -0.11902 | -0.15106 | -0.15106 | -0.21057 | -0.091553 | -0.068665 | 122.1405 | 122.2916 | 57.8384 | -122.168 | 122.0169 | 122.0993 | 60.4385 | -122.287
1211.7969 | 122.3602 | -58.0719 | 64.2517 | 0.0054168 | -0.033893 | 0.11829 | 0.030142 | 0.055006 | -0.024808 | -0.023565 | -0.0003053 | -0.0022239 | 0.043671 | 0.062203 | -0.017867 | -0.015744 | 64.2654 | -56.0211 | -0.39825 | -58.0078 | 64.1922 | -58.0673 | -57.9987 | -58.2184 | 2.2934 | -58.3328 | 64.119 | 64.1785 | -57.9391 | -58.1223 | 0.004577 | 0.073242 | -0.059509 | 2.0508 | 0.064087 | -0.009155 | 0.013733 | 0.13275 | -0.050354 | -0.13275 | -0.14648 | -0.26093 | -0.21057 | -0.073242 | 122.2641 | 122.3373 | 57.6736 | -122.2504 | 122.1909 | 122.2504 | 60.3653 | -122.374
1213.5938 | 122.374 | -58.0307 | 64.2288 | -0.0098417 | -0.035816 | 0.11359 | 0.024374 | 0.054578 | -0.019895 | -0.021856 | 0.0073242 | 0.00055335 | 0.042603 | 0.061562 | -0.014236 | -0.01254 | 64.238 | -56.0898 | -0.60425 | -58.0353 | 64.238 | -58.0444 | -58.0124 | -58.2047 | 2.1332 | -58.374 | 64.119 | 64.1968 | -57.9208 | -58.1223 | -0.013733 | 0.018311 | 0.009155 | 1.9409 | -0.004577 | -0.022888 | 0.009155 | 0.10986 | -0.091552 | -0.10986 | -0.17395 | -0.34332 | -0.25177 | -0.032044 | 122.2687 | 122.2687 | 57.4265 | -122.2412 | 122.1497 | 122.2275 | 60.1639 | -122.3511
1215.3125 | 122.4197 | -57.8751 | 64.357 | 0.0054168 | -0.033466 | 0.11594 | 0.028433 | 0.05351 | -0.019895 | -0.022283 | -0.0003053 | -0.00072845 | 0.043671 | 0.061135 | -0.015518 | -0.014249 | 64.4394 | -55.7785 | -0.5722 | -57.8522 | 64.3707 | -57.8979 | -57.8522 | -57.9803 | 2.3163 | -58.1589 | 64.2609 | 64.3341 | -57.7789 | -57.9666 | -0.022888 | 0.022888 | 0.013733 | 2.0966 | 0.022888 | 0 | 0.082397 | 0.09613 | -0.091553 | -0.096131 | -0.10529 | -0.28381 | -0.19226 | -0.022889 | 122.2458 | 122.3145 | 57.3029 | -122.2092 | 122.1359 | 122.2092 | 60.1913 | -122.3236
1217.0781 | 122.406 | -57.8384 | 64.389 | -0.0022127 | -0.031544 | 0.11594 | 0.028647 | 0.053724 | -0.023526 | -0.020574 | 0.0073242 | -0.0024375 | 0.044953 | 0.06028 | -0.015304 | -0.01318 | 64.4348 | -55.7648 | -0.60425 | -57.8064 | 64.3982 | -57.8888 | -57.8293 | -57.962 | 2.3621 | -58.1223 | 64.2883 | 64.3753 | -57.7652 | -57.9437 | -0.050354 | 0.009155 | 0.009155 | 2.0737 | 0.032044 | 0.022889 | 0.045776 | 0.073242 | -0.10529 | -0.10071 | -0.1236 | -0.28381 | -0.17853 | -0.013733 | 122.2366 | 122.2733 | 57.2342 | -122.2183 | 122.1268 | 122.2137 | 60.2005 | -122.3328
1218.8438 | 122.3557 | -57.7103 | 64.5538 | -0.0022127 | -0.032398 | 0.11487 | 0.030997 | 0.053297 | -0.025662 | -0.022924 | 0.0073242 | -0.0030783 | 0.042176 | 0.061135 | -0.019363 | -0.012326 | 64.4989 | -55.632 | -0.62256 | -57.7286 | 64.4943 | -57.756 | -57.7011 | -57.9163 | 2.3849 | -58.0536 | 64.4073 | 64.4852 | -57.6508 | -57.8156 | -0.045776 | 0.009155 | -0.059509 | 2.0782 | -0.018311 | -0.027466 | -0.054932 | 0.059509 | -0.10529 | -0.14648 | -0.20599 | -0.34332 | -0.23804 | -0.068665 | 122.2046 | 122.2092 | 57.0877 | -122.2549 | 122.1176 | 122.1954 | 60.0952 | -122.3694
1220.5781 | 122.3785 | -57.6965 | 64.5264 | 0.013046 | -0.034962 | 0.11722 | 0.026083 | 0.055006 | -0.022031 | -0.023565 | 0.014954 | 0.0018351 | 0.042389 | 0.061562 | -0.015518 | -0.013394 | 64.5264 | -55.5588 | -0.8194 | -57.7148 | 64.5538 | -57.7286 | -57.6828 | -57.9163 | 2.0554 | -58.049 | 64.4302 | 64.5172 | -57.6004 | -57.811 | -0.032044 | 0.013733 | 0.027466 | 2.1378 | -0.018311 | -0.032044 | 0 | 0.09613 | -0.11444 | -0.09613 | -0.21973 | -0.35248 | -0.23804 | -0.009155 | 122.2504 | 122.2229 | 56.8771 | -122.2092 | 122.1268 | 122.2137 | 59.7519 | -122.3373
1222.3594 | 122.4747 | -57.5226 | 64.6225 | 0.0054168 | -0.037525 | 0.11786 | 0.029929 | 0.055647 | -0.031003 | -0.026342 | 0.0073242 | -0.0050009 | 0.042389 | 0.061562 | -0.019149 | -0.012326 | 64.7369 | -55.22 | -0.6958 | -57.4905 | 64.595 | -57.5867 | -57.5272 | -57.6736 | 2.1057 | -57.756 | 64.4806 | 64.595 | -57.4539 | -57.6553 | -0.064087 | -0.004578 | -0.027466 | 2.3026 | 0.032043 | 0.036621 | 0.11444 | 0.068665 | -0.13275 | -0.14191 | -0.15106 | -0.23346 | -0.10071 | -0.027466 | 122.1176 | 122.2595 | 56.8268 | -122.1497 | 122.0032 | 122.1176 | 59.6283 | -122.2778
1224.1406 | 122.374 | -57.5226 | 64.7461 | 0.020676 | -0.03603 | 0.11616 | 0.027579 | 0.055006 | -0.024167 | -0.022924 | -0.0003053 | -0.0013693 | 0.042816 | 0.059639 | -0.016799 | -0.014676 | 64.7232 | -55.2658 | -0.96588 | -57.5134 | 64.7415 | -57.55 | -57.4631 | -57.7194 | 1.9638 | -57.8384 | 64.6408 | 64.7003 | -57.431 | -57.6233 | -0.027466 | 0.059509 | -0.004578 | 2.2568 | 0.009155 | -0.050354 | -0.022888 | 0.091553 | -0.10071 | -0.10529 | -0.19684 | -0.31586 | -0.21515 | -0.045777 | 122.2641 | 122.2458 | 56.5567 | -122.2092 | 122.1634 | 122.2229 | 59.4864 | -122.3694
1225.9219 | 122.3602 | -57.4493 | 64.8056 | 0.0054168 | -0.029835 | 0.11381 | 0.027792 | 0.05351 | -0.020963 | -0.022283 | -0.0003053 | 0.0026895 | 0.043671 | 0.060494 | -0.01509 | -0.013394 | 64.8056 | -55.1651 | -1.0437 | -57.4402 | 64.8331 | -57.4585 | -57.399 | -57.6141 | 1.8127 | -57.7927 | 64.7003 | 64.769 | -57.3303 | -57.5455 | -0.009155 | 0.050354 | 0.027466 | 2.2842 | 0.009155 | -0.041199 | 0 | 0.11902 | -0.09613 | -0.10529 | -0.1648 | -0.34332 | -0.24719 | -0.036621 | 122.2824 | 122.2549 | 56.4056 | -122.2046 | 122.1497 | 122.2183 | 59.2621 | -122.3511
1227.7031 | 122.3877 | -56.8588 | 65.3229 | 0.013046 | -0.034748 | 0.11381 | 0.026938 | 0.053083 | -0.023313 | -0.021642 | 0.022583 | -0.00051485 | 0.041535 | 0.060707 | -0.014663 | -0.013821 | 65.4099 | -53.8467 | -0.89264 | -56.7261 | 65.4282 | -56.8542 | -56.7993 | -56.9733 | 2.037 | -57.1243 | 65.2679 | 65.3687 | -56.749 | -56.9504 | 0.004578 | 0.05951 | 0.10529 | 3.0121 | 0.13275 | 0.073242 | 0.086975 | 0.10986 | -0.091552 | -0.054932 | -0.11444 | -0.2655 | -0.17395 | 0.045776 | 122.287 | 122.2687 | 55.9662 | -122.1222 | 122.1268 | 122.2275 | 58.8959 | -122.2733
1229.4219 | 122.3373 | -56.6711 | 65.5701 | -0.0098417 | -0.03603 | 0.11509 | 0.025229 | 0.057783 | -0.023526 | -0.01972 | 0.0073242 | 0.0018351 | 0.041321 | 0.061989 | -0.01509 | -0.013608 | 65.7166 | -53.5355 | -0.8606 | -56.5979 | 65.6067 | -56.6345 | -56.5933 | -56.781 | 2.0874 | -56.9641 | 65.4877 | 65.5563 | -56.5704 | -56.749 | 0.036622 | 0.07782 | 0.036621 | 3.1357 | 0.073243 | -0.004577 | 0.14648 | 0.10071 | -0.077819 | -0.082397 | -0.10986 | -0.29297 | -0.21515 | -0.013733 | 122.2778 | 122.3877 | 55.8105 | -122.1634 | 122.1588 | 122.2275 | 58.7585 | -122.319
1231.2188 | 122.3969 | -56.5063 | 65.744 | -0.0022127 | -0.036671 | 0.11786 | 0.02822 | 0.054792 | -0.025449 | -0.024633 | 0.0073242 | -0.0017965 | 0.041748 | 0.06028 | -0.018081 | -0.011471 | 65.7394 | -53.4073 | -0.94299 | -56.4651 | 65.7898 | -56.5109 | -56.4468 | -56.6757 | 2.0874 | -56.813 | 65.6799 | 65.7349 | -56.3919 | -56.5796 | -0.004577 | 0.05951 | 0.045776 | 3.0991 | 0.041199 | -0.018311 | -0.004578 | 0.11444 | -0.073242 | -0.064087 | -0.16937 | -0.3067 | -0.23346 | -0.009156 | 122.2961 | 122.2458 | 55.5634 | -122.1909 | 122.1863 | 122.2412 | 58.5938 | -122.3236
1233 | 122.5067 | -56.1493 | 66.0095 | -0.0022127 | -0.035602 | 0.11872 | 0.029288 | 0.055433 | -0.030149 | -0.023351 | 0.0073242 | -0.0073507 | 0.041535 | 0.060494 | -0.020431 | -0.011685 | 66.0645 | -52.8076 | -0.78278 | -56.1447 | 65.9821 | -56.2225 | -56.1539 | -56.3278 | 2.124 | -56.4239 | 65.8585 | 65.95 | -56.1035 | -56.2775 | -0.073242 | -0.004578 | -0.027465 | 3.3417 | 0.004578 | 0.009156 | 0.054932 | 0.045776 | -0.12817 | -0.15106 | -0.17853 | -0.27466 | -0.14648 | -0.059509 | 122.1313 | 122.2137 | 55.3665 | -122.1634 | 122.0078 | 122.0993 | 58.2733 | -122.287
1234.7656 | 122.3648 | -56.1081 | 66.1606 | 0.013046 | -0.034534 | 0.11594 | 0.025656 | 0.056287 | -0.022244 | -0.021642 | 0.0073242 | 0.00076695 | 0.041962 | 0.060494 | -0.013381 | -0.016171 | 66.1423 | -52.6703 | -0.85602 | -56.0944 | 66.1606 | -56.1218 | -56.0532 | -56.25 | 2.0782 | -56.4331 | 66.0278 | 66.1194 | -55.9937 | -56.1905 | -0.013733 | 0.054931 | 0 | 3.4378 | 0.013733 | -0.041198 | -0.01831 | 0.11444 | -0.082398 | -0.13275 | -0.14191 | -0.32501 | -0.24261 | -0.041198 | 122.2687 | 122.2504 | 55.2521 | -122.2137 | 122.1359 | 122.2275 | 58.1863 | -122.3511
1236.5625 | 122.4289 | -56.044 | 66.1606 | -0.0022127 | -0.036243 | 0.11851 | 0.027792 | 0.054578 | -0.027585 | -0.026769 | 0.014954 | -0.0013693 | 0.040894 | 0.06028 | -0.018936 | -0.011258 | 66.2476 | -52.5055 | -0.64545 | -55.9982 | 66.124 | -56.0577 | -55.9937 | -56.1584 | 2.2018 | -56.282 | 66.0416 | 66.1057 | -55.9113 | -56.1264 | -0.013733 | 0.050354 | -0.036621 | 3.5385 | 0.045776 | -0.004578 | 0.086976 | 0.13275 | -0.082398 | -0.11902 | -0.11444 | -0.23804 | -0.15564 | -0.054931 | 122.168 | 122.2916 | 55.3986 | -122.1542 | 122.0856 | 122.1497 | 58.2458 | -122.287
1238.2969 | 122.493 | -55.9845 | 66.1972 | 0.013046 | -0.036243 | 0.11616 | 0.025229 | 0.057783 | -0.020535 | -0.02506 | 0.014954 | -0.0028647 | 0.042176 | 0.060707 | -0.014449 | -0.014462 | 66.2201 | -52.5879 | -0.70038 | -56.0074 | 66.2018 | -56.044 | -55.9937 | -56.1172 | 2.0966 | -56.3004 | 66.0873 | 66.1331 | -55.9113 | -56.0898 | -0.059509 | -0.009155 | 0.004577 | 3.3966 | -0.022888 | -0.013733 | 0.022888 | 0.073242 | -0.10529 | -0.10986 | -0.13275 | -0.31586 | -0.21057 | -0.064087 | 122.1863 | 122.2046 | 55.2841 | -122.1909 | 122.0718 | 122.1176 | 58.0811 | -122.287
1240.0781 | 122.493 | -55.9387 | 66.2384 | 0.0054168 | -0.038593 | 0.11637 | 0.029074 | 0.053724 | -0.02908 | -0.023351 | 0.0073242 | -0.0043601 | 0.041535 | 0.059853 | -0.020004 | -0.013821 | 66.3483 | -52.4826 | -0.54474 | -55.8701 | 66.2018 | -55.9799 | -55.8884 | -56.012 | 2.1286 | -56.1676 | 66.1011 | 66.1835 | -55.838 | -56.0486 | -0.041198 | 0.050354 | -0.036621 | 3.4561 | 0.068665 | 0.018311 | 0.10986 | 0.10071 | -0.10986 | -0.13733 | -0.073242 | -0.22888 | -0.11902 | -0.054931 | 122.1405 | 122.287 | 55.394 | -122.1268 | 122.0398 | 122.1222 | 58.0673 | -122.287
1241.7812 | 122.5113 | -55.9296 | 66.2704 | 0.013046 | -0.034321 | 0.11701 | 0.030569 | 0.052229 | -0.029294 | -0.024633 | 0.014954 | -0.0032919 | 0.041107 | 0.062203 | -0.020004 | -0.013394 | 66.362 | -52.5421 | -0.5722 | -55.8563 | 66.2521 | -55.9387 | -55.9204 | -56.0028 | 2.0782 | -56.131 | 66.1285 | 66.2109 | -55.8243 | -56.012 | -0.009156 | 0.009155 | -0.018311 | 3.3875 | 0.073242 | 0.064087 | 0.091553 | 0.10528 | -0.082398 | -0.14191 | -0.073243 | -0.20142 | -0.11902 | -0.05951 | 122.1817 | 122.2916 | 55.3574 | -122.1909 | 122.0581 | 122.1405 | 58.0078 | -122.2824
1243.5781 | 122.3648 | -55.8563 | 66.394 | 0.020676 | -0.032825 | 0.11509 | 0.02822 | 0.055647 | -0.02374 | -0.024633 | -0.0003053 | -0.00030125 | 0.04068 | 0.060067 | -0.016372 | -0.015958 | 66.3849 | -52.5146 | -0.6958 | -55.8334 | 66.3803 | -55.9067 | -55.8472 | -55.9982 | 1.9318 | -56.1951 | 66.3025 | 66.3528 | -55.7785 | -55.9708 | -0.050354 | 0.009155 | -0.013733 | 3.3417 | 0.022888 | 0.013733 | -0.009155 | 0.07782 | -0.11444 | -0.091553 | -0.14191 | -0.33874 | -0.2243 | -0.041199 | 122.2366 | 122.2412 | 55.1605 | -122.2412 | 122.1588 | 122.2092 | 57.7881 | -122.3648
1245.2969 | 122.4426 | -55.8701 | 66.3345 | -0.0022127 | -0.037311 | 0.11573 | 0.027579 | 0.055006 | -0.028226 | -0.023992 | -0.0003053 | -0.0037191 | 0.043457 | 0.061562 | -0.019149 | -0.01318 | 66.4032 | -52.5055 | -0.65918 | -55.8197 | 66.3071 | -55.9113 | -55.8197 | -55.8884 | 1.9089 | -56.1539 | 66.188 | 66.3025 | -55.7877 | -55.9525 | -0.041199 | 0.050354 | -0.027466 | 3.3646 | 0.050354 | 0 | 0.068664 | 0.082397 | -0.082398 | -0.14648 | -0.018311 | -0.28381 | -0.20142 | -0.032044 | 122.1771 | 122.2733 | 55.2109 | -122.1542 | 122.0581 | 122.1725 | 57.7789 | -122.287
1247.0781 | 122.3419 | -56.044 | 66.2384 | 0.0054168 | -0.035389 | 0.11551 | 0.022879 | 0.052442 | -0.018613 | -0.021001 | 0.0073242 | 0.0014077 | 0.042816 | 0.063271 | -0.01274 | -0.014462 | 66.2521 | -52.8809 | -0.737 | -55.9616 | 66.2247 | -56.0532 | -55.9937 | -56.044 | 1.8631 | -56.3919 | 66.1148 | 66.1926 | -55.9296 | -56.1035 | -0.009156 | 0.050354 | -0.013733 | 3.1631 | 0.082397 | 0.032043 | 0.013733 | 0.11444 | -0.05951 | -0.1236 | 0 | -0.3479 | -0.28839 | -0.045776 | 122.2687 | 122.2961 | 55.307 | -122.2321 | 122.1588 | 122.2366 | 57.9071 | -122.3419
1248.7812 | 122.319 | -55.8517 | 66.3803 | 0.0054168 | -0.033039 | 0.11445 | 0.025656 | 0.055006 | -0.018186 | -0.021215 | -0.0079343 | 0.0014077 | 0.043244 | 0.061776 | -0.013381 | -0.014676 | 66.4444 | -52.5238 | -0.83313 | -55.7693 | 66.4124 | -55.8655 | -55.8243 | -55.8517 | 1.6754 | -56.1859 | 66.275 | 66.3574 | -55.7556 | -55.9433 | -0.013733 | 0.027466 | 0.032044 | 3.3279 | 0.082398 | 0.054932 | 0.064087 | 0.096131 | -0.091552 | -0.10529 | 0 | -0.33417 | -0.24262 | -0.022888 | 122.2641 | 122.2961 | 55.0186 | -122.2046 | 122.1268 | 122.2092 | 57.5272 | -122.3236
1250.5781 | 122.4701 | -52.977 | 69.191 | 0.0054168 | -0.036457 | 0.1168 | 0.029715 | 0.055006 | -0.025876 | -0.021642 | 0.014954 | -0.0052145 | 0.040039 | 0.060067 | -0.020217 | -0.011899 | 69.2963 | -49.6994 | 0 | -52.6566 | 69.1727 | -53.0045 | -52.9587 | -52.9404 | 2.2018 | -53.1967 | 69.0537 | 69.1315 | -52.858 | -53.0777 | -0.027466 | 0.018311 | -0.018311 | 3.2776 | 0.32044 | 0.30212 | 0.10529 | 0.11902 | -0.10071 | -0.13733 | 0.036621 | -0.21973 | -0.11902 | -0.059509 | 122.1497 | 122.2733 | 52.977 | -122.1497 | 122.0306 | 122.1085 | 55.1788 | -122.2687
1252.2812 | 122.3328 | -51.9928 | 70.2942 | -0.0022127 | -0.032825 | 0.11744 | 0.026297 | 0.057142 | -0.015836 | -0.024419 | -0.0003053 | 0.00033975 | 0.040467 | 0.061135 | -0.013168 | -0.011685 | 70.3354 | -48.9075 | 0.23346 | -51.5167 | 70.2759 | -51.9653 | -51.9012 | -51.9653 | 2.2247 | -52.3087 | 70.1797 | 70.2393 | -51.8738 | -52.0615 | 0.027466 | 0.091553 | -0.01831 | 3.0853 | 0.47607 | 0.38452 | 0.041199 | 0.11902 | -0.068664 | -0.11444 | 0.027466 | -0.31586 | -0.24719 | -0.054931 | 122.2687 | 122.3282 | 52.2263 | -122.1954 | 122.1725 | 122.2321 | 54.2175 | -122.3557
1254.0625 | 122.3602 | -51.2558 | 71.022 | 0.013046 | -0.034321 | 0.11915 | 0.03121 | 0.054151 | -0.022244 | -0.023138 | 0.0073242 | -0.00094205 | 0.04303 | 0.062844 | -0.018508 | -0.012112 | 71.0037 | -48.1476 | 0.51727 | -50.7751 | 70.9991 | -51.2512 | -51.1963 | -51.2833 | 2.5314 | -51.5762 | 70.8939 | 70.99 | -51.1597 | -51.297 | 0.004577 | 0.059509 | -0.022888 | 3.1082 | 0.48065 | 0.42114 | -0.018311 | 0.09613 | -0.041199 | -0.12817 | -0.027466 | -0.32044 | -0.27924 | -0.032044 | 122.2549 | 122.2595 | 51.7731 | -122.2183 | 122.1497 | 122.2458 | 53.7872 | -122.319
1255.8281 | 122.3328 | -49.8734 | 72.4182 | -0.0022127 | -0.032612 | 0.11808 | 0.030569 | 0.056715 | -0.023953 | -0.02271 | 0.0073242 | -0.0039329 | 0.043885 | 0.063271 | -0.016799 | -0.015744 | 72.4411 | -46.7651 | -0.75989 | -49.2691 | 72.345 | -49.8459 | -49.8093 | -49.8093 | 2.4811 | -50.1389 | 72.2763 | 72.3587 | -49.7406 | -49.9146 | 0.027466 | 0.064087 | -0.073242 | 3.1082 | 0.60425 | 0.54016 | 0.022888 | 0.13275 | -0.041199 | -0.14191 | 0.064087 | -0.2655 | -0.2243 | -0.059509 | 122.2183 | 122.3145 | 49.1135 | -122.2275 | 122.1497 | 122.2321 | 52.3544 | -122.3328
1257.5469 | 122.4838 | -49.4705 | 72.7112 | -0.0022127 | -0.037525 | 0.11744 | 0.026938 | 0.055006 | -0.023953 | -0.02271 | 0.0073242 | -0.0035055 | 0.041962 | 0.06028 | -0.020431 | -0.013394 | 72.7432 | -46.376 | -0.82398 | -48.9212 | 72.6791 | -49.53 | -49.4843 | -49.4659 | 2.5314 | -49.7589 | 72.5555 | 72.67 | -49.3927 | -49.5804 | -0.059509 | -0.013733 | -0.032044 | 3.0945 | 0.54932 | 0.56305 | 0.032043 | 0.07782 | -0.10986 | -0.15564 | 0.004578 | -0.28839 | -0.17853 | -0.041199 | 122.1497 | 122.2137 | 48.6465 | -122.1954 | 122.0261 | 122.1405 | 52.002 | -122.2916
1259.3125 | 122.438 | -48.4085 | 73.7869 | 0.013046 | -0.038807 | 0.11851 | 0.026938 | 0.055219 | -0.022672 | -0.023778 | 0.014954 | -0.0026511 | 0.043671 | 0.060707 | -0.019149 | -0.011899 | 73.819 | -45.0165 | -0.40741 | -47.8317 | 73.7549 | -48.468 | -48.4039 | -48.3902 | 2.6733 | -48.7335 | 73.6221 | 73.7274 | -48.349 | -48.5367 | -0.05951 | 0.004577 | -0.032043 | 3.392 | 0.57678 | 0.5722 | 0.032044 | 0.059509 | -0.12817 | -0.16479 | 0.01831 | -0.32501 | -0.19684 | -0.059509 | 122.1634 | 122.2275 | 48.0011 | -122.1909 | 122.0306 | 122.1359 | 51.0818 | -122.3236
1261.0938 | 122.3373 | -47.6028 | 74.6704 | 0.0054168 | -0.035602 | 0.11487 | 0.024588 | 0.054578 | -0.015195 | -0.02036 | 0.0073242 | 0.0018351 | 0.043885 | 0.061562 | -0.013809 | -0.016598 | 74.7482 | -44.1971 | -0.082397 | -46.8475 | 74.6613 | -47.58 | -47.5296 | -47.4426 | 2.8839 | -47.9095 | 74.5422 | 74.6384 | -47.4838 | -47.6669 | 0.022888 | 0.073242 | -0.009155 | 3.4058 | 0.75531 | 0.68207 | 0.07782 | 0.11902 | -0.064087 | -0.12817 | 0.16022 | -0.3067 | -0.24262 | -0.032043 | 122.2641 | 122.3511 | 47.5204 | -122.2 | 122.1451 | 122.2412 | 50.4868 | -122.3373
1262.8125 | 122.3419 | -46.5729 | 75.6775 | 0.013046 | -0.032184 | 0.1168 | 0.024802 | 0.055647 | -0.015622 | -0.022924 | 0.0073242 | -0.00051485 | 0.040894 | 0.060707 | -0.013168 | -0.012112 | 75.6546 | -42.8421 | 0.31586 | -45.8542 | 75.7141 | -46.5912 | -46.5271 | -46.4447 | 3.0533 | -46.9711 | 75.5951 | 75.6546 | -46.4951 | -46.669 | -0.018311 | 0.045776 | 0.036621 | 3.7308 | 0.71869 | 0.67291 | -0.022888 | 0.07782 | -0.09613 | -0.082397 | 0.12817 | -0.39825 | -0.30212 | -0.022888 | 122.287 | 122.2275 | 46.8887 | -122.2046 | 122.168 | 122.2275 | 49.6262 | -122.3465
1264.6094 | 122.374 | -46.4264 | 75.8194 | 0.0054168 | -0.035816 | 0.11979 | 0.029929 | 0.056928 | -0.020535 | -0.022283 | 0.014954 | -0.0032919 | 0.043671 | 0.060707 | -0.015731 | -0.011685 | 75.7874 | -42.5812 | 0.54932 | -45.7306 | 75.7919 | -46.4401 | -46.4264 | -46.2936 | 3.186 | -46.8109 | 75.7278 | 75.7553 | -46.3669 | -46.5454 | -0.013733 | 0 | -0.027466 | 3.8452 | 0.6958 | 0.6958 | -0.032043 | 0.05951 | -0.11902 | -0.091553 | 0.13275 | -0.38452 | -0.2655 | -0.064087 | 122.2183 | 122.2137 | 46.9757 | -122.2458 | 122.1542 | 122.1817 | 49.6124 | -122.3648
1266.3438 | 122.4472 | -45.9961 | 76.1581 | 0.013046 | -0.035389 | 0.11851 | 0.026083 | 0.055006 | -0.019895 | -0.023992 | -0.0003053 | -0.0022239 | 0.041535 | 0.064339 | -0.014877 | -0.011471 | 76.1856 | -42.0959 | 0.70038 | -45.2957 | 76.1902 | -46.051 | -46.0007 | -45.8038 | 3.2501 | -46.3669 | 76.0391 | 76.1398 | -45.9412 | -46.1243 | -0.054931 | -0.004577 | 0.032044 | 3.9001 | 0.70038 | 0.70496 | 0.027466 | 0.054932 | -0.12817 | -0.11902 | 0.19226 | -0.37079 | -0.24261 | -0.01831 | 122.1863 | 122.1817 | 46.6965 | -122.1588 | 122.0352 | 122.1359 | 49.2462 | -122.2824
1268.1094 | 122.4518 | -45.3964 | 76.7899 | 0.013046 | -0.034321 | 0.11701 | 0.026724 | 0.057783 | -0.019254 | -0.02271 | 0.0073242 | -0.00030125 | 0.041107 | 0.061135 | -0.015945 | -0.011899 | 76.7899 | -41.1621 | 0.75073 | -44.6411 | 76.8356 | -45.433 | -45.3781 | -45.1813 | 3.3646 | -45.7581 | 76.6846 | 76.767 | -45.3278 | -45.4971 | -0.036621 | 0.01831 | 0.045776 | 4.2343 | 0.75531 | 0.737 | 0 | 0.068664 | -0.10071 | -0.10529 | 0.21515 | -0.36163 | -0.26093 | -0.022888 | 122.2321 | 122.1863 | 46.1472 | -122.168 | 122.081 | 122.1634 | 48.761 | -122.287
1269.7969 | 122.4655 | -45.1355 | 77.0691 | 0.0054168 | -0.034534 | 0.11872 | 0.030569 | 0.055433 | -0.024594 | -0.022283 | 0.014954 | -0.0060691 | 0.041321 | 0.059426 | -0.020858 | -0.014462 | 77.092 | -40.6265 | -0.013733 | -44.0598 | 76.9501 | -45.1767 | -45.1172 | -44.8059 | 3.3783 | -45.4056 | 76.8631 | 76.9867 | -45.0439 | -45.2316 | -0.041199 | 0.018311 | -0.11902 | 4.509 | 1.0757 | 1.0574 | 0.022888 | 0.091553 | -0.09613 | -0.20599 | 0.32959 | -0.27008 | -0.17395 | -0.082398 | 122.0856 | 122.2275 | 45.1218 | -122.1863 | 121.9986 | 122.1222 | 48.5138 | -122.3007
1271.5781 | 122.4655 | -44.014 | 78.1631 | 0.013046 | -0.039234 | 0.12 | 0.027792 | 0.056928 | -0.024381 | -0.024206 | 0.0073242 | -0.0045737 | 0.043885 | 0.058999 | -0.019149 | -0.014035 | 78.2227 | -38.681 | 0.24261 | -43.2678 | 78.1586 | -44.0369 | -44.0002 | -43.6844 | 3.5797 | -44.2703 | 78.035 | 78.1448 | -43.9178 | -44.0918 | -0.022888 | 0.013733 | -0.004578 | 5.3329 | 0.74615 | 0.73242 | 0.059509 | 0.09613 | -0.07782 | -0.12817 | 0.32959 | -0.25635 | -0.17853 | -0.018311 | 122.1725 | 122.2366 | 44.2566 | -122.1634 | 122.0489 | 122.1588 | 47.5937 | -122.2549
1273.3594 | 122.3419 | -43.428 | 78.8498 | 0.0054168 | -0.034534 | 0.12107 | 0.02587 | 0.057569 | -0.020108 | -0.024847 | 0.0073242 | -0.0020103 | 0.042816 | 0.059639 | -0.018508 | -0.017026 | 78.9368 | -38.1683 | 0.60883 | -42.54 | 78.8315 | -43.3273 | -43.3365 | -42.7689 | 3.8223 | -43.6935 | 78.6804 | 78.772 | -43.309 | -43.4738 | 0.10071 | 0.091553 | -0.01831 | 5.2597 | 0.88806 | 0.79651 | 0.086976 | 0.11902 | -0.045776 | -0.16937 | 0.65918 | -0.2655 | -0.21973 | -0.077819 | 122.2595 | 122.3648 | 44.0369 | -122.1863 | 122.1085 | 122.2 | 47.2504 | -122.3236
1275.0625 | 122.4609 | -42.9474 | 79.2709 | 0.0054168 | -0.035602 | 0.12171 | 0.026083 | 0.056715 | -0.022244 | -0.024419 | 0.0073242 | -0.0032919 | 0.04068 | 0.060067 | -0.017013 | -0.014035 | 79.1885 | -38.0402 | 0.58594 | -42.2058 | 79.0878 | -43.0298 | -43.0069 | -42.247 | 4.0054 | -43.2083 | 79.0787 | 79.1565 | -42.8696 | -43.0481 | -0.082397 | -0.059509 | -0.1831 | 4.9072 | 0.74158 | 0.80109 | -0.082397 | 0.07782 | -0.10071 | -0.19226 | 0.70038 | -0.26093 | -0.16022 | -0.11444 | 122.0352 | 122.1359 | 43.5333 | -122.2778 | 122.0261 | 122.1039 | 46.9528 | -122.319
1276.8281 | 122.4609 | -43.396 | 78.7903 | -0.0022127 | -0.036243 | 0.11915 | 0.024588 | 0.056928 | -0.020963 | -0.025274 | -0.0003053 | -0.0043601 | 0.039612 | 0.058785 | -0.018936 | -0.01254 | 78.7994 | -38.3835 | 2.6184 | -42.5766 | 78.7582 | -43.4464 | -43.4143 | -42.9794 | 4.3442 | -43.7256 | 78.6301 | 78.7399 | -43.3502 | -43.5104 | -0.050354 | -0.018311 | -0.032043 | 5.0125 | 0.8194 | 0.83771 | 0.009155 | 0.045776 | -0.11444 | -0.16022 | 0.41656 | -0.32959 | -0.21515 | -0.050354 | 122.1542 | 122.1954 | 46.0144 | -122.2046 | 122.0261 | 122.1359 | 47.7402 | -122.3007
1278.625 | 122.4014 | -42.8375 | 79.3304 | -0.0022127 | -0.03603 | 0.11872 | 0.023093 | 0.056501 | -0.016904 | -0.022497 | 0.0073242 | -0.0032919 | 0.039612 | 0.059426 | -0.017867 | -0.01553 | 79.4495 | -37.0056 | 2.6459 | -41.9907 | 79.303 | -42.8696 | -42.8192 | -42.3019 | 4.3716 | -43.1259 | 79.1885 | 79.2984 | -42.7734 | -42.9291 | -0.032044 | 0.01831 | -0.027465 | 5.8319 | 0.84686 | 0.82855 | 0.11902 | 0.064087 | -0.091553 | -0.14191 | 0.53558 | -0.28839 | -0.19684 | -0.032043 | 122.1405 | 122.287 | 45.4834 | -122.1497 | 122.0261 | 122.1359 | 47.2092 | -122.2595
1280.4062 | 122.4014 | -43.9362 | 78.2913 | 0.013046 | -0.031757 | 0.11765 | 0.02352 | 0.060346 | -0.015195 | -0.023351 | -0.0003053 | 0.0024759 | 0.041962 | 0.060494 | -0.01509 | -0.01553 | 78.3279 | -37.7792 | 5.4337 | -42.9382 | 78.3005 | -43.959 | -43.9316 | -43.4097 | 4.8386 | -44.2886 | 78.1723 | 78.2501 | -43.84 | -44.0048 | -0.022888 | 0.004577 | 0.009155 | 6.1569 | 0.99793 | 0.99335 | 0.036621 | 0.09613 | -0.068665 | -0.11902 | 0.52643 | -0.35248 | -0.28381 | -0.041199 | 122.2366 | 122.2641 | 49.3698 | -122.2229 | 122.1085 | 122.1863 | 48.7747 | -122.2961
1282.125 | 122.3785 | -43.2129 | 78.9871 | 0.0054168 | -0.031544 | 0.12043 | 0.026297 | 0.057996 | -0.013059 | -0.021001 | 0.014954 | -8.7654e-05 | 0.043457 | 0.060921 | -0.017227 | -0.012967 | 79.0787 | -36.6623 | 5.5206 | -42.2562 | 79.0649 | -43.2083 | -43.1671 | -42.485 | 5.191 | -43.4509 | 78.9825 | 79.0375 | -43.0573 | -43.2312 | 0.004578 | 0.045777 | 0.077819 | 6.5506 | 0.95673 | 0.91095 | 0.091552 | 0.15564 | -0.01831 | -0.004578 | 0.72785 | -0.23804 | -0.21973 | 0.050354 | 122.2778 | 122.2916 | 48.7335 | -122.1542 | 122.1954 | 122.2504 | 48.4039 | -122.2183
1283.8906 | 122.4564 | -42.8009 | 79.3625 | -0.0022127 | -0.035175 | 0.12107 | 0.026511 | 0.053297 | -0.017972 | -0.022069 | 0.0073242 | -0.0013693 | 0.041321 | 0.061348 | -0.01509 | -0.0095489 | 79.3991 | -35.1883 | 5.9647 | -41.9128 | 79.4037 | -42.8284 | -42.8192 | -42.2379 | 5.127 | -43.2037 | 79.2664 | 79.3121 | -42.7643 | -42.9291 | -0.027466 | -0.018311 | 0.041199 | 7.6126 | 0.88806 | 0.90637 | 0.036621 | 0.036621 | -0.12817 | -0.096131 | 0.56305 | -0.40283 | -0.27466 | -0.050354 | 122.2046 | 122.2 | 48.7656 | -122.1817 | 122.0673 | 122.113 | 47.9279 | -122.2916
1285.6719 | 122.3236 | -42.5583 | 79.6555 | 0.0054168 | -0.032825 | 0.11893 | 0.025229 | 0.055433 | -0.014127 | -0.021642 | 0.0073242 | -0.00030125 | 0.042816 | 0.061989 | -0.016372 | -0.014249 | 79.7379 | -34.2957 | 6.8939 | -41.4871 | 79.6829 | -42.54 | -42.5171 | -41.9678 | 5.5847 | -42.8879 | 79.5639 | 79.6417 | -42.4484 | -42.6361 | 0.018311 | 0.041199 | 0.027465 | 8.2626 | 1.0712 | 1.03 | 0.082397 | 0.10986 | -0.077819 | -0.091553 | 0.59052 | -0.32959 | -0.25177 | -0.013733 | 122.2412 | 122.2961 | 49.4522 | -122.1725 | 122.1222 | 122.2 | 48.143 | -122.2916
1287.4062 | 122.3236 | -42.2928 | 79.9622 | 0.013046 | -0.033893 | 0.11829 | 0.02822 | 0.054365 | -0.014554 | -0.023565 | -0.0003053 | -0.0020103 | 0.042603 | 0.06028 | -0.015518 | -0.013394 | 79.9118 | -36.9186 | 4.7791 | -41.1942 | 79.9255 | -42.2791 | -42.2791 | -41.7755 | 5.2139 | -42.6773 | 79.8111 | 79.9026 | -42.2424 | -42.3935 | 0.013733 | 0.013733 | -0.036621 | 5.3741 | 1.0986 | 1.0849 | -0.050354 | 0.050354 | -0.10071 | -0.15106 | 0.51727 | -0.38452 | -0.28381 | -0.059509 | 122.2183 | 122.2046 | 47.0718 | -122.2412 | 122.1039 | 122.1954 | 47.5067 | -122.3557
1289.1875 | 122.3007 | -41.8442 | 80.4199 | 0.013046 | -0.034107 | 0.1168 | 0.02587 | 0.057996 | -0.017331 | -0.022283 | -0.0003053 | 0.0020487 | 0.043457 | 0.060067 | -0.017654 | -0.012753 | 80.3421 | -36.2961 | 4.6829 | -40.7547 | 80.3375 | -41.8854 | -41.8716 | -41.2491 | 5.2231 | -42.1967 | 80.278 | 80.3741 | -41.7297 | -41.8945 | -0.041199 | -0.027466 | -0.082398 | 5.5481 | 1.0895 | 1.1169 | -0.07782 | 0.11444 | -0.050354 | -0.14191 | 0.59509 | -0.35248 | -0.30212 | -0.045776 | 122.1817 | 122.1863 | 46.5271 | -122.2916 | 122.1222 | 122.2183 | 47.0673 | -122.3145
1290.9688 | 122.319 | -41.153 | 81.134 | 0.0054168 | -0.029621 | 0.11744 | 0.030356 | 0.058851 | -0.015409 | -0.021001 | 0.0073242 | -0.00030125 | 0.044312 | 0.061989 | -0.015731 | -0.01318 | 81.0699 | -35.3622 | 4.2526 | -40.1138 | 81.0883 | -41.1301 | -41.1072 | -40.4617 | 5.0903 | -41.5146 | 80.9738 | 81.0928 | -41.0294 | -41.2308 | 0.022888 | 0.045776 | -0.045776 | 5.7907 | 1.0391 | 0.99335 | -0.064087 | 0.1236 | -0.07782 | -0.16022 | 0.69122 | -0.36163 | -0.28381 | -0.041199 | 122.2412 | 122.2229 | 45.4056 | -122.2412 | 122.1268 | 122.2458 | 46.2433 | -122.3648
1292.6875 | 122.3785 | -41.2857 | 80.9601 | 0.0054168 | -0.034107 | 0.1215 | 0.026938 | 0.058851 | -0.018826 | -0.020788 | 0.0073242 | -0.0011557 | 0.042603 | 0.061562 | -0.017867 | -0.013394 | 80.9006 | -35.1059 | 3.511 | -39.9399 | 80.9509 | -41.2949 | -41.2445 | -40.567 | 4.834 | -41.629 | 80.8411 | 80.928 | -41.185 | -41.3361 | -0.009155 | 0.041199 | -0.009155 | 6.1798 | 1.3458 | 1.3046 | -0.059509 | 0.10071 | -0.050354 | -0.11902 | 0.71869 | -0.34332 | -0.29297 | -0.032043 | 122.2366 | 122.1863 | 44.7968 | -122.2046 | 122.1268 | 122.2137 | 46.1197 | -122.2961
1294.4688 | 122.4014 | -35.463 | 86.7783 | 0.0054168 | -0.033466 | 0.12256 | 0.03121 | 0.066969 | -0.026517 | -0.021642 | 0.0073242 | -0.0058555 | 0.043244 | 0.062203 | -0.021285 | -0.01318 | 86.8378 | -15.4953 | 11.1191 | -34.7946 | 86.7233 | -35.408 | -35.4172 | -34.6161 | 8.4824 | -35.701 | 86.5997 | 86.7462 | -35.3256 | -35.5042 | 0.054932 | 0.045777 | -0.054931 | 19.9677 | 0.66833 | 0.62256 | 0.05951 | 0.13733 | -0.041198 | -0.17853 | 0.84686 | -0.23804 | -0.19684 | -0.032043 | 122.1863 | 122.3007 | 46.582 | -122.1954 | 122.0627 | 122.2092 | 43.9453 | -122.2824
1296.2031 | 122.374 | -35.3531 | 86.8835 | -0.0098417 | -0.03368 | 0.12449 | 0.02886 | 0.06825 | -0.024594 | -0.023992 | 0.014954 | -0.0050009 | 0.044739 | 0.056221 | -0.019363 | -0.01318 | 86.8927 | -15.3122 | 11.8698 | -34.6802 | 86.824 | -35.3119 | -35.3439 | -34.5749 | 8.7158 | -35.6323 | 86.7004 | 86.8057 | -35.2524 | -35.3897 | 0.041198 | 0.009155 | -0.059509 | 20.0409 | 0.67291 | 0.66376 | 0.009155 | 0.10071 | -0.036621 | -0.18311 | 0.7782 | -0.27924 | -0.24261 | -0.07782 | 122.1771 | 122.2458 | 47.2229 | -122.2275 | 122.0535 | 122.1588 | 44.0689 | -122.2733
1297.9688 | 122.4426 | -35.0739 | 87.1033 | 0.0054168 | -0.041797 | 0.12449 | 0.028433 | 0.066328 | -0.024381 | -0.024847 | 0.0073242 | -0.0047873 | 0.040467 | 0.060921 | -0.017013 | -0.011685 | 87.1674 | -14.4058 | 12.1124 | -34.4696 | 87.0529 | -35.0784 | -35.0784 | -34.2545 | 8.7387 | -35.3531 | 86.9247 | 87.0255 | -35.0281 | -35.1471 | -0.004577 | -0.004577 | -0.050354 | 20.668 | 0.60425 | 0.60883 | 0.064087 | 0.045777 | -0.073242 | -0.17853 | 0.8194 | -0.27923 | -0.20599 | -0.077819 | 122.1268 | 122.2412 | 47.1863 | -122.1817 | 121.9986 | 122.0993 | 43.8126 | -122.2504
1299.6719 | 122.4152 | -34.8267 | 87.3734 | -0.0098417 | -0.033893 | 0.12192 | 0.029288 | 0.068464 | -0.022244 | -0.024419 | -0.0003053 | -0.0056419 | 0.043244 | 0.061562 | -0.018295 | -0.014676 | 87.4146 | -13.5635 | 12.8815 | -34.1812 | 87.3047 | -34.8312 | -34.8129 | -33.9203 | 9.2102 | -35.1013 | 87.2269 | 87.2864 | -34.7717 | -34.9045 | -0.004578 | 0.013733 | -0.068665 | 21.2631 | 0.64545 | 0.63171 | 0.041199 | 0.054931 | -0.07782 | -0.14648 | 0.90637 | -0.27466 | -0.19684 | -0.086975 | 122.1313 | 122.2412 | 47.7081 | -122.1863 | 122.0535 | 122.113 | 44.0369 | -122.2778
1301.4688 | 122.3328 | -34.584 | 87.6663 | 0.0054168 | -0.029835 | 0.12256 | 0.027365 | 0.069318 | -0.018826 | -0.023138 | 0.014954 | -0.00051485 | 0.04303 | 0.060707 | -0.016799 | -0.013821 | 87.5977 | -13.4308 | 13.0463 | -33.9798 | 87.6526 | -34.5978 | -34.5566 | -33.728 | 9.0683 | -34.9731 | 87.5519 | 87.6434 | -34.52 | -34.6619 | -0.013733 | 0.027465 | -0.013733 | 21.1533 | 0.60425 | 0.57678 | -0.068665 | 0.064087 | -0.07782 | -0.11444 | 0.85602 | -0.3891 | -0.31128 | -0.022888 | 122.2366 | 122.1817 | 47.6303 | -122.2229 | 122.1359 | 122.2275 | 43.6523 | -122.3282
1303.1875 | 122.3282 | -33.522 | 88.7741 | 0.013046 | -0.030903 | 0.1215 | 0.029074 | 0.067396 | -0.018613 | -0.021856 | 0.0073242 | -0.0028647 | 0.044739 | 0.061562 | -0.018508 | -0.01318 | 88.7512 | -13.6368 | 13.5773 | -32.5607 | 88.7375 | -33.4854 | -33.4671 | -32.6157 | 9.5489 | -33.8516 | 88.6047 | 88.7054 | -33.4122 | -33.5541 | 0.036621 | 0.054932 | -0.036621 | 19.8853 | 0.9613 | 0.90637 | -0.022888 | 0.10986 | -0.032043 | -0.16937 | 0.90637 | -0.32959 | -0.29755 | -0.068665 | 122.2595 | 122.2733 | 47.0993 | -122.2412 | 122.1268 | 122.2275 | 43.071 | -122.3282
1304.9531 | 122.4518 | -32.9453 | 89.2227 | -0.0022127 | -0.035389 | 0.12641 | 0.026511 | 0.065901 | -0.020108 | -0.02271 | 0.0073242 | -0.0050009 | 0.043457 | 0.060067 | -0.017867 | -0.01318 | 89.2822 | -13.8153 | 14.6576 | -32.0709 | 89.241 | -32.9453 | -32.9361 | -32.1716 | 9.8145 | -33.252 | 89.0625 | 89.1678 | -32.8812 | -33.0276 | 0 | 0.009155 | 0.018311 | 19.1299 | 0.87433 | 0.86517 | 0.05951 | 0.064086 | -0.082398 | -0.16022 | 0.77362 | -0.3067 | -0.2243 | -0.054931 | 122.1863 | 122.2275 | 47.6028 | -122.1588 | 122.0078 | 122.113 | 42.7597 | -122.2504
1306.7344 | 122.4106 | -33.3252 | 88.8657 | -0.0022127 | -0.033466 | 0.12491 | 0.023734 | 0.066541 | -0.015195 | -0.022283 | 0.014954 | -0.0030783 | 0.040039 | 0.06028 | -0.01509 | -0.014035 | 88.9343 | -13.8016 | 16.6626 | -32.0389 | 88.8382 | -33.3298 | -33.3023 | -32.6019 | 10.2768 | -33.6182 | 88.71 | 88.8107 | -33.2565 | -33.3664 | -0.004578 | 0.022888 | -0.027466 | 19.5236 | 1.2863 | 1.2634 | 0.068664 | 0.068664 | -0.041199 | -0.15564 | 0.72327 | -0.29297 | -0.25177 | -0.054932 | 122.1634 | 122.2595 | 49.9878 | -122.168 | 122.0352 | 122.1359 | 43.602 | -122.2321
1308.4531 | 122.374 | -32.8949 | 89.3417 | 0.013046 | -0.032825 | 0.1247 | 0.028433 | 0.065473 | -0.011777 | -0.02271 | -0.0003053 | 0.00055335 | 0.042603 | 0.061135 | -0.013595 | -0.017453 | 89.3692 | -13.8382 | 16.42 | -31.4484 | 89.3738 | -32.8812 | -32.8857 | -32.2495 | 10.1532 | -33.252 | 89.2456 | 89.3051 | -32.8125 | -32.9453 | 0.013732 | 0.009155 | 0.032043 | 19.0567 | 1.4465 | 1.4374 | 0.027466 | 0.082397 | -0.050354 | -0.096131 | 0.64545 | -0.35706 | -0.3067 | -0.036621 | 122.2687 | 122.2641 | 49.3149 | -122.2275 | 122.1405 | 122.2 | 43.0481 | -122.287
1310.2344 | 122.4197 | -32.9544 | 89.2456 | 0.020676 | -0.034534 | 0.12449 | 0.026724 | 0.065687 | -0.015195 | -0.01972 | 0.0073242 | -0.0015829 | 0.040253 | 0.058999 | -0.01744 | -0.012967 | 89.3692 | -13.3301 | 15.5594 | -31.2378 | 89.2502 | -32.8995 | -32.8766 | -32.2037 | 10.0479 | -33.2016 | 89.1541 | 89.2776 | -32.8079 | -32.9636 | 0.054932 | 0.07782 | 0.004578 | 19.6243 | 1.7166 | 1.6388 | 0.1236 | 0.14649 | -0.009155 | -0.091552 | 0.75073 | -0.24719 | -0.23804 | 0.032044 | 122.2046 | 122.3236 | 48.5138 | -122.1222 | 122.1085 | 122.2321 | 43.0023 | -122.2092
1312.0312 | 122.4564 | -34.1309 | 88.06 | 0.0054168 | -0.03368 | 0.12812 | 0.030569 | 0.067823 | -0.017972 | -0.022069 | -0.0003053 | -0.00051485 | 0.042176 | 0.06263 | -0.017654 | -0.014035 | 88.0188 | -12.941 | 17.2714 | -32.8766 | 87.9959 | -34.1949 | -34.1766 | -33.0643 | 10.849 | -34.5062 | 87.8677 | 88.0234 | -34.0668 | -34.227 | -0.064087 | -0.045777 | -0.064087 | 21.1899 | 1.2543 | 1.3 | -0.041199 | 0.064087 | -0.096131 | -0.19226 | 1.0666 | -0.37537 | -0.27924 | -0.036622 | 122.1268 | 122.1497 | 51.4023 | -122.2366 | 121.9986 | 122.1542 | 44.9799 | -122.287
1313.8125 | 122.3969 | -34.8267 | 87.3505 | 0.0054168 | -0.035602 | 0.12726 | 0.025656 | 0.071882 | -0.015409 | -0.020147 | 0.0073242 | -0.0047873 | 0.042176 | 0.060494 | -0.015304 | -0.011899 | 87.4146 | -12.1628 | 17.3538 | -33.4122 | 87.323 | -34.8358 | -34.8129 | -33.4671 | 10.5331 | -35.1471 | 87.2177 | 87.3093 | -34.7305 | -34.8862 | -0.009155 | 0.013733 | -0.027466 | 22.6639 | 1.4145 | 1.4008 | 0.064087 | 0.09613 | -0.059509 | -0.13275 | 1.3596 | -0.32044 | -0.26093 | -0.041199 | 122.1497 | 122.2412 | 52.1805 | -122.1634 | 122.0444 | 122.1359 | 45.3598 | -122.2366
1315.6094 | 122.2961 | -34.8083 | 87.4283 | 0.0054168 | -0.030689 | 0.1294 | 0.025656 | 0.069105 | -0.011563 | -0.021001 | 0.0073242 | 0.0016213 | 0.043457 | 0.061135 | -0.01274 | -0.012967 | 87.4191 | -11.9385 | 18.4845 | -33.6685 | 87.41 | -34.7992 | -34.8129 | -33.0276 | 10.8902 | -35.202 | 87.2955 | 87.4008 | -34.7443 | -34.8816 | 0.009156 | -0.004577 | -0.018311 | 22.8699 | 1.1398 | 1.1444 | -0.009156 | 0.064087 | -0.073242 | -0.13275 | 1.7807 | -0.39368 | -0.32043 | -0.027466 | 122.2183 | 122.2275 | 53.2928 | -122.2412 | 122.1039 | 122.2092 | 45.6985 | -122.3099
1317.3281 | 122.3648 | -34.0576 | 88.147 | 0.013046 | -0.032184 | 0.13175 | 0.028647 | 0.069105 | -0.019467 | -0.022069 | 0.0073242 | -0.0047873 | 0.043671 | 0.058999 | -0.017654 | -0.014035 | 88.2156 | -11.7554 | 21.9818 | -32.6248 | 88.1378 | -34.0073 | -33.9981 | -31.9885 | 11.4624 | -34.3185 | 88.0096 | 88.092 | -33.9386 | -34.0942 | 0.050354 | 0.059509 | -0.009156 | 22.3022 | 1.4328 | 1.3733 | 0.068664 | 0.11902 | -0.036621 | -0.13733 | 2.0691 | -0.26093 | -0.2243 | -0.054932 | 122.1954 | 122.2733 | 56.0394 | -122.1451 | 122.0673 | 122.1497 | 45.52 | -122.2412
1319.0938 | 122.4609 | -34.2453 | 87.9272 | 0.0054168 | -0.033039 | 0.12919 | 0.026938 | 0.069318 | -0.015195 | -0.01972 | 0.0073242 | -0.0017965 | 0.043244 | 0.061348 | -0.01509 | -0.014035 | 87.973 | -11.6684 | 21.7209 | -32.9453 | 87.9501 | -34.2499 | -34.2224 | -32.0435 | 11.5906 | -34.5657 | 87.7945 | 87.8952 | -34.1812 | -34.3002 | -0.004578 | 0.022888 | 0.022888 | 22.5769 | 1.3 | 1.2772 | 0.045776 | 0.064087 | -0.054932 | -0.13275 | 2.2018 | -0.32043 | -0.2655 | -0.032043 | 122.1954 | 122.2183 | 55.9662 | -122.1497 | 122.0398 | 122.1405 | 45.8359 | -122.2275
1320.8594 | 122.4243 | -33.9844 | 88.1927 | 0.013046 | -0.036457 | 0.13474 | 0.029074 | 0.069746 | -0.017545 | -0.020574 | -0.0003053 | -0.0030783 | 0.042176 | 0.061776 | -0.017227 | -0.014462 | 88.2111 | -11.6318 | 24.3622 | -32.0892 | 88.1927 | -33.9844 | -33.9706 | -31.6086 | 11.1877 | -34.3231 | 88.0646 | 88.1607 | -33.8791 | -34.0714 | 0 | 0.013733 | 0 | 22.3526 | 1.8951 | 1.8814 | 0.018311 | 0.10529 | -0.086975 | -0.12817 | 2.3758 | -0.33875 | -0.25177 | -0.032043 | 122.1771 | 122.1954 | 58.3466 | -122.1634 | 122.049 | 122.1451 | 45.1721 | -122.2641
1322.6406 | 122.3053 | -34.4879 | 87.7213 | -0.0098417 | -0.031544 | 0.13367 | 0.029715 | 0.07295 | -0.015195 | -0.019292 | 0.0073242 | -0.00051485 | 0.043457 | 0.062416 | -0.016158 | -0.016598 | 87.8082 | -12.0117 | 16.9327 | -32.8812 | 87.7716 | -34.4147 | -34.4192 | -31.7642 | 11.8652 | -34.7809 | 87.6709 | 87.7853 | -34.3506 | -34.5062 | 0.073242 | 0.068665 | 0.050354 | 22.4762 | 1.6067 | 1.5381 | 0.086976 | 0.13733 | -0.018311 | -0.050354 | 2.7237 | -0.29297 | -0.27466 | 0.064087 | 122.2595 | 122.2961 | 51.4206 | -122.1405 | 122.1588 | 122.2733 | 46.3531 | -122.2275
1324.3594 | 122.4243 | -34.0988 | 88.0234 | 0.0054168 | -0.033039 | 0.1341 | 0.030569 | 0.070814 | -0.018186 | -0.020147 | 0.0073242 | -0.0022239 | 0.041321 | 0.061989 | -0.018081 | -0.013608 | 88.1241 | -11.8378 | 19.2581 | -32.3685 | 88.0234 | -34.1309 | -34.0988 | -30.899 | 12.3734 | -34.3826 | 87.8998 | 87.9593 | -34.0393 | -34.2087 | -0.032043 | 0 | 0 | 22.261 | 1.7303 | 1.7303 | 0.10071 | 0.059509 | -0.10986 | -0.1236 | 3.1998 | -0.28381 | -0.17395 | -0.064086 | 122.1222 | 122.2229 | 53.3569 | -122.1222 | 121.9986 | 122.0581 | 46.4722 | -122.2321
1326.125 | 122.3282 | -34.4604 | 87.7991 | 0.013046 | -0.029835 | 0.13474 | 0.02886 | 0.072736 | -0.01135 | -0.020788 | -0.0003053 | 0.00012615 | 0.041748 | 0.063271 | -0.015518 | -0.015744 | 87.7945 | -11.9019 | 20.1004 | -32.6111 | 87.7716 | -34.4238 | -34.4147 | -31.1371 | 12.2452 | -34.8175 | 87.6801 | 87.7304 | -34.346 | -34.5154 | 0.036621 | 0.045776 | -0.027466 | 22.5586 | 1.8494 | 1.8036 | -0.004577 | 0.11444 | -0.054932 | -0.11902 | 3.3234 | -0.35706 | -0.30212 | -0.068664 | 122.2321 | 122.2549 | 54.5609 | -122.2137 | 122.1405 | 122.1909 | 46.7056 | -122.3145
1327.8281 | 122.3282 | -36.5891 | 85.6796 | 0.0054168 | -0.029621 | 0.13709 | 0.028433 | 0.074659 | -0.016904 | -0.019506 | 0.022583 | -0.0015829 | 0.042816 | 0.061776 | -0.017867 | -0.014035 | 85.5515 | -11.2244 | 23.2635 | -34.9274 | 85.4553 | -36.676 | -36.6806 | -33.0917 | 11.4029 | -36.9781 | 85.3683 | 85.4645 | -36.5982 | -36.7676 | -0.086975 | -0.091553 | -0.2243 | 25.3647 | 1.6617 | 1.7532 | -0.12817 | -0.009156 | -0.17853 | -0.31128 | 3.4973 | -0.3891 | -0.21057 | -0.21515 | 122.0444 | 122.1405 | 59.8526 | -122.3602 | 121.9574 | 122.0535 | 47.9919 | -122.4472
1329.6094 | 122.406 | -36.5479 | 85.6384 | -0.0022127 | -0.034107 | 0.13666 | 0.024588 | 0.0706 | -0.015195 | -0.018865 | 0.014954 | -0.0020103 | 0.039826 | 0.064553 | -0.015518 | -0.013821 | 85.7071 | -10.9497 | 23.8037 | -35.0739 | 85.5927 | -36.5524 | -36.5067 | -32.547 | 11.2564 | -36.8454 | 85.4919 | 85.5743 | -36.4517 | -36.6119 | -0.004577 | 0.041199 | -0.045777 | 25.5981 | 1.474 | 1.4328 | 0.068664 | 0.096131 | -0.064086 | -0.14648 | 4.0009 | -0.29755 | -0.23346 | -0.064087 | 122.1405 | 122.2549 | 60.3516 | -122.1451 | 122.0398 | 122.1222 | 47.8043 | -122.2504
1331.3281 | 122.319 | -37.2391 | 84.9792 | 0.0054168 | -0.032398 | 0.1373 | 0.02587 | 0.074659 | -0.010068 | -0.017156 | 0.014954 | 0.00033975 | 0.042176 | 0.063057 | -0.013381 | -0.01553 | 85.112 | -11.2244 | 25.177 | -35.1334 | 85.0845 | -37.1246 | -37.1384 | -33.1375 | 11.0916 | -37.4817 | 84.9609 | 85.0296 | -37.056 | -37.2116 | 0.11444 | 0.10071 | 0.10529 | 26.0147 | 2.1057 | 2.005 | 0.13275 | 0.18311 | 0.027466 | -0.018311 | 4.1016 | -0.24261 | -0.27008 | 0.050354 | 122.3236 | 122.3511 | 62.4161 | -122.1176 | 122.2 | 122.2687 | 48.3307 | -122.1909
1333.125 | 122.3145 | -37.1017 | 85.1486 | 0.0054168 | -0.032612 | 0.14264 | 0.026724 | 0.074232 | -0.01434 | -0.017156 | -0.0079343 | -0.00094205 | 0.041107 | 0.063485 | -0.017654 | -0.011899 | 85.112 | -11.1511 | 24.8199 | -35.1379 | 85.1028 | -37.0789 | -37.0605 | -32.9224 | 11.1694 | -37.413 | 85.0296 | 85.1303 | -36.9919 | -37.1475 | 0.022889 | 0.041199 | -0.045777 | 25.9506 | 1.9638 | 1.9226 | -0.036621 | 0.10986 | -0.045776 | -0.11902 | 4.1794 | -0.31128 | -0.2655 | -0.018311 | 122.2046 | 122.2137 | 61.9217 | -122.2092 | 122.1313 | 122.2321 | 48.2712 | -122.2961
1334.8438 | 122.3557 | -36.3831 | 85.8582 | 0.0054168 | -0.029407 | 0.14222 | 0.027579 | 0.075514 | -0.011991 | -0.016515 | 0.0073242 | -0.00030125 | 0.042603 | 0.066048 | -0.017227 | -0.013394 | 85.8398 | -11.2518 | 18.8232 | -34.4467 | 85.8948 | -36.3556 | -36.3373 | -32.1075 | 11.1877 | -36.7355 | 85.7666 | 85.8398 | -36.264 | -36.4151 | 0.027466 | 0.045777 | 0.036621 | 25.1312 | 1.9363 | 1.8906 | -0.01831 | 0.11902 | -0.032043 | -0.091552 | 4.2755 | -0.35248 | -0.32043 | -0.01831 | 122.2778 | 122.2229 | 55.2063 | -122.1954 | 122.1497 | 122.2229 | 47.5708 | -122.2733
1336.625 | 122.4518 | -35.6277 | 86.5173 | 0.013046 | -0.034748 | 0.14628 | 0.028006 | 0.073805 | -0.015836 | -0.016088 | 0.014954 | -0.0054281 | 0.040467 | 0.062203 | -0.019576 | -0.011471 | 86.5448 | -11.6226 | 21.579 | -33.5632 | 86.5265 | -35.6461 | -35.6415 | -31.2698 | 11.8515 | -35.9024 | 86.3663 | 86.499 | -35.5545 | -35.7056 | -0.01831 | -0.013732 | 0.009155 | 24.0051 | 2.0645 | 2.0782 | 0.027466 | 0.073243 | -0.077819 | -0.15106 | 4.3579 | -0.27466 | -0.19684 | -0.018311 | 122.1542 | 122.1725 | 57.2067 | -122.1588 | 121.994 | 122.1268 | 47.4792 | -122.2229
1338.3594 | 122.3328 | -34.9045 | 87.3459 | 0.0054168 | -0.030689 | 0.14499 | 0.027792 | 0.077436 | -0.0089999 | -0.016302 | 0.022583 | -0.00094205 | 0.043244 | 0.06263 | -0.016799 | -0.013608 | 87.2772 | -11.7599 | 19.6014 | -32.4188 | 87.2955 | -34.9136 | -34.9319 | -30.5237 | 12.0941 | -35.2798 | 87.2086 | 87.291 | -34.8038 | -34.9457 | -0.009155 | -0.027466 | -0.050354 | 23.1445 | 2.4857 | 2.5131 | -0.068664 | 0.10071 | -0.041199 | -0.13733 | 4.3808 | -0.37537 | -0.33417 | -0.054931 | 122.2 | 122.1817 | 54.5059 | -122.2778 | 122.113 | 122.1954 | 46.9986 | -122.2916
1340.1406 | 122.2778 | -32.6111 | 89.653 | 0.013046 | -0.027485 | 0.14692 | 0.027365 | 0.070814 | 0.00082671 | -0.012884 | -0.0003053 | 0.00076695 | 0.044953 | 0.064125 | -0.012954 | -0.011471 | 89.5889 | -12.7441 | 23.3093 | -29.3335 | 89.6301 | -32.5928 | -32.5836 | -28.2944 | 13.1424 | -32.9956 | 89.5111 | 89.5706 | -32.5058 | -32.6523 | 0.018311 | 0.027466 | -0.022888 | 19.8669 | 3.2776 | 3.2501 | -0.064087 | 0.10529 | -0.041199 | -0.14191 | 4.3167 | -0.38452 | -0.34332 | -0.082397 | 122.2412 | 122.2 | 55.9204 | -122.2366 | 122.1222 | 122.1817 | 45.7535 | -122.3053
1341.8438 | 122.406 | -32.0206 | 90.1794 | -0.0022127 | -0.032825 | 0.14905 | 0.027792 | 0.069318 | -0.0081455 | -0.013097 | 0.014954 | -0.0037191 | 0.040467 | 0.062844 | -0.018081 | -0.011258 | 90.1428 | -12.735 | 20.755 | -28.6285 | 90.1291 | -31.9931 | -31.9885 | -27.7588 | 13.7833 | -32.3273 | 90.0375 | 90.1703 | -31.929 | -32.0663 | 0.027466 | 0.032044 | -0.050354 | 19.2856 | 3.392 | 3.36 | -0.036621 | 0.091553 | -0.045776 | -0.14191 | 4.2618 | -0.3067 | -0.26093 | -0.009155 | 122.1497 | 122.1634 | 52.7756 | -122.168 | 122.0581 | 122.1909 | 45.8038 | -122.2458
1343.625 | 122.3923 | -29.6402 | 92.5323 | -0.0022127 | -0.031544 | 0.15204 | 0.02587 | 0.072523 | 0.0027493 | -0.011388 | 0.014954 | -0.00051485 | 0.041321 | 0.063912 | -0.014449 | -0.012753 | 92.5644 | -13.1973 | 19.986 | -25.3922 | 92.4866 | -29.6356 | -29.6585 | -25.4974 | 15.0742 | -29.9652 | 92.3401 | 92.4728 | -29.5898 | -29.7043 | 0.004578 | -0.01831 | -0.045777 | 16.4429 | 4.248 | 4.2664 | 0.032043 | 0.050354 | -0.064087 | -0.19226 | 4.1428 | -0.32501 | -0.26093 | -0.05951 | 122.1268 | 122.2046 | 49.6262 | -122.1909 | 121.9803 | 122.113 | 44.7144 | -122.2366
1345.3438 | 122.4152 | -27.5116 | 94.6335 | 0.013046 | -0.028766 | 0.15397 | 0.025443 | 0.068891 | 0.0076627 | -0.011175 | 0.0073242 | -8.7654e-05 | 0.042389 | 0.062416 | -0.014236 | -0.013821 | 94.5831 | -13.9481 | 19.6289 | -22.6044 | 94.6426 | -27.5436 | -27.5574 | -23.5794 | 16.0172 | -27.9099 | 94.4916 | 94.6152 | -27.4658 | -27.6169 | -0.032043 | -0.045776 | 0.009155 | 13.5635 | 4.9072 | 4.953 | -0.050354 | 0.045777 | -0.10529 | -0.14191 | 3.9322 | -0.39825 | -0.29297 | -0.018311 | 122.1542 | 122.0947 | 47.1405 | -122.1909 | 122.0032 | 122.1268 | 43.5287 | -122.2504
1347.125 | 122.2916 | -25.7263 | 96.5561 | 0.013046 | -0.030903 | 0.15717 | 0.027792 | 0.071455 | 0.0091581 | -0.0094656 | 0.014954 | -0.0011557 | 0.043457 | 0.061562 | -0.018508 | -0.012112 | 96.4737 | -14.6622 | 21.1258 | -20.3842 | 96.4828 | -25.6897 | -25.6805 | -21.936 | 16.5756 | -26.0605 | 96.4096 | 96.5057 | -25.621 | -25.7492 | 0.036621 | 0.045776 | -0.073242 | 11.0641 | 5.3421 | 5.2963 | -0.082397 | 0.10528 | -0.022889 | -0.14648 | 3.7903 | -0.33417 | -0.31128 | -0.050354 | 122.2092 | 122.2 | 46.8521 | -122.2366 | 122.1359 | 122.2321 | 42.3019 | -122.3053
1348.8438 | 122.3099 | -24.5636 | 97.6364 | -0.0098417 | -0.02898 | 0.15931 | 0.029929 | 0.070173 | 0.011722 | -0.009252 | 0.0073242 | -0.0024375 | 0.04303 | 0.060707 | -0.020217 | -0.01318 | 97.6593 | -14.7766 | 23.378 | -18.5944 | 97.5677 | -24.5224 | -24.5499 | -20.7687 | 17.2714 | -24.8383 | 97.4854 | 97.6044 | -24.4766 | -24.5819 | 0.041199 | 0.013733 | -0.068665 | 9.787 | 5.9692 | 5.9555 | 0.022888 | 0.086975 | -0.01831 | -0.15106 | 3.7949 | -0.27466 | -0.25635 | -0.032044 | 122.1313 | 122.2229 | 47.9416 | -122.1863 | 122.049 | 122.168 | 41.835 | -122.2183
1350.6406 | 122.3648 | -27.5162 | 94.6381 | -0.0022127 | -0.029835 | 0.17682 | 0.02587 | 0.075514 | 0.019839 | -0.006475 | 0.014954 | -0.00094205 | 0.041535 | 0.064125 | -0.015945 | -0.011258 | 94.6426 | -16.9968 | 23.9273 | -20.3888 | 94.5831 | -27.5482 | -27.5253 | -23.3597 | 16.1865 | -27.8641 | 94.4687 | 94.5602 | -27.4612 | -27.5986 | -0.032044 | -0.009156 | -0.054932 | 10.5194 | 7.1274 | 7.1365 | 0.004577 | 0.054931 | -0.082398 | -0.16937 | 4.1565 | -0.3479 | -0.2655 | -0.07782 | 122.0993 | 122.1588 | 51.4435 | -122.1634 | 121.9849 | 122.0764 | 43.7027 | -122.2366
1352.3594 | 122.287 | -29.0176 | 93.2236 | 0.0054168 | -0.024708 | 0.18644 | 0.027365 | 0.07765 | 0.031589 | -0.0056204 | 0.0073242 | 0.00055335 | 0.043671 | 0.063485 | -0.013168 | -0.014035 | 93.2465 | -18.1137 | 26.2573 | -21.0663 | 93.2648 | -28.9581 | -28.9536 | -24.4125 | 15.6555 | -29.3427 | 93.1091 | 93.2053 | -28.9032 | -29.0405 | 0.059509 | 0.064087 | 0.041199 | 10.9039 | 7.9514 | 7.8873 | 0.022888 | 0.11444 | -0.022888 | -0.11444 | 4.6051 | -0.32501 | -0.30212 | -0.018311 | 122.2824 | 122.2641 | 55.275 | -122.1771 | 122.1268 | 122.2229 | 44.6732 | -122.2641
1354.125 | 122.2824 | -31.2607 | 90.9348 | 0.013046 | -0.027485 | 0.19434 | 0.026297 | 0.076582 | 0.035861 | -0.007543 | 0.0073242 | 0.0026895 | 0.043457 | 0.063698 | -0.013168 | -0.012967 | 90.9485 | -20.1187 | 24.2844 | -22.5128 | 90.9622 | -31.2424 | -31.2332 | -26.2436 | 14.4333 | -31.5353 | 90.8615 | 90.9531 | -31.1417 | -31.2973 | 0.01831 | 0.027466 | 0.027466 | 11.142 | 8.7479 | 8.7204 | 0.013733 | 0.11902 | -0.036621 | -0.073242 | 5.0171 | -0.27466 | -0.23804 | 0.018311 | 122.2229 | 122.2092 | 55.545 | -122.168 | 122.1222 | 122.2137 | 45.694 | -122.2321
1355.8906 | 122.3785 | -54.1397 | 67.9825 | 0.020676 | -0.024494 | 0.25117 | 0.032492 | 0.088758 | 0.056796 | -0.0032706 | -0.0003053 | 0.0024759 | 0.04538 | 0.066903 | -0.016158 | -0.012967 | 67.9916 | -34.9548 | 1.8265 | -41.0934 | 68.0099 | -54.2038 | -54.1351 | -45.8267 | 2.5131 | -54.4647 | 67.9184 | 68.0008 | -54.1168 | -54.2542 | -0.064087 | 0.004577 | 0.027466 | 19.1849 | 13.0463 | 13.0417 | 0.009155 | 0.022888 | -0.11444 | -0.064087 | 8.313 | -0.32501 | -0.21057 | 0.01831 | 122.1497 | 122.1313 | 55.9662 | -122.1176 | 122.0581 | 122.1405 | 56.6528 | -122.2366
1357.6094 | 122.3877 | -80.0766 | 41.9861 | 0.013046 | -0.031116 | 0.5543 | 0.026724 | 0.14387 | 0.27619 | 0.00078825 | 0.0073242 | 0.00055335 | 0.04303 | 0.068184 | -0.014877 | -0.011471 | 41.7252 | -14.9872 | -17.8665 | -6.4224 | 41.8076 | -80.4382 | -80.2597 | -71.1273 | -9.1141 | -80.5023 | 41.7755 | 41.8259 | -80.1773 | -80.3741 | -0.36163 | -0.18311 | -0.17853 | 65.0894 | 73.6542 | 73.8373 | -0.26093 | -0.10071 | -0.29755 | -0.21057 | 8.9493 | -0.42572 | -0.12817 | -0.16022 | 121.8842 | 121.8018 | 62.2101 | -122.2458 | 121.8521 | 121.9025 | 70.9625 | -122.3602
1359.4062 | 122.287 | -45.3827 | 76.7578 | 0.013046 | -0.029621 | 0.42335 | 0.026511 | 0.11867 | 0.2027 | 0.00014745 | 0.0073242 | 0.00033975 | 0.043885 | 0.065407 | -0.014022 | -0.012326 | 76.6663 | 8.3908 | 9.6634 | -2.8885 | 76.7166 | -45.369 | -45.3461 | -40.7043 | 8.3359 | -45.7901 | 76.6434 | 76.7899 | -45.2728 | -45.4514 | 0.013732 | 0.036621 | -0.041198 | 53.7735 | 42.4942 | 42.4576 | -0.091552 | 0.10986 | -0.068665 | -0.11444 | 4.6783 | -0.40741 | -0.33875 | 0.032044 | 122.0993 | 122.0489 | 55.0461 | -122.1039 | 122.0261 | 122.1725 | 53.7186 | -122.2092
1361.1875 | 122.287 | -105.5603 | 16.5024 | 0.0054168 | -0.028553 | 0.9448 | 0.030569 | 0.16994 | 0.612 | 0.0035654 | 0.014954 | 0.00033975 | 0.042816 | 0.067543 | -0.015304 | -0.0095489 | 16.5894 | -11.7874 | -47.1222 | -5.1819 | 16.6718 | -105.5649 | -105.3864 | -94.6655 | -21.9543 | -105.661 | 16.5527 | 16.5939 | -105.4321 | -105.661 | -0.004577 | 0.17395 | 0.16937 | 93.7729 | 100.3784 | 100.2045 | 0.086975 | 0.12817 | -0.10071 | 0.050354 | 10.8948 | -0.10071 | 0 | 0.091553 | 122.2321 | 122.1497 | 58.4381 | -121.8887 | 122.113 | 122.1542 | 83.606 | -122.1634
1362.9219 | 122.3236 | -114.0381 | 8.0521 | -0.0022127 | -0.035175 | 1.0471 | 0.02822 | 0.18254 | 0.67481 | 0.005488 | -0.0079343 | -0.0039329 | 0.040467 | 0.068825 | -0.017867 | -0.0099763 | 7.9422 | -10.4828 | -55.188 | -3.8132 | 7.9926 | -114.0884 | -113.8824 | -99.6826 | -25.383 | -114.0106 | 7.933 | 7.9742 | -113.9191 | -114.1754 | -0.050354 | 0.15564 | -0.059509 | 103.5553 | 110.2249 | 110.0693 | -0.10986 | 0.11902 | -0.13733 | -0.11902 | 14.3555 | 0.027466 | 0.16479 | -0.07782 | 122.0306 | 121.9803 | 58.8501 | -121.9345 | 121.9711 | 122.0123 | 88.6551 | -122.2275
1364.7031 | 122.1817 | -115.6631 | 6.4178 | 0.0054168 | -0.029835 | 1.0873 | 0.025443 | 0.20497 | 0.69745 | 0.0067696 | 0.0073242 | 0.00033975 | 0.043244 | 0.073525 | -0.014022 | -0.0091217 | 6.1615 | -9.2743 | -57.2113 | -3.5385 | 6.3904 | -115.7135 | -115.5487 | -95.5215 | -26.4862 | -115.8463 | 6.3309 | 6.3766 | -115.5533 | -115.8325 | -0.050354 | 0.11444 | -0.027466 | 106.3889 | 112.1246 | 112.0102 | -0.25635 | 0.10986 | -0.16937 | -0.086975 | 20.1416 | -0.18311 | -0.013732 | -0.041199 | 122.0535 | 121.8246 | 58.4518 | -121.9666 | 121.994 | 122.0398 | 89.1769 | -122.2504
1366.5 | 122.2366 | -116.3773 | 5.6625 | 0.0054168 | -0.033039 | 1.143 | 0.030142 | 0.20262 | 0.69361 | 0.0046334 | -0.0003053 | -0.0037191 | 0.04068 | 0.12052 | -0.018936 | -0.0089081 | 5.5069 | -7.6584 | -53.064 | -3.2181 | 5.5801 | -116.3773 | -116.2079 | -10.2036 | -24.6323 | -116.3544 | 5.571 | 5.6168 | -116.2216 | -116.5054 | 0 | 0.16937 | -0.082398 | 108.7189 | 113.1592 | 112.9898 | -0.15564 | 0.15564 | -0.12817 | -0.091553 | 106.1737 | 0.022888 | 0.15106 | -0.045777 | 121.9574 | 121.8842 | 63.3133 | -121.8704 | 121.9482 | 121.994 | 91.745 | -122.168
1368.2188 | 122.1313 | -116.8808 | 5.1865 | 0.0054168 | -0.029835 | 1.1509 | 0.030997 | 0.20433 | 0.70386 | 0.006556 | 0.0073242 | -0.0011557 | 0.042603 | 0.12309 | -0.018722 | -0.012112 | 4.9667 | -6.4316 | -54.2542 | -3.0579 | 5.1041 | -116.8854 | -116.716 | -8.9722 | -25.5981 | -116.9586 | 5.0766 | 5.1315 | -116.7297 | -116.9952 | -0.004578 | 0.16479 | -0.082397 | 110.4492 | 113.8229 | 113.6581 | -0.21973 | 0.15106 | -0.11444 | -0.10986 | 107.9086 | -0.07782 | 0.036621 | -0.054931 | 121.9849 | 121.8475 | 62.6266 | -121.9025 | 121.9574 | 122.0123 | 91.2827 | -122.1817
1370 | 122.1176 | -117.0593 | 4.9805 | 0.013046 | -0.030262 | 1.1892 | 0.027365 | 0.20988 | 0.70536 | 0.008906 | 0.0073242 | -0.0015829 | 0.043457 | 0.12266 | -0.017227 | -0.012753 | 4.6921 | -5.7266 | -53.5904 | -2.9663 | 4.921 | -117.0914 | -116.9357 | -8.4686 | -27.8549 | -117.1646 | 4.8798 | 4.9301 | -116.9037 | -117.2012 | -0.032044 | 0.1236 | -0.05951 | 111.3327 | 114.093 | 113.9694 | -0.28839 | 0.15564 | -0.14191 | -0.10071 | 108.5907 | -0.10529 | 0.036621 | -0.050354 | 121.9803 | 121.7514 | 63.4689 | -121.9162 | 121.9391 | 121.9894 | 89.2044 | -122.1817
1371.7188 | 122.1451 | -116.4047 | 5.2734 | 0.0054168 | -0.034321 | 1.2445 | 0.025443 | 0.22249 | 0.70493 | 0.011042 | 0.014954 | -0.0037191 | 0.039612 | 0.12202 | -0.012313 | -0.010403 | 4.6829 | -4.6738 | -53.6224 | -2.7649 | 4.7653 | -117.1188 | -116.954 | -7.9651 | -28.2394 | -117.1692 | 4.7333 | 4.8157 | -116.9632 | -117.2699 | -0.71411 | -0.54932 | -0.50812 | 111.731 | 113.6398 | 114.1891 | -0.59052 | -0.55847 | -0.86517 | -0.54016 | 108.4396 | -0.76447 | 0.10071 | -0.45776 | 121.17 | 121.0876 | 62.7823 | -122.2275 | 121.138 | 121.2204 | 88.1653 | -122.5433
1373.5 | 122.2321 | -117.1555 | 4.7607 | 0.0054168 | -0.03368 | 1.3654 | 0.026297 | 0.28123 | 0.71134 | 0.0080514 | 0.0073242 | -0.00030125 | 0.042603 | 0.12287 | -0.012954 | -0.011044 | 4.4403 | -4.4128 | -53.6316 | -2.7649 | 4.6509 | -117.2607 | -117.1097 | -7.9605 | -28.4225 | -117.3248 | 4.6234 | 4.6783 | -117.0914 | -117.4026 | -0.10528 | 0.045777 | -0.10986 | 112.7426 | 114.3906 | 114.3448 | -0.32043 | 0.064087 | -0.24719 | -0.13733 | 109.1949 | -0.16937 | 0.07782 | -0.082397 | 121.8063 | 121.5958 | 63.5239 | -121.8704 | 121.7789 | 121.8338 | 88.7329 | -122.1634
1375.2188 | 122.1405 | -87.8311 | 34.0805 | 0.013046 | -0.028766 | 0.93198 | 0.025229 | 0.20582 | 0.54108 | 0.006556 | 0.014954 | -0.0022239 | 0.043457 | 0.10407 | -0.014449 | -0.012112 | 33.7784 | 3.9139 | -28.8803 | -1.9272 | 33.728 | -88.0508 | -87.941 | -6.9168 | -13.4903 | -88.1561 | 33.7051 | 33.7692 | -87.9227 | -88.147 | -0.21973 | -0.10986 | -0.35248 | 91.745 | 85.9039 | 86.0138 | -0.30212 | -0.091552 | -0.31586 | -0.37537 | 80.9143 | -0.32501 | -0.009155 | -0.31128 | 121.5591 | 121.6095 | 58.9508 | -122.0215 | 121.5363 | 121.6003 | 74.3408 | -122.2275
1376.9844 | 122.0856 | -93.8736 | 28.0655 | 0.0054168 | -0.029407 | 0.87943 | 0.026511 | 0.19685 | 0.4896 | 0.01446 | 0.0073242 | 0.00033975 | 0.045166 | 0.1107 | -0.013168 | -0.010403 | 28.4683 | -0.70953 | -33.2199 | -1.9318 | 28.4363 | -93.512 | -93.4021 | -7.8598 | -16.9052 | -94.0155 | 28.0838 | 28.125 | -93.6493 | -93.9423 | 0.36163 | 0.4715 | 0.37079 | 93.1641 | 91.9418 | 91.4703 | 0.40283 | 0.2243 | -0.068665 | 0.01831 | 86.0138 | -0.14191 | -0.073242 | 0.059509 | 122.3099 | 122.3419 | 60.6537 | -121.4676 | 121.9574 | 121.9986 | 76.9684 | -122.0078
1378.7656 | 122.049 | -79.6326 | 42.3386 | 0.0054168 | -0.027057 | 0.83286 | 0.028433 | 0.18468 | 0.48426 | 0.013606 | -0.0003053 | -0.0020103 | 0.044953 | 0.10215 | -0.013595 | -0.0099763 | 42.1646 | 1.9821 | -20.2927 | -1.7075 | 42.1875 | -79.6692 | -79.5776 | -6.7795 | -9.4482 | -79.921 | 42.1646 | 42.2379 | -79.5502 | -79.7974 | -0.036621 | 0.054931 | -0.15106 | 81.6147 | 77.9251 | 77.8702 | -0.17395 | 0.082397 | -0.16479 | -0.17395 | 72.8531 | -0.28839 | -0.1236 | -0.10071 | 121.8201 | 121.7972 | 59.3399 | -121.9162 | 121.7972 | 121.8704 | 70.1843 | -122.1359
1380.5469 | 122.1909 | -76.7395 | 45.1263 | -0.0022127 | -0.029407 | 0.81193 | 0.028006 | 0.18532 | 0.4646 | 0.013606 | 0.014954 | -0.0037191 | 0.043244 | 0.10087 | -0.01274 | -0.011471 | 44.9707 | 1.2817 | -18.3701 | -1.5701 | 44.9295 | -76.8768 | -76.7624 | -6.7978 | -8.1116 | -76.9867 | 44.9341 | 45.0394 | -76.6846 | -76.8723 | -0.13733 | -0.022888 | -0.19684 | 78.0212 | 75.1694 | 75.1923 | -0.15564 | 0.054932 | -0.13275 | -0.19226 | 69.9417 | -0.24719 | -0.11444 | -0.086975 | 121.669 | 121.7102 | 58.3694 | -121.8887 | 121.6736 | 121.7789 | 68.6279 | -121.9986
1382.2812 | 122.2046 | -84.5993 | 37.2574 | -0.0098417 | -0.029194 | 0.93027 | 0.03121 | 0.24235 | 0.51032 | 0.0097604 | 0.014954 | -0.0017965 | 0.044525 | 0.10535 | -0.015304 | -0.0097625 | 37.0331 | -0.74616 | -24.0555 | -1.8265 | 36.9095 | -84.9106 | -84.7778 | -7.1228 | -12.7487 | -84.8969 | 36.969 | 37.0697 | -84.6497 | -84.8419 | -0.31128 | -0.17853 | -0.3479 | 83.8531 | 82.7728 | 82.9514 | -0.2243 | -0.050354 | -0.24262 | -0.28839 | 77.4765 | -0.29755 | -0.054932 | -0.18768 | 121.5088 | 121.6324 | 60.5438 | -122.0352 | 121.5683 | 121.669 | 71.8506 | -122.0993
1384.0625 | 122.0856 | -95.7092 | 26.1749 | 0.013046 | -0.023426 | 0.99201 | 0.029074 | 0.24769 | 0.54749 | 0.012538 | -0.0003053 | 0.00076695 | 0.044312 | 0.10899 | -0.011886 | -0.010831 | 25.8682 | -0.3067 | -32.9681 | -1.8723 | 25.9323 | -95.9427 | -95.8008 | -7.9514 | -18.7134 | -96.1258 | 25.9323 | 25.9689 | -95.8054 | -96.0846 | -0.23346 | -0.091552 | -0.24262 | 95.4025 | 93.837 | 93.9285 | -0.3067 | -0.09613 | -0.37537 | -0.24262 | 87.7579 | -0.41656 | -0.041198 | -0.20599 | 121.6415 | 121.5775 | 62.7411 | -121.9757 | 121.6415 | 121.6782 | 76.9958 | -122.2595
1385.8281 | 121.9437 | -84.4666 | 37.4222 | 0.013046 | -0.02663 | 1.9644 | 0.029715 | 1.3716 | 0.42572 | 0.010615 | 0.0073242 | -0.0026511 | 0.043244 | 0.106 | -0.018722 | -0.010617 | 37.3352 | 3.8635 | -24.7009 | -12.4008 | 37.4634 | -84.0179 | -83.8806 | -7.2784 | -13.2614 | -84.7275 | 37.2437 | 37.294 | -84.3018 | -84.5764 | 0.44861 | 0.58594 | 0.041199 | 88.3301 | 72.0657 | 71.4798 | -0.086975 | 0.16479 | -0.10986 | -0.17853 | 77.1881 | -0.26093 | -0.15106 | -0.12817 | 121.9299 | 121.8018 | 59.7656 | -121.3028 | 121.7102 | 121.7606 | 71.2051 | -121.9986
1387.6094 | 121.9345 | -68.7424 | 53.0365 | 0.013046 | -0.029835 | 1.9514 | 0.027152 | 1.428 | 0.4097 | 0.011042 | 0.0073242 | -0.0028647 | 0.039398 | 0.097451 | -0.015304 | -0.011685 | 58.4702 | 4.4174 | -6.9626 | -2.5406 | 56.044 | -65.8997 | -66.069 | -6.2073 | -3.5843 | -66.2521 | 54.6295 | 54.7394 | -67.0166 | -67.4469 | 2.8427 | 2.6733 | 3.0075 | 73.1598 | 66.2018 | 63.5284 | 5.4337 | 1.7258 | 1.2955 | 1.593 | 62.5351 | 2.4902 | 1.1948 | 1.7029 | 124.7864 | 127.2125 | 61.7798 | -119.1055 | 123.3719 | 123.4818 | 65.1581 | -120.4834
1389.3281 | 121.8201 | -87.2635 | 34.3231 | 0.0054168 | -0.026417 | 3.566 | 0.026511 | 3.2514 | 0.29947 | 0.015955 | 0.0073242 | 0.0018351 | 0.042176 | 0.10493 | -0.01274 | -0.010403 | 33.7601 | 0.036621 | -27.1729 | -37.5778 | 33.5587 | -87.4237 | -87.3138 | -7.5851 | -15.7974 | -88.2065 | 33.8654 | 33.8928 | -87.5473 | -87.8128 | -0.16022 | -0.050354 | -0.76447 | 87.3001 | 49.6857 | 49.736 | -0.56305 | -0.28381 | -0.54932 | -0.45776 | 79.6783 | -0.94299 | -0.39368 | -0.4303 | 120.8221 | 121.0236 | 60.0906 | -121.637 | 121.1288 | 121.1563 | 71.4661 | -122.1359
1391.1094 | 121.7651 | -83.876 | 37.5412 | 0.013046 | -0.031116 | 5.9713 | 0.032706 | 5.5558 | 0.25717 | 0.015315 | 0.0073242 | -0.0047873 | 0.042816 | 0.10322 | -0.020004 | -0.0091217 | 37.1979 | -2.33 | -21.6293 | -29.3747 | 37.4634 | -83.2214 | -83.2672 | -7.3196 | -13.1973 | -83.7891 | 37.5458 | 37.706 | -83.519 | -83.812 | 0.6546 | 0.60883 | -0.07782 | 81.546 | 54.5013 | 53.8925 | -0.34332 | 0.35706 | 0.064087 | 0.004577 | 76.5564 | 0.086976 | 0.022889 | 0.16479 | 121.3394 | 121.0739 | 62.2467 | -120.8084 | 121.4218 | 121.582 | 70.6787 | -121.3531
1392.8125 | 121.9208 | -71.3928 | 49.8459 | 0.0054168 | -0.026203 | 1.584 | 0.032278 | 1.2169 | 0.14588 | 0.014887 | 0.014954 | -0.0011557 | 0.045166 | 0.095528 | -0.014877 | -0.0097625 | 52.3819 | 0.83313 | -7.0953 | -42.3981 | 52.3453 | -69.1223 | -69.0308 | -6.7657 | -5.4886 | -69.4656 | 52.4139 | 52.3224 | -69.2596 | -69.4565 | 2.2705 | 2.3621 | 2.4994 | 72.226 | 28.9948 | 26.6327 | 2.536 | 2.1332 | 1.9363 | 2.5681 | 64.6271 | 1.9272 | -0.009155 | 2.4765 | 123.7381 | 123.7747 | 64.2975 | -118.8766 | 123.8068 | 123.7152 | 65.9042 | -119.3024
1394.5938 | 121.907 | -54.5792 | 67.2775 | 0.0054168 | -0.030048 | 1.0582 | 0.024802 | 0.80867 | 0.16147 | 0.014246 | 0.0073242 | -0.0013693 | 0.043244 | 0.087838 | -0.014877 | -0.012326 | 65.9088 | 0.027466 | 8.2169 | -24.4034 | 65.3503 | -55.9433 | -55.8975 | -5.5801 | 2.0187 | -56.5384 | 65.1169 | 65.4419 | -55.8472 | -55.8609 | -1.3641 | -1.3184 | -1.9272 | 54.6066 | 30.1758 | 31.4941 | -1.3687 | -1.268 | -1.2817 | -2.1606 | 48.999 | -1.9592 | -0.67749 | -1.8356 | 119.9295 | 120.488 | 62.796 | -123.175 | 119.696 | 120.0211 | 56.5979 | -123.1384
1396.3125 | 121.9757 | -120.1813 | 1.4694 | 0.0054168 | -0.035816 | 0.16913 | 0.022879 | -0.017199 | 0.0021085 | -0.02506 | 0.0073242 | -0.0037191 | 0.040039 | 0.12351 | -0.010818 | -0.0080535 | 1.474 | 0.1236 | -0.13275 | 0.15564 | 1.506 | 0.38452 | 0.23346 | -8.3908 | -29.8599 | -120.2499 | 1.3779 | 1.4008 | -120.1538 | -120.3781 | 120.5658 | 120.4147 | 0.036621 | 120.3049 | 120.3369 | -0.077819 | 0.004578 | 0.027465 | -0.19684 | -0.091552 | 111.7905 | -0.068665 | 0.12817 | -0.068664 | 121.6873 | 121.6553 | 120.0485 | -1.236 | 121.5591 | 121.582 | 90.3213 | -121.8475
1398.0938 | 122.0261 | -120.5566 | 1.3458 | 0.013046 | -0.042225 | 0.17341 | 0.023734 | 0.0045907 | -0.026944 | -0.025701 | 0.0073242 | -0.0041465 | 0.038544 | 0.12223 | -0.01274 | -0.0080535 | 1.3275 | 0.19684 | -0.33417 | 0.1831 | 1.3504 | 0.082397 | -0.041199 | -7.5485 | -30.0293 | -120.5429 | 1.2177 | 1.2863 | -120.4193 | -120.7123 | 120.639 | 120.5154 | 0.004578 | 120.7535 | 120.7397 | 0.2243 | -0.01831 | 0.13733 | -0.15564 | -0.12817 | 113.0081 | 0.013733 | 0.16937 | -0.059509 | 121.907 | 121.8842 | 120.2225 | -1.387 | 121.7743 | 121.843 | 90.5273 | -122.0581
1399.8594 | 122.0993 | -120.6619 | 1.2909 | 0.0054168 | -0.036457 | 0.17191 | 0.025229 | 0.0048045 | -0.019895 | -0.023778 | 0.0073242 | -0.0022239 | 0.040467 | 0.12373 | -0.011245 | -0.0089081 | 1.2039 | 0.009155 | -0.63171 | 0.082397 | 1.3412 | 0.059509 | -0.064087 | -7.4158 | -30.0934 | -120.7672 | 1.2131 | 1.236 | -120.5383 | -120.845 | 120.7214 | 120.5978 | 0.050354 | 120.6711 | 120.7443 | 0.14648 | -0.086976 | 0.1236 | -0.18311 | -0.07782 | 113.2462 | -0.10529 | 0.07782 | -0.054932 | 122.0032 | 121.8658 | 120.0302 | -1.355 | 121.875 | 121.8979 | 90.5685 | -122.1359
1401.5781 | 122.1313 | -120.7672 | 1.1719 | 0.0054168 | -0.03838 | 0.17298 | 0.025015 | 0.0073679 | -0.023526 | -0.02506 | 0.0073242 | -0.0035055 | 0.039398 | 0.12693 | -0.01509 | -0.0071991 | 1.1993 | 0.15106 | -0.88348 | 0.19684 | 1.1948 | 0.07782 | -0.022888 | -7.0908 | -30.4001 | -120.7397 | 1.0574 | 1.1032 | -120.6345 | -120.9183 | 120.845 | 120.7443 | 0.022888 | 120.9183 | 120.9641 | 0.21973 | 0.027466 | 0.13275 | -0.15106 | -0.11444 | 113.6765 | 0.027466 | 0.17853 | -0.068665 | 121.962 | 121.9666 | 119.8837 | -1.1948 | 121.8246 | 121.8704 | 90.3671 | -122.0901
1403.3594 | 122.2 | -120.7626 | 1.1948 | 0.013046 | -0.037739 | 0.17063 | 0.025443 | 0.0080087 | -0.023099 | -0.023778 | 0.0073242 | -0.0017965 | 0.041321 | 0.12672 | -0.011031 | -0.0097625 | 1.1902 | 0.11444 | -0.50354 | 0.14648 | 1.236 | 0.073242 | -0.054932 | -6.9946 | -31.2653 | -120.7672 | 1.1032 | 1.1444 | -120.6436 | -120.932 | 120.8359 | 120.7077 | 0.041199 | 120.8771 | 120.9091 | 0.20142 | -0.004577 | 0.11902 | -0.16937 | -0.091553 | 113.768 | -0.004578 | 0.16479 | -0.050354 | 121.9986 | 121.9528 | 120.2591 | -1.2497 | 121.8658 | 121.907 | 89.4974 | -122.1268
1405.0625 | 122.1405 | -120.8221 | 1.149 | 0.013046 | -0.041797 | 0.17512 | 0.026511 | 0.0075815 | -0.02844 | -0.024633 | 0.0073242 | -0.0043601 | 0.04068 | 0.12586 | -0.014877 | -0.0069855 | 1.1444 | 0.16479 | -1.0895 | 0.15564 | 1.1627 | 0.10529 | -0.050354 | -6.8848 | -31.6315 | -120.8359 | 1.0391 | 1.0757 | -120.7031 | -121.0007 | 120.9274 | 120.7718 | 0.013733 | 120.9869 | 120.9778 | 0.20599 | -0.004578 | 0.11902 | -0.17853 | -0.10986 | 113.9374 | -0.013732 | 0.16479 | -0.073242 | 121.9849 | 121.9666 | 119.7327 | -1.1993 | 121.8613 | 121.8979 | 89.1907 | -122.1497
1406.8281 | 122.2046 | -120.8038 | 1.1581 | -0.0022127 | -0.034321 | 0.17191 | 0.026511 | 0.0067271 | -0.021817 | -0.023138 | -0.0003053 | 0.00055335 | 0.040467 | 0.1265 | -0.010177 | -0.0069855 | 1.0803 | 0.041199 | -0.90637 | 0.086975 | 1.2131 | 0.054932 | -0.07782 | -6.871 | -31.9931 | -120.9091 | 1.0529 | 1.1032 | -120.7077 | -121.0236 | 120.8588 | 120.726 | 0.054932 | 120.845 | 120.8908 | 0.16479 | -0.07782 | 0.09613 | -0.21973 | -0.10529 | 113.9328 | -0.10529 | 0.11444 | -0.054932 | 122.0169 | 121.8842 | 119.8975 | -1.236 | 121.8567 | 121.907 | 88.8107 | -122.1817
1408.6094 | 122.113 | -120.9778 | 1.0574 | 0.013046 | -0.034534 | 0.17298 | 0.027579 | 0.0071543 | -0.020963 | -0.023992 | 0.0073242 | 0.0033303 | 0.042389 | 0.12693 | -0.011886 | -0.0071991 | 0.94757 | 0.004578 | -0.58136 | 0.10529 | 1.0895 | 0.050354 | -0.091553 | -6.7932 | -32.6706 | -121.0831 | 0.96588 | 1.0254 | -120.8679 | -121.17 | 121.0281 | 120.8862 | 0.032044 | 120.9824 | 121.0831 | 0.19684 | -0.10986 | 0.10986 | -0.19226 | -0.091553 | 114.1846 | -0.10529 | 0.086975 | -0.032043 | 122.0673 | 121.9254 | 120.3964 | -1.149 | 121.9437 | 122.0032 | 88.3072 | -122.2275
1410.3125 | 122.1954 | -121.0373 | 0.98419 | 0.0054168 | -0.039875 | 0.17554 | 0.029929 | 0.0056589 | -0.02908 | -0.024633 | 0.0073242 | -0.0041465 | 0.04303 | 0.12757 | -0.016372 | -0.0033539 | 0.94757 | 0.14648 | -0.85144 | 0.13733 | 0.99792 | 0.082397 | -0.054932 | -6.633 | -33.3435 | -121.0464 | 0.88348 | 0.92926 | -120.8908 | -121.1746 | 121.1197 | 120.9824 | 0.013733 | 121.1838 | 121.1746 | 0.19226 | -0.036621 | 0.14648 | -0.13733 | -0.10071 | 114.4043 | -0.009156 | 0.12817 | -0.054932 | 122.0352 | 121.9849 | 120.1859 | -1.0391 | 121.9208 | 121.9666 | 87.6938 | -122.1588
1412.0938 | 122.1222 | -121.0648 | 1.0117 | 0.0054168 | -0.034748 | 0.17255 | 0.030569 | 0.0080087 | -0.024381 | -0.027624 | 0.0073242 | -0.00030125 | 0.041321 | 0.128 | -0.0121 | -0.0059173 | 0.90179 | 0.059509 | -1.2268 | 0.086975 | 1.062 | 0.041199 | -0.082397 | -6.6147 | -34.0988 | -121.106 | 0.92468 | 0.9613 | -120.9137 | -121.1838 | 121.106 | 120.9824 | 0.050354 | 121.1243 | 121.1517 | 0.16937 | -0.10986 | 0.15106 | -0.11902 | -0.086975 | 114.4501 | -0.041199 | 0.07782 | -0.050354 | 122.1268 | 121.9666 | 119.838 | -1.0941 | 121.9894 | 122.0261 | 86.9659 | -122.1954
1413.8906 | 122.1268 | -121.0739 | 1.0117 | 0.013046 | -0.027271 | 0.16956 | 0.02822 | 0.0060861 | -0.019467 | -0.025701 | 0.0073242 | 0.0022623 | 0.043457 | 0.12885 | -0.014022 | -0.0063447 | 0.97504 | 0.11444 | -1.0391 | 0.13275 | 1.0345 | 0.054932 | -0.07782 | -6.4682 | -35.2112 | -121.0739 | 0.91553 | 0.9613 | -120.9229 | -121.2204 | 121.1288 | 120.9961 | 0.022888 | 121.1884 | 121.2067 | 0.21057 | -0.036621 | 0.15106 | -0.14648 | -0.096131 | 114.6057 | 0 | 0.14648 | -0.050354 | 122.1085 | 122.049 | 120.0348 | -1.0895 | 121.9894 | 122.0352 | 85.8627 | -122.2321
1415.6094 | 122.1222 | -121.1884 | 0.90179 | 0.013046 | -0.016163 | 0.15803 | 0.026297 | 0.0062997 | -0.021817 | -0.023565 | 0.0073242 | 0.0016213 | 0.042816 | 0.12928 | -0.010391 | -0.0050629 | 0.79651 | 0.064087 | -1.4099 | 0.09613 | 0.95673 | 0.064087 | -0.082397 | -6.4819 | -35.9024 | -121.225 | 0.82398 | 0.86517 | -121.0281 | -121.3257 | 121.2524 | 121.106 | 0.054932 | 121.2524 | 121.2845 | 0.17853 | -0.10528 | 0.16022 | -0.13733 | -0.077819 | 114.7064 | -0.036622 | 0.10071 | -0.036621 | 122.1451 | 121.9849 | 119.7784 | -0.98419 | 122.0123 | 122.0535 | 85.2859 | -122.2275
1417.375 | 122.1634 | -121.7148 | 0.3891 | 0.0054168 | 0.053692 | 0.094793 | 0.027152 | 0.0050181 | -0.022031 | -0.022924 | -0.0003053 | 0.00033975 | 0.041321 | 0.12821 | -0.011459 | -0.0044221 | 0.29755 | 0.17853 | -0.72327 | 0.21515 | 0.39825 | 0.15564 | 0.018311 | -6.3766 | -36.8042 | -121.6644 | 0.26093 | 0.33417 | -121.5775 | -121.8521 | 121.8704 | 121.7331 | 0.009155 | 121.8933 | 121.9299 | 0.19684 | -0.091553 | 0.13733 | -0.13733 | -0.12817 | 115.3381 | 0.050354 | 0.18768 | -0.054932 | 122.113 | 122.0123 | 120.9915 | -0.37079 | 121.9757 | 122.0489 | 84.9106 | -122.2412
1419.1562 | 122.168 | -121.8018 | 0.28839 | 0.0054168 | 0.060742 | 0.083898 | 0.024161 | 0.0073679 | -0.022244 | -0.024633 | 0.0073242 | 0.00076695 | 0.041321 | 0.13184 | -0.0088952 | -0.0010041 | 0.16479 | 0.07782 | -0.70496 | 0.13275 | 0.34332 | 0.11444 | 0.004578 | -6.4041 | -37.1704 | -121.8292 | 0.20599 | 0.25635 | -121.669 | -121.9437 | 121.9162 | 121.8063 | 0.054932 | 121.8796 | 121.9345 | 0.12817 | -0.1236 | 0.13275 | -0.14191 | -0.082397 | 115.3976 | -0.027466 | 0.11444 | -0.032043 | 122.1451 | 121.9666 | 121.0968 | -0.28381 | 122.0078 | 122.0581 | 84.6313 | -122.2321
1420.9219 | 122.1405 | -121.8246 | 0.29755 | -0.0022127 | 0.06715 | 0.083685 | 0.026938 | 0.0033091 | -0.022244 | -0.023565 | -0.0003053 | 0.0029031 | 0.044953 | 0.13056 | -0.0097498 | -0.0012177 | 0.14191 | 0.091553 | -0.75073 | 0.13275 | 0.31586 | 0.13275 | -0.022888 | -6.3675 | -38.0035 | -121.8018 | 0.19226 | 0.25635 | -121.6736 | -121.9757 | 121.9574 | 121.8018 | 0.018311 | 121.9162 | 121.9574 | 0.15564 | -0.15564 | 0.15106 | -0.15106 | -0.10528 | 115.4572 | 0.022888 | 0.17395 | -0.041198 | 122.1405 | 121.9666 | 121.0739 | -0.32043 | 122.0169 | 122.081 | 83.8211 | -122.2733
1422.7031 | 122.2366 | -121.8063 | 0.26093 | 0.0054168 | 0.067364 | 0.083257 | 0.028006 | 0.0060861 | -0.023526 | -0.023138 | -0.0003053 | 0.0024759 | 0.044098 | 0.12928 | -0.010604 | -0.0027131 | 0.17395 | 0.11444 | -0.82398 | 0.12817 | 0.3067 | 0.10986 | -0.032043 | -6.3263 | -38.15 | -121.7651 | 0.18768 | 0.23346 | -121.7148 | -121.9757 | 121.9162 | 121.7743 | 0.045777 | 121.9208 | 121.9345 | 0.16022 | -0.086975 | 0.091552 | -0.16937 | -0.073242 | 115.48 | 0.041198 | 0.21057 | -0.027466 | 122.113 | 121.9803 | 120.9824 | -0.29297 | 121.994 | 122.0398 | 83.6563 | -122.2366
1424.5156 | 122.2549 | -121.7926 | 0.24261 | -0.0098417 | 0.068005 | 0.085607 | 0.029501 | 0.0043771 | -0.029508 | -0.024419 | 0.0073242 | -0.0047873 | 0.041962 | 0.12629 | -0.011245 | -0.00014946 | 0.25635 | 0.3067 | -0.41657 | 0.25177 | 0.2655 | 0.14648 | 0.032043 | -6.2439 | -39.0747 | -121.5317 | 0.13733 | 0.19684 | -121.6827 | -121.9711 | 121.9391 | 121.8246 | 0.022888 | 122.0993 | 122.0444 | 0.21973 | 0.013733 | 0.10986 | -0.17853 | -0.10529 | 115.5487 | 0.26093 | 0.43945 | -0.045777 | 122.0581 | 122.049 | 121.376 | -0.21057 | 121.9299 | 121.9894 | 82.7179 | -122.2137
1426.2812 | 122.1954 | -121.8109 | 0.27924 | 0.0054168 | 0.081249 | 0.085394 | 0.026511 | 0.0067271 | -0.020749 | -0.025487 | 0.014954 | 0.0018351 | 0.042389 | 0.12779 | 0.0071264 | -0.00036306 | 0.21515 | 0.19684 | -0.69122 | 0.19684 | 0.32959 | 0.12817 | 0.004578 | -6.4178 | -41.1301 | -121.2616 | 0.19684 | 0.22888 | -121.6782 | -121.9482 | 121.9391 | 121.8155 | 0.050354 | 122.0078 | 122.0078 | 0.19226 | -0.064087 | 0.13275 | -0.13733 | -0.082398 | 115.3931 | 0.54932 | 0.68664 | -0.050354 | 122.1405 | 122.0261 | 121.1197 | -0.27466 | 122.0078 | 122.0398 | 80.6808 | -122.2275
1428 | 122.2595 | -121.7926 | 0.2655 | 0.0054168 | 0.083386 | 0.08283 | 0.026297 | 0.0092905 | -0.022458 | -0.024847 | -0.0003053 | 0.0018351 | 0.043457 | 0.13419 | 0.0017858 | 0.0011321 | 0.1831 | 0.14648 | -2.037 | 0.17853 | 0.31128 | 0.11902 | 0.004578 | -6.3446 | -41.6382 | -121.3852 | 0.19226 | 0.24261 | -121.6736 | -121.9482 | 121.9116 | 121.7972 | 0.045776 | 121.9391 | 121.9711 | 0.17395 | -0.082398 | 0.11902 | -0.15564 | -0.073242 | 115.448 | 0.40741 | 0.56305 | -0.022888 | 122.1039 | 121.9757 | 119.7556 | -0.26092 | 121.9849 | 122.0352 | 80.1544 | -122.2137
1429.7188 | 122.1771 | -121.8292 | 0.29755 | 0.0054168 | 0.087231 | 0.085394 | 0.032278 | 0.0065133 | -0.023526 | -0.026983 | 0.0073242 | -0.00072845 | 0.043671 | 0.13142 | -0.00077757 | 0.0051911 | 0.17395 | 0.15564 | -3.4836 | 0.19226 | 0.32959 | 0.16022 | 0.013733 | -6.4407 | -46.9391 | -121.3943 | 0.2243 | 0.25635 | -121.7102 | -121.9666 | 121.9894 | 121.843 | 0.032044 | 121.9849 | 122.0215 | 0.17853 | -0.1236 | 0.11902 | -0.13733 | -0.073242 | 115.3885 | 0.43488 | 0.57221 | -0.041198 | 122.1588 | 122.0032 | 118.3456 | -0.28381 | 122.0535 | 122.0856 | 74.8901 | -122.2641
1431.5156 | 122.1497 | -121.8063 | 0.31586 | 0.013046 | 0.10154 | 0.087957 | 0.027365 | 0.0062997 | -0.026517 | -0.024847 | -0.0003053 | -0.0015829 | 0.043457 | 0.12821 | 0.014817 | 0.0083953 | 0.27008 | 0.28839 | -1.0712 | 0.29297 | 0.30212 | 0.18768 | 0.054932 | -6.2851 | -51.1185 | -120.3506 | 0.20142 | 0.24719 | -121.6507 | -121.9299 | 121.994 | 121.8613 | -0.013733 | 122.0947 | 122.0993 | 0.23804 | -0.045776 | 0.15564 | -0.1236 | -0.11444 | 115.5212 | 1.4557 | 1.5793 | -0.068665 | 122.1085 | 122.0764 | 120.7352 | -0.26093 | 122.0078 | 122.0535 | 70.6879 | -122.2458
1433.2344 | 122.2366 | -121.7972 | 0.3067 | 0.0054168 | 0.1024 | 0.084325 | 0.029288 | 0.0043771 | -0.028226 | -0.028905 | 0.0073242 | -0.0013693 | 0.044312 | 0.13248 | 0.01204 | 0.0077545 | 0.29297 | 0.28839 | -2.9526 | 0.28839 | 0.31586 | 0.19226 | 0.059509 | -6.0104 | -50.7797 | -120.8405 | 0.16937 | 0.22888 | -121.6553 | -121.9116 | 121.9894 | 121.8567 | 0.009155 | 122.0856 | 122.0856 | 0.22888 | -0.013733 | 0.14191 | -0.11444 | -0.13733 | 115.7867 | 0.95673 | 1.0712 | -0.07782 | 122.113 | 122.0901 | 118.8446 | -0.24719 | 121.9666 | 122.0261 | 71.0175 | -122.2183
1434.9375 | 122.1588 | -121.8018 | 0.32501 | 0.0054168 | 0.10859 | 0.084325 | 0.02822 | 0.0069407 | -0.024594 | -0.026342 | -0.0003053 | 0.00033975 | 0.044098 | 0.13184 | 0.019089 | 0.010104 | 0.24719 | 0.23346 | -3.3325 | 0.2655 | 0.32044 | 0.16479 | 0.054932 | -6.2302 | -50.6332 | -120.639 | 0.24719 | 0.27924 | -121.6599 | -121.9482 | 121.9666 | 121.8567 | -0.004577 | 122.0352 | 122.0673 | 0.21057 | -0.07782 | 0.14191 | -0.14648 | -0.07782 | 115.5716 | 1.1627 | 1.3092 | -0.045776 | 122.1222 | 122.049 | 118.4692 | -0.27008 | 122.049 | 122.081 | 71.1685 | -122.2733
1436.7188 | 122.2824 | -121.7606 | 0.28381 | 0.013046 | 0.10966 | 0.089239 | 0.021811 | 0.0088633 | -0.023099 | -0.024847 | 0.014954 | 0.0029031 | 0.044739 | 0.12885 | 0.024216 | 0.010532 | 0.3067 | 0.28839 | -3.0624 | 0.3067 | 0.29755 | 0.20599 | 0.091553 | -5.9967 | -50.7202 | -120.488 | 0.16937 | 0.21515 | -121.6324 | -121.9116 | 121.9666 | 121.8521 | 0.013733 | 122.049 | 122.0673 | 0.21515 | 0.022889 | 0.12817 | -0.15106 | -0.11444 | 115.7639 | 1.2726 | 1.4236 | -0.068664 | 122.0581 | 122.0673 | 118.6981 | -0.19226 | 121.9299 | 121.9757 | 71.0403 | -122.1954
1438.5 | 122.168 | -121.8155 | 0.31586 | -0.0022127 | 0.11692 | 0.089452 | 0.025656 | 0.0082223 | -0.027158 | -0.025915 | 0.014954 | 0.0011941 | 0.044098 | 0.13163 | 0.023575 | 0.011813 | 0.28839 | 0.30212 | -3.4836 | 0.32044 | 0.3067 | 0.18768 | 0.054932 | -6.102 | -51.9058 | -120.7031 | 0.19684 | 0.21973 | -121.6553 | -121.9345 | 122.0032 | 121.8704 | -0.009155 | 122.1176 | 122.1359 | 0.2655 | -0.027466 | 0.16022 | -0.11902 | -0.11902 | 115.7135 | 1.1124 | 1.2314 | -0.09613 | 122.1222 | 122.1039 | 118.3319 | -0.26093 | 122.0123 | 122.0352 | 69.9097 | -122.2504
1440.2812 | 122.0947 | -121.2479 | 0.87433 | 0.013046 | 0.51042 | 0.10056 | 0.026511 | 0.0099313 | -0.025022 | -0.025274 | 0.0073242 | -8.7654e-05 | 0.041321 | 0.13633 | 0.42583 | 0.017581 | 0.79651 | 0.74158 | -2.9343 | 0.70953 | 0.81024 | 0.64087 | 0.47607 | -10.8124 | -48.9029 | -84.6085 | 0.76446 | 0.79651 | -121.0876 | -121.3577 | 121.8887 | 121.7239 | -0.064087 | 121.9894 | 121.9574 | 0.23346 | -0.07782 | 0.16022 | -0.10986 | -0.10986 | 110.4355 | 36.6394 | 36.7493 | -0.07782 | 122.0581 | 122.0444 | 118.3136 | -0.39826 | 122.0123 | 122.0444 | 72.345 | -122.2321
1442.0469 | 122.1451 | -119.87 | 2.0782 | 0.013046 | 1.6001 | 0.12662 | 0.024802 | 0.0073679 | -0.021176 | -0.025487 | 0.0073242 | 0.0016213 | 0.042603 | 0.14787 | 1.5277 | 0.019717 | 1.9455 | 1.6617 | -2.0187 | 1.5793 | 2.005 | 1.593 | 1.4511 | -0.50354 | -47.8958 | -71.3882 | 2.0142 | 2.0187 | -119.5908 | -119.8654 | 121.463 | 121.3211 | -0.073242 | 121.5317 | 121.4493 | 0.12817 | -0.13275 | 0.27924 | 0.004578 | -0.064087 | 119.3665 | 48.4818 | 48.4772 | -0.059509 | 121.875 | 121.8155 | 117.8513 | -0.62714 | 121.8842 | 121.8887 | 71.9742 | -121.9437
1443.7656 | 122.1588 | -121.2021 | 0.75531 | 0.020676 | 0.52067 | 0.10227 | 0.028647 | 0.0065133 | -0.026944 | -0.026983 | -0.0003053 | 0.0014077 | 0.042603 | 0.1453 | 0.4207 | 0.022067 | 0.70038 | 0.62714 | -3.1174 | 0.62714 | 0.75531 | 0.59052 | 0.45319 | -0.50812 | -56.9687 | -127.6886 | 0.65918 | 0.73242 | -121.0098 | -121.3257 | 121.7926 | 121.6553 | 0 | 121.8292 | 121.8292 | 0.17395 | -0.054932 | 0.19226 | -0.1236 | -0.09613 | 120.694 | -6.4865 | -6.3629 | -0.022888 | 121.9574 | 121.9025 | 118.0847 | -0.30212 | 121.8613 | 121.9345 | 64.2334 | -122.081
1445.5469 | 121.9299 | -118.9453 | 2.8702 | -0.0022127 | 2.4247 | 0.14905 | 0.027365 | 0.0090769 | -0.025235 | -0.030401 | -0.0003053 | -0.0017965 | 0.044525 | 0.15727 | 2.3598 | 0.022922 | 2.655 | 2.3071 | -0.99335 | 2.1515 | 2.6505 | 2.1606 | 2.0279 | -4.2892 | -52.272 | -42.9565 | 2.774 | 2.8015 | -118.5928 | -118.8858 | 121.106 | 120.9732 | -0.21973 | 121.2524 | 121.0968 | 0.1236 | -0.21515 | 0.35248 | 0.059509 | -0.09613 | 114.6561 | 75.9888 | 75.9293 | -0.068664 | 121.5958 | 121.6003 | 117.952 | -0.84228 | 121.7194 | 121.7468 | 66.6733 | -121.756
1447.3281 | 121.8292 | -119.0826 | 2.6871 | -0.0022127 | 2.307 | 0.15055 | 0.02886 | 0.0095041 | -0.025022 | -0.024633 | 0.0073242 | -0.0013693 | 0.047943 | 0.23289 | 2.1622 | 0.023135 | 2.504 | 2.1973 | -1.799 | 2.0462 | 2.4994 | 2.0096 | 1.886 | -3.0075 | -53.7689 | -53.9978 | 2.5772 | 2.6093 | -118.7851 | -119.0414 | 121.0922 | 120.9686 | -0.18768 | 121.2799 | 121.1288 | 0.16022 | -0.18311 | 0.29755 | 0.041199 | -0.10986 | 116.0751 | 65.0848 | 65.0436 | -0.07782 | 121.582 | 121.5866 | 117.2836 | -0.80109 | 121.6599 | 121.6919 | 65.3137 | -121.7285
1449.0469 | 121.907 | -119.1467 | 2.5269 | 0.013046 | 2.1728 | 0.15247 | 0.02822 | 0.0077951 | -0.026731 | -0.029546 | -0.0003053 | 0.00012615 | 0.045594 | 0.35059 | 1.9169 | 0.026767 | 2.3346 | 2.0416 | -2.3712 | 1.918 | 2.3529 | 1.886 | 1.7532 | -2.5223 | -52.0157 | -34.7534 | 2.4307 | 2.4673 | -118.8812 | -119.1513 | 121.0327 | 120.9 | -0.17395 | 121.1884 | 121.0648 | 0.16479 | -0.19226 | 0.2655 | -0.004577 | -0.09613 | 116.6245 | 84.3933 | 84.3979 | -0.059509 | 121.4996 | 121.4813 | 116.7755 | -0.77362 | 121.5775 | 121.6141 | 67.131 | -121.6782
1450.8281 | 121.6049 | -117.9977 | 3.6484 | 0.0054168 | 3.2089 | 0.19584 | 0.030783 | 0.011213 | -0.024594 | -0.027837 | 0.0073242 | 0.0011941 | 0.047516 | 1.4302 | 2.0318 | 0.030826 | 3.3051 | 2.774 | -1.6891 | 2.6321 | 3.2913 | 2.6047 | 2.4719 | -2.8519 | -51.5991 | -65.2359 | 3.5843 | 3.6072 | -117.6041 | -117.8925 | 120.6024 | 120.4697 | -0.35705 | 120.7718 | 120.6299 | 0.16022 | -0.34332 | 0.39368 | 0.10529 | -0.064086 | 115.1459 | 52.7618 | 52.6566 | -0.041198 | 121.2891 | 121.3028 | 116.3086 | -1.1765 | 121.582 | 121.6049 | 66.3986 | -121.5408
1452.5938 | 121.7056 | -118.9819 | 2.6642 | 0.0054168 | 2.4881 | 0.16016 | 0.027579 | 0.0092905 | -0.016904 | -0.026769 | -0.0003053 | 0.0029031 | 0.04773 | 0.16923 | 2.4097 | 0.033389 | 2.4719 | 2.0782 | -1.0483 | 1.9867 | 2.4811 | 1.9226 | 1.799 | -2.0874 | -57.8567 | -33.371 | 2.5864 | 2.6321 | -118.6752 | -118.927 | 120.9045 | 120.7809 | -0.18311 | 121.0602 | 120.9686 | 0.18768 | -0.19226 | 0.3067 | 0.054932 | -0.07782 | 116.8945 | 85.611 | 85.556 | -0.032044 | 121.463 | 121.4539 | 117.9337 | -0.86517 | 121.5683 | 121.6141 | 61.1252 | -121.5912
1454.375 | 121.7377 | -118.9453 | 2.6688 | -0.0022127 | 2.4758 | 0.16892 | 0.02587 | 0.014204 | -0.021817 | -0.031469 | 0.014954 | 0.0014077 | 0.05008 | 0.17179 | 2.3779 | 0.054324 | 2.3575 | 2.0187 | -2.0325 | 1.9501 | 2.4857 | 1.8906 | 1.7487 | -3.3691 | -68.2709 | -40.5075 | 2.5681 | 2.6093 | -118.689 | -118.9407 | 120.8359 | 120.694 | -0.18311 | 120.9641 | 120.8954 | 0.20142 | -0.31128 | 0.25635 | 0.004577 | -0.10071 | 115.5762 | 78.4378 | 78.4332 | -0.059509 | 121.431 | 121.3028 | 116.9128 | -0.92011 | 121.5134 | 121.5546 | 50.6744 | -121.6095
1456.1562 | 121.6919 | -118.9453 | 2.5955 | 0.013046 | 2.4542 | 0.17789 | 0.025229 | 0.019972 | -0.026303 | -0.03745 | 0.0073242 | 0.0082437 | 0.048584 | 0.17457 | 2.3412 | 0.089359 | 2.4353 | 2.1286 | -6.1798 | 1.9684 | 2.4124 | 1.8814 | 1.7578 | -2.8976 | -70.5414 | -43.7622 | 2.5131 | 2.5497 | -118.6386 | -118.8904 | 120.8267 | 120.7031 | -0.1831 | 121.0739 | 120.9137 | 0.21057 | -0.16022 | 0.3067 | 0.054931 | -0.082397 | 116.0477 | 75.1831 | 75.1282 | -0.045776 | 121.3577 | 121.3806 | 112.7655 | -0.83771 | 121.4584 | 121.4951 | 48.4039 | -121.4859
1457.9219 | 121.7514 | -119.0964 | 2.4261 | -0.0098417 | 2.3145 | 0.21934 | 0.026511 | 0.022108 | -0.022031 | -0.041509 | -0.0003053 | 0.011235 | 0.055207 | 0.27946 | 2.1735 | 0.16028 | 2.1744 | 1.8311 | -14.7995 | 1.7532 | 2.3026 | 1.6479 | 1.506 | -1.8951 | -67.6941 | -47.4472 | 2.4353 | 2.4628 | -118.8354 | -119.0918 | 120.7443 | 120.6024 | -0.1236 | 120.9274 | 120.8496 | 0.24719 | -0.25177 | 0.26093 | 0.004578 | 0.009156 | 117.2012 | 71.6492 | 71.6446 | 0.036622 | 121.3989 | 121.2708 | 104.2969 | -0.9201 | 121.5317 | 121.5591 | 51.4023 | -121.5179
1459.7031 | 121.637 | -119.6274 | 1.9089 | 0.0054168 | 1.7379 | 0.16678 | 0.029501 | 0.018903 | -0.022458 | -0.03745 | 0.0073242 | 1.2052 | 0.05008 | 0.40421 | 2.5001 | 0.14875 | 1.6388 | 1.4053 | -21.3593 | 1.3641 | 1.7761 | 1.2543 | 1.1261 | -1.9318 | -58.6029 | -33.7509 | 1.7303 | 1.7624 | -119.3115 | -119.5358 | 120.8817 | 120.7535 | -0.13275 | 121.0327 | 120.9915 | 0.23804 | -0.27008 | 0.31586 | 0.091552 | -0.17853 | 117.6956 | 85.8765 | 85.7849 | -0.14649 | 121.4035 | 121.2662 | 98.2681 | -0.78278 | 121.3577 | 121.3898 | 61.0245 | -121.4447
1461.4375 | 121.4859 | -119.8196 | 1.6754 | -0.0022127 | 1.4237 | 0.69422 | 0.029074 | 0.01164 | -0.026944 | -0.031682 | 0.0073242 | 1.3641 | 0.049225 | 0.25147 | 2.4933 | 0.72809 | 1.3596 | 1.2268 | -6.6559 | 1.1765 | 1.5289 | 1.1627 | 1.03 | -2.4765 | -54.2633 | -35.376 | 1.5015 | 1.506 | -119.4305 | -119.7098 | 120.9824 | 120.8496 | -0.14648 | 121.0464 | 120.9961 | 0.14648 | -0.31586 | 0.3891 | 0.10986 | -0.17395 | 117.3431 | 84.4437 | 84.3338 | -0.16937 | 121.3486 | 121.1792 | 113.1638 | -0.64545 | 121.3211 | 121.3257 | 65.5563 | -121.3852
1463.2188 | 121.344 | -120.4697 | 0.86975 | 0.0054168 | 0.62193 | 1.0078 | 0.024802 | 0.0052317 | -0.020108 | -0.025915 | 0.0073242 | 3.2015 | 0.052429 | 1.1299 | 2.5665 | 1.0295 | 0.57678 | 0.59052 | -1.8768 | 0.59509 | 0.77362 | 0.54474 | 0.41657 | -1.1398 | -60.8139 | -33.7097 | 0.51727 | 0.54932 | -120.0256 | -120.2728 | 121.0144 | 120.8862 | -0.09613 | 121.0602 | 121.0648 | 0.17853 | -0.29297 | 0.44403 | 0.19684 | -0.35248 | 119.3298 | 86.7599 | 86.5631 | -0.32044 | 121.2433 | 121.0464 | 118.5928 | -0.45319 | 120.9869 | 121.019 | 59.6558 | -121.1426
1465 | 121.3623 | -118.8675 | 2.3117 | 0.013046 | 2.1094 | 0.17042 | 0.026938 | 0.026167 | -0.027158 | -0.048345 | -0.0003053 | 3.3147 | 0.054352 | 3.186 | 2.1771 | 0.18784 | 2.1561 | 1.8951 | -25.0626 | 1.7624 | 2.1423 | 1.6067 | 1.4648 | -1.68 | -59.5963 | -50.1709 | 1.9547 | 1.9867 | -118.3365 | -118.5974 | 120.4742 | 120.3323 | -0.16937 | 120.7626 | 120.6299 | 0.29755 | -0.15564 | 0.53101 | 0.27008 | -0.35706 | 117.1875 | 68.6966 | 68.4265 | -0.32501 | 121.0098 | 121.0236 | 93.8049 | -0.84686 | 120.8221 | 120.8542 | 59.2712 | -120.9091
1466.7188 | 121.701 | -121.4401 | 0.13275 | -0.0022127 | 0.033611 | 0.088171 | 0.03121 | 0.0084361 | -0.029508 | -0.025915 | -0.0003053 | 0.032597 | -0.029815 | -0.0085065 | -0.0082544 | 0.011173 | 0.13275 | 0.20599 | 0.17853 | 0.19226 | 0.15106 | 0.10986 | -0.036621 | 0.09613 | 0.17395 | 0.073242 | 0.045776 | 0.059509 | 0.07782 | -0.018311 | 121.55 | 121.4035 | 0.018311 | 121.6461 | 121.6324 | 0.22888 | 0 | 121.5179 | 121.4218 | -0.086975 | 121.5363 | 121.5134 | 0.091553 | -0.073242 | 121.5912 | 121.5729 | 121.6187 | -0.16937 | 121.4859 | 121.4996 | 121.6141 | -0.15106
1468.5 | 121.7239 | -121.5454 | 0.16937 | 0.013046 | 0.030834 | 0.085394 | 0.029501 | 0.0048045 | -0.021604 | -0.023778 | 0.0073242 | 0.037083 | -0.029175 | -0.0061567 | -0.0093226 | 0.0090363 | 0.045776 | 0.050354 | 0.064087 | 0.10529 | 0.19226 | 0.059509 | -0.068665 | -0.018311 | 0.027466 | -0.086975 | 0.10529 | 0.11902 | 0.054932 | -0.036621 | 121.6049 | 121.4767 | 0.022888 | 121.5958 | 121.6507 | 0.17395 | -0.1236 | 121.6003 | 121.5088 | -0.064087 | 121.5271 | 121.4584 | -0.050354 | -0.050354 | 121.7377 | 121.5912 | 121.6095 | -0.23804 | 121.6507 | 121.6644 | 121.5729 | -0.20599
1470.2812 | 121.8109 | -121.582 | 0.13733 | 0.020676 | 0.038738 | 0.082403 | 0.024802 | 0.0056589 | -0.022458 | -0.02271 | 0.0073242 | 0.039219 | -0.029602 | -0.0057293 | -0.0061182 | 0.0077545 | 0.054932 | -0.004578 | 0.054932 | 0.10529 | 0.20599 | 0.050354 | -0.064087 | 0.013733 | 0 | -0.07782 | 0.10071 | 0.13733 | 0.068665 | -0.018311 | 121.6324 | 121.5179 | 0.068665 | 121.5775 | 121.6873 | 0.16937 | -0.082397 | 121.6507 | 121.5637 | -0.036621 | 121.5958 | 121.5042 | -0.059509 | 0 | 121.788 | 121.637 | 121.637 | -0.20142 | 121.6827 | 121.7194 | 121.582 | -0.15564
1472 | 121.8704 | -121.5271 | 0.21515 | 0.0054168 | 0.11393 | 0.088812 | 0.025229 | 0.0037363 | -0.029294 | -0.026769 | -0.0003053 | 0.040928 | -0.030456 | -0.0093609 | -0.0082544 | 0.0116 | 0.17395 | 0.1831 | 0.21515 | 0.21973 | 0.21973 | 0.16022 | 0.045776 | 0.13275 | 0.16937 | 0.07782 | 0.13275 | 0.17395 | 0.17395 | 0.082397 | 121.6873 | 121.5729 | 0.004578 | 121.7102 | 121.7468 | 0.17395 | -0.041199 | 121.7011 | 121.6095 | -0.082398 | 121.6599 | 121.6049 | -0.004577 | -0.041199 | 121.7468 | 121.7011 | 121.7422 | -0.16937 | 121.6599 | 121.7011 | 121.6965 | -0.13275
1473.7812 | 121.8979 | -121.55 | 0.19226 | -0.0098417 | 0.093853 | 0.084966 | 0.027365 | 0.0043771 | -0.026517 | -0.025487 | -0.0003053 | 0.03986 | -0.029815 | -0.010215 | -0.0074 | 0.0096771 | 0.21973 | 0.21057 | 0.25177 | 0.21973 | 0.1831 | 0.16479 | 0.032043 | 0.16479 | 0.19684 | 0.1236 | 0.10529 | 0.13275 | 0.15106 | 0.073242 | 121.7148 | 121.582 | -0.009156 | 121.7606 | 121.7697 | 0.18768 | 0.027466 | 121.701 | 121.6232 | -0.086975 | 121.7148 | 121.6736 | 0.050354 | -0.05951 | 121.7331 | 121.7697 | 121.8018 | -0.16022 | 121.6553 | 121.6827 | 121.7468 | -0.11902
1475.5 | 121.875 | -121.3028 | 0.49439 | 0.0054168 | 0.32884 | 0.094793 | 0.026297 | 0.0037363 | -0.022885 | -0.023778 | 0.014954 | 0.072117 | -0.030883 | -0.0087201 | -0.0048364 | 0.0077545 | 0.40741 | 0.3479 | 0.39368 | 0.39368 | 0.50812 | 0.35248 | 0.21057 | 0.39368 | 0.3891 | 0.32044 | 0.45319 | 0.44861 | 0.38452 | 0.32044 | 121.6553 | 121.5134 | 0.013733 | 121.6507 | 121.6965 | 0.18311 | -0.086975 | 121.6873 | 121.6232 | -0.041199 | 121.6965 | 121.6232 | 0 | -0.045777 | 121.8109 | 121.7102 | 121.6965 | -0.28381 | 121.756 | 121.7514 | 121.6919 | -0.17395
1477.2656 | 121.8704 | -121.1197 | 0.6546 | -0.0022127 | 0.46257 | 0.10462 | 0.027579 | 0.0065133 | -0.023099 | -0.02271 | 0.0073242 | 0.088566 | -0.029815 | -0.0085065 | -0.0046228 | 0.0073273 | 0.52185 | 0.46234 | 0.53558 | 0.48523 | 0.64545 | 0.44403 | 0.3067 | 0.48523 | 0.49439 | 0.43488 | 0.57678 | 0.59967 | 0.52643 | 0.45319 | 121.5637 | 121.4264 | -0.009155 | 121.582 | 121.6049 | 0.17853 | -0.13275 | 121.6461 | 121.5729 | -0.07782 | 121.6049 | 121.5546 | -0.018311 | -0.054932 | 121.7651 | 121.6415 | 121.6553 | -0.3479 | 121.6965 | 121.7194 | 121.6141 | -0.20142
1479.0469 | 121.8384 | -121.0327 | 0.74158 | 0.013046 | 0.52409 | 0.12427 | 0.02822 | 0.0056589 | -0.021817 | -0.025274 | 0.0073242 | 0.098179 | -0.028106 | -0.0040203 | -0.0054772 | 0.010745 | 0.58136 | 0.48523 | 0.57678 | 0.52643 | 0.73242 | 0.52185 | 0.38452 | 0.56763 | 0.52185 | 0.48523 | 0.67749 | 0.68207 | 0.62256 | 0.54016 | 121.5546 | 121.4172 | -0.009155 | 121.5179 | 121.5591 | 0.14191 | -0.16022 | 121.6553 | 121.5729 | -0.064087 | 121.6003 | 121.5179 | -0.054932 | -0.059509 | 121.7651 | 121.6141 | 121.6095 | -0.35706 | 121.7102 | 121.7148 | 121.5546 | -0.20142
1480.7656 | 121.9574 | -120.9641 | 0.7782 | 0.013046 | 0.5587 | 0.15226 | 0.027365 | 0.0067271 | -0.032071 | -0.025487 | 0.014954 | 0.097752 | -0.030243 | -0.0074383 | -0.0076136 | 0.011173 | 0.65918 | 0.65002 | 0.72784 | 0.60883 | 0.74616 | 0.59967 | 0.4715 | 0.64087 | 0.67291 | 0.64087 | 0.70953 | 0.737 | 0.69122 | 0.60425 | 121.5637 | 121.4355 | -0.032043 | 121.6141 | 121.5729 | 0.13733 | -0.11902 | 121.6553 | 121.5683 | -0.068664 | 121.6049 | 121.6049 | 0.036621 | -0.041198 | 121.7102 | 121.6232 | 121.6919 | -0.3067 | 121.6736 | 121.701 | 121.637 | -0.17395
1482.5469 | 121.843 | -120.9732 | 0.80109 | 0.020676 | 0.54011 | 0.17148 | 0.026511 | 0.0050181 | -0.022458 | -0.02506 | 0.0073242 | 0.099247 | -0.027679 | -0.0063703 | -0.0052636 | 0.010318 | 0.6546 | 0.57678 | 0.66834 | 0.5722 | 0.81482 | 0.56305 | 0.44403 | 0.6134 | 0.6134 | 0.58136 | 0.75989 | 0.75073 | 0.69122 | 0.59509 | 121.5363 | 121.4172 | 0.013733 | 121.55 | 121.5454 | 0.12817 | -0.14648 | 121.6644 | 121.5683 | -0.041198 | 121.5866 | 121.5546 | -0.013733 | -0.050354 | 121.788 | 121.6278 | 121.6415 | -0.35705 | 121.7331 | 121.7239 | 121.5866 | -0.20599
1484.2656 | 121.8796 | -120.9732 | 0.80109 | 0.0054168 | 0.53199 | 0.18708 | 0.030356 | 0.0058725 | -0.02609 | -0.028905 | 0.0073242 | 0.10032 | -0.029388 | -0.0095745 | -0.0086816 | 0.010532 | 0.76446 | 0.73242 | 0.8194 | 0.68207 | 0.75073 | 0.63171 | 0.50812 | 0.72327 | 0.76904 | 0.70496 | 0.71869 | 0.71869 | 0.71869 | 0.64087 | 121.6049 | 121.4813 | -0.050354 | 121.7056 | 121.6553 | 0.17395 | -0.036621 | 121.6919 | 121.6141 | -0.082397 | 121.6965 | 121.6782 | 0.064087 | -0.082397 | 121.7239 | 121.7377 | 121.7926 | -0.29297 | 121.6919 | 121.6919 | 121.7422 | -0.16022
1486.0312 | 121.8475 | -120.9732 | 0.8194 | 0.020676 | 0.51341 | 0.2063 | 0.027792 | 0.0048045 | -0.026517 | -0.024847 | 0.0073242 | 0.096256 | -0.030243 | -0.0089337 | -0.0074 | 0.0083953 | 0.76446 | 0.72327 | 0.80109 | 0.67749 | 0.76904 | 0.63171 | 0.50354 | 0.737 | 0.75531 | 0.70953 | 0.6958 | 0.75531 | 0.73242 | 0.64087 | 121.6049 | 121.4767 | -0.050354 | 121.6965 | 121.6507 | 0.17395 | -0.054932 | 121.7056 | 121.6141 | -0.1236 | 121.7102 | 121.6827 | 0.068665 | -0.064087 | 121.7422 | 121.7377 | 121.7743 | -0.31586 | 121.669 | 121.7285 | 121.7285 | -0.17853
1487.75 | 121.8613 | -120.9412 | 0.85144 | 0.0054168 | 0.49546 | 0.21912 | 0.029074 | 0.0069407 | -0.022244 | -0.025487 | 0.014954 | 0.10074 | -0.02832 | -0.0082929 | -0.0048364 | 0.0090363 | 0.68207 | 0.62256 | 0.67749 | 0.6134 | 0.84228 | 0.6134 | 0.48981 | 0.65918 | 0.64545 | 0.58136 | 0.79651 | 0.80566 | 0.70953 | 0.63629 | 121.5546 | 121.431 | -0.009155 | 121.5637 | 121.5546 | 0.1236 | -0.16937 | 121.6507 | 121.5775 | -0.054931 | 121.6003 | 121.5225 | -0.054932 | -0.045776 | 121.7834 | 121.6232 | 121.6187 | -0.36163 | 121.7377 | 121.7468 | 121.5866 | -0.21515
1489.5469 | 121.8201 | -120.9412 | 0.85602 | 0.0054168 | 0.48542 | 0.22938 | 0.027152 | 0.0067271 | -0.026303 | -0.025701 | -0.0003053 | 0.099888 | -0.027893 | -0.0061567 | -0.0069726 | 0.010318 | 0.74158 | 0.6958 | 0.74616 | 0.65918 | 0.81482 | 0.65918 | 0.50812 | 0.67749 | 0.68665 | 0.63629 | 0.78735 | 0.8194 | 0.73242 | 0.65918 | 121.6003 | 121.4493 | -0.041199 | 121.637 | 121.6003 | 0.15106 | -0.11444 | 121.6736 | 121.6003 | -0.068664 | 121.6187 | 121.5775 | -0.022888 | -0.036621 | 121.756 | 121.6827 | 121.6873 | -0.3479 | 121.7285 | 121.7606 | 121.6278 | -0.19684
1491.3281 | 121.8658 | -120.932 | 0.87891 | 0.0054168 | 0.47389 | 0.23493 | 0.029501 | 0.0092905 | -0.021817 | -0.022283 | -0.0003053 | 0.09882 | -0.02832 | -0.0059429 | -0.0044092 | 0.0069001 | 0.71411 | 0.64545 | 0.72327 | 0.66834 | 0.82398 | 0.63629 | 0.48065 | 0.72327 | 0.69122 | 0.64545 | 0.81024 | 0.80566 | 0.737 | 0.66834 | 121.5683 | 121.4127 | -0.054931 | 121.5775 | 121.6003 | 0.18768 | -0.16479 | 121.669 | 121.6003 | -0.068664 | 121.6553 | 121.5775 | -0.022888 | -0.073242 | 121.756 | 121.6461 | 121.6553 | -0.39825 | 121.7422 | 121.7377 | 121.6232 | -0.21057
1493.0312 | 121.9345 | -120.9045 | 0.82855 | -0.0022127 | 0.47367 | 0.24497 | 0.024161 | 0.0060861 | -0.022244 | -0.026556 | 0.0073242 | 0.097325 | -0.028106 | -0.0046613 | -0.00505 | 0.0090363 | 0.71411 | 0.6134 | 0.68665 | 0.62256 | 0.83771 | 0.64545 | 0.50354 | 0.71411 | 0.62714 | 0.62714 | 0.80109 | 0.8194 | 0.73242 | 0.6546 | 121.55 | 121.4081 | 0.009156 | 121.5179 | 121.5271 | 0.11902 | -0.11444 | 121.637 | 121.5591 | -0.027466 | 121.6187 | 121.5317 | -0.027466 | -0.009155 | 121.7422 | 121.6187 | 121.5912 | -0.32501 | 121.7056 | 121.7239 | 121.5317 | -0.17395
1494.8125 | 121.962 | -120.8908 | 0.81482 | -0.0022127 | 0.47474 | 0.25266 | 0.022879 | 0.0073679 | -0.024167 | -0.02271 | -0.0003053 | 0.090489 | -0.02832 | -0.0078657 | -0.0035546 | 0.0092499 | 0.72784 | 0.65002 | 0.72784 | 0.64087 | 0.81024 | 0.65002 | 0.50812 | 0.75989 | 0.70496 | 0.70496 | 0.77362 | 0.7782 | 0.75989 | 0.67749 | 121.5408 | 121.3989 | -0.004577 | 121.5408 | 121.5317 | 0.13275 | -0.086975 | 121.6507 | 121.5683 | -0.041198 | 121.6507 | 121.5958 | 0.027466 | -0.036621 | 121.7011 | 121.6187 | 121.6187 | -0.3067 | 121.6644 | 121.669 | 121.5958 | -0.13733
1496.6094 | 121.8338 | -120.9229 | 0.84686 | 0.013046 | 0.46064 | 0.25586 | 0.023306 | 0.0062997 | -0.022672 | -0.022924 | 0.0073242 | 0.093479 | -0.032165 | -0.0065839 | -0.002273 | 0.010318 | 0.67749 | 0.58136 | 0.67291 | 0.61798 | 0.85602 | 0.62714 | 0.49896 | 0.70496 | 0.6134 | 0.59509 | 0.79651 | 0.80566 | 0.74158 | 0.66834 | 121.55 | 121.4218 | 0.009155 | 121.5042 | 121.5408 | 0.11902 | -0.16937 | 121.6644 | 121.5912 | -0.050354 | 121.6278 | 121.5179 | -0.073242 | -0.041199 | 121.7789 | 121.6003 | 121.5958 | -0.3479 | 121.7194 | 121.7285 | 121.5363 | -0.17853
1498.3906 | 121.907 | -120.9457 | 0.83313 | 0.013046 | 0.46769 | 0.26398 | 0.028006 | 0.0060861 | -0.030362 | -0.023778 | 0.022583 | 0.085575 | -0.030883 | -0.01107 | -0.006759 | 0.010745 | 0.75531 | 0.71869 | 0.75531 | 0.65002 | 0.79651 | 0.67291 | 0.53101 | 0.71411 | 0.73242 | 0.70953 | 0.75531 | 0.79193 | 0.74616 | 0.67749 | 121.6187 | 121.4767 | -0.036621 | 121.6644 | 121.5958 | 0.11902 | -0.07782 | 121.6919 | 121.6232 | -0.07782 | 121.6599 | 121.6553 | 0.032044 | -0.041199 | 121.7422 | 121.701 | 121.701 | -0.30212 | 121.701 | 121.7377 | 121.6782 | -0.15564
1500.1562 | 121.9574 | -120.8817 | 0.83313 | 0.0054168 | 0.46363 | 0.2706 | 0.029288 | 0.0041635 | -0.030789 | -0.027837 | 0.014954 | 0.08408 | -0.032165 | -0.0089337 | -0.008468 | 0.010318 | 0.7782 | 0.76446 | 0.83313 | 0.6958 | 0.80109 | 0.67291 | 0.53558 | 0.79193 | 0.82855 | 0.77362 | 0.75989 | 0.7782 | 0.78278 | 0.68665 | 121.5546 | 121.4172 | -0.032044 | 121.6461 | 121.5775 | 0.16022 | -0.054932 | 121.6644 | 121.5683 | -0.073242 | 121.6736 | 121.6553 | 0.086975 | -0.054932 | 121.6827 | 121.6599 | 121.7148 | -0.29755 | 121.6415 | 121.6599 | 121.7102 | -0.14648
1501.8594 | 121.8155 | -120.9229 | 0.87433 | 0.013046 | 0.46577 | 0.27701 | 0.030997 | 0.0054453 | -0.025662 | -0.026128 | 0.014954 | 0.071263 | -0.028106 | -0.0095745 | -0.0074 | 0.010104 | 0.80109 | 0.75531 | 0.8194 | 0.70496 | 0.81024 | 0.64545 | 0.54016 | 0.75989 | 0.78278 | 0.72784 | 0.76446 | 0.78278 | 0.76446 | 0.65918 | 121.5683 | 121.463 | -0.064087 | 121.6782 | 121.6278 | 0.1648 | -0.073243 | 121.6873 | 121.582 | -0.10986 | 121.6827 | 121.6507 | 0.068664 | -0.091553 | 121.7331 | 121.7239 | 121.7422 | -0.33417 | 121.6873 | 121.7056 | 121.7056 | -0.21515
1503.6406 | 121.907 | -120.9 | 0.83771 | 0.013046 | 0.46791 | 0.28107 | 0.027579 | 0.0030955 | -0.02908 | -0.024847 | 0.022583 | 0.06934 | -0.028534 | -0.0080793 | -0.0086816 | 0.0066863 | 0.72327 | 0.70953 | 0.75073 | 0.65918 | 0.81482 | 0.67291 | 0.52643 | 0.75073 | 0.72784 | 0.70496 | 0.75989 | 0.77362 | 0.78278 | 0.6958 | 121.5729 | 121.4264 | -0.022889 | 121.6095 | 121.5591 | 0.13275 | -0.11444 | 121.6827 | 121.5958 | -0.07782 | 121.6507 | 121.6049 | 0.009155 | -0.064087 | 121.7148 | 121.6232 | 121.6507 | -0.31128 | 121.6599 | 121.6736 | 121.6278 | -0.14191
1505.4219 | 121.8613 | -120.932 | 0.85144 | 0.0054168 | 0.45082 | 0.28107 | 0.030142 | 0.0058725 | -0.022458 | -0.026983 | 0.014954 | 0.083012 | -0.028747 | -0.0095745 | -0.0024866 | 0.0056183 | 0.71411 | 0.63171 | 0.67291 | 0.62256 | 0.83313 | 0.63171 | 0.48065 | 0.70038 | 0.70496 | 0.63629 | 0.79651 | 0.79651 | 0.75073 | 0.66376 | 121.5637 | 121.4127 | -0.01831 | 121.5637 | 121.5546 | 0.14191 | -0.13733 | 121.6827 | 121.5958 | -0.054931 | 121.6324 | 121.5683 | -0.027465 | -0.054931 | 121.7651 | 121.6461 | 121.6049 | -0.37079 | 121.7285 | 121.7285 | 121.637 | -0.18768
1507.1875 | 121.8933 | -120.8817 | 0.85602 | 0.013046 | 0.45402 | 0.28599 | 0.026938 | 0.0041635 | -0.027799 | -0.02506 | 0.0073242 | 0.081089 | -0.03067 | -0.0091473 | -0.0052636 | 0.0077545 | 0.79651 | 0.79651 | 0.82398 | 0.70953 | 0.81482 | 0.64545 | 0.51727 | 0.82398 | 0.84686 | 0.78735 | 0.75989 | 0.77362 | 0.7782 | 0.70496 | 121.5271 | 121.3989 | -0.041199 | 121.6782 | 121.5912 | 0.19226 | -0.059509 | 121.6599 | 121.5866 | -0.09613 | 121.7056 | 121.669 | 0.082398 | -0.082397 | 121.6965 | 121.6782 | 121.7056 | -0.33874 | 121.6415 | 121.6553 | 121.7285 | -0.15106
1508.9844 | 121.9666 | -120.8405 | 0.84686 | -0.0022127 | 0.4506 | 0.28855 | 0.027365 | 0.0052317 | -0.026517 | -0.026342 | 0.014954 | 0.079594 | -0.030243 | -0.0089337 | -0.0071862 | 0.0092499 | 0.75531 | 0.75531 | 0.78735 | 0.70038 | 0.82398 | 0.66834 | 0.50354 | 0.80109 | 0.80566 | 0.7782 | 0.78278 | 0.78735 | 0.79193 | 0.71869 | 121.5088 | 121.344 | -0.022888 | 121.5958 | 121.5408 | 0.19684 | -0.091553 | 121.6324 | 121.5591 | -0.064087 | 121.6415 | 121.6187 | 0.059509 | -0.059509 | 121.6644 | 121.5958 | 121.6278 | -0.34332 | 121.6232 | 121.6278 | 121.6461 | -0.12817
1510.7656 | 121.8658 | -120.8725 | 0.87433 | 0.0054168 | 0.4365 | 0.28898 | 0.029074 | 0.0030955 | -0.021176 | -0.022497 | -0.0079343 | 0.083653 | -0.028534 | -0.0050885 | -0.003982 | 0.0049775 | 0.77362 | 0.6958 | 0.73242 | 0.69122 | 0.8606 | 0.63629 | 0.47607 | 0.77362 | 0.74616 | 0.67749 | 0.81482 | 0.82855 | 0.78735 | 0.68665 | 121.5088 | 121.3486 | -0.013733 | 121.5683 | 121.5637 | 0.21515 | -0.10071 | 121.6599 | 121.5591 | -0.05951 | 121.6461 | 121.55 | -0.009156 | -0.045777 | 121.7331 | 121.6461 | 121.6049 | -0.39826 | 121.6873 | 121.701 | 121.6187 | -0.18768
1512.5469 | 121.8979 | -120.8633 | 0.84228 | -0.0022127 | 0.44334 | 0.29261 | 0.026083 | 0.0056589 | -0.024594 | -0.020788 | -0.0003053 | 0.078739 | -0.029602 | -0.0055157 | -0.0061182 | 0.0083953 | 0.83771 | 0.78278 | 0.83771 | 0.72327 | 0.81024 | 0.65918 | 0.53101 | 0.8606 | 0.82398 | 0.78735 | 0.77362 | 0.79193 | 0.81482 | 0.737 | 121.5225 | 121.3943 | -0.032043 | 121.6461 | 121.5866 | 0.19226 | -0.004577 | 121.6782 | 121.6003 | -0.068664 | 121.7239 | 121.6507 | 0.050354 | -0.050354 | 121.6736 | 121.7011 | 121.7011 | -0.31128 | 121.637 | 121.6553 | 121.6873 | -0.10528
1514.2656 | 121.8018 | -120.9091 | 0.90179 | -0.0022127 | 0.43373 | 0.30436 | 0.027579 | 0.0043771 | -0.024594 | -0.023351 | 0.0073242 | 0.080876 | -0.028106 | -0.0074383 | -0.0046228 | 0.0077545 | 0.76446 | 0.67749 | 0.76904 | 0.6546 | 0.88806 | 0.64087 | 0.50812 | 0.75989 | 0.74616 | 0.67749 | 0.8606 | 0.87433 | 0.78735 | 0.70496 | 121.55 | 121.4172 | -0.013732 | 121.5866 | 121.5637 | 0.14648 | -0.13733 | 121.6965 | 121.6141 | -0.041198 | 121.669 | 121.5866 | -0.027466 | -0.027465 | 121.7972 | 121.6736 | 121.6782 | -0.39368 | 121.7697 | 121.7834 | 121.6553 | -0.19684
1516.0312 | 121.8842 | -121.5317 | 0.27924 | -0.0098417 | 0.083172 | 0.13025 | 0.028433 | 0.0058725 | -0.022885 | -0.02271 | -0.0003053 | 0.043492 | -0.02832 | -0.0097883 | -0.0046228 | 0.0092499 | 0.1831 | 0.11902 | 0.17395 | 0.21057 | 0.30212 | 0.15106 | 0.018311 | 0.15564 | 0.18768 | 0.082397 | 0.21515 | 0.24261 | 0.21057 | 0.13275 | 121.6827 | 121.55 | 0.022888 | 121.6507 | 121.7422 | 0.19226 | -0.096131 | 121.7422 | 121.6644 | -0.064087 | 121.6873 | 121.6141 | -0.050354 | -0.036621 | 121.8338 | 121.7148 | 121.7056 | -0.26092 | 121.7468 | 121.7743 | 121.7194 | -0.14648
1517.7969 | 121.875 | -121.5363 | 0.30212 | 0.0054168 | 0.086804 | 0.13047 | 0.029074 | 0.0033091 | -0.026517 | -0.023778 | 0.0073242 | 0.038578 | -0.030029 | -0.010215 | -0.0076136 | 0.010959 | 0.26093 | 0.25635 | 0.31586 | 0.29297 | 0.27466 | 0.20142 | 0.086975 | 0.2243 | 0.30212 | 0.16937 | 0.20599 | 0.21973 | 0.23346 | 0.14648 | 121.7377 | 121.6232 | -0.027466 | 121.7926 | 121.8292 | 0.20599 | -0.041199 | 121.7697 | 121.6827 | -0.09613 | 121.7606 | 121.7056 | 0.022889 | -0.082397 | 121.8109 | 121.7972 | 121.8521 | -0.21515 | 121.7422 | 121.756 | 121.8384 | -0.15564
1519.5156 | 122.0078 | -121.5134 | 0.2655 | 0.0054168 | 0.091931 | 0.12769 | 0.026083 | 0.0060861 | -0.022244 | -0.023351 | 0.0073242 | 0.041142 | -0.029602 | -0.0089337 | -0.0052636 | 0.0064727 | 0.31128 | 0.24261 | 0.32959 | 0.30212 | 0.27466 | 0.2243 | 0.086975 | 0.28381 | 0.31128 | 0.21057 | 0.19684 | 0.20599 | 0.25635 | 0.19684 | 121.7377 | 121.6003 | 0.009155 | 121.756 | 121.8155 | 0.21515 | 0.045776 | 121.7697 | 121.7102 | -0.068665 | 121.7972 | 121.7239 | 0.013733 | -0.059509 | 121.788 | 121.8246 | 121.843 | -0.17853 | 121.7102 | 121.7194 | 121.8246 | -0.068665
1521.2969 | 121.8933 | -121.5866 | 0.30212 | -0.0022127 | 0.084026 | 0.1294 | 0.028647 | 0.0060861 | -0.024594 | -0.023138 | 0.014954 | 0.043064 | -0.02832 | -0.0091473 | -0.0054772 | 0.0098907 | 0.24719 | 0.17853 | 0.26093 | 0.24261 | 0.31128 | 0.20142 | 0.064087 | 0.17395 | 0.23804 | 0.11902 | 0.24261 | 0.24719 | 0.23346 | 0.13733 | 121.788 | 121.6507 | 0.009155 | 121.7651 | 121.8292 | 0.17853 | -0.054932 | 121.8201 | 121.7239 | -0.059509 | 121.7606 | 121.7056 | -0.01831 | -0.054932 | 121.8979 | 121.8338 | 121.8475 | -0.23804 | 121.8292 | 121.8338 | 121.8246 | -0.16479
1523.0625 | 122.0444 | -121.5225 | 0.30212 | 0.013046 | 0.091076 | 0.13282 | 0.02587 | 0.0028819 | -0.028226 | -0.023351 | 0.014954 | 0.040074 | -0.032806 | -0.011283 | -0.0076136 | 0.0092499 | 0.25635 | 0.23804 | 0.31586 | 0.28839 | 0.30212 | 0.21973 | 0.086975 | 0.2655 | 0.33875 | 0.24719 | 0.21515 | 0.23804 | 0.27924 | 0.1831 | 121.7422 | 121.6095 | 0 | 121.7606 | 121.8109 | 0.20142 | -0.045776 | 121.8018 | 121.7056 | -0.086975 | 121.788 | 121.7697 | 0.064087 | -0.064087 | 121.8246 | 121.7789 | 121.8384 | -0.21515 | 121.7377 | 121.7606 | 121.8613 | -0.11902
1524.8438 | 122.0261 | -121.5225 | 0.28381 | 0.013046 | 0.085735 | 0.12769 | 0.027152 | 0.0037363 | -0.021604 | -0.021001 | 0.0073242 | 0.048191 | -0.029175 | -0.0050885 | -0.0046228 | 0.0086091 | 0.22888 | 0.10529 | 0.21515 | 0.21515 | 0.33875 | 0.20142 | 0.086975 | 0.20599 | 0.19684 | 0.10986 | 0.25177 | 0.25635 | 0.24719 | 0.16937 | 121.7239 | 121.6095 | 0.054932 | 121.6278 | 121.7377 | 0.12817 | -0.054931 | 121.7697 | 121.6919 | -0.032043 | 121.7285 | 121.6324 | -0.05951 | -0.027465 | 121.8613 | 121.7514 | 121.7377 | -0.19684 | 121.7743 | 121.7789 | 121.7194 | -0.11444
1526.5625 | 121.9894 | -121.5454 | 0.28839 | -0.0022127 | 0.089794 | 0.12876 | 0.021384 | 0.0018137 | -0.025449 | -0.021215 | -0.0003053 | 0.045414 | -0.032592 | -0.0085065 | -0.0041956 | 0.0098907 | 0.3067 | 0.2243 | 0.3479 | 0.28839 | 0.29755 | 0.23804 | 0.11902 | 0.27008 | 0.31586 | 0.23346 | 0.20142 | 0.24261 | 0.2655 | 0.19684 | 121.7834 | 121.6644 | 0.009155 | 121.7697 | 121.8338 | 0.16937 | 0.018311 | 121.8109 | 121.7422 | -0.086975 | 121.8155 | 121.7789 | 0.036621 | -0.045776 | 121.843 | 121.8521 | 121.8933 | -0.16937 | 121.7468 | 121.788 | 121.8613 | -0.091553
1528.3281 | 122.0627 | -121.5179 | 0.28381 | -0.0022127 | 0.089367 | 0.13068 | 0.027152 | 0.0020273 | -0.027585 | -0.024847 | -0.0003053 | 0.046482 | -0.031097 | -0.010643 | -0.0063318 | 0.010532 | 0.26093 | 0.18768 | 0.34332 | 0.30212 | 0.32501 | 0.23346 | 0.1236 | 0.27008 | 0.35248 | 0.23346 | 0.23346 | 0.25177 | 0.28839 | 0.20142 | 121.7514 | 121.6415 | 0.041199 | 121.7056 | 121.8201 | 0.17853 | -0.022888 | 121.8063 | 121.7194 | -0.050354 | 121.788 | 121.7514 | 0.032043 | -0.032043 | 121.843 | 121.7789 | 121.8613 | -0.16022 | 121.7514 | 121.7697 | 121.8704 | -0.082397
1530.0469 | 122.0535 | -121.5546 | 0.28381 | 0.0054168 | 0.084026 | 0.12876 | 0.024374 | 0.0050181 | -0.02374 | -0.021215 | -0.0003053 | 0.053318 | -0.031738 | -0.0091473 | -0.0014184 | 0.0090363 | 0.32959 | 0.21973 | 0.3479 | 0.32501 | 0.3067 | 0.24261 | 0.10529 | 0.31586 | 0.32044 | 0.2243 | 0.2243 | 0.23346 | 0.27466 | 0.18768 | 121.7972 | 121.6599 | 0.022889 | 121.7743 | 121.8796 | 0.21973 | 0.045777 | 121.8292 | 121.7422 | -0.059509 | 121.8704 | 121.7789 | 0.036621 | -0.050354 | 121.8613 | 121.8842 | 121.9025 | -0.17853 | 121.7789 | 121.788 | 121.875 | -0.09613
1531.8125 | 122.0673 | -121.5317 | 0.3067 | -0.0022127 | 0.082318 | 0.12662 | 0.02822 | 0.0045907 | -0.020108 | -0.02271 | 0.0073242 | 0.0546 | -0.02832 | -0.0097883 | -0.0029138 | 0.0086091 | 0.26093 | 0.10529 | 0.25177 | 0.24261 | 0.34332 | 0.23346 | 0.082397 | 0.2655 | 0.24719 | 0.15564 | 0.24719 | 0.25177 | 0.25635 | 0.17395 | 121.7651 | 121.6141 | 0.036621 | 121.637 | 121.7743 | 0.16022 | -0.045777 | 121.788 | 121.7056 | -0.05951 | 121.7972 | 121.6873 | -0.01831 | -0.054932 | 121.875 | 121.7926 | 121.7834 | -0.2243 | 121.7789 | 121.7834 | 121.7789 | -0.13275
1533.5938 | 122.0627 | -121.5546 | 0.3067 | -0.0022127 | 0.087658 | 0.1294 | 0.028433 | 0.0041635 | -0.027585 | -0.023138 | -0.0003053 | 0.051396 | -0.031097 | -0.0097883 | -0.0080408 | 0.012241 | 0.34332 | 0.25177 | 0.37079 | 0.33417 | 0.30212 | 0.23804 | 0.10986 | 0.30212 | 0.38452 | 0.28381 | 0.21057 | 0.25177 | 0.28839 | 0.20599 | 121.7926 | 121.6644 | -0.004578 | 121.8063 | 121.8887 | 0.2243 | 0.036621 | 121.843 | 121.7606 | -0.096131 | 121.8567 | 121.8384 | 0.077819 | -0.054932 | 121.8567 | 121.8979 | 121.9254 | -0.19684 | 121.7651 | 121.8063 | 121.9391 | -0.10071
1535.375 | 122.0856 | -121.5271 | 0.29755 | 0.013046 | 0.082958 | 0.12812 | 0.024374 | 0.0052317 | -0.019681 | -0.021856 | -0.0003053 | 0.056523 | -0.030456 | -0.0078657 | -0.0037684 | 0.0088227 | 0.29755 | 0.15106 | 0.28839 | 0.28381 | 0.33417 | 0.23804 | 0.09613 | 0.29297 | 0.27924 | 0.20142 | 0.24719 | 0.24261 | 0.27924 | 0.20142 | 121.7651 | 121.6232 | 0.036621 | 121.6782 | 121.8109 | 0.18768 | 0 | 121.8063 | 121.7285 | -0.050354 | 121.8201 | 121.7285 | 0 | -0.054931 | 121.8613 | 121.8246 | 121.8155 | -0.20142 | 121.7743 | 121.7697 | 121.8063 | -0.09613
1537.1406 | 121.9528 | -121.5683 | 0.32959 | 0.0054168 | 0.077191 | 0.1247 | 0.026297 | 0.0045907 | -0.021176 | -0.021001 | -0.0003053 | 0.0593 | -0.030883 | -0.0080793 | -0.0035546 | 0.0083953 | 0.22888 | 0.045776 | 0.20599 | 0.23804 | 0.36163 | 0.20142 | 0.07782 | 0.19226 | 0.19226 | 0.10071 | 0.2655 | 0.29755 | 0.25177 | 0.16479 | 121.7697 | 121.6461 | 0.032043 | 121.6141 | 121.8063 | 0.16022 | -0.10071 | 121.8201 | 121.7331 | -0.064087 | 121.7606 | 121.669 | -0.064087 | -0.032044 | 121.9299 | 121.7972 | 121.7743 | -0.25177 | 121.8338 | 121.8658 | 121.7606 | -0.16479
1538.8594 | 122.0901 | -121.5591 | 0.28381 | 0.013046 | 0.0789 | 0.12684 | 0.025229 | 0.0050181 | -0.022244 | -0.020147 | 0.0073242 | 0.056736 | -0.030883 | -0.0072247 | -0.0054772 | 0.0096771 | 0.22888 | 0.086975 | 0.22888 | 0.22888 | 0.32959 | 0.21515 | 0.073242 | 0.23346 | 0.23804 | 0.14648 | 0.22888 | 0.23804 | 0.27466 | 0.18768 | 121.7743 | 121.6324 | 0.045777 | 121.6461 | 121.788 | 0.15564 | -0.054931 | 121.8338 | 121.7468 | -0.054931 | 121.7926 | 121.7056 | -0.041199 | -0.045776 | 121.8887 | 121.788 | 121.788 | -0.21057 | 121.788 | 121.7972 | 121.7972 | -0.09613
1540.6406 | 122.0627 | -121.6003 | 0.29297 | 0.013046 | 0.083599 | 0.12598 | 0.028006 | 0.0035227 | -0.028226 | -0.023351 | 0.0073242 | 0.052891 | -0.03067 | -0.010002 | -0.008468 | 0.012882 | 0.24719 | 0.15564 | 0.29297 | 0.27466 | 0.29755 | 0.23346 | 0.10071 | 0.21973 | 0.2655 | 0.19226 | 0.21515 | 0.23804 | 0.27466 | 0.1831 | 121.8338 | 121.701 | 0.004577 | 121.756 | 121.875 | 0.17395 | -0.045777 | 121.875 | 121.7834 | -0.07782 | 121.8201 | 121.7926 | 0.009156 | -0.054932 | 121.8979 | 121.8475 | 121.8933 | -0.19226 | 121.8155 | 121.8384 | 121.8658 | -0.10986
1542.4219 | 121.994 | -121.6324 | 0.32501 | 0.0054168 | 0.074413 | 0.1309 | 0.029288 | 0.0026681 | -0.022458 | -0.021215 | 0.0073242 | 0.055668 | -0.028106 | -0.0091473 | -0.0080408 | 0.0077545 | 0.20599 | 0.09613 | 0.22888 | 0.21973 | 0.34332 | 0.1831 | 0.059509 | 0.15106 | 0.21515 | 0.10529 | 0.2655 | 0.27466 | 0.23346 | 0.14191 | 121.8155 | 121.6919 | 0.018311 | 121.7285 | 121.8521 | 0.16022 | -0.11902 | 121.8658 | 121.7743 | -0.059509 | 121.7834 | 121.7377 | -0.036621 | -0.050354 | 121.9757 | 121.8384 | 121.8613 | -0.2655 | 121.8979 | 121.907 | 121.8475 | -0.18311
1544.1875 | 121.9528 | -121.6599 | 0.29297 | -0.0022127 | 0.064373 | 0.12086 | 0.028647 | 0.0018137 | -0.019467 | -0.018438 | 0.0073242 | 0.053746 | -0.02832 | -0.0076519 | -0.0035546 | 0.0077545 | 0.23346 | 0.11444 | 0.21973 | 0.23804 | 0.29755 | 0.19684 | 0.059509 | 0.17853 | 0.19684 | 0.054932 | 0.2243 | 0.23346 | 0.21057 | 0.14191 | 121.8567 | 121.7194 | 0.004577 | 121.7743 | 121.8979 | 0.17853 | -0.05951 | 121.8704 | 121.8018 | -0.068665 | 121.8384 | 121.7148 | -0.086975 | -0.05951 | 121.9574 | 121.8933 | 121.8796 | -0.23346 | 121.8842 | 121.8933 | 121.8567 | -0.15106
1545.9844 | 122.1085 | -121.6003 | 0.24719 | -0.0022127 | 0.073773 | 0.12491 | 0.02587 | -0.0090811 | -0.032498 | -0.011816 | 0.014954 | 0.049473 | -0.030883 | -0.0078657 | -0.0074 | 0.011173 | 0.21973 | 0.16937 | 0.27924 | 0.26093 | 0.2655 | 0.19684 | 0.086975 | 0.21057 | 0.29297 | 0.19684 | 0.18768 | 0.20599 | 0.22888 | 0.15564 | 121.7972 | 121.6873 | 0.018311 | 121.7697 | 121.8613 | 0.17395 | -0.027465 | 121.8292 | 121.756 | -0.059509 | 121.8109 | 121.7972 | 0.041198 | -0.041198 | 121.8658 | 121.8201 | 121.8796 | -0.16022 | 121.788 | 121.8063 | 121.8933 | -0.091552
1547.7656 | 121.9666 | -121.669 | 0.27008 | 0.013046 | 0.066937 | 0.12705 | 0.030997 | -0.011645 | -0.023099 | -0.004766 | -0.0003053 | 0.05225 | -0.029388 | -0.0089337 | -0.0069726 | 0.010104 | 0.17853 | 0.091553 | 0.19226 | 0.21057 | 0.29755 | 0.17853 | 0.054932 | 0.1236 | 0.19226 | 0.059509 | 0.23346 | 0.23346 | 0.20142 | 0.10986 | 121.8475 | 121.7239 | 0.027465 | 121.7606 | 121.8796 | 0.15564 | -0.091553 | 121.8704 | 121.7789 | -0.036622 | 121.7926 | 121.7285 | -0.050354 | -0.036622 | 121.9666 | 121.8475 | 121.8613 | -0.21515 | 121.9025 | 121.9025 | 121.8613 | -0.16022
1549.5625 | 121.9757 | -121.6736 | 0.27924 | 0.0054168 | 0.073559 | 0.12534 | 0.028647 | -0.013567 | -0.027371 | -0.0062614 | 0.0073242 | 0.050114 | -0.029388 | -0.010002 | -0.0082544 | 0.011173 | 0.26093 | 0.22888 | 0.3067 | 0.29297 | 0.27008 | 0.21515 | 0.082397 | 0.2243 | 0.30212 | 0.17853 | 0.16022 | 0.19684 | 0.23346 | 0.13733 | 121.8887 | 121.756 | -0.009155 | 121.9025 | 121.9666 | 0.21057 | -0.018311 | 121.907 | 121.8109 | -0.11902 | 121.8979 | 121.8521 | 0.041199 | -0.082398 | 121.9437 | 121.9345 | 121.9803 | -0.19684 | 121.8338 | 121.8704 | 121.9757 | -0.14191
1551.2969 | 122.0078 | -121.7651 | 0.16022 | 0.0054168 | 0.017162 | 0.098211 | 0.026938 | -0.00096352 | -0.02374 | -0.017583 | 0.0073242 | 0.037937 | -0.030029 | -0.0091473 | -0.0035546 | 0.0083953 | 0.07782 | 0.032043 | 0.07782 | 0.13275 | 0.19226 | 0.086975 | -0.041199 | 0.045776 | 0.10986 | -0.032043 | 0.10071 | 0.1236 | 0.082397 | 0.027466 | 121.8521 | 121.7239 | 0.032044 | 121.7972 | 121.8979 | 0.17395 | -0.082397 | 121.8475 | 121.7926 | -0.059509 | 121.8109 | 121.7331 | -0.059509 | -0.036621 | 121.9574 | 121.843 | 121.843 | -0.20142 | 121.8658 | 121.8887 | 121.875 | -0.13275
1553.0781 | 121.9849 | -121.788 | 0.15106 | 0.013046 | 0.016522 | 0.095861 | 0.028006 | -0.00032252 | -0.020535 | -0.018865 | 0.0073242 | 0.037937 | -0.026611 | -0.0074383 | -0.0018458 | 0.0086091 | 0.10986 | 0.068665 | 0.11902 | 0.16022 | 0.15564 | 0.073242 | -0.036621 | 0.086975 | 0.1236 | -0.036621 | 0.07782 | 0.10529 | 0.10529 | 0.013733 | 121.8613 | 121.7514 | 0.004578 | 121.8567 | 121.9482 | 0.19684 | -0.041199 | 121.8933 | 121.8018 | -0.073242 | 121.875 | 121.7514 | -0.050354 | -0.045776 | 121.9437 | 121.8979 | 121.907 | -0.18768 | 121.8658 | 121.8933 | 121.9116 | -0.13733
1554.7812 | 122.081 | -121.7514 | 0.10986 | 0.013046 | 0.025921 | 0.099279 | 0.029501 | -0.0033133 | -0.027799 | -0.018011 | 0.014954 | 0.031956 | -0.031097 | -0.0089337 | -0.0076136 | 0.010104 | 0.050354 | 0.10071 | 0.13733 | 0.16022 | 0.14191 | 0.10529 | -0.022888 | 0.064087 | 0.13275 | 0.018311 | 0.050354 | 0.059509 | 0.09613 | 0.027466 | 121.8567 | 121.7285 | 0.032044 | 121.8521 | 121.9116 | 0.1831 | -0.059509 | 121.8475 | 121.7789 | -0.059509 | 121.8155 | 121.7697 | -0.009155 | -0.050354 | 121.8933 | 121.8018 | 121.8887 | -0.13275 | 121.8018 | 121.8109 | 121.8842 | -0.082397
1556.5781 | 122.1085 | -121.7651 | 0.11902 | 0.0054168 | 0.026776 | 0.095007 | 0.024161 | -0.0024587 | -0.02374 | -0.019079 | 0.0073242 | 0.038365 | -0.032165 | -0.0078657 | -0.0046228 | 0.010532 | 0.16479 | 0.15106 | 0.18768 | 0.19684 | 0.12817 | 0.1236 | -0.018311 | 0.13275 | 0.17853 | 0.064087 | 0.050354 | 0.059509 | 0.12817 | 0.045776 | 121.8887 | 121.7468 | 0.009155 | 121.9162 | 121.962 | 0.21515 | 0.045776 | 121.8933 | 121.8109 | -0.068665 | 121.8979 | 121.8292 | 0.018311 | -0.05951 | 121.8933 | 121.9299 | 121.9528 | -0.13733 | 121.8155 | 121.8246 | 121.9437 | -0.073243
1558.3594 | 121.9574 | -120.163 | 1.6937 | 0.0054168 | 0.57301 | 0.40305 | 0.030142 | -0.24471 | -0.026731 | 0.22659 | -0.0003053 | 0.28617 | -0.027679 | -0.0080793 | -0.0061182 | 0.0088227 | 1.5289 | 0.49896 | 1.5289 | 1.3733 | 1.6754 | 1.442 | 1.3275 | 1.4191 | 1.3184 | 1.3779 | 1.6617 | 1.6617 | 1.5106 | 1.442 | 121.6049 | 121.4905 | -0.018311 | 120.6619 | 121.5363 | 0.045776 | -0.1648 | 121.6736 | 121.6049 | -0.032044 | 121.582 | 121.5408 | -0.064087 | -0.032044 | 121.8384 | 121.6919 | 121.6919 | -0.36621 | 121.8246 | 121.8246 | 121.4813 | -0.25177
1560.1406 | 122.0581 | -121.7743 | 0.09613 | 0.013046 | 0.023144 | 0.082189 | 0.028647 | -0.075304 | -0.020108 | 0.008906 | 0.014954 | 0.014225 | -0.03067 | -0.0076519 | -0.0052636 | 0.0090363 | 0.086975 | 0.064087 | 0.11444 | 0.14191 | 0.13275 | 0.07782 | -0.041199 | 0.10986 | 0.11444 | 0.018311 | 0.022888 | 0.027466 | 0.10986 | 0.009155 | 121.8521 | 121.7331 | 0.036621 | 121.8384 | 121.9162 | 0.18311 | -0.009155 | 121.8842 | 121.7834 | -0.073242 | 121.8842 | 121.7926 | 0.009156 | -0.068664 | 121.907 | 121.8613 | 121.8887 | -0.13733 | 121.7972 | 121.8018 | 121.8887 | -0.086975
1561.8594 | 122.0123 | -121.8384 | 0.10986 | -0.0022127 | 0.013531 | 0.084325 | 0.029929 | -0.0721 | -0.022885 | 0.0080514 | 0.0073242 | 0.012943 | -0.028534 | -0.0074383 | -0.0037684 | 0.0079681 | 0.018311 | 0.018311 | 0.036621 | 0.11444 | 0.14191 | 0.041199 | -0.068665 | 0.013733 | 0.068665 | -0.073242 | 0.054932 | 0.059509 | 0.045776 | -0.022888 | 121.8796 | 121.7697 | 0.032044 | 121.8567 | 121.9528 | 0.18311 | -0.091552 | 121.8842 | 121.8155 | -0.054931 | 121.8521 | 121.7651 | -0.050354 | -0.050354 | 121.9803 | 121.8567 | 121.875 | -0.17853 | 121.8933 | 121.8979 | 121.907 | -0.13275
1563.6406 | 121.962 | -121.8658 | 0.1236 | 0.0054168 | 0.014172 | 0.085607 | 0.026083 | -0.074877 | -0.021817 | 0.0080514 | 0.0073242 | 0.016575 | -0.029815 | -0.0065839 | -0.003982 | 0.0092499 | 0.07782 | 0.054932 | 0.073242 | 0.11444 | 0.13733 | 0.054932 | -0.064087 | 0.032043 | 0.07782 | -0.082397 | 0.045776 | 0.073242 | 0.054932 | -0.027466 | 121.9208 | 121.8018 | 0.013733 | 121.9208 | 121.9803 | 0.17853 | -0.045776 | 121.9208 | 121.8384 | -0.07782 | 121.8979 | 121.7834 | -0.054931 | -0.050354 | 122.0032 | 121.9437 | 121.9391 | -0.18768 | 121.9116 | 121.9391 | 121.9437 | -0.15106
1565.4219 | 122.0581 | -121.8521 | 0.086975 | 0.020676 | 0.014813 | 0.082616 | 0.029074 | -0.073809 | -0.022672 | 0.007197 | 0.0073242 | 0.015293 | -0.028534 | -0.0072247 | -0.0069726 | 0.0083953 | 0.027466 | 0.027466 | 0.073242 | 0.12817 | 0.13733 | 0.041199 | -0.068665 | 0.032043 | 0.086975 | -0.054932 | 0.041199 | 0.07782 | 0.045776 | -0.032043 | 121.8933 | 121.7834 | 0.050354 | 121.8796 | 121.9803 | 0.19684 | -0.059509 | 121.8979 | 121.8201 | -0.045776 | 121.8842 | 121.7972 | -0.022889 | -0.009155 | 121.9894 | 121.8796 | 121.9254 | -0.15564 | 121.8933 | 121.9299 | 121.9391 | -0.11902
1567.2031 | 122.0673 | -121.8567 | 0.11444 | -0.0098417 | 0.013104 | 0.083685 | 0.027365 | -0.074236 | -0.024167 | 0.0080514 | 0.014954 | 0.016148 | -0.030029 | -0.0057293 | -0.0046228 | 0.011173 | 0.050354 | 0.036621 | 0.064087 | 0.12817 | 0.14191 | 0.054932 | -0.07782 | 0.032043 | 0.091553 | -0.045776 | 0.059509 | 0.064087 | 0.059509 | -0.027466 | 121.9116 | 121.7789 | 0.027466 | 121.8933 | 121.9849 | 0.20599 | -0.064087 | 121.9162 | 121.8292 | -0.054932 | 121.8887 | 121.8109 | -0.01831 | -0.050354 | 121.9986 | 121.907 | 121.9208 | -0.19226 | 121.9162 | 121.9208 | 121.9482 | -0.14191
1569.0156 | 122.049 | -121.8613 | 0.10529 | 0.0054168 | 0.015667 | 0.083685 | 0.029501 | -0.074663 | -0.025876 | 0.0074106 | 0.014954 | 0.013584 | -0.028961 | -0.0063703 | -0.0054772 | 0.010104 | -0.004578 | 0.004578 | 0.022888 | 0.09613 | 0.16479 | 0.032043 | -0.073242 | -0.032043 | 0.050354 | -0.10071 | 0.050354 | 0.073242 | 0.050354 | -0.027466 | 121.8933 | 121.788 | 0.059509 | 121.8658 | 121.9574 | 0.16937 | -0.10986 | 121.9116 | 121.8338 | -0.054932 | 121.8292 | 121.7606 | -0.073242 | -0.032044 | 122.0261 | 121.8567 | 121.8842 | -0.17853 | 121.9116 | 121.9345 | 121.9116 | -0.13275
1570.8125 | 122.0215 | -121.8658 | 0.14191 | -0.0022127 | 0.013317 | 0.083685 | 0.025229 | -0.075518 | -0.023526 | 0.0078378 | -0.0003053 | 0.014866 | -0.032165 | -0.0057293 | -0.0027002 | 0.0116 | 0.050354 | 0.054932 | 0.068665 | 0.10986 | 0.13733 | 0.068665 | -0.050354 | 0.013733 | 0.045776 | -0.091553 | 0.036621 | 0.054932 | 0.064087 | -0.032043 | 121.9345 | 121.8155 | -0.004578 | 121.9208 | 121.9757 | 0.16022 | -0.091553 | 121.9299 | 121.8338 | -0.10529 | 121.8796 | 121.7743 | -0.05951 | -0.086975 | 122.0032 | 121.9162 | 121.9345 | -0.19226 | 121.9025 | 121.9208 | 121.9116 | -0.17395
1572.5156 | 122.1497 | -121.8887 | 0.09613 | 0.0054168 | 0.025494 | 0.086675 | 0.028433 | -0.072314 | -0.030576 | 0.006556 | 0.014954 | 0.011021 | -0.032165 | -0.0080793 | -0.008468 | 0.0116 | 0.018311 | 0.073242 | 0.11902 | 0.1236 | 0.10986 | 0.082397 | -0.064087 | 0.013733 | 0.091553 | 0 | 0.013733 | 0.036621 | 0.068665 | -0.004578 | 121.9711 | 121.8246 | 0.013733 | 121.962 | 122.0123 | 0.18768 | -0.077819 | 121.9574 | 121.8842 | -0.082397 | 121.9025 | 121.8887 | 0.004578 | -0.059509 | 121.9986 | 121.907 | 122.0078 | -0.16022 | 121.9025 | 121.9254 | 121.9803 | -0.10071
1574.2969 | 122.1039 | -121.8933 | 0.10986 | 0.013046 | 0.022289 | 0.087103 | 0.028433 | -0.073382 | -0.028012 | 0.0044198 | 0.0073242 | 0.010166 | -0.028961 | -0.010643 | -0.0071862 | 0.0096771 | 0.10071 | 0.15564 | 0.1831 | 0.16022 | 0.091553 | 0.082397 | -0.041199 | 0.09613 | 0.19684 | 0.054932 | 0.013733 | 0.027466 | 0.082397 | -0.009155 | 121.9757 | 121.8521 | -0.01831 | 122.049 | 122.0535 | 0.20142 | -0.009155 | 121.9757 | 121.8842 | -0.09613 | 121.9894 | 121.9482 | 0.064087 | -0.082397 | 121.9849 | 121.994 | 122.0764 | -0.15106 | 121.907 | 121.9208 | 122.0901 | -0.11902
1576.0312 | 122.1268 | -121.8887 | 0.086975 | 0.0054168 | 0.028698 | 0.083685 | 0.024161 | -0.074663 | -0.026731 | 0.004847 | 0.014954 | 0.011875 | -0.028961 | -0.0082929 | -0.0071862 | 0.0075409 | 0.10071 | 0.11444 | 0.16937 | 0.16479 | 0.10986 | 0.07782 | -0.027466 | 0.07782 | 0.13733 | 0.022888 | 0.022888 | 0.022888 | 0.082397 | 0.004578 | 121.9666 | 121.8613 | 0.022888 | 122.0032 | 122.0535 | 0.19226 | 0.013733 | 121.9711 | 121.8933 | -0.064087 | 121.9666 | 121.9116 | 0.01831 | -0.064087 | 121.9986 | 121.9894 | 122.0581 | -0.11444 | 121.9116 | 121.9116 | 122.0261 | -0.082397
1577.8125 | 122.1542 | -121.8704 | 0.082397 | -0.0022127 | 0.024426 | 0.083044 | 0.02352 | -0.069964 | -0.023313 | 0.0050608 | 0.014954 | 0.01273 | -0.031311 | -0.0070111 | -0.0052636 | 0.0098907 | 0.14191 | 0.11902 | 0.15564 | 0.16479 | 0.10529 | 0.09613 | -0.027466 | 0.10071 | 0.14648 | 0.036621 | 0.009155 | 0.022888 | 0.10071 | 0.013733 | 121.9666 | 121.843 | 0.022889 | 121.9894 | 122.0352 | 0.19226 | 0.05951 | 121.9711 | 121.8842 | -0.073242 | 121.9711 | 121.907 | 0.022888 | -0.059509 | 121.9757 | 122.0123 | 122.0261 | -0.10986 | 121.8796 | 121.8933 | 122.0169 | -0.068664
1579.6094 | 122.1863 | -121.8704 | 0.082397 | 0.0054168 | 0.023358 | 0.084325 | 0.023306 | -0.071673 | -0.022458 | 0.006556 | 0.0073242 | 0.016361 | -0.03067 | -0.0087201 | -0.0029138 | 0.010104 | 0.09613 | 0.091553 | 0.13275 | 0.14191 | 0.10986 | 0.091553 | -0.045776 | 0.09613 | 0.12817 | 0.009155 | 0 | 0.041199 | 0.09613 | 0.004578 | 121.962 | 121.8246 | 0.027466 | 121.962 | 122.0123 | 0.18768 | 0.013733 | 121.9666 | 121.875 | -0.082397 | 121.9666 | 121.8796 | 0.004577 | -0.041198 | 121.9803 | 121.9666 | 122.0032 | -0.12817 | 121.8704 | 121.9116 | 121.9986 | -0.077819
1581.3438 | 122.1176 | -121.9208 | 0.10529 | 0.0054168 | 0.015881 | 0.083471 | 0.026511 | -0.071886 | -0.020535 | 0.0059152 | 0.0073242 | 0.015934 | -0.029602 | -0.0070111 | -0.0044092 | 0.0088227 | 0.036621 | 0.004578 | 0.050354 | 0.11444 | 0.12817 | 0.045776 | -0.068665 | 0.013733 | 0.086975 | -0.059509 | 0.032043 | 0.050354 | 0.059509 | -0.027466 | 121.9666 | 121.8521 | 0.022888 | 121.9254 | 122.0352 | 0.18311 | -0.068665 | 121.9803 | 121.8933 | -0.073243 | 121.9345 | 121.8613 | -0.032043 | -0.054932 | 122.049 | 121.9574 | 121.9711 | -0.17395 | 121.9528 | 121.9711 | 122.0078 | -0.13275
1583.1094 | 122.113 | -121.907 | 0.091553 | 0.0054168 | 0.013958 | 0.086248 | 0.032706 | -0.072741 | -0.022244 | 0.0076242 | 0.014954 | 0.016575 | -0.028106 | -0.0078657 | -0.005691 | 0.0083953 | 0.027466 | -0.004578 | 0.050354 | 0.091553 | 0.13733 | 0.059509 | -0.086975 | -0.009155 | 0.054932 | -0.086975 | 0.050354 | 0.059509 | 0.045776 | -0.027466 | 121.9666 | 121.8201 | 0.045776 | 121.9025 | 121.9986 | 0.17853 | -0.064087 | 121.9528 | 121.8796 | -0.041199 | 121.8979 | 121.8201 | -0.059509 | -0.032044 | 122.0444 | 121.9345 | 121.9574 | -0.17853 | 121.9574 | 121.9666 | 121.962 | -0.11902
1584.8281 | 122.0581 | -121.9299 | 0.10986 | 0.013046 | 0.013531 | 0.084112 | 0.02587 | -0.073382 | -0.020535 | 0.0084786 | 0.014954 | 0.016148 | -0.029175 | -0.0057293 | -0.003982 | 0.0088227 | 0.004578 | -0.013733 | 0.036621 | 0.091553 | 0.14191 | 0.064087 | -0.07782 | -0.032043 | -0.009155 | -0.11902 | 0.050354 | 0.091553 | 0.041199 | -0.022888 | 121.994 | 121.8521 | 0.032044 | 121.9162 | 122.0215 | 0.16937 | -0.10529 | 121.9711 | 121.907 | -0.059509 | 121.8979 | 121.8109 | -0.096131 | -0.01831 | 122.0718 | 121.9345 | 121.9666 | -0.18768 | 121.9803 | 122.0215 | 121.9208 | -0.13275
1586.625 | 122.2 | -121.9254 | 0.086975 | -0.0022127 | 0.024853 | 0.086034 | 0.024588 | -0.075091 | -0.030576 | 0.005488 | 0.0073242 | 0.010166 | -0.030243 | -0.0091473 | -0.0071862 | 0.010745 | 0.036621 | 0.073242 | 0.10529 | 0.11444 | 0.11444 | 0.082397 | -0.036621 | 0.009155 | 0.091553 | -0.013733 | 0.013733 | 0.032043 | 0.073242 | 0.013733 | 122.0078 | 121.8887 | 0.027466 | 121.9986 | 122.0398 | 0.15106 | -0.050354 | 121.9986 | 121.9391 | -0.073242 | 121.9345 | 121.9116 | -0.027466 | -0.054932 | 122.0398 | 121.962 | 122.0306 | -0.1236 | 121.9391 | 121.9574 | 122.0169 | -0.073242
1588.4062 | 122.2 | -121.8933 | 0.09613 | 0.0054168 | 0.023785 | 0.084325 | 0.025443 | -0.071245 | -0.025235 | 0.0029244 | -0.0003053 | 0.012516 | -0.028961 | -0.0080793 | -0.0044092 | 0.010532 | 0.10986 | 0.11444 | 0.15106 | 0.17395 | 0.10071 | 0.09613 | -0.045776 | 0.091553 | 0.13733 | 0.027466 | 0.004578 | 0.022888 | 0.086975 | 0.018311 | 121.9894 | 121.8475 | 0.004578 | 122.0078 | 122.0673 | 0.21973 | 0.013733 | 121.9803 | 121.9116 | -0.091552 | 121.9849 | 121.9208 | 0.009155 | -0.073242 | 121.994 | 122.0032 | 122.0444 | -0.14191 | 121.8979 | 121.9162 | 122.0306 | -0.077819
1590.1094 | 122.1725 | -121.9345 | 0.091553 | 0.013046 | 0.02293 | 0.085394 | 0.026297 | -0.07445 | -0.025449 | 0.0061288 | 0.014954 | 0.011235 | -0.030456 | -0.0093609 | -0.006759 | 0.010532 | 0.10529 | 0.11902 | 0.15106 | 0.14191 | 0.09613 | 0.086975 | -0.027466 | 0.032043 | 0.091553 | 0.009155 | 0.027466 | 0.059509 | 0.07782 | -0.004578 | 122.0215 | 121.907 | 0.004577 | 122.0535 | 122.0764 | 0.16937 | 0.013733 | 122.0123 | 121.9299 | -0.064087 | 121.9666 | 121.9437 | 0.013733 | -0.032044 | 122.0306 | 122.0398 | 122.0856 | -0.11902 | 121.962 | 121.994 | 122.0261 | -0.096131
1591.8906 | 122.1497 | -121.9391 | 0.086975 | 0.0054168 | 0.021008 | 0.085607 | 0.030356 | -0.068896 | -0.026517 | 0.0035654 | 0.014954 | 0.010807 | -0.029602 | -0.0080793 | -0.0071862 | 0.010532 | 0.11902 | 0.16022 | 0.17853 | 0.16937 | 0.07782 | 0.082397 | -0.032043 | 0.10071 | 0.19226 | 0.036621 | 0.013733 | 0.018311 | 0.09613 | 0.004578 | 122.0215 | 121.907 | -0.009155 | 122.0993 | 122.1085 | 0.20142 | 0.032044 | 122.0352 | 121.9437 | -0.073242 | 122.0398 | 121.9757 | 0.032043 | -0.068664 | 122.0169 | 122.0581 | 122.1176 | -0.11902 | 121.9528 | 121.9574 | 122.1313 | -0.082397
1593.6875 | 122.081 | -121.9711 | 0.12817 | 0.0054168 | 0.018871 | 0.086034 | 0.031851 | -0.073382 | -0.024381 | 0.0046334 | 0.0073242 | 0.014012 | -0.029175 | -0.0089337 | -0.0069726 | 0.0092499 | 0.10071 | 0.12817 | 0.13733 | 0.15564 | 0.10529 | 0.07782 | -0.050354 | 0.027466 | 0.12817 | -0.009155 | 0.013733 | 0.059509 | 0.045776 | -0.027466 | 122.049 | 121.9208 | -0.022888 | 122.0993 | 122.1268 | 0.20599 | -0.027466 | 122.0169 | 121.9437 | -0.11444 | 121.9986 | 121.962 | 0.018311 | -0.068665 | 122.0764 | 122.0718 | 122.1085 | -0.17853 | 121.9849 | 122.0306 | 122.0993 | -0.15564
1595.4062 | 122.2229 | -121.9116 | 0.068665 | -0.0022127 | 0.022076 | 0.083471 | 0.026724 | -0.074236 | -0.022244 | 0.0044198 | 0.0073242 | 0.015507 | -0.028961 | -0.0080793 | -0.002273 | 0.0088227 | 0.10071 | 0.07782 | 0.11444 | 0.13275 | 0.1236 | 0.07782 | -0.054932 | 0.10986 | 0.13275 | 0.004578 | 0.022888 | 0.018311 | 0.073242 | 0.004578 | 121.9894 | 121.8567 | 0.054931 | 121.9894 | 122.0444 | 0.18768 | 0.032043 | 121.9849 | 121.9162 | -0.045777 | 122.0215 | 121.9162 | 0 | -0.050354 | 122.0352 | 122.0123 | 122.0261 | -0.1236 | 121.9345 | 121.9299 | 122.0444 | -0.064087
1597.125 | 122.0947 | -122.0032 | 0.12817 | 0.0054168 | 0.01759 | 0.085607 | 0.029929 | -0.070605 | -0.024808 | 0.0050608 | -0.0003053 | 0.013371 | -0.029175 | -0.010429 | -0.0065454 | 0.010959 | 0.086975 | 0.073242 | 0.10071 | 0.1236 | 0.1236 | 0.050354 | -0.07782 | -0.004578 | 0.07782 | -0.068665 | 0.054932 | 0.041199 | 0.045776 | -0.027466 | 122.0535 | 121.9254 | -0.004578 | 122.0764 | 122.1268 | 0.20142 | -0.041199 | 122.049 | 121.9757 | -0.073242 | 121.9986 | 121.9345 | -0.041199 | -0.086975 | 122.1268 | 122.0901 | 122.1039 | -0.20599 | 122.0581 | 122.0444 | 122.081 | -0.15564
1598.9219 | 122.1176 | -121.994 | 0.11444 | 0.013046 | 0.020153 | 0.086248 | 0.029288 | -0.0721 | -0.025876 | 0.0033518 | 0.0073242 | 0.012516 | -0.03067 | -0.010643 | -0.0054772 | 0.0094635 | 0.11902 | 0.15564 | 0.16937 | 0.16937 | 0.10529 | 0.091553 | -0.032043 | 0.10071 | 0.16479 | 0.022888 | 0.004578 | 0.013733 | 0.073242 | 0.004578 | 122.0856 | 121.962 | -0.009155 | 122.1497 | 122.1634 | 0.20142 | 0.004578 | 122.0673 | 121.9986 | -0.10986 | 122.0947 | 122.0169 | 0.01831 | -0.10071 | 122.0993 | 122.113 | 122.1634 | -0.14648 | 121.9986 | 122.0078 | 122.1588 | -0.10986
1600.7031 | 122.2275 | -121.9574 | 0.091553 | 0.0054168 | 0.024639 | 0.086248 | 0.027152 | -0.073168 | -0.026944 | 0.0024972 | -0.0003053 | 0.01273 | -0.030883 | -0.010643 | -0.0061182 | 0.010104 | 0.054932 | 0.07782 | 0.1236 | 0.13733 | 0.10986 | 0.073242 | -0.032043 | 0.036621 | 0.07782 | -0.013733 | 0.022888 | 0.041199 | 0.07782 | 0.004578 | 122.0306 | 121.9254 | 0.01831 | 122.0352 | 122.0947 | 0.16937 | -0.036621 | 122.0352 | 121.962 | -0.068665 | 121.994 | 121.9437 | -0.018311 | -0.050354 | 122.0673 | 122.0123 | 122.081 | -0.1236 | 121.9803 | 121.9986 | 122.0352 | -0.086975
1602.4375 | 122.2366 | -121.9574 | 0.082397 | 0.013046 | 0.023358 | 0.081976 | 0.027579 | -0.070177 | -0.020749 | 0.008265 | -0.0003053 | 0.015293 | -0.028747 | -0.0072247 | -0.0052636 | 0.0075409 | 0.1236 | 0.11444 | 0.16022 | 0.17853 | 0.10986 | 0.091553 | -0.032043 | 0.1236 | 0.15106 | 0.009155 | 0 | 0.004578 | 0.09613 | 0.018311 | 122.049 | 121.9254 | 0.027466 | 122.0718 | 122.1359 | 0.21057 | 0.041199 | 122.0535 | 121.9757 | -0.082397 | 122.081 | 121.9666 | -0.009156 | -0.077819 | 122.0673 | 122.081 | 122.1176 | -0.11444 | 121.9574 | 121.962 | 122.1085 | -0.064086
1604.2188 | 122.1725 | -121.9849 | 0.11444 | 0.0054168 | 0.013745 | 0.08518 | 0.029288 | -0.076372 | -0.023526 | 0.0067696 | 0.014954 | 0.01743 | -0.027893 | -0.0061567 | -0.0059046 | 0.0066863 | 0.022888 | 0 | 0.009155 | 0.07782 | 0.15106 | 0.036621 | -0.10071 | -0.022888 | 0.050354 | -0.10071 | 0.050354 | 0.050354 | 0.068665 | -0.022888 | 122.0215 | 121.8842 | 0.036621 | 121.9849 | 122.0627 | 0.17853 | -0.091553 | 122.0535 | 121.962 | -0.064087 | 121.962 | 121.8842 | -0.07782 | -0.064087 | 122.1359 | 122.0078 | 121.994 | -0.21515 | 122.0352 | 122.0352 | 122.0352 | -0.13733
1606.0156 | 122.2504 | -121.9482 | 0.091553 | -0.0022127 | 0.021435 | 0.084325 | 0.02886 | -0.072527 | -0.02844 | 0.0067696 | 0.014954 | 0.013157 | -0.029602 | -0.0087201 | -0.0093226 | 0.010745 | 0.11444 | 0.16022 | 0.18768 | 0.16479 | 0.10986 | 0.086975 | -0.050354 | 0.10529 | 0.20142 | 0.068665 | 0.018311 | 0.036621 | 0.10071 | 0.009155 | 122.0352 | 121.8979 | 0.01831 | 122.1085 | 122.113 | 0.21515 | 0.022888 | 122.0489 | 121.9574 | -0.073242 | 122.0535 | 122.0169 | 0.05951 | -0.054932 | 122.0581 | 122.0627 | 122.1359 | -0.14191 | 121.9666 | 121.9849 | 122.1497 | -0.082398
1607.7812 | 122.2687 | -121.9437 | 0.064087 | -0.0022127 | 0.02293 | 0.086248 | 0.028006 | -0.071032 | -0.028226 | 0.004847 | -0.0003053 | 0.01273 | -0.030029 | -0.0093609 | -0.0048364 | 0.0086091 | 0.091553 | 0.14191 | 0.15106 | 0.16479 | 0.10986 | 0.068665 | -0.032043 | 0.073242 | 0.16479 | 0.036621 | 0.004578 | 0.045776 | 0.082397 | -0.004578 | 122.0123 | 121.9116 | 0.045776 | 122.0856 | 122.1085 | 0.19684 | 0.027466 | 122.0261 | 121.9391 | -0.059509 | 122.0169 | 121.9803 | 0.041199 | -0.018311 | 122.0535 | 122.0352 | 122.0947 | -0.09613 | 121.9482 | 121.9894 | 122.1085 | -0.068665
1609.5 | 122.2549 | -121.9528 | 0.082397 | 0.013046 | 0.022289 | 0.082189 | 0.02587 | -0.071245 | -0.021176 | 0.006556 | -0.0003053 | 0.014866 | -0.029815 | -0.0076519 | -0.0024866 | 0.011386 | 0.14648 | 0.13275 | 0.15564 | 0.17395 | 0.10529 | 0.09613 | -0.050354 | 0.1236 | 0.14191 | 0.027466 | 0 | 0.018311 | 0.10529 | 0.013733 | 122.049 | 121.9025 | 0.022889 | 122.0856 | 122.1268 | 0.2243 | 0.064087 | 122.0581 | 121.9666 | -0.082397 | 122.0764 | 121.9803 | 0.013733 | -0.064086 | 122.0581 | 122.0993 | 122.1085 | -0.13275 | 121.9528 | 121.9711 | 122.0947 | -0.068664
1611.2812 | 122.168 | -122.0078 | 0.10071 | 0.0054168 | 0.013745 | 0.084966 | 0.029288 | -0.074236 | -0.021817 | 0.0046334 | 0.022583 | 0.017216 | -0.029815 | -0.0078657 | -0.002273 | 0.0083953 | 0.032043 | 0.009155 | 0.027466 | 0.10071 | 0.15106 | 0.050354 | -0.07782 | 0.013733 | 0.073242 | -0.091553 | 0.045776 | 0.068665 | 0.050354 | -0.036621 | 122.0581 | 121.9299 | 0.050354 | 122.0169 | 122.1085 | 0.17853 | -0.068665 | 122.0581 | 121.9711 | -0.054932 | 122.0215 | 121.9162 | -0.054932 | -0.032043 | 122.1588 | 122.0398 | 122.0352 | -0.17853 | 122.0535 | 122.0764 | 122.081 | -0.13733
1613.0781 | 122.2321 | -121.9711 | 0.09613 | 0.0054168 | 0.024853 | 0.08518 | 0.023947 | -0.073809 | -0.027585 | 0.004847 | -0.0003053 | 0.012943 | -0.029175 | -0.0093609 | -0.0048364 | 0.0116 | 0.10071 | 0.13733 | 0.15564 | 0.14191 | 0.10071 | 0.091553 | -0.041199 | 0.068665 | 0.1236 | -0.004578 | 0.004578 | 0.045776 | 0.10529 | 0.009155 | 122.0627 | 121.9299 | 0.004578 | 122.1085 | 122.113 | 0.18311 | 0.004578 | 122.0764 | 121.9803 | -0.091552 | 122.0398 | 121.9666 | -0.013733 | -0.050354 | 122.0718 | 122.0718 | 122.1268 | -0.13733 | 121.9757 | 122.0169 | 122.0947 | -0.086975
1614.7969 | 122.1451 | -122.0123 | 0.1236 | -0.0022127 | 0.016949 | 0.083257 | 0.02886 | -0.071673 | -0.024167 | 0.0061288 | -0.0003053 | 0.01743 | -0.027679 | -0.0072247 | -0.00505 | 0.0090363 | 0.032043 | 0.009155 | 0.036621 | 0.068665 | 0.14648 | 0.022888 | -0.082397 | -0.018311 | 0.050354 | -0.09613 | 0.054932 | 0.068665 | 0.064087 | -0.036621 | 122.0352 | 121.9299 | 0.022888 | 122.0215 | 122.081 | 0.15106 | -0.091553 | 122.0764 | 121.9757 | -0.068664 | 121.994 | 121.9162 | -0.059509 | -0.054931 | 122.1588 | 122.0444 | 122.0489 | -0.20599 | 122.0673 | 122.081 | 122.0627 | -0.16022
1616.5938 | 122.1497 | -122.0261 | 0.10986 | 0.020676 | 0.016094 | 0.081548 | 0.025656 | -0.072741 | -0.022031 | 0.006556 | 0.022583 | 0.017002 | -0.025757 | -0.0078657 | -0.0024866 | 0.010532 | 0.022888 | -0.004578 | 0.027466 | 0.086975 | 0.14191 | 0.068665 | -0.073242 | -0.022888 | 0.004578 | -0.13275 | 0.050354 | 0.064087 | 0.054932 | -0.041199 | 122.0947 | 121.9528 | 0.032044 | 122.0215 | 122.113 | 0.16022 | -0.086975 | 122.081 | 121.9849 | -0.059509 | 122.0032 | 121.8933 | -0.091552 | -0.045776 | 122.168 | 122.0489 | 122.0535 | -0.18311 | 122.0764 | 122.0901 | 122.0306 | -0.15106
1618.375 | 122.1497 | -122.0306 | 0.10986 | 0.013046 | 0.015881 | 0.084753 | 0.030356 | -0.07445 | -0.02374 | 0.0033518 | 0.014954 | 0.016575 | -0.030243 | -0.0078657 | -0.0082544 | 0.0116 | 0.009155 | 0.018311 | 0.041199 | 0.091553 | 0.14648 | 0.045776 | -0.10071 | -0.018311 | 0.036621 | -0.086975 | 0.054932 | 0.086975 | 0.045776 | -0.027466 | 122.0764 | 121.9299 | 0.036621 | 122.049 | 122.1222 | 0.19226 | -0.10071 | 122.0764 | 122.0032 | -0.054931 | 122.0123 | 121.9437 | -0.059509 | -0.022888 | 122.1771 | 122.0398 | 122.0718 | -0.21057 | 122.0856 | 122.1176 | 122.0673 | -0.13733
1620.1562 | 122.1405 | -122.0078 | 0.10986 | 0.0054168 | 0.014172 | 0.083685 | 0.026297 | -0.071032 | -0.020322 | 0.0059152 | -0.0079343 | 0.015934 | -0.030029 | -0.0080793 | -0.0031274 | 0.0096771 | 0.068665 | 0.050354 | 0.054932 | 0.10986 | 0.13733 | 0.068665 | -0.07782 | 0.027466 | 0.045776 | -0.09613 | 0.050354 | 0.059509 | 0.064087 | -0.018311 | 122.0764 | 121.9299 | 0.027466 | 122.0581 | 122.1176 | 0.18768 | -0.041198 | 122.0718 | 121.9894 | -0.059509 | 122.0352 | 121.9116 | -0.077819 | -0.050354 | 122.1451 | 122.0764 | 122.0627 | -0.18768 | 122.0581 | 122.0673 | 122.0535 | -0.12817
1621.9375 | 122.1725 | -122.0535 | 0.11444 | 0.013046 | 0.013531 | 0.087316 | 0.028433 | -0.072741 | -0.025876 | 0.00207 | -0.0003053 | 0.01508 | -0.030883 | -0.0078657 | -0.006759 | 0.0116 | -0.009155 | 0.032043 | 0.022888 | 0.07782 | 0.14648 | 0.036621 | -0.068665 | -0.036621 | 0.050354 | -0.09613 | 0.064087 | 0.050354 | 0.050354 | -0.022888 | 122.0901 | 121.9849 | 0.032043 | 122.0856 | 122.1313 | 0.14649 | -0.1236 | 122.1039 | 122.0306 | -0.050354 | 122.0169 | 121.9574 | -0.073242 | -0.064087 | 122.2 | 122.0444 | 122.0764 | -0.18311 | 122.1176 | 122.1039 | 122.1039 | -0.13733
1623.7188 | 122.2641 | -121.9894 | 0.082397 | 0.020676 | 0.024639 | 0.086675 | 0.026297 | -0.069537 | -0.029721 | 0.0046334 | -0.0003053 | 0.013798 | -0.032165 | -0.0087201 | -0.0080408 | 0.0096771 | 0.041199 | 0.082397 | 0.11902 | 0.12817 | 0.12817 | 0.082397 | -0.054932 | 0.022888 | 0.082397 | -0.018311 | 0.018311 | 0.009155 | 0.091553 | -0.013733 | 122.0718 | 121.9345 | 0.045777 | 122.0718 | 122.1176 | 0.18311 | -0.041198 | 122.081 | 121.9757 | -0.064086 | 122.0123 | 121.9711 | -0.004578 | -0.073242 | 122.1176 | 122.0306 | 122.1085 | -0.13733 | 122.0078 | 121.9986 | 122.0718 | -0.09613
1625.4375 | 122.1771 | -122.0352 | 0.10071 | 0.0054168 | 0.014813 | 0.082403 | 0.023947 | -0.072314 | -0.021176 | 0.0061288 | -0.0003053 | 0.016148 | -0.029602 | -0.0063703 | -0.003341 | 0.0116 | -0.004578 | -0.032043 | 0.009155 | 0.07782 | 0.14191 | 0.041199 | -0.073242 | -0.013733 | -0.009155 | -0.11444 | 0.054932 | 0.050354 | 0.054932 | -0.036621 | 122.0764 | 121.962 | 0.041199 | 122.0032 | 122.113 | 0.15106 | -0.10529 | 122.0901 | 121.9986 | -0.045776 | 122.0215 | 121.9208 | -0.07782 | -0.050354 | 122.1771 | 122.0306 | 122.0444 | -0.17395 | 122.0901 | 122.0856 | 122.0261 | -0.13733
1627.2344 | 122.2412 | -122.0398 | 0.09613 | -0.0022127 | 0.019512 | 0.086462 | 0.030569 | -0.072741 | -0.027371 | 0.0057016 | 0.0073242 | 0.014225 | -0.029602 | -0.0087201 | -0.006759 | 0.010532 | 0.10071 | 0.17853 | 0.17395 | 0.16937 | 0.10071 | 0.086975 | -0.045776 | 0.086975 | 0.1831 | 0.054932 | -0.004578 | 0.027466 | 0.09613 | 0.009155 | 122.1268 | 121.994 | 0.004578 | 122.2183 | 122.2092 | 0.21515 | 0.004578 | 122.1359 | 122.049 | -0.10071 | 122.1268 | 122.0947 | 0.045777 | -0.068664 | 122.1405 | 122.1405 | 122.2137 | -0.14191 | 122.0352 | 122.0673 | 122.2229 | -0.086975
1629.0312 | 122.3007 | -121.9803 | 0.068665 | 0.0054168 | 0.024426 | 0.084112 | 0.026938 | -0.071245 | -0.029508 | 0.0042062 | 0.0073242 | 0.016148 | -0.032379 | -0.0093609 | -0.0086816 | 0.0116 | 0.045776 | 0.082397 | 0.09613 | 0.13733 | 0.10529 | 0.073242 | -0.068665 | 0.036621 | 0.1236 | 0.004578 | 0.032043 | 0.022888 | 0.09613 | -0.004578 | 122.0535 | 121.9116 | 0.036621 | 122.0627 | 122.1176 | 0.20599 | -0.022889 | 122.0764 | 121.9757 | -0.036622 | 122.0169 | 121.9849 | 0.009156 | -0.045777 | 122.0856 | 122.0261 | 122.0764 | -0.13733 | 122.0123 | 122.0032 | 122.1039 | -0.073243
1630.8125 | 122.3053 | -121.994 | 0.068665 | 0.0054168 | 0.024639 | 0.084753 | 0.02822 | -0.070391 | -0.028012 | 0.0022836 | 0.014954 | 0.014225 | -0.029602 | -0.0082929 | -0.0082544 | 0.0116 | 0.054932 | 0.07782 | 0.11444 | 0.12817 | 0.11444 | 0.10071 | -0.045776 | 0.041199 | 0.10986 | 0.013733 | 0.022888 | 0.036621 | 0.073242 | 0.004578 | 122.0947 | 121.9482 | 0.045776 | 122.0718 | 122.1222 | 0.17395 | -0.013733 | 122.0673 | 121.9986 | -0.045777 | 122.0352 | 122.0078 | 0.009155 | -0.032044 | 122.1085 | 122.049 | 122.1085 | -0.11444 | 122.0169 | 122.0306 | 122.1039 | -0.064087
1632.5469 | 122.2916 | -121.9849 | 0.091553 | 0.013046 | 0.023785 | 0.08283 | 0.027152 | -0.075304 | -0.026517 | 0.0027108 | 0.0073242 | 0.013798 | -0.031097 | -0.0080793 | -0.0069726 | 0.0077545 | 0.073242 | 0.07782 | 0.11444 | 0.13275 | 0.10986 | 0.086975 | -0.054932 | 0.041199 | 0.10071 | -0.027466 | 0.009155 | 0.032043 | 0.068665 | 0.009155 | 122.0718 | 121.9299 | 0.01831 | 122.0627 | 122.1176 | 0.18768 | -0.018311 | 122.0535 | 121.994 | -0.082398 | 122.0261 | 121.9574 | -0.036621 | -0.05951 | 122.0947 | 122.0581 | 122.0993 | -0.14649 | 121.994 | 122.0169 | 122.0856 | -0.082398
1634.3281 | 122.2641 | -122.0078 | 0.086975 | 0.0054168 | 0.027416 | 0.080907 | 0.022879 | -0.071673 | -0.022031 | 0.0059152 | -0.0003053 | 0.015934 | -0.029815 | -0.0072247 | -0.005691 | 0.0069001 | 0.14648 | 0.13733 | 0.15106 | 0.16022 | 0.091553 | 0.11444 | -0.032043 | 0.10529 | 0.11902 | 0.027466 | 0.009155 | -0.009155 | 0.10071 | 0.018311 | 122.1222 | 121.9757 | 0.004578 | 122.1451 | 122.168 | 0.19226 | 0.059509 | 122.1085 | 122.0261 | -0.07782 | 122.113 | 122.0352 | 0.009155 | -0.09613 | 122.0993 | 122.1542 | 122.1588 | -0.11902 | 122.0169 | 121.9986 | 122.1268 | -0.068664
1636.1094 | 122.1634 | -122.0444 | 0.11902 | 0.0054168 | 0.014385 | 0.085394 | 0.026083 | -0.0721 | -0.01904 | 0.0067696 | 0.014954 | 0.01743 | -0.030883 | -0.0089337 | -0.0012048 | 0.0096771 | 0.073242 | 0.050354 | 0.054932 | 0.10071 | 0.14191 | 0.073242 | -0.082397 | 0.041199 | 0.032043 | -0.10071 | 0.036621 | 0.059509 | 0.064087 | -0.022888 | 122.1176 | 121.962 | 0.022888 | 122.0947 | 122.1451 | 0.18311 | -0.045777 | 122.1085 | 122.0215 | -0.082398 | 122.0856 | 121.9437 | -0.07782 | -0.05951 | 122.1863 | 122.1176 | 122.0993 | -0.20142 | 122.081 | 122.1039 | 122.0764 | -0.14191
1637.9062 | 122.2733 | -122.0215 | 0.082397 | -0.0022127 | 0.019512 | 0.081548 | 0.025015 | -0.0721 | -0.02139 | 0.0097604 | 0.022583 | 0.015507 | -0.026825 | -0.0080793 | -0.001632 | 0.0098907 | 0.022888 | -0.004578 | 0.013733 | 0.073242 | 0.1236 | 0.068665 | -0.086975 | -0.004578 | 0.009155 | -0.09613 | 0.054932 | 0.064087 | 0.054932 | -0.027466 | 122.0901 | 121.9345 | 0.041199 | 122.0169 | 122.0947 | 0.16022 | -0.059509 | 122.0764 | 121.994 | -0.027465 | 122.0169 | 121.9254 | -0.068664 | -0.01831 | 122.1451 | 122.0444 | 122.0352 | -0.16937 | 122.0764 | 122.0856 | 122.0306 | -0.10986
1639.7031 | 122.3145 | -122.0215 | 0.086975 | 0.013046 | 0.022717 | 0.085607 | 0.027365 | -0.072741 | -0.028653 | 0.0063424 | 0.014954 | 0.011235 | -0.029175 | -0.0085065 | -0.0088952 | 0.0098907 | 0.11902 | 0.1831 | 0.19684 | 0.16022 | 0.073242 | 0.086975 | -0.032043 | 0.10529 | 0.21057 | 0.050354 | -0.004578 | 0.018311 | 0.09613 | 0 | 122.1085 | 121.9894 | -0.013733 | 122.2046 | 122.1817 | 0.19226 | 0.032044 | 122.1176 | 122.0215 | -0.091553 | 122.1268 | 122.0718 | 0.050354 | -0.068664 | 122.0947 | 122.1405 | 122.2183 | -0.11902 | 122.0169 | 122.0398 | 122.2321 | -0.086975
1641.4219 | 122.319 | -122.0398 | 0.082397 | 0.0054168 | 0.022503 | 0.088812 | 0.028433 | -0.073382 | -0.02844 | 0.0044198 | 0.014954 | 0.011875 | -0.028961 | -0.01107 | -0.0076136 | 0.0096771 | 0.12817 | 0.16479 | 0.1831 | 0.16937 | 0.091553 | 0.07782 | -0.032043 | 0.086975 | 0.18768 | 0.068665 | 0.004578 | 0.022888 | 0.09613 | 0.013733 | 122.1176 | 122.0078 | 0.009156 | 122.2046 | 122.2092 | 0.20142 | 0.045777 | 122.1359 | 122.0535 | -0.077819 | 122.1268 | 122.1085 | 0.054932 | -0.059509 | 122.1313 | 122.168 | 122.2229 | -0.11444 | 122.0444 | 122.0627 | 122.2275 | -0.068664
1643.2031 | 122.2733 | -122.0764 | 0.091553 | 0.013046 | 0.021008 | 0.08518 | 0.030783 | -0.071673 | -0.026303 | 0.0039926 | -0.0003053 | 0.0097391 | -0.02832 | -0.010643 | -0.0063318 | 0.0081817 | 0.13275 | 0.16022 | 0.18768 | 0.16937 | 0.091553 | 0.091553 | -0.036621 | 0.10071 | 0.17853 | 0.041199 | 0.013733 | 0.022888 | 0.07782 | 0.004578 | 122.168 | 122.0398 | 0 | 122.2366 | 122.2458 | 0.20599 | 0.041198 | 122.1542 | 122.081 | -0.07782 | 122.1771 | 122.1176 | 0.036621 | -0.068665 | 122.168 | 122.2092 | 122.2641 | -0.12817 | 122.0901 | 122.0993 | 122.2549 | -0.086975
1645 | 122.2092 | -122.0535 | 0.10529 | -0.0098417 | 0.021221 | 0.085821 | 0.02886 | -0.073809 | -0.026303 | 0.0052744 | 0.014954 | 0.013584 | -0.029175 | -0.0065839 | -0.0069726 | 0.0086091 | 0.11902 | 0.16022 | 0.16022 | 0.16937 | 0.10529 | 0.091553 | -0.027466 | 0.09613 | 0.17395 | 0.018311 | 0.032043 | 0.022888 | 0.11444 | 0.009155 | 122.1451 | 122.0261 | 0 | 122.2137 | 122.2229 | 0.19684 | 0.013733 | 122.168 | 122.0627 | -0.073243 | 122.1497 | 122.0718 | 0.009156 | -0.082398 | 122.1588 | 122.1725 | 122.2137 | -0.13275 | 122.0856 | 122.0764 | 122.2275 | -0.096131
1646.7969 | 122.2778 | -122.0444 | 0.073242 | -0.0022127 | 0.02293 | 0.084325 | 0.023306 | -0.073382 | -0.025235 | 0.0052744 | 0.0073242 | 0.014439 | -0.029388 | -0.0085065 | -0.005691 | 0.0096771 | 0.14191 | 0.13733 | 0.17395 | 0.15564 | 0.086975 | 0.09613 | -0.032043 | 0.09613 | 0.15106 | 0.027466 | 0.004578 | 0.041199 | 0.086975 | -0.004578 | 122.1405 | 122.0123 | 0.013733 | 122.1817 | 122.2 | 0.18768 | 0.068665 | 122.1313 | 122.0398 | -0.068664 | 122.1405 | 122.0718 | 0.032044 | -0.032043 | 122.1313 | 122.1863 | 122.2183 | -0.10529 | 122.049 | 122.0856 | 122.1954 | -0.07782
1648.5156 | 122.2549 | -122.049 | 0.10071 | 0.0054168 | 0.014385 | 0.084112 | 0.026938 | -0.072954 | -0.022672 | 0.0042062 | 0.0073242 | 0.014012 | -0.028106 | -0.010429 | -0.0029138 | 0.0098907 | 0.022888 | 0.009155 | 0.032043 | 0.09613 | 0.12817 | 0.045776 | -0.07782 | 0.018311 | 0.045776 | -0.10071 | 0.036621 | 0.064087 | 0.059509 | -0.013733 | 122.0947 | 121.9711 | 0.027466 | 122.0581 | 122.1451 | 0.17395 | -0.07782 | 122.1085 | 122.0352 | -0.064087 | 122.0673 | 121.9482 | -0.086975 | -0.036621 | 122.1771 | 122.0718 | 122.081 | -0.17853 | 122.0856 | 122.113 | 122.0947 | -0.11444
1650.2812 | 122.3511 | -122.0581 | 0.068665 | 0.0054168 | 0.022076 | 0.086034 | 0.02587 | -0.073809 | -0.029294 | 0.0050608 | 0.0073242 | 0.010594 | -0.029175 | -0.0089337 | -0.0069726 | 0.0098907 | 0.045776 | 0.082397 | 0.11444 | 0.14648 | 0.1236 | 0.086975 | -0.050354 | 0.041199 | 0.12817 | 0.004578 | 0.022888 | 0.045776 | 0.082397 | 0.018311 | 122.1451 | 122.0078 | 0.054931 | 122.1405 | 122.2046 | 0.19684 | -0.022889 | 122.1405 | 122.0764 | -0.045777 | 122.0993 | 122.0627 | -0.013733 | -0.022889 | 122.1817 | 122.1039 | 122.1725 | -0.11902 | 122.081 | 122.1039 | 122.1863 | -0.050354
1652.0781 | 122.2046 | -122.0673 | 0.10071 | 0.0054168 | 0.013531 | 0.08283 | 0.026083 | -0.071886 | -0.018186 | 0.0044198 | 0.0073242 | 0.015507 | -0.029602 | -0.0076519 | -0.0020594 | 0.0098907 | 0.10529 | 0.07782 | 0.082397 | 0.1236 | 0.11902 | 0.064087 | -0.064087 | 0.045776 | 0.068665 | -0.073242 | 0.036621 | 0.050354 | 0.082397 | -0.013733 | 122.1313 | 122.0032 | 0.018311 | 122.1451 | 122.1909 | 0.18768 | 0.004578 | 122.1497 | 122.0535 | -0.064087 | 122.113 | 121.994 | -0.059509 | -0.050354 | 122.1863 | 122.1725 | 122.1497 | -0.1648 | 122.1039 | 122.1176 | 122.1359 | -0.11444
1653.7969 | 122.3465 | -122.0535 | 0.086975 | 0.0054168 | 0.023785 | 0.086462 | 0.025656 | -0.07445 | -0.027799 | 0.006556 | 0.0073242 | 0.012516 | -0.027466 | -0.0093609 | -0.0059046 | 0.011173 | 0.09613 | 0.13275 | 0.15564 | 0.15564 | 0.09613 | 0.082397 | -0.064087 | 0.086975 | 0.17853 | 0.068665 | 0.018311 | 0.036621 | 0.086975 | 0.009155 | 122.1359 | 121.9894 | 0.009155 | 122.1863 | 122.2092 | 0.21973 | 0.009155 | 122.1405 | 122.0627 | -0.068664 | 122.1405 | 122.1222 | 0.05951 | -0.050354 | 122.1497 | 122.1497 | 122.2092 | -0.15106 | 122.0718 | 122.0901 | 122.2321 | -0.07782
1655.5781 | 122.2687 | -122.0581 | 0.082397 | 0.020676 | 0.018231 | 0.080907 | 0.02587 | -0.073168 | -0.020535 | 0.008265 | -0.0003053 | 0.014652 | -0.026184 | -0.0065839 | -0.003341 | 0.0096771 | 0.032043 | -0.018311 | 0.032043 | 0.07782 | 0.13275 | 0.050354 | -0.082397 | -0.009155 | 0 | -0.10529 | 0.041199 | 0.054932 | 0.064087 | -0.036621 | 122.1085 | 121.9757 | 0.050354 | 122.0398 | 122.1359 | 0.16022 | -0.050354 | 122.1222 | 122.0215 | -0.041198 | 122.0489 | 121.9528 | -0.068665 | -0.027465 | 122.1909 | 122.0901 | 122.0901 | -0.16479 | 122.0993 | 122.113 | 122.0581 | -0.11902
1657.3594 | 122.2961 | -122.0444 | 0.082397 | 0.013046 | 0.023785 | 0.086248 | 0.02587 | -0.074023 | -0.028867 | 0.0069834 | 0.0073242 | 0.011021 | -0.032806 | -0.0093609 | -0.0069726 | 0.010959 | 0.068665 | 0.11444 | 0.1236 | 0.12817 | 0.10071 | 0.082397 | -0.050354 | 0.041199 | 0.09613 | -0.004578 | 0.004578 | 0.050354 | 0.082397 | -0.009155 | 122.1268 | 121.994 | 0.018311 | 122.1588 | 122.1725 | 0.17853 | -0.013732 | 122.1268 | 122.0352 | -0.077819 | 122.0856 | 122.0398 | 0.004577 | -0.032043 | 122.1451 | 122.113 | 122.168 | -0.13275 | 122.049 | 122.0947 | 122.1405 | -0.091552
1659.0781 | 122.3648 | -122.0352 | 0.10529 | 0.013046 | 0.023571 | 0.087103 | 0.02886 | -0.071886 | -0.027371 | 0.0029244 | -0.0003053 | 0.011875 | -0.029175 | -0.010643 | -0.0086816 | 0.0081817 | 0.1236 | 0.16479 | 0.16937 | 0.17395 | 0.10071 | 0.09613 | -0.041199 | 0.10529 | 0.19684 | 0.068665 | 0.013733 | 0.013733 | 0.07782 | 0.022888 | 122.1313 | 121.994 | -0.004578 | 122.2 | 122.2092 | 0.21515 | 0.01831 | 122.113 | 122.0581 | -0.091553 | 122.1405 | 122.1039 | 0.045777 | -0.091553 | 122.1359 | 122.1588 | 122.2046 | -0.14649 | 122.049 | 122.049 | 122.2321 | -0.082398
1660.8594 | 122.2229 | -122.1039 | 0.11902 | 0.0054168 | 0.016735 | 0.087103 | 0.029929 | -0.07445 | -0.023099 | 0.0039926 | 0.0073242 | 0.012089 | -0.027466 | -0.012779 | -0.005691 | 0.0077545 | 0.10529 | 0.14191 | 0.16022 | 0.16937 | 0.10529 | 0.09613 | -0.045776 | 0.064087 | 0.1831 | 0.018311 | 0.013733 | 0.027466 | 0.068665 | -0.004578 | 122.2 | 122.0581 | -0.013733 | 122.2458 | 122.2733 | 0.21515 | -0.013733 | 122.1725 | 122.0993 | -0.10529 | 122.168 | 122.1222 | 0.022889 | -0.091553 | 122.2092 | 122.2092 | 122.2641 | -0.16479 | 122.1176 | 122.1313 | 122.287 | -0.1236
1662.6562 | 122.3877 | -122.0947 | 0.086975 | -0.0022127 | 0.022717 | 0.086248 | 0.02886 | -0.073595 | -0.028012 | 0.0046334 | 0.0073242 | 0.0090981 | -0.026825 | -0.0089337 | -0.0088952 | 0.011173 | 0.07782 | 0.10529 | 0.13733 | 0.14191 | 0.11902 | 0.086975 | -0.050354 | 0.064087 | 0.14191 | 0.027466 | 0.032043 | 0.027466 | 0.086975 | -0.004578 | 122.1817 | 122.0444 | 0.032044 | 122.2 | 122.2366 | 0.19226 | -0.009155 | 122.1817 | 122.0901 | -0.054932 | 122.1588 | 122.1222 | 0.032044 | -0.059509 | 122.2137 | 122.1725 | 122.2321 | -0.13733 | 122.1268 | 122.1222 | 122.2366 | -0.091553
1664.375 | 122.2961 | -122.0627 | 0.10071 | -0.0022127 | 0.016735 | 0.081335 | 0.025443 | -0.074663 | -0.018613 | 0.0033518 | 0.014954 | 0.016361 | -0.026397 | -0.0080793 | -0.00505 | 0.0083953 | 0.045776 | -0.018311 | 0.018311 | 0.07782 | 0.13733 | 0.064087 | -0.091553 | -0.004578 | 0 | -0.11902 | 0.050354 | 0.059509 | 0.068665 | -0.013733 | 122.1268 | 121.9711 | 0.036621 | 122.0444 | 122.1405 | 0.16937 | -0.054932 | 122.1313 | 122.049 | -0.050354 | 122.0581 | 121.9437 | -0.10529 | -0.041199 | 122.2 | 122.1085 | 122.081 | -0.19226 | 122.113 | 122.1222 | 122.0627 | -0.11444
1666.1406 | 122.3465 | -122.081 | 0.082397 | 0.0054168 | 0.022076 | 0.087743 | 0.029715 | -0.074877 | -0.027371 | 0.0046334 | 0.0073242 | 0.0093119 | -0.02832 | -0.010429 | -0.005691 | 0.010959 | 0.13733 | 0.20142 | 0.17853 | 0.1831 | 0.11444 | 0.086975 | -0.050354 | 0.10071 | 0.20142 | 0.050354 | 0.018311 | 0.036621 | 0.09613 | 0 | 122.168 | 122.0306 | 0.032044 | 122.2824 | 122.2641 | 0.23346 | 0.054932 | 122.1771 | 122.081 | -0.064086 | 122.1817 | 122.1313 | 0.050354 | -0.045776 | 122.1954 | 122.2183 | 122.2595 | -0.13275 | 122.0993 | 122.1176 | 122.2824 | -0.082397
1667.8594 | 122.2549 | -122.0947 | 0.09613 | -0.0022127 | 0.017162 | 0.081976 | 0.026938 | -0.072954 | -0.019895 | 0.0067696 | 0.014954 | 0.01743 | -0.028747 | -0.0065839 | -0.0048364 | 0.0086091 | 0.032043 | -0.018311 | 0.032043 | 0.082397 | 0.15564 | 0.045776 | -0.082397 | -0.013733 | -0.009155 | -0.1236 | 0.064087 | 0.091553 | 0.064087 | -0.036621 | 122.1405 | 122.0123 | 0.05951 | 122.0764 | 122.1771 | 0.16479 | -0.064087 | 122.1588 | 122.0581 | -0.032043 | 122.081 | 121.9711 | -0.086975 | -0.004577 | 122.2504 | 122.1268 | 122.1268 | -0.17853 | 122.1588 | 122.1863 | 122.0856 | -0.13275
1669.6406 | 122.3648 | -122.0627 | 0.091553 | 0.013046 | 0.021221 | 0.084539 | 0.028006 | -0.073809 | -0.026944 | 0.0057016 | -0.0003053 | 0.0095255 | -0.029815 | -0.010856 | -0.0061182 | 0.010959 | 0.12817 | 0.16937 | 0.16937 | 0.16022 | 0.082397 | 0.082397 | -0.032043 | 0.10071 | 0.20599 | 0.064087 | 0.013733 | 0.018311 | 0.091553 | 0.018311 | 122.1451 | 122.0306 | -0.009156 | 122.2321 | 122.2229 | 0.19226 | 0.036621 | 122.1542 | 122.081 | -0.07782 | 122.1634 | 122.1268 | 0.045776 | -0.073242 | 122.1451 | 122.1909 | 122.2321 | -0.1236 | 122.0764 | 122.081 | 122.2687 | -0.073242
1671.3594 | 122.3282 | -122.0673 | 0.07782 | 0.013046 | 0.025494 | 0.083898 | 0.026724 | -0.073382 | -0.025449 | 0.0035654 | -0.0003053 | 0.011448 | -0.027252 | -0.0053021 | -0.006759 | 0.0116 | 0.11444 | 0.13275 | 0.15106 | 0.15564 | 0.10986 | 0.09613 | -0.032043 | 0.068665 | 0.10529 | 0.009155 | 0.013733 | 0.027466 | 0.10529 | 0.022888 | 122.1634 | 122.0352 | 0.032043 | 122.2 | 122.2229 | 0.18768 | 0.036621 | 122.1725 | 122.0901 | -0.064087 | 122.1359 | 122.0764 | -0.013733 | -0.050354 | 122.1771 | 122.1817 | 122.2183 | -0.10986 | 122.081 | 122.0947 | 122.1725 | -0.054932
1673.1406 | 122.2458 | -122.1039 | 0.11902 | 0.013046 | 0.01524 | 0.084325 | 0.030142 | -0.071245 | -0.022458 | 0.006556 | -0.0003053 | 0.013798 | -0.026397 | -0.010215 | -0.0037684 | 0.0081817 | 0.041199 | 0.041199 | 0.068665 | 0.10071 | 0.13733 | 0.059509 | -0.091553 | -0.013733 | 0.050354 | -0.07782 | 0.054932 | 0.068665 | 0.054932 | -0.022888 | 122.1634 | 122.0123 | 0.01831 | 122.1451 | 122.2046 | 0.19226 | -0.07782 | 122.1588 | 122.081 | -0.064087 | 122.0901 | 122.0261 | -0.054932 | -0.050354 | 122.2412 | 122.1451 | 122.1725 | -0.21057 | 122.1588 | 122.1725 | 122.1542 | -0.14191
1674.8594 | 122.3923 | -122.0764 | 0.064087 | -0.0022127 | 0.023571 | 0.087103 | 0.027579 | -0.075732 | -0.029935 | 0.0057016 | 0.014954 | 0.010807 | -0.028534 | -0.0085065 | -0.0059046 | 0.012668 | 0.064087 | 0.09613 | 0.11444 | 0.14191 | 0.10986 | 0.07782 | -0.041199 | 0.064087 | 0.13733 | 0.013733 | 0 | 0.041199 | 0.09613 | 0.013733 | 122.1542 | 122.0352 | 0.045776 | 122.1725 | 122.2183 | 0.18311 | 0 | 122.1725 | 122.0901 | -0.064087 | 122.1405 | 122.0901 | 0 | -0.022888 | 122.1863 | 122.1405 | 122.1909 | -0.10529 | 122.0764 | 122.1176 | 122.2137 | -0.050354
1676.6406 | 122.3328 | -122.0947 | 0.086975 | 0.0054168 | 0.017376 | 0.08283 | 0.025656 | -0.074236 | -0.020108 | 0.0076242 | 0.014954 | 0.015293 | -0.028747 | -0.0082929 | -0.0035546 | 0.0077545 | 0.045776 | 0 | 0.027466 | 0.082397 | 0.13733 | 0.045776 | -0.064087 | 0.009155 | 0.013733 | -0.10071 | 0.041199 | 0.068665 | 0.068665 | -0.032043 | 122.1405 | 122.0306 | 0.050354 | 122.0947 | 122.1771 | 0.14648 | -0.041199 | 122.1634 | 122.0627 | -0.045776 | 122.1039 | 121.994 | -0.068665 | -0.01831 | 122.2321 | 122.1405 | 122.1222 | -0.15106 | 122.1359 | 122.1634 | 122.1085 | -0.11902
1678.4375 | 122.3923 | -122.0764 | 0.082397 | -0.0098417 | 0.020794 | 0.087957 | 0.026297 | -0.071886 | -0.02844 | 0.0052744 | 0.014954 | 0.01038 | -0.028534 | -0.0093609 | -0.008468 | 0.0083953 | 0.10529 | 0.15564 | 0.15564 | 0.17395 | 0.10529 | 0.082397 | -0.032043 | 0.10071 | 0.1831 | 0.064087 | 0.009155 | 0.018311 | 0.09613 | 0.004578 | 122.1588 | 122.0444 | 0.022889 | 122.2321 | 122.2504 | 0.20599 | 0.022889 | 122.1725 | 122.081 | -0.073242 | 122.1771 | 122.1405 | 0.059509 | -0.064086 | 122.1817 | 122.1817 | 122.2321 | -0.11444 | 122.0856 | 122.0947 | 122.2595 | -0.077819
1680.2188 | 122.3328 | -122.113 | 0.091553 | -0.0022127 | 0.020794 | 0.082403 | 0.028433 | -0.073809 | -0.025449 | 0.0046334 | 0.0073242 | 0.012943 | -0.026184 | -0.0091473 | -0.0059046 | 0.0116 | 0.10529 | 0.10986 | 0.15106 | 0.13275 | 0.086975 | 0.09613 | -0.027466 | 0.059509 | 0.11902 | -0.004578 | 0.009155 | 0.032043 | 0.10071 | 0.013733 | 122.2092 | 122.0856 | -0.004578 | 122.2229 | 122.2458 | 0.16022 | 0.013733 | 122.2137 | 122.1268 | -0.082398 | 122.1725 | 122.1085 | -0.018311 | -0.05951 | 122.2 | 122.2183 | 122.2641 | -0.11902 | 122.1222 | 122.1451 | 122.2321 | -0.07782
1682.0156 | 122.2412 | -122.1313 | 0.10986 | 0.013046 | 0.01289 | 0.081976 | 0.025656 | -0.072741 | -0.020749 | 0.005488 | 0.014954 | 0.017857 | -0.025116 | -0.0067975 | -0.0041956 | 0.0092499 | 0.064087 | 0.004578 | 0.036621 | 0.10071 | 0.13275 | 0.054932 | -0.086975 | 0.013733 | 0.022888 | -0.11902 | 0.050354 | 0.059509 | 0.064087 | -0.032043 | 122.1863 | 122.0444 | 0.022888 | 122.1359 | 122.2321 | 0.18768 | -0.045776 | 122.1954 | 122.0993 | -0.059509 | 122.1451 | 122.0123 | -0.086976 | -0.050354 | 122.2641 | 122.1954 | 122.168 | -0.19684 | 122.1817 | 122.1909 | 122.1542 | -0.14191
1683.7344 | 122.3923 | -122.0764 | 0.073242 | 0.0054168 | 0.022503 | 0.086034 | 0.028006 | -0.071459 | -0.028867 | 0.0044198 | 0.0073242 | 0.0086709 | -0.02832 | -0.0097883 | -0.0074 | 0.010745 | 0.13275 | 0.13275 | 0.16937 | 0.16022 | 0.073242 | 0.086975 | -0.032043 | 0.082397 | 0.19226 | 0.073242 | 0.009155 | 0.032043 | 0.10986 | 0.027466 | 122.1634 | 122.0444 | 0 | 122.2092 | 122.2366 | 0.19226 | 0.059509 | 122.1863 | 122.1039 | -0.064087 | 122.1588 | 122.1497 | 0.045776 | -0.041199 | 122.1497 | 122.2092 | 122.2458 | -0.10529 | 122.0856 | 122.1085 | 122.2687 | -0.045776
1685.5 | 122.3007 | -122.1039 | 0.10071 | 0.0054168 | 0.013104 | 0.084753 | 0.026938 | -0.071673 | -0.018826 | 0.0059152 | 0.0073242 | 0.015721 | -0.026184 | -0.0070111 | -0.0029138 | 0.0064727 | 0.082397 | 0.050354 | 0.073242 | 0.11902 | 0.12817 | 0.073242 | -0.064087 | 0.054932 | 0.10071 | -0.045776 | 0.050354 | 0.054932 | 0.059509 | -0.013733 | 122.1771 | 122.0398 | 0.027466 | 122.1542 | 122.2229 | 0.18311 | -0.018311 | 122.1634 | 122.0901 | -0.050354 | 122.1588 | 122.0581 | -0.032043 | -0.045776 | 122.2321 | 122.1863 | 122.1771 | -0.1648 | 122.1542 | 122.1588 | 122.2046 | -0.11444
1687.2812 | 122.3465 | -122.1176 | 0.082397 | 0.0054168 | 0.024426 | 0.084325 | 0.023947 | -0.072314 | -0.025022 | 0.0059152 | -0.0003053 | 0.01273 | -0.028106 | -0.010429 | -0.0069726 | 0.013095 | 0.12817 | 0.14648 | 0.16937 | 0.17395 | 0.07782 | 0.09613 | -0.022888 | 0.10986 | 0.16022 | 0.027466 | 0.004578 | 0.018311 | 0.09613 | 0.022888 | 122.2137 | 122.0947 | -0.004577 | 122.2641 | 122.2916 | 0.19684 | 0.045777 | 122.2137 | 122.1405 | -0.077819 | 122.2275 | 122.1451 | 0.004578 | -0.064086 | 122.1954 | 122.2458 | 122.287 | -0.10528 | 122.1222 | 122.1359 | 122.2778 | -0.059509
1689.0625 | 122.2641 | -122.1451 | 0.10986 | 0.0054168 | 0.016094 | 0.08518 | 0.02822 | -0.0721 | -0.025449 | 0.0046334 | -0.0079343 | 0.014225 | -0.027679 | -0.0087201 | -0.0052636 | 0.011173 | 0.050354 | 0.068665 | 0.068665 | 0.10529 | 0.12817 | 0.068665 | -0.073242 | -0.013733 | 0.064087 | -0.073242 | 0.050354 | 0.050354 | 0.054932 | -0.041199 | 122.2137 | 122.0718 | 0.018311 | 122.2137 | 122.2504 | 0.17853 | -0.059509 | 122.2 | 122.1039 | -0.059509 | 122.1313 | 122.0718 | -0.032043 | -0.059509 | 122.2733 | 122.1954 | 122.2137 | -0.18311 | 122.1954 | 122.1954 | 122.2092 | -0.15106
1690.8438 | 122.3328 | -122.1085 | 0.10071 | 0.013046 | 0.016308 | 0.082189 | 0.024802 | -0.074236 | -0.021817 | 0.004847 | 0.014954 | 0.014225 | -0.028106 | -0.0065839 | -0.0044092 | 0.0094635 | 0.032043 | -0.032043 | 0.018311 | 0.082397 | 0.13275 | 0.059509 | -0.068665 | -0.013733 | 0 | -0.10529 | 0.041199 | 0.059509 | 0.054932 | -0.018311 | 122.168 | 122.0398 | 0.032043 | 122.0764 | 122.1909 | 0.15106 | -0.068665 | 122.1634 | 122.0901 | -0.059509 | 122.0947 | 122.0032 | -0.086975 | -0.041199 | 122.2412 | 122.1405 | 122.1268 | -0.16937 | 122.1497 | 122.168 | 122.1085 | -0.11902
1692.5625 | 122.3465 | -122.1222 | 0.082397 | 0.0054168 | 0.023144 | 0.083685 | 0.026724 | -0.071245 | -0.026517 | 0.004847 | 0.022583 | 0.01038 | -0.029602 | -0.010643 | -0.0063318 | 0.010532 | 0.11902 | 0.11902 | 0.15106 | 0.15106 | 0.082397 | 0.10071 | -0.022888 | 0.050354 | 0.12817 | 0.004578 | 0.013733 | 0.032043 | 0.082397 | 0.022888 | 122.2229 | 122.0993 | 0 | 122.2412 | 122.2733 | 0.17395 | 0.036622 | 122.2046 | 122.1451 | -0.068664 | 122.1725 | 122.1268 | -0.01831 | -0.050354 | 122.2046 | 122.2412 | 122.2733 | -0.10528 | 122.1359 | 122.1542 | 122.2504 | -0.059509
1694.3281 | 122.3648 | -122.1085 | 0.091553 | 0.013046 | 0.021649 | 0.087103 | 0.026083 | -0.075091 | -0.027158 | 0.0046334 | 0.0073242 | 0.011021 | -0.03067 | -0.010002 | -0.0086816 | 0.010959 | 0.07782 | 0.086975 | 0.1236 | 0.11444 | 0.09613 | 0.086975 | -0.032043 | 0.018311 | 0.091553 | -0.004578 | 0.022888 | 0.032043 | 0.07782 | 0.022888 | 122.1954 | 122.0764 | 0.004577 | 122.1954 | 122.2229 | 0.14648 | -0.013733 | 122.1863 | 122.1313 | -0.068665 | 122.1268 | 122.1039 | -0.027466 | -0.05951 | 122.2046 | 122.1863 | 122.2321 | -0.1236 | 122.1313 | 122.1405 | 122.2 | -0.068665
1696.1094 | 122.2549 | -122.168 | 0.11444 | -0.0022127 | 0.013531 | 0.084966 | 0.024802 | -0.071673 | -0.019467 | 0.0050608 | 0.0073242 | 0.017002 | -0.030029 | -0.0093609 | -0.0020594 | 0.0094635 | 0.09613 | 0.022888 | 0.073242 | 0.11444 | 0.12817 | 0.059509 | -0.073242 | 0.022888 | 0.050354 | -0.082397 | 0.022888 | 0.064087 | 0.050354 | -0.041199 | 122.2275 | 122.0947 | 0.013733 | 122.1909 | 122.2824 | 0.18768 | -0.018311 | 122.2183 | 122.1268 | -0.091553 | 122.1909 | 122.0856 | -0.041198 | -0.050354 | 122.2961 | 122.2641 | 122.2412 | -0.18768 | 122.1909 | 122.2321 | 122.2183 | -0.15564
1697.8906 | 122.3236 | -122.1359 | 0.068665 | 0.0054168 | 0.020153 | 0.080267 | 0.02352 | -0.071459 | -0.02139 | 0.0074106 | 0.030213 | 0.014652 | -0.029815 | -0.0078657 | -0.0044092 | 0.0079681 | 0.013733 | -0.027466 | 0.022888 | 0.068665 | 0.14648 | 0.054932 | -0.082397 | -0.013733 | 0 | -0.091553 | 0.041199 | 0.07782 | 0.064087 | -0.004578 | 122.1909 | 122.0535 | 0.077819 | 122.1085 | 122.2046 | 0.15106 | -0.054932 | 122.2 | 122.1313 | -0.027466 | 122.1222 | 122.0444 | -0.086975 | 0.009155 | 122.2824 | 122.1497 | 122.1588 | -0.15106 | 122.1771 | 122.2137 | 122.1359 | -0.073243
1699.6719 | 122.3969 | -122.1222 | 0.086975 | 0.0054168 | 0.022503 | 0.086462 | 0.028006 | -0.07445 | -0.02908 | 0.0035654 | -0.0003053 | 0.011021 | -0.027038 | -0.0095745 | -0.0076136 | 0.011386 | 0.059509 | 0.059509 | 0.10986 | 0.13275 | 0.091553 | 0.073242 | -0.054932 | 0.022888 | 0.091553 | -0.009155 | 0.022888 | 0.041199 | 0.07782 | 0.013733 | 122.1954 | 122.0673 | 0.004578 | 122.1817 | 122.2549 | 0.18768 | -0.027466 | 122.2 | 122.1359 | -0.064087 | 122.1451 | 122.113 | -0.022888 | -0.045776 | 122.2137 | 122.1817 | 122.2321 | -0.14191 | 122.1451 | 122.1634 | 122.2137 | -0.073242
1701.4531 | 122.319 | -122.1451 | 0.091553 | -0.0022127 | 0.015453 | 0.083044 | 0.030783 | -0.072741 | -0.019895 | 0.0046334 | 0.022583 | 0.015721 | -0.024902 | -0.0070111 | -0.0046228 | 0.0086091 | 0.07782 | 0.050354 | 0.082397 | 0.14191 | 0.13275 | 0.054932 | -0.073242 | 0.041199 | 0.09613 | -0.059509 | 0.050354 | 0.050354 | 0.050354 | -0.018311 | 122.2 | 122.0718 | 0.041198 | 122.1954 | 122.287 | 0.21515 | -0.013733 | 122.1954 | 122.1268 | -0.041199 | 122.1863 | 122.0856 | -0.041198 | -0.041199 | 122.2778 | 122.2229 | 122.2275 | -0.16479 | 122.1954 | 122.1954 | 122.2412 | -0.10986
1703.1719 | 122.3785 | -122.1405 | 0.09613 | 0.020676 | 0.018231 | 0.084539 | 0.02886 | -0.072527 | -0.028012 | 0.0067696 | 0.014954 | 0.010594 | -0.027679 | -0.0085065 | -0.0074 | 0.012027 | 0.10071 | 0.16022 | 0.1831 | 0.16937 | 0.10071 | 0.07782 | -0.045776 | 0.10071 | 0.20599 | 0.050354 | -0.004578 | 0.004578 | 0.086975 | 0.018311 | 122.2183 | 122.0947 | 0.004578 | 122.3007 | 122.3099 | 0.21515 | 0.004578 | 122.2275 | 122.1588 | -0.10071 | 122.2412 | 122.1909 | 0.032043 | -0.091552 | 122.2412 | 122.2412 | 122.3236 | -0.14191 | 122.1359 | 122.1451 | 122.3465 | -0.077819
1704.9375 | 122.287 | -122.1817 | 0.1236 | 0.013046 | 0.016949 | 0.085394 | 0.027579 | -0.070818 | -0.024808 | 0.0029244 | 0.014954 | 0.013798 | -0.028106 | -0.010215 | -0.0052636 | 0.013309 | 0.050354 | 0.073242 | 0.073242 | 0.10071 | 0.11444 | 0.064087 | -0.064087 | -0.022888 | 0.054932 | -0.073242 | 0.054932 | 0.054932 | 0.045776 | -0.022888 | 122.2458 | 122.1176 | -0.009155 | 122.2549 | 122.2824 | 0.1648 | -0.073242 | 122.2275 | 122.1588 | -0.068664 | 122.1588 | 122.1085 | -0.050354 | -0.068664 | 122.2961 | 122.2321 | 122.2549 | -0.18768 | 122.2366 | 122.2366 | 122.2366 | -0.14648
1706.7188 | 122.4152 | -122.1405 | 0.086975 | -0.0022127 | 0.022503 | 0.086462 | 0.029501 | -0.0721 | -0.027585 | 0.0035654 | -0.0003053 | 0.011021 | -0.026825 | -0.0078657 | -0.011031 | 0.011173 | 0.10986 | 0.17395 | 0.17853 | 0.16022 | 0.10071 | 0.07782 | -0.041199 | 0.082397 | 0.21057 | 0.059509 | -0.004578 | 0.027466 | 0.091553 | 0.013733 | 122.2183 | 122.0993 | 0.013733 | 122.3145 | 122.3007 | 0.20142 | 0.022888 | 122.2321 | 122.1542 | -0.091553 | 122.2229 | 122.2 | 0.045776 | -0.059509 | 122.2412 | 122.2504 | 122.319 | -0.12817 | 122.1359 | 122.168 | 122.3511 | -0.073242
1708.5 | 122.4106 | -122.1268 | 0.09613 | 0.0054168 | 0.021008 | 0.084753 | 0.029288 | -0.071673 | -0.028867 | 0.0029244 | -0.0003053 | 0.011021 | -0.027252 | -0.0059429 | -0.006759 | 0.0098907 | 0.054932 | 0.082397 | 0.10986 | 0.14191 | 0.10071 | 0.086975 | -0.027466 | 0.027466 | 0.10071 | -0.009155 | 0.004578 | 0.032043 | 0.09613 | 0.013733 | 122.2137 | 122.0993 | 0.004578 | 122.2092 | 122.2687 | 0.16937 | -0.041198 | 122.2229 | 122.1405 | -0.091552 | 122.1542 | 122.1176 | -0.022888 | -0.064087 | 122.2275 | 122.1817 | 122.2366 | -0.1236 | 122.1313 | 122.1588 | 122.2275 | -0.082397
1710.2031 | 122.2916 | -122.168 | 0.10071 | 0.0054168 | 0.01524 | 0.086248 | 0.026297 | -0.071459 | -0.025662 | 0.0050608 | 0.0073242 | 0.012943 | -0.028106 | -0.0080793 | -0.0044092 | 0.0081817 | 0.086975 | 0.10986 | 0.10529 | 0.14648 | 0.11444 | 0.073242 | -0.054932 | 0.004578 | 0.091553 | -0.054932 | 0.041199 | 0.054932 | 0.082397 | -0.009155 | 122.2412 | 122.113 | 0.013733 | 122.2778 | 122.3145 | 0.20142 | -0.013733 | 122.2504 | 122.1588 | -0.059509 | 122.1725 | 122.113 | -0.045777 | -0.045776 | 122.2824 | 122.2549 | 122.2733 | -0.15564 | 122.2092 | 122.2229 | 122.2595 | -0.10986
1711.9688 | 122.3053 | -122.168 | 0.11444 | -0.0022127 | 0.016949 | 0.084325 | 0.025015 | -0.071673 | -0.026517 | 0.0033518 | 0.014954 | 0.012516 | -0.029602 | -0.0085065 | -0.0080408 | 0.010104 | 0.10529 | 0.12817 | 0.13275 | 0.15564 | 0.09613 | 0.082397 | -0.073242 | 0.032043 | 0.11444 | -0.045776 | 0.027466 | 0.054932 | 0.068665 | 0 | 122.2504 | 122.0947 | -0.018311 | 122.2961 | 122.3236 | 0.22888 | -0.009155 | 122.2366 | 122.168 | -0.086975 | 122.2 | 122.1222 | -0.045776 | -0.059509 | 122.2641 | 122.2733 | 122.3007 | -0.18768 | 122.1954 | 122.2229 | 122.2824 | -0.11444
1713.7344 | 122.374 | -122.1542 | 0.091553 | 0.013046 | 0.022503 | 0.083898 | 0.026938 | -0.073168 | -0.026303 | 0.0057016 | 0.022583 | 0.01273 | -0.027252 | -0.0080793 | -0.0063318 | 0.0090363 | 0.10529 | 0.11444 | 0.14648 | 0.1236 | 0.091553 | 0.091553 | -0.027466 | 0.059509 | 0.10071 | -0.013733 | 0.018311 | 0.013733 | 0.10071 | 0.004578 | 122.2458 | 122.1268 | 0 | 122.2687 | 122.2778 | 0.15106 | 0.013733 | 122.2549 | 122.1588 | -0.073242 | 122.2137 | 122.1405 | -0.018311 | -0.07782 | 122.2458 | 122.2595 | 122.3007 | -0.11902 | 122.1725 | 122.168 | 122.2549 | -0.086975
1715.5156 | 122.4197 | -122.1313 | 0.073242 | -0.0022127 | 0.024639 | 0.085394 | 0.029288 | -0.074877 | -0.026944 | 0.005488 | 0.014954 | 0.012516 | -0.026397 | -0.0093609 | -0.0088952 | 0.010104 | 0.1236 | 0.16022 | 0.19226 | 0.16937 | 0.082397 | 0.082397 | -0.036621 | 0.11444 | 0.19684 | 0.068665 | 0.009155 | 0.018311 | 0.10071 | -0.004578 | 122.2137 | 122.0947 | 0.009155 | 122.2916 | 122.3007 | 0.20599 | 0.050354 | 122.2321 | 122.1268 | -0.064087 | 122.2458 | 122.2 | 0.073243 | -0.054931 | 122.2137 | 122.2549 | 122.3236 | -0.10986 | 122.1405 | 122.1497 | 122.3282 | -0.07782
1717.2344 | 122.3053 | -122.168 | 0.11902 | 0.0054168 | 0.013104 | 0.084112 | 0.026724 | -0.071886 | -0.017331 | 0.0095468 | 0.014954 | 0.015293 | -0.024688 | -0.0046613 | -0.0027002 | 0.0083953 | 0.12817 | 0.068665 | 0.09613 | 0.11902 | 0.13275 | 0.064087 | -0.054932 | 0.059509 | 0.091553 | -0.068665 | 0.054932 | 0.059509 | 0.073242 | 0.004578 | 122.2321 | 122.113 | 0.013732 | 122.2366 | 122.287 | 0.17395 | 0.009155 | 122.2412 | 122.1725 | -0.064087 | 122.2275 | 122.0993 | -0.073243 | -0.05951 | 122.3007 | 122.2961 | 122.2641 | -0.17395 | 122.2229 | 122.2275 | 122.2595 | -0.11444
1719.0312 | 122.438 | -122.1497 | 0.086975 | 0.0054168 | 0.021862 | 0.086034 | 0.028006 | -0.070818 | -0.02844 | 0.0039926 | -0.0003053 | 0.011662 | -0.027679 | -0.0065839 | -0.0082544 | 0.010318 | 0.12817 | 0.17395 | 0.17395 | 0.16937 | 0.082397 | 0.082397 | -0.036621 | 0.1236 | 0.21057 | 0.068665 | 0.009155 | 0.009155 | 0.09613 | 0.013733 | 122.2321 | 122.113 | -0.004578 | 122.3236 | 122.319 | 0.20599 | 0.041199 | 122.2458 | 122.1634 | -0.07782 | 122.2733 | 122.2183 | 0.054932 | -0.07782 | 122.2321 | 122.2778 | 122.3236 | -0.1236 | 122.1588 | 122.1588 | 122.3602 | -0.073242
1720.8125 | 122.3007 | -122.1725 | 0.10529 | 0.0054168 | 0.01289 | 0.083257 | 0.029288 | -0.071673 | -0.01669 | 0.0076242 | 0.0073242 | 0.016148 | -0.026184 | -0.0050885 | -0.0048364 | 0.0073273 | 0.1236 | 0.082397 | 0.086975 | 0.1236 | 0.11902 | 0.068665 | -0.064087 | 0.054932 | 0.07782 | -0.054932 | 0.022888 | 0.064087 | 0.07782 | -0.009155 | 122.2412 | 122.1085 | 0.013733 | 122.2549 | 122.2961 | 0.18768 | 0.01831 | 122.2504 | 122.1634 | -0.082398 | 122.2275 | 122.1176 | -0.045777 | -0.041199 | 122.2916 | 122.2961 | 122.2595 | -0.16937 | 122.1954 | 122.2366 | 122.2504 | -0.11444
1722.5312 | 122.4609 | -122.1405 | 0.073242 | 0.0054168 | 0.023998 | 0.08518 | 0.029715 | -0.071245 | -0.028653 | 0.0044198 | 0.0073242 | 0.010594 | -0.028747 | -0.0076519 | -0.006759 | 0.011386 | 0.045776 | 0.082397 | 0.1236 | 0.1236 | 0.091553 | 0.091553 | -0.041199 | 0.059509 | 0.14191 | 0.018311 | 0.004578 | 0.036621 | 0.10071 | 0.013733 | 122.2321 | 122.0993 | 0.018311 | 122.2229 | 122.2641 | 0.16479 | -0.027466 | 122.2412 | 122.1542 | -0.068664 | 122.2 | 122.1588 | 0.004578 | -0.036621 | 122.2321 | 122.1863 | 122.2641 | -0.11444 | 122.1451 | 122.1771 | 122.2824 | -0.059509
1724.3125 | 122.2916 | -122.1909 | 0.091553 | 0.0054168 | 0.013531 | 0.082616 | 0.025443 | -0.073595 | -0.020749 | 0.0046334 | 0.022583 | 0.019779 | -0.027466 | -0.0057293 | -0.003341 | 0.0077545 | 0.068665 | 0.036621 | 0.064087 | 0.10529 | 0.11902 | 0.054932 | -0.073242 | 0.032043 | 0.045776 | -0.10986 | 0.054932 | 0.059509 | 0.064087 | -0.018311 | 122.2458 | 122.1176 | 0.027466 | 122.2275 | 122.2961 | 0.17853 | -0.022888 | 122.2549 | 122.1725 | -0.036621 | 122.2229 | 122.081 | -0.091552 | -0.032044 | 122.3099 | 122.2595 | 122.2549 | -0.16479 | 122.2458 | 122.2504 | 122.2366 | -0.10986
1726.0312 | 122.3923 | -122.1588 | 0.09613 | -0.0022127 | 0.022076 | 0.081976 | 0.026297 | -0.07445 | -0.026303 | 0.0022836 | 0.0073242 | 0.012089 | -0.028747 | -0.0076519 | -0.0071862 | 0.011813 | 0.11444 | 0.11902 | 0.16479 | 0.14648 | 0.07782 | 0.091553 | -0.050354 | 0.073242 | 0.13275 | 0.004578 | 0.013733 | 0.022888 | 0.10071 | 0.013733 | 122.2504 | 122.1085 | -0.01831 | 122.2778 | 122.3053 | 0.19684 | 0.018311 | 122.2595 | 122.1725 | -0.082397 | 122.2321 | 122.1634 | -0.009155 | -0.073242 | 122.2366 | 122.2733 | 122.3236 | -0.14648 | 122.1725 | 122.1817 | 122.2916 | -0.082397
1727.8125 | 122.3282 | -122.2137 | 0.10529 | -0.0022127 | 0.014599 | 0.083044 | 0.029929 | -0.073382 | -0.023526 | 0.004847 | -0.0003053 | 0.016148 | -0.027038 | -0.0067975 | -0.006759 | 0.0098907 | 0.018311 | 0.004578 | 0.027466 | 0.07782 | 0.14648 | 0.059509 | -0.086975 | -0.036621 | 0.050354 | -0.07782 | 0.068665 | 0.068665 | 0.059509 | -0.018311 | 122.2733 | 122.1268 | 0.041198 | 122.2183 | 122.2916 | 0.16479 | -0.086975 | 122.2733 | 122.1954 | -0.036621 | 122.1771 | 122.1359 | -0.059509 | -0.036621 | 122.3602 | 122.2321 | 122.2412 | -0.19226 | 122.2824 | 122.2824 | 122.2641 | -0.1236
1729.5938 | 122.4472 | -122.1634 | 0.086975 | 0.013046 | 0.019726 | 0.080694 | 0.025656 | -0.06975 | -0.023313 | 0.0050608 | -0.0003053 | 0.01508 | -0.026611 | -0.0061567 | -0.003341 | 0.010959 | 0.050354 | 0.018311 | 0.050354 | 0.09613 | 0.13275 | 0.050354 | -0.059509 | 0.054932 | 0.082397 | -0.032043 | 0.041199 | 0.036621 | 0.07782 | 0.004578 | 122.2137 | 122.1039 | 0.045776 | 122.1817 | 122.2595 | 0.15564 | -0.036621 | 122.2412 | 122.168 | -0.045776 | 122.2183 | 122.1313 | -0.036621 | -0.050354 | 122.2961 | 122.2137 | 122.2137 | -0.14648 | 122.2046 | 122.2 | 122.2458 | -0.082397
1731.375 | 122.3145 | -122.1909 | 0.11902 | 0.013046 | 0.014385 | 0.084325 | 0.027365 | -0.069964 | -0.025662 | 0.0027108 | 0.0073242 | 0.013371 | -0.027679 | -0.0087201 | -0.0065454 | 0.012027 | 0.064087 | 0.082397 | 0.10071 | 0.1236 | 0.11444 | 0.068665 | -0.054932 | 0 | 0.086975 | -0.059509 | 0.041199 | 0.064087 | 0.073242 | -0.018311 | 122.2595 | 122.1359 | -0.004578 | 122.2733 | 122.3145 | 0.17853 | -0.054932 | 122.2641 | 122.1725 | -0.07782 | 122.1909 | 122.1313 | -0.041198 | -0.054932 | 122.3053 | 122.2549 | 122.2916 | -0.17395 | 122.2321 | 122.2549 | 122.2778 | -0.13733
1733.1094 | 122.374 | -122.2 | 0.10986 | -0.0022127 | 0.012676 | 0.083044 | 0.026297 | -0.073382 | -0.021604 | 0.0069834 | 0.022583 | 0.015934 | -0.027466 | -0.0055157 | -0.003341 | 0.0088227 | 0.073242 | 0.059509 | 0.082397 | 0.12817 | 0.13275 | 0.059509 | -0.064087 | 0.036621 | 0.091553 | -0.036621 | 0.032043 | 0.054932 | 0.068665 | -0.018311 | 122.2595 | 122.1359 | 0.022888 | 122.2595 | 122.3282 | 0.19226 | -0.036621 | 122.2687 | 122.1817 | -0.07782 | 122.2366 | 122.1634 | -0.01831 | -0.054931 | 122.3328 | 122.2733 | 122.2824 | -0.17395 | 122.2321 | 122.2549 | 122.2916 | -0.12817
1734.8906 | 122.3236 | -122.168 | 0.091553 | -0.0022127 | 0.013317 | 0.083044 | 0.024588 | -0.072741 | -0.020963 | 0.0078378 | -0.0003053 | 0.017643 | -0.027252 | -0.0074383 | -0.0037684 | 0.011173 | 0.091553 | 0.068665 | 0.09613 | 0.12817 | 0.11444 | 0.064087 | -0.041199 | 0.041199 | 0.09613 | -0.064087 | 0.032043 | 0.054932 | 0.073242 | -0.009155 | 122.2321 | 122.1268 | 0.022888 | 122.2366 | 122.2961 | 0.16937 | 0 | 122.2412 | 122.1588 | -0.05951 | 122.2092 | 122.1039 | -0.054932 | -0.036621 | 122.2824 | 122.2595 | 122.2641 | -0.13275 | 122.2 | 122.2229 | 122.2641 | -0.10071
1736.6719 | 122.3053 | -122.2046 | 0.11902 | -0.0022127 | 0.013958 | 0.082403 | 0.024802 | -0.072527 | -0.02139 | 0.005488 | 0.014954 | 0.016148 | -0.026611 | -0.0078657 | -0.003341 | 0.010959 | 0.041199 | 0.032043 | 0.054932 | 0.09613 | 0.13275 | 0.064087 | -0.07782 | 0.004578 | 0.027466 | -0.10986 | 0.050354 | 0.050354 | 0.064087 | -0.013733 | 122.2687 | 122.1268 | 0.013732 | 122.2366 | 122.3007 | 0.17395 | -0.07782 | 122.2687 | 122.1909 | -0.068665 | 122.2092 | 122.0947 | -0.09613 | -0.068665 | 122.3373 | 122.2458 | 122.2595 | -0.19684 | 122.2549 | 122.2549 | 122.2321 | -0.13275
1738.4531 | 122.4243 | -122.1634 | 0.054932 | 0.0054168 | 0.022289 | 0.083685 | 0.025015 | -0.073595 | -0.027585 | 0.0076242 | 0.0073242 | 0.012516 | -0.029388 | -0.0091473 | -0.0063318 | 0.010532 | 0.09613 | 0.15106 | 0.16937 | 0.16022 | 0.082397 | 0.09613 | -0.018311 | 0.07782 | 0.15564 | 0.032043 | 0.004578 | 0.018311 | 0.082397 | 0.022888 | 122.2595 | 122.1451 | 0.027465 | 122.3145 | 122.3236 | 0.17853 | 0.041198 | 122.2458 | 122.1863 | -0.050354 | 122.2412 | 122.1954 | 0.009155 | -0.036621 | 122.2458 | 122.2595 | 122.3328 | -0.073243 | 122.168 | 122.1817 | 122.319 | -0.032044
1740.2188 | 122.4106 | -122.1817 | 0.091553 | 0.013046 | 0.02293 | 0.086034 | 0.027579 | -0.074663 | -0.027158 | 0.0042062 | 0.014954 | 0.012303 | -0.029388 | -0.0085065 | -0.0063318 | 0.012027 | 0.07782 | 0.091553 | 0.1236 | 0.11902 | 0.086975 | 0.086975 | -0.032043 | 0.018311 | 0.10986 | 0.004578 | 0.009155 | 0.032043 | 0.086975 | 0 | 122.2687 | 122.1497 | -0.004578 | 122.2733 | 122.3007 | 0.15106 | -0.013733 | 122.2687 | 122.1817 | -0.082398 | 122.2 | 122.1863 | 0.004578 | -0.05951 | 122.2687 | 122.2595 | 122.3053 | -0.1236 | 122.1909 | 122.2137 | 122.2916 | -0.091553
1742 | 122.3282 | -122.2137 | 0.10986 | -0.0098417 | 0.012463 | 0.084325 | 0.026938 | -0.073382 | -0.019681 | 0.006556 | 0.0073242 | 0.016361 | -0.028961 | -0.0082929 | -0.0037684 | 0.0092499 | 0.032043 | 0.018311 | 0.041199 | 0.10529 | 0.13275 | 0.068665 | -0.07782 | -0.013733 | 0.027466 | -0.10986 | 0.054932 | 0.068665 | 0.082397 | -0.018311 | 122.2824 | 122.1359 | 0.022888 | 122.2321 | 122.319 | 0.18311 | -0.07782 | 122.2961 | 122.1954 | -0.054931 | 122.2 | 122.1039 | -0.091552 | -0.041198 | 122.3465 | 122.2458 | 122.2549 | -0.18768 | 122.2687 | 122.2824 | 122.2412 | -0.12817
1743.7188 | 122.4426 | -122.1451 | 0.086975 | 0.0054168 | 0.018231 | 0.087316 | 0.026938 | -0.070605 | -0.027799 | 0.0029244 | 0.014954 | 0.011021 | -0.027252 | -0.0085065 | -0.0078272 | 0.011813 | 0.10529 | 0.16022 | 0.1831 | 0.17395 | 0.10529 | 0.10071 | -0.036621 | 0.086975 | 0.21057 | 0.059509 | 0.018311 | 0.013733 | 0.10986 | 0.022888 | 122.2458 | 122.1085 | 0.018311 | 122.3053 | 122.319 | 0.21057 | 0.018311 | 122.2549 | 122.168 | -0.068664 | 122.2321 | 122.2046 | 0.036621 | -0.073242 | 122.2504 | 122.2504 | 122.3282 | -0.1236 | 122.1634 | 122.1588 | 122.3557 | -0.064087
1745.5156 | 122.4106 | -122.1954 | 0.068665 | 0.0054168 | 0.024853 | 0.086462 | 0.029074 | -0.072314 | -0.029294 | 0.0042062 | 0.0073242 | 0.01508 | -0.030029 | -0.0097883 | -0.0099634 | 0.011173 | 0.07782 | 0.09613 | 0.12817 | 0.1236 | 0.10529 | 0.091553 | -0.027466 | 0.027466 | 0.10071 | 0.004578 | 0.022888 | 0.041199 | 0.086975 | 0.009155 | 122.287 | 122.168 | 0.036621 | 122.2916 | 122.319 | 0.15106 | 0.009155 | 122.2824 | 122.2046 | -0.045777 | 122.2229 | 122.2 | -0.004577 | -0.027466 | 122.3007 | 122.2733 | 122.3236 | -0.096131 | 122.2183 | 122.2366 | 122.2961 | -0.05951
1747.2344 | 122.3831 | -122.2137 | 0.10071 | 0.0054168 | 0.012676 | 0.084539 | 0.032065 | -0.071245 | -0.022672 | 0.004847 | 0.0073242 | 0.018498 | -0.028747 | -0.0072247 | -0.0065454 | 0.0060455 | 0.041199 | 0.004578 | 0.045776 | 0.10529 | 0.12817 | 0.045776 | -0.082397 | -0.013733 | 0.054932 | -0.09613 | 0.054932 | 0.073242 | 0.07782 | -0.009155 | 122.2595 | 122.1313 | 0.027466 | 122.2183 | 122.319 | 0.18768 | -0.059509 | 122.2916 | 122.2046 | -0.045776 | 122.2 | 122.1176 | -0.086975 | -0.027466 | 122.3419 | 122.2549 | 122.2595 | -0.18311 | 122.2687 | 122.287 | 122.2687 | -0.10986
1749.0156 | 122.3923 | -122.2092 | 0.09613 | 0.013046 | 0.013531 | 0.083257 | 0.031424 | -0.071245 | -0.022885 | 0.005488 | 0.0073242 | 0.016361 | -0.028534 | -0.0059429 | -0.0054772 | 0.0073273 | 0.013733 | 0.013733 | 0.022888 | 0.09613 | 0.13733 | 0.059509 | -0.068665 | -0.009155 | 0.054932 | -0.086975 | 0.054932 | 0.045776 | 0.068665 | -0.022888 | 122.2687 | 122.1405 | 0.041199 | 122.2229 | 122.3053 | 0.16479 | -0.082397 | 122.2778 | 122.1863 | -0.041198 | 122.2 | 122.1222 | -0.064087 | -0.050354 | 122.3465 | 122.2229 | 122.2321 | -0.16479 | 122.2641 | 122.2549 | 122.2641 | -0.11902
1750.7188 | 122.438 | -122.1588 | 0.07782 | 0.013046 | 0.018231 | 0.082403 | 0.023734 | -0.071459 | -0.023099 | 0.0044198 | 0.0073242 | 0.016789 | -0.030029 | -0.0061567 | -0.0046228 | 0.010318 | 0.027466 | -0.018311 | 0.027466 | 0.086975 | 0.13275 | 0.054932 | -0.07782 | 0.004578 | 0.032043 | -0.091553 | 0.022888 | 0.059509 | 0.068665 | -0.004578 | 122.2137 | 122.081 | 0.054931 | 122.1405 | 122.2458 | 0.16479 | -0.050354 | 122.2275 | 122.1542 | -0.054932 | 122.1634 | 122.0673 | -0.086975 | -0.018311 | 122.2916 | 122.1863 | 122.1863 | -0.15564 | 122.1817 | 122.2183 | 122.1909 | -0.082398
1752.5 | 122.438 | -122.1817 | 0.07782 | 0.013046 | 0.021008 | 0.083685 | 0.026938 | -0.073809 | -0.023526 | 0.0042062 | 0.0073242 | 0.013584 | -0.029815 | -0.0078657 | -0.0046228 | 0.010318 | 0.1236 | 0.13275 | 0.16937 | 0.17395 | 0.091553 | 0.10529 | -0.041199 | 0.10071 | 0.15564 | 0.041199 | 0.004578 | 0.013733 | 0.09613 | 0.018311 | 122.287 | 122.1405 | 0.013733 | 122.3145 | 122.3557 | 0.21515 | 0.045776 | 122.2778 | 122.2 | -0.073242 | 122.2824 | 122.2229 | 0.022888 | -0.064087 | 122.2733 | 122.3053 | 122.3511 | -0.11902 | 122.1863 | 122.1954 | 122.3373 | -0.059509
1754.2812 | 122.3511 | -122.2183 | 0.11902 | -0.0022127 | 0.02058 | 0.084325 | 0.030783 | -0.073595 | -0.027585 | 0.0035654 | 0.0073242 | 0.013584 | -0.027893 | -0.0087201 | -0.0082544 | 0.0098907 | 0.091553 | 0.13275 | 0.14648 | 0.17853 | 0.091553 | 0.082397 | -0.036621 | 0.032043 | 0.14648 | -0.013733 | 0.018311 | 0.041199 | 0.091553 | -0.009155 | 122.3007 | 122.1817 | -0.027466 | 122.3511 | 122.3969 | 0.21515 | -0.027466 | 122.3099 | 122.2092 | -0.10071 | 122.2504 | 122.2046 | -0.004578 | -0.07782 | 122.3099 | 122.3099 | 122.3648 | -0.15564 | 122.2366 | 122.2595 | 122.3648 | -0.12817
1756 | 122.3557 | -122.2137 | 0.10986 | 0.013046 | 0.01759 | 0.084112 | 0.030997 | -0.070177 | -0.026731 | 0.003779 | 0.022583 | 0.013157 | -0.029175 | -0.0076519 | -0.0071862 | 0.0094635 | 0.10071 | 0.13733 | 0.16479 | 0.16937 | 0.09613 | 0.09613 | -0.036621 | 0.059509 | 0.17395 | 0.004578 | 0.022888 | 0.036621 | 0.10529 | 0.032043 | 122.3099 | 122.1771 | -0.013733 | 122.3511 | 122.3831 | 0.20599 | -0.009155 | 122.319 | 122.2458 | -0.086975 | 122.2733 | 122.2183 | -0.027465 | -0.073242 | 122.3099 | 122.3145 | 122.3785 | -0.14648 | 122.2366 | 122.2504 | 122.3877 | -0.07782
1757.7656 | 122.3831 | -122.2412 | 0.10529 | -0.0022127 | 0.019512 | 0.086675 | 0.027365 | -0.068682 | -0.026303 | 0.003138 | 0.014954 | 0.014439 | -0.027893 | -0.0091473 | -0.0065454 | 0.0096771 | 0.10986 | 0.14191 | 0.17395 | 0.16937 | 0.09613 | 0.082397 | -0.027466 | 0.091553 | 0.16479 | 0.032043 | 0.009155 | 0.027466 | 0.10529 | 0.004578 | 122.3236 | 122.2137 | -0.009156 | 122.3831 | 122.4106 | 0.19684 | 0.004577 | 122.3465 | 122.2458 | -0.096131 | 122.3328 | 122.2733 | 0.027465 | -0.07782 | 122.3373 | 122.3511 | 122.4152 | -0.13275 | 122.2504 | 122.2687 | 122.406 | -0.10071
1759.5469 | 122.4792 | -122.1771 | 0.068665 | 0.013046 | 0.022076 | 0.08753 | 0.025229 | -0.072741 | -0.028226 | 0.00207 | 0.0073242 | 0.012943 | -0.031524 | -0.0078657 | -0.0074 | 0.010104 | 0.10986 | 0.14648 | 0.16479 | 0.16479 | 0.091553 | 0.10071 | -0.032043 | 0.082397 | 0.19226 | 0.054932 | 0 | 0.009155 | 0.10986 | 0.022888 | 122.2778 | 122.1451 | 0.022888 | 122.3236 | 122.3419 | 0.19684 | 0.041198 | 122.287 | 122.2 | -0.068665 | 122.2595 | 122.2321 | 0.032044 | -0.05951 | 122.2687 | 122.287 | 122.3419 | -0.10071 | 122.1771 | 122.1863 | 122.3694 | -0.045777
1761.3281 | 122.374 | -122.2321 | 0.10986 | 0.013046 | 0.017803 | 0.086462 | 0.02822 | -0.073809 | -0.024594 | 0.0035654 | 0.014954 | 0.014866 | -0.031097 | -0.0085065 | -0.0037684 | 0.010104 | 0.045776 | 0.045776 | 0.07782 | 0.10529 | 0.13275 | 0.059509 | -0.073242 | -0.013733 | 0.041199 | -0.068665 | 0.064087 | 0.064087 | 0.054932 | -0.027466 | 122.2916 | 122.1588 | 0.022888 | 122.2778 | 122.3373 | 0.17853 | -0.064087 | 122.287 | 122.2046 | -0.045776 | 122.2183 | 122.1634 | -0.041199 | -0.045776 | 122.3648 | 122.2778 | 122.3099 | -0.18311 | 122.2961 | 122.2961 | 122.2733 | -0.13733
1763.0469 | 122.3602 | -122.2137 | 0.10529 | 0.0054168 | 0.016094 | 0.08283 | 0.025229 | -0.070818 | -0.020108 | 0.0069834 | 0.0073242 | 0.018498 | -0.027679 | -0.0063703 | -0.001632 | 0.0077545 | 0.022888 | -0.013733 | 0.004578 | 0.07782 | 0.11444 | 0.041199 | -0.054932 | -0.009155 | -0.004578 | -0.11444 | 0.054932 | 0.07782 | 0.07782 | -0.009155 | 122.2549 | 122.1588 | 0.009155 | 122.2 | 122.2916 | 0.13275 | -0.082398 | 122.2916 | 122.2046 | -0.050354 | 122.2046 | 122.0993 | -0.10529 | -0.027466 | 122.3282 | 122.2366 | 122.2183 | -0.16022 | 122.2687 | 122.2916 | 122.2092 | -0.11444
1764.8281 | 122.3831 | -122.2504 | 0.10071 | 0.013046 | 0.018017 | 0.087103 | 0.026511 | -0.069323 | -0.02844 | 0.0061288 | 0.0073242 | 0.01273 | -0.031738 | -0.0082929 | -0.0063318 | 0.011386 | 0.10529 | 0.14191 | 0.17853 | 0.1831 | 0.086975 | 0.09613 | -0.045776 | 0.073242 | 0.18768 | 0.013733 | 0.004578 | 0.036621 | 0.091553 | 0.009155 | 122.3465 | 122.2046 | -0.013733 | 122.3923 | 122.4335 | 0.22888 | 0.004578 | 122.3419 | 122.2595 | -0.09613 | 122.3236 | 122.2641 | 0.004578 | -0.064087 | 122.3373 | 122.3557 | 122.4289 | -0.14648 | 122.2549 | 122.287 | 122.438 | -0.091553
1766.6094 | 122.4106 | -122.2183 | 0.10529 | 0.0054168 | 0.01524 | 0.083471 | 0.026297 | -0.074236 | -0.021176 | 0.0063424 | 0.014954 | 0.017216 | -0.030456 | -0.0074383 | -0.0044092 | 0.0083953 | 0.086975 | 0.050354 | 0.07782 | 0.13733 | 0.12817 | 0.050354 | -0.07782 | 0.054932 | 0.10071 | -0.054932 | 0.032043 | 0.059509 | 0.073242 | -0.022888 | 122.2687 | 122.1405 | 0.022888 | 122.2687 | 122.3557 | 0.21515 | -0.018311 | 122.2916 | 122.1954 | -0.073243 | 122.2733 | 122.1634 | -0.032044 | -0.045777 | 122.3465 | 122.3053 | 122.2961 | -0.18311 | 122.2504 | 122.2778 | 122.319 | -0.12817
1768.3906 | 122.4838 | -122.1725 | 0.082397 | 0.0054168 | 0.018871 | 0.084325 | 0.020956 | -0.071673 | -0.022031 | 0.0061288 | 0.0073242 | 0.018498 | -0.031311 | -0.0074383 | -0.0054772 | 0.0116 | 0.050354 | 0.022888 | 0.068665 | 0.10529 | 0.11902 | 0.07782 | -0.054932 | 0.059509 | 0.082397 | -0.004578 | 0.013733 | 0.041199 | 0.10071 | 0.018311 | 122.2504 | 122.1176 | 0.036622 | 122.1954 | 122.2778 | 0.16022 | -0.032043 | 122.2733 | 122.1909 | -0.068664 | 122.2321 | 122.168 | -0.022889 | -0.041198 | 122.2916 | 122.2229 | 122.2412 | -0.13733 | 122.1863 | 122.2137 | 122.2549 | -0.064086
1770.1094 | 122.4838 | -122.2229 | 0.09613 | -0.0022127 | 0.021221 | 0.086675 | 0.029501 | -0.071245 | -0.028653 | 0.004847 | 0.014954 | 0.010807 | -0.029175 | -0.0095745 | -0.008468 | 0.011173 | 0.045776 | 0.07782 | 0.11902 | 0.15106 | 0.11444 | 0.091553 | -0.054932 | 0.032043 | 0.13733 | 0.018311 | 0.009155 | 0.032043 | 0.091553 | 0.004578 | 122.3145 | 122.168 | 0.018311 | 122.3007 | 122.374 | 0.20599 | -0.050354 | 122.3145 | 122.2275 | -0.086975 | 122.2549 | 122.2412 | 0.013733 | -0.064087 | 122.3373 | 122.2687 | 122.3419 | -0.15106 | 122.2321 | 122.2549 | 122.3602 | -0.091552
1771.875 | 122.4655 | -122.2 | 0.086975 | -0.0022127 | 0.024212 | 0.086675 | 0.027579 | -0.073382 | -0.026303 | 0.0024972 | 0.0073242 | 0.014225 | -0.031738 | -0.0078657 | -0.0078272 | 0.010959 | 0.059509 | 0.07782 | 0.11902 | 0.13275 | 0.09613 | 0.10529 | -0.032043 | 0.027466 | 0.10071 | -0.009155 | 0.036621 | 0.032043 | 0.086975 | 0.009155 | 122.3053 | 122.168 | 0.009155 | 122.2778 | 122.3328 | 0.16479 | -0.027466 | 122.287 | 122.2092 | -0.050354 | 122.2275 | 122.1909 | -0.01831 | -0.054932 | 122.2961 | 122.2595 | 122.319 | -0.11902 | 122.2366 | 122.2321 | 122.3007 | -0.07782
1773.5938 | 122.493 | -122.2092 | 0.082397 | 0.0054168 | 0.023144 | 0.085607 | 0.029288 | -0.072314 | -0.027585 | 0.0035654 | 0.014954 | 0.013584 | -0.031311 | -0.0082929 | -0.0086816 | 0.0083953 | 0.091553 | 0.1236 | 0.15106 | 0.16937 | 0.091553 | 0.086975 | -0.036621 | 0.09613 | 0.16937 | 0.054932 | -0.004578 | 0.022888 | 0.11444 | 0.009155 | 122.2961 | 122.1725 | 0.009156 | 122.3328 | 122.3785 | 0.20599 | 0.009156 | 122.3236 | 122.2183 | -0.086975 | 122.3053 | 122.2641 | 0.045777 | -0.059509 | 122.3007 | 122.3007 | 122.3602 | -0.11902 | 122.2046 | 122.2321 | 122.3785 | -0.073242
1775.375 | 122.4884 | -122.1909 | 0.09613 | 0.0054168 | 0.022503 | 0.085607 | 0.032278 | -0.073168 | -0.025022 | 0.0022836 | 0.014954 | 0.014225 | -0.027038 | -0.010215 | -0.0069726 | 0.0086091 | 0.1236 | 0.15106 | 0.17853 | 0.16479 | 0.10986 | 0.086975 | -0.041199 | 0.09613 | 0.21973 | 0.064087 | 0 | 0.013733 | 0.091553 | 0.013733 | 122.2778 | 122.1497 | 0.013733 | 122.3419 | 122.3557 | 0.20599 | 0.027466 | 122.2824 | 122.2046 | -0.09613 | 122.287 | 122.2549 | 0.050354 | -0.082397 | 122.3007 | 122.3145 | 122.3694 | -0.13733 | 122.1909 | 122.2046 | 122.4106 | -0.082397
1777.1562 | 122.4335 | -122.2229 | 0.091553 | 0.020676 | 0.018231 | 0.082189 | 0.024161 | -0.071459 | -0.020535 | 0.0052744 | 0.014954 | 0.018284 | -0.028961 | -0.0065839 | -0.0029138 | 0.0092499 | 0.032043 | -0.022888 | 0.009155 | 0.082397 | 0.14191 | 0.045776 | -0.07782 | 0 | 0.004578 | -0.10529 | 0.054932 | 0.041199 | 0.045776 | -0.027466 | 122.2687 | 122.1451 | 0.050354 | 122.2 | 122.3053 | 0.16022 | -0.05951 | 122.2687 | 122.1954 | -0.036621 | 122.2229 | 122.1176 | -0.07782 | -0.050354 | 122.3648 | 122.2549 | 122.2321 | -0.16937 | 122.2778 | 122.2641 | 122.2275 | -0.11902
1778.875 | 122.3602 | -122.2366 | 0.12817 | 0.0054168 | 0.011181 | 0.084966 | 0.024588 | -0.072527 | -0.020108 | 0.0061288 | -0.0003053 | 0.019139 | -0.028961 | -0.0072247 | -0.00505 | 0.0083953 | 0.091553 | 0.064087 | 0.086975 | 0.1236 | 0.12817 | 0.064087 | -0.07782 | 0.054932 | 0.059509 | -0.064087 | 0.045776 | 0.068665 | 0.091553 | -0.004578 | 122.3007 | 122.1588 | 0 | 122.3007 | 122.3602 | 0.20142 | -0.036621 | 122.3282 | 122.2321 | -0.082398 | 122.2916 | 122.1725 | -0.059509 | -0.059509 | 122.3648 | 122.3282 | 122.3236 | -0.20599 | 122.2824 | 122.3053 | 122.2961 | -0.13275
1780.6406 | 122.4655 | -122.2321 | 0.091553 | -0.0022127 | 0.019726 | 0.084112 | 0.02587 | -0.075518 | -0.021176 | 0.0067696 | 0.0073242 | 0.016575 | -0.028747 | -0.0072247 | -0.0041956 | 0.0092499 | 0.027466 | -0.018311 | 0.018311 | 0.10071 | 0.13733 | 0.064087 | -0.059509 | 0.004578 | 0.022888 | -0.07782 | 0.050354 | 0.050354 | 0.059509 | -0.004578 | 122.2961 | 122.1725 | 0.045776 | 122.2137 | 122.3328 | 0.16022 | -0.064087 | 122.2916 | 122.2275 | -0.041199 | 122.2366 | 122.1542 | -0.073242 | -0.041199 | 122.3694 | 122.2595 | 122.2504 | -0.15106 | 122.2824 | 122.2824 | 122.2549 | -0.096131
1782.4062 | 122.5113 | -122.2 | 0.07782 | 0.013046 | 0.019512 | 0.081976 | 0.023947 | -0.068468 | -0.023313 | 0.006556 | 0.0073242 | 0.014652 | -0.029602 | -0.0076519 | -0.0044092 | 0.010959 | 0.045776 | 0.018311 | 0.050354 | 0.086975 | 0.11902 | 0.064087 | -0.068665 | 0.018311 | 0.07782 | -0.059509 | 0.027466 | 0.045776 | 0.07782 | 0.009155 | 122.2641 | 122.1313 | 0.041199 | 122.2183 | 122.287 | 0.15564 | -0.032044 | 122.2778 | 122.2092 | -0.050354 | 122.2183 | 122.1405 | -0.068664 | -0.032044 | 122.319 | 122.2458 | 122.2504 | -0.14649 | 122.2275 | 122.2458 | 122.2778 | -0.068665
1784.1406 | 122.3648 | -122.2641 | 0.1236 | 0.013046 | 0.013958 | 0.083471 | 0.023093 | -0.073168 | -0.022672 | 0.0078378 | -0.0003053 | 0.017857 | -0.027679 | -0.0080793 | -0.0012048 | 0.010318 | 0.073242 | 0.050354 | 0.064087 | 0.1236 | 0.11902 | 0.064087 | -0.068665 | 0.022888 | 0.041199 | -0.091553 | 0.050354 | 0.068665 | 0.082397 | -0.018311 | 122.3282 | 122.1954 | -0.004577 | 122.3145 | 122.3877 | 0.19226 | -0.050354 | 122.3465 | 122.2458 | -0.073242 | 122.287 | 122.1725 | -0.073242 | -0.054931 | 122.3831 | 122.3373 | 122.3282 | -0.19226 | 122.3145 | 122.3328 | 122.3053 | -0.14191
1785.9062 | 122.3831 | -122.2549 | 0.10529 | 0.013046 | 0.016522 | 0.086248 | 0.028433 | -0.073168 | -0.027585 | 0.0033518 | -0.0003053 | 0.011235 | -0.030029 | -0.0087201 | -0.0086816 | 0.011386 | 0.07782 | 0.13275 | 0.16937 | 0.17853 | 0.073242 | 0.082397 | -0.022888 | 0.050354 | 0.17395 | 0.004578 | 0.009155 | 0.050354 | 0.086975 | 0.004578 | 122.3373 | 122.2321 | -0.032044 | 122.3877 | 122.4335 | 0.20142 | -0.027466 | 122.3419 | 122.2595 | -0.096131 | 122.3053 | 122.2595 | 0 | -0.054932 | 122.3282 | 122.3328 | 122.4243 | -0.12817 | 122.2641 | 122.3053 | 122.4289 | -0.10071
1787.6094 | 122.4747 | -122.2183 | 0.082397 | 0.020676 | 0.021221 | 0.084112 | 0.024161 | -0.070605 | -0.027158 | 0.0029244 | 0.022583 | 0.012516 | -0.028534 | -0.010643 | -0.0065454 | 0.011173 | 0.11444 | 0.13733 | 0.16937 | 0.17395 | 0.07782 | 0.09613 | -0.027466 | 0.091553 | 0.15106 | 0.045776 | -0.004578 | 0.022888 | 0.09613 | 0.027466 | 122.3145 | 122.1909 | -0.004577 | 122.3557 | 122.3923 | 0.20142 | 0.032044 | 122.3145 | 122.2458 | -0.086975 | 122.3099 | 122.2641 | 0.01831 | -0.059509 | 122.2961 | 122.3328 | 122.3877 | -0.10986 | 122.2137 | 122.2412 | 122.3694 | -0.054931
1789.3906 | 122.3694 | -122.2824 | 0.09613 | 0.0054168 | 0.014385 | 0.083044 | 0.026724 | -0.071459 | -0.018613 | 0.005488 | -0.0003053 | 0.017857 | -0.028106 | -0.0059429 | -0.0037684 | 0.0088227 | 0.032043 | 0 | 0.045776 | 0.09613 | 0.13275 | 0.073242 | -0.064087 | -0.009155 | 0.022888 | -0.11444 | 0.027466 | 0.064087 | 0.059509 | -0.032043 | 122.3557 | 122.2183 | 0.036621 | 122.2824 | 122.3785 | 0.16022 | -0.064087 | 122.3419 | 122.2504 | -0.068664 | 122.2733 | 122.168 | -0.082398 | -0.032043 | 122.4152 | 122.3145 | 122.3282 | -0.16022 | 122.3099 | 122.3465 | 122.3053 | -0.12817
1791.1094 | 122.4243 | -122.2641 | 0.086975 | 0.013046 | 0.015667 | 0.084539 | 0.023734 | -0.0721 | -0.021176 | 0.0057016 | -0.0003053 | 0.017002 | -0.027466 | -0.0057293 | -0.005691 | 0.011173 | 0.018311 | -0.022888 | 0.018311 | 0.086975 | 0.11444 | 0.041199 | -0.082397 | -0.027466 | -0.009155 | -0.11444 | 0.036621 | 0.082397 | 0.054932 | -0.027466 | 122.3053 | 122.1817 | 0.027466 | 122.2412 | 122.3511 | 0.16937 | -0.068664 | 122.319 | 122.2366 | -0.050354 | 122.2366 | 122.1497 | -0.086975 | -0.004578 | 122.3785 | 122.2824 | 122.2824 | -0.16937 | 122.3007 | 122.3465 | 122.2549 | -0.11444
1792.875 | 122.4197 | -122.2504 | 0.10986 | 0.0054168 | 0.015453 | 0.085821 | 0.031851 | -0.071245 | -0.026303 | 0.003779 | 0.0073242 | 0.017216 | -0.025543 | -0.0070111 | -0.0076136 | 0.0094635 | 0.004578 | 0 | 0.036621 | 0.082397 | 0.13733 | 0.068665 | -0.091553 | -0.041199 | 0.036621 | -0.09613 | 0.064087 | 0.086975 | 0.059509 | -0.022888 | 122.319 | 122.1588 | 0.027466 | 122.2504 | 122.3328 | 0.17395 | -0.10529 | 122.3099 | 122.2275 | -0.045776 | 122.2092 | 122.1542 | -0.073242 | -0.022888 | 122.3877 | 122.2549 | 122.287 | -0.20142 | 122.3145 | 122.3373 | 122.287 | -0.13275
1794.6562 | 122.406 | -122.2595 | 0.10529 | 0.0054168 | 0.011395 | 0.083257 | 0.025656 | -0.071673 | -0.02139 | 0.0057016 | 0.014954 | 0.015507 | -0.028106 | -0.0080793 | -0.0052636 | 0.010959 | 0.082397 | 0.082397 | 0.10071 | 0.1236 | 0.11902 | 0.059509 | -0.054932 | 0.041199 | 0.082397 | -0.054932 | 0.027466 | 0.054932 | 0.073242 | -0.013733 | 122.319 | 122.2046 | 0.013733 | 122.3419 | 122.3831 | 0.17853 | -0.022889 | 122.3328 | 122.2458 | -0.07782 | 122.3007 | 122.2046 | -0.041199 | -0.050354 | 122.3785 | 122.3419 | 122.3602 | -0.16022 | 122.287 | 122.3145 | 122.3419 | -0.11902
1796.4375 | 122.3877 | -122.2687 | 0.10986 | 0.0054168 | 0.016094 | 0.086034 | 0.02822 | -0.071032 | -0.02609 | 0.003779 | 0.0073242 | 0.013371 | -0.025543 | -0.0091473 | -0.0078272 | 0.012241 | 0.018311 | 0.004578 | 0.059509 | 0.07782 | 0.12817 | 0.050354 | -0.082397 | -0.032043 | 0.054932 | -0.068665 | 0.050354 | 0.086975 | 0.068665 | -0.022888 | 122.319 | 122.1863 | 0.018311 | 122.2733 | 122.3465 | 0.16022 | -0.091552 | 122.3373 | 122.2458 | -0.059509 | 122.2366 | 122.2 | -0.045777 | -0.022888 | 122.3969 | 122.287 | 122.3282 | -0.19226 | 122.319 | 122.3557 | 122.3236 | -0.13275
1798.2188 | 122.4701 | -122.2549 | 0.082397 | 0.0054168 | 0.024212 | 0.084112 | 0.026297 | -0.070391 | -0.027799 | 0.0033518 | 0.014954 | 0.010594 | -0.029388 | -0.0076519 | -0.0088952 | 0.0096771 | 0.073242 | 0.10529 | 0.13733 | 0.14191 | 0.086975 | 0.091553 | -0.018311 | 0.045776 | 0.10986 | -0.004578 | 0 | 0.041199 | 0.10071 | 0.018311 | 122.3465 | 122.2366 | 0.004578 | 122.3602 | 122.3969 | 0.16022 | -0.009155 | 122.3557 | 122.2733 | -0.082397 | 122.3007 | 122.2504 | -0.022889 | -0.041198 | 122.3419 | 122.3282 | 122.3923 | -0.10071 | 122.2549 | 122.2961 | 122.3648 | -0.064086
1800 | 122.374 | -122.2549 | 0.10529 | 0.0054168 | 0.014172 | 0.084753 | 0.023734 | -0.0721 | -0.020322 | 0.0078378 | 0.014954 | 0.015507 | -0.027038 | -0.0080793 | -0.0018458 | 0.0096771 | 0.064087 | 0.032043 | 0.054932 | 0.10071 | 0.1236 | 0.059509 | -0.050354 | 0.009155 | 0.045776 | -0.10071 | 0.036621 | 0.064087 | 0.064087 | -0.009155 | 122.3145 | 122.2046 | 0.01831 | 122.287 | 122.3557 | 0.15106 | -0.041199 | 122.319 | 122.2458 | -0.068665 | 122.2641 | 122.1542 | -0.091553 | -0.041199 | 122.3785 | 122.319 | 122.3099 | -0.15564 | 122.2916 | 122.319 | 122.3007 | -0.11444
1801.7656 | 122.3969 | -122.2687 | 0.10071 | 0.013046 | 0.014813 | 0.08283 | 0.025656 | -0.0721 | -0.022031 | 0.008265 | -0.0003053 | 0.016148 | -0.026397 | -0.0048749 | -0.0029138 | 0.0096771 | 0.036621 | 0.009155 | 0.045776 | 0.091553 | 0.11902 | 0.054932 | -0.050354 | -0.018311 | 0.018311 | -0.10529 | 0.041199 | 0.050354 | 0.07782 | -0.022888 | 122.3236 | 122.2183 | 0.018311 | 122.2778 | 122.3602 | 0.14191 | -0.064087 | 122.3465 | 122.2458 | -0.059509 | 122.2504 | 122.1634 | -0.082398 | -0.050354 | 122.3877 | 122.3053 | 122.3145 | -0.15106 | 122.3099 | 122.319 | 122.287 | -0.1236
1803.5469 | 122.406 | -122.2778 | 0.11902 | 0.013046 | 0.014385 | 0.088384 | 0.027365 | -0.071245 | -0.02908 | 0.0046334 | 0.0073242 | 0.013584 | -0.027252 | -0.0080793 | -0.0061182 | 0.010745 | 0.036621 | 0.07782 | 0.10986 | 0.12817 | 0.10071 | 0.068665 | -0.064087 | -0.036621 | 0.068665 | -0.068665 | 0.050354 | 0.045776 | 0.050354 | -0.009155 | 122.3465 | 122.2137 | -0.018311 | 122.3557 | 122.406 | 0.19226 | -0.082398 | 122.3282 | 122.2687 | -0.068665 | 122.2412 | 122.2092 | -0.05951 | -0.073243 | 122.3785 | 122.3145 | 122.3877 | -0.18311 | 122.3282 | 122.3236 | 122.3465 | -0.12817
1805.25 | 122.4884 | -122.2321 | 0.091553 | 0.013046 | 0.023358 | 0.083898 | 0.025656 | -0.072741 | -0.027158 | 0.005488 | 0.0073242 | 0.010166 | -0.029815 | -0.0091473 | -0.0082544 | 0.011173 | 0.10529 | 0.14191 | 0.16022 | 0.16022 | 0.09613 | 0.10071 | -0.027466 | 0.059509 | 0.13275 | 0.036621 | -0.004578 | 0.018311 | 0.10986 | 0.027466 | 122.3328 | 122.2046 | 0.004577 | 122.374 | 122.3923 | 0.18768 | 0.013733 | 122.3419 | 122.2595 | -0.096131 | 122.2916 | 122.2687 | 0.009155 | -0.073242 | 122.3282 | 122.3373 | 122.3923 | -0.11902 | 122.2275 | 122.2504 | 122.3648 | -0.064087
1807.0312 | 122.4106 | -122.2778 | 0.12817 | 0.0054168 | 0.012036 | 0.084966 | 0.028647 | -0.073382 | -0.023313 | 0.0039926 | 0.0073242 | 0.016361 | -0.027893 | -0.010429 | -0.0091088 | 0.010318 | 0.013733 | 0.022888 | 0.036621 | 0.082397 | 0.16479 | 0.054932 | -0.086975 | -0.032043 | 0.045776 | -0.091553 | 0.045776 | 0.059509 | 0.059509 | -0.022888 | 122.3328 | 122.1909 | 0.036621 | 122.3007 | 122.3602 | 0.16937 | -0.11444 | 122.3373 | 122.2549 | -0.082398 | 122.2458 | 122.1863 | -0.068665 | -0.068665 | 122.4426 | 122.2916 | 122.3145 | -0.21515 | 122.3236 | 122.3373 | 122.3236 | -0.15106
1808.8125 | 122.3831 | -122.2778 | 0.091553 | 0.013046 | 0.015026 | 0.084325 | 0.024374 | -0.072954 | -0.019681 | 0.0042062 | 0.0073242 | 0.017002 | -0.028106 | -0.0076519 | -0.0035546 | 0.0083953 | 0.036621 | 0.013733 | 0.050354 | 0.09613 | 0.12817 | 0.050354 | -0.068665 | -0.018311 | 0.009155 | -0.10529 | 0.045776 | 0.068665 | 0.059509 | -0.013733 | 122.3282 | 122.2092 | 0.036621 | 122.2916 | 122.374 | 0.16479 | -0.054932 | 122.3373 | 122.2641 | -0.045777 | 122.2595 | 122.1725 | -0.091553 | -0.022888 | 122.406 | 122.3145 | 122.3282 | -0.16022 | 122.3236 | 122.3465 | 122.287 | -0.10529
1810.5312 | 122.4289 | -122.287 | 0.1236 | 0.0054168 | 0.015667 | 0.08048 | 0.02587 | -0.071886 | -0.022458 | 0.0046334 | 0.0073242 | 0.016148 | -0.026825 | -0.0070111 | -0.00505 | 0.010532 | 0.009155 | -0.013733 | 0.018311 | 0.082397 | 0.13275 | 0.054932 | -0.059509 | -0.022888 | 0 | -0.11444 | 0.064087 | 0.073242 | 0.073242 | -0.022888 | 122.3419 | 122.2275 | 0.009155 | 122.2733 | 122.3694 | 0.14191 | -0.11444 | 122.3602 | 122.2641 | -0.059509 | 122.2641 | 122.1725 | -0.091553 | -0.050354 | 122.4197 | 122.2961 | 122.3053 | -0.1831 | 122.3511 | 122.3602 | 122.287 | -0.14648
1812.3125 | 122.374 | -122.2916 | 0.10529 | 0.0054168 | 0.017162 | 0.084112 | 0.026938 | -0.070605 | -0.021604 | 0.004847 | 0.0073242 | 0.015293 | -0.02597 | -0.0065839 | -0.0054772 | 0.0098907 | 0.032043 | 0.018311 | 0.054932 | 0.09613 | 0.1236 | 0.064087 | -0.068665 | -0.022888 | 0.027466 | -0.10529 | 0.027466 | 0.064087 | 0.07782 | -0.022888 | 122.3557 | 122.2229 | 0.01831 | 122.3099 | 122.3877 | 0.16479 | -0.073243 | 122.3694 | 122.2687 | -0.07782 | 122.2687 | 122.1863 | -0.082398 | -0.041199 | 122.4152 | 122.3236 | 122.3465 | -0.17395 | 122.319 | 122.3557 | 122.319 | -0.12817
1814.0938 | 122.4014 | -122.3053 | 0.13275 | 0.0054168 | 0.016522 | 0.087103 | 0.030142 | -0.072314 | -0.028653 | 0.0076242 | 0.0073242 | 0.011021 | -0.026184 | -0.0074383 | -0.0082544 | 0.0116 | 0.059509 | 0.1236 | 0.14191 | 0.16479 | 0.086975 | 0.10071 | -0.050354 | 0.009155 | 0.13275 | -0.050354 | 0.032043 | 0.045776 | 0.068665 | -0.009155 | 122.406 | 122.2549 | -0.045776 | 122.4289 | 122.4701 | 0.21515 | -0.073242 | 122.374 | 122.2961 | -0.10071 | 122.3145 | 122.2549 | -0.041199 | -0.086975 | 122.3923 | 122.3648 | 122.4472 | -0.18311 | 122.3373 | 122.3511 | 122.438 | -0.14191
1815.7969 | 122.4518 | -122.2687 | 0.10986 | -0.0022127 | 0.014813 | 0.084112 | 0.034415 | -0.0721 | -0.025022 | 0.0018564 | 0.0073242 | 0.014012 | -0.02362 | -0.0061567 | -0.0069726 | 0.010318 | 0.004578 | 0.013733 | 0.022888 | 0.10071 | 0.1236 | 0.041199 | -0.059509 | -0.022888 | 0.041199 | -0.086975 | 0.041199 | 0.054932 | 0.045776 | -0.027466 | 122.3099 | 122.2092 | 0.013733 | 122.2824 | 122.3694 | 0.16022 | -0.10529 | 122.3145 | 122.2412 | -0.068664 | 122.2458 | 122.1817 | -0.059509 | -0.054931 | 122.3923 | 122.2733 | 122.2916 | -0.16937 | 122.3099 | 122.3236 | 122.3099 | -0.13733
1817.5781 | 122.4609 | -122.2641 | 0.10529 | 0.0054168 | 0.01289 | 0.08518 | 0.029074 | -0.070391 | -0.022672 | 0.0063424 | -0.0079343 | 0.014439 | -0.026611 | -0.0072247 | -0.0052636 | 0.0079681 | 0.009155 | 0.022888 | 0.032043 | 0.10071 | 0.13275 | 0.045776 | -0.064087 | 0 | 0.064087 | -0.07782 | 0.045776 | 0.059509 | 0.036621 | -0.013733 | 122.3099 | 122.2 | 0.027465 | 122.287 | 122.3648 | 0.1648 | -0.096131 | 122.3007 | 122.2504 | -0.05951 | 122.2641 | 122.1863 | -0.064087 | -0.045777 | 122.3969 | 122.2733 | 122.2961 | -0.16937 | 122.3099 | 122.3236 | 122.3282 | -0.11902
1819.3594 | 122.493 | -122.2412 | 0.09613 | 0.0054168 | 0.023785 | 0.084753 | 0.02886 | -0.069323 | -0.030789 | 0.003779 | 0.0073242 | 0.011448 | -0.027038 | -0.0059429 | -0.010391 | 0.011813 | 0.045776 | 0.091553 | 0.12817 | 0.11444 | 0.091553 | 0.082397 | -0.022888 | 0.032043 | 0.10071 | -0.004578 | 0.013733 | 0.041199 | 0.091553 | 0.027466 | 122.3236 | 122.2183 | -0.004577 | 122.3328 | 122.3557 | 0.13733 | -0.050354 | 122.3328 | 122.2687 | -0.082397 | 122.2733 | 122.2366 | -0.032044 | -0.054931 | 122.3328 | 122.287 | 122.3694 | -0.11902 | 122.2549 | 122.2824 | 122.3419 | -0.068664
1821.1406 | 122.406 | -122.2961 | 0.13733 | 0.0054168 | 0.013104 | 0.08283 | 0.024161 | -0.073595 | -0.020535 | 0.0061288 | 0.0073242 | 0.017002 | -0.026611 | -0.0063703 | -0.0035546 | 0.0094635 | 0.059509 | 0.041199 | 0.054932 | 0.11902 | 0.1236 | 0.059509 | -0.059509 | -0.013733 | 0.036621 | -0.10986 | 0.032043 | 0.059509 | 0.082397 | -0.018311 | 122.3557 | 122.2366 | -0.013733 | 122.3373 | 122.4152 | 0.17853 | -0.07782 | 122.3785 | 122.2778 | -0.10529 | 122.2824 | 122.1863 | -0.091552 | -0.07782 | 122.4197 | 122.3557 | 122.3511 | -0.19684 | 122.3282 | 122.3557 | 122.3328 | -0.15564
1822.8594 | 122.5342 | -122.2778 | 0.068665 | 0.0054168 | 0.023358 | 0.085394 | 0.028006 | -0.073595 | -0.029721 | 0.0057016 | 0.0073242 | 0.011448 | -0.029175 | -0.010002 | -0.0082544 | 0.011813 | 0.032043 | 0.07782 | 0.11444 | 0.1236 | 0.082397 | 0.09613 | -0.036621 | 0.018311 | 0.091553 | -0.004578 | 0.022888 | 0.022888 | 0.09613 | -0.004578 | 122.374 | 122.2412 | 0.013732 | 122.3557 | 122.4014 | 0.16022 | -0.036622 | 122.374 | 122.2733 | -0.045777 | 122.2961 | 122.2733 | 0 | -0.045777 | 122.3602 | 122.3099 | 122.3923 | -0.10529 | 122.3007 | 122.3007 | 122.3694 | -0.073243
1824.6406 | 122.3831 | -122.2916 | 0.10986 | 0.013046 | 0.012676 | 0.082616 | 0.02587 | -0.069537 | -0.017545 | 0.006556 | 0.0073242 | 0.016789 | -0.027038 | -0.0070111 | -0.003982 | 0.010104 | 0.068665 | 0.050354 | 0.073242 | 0.10071 | 0.1236 | 0.064087 | -0.073242 | 0.022888 | 0.036621 | -0.086975 | 0.022888 | 0.059509 | 0.086975 | -0.004578 | 122.3557 | 122.2183 | 0.013733 | 122.3419 | 122.3923 | 0.17395 | -0.041198 | 122.3785 | 122.287 | -0.086975 | 122.3145 | 122.2046 | -0.082397 | -0.050354 | 122.4152 | 122.3602 | 122.3648 | -0.18311 | 122.3145 | 122.3511 | 122.3282 | -0.11444
1826.4219 | 122.4197 | -122.287 | 0.10529 | 0.0054168 | 0.013958 | 0.085607 | 0.023306 | -0.070818 | -0.022885 | 0.005488 | -0.0003053 | 0.016361 | -0.027466 | -0.0091473 | -0.0020594 | 0.010318 | 0.068665 | 0.073242 | 0.082397 | 0.10986 | 0.11902 | 0.068665 | -0.059509 | 0.041199 | 0.068665 | -0.07782 | 0.036621 | 0.050354 | 0.059509 | -0.018311 | 122.3557 | 122.2275 | 0.013733 | 122.3602 | 122.3969 | 0.16937 | -0.036621 | 122.3465 | 122.2687 | -0.068665 | 122.3282 | 122.2092 | -0.059509 | -0.054932 | 122.406 | 122.3557 | 122.3694 | -0.16479 | 122.3236 | 122.3373 | 122.3557 | -0.1236
1828.2031 | 122.4243 | -122.2961 | 0.09613 | 0.0054168 | 0.016522 | 0.085394 | 0.029715 | -0.071245 | -0.02908 | 0.003138 | -0.0079343 | 0.012303 | -0.026611 | -0.0093609 | -0.0080408 | 0.011386 | 0.041199 | 0.059509 | 0.082397 | 0.11902 | 0.10986 | 0.050354 | -0.082397 | -0.036621 | 0.059509 | -0.064087 | 0.022888 | 0.054932 | 0.07782 | -0.022888 | 122.3465 | 122.2137 | 0.013733 | 122.3557 | 122.4152 | 0.20142 | -0.054931 | 122.374 | 122.2733 | -0.073242 | 122.2595 | 122.2321 | -0.041199 | -0.041198 | 122.406 | 122.3373 | 122.3785 | -0.17853 | 122.319 | 122.3511 | 122.3557 | -0.11902
1830 | 122.4289 | -122.2961 | 0.11902 | 0.020676 | 0.015881 | 0.085607 | 0.026083 | -0.071673 | -0.027585 | 0.0018564 | 0.022583 | 0.013371 | -0.026611 | -0.0080793 | -0.0063318 | 0.011386 | 0.018311 | 0.036621 | 0.073242 | 0.10986 | 0.13275 | 0.045776 | -0.068665 | -0.027466 | 0.050354 | -0.086975 | 0.050354 | 0.050354 | 0.068665 | -0.022888 | 122.3419 | 122.2275 | 0.013732 | 122.3328 | 122.406 | 0.17853 | -0.10071 | 122.3648 | 122.2733 | -0.068665 | 122.2687 | 122.2092 | -0.064087 | -0.068665 | 122.4289 | 122.3145 | 122.3694 | -0.18768 | 122.3465 | 122.3465 | 122.3465 | -0.14191
1831.7812 | 122.4609 | -122.2733 | 0.10529 | -0.0022127 | 0.013104 | 0.083685 | 0.027792 | -0.071673 | -0.02139 | 0.003779 | 0.014954 | 0.014439 | -0.026611 | -0.0067975 | -0.0059046 | 0.0088227 | 0.027466 | -0.004578 | 0.036621 | 0.10071 | 0.13275 | 0.050354 | -0.068665 | -0.013733 | 0.064087 | -0.082397 | 0.054932 | 0.054932 | 0.054932 | -0.013733 | 122.3236 | 122.2046 | 0.027465 | 122.2687 | 122.374 | 0.16937 | -0.07782 | 122.3282 | 122.2595 | -0.050354 | 122.2595 | 122.1909 | -0.068664 | -0.050354 | 122.406 | 122.3007 | 122.3099 | -0.17395 | 122.3282 | 122.3282 | 122.3373 | -0.11902
1833.5625 | 122.5342 | -122.2321 | 0.068665 | 0.013046 | 0.02293 | 0.08283 | 0.025015 | -0.071245 | -0.026731 | 0.004847 | 0.022583 | 0.014439 | -0.028534 | -0.0091473 | -0.003341 | 0.0116 | 0.10986 | 0.13733 | 0.17853 | 0.17395 | 0.10071 | 0.10071 | -0.018311 | 0.09613 | 0.16022 | 0.036621 | 0.009155 | 0.022888 | 0.10986 | 0.036621 | 122.3328 | 122.2137 | 0.032043 | 122.3694 | 122.406 | 0.19226 | 0.041198 | 122.3419 | 122.2687 | -0.05951 | 122.3282 | 122.2687 | 0 | -0.045777 | 122.3328 | 122.3419 | 122.4106 | -0.086976 | 122.2412 | 122.2549 | 122.3923 | -0.032044
1835.3438 | 122.4518 | -122.2824 | 0.10986 | -0.0098417 | 0.014172 | 0.081548 | 0.027579 | -0.075945 | -0.023099 | 0.0050608 | 0.0073242 | 0.015507 | -0.028961 | -0.0055157 | -0.0027002 | 0.0098907 | 0.064087 | 0.059509 | 0.086975 | 0.12817 | 0.11902 | 0.068665 | -0.068665 | 0.045776 | 0.091553 | -0.050354 | 0.036621 | 0.054932 | 0.073242 | -0.004578 | 122.3511 | 122.2137 | 0.009156 | 122.3419 | 122.4106 | 0.19684 | -0.045776 | 122.3557 | 122.2778 | -0.073242 | 122.3282 | 122.2321 | -0.045776 | -0.054931 | 122.4014 | 122.3465 | 122.3694 | -0.17853 | 122.319 | 122.3373 | 122.374 | -0.11444
1837.0625 | 122.438 | -122.2824 | 0.10529 | -0.0022127 | 0.016094 | 0.088812 | 0.026083 | -0.070605 | -0.025876 | 0.0029244 | 0.0073242 | 0.011021 | -0.027679 | -0.0097883 | -0.006759 | 0.0098907 | 0.086975 | 0.13275 | 0.15564 | 0.16022 | 0.09613 | 0.082397 | -0.045776 | 0.032043 | 0.13733 | -0.004578 | 0.009155 | 0.041199 | 0.091553 | 0.009155 | 122.3648 | 122.2366 | -0.009156 | 122.4152 | 122.4426 | 0.20599 | -0.018311 | 122.374 | 122.2916 | -0.096131 | 122.3145 | 122.2778 | -0.013733 | -0.064087 | 122.3785 | 122.3694 | 122.4381 | -0.15106 | 122.2916 | 122.3236 | 122.4197 | -0.096131
1838.8594 | 122.5479 | -122.2687 | 0.086975 | 0.020676 | 0.016735 | 0.084325 | 0.026938 | -0.070391 | -0.023526 | 0.0050608 | 0.0073242 | 0.014866 | -0.026825 | -0.0067975 | -0.0046228 | 0.0096771 | -0.004578 | 0.009155 | 0.027466 | 0.073242 | 0.13733 | 0.064087 | -0.064087 | -0.009155 | 0.009155 | -0.086975 | 0.032043 | 0.059509 | 0.064087 | 0.004578 | 122.3328 | 122.2046 | 0.050354 | 122.2778 | 122.3419 | 0.13733 | -0.091553 | 122.3328 | 122.2733 | -0.054932 | 122.2595 | 122.1817 | -0.091553 | -0.027466 | 122.406 | 122.2641 | 122.2961 | -0.15106 | 122.3007 | 122.3282 | 122.2778 | -0.082397
1840.6406 | 122.4884 | -122.3053 | 0.10986 | 0.013046 | 0.014813 | 0.083898 | 0.027792 | -0.070177 | -0.023953 | 0.003779 | 0.014954 | 0.016148 | -0.024902 | -0.0080793 | -0.0059046 | 0.0096771 | 0.027466 | 0.022888 | 0.054932 | 0.091553 | 0.11902 | 0.059509 | -0.068665 | 0.013733 | 0.07782 | -0.073242 | 0.041199 | 0.041199 | 0.059509 | -0.013733 | 122.3648 | 122.2366 | 0.009156 | 122.3282 | 122.3969 | 0.16022 | -0.082397 | 122.3648 | 122.2916 | -0.068664 | 122.319 | 122.2321 | -0.059509 | -0.068664 | 122.4243 | 122.3328 | 122.3602 | -0.17853 | 122.3465 | 122.3465 | 122.3831 | -0.1236
1842.4219 | 122.5616 | -122.2733 | 0.086975 | 0.0054168 | 0.023998 | 0.084753 | 0.026938 | -0.071459 | -0.029294 | 0.0042062 | 0.0073242 | 0.011662 | -0.02832 | -0.0087201 | -0.0088952 | 0.010532 | 0.036621 | 0.082397 | 0.11444 | 0.12817 | 0.086975 | 0.091553 | -0.041199 | 0.013733 | 0.07782 | -0.018311 | 0.018311 | 0.032043 | 0.10529 | 0.009155 | 122.3648 | 122.2321 | 0 | 122.3557 | 122.4014 | 0.16937 | -0.050354 | 122.3785 | 122.2824 | -0.068664 | 122.287 | 122.2549 | -0.027466 | -0.054932 | 122.3602 | 122.3099 | 122.3877 | -0.12817 | 122.2916 | 122.3053 | 122.3511 | -0.07782
1844.1406 | 122.5296 | -122.2824 | 0.10071 | 0.0054168 | 0.024853 | 0.087743 | 0.026083 | -0.073595 | -0.027371 | 0.0046334 | 0.0073242 | 0.010166 | -0.029602 | -0.0091473 | -0.0059046 | 0.0098907 | 0.068665 | 0.07782 | 0.1236 | 0.12817 | 0.10986 | 0.091553 | -0.027466 | 0.022888 | 0.073242 | -0.013733 | 0.009155 | 0.032043 | 0.091553 | 0.022888 | 122.374 | 122.2549 | 0.009155 | 122.3602 | 122.4106 | 0.15564 | -0.032043 | 122.374 | 122.3053 | -0.091553 | 122.3053 | 122.2687 | -0.036621 | -0.068665 | 122.3923 | 122.3511 | 122.406 | -0.12817 | 122.2916 | 122.3145 | 122.3557 | -0.07782
1845.9062 | 122.5708 | -122.2641 | 0.091553 | 0.0054168 | 0.021862 | 0.089025 | 0.029501 | -0.072314 | -0.027371 | 0.0027108 | -0.0003053 | 0.011021 | -0.027038 | -0.0087201 | -0.0059046 | 0.0090363 | 0.12817 | 0.17853 | 0.20142 | 0.18768 | 0.082397 | 0.10071 | -0.027466 | 0.091553 | 0.18768 | 0.068665 | 0.004578 | 0.022888 | 0.10986 | 0.027466 | 122.3648 | 122.2366 | -0.009156 | 122.4426 | 122.4518 | 0.21515 | 0.036621 | 122.374 | 122.2916 | -0.086975 | 122.3557 | 122.3328 | 0.041199 | -0.068665 | 122.3465 | 122.3923 | 122.4655 | -0.11902 | 122.2687 | 122.287 | 122.4518 | -0.064087
1847.6875 | 122.5616 | -122.2733 | 0.054932 | 0.0054168 | 0.020794 | 0.081762 | 0.024374 | -0.070605 | -0.020963 | 0.0035654 | 0.0073242 | 0.016575 | -0.026611 | -0.0087201 | -0.00505 | 0.010104 | 0.050354 | 0.004578 | 0.041199 | 0.09613 | 0.12817 | 0.054932 | -0.054932 | 0.027466 | 0.045776 | -0.059509 | 0.027466 | 0.036621 | 0.082397 | 0.013733 | 122.3282 | 122.2183 | 0.073242 | 122.2778 | 122.3694 | 0.15106 | -0.004578 | 122.3557 | 122.287 | -0.027466 | 122.3007 | 122.2137 | -0.073242 | -0.018311 | 122.4014 | 122.3236 | 122.3145 | -0.10986 | 122.3007 | 122.3099 | 122.319 | -0.041199
1849.3906 | 122.5067 | -122.2778 | 0.09613 | 0.013046 | 0.019085 | 0.086462 | 0.028006 | -0.072741 | -0.025662 | 0.0059152 | -0.0003053 | 0.011448 | -0.027038 | -0.010002 | -0.0076136 | 0.010745 | 0.12817 | 0.16937 | 0.17395 | 0.17853 | 0.086975 | 0.07782 | -0.041199 | 0.091553 | 0.19226 | 0.036621 | 0 | 0.032043 | 0.10071 | 0.009155 | 122.3557 | 122.2366 | -0.009155 | 122.4472 | 122.4564 | 0.21973 | 0.032044 | 122.3785 | 122.287 | -0.09613 | 122.3694 | 122.3145 | 0.027466 | -0.064087 | 122.3648 | 122.406 | 122.4518 | -0.13733 | 122.2778 | 122.3099 | 122.4701 | -0.086975
1851.1875 | 122.4426 | -122.3236 | 0.11902 | -0.0022127 | 0.015667 | 0.086248 | 0.027152 | -0.073168 | -0.024381 | 0.004847 | 0.0073242 | 0.01273 | -0.025757 | -0.0078657 | -0.0074 | 0.010532 | 0.045776 | 0.050354 | 0.07782 | 0.10071 | 0.11902 | 0.064087 | -0.068665 | -0.018311 | 0.041199 | -0.082397 | 0.032043 | 0.064087 | 0.064087 | -0.032043 | 122.3877 | 122.2549 | 0 | 122.374 | 122.4243 | 0.16937 | -0.073243 | 122.3877 | 122.2916 | -0.086976 | 122.3053 | 122.2412 | -0.050354 | -0.054932 | 122.4426 | 122.3694 | 122.4014 | -0.18768 | 122.3557 | 122.3877 | 122.3648 | -0.15106
1852.9688 | 122.5159 | -122.2961 | 0.07782 | 0.0054168 | 0.024639 | 0.085607 | 0.028647 | -0.073168 | -0.026517 | 0.005488 | 0.014954 | 0.011448 | -0.027466 | -0.0089337 | -0.0082544 | 0.010959 | 0.082397 | 0.10529 | 0.13275 | 0.1236 | 0.09613 | 0.10071 | -0.027466 | 0.032043 | 0.10071 | 0 | 0.004578 | 0.041199 | 0.10529 | 0.022888 | 122.3969 | 122.2687 | 0.01831 | 122.4014 | 122.4197 | 0.15106 | 0.004577 | 122.4014 | 122.319 | -0.073242 | 122.3282 | 122.2961 | -0.022888 | -0.036621 | 122.3923 | 122.3785 | 122.4289 | -0.10529 | 122.3007 | 122.3373 | 122.3969 | -0.054932
1854.75 | 122.5891 | -122.2916 | 0.07782 | 0.013046 | 0.025067 | 0.088598 | 0.028433 | -0.074663 | -0.027799 | 0.0042062 | 0.022583 | 0.013157 | -0.027893 | -0.0087201 | -0.0078272 | 0.0083953 | 0.09613 | 0.13275 | 0.15564 | 0.14648 | 0.09613 | 0.07782 | -0.036621 | 0.091553 | 0.16479 | 0.045776 | 0.004578 | 0.022888 | 0.10529 | 0.027466 | 122.3694 | 122.2549 | 0.01831 | 122.4243 | 122.438 | 0.18311 | 0.01831 | 122.3969 | 122.319 | -0.073242 | 122.3831 | 122.3373 | 0.01831 | -0.054932 | 122.3877 | 122.3877 | 122.4472 | -0.11444 | 122.2961 | 122.3145 | 122.4564 | -0.050354
1856.4688 | 122.5662 | -122.2595 | 0.082397 | 0.0054168 | 0.020153 | 0.082403 | 0.025656 | -0.073595 | -0.019895 | 0.0076242 | 0.0073242 | 0.014012 | -0.027038 | -0.0061567 | -0.0031274 | 0.0088227 | 0.050354 | 0.018311 | 0.054932 | 0.086975 | 0.13275 | 0.050354 | -0.073242 | 0.013733 | 0.032043 | -0.064087 | 0.041199 | 0.041199 | 0.054932 | -0.004578 | 122.3099 | 122.1863 | 0.050354 | 122.2778 | 122.3465 | 0.16022 | -0.032043 | 122.3145 | 122.2549 | -0.041198 | 122.2733 | 122.1954 | -0.059509 | -0.041198 | 122.3923 | 122.3099 | 122.3145 | -0.15564 | 122.3007 | 122.3007 | 122.2916 | -0.086975
1858.25 | 122.4518 | -122.3373 | 0.10529 | -0.0098417 | 0.015881 | 0.086675 | 0.02822 | -0.072741 | -0.025876 | 0.0057016 | 0.014954 | 0.013157 | -0.026825 | -0.0093609 | -0.006759 | 0.0096771 | 0.032043 | 0.064087 | 0.082397 | 0.09613 | 0.11444 | 0.059509 | -0.07782 | -0.009155 | 0.054932 | -0.07782 | 0.054932 | 0.064087 | 0.059509 | -0.022888 | 122.3969 | 122.2595 | 0.009155 | 122.4014 | 122.4335 | 0.17395 | -0.073243 | 122.3969 | 122.3145 | -0.050354 | 122.3282 | 122.2595 | -0.054932 | -0.041199 | 122.4518 | 122.3694 | 122.4197 | -0.18311 | 122.3923 | 122.4014 | 122.3923 | -0.12817
1860.0469 | 122.5754 | -122.287 | 0.068665 | -0.0022127 | 0.019512 | 0.083257 | 0.024802 | -0.072527 | -0.020108 | 0.0074106 | 0.022583 | 0.016575 | -0.029388 | -0.0057293 | -0.0037684 | 0.011173 | 0.032043 | 0.009155 | 0.041199 | 0.07782 | 0.13275 | 0.045776 | -0.064087 | 0.009155 | 0.022888 | -0.082397 | 0.041199 | 0.045776 | 0.068665 | 0.004578 | 122.3328 | 122.2229 | 0.064086 | 122.2961 | 122.3648 | 0.14191 | -0.036622 | 122.3557 | 122.2916 | -0.027466 | 122.2961 | 122.2046 | -0.086975 | -0.022889 | 122.4197 | 122.319 | 122.3282 | -0.13275 | 122.3282 | 122.3328 | 122.3099 | -0.064087
1861.7656 | 122.5388 | -122.2961 | 0.054932 | 0.020676 | 0.021862 | 0.084325 | 0.022879 | -0.070605 | -0.024381 | 0.005488 | 0.014954 | 0.013798 | -0.02832 | -0.0074383 | -0.0041956 | 0.010318 | 0.10529 | 0.14191 | 0.16937 | 0.17395 | 0.073242 | 0.10071 | -0.027466 | 0.11902 | 0.15106 | 0.022888 | -0.022888 | 0.013733 | 0.10986 | 0.022888 | 122.3969 | 122.2687 | 0.01831 | 122.4381 | 122.4701 | 0.20142 | 0.050354 | 122.406 | 122.319 | -0.07782 | 122.4152 | 122.319 | 0 | -0.041199 | 122.3694 | 122.4014 | 122.4655 | -0.082398 | 122.2733 | 122.3099 | 122.4472 | -0.032044
1863.5469 | 122.58 | -122.2916 | 0.068665 | 0.0054168 | 0.019726 | 0.084539 | 0.02117 | -0.0721 | -0.02374 | 0.0076242 | -0.0003053 | 0.014012 | -0.030883 | -0.0082929 | -0.0037684 | 0.0090363 | 0.09613 | 0.07782 | 0.11902 | 0.1236 | 0.091553 | 0.086975 | -0.045776 | 0.10071 | 0.13733 | 0.018311 | -0.013733 | 0.004578 | 0.1236 | 0.027466 | 122.3785 | 122.2458 | 0.022888 | 122.3694 | 122.4152 | 0.16937 | 0.027465 | 122.4152 | 122.319 | -0.082398 | 122.3923 | 122.3099 | -0.009155 | -0.064087 | 122.3831 | 122.3877 | 122.4106 | -0.11444 | 122.2778 | 122.2961 | 122.4289 | -0.041199
1865.3438 | 122.5754 | -122.3007 | 0.068665 | 0.0054168 | 0.020367 | 0.084539 | 0.026297 | -0.06975 | -0.023526 | 0.0061288 | 0.014954 | 0.012943 | -0.027893 | -0.0067975 | -0.0031274 | 0.010318 | 0.10071 | 0.10986 | 0.14648 | 0.14648 | 0.09613 | 0.10071 | -0.032043 | 0.10529 | 0.14191 | 0.022888 | 0.018311 | 0.013733 | 0.11902 | 0.032043 | 122.4014 | 122.2687 | 0.027465 | 122.4106 | 122.4472 | 0.17853 | 0.032043 | 122.4197 | 122.3328 | -0.050354 | 122.406 | 122.3236 | -0.009155 | -0.054932 | 122.3969 | 122.4014 | 122.4472 | -0.10071 | 122.319 | 122.3145 | 122.4426 | -0.036622
1867.0625 | 122.4976 | -122.3282 | 0.10986 | 0.0054168 | 0.01289 | 0.085607 | 0.029929 | -0.072954 | -0.02374 | 0.0057016 | 0.014954 | 0.013584 | -0.024902 | -0.0080793 | -0.006759 | 0.010959 | -0.004578 | 0.018311 | 0.027466 | 0.082397 | 0.15106 | 0.059509 | -0.068665 | -0.027466 | 0.050354 | -0.10071 | 0.041199 | 0.045776 | 0.041199 | -0.013733 | 122.3877 | 122.2595 | 0.041199 | 122.3465 | 122.4106 | 0.15106 | -0.11444 | 122.3694 | 122.3145 | -0.068664 | 122.3007 | 122.2275 | -0.086975 | -0.064087 | 122.4792 | 122.3236 | 122.3557 | -0.17853 | 122.3694 | 122.374 | 122.3785 | -0.1236
1868.8438 | 122.4243 | -122.3328 | 0.086975 | 0.0054168 | 0.013531 | 0.083471 | 0.026724 | -0.071459 | -0.021176 | 0.0061288 | 0.0073242 | 0.016789 | -0.023407 | -0.0074383 | -0.0031274 | 0.010318 | 0.041199 | 0.032043 | 0.054932 | 0.10529 | 0.11444 | 0.064087 | -0.064087 | 0.004578 | 0.032043 | -0.11444 | 0.027466 | 0.050354 | 0.07782 | -0.027466 | 122.3969 | 122.2687 | 0.027466 | 122.3648 | 122.4381 | 0.16937 | -0.045776 | 122.4106 | 122.3053 | -0.059509 | 122.3373 | 122.2183 | -0.086975 | -0.036621 | 122.4472 | 122.374 | 122.3877 | -0.15106 | 122.3602 | 122.3831 | 122.3648 | -0.11444
1870.625 | 122.5296 | -122.3007 | 0.086975 | 0.013046 | 0.022503 | 0.089025 | 0.027792 | -0.071886 | -0.031217 | 0.0039926 | 0.0073242 | 0.0088845 | -0.02832 | -0.0091473 | -0.0071862 | 0.012454 | 0.041199 | 0.10071 | 0.13275 | 0.13275 | 0.086975 | 0.11444 | -0.036621 | 0.045776 | 0.10986 | -0.013733 | 0.009155 | 0.013733 | 0.09613 | 0.013733 | 122.4152 | 122.2641 | 0 | 122.4014 | 122.4335 | 0.16937 | -0.045776 | 122.3969 | 122.3145 | -0.07782 | 122.3465 | 122.287 | -0.027466 | -0.073242 | 122.3877 | 122.3419 | 122.4335 | -0.1236 | 122.3099 | 122.3145 | 122.4106 | -0.073242
1872.3906 | 122.5937 | -122.2504 | 0.064087 | 0.0054168 | 0.021649 | 0.085821 | 0.026511 | -0.075518 | -0.031644 | 0.0046334 | -0.0003053 | 0.010166 | -0.029602 | -0.0097883 | -0.0069726 | 0.010959 | 0.032043 | 0.091553 | 0.11444 | 0.13275 | 0.10529 | 0.082397 | -0.041199 | 0.036621 | 0.11902 | 0.004578 | 0.013733 | 0.036621 | 0.10529 | 0.022888 | 122.3328 | 122.2092 | 0.041199 | 122.3419 | 122.3831 | 0.17395 | -0.032044 | 122.3557 | 122.2733 | -0.050354 | 122.287 | 122.2549 | -0.01831 | -0.027466 | 122.3557 | 122.2824 | 122.3648 | -0.10529 | 122.2641 | 122.287 | 122.3694 | -0.041199
1874.1719 | 122.5296 | -122.287 | 0.068665 | 0.0054168 | 0.024426 | 0.087316 | 0.025015 | -0.071459 | -0.02609 | 0.0044198 | -0.0003053 | 0.013157 | -0.028534 | -0.0085065 | -0.0054772 | 0.012027 | 0.1236 | 0.15106 | 0.16937 | 0.15106 | 0.07782 | 0.10986 | -0.027466 | 0.07782 | 0.13275 | 0.032043 | -0.004578 | 0.004578 | 0.10529 | 0.045776 | 122.3969 | 122.2595 | 0.009155 | 122.438 | 122.438 | 0.17853 | 0.054931 | 122.3923 | 122.3328 | -0.073243 | 122.3648 | 122.319 | -0.013733 | -0.064087 | 122.3648 | 122.4106 | 122.4564 | -0.096131 | 122.2824 | 122.2916 | 122.4197 | -0.022889
1875.8906 | 122.6028 | -122.2916 | 0.082397 | 0.0054168 | 0.023144 | 0.086248 | 0.027792 | -0.073168 | -0.02844 | 0.0035654 | 0.014954 | 0.011021 | -0.027466 | -0.010429 | -0.0069726 | 0.010959 | 0.091553 | 0.11902 | 0.14191 | 0.16022 | 0.10529 | 0.10071 | -0.041199 | 0.073242 | 0.16022 | 0.050354 | 0.018311 | 0.009155 | 0.10071 | 0.027466 | 122.3923 | 122.2504 | 0.022889 | 122.4106 | 122.4518 | 0.20142 | 0.009156 | 122.3923 | 122.319 | -0.064086 | 122.3648 | 122.3419 | 0.022888 | -0.073242 | 122.3969 | 122.3831 | 122.4335 | -0.1236 | 122.3099 | 122.3007 | 122.4518 | -0.054931
1877.6719 | 122.4655 | -122.3328 | 0.11444 | -0.0022127 | 0.015453 | 0.080267 | 0.02822 | -0.071673 | -0.018186 | 0.0052744 | 0.014954 | 0.017643 | -0.026825 | -0.0074383 | -0.0031274 | 0.0069001 | 0.09613 | 0.064087 | 0.064087 | 0.10529 | 0.10986 | 0.068665 | -0.054932 | 0.032043 | 0.032043 | -0.09613 | 0.041199 | 0.064087 | 0.073242 | -0.013733 | 122.4014 | 122.2778 | -0.004578 | 122.3969 | 122.4381 | 0.16022 | -0.018311 | 122.406 | 122.319 | -0.073242 | 122.3648 | 122.2366 | -0.082397 | -0.050354 | 122.4426 | 122.4289 | 122.3969 | -0.16937 | 122.374 | 122.3969 | 122.3648 | -0.12817
1879.4531 | 122.5433 | -122.2778 | 0.082397 | 0.020676 | 0.023785 | 0.084325 | 0.024161 | -0.071886 | -0.02609 | 0.005488 | -0.0003053 | 0.010807 | -0.027679 | -0.0082929 | -0.0059046 | 0.0096771 | 0.11902 | 0.14191 | 0.17853 | 0.15564 | 0.082397 | 0.10529 | -0.036621 | 0.10071 | 0.14191 | 0.022888 | 0.004578 | 0.027466 | 0.10986 | 0.018311 | 122.3831 | 122.2412 | 0 | 122.4197 | 122.4335 | 0.19226 | 0.036622 | 122.3877 | 122.2961 | -0.077819 | 122.3785 | 122.3007 | 0.004577 | -0.054931 | 122.3602 | 122.3969 | 122.4564 | -0.11902 | 122.2824 | 122.3053 | 122.4197 | -0.064086
1881.25 | 122.612 | -122.3099 | 0.073242 | 0.0054168 | 0.023571 | 0.085394 | 0.025656 | -0.074023 | -0.026731 | 0.0035654 | 0.0073242 | 0.011662 | -0.028106 | -0.010002 | -0.0063318 | 0.012882 | 0.045776 | 0.10071 | 0.12817 | 0.14191 | 0.091553 | 0.086975 | -0.041199 | 0.050354 | 0.12817 | 0.018311 | 0.004578 | 0.022888 | 0.09613 | 0.022888 | 122.3969 | 122.2687 | 0.018311 | 122.4106 | 122.4518 | 0.18311 | -0.027466 | 122.406 | 122.3328 | -0.068664 | 122.3602 | 122.3282 | -0.004577 | -0.050354 | 122.4014 | 122.3557 | 122.438 | -0.11444 | 122.3145 | 122.3328 | 122.438 | -0.050354
1883.0312 | 122.4335 | -122.3557 | 0.1236 | -0.0022127 | 0.011395 | 0.083044 | 0.026083 | -0.073168 | -0.017331 | 0.0067696 | -0.0003053 | 0.015293 | -0.028106 | -0.0065839 | -0.0041956 | 0.010318 | 0.082397 | 0.064087 | 0.068665 | 0.10986 | 0.10986 | 0.073242 | -0.045776 | 0.036621 | 0.050354 | -0.10071 | 0.032043 | 0.064087 | 0.059509 | 0 | 122.4289 | 122.3099 | -0.013733 | 122.4197 | 122.4655 | 0.15564 | -0.041199 | 122.4152 | 122.3557 | -0.091553 | 122.3923 | 122.2549 | -0.10071 | -0.059509 | 122.4655 | 122.438 | 122.4243 | -0.16937 | 122.3877 | 122.4197 | 122.406 | -0.1236
1884.8125 | 122.525 | -122.3007 | 0.068665 | -0.0022127 | 0.024212 | 0.086248 | 0.025229 | -0.074663 | -0.02908 | 0.0063424 | 0.014954 | 0.010594 | -0.027466 | -0.010002 | -0.0080408 | 0.0116 | 0.091553 | 0.1236 | 0.14191 | 0.14191 | 0.068665 | 0.11902 | -0.041199 | 0.045776 | 0.11902 | -0.004578 | 0.004578 | 0.004578 | 0.10529 | 0.022888 | 122.4197 | 122.2595 | 0 | 122.4243 | 122.4426 | 0.18311 | 0.022888 | 122.406 | 122.3236 | -0.064087 | 122.3465 | 122.2961 | -0.027466 | -0.064087 | 122.3694 | 122.3923 | 122.4426 | -0.10986 | 122.3053 | 122.3053 | 122.4197 | -0.045777
1886.6094 | 122.5983 | -122.2687 | 0.059509 | 0.0054168 | 0.020367 | 0.080267 | 0.026083 | -0.073595 | -0.022031 | 0.005488 | 0.0073242 | 0.014012 | -0.027466 | -0.0093609 | -0.0048364 | 0.011173 | 0.13733 | 0.10529 | 0.14648 | 0.16022 | 0.091553 | 0.10071 | -0.027466 | 0.10986 | 0.15106 | 0.013733 | 0.009155 | 0.027466 | 0.10529 | 0.018311 | 122.3694 | 122.2412 | 0.032044 | 122.374 | 122.4289 | 0.18768 | 0.07782 | 122.374 | 122.287 | -0.050354 | 122.3785 | 122.2824 | -0.004578 | -0.032043 | 122.3602 | 122.406 | 122.4152 | -0.086975 | 122.2778 | 122.2961 | 122.4197 | -0.041198
1888.3281 | 122.5571 | -122.3099 | 0.073242 | 0.0054168 | 0.021435 | 0.083044 | 0.025015 | -0.0721 | -0.025876 | 0.0061288 | 0.0073242 | 0.012943 | -0.030883 | -0.0097883 | -0.0065454 | 0.0090363 | 0.12817 | 0.13733 | 0.16479 | 0.15564 | 0.07782 | 0.09613 | -0.013733 | 0.10529 | 0.15106 | 0.032043 | 0.018311 | 0.009155 | 0.10529 | 0.018311 | 122.406 | 122.2961 | 0.004578 | 122.4472 | 122.4655 | 0.16937 | 0.054932 | 122.4152 | 122.3282 | -0.054931 | 122.4152 | 122.3419 | 0.013732 | -0.064087 | 122.3877 | 122.438 | 122.4747 | -0.086975 | 122.3282 | 122.319 | 122.4609 | -0.054931
1890.1094 | 122.5525 | -122.3373 | 0.10071 | 0.0054168 | 0.023571 | 0.082616 | 0.028647 | -0.071886 | -0.027158 | 0.0052744 | 0.014954 | 0.011235 | -0.028961 | -0.0078657 | -0.008468 | 0.0096771 | 0.082397 | 0.07782 | 0.1236 | 0.13733 | 0.07782 | 0.09613 | -0.027466 | 0.045776 | 0.10071 | -0.018311 | 0.004578 | 0.032043 | 0.10529 | 0.013733 | 122.4335 | 122.3099 | -0.022888 | 122.4152 | 122.4747 | 0.16479 | -0.018311 | 122.4426 | 122.3511 | -0.09613 | 122.3831 | 122.319 | -0.032044 | -0.068665 | 122.4152 | 122.4197 | 122.4609 | -0.12817 | 122.3419 | 122.3694 | 122.438 | -0.086975
1891.9062 | 122.5067 | -122.3099 | 0.10986 | 0.013046 | 0.016735 | 0.08518 | 0.026938 | -0.0721 | -0.01904 | 0.0046334 | -0.0003053 | 0.017002 | -0.028534 | -0.0067975 | -0.002273 | 0.0096771 | 0.10071 | 0.054932 | 0.082397 | 0.13733 | 0.12817 | 0.064087 | -0.082397 | 0.073242 | 0.086975 | -0.050354 | 0.041199 | 0.064087 | 0.068665 | 0 | 122.374 | 122.2275 | 0.018311 | 122.3648 | 122.4472 | 0.21973 | -0.009155 | 122.3785 | 122.3099 | -0.068664 | 122.3831 | 122.2595 | -0.050354 | -0.045776 | 122.438 | 122.4106 | 122.3923 | -0.19226 | 122.3511 | 122.374 | 122.3969 | -0.10986
1893.625 | 122.58 | -122.3099 | 0.086975 | -0.0022127 | 0.022076 | 0.08753 | 0.025443 | -0.071032 | -0.029294 | 0.0067696 | 0.0073242 | 0.011875 | -0.028961 | -0.0089337 | -0.0069726 | 0.0092499 | 0.13733 | 0.17853 | 0.19226 | 0.17853 | 0.086975 | 0.086975 | -0.032043 | 0.091553 | 0.20599 | 0.054932 | 0 | 0.013733 | 0.11902 | 0.018311 | 122.3969 | 122.2778 | 0 | 122.4884 | 122.4884 | 0.21057 | 0.050354 | 122.4289 | 122.3282 | -0.086975 | 122.4014 | 122.3648 | 0.036621 | -0.073242 | 122.3969 | 122.4472 | 122.5021 | -0.11902 | 122.3099 | 122.3236 | 122.5159 | -0.068664
1895.4062 | 122.5525 | -122.3145 | 0.073242 | 0.013046 | 0.021649 | 0.086675 | 0.027579 | -0.075732 | -0.026944 | 0.0050608 | -0.0003053 | 0.0097391 | -0.028961 | -0.0089337 | -0.0044092 | 0.0116 | 0.091553 | 0.11444 | 0.13733 | 0.12817 | 0.09613 | 0.09613 | -0.032043 | 0.054932 | 0.11444 | -0.009155 | 0.009155 | 0.018311 | 0.11444 | 0.027466 | 122.4106 | 122.2824 | 0.022888 | 122.4289 | 122.4426 | 0.16022 | 0.018311 | 122.4289 | 122.3419 | -0.064087 | 122.3694 | 122.3053 | -0.036621 | -0.054931 | 122.4106 | 122.406 | 122.4518 | -0.10529 | 122.3236 | 122.3328 | 122.4289 | -0.045776
1897.1875 | 122.5021 | -122.3373 | 0.10529 | -0.0022127 | 0.015026 | 0.087957 | 0.026724 | -0.072527 | -0.022458 | 0.0033518 | -0.0003053 | 0.014012 | -0.026611 | -0.0080793 | -0.0061182 | 0.0079681 | 0.013733 | 0.013733 | 0.036621 | 0.082397 | 0.14191 | 0.059509 | -0.068665 | -0.009155 | 0.032043 | -0.10071 | 0.050354 | 0.064087 | 0.064087 | -0.022888 | 122.3969 | 122.2687 | 0.036621 | 122.3511 | 122.4197 | 0.15106 | -0.091553 | 122.4014 | 122.3145 | -0.054932 | 122.3282 | 122.2366 | -0.07782 | -0.041199 | 122.4792 | 122.3511 | 122.374 | -0.17395 | 122.3877 | 122.4014 | 122.3694 | -0.12817
1898.9062 | 122.5571 | -122.3557 | 0.091553 | 0.013046 | 0.022076 | 0.085394 | 0.026724 | -0.072954 | -0.026517 | 0.0076242 | -0.0003053 | 0.010594 | -0.027466 | -0.0082929 | -0.0082544 | 0.012241 | 0.10529 | 0.09613 | 0.13275 | 0.12817 | 0.07782 | 0.07782 | -0.045776 | 0.045776 | 0.11444 | -0.004578 | 0.009155 | -0.004578 | 0.10986 | 0.027466 | 122.4335 | 122.3099 | -0.013733 | 122.4518 | 122.4838 | 0.17395 | 0.013733 | 122.4655 | 122.3831 | -0.082398 | 122.4014 | 122.3511 | -0.032044 | -0.096131 | 122.4335 | 122.4609 | 122.4884 | -0.13733 | 122.3648 | 122.3511 | 122.4701 | -0.064087
1900.6875 | 122.5067 | -122.3282 | 0.091553 | 0.0054168 | 0.016094 | 0.085394 | 0.026083 | -0.072527 | -0.022244 | 0.008265 | 0.0073242 | 0.017643 | -0.028534 | -0.0093609 | -0.0044092 | 0.0071137 | 0.086975 | 0.050354 | 0.059509 | 0.13275 | 0.11902 | 0.064087 | -0.064087 | 0.045776 | 0.10529 | -0.045776 | 0.041199 | 0.059509 | 0.086975 | -0.004578 | 122.3923 | 122.2641 | 0.027466 | 122.3785 | 122.4609 | 0.19684 | -0.004578 | 122.4152 | 122.3236 | -0.050354 | 122.374 | 122.2824 | -0.041198 | -0.032044 | 122.4472 | 122.4152 | 122.3877 | -0.15564 | 122.3694 | 122.3877 | 122.4335 | -0.096131
1902.4688 | 122.5754 | -122.3236 | 0.068665 | 0.013046 | 0.02528 | 0.085394 | 0.025656 | -0.073382 | -0.026517 | 0.005488 | 0.0073242 | 0.011662 | -0.026611 | -0.010215 | -0.0074 | 0.012027 | 0.1236 | 0.15106 | 0.17395 | 0.16479 | 0.07782 | 0.10529 | -0.032043 | 0.086975 | 0.13275 | 0.022888 | -0.004578 | 0.004578 | 0.12817 | 0.013733 | 122.4289 | 122.2916 | 0.009155 | 122.4747 | 122.4884 | 0.19684 | 0.054931 | 122.4518 | 122.3373 | -0.073243 | 122.4106 | 122.3465 | 0.009155 | -0.064087 | 122.4014 | 122.4472 | 122.4976 | -0.10071 | 122.319 | 122.3282 | 122.4564 | -0.054932
1904.1875 | 122.5662 | -122.3145 | 0.07782 | -0.0022127 | 0.023358 | 0.086889 | 0.02587 | -0.074877 | -0.028867 | 0.005488 | 0.014954 | 0.011662 | -0.030243 | -0.0089337 | -0.006759 | 0.0083953 | 0.07782 | 0.082397 | 0.10529 | 0.11902 | 0.068665 | 0.082397 | -0.027466 | 0.032043 | 0.11444 | -0.013733 | 0.009155 | 0.018311 | 0.09613 | 0.004578 | 122.3969 | 122.287 | -0.009155 | 122.3969 | 122.4335 | 0.14649 | 0 | 122.4106 | 122.319 | -0.068665 | 122.3465 | 122.3007 | -0.018311 | -0.059509 | 122.3831 | 122.3923 | 122.4197 | -0.10529 | 122.3236 | 122.3328 | 122.4289 | -0.073242
1905.9688 | 122.5891 | -122.3236 | 0.07782 | 0.013046 | 0.023998 | 0.08518 | 0.027579 | -0.073382 | -0.027799 | 0.0057016 | -0.0003053 | 0.013584 | -0.027038 | -0.0095745 | -0.0080408 | 0.010318 | 0.059509 | 0.086975 | 0.10986 | 0.12817 | 0.10071 | 0.073242 | -0.027466 | 0.036621 | 0.10071 | -0.004578 | 0.027466 | 0.041199 | 0.07782 | 0.022888 | 122.3968 | 122.2961 | 0.022888 | 122.4106 | 122.4518 | 0.15564 | -0.018311 | 122.4014 | 122.3465 | -0.050354 | 122.3602 | 122.319 | -0.027466 | -0.036621 | 122.4243 | 122.3831 | 122.4335 | -0.10529 | 122.3511 | 122.3648 | 122.4243 | -0.054932
1907.75 | 122.612 | -122.3053 | 0.073242 | 0.013046 | 0.021862 | 0.085607 | 0.026724 | -0.073595 | -0.021604 | 0.0059152 | 0.0073242 | 0.013798 | -0.028961 | -0.0080793 | -0.0031274 | 0.0088227 | 0.12817 | 0.11444 | 0.16022 | 0.18768 | 0.086975 | 0.086975 | -0.032043 | 0.1236 | 0.14191 | 0.022888 | -0.013733 | 0 | 0.11902 | 0.036621 | 122.3923 | 122.2733 | 0.013733 | 122.4197 | 122.493 | 0.21973 | 0.054932 | 122.4243 | 122.3419 | -0.086975 | 122.4289 | 122.3282 | -0.013733 | -0.073242 | 122.3923 | 122.4335 | 122.4655 | -0.10529 | 122.2916 | 122.3053 | 122.4472 | -0.036621
1909.4688 | 122.5479 | -122.3328 | 0.07782 | -0.0022127 | 0.02528 | 0.084966 | 0.026297 | -0.070605 | -0.025235 | 0.0052744 | -0.0003053 | 0.011875 | -0.028106 | -0.0087201 | -0.0069726 | 0.0098907 | 0.10071 | 0.1236 | 0.13733 | 0.14648 | 0.091553 | 0.082397 | -0.018311 | 0.032043 | 0.10529 | -0.009155 | 0.009155 | 0.027466 | 0.11444 | 0.004578 | 122.4152 | 122.3145 | 0.013733 | 122.4564 | 122.4792 | 0.16479 | 0.022888 | 122.4472 | 122.3373 | -0.068665 | 122.3648 | 122.3236 | -0.013733 | -0.050354 | 122.4243 | 122.4335 | 122.4701 | -0.096131 | 122.3419 | 122.3602 | 122.4381 | -0.073242
1911.2656 | 122.6166 | -122.319 | 0.07782 | 0.0054168 | 0.022503 | 0.087316 | 0.029715 | -0.073168 | -0.025876 | 0.0039926 | 0.0073242 | 0.01038 | -0.026611 | -0.0087201 | -0.0082544 | 0.0075409 | 0.11444 | 0.15564 | 0.16022 | 0.16479 | 0.10071 | 0.091553 | -0.018311 | 0.10071 | 0.18768 | 0.059509 | -0.004578 | 0.022888 | 0.10071 | 0.018311 | 122.4106 | 122.3007 | 0.022888 | 122.4747 | 122.4838 | 0.18311 | 0.036621 | 122.4197 | 122.3373 | -0.082398 | 122.4197 | 122.3785 | 0.041198 | -0.054932 | 122.4197 | 122.4335 | 122.4792 | -0.096131 | 122.3145 | 122.3419 | 122.5067 | -0.059509
1912.9688 | 122.4747 | -122.3557 | 0.11444 | 0.0054168 | 0.015026 | 0.082616 | 0.026724 | -0.074023 | -0.018186 | 0.0080514 | 0.0073242 | 0.01807 | -0.025757 | -0.0074383 | -0.0031274 | 0.0071137 | 0.10529 | 0.091553 | 0.10071 | 0.12817 | 0.12817 | 0.07782 | -0.054932 | 0.068665 | 0.086975 | -0.073242 | 0.036621 | 0.036621 | 0.064087 | 0.004578 | 122.4335 | 122.3007 | 0.013733 | 122.4472 | 122.4838 | 0.18311 | -0.009155 | 122.4197 | 122.3602 | -0.07782 | 122.4243 | 122.2824 | -0.07782 | -0.07782 | 122.4838 | 122.4609 | 122.4564 | -0.16937 | 122.3923 | 122.3923 | 122.4426 | -0.10986
1914.75 | 122.6074 | -122.2961 | 0.082397 | 0.0054168 | 0.021435 | 0.084539 | 0.026083 | -0.071673 | -0.022672 | 0.005488 | -0.0003053 | 0.012303 | -0.026397 | -0.0072247 | -0.0014184 | 0.011173 | 0.1236 | 0.11444 | 0.15564 | 0.16022 | 0.086975 | 0.091553 | -0.045776 | 0.10986 | 0.13733 | 0.018311 | 0 | 0.018311 | 0.1236 | 0.022888 | 122.3877 | 122.2504 | 0.004578 | 122.4106 | 122.4564 | 0.20599 | 0.041199 | 122.4197 | 122.319 | -0.082397 | 122.406 | 122.3145 | -0.004577 | -0.064086 | 122.3831 | 122.4197 | 122.4518 | -0.12817 | 122.2961 | 122.3145 | 122.4335 | -0.059509
1916.5469 | 122.5616 | -122.3282 | 0.064087 | 0.0054168 | 0.025067 | 0.085394 | 0.027579 | -0.072954 | -0.027799 | 0.0052744 | 0.022583 | 0.012943 | -0.029175 | -0.0057293 | -0.0061182 | 0.010745 | 0.11444 | 0.13733 | 0.16022 | 0.16022 | 0.07782 | 0.10071 | -0.022888 | 0.09613 | 0.14648 | 0.022888 | 0.018311 | 0.018311 | 0.11444 | 0.004578 | 122.4289 | 122.3053 | 0.013733 | 122.4655 | 122.4884 | 0.1831 | 0.050354 | 122.4426 | 122.3328 | -0.045776 | 122.4243 | 122.3511 | 0.01831 | -0.045776 | 122.406 | 122.4426 | 122.4884 | -0.086975 | 122.3465 | 122.3465 | 122.4747 | -0.059509
1918.2656 | 122.5937 | -122.3282 | 0.073242 | 0.013046 | 0.01994 | 0.088812 | 0.026938 | -0.071459 | -0.027158 | 0.003138 | 0.0073242 | 0.011662 | -0.030456 | -0.010429 | -0.0063318 | 0.0098907 | 0.036621 | 0.091553 | 0.12817 | 0.13275 | 0.10529 | 0.10529 | -0.036621 | 0.050354 | 0.12817 | 0.013733 | 0.013733 | 0.022888 | 0.09613 | 0.013733 | 122.4335 | 122.2916 | 0.032044 | 122.4197 | 122.4609 | 0.16937 | -0.036621 | 122.4243 | 122.3419 | -0.059509 | 122.3785 | 122.3419 | 0 | -0.050354 | 122.4335 | 122.3648 | 122.4564 | -0.10986 | 122.3419 | 122.3511 | 122.4564 | -0.059509
1920.0469 | 122.5479 | -122.319 | 0.10986 | -0.0022127 | 0.019085 | 0.086034 | 0.029074 | -0.071673 | -0.025235 | 0.004847 | -0.0003053 | 0.012943 | -0.028747 | -0.0091473 | -0.0059046 | 0.0098907 | 0.12817 | 0.15564 | 0.17853 | 0.16022 | 0.086975 | 0.10071 | -0.041199 | 0.10529 | 0.17853 | 0.036621 | 0.009155 | 0.013733 | 0.10071 | 0.045776 | 122.4197 | 122.2778 | -0.022888 | 122.4747 | 122.4792 | 0.20142 | 0.018311 | 122.4197 | 122.3648 | -0.10071 | 122.4243 | 122.3557 | -0.009155 | -0.09613 | 122.406 | 122.4472 | 122.4976 | -0.15106 | 122.3282 | 122.3328 | 122.4976 | -0.064087
1921.8281 | 122.6212 | -122.3282 | 0.064087 | 0.013046 | 0.021862 | 0.085394 | 0.022238 | -0.071886 | -0.022244 | 0.0044198 | 0.0073242 | 0.015507 | -0.030883 | -0.0063703 | -0.0046228 | 0.0098907 | 0.082397 | 0.050354 | 0.073242 | 0.11444 | 0.11444 | 0.086975 | -0.054932 | 0.082397 | 0.10986 | 0.004578 | 0.004578 | 0.045776 | 0.11444 | 0.022888 | 122.4152 | 122.2733 | 0.050354 | 122.3785 | 122.4426 | 0.16937 | 0.01831 | 122.4426 | 122.3511 | -0.059509 | 122.4106 | 122.3328 | -0.01831 | -0.018311 | 122.4426 | 122.4106 | 122.4014 | -0.11902 | 122.3328 | 122.374 | 122.438 | -0.041199
1923.5469 | 122.6028 | -122.3419 | 0.086975 | -0.0022127 | 0.020794 | 0.084966 | 0.028433 | -0.069109 | -0.029508 | 0.003779 | -0.0003053 | 0.0099527 | -0.025329 | -0.0082929 | -0.0097498 | 0.0096771 | 0.13733 | 0.19684 | 0.19684 | 0.1831 | 0.09613 | 0.10071 | -0.032043 | 0.11444 | 0.21057 | 0.064087 | -0.009155 | 0.018311 | 0.086975 | 0.022888 | 122.4426 | 122.3099 | 0.009155 | 122.5388 | 122.525 | 0.21515 | 0.050354 | 122.4289 | 122.3648 | -0.09613 | 122.4564 | 122.406 | 0.041199 | -0.068664 | 122.438 | 122.4792 | 122.5388 | -0.11902 | 122.3328 | 122.3602 | 122.5525 | -0.064087
1925.3281 | 122.5937 | -122.3145 | 0.054932 | -0.0022127 | 0.024212 | 0.084112 | 0.025229 | -0.072314 | -0.022031 | 0.0063424 | -0.0003053 | 0.012089 | -0.029388 | -0.0078657 | -0.003982 | 0.0086091 | 0.12817 | 0.14191 | 0.17853 | 0.17853 | 0.086975 | 0.1236 | -0.018311 | 0.11902 | 0.16022 | 0.045776 | -0.009155 | 0 | 0.11444 | 0.036621 | 122.438 | 122.2961 | 0.032043 | 122.4564 | 122.493 | 0.19684 | 0.073242 | 122.4289 | 122.3511 | -0.064087 | 122.4335 | 122.3602 | 0.009155 | -0.054932 | 122.4014 | 122.4426 | 122.493 | -0.073243 | 122.3053 | 122.3145 | 122.4747 | -0.018311
1927.125 | 122.5204 | -122.3602 | 0.11902 | -0.0022127 | 0.019299 | 0.084325 | 0.027152 | -0.074023 | -0.021176 | 0.0078378 | 0.0073242 | 0.015934 | -0.02597 | -0.0065839 | -0.0035546 | 0.0086091 | 0.018311 | -0.009155 | 0.013733 | 0.10071 | 0.1236 | 0.064087 | -0.068665 | 0.004578 | -0.004578 | -0.10529 | 0.059509 | 0.059509 | 0.07782 | -0.013733 | 122.4243 | 122.2916 | 0.004577 | 122.3511 | 122.4609 | 0.16937 | -0.10071 | 122.438 | 122.3465 | -0.05951 | 122.3648 | 122.2549 | -0.091553 | -0.05951 | 122.4838 | 122.3785 | 122.374 | -0.18768 | 122.4197 | 122.4197 | 122.3557 | -0.13275
1928.8438 | 122.6303 | -122.3282 | 0.064087 | 0.020676 | 0.02293 | 0.085821 | 0.028006 | -0.073595 | -0.028867 | 0.0059152 | 0.0073242 | 0.010807 | -0.028534 | -0.0080793 | -0.0076136 | 0.010318 | 0.068665 | 0.11902 | 0.14191 | 0.12817 | 0.10529 | 0.09613 | -0.022888 | 0.07782 | 0.16937 | 0.045776 | 0 | 0.027466 | 0.1236 | 0.032043 | 122.4243 | 122.3053 | 0.041199 | 122.4472 | 122.4564 | 0.15106 | 0.004578 | 122.4518 | 122.3602 | -0.064087 | 122.406 | 122.374 | 0.013733 | -0.036621 | 122.4335 | 122.3969 | 122.4701 | -0.086975 | 122.3282 | 122.3557 | 122.4976 | -0.032044
1930.625 | 122.4884 | -122.3328 | 0.10986 | 0.0054168 | 0.014813 | 0.084112 | 0.02822 | -0.071245 | -0.018826 | 0.0076242 | 0.0073242 | 0.015934 | -0.026825 | -0.0093609 | -0.003982 | 0.0081817 | 0.11902 | 0.082397 | 0.09613 | 0.12817 | 0.10529 | 0.068665 | -0.068665 | 0.059509 | 0.07782 | -0.059509 | 0.027466 | 0.045776 | 0.086975 | -0.013733 | 122.4014 | 122.2641 | -0.004577 | 122.4152 | 122.4609 | 0.19684 | 0.009156 | 122.4197 | 122.319 | -0.082397 | 122.3923 | 122.2733 | -0.045776 | -0.064087 | 122.4381 | 122.4518 | 122.4289 | -0.17853 | 122.3602 | 122.3785 | 122.4106 | -0.1236
1932.3594 | 122.6028 | -122.3236 | 0.059509 | 0.013046 | 0.021008 | 0.082616 | 0.027152 | -0.070391 | -0.022458 | 0.0080514 | 0.014954 | 0.011875 | -0.025329 | -0.010215 | -0.0054772 | 0.0088227 | 0.10986 | 0.1236 | 0.15564 | 0.17395 | 0.082397 | 0.091553 | -0.009155 | 0.10529 | 0.15564 | 0.027466 | -0.009155 | 0.009155 | 0.10986 | 0.022888 | 122.4152 | 122.3145 | 0.022888 | 122.4472 | 122.4976 | 0.1831 | 0.050354 | 122.4335 | 122.3465 | -0.068664 | 122.4289 | 122.3511 | 0.004578 | -0.050354 | 122.406 | 122.4335 | 122.4792 | -0.068664 | 122.3145 | 122.3328 | 122.4792 | -0.036621
1934.1406 | 122.5571 | -122.3557 | 0.10529 | 0.013046 | 0.015026 | 0.081335 | 0.02886 | -0.071459 | -0.020535 | 0.0067696 | 0.014954 | 0.018711 | -0.026184 | -0.0059429 | -0.0046228 | 0.0083953 | 0.059509 | 0.050354 | 0.064087 | 0.12817 | 0.1236 | 0.059509 | -0.059509 | 0.036621 | 0.10071 | -0.041199 | 0.041199 | 0.050354 | 0.086975 | -0.009155 | 122.4152 | 122.2961 | 0.01831 | 122.406 | 122.4838 | 0.18768 | -0.045777 | 122.4426 | 122.3465 | -0.064087 | 122.3923 | 122.3145 | -0.032044 | -0.054932 | 122.4792 | 122.4152 | 122.4197 | -0.16479 | 122.3969 | 122.406 | 122.4564 | -0.11444
1935.9062 | 122.5388 | -122.3785 | 0.10529 | 0.0054168 | 0.01759 | 0.08518 | 0.030997 | -0.069537 | -0.024167 | 0.005488 | 0.0073242 | 0.015507 | -0.025329 | -0.0074383 | -0.0074 | 0.010745 | 0.009155 | 0.018311 | 0.036621 | 0.086975 | 0.1236 | 0.064087 | -0.07782 | -0.027466 | 0.050354 | -0.086975 | 0.064087 | 0.054932 | 0.068665 | -0.009155 | 122.4426 | 122.3007 | 0.01831 | 122.3969 | 122.4655 | 0.16479 | -0.096131 | 122.4472 | 122.3694 | -0.041199 | 122.3511 | 122.2916 | -0.07782 | -0.050354 | 122.5021 | 122.3877 | 122.4152 | -0.18311 | 122.4426 | 122.4335 | 122.4289 | -0.11444
1937.6406 | 122.5983 | -122.3236 | 0.082397 | 0.013046 | 0.020153 | 0.083471 | 0.023947 | -0.074877 | -0.022244 | 0.0046334 | 0.014954 | 0.015721 | -0.028106 | -0.0074383 | -0.0048364 | 0.010104 | 0.018311 | 0.013733 | 0.022888 | 0.073242 | 0.12817 | 0.064087 | -0.07782 | 0.004578 | 0.036621 | -0.086975 | 0.045776 | 0.054932 | 0.07782 | -0.004578 | 122.3877 | 122.2458 | 0.045777 | 122.3373 | 122.3968 | 0.15106 | -0.064086 | 122.4014 | 122.319 | -0.036621 | 122.3282 | 122.2366 | -0.082397 | -0.027465 | 122.4518 | 122.3419 | 122.3465 | -0.16022 | 122.3694 | 122.3785 | 122.3602 | -0.086975
1939.4375 | 122.5479 | -122.3694 | 0.091553 | -0.0022127 | 0.015881 | 0.084112 | 0.028647 | -0.071459 | -0.022458 | 0.0076242 | 0.0073242 | 0.01807 | -0.026397 | -0.0078657 | -0.0041956 | 0.0094635 | 0.032043 | 0.027466 | 0.059509 | 0.11444 | 0.1236 | 0.054932 | -0.073242 | 0.032043 | 0.10529 | -0.054932 | 0.050354 | 0.045776 | 0.073242 | -0.018311 | 122.4243 | 122.2961 | 0.032043 | 122.3969 | 122.4838 | 0.18768 | -0.05951 | 122.4426 | 122.3511 | -0.041199 | 122.4014 | 122.3145 | -0.036621 | -0.045777 | 122.493 | 122.4014 | 122.4289 | -0.16479 | 122.4197 | 122.4152 | 122.4747 | -0.10986
1941.1719 | 122.5388 | -122.3877 | 0.10529 | 0.013046 | 0.013531 | 0.088384 | 0.025656 | -0.073809 | -0.02609 | 0.0057016 | 0.0073242 | 0.014652 | -0.029388 | -0.010002 | -0.0052636 | 0.012241 | 0.018311 | 0.027466 | 0.022888 | 0.086975 | 0.1236 | 0.045776 | -0.064087 | -0.022888 | 0.045776 | -0.10071 | 0.045776 | 0.064087 | 0.059509 | -0.009155 | 122.4335 | 122.3236 | 0.01831 | 122.4152 | 122.4747 | 0.15106 | -0.086975 | 122.4472 | 122.3785 | -0.05951 | 122.3648 | 122.287 | -0.091553 | -0.041199 | 122.5113 | 122.406 | 122.4106 | -0.16937 | 122.4335 | 122.4518 | 122.4335 | -0.11444
1942.9688 | 122.6303 | -122.3419 | 0.09613 | 0.013046 | 0.024639 | 0.087743 | 0.027792 | -0.073595 | -0.030149 | 0.0027108 | -0.0003053 | 0.0099527 | -0.027038 | -0.0091473 | -0.0078272 | 0.010318 | 0.11902 | 0.18768 | 0.19226 | 0.17395 | 0.10529 | 0.086975 | -0.032043 | 0.082397 | 0.20142 | 0.064087 | 0.009155 | 0.009155 | 0.10529 | 0.013733 | 122.4289 | 122.3099 | 0.009156 | 122.5296 | 122.5159 | 0.20599 | 0.022889 | 122.4472 | 122.3557 | -0.086975 | 122.4243 | 122.406 | 0.050354 | -0.086975 | 122.4472 | 122.4609 | 122.5342 | -0.12817 | 122.3511 | 122.3511 | 122.5433 | -0.082397
1944.6875 | 122.6166 | -122.3282 | 0.068665 | 0.0054168 | 0.022717 | 0.08048 | 0.027365 | -0.072741 | -0.022031 | 0.0050608 | 0.014954 | 0.015293 | -0.027679 | -0.0082929 | -0.006759 | 0.0092499 | 0.036621 | -0.004578 | 0.059509 | 0.091553 | 0.10986 | 0.073242 | -0.059509 | 0.041199 | 0.054932 | -0.045776 | 0.027466 | 0.027466 | 0.09613 | 0.022888 | 122.4014 | 122.2687 | 0.041198 | 122.3236 | 122.4197 | 0.15106 | -0.032044 | 122.4243 | 122.3511 | -0.041199 | 122.3694 | 122.2824 | -0.068664 | -0.041199 | 122.438 | 122.3648 | 122.3877 | -0.12817 | 122.3557 | 122.3557 | 122.3831 | -0.045777
1946.4688 | 122.5479 | -122.3694 | 0.11444 | 0.0054168 | 0.015667 | 0.084753 | 0.026724 | -0.072741 | -0.021817 | 0.0061288 | 0.014954 | 0.016575 | -0.027893 | -0.0057293 | -0.0052636 | 0.010318 | 0.004578 | -0.027466 | 0 | 0.082397 | 0.11444 | 0.059509 | -0.064087 | -0.018311 | 0.013733 | -0.10986 | 0.036621 | 0.073242 | 0.07782 | -0.022888 | 122.4289 | 122.3053 | 0 | 122.3419 | 122.4518 | 0.14648 | -0.10986 | 122.4472 | 122.3465 | -0.07782 | 122.3511 | 122.2595 | -0.086975 | -0.041199 | 122.4838 | 122.374 | 122.3694 | -0.17853 | 122.406 | 122.4426 | 122.3831 | -0.13733
1948.1875 | 122.5388 | -122.3648 | 0.10529 | -0.0022127 | 0.013531 | 0.086034 | 0.02822 | -0.071459 | -0.024167 | 0.0046334 | -0.0003053 | 0.017002 | -0.026611 | -0.0055157 | -0.0069726 | 0.0090363 | 0.027466 | -0.004578 | 0.022888 | 0.09613 | 0.13733 | 0.045776 | -0.07782 | -0.027466 | 0.041199 | -0.10071 | 0.045776 | 0.064087 | 0.036621 | -0.004578 | 122.4106 | 122.287 | 0.032043 | 122.3602 | 122.4609 | 0.17395 | -0.07782 | 122.4014 | 122.3602 | -0.05951 | 122.3373 | 122.2641 | -0.09613 | -0.041199 | 122.5021 | 122.3923 | 122.3877 | -0.18311 | 122.4106 | 122.4289 | 122.406 | -0.10986
1949.9688 | 122.5021 | -122.374 | 0.09613 | 0.013046 | 0.017803 | 0.087103 | 0.026724 | -0.071245 | -0.027799 | 0.0042062 | 0.0073242 | 0.011021 | -0.028747 | -0.010002 | -0.0088952 | 0.0094635 | 0.07782 | 0.14191 | 0.16479 | 0.16022 | 0.09613 | 0.082397 | -0.032043 | 0.050354 | 0.15106 | 0 | 0 | 0.045776 | 0.091553 | 0.004578 | 122.4564 | 122.3419 | 0 | 122.5159 | 122.5342 | 0.19226 | -0.01831 | 122.4655 | 122.3785 | -0.09613 | 122.4243 | 122.374 | -0.004578 | -0.050354 | 122.4701 | 122.4518 | 122.5388 | -0.12817 | 122.374 | 122.4197 | 122.525 | -0.091552
1951.75 | 122.4976 | -122.3969 | 0.10986 | -0.0022127 | 0.015667 | 0.089452 | 0.029288 | -0.070818 | -0.025235 | 0.003779 | 0.0073242 | 0.014012 | -0.028961 | -0.0080793 | -0.0076136 | 0.0098907 | 0.013733 | 0.022888 | 0.036621 | 0.073242 | 0.13275 | 0.064087 | -0.07782 | -0.045776 | 0.045776 | -0.073242 | 0.059509 | 0.050354 | 0.064087 | -0.004578 | 122.4609 | 122.319 | 0.022888 | 122.4197 | 122.4701 | 0.15106 | -0.09613 | 122.4609 | 122.3923 | -0.050354 | 122.3511 | 122.3236 | -0.068664 | -0.059509 | 122.5296 | 122.4106 | 122.4335 | -0.18768 | 122.4564 | 122.4472 | 122.4426 | -0.11444
1953.5156 | 122.5479 | -122.3831 | 0.10529 | 0.0054168 | 0.016949 | 0.083257 | 0.029501 | -0.072527 | -0.023953 | 0.0024972 | 0.0073242 | 0.013371 | -0.025757 | -0.0070111 | -0.005691 | 0.0092499 | 0.009155 | 0.009155 | 0.036621 | 0.068665 | 0.14648 | 0.059509 | -0.073242 | -0.032043 | 0.036621 | -0.086975 | 0.054932 | 0.059509 | 0.068665 | -0.018311 | 122.4426 | 122.3099 | 0.041198 | 122.3923 | 122.4518 | 0.14191 | -0.096131 | 122.4518 | 122.3648 | -0.050354 | 122.3511 | 122.2961 | -0.068664 | -0.045777 | 122.5296 | 122.3923 | 122.4197 | -0.17853 | 122.438 | 122.4426 | 122.4197 | -0.1236
1955.2969 | 122.525 | -122.3969 | 0.10529 | -0.0022127 | 0.017376 | 0.086889 | 0.030783 | -0.075945 | -0.025449 | 0.0027108 | 0.014954 | 0.014225 | -0.026825 | -0.0078657 | -0.0071862 | 0.010318 | 0 | 0.004578 | 0.041199 | 0.07782 | 0.13733 | 0.050354 | -0.068665 | -0.032043 | 0.045776 | -0.07782 | 0.022888 | 0.073242 | 0.059509 | -0.018311 | 122.4472 | 122.3282 | 0.032043 | 122.4014 | 122.4747 | 0.14649 | -0.10529 | 122.4564 | 122.3785 | -0.082398 | 122.3648 | 122.319 | -0.059509 | -0.032044 | 122.5342 | 122.3969 | 122.4381 | -0.17395 | 122.4197 | 122.4701 | 122.4426 | -0.1236
1957.0781 | 122.5113 | -122.3877 | 0.10986 | 0.013046 | 0.016308 | 0.088598 | 0.02886 | -0.07445 | -0.025449 | 0.0022836 | 0.0073242 | 0.013584 | -0.026611 | -0.0082929 | -0.0059046 | 0.010959 | -0.004578 | 0.041199 | 0.054932 | 0.086975 | 0.1236 | 0.068665 | -0.086975 | -0.027466 | 0.050354 | -0.07782 | 0.045776 | 0.064087 | 0.059509 | 0 | 122.4564 | 122.3007 | 0.013733 | 122.4289 | 122.4747 | 0.17395 | -0.11444 | 122.4472 | 122.3877 | -0.064087 | 122.3602 | 122.3099 | -0.07782 | -0.045776 | 122.5113 | 122.3831 | 122.4426 | -0.19684 | 122.4335 | 122.4518 | 122.438 | -0.10986
1958.8438 | 122.6349 | -122.374 | 0.073242 | 0.035934 | 0.023571 | 0.085821 | 0.027579 | -0.072741 | -0.030576 | 0.0029244 | 0.022583 | 0.010807 | -0.028534 | -0.010215 | -0.0086816 | 0.010745 | 0.12817 | 0.16937 | 0.19684 | 0.17853 | 0.086975 | 0.09613 | -0.036621 | 0.082397 | 0.21057 | 0.050354 | -0.013733 | 0.004578 | 0.11902 | 0.041199 | 122.4701 | 122.3373 | 0.013733 | 122.5433 | 122.5525 | 0.21515 | 0.054932 | 122.493 | 122.4152 | -0.086975 | 122.4564 | 122.4243 | 0.009155 | -0.068664 | 122.4609 | 122.5021 | 122.5708 | -0.10986 | 122.3602 | 122.3785 | 122.5845 | -0.032043
1960.5625 | 122.58 | -122.3557 | 0.086975 | 0.0054168 | 0.024639 | 0.084753 | 0.024588 | -0.071673 | -0.02374 | 0.0046334 | 0.014954 | 0.011662 | -0.028534 | -0.0091473 | -0.003341 | 0.0092499 | 0.12817 | 0.13733 | 0.17853 | 0.16479 | 0.082397 | 0.091553 | -0.027466 | 0.09613 | 0.15106 | 0.027466 | -0.004578 | 0.004578 | 0.091553 | 0.036621 | 122.4472 | 122.3282 | -0.004578 | 122.493 | 122.5204 | 0.19226 | 0.041199 | 122.4472 | 122.3923 | -0.091553 | 122.4518 | 122.3831 | -0.009155 | -0.082397 | 122.438 | 122.4838 | 122.5342 | -0.11444 | 122.3511 | 122.3602 | 122.5067 | -0.050354
1962.3438 | 122.5708 | -122.3785 | 0.10986 | 0.013046 | 0.016522 | 0.087316 | 0.031424 | -0.0721 | -0.021604 | 0.0039926 | 0.0073242 | 0.01508 | -0.026397 | -0.0067975 | -0.006759 | 0.0094635 | 0.013733 | 0.009155 | 0.027466 | 0.09613 | 0.13275 | 0.045776 | -0.073242 | -0.022888 | 0.045776 | -0.09613 | 0.041199 | 0.059509 | 0.073242 | -0.013733 | 122.4243 | 122.3053 | 0.022888 | 122.3877 | 122.4747 | 0.16937 | -0.09613 | 122.4518 | 122.3648 | -0.068664 | 122.3557 | 122.2824 | -0.082397 | -0.050354 | 122.5113 | 122.3923 | 122.406 | -0.18311 | 122.4197 | 122.438 | 122.4243 | -0.1236
1964.0781 | 122.5616 | -122.3694 | 0.091553 | -0.0022127 | 0.014385 | 0.083685 | 0.02886 | -0.072954 | -0.021176 | 0.004847 | 0.0073242 | 0.017643 | -0.028747 | -0.0074383 | -0.0054772 | 0.0088227 | 0.032043 | 0.018311 | 0.050354 | 0.10529 | 0.12817 | 0.054932 | -0.082397 | 0 | 0.068665 | -0.07782 | 0.041199 | 0.059509 | 0.07782 | 0 | 122.4243 | 122.287 | 0.036621 | 122.3877 | 122.4747 | 0.18768 | -0.05951 | 122.4472 | 122.3694 | -0.050354 | 122.3694 | 122.2916 | -0.07782 | -0.032044 | 122.4976 | 122.4014 | 122.4197 | -0.17395 | 122.4106 | 122.4289 | 122.438 | -0.091553
1965.8594 | 122.6349 | -122.3282 | 0.064087 | 0.020676 | 0.023358 | 0.087743 | 0.029074 | -0.072954 | -0.029721 | 0.0046334 | 0.014954 | 0.010807 | -0.027679 | -0.0097883 | -0.0059046 | 0.012241 | 0.11902 | 0.19226 | 0.19684 | 0.18768 | 0.082397 | 0.086975 | -0.027466 | 0.07782 | 0.18768 | 0.064087 | -0.004578 | 0.022888 | 0.10529 | 0.032043 | 122.4152 | 122.3007 | 0.01831 | 122.5204 | 122.5159 | 0.21515 | 0.054932 | 122.4335 | 122.3602 | -0.068665 | 122.406 | 122.3923 | 0.032044 | -0.041199 | 122.4106 | 122.4472 | 122.525 | -0.091553 | 122.3236 | 122.3511 | 122.5159 | -0.032044
1967.6562 | 122.6166 | -122.3648 | 0.07782 | -0.0022127 | 0.022076 | 0.084539 | 0.022879 | -0.072314 | -0.020963 | 0.0050608 | 0.014954 | 0.014652 | -0.029175 | -0.0072247 | -0.0018458 | 0.0086091 | 0.054932 | 0 | 0.009155 | 0.086975 | 0.12817 | 0.064087 | -0.068665 | -0.009155 | 0.027466 | -0.091553 | 0.045776 | 0.064087 | 0.064087 | -0.004578 | 122.4289 | 122.2961 | 0.050354 | 122.3648 | 122.4518 | 0.15564 | -0.022888 | 122.4289 | 122.3602 | -0.032044 | 122.3557 | 122.2733 | -0.086975 | -0.013733 | 122.493 | 122.4197 | 122.374 | -0.14649 | 122.4106 | 122.4289 | 122.3923 | -0.082398
1969.3906 | 122.5525 | -122.3969 | 0.09613 | 0.0054168 | 0.016735 | 0.084539 | 0.027579 | -0.075091 | -0.025022 | 0.0046334 | 0.014954 | 0.014866 | -0.027466 | -0.0076519 | -0.0074 | 0.010104 | 0.004578 | 0.018311 | 0.027466 | 0.064087 | 0.1236 | 0.041199 | -0.073242 | -0.022888 | 0.041199 | -0.09613 | 0.041199 | 0.054932 | 0.059509 | -0.022888 | 122.4381 | 122.3236 | 0.027466 | 122.4152 | 122.4609 | 0.13733 | -0.091552 | 122.4564 | 122.374 | -0.054931 | 122.374 | 122.3007 | -0.073242 | -0.041198 | 122.5204 | 122.4014 | 122.4243 | -0.16937 | 122.4381 | 122.4518 | 122.4381 | -0.11902
1971.1562 | 122.5159 | -122.374 | 0.091553 | 0.0054168 | 0.01524 | 0.084753 | 0.023093 | -0.073382 | -0.021817 | 0.0059152 | 0.014954 | 0.015293 | -0.028106 | -0.0061567 | -0.0027002 | 0.010532 | 0.10071 | 0.086975 | 0.082397 | 0.13275 | 0.13275 | 0.059509 | -0.059509 | 0.041199 | 0.091553 | -0.064087 | 0.045776 | 0.054932 | 0.086975 | 0 | 122.4335 | 122.3145 | 0.041198 | 122.4609 | 122.5067 | 0.19226 | 0.009155 | 122.4609 | 122.374 | -0.045777 | 122.4152 | 122.3099 | -0.064087 | -0.036621 | 122.5067 | 122.4747 | 122.4564 | -0.15106 | 122.4197 | 122.4289 | 122.4655 | -0.091553
1972.9375 | 122.5342 | -122.3923 | 0.086975 | -0.0022127 | 0.017803 | 0.091161 | 0.029288 | -0.072314 | -0.026731 | 0.0033518 | 0.014954 | 0.012303 | -0.025543 | -0.0093609 | -0.0069726 | 0.011173 | 0.064087 | 0.12817 | 0.13275 | 0.16022 | 0.10529 | 0.073242 | -0.050354 | 0.009155 | 0.12817 | -0.036621 | 0.036621 | 0.041199 | 0.086975 | 0.004578 | 122.4655 | 122.3419 | 0.018311 | 122.5204 | 122.5525 | 0.21057 | -0.022888 | 122.4792 | 122.3969 | -0.050354 | 122.4014 | 122.3557 | -0.041199 | -0.045776 | 122.4976 | 122.4564 | 122.525 | -0.13733 | 122.4289 | 122.4335 | 122.5204 | -0.082397
1974.7188 | 122.612 | -122.3602 | 0.091553 | 0.0054168 | 0.023785 | 0.089239 | 0.026511 | -0.072954 | -0.02908 | 0.003779 | 0.0073242 | 0.011021 | -0.029815 | -0.0097883 | -0.0069726 | 0.012454 | 0.036621 | 0.082397 | 0.11444 | 0.12817 | 0.086975 | 0.07782 | -0.036621 | 0.009155 | 0.10071 | -0.018311 | 0.018311 | 0.027466 | 0.07782 | 0.009155 | 122.438 | 122.3236 | -0.004578 | 122.4426 | 122.4884 | 0.1648 | -0.054932 | 122.438 | 122.3694 | -0.073242 | 122.3694 | 122.3419 | -0.027466 | -0.064087 | 122.4472 | 122.3969 | 122.4747 | -0.12817 | 122.3785 | 122.3877 | 122.4609 | -0.082398
1976.4375 | 122.5204 | -122.4014 | 0.091553 | 0.013046 | 0.015453 | 0.085821 | 0.027792 | -0.072527 | -0.017972 | 0.0052744 | 0.022583 | 0.016575 | -0.025757 | -0.0061567 | -0.003341 | 0.010532 | 0.045776 | 0.027466 | 0.041199 | 0.09613 | 0.11902 | 0.059509 | -0.068665 | -0.004578 | 0.018311 | -0.13275 | 0.064087 | 0.045776 | 0.068665 | -0.018311 | 122.4609 | 122.3328 | 0.027466 | 122.4289 | 122.4976 | 0.16479 | -0.045777 | 122.4701 | 122.3831 | -0.027466 | 122.3969 | 122.2687 | -0.11444 | -0.045777 | 122.5204 | 122.4472 | 122.4426 | -0.16022 | 122.4655 | 122.4472 | 122.4197 | -0.10986
1978.2344 | 122.6395 | -122.3465 | 0.064087 | 0.020676 | 0.019726 | 0.086248 | 0.025443 | -0.070605 | -0.022031 | 0.007197 | 0.0073242 | 0.016789 | -0.027679 | -0.0091473 | -0.0037684 | 0.011386 | 0.013733 | 0.018311 | 0.041199 | 0.086975 | 0.1236 | 0.07782 | -0.045776 | 0.022888 | 0.032043 | -0.068665 | 0.032043 | 0.036621 | 0.10071 | 0.009155 | 122.4243 | 122.3007 | 0.059509 | 122.3648 | 122.4335 | 0.13275 | -0.050354 | 122.4472 | 122.3557 | -0.032044 | 122.3694 | 122.2778 | -0.07782 | -0.027466 | 122.4701 | 122.3602 | 122.3877 | -0.10986 | 122.3785 | 122.3831 | 122.3785 | -0.054932
1980 | 122.6257 | -122.3511 | 0.086975 | -0.0022127 | 0.026348 | 0.086675 | 0.028647 | -0.072741 | -0.027585 | 0.0044198 | 0.0073242 | 0.01273 | -0.027252 | -0.0093609 | -0.0093226 | 0.010104 | 0.045776 | 0.07782 | 0.1236 | 0.13275 | 0.091553 | 0.091553 | -0.027466 | 0.018311 | 0.10986 | -0.004578 | 0.004578 | 0.036621 | 0.10071 | 0.022888 | 122.4426 | 122.3236 | 0.004578 | 122.4289 | 122.4838 | 0.16022 | -0.041199 | 122.4518 | 122.374 | -0.082397 | 122.3694 | 122.3465 | -0.027466 | -0.050354 | 122.4426 | 122.3969 | 122.4747 | -0.11444 | 122.3557 | 122.3877 | 122.4609 | -0.064087
1981.7656 | 122.6532 | -122.3557 | 0.054932 | 0.013046 | 0.024212 | 0.086462 | 0.023734 | -0.070605 | -0.024594 | 0.0029244 | 0.014954 | 0.01273 | -0.02832 | -0.0089337 | -0.0037684 | 0.0086091 | 0.11902 | 0.13275 | 0.14648 | 0.16937 | 0.09613 | 0.086975 | -0.032043 | 0.10071 | 0.13733 | 0.032043 | -0.004578 | -0.004578 | 0.10986 | 0.041199 | 122.4426 | 122.3236 | 0.041198 | 122.4884 | 122.525 | 0.20142 | 0.064087 | 122.4655 | 122.3969 | -0.05951 | 122.4564 | 122.3877 | -0.009156 | -0.05951 | 122.4518 | 122.4747 | 122.5021 | -0.086975 | 122.3511 | 122.3511 | 122.493 | -0.013733
1983.5625 | 122.5388 | -122.3969 | 0.11444 | 0.0054168 | 0.01994 | 0.086675 | 0.032065 | -0.070605 | -0.027585 | 0.003779 | 0.0073242 | 0.015293 | -0.029602 | -0.0097883 | -0.0097498 | 0.010104 | 0.082397 | 0.10529 | 0.12817 | 0.14648 | 0.091553 | 0.07782 | -0.054932 | 0 | 0.10071 | -0.041199 | 0.045776 | 0.045776 | 0.086975 | 0 | 122.4747 | 122.3419 | -0.022888 | 122.5021 | 122.5433 | 0.20142 | -0.032044 | 122.4838 | 122.3969 | -0.068665 | 122.3969 | 122.3557 | -0.041199 | -0.068665 | 122.4884 | 122.4792 | 122.525 | -0.16937 | 122.4426 | 122.4426 | 122.4976 | -0.11444
1985.2812 | 122.6486 | -122.3648 | 0.064087 | 0.013046 | 0.02528 | 0.082616 | 0.02822 | -0.070177 | -0.025022 | 0.0061288 | 0.0073242 | 0.013157 | -0.027679 | -0.0074383 | -0.0054772 | 0.0086091 | 0.13275 | 0.11444 | 0.15564 | 0.17853 | 0.082397 | 0.10529 | -0.009155 | 0.11444 | 0.14191 | 0.027466 | 0 | 0.018311 | 0.11902 | 0.036621 | 122.4701 | 122.3557 | 0.01831 | 122.4792 | 122.5433 | 0.18768 | 0.068664 | 122.4838 | 122.4014 | -0.064087 | 122.4792 | 122.3923 | -0.009155 | -0.045776 | 122.4472 | 122.4976 | 122.5204 | -0.073242 | 122.3648 | 122.3831 | 122.5067 | -0.027466
1987.0781 | 122.6669 | -122.3694 | 0.064087 | 0.0054168 | 0.024212 | 0.087957 | 0.030569 | -0.073382 | -0.029294 | 0.0042062 | -0.0003053 | 0.013371 | -0.027252 | -0.0080793 | -0.008468 | 0.011173 | 0.041199 | 0.082397 | 0.10986 | 0.1236 | 0.11444 | 0.082397 | -0.032043 | 0.036621 | 0.11902 | 0.004578 | 0.032043 | 0.018311 | 0.10529 | 0.009155 | 122.4518 | 122.3373 | 0.050354 | 122.4518 | 122.493 | 0.15564 | -0.022888 | 122.4747 | 122.3785 | -0.032044 | 122.406 | 122.374 | -0.004577 | -0.045776 | 122.4838 | 122.4106 | 122.4792 | -0.09613 | 122.4014 | 122.3877 | 122.4884 | -0.054932
1988.7812 | 122.5296 | -122.3923 | 0.11444 | 0.013046 | 0.01759 | 0.08753 | 0.031424 | -0.073168 | -0.024381 | 0.0033518 | -0.0003053 | 0.016361 | -0.027466 | -0.0061567 | -0.00505 | 0.0071137 | 0.032043 | 0.009155 | 0.041199 | 0.082397 | 0.13275 | 0.054932 | -0.07782 | -0.018311 | 0.041199 | -0.086975 | 0.068665 | 0.064087 | 0.059509 | -0.009155 | 122.4472 | 122.3145 | 0.01831 | 122.4014 | 122.4747 | 0.16022 | -0.082398 | 122.4518 | 122.3831 | -0.045776 | 122.374 | 122.3053 | -0.07782 | -0.050354 | 122.525 | 122.4243 | 122.4335 | -0.19226 | 122.4609 | 122.4564 | 122.4335 | -0.1236
1990.5625 | 122.5891 | -122.3831 | 0.091553 | 0.0054168 | 0.022289 | 0.090093 | 0.027792 | -0.071032 | -0.027158 | 0.003138 | 0.014954 | 0.013371 | -0.029815 | -0.0070111 | -0.00505 | 0.010318 | 0.11902 | 0.16937 | 0.19684 | 0.17395 | 0.07782 | 0.086975 | -0.032043 | 0.09613 | 0.18768 | 0.050354 | 0.004578 | 0.013733 | 0.11444 | 0.027466 | 122.4701 | 122.3511 | -0.013733 | 122.5525 | 122.5571 | 0.20599 | 0.027466 | 122.4976 | 122.4106 | -0.086975 | 122.4792 | 122.4335 | 0.022888 | -0.07782 | 122.4609 | 122.5021 | 122.58 | -0.1236 | 122.3877 | 122.3969 | 122.5708 | -0.064087
1992.2812 | 122.5616 | -122.3923 | 0.10071 | 0.0054168 | 0.023571 | 0.087957 | 0.028006 | -0.072741 | -0.026517 | 0.0035654 | 0.014954 | 0.011448 | -0.030029 | -0.010215 | -0.0054772 | 0.010532 | 0.12817 | 0.16022 | 0.16479 | 0.1831 | 0.086975 | 0.09613 | -0.027466 | 0.082397 | 0.16937 | 0.027466 | 0.018311 | 0.022888 | 0.10986 | 0.013733 | 122.4884 | 122.3648 | -0.013733 | 122.5525 | 122.5754 | 0.21057 | 0.027466 | 122.5021 | 122.406 | -0.082397 | 122.4747 | 122.4197 | 0.013733 | -0.07782 | 122.4792 | 122.5204 | 122.5571 | -0.12817 | 122.4106 | 122.4152 | 122.5616 | -0.086975
1994.0625 | 122.6486 | -122.374 | 0.086975 | 0.0054168 | 0.024853 | 0.086675 | 0.026083 | -0.075304 | -0.025022 | 0.004847 | 0.0073242 | 0.014225 | -0.029175 | -0.0082929 | -0.0074 | 0.0098907 | 0.054932 | 0.068665 | 0.11444 | 0.11444 | 0.10529 | 0.073242 | -0.045776 | 0.032043 | 0.10071 | -0.018311 | 0.022888 | 0.013733 | 0.086975 | 0.009155 | 122.4472 | 122.3282 | 0.018311 | 122.4426 | 122.4884 | 0.16022 | -0.032043 | 122.4609 | 122.3831 | -0.064087 | 122.406 | 122.3557 | -0.027466 | -0.073242 | 122.4792 | 122.4289 | 122.4884 | -0.13275 | 122.3969 | 122.3877 | 122.4747 | -0.07782
1995.8281 | 122.6532 | -122.3923 | 0.082397 | 0.0054168 | 0.026989 | 0.089239 | 0.025229 | -0.07445 | -0.027799 | 0.0024972 | 0.014954 | 0.011235 | -0.029388 | -0.0091473 | -0.006759 | 0.011386 | 0.054932 | 0.10529 | 0.11902 | 0.13275 | 0.09613 | 0.07782 | -0.041199 | 0.054932 | 0.12817 | 0.013733 | 0.009155 | 0.022888 | 0.086975 | 0.032043 | 122.4701 | 122.3511 | 0.013733 | 122.4976 | 122.525 | 0.17395 | -0.027465 | 122.4792 | 122.4243 | -0.073242 | 122.4472 | 122.406 | -0.01831 | -0.059509 | 122.4884 | 122.4472 | 122.5113 | -0.1236 | 122.4014 | 122.4152 | 122.5204 | -0.050354
1997.5469 | 122.6349 | -122.3602 | 0.07782 | 0.0054168 | 0.027844 | 0.088812 | 0.026938 | -0.071459 | -0.023953 | 0.0016428 | 0.022583 | 0.014439 | -0.030456 | -0.0089337 | -0.0054772 | 0.012454 | 0.086975 | 0.082397 | 0.10529 | 0.13275 | 0.10071 | 0.07782 | -0.027466 | 0.041199 | 0.091553 | -0.022888 | 0.004578 | 0.032043 | 0.082397 | 0.013733 | 122.438 | 122.3328 | 0.022888 | 122.4426 | 122.493 | 0.16022 | 0.009155 | 122.4426 | 122.374 | -0.073242 | 122.4014 | 122.3373 | -0.036621 | -0.045777 | 122.4609 | 122.4472 | 122.4655 | -0.10529 | 122.3648 | 122.3923 | 122.4518 | -0.064087
1999.3281 | 122.5433 | -122.3969 | 0.1236 | 0.0054168 | 0.018658 | 0.087743 | 0.031424 | -0.071673 | -0.021817 | 0.0018564 | 0.014954 | 0.016361 | -0.028106 | -0.0089337 | -0.0076136 | 0.0081817 | 0.054932 | 0.022888 | 0.054932 | 0.07782 | 0.11902 | 0.068665 | -0.064087 | -0.009155 | 0.050354 | -0.082397 | 0.045776 | 0.064087 | 0.068665 | -0.004578 | 122.4655 | 122.3328 | -0.004577 | 122.4197 | 122.4747 | 0.14191 | -0.068664 | 122.4655 | 122.3923 | -0.07782 | 122.3877 | 122.3145 | -0.077819 | -0.059509 | 122.5159 | 122.4518 | 122.4518 | -0.18768 | 122.4426 | 122.4609 | 122.4472 | -0.12817
2001.0469 | 122.6212 | -122.3923 | 0.07782 | 0.013046 | 0.026135 | 0.089025 | 0.026511 | -0.073809 | -0.027585 | 0.003779 | 0.0073242 | 0.013371 | -0.030243 | -0.0076519 | -0.0071862 | 0.0088227 | 0.07782 | 0.09613 | 0.12817 | 0.12817 | 0.086975 | 0.086975 | -0.032043 | 0.041199 | 0.09613 | -0.009155 | 0.027466 | 0.018311 | 0.10529 | 0.018311 | 122.4792 | 122.3602 | 0.009155 | 122.4884 | 122.5204 | 0.16022 | 0 | 122.4976 | 122.4106 | -0.050354 | 122.4335 | 122.3831 | -0.027466 | -0.059509 | 122.4792 | 122.4701 | 122.5204 | -0.10986 | 122.4197 | 122.4106 | 122.4884 | -0.059509
2002.8281 | 122.5616 | -122.406 | 0.09613 | 0.020676 | 0.022717 | 0.089452 | 0.030783 | -0.070818 | -0.025876 | 0.0057016 | -0.0003053 | 0.014225 | -0.025757 | -0.0072247 | -0.0054772 | 0.0073273 | 0.13275 | 0.16937 | 0.1831 | 0.16937 | 0.09613 | 0.086975 | -0.032043 | 0.11444 | 0.1831 | 0.032043 | 0 | 0.036621 | 0.091553 | 0.036621 | 122.493 | 122.374 | 0 | 122.5754 | 122.5754 | 0.20142 | 0.036621 | 122.4976 | 122.4426 | -0.09613 | 122.5204 | 122.438 | -0.004578 | -0.059509 | 122.5021 | 122.5388 | 122.5891 | -0.12817 | 122.406 | 122.4426 | 122.5891 | -0.059509
2004.6094 | 122.6624 | -122.3648 | 0.073242 | 0.0054168 | 0.024212 | 0.085607 | 0.027365 | -0.073382 | -0.025876 | 0.0033518 | 0.0073242 | 0.011875 | -0.025757 | -0.0078657 | -0.0069726 | 0.010959 | 0.068665 | 0.068665 | 0.1236 | 0.13275 | 0.10529 | 0.091553 | -0.041199 | 0.064087 | 0.086975 | -0.004578 | 0.018311 | 0.032043 | 0.091553 | 0.009155 | 122.4564 | 122.3236 | 0.032044 | 122.4335 | 122.4976 | 0.17395 | -0.004577 | 122.4564 | 122.374 | -0.054931 | 122.4289 | 122.3602 | -0.013733 | -0.041199 | 122.4701 | 122.4335 | 122.4884 | -0.11444 | 122.3831 | 122.3969 | 122.4518 | -0.064087
2006.3906 | 122.5388 | -122.406 | 0.11444 | -0.0098417 | 0.017803 | 0.085607 | 0.024374 | -0.072314 | -0.01904 | 0.0067696 | 0.0073242 | 0.018284 | -0.027893 | -0.0063703 | -0.0012048 | 0.0077545 | 0.064087 | 0.013733 | 0.036621 | 0.07782 | 0.13275 | 0.059509 | -0.07782 | 0 | 0.027466 | -0.11444 | 0.036621 | 0.059509 | 0.073242 | -0.004578 | 122.4655 | 122.3282 | 0.01831 | 122.4197 | 122.4838 | 0.15564 | -0.050354 | 122.4792 | 122.4014 | -0.07782 | 122.406 | 122.2916 | -0.10986 | -0.054932 | 122.5388 | 122.4701 | 122.4426 | -0.19226 | 122.4426 | 122.4655 | 122.4335 | -0.11902
2008.1719 | 122.6166 | -122.3831 | 0.054932 | 0.0054168 | 0.028057 | 0.086034 | 0.026083 | -0.075945 | -0.026944 | 0.005488 | 0.014954 | 0.011662 | -0.027038 | -0.0095745 | -0.0065454 | 0.012454 | 0.12817 | 0.14648 | 0.16022 | 0.15106 | 0.059509 | 0.10071 | -0.027466 | 0.091553 | 0.14191 | 0.022888 | 0.013733 | 0.022888 | 0.11444 | 0.036621 | 122.4838 | 122.3557 | 0.004577 | 122.5296 | 122.5342 | 0.17853 | 0.073242 | 122.4976 | 122.4197 | -0.041199 | 122.4747 | 122.406 | -0.013733 | -0.032044 | 122.4426 | 122.5113 | 122.5433 | -0.082398 | 122.3969 | 122.406 | 122.525 | -0.018311
2009.9531 | 122.5708 | -122.3785 | 0.09613 | 0.013046 | 0.017162 | 0.082189 | 0.026511 | -0.070818 | -0.018399 | 0.0076242 | 0.0073242 | 0.015721 | -0.027466 | -0.0061567 | -0.0044092 | 0.010104 | 0.086975 | 0.082397 | 0.086975 | 0.13275 | 0.13733 | 0.059509 | -0.068665 | 0.054932 | 0.09613 | -0.064087 | 0.022888 | 0.064087 | 0.082397 | 0.009155 | 122.438 | 122.3099 | 0.041199 | 122.4609 | 122.5113 | 0.20142 | -0.009155 | 122.4609 | 122.3877 | -0.073242 | 122.4335 | 122.3145 | -0.073242 | -0.032043 | 122.5159 | 122.4655 | 122.4655 | -0.16479 | 122.4014 | 122.4426 | 122.4747 | -0.086975
2011.6719 | 122.6669 | -122.374 | 0.059509 | -0.0022127 | 0.022717 | 0.084112 | 0.022665 | -0.071886 | -0.025022 | 0.0069834 | 0.0073242 | 0.013798 | -0.028534 | -0.0085065 | -0.0046228 | 0.010532 | 0.059509 | 0.054932 | 0.073242 | 0.10529 | 0.11902 | 0.068665 | -0.050354 | 0.059509 | 0.10529 | -0.009155 | 0.013733 | 0.041199 | 0.10986 | 0.022888 | 122.4426 | 122.3236 | 0.05951 | 122.4289 | 122.4792 | 0.15564 | 0 | 122.4838 | 122.3969 | -0.045776 | 122.4335 | 122.3648 | -0.032043 | -0.01831 | 122.493 | 122.4335 | 122.4472 | -0.10986 | 122.3877 | 122.4152 | 122.4792 | -0.036621
2013.4688 | 122.5342 | -122.4197 | 0.11444 | -0.0022127 | 0.020794 | 0.088171 | 0.026083 | -0.072314 | -0.028012 | 0.0067696 | 0.0073242 | 0.013798 | -0.028534 | -0.0085065 | -0.0069726 | 0.010959 | 0.09613 | 0.13275 | 0.15106 | 0.16022 | 0.10529 | 0.09613 | -0.036621 | 0.064087 | 0.14191 | -0.013733 | 0.018311 | 0.004578 | 0.091553 | 0.009155 | 122.5159 | 122.3831 | -0.009155 | 122.5525 | 122.58 | 0.19684 | -0.018311 | 122.5113 | 122.4289 | -0.09613 | 122.4838 | 122.406 | -0.022888 | -0.10986 | 122.525 | 122.5159 | 122.5708 | -0.15106 | 122.4381 | 122.4243 | 122.5616 | -0.10529
2015.1875 | 122.6761 | -122.3694 | 0.059509 | 0.0054168 | 0.025494 | 0.085821 | 0.02886 | -0.073168 | -0.02908 | 0.0050608 | 0.014954 | 0.012516 | -0.027466 | -0.0093609 | -0.0099634 | 0.0116 | 0.050354 | 0.086975 | 0.11902 | 0.13275 | 0.10529 | 0.073242 | -0.041199 | 0.054932 | 0.14648 | 0.027466 | 0.013733 | 0.022888 | 0.091553 | 0.009155 | 122.4426 | 122.3282 | 0.045777 | 122.4564 | 122.5021 | 0.17395 | -0.009155 | 122.4609 | 122.3785 | -0.045776 | 122.4243 | 122.3969 | 0.018311 | -0.036621 | 122.4747 | 122.4197 | 122.4884 | -0.10071 | 122.3831 | 122.3923 | 122.5159 | -0.050354
2016.9531 | 122.5937 | -122.4197 | 0.10529 | 0.013046 | 0.01524 | 0.086462 | 0.029288 | -0.071459 | -0.020749 | 0.0050608 | 0.0073242 | 0.014012 | -0.027679 | -0.0067975 | -0.0052636 | 0.0073273 | 0.027466 | 0.004578 | 0.032043 | 0.10071 | 0.13733 | 0.045776 | -0.073242 | -0.004578 | 0.041199 | -0.07782 | 0.050354 | 0.054932 | 0.082397 | -0.004578 | 122.4655 | 122.3465 | 0.032043 | 122.4243 | 122.5204 | 0.17395 | -0.07782 | 122.5021 | 122.4152 | -0.054932 | 122.4152 | 122.3419 | -0.073242 | -0.050354 | 122.5571 | 122.4472 | 122.4518 | -0.17853 | 122.4701 | 122.4747 | 122.4609 | -0.10986
2018.7344 | 122.6761 | -122.374 | 0.068665 | -0.0022127 | 0.025921 | 0.084539 | 0.027152 | -0.072314 | -0.028653 | 0.0063424 | 0.0073242 | 0.010807 | -0.028747 | -0.011283 | -0.006759 | 0.012027 | 0.036621 | 0.09613 | 0.11902 | 0.13733 | 0.10071 | 0.086975 | -0.018311 | 0.041199 | 0.1236 | 0.004578 | 0.018311 | 0.013733 | 0.10986 | 0.009155 | 122.4609 | 122.3557 | 0.032043 | 122.4701 | 122.5113 | 0.15564 | -0.032044 | 122.4838 | 122.3831 | -0.050354 | 122.4152 | 122.3785 | -0.004577 | -0.054932 | 122.4747 | 122.4106 | 122.493 | -0.086976 | 122.3923 | 122.3877 | 122.4976 | -0.05951
2020.5156 | 122.612 | -122.374 | 0.086975 | 0.0054168 | 0.025494 | 0.086889 | 0.02587 | -0.072741 | -0.02609 | 0.003779 | -0.0003053 | 0.011021 | -0.028961 | -0.0093609 | -0.0076136 | 0.011386 | 0.10071 | 0.12817 | 0.15106 | 0.13733 | 0.07782 | 0.10071 | -0.045776 | 0.073242 | 0.14191 | 0.022888 | 0.004578 | 0.018311 | 0.10986 | 0.022888 | 122.4747 | 122.3282 | -0.009155 | 122.5021 | 122.5113 | 0.18311 | 0.013733 | 122.4838 | 122.3969 | -0.082397 | 122.4472 | 122.3969 | 0 | -0.068664 | 122.4518 | 122.4747 | 122.525 | -0.13275 | 122.3785 | 122.3923 | 122.5159 | -0.064087
2022.2344 | 122.6257 | -122.3923 | 0.07782 | 0.0054168 | 0.027844 | 0.089239 | 0.022665 | -0.072741 | -0.027371 | 0.0035654 | -0.0079343 | 0.014012 | -0.028534 | -0.0097883 | -0.0059046 | 0.013309 | 0.11902 | 0.16022 | 0.16022 | 0.15564 | 0.091553 | 0.09613 | -0.027466 | 0.09613 | 0.13275 | 0.018311 | 0.022888 | 0 | 0.10529 | 0.022888 | 122.4884 | 122.3648 | 0.013733 | 122.5525 | 122.5479 | 0.18311 | 0.041199 | 122.4976 | 122.4152 | -0.054932 | 122.4884 | 122.4106 | -0.004577 | -0.07782 | 122.4838 | 122.5113 | 122.5525 | -0.10529 | 122.4152 | 122.3923 | 122.525 | -0.054932
2024.0312 | 122.6761 | -122.3557 | 0.068665 | 0.020676 | 0.027203 | 0.087957 | 0.027152 | -0.073168 | -0.027799 | 0.003138 | 0.0073242 | 0.0097391 | -0.028961 | -0.0095745 | -0.0069726 | 0.0092499 | 0.068665 | 0.10071 | 0.13275 | 0.13733 | 0.09613 | 0.10071 | -0.032043 | 0.054932 | 0.13275 | 0.022888 | -0.013733 | 0.022888 | 0.09613 | 0.013733 | 122.4564 | 122.3236 | 0.027465 | 122.4564 | 122.493 | 0.16937 | 0 | 122.4518 | 122.3694 | -0.082398 | 122.4106 | 122.3785 | 0.009155 | -0.045777 | 122.4518 | 122.4243 | 122.4884 | -0.10071 | 122.3419 | 122.3785 | 122.4884 | -0.054932
2025.7344 | 122.6166 | -122.374 | 0.068665 | 0.013046 | 0.023358 | 0.090307 | 0.027579 | -0.06975 | -0.025235 | 0.003779 | 0.0073242 | 0.012089 | -0.030883 | -0.010429 | -0.00505 | 0.011386 | 0.086975 | 0.10986 | 0.12817 | 0.1236 | 0.091553 | 0.10529 | -0.022888 | 0.050354 | 0.086975 | 0.004578 | 0.009155 | 0.027466 | 0.10529 | 0.018311 | 122.4792 | 122.3511 | 0.022888 | 122.4838 | 122.4976 | 0.14648 | 0.01831 | 122.4792 | 122.3923 | -0.05951 | 122.4243 | 122.3785 | -0.013733 | -0.041199 | 122.4655 | 122.4609 | 122.5021 | -0.091553 | 122.3831 | 122.4014 | 122.4609 | -0.050354
2027.5156 | 122.58 | -122.4243 | 0.10529 | -0.0098417 | 0.016522 | 0.088812 | 0.027365 | -0.071459 | -0.020108 | 0.0057016 | 0.0073242 | 0.014866 | -0.029175 | -0.0070111 | -0.003982 | 0.010532 | 0.027466 | 0.018311 | 0.027466 | 0.10071 | 0.13733 | 0.050354 | -0.07782 | -0.004578 | 0.036621 | -0.10071 | 0.064087 | 0.036621 | 0.07782 | -0.004578 | 122.4747 | 122.3465 | 0.032043 | 122.4426 | 122.525 | 0.17853 | -0.07782 | 122.5021 | 122.4197 | -0.041199 | 122.4197 | 122.3236 | -0.09613 | -0.068665 | 122.5616 | 122.4518 | 122.4518 | -0.18311 | 122.4884 | 122.4609 | 122.4609 | -0.10986
2029.3281 | 122.6624 | -122.3648 | 0.059509 | 0.0054168 | 0.023358 | 0.085607 | 0.024802 | -0.071673 | -0.020322 | 0.0059152 | 0.014954 | 0.016148 | -0.028534 | -0.0059429 | -0.0048364 | 0.011386 | 0.059509 | 0.018311 | 0.068665 | 0.10071 | 0.11444 | 0.068665 | -0.050354 | 0.054932 | 0.082397 | -0.036621 | 0.022888 | 0.022888 | 0.10529 | 0.018311 | 122.4335 | 122.3145 | 0.054932 | 122.3831 | 122.4655 | 0.15106 | 0 | 122.4701 | 122.3831 | -0.036621 | 122.4197 | 122.3282 | -0.054932 | -0.036621 | 122.4792 | 122.4243 | 122.4335 | -0.10986 | 122.3877 | 122.3877 | 122.4472 | -0.041198
2031.0469 | 122.5296 | -122.4243 | 0.10529 | 0.0054168 | 0.015881 | 0.084325 | 0.025229 | -0.073809 | -0.019895 | 0.0069834 | 0.0073242 | 0.018925 | -0.029175 | -0.0063703 | -0.0031274 | 0.011173 | 0.064087 | 0.050354 | 0.068665 | 0.1236 | 0.1236 | 0.054932 | -0.054932 | 0.050354 | 0.050354 | -0.091553 | 0.018311 | 0.036621 | 0.07782 | -0.013733 | 122.4792 | 122.3694 | 0.01831 | 122.4747 | 122.5479 | 0.17853 | -0.041199 | 122.5021 | 122.4106 | -0.086975 | 122.4747 | 122.3328 | -0.07782 | -0.068665 | 122.5479 | 122.4884 | 122.493 | -0.16022 | 122.4426 | 122.4609 | 122.4747 | -0.11902
2032.8281 | 122.5433 | -122.4197 | 0.10529 | 0.013046 | 0.020153 | 0.088171 | 0.02886 | -0.06975 | -0.027371 | 0.0033518 | 0.014954 | 0.012516 | -0.028106 | -0.0074383 | -0.0097498 | 0.010104 | 0.073242 | 0.10986 | 0.13275 | 0.15106 | 0.10529 | 0.082397 | -0.054932 | 0.013733 | 0.091553 | -0.032043 | 0.018311 | 0.045776 | 0.07782 | -0.013733 | 122.5021 | 122.3648 | 0 | 122.5296 | 122.5708 | 0.20599 | -0.032044 | 122.4976 | 122.406 | -0.086975 | 122.4335 | 122.3877 | -0.01831 | -0.05951 | 122.525 | 122.493 | 122.5525 | -0.16022 | 122.4381 | 122.4655 | 122.5113 | -0.11902
2034.5938 | 122.5433 | -122.4335 | 0.09613 | -0.0022127 | 0.01759 | 0.084966 | 0.029288 | -0.074023 | -0.020535 | 0.0061288 | 0.0073242 | 0.016361 | -0.028534 | -0.0076519 | -0.0061182 | 0.0090363 | 0.082397 | 0.059509 | 0.07782 | 0.1236 | 0.10986 | 0.073242 | -0.050354 | 0.027466 | 0.073242 | -0.073242 | 0.045776 | 0.045776 | 0.073242 | -0.004578 | 122.5067 | 122.3831 | 0.013733 | 122.493 | 122.5571 | 0.17395 | -0.013733 | 122.5067 | 122.4289 | -0.050354 | 122.4609 | 122.3602 | -0.068664 | -0.050354 | 122.5433 | 122.5159 | 122.5113 | -0.14648 | 122.4792 | 122.4792 | 122.5067 | -0.10071
2036.3125 | 122.5433 | -122.438 | 0.1236 | 0.0054168 | 0.016308 | 0.084325 | 0.027579 | -0.071245 | -0.023313 | 0.007197 | 0.014954 | 0.016361 | -0.027466 | -0.0063703 | -0.0046228 | 0.0092499 | 0.059509 | 0.091553 | 0.064087 | 0.11444 | 0.1236 | 0.073242 | -0.045776 | 0.036621 | 0.073242 | -0.068665 | 0.022888 | 0.050354 | 0.07782 | 0.004578 | 122.5113 | 122.3923 | 0 | 122.5296 | 122.5525 | 0.16022 | -0.064087 | 122.5159 | 122.4426 | -0.10071 | 122.4747 | 122.3694 | -0.073243 | -0.073242 | 122.5616 | 122.4976 | 122.5021 | -0.16937 | 122.4609 | 122.4884 | 122.5113 | -0.11902
2038.0938 | 122.612 | -122.3969 | 0.091553 | -0.0022127 | 0.028057 | 0.085607 | 0.028006 | -0.06975 | -0.029294 | 0.0061288 | 0.0073242 | 0.011021 | -0.026825 | -0.0078657 | -0.0078272 | 0.012454 | 0.07782 | 0.14191 | 0.17395 | 0.14648 | 0.086975 | 0.091553 | -0.018311 | 0.086975 | 0.13733 | 0.022888 | 0.013733 | 0.018311 | 0.10986 | 0.032043 | 122.4884 | 122.3785 | -0.004578 | 122.5388 | 122.5433 | 0.16479 | -0.013733 | 122.5067 | 122.4289 | -0.07782 | 122.4838 | 122.4197 | -0.009155 | -0.073242 | 122.4838 | 122.4747 | 122.5708 | -0.10986 | 122.4106 | 122.4152 | 122.5342 | -0.05951
2039.8125 | 122.5525 | -122.4335 | 0.1236 | 0.0054168 | 0.017376 | 0.088812 | 0.032278 | -0.072314 | -0.026731 | 0.0044198 | 0.014954 | 0.012516 | -0.02597 | -0.0082929 | -0.0080408 | 0.011813 | 0 | 0.009155 | 0.059509 | 0.091553 | 0.11902 | 0.054932 | -0.073242 | -0.022888 | 0.050354 | -0.073242 | 0.050354 | 0.064087 | 0.064087 | -0.009155 | 122.4884 | 122.3602 | -0.004577 | 122.4426 | 122.525 | 0.16479 | -0.1236 | 122.4976 | 122.4243 | -0.073242 | 122.4106 | 122.3602 | -0.064087 | -0.059509 | 122.5525 | 122.4335 | 122.493 | -0.19684 | 122.4838 | 122.4976 | 122.4838 | -0.13275
2041.6094 | 122.5525 | -122.4289 | 0.082397 | 0.0054168 | 0.016094 | 0.086248 | 0.026511 | -0.072314 | -0.022458 | 0.0057016 | 0.014954 | 0.017002 | -0.029388 | -0.0067975 | -0.003341 | 0.0090363 | 0.086975 | 0.059509 | 0.082397 | 0.14191 | 0.10071 | 0.059509 | -0.041199 | 0.059509 | 0.091553 | -0.045776 | 0.018311 | 0.054932 | 0.091553 | -0.004578 | 122.4884 | 122.3877 | 0.018311 | 122.4884 | 122.5708 | 0.18311 | 0.004578 | 122.5204 | 122.4243 | -0.064086 | 122.4884 | 122.3831 | -0.041198 | -0.027465 | 122.5296 | 122.5159 | 122.5113 | -0.1236 | 122.4472 | 122.4838 | 122.5204 | -0.086975
2043.3438 | 122.5342 | -122.4243 | 0.11444 | 0.013046 | 0.01994 | 0.087316 | 0.02587 | -0.070605 | -0.023313 | 0.0057016 | 0.0073242 | 0.015721 | -0.027038 | -0.0074383 | -0.0044092 | 0.012027 | 0.018311 | 0.045776 | 0.036621 | 0.09613 | 0.10986 | 0.054932 | -0.041199 | -0.009155 | 0.013733 | -0.10986 | 0.041199 | 0.050354 | 0.059509 | -0.004578 | 122.4792 | 122.3831 | -0.004578 | 122.4701 | 122.5204 | 0.13733 | -0.09613 | 122.4838 | 122.4197 | -0.073242 | 122.4152 | 122.3145 | -0.10529 | -0.064087 | 122.5342 | 122.4426 | 122.4609 | -0.15564 | 122.4655 | 122.4747 | 122.438 | -0.11902
2045.1406 | 122.5937 | -122.4289 | 0.091553 | 0.020676 | 0.015667 | 0.087957 | 0.025656 | -0.071886 | -0.025235 | 0.0069834 | -0.0003053 | 0.014866 | -0.02597 | -0.0070111 | -0.0063318 | 0.010532 | 0.027466 | 0.045776 | 0.068665 | 0.1236 | 0.11902 | 0.050354 | -0.059509 | 0.018311 | 0.091553 | -0.050354 | 0.032043 | 0.054932 | 0.082397 | 0.022888 | 122.4792 | 122.3694 | 0.027466 | 122.4747 | 122.5525 | 0.1831 | -0.064087 | 122.5113 | 122.4518 | -0.05951 | 122.4472 | 122.3785 | -0.073242 | -0.036621 | 122.5479 | 122.4564 | 122.4976 | -0.15106 | 122.4609 | 122.4838 | 122.5204 | -0.068665
2046.9219 | 122.6807 | -122.3602 | 0.073242 | 0.0054168 | 0.026348 | 0.089666 | 0.023306 | -0.074877 | -0.029721 | 0.0029244 | 0.014954 | 0.011021 | -0.03067 | -0.0093609 | -0.0091088 | 0.012882 | 0.027466 | 0.086975 | 0.11444 | 0.1236 | 0.10986 | 0.091553 | -0.041199 | 0.018311 | 0.1236 | 0.009155 | 0.009155 | 0.036621 | 0.10071 | 0.004578 | 122.4518 | 122.319 | 0.036621 | 122.4472 | 122.4838 | 0.16479 | -0.045776 | 122.4609 | 122.3648 | -0.064087 | 122.3785 | 122.3694 | 0.004577 | -0.036621 | 122.4701 | 122.3877 | 122.4747 | -0.11444 | 122.3694 | 122.3969 | 122.4838 | -0.068664
2048.6875 | 122.6761 | -122.3694 | 0.064087 | 0.013046 | 0.024853 | 0.088384 | 0.026724 | -0.07445 | -0.028653 | 0.003779 | 0.022583 | 0.011021 | -0.028961 | -0.0082929 | -0.0095362 | 0.0116 | 0.036621 | 0.082397 | 0.12817 | 0.12817 | 0.10529 | 0.10071 | -0.045776 | 0.009155 | 0.10071 | 0.013733 | 0.018311 | 0.036621 | 0.09613 | 0.022888 | 122.4701 | 122.3236 | 0.041199 | 122.4518 | 122.4976 | 0.17395 | -0.027466 | 122.4655 | 122.3923 | -0.045776 | 122.3785 | 122.3831 | -0.009155 | -0.027466 | 122.4747 | 122.406 | 122.4976 | -0.10986 | 122.3877 | 122.406 | 122.4701 | -0.041199
2050.4844 | 122.6486 | -122.4106 | 0.073242 | 0.013046 | 0.026562 | 0.088598 | 0.027365 | -0.072314 | -0.028653 | 0.0050608 | 0.0073242 | 0.012089 | -0.027252 | -0.0095745 | -0.0069726 | 0.010532 | 0.054932 | 0.07782 | 0.11444 | 0.1236 | 0.073242 | 0.09613 | -0.041199 | 0.032043 | 0.10071 | -0.009155 | 0.004578 | 0.027466 | 0.10071 | 0.032043 | 122.5067 | 122.3694 | 0 | 122.4884 | 122.5342 | 0.16479 | -0.01831 | 122.5113 | 122.4426 | -0.068664 | 122.4426 | 122.4014 | -0.041198 | -0.045776 | 122.4838 | 122.4655 | 122.525 | -0.11444 | 122.4152 | 122.438 | 122.5113 | -0.041199
2052.2031 | 122.5296 | -122.4426 | 0.10529 | -0.0022127 | 0.016094 | 0.086034 | 0.024588 | -0.073168 | -0.020749 | 0.0052744 | 0.014954 | 0.016575 | -0.027252 | -0.0061567 | -0.0020594 | 0.0081817 | 0.032043 | 0.004578 | 0.032043 | 0.091553 | 0.13733 | 0.068665 | -0.054932 | -0.013733 | 0 | -0.12817 | 0.036621 | 0.045776 | 0.073242 | -0.004578 | 122.5113 | 122.3877 | 0.032043 | 122.4472 | 122.5342 | 0.14649 | -0.073243 | 122.5159 | 122.438 | -0.068665 | 122.4289 | 122.3145 | -0.1236 | -0.05951 | 122.58 | 122.4747 | 122.4747 | -0.16022 | 122.4792 | 122.4884 | 122.4426 | -0.10986
2053.9844 | 122.5983 | -122.4106 | 0.10529 | 0.0054168 | 0.017162 | 0.085394 | 0.029715 | -0.069323 | -0.020322 | 0.0050608 | 0.0073242 | 0.014439 | -0.025757 | -0.0078657 | -0.0054772 | 0.0088227 | 0.041199 | 0.027466 | 0.068665 | 0.10986 | 0.11902 | 0.068665 | -0.059509 | 0.032043 | 0.082397 | -0.064087 | 0.036621 | 0.059509 | 0.07782 | -0.018311 | 122.4792 | 122.3511 | 0.013733 | 122.438 | 122.5204 | 0.16937 | -0.064087 | 122.4884 | 122.3923 | -0.068665 | 122.4426 | 122.3465 | -0.045776 | -0.045777 | 122.5296 | 122.4518 | 122.4792 | -0.16479 | 122.4472 | 122.4701 | 122.493 | -0.1236
2055.7344 | 122.6486 | -122.3831 | 0.086975 | 0.0054168 | 0.027203 | 0.086889 | 0.02352 | -0.072527 | -0.026731 | 0.0052744 | 0.0073242 | 0.012516 | -0.029175 | -0.0076519 | -0.00505 | 0.0096771 | 0.10986 | 0.15106 | 0.16022 | 0.16937 | 0.068665 | 0.10071 | -0.022888 | 0.091553 | 0.15564 | 0.032043 | 0 | 0.027466 | 0.10986 | 0.036621 | 122.4838 | 122.3602 | -0.01831 | 122.5342 | 122.5525 | 0.19226 | 0.022888 | 122.493 | 122.4197 | -0.086975 | 122.4747 | 122.4152 | -0.004578 | -0.059509 | 122.4518 | 122.493 | 122.5433 | -0.10986 | 122.3831 | 122.4106 | 122.5388 | -0.050354
2057.4531 | 122.58 | -122.4289 | 0.11444 | -0.0098417 | 0.020794 | 0.086248 | 0.025229 | -0.072741 | -0.022031 | 0.0063424 | 0.014954 | 0.016575 | -0.028961 | -0.0061567 | -0.003341 | 0.0088227 | 0.009155 | 0.004578 | 0.022888 | 0.07782 | 0.1236 | 0.068665 | -0.064087 | -0.018311 | -0.009155 | -0.10529 | 0.041199 | 0.054932 | 0.059509 | 0.004578 | 122.4976 | 122.3648 | 0.009155 | 122.4335 | 122.5067 | 0.14191 | -0.10529 | 122.4884 | 122.4335 | -0.073242 | 122.4106 | 122.3236 | -0.10986 | -0.059509 | 122.5525 | 122.438 | 122.4518 | -0.17853 | 122.4701 | 122.4838 | 122.4197 | -0.10986
2059.25 | 122.5708 | -122.4335 | 0.10986 | -0.0022127 | 0.017162 | 0.087957 | 0.029501 | -0.074023 | -0.026303 | 0.0044198 | 0.030213 | 0.013157 | -0.024688 | -0.0065839 | -0.0078272 | 0.010318 | 0.004578 | 0.027466 | 0.050354 | 0.073242 | 0.13733 | 0.050354 | -0.082397 | -0.041199 | 0.041199 | -0.082397 | 0.054932 | 0.054932 | 0.054932 | -0.032043 | 122.4838 | 122.3511 | 0.027466 | 122.4609 | 122.5067 | 0.15564 | -0.10529 | 122.4884 | 122.4014 | -0.054931 | 122.3923 | 122.3511 | -0.050354 | -0.054931 | 122.5708 | 122.438 | 122.4838 | -0.19226 | 122.4884 | 122.4884 | 122.4747 | -0.14191
2061.0312 | 122.5525 | -122.4518 | 0.10529 | -0.0022127 | 0.021008 | 0.08753 | 0.029715 | -0.073168 | -0.025449 | 0.0044198 | 0.014954 | 0.013157 | -0.028534 | -0.0072247 | -0.0093226 | 0.0090363 | 0.073242 | 0.082397 | 0.11902 | 0.14648 | 0.09613 | 0.082397 | -0.041199 | -0.009155 | 0.073242 | -0.059509 | 0.027466 | 0.050354 | 0.082397 | -0.009155 | 122.5342 | 122.4106 | -0.009156 | 122.5342 | 122.5983 | 0.18768 | -0.032044 | 122.5342 | 122.4426 | -0.07782 | 122.4426 | 122.3923 | -0.050354 | -0.054932 | 122.5479 | 122.525 | 122.5708 | -0.14649 | 122.4792 | 122.5021 | 122.525 | -0.11444
2062.7344 | 122.699 | -122.4014 | 0.064087 | 0.013046 | 0.027203 | 0.086889 | 0.029929 | -0.073168 | -0.028653 | 0.0035654 | 0.014954 | 0.011662 | -0.028106 | -0.0061567 | -0.0091088 | 0.0090363 | 0.07782 | 0.1236 | 0.14191 | 0.14191 | 0.10986 | 0.09613 | -0.027466 | 0.073242 | 0.16479 | 0.041199 | 0.022888 | 0.027466 | 0.11444 | 0.036621 | 122.4976 | 122.374 | 0.045776 | 122.525 | 122.5433 | 0.16937 | 0.013733 | 122.5159 | 122.438 | -0.041199 | 122.4747 | 122.4426 | 0.004578 | -0.036621 | 122.5113 | 122.4792 | 122.5433 | -0.091553 | 122.4243 | 122.4289 | 122.5662 | -0.027466
2064.5469 | 122.6395 | -122.3969 | 0.064087 | 0.0054168 | 0.027203 | 0.087743 | 0.02587 | -0.071886 | -0.027158 | 0.0050608 | 0.0073242 | 0.011235 | -0.027893 | -0.0063703 | -0.0046228 | 0.0090363 | 0.12817 | 0.14191 | 0.16479 | 0.16937 | 0.064087 | 0.10071 | -0.009155 | 0.091553 | 0.14191 | 0.027466 | 0.013733 | 0.013733 | 0.10529 | 0.018311 | 122.4976 | 122.3877 | 0 | 122.5388 | 122.5662 | 0.17853 | 0.064087 | 122.5021 | 122.4152 | -0.050354 | 122.4884 | 122.4243 | 0.009155 | -0.050354 | 122.4609 | 122.525 | 122.5616 | -0.073242 | 122.4106 | 122.4106 | 122.5388 | -0.045776
2066.2812 | 122.6166 | -122.3923 | 0.082397 | 0.020676 | 0.025921 | 0.088812 | 0.025656 | -0.074023 | -0.026517 | 0.003779 | 0.014954 | 0.011875 | -0.028961 | -0.0097883 | -0.0071862 | 0.0096771 | 0.086975 | 0.09613 | 0.1236 | 0.12817 | 0.086975 | 0.091553 | -0.032043 | 0.032043 | 0.10529 | -0.009155 | 0.027466 | 0.018311 | 0.11902 | 0.013733 | 122.4838 | 122.3602 | 0.004578 | 122.4884 | 122.5204 | 0.16022 | 0.004578 | 122.5113 | 122.406 | -0.054931 | 122.4243 | 122.3831 | -0.022888 | -0.064086 | 122.4792 | 122.4792 | 122.5159 | -0.11444 | 122.4197 | 122.4106 | 122.4976 | -0.068664
2068.0781 | 122.6166 | -122.4426 | 0.10986 | 0.0054168 | 0.018017 | 0.08518 | 0.029929 | -0.071245 | -0.021176 | 0.0050608 | 0.0073242 | 0.015934 | -0.024688 | -0.0057293 | -0.0035546 | 0.0081817 | 0.064087 | 0.054932 | 0.068665 | 0.11902 | 0.11902 | 0.064087 | -0.064087 | 0.045776 | 0.07782 | -0.054932 | 0.036621 | 0.050354 | 0.064087 | 0 | 122.5067 | 122.3785 | 0.009156 | 122.4976 | 122.5616 | 0.18311 | -0.045776 | 122.5067 | 122.4426 | -0.073242 | 122.4884 | 122.3877 | -0.054932 | -0.059509 | 122.5616 | 122.5067 | 122.5113 | -0.17395 | 122.4792 | 122.493 | 122.5204 | -0.10986
2069.7812 | 122.5891 | -122.4106 | 0.091553 | 0.013046 | 0.015881 | 0.085821 | 0.026938 | -0.071673 | -0.023526 | 0.0057016 | 0.014954 | 0.015934 | -0.027466 | -0.0070111 | -0.005691 | 0.0056183 | 0.073242 | 0.068665 | 0.064087 | 0.10529 | 0.1236 | 0.041199 | -0.068665 | 0.059509 | 0.10071 | -0.041199 | 0.032043 | 0.064087 | 0.086975 | 0.004578 | 122.4518 | 122.3419 | 0.032043 | 122.4792 | 122.5159 | 0.17395 | -0.018311 | 122.4976 | 122.4152 | -0.05951 | 122.4701 | 122.3694 | -0.045777 | -0.027466 | 122.5342 | 122.4838 | 122.4747 | -0.16022 | 122.4426 | 122.4747 | 122.5113 | -0.086975
2071.5781 | 122.6624 | -122.4106 | 0.068665 | 0.013046 | 0.02998 | 0.089025 | 0.025443 | -0.074877 | -0.027158 | 0.0050608 | -0.0003053 | 0.0099527 | -0.027893 | -0.0080793 | -0.0076136 | 0.010959 | 0.10986 | 0.13733 | 0.16479 | 0.16479 | 0.07782 | 0.091553 | -0.032043 | 0.091553 | 0.13733 | 0.036621 | -0.004578 | 0.018311 | 0.10071 | 0.032043 | 122.5021 | 122.3785 | 0.009155 | 122.5479 | 122.5754 | 0.19684 | 0.041198 | 122.5113 | 122.4426 | -0.073243 | 122.5021 | 122.4472 | 0.004578 | -0.050354 | 122.4884 | 122.5204 | 122.5754 | -0.10071 | 122.406 | 122.4289 | 122.5479 | -0.036622
2073.3594 | 122.6898 | -122.374 | 0.07782 | 0.020676 | 0.021862 | 0.086034 | 0.026083 | -0.074236 | -0.02139 | 0.005488 | 0.014954 | 0.015934 | -0.02597 | -0.0070111 | -0.0029138 | 0.0096771 | 0.036621 | 0.009155 | 0.032043 | 0.09613 | 0.1236 | 0.059509 | -0.073242 | 0.032043 | 0.032043 | -0.082397 | 0.032043 | 0.045776 | 0.07782 | 0.004578 | 122.4335 | 122.3007 | 0.045776 | 122.3831 | 122.4701 | 0.16937 | -0.041199 | 122.4518 | 122.3785 | -0.045777 | 122.406 | 122.2916 | -0.086975 | -0.032044 | 122.4976 | 122.4106 | 122.406 | -0.15106 | 122.406 | 122.4197 | 122.406 | -0.073242
2075.0781 | 122.5616 | -122.4289 | 0.09613 | 0.020676 | 0.019726 | 0.088384 | 0.02886 | -0.073382 | -0.021817 | 0.0052744 | 0.014954 | 0.016575 | -0.027466 | -0.0067975 | -0.0027002 | 0.010104 | 0.009155 | -0.004578 | 0.022888 | 0.082397 | 0.1236 | 0.059509 | -0.064087 | -0.013733 | 0.022888 | -0.12817 | 0.050354 | 0.050354 | 0.07782 | 0.009155 | 122.4884 | 122.3648 | 0.027466 | 122.4243 | 122.5113 | 0.14648 | -0.086975 | 122.5067 | 122.438 | -0.045776 | 122.4152 | 122.3007 | -0.13733 | -0.045776 | 122.5525 | 122.438 | 122.4518 | -0.16022 | 122.4792 | 122.4792 | 122.4518 | -0.086975
2076.8594 | 122.5754 | -122.4335 | 0.11444 | 0.013046 | 0.021649 | 0.086675 | 0.029501 | -0.068896 | -0.027585 | 0.0039926 | -0.0003053 | 0.012516 | -0.02597 | -0.0093609 | -0.0078272 | 0.010318 | 0.068665 | 0.1236 | 0.13275 | 0.15106 | 0.10529 | 0.09613 | -0.050354 | 0.018311 | 0.10529 | -0.036621 | 0.027466 | 0.050354 | 0.07782 | -0.004578 | 122.5296 | 122.3831 | -0.009155 | 122.5571 | 122.5845 | 0.20142 | -0.045776 | 122.5113 | 122.4289 | -0.086975 | 122.4518 | 122.3969 | -0.032043 | -0.064087 | 122.5388 | 122.5021 | 122.5662 | -0.16479 | 122.4609 | 122.4838 | 122.5388 | -0.11902
2078.6406 | 122.612 | -122.4289 | 0.10986 | 0.0054168 | 0.018444 | 0.089025 | 0.029929 | -0.067614 | -0.022244 | 0.0042062 | -0.015564 | 0.015293 | -0.026184 | -0.0082929 | -0.0059046 | 0.010104 | 0.004578 | 0.009155 | 0.032043 | 0.086975 | 0.11902 | 0.045776 | -0.086975 | -0.022888 | 0.054932 | -0.086975 | 0.036621 | 0.041199 | 0.054932 | -0.004578 | 122.4747 | 122.3419 | 0.009156 | 122.438 | 122.5159 | 0.17395 | -0.10529 | 122.4838 | 122.4243 | -0.073242 | 122.406 | 122.3419 | -0.082397 | -0.068664 | 122.5479 | 122.4335 | 122.4609 | -0.19684 | 122.4655 | 122.4701 | 122.4838 | -0.11444
2080.375 | 122.5754 | -122.4564 | 0.10071 | 0.0054168 | 0.020153 | 0.088598 | 0.029715 | -0.071245 | -0.025876 | 0.005488 | 0.014954 | 0.014652 | -0.026397 | -0.0087201 | -0.0037684 | 0.0116 | 0.004578 | 0.013733 | 0.041199 | 0.07782 | 0.11444 | 0.050354 | -0.091553 | -0.036621 | 0.045776 | -0.086975 | 0.022888 | 0.082397 | 0.07782 | -0.004578 | 122.5067 | 122.3648 | 0.013733 | 122.4701 | 122.5342 | 0.16937 | -0.09613 | 122.5342 | 122.4518 | -0.07782 | 122.4197 | 122.3694 | -0.082397 | -0.018311 | 122.5708 | 122.4609 | 122.4976 | -0.19226 | 122.4792 | 122.5388 | 122.5021 | -0.10529
2082.1562 | 122.6715 | -122.4106 | 0.064087 | 0.013046 | 0.026135 | 0.086248 | 0.023947 | -0.071886 | -0.023526 | 0.004847 | -0.0003053 | 0.011448 | -0.028106 | -0.010215 | -0.0018458 | 0.0092499 | 0.11444 | 0.14191 | 0.15564 | 0.17395 | 0.091553 | 0.10986 | -0.013733 | 0.10529 | 0.16479 | 0.027466 | -0.018311 | 0.013733 | 0.12817 | 0.045776 | 122.5204 | 122.3969 | 0.027466 | 122.5525 | 122.5845 | 0.18768 | 0.050354 | 122.5388 | 122.4564 | -0.082398 | 122.5159 | 122.438 | -0.01831 | -0.050354 | 122.5021 | 122.525 | 122.5662 | -0.07782 | 122.3923 | 122.4243 | 122.5754 | -0.018311
2083.9531 | 122.6028 | -122.4243 | 0.086975 | -0.0022127 | 0.021435 | 0.086462 | 0.026511 | -0.073168 | -0.022244 | 0.006556 | 0.0073242 | 0.015721 | -0.027252 | -0.0063703 | -0.0059046 | 0.0098907 | 0.013733 | -0.022888 | 0.018311 | 0.082397 | 0.1236 | 0.064087 | -0.068665 | -0.027466 | -0.009155 | -0.09613 | 0.045776 | 0.059509 | 0.073242 | -0.018311 | 122.4884 | 122.3557 | 0.036621 | 122.4014 | 122.5067 | 0.15106 | -0.073242 | 122.4976 | 122.406 | -0.041199 | 122.3969 | 122.3282 | -0.077819 | -0.027466 | 122.5479 | 122.438 | 122.4426 | -0.15564 | 122.4701 | 122.4838 | 122.4152 | -0.10529
2085.6562 | 122.6212 | -122.4197 | 0.086975 | -0.0022127 | 0.022076 | 0.08518 | 0.025656 | -0.072314 | -0.020535 | 0.0069834 | 0.014954 | 0.015934 | -0.030029 | -0.0080793 | -0.0037684 | 0.011386 | 0.004578 | -0.004578 | 0.032043 | 0.082397 | 0.12817 | 0.073242 | -0.068665 | -0.018311 | 0.004578 | -0.09613 | 0.050354 | 0.064087 | 0.073242 | -0.009155 | 122.493 | 122.3511 | 0.041199 | 122.4152 | 122.5021 | 0.15106 | -0.082397 | 122.493 | 122.4106 | -0.036621 | 122.4014 | 122.3236 | -0.086975 | -0.022888 | 122.5479 | 122.4243 | 122.4518 | -0.15564 | 122.4701 | 122.4838 | 122.4243 | -0.09613
2087.4375 | 122.5479 | -122.438 | 0.091553 | 0.0054168 | 0.015667 | 0.086462 | 0.025015 | -0.072954 | -0.020963 | 0.0063424 | 0.0073242 | 0.017216 | -0.026184 | -0.0055157 | -0.0037684 | 0.010959 | 0.054932 | 0.054932 | 0.059509 | 0.11444 | 0.11902 | 0.082397 | -0.073242 | 0.004578 | 0.054932 | -0.091553 | 0.027466 | 0.064087 | 0.086975 | 0 | 122.5204 | 122.3648 | 0.027466 | 122.493 | 122.5525 | 0.18768 | -0.036621 | 122.525 | 122.438 | -0.064087 | 122.4426 | 122.3465 | -0.091553 | -0.027466 | 122.5571 | 122.493 | 122.4976 | -0.16479 | 122.4655 | 122.5021 | 122.493 | -0.091553
2089.1719 | 122.6852 | -122.4152 | 0.07782 | 0.0054168 | 0.02998 | 0.089452 | 0.030569 | -0.073168 | -0.03143 | 0.0059152 | -0.0003053 | 0.0099527 | -0.02597 | -0.010002 | -0.010818 | 0.011386 | 0.036621 | 0.082397 | 0.12817 | 0.13275 | 0.10071 | 0.082397 | -0.045776 | 0.027466 | 0.13275 | 0.027466 | -0.009155 | 0.027466 | 0.10071 | 0.036621 | 122.4976 | 122.3694 | 0.022888 | 122.4976 | 122.5479 | 0.17853 | -0.041199 | 122.5159 | 122.4518 | -0.086975 | 122.4426 | 122.4426 | -0.009155 | -0.050354 | 122.5159 | 122.4518 | 122.5433 | -0.1236 | 122.406 | 122.4426 | 122.5479 | -0.041199
2090.9531 | 122.58 | -122.4243 | 0.09613 | -0.0022127 | 0.018444 | 0.08518 | 0.027365 | -0.07445 | -0.020108 | 0.0046334 | 0.014954 | 0.015721 | -0.027252 | -0.0061567 | -0.0054772 | 0.0081817 | 0.073242 | 0.064087 | 0.082397 | 0.12817 | 0.10986 | 0.064087 | -0.064087 | 0.045776 | 0.091553 | -0.032043 | 0.045776 | 0.041199 | 0.054932 | 0 | 122.4884 | 122.3602 | 0.013733 | 122.4884 | 122.5525 | 0.19226 | -0.022888 | 122.4792 | 122.4243 | -0.050354 | 122.4701 | 122.3923 | -0.032043 | -0.054931 | 122.5342 | 122.4976 | 122.5067 | -0.16022 | 122.4701 | 122.4655 | 122.5159 | -0.09613
2092.7344 | 122.6166 | -122.4335 | 0.091553 | 0.013046 | 0.017803 | 0.087316 | 0.027152 | -0.071886 | -0.022885 | 0.005488 | -0.0003053 | 0.016789 | -0.02832 | -0.0076519 | -0.0029138 | 0.010959 | 0.082397 | 0.064087 | 0.09613 | 0.1236 | 0.13275 | 0.054932 | -0.073242 | 0.036621 | 0.09613 | -0.032043 | 0.036621 | 0.050354 | 0.07782 | 0.013733 | 122.4884 | 122.3602 | 0.041198 | 122.4976 | 122.5571 | 0.19684 | -0.009156 | 122.5113 | 122.4472 | -0.054932 | 122.4701 | 122.4014 | -0.045776 | -0.041199 | 122.5662 | 122.5159 | 122.5296 | -0.16479 | 122.4701 | 122.4838 | 122.5296 | -0.07782
2094.5312 | 122.6532 | -122.438 | 0.082397 | 0.020676 | 0.027203 | 0.08753 | 0.024374 | -0.071673 | -0.027585 | 0.0039926 | 0.0073242 | 0.010807 | -0.028534 | -0.0087201 | -0.0088952 | 0.011813 | 0.045776 | 0.086975 | 0.12817 | 0.12817 | 0.086975 | 0.09613 | -0.050354 | 0.027466 | 0.10071 | -0.013733 | 0.018311 | 0.022888 | 0.10529 | 0.036621 | 122.5342 | 122.3877 | 0.004578 | 122.525 | 122.5662 | 0.17853 | -0.036621 | 122.5433 | 122.4747 | -0.064086 | 122.4655 | 122.4243 | -0.050354 | -0.059509 | 122.525 | 122.4838 | 122.5662 | -0.13275 | 122.4564 | 122.4609 | 122.5388 | -0.045776
2096.25 | 122.7036 | -122.3969 | 0.07782 | 0.0054168 | 0.028698 | 0.086675 | 0.030997 | -0.073168 | -0.028653 | 0.0039926 | 0.014954 | 0.01273 | -0.028534 | -0.0072247 | -0.010604 | 0.0092499 | 0.10071 | 0.14191 | 0.1831 | 0.16937 | 0.086975 | 0.091553 | -0.022888 | 0.086975 | 0.18768 | 0.064087 | 0 | 0.027466 | 0.11902 | 0.027466 | 122.4884 | 122.374 | 0.009155 | 122.5388 | 122.5662 | 0.19226 | 0.022888 | 122.5159 | 122.4243 | -0.07782 | 122.4838 | 122.4609 | 0.036621 | -0.050354 | 122.4838 | 122.4976 | 122.58 | -0.10071 | 122.3969 | 122.4243 | 122.5845 | -0.050354
2098.0312 | 122.699 | -122.3969 | 0.064087 | 0.020676 | 0.024639 | 0.086675 | 0.027152 | -0.0721 | -0.022672 | 0.006556 | 0.014954 | 0.015293 | -0.026184 | -0.0080793 | -0.003341 | 0.0079681 | 0.059509 | 0.022888 | 0.068665 | 0.086975 | 0.12817 | 0.091553 | -0.032043 | 0.045776 | 0.068665 | -0.032043 | 0.004578 | 0.036621 | 0.091553 | 0.036621 | 122.4884 | 122.3648 | 0.064087 | 122.4197 | 122.4838 | 0.11902 | -0.004578 | 122.4884 | 122.4335 | -0.059509 | 122.4426 | 122.3648 | -0.068664 | -0.027466 | 122.525 | 122.4564 | 122.4655 | -0.09613 | 122.4014 | 122.4335 | 122.4655 | -0.027466
2099.7344 | 122.6349 | -122.406 | 0.082397 | 0.013046 | 0.026989 | 0.088384 | 0.029288 | -0.071245 | -0.027799 | 0.004847 | 0.0073242 | 0.010807 | -0.02597 | -0.010643 | -0.0076136 | 0.010318 | 0.10986 | 0.17395 | 0.1831 | 0.16937 | 0.07782 | 0.07782 | -0.032043 | 0.091553 | 0.18768 | 0.041199 | 0.013733 | 0.032043 | 0.11444 | 0.036621 | 122.4838 | 122.374 | -0.004577 | 122.58 | 122.5754 | 0.20142 | 0.027466 | 122.5204 | 122.4426 | -0.068664 | 122.4976 | 122.4472 | 0.004578 | -0.050354 | 122.4838 | 122.5159 | 122.5891 | -0.11444 | 122.4197 | 122.438 | 122.5937 | -0.045776
2101.5312 | 122.6807 | -122.4014 | 0.064087 | 0.0054168 | 0.024853 | 0.086889 | 0.023947 | -0.073809 | -0.021176 | 0.0042062 | 0.014954 | 0.01273 | -0.030029 | -0.0095745 | -0.0027002 | 0.0086091 | 0.09613 | 0.10986 | 0.13275 | 0.15564 | 0.10529 | 0.086975 | -0.032043 | 0.09613 | 0.13733 | 0.004578 | -0.009155 | 0.009155 | 0.11444 | 0.050354 | 122.4884 | 122.3694 | 0.041199 | 122.5113 | 122.5571 | 0.18768 | 0.032043 | 122.5159 | 122.4518 | -0.073242 | 122.4976 | 122.406 | -0.045776 | -0.054932 | 122.5067 | 122.4976 | 122.5342 | -0.09613 | 122.3923 | 122.4106 | 122.5388 | -0.013733
2103.3125 | 122.699 | -122.4197 | 0.068665 | 0.013046 | 0.02998 | 0.091375 | 0.027579 | -0.072954 | -0.028867 | 0.0052744 | 0.014954 | 0.011875 | -0.029175 | -0.010429 | -0.006759 | 0.010318 | 0.050354 | 0.07782 | 0.11444 | 0.1236 | 0.10071 | 0.10986 | -0.041199 | 0.045776 | 0.10529 | 0.004578 | 0.013733 | 0.027466 | 0.091553 | 0.036621 | 122.5296 | 122.3785 | 0.032043 | 122.4976 | 122.5433 | 0.16479 | -0.018311 | 122.5113 | 122.4564 | -0.054932 | 122.4655 | 122.4243 | -0.032043 | -0.041199 | 122.5204 | 122.4701 | 122.5342 | -0.10986 | 122.4335 | 122.4472 | 122.525 | -0.032044
2105.0469 | 122.5983 | -122.4472 | 0.07782 | 0.0054168 | 0.018658 | 0.087316 | 0.026724 | -0.071032 | -0.018826 | 0.0046334 | 0.0073242 | 0.01807 | -0.027893 | -0.0093609 | -0.0052636 | 0.010104 | 0.10071 | 0.068665 | 0.091553 | 0.12817 | 0.1236 | 0.07782 | -0.064087 | 0.059509 | 0.10529 | -0.050354 | 0.032043 | 0.054932 | 0.086975 | 0.004578 | 122.525 | 122.3831 | 0.045776 | 122.5159 | 122.5754 | 0.19226 | 0.022888 | 122.5342 | 122.4518 | -0.045777 | 122.5067 | 122.3969 | -0.054932 | -0.022888 | 122.5708 | 122.5479 | 122.5388 | -0.14191 | 122.4792 | 122.5021 | 122.5525 | -0.073242
2106.8125 | 122.699 | -122.4106 | 0.068665 | -0.0022127 | 0.027416 | 0.085821 | 0.030569 | -0.073809 | -0.02908 | 0.003779 | 0.0073242 | 0.011021 | -0.027038 | -0.0082929 | -0.0099634 | 0.010318 | 0.10986 | 0.16937 | 0.20142 | 0.16479 | 0.09613 | 0.10071 | -0.032043 | 0.086975 | 0.19684 | 0.068665 | 0.022888 | 0.013733 | 0.11444 | 0.018311 | 122.5113 | 122.3785 | 0.027465 | 122.58 | 122.5754 | 0.19684 | 0.041198 | 122.525 | 122.4289 | -0.045777 | 122.4976 | 122.4792 | 0.050354 | -0.054932 | 122.5067 | 122.5204 | 122.612 | -0.10071 | 122.4335 | 122.4243 | 122.6074 | -0.050354
2108.5469 | 122.644 | -122.4197 | 0.07782 | 0.013046 | 0.029553 | 0.088812 | 0.025443 | -0.069964 | -0.028012 | 0.0061288 | 0.0073242 | 0.013371 | -0.027038 | -0.01107 | -0.0063318 | 0.010959 | 0.082397 | 0.13275 | 0.14191 | 0.13275 | 0.082397 | 0.091553 | -0.018311 | 0.059509 | 0.09613 | -0.004578 | 0.004578 | 0.041199 | 0.11444 | 0.036621 | 122.5113 | 122.4014 | 0.004577 | 122.5525 | 122.5525 | 0.15106 | 0.004577 | 122.5342 | 122.4564 | -0.073242 | 122.4792 | 122.4152 | -0.041199 | -0.036621 | 122.5021 | 122.5021 | 122.5616 | -0.096131 | 122.4243 | 122.4609 | 122.5159 | -0.041199
2110.3281 | 122.6303 | -122.4289 | 0.11902 | -0.0022127 | 0.018658 | 0.086675 | 0.026297 | -0.072527 | -0.020535 | 0.0069834 | -0.0003053 | 0.018925 | -0.027893 | -0.0055157 | -0.0024866 | 0.0096771 | 0.082397 | 0.050354 | 0.073242 | 0.1236 | 0.11444 | 0.059509 | -0.082397 | 0.054932 | 0.086975 | -0.050354 | 0.036621 | 0.054932 | 0.07782 | 0.004578 | 122.4884 | 122.3465 | -0.004578 | 122.4792 | 122.5525 | 0.20599 | -0.036622 | 122.5067 | 122.4335 | -0.082398 | 122.4838 | 122.3785 | -0.054932 | -0.064087 | 122.5433 | 122.5113 | 122.5021 | -0.20142 | 122.4655 | 122.4838 | 122.5159 | -0.11444
2112.1094 | 122.7127 | -122.3785 | 0.059509 | 0.0054168 | 0.02293 | 0.087103 | 0.025443 | -0.071673 | -0.02374 | 0.0033518 | 0.022583 | 0.017857 | -0.028106 | -0.0070111 | -0.002273 | 0.0096771 | 0.027466 | 0.018311 | 0.054932 | 0.091553 | 0.11902 | 0.073242 | -0.059509 | 0.045776 | 0.041199 | -0.059509 | 0.027466 | 0.036621 | 0.11444 | 0.022888 | 122.4518 | 122.319 | 0.05951 | 122.3969 | 122.4701 | 0.15106 | -0.032043 | 122.493 | 122.4014 | -0.032043 | 122.4243 | 122.319 | -0.082397 | -0.022888 | 122.4976 | 122.406 | 122.4335 | -0.11902 | 122.406 | 122.4152 | 122.4197 | -0.036621
2113.8125 | 122.644 | -122.4426 | 0.07782 | 0.0054168 | 0.024426 | 0.086675 | 0.025656 | -0.072314 | -0.019895 | 0.0050608 | -0.0003053 | 0.01807 | -0.028534 | -0.0074383 | -0.003982 | 0.0090363 | 0.022888 | -0.009155 | 0.022888 | 0.073242 | 0.13275 | 0.064087 | -0.054932 | 0 | 0.013733 | -0.09613 | 0.045776 | 0.054932 | 0.073242 | 0.004578 | 122.5067 | 122.3877 | 0.054931 | 122.4335 | 122.5159 | 0.12817 | -0.054932 | 122.5159 | 122.4472 | -0.032044 | 122.4426 | 122.3465 | -0.10071 | -0.022888 | 122.5754 | 122.4655 | 122.4655 | -0.13275 | 122.4884 | 122.4976 | 122.4564 | -0.073242
2115.5938 | 122.5708 | -122.4335 | 0.091553 | 0.0054168 | 0.017162 | 0.085821 | 0.027365 | -0.071245 | -0.022458 | 0.005488 | -0.0003053 | 0.017002 | -0.026397 | -0.0078657 | -0.0044092 | 0.0094635 | 0.086975 | 0.073242 | 0.082397 | 0.13275 | 0.10986 | 0.073242 | -0.068665 | 0.054932 | 0.086975 | -0.050354 | 0.027466 | 0.054932 | 0.10986 | 0.027466 | 122.5067 | 122.3648 | 0.01831 | 122.5067 | 122.5662 | 0.20142 | -0.004578 | 122.5433 | 122.4609 | -0.064087 | 122.4884 | 122.3831 | -0.07782 | -0.036621 | 122.5433 | 122.5204 | 122.5159 | -0.16022 | 122.4609 | 122.4884 | 122.5204 | -0.064087
2117.375 | 122.6212 | -122.438 | 0.10071 | 0.013046 | 0.018658 | 0.089666 | 0.02822 | -0.069537 | -0.021817 | 0.0057016 | 0.0073242 | 0.015934 | -0.024048 | -0.0067975 | -0.0048364 | 0.0098907 | 0.064087 | 0.07782 | 0.073242 | 0.13275 | 0.11902 | 0.064087 | -0.064087 | 0.036621 | 0.086975 | -0.050354 | 0.027466 | 0.036621 | 0.09613 | 0.009155 | 122.5021 | 122.374 | 0.018311 | 122.5159 | 122.5708 | 0.19684 | -0.036621 | 122.5342 | 122.4472 | -0.073242 | 122.4747 | 122.3877 | -0.059509 | -0.064087 | 122.5571 | 122.5021 | 122.5113 | -0.1648 | 122.4655 | 122.4747 | 122.525 | -0.091553
2119.1719 | 122.6486 | -122.4335 | 0.10986 | 0.013046 | 0.029553 | 0.090521 | 0.024161 | -0.074877 | -0.030576 | 0.004847 | 0.0073242 | 0.011235 | -0.027038 | -0.0076519 | -0.0078272 | 0.012454 | 0.064087 | 0.11444 | 0.13275 | 0.1236 | 0.068665 | 0.09613 | -0.022888 | 0.022888 | 0.11444 | 0.022888 | 0.013733 | 0.041199 | 0.11444 | 0.032043 | 122.5296 | 122.4106 | -0.041198 | 122.5479 | 122.5571 | 0.14648 | -0.045776 | 122.5479 | 122.4655 | -0.09613 | 122.4564 | 122.4564 | -0.009155 | -0.068664 | 122.5021 | 122.4976 | 122.5662 | -0.13275 | 122.4472 | 122.4747 | 122.5479 | -0.07782
2120.9375 | 122.6166 | -122.4289 | 0.091553 | 0.013046 | 0.019299 | 0.091375 | 0.024588 | -0.071459 | -0.023953 | 0.0039926 | 0.0073242 | 0.017216 | -0.025543 | -0.0089337 | -0.0046228 | 0.011173 | 0.013733 | 0.022888 | 0.041199 | 0.10986 | 0.11444 | 0.059509 | -0.073242 | 0.013733 | 0.07782 | -0.068665 | 0.045776 | 0.054932 | 0.07782 | 0.004578 | 122.4884 | 122.3557 | 0.022888 | 122.4518 | 122.5388 | 0.18311 | -0.07782 | 122.5067 | 122.4335 | -0.045777 | 122.4426 | 122.3602 | -0.073243 | -0.036621 | 122.5433 | 122.4426 | 122.4701 | -0.16479 | 122.4747 | 122.4838 | 122.5067 | -0.086975
2122.6562 | 122.644 | -122.4197 | 0.054932 | 0.0054168 | 0.030621 | 0.089666 | 0.024802 | -0.074023 | -0.028226 | 0.0057016 | 0.0073242 | 0.012303 | -0.028747 | -0.010002 | -0.0063318 | 0.012241 | 0.086975 | 0.1236 | 0.14648 | 0.14648 | 0.086975 | 0.09613 | -0.018311 | 0.050354 | 0.11444 | 0.004578 | 0 | 0.027466 | 0.10529 | 0.022888 | 122.5159 | 122.4014 | 0.032043 | 122.5433 | 122.5662 | 0.16479 | 0.032043 | 122.525 | 122.4426 | -0.054932 | 122.4701 | 122.4243 | -0.01831 | -0.027466 | 122.5067 | 122.5067 | 122.5662 | -0.073243 | 122.4197 | 122.4472 | 122.5342 | -0.032044
2124.4531 | 122.6028 | -122.4518 | 0.10986 | 0.013046 | 0.026348 | 0.091375 | 0.028433 | -0.0721 | -0.027585 | 0.0033518 | 0.014954 | 0.011875 | -0.027252 | -0.0080793 | -0.008468 | 0.0094635 | 0.10529 | 0.14648 | 0.19226 | 0.17395 | 0.091553 | 0.10529 | -0.022888 | 0.086975 | 0.19684 | 0.022888 | 0 | 0.022888 | 0.09613 | 0.032043 | 122.5571 | 122.4289 | -0.01831 | 122.5983 | 122.6257 | 0.19684 | -0.004577 | 122.5479 | 122.4838 | -0.10986 | 122.5388 | 122.4747 | -0.009155 | -0.086975 | 122.5433 | 122.5571 | 122.644 | -0.13275 | 122.4518 | 122.4747 | 122.6486 | -0.07782
2126.2344 | 122.5571 | -122.4335 | 0.10529 | 0.0054168 | 0.021435 | 0.086034 | 0.027792 | -0.071032 | -0.020108 | 0.0057016 | 0.0073242 | 0.018498 | -0.026397 | -0.0046613 | -0.0037684 | 0.0090363 | 0.082397 | 0.027466 | 0.07782 | 0.10986 | 0.10986 | 0.07782 | -0.059509 | 0.022888 | 0.032043 | -0.10071 | 0.032043 | 0.059509 | 0.073242 | -0.013733 | 122.5113 | 122.374 | 0.004577 | 122.4609 | 122.5433 | 0.16937 | -0.022889 | 122.5067 | 122.4197 | -0.073243 | 122.4564 | 122.3328 | -0.086975 | -0.045777 | 122.5433 | 122.5159 | 122.5113 | -0.16479 | 122.4655 | 122.493 | 122.4655 | -0.11902
2127.9375 | 122.6761 | -122.4152 | 0.082397 | 0.0054168 | 0.028698 | 0.091802 | 0.02822 | -0.072314 | -0.029294 | 0.0033518 | 0.0073242 | 0.012303 | -0.029175 | -0.0082929 | -0.0086816 | 0.012027 | 0.15564 | 0.1831 | 0.19226 | 0.17853 | 0.07782 | 0.10071 | -0.022888 | 0.091553 | 0.21057 | 0.054932 | -0.004578 | 0.018311 | 0.12817 | 0.022888 | 122.5159 | 122.3923 | -0.004577 | 122.5983 | 122.5937 | 0.20142 | 0.073243 | 122.5433 | 122.438 | -0.086975 | 122.5067 | 122.4701 | 0.032044 | -0.064086 | 122.493 | 122.5708 | 122.6074 | -0.10528 | 122.4106 | 122.4335 | 122.6257 | -0.059509
2129.7344 | 122.699 | -122.3831 | 0.068665 | 0.013046 | 0.032116 | 0.08753 | 0.029929 | -0.072527 | -0.027371 | 0.0029244 | 0.014954 | 0.011662 | -0.027252 | -0.0093609 | -0.010604 | 0.010959 | 0.091553 | 0.10986 | 0.14648 | 0.14648 | 0.10529 | 0.086975 | -0.032043 | 0.068665 | 0.16022 | 0.045776 | 0 | 0.036621 | 0.11444 | 0.018311 | 122.4701 | 122.3511 | 0.036621 | 122.493 | 122.5296 | 0.17853 | 0.022888 | 122.4976 | 122.4014 | -0.068665 | 122.4518 | 122.4289 | 0.027465 | -0.032044 | 122.4884 | 122.4747 | 122.5296 | -0.10071 | 122.3831 | 122.4197 | 122.5433 | -0.050354
2131.5156 | 122.7036 | -122.3877 | 0.07782 | 0.013046 | 0.031262 | 0.086889 | 0.026511 | -0.068682 | -0.020108 | 0.0057016 | 0.022583 | 0.016575 | -0.027038 | -0.0063703 | -0.0059046 | 0.0088227 | 0.13275 | 0.10071 | 0.14191 | 0.18768 | 0.086975 | 0.09613 | -0.045776 | 0.10071 | 0.13275 | 0.022888 | 0.004578 | 0.013733 | 0.11902 | 0.050354 | 122.4838 | 122.3419 | 0.009155 | 122.4884 | 122.5754 | 0.23346 | 0.054931 | 122.5067 | 122.438 | -0.073242 | 122.4884 | 122.4106 | -0.027466 | -0.064087 | 122.4747 | 122.5204 | 122.5296 | -0.1236 | 122.3923 | 122.4014 | 122.5204 | -0.027466
2133.25 | 122.6486 | -122.4289 | 0.07782 | 0.013046 | 0.029553 | 0.086462 | 0.028647 | -0.070818 | -0.024594 | 0.0061288 | -0.0003053 | 0.012943 | -0.025757 | -0.0067975 | -0.0061182 | 0.010532 | 0.14191 | 0.13275 | 0.19684 | 0.16937 | 0.082397 | 0.1236 | -0.018311 | 0.10529 | 0.15106 | 0.032043 | -0.004578 | 0.013733 | 0.11902 | 0.041199 | 122.5525 | 122.4106 | 0.004577 | 122.5616 | 122.5983 | 0.18768 | 0.064087 | 122.5479 | 122.4701 | -0.082398 | 122.5342 | 122.4609 | -0.009156 | -0.064087 | 122.5113 | 122.5708 | 122.6257 | -0.096131 | 122.4243 | 122.4426 | 122.58 | -0.036621
2135.0312 | 122.6028 | -122.4564 | 0.09613 | 0.013046 | 0.023571 | 0.085821 | 0.026938 | -0.0721 | -0.021176 | 0.0046334 | 0.014954 | 0.015721 | -0.026184 | -0.0065839 | -0.00035037 | 0.0094635 | 0.041199 | -0.018311 | 0.027466 | 0.09613 | 0.1236 | 0.059509 | -0.059509 | -0.004578 | -0.004578 | -0.091553 | 0.050354 | 0.068665 | 0.086975 | 0.004578 | 122.5159 | 122.3969 | 0.027466 | 122.438 | 122.5525 | 0.15564 | -0.054931 | 122.5433 | 122.4609 | -0.045776 | 122.4518 | 122.3648 | -0.096131 | -0.027465 | 122.58 | 122.4976 | 122.4838 | -0.15564 | 122.5067 | 122.525 | 122.4518 | -0.091552
2136.7344 | 122.6624 | -122.4106 | 0.07782 | 0.013046 | 0.028698 | 0.089239 | 0.022879 | -0.069323 | -0.02609 | 0.0042062 | -0.0079343 | 0.014225 | -0.030029 | -0.0076519 | -0.0035546 | 0.010959 | 0.11902 | 0.15106 | 0.17853 | 0.1831 | 0.073242 | 0.086975 | -0.018311 | 0.10986 | 0.16479 | 0.045776 | 0.004578 | 0.013733 | 0.09613 | 0.027466 | 122.4976 | 122.3923 | -0.004578 | 122.5616 | 122.5937 | 0.20142 | 0.041199 | 122.5067 | 122.438 | -0.073242 | 122.5204 | 122.4564 | 0.01831 | -0.064087 | 122.4838 | 122.5296 | 122.5891 | -0.096131 | 122.4152 | 122.4243 | 122.5754 | -0.050354
2138.5156 | 122.644 | -122.4106 | 0.09613 | 0.0054168 | 0.02528 | 0.08753 | 0.026938 | -0.071459 | -0.022458 | 0.0059152 | 0.0073242 | 0.01807 | -0.026611 | -0.0067975 | -0.0035546 | 0.010532 | 0.036621 | -0.013733 | 0.004578 | 0.082397 | 0.1236 | 0.054932 | -0.059509 | -0.004578 | 0.022888 | -0.09613 | 0.022888 | 0.073242 | 0.082397 | 0 | 122.4655 | 122.3511 | 0.027466 | 122.3969 | 122.493 | 0.14191 | -0.059509 | 122.493 | 122.4106 | -0.073242 | 122.406 | 122.3145 | -0.09613 | -0.022888 | 122.5342 | 122.4472 | 122.4152 | -0.15564 | 122.4335 | 122.4838 | 122.4335 | -0.09613
2140.2969 | 122.6028 | -122.438 | 0.10071 | 0.0054168 | 0.020794 | 0.09223 | 0.028006 | -0.073168 | -0.024167 | 0.0057016 | 0.014954 | 0.015293 | -0.02597 | -0.0072247 | -0.003982 | 0.011173 | 0.018311 | 0.032043 | 0.041199 | 0.086975 | 0.13733 | 0.050354 | -0.086975 | -0.027466 | 0.045776 | -0.086975 | 0.050354 | 0.054932 | 0.050354 | 0 | 122.4884 | 122.3511 | 0.036621 | 122.4701 | 122.525 | 0.17395 | -0.082397 | 122.4884 | 122.438 | -0.050354 | 122.4106 | 122.3511 | -0.086975 | -0.045776 | 122.5754 | 122.4564 | 122.4792 | -0.18768 | 122.4884 | 122.493 | 122.4838 | -0.10071
2142.0156 | 122.6898 | -122.4014 | 0.07782 | 0.0054168 | 0.034039 | 0.089666 | 0.029501 | -0.075518 | -0.029721 | 0.0059152 | 0.0073242 | 0.010807 | -0.025543 | -0.0070111 | -0.011245 | 0.010532 | 0.059509 | 0.064087 | 0.11902 | 0.14191 | 0.11444 | 0.10529 | -0.036621 | 0.022888 | 0.10986 | 0.004578 | 0.022888 | 0.036621 | 0.10529 | 0.027466 | 122.5067 | 122.3648 | 0.036621 | 122.4655 | 122.5433 | 0.17853 | -0.018311 | 122.5067 | 122.4289 | -0.054932 | 122.4243 | 122.406 | -0.022888 | -0.041199 | 122.5159 | 122.4609 | 122.5204 | -0.11444 | 122.4243 | 122.438 | 122.5113 | -0.050354
2143.7812 | 122.6166 | -122.4243 | 0.10529 | 0.013046 | 0.023144 | 0.089452 | 0.027365 | -0.072741 | -0.02139 | 0.0076242 | 0.0073242 | 0.01807 | -0.025757 | -0.0059429 | -0.0037684 | 0.0096771 | 0.09613 | 0.054932 | 0.082397 | 0.13733 | 0.1236 | 0.059509 | -0.059509 | 0.059509 | 0.10529 | -0.050354 | 0.022888 | 0.050354 | 0.086975 | 0 | 122.4838 | 122.3648 | 0.01831 | 122.4792 | 122.5616 | 0.19684 | -0.009156 | 122.5113 | 122.4243 | -0.082398 | 122.4838 | 122.374 | -0.050354 | -0.054932 | 122.5479 | 122.5204 | 122.5067 | -0.16479 | 122.4472 | 122.4747 | 122.5296 | -0.10529
2145.5 | 122.6257 | -122.438 | 0.10529 | 0.0054168 | 0.023998 | 0.090307 | 0.025443 | -0.071673 | -0.020749 | 0.0061288 | -0.0003053 | 0.017857 | -0.025543 | -0.0087201 | -0.0046228 | 0.0077545 | 0.073242 | 0.050354 | 0.07782 | 0.13733 | 0.1236 | 0.050354 | -0.068665 | 0.041199 | 0.082397 | -0.045776 | 0.036621 | 0.050354 | 0.07782 | 0.022888 | 122.4884 | 122.3694 | 0.01831 | 122.4884 | 122.5754 | 0.20599 | -0.032044 | 122.5159 | 122.4609 | -0.068665 | 122.4792 | 122.3923 | -0.068664 | -0.054932 | 122.5616 | 122.5113 | 122.5159 | -0.17395 | 122.4747 | 122.4884 | 122.5204 | -0.082398
2147.2812 | 122.6898 | -122.3923 | 0.07782 | 0.0054168 | 0.032757 | 0.088384 | 0.022025 | -0.069964 | -0.026944 | 0.006556 | 0.0073242 | 0.013584 | -0.027679 | -0.0085065 | -0.0059046 | 0.010959 | 0.11902 | 0.13733 | 0.16937 | 0.17853 | 0.086975 | 0.10986 | -0.018311 | 0.11902 | 0.15564 | 0.050354 | 0 | 0.013733 | 0.10529 | 0.059509 | 122.5021 | 122.374 | 0.009155 | 122.5296 | 122.5708 | 0.19684 | 0.041199 | 122.4976 | 122.4518 | -0.07782 | 122.5113 | 122.4426 | -0.009155 | -0.064087 | 122.4792 | 122.5113 | 122.5616 | -0.096131 | 122.3923 | 122.406 | 122.5479 | -0.018311
2149 | 122.6349 | -122.4335 | 0.10529 | 0.013046 | 0.022503 | 0.090948 | 0.029929 | -0.069323 | -0.024808 | 0.005488 | -0.0003053 | 0.017216 | -0.026184 | -0.0085065 | -0.0046228 | 0.0092499 | 0.050354 | 0.036621 | 0.082397 | 0.11444 | 0.11902 | 0.073242 | -0.068665 | 0.032043 | 0.09613 | -0.032043 | 0.041199 | 0.032043 | 0.073242 | 0.013733 | 122.5067 | 122.3648 | 0.013733 | 122.4701 | 122.5479 | 0.18311 | -0.054932 | 122.5067 | 122.4472 | -0.064087 | 122.4655 | 122.4014 | -0.045776 | -0.073243 | 122.5525 | 122.4838 | 122.5159 | -0.17395 | 122.4747 | 122.4655 | 122.5296 | -0.091553
2150.7656 | 122.5479 | -122.4335 | 0.10986 | 0.013046 | 0.022289 | 0.08753 | 0.026511 | -0.071459 | -0.020535 | 0.006556 | 0.0073242 | 0.017216 | -0.026825 | -0.0091473 | -0.0024866 | 0.012668 | 0.050354 | 0.027466 | 0.045776 | 0.091553 | 0.10986 | 0.068665 | -0.059509 | 0.004578 | 0.041199 | -0.09613 | 0.027466 | 0.059509 | 0.07782 | 0.032043 | 122.5021 | 122.374 | 0 | 122.4609 | 122.525 | 0.15106 | -0.059509 | 122.5113 | 122.4655 | -0.082397 | 122.438 | 122.3373 | -0.12817 | -0.050354 | 122.5433 | 122.4838 | 122.4792 | -0.16937 | 122.4609 | 122.493 | 122.4747 | -0.07782
2152.5469 | 122.6074 | -122.4472 | 0.11444 | 0.020676 | 0.020153 | 0.093084 | 0.02822 | -0.069964 | -0.025235 | 0.005488 | 0.0073242 | 0.017002 | -0.025757 | -0.0070111 | -0.0074 | 0.010959 | 0.009155 | 0 | 0.050354 | 0.091553 | 0.12817 | 0.050354 | -0.064087 | -0.036621 | 0.050354 | -0.10071 | 0.050354 | 0.073242 | 0.086975 | 0.013733 | 122.4976 | 122.3831 | 0.013733 | 122.4472 | 122.5388 | 0.15564 | -0.10529 | 122.5342 | 122.4609 | -0.064087 | 122.4106 | 122.3465 | -0.11444 | -0.041199 | 122.5754 | 122.4564 | 122.4976 | -0.17853 | 122.4976 | 122.5204 | 122.4976 | -0.10071
2154.2656 | 122.5891 | -122.4609 | 0.1236 | 0.013046 | 0.024639 | 0.091589 | 0.032919 | -0.070818 | -0.024167 | 0.0046334 | -0.0003053 | 0.017002 | -0.024048 | -0.0061567 | -0.0086816 | 0.010959 | -0.004578 | 0.004578 | 0.045776 | 0.07782 | 0.13733 | 0.050354 | -0.082397 | -0.050354 | 0.068665 | -0.086975 | 0.036621 | 0.064087 | 0.050354 | -0.004578 | 122.5113 | 122.3785 | 0.013733 | 122.4655 | 122.5388 | 0.16022 | -0.12817 | 122.5113 | 122.4564 | -0.086975 | 122.4106 | 122.374 | -0.082397 | -0.059509 | 122.5983 | 122.4564 | 122.5067 | -0.20599 | 122.4976 | 122.525 | 122.5296 | -0.12817
2156.0469 | 122.5983 | -122.4289 | 0.11444 | 0.020676 | 0.024853 | 0.092443 | 0.024802 | -0.07445 | -0.022458 | 0.0033518 | 0.014954 | 0.019139 | -0.025329 | -0.0082929 | -0.0046228 | 0.0088227 | 0.068665 | 0.082397 | 0.09613 | 0.13275 | 0.12817 | 0.086975 | -0.059509 | 0.054932 | 0.11444 | -0.045776 | 0.022888 | 0.054932 | 0.09613 | 0.032043 | 122.5159 | 122.3694 | 0.013733 | 122.5113 | 122.5616 | 0.19226 | -0.045776 | 122.525 | 122.4609 | -0.091553 | 122.4838 | 122.3831 | -0.077819 | -0.059509 | 122.5571 | 122.4976 | 122.525 | -0.17395 | 122.4518 | 122.4838 | 122.5433 | -0.082398
2157.8281 | 122.6166 | -122.4426 | 0.09613 | 0.020676 | 0.021435 | 0.09522 | 0.026724 | -0.073168 | -0.023953 | 0.0039926 | 0.0073242 | 0.016148 | -0.027038 | -0.0089337 | -0.00505 | 0.012454 | 0.009155 | 0.009155 | 0.027466 | 0.10071 | 0.13733 | 0.068665 | -0.050354 | -0.004578 | 0.068665 | -0.068665 | 0.054932 | 0.068665 | 0.091553 | 0.018311 | 122.5113 | 122.3923 | 0.041199 | 122.4518 | 122.5433 | 0.15106 | -0.086975 | 122.5342 | 122.4609 | -0.041198 | 122.438 | 122.374 | -0.086976 | -0.027465 | 122.58 | 122.4518 | 122.4701 | -0.14648 | 122.4976 | 122.5113 | 122.5113 | -0.077819
2159.6406 | 122.6028 | -122.4472 | 0.09613 | 0.028305 | 0.023571 | 0.093084 | 0.02886 | -0.072314 | -0.027799 | 0.0059152 | 0.022583 | 0.018925 | -0.027038 | -0.0057293 | -0.0069726 | 0.012027 | 0.009155 | 0.004578 | 0.045776 | 0.07782 | 0.14648 | 0.054932 | -0.050354 | -0.022888 | 0.041199 | -0.086975 | 0.041199 | 0.091553 | 0.064087 | 0.004578 | 122.5021 | 122.3969 | 0.050354 | 122.4518 | 122.525 | 0.12817 | -0.086975 | 122.5113 | 122.4518 | -0.054931 | 122.4243 | 122.3602 | -0.091553 | -0.004577 | 122.5937 | 122.4564 | 122.493 | -0.14648 | 122.4884 | 122.5388 | 122.4884 | -0.091552
2161.4375 | 122.6303 | -122.406 | 0.091553 | 0.0054168 | 0.030834 | 0.092443 | 0.02822 | -0.071459 | -0.028653 | 0.0035654 | 0.022583 | 0.013584 | -0.027466 | -0.0093609 | -0.0069726 | 0.0098907 | 0.10071 | 0.16022 | 0.17853 | 0.16937 | 0.082397 | 0.086975 | -0.022888 | 0.086975 | 0.21515 | 0.054932 | -0.004578 | 0.032043 | 0.11444 | 0.064087 | 122.493 | 122.3831 | -0.009156 | 122.5662 | 122.5754 | 0.19226 | 0.009155 | 122.5204 | 122.4701 | -0.096131 | 122.493 | 122.4609 | -0.009155 | -0.05951 | 122.4884 | 122.5067 | 122.5845 | -0.11444 | 122.4014 | 122.438 | 122.6212 | -0.027466
2163.1719 | 122.6532 | -122.4106 | 0.091553 | -0.0022127 | 0.033184 | 0.091375 | 0.029074 | -0.071459 | -0.028012 | 0.0033518 | 0.014954 | 0.014439 | -0.024902 | -0.0085065 | -0.0093226 | 0.0098907 | 0.13275 | 0.14648 | 0.19226 | 0.1831 | 0.10071 | 0.086975 | -0.022888 | 0.082397 | 0.20142 | 0.050354 | 0.009155 | 0.027466 | 0.1236 | 0.064087 | 122.4976 | 122.3877 | 0.009155 | 122.5571 | 122.5937 | 0.20599 | 0.041198 | 122.5342 | 122.4747 | -0.082398 | 122.493 | 122.4609 | -0.013733 | -0.064087 | 122.5113 | 122.5433 | 122.6028 | -0.11444 | 122.4197 | 122.438 | 122.612 | -0.027466
2164.9688 | 122.5708 | -122.4335 | 0.11902 | -0.0022127 | 0.025494 | 0.097356 | 0.026724 | -0.071032 | -0.025449 | 0.0033518 | 0.0073242 | 0.016361 | -0.025543 | -0.0082929 | -0.0052636 | 0.0088227 | 0.059509 | 0.064087 | 0.073242 | 0.10529 | 0.12817 | 0.086975 | -0.059509 | -0.018311 | 0.059509 | -0.064087 | 0.045776 | 0.07782 | 0.050354 | 0.022888 | 122.5204 | 122.374 | 0.009155 | 122.4976 | 122.5388 | 0.16479 | -0.05951 | 122.4838 | 122.4564 | -0.073243 | 122.4152 | 122.3694 | -0.086975 | -0.041199 | 122.5616 | 122.493 | 122.5067 | -0.17853 | 122.4792 | 122.5113 | 122.493 | -0.096131
2166.6875 | 122.7173 | -122.3831 | 0.07782 | 0.0054168 | 0.038525 | 0.090307 | 0.026083 | -0.073168 | -0.022031 | 0.0027108 | 0.0073242 | 0.01743 | -0.027038 | -0.0080793 | -0.0048364 | 0.0086091 | 0.1236 | 0.091553 | 0.13275 | 0.16937 | 0.11902 | 0.1236 | -0.027466 | 0.09613 | 0.15564 | 0.009155 | 0.004578 | 0.022888 | 0.13733 | 0.050354 | 122.5067 | 122.3557 | 0.041199 | 122.4747 | 122.5525 | 0.19684 | 0.045776 | 122.5204 | 122.4335 | -0.073242 | 122.4792 | 122.3923 | -0.041199 | -0.054932 | 122.5021 | 122.5067 | 122.5159 | -0.10529 | 122.3877 | 122.406 | 122.5388 | -0.027466
2168.4844 | 122.699 | -122.3694 | 0.10071 | 0.013046 | 0.03532 | 0.091375 | 0.024802 | -0.070818 | -0.023313 | 0.006556 | 0.014954 | 0.014225 | -0.027679 | -0.0097883 | -0.003982 | 0.0094635 | 0.11444 | 0.11444 | 0.13733 | 0.16022 | 0.09613 | 0.10071 | -0.041199 | 0.10529 | 0.13733 | 0.032043 | 0 | 0.013733 | 0.1236 | 0.054932 | 122.4701 | 122.3282 | -0.004578 | 122.4838 | 122.5296 | 0.20142 | 0.013733 | 122.493 | 122.4243 | -0.10071 | 122.4747 | 122.4014 | -0.022889 | -0.086975 | 122.4655 | 122.4838 | 122.5067 | -0.14191 | 122.3694 | 122.3831 | 122.5067 | -0.045776
2170.2344 | 122.6898 | -122.3969 | 0.073242 | 0.0054168 | 0.034893 | 0.092657 | 0.029074 | -0.073595 | -0.027158 | 0.003779 | 0.0073242 | 0.014012 | -0.025757 | -0.0093609 | -0.0099634 | 0.0096771 | 0.12817 | 0.1831 | 0.19226 | 0.17853 | 0.091553 | 0.11444 | -0.004578 | 0.086975 | 0.20142 | 0.068665 | 0.013733 | 0.032043 | 0.1236 | 0.059509 | 122.5113 | 122.3923 | 0.018311 | 122.58 | 122.5754 | 0.18311 | 0.054932 | 122.5204 | 122.4564 | -0.059509 | 122.4838 | 122.4655 | 0.009156 | -0.041199 | 122.4884 | 122.525 | 122.5891 | -0.07782 | 122.4106 | 122.4289 | 122.5983 | -0.013733
2172.0156 | 122.5708 | -122.4564 | 0.11902 | -0.0098417 | 0.026562 | 0.093511 | 0.024802 | -0.072954 | -0.019895 | 0.0069834 | 0.0073242 | 0.018498 | -0.025757 | -0.0074383 | -0.0018458 | 0.0088227 | 0.059509 | 0.009155 | 0.032043 | 0.091553 | 0.12817 | 0.068665 | -0.054932 | -0.004578 | 0 | -0.10986 | 0.041199 | 0.073242 | 0.086975 | 0.004578 | 122.525 | 122.4014 | 0.009155 | 122.4655 | 122.5479 | 0.14649 | -0.05951 | 122.5433 | 122.4609 | -0.07782 | 122.4518 | 122.3465 | -0.11444 | -0.045777 | 122.5845 | 122.5159 | 122.4884 | -0.17395 | 122.4976 | 122.5296 | 122.4564 | -0.11444
2173.7812 | 122.5845 | -122.4289 | 0.10529 | 0.0054168 | 0.034039 | 0.093298 | 0.026511 | -0.074663 | -0.028653 | 0.0042062 | 0.014954 | 0.014225 | -0.026397 | -0.0078657 | -0.0074 | 0.011813 | 0.13733 | 0.16937 | 0.17395 | 0.16937 | 0.073242 | 0.10071 | -0.027466 | 0.073242 | 0.19684 | 0.027466 | 0.013733 | 0.032043 | 0.10986 | 0.045776 | 122.5296 | 122.4014 | -0.032044 | 122.5983 | 122.5983 | 0.19684 | 0.032043 | 122.5388 | 122.4747 | -0.091553 | 122.5021 | 122.4564 | -0.01831 | -0.073243 | 122.5021 | 122.5662 | 122.6028 | -0.13275 | 122.4426 | 122.4609 | 122.6257 | -0.05951
2175.5 | 122.6074 | -122.4518 | 0.10529 | 0.0054168 | 0.035748 | 0.093725 | 0.029715 | -0.071459 | -0.028226 | 0.0035654 | 0.0073242 | 0.015293 | -0.024688 | -0.0085065 | -0.0061182 | 0.012027 | 0.11902 | 0.16937 | 0.19226 | 0.17853 | 0.086975 | 0.10529 | -0.013733 | 0.086975 | 0.19684 | 0.041199 | 0.009155 | 0.018311 | 0.11902 | 0.041199 | 122.5571 | 122.438 | -0.018311 | 122.6212 | 122.6303 | 0.19226 | 0.013733 | 122.5708 | 122.493 | -0.096131 | 122.5388 | 122.493 | 0 | -0.086975 | 122.5388 | 122.5708 | 122.644 | -0.11902 | 122.4609 | 122.4701 | 122.6486 | -0.064087
2177.2188 | 122.6944 | -122.3602 | 0.059509 | 0.013046 | 0.037243 | 0.092657 | 0.027152 | -0.071886 | -0.022244 | 0.0057016 | 0.022583 | 0.015934 | -0.024688 | -0.0063703 | -0.0052636 | 0.0092499 | 0.086975 | 0.086975 | 0.11902 | 0.14191 | 0.10071 | 0.09613 | -0.041199 | 0.10071 | 0.13275 | 0.013733 | 0.009155 | 0.041199 | 0.10986 | 0.064087 | 122.4564 | 122.319 | 0.041199 | 122.4472 | 122.5021 | 0.18311 | 0.027466 | 122.4701 | 122.4243 | -0.050354 | 122.4609 | 122.374 | -0.050354 | -0.01831 | 122.4609 | 122.4472 | 122.4792 | -0.10071 | 122.3694 | 122.4014 | 122.493 | 0.004578
2179 | 122.5983 | -122.4289 | 0.10529 | 0.013046 | 0.034893 | 0.093938 | 0.024588 | -0.073382 | -0.019254 | 0.0057016 | 0.0073242 | 0.01807 | -0.026184 | -0.0074383 | -0.0061182 | 0.0088227 | 0.091553 | 0.064087 | 0.09613 | 0.13275 | 0.10529 | 0.082397 | -0.064087 | 0.050354 | 0.10986 | -0.045776 | 0.050354 | 0.064087 | 0.09613 | 0.027466 | 122.5113 | 122.3648 | 0 | 122.493 | 122.5616 | 0.19684 | -0.013733 | 122.525 | 122.4564 | -0.054932 | 122.4792 | 122.3831 | -0.073242 | -0.041199 | 122.5342 | 122.5204 | 122.525 | -0.16937 | 122.4792 | 122.493 | 122.5388 | -0.07782
2180.7812 | 122.6624 | -122.4289 | 0.07782 | -0.0022127 | 0.033825 | 0.096075 | 0.02822 | -0.071032 | -0.030362 | 0.0050608 | 0.0073242 | 0.014439 | -0.024688 | -0.0080793 | -0.0074 | 0.012454 | 0.059509 | 0.10071 | 0.12817 | 0.14648 | 0.11902 | 0.10071 | -0.018311 | 0.050354 | 0.10529 | 0.004578 | 0.027466 | 0.045776 | 0.10529 | 0.050354 | 122.5296 | 122.4106 | 0.041199 | 122.5296 | 122.5754 | 0.16479 | -0.018311 | 122.5342 | 122.4792 | -0.050354 | 122.4792 | 122.4335 | -0.045776 | -0.032044 | 122.5479 | 122.4884 | 122.5571 | -0.096131 | 122.4564 | 122.4747 | 122.5342 | -0.027466
2182.4844 | 122.5937 | -122.4106 | 0.11902 | 0.0054168 | 0.038098 | 0.09522 | 0.026938 | -0.072954 | -0.020749 | 0.0067696 | 0.0073242 | 0.019139 | -0.025757 | -0.0072247 | -0.0046228 | 0.0064727 | 0.10071 | 0.073242 | 0.09613 | 0.1236 | 0.13275 | 0.07782 | -0.045776 | 0.064087 | 0.10071 | -0.050354 | 0.018311 | 0.050354 | 0.086975 | 0.041199 | 122.4884 | 122.3648 | 0.013732 | 122.4838 | 122.5342 | 0.16937 | -0.018311 | 122.4976 | 122.4518 | -0.10071 | 122.4747 | 122.3602 | -0.091553 | -0.068665 | 122.5433 | 122.5113 | 122.5067 | -0.16479 | 122.4289 | 122.4609 | 122.5113 | -0.07782
2184.2188 | 122.7081 | -122.3969 | 0.064087 | -0.0022127 | 0.038311 | 0.097356 | 0.024161 | -0.074023 | -0.030576 | 0.003779 | 0.022583 | 0.014652 | -0.027466 | -0.0087201 | -0.0080408 | 0.011173 | 0.082397 | 0.11444 | 0.15106 | 0.17853 | 0.091553 | 0.11444 | -0.022888 | 0.091553 | 0.19684 | 0.059509 | 0.004578 | 0.032043 | 0.13275 | 0.064087 | 122.5113 | 122.374 | 0.027466 | 122.5113 | 122.5754 | 0.20142 | 0.01831 | 122.5296 | 122.4609 | -0.059509 | 122.4884 | 122.4564 | -0.004578 | -0.032044 | 122.4884 | 122.4792 | 122.5479 | -0.086975 | 122.4014 | 122.4289 | 122.5937 | 0
2185.9688 | 122.6715 | -122.3785 | 0.10071 | 0.0054168 | 0.043652 | 0.09287 | 0.028006 | -0.0721 | -0.019681 | 0.004847 | -0.0079343 | 0.019993 | -0.02127 | -0.0059429 | -0.0044092 | 0.010104 | 0.059509 | -0.018311 | 0.041199 | 0.09613 | 0.13275 | 0.073242 | -0.050354 | 0.022888 | 0.027466 | -0.082397 | 0.054932 | 0.068665 | 0.082397 | 0.036621 | 122.4518 | 122.3282 | 0.032043 | 122.3602 | 122.4747 | 0.14648 | -0.041199 | 122.4609 | 122.4152 | -0.045776 | 122.4014 | 122.2961 | -0.11902 | -0.032043 | 122.5113 | 122.438 | 122.4197 | -0.15106 | 122.4335 | 122.4472 | 122.406 | -0.064087
2187.6875 | 122.6532 | -122.4152 | 0.09613 | 0.013046 | 0.03767 | 0.10013 | 0.027579 | -0.073168 | -0.02844 | 0.007197 | 0.014954 | 0.013798 | -0.02597 | -0.0097883 | -0.008468 | 0.010959 | 0.064087 | 0.10071 | 0.13733 | 0.14648 | 0.10071 | 0.11444 | -0.032043 | 0.050354 | 0.11902 | 0.018311 | 0.018311 | 0.041199 | 0.10986 | 0.045776 | 122.5296 | 122.3831 | 0.004578 | 122.5159 | 122.5616 | 0.17853 | -0.032043 | 122.525 | 122.4609 | -0.077819 | 122.4655 | 122.4335 | -0.027465 | -0.054931 | 122.5159 | 122.4792 | 122.5525 | -0.12817 | 122.4335 | 122.4564 | 122.5342 | -0.050354
2189.4062 | 122.5937 | -122.4014 | 0.082397 | 0.013046 | 0.043652 | 0.096075 | 0.024161 | -0.072314 | -0.019895 | 0.005488 | 0.014954 | 0.019993 | -0.024261 | -0.0061567 | -0.0027002 | 0.010318 | 0.036621 | -0.004578 | 0.022888 | 0.10529 | 0.13733 | 0.068665 | -0.054932 | 0 | 0.004578 | -0.091553 | 0.07782 | 0.068665 | 0.10529 | 0.022888 | 122.4701 | 122.3465 | 0.054932 | 122.3969 | 122.5067 | 0.16022 | -0.045776 | 122.5067 | 122.4243 | -0.004577 | 122.4014 | 122.3099 | -0.11444 | -0.013732 | 122.5388 | 122.438 | 122.4243 | -0.13733 | 122.4792 | 122.4701 | 122.406 | -0.059509
2191.1094 | 122.6074 | -122.4243 | 0.11902 | 0.0054168 | 0.041088 | 0.099706 | 0.027792 | -0.068896 | -0.023953 | 0.0052744 | -0.0003053 | 0.018498 | -0.022339 | -0.0057293 | -0.0071862 | 0.0088227 | 0.036621 | 0.022888 | 0.054932 | 0.1236 | 0.14191 | 0.041199 | -0.07782 | 0.004578 | 0.064087 | -0.07782 | 0.064087 | 0.07782 | 0.091553 | 0.022888 | 122.4655 | 122.3465 | 0.022888 | 122.4472 | 122.5479 | 0.20142 | -0.082398 | 122.5159 | 122.4472 | -0.054932 | 122.4289 | 122.3465 | -0.10071 | -0.041199 | 122.5662 | 122.4609 | 122.4792 | -0.19684 | 122.4884 | 122.5021 | 122.4884 | -0.096131
2192.8438 | 122.58 | -122.4472 | 0.11444 | 0.0054168 | 0.046429 | 0.096929 | 0.023947 | -0.070177 | -0.024381 | 0.0050608 | 0.014954 | 0.018925 | -0.022552 | -0.0074383 | -0.003982 | 0.010318 | 0.027466 | -0.004578 | 0.041199 | 0.091553 | 0.14191 | 0.073242 | -0.059509 | 0 | 0.022888 | -0.11444 | 0.054932 | 0.086975 | 0.09613 | 0.032043 | 122.5204 | 122.3877 | 0.027466 | 122.4426 | 122.5388 | 0.15106 | -0.086975 | 122.5433 | 122.4792 | -0.059509 | 122.4472 | 122.3328 | -0.14648 | -0.027466 | 122.5891 | 122.4747 | 122.4884 | -0.17395 | 122.5021 | 122.5342 | 122.4701 | -0.082398
2194.5469 | 122.5433 | -122.4243 | 0.13733 | 0.0054168 | 0.043865 | 0.099706 | 0.026724 | -0.072527 | -0.020963 | 0.0044198 | 0.014954 | 0.023411 | -0.022979 | -0.0063703 | -0.0054772 | 0.010532 | 0.073242 | 0.050354 | 0.082397 | 0.13275 | 0.1236 | 0.064087 | -0.045776 | 0.022888 | 0.059509 | -0.091553 | 0.054932 | 0.064087 | 0.091553 | 0.027466 | 122.4884 | 122.3785 | -0.013733 | 122.4747 | 122.5571 | 0.17853 | -0.064087 | 122.5159 | 122.4518 | -0.082397 | 122.4472 | 122.3328 | -0.11902 | -0.073242 | 122.5479 | 122.4976 | 122.5067 | -0.18311 | 122.4792 | 122.4884 | 122.4838 | -0.10986
2196.25 | 121.907 | -121.6095 | 0.10529 | -0.0022127 | -0.00035461 | 0.068517 | 0.030142 | -0.066119 | -0.029508 | 0.0010018 | 0.014954 | 0.03986 | 0.024231 | -0.011497 | -0.011031 | 0.015659 | 0.086975 | 0.14191 | 0.17853 | 0.16479 | 0.068665 | 0.10071 | -0.027466 | 0.091553 | 0.21057 | 0.054932 | 0.013733 | 0.032043 | 0.11444 | 0.064087 | 121.7102 | 121.582 | -0.036621 | 121.7514 | 121.7743 | 0.19226 | -0.018311 | 121.7239 | 121.6736 | -0.091553 | 121.7011 | 121.6644 | -0.009155 | -0.073243 | 121.6782 | 121.6965 | 121.788 | -0.13275 | 121.6232 | 121.6415 | 121.8201 | -0.041199
2197.9531 | 122.4609 | -122.2641 | 0.12817 | 0.0054168 | 0.008404 | 0.067236 | 0.027365 | -0.067614 | -0.019254 | 0.00207 | -0.0003053 | 0.047978 | 0.026367 | -0.01107 | -0.0041956 | 0.011813 | 0.004578 | -0.013733 | 0.018311 | 0.068665 | 0.13275 | 0.045776 | -0.064087 | -0.009155 | 0.027466 | -0.10529 | 0.041199 | 0.064087 | 0.091553 | 0.022888 | 122.3099 | 122.2 | 0.004577 | 122.2504 | 122.3328 | 0.13275 | -0.1236 | 122.3557 | 122.287 | -0.086975 | 122.2549 | 122.1588 | -0.12817 | -0.064087 | 122.3969 | 122.2687 | 122.2824 | -0.19226 | 122.3053 | 122.3282 | 122.2916 | -0.10529
2199.6875 | 122.5296 | -122.2778 | 0.10986 | 0.0054168 | 0.00071339 | 0.070013 | 0.026511 | -0.069323 | -0.022672 | 0.00207 | 0.0073242 | 0.04755 | 0.025727 | -0.0093609 | -0.0041956 | 0.012241 | 0.022888 | 0.018311 | 0.050354 | 0.11444 | 0.086975 | 0.059509 | -0.082397 | 0.036621 | 0.10071 | -0.041199 | 0.041199 | 0.059509 | 0.10529 | 0.022888 | 122.3373 | 122.1954 | -0.022888 | 122.2961 | 122.3923 | 0.19684 | -0.086975 | 122.3831 | 122.3007 | -0.068664 | 122.3145 | 122.2366 | -0.064087 | -0.050354 | 122.3648 | 122.3007 | 122.3282 | -0.19226 | 122.319 | 122.3373 | 122.3785 | -0.086975
2201.3906 | 122.4976 | -122.3328 | 0.1236 | -0.0022127 | 0.0017816 | 0.067663 | 0.028647 | -0.066332 | -0.028653 | 0.0016428 | 0.014954 | 0.043064 | 0.025727 | -0.011924 | -0.0091088 | 0.013736 | 0.064087 | 0.13275 | 0.14648 | 0.16479 | 0.09613 | 0.068665 | -0.036621 | 0.054932 | 0.18768 | 0.032043 | 0.022888 | 0.050354 | 0.13733 | 0.054932 | 122.4014 | 122.2961 | -0.027466 | 122.4655 | 122.4976 | 0.20142 | -0.059509 | 122.4701 | 122.3877 | -0.10071 | 122.3877 | 122.3648 | -0.022889 | -0.073242 | 122.4289 | 122.3969 | 122.4792 | -0.16022 | 122.3557 | 122.3831 | 122.5204 | -0.068664
2203.0938 | 122.5342 | -122.3328 | 0.11444 | 0.013046 | 0.001568 | 0.067449 | 0.026938 | -0.068041 | -0.020963 | -0.0015616 | 0.014954 | 0.047123 | 0.026154 | -0.0078657 | -0.0048364 | 0.012454 | -0.009155 | 0 | 0.036621 | 0.07782 | 0.10986 | 0.050354 | -0.082397 | 0 | 0.073242 | -0.068665 | 0.054932 | 0.07782 | 0.064087 | 0.041199 | 122.3831 | 122.2504 | -0.004578 | 122.3328 | 122.4106 | 0.16022 | -0.1236 | 122.3969 | 122.374 | -0.059509 | 122.3328 | 122.2641 | -0.10986 | -0.036621 | 122.4426 | 122.3236 | 122.3694 | -0.19684 | 122.3877 | 122.4106 | 122.406 | -0.073242
2204.8125 | 122.5571 | -122.3282 | 0.10986 | 0.0054168 | 0.0026362 | 0.067236 | 0.02822 | -0.068468 | -0.020963 | -0.00027975 | 0.0073242 | 0.047337 | 0.027863 | -0.0089337 | -0.0044092 | 0.0094635 | 0.032043 | 0.036621 | 0.073242 | 0.1236 | 0.10529 | 0.059509 | -0.064087 | 0.050354 | 0.11444 | -0.045776 | 0.045776 | 0.068665 | 0.11444 | 0.027466 | 122.3877 | 122.2641 | -0.004577 | 122.3648 | 122.4518 | 0.18768 | -0.07782 | 122.4426 | 122.3557 | -0.064087 | 122.3785 | 122.2824 | -0.073242 | -0.041198 | 122.4335 | 122.3602 | 122.4014 | -0.17395 | 122.374 | 122.3969 | 122.4426 | -0.082397
2206.6094 | 122.6303 | -122.3328 | 0.082397 | -0.0022127 | 0.00049979 | 0.069372 | 0.026511 | -0.069537 | -0.023953 | 0.0014292 | -0.0003053 | 0.045414 | 0.025299 | -0.0087201 | -0.00505 | 0.013309 | 0 | -0.004578 | 0.032043 | 0.07782 | 0.11444 | 0.064087 | -0.073242 | 0.022888 | 0.045776 | -0.050354 | 0.045776 | 0.068665 | 0.10986 | 0.059509 | 122.3969 | 122.2595 | 0.032044 | 122.3282 | 122.4106 | 0.15106 | -0.082397 | 122.4426 | 122.3923 | -0.036621 | 122.3557 | 122.2824 | -0.10986 | -0.013732 | 122.4472 | 122.3328 | 122.3648 | -0.15564 | 122.3785 | 122.4014 | 122.3785 | -0.022888
2208.4219 | 122.5204 | -122.3648 | 0.12817 | 0.0054168 | 0.0041314 | 0.068517 | 0.027152 | -0.068255 | -0.022672 | -0.00027975 | 0.014954 | 0.048832 | 0.02359 | -0.0089337 | -0.0037684 | 0.011386 | 0 | 0.004578 | 0.022888 | 0.086975 | 0.10529 | 0.041199 | -0.082397 | -0.004578 | 0.022888 | -0.091553 | 0.064087 | 0.073242 | 0.091553 | 0.032043 | 122.406 | 122.2824 | -0.022888 | 122.3694 | 122.4518 | 0.16937 | -0.12817 | 122.4564 | 122.3969 | -0.064087 | 122.3602 | 122.2733 | -0.1236 | -0.054932 | 122.4701 | 122.3648 | 122.3877 | -0.21057 | 122.4289 | 122.438 | 122.3877 | -0.096131
2210.2344 | 122.5616 | -122.374 | 0.10529 | 0.0054168 | -0.00014101 | 0.070654 | 0.027365 | -0.068682 | -0.021176 | 0.0014292 | 0.0073242 | 0.048191 | 0.02594 | -0.010643 | -0.0035546 | 0.013736 | 0.032043 | 0.045776 | 0.064087 | 0.11444 | 0.09613 | 0.059509 | -0.068665 | 0.045776 | 0.10986 | -0.032043 | 0.041199 | 0.068665 | 0.091553 | 0.032043 | 122.4335 | 122.3053 | -0.009156 | 122.4197 | 122.4884 | 0.18311 | -0.073243 | 122.4655 | 122.406 | -0.064087 | 122.4197 | 122.3419 | -0.064086 | -0.036621 | 122.4701 | 122.406 | 122.438 | -0.17395 | 122.4152 | 122.4426 | 122.4838 | -0.073243
2212.0312 | 122.612 | -122.3648 | 0.091553 | 0.013046 | 0.0026362 | 0.072149 | 0.028433 | -0.068682 | -0.031644 | -0.00092075 | 0.0073242 | 0.041996 | 0.025299 | -0.011283 | -0.0076136 | 0.016513 | 0.068665 | 0.11444 | 0.15106 | 0.13733 | 0.073242 | 0.091553 | -0.009155 | 0.073242 | 0.15106 | 0.041199 | 0.018311 | 0.032043 | 0.11444 | 0.073242 | 122.4564 | 122.3557 | -0.018311 | 122.4792 | 122.5021 | 0.14648 | -0.022888 | 122.4792 | 122.438 | -0.073242 | 122.438 | 122.406 | -0.032043 | -0.05951 | 122.438 | 122.4335 | 122.5159 | -0.10071 | 122.3831 | 122.3969 | 122.5159 | -0.018311
2213.8125 | 122.6257 | -122.3373 | 0.091553 | -0.0022127 | 0.0022088 | 0.068517 | 0.027365 | -0.069537 | -0.024808 | -0.00027975 | 0.0073242 | 0.042851 | 0.024659 | -0.010002 | -0.0086816 | 0.012241 | 0.086975 | 0.1236 | 0.16022 | 0.16022 | 0.045776 | 0.10529 | -0.022888 | 0.10071 | 0.16937 | 0.059509 | 0.009155 | 0.027466 | 0.11902 | 0.07782 | 122.4426 | 122.3145 | -0.045777 | 122.4609 | 122.4976 | 0.1831 | -0.004578 | 122.4564 | 122.4152 | -0.082398 | 122.438 | 122.3969 | -0.018311 | -0.064087 | 122.3831 | 122.4243 | 122.4976 | -0.11444 | 122.3465 | 122.3648 | 122.5067 | -0.013733
2215.625 | 122.5388 | -122.3785 | 0.13733 | 0.0054168 | 0.001568 | 0.068304 | 0.026297 | -0.066973 | -0.022031 | 0.0010018 | 0.0073242 | 0.049046 | 0.025727 | -0.0080793 | -0.0048364 | 0.0096771 | 0.004578 | -0.022888 | 0.018311 | 0.073242 | 0.09613 | 0.059509 | -0.064087 | 0.009155 | 0.013733 | -0.11902 | 0.054932 | 0.091553 | 0.086975 | 0.041199 | 122.438 | 122.3145 | -0.041199 | 122.3557 | 122.4518 | 0.13733 | -0.13275 | 122.4655 | 122.4197 | -0.082397 | 122.3877 | 122.2595 | -0.16022 | -0.045776 | 122.4747 | 122.3831 | 122.3969 | -0.20142 | 122.4335 | 122.4701 | 122.3923 | -0.09613
2217.3594 | 122.5433 | -122.3877 | 0.10529 | 0.013046 | 7.2586e-05 | 0.068731 | 0.02587 | -0.067828 | -0.022031 | -0.00027975 | 0.0073242 | 0.049046 | 0.022736 | -0.0085065 | -0.003341 | 0.013736 | 0.064087 | 0.059509 | 0.068665 | 0.11902 | 0.086975 | 0.059509 | -0.07782 | 0.059509 | 0.11444 | -0.045776 | 0.041199 | 0.045776 | 0.09613 | 0.045776 | 122.4472 | 122.3099 | -0.018311 | 122.4472 | 122.5067 | 0.19684 | -0.041199 | 122.4838 | 122.4335 | -0.064087 | 122.4472 | 122.3419 | -0.091552 | -0.05951 | 122.4747 | 122.4518 | 122.4564 | -0.18311 | 122.4289 | 122.4335 | 122.5021 | -0.05951
2219.1406 | 122.5388 | -122.3969 | 0.1236 | 0.0054168 | 7.2586e-05 | 0.068945 | 0.029929 | -0.067187 | -0.02908 | -0.0015616 | -0.0003053 | 0.045841 | 0.024231 | -0.010429 | -0.0086816 | 0.01395 | 0.032043 | 0.073242 | 0.10986 | 0.11902 | 0.091553 | 0.07782 | -0.073242 | -0.013733 | 0.10071 | -0.041199 | 0.054932 | 0.059509 | 0.11444 | 0.022888 | 122.4747 | 122.3236 | -0.032043 | 122.4701 | 122.5159 | 0.19226 | -0.091553 | 122.5113 | 122.4197 | -0.068664 | 122.3831 | 122.3557 | -0.064087 | -0.064087 | 122.4884 | 122.4289 | 122.5067 | -0.19684 | 122.4518 | 122.4564 | 122.4976 | -0.10071
2220.9219 | 122.5388 | -122.406 | 0.10529 | 0.013046 | 0.0022088 | 0.066167 | 0.026297 | -0.068896 | -0.019895 | -6.615e-05 | 0.0073242 | 0.049473 | 0.027222 | -0.0076519 | -0.0061182 | 0.011173 | 0.068665 | 0.064087 | 0.082397 | 0.11902 | 0.091553 | 0.064087 | -0.068665 | 0.050354 | 0.11444 | -0.032043 | 0.050354 | 0.054932 | 0.10529 | 0.050354 | 122.4701 | 122.3373 | -0.013733 | 122.4701 | 122.525 | 0.18768 | -0.036621 | 122.5113 | 122.4564 | -0.054932 | 122.4564 | 122.374 | -0.082397 | -0.050354 | 122.4976 | 122.4747 | 122.4884 | -0.17395 | 122.4564 | 122.4609 | 122.5204 | -0.054932
2222.7031 | 122.6578 | -122.3602 | 0.09613 | 0.0054168 | 0.004345 | 0.072149 | 0.027792 | -0.071032 | -0.029935 | 0.00057465 | 0.022583 | 0.044773 | 0.025086 | -0.0089337 | -0.0076136 | 0.013095 | 0.022888 | 0.054932 | 0.10071 | 0.1236 | 0.07782 | 0.073242 | -0.032043 | 0.027466 | 0.1236 | 0.009155 | 0.027466 | 0.041199 | 0.11902 | 0.050354 | 122.4335 | 122.3282 | -0.01831 | 122.4152 | 122.4838 | 0.15564 | -0.073242 | 122.4792 | 122.4106 | -0.068664 | 122.3877 | 122.3694 | -0.041199 | -0.054931 | 122.438 | 122.3831 | 122.4609 | -0.12817 | 122.3877 | 122.4014 | 122.4838 | -0.045776
2224.4844 | 122.6074 | -122.3831 | 0.11902 | -0.0098417 | 0.00071339 | 0.072576 | 0.026938 | -0.066973 | -0.023953 | -0.0024162 | 0.0073242 | 0.045841 | 0.026795 | -0.0087201 | -0.0048364 | 0.012241 | -0.009155 | 0 | 0.018311 | 0.082397 | 0.11444 | 0.064087 | -0.09613 | -0.022888 | 0.059509 | -0.086975 | 0.059509 | 0.07782 | 0.082397 | 0.032043 | 122.4472 | 122.287 | -0.004578 | 122.3831 | 122.4655 | 0.17853 | -0.12817 | 122.4655 | 122.4152 | -0.05951 | 122.3602 | 122.2961 | -0.11902 | -0.041199 | 122.4976 | 122.374 | 122.4014 | -0.21515 | 122.4426 | 122.4609 | 122.4426 | -0.086976
2226.2188 | 122.644 | -122.3694 | 0.09613 | 0.0054168 | 0.0026362 | 0.071935 | 0.024374 | -0.068896 | -0.024808 | -0.00049335 | 0.0073242 | 0.043705 | 0.024445 | -0.01107 | -0.0044092 | 0.012882 | 0.09613 | 0.11902 | 0.16022 | 0.15564 | 0.059509 | 0.10529 | -0.050354 | 0.11444 | 0.15564 | 0.059509 | 0.018311 | 0.041199 | 0.1236 | 0.064087 | 122.4747 | 122.319 | -0.036621 | 122.4884 | 122.525 | 0.20599 | 0 | 122.493 | 122.4335 | -0.077819 | 122.4838 | 122.4289 | -0.004578 | -0.054931 | 122.4289 | 122.4655 | 122.5296 | -0.14648 | 122.3877 | 122.4106 | 122.525 | -0.032043
2227.9219 | 122.6486 | -122.3877 | 0.086975 | 0.013046 | 0.0017816 | 0.073217 | 0.025229 | -0.068896 | -0.02844 | -0.00027975 | 0.014954 | 0.044987 | 0.022736 | -0.010002 | -0.0041956 | 0.015872 | 0.045776 | 0.082397 | 0.10529 | 0.1236 | 0.086975 | 0.073242 | -0.036621 | 0.036621 | 0.11902 | 0.004578 | 0.022888 | 0.045776 | 0.1236 | 0.050354 | 122.4609 | 122.3511 | 0 | 122.4701 | 122.5113 | 0.16022 | -0.041199 | 122.5113 | 122.438 | -0.064087 | 122.4243 | 122.3923 | -0.045776 | -0.041199 | 122.4747 | 122.4335 | 122.493 | -0.1236 | 122.4106 | 122.4335 | 122.5067 | -0.036621
2229.6406 | 122.5845 | -122.3831 | 0.11902 | 0.0054168 | 0.00071339 | 0.069158 | 0.03121 | -0.068682 | -0.025662 | -0.00070715 | 0.014954 | 0.043705 | 0.026581 | -0.010429 | -0.00505 | 0.010745 | 0.091553 | 0.13275 | 0.16937 | 0.16479 | 0.059509 | 0.10071 | -0.036621 | 0.09613 | 0.18768 | 0.054932 | 0.009155 | 0.054932 | 0.14648 | 0.064087 | 122.4838 | 122.3465 | -0.05951 | 122.5159 | 122.5479 | 0.20142 | -0.027466 | 122.5296 | 122.4472 | -0.10986 | 122.4792 | 122.438 | -0.009155 | -0.064087 | 122.4426 | 122.4747 | 122.5525 | -0.15564 | 122.3923 | 122.438 | 122.5708 | -0.054932
2231.3594 | 122.6532 | -122.3694 | 0.10071 | -0.0022127 | -0.00014101 | 0.069799 | 0.028433 | -0.067828 | -0.024381 | -0.0015616 | 0.022583 | 0.044346 | 0.024659 | -0.010429 | -0.0078272 | 0.010745 | 0.13733 | 0.16937 | 0.1831 | 0.17395 | 0.07782 | 0.082397 | -0.041199 | 0.11902 | 0.20599 | 0.073242 | 0.009155 | 0.041199 | 0.12817 | 0.07782 | 122.4518 | 122.3282 | -0.022888 | 122.5388 | 122.5433 | 0.21515 | 0.036621 | 122.4976 | 122.4472 | -0.091553 | 122.4884 | 122.4426 | -0.004578 | -0.059509 | 122.4472 | 122.5067 | 122.5525 | -0.14191 | 122.3785 | 122.4106 | 122.5754 | -0.022888
2233.1406 | 122.644 | -122.3511 | 0.10071 | 0.0054168 | 0.00071339 | 0.068517 | 0.025015 | -0.068896 | -0.020749 | 0.0014292 | 0.0073242 | 0.050968 | 0.02295 | -0.0095745 | -0.0027002 | 0.011386 | 0.050354 | -0.009155 | 0 | 0.059509 | 0.1236 | 0.054932 | -0.073242 | 0.009155 | 0.018311 | -0.059509 | 0.059509 | 0.09613 | 0.091553 | 0.045776 | 122.406 | 122.2778 | 0.022888 | 122.3419 | 122.4106 | 0.13275 | -0.050354 | 122.4426 | 122.3969 | -0.041199 | 122.3602 | 122.2916 | -0.10528 | -0.004578 | 122.4747 | 122.4014 | 122.3511 | -0.17395 | 122.4106 | 122.4472 | 122.3694 | -0.054932
2234.9219 | 122.5754 | -122.406 | 0.11444 | 0.013046 | -0.00056821 | 0.071935 | 0.028433 | -0.067614 | -0.022672 | 0.0012154 | 0.0073242 | 0.04755 | 0.027649 | -0.011283 | -0.0052636 | 0.012882 | 0.004578 | 0.004578 | 0.022888 | 0.07782 | 0.11444 | 0.064087 | -0.091553 | -0.004578 | 0.050354 | -0.073242 | 0.064087 | 0.07782 | 0.082397 | 0.036621 | 122.4701 | 122.3145 | 0 | 122.4106 | 122.4838 | 0.16937 | -0.10986 | 122.4884 | 122.4426 | -0.050354 | 122.4014 | 122.3328 | -0.10986 | -0.036621 | 122.5204 | 122.4106 | 122.4289 | -0.20599 | 122.4701 | 122.4838 | 122.4564 | -0.07782
2236.7188 | 122.6669 | -122.3557 | 0.10071 | 0.013046 | 0.0024224 | 0.070654 | 0.031638 | -0.069964 | -0.027799 | -0.00049335 | 0.014954 | 0.045414 | 0.026795 | -0.01342 | -0.0074 | 0.012668 | 0.11444 | 0.16937 | 0.16479 | 0.16022 | 0.086975 | 0.07782 | -0.045776 | 0.10529 | 0.22888 | 0.086975 | 0.018311 | 0.041199 | 0.14191 | 0.059509 | 122.4335 | 122.3099 | -0.013733 | 122.525 | 122.5159 | 0.20599 | 0.013733 | 122.4976 | 122.4152 | -0.082397 | 122.4609 | 122.4426 | 0.027466 | -0.059509 | 122.4426 | 122.4701 | 122.5204 | -0.14648 | 122.374 | 122.3969 | 122.5845 | -0.041199
2238.5156 | 122.6486 | -122.3694 | 0.09613 | 0.020676 | 0.0019952 | 0.070013 | 0.02822 | -0.067614 | -0.023953 | 0.00078825 | 0.014954 | 0.046269 | 0.026154 | -0.011711 | -0.0063318 | 0.013522 | 0.11444 | 0.12817 | 0.15106 | 0.17395 | 0.054932 | 0.10986 | -0.036621 | 0.14191 | 0.17853 | 0.054932 | 0.027466 | 0.022888 | 0.14648 | 0.068665 | 122.4792 | 122.3328 | -0.041198 | 122.4976 | 122.5433 | 0.21057 | 0.018311 | 122.5159 | 122.438 | -0.068664 | 122.5113 | 122.4243 | -0.013733 | -0.073242 | 122.4243 | 122.4838 | 122.5204 | -0.13275 | 122.3969 | 122.3923 | 122.5479 | -0.027465
2240.25 | 122.6715 | -122.3465 | 0.09613 | 0.0054168 | 0.00028619 | 0.071722 | 0.026511 | -0.064837 | -0.022031 | 0.0022836 | 0.014954 | 0.047978 | 0.025513 | -0.010002 | -0.0035546 | 0.010745 | 0.10071 | 0.10529 | 0.11444 | 0.14191 | 0.091553 | 0.086975 | -0.041199 | 0.13275 | 0.15564 | 0.050354 | 0.022888 | 0.036621 | 0.13733 | 0.07782 | 122.4335 | 122.3053 | -0.004577 | 122.4518 | 122.4884 | 0.18311 | 0.004578 | 122.4838 | 122.4243 | -0.073242 | 122.4792 | 122.3969 | -0.027466 | -0.059509 | 122.4381 | 122.4472 | 122.4609 | -0.13733 | 122.3694 | 122.3831 | 122.5021 | -0.01831
2242.0312 | 122.5937 | -122.406 | 0.11902 | -0.0022127 | -0.00099541 | 0.068304 | 0.025656 | -0.0674 | -0.022672 | -0.001348 | 0.022583 | 0.049473 | 0.028504 | -0.010643 | -0.0046228 | 0.011173 | 0.013733 | -0.009155 | 0.022888 | 0.091553 | 0.12817 | 0.054932 | -0.091553 | 0.013733 | 0.068665 | -0.073242 | 0.068665 | 0.086975 | 0.082397 | 0.027466 | 122.4609 | 122.3145 | 0.009155 | 122.3969 | 122.4976 | 0.18311 | -0.10529 | 122.4884 | 122.4335 | -0.050354 | 122.4197 | 122.3328 | -0.10071 | -0.032044 | 122.5342 | 122.4197 | 122.4289 | -0.21057 | 122.4747 | 122.493 | 122.4747 | -0.091553
2243.7969 | 122.6532 | -122.3465 | 0.10986 | 0.013046 | 0.0026362 | 0.070013 | 0.030783 | -0.070177 | -0.02844 | 0.00078825 | 0.014954 | 0.046055 | 0.027008 | -0.01107 | -0.0086816 | 0.012668 | 0.050354 | 0.073242 | 0.10986 | 0.1236 | 0.073242 | 0.082397 | -0.054932 | 0.059509 | 0.1236 | 0.018311 | 0.022888 | 0.054932 | 0.1236 | 0.064087 | 122.4289 | 122.2916 | -0.036621 | 122.4197 | 122.4701 | 0.17853 | -0.059509 | 122.4701 | 122.4106 | -0.086975 | 122.406 | 122.3648 | -0.045776 | -0.054931 | 122.4197 | 122.3969 | 122.4564 | -0.16479 | 122.3694 | 122.4014 | 122.4701 | -0.045776
2245.5312 | 122.6303 | -122.3694 | 0.09613 | 0.0054168 | 0.0017816 | 0.070867 | 0.027365 | -0.070605 | -0.023953 | 0.0029244 | -0.0003053 | 0.046696 | 0.028931 | -0.010429 | -0.0044092 | 0.012454 | 0.11444 | 0.13275 | 0.16479 | 0.15106 | 0.064087 | 0.091553 | -0.050354 | 0.11444 | 0.15564 | 0.050354 | 0.013733 | 0.041199 | 0.12817 | 0.068665 | 122.4609 | 122.319 | -0.032043 | 122.5021 | 122.5204 | 0.20142 | 0.018311 | 122.4976 | 122.438 | -0.082397 | 122.4838 | 122.4197 | -0.018311 | -0.054931 | 122.4335 | 122.4838 | 122.5342 | -0.14648 | 122.3831 | 122.4106 | 122.525 | -0.027465
2247.3125 | 122.5891 | -122.3694 | 0.13733 | 0.0054168 | 0.00049979 | 0.067236 | 0.02822 | -0.06505 | -0.020963 | 0.0018564 | 0.014954 | 0.052464 | 0.029999 | -0.0097883 | -0.0029138 | 0.011173 | 0.041199 | 0.004578 | 0.041199 | 0.09613 | 0.10529 | 0.054932 | -0.07782 | 0.068665 | 0.091553 | -0.036621 | 0.054932 | 0.082397 | 0.10071 | 0.036621 | 122.4243 | 122.2916 | -0.032043 | 122.374 | 122.4655 | 0.17395 | -0.09613 | 122.4701 | 122.406 | -0.082397 | 122.438 | 122.3328 | -0.073242 | -0.054932 | 122.4747 | 122.4106 | 122.4106 | -0.21515 | 122.4243 | 122.4518 | 122.4609 | -0.10071
2249.0938 | 122.612 | -122.3785 | 0.11902 | 0.013046 | 0.00071339 | 0.066595 | 0.026297 | -0.067828 | -0.021817 | 0.0024972 | 0.0073242 | 0.054386 | 0.029999 | -0.010215 | -0.0048364 | 0.013522 | 0.027466 | -0.013733 | 0 | 0.059509 | 0.13275 | 0.050354 | -0.064087 | 0.018311 | 0.045776 | -0.064087 | 0.050354 | 0.07782 | 0.10071 | 0.041199 | 122.4289 | 122.3145 | 0.013732 | 122.3648 | 122.438 | 0.1236 | -0.091553 | 122.4792 | 122.4197 | -0.068665 | 122.3969 | 122.3145 | -0.10529 | -0.041199 | 122.5113 | 122.406 | 122.3785 | -0.18311 | 122.4289 | 122.4564 | 122.4243 | -0.07782
2250.875 | 122.5525 | -122.3969 | 0.14648 | 0.0054168 | -0.00014101 | 0.06809 | 0.028006 | -0.0674 | -0.027371 | -0.0017752 | -0.0003053 | 0.048832 | 0.031067 | -0.0082929 | -0.0088952 | 0.014163 | 0.013733 | 0.027466 | 0.059509 | 0.10986 | 0.091553 | 0.027466 | -0.082397 | 0.018311 | 0.091553 | -0.054932 | 0.068665 | 0.082397 | 0.09613 | 0.045776 | 122.4243 | 122.3145 | -0.054931 | 122.4243 | 122.5067 | 0.19226 | -0.13275 | 122.493 | 122.4426 | -0.077819 | 122.4152 | 122.3419 | -0.10071 | -0.064087 | 122.4884 | 122.4106 | 122.4564 | -0.22888 | 122.4655 | 122.4792 | 122.4884 | -0.10071
2252.6562 | 122.5891 | -122.3602 | 0.15106 | 0.0054168 | 0.0013544 | 0.070013 | 0.025656 | -0.066546 | -0.022885 | 0.00207 | 0.0073242 | 0.051396 | 0.029358 | -0.010856 | -0.0031274 | 0.0096771 | 0.032043 | 0.027466 | 0.036621 | 0.09613 | 0.10529 | 0.045776 | -0.050354 | 0.059509 | 0.10529 | -0.027466 | 0.054932 | 0.091553 | 0.10529 | 0.041199 | 122.406 | 122.3099 | -0.045776 | 122.3877 | 122.4564 | 0.14648 | -0.11902 | 122.4655 | 122.4014 | -0.09613 | 122.4197 | 122.3328 | -0.068665 | -0.059509 | 122.4655 | 122.3923 | 122.3969 | -0.20142 | 122.4152 | 122.4518 | 122.4655 | -0.10986
2254.3906 | 122.5616 | -122.3648 | 0.14648 | 0.0054168 | -0.0012092 | 0.071722 | 0.02587 | -0.065264 | -0.024167 | 0.00036105 | 0.0073242 | 0.050541 | 0.029145 | -0.010856 | -0.0065454 | 0.012027 | -0.018311 | 0.004578 | 0.036621 | 0.073242 | 0.10529 | 0.059509 | -0.086975 | -0.013733 | 0.064087 | -0.059509 | 0.059509 | 0.064087 | 0.10529 | 0.027466 | 122.4243 | 122.2778 | -0.041198 | 122.3694 | 122.438 | 0.16022 | -0.16479 | 122.4701 | 122.3923 | -0.086975 | 122.3511 | 122.3053 | -0.086975 | -0.082397 | 122.4701 | 122.3465 | 122.4014 | -0.23346 | 122.4243 | 122.4289 | 122.4289 | -0.11902
2256.1875 | 122.5891 | -122.3694 | 0.11902 | 0.0054168 | 0.001568 | 0.070654 | 0.029288 | -0.066759 | -0.026731 | 0.0010018 | 0.0073242 | 0.047764 | 0.029145 | -0.012352 | -0.006759 | 0.012454 | 0.091553 | 0.15106 | 0.16479 | 0.16937 | 0.064087 | 0.091553 | -0.036621 | 0.10986 | 0.2243 | 0.082397 | 0.022888 | 0.050354 | 0.14648 | 0.07782 | 122.4609 | 122.3328 | -0.054932 | 122.5204 | 122.5388 | 0.20599 | -0.027466 | 122.5159 | 122.4472 | -0.096131 | 122.4792 | 122.4518 | 0.004577 | -0.068665 | 122.4335 | 122.4609 | 122.5342 | -0.15564 | 122.3923 | 122.4197 | 122.5937 | -0.041199
2257.9688 | 122.6669 | -122.3511 | 0.10071 | -0.0022127 | 0.0030634 | 0.072149 | 0.029501 | -0.070177 | -0.028653 | -0.001348 | 0.0073242 | 0.047978 | 0.026795 | -0.012565 | -0.0080408 | 0.014804 | 0.027466 | 0.073242 | 0.086975 | 0.10986 | 0.086975 | 0.082397 | -0.054932 | 0.064087 | 0.15564 | 0.045776 | 0.036621 | 0.064087 | 0.13275 | 0.068665 | 122.4335 | 122.2961 | -0.013733 | 122.4243 | 122.4609 | 0.16479 | -0.073242 | 122.4838 | 122.4197 | -0.064087 | 122.4152 | 122.3969 | -0.022889 | -0.036621 | 122.438 | 122.3785 | 122.438 | -0.15564 | 122.3877 | 122.4152 | 122.5067 | -0.032043
2259.6875 | 122.5937 | -122.3465 | 0.13275 | 0.0054168 | 7.2586e-05 | 0.07044 | 0.026724 | -0.067614 | -0.020535 | 0.00014745 | 0.0073242 | 0.053746 | 0.030213 | -0.0095745 | -0.0037684 | 0.010532 | 0.013733 | 0.004578 | 0.022888 | 0.10986 | 0.11444 | 0.041199 | -0.068665 | 0.027466 | 0.091553 | -0.068665 | 0.082397 | 0.082397 | 0.11444 | 0.045776 | 122.3877 | 122.2778 | -0.01831 | 122.3511 | 122.4564 | 0.17853 | -0.11902 | 122.4609 | 122.3923 | -0.050354 | 122.374 | 122.2778 | -0.11444 | -0.050354 | 122.4609 | 122.3602 | 122.3694 | -0.20142 | 122.4289 | 122.4289 | 122.4381 | -0.086975
2261.4844 | 122.6166 | -122.3511 | 0.11902 | 0.020676 | 0.0028498 | 0.069372 | 0.021597 | -0.067828 | -0.024594 | 0.00207 | 0.0073242 | 0.052037 | 0.028504 | -0.011283 | -0.0046228 | 0.012027 | 0.11902 | 0.1236 | 0.16022 | 0.16479 | 0.073242 | 0.09613 | -0.032043 | 0.13733 | 0.1831 | 0.073242 | 0.018311 | 0.045776 | 0.14648 | 0.091553 | 122.4472 | 122.319 | -0.045777 | 122.4747 | 122.5159 | 0.19684 | 0 | 122.4976 | 122.4426 | -0.10071 | 122.4884 | 122.4243 | -0.018311 | -0.073243 | 122.4243 | 122.4701 | 122.5113 | -0.15106 | 122.3694 | 122.3969 | 122.5342 | -0.027466
2263.2031 | 122.5708 | -122.3328 | 0.1236 | 0.0054168 | -0.00014101 | 0.067663 | 0.026938 | -0.066973 | -0.022244 | 0.00057465 | 0.014954 | 0.059086 | 0.036194 | -0.0095745 | -0.001632 | 0.012454 | 0.009155 | -0.022888 | 0.004578 | 0.07782 | 0.13275 | 0.064087 | -0.07782 | 0.032043 | 0.032043 | -0.054932 | 0.10529 | 0.086975 | 0.1236 | 0.059509 | 122.3969 | 122.2549 | 0.009155 | 122.3099 | 122.4106 | 0.15564 | -0.11444 | 122.4564 | 122.3923 | -0.01831 | 122.3648 | 122.2778 | -0.11444 | -0.036621 | 122.4655 | 122.3419 | 122.3373 | -0.20142 | 122.4381 | 122.4197 | 122.3648 | -0.064087
2264.9844 | 122.5983 | -122.3099 | 0.15564 | 0.0054168 | 0.0045588 | 0.074072 | 0.02822 | -0.06975 | -0.025876 | 0.0014292 | 0.022583 | 0.062077 | 0.042176 | -0.014701 | -0.006759 | 0.014163 | 0.10529 | 0.13733 | 0.17395 | 0.15106 | 0.068665 | 0.10986 | -0.022888 | 0.14191 | 0.20599 | 0.086975 | 0.073242 | 0.086975 | 0.1831 | 0.10529 | 122.4197 | 122.287 | -0.086975 | 122.4472 | 122.4609 | 0.17395 | -0.050354 | 122.493 | 122.4152 | -0.082398 | 122.4518 | 122.3969 | -0.018311 | -0.068665 | 122.3785 | 122.4152 | 122.4838 | -0.17853 | 122.3831 | 122.3969 | 122.5159 | -0.050354
2266.7656 | 122.5525 | -121.9528 | 0.4303 | 0.0054168 | 7.2586e-05 | 0.072149 | 0.02886 | -0.068255 | -0.028653 | -0.0024162 | 0.0073242 | 0.15137 | 0.13574 | -0.01641 | -0.0086816 | 0.016086 | 0.064087 | 0.07782 | 0.10529 | 0.10529 | 0.086975 | 0.10071 | -0.013733 | 0.31586 | 0.42572 | 0.32501 | 0.31128 | 0.33875 | 0.41199 | 0.36163 | 122.0535 | 121.9391 | -0.34332 | 122.0306 | 122.0581 | 0.11902 | -0.36621 | 122.3648 | 122.3145 | -0.11902 | 122.2687 | 122.2778 | -0.036621 | -0.091553 | 122.0398 | 122.0169 | 122.0581 | -0.44403 | 122.2641 | 122.2916 | 122.3785 | -0.068665
2268.5625 | 120.3781 | -91.1728 | 28.5919 | 0.0054168 | 0.0013544 | 0.070226 | 0.029715 | -0.069109 | -0.023313 | -0.0026298 | -0.0003053 | 7.0044 | 7.0272 | -0.25246 | -0.0086816 | 0.21924 | 0.25635 | 0.26093 | 0.27466 | 0.31128 | 0.33875 | 0.28839 | 0.15564 | 23.2315 | 23.5428 | 23.7854 | 27.2186 | 27.3788 | 9.1278 | 9.0179 | 91.4612 | 91.3284 | -28.2532 | 91.4337 | 91.4841 | 0.15564 | -28.3356 | 100.3006 | 100.1907 | -1.3733 | 114.4043 | 114.9582 | 14.7675 | -1.2131 | 91.5115 | 91.4291 | 91.4474 | -28.4363 | 118.3914 | 118.5516 | 114.7156 | -19.574
2270.3438 | 119.6548 | -104.686 | 14.6942 | 0.0054168 | 0.0013544 | 0.069372 | 0.028433 | -0.066973 | -0.022672 | -0.0017752 | 0.014954 | 7.0044 | 7.0272 | -0.35842 | -0.0093226 | 0.33908 | 0.29755 | 0.26093 | 0.30212 | 0.36621 | 0.38452 | 0.32501 | 0.19684 | 6.8253 | 7.4753 | 7.3608 | 12.0392 | 12.0483 | 7.283 | 7.2693 | 105.011 | 104.8828 | -14.3097 | 104.9469 | 105.0522 | 0.16937 | -14.3967 | 111.969 | 111.9553 | -2.655 | 111.5112 | 112.0468 | 0.091553 | -2.6459 | 105.0705 | 104.9835 | 104.9881 | -14.4974 | 116.7252 | 116.7343 | 112.1613 | -7.4249
2272.0625 | 119.9066 | -91.0217 | 28.8071 | 0.0054168 | 0.0019952 | 0.069799 | 0.026511 | -0.066973 | -0.023313 | -6.615e-05 | -0.0003053 | 7.0044 | 7.0272 | -0.56564 | -0.0059046 | 0.54096 | 0.1831 | 0.1236 | 0.16937 | 0.23804 | 0.26093 | 0.1831 | 0.059509 | 25.1266 | 24.9893 | 24.7604 | 27.6672 | 27.6443 | 9.1324 | 9.0088 | 91.2048 | 91.0812 | -28.5461 | 91.1453 | 91.2598 | 0.17853 | -28.624 | 100.1541 | 100.0305 | -1.1398 | 116.1484 | 115.7822 | 15.7516 | -1.1627 | 91.2827 | 91.2048 | 91.1911 | -28.7476 | 118.689 | 118.6661 | 116.011 | -19.7983
2273.8438 | 121.0831 | -120.7764 | 0.14191 | 0.013046 | -0.00014101 | 0.069372 | 0.026938 | -0.068682 | -0.029935 | 0.00036105 | 0.0073242 | 0.21524 | 0.20261 | -0.049522 | -0.0074 | 0.020358 | 0.10529 | 0.14191 | 0.19226 | 0.16022 | 0.068665 | 0.10071 | -0.036621 | 0.15106 | 0.23804 | 0.091553 | 0.059509 | 0.10986 | 0.16022 | 0.10529 | 120.8771 | 120.7397 | -0.073242 | 120.9183 | 120.9366 | 0.19684 | -0.036621 | 120.9366 | 120.8817 | -0.082398 | 120.9274 | 120.8679 | -0.013733 | -0.032044 | 120.845 | 120.8817 | 120.9686 | -0.17853 | 120.8359 | 120.8862 | 121.0144 | -0.036621
2275.625 | 121.4172 | -120.9274 | 0.25635 | 0.0054168 | 0.0022088 | 0.071935 | 0.026938 | -0.067828 | -0.028653 | -0.00049335 | 0.0073242 | 0.31479 | 0.30023 | -0.05294 | -0.0074 | 0.020999 | 0.059509 | 0.082397 | 0.11444 | 0.09613 | 0.082397 | 0.086975 | -0.022888 | 0.10529 | 0.1831 | 0.073242 | 0.15106 | 0.16022 | 0.18768 | 0.1236 | 121.0144 | 120.9045 | -0.17395 | 121.0098 | 121.0236 | 0.11902 | -0.19684 | 121.1151 | 121.051 | -0.10529 | 121.0327 | 121.0007 | -0.050354 | -0.096131 | 121.0098 | 120.9869 | 121.0419 | -0.27924 | 121.0785 | 121.0876 | 121.1105 | -0.13275
2277.4062 | 121.2341 | -120.5933 | 0.60425 | 0.013046 | 0.00049979 | 0.068517 | 0.027365 | -0.067187 | -0.027799 | -0.00092075 | 0.014954 | 0.73413 | 0.72107 | -0.064262 | -0.0059046 | 0.033176 | 0.10071 | 0.12817 | 0.15564 | 0.17395 | 0.068665 | 0.09613 | -0.032043 | 0.28381 | 0.37537 | 0.23804 | 0.38452 | 0.41657 | 0.3479 | 0.27466 | 120.6894 | 120.5612 | -0.53558 | 120.7214 | 120.7672 | 0.20599 | -0.50354 | 120.9412 | 120.8679 | -0.21973 | 120.8771 | 120.8313 | -0.036621 | -0.18768 | 120.6619 | 120.694 | 120.7489 | -0.63629 | 120.9778 | 121.0098 | 120.9686 | -0.32959
2279.1875 | 121.4767 | -121.0968 | 0.23804 | 0.0054168 | 0.0030634 | 0.068304 | 0.022665 | -0.067187 | -0.020963 | 0.00036105 | -0.0003053 | 0.2898 | 0.27033 | -0.051017 | -0.0046228 | 0.019717 | 0.032043 | -0.032043 | 0.004578 | 0.07782 | 0.11444 | 0.050354 | -0.064087 | 0.091553 | 0.086975 | -0.018311 | 0.17853 | 0.19684 | 0.16479 | 0.10071 | 121.1472 | 121.0327 | -0.1236 | 121.0648 | 121.1746 | 0.14191 | -0.20599 | 121.2616 | 121.1975 | -0.059509 | 121.1884 | 121.0785 | -0.11902 | -0.041199 | 121.2112 | 121.1288 | 121.1014 | -0.30212 | 121.2753 | 121.2936 | 121.1838 | -0.13733
2280.8906 | 120.4102 | -119.8791 | 0.46234 | 0.013046 | 0.001568 | 0.069799 | 0.029929 | -0.068682 | -0.026517 | 0.00036105 | 0.0073242 | 0.56943 | 0.55594 | -0.057853 | -0.0088952 | 0.027194 | 0.11444 | 0.13733 | 0.17853 | 0.16022 | 0.073242 | 0.091553 | -0.027466 | 0.25177 | 0.33417 | 0.19684 | 0.28839 | 0.29755 | 0.26093 | 0.2243 | 119.9707 | 119.8517 | -0.3891 | 120.0165 | 120.0394 | 0.18768 | -0.3479 | 120.1401 | 120.1035 | -0.17395 | 120.1309 | 120.076 | -0.027466 | -0.1648 | 119.9524 | 119.9936 | 120.0577 | -0.48981 | 120.1675 | 120.1767 | 120.2133 | -0.23804
2282.6875 | 120.9915 | -120.6299 | 0.091553 | -0.0022127 | 0.0030634 | 0.072149 | 0.030783 | -0.070818 | -0.030149 | -0.0011344 | -0.0003053 | 0.089848 | 0.078064 | -0.046745 | -0.0080408 | 0.015445 | 0.073242 | 0.073242 | 0.11902 | 0.14191 | 0.068665 | 0.073242 | -0.050354 | 0.082397 | 0.15564 | 0.050354 | 0.018311 | 0.018311 | 0.10986 | 0.054932 | 120.7031 | 120.5795 | -0.022888 | 120.7031 | 120.7718 | 0.19226 | -0.018311 | 120.7397 | 120.6848 | -0.073242 | 120.7123 | 120.6802 | -0.004578 | -0.073242 | 120.6985 | 120.7031 | 120.7489 | -0.14191 | 120.6482 | 120.6482 | 120.7855 | -0.036621
2284.4688 | 119.5358 | -117.9291 | 1.5381 | 0.0054168 | 0.0019952 | 0.071081 | 0.024588 | -0.067187 | -0.019254 | 0.00057465 | 0.0073242 | 2.0716 | 2.0814 | -0.093528 | -0.0024866 | 0.063083 | 0.041199 | -0.027466 | 0.022888 | 0.091553 | 0.1236 | 0.073242 | -0.059509 | 0.66376 | 0.67291 | 0.57678 | 1.1673 | 1.1993 | 0.76904 | 0.70953 | 118.0023 | 117.8696 | -1.4145 | 117.9016 | 118.0206 | 0.15106 | -1.4969 | 118.6981 | 118.6386 | -0.37079 | 118.5928 | 118.5059 | -0.13275 | -0.33875 | 118.0527 | 117.9703 | 117.952 | -1.5976 | 119.0964 | 119.1284 | 118.602 | -0.82855
2286.25 | 120.9732 | -120.0119 | 0.77362 | 0.0054168 | 0.0028498 | 0.069799 | 0.030997 | -0.06975 | -0.029508 | 0.00014745 | 0.014954 | 0.98151 | 0.9772 | -0.067894 | -0.008468 | 0.040012 | 0.068665 | 0.091553 | 0.1236 | 0.12817 | 0.086975 | 0.086975 | -0.009155 | 0.3067 | 0.36163 | 0.28381 | 0.50354 | 0.54016 | 0.42114 | 0.3479 | 120.0989 | 120.0027 | -0.68665 | 120.1035 | 120.1401 | 0.13733 | -0.70496 | 120.433 | 120.3598 | -0.27008 | 120.3186 | 120.2957 | -0.064087 | -0.23346 | 120.0989 | 120.0806 | 120.1355 | -0.78278 | 120.5154 | 120.5521 | 120.3735 | -0.42572
2288.0469 | 120.6482 | -119.9799 | 0.41657 | 0.013046 | 0.0011408 | 0.06809 | 0.026083 | -0.069964 | -0.023526 | 0.00078825 | 0.014954 | 0.49936 | 0.47775 | -0.056144 | -0.0037684 | 0.025058 | 0.12817 | 0.11902 | 0.14191 | 0.16022 | 0.082397 | 0.091553 | -0.027466 | 0.28839 | 0.32501 | 0.23804 | 0.27466 | 0.28839 | 0.32044 | 0.25177 | 120.0714 | 119.9524 | -0.33417 | 120.0989 | 120.1401 | 0.18768 | -0.28839 | 120.3003 | 120.2316 | -0.14191 | 120.2682 | 120.2179 | -0.013733 | -0.12817 | 120.0623 | 120.108 | 120.1218 | -0.44403 | 120.2545 | 120.2682 | 120.3049 | -0.1648
2289.7656 | 115.3198 | -113.7405 | 1.442 | 0.020676 | -0.0014228 | 0.067449 | 0.031638 | -0.068041 | -0.025022 | 0.00036105 | 0.014954 | 1.8407 | 1.84 | -0.08477 | -0.0082544 | 0.053684 | 0.032043 | 0.032043 | 0.045776 | 0.073242 | 0.14191 | 0.050354 | -0.050354 | 0.6134 | 0.75073 | 0.63171 | 1.149 | 1.1673 | 0.80566 | 0.73242 | 113.7909 | 113.6902 | -1.3 | 113.7726 | 113.8138 | 0.1236 | -1.4099 | 114.5462 | 114.473 | -0.29297 | 114.3539 | 114.3723 | -0.10071 | -0.27466 | 113.8824 | 113.7726 | 113.7863 | -1.4923 | 114.8895 | 114.9078 | 114.4913 | -0.70953
2291.5469 | 117.2104 | -78.7308 | 38.8824 | 0.013046 | -0.00035461 | 0.066808 | 0.027152 | -0.06975 | -0.020749 | 0.00036105 | 0.0073242 | 7.0044 | 7.0272 | -0.66219 | -0.003982 | 0.63538 | 0.32044 | 0.30212 | 0.30212 | 0.35248 | 0.32959 | 0.29755 | 0.16479 | 30.4871 | 30.304 | 30.5191 | 34.8312 | 34.8633 | 9.1278 | 9.0179 | 79.0283 | 78.8956 | -38.5529 | 79.0329 | 79.0833 | 0.18768 | -38.562 | 87.8586 | 87.7487 | -4.0512 | 109.2178 | 109.2499 | 21.5012 | -4.0192 | 79.0604 | 79.0512 | 79.0329 | -38.7177 | 113.562 | 113.5941 | 109.0347 | -29.8645
2293.2656 | 118.3411 | -78.7857 | 39.1891 | -0.0022127 | 0.0022088 | 0.070013 | 0.023947 | -0.067828 | -0.020963 | 0.00078825 | 0.0073242 | 7.0044 | 7.0272 | -0.71304 | -0.0063318 | 0.67639 | 0.2243 | 0.24261 | 0.2655 | 0.31128 | 0.29297 | 0.26093 | 0.13733 | 32.4692 | 32.2311 | 32.2906 | 36.3464 | 36.3647 | 9.1232 | 9.0179 | 79.0466 | 78.923 | -38.8962 | 79.0283 | 79.097 | 0.17395 | -38.9648 | 87.9089 | 87.8037 | -2.8427 | 111.2549 | 111.0764 | 23.2727 | -2.8244 | 79.0787 | 79.01 | 79.0512 | -39.0518 | 115.1321 | 115.1505 | 111.0168 | -30.1712
2295.0469 | 119.9799 | -119.8975 | 0.11902 | 0.0054168 | 0.0024224 | 0.07044 | 0.026511 | -0.06975 | -0.022672 | 0.00078825 | 0.0073242 | 0.028324 | 0.0069278 | -0.040336 | -0.0027002 | 0.014163 | -0.013733 | -0.032043 | 0.013733 | 0.073242 | 0.11444 | 0.050354 | -0.07782 | -0.032043 | 0.009155 | -0.15106 | 0.018311 | 0.059509 | 0.07782 | 0.004578 | 119.9478 | 119.8196 | -0.004578 | 119.8654 | 119.9707 | 0.15106 | -0.13275 | 119.9753 | 119.902 | -0.10071 | 119.8654 | 119.7464 | -0.15564 | -0.05951 | 120.0119 | 119.8837 | 119.9112 | -0.19684 | 119.9158 | 119.957 | 119.9066 | -0.11444
2296.8438 | 120.3598 | -120.0851 | 0.068665 | -0.0022127 | 0.0045588 | 0.071722 | 0.025656 | -0.067828 | -0.026517 | -0.00070715 | 0.014954 | 0.027897 | 0.0052188 | -0.044822 | -0.0020594 | 0.016086 | 0.073242 | 0.10529 | 0.13275 | 0.14648 | 0.050354 | 0.091553 | -0.041199 | 0.07782 | 0.13733 | 0.004578 | -0.018311 | 0.009155 | 0.09613 | 0.041199 | 120.1767 | 120.0439 | -0.018311 | 120.1904 | 120.2316 | 0.18768 | 0.004577 | 120.1813 | 120.1263 | -0.086976 | 120.163 | 120.0897 | -0.036621 | -0.05951 | 120.1355 | 120.1584 | 120.2179 | -0.10986 | 120.0668 | 120.0943 | 120.2225 | -0.027466
2298.6406 | 120.4926 | -120.1767 | 0.054932 | 0.020676 | 0.001568 | 0.070226 | 0.030783 | -0.067187 | -0.030576 | -6.615e-05 | 0.0073242 | 0.025761 | 0.0054324 | -0.046959 | -0.0088952 | 0.015872 | 0.041199 | 0.091553 | 0.12817 | 0.12817 | 0.073242 | 0.073242 | -0.050354 | 0.045776 | 0.14648 | 0.027466 | 0 | 0.018311 | 0.091553 | 0.032043 | 120.2499 | 120.1263 | 0.01831 | 120.2683 | 120.3049 | 0.17853 | -0.013733 | 120.2683 | 120.2087 | -0.054932 | 120.2225 | 120.2042 | -0.004577 | -0.036621 | 120.2499 | 120.2179 | 120.3049 | -0.10529 | 120.1767 | 120.195 | 120.3232 | -0.022889
2300.3594 | 120.5063 | -120.2774 | 0.054932 | -0.0022127 | 7.2586e-05 | 0.074926 | 0.027579 | -0.072527 | -0.028226 | 0.00014745 | 0.014954 | 0.027897 | 0.004578 | -0.047599 | -0.00505 | 0.0163 | 0.050354 | 0.073242 | 0.10986 | 0.10986 | 0.07782 | 0.086975 | -0.041199 | 0.013733 | 0.10071 | -0.027466 | -0.004578 | 0.009155 | 0.091553 | 0.027466 | 120.3644 | 120.2362 | 0.022888 | 120.3506 | 120.3873 | 0.15106 | -0.004578 | 120.369 | 120.3049 | -0.05951 | 120.2911 | 120.2499 | -0.054932 | -0.045777 | 120.3552 | 120.3278 | 120.3873 | -0.096131 | 120.2728 | 120.2866 | 120.3781 | -0.027466
2302.1406 | 120.4742 | -120.3461 | 0.073242 | 0.013046 | 0.001568 | 0.068517 | 0.026511 | -0.068682 | -0.019895 | -6.615e-05 | 0.0073242 | 0.03516 | 0.0060732 | -0.04589 | -0.0041956 | 0.014377 | 0.022888 | -0.022888 | 0.013733 | 0.082397 | 0.11444 | 0.022888 | -0.050354 | -0.022888 | -0.009155 | -0.13275 | 0.013733 | 0.050354 | 0.07782 | 0.004578 | 120.369 | 120.2957 | 0.041199 | 120.3232 | 120.4285 | 0.13275 | -0.050354 | 120.4239 | 120.3506 | -0.059509 | 120.3232 | 120.2133 | -0.13733 | -0.022888 | 120.4605 | 120.369 | 120.3598 | -0.1236 | 120.3598 | 120.3964 | 120.3369 | -0.068664
2303.8438 | 120.5109 | -120.2225 | 0.21973 | -0.0022127 | 0.00028619 | 0.069158 | 0.02587 | -0.065264 | -0.019467 | 0.0018564 | 0.0073242 | 0.19388 | 0.16501 | -0.054008 | -0.0046228 | 0.022495 | 0.07782 | 0.050354 | 0.054932 | 0.1236 | 0.10071 | 0.059509 | -0.082397 | 0.1236 | 0.16479 | 0.032043 | 0.14191 | 0.15564 | 0.17395 | 0.091553 | 120.282 | 120.1401 | -0.11902 | 120.2728 | 120.3461 | 0.20599 | -0.14191 | 120.3964 | 120.314 | -0.07782 | 120.3461 | 120.2545 | -0.05951 | -0.064087 | 120.3232 | 120.3003 | 120.2774 | -0.30212 | 120.3644 | 120.3781 | 120.3873 | -0.12817
2305.6406 | 120.5475 | -120.2728 | 0.25177 | 0.0054168 | 0.001568 | 0.069372 | 0.025229 | -0.071673 | -0.021817 | 0.00057465 | 0.0073242 | 0.16867 | 0.14002 | -0.051445 | -0.0052636 | 0.022281 | -0.004578 | -0.041199 | 0.018311 | 0.054932 | 0.10986 | 0.045776 | -0.068665 | 0.050354 | 0.050354 | -0.059509 | 0.12817 | 0.14648 | 0.13733 | 0.073242 | 120.3186 | 120.2042 | -0.14191 | 120.2316 | 120.3278 | 0.1236 | -0.25635 | 120.4102 | 120.3461 | -0.1236 | 120.3232 | 120.2133 | -0.13275 | -0.10529 | 120.3827 | 120.2682 | 120.2911 | -0.32044 | 120.401 | 120.4193 | 120.3232 | -0.17853
2307.3594 | 120.6573 | -120.4605 | 0.068665 | 0.0054168 | 0.0013544 | 0.071722 | 0.024588 | -0.067614 | -0.029294 | -0.001348 | 0.014954 | 0.034947 | 0.0159 | -0.046745 | -0.006759 | 0.017368 | 0.064087 | 0.09613 | 0.1236 | 0.1236 | 0.068665 | 0.07782 | -0.050354 | 0.018311 | 0.09613 | -0.004578 | 0 | 0.018311 | 0.09613 | 0.050354 | 120.5383 | 120.4102 | 0 | 120.5566 | 120.5841 | 0.17395 | -0.004578 | 120.5566 | 120.5109 | -0.068665 | 120.4788 | 120.4559 | -0.054932 | -0.050354 | 120.5292 | 120.5246 | 120.5841 | -0.11902 | 120.4605 | 120.4788 | 120.5566 | -0.018311
2309.1406 | 120.6162 | -120.3461 | 0.21515 | 0.013046 | 0.0030634 | 0.07044 | 0.028006 | -0.067614 | -0.019895 | 0.00036105 | 0.014954 | 0.17658 | 0.15091 | -0.050376 | -0.0052636 | 0.022495 | -0.009155 | -0.054932 | -0.009155 | 0.054932 | 0.11444 | 0.050354 | -0.068665 | 0.032043 | 0.054932 | -0.054932 | 0.13275 | 0.14191 | 0.12817 | 0.064087 | 120.3964 | 120.2774 | -0.10071 | 120.2911 | 120.401 | 0.1236 | -0.2243 | 120.4742 | 120.4102 | -0.082398 | 120.3781 | 120.2911 | -0.11902 | -0.073242 | 120.4605 | 120.3369 | 120.3369 | -0.28381 | 120.4788 | 120.488 | 120.401 | -0.15106
2310.9219 | 120.7306 | -120.4926 | 0.054932 | 0.013046 | 0.0026362 | 0.071508 | 0.028647 | -0.0674 | -0.029508 | 0.0022836 | 0.0073242 | 0.035588 | 0.018463 | -0.047813 | -0.0080408 | 0.015872 | 0.086975 | 0.11902 | 0.17395 | 0.13733 | 0.054932 | 0.10071 | -0.032043 | 0.059509 | 0.12817 | 0.022888 | -0.013733 | 0.004578 | 0.10986 | 0.064087 | 120.5933 | 120.4605 | 0 | 120.6116 | 120.6299 | 0.16937 | 0.032043 | 120.6024 | 120.5566 | -0.068665 | 120.5521 | 120.5154 | -0.041199 | -0.050354 | 120.5475 | 120.5795 | 120.6665 | -0.086975 | 120.4788 | 120.4971 | 120.6207 | 0.009155
2312.6406 | 120.7809 | -120.5521 | 0.068665 | 0.0054168 | 0.0022088 | 0.071081 | 0.032278 | -0.068682 | -0.027585 | -0.0026298 | 0.0073242 | 0.037724 | 0.017823 | -0.046745 | -0.0078272 | 0.013309 | 0.091553 | 0.14191 | 0.16937 | 0.16479 | 0.064087 | 0.086975 | -0.032043 | 0.082397 | 0.1831 | 0.041199 | -0.004578 | 0.013733 | 0.10071 | 0.041199 | 120.639 | 120.52 | -0.004578 | 120.694 | 120.7169 | 0.19684 | 0.022888 | 120.6528 | 120.5933 | -0.073243 | 120.6345 | 120.5933 | 0 | -0.054932 | 120.6162 | 120.6436 | 120.7214 | -0.10071 | 120.5475 | 120.5658 | 120.7352 | -0.027466
2314.4375 | 120.8633 | -120.5933 | 0.07782 | 0.0054168 | 0.004986 | 0.071935 | 0.031638 | -0.070177 | -0.028012 | -0.004125 | -0.0003053 | 0.03751 | 0.0159 | -0.047599 | -0.008468 | 0.015659 | 0.036621 | 0.059509 | 0.10071 | 0.1236 | 0.082397 | 0.091553 | -0.041199 | 0.027466 | 0.10986 | -0.013733 | 0 | 0.022888 | 0.10986 | 0.050354 | 120.6848 | 120.5521 | 0.004577 | 120.6528 | 120.7169 | 0.16479 | -0.041199 | 120.7031 | 120.6436 | -0.07782 | 120.6207 | 120.5795 | -0.064087 | -0.054932 | 120.6757 | 120.6299 | 120.694 | -0.11902 | 120.5933 | 120.6161 | 120.7031 | -0.027466
2316.1562 | 120.8908 | -120.5841 | 0.064087 | -0.0022127 | 0.0030634 | 0.072149 | 0.025015 | -0.069964 | -0.025022 | -0.00049335 | 0.0073242 | 0.040501 | 0.017182 | -0.044181 | -0.0044092 | 0.01395 | 0.10986 | 0.073242 | 0.11444 | 0.13275 | 0.07782 | 0.07782 | -0.041199 | 0.09613 | 0.11444 | 0.004578 | -0.004578 | -0.004578 | 0.1236 | 0.054932 | 120.6619 | 120.5429 | 0.013733 | 120.6573 | 120.7169 | 0.17395 | 0.045776 | 120.7077 | 120.639 | -0.068665 | 120.6802 | 120.5887 | -0.050354 | -0.068665 | 120.6619 | 120.694 | 120.6985 | -0.10529 | 120.5795 | 120.5795 | 120.6985 | -0.009155
2317.9219 | 120.7169 | -120.0027 | 0.5722 | 0.0054168 | 0.0017816 | 0.07514 | 0.025443 | -0.067614 | -0.02609 | 0.00036105 | 0.014954 | 0.61707 | 0.59161 | -0.073875 | -0.0069726 | 0.040653 | 0.064087 | 0.086975 | 0.11902 | 0.11902 | 0.07782 | 0.07782 | -0.032043 | 0.31586 | 0.37537 | 0.25177 | 0.43945 | 0.43488 | 0.40283 | 0.33875 | 120.0806 | 119.9707 | -0.49438 | 120.0897 | 120.1218 | 0.15106 | -0.50812 | 120.4056 | 120.3415 | -0.13275 | 120.3186 | 120.2545 | -0.086975 | -0.13733 | 120.0806 | 120.0668 | 120.1218 | -0.60425 | 120.4422 | 120.4376 | 120.3781 | -0.23346
2319.7031 | 120.845 | -120.6619 | 0.09613 | 0.013046 | -0.00099541 | 0.069799 | 0.028647 | -0.0674 | -0.024167 | 0.00078825 | 0.022583 | 0.043278 | 0.018677 | -0.045677 | -0.00505 | 0.012454 | 0.036621 | -0.018311 | 0.022888 | 0.082397 | 0.10529 | 0.036621 | -0.091553 | -0.009155 | 0.045776 | -0.09613 | 0.045776 | 0.036621 | 0.059509 | 0.004578 | 120.6985 | 120.5704 | 0.009156 | 120.6436 | 120.7443 | 0.17395 | -0.059509 | 120.7214 | 120.6665 | -0.050354 | 120.6528 | 120.5658 | -0.10071 | -0.059509 | 120.7672 | 120.6985 | 120.6848 | -0.18768 | 120.7077 | 120.6985 | 120.7077 | -0.091552
2321.4844 | 120.8496 | -120.694 | 0.10986 | -0.0022127 | -0.00035461 | 0.068517 | 0.028647 | -0.069323 | -0.026517 | 0.0010018 | 0.0073242 | 0.038151 | 0.019532 | -0.044609 | -0.0080408 | 0.013736 | 0.11444 | 0.13733 | 0.17853 | 0.16022 | 0.059509 | 0.082397 | -0.022888 | 0.082397 | 0.16937 | 0.013733 | -0.018311 | 0.009155 | 0.09613 | 0.036621 | 120.7764 | 120.6711 | -0.050354 | 120.8313 | 120.8542 | 0.1831 | 0.004578 | 120.7901 | 120.7306 | -0.12817 | 120.7764 | 120.7077 | -0.022888 | -0.10071 | 120.7535 | 120.8084 | 120.8725 | -0.13275 | 120.6757 | 120.7031 | 120.8633 | -0.073242
2323.25 | 120.845 | -120.7581 | 0.086975 | -0.0022127 | 0.0019952 | 0.074285 | 0.027152 | -0.068682 | -0.023313 | 0.00014745 | 0.014954 | 0.051182 | 0.023377 | -0.047386 | -0.0065454 | 0.015872 | 0.045776 | 0.054932 | 0.068665 | 0.10529 | 0.10986 | 0.054932 | -0.068665 | -0.018311 | 0.050354 | -0.091553 | 0.041199 | 0.054932 | 0.059509 | 0.022888 | 120.813 | 120.6894 | 0.022888 | 120.813 | 120.8633 | 0.17395 | -0.041199 | 120.8176 | 120.7809 | -0.045776 | 120.7397 | 120.6665 | -0.11444 | -0.032043 | 120.8679 | 120.8038 | 120.8267 | -0.15564 | 120.7993 | 120.813 | 120.8084 | -0.064087
2324.9844 | 121.0144 | -120.7306 | 0.064087 | 0.0054168 | 0.0026362 | 0.072576 | 0.026938 | -0.068468 | -0.027585 | 0.00057465 | -0.0003053 | 0.03751 | 0.017182 | -0.04824 | -0.008468 | 0.015018 | 0.091553 | 0.13275 | 0.15564 | 0.14648 | 0.068665 | 0.082397 | -0.032043 | 0.091553 | 0.17853 | 0.054932 | 0.004578 | 0.022888 | 0.10071 | 0.045776 | 120.813 | 120.6985 | 0.004578 | 120.8633 | 120.8771 | 0.17853 | 0.027466 | 120.8313 | 120.7764 | -0.059509 | 120.8221 | 120.7855 | 0.009156 | -0.041199 | 120.7993 | 120.8221 | 120.8862 | -0.09613 | 120.7352 | 120.7535 | 120.9091 | -0.018311
2326.7656 | 120.9503 | -120.7809 | 0.091553 | 0.013046 | 0.00071339 | 0.070867 | 0.025443 | -0.065691 | -0.021604 | 0.0012154 | 0.022583 | 0.043064 | 0.019318 | -0.044395 | -0.0054772 | 0.011813 | 0.07782 | 0.041199 | 0.064087 | 0.1236 | 0.10529 | 0.045776 | -0.064087 | 0.059509 | 0.091553 | -0.059509 | 0.032043 | 0.041199 | 0.07782 | 0.027466 | 120.8267 | 120.7169 | 0.013733 | 120.8221 | 120.9045 | 0.18768 | -0.013733 | 120.8588 | 120.8084 | -0.05951 | 120.8405 | 120.7214 | -0.086975 | -0.050354 | 120.8862 | 120.8588 | 120.845 | -0.15564 | 120.813 | 120.8221 | 120.8725 | -0.064087
2328.5625 | 121.0464 | -120.7397 | 0.086975 | -0.0022127 | 0.0013544 | 0.073003 | 0.029929 | -0.0674 | -0.028226 | 0.0010018 | 0.0073242 | 0.043064 | 0.023163 | -0.047386 | -0.0095362 | 0.016513 | 0.1236 | 0.16022 | 0.17853 | 0.17395 | 0.064087 | 0.073242 | -0.036621 | 0.10071 | 0.19226 | 0.050354 | -0.022888 | 0.004578 | 0.11444 | 0.036621 | 120.813 | 120.7031 | -0.022888 | 120.9 | 120.9137 | 0.21057 | 0.036621 | 120.8542 | 120.7764 | -0.10986 | 120.8405 | 120.7901 | 0.013733 | -0.082397 | 120.8038 | 120.8633 | 120.9183 | -0.1236 | 120.7169 | 120.7443 | 120.932 | -0.050354
2330.2969 | 120.9961 | -120.8038 | 0.10071 | 0.0054168 | 0.001568 | 0.071508 | 0.030783 | -0.068468 | -0.025876 | -0.0015616 | 0.0073242 | 0.054173 | 0.034485 | -0.046745 | -0.005691 | 0.014377 | 0.064087 | 0.068665 | 0.11902 | 0.11902 | 0.09613 | 0.059509 | -0.059509 | 0.009155 | 0.073242 | -0.045776 | 0.022888 | 0.050354 | 0.086975 | 0.022888 | 120.8633 | 120.7443 | -0.004578 | 120.8725 | 120.9229 | 0.17853 | -0.036621 | 120.8908 | 120.8267 | -0.07782 | 120.813 | 120.7581 | -0.068664 | -0.050354 | 120.9 | 120.8679 | 120.9229 | -0.16022 | 120.8267 | 120.8542 | 120.8771 | -0.07782
2332.0781 | 120.9824 | -120.8038 | 0.068665 | 0.020676 | 0.001568 | 0.069372 | 0.026938 | -0.070818 | -0.021817 | 0.0010018 | -0.0003053 | 0.039646 | 0.01825 | -0.044395 | -0.0041956 | 0.011813 | 0.004578 | -0.032043 | -0.009155 | 0.073242 | 0.10071 | 0.068665 | -0.073242 | -0.022888 | 0 | -0.12817 | 0.032043 | 0.041199 | 0.059509 | 0 | 120.8725 | 120.7306 | 0.032043 | 120.7718 | 120.8771 | 0.14648 | -0.064087 | 120.8633 | 120.8038 | -0.036622 | 120.7809 | 120.6757 | -0.12817 | -0.027466 | 120.9045 | 120.8084 | 120.7947 | -0.14191 | 120.8359 | 120.845 | 120.8038 | -0.068665
2333.8594 | 121.0144 | -120.8496 | 0.086975 | 0.0054168 | 0.00071339 | 0.067022 | 0.026938 | -0.066973 | -0.022458 | 0.0022836 | 0.022583 | 0.040501 | 0.020813 | -0.045036 | -0.0037684 | 0.012882 | 0.041199 | 0.041199 | 0.059509 | 0.10986 | 0.10986 | 0.054932 | -0.082397 | 0.045776 | 0.086975 | -0.059509 | 0.018311 | 0.045776 | 0.09613 | 0 | 120.9045 | 120.7672 | 0.022888 | 120.8908 | 120.9595 | 0.19226 | -0.045776 | 120.9457 | 120.8496 | -0.068664 | 120.8954 | 120.7901 | -0.059509 | -0.041199 | 120.9595 | 120.8908 | 120.9091 | -0.16937 | 120.8679 | 120.8954 | 120.9366 | -0.086975
2335.5781 | 121.1197 | -120.8221 | 0.068665 | -0.0022127 | 0.0026362 | 0.071935 | 0.027792 | -0.069537 | -0.026731 | 0.00014745 | 0.0073242 | 0.055027 | 0.034699 | -0.046318 | -0.011031 | 0.017581 | 0.036621 | 0.068665 | 0.11902 | 0.10986 | 0.07782 | 0.091553 | -0.045776 | 0.041199 | 0.11444 | -0.004578 | 0.022888 | 0.022888 | 0.11444 | 0.036621 | 120.9137 | 120.7764 | 0.009155 | 120.8908 | 120.932 | 0.15564 | -0.032044 | 120.9366 | 120.8588 | -0.045777 | 120.8633 | 120.8176 | -0.041199 | -0.045777 | 120.9 | 120.8588 | 120.9412 | -0.11444 | 120.845 | 120.845 | 120.9366 | -0.032044
2337.3594 | 120.5383 | -120.9183 | 0.10529 | 0.0054168 | 0.0041314 | 0.068304 | 0.027365 | -0.071245 | -0.020322 | -0.00027975 | 0.0073242 | 0.049473 | 0.028931 | -0.045463 | -0.0037684 | 0.012454 | 0.073242 | 0.059509 | 0.086975 | 0.12817 | 0.09613 | 0.073242 | -0.068665 | 0.068665 | 0.082397 | -0.054932 | 0.018311 | 0.054932 | 0.11444 | 0.059509 | 120.9915 | 120.8496 | -0.009156 | 120.9778 | 121.0464 | 0.19684 | -0.032044 | 121.0327 | 120.9778 | -0.086975 | 120.9869 | 120.8633 | -0.11444 | -0.050354 | 121.0144 | 120.9915 | 121.0052 | -0.17395 | 120.9366 | 120.9732 | 121.0007 | -0.045777
2339.1406 | 121.1151 | -120.8771 | 0.07782 | 0.0054168 | 0.0017816 | 0.067236 | 0.026083 | -0.069537 | -0.021817 | 0.0010018 | 0.0073242 | 0.040287 | 0.020386 | -0.044395 | -0.0071862 | 0.015231 | 0 | -0.027466 | 0.018311 | 0.082397 | 0.10071 | 0.045776 | -0.082397 | -0.009155 | 0 | -0.091553 | 0.018311 | 0.022888 | 0.086975 | 0.009155 | 120.9229 | 120.7947 | 0.022888 | 120.8496 | 120.9595 | 0.16479 | -0.07782 | 120.9641 | 120.8862 | -0.059509 | 120.8679 | 120.7855 | -0.10071 | -0.054932 | 120.9778 | 120.8771 | 120.8954 | -0.16022 | 120.8954 | 120.9 | 120.8771 | -0.068665
2340.8594 | 121.1288 | -120.8908 | 0.082397 | 0.0054168 | -0.00056821 | 0.067663 | 0.026297 | -0.067614 | -0.022672 | 0.0016428 | 0.0073242 | 0.042637 | 0.020386 | -0.046745 | -0.006759 | 0.013736 | 0.027466 | 0.045776 | 0.054932 | 0.11902 | 0.10986 | 0.036621 | -0.073242 | 0.036621 | 0.10071 | -0.064087 | 0.013733 | 0.041199 | 0.073242 | 0.013733 | 120.9274 | 120.8176 | 0.027466 | 120.9366 | 121.0098 | 0.19226 | -0.054931 | 120.9641 | 120.9045 | -0.068664 | 120.9274 | 120.8267 | -0.07782 | -0.041198 | 121.0007 | 120.9183 | 120.9457 | -0.15564 | 120.9045 | 120.932 | 120.9915 | -0.068664
2342.6406 | 121.0693 | -120.9457 | 0.073242 | 0.013046 | 0.001568 | 0.070226 | 0.027365 | -0.067187 | -0.024381 | 0.0016428 | 0.014954 | 0.041569 | 0.019959 | -0.044395 | -0.005691 | 0.016727 | -0.018311 | -0.027466 | 0.009155 | 0.073242 | 0.10071 | 0.068665 | -0.07782 | -0.032043 | 0.004578 | -0.13275 | 0.032043 | 0.045776 | 0.064087 | -0.004578 | 121.0144 | 120.8679 | 0.027466 | 120.9183 | 121.019 | 0.15106 | -0.091553 | 121.0098 | 120.9412 | -0.041199 | 120.9137 | 120.813 | -0.12817 | -0.027466 | 121.0464 | 120.9274 | 120.9549 | -0.15106 | 120.9778 | 120.9915 | 120.9503 | -0.07782
2344.4219 | 121.1838 | -120.9503 | 0.045776 | 0.0054168 | 0.0026362 | 0.069799 | 0.027365 | -0.069323 | -0.029508 | 0.0022836 | 0.0073242 | 0.038578 | 0.01825 | -0.047386 | -0.0076136 | 0.018649 | 0.086975 | 0.11444 | 0.15564 | 0.13275 | 0.041199 | 0.07782 | -0.022888 | 0.064087 | 0.13733 | 0.027466 | 0 | 0.009155 | 0.10529 | 0.059509 | 121.0281 | 120.9274 | -0.004577 | 121.0648 | 121.0831 | 0.15564 | 0.041199 | 121.0556 | 121.0098 | -0.045776 | 121.0144 | 120.9778 | -0.032043 | -0.036621 | 120.9915 | 121.0373 | 121.106 | -0.068664 | 120.9503 | 120.9595 | 121.0876 | 0.013733
2346.1406 | 121.0785 | -120.7626 | 0.24261 | 0.013046 | 0.004986 | 0.067022 | 0.027579 | -0.065905 | -0.021817 | 0.0014292 | 0.0073242 | 0.18 | 0.15689 | -0.049949 | -0.005691 | 0.018222 | 0 | -0.032043 | 0 | 0.073242 | 0.11902 | 0.068665 | -0.07782 | 0.032043 | 0.050354 | -0.054932 | 0.1236 | 0.13275 | 0.14191 | 0.059509 | 120.8313 | 120.6848 | -0.1236 | 120.7306 | 120.8359 | 0.15106 | -0.24261 | 120.9045 | 120.8221 | -0.11902 | 120.7947 | 120.7077 | -0.11444 | -0.10986 | 120.8817 | 120.7626 | 120.7626 | -0.32044 | 120.8862 | 120.8954 | 120.813 | -0.18311
2347.9219 | 121.2753 | -120.9778 | 0.068665 | 0.020676 | 0.0022088 | 0.070226 | 0.026938 | -0.069964 | -0.02374 | -0.00027975 | 0.022583 | 0.041783 | 0.020172 | -0.043968 | -0.0048364 | 0.013309 | 0.045776 | 0.041199 | 0.082397 | 0.11444 | 0.082397 | 0.086975 | -0.054932 | 0.059509 | 0.10071 | 0 | -0.022888 | 0 | 0.11444 | 0.064087 | 121.0648 | 120.9229 | 0.013732 | 121.019 | 121.0922 | 0.16937 | -0.022889 | 121.0922 | 121.0419 | -0.091553 | 121.0373 | 120.9778 | -0.064087 | -0.068665 | 121.0602 | 121.0236 | 121.0602 | -0.1236 | 120.9549 | 120.9778 | 121.0785 | -0.004578
2349.7031 | 121.1563 | -121.0373 | 0.10986 | -0.0022127 | -0.00035461 | 0.069372 | 0.031638 | -0.069323 | -0.027585 | -0.0017752 | 0.0073242 | 0.04221 | 0.024445 | -0.046745 | -0.0082544 | 0.014591 | -0.022888 | 0.004578 | 0.050354 | 0.059509 | 0.091553 | 0.050354 | -0.064087 | -0.045776 | 0.050354 | -0.086975 | 0.032043 | 0.036621 | 0.068665 | 0 | 121.0876 | 120.9732 | -0.01831 | 121.0419 | 121.0968 | 0.1236 | -0.13275 | 121.106 | 121.0373 | -0.07782 | 120.9915 | 120.9503 | -0.086975 | -0.073242 | 121.1288 | 121.0144 | 121.0876 | -0.17395 | 121.0693 | 121.0739 | 121.0876 | -0.10986
2351.4219 | 121.2158 | -121.0602 | 0.086975 | 0.0054168 | 0.0013544 | 0.067663 | 0.029501 | -0.067187 | -0.023526 | 0.00014745 | -0.0003053 | 0.041355 | 0.020172 | -0.0429 | -0.0046228 | 0.013522 | 0.004578 | 0.009155 | 0.013733 | 0.082397 | 0.11444 | 0.041199 | -0.091553 | -0.045776 | 0.036621 | -0.091553 | 0.022888 | 0.054932 | 0.064087 | 0 | 121.1014 | 120.9686 | 0.027466 | 121.0693 | 121.1426 | 0.17395 | -0.082397 | 121.1243 | 121.0602 | -0.064087 | 121.0144 | 120.9686 | -0.091553 | -0.032043 | 121.1746 | 121.0648 | 121.0739 | -0.17853 | 121.0831 | 121.1151 | 121.0968 | -0.086975
2353.2031 | 121.2341 | -121.0602 | 0.091553 | -0.0098417 | 0.001568 | 0.069799 | 0.028647 | -0.066973 | -0.025235 | -0.0015616 | 0.0073242 | 0.042637 | 0.024872 | -0.04589 | -0.0082544 | 0.014163 | 0.045776 | 0.073242 | 0.09613 | 0.1236 | 0.10071 | 0.059509 | -0.050354 | -0.022888 | 0.073242 | -0.073242 | 0.032043 | 0.036621 | 0.082397 | 0.018311 | 121.1197 | 121.0098 | 0.009155 | 121.1334 | 121.1838 | 0.17395 | -0.045777 | 121.1426 | 121.0785 | -0.05951 | 121.0373 | 120.9869 | -0.091553 | -0.054932 | 121.1609 | 121.106 | 121.1563 | -0.14191 | 121.0922 | 121.0968 | 121.1334 | -0.073242
2354.9062 | 121.2112 | -121.0739 | 0.068665 | 0.0054168 | 0.0028498 | 0.065527 | 0.027792 | -0.068041 | -0.019681 | -0.0011344 | -0.0003053 | 0.04456 | 0.019745 | -0.0429 | -0.0048364 | 0.012454 | 0.064087 | 0.050354 | 0.073242 | 0.1236 | 0.086975 | 0.059509 | -0.091553 | 0.050354 | 0.091553 | -0.054932 | 0.027466 | 0.045776 | 0.082397 | 0.018311 | 121.1334 | 120.9824 | 0.01831 | 121.1243 | 121.1975 | 0.21515 | -0.004578 | 121.1563 | 121.0922 | -0.041199 | 121.1243 | 121.019 | -0.073243 | -0.022889 | 121.1609 | 121.138 | 121.1472 | -0.16022 | 121.1014 | 121.1197 | 121.1655 | -0.050354
2356.6875 | 121.3715 | -121.051 | 0.054932 | 0.020676 | 0.0026362 | 0.074499 | 0.02886 | -0.068468 | -0.030576 | -0.00092075 | 0.014954 | 0.039219 | 0.020386 | -0.046745 | -0.0071862 | 0.014591 | 0.027466 | 0.068665 | 0.10529 | 0.13733 | 0.07782 | 0.091553 | -0.041199 | 0.032043 | 0.11444 | 0.018311 | -0.018311 | 0.022888 | 0.11444 | 0.045776 | 121.1426 | 121.0098 | 0.022888 | 121.1197 | 121.1884 | 0.17853 | -0.027466 | 121.1655 | 121.0968 | -0.073243 | 121.0831 | 121.0693 | -0.027465 | -0.032044 | 121.1288 | 121.0785 | 121.1563 | -0.096131 | 121.0327 | 121.0739 | 121.1655 | -0.009156
2358.4844 | 121.2387 | -121.1105 | 0.091553 | 0.0054168 | 0.0019952 | 0.070013 | 0.026083 | -0.067187 | -0.026517 | -0.0011344 | 0.0073242 | 0.041569 | 0.020386 | -0.046104 | -0.005691 | 0.014377 | 0.09613 | 0.1236 | 0.14648 | 0.16479 | 0.073242 | 0.086975 | -0.041199 | 0.07782 | 0.16022 | 0.027466 | 0.004578 | 0.018311 | 0.10986 | 0.027466 | 121.1975 | 121.0693 | -0.018311 | 121.2341 | 121.2753 | 0.20599 | 0.004577 | 121.2204 | 121.138 | -0.086975 | 121.1884 | 121.138 | 0 | -0.073242 | 121.1838 | 121.2067 | 121.257 | -0.13275 | 121.1151 | 121.1288 | 121.2708 | -0.064087
2360.2031 | 121.344 | -121.0419 | 0.07782 | 0.020676 | 0.0028498 | 0.070226 | 0.030142 | -0.065905 | -0.026303 | -0.0019888 | 0.0073242 | 0.042423 | 0.02295 | -0.047172 | -0.008468 | 0.013095 | 0.11902 | 0.16022 | 0.16937 | 0.15564 | 0.059509 | 0.086975 | -0.041199 | 0.086975 | 0.21057 | 0.054932 | -0.004578 | 0.009155 | 0.10071 | 0.050354 | 121.1288 | 121.0007 | -0.018311 | 121.2021 | 121.1975 | 0.19684 | 0.041199 | 121.1426 | 121.0922 | -0.082398 | 121.1288 | 121.0968 | 0.004578 | -0.068665 | 121.1014 | 121.1609 | 121.2112 | -0.11902 | 121.0373 | 121.051 | 121.2524 | -0.027466
2361.9844 | 121.3074 | -121.1197 | 0.09613 | 0.0054168 | 0.00092719 | 0.067663 | 0.029929 | -0.067614 | -0.022885 | 0.0010018 | 0.0073242 | 0.046055 | 0.024872 | -0.044395 | -0.00505 | 0.013522 | 0.022888 | 0.004578 | 0.041199 | 0.086975 | 0.10529 | 0.050354 | -0.082397 | 0.018311 | 0.064087 | -0.073242 | 0.027466 | 0.041199 | 0.068665 | 0 | 121.17 | 121.0373 | 0.009156 | 121.1243 | 121.2067 | 0.16937 | -0.073242 | 121.1884 | 121.1197 | -0.068664 | 121.138 | 121.0464 | -0.073242 | -0.054931 | 121.225 | 121.1426 | 121.1609 | -0.17853 | 121.1472 | 121.1609 | 121.1838 | -0.09613
2363.7656 | 121.4081 | -121.0831 | 0.068665 | 0.0054168 | 0.0028498 | 0.073003 | 0.027792 | -0.068682 | -0.027799 | -0.0011344 | 0.022583 | 0.046482 | 0.024445 | -0.046318 | -0.0076136 | 0.013309 | 0.11902 | 0.15564 | 0.16479 | 0.16479 | 0.07782 | 0.082397 | -0.032043 | 0.10986 | 0.21057 | 0.054932 | -0.013733 | 0.022888 | 0.10529 | 0.050354 | 121.1655 | 121.051 | 0.009155 | 121.2387 | 121.2479 | 0.19684 | 0.050354 | 121.1884 | 121.1334 | -0.082398 | 121.1929 | 121.138 | 0.004578 | -0.045777 | 121.1609 | 121.2021 | 121.2479 | -0.10071 | 121.0693 | 121.106 | 121.2936 | -0.018311
2365.5469 | 121.2799 | -121.0236 | 0.11444 | 0.013046 | 0.0039178 | 0.069799 | 0.026083 | -0.069323 | -0.025235 | -0.00070715 | 0.0073242 | 0.084507 | 0.061188 | -0.045036 | -0.0069726 | 0.016513 | 0.10529 | 0.11444 | 0.15564 | 0.15106 | 0.059509 | 0.082397 | -0.041199 | 0.09613 | 0.15106 | 0.045776 | 0.036621 | 0.045776 | 0.11444 | 0.073242 | 121.106 | 120.9824 | -0.054932 | 121.138 | 121.1746 | 0.19226 | -0.009155 | 121.138 | 121.0968 | -0.07782 | 121.1197 | 121.0693 | -0.027466 | -0.068665 | 121.0831 | 121.1288 | 121.1792 | -0.15564 | 121.0602 | 121.0693 | 121.1746 | -0.041199
2367.3281 | 119.902 | -119.6732 | 0.064087 | 0.0054168 | 0.0013544 | 0.070013 | 0.025229 | -0.068896 | -0.018826 | 0.00036105 | -0.0003053 | 0.050968 | 0.030854 | -0.044609 | -0.0027002 | 0.015872 | 0.036621 | -0.018311 | 0.041199 | 0.064087 | 0.09613 | 0.036621 | -0.068665 | 0.036621 | 0.022888 | -0.073242 | 0.036621 | 0.045776 | 0.091553 | 0.032043 | 119.7098 | 119.6045 | 0.032043 | 119.6548 | 119.7372 | 0.13275 | -0.027466 | 119.7647 | 119.7052 | -0.027466 | 119.7098 | 119.5999 | -0.10529 | -0.018311 | 119.7693 | 119.7098 | 119.7144 | -0.13275 | 119.7098 | 119.7189 | 119.696 | -0.032044
2369.0469 | 120.8405 | -120.7672 | 0.10071 | 0.013046 | 0.0026362 | 0.06574 | 0.027365 | -0.069109 | -0.021817 | 0.0018564 | 0.014954 | 0.055668 | 0.03534 | -0.044181 | -0.003341 | 0.01395 | 0.022888 | -0.009155 | 0.022888 | 0.082397 | 0.10071 | 0.036621 | -0.091553 | -0.018311 | 0 | -0.1236 | 0.036621 | 0.045776 | 0.07782 | 0.013733 | 120.8038 | 120.6757 | 0 | 120.7581 | 120.8496 | 0.17395 | -0.07782 | 120.845 | 120.7809 | -0.064087 | 120.7489 | 120.6436 | -0.13733 | -0.054932 | 120.8679 | 120.7901 | 120.7901 | -0.19226 | 120.8038 | 120.813 | 120.7672 | -0.086975
2370.8438 | 121.0739 | -120.8038 | 0.068665 | 0.0054168 | 0.0022088 | 0.068731 | 0.027579 | -0.068041 | -0.025022 | 0.0024972 | 0.022583 | 0.050968 | 0.032563 | -0.043113 | -0.0044092 | 0.016513 | 0.10529 | 0.11444 | 0.13733 | 0.16937 | 0.059509 | 0.10986 | -0.022888 | 0.11444 | 0.12817 | 0.013733 | -0.009155 | 0.004578 | 0.11444 | 0.054932 | 120.9137 | 120.7809 | -0.009156 | 120.9183 | 120.9732 | 0.19226 | 0.036621 | 120.9183 | 120.8588 | -0.07782 | 120.9183 | 120.8176 | -0.041199 | -0.064087 | 120.8633 | 120.9091 | 120.9412 | -0.091553 | 120.7947 | 120.8084 | 120.932 | -0.013733
2372.625 | 121.106 | -120.8633 | 0.073242 | 0.013046 | 0.004986 | 0.071294 | 0.025229 | -0.065478 | -0.021817 | 0.0010018 | 0.014954 | 0.053959 | 0.034058 | -0.043754 | -0.0046228 | 0.016513 | 0 | -0.013733 | 0.009155 | 0.086975 | 0.10071 | 0.059509 | -0.07782 | -0.018311 | 0.018311 | -0.09613 | 0.036621 | 0.050354 | 0.068665 | 0.004578 | 120.9229 | 120.7855 | 0.027466 | 120.8496 | 120.9503 | 0.16479 | -0.073242 | 120.932 | 120.8679 | -0.036621 | 120.845 | 120.7672 | -0.10071 | -0.022888 | 120.9641 | 120.8633 | 120.8725 | -0.15106 | 120.9 | 120.9137 | 120.8817 | -0.068664
2374.3594 | 121.1563 | -120.9045 | 0.082397 | -0.0022127 | 0.0030634 | 0.068517 | 0.029288 | -0.067828 | -0.025235 | -0.0015616 | 0.0073242 | 0.051823 | 0.036194 | -0.045036 | -0.008468 | 0.013522 | 0.068665 | 0.1236 | 0.15564 | 0.16022 | 0.054932 | 0.082397 | -0.022888 | 0.082397 | 0.12817 | 0.022888 | -0.009155 | 0.004578 | 0.091553 | 0.036621 | 120.9869 | 120.8817 | -0.027465 | 121.0281 | 121.0648 | 0.1831 | -0.013732 | 120.9961 | 120.9412 | -0.091552 | 120.9869 | 120.9274 | -0.013733 | -0.077819 | 120.9595 | 120.9732 | 121.0602 | -0.10528 | 120.8954 | 120.9091 | 121.0327 | -0.045776
2376.1406 | 121.2708 | -120.9274 | 0.07782 | 0.0054168 | 0.0011408 | 0.073217 | 0.027365 | -0.068255 | -0.031003 | -0.0011344 | 0.014954 | 0.056523 | 0.037262 | -0.045463 | -0.006759 | 0.015018 | 0.059509 | 0.086975 | 0.1236 | 0.13275 | 0.064087 | 0.073242 | -0.041199 | 0.064087 | 0.14648 | 0.036621 | -0.004578 | 0.013733 | 0.11444 | 0.027466 | 121.0007 | 120.8862 | -0.013733 | 121.0144 | 121.0602 | 0.17395 | -0.018311 | 121.0419 | 120.9549 | -0.082398 | 120.9915 | 120.9641 | 0.009155 | -0.064087 | 120.9915 | 120.9869 | 121.051 | -0.11902 | 120.9229 | 120.9412 | 121.0739 | -0.050354
2377.9219 | 121.1655 | -120.9869 | 0.082397 | 0.0054168 | 0.0028498 | 0.070867 | 0.024588 | -0.068255 | -0.02139 | 0.00036105 | 0.0073242 | 0.055668 | 0.034058 | -0.0429 | -0.003982 | 0.013522 | 0.009155 | -0.032043 | 0.004578 | 0.073242 | 0.10529 | 0.059509 | -0.064087 | -0.027466 | 0.009155 | -0.10529 | 0.041199 | 0.041199 | 0.050354 | -0.004578 | 121.0464 | 120.9229 | 0.022889 | 120.9549 | 121.0602 | 0.13733 | -0.073242 | 121.0373 | 120.9824 | -0.041198 | 120.9595 | 120.8817 | -0.10071 | -0.041198 | 121.0922 | 120.9961 | 120.9915 | -0.14648 | 121.0281 | 121.0281 | 120.9961 | -0.086975
2379.7188 | 121.3165 | -121.0098 | 0.11444 | -0.0022127 | 0.001568 | 0.07044 | 0.026938 | -0.068896 | -0.023099 | 0.00036105 | 0.014954 | 0.067204 | 0.047089 | -0.044822 | -0.003982 | 0.013309 | 0.013733 | 0 | 0.022888 | 0.10071 | 0.091553 | 0.059509 | -0.091553 | -0.009155 | 0.064087 | -0.086975 | 0.050354 | 0.068665 | 0.09613 | 0.022888 | 121.0693 | 120.9183 | -0.022888 | 121.0098 | 121.1105 | 0.19226 | -0.10071 | 121.106 | 121.0327 | -0.064087 | 121.0007 | 120.9229 | -0.10986 | -0.045776 | 121.1014 | 121.0236 | 121.0327 | -0.20599 | 121.0602 | 121.0785 | 121.0739 | -0.091553
2381.4375 | 121.1655 | -121.0831 | 0.091553 | 0.013046 | -0.00014101 | 0.06809 | 0.030142 | -0.068041 | -0.026731 | 0.0012154 | 0.0073242 | 0.048619 | 0.032135 | -0.046531 | -0.0078272 | 0.015231 | 0.050354 | 0.082397 | 0.10071 | 0.13275 | 0.091553 | 0.050354 | -0.054932 | -0.013733 | 0.073242 | -0.050354 | 0.018311 | 0.045776 | 0.07782 | 0.013733 | 121.1334 | 121.0281 | 0 | 121.1655 | 121.2158 | 0.18768 | -0.041199 | 121.1609 | 121.0968 | -0.073242 | 121.0693 | 121.0327 | -0.064087 | -0.045777 | 121.1746 | 121.1334 | 121.1838 | -0.14649 | 121.1014 | 121.1288 | 121.1563 | -0.07782
2383.2188 | 121.2982 | -121.0876 | 0.082397 | -0.0022127 | 0.004345 | 0.071508 | 0.023947 | -0.068682 | -0.031644 | -0.00092075 | -0.0003053 | 0.054386 | 0.033203 | -0.046104 | -0.0095362 | 0.014591 | 0.050354 | 0.064087 | 0.09613 | 0.11902 | 0.07782 | 0.068665 | -0.041199 | 0.018311 | 0.091553 | -0.018311 | -0.004578 | 0.013733 | 0.10529 | 0.032043 | 121.1563 | 121.0464 | -0.004577 | 121.1517 | 121.2067 | 0.16022 | -0.032043 | 121.1929 | 121.1197 | -0.086975 | 121.106 | 121.0693 | -0.050354 | -0.068664 | 121.1655 | 121.138 | 121.1838 | -0.1236 | 121.0831 | 121.1014 | 121.1792 | -0.050354
2384.9219 | 121.2387 | -121.0922 | 0.082397 | 0.0054168 | 0.0069086 | 0.064459 | 0.028647 | -0.067614 | -0.01904 | -6.615e-05 | 0.014954 | 0.055027 | 0.034912 | -0.044822 | -0.006759 | 0.0116 | -0.013733 | -0.064087 | 0 | 0.059509 | 0.09613 | 0.073242 | -0.054932 | -0.022888 | -0.009155 | -0.1236 | 0.027466 | 0.041199 | 0.073242 | 0.009155 | 121.1655 | 121.0373 | 0.013733 | 121.0281 | 121.1517 | 0.11444 | -0.09613 | 121.1655 | 121.1014 | -0.054931 | 121.0693 | 120.9686 | -0.13275 | -0.041198 | 121.1884 | 121.0785 | 121.0922 | -0.13733 | 121.1197 | 121.1334 | 121.0831 | -0.073242
2386.7031 | 121.2891 | -121.0648 | 0.09613 | 0.020676 | 0.0037042 | 0.07279 | 0.026511 | -0.068041 | -0.031644 | 0.00036105 | -0.0003053 | 0.073612 | 0.058625 | -0.04525 | -0.0063318 | 0.015445 | 0.050354 | 0.064087 | 0.11444 | 0.1236 | 0.064087 | 0.10071 | -0.050354 | 0.018311 | 0.09613 | 0 | 0.004578 | 0.032043 | 0.10986 | 0.050354 | 121.1655 | 121.0144 | -0.032043 | 121.1288 | 121.1884 | 0.17395 | -0.045776 | 121.1746 | 121.1151 | -0.091552 | 121.0831 | 121.0648 | -0.050354 | -0.064087 | 121.1288 | 121.1151 | 121.1792 | -0.14648 | 121.0693 | 121.0968 | 121.1609 | -0.045776
2388.5 | 120.4468 | -120.4056 | 0.10529 | 0.0054168 | 7.2586e-05 | 0.071935 | 0.026297 | -0.066546 | -0.025876 | 0.00078825 | 0.014954 | 0.051396 | 0.032563 | -0.04589 | -0.0054772 | 0.01395 | 0.004578 | 0.013733 | 0.027466 | 0.064087 | 0.10071 | 0.041199 | -0.068665 | -0.027466 | 0.045776 | -0.091553 | 0.050354 | 0.059509 | 0.054932 | -0.004578 | 120.4468 | 120.3369 | -0.004578 | 120.4193 | 120.4697 | 0.13275 | -0.10071 | 120.4605 | 120.401 | -0.054932 | 120.3781 | 120.314 | -0.086975 | -0.045777 | 120.5063 | 120.4102 | 120.433 | -0.17395 | 120.4559 | 120.4651 | 120.4514 | -0.10986
2390.2969 | 121.051 | -120.9091 | 0.091553 | 0.0054168 | 0.0013544 | 0.067236 | 0.029929 | -0.065691 | -0.022244 | 0.0010018 | -0.0003053 | 0.05225 | 0.032135 | -0.044395 | -0.0074 | 0.012027 | 0.013733 | -0.013733 | 0.013733 | 0.091553 | 0.10986 | 0.036621 | -0.07782 | -0.032043 | 0.041199 | -0.082397 | 0.004578 | 0.045776 | 0.068665 | 0.004578 | 120.9457 | 120.8313 | 0.01831 | 120.8954 | 121.0007 | 0.16937 | -0.07782 | 120.9778 | 120.9137 | -0.086975 | 120.8771 | 120.8267 | -0.086975 | -0.045777 | 121.019 | 120.9229 | 120.9229 | -0.16937 | 120.9137 | 120.9549 | 120.9503 | -0.086975
2392.0625 | 121.1014 | -120.9778 | 0.10071 | 0.013046 | 0.00028619 | 0.068945 | 0.026511 | -0.069537 | -0.022672 | 0.0027108 | 0.0073242 | 0.052677 | 0.033631 | -0.043968 | -0.0048364 | 0.014163 | 0.004578 | -0.036621 | 0.018311 | 0.073242 | 0.10529 | 0.036621 | -0.082397 | -0.018311 | -0.013733 | -0.13733 | 0.032043 | 0.050354 | 0.068665 | -0.009155 | 121.0144 | 120.8954 | 0.004578 | 120.9412 | 121.051 | 0.15564 | -0.09613 | 121.0464 | 120.9686 | -0.068665 | 120.9595 | 120.8405 | -0.12817 | -0.050354 | 121.0831 | 120.9824 | 120.9961 | -0.18311 | 121.0098 | 121.0281 | 120.9641 | -0.10986
2393.8594 | 121.2479 | -120.932 | 0.086975 | 0.013046 | 0.0022088 | 0.071508 | 0.025015 | -0.066759 | -0.024808 | 0.00207 | 0.014954 | 0.083439 | 0.060547 | -0.046745 | -0.0020594 | 0.015872 | 0.09613 | 0.11444 | 0.13275 | 0.15564 | 0.068665 | 0.082397 | -0.036621 | 0.11902 | 0.14648 | 0.045776 | -0.004578 | 0.022888 | 0.12817 | 0.068665 | 121.0144 | 120.8954 | -0.01831 | 121.0464 | 121.0876 | 0.19226 | 0.009155 | 121.0602 | 121.0007 | -0.091553 | 121.051 | 120.9778 | -0.022889 | -0.064087 | 121.0007 | 121.0281 | 121.0648 | -0.1236 | 120.9274 | 120.9549 | 121.0785 | -0.01831
2395.5938 | 121.1746 | -121.0236 | 0.10986 | 0.0054168 | 0.0019952 | 0.070226 | 0.028433 | -0.068255 | -0.02609 | 0.0010018 | 0.014954 | 0.048405 | 0.031922 | -0.047599 | -0.0086816 | 0.015018 | 0.068665 | 0.13733 | 0.16479 | 0.16022 | 0.050354 | 0.10071 | -0.050354 | 0.073242 | 0.1831 | 0.036621 | -0.018311 | 0.013733 | 0.09613 | 0.045776 | 121.1243 | 120.9732 | -0.059509 | 121.1609 | 121.1838 | 0.21057 | -0.041198 | 121.1197 | 121.0693 | -0.12817 | 121.0968 | 121.0602 | -0.009155 | -0.09613 | 121.0739 | 121.0922 | 121.1884 | -0.16022 | 121.0052 | 121.0373 | 121.2067 | -0.064087
2397.375 | 121.2067 | -121.0693 | 0.086975 | 0.020676 | 0.00028619 | 0.072149 | 0.02822 | -0.067828 | -0.020749 | 0.00014745 | 0.022583 | 0.052677 | 0.034272 | -0.043968 | -0.0048364 | 0.012241 | 0.07782 | 0.07782 | 0.073242 | 0.11444 | 0.10529 | 0.050354 | -0.059509 | 0.045776 | 0.068665 | -0.059509 | 0.032043 | 0.027466 | 0.082397 | 0.009155 | 121.1197 | 121.0098 | 0.018311 | 121.1472 | 121.1838 | 0.17395 | -0.009155 | 121.1517 | 121.0785 | -0.054932 | 121.1151 | 121.0098 | -0.068664 | -0.059509 | 121.1746 | 121.1472 | 121.1426 | -0.14648 | 121.1014 | 121.0968 | 121.138 | -0.07782
2399.1719 | 121.2021 | -120.9869 | 0.1831 | 0.0054168 | 0.0026362 | 0.071508 | 0.029715 | -0.068255 | -0.027371 | 0.00036105 | 0.014954 | 0.14624 | 0.12421 | -0.049308 | -0.0071862 | 0.01694 | 0.07782 | 0.11902 | 0.13733 | 0.15106 | 0.086975 | 0.09613 | -0.050354 | 0.068665 | 0.14648 | 0.018311 | 0.07782 | 0.10071 | 0.11902 | 0.036621 | 121.0831 | 120.9366 | -0.09613 | 121.106 | 121.138 | 0.20142 | -0.10528 | 121.106 | 121.0236 | -0.10528 | 121.0556 | 121.0052 | -0.01831 | -0.082397 | 121.0739 | 121.0648 | 121.1243 | -0.23346 | 121.0648 | 121.0876 | 121.1334 | -0.14648
2400.9062 | 121.2387 | -121.1105 | 0.07782 | 0.013046 | 0.0034906 | 0.065527 | 0.030997 | -0.066332 | -0.020963 | 0.0022836 | 0.0073242 | 0.0546 | 0.036835 | -0.043968 | -0.006759 | 0.01395 | 0.059509 | 0.050354 | 0.082397 | 0.1236 | 0.09613 | 0.054932 | -0.073242 | 0.045776 | 0.10071 | -0.054932 | 0.022888 | 0.013733 | 0.091553 | 0.032043 | 121.1655 | 121.0373 | 0.01831 | 121.1609 | 121.2341 | 0.19684 | -0.018311 | 121.2021 | 121.1426 | -0.054932 | 121.1563 | 121.0556 | -0.086975 | -0.064087 | 121.2067 | 121.17 | 121.1929 | -0.15106 | 121.1334 | 121.1243 | 121.2112 | -0.045777
2402.6875 | 121.3715 | -121.0602 | 0.050354 | 0.0054168 | 0.0039178 | 0.071081 | 0.024802 | -0.067614 | -0.025662 | 0.0014292 | 0.0073242 | 0.049687 | 0.031067 | -0.045463 | -0.0054772 | 0.014163 | 0.07782 | 0.12817 | 0.14191 | 0.16479 | 0.050354 | 0.091553 | -0.032043 | 0.10071 | 0.13275 | 0.009155 | -0.018311 | 0 | 0.1236 | 0.041199 | 121.1517 | 121.0281 | 0 | 121.1884 | 121.225 | 0.19684 | 0.027466 | 121.1838 | 121.1014 | -0.068665 | 121.1609 | 121.0693 | -0.032044 | -0.050354 | 121.1105 | 121.138 | 121.2021 | -0.082397 | 121.0419 | 121.0602 | 121.1929 | -0.009155
2404.4844 | 121.3989 | -121.1288 | 0.073242 | 0.0054168 | 0.0037042 | 0.072149 | 0.027152 | -0.066973 | -0.030362 | -0.001348 | 0.0073242 | 0.049687 | 0.032349 | -0.045463 | -0.0088952 | 0.014377 | 0.009155 | 0.059509 | 0.091553 | 0.11902 | 0.07782 | 0.082397 | -0.064087 | 0.032043 | 0.11444 | -0.004578 | -0.004578 | 0.032043 | 0.11444 | 0.045776 | 121.2112 | 121.0648 | 0.004578 | 121.1884 | 121.2479 | 0.18311 | -0.064087 | 121.2433 | 121.1746 | -0.07782 | 121.1609 | 121.1243 | -0.050354 | -0.041199 | 121.2067 | 121.138 | 121.2204 | -0.13733 | 121.1243 | 121.1609 | 121.2433 | -0.027466
2406.2031 | 121.2662 | -121.1426 | 0.086975 | 0.0054168 | 0.0058404 | 0.066167 | 0.029074 | -0.066332 | -0.019895 | 0.00207 | 0.014954 | 0.055882 | 0.036194 | -0.043113 | -0.0041956 | 0.012241 | 0.018311 | -0.027466 | 0.032043 | 0.082397 | 0.10071 | 0.059509 | -0.064087 | -0.027466 | -0.004578 | -0.14191 | 0.022888 | 0.054932 | 0.068665 | 0.022888 | 121.2021 | 121.0785 | 0.013733 | 121.1151 | 121.225 | 0.14648 | -0.068664 | 121.2112 | 121.1655 | -0.064087 | 121.1151 | 121.0007 | -0.16479 | -0.032043 | 121.2433 | 121.1609 | 121.1746 | -0.15106 | 121.1655 | 121.1975 | 121.138 | -0.064087
2407.9688 | 121.3623 | -121.1334 | 0.07782 | 0.0054168 | 0.0013544 | 0.068731 | 0.027792 | -0.068468 | -0.027799 | -6.615e-05 | 0.014954 | 0.053105 | 0.037262 | -0.046531 | -0.0080408 | 0.015872 | 0.082397 | 0.10986 | 0.13733 | 0.14191 | 0.059509 | 0.10071 | -0.027466 | 0.050354 | 0.10986 | 0.013733 | -0.018311 | -0.013733 | 0.10529 | 0.036621 | 121.2341 | 121.106 | -0.018311 | 121.2433 | 121.2753 | 0.16937 | 0.004577 | 121.2387 | 121.17 | -0.096131 | 121.1838 | 121.1472 | -0.022888 | -0.091553 | 121.1929 | 121.2158 | 121.2708 | -0.10529 | 121.1151 | 121.1197 | 121.2433 | -0.041199
2409.6875 | 121.344 | -121.1792 | 0.073242 | 0.013046 | 0.0019952 | 0.06809 | 0.026297 | -0.067828 | -0.022244 | 0.0016428 | 0.014954 | 0.055241 | 0.034699 | -0.04525 | -0.0035546 | 0.0098907 | 0.054932 | 0.059509 | 0.07782 | 0.1236 | 0.11902 | 0.054932 | -0.064087 | 0.050354 | 0.068665 | -0.059509 | 0.009155 | 0.027466 | 0.07782 | 0.004578 | 121.2341 | 121.1151 | 0.045777 | 121.2387 | 121.3028 | 0.18768 | -0.01831 | 121.257 | 121.1838 | -0.064087 | 121.2296 | 121.1197 | -0.064087 | -0.045776 | 121.2982 | 121.2341 | 121.257 | -0.13733 | 121.1884 | 121.2067 | 121.2479 | -0.068664
2411.4844 | 121.4722 | -121.1563 | 0.064087 | 0.013046 | 0.003277 | 0.068945 | 0.027792 | -0.067614 | -0.030149 | -0.00049335 | 0.014954 | 0.050114 | 0.032563 | -0.047813 | -0.0080408 | 0.015659 | 0.059509 | 0.1236 | 0.14191 | 0.14191 | 0.07782 | 0.082397 | -0.045776 | 0.082397 | 0.16937 | 0.054932 | -0.013733 | 0.018311 | 0.11902 | 0.036621 | 121.2387 | 121.1105 | 0.013733 | 121.2799 | 121.2982 | 0.18768 | -0.004578 | 121.2753 | 121.1929 | -0.07782 | 121.2387 | 121.2112 | 0.018311 | -0.045776 | 121.2341 | 121.2158 | 121.2982 | -0.10986 | 121.1426 | 121.1746 | 121.3257 | -0.027466
2413.2656 | 121.344 | -121.2112 | 0.082397 | 0.013046 | 0.0022088 | 0.069158 | 0.026297 | -0.06975 | -0.019681 | 0.0018564 | -0.0003053 | 0.0593 | 0.03833 | -0.044395 | -0.0024866 | 0.014163 | 0 | -0.032043 | 0.004578 | 0.07782 | 0.10071 | 0.059509 | -0.068665 | -0.018311 | -0.013733 | -0.1236 | 0.036621 | 0.041199 | 0.068665 | 0.022888 | 121.2708 | 121.1426 | 0.018311 | 121.1792 | 121.2891 | 0.14649 | -0.082397 | 121.2799 | 121.2341 | -0.045776 | 121.1929 | 121.0876 | -0.14648 | -0.041198 | 121.312 | 121.2112 | 121.2158 | -0.15106 | 121.2479 | 121.2524 | 121.1975 | -0.059509
2415.0469 | 121.3394 | -121.2341 | 0.10071 | 0.013046 | 0.00049979 | 0.07044 | 0.026511 | -0.069323 | -0.025449 | -0.00027975 | 0.030213 | 0.084294 | 0.062683 | -0.04589 | -0.0076136 | 0.015872 | 0.027466 | 0.036621 | 0.059509 | 0.10071 | 0.09613 | 0.064087 | -0.073242 | -0.022888 | 0.068665 | -0.068665 | 0.045776 | 0.059509 | 0.086975 | 0.018311 | 121.2982 | 121.1609 | -0.004578 | 121.2708 | 121.3348 | 0.17395 | -0.073242 | 121.3211 | 121.2524 | -0.054932 | 121.2112 | 121.1655 | -0.086976 | -0.041199 | 121.3303 | 121.2616 | 121.2936 | -0.17395 | 121.2799 | 121.2936 | 121.3028 | -0.082397
2416.75 | 121.4996 | -121.2021 | 0.059509 | 0.013046 | 0.0019952 | 0.070867 | 0.022452 | -0.068682 | -0.023953 | 0.0018564 | 0.014954 | 0.052677 | 0.031281 | -0.046104 | -0.0044092 | 0.014163 | 0.11902 | 0.1236 | 0.14191 | 0.16479 | 0.073242 | 0.086975 | -0.027466 | 0.086975 | 0.15106 | 0.022888 | -0.027466 | 0.013733 | 0.11902 | 0.027466 | 121.2891 | 121.1746 | 0.013733 | 121.3257 | 121.3669 | 0.19226 | 0.05951 | 121.3211 | 121.2296 | -0.086975 | 121.2891 | 121.225 | -0.004578 | -0.045776 | 121.2753 | 121.3211 | 121.344 | -0.086975 | 121.1746 | 121.2158 | 121.3531 | -0.032043
2418.5469 | 121.4355 | -121.2387 | 0.086975 | 0.013046 | 0.0037042 | 0.068945 | 0.032706 | -0.068682 | -0.028653 | 0.00057465 | 0.0073242 | 0.050755 | 0.034699 | -0.047172 | -0.0093226 | 0.014804 | 0.09613 | 0.13733 | 0.16937 | 0.17853 | 0.050354 | 0.082397 | -0.045776 | 0.07782 | 0.18768 | 0.045776 | -0.018311 | 0.018311 | 0.091553 | 0.032043 | 121.3211 | 121.1929 | -0.036621 | 121.376 | 121.4172 | 0.2243 | 0.009155 | 121.3303 | 121.2708 | -0.10529 | 121.3165 | 121.2845 | 0.013733 | -0.068664 | 121.2891 | 121.3348 | 121.4081 | -0.13275 | 121.2204 | 121.257 | 121.4264 | -0.054932
2420.3281 | 121.5134 | -121.2296 | 0.07782 | 0.013046 | 0.001568 | 0.069158 | 0.029288 | -0.066332 | -0.028012 | -0.00070715 | -0.0003053 | 0.049473 | 0.034699 | -0.044181 | -0.0082544 | 0.0116 | 0.10986 | 0.15106 | 0.16937 | 0.16937 | 0.054932 | 0.10071 | -0.059509 | 0.086975 | 0.19226 | 0.045776 | -0.004578 | -0.004578 | 0.11444 | 0.054932 | 121.3303 | 121.17 | -0.022888 | 121.3806 | 121.3989 | 0.22888 | 0.032043 | 121.344 | 121.2845 | -0.082398 | 121.3165 | 121.2753 | -0.009156 | -0.082398 | 121.2845 | 121.3394 | 121.3989 | -0.13733 | 121.225 | 121.225 | 121.4218 | -0.022888
2422.0469 | 121.5179 | -121.2296 | 0.059509 | -0.0022127 | 0.0011408 | 0.069372 | 0.023947 | -0.069964 | -0.019681 | 0.0010018 | 0.014954 | 0.053105 | 0.035767 | -0.043327 | -0.0029138 | 0.012027 | 0.054932 | 0.018311 | 0.07782 | 0.10529 | 0.082397 | 0.068665 | -0.041199 | 0.07782 | 0.09613 | -0.009155 | 0.004578 | 0.022888 | 0.10071 | 0.045776 | 121.2982 | 121.1884 | 0.022888 | 121.2479 | 121.3348 | 0.14649 | -0.004577 | 121.3303 | 121.2753 | -0.054931 | 121.3074 | 121.2204 | -0.054931 | -0.036621 | 121.3119 | 121.2845 | 121.3074 | -0.10071 | 121.2341 | 121.2524 | 121.3257 | -0.013733
2423.8281 | 121.4676 | -121.2708 | 0.10529 | 0.0054168 | -0.00056821 | 0.069585 | 0.028647 | -0.068896 | -0.020749 | 0.0022836 | -0.0003053 | 0.055668 | 0.037262 | -0.044609 | -0.0041956 | 0.013309 | 0.036621 | 0.009155 | 0.036621 | 0.10529 | 0.091553 | 0.064087 | -0.082397 | 0.032043 | 0.064087 | -0.064087 | 0.018311 | 0.050354 | 0.07782 | -0.004578 | 121.3348 | 121.1884 | -0.013733 | 121.2799 | 121.376 | 0.18768 | -0.068665 | 121.3486 | 121.2662 | -0.086975 | 121.3028 | 121.2067 | -0.059509 | -0.054932 | 121.3623 | 121.3074 | 121.3074 | -0.18768 | 121.2891 | 121.3211 | 121.3348 | -0.10986
2425.5625 | 121.4355 | -121.2982 | 0.10071 | 0.013046 | 0.00092719 | 0.071081 | 0.02886 | -0.068255 | -0.024594 | -6.615e-05 | 0.0073242 | 0.049259 | 0.034058 | -0.045677 | -0.0069726 | 0.015018 | 0.045776 | 0.082397 | 0.10529 | 0.1236 | 0.086975 | 0.068665 | -0.059509 | 0.004578 | 0.082397 | -0.068665 | 0.027466 | 0.050354 | 0.07782 | -0.004578 | 121.3669 | 121.2387 | -0.013733 | 121.3806 | 121.4218 | 0.1831 | -0.054932 | 121.376 | 121.2936 | -0.073242 | 121.3028 | 121.2296 | -0.064087 | -0.050354 | 121.3852 | 121.344 | 121.4035 | -0.16022 | 121.3257 | 121.3486 | 121.3806 | -0.10529
2427.3438 | 121.4127 | -121.3028 | 0.091553 | 0.020676 | 0.0017816 | 0.067876 | 0.028006 | -0.068682 | -0.021176 | 0.0024972 | 0.0073242 | 0.055241 | 0.035126 | -0.044609 | -0.0018458 | 0.014591 | 0.027466 | -0.004578 | 0.032043 | 0.086975 | 0.10071 | 0.059509 | -0.07782 | 0.004578 | 0.009155 | -0.1236 | 0.032043 | 0.027466 | 0.086975 | 0.009155 | 121.3623 | 121.225 | 0.009155 | 121.2982 | 121.3898 | 0.16479 | -0.064087 | 121.3898 | 121.312 | -0.05951 | 121.3074 | 121.1792 | -0.13275 | -0.064087 | 121.4035 | 121.3303 | 121.3348 | -0.16937 | 121.3348 | 121.3303 | 121.312 | -0.082398
2429.1406 | 121.5179 | -121.2982 | 0.10071 | -0.0098417 | 7.2586e-05 | 0.07044 | 0.024161 | -0.0674 | -0.023526 | -0.00027975 | 0.0073242 | 0.052677 | 0.033631 | -0.044609 | -0.0027002 | 0.014804 | 0.032043 | 0.045776 | 0.059509 | 0.10529 | 0.10529 | 0.059509 | -0.07782 | 0.032043 | 0.068665 | -0.054932 | 0.004578 | 0.032043 | 0.059509 | 0.009155 | 121.3577 | 121.2204 | 0.004578 | 121.344 | 121.4035 | 0.18311 | -0.068665 | 121.3577 | 121.3074 | -0.09613 | 121.3303 | 121.2433 | -0.064087 | -0.068665 | 121.4035 | 121.3303 | 121.3577 | -0.17853 | 121.3028 | 121.3303 | 121.3669 | -0.091553
2430.9531 | 121.5042 | -121.3348 | 0.086975 | 0.020676 | 0.0028498 | 0.067236 | 0.025229 | -0.070177 | -0.023313 | 0.00078825 | 0.014954 | 0.053532 | 0.034058 | -0.042686 | -0.0063318 | 0.013522 | -0.013733 | -0.041199 | 0.013733 | 0.07782 | 0.10071 | 0.050354 | -0.068665 | -0.041199 | -0.018311 | -0.1236 | 0.022888 | 0.064087 | 0.07782 | 0.004578 | 121.3852 | 121.2662 | 0.013733 | 121.2936 | 121.4127 | 0.14649 | -0.10071 | 121.4127 | 121.3394 | -0.064087 | 121.2936 | 121.2112 | -0.12817 | -0.022888 | 121.4355 | 121.3211 | 121.3486 | -0.15564 | 121.3577 | 121.3989 | 121.3165 | -0.082397
2432.6719 | 121.5042 | -121.3531 | 0.09613 | 0.013046 | -0.00014101 | 0.069158 | 0.029501 | -0.070177 | -0.027158 | 0.00036105 | 0.0073242 | 0.050755 | 0.033631 | -0.04525 | -0.010177 | 0.015872 | -0.013733 | 0.004578 | 0.041199 | 0.073242 | 0.07782 | 0.041199 | -0.086975 | -0.036621 | 0.045776 | -0.09613 | 0.045776 | 0.050354 | 0.064087 | -0.013733 | 121.3943 | 121.2662 | -0.01831 | 121.3577 | 121.4264 | 0.16022 | -0.10986 | 121.4172 | 121.3394 | -0.050354 | 121.3165 | 121.257 | -0.082397 | -0.045776 | 121.431 | 121.3394 | 121.3943 | -0.1831 | 121.3989 | 121.4035 | 121.3989 | -0.10986
2434.4688 | 121.55 | -121.3348 | 0.09613 | 0.013046 | 0.0037042 | 0.070654 | 0.029288 | -0.067614 | -0.027585 | -0.0011344 | -0.0003053 | 0.049473 | 0.032135 | -0.048027 | -0.0076136 | 0.014377 | 0.091553 | 0.16479 | 0.17853 | 0.16479 | 0.059509 | 0.086975 | -0.032043 | 0.064087 | 0.19684 | 0.045776 | -0.009155 | 0.004578 | 0.09613 | 0.050354 | 121.4218 | 121.3028 | -0.036621 | 121.4996 | 121.4996 | 0.19684 | -0.004577 | 121.431 | 121.3852 | -0.10528 | 121.3989 | 121.3806 | -0.004578 | -0.091552 | 121.3943 | 121.4264 | 121.5134 | -0.12817 | 121.3257 | 121.3394 | 121.5317 | -0.045776
2436.2656 | 121.5683 | -121.3394 | 0.082397 | -0.0022127 | 0.0022088 | 0.071081 | 0.028006 | -0.072314 | -0.027585 | -6.615e-05 | -0.0079343 | 0.051182 | 0.032563 | -0.046318 | -0.0071862 | 0.014804 | 0.068665 | 0.10986 | 0.15106 | 0.11902 | 0.045776 | 0.091553 | -0.036621 | 0.032043 | 0.10529 | -0.004578 | -0.018311 | 0.004578 | 0.10986 | 0.041199 | 121.431 | 121.3028 | -0.036621 | 121.4493 | 121.4584 | 0.15564 | -0.013732 | 121.4493 | 121.3806 | -0.10071 | 121.3715 | 121.3348 | -0.045777 | -0.077819 | 121.3852 | 121.4081 | 121.4905 | -0.11902 | 121.3211 | 121.344 | 121.4447 | -0.041198
2438.0625 | 121.6095 | -121.3211 | 0.059509 | 0.0054168 | 0.0017816 | 0.069585 | 0.029929 | -0.067828 | -0.022031 | -0.00027975 | -0.0003053 | 0.053105 | 0.03299 | -0.043968 | -0.0044092 | 0.012668 | 0.013733 | -0.004578 | 0.022888 | 0.068665 | 0.10071 | 0.045776 | -0.073242 | 0 | 0.022888 | -0.082397 | 0.018311 | 0.041199 | 0.050354 | 0.013733 | 121.3669 | 121.2479 | 0.041199 | 121.3165 | 121.3898 | 0.14191 | -0.045776 | 121.3715 | 121.3348 | -0.041198 | 121.3211 | 121.2387 | -0.09613 | -0.01831 | 121.4218 | 121.3348 | 121.344 | -0.13275 | 121.3394 | 121.3623 | 121.344 | -0.045776
2439.8594 | 121.6324 | -121.3577 | 0.073242 | -0.0022127 | 0.0024224 | 0.07279 | 0.028433 | -0.06975 | -0.02844 | -6.615e-05 | 0.0073242 | 0.050968 | 0.035767 | -0.045036 | -0.0086816 | 0.016513 | 0.064087 | 0.13733 | 0.15106 | 0.15106 | 0.07782 | 0.091553 | -0.050354 | 0.07782 | 0.17395 | 0.059509 | 0.013733 | 0.013733 | 0.13275 | 0.059509 | 121.4493 | 121.3074 | 0.004578 | 121.4951 | 121.5088 | 0.20142 | -0.009155 | 121.4905 | 121.4172 | -0.059509 | 121.4355 | 121.4172 | 0 | -0.059509 | 121.4355 | 121.4218 | 121.5088 | -0.1236 | 121.3715 | 121.3715 | 121.5317 | -0.013733
2441.5781 | 121.5775 | -121.3943 | 0.10071 | 0.0054168 | -0.0014228 | 0.070013 | 0.030142 | -0.064837 | -0.021817 | 0.0012154 | 0.0073242 | 0.055241 | 0.034699 | -0.04525 | -0.0041956 | 0.012027 | 0.022888 | -0.013733 | 0.009155 | 0.082397 | 0.12817 | 0.050354 | -0.07782 | -0.013733 | 0.045776 | -0.09613 | 0.041199 | 0.050354 | 0.082397 | 0 | 121.4447 | 121.3165 | 0.027466 | 121.3806 | 121.4767 | 0.16022 | -0.07782 | 121.4767 | 121.3943 | -0.059509 | 121.3806 | 121.2982 | -0.09613 | -0.050354 | 121.5225 | 121.4172 | 121.4035 | -0.17853 | 121.4355 | 121.4447 | 121.4401 | -0.10071
2443.3594 | 121.5637 | -121.3943 | 0.091553 | 0.0054168 | 0.00028619 | 0.068731 | 0.022665 | -0.065905 | -0.022458 | -0.00027975 | 0.014954 | 0.053532 | 0.030213 | -0.045036 | -0.003341 | 0.013736 | 0.059509 | 0.059509 | 0.068665 | 0.10529 | 0.11444 | 0.054932 | -0.073242 | 0.050354 | 0.086975 | -0.059509 | 0.013733 | 0.041199 | 0.07782 | 0.013733 | 121.4493 | 121.3211 | 0.022888 | 121.4539 | 121.4996 | 0.17853 | -0.032044 | 121.4722 | 121.4081 | -0.07782 | 121.4447 | 121.3348 | -0.073242 | -0.050354 | 121.5088 | 121.4539 | 121.463 | -0.16479 | 121.4081 | 121.4355 | 121.4813 | -0.07782
2445.0938 | 121.5683 | -121.4172 | 0.091553 | 0.0054168 | 0.004986 | 0.068731 | 0.027792 | -0.068255 | -0.022885 | 0.00207 | 0.014954 | 0.054173 | 0.03534 | -0.046104 | -0.003341 | 0.014377 | 0.004578 | -0.027466 | 0.022888 | 0.073242 | 0.10071 | 0.054932 | -0.073242 | -0.027466 | -0.009155 | -0.11444 | 0.018311 | 0.041199 | 0.073242 | 0.009155 | 121.4722 | 121.344 | 0.009155 | 121.3898 | 121.4905 | 0.14648 | -0.086975 | 121.4905 | 121.4264 | -0.073242 | 121.3898 | 121.3028 | -0.1236 | -0.050354 | 121.5179 | 121.4218 | 121.4401 | -0.16479 | 121.4355 | 121.4584 | 121.4081 | -0.082398
2446.8906 | 121.6187 | -121.4035 | 0.073242 | 0.0054168 | 0.00049979 | 0.067663 | 0.028006 | -0.067828 | -0.023526 | 0.0010018 | 0.0073242 | 0.055454 | 0.038758 | -0.045036 | -0.0054772 | 0.014163 | 0.032043 | 0.054932 | 0.064087 | 0.10071 | 0.091553 | 0.036621 | -0.059509 | 0.041199 | 0.082397 | -0.059509 | 0.018311 | 0.050354 | 0.07782 | 0.018311 | 121.4401 | 121.344 | 0.018311 | 121.4584 | 121.5042 | 0.16022 | -0.041199 | 121.4813 | 121.4218 | -0.054931 | 121.4447 | 121.344 | -0.07782 | -0.022888 | 121.4951 | 121.4355 | 121.4676 | -0.13275 | 121.4218 | 121.4539 | 121.4859 | -0.054931
2448.6875 | 121.7148 | -121.4127 | 0.091553 | 0.0054168 | 0.0026362 | 0.070867 | 0.029929 | -0.069537 | -0.030149 | 0.00057465 | 0.014954 | 0.05695 | 0.04068 | -0.046104 | -0.0093226 | 0.015659 | 0.086975 | 0.16479 | 0.17853 | 0.16937 | 0.064087 | 0.086975 | -0.041199 | 0.086975 | 0.19684 | 0.041199 | -0.018311 | 0.004578 | 0.1236 | 0.050354 | 121.4996 | 121.3715 | -0.027466 | 121.5775 | 121.582 | 0.21057 | -0.004578 | 121.5363 | 121.463 | -0.10986 | 121.4996 | 121.4539 | -0.009155 | -0.086975 | 121.4767 | 121.4996 | 121.5912 | -0.13275 | 121.3943 | 121.4172 | 121.6095 | -0.041199
2450.5 | 121.701 | -121.3898 | 0.054932 | 0.013046 | 0.0028498 | 0.070226 | 0.022665 | -0.067828 | -0.023953 | -0.00049335 | 0.0073242 | 0.060154 | 0.041107 | -0.046104 | -0.0061182 | 0.014591 | 0.10071 | 0.10986 | 0.14191 | 0.15564 | 0.082397 | 0.09613 | -0.027466 | 0.091553 | 0.15106 | 0.018311 | -0.013733 | 0.018311 | 0.11902 | 0.064087 | 121.4859 | 121.3623 | 0.027465 | 121.4996 | 121.5454 | 0.18311 | 0.045776 | 121.5088 | 121.4539 | -0.068665 | 121.4813 | 121.4081 | -0.045776 | -0.036621 | 121.4722 | 121.4905 | 121.5317 | -0.082398 | 121.376 | 121.4081 | 121.5408 | 0.009155
2452.2969 | 121.5363 | -121.4676 | 0.086975 | 0.0054168 | 0.00071339 | 0.071508 | 0.02587 | -0.068896 | -0.021817 | 0.003138 | 0.014954 | 0.061436 | 0.040253 | -0.045677 | -0.0044092 | 0.014804 | 0.009155 | 0.009155 | 0.018311 | 0.086975 | 0.086975 | 0.059509 | -0.07782 | -0.018311 | 0.009155 | -0.11444 | 0.013733 | 0.059509 | 0.068665 | -0.004578 | 121.5271 | 121.3898 | 0 | 121.4767 | 121.5546 | 0.16479 | -0.07782 | 121.5363 | 121.463 | -0.073242 | 121.4493 | 121.3531 | -0.10986 | -0.027466 | 121.5546 | 121.4767 | 121.4859 | -0.16479 | 121.4813 | 121.5271 | 121.4767 | -0.091553
2454.0938 | 121.6049 | -121.4447 | 0.086975 | 0.0054168 | 0.0011408 | 0.071081 | 0.027152 | -0.0674 | -0.02908 | -0.0022024 | -0.0003053 | 0.06165 | 0.04538 | -0.047813 | -0.006759 | 0.016727 | 0.091553 | 0.16022 | 0.16022 | 0.17853 | 0.059509 | 0.082397 | -0.036621 | 0.082397 | 0.16937 | 0.050354 | 0.013733 | 0.022888 | 0.10529 | 0.041199 | 121.5271 | 121.4081 | -0.027466 | 121.6049 | 121.6232 | 0.21515 | 0.004578 | 121.55 | 121.4859 | -0.073242 | 121.5271 | 121.4951 | 0.009155 | -0.064087 | 121.5042 | 121.5363 | 121.6049 | -0.1236 | 121.4584 | 121.4676 | 121.6141 | -0.045776
2455.8125 | 114.9078 | -105.0705 | 9.9014 | 0.0054168 | -0.0020636 | 0.068304 | 0.029288 | -0.068896 | -0.02374 | 0.00014745 | 0.014954 | 7.0044 | 7.0272 | -0.22021 | -0.0082544 | 0.18357 | 0.16022 | 0.14191 | 0.16937 | 0.23346 | 0.25635 | 0.20599 | 0.07782 | 3.8406 | 3.7262 | 3.7674 | 7.2647 | 7.2601 | 3.9963 | 3.9505 | 105.2765 | 105.1483 | -9.6451 | 105.2124 | 105.304 | 0.15564 | -9.7412 | 109.0668 | 109.021 | -2.6367 | 108.9111 | 108.8379 | -0.1831 | -2.6413 | 105.3268 | 105.2307 | 105.2399 | -9.8236 | 112.3352 | 112.3306 | 108.7967 | -5.9509
2457.5938 | 121.2662 | -120.9595 | 0.059509 | 0.013046 | 0.0045588 | 0.070654 | 0.024588 | -0.066973 | -0.025876 | 0.0024972 | -0.0003053 | 0.049046 | 0.027008 | -0.044609 | -0.0046228 | 0.015445 | 0.10071 | 0.1236 | 0.12817 | 0.14191 | 0.07782 | 0.09613 | -0.041199 | 0.086975 | 0.10529 | 0.013733 | -0.018311 | 0.004578 | 0.1236 | 0.036621 | 121.0556 | 120.9183 | 0.018311 | 121.0831 | 121.1014 | 0.18311 | 0.041199 | 121.0831 | 120.9961 | -0.07782 | 121.0464 | 120.9732 | -0.022888 | -0.054931 | 121.0373 | 121.0602 | 121.0876 | -0.10071 | 120.9412 | 120.9641 | 121.0648 | -0.022888
2459.3125 | 121.257 | -121.0876 | 0.09613 | 0.0054168 | -0.00056821 | 0.070226 | 0.026083 | -0.06975 | -0.021817 | -0.00070715 | 0.022583 | 0.055241 | 0.034058 | -0.045677 | -0.0082544 | 0.01395 | 0.059509 | 0.064087 | 0.091553 | 0.10986 | 0.086975 | 0.064087 | -0.07782 | 0.027466 | 0.068665 | -0.068665 | 0.009155 | 0.041199 | 0.086975 | 0.018311 | 121.1517 | 121.0098 | -0.009155 | 121.1517 | 121.1975 | 0.18768 | -0.036621 | 121.1746 | 121.106 | -0.086975 | 121.1151 | 121.019 | -0.086976 | -0.054931 | 121.1746 | 121.1472 | 121.1792 | -0.17395 | 121.0968 | 121.1288 | 121.1563 | -0.077819
2461.1094 | 115.7547 | -109.1583 | 6.3904 | 0.0054168 | 0.00028619 | 0.070013 | 0.031424 | -0.068468 | -0.025876 | -0.0011344 | 0.0073242 | 7.0044 | 7.0272 | -0.1794 | -0.006759 | 0.15259 | 0.1236 | 0.13275 | 0.15564 | 0.21057 | 0.26093 | 0.17853 | 0.054932 | 3.0167 | 2.948 | 3.2272 | 5.8731 | 5.9006 | 3.1998 | 3.1403 | 109.3369 | 109.2133 | -6.1295 | 109.2911 | 109.3689 | 0.15564 | -6.2668 | 112.3581 | 112.2986 | -0.51727 | 112.175 | 112.3856 | 0.086975 | -0.48981 | 109.4193 | 109.2819 | 109.314 | -6.3354 | 115.0314 | 115.0589 | 112.1063 | -3.2501
2462.8281 | 121.0098 | -120.8679 | 0.10071 | 0.013046 | 0.001568 | 0.067876 | 0.025656 | -0.067187 | -0.022672 | 0.00014745 | 0.014954 | 0.062504 | 0.041321 | -0.043968 | -0.0048364 | 0.016086 | -0.027466 | -0.027466 | 0 | 0.082397 | 0.10529 | 0.050354 | -0.064087 | -0.022888 | -0.013733 | -0.11444 | 0.032043 | 0.054932 | 0.07782 | 0.009155 | 120.9183 | 120.8038 | 0.004578 | 120.8405 | 120.9503 | 0.14648 | -0.12817 | 120.9457 | 120.8771 | -0.068665 | 120.845 | 120.7535 | -0.1236 | -0.045776 | 120.9732 | 120.8405 | 120.8679 | -0.1648 | 120.9 | 120.9229 | 120.8542 | -0.091553
2464.625 | 121.1426 | -120.9915 | 0.091553 | -0.0022127 | -0.00014101 | 0.070226 | 0.02822 | -0.0674 | -0.026944 | -6.615e-05 | 0.014954 | 0.062931 | 0.041535 | -0.045463 | -0.003341 | 0.014804 | -0.004578 | 0.018311 | 0.027466 | 0.10529 | 0.10071 | 0.050354 | -0.07782 | -0.004578 | 0.073242 | -0.082397 | 0.013733 | 0.050354 | 0.068665 | 0.018311 | 121.0419 | 120.9137 | 0.009155 | 121.0098 | 121.0968 | 0.18311 | -0.096131 | 121.0602 | 121.0098 | -0.07782 | 120.9869 | 120.9091 | -0.10071 | -0.041199 | 121.0922 | 120.9869 | 121.019 | -0.16937 | 121.0052 | 121.0419 | 121.0648 | -0.073242
2466.4219 | 121.1517 | -121.0556 | 0.11902 | 0.013046 | 0.0028498 | 0.071294 | 0.03121 | -0.069537 | -0.027585 | -0.0019888 | 0.0073242 | 0.0593 | 0.040253 | -0.044822 | -0.0082544 | 0.014377 | 0.036621 | 0.064087 | 0.091553 | 0.11902 | 0.073242 | 0.050354 | -0.068665 | -0.018311 | 0.059509 | -0.059509 | 0.036621 | 0.041199 | 0.082397 | 0.018311 | 121.106 | 120.9869 | -0.045777 | 121.1197 | 121.1746 | 0.18768 | -0.082398 | 121.138 | 121.0739 | -0.082398 | 121.0373 | 120.9961 | -0.07782 | -0.07782 | 121.1288 | 121.0922 | 121.1472 | -0.18768 | 121.0922 | 121.0968 | 121.1151 | -0.10071
2468.1562 | 121.3257 | -121.019 | 0.082397 | 0.013046 | 0.001568 | 0.071081 | 0.032492 | -0.071032 | -0.029935 | -0.0026298 | 0.0073242 | 0.058232 | 0.042816 | -0.046745 | -0.0091088 | 0.013309 | 0.027466 | 0.082397 | 0.11902 | 0.11444 | 0.064087 | 0.086975 | -0.027466 | 0.036621 | 0.14191 | 0.032043 | 0 | 0.013733 | 0.10986 | 0.036621 | 121.106 | 120.9915 | -0.01831 | 121.1014 | 121.1334 | 0.14191 | -0.054931 | 121.1288 | 121.0556 | -0.082397 | 121.0556 | 121.051 | -0.004578 | -0.068664 | 121.0831 | 121.0464 | 121.138 | -0.10986 | 121.019 | 121.0327 | 121.1609 | -0.045776
2469.9531 | 121.3028 | -121.0556 | 0.07782 | 0.020676 | 0.0047724 | 0.069372 | 0.026083 | -0.069109 | -0.025449 | 0.0014292 | 0.0073242 | 0.099461 | 0.10178 | -0.043113 | -0.0061182 | 0.013736 | 0.11444 | 0.11444 | 0.16479 | 0.16479 | 0.050354 | 0.10071 | -0.032043 | 0.10071 | 0.14648 | 0.022888 | 0.027466 | 0.013733 | 0.13275 | 0.054932 | 121.1563 | 121.0236 | -0.027466 | 121.17 | 121.2204 | 0.19684 | 0.036621 | 121.1884 | 121.1105 | -0.050354 | 121.1563 | 121.0785 | -0.032044 | -0.064087 | 121.106 | 121.17 | 121.2204 | -0.10986 | 121.0831 | 121.0693 | 121.2021 | -0.022888
2471.75 | 120.9824 | -120.6024 | 0.10071 | -0.0022127 | 0.001568 | 0.069799 | 0.026297 | -0.069323 | -0.021817 | 0.00014745 | 0.014954 | 0.10843 | 0.087464 | -0.042472 | -0.005691 | 0.013522 | 0.013733 | -0.013733 | 0.013733 | 0.059509 | 0.10071 | 0.045776 | -0.073242 | 0.018311 | 0.027466 | -0.064087 | 0.050354 | 0.059509 | 0.09613 | 0.045776 | 120.6482 | 120.5292 | 0 | 120.5887 | 120.6619 | 0.13275 | -0.086975 | 120.6985 | 120.6482 | -0.050354 | 120.6207 | 120.5383 | -0.10986 | -0.041199 | 120.7031 | 120.6162 | 120.6162 | -0.17395 | 120.6528 | 120.6619 | 120.6299 | -0.054932
2473.5469 | 121.2204 | -120.8862 | 0.082397 | 0.013046 | 0.0028498 | 0.071722 | 0.029501 | -0.070605 | -0.02908 | -0.00027975 | 0.0073242 | 0.0499 | 0.035767 | -0.046745 | -0.010818 | 0.014591 | 0.022888 | 0.082397 | 0.1236 | 0.14191 | 0.068665 | 0.073242 | -0.045776 | 0.022888 | 0.11444 | 0.004578 | 0 | 0.009155 | 0.09613 | 0.036621 | 120.9595 | 120.8405 | -0.013732 | 120.9686 | 121.0281 | 0.18768 | -0.059509 | 120.9824 | 120.9229 | -0.082397 | 120.9091 | 120.8908 | -0.032043 | -0.073242 | 120.9549 | 120.9091 | 121.0098 | -0.12817 | 120.8862 | 120.8954 | 121.0007 | -0.045776
2475.3281 | 121.0648 | -120.8679 | 0.19684 | 0.0054168 | 0.00071339 | 0.069799 | 0.027792 | -0.066332 | -0.018613 | 0.0018564 | 0.0073242 | 0.21802 | 0.1947 | -0.047386 | -0.0044092 | 0.015231 | 0.07782 | 0.045776 | 0.07782 | 0.1236 | 0.10529 | 0.068665 | -0.082397 | 0.10986 | 0.13733 | -0.013733 | 0.09613 | 0.11444 | 0.13733 | 0.064087 | 120.9366 | 120.7855 | -0.091552 | 120.9137 | 120.9915 | 0.20599 | -0.11902 | 121.0052 | 120.932 | -0.10071 | 120.9778 | 120.8542 | -0.07782 | -0.082397 | 120.9732 | 120.9457 | 120.9457 | -0.27924 | 120.9641 | 120.9824 | 121.0052 | -0.13275
2477.0469 | 121.1014 | -120.0668 | 0.78278 | -0.0022127 | 0.0024224 | 0.071722 | 0.026511 | -0.067614 | -0.029721 | -0.0015616 | 0.014954 | 0.83582 | 0.76785 | -0.053794 | -0.0080408 | 0.024631 | 0.10986 | 0.17853 | 0.16937 | 0.17853 | 0.068665 | 0.10986 | -0.027466 | 0.33417 | 0.43945 | 0.28381 | 0.38452 | 0.40741 | 0.33875 | 0.29297 | 120.1767 | 120.0394 | -0.71411 | 120.2454 | 120.2454 | 0.20599 | -0.67291 | 120.4056 | 120.3598 | -0.39826 | 120.401 | 120.3506 | -0.009156 | -0.37537 | 120.1355 | 120.1767 | 120.2362 | -0.81024 | 120.4514 | 120.4742 | 120.5063 | -0.48981
2478.8281 | 121.3257 | -121.0144 | 0.068665 | 0.013046 | 0.0039178 | 0.071081 | 0.02822 | -0.068041 | -0.02908 | -0.0011344 | 0.0073242 | 0.0546 | 0.034272 | -0.04525 | -0.008468 | 0.015659 | 0.07782 | 0.11444 | 0.13733 | 0.15106 | 0.064087 | 0.086975 | -0.041199 | 0.068665 | 0.15106 | 0.045776 | 0 | 0.022888 | 0.10071 | 0.050354 | 121.1014 | 120.9732 | -0.004578 | 121.1288 | 121.1655 | 0.19226 | 0.009155 | 121.1151 | 121.0648 | -0.068665 | 121.0831 | 121.0602 | -0.004578 | -0.045777 | 121.0785 | 121.0922 | 121.1517 | -0.10986 | 121.0144 | 121.0373 | 121.1655 | -0.018311
2480.625 | 120.8954 | -119.6503 | 1.2726 | 0.013046 | 0.0024224 | 0.071722 | 0.029074 | -0.069964 | -0.025662 | -0.00027975 | -0.0003053 | 1.801 | 1.7268 | -0.070243 | -0.0065454 | 0.036594 | 0.12817 | 0.11444 | 0.13275 | 0.15564 | 0.10071 | 0.11444 | -0.041199 | 0.54932 | 0.57678 | 0.48523 | 0.90179 | 0.92468 | 0.62714 | 0.53558 | 119.7647 | 119.6091 | -1.1719 | 119.7647 | 119.8059 | 0.19684 | -1.1444 | 120.2774 | 120.1859 | -0.37079 | 120.1996 | 120.1355 | -0.050354 | -0.3479 | 119.751 | 119.7784 | 119.783 | -1.3138 | 120.5521 | 120.575 | 120.2271 | -0.737
2482.3438 | 121.2479 | -120.9595 | 0.15564 | 0.0054168 | 0.0037042 | 0.071722 | 0.027579 | -0.070177 | -0.026944 | 0.0014292 | 0.022583 | 0.1471 | 0.12399 | -0.046745 | -0.005691 | 0.014804 | 0.10986 | 0.13275 | 0.15564 | 0.14191 | 0.054932 | 0.09613 | -0.022888 | 0.10529 | 0.13275 | 0.032043 | 0.032043 | 0.045776 | 0.12817 | 0.068665 | 121.0556 | 120.9366 | -0.10071 | 121.0922 | 121.1014 | 0.16479 | -0.045777 | 121.0876 | 121.0281 | -0.1236 | 121.0648 | 120.9915 | -0.036622 | -0.10986 | 121.0144 | 121.0693 | 121.1151 | -0.17853 | 120.9915 | 121.0052 | 121.0922 | -0.086975
2484.125 | 116.6702 | -116.4001 | 0.22888 | -0.0098417 | 0.00092719 | 0.07044 | 0.028006 | -0.066546 | -0.019467 | -0.00070715 | -0.0003053 | 0.54401 | 0.48117 | -0.04589 | -0.003341 | 0.014591 | 0 | -0.022888 | -0.018311 | 0.07782 | 0.09613 | 0.036621 | -0.086975 | 0.068665 | 0.24719 | 0.49896 | -0.07782 | 0.11902 | 0.37994 | 0.45776 | 116.4368 | 116.3132 | -0.13275 | 116.3773 | 116.478 | 0.16479 | -0.22888 | 116.7801 | 116.8579 | -0.3067 | 116.4688 | 116.8991 | 0.041198 | -0.10986 | 116.4963 | 116.4001 | 116.3818 | -0.31586 | 116.3223 | 116.5192 | 116.6473 | 0.22888
2485.8594 | 120.3323 | -118.7073 | 1.7303 | 0.0054168 | 0.0022088 | 0.070013 | 0.027365 | -0.071245 | -0.019895 | 0.00207 | 0.0073242 | 2.4961 | 2.4187 | -0.077293 | -0.0014184 | 0.046848 | 0.11444 | 0.10986 | 0.10986 | 0.1236 | 0.10529 | 0.091553 | -0.041199 | 0.74616 | 0.62714 | 0.58136 | 1.2085 | 1.2268 | 0.75989 | 0.70953 | 118.7988 | 118.6661 | -1.6251 | 118.8171 | 118.8309 | 0.16479 | -1.6159 | 119.4672 | 119.4168 | -0.52185 | 119.4534 | 119.2886 | -0.12817 | -0.50354 | 118.8126 | 118.8217 | 118.8171 | -1.7715 | 119.9158 | 119.9341 | 119.3344 | -1.0208
2487.6406 | 120.9 | -120.1721 | 0.55847 | 0.013046 | 0.0024224 | 0.07279 | 0.027792 | -0.069109 | -0.028653 | 0.0022836 | 0.014954 | 0.78754 | 0.74884 | -0.056999 | -0.0071862 | 0.026553 | 0.013733 | 0.073242 | 0.11902 | 0.11902 | 0.082397 | 0.091553 | -0.054932 | 0.2655 | 0.31586 | 0.22888 | 0.37994 | 0.3891 | 0.32044 | 0.25635 | 120.2637 | 120.1172 | -0.47607 | 120.2454 | 120.2911 | 0.17395 | -0.54474 | 120.4926 | 120.4285 | -0.17853 | 120.4376 | 120.401 | -0.027466 | -0.16937 | 120.2545 | 120.1859 | 120.2911 | -0.6134 | 120.5521 | 120.5612 | 120.488 | -0.30212
2489.4375 | 121.0739 | -120.7169 | 0.16479 | 0.0054168 | 0.0017816 | 0.073003 | 0.027365 | -0.066759 | -0.028226 | 0.00057465 | 0.014954 | 0.23319 | 0.20816 | -0.048454 | -0.008468 | 0.015872 | 0.09613 | 0.13733 | 0.15564 | 0.15106 | 0.068665 | 0.09613 | -0.027466 | 0.15564 | 0.24719 | 0.11902 | 0.064087 | 0.086975 | 0.15564 | 0.09613 | 120.813 | 120.6894 | -0.09613 | 120.8542 | 120.8679 | 0.17853 | -0.068665 | 120.8725 | 120.813 | -0.10071 | 120.8725 | 120.8359 | 0.022889 | -0.07782 | 120.7855 | 120.813 | 120.8725 | -0.19226 | 120.7809 | 120.8038 | 120.9641 | -0.068665
2491.1719 | 120.3049 | -120.0485 | 0.11902 | -0.0022127 | 7.2586e-05 | 0.071722 | 0.02886 | -0.069323 | -0.027371 | -0.003057 | 0.0073242 | 0.083439 | 0.066956 | -0.044822 | -0.0076136 | 0.014591 | 0.12817 | 0.14648 | 0.16479 | 0.16479 | 0.059509 | 0.082397 | -0.045776 | 0.10071 | 0.20599 | 0.054932 | 0.004578 | 0.018311 | 0.11902 | 0.054932 | 120.1309 | 120.0027 | -0.05951 | 120.195 | 120.2133 | 0.21057 | 0.009155 | 120.1675 | 120.1035 | -0.11444 | 120.1492 | 120.1035 | 0 | -0.10071 | 120.108 | 120.1767 | 120.2133 | -0.16479 | 120.0531 | 120.0668 | 120.2545 | -0.064087
2492.9531 | 120.9732 | -120.6894 | 0.068665 | 0.020676 | 0.001568 | 0.077062 | 0.026083 | -0.071032 | -0.028226 | -0.00070715 | 0.0073242 | 0.050755 | 0.031067 | -0.046531 | -0.0054772 | 0.014804 | 0.10986 | 0.13275 | 0.14191 | 0.15106 | 0.073242 | 0.07782 | -0.032043 | 0.082397 | 0.16937 | 0.041199 | -0.013733 | 0.004578 | 0.10071 | 0.032043 | 120.7672 | 120.6573 | 0.004577 | 120.8221 | 120.8405 | 0.18311 | 0.041198 | 120.7901 | 120.7214 | -0.082398 | 120.7718 | 120.7306 | 0.009156 | -0.064087 | 120.7626 | 120.7993 | 120.8313 | -0.10071 | 120.6757 | 120.694 | 120.8588 | -0.036622
2494.6719 | 121.0327 | -120.7489 | 0.09613 | 0.013046 | 0.0056268 | 0.073217 | 0.026724 | -0.06975 | -0.025876 | 0.0010018 | 0.014954 | 0.074894 | 0.055847 | -0.047386 | -0.0054772 | 0.013309 | 0.10986 | 0.1236 | 0.16022 | 0.13733 | 0.059509 | 0.10071 | -0.045776 | 0.09613 | 0.11902 | 0.013733 | 0.004578 | 0.013733 | 0.11902 | 0.045776 | 120.8496 | 120.7031 | -0.036621 | 120.8725 | 120.8862 | 0.18311 | 0.013733 | 120.8679 | 120.7947 | -0.091552 | 120.845 | 120.7626 | -0.032043 | -0.082397 | 120.8084 | 120.8588 | 120.9091 | -0.14191 | 120.7535 | 120.7626 | 120.8679 | -0.050354
2496.4531 | 120.6711 | -120.1401 | 0.35248 | 0.013046 | 0.0037042 | 0.074926 | 0.028433 | -0.06975 | -0.02609 | -0.0011344 | -0.0003053 | 0.51538 | 0.48566 | -0.054222 | -0.0086816 | 0.020786 | 0.064087 | 0.064087 | 0.10986 | 0.11444 | 0.086975 | 0.086975 | -0.036621 | 0.17853 | 0.21973 | 0.12817 | 0.22888 | 0.24719 | 0.24719 | 0.16937 | 120.2271 | 120.1035 | -0.2655 | 120.2042 | 120.2545 | 0.15106 | -0.28839 | 120.3873 | 120.3094 | -0.1236 | 120.3186 | 120.2682 | -0.041199 | -0.10529 | 120.2271 | 120.2042 | 120.2499 | -0.3891 | 120.369 | 120.3873 | 120.3598 | -0.18311
2498.25 | 120.8771 | -120.4605 | 0.22888 | 0.020676 | 0.0037042 | 0.069158 | 0.028006 | -0.068255 | -0.022885 | 0.0010018 | -0.0003053 | 0.20542 | 0.1915 | -0.046531 | -0.0059046 | 0.017795 | 0.13275 | 0.13275 | 0.15106 | 0.14648 | 0.059509 | 0.11444 | -0.022888 | 0.14648 | 0.18768 | 0.086975 | 0.086975 | 0.086975 | 0.15564 | 0.09613 | 120.575 | 120.4376 | -0.16937 | 120.5933 | 120.607 | 0.16937 | -0.096131 | 120.6162 | 120.5566 | -0.14191 | 120.607 | 120.5475 | -0.009155 | -0.14191 | 120.52 | 120.5933 | 120.6116 | -0.25177 | 120.5475 | 120.5475 | 120.6482 | -0.13275
2500.0469 | 120.5521 | -120.2225 | 0.09613 | 0.0054168 | 0.0017816 | 0.069585 | 0.027792 | -0.068896 | -0.025449 | 0.0039926 | -0.0003053 | 0.11548 | 0.095154 | -0.046318 | -0.0082544 | 0.016086 | 0.10529 | 0.11444 | 0.12817 | 0.13275 | 0.059509 | 0.086975 | -0.041199 | 0.082397 | 0.11902 | 0.004578 | 0.032043 | 0.022888 | 0.1236 | 0.041199 | 120.3094 | 120.1813 | -0.036621 | 120.3369 | 120.3552 | 0.17395 | 0.009156 | 120.3461 | 120.2637 | -0.064087 | 120.3049 | 120.2271 | -0.036621 | -0.073242 | 120.282 | 120.3278 | 120.3506 | -0.13733 | 120.2545 | 120.2454 | 120.3415 | -0.054931
2501.7812 | 120.8221 | -120.5429 | 0.09613 | 0.0054168 | 0.0058404 | 0.071722 | 0.02822 | -0.070605 | -0.025449 | -0.00049335 | 0.0073242 | 0.081303 | 0.063538 | -0.045463 | -0.005691 | 0.014377 | 0.086975 | 0.086975 | 0.11902 | 0.11444 | 0.068665 | 0.073242 | -0.041199 | 0.068665 | 0.10071 | -0.013733 | 0.013733 | 0.022888 | 0.10986 | 0.045776 | 120.6161 | 120.5017 | -0.027465 | 120.6299 | 120.6573 | 0.15564 | -0.009155 | 120.6528 | 120.5887 | -0.082397 | 120.6116 | 120.5292 | -0.059509 | -0.073242 | 120.6116 | 120.6299 | 120.6619 | -0.13733 | 120.5566 | 120.5658 | 120.6436 | -0.050354
2503.5781 | 120.6985 | -120.1401 | 0.52643 | 0.0054168 | 0.001568 | 0.067449 | 0.031424 | -0.068041 | -0.024594 | 0.00078825 | 0.014954 | 0.59763 | 0.57645 | -0.053794 | -0.0061182 | 0.020358 | 0.10071 | 0.13275 | 0.16479 | 0.16937 | 0.054932 | 0.086975 | -0.050354 | 0.24719 | 0.31128 | 0.16479 | 0.30212 | 0.33875 | 0.27008 | 0.21973 | 120.2271 | 120.0897 | -0.4715 | 120.2728 | 120.3094 | 0.21973 | -0.42572 | 120.4102 | 120.3598 | -0.2243 | 120.3873 | 120.3049 | -0.054932 | -0.18768 | 120.195 | 120.2408 | 120.3049 | -0.57678 | 120.4422 | 120.4788 | 120.4514 | -0.3067
2505.3594 | 120.639 | -120.5292 | 0.09613 | 0.0054168 | 0.0028498 | 0.073003 | 0.028647 | -0.070177 | -0.024594 | 0.0010018 | 0.0073242 | 0.048619 | 0.032563 | -0.046531 | -0.0054772 | 0.012454 | 0.091553 | 0.10986 | 0.1236 | 0.13733 | 0.068665 | 0.059509 | -0.068665 | 0.032043 | 0.086975 | -0.064087 | 0.013733 | 0.022888 | 0.082397 | 0.009155 | 120.5887 | 120.4605 | -0.027465 | 120.639 | 120.6665 | 0.20599 | -0.004577 | 120.6116 | 120.5383 | -0.082397 | 120.5612 | 120.4651 | -0.073242 | -0.073242 | 120.5978 | 120.6207 | 120.6528 | -0.16479 | 120.5429 | 120.5521 | 120.6161 | -0.086975
2507.1406 | 120.8496 | -120.6482 | 0.073242 | 0.0054168 | -0.00014101 | 0.069158 | 0.027579 | -0.066973 | -0.019681 | -0.00070715 | 0.0073242 | 0.054173 | 0.037262 | -0.043541 | -0.0029138 | 0.011813 | 0.032043 | 0.022888 | 0.027466 | 0.10071 | 0.09613 | 0.032043 | -0.086975 | 0.004578 | 0.059509 | -0.09613 | 0.032043 | 0.045776 | 0.064087 | 0.004578 | 120.6802 | 120.5612 | 0.022888 | 120.6711 | 120.7489 | 0.18768 | -0.041199 | 120.7123 | 120.6528 | -0.041199 | 120.6528 | 120.5521 | -0.10071 | -0.027466 | 120.7443 | 120.6802 | 120.6757 | -0.16022 | 120.6802 | 120.694 | 120.7077 | -0.068664
2508.9375 | 120.7123 | -120.5704 | 0.1236 | 0.013046 | 0.0022088 | 0.065313 | 0.02587 | -0.067614 | -0.019895 | 0.0018564 | 0.014954 | 0.14624 | 0.12912 | -0.041832 | -0.0046228 | 0.014163 | 0.013733 | -0.022888 | 0.009155 | 0.082397 | 0.11444 | 0.059509 | -0.059509 | 0.032043 | 0.022888 | -0.09613 | 0.082397 | 0.09613 | 0.11444 | 0.036621 | 120.6299 | 120.5109 | -0.009155 | 120.5475 | 120.6528 | 0.14191 | -0.10986 | 120.6848 | 120.607 | -0.041199 | 120.6024 | 120.4742 | -0.13275 | -0.027466 | 120.6848 | 120.5841 | 120.5795 | -0.1831 | 120.6528 | 120.6665 | 120.5933 | -0.086975
2510.6562 | 121.0236 | -120.7214 | 0.068665 | -0.0022127 | 0.003277 | 0.068945 | 0.025443 | -0.070177 | -0.024167 | 0.00207 | 0.0073242 | 0.053318 | 0.031922 | -0.044609 | -0.00505 | 0.015659 | 0.064087 | 0.073242 | 0.091553 | 0.11902 | 0.082397 | 0.09613 | -0.045776 | 0.09613 | 0.1236 | 0.013733 | -0.009155 | 0.013733 | 0.10071 | 0.036621 | 120.8176 | 120.6757 | 0.013732 | 120.7947 | 120.8405 | 0.16479 | -0.004578 | 120.8221 | 120.7581 | -0.07782 | 120.8176 | 120.7352 | -0.022888 | -0.054932 | 120.8038 | 120.7855 | 120.813 | -0.11444 | 120.7123 | 120.7352 | 120.845 | -0.032044
2512.4375 | 115.9195 | -115.0864 | 0.48981 | 0.0054168 | -0.0050544 | 0.068731 | 0.025443 | -0.068041 | -0.020749 | -0.00027975 | -0.0003053 | 1.5636 | 1.4241 | -0.057426 | -0.0031274 | 0.029544 | 0.054932 | 0.022888 | 0.059509 | 0.1236 | 0.11444 | 0.059509 | -0.059509 | 0.1831 | 0.091553 | 0.018311 | 0.55389 | 0.5127 | 0.31128 | 0.2243 | 115.1459 | 115.0269 | -0.37537 | 115.1093 | 115.21 | 0.1831 | -0.43488 | 115.3976 | 115.3107 | 0.064087 | 115.2695 | 115.1047 | -0.20599 | 0.022888 | 115.2008 | 115.1413 | 115.1459 | -0.54932 | 115.6403 | 115.5991 | 115.1779 | -0.2655
2514.1562 | 120.8359 | -120.4971 | 0.041199 | -0.0098417 | 0.0030634 | 0.071935 | 0.02822 | -0.067187 | -0.032071 | -0.00027975 | 0.0073242 | 0.048619 | 0.035126 | -0.046104 | -0.0091088 | 0.016513 | 0.050354 | 0.10071 | 0.13275 | 0.13275 | 0.068665 | 0.07782 | -0.045776 | 0.064087 | 0.16022 | 0.036621 | -0.022888 | 0.004578 | 0.11444 | 0.036621 | 120.575 | 120.4514 | 0.027466 | 120.5978 | 120.6299 | 0.17853 | 0.009155 | 120.6116 | 120.5338 | -0.064087 | 120.5612 | 120.5338 | 0 | -0.036621 | 120.5658 | 120.5475 | 120.6299 | -0.086975 | 120.4742 | 120.5017 | 120.6573 | -0.004578
2515.9531 | 120.8633 | -120.5795 | 0.10529 | 0.020676 | 0.0051996 | 0.07279 | 0.02587 | -0.068896 | -0.025235 | -0.0026298 | 0.0073242 | 0.097111 | 0.07956 | -0.046745 | -0.0046228 | 0.016086 | 0.10529 | 0.11902 | 0.14191 | 0.14191 | 0.059509 | 0.082397 | -0.032043 | 0.064087 | 0.12817 | 0.018311 | 0.004578 | 0.036621 | 0.12817 | 0.064087 | 120.6619 | 120.5475 | -0.045777 | 120.6985 | 120.7214 | 0.17395 | 0 | 120.7077 | 120.6436 | -0.10071 | 120.6436 | 120.5978 | -0.045776 | -0.068665 | 120.639 | 120.6848 | 120.7214 | -0.13733 | 120.5841 | 120.6161 | 120.7077 | -0.041199
2517.7344 | 120.8588 | -120.5566 | 0.21057 | 0.0054168 | -0.0016364 | 0.068731 | 0.029074 | -0.070177 | -0.020322 | 0.00207 | 0.014954 | 0.21909 | 0.19663 | -0.04824 | -0.0024866 | 0.014377 | 0.10071 | 0.073242 | 0.07782 | 0.10986 | 0.10529 | 0.054932 | -0.07782 | 0.091553 | 0.16937 | 0.009155 | 0.10071 | 0.11902 | 0.13275 | 0.064087 | 120.6116 | 120.4788 | -0.10529 | 120.6299 | 120.6665 | 0.18768 | -0.10986 | 120.6894 | 120.6207 | -0.10986 | 120.6482 | 120.5658 | -0.054932 | -0.091552 | 120.6619 | 120.6573 | 120.6345 | -0.28839 | 120.6573 | 120.6757 | 120.726 | -0.14648
2519.5156 | 120.5841 | -120.3598 | 0.064087 | 0.020676 | 0.0071222 | 0.070226 | 0.027152 | -0.069109 | -0.026517 | 0.0042062 | 0.014954 | 0.048619 | 0.035767 | -0.045677 | -0.008468 | 0.013309 | 0.091553 | 0.13733 | 0.16479 | 0.15564 | 0.050354 | 0.10071 | -0.045776 | 0.09613 | 0.15564 | 0.027466 | -0.036621 | -0.004578 | 0.10071 | 0.045776 | 120.4605 | 120.314 | -0.013733 | 120.4971 | 120.5154 | 0.20142 | 0.027466 | 120.4605 | 120.4056 | -0.10071 | 120.4559 | 120.3873 | -0.01831 | -0.068665 | 120.4102 | 120.4514 | 120.5246 | -0.10986 | 120.3232 | 120.3552 | 120.5154 | -0.018311
2521.2969 | 120.7947 | -120.5338 | 0.059509 | 0.0054168 | 0.0026362 | 0.067449 | 0.026083 | -0.069964 | -0.024594 | 0.0027108 | 0.014954 | 0.052891 | 0.034699 | -0.04525 | -0.0052636 | 0.012668 | 0.10986 | 0.10986 | 0.14191 | 0.16937 | 0.054932 | 0.10071 | -0.018311 | 0.10071 | 0.13275 | 0.018311 | -0.013733 | -0.009155 | 0.1236 | 0.059509 | 120.6345 | 120.5154 | -0.004577 | 120.6436 | 120.7031 | 0.18768 | 0.050354 | 120.6573 | 120.5933 | -0.073242 | 120.6345 | 120.5521 | -0.041198 | -0.068664 | 120.5887 | 120.6436 | 120.6757 | -0.07782 | 120.52 | 120.5246 | 120.6665 | 0
2523.0781 | 120.8542 | -120.5978 | 0.07782 | 0.013046 | 0.0039178 | 0.070654 | 0.026724 | -0.069323 | -0.029935 | 0.00036105 | 0.014954 | 0.048832 | 0.034058 | -0.045463 | -0.0078272 | 0.015018 | 0.050354 | 0.064087 | 0.10529 | 0.11444 | 0.068665 | 0.07782 | -0.032043 | 0.032043 | 0.091553 | -0.009155 | 0 | 0.018311 | 0.091553 | 0.045776 | 120.6757 | 120.5658 | -0.009155 | 120.6619 | 120.7123 | 0.14648 | -0.027466 | 120.6894 | 120.6436 | -0.07782 | 120.6299 | 120.5887 | -0.054931 | -0.059509 | 120.6665 | 120.6482 | 120.7031 | -0.10986 | 120.5978 | 120.6161 | 120.6894 | -0.032044
2524.8594 | 120.8542 | -120.694 | 0.11444 | 0.013046 | -0.00014101 | 0.070654 | 0.029074 | -0.069109 | -0.024808 | -0.00027975 | 0.014954 | 0.056523 | 0.036835 | -0.045463 | -0.0069726 | 0.011813 | 0.009155 | 0.009155 | 0.022888 | 0.068665 | 0.11444 | 0.036621 | -0.07782 | -0.032043 | 0.032043 | -0.09613 | 0.032043 | 0.068665 | 0.064087 | 0.013733 | 120.7306 | 120.6161 | 0 | 120.7031 | 120.7626 | 0.14649 | -0.10529 | 120.7581 | 120.7077 | -0.082398 | 120.6619 | 120.5978 | -0.10986 | -0.045776 | 120.8084 | 120.7031 | 120.7169 | -0.19226 | 120.726 | 120.7626 | 120.726 | -0.10071
2526.6562 | 120.9503 | -120.7214 | 0.07782 | -0.0022127 | 0.0056268 | 0.070654 | 0.023306 | -0.06975 | -0.024594 | 0.0018564 | 0.014954 | 0.055454 | 0.03769 | -0.045463 | -0.0054772 | 0.014591 | 0.10986 | 0.15106 | 0.16022 | 0.15564 | 0.050354 | 0.10071 | -0.027466 | 0.09613 | 0.13275 | 0.009155 | -0.009155 | 0.018311 | 0.10071 | 0.045776 | 120.8221 | 120.694 | -0.027466 | 120.8725 | 120.8771 | 0.18311 | 0.032043 | 120.8221 | 120.7672 | -0.086975 | 120.8176 | 120.7306 | -0.036621 | -0.059509 | 120.7718 | 120.8313 | 120.8817 | -0.10529 | 120.7123 | 120.7397 | 120.8542 | -0.032044
2528.4375 | 120.8817 | -120.7489 | 0.11902 | 0.0054168 | 0.00071339 | 0.067663 | 0.024374 | -0.06975 | -0.019254 | 0.0014292 | 0.0073242 | 0.059086 | 0.038117 | -0.042045 | -0.003982 | 0.013736 | 0.059509 | 0.004578 | 0.036621 | 0.09613 | 0.09613 | 0.054932 | -0.059509 | 0.009155 | 0.018311 | -0.11444 | 0.018311 | 0.045776 | 0.082397 | 0.004578 | 120.8038 | 120.6894 | -0.022889 | 120.7535 | 120.845 | 0.15564 | -0.05951 | 120.8313 | 120.7535 | -0.10071 | 120.7581 | 120.6345 | -0.11902 | -0.073243 | 120.845 | 120.8084 | 120.7855 | -0.17853 | 120.7672 | 120.7947 | 120.7672 | -0.11444
2530.1562 | 120.9503 | -120.8176 | 0.082397 | 0.013046 | 0.0013544 | 0.071935 | 0.027152 | -0.067828 | -0.028653 | -0.00049335 | 0.014954 | 0.055668 | 0.039612 | -0.047599 | -0.0074 | 0.015445 | 0.09613 | 0.14191 | 0.16022 | 0.15564 | 0.073242 | 0.091553 | -0.018311 | 0.059509 | 0.16479 | 0.018311 | -0.013733 | 0.013733 | 0.10529 | 0.041199 | 120.9091 | 120.7993 | -0.009155 | 120.9595 | 120.9732 | 0.17395 | 0.013733 | 120.9229 | 120.8588 | -0.09613 | 120.8771 | 120.8359 | -0.022888 | -0.068664 | 120.8908 | 120.9137 | 120.9778 | -0.10071 | 120.8038 | 120.8313 | 120.9824 | -0.041198
2531.9531 | 121.0419 | -120.8038 | 0.086975 | 0.013046 | 0.0079766 | 0.072363 | 0.02587 | -0.068682 | -0.026944 | 0.0010018 | 0.0073242 | 0.0546 | 0.037903 | -0.046959 | -0.0041956 | 0.014377 | 0.11902 | 0.13733 | 0.16022 | 0.15106 | 0.045776 | 0.10071 | -0.013733 | 0.082397 | 0.14191 | 0.032043 | -0.018311 | 0.004578 | 0.11902 | 0.045776 | 120.9045 | 120.7901 | -0.041199 | 120.9412 | 120.9549 | 0.16479 | 0.032044 | 120.9229 | 120.8496 | -0.10529 | 120.8862 | 120.8359 | -0.013733 | -0.082397 | 120.8496 | 120.9229 | 120.9641 | -0.10071 | 120.7855 | 120.8084 | 120.9457 | -0.041199
2533.7344 | 121.051 | -120.8267 | 0.064087 | 0.0054168 | 0.004345 | 0.071081 | 0.027365 | -0.067614 | -0.026731 | 0.0012154 | 0.014954 | 0.057377 | 0.037049 | -0.04824 | -0.0080408 | 0.016727 | 0.10529 | 0.09613 | 0.14191 | 0.13733 | 0.064087 | 0.07782 | -0.041199 | 0.045776 | 0.10071 | 0.009155 | -0.004578 | 0.032043 | 0.11902 | 0.036621 | 120.9045 | 120.7855 | 0 | 120.9229 | 120.9641 | 0.17853 | 0.041199 | 120.9457 | 120.8633 | -0.068665 | 120.8725 | 120.8359 | -0.027466 | -0.032044 | 120.8908 | 120.932 | 120.9686 | -0.10529 | 120.8221 | 120.8588 | 120.9274 | -0.027466
2535.5312 | 121.0968 | -120.845 | 0.086975 | 0.0054168 | 0.0041314 | 0.071081 | 0.025229 | -0.069537 | -0.025662 | -6.615e-05 | 0.0073242 | 0.057591 | 0.037049 | -0.046104 | -0.0059046 | 0.015018 | 0.11444 | 0.1236 | 0.15106 | 0.13733 | 0.073242 | 0.09613 | -0.027466 | 0.059509 | 0.11444 | -0.004578 | -0.004578 | 0.004578 | 0.10071 | 0.032043 | 120.9412 | 120.8176 | -0.013733 | 120.9686 | 120.9824 | 0.16479 | 0.027466 | 120.9457 | 120.8771 | -0.091553 | 120.9045 | 120.8405 | -0.036621 | -0.082397 | 120.9183 | 120.9595 | 120.9961 | -0.11444 | 120.8405 | 120.8496 | 120.9595 | -0.054932
2537.3125 | 121.0373 | -120.8954 | 0.09613 | 0.013046 | -0.0024908 | 0.071935 | 0.026297 | -0.068896 | -0.018399 | 0.00036105 | 0.0073242 | 0.059727 | 0.040467 | -0.043113 | -0.0041956 | 0.0116 | 0.11444 | 0.064087 | 0.07782 | 0.11902 | 0.086975 | 0.064087 | -0.073242 | 0.054932 | 0.091553 | -0.059509 | 0.027466 | 0.041199 | 0.091553 | 0.027466 | 120.9595 | 120.8221 | -0.009155 | 120.9595 | 121.0144 | 0.19226 | 0.018311 | 120.9869 | 120.9229 | -0.068664 | 120.9503 | 120.8359 | -0.086975 | -0.054931 | 120.9824 | 121.0098 | 120.9732 | -0.16937 | 120.9229 | 120.9366 | 120.9869 | -0.068664
2539.0469 | 121.1792 | -120.8542 | 0.073242 | 0.0054168 | 0.004986 | 0.068304 | 0.025015 | -0.067187 | -0.022672 | -0.00070715 | 0.014954 | 0.059513 | 0.037476 | -0.044395 | -0.005691 | 0.013309 | 0.10986 | 0.07782 | 0.10529 | 0.14191 | 0.07782 | 0.10071 | -0.027466 | 0.091553 | 0.12817 | 0.004578 | -0.018311 | 0.027466 | 0.10986 | 0.073242 | 120.9549 | 120.8267 | 0.004578 | 120.932 | 120.9961 | 0.16937 | 0.036621 | 120.9641 | 120.9274 | -0.091553 | 120.9457 | 120.8588 | -0.068664 | -0.045776 | 120.932 | 120.9641 | 120.9595 | -0.10071 | 120.8359 | 120.8817 | 120.9824 | 0
2540.8281 | 121.0693 | -120.9366 | 0.09613 | -0.0022127 | 0.00092719 | 0.072149 | 0.026938 | -0.066332 | -0.02609 | -0.00092075 | 0.0073242 | 0.057591 | 0.040467 | -0.047172 | -0.0076136 | 0.013736 | 0.086975 | 0.10071 | 0.10986 | 0.14648 | 0.082397 | 0.064087 | -0.045776 | 0.018311 | 0.086975 | -0.059509 | 0.022888 | 0.036621 | 0.086975 | 0.009155 | 121.0007 | 120.8908 | -0.013733 | 121.0373 | 121.0831 | 0.19226 | -0.009155 | 121.0236 | 120.9457 | -0.073242 | 120.9549 | 120.8771 | -0.068664 | -0.059509 | 121.019 | 121.0236 | 121.0464 | -0.14191 | 120.9595 | 120.9732 | 121.0236 | -0.086975
2542.6094 | 121.0739 | -120.9549 | 0.11444 | 0.0054168 | 0.0019952 | 0.067449 | 0.026938 | -0.068255 | -0.020749 | 0.0018564 | -0.0003053 | 0.060581 | 0.039826 | -0.042472 | -0.0027002 | 0.01395 | 0.027466 | -0.009155 | 0.036621 | 0.073242 | 0.11902 | 0.064087 | -0.086975 | -0.004578 | 0 | -0.1236 | 0.045776 | 0.059509 | 0.068665 | 0.027466 | 121.019 | 120.8679 | 0.004578 | 120.9457 | 121.0281 | 0.16022 | -0.086975 | 121.0236 | 120.9824 | -0.068665 | 120.9503 | 120.8313 | -0.15106 | -0.054932 | 121.0739 | 120.9824 | 120.9915 | -0.20142 | 121.0007 | 121.0144 | 120.9549 | -0.086975
2544.3906 | 121.1975 | -120.9274 | 0.064087 | -0.0022127 | 0.0026362 | 0.070867 | 0.026724 | -0.068468 | -0.025022 | 0.00078825 | 0.0073242 | 0.056095 | 0.04068 | -0.046318 | -0.0063318 | 0.014591 | 0.11902 | 0.13275 | 0.16479 | 0.16479 | 0.059509 | 0.10529 | -0.032043 | 0.11444 | 0.16022 | 0.036621 | 0.009155 | 0.004578 | 0.11444 | 0.050354 | 121.0327 | 120.8954 | -0.004578 | 121.0602 | 121.0922 | 0.19684 | 0.054932 | 121.0419 | 120.9778 | -0.054932 | 121.0419 | 120.9641 | -0.013733 | -0.059509 | 120.9869 | 121.0464 | 121.0922 | -0.09613 | 120.9366 | 120.932 | 121.0876 | -0.013733
2546.1719 | 121.1838 | -120.9869 | 0.09613 | 0.013046 | -0.0020636 | 0.069799 | 0.030997 | -0.068682 | -0.025022 | -6.615e-05 | 0.014954 | 0.059513 | 0.040894 | -0.042259 | -0.0071862 | 0.012882 | -0.004578 | 0.009155 | 0.013733 | 0.09613 | 0.11902 | 0.041199 | -0.09613 | -0.013733 | 0.041199 | -0.10529 | 0.032043 | 0.032043 | 0.07782 | 0.018311 | 121.0281 | 120.8908 | 0.022889 | 120.9961 | 121.0831 | 0.19226 | -0.10071 | 121.0648 | 121.0052 | -0.064087 | 120.9732 | 120.8817 | -0.1236 | -0.064087 | 121.106 | 120.9824 | 121.0007 | -0.19226 | 121.019 | 121.019 | 121.0281 | -0.077819
2547.8906 | 121.2891 | -120.9641 | 0.073242 | 0.0054168 | 0.0022088 | 0.07044 | 0.024588 | -0.067187 | -0.023099 | 0.0024972 | 0.0073242 | 0.060795 | 0.040467 | -0.043327 | -0.005691 | 0.014377 | 0.041199 | 0.054932 | 0.091553 | 0.12817 | 0.064087 | 0.073242 | -0.054932 | 0.082397 | 0.10986 | -0.013733 | -0.004578 | 0.018311 | 0.11902 | 0.045776 | 121.0373 | 120.9091 | -0.009155 | 121.019 | 121.0922 | 0.18311 | -0.032043 | 121.0831 | 121.0098 | -0.07782 | 121.0464 | 120.9503 | -0.059509 | -0.054931 | 121.0281 | 121.0052 | 121.0556 | -0.12817 | 120.9595 | 120.9824 | 121.0739 | -0.027466
2549.6719 | 121.257 | -121.019 | 0.07782 | 0.0054168 | 0.0019952 | 0.072576 | 0.027579 | -0.068896 | -0.029721 | -0.001348 | -0.0003053 | 0.055668 | 0.038971 | -0.047172 | -0.006759 | 0.014163 | 0.10986 | 0.16479 | 0.16937 | 0.17395 | 0.07782 | 0.09613 | -0.041199 | 0.086975 | 0.18768 | 0.054932 | -0.009155 | 0.009155 | 0.10071 | 0.041199 | 121.1151 | 120.9778 | 0 | 121.1838 | 121.1929 | 0.21515 | 0.032043 | 121.1197 | 121.0602 | -0.086975 | 121.106 | 121.0739 | 0.013733 | -0.068665 | 121.0968 | 121.1288 | 121.1884 | -0.11902 | 121.0098 | 121.0281 | 121.2067 | -0.036621
2551.3906 | 121.2296 | -121.0464 | 0.073242 | 0.013046 | -0.00078181 | 0.070226 | 0.026297 | -0.069537 | -0.023953 | 0.00014745 | -0.0003053 | 0.059727 | 0.038758 | -0.044609 | -0.0059046 | 0.014591 | 0.064087 | 0.036621 | 0.07782 | 0.1236 | 0.10071 | 0.054932 | -0.068665 | 0.050354 | 0.073242 | -0.054932 | 0.013733 | 0.041199 | 0.07782 | 0.018311 | 121.1014 | 120.9778 | 0.027466 | 121.0831 | 121.17 | 0.19226 | -0.009155 | 121.1243 | 121.0648 | -0.059509 | 121.0968 | 120.9915 | -0.073243 | -0.032043 | 121.1472 | 121.1105 | 121.1243 | -0.14191 | 121.0602 | 121.0876 | 121.1197 | -0.054931
2553.1719 | 121.2479 | -121.0602 | 0.082397 | 0.0054168 | 0.0030634 | 0.068304 | 0.026297 | -0.067614 | -0.023526 | -0.00070715 | 0.0073242 | 0.059513 | 0.04068 | -0.042686 | -0.0063318 | 0.016086 | 0.004578 | -0.018311 | 0.009155 | 0.068665 | 0.11444 | 0.054932 | -0.064087 | -0.004578 | 0 | -0.10529 | 0.036621 | 0.050354 | 0.086975 | 0.018311 | 121.1151 | 120.9961 | 0.032044 | 121.0419 | 121.1288 | 0.13275 | -0.077819 | 121.1472 | 121.0785 | -0.045776 | 121.0556 | 120.9549 | -0.1236 | -0.032043 | 121.1746 | 121.0648 | 121.0693 | -0.14648 | 121.0968 | 121.1105 | 121.0602 | -0.064086
2554.9688 | 121.2387 | -121.1105 | 0.11444 | 0.013046 | 0.0024224 | 0.072149 | 0.030569 | -0.070177 | -0.026731 | -6.615e-05 | 0.0073242 | 0.057377 | 0.041107 | -0.045036 | -0.0080408 | 0.014591 | -0.009155 | 0.013733 | 0.022888 | 0.086975 | 0.09613 | 0.050354 | -0.07782 | -0.036621 | 0.032043 | -0.09613 | 0.050354 | 0.054932 | 0.07782 | 0.009155 | 121.1609 | 121.0327 | -0.018311 | 121.1243 | 121.1975 | 0.16479 | -0.1236 | 121.1884 | 121.1197 | -0.064087 | 121.0739 | 121.0144 | -0.10528 | -0.059509 | 121.2067 | 121.1014 | 121.1334 | -0.19226 | 121.1609 | 121.1655 | 121.1426 | -0.10529
2556.75 | 121.3669 | -121.0693 | 0.082397 | 0.0054168 | 0.004345 | 0.073003 | 0.025656 | -0.068041 | -0.029508 | 0.00014745 | 0.0073242 | 0.056095 | 0.036408 | -0.045677 | -0.0071862 | 0.014591 | 0.022888 | 0.064087 | 0.10529 | 0.12817 | 0.068665 | 0.086975 | -0.041199 | 0.022888 | 0.10986 | 0.009155 | 0.009155 | 0.036621 | 0.10529 | 0.032043 | 121.1563 | 121.0281 | -0.013732 | 121.1334 | 121.1975 | 0.16937 | -0.059509 | 121.1746 | 121.1014 | -0.073242 | 121.0922 | 121.0785 | -0.022888 | -0.045776 | 121.138 | 121.0922 | 121.1746 | -0.1236 | 121.0785 | 121.106 | 121.1792 | -0.050354
2558.4688 | 121.3348 | -121.0693 | 0.073242 | 0.0054168 | 0.004986 | 0.071081 | 0.026297 | -0.071886 | -0.024808 | -0.00049335 | -0.0003053 | 0.056736 | 0.039826 | -0.046531 | -0.00505 | 0.015231 | 0.10986 | 0.13733 | 0.16022 | 0.14191 | 0.050354 | 0.10529 | -0.036621 | 0.091553 | 0.15106 | 0.022888 | -0.009155 | -0.004578 | 0.10529 | 0.068665 | 121.1746 | 121.0327 | -0.022888 | 121.2067 | 121.2112 | 0.17853 | 0.036621 | 121.1746 | 121.138 | -0.082397 | 121.1609 | 121.0922 | -0.045777 | -0.07782 | 121.1197 | 121.1792 | 121.2296 | -0.10986 | 121.0602 | 121.0648 | 121.2204 | -0.004577
2560.2344 | 121.2936 | -121.1151 | 0.07782 | -0.0022127 | -0.0022772 | 0.071081 | 0.026938 | -0.067828 | -0.022031 | 0.0010018 | 0.0073242 | 0.061222 | 0.040467 | -0.04525 | -0.0031274 | 0.013309 | 0.082397 | 0.073242 | 0.091553 | 0.10529 | 0.086975 | 0.054932 | -0.064087 | 0.050354 | 0.10529 | -0.041199 | 0.032043 | 0.041199 | 0.091553 | 0.004578 | 121.17 | 121.051 | 0.009155 | 121.1884 | 121.2204 | 0.16937 | 0.004577 | 121.2067 | 121.1197 | -0.045777 | 121.1655 | 121.0739 | -0.045777 | -0.036621 | 121.2021 | 121.1975 | 121.2067 | -0.14191 | 121.1472 | 121.1563 | 121.2204 | -0.073242
2562.0312 | 121.2616 | -121.1243 | 0.10529 | 0.0054168 | -0.00099541 | 0.067449 | 0.026511 | -0.068468 | -0.021817 | 0.0010018 | 0.022583 | 0.060795 | 0.041748 | -0.044395 | -0.003982 | 0.012668 | 0.07782 | 0.064087 | 0.064087 | 0.10071 | 0.10071 | 0.07782 | -0.059509 | 0.032043 | 0.068665 | -0.064087 | 0.022888 | 0.045776 | 0.07782 | 0.009155 | 121.2021 | 121.0648 | -0.004578 | 121.1884 | 121.225 | 0.16022 | -0.027466 | 121.2021 | 121.1334 | -0.082398 | 121.1563 | 121.0602 | -0.073242 | -0.05951 | 121.225 | 121.2021 | 121.1884 | -0.16479 | 121.1472 | 121.17 | 121.1929 | -0.096131
2563.7969 | 121.3531 | -121.1288 | 0.073242 | 0.013046 | 0.0011408 | 0.06809 | 0.024161 | -0.067187 | -0.024167 | 0.0022836 | 0.0073242 | 0.060795 | 0.039612 | -0.04589 | -0.00505 | 0.013736 | 0.018311 | -0.022888 | 0.004578 | 0.073242 | 0.10529 | 0.059509 | -0.054932 | -0.013733 | 0 | -0.10986 | 0.036621 | 0.054932 | 0.073242 | 0.013733 | 121.1884 | 121.0739 | 0.032044 | 121.106 | 121.2021 | 0.12817 | -0.054931 | 121.2021 | 121.1426 | -0.036621 | 121.1151 | 121.019 | -0.1236 | -0.01831 | 121.2341 | 121.1472 | 121.1334 | -0.12817 | 121.1655 | 121.1838 | 121.1288 | -0.059509
2565.5312 | 121.3898 | -121.1517 | 0.082397 | 0.020676 | 0.0019952 | 0.070013 | 0.029929 | -0.069537 | -0.031217 | -0.00049335 | 0.014954 | 0.055027 | 0.039185 | -0.046318 | -0.0097498 | 0.015018 | 0.027466 | 0.082397 | 0.1236 | 0.1236 | 0.068665 | 0.10071 | -0.050354 | 0.022888 | 0.10529 | -0.018311 | 0.013733 | 0.022888 | 0.09613 | 0.059509 | 121.2524 | 121.1014 | -0.013732 | 121.2341 | 121.2753 | 0.17395 | -0.054931 | 121.2479 | 121.2112 | -0.068664 | 121.1746 | 121.1334 | -0.07782 | -0.059509 | 121.2204 | 121.1792 | 121.2753 | -0.13275 | 121.1655 | 121.1746 | 121.257 | -0.022888
2567.3125 | 121.3623 | -121.1838 | 0.09613 | 0.013046 | -0.0014228 | 0.069158 | 0.030356 | -0.068041 | -0.022885 | -0.001348 | 0.014954 | 0.059941 | 0.042603 | -0.044395 | -0.0052636 | 0.012454 | 0.022888 | 0.013733 | 0.045776 | 0.09613 | 0.10529 | 0.064087 | -0.082397 | 0.009155 | 0.073242 | -0.082397 | 0.032043 | 0.045776 | 0.073242 | 0.009155 | 121.2479 | 121.1014 | 0.009156 | 121.1975 | 121.2799 | 0.17853 | -0.073242 | 121.257 | 121.1929 | -0.064087 | 121.1929 | 121.1014 | -0.091552 | -0.050354 | 121.2891 | 121.2067 | 121.2296 | -0.17853 | 121.2158 | 121.2296 | 121.257 | -0.086975
2569.0938 | 121.3303 | -121.17 | 0.10529 | 0.020676 | -0.00056821 | 0.068304 | 0.024374 | -0.070818 | -0.021176 | 0.0029244 | 0.0073242 | 0.062718 | 0.04068 | -0.043327 | -0.0035546 | 0.013736 | 0.022888 | 0.013733 | 0.045776 | 0.09613 | 0.09613 | 0.059509 | -0.059509 | -0.004578 | 0.013733 | -0.11444 | 0.045776 | 0.054932 | 0.073242 | 0.018311 | 121.2296 | 121.1105 | -0.009156 | 121.1838 | 121.2662 | 0.15564 | -0.082398 | 121.2433 | 121.1884 | -0.05951 | 121.1655 | 121.0556 | -0.13275 | -0.050354 | 121.2662 | 121.1929 | 121.2158 | -0.16479 | 121.2158 | 121.225 | 121.1838 | -0.086975
2570.8125 | 121.3943 | -121.1884 | 0.082397 | 0.0054168 | -0.0031318 | 0.068304 | 0.025443 | -0.069537 | -0.021817 | -0.00027975 | 0.0073242 | 0.060368 | 0.041321 | -0.043541 | -0.0059046 | 0.01395 | 0.027466 | 0.022888 | 0.054932 | 0.1236 | 0.10071 | 0.059509 | -0.054932 | 0.013733 | 0.07782 | -0.050354 | 0.022888 | 0.064087 | 0.086975 | 0.027466 | 121.2479 | 121.1334 | 0.018311 | 121.2112 | 121.312 | 0.17853 | -0.054931 | 121.2753 | 121.2158 | -0.059509 | 121.2021 | 121.138 | -0.07782 | -0.01831 | 121.2891 | 121.2158 | 121.2433 | -0.13733 | 121.2112 | 121.2524 | 121.2662 | -0.054931
2572.5938 | 121.3531 | -121.2296 | 0.11444 | 0.013046 | -0.0012092 | 0.068945 | 0.028647 | -0.0674 | -0.02609 | -0.0017752 | -0.0003053 | 0.060581 | 0.043457 | -0.043541 | -0.0076136 | 0.015445 | -0.018311 | 0.022888 | 0.050354 | 0.07782 | 0.10529 | 0.050354 | -0.082397 | -0.027466 | 0.041199 | -0.073242 | 0.050354 | 0.059509 | 0.068665 | 0.013733 | 121.2799 | 121.1472 | -0.009155 | 121.2524 | 121.3074 | 0.16022 | -0.13275 | 121.2982 | 121.2433 | -0.064087 | 121.2021 | 121.1563 | -0.086975 | -0.054932 | 121.3348 | 121.2112 | 121.2799 | -0.19684 | 121.2799 | 121.2891 | 121.2708 | -0.10071
2574.375 | 121.463 | -121.1929 | 0.068665 | 0.0054168 | 0.0024224 | 0.075353 | 0.030783 | -0.069964 | -0.031217 | 0.00036105 | 0.014954 | 0.056736 | 0.041321 | -0.045036 | -0.0088952 | 0.015445 | 0.086975 | 0.16022 | 0.16937 | 0.16479 | 0.059509 | 0.09613 | -0.041199 | 0.07782 | 0.20599 | 0.041199 | 0 | 0.009155 | 0.10529 | 0.036621 | 121.2891 | 121.1517 | -0.009156 | 121.3531 | 121.3577 | 0.20599 | 0.01831 | 121.2982 | 121.2296 | -0.068665 | 121.2708 | 121.2341 | 0.004578 | -0.05951 | 121.2524 | 121.2799 | 121.3623 | -0.10986 | 121.1929 | 121.2021 | 121.3989 | -0.032044
2576.1562 | 121.4081 | -121.2433 | 0.10529 | 0.020676 | -0.00014101 | 0.069158 | 0.026511 | -0.066119 | -0.02609 | -0.003057 | 0.014954 | 0.060368 | 0.041321 | -0.045677 | -0.006759 | 0.013736 | -0.004578 | -0.004578 | 0.018311 | 0.082397 | 0.14191 | 0.059509 | -0.086975 | -0.059509 | 0.045776 | -0.10071 | 0.050354 | 0.068665 | 0.045776 | 0.022888 | 121.3028 | 121.1563 | 0.036621 | 121.2387 | 121.3257 | 0.16937 | -0.10986 | 121.2891 | 121.2662 | -0.054932 | 121.1838 | 121.1426 | -0.1236 | -0.036621 | 121.3852 | 121.2387 | 121.2616 | -0.19226 | 121.2936 | 121.312 | 121.2891 | -0.082398
2577.875 | 121.5408 | -121.1838 | 0.091553 | 0.013046 | 0.003277 | 0.073644 | 0.026297 | -0.070391 | -0.032498 | -0.0015616 | 0.0073242 | 0.055668 | 0.038971 | -0.048454 | -0.0082544 | 0.013522 | 0.064087 | 0.10529 | 0.13733 | 0.13733 | 0.068665 | 0.082397 | -0.050354 | 0.064087 | 0.15564 | 0.036621 | 0 | 0.032043 | 0.1236 | 0.064087 | 121.2662 | 121.1334 | -0.022888 | 121.2891 | 121.3211 | 0.18768 | -0.027466 | 121.3074 | 121.2479 | -0.091553 | 121.2479 | 121.2204 | -0.027466 | -0.05951 | 121.2524 | 121.2479 | 121.3211 | -0.14191 | 121.1838 | 121.2158 | 121.3394 | -0.027466
2579.6562 | 121.5134 | -121.1975 | 0.073242 | 0.0054168 | 0.0011408 | 0.068945 | 0.026511 | -0.068255 | -0.022885 | -0.00049335 | 0.0073242 | 0.060368 | 0.040039 | -0.045036 | -0.00505 | 0.014163 | 0.068665 | 0.041199 | 0.082397 | 0.11444 | 0.082397 | 0.073242 | -0.045776 | 0.07782 | 0.10071 | -0.009155 | -0.004578 | 0.013733 | 0.11444 | 0.050354 | 121.2708 | 121.1517 | 0.009155 | 121.2387 | 121.312 | 0.16022 | -0.004577 | 121.312 | 121.2479 | -0.07782 | 121.2753 | 121.1884 | -0.059509 | -0.059509 | 121.2799 | 121.2662 | 121.2799 | -0.11902 | 121.1929 | 121.2112 | 121.2982 | -0.022888
2581.4375 | 121.4127 | -121.2845 | 0.10071 | 0.0054168 | 0.00092719 | 0.07044 | 0.026083 | -0.069964 | -0.027158 | 0.0012154 | 0.0073242 | 0.060154 | 0.04068 | -0.045463 | -0.0071862 | 0.014377 | 0.091553 | 0.10986 | 0.13733 | 0.16937 | 0.082397 | 0.07782 | -0.050354 | 0.036621 | 0.12817 | -0.018311 | 0.018311 | 0.032043 | 0.086975 | 0.032043 | 121.3623 | 121.2341 | -0.018311 | 121.3943 | 121.4539 | 0.21973 | -0.009155 | 121.3715 | 121.3165 | -0.082397 | 121.3211 | 121.2662 | -0.050354 | -0.068665 | 121.3669 | 121.376 | 121.4218 | -0.15106 | 121.3028 | 121.3165 | 121.4127 | -0.068665
2583.2344 | 121.4401 | -121.2708 | 0.10071 | 0.013046 | 0.0017816 | 0.070226 | 0.024374 | -0.068255 | -0.01904 | 0.0016428 | 0.0073242 | 0.06165 | 0.04068 | -0.043541 | -0.0059046 | 0.014163 | 0.009155 | -0.041199 | 0.022888 | 0.082397 | 0.1236 | 0.068665 | -0.064087 | -0.027466 | -0.013733 | -0.11902 | 0.032043 | 0.082397 | 0.07782 | 0.009155 | 121.3394 | 121.2067 | 0.022888 | 121.2296 | 121.3531 | 0.14648 | -0.091553 | 121.3486 | 121.2799 | -0.068665 | 121.2433 | 121.1517 | -0.12817 | -0.018311 | 121.3943 | 121.2799 | 121.2936 | -0.1648 | 121.3028 | 121.3531 | 121.257 | -0.091553
2585.0312 | 121.55 | -121.2387 | 0.068665 | 0.013046 | 0.0011408 | 0.069799 | 0.02352 | -0.068896 | -0.023313 | 0.0010018 | -0.0003053 | 0.063359 | 0.040467 | -0.046104 | -0.003341 | 0.01395 | 0.018311 | -0.004578 | 0.022888 | 0.073242 | 0.09613 | 0.068665 | -0.064087 | 0.018311 | 0.036621 | -0.059509 | 0.022888 | 0.054932 | 0.09613 | 0.059509 | 121.3074 | 121.1746 | 0.027465 | 121.2341 | 121.3119 | 0.13733 | -0.050354 | 121.3348 | 121.2982 | -0.045777 | 121.257 | 121.1792 | -0.11902 | -0.013733 | 121.3348 | 121.257 | 121.2616 | -0.13275 | 121.2616 | 121.2936 | 121.2753 | -0.009156
2586.8281 | 121.4813 | -121.3028 | 0.091553 | 0.0054168 | -0.0024908 | 0.069158 | 0.028647 | -0.068682 | -0.022885 | 0.0010018 | 0.0073242 | 0.062077 | 0.04303 | -0.043968 | -0.0044092 | 0.014377 | 0.045776 | 0.032043 | 0.054932 | 0.10529 | 0.10529 | 0.050354 | -0.068665 | 0.032043 | 0.086975 | -0.059509 | 0.027466 | 0.045776 | 0.082397 | 0.013733 | 121.3531 | 121.2341 | 0.013733 | 121.3348 | 121.4081 | 0.17395 | -0.045777 | 121.3852 | 121.3165 | -0.064087 | 121.3348 | 121.2433 | -0.073242 | -0.045777 | 121.4081 | 121.3486 | 121.3577 | -0.16022 | 121.3303 | 121.3486 | 121.3898 | -0.07782
2588.5625 | 121.5729 | -121.2799 | 0.068665 | 0.013046 | 0.0034906 | 0.071508 | 0.028433 | -0.070391 | -0.031003 | -0.0011344 | 0.014954 | 0.056736 | 0.043457 | -0.043113 | -0.010391 | 0.0163 | 0.07782 | 0.11902 | 0.14191 | 0.16022 | 0.068665 | 0.09613 | -0.050354 | 0.064087 | 0.19226 | 0.045776 | 0.004578 | 0.036621 | 0.11444 | 0.050354 | 121.376 | 121.2296 | 0 | 121.3989 | 121.4401 | 0.21057 | 0.009155 | 121.3943 | 121.3303 | -0.064087 | 121.344 | 121.3257 | -0.004578 | -0.032044 | 121.3486 | 121.3577 | 121.4218 | -0.11902 | 121.2845 | 121.3165 | 121.4722 | -0.018311
2590.3281 | 121.5591 | -121.312 | 0.07782 | 0.013046 | 0.0045588 | 0.072576 | 0.026083 | -0.067187 | -0.026731 | -0.0019888 | 0.0073242 | 0.059727 | 0.040467 | -0.044181 | -0.0078272 | 0.014163 | 0.11444 | 0.13275 | 0.16479 | 0.16479 | 0.054932 | 0.10529 | -0.022888 | 0.086975 | 0.15106 | 0.022888 | -0.004578 | 0.004578 | 0.1236 | 0.054932 | 121.4172 | 121.2891 | -0.022888 | 121.4447 | 121.4767 | 0.18768 | 0.036621 | 121.4355 | 121.3669 | -0.082398 | 121.3989 | 121.3348 | -0.032044 | -0.073242 | 121.3669 | 121.4264 | 121.4767 | -0.10071 | 121.3074 | 121.3165 | 121.463 | -0.022888
2592.1094 | 121.5775 | -121.2982 | 0.068665 | 0.020676 | 0.0041314 | 0.074072 | 0.026724 | -0.070818 | -0.028012 | -0.0011344 | 0.0073242 | 0.058232 | 0.041962 | -0.045463 | -0.0071862 | 0.015018 | 0.050354 | 0.059509 | 0.10071 | 0.1236 | 0.086975 | 0.086975 | -0.032043 | 0.032043 | 0.091553 | -0.004578 | 0.013733 | 0.009155 | 0.091553 | 0.036621 | 121.3852 | 121.2662 | 0.01831 | 121.3577 | 121.4218 | 0.15564 | -0.018311 | 121.3898 | 121.3348 | -0.054932 | 121.3303 | 121.2936 | -0.041199 | -0.05951 | 121.3852 | 121.3486 | 121.3989 | -0.10071 | 121.312 | 121.3074 | 121.3898 | -0.032044
2593.8125 | 121.5179 | -121.3394 | 0.086975 | 0.013046 | -0.00056821 | 0.074285 | 0.02886 | -0.068896 | -0.026303 | -0.00070715 | -0.0003053 | 0.061436 | 0.041535 | -0.04525 | -0.008468 | 0.013309 | 0.11902 | 0.14191 | 0.1831 | 0.16479 | 0.064087 | 0.082397 | -0.041199 | 0.091553 | 0.17853 | 0.027466 | 0.004578 | 0.027466 | 0.10071 | 0.036621 | 121.4218 | 121.2982 | -0.022888 | 121.4813 | 121.5042 | 0.20599 | 0.032044 | 121.4401 | 121.376 | -0.082397 | 121.431 | 121.3669 | -0.009155 | -0.059509 | 121.4035 | 121.4584 | 121.5225 | -0.12817 | 121.344 | 121.3669 | 121.5179 | -0.050354
2595.5938 | 121.6415 | -121.3211 | 0.073242 | 0.020676 | 0.0054132 | 0.073003 | 0.028006 | -0.068468 | -0.02844 | -0.00070715 | 0.014954 | 0.056736 | 0.042389 | -0.045677 | -0.0082544 | 0.013309 | 0.086975 | 0.10986 | 0.14191 | 0.15564 | 0.07782 | 0.086975 | -0.022888 | 0.086975 | 0.15564 | 0.027466 | 0.013733 | 0.022888 | 0.11902 | 0.045776 | 121.4081 | 121.2982 | 0.004578 | 121.431 | 121.4767 | 0.17853 | 0.013733 | 121.4401 | 121.3669 | -0.059509 | 121.4081 | 121.3486 | -0.01831 | -0.050354 | 121.3989 | 121.4081 | 121.463 | -0.09613 | 121.3348 | 121.344 | 121.4767 | -0.027466
2597.3125 | 121.6278 | -121.3165 | 0.068665 | -0.0022127 | 0.0019952 | 0.068517 | 0.026297 | -0.071032 | -0.020322 | 0.0012154 | 0.0073242 | 0.063145 | 0.043244 | -0.042686 | -0.003341 | 0.012241 | 0.054932 | 0.027466 | 0.050354 | 0.091553 | 0.10071 | 0.064087 | -0.064087 | 0.059509 | 0.059509 | -0.050354 | 0.009155 | 0.022888 | 0.086975 | 0.045776 | 121.3806 | 121.2524 | 0.032043 | 121.344 | 121.4081 | 0.15564 | -0.013733 | 121.4035 | 121.3623 | -0.05951 | 121.376 | 121.2662 | -0.09613 | -0.045777 | 121.4172 | 121.3715 | 121.3669 | -0.13275 | 121.3257 | 121.3394 | 121.376 | -0.022889
2599.0938 | 121.5042 | -121.3806 | 0.09613 | 0.0054168 | -0.0031318 | 0.071935 | 0.030356 | -0.068041 | -0.025449 | -0.00027975 | 0.022583 | 0.061222 | 0.044953 | -0.045677 | -0.0078272 | 0.013736 | 0.064087 | 0.082397 | 0.10071 | 0.1236 | 0.082397 | 0.068665 | -0.045776 | 0.009155 | 0.086975 | -0.059509 | 0.036621 | 0.050354 | 0.07782 | 0.018311 | 121.4493 | 121.3348 | -0.013733 | 121.463 | 121.5042 | 0.16937 | -0.032043 | 121.4584 | 121.3989 | -0.059509 | 121.3898 | 121.3211 | -0.07782 | -0.045776 | 121.463 | 121.4447 | 121.4813 | -0.14191 | 121.4172 | 121.431 | 121.4676 | -0.077819
2600.8281 | 121.6644 | -121.3257 | 0.064087 | -0.0022127 | 0.0037042 | 0.069158 | 0.028433 | -0.067614 | -0.029508 | -6.615e-05 | 0.014954 | 0.0593 | 0.041535 | -0.046745 | -0.0078272 | 0.014804 | 0.07782 | 0.10529 | 0.13275 | 0.14191 | 0.059509 | 0.091553 | -0.027466 | 0.07782 | 0.15106 | 0.032043 | -0.004578 | 0.022888 | 0.10071 | 0.045776 | 121.4172 | 121.2982 | -0.004578 | 121.431 | 121.4676 | 0.16937 | 0.013733 | 121.4264 | 121.3715 | -0.068665 | 121.4035 | 121.3577 | -0.013733 | -0.041199 | 121.3852 | 121.4035 | 121.4584 | -0.091553 | 121.3211 | 121.3486 | 121.4767 | -0.018311
2602.6094 | 121.6507 | -121.3623 | 0.07782 | 0.013046 | 0.0041314 | 0.070226 | 0.02587 | -0.068468 | -0.023099 | 0.0010018 | -0.0003053 | 0.062504 | 0.042816 | -0.043113 | -0.0063318 | 0.014163 | 0.12817 | 0.12817 | 0.13733 | 0.16479 | 0.073242 | 0.086975 | -0.036621 | 0.12817 | 0.14191 | 0.009155 | 0 | 0.009155 | 0.1236 | 0.073242 | 121.4493 | 121.3257 | -0.004578 | 121.4905 | 121.5271 | 0.20142 | 0.050354 | 121.4859 | 121.4355 | -0.07782 | 121.4905 | 121.3715 | -0.064087 | -0.068665 | 121.4355 | 121.4905 | 121.4996 | -0.11444 | 121.3623 | 121.3715 | 121.5042 | -0.004578
2604.4062 | 121.6232 | -121.3577 | 0.082397 | 0.0054168 | 0.0037042 | 0.068945 | 0.022025 | -0.067614 | -0.023526 | 0.0029244 | -0.0003053 | 0.062077 | 0.043671 | -0.046959 | -0.0029138 | 0.014591 | 0.11444 | 0.15106 | 0.16479 | 0.14191 | 0.07782 | 0.09613 | -0.032043 | 0.11444 | 0.14191 | 0.027466 | 0 | 0 | 0.11444 | 0.068665 | 121.4539 | 121.3257 | -0.004577 | 121.5088 | 121.4996 | 0.17395 | 0.032044 | 121.4722 | 121.4264 | -0.082397 | 121.4722 | 121.3852 | -0.041199 | -0.082397 | 121.4355 | 121.4722 | 121.5225 | -0.11444 | 121.3577 | 121.3577 | 121.4996 | -0.013732
2606.1406 | 121.6232 | -121.3852 | 0.091553 | -0.0022127 | 0.0019952 | 0.071294 | 0.024161 | -0.068255 | -0.025235 | 0.00014745 | 0.014954 | 0.062718 | 0.04303 | -0.044609 | -0.0065454 | 0.015872 | 0.073242 | 0.07782 | 0.10986 | 0.11902 | 0.068665 | 0.10986 | -0.036621 | 0.036621 | 0.091553 | -0.009155 | 0.009155 | 0.041199 | 0.10986 | 0.054932 | 121.4951 | 121.3486 | -0.022888 | 121.463 | 121.5042 | 0.15564 | -0.018311 | 121.4951 | 121.4401 | -0.082398 | 121.4218 | 121.376 | -0.064087 | -0.050354 | 121.4539 | 121.4584 | 121.4951 | -0.12817 | 121.3943 | 121.4264 | 121.4767 | -0.036621
2607.9219 | 121.5775 | -121.4218 | 0.11444 | 0.0054168 | 0.0013544 | 0.072149 | 0.024802 | -0.068682 | -0.025235 | 0.00014745 | -0.0003053 | 0.063999 | 0.043457 | -0.046104 | -0.0059046 | 0.012882 | 0.12817 | 0.14191 | 0.15564 | 0.16937 | 0.073242 | 0.091553 | -0.041199 | 0.091553 | 0.16937 | 0.013733 | 0 | 0.009155 | 0.11902 | 0.045776 | 121.5134 | 121.3806 | -0.041199 | 121.5637 | 121.5912 | 0.21057 | 0.013733 | 121.5408 | 121.4676 | -0.11444 | 121.5134 | 121.4355 | -0.032043 | -0.10529 | 121.4951 | 121.55 | 121.5775 | -0.15564 | 121.4218 | 121.431 | 121.5912 | -0.068665
2609.7031 | 121.6003 | -121.3943 | 0.11444 | 0.0054168 | -0.0039862 | 0.068945 | 0.026297 | -0.066119 | -0.018399 | 0.0014292 | 0.014954 | 0.067631 | 0.046875 | -0.043541 | -0.00505 | 0.012454 | 0.10071 | 0.059509 | 0.07782 | 0.11444 | 0.10071 | 0.059509 | -0.082397 | 0.068665 | 0.10529 | -0.054932 | 0.032043 | 0.050354 | 0.086975 | 0.018311 | 121.4539 | 121.312 | -0.013733 | 121.4539 | 121.5088 | 0.19684 | -0.013733 | 121.4813 | 121.4127 | -0.082398 | 121.463 | 121.3394 | -0.073243 | -0.064087 | 121.4951 | 121.4951 | 121.4722 | -0.19684 | 121.4264 | 121.4447 | 121.4996 | -0.09613
2611.4844 | 121.5683 | -121.3852 | 0.07782 | 0.020676 | 0.003277 | 0.067876 | 0.026938 | -0.068255 | -0.021176 | 0.0035654 | 0.014954 | 0.079594 | 0.059693 | -0.043754 | -0.0048364 | 0.016513 | 0.027466 | -0.004578 | 0 | 0.073242 | 0.10986 | 0.059509 | -0.064087 | 0 | 0.009155 | -0.10071 | 0.054932 | 0.068665 | 0.073242 | 0.022888 | 121.4447 | 121.3211 | 0.032043 | 121.3806 | 121.4584 | 0.13733 | -0.050354 | 121.4584 | 121.4081 | -0.022888 | 121.3852 | 121.2845 | -0.1236 | -0.009155 | 121.4951 | 121.4127 | 121.3852 | -0.14191 | 121.4401 | 121.4539 | 121.3943 | -0.054932
2613.2656 | 121.6873 | -121.3806 | 0.07782 | 0.0054168 | 0.0022088 | 0.069799 | 0.028006 | -0.068682 | -0.022244 | 0.0018564 | 0.0073242 | 0.063359 | 0.046662 | -0.043113 | -0.00505 | 0.015231 | 0.013733 | 0.009155 | 0.032043 | 0.073242 | 0.10071 | 0.050354 | -0.054932 | 0.022888 | 0.032043 | -0.054932 | 0.027466 | 0.045776 | 0.09613 | 0.045776 | 121.431 | 121.3257 | 0.022888 | 121.3898 | 121.4539 | 0.12817 | -0.064087 | 121.4767 | 121.4264 | -0.050354 | 121.4035 | 121.3257 | -0.10071 | -0.032044 | 121.4813 | 121.3943 | 121.4127 | -0.13275 | 121.4081 | 121.4264 | 121.4127 | -0.032044
2615.0469 | 121.6232 | -121.431 | 0.10986 | 0.0054168 | -0.0012092 | 0.067663 | 0.030783 | -0.066973 | -0.024167 | 0.0035654 | 0.0073242 | 0.065495 | 0.045166 | -0.043968 | -0.006759 | 0.014804 | 0.054932 | 0.041199 | 0.064087 | 0.11902 | 0.09613 | 0.059509 | -0.064087 | 0.045776 | 0.10529 | -0.064087 | 0.036621 | 0.041199 | 0.07782 | 0.027466 | 121.4905 | 121.3669 | -0.013733 | 121.4722 | 121.55 | 0.18311 | -0.054931 | 121.5088 | 121.4584 | -0.073242 | 121.4767 | 121.3669 | -0.091553 | -0.068664 | 121.5271 | 121.4859 | 121.4951 | -0.17395 | 121.4676 | 121.4722 | 121.5363 | -0.082397
2616.7656 | 121.5683 | -121.3989 | 0.10529 | 0.0054168 | 0.001568 | 0.071935 | 0.030142 | -0.0674 | -0.029721 | -6.615e-05 | -0.0003053 | 0.06699 | 0.049225 | -0.045677 | -0.0063318 | 0.015231 | 0.086975 | 0.15564 | 0.16937 | 0.16937 | 0.082397 | 0.11444 | -0.041199 | 0.068665 | 0.19226 | 0.050354 | 0.004578 | 0.027466 | 0.10071 | 0.064087 | 121.5134 | 121.3577 | -0.022889 | 121.5546 | 121.5683 | 0.21057 | -0.018311 | 121.4996 | 121.463 | -0.10071 | 121.4676 | 121.4493 | -0.013733 | -0.07782 | 121.4813 | 121.4859 | 121.5683 | -0.14649 | 121.4035 | 121.4264 | 121.5912 | -0.041199
2618.5625 | 121.4859 | -121.3669 | 0.11902 | 0.0054168 | -0.0027044 | 0.067876 | 0.026511 | -0.068896 | -0.021817 | 0.0012154 | 0.022583 | 0.097752 | 0.07486 | -0.043968 | -0.0041956 | 0.015018 | 0.013733 | 0.013733 | 0.032043 | 0.073242 | 0.10071 | 0.054932 | -0.07782 | 0 | 0.027466 | -0.11444 | 0.054932 | 0.073242 | 0.091553 | 0.018311 | 121.4218 | 121.2891 | -0.018311 | 121.3806 | 121.4401 | 0.15106 | -0.10529 | 121.4584 | 121.3852 | -0.064087 | 121.3669 | 121.2524 | -0.13275 | -0.045777 | 121.4676 | 121.3806 | 121.3989 | -0.19684 | 121.4218 | 121.4401 | 121.3943 | -0.10071
2620.2812 | 121.4081 | -121.2433 | 0.21057 | -0.0022127 | -0.0014228 | 0.069372 | 0.026724 | -0.068255 | -0.026517 | -0.0022024 | 0.014954 | 0.19004 | 0.16565 | -0.049095 | -0.0065454 | 0.018009 | 0.068665 | 0.11444 | 0.11444 | 0.15106 | 0.068665 | 0.07782 | -0.032043 | 0.064087 | 0.16937 | 0.013733 | 0.086975 | 0.11444 | 0.14648 | 0.064087 | 121.3211 | 121.2112 | -0.14191 | 121.3577 | 121.3943 | 0.18311 | -0.14191 | 121.3898 | 121.3074 | -0.1236 | 121.3074 | 121.257 | -0.050354 | -0.09613 | 121.312 | 121.312 | 121.3577 | -0.24261 | 121.3303 | 121.3577 | 121.4127 | -0.14648
2622.0625 | 115.448 | -111.4197 | 4.1382 | 0.0054168 | -0.0033454 | 0.068945 | 0.026724 | -0.0674 | -0.02374 | 0.00078825 | -0.0003053 | 6.7743 | 6.7296 | -0.14565 | -0.0048364 | 0.11072 | 0.091553 | 0.068665 | 0.086975 | 0.14648 | 0.16937 | 0.11902 | 0 | 1.7899 | 1.9775 | 1.8494 | 3.3279 | 3.36 | 1.9272 | 1.8997 | 111.5387 | 111.4197 | -3.9688 | 111.4883 | 111.5662 | 0.14648 | -4.0466 | 113.3469 | 113.3194 | -0.81024 | 113.2095 | 113.269 | -0.050354 | -0.7782 | 111.5891 | 111.5112 | 111.5067 | -4.1382 | 114.7476 | 114.7797 | 113.3972 | -2.2385
2623.8438 | 121.0281 | -120.7993 | 0.073242 | 0.0054168 | 0.0019952 | 0.070867 | 0.029715 | -0.069964 | -0.030576 | -6.615e-05 | -0.0003053 | 0.060154 | 0.043457 | -0.043968 | -0.0078272 | 0.014804 | 0.10071 | 0.17853 | 0.17395 | 0.16022 | 0.073242 | 0.09613 | -0.032043 | 0.07782 | 0.21057 | 0.059509 | 0.004578 | 0.009155 | 0.09613 | 0.059509 | 120.8954 | 120.7672 | 0 | 120.9778 | 120.9595 | 0.19226 | 0.027466 | 120.8954 | 120.8588 | -0.068664 | 120.8771 | 120.8588 | 0 | -0.064087 | 120.8725 | 120.9 | 120.9732 | -0.10529 | 120.8038 | 120.8084 | 121.0098 | -0.013733
2625.6406 | 121.1838 | -120.8817 | 0.07782 | -0.0022127 | 0.0054132 | 0.074285 | 0.029074 | -0.071673 | -0.028867 | -0.00049335 | -0.0003053 | 0.06229 | 0.044953 | -0.046318 | -0.0097498 | 0.012882 | 0.059509 | 0.10529 | 0.12817 | 0.16022 | 0.064087 | 0.073242 | -0.032043 | 0.073242 | 0.17395 | 0.036621 | 0 | 0.004578 | 0.1236 | 0.050354 | 120.9549 | 120.8496 | -0.013733 | 120.9869 | 121.0419 | 0.19226 | -0.018311 | 121.0052 | 120.932 | -0.07782 | 120.9549 | 120.9183 | -0.013733 | -0.073242 | 120.9457 | 120.9412 | 121.0098 | -0.10986 | 120.8817 | 120.8862 | 121.0556 | -0.027466
2627.3594 | 121.2341 | -120.9503 | 0.082397 | -0.0022127 | 0.0056268 | 0.070654 | 0.02822 | -0.068682 | -0.026944 | -0.001348 | 0.014954 | 0.063145 | 0.044953 | -0.047172 | -0.006759 | 0.015018 | 0.041199 | 0.068665 | 0.10071 | 0.10986 | 0.054932 | 0.082397 | -0.045776 | 0.045776 | 0.10071 | 0.013733 | 0.009155 | 0.013733 | 0.10071 | 0.054932 | 121.0327 | 120.9045 | -0.027465 | 121.019 | 121.0602 | 0.15564 | -0.041198 | 121.051 | 121.0052 | -0.073242 | 120.9961 | 120.9641 | -0.041199 | -0.068664 | 121.0052 | 120.9915 | 121.051 | -0.12817 | 120.9595 | 120.9641 | 121.051 | -0.027465
2629.1406 | 121.2753 | -120.9457 | 0.073242 | 0.0054168 | 0.0024224 | 0.067449 | 0.024161 | -0.068896 | -0.021176 | 0.00036105 | 0.014954 | 0.06699 | 0.046021 | -0.04589 | -0.0048364 | 0.013095 | 0.073242 | 0.032043 | 0.082397 | 0.10986 | 0.07782 | 0.068665 | -0.054932 | 0.086975 | 0.091553 | -0.004578 | -0.004578 | 0.032043 | 0.11902 | 0.050354 | 121.0144 | 120.8908 | 0.004578 | 120.9778 | 121.0556 | 0.16479 | 0 | 121.0648 | 120.9961 | -0.07782 | 121.0327 | 120.9412 | -0.054932 | -0.041199 | 121.0236 | 121.019 | 121.0281 | -0.12817 | 120.9412 | 120.9778 | 121.0373 | -0.022888
2630.8594 | 121.1929 | -121.0144 | 0.11444 | -0.0022127 | 0.00092719 | 0.066167 | 0.02822 | -0.068041 | -0.019895 | 0.00207 | 0.0073242 | 0.066563 | 0.047089 | -0.043754 | -0.003982 | 0.012027 | 0.027466 | -0.018311 | 0.018311 | 0.09613 | 0.12817 | 0.050354 | -0.07782 | -0.004578 | -0.018311 | -0.1236 | 0.036621 | 0.054932 | 0.064087 | 0.022888 | 121.0648 | 120.9366 | 0.013733 | 120.9961 | 121.1105 | 0.17395 | -0.086975 | 121.0785 | 121.0373 | -0.07782 | 121.0098 | 120.8908 | -0.14648 | -0.059509 | 121.1426 | 121.0419 | 121.0327 | -0.19226 | 121.051 | 121.0693 | 120.9961 | -0.091553
2632.6406 | 121.2845 | -121.0052 | 0.09613 | 0.0054168 | 0.0045588 | 0.07044 | 0.027792 | -0.069109 | -0.027585 | -0.00027975 | 0.014954 | 0.071476 | 0.052857 | -0.046745 | -0.0029138 | 0.015872 | 0.09613 | 0.14191 | 0.16937 | 0.16937 | 0.041199 | 0.10529 | -0.045776 | 0.10071 | 0.14648 | 0.045776 | 0 | 0.027466 | 0.11444 | 0.041199 | 121.1105 | 120.9595 | -0.054931 | 121.1472 | 121.1746 | 0.21515 | 0 | 121.1197 | 121.0464 | -0.09613 | 121.106 | 121.051 | 0.004577 | -0.068664 | 121.0464 | 121.1014 | 121.1746 | -0.14191 | 121.0052 | 121.0327 | 121.1517 | -0.054931
2634.4219 | 121.3028 | -121.0281 | 0.07782 | 0.0054168 | 0.004345 | 0.069372 | 0.02587 | -0.067187 | -0.025022 | 0.0016428 | 0.014954 | 0.064854 | 0.046234 | -0.045036 | -0.0054772 | 0.014804 | 0.11444 | 0.14191 | 0.16479 | 0.16937 | 0.073242 | 0.10986 | -0.041199 | 0.11444 | 0.15564 | 0.032043 | -0.013733 | 0.004578 | 0.1236 | 0.054932 | 121.138 | 120.9869 | -0.004578 | 121.17 | 121.1975 | 0.21057 | 0.036621 | 121.1517 | 121.0831 | -0.091553 | 121.1426 | 121.0602 | -0.022889 | -0.073242 | 121.1014 | 121.1426 | 121.1929 | -0.11902 | 121.0144 | 121.0327 | 121.1838 | -0.022888
2636.1719 | 121.3623 | -121.0602 | 0.082397 | 0.013046 | 0.004986 | 0.068731 | 0.023947 | -0.070177 | -0.024167 | 0.0012154 | 0.0073242 | 0.068699 | 0.046448 | -0.046318 | -0.006759 | 0.012882 | 0.086975 | 0.086975 | 0.10529 | 0.14648 | 0.086975 | 0.09613 | -0.036621 | 0.10071 | 0.12817 | 0.018311 | -0.009155 | 0.022888 | 0.11444 | 0.064087 | 121.1563 | 121.0236 | 0.004578 | 121.1472 | 121.2067 | 0.18311 | 0.004578 | 121.1746 | 121.1243 | -0.091552 | 121.1609 | 121.0785 | -0.045776 | -0.059509 | 121.1472 | 121.1472 | 121.1655 | -0.11902 | 121.051 | 121.0831 | 121.1884 | -0.01831
2637.9531 | 121.3623 | -121.0602 | 0.082397 | 0.0054168 | 0.0030634 | 0.066167 | 0.028647 | -0.066332 | -0.024381 | 0.0027108 | -0.0003053 | 0.066349 | 0.049439 | -0.046104 | -0.0065454 | 0.014163 | 0.13275 | 0.13275 | 0.15564 | 0.17853 | 0.041199 | 0.091553 | -0.022888 | 0.10986 | 0.15106 | 0.027466 | 0 | 0.004578 | 0.13275 | 0.059509 | 121.1517 | 121.0373 | -0.041198 | 121.1929 | 121.2387 | 0.20142 | 0.050354 | 121.1929 | 121.1197 | -0.082397 | 121.17 | 121.0876 | -0.032043 | -0.077819 | 121.1014 | 121.1929 | 121.2158 | -0.10528 | 121.0602 | 121.0648 | 121.2112 | -0.022888
2639.7344 | 121.3806 | -121.1197 | 0.068665 | 0.013046 | 0.0041314 | 0.074499 | 0.026511 | -0.066332 | -0.027799 | -6.615e-05 | 0.014954 | 0.067845 | 0.049225 | -0.045463 | -0.0071862 | 0.016086 | 0.041199 | 0.068665 | 0.086975 | 0.1236 | 0.086975 | 0.082397 | -0.041199 | 0.027466 | 0.091553 | -0.004578 | 0.004578 | 0.041199 | 0.09613 | 0.050354 | 121.2021 | 121.0785 | 0.01831 | 121.1884 | 121.2433 | 0.16479 | -0.027466 | 121.2158 | 121.17 | -0.064087 | 121.1472 | 121.1151 | -0.054932 | -0.027466 | 121.2067 | 121.1609 | 121.2067 | -0.10986 | 121.1243 | 121.1609 | 121.2112 | -0.018311
2641.5156 | 121.1288 | -120.6665 | 0.49896 | 0.0054168 | -0.0016364 | 0.074712 | 0.027365 | -0.0674 | -0.024381 | 0.00036105 | 0.022583 | 0.61536 | 0.58136 | -0.056572 | -0.0063318 | 0.023349 | 0.11444 | 0.13275 | 0.15106 | 0.16937 | 0.09613 | 0.09613 | -0.032043 | 0.26093 | 0.34332 | 0.20142 | 0.30212 | 0.33417 | 0.3067 | 0.21973 | 120.7626 | 120.6345 | -0.40283 | 120.7993 | 120.8359 | 0.20142 | -0.38452 | 120.9732 | 120.8862 | -0.19684 | 120.9274 | 120.8679 | -0.018311 | -0.1648 | 120.7626 | 120.7809 | 120.8176 | -0.53101 | 120.9686 | 121.0007 | 121.0098 | -0.27924
2643.3125 | 121.1746 | -120.8954 | 0.2655 | 0.013046 | -0.0054816 | 0.069799 | 0.024588 | -0.06975 | -0.020322 | 0.00014745 | 0.0073242 | 0.30817 | 0.28058 | -0.047386 | -0.0014184 | 0.017154 | 0.091553 | 0.059509 | 0.07782 | 0.1236 | 0.10529 | 0.082397 | -0.045776 | 0.15106 | 0.17395 | 0.022888 | 0.14648 | 0.16937 | 0.17395 | 0.10529 | 120.9778 | 120.8496 | -0.16022 | 120.9549 | 121.019 | 0.16937 | -0.17395 | 121.0693 | 121.0007 | -0.11902 | 121.0464 | 120.9183 | -0.082398 | -0.09613 | 121.0007 | 120.9869 | 120.9732 | -0.31128 | 121.0419 | 121.0648 | 121.0693 | -0.16022
2645.0938 | 121.2753 | -120.7718 | 0.27924 | -0.0022127 | 0.0041314 | 0.071722 | 0.02822 | -0.068468 | -0.02844 | -0.0015616 | 0.0073242 | 0.38828 | 0.36432 | -0.053581 | -0.0074 | 0.021854 | 0.11444 | 0.13733 | 0.16022 | 0.15106 | 0.07782 | 0.086975 | -0.045776 | 0.19226 | 0.30212 | 0.16937 | 0.17395 | 0.16937 | 0.21973 | 0.15564 | 120.8588 | 120.726 | -0.20142 | 120.9091 | 120.9229 | 0.19684 | -0.16479 | 120.9915 | 120.9274 | -0.10529 | 120.9641 | 120.9412 | 0.013733 | -0.10986 | 120.8496 | 120.8862 | 120.932 | -0.32501 | 120.9457 | 120.9412 | 121.0739 | -0.1236
2646.875 | 121.0831 | -120.2545 | 0.68207 | 0.0054168 | -0.0031318 | 0.068304 | 0.029501 | -0.068682 | -0.02139 | 0.00014745 | 0.0073242 | 0.89692 | 0.84796 | -0.056358 | -0.0059046 | 0.027194 | 0.050354 | 0.022888 | 0.064087 | 0.1236 | 0.11444 | 0.082397 | -0.064087 | 0.32044 | 0.37537 | 0.24261 | 0.47607 | 0.49896 | 0.36621 | 0.31128 | 120.3369 | 120.1904 | -0.56763 | 120.2774 | 120.3781 | 0.18768 | -0.63171 | 120.6207 | 120.5658 | -0.20599 | 120.575 | 120.4971 | -0.068664 | -0.18311 | 120.369 | 120.3049 | 120.3186 | -0.74616 | 120.7306 | 120.7535 | 120.6299 | -0.37079
2648.6719 | 121.3211 | -121.0739 | 0.082397 | 0.020676 | 0.0034906 | 0.072576 | 0.026724 | -0.068682 | -0.026517 | 0.00036105 | 0.0073242 | 0.052037 | 0.033844 | -0.045677 | -0.0091088 | 0.017581 | 0.027466 | 0.068665 | 0.10986 | 0.1236 | 0.064087 | 0.073242 | -0.045776 | 0.027466 | 0.10986 | -0.018311 | 0.009155 | 0.004578 | 0.10071 | 0.027466 | 121.1472 | 121.0281 | -0.01831 | 121.1426 | 121.1975 | 0.16937 | -0.054931 | 121.1746 | 121.1014 | -0.073242 | 121.1014 | 121.0556 | -0.045777 | -0.077819 | 121.138 | 121.1014 | 121.1838 | -0.12817 | 121.0831 | 121.0785 | 121.1838 | -0.054931
2650.3906 | 121.2204 | -121.17 | 0.086975 | 0.020676 | -0.0041998 | 0.07044 | 0.024588 | -0.067187 | -0.019681 | 0.0018564 | 0.0073242 | 0.053105 | 0.034485 | -0.045677 | -0.002273 | 0.01395 | 0.09613 | 0.068665 | 0.068665 | 0.10529 | 0.09613 | 0.073242 | -0.073242 | 0.027466 | 0.059509 | -0.091553 | 0.009155 | 0.027466 | 0.059509 | 0.018311 | 121.2433 | 121.0968 | 0.009155 | 121.2387 | 121.2753 | 0.17853 | 0.009155 | 121.2296 | 121.1884 | -0.07782 | 121.1975 | 121.0785 | -0.10986 | -0.059509 | 121.2662 | 121.2662 | 121.2387 | -0.16022 | 121.1792 | 121.1975 | 121.2296 | -0.068664
2652.1875 | 121.3303 | -121.1334 | 0.10071 | 0.013046 | -0.0020636 | 0.070013 | 0.027152 | -0.068468 | -0.022458 | 0.0014292 | -0.0003053 | 0.068699 | 0.047943 | -0.046745 | -0.0018458 | 0.01395 | 0.041199 | 0.050354 | 0.050354 | 0.11444 | 0.082397 | 0.064087 | -0.086975 | 0.036621 | 0.10071 | -0.059509 | 0.009155 | 0.036621 | 0.07782 | 0.022888 | 121.1975 | 121.0464 | -0.018311 | 121.1838 | 121.2479 | 0.20142 | -0.059509 | 121.2112 | 121.1563 | -0.091553 | 121.17 | 121.0739 | -0.082397 | -0.064087 | 121.2158 | 121.1746 | 121.1838 | -0.18768 | 121.1426 | 121.17 | 121.2341 | -0.07782
2653.9844 | 121.3806 | -121.1105 | 0.050354 | -0.0022127 | 0.0030634 | 0.069372 | 0.026083 | -0.071245 | -0.025876 | 0.0018564 | 0.0073242 | 0.048405 | 0.029358 | -0.04589 | -0.0071862 | 0.013309 | 0.10529 | 0.11902 | 0.15564 | 0.17395 | 0.050354 | 0.091553 | -0.022888 | 0.09613 | 0.14648 | 0.013733 | -0.022888 | -0.013733 | 0.11444 | 0.050354 | 121.2021 | 121.0876 | 0 | 121.2296 | 121.2845 | 0.19684 | 0.054932 | 121.225 | 121.1609 | -0.073242 | 121.2067 | 121.1243 | -0.036621 | -0.064087 | 121.1609 | 121.2158 | 121.2662 | -0.073242 | 121.0876 | 121.0968 | 121.257 | 0
2655.7031 | 121.3989 | -121.1151 | 0.073242 | -0.0022127 | 0.0028498 | 0.071294 | 0.031424 | -0.068255 | -0.030149 | 0.00014745 | 0.014954 | 0.0499 | 0.033203 | -0.04589 | -0.0091088 | 0.015659 | 0.10071 | 0.15106 | 0.17853 | 0.16022 | 0.064087 | 0.086975 | -0.041199 | 0.086975 | 0.1831 | 0.050354 | -0.022888 | 0 | 0.10529 | 0.050354 | 121.2021 | 121.0739 | -0.009155 | 121.2662 | 121.2753 | 0.20142 | 0.027466 | 121.2204 | 121.1655 | -0.09613 | 121.2021 | 121.1655 | 0 | -0.073242 | 121.1792 | 121.2158 | 121.2936 | -0.11444 | 121.0922 | 121.1151 | 121.2982 | -0.022888
2657.4844 | 121.3623 | -121.1563 | 0.068665 | 0.0054168 | 0.00028619 | 0.068517 | 0.029288 | -0.070818 | -0.019895 | 0.0016428 | 0.014954 | 0.0499 | 0.03299 | -0.043968 | -0.0071862 | 0.013309 | 0 | -0.032043 | 0.009155 | 0.07782 | 0.091553 | 0.059509 | -0.064087 | -0.036621 | -0.018311 | -0.11444 | 0.004578 | 0.036621 | 0.07782 | 0.009155 | 121.2158 | 121.0922 | 0.022888 | 121.1243 | 121.2341 | 0.14191 | -0.068665 | 121.2341 | 121.1655 | -0.064087 | 121.1197 | 121.0419 | -0.1236 | -0.032044 | 121.2479 | 121.1563 | 121.1655 | -0.13275 | 121.1609 | 121.1929 | 121.138 | -0.05951
2659.2656 | 121.4127 | -121.1426 | 0.054932 | 0.0054168 | 0.0051996 | 0.067022 | 0.026511 | -0.065478 | -0.026731 | -6.615e-05 | 0.0073242 | 0.04755 | 0.02594 | -0.044395 | -0.0046228 | 0.014377 | 0.10529 | 0.10529 | 0.13733 | 0.17395 | 0.054932 | 0.09613 | -0.018311 | 0.091553 | 0.14191 | 0.013733 | -0.022888 | -0.013733 | 0.11444 | 0.050354 | 121.2387 | 121.1243 | 0 | 121.2479 | 121.3165 | 0.19226 | 0.050354 | 121.257 | 121.1929 | -0.07782 | 121.2341 | 121.1563 | -0.036621 | -0.068665 | 121.1975 | 121.2479 | 121.2799 | -0.073243 | 121.1197 | 121.1288 | 121.2845 | -0.004578
2661.0625 | 121.4264 | -121.1517 | 0.050354 | 0.0054168 | 0.0019952 | 0.071294 | 0.023734 | -0.068682 | -0.02609 | 0.0016428 | 0.014954 | 0.057591 | 0.037903 | -0.044395 | -0.003982 | 0.013522 | 0.064087 | 0.064087 | 0.10529 | 0.13733 | 0.068665 | 0.082397 | -0.032043 | 0.09613 | 0.11902 | -0.004578 | -0.022888 | 0.004578 | 0.10986 | 0.041199 | 121.2341 | 121.1197 | 0.018311 | 121.2158 | 121.2891 | 0.16937 | 0.013733 | 121.2616 | 121.1929 | -0.073242 | 121.2479 | 121.1472 | -0.045777 | -0.045776 | 121.2204 | 121.2158 | 121.257 | -0.082397 | 121.1288 | 121.1563 | 121.2708 | -0.009155
2662.7812 | 121.4264 | -121.1746 | 0.050354 | 0.013046 | 0.003277 | 0.072576 | 0.029074 | -0.0674 | -0.028226 | -0.0011344 | 0.0073242 | 0.046055 | 0.028504 | -0.045463 | -0.0082544 | 0.014591 | 0.10529 | 0.16022 | 0.16479 | 0.14648 | 0.036621 | 0.091553 | -0.032043 | 0.086975 | 0.18768 | 0.045776 | -0.018311 | -0.004578 | 0.09613 | 0.050354 | 121.2662 | 121.1426 | -0.013733 | 121.3348 | 121.3211 | 0.17853 | 0.054932 | 121.2708 | 121.225 | -0.068665 | 121.2616 | 121.2204 | -0.004578 | -0.054932 | 121.2112 | 121.2799 | 121.3394 | -0.082397 | 121.1563 | 121.17 | 121.3623 | 0
2664.5781 | 121.3898 | -121.3165 | 0.086975 | -0.0022127 | -0.0020636 | 0.075353 | 0.029288 | -0.065691 | -0.024808 | -0.00092075 | 0.0073242 | 0.047978 | 0.027436 | -0.04525 | -0.0054772 | 0.014591 | 0.054932 | 0.09613 | 0.11444 | 0.11902 | 0.07782 | 0.064087 | -0.036621 | -0.004578 | 0.073242 | -0.073242 | 0.013733 | 0.013733 | 0.082397 | 0.022888 | 121.3806 | 121.2799 | -0.009155 | 121.4127 | 121.4355 | 0.15564 | -0.032043 | 121.3989 | 121.3394 | -0.073242 | 121.312 | 121.2433 | -0.09613 | -0.073242 | 121.3943 | 121.3715 | 121.431 | -0.1236 | 121.3303 | 121.3303 | 121.3898 | -0.064087
2666.2969 | 121.582 | -121.2799 | 0.073242 | 0.0054168 | 0.0051996 | 0.071722 | 0.027579 | -0.070818 | -0.028012 | 0.00014745 | 0.0073242 | 0.047337 | 0.027436 | -0.044822 | -0.0093226 | 0.014591 | 0.091553 | 0.1236 | 0.14648 | 0.13275 | 0.086975 | 0.086975 | -0.032043 | 0.064087 | 0.16022 | 0.054932 | 0 | -0.013733 | 0.10529 | 0.036621 | 121.3669 | 121.2479 | 0.013733 | 121.4035 | 121.4127 | 0.16479 | 0.018311 | 121.3852 | 121.3165 | -0.073242 | 121.344 | 121.3348 | 0.018311 | -0.086975 | 121.3669 | 121.3715 | 121.4264 | -0.10529 | 121.2799 | 121.2662 | 121.4401 | -0.036621
2668.1094 | 121.5088 | -121.3165 | 0.064087 | 0.0054168 | -0.0041998 | 0.071294 | 0.026297 | -0.069323 | -0.020322 | 0.00014745 | 0.0073242 | 0.049687 | 0.027649 | -0.042045 | -0.003982 | 0.012241 | 0.045776 | 0.009155 | 0.041199 | 0.10529 | 0.09613 | 0.050354 | -0.086975 | 0.027466 | 0.073242 | -0.064087 | 0.027466 | 0.018311 | 0.068665 | -0.009155 | 121.3669 | 121.2296 | 0.032043 | 121.3257 | 121.4218 | 0.19226 | -0.018311 | 121.3852 | 121.3074 | -0.036621 | 121.344 | 121.2524 | -0.054932 | -0.045776 | 121.4127 | 121.3623 | 121.3577 | -0.15106 | 121.344 | 121.3348 | 121.3898 | -0.073242
2669.8281 | 121.5546 | -121.3394 | 0.059509 | 0.0054168 | 0.0039178 | 0.069158 | 0.024588 | -0.068255 | -0.023953 | 0.0014292 | 0.014954 | 0.047978 | 0.027649 | -0.046531 | -0.005691 | 0.015659 | 0.11902 | 0.12817 | 0.16479 | 0.16022 | 0.050354 | 0.10529 | -0.018311 | 0.10071 | 0.14191 | 0.022888 | -0.032043 | -0.004578 | 0.10986 | 0.050354 | 121.4447 | 121.3211 | -0.009155 | 121.4676 | 121.4996 | 0.17853 | 0.05951 | 121.4493 | 121.3898 | -0.091552 | 121.4401 | 121.3623 | -0.027466 | -0.064087 | 121.3898 | 121.4584 | 121.5042 | -0.07782 | 121.3074 | 121.3348 | 121.4813 | -0.009155
2671.6094 | 121.5134 | -121.3211 | 0.09613 | 0.013046 | -0.0037726 | 0.07044 | 0.030142 | -0.065905 | -0.024381 | -0.001348 | 0.0073242 | 0.048832 | 0.02829 | -0.042472 | -0.0063318 | 0.012454 | 0.018311 | -0.013733 | 0.022888 | 0.082397 | 0.091553 | 0.027466 | -0.091553 | -0.022888 | 0.032043 | -0.10071 | 0.027466 | 0.045776 | 0.045776 | 0.009155 | 121.3486 | 121.2296 | -0.004577 | 121.3074 | 121.4035 | 0.17395 | -0.077819 | 121.3669 | 121.3303 | -0.068664 | 121.2982 | 121.2204 | -0.10986 | -0.050354 | 121.4127 | 121.3394 | 121.344 | -0.18768 | 121.3486 | 121.3669 | 121.3531 | -0.086975
2673.4062 | 121.4813 | -121.3806 | 0.091553 | 0.0054168 | -0.0056952 | 0.070654 | 0.024802 | -0.068896 | -0.022031 | 0.00207 | 0.014954 | 0.051396 | 0.026795 | -0.043113 | -0.003341 | 0.014163 | 0.091553 | 0.064087 | 0.073242 | 0.10529 | 0.10071 | 0.064087 | -0.054932 | 0.032043 | 0.073242 | -0.082397 | 0.004578 | 0.032043 | 0.073242 | 0.018311 | 121.4447 | 121.3257 | 0.009155 | 121.4447 | 121.4859 | 0.16022 | 0 | 121.4539 | 121.3989 | -0.086975 | 121.4127 | 121.2982 | -0.10071 | -0.05951 | 121.4813 | 121.4722 | 121.4539 | -0.14649 | 121.3852 | 121.4127 | 121.4539 | -0.073242
2675.1406 | 121.4813 | -121.3806 | 0.07782 | -0.0022127 | -0.0048406 | 0.067876 | 0.02587 | -0.068468 | -0.022244 | 0.0016428 | 0.022583 | 0.049473 | 0.027863 | -0.042686 | -0.002273 | 0.014377 | 0.018311 | -0.022888 | 0.018311 | 0.073242 | 0.091553 | 0.054932 | -0.086975 | -0.027466 | 0.013733 | -0.12817 | 0.036621 | 0.032043 | 0.073242 | 0.009155 | 121.4355 | 121.2936 | 0.013733 | 121.3577 | 121.4539 | 0.16022 | -0.059509 | 121.4539 | 121.3898 | -0.041199 | 121.3531 | 121.2524 | -0.13733 | -0.045777 | 121.4722 | 121.3989 | 121.3989 | -0.16479 | 121.4172 | 121.4127 | 121.3943 | -0.068665
2676.9375 | 121.5363 | -121.4218 | 0.091553 | -0.0022127 | -0.002918 | 0.07279 | 0.029288 | -0.067187 | -0.028226 | -0.00049335 | -0.0003053 | 0.050541 | 0.029785 | -0.045463 | -0.0069726 | 0.015872 | 0.018311 | 0.041199 | 0.054932 | 0.091553 | 0.073242 | 0.045776 | -0.073242 | -0.027466 | 0.059509 | -0.086975 | 0.009155 | 0.032043 | 0.054932 | 0.009155 | 121.4676 | 121.3486 | -0.018311 | 121.463 | 121.5134 | 0.16479 | -0.073242 | 121.4767 | 121.431 | -0.082398 | 121.3943 | 121.3348 | -0.09613 | -0.05951 | 121.4951 | 121.4401 | 121.4767 | -0.16479 | 121.431 | 121.4539 | 121.4813 | -0.082398
2678.7344 | 121.6507 | -121.344 | 0.07782 | 0.0054168 | 0.001568 | 0.069158 | 0.025015 | -0.066546 | -0.023313 | -0.00027975 | 0.014954 | 0.080235 | 0.061188 | -0.044822 | -0.0048364 | 0.016513 | 0.009155 | -0.009155 | 0.018311 | 0.068665 | 0.10986 | 0.054932 | -0.082397 | 0.009155 | 0.018311 | -0.082397 | 0.022888 | 0.050354 | 0.086975 | 0.018311 | 121.3989 | 121.2616 | 0.032043 | 121.3348 | 121.4127 | 0.15106 | -0.068665 | 121.431 | 121.3623 | -0.054932 | 121.3531 | 121.2616 | -0.10071 | -0.027466 | 121.4539 | 121.3531 | 121.3623 | -0.16022 | 121.3669 | 121.3943 | 121.3623 | -0.059509
2680.5156 | 121.6919 | -121.4127 | 0.073242 | 0.0054168 | 0.004345 | 0.06809 | 0.026938 | -0.068255 | -0.024381 | 0.0022836 | -0.0003053 | 0.045414 | 0.028504 | -0.046104 | -0.0069726 | 0.013309 | 0.09613 | 0.082397 | 0.13275 | 0.15106 | 0.050354 | 0.09613 | -0.027466 | 0.07782 | 0.12817 | 0.022888 | -0.032043 | -0.004578 | 0.10529 | 0.041199 | 121.5088 | 121.3852 | -0.022888 | 121.4951 | 121.5637 | 0.17853 | 0.022888 | 121.5179 | 121.4539 | -0.10529 | 121.4905 | 121.4355 | -0.018311 | -0.07782 | 121.463 | 121.5088 | 121.5454 | -0.10071 | 121.3806 | 121.4081 | 121.5408 | -0.032043
2682.25 | 121.6599 | -121.431 | 0.036621 | 0.013046 | 0.0054132 | 0.067449 | 0.026083 | -0.070391 | -0.027799 | 0.00036105 | 0.0073242 | 0.044346 | 0.026367 | -0.046531 | -0.006759 | 0.014591 | 0.073242 | 0.13275 | 0.17395 | 0.15106 | 0.054932 | 0.07782 | -0.045776 | 0.054932 | 0.1236 | 0.032043 | -0.041199 | -0.004578 | 0.09613 | 0.045776 | 121.5088 | 121.3852 | 0.018311 | 121.5637 | 121.582 | 0.19684 | 0.036621 | 121.5271 | 121.4767 | -0.07782 | 121.4859 | 121.463 | -0.013733 | -0.041199 | 121.4859 | 121.5042 | 121.6049 | -0.082397 | 121.3898 | 121.4264 | 121.5546 | 0.009155
2684.0469 | 121.7285 | -121.4035 | 0.041199 | 0.013046 | 0.0030634 | 0.072149 | 0.028647 | -0.0674 | -0.024594 | 0.0012154 | 0.0073242 | 0.047978 | 0.029358 | -0.044395 | -0.0044092 | 0.014163 | 0.032043 | 0.004578 | 0.054932 | 0.082397 | 0.10071 | 0.068665 | -0.045776 | 0.032043 | 0.068665 | -0.045776 | 0 | 0.009155 | 0.086975 | 0.050354 | 121.4722 | 121.3577 | 0.059509 | 121.4081 | 121.4859 | 0.12817 | -0.009156 | 121.4905 | 121.4539 | -0.041199 | 121.4355 | 121.3577 | -0.09613 | -0.032044 | 121.5042 | 121.4355 | 121.4584 | -0.086975 | 121.4035 | 121.4127 | 121.4722 | 0.009155
2685.7656 | 121.6415 | -121.4767 | 0.086975 | 0.020676 | -0.0050544 | 0.071722 | 0.030356 | -0.0674 | -0.023953 | 0.0010018 | -0.0079343 | 0.04755 | 0.030426 | -0.043754 | -0.0065454 | 0.014377 | 0 | -0.022888 | 0.013733 | 0.07782 | 0.086975 | 0.045776 | -0.10529 | -0.022888 | 0.045776 | -0.09613 | 0.032043 | 0.045776 | 0.064087 | 0.013733 | 121.5225 | 121.3715 | 0 | 121.4539 | 121.5546 | 0.18311 | -0.086975 | 121.5408 | 121.4905 | -0.054932 | 121.4539 | 121.3806 | -0.10986 | -0.041199 | 121.5637 | 121.4767 | 121.4905 | -0.19226 | 121.5088 | 121.5225 | 121.5225 | -0.073242
2687.5469 | 121.7514 | -121.431 | 0.045776 | -0.0022127 | 0.0022088 | 0.069799 | 0.026511 | -0.067828 | -0.024381 | 0.0014292 | 0.014954 | 0.049473 | 0.032349 | -0.04525 | -0.0065454 | 0.016086 | 0.050354 | 0.041199 | 0.07782 | 0.10986 | 0.07782 | 0.068665 | -0.054932 | 0.073242 | 0.10986 | -0.009155 | -0.022888 | -0.018311 | 0.10529 | 0.036621 | 121.4996 | 121.376 | 0.032044 | 121.4722 | 121.5408 | 0.16479 | 0.004578 | 121.5363 | 121.4676 | -0.068664 | 121.5042 | 121.4218 | -0.045776 | -0.064087 | 121.5088 | 121.4813 | 121.5088 | -0.10071 | 121.4081 | 121.4127 | 121.5408 | -0.009155
2689.3438 | 120.9869 | -120.9229 | 0.086975 | 0.0054168 | -0.0044134 | 0.067663 | 0.023947 | -0.069109 | -0.02139 | 0.00078825 | 0.014954 | 0.047337 | 0.026581 | -0.0429 | -0.0041956 | 0.012882 | -0.009155 | -0.032043 | 0.013733 | 0.064087 | 0.09613 | 0.054932 | -0.073242 | -0.036621 | -0.013733 | -0.15106 | 0.018311 | 0.027466 | 0.073242 | 0.009155 | 120.9778 | 120.8496 | 0.009155 | 120.8908 | 120.9869 | 0.13733 | -0.09613 | 120.9961 | 120.932 | -0.068664 | 120.8862 | 120.7718 | -0.16022 | -0.059509 | 121.019 | 120.9137 | 120.9366 | -0.16022 | 120.9412 | 120.9503 | 120.9091 | -0.07782
2691.0781 | 121.3806 | -121.1151 | 0.068665 | 0.0054168 | 0.0064814 | 0.074499 | 0.030569 | -0.070818 | -0.030149 | -0.00049335 | 0.022583 | 0.041355 | 0.029785 | -0.045036 | -0.0093226 | 0.01694 | 0.009155 | 0.059509 | 0.086975 | 0.11444 | 0.059509 | 0.086975 | -0.041199 | -0.004578 | 0.09613 | -0.013733 | -0.009155 | 0 | 0.09613 | 0.013733 | 121.2021 | 121.0739 | -0.009156 | 121.1746 | 121.2296 | 0.15564 | -0.05951 | 121.2112 | 121.1288 | -0.07782 | 121.1105 | 121.1014 | -0.027466 | -0.068665 | 121.1746 | 121.1243 | 121.2021 | -0.10986 | 121.106 | 121.1151 | 121.2112 | -0.054932
2692.8438 | 121.3303 | -121.2387 | 0.091553 | 0.0054168 | -0.0037726 | 0.072149 | 0.027792 | -0.068468 | -0.027585 | -0.0017752 | 0.014954 | 0.046269 | 0.028931 | -0.044395 | -0.0086816 | 0.014591 | 0 | 0.013733 | 0.045776 | 0.073242 | 0.091553 | 0.041199 | -0.091553 | -0.050354 | 0.032043 | -0.09613 | 0.027466 | 0.041199 | 0.059509 | -0.009155 | 121.2799 | 121.1472 | 0 | 121.2524 | 121.3119 | 0.16479 | -0.091553 | 121.2982 | 121.2296 | -0.064087 | 121.1884 | 121.1426 | -0.086975 | -0.050354 | 121.3303 | 121.2387 | 121.2845 | -0.18311 | 121.2662 | 121.2799 | 121.2708 | -0.10071
2694.5781 | 121.4951 | -121.2067 | 0.041199 | 0.013046 | 0.0054132 | 0.073858 | 0.02886 | -0.068896 | -0.031003 | -6.615e-05 | -0.0079343 | 0.041569 | 0.026154 | -0.04589 | -0.0095362 | 0.012668 | 0.091553 | 0.16479 | 0.17853 | 0.16022 | 0.073242 | 0.086975 | -0.036621 | 0.073242 | 0.18768 | 0.068665 | -0.018311 | 0 | 0.10986 | 0.041199 | 121.2936 | 121.17 | 0.032043 | 121.3715 | 121.3669 | 0.19684 | 0.050354 | 121.3165 | 121.2479 | -0.05951 | 121.2799 | 121.2753 | 0.027466 | -0.041199 | 121.2799 | 121.2982 | 121.3852 | -0.07782 | 121.1884 | 121.2067 | 121.3943 | 0
2696.3594 | 121.0602 | -120.932 | 0.073242 | 0.0054168 | 0.0041314 | 0.071081 | 0.031638 | -0.069109 | -0.027371 | -0.00049335 | 0.0073242 | 0.045414 | 0.029145 | -0.044181 | -0.0076136 | 0.012882 | 0.10529 | 0.15564 | 0.15564 | 0.16022 | 0.050354 | 0.073242 | -0.059509 | 0.068665 | 0.1831 | 0.036621 | -0.022888 | -0.022888 | 0.091553 | 0.054932 | 121.0052 | 120.8725 | -0.022888 | 121.0876 | 121.0922 | 0.21973 | 0.032044 | 121.0236 | 120.9869 | -0.09613 | 121.0007 | 120.9686 | -0.018311 | -0.09613 | 120.9824 | 121.0373 | 121.0876 | -0.13275 | 120.9091 | 120.9091 | 121.1151 | -0.01831
2698.0781 | 121.2021 | -121.1472 | 0.10071 | 0.0054168 | 0.00028619 | 0.071722 | 0.033347 | -0.069964 | -0.024594 | 0.00036105 | 0.0073242 | 0.047764 | 0.030213 | -0.044822 | -0.0063318 | 0.014377 | 0.041199 | 0.07782 | 0.082397 | 0.11444 | 0.064087 | 0.054932 | -0.064087 | -0.027466 | 0.050354 | -0.091553 | 0.036621 | 0.022888 | 0.064087 | 0.009155 | 121.2021 | 121.0831 | -0.036621 | 121.225 | 121.2616 | 0.17853 | -0.059509 | 121.2112 | 121.1563 | -0.064087 | 121.1197 | 121.0556 | -0.10071 | -0.07782 | 121.2112 | 121.1884 | 121.2296 | -0.1648 | 121.1838 | 121.17 | 121.1975 | -0.091553
2699.8594 | 121.3028 | -121.1838 | 0.082397 | 0.0054168 | -0.0048406 | 0.068304 | 0.026297 | -0.066759 | -0.019254 | 0.0022836 | 0.0073242 | 0.050328 | 0.029145 | -0.044822 | -0.0027002 | 0.01395 | 0.073242 | 0.050354 | 0.068665 | 0.11902 | 0.082397 | 0.045776 | -0.068665 | 0.045776 | 0.07782 | -0.068665 | 0 | 0.018311 | 0.09613 | 0.018311 | 121.2296 | 121.1151 | 0 | 121.2341 | 121.3028 | 0.18768 | -0.009155 | 121.2799 | 121.2021 | -0.082397 | 121.2296 | 121.1151 | -0.086976 | -0.064086 | 121.2662 | 121.257 | 121.2524 | -0.15106 | 121.1838 | 121.2021 | 121.2616 | -0.064086
2701.6562 | 121.4172 | -121.1792 | 0.050354 | 0.0054168 | 0.0047724 | 0.071722 | 0.02886 | -0.069323 | -0.029508 | -0.0011344 | 0.014954 | 0.051182 | 0.031067 | -0.045463 | -0.0082544 | 0.015872 | 0.018311 | 0.07782 | 0.11902 | 0.11444 | 0.054932 | 0.073242 | -0.064087 | 0.036621 | 0.11444 | 0.009155 | 0.004578 | 0.027466 | 0.086975 | 0.027466 | 121.2524 | 121.1151 | 0.004578 | 121.257 | 121.2936 | 0.17853 | -0.032043 | 121.2662 | 121.2067 | -0.045776 | 121.2158 | 121.1884 | -0.018311 | -0.022888 | 121.2341 | 121.1975 | 121.2982 | -0.11444 | 121.1838 | 121.2067 | 121.2936 | -0.022888
2703.4375 | 120.9961 | -120.9 | 0.064087 | -0.0022127 | -0.0012092 | 0.067663 | 0.023947 | -0.069323 | -0.022458 | -0.00092075 | 0.022583 | 0.050968 | 0.02829 | -0.043113 | -0.003341 | 0.012241 | 0.013733 | -0.027466 | 0.004578 | 0.086975 | 0.091553 | 0.041199 | -0.082397 | -0.032043 | -0.004578 | -0.1236 | 0.036621 | 0.032043 | 0.064087 | -0.004578 | 120.9412 | 120.8176 | 0.027466 | 120.8725 | 120.9869 | 0.16937 | -0.050354 | 120.9641 | 120.8954 | -0.027466 | 120.8679 | 120.7764 | -0.11902 | -0.032044 | 120.9915 | 120.9137 | 120.9045 | -0.14648 | 120.9366 | 120.932 | 120.8954 | -0.068665
2705.2344 | 121.1929 | -120.9778 | 0.068665 | 0.0054168 | 0.0051996 | 0.070013 | 0.025229 | -0.068255 | -0.029721 | 0.0016428 | 0.014954 | 0.047337 | 0.031067 | -0.047172 | -0.0065454 | 0.0163 | 0.027466 | 0.073242 | 0.10529 | 0.11444 | 0.054932 | 0.07782 | -0.041199 | 0.022888 | 0.086975 | -0.022888 | -0.022888 | 0 | 0.09613 | 0.036621 | 121.0556 | 120.9366 | -0.013733 | 121.051 | 121.0922 | 0.15564 | -0.041199 | 121.0739 | 121.0144 | -0.091553 | 121.0007 | 120.9549 | -0.059509 | -0.068665 | 121.0327 | 121.0052 | 121.0831 | -0.10986 | 120.9549 | 120.9778 | 121.0648 | -0.032044
2707.0312 | 121.2067 | -121.0968 | 0.09613 | -0.0022127 | -0.0041998 | 0.072149 | 0.030142 | -0.068041 | -0.021817 | -6.615e-05 | 0.0073242 | 0.08173 | 0.060547 | -0.045463 | -0.0074 | 0.014377 | 0.009155 | 0.004578 | 0.022888 | 0.068665 | 0.09613 | 0.050354 | -0.086975 | -0.022888 | 0.018311 | -0.1236 | 0.032043 | 0.064087 | 0.068665 | 0.032043 | 121.1472 | 121.0098 | 0 | 121.1014 | 121.1655 | 0.15564 | -0.086975 | 121.1655 | 121.1288 | -0.064087 | 121.0739 | 120.9732 | -0.15564 | -0.032043 | 121.1929 | 121.106 | 121.1197 | -0.1831 | 121.1288 | 121.1609 | 121.1151 | -0.064087
2708.75 | 121.3394 | -121.0648 | 0.059509 | 0.0054168 | 0.0073358 | 0.071722 | 0.026083 | -0.068682 | -0.02844 | 0.00014745 | -0.0003053 | 0.046696 | 0.02829 | -0.044181 | -0.0074 | 0.015659 | 0.045776 | 0.059509 | 0.09613 | 0.10529 | 0.064087 | 0.07782 | -0.054932 | 0.004578 | 0.086975 | -0.022888 | -0.018311 | 0.004578 | 0.086975 | 0.041199 | 121.1426 | 121.0098 | 0.004578 | 121.1243 | 121.17 | 0.16022 | -0.013733 | 121.1517 | 121.106 | -0.07782 | 121.0693 | 121.0419 | -0.064087 | -0.054931 | 121.1288 | 121.1105 | 121.1609 | -0.11444 | 121.0464 | 121.0693 | 121.1517 | -0.01831
2710.5312 | 121.4264 | -121.1014 | 0.041199 | 0.0054168 | 0.0075494 | 0.072149 | 0.024588 | -0.068041 | -0.023313 | 0.0016428 | 0.014954 | 0.049473 | 0.03064 | -0.047386 | -0.0029138 | 0.012027 | 0.1236 | 0.1236 | 0.16022 | 0.14191 | 0.054932 | 0.091553 | -0.036621 | 0.10071 | 0.14191 | 0.013733 | -0.009155 | 0.009155 | 0.10529 | 0.032043 | 121.1929 | 121.0648 | 0.013733 | 121.225 | 121.2433 | 0.17853 | 0.082397 | 121.2067 | 121.1334 | -0.050354 | 121.2021 | 121.1151 | -0.01831 | -0.032044 | 121.1563 | 121.225 | 121.2616 | -0.07782 | 121.0922 | 121.1105 | 121.2433 | -0.009156
2712.25 | 120.726 | -120.4971 | 0.11902 | -0.0022127 | 0.0054132 | 0.07279 | 0.029074 | -0.067828 | -0.025235 | -0.00027975 | 0.0073242 | 0.12125 | 0.10199 | -0.046745 | -0.0095362 | 0.015018 | 0.050354 | 0.059509 | 0.10986 | 0.11444 | 0.068665 | 0.07782 | -0.045776 | 0.041199 | 0.091553 | 0.009155 | 0.041199 | 0.036621 | 0.1236 | 0.064087 | 120.575 | 120.4514 | -0.050354 | 120.5566 | 120.6116 | 0.16022 | -0.068665 | 120.6207 | 120.5612 | -0.07782 | 120.5383 | 120.5063 | -0.054932 | -0.082398 | 120.5658 | 120.5475 | 120.607 | -0.16479 | 120.5383 | 120.5338 | 120.5887 | -0.054932
2714.0312 | 120.9824 | -120.7718 | 0.082397 | 0.0054168 | 0.0017816 | 0.07279 | 0.028433 | -0.065905 | -0.02609 | 0.00057465 | 0.014954 | 0.044346 | 0.027222 | -0.04525 | -0.0076136 | 0.014804 | 0.11902 | 0.14191 | 0.16937 | 0.16022 | 0.054932 | 0.082397 | -0.045776 | 0.091553 | 0.16937 | 0.022888 | -0.032043 | -0.004578 | 0.10986 | 0.027466 | 120.8542 | 120.726 | -0.027465 | 120.9137 | 120.932 | 0.20599 | 0.036622 | 120.8817 | 120.7993 | -0.11444 | 120.8633 | 120.7947 | -0.004578 | -0.086975 | 120.8267 | 120.8908 | 120.9412 | -0.12817 | 120.7397 | 120.7672 | 120.9412 | -0.054931
2715.8281 | 121.1105 | -120.6665 | 0.1831 | 0.0054168 | 0.0034906 | 0.069585 | 0.024374 | -0.070177 | -0.020749 | 0.0010018 | 0.014954 | 0.2349 | 0.20966 | -0.047172 | -0.0048364 | 0.014804 | 0.059509 | 0.027466 | 0.059509 | 0.10071 | 0.09613 | 0.07782 | -0.068665 | 0.12817 | 0.14191 | 0.032043 | 0.073242 | 0.091553 | 0.15564 | 0.10071 | 120.7443 | 120.5978 | -0.086975 | 120.694 | 120.7672 | 0.16937 | -0.1236 | 120.8221 | 120.7672 | -0.10986 | 120.7947 | 120.6985 | -0.068665 | -0.091552 | 120.7626 | 120.726 | 120.726 | -0.25177 | 120.7397 | 120.7581 | 120.8084 | -0.082397
2717.5938 | 121.1243 | -120.7306 | 0.15564 | 0.013046 | 0.004345 | 0.070867 | 0.023306 | -0.0674 | -0.023099 | 0.00207 | 0.0073242 | 0.18662 | 0.16138 | -0.04525 | -0.0044092 | 0.015445 | 0.036621 | -0.004578 | 0.013733 | 0.082397 | 0.10071 | 0.064087 | -0.064087 | 0.064087 | 0.059509 | -0.032043 | 0.091553 | 0.09613 | 0.09613 | 0.059509 | 120.7947 | 120.6665 | -0.054932 | 120.726 | 120.813 | 0.14648 | -0.11902 | 120.8267 | 120.7901 | -0.064087 | 120.7947 | 120.6985 | -0.091552 | -0.05951 | 120.8313 | 120.7672 | 120.7443 | -0.21973 | 120.8221 | 120.8267 | 120.7901 | -0.096131
2719.3125 | 121.1151 | -120.813 | 0.16022 | 0.013046 | 0.0079766 | 0.072363 | 0.027152 | -0.072314 | -0.028226 | 0.00014745 | 0.0073242 | 0.17615 | 0.15326 | -0.046745 | -0.0059046 | 0.017581 | 0.086975 | 0.091553 | 0.11902 | 0.13275 | 0.045776 | 0.07782 | -0.032043 | 0.091553 | 0.12817 | 0.027466 | 0.032043 | 0.064087 | 0.15106 | 0.07782 | 120.8908 | 120.7809 | -0.11444 | 120.9045 | 120.9457 | 0.16479 | -0.073242 | 120.9641 | 120.8908 | -0.12817 | 120.9045 | 120.8405 | -0.050354 | -0.09613 | 120.8588 | 120.9 | 120.932 | -0.19226 | 120.845 | 120.8771 | 120.9412 | -0.082397
2721.0469 | 121.1792 | -120.9503 | 0.064087 | 0.020676 | 0.006054 | 0.070654 | 0.026724 | -0.070177 | -0.025876 | 0.0012154 | 0.030213 | 0.050541 | 0.029999 | -0.044822 | -0.0065454 | 0.014377 | 0.10986 | 0.11444 | 0.14191 | 0.13733 | 0.050354 | 0.073242 | -0.041199 | 0.050354 | 0.091553 | -0.018311 | -0.018311 | 0 | 0.091553 | 0.041199 | 121.0236 | 120.9091 | -0.013733 | 121.0648 | 121.0876 | 0.17853 | 0.045776 | 121.0419 | 120.9915 | -0.082398 | 121.0007 | 120.932 | -0.05951 | -0.064087 | 121.0007 | 121.0602 | 121.0922 | -0.10529 | 120.932 | 120.9503 | 121.0419 | -0.022888
2722.7656 | 121.2067 | -120.9641 | 0.086975 | 0.013046 | 0.0051996 | 0.073217 | 0.024802 | -0.069109 | -0.027158 | 0.00036105 | 0.014954 | 0.071903 | 0.05008 | -0.044181 | -0.0071862 | 0.017154 | 0.064087 | 0.082397 | 0.10986 | 0.13275 | 0.073242 | 0.09613 | -0.036621 | 0.041199 | 0.091553 | -0.022888 | 0.004578 | 0.004578 | 0.10529 | 0.027466 | 121.0602 | 120.9274 | -0.013733 | 121.0464 | 121.0968 | 0.16937 | -0.022888 | 121.0693 | 120.9915 | -0.082397 | 121.0052 | 120.9412 | -0.050354 | -0.082397 | 121.0373 | 121.0281 | 121.0739 | -0.1236 | 120.9686 | 120.9686 | 121.0556 | -0.059509
2724.4688 | 121.1426 | -120.9457 | 0.11444 | 0.0054168 | 0.0028498 | 0.068304 | 0.024374 | -0.0721 | -0.022885 | 0.00036105 | 0.0073242 | 0.11335 | 0.081482 | -0.04589 | -0.0054772 | 0.01395 | 0.11444 | 0.091553 | 0.11902 | 0.14648 | 0.07782 | 0.086975 | -0.041199 | 0.1236 | 0.14648 | 0.013733 | 0 | 0.041199 | 0.13275 | 0.068665 | 121.0327 | 120.9045 | -0.036621 | 121.0373 | 121.0922 | 0.18768 | 0 | 121.0785 | 121.0144 | -0.11444 | 121.0693 | 120.9595 | -0.054932 | -0.073242 | 121.0236 | 121.0602 | 121.0648 | -0.15564 | 120.9457 | 120.9869 | 121.0922 | -0.045776
2726.1719 | 121.2845 | -120.7993 | 0.22888 | 0.013046 | 0.0041314 | 0.072149 | 0.02822 | -0.069537 | -0.028012 | -0.00070715 | 0.014954 | 0.33829 | 0.31113 | -0.051872 | -0.0065454 | 0.017581 | 0.11444 | 0.13733 | 0.15564 | 0.15564 | 0.059509 | 0.09613 | -0.027466 | 0.19226 | 0.27924 | 0.15106 | 0.13275 | 0.14191 | 0.19226 | 0.12817 | 120.8954 | 120.7718 | -0.16937 | 120.9366 | 120.9549 | 0.18311 | -0.11444 | 120.9915 | 120.9274 | -0.096131 | 120.9915 | 120.9503 | 0.022888 | -0.086975 | 120.8588 | 120.9137 | 120.9549 | -0.25635 | 120.932 | 120.9412 | 121.0785 | -0.10071
2727.875 | 121.0098 | -120.4697 | 0.48523 | -0.0022127 | 0.0011408 | 0.070013 | 0.025443 | -0.066546 | -0.019254 | 0.00078825 | 0.0073242 | 0.53269 | 0.50574 | -0.049522 | -0.0037684 | 0.020999 | 0.041199 | -0.045776 | -0.013733 | 0.07782 | 0.10986 | 0.068665 | -0.07782 | 0.23346 | 0.19684 | 0.050354 | 0.32501 | 0.3479 | 0.27466 | 0.20599 | 120.5383 | 120.3918 | -0.37537 | 120.4239 | 120.5475 | 0.15564 | -0.44403 | 120.7443 | 120.6757 | -0.16022 | 120.7031 | 120.52 | -0.15564 | -0.13733 | 120.5795 | 120.5109 | 120.4559 | -0.56305 | 120.7947 | 120.8176 | 120.6665 | -0.27924
2729.6094 | 121.0556 | -120.3735 | 0.50812 | -0.0022127 | -0.0022772 | 0.071081 | 0.027792 | -0.070818 | -0.022885 | 0.0018564 | 0.0073242 | 0.69397 | 0.65186 | -0.052726 | -0.0059046 | 0.022281 | 0.041199 | -0.018311 | 0.004578 | 0.082397 | 0.10071 | 0.050354 | -0.07782 | 0.17853 | 0.1831 | 0.091553 | 0.35706 | 0.37537 | 0.27466 | 0.19684 | 120.4239 | 120.2957 | -0.40741 | 120.3552 | 120.4559 | 0.16022 | -0.46692 | 120.6482 | 120.5704 | -0.15106 | 120.5521 | 120.4651 | -0.10529 | -0.13275 | 120.4742 | 120.4147 | 120.3781 | -0.58594 | 120.7306 | 120.7489 | 120.5566 | -0.31128
2731.3438 | 121.2067 | -120.8954 | 0.17853 | 0.013046 | 7.2586e-05 | 0.07279 | 0.033774 | -0.069537 | -0.02908 | -0.00027975 | -0.0003053 | 0.18662 | 0.168 | -0.048454 | -0.0099634 | 0.017154 | 0.091553 | 0.14648 | 0.16937 | 0.15564 | 0.064087 | 0.086975 | -0.041199 | 0.1236 | 0.2243 | 0.064087 | 0.059509 | 0.064087 | 0.16022 | 0.086975 | 120.9824 | 120.8542 | -0.11444 | 121.0419 | 121.051 | 0.19684 | -0.086975 | 121.0556 | 120.9824 | -0.11902 | 121.019 | 120.9595 | -0.022888 | -0.11444 | 120.9595 | 120.9869 | 121.0648 | -0.21973 | 120.9549 | 120.9595 | 121.1197 | -0.091553
2733.0625 | 121.312 | -121.0556 | 0.059509 | 0.013046 | 0.0041314 | 0.070867 | 0.032492 | -0.070605 | -0.026517 | 0.0027108 | 0.0073242 | 0.047337 | 0.031494 | -0.047813 | -0.0093226 | 0.014591 | 0.10071 | 0.16022 | 0.15106 | 0.15106 | 0.054932 | 0.07782 | -0.027466 | 0.086975 | 0.1831 | 0.036621 | -0.027466 | -0.009155 | 0.10529 | 0.036621 | 121.1334 | 121.0281 | -0.004577 | 121.2158 | 121.2067 | 0.17853 | 0.041199 | 121.1609 | 121.0922 | -0.086975 | 121.1426 | 121.0922 | 0 | -0.068664 | 121.1105 | 121.1563 | 121.2067 | -0.086975 | 121.0281 | 121.0464 | 121.2387 | -0.022888
2734.7812 | 121.3898 | -121.0831 | 0.059509 | 0.0054168 | 0.0047724 | 0.072149 | 0.02886 | -0.067614 | -0.026517 | 0.00057465 | -0.0003053 | 0.046696 | 0.031494 | -0.04589 | -0.0071862 | 0.015872 | 0.091553 | 0.12817 | 0.15106 | 0.16937 | 0.064087 | 0.086975 | -0.032043 | 0.07782 | 0.16937 | 0.041199 | -0.009155 | -0.004578 | 0.10071 | 0.059509 | 121.17 | 121.051 | 0.004578 | 121.2112 | 121.2524 | 0.20142 | 0.032044 | 121.1838 | 121.1426 | -0.068664 | 121.1609 | 121.1243 | -0.01831 | -0.064087 | 121.1472 | 121.1746 | 121.2341 | -0.091552 | 121.0739 | 121.0785 | 121.2524 | 0
2736.5156 | 121.344 | -121.106 | 0.068665 | 0.0054168 | 0.0030634 | 0.071081 | 0.028433 | -0.0674 | -0.023953 | 0.0014292 | 0.014954 | 0.04755 | 0.030213 | -0.045677 | -0.0059046 | 0.013309 | 0.10529 | 0.17853 | 0.16022 | 0.16022 | 0.064087 | 0.086975 | -0.032043 | 0.10986 | 0.19684 | 0.050354 | -0.013733 | -0.004578 | 0.09613 | 0.036621 | 121.1929 | 121.0739 | -0.004578 | 121.2845 | 121.2662 | 0.19226 | 0.036621 | 121.2021 | 121.1426 | -0.082398 | 121.2158 | 121.1563 | 0.013733 | -0.073243 | 121.17 | 121.2112 | 121.2662 | -0.10071 | 121.0922 | 121.1014 | 121.3028 | -0.032044
2738.25 | 121.3623 | -121.1334 | 0.073242 | 0.020676 | 0.0073358 | 0.07279 | 0.024374 | -0.06975 | -0.027371 | 0.0018564 | -0.0003053 | 0.046482 | 0.029785 | -0.047599 | -0.0065454 | 0.012454 | 0.073242 | 0.091553 | 0.10529 | 0.10529 | 0.068665 | 0.086975 | -0.041199 | 0.041199 | 0.091553 | -0.013733 | 0.009155 | 0 | 0.086975 | 0.032043 | 121.2204 | 121.0922 | -0.004577 | 121.225 | 121.2387 | 0.14649 | 0 | 121.2204 | 121.1655 | -0.064087 | 121.1746 | 121.1197 | -0.045776 | -0.073242 | 121.2021 | 121.2067 | 121.2387 | -0.11444 | 121.1426 | 121.1334 | 121.225 | -0.041199
2740 | 121.2799 | -121.1792 | 0.09613 | 0.013046 | -0.0059088 | 0.069585 | 0.027579 | -0.068682 | -0.019681 | 0.0022836 | 0.014954 | 0.052677 | 0.029999 | -0.044181 | -0.002273 | 0.012241 | 0.068665 | 0.032043 | 0.027466 | 0.091553 | 0.10529 | 0.045776 | -0.059509 | 0.013733 | 0.018311 | -0.11444 | 0.018311 | 0.041199 | 0.082397 | 0.004578 | 121.225 | 121.1197 | 0.009156 | 121.2112 | 121.2708 | 0.15106 | -0.027465 | 121.2616 | 121.1838 | -0.077819 | 121.1929 | 121.0648 | -0.11902 | -0.054931 | 121.2845 | 121.2479 | 121.2067 | -0.15564 | 121.1975 | 121.2204 | 121.1975 | -0.091552
2741.6875 | 121.3211 | -121.1746 | 0.09613 | 0.013046 | 0.00071339 | 0.071722 | 0.031638 | -0.0674 | -0.025876 | 0.00078825 | -0.0003053 | 0.048191 | 0.030854 | -0.046318 | -0.0071862 | 0.014377 | 0.082397 | 0.10529 | 0.14191 | 0.14648 | 0.054932 | 0.064087 | -0.050354 | 0.018311 | 0.10071 | -0.041199 | 0 | 0.018311 | 0.09613 | 0.032043 | 121.2387 | 121.1243 | -0.041198 | 121.2799 | 121.3211 | 0.19684 | -0.013733 | 121.2708 | 121.2067 | -0.09613 | 121.1929 | 121.1334 | -0.073242 | -0.077819 | 121.2296 | 121.257 | 121.3165 | -0.14648 | 121.1746 | 121.1929 | 121.2753 | -0.064087
2743.3906 | 121.3165 | -121.2021 | 0.09613 | 0.013046 | -0.0031318 | 0.071508 | 0.030783 | -0.065478 | -0.023313 | -6.615e-05 | 0.014954 | 0.049259 | 0.031494 | -0.045036 | -0.0086816 | 0.012882 | 0.018311 | 0.027466 | 0.064087 | 0.091553 | 0.07782 | 0.054932 | -0.073242 | -0.018311 | 0.050354 | -0.07782 | 0 | 0.050354 | 0.07782 | -0.004578 | 121.257 | 121.1288 | -0.01831 | 121.2296 | 121.2936 | 0.16479 | -0.077819 | 121.2799 | 121.1975 | -0.09613 | 121.1838 | 121.1243 | -0.073242 | -0.045776 | 121.2799 | 121.2204 | 121.2662 | -0.16937 | 121.2021 | 121.2524 | 121.2524 | -0.10071
2745.0938 | 121.3898 | -121.2021 | 0.10071 | 0.013046 | -0.0027044 | 0.069158 | 0.031851 | -0.067614 | -0.022031 | -0.0011344 | 0.0073242 | 0.051182 | 0.032135 | -0.043113 | -0.005691 | 0.011173 | 0 | 0.004578 | 0.018311 | 0.07782 | 0.10986 | 0.041199 | -0.086975 | -0.018311 | 0.041199 | -0.09613 | 0.013733 | 0.027466 | 0.064087 | 0 | 121.2433 | 121.1151 | 0.009155 | 121.2067 | 121.2799 | 0.16479 | -0.10071 | 121.2662 | 121.2021 | -0.086975 | 121.1838 | 121.106 | -0.09613 | -0.073242 | 121.312 | 121.2021 | 121.2204 | -0.18768 | 121.2158 | 121.2296 | 121.2433 | -0.10071
2746.8125 | 121.4172 | -121.2387 | 0.068665 | 0.013046 | -0.0039862 | 0.06809 | 0.029074 | -0.067828 | -0.022672 | 0.0012154 | 0.014954 | 0.052464 | 0.030426 | -0.04525 | -0.0054772 | 0.01395 | 0.032043 | 0.041199 | 0.068665 | 0.10529 | 0.091553 | 0.059509 | -0.064087 | 0.036621 | 0.086975 | -0.064087 | 0.022888 | 0.032043 | 0.068665 | 0.009155 | 121.2982 | 121.1746 | 0.022888 | 121.2799 | 121.344 | 0.16937 | -0.036622 | 121.3074 | 121.2479 | -0.045777 | 121.2753 | 121.1746 | -0.073242 | -0.036622 | 121.3303 | 121.2708 | 121.3074 | -0.13275 | 121.2616 | 121.2708 | 121.3257 | -0.05951
2748.5156 | 121.4127 | -121.257 | 0.073242 | 0.0054168 | 0.0026362 | 0.072363 | 0.029074 | -0.069537 | -0.02844 | 0.0035654 | 0.0073242 | 0.046482 | 0.031922 | -0.046531 | -0.0074 | 0.015018 | 0.07782 | 0.16022 | 0.16022 | 0.16479 | 0.050354 | 0.07782 | -0.054932 | 0.091553 | 0.1831 | 0.018311 | -0.022888 | 0.009155 | 0.10071 | 0.027466 | 121.3348 | 121.2021 | -0.022888 | 121.4172 | 121.4218 | 0.21973 | 0.004578 | 121.3577 | 121.2845 | -0.09613 | 121.3486 | 121.2753 | -0.009155 | -0.064087 | 121.3074 | 121.3348 | 121.4172 | -0.12817 | 121.2341 | 121.2662 | 121.4401 | -0.045776
2750.2344 | 121.4218 | -121.2296 | 0.073242 | 0.0054168 | -0.0039862 | 0.07044 | 0.02886 | -0.069964 | -0.021176 | 0.00057465 | 0.0073242 | 0.052464 | 0.031281 | -0.044181 | -0.0063318 | 0.015018 | -0.004578 | -0.004578 | 0 | 0.073242 | 0.09613 | 0.032043 | -0.073242 | -0.013733 | 0.045776 | -0.09613 | 0.027466 | 0.032043 | 0.068665 | -0.004578 | 121.2616 | 121.1563 | 0.022888 | 121.225 | 121.3028 | 0.14648 | -0.07782 | 121.2982 | 121.225 | -0.045776 | 121.2158 | 121.1334 | -0.091552 | -0.041199 | 121.3257 | 121.225 | 121.2296 | -0.14648 | 121.257 | 121.2616 | 121.2753 | -0.07782
2751.9844 | 121.4859 | -121.2341 | 0.059509 | 0.013046 | -0.00078181 | 0.064459 | 0.025656 | -0.068682 | -0.021604 | 0.0016428 | 0.014954 | 0.052037 | 0.033631 | -0.043113 | -0.0048364 | 0.014377 | -0.004578 | -0.022888 | -0.009155 | 0.064087 | 0.11902 | 0.054932 | -0.068665 | -0.027466 | 0 | -0.10071 | 0.013733 | 0.032043 | 0.068665 | -0.004578 | 121.2891 | 121.1655 | 0.05951 | 121.2112 | 121.2982 | 0.13275 | -0.064087 | 121.3028 | 121.2296 | -0.045776 | 121.2067 | 121.1334 | -0.09613 | -0.027466 | 121.3531 | 121.2296 | 121.225 | -0.12817 | 121.2479 | 121.2662 | 121.2341 | -0.064087
2753.6875 | 121.4539 | -121.2708 | 0.09613 | 0.020676 | -0.0061224 | 0.073644 | 0.030783 | -0.068682 | -0.026303 | 0.0018564 | 0.0073242 | 0.05225 | 0.034912 | -0.044822 | -0.0063318 | 0.015445 | -0.027466 | 0.009155 | 0.018311 | 0.064087 | 0.10986 | 0.027466 | -0.07782 | -0.050354 | 0.036621 | -0.086975 | 0.032043 | 0.027466 | 0.050354 | 0 | 121.2982 | 121.1929 | 0.013733 | 121.2799 | 121.3348 | 0.14191 | -0.1236 | 121.3211 | 121.2708 | -0.064087 | 121.2204 | 121.1838 | -0.086975 | -0.068664 | 121.3806 | 121.2433 | 121.2891 | -0.17395 | 121.3028 | 121.2982 | 121.3074 | -0.09613
2755.3906 | 121.4584 | -121.3028 | 0.086975 | -0.0022127 | -0.0048406 | 0.071722 | 0.032278 | -0.067828 | -0.025022 | 0.0010018 | -0.0003053 | 0.050541 | 0.03299 | -0.043541 | -0.0074 | 0.014377 | -0.027466 | 0.009155 | 0.009155 | 0.073242 | 0.10529 | 0.050354 | -0.09613 | -0.036621 | 0.041199 | -0.10071 | 0.032043 | 0.032043 | 0.064087 | 0.004578 | 121.3531 | 121.2067 | 0.018311 | 121.312 | 121.376 | 0.16937 | -0.11444 | 121.3669 | 121.3074 | -0.054932 | 121.2662 | 121.2021 | -0.10529 | -0.054932 | 121.4081 | 121.2753 | 121.312 | -0.1831 | 121.3348 | 121.3348 | 121.344 | -0.082397
2757.125 | 121.4584 | -121.3211 | 0.086975 | 0.0054168 | -0.0022772 | 0.071722 | 0.03121 | -0.066973 | -0.027585 | -6.615e-05 | 0.014954 | 0.04691 | 0.034272 | -0.043541 | -0.0071862 | 0.015018 | 0.059509 | 0.11902 | 0.11444 | 0.14648 | 0.068665 | 0.059509 | -0.073242 | 0.018311 | 0.10071 | -0.050354 | 0.013733 | 0.022888 | 0.07782 | 0.013733 | 121.3806 | 121.2479 | -0.01831 | 121.4401 | 121.4676 | 0.21973 | -0.027466 | 121.3989 | 121.3348 | -0.073242 | 121.3394 | 121.2708 | -0.064087 | -0.064087 | 121.3898 | 121.3806 | 121.4355 | -0.16022 | 121.3348 | 121.344 | 121.4218 | -0.073242
2758.875 | 121.4401 | -121.3577 | 0.082397 | 0.0054168 | -0.00185 | 0.073431 | 0.029929 | -0.069109 | -0.026944 | -0.00027975 | 0.022583 | 0.048832 | 0.03299 | -0.044822 | -0.010177 | 0.014804 | 0.009155 | 0.059509 | 0.059509 | 0.10529 | 0.082397 | 0.059509 | -0.059509 | -0.032043 | 0.059509 | -0.082397 | 0.022888 | 0.022888 | 0.086975 | 0 | 121.4172 | 121.2982 | 0 | 121.4172 | 121.463 | 0.16479 | -0.073242 | 121.4447 | 121.3577 | -0.059509 | 121.3257 | 121.2753 | -0.082397 | -0.059509 | 121.4401 | 121.3669 | 121.4172 | -0.14191 | 121.3806 | 121.3806 | 121.4172 | -0.082397
2760.5781 | 121.5271 | -121.3394 | 0.064087 | 0.0054168 | -0.00078181 | 0.069158 | 0.028006 | -0.070605 | -0.020749 | 0.0016428 | 0.0073242 | 0.050968 | 0.033203 | -0.041832 | -0.0054772 | 0.013095 | 0.013733 | 0.009155 | 0.018311 | 0.10529 | 0.091553 | 0.045776 | -0.064087 | 0.009155 | 0.073242 | -0.064087 | 0.018311 | 0.032043 | 0.073242 | -0.004578 | 121.3852 | 121.2753 | 0.027466 | 121.3486 | 121.4447 | 0.16937 | -0.050354 | 121.4127 | 121.3348 | -0.045776 | 121.3486 | 121.2753 | -0.059509 | -0.032044 | 121.431 | 121.3531 | 121.3577 | -0.12817 | 121.3577 | 121.3715 | 121.4127 | -0.068665
2762.2812 | 121.55 | -121.3394 | 0.068665 | 0.013046 | -0.00099541 | 0.068304 | 0.026083 | -0.064196 | -0.023953 | 0.00057465 | -0.0003053 | 0.051823 | 0.033203 | -0.041618 | -0.003982 | 0.013309 | -0.022888 | -0.018311 | 0 | 0.059509 | 0.10071 | 0.045776 | -0.073242 | -0.013733 | -0.004578 | -0.11902 | 0.032043 | 0.032043 | 0.068665 | 0.009155 | 121.3852 | 121.2662 | 0.032043 | 121.3211 | 121.3989 | 0.13275 | -0.091553 | 121.4081 | 121.3486 | -0.036622 | 121.3257 | 121.2204 | -0.12817 | -0.036622 | 121.4401 | 121.3165 | 121.3394 | -0.14191 | 121.3715 | 121.3715 | 121.3348 | -0.05951
2764.0156 | 121.5729 | -121.3303 | 0.07782 | 0.0054168 | 0.0058404 | 0.07279 | 0.02886 | -0.067828 | -0.028012 | -6.615e-05 | 0.014954 | 0.050968 | 0.029785 | -0.047599 | -0.0091088 | 0.017154 | 0.054932 | 0.10529 | 0.12817 | 0.11902 | 0.050354 | 0.09613 | -0.054932 | 0.022888 | 0.11444 | 0 | -0.027466 | 0.004578 | 0.10529 | 0.036621 | 121.4264 | 121.2753 | -0.027466 | 121.4355 | 121.4493 | 0.17395 | -0.022888 | 121.4355 | 121.3669 | -0.10529 | 121.3531 | 121.3303 | -0.036621 | -0.073242 | 121.3806 | 121.3852 | 121.4584 | -0.13275 | 121.3028 | 121.3348 | 121.4447 | -0.041199
2765.75 | 121.6324 | -121.3486 | 0.045776 | 0.013046 | 0.0013544 | 0.069158 | 0.025229 | -0.068896 | -0.023526 | 0.0010018 | 0.0073242 | 0.05225 | 0.027222 | -0.04525 | -0.0048364 | 0.014377 | 0.032043 | 0.036621 | 0.041199 | 0.10071 | 0.082397 | 0.068665 | -0.054932 | 0.036621 | 0.07782 | -0.027466 | -0.004578 | 0.013733 | 0.091553 | 0.036621 | 121.4172 | 121.2936 | 0.036621 | 121.3852 | 121.4493 | 0.15564 | -0.013733 | 121.4401 | 121.3852 | -0.050354 | 121.3852 | 121.3211 | -0.064087 | -0.032043 | 121.431 | 121.3806 | 121.3898 | -0.10071 | 121.344 | 121.3623 | 121.4264 | -0.009155
2767.4531 | 121.5317 | -121.3898 | 0.073242 | 0.0054168 | -0.00185 | 0.069799 | 0.027152 | -0.070177 | -0.022031 | 0.00036105 | 0.0073242 | 0.052464 | 0.029358 | -0.045677 | -0.0031274 | 0.014804 | 0.013733 | -0.036621 | -0.004578 | 0.073242 | 0.10529 | 0.045776 | -0.07782 | -0.041199 | -0.022888 | -0.13733 | 0.018311 | 0.050354 | 0.068665 | 0.004578 | 121.4355 | 121.312 | 0.032044 | 121.3531 | 121.463 | 0.15106 | -0.059509 | 121.4584 | 121.3943 | -0.054931 | 121.3486 | 121.2524 | -0.14191 | -0.022888 | 121.4951 | 121.4035 | 121.3852 | -0.15106 | 121.4081 | 121.4401 | 121.3669 | -0.068664
2769.1562 | 121.5546 | -121.3943 | 0.086975 | 0.013046 | -0.0061224 | 0.070654 | 0.026938 | -0.068255 | -0.02139 | 0.0014292 | 0.0073242 | 0.051182 | 0.032135 | -0.045463 | -0.001632 | 0.013736 | 0.054932 | 0.036621 | 0.054932 | 0.11902 | 0.10071 | 0.059509 | -0.086975 | 0.013733 | 0.09613 | -0.045776 | 0.004578 | 0.022888 | 0.07782 | 0.004578 | 121.4539 | 121.3074 | 0.013733 | 121.431 | 121.5134 | 0.20599 | -0.032043 | 121.4722 | 121.3989 | -0.082397 | 121.4081 | 121.3486 | -0.050354 | -0.064087 | 121.4951 | 121.4493 | 121.4493 | -0.17395 | 121.3989 | 121.4172 | 121.4905 | -0.082397
2770.9219 | 121.6232 | -121.3806 | 0.059509 | 0.013046 | 0.0045588 | 0.070654 | 0.02587 | -0.067828 | -0.026517 | -0.00027975 | 0.014954 | 0.047764 | 0.030213 | -0.045463 | -0.0074 | 0.016727 | 0.091553 | 0.1236 | 0.15564 | 0.14191 | 0.041199 | 0.073242 | -0.032043 | 0.050354 | 0.11902 | 0.018311 | -0.032043 | 0.009155 | 0.10071 | 0.036621 | 121.4539 | 121.3486 | -0.01831 | 121.5042 | 121.5225 | 0.17395 | 0.032044 | 121.4813 | 121.4172 | -0.091552 | 121.431 | 121.3989 | -0.01831 | -0.050354 | 121.4218 | 121.4722 | 121.5363 | -0.091552 | 121.3486 | 121.3898 | 121.4996 | -0.022888
2772.6562 | 121.6278 | -121.3989 | 0.082397 | 0.020676 | 0.0051996 | 0.073858 | 0.029074 | -0.070605 | -0.030576 | -0.001348 | 0.0073242 | 0.045414 | 0.028504 | -0.04525 | -0.0061182 | 0.015445 | 0.059509 | 0.059509 | 0.10529 | 0.11902 | 0.073242 | 0.082397 | -0.045776 | 0.013733 | 0.091553 | -0.018311 | -0.036621 | 0.009155 | 0.086975 | 0.045776 | 121.4813 | 121.3531 | -0.009155 | 121.4584 | 121.5179 | 0.16479 | -0.022888 | 121.4859 | 121.4447 | -0.11902 | 121.4127 | 121.3806 | -0.064087 | -0.073242 | 121.4722 | 121.4584 | 121.5042 | -0.12817 | 121.3623 | 121.4081 | 121.4905 | -0.036621
2774.3594 | 121.6782 | -121.4172 | 0.068665 | 0.0054168 | 0.0047724 | 0.073003 | 0.030569 | -0.068468 | -0.029935 | -0.001348 | -0.0003053 | 0.048405 | 0.031708 | -0.04589 | -0.0095362 | 0.013522 | 0.11902 | 0.12817 | 0.15106 | 0.14191 | 0.073242 | 0.091553 | -0.054932 | 0.073242 | 0.16937 | 0.050354 | -0.022888 | 0.013733 | 0.10986 | 0.045776 | 121.5088 | 121.3623 | 0.004577 | 121.5454 | 121.5591 | 0.19684 | 0.050354 | 121.5271 | 121.463 | -0.091553 | 121.4905 | 121.4676 | 0.004578 | -0.054932 | 121.4905 | 121.5363 | 121.5683 | -0.1236 | 121.3943 | 121.431 | 121.5866 | -0.022889
2776.0781 | 121.6553 | -121.4264 | 0.073242 | 0.0054168 | 0.0047724 | 0.071081 | 0.024374 | -0.0674 | -0.026303 | -0.00070715 | 0.014954 | 0.050114 | 0.031922 | -0.046104 | -0.0048364 | 0.014377 | 0.12817 | 0.086975 | 0.14648 | 0.13275 | 0.064087 | 0.10529 | -0.013733 | 0.068665 | 0.11444 | 0 | -0.027466 | 0.022888 | 0.11902 | 0.036621 | 121.5317 | 121.4127 | -0.009155 | 121.5134 | 121.5591 | 0.14648 | 0.054932 | 121.5454 | 121.463 | -0.10071 | 121.4951 | 121.4264 | -0.036621 | -0.050354 | 121.4905 | 121.5546 | 121.5729 | -0.086975 | 121.3989 | 121.4493 | 121.5408 | -0.036621
2777.7812 | 121.5683 | -121.4264 | 0.09613 | 0.0054168 | -0.0039862 | 0.068945 | 0.026511 | -0.067828 | -0.017331 | -0.00027975 | 0.0073242 | 0.053105 | 0.031281 | -0.04525 | -0.0018458 | 0.0116 | 0.11444 | 0.054932 | 0.073242 | 0.10071 | 0.091553 | 0.068665 | -0.091553 | 0.032043 | 0.059509 | -0.086975 | 0.009155 | 0.027466 | 0.068665 | 0.009155 | 121.4951 | 121.3348 | -0.004577 | 121.4813 | 121.5271 | 0.19226 | 0.018311 | 121.4951 | 121.4355 | -0.086975 | 121.4584 | 121.3394 | -0.09613 | -0.068664 | 121.5179 | 121.5408 | 121.4996 | -0.18768 | 121.4355 | 121.4539 | 121.4859 | -0.086975
2779.5 | 121.669 | -121.4081 | 0.064087 | 0.0054168 | 0.004345 | 0.068731 | 0.026297 | -0.066546 | -0.02609 | 0.0014292 | 0.014954 | 0.049473 | 0.031067 | -0.046531 | -0.0069726 | 0.017154 | 0.12817 | 0.11444 | 0.16022 | 0.13733 | 0.041199 | 0.10529 | -0.041199 | 0.091553 | 0.14191 | 0.027466 | -0.027466 | 0 | 0.07782 | 0.050354 | 121.5134 | 121.3669 | -0.022888 | 121.5225 | 121.5454 | 0.17853 | 0.064087 | 121.4859 | 121.4584 | -0.091553 | 121.4996 | 121.4355 | -0.022888 | -0.064087 | 121.4493 | 121.5363 | 121.5683 | -0.10529 | 121.3806 | 121.4081 | 121.55 | -0.013733
2781.2188 | 121.3211 | -121.0602 | 0.054932 | 0.0054168 | 0.0051996 | 0.069372 | 0.030783 | -0.068255 | -0.028226 | 0.00014745 | -0.0003053 | 0.045628 | 0.030426 | -0.045677 | -0.0074 | 0.015231 | 0.045776 | 0.041199 | 0.10529 | 0.11902 | 0.054932 | 0.091553 | -0.045776 | 0.027466 | 0.082397 | -0.009155 | -0.022888 | 0.022888 | 0.086975 | 0.018311 | 121.1517 | 121.0144 | 0 | 121.1014 | 121.1792 | 0.16479 | -0.009156 | 121.1472 | 121.0785 | -0.07782 | 121.0876 | 121.051 | -0.027466 | -0.032044 | 121.1151 | 121.106 | 121.1655 | -0.10071 | 121.0373 | 121.0831 | 121.1426 | -0.036621
2782.9844 | 121.4172 | -121.2112 | 0.068665 | 0.0054168 | -0.0037726 | 0.070226 | 0.027579 | -0.06975 | -0.02139 | -0.00027975 | -0.0003053 | 0.050541 | 0.031708 | -0.044395 | -0.0046228 | 0.011173 | 0.07782 | 0.022888 | 0.068665 | 0.10529 | 0.10071 | 0.064087 | -0.064087 | 0.041199 | 0.07782 | -0.068665 | 0.004578 | 0.032043 | 0.068665 | 0.009155 | 121.2753 | 121.1472 | 0.032043 | 121.2341 | 121.3165 | 0.16937 | 0.009155 | 121.2799 | 121.2204 | -0.064087 | 121.2524 | 121.1426 | -0.07782 | -0.036622 | 121.312 | 121.2891 | 121.2799 | -0.13275 | 121.2158 | 121.2433 | 121.2891 | -0.05951
2784.6875 | 121.4035 | -121.3165 | 0.07782 | 0.020676 | -0.0041998 | 0.065954 | 0.029288 | -0.068896 | -0.020749 | 0.0029244 | 0.014954 | 0.050328 | 0.031067 | -0.043968 | -0.0052636 | 0.012027 | 0.086975 | 0.059509 | 0.068665 | 0.10986 | 0.086975 | 0.054932 | -0.041199 | 0.018311 | 0.068665 | -0.073242 | 0.004578 | 0.045776 | 0.082397 | 0.013733 | 121.3715 | 121.2753 | 0.009155 | 121.376 | 121.4264 | 0.15106 | 0.009155 | 121.3989 | 121.3303 | -0.073242 | 121.3348 | 121.2433 | -0.086975 | -0.032044 | 121.4035 | 121.4035 | 121.3852 | -0.11902 | 121.3211 | 121.3623 | 121.3852 | -0.064087
2786.3906 | 121.5866 | -121.2982 | 0.041199 | 0.0054168 | 0.004986 | 0.07044 | 0.029929 | -0.066973 | -0.029935 | -0.001348 | 0.030213 | 0.043492 | 0.031067 | -0.044609 | -0.0061182 | 0.01694 | 0.013733 | 0.059509 | 0.10529 | 0.10986 | 0.091553 | 0.086975 | -0.041199 | 0.041199 | 0.10529 | 0.004578 | 0 | 0.013733 | 0.091553 | 0.022888 | 121.3852 | 121.257 | 0.050354 | 121.3577 | 121.4081 | 0.15106 | -0.027466 | 121.3898 | 121.3211 | -0.041199 | 121.3394 | 121.3028 | -0.01831 | -0.027466 | 121.3898 | 121.312 | 121.4035 | -0.082398 | 121.2982 | 121.312 | 121.4035 | -0.018311
2788.1094 | 121.2982 | -121.0373 | 0.059509 | 0.0054168 | 0.0026362 | 0.073003 | 0.027365 | -0.068041 | -0.02844 | -0.0015616 | 0.014954 | 0.046269 | 0.030426 | -0.04525 | -0.0099634 | 0.015231 | 0.11444 | 0.16022 | 0.16937 | 0.16937 | 0.059509 | 0.091553 | -0.064087 | 0.07782 | 0.1831 | 0.050354 | -0.018311 | 0.004578 | 0.10071 | 0.036621 | 121.1288 | 120.9732 | 0 | 121.1975 | 121.2067 | 0.23346 | 0.054932 | 121.138 | 121.0739 | -0.07782 | 121.1151 | 121.0876 | 0.013733 | -0.054931 | 121.0968 | 121.1517 | 121.2067 | -0.1236 | 121.019 | 121.0419 | 121.2204 | -0.022888
2789.8125 | 121.4127 | -121.17 | 0.054932 | 0.013046 | 0.0041314 | 0.071935 | 0.023306 | -0.06975 | -0.025022 | 0.00057465 | 0.0073242 | 0.04691 | 0.026581 | -0.04824 | -0.0046228 | 0.014591 | 0.11902 | 0.11902 | 0.15106 | 0.16022 | 0.045776 | 0.10071 | -0.027466 | 0.10986 | 0.13733 | 0.013733 | -0.013733 | -0.004578 | 0.10529 | 0.050354 | 121.2708 | 121.1426 | -0.009156 | 121.2891 | 121.3303 | 0.18768 | 0.064087 | 121.2753 | 121.2204 | -0.068665 | 121.2799 | 121.1838 | -0.036621 | -0.05951 | 121.2158 | 121.2891 | 121.3211 | -0.082398 | 121.1563 | 121.1655 | 121.3074 | -0.004578
2791.5156 | 121.4035 | -121.2662 | 0.07782 | 0.0054168 | -0.004627 | 0.067663 | 0.029074 | -0.067187 | -0.022672 | 0.0010018 | 0.014954 | 0.0499 | 0.031067 | -0.043541 | -0.0061182 | 0.012882 | 0.004578 | -0.018311 | 0.009155 | 0.07782 | 0.10529 | 0.068665 | -0.082397 | -0.050354 | 0.009155 | -0.11902 | 0.018311 | 0.032043 | 0.041199 | 0 | 121.3348 | 121.1838 | 0.027466 | 121.2479 | 121.344 | 0.16022 | -0.073242 | 121.3074 | 121.2662 | -0.059509 | 121.2158 | 121.1472 | -0.11902 | -0.045777 | 121.3715 | 121.2708 | 121.2753 | -0.16022 | 121.2845 | 121.2982 | 121.2753 | -0.07782
2793.2188 | 121.4172 | -121.2845 | 0.10529 | -0.0022127 | -0.0039862 | 0.070226 | 0.030997 | -0.068682 | -0.024594 | -0.00070715 | 0.014954 | 0.04755 | 0.029358 | -0.045036 | -0.008468 | 0.013522 | 0.004578 | 0.013733 | 0.045776 | 0.064087 | 0.091553 | 0.041199 | -0.091553 | -0.036621 | 0.032043 | -0.10529 | 0.041199 | 0.050354 | 0.045776 | -0.009155 | 121.3257 | 121.1929 | -0.013733 | 121.2982 | 121.3486 | 0.15564 | -0.10071 | 121.3303 | 121.2753 | -0.064087 | 121.2479 | 121.1792 | -0.096131 | -0.054932 | 121.376 | 121.2891 | 121.3303 | -0.19684 | 121.3257 | 121.3348 | 121.3165 | -0.11444
2794.9844 | 121.55 | -121.2891 | 0.041199 | 0.0054168 | 0.006054 | 0.070013 | 0.024374 | -0.067614 | -0.023526 | -0.00027975 | 0.014954 | 0.047337 | 0.025299 | -0.043968 | -0.003982 | 0.015231 | 0.1236 | 0.13733 | 0.14191 | 0.15106 | 0.054932 | 0.082397 | -0.032043 | 0.10986 | 0.12817 | 0.027466 | -0.036621 | -0.004578 | 0.10986 | 0.050354 | 121.3715 | 121.257 | 0.013733 | 121.4264 | 121.4401 | 0.18311 | 0.082397 | 121.3989 | 121.3394 | -0.07782 | 121.3989 | 121.3165 | -0.022888 | -0.045777 | 121.344 | 121.4127 | 121.431 | -0.073242 | 121.2524 | 121.2845 | 121.4172 | 0.009155
2796.7188 | 121.5637 | -121.3074 | 0.045776 | 0.013046 | 0.0045588 | 0.069158 | 0.022452 | -0.069109 | -0.021817 | 0.00207 | 0.014954 | 0.048405 | 0.028076 | -0.046318 | -0.0035546 | 0.013736 | 0.11902 | 0.11902 | 0.14191 | 0.16937 | 0.041199 | 0.086975 | -0.004578 | 0.10529 | 0.13275 | 0.013733 | -0.032043 | -0.004578 | 0.11444 | 0.041199 | 121.3943 | 121.3028 | -0.004577 | 121.4264 | 121.4767 | 0.17395 | 0.073243 | 121.4218 | 121.3486 | -0.077819 | 121.4127 | 121.3211 | -0.027466 | -0.050354 | 121.3486 | 121.4264 | 121.4493 | -0.050354 | 121.2753 | 121.3028 | 121.4401 | -0.004577
2798.4375 | 121.5271 | -121.344 | 0.068665 | 0.013046 | -0.00056821 | 0.067876 | 0.025443 | -0.069109 | -0.022672 | 0.00014745 | 0.0073242 | 0.049687 | 0.028076 | -0.046104 | -0.0027002 | 0.015018 | 0.004578 | -0.036621 | 0.009155 | 0.073242 | 0.10071 | 0.036621 | -0.073242 | -0.022888 | -0.018311 | -0.1236 | 0.022888 | 0.027466 | 0.059509 | -0.009155 | 121.3806 | 121.2708 | 0.032043 | 121.3074 | 121.4172 | 0.14648 | -0.064087 | 121.4035 | 121.3348 | -0.045777 | 121.3211 | 121.2204 | -0.11444 | -0.041199 | 121.4447 | 121.3486 | 121.3531 | -0.14191 | 121.3669 | 121.3715 | 121.3257 | -0.07782
2800.1406 | 121.5042 | -121.3531 | 0.073242 | 0.0054168 | -0.0020636 | 0.065527 | 0.027152 | -0.066546 | -0.020749 | 0.0033518 | 0.014954 | 0.050114 | 0.027863 | -0.04525 | -0.003982 | 0.015445 | -0.009155 | -0.050354 | -0.013733 | 0.068665 | 0.086975 | 0.041199 | -0.068665 | -0.018311 | -0.004578 | -0.13275 | 0.032043 | 0.045776 | 0.068665 | 0.009155 | 121.3943 | 121.2845 | 0.013733 | 121.3028 | 121.4218 | 0.13733 | -0.082397 | 121.4218 | 121.3623 | -0.041199 | 121.3348 | 121.2204 | -0.14191 | -0.027466 | 121.4401 | 121.344 | 121.3394 | -0.14191 | 121.3852 | 121.3989 | 121.3486 | -0.064087
2801.9062 | 121.5729 | -121.3577 | 0.045776 | 0.013046 | -0.003559 | 0.068304 | 0.026724 | -0.070391 | -0.023099 | 0.00057465 | 0.014954 | 0.049687 | 0.027649 | -0.043968 | -0.0054772 | 0.014591 | -0.004578 | -0.027466 | 0.018311 | 0.07782 | 0.09613 | 0.07782 | -0.082397 | -0.027466 | -0.009155 | -0.11902 | 0.022888 | 0.045776 | 0.064087 | -0.004578 | 121.4355 | 121.2753 | 0.050354 | 121.3303 | 121.4355 | 0.16022 | -0.050354 | 121.4218 | 121.3531 | -0.022888 | 121.3303 | 121.2387 | -0.11444 | 0 | 121.4539 | 121.3531 | 121.376 | -0.12817 | 121.3806 | 121.4035 | 121.3486 | -0.050354
2803.6094 | 121.5408 | -121.4172 | 0.073242 | 0.0054168 | -0.0031318 | 0.068731 | 0.026724 | -0.069323 | -0.021817 | 0.0018564 | -0.0003053 | 0.049473 | 0.030854 | -0.043968 | -0.0044092 | 0.015231 | -0.009155 | -0.013733 | 0.013733 | 0.068665 | 0.091553 | 0.064087 | -0.073242 | -0.032043 | 0.009155 | -0.13733 | 0.027466 | 0.036621 | 0.068665 | -0.004578 | 121.4813 | 121.344 | 0.018311 | 121.4035 | 121.4859 | 0.14191 | -0.082397 | 121.4859 | 121.4127 | -0.045776 | 121.3852 | 121.2799 | -0.13275 | -0.036621 | 121.5088 | 121.4081 | 121.431 | -0.14648 | 121.4447 | 121.4539 | 121.4264 | -0.07782
2805.3125 | 121.6553 | -121.3806 | 0.050354 | 0.0054168 | 0.0075494 | 0.072363 | 0.029929 | -0.070605 | -0.029508 | -0.00092075 | 0.014954 | 0.046696 | 0.03064 | -0.044181 | -0.0091088 | 0.016086 | 0.027466 | 0.050354 | 0.10529 | 0.11902 | 0.068665 | 0.068665 | -0.050354 | 0.009155 | 0.086975 | -0.022888 | -0.009155 | 0.022888 | 0.10529 | 0.027466 | 121.4493 | 121.3303 | 0.018311 | 121.431 | 121.4996 | 0.16937 | -0.022888 | 121.4859 | 121.4081 | -0.059509 | 121.3898 | 121.3577 | -0.050354 | -0.027466 | 121.4493 | 121.4081 | 121.4859 | -0.10071 | 121.3715 | 121.4035 | 121.4676 | -0.022888
2807.0156 | 120.7077 | -120.314 | 0.15564 | -0.0022127 | 0.0051996 | 0.073644 | 0.029501 | -0.066546 | -0.030362 | 0.00057465 | 0.0073242 | 0.21268 | 0.19257 | -0.046745 | -0.010177 | 0.01694 | 0.086975 | 0.11902 | 0.15564 | 0.15106 | 0.059509 | 0.086975 | -0.032043 | 0.11902 | 0.20599 | 0.07782 | 0.07782 | 0.07782 | 0.14648 | 0.09613 | 120.401 | 120.282 | -0.096131 | 120.433 | 120.4651 | 0.18311 | -0.068665 | 120.4605 | 120.4102 | -0.07782 | 120.433 | 120.3918 | -0.01831 | -0.07782 | 120.3735 | 120.401 | 120.4697 | -0.18768 | 120.3918 | 120.3918 | 120.52 | -0.05951
2808.7188 | 120.9457 | -120.6665 | 0.064087 | 0.013046 | 0.0071222 | 0.072576 | 0.02886 | -0.069323 | -0.027585 | -0.00092075 | 0.0073242 | 0.045628 | 0.030213 | -0.046318 | -0.0054772 | 0.013522 | 0.036621 | 0.064087 | 0.10071 | 0.10986 | 0.059509 | 0.064087 | -0.027466 | 0.009155 | 0.068665 | -0.013733 | 0 | 0.022888 | 0.09613 | 0.036621 | 120.7306 | 120.639 | -0.004578 | 120.7306 | 120.7764 | 0.13733 | -0.027466 | 120.7626 | 120.7031 | -0.064087 | 120.6757 | 120.6528 | -0.050354 | -0.041199 | 120.726 | 120.7031 | 120.7672 | -0.091553 | 120.6665 | 120.6894 | 120.7352 | -0.027466
2810.4219 | 121.0602 | -120.7947 | 0.045776 | 0.0054168 | 0.0037042 | 0.06809 | 0.023306 | -0.068896 | -0.02374 | 0.0010018 | 0.0073242 | 0.049687 | 0.029145 | -0.046104 | -0.0041956 | 0.014163 | 0.1236 | 0.10986 | 0.14191 | 0.15106 | 0.064087 | 0.086975 | -0.032043 | 0.10529 | 0.11444 | 0.022888 | -0.009155 | -0.018311 | 0.10529 | 0.064087 | 120.8817 | 120.7626 | 0.018311 | 120.9045 | 120.9457 | 0.18311 | 0.07782 | 120.9 | 120.8588 | -0.054931 | 120.9 | 120.8176 | -0.041199 | -0.064087 | 120.8588 | 120.9183 | 120.9366 | -0.077819 | 120.7855 | 120.7764 | 120.9091 | 0.018311
2812.1406 | 121.138 | -120.8588 | 0.050354 | 0.0054168 | 0.0024224 | 0.067236 | 0.025229 | -0.068255 | -0.021817 | 0.0014292 | 0.0073242 | 0.050968 | 0.028717 | -0.043541 | -0.0035546 | 0.013736 | 0.054932 | 0.004578 | 0.054932 | 0.082397 | 0.09613 | 0.064087 | -0.064087 | 0.036621 | 0.054932 | -0.032043 | 0.009155 | 0.018311 | 0.082397 | 0.036621 | 120.9229 | 120.7947 | 0.045776 | 120.8633 | 120.9412 | 0.14648 | 0.004578 | 120.9412 | 120.8954 | -0.041199 | 120.8954 | 120.8267 | -0.068664 | -0.032043 | 120.9549 | 120.9137 | 120.9137 | -0.11444 | 120.8679 | 120.8771 | 120.9137 | -0.013733
2813.9062 | 121.1929 | -120.9045 | 0.050354 | 0.0054168 | 0.0041314 | 0.069585 | 0.027579 | -0.06975 | -0.023526 | -0.00027975 | 0.0073242 | 0.045841 | 0.026795 | -0.04525 | -0.0027002 | 0.014163 | 0.11444 | 0.086975 | 0.12817 | 0.16022 | 0.068665 | 0.086975 | -0.032043 | 0.10071 | 0.11902 | 0.013733 | -0.022888 | -0.004578 | 0.10071 | 0.064087 | 120.9915 | 120.8725 | 0.018311 | 120.9915 | 121.0648 | 0.19226 | 0.064087 | 121.0052 | 120.9686 | -0.073242 | 121.0052 | 120.9183 | -0.050354 | -0.054932 | 120.9732 | 121.019 | 121.0327 | -0.082397 | 120.8817 | 120.9 | 121.0236 | 0.013733
2815.625 | 121.1884 | -120.9503 | 0.045776 | -0.0098417 | 0.0051996 | 0.07044 | 0.025015 | -0.068255 | -0.025876 | 0.0014292 | 0.014954 | 0.046482 | 0.027008 | -0.045463 | -0.0054772 | 0.014163 | 0.1236 | 0.10986 | 0.15564 | 0.15564 | 0.045776 | 0.082397 | -0.027466 | 0.10529 | 0.14191 | 0.018311 | -0.022888 | -0.013733 | 0.10986 | 0.054932 | 121.0327 | 120.9229 | 0 | 121.0602 | 121.106 | 0.18311 | 0.07782 | 121.0602 | 121.0052 | -0.068664 | 121.0556 | 120.9686 | -0.036621 | -0.059509 | 120.9961 | 121.0739 | 121.106 | -0.073242 | 120.9274 | 120.9366 | 121.0922 | 0.009156
2817.3438 | 121.1517 | -121.0052 | 0.073242 | 0.013046 | -0.0044134 | 0.069585 | 0.026938 | -0.067828 | -0.020108 | 0.0010018 | 0.0073242 | 0.047764 | 0.030426 | -0.044609 | -0.0037684 | 0.012241 | 0.073242 | 0.036621 | 0.068665 | 0.11444 | 0.10986 | 0.059509 | -0.07782 | 0.050354 | 0.082397 | -0.054932 | 0.018311 | 0.027466 | 0.07782 | 0 | 121.0648 | 120.9274 | 0.036621 | 121.0419 | 121.1197 | 0.19226 | 0 | 121.0831 | 121.0052 | -0.054931 | 121.0556 | 120.9503 | -0.054932 | -0.045776 | 121.1151 | 121.0785 | 121.0739 | -0.15106 | 121.0236 | 121.0327 | 121.0876 | -0.073242
2819.0781 | 121.2524 | -121.019 | 0.050354 | 0.028305 | 0.0051996 | 0.066595 | 0.021597 | -0.068896 | -0.024167 | 0.0024972 | -0.0003053 | 0.04755 | 0.026581 | -0.044822 | -0.0059046 | 0.015872 | 0.11444 | 0.12817 | 0.16022 | 0.16022 | 0.045776 | 0.086975 | -0.032043 | 0.086975 | 0.15564 | 0.022888 | -0.032043 | -0.004578 | 0.10529 | 0.068665 | 121.106 | 120.9869 | -0.004578 | 121.1472 | 121.1792 | 0.19226 | 0.064087 | 121.1243 | 121.0876 | -0.082397 | 121.106 | 121.0419 | -0.045777 | -0.054932 | 121.0648 | 121.1334 | 121.1792 | -0.082397 | 120.9869 | 121.0144 | 121.1746 | 0.018311
2820.7812 | 121.2982 | -121.0098 | 0.032043 | 0.020676 | 0.0034906 | 0.066381 | 0.023306 | -0.066759 | -0.024167 | 0.0022836 | 0.014954 | 0.046696 | 0.029572 | -0.045677 | -0.0061182 | 0.013095 | 0.12817 | 0.10986 | 0.14191 | 0.15564 | 0.059509 | 0.10071 | -0.013733 | 0.10071 | 0.13275 | 0.018311 | -0.027466 | 0 | 0.11902 | 0.050354 | 121.1105 | 120.9961 | 0.027466 | 121.1197 | 121.1655 | 0.16937 | 0.096131 | 121.1288 | 121.0602 | -0.059509 | 121.1105 | 121.0281 | -0.032043 | -0.032043 | 121.0693 | 121.138 | 121.1517 | -0.045776 | 120.9824 | 121.0098 | 121.1426 | 0.018311
2822.4844 | 121.3303 | -121.0327 | 0.054932 | 0.013046 | 0.0058404 | 0.073431 | 0.028006 | -0.068682 | -0.030362 | 0.00036105 | 0.0073242 | 0.050328 | 0.031708 | -0.046531 | -0.0080408 | 0.015445 | 0.086975 | 0.11444 | 0.14648 | 0.14191 | 0.064087 | 0.086975 | -0.054932 | 0.068665 | 0.14191 | 0.027466 | -0.009155 | 0.013733 | 0.09613 | 0.041199 | 121.1197 | 120.9778 | 0.009155 | 121.1472 | 121.1746 | 0.19684 | 0.032043 | 121.1288 | 121.0739 | -0.064087 | 121.1014 | 121.0602 | -0.013733 | -0.041199 | 121.0968 | 121.1197 | 121.1792 | -0.10986 | 121.0236 | 121.0464 | 121.1746 | -0.013733
2824.1875 | 121.3165 | -121.0968 | 0.054932 | 0.0054168 | 0.004345 | 0.073431 | 0.026938 | -0.066973 | -0.028226 | 0.0014292 | 0.014954 | 0.04691 | 0.026795 | -0.04589 | -0.0054772 | 0.014591 | 0.086975 | 0.07782 | 0.11444 | 0.10986 | 0.059509 | 0.07782 | -0.041199 | 0.036621 | 0.07782 | -0.022888 | -0.004578 | 0.022888 | 0.1236 | 0.041199 | 121.1746 | 121.0556 | 0.004577 | 121.1746 | 121.2067 | 0.15106 | 0.032043 | 121.2204 | 121.138 | -0.05951 | 121.1334 | 121.0739 | -0.064087 | -0.032044 | 121.1563 | 121.1838 | 121.2112 | -0.096131 | 121.0922 | 121.1197 | 121.1746 | -0.013733
2825.9375 | 121.376 | -121.1014 | 0.054932 | 0.0054168 | 0.006054 | 0.073003 | 0.027152 | -0.069109 | -0.028867 | -0.0011344 | 0.014954 | 0.047978 | 0.030213 | -0.046104 | -0.006759 | 0.014591 | 0.064087 | 0.041199 | 0.10071 | 0.11444 | 0.064087 | 0.082397 | -0.059509 | 0.027466 | 0.091553 | -0.004578 | 0 | 0.013733 | 0.10071 | 0.036621 | 121.1838 | 121.0419 | 0.009155 | 121.1426 | 121.2158 | 0.17395 | 0.009155 | 121.2021 | 121.138 | -0.054932 | 121.1288 | 121.0968 | -0.041199 | -0.041199 | 121.1655 | 121.1655 | 121.2021 | -0.11444 | 121.1014 | 121.1151 | 121.1929 | -0.018311
2827.6406 | 121.3852 | -121.1243 | 0.050354 | 0.0054168 | 0.0051996 | 0.07044 | 0.025443 | -0.067828 | -0.022885 | 0.0029244 | 0.014954 | 0.048405 | 0.029572 | -0.044395 | -0.003982 | 0.0116 | 0.14191 | 0.09613 | 0.15106 | 0.16022 | 0.054932 | 0.10071 | -0.054932 | 0.10986 | 0.12817 | 0.018311 | -0.027466 | -0.004578 | 0.10071 | 0.050354 | 121.225 | 121.0693 | 0.004578 | 121.2204 | 121.2845 | 0.21515 | 0.091553 | 121.225 | 121.1746 | -0.07782 | 121.2341 | 121.1426 | -0.032043 | -0.054932 | 121.1792 | 121.2662 | 121.2753 | -0.10529 | 121.0968 | 121.1197 | 121.2524 | 0
2829.3594 | 121.2845 | -121.2112 | 0.10529 | 0.020676 | -0.0022772 | 0.071081 | 0.030356 | -0.067614 | -0.022458 | 0.0012154 | 0.0073242 | 0.050968 | 0.030854 | -0.043113 | -0.0091088 | 0.012241 | 0.054932 | 0.036621 | 0.059509 | 0.073242 | 0.086975 | 0.054932 | -0.082397 | -0.027466 | 0.032043 | -0.086975 | 0.009155 | 0.041199 | 0.059509 | -0.013733 | 121.2662 | 121.1288 | -0.018311 | 121.2479 | 121.2845 | 0.15564 | -0.050354 | 121.2708 | 121.1975 | -0.096131 | 121.1838 | 121.1243 | -0.073242 | -0.064087 | 121.2982 | 121.2662 | 121.2708 | -0.18768 | 121.2204 | 121.2524 | 121.2433 | -0.11902
2831.0625 | 121.4447 | -121.1792 | 0.054932 | 0.013046 | 0.0054132 | 0.069585 | 0.029501 | -0.070177 | -0.02844 | 0.0016428 | 0.0073242 | 0.046269 | 0.03064 | -0.045677 | -0.0076136 | 0.0163 | 0.11902 | 0.13733 | 0.15106 | 0.15106 | 0.059509 | 0.068665 | -0.027466 | 0.10529 | 0.16479 | 0.050354 | -0.022888 | -0.013733 | 0.091553 | 0.036621 | 121.2479 | 121.1517 | 0.004577 | 121.3165 | 121.3303 | 0.17853 | 0.064087 | 121.2708 | 121.2158 | -0.07782 | 121.2845 | 121.2296 | 0.013733 | -0.068665 | 121.2387 | 121.2982 | 121.3303 | -0.082398 | 121.1563 | 121.1655 | 121.344 | -0.018311
2832.8125 | 121.463 | -121.1975 | 0.045776 | 0.0054168 | 0.006695 | 0.070867 | 0.028433 | -0.068682 | -0.025876 | -0.00027975 | 0.0073242 | 0.045841 | 0.029785 | -0.045677 | -0.0082544 | 0.014377 | 0.068665 | 0.059509 | 0.10529 | 0.1236 | 0.091553 | 0.073242 | -0.050354 | 0.041199 | 0.086975 | -0.018311 | -0.004578 | -0.004578 | 0.082397 | 0.036621 | 121.2708 | 121.1472 | 0.045777 | 121.257 | 121.3211 | 0.17395 | 0.022889 | 121.2799 | 121.2341 | -0.050354 | 121.2387 | 121.1792 | -0.054932 | -0.050354 | 121.2891 | 121.2662 | 121.3028 | -0.09613 | 121.1929 | 121.1929 | 121.2845 | -0.009155
2834.5156 | 121.4401 | -121.2021 | 0.073242 | 0.0054168 | 0.0051996 | 0.073431 | 0.023093 | -0.071459 | -0.023313 | 0.00078825 | 0.022583 | 0.04691 | 0.027649 | -0.046104 | -0.0052636 | 0.015445 | 0.12817 | 0.11444 | 0.12817 | 0.11902 | 0.050354 | 0.068665 | -0.045776 | 0.068665 | 0.10071 | -0.018311 | -0.018311 | -0.004578 | 0.10529 | 0.041199 | 121.2708 | 121.1563 | -0.022888 | 121.3165 | 121.3211 | 0.16479 | 0.054932 | 121.3074 | 121.2433 | -0.091553 | 121.2708 | 121.1838 | -0.05951 | -0.07782 | 121.2524 | 121.3303 | 121.3303 | -0.11902 | 121.1838 | 121.1975 | 121.3028 | -0.032043
2836.2188 | 121.4996 | -121.225 | 0.054932 | 0.013046 | 0.0054132 | 0.071722 | 0.025229 | -0.069537 | -0.027158 | -0.00027975 | 0.014954 | 0.0499 | 0.03064 | -0.045036 | -0.0054772 | 0.014804 | 0.068665 | 0.045776 | 0.086975 | 0.10071 | 0.054932 | 0.07782 | -0.041199 | 0.036621 | 0.10071 | -0.022888 | -0.004578 | 0 | 0.091553 | 0.027466 | 121.3028 | 121.1838 | 0 | 121.2708 | 121.3257 | 0.14191 | 0.013733 | 121.3165 | 121.2524 | -0.05951 | 121.2616 | 121.2021 | -0.050354 | -0.054932 | 121.2799 | 121.2936 | 121.312 | -0.096131 | 121.2204 | 121.225 | 121.3257 | -0.027466
2837.9844 | 121.4447 | -121.2662 | 0.059509 | 0.020676 | 0.006054 | 0.074072 | 0.024802 | -0.069109 | -0.025022 | -0.00070715 | 0.014954 | 0.048832 | 0.028717 | -0.045677 | -0.0052636 | 0.016086 | 0.09613 | 0.068665 | 0.10986 | 0.11902 | 0.073242 | 0.068665 | -0.045776 | 0.045776 | 0.09613 | -0.032043 | -0.013733 | 0.013733 | 0.10529 | 0.041199 | 121.3348 | 121.2204 | 0.013733 | 121.3348 | 121.3852 | 0.16479 | 0.036621 | 121.3715 | 121.3074 | -0.073242 | 121.312 | 121.2341 | -0.073242 | -0.045776 | 121.3394 | 121.3623 | 121.376 | -0.10528 | 121.2524 | 121.2799 | 121.3623 | -0.01831
2839.6875 | 120.5704 | -120.4559 | 0.082397 | 0.0054168 | -0.0041998 | 0.07044 | 0.027152 | -0.066546 | -0.017331 | 0.00014745 | 0.0073242 | 0.050114 | 0.026581 | -0.044395 | -0.0031274 | 0.011173 | 0.10986 | 0.050354 | 0.07782 | 0.10986 | 0.082397 | 0.059509 | -0.086975 | 0.068665 | 0.082397 | -0.073242 | 0.013733 | 0.027466 | 0.091553 | 0.009155 | 120.5154 | 120.369 | 0 | 120.5063 | 120.5658 | 0.19684 | 0.027466 | 120.5475 | 120.4651 | -0.068664 | 120.5246 | 120.3827 | -0.082397 | -0.054931 | 120.5383 | 120.5658 | 120.5338 | -0.16937 | 120.4697 | 120.4834 | 120.5383 | -0.073242
2841.4219 | 120.8221 | -120.6894 | 0.091553 | 0.0054168 | -0.0041998 | 0.071935 | 0.028006 | -0.066546 | -0.022458 | 0.0022836 | 0.014954 | 0.047764 | 0.02359 | -0.044181 | -0.0063318 | 0.013309 | 0.018311 | -0.004578 | 0.022888 | 0.07782 | 0.11444 | 0.036621 | -0.086975 | -0.022888 | 0.027466 | -0.11444 | 0.027466 | 0.045776 | 0.054932 | 0 | 120.726 | 120.6024 | 0.022888 | 120.6848 | 120.7672 | 0.16479 | -0.073242 | 120.7443 | 120.6894 | -0.064087 | 120.6665 | 120.575 | -0.11444 | -0.045777 | 120.8038 | 120.7077 | 120.7123 | -0.17853 | 120.7169 | 120.7352 | 120.7169 | -0.091553
2843.1406 | 121.0007 | -120.726 | 0.054932 | 0.0054168 | 0.0011408 | 0.068304 | 0.023093 | -0.067187 | -0.020108 | 0.0029244 | 0.022583 | 0.04755 | 0.026154 | -0.044609 | -0.00505 | 0.015659 | 0.022888 | -0.022888 | 0.009155 | 0.068665 | 0.091553 | 0.050354 | -0.073242 | -0.018311 | 0.009155 | -0.11444 | 0.009155 | 0.045776 | 0.068665 | 0.013733 | 120.7764 | 120.6528 | 0.036621 | 120.7031 | 120.7947 | 0.14191 | -0.032044 | 120.7947 | 120.7397 | -0.045777 | 120.7077 | 120.6116 | -0.12817 | -0.009156 | 120.8176 | 120.7489 | 120.7352 | -0.12817 | 120.7352 | 120.7718 | 120.7352 | -0.041199
2844.9062 | 121.0785 | -120.7993 | 0.045776 | 0.0054168 | 0.0058404 | 0.072149 | 0.026297 | -0.069109 | -0.029508 | 0.00014745 | 0.014954 | 0.04456 | 0.025513 | -0.045463 | -0.010177 | 0.014591 | 0.036621 | 0.059509 | 0.10529 | 0.12817 | 0.086975 | 0.082397 | -0.054932 | 0.022888 | 0.11902 | 0.004578 | -0.041199 | 0.013733 | 0.091553 | 0.027466 | 120.8817 | 120.7443 | 0.041199 | 120.8588 | 120.9274 | 0.18311 | -0.009155 | 120.8908 | 120.8267 | -0.086975 | 120.8221 | 120.8038 | -0.022888 | -0.032043 | 120.8862 | 120.8359 | 120.9045 | -0.10071 | 120.7581 | 120.813 | 120.9183 | -0.01831
2846.6094 | 121.0281 | -120.8771 | 0.068665 | 0.013046 | -0.00035461 | 0.071722 | 0.025443 | -0.06975 | -0.020322 | 0.0024972 | 0.0073242 | 0.050114 | 0.027008 | -0.042686 | -0.0031274 | 0.015231 | 0.018311 | -0.022888 | 0.009155 | 0.064087 | 0.11902 | 0.059509 | -0.073242 | -0.027466 | -0.022888 | -0.12817 | 0.022888 | 0.032043 | 0.054932 | -0.004578 | 120.9366 | 120.8038 | 0.050354 | 120.8542 | 120.9412 | 0.13733 | -0.050354 | 120.932 | 120.8725 | -0.045777 | 120.8496 | 120.7489 | -0.1236 | -0.036622 | 120.9961 | 120.8954 | 120.8862 | -0.14191 | 120.9 | 120.9091 | 120.8542 | -0.073243
2848.3594 | 121.1655 | -120.8862 | 0.064087 | -0.0098417 | 0.0024224 | 0.068304 | 0.02587 | -0.068896 | -0.022458 | 0.00207 | 0.014954 | 0.047337 | 0.026581 | -0.043113 | -0.00505 | 0.012241 | 0.041199 | 0.004578 | 0.059509 | 0.10071 | 0.073242 | 0.07782 | -0.064087 | 0.054932 | 0.086975 | -0.036621 | -0.013733 | 0.009155 | 0.086975 | 0.045776 | 120.9641 | 120.8221 | 0.009155 | 120.8908 | 120.9869 | 0.1648 | -0.022888 | 120.9732 | 120.932 | -0.07782 | 120.9412 | 120.8496 | -0.082397 | -0.054932 | 120.9595 | 120.9274 | 120.9457 | -0.12817 | 120.8725 | 120.8954 | 120.9732 | -0.018311
2850.0781 | 121.1151 | -120.9366 | 0.07782 | -0.0022127 | -0.0024908 | 0.069158 | 0.026083 | -0.067187 | -0.022244 | 0.0022836 | 0.014954 | 0.048191 | 0.027863 | -0.042259 | -0.0065454 | 0.012454 | 0.004578 | -0.041199 | 0 | 0.073242 | 0.091553 | 0.041199 | -0.07782 | -0.022888 | 0.004578 | -0.10986 | 0.013733 | 0.036621 | 0.068665 | 0.018311 | 120.9778 | 120.8588 | 0.013733 | 120.8954 | 121.0098 | 0.15106 | -0.073242 | 121.0052 | 120.9549 | -0.064087 | 120.9137 | 120.8267 | -0.12817 | -0.041199 | 121.0281 | 120.9412 | 120.9366 | -0.15564 | 120.9503 | 120.9732 | 120.9412 | -0.059509
2851.7812 | 121.1655 | -120.9824 | 0.07782 | 0.0054168 | -0.0050544 | 0.069372 | 0.032919 | -0.067614 | -0.025449 | 0.0012154 | 0.022583 | 0.048619 | 0.027863 | -0.042472 | -0.0074 | 0.013522 | 0.013733 | 0.009155 | 0.032043 | 0.09613 | 0.086975 | 0.041199 | -0.064087 | 0 | 0.07782 | -0.086975 | 0.018311 | 0.032043 | 0.07782 | 0.027466 | 121.0236 | 120.9183 | 0.009155 | 120.9915 | 121.0785 | 0.16022 | -0.064087 | 121.0602 | 121.0098 | -0.059509 | 120.9824 | 120.8954 | -0.11444 | -0.045777 | 121.0693 | 120.9961 | 121.0144 | -0.14191 | 121.0007 | 121.0144 | 121.0602 | -0.050354
2853.4844 | 121.0693 | -120.9686 | 0.045776 | 0.0054168 | 0.00028619 | 0.070867 | 0.029074 | -0.06975 | -0.02139 | -0.00049335 | 0.022583 | 0.052677 | 0.027436 | -0.045463 | -0.003982 | 0.014591 | 0.009155 | -0.027466 | -0.004578 | 0.07782 | 0.086975 | 0.045776 | -0.073242 | -0.022888 | -0.013733 | -0.09613 | 0.013733 | 0.041199 | 0.068665 | 0.009155 | 121.0144 | 120.8954 | 0.041199 | 120.9412 | 121.0464 | 0.15106 | -0.036621 | 121.0373 | 120.9778 | -0.032043 | 120.9457 | 120.8725 | -0.10528 | -0.004577 | 121.0556 | 120.9778 | 120.9641 | -0.11902 | 120.9824 | 121.0098 | 120.9549 | -0.036621
2855.1875 | 121.1929 | -121.019 | 0.082397 | -0.0022127 | -0.00035461 | 0.06809 | 0.024588 | -0.071459 | -0.022458 | 0.0024972 | 0.022583 | 0.0499 | 0.029572 | -0.043754 | -0.0037684 | 0.014377 | 0.009155 | -0.036621 | 0.022888 | 0.068665 | 0.09613 | 0.045776 | -0.082397 | -0.032043 | -0.004578 | -0.11902 | 0.009155 | 0.036621 | 0.059509 | 0.009155 | 121.0648 | 120.9366 | 0.013733 | 120.9824 | 121.0876 | 0.15106 | -0.073242 | 121.0785 | 121.0281 | -0.073242 | 120.9869 | 120.9 | -0.12817 | -0.045776 | 121.1151 | 121.0281 | 121.0419 | -0.16479 | 121.0281 | 121.0556 | 121.0144 | -0.073242
2856.9219 | 121.312 | -121.0144 | 0.045776 | -0.0022127 | 0.0017816 | 0.068517 | 0.026724 | -0.068041 | -0.025235 | 0.0018564 | 0.014954 | 0.047764 | 0.025513 | -0.045677 | -0.0046228 | 0.015659 | 0.045776 | 0.022888 | 0.068665 | 0.10071 | 0.086975 | 0.068665 | -0.054932 | 0.036621 | 0.091553 | -0.013733 | -0.013733 | 0.009155 | 0.09613 | 0.032043 | 121.0831 | 120.9595 | 0.041199 | 121.0373 | 121.1151 | 0.15564 | 0 | 121.1105 | 121.0464 | -0.059509 | 121.051 | 121.0007 | -0.045776 | -0.036621 | 121.1014 | 121.0602 | 121.0831 | -0.10071 | 121.0007 | 121.0236 | 121.106 | -0.013733
2858.625 | 120.3552 | -120.2225 | 0.059509 | 0.0054168 | 0.0062676 | 0.073431 | 0.027579 | -0.070391 | -0.027799 | -0.00092075 | 0.014954 | 0.050114 | 0.033844 | -0.046745 | -0.0059046 | 0.016086 | 0.091553 | 0.10529 | 0.15106 | 0.1236 | 0.045776 | 0.09613 | -0.022888 | 0.027466 | 0.11444 | -0.018311 | 0 | 0.009155 | 0.10529 | 0.036621 | 120.3186 | 120.1996 | -0.013733 | 120.3278 | 120.3461 | 0.14648 | 0.032044 | 120.3278 | 120.2591 | -0.059509 | 120.2499 | 120.2042 | -0.054932 | -0.050354 | 120.2682 | 120.314 | 120.3735 | -0.082397 | 120.2225 | 120.2316 | 120.3369 | -0.022888
2860.3594 | 120.8176 | -120.7581 | 0.10986 | 0.013046 | -0.00014101 | 0.072576 | 0.03121 | -0.070605 | -0.029294 | -0.0026298 | 0.0073242 | 0.053959 | 0.035767 | -0.046531 | -0.0093226 | 0.016513 | 0.086975 | 0.10986 | 0.13733 | 0.14191 | 0.064087 | 0.086975 | -0.054932 | 0.027466 | 0.1236 | -0.018311 | -0.009155 | 0.009155 | 0.086975 | 0.032043 | 120.845 | 120.7031 | -0.045776 | 120.8679 | 120.9 | 0.19684 | -0.022888 | 120.845 | 120.7901 | -0.11902 | 120.7855 | 120.7397 | -0.050354 | -0.10071 | 120.8221 | 120.845 | 120.8954 | -0.16479 | 120.7489 | 120.7672 | 120.8817 | -0.07782
2862.0625 | 121.0236 | -120.7581 | 0.068665 | 0.0054168 | 0.0047724 | 0.072149 | 0.027579 | -0.069323 | -0.027158 | -0.0026298 | 0.022583 | 0.051396 | 0.034699 | -0.046745 | -0.0099634 | 0.013309 | 0.10529 | 0.14191 | 0.16022 | 0.15106 | 0.054932 | 0.086975 | -0.041199 | 0.086975 | 0.19226 | 0.041199 | -0.027466 | 0.009155 | 0.09613 | 0.041199 | 120.845 | 120.7169 | -0.013733 | 120.9 | 120.9091 | 0.19226 | 0.036621 | 120.8542 | 120.7993 | -0.096131 | 120.845 | 120.7993 | 0 | -0.05951 | 120.813 | 120.8633 | 120.9183 | -0.10986 | 120.7306 | 120.7672 | 120.9503 | -0.027466
2863.7656 | 121.0922 | -120.8221 | 0.068665 | 0.0054168 | 0.003277 | 0.069585 | 0.025015 | -0.067187 | -0.023526 | 0.0014292 | 0.014954 | 0.055668 | 0.033203 | -0.043754 | -0.0046228 | 0.013736 | 0.1236 | 0.059509 | 0.11444 | 0.15106 | 0.073242 | 0.086975 | -0.045776 | 0.09613 | 0.1236 | 0.018311 | -0.032043 | 0 | 0.09613 | 0.041199 | 120.9091 | 120.7764 | 0.004577 | 120.8817 | 120.9732 | 0.19684 | 0.054931 | 120.9183 | 120.8633 | -0.10071 | 120.9183 | 120.8405 | -0.022888 | -0.068665 | 120.8954 | 120.9457 | 120.9366 | -0.11444 | 120.7901 | 120.8221 | 120.9457 | -0.027466
2865.5 | 121.0648 | -120.8862 | 0.086975 | 0.0054168 | -0.0050544 | 0.069158 | 0.029074 | -0.067614 | -0.022458 | -6.615e-05 | -0.0003053 | 0.057804 | 0.03769 | -0.043968 | -0.0063318 | 0.013095 | 0.018311 | -0.013733 | 0.032043 | 0.086975 | 0.11902 | 0.054932 | -0.09613 | -0.022888 | 0.041199 | -0.10986 | 0.022888 | 0.036621 | 0.064087 | 0.004578 | 120.9412 | 120.7901 | 0.032044 | 120.8725 | 120.9732 | 0.1831 | -0.068664 | 120.9503 | 120.8908 | -0.064087 | 120.8633 | 120.7764 | -0.11444 | -0.050354 | 121.0052 | 120.9045 | 120.9183 | -0.1831 | 120.9091 | 120.9229 | 120.9274 | -0.082397
2867.2031 | 121.17 | -120.9137 | 0.059509 | 0.0054168 | 0.0064814 | 0.072149 | 0.030356 | -0.070391 | -0.028653 | -0.00049335 | 0.014954 | 0.048405 | 0.033844 | -0.04589 | -0.0080408 | 0.014804 | 0.10986 | 0.15106 | 0.17853 | 0.15564 | 0.045776 | 0.086975 | -0.050354 | 0.082397 | 0.18768 | 0.045776 | -0.013733 | 0.013733 | 0.12817 | 0.032043 | 121.0007 | 120.8633 | -0.013733 | 121.0648 | 121.0693 | 0.20599 | 0.050354 | 121.0419 | 120.9457 | -0.073242 | 120.9961 | 120.9595 | 0.013733 | -0.045776 | 120.9595 | 121.0236 | 121.0922 | -0.10986 | 120.9 | 120.9274 | 121.1014 | -0.027466
2868.9062 | 121.2021 | -120.9183 | 0.054932 | 0.028305 | 0.0069086 | 0.072576 | 0.029288 | -0.066546 | -0.028867 | -0.001348 | 0.0073242 | 0.051182 | 0.033631 | -0.043968 | -0.0063318 | 0.015445 | 0.041199 | 0.091553 | 0.11902 | 0.11902 | 0.064087 | 0.068665 | -0.036621 | 0.050354 | 0.13733 | 0.022888 | -0.013733 | 0.018311 | 0.10529 | 0.041199 | 120.9869 | 120.8817 | 0.009155 | 121.0098 | 121.0373 | 0.15564 | -0.013733 | 121.0236 | 120.9595 | -0.068665 | 120.9686 | 120.9412 | -0.018311 | -0.036621 | 120.9824 | 120.9595 | 121.0373 | -0.091553 | 120.9045 | 120.9366 | 121.0556 | -0.013733
2870.625 | 121.1472 | -120.9915 | 0.082397 | 0.020676 | -0.00078181 | 0.07044 | 0.029074 | -0.066973 | -0.02139 | -0.0017752 | 0.0073242 | 0.055454 | 0.034272 | -0.044822 | -0.0048364 | 0.0116 | 0.009155 | 0.004578 | 0.027466 | 0.068665 | 0.091553 | 0.041199 | -0.10071 | -0.009155 | 0.032043 | -0.10986 | 0.045776 | 0.041199 | 0.068665 | 0.004578 | 121.0327 | 120.8908 | 0.009156 | 120.9961 | 121.0602 | 0.16937 | -0.073242 | 121.0602 | 120.9961 | -0.036621 | 120.9824 | 120.8817 | -0.11444 | -0.041198 | 121.0831 | 121.0007 | 121.019 | -0.18311 | 121.0373 | 121.0327 | 121.0236 | -0.077819
2872.3438 | 119.1605 | -119.133 | 0.091553 | -0.0022127 | -0.0031318 | 0.068304 | 0.026297 | -0.0674 | -0.020322 | 0.00036105 | 0.0073242 | 0.069767 | 0.047516 | -0.043754 | -0.0018458 | 0.013095 | -0.004578 | -0.036621 | -0.013733 | 0.059509 | 0.10986 | 0.059509 | -0.07782 | -0.018311 | -0.018311 | -0.13275 | 0.027466 | 0.054932 | 0.064087 | 0.032043 | 119.1925 | 119.0552 | 0.01831 | 119.0964 | 119.1925 | 0.13733 | -0.096131 | 119.1971 | 119.165 | -0.064087 | 119.1147 | 119.0002 | -0.16479 | -0.036621 | 119.2429 | 119.1284 | 119.1193 | -0.16937 | 119.1605 | 119.1879 | 119.1147 | -0.05951
2874.0625 | 119.5404 | -119.5312 | 0.09613 | 0.013046 | -0.0054816 | 0.070654 | 0.02587 | -0.068041 | -0.022885 | 0.0050608 | 0.0073242 | 0.050755 | 0.031067 | -0.043113 | -0.0029138 | 0.012454 | -0.004578 | -0.022888 | 0 | 0.064087 | 0.091553 | 0.054932 | -0.068665 | -0.013733 | 0.004578 | -0.11902 | 0.013733 | 0.064087 | 0.059509 | 0.018311 | 119.5862 | 119.4626 | -0.004577 | 119.5084 | 119.5953 | 0.13275 | -0.10071 | 119.5908 | 119.5496 | -0.082397 | 119.5175 | 119.4122 | -0.13733 | -0.032043 | 119.6228 | 119.5267 | 119.5312 | -0.16479 | 119.545 | 119.5953 | 119.5358 | -0.077819
2875.7656 | 120.4697 | -120.3918 | 0.10986 | 0.0054168 | -0.002918 | 0.071508 | 0.03356 | -0.069323 | -0.023526 | 0.00078825 | 0.0073242 | 0.052037 | 0.032135 | -0.043113 | -0.0074 | 0.012241 | -0.013733 | 0.009155 | 0.027466 | 0.064087 | 0.10071 | 0.045776 | -0.09613 | -0.027466 | 0.022888 | -0.10071 | 0.032043 | 0.041199 | 0.064087 | -0.009155 | 120.4376 | 120.2957 | -0.009155 | 120.401 | 120.4559 | 0.16022 | -0.1236 | 120.4559 | 120.3827 | -0.07782 | 120.3644 | 120.2911 | -0.091553 | -0.068664 | 120.4926 | 120.3781 | 120.4193 | -0.20599 | 120.4239 | 120.433 | 120.4147 | -0.11902
2877.4844 | 120.639 | -120.4514 | 0.059509 | -0.0022127 | 0.0056268 | 0.071294 | 0.030142 | -0.069109 | -0.02908 | 0.00207 | 0.014954 | 0.047337 | 0.03064 | -0.042259 | -0.010177 | 0.015445 | 0.068665 | 0.11902 | 0.13733 | 0.13275 | 0.054932 | 0.07782 | -0.032043 | 0.032043 | 0.11444 | 0.004578 | -0.013733 | -0.004578 | 0.10986 | 0.032043 | 120.5292 | 120.4193 | -0.004577 | 120.5704 | 120.5841 | 0.16479 | 0.009156 | 120.5612 | 120.4834 | -0.073242 | 120.4834 | 120.4559 | -0.027465 | -0.064087 | 120.5063 | 120.52 | 120.5887 | -0.091552 | 120.4376 | 120.4468 | 120.5658 | -0.027466
2879.2031 | 120.7947 | -120.52 | 0.064087 | 0.013046 | 0.0054132 | 0.072363 | 0.027792 | -0.068255 | -0.027158 | -0.00027975 | 0.014954 | 0.044987 | 0.028076 | -0.044395 | -0.008468 | 0.012454 | 0.091553 | 0.11444 | 0.13275 | 0.13733 | 0.064087 | 0.086975 | -0.050354 | 0.054932 | 0.16479 | 0.041199 | -0.018311 | 0.004578 | 0.11444 | 0.036621 | 120.607 | 120.4697 | 0 | 120.6345 | 120.6573 | 0.18768 | 0.027466 | 120.6345 | 120.5566 | -0.082398 | 120.575 | 120.5612 | 0.004578 | -0.059509 | 120.5841 | 120.6116 | 120.6528 | -0.11444 | 120.5017 | 120.5246 | 120.6848 | -0.027466
2880.9062 | 120.813 | -120.5887 | 0.068665 | 0.0054168 | 0.0069086 | 0.073431 | 0.02587 | -0.066119 | -0.02908 | -0.0019888 | 0.014954 | 0.048832 | 0.029145 | -0.044822 | -0.0076136 | 0.011813 | 0.045776 | 0.073242 | 0.091553 | 0.11902 | 0.068665 | 0.064087 | -0.041199 | 0.022888 | 0.07782 | -0.022888 | -0.013733 | 0.009155 | 0.091553 | 0.027466 | 120.6528 | 120.5475 | 0 | 120.6619 | 120.7077 | 0.16022 | -0.022889 | 120.6802 | 120.6162 | -0.082398 | 120.6116 | 120.5658 | -0.050354 | -0.05951 | 120.6573 | 120.6345 | 120.6802 | -0.10986 | 120.575 | 120.5978 | 120.6665 | -0.041199
2882.625 | 120.8359 | -120.5978 | 0.054932 | 0.0054168 | 0.0039178 | 0.069158 | 0.022879 | -0.066119 | -0.022458 | 0.0033518 | 0.0073242 | 0.049473 | 0.025513 | -0.045677 | -0.0035546 | 0.0116 | 0.12817 | 0.1236 | 0.15106 | 0.16479 | 0.045776 | 0.086975 | -0.027466 | 0.10986 | 0.14648 | 0.013733 | -0.041199 | -0.013733 | 0.10529 | 0.041199 | 120.6848 | 120.5704 | -0.009156 | 120.7214 | 120.7626 | 0.19226 | 0.073242 | 120.7031 | 120.639 | -0.096131 | 120.7077 | 120.6116 | -0.027466 | -0.068665 | 120.6436 | 120.726 | 120.7489 | -0.082398 | 120.5566 | 120.5841 | 120.7443 | -0.013733
2884.3906 | 120.8221 | -120.7077 | 0.09613 | 0.013046 | -0.0033454 | 0.072149 | 0.029715 | -0.06975 | -0.021176 | 0.00036105 | 0.014954 | 0.050968 | 0.030213 | -0.044395 | -0.0074 | 0.011386 | 0.018311 | 0.004578 | 0.036621 | 0.064087 | 0.11444 | 0.041199 | -0.082397 | -0.036621 | 0.027466 | -0.09613 | 0.032043 | 0.045776 | 0.068665 | 0.009155 | 120.7489 | 120.6253 | 0.018311 | 120.7123 | 120.7718 | 0.14648 | -0.077819 | 120.7764 | 120.7169 | -0.064087 | 120.6711 | 120.6116 | -0.10528 | -0.050354 | 120.8221 | 120.726 | 120.7443 | -0.17853 | 120.7397 | 120.7535 | 120.7352 | -0.086975
2886.0938 | 120.9503 | -120.6894 | 0.068665 | 0.0054168 | 0.003277 | 0.072576 | 0.029501 | -0.06975 | -0.026517 | -0.0017752 | 0.014954 | 0.047978 | 0.029999 | -0.041191 | -0.006759 | 0.012241 | 0.1236 | 0.17853 | 0.17395 | 0.16022 | 0.059509 | 0.082397 | -0.032043 | 0.082397 | 0.17853 | 0.041199 | -0.009155 | 0 | 0.09613 | 0.054932 | 120.7718 | 120.6573 | -0.009156 | 120.8679 | 120.8496 | 0.19226 | 0.054931 | 120.7855 | 120.7443 | -0.07782 | 120.7718 | 120.7306 | -0.013733 | -0.068665 | 120.7489 | 120.813 | 120.8633 | -0.10071 | 120.6802 | 120.6894 | 120.8679 | -0.013733
2887.8281 | 120.8679 | -120.7855 | 0.10529 | 0.020676 | 7.2586e-05 | 0.073003 | 0.030783 | -0.066759 | -0.02374 | 0.00014745 | -0.0079343 | 0.047978 | 0.031067 | -0.044181 | -0.006759 | 0.011386 | 0.064087 | 0.068665 | 0.086975 | 0.12817 | 0.082397 | 0.059509 | -0.068665 | -0.009155 | 0.068665 | -0.073242 | 0.013733 | 0.027466 | 0.082397 | 0.004578 | 120.845 | 120.7169 | -0.022889 | 120.8542 | 120.9137 | 0.19684 | -0.041199 | 120.8679 | 120.7901 | -0.091553 | 120.7764 | 120.7123 | -0.07782 | -0.07782 | 120.8679 | 120.8496 | 120.8725 | -0.17395 | 120.7993 | 120.813 | 120.8542 | -0.10071
2889.5469 | 120.9183 | -120.7855 | 0.082397 | 0.013046 | -0.0024908 | 0.070867 | 0.030142 | -0.068896 | -0.023313 | -0.00070715 | 0.014954 | 0.04691 | 0.029358 | -0.040977 | -0.0074 | 0.011813 | 0.013733 | 0.027466 | 0.041199 | 0.07782 | 0.10529 | 0.032043 | -0.091553 | -0.018311 | 0.032043 | -0.09613 | 0.032043 | 0.045776 | 0.045776 | -0.004578 | 120.8176 | 120.694 | 0.022889 | 120.813 | 120.8633 | 0.16937 | -0.068664 | 120.8313 | 120.7809 | -0.050354 | 120.7672 | 120.6894 | -0.091552 | -0.036621 | 120.8908 | 120.7993 | 120.8267 | -0.17395 | 120.8176 | 120.8313 | 120.8176 | -0.086975
2891.25 | 120.9961 | -120.813 | 0.086975 | 0.013046 | -0.0059088 | 0.070867 | 0.03121 | -0.068255 | -0.022244 | -6.615e-05 | 0.0073242 | 0.04755 | 0.028931 | -0.042686 | -0.0069726 | 0.010745 | 0.018311 | 0.004578 | 0.018311 | 0.07782 | 0.10071 | 0.045776 | -0.07782 | -0.004578 | 0.022888 | -0.10986 | -0.004578 | 0.054932 | 0.054932 | 0.009155 | 120.8588 | 120.7352 | 0.013733 | 120.8176 | 120.8908 | 0.15564 | -0.068664 | 120.8679 | 120.8221 | -0.091553 | 120.8084 | 120.7031 | -0.11902 | -0.032043 | 120.9137 | 120.8313 | 120.8313 | -0.16479 | 120.8084 | 120.8679 | 120.8359 | -0.07782
2892.9531 | 121.0098 | -120.8542 | 0.068665 | 0.0054168 | -0.0041998 | 0.072149 | 0.029715 | -0.0674 | -0.020963 | 0.00078825 | 0.0073242 | 0.046269 | 0.027008 | -0.043327 | -0.0046228 | 0.010532 | 0.004578 | 0 | 0.032043 | 0.082397 | 0.091553 | 0.045776 | -0.059509 | -0.004578 | 0.054932 | -0.09613 | 0.013733 | 0.018311 | 0.068665 | 0.009155 | 120.9 | 120.7947 | 0.022888 | 120.8542 | 120.9366 | 0.14191 | -0.064087 | 120.9229 | 120.8633 | -0.054932 | 120.8496 | 120.7581 | -0.10528 | -0.050354 | 120.9457 | 120.8588 | 120.8862 | -0.12817 | 120.8679 | 120.8725 | 120.9091 | -0.05951
2894.6719 | 121.0739 | -120.8588 | 0.07782 | 0.0054168 | 0.008404 | 0.067449 | 0.026938 | -0.066759 | -0.02844 | 0.00057465 | -0.0003053 | 0.042851 | 0.024445 | -0.042686 | -0.0052636 | 0.014377 | 0.086975 | 0.1236 | 0.14191 | 0.15106 | 0.064087 | 0.068665 | -0.050354 | 0.064087 | 0.10529 | -0.004578 | -0.018311 | 0.004578 | 0.10986 | 0.027466 | 120.9274 | 120.8084 | -0.013733 | 120.9824 | 121.0098 | 0.20142 | 0.009155 | 120.9686 | 120.8862 | -0.096131 | 120.9229 | 120.8542 | -0.032044 | -0.073242 | 120.9229 | 120.9457 | 121.0007 | -0.12817 | 120.8405 | 120.8633 | 120.9641 | -0.050354
2896.375 | 121.138 | -120.8862 | 0.045776 | 0.0054168 | 0.0028498 | 0.071294 | 0.024588 | -0.069323 | -0.022885 | 0.0018564 | 0.014954 | 0.045201 | 0.023804 | -0.043968 | -0.0029138 | 0.010532 | 0.10986 | 0.10986 | 0.12817 | 0.16479 | 0.059509 | 0.10071 | -0.027466 | 0.10071 | 0.13275 | 0.018311 | -0.027466 | -0.013733 | 0.11902 | 0.050354 | 120.9869 | 120.8588 | 0.013733 | 120.9961 | 121.051 | 0.19226 | 0.064087 | 121.0052 | 120.9366 | -0.073242 | 120.9869 | 120.9045 | -0.032043 | -0.059509 | 120.9457 | 120.9961 | 121.0144 | -0.073242 | 120.8588 | 120.8725 | 121.019 | 0.004578
2898.0781 | 121.1014 | -120.8862 | 0.041199 | 0.0054168 | 0.0051996 | 0.071935 | 0.025015 | -0.06975 | -0.025876 | 0.00207 | 0.0073242 | 0.047337 | 0.026367 | -0.043968 | -0.0041956 | 0.012241 | 0.10986 | 0.13275 | 0.15106 | 0.15564 | 0.064087 | 0.10986 | -0.032043 | 0.091553 | 0.1236 | 0.004578 | -0.022888 | -0.018311 | 0.09613 | 0.045776 | 120.9961 | 120.8542 | 0.022888 | 121.019 | 121.0419 | 0.18768 | 0.068664 | 120.9824 | 120.932 | -0.064087 | 120.9778 | 120.8908 | -0.041198 | -0.05951 | 120.9503 | 120.9961 | 121.0373 | -0.073242 | 120.8633 | 120.8679 | 121.0098 | 0.004577
2899.7812 | 120.6848 | -120.5704 | 0.07782 | 0.0054168 | -0.005268 | 0.07279 | 0.026083 | -0.068468 | -0.022458 | 0.00036105 | -0.0003053 | 0.051182 | 0.022736 | -0.041404 | -0.0029138 | 0.010959 | 0.091553 | 0.050354 | 0.059509 | 0.10529 | 0.082397 | 0.054932 | -0.068665 | 0.032043 | 0.086975 | -0.050354 | 0.018311 | 0.022888 | 0.073242 | 0.022888 | 120.6253 | 120.5017 | 0.004577 | 120.6207 | 120.6757 | 0.17395 | 0.013733 | 120.6436 | 120.5933 | -0.059509 | 120.6024 | 120.52 | -0.073242 | -0.054932 | 120.6528 | 120.6619 | 120.6299 | -0.14649 | 120.5887 | 120.5933 | 120.6573 | -0.054932
2901.5 | 120.4056 | -120.163 | 0.050354 | 0.0054168 | 0.0058404 | 0.076208 | 0.025015 | -0.067614 | -0.025662 | 0.00036105 | 0.014954 | 0.048619 | 0.030854 | -0.046318 | -0.0065454 | 0.014804 | 0.07782 | 0.1236 | 0.14648 | 0.1236 | 0.036621 | 0.091553 | -0.027466 | 0.045776 | 0.11444 | -0.004578 | -0.013733 | 0.004578 | 0.091553 | 0.041199 | 120.2545 | 120.1355 | -0.013733 | 120.2866 | 120.2866 | 0.15106 | 0.027466 | 120.2545 | 120.2042 | -0.064087 | 120.2087 | 120.1584 | -0.045777 | -0.045776 | 120.1996 | 120.2408 | 120.3094 | -0.07782 | 120.1492 | 120.1675 | 120.2774 | -0.009155
2903.2188 | 120.5704 | -120.3323 | 0.15564 | 0.020676 | -0.00185 | 0.069799 | 0.023734 | -0.06975 | -0.021176 | 0.0022836 | 0.014954 | 0.080876 | 0.058625 | -0.042259 | -0.0035546 | 0.011813 | 0.022888 | -0.036621 | 0.013733 | 0.068665 | 0.09613 | 0.059509 | -0.07782 | -0.041199 | -0.018311 | -0.16479 | 0.027466 | 0.036621 | 0.07782 | -0.004578 | 120.3918 | 120.2545 | -0.05951 | 120.2957 | 120.401 | 0.14649 | -0.13275 | 120.4102 | 120.3278 | -0.12817 | 120.2911 | 120.1675 | -0.16022 | -0.11902 | 120.4285 | 120.3552 | 120.3461 | -0.23346 | 120.3598 | 120.369 | 120.314 | -0.16022
2904.9844 | 120.7764 | -120.488 | 0.073242 | 0.020676 | 0.0092584 | 0.072149 | 0.026511 | -0.069964 | -0.030362 | -0.00070715 | -0.0003053 | 0.052891 | 0.036621 | -0.044395 | -0.0082544 | 0.014377 | 0.050354 | 0.064087 | 0.11444 | 0.10986 | 0.059509 | 0.07782 | -0.050354 | 0 | 0.091553 | -0.004578 | -0.013733 | 0.022888 | 0.07782 | 0.013733 | 120.5658 | 120.4376 | -0.013733 | 120.5521 | 120.5978 | 0.16022 | -0.022888 | 120.5658 | 120.5017 | -0.086975 | 120.488 | 120.4834 | -0.018311 | -0.050354 | 120.5475 | 120.5383 | 120.6024 | -0.1236 | 120.4742 | 120.5109 | 120.5795 | -0.059509
2906.6875 | 119.3985 | -119.133 | 0.086975 | 0.013046 | 0.004986 | 0.070013 | 0.024802 | -0.06975 | -0.022458 | 0.00014745 | 0.0073242 | 0.092625 | 0.071656 | -0.044395 | -0.00505 | 0.0116 | 0.13733 | 0.10986 | 0.1236 | 0.16937 | 0.064087 | 0.10529 | -0.032043 | 0.10071 | 0.14191 | 0.027466 | -0.009155 | 0 | 0.10071 | 0.082397 | 119.2383 | 119.101 | -0.022888 | 119.2429 | 119.3024 | 0.20142 | 0.050354 | 119.2337 | 119.2154 | -0.09613 | 119.2337 | 119.1605 | -0.054931 | -0.086975 | 119.1971 | 119.2703 | 119.2566 | -0.11902 | 119.1238 | 119.133 | 119.2749 | -0.004578
2908.4219 | 120.5933 | -120.3781 | 0.050354 | -0.0022127 | 0.0062676 | 0.069372 | 0.024374 | -0.066119 | -0.026517 | 0.00057465 | -0.0003053 | 0.047337 | 0.029358 | -0.044395 | -0.0048364 | 0.013522 | 0.1236 | 0.11444 | 0.16479 | 0.14191 | 0.041199 | 0.10071 | -0.018311 | 0.068665 | 0.13275 | 0.009155 | -0.018311 | -0.004578 | 0.11444 | 0.041199 | 120.4788 | 120.3598 | -0.009155 | 120.4926 | 120.52 | 0.16022 | 0.073242 | 120.4926 | 120.4193 | -0.068665 | 120.4468 | 120.3873 | -0.032044 | -0.054932 | 120.4193 | 120.5017 | 120.5429 | -0.068665 | 120.3598 | 120.3735 | 120.5109 | -0.009155
2910.1562 | 120.6985 | -120.4559 | 0.068665 | 0.0054168 | 0.0034906 | 0.071508 | 0.026511 | -0.068468 | -0.025876 | -6.615e-05 | -0.0003053 | 0.052677 | 0.032776 | -0.046531 | -0.0069726 | 0.012668 | 0.086975 | 0.068665 | 0.1236 | 0.1236 | 0.068665 | 0.086975 | -0.036621 | 0.027466 | 0.09613 | -0.032043 | -0.009155 | 0.018311 | 0.10986 | 0.041199 | 120.5429 | 120.4193 | 0 | 120.5246 | 120.5795 | 0.16022 | 0.01831 | 120.5658 | 120.4971 | -0.07782 | 120.4834 | 120.4239 | -0.073242 | -0.050354 | 120.5246 | 120.5429 | 120.5795 | -0.10529 | 120.4468 | 120.4742 | 120.5521 | -0.027466
2911.9219 | 120.2179 | -120.0714 | 0.09613 | -0.0022127 | -0.0048406 | 0.072576 | 0.029288 | -0.069109 | -0.023313 | -0.00049335 | 0.014954 | 0.050328 | 0.03299 | -0.0429 | -0.0063318 | 0.012668 | 0.036621 | -0.018311 | 0.022888 | 0.068665 | 0.086975 | 0.036621 | -0.091553 | -0.022888 | 0.036621 | -0.11902 | 0.018311 | 0.045776 | 0.054932 | -0.013733 | 120.108 | 119.9799 | -0.009155 | 120.0531 | 120.1401 | 0.16022 | -0.059509 | 120.1263 | 120.0577 | -0.077819 | 120.0485 | 119.9524 | -0.10529 | -0.050354 | 120.1584 | 120.108 | 120.0943 | -0.18768 | 120.0897 | 120.1172 | 120.108 | -0.10986
2913.625 | 120.3552 | -120.2591 | 0.10071 | 0.0054168 | -0.0024908 | 0.071722 | 0.030569 | -0.068896 | -0.023526 | 0.00078825 | 0.022583 | 0.052677 | 0.034699 | -0.042472 | -0.0093226 | 0.010104 | 0 | 0.004578 | 0.013733 | 0.064087 | 0.11444 | 0.045776 | -0.086975 | -0.041199 | 0.045776 | -0.11444 | 0.013733 | 0.059509 | 0.059509 | -0.004578 | 120.3049 | 120.1721 | 0.013733 | 120.2637 | 120.3232 | 0.15106 | -0.10071 | 120.3186 | 120.2545 | -0.086975 | 120.2179 | 120.1447 | -0.10986 | -0.041199 | 120.3735 | 120.2591 | 120.2728 | -0.18768 | 120.2728 | 120.3186 | 120.3049 | -0.10529
2915.3438 | 120.4559 | -120.2133 | 0.032043 | 0.0054168 | 0.0011408 | 0.069158 | 0.026938 | -0.065905 | -0.023953 | 0.0012154 | 0.014954 | 0.051396 | 0.029145 | -0.041832 | -0.0029138 | 0.011386 | 0.050354 | 0 | 0.032043 | 0.073242 | 0.09613 | 0.068665 | -0.068665 | 0.050354 | 0.059509 | -0.050354 | 0.004578 | 0.022888 | 0.09613 | 0.036621 | 120.282 | 120.1447 | 0.064087 | 120.2133 | 120.2866 | 0.14191 | 0.018311 | 120.3094 | 120.2499 | -0.027465 | 120.2637 | 120.163 | -0.086975 | -0.009155 | 120.3094 | 120.2637 | 120.2454 | -0.10071 | 120.2179 | 120.2362 | 120.2728 | 0.004578
2917.0469 | 120.4788 | -120.3461 | 0.059509 | 0.013046 | -0.003559 | 0.068731 | 0.024374 | -0.067828 | -0.022672 | 0.00207 | 0.0073242 | 0.049046 | 0.030854 | -0.043754 | -0.0041956 | 0.013522 | 0.013733 | -0.036621 | -0.004578 | 0.082397 | 0.091553 | 0.045776 | -0.073242 | -0.032043 | -0.013733 | -0.12817 | 0.013733 | 0.032043 | 0.050354 | 0 | 120.3918 | 120.2728 | 0.032044 | 120.3094 | 120.4285 | 0.15564 | -0.045776 | 120.3964 | 120.3461 | -0.045776 | 120.314 | 120.2179 | -0.12817 | -0.027466 | 120.4376 | 120.3598 | 120.3415 | -0.13275 | 120.3598 | 120.3781 | 120.3323 | -0.059509
2918.75 | 120.6848 | -120.3644 | 0.045776 | 0.0054168 | 0.0064814 | 0.072576 | 0.028433 | -0.070391 | -0.031003 | -0.0022024 | 0.014954 | 0.046696 | 0.029999 | -0.045463 | -0.0088952 | 0.012882 | 0.054932 | 0.086975 | 0.1236 | 0.1236 | 0.054932 | 0.10071 | -0.041199 | 0.041199 | 0.15106 | 0.022888 | -0.022888 | 0.004578 | 0.091553 | 0.045776 | 120.4651 | 120.3232 | 0.009156 | 120.4514 | 120.488 | 0.16479 | 0.009156 | 120.4559 | 120.4102 | -0.068664 | 120.4056 | 120.3873 | -0.022888 | -0.041198 | 120.4193 | 120.4193 | 120.488 | -0.086975 | 120.3415 | 120.369 | 120.5154 | 0
2920.4531 | 120.726 | -120.4193 | 0.054932 | 0.013046 | 0.006695 | 0.074285 | 0.026938 | -0.067187 | -0.02609 | -0.00049335 | 0.022583 | 0.048191 | 0.029358 | -0.044181 | -0.0076136 | 0.012027 | 0.054932 | 0.050354 | 0.10529 | 0.11902 | 0.068665 | 0.068665 | -0.050354 | 0.022888 | 0.10986 | -0.009155 | -0.018311 | 0.013733 | 0.091553 | 0.027466 | 120.488 | 120.369 | 0.013733 | 120.4697 | 120.5383 | 0.16937 | 0 | 120.5109 | 120.4468 | -0.073243 | 120.4422 | 120.4102 | -0.036621 | -0.041199 | 120.488 | 120.4742 | 120.5246 | -0.10529 | 120.401 | 120.433 | 120.5292 | -0.027466
2922.1719 | 120.6802 | -120.4971 | 0.082397 | -0.0022127 | -0.0041998 | 0.07044 | 0.029288 | -0.068041 | -0.020322 | 0.00057465 | -0.0003053 | 0.049259 | 0.029358 | -0.044822 | -0.0035546 | 0.010318 | 0.059509 | 0.032043 | 0.041199 | 0.10986 | 0.086975 | 0.050354 | -0.082397 | 0.027466 | 0.07782 | -0.068665 | 0.009155 | 0.032043 | 0.07782 | 0.004578 | 120.5475 | 120.4147 | 0.004578 | 120.5292 | 120.607 | 0.19226 | -0.022888 | 120.575 | 120.5017 | -0.073242 | 120.5246 | 120.4285 | -0.073243 | -0.050354 | 120.5841 | 120.5566 | 120.5383 | -0.16479 | 120.5063 | 120.5292 | 120.575 | -0.077819
2923.9375 | 120.726 | -120.52 | 0.073242 | 0.0054168 | -0.00185 | 0.067236 | 0.028006 | -0.070177 | -0.021176 | 0.0016428 | -0.0003053 | 0.051396 | 0.036621 | -0.041618 | -0.0044092 | 0.012668 | 0.013733 | -0.032043 | 0.004578 | 0.07782 | 0.09613 | 0.050354 | -0.091553 | -0.018311 | -0.013733 | -0.11902 | 0.004578 | 0.027466 | 0.064087 | -0.004578 | 120.5704 | 120.4285 | 0.022888 | 120.488 | 120.5978 | 0.16937 | -0.059509 | 120.5841 | 120.5154 | -0.068664 | 120.5017 | 120.401 | -0.11444 | -0.045776 | 120.6162 | 120.5338 | 120.5246 | -0.16479 | 120.5246 | 120.5475 | 120.5063 | -0.07782
2925.6562 | 120.1584 | -119.8929 | 0.041199 | -0.0022127 | -0.00056821 | 0.071722 | 0.027579 | -0.0721 | -0.021604 | 0.0014292 | 0.022583 | 0.053318 | 0.030426 | -0.040763 | -0.0029138 | 0.013522 | 0.022888 | -0.009155 | 0.018311 | 0.064087 | 0.09613 | 0.064087 | -0.068665 | 0.013733 | 0.018311 | -0.082397 | 0.004578 | 0.032043 | 0.082397 | 0.022888 | 119.957 | 119.8242 | 0.054931 | 119.8837 | 119.957 | 0.13275 | -0.018311 | 119.9753 | 119.9158 | -0.036621 | 119.9066 | 119.8105 | -0.10528 | -0.009156 | 119.989 | 119.9158 | 119.9112 | -0.10986 | 119.8975 | 119.9249 | 119.9112 | -0.018311
2927.3906 | 120.4193 | -120.282 | 0.09613 | 0.013046 | 0.00028619 | 0.072149 | 0.028006 | -0.070177 | -0.028012 | -0.00027975 | -0.0003053 | 0.047337 | 0.032135 | -0.043968 | -0.0091088 | 0.011813 | 0.050354 | 0.10529 | 0.11902 | 0.12817 | 0.082397 | 0.082397 | -0.064087 | 0.009155 | 0.09613 | -0.054932 | 0 | 0.041199 | 0.073242 | 0.013733 | 120.3644 | 120.2179 | -0.013733 | 120.3873 | 120.4102 | 0.19226 | -0.045776 | 120.3552 | 120.2957 | -0.09613 | 120.2911 | 120.2271 | -0.068665 | -0.054931 | 120.3644 | 120.3323 | 120.401 | -0.16022 | 120.282 | 120.3232 | 120.3781 | -0.082397
2929.1094 | 120.4559 | -120.401 | 0.10529 | 0.013046 | -0.0039862 | 0.067663 | 0.028433 | -0.065478 | -0.022031 | 0.0010018 | 0.0073242 | 0.05695 | 0.03769 | -0.042045 | -0.0046228 | 0.012882 | 0.082397 | 0.054932 | 0.059509 | 0.091553 | 0.086975 | 0.07782 | -0.068665 | 0.013733 | 0.050354 | -0.10071 | 0 | 0.032043 | 0.068665 | 0.018311 | 120.4788 | 120.3323 | -0.018311 | 120.4559 | 120.4926 | 0.16022 | -0.022889 | 120.4697 | 120.4193 | -0.10529 | 120.4147 | 120.3003 | -0.11902 | -0.073243 | 120.488 | 120.4834 | 120.4605 | -0.17395 | 120.401 | 120.433 | 120.4514 | -0.086975
2930.8125 | 120.6528 | -120.4742 | 0.073242 | -0.0022127 | -0.0037726 | 0.069158 | 0.027579 | -0.069537 | -0.022672 | 0.0016428 | -0.0003053 | 0.053746 | 0.034272 | -0.0429 | -0.0059046 | 0.012027 | 0.032043 | 0.027466 | 0.059509 | 0.11444 | 0.082397 | 0.054932 | -0.07782 | 0.022888 | 0.086975 | -0.059509 | 0.009155 | 0.036621 | 0.07782 | 0.004578 | 120.5292 | 120.3964 | 0.009155 | 120.5017 | 120.5887 | 0.19226 | -0.041199 | 120.5521 | 120.4788 | -0.064087 | 120.4971 | 120.4147 | -0.064087 | -0.036621 | 120.5566 | 120.5063 | 120.5338 | -0.15106 | 120.4834 | 120.5109 | 120.5612 | -0.068664
2932.5156 | 120.8176 | -120.1767 | 0.48523 | 0.013046 | 0.00028619 | 0.071935 | 0.032706 | -0.0674 | -0.029294 | 0.0010018 | 0.014954 | 1.0819 | 1.0347 | -0.055076 | -0.011245 | 0.025058 | 0.086975 | 0.16937 | 0.18768 | 0.17853 | 0.050354 | 0.086975 | -0.050354 | 0.39825 | 0.46234 | 0.3479 | 0.52185 | 0.52185 | 0.39368 | 0.33875 | 120.2637 | 120.1263 | -0.43488 | 120.3461 | 120.3552 | 0.22888 | -0.39825 | 120.5704 | 120.5154 | 0.036622 | 120.575 | 120.5246 | 0.009155 | 0.036622 | 120.2271 | 120.2637 | 120.3644 | -0.53558 | 120.6985 | 120.6985 | 120.639 | -0.14648
2934.2188 | 119.7372 | -8.6838 | 111.1084 | 0.013046 | 0.0017816 | 0.073858 | 0.026297 | -0.067828 | -0.029935 | -0.00092075 | 0.014954 | 0.031101 | 0.0084232 | -0.043754 | -0.0082544 | 0.011173 | 0.09613 | 0.11902 | 0.13733 | 0.1236 | 0.013733 | 0.054932 | -0.068665 | 0.045776 | 0.14191 | 0.018311 | -0.073242 | -0.041199 | 0.068665 | 0.004578 | 8.7387 | 8.6151 | -111.0947 | 8.8028 | 8.8074 | 0.19226 | -111.0123 | 8.7524 | 8.6884 | -111.1816 | 8.7296 | 8.7021 | 0.013733 | -111.1496 | 8.6975 | 8.7799 | 8.8211 | -111.1771 | 8.6105 | 8.6426 | 8.8257 | -111.1038
2935.9844 | 120.2591 | -44.1422 | 75.7324 | 0.0054168 | 0.0051996 | 0.071508 | 0.022452 | -0.066119 | -0.02374 | -0.00027975 | 0.0073242 | 0.033238 | 0.0067142 | -0.044822 | -0.0063318 | 0.0116 | 0.10529 | 0.10986 | 0.12817 | 0.12817 | 0.036621 | 0.068665 | -0.050354 | 0.050354 | 0.11902 | 0 | -0.059509 | -0.018311 | 0.059509 | 0.018311 | 44.2108 | 44.0918 | -75.6958 | 44.252 | 44.2703 | 0.17853 | -75.6271 | 44.2017 | 44.1605 | -75.7919 | 44.1925 | 44.1422 | -0.018311 | -75.7507 | 44.1788 | 44.2474 | 44.2703 | -75.7828 | 44.0826 | 44.1238 | 44.2612 | -75.7141
2937.6875 | 120.1675 | -76.5015 | 43.9407 | 0.020676 | -0.0031318 | 0.071081 | 0.02587 | -0.067828 | -0.020963 | 0.00036105 | 0.014954 | 0.036015 | 0.0065006 | -0.045463 | -0.003341 | 0.010745 | 0.054932 | 0.050354 | 0.050354 | 0.059509 | 0.091553 | 0.050354 | -0.10529 | 0.009155 | 0.054932 | -0.10529 | -0.027466 | 0.004578 | 0.068665 | -0.004578 | 76.5518 | 76.3962 | -43.8492 | 76.5518 | 76.561 | 0.16479 | -43.8858 | 76.5701 | 76.4969 | -43.9682 | 76.5106 | 76.3962 | -0.10071 | -43.9362 | 76.593 | 76.5564 | 76.5518 | -44.046 | 76.474 | 76.506 | 76.5564 | -43.9453
2939.4219 | 120.3598 | -119.9799 | 0.073242 | 0.013046 | -0.0059088 | 0.070654 | 0.026938 | -0.067828 | -0.021604 | 0.00207 | 0.0073242 | 0.03516 | 0.0092776 | -0.043113 | -0.0048364 | 0.013309 | 0.064087 | 0.041199 | 0.064087 | 0.10986 | 0.086975 | 0.059509 | -0.07782 | 0.032043 | 0.07782 | -0.068665 | 0.009155 | 0.032043 | 0.073242 | 0.004578 | 120.0394 | 119.902 | 0.013733 | 120.0211 | 120.0897 | 0.18768 | -0.009155 | 120.0531 | 119.9844 | -0.064087 | 120.0119 | 119.9112 | -0.073243 | -0.041199 | 120.0668 | 120.0439 | 120.0439 | -0.15106 | 119.989 | 120.0119 | 120.0577 | -0.068664
2941.125 | 120.282 | -119.8791 | 0.1236 | 0.0054168 | -0.0044134 | 0.069799 | 0.031424 | -0.067187 | -0.022672 | 0.0016428 | 0.0073242 | 0.033024 | 0.011627 | -0.043327 | -0.0071862 | 0.012241 | 0.027466 | 0.009155 | 0.032043 | 0.10529 | 0.086975 | 0.045776 | -0.068665 | 0.009155 | 0.073242 | -0.068665 | 0.004578 | 0.022888 | 0.064087 | 0.013733 | 119.9249 | 119.8105 | -0.036621 | 119.8883 | 119.9844 | 0.17395 | -0.09613 | 119.9432 | 119.8929 | -0.11902 | 119.8883 | 119.8105 | -0.082398 | -0.10071 | 119.9661 | 119.9066 | 119.9112 | -0.19226 | 119.8837 | 119.902 | 119.9524 | -0.10986
2942.8906 | 120.3873 | -120.1126 | 0.13275 | 0.0054168 | -0.0033454 | 0.070654 | 0.032706 | -0.068041 | -0.025876 | -0.0011344 | 0.014954 | 0.033879 | 0.0088504 | -0.043327 | -0.0074 | 0.013522 | -0.009155 | -0.004578 | 0.013733 | 0.073242 | 0.10529 | 0.036621 | -0.09613 | -0.054932 | 0.032043 | -0.10986 | 0.013733 | 0.036621 | 0.059509 | -0.013733 | 120.1492 | 120.0165 | -0.027465 | 120.108 | 120.1859 | 0.16937 | -0.14191 | 120.1721 | 120.0989 | -0.11902 | 120.0577 | 120.0027 | -0.09613 | -0.09613 | 120.2179 | 120.1035 | 120.1263 | -0.22888 | 120.1263 | 120.1492 | 120.1447 | -0.14648
2944.5938 | 120.2225 | -119.9982 | 0.14648 | 0.0054168 | -0.00099541 | 0.07044 | 0.031638 | -0.070391 | -0.026944 | 0.0010018 | 0.014954 | 0.030888 | 0.010773 | -0.045036 | -0.010177 | 0.013095 | 0.064087 | 0.11444 | 0.15564 | 0.15564 | 0.068665 | 0.073242 | -0.041199 | 0.027466 | 0.13733 | -0.013733 | -0.022888 | 0.009155 | 0.07782 | 0.013733 | 120.0714 | 119.957 | -0.077819 | 120.1126 | 120.1538 | 0.19684 | -0.082397 | 120.076 | 120.0119 | -0.16937 | 120.0256 | 119.9844 | -0.027466 | -0.13733 | 120.0668 | 120.0623 | 120.1538 | -0.18768 | 119.9753 | 120.0073 | 120.1355 | -0.13275
2946.3125 | 120.3964 | -120.1309 | 0.10529 | 0.0054168 | 0.00071339 | 0.069799 | 0.026511 | -0.070818 | -0.022244 | -6.615e-05 | -0.0003053 | 0.03281 | 0.0077822 | -0.042259 | -0.0048364 | 0.012241 | 0.004578 | -0.041199 | 0 | 0.064087 | 0.09613 | 0.064087 | -0.068665 | -0.036621 | -0.022888 | -0.11902 | 0 | 0.045776 | 0.064087 | 0 | 120.195 | 120.0623 | -0.009156 | 120.0897 | 120.195 | 0.13275 | -0.10071 | 120.195 | 120.1309 | -0.10529 | 120.0943 | 120.0119 | -0.11902 | -0.05951 | 120.2271 | 120.1355 | 120.1309 | -0.17395 | 120.1309 | 120.1767 | 120.108 | -0.10529
2948.0312 | 120.5017 | -119.9432 | 0.28839 | 0.0054168 | 0.004345 | 0.070226 | 0.028433 | -0.068896 | -0.024594 | 0.0022836 | 0.014954 | 0.034092 | 0.0058596 | -0.043754 | -0.003982 | 0.012882 | 0.068665 | 0.082397 | 0.11444 | 0.12817 | 0.07782 | 0.091553 | -0.045776 | 0.073242 | 0.11444 | 0 | -0.036621 | -0.013733 | 0.10986 | 0.054932 | 120.0348 | 119.8975 | -0.21057 | 120.0256 | 120.0714 | 0.17395 | -0.21973 | 120.0531 | 119.9982 | -0.32501 | 120.0165 | 119.9432 | -0.054932 | -0.30212 | 120.0211 | 120.0119 | 120.0577 | -0.33417 | 119.9066 | 119.9295 | 120.0577 | -0.23346
2949.75 | 120.314 | -119.5633 | 0.65918 | 0.0054168 | -0.0050544 | 0.070867 | 0.027152 | -0.068682 | -0.020322 | -0.00070715 | 0.0073242 | 0.037297 | 0.0092776 | -0.0429 | -0.0014184 | 0.012668 | 0.07782 | 0.059509 | 0.073242 | 0.1236 | 0.082397 | 0.064087 | -0.050354 | 0.022888 | 0.073242 | -0.068665 | 0 | 0.022888 | 0.07782 | 0.013733 | 119.6274 | 119.5129 | -0.57678 | 119.6228 | 119.6869 | 0.17395 | -0.58136 | 119.6411 | 119.577 | -0.65918 | 119.5862 | 119.4946 | -0.082398 | -0.63629 | 119.6457 | 119.6411 | 119.6365 | -0.70953 | 119.5633 | 119.5862 | 119.6365 | -0.64545
2951.5 | 120.3049 | -119.7968 | 0.032043 | 0.013046 | 0.0019952 | 0.071081 | 0.02352 | -0.073168 | -0.025235 | 0.0029244 | 0.0073242 | 0.03281 | 0.005646 | -0.041832 | -0.0048364 | 0.013309 | 0.050354 | 0.032043 | 0.07782 | 0.11444 | 0.064087 | 0.073242 | -0.054932 | 0.059509 | 0.11444 | -0.022888 | -0.022888 | -0.004578 | 0.11444 | 0.045776 | 119.87 | 119.7418 | 0.032044 | 119.8288 | 119.9112 | 0.16937 | 0.018311 | 119.9112 | 119.8425 | -0.054931 | 119.8563 | 119.7739 | -0.068664 | -0.036621 | 119.8608 | 119.8471 | 119.8746 | -0.086975 | 119.7739 | 119.7922 | 119.9112 | 0.013733
2953.25 | 120.4376 | -120.2179 | 0.10071 | -0.0022127 | -0.0012092 | 0.070867 | 0.030356 | -0.069537 | -0.025449 | -0.00027975 | 0.0073242 | 0.035374 | 0.010346 | -0.040336 | -0.010604 | 0.01395 | -0.004578 | -0.009155 | 0.059509 | 0.068665 | 0.091553 | 0.032043 | -0.073242 | -0.054932 | 0.041199 | -0.11444 | 0.022888 | 0.041199 | 0.041199 | -0.013733 | 120.2499 | 120.1447 | -0.009155 | 120.2087 | 120.2866 | 0.14191 | -0.10529 | 120.2591 | 120.2042 | -0.07782 | 120.163 | 120.1035 | -0.10071 | -0.059509 | 120.3094 | 120.2133 | 120.2774 | -0.17395 | 120.2408 | 120.2591 | 120.2591 | -0.11444
2955.0312 | 120.4971 | -120.3461 | 0.09613 | -0.0098417 | -0.0048406 | 0.071294 | 0.026511 | -0.067828 | -0.022885 | 0.00078825 | 0.022583 | 0.036656 | 0.0054324 | -0.041404 | -0.00505 | 0.0116 | 0.004578 | -0.013733 | 0.013733 | 0.082397 | 0.10071 | 0.054932 | -0.086975 | -0.032043 | -0.004578 | -0.14648 | 0.004578 | 0.032043 | 0.054932 | -0.009155 | 120.401 | 120.2591 | 0.004578 | 120.3323 | 120.4285 | 0.16937 | -0.091552 | 120.401 | 120.3369 | -0.091552 | 120.314 | 120.1996 | -0.13733 | -0.064087 | 120.4468 | 120.3506 | 120.3598 | -0.1831 | 120.3506 | 120.3781 | 120.3415 | -0.10528
2956.7344 | 120.5292 | -120.3964 | 0.082397 | 0.013046 | -0.0033454 | 0.068731 | 0.025229 | -0.066332 | -0.022458 | 0.0010018 | -0.0003053 | 0.034733 | 0.009064 | -0.043754 | -0.003982 | 0.014163 | 0 | -0.036621 | 0.004578 | 0.064087 | 0.082397 | 0.050354 | -0.068665 | -0.041199 | -0.004578 | -0.13275 | 0.018311 | 0.036621 | 0.064087 | -0.009155 | 120.4468 | 120.3278 | 0 | 120.3598 | 120.4605 | 0.13275 | -0.082397 | 120.4605 | 120.3873 | -0.064086 | 120.3552 | 120.2637 | -0.1236 | -0.045776 | 120.4788 | 120.3964 | 120.401 | -0.15106 | 120.4147 | 120.433 | 120.3918 | -0.091552
2958.5 | 120.6665 | -120.314 | 0.12817 | 0.013046 | 0.0028498 | 0.073217 | 0.029501 | -0.068468 | -0.031857 | -0.001348 | -0.0003053 | 0.031101 | 0.0075686 | -0.0429 | -0.0080408 | 0.014591 | 0.027466 | 0.050354 | 0.091553 | 0.10986 | 0.068665 | 0.091553 | -0.050354 | -0.009155 | 0.082397 | -0.022888 | -0.027466 | 0.009155 | 0.086975 | 0.022888 | 120.4056 | 120.2637 | -0.059509 | 120.3644 | 120.4239 | 0.16022 | -0.10071 | 120.401 | 120.3369 | -0.15564 | 120.3049 | 120.2911 | -0.045776 | -0.11902 | 120.3827 | 120.3415 | 120.4056 | -0.17853 | 120.2866 | 120.3232 | 120.3964 | -0.10529
2960.2188 | 120.7352 | -120.401 | 0.045776 | 0.020676 | 0.0047724 | 0.072149 | 0.030783 | -0.071673 | -0.029721 | -0.0022024 | 0.0073242 | 0.030888 | 0.0088504 | -0.044822 | -0.0095362 | 0.013736 | 0.09613 | 0.13733 | 0.16937 | 0.15106 | 0.050354 | 0.082397 | -0.022888 | 0.07782 | 0.16479 | 0.064087 | -0.009155 | 0.004578 | 0.11902 | 0.059509 | 120.4834 | 120.3781 | 0.004578 | 120.5383 | 120.5521 | 0.17395 | 0.050354 | 120.52 | 120.4605 | -0.054931 | 120.4788 | 120.4651 | 0.004578 | -0.041198 | 120.4514 | 120.4971 | 120.5704 | -0.068664 | 120.3918 | 120.4056 | 120.5658 | 0.013733
2962.0156 | 120.6299 | -120.4742 | 0.09613 | 0.0054168 | -0.003559 | 0.069372 | 0.026938 | -0.06975 | -0.020108 | -0.00049335 | 0.0073242 | 0.034733 | 0.010132 | -0.041618 | -0.003982 | 0.011386 | -0.004578 | -0.07782 | -0.009155 | 0.050354 | 0.091553 | 0.050354 | -0.054932 | -0.032043 | -0.027466 | -0.1236 | 0.013733 | 0.018311 | 0.045776 | 0.009155 | 120.5246 | 120.4193 | -0.004577 | 120.3964 | 120.5246 | 0.10529 | -0.10071 | 120.52 | 120.4834 | -0.082397 | 120.4422 | 120.3506 | -0.13275 | -0.077819 | 120.5658 | 120.4697 | 120.4651 | -0.15106 | 120.488 | 120.4926 | 120.4468 | -0.086975
2963.7188 | 115.361 | -12.8586 | 92.3538 | 0.0054168 | -0.00185 | 0.072149 | 0.027152 | -0.069323 | -0.02374 | 0.00207 | 0.0073242 | 0.033451 | 0.0094912 | -0.040336 | -0.00505 | 0.012668 | -0.022888 | -0.082397 | -0.041199 | 0.036621 | 0.054932 | 0.022888 | -0.1236 | -0.068665 | -0.064087 | -0.16937 | -0.018311 | -0.009155 | 0.032043 | -0.036621 | 12.8815 | 12.735 | -92.2989 | 12.7762 | 12.8952 | 0.16022 | -92.3767 | 12.8906 | 12.822 | -92.3721 | 12.7899 | 12.6892 | -0.13275 | -92.363 | 12.9135 | 12.8357 | 12.8174 | -92.4774 | 12.8403 | 12.8494 | 12.7945 | -92.3904
2965.4375 | 96.9452 | -0.10529 | 96.0434 | 0.0054168 | -0.0031318 | 0.070654 | 0.031424 | -0.070818 | -0.022672 | 0.00014745 | 0.0073242 | 0.031956 | 0.010132 | -0.042045 | -0.0061182 | 0.0116 | -0.036621 | -0.036621 | -0.004578 | 0.045776 | 0.036621 | 0 | -0.11902 | -0.041199 | 0.018311 | -0.14191 | -0.009155 | -0.009155 | 0.013733 | -0.045776 | 0.10529 | -0.013733 | -96.0068 | 0.068665 | 0.15106 | 0.16479 | -96.08 | 0.11902 | 0.05951 | -96.0526 | 0.064087 | -0.036621 | -0.096131 | -96.0526 | 0.14191 | 0.068665 | 0.10071 | -96.1624 | 0.096131 | 0.096131 | 0.1236 | -96.0892
2967.1562 | 120.5704 | -2.861 | 116.8716 | 0.020676 | 0.00092719 | 0.069372 | 0.026724 | -0.0721 | -0.024381 | 0.0022836 | -0.0003053 | 0.031101 | 0.005646 | -0.043327 | -0.0054772 | 0.013095 | 0.068665 | 0.054932 | 0.091553 | 0.11902 | 0.018311 | 0.054932 | -0.091553 | 0.041199 | 0.09613 | -0.032043 | -0.07782 | -0.059509 | 0.073242 | 0.009155 | 2.916 | 2.7695 | -116.8533 | 2.916 | 2.98 | 0.21057 | -116.803 | 2.9343 | 2.8702 | -116.9495 | 2.9022 | 2.829 | -0.041198 | -116.9312 | 2.8793 | 2.9297 | 2.9526 | -116.9632 | 2.7832 | 2.8015 | 2.9572 | -116.8625
2968.9375 | 120.694 | -4.0604 | 116.1667 | 0.013046 | 0.0056268 | 0.070867 | 0.024802 | -0.065264 | -0.025449 | -0.00070715 | 0.0073242 | 0.032383 | 0.007355 | -0.043541 | -0.0059046 | 0.012454 | 0.064087 | 0.073242 | 0.11444 | 0.11902 | 0.004578 | 0.054932 | -0.073242 | 0.059509 | 0.086975 | -0.027466 | -0.082397 | -0.064087 | 0.045776 | -0.009155 | 4.1153 | 3.9871 | -116.1621 | 4.1336 | 4.1794 | 0.19226 | -116.1026 | 4.1061 | 4.0512 | -116.2491 | 4.1199 | 4.0329 | -0.018311 | -116.2308 | 4.0649 | 4.1245 | 4.1748 | -116.2399 | 3.978 | 3.9963 | 4.1473 | -116.1758
2970.6875 | 115.9927 | -60.6995 | 54.8126 | -0.0022127 | -0.0033454 | 0.069585 | 0.028647 | -0.067614 | -0.023099 | -0.0011344 | 0.0073242 | 0.032597 | 0.0097048 | -0.0429 | -0.0082544 | 0.011173 | -0.013733 | -0.045776 | 0 | 0.050354 | 0.073242 | 0.018311 | -0.10986 | -0.050354 | 0 | -0.13275 | 0.009155 | 0.013733 | 0.036621 | -0.027466 | 60.7178 | 60.5896 | -54.7394 | 60.6537 | 60.7498 | 0.16022 | -54.8264 | 60.7361 | 60.672 | -54.8035 | 60.6491 | 60.5667 | -0.10529 | -54.7989 | 60.7727 | 60.6857 | 60.6995 | -54.9225 | 60.7086 | 60.7132 | 60.6995 | -54.8401
2972.3906 | 120.5566 | -91.2415 | 25.3372 | 0.020676 | -0.0048406 | 0.068945 | 0.029929 | -0.071459 | -0.024167 | -0.00049335 | 0.0073242 | 0.031101 | 0.011414 | -0.043327 | -0.0063318 | 0.0116 | -0.022888 | -0.036621 | -0.004578 | 0.041199 | 0.086975 | 0.032043 | -0.091553 | -0.054932 | 0.004578 | -0.11902 | -0.004578 | 0.013733 | 0.045776 | -0.018311 | 91.2735 | 91.1499 | -25.2502 | 91.2048 | 91.2827 | 0.13275 | -25.3601 | 91.2872 | 91.2231 | -25.3418 | 91.1865 | 91.1224 | -0.10071 | -25.3235 | 91.3284 | 91.2186 | 91.2369 | -25.4288 | 91.2369 | 91.2552 | 91.246 | -25.3555
2974.0938 | 120.5017 | -14.9826 | 104.8782 | 0.013046 | 0.0039178 | 0.069799 | 0.024374 | -0.069323 | -0.026517 | 0.00036105 | 0.0073242 | 0.030888 | 0.0058596 | -0.043113 | -0.00505 | 0.012882 | 0.073242 | 0.082397 | 0.12817 | 0.10986 | 0.013733 | 0.059509 | -0.064087 | 0.041199 | 0.09613 | -0.022888 | -0.068665 | -0.050354 | 0.068665 | 0 | 15.0421 | 14.9185 | -104.8645 | 15.065 | 15.0925 | 0.17395 | -104.805 | 15.0513 | 14.9826 | -104.9469 | 15.0238 | 14.9597 | -0.022888 | -104.9286 | 14.9963 | 15.0558 | 15.1108 | -104.9423 | 14.9139 | 14.9323 | 15.0787 | -104.8782
2975.7969 | 119.8975 | -12.4786 | 107.1625 | 0.020676 | -0.002918 | 0.069585 | 0.027579 | -0.069964 | -0.023953 | 0.00057465 | 0.014954 | 0.034092 | 0.0065006 | -0.044181 | -0.0029138 | 0.013522 | -0.018311 | -0.068665 | -0.041199 | 0.027466 | 0.068665 | 0.013733 | -0.09613 | -0.07782 | -0.073242 | -0.16937 | -0.027466 | -0.022888 | 0.036621 | -0.041199 | 12.4924 | 12.3825 | -107.0938 | 12.41 | 12.5061 | 0.1236 | -107.1808 | 12.5153 | 12.4374 | -107.1899 | 12.4008 | 12.3093 | -0.12817 | -107.1854 | 12.5473 | 12.4603 | 12.4374 | -107.2586 | 12.4512 | 12.4558 | 12.4054 | -107.2037
2977.5 | 92.6651 | -0.13275 | 94.693 | 0.0054168 | -0.003559 | 0.070867 | 0.026083 | -0.067614 | -0.020963 | 0.0012154 | 0.0073242 | 0.034947 | 0.0069278 | -0.042045 | -0.0048364 | 0.013095 | 0.013733 | 0 | 0.013733 | 0.064087 | 0.041199 | 0.022888 | -0.13733 | -0.027466 | 0.036621 | -0.10986 | -0.036621 | -0.004578 | 0.022888 | -0.045776 | 0.15564 | -0.004578 | -94.6518 | 0.13275 | 0.19684 | 0.20142 | -94.6793 | 0.15564 | 0.086975 | -94.7296 | 0.10529 | 0.022888 | -0.064087 | -94.6976 | 0.17395 | 0.14648 | 0.14648 | -94.8303 | 0.09613 | 0.12817 | 0.16937 | -94.7388
2979.2188 | 99.8062 | -2.6642 | 86.6455 | 0.0054168 | -0.0031318 | 0.070867 | 0.02886 | -0.070605 | -0.025235 | -0.00092075 | 0.0073242 | 0.033665 | 0.0094912 | -0.042686 | -0.0086816 | 0.015659 | -0.041199 | -0.059509 | -0.032043 | 0.027466 | 0.064087 | 0.022888 | -0.13275 | -0.082397 | -0.022888 | -0.16022 | -0.022888 | -0.009155 | 0.018311 | -0.027466 | 2.6871 | 2.5314 | -86.5814 | 2.6047 | 2.6917 | 0.16022 | -86.6867 | 2.6825 | 2.6367 | -86.6684 | 2.5818 | 2.504 | -0.13275 | -86.6547 | 2.7283 | 2.623 | 2.6321 | -86.7783 | 2.6413 | 2.655 | 2.6413 | -86.673
2980.9844 | 120.6528 | -3.9642 | 115.9103 | 0.013046 | 0.0024224 | 0.068517 | 0.025443 | -0.066973 | -0.025876 | 0.0022836 | 0.014954 | 0.031101 | 0.0069278 | -0.044609 | -0.0065454 | 0.011813 | 0.059509 | 0.068665 | 0.1236 | 0.1236 | 0 | 0.054932 | -0.059509 | 0.041199 | 0.091553 | -0.013733 | -0.073242 | -0.054932 | 0.041199 | 0.004578 | 4.0192 | 3.9047 | -115.9103 | 4.0329 | 4.0878 | 0.1831 | -115.8508 | 4.0054 | 3.9688 | -115.9836 | 4.0054 | 3.9505 | -0.018311 | -115.9653 | 3.9642 | 4.0237 | 4.0878 | -115.9698 | 3.891 | 3.9093 | 4.0558 | -115.9058
2982.6875 | 119.6548 | -106.5445 | 12.6892 | 0.0054168 | 0.001568 | 0.067236 | 0.028433 | -0.069109 | -0.023313 | 0.00036105 | 0.014954 | 0.035374 | 0.007355 | -0.043754 | -0.0041956 | 0.013736 | 0.036621 | -0.027466 | 0.013733 | 0.073242 | 0.10071 | 0.054932 | -0.07782 | -0.004578 | 0.013733 | -0.082397 | -0.009155 | 0.018311 | 0.064087 | 0.027466 | 106.5994 | 106.4667 | -12.5885 | 106.517 | 106.6177 | 0.15106 | -12.6526 | 106.6086 | 106.572 | -12.6984 | 106.5399 | 106.4621 | -0.10986 | -12.6709 | 106.6452 | 106.5811 | 106.5582 | -12.767 | 106.5353 | 106.5628 | 106.5582 | -12.6617
2984.4688 | 120.6253 | -106.4117 | 13.7238 | -0.0022127 | 0.00028619 | 0.070654 | 0.029074 | -0.068896 | -0.022672 | -0.00070715 | -0.0003053 | 0.035801 | 0.0099186 | -0.039909 | -0.0063318 | 0.013522 | -0.013733 | -0.032043 | 0.004578 | 0.045776 | 0.10529 | 0.050354 | -0.07782 | -0.036621 | -0.018311 | -0.11902 | 0.009155 | 0.022888 | 0.050354 | 0 | 106.4621 | 106.3339 | -13.6185 | 106.3797 | 106.4575 | 0.1236 | -13.7375 | 106.4621 | 106.4117 | -13.7146 | 106.3751 | 106.2927 | -0.11902 | -13.7009 | 106.517 | 106.398 | 106.4163 | -13.8016 | 106.4209 | 106.4346 | 106.3934 | -13.7238
2986.1719 | 120.5109 | -105.7663 | 14.1495 | 0.013046 | 0.00092719 | 0.069799 | 0.031638 | -0.069323 | -0.022885 | 0.0012154 | 0.014954 | 0.033665 | 0.011414 | -0.039482 | -0.0063318 | 0.013309 | 0.004578 | -0.018311 | 0 | 0.068665 | 0.10986 | 0.050354 | -0.082397 | -0.013733 | -0.013733 | -0.086975 | 0 | 0.013733 | 0.068665 | 0.004578 | 105.8166 | 105.6839 | -14.0396 | 105.748 | 105.835 | 0.15106 | -14.1449 | 105.835 | 105.7709 | -14.1495 | 105.7526 | 105.6793 | -0.091553 | -14.1357 | 105.8762 | 105.7709 | 105.7663 | -14.2319 | 105.7663 | 105.78 | 105.7526 | -14.1449
2987.9375 | 115.2969 | -47.9233 | 66.5451 | 0.020676 | 0.0062676 | 0.072576 | 0.028006 | -0.066546 | -0.027799 | -0.0017752 | 0.014954 | 0.031101 | 0.0094912 | -0.04589 | -0.0082544 | 0.015659 | 0.073242 | 0.10071 | 0.13733 | 0.11902 | 0.027466 | 0.064087 | -0.041199 | 0.041199 | 0.082397 | -0.018311 | -0.045776 | -0.032043 | 0.068665 | 0.013733 | 47.9874 | 47.8821 | -66.5176 | 48.024 | 48.0423 | 0.16022 | -66.4719 | 47.9919 | 47.937 | -66.5909 | 47.9645 | 47.905 | -0.032044 | -66.5771 | 47.9507 | 47.9965 | 48.0606 | -66.5863 | 47.8775 | 47.8912 | 48.0057 | -66.5314
2989.6406 | 120.4102 | -0.38452 | 119.3115 | 0.013046 | 0.006695 | 0.073003 | 0.026083 | -0.066759 | -0.027371 | -0.00027975 | 0.0073242 | 0.031956 | 0.0077822 | -0.042686 | -0.0091088 | 0.015018 | 0.036621 | 0.032043 | 0.073242 | 0.07782 | 0.022888 | 0.036621 | -0.082397 | -0.027466 | 0.041199 | -0.073242 | -0.059509 | -0.041199 | 0.054932 | 0.004578 | 0.42114 | 0.30212 | -119.2886 | 0.41656 | 0.46234 | 0.16022 | -119.2749 | 0.43945 | 0.3891 | -119.371 | 0.35706 | 0.31128 | -0.07782 | -119.3527 | 0.40741 | 0.42114 | 0.45776 | -119.3939 | 0.32501 | 0.34332 | 0.42572 | -119.3069
2991.3438 | 119.8196 | -0.737 | 118.309 | 0.0054168 | 0.0028498 | 0.072363 | 0.031851 | -0.066973 | -0.026731 | -0.00092075 | -0.0003053 | 0.029606 | 0.0092776 | -0.043754 | -0.0080408 | 0.011813 | 0.064087 | 0.10529 | 0.13275 | 0.1236 | 0.018311 | 0.045776 | -0.07782 | 0.027466 | 0.1236 | -0.013733 | -0.068665 | -0.050354 | 0.054932 | 0 | 0.78278 | 0.65918 | -118.2907 | 0.84229 | 0.8606 | 0.20142 | -118.2449 | 0.79193 | 0.737 | -118.3777 | 0.76447 | 0.72327 | -0.013733 | -118.3594 | 0.75531 | 0.80109 | 0.86975 | -118.3868 | 0.66834 | 0.68665 | 0.8606 | -118.309
2993.0781 | 120.4193 | -0.54932 | 119.3619 | -0.0022127 | 0.0024224 | 0.068945 | 0.02117 | -0.068041 | -0.021604 | -6.615e-05 | 0.0073242 | 0.03516 | 0.007996 | -0.042045 | -0.0035546 | 0.011813 | 0.032043 | -0.009155 | 0.027466 | 0.07782 | 0.032043 | 0.027466 | -0.09613 | 0.027466 | 0.054932 | -0.082397 | -0.064087 | -0.022888 | 0.059509 | -0.009155 | 0.57678 | 0.45319 | -119.3298 | 0.54016 | 0.62714 | 0.17395 | -119.3298 | 0.60883 | 0.54016 | -119.426 | 0.57678 | 0.46692 | -0.073242 | -119.3848 | 0.58136 | 0.58136 | 0.57678 | -119.458 | 0.48523 | 0.52643 | 0.60425 | -119.371
2994.7812 | 120.1584 | -1.2955 | 118.8538 | 0.0054168 | -0.00056821 | 0.068945 | 0.026083 | -0.064837 | -0.020535 | 0.00014745 | 0.0073242 | 0.033451 | 0.0084232 | -0.043754 | -0.0024866 | 0.012882 | -0.045776 | -0.10529 | -0.050354 | 0.013733 | 0.050354 | 0.013733 | -0.11902 | -0.068665 | -0.068665 | -0.17853 | -0.004578 | -0.004578 | 0.022888 | -0.027466 | 1.3092 | 1.1765 | -118.8034 | 1.1902 | 1.3092 | 0.13275 | -118.8995 | 1.3184 | 1.268 | -118.8583 | 1.2268 | 1.1169 | -0.15106 | -118.8583 | 1.3458 | 1.2497 | 1.2451 | -118.9728 | 1.2909 | 1.2909 | 1.2268 | -118.8812
2996.5156 | 120.3918 | -1.3824 | 119.0689 | 0.0054168 | -0.0031318 | 0.071935 | 0.029715 | -0.067828 | -0.026517 | 0.00078825 | 0.014954 | 0.033665 | 0.0092776 | -0.043541 | -0.0093226 | 0.012882 | 0.004578 | 0 | 0.041199 | 0.059509 | 0.041199 | 0 | -0.11902 | -0.082397 | 0.009155 | -0.12817 | -0.013733 | -0.013733 | 0.018311 | -0.041199 | 1.3824 | 1.2634 | -119.0277 | 1.3824 | 1.442 | 0.17853 | -119.0643 | 1.4008 | 1.3412 | -119.0826 | 1.3 | 1.2543 | -0.086975 | -119.0826 | 1.4236 | 1.387 | 1.4236 | -119.1879 | 1.3687 | 1.3687 | 1.3916 | -119.1101
2998.25 | 120.4468 | -0.58136 | 119.3298 | 0.013046 | -0.00078181 | 0.06809 | 0.026083 | -0.067614 | -0.021817 | 0.0012154 | 0.0073242 | 0.034733 | 0.0088504 | -0.039482 | -0.0052636 | 0.012882 | -0.045776 | -0.073242 | -0.032043 | 0.027466 | 0.068665 | 0.018311 | -0.1236 | -0.068665 | -0.054932 | -0.16479 | -0.036621 | -0.009155 | 0.027466 | -0.036621 | 0.59967 | 0.45776 | -119.2612 | 0.50812 | 0.60883 | 0.15106 | -119.3756 | 0.60883 | 0.54474 | -119.3665 | 0.5127 | 0.41656 | -0.12817 | -119.339 | 0.65002 | 0.53558 | 0.54932 | -119.4534 | 0.54474 | 0.5722 | 0.52643 | -119.3665
3000 | 120.5841 | -0.74158 | 119.5358 | 0.0054168 | 0.0045588 | 0.073003 | 0.029074 | -0.067614 | -0.031644 | -0.00070715 | 0.0073242 | 0.028965 | 0.0084232 | -0.042686 | -0.0093226 | 0.012882 | 0.009155 | 0.050354 | 0.09613 | 0.10529 | 0.022888 | 0.036621 | -0.082397 | 0.018311 | 0.10986 | -0.013733 | -0.082397 | -0.054932 | 0.068665 | -0.018311 | 0.7782 | 0.65918 | -119.5129 | 0.79193 | 0.84686 | 0.18768 | -119.5267 | 0.81024 | 0.72327 | -119.6182 | 0.75989 | 0.72784 | 0.004578 | -119.5908 | 0.76447 | 0.75073 | 0.83771 | -119.6182 | 0.65918 | 0.68665 | 0.85144 | -119.5541
3001.7031 | 120.6116 | -0.82855 | 119.5587 | 0.013046 | 0.0041314 | 0.070654 | 0.023947 | -0.068682 | -0.02374 | 0.00036105 | 0.0073242 | 0.031315 | 0.0071414 | -0.044181 | -0.0054772 | 0.012454 | 0.068665 | 0.073242 | 0.10986 | 0.10529 | 0 | 0.045776 | -0.059509 | 0.054932 | 0.09613 | -0.018311 | -0.082397 | -0.050354 | 0.059509 | 0.013733 | 0.87433 | 0.76904 | -119.5587 | 0.90179 | 0.93384 | 0.16479 | -119.4901 | 0.88806 | 0.84228 | -119.6411 | 0.88348 | 0.81024 | -0.032044 | -119.6091 | 0.82855 | 0.89722 | 0.93841 | -119.6182 | 0.74615 | 0.7782 | 0.92468 | -119.545
3003.4062 | 119.6411 | -1.0757 | 119.0872 | -0.0022127 | 0.0026362 | 0.068304 | 0.02352 | -0.069964 | -0.025876 | 0.0012154 | -0.0079343 | 0.033879 | 0.0071414 | -0.043327 | -0.0037684 | 0.011173 | 0.07782 | 0.059509 | 0.086975 | 0.10986 | 0.022888 | 0.050354 | -0.073242 | 0.050354 | 0.082397 | -0.027466 | -0.086975 | -0.064087 | 0.068665 | 0.022888 | 1.1261 | 1.0025 | -119.0643 | 1.1353 | 1.1856 | 0.18311 | -119.0094 | 1.1444 | 1.0986 | -119.1742 | 1.1261 | 1.0483 | -0.050354 | -119.1513 | 1.0986 | 1.1536 | 1.1627 | -119.1605 | 0.98877 | 1.0117 | 1.1581 | -119.0643
3005.1406 | 120.2087 | -1.1261 | 119.2017 | -0.0022127 | 0.0037042 | 0.073858 | 0.023306 | -0.06975 | -0.028226 | -6.615e-05 | 0.014954 | 0.032383 | 0.005646 | -0.046104 | -0.0080408 | 0.013095 | 0.022888 | 0.009155 | 0.054932 | 0.073242 | 0.032043 | 0.059509 | -0.082397 | -0.032043 | 0.041199 | -0.073242 | -0.050354 | -0.036621 | 0.054932 | -0.013733 | 1.1856 | 1.0437 | -119.1696 | 1.1353 | 1.1993 | 0.15564 | -119.1788 | 1.181 | 1.1124 | -119.252 | 1.0941 | 1.0529 | -0.059509 | -119.2383 | 1.1581 | 1.149 | 1.181 | -119.2841 | 1.0757 | 1.0895 | 1.1673 | -119.2154
3006.8438 | 119.5679 | -102.4475 | 16.4429 | -0.0022127 | 0.0045588 | 0.074712 | 0.028006 | -0.070177 | -0.02609 | -0.00049335 | 0.0073242 | 0.031315 | 0.0067142 | -0.044822 | -0.0071862 | 0.012454 | 0.027466 | 0.041199 | 0.09613 | 0.09613 | 0.064087 | 0.082397 | -0.068665 | 0.018311 | 0.091553 | -0.022888 | -0.018311 | 0 | 0.10529 | 0.018311 | 102.5299 | 102.3788 | -16.3788 | 102.4887 | 102.5436 | 0.16479 | -16.4154 | 102.5528 | 102.4658 | -16.4612 | 102.4658 | 102.4246 | -0.041199 | -16.4429 | 102.5116 | 102.475 | 102.5436 | -16.5115 | 102.4292 | 102.4475 | 102.5391 | -16.4246
3008.5469 | 120.4468 | -2.7191 | 117.5262 | 0.0054168 | 0.0062676 | 0.072576 | 0.026297 | -0.070818 | -0.027371 | -0.0022024 | 0.0073242 | 0.031956 | 0.0054324 | -0.044395 | -0.0059046 | 0.012668 | 0.013733 | 0.009155 | 0.054932 | 0.068665 | 0.032043 | 0.050354 | -0.086975 | -0.018311 | 0.032043 | -0.064087 | -0.059509 | -0.036621 | 0.054932 | -0.027466 | 2.7695 | 2.6321 | -117.4942 | 2.7283 | 2.7878 | 0.15564 | -117.5125 | 2.774 | 2.6917 | -117.5858 | 2.7008 | 2.655 | -0.036621 | -117.5629 | 2.7512 | 2.7328 | 2.774 | -117.6132 | 2.6596 | 2.6825 | 2.7512 | -117.5537
3010.2812 | 88.4857 | -0.11902 | 86.2976 | 0.0054168 | -0.0037726 | 0.071294 | 0.02822 | -0.068468 | -0.021817 | -0.0024162 | 0.0073242 | 0.034733 | 0.0077822 | -0.043541 | -0.0037684 | 0.0090363 | 0.004578 | -0.064087 | -0.022888 | 0.032043 | 0.059509 | 0.004578 | -0.11444 | -0.059509 | -0.013733 | -0.17853 | -0.018311 | -0.022888 | 0.018311 | -0.032043 | 0.1236 | 0.004578 | -86.2381 | 0.054932 | 0.15106 | 0.14648 | -86.293 | 0.13733 | 0.086976 | -86.3159 | 0.05951 | -0.059509 | -0.14648 | -86.3205 | 0.17853 | 0.1236 | 0.096131 | -86.412 | 0.10071 | 0.096131 | 0.10529 | -86.3297
3011.9844 | 111.7355 | -2.4765 | 89.6027 | 0.020676 | -0.006977 | 0.065099 | 0.029715 | -0.065691 | -0.019895 | 0.0046334 | 0.0073242 | 0.035374 | 0.012055 | -0.039268 | -0.0054772 | 0.0096771 | 0.064087 | 0.013733 | 0.041199 | 0.073242 | 0.050354 | 0.018311 | -0.10986 | 0 | 0.013733 | -0.13275 | -0.013733 | -0.036621 | 0.022888 | -0.032043 | 2.4948 | 2.3666 | -89.5523 | 2.4902 | 2.5497 | 0.18311 | -89.5386 | 2.4994 | 2.4445 | -89.6164 | 2.4765 | 2.3438 | -0.10071 | -89.6393 | 2.5269 | 2.5406 | 2.5177 | -89.7125 | 2.4628 | 2.4399 | 2.4902 | -89.6347
3013.7031 | 120.3369 | -81.4133 | 40.3427 | 0.028305 | 0.0039178 | 0.070013 | 0.030569 | -0.067187 | -0.028226 | -0.0011344 | 0.0073242 | 0.031956 | 0.0097048 | -0.0429 | -0.012313 | 0.011173 | 0.10529 | 0.16937 | 0.16479 | 0.14648 | 0.045776 | 0.068665 | -0.059509 | 0.073242 | 0.16479 | 0.018311 | -0.050354 | -0.004578 | 0.10529 | 0.041199 | 81.4819 | 81.3538 | -40.2969 | 81.5826 | 81.5598 | 0.20599 | -40.2374 | 81.5186 | 81.4545 | -40.3931 | 81.4865 | 81.4316 | -0.022888 | -40.3473 | 81.459 | 81.5186 | 81.5781 | -40.4022 | 81.3629 | 81.4087 | 81.5781 | -40.3015
3015.4219 | 120.5612 | -108.6411 | 11.2793 | 0.0054168 | 0.0073358 | 0.069158 | 0.029074 | -0.069964 | -0.028867 | -0.0017752 | 0.0073242 | 0.031956 | 0.0094912 | -0.044822 | -0.0076136 | 0.012668 | 0.059509 | 0.068665 | 0.10986 | 0.14191 | 0.054932 | 0.068665 | -0.054932 | 0.045776 | 0.13275 | 0.022888 | -0.036621 | -0.018311 | 0.091553 | 0.018311 | 108.7097 | 108.5861 | -11.2244 | 108.7097 | 108.783 | 0.19684 | -11.2198 | 108.7326 | 108.6594 | -11.3159 | 108.6868 | 108.6639 | 0.004577 | -11.2976 | 108.696 | 108.7006 | 108.7509 | -11.3342 | 108.6044 | 108.6227 | 108.7738 | -11.261
3017.125 | 119.9432 | -0.14648 | 119.8883 | 0.0054168 | 0.0054132 | 0.071935 | 0.025443 | -0.066759 | -0.027158 | -0.00092075 | 0.0073242 | 0.031315 | 0.0058596 | -0.043754 | -0.0059046 | 0.012454 | 0.004578 | 0.032043 | 0.073242 | 0.07782 | 0.027466 | 0.041199 | -0.091553 | 0.004578 | 0.073242 | -0.050354 | -0.050354 | -0.050354 | 0.050354 | -0.009155 | 0.18768 | 0.054931 | -119.8608 | 0.17853 | 0.2243 | 0.16937 | -119.8837 | 0.19684 | 0.13733 | -119.9387 | 0.15106 | 0.09613 | -0.041199 | -119.9387 | 0.17395 | 0.15106 | 0.21973 | -119.9799 | 0.09613 | 0.09613 | 0.21973 | -119.8975
3018.875 | 119.9615 | -0.16479 | 119.4168 | -0.0022127 | 0.004986 | 0.071935 | 0.023947 | -0.06975 | -0.025876 | 0.00078825 | 0.0073242 | 0.031742 | 0.0060732 | -0.043327 | -0.006759 | 0.013095 | 0.022888 | 0.050354 | 0.082397 | 0.064087 | 0.013733 | 0.027466 | -0.082397 | -0.004578 | 0.059509 | -0.073242 | -0.050354 | -0.054932 | 0.045776 | -0.022888 | 0.19226 | 0.082398 | -119.4031 | 0.21515 | 0.22888 | 0.14648 | -119.3939 | 0.21057 | 0.14191 | -119.4672 | 0.16022 | 0.091553 | -0.050354 | -119.4717 | 0.17853 | 0.18768 | 0.24719 | -119.4992 | 0.11444 | 0.10986 | 0.2243 | -119.4397
3020.5938 | 119.8471 | -0.022888 | 116.1575 | 0.013046 | 0.0047724 | 0.068945 | 0.024588 | -0.068255 | -0.023313 | 0.0018564 | 0.0073242 | 0.036015 | 0.0054324 | -0.041832 | -0.0048364 | 0.0116 | 0.013733 | -0.022888 | 0.004578 | 0.064087 | 0.045776 | 0.018311 | -0.10986 | 0.027466 | 0.045776 | -0.086975 | -0.059509 | -0.036621 | 0.064087 | -0.004578 | 0.041199 | -0.086975 | -116.1118 | 0 | 0.086975 | 0.17395 | -116.1438 | 0.086975 | 0.01831 | -116.217 | 0.050354 | -0.064087 | -0.082397 | -116.1942 | 0.068664 | 0.036621 | 0.027466 | -116.2674 | -0.036621 | -0.013733 | 0.068664 | -116.1621
3022.2969 | 120.4834 | -0.17395 | 119.7739 | 0.013046 | -0.00078181 | 0.070013 | 0.024588 | -0.070818 | -0.019681 | 0.00207 | -0.0079343 | 0.03751 | 0.0082096 | -0.04055 | -0.0024866 | 0.012668 | -0.018311 | -0.082397 | -0.032043 | 0.022888 | 0.054932 | 0.018311 | -0.11902 | -0.064087 | -0.059509 | -0.15564 | -0.027466 | -0.022888 | 0.027466 | -0.032043 | 0.19226 | 0.054931 | -119.7189 | 0.091553 | 0.19684 | 0.14191 | -119.7922 | 0.20142 | 0.14191 | -119.8013 | 0.10986 | 0.01831 | -0.1236 | -119.7968 | 0.22888 | 0.15564 | 0.14191 | -119.8929 | 0.14648 | 0.15106 | 0.11444 | -119.8059
3024.0156 | 119.9844 | -0.15106 | 119.1879 | 0.0054168 | 0.0058404 | 0.074072 | 0.026511 | -0.069323 | -0.028867 | -6.615e-05 | 0.022583 | 0.030033 | 0.0052188 | -0.043327 | -0.0082544 | 0.015659 | 0.004578 | 0.027466 | 0.059509 | 0.07782 | 0.022888 | 0.022888 | -0.07782 | -0.027466 | 0.050354 | -0.068665 | -0.059509 | -0.022888 | 0.054932 | -0.018311 | 0.17395 | 0.073242 | -119.165 | 0.17853 | 0.22888 | 0.15564 | -119.1833 | 0.20599 | 0.13275 | -119.2474 | 0.1236 | 0.082397 | -0.050354 | -119.2108 | 0.17395 | 0.15564 | 0.21057 | -119.2657 | 0.091553 | 0.12817 | 0.20142 | -119.2062
3025.7188 | 89.8773 | -46.376 | 72.3495 | 0.013046 | 0.001568 | 0.067236 | 0.024374 | -0.0721 | -0.01904 | -0.00027975 | 0.0073242 | 0.036869 | 0.0058596 | -0.043968 | -0.0046228 | 0.0116 | -0.004578 | -0.054932 | -0.027466 | 0.045776 | 0.073242 | 0.027466 | -0.10986 | -0.045776 | -0.036621 | -0.14648 | 0 | 0.004578 | 0.045776 | -0.041199 | 46.4035 | 46.2662 | -72.2763 | 46.3211 | 46.4218 | 0.15564 | -72.3541 | 46.4218 | 46.3348 | -72.3495 | 46.3303 | 46.2296 | -0.10529 | -72.345 | 46.4493 | 46.3715 | 46.3486 | -72.4594 | 46.376 | 46.3806 | 46.3394 | -72.3907
3027.4531 | 119.5038 | -3.6255 | 87.6709 | 0.0054168 | -0.0048406 | 0.07044 | 0.029715 | -0.067828 | -0.023313 | -6.615e-05 | 0.014954 | 0.034092 | 0.0099186 | -0.041404 | -0.005691 | 0.012882 | -0.027466 | -0.041199 | -0.018311 | 0.045776 | 0.054932 | 0 | -0.13733 | -0.064087 | 0.013733 | -0.14648 | -0.004578 | -0.018311 | 0.013733 | -0.022888 | 3.6255 | 3.4882 | -87.616 | 3.5843 | 3.6713 | 0.18311 | -87.6984 | 3.6392 | 3.6026 | -87.6755 | 3.5614 | 3.479 | -0.1236 | -87.6892 | 3.6804 | 3.598 | 3.6072 | -87.8082 | 3.6209 | 3.6072 | 3.6392 | -87.6938
3029.1719 | 111.3785 | -21.0571 | 97.8882 | 0.020676 | 0.001568 | 0.071294 | 0.024588 | -0.071459 | -0.022885 | 0.003779 | 0.014954 | 0.035374 | 0.0077822 | -0.042259 | -0.0027002 | 0.012454 | -0.009155 | -0.041199 | -0.022888 | 0.027466 | 0.059509 | 0.027466 | -0.10986 | -0.032043 | -0.018311 | -0.11444 | -0.036621 | -0.032043 | 0.036621 | -0.022888 | 21.0846 | 20.9473 | -97.8287 | 21.0159 | 21.0846 | 0.13733 | -97.8973 | 21.0938 | 21.0342 | -97.9248 | 21.0251 | 20.9427 | -0.091553 | -97.9202 | 21.1166 | 21.048 | 21.0342 | -97.998 | 21.0205 | 21.0251 | 21.0388 | -97.9111
3030.9375 | 120.3094 | -117.3615 | 2.623 | 0.013046 | 0.00049979 | 0.070867 | 0.030356 | -0.067614 | -0.029508 | 0.00036105 | -0.0003053 | 0.033451 | 0.0094912 | -0.044181 | -0.0091088 | 0.014377 | 0.082397 | 0.13275 | 0.14648 | 0.15106 | 0.064087 | 0.10071 | -0.059509 | 0.041199 | 0.15564 | 0.009155 | -0.009155 | 0 | 0.07782 | 0.036621 | 117.4622 | 117.3019 | -2.5589 | 117.4942 | 117.5125 | 0.21057 | -2.5406 | 117.4393 | 117.3981 | -2.6321 | 117.4026 | 117.3706 | -0.027466 | -2.623 | 117.4255 | 117.4438 | 117.5079 | -2.6825 | 117.3523 | 117.3615 | 117.5171 | -2.5864
3032.6406 | 118.634 | -6.8024 | 95.3384 | 0.0054168 | -0.0027044 | 0.069799 | 0.025443 | -0.067187 | -0.017758 | 0.0010018 | 0.014954 | 0.034306 | 0.009064 | -0.0429 | -0.0061182 | 0.012027 | -0.036621 | -0.086975 | -0.027466 | 0.018311 | 0.064087 | 0.009155 | -0.11444 | -0.07782 | -0.054932 | -0.17853 | -0.027466 | -0.009155 | 0.032043 | -0.045776 | 6.8115 | 6.6879 | -95.2744 | 6.7154 | 6.8207 | 0.13275 | -95.3751 | 6.8344 | 6.7566 | -95.3659 | 6.7245 | 6.6238 | -0.13275 | -95.3476 | 6.8665 | 6.7657 | 6.7749 | -95.4529 | 6.7749 | 6.7932 | 6.7474 | -95.3842
3034.3594 | 94.6335 | -0.32959 | 85.5606 | 0.020676 | -0.005268 | 0.069372 | 0.029288 | -0.067614 | -0.023099 | -0.0019888 | 0.0073242 | 0.034519 | 0.0099186 | -0.042472 | -0.006759 | 0.012027 | -0.045776 | -0.059509 | -0.013733 | 0.045776 | 0.064087 | 0 | -0.13733 | -0.054932 | 0 | -0.14191 | -0.009155 | -0.022888 | 0.032043 | -0.045776 | 0.32959 | 0.19226 | -85.4965 | 0.27008 | 0.37537 | 0.18311 | -85.6064 | 0.36163 | 0.28381 | -85.5698 | 0.27466 | 0.18768 | -0.096131 | -85.5835 | 0.39368 | 0.28381 | 0.31586 | -85.6979 | 0.32043 | 0.3067 | 0.32959 | -85.6064
3036.0781 | 120.0989 | -7.4249 | 111.9141 | 0.013046 | 0.003277 | 0.07044 | 0.024802 | -0.070177 | -0.028012 | -6.615e-05 | 0.014954 | 0.031529 | 0.0069278 | -0.042686 | -0.006759 | 0.015872 | 0.050354 | 0.07782 | 0.10529 | 0.086975 | 0.013733 | 0.045776 | -0.068665 | 0.018311 | 0.07782 | -0.032043 | -0.07782 | -0.041199 | 0.054932 | -0.004578 | 7.4707 | 7.3563 | -111.9003 | 7.5027 | 7.5119 | 0.15564 | -111.8637 | 7.4799 | 7.4203 | -111.9919 | 7.4432 | 7.3929 | -0.027465 | -111.9553 | 7.4387 | 7.4753 | 7.5302 | -111.9827 | 7.3471 | 7.3837 | 7.5027 | -111.9186
3037.7812 | 120.5933 | -6.752 | 112.9074 | 0.0054168 | 0.0013544 | 0.070013 | 0.023734 | -0.068041 | -0.023313 | 0.0016428 | 0.0073242 | 0.036656 | 0.0086368 | -0.042686 | -0.0018458 | 0.010532 | -0.022888 | -0.082397 | -0.050354 | 0.022888 | 0.050354 | 0.004578 | -0.11902 | -0.064087 | -0.054932 | -0.15106 | -0.013733 | -0.004578 | 0.022888 | -0.036621 | 6.7566 | 6.633 | -112.8571 | 6.6696 | 6.7749 | 0.14191 | -112.9303 | 6.7749 | 6.7154 | -112.9211 | 6.6879 | 6.601 | -0.11444 | -112.912 | 6.8024 | 6.7291 | 6.7017 | -113.0264 | 6.7383 | 6.7474 | 6.6971 | -112.944
3039.5 | 119.5862 | -35.0601 | 84.3658 | 0.0054168 | 0.0026362 | 0.069372 | 0.030783 | -0.0674 | -0.026303 | -0.0028434 | 0.0073242 | 0.030888 | 0.0088504 | -0.045036 | -0.0069726 | 0.01395 | -0.032043 | -0.018311 | 0.009155 | 0.045776 | 0.068665 | 0.013733 | -0.11444 | -0.086975 | 0.013733 | -0.11444 | -0.004578 | 0.004578 | 0.022888 | -0.027466 | 35.0739 | 34.9457 | -84.2972 | 35.0418 | 35.1059 | 0.16022 | -84.3979 | 35.083 | 35.0327 | -84.3704 | 34.9731 | 34.9457 | -0.086975 | -84.3613 | 35.1288 | 35.0281 | 35.0693 | -84.4803 | 35.0555 | 35.0647 | 35.0739 | -84.3933
3041.2344 | 120.2774 | -20.1828 | 99.8016 | 0.0054168 | 0.006054 | 0.072363 | 0.02822 | -0.068041 | -0.030576 | -0.0011344 | 0.0073242 | 0.030674 | 0.0065006 | -0.044181 | -0.0091088 | 0.01395 | 0.004578 | 0.045776 | 0.091553 | 0.091553 | 0.022888 | 0.036621 | -0.073242 | -0.013733 | 0.091553 | -0.018311 | -0.045776 | -0.022888 | 0.059509 | 0.004578 | 20.2194 | 20.1096 | -99.7787 | 20.2286 | 20.2744 | 0.16479 | -99.7971 | 20.2423 | 20.1874 | -99.8474 | 20.1691 | 20.1645 | -0.022889 | -99.8245 | 20.2057 | 20.1874 | 20.2744 | -99.8749 | 20.137 | 20.1599 | 20.2744 | -99.7971
3042.9844 | 120.3506 | -39.6194 | 80.3696 | 0.013046 | 0.0062676 | 0.073003 | 0.024802 | -0.067614 | -0.026303 | -0.0019888 | -0.0003053 | 0.031956 | 0.003937 | -0.043754 | -0.0046228 | 0.012027 | 0.073242 | 0.10071 | 0.11902 | 0.11902 | 0.022888 | 0.050354 | -0.045776 | 0.045776 | 0.11902 | -0.022888 | -0.054932 | -0.036621 | 0.068665 | 0.018311 | 39.6698 | 39.5737 | -80.3467 | 39.7202 | 39.7385 | 0.16479 | -80.2963 | 39.6881 | 39.6378 | -80.4245 | 39.6652 | 39.5966 | -0.041199 | -80.4062 | 39.6423 | 39.6927 | 39.7385 | -80.4153 | 39.5645 | 39.5828 | 39.7385 | -80.3513
3044.6875 | 115.0726 | -24.4492 | 95.7916 | -0.0022127 | -0.00099541 | 0.071081 | 0.030783 | -0.065264 | -0.024808 | -0.001348 | 0.014954 | 0.030888 | 0.0082096 | -0.043754 | -0.0091088 | 0.012241 | 0.064087 | 0.073242 | 0.11902 | 0.1236 | 0.036621 | 0.064087 | -0.07782 | -0.013733 | 0.073242 | -0.045776 | -0.041199 | -0.004578 | 0.050354 | -0.022888 | 24.5132 | 24.3713 | -95.755 | 24.5224 | 24.5728 | 0.20142 | -95.7275 | 24.4995 | 24.4263 | -95.8328 | 24.4354 | 24.4034 | -0.022888 | -95.7962 | 24.4858 | 24.5132 | 24.5682 | -95.8694 | 24.408 | 24.4446 | 24.5224 | -95.8145
3046.4062 | 105.8441 | -22.9477 | 97.1512 | 0.013046 | -0.003559 | 0.067022 | 0.026511 | -0.066332 | -0.019895 | -0.00092075 | 0.0073242 | 0.034947 | 0.010132 | -0.0429 | -0.0035546 | 0.010318 | 0.064087 | 0.022888 | 0.045776 | 0.073242 | 0.054932 | 0.027466 | -0.10529 | 0 | 0.041199 | -0.11444 | -0.032043 | -0.027466 | 0.041199 | -0.018311 | 22.9752 | 22.8424 | -97.0963 | 22.9706 | 23.0209 | 0.17853 | -97.0871 | 22.9889 | 22.9294 | -97.1832 | 22.9477 | 22.8333 | -0.09613 | -97.1787 | 23.0026 | 23.0118 | 22.9935 | -97.2565 | 22.9156 | 22.9202 | 22.9889 | -97.1695
3048.1094 | 120.1996 | -6.4178 | 113.1088 | 0.0054168 | -0.0020636 | 0.068517 | 0.029074 | -0.066759 | -0.020749 | 0.00207 | 0.014954 | 0.036228 | 0.0077822 | -0.042045 | -0.0046228 | 0.012882 | 0.022888 | 0.032043 | 0.041199 | 0.064087 | 0.050354 | 0.022888 | -0.10529 | -0.004578 | 0.032043 | -0.11902 | -0.032043 | -0.009155 | 0.032043 | -0.022888 | 6.4407 | 6.3126 | -113.0585 | 6.4499 | 6.4819 | 0.16937 | -113.0859 | 6.4499 | 6.395 | -113.1409 | 6.4133 | 6.2988 | -0.096131 | -113.118 | 6.4682 | 6.4407 | 6.459 | -113.2141 | 6.3858 | 6.4087 | 6.4499 | -113.1317
3049.875 | 120.5063 | -5.983 | 114.1205 | 0.013046 | -0.00014101 | 0.072576 | 0.03121 | -0.068468 | -0.029721 | 0.0016428 | 0.0073242 | 0.030033 | 0.007996 | -0.043754 | -0.0086816 | 0.014163 | 0.050354 | 0.13275 | 0.12817 | 0.1236 | 0.022888 | 0.036621 | -0.086975 | 0.027466 | 0.14191 | 0.004578 | -0.064087 | -0.045776 | 0.054932 | 0.009155 | 6.0196 | 5.896 | -114.0976 | 6.1157 | 6.1066 | 0.21057 | -114.0701 | 6.0379 | 5.9921 | -114.1846 | 6.0104 | 5.9875 | -0.004577 | -114.1663 | 6.0059 | 6.0333 | 6.1111 | -114.2075 | 5.9189 | 5.9372 | 6.1249 | -114.1113
3051.5781 | 119.9799 | -6.4407 | 113.9053 | 0.0054168 | -0.0014228 | 0.067449 | 0.029288 | -0.066546 | -0.022031 | 0.0012154 | 0.014954 | 0.033665 | 0.010559 | -0.040763 | -0.005691 | 0.0092499 | 0.004578 | 0 | 0.032043 | 0.064087 | 0.059509 | 0 | -0.11902 | -0.013733 | 0.027466 | -0.1236 | -0.036621 | -0.004578 | 0.022888 | -0.027466 | 6.4407 | 6.3217 | -113.8458 | 6.4407 | 6.5048 | 0.18311 | -113.9008 | 6.4636 | 6.4133 | -113.942 | 6.427 | 6.3171 | -0.09613 | -113.9099 | 6.5002 | 6.4453 | 6.4728 | -114.0244 | 6.4041 | 6.4362 | 6.4682 | -113.9328
3053.2969 | 120.5933 | -4.7012 | 115.2054 | 0.0054168 | 0.0026362 | 0.070654 | 0.023947 | -0.069964 | -0.023526 | 0.0012154 | 0.014954 | 0.034092 | 0.0077822 | -0.041618 | -0.0059046 | 0.010959 | 0.032043 | 0.036621 | 0.068665 | 0.082397 | 0.036621 | 0.027466 | -0.068665 | 0.045776 | 0.082397 | -0.022888 | -0.064087 | -0.045776 | 0.054932 | -0.004578 | 4.7287 | 4.6326 | -115.1688 | 4.7379 | 4.7836 | 0.15106 | -115.1733 | 4.7562 | 4.6967 | -115.2695 | 4.747 | 4.6783 | -0.01831 | -115.2512 | 4.7379 | 4.7333 | 4.7699 | -115.274 | 4.6371 | 4.6555 | 4.7836 | -115.21
3055.0156 | 120.6253 | -38.7589 | 81.3812 | 0.0054168 | 0.0037042 | 0.071935 | 0.029715 | -0.06975 | -0.029721 | 0.00057465 | 0.014954 | 0.030461 | 0.0067142 | -0.041191 | -0.0091088 | 0.013736 | 0.059509 | 0.11444 | 0.14191 | 0.10529 | 0.018311 | 0.059509 | -0.086975 | 0.041199 | 0.16022 | 0.027466 | -0.068665 | -0.054932 | 0.054932 | -0.013733 | 38.8184 | 38.6719 | -81.3629 | 38.8733 | 38.8641 | 0.19226 | -81.3217 | 38.8138 | 38.7451 | -81.4499 | 38.8 | 38.7863 | 0.041199 | -81.4362 | 38.7772 | 38.8184 | 38.9008 | -81.4682 | 38.6902 | 38.7039 | 38.9191 | -81.395
3056.7344 | 120.5978 | -3.4607 | 117.009 | 0.013046 | 0.0017816 | 0.070013 | 0.025229 | -0.067828 | -0.020322 | -0.00027975 | 0.014954 | 0.034092 | 0.009064 | -0.042686 | -0.003341 | 0.0094635 | -0.041199 | -0.073242 | -0.032043 | 0.027466 | 0.054932 | 0.009155 | -0.1236 | -0.07782 | -0.045776 | -0.17395 | -0.027466 | -0.004578 | 0.013733 | -0.045776 | 3.4698 | 3.3371 | -116.954 | 3.3875 | 3.4882 | 0.15106 | -117.0502 | 3.4744 | 3.4149 | -117.0364 | 3.3829 | 3.2867 | -0.12817 | -117.0135 | 3.5156 | 3.4195 | 3.4287 | -117.1326 | 3.4332 | 3.4561 | 3.4149 | -117.0547
3058.4844 | 120.0623 | -119.6457 | 0.064087 | 0.013046 | 0.0054132 | 0.068945 | 0.025443 | -0.068682 | -0.023953 | 0.0018564 | 0.022583 | 0.031742 | 0.0058596 | -0.044181 | -0.0059046 | 0.0116 | 0.07782 | 0.11902 | 0.11444 | 0.13275 | 0.045776 | 0.10529 | -0.041199 | 0.091553 | 0.15106 | 0.004578 | -0.013733 | 0 | 0.11444 | 0.036621 | 119.751 | 119.6045 | -0.018311 | 119.7647 | 119.7784 | 0.17395 | 0.013733 | 119.7601 | 119.6823 | -0.07782 | 119.7372 | 119.6503 | -0.032043 | -0.064087 | 119.6915 | 119.7235 | 119.7601 | -0.10529 | 119.632 | 119.6457 | 119.7968 | -0.027466
3060.1875 | 120.4422 | -120.0531 | 0.064087 | 0.0054168 | 0.0037042 | 0.070226 | 0.026724 | -0.069109 | -0.024167 | -6.615e-05 | -0.0003053 | 0.033451 | 0.0050052 | -0.04525 | -0.0052636 | 0.013095 | 0.086975 | 0.11902 | 0.12817 | 0.16022 | 0.041199 | 0.091553 | -0.013733 | 0.086975 | 0.14191 | 0.004578 | -0.022888 | -0.009155 | 0.10071 | 0.059509 | 120.1447 | 120.0394 | -0.022888 | 120.1721 | 120.2133 | 0.17395 | 0.022888 | 120.1538 | 120.1126 | -0.086975 | 120.1401 | 120.0577 | -0.054931 | -0.073242 | 120.0943 | 120.1401 | 120.1813 | -0.07782 | 120.0302 | 120.0439 | 120.195 | -0.004578
3061.9375 | 120.5246 | -120.2042 | 0.10071 | 0.020676 | 0.004345 | 0.075567 | 0.029715 | -0.069323 | -0.029721 | -6.615e-05 | 0.022583 | 0.030033 | 0.0069278 | -0.042472 | -0.0088952 | 0.013736 | 0.045776 | 0.064087 | 0.11444 | 0.10071 | 0.068665 | 0.09613 | -0.064087 | 0.018311 | 0.07782 | -0.018311 | -0.027466 | -0.022888 | 0.09613 | 0.027466 | 120.3003 | 120.1401 | -0.032043 | 120.2682 | 120.3049 | 0.1648 | -0.054932 | 120.3003 | 120.2316 | -0.12817 | 120.2225 | 120.1859 | -0.045777 | -0.1236 | 120.2728 | 120.2499 | 120.3186 | -0.1648 | 120.1767 | 120.1813 | 120.282 | -0.073242
3063.6875 | 120.4193 | -120.195 | 0.21515 | 0.0054168 | 7.2586e-05 | 0.073858 | 0.029501 | -0.068896 | -0.025876 | -0.001348 | -0.0003053 | 0.031101 | 0.0084232 | -0.046531 | -0.0082544 | 0.0116 | 0.09613 | 0.1236 | 0.14648 | 0.16022 | 0.054932 | 0.068665 | -0.054932 | 0.050354 | 0.15106 | -0.004578 | -0.013733 | -0.004578 | 0.082397 | 0.032043 | 120.2637 | 120.1401 | -0.16022 | 120.3186 | 120.3552 | 0.21515 | -0.11902 | 120.2774 | 120.2271 | -0.22888 | 120.2454 | 120.1904 | -0.036621 | -0.21973 | 120.2499 | 120.2911 | 120.3415 | -0.27008 | 120.1813 | 120.1904 | 120.3461 | -0.18311
3065.4062 | 119.9158 | -119.4122 | 0.10529 | 0.013046 | 0.0026362 | 0.070867 | 0.032278 | -0.070818 | -0.028226 | -0.0032706 | 0.0073242 | 0.030461 | 0.0086368 | -0.045036 | -0.010391 | 0.011386 | 0.11444 | 0.16022 | 0.17853 | 0.16937 | 0.059509 | 0.082397 | -0.032043 | 0.082397 | 0.17853 | 0.045776 | -0.036621 | 0 | 0.07782 | 0.050354 | 119.4946 | 119.3802 | -0.045777 | 119.5724 | 119.5816 | 0.20142 | 0.009155 | 119.4901 | 119.4626 | -0.14191 | 119.4946 | 119.458 | -0.004578 | -0.10529 | 119.4717 | 119.5267 | 119.5908 | -0.13733 | 119.3756 | 119.4122 | 119.5908 | -0.054932
3067.1094 | 120.0714 | -119.6503 | 0.20142 | 0.0054168 | 0.0019952 | 0.071081 | 0.029288 | -0.068896 | -0.025022 | -0.00049335 | 0.014954 | 0.02982 | 0.0088504 | -0.043754 | -0.0099634 | 0.012454 | 0.10529 | 0.15106 | 0.16479 | 0.14648 | 0.059509 | 0.086975 | -0.050354 | 0.086975 | 0.16937 | 0.045776 | -0.032043 | -0.013733 | 0.09613 | 0.041199 | 119.7372 | 119.5999 | -0.14191 | 119.8013 | 119.7968 | 0.19684 | -0.09613 | 119.7464 | 119.6915 | -0.23346 | 119.7372 | 119.696 | 0.004577 | -0.21515 | 119.7098 | 119.7556 | 119.8151 | -0.25177 | 119.6182 | 119.6365 | 119.8196 | -0.16022
3068.875 | 119.8975 | -119.4901 | 0.068665 | 0.0054168 | 0.004345 | 0.07044 | 0.023947 | -0.068468 | -0.023526 | 0.00057465 | 0.0073242 | 0.030674 | 0.007355 | -0.041618 | -0.003341 | 0.0116 | 0.12817 | 0.12817 | 0.16022 | 0.16022 | 0.045776 | 0.086975 | -0.036621 | 0.1236 | 0.13275 | 0.009155 | -0.036621 | -0.018311 | 0.10071 | 0.036621 | 119.577 | 119.4534 | -0.022889 | 119.6182 | 119.6503 | 0.19684 | 0.059509 | 119.5908 | 119.5267 | -0.10529 | 119.6136 | 119.4992 | -0.027466 | -0.086976 | 119.5358 | 119.6182 | 119.6503 | -0.10529 | 119.4534 | 119.4717 | 119.6228 | -0.032044
3070.5781 | 120.2911 | -119.9341 | 0.091553 | 0.028305 | 0.0013544 | 0.071935 | 0.029074 | -0.069323 | -0.026731 | -0.00070715 | 0.0073242 | 0.030888 | 0.007996 | -0.043541 | -0.008468 | 0.010104 | 0.12817 | 0.17395 | 0.17395 | 0.16022 | 0.068665 | 0.10529 | -0.041199 | 0.091553 | 0.17853 | 0.036621 | -0.027466 | -0.013733 | 0.09613 | 0.032043 | 120.0394 | 119.8929 | -0.022888 | 120.108 | 120.0943 | 0.20142 | 0.036621 | 120.0302 | 119.9661 | -0.11902 | 120.0256 | 119.9707 | 0.004578 | -0.10529 | 120.0027 | 120.0623 | 120.108 | -0.13275 | 119.9066 | 119.9203 | 120.1126 | -0.05951
3072.2812 | 120.2866 | -120.0485 | 0.15106 | 0.013046 | -0.0024908 | 0.070226 | 0.027792 | -0.068682 | -0.022244 | -0.00049335 | 0.0073242 | 0.034519 | 0.0084232 | -0.043113 | -0.0063318 | 0.011813 | 0.018311 | -0.009155 | 0.022888 | 0.068665 | 0.10529 | 0.032043 | -0.082397 | -0.036621 | 0.022888 | -0.1236 | 0.009155 | 0.036621 | 0.059509 | -0.009155 | 120.0806 | 119.9661 | -0.045776 | 120.0394 | 120.1172 | 0.15106 | -0.13275 | 120.108 | 120.0394 | -0.14191 | 120.0119 | 119.9249 | -0.11444 | -0.11444 | 120.1538 | 120.0668 | 120.0714 | -0.23346 | 120.0577 | 120.0851 | 120.0714 | -0.16022
3074 | 120.3781 | -120.0668 | 0.059509 | 0.0054168 | 0.001568 | 0.072149 | 0.025656 | -0.067187 | -0.020322 | 0.00036105 | 0.014954 | 0.034947 | 0.009064 | -0.043113 | -0.0020594 | 0.011386 | 0.022888 | -0.009155 | 0.018311 | 0.068665 | 0.10986 | 0.068665 | -0.082397 | -0.004578 | 0.009155 | -0.10986 | 0 | 0.018311 | 0.064087 | 0.009155 | 120.1355 | 119.9844 | 0.050354 | 120.0577 | 120.1355 | 0.15106 | -0.036621 | 120.1309 | 120.076 | -0.059509 | 120.0623 | 119.957 | -0.11902 | -0.041198 | 120.1767 | 120.0897 | 120.0851 | -0.14191 | 120.0668 | 120.0851 | 120.076 | -0.050354
3075.7344 | 120.4285 | -119.8837 | 0.27924 | 0.013046 | 0.0026362 | 0.070226 | 0.02587 | -0.069537 | -0.022672 | 0.003138 | 0.0073242 | 0.033665 | 0.0058596 | -0.045036 | -0.003341 | 0.014377 | 0.050354 | 0.036621 | 0.064087 | 0.10071 | 0.082397 | 0.054932 | -0.064087 | 0.064087 | 0.086975 | -0.022888 | -0.027466 | 0.004578 | 0.10529 | 0.032043 | 119.9387 | 119.8196 | -0.19684 | 119.9203 | 119.9844 | 0.1648 | -0.22888 | 119.989 | 119.9158 | -0.3067 | 119.9478 | 119.8608 | -0.054931 | -0.27466 | 119.9661 | 119.9341 | 119.9478 | -0.34332 | 119.8563 | 119.8883 | 119.9707 | -0.24719
3077.6562 | 119.165 | -118.6615 | 0.19684 | 0.013046 | 0.0041314 | 0.069372 | 0.023093 | -0.069109 | -0.024808 | 0.0018564 | 0.014954 | 0.033024 | 0.0069278 | -0.0429 | -0.0048364 | 0.0116 | 0.1236 | 0.12817 | 0.16022 | 0.15564 | 0.054932 | 0.086975 | -0.032043 | 0.10071 | 0.13733 | 0.018311 | -0.041199 | -0.004578 | 0.10529 | 0.045776 | 118.7485 | 118.6295 | -0.14191 | 118.7897 | 118.8171 | 0.18768 | -0.073242 | 118.7668 | 118.7073 | -0.23804 | 118.7622 | 118.6798 | -0.027465 | -0.20142 | 118.7164 | 118.7851 | 118.8217 | -0.22888 | 118.6203 | 118.6569 | 118.7988 | -0.15106
3079.5 | 120.3415 | -120.0943 | 0.091553 | 0.0054168 | -0.0014228 | 0.073003 | 0.026297 | -0.069323 | -0.025449 | 0.0018564 | 0.0073242 | 0.034733 | 0.0077822 | -0.043754 | -0.006759 | 0.013522 | 0.013733 | -0.004578 | 0.009155 | 0.064087 | 0.10071 | 0.036621 | -0.07782 | -0.032043 | 0.036621 | -0.11902 | 0.022888 | 0.032043 | 0.045776 | -0.004578 | 120.1309 | 120.0165 | 0.009155 | 120.0897 | 120.1584 | 0.14191 | -0.07782 | 120.1401 | 120.0897 | -0.068665 | 120.0623 | 119.9753 | -0.11444 | -0.05951 | 120.195 | 120.108 | 120.1035 | -0.16937 | 120.1172 | 120.1263 | 120.1309 | -0.096131
3081.2344 | 120.488 | -120.1538 | 0.07782 | 0.020676 | 0.0041314 | 0.070867 | 0.026511 | -0.067614 | -0.023099 | 0.0012154 | 0.014954 | 0.033238 | 0.007355 | -0.043541 | -0.0069726 | 0.012668 | 0.050354 | 0.054932 | 0.068665 | 0.11444 | 0.073242 | 0.068665 | -0.050354 | 0.064087 | 0.091553 | -0.013733 | -0.032043 | 0 | 0.11444 | 0.036621 | 120.2225 | 120.1035 | -0.004578 | 120.2087 | 120.2682 | 0.16479 | -0.027466 | 120.2682 | 120.1904 | -0.10986 | 120.2179 | 120.1401 | -0.050354 | -0.07782 | 120.2271 | 120.2042 | 120.2225 | -0.12817 | 120.1218 | 120.1538 | 120.2454 | -0.041199
3083.0156 | 120.5109 | -120.2179 | 0.091553 | 0.013046 | 0.0073358 | 0.074072 | 0.026938 | -0.067614 | -0.027371 | 0.00078825 | 0.014954 | 0.030033 | 0.007355 | -0.04589 | -0.0059046 | 0.016727 | 0.07782 | 0.11902 | 0.13275 | 0.11902 | 0.041199 | 0.091553 | -0.018311 | 0.041199 | 0.10986 | -0.004578 | -0.027466 | -0.018311 | 0.073242 | 0.018311 | 120.3094 | 120.1996 | -0.050354 | 120.3369 | 120.3369 | 0.13733 | -0.013733 | 120.2911 | 120.2362 | -0.11902 | 120.2591 | 120.2133 | -0.022889 | -0.10986 | 120.2591 | 120.2957 | 120.3506 | -0.10986 | 120.1904 | 120.1996 | 120.3278 | -0.073242
3084.8125 | 120.4376 | -120.2957 | 0.10529 | 0.020676 | -0.00056821 | 0.070226 | 0.029929 | -0.066332 | -0.021817 | -0.0011344 | 0.014954 | 0.036228 | 0.0092776 | -0.042045 | -0.0052636 | 0.012027 | 0.018311 | -0.018311 | 0.018311 | 0.086975 | 0.086975 | 0.050354 | -0.091553 | 0 | 0.050354 | -0.10071 | 0.013733 | 0.036621 | 0.073242 | -0.009155 | 120.3461 | 120.2042 | -0.018311 | 120.2774 | 120.3827 | 0.17853 | -0.086975 | 120.369 | 120.2866 | -0.091553 | 120.2957 | 120.195 | -0.091553 | -0.068665 | 120.3827 | 120.314 | 120.314 | -0.19684 | 120.3094 | 120.3323 | 120.3461 | -0.11444
3086.625 | 120.5475 | -120.3186 | 0.07782 | 0.0054168 | 0.0026362 | 0.067876 | 0.026083 | -0.067614 | -0.022458 | 0.0014292 | 0.0073242 | 0.032597 | 0.0088504 | -0.042045 | -0.0059046 | 0.013309 | 0.004578 | -0.032043 | 0.004578 | 0.068665 | 0.086975 | 0.068665 | -0.068665 | -0.022888 | 0 | -0.11444 | 0.022888 | 0.018311 | 0.073242 | 0.013733 | 120.3873 | 120.2499 | 0.009155 | 120.2866 | 120.3873 | 0.13733 | -0.073242 | 120.3918 | 120.3323 | -0.054932 | 120.2957 | 120.2042 | -0.12817 | -0.059509 | 120.4056 | 120.3232 | 120.3232 | -0.14649 | 120.3415 | 120.3369 | 120.3186 | -0.064087
3088.3438 | 120.6299 | -120.3278 | 0.050354 | 0.0054168 | 0.0024224 | 0.069799 | 0.022665 | -0.069323 | -0.024808 | 0.00014745 | 0.0073242 | 0.033451 | 0.0058596 | -0.043968 | -0.0044092 | 0.013095 | 0.059509 | 0.045776 | 0.091553 | 0.10986 | 0.073242 | 0.07782 | -0.054932 | 0.073242 | 0.10986 | -0.009155 | -0.022888 | -0.004578 | 0.10529 | 0.054932 | 120.4056 | 120.2728 | 0.022888 | 120.3735 | 120.4376 | 0.16479 | 0.009155 | 120.433 | 120.3827 | -0.073242 | 120.401 | 120.3186 | -0.064087 | -0.054932 | 120.401 | 120.3873 | 120.4193 | -0.10529 | 120.3049 | 120.3232 | 120.4376 | 0.004578
3090.125 | 120.5841 | -120.3918 | 0.09613 | 0.0054168 | -0.002918 | 0.070013 | 0.027792 | -0.069109 | -0.020108 | -0.00070715 | 0.014954 | 0.035374 | 0.0094912 | -0.043327 | -0.0061182 | 0.012454 | 0.050354 | 0.036621 | 0.050354 | 0.10986 | 0.10529 | 0.054932 | -0.082397 | 0.018311 | 0.07782 | -0.073242 | 0.009155 | 0.041199 | 0.059509 | 0.013733 | 120.4468 | 120.3094 | 0.009156 | 120.4285 | 120.5017 | 0.19226 | -0.045776 | 120.4514 | 120.4056 | -0.086975 | 120.4102 | 120.3186 | -0.086975 | -0.054931 | 120.4971 | 120.4422 | 120.4422 | -0.17853 | 120.401 | 120.433 | 120.4697 | -0.082397
3091.9062 | 120.6162 | -120.433 | 0.068665 | 0.013046 | -0.00099541 | 0.071081 | 0.031851 | -0.067828 | -0.030362 | -0.00027975 | 0.014954 | 0.031315 | 0.012268 | -0.044395 | -0.0097498 | 0.014591 | 0.082397 | 0.14191 | 0.17395 | 0.16022 | 0.045776 | 0.082397 | -0.050354 | 0.073242 | 0.16937 | 0.027466 | -0.045776 | -0.004578 | 0.10529 | 0.041199 | 120.5154 | 120.3827 | -0.022889 | 120.575 | 120.5933 | 0.21057 | 0.013732 | 120.5383 | 120.4742 | -0.11444 | 120.5063 | 120.4605 | -0.013733 | -0.073243 | 120.4788 | 120.5154 | 120.607 | -0.11902 | 120.3873 | 120.4285 | 120.6024 | -0.027466
3093.6406 | 120.5841 | -120.4422 | 0.07782 | 0.0054168 | 0.00049979 | 0.068304 | 0.026511 | -0.0674 | -0.021604 | -6.615e-05 | 0.0073242 | 0.036656 | 0.0094912 | -0.040123 | -0.0052636 | 0.013522 | -0.027466 | -0.064087 | -0.009155 | 0.064087 | 0.10529 | 0.050354 | -0.086975 | -0.036621 | -0.013733 | -0.14648 | 0.018311 | 0.022888 | 0.054932 | -0.004578 | 120.4926 | 120.3552 | 0.027466 | 120.3781 | 120.5063 | 0.15106 | -0.10529 | 120.4971 | 120.4376 | -0.059509 | 120.4056 | 120.2957 | -0.14191 | -0.054932 | 120.5475 | 120.4147 | 120.433 | -0.16479 | 120.4605 | 120.4651 | 120.4285 | -0.082398
3095.3906 | 120.6024 | -120.488 | 0.10529 | 0.0054168 | -0.0031318 | 0.07044 | 0.025656 | -0.068896 | -0.022244 | 0.0018564 | 0.0073242 | 0.036015 | 0.0086368 | -0.042259 | -0.0054772 | 0.013736 | 0.018311 | 0.004578 | 0.027466 | 0.07782 | 0.082397 | 0.050354 | -0.059509 | -0.018311 | 0.009155 | -0.13275 | 0.004578 | 0.036621 | 0.073242 | 0.009155 | 120.5383 | 120.4285 | -0.022889 | 120.4926 | 120.5658 | 0.13733 | -0.086975 | 120.5612 | 120.4971 | -0.10071 | 120.4697 | 120.3552 | -0.14191 | -0.068665 | 120.5704 | 120.5063 | 120.5154 | -0.16479 | 120.4926 | 120.5246 | 120.4971 | -0.096131
3097.1875 | 120.6162 | -120.5154 | 0.10986 | 0.013046 | 0.00071339 | 0.073858 | 0.027365 | -0.065691 | -0.028653 | -0.00092075 | 0.014954 | 0.029606 | 0.0069278 | -0.044395 | -0.0080408 | 0.013095 | 0.068665 | 0.1236 | 0.16479 | 0.15564 | 0.054932 | 0.073242 | -0.036621 | 0.054932 | 0.15564 | -0.004578 | -0.013733 | 0.009155 | 0.086975 | 0.032043 | 120.5887 | 120.4788 | -0.054931 | 120.639 | 120.6711 | 0.19226 | -0.041198 | 120.6024 | 120.5475 | -0.1236 | 120.5704 | 120.5109 | -0.036621 | -0.10071 | 120.5704 | 120.5841 | 120.6802 | -0.14648 | 120.5017 | 120.5246 | 120.6711 | -0.07782
3098.9688 | 120.7535 | -120.4834 | 0.082397 | 0.013046 | 0.0054132 | 0.073217 | 0.027792 | -0.067614 | -0.02844 | -0.0017752 | 0.0073242 | 0.030888 | 0.0065006 | -0.043327 | -0.0080408 | 0.01395 | 0.027466 | 0.054932 | 0.09613 | 0.11444 | 0.059509 | 0.082397 | -0.041199 | -0.004578 | 0.07782 | -0.018311 | -0.022888 | 0.004578 | 0.09613 | 0.022888 | 120.5658 | 120.4422 | -0.022888 | 120.5383 | 120.5978 | 0.15564 | -0.054931 | 120.5795 | 120.5063 | -0.10528 | 120.4788 | 120.4651 | -0.041199 | -0.077819 | 120.5429 | 120.5109 | 120.5795 | -0.1236 | 120.4605 | 120.488 | 120.5612 | -0.059509
3100.7031 | 120.7993 | -120.5109 | 0.073242 | 0.013046 | 0.0051996 | 0.073858 | 0.029929 | -0.067187 | -0.027799 | -0.0028434 | 0.014954 | 0.031101 | 0.0071414 | -0.044395 | -0.0063318 | 0.011813 | 0.10986 | 0.14191 | 0.16022 | 0.15564 | 0.064087 | 0.082397 | -0.045776 | 0.073242 | 0.15564 | 0.045776 | -0.013733 | -0.027466 | 0.091553 | 0.032043 | 120.5933 | 120.4651 | -0.009155 | 120.6528 | 120.6665 | 0.20142 | 0.036621 | 120.6024 | 120.5429 | -0.086975 | 120.5841 | 120.5566 | 0.013733 | -0.10071 | 120.575 | 120.6207 | 120.6711 | -0.11902 | 120.4971 | 120.4834 | 120.6665 | -0.041199
3102.5156 | 120.8084 | -120.5063 | 0.064087 | 0.0054168 | 0.0028498 | 0.071294 | 0.029074 | -0.071673 | -0.026944 | -0.0026298 | 0.014954 | 0.02982 | 0.006287 | -0.04589 | -0.006759 | 0.012241 | 0.045776 | 0.091553 | 0.11902 | 0.11902 | 0.07782 | 0.082397 | -0.036621 | 0.036621 | 0.11902 | 0.009155 | -0.027466 | 0 | 0.091553 | 0.036621 | 120.5887 | 120.4697 | 0.013733 | 120.5978 | 120.6253 | 0.15564 | -0.018311 | 120.5978 | 120.5429 | -0.091553 | 120.5429 | 120.5154 | -0.027466 | -0.064087 | 120.5841 | 120.5521 | 120.6253 | -0.10071 | 120.4788 | 120.5063 | 120.6253 | -0.027466
3104.25 | 120.7214 | -120.575 | 0.10529 | 0.013046 | -0.00185 | 0.070013 | 0.033987 | -0.067828 | -0.022672 | -0.0019888 | 0.014954 | 0.033238 | 0.010773 | -0.041404 | -0.008468 | 0.0086091 | 0.022888 | 0.004578 | 0.041199 | 0.073242 | 0.10071 | 0.050354 | -0.082397 | -0.036621 | 0.004578 | -0.10071 | 0.027466 | 0.041199 | 0.059509 | -0.004578 | 120.6253 | 120.4926 | -0.004578 | 120.5795 | 120.6482 | 0.15564 | -0.082398 | 120.6345 | 120.5704 | -0.07782 | 120.5383 | 120.4742 | -0.09613 | -0.064087 | 120.6757 | 120.5978 | 120.6162 | -0.18768 | 120.6024 | 120.6162 | 120.5795 | -0.10986
3105.9688 | 120.7031 | -120.5933 | 0.09613 | 0.013046 | -0.0044134 | 0.06809 | 0.025443 | -0.067614 | -0.019254 | 0.0027108 | 0.0073242 | 0.034306 | 0.0075686 | -0.041832 | -0.0041956 | 0.010532 | 0.073242 | 0.045776 | 0.054932 | 0.11902 | 0.10529 | 0.041199 | -0.07782 | 0.022888 | 0.027466 | -0.10071 | 0.009155 | 0.027466 | 0.073242 | 0 | 120.6345 | 120.5154 | 0.009156 | 120.639 | 120.7123 | 0.19684 | -0.022888 | 120.6665 | 120.5933 | -0.086975 | 120.6161 | 120.4926 | -0.10071 | -0.068664 | 120.6985 | 120.6665 | 120.6482 | -0.17395 | 120.6024 | 120.6207 | 120.6207 | -0.09613
3107.75 | 120.8633 | -120.5658 | 0.07782 | -0.0022127 | 0.006054 | 0.070867 | 0.026938 | -0.069109 | -0.024808 | 0.0014292 | -0.0003053 | 0.030888 | 0.0097048 | -0.043754 | -0.0046228 | 0.013522 | 0.11902 | 0.13733 | 0.15106 | 0.16937 | 0.064087 | 0.10529 | -0.022888 | 0.10529 | 0.13733 | 0.013733 | -0.045776 | -0.018311 | 0.10529 | 0.050354 | 120.6711 | 120.5429 | -0.013733 | 120.7031 | 120.7352 | 0.19226 | 0.041199 | 120.6711 | 120.6162 | -0.1236 | 120.6711 | 120.5795 | -0.036621 | -0.096131 | 120.6299 | 120.6848 | 120.7169 | -0.10071 | 120.52 | 120.5475 | 120.7031 | -0.027466
3109.5469 | 120.8084 | -120.6436 | 0.082397 | 0.0054168 | -0.0031318 | 0.069158 | 0.029288 | -0.068255 | -0.024808 | -6.615e-05 | 0.014954 | 0.033024 | 0.009064 | -0.043113 | -0.0071862 | 0.011386 | 0 | -0.004578 | 0.022888 | 0.073242 | 0.11444 | 0.036621 | -0.091553 | -0.036621 | 0.018311 | -0.11444 | 0.013733 | 0.027466 | 0.054932 | -0.004578 | 120.6802 | 120.5521 | 0.032044 | 120.639 | 120.7169 | 0.16479 | -0.082397 | 120.6985 | 120.639 | -0.068664 | 120.607 | 120.5292 | -0.10986 | -0.054931 | 120.7581 | 120.6436 | 120.6665 | -0.17395 | 120.6573 | 120.6711 | 120.6619 | -0.086975
3111.2812 | 115.5579 | -77.8152 | 37.587 | 0.013046 | 0.0030634 | 0.07044 | 0.028006 | -0.070605 | -0.021176 | 0.0010018 | 0.0073242 | 0.034092 | 0.009064 | -0.040123 | -0.0048364 | 0.013522 | 0.004578 | -0.036621 | -0.009155 | 0.054932 | 0.091553 | 0.032043 | -0.082397 | -0.032043 | -0.013733 | -0.12817 | -0.009155 | 0.009155 | 0.050354 | -0.013733 | 77.8473 | 77.7328 | -37.4954 | 77.7786 | 77.8702 | 0.13733 | -37.5824 | 77.8656 | 77.8015 | -37.5961 | 77.7832 | 77.6871 | -0.11444 | -37.5778 | 77.9068 | 77.8198 | 77.8061 | -37.6694 | 77.8061 | 77.8244 | 77.8015 | -37.6007
3113.0781 | 120.6299 | -120.2728 | 0.082397 | -0.0022127 | 0.00071339 | 0.071508 | 0.027365 | -0.065264 | -0.029508 | 0.00014745 | 0.0073242 | 0.031742 | 0.0060732 | -0.043541 | -0.0086816 | 0.013736 | 0.086975 | 0.15106 | 0.16937 | 0.16022 | 0.059509 | 0.082397 | -0.027466 | 0.064087 | 0.19684 | 0.032043 | -0.036621 | -0.013733 | 0.11902 | 0.032043 | 120.3552 | 120.2454 | -0.022888 | 120.4239 | 120.433 | 0.18768 | 0.004578 | 120.3918 | 120.3049 | -0.11902 | 120.3369 | 120.3049 | 0 | -0.09613 | 120.3323 | 120.3598 | 120.4422 | -0.10986 | 120.2362 | 120.2591 | 120.4697 | -0.050354
3114.8125 | 120.726 | -120.4056 | 0.073242 | 0.0054168 | 0.0045588 | 0.069799 | 0.025015 | -0.069964 | -0.025876 | 0.00036105 | 0.0073242 | 0.032597 | 0.007355 | -0.042686 | -0.0054772 | 0.012882 | 0.10986 | 0.11902 | 0.16479 | 0.15106 | 0.045776 | 0.10986 | -0.022888 | 0.07782 | 0.15106 | 0.013733 | -0.032043 | -0.009155 | 0.10529 | 0.050354 | 120.5154 | 120.3827 | -0.027466 | 120.5246 | 120.5566 | 0.17395 | 0.036621 | 120.5109 | 120.4559 | -0.10529 | 120.4834 | 120.4193 | -0.036621 | -0.082397 | 120.4514 | 120.5154 | 120.5704 | -0.09613 | 120.3735 | 120.3964 | 120.5566 | -0.022888
3116.5938 | 120.7626 | -120.488 | 0.041199 | -0.0022127 | 0.006695 | 0.070654 | 0.022665 | -0.066759 | -0.027158 | 0.00014745 | 0.0073242 | 0.031315 | 0.0067142 | -0.043968 | -0.006759 | 0.015231 | 0.11444 | 0.12817 | 0.14648 | 0.15106 | 0.059509 | 0.09613 | -0.041199 | 0.086975 | 0.13275 | 0.032043 | -0.022888 | -0.013733 | 0.10986 | 0.041199 | 120.5841 | 120.4468 | 0.01831 | 120.6162 | 120.639 | 0.19226 | 0.073242 | 120.5978 | 120.5292 | -0.064087 | 120.575 | 120.52 | -0.009156 | -0.054932 | 120.5475 | 120.6024 | 120.6345 | -0.082398 | 120.4651 | 120.4742 | 120.6207 | 0
3118.3906 | 120.7993 | -120.5566 | 0.082397 | 0.013046 | 0.0030634 | 0.072149 | 0.029074 | -0.066119 | -0.026517 | -0.00070715 | 0.0073242 | 0.030033 | 0.0094912 | -0.042259 | -0.0076136 | 0.014163 | 0.10986 | 0.13733 | 0.16937 | 0.15564 | 0.059509 | 0.07782 | -0.032043 | 0.07782 | 0.17853 | 0.036621 | -0.036621 | -0.022888 | 0.10529 | 0.036621 | 120.6345 | 120.5246 | -0.022888 | 120.694 | 120.7123 | 0.18768 | 0.027466 | 120.6619 | 120.5933 | -0.11902 | 120.6345 | 120.5933 | 0 | -0.10528 | 120.6162 | 120.6665 | 120.726 | -0.11444 | 120.52 | 120.5338 | 120.7352 | -0.045776
3120.1875 | 120.8771 | -120.5612 | 0.059509 | 0.0054168 | 0.0028498 | 0.07044 | 0.025229 | -0.070391 | -0.022031 | -0.00027975 | 0.022583 | 0.033879 | 0.0060732 | -0.040977 | -0.0037684 | 0.010318 | 0.086975 | 0.054932 | 0.091553 | 0.11444 | 0.086975 | 0.086975 | -0.059509 | 0.07782 | 0.10986 | 0.004578 | -0.013733 | -0.022888 | 0.10986 | 0.041199 | 120.6482 | 120.5017 | 0.027466 | 120.6161 | 120.6757 | 0.17395 | 0.027466 | 120.6711 | 120.6024 | -0.073242 | 120.639 | 120.5658 | -0.036621 | -0.082397 | 120.6482 | 120.6482 | 120.6528 | -0.11902 | 120.5475 | 120.5383 | 120.6711 | -0.01831
3121.9062 | 120.7718 | -120.6116 | 0.11902 | 0.0054168 | -0.0024908 | 0.069799 | 0.029715 | -0.068041 | -0.02374 | 0.00036105 | 0.014954 | 0.034733 | 0.009064 | -0.040123 | -0.0074 | 0.012454 | -0.004578 | 0 | 0.032043 | 0.050354 | 0.10071 | 0.036621 | -0.086975 | -0.032043 | 0.032043 | -0.11444 | 0.018311 | 0.041199 | 0.068665 | 0 | 120.6482 | 120.5246 | -0.018311 | 120.6116 | 120.6619 | 0.13733 | -0.1236 | 120.6802 | 120.6116 | -0.10071 | 120.5795 | 120.4971 | -0.11444 | -0.07782 | 120.7123 | 120.607 | 120.6436 | -0.20599 | 120.6299 | 120.6528 | 120.6436 | -0.11902
3123.6875 | 120.7901 | -120.6665 | 0.11902 | 0.013046 | -0.0020636 | 0.071294 | 0.029501 | -0.066759 | -0.025449 | -0.00027975 | 0.0073242 | 0.033024 | 0.0082096 | -0.043968 | -0.0063318 | 0.012241 | 0.054932 | 0.091553 | 0.07782 | 0.13275 | 0.07782 | 0.050354 | -0.050354 | -0.004578 | 0.07782 | -0.07782 | 0.013733 | 0.045776 | 0.064087 | 0.004578 | 120.7169 | 120.6162 | -0.041199 | 120.7581 | 120.7993 | 0.18311 | -0.064087 | 120.7306 | 120.6711 | -0.10529 | 120.6619 | 120.5887 | -0.082398 | -0.073243 | 120.7443 | 120.7214 | 120.7443 | -0.16937 | 120.6802 | 120.7123 | 120.7443 | -0.11444
3125.4688 | 120.2087 | -119.9615 | 0.068665 | 0.013046 | -0.00014101 | 0.071081 | 0.030569 | -0.06975 | -0.026944 | -0.00070715 | 0.0073242 | 0.031315 | 0.0082096 | -0.043541 | -0.0076136 | 0.011386 | 0.091553 | 0.15564 | 0.15564 | 0.15564 | 0.054932 | 0.07782 | -0.032043 | 0.064087 | 0.16022 | 0.018311 | -0.027466 | -0.009155 | 0.09613 | 0.045776 | 120.0394 | 119.9295 | -0.013733 | 120.1172 | 120.1172 | 0.18768 | 0.022888 | 120.0577 | 120.0073 | -0.096131 | 120.0256 | 119.9799 | -0.027465 | -0.07782 | 120.0165 | 120.0531 | 120.1172 | -0.10071 | 119.9341 | 119.9524 | 120.1218 | -0.022889
3127.2656 | 120.575 | -120.3232 | 0.091553 | 0.013046 | -0.0037726 | 0.071081 | 0.024161 | -0.0674 | -0.020322 | -0.0017752 | 0.0073242 | 0.03516 | 0.0092776 | -0.041404 | -0.0031274 | 0.011173 | 0.082397 | 0.050354 | 0.059509 | 0.1236 | 0.09613 | 0.054932 | -0.082397 | 0.045776 | 0.082397 | -0.068665 | 0.004578 | 0.022888 | 0.07782 | 0.022888 | 120.3781 | 120.2408 | 0.004577 | 120.3735 | 120.4468 | 0.20599 | -0.009156 | 120.401 | 120.3461 | -0.086975 | 120.369 | 120.2545 | -0.091553 | -0.068665 | 120.4193 | 120.4056 | 120.3827 | -0.17395 | 120.3278 | 120.3461 | 120.4056 | -0.068665
3129.0469 | 120.6757 | -120.4422 | 0.082397 | 0.020676 | -0.00185 | 0.069585 | 0.029929 | -0.068255 | -0.023313 | 0.0029244 | 0.014954 | 0.03516 | 0.0097048 | -0.041191 | -0.0054772 | 0.012241 | 0.027466 | 0.018311 | 0.041199 | 0.082397 | 0.10071 | 0.054932 | -0.10529 | -0.004578 | 0.068665 | -0.07782 | 0.009155 | 0.018311 | 0.073242 | -0.004578 | 120.4971 | 120.3369 | 0.018311 | 120.4605 | 120.5246 | 0.18768 | -0.054931 | 120.5154 | 120.4376 | -0.073242 | 120.4376 | 120.3644 | -0.073242 | -0.064086 | 120.5429 | 120.4697 | 120.4834 | -0.18768 | 120.4514 | 120.4605 | 120.5109 | -0.086975
3130.7812 | 120.7993 | -120.488 | 0.054932 | 0.0054168 | 0.0047724 | 0.069158 | 0.023306 | -0.069109 | -0.024808 | 0.00207 | 0.022583 | 0.033238 | 0.0052188 | -0.043754 | -0.005691 | 0.012454 | 0.045776 | 0.068665 | 0.086975 | 0.10071 | 0.091553 | 0.07782 | -0.036621 | 0.07782 | 0.1236 | -0.018311 | -0.027466 | -0.009155 | 0.091553 | 0.032043 | 120.5658 | 120.4514 | 0.036621 | 120.5566 | 120.5887 | 0.13733 | -0.009156 | 120.5795 | 120.52 | -0.082398 | 120.5658 | 120.4697 | -0.050354 | -0.064087 | 120.5795 | 120.5338 | 120.575 | -0.091553 | 120.4605 | 120.4788 | 120.6116 | -0.022889
3132.5781 | 120.7489 | -120.5658 | 0.059509 | 0.013046 | 0.0011408 | 0.070226 | 0.024802 | -0.068041 | -0.022031 | 0.0010018 | 0.014954 | 0.034947 | 0.0092776 | -0.043541 | -0.0031274 | 0.012241 | 0.004578 | -0.018311 | 0.004578 | 0.068665 | 0.10071 | 0.050354 | -0.082397 | -0.032043 | 0 | -0.11902 | 0.004578 | 0.036621 | 0.064087 | 0 | 120.6162 | 120.4834 | 0.041199 | 120.5475 | 120.6345 | 0.15106 | -0.054931 | 120.6299 | 120.5658 | -0.054931 | 120.5338 | 120.4468 | -0.11902 | -0.022888 | 120.6665 | 120.5704 | 120.5704 | -0.14191 | 120.5704 | 120.6024 | 120.5658 | -0.059509
3134.375 | 120.8359 | -120.5658 | 0.059509 | 0.0054168 | 0.0028498 | 0.074285 | 0.028006 | -0.071245 | -0.031003 | 0.0010018 | 0.0073242 | 0.030247 | 0.0086368 | -0.046104 | -0.0095362 | 0.014804 | 0.032043 | 0.059509 | 0.10529 | 0.10071 | 0.064087 | 0.086975 | -0.068665 | 0.004578 | 0.073242 | -0.009155 | -0.018311 | 0 | 0.086975 | 0.036621 | 120.6528 | 120.4971 | 0.004578 | 120.6253 | 120.6665 | 0.16937 | -0.027466 | 120.6528 | 120.6024 | -0.07782 | 120.5704 | 120.5566 | -0.045776 | -0.059509 | 120.6299 | 120.5978 | 120.6711 | -0.12817 | 120.5475 | 120.5658 | 120.639 | -0.022888
3136.1719 | 120.8221 | -120.5704 | 0.13733 | 0.0054168 | 0.00028619 | 0.075353 | 0.028433 | -0.068682 | -0.030362 | -6.615e-05 | -0.0003053 | 0.031529 | 0.0035098 | -0.043754 | -0.0091088 | 0.012241 | 0.10986 | 0.12817 | 0.16479 | 0.16022 | 0.064087 | 0.082397 | -0.045776 | 0.059509 | 0.18768 | 0.013733 | -0.032043 | 0.004578 | 0.11444 | 0.027466 | 120.6528 | 120.5246 | -0.073242 | 120.6985 | 120.7306 | 0.20599 | -0.027466 | 120.6848 | 120.5978 | -0.16937 | 120.6299 | 120.5841 | -0.013733 | -0.13275 | 120.6345 | 120.6802 | 120.7352 | -0.18311 | 120.5383 | 120.575 | 120.7581 | -0.10986
3137.875 | 120.7672 | -120.6528 | 0.082397 | 0.013046 | -0.0016364 | 0.069799 | 0.025656 | -0.066119 | -0.019467 | 0.00036105 | -0.0003053 | 0.037724 | 0.0094912 | -0.042686 | -0.0018458 | 0.0096771 | 0.045776 | 0.018311 | 0.050354 | 0.082397 | 0.09613 | 0.054932 | -0.086975 | -0.004578 | 0.004578 | -0.13275 | 0.009155 | 0.032043 | 0.064087 | -0.004578 | 120.7077 | 120.5658 | 0.013733 | 120.6711 | 120.7352 | 0.16937 | -0.036621 | 120.7169 | 120.6482 | -0.073242 | 120.6482 | 120.52 | -0.12817 | -0.050354 | 120.7489 | 120.6985 | 120.7031 | -0.16937 | 120.6619 | 120.6848 | 120.6573 | -0.086975
3139.6562 | 120.7993 | -120.5658 | 0.16022 | 0.013046 | -0.0044134 | 0.069372 | 0.025229 | -0.0674 | -0.021604 | 0.0044198 | 0.0073242 | 0.034947 | 0.0084232 | -0.043754 | -0.0041956 | 0.012027 | 0.064087 | 0.073242 | 0.068665 | 0.10529 | 0.07782 | 0.054932 | -0.064087 | 0.004578 | 0.073242 | -0.09613 | 0.013733 | 0.018311 | 0.064087 | 0.013733 | 120.6207 | 120.5017 | -0.082397 | 120.639 | 120.6711 | 0.16937 | -0.09613 | 120.6299 | 120.5795 | -0.14648 | 120.5704 | 120.4697 | -0.10986 | -0.14191 | 120.6436 | 120.6299 | 120.6345 | -0.2243 | 120.5795 | 120.5841 | 120.639 | -0.14648
3141.4531 | 120.8862 | -120.6573 | 0.11902 | 0.0054168 | -0.0022772 | 0.07044 | 0.030569 | -0.068468 | -0.026731 | -0.0019888 | 0.0073242 | 0.033665 | 0.0084232 | -0.041404 | -0.0080408 | 0.013522 | 0 | -0.013733 | 0.013733 | 0.073242 | 0.1236 | 0.036621 | -0.086975 | -0.050354 | 0.018311 | -0.10071 | 0.032043 | 0.064087 | 0.045776 | 0 | 120.694 | 120.5704 | 0.004577 | 120.6436 | 120.7306 | 0.16022 | -0.11902 | 120.7031 | 120.6573 | -0.086976 | 120.607 | 120.5566 | -0.10071 | -0.054932 | 120.7809 | 120.6573 | 120.6711 | -0.20599 | 120.6894 | 120.7214 | 120.6757 | -0.11902
3143.2344 | 120.845 | -120.7169 | 0.10986 | 0.0054168 | -0.00099541 | 0.072363 | 0.030997 | -0.066759 | -0.028653 | -0.0015616 | 0.014954 | 0.029179 | 0.0088504 | -0.043541 | -0.0069726 | 0.013736 | 0.073242 | 0.1236 | 0.13733 | 0.15564 | 0.045776 | 0.073242 | -0.045776 | 0.022888 | 0.11902 | -0.027466 | 0 | 0.027466 | 0.073242 | 0.009155 | 120.7901 | 120.6711 | -0.064087 | 120.8405 | 120.8725 | 0.20142 | -0.036621 | 120.7901 | 120.726 | -0.10986 | 120.7397 | 120.6894 | -0.036621 | -0.082397 | 120.7626 | 120.7901 | 120.8542 | -0.15564 | 120.7169 | 120.7443 | 120.8359 | -0.10071
3145.0156 | 120.6116 | -120.2774 | 0.050354 | 0.013046 | 0.0056268 | 0.075567 | 0.02886 | -0.069109 | -0.02908 | -0.001348 | -0.0003053 | 0.029392 | 0.0071414 | -0.044609 | -0.0086816 | 0.011386 | 0.013733 | 0.054932 | 0.091553 | 0.10529 | 0.059509 | 0.086975 | -0.054932 | 0.027466 | 0.10986 | 0.004578 | -0.013733 | 0.009155 | 0.11444 | 0.041199 | 120.3644 | 120.2225 | 0.009155 | 120.3323 | 120.3827 | 0.16022 | -0.036621 | 120.3918 | 120.3186 | -0.064087 | 120.3049 | 120.282 | -0.036621 | -0.041199 | 120.3369 | 120.2911 | 120.369 | -0.10529 | 120.2637 | 120.2866 | 120.3873 | -0.009155
3146.8125 | 120.8084 | -120.5566 | 0.064087 | -0.0022127 | 0.0058404 | 0.070867 | 0.027579 | -0.069537 | -0.027799 | -0.00049335 | 0.0073242 | 0.03217 | 0.0058596 | -0.0429 | -0.0069726 | 0.011813 | 0.050354 | 0.086975 | 0.10986 | 0.10529 | 0.054932 | 0.07782 | -0.018311 | 0.018311 | 0.086975 | -0.018311 | -0.027466 | 0.004578 | 0.086975 | 0.045776 | 120.6345 | 120.5383 | -0.009155 | 120.6436 | 120.6619 | 0.1236 | -0.013733 | 120.6436 | 120.6024 | -0.091553 | 120.575 | 120.5383 | -0.064087 | -0.059509 | 120.6116 | 120.607 | 120.6665 | -0.082398 | 120.5292 | 120.5612 | 120.6436 | -0.018311
3148.5469 | 120.7993 | -120.6573 | 0.082397 | 0.0054168 | 0.0011408 | 0.07044 | 0.02822 | -0.068896 | -0.02374 | -0.00049335 | 0.014954 | 0.03217 | 0.007355 | -0.040123 | -0.0061182 | 0.011386 | 0.10071 | 0.12817 | 0.15564 | 0.14191 | 0.059509 | 0.086975 | -0.050354 | 0.059509 | 0.16479 | 0.004578 | -0.027466 | -0.004578 | 0.086975 | 0.036621 | 120.7443 | 120.607 | -0.022888 | 120.7855 | 120.7993 | 0.19226 | 0.018311 | 120.7443 | 120.694 | -0.10986 | 120.7169 | 120.6619 | -0.032043 | -0.086975 | 120.7169 | 120.7581 | 120.813 | -0.13275 | 120.6299 | 120.6528 | 120.8221 | -0.045776
3150.3438 | 120.8633 | -120.6757 | 0.10071 | 0.0054168 | -0.0041998 | 0.070654 | 0.032492 | -0.067614 | -0.023099 | 0.0016428 | 0.022583 | 0.033879 | 0.010559 | -0.041191 | -0.0061182 | 0.0090363 | 0.013733 | -0.009155 | 0 | 0.059509 | 0.11444 | 0.050354 | -0.09613 | -0.027466 | 0.027466 | -0.10529 | 0.018311 | 0.041199 | 0.059509 | 0 | 120.726 | 120.5795 | 0.013733 | 120.6665 | 120.7352 | 0.15564 | -0.086975 | 120.7352 | 120.6757 | -0.082397 | 120.6482 | 120.5704 | -0.10529 | -0.059509 | 120.7901 | 120.6894 | 120.6757 | -0.19684 | 120.694 | 120.7169 | 120.7031 | -0.10071
3152.125 | 120.8588 | -120.7169 | 0.10529 | 0.013046 | -0.00014101 | 0.070867 | 0.02587 | -0.067614 | -0.018186 | -0.00027975 | 0.014954 | 0.036228 | 0.009064 | -0.043113 | -0.003982 | 0.011173 | 0 | -0.041199 | 0.004578 | 0.064087 | 0.10986 | 0.045776 | -0.068665 | -0.041199 | -0.022888 | -0.13275 | 0.022888 | 0.041199 | 0.059509 | 0 | 120.7626 | 120.6482 | 0.004577 | 120.6757 | 120.7809 | 0.13275 | -0.10529 | 120.7764 | 120.7169 | -0.082398 | 120.6757 | 120.5841 | -0.13275 | -0.064087 | 120.8267 | 120.7169 | 120.7214 | -0.17395 | 120.7397 | 120.7581 | 120.694 | -0.10529
3153.8438 | 120.8633 | -120.7077 | 0.086975 | 0.013046 | -0.0024908 | 0.068731 | 0.023734 | -0.069323 | -0.023099 | 0.003138 | 0.0073242 | 0.035588 | 0.007996 | -0.041832 | -0.0031274 | 0.01395 | 0.004578 | -0.036621 | 0.004578 | 0.054932 | 0.07782 | 0.045776 | -0.073242 | -0.018311 | -0.009155 | -0.13733 | 0.013733 | 0.027466 | 0.082397 | 0.004578 | 120.7535 | 120.6345 | -0.009155 | 120.6711 | 120.7626 | 0.12817 | -0.082397 | 120.7901 | 120.7123 | -0.073242 | 120.6894 | 120.5704 | -0.14191 | -0.059509 | 120.7855 | 120.7123 | 120.7123 | -0.16022 | 120.7214 | 120.7352 | 120.6985 | -0.082397
3155.625 | 121.0098 | -120.7535 | 0.064087 | 0.0054168 | 0.003277 | 0.073003 | 0.02822 | -0.070391 | -0.031644 | 0.0012154 | 0.014954 | 0.028752 | 0.0058596 | -0.044181 | -0.0091088 | 0.015018 | 0.036621 | 0.073242 | 0.10071 | 0.10986 | 0.07782 | 0.07782 | -0.045776 | 0.009155 | 0.10071 | -0.018311 | -0.009155 | 0 | 0.10071 | 0.032043 | 120.8313 | 120.7077 | 0.013733 | 120.8267 | 120.8633 | 0.15564 | -0.027466 | 120.8542 | 120.7855 | -0.073242 | 120.7626 | 120.7352 | -0.050354 | -0.064087 | 120.8313 | 120.7901 | 120.8542 | -0.10986 | 120.7443 | 120.7535 | 120.8542 | -0.032044
3157.4375 | 120.9183 | -120.7764 | 0.091553 | 0.020676 | 0.00092719 | 0.068731 | 0.025443 | -0.067614 | -0.018399 | 0.0016428 | 0.0073242 | 0.034733 | 0.007996 | -0.043754 | -0.0027002 | 0.012668 | 0.009155 | -0.054932 | -0.022888 | 0.068665 | 0.082397 | 0.054932 | -0.082397 | -0.022888 | -0.036621 | -0.13275 | 0.018311 | 0.041199 | 0.059509 | 0.009155 | 120.8313 | 120.694 | -0.009156 | 120.7214 | 120.845 | 0.15106 | -0.082398 | 120.8359 | 120.7855 | -0.073242 | 120.7535 | 120.6436 | -0.14191 | -0.050354 | 120.8588 | 120.7855 | 120.7535 | -0.17395 | 120.7947 | 120.8176 | 120.7397 | -0.082398
3159.1719 | 120.9183 | -120.6207 | 0.27466 | -0.0022127 | -0.00056821 | 0.066167 | 0.026297 | -0.068041 | -0.023313 | 0.00078825 | 0.022583 | 0.035374 | 0.0099186 | -0.041404 | -0.0054772 | 0.012454 | 0 | -0.036621 | 0.022888 | 0.064087 | 0.082397 | 0.059509 | -0.082397 | -0.027466 | -0.022888 | -0.14191 | 0.022888 | 0.036621 | 0.064087 | 0.004578 | 120.6802 | 120.5383 | -0.19226 | 120.5841 | 120.6848 | 0.14648 | -0.27466 | 120.6848 | 120.6253 | -0.25177 | 120.5933 | 120.4788 | -0.14649 | -0.23804 | 120.7031 | 120.6207 | 120.6436 | -0.35706 | 120.6436 | 120.6573 | 120.5978 | -0.27008
3160.9531 | 121.138 | -120.7581 | 0.064087 | 0.0054168 | 0.0034906 | 0.073003 | 0.02886 | -0.069323 | -0.031217 | 0.0010018 | -0.0003053 | 0.029179 | 0.0069278 | -0.04525 | -0.0099634 | 0.014163 | 0.041199 | 0.073242 | 0.13275 | 0.12817 | 0.050354 | 0.086975 | -0.041199 | 0.036621 | 0.13733 | 0.018311 | -0.018311 | 0.013733 | 0.11444 | 0.036621 | 120.845 | 120.7169 | -0.013733 | 120.8313 | 120.8862 | 0.16937 | -0.022888 | 120.8725 | 120.7947 | -0.082398 | 120.7947 | 120.7764 | -0.01831 | -0.050354 | 120.8084 | 120.7993 | 120.8908 | -0.10529 | 120.7397 | 120.7718 | 120.8954 | -0.027466
3162.6875 | 120.9229 | -120.6619 | 0.21515 | 0.013046 | -0.0014228 | 0.069799 | 0.029074 | -0.0674 | -0.021604 | 0.0010018 | 0.014954 | 0.035374 | 0.0082096 | -0.041832 | -0.0054772 | 0.010532 | 0.032043 | -0.004578 | 0.050354 | 0.10529 | 0.10071 | 0.054932 | -0.073242 | 0.018311 | 0.045776 | -0.086975 | 0.018311 | 0.041199 | 0.068665 | 0.009155 | 120.7169 | 120.5887 | -0.11444 | 120.6573 | 120.7672 | 0.17853 | -0.18311 | 120.7306 | 120.6711 | -0.19684 | 120.6802 | 120.575 | -0.09613 | -0.17395 | 120.7626 | 120.694 | 120.7123 | -0.28839 | 120.6802 | 120.7031 | 120.7077 | -0.20599
3164.4844 | 121.0648 | -120.7031 | 0.073242 | 0.0054168 | 0.004986 | 0.071508 | 0.027579 | -0.071245 | -0.027799 | 0.00078825 | 0.014954 | 0.031101 | 0.005646 | -0.045036 | -0.0052636 | 0.01395 | 0.10986 | 0.13275 | 0.14648 | 0.14191 | 0.041199 | 0.086975 | -0.032043 | 0.050354 | 0.11444 | 0.009155 | -0.013733 | 0.004578 | 0.10529 | 0.050354 | 120.7901 | 120.6711 | -0.032043 | 120.8359 | 120.845 | 0.17395 | 0.036621 | 120.8084 | 120.7535 | -0.086975 | 120.7535 | 120.7123 | -0.041199 | -0.068664 | 120.7443 | 120.813 | 120.8496 | -0.10529 | 120.6894 | 120.7077 | 120.8176 | -0.022888
3166.2188 | 121.0144 | -120.8542 | 0.10529 | 0.0054168 | -0.00078181 | 0.068731 | 0.030142 | -0.066973 | -0.025449 | -0.0024162 | 0.014954 | 0.030247 | 0.0082096 | -0.043113 | -0.0086816 | 0.0116 | 0.068665 | 0.086975 | 0.11902 | 0.1236 | 0.086975 | 0.09613 | -0.054932 | -0.009155 | 0.068665 | -0.050354 | 0.009155 | 0.018311 | 0.073242 | 0.004578 | 120.9503 | 120.7993 | -0.018311 | 120.9412 | 120.9778 | 0.17853 | -0.036621 | 120.9274 | 120.8588 | -0.096131 | 120.845 | 120.8038 | -0.054932 | -0.086975 | 120.9412 | 120.9229 | 120.9732 | -0.16022 | 120.8633 | 120.8725 | 120.9229 | -0.10071
3168.0156 | 120.8725 | -120.0211 | 0.073242 | 0.013046 | 0.0030634 | 0.073003 | 0.030142 | -0.069109 | -0.030149 | -0.0022024 | -0.0003053 | 0.028965 | 0.0082096 | -0.04525 | -0.006759 | 0.012027 | 0.032043 | 0.073242 | 0.091553 | 0.1236 | 0.073242 | 1.0117 | 0.96588 | 0.004578 | 0.091553 | -0.036621 | -0.013733 | -0.041199 | 2.7237 | 1.6891 | 121.0327 | 120.9869 | 0 | 120.0943 | 120.1447 | -0.84228 | -0.041199 | 122.7448 | 121.7102 | -0.086975 | 120.0256 | 119.9844 | -1.7258 | -0.11444 | 120.0943 | 120.0531 | 120.1126 | 0.89264 | 120.0073 | 119.9799 | 120.1126 | 1.6159
3169.7344 | 121.0281 | -120.6894 | 0.054932 | 0.020676 | 0.0039178 | 0.072363 | 0.030569 | -0.066332 | -0.027371 | -0.0024162 | 0.014954 | 0.02747 | 0.009064 | -0.043968 | -0.0076136 | 0.0116 | 0.054932 | 0.091553 | 0.13275 | 0.13275 | 0.064087 | 0.059509 | -0.041199 | 0.054932 | 0.14191 | 0.032043 | -0.013733 | -0.018311 | 0.10986 | 0.032043 | 120.7489 | 120.6482 | 0.009155 | 120.7809 | 120.8221 | 0.17395 | 0 | 120.7993 | 120.7214 | -0.068665 | 120.7443 | 120.7214 | 0 | -0.073243 | 120.7535 | 120.7443 | 120.8221 | -0.096131 | 120.6757 | 120.6711 | 120.8313 | -0.022889
3171.5312 | 121.0281 | -120.7764 | 0.059509 | 0.013046 | 0.0034906 | 0.070867 | 0.025015 | -0.068682 | -0.024808 | -0.0011344 | 0.014954 | 0.031529 | 0.007996 | -0.046959 | -0.00505 | 0.011813 | 0.13275 | 0.1236 | 0.15564 | 0.16937 | 0.050354 | 0.086975 | -0.027466 | 0.10986 | 0.13733 | 0.022888 | -0.013733 | 0 | 0.10071 | 0.045776 | 120.8633 | 120.7489 | -0.009155 | 120.9 | 120.9457 | 0.19684 | 0.073242 | 120.8771 | 120.8221 | -0.073242 | 120.8862 | 120.7993 | -0.022888 | -0.059509 | 120.8267 | 120.9091 | 120.932 | -0.086975 | 120.7626 | 120.7764 | 120.9137 | -0.013733
3173.3281 | 121.0236 | -120.7947 | 0.082397 | 0.020676 | 0.0054132 | 0.071081 | 0.029715 | -0.068041 | -0.026303 | -0.0017752 | 0.014954 | 0.031956 | 0.0084232 | -0.043541 | -0.0082544 | 0.012027 | 0.059509 | 0.068665 | 0.10071 | 0.091553 | 0.073242 | 0.091553 | -0.041199 | 0.022888 | 0.068665 | -0.032043 | -0.009155 | -0.013733 | 0.09613 | 0.022888 | 120.8862 | 120.7535 | -0.009155 | 120.8633 | 120.8862 | 0.13275 | -0.022888 | 120.8908 | 120.8176 | -0.091552 | 120.8176 | 120.7626 | -0.054931 | -0.09613 | 120.8679 | 120.8542 | 120.8954 | -0.1236 | 120.7855 | 120.7809 | 120.8633 | -0.059509
3175.125 | 121.1151 | -120.7855 | 0.064087 | 0.013046 | 0.0028498 | 0.074926 | 0.029501 | -0.069323 | -0.026944 | -0.00070715 | 0.014954 | 0.03217 | 0.0067142 | -0.045036 | -0.0069726 | 0.012027 | 0.09613 | 0.1236 | 0.13275 | 0.14191 | 0.064087 | 0.082397 | -0.045776 | 0.082397 | 0.16022 | 0.032043 | -0.036621 | -0.009155 | 0.09613 | 0.032043 | 120.8679 | 120.7397 | 0 | 120.9091 | 120.9274 | 0.18768 | 0.032043 | 120.8817 | 120.8176 | -0.10071 | 120.8679 | 120.8176 | 0 | -0.073242 | 120.8496 | 120.8817 | 120.9183 | -0.10986 | 120.7489 | 120.7764 | 120.9457 | -0.032044
3176.9531 | 121.1426 | -120.8405 | 0.068665 | 0.013046 | 0.004986 | 0.069585 | 0.026511 | -0.068041 | -0.019681 | -0.0011344 | 0.014954 | 0.033665 | 0.0047916 | -0.043113 | -0.0048364 | 0.010959 | 0.11902 | 0.091553 | 0.11902 | 0.15106 | 0.068665 | 0.091553 | -0.032043 | 0.10071 | 0.10529 | -0.009155 | -0.022888 | -0.013733 | 0.11444 | 0.045776 | 120.932 | 120.8084 | 0 | 120.932 | 120.9915 | 0.18311 | 0.050354 | 120.9549 | 120.8862 | -0.091553 | 120.9412 | 120.8313 | -0.054931 | -0.082398 | 120.9091 | 120.9595 | 120.9595 | -0.10071 | 120.8176 | 120.8267 | 120.9457 | -0.022889
3178.6875 | 121.0739 | -120.8817 | 0.064087 | 0.0054168 | 0.0054132 | 0.073644 | 0.027365 | -0.070818 | -0.024381 | -0.0011344 | 0.022583 | 0.031101 | 0.0043644 | -0.043113 | -0.0054772 | 0.012882 | 0.10071 | 0.12817 | 0.14191 | 0.11902 | 0.054932 | 0.086975 | -0.022888 | 0.059509 | 0.10986 | -0.009155 | -0.009155 | -0.009155 | 0.10071 | 0.041199 | 120.9686 | 120.8588 | -0.009155 | 121.0098 | 121.0007 | 0.14191 | 0.036621 | 120.9824 | 120.9229 | -0.073242 | 120.9412 | 120.8725 | -0.050354 | -0.073242 | 120.9366 | 120.9824 | 121.0236 | -0.086975 | 120.8725 | 120.8725 | 120.9915 | -0.022888
3180.4219 | 121.138 | -120.8633 | 0.073242 | 0.020676 | 0.0056268 | 0.07279 | 0.026938 | -0.070177 | -0.026517 | -0.0011344 | 0.0073242 | 0.02982 | 0.006287 | -0.0429 | -0.0093226 | 0.012454 | 0.073242 | 0.082397 | 0.11902 | 0.10529 | 0.07782 | 0.07782 | -0.013733 | 0.027466 | 0.091553 | -0.036621 | -0.013733 | 0.004578 | 0.091553 | 0.022888 | 120.9412 | 120.8496 | 0.004578 | 120.9457 | 120.9686 | 0.11902 | 0 | 120.9549 | 120.8862 | -0.086975 | 120.8908 | 120.8267 | -0.059509 | -0.068664 | 120.9412 | 120.9366 | 120.9824 | -0.086975 | 120.8496 | 120.8679 | 120.9549 | -0.050354
3182.1562 | 121.1884 | -120.8908 | 0.082397 | 0.020676 | 0.0039178 | 0.074285 | 0.030997 | -0.066973 | -0.02609 | -0.0024162 | 0.022583 | 0.029606 | 0.0088504 | -0.042259 | -0.006759 | 0.010745 | 0.10529 | 0.13733 | 0.15106 | 0.14191 | 0.054932 | 0.09613 | -0.036621 | 0.086975 | 0.16937 | 0.050354 | -0.013733 | -0.009155 | 0.09613 | 0.050354 | 120.9869 | 120.8542 | -0.027465 | 121.0281 | 121.0327 | 0.17853 | 0.022889 | 120.9869 | 120.9412 | -0.09613 | 120.9778 | 120.9412 | 0 | -0.091552 | 120.9457 | 120.9961 | 121.0419 | -0.11902 | 120.8771 | 120.8817 | 121.0602 | -0.032043
3183.9531 | 121.2387 | -120.8908 | 0.059509 | 0.013046 | 0.0051996 | 0.073217 | 0.028647 | -0.070177 | -0.026731 | -6.615e-05 | 0.014954 | 0.03281 | 0.0069278 | -0.044395 | -0.0097498 | 0.010532 | 0.07782 | 0.07782 | 0.1236 | 0.12817 | 0.068665 | 0.068665 | -0.041199 | 0.054932 | 0.14191 | 0.004578 | -0.004578 | 0.004578 | 0.10986 | 0.022888 | 120.9595 | 120.8496 | 0.009156 | 120.9686 | 121.019 | 0.16937 | 0.018311 | 121.0007 | 120.9137 | -0.064087 | 120.9457 | 120.8954 | -0.01831 | -0.054931 | 120.9595 | 120.9686 | 121.0144 | -0.10071 | 120.8862 | 120.8954 | 121.0327 | -0.036621
3185.6719 | 121.1563 | -120.9091 | 0.054932 | 0.013046 | 0.006054 | 0.073431 | 0.025656 | -0.068896 | -0.024381 | -0.00049335 | 0.0073242 | 0.031529 | 0.0067142 | -0.045036 | -0.0041956 | 0.013095 | 0.11444 | 0.10529 | 0.13275 | 0.1236 | 0.050354 | 0.073242 | -0.041199 | 0.045776 | 0.10529 | -0.022888 | -0.022888 | 0.009155 | 0.091553 | 0.041199 | 120.9824 | 120.8679 | -0.004578 | 121.0144 | 121.0327 | 0.16479 | 0.059509 | 121.0007 | 120.9503 | -0.07782 | 120.9549 | 120.8862 | -0.064087 | -0.045777 | 120.9595 | 121.0236 | 121.0419 | -0.096131 | 120.8862 | 120.9183 | 121.0144 | -0.013733
3187.4531 | 121.2296 | -120.8954 | 0.054932 | 0.0054168 | 0.001568 | 0.070654 | 0.022238 | -0.069537 | -0.017972 | 0.00036105 | 0.014954 | 0.036869 | 0.0067142 | -0.042686 | -0.0031274 | 0.010532 | 0.073242 | 0.009155 | 0.050354 | 0.086975 | 0.091553 | 0.059509 | -0.059509 | 0.064087 | 0.059509 | -0.041199 | -0.009155 | 0.009155 | 0.091553 | 0.036621 | 120.9549 | 120.8359 | 0.036621 | 120.9045 | 120.9824 | 0.14648 | 0.01831 | 120.9869 | 120.932 | -0.064087 | 120.9595 | 120.8542 | -0.07782 | -0.045777 | 120.9869 | 120.9686 | 120.9457 | -0.11444 | 120.8862 | 120.9045 | 120.9549 | -0.018311
3189.1562 | 121.2524 | -120.9366 | 0.050354 | -0.0022127 | 0.0047724 | 0.071508 | 0.020102 | -0.069964 | -0.02374 | -6.615e-05 | 0.014954 | 0.030674 | 0.0047916 | -0.044181 | -0.003982 | 0.012027 | 0.13733 | 0.12817 | 0.14648 | 0.15564 | 0.050354 | 0.091553 | -0.018311 | 0.10529 | 0.14648 | 0.009155 | 0 | -0.013733 | 0.09613 | 0.050354 | 121.0281 | 120.9183 | 0 | 121.0648 | 121.0922 | 0.17395 | 0.086975 | 121.0327 | 120.9869 | -0.050354 | 121.0419 | 120.9457 | -0.041199 | -0.064087 | 120.9869 | 121.0739 | 121.0831 | -0.068665 | 120.9366 | 120.9229 | 121.0831 | 0
3190.875 | 121.0922 | -120.9915 | 0.07782 | 0.013046 | -0.0037726 | 0.070226 | 0.025229 | -0.066973 | -0.020108 | 0.0012154 | 0.0073242 | 0.035374 | 0.009064 | -0.043541 | -0.0029138 | 0.012027 | 0.086975 | 0.041199 | 0.045776 | 0.10986 | 0.09613 | 0.064087 | -0.068665 | 0.027466 | 0.027466 | -0.10529 | -0.018311 | 0.013733 | 0.059509 | 0.004578 | 121.0556 | 120.9229 | 0.01831 | 121.0327 | 121.1014 | 0.17853 | 0.009155 | 121.051 | 120.9961 | -0.096131 | 121.019 | 120.8862 | -0.10986 | -0.064087 | 121.0876 | 121.0785 | 121.0373 | -0.14649 | 120.9732 | 121.0052 | 121.019 | -0.073242
3192.5938 | 121.1746 | -121.0052 | 0.10986 | 0.013046 | -0.0033454 | 0.072363 | 0.02886 | -0.069109 | -0.024808 | 0.00014745 | 0.0073242 | 0.034306 | 0.010132 | -0.043113 | -0.0074 | 0.012668 | 0 | 0.022888 | 0.032043 | 0.064087 | 0.10071 | 0.036621 | -0.068665 | -0.036621 | 0.041199 | -0.10071 | 0.018311 | 0.027466 | 0.059509 | 0 | 121.0419 | 120.9366 | -0.009155 | 121.0281 | 121.0693 | 0.13275 | -0.10986 | 121.0648 | 121.0052 | -0.091552 | 120.9686 | 120.9045 | -0.10071 | -0.082397 | 121.106 | 121.0052 | 121.0373 | -0.17853 | 121.0236 | 121.0327 | 121.0464 | -0.10986
3194.3281 | 121.2662 | -120.9686 | 0.086975 | 0.013046 | 0.0058404 | 0.073217 | 0.027792 | -0.066973 | -0.028012 | -0.001348 | 0.0073242 | 0.029606 | 0.007355 | -0.043754 | -0.0069726 | 0.014377 | 0.045776 | 0.07782 | 0.10071 | 0.10986 | 0.064087 | 0.082397 | -0.050354 | 0.018311 | 0.09613 | -0.032043 | -0.018311 | -0.004578 | 0.091553 | 0.036621 | 121.051 | 120.9183 | -0.022888 | 121.0464 | 121.0785 | 0.16022 | -0.041199 | 121.0602 | 121.0052 | -0.10529 | 120.9869 | 120.9366 | -0.068664 | -0.091553 | 121.0327 | 121.0144 | 121.0693 | -0.13733 | 120.9503 | 120.9641 | 121.0648 | -0.050354
3196.0469 | 121.1792 | -120.9732 | 0.13733 | 0.0054168 | -0.0014228 | 0.068517 | 0.028433 | -0.068468 | -0.021604 | 0.0016428 | 0.0073242 | 0.035588 | 0.0082096 | -0.04055 | -0.00505 | 0.010532 | 0.068665 | 0.036621 | 0.059509 | 0.1236 | 0.09613 | 0.059509 | -0.064087 | 0.032043 | 0.068665 | -0.073242 | -0.009155 | 0.036621 | 0.10986 | 0.059509 | 121.0327 | 120.9091 | -0.041199 | 121.0098 | 121.0968 | 0.18768 | -0.068664 | 121.0831 | 121.0327 | -0.14648 | 121.0052 | 120.9 | -0.13275 | -0.10071 | 121.0693 | 121.0419 | 121.0327 | -0.20142 | 120.9641 | 121.0098 | 121.0419 | -0.07782
3197.75 | 121.225 | -121.0236 | 0.073242 | 0.013046 | -0.003559 | 0.069585 | 0.029715 | -0.069964 | -0.02139 | 0.00207 | 0.0073242 | 0.037083 | 0.010346 | -0.043113 | -0.0061182 | 0.012668 | 0.068665 | 0.068665 | 0.073242 | 0.11902 | 0.10071 | 0.050354 | -0.07782 | 0.050354 | 0.086975 | -0.064087 | 0.009155 | 0.013733 | 0.073242 | 0.018311 | 121.0739 | 120.9457 | 0.027466 | 121.0922 | 121.1426 | 0.19684 | -0.004577 | 121.0968 | 121.0419 | -0.064087 | 121.0739 | 120.9595 | -0.082398 | -0.059509 | 121.1243 | 121.0922 | 121.0968 | -0.15106 | 121.0327 | 121.0373 | 121.1105 | -0.054931
3199.4688 | 121.225 | -121.0098 | 0.059509 | 0.0054168 | 0.0058404 | 0.070226 | 0.028433 | -0.069109 | -0.02908 | 0.0014292 | 0.022583 | 0.028324 | 0.0077822 | -0.042259 | -0.008468 | 0.014591 | 0.059509 | 0.11902 | 0.13733 | 0.13733 | 0.059509 | 0.07782 | -0.027466 | 0.045776 | 0.10529 | -0.004578 | -0.022888 | -0.004578 | 0.091553 | 0.032043 | 121.0876 | 120.9824 | 0 | 121.1288 | 121.1472 | 0.16479 | 0 | 121.1014 | 121.0419 | -0.082397 | 121.0556 | 121.0052 | -0.036621 | -0.064087 | 121.0693 | 121.0693 | 121.1472 | -0.086975 | 120.9869 | 121.0052 | 121.1151 | -0.027466
3201.2031 | 121.1975 | -121.051 | 0.091553 | 0.0054168 | -0.00185 | 0.068304 | 0.027579 | -0.067828 | -0.021176 | 0.00014745 | 0.0073242 | 0.033665 | 0.0086368 | -0.041191 | -0.003982 | 0.012668 | -0.027466 | -0.045776 | -0.018311 | 0.068665 | 0.09613 | 0.059509 | -0.068665 | -0.032043 | -0.018311 | -0.13733 | 0.018311 | 0.041199 | 0.064087 | 0.004578 | 121.1105 | 120.9824 | 0.004577 | 121.0052 | 121.1197 | 0.13733 | -0.11902 | 121.1151 | 121.0556 | -0.073242 | 121.019 | 120.9137 | -0.14191 | -0.050354 | 121.1472 | 121.0236 | 121.0327 | -0.16022 | 121.0693 | 121.0922 | 121.0327 | -0.086975
3202.9688 | 121.2433 | -121.0602 | 0.064087 | 0.013046 | 0.00092719 | 0.072363 | 0.032919 | -0.071032 | -0.02908 | 0.00078825 | 0.0073242 | 0.030674 | 0.0092776 | -0.043968 | -0.0086816 | 0.012882 | 0.086975 | 0.15564 | 0.17853 | 0.16937 | 0.050354 | 0.073242 | -0.041199 | 0.07782 | 0.17395 | 0.018311 | -0.027466 | 0 | 0.10986 | 0.050354 | 121.1334 | 121.019 | -0.013733 | 121.2158 | 121.2296 | 0.21057 | 0.022888 | 121.17 | 121.1105 | -0.091553 | 121.138 | 121.0785 | -0.032043 | -0.064087 | 121.1105 | 121.1472 | 121.2387 | -0.10529 | 121.0327 | 121.0602 | 121.2341 | -0.013733
3204.6875 | 121.3165 | -120.9824 | 0.059509 | 0.0054168 | 0.0047724 | 0.070226 | 0.03121 | -0.06975 | -0.02844 | -0.003057 | -0.0003053 | 0.030247 | 0.0075686 | -0.041404 | -0.0097498 | 0.012668 | 0.07782 | 0.1236 | 0.14648 | 0.14648 | 0.068665 | 0.09613 | -0.050354 | 0.059509 | 0.16022 | 0.045776 | -0.013733 | 0 | 0.09613 | 0.045776 | 121.0785 | 120.932 | 0.009156 | 121.106 | 121.1288 | 0.19684 | 0.018311 | 121.0785 | 121.0281 | -0.073242 | 121.0419 | 121.0281 | 0 | -0.059509 | 121.051 | 121.0602 | 121.1288 | -0.10986 | 120.9686 | 120.9824 | 121.1426 | -0.013733
3206.4062 | 121.3806 | -120.9961 | 0.086975 | -0.0098417 | 0.0045588 | 0.071508 | 0.027579 | -0.064623 | -0.026944 | -0.0024162 | 0.0073242 | 0.031529 | 0.0084232 | -0.044822 | -0.011245 | 0.012454 | 0.10986 | 0.10986 | 0.14191 | 0.16479 | 0.073242 | 0.086975 | -0.036621 | 0.068665 | 0.1831 | 0.045776 | -0.027466 | 0 | 0.11444 | 0.036621 | 121.0831 | 120.9595 | -0.013733 | 121.106 | 121.1609 | 0.20142 | 0.022888 | 121.1105 | 121.0327 | -0.11444 | 121.0648 | 121.0419 | 0.009155 | -0.086975 | 121.0693 | 121.106 | 121.138 | -0.1236 | 120.9686 | 120.9961 | 121.1792 | -0.050354
3208.125 | 121.4035 | -121.0373 | 0.07782 | 0.013046 | 0.00092719 | 0.071722 | 0.026938 | -0.066332 | -0.026517 | -0.0022024 | 0.0073242 | 0.030247 | 0.0067142 | -0.042045 | -0.0095362 | 0.0098907 | 0.12817 | 0.1236 | 0.16937 | 0.15106 | 0.073242 | 0.082397 | -0.041199 | 0.086975 | 0.17853 | 0.059509 | -0.018311 | -0.009155 | 0.11444 | 0.036621 | 121.1197 | 120.9961 | -0.004578 | 121.1609 | 121.1884 | 0.19226 | 0.050354 | 121.1517 | 121.0739 | -0.096131 | 121.1243 | 121.0968 | 0.022888 | -0.086975 | 121.1105 | 121.1655 | 121.2067 | -0.11902 | 121.019 | 121.0281 | 121.2158 | -0.041199
3209.8906 | 121.3211 | -121.0419 | 0.068665 | 0.0054168 | 0.0039178 | 0.074285 | 0.025229 | -0.070818 | -0.027585 | -0.001348 | 0.0073242 | 0.033024 | 0.0075686 | -0.044822 | -0.0065454 | 0.012241 | 0.073242 | 0.050354 | 0.10529 | 0.10986 | 0.059509 | 0.086975 | -0.022888 | 0.036621 | 0.086975 | -0.027466 | -0.013733 | 0 | 0.13733 | 0.073242 | 121.1288 | 121.019 | -0.009156 | 121.0922 | 121.1517 | 0.13275 | 0.004577 | 121.1792 | 121.1151 | -0.082398 | 121.0785 | 121.0144 | -0.10071 | -0.068665 | 121.1014 | 121.1151 | 121.1472 | -0.091553 | 121.0281 | 121.0419 | 121.1288 | 0.004577
3211.6094 | 121.2616 | -121.0968 | 0.086975 | 0.013046 | 0.00049979 | 0.07044 | 0.029074 | -0.071032 | -0.026303 | -0.00092075 | 0.0073242 | 0.034306 | 0.0088504 | -0.041618 | -0.0078272 | 0.011173 | 0.032043 | 0 | 0.027466 | 0.045776 | 0.086975 | 0.036621 | -0.091553 | -0.027466 | 0.041199 | -0.10986 | 0.027466 | 0.032043 | 0.054932 | -0.013733 | 121.1334 | 121.0052 | 0 | 121.0968 | 121.1426 | 0.13733 | -0.054932 | 121.1517 | 121.0831 | -0.059509 | 121.0693 | 120.9869 | -0.09613 | -0.054932 | 121.1838 | 121.1288 | 121.1243 | -0.17853 | 121.1243 | 121.1288 | 121.138 | -0.10071
3213.3125 | 121.2799 | -121.138 | 0.10071 | 0.013046 | -0.00185 | 0.06809 | 0.028006 | -0.068896 | -0.018399 | 0.0022836 | 0.014954 | 0.036015 | 0.0088504 | -0.041618 | -0.0046228 | 0.010745 | 0.086975 | 0.064087 | 0.059509 | 0.13275 | 0.09613 | 0.045776 | -0.082397 | 0.059509 | 0.09613 | -0.059509 | 0.022888 | 0.032043 | 0.068665 | 0.018311 | 121.1838 | 121.0556 | -0.004578 | 121.2021 | 121.2708 | 0.21515 | -0.013733 | 121.2067 | 121.1563 | -0.07782 | 121.1975 | 121.0785 | -0.07782 | -0.068665 | 121.2341 | 121.225 | 121.1975 | -0.18311 | 121.1609 | 121.17 | 121.2341 | -0.082397
3215.0312 | 121.2433 | -121.0922 | 0.12817 | 0.0054168 | -0.0024908 | 0.066381 | 0.029929 | -0.065691 | -0.022031 | 0.00057465 | 0.022583 | 0.034947 | 0.0097048 | -0.040336 | -0.0061182 | 0.012241 | 0.041199 | 0.032043 | 0.050354 | 0.09613 | 0.09613 | 0.050354 | -0.082397 | 0.032043 | 0.073242 | -0.073242 | 0.013733 | 0.018311 | 0.059509 | 0 | 121.1426 | 121.0098 | -0.032044 | 121.1243 | 121.1884 | 0.17853 | -0.086975 | 121.1517 | 121.0922 | -0.11444 | 121.1243 | 121.019 | -0.073242 | -0.10986 | 121.1884 | 121.1334 | 121.1426 | -0.21057 | 121.106 | 121.1105 | 121.1655 | -0.12817
3216.7344 | 121.3211 | -121.0327 | 0.10986 | 0.0054168 | 0.004986 | 0.070654 | 0.029715 | -0.068896 | -0.027585 | 0.0027108 | 0.0073242 | 0.028965 | 0.0075686 | -0.043541 | -0.0078272 | 0.015018 | 0.059509 | 0.10529 | 0.10986 | 0.10071 | 0.054932 | 0.07782 | -0.036621 | 0.022888 | 0.10529 | -0.004578 | -0.041199 | -0.009155 | 0.09613 | 0.018311 | 121.1105 | 120.9961 | -0.054931 | 121.138 | 121.1334 | 0.13733 | -0.050354 | 121.1288 | 121.051 | -0.15106 | 121.0556 | 121.0281 | -0.022889 | -0.11902 | 121.0876 | 121.0922 | 121.1426 | -0.14648 | 120.9915 | 121.0236 | 121.138 | -0.091552
3218.5 | 120.3323 | -8.6517 | 112.0651 | 0.0054168 | -0.004627 | 0.071722 | 0.029074 | -0.068682 | -0.021817 | -0.00049335 | 0.0073242 | 0.034947 | 0.009064 | -0.041191 | -0.0052636 | 0.012454 | -0.045776 | -0.041199 | -0.018311 | 0.032043 | 0.059509 | -0.009155 | -0.13733 | -0.068665 | -0.004578 | -0.14648 | -0.022888 | 0.009155 | 0.022888 | -0.027466 | 8.6426 | 8.5144 | -112.0056 | 8.6105 | 8.6838 | 0.16937 | -112.1109 | 8.6746 | 8.6243 | -112.088 | 8.5831 | 8.5052 | -0.11902 | -112.056 | 8.7112 | 8.606 | 8.6334 | -112.2025 | 8.6288 | 8.6609 | 8.6472 | -112.0926
3220.2031 | 120.3873 | -9.2148 | 111.1816 | 0.013046 | -0.0020636 | 0.068731 | 0.026083 | -0.071673 | -0.022031 | 0.0033518 | 0.0073242 | 0.034092 | 0.0094912 | -0.041191 | -0.0048364 | 0.010959 | 0.013733 | -0.009155 | 0.013733 | 0.07782 | 0.050354 | 0.009155 | -0.11444 | -0.004578 | 0.045776 | -0.10529 | -0.032043 | -0.027466 | 0.032043 | -0.032043 | 9.2239 | 9.1003 | -111.1313 | 9.2056 | 9.2926 | 0.19226 | -111.1679 | 9.2468 | 9.1827 | -111.2137 | 9.2102 | 9.1095 | -0.073243 | -111.2091 | 9.2651 | 9.2285 | 9.2285 | -111.2961 | 9.1827 | 9.1873 | 9.2606 | -111.2137
3221.9062 | 121.2433 | -6.2164 | 114.8392 | 0.0054168 | 0.00092719 | 0.071081 | 0.025015 | -0.068468 | -0.022672 | 0.00057465 | 0.014954 | 0.034947 | 0.0060732 | -0.042045 | -0.0024866 | 0.01395 | -0.032043 | -0.041199 | -0.018311 | 0.032043 | 0.064087 | 0.013733 | -0.10529 | -0.054932 | -0.032043 | -0.14191 | -0.027466 | -0.013733 | 0.018311 | -0.013733 | 6.2302 | 6.1111 | -114.7751 | 6.1752 | 6.2485 | 0.13733 | -114.8712 | 6.2347 | 6.2027 | -114.8666 | 6.1615 | 6.0745 | -0.12817 | -114.8529 | 6.2805 | 6.1844 | 6.1981 | -114.9445 | 6.189 | 6.2027 | 6.1844 | -114.8529
3223.6094 | 121.2479 | -4.7012 | 116.423 | 0.013046 | 0.00049979 | 0.071935 | 0.030356 | -0.068468 | -0.029721 | 0.00036105 | 0.014954 | 0.030461 | 0.0094912 | -0.044822 | -0.0088952 | 0.0116 | 0.041199 | 0.11444 | 0.12817 | 0.1236 | 0 | 0.036621 | -0.09613 | 0.032043 | 0.14191 | 0 | -0.07782 | -0.059509 | 0.064087 | 0.004578 | 4.7379 | 4.6051 | -116.423 | 4.8157 | 4.8248 | 0.21973 | -116.3818 | 4.7653 | 4.7058 | -116.5009 | 4.7333 | 4.7012 | -0.004578 | -116.4825 | 4.7012 | 4.7424 | 4.8294 | -116.5192 | 4.6234 | 4.6417 | 4.8431 | -116.4185
3225.3906 | 121.1609 | -5.9143 | 114.592 | -0.0022127 | 0.00049979 | 0.071935 | 0.028647 | -0.067187 | -0.025022 | -0.001348 | 0.014954 | 0.034733 | 0.007355 | -0.041618 | -0.0080408 | 0.013522 | -0.009155 | -0.004578 | 0.022888 | 0.032043 | 0.045776 | 0.022888 | -0.09613 | -0.068665 | 0.004578 | -0.1236 | -0.022888 | -0.004578 | 0.050354 | -0.036621 | 5.9372 | 5.8182 | -114.5462 | 5.9097 | 5.9463 | 0.12817 | -114.6011 | 5.9647 | 5.8777 | -114.6149 | 5.8456 | 5.7907 | -0.086975 | -114.5966 | 5.9601 | 5.9052 | 5.9372 | -114.6881 | 5.8914 | 5.9097 | 5.9189 | -114.6286
3227.1094 | 121.2021 | -3.3142 | 117.7368 | 0.013046 | 0.00028619 | 0.072149 | 0.029929 | -0.069537 | -0.024808 | -0.00092075 | 0.022583 | 0.033879 | 0.009064 | -0.042259 | -0.0069726 | 0.010104 | -0.054932 | -0.027466 | 0 | 0.032043 | 0.059509 | 0 | -0.13733 | -0.09613 | -0.009155 | -0.14191 | -0.018311 | 0.004578 | 0 | -0.059509 | 3.3142 | 3.1769 | -117.6773 | 3.2867 | 3.3463 | 0.16937 | -117.7917 | 3.3142 | 3.2547 | -117.7551 | 3.2181 | 3.1723 | -0.082398 | -117.7322 | 3.3737 | 3.2593 | 3.3142 | -117.8741 | 3.2959 | 3.3188 | 3.3051 | -117.7963
3228.8438 | 121.2112 | -3.1174 | 118.1259 | 0.0054168 | -0.003559 | 0.070654 | 0.025015 | -0.06975 | -0.020108 | -0.00027975 | 0.0073242 | 0.034519 | 0.0088504 | -0.043754 | -0.0041956 | 0.012668 | 0.018311 | 0.009155 | 0.013733 | 0.068665 | 0.041199 | 0.022888 | -0.12817 | -0.041199 | -0.013733 | -0.16022 | -0.036621 | -0.013733 | 0.041199 | -0.041199 | 3.1403 | 2.9892 | -118.0847 | 3.1265 | 3.186 | 0.19684 | -118.1076 | 3.1586 | 3.0762 | -118.1625 | 3.0762 | 2.9572 | -0.11902 | -118.1396 | 3.1586 | 3.1357 | 3.1311 | -118.2541 | 3.0808 | 3.1036 | 3.1036 | -118.1671
3230.5625 | 121.3303 | -3.7765 | 117.5079 | 0.0054168 | 0.006054 | 0.07279 | 0.027579 | -0.069323 | -0.028867 | 0.0016428 | 0.014954 | 0.031315 | 0.007996 | -0.045677 | -0.0071862 | 0.015872 | -0.018311 | 0.059509 | 0.09613 | 0.073242 | 0.013733 | 0.050354 | -0.082397 | -0.018311 | 0.045776 | -0.059509 | -0.064087 | -0.041199 | 0.059509 | 0.009155 | 3.8269 | 3.6942 | -117.4942 | 3.8361 | 3.8498 | 0.15564 | -117.5262 | 3.8361 | 3.7857 | -117.572 | 3.7582 | 3.717 | -0.068664 | -117.5491 | 3.7903 | 3.7582 | 3.8727 | -117.5903 | 3.7125 | 3.7354 | 3.8223 | -117.4988
3232.2812 | 121.3028 | -9.1782 | 111.9232 | 0.0054168 | 0.0062676 | 0.072363 | 0.025229 | -0.070177 | -0.025449 | 0.00014745 | 0.0073242 | 0.033451 | 0.0047916 | -0.046318 | -0.0069726 | 0.015872 | 0.050354 | 0.073242 | 0.10529 | 0.091553 | 0.013733 | 0.036621 | -0.086975 | -0.009155 | 0.064087 | -0.045776 | -0.064087 | -0.027466 | 0.059509 | 0.009155 | 9.2148 | 9.0912 | -111.9095 | 9.2514 | 9.2697 | 0.17853 | -111.8729 | 9.2377 | 9.1873 | -111.9873 | 9.169 | 9.1324 | -0.054931 | -111.9507 | 9.1919 | 9.2285 | 9.2834 | -112.0102 | 9.1141 | 9.1507 | 9.2422 | -111.9141
3234.0156 | 121.1517 | -5.0629 | 115.6494 | 0.020676 | 0.004986 | 0.071081 | 0.024802 | -0.069323 | -0.026731 | 0.00014745 | 0.014954 | 0.030247 | 0.0058596 | -0.042472 | -0.0071862 | 0.014163 | 0.068665 | 0.07782 | 0.10529 | 0.11444 | 0.027466 | 0.045776 | -0.073242 | 0.018311 | 0.07782 | -0.018311 | -0.073242 | -0.068665 | 0.064087 | 0 | 5.1086 | 4.9896 | -115.6219 | 5.1407 | 5.1773 | 0.18768 | -115.5807 | 5.127 | 5.0629 | -115.7227 | 5.0812 | 5.0446 | -0.018311 | -115.7181 | 5.0903 | 5.1315 | 5.1682 | -115.7227 | 4.9896 | 4.9942 | 5.1407 | -115.6494
3235.7344 | 121.3303 | -4.3488 | 116.89 | 0.020676 | 0.0013544 | 0.069799 | 0.025229 | -0.068468 | -0.022244 | -6.615e-05 | 0.0073242 | 0.032597 | 0.0082096 | -0.0429 | -0.0037684 | 0.012241 | -0.009155 | -0.050354 | -0.027466 | 0.027466 | 0.045776 | 0.009155 | -0.11444 | -0.041199 | -0.036621 | -0.12817 | -0.032043 | -0.022888 | 0.022888 | -0.022888 | 4.3579 | 4.2343 | -116.8442 | 4.2984 | 4.3762 | 0.14191 | -116.8991 | 4.3716 | 4.3259 | -116.922 | 4.3076 | 4.2206 | -0.10529 | -116.9128 | 4.3945 | 4.3396 | 4.3213 | -117.0044 | 4.3167 | 4.3259 | 4.3121 | -116.9128
3237.4531 | 121.376 | -4.9942 | 115.535 | -0.0022127 | 0.0054132 | 0.069158 | 0.024802 | -0.067828 | -0.022458 | -0.00027975 | 0.0073242 | 0.034306 | 0.007996 | -0.041618 | -0.0027002 | 0.011173 | 0.022888 | -0.009155 | 0.036621 | 0.054932 | 0.041199 | 0.032043 | -0.091553 | 0.013733 | 0.059509 | -0.054932 | -0.064087 | -0.041199 | 0.073242 | -0.009155 | 5.0262 | 4.9026 | -115.4938 | 4.985 | 5.0491 | 0.14649 | -115.5121 | 5.0674 | 4.985 | -115.5991 | 5.0079 | 4.9393 | -0.045777 | -115.5762 | 5.0354 | 5.0171 | 5.0308 | -115.6265 | 4.9301 | 4.953 | 5.0537 | -115.5441
3239.1875 | 121.4539 | -113.4567 | 7.4615 | 0.0054168 | 0.003277 | 0.071294 | 0.029501 | -0.071673 | -0.027585 | -0.00027975 | 0.0073242 | 0.031101 | 0.0084232 | -0.0429 | -0.008468 | 0.011386 | 0.045776 | 0.054932 | 0.09613 | 0.11444 | 0.064087 | 0.073242 | -0.050354 | 0.022888 | 0.068665 | -0.018311 | -0.004578 | 0.013733 | 0.091553 | 0.032043 | 113.53 | 113.4064 | -7.3975 | 113.5117 | 113.5712 | 0.16479 | -7.4158 | 113.5483 | 113.4888 | -7.4661 | 113.4796 | 113.4384 | -0.050354 | -7.4478 | 113.5208 | 113.5025 | 113.5529 | -7.5119 | 113.4521 | 113.4705 | 113.5254 | -7.4295
3240.9688 | 121.4584 | -120.9732 | 0.16479 | 0.0054168 | 0.0030634 | 0.07044 | 0.026511 | -0.068896 | -0.025449 | 0.00207 | 0.014954 | 0.032597 | 0.0050052 | -0.04525 | -0.0054772 | 0.012454 | 0.12817 | 0.1236 | 0.15106 | 0.15564 | 0.050354 | 0.086975 | -0.036621 | 0.07782 | 0.13275 | 0.018311 | -0.036621 | -0.009155 | 0.10071 | 0.032043 | 121.0602 | 120.9366 | -0.11444 | 121.0968 | 121.1288 | 0.19226 | -0.036621 | 121.0739 | 121.0052 | -0.20142 | 121.051 | 120.9915 | -0.013732 | -0.17395 | 121.0236 | 121.1014 | 121.1243 | -0.20142 | 120.9366 | 120.9641 | 121.106 | -0.13275
3242.6875 | 121.4447 | -120.8496 | 0.30212 | 0.0054168 | 0.0047724 | 0.069372 | 0.026724 | -0.066332 | -0.025022 | -0.00070715 | 0.0073242 | 0.031956 | 0.0067142 | -0.043968 | -0.00505 | 0.011813 | 0.12817 | 0.13275 | 0.16022 | 0.15106 | 0.045776 | 0.086975 | -0.041199 | 0.086975 | 0.1236 | 0.013733 | -0.027466 | -0.004578 | 0.10529 | 0.041199 | 120.9366 | 120.8084 | -0.25635 | 120.9824 | 121.0007 | 0.19226 | -0.17395 | 120.9549 | 120.8908 | -0.32959 | 120.9366 | 120.8633 | -0.027466 | -0.3067 | 120.8954 | 120.9778 | 121.0098 | -0.34332 | 120.8221 | 120.845 | 120.9732 | -0.26093
3244.4688 | 121.4035 | -120.5704 | 0.6546 | -0.0022127 | -0.0012092 | 0.067876 | 0.02587 | -0.066759 | -0.020535 | 0.0027108 | 0.014954 | 0.035801 | 0.0067142 | -0.0429 | -0.0074 | 0.010318 | 0.068665 | 0.032043 | 0.054932 | 0.10986 | 0.10529 | 0.050354 | -0.07782 | 0.032043 | 0.068665 | -0.086975 | 0 | 0.018311 | 0.073242 | 0.004578 | 120.6207 | 120.4926 | -0.54932 | 120.6024 | 120.6802 | 0.18768 | -0.58594 | 120.6436 | 120.575 | -0.6546 | 120.6024 | 120.4834 | -0.091553 | -0.63629 | 120.6757 | 120.639 | 120.6253 | -0.73242 | 120.5704 | 120.5887 | 120.639 | -0.65002
3246.1719 | 121.344 | -120.8176 | 0.41199 | 0.0054168 | -0.00099541 | 0.067022 | 0.029501 | -0.068468 | -0.022031 | -6.615e-05 | 0.0073242 | 0.034306 | 0.010773 | -0.040123 | -0.0052636 | 0.010745 | 0.059509 | 0.045776 | 0.064087 | 0.11444 | 0.09613 | 0.041199 | -0.07782 | 0.045776 | 0.082397 | -0.064087 | 0.018311 | 0.045776 | 0.068665 | 0.022888 | 120.8588 | 120.7397 | -0.31586 | 120.8633 | 120.932 | 0.19226 | -0.35248 | 120.8862 | 120.8405 | -0.39368 | 120.8633 | 120.7535 | -0.086975 | -0.36621 | 120.9137 | 120.8771 | 120.8817 | -0.48981 | 120.8359 | 120.8633 | 120.9 | -0.3891
3247.9375 | 121.4401 | -120.8771 | 0.36621 | 0.0054168 | 0.00092719 | 0.072363 | 0.029929 | -0.069109 | -0.029935 | 0.00078825 | 0.014954 | 0.030033 | 0.006287 | -0.046104 | -0.0095362 | 0.014804 | 0.082397 | 0.15564 | 0.17853 | 0.15106 | 0.064087 | 0.082397 | -0.054932 | 0.073242 | 0.1831 | 0.036621 | -0.027466 | -0.004578 | 0.09613 | 0.050354 | 120.9595 | 120.8221 | -0.30212 | 121.0327 | 121.0281 | 0.20599 | -0.28381 | 120.9732 | 120.9274 | -0.39368 | 120.9503 | 120.9137 | -0.013733 | -0.37079 | 120.9412 | 120.9595 | 121.0556 | -0.42114 | 120.8496 | 120.8725 | 121.0602 | -0.31586
3249.6406 | 121.3394 | -120.8221 | 0.44861 | -0.0022127 | -0.0024908 | 0.069372 | 0.027152 | -0.067187 | -0.02139 | 0.0024972 | 0.0073242 | 0.035588 | 0.0086368 | -0.044609 | -0.0029138 | 0.010745 | 0.022888 | -0.004578 | 0.032043 | 0.086975 | 0.082397 | 0.064087 | -0.082397 | -0.022888 | 0.004578 | -0.13275 | 0.009155 | 0.022888 | 0.073242 | -0.013733 | 120.8862 | 120.7397 | -0.36621 | 120.8176 | 120.9091 | 0.16937 | -0.42572 | 120.8954 | 120.8084 | -0.43945 | 120.7993 | 120.6894 | -0.11902 | -0.42572 | 120.9045 | 120.845 | 120.8542 | -0.531 | 120.8313 | 120.845 | 120.8267 | -0.46234
3251.3438 | 121.4539 | -120.9595 | 0.27008 | 0.013046 | 0.0034906 | 0.071294 | 0.02587 | -0.0674 | -0.023953 | 0.00078825 | 0.0073242 | 0.033238 | 0.0069278 | -0.043754 | -0.0031274 | 0.014163 | 0.009155 | -0.009155 | 0.027466 | 0.073242 | 0.09613 | 0.045776 | -0.064087 | -0.004578 | 0.027466 | -0.068665 | 0.009155 | 0.013733 | 0.086975 | 0.009155 | 121.0052 | 120.8954 | -0.17395 | 120.9503 | 121.0327 | 0.13733 | -0.26093 | 121.0464 | 120.9686 | -0.26093 | 120.9549 | 120.8908 | -0.07782 | -0.25635 | 121.0556 | 120.9686 | 120.9869 | -0.33417 | 120.9686 | 120.9732 | 120.9869 | -0.26093
3253.0781 | 121.4722 | -120.9366 | 0.32959 | 0.0054168 | 0.0041314 | 0.071722 | 0.029929 | -0.069964 | -0.030149 | 0.0014292 | 0.014954 | 0.030247 | 0.0067142 | -0.044609 | -0.0097498 | 0.015445 | 0.009155 | 0.054932 | 0.10529 | 0.11902 | 0.073242 | 0.07782 | -0.045776 | 0.022888 | 0.10986 | -0.004578 | -0.018311 | 0 | 0.10071 | 0.027466 | 121.0144 | 120.8908 | -0.25635 | 120.9915 | 121.0556 | 0.16479 | -0.32043 | 121.0373 | 120.9641 | -0.3479 | 120.9595 | 120.932 | -0.032044 | -0.32959 | 121.0098 | 120.9457 | 121.0419 | -0.37537 | 120.9183 | 120.9366 | 121.0464 | -0.30212
3254.7969 | 121.4355 | -120.8542 | 0.36621 | 0.0054168 | 0.001568 | 0.070226 | 0.029715 | -0.067187 | -0.029294 | -0.001348 | 0.014954 | 0.031315 | 0.0075686 | -0.041404 | -0.0097498 | 0.011813 | 0.10529 | 0.16022 | 0.17853 | 0.16937 | 0.054932 | 0.082397 | -0.045776 | 0.082397 | 0.19226 | 0.045776 | -0.027466 | 0 | 0.10529 | 0.059509 | 120.9366 | 120.8084 | -0.31128 | 121.0144 | 121.0236 | 0.21515 | -0.26093 | 120.9595 | 120.9137 | -0.39368 | 120.9366 | 120.9 | -0.013733 | -0.36621 | 120.9091 | 120.9595 | 121.0327 | -0.41199 | 120.8267 | 120.8542 | 121.0464 | -0.3067
3256.5156 | 121.4859 | -120.9503 | 0.32044 | 0.0054168 | 0.00092719 | 0.071081 | 0.029715 | -0.068468 | -0.026731 | -0.0015616 | 0.022583 | 0.029392 | 0.0094912 | -0.042472 | -0.0078272 | 0.011173 | 0.10529 | 0.15106 | 0.16479 | 0.16479 | 0.064087 | 0.086975 | -0.050354 | 0.068665 | 0.17395 | 0.032043 | -0.027466 | 0 | 0.10071 | 0.027466 | 121.0373 | 120.9 | -0.25635 | 121.1014 | 121.1151 | 0.21515 | -0.21515 | 121.051 | 120.9778 | -0.3479 | 121.019 | 120.9824 | 0.004577 | -0.32044 | 121.0144 | 121.0556 | 121.1151 | -0.37079 | 120.9229 | 120.9503 | 121.1243 | -0.29297
3258.2188 | 121.312 | -119.3939 | 1.918 | 0.0054168 | -0.00014101 | 0.069158 | 0.027792 | -0.068255 | -0.02374 | -0.0022024 | 0.014954 | 0.033879 | 0.010346 | -0.043327 | -0.006759 | 0.010745 | 0.027466 | 0.004578 | 0.041199 | 0.073242 | 0.086975 | 0.045776 | -0.07782 | -0.022888 | 0.022888 | -0.10071 | 0.013733 | 0.036621 | 0.073242 | 0 | 119.4397 | 119.3161 | -1.8311 | 119.3985 | 119.4672 | 0.15106 | -1.8906 | 119.4672 | 119.3939 | -1.9043 | 119.371 | 119.2932 | -0.10071 | -1.8814 | 119.4809 | 119.4214 | 119.4351 | -1.9958 | 119.4077 | 119.4305 | 119.4168 | -1.918
3260 | 121.4355 | -121.138 | 0.2243 | 0.0054168 | -0.004627 | 0.071935 | 0.030569 | -0.069109 | -0.021817 | -0.001348 | 0.0073242 | 0.033024 | 0.007996 | -0.042259 | -0.0069726 | 0.011386 | 0.013733 | -0.013733 | 0.009155 | 0.064087 | 0.10529 | 0.036621 | -0.082397 | -0.027466 | 0.032043 | -0.11444 | 0.009155 | 0.032043 | 0.082397 | 0.009155 | 121.1746 | 121.0556 | -0.11902 | 121.1243 | 121.2021 | 0.14648 | -0.21057 | 121.2204 | 121.1472 | -0.21515 | 121.1105 | 121.0236 | -0.1236 | -0.19226 | 121.2433 | 121.1517 | 121.1472 | -0.3067 | 121.1472 | 121.17 | 121.17 | -0.21515
3261.7031 | 121.4218 | -119.7464 | 1.6113 | 0.013046 | -0.00014101 | 0.071294 | 0.031424 | -0.069323 | -0.026303 | 0.00014745 | 0.0073242 | 0.030888 | 0.0084232 | -0.044395 | -0.0093226 | 0.013095 | 0.09613 | 0.14648 | 0.16479 | 0.15564 | 0.068665 | 0.091553 | -0.041199 | 0.073242 | 0.16937 | 0.018311 | -0.027466 | 0 | 0.10529 | 0.027466 | 119.838 | 119.7052 | -1.5427 | 119.8929 | 119.902 | 0.19684 | -1.5152 | 119.8517 | 119.7739 | -1.6388 | 119.8196 | 119.7647 | -0.009155 | -1.6113 | 119.8151 | 119.8425 | 119.9112 | -1.6525 | 119.7189 | 119.7464 | 119.9158 | -1.5839
3263.4688 | 121.1563 | -117.2699 | 4.0833 | 0.020676 | 7.2586e-05 | 0.070226 | 0.030783 | -0.068896 | -0.023526 | -0.001348 | 0.0073242 | 0.034306 | 0.0097048 | -0.04055 | -0.0065454 | 0.012027 | 0.018311 | 0.022888 | 0.036621 | 0.086975 | 0.10529 | 0.045776 | -0.068665 | -0.041199 | 0.041199 | -0.09613 | 0.013733 | 0.027466 | 0.059509 | 0.009155 | 117.3157 | 117.2012 | -3.978 | 117.2928 | 117.3569 | 0.15564 | -4.0649 | 117.3294 | 117.2791 | -4.0695 | 117.2287 | 117.1738 | -0.10528 | -4.0558 | 117.3752 | 117.2882 | 117.3065 | -4.1519 | 117.2836 | 117.2974 | 117.3111 | -4.0741
3265.1875 | 121.4539 | -119.9066 | 1.4053 | 0.020676 | -0.0012092 | 0.070867 | 0.029074 | -0.06975 | -0.021817 | -0.001348 | 0.0073242 | 0.033665 | 0.0088504 | -0.042686 | -0.0059046 | 0.0116 | -0.004578 | 0.013733 | 0.022888 | 0.091553 | 0.09613 | 0.045776 | -0.091553 | -0.004578 | 0.050354 | -0.09613 | 0.018311 | 0.022888 | 0.068665 | -0.004578 | 119.9524 | 119.8151 | -1.3092 | 119.9203 | 119.9982 | 0.18311 | -1.4099 | 119.9753 | 119.902 | -1.387 | 119.902 | 119.8105 | -0.091552 | -1.3824 | 120.0027 | 119.902 | 119.9295 | -1.4969 | 119.9249 | 119.9295 | 119.957 | -1.4099
3266.9531 | 121.3303 | -118.7805 | 2.4857 | -0.0022127 | -0.00099541 | 0.072576 | 0.029715 | -0.069109 | -0.027371 | -6.615e-05 | 0.0073242 | 0.031315 | 0.010132 | -0.0429 | -0.0059046 | 0.012027 | 0.059509 | 0.11902 | 0.11444 | 0.13275 | 0.073242 | 0.054932 | -0.059509 | 0.013733 | 0.10071 | -0.050354 | 0.004578 | 0.036621 | 0.064087 | 0.013733 | 118.8354 | 118.721 | -2.4124 | 118.8995 | 118.9133 | 0.19226 | -2.4261 | 118.8446 | 118.7943 | -2.4811 | 118.7943 | 118.7302 | -0.064087 | -2.449 | 118.8538 | 118.84 | 118.895 | -2.5452 | 118.7851 | 118.8171 | 118.8812 | -2.4719
3268.6719 | 121.4859 | -121.0693 | 0.26093 | 0.013046 | -0.0016364 | 0.07044 | 0.027579 | -0.066546 | -0.020322 | 0.00036105 | 0.0073242 | 0.033238 | 0.0088504 | -0.040763 | -0.0046228 | 0.011386 | 0.013733 | 0.018311 | 0.032043 | 0.091553 | 0.091553 | 0.050354 | -0.073242 | 0.009155 | 0.073242 | -0.091553 | 0.009155 | 0.018311 | 0.059509 | -0.004578 | 121.1197 | 120.9961 | -0.16937 | 121.0876 | 121.1609 | 0.16479 | -0.24719 | 121.1288 | 121.0648 | -0.25177 | 121.0785 | 120.9778 | -0.086975 | -0.24261 | 121.1609 | 121.0831 | 121.1014 | -0.33417 | 121.0785 | 121.0876 | 121.1426 | -0.2655
3270.3906 | 120.163 | -119.8929 | 0.10071 | -0.0022127 | -0.0031318 | 0.06809 | 0.026938 | -0.069109 | -0.020535 | 0.0016428 | 0.0073242 | 0.033879 | 0.0092776 | -0.039909 | -0.0027002 | 0.0116 | 0.050354 | 0.07782 | 0.07782 | 0.11444 | 0.091553 | 0.045776 | -0.064087 | 0.022888 | 0.068665 | -0.07782 | 0.004578 | 0.004578 | 0.068665 | 0.013733 | 119.9387 | 119.8288 | -0.009155 | 119.9707 | 120.0073 | 0.17853 | -0.050354 | 119.9615 | 119.9066 | -0.09613 | 119.9158 | 119.8151 | -0.091553 | -0.09613 | 119.9844 | 119.9432 | 119.9707 | -0.1648 | 119.8975 | 119.8975 | 119.9615 | -0.086975
3272.1094 | 120.0256 | -120.6345 | 0.10071 | 0.013046 | 0.00049979 | 0.071294 | 0.024588 | -0.069109 | -0.021817 | 0.0016428 | 0.0073242 | 0.033024 | 0.0084232 | -0.041832 | -0.0046228 | 0.013095 | -0.013733 | -0.009155 | 0.004578 | 0.059509 | 0.10071 | 0.022888 | -0.10071 | -0.041199 | -0.022888 | -0.12817 | 0.009155 | 0.041199 | 0.064087 | 0.027466 | 120.6573 | 120.5338 | 0 | 120.6253 | 120.694 | 0.16022 | -0.11444 | 120.6985 | 120.6619 | -0.091553 | 120.5933 | 120.5063 | -0.15564 | -0.059509 | 120.7352 | 120.6207 | 120.639 | -0.20142 | 120.6436 | 120.6757 | 120.6116 | -0.073242
3273.875 | 120.7947 | -120.3598 | 0.32501 | 0.0054168 | 7.2586e-05 | 0.071722 | 0.029501 | -0.069537 | -0.02844 | -0.00092075 | 0.014954 | 0.031956 | 0.0054324 | -0.043968 | -0.0063318 | 0.014163 | 0.050354 | 0.11902 | 0.13275 | 0.15106 | 0.059509 | 0.07782 | -0.050354 | 0.009155 | 0.14191 | -0.027466 | 0.009155 | 0.041199 | 0.091553 | 0.013733 | 120.4376 | 120.3094 | -0.2655 | 120.4788 | 120.5109 | 0.20142 | -0.27466 | 120.4514 | 120.3735 | -0.31586 | 120.369 | 120.3323 | -0.041199 | -0.28381 | 120.4193 | 120.4102 | 120.4926 | -0.37537 | 120.369 | 120.401 | 120.5017 | -0.31128
3275.5781 | 121.0327 | -120.6802 | 0.10986 | 0.013046 | 0.0058404 | 0.071935 | 0.029288 | -0.066973 | -0.02844 | 0.00036105 | 0.0073242 | 0.029179 | 0.0071414 | -0.044395 | -0.0099634 | 0.012668 | 0.032043 | 0.068665 | 0.10071 | 0.10529 | 0.064087 | 0.064087 | -0.045776 | 0.004578 | 0.086975 | -0.027466 | -0.018311 | -0.013733 | 0.10529 | 0.045776 | 120.7443 | 120.6345 | -0.045776 | 120.7489 | 120.7855 | 0.15106 | -0.07782 | 120.7855 | 120.726 | -0.12817 | 120.6848 | 120.6528 | -0.073242 | -0.1236 | 120.7443 | 120.7123 | 120.7809 | -0.15564 | 120.6619 | 120.6665 | 120.7672 | -0.064087
3277.2969 | 121.0373 | -120.7947 | 0.091553 | -0.0098417 | -0.0039862 | 0.07044 | 0.031638 | -0.068682 | -0.020963 | 0.00014745 | 0.022583 | 0.033238 | 0.0086368 | -0.04055 | -0.0061182 | 0.012668 | 0 | 0.004578 | 0.018311 | 0.082397 | 0.086975 | 0.041199 | -0.10529 | -0.032043 | 0.027466 | -0.10529 | 0.032043 | 0.022888 | 0.073242 | -0.027466 | 120.8359 | 120.6894 | -0.004578 | 120.7993 | 120.8771 | 0.18768 | -0.091553 | 120.8679 | 120.7672 | -0.05951 | 120.7626 | 120.6894 | -0.07782 | -0.068665 | 120.8817 | 120.7947 | 120.813 | -0.19684 | 120.8267 | 120.8176 | 120.8221 | -0.11902
3279 | 121.0693 | -120.6207 | 0.23804 | 0.028305 | 0.0054132 | 0.073431 | 0.026297 | -0.067614 | -0.024808 | 0.00057465 | 0.0073242 | 0.030674 | 0.0050052 | -0.044822 | -0.0041956 | 0.011813 | 0.09613 | 0.13733 | 0.15106 | 0.16022 | 0.041199 | 0.086975 | -0.027466 | 0.082397 | 0.13733 | 0.009155 | -0.027466 | -0.018311 | 0.10529 | 0.036621 | 120.7077 | 120.5933 | -0.19684 | 120.7581 | 120.7809 | 0.18768 | -0.14191 | 120.726 | 120.6573 | -0.2655 | 120.7031 | 120.6299 | -0.027466 | -0.25635 | 120.6619 | 120.7169 | 120.7718 | -0.2655 | 120.5933 | 120.6024 | 120.7581 | -0.20142
3280.7188 | 121.1746 | -120.8176 | 0.054932 | 0.013046 | 0.0041314 | 0.072149 | 0.026083 | -0.070391 | -0.023526 | 0.00057465 | -0.0003053 | 0.033024 | 0.0067142 | -0.042472 | -0.0029138 | 0.013522 | 0.036621 | 0.027466 | 0.064087 | 0.10071 | 0.086975 | 0.07782 | -0.050354 | 0.059509 | 0.091553 | -0.027466 | -0.022888 | 0.009155 | 0.082397 | 0.045776 | 120.8954 | 120.7672 | 0.032043 | 120.845 | 120.9183 | 0.15106 | -0.018311 | 120.9 | 120.8633 | -0.07782 | 120.8771 | 120.7901 | -0.073242 | -0.045777 | 120.9045 | 120.8542 | 120.8817 | -0.10529 | 120.7947 | 120.8267 | 120.9091 | -0.009156
3282.4531 | 121.0785 | -120.9183 | 0.09613 | 0.0054168 | 7.2586e-05 | 0.070226 | 0.02822 | -0.066332 | -0.021604 | 0.003138 | 0.014954 | 0.033238 | 0.010773 | -0.041832 | -0.0061182 | 0.011386 | -0.022888 | -0.045776 | -0.009155 | 0.054932 | 0.10071 | 0.050354 | -0.064087 | -0.032043 | -0.027466 | -0.13275 | 0.018311 | 0.041199 | 0.050354 | 0.013733 | 120.9686 | 120.8542 | 0.004578 | 120.8725 | 120.9732 | 0.11902 | -0.11902 | 120.9686 | 120.932 | -0.077819 | 120.8862 | 120.7855 | -0.14648 | -0.054931 | 121.019 | 120.8954 | 120.9091 | -0.16022 | 120.9366 | 120.9595 | 120.8908 | -0.082397
3284.1562 | 121.2204 | -120.6894 | 0.24261 | 0.013046 | 0.0022088 | 0.070654 | 0.028647 | -0.067614 | -0.025022 | 0.0012154 | 0.0073242 | 0.02982 | 0.0084232 | -0.042472 | -0.0071862 | 0.014163 | 0.086975 | 0.10529 | 0.13275 | 0.13733 | 0.045776 | 0.082397 | -0.041199 | 0.068665 | 0.12817 | 0.004578 | -0.032043 | -0.018311 | 0.10986 | 0.054932 | 120.7718 | 120.6482 | -0.19684 | 120.7947 | 120.8267 | 0.17853 | -0.15564 | 120.7993 | 120.7443 | -0.27466 | 120.7581 | 120.694 | -0.050354 | -0.26093 | 120.7352 | 120.7764 | 120.8221 | -0.28381 | 120.6573 | 120.6711 | 120.8176 | -0.18768
3285.9062 | 121.2845 | -120.9229 | 0.054932 | 0.0054168 | 0.0030634 | 0.074712 | 0.030356 | -0.072314 | -0.030576 | -0.0024162 | 0.0073242 | 0.02747 | 0.0088504 | -0.043968 | -0.011459 | 0.014804 | 0.041199 | 0.10986 | 0.11902 | 0.12817 | 0.073242 | 0.059509 | -0.054932 | 0.041199 | 0.14191 | 0.022888 | -0.018311 | 0 | 0.086975 | 0.027466 | 120.9824 | 120.8679 | 0.01831 | 121.0327 | 121.051 | 0.18311 | -0.013733 | 121.0098 | 120.9503 | -0.073243 | 120.9641 | 120.9457 | -0.004578 | -0.054932 | 120.9961 | 120.9641 | 121.0419 | -0.10986 | 120.9045 | 120.9229 | 121.0648 | -0.027466
3287.625 | 121.1746 | -121.0007 | 0.068665 | 0.013046 | -0.0031318 | 0.069799 | 0.027579 | -0.068255 | -0.022672 | -0.00049335 | 0.022583 | 0.034519 | 0.006287 | -0.04055 | -0.0041956 | 0.0094635 | 0.068665 | 0.036621 | 0.064087 | 0.10529 | 0.10529 | 0.059509 | -0.068665 | 0.032043 | 0.07782 | -0.059509 | 0.013733 | 0.022888 | 0.07782 | 0.018311 | 121.0602 | 120.932 | 0.036621 | 121.0373 | 121.106 | 0.17395 | 0 | 121.0785 | 121.019 | -0.054932 | 121.0327 | 120.9412 | -0.07782 | -0.045777 | 121.106 | 121.0693 | 121.0648 | -0.13733 | 121.0144 | 121.0236 | 121.0785 | -0.050354
3289.4062 | 121.1746 | -121.019 | 0.10071 | 0.013046 | -0.00078181 | 0.071935 | 0.032278 | -0.071032 | -0.027585 | -0.0017752 | 0.0073242 | 0.031315 | 0.0097048 | -0.042259 | -0.0080408 | 0.010959 | 0.004578 | 0.045776 | 0.050354 | 0.073242 | 0.082397 | 0.041199 | -0.073242 | -0.041199 | 0.050354 | -0.10071 | 0.009155 | 0.045776 | 0.068665 | 0.009155 | 121.0602 | 120.9457 | -0.018311 | 121.0648 | 121.0922 | 0.14648 | -0.09613 | 121.0876 | 121.0281 | -0.091553 | 120.9778 | 120.9183 | -0.10986 | -0.054932 | 121.1014 | 121.0236 | 121.0693 | -0.17395 | 121.0281 | 121.0648 | 121.0693 | -0.091553
3291.125 | 121.2296 | -121.0327 | 0.09613 | 0.0054168 | -0.005268 | 0.071081 | 0.026724 | -0.069109 | -0.024381 | 0.0016428 | -0.0003053 | 0.031315 | 0.0084232 | -0.042686 | -0.0069726 | 0.010104 | 0.009155 | 0.013733 | 0.022888 | 0.086975 | 0.09613 | 0.054932 | -0.073242 | -0.022888 | 0.041199 | -0.09613 | 0.004578 | 0.036621 | 0.054932 | 0.004578 | 121.0876 | 120.9595 | 0 | 121.0464 | 121.1197 | 0.16022 | -0.086975 | 121.0876 | 121.0373 | -0.091552 | 121.0098 | 120.9366 | -0.10071 | -0.059509 | 121.1288 | 121.0419 | 121.0556 | -0.16937 | 121.0373 | 121.0693 | 121.0739 | -0.091552
3292.8438 | 121.3028 | -121.0556 | 0.068665 | -0.0022127 | 0.0039178 | 0.074499 | 0.028647 | -0.066759 | -0.029508 | -6.615e-05 | 0.014954 | 0.029392 | 0.0069278 | -0.043968 | -0.0069726 | 0.01395 | 0.018311 | 0.07782 | 0.10986 | 0.11902 | 0.059509 | 0.091553 | -0.036621 | 0.009155 | 0.086975 | -0.022888 | -0.018311 | 0.009155 | 0.09613 | 0.032043 | 121.1472 | 121.019 | -0.009156 | 121.1334 | 121.1746 | 0.15564 | -0.050354 | 121.1517 | 121.0876 | -0.086976 | 121.0648 | 121.0327 | -0.054931 | -0.05951 | 121.1151 | 121.0739 | 121.1655 | -0.10529 | 121.0373 | 121.0648 | 121.1426 | -0.036622
3294.5469 | 121.2753 | -121.0556 | 0.086975 | 0.028305 | -0.0041998 | 0.068517 | 0.030356 | -0.0674 | -0.022244 | -0.0015616 | 0.0073242 | 0.034733 | 0.0086368 | -0.041618 | -0.0071862 | 0.0098907 | 0.022888 | -0.004578 | 0.032043 | 0.091553 | 0.10071 | 0.050354 | -0.07782 | 0.013733 | 0.050354 | -0.082397 | 0.022888 | 0.032043 | 0.068665 | 0 | 121.106 | 120.9778 | 0.013733 | 121.051 | 121.1472 | 0.16937 | -0.064087 | 121.1243 | 121.0556 | -0.064087 | 121.0693 | 120.9732 | -0.082397 | -0.054932 | 121.1563 | 121.0785 | 121.0876 | -0.16479 | 121.0785 | 121.0876 | 121.106 | -0.086975
3296.2812 | 121.2479 | -121.0602 | 0.07782 | 0.028305 | -0.004627 | 0.067236 | 0.029074 | -0.067614 | -0.02139 | 0.0010018 | 0.0073242 | 0.035374 | 0.0092776 | -0.043327 | -0.0046228 | 0.011173 | 0.068665 | 0.050354 | 0.073242 | 0.10071 | 0.10529 | 0.050354 | -0.091553 | 0.013733 | 0.073242 | -0.07782 | -0.004578 | 0.032043 | 0.068665 | 0.009155 | 121.1105 | 120.9686 | 0.027466 | 121.1105 | 121.1609 | 0.19226 | -0.009155 | 121.1288 | 121.0693 | -0.082398 | 121.0739 | 120.9824 | -0.086975 | -0.045777 | 121.1655 | 121.1288 | 121.1334 | -0.16937 | 121.0556 | 121.0922 | 121.1334 | -0.068665
3297.9844 | 121.3669 | -121.0648 | 0.059509 | 0.0054168 | 0.0019952 | 0.067876 | 0.025443 | -0.067828 | -0.025022 | 0.00036105 | 0.014954 | 0.033665 | 0.007996 | -0.040336 | -0.0061182 | 0.012027 | 0.013733 | 0.004578 | 0.036621 | 0.073242 | 0.10071 | 0.073242 | -0.068665 | 0.018311 | 0.050354 | -0.050354 | -0.027466 | 0.009155 | 0.086975 | 0.022888 | 121.138 | 120.9961 | 0.041199 | 121.0693 | 121.138 | 0.14191 | -0.045776 | 121.1517 | 121.0876 | -0.086975 | 121.0831 | 121.0144 | -0.073242 | -0.050354 | 121.1655 | 121.0785 | 121.1014 | -0.12817 | 121.0373 | 121.0739 | 121.1151 | -0.036621
3299.7031 | 121.3531 | -121.0831 | 0.064087 | 0.013046 | 0.0028498 | 0.069799 | 0.026297 | -0.068896 | -0.025022 | 0.0022836 | 0.014954 | 0.030888 | 0.0058596 | -0.041832 | -0.0041956 | 0.013736 | 0.059509 | 0.086975 | 0.10529 | 0.12817 | 0.082397 | 0.086975 | -0.045776 | 0.07782 | 0.13733 | 0 | -0.027466 | -0.018311 | 0.11444 | 0.045776 | 121.17 | 121.0373 | 0.01831 | 121.17 | 121.2112 | 0.17395 | -0.004578 | 121.1975 | 121.1288 | -0.091553 | 121.1609 | 121.0831 | -0.045776 | -0.082398 | 121.1655 | 121.1426 | 121.1884 | -0.10986 | 121.0556 | 121.0648 | 121.2204 | -0.018311
3301.4688 | 121.3806 | -121.0968 | 0.07782 | 0.0054168 | 0.0047724 | 0.073644 | 0.029715 | -0.068255 | -0.02908 | -0.00027975 | -0.0003053 | 0.029606 | 0.0067142 | -0.043968 | -0.010177 | 0.012882 | 0.022888 | 0.054932 | 0.10529 | 0.11902 | 0.050354 | 0.086975 | -0.064087 | 0.004578 | 0.07782 | -0.009155 | -0.009155 | 0.027466 | 0.086975 | 0.032043 | 121.1838 | 121.0327 | -0.027466 | 121.1517 | 121.2158 | 0.18311 | -0.054932 | 121.1838 | 121.1288 | -0.086975 | 121.1014 | 121.0876 | -0.041198 | -0.050354 | 121.1472 | 121.1197 | 121.2021 | -0.14191 | 121.0876 | 121.1243 | 121.1746 | -0.045777
3303.1875 | 121.4218 | -121.0968 | 0.054932 | 0.013046 | 0.0045588 | 0.071935 | 0.029929 | -0.068041 | -0.029294 | -0.001348 | 0.014954 | 0.030033 | 0.0084232 | -0.041832 | -0.0099634 | 0.0116 | 0.10529 | 0.14191 | 0.15106 | 0.14648 | 0.050354 | 0.082397 | -0.064087 | 0.073242 | 0.17395 | 0.068665 | -0.018311 | 0.009155 | 0.10529 | 0.041199 | 121.1792 | 121.0327 | -0.004578 | 121.2387 | 121.2433 | 0.21057 | 0.050354 | 121.2021 | 121.138 | -0.073243 | 121.17 | 121.1655 | 0.027466 | -0.045777 | 121.1472 | 121.2021 | 121.2479 | -0.11902 | 121.0785 | 121.106 | 121.2708 | -0.013733
3304.9531 | 121.3623 | -121.1563 | 0.10071 | 0.013046 | -0.00099541 | 0.067876 | 0.023093 | -0.068896 | -0.020322 | -0.00092075 | 0.014954 | 0.034947 | 0.0071414 | -0.042045 | -0.0014184 | 0.011813 | 0.013733 | -0.032043 | 0.004578 | 0.068665 | 0.10071 | 0.045776 | -0.082397 | -0.022888 | -0.022888 | -0.1236 | 0.009155 | 0.022888 | 0.082397 | 0 | 121.2021 | 121.0739 | 0 | 121.1243 | 121.225 | 0.15106 | -0.086975 | 121.2387 | 121.1563 | -0.091553 | 121.1334 | 121.0327 | -0.1236 | -0.07782 | 121.257 | 121.17 | 121.1609 | -0.18311 | 121.1655 | 121.1792 | 121.1334 | -0.10071
3306.6562 | 121.4172 | -121.1426 | 0.082397 | 0.0054168 | 0.00049979 | 0.07044 | 0.026938 | -0.067187 | -0.02139 | 0.0016428 | 0.014954 | 0.033238 | 0.0086368 | -0.042259 | -0.0037684 | 0.013309 | 0 | -0.013733 | 0.009155 | 0.07782 | 0.11902 | 0.041199 | -0.064087 | -0.009155 | 0 | -0.10071 | 0.013733 | 0.022888 | 0.068665 | 0.009155 | 121.1838 | 121.0785 | 0.036622 | 121.1288 | 121.2204 | 0.14191 | -0.082397 | 121.2112 | 121.1517 | -0.068664 | 121.1334 | 121.0419 | -0.10986 | -0.059509 | 121.2616 | 121.1426 | 121.1517 | -0.14648 | 121.1563 | 121.1655 | 121.1426 | -0.073242
3308.3594 | 121.3531 | -121.1838 | 0.054932 | 0.013046 | 0.0034906 | 0.071508 | 0.026511 | -0.068896 | -0.026517 | 0.00036105 | 0.0073242 | 0.031529 | 0.0067142 | -0.044609 | -0.0082544 | 0.012668 | 0.10071 | 0.11902 | 0.15106 | 0.15106 | 0.036621 | 0.086975 | -0.027466 | 0.068665 | 0.13733 | 0.018311 | -0.022888 | -0.013733 | 0.11444 | 0.054932 | 121.2708 | 121.1563 | -0.018311 | 121.3028 | 121.3348 | 0.17853 | 0.045776 | 121.2982 | 121.2387 | -0.07782 | 121.2524 | 121.2021 | -0.036621 | -0.068665 | 121.2204 | 121.2845 | 121.3348 | -0.082398 | 121.1609 | 121.17 | 121.3211 | 0
3310.0938 | 121.2982 | -121.2021 | 0.12817 | 0.013046 | 0.00049979 | 0.072363 | 0.030356 | -0.068896 | -0.026517 | 0.00014745 | 0.014954 | 0.031529 | 0.007355 | -0.043968 | -0.0091088 | 0.011386 | 0.068665 | 0.09613 | 0.11902 | 0.13275 | 0.082397 | 0.068665 | -0.054932 | 0.004578 | 0.09613 | -0.050354 | -0.004578 | 0.013733 | 0.064087 | 0.009155 | 121.2708 | 121.1472 | -0.045777 | 121.2982 | 121.3348 | 0.18768 | -0.059509 | 121.2662 | 121.2112 | -0.13275 | 121.2067 | 121.1517 | -0.059509 | -0.11444 | 121.2845 | 121.2708 | 121.3211 | -0.18311 | 121.1975 | 121.2158 | 121.2982 | -0.11902
3311.7969 | 121.4264 | -121.1517 | 0.11444 | 0.0054168 | 0.00092719 | 0.073003 | 0.030142 | -0.068468 | -0.027799 | -0.00070715 | 0.0073242 | 0.028752 | 0.0082096 | -0.044181 | -0.0080408 | 0.013095 | 0.10986 | 0.14648 | 0.17853 | 0.16937 | 0.064087 | 0.082397 | -0.036621 | 0.07782 | 0.18768 | 0.041199 | -0.032043 | 0.013733 | 0.082397 | 0.050354 | 121.2341 | 121.1151 | -0.050354 | 121.2982 | 121.3211 | 0.20599 | -0.004578 | 121.2341 | 121.2021 | -0.14648 | 121.2296 | 121.1929 | -0.009155 | -0.10071 | 121.2158 | 121.2616 | 121.3303 | -0.15106 | 121.1197 | 121.1655 | 121.3394 | -0.064087
3313.5 | 121.4172 | -121.1838 | 0.09613 | 0.0054168 | -0.0033454 | 0.070867 | 0.028647 | -0.066332 | -0.021817 | 0.0010018 | 0.022583 | 0.034306 | 0.010559 | -0.040763 | -0.0063318 | 0.011813 | 0.018311 | 0 | 0.022888 | 0.086975 | 0.11444 | 0.032043 | -0.086975 | -0.004578 | 0.036621 | -0.10071 | 0.027466 | 0.027466 | 0.050354 | 0 | 121.2158 | 121.0968 | 0.018311 | 121.1838 | 121.2708 | 0.17395 | -0.077819 | 121.2341 | 121.1838 | -0.068664 | 121.1792 | 121.0831 | -0.10071 | -0.068664 | 121.2982 | 121.2021 | 121.2067 | -0.1831 | 121.2112 | 121.2112 | 121.2204 | -0.09613
3315.2188 | 121.3898 | -121.2112 | 0.10986 | 0.0054168 | -0.00185 | 0.073858 | 0.030356 | -0.067828 | -0.027799 | 0.00014745 | 0.0073242 | 0.032383 | 0.009064 | -0.042259 | -0.0078272 | 0.0116 | -0.009155 | 0.009155 | 0.036621 | 0.073242 | 0.10071 | 0.045776 | -0.073242 | -0.036621 | 0.018311 | -0.11444 | 0.022888 | 0.036621 | 0.050354 | 0.004578 | 121.257 | 121.138 | -0.009155 | 121.2204 | 121.2845 | 0.14648 | -0.11902 | 121.2616 | 121.2158 | -0.086975 | 121.1746 | 121.0968 | -0.11902 | -0.073242 | 121.312 | 121.2021 | 121.2479 | -0.18311 | 121.2341 | 121.2479 | 121.2296 | -0.10529
3316.9844 | 115.3519 | -72.7341 | 42.6773 | 0.013046 | 0.0026362 | 0.069372 | 0.02352 | -0.06975 | -0.022031 | 0.0016428 | 0.0073242 | 0.03217 | 0.0075686 | -0.041618 | -0.0024866 | 0.012241 | 0.009155 | 0.004578 | 0.018311 | 0.064087 | 0.068665 | 0.032043 | -0.07782 | 0.009155 | 0.032043 | -0.07782 | -0.013733 | -0.013733 | 0.073242 | 0.009155 | 72.7661 | 72.6562 | -42.6086 | 72.7386 | 72.7982 | 0.14191 | -42.6682 | 72.8073 | 72.7432 | -42.691 | 72.7432 | 72.6562 | -0.086975 | -42.691 | 72.8027 | 72.7432 | 72.7524 | -42.7551 | 72.7203 | 72.7203 | 72.7661 | -42.6682
3318.7031 | 120.7855 | -120.2545 | 0.068665 | 0.0054168 | 0.0051996 | 0.070654 | 0.027579 | -0.068255 | -0.02844 | -0.0015616 | 0.0073242 | 0.029392 | 0.005646 | -0.043968 | -0.0095362 | 0.013522 | 0.032043 | 0.086975 | 0.10986 | 0.13275 | 0.073242 | 0.07782 | -0.041199 | 0.027466 | 0.11902 | -0.004578 | -0.022888 | 0.004578 | 0.082397 | 0.027466 | 120.3323 | 120.2133 | 0.004577 | 120.3415 | 120.3873 | 0.17395 | -0.036622 | 120.3369 | 120.282 | -0.091553 | 120.282 | 120.2499 | -0.032044 | -0.064087 | 120.3278 | 120.2866 | 120.3644 | -0.10986 | 120.2316 | 120.2591 | 120.3735 | -0.041199
3320.4688 | 120.5109 | -119.87 | 0.17395 | 0.0054168 | 0.0028498 | 0.069158 | 0.025229 | -0.068041 | -0.020749 | 0.00036105 | 0.014954 | 0.03516 | 0.0050052 | -0.042045 | -0.003982 | 0.0116 | 0.10986 | 0.10071 | 0.11902 | 0.15106 | 0.059509 | 0.09613 | -0.027466 | 0.091553 | 0.1236 | 0.013733 | -0.050354 | -0.009155 | 0.11444 | 0.036621 | 119.9661 | 119.8425 | -0.11444 | 119.9707 | 120.0211 | 0.17853 | -0.064087 | 119.9844 | 119.9066 | -0.2243 | 119.9615 | 119.8837 | -0.022888 | -0.1831 | 119.9295 | 119.9799 | 119.989 | -0.20142 | 119.8196 | 119.8608 | 119.9936 | -0.13733
3322.1875 | 120.7672 | -120.4376 | 0.07782 | 0.013046 | 0.004986 | 0.071081 | 0.027365 | -0.070818 | -0.028012 | 0.0012154 | -0.0003053 | 0.030674 | 0.005646 | -0.045036 | -0.0063318 | 0.013736 | 0.09613 | 0.10529 | 0.14648 | 0.13275 | 0.045776 | 0.082397 | -0.027466 | 0.050354 | 0.09613 | -0.004578 | -0.018311 | -0.009155 | 0.09613 | 0.045776 | 120.52 | 120.4102 | -0.032044 | 120.5429 | 120.5704 | 0.16022 | 0.01831 | 120.5338 | 120.4834 | -0.096131 | 120.488 | 120.433 | -0.050354 | -0.086975 | 120.4834 | 120.5338 | 120.5841 | -0.10529 | 120.4193 | 120.4285 | 120.5338 | -0.032044
3323.9531 | 120.8359 | -120.0806 | 0.36621 | -0.0022127 | 0.0017816 | 0.067449 | 0.026938 | -0.068896 | -0.02139 | 0.0010018 | 0.014954 | 0.033238 | 0.0077822 | -0.040977 | -0.006759 | 0.012027 | 0.036621 | -0.004578 | 0.013733 | 0.07782 | 0.07782 | 0.059509 | -0.073242 | 0.009155 | 0.009155 | -0.10529 | 0.004578 | 0.027466 | 0.073242 | 0.022888 | 120.1401 | 120.0073 | -0.28839 | 120.076 | 120.1584 | 0.15106 | -0.32959 | 120.1538 | 120.1035 | -0.36163 | 120.0897 | 119.9753 | -0.12817 | -0.33875 | 120.1584 | 120.1172 | 120.0943 | -0.43945 | 120.0851 | 120.108 | 120.0897 | -0.34332
3325.6562 | 120.5063 | -118.7714 | 1.561 | 0.0054168 | 0.00049979 | 0.070654 | 0.026724 | -0.069323 | -0.022244 | 0.0029244 | -0.0003053 | 0.034519 | 0.0067142 | -0.04055 | -0.0031274 | 0.010532 | 0.009155 | -0.032043 | -0.009155 | 0.064087 | 0.10529 | 0.041199 | -0.068665 | -0.022888 | -0.004578 | -0.12817 | 0.009155 | 0.045776 | 0.064087 | 0.004578 | 118.8126 | 118.7027 | -1.4557 | 118.7393 | 118.8354 | 0.13275 | -1.5518 | 118.8354 | 118.7759 | -1.5518 | 118.7485 | 118.6432 | -0.13275 | -1.5152 | 118.8766 | 118.7805 | 118.7622 | -1.6296 | 118.7805 | 118.8171 | 118.7668 | -1.5564
3327.3906 | 120.9045 | -120.5109 | 0.1236 | 0.0054168 | 0.004986 | 0.072363 | 0.030997 | -0.069964 | -0.029508 | -0.0024162 | 0.022583 | 0.031742 | 0.0069278 | -0.043327 | -0.0091088 | 0.01395 | 0.036621 | 0.059509 | 0.10529 | 0.11902 | 0.064087 | 0.086975 | -0.059509 | 0.022888 | 0.082397 | -0.022888 | -0.018311 | 0.022888 | 0.11444 | 0.036621 | 120.5978 | 120.4514 | -0.059509 | 120.5704 | 120.6299 | 0.17853 | -0.086975 | 120.6253 | 120.5475 | -0.14191 | 120.5338 | 120.488 | -0.059509 | -0.10071 | 120.575 | 120.5475 | 120.6162 | -0.1831 | 120.4926 | 120.5338 | 120.5933 | -0.086975
3329.0938 | 120.8908 | -120.6345 | 0.07782 | 0.013046 | 0.004986 | 0.072576 | 0.029929 | -0.067614 | -0.028226 | 0.00014745 | 0.014954 | 0.029606 | 0.0050052 | -0.042045 | -0.0093226 | 0.012454 | 0.1236 | 0.1236 | 0.15564 | 0.15106 | 0.064087 | 0.09613 | -0.054932 | 0.073242 | 0.16937 | 0.059509 | -0.018311 | -0.009155 | 0.091553 | 0.041199 | 120.7306 | 120.5795 | -0.013733 | 120.7581 | 120.7855 | 0.20599 | 0.045776 | 120.726 | 120.6757 | -0.096131 | 120.7077 | 120.694 | 0.01831 | -0.086975 | 120.6985 | 120.7581 | 120.7901 | -0.13275 | 120.6161 | 120.6253 | 120.8038 | -0.036621
3330.8125 | 120.607 | -120.1035 | 0.39368 | 0.013046 | -0.0044134 | 0.071294 | 0.028006 | -0.069537 | -0.021817 | -0.00027975 | -0.0003053 | 0.035801 | 0.007996 | -0.042472 | -0.0046228 | 0.0083953 | 0.032043 | -0.004578 | 0.013733 | 0.07782 | 0.10529 | 0.054932 | -0.082397 | -0.009155 | 0.054932 | -0.10529 | 0.022888 | 0.036621 | 0.054932 | -0.004578 | 120.1584 | 120.0211 | -0.28839 | 120.0989 | 120.1813 | 0.16022 | -0.36163 | 120.1584 | 120.0989 | -0.37079 | 120.0943 | 119.9982 | -0.10071 | -0.35706 | 120.2087 | 120.1355 | 120.1172 | -0.47607 | 120.1263 | 120.1401 | 120.1584 | -0.39826
3332.5469 | 120.607 | -120.1859 | 0.37537 | 0.020676 | 0.0064814 | 0.070867 | 0.025443 | -0.068682 | -0.025235 | 0.0012154 | 0.0073242 | 0.030461 | 0.010346 | -0.042686 | -0.0074 | 0.013095 | 0.082397 | 0.11444 | 0.15106 | 0.12817 | 0.059509 | 0.091553 | -0.041199 | 0.041199 | 0.10529 | 0 | 0.009155 | 0.013733 | 0.11444 | 0.036621 | 120.2774 | 120.1447 | -0.31586 | 120.3003 | 120.314 | 0.16937 | -0.29297 | 120.3003 | 120.2225 | -0.36621 | 120.2271 | 120.1859 | -0.036621 | -0.36163 | 120.2454 | 120.2682 | 120.3369 | -0.41656 | 120.195 | 120.1996 | 120.2911 | -0.33874
3334.25 | 120.7855 | -120.6116 | 0.1236 | 0.013046 | 0.00049979 | 0.072149 | 0.030142 | -0.068682 | -0.025235 | -0.0017752 | -0.0003053 | 0.03217 | 0.007355 | -0.044395 | -0.0074 | 0.011813 | 0.068665 | 0.09613 | 0.10986 | 0.1236 | 0.082397 | 0.073242 | -0.059509 | -0.004578 | 0.064087 | -0.07782 | 0.004578 | 0.018311 | 0.068665 | 0.013733 | 120.6848 | 120.5521 | -0.041199 | 120.7077 | 120.7352 | 0.1831 | -0.054931 | 120.6802 | 120.6253 | -0.11902 | 120.607 | 120.5338 | -0.091553 | -0.10528 | 120.694 | 120.6802 | 120.7214 | -0.1831 | 120.6161 | 120.6299 | 120.6757 | -0.10986
3335.9844 | 120.7901 | -120.1172 | 0.4303 | 0.013046 | -0.005268 | 0.067022 | 0.029288 | -0.069964 | -0.020749 | 0.00014745 | 0.014954 | 0.035374 | 0.009064 | -0.041191 | -0.00505 | 0.0094635 | 0.073242 | 0.022888 | 0.073242 | 0.11444 | 0.086975 | 0.041199 | -0.064087 | 0.032043 | 0.068665 | -0.073242 | 0.004578 | 0.022888 | 0.068665 | 0.009155 | 120.1584 | 120.0531 | -0.34332 | 120.1401 | 120.2316 | 0.17853 | -0.35706 | 120.1859 | 120.1263 | -0.42572 | 120.1492 | 120.0439 | -0.082397 | -0.40741 | 120.2042 | 120.1904 | 120.1904 | -0.49439 | 120.1218 | 120.1401 | 120.1859 | -0.42114
3337.6875 | 120.6619 | -119.9661 | 0.67749 | 0.0054168 | -0.0020636 | 0.067449 | 0.027152 | -0.0674 | -0.022672 | 0.003779 | 0.0073242 | 0.032597 | 0.0088504 | -0.042259 | -0.0031274 | 0.012241 | 0.064087 | 0.059509 | 0.054932 | 0.10071 | 0.07782 | 0.059509 | -0.059509 | 0.004578 | 0.022888 | -0.091553 | 0.022888 | 0.050354 | 0.073242 | 0 | 120.0256 | 119.9066 | -0.59967 | 120.0256 | 120.0668 | 0.16022 | -0.6134 | 120.0394 | 119.9661 | -0.6546 | 119.9707 | 119.8746 | -0.091553 | -0.62714 | 120.0439 | 120.0302 | 120.0211 | -0.737 | 119.989 | 120.0165 | 119.989 | -0.67749
3339.4375 | 120.9503 | -120.5841 | 0.068665 | 0.013046 | 0.004345 | 0.074712 | 0.029501 | -0.070177 | -0.03143 | 0.0024972 | 0.014954 | 0.026829 | 0.0077822 | -0.043968 | -0.0063318 | 0.014163 | 0.045776 | 0.10529 | 0.12817 | 0.14648 | 0.068665 | 0.07782 | -0.050354 | 0.045776 | 0.17395 | 0.027466 | -0.018311 | 0.004578 | 0.091553 | 0.036621 | 120.6619 | 120.5338 | 0 | 120.6894 | 120.7306 | 0.19684 | -0.022889 | 120.6757 | 120.6207 | -0.086976 | 120.6299 | 120.6116 | -0.009155 | -0.064087 | 120.6528 | 120.6299 | 120.7123 | -0.11902 | 120.5658 | 120.5887 | 120.7581 | -0.032044
3341.1562 | 120.845 | -120.4742 | 0.27466 | 0.0054168 | -0.0039862 | 0.07044 | 0.029288 | -0.069964 | -0.021817 | -0.00049335 | 0.014954 | 0.034306 | 0.0097048 | -0.042686 | -0.0074 | 0.012241 | -0.004578 | -0.013733 | 0.009155 | 0.068665 | 0.091553 | 0.036621 | -0.09613 | -0.036621 | 0.032043 | -0.10529 | 0.013733 | 0.032043 | 0.054932 | 0.009155 | 120.5109 | 120.3781 | -0.18311 | 120.4605 | 120.5429 | 0.16479 | -0.27924 | 120.5292 | 120.4834 | -0.26093 | 120.4376 | 120.369 | -0.11444 | -0.24262 | 120.5658 | 120.4697 | 120.4834 | -0.37079 | 120.488 | 120.5063 | 120.5063 | -0.2655
3342.9219 | 120.9869 | -120.7169 | 0.059509 | -0.0022127 | 0.0086176 | 0.072149 | 0.028647 | -0.070605 | -0.029508 | -0.00092075 | 0.014954 | 0.031315 | 0.006287 | -0.044181 | -0.006759 | 0.013736 | 0.050354 | 0.082397 | 0.1236 | 0.10071 | 0.059509 | 0.086975 | -0.041199 | 0.013733 | 0.082397 | -0.036621 | -0.027466 | -0.004578 | 0.09613 | 0.022888 | 120.8038 | 120.6757 | 0 | 120.7993 | 120.8176 | 0.14191 | -0.009155 | 120.813 | 120.7397 | -0.086975 | 120.7306 | 120.6802 | -0.059509 | -0.064087 | 120.7764 | 120.7672 | 120.8405 | -0.10071 | 120.6894 | 120.7123 | 120.7993 | -0.036621
3344.6406 | 120.9137 | -120.7672 | 0.068665 | 0.0054168 | 0.0051996 | 0.07044 | 0.030569 | -0.070391 | -0.028867 | -0.0017752 | 0.022583 | 0.031529 | 0.0084232 | -0.043754 | -0.0088952 | 0.0116 | 0.10986 | 0.16022 | 0.16937 | 0.15564 | 0.059509 | 0.09613 | -0.018311 | 0.091553 | 0.19226 | 0.036621 | -0.022888 | -0.013733 | 0.11902 | 0.036621 | 120.8633 | 120.7489 | -0.009156 | 120.9274 | 120.9229 | 0.17395 | 0.041198 | 120.8862 | 120.8038 | -0.091553 | 120.8588 | 120.8038 | 0 | -0.082398 | 120.8267 | 120.8771 | 120.9366 | -0.086976 | 120.7443 | 120.7535 | 120.9595 | -0.032044
3346.3594 | 120.8954 | -120.0485 | 0.65918 | 0.0054168 | 0.0026362 | 0.071935 | 0.028433 | -0.066973 | -0.028867 | -0.00092075 | 0.0073242 | 0.031956 | 0.0069278 | -0.044609 | -0.0088952 | 0.013736 | 0.10529 | 0.13733 | 0.16937 | 0.16022 | 0.064087 | 0.07782 | -0.045776 | 0.091553 | 0.16937 | 0.050354 | -0.027466 | 0.004578 | 0.10986 | 0.036621 | 120.1263 | 120.0027 | -0.59509 | 120.1859 | 120.2087 | 0.20599 | -0.55389 | 120.1584 | 120.0851 | -0.68665 | 120.1401 | 120.0989 | 0.013733 | -0.6546 | 120.1126 | 120.1538 | 120.2179 | -0.70496 | 120.0211 | 120.0531 | 120.2179 | -0.62256
3348.0938 | 120.7535 | -120.7764 | 0.073242 | 0.013046 | 0.0041314 | 0.071508 | 0.026724 | -0.069964 | -0.026517 | -0.0015616 | 0.0073242 | 0.030033 | 0.0082096 | -0.043968 | -0.0071862 | 0.011386 | 0.11444 | 0.16022 | 0.17853 | 0.15106 | 0.073242 | 0.082397 | -0.045776 | 0.091553 | 0.17395 | 0.050354 | -0.032043 | -0.013733 | 0.10071 | 0.013733 | 120.8588 | 120.7306 | 0 | 120.9366 | 120.9274 | 0.19684 | 0.041199 | 120.8771 | 120.7901 | -0.10529 | 120.8679 | 120.8267 | 0.036621 | -0.086975 | 120.8496 | 120.8908 | 120.9549 | -0.11902 | 120.7443 | 120.7626 | 120.9503 | -0.059509
3349.8125 | 116.2628 | -82.8964 | 33.0368 | 0.013046 | 0.0039178 | 0.072576 | 0.028647 | -0.068255 | -0.025235 | -0.0015616 | 0.0073242 | 0.030033 | 0.0058596 | -0.042686 | -0.0078272 | 0.010532 | 0.1236 | 0.15564 | 0.16479 | 0.15106 | 0.045776 | 0.068665 | -0.073242 | 0.082397 | 0.14648 | 0.032043 | -0.050354 | -0.032043 | 0.091553 | 0.027466 | 82.9651 | 82.8232 | -32.991 | 83.0521 | 83.0475 | 0.2243 | -32.9132 | 82.988 | 82.9239 | -33.0872 | 82.9788 | 82.9285 | 0.004577 | -33.0688 | 82.9422 | 83.02 | 83.0612 | -33.11 | 82.8461 | 82.8644 | 83.0429 | -33.0093
3351.5312 | 120.6848 | -120.1492 | 0.24261 | 0.013046 | -0.005268 | 0.067876 | 0.025443 | -0.065478 | -0.017972 | 0.003138 | 0.022583 | 0.038365 | 0.007996 | -0.040123 | -0.00099117 | 0.010745 | 0.036621 | -0.018311 | 0.013733 | 0.082397 | 0.10071 | 0.068665 | -0.068665 | -0.013733 | -0.004578 | -0.15106 | 0.004578 | 0.027466 | 0.059509 | 0.004578 | 120.2179 | 120.0806 | -0.14191 | 120.1309 | 120.2316 | 0.15106 | -0.20599 | 120.2087 | 120.1538 | -0.23804 | 120.1355 | 119.9982 | -0.15564 | -0.21515 | 120.2499 | 120.1859 | 120.163 | -0.31128 | 120.1538 | 120.1767 | 120.1447 | -0.23804
3353.25 | 120.163 | -119.8654 | 0.10529 | 0.0054168 | -0.00099541 | 0.067449 | 0.024374 | -0.069537 | -0.019681 | 0.0016428 | -0.0003053 | 0.035374 | 0.0082096 | -0.041832 | -0.0048364 | 0.012241 | 0.009155 | -0.022888 | 0.009155 | 0.064087 | 0.10529 | 0.036621 | -0.073242 | -0.018311 | -0.036621 | -0.13275 | 0.022888 | 0.036621 | 0.050354 | -0.013733 | 119.902 | 119.7922 | 0 | 119.8425 | 119.9295 | 0.13733 | -0.096131 | 119.9158 | 119.8517 | -0.082398 | 119.8471 | 119.7327 | -0.11902 | -0.068665 | 119.9707 | 119.8746 | 119.8746 | -0.17853 | 119.8883 | 119.902 | 119.8288 | -0.11902
3355 | 120.5566 | -120.1721 | 0.086975 | 0.0054168 | 0.0041314 | 0.072149 | 0.027579 | -0.067614 | -0.032071 | -0.0015616 | 0.0073242 | 0.02982 | 0.007355 | -0.04525 | -0.0088952 | 0.014377 | 0.086975 | 0.11444 | 0.14648 | 0.13733 | 0.059509 | 0.068665 | -0.050354 | 0.064087 | 0.17395 | 0.045776 | -0.027466 | -0.032043 | 0.10529 | 0.036621 | 120.2408 | 120.1218 | -0.027466 | 120.2866 | 120.3094 | 0.18768 | 0 | 120.2774 | 120.2087 | -0.11444 | 120.2362 | 120.2179 | 0.009155 | -0.11902 | 120.2316 | 120.2591 | 120.3186 | -0.13733 | 120.1447 | 120.1401 | 120.3461 | -0.050354
3356.7031 | 120.639 | -120.4422 | 0.07782 | 0.013046 | 0.00028619 | 0.068945 | 0.031638 | -0.069537 | -0.024167 | 0.0022836 | 0.014954 | 0.032597 | 0.0067142 | -0.042686 | -0.0091088 | 0.013309 | 0.082397 | 0.11902 | 0.13275 | 0.15106 | 0.068665 | 0.073242 | -0.054932 | 0.022888 | 0.10986 | -0.022888 | -0.013733 | 0.009155 | 0.07782 | 0.004578 | 120.5154 | 120.3873 | -0.009155 | 120.5612 | 120.5933 | 0.20599 | 0.004577 | 120.52 | 120.4468 | -0.091553 | 120.4651 | 120.4193 | -0.027466 | -0.068665 | 120.5109 | 120.5246 | 120.575 | -0.13275 | 120.4285 | 120.4514 | 120.5521 | -0.073242
3358.4062 | 120.6665 | -120.4605 | 0.068665 | 0.0054168 | -0.0044134 | 0.069585 | 0.026724 | -0.065478 | -0.022458 | -6.615e-05 | 0.014954 | 0.035374 | 0.0099186 | -0.041191 | -0.0059046 | 0.0088227 | 0.009155 | -0.013733 | 0.018311 | 0.09613 | 0.10071 | 0.050354 | -0.091553 | -0.009155 | 0.054932 | -0.10071 | 0.027466 | 0.018311 | 0.068665 | 0 | 120.5109 | 120.369 | 0.032043 | 120.4468 | 120.5566 | 0.18768 | -0.05951 | 120.5292 | 120.4605 | -0.041199 | 120.4514 | 120.3598 | -0.10071 | -0.050354 | 120.5612 | 120.4697 | 120.4788 | -0.16022 | 120.488 | 120.4788 | 120.5154 | -0.068665
3360.125 | 120.7626 | -120.5017 | 0.073242 | 0.013046 | 0.0039178 | 0.070654 | 0.025229 | -0.069323 | -0.027158 | 0.00014745 | 0.0073242 | 0.030888 | 0.0060732 | -0.044181 | -0.0080408 | 0.012454 | 0.032043 | 0.073242 | 0.091553 | 0.11902 | 0.059509 | 0.073242 | -0.050354 | 0.013733 | 0.09613 | -0.036621 | -0.036621 | 0.013733 | 0.086975 | 0.022888 | 120.575 | 120.4514 | -0.013733 | 120.575 | 120.6207 | 0.16937 | -0.041199 | 120.5887 | 120.5246 | -0.10986 | 120.5154 | 120.4651 | -0.059509 | -0.059509 | 120.5612 | 120.5338 | 120.5933 | -0.1236 | 120.4651 | 120.5154 | 120.5978 | -0.050354
3361.8281 | 120.7901 | -120.5292 | 0.086975 | 0.0054168 | 0.0075494 | 0.073003 | 0.026083 | -0.071673 | -0.028226 | -0.00049335 | 0.0073242 | 0.030888 | 0.0075686 | -0.044822 | -0.006759 | 0.013095 | 0.054932 | 0.082397 | 0.09613 | 0.11444 | 0.064087 | 0.086975 | -0.041199 | 0.022888 | 0.086975 | -0.032043 | -0.036621 | 0 | 0.082397 | 0.022888 | 120.6161 | 120.488 | -0.022888 | 120.6116 | 120.6436 | 0.15564 | -0.032043 | 120.6116 | 120.5521 | -0.1236 | 120.5521 | 120.4971 | -0.054931 | -0.086975 | 120.5933 | 120.5841 | 120.6253 | -0.12817 | 120.4926 | 120.5292 | 120.6161 | -0.064087
3363.5469 | 120.7123 | -120.2866 | 0.33417 | -0.0022127 | -0.0016364 | 0.070867 | 0.026297 | -0.068468 | -0.01904 | 0.0010018 | 0.0073242 | 0.036015 | 0.0084232 | -0.040977 | -0.0041956 | 0.010532 | 0.09613 | 0.050354 | 0.064087 | 0.10529 | 0.091553 | 0.054932 | -0.068665 | 0.036621 | 0.09613 | -0.068665 | 0.013733 | 0.018311 | 0.068665 | 0.009155 | 120.3415 | 120.2179 | -0.24261 | 120.3369 | 120.3918 | 0.17395 | -0.23804 | 120.3552 | 120.2957 | -0.32043 | 120.3232 | 120.2179 | -0.07782 | -0.31586 | 120.3781 | 120.3827 | 120.3506 | -0.40283 | 120.3003 | 120.3049 | 120.3827 | -0.32501
3365.2812 | 119.7784 | -119.2474 | 0.21515 | -0.0098417 | 0.0073358 | 0.072363 | 0.026297 | -0.066546 | -0.026944 | 0.0012154 | 0.014954 | 0.028965 | 0.0050052 | -0.044181 | -0.0052636 | 0.01395 | 0.050354 | 0.07782 | 0.091553 | 0.11444 | 0.068665 | 0.068665 | -0.032043 | 0.022888 | 0.091553 | -0.013733 | -0.022888 | -0.004578 | 0.086975 | 0.022888 | 119.3161 | 119.2154 | -0.14648 | 119.3253 | 119.3619 | 0.14648 | -0.16479 | 119.3344 | 119.2703 | -0.23804 | 119.2703 | 119.2337 | -0.036621 | -0.21973 | 119.3161 | 119.2978 | 119.339 | -0.24719 | 119.2245 | 119.2429 | 119.339 | -0.19226
3366.9844 | 120.1492 | -119.8151 | 0.18768 | -0.0098417 | 0.0028498 | 0.071081 | 0.029715 | -0.068255 | -0.026731 | -0.00070715 | 0.022583 | 0.028538 | 0.006287 | -0.044181 | -0.0099634 | 0.012241 | 0.11444 | 0.16479 | 0.16479 | 0.14648 | 0.054932 | 0.086975 | -0.054932 | 0.07782 | 0.1831 | 0.032043 | -0.032043 | -0.018311 | 0.10986 | 0.045776 | 119.902 | 119.7601 | -0.13275 | 119.9799 | 119.9615 | 0.20142 | -0.073242 | 119.9249 | 119.8608 | -0.21973 | 119.8929 | 119.8471 | -0.013733 | -0.20599 | 119.87 | 119.9295 | 119.9799 | -0.24261 | 119.783 | 119.7968 | 119.9982 | -0.14191
3368.7188 | 120.2362 | -120.0073 | 0.14191 | 0.0054168 | -0.0031318 | 0.069799 | 0.025656 | -0.068896 | -0.021817 | 0.00078825 | 0.014954 | 0.034947 | 0.0092776 | -0.040977 | -0.0020594 | 0.0096771 | 0.045776 | 0.009155 | 0.027466 | 0.10071 | 0.09613 | 0.041199 | -0.07782 | 0.018311 | 0.064087 | -0.086975 | 0.036621 | 0.032043 | 0.073242 | 0.004578 | 120.0485 | 119.9295 | -0.045777 | 120.0165 | 120.108 | 0.17853 | -0.096131 | 120.0806 | 120.0119 | -0.10529 | 120.0256 | 119.9203 | -0.091553 | -0.10986 | 120.1035 | 120.0531 | 120.0348 | -0.21973 | 120.0439 | 120.0394 | 120.0714 | -0.13733
3370.4531 | 120.2499 | -119.9295 | 0.27008 | -0.0022127 | -0.0048406 | 0.070226 | 0.02822 | -0.068468 | -0.020322 | 0.0024972 | -0.0003053 | 0.03516 | 0.009064 | -0.040336 | -0.0054772 | 0.010745 | 0.068665 | 0.064087 | 0.073242 | 0.10986 | 0.07782 | 0.064087 | -0.064087 | 0.054932 | 0.091553 | -0.073242 | 0.004578 | 0.013733 | 0.059509 | 0 | 119.9936 | 119.8654 | -0.19226 | 119.9936 | 120.0394 | 0.17395 | -0.20142 | 119.989 | 119.9295 | -0.2655 | 119.9844 | 119.8563 | -0.073242 | -0.25635 | 120.0073 | 119.9982 | 120.0027 | -0.33417 | 119.9341 | 119.9432 | 120.0211 | -0.27008
3372.1719 | 120.1584 | -119.5358 | 0.45319 | 0.0054168 | -0.0039862 | 0.070654 | 0.026724 | -0.06975 | -0.020749 | 0.00057465 | -0.0003053 | 0.033665 | 0.007996 | -0.043113 | -0.0063318 | 0.012027 | 0.050354 | 0.064087 | 0.068665 | 0.11444 | 0.082397 | 0.041199 | -0.050354 | 0.041199 | 0.091553 | -0.068665 | 0 | 0.013733 | 0.059509 | 0.004578 | 119.577 | 119.4855 | -0.37079 | 119.5999 | 119.6503 | 0.16479 | -0.40283 | 119.5953 | 119.5404 | -0.45319 | 119.577 | 119.4672 | -0.073243 | -0.43945 | 119.6182 | 119.5862 | 119.6045 | -0.50354 | 119.5358 | 119.5496 | 119.6274 | -0.44861
3373.875 | 120.3506 | -119.8929 | 0.32501 | 0.020676 | -0.003559 | 0.068304 | 0.027792 | -0.068041 | -0.024167 | 0.0014292 | 0.014954 | 0.033665 | 0.010987 | -0.041191 | -0.0059046 | 0.012668 | 0.027466 | 0.059509 | 0.064087 | 0.10529 | 0.086975 | 0.045776 | -0.086975 | 0.027466 | 0.082397 | -0.059509 | 0.004578 | 0.018311 | 0.073242 | 0.013733 | 119.9387 | 119.8059 | -0.23804 | 119.9524 | 119.9982 | 0.19226 | -0.29755 | 119.9661 | 119.9066 | -0.32043 | 119.9203 | 119.8334 | -0.073242 | -0.3067 | 119.9799 | 119.9203 | 119.957 | -0.41199 | 119.8975 | 119.9112 | 119.9753 | -0.31128
3375.6094 | 120.488 | -120.1859 | 0.068665 | 0.028305 | 0.0051996 | 0.07279 | 0.029501 | -0.067828 | -0.028653 | -0.00070715 | 0.014954 | 0.028324 | 0.0069278 | -0.045677 | -0.010177 | 0.014804 | 0.022888 | 0.082397 | 0.10529 | 0.10986 | 0.041199 | 0.086975 | -0.050354 | 0.022888 | 0.09613 | -0.009155 | -0.009155 | 0.032043 | 0.086975 | 0.036621 | 120.2728 | 120.1355 | -0.027466 | 120.2682 | 120.2957 | 0.16022 | -0.045777 | 120.2728 | 120.2225 | -0.07782 | 120.2087 | 120.1767 | -0.045776 | -0.036622 | 120.2271 | 120.2087 | 120.2911 | -0.11902 | 120.1767 | 120.2179 | 120.282 | -0.032044
3377.3281 | 120.3918 | -120.0531 | 0.28839 | -0.0022127 | -0.00014101 | 0.069799 | 0.030569 | -0.067614 | -0.028226 | -0.0024162 | -0.0003053 | 0.031742 | 0.0067142 | -0.043754 | -0.0097498 | 0.010532 | 0.059509 | 0.09613 | 0.10986 | 0.13733 | 0.064087 | 0.064087 | -0.059509 | 0.018311 | 0.10986 | -0.036621 | -0.009155 | 0.009155 | 0.07782 | 0.022888 | 120.1172 | 119.9936 | -0.2243 | 120.1492 | 120.1904 | 0.19684 | -0.22888 | 120.1309 | 120.076 | -0.29755 | 120.0714 | 120.0165 | -0.059509 | -0.27924 | 120.1172 | 120.1126 | 120.163 | -0.3479 | 120.0439 | 120.0623 | 120.163 | -0.2655
3379.0469 | 120.5933 | -120.3186 | 0.050354 | 0.013046 | 0.0069086 | 0.071081 | 0.028647 | -0.068041 | -0.028867 | -0.00092075 | 0.014954 | 0.030461 | 0.007996 | -0.0429 | -0.0076136 | 0.014377 | 0.022888 | 0.068665 | 0.11444 | 0.11444 | 0.064087 | 0.073242 | -0.054932 | 0.004578 | 0.091553 | -0.013733 | -0.018311 | 0.004578 | 0.086975 | 0.027466 | 120.3918 | 120.2637 | 0.013733 | 120.3873 | 120.433 | 0.16937 | -0.027466 | 120.4056 | 120.3461 | -0.068665 | 120.3232 | 120.3049 | -0.041199 | -0.045776 | 120.3827 | 120.3415 | 120.433 | -0.10529 | 120.3003 | 120.3232 | 120.4102 | -0.022888
3380.75 | 120.5246 | -120.1355 | 0.068665 | 0.0054168 | 0.0051996 | 0.073431 | 0.027579 | -0.068255 | -0.02844 | -0.00070715 | 0.014954 | 0.031101 | 0.0054324 | -0.043113 | -0.0069726 | 0.010959 | 0.09613 | 0.1236 | 0.14191 | 0.13733 | 0.045776 | 0.086975 | -0.032043 | 0.082397 | 0.15564 | 0.045776 | -0.032043 | -0.004578 | 0.11444 | 0.045776 | 120.2225 | 120.1035 | -0.022889 | 120.2591 | 120.2728 | 0.16937 | 0.027465 | 120.2499 | 120.1813 | -0.10071 | 120.2179 | 120.1813 | 0 | -0.073243 | 120.1813 | 120.2316 | 120.2774 | -0.10071 | 120.1035 | 120.1309 | 120.2911 | -0.022889
3382.4531 | 120.5383 | -120.3964 | 0.09613 | -0.0022127 | 0.0011408 | 0.07279 | 0.02587 | -0.068896 | -0.023099 | -0.0019888 | 0.0073242 | 0.03281 | 0.0088504 | -0.041404 | -0.0065454 | 0.0094635 | 0.086975 | 0.11444 | 0.11902 | 0.14191 | 0.07782 | 0.086975 | -0.054932 | 0.022888 | 0.086975 | -0.059509 | -0.018311 | 0.018311 | 0.068665 | 0.018311 | 120.4834 | 120.3415 | -0.01831 | 120.5109 | 120.5383 | 0.19684 | -0.009155 | 120.4651 | 120.4147 | -0.11444 | 120.4193 | 120.3369 | -0.07782 | -0.077819 | 120.4742 | 120.4834 | 120.5154 | -0.15106 | 120.3781 | 120.4147 | 120.4834 | -0.077819
3384.1719 | 120.6573 | -120.369 | 0.054932 | 0.0054168 | 0.0051996 | 0.07044 | 0.024161 | -0.068896 | -0.021817 | 0.00036105 | -0.0003053 | 0.031742 | 0.0050052 | -0.044609 | -0.003982 | 0.012027 | 0.11902 | 0.12817 | 0.14648 | 0.15564 | 0.054932 | 0.09613 | -0.027466 | 0.10529 | 0.13275 | 0.018311 | -0.032043 | -0.009155 | 0.091553 | 0.036621 | 120.4651 | 120.3415 | 0 | 120.4971 | 120.5246 | 0.18311 | 0.064087 | 120.4605 | 120.4056 | -0.086975 | 120.4742 | 120.3873 | -0.01831 | -0.064087 | 120.4239 | 120.488 | 120.5154 | -0.082398 | 120.3369 | 120.3598 | 120.5017 | -0.018311
3385.8906 | 120.6345 | -120.4193 | 0.07782 | 0.0054168 | -0.0044134 | 0.069158 | 0.026083 | -0.068041 | -0.020963 | 0.00078825 | 0.014954 | 0.034306 | 0.0094912 | -0.042472 | -0.003982 | 0.0094635 | 0.018311 | 0.022888 | 0.045776 | 0.091553 | 0.09613 | 0.054932 | -0.082397 | 0.022888 | 0.045776 | -0.07782 | 0.004578 | 0.027466 | 0.068665 | -0.013733 | 120.4742 | 120.3369 | 0.01831 | 120.4422 | 120.5109 | 0.17395 | -0.059509 | 120.488 | 120.4056 | -0.073242 | 120.4422 | 120.3415 | -0.064087 | -0.050354 | 120.5154 | 120.4376 | 120.4651 | -0.16022 | 120.4239 | 120.4468 | 120.4651 | -0.091553
3387.625 | 120.6436 | -120.4468 | 0.07782 | 0.0054168 | -0.00185 | 0.067449 | 0.023734 | -0.071459 | -0.022672 | 0.0014292 | 0.0073242 | 0.033238 | 0.007996 | -0.04055 | -0.0046228 | 0.012241 | 0 | -0.036621 | 0 | 0.068665 | 0.09613 | 0.041199 | -0.07782 | -0.027466 | -0.018311 | -0.1236 | 0.022888 | 0.041199 | 0.059509 | 0.009155 | 120.488 | 120.369 | 0.01831 | 120.4102 | 120.5154 | 0.14649 | -0.07782 | 120.5063 | 120.4559 | -0.054932 | 120.4193 | 120.3232 | -0.13275 | -0.036621 | 120.5429 | 120.4468 | 120.4468 | -0.15564 | 120.4697 | 120.488 | 120.4285 | -0.068665
3389.3906 | 120.5292 | -119.8196 | 0.5127 | 0.0054168 | 7.2586e-05 | 0.068517 | 0.025015 | -0.070391 | -0.023313 | 0.0039926 | 0.022583 | 0.032383 | 0.0065006 | -0.041191 | -0.0046228 | 0.01395 | 0.022888 | -0.009155 | 0.013733 | 0.054932 | 0.086975 | 0.045776 | -0.073242 | -0.027466 | 0.009155 | -0.10071 | 0.013733 | 0.032043 | 0.082397 | 0.022888 | 119.8654 | 119.7464 | -0.42572 | 119.8105 | 119.8746 | 0.12817 | -0.48981 | 119.902 | 119.8425 | -0.49896 | 119.7922 | 119.7189 | -0.1236 | -0.48065 | 119.9066 | 119.8425 | 119.8334 | -0.58594 | 119.8334 | 119.8517 | 119.8288 | -0.48981
3391.1094 | 120.5109 | -119.5312 | 0.85144 | 0.0054168 | -0.002918 | 0.068945 | 0.024161 | -0.065264 | -0.022672 | 0.0016428 | 0.0073242 | 0.034947 | 0.0094912 | -0.041191 | -0.003982 | 0.013309 | 0.004578 | -0.022888 | -0.009155 | 0.073242 | 0.11902 | 0.041199 | -0.073242 | -0.027466 | -0.009155 | -0.11444 | 0.018311 | 0.036621 | 0.059509 | 0.009155 | 119.5724 | 119.458 | -0.73242 | 119.5084 | 119.6045 | 0.14648 | -0.84686 | 119.5908 | 119.5404 | -0.83313 | 119.5038 | 119.4168 | -0.1236 | -0.81482 | 119.6503 | 119.5358 | 119.5221 | -0.92468 | 119.5496 | 119.5679 | 119.5221 | -0.84228
3392.8281 | 120.7581 | -120.433 | 0.091553 | 0.020676 | 0.0056268 | 0.07044 | 0.026083 | -0.070177 | -0.02908 | 0.0010018 | 0.014954 | 0.02982 | 0.0077822 | -0.044609 | -0.008468 | 0.014377 | 0.082397 | 0.10529 | 0.15564 | 0.13275 | 0.050354 | 0.07782 | -0.032043 | 0.032043 | 0.10071 | -0.004578 | -0.018311 | 0 | 0.09613 | 0.022888 | 120.5109 | 120.401 | -0.041199 | 120.5383 | 120.5658 | 0.16479 | -0.009156 | 120.5292 | 120.4559 | -0.10986 | 120.4651 | 120.4285 | -0.027466 | -0.091553 | 120.4834 | 120.5154 | 120.5887 | -0.1236 | 120.4147 | 120.433 | 120.5338 | -0.068665
3394.5469 | 120.5383 | -119.4168 | 0.88806 | 0.0054168 | 0.0011408 | 0.068304 | 0.024802 | -0.068468 | -0.02139 | 0.0016428 | 0.0073242 | 0.034519 | 0.0065006 | -0.042045 | -0.0044092 | 0.012882 | 0.018311 | -0.013733 | 0.009155 | 0.073242 | 0.09613 | 0.059509 | -0.10529 | -0.032043 | 0.013733 | -0.10529 | 0.009155 | 0.018311 | 0.064087 | 0.013733 | 119.4763 | 119.3115 | -0.79193 | 119.4031 | 119.4901 | 0.17853 | -0.86975 | 119.4809 | 119.4305 | -0.87891 | 119.3848 | 119.3115 | -0.11902 | -0.86975 | 119.5129 | 119.4351 | 119.426 | -0.99335 | 119.426 | 119.4351 | 119.4305 | -0.87433
3396.3125 | 120.7031 | -120.4056 | 0.082397 | -0.0022127 | 0.0011408 | 0.070226 | 0.026297 | -0.067614 | -0.024167 | 0.0027108 | 0.014954 | 0.033451 | 0.0052188 | -0.042686 | -0.0027002 | 0.016086 | 0.013733 | -0.018311 | -0.004578 | 0.064087 | 0.086975 | 0.041199 | -0.073242 | -0.022888 | 0.009155 | -0.10529 | 0.004578 | 0.045776 | 0.045776 | 0.004578 | 120.4468 | 120.3323 | 0.004578 | 120.3873 | 120.4697 | 0.13733 | -0.068664 | 120.4514 | 120.4102 | -0.077819 | 120.3827 | 120.3003 | -0.10986 | -0.036621 | 120.4926 | 120.4193 | 120.401 | -0.15564 | 120.4102 | 120.4514 | 120.4147 | -0.077819
3398.0938 | 120.5521 | -119.8837 | 0.70953 | 0.020676 | -0.00078181 | 0.072576 | 0.031638 | -0.067828 | -0.026303 | -0.0011344 | 0.0073242 | 0.033024 | 0.010132 | -0.044181 | -0.0071862 | 0.014591 | 0 | 0.018311 | 0.054932 | 0.068665 | 0.082397 | 0.050354 | -0.091553 | -0.045776 | 0.032043 | -0.086975 | 0.032043 | 0.036621 | 0.050354 | -0.013733 | 119.9341 | 119.7922 | -0.62714 | 119.902 | 119.9524 | 0.16022 | -0.70953 | 119.9341 | 119.87 | -0.67749 | 119.838 | 119.7968 | -0.073242 | -0.67291 | 119.9661 | 119.8837 | 119.9387 | -0.80109 | 119.9158 | 119.9203 | 119.9158 | -0.72327
3399.8438 | 120.8267 | -120.4788 | 0.10529 | 0.0054168 | 0.0022088 | 0.07279 | 0.029929 | -0.070391 | -0.029508 | -0.0015616 | -0.0003053 | 0.028965 | 0.0065006 | -0.043754 | -0.0080408 | 0.013095 | 0.10071 | 0.17853 | 0.16937 | 0.16022 | 0.059509 | 0.082397 | -0.036621 | 0.059509 | 0.17853 | 0.041199 | -0.022888 | 0.004578 | 0.10986 | 0.022888 | 120.5612 | 120.4422 | -0.045777 | 120.6573 | 120.639 | 0.19684 | -0.004578 | 120.5887 | 120.5017 | -0.12817 | 120.5383 | 120.52 | 0.018311 | -0.10071 | 120.5383 | 120.5795 | 120.6482 | -0.14191 | 120.4559 | 120.4834 | 120.6573 | -0.082398
3401.6406 | 120.7718 | -120.5566 | 0.082397 | 0.0054168 | -0.002918 | 0.071935 | 0.02822 | -0.0674 | -0.019895 | -0.00070715 | 0.0073242 | 0.033238 | 0.0077822 | -0.0429 | -0.00505 | 0.010532 | 0.018311 | 0.013733 | 0.032043 | 0.09613 | 0.11444 | 0.050354 | -0.091553 | -0.009155 | 0.045776 | -0.086975 | 0.013733 | 0.032043 | 0.07782 | -0.013733 | 120.607 | 120.4651 | 0.032044 | 120.5704 | 120.6528 | 0.18768 | -0.064086 | 120.6345 | 120.5429 | -0.068664 | 120.5475 | 120.4697 | -0.073242 | -0.050354 | 120.6711 | 120.575 | 120.5887 | -0.17395 | 120.5704 | 120.5887 | 120.6024 | -0.09613
3403.4375 | 120.7947 | -120.6207 | 0.091553 | -0.0022127 | 0.0013544 | 0.072149 | 0.030356 | -0.066546 | -0.030362 | -6.615e-05 | 0.014954 | 0.030247 | 0.0077822 | -0.043113 | -0.0071862 | 0.012882 | 0.082397 | 0.13275 | 0.16479 | 0.16022 | 0.050354 | 0.091553 | -0.054932 | 0.082397 | 0.16479 | 0.027466 | -0.027466 | 0 | 0.10529 | 0.018311 | 120.7123 | 120.5658 | -0.041199 | 120.7535 | 120.7809 | 0.21515 | -0.009156 | 120.726 | 120.639 | -0.11902 | 120.7031 | 120.6482 | 0.009155 | -0.091553 | 120.6711 | 120.7031 | 120.7855 | -0.14649 | 120.5933 | 120.6207 | 120.7855 | -0.073242
3405.1875 | 120.7764 | -120.6619 | 0.086975 | 0.013046 | 0.00028619 | 0.07044 | 0.029288 | -0.067614 | -0.024808 | -0.0011344 | 0.014954 | 0.036656 | 0.007355 | -0.0429 | -0.006759 | 0.012668 | 0.036621 | 0.032043 | 0.068665 | 0.073242 | 0.09613 | 0.054932 | -0.086975 | -0.032043 | 0.041199 | -0.10986 | 0.013733 | 0.054932 | 0.07782 | -0.018311 | 120.7169 | 120.575 | 0.009155 | 120.694 | 120.7352 | 0.16022 | -0.050354 | 120.7397 | 120.6436 | -0.073242 | 120.6299 | 120.5521 | -0.091552 | -0.032043 | 120.7581 | 120.6985 | 120.7306 | -0.17395 | 120.6757 | 120.7169 | 120.7031 | -0.10529
3406.9844 | 120.7535 | -120.3506 | 0.32501 | 0.013046 | -0.002918 | 0.071294 | 0.027365 | -0.069323 | -0.026731 | 0.00036105 | 0.022583 | 0.031742 | 0.006287 | -0.041404 | -0.0054772 | 0.012882 | 0.009155 | -0.009155 | 0.018311 | 0.059509 | 0.10071 | 0.045776 | -0.09613 | -0.045776 | 0.032043 | -0.10529 | 0.018311 | 0.041199 | 0.050354 | -0.013733 | 120.3964 | 120.2545 | -0.2243 | 120.3415 | 120.4102 | 0.15564 | -0.31586 | 120.401 | 120.3369 | -0.3067 | 120.3049 | 120.2454 | -0.091553 | -0.28381 | 120.4514 | 120.3598 | 120.369 | -0.42114 | 120.369 | 120.3918 | 120.3827 | -0.33875
3408.7812 | 120.9595 | -120.6116 | 0.082397 | 0.0054168 | 0.0013544 | 0.071294 | 0.030356 | -0.068468 | -0.029721 | -0.00092075 | 0.014954 | 0.029179 | 0.0052188 | -0.044395 | -0.0078272 | 0.01395 | 0.10986 | 0.14648 | 0.16937 | 0.15106 | 0.07782 | 0.07782 | -0.041199 | 0.07782 | 0.17853 | 0.059509 | -0.027466 | -0.004578 | 0.10071 | 0.004578 | 120.6894 | 120.5704 | -0.004577 | 120.7581 | 120.7626 | 0.19226 | 0.027466 | 120.7123 | 120.6161 | -0.10986 | 120.6894 | 120.6711 | 0.054931 | -0.086975 | 120.6894 | 120.7214 | 120.7809 | -0.1236 | 120.5841 | 120.607 | 120.7901 | -0.077819
3410.5781 | 120.8588 | -120.6573 | 0.10986 | 0.013046 | -0.0037726 | 0.068304 | 0.027152 | -0.066546 | -0.01904 | 0.0022836 | 0.014954 | 0.036656 | 0.0097048 | -0.0429 | -0.0063318 | 0.012027 | 0.032043 | -0.027466 | 0 | 0.064087 | 0.086975 | 0.054932 | -0.091553 | -0.036621 | -0.009155 | -0.15106 | 0.013733 | 0.032043 | 0.064087 | -0.018311 | 120.7123 | 120.5658 | -0.022888 | 120.6299 | 120.7214 | 0.15564 | -0.07782 | 120.7214 | 120.639 | -0.09613 | 120.6207 | 120.5063 | -0.13275 | -0.07782 | 120.7443 | 120.6894 | 120.6573 | -0.20142 | 120.6711 | 120.6894 | 120.6482 | -0.12817
3412.3125 | 120.9457 | -120.5612 | 0.14191 | 0.0054168 | 0.004986 | 0.072576 | 0.024374 | -0.066119 | -0.02139 | 0.00036105 | 0.014954 | 0.034733 | 0.0075686 | -0.043541 | -0.0063318 | 0.012027 | 0.022888 | -0.004578 | 0.032043 | 0.073242 | 0.10986 | 0.064087 | -0.073242 | 0.022888 | 0.041199 | -0.07782 | -0.013733 | 0.027466 | 0.07782 | 0.013733 | 120.6253 | 120.488 | -0.032044 | 120.5566 | 120.6345 | 0.14648 | -0.11902 | 120.639 | 120.575 | -0.15564 | 120.5841 | 120.4834 | -0.091553 | -0.11444 | 120.6711 | 120.5841 | 120.5933 | -0.21515 | 120.5475 | 120.5887 | 120.6024 | -0.12817
3414.0938 | 120.8633 | -120.7031 | 0.09613 | 0.0054168 | -0.0012092 | 0.069372 | 0.026297 | -0.068468 | -0.022031 | 0.0014292 | 0.0073242 | 0.034519 | 0.0086368 | -0.042045 | -0.003982 | 0.014163 | 0.064087 | 0.045776 | 0.059509 | 0.1236 | 0.10071 | 0.045776 | -0.07782 | 0.018311 | 0.086975 | -0.064087 | 0.009155 | 0.041199 | 0.068665 | -0.004578 | 120.7489 | 120.6253 | 0.004578 | 120.7489 | 120.8267 | 0.20142 | -0.032043 | 120.7718 | 120.6985 | -0.086975 | 120.7214 | 120.639 | -0.059509 | -0.054931 | 120.8038 | 120.7672 | 120.7626 | -0.17395 | 120.7123 | 120.7443 | 120.7901 | -0.10071
3415.8125 | 120.8405 | -120.7031 | 0.11902 | 0.0054168 | -0.00035461 | 0.071294 | 0.025656 | -0.066119 | -0.022031 | 0.0018564 | 0.0073242 | 0.03516 | 0.006287 | -0.040763 | -0.0044092 | 0.014163 | -0.013733 | -0.045776 | 0.004578 | 0.068665 | 0.10071 | 0.050354 | -0.068665 | -0.022888 | 0 | -0.12817 | 0.009155 | 0.054932 | 0.064087 | -0.004578 | 120.7535 | 120.6345 | -0.018311 | 120.6573 | 120.7718 | 0.13733 | -0.13275 | 120.7672 | 120.6985 | -0.10986 | 120.6802 | 120.575 | -0.1236 | -0.064087 | 120.8038 | 120.6894 | 120.7077 | -0.18768 | 120.7123 | 120.7581 | 120.7031 | -0.1236
3417.625 | 120.9137 | -120.7581 | 0.10529 | 0.020676 | -0.00185 | 0.068731 | 0.027579 | -0.070391 | -0.021604 | 0.0012154 | 0.0073242 | 0.034947 | 0.0075686 | -0.043541 | -0.0029138 | 0.012668 | 0.068665 | 0.059509 | 0.07782 | 0.11444 | 0.086975 | 0.050354 | -0.07782 | 0.022888 | 0.07782 | -0.073242 | 0.018311 | 0.022888 | 0.068665 | 0 | 120.8084 | 120.6802 | -0.018311 | 120.8176 | 120.8725 | 0.19226 | -0.036621 | 120.8267 | 120.7581 | -0.086975 | 120.7809 | 120.6848 | -0.073242 | -0.082398 | 120.845 | 120.8267 | 120.8359 | -0.18311 | 120.7764 | 120.7809 | 120.8359 | -0.10529
3419.4219 | 121.0007 | -120.7626 | 0.054932 | 0.013046 | 0.003277 | 0.073003 | 0.027792 | -0.070818 | -0.029935 | 0.00014745 | -0.0003053 | 0.030461 | 0.0069278 | -0.043968 | -0.0086816 | 0.013522 | 0.045776 | 0.10529 | 0.11444 | 0.1236 | 0.050354 | 0.068665 | -0.045776 | -0.004578 | 0.086975 | -0.018311 | -0.022888 | 0.013733 | 0.086975 | 0.009155 | 120.8313 | 120.7169 | -0.004578 | 120.8679 | 120.8862 | 0.16937 | -0.009156 | 120.8496 | 120.7718 | -0.07782 | 120.7581 | 120.7443 | -0.027466 | -0.041199 | 120.813 | 120.8084 | 120.8771 | -0.10071 | 120.7397 | 120.7764 | 120.8496 | -0.045777
3421.2188 | 119.8471 | -77.3666 | 42.3614 | 0.0054168 | 0.0013544 | 0.067663 | 0.030569 | -0.068041 | -0.021604 | -0.00070715 | 0.014954 | 0.035588 | 0.0097048 | -0.042045 | -0.00505 | 0.012027 | -0.013733 | -0.054932 | -0.013733 | 0.054932 | 0.091553 | 0.032043 | -0.086975 | -0.045776 | -0.018311 | -0.16937 | -0.013733 | 0.027466 | 0.054932 | -0.045776 | 77.3987 | 77.2797 | -42.2699 | 77.3117 | 77.4216 | 0.14191 | -42.3752 | 77.4216 | 77.3209 | -42.3752 | 77.3209 | 77.1973 | -0.1236 | -42.334 | 77.4582 | 77.3529 | 77.3529 | -42.4484 | 77.3529 | 77.3941 | 77.3483 | -42.4072
3422.9375 | 120.7169 | -118.2266 | 2.0462 | 0.013046 | 0.0056268 | 0.068731 | 0.026083 | -0.066973 | -0.026731 | 0.00207 | 0.014954 | 0.030674 | 0.007355 | -0.043327 | -0.0063318 | 0.01395 | 0.10071 | 0.11444 | 0.15564 | 0.15564 | 0.041199 | 0.086975 | -0.050354 | 0.082397 | 0.15106 | 0.027466 | -0.045776 | -0.004578 | 0.09613 | 0.032043 | 118.3136 | 118.1763 | -2.005 | 118.3411 | 118.3823 | 0.20599 | -1.9455 | 118.3228 | 118.2587 | -2.092 | 118.309 | 118.2541 | -0.004577 | -2.0508 | 118.2678 | 118.3273 | 118.3823 | -2.0966 | 118.1808 | 118.222 | 118.3777 | -2.0142
3424.7188 | 121.7606 | -67.5339 | 50.6516 | 0.0054168 | -0.00099541 | 0.065527 | 0.027365 | -0.065478 | -0.020322 | 0.00078825 | -0.0003053 | 0.034947 | 0.010346 | -0.043113 | -0.0052636 | 0.011173 | 0.054932 | 0.036621 | 0.054932 | 0.091553 | 0.073242 | 0.041199 | -0.091553 | 0.018311 | 0.064087 | -0.073242 | -0.004578 | 0.009155 | 0.050354 | -0.013733 | 67.5751 | 67.4423 | -50.5783 | 67.5705 | 67.6254 | 0.18311 | -50.5966 | 67.5842 | 67.5201 | -50.6561 | 67.5522 | 67.4606 | -0.059509 | -50.6424 | 67.6071 | 67.5888 | 67.5888 | -50.7431 | 67.5293 | 67.543 | 67.598 | -50.6653
3426.4375 | 120.8588 | -119.3985 | 1.0941 | 0.013046 | 0.0051996 | 0.070013 | 0.025443 | -0.067187 | -0.026944 | -0.00092075 | 0.0073242 | 0.03281 | 0.007355 | -0.043541 | -0.0044092 | 0.014591 | 0.09613 | 0.13733 | 0.16022 | 0.15106 | 0.032043 | 0.091553 | -0.036621 | 0.086975 | 0.14191 | 0.013733 | -0.041199 | -0.013733 | 0.07782 | 0.027466 | 119.4901 | 119.3619 | -1.062 | 119.5358 | 119.5496 | 0.18768 | -0.99792 | 119.4763 | 119.426 | -1.1353 | 119.4855 | 119.4122 | -0.013733 | -1.1078 | 119.4305 | 119.4946 | 119.5587 | -1.1307 | 119.3573 | 119.3848 | 119.5404 | -1.0666
3428.2188 | 120.8771 | -114.6652 | 4.3625 | 0.0054168 | 0.0056268 | 0.072576 | 0.02822 | -0.070177 | -0.029935 | -0.00070715 | 0.014954 | 0.028965 | 0.0077822 | -0.043754 | -0.0076136 | 0.014163 | 0.07782 | 0.10986 | 0.1236 | 0.1236 | 0.050354 | 0.073242 | -0.036621 | 0.027466 | 0.086975 | -0.027466 | -0.027466 | 0.018311 | 0.091553 | -0.004578 | 114.7385 | 114.6286 | -4.3121 | 114.7751 | 114.7888 | 0.16022 | -4.2847 | 114.7568 | 114.6606 | -4.39 | 114.6927 | 114.6378 | -0.022888 | -4.3442 | 114.7156 | 114.743 | 114.7888 | -4.3991 | 114.6378 | 114.6835 | 114.7522 | -4.3671
3430.0156 | 120.8313 | -119.8929 | 0.84228 | 0.0054168 | -0.00078181 | 0.067236 | 0.027152 | -0.067828 | -0.019895 | 0.0012154 | 0.014954 | 0.036015 | 0.0082096 | -0.043113 | -0.0048364 | 0.010318 | 0.068665 | 0.059509 | 0.064087 | 0.10529 | 0.091553 | 0.059509 | -0.068665 | 0.013733 | 0.050354 | -0.091553 | 0.009155 | 0.013733 | 0.054932 | -0.018311 | 119.9524 | 119.8242 | -0.75073 | 119.9524 | 119.9982 | 0.17395 | -0.77362 | 119.9478 | 119.8746 | -0.83313 | 119.9066 | 119.8013 | -0.073242 | -0.82855 | 119.9844 | 119.9615 | 119.957 | -0.91095 | 119.902 | 119.9066 | 119.9432 | -0.8606
3431.7344 | 120.9457 | -119.8425 | 0.85144 | 0.0054168 | 0.0054132 | 0.071294 | 0.028433 | -0.068041 | -0.02609 | -0.001348 | -0.0003053 | 0.031529 | 0.0092776 | -0.045677 | -0.0069726 | 0.013095 | 0.091553 | 0.1236 | 0.15106 | 0.16022 | 0.059509 | 0.09613 | -0.041199 | 0.082397 | 0.14191 | 0.018311 | -0.022888 | 0 | 0.09613 | 0.027466 | 119.9387 | 119.8013 | -0.79193 | 119.9661 | 120.0027 | 0.20142 | -0.75989 | 119.9387 | 119.87 | -0.87433 | 119.9249 | 119.8608 | -0.009155 | -0.85144 | 119.902 | 119.9341 | 119.9936 | -0.89264 | 119.8196 | 119.8425 | 119.9844 | -0.82397
3433.5156 | 120.8817 | -120.0073 | 0.81482 | 0.013046 | -0.00185 | 0.071294 | 0.030142 | -0.067187 | -0.025876 | -0.0011344 | 0.022583 | 0.035588 | 0.0097048 | -0.042259 | -0.0074 | 0.013736 | -0.018311 | 0.009155 | 0.032043 | 0.082397 | 0.11444 | 0.036621 | -0.086975 | -0.050354 | 0.027466 | -0.10071 | 0.027466 | 0.041199 | 0.059509 | -0.004578 | 120.0439 | 119.9203 | -0.70038 | 120.0165 | 120.0897 | 0.16937 | -0.83313 | 120.0668 | 120.0027 | -0.78735 | 119.957 | 119.9066 | -0.09613 | -0.77362 | 120.1218 | 119.989 | 120.0394 | -0.90179 | 120.0348 | 120.0485 | 120.0348 | -0.8194
3435.3125 | 120.9961 | -120.1035 | 0.63629 | 0.013046 | 0.003277 | 0.072363 | 0.028433 | -0.067187 | -0.028653 | -0.0011344 | 0.0073242 | 0.027256 | 0.0069278 | -0.044395 | -0.010391 | 0.013522 | 0.036621 | 0.073242 | 0.11444 | 0.12817 | 0.064087 | 0.073242 | -0.045776 | 0.027466 | 0.12817 | 0.009155 | -0.013733 | 0 | 0.082397 | 0.013733 | 120.1767 | 120.0577 | -0.5722 | 120.1767 | 120.2316 | 0.17395 | -0.59967 | 120.1859 | 120.1172 | -0.65002 | 120.1309 | 120.1126 | -0.004578 | -0.63629 | 120.1675 | 120.1401 | 120.2179 | -0.68207 | 120.0897 | 120.1035 | 120.2316 | -0.62256
3437.0469 | 121.051 | -120.1401 | 0.61798 | 0.028305 | 0.003277 | 0.069158 | 0.025229 | -0.068041 | -0.024594 | 0.00078825 | 0.0073242 | 0.034092 | 0.0065006 | -0.041404 | -0.0063318 | 0.0116 | 0.091553 | 0.07782 | 0.11902 | 0.14648 | 0.064087 | 0.082397 | -0.041199 | 0.091553 | 0.10529 | 0.004578 | -0.009155 | 0 | 0.09613 | 0.022888 | 120.2225 | 120.0989 | -0.55389 | 120.2179 | 120.2866 | 0.18768 | -0.52643 | 120.2362 | 120.163 | -0.62714 | 120.2316 | 120.1447 | -0.01831 | -0.61798 | 120.2042 | 120.2316 | 120.2591 | -0.65918 | 120.1309 | 120.1401 | 120.2454 | -0.59509
3438.8281 | 121.0556 | -119.4946 | 1.2817 | -0.0022127 | 0.00092719 | 0.072363 | 0.027365 | -0.069323 | -0.029508 | -0.00092075 | 0.0073242 | 0.030674 | 0.0069278 | -0.045036 | -0.0065454 | 0.012241 | 0.12817 | 0.16022 | 0.17853 | 0.16022 | 0.050354 | 0.10071 | -0.041199 | 0.059509 | 0.17853 | 0.032043 | -0.027466 | -0.009155 | 0.11444 | 0.022888 | 119.5953 | 119.4534 | -1.2314 | 119.6548 | 119.6548 | 0.20142 | -1.1536 | 119.6091 | 119.5175 | -1.3092 | 119.5541 | 119.5267 | 0.009155 | -1.2909 | 119.545 | 119.6228 | 119.6732 | -1.3229 | 119.4672 | 119.4855 | 119.6732 | -1.2589
3440.5469 | 120.9961 | -120.3598 | 0.50812 | 0.020676 | -0.00185 | 0.067449 | 0.028006 | -0.067614 | -0.022031 | 0.00078825 | 0.0073242 | 0.033879 | 0.010346 | -0.0429 | -0.00505 | 0.0092499 | 0.050354 | 0.018311 | 0.045776 | 0.10529 | 0.10071 | 0.045776 | -0.086975 | 0.036621 | 0.059509 | -0.082397 | 0.004578 | 0.041199 | 0.073242 | -0.013733 | 120.4056 | 120.2728 | -0.40741 | 120.3781 | 120.4651 | 0.19226 | -0.45776 | 120.433 | 120.3461 | -0.50354 | 120.3964 | 120.2774 | -0.068664 | -0.46692 | 120.4605 | 120.4102 | 120.4056 | -0.59509 | 120.3644 | 120.401 | 120.4193 | -0.52185
3442.2812 | 120.9549 | -119.0598 | 1.7212 | 0.013046 | 0.003277 | 0.073431 | 0.028647 | -0.068041 | -0.026517 | -0.00027975 | 0.014954 | 0.029179 | 0.0084232 | -0.044395 | -0.008468 | 0.012454 | 0.10529 | 0.14191 | 0.16937 | 0.14191 | 0.054932 | 0.07782 | -0.050354 | 0.068665 | 0.18768 | 0.009155 | -0.036621 | 0.004578 | 0.091553 | 0.022888 | 119.1376 | 119.0094 | -1.6663 | 119.2017 | 119.2017 | 0.19226 | -1.6159 | 119.1513 | 119.0826 | -1.7578 | 119.1284 | 119.0689 | -0.013733 | -1.7166 | 119.1147 | 119.165 | 119.2291 | -1.7715 | 119.0231 | 119.0643 | 119.2474 | -1.6983
3444.0625 | 120.9824 | -120.4651 | 0.44861 | 0.013046 | -0.0024908 | 0.069585 | 0.029288 | -0.071459 | -0.022885 | 0.00014745 | 0.014954 | 0.034519 | 0.0086368 | -0.041832 | -0.0054772 | 0.012241 | -0.004578 | -0.018311 | 0.018311 | 0.068665 | 0.091553 | 0.036621 | -0.086975 | -0.041199 | 0.013733 | -0.11902 | 0.013733 | 0.032043 | 0.054932 | -0.027466 | 120.5017 | 120.3781 | -0.35706 | 120.4468 | 120.5338 | 0.15564 | -0.45319 | 120.52 | 120.4376 | -0.43488 | 120.4239 | 120.3461 | -0.091553 | -0.41657 | 120.5566 | 120.4605 | 120.4834 | -0.53558 | 120.4788 | 120.4971 | 120.4788 | -0.47607
3445.8438 | 120.9366 | -118.5196 | 2.4124 | 0.0054168 | -0.0014228 | 0.06809 | 0.025229 | -0.06975 | -0.021176 | 0.0016428 | 0.014954 | 0.036228 | 0.007355 | -0.043327 | -0.0031274 | 0.010959 | -0.004578 | -0.059509 | -0.004578 | 0.064087 | 0.09613 | 0.036621 | -0.07782 | -0.041199 | -0.013733 | -0.13275 | 0.027466 | 0.050354 | 0.054932 | -0.013733 | 118.5562 | 118.4418 | -2.3163 | 118.4601 | 118.5837 | 0.14191 | -2.417 | 118.5745 | 118.5059 | -2.3849 | 118.4784 | 118.3868 | -0.11902 | -2.3621 | 118.6157 | 118.515 | 118.515 | -2.4902 | 118.5471 | 118.5699 | 118.5059 | -2.4261
3447.5938 | 121.1014 | -119.8654 | 1.0666 | 0.013046 | 0.0037042 | 0.07279 | 0.030142 | -0.068896 | -0.028012 | 0.0024972 | 0.014954 | 0.031529 | 0.006287 | -0.044609 | -0.0093226 | 0.012241 | 0.09613 | 0.15106 | 0.16479 | 0.14648 | 0.064087 | 0.073242 | -0.036621 | 0.091553 | 0.20142 | 0.032043 | -0.054932 | -0.004578 | 0.10529 | 0.036621 | 119.9387 | 119.8288 | -1.0025 | 120.0165 | 120.0119 | 0.18311 | -0.97046 | 119.9707 | 119.902 | -1.1215 | 119.957 | 119.8975 | -0.004578 | -1.0712 | 119.9295 | 119.9615 | 120.0302 | -1.1032 | 119.8105 | 119.8608 | 120.0668 | -1.03
3449.375 | 121.1197 | -120.3049 | 0.60883 | 0.0054168 | 0.0058404 | 0.074285 | 0.029074 | -0.068468 | -0.027585 | -0.0017752 | 0.022583 | 0.03217 | 0.0075686 | -0.044181 | -0.006759 | 0.015018 | 0.027466 | 0.068665 | 0.10529 | 0.11444 | 0.073242 | 0.059509 | -0.032043 | 0.009155 | 0.091553 | -0.032043 | -0.027466 | 0 | 0.09613 | -0.009155 | 120.3644 | 120.2728 | -0.53558 | 120.3735 | 120.4193 | 0.14648 | -0.58136 | 120.401 | 120.2957 | -0.63629 | 120.314 | 120.2728 | -0.022888 | -0.60883 | 120.3781 | 120.3323 | 120.4102 | -0.64087 | 120.2774 | 120.3049 | 120.3964 | -0.61798
3451.1719 | 121.0648 | -120.1172 | 0.82398 | -0.0022127 | 0.00049979 | 0.072363 | 0.030569 | -0.068255 | -0.025876 | 0.00078825 | 0.0073242 | 0.030461 | 0.007355 | -0.046104 | -0.006759 | 0.013736 | 0.10071 | 0.13733 | 0.16022 | 0.15564 | 0.045776 | 0.082397 | -0.045776 | 0.045776 | 0.13733 | 0 | -0.022888 | -0.009155 | 0.086975 | 0.013733 | 120.1996 | 120.0714 | -0.7782 | 120.2545 | 120.2728 | 0.20142 | -0.72327 | 120.2042 | 120.1309 | -0.84686 | 120.163 | 120.1172 | -0.013733 | -0.83313 | 120.163 | 120.2179 | 120.2774 | -0.86975 | 120.0943 | 120.108 | 120.2545 | -0.81024
3452.9062 | 121.0876 | -120.0302 | 0.94299 | 0.013046 | -0.0012092 | 0.069158 | 0.028647 | -0.066759 | -0.022244 | 0.00036105 | -0.0003053 | 0.034092 | 0.007355 | -0.041618 | -0.0037684 | 0.010104 | 0.027466 | 0.004578 | 0.032043 | 0.10529 | 0.10529 | 0.045776 | -0.073242 | -0.004578 | 0.041199 | -0.091553 | 0.027466 | 0.032043 | 0.068665 | -0.009155 | 120.076 | 119.957 | -0.83771 | 120.0348 | 120.1355 | 0.17853 | -0.91553 | 120.0989 | 120.0211 | -0.91553 | 120.0256 | 119.9387 | -0.082398 | -0.91095 | 120.1355 | 120.0577 | 120.0623 | -1.0162 | 120.0577 | 120.0623 | 120.0714 | -0.95215
3454.7031 | 121.1884 | -120.0394 | 0.90637 | 0.0054168 | 0.00049979 | 0.071508 | 0.026938 | -0.068468 | -0.028226 | -0.0011344 | 0.0073242 | 0.031101 | 0.005646 | -0.043113 | -0.0078272 | 0.011173 | 0.13275 | 0.17853 | 0.16937 | 0.16479 | 0.07782 | 0.07782 | -0.068665 | 0.073242 | 0.1831 | 0.036621 | -0.018311 | -0.009155 | 0.10071 | 0.022888 | 120.1172 | 119.9707 | -0.82855 | 120.2179 | 120.2042 | 0.23346 | -0.77362 | 120.1401 | 120.0623 | -0.92468 | 120.1126 | 120.076 | 0.013733 | -0.91553 | 120.1172 | 120.1721 | 120.2087 | -0.97504 | 120.0211 | 120.0302 | 120.2225 | -0.88348
3456.4375 | 121.17 | -120.4605 | 0.41657 | 0.013046 | 0.0051996 | 0.071722 | 0.026511 | -0.0721 | -0.025022 | -0.00049335 | -0.0003053 | 0.031529 | 0.0077822 | -0.044822 | -0.0054772 | 0.011813 | 0.11444 | 0.14191 | 0.16022 | 0.15106 | 0.036621 | 0.09613 | -0.045776 | 0.086975 | 0.13733 | 0.013733 | -0.036621 | -0.018311 | 0.10071 | 0.022888 | 120.5566 | 120.4147 | -0.37994 | 120.6024 | 120.6116 | 0.19684 | -0.30212 | 120.5612 | 120.4834 | -0.45319 | 120.5475 | 120.4742 | -0.009155 | -0.43488 | 120.4971 | 120.575 | 120.6207 | -0.46234 | 120.4239 | 120.4422 | 120.5978 | -0.39368
3458.25 | 121.0693 | -120.5429 | 0.47607 | 0.013046 | 0.00071339 | 0.070013 | 0.025015 | -0.068896 | -0.020535 | 0.0010018 | 0.0073242 | 0.034092 | 0.0054324 | -0.044181 | -0.0012048 | 0.010959 | 0.018311 | -0.018311 | 0.022888 | 0.059509 | 0.10071 | 0.064087 | -0.059509 | -0.032043 | -0.018311 | -0.14191 | 0.018311 | 0.036621 | 0.059509 | -0.027466 | 120.607 | 120.4834 | -0.37537 | 120.5246 | 120.6024 | 0.11902 | -0.45776 | 120.6024 | 120.5154 | -0.45776 | 120.5109 | 120.401 | -0.11444 | -0.43945 | 120.6436 | 120.5612 | 120.5658 | -0.53558 | 120.5612 | 120.5795 | 120.5246 | -0.50354
3460.0469 | 121.0602 | -120.6024 | 0.43488 | 0.013046 | -0.0016364 | 0.069799 | 0.024588 | -0.0674 | -0.022672 | 0.0027108 | 0.0073242 | 0.034306 | 0.0060732 | -0.043327 | -0.002273 | 0.015231 | -0.004578 | -0.045776 | -0.009155 | 0.054932 | 0.10071 | 0.064087 | -0.064087 | -0.018311 | -0.013733 | -0.13275 | 0.004578 | 0.050354 | 0.059509 | -0.013733 | 120.6665 | 120.5383 | -0.33417 | 120.5566 | 120.6573 | 0.11902 | -0.43945 | 120.6619 | 120.5887 | -0.4303 | 120.5841 | 120.4697 | -0.11902 | -0.38452 | 120.7031 | 120.5978 | 120.5933 | -0.49896 | 120.607 | 120.6528 | 120.5887 | -0.44861
3461.7812 | 121.1838 | -120.52 | 0.45776 | 0.013046 | 0.006695 | 0.072149 | 0.026511 | -0.068468 | -0.028226 | 0.00078825 | 0.0073242 | 0.028965 | 0.006287 | -0.044822 | -0.010391 | 0.01395 | 0.027466 | 0.050354 | 0.11444 | 0.10071 | 0.082397 | 0.082397 | -0.050354 | 0.009155 | 0.07782 | -0.027466 | -0.018311 | 0.004578 | 0.10071 | 0.018311 | 120.6024 | 120.4697 | -0.37537 | 120.5704 | 120.6207 | 0.15106 | -0.4303 | 120.6207 | 120.5383 | -0.47608 | 120.5292 | 120.4926 | -0.045777 | -0.45319 | 120.6024 | 120.5475 | 120.6345 | -0.50812 | 120.5017 | 120.5246 | 120.5978 | -0.43945
3463.5625 | 121.1105 | -120.4971 | 0.50812 | 0.0054168 | -0.0012092 | 0.07044 | 0.024802 | -0.06505 | -0.019467 | -0.00027975 | 0.0073242 | 0.036869 | 0.006287 | -0.042472 | -0.0031274 | 0.012454 | 0 | -0.036621 | 0.004578 | 0.073242 | 0.091553 | 0.050354 | -0.082397 | -0.032043 | -0.018311 | -0.14648 | 0.018311 | 0.041199 | 0.059509 | -0.018311 | 120.5475 | 120.4147 | -0.41656 | 120.4605 | 120.5704 | 0.15564 | -0.50812 | 120.5566 | 120.4788 | -0.48981 | 120.4651 | 120.3506 | -0.12817 | -0.46692 | 120.5887 | 120.4971 | 120.5017 | -0.59051 | 120.5154 | 120.5383 | 120.4788 | -0.52643
3465.375 | 121.1746 | -120.5566 | 0.52185 | -0.0022127 | -0.00014101 | 0.071081 | 0.028433 | -0.066973 | -0.025662 | -0.00049335 | 0.0073242 | 0.032383 | 0.0097048 | -0.043541 | -0.0071862 | 0.012454 | -0.013733 | 0.009155 | 0.022888 | 0.068665 | 0.091553 | 0.054932 | -0.09613 | -0.045776 | 0.036621 | -0.1236 | 0.027466 | 0.027466 | 0.050354 | -0.022888 | 120.6116 | 120.4605 | -0.4303 | 120.5658 | 120.6253 | 0.16479 | -0.53558 | 120.607 | 120.5338 | -0.49438 | 120.5109 | 120.433 | -0.10071 | -0.49438 | 120.6482 | 120.5429 | 120.5795 | -0.61798 | 120.5841 | 120.5841 | 120.5933 | -0.54474
3467.125 | 121.1746 | -120.4834 | 0.55847 | 0.013046 | 0.0026362 | 0.074712 | 0.026297 | -0.069537 | -0.025876 | -0.001348 | 0.0073242 | 0.032597 | 0.0094912 | -0.044395 | -0.011886 | 0.013095 | 0.059509 | 0.07782 | 0.11902 | 0.12817 | 0.054932 | 0.07782 | -0.036621 | 0.022888 | 0.082397 | -0.032043 | -0.018311 | 0.013733 | 0.091553 | 0.018311 | 120.5612 | 120.4468 | -0.50354 | 120.5612 | 120.6116 | 0.1648 | -0.49896 | 120.575 | 120.5017 | -0.57678 | 120.5063 | 120.4514 | -0.050354 | -0.54474 | 120.5383 | 120.5429 | 120.6024 | -0.59509 | 120.4651 | 120.4971 | 120.5658 | -0.54016
3468.9062 | 121.2021 | -120.5795 | 0.46234 | 0.013046 | -0.004627 | 0.071722 | 0.029074 | -0.066546 | -0.022885 | -0.00092075 | 0.0073242 | 0.031742 | 0.0086368 | -0.043754 | -0.0086816 | 0.010959 | 0.009155 | 0.018311 | 0.041199 | 0.07782 | 0.10529 | 0.054932 | -0.082397 | -0.041199 | 0.041199 | -0.09613 | 0.004578 | 0.045776 | 0.064087 | -0.018311 | 120.6345 | 120.4971 | -0.35706 | 120.5978 | 120.6573 | 0.16022 | -0.45319 | 120.6436 | 120.5612 | -0.45776 | 120.5383 | 120.4834 | -0.077819 | -0.41657 | 120.6848 | 120.5887 | 120.6207 | -0.54474 | 120.5841 | 120.6253 | 120.6207 | -0.48065
3470.6875 | 121.1014 | -120.0806 | 0.86517 | 0.020676 | -0.0012092 | 0.070654 | 0.025656 | -0.0674 | -0.019254 | 0.0044198 | 0.0073242 | 0.037083 | 0.0092776 | -0.044395 | -0.0048364 | 0.012241 | -0.004578 | -0.032043 | -0.004578 | 0.059509 | 0.086975 | 0.054932 | -0.082397 | -0.018311 | -0.022888 | -0.14648 | 0.027466 | 0.022888 | 0.064087 | -0.004578 | 120.1355 | 119.9982 | -0.7782 | 120.0485 | 120.1401 | 0.14191 | -0.86975 | 120.1447 | 120.076 | -0.83771 | 120.0623 | 119.9341 | -0.14191 | -0.84228 | 120.1675 | 120.076 | 120.076 | -0.94757 | 120.108 | 120.1035 | 120.0577 | -0.86975
3472.4844 | 121.2158 | -120.4376 | 0.72327 | 0.013046 | -0.00185 | 0.072149 | 0.02886 | -0.067187 | -0.029294 | 0.0012154 | 0.0073242 | 0.03217 | 0.007996 | -0.043113 | -0.0078272 | 0.013522 | 0.091553 | 0.12817 | 0.14648 | 0.14648 | 0.050354 | 0.07782 | -0.068665 | 0.050354 | 0.15564 | -0.009155 | -0.036621 | 0.013733 | 0.073242 | -0.009155 | 120.5154 | 120.369 | -0.67291 | 120.5658 | 120.5841 | 0.21515 | -0.63171 | 120.5109 | 120.4285 | -0.75989 | 120.488 | 120.4285 | 0 | -0.70953 | 120.488 | 120.5292 | 120.5841 | -0.79193 | 120.401 | 120.4514 | 120.5933 | -0.73242
3474.2188 | 121.3394 | -120.5017 | 0.57678 | 0.013046 | 0.0028498 | 0.07279 | 0.029715 | -0.066546 | -0.030789 | -0.0011344 | -0.0003053 | 0.029606 | 0.0043644 | -0.046318 | -0.0082544 | 0.01395 | 0.086975 | 0.13733 | 0.14191 | 0.13733 | 0.07782 | 0.07782 | -0.041199 | 0.064087 | 0.16937 | 0.045776 | -0.041199 | 0.004578 | 0.091553 | 0.018311 | 120.5795 | 120.4605 | -0.49896 | 120.639 | 120.639 | 0.17853 | -0.48981 | 120.5933 | 120.52 | -0.61798 | 120.5658 | 120.5475 | 0.027465 | -0.5722 | 120.5795 | 120.5887 | 120.6436 | -0.61798 | 120.4605 | 120.5063 | 120.6711 | -0.55847
3476.0156 | 121.1975 | -120.6482 | 0.47607 | 0.020676 | -0.0041998 | 0.070654 | 0.028647 | -0.067187 | -0.019895 | -0.00027975 | 0.0073242 | 0.034519 | 0.007996 | -0.043968 | -0.0054772 | 0.010745 | 0.022888 | 0.013733 | 0.032043 | 0.09613 | 0.10986 | 0.027466 | -0.09613 | 0.009155 | 0.059509 | -0.086975 | 0.004578 | 0.018311 | 0.064087 | -0.022888 | 120.6757 | 120.5521 | -0.36621 | 120.6619 | 120.7443 | 0.19226 | -0.45319 | 120.7123 | 120.6253 | -0.4715 | 120.6573 | 120.5612 | -0.064087 | -0.45776 | 120.7581 | 120.6711 | 120.6802 | -0.5722 | 120.6528 | 120.6665 | 120.7077 | -0.49896
3477.75 | 119.632 | -9.8923 | 109.5886 | -0.0098417 | 0.004986 | 0.072576 | 0.027152 | -0.066119 | -0.024594 | -0.00070715 | -0.0003053 | 0.031101 | 0.0082096 | -0.044181 | -0.0086816 | 0.012882 | 0.041199 | 0.082397 | 0.09613 | 0.082397 | 0.027466 | 0.041199 | -0.073242 | 0.004578 | 0.059509 | -0.054932 | -0.054932 | -0.041199 | 0.041199 | -0.027466 | 9.9335 | 9.819 | -109.5612 | 9.9747 | 9.9747 | 0.15564 | -109.5474 | 9.9335 | 9.8648 | -109.6436 | 9.8969 | 9.8373 | -0.027466 | -109.6298 | 9.9197 | 9.9335 | 9.9884 | -109.6619 | 9.8373 | 9.8511 | 9.9518 | -109.6161
3479.5312 | 120.6619 | -13.9389 | 106.7459 | 0.020676 | 0.0056268 | 0.069585 | 0.024802 | -0.068041 | -0.024594 | -6.615e-05 | 0.014954 | 0.031742 | 0.0054324 | -0.045036 | -0.0029138 | 0.012027 | 0.086975 | 0.10071 | 0.10529 | 0.1236 | 0.013733 | 0.041199 | -0.073242 | 0.064087 | 0.10071 | -0.013733 | -0.073242 | -0.073242 | 0.059509 | -0.009155 | 13.9801 | 13.8657 | -106.7322 | 14.0396 | 14.0625 | 0.19684 | -106.6589 | 13.9984 | 13.9297 | -106.8192 | 14.003 | 13.9252 | -0.004578 | -106.8192 | 13.9526 | 14.0259 | 14.0442 | -106.8192 | 13.8657 | 13.8657 | 14.0396 | -106.7551
3481.2656 | 108.6502 | -54.6753 | 66.0233 | 0.013046 | -0.0024908 | 0.069158 | 0.030142 | -0.066546 | -0.022885 | 0.00057465 | 0.0073242 | 0.034306 | 0.0088504 | -0.043113 | -0.00505 | 0.010318 | -0.004578 | -0.041199 | -0.009155 | 0.059509 | 0.09613 | 0.013733 | -0.11902 | -0.041199 | 0.013733 | -0.12817 | 0.009155 | 0.032043 | 0.045776 | -0.032043 | 54.689 | 54.5563 | -65.9271 | 54.6341 | 54.7348 | 0.17853 | -66.0278 | 54.7211 | 54.6433 | -66.0141 | 54.6341 | 54.5471 | -0.096131 | -65.9912 | 54.7714 | 54.6707 | 54.6661 | -66.1423 | 54.6844 | 54.7073 | 54.689 | -66.0553
3483.0625 | 121.3486 | -117.6041 | 3.392 | 0.013046 | 0.0026362 | 0.073003 | 0.030142 | -0.066973 | -0.028653 | -0.00027975 | 0.030213 | 0.02982 | 0.0050052 | -0.045036 | -0.0086816 | 0.013309 | 0.10529 | 0.16479 | 0.15564 | 0.15106 | 0.054932 | 0.073242 | -0.059509 | 0.07782 | 0.18768 | 0.027466 | -0.032043 | -0.027466 | 0.09613 | 0.009155 | 117.6773 | 117.5446 | -3.3371 | 117.7689 | 117.7551 | 0.21057 | -3.2867 | 117.7002 | 117.6132 | -3.4241 | 117.6819 | 117.6315 | 0.018311 | -3.4195 | 117.659 | 117.7094 | 117.7597 | -3.4515 | 117.572 | 117.5766 | 117.7917 | -3.3829
3484.8594 | 121.2753 | -118.8309 | 2.0416 | 0.0054168 | 0.0041314 | 0.071722 | 0.027579 | -0.070391 | -0.02609 | -6.615e-05 | -0.0079343 | 0.033238 | 0.0065006 | -0.043968 | -0.0071862 | 0.012882 | 0.10071 | 0.086975 | 0.1236 | 0.11444 | 0.050354 | 0.07782 | -0.041199 | 0.036621 | 0.091553 | -0.018311 | -0.022888 | 0.004578 | 0.11444 | 0.018311 | 118.9087 | 118.7897 | -1.9913 | 118.9178 | 118.9453 | 0.15564 | -1.9409 | 118.9453 | 118.8492 | -2.0645 | 118.8675 | 118.8126 | -0.036622 | -2.037 | 118.8812 | 118.9316 | 118.9545 | -2.0828 | 118.808 | 118.8354 | 118.9224 | -2.0233
3486.6562 | 121.2158 | -119.1605 | 1.8082 | -0.0022127 | -0.00078181 | 0.07044 | 0.024802 | -0.068041 | -0.019467 | 0.0033518 | 0.014954 | 0.036442 | 0.0065006 | -0.042045 | -0.0018458 | 0.011173 | 0.082397 | 0.068665 | 0.068665 | 0.11444 | 0.073242 | 0.045776 | -0.10071 | 0.036621 | 0.064087 | -0.086975 | 0.009155 | 0.018311 | 0.054932 | 0.004578 | 119.2062 | 119.0598 | -1.7349 | 119.2291 | 119.2749 | 0.21515 | -1.7258 | 119.2154 | 119.165 | -1.799 | 119.1971 | 119.0735 | -0.091553 | -1.7899 | 119.2337 | 119.2429 | 119.2291 | -1.9089 | 119.1696 | 119.1788 | 119.2245 | -1.8036
3488.3906 | 121.3165 | -120.3827 | 0.54016 | 0.020676 | 0.004986 | 0.073431 | 0.025656 | -0.068041 | -0.025449 | 0.0027108 | 0.0073242 | 0.030888 | 0.0069278 | -0.043541 | -0.0069726 | 0.011813 | 0.10071 | 0.13733 | 0.16479 | 0.14191 | 0.050354 | 0.082397 | -0.022888 | 0.07782 | 0.11902 | 0.027466 | -0.022888 | -0.013733 | 0.10529 | 0.004578 | 120.4651 | 120.3598 | -0.48981 | 120.52 | 120.5246 | 0.16479 | -0.43945 | 120.488 | 120.3873 | -0.56305 | 120.4605 | 120.4102 | 0.022888 | -0.55389 | 120.433 | 120.4834 | 120.5475 | -0.56305 | 120.3598 | 120.369 | 120.5017 | -0.53558
3490.1875 | 121.3486 | -120.0806 | 0.91095 | -0.0022127 | 0.0024224 | 0.073431 | 0.02886 | -0.068041 | -0.029721 | -6.615e-05 | 0.0073242 | 0.030033 | 0.007355 | -0.044822 | -0.0093226 | 0.0116 | 0.10986 | 0.14191 | 0.16022 | 0.16479 | 0.054932 | 0.073242 | -0.036621 | 0.073242 | 0.17395 | 0.059509 | -0.018311 | -0.004578 | 0.09613 | 0.013733 | 120.1538 | 120.0439 | -0.85602 | 120.2225 | 120.2454 | 0.20142 | -0.80109 | 120.1767 | 120.0943 | -0.92926 | 120.1538 | 120.1401 | 0.045776 | -0.91553 | 120.1355 | 120.1904 | 120.2408 | -0.94757 | 120.0623 | 120.076 | 120.2545 | -0.89722
3491.9688 | 121.3348 | -103.7521 | 17.0929 | 0.013046 | 0.0062676 | 0.074712 | 0.029501 | -0.070177 | -0.028653 | -0.0011344 | 0.014954 | 0.031101 | 0.006287 | -0.042259 | -0.0078272 | 0.010959 | 0.045776 | 0.082397 | 0.10529 | 0.10986 | 0.054932 | 0.073242 | -0.064087 | 0.041199 | 0.10986 | 0.004578 | -0.018311 | -0.018311 | 0.082397 | 0.004578 | 103.8254 | 103.688 | -17.038 | 103.8345 | 103.862 | 0.17395 | -17.0471 | 103.8345 | 103.7567 | -17.1112 | 103.7933 | 103.7567 | 0 | -17.1112 | 103.8071 | 103.7979 | 103.8574 | -17.157 | 103.7338 | 103.7338 | 103.862 | -17.0883
3493.75 | 121.4447 | -119.9295 | 1.0345 | 0.013046 | 0.003277 | 0.07044 | 0.023734 | -0.068682 | -0.021176 | -0.00027975 | 0.0073242 | 0.033238 | 0.0047916 | -0.042686 | -0.0027002 | 0.010959 | 0.068665 | 0.045776 | 0.059509 | 0.10529 | 0.091553 | 0.07782 | -0.050354 | 0.059509 | 0.09613 | -0.041199 | 0.004578 | -0.009155 | 0.10529 | 0.036621 | 120.0073 | 119.8791 | -0.94299 | 119.9753 | 120.0348 | 0.15564 | -0.96588 | 120.0348 | 119.9661 | -1.03 | 119.989 | 119.8883 | -0.07782 | -1.0437 | 120.0211 | 119.9982 | 119.989 | -1.0849 | 119.9341 | 119.9203 | 120.0256 | -0.99792
3495.4688 | 121.3943 | -119.5633 | 1.5289 | 0.013046 | 0.0071222 | 0.073217 | 0.027792 | -0.070605 | -0.028653 | 0.00207 | 0.0073242 | 0.030888 | 0.006287 | -0.04525 | -0.0054772 | 0.014377 | 0.064087 | 0.10529 | 0.1236 | 0.11444 | 0.059509 | 0.07782 | -0.041199 | 0.041199 | 0.086975 | -0.027466 | -0.018311 | -0.009155 | 0.10071 | 0.004578 | 119.6411 | 119.5221 | -1.4694 | 119.6686 | 119.6777 | 0.15564 | -1.4648 | 119.664 | 119.5679 | -1.5472 | 119.6045 | 119.5358 | -0.032044 | -1.5381 | 119.6228 | 119.6274 | 119.6869 | -1.5701 | 119.545 | 119.5541 | 119.6503 | -1.5244
3497.25 | 121.344 | -119.6182 | 1.4648 | 0.013046 | 0.00028619 | 0.067236 | 0.027792 | -0.069964 | -0.018613 | 0.0022836 | 0.0073242 | 0.035801 | 0.0071414 | -0.043327 | -0.0024866 | 0.0098907 | 0.009155 | -0.036621 | 0.018311 | 0.064087 | 0.091553 | 0.050354 | -0.082397 | -0.013733 | -0.022888 | -0.12817 | 0.013733 | 0.009155 | 0.054932 | -0.022888 | 119.6686 | 119.5358 | -1.3733 | 119.5816 | 119.6823 | 0.14648 | -1.4557 | 119.6732 | 119.5953 | -1.4511 | 119.6045 | 119.4901 | -0.10529 | -1.4557 | 119.7098 | 119.6274 | 119.6365 | -1.5472 | 119.632 | 119.6274 | 119.5953 | -1.4877
3499.0312 | 120.2042 | -120.0073 | 0.13733 | 0.0054168 | -0.00078181 | 0.07044 | 0.030142 | -0.066759 | -0.02609 | 0.00036105 | 0.014954 | 0.031529 | 0.0097048 | -0.044181 | -0.006759 | 0.012454 | 0.054932 | 0.073242 | 0.086975 | 0.10986 | 0.07782 | 0.041199 | -0.073242 | -0.018311 | 0.054932 | -0.10071 | 0.009155 | 0.027466 | 0.050354 | -0.009155 | 120.0485 | 119.9341 | -0.059509 | 120.0806 | 120.1172 | 0.18311 | -0.082397 | 120.0577 | 119.9982 | -0.12817 | 119.989 | 119.9066 | -0.091553 | -0.10986 | 120.0851 | 120.0623 | 120.0943 | -0.21057 | 120.0165 | 120.0348 | 120.0623 | -0.14648
3500.8281 | 120.9824 | -120.6573 | 0.059509 | 0.0054168 | 0.0011408 | 0.070654 | 0.026511 | -0.068682 | -0.023953 | 0.00078825 | 0.014954 | 0.032597 | 0.0065006 | -0.041191 | -0.0054772 | 0.013736 | 0.1236 | 0.12817 | 0.15106 | 0.15564 | 0.050354 | 0.10071 | -0.036621 | 0.10071 | 0.14191 | 0.027466 | -0.045776 | -0.009155 | 0.10529 | 0.022888 | 120.7581 | 120.6207 | -0.009155 | 120.7855 | 120.813 | 0.19226 | 0.064087 | 120.7626 | 120.6802 | -0.10528 | 120.7581 | 120.6848 | 0.004578 | -0.068664 | 120.7077 | 120.7809 | 120.8084 | -0.09613 | 120.6116 | 120.6482 | 120.7993 | -0.036621
3502.6406 | 121.0968 | -120.7489 | 0.059509 | 0.0054168 | 0.0030634 | 0.076208 | 0.024802 | -0.068468 | -0.028867 | 0.00014745 | 0.022583 | 0.030674 | 0.0054324 | -0.043327 | -0.0065454 | 0.012241 | 0.10529 | 0.16022 | 0.15564 | 0.14648 | 0.068665 | 0.086975 | -0.050354 | 0.091553 | 0.1831 | 0.041199 | -0.022888 | -0.018311 | 0.10529 | 0.032043 | 120.8359 | 120.6985 | 0.009156 | 120.9091 | 120.8954 | 0.19684 | 0.045777 | 120.8542 | 120.7809 | -0.082397 | 120.8405 | 120.7901 | 0.009156 | -0.07782 | 120.8176 | 120.8542 | 120.9045 | -0.10986 | 120.726 | 120.7306 | 120.932 | -0.027466
3504.4219 | 121.051 | -120.8542 | 0.086975 | -0.0022127 | 0.00028619 | 0.073858 | 0.029929 | -0.068041 | -0.026944 | 0.00036105 | 0.014954 | 0.031956 | 0.0069278 | -0.043968 | -0.0071862 | 0.012882 | 0.09613 | 0.13733 | 0.16022 | 0.16022 | 0.050354 | 0.086975 | -0.064087 | 0.086975 | 0.17853 | 0.027466 | -0.032043 | -0.004578 | 0.091553 | 0.018311 | 120.9412 | 120.7901 | -0.036621 | 120.9915 | 121.0144 | 0.2243 | 0.009155 | 120.9457 | 120.8725 | -0.11902 | 120.9412 | 120.8817 | 0.009155 | -0.091553 | 120.9045 | 120.9503 | 121.0144 | -0.15106 | 120.8221 | 120.8496 | 121.0327 | -0.068664
3506.1562 | 121.1884 | -120.8359 | 0.07782 | 0.013046 | 0.0022088 | 0.070867 | 0.026938 | -0.069537 | -0.021176 | 0.0012154 | 0.014954 | 0.033238 | 0.0067142 | -0.042686 | -0.00505 | 0.011386 | 0.054932 | 0.027466 | 0.07782 | 0.091553 | 0.086975 | 0.068665 | -0.068665 | 0.064087 | 0.086975 | -0.032043 | -0.013733 | 0.013733 | 0.07782 | 0.027466 | 120.9045 | 120.7672 | 0.009155 | 120.8633 | 120.9274 | 0.16022 | -0.022888 | 120.9137 | 120.8633 | -0.091553 | 120.9 | 120.8038 | -0.059509 | -0.064087 | 120.9229 | 120.8908 | 120.9137 | -0.14649 | 120.8221 | 120.8496 | 120.9229 | -0.050354
3507.9531 | 120.8633 | -120.9091 | 0.1236 | 0.013046 | -0.0020636 | 0.067022 | 0.02822 | -0.068468 | -0.018826 | 0.0029244 | -0.0003053 | 0.035801 | 0.010559 | -0.043968 | -0.003982 | 0.011813 | 0.068665 | 0.036621 | 0.050354 | 0.10071 | 0.10071 | 0.064087 | -0.07782 | 0 | 0.036621 | -0.10529 | 0.004578 | 0.032043 | 0.086975 | -0.018311 | 120.9732 | 120.8313 | -0.022888 | 120.9457 | 121.0098 | 0.17853 | -0.054931 | 120.9961 | 120.8908 | -0.11902 | 120.9091 | 120.8038 | -0.086975 | -0.091553 | 121.0098 | 120.9778 | 120.9595 | -0.20142 | 120.9137 | 120.9412 | 120.9457 | -0.14191
3509.7344 | 121.2341 | -120.8954 | 0.073242 | 0.013046 | 0.0019952 | 0.071722 | 0.026297 | -0.069964 | -0.02139 | 0.0024972 | 0.0073242 | 0.034306 | 0.0094912 | -0.0429 | -0.0048364 | 0.013736 | 0.022888 | 0 | 0.036621 | 0.082397 | 0.10071 | 0.050354 | -0.064087 | 0.027466 | 0.041199 | -0.073242 | 0.004578 | 0.013733 | 0.086975 | 0.013733 | 120.9457 | 120.8313 | 0.027466 | 120.8954 | 120.9778 | 0.14648 | -0.050354 | 120.9824 | 120.9091 | -0.068664 | 120.9229 | 120.8221 | -0.086975 | -0.059509 | 120.9961 | 120.9183 | 120.932 | -0.13733 | 120.9 | 120.9091 | 120.9366 | -0.059509
3511.4531 | 121.2296 | -120.9091 | 0.064087 | 0.0054168 | 0.0034906 | 0.070013 | 0.027152 | -0.0721 | -0.026517 | 0.0033518 | 0.0073242 | 0.031956 | 0.0054324 | -0.043541 | -0.0052636 | 0.012668 | 0.086975 | 0.1236 | 0.14191 | 0.14648 | 0.045776 | 0.10071 | -0.027466 | 0.086975 | 0.13275 | 0.009155 | -0.032043 | -0.013733 | 0.11444 | 0.027466 | 121.0098 | 120.8817 | -0.018311 | 121.0327 | 121.0556 | 0.17395 | 0.022888 | 121.0236 | 120.9366 | -0.09613 | 120.9961 | 120.9183 | -0.018311 | -0.07782 | 120.9549 | 120.9961 | 121.051 | -0.091553 | 120.8771 | 120.8954 | 121.0419 | -0.036621
3513.25 | 121.2524 | -120.9595 | 0.059509 | 0.013046 | 0.0011408 | 0.07044 | 0.02587 | -0.069537 | -0.022244 | 0.00207 | -0.0003053 | 0.033665 | 0.0069278 | -0.044395 | -0.00505 | 0.012454 | 0 | 0.004578 | 0.018311 | 0.082397 | 0.09613 | 0.064087 | -0.068665 | -0.004578 | 0.022888 | -0.086975 | 0.013733 | 0.036621 | 0.07782 | -0.004578 | 121.0236 | 120.8908 | 0.036621 | 120.9641 | 121.0419 | 0.15106 | -0.059509 | 121.0373 | 120.9549 | -0.045776 | 120.9549 | 120.8725 | -0.082397 | -0.022888 | 121.0556 | 120.9595 | 120.9778 | -0.12817 | 120.9732 | 120.9961 | 120.9824 | -0.064087
3515.0469 | 121.2387 | -120.9778 | 0.054932 | 0.013046 | 0.004345 | 0.071294 | 0.028433 | -0.067828 | -0.026303 | -0.00070715 | 0.0073242 | 0.03281 | 0.007355 | -0.043541 | -0.0078272 | 0.014804 | 0.10071 | 0.14191 | 0.17853 | 0.15564 | 0.041199 | 0.10529 | -0.045776 | 0.073242 | 0.13275 | 0.018311 | -0.041199 | -0.013733 | 0.11902 | 0.032043 | 121.0831 | 120.932 | -0.013733 | 121.1197 | 121.1334 | 0.20142 | 0.045776 | 121.0968 | 121.0098 | -0.096131 | 121.051 | 120.9961 | -0.013732 | -0.068665 | 121.019 | 121.0785 | 121.1563 | -0.10071 | 120.9366 | 120.9641 | 121.1105 | -0.022889
3516.7656 | 121.2845 | -121.0007 | 0.054932 | 0.013046 | 0.0041314 | 0.067449 | 0.025656 | -0.067614 | -0.024167 | 0.0018564 | 0.014954 | 0.030033 | 0.007355 | -0.042259 | -0.0059046 | 0.013095 | 0.10529 | 0.13275 | 0.14648 | 0.16479 | 0.050354 | 0.10529 | -0.041199 | 0.082397 | 0.13275 | 0.018311 | -0.036621 | -0.018311 | 0.10529 | 0.022888 | 121.106 | 120.9595 | -0.004578 | 121.1334 | 121.1655 | 0.20599 | 0.050354 | 121.106 | 121.0236 | -0.091553 | 121.0831 | 121.019 | -0.004577 | -0.073243 | 121.051 | 121.106 | 121.1472 | -0.096131 | 120.9641 | 120.9824 | 121.1334 | -0.032044
3518.5625 | 121.2616 | -121.0236 | 0.082397 | 0.013046 | 0.0058404 | 0.070654 | 0.029288 | -0.070177 | -0.025662 | 0.00057465 | 0.014954 | 0.031529 | 0.0084232 | -0.043113 | -0.0063318 | 0.015445 | 0.07782 | 0.11902 | 0.14191 | 0.12817 | 0.045776 | 0.09613 | -0.032043 | 0.050354 | 0.10529 | 0.004578 | -0.018311 | -0.004578 | 0.09613 | 0.013733 | 121.1197 | 120.9915 | -0.036621 | 121.1426 | 121.1517 | 0.16022 | -0.004577 | 121.1197 | 121.0373 | -0.10071 | 121.0739 | 121.0281 | -0.009155 | -0.086975 | 121.0693 | 121.1014 | 121.1655 | -0.11444 | 121.0052 | 121.019 | 121.1288 | -0.068664
3520.3125 | 121.2753 | -121.0373 | 0.073242 | 0.013046 | 0.006054 | 0.071722 | 0.025443 | -0.068896 | -0.026303 | 0.00207 | 0.0073242 | 0.030247 | 0.0058596 | -0.043754 | -0.0076136 | 0.013522 | 0.10071 | 0.1236 | 0.14648 | 0.14648 | 0.050354 | 0.07782 | -0.036621 | 0.073242 | 0.13275 | 0.018311 | -0.032043 | 0.004578 | 0.10071 | 0.013733 | 121.1151 | 121.0007 | -0.022888 | 121.1609 | 121.1838 | 0.18311 | 0.027466 | 121.138 | 121.051 | -0.10529 | 121.1105 | 121.0556 | 0.004578 | -0.068664 | 121.0876 | 121.138 | 121.1838 | -0.10986 | 121.0052 | 121.0419 | 121.17 | -0.059509
3522.0469 | 120.9549 | -121.019 | 0.10529 | 0.013046 | -0.00099541 | 0.070867 | 0.030997 | -0.065478 | -0.026517 | 0.00014745 | 0.014954 | 0.031315 | 0.0084232 | -0.041832 | -0.0069726 | 0.0098907 | 0.009155 | 0.032043 | 0.064087 | 0.086975 | 0.10529 | 0.054932 | -0.068665 | -0.032043 | 0.041199 | -0.09613 | 0.022888 | 0.032043 | 0.054932 | -0.022888 | 121.0739 | 120.9503 | 0 | 121.051 | 121.106 | 0.15564 | -0.096131 | 121.0739 | 120.9961 | -0.082398 | 120.9869 | 120.9229 | -0.073242 | -0.073243 | 121.1243 | 121.0281 | 121.0831 | -0.17395 | 121.0419 | 121.051 | 121.0602 | -0.12817
3523.8281 | 121.3348 | -121.0831 | 0.059509 | -0.0022127 | 0.004345 | 0.073644 | 0.028433 | -0.072314 | -0.029508 | -0.0019888 | 0.014954 | 0.030888 | 0.0060732 | -0.043327 | -0.0078272 | 0.012454 | 0.032043 | 0.064087 | 0.11444 | 0.10986 | 0.068665 | 0.07782 | -0.050354 | 0.018311 | 0.086975 | -0.018311 | -0.009155 | 0 | 0.086975 | 0.004578 | 121.1609 | 121.0327 | 0.009156 | 121.1472 | 121.1929 | 0.16022 | -0.027466 | 121.17 | 121.0876 | -0.068664 | 121.1014 | 121.0648 | -0.022889 | -0.059509 | 121.1517 | 121.1151 | 121.1975 | -0.10986 | 121.0739 | 121.0831 | 121.17 | -0.054931
3525.625 | 120.8267 | -120.5978 | 0.082397 | 0.0054168 | -0.00078181 | 0.069799 | 0.025015 | -0.070391 | -0.01904 | -0.00027975 | 0.0073242 | 0.03516 | 0.0082096 | -0.042472 | -0.003341 | 0.0079681 | 0.041199 | 0.022888 | 0.036621 | 0.10529 | 0.10986 | 0.068665 | -0.073242 | 0.022888 | 0.059509 | -0.068665 | 0.018311 | 0.027466 | 0.064087 | -0.004578 | 120.6665 | 120.5246 | 0.027466 | 120.6207 | 120.7031 | 0.17853 | -0.041198 | 120.6619 | 120.5933 | -0.064086 | 120.6207 | 120.5292 | -0.064087 | -0.054931 | 120.7077 | 120.639 | 120.6345 | -0.15564 | 120.6161 | 120.6253 | 120.6573 | -0.086975
3527.4531 | 121.2891 | -121.1105 | 0.10071 | 0.013046 | 0.00092719 | 0.070867 | 0.02886 | -0.06975 | -0.028653 | 0.0010018 | 0.014954 | 0.030461 | 0.0058596 | -0.043541 | -0.006759 | 0.012241 | 0.10529 | 0.14191 | 0.16479 | 0.15564 | 0.064087 | 0.082397 | -0.041199 | 0.07782 | 0.1831 | 0.036621 | -0.022888 | -0.004578 | 0.10071 | 0.018311 | 121.1929 | 121.0693 | -0.036621 | 121.2524 | 121.2662 | 0.19684 | 0.004578 | 121.2112 | 121.1288 | -0.1236 | 121.1884 | 121.1472 | 0.01831 | -0.10529 | 121.1746 | 121.2158 | 121.2753 | -0.14191 | 121.0876 | 121.106 | 121.2936 | -0.082397
3529.2344 | 121.2067 | -121.0922 | 0.10986 | 0.0054168 | -0.0022772 | 0.073003 | 0.030142 | -0.068468 | -0.024594 | -0.00092075 | -0.0003053 | 0.030888 | 0.0075686 | -0.040763 | -0.008468 | 0.012241 | 0.050354 | 0.050354 | 0.082397 | 0.10529 | 0.10071 | 0.068665 | -0.086975 | -0.032043 | 0.068665 | -0.086975 | 0.004578 | 0.032043 | 0.059509 | -0.022888 | 121.1609 | 121.0052 | -0.009155 | 121.1426 | 121.1975 | 0.19226 | -0.059509 | 121.1517 | 121.0693 | -0.10529 | 121.0602 | 121.0052 | -0.064087 | -0.07782 | 121.1929 | 121.1426 | 121.1746 | -0.19684 | 121.0968 | 121.1243 | 121.1609 | -0.13275
3530.9844 | 121.3715 | -121.0876 | 0.07782 | -0.0022127 | 0.0034906 | 0.072576 | 0.027152 | -0.06505 | -0.029935 | -0.0022024 | 0.0073242 | 0.030247 | 0.0050052 | -0.042686 | -0.0074 | 0.011386 | 0.14191 | 0.16937 | 0.18768 | 0.17853 | 0.054932 | 0.082397 | -0.064087 | 0.082397 | 0.18768 | 0.032043 | -0.027466 | -0.009155 | 0.11902 | 0.013733 | 121.17 | 121.0236 | -0.022888 | 121.257 | 121.2662 | 0.24261 | 0.064087 | 121.2067 | 121.1014 | -0.10529 | 121.17 | 121.1197 | 0.01831 | -0.086975 | 121.1426 | 121.2296 | 121.2753 | -0.14191 | 121.0602 | 121.0785 | 121.2753 | -0.064087
3532.7812 | 121.4172 | -121.0602 | 0.068665 | 0.013046 | 0.0028498 | 0.069372 | 0.027152 | -0.070391 | -0.020108 | 0.00036105 | 0.0073242 | 0.034306 | 0.0067142 | -0.042686 | -0.0046228 | 0.0094635 | 0.045776 | 0.004578 | 0.032043 | 0.059509 | 0.10071 | 0.045776 | -0.082397 | 0.027466 | 0.036621 | -0.073242 | 0.004578 | 0.013733 | 0.07782 | 0 | 121.106 | 120.9778 | 0.032043 | 121.0648 | 121.1197 | 0.14191 | -0.022889 | 121.138 | 121.0602 | -0.064087 | 121.0876 | 120.9869 | -0.073242 | -0.054932 | 121.1609 | 121.106 | 121.0922 | -0.15106 | 121.0648 | 121.0739 | 121.0968 | -0.068665
3534.5781 | 121.4127 | -121.1334 | 0.082397 | 0.013046 | 0.004345 | 0.071508 | 0.027365 | -0.068682 | -0.029721 | -0.0011344 | 0.022583 | 0.030461 | 0.0067142 | -0.0429 | -0.0080408 | 0.011813 | 0.032043 | 0.059509 | 0.10071 | 0.1236 | 0.068665 | 0.07782 | -0.032043 | 0.022888 | 0.09613 | -0.013733 | -0.004578 | -0.004578 | 0.091553 | 0.004578 | 121.2112 | 121.1014 | -0.013732 | 121.1929 | 121.257 | 0.15564 | -0.050354 | 121.225 | 121.138 | -0.086975 | 121.1563 | 121.1197 | -0.018311 | -0.086975 | 121.2021 | 121.1655 | 121.2341 | -0.11444 | 121.1288 | 121.1288 | 121.2296 | -0.077819
3536.3594 | 121.4264 | -121.1243 | 0.064087 | 0.0054168 | 0.0034906 | 0.073217 | 0.028433 | -0.070391 | -0.027799 | -0.00070715 | -0.0003053 | 0.030888 | 0.0075686 | -0.041832 | -0.0080408 | 0.014591 | 0.045776 | 0.068665 | 0.10071 | 0.11444 | 0.068665 | 0.091553 | -0.045776 | 0.027466 | 0.07782 | -0.027466 | -0.027466 | -0.009155 | 0.09613 | 0.018311 | 121.2158 | 121.0785 | 0.004578 | 121.1929 | 121.2387 | 0.16022 | -0.018311 | 121.2204 | 121.1426 | -0.091553 | 121.1517 | 121.0968 | -0.045777 | -0.073242 | 121.1929 | 121.17 | 121.225 | -0.10986 | 121.0968 | 121.1151 | 121.2021 | -0.045776
3538.0938 | 116.2445 | -77.2659 | 38.7039 | 0.020676 | 0.0034906 | 0.073431 | 0.02886 | -0.06975 | -0.026303 | -0.0019888 | 0.014954 | 0.030033 | 0.0058596 | -0.043541 | -0.0048364 | 0.012027 | 0.050354 | 0.068665 | 0.091553 | 0.10986 | 0.045776 | 0.086975 | -0.064087 | 0.009155 | 0.054932 | -0.045776 | -0.032043 | -0.022888 | 0.068665 | 0.009155 | 77.3529 | 77.2018 | -38.6581 | 77.3346 | 77.3758 | 0.17395 | -38.6536 | 77.3346 | 77.2751 | -38.736 | 77.2751 | 77.2202 | -0.054931 | -38.7268 | 77.3117 | 77.3163 | 77.3575 | -38.768 | 77.2339 | 77.243 | 77.3209 | -38.6948
3539.875 | 121.1014 | -5.3329 | 114.6698 | 0.013046 | 0.00092719 | 0.071722 | 0.029929 | -0.066973 | -0.023953 | -0.00027975 | -0.0003053 | 0.03281 | 0.0075686 | -0.044609 | -0.0054772 | 0.0083953 | 0.082397 | 0.10071 | 0.11902 | 0.11444 | 0.022888 | 0.041199 | -0.09613 | 0.041199 | 0.13733 | -0.018311 | -0.068665 | -0.027466 | 0.041199 | -0.027466 | 5.3741 | 5.2368 | -114.6469 | 5.4337 | 5.4474 | 0.21057 | -114.5874 | 5.3741 | 5.3055 | -114.7385 | 5.3741 | 5.3146 | 0.009155 | -114.6973 | 5.3558 | 5.4153 | 5.452 | -114.7659 | 5.2643 | 5.3055 | 5.4703 | -114.6973
3541.6094 | 121.0831 | -3.9597 | 116.3361 | 0.013046 | 0.003277 | 0.07279 | 0.029501 | -0.068896 | -0.027371 | -0.00027975 | -0.0003053 | 0.030888 | 0.0071414 | -0.044822 | -0.0059046 | 0.011813 | 0.07782 | 0.11902 | 0.14191 | 0.11902 | 0.018311 | 0.045776 | -0.082397 | 0.064087 | 0.14191 | 0.004578 | -0.059509 | -0.064087 | 0.050354 | -0.032043 | 4.0054 | 3.8773 | -116.3177 | 4.0787 | 4.0787 | 0.20142 | -116.2582 | 4.01 | 3.9276 | -116.3956 | 4.0237 | 3.9642 | 0.036621 | -116.4001 | 3.978 | 4.0375 | 4.1016 | -116.4185 | 3.9001 | 3.8956 | 4.1016 | -116.3681
3543.4062 | 121.1792 | -4.0009 | 108.2565 | -0.0022127 | 0.00028619 | 0.072363 | 0.028647 | -0.067828 | -0.023313 | -0.00049335 | 0.0073242 | 0.034519 | 0.0069278 | -0.041404 | -0.0052636 | 0.011813 | -0.004578 | -0.018311 | 0.009155 | 0.036621 | 0.045776 | 0.009155 | -0.11902 | -0.050354 | 0 | -0.12817 | -0.018311 | 0 | 0.013733 | -0.054932 | 4.01 | 3.8818 | -108.2108 | 3.9825 | 4.0375 | 0.15564 | -108.2611 | 4.0146 | 3.9459 | -108.2748 | 3.9505 | 3.8727 | -0.073242 | -108.2565 | 4.0466 | 3.9963 | 4.01 | -108.3755 | 3.9825 | 4.0009 | 4.0009 | -108.3115
3545.2031 | 120.8862 | -2.9755 | 111.3693 | -0.0098417 | -0.00185 | 0.066808 | 0.026938 | -0.068255 | -0.019681 | 0.00057465 | 0.014954 | 0.036442 | 0.007355 | -0.0429 | -0.0048364 | 0.0096771 | 0.032043 | -0.009155 | 0.013733 | 0.064087 | 0.059509 | 0.013733 | -0.11902 | 0.013733 | 0.045776 | -0.10529 | -0.041199 | -0.004578 | 0.022888 | -0.054932 | 2.9892 | 2.8564 | -111.3098 | 2.9663 | 3.0396 | 0.18311 | -111.3373 | 2.9984 | 2.9205 | -111.4105 | 2.9892 | 2.8702 | -0.050354 | -111.3739 | 3.035 | 3.0075 | 2.9892 | -111.4883 | 2.9343 | 2.9709 | 3.0212 | -111.4243
3546.9219 | 121.3211 | -3.7674 | 116.8304 | 0.013046 | 0.0026362 | 0.070867 | 0.023306 | -0.06975 | -0.025449 | 0.0010018 | 0.0073242 | 0.03217 | 0.0037234 | -0.043968 | -0.003982 | 0.0116 | 0.07782 | 0.082397 | 0.10071 | 0.11444 | 0.013733 | 0.041199 | -0.050354 | 0.059509 | 0.10529 | -0.018311 | -0.068665 | -0.027466 | 0.059509 | 0 | 3.8086 | 3.717 | -116.8167 | 3.8498 | 3.8818 | 0.16479 | -116.7526 | 3.8269 | 3.7674 | -116.8991 | 3.8269 | 3.7491 | -0.018311 | -116.8579 | 3.7811 | 3.8452 | 3.8681 | -116.8808 | 3.6987 | 3.7399 | 3.8727 | -116.8304
3548.7188 | 121.2341 | -4.129 | 117.0731 | 0.013046 | 0.00049979 | 0.067449 | 0.024588 | -0.068255 | -0.019467 | 0.0029244 | 0.0073242 | 0.035801 | 0.007355 | -0.042045 | -0.0041956 | 0.012241 | -0.032043 | -0.082397 | -0.032043 | 0.013733 | 0.059509 | 0.018311 | -0.11444 | -0.059509 | -0.045776 | -0.16022 | -0.022888 | -0.009155 | 0.018311 | -0.041199 | 4.1473 | 4.0146 | -117.0135 | 4.0466 | 4.1428 | 0.12817 | -117.1051 | 4.1473 | 4.0878 | -117.0959 | 4.0695 | 3.9688 | -0.11902 | -117.0822 | 4.1885 | 4.097 | 4.097 | -117.1875 | 4.1061 | 4.1199 | 4.0833 | -117.1143
3550.5156 | 102.5116 | -45.6619 | 75.4623 | 0.013046 | -0.00078181 | 0.067876 | 0.026724 | -0.068468 | -0.023526 | 0.00078825 | 0.0073242 | 0.034519 | 0.0112 | -0.043327 | -0.005691 | 0.010318 | 0.022888 | 0.009155 | 0.036621 | 0.086975 | 0.086975 | 0.032043 | -0.09613 | 0.013733 | 0.064087 | -0.091553 | -0.013733 | 0.004578 | 0.059509 | -0.022888 | 45.694 | 45.5658 | -75.3754 | 45.6711 | 45.7489 | 0.1831 | -75.4395 | 45.7214 | 45.639 | -75.4761 | 45.6757 | 45.5704 | -0.068665 | -75.4578 | 45.7489 | 45.6848 | 45.6985 | -75.5585 | 45.6482 | 45.6665 | 45.726 | -75.4852
3552.25 | 120.9595 | -115.7822 | 4.7424 | 0.013046 | 0.0071222 | 0.073217 | 0.027792 | -0.069964 | -0.029721 | 0.00036105 | -0.0003053 | 0.03281 | 0.006287 | -0.043113 | -0.0061182 | 0.015018 | 0.059509 | 0.086975 | 0.10986 | 0.10529 | 0.059509 | 0.086975 | -0.036621 | 0.018311 | 0.10071 | -0.022888 | -0.018311 | 0.009155 | 0.086975 | 0.018311 | 115.8691 | 115.7455 | -4.6829 | 115.8691 | 115.8875 | 0.14191 | -4.6829 | 115.8691 | 115.8005 | -4.7607 | 115.8005 | 115.7593 | -0.041199 | -4.7333 | 115.8417 | 115.8417 | 115.892 | -4.7791 | 115.7639 | 115.7913 | 115.8829 | -4.7241
3554.0469 | 121.2708 | -113.5941 | 7.251 | 0.013046 | 0.0051996 | 0.07044 | 0.02886 | -0.067187 | -0.030149 | -0.0015616 | 0.0073242 | 0.031956 | 0.007996 | -0.044822 | -0.0091088 | 0.012668 | 0.064087 | 0.086975 | 0.11902 | 0.1236 | 0.068665 | 0.086975 | -0.073242 | 0.036621 | 0.15106 | 0.013733 | -0.009155 | -0.009155 | 0.10071 | 0.004578 | 113.681 | 113.5208 | -7.1823 | 113.681 | 113.7177 | 0.19684 | -7.1869 | 113.6948 | 113.5986 | -7.2601 | 113.6307 | 113.6078 | 0.009155 | -7.2601 | 113.6627 | 113.6581 | 113.7131 | -7.3242 | 113.5849 | 113.5849 | 113.7451 | -7.2464
3555.7656 | 121.3028 | -97.4167 | 23.2681 | 0.020676 | 0.0026362 | 0.072149 | 0.023947 | -0.068255 | -0.02139 | 0.00207 | 0.0073242 | 0.03217 | 0.0071414 | -0.044395 | -0.0046228 | 0.013095 | 0.10986 | 0.1236 | 0.13733 | 0.14648 | 0.050354 | 0.10071 | -0.045776 | 0.082397 | 0.13733 | 0.013733 | -0.041199 | -0.045776 | 0.068665 | 0.022888 | 97.5174 | 97.3709 | -23.2178 | 97.5403 | 97.5632 | 0.19226 | -23.1583 | 97.4854 | 97.4396 | -23.3093 | 97.4991 | 97.4304 | -0.009155 | -23.3139 | 97.467 | 97.5266 | 97.554 | -23.3139 | 97.3755 | 97.3709 | 97.554 | -23.2452
3557.5469 | 120.5429 | -115.3839 | 4.9072 | 0.013046 | -0.0012092 | 0.068517 | 0.023947 | -0.068255 | -0.020108 | 0.00078825 | 0.0073242 | 0.038792 | 0.007996 | -0.043327 | -0.002273 | 0.011173 | 0.045776 | 0.013733 | 0.041199 | 0.091553 | 0.082397 | 0.059509 | -0.073242 | -0.018311 | 0.009155 | -0.11902 | 0.004578 | 0.032043 | 0.059509 | -0.013733 | 115.4434 | 115.3107 | -4.8248 | 115.3976 | 115.4755 | 0.16479 | -4.8615 | 115.4434 | 115.3702 | -4.9026 | 115.3656 | 115.2649 | -0.10529 | -4.8752 | 115.4663 | 115.4297 | 115.4251 | -4.9805 | 115.3885 | 115.416 | 115.3931 | -4.921
3559.3438 | 120.9229 | -115.3976 | 5.2551 | 0.013046 | -0.0022772 | 0.070654 | 0.026083 | -0.067614 | -0.022885 | 0.00057465 | 0.030213 | 0.034306 | 0.0077822 | -0.042259 | -0.0078272 | 0.012882 | 0.059509 | 0.027466 | 0.050354 | 0.10529 | 0.09613 | 0.059509 | -0.07782 | 0.022888 | 0.082397 | -0.068665 | -0.004578 | 0.018311 | 0.045776 | -0.013733 | 115.4572 | 115.3198 | -5.159 | 115.4251 | 115.5029 | 0.18311 | -5.1956 | 115.4434 | 115.3839 | -5.2597 | 115.4205 | 115.329 | -0.054932 | -5.2368 | 115.4938 | 115.4572 | 115.448 | -5.3329 | 115.3931 | 115.416 | 115.48 | -5.2689
3561.125 | 121.0098 | -114.2807 | 6.2942 | 0.013046 | 0.0045588 | 0.073858 | 0.028006 | -0.06975 | -0.030576 | 0.0029244 | -0.0003053 | 0.028538 | 0.006287 | -0.043113 | -0.0091088 | 0.014591 | 0.091553 | 0.16937 | 0.16937 | 0.16479 | 0.045776 | 0.07782 | -0.022888 | 0.064087 | 0.1831 | 0.036621 | -0.009155 | 0 | 0.10529 | 0.032043 | 114.3585 | 114.2578 | -6.2485 | 114.4501 | 114.4455 | 0.18768 | -6.2027 | 114.386 | 114.3127 | -6.3034 | 114.3448 | 114.3173 | 0.004578 | -6.2942 | 114.3265 | 114.3723 | 114.4501 | -6.3171 | 114.2715 | 114.2807 | 114.4638 | -6.2622
3562.9062 | 120.9366 | -116.2903 | 4.5044 | 0.013046 | 7.2586e-05 | 0.071722 | 0.029288 | -0.066119 | -0.027799 | 0.0016428 | -0.0079343 | 0.031315 | 0.0058596 | -0.043541 | -0.0065454 | 0.013309 | 0.086975 | 0.10529 | 0.13733 | 0.14191 | 0.064087 | 0.082397 | -0.032043 | 0.027466 | 0.11444 | -0.022888 | -0.004578 | 0.013733 | 0.086975 | -0.004578 | 116.3727 | 116.2582 | -4.4403 | 116.3956 | 116.4322 | 0.17395 | -4.4174 | 116.3773 | 116.2857 | -4.509 | 116.3177 | 116.2674 | -0.01831 | -4.4907 | 116.3544 | 116.3773 | 116.4276 | -4.5364 | 116.2857 | 116.304 | 116.4047 | -4.509
3564.6406 | 121.019 | -118.4967 | 2.3666 | 0.013046 | -0.00099541 | 0.067449 | 0.022665 | -0.067187 | -0.019254 | 0.0018564 | 0.014954 | 0.035588 | 0.0071414 | -0.042472 | -0.0029138 | 0.0116 | 0.041199 | 0 | 0.022888 | 0.086975 | 0.10071 | 0.059509 | -0.07782 | -0.018311 | 0.004578 | -0.1236 | 0.013733 | 0.045776 | 0.059509 | -0.018311 | 118.5562 | 118.4189 | -2.2659 | 118.4967 | 118.5837 | 0.16479 | -2.3254 | 118.5562 | 118.4784 | -2.3529 | 118.4784 | 118.3731 | -0.10528 | -2.3209 | 118.5974 | 118.5379 | 118.5196 | -2.4445 | 118.5104 | 118.5425 | 118.5013 | -2.3849
3566.4531 | 121.1105 | -117.3889 | 3.3188 | 0.013046 | 0.004345 | 0.072576 | 0.026511 | -0.070177 | -0.027585 | 0.00078825 | 0.0073242 | 0.030674 | 0.004578 | -0.042259 | -0.0086816 | 0.0116 | 0.091553 | 0.11902 | 0.14648 | 0.14191 | 0.045776 | 0.091553 | -0.027466 | 0.064087 | 0.1236 | 0.013733 | -0.036621 | 0.004578 | 0.086975 | 0.013733 | 117.4805 | 117.3614 | -3.273 | 117.5079 | 117.5308 | 0.16937 | -3.2272 | 117.4759 | 117.4026 | -3.3554 | 117.453 | 117.4026 | 0 | -3.3142 | 117.4347 | 117.4805 | 117.5354 | -3.3463 | 117.3523 | 117.3935 | 117.5125 | -3.3051
3568.25 | 121.1288 | -114.7751 | 6.0379 | 0.020676 | 0.003277 | 0.069585 | 0.025015 | -0.068041 | -0.027585 | 0.0022836 | 0.014954 | 0.03217 | 0.0069278 | -0.0429 | -0.006759 | 0.013736 | 0.10529 | 0.09613 | 0.14191 | 0.13733 | 0.050354 | 0.091553 | -0.036621 | 0.064087 | 0.12817 | 0 | -0.032043 | -0.009155 | 0.073242 | 0.022888 | 114.8666 | 114.7385 | -5.9875 | 114.8712 | 114.9124 | 0.17395 | -5.9326 | 114.8483 | 114.798 | -6.0699 | 114.8392 | 114.7751 | -0.022888 | -6.0471 | 114.8254 | 114.8804 | 114.917 | -6.0745 | 114.743 | 114.7659 | 114.9033 | -6.015
3570.0469 | 120.9961 | -114.4226 | 6.3538 | 0.0054168 | -0.0020636 | 0.069158 | 0.027365 | -0.065264 | -0.022244 | -6.615e-05 | 0.014954 | 0.034519 | 0.0092776 | -0.042686 | -0.00505 | 0.010745 | 0.032043 | 0.009155 | 0.032043 | 0.073242 | 0.086975 | 0.027466 | -0.07782 | -0.009155 | 0.059509 | -0.086975 | 0.022888 | 0.022888 | 0.064087 | -0.009155 | 114.4501 | 114.3448 | -6.2668 | 114.4318 | 114.4958 | 0.15106 | -6.3217 | 114.4867 | 114.4135 | -6.3309 | 114.4135 | 114.3356 | -0.07782 | -6.3309 | 114.5096 | 114.4547 | 114.4547 | -6.4316 | 114.4455 | 114.4455 | 114.4821 | -6.3629
3571.8281 | 121.0052 | -116.5878 | 4.3121 | 0.020676 | -0.0012092 | 0.07044 | 0.029074 | -0.0674 | -0.025876 | 0.0012154 | 0.0073242 | 0.031956 | 0.010559 | -0.043327 | -0.0088952 | 0.013095 | 0.027466 | 0.022888 | 0.054932 | 0.086975 | 0.07782 | 0.036621 | -0.082397 | -0.050354 | 0.041199 | -0.091553 | 0.022888 | 0.045776 | 0.054932 | -0.013733 | 116.6245 | 116.5054 | -4.2343 | 116.6107 | 116.6748 | 0.16937 | -4.2847 | 116.6428 | 116.5741 | -4.2892 | 116.5375 | 116.4963 | -0.07782 | -4.2664 | 116.6656 | 116.6153 | 116.6428 | -4.3945 | 116.6107 | 116.6336 | 116.629 | -4.3259
3573.625 | 121.0281 | -117.6682 | 3.2593 | 0.0054168 | -0.0016364 | 0.066808 | 0.025015 | -0.068682 | -0.019681 | 0.0022836 | 0.014954 | 0.035374 | 0.007355 | -0.041404 | -0.0044092 | 0.012241 | 0.018311 | 0.004578 | 0.013733 | 0.073242 | 0.10986 | 0.050354 | -0.082397 | -0.009155 | 0.013733 | -0.13275 | 0.022888 | 0.032043 | 0.07782 | -0.013733 | 117.7185 | 117.5858 | -3.1494 | 117.6727 | 117.7414 | 0.15564 | -3.241 | 117.746 | 117.6544 | -3.2364 | 117.659 | 117.5354 | -0.11902 | -3.2272 | 117.778 | 117.6865 | 117.6819 | -3.3417 | 117.691 | 117.7002 | 117.6819 | -3.273
3575.375 | 121.0602 | -116.6519 | 4.2892 | 0.020676 | -0.0016364 | 0.069372 | 0.031638 | -0.068255 | -0.022885 | 0.0012154 | 0.0073242 | 0.031956 | 0.010132 | -0.044609 | -0.0078272 | 0.01395 | 0 | 0.004578 | 0.013733 | 0.073242 | 0.11444 | 0.036621 | -0.10529 | -0.027466 | 0.027466 | -0.10986 | 0.032043 | 0.032043 | 0.068665 | -0.032043 | 116.6885 | 116.5466 | -4.1748 | 116.6565 | 116.7252 | 0.17853 | -4.2892 | 116.7206 | 116.6199 | -4.2572 | 116.6245 | 116.5421 | -0.07782 | -4.2572 | 116.7664 | 116.6519 | 116.6656 | -4.3945 | 116.684 | 116.684 | 116.6794 | -4.3213
3577.1719 | 121.1334 | -117.7231 | 3.1357 | -0.0022127 | 0.0056268 | 0.070654 | 0.02587 | -0.068896 | -0.030149 | -0.00049335 | 0.0073242 | 0.031529 | 0.0065006 | -0.042472 | -0.008468 | 0.014804 | 0.027466 | 0.059509 | 0.09613 | 0.10986 | 0.064087 | 0.091553 | -0.064087 | 0.009155 | 0.091553 | -0.018311 | -0.009155 | -0.004578 | 0.091553 | 0.022888 | 117.8146 | 117.659 | -3.0716 | 117.7826 | 117.8329 | 0.17395 | -3.1082 | 117.8146 | 117.746 | -3.1448 | 117.7322 | 117.7048 | -0.041199 | -3.1403 | 117.7872 | 117.7505 | 117.8192 | -3.1998 | 117.7139 | 117.7185 | 117.8146 | -3.1128
3578.9062 | 121.1014 | -115.416 | 5.4474 | 0.013046 | 0.0086176 | 0.07514 | 0.027792 | -0.068255 | -0.02844 | 0.00014745 | 0.0073242 | 0.029179 | 0.005646 | -0.04589 | -0.0078272 | 0.012668 | 0.045776 | 0.059509 | 0.10071 | 0.11902 | 0.059509 | 0.082397 | -0.050354 | -0.009155 | 0.073242 | -0.022888 | -0.027466 | 0.013733 | 0.10529 | 0.018311 | 115.4984 | 115.3656 | -5.3879 | 115.4755 | 115.535 | 0.16937 | -5.4016 | 115.5212 | 115.4343 | -5.4749 | 115.4068 | 115.3931 | -0.041199 | -5.4337 | 115.4755 | 115.4617 | 115.5167 | -5.4977 | 115.3885 | 115.4297 | 115.4892 | -5.4291
3580.7031 | 121.1243 | -117.9108 | 2.9617 | 0.013046 | 0.0034906 | 0.069372 | 0.026297 | -0.06505 | -0.02609 | -0.001348 | -0.0003053 | 0.032383 | 0.0060732 | -0.045463 | -0.0061182 | 0.012882 | 0.1236 | 0.1236 | 0.16479 | 0.14191 | 0.054932 | 0.09613 | -0.022888 | 0.073242 | 0.11444 | 0.004578 | -0.018311 | -0.009155 | 0.086975 | 0.009155 | 118.0069 | 117.8879 | -2.9068 | 118.0344 | 118.0527 | 0.16479 | -2.8381 | 117.9977 | 117.9199 | -2.98 | 117.984 | 117.9153 | -0.004577 | -2.9709 | 117.9657 | 118.0344 | 118.0756 | -2.9846 | 117.8925 | 117.9016 | 118.0252 | -2.9526
3582.5156 | 121.2799 | -116.4368 | 4.4312 | 0.013046 | 0.0041314 | 0.071294 | 0.024161 | -0.06975 | -0.026731 | -0.00049335 | 0.014954 | 0.031315 | 0.0060732 | -0.04525 | -0.0059046 | 0.012241 | 0.1236 | 0.11444 | 0.15106 | 0.1236 | 0.050354 | 0.07782 | -0.032043 | 0.07782 | 0.11444 | 0.009155 | -0.027466 | -0.013733 | 0.10071 | 0.022888 | 116.5146 | 116.4047 | -4.3808 | 116.5512 | 116.5604 | 0.15564 | -4.3076 | 116.5375 | 116.4597 | -4.4586 | 116.5146 | 116.4459 | -0.013733 | -4.4449 | 116.4871 | 116.5604 | 116.5878 | -4.4632 | 116.4093 | 116.423 | 116.5512 | -4.4083
3584.2656 | 121.3486 | -120.1675 | 0.80109 | 0.013046 | 0.0037042 | 0.073217 | 0.029501 | -0.068896 | -0.026731 | -0.0011344 | 0.022583 | 0.032597 | 0.0065006 | -0.04525 | -0.0091088 | 0.011386 | 0.11444 | 0.13733 | 0.15564 | 0.15564 | 0.059509 | 0.086975 | -0.041199 | 0.082397 | 0.17395 | 0.059509 | -0.041199 | -0.009155 | 0.09613 | 0.027466 | 120.2545 | 120.1263 | -0.74158 | 120.3049 | 120.3232 | 0.19684 | -0.68664 | 120.2637 | 120.195 | -0.84228 | 120.2499 | 120.2271 | 0.032043 | -0.81024 | 120.2271 | 120.282 | 120.3232 | -0.84228 | 120.1263 | 120.1584 | 120.3415 | -0.77362
3586.0625 | 121.1838 | -120.1355 | 0.96588 | 0.0054168 | 0.0013544 | 0.070226 | 0.029288 | -0.068041 | -0.025022 | -0.0026298 | 0.0073242 | 0.033451 | 0.0088504 | -0.045036 | -0.0044092 | 0.011386 | 0.09613 | 0.1236 | 0.16022 | 0.15106 | 0.059509 | 0.09613 | -0.050354 | 0.064087 | 0.15106 | -0.004578 | -0.018311 | 0.004578 | 0.09613 | 0.009155 | 120.2316 | 120.0851 | -0.90637 | 120.2591 | 120.2866 | 0.20142 | -0.86975 | 120.2316 | 120.1447 | -0.98419 | 120.1996 | 120.1309 | -0.013733 | -0.9613 | 120.195 | 120.2316 | 120.2957 | -1.0162 | 120.1172 | 120.1401 | 120.2866 | -0.95673
3587.7812 | 121.3257 | -120.3094 | 0.7782 | 0.0054168 | 0.0028498 | 0.071722 | 0.028433 | -0.068468 | -0.02609 | -0.0034842 | 0.014954 | 0.030674 | 0.0047916 | -0.042686 | -0.0082544 | 0.012454 | 0.1236 | 0.14191 | 0.16022 | 0.15106 | 0.054932 | 0.082397 | -0.064087 | 0.091553 | 0.18768 | 0.041199 | -0.032043 | -0.009155 | 0.10529 | 0.027466 | 120.3918 | 120.2454 | -0.72327 | 120.4514 | 120.4605 | 0.21515 | -0.6546 | 120.4147 | 120.3369 | -0.81024 | 120.401 | 120.3506 | 0.013733 | -0.78735 | 120.3644 | 120.433 | 120.4697 | -0.84228 | 120.2774 | 120.3003 | 120.4971 | -0.75073
3589.5938 | 121.2433 | -119.4489 | 1.6663 | 0.013046 | -0.0014228 | 0.071508 | 0.026511 | -0.067187 | -0.022672 | 0.00014745 | -0.0003053 | 0.036228 | 0.010132 | -0.042686 | -0.003341 | 0.010745 | 0.013733 | -0.013733 | 0.013733 | 0.073242 | 0.10071 | 0.027466 | -0.09613 | -0.004578 | 0.013733 | -0.11902 | 0.022888 | 0.027466 | 0.045776 | -0.022888 | 119.4763 | 119.3527 | -1.5656 | 119.4351 | 119.5221 | 0.16937 | -1.6525 | 119.4946 | 119.426 | -1.6434 | 119.4443 | 119.3298 | -0.096131 | -1.6388 | 119.5496 | 119.4626 | 119.4626 | -1.7624 | 119.4717 | 119.4763 | 119.4626 | -1.6891
3591.3438 | 121.3486 | -120.5887 | 0.52185 | 0.013046 | 0.006054 | 0.071722 | 0.027579 | -0.067828 | -0.028653 | 0.00207 | 0.022583 | 0.02982 | 0.0092776 | -0.0429 | -0.0088952 | 0.0116 | 0.059509 | 0.07782 | 0.10529 | 0.1236 | 0.07782 | 0.086975 | -0.064087 | 0.050354 | 0.12817 | 0.004578 | -0.032043 | 0.018311 | 0.091553 | 0.022888 | 120.6757 | 120.5246 | -0.44403 | 120.6665 | 120.7123 | 0.18768 | -0.46234 | 120.6802 | 120.6116 | -0.55389 | 120.639 | 120.5933 | -0.01831 | -0.50354 | 120.6665 | 120.6482 | 120.694 | -0.58594 | 120.5566 | 120.607 | 120.7169 | -0.49896
3593.1406 | 121.2982 | -120.2179 | 0.86975 | 0.0054168 | 0.0054132 | 0.070867 | 0.026511 | -0.068041 | -0.023953 | 0.00036105 | 0.014954 | 0.03217 | 0.006287 | -0.043113 | -0.0052636 | 0.010959 | 0.1236 | 0.13275 | 0.15564 | 0.15106 | 0.050354 | 0.086975 | -0.022888 | 0.091553 | 0.14648 | 0.013733 | -0.050354 | -0.027466 | 0.091553 | 0.022888 | 120.3049 | 120.195 | -0.8194 | 120.3506 | 120.369 | 0.17395 | -0.74616 | 120.3094 | 120.2408 | -0.92011 | 120.3094 | 120.2316 | -0.009155 | -0.89722 | 120.2682 | 120.3415 | 120.3735 | -0.89264 | 120.1675 | 120.1904 | 120.3644 | -0.84686
3594.9531 | 121.2524 | -120.7489 | 0.40283 | 0.0054168 | -0.0012092 | 0.069158 | 0.028647 | -0.069109 | -0.020535 | 0.0014292 | 0.014954 | 0.034947 | 0.0071414 | -0.041832 | -0.005691 | 0.011386 | 0.032043 | 0.004578 | 0.027466 | 0.086975 | 0.10071 | 0.050354 | -0.064087 | -0.004578 | 0.036621 | -0.10071 | 0.022888 | 0.050354 | 0.073242 | -0.009155 | 120.7993 | 120.6848 | -0.30212 | 120.7535 | 120.8359 | 0.15106 | -0.37079 | 120.8221 | 120.7397 | -0.37994 | 120.7443 | 120.6482 | -0.091553 | -0.35248 | 120.8496 | 120.7809 | 120.7764 | -0.46692 | 120.7718 | 120.7993 | 120.7855 | -0.41199
3596.7344 | 121.3394 | -120.7443 | 0.4303 | -0.0022127 | 0.004986 | 0.07279 | 0.028006 | -0.067614 | -0.027799 | -0.00027975 | -0.0003053 | 0.029179 | 0.0060732 | -0.044181 | -0.0063318 | 0.013095 | 0.07782 | 0.082397 | 0.11902 | 0.10986 | 0.054932 | 0.082397 | -0.027466 | 0.036621 | 0.086975 | -0.027466 | -0.009155 | 0.009155 | 0.09613 | 0.022888 | 120.8267 | 120.7169 | -0.37537 | 120.8267 | 120.8542 | 0.13733 | -0.35248 | 120.8405 | 120.7672 | -0.43945 | 120.7809 | 120.7169 | -0.050354 | -0.42114 | 120.7993 | 120.8221 | 120.8633 | -0.45776 | 120.7352 | 120.7535 | 120.8313 | -0.40741
3598.4688 | 121.3806 | -120.6848 | 0.47607 | -0.0022127 | 0.0073358 | 0.069799 | 0.02886 | -0.067187 | -0.026303 | -0.0015616 | 0.0073242 | 0.02982 | 0.0054324 | -0.044181 | -0.005691 | 0.01395 | 0.041199 | 0.059509 | 0.091553 | 0.13275 | 0.054932 | 0.07782 | -0.050354 | 0.018311 | 0.091553 | -0.027466 | -0.018311 | 0 | 0.082397 | 0 | 120.7626 | 120.6345 | -0.42114 | 120.7443 | 120.8176 | 0.18311 | -0.43488 | 120.7672 | 120.6848 | -0.49439 | 120.7031 | 120.6573 | -0.027466 | -0.47607 | 120.7397 | 120.726 | 120.7764 | -0.52643 | 120.6665 | 120.6848 | 120.7764 | -0.47607
3600.2656 | 121.2982 | -118.0847 | 3.1082 | 0.013046 | 0.0056268 | 0.071508 | 0.028006 | -0.070177 | -0.025022 | -0.00049335 | 0.014954 | 0.033879 | 0.0060732 | -0.044395 | -0.0059046 | 0.012882 | 0.064087 | 0.091553 | 0.11902 | 0.09613 | 0.054932 | 0.091553 | -0.054932 | 0.036621 | 0.07782 | -0.022888 | -0.018311 | -0.004578 | 0.09613 | 0.022888 | 118.1763 | 118.0298 | -3.0533 | 118.1763 | 118.1808 | 0.15106 | -3.0441 | 118.1808 | 118.1076 | -3.1265 | 118.1213 | 118.0618 | -0.045776 | -3.1128 | 118.1396 | 118.1488 | 118.2037 | -3.1631 | 118.0664 | 118.0801 | 118.1625 | -3.0853
3602.0625 | 121.3852 | -120.7809 | 0.37994 | 0.0054168 | 0.0028498 | 0.071935 | 0.029929 | -0.068896 | -0.025235 | 0.00014745 | -0.0003053 | 0.03281 | 0.009064 | -0.043754 | -0.0078272 | 0.010745 | 0.13275 | 0.17395 | 0.17853 | 0.16479 | 0.068665 | 0.082397 | -0.036621 | 0.091553 | 0.16937 | 0.045776 | -0.013733 | -0.018311 | 0.091553 | 0.022888 | 120.8633 | 120.7443 | -0.31128 | 120.9549 | 120.9457 | 0.20142 | -0.24719 | 120.8725 | 120.8038 | -0.39368 | 120.8725 | 120.8267 | 0.022888 | -0.39826 | 120.8496 | 120.9137 | 120.9595 | -0.41657 | 120.7672 | 120.7626 | 120.9503 | -0.35706
3603.7812 | 121.3943 | -120.7352 | 0.39368 | 0.0054168 | 0.0041314 | 0.07279 | 0.027152 | -0.068468 | -0.022672 | 0.00057465 | -0.0003053 | 0.031956 | 0.0041506 | -0.044395 | -0.0020594 | 0.0086091 | 0.1236 | 0.13275 | 0.14191 | 0.16022 | 0.068665 | 0.09613 | -0.032043 | 0.10529 | 0.1236 | 0.004578 | -0.027466 | -0.018311 | 0.10529 | 0.022888 | 120.8313 | 120.7031 | -0.32501 | 120.8679 | 120.8954 | 0.19226 | -0.27008 | 120.8405 | 120.7581 | -0.42114 | 120.8405 | 120.7397 | -0.01831 | -0.41199 | 120.8038 | 120.8588 | 120.8771 | -0.42572 | 120.7077 | 120.7169 | 120.8588 | -0.37079
3605.5781 | 119.87 | -116.629 | 2.8839 | 0.0054168 | 0.0019952 | 0.071294 | 0.027152 | -0.066546 | -0.025235 | 0.00014745 | 0.014954 | 0.031315 | 0.005646 | -0.046531 | -0.00505 | 0.013522 | 0.11444 | 0.13275 | 0.16479 | 0.14191 | 0.045776 | 0.086975 | -0.027466 | 0.07782 | 0.12817 | 0.009155 | -0.009155 | -0.009155 | 0.086975 | 0.036621 | 116.716 | 116.6016 | -2.8381 | 116.7618 | 116.7709 | 0.16937 | -2.7695 | 116.716 | 116.6656 | -2.8931 | 116.7068 | 116.6382 | -0.027466 | -2.8931 | 116.6748 | 116.7435 | 116.7938 | -2.9114 | 116.6199 | 116.6199 | 116.7572 | -2.8473
3607.3906 | 120.8496 | -119.3527 | 1.2222 | 0.0054168 | -0.0024908 | 0.07044 | 0.025656 | -0.068896 | -0.019467 | 0.00207 | 0.022583 | 0.035801 | 0.0054324 | -0.043327 | -0.0018458 | 0.011813 | 0.086975 | 0.064087 | 0.059509 | 0.09613 | 0.082397 | 0.059509 | -0.059509 | 0.041199 | 0.086975 | -0.07782 | 0.013733 | 0.027466 | 0.073242 | 0.004578 | 119.4122 | 119.2932 | -1.1398 | 119.4168 | 119.4489 | 0.15564 | -1.1353 | 119.426 | 119.3573 | -1.2085 | 119.3939 | 119.2749 | -0.082398 | -1.1948 | 119.4351 | 119.4397 | 119.4122 | -1.2817 | 119.3665 | 119.3802 | 119.4397 | -1.2177
3609.1719 | 121.0327 | -119.7144 | 0.96588 | 0.0054168 | 0.0019952 | 0.073858 | 0.029501 | -0.069323 | -0.026944 | 0.003138 | -0.0003053 | 0.029606 | 0.0075686 | -0.045036 | -0.008468 | 0.013736 | 0.11444 | 0.18768 | 0.1831 | 0.16479 | 0.045776 | 0.091553 | -0.045776 | 0.073242 | 0.1831 | 0.045776 | -0.018311 | -0.004578 | 0.07782 | 0.032043 | 119.8059 | 119.6686 | -0.9201 | 119.902 | 119.8791 | 0.21057 | -0.85144 | 119.7922 | 119.7464 | -0.98419 | 119.7876 | 119.7601 | 0.013733 | -0.97046 | 119.7601 | 119.8288 | 119.8975 | -1.0117 | 119.696 | 119.7098 | 119.8975 | -0.93384
3610.9688 | 120.9686 | -120.195 | 0.6546 | 0.013046 | 0.00028619 | 0.06809 | 0.02352 | -0.068468 | -0.019681 | 0.0035654 | 0.0073242 | 0.034306 | 0.0067142 | -0.043541 | -0.0037684 | 0.013095 | -0.004578 | -0.036621 | 0.004578 | 0.064087 | 0.11444 | 0.050354 | -0.09613 | -0.027466 | -0.022888 | -0.14191 | 0.032043 | 0.041199 | 0.068665 | -0.013733 | 120.2454 | 120.0989 | -0.54016 | 120.1584 | 120.2591 | 0.16022 | -0.65918 | 120.2637 | 120.1813 | -0.62256 | 120.1675 | 120.0531 | -0.12817 | -0.6134 | 120.3094 | 120.1904 | 120.1996 | -0.75073 | 120.2271 | 120.2362 | 120.1721 | -0.66834
3612.75 | 121.019 | -120.314 | 0.5722 | 0.013046 | -0.00078181 | 0.064672 | 0.030356 | -0.066546 | -0.020963 | 0.0012154 | 0.0073242 | 0.035374 | 0.011841 | -0.040336 | -0.0063318 | 0.011173 | 0.004578 | -0.050354 | -0.004578 | 0.054932 | 0.10071 | 0.050354 | -0.064087 | -0.032043 | -0.009155 | -0.13275 | 0.027466 | 0.032043 | 0.068665 | -0.022888 | 120.3644 | 120.2499 | -0.4715 | 120.2637 | 120.369 | 0.11902 | -0.56763 | 120.3827 | 120.2911 | -0.54474 | 120.282 | 120.1813 | -0.10986 | -0.54016 | 120.4147 | 120.3186 | 120.3094 | -0.63629 | 120.3415 | 120.3461 | 120.3049 | -0.59509
3614.5469 | 121.0556 | -120.488 | 0.46234 | 0.013046 | 0.0013544 | 0.068731 | 0.025656 | -0.06975 | -0.019254 | 0.0018564 | 0.014954 | 0.034519 | 0.0092776 | -0.041832 | -0.0037684 | 0.013309 | -0.009155 | -0.041199 | 0 | 0.07782 | 0.09613 | 0.050354 | -0.082397 | -0.032043 | -0.009155 | -0.13275 | 0.013733 | 0.045776 | 0.054932 | 0 | 120.5383 | 120.4056 | -0.36621 | 120.4468 | 120.5658 | 0.16022 | -0.4715 | 120.5429 | 120.488 | -0.44861 | 120.4559 | 120.3552 | -0.13275 | -0.41657 | 120.5841 | 120.4788 | 120.488 | -0.54474 | 120.5017 | 120.5338 | 120.4788 | -0.46234
3616.2812 | 121.1609 | -120.4147 | 0.49439 | -0.0022127 | 0.0058404 | 0.06809 | 0.02587 | -0.066546 | -0.026303 | 0.0016428 | 0.014954 | 0.033238 | 0.0071414 | -0.0429 | -0.0074 | 0.013095 | 0.086975 | 0.10071 | 0.11444 | 0.12817 | 0.068665 | 0.064087 | -0.050354 | 0.07782 | 0.14191 | 0.004578 | -0.041199 | -0.004578 | 0.10986 | 0.032043 | 120.4788 | 120.3644 | -0.42572 | 120.5154 | 120.5429 | 0.17853 | -0.40741 | 120.5246 | 120.4468 | -0.53558 | 120.4926 | 120.4193 | -0.027465 | -0.49896 | 120.4834 | 120.5017 | 120.5292 | -0.54474 | 120.3735 | 120.4102 | 120.5566 | -0.46234
3618.0781 | 121.1792 | -120.4926 | 0.43945 | 0.013046 | 0.0030634 | 0.071508 | 0.02587 | -0.067614 | -0.024381 | 0.00207 | 0.014954 | 0.034092 | 0.007996 | -0.0429 | -0.0046228 | 0.013736 | 0.091553 | 0.09613 | 0.14648 | 0.16479 | 0.054932 | 0.082397 | -0.036621 | 0.086975 | 0.14191 | 0.022888 | -0.032043 | 0.004578 | 0.10071 | 0.022888 | 120.575 | 120.4559 | -0.38452 | 120.5887 | 120.6573 | 0.20142 | -0.3479 | 120.5933 | 120.5154 | -0.4715 | 120.5795 | 120.5154 | 0 | -0.43487 | 120.5475 | 120.5841 | 120.639 | -0.47607 | 120.4605 | 120.4971 | 120.6345 | -0.41656
3619.875 | 121.1609 | -120.5246 | 0.43945 | -0.0022127 | 0.003277 | 0.072576 | 0.025229 | -0.071032 | -0.027799 | -0.00049335 | -0.0003053 | 0.030461 | 0.0050052 | -0.043327 | -0.0088952 | 0.013095 | 0.068665 | 0.10071 | 0.13275 | 0.1236 | 0.050354 | 0.07782 | -0.054932 | 0.022888 | 0.10529 | 0 | -0.022888 | 0.004578 | 0.09613 | 0.022888 | 120.6024 | 120.4697 | -0.3891 | 120.6253 | 120.6482 | 0.17853 | -0.37079 | 120.6207 | 120.5475 | -0.46234 | 120.5475 | 120.5246 | -0.022888 | -0.43487 | 120.575 | 120.5933 | 120.6573 | -0.49438 | 120.5017 | 120.5292 | 120.6299 | -0.41656
3621.6562 | 121.2021 | -120.5246 | 0.45319 | 0.020676 | 0.0047724 | 0.070013 | 0.026511 | -0.070391 | -0.023313 | -0.00049335 | 0.014954 | 0.03281 | 0.0075686 | -0.042045 | -0.00505 | 0.013736 | 0.10071 | 0.1236 | 0.13733 | 0.16022 | 0.050354 | 0.09613 | -0.027466 | 0.10071 | 0.14191 | 0.004578 | -0.013733 | -0.032043 | 0.10071 | 0.032043 | 120.6207 | 120.4971 | -0.40283 | 120.6482 | 120.6848 | 0.18768 | -0.35248 | 120.6253 | 120.5566 | -0.46692 | 120.6253 | 120.5292 | -0.027465 | -0.48523 | 120.575 | 120.6253 | 120.6619 | -0.48065 | 120.5109 | 120.4926 | 120.6665 | -0.42114
3623.4531 | 121.1746 | -120.7397 | 0.29297 | 0.013046 | 0.0026362 | 0.07044 | 0.029074 | -0.066332 | -0.027158 | -0.00049335 | 0.014954 | 0.030674 | 0.0077822 | -0.043754 | -0.006759 | 0.015872 | 0.068665 | 0.10529 | 0.13275 | 0.11902 | 0.059509 | 0.091553 | -0.041199 | 0.018311 | 0.091553 | -0.018311 | -0.013733 | 0.004578 | 0.091553 | 0.022888 | 120.8313 | 120.6985 | -0.23346 | 120.845 | 120.8588 | 0.16022 | -0.2243 | 120.8313 | 120.7626 | -0.3067 | 120.7581 | 120.7214 | -0.041199 | -0.28839 | 120.7993 | 120.8084 | 120.8725 | -0.33417 | 120.726 | 120.7443 | 120.8313 | -0.27008
3625.1875 | 121.1792 | -120.7535 | 0.3067 | 0.013046 | 0.00049979 | 0.070013 | 0.024374 | -0.068896 | -0.021817 | -0.00092075 | 0.0073242 | 0.036015 | 0.0082096 | -0.044395 | -0.0024866 | 0.012241 | 0.013733 | -0.027466 | -0.013733 | 0.068665 | 0.091553 | 0.041199 | -0.068665 | -0.027466 | -0.022888 | -0.1236 | 0.009155 | 0.036621 | 0.068665 | -0.027466 | 120.7947 | 120.6848 | -0.21515 | 120.726 | 120.8221 | 0.13733 | -0.29297 | 120.8221 | 120.726 | -0.29755 | 120.726 | 120.6299 | -0.09613 | -0.27008 | 120.845 | 120.7672 | 120.7397 | -0.37537 | 120.7626 | 120.7901 | 120.7306 | -0.33417
3626.9688 | 121.1792 | -120.6253 | 0.44403 | 0.0054168 | 0.0011408 | 0.070867 | 0.025443 | -0.068896 | -0.020322 | 0.00207 | -0.0003053 | 0.035801 | 0.0082096 | -0.043113 | -0.0048364 | 0.012882 | -0.009155 | -0.022888 | -0.004578 | 0.068665 | 0.09613 | 0.054932 | -0.068665 | -0.004578 | -0.022888 | -0.14191 | 0.009155 | 0.041199 | 0.059509 | -0.013733 | 120.6802 | 120.5566 | -0.3479 | 120.6024 | 120.694 | 0.13733 | -0.45319 | 120.6848 | 120.6116 | -0.43488 | 120.6207 | 120.4834 | -0.12817 | -0.40283 | 120.7214 | 120.6161 | 120.6207 | -0.5127 | 120.6345 | 120.6665 | 120.6024 | -0.45776
3628.75 | 121.2982 | -120.7077 | 0.34332 | 0.0054168 | 0.006054 | 0.070013 | 0.027792 | -0.06505 | -0.024381 | -0.0015616 | 0.0073242 | 0.030461 | 0.0060732 | -0.043327 | -0.005691 | 0.013736 | 0.09613 | 0.10529 | 0.14648 | 0.15564 | 0.059509 | 0.091553 | -0.027466 | 0.073242 | 0.12817 | 0.013733 | -0.032043 | -0.022888 | 0.10071 | 0.027466 | 120.7993 | 120.6802 | -0.28381 | 120.813 | 120.8633 | 0.18311 | -0.24719 | 120.8084 | 120.7352 | -0.37537 | 120.7809 | 120.7214 | -0.013733 | -0.36621 | 120.7672 | 120.8038 | 120.8542 | -0.37079 | 120.6757 | 120.6848 | 120.8359 | -0.31586
3630.4844 | 121.2662 | -120.7306 | 0.39368 | 0.020676 | 0.0022088 | 0.069372 | 0.026724 | -0.066332 | -0.019895 | 0.0018564 | 0.0073242 | 0.03281 | 0.0071414 | -0.041618 | -0.0063318 | 0.013522 | -0.004578 | -0.032043 | -0.004578 | 0.068665 | 0.091553 | 0.050354 | -0.064087 | -0.022888 | -0.018311 | -0.11902 | 0.009155 | 0.045776 | 0.059509 | -0.018311 | 120.7809 | 120.6665 | -0.30212 | 120.6985 | 120.7993 | 0.13275 | -0.39826 | 120.7901 | 120.7123 | -0.38452 | 120.7077 | 120.6116 | -0.10071 | -0.3479 | 120.8221 | 120.726 | 120.726 | -0.45776 | 120.7397 | 120.7764 | 120.7123 | -0.41199
3632.2812 | 121.2936 | -120.7947 | 0.29755 | -0.0022127 | 0.0024224 | 0.071081 | 0.027152 | -0.066973 | -0.023526 | 0.0027108 | -0.0003053 | 0.033238 | 0.007996 | -0.044395 | -0.0074 | 0.0116 | 0.036621 | 0.073242 | 0.11444 | 0.10986 | 0.064087 | 0.073242 | -0.050354 | 0.07782 | 0.10071 | -0.013733 | -0.032043 | -0.018311 | 0.10071 | 0.027466 | 120.8679 | 120.7443 | -0.23346 | 120.8679 | 120.9045 | 0.16022 | -0.26092 | 120.8954 | 120.8221 | -0.32959 | 120.8725 | 120.7809 | -0.041199 | -0.31586 | 120.8588 | 120.8313 | 120.9091 | -0.3479 | 120.7626 | 120.7764 | 120.8954 | -0.27008
3634.0781 | 121.3165 | -120.6757 | 0.40741 | 0.013046 | 0.001568 | 0.073644 | 0.03121 | -0.068682 | -0.030576 | -0.00070715 | 0.0073242 | 0.029606 | 0.0067142 | -0.046745 | -0.0074 | 0.012027 | 0.09613 | 0.17395 | 0.19226 | 0.15106 | 0.068665 | 0.07782 | -0.041199 | 0.064087 | 0.18768 | 0.045776 | -0.022888 | -0.013733 | 0.10529 | 0.027466 | 120.7535 | 120.6345 | -0.33874 | 120.8496 | 120.8267 | 0.19226 | -0.31128 | 120.7809 | 120.7031 | -0.4303 | 120.7397 | 120.7214 | 0.01831 | -0.42114 | 120.7443 | 120.7718 | 120.8679 | -0.44861 | 120.6528 | 120.6619 | 120.8633 | -0.37994
3635.7969 | 121.3806 | -120.8313 | 0.49896 | 0.0054168 | -0.00056821 | 0.071935 | 0.029501 | -0.068468 | -0.027371 | -0.00049335 | -0.0003053 | 0.034519 | 0.0082096 | -0.041832 | -0.008468 | 0.012241 | 0.013733 | 0 | 0.032043 | 0.054932 | 0.10529 | 0.050354 | -0.082397 | -0.041199 | 0.036621 | -0.10529 | 0.013733 | 0.041199 | 0.054932 | -0.027466 | 120.8817 | 120.7489 | -0.39368 | 120.8313 | 120.8862 | 0.13733 | -0.48523 | 120.8862 | 120.8038 | -0.48523 | 120.7901 | 120.726 | -0.07782 | -0.45776 | 120.9366 | 120.845 | 120.8633 | -0.58136 | 120.845 | 120.8725 | 120.8679 | -0.52643
3637.5938 | 121.2296 | -121.0007 | 0.17395 | -0.0022127 | -0.003559 | 0.070013 | 0.02587 | -0.071673 | -0.018186 | -6.615e-05 | -0.0003053 | 0.037724 | 0.0071414 | -0.042686 | -0.0041956 | 0.012027 | 0.086975 | 0.064087 | 0.082397 | 0.10986 | 0.073242 | 0.059509 | -0.064087 | 0.054932 | 0.073242 | -0.068665 | 0.013733 | 0.027466 | 0.068665 | 0 | 121.0602 | 120.9366 | -0.10071 | 121.0648 | 121.1105 | 0.17395 | -0.086975 | 121.0693 | 121.0007 | -0.16022 | 121.0556 | 120.932 | -0.068665 | -0.14648 | 121.0739 | 121.0876 | 121.0831 | -0.23804 | 121.0144 | 121.0281 | 121.0739 | -0.17395
3639.3281 | 121.3028 | -120.9641 | 0.13733 | -0.0022127 | 0.004986 | 0.073217 | 0.026724 | -0.068682 | -0.027158 | 0.0012154 | 0.022583 | 0.031101 | 0.0060732 | -0.043968 | -0.0059046 | 0.013522 | 0.10071 | 0.11444 | 0.16937 | 0.15106 | 0.045776 | 0.086975 | -0.032043 | 0.091553 | 0.13275 | 0.018311 | -0.032043 | -0.018311 | 0.10986 | 0.018311 | 121.051 | 120.932 | -0.091553 | 121.0785 | 121.1151 | 0.18311 | -0.036621 | 121.0739 | 120.9824 | -0.16937 | 121.0556 | 120.9824 | 0 | -0.15564 | 121.0098 | 121.0648 | 121.1334 | -0.16937 | 120.932 | 120.9457 | 121.0968 | -0.11902
3641.125 | 121.2799 | -120.7214 | 0.46692 | 0.013046 | 0.00028619 | 0.067449 | 0.024802 | -0.068255 | -0.019467 | 0.0010018 | 0.014954 | 0.03751 | 0.0071414 | -0.041191 | -0.00505 | 0.014804 | 0.041199 | 0.018311 | 0.045776 | 0.073242 | 0.10529 | 0.050354 | -0.068665 | -0.018311 | 0.013733 | -0.11902 | 0.009155 | 0.036621 | 0.064087 | -0.013733 | 120.7718 | 120.6528 | -0.36163 | 120.7397 | 120.7947 | 0.14191 | -0.42572 | 120.7855 | 120.7077 | -0.45776 | 120.7031 | 120.6024 | -0.10529 | -0.4303 | 120.8267 | 120.7626 | 120.7672 | -0.53558 | 120.7306 | 120.7581 | 120.7352 | -0.48065
3642.8438 | 120.5383 | -15.303 | 98.7579 | 0.0054168 | 0.00028619 | 0.068517 | 0.02587 | -0.068041 | -0.023953 | 0.0014292 | 0.014954 | 0.035374 | 0.0094912 | -0.039482 | -0.0052636 | 0.013095 | -0.018311 | -0.064087 | -0.032043 | 0.027466 | 0.054932 | 0.009155 | -0.1236 | -0.064087 | -0.064087 | -0.16479 | -0.018311 | 0.018311 | 0.027466 | -0.059509 | 15.3122 | 15.1794 | -98.703 | 15.239 | 15.3305 | 0.15106 | -98.7762 | 15.3305 | 15.2435 | -98.7762 | 15.239 | 15.1382 | -0.10529 | -98.7396 | 15.358 | 15.2847 | 15.271 | -98.8815 | 15.2847 | 15.3214 | 15.239 | -98.8174
3644.6406 | 121.1746 | -95.723 | 24.9023 | 0.0054168 | 0.0039178 | 0.07279 | 0.029074 | -0.069964 | -0.030149 | 0.0012154 | -0.0003053 | 0.031956 | 0.007996 | -0.044181 | -0.0097498 | 0.015445 | 0.050354 | 0.086975 | 0.11444 | 0.11902 | 0.054932 | 0.068665 | -0.050354 | 0.013733 | 0.10071 | -0.022888 | -0.045776 | 0 | 0.091553 | 0.013733 | 95.7916 | 95.6726 | -24.8474 | 95.8099 | 95.842 | 0.16937 | -24.852 | 95.8145 | 95.7367 | -24.9481 | 95.7367 | 95.7001 | -0.036621 | -24.9023 | 95.7779 | 95.7733 | 95.8374 | -24.9527 | 95.6772 | 95.723 | 95.8237 | -24.8886
3646.3906 | 121.2616 | -95.8008 | 24.9527 | 0.0054168 | 0.0045588 | 0.072149 | 0.030356 | -0.068255 | -0.028012 | -0.00049335 | 0.014954 | 0.031742 | 0.0069278 | -0.044395 | -0.0099634 | 0.011173 | 0.041199 | 0.082397 | 0.11902 | 0.11902 | 0.059509 | 0.068665 | -0.050354 | 0.004578 | 0.073242 | -0.036621 | -0.027466 | -0.013733 | 0.09613 | 0.004578 | 95.8694 | 95.7504 | -24.8932 | 95.8832 | 95.9198 | 0.16937 | -24.9115 | 95.8969 | 95.8054 | -24.9802 | 95.8054 | 95.7642 | -0.041199 | -24.9664 | 95.8603 | 95.842 | 95.9198 | -25.0031 | 95.7733 | 95.787 | 95.874 | -24.9481
3648.1875 | 121.2296 | -95.8786 | 25.0122 | 0.013046 | -0.0014228 | 0.068304 | 0.02886 | -0.069537 | -0.019895 | 0.00078825 | 0.014954 | 0.033665 | 0.0086368 | -0.043327 | -0.0044092 | 0.010318 | 0.004578 | -0.013733 | 0.022888 | 0.086975 | 0.086975 | 0.050354 | -0.082397 | 0.009155 | 0.050354 | -0.091553 | 0.027466 | 0.041199 | 0.041199 | -0.013733 | 95.929 | 95.7962 | -24.9252 | 95.8649 | 95.9656 | 0.16937 | -25.0076 | 95.9198 | 95.8649 | -24.9847 | 95.8878 | 95.787 | -0.07782 | -24.971 | 95.9656 | 95.8832 | 95.9015 | -25.0946 | 95.9061 | 95.9198 | 95.929 | -25.0259
3649.9062 | 121.1838 | -95.9747 | 25.0214 | 0.020676 | -0.0012092 | 0.06809 | 0.025443 | -0.067828 | -0.02139 | 0.0016428 | 0.014954 | 0.034306 | 0.0092776 | -0.042686 | -0.0046228 | 0.010104 | 0.064087 | 0.032043 | 0.064087 | 0.09613 | 0.09613 | 0.054932 | -0.082397 | 0.059509 | 0.054932 | -0.091553 | 0 | 0.036621 | 0.064087 | 0 | 96.0297 | 95.8923 | -24.9252 | 96.0068 | 96.0709 | 0.17853 | -24.9573 | 96.0388 | 95.9747 | -25.0214 | 96.0342 | 95.8832 | -0.091553 | -24.9847 | 96.0709 | 96.0388 | 96.0388 | -25.1038 | 95.9747 | 96.0114 | 96.0297 | -25.0214
3651.6875 | 121.17 | -95.929 | 25.1129 | 0.013046 | -0.00185 | 0.069372 | 0.026297 | -0.06975 | -0.021817 | 0.00078825 | -0.0003053 | 0.033451 | 0.0097048 | -0.043754 | -0.0029138 | 0.012882 | 0.018311 | 0.018311 | 0.027466 | 0.073242 | 0.086975 | 0.045776 | -0.073242 | -0.027466 | 0.004578 | -0.12817 | -0.018311 | 0.022888 | 0.036621 | -0.022888 | 95.9747 | 95.8557 | -25.0259 | 95.9473 | 96.0022 | 0.14648 | -25.0946 | 95.9656 | 95.9061 | -25.1312 | 95.9015 | 95.8008 | -0.10529 | -25.09 | 96.0159 | 95.9473 | 95.9564 | -25.1862 | 95.9106 | 95.9518 | 95.9335 | -25.1358
3653.4844 | 121.3028 | -96.4188 | 24.5728 | 0.0054168 | 0.0054132 | 0.073644 | 0.026511 | -0.0721 | -0.031857 | 0.00036105 | 0.014954 | 0.029179 | 0.0082096 | -0.045036 | -0.0093226 | 0.014163 | -0.004578 | 0.068665 | 0.09613 | 0.09613 | 0.064087 | 0.064087 | -0.054932 | -0.004578 | 0.073242 | -0.032043 | -0.027466 | -0.004578 | 0.07782 | 0 | 96.4828 | 96.3638 | -24.5087 | 96.4874 | 96.5149 | 0.15106 | -24.5773 | 96.4966 | 96.4188 | -24.6002 | 96.4142 | 96.3867 | -0.032043 | -24.5773 | 96.4828 | 96.4142 | 96.5149 | -24.6277 | 96.3913 | 96.4142 | 96.492 | -24.5728
3655.2656 | 121.2341 | -96.9818 | 24.1104 | 0.0054168 | 0.0022088 | 0.07749 | 0.028006 | -0.064623 | -0.026731 | -0.00027975 | 0.0073242 | 0.030247 | 0.0052188 | -0.043113 | -0.005691 | 0.011386 | 0.073242 | 0.10986 | 0.12817 | 0.14191 | 0.032043 | 0.064087 | -0.050354 | 0.018311 | 0.1236 | -0.032043 | -0.032043 | 0.009155 | 0.073242 | -0.009155 | 97.0459 | 96.9315 | -24.0784 | 97.0917 | 97.1237 | 0.19226 | -24.0372 | 97.0551 | 96.9727 | -24.1425 | 97.0001 | 96.9498 | -0.022888 | -24.1013 | 97.0139 | 97.0551 | 97.11 | -24.1608 | 96.9498 | 96.991 | 97.1054 | -24.1196
3657 | 121.3486 | -21.7575 | 99.1882 | 0.0054168 | 0.004986 | 0.069585 | 0.025443 | -0.068041 | -0.021604 | -6.615e-05 | 0.014954 | 0.034092 | 0.0065006 | -0.043541 | -0.0061182 | 0.013095 | 0.082397 | 0.064087 | 0.09613 | 0.1236 | 0.022888 | 0.054932 | -0.064087 | 0.054932 | 0.09613 | -0.022888 | -0.068665 | -0.045776 | 0.073242 | -0.009155 | 21.8124 | 21.6934 | -99.1653 | 21.8216 | 21.8811 | 0.18768 | -99.1058 | 21.8307 | 21.7484 | -99.2569 | 21.8124 | 21.7346 | -0.013733 | -99.234 | 21.7804 | 21.8399 | 21.8536 | -99.2523 | 21.6888 | 21.7117 | 21.8536 | -99.1974
3658.7812 | 121.2616 | -3.804 | 117.1326 | -0.0022127 | 0.0011408 | 0.077062 | 0.027152 | -0.067187 | -0.028226 | -0.0028434 | 0.0073242 | 0.031529 | 0.0047916 | -0.044395 | -0.0074 | 0.011173 | 0.082397 | 0.10071 | 0.12817 | 0.10071 | 0.013733 | 0.036621 | -0.07782 | 0.013733 | 0.14191 | 0.004578 | -0.050354 | -0.050354 | 0.059509 | -0.018311 | 3.8406 | 3.7262 | -117.1188 | 3.9047 | 3.9047 | 0.17853 | -117.0502 | 3.8635 | 3.7857 | -117.1829 | 3.8177 | 3.8086 | 0.022889 | -117.1829 | 3.8177 | 3.8864 | 3.9322 | -117.2104 | 3.7537 | 3.7537 | 3.9459 | -117.1509
3660.5781 | 121.2845 | -4.7562 | 116.0843 | 0.013046 | -0.0020636 | 0.07044 | 0.026724 | -0.067828 | -0.018186 | 0.00036105 | 0.022583 | 0.035588 | 0.010559 | -0.0429 | -0.00099117 | 0.010104 | 0.054932 | 0.022888 | 0.022888 | 0.068665 | 0.045776 | 0.004578 | -0.1236 | -0.004578 | 0.032043 | -0.1236 | -0.013733 | -0.013733 | 0.032043 | -0.022888 | 4.7607 | 4.6326 | -116.0385 | 4.7791 | 4.8248 | 0.19226 | -116.0294 | 4.7882 | 4.7333 | -116.098 | 4.7516 | 4.6326 | -0.10071 | -116.098 | 4.8019 | 4.8111 | 4.7791 | -116.2079 | 4.7424 | 4.7424 | 4.7882 | -116.1072
3662.3125 | 121.2296 | -5.7037 | 115.0314 | 0.013046 | 0.00049979 | 0.066808 | 0.022879 | -0.068255 | -0.021176 | 0.00207 | 0.014954 | 0.037083 | 0.009064 | -0.040123 | -0.0041956 | 0.013095 | 0.009155 | -0.009155 | -0.009155 | 0.036621 | 0.045776 | 0.009155 | -0.10986 | -0.064087 | -0.041199 | -0.16479 | -0.032043 | 0.004578 | 0.045776 | -0.027466 | 5.7129 | 5.5939 | -114.9857 | 5.6946 | 5.7404 | 0.14648 | -115.0223 | 5.7495 | 5.6763 | -115.0635 | 5.6396 | 5.5389 | -0.13733 | -115.0269 | 5.7495 | 5.7129 | 5.6946 | -115.1413 | 5.6717 | 5.7083 | 5.6625 | -115.0589
3664.1094 | 121.2708 | -4.1748 | 117.1371 | 0.013046 | 0.0034906 | 0.071722 | 0.024802 | -0.069964 | -0.028226 | 0.0014292 | 0.022583 | 0.031742 | 0.007355 | -0.045677 | -0.0059046 | 0.014163 | 0.050354 | 0.073242 | 0.10986 | 0.10529 | 0.022888 | 0.059509 | -0.082397 | 0.013733 | 0.07782 | -0.032043 | -0.054932 | -0.041199 | 0.054932 | -0.022888 | 4.2343 | 4.0924 | -117.1143 | 4.248 | 4.2801 | 0.18768 | -117.0868 | 4.2297 | 4.1519 | -117.1921 | 4.1885 | 4.1428 | -0.009155 | -117.1783 | 4.1977 | 4.2252 | 4.2847 | -117.2195 | 4.1199 | 4.1336 | 4.2526 | -117.16
3665.9062 | 121.431 | -4.8203 | 116.7206 | 0.0054168 | 0.0051996 | 0.072149 | 0.02822 | -0.068041 | -0.03143 | -0.004125 | 0.0073242 | 0.029179 | 0.007355 | -0.045036 | -0.008468 | 0.01395 | 0.018311 | 0.045776 | 0.09613 | 0.10071 | 0.027466 | 0.032043 | -0.09613 | 0.009155 | 0.10986 | -0.018311 | -0.059509 | -0.027466 | 0.054932 | 0 | 4.8523 | 4.7241 | -116.6931 | 4.866 | 4.921 | 0.19684 | -116.7023 | 4.8752 | 4.8203 | -116.7801 | 4.8294 | 4.8019 | -0.018311 | -116.748 | 4.8477 | 4.8386 | 4.9164 | -116.8167 | 4.7607 | 4.7928 | 4.9301 | -116.7206
3667.6875 | 121.3989 | -112.9028 | 8.1894 | 0.013046 | 0.00028619 | 0.071081 | 0.032065 | -0.067614 | -0.025022 | -0.0017752 | 0.0073242 | 0.03217 | 0.0077822 | -0.043968 | -0.0082544 | 0.010318 | 0.082397 | 0.10071 | 0.12817 | 0.1236 | 0.059509 | 0.073242 | -0.045776 | 0.018311 | 0.10529 | -0.036621 | -0.009155 | 0.009155 | 0.036621 | -0.018311 | 112.9761 | 112.8571 | -8.1299 | 113.0035 | 113.0264 | 0.16937 | -8.107 | 112.9395 | 112.8845 | -8.1985 | 112.9211 | 112.8662 | -0.01831 | -8.1802 | 112.9623 | 112.9852 | 113.031 | -8.2352 | 112.8937 | 112.912 | 113.0081 | -8.2077
3669.4844 | 121.5088 | -114.2212 | 6.839 | 0.013046 | 0.0047724 | 0.066381 | 0.026938 | -0.066119 | -0.022672 | -0.00092075 | 0.014954 | 0.03217 | 0.005646 | -0.041404 | -0.00505 | 0.0090363 | 0.068665 | 0.036621 | 0.091553 | 0.12817 | 0.091553 | 0.050354 | -0.059509 | 0.07782 | 0.11902 | -0.009155 | -0.027466 | 0.013733 | 0.10529 | 0.022888 | 114.2715 | 114.1617 | -6.7474 | 114.2578 | 114.3494 | 0.18768 | -6.7703 | 114.3265 | 114.2441 | -6.8665 | 114.299 | 114.212 | -0.032043 | -6.8253 | 114.3127 | 114.2899 | 114.3127 | -6.8985 | 114.1937 | 114.2349 | 114.3402 | -6.8161
3671.2656 | 121.4951 | -114.5599 | 6.6055 | 0.013046 | 0.0030634 | 0.06809 | 0.027579 | -0.069323 | -0.022885 | 0.0010018 | 0.014954 | 0.033879 | 0.0082096 | -0.044609 | -0.00505 | 0.011386 | 0.11444 | 0.10529 | 0.15106 | 0.16479 | 0.054932 | 0.086975 | -0.032043 | 0.091553 | 0.12817 | 0.013733 | -0.032043 | -0.013733 | 0.082397 | 0.032043 | 114.6469 | 114.5279 | -6.5506 | 114.6652 | 114.7247 | 0.19684 | -6.4911 | 114.6423 | 114.592 | -6.6376 | 114.6515 | 114.5737 | -0.01831 | -6.6193 | 114.6149 | 114.6744 | 114.711 | -6.6376 | 114.5279 | 114.5462 | 114.6881 | -6.5735
3673 | 121.4951 | -114.8163 | 6.3675 | 0.0054168 | 0.0034906 | 0.071935 | 0.023947 | -0.066546 | -0.025022 | -0.00092075 | 0.014954 | 0.03516 | 0.005646 | -0.043327 | -0.00505 | 0.012241 | 0.045776 | 0.009155 | 0.050354 | 0.07782 | 0.091553 | 0.082397 | -0.068665 | 0.032043 | 0.068665 | -0.050354 | -0.013733 | 0 | 0.10071 | 0.009155 | 114.8987 | 114.7476 | -6.2759 | 114.8254 | 114.8941 | 0.14649 | -6.3217 | 114.917 | 114.8254 | -6.3812 | 114.8483 | 114.7659 | -0.059509 | -6.3675 | 114.9078 | 114.8621 | 114.8666 | -6.4362 | 114.8026 | 114.8163 | 114.8849 | -6.3583
3674.7812 | 121.4081 | -116.0522 | 5.2231 | 0.020676 | -0.00035461 | 0.070226 | 0.029288 | -0.067187 | -0.027799 | -0.00027975 | 0.014954 | 0.031315 | 0.009064 | -0.043541 | -0.0076136 | 0.010318 | 0.091553 | 0.1236 | 0.16022 | 0.15106 | 0.050354 | 0.082397 | -0.041199 | 0.054932 | 0.17395 | 0 | -0.022888 | -0.018311 | 0.09613 | 0.032043 | 116.1346 | 116.011 | -5.1727 | 116.1758 | 116.2033 | 0.19226 | -5.1315 | 116.1484 | 116.0843 | -5.246 | 116.1072 | 116.0522 | -0.032043 | -5.2414 | 116.1026 | 116.1438 | 116.2125 | -5.2643 | 116.0294 | 116.0339 | 116.2262 | -5.191
3676.5938 | 121.4218 | -116.0019 | 5.3238 | 0.0054168 | -0.0020636 | 0.068304 | 0.029288 | -0.068468 | -0.02374 | -0.00049335 | 0.014954 | 0.03217 | 0.007996 | -0.042259 | -0.0061182 | 0.012241 | 0.009155 | -0.013733 | 0.004578 | 0.059509 | 0.09613 | 0.036621 | -0.086975 | -0.032043 | 0.018311 | -0.11902 | 0.032043 | 0.041199 | 0.059509 | -0.027466 | 116.0385 | 115.9149 | -5.2277 | 115.9882 | 116.0614 | 0.14648 | -5.3146 | 116.0614 | 115.9744 | -5.2917 | 115.9698 | 115.8829 | -0.091553 | -5.2826 | 116.098 | 116.011 | 116.0065 | -5.4108 | 116.0339 | 116.0431 | 116.0202 | -5.3513
3678.3281 | 121.3806 | -115.5533 | 5.7724 | 0.0054168 | 0.00071339 | 0.068517 | 0.029288 | -0.068468 | -0.025235 | -0.00027975 | -0.0003053 | 0.033665 | 0.0094912 | -0.044609 | -0.0099634 | 0.011386 | 0.059509 | 0.059509 | 0.10986 | 0.1236 | 0.064087 | 0.068665 | -0.073242 | -0.018311 | 0.064087 | -0.068665 | 0.009155 | 0.032043 | 0.059509 | -0.013733 | 115.6219 | 115.48 | -5.7083 | 115.6128 | 115.6769 | 0.19684 | -5.7129 | 115.6128 | 115.5396 | -5.7632 | 115.535 | 115.4846 | -0.054932 | -5.7404 | 115.6174 | 115.6128 | 115.6631 | -5.8456 | 115.5624 | 115.5853 | 115.6174 | -5.7861
3680.1094 | 121.3852 | -116.4825 | 4.8111 | 0.0054168 | -0.00014101 | 0.07279 | 0.030142 | -0.070605 | -0.02609 | -0.0017752 | 0.022583 | 0.033665 | 0.0099186 | -0.043113 | -0.005691 | 0.013309 | 0.004578 | 0.009155 | 0.032043 | 0.064087 | 0.086975 | 0.045776 | -0.09613 | -0.036621 | 0.050354 | -0.09613 | 0.022888 | 0.032043 | 0.050354 | -0.032043 | 116.5283 | 116.3864 | -4.7241 | 116.4917 | 116.5466 | 0.16022 | -4.8065 | 116.5329 | 116.4505 | -4.7882 | 116.4459 | 116.3864 | -0.064087 | -4.7791 | 116.5695 | 116.4871 | 116.5146 | -4.9072 | 116.5054 | 116.5146 | 116.5329 | -4.8431
3681.9062 | 121.3852 | -117.3615 | 3.9734 | 0.013046 | -0.0033454 | 0.07044 | 0.024802 | -0.070818 | -0.021604 | 0.003779 | 0.022583 | 0.03516 | 0.007996 | -0.041832 | -0.00035037 | 0.011386 | 0.064087 | 0.041199 | 0.054932 | 0.091553 | 0.082397 | 0.054932 | -0.073242 | 0.018311 | 0.045776 | -0.10071 | 0.013733 | 0.027466 | 0.064087 | -0.032043 | 117.4164 | 117.2882 | -3.891 | 117.4026 | 117.453 | 0.16479 | -3.9093 | 117.4255 | 117.3294 | -3.9597 | 117.3798 | 117.2607 | -0.068665 | -3.9459 | 117.4438 | 117.4255 | 117.4164 | -4.0466 | 117.3752 | 117.3889 | 117.4072 | -4.0054
3683.7031 | 121.4035 | -117.6178 | 3.7354 | 0.020676 | -0.00035461 | 0.071722 | 0.028433 | -0.069537 | -0.028653 | -0.0019888 | 0.0073242 | 0.031101 | 0.0097048 | -0.0429 | -0.0069726 | 0.013736 | 0.086975 | 0.14191 | 0.14648 | 0.16022 | 0.054932 | 0.082397 | -0.041199 | 0.064087 | 0.17853 | 0.018311 | -0.022888 | 0.004578 | 0.10529 | 0.018311 | 117.7002 | 117.5766 | -3.6804 | 117.7597 | 117.778 | 0.20142 | -3.6484 | 117.7231 | 117.6361 | -3.7582 | 117.6819 | 117.6361 | 0 | -3.7308 | 117.6727 | 117.7048 | 117.7643 | -3.7766 | 117.5949 | 117.6224 | 117.7963 | -3.717
3685.5 | 121.5363 | -118.1168 | 3.1265 | 0.0054168 | 0.007763 | 0.076208 | 0.023306 | -0.071459 | -0.029508 | -0.001348 | 0.0073242 | 0.031529 | 0.0047916 | -0.043327 | -0.0059046 | 0.013095 | 0.086975 | 0.11902 | 0.14191 | 0.15106 | 0.068665 | 0.064087 | -0.050354 | 0.059509 | 0.17853 | 0.045776 | -0.032043 | -0.004578 | 0.11902 | 0.027466 | 118.1808 | 118.0664 | -3.0579 | 118.2358 | 118.2678 | 0.20142 | -3.0396 | 118.2358 | 118.1442 | -3.1586 | 118.1763 | 118.1625 | 0.01831 | -3.1311 | 118.1854 | 118.2037 | 118.2587 | -3.1769 | 118.0847 | 118.1122 | 118.2953 | -3.0991
3687.2344 | 121.4493 | -118.3548 | 3.0075 | 0.013046 | -0.00014101 | 0.06809 | 0.025656 | -0.069537 | -0.020963 | 0.00078825 | 0.022583 | 0.035588 | 0.0075686 | -0.043327 | -0.003341 | 0.013309 | 0.013733 | -0.045776 | 0 | 0.064087 | 0.10529 | 0.045776 | -0.068665 | -0.027466 | -0.018311 | -0.13275 | 0.018311 | 0.036621 | 0.068665 | -0.022888 | 118.4006 | 118.2861 | -2.9022 | 118.309 | 118.4189 | 0.13275 | -2.9938 | 118.4235 | 118.3319 | -2.9892 | 118.3273 | 118.222 | -0.10986 | -2.9709 | 118.4601 | 118.3685 | 118.3548 | -3.0762 | 118.3731 | 118.3914 | 118.3365 | -3.0304
3689.0312 | 121.4127 | -118.4463 | 2.9114 | -0.0022127 | 0.00028619 | 0.069799 | 0.025656 | -0.0674 | -0.022885 | 0.0018564 | 0.022583 | 0.033451 | 0.0069278 | -0.044609 | -0.001632 | 0.012882 | 0.013733 | -0.045776 | 0.004578 | 0.073242 | 0.09613 | 0.045776 | -0.09613 | -0.045776 | -0.018311 | -0.16022 | 0.018311 | 0.045776 | 0.054932 | 0.004578 | 118.4921 | 118.3502 | -2.8152 | 118.4006 | 118.5196 | 0.16937 | -2.8976 | 118.5013 | 118.4509 | -2.8931 | 118.4006 | 118.2861 | -0.16479 | -2.8656 | 118.5425 | 118.4601 | 118.4509 | -3.0075 | 118.4647 | 118.4921 | 118.428 | -2.9068
3690.8281 | 121.4905 | -118.5837 | 2.6962 | 0.013046 | 0.0069086 | 0.073644 | 0.023306 | -0.070605 | -0.02844 | -0.0011344 | 0.0073242 | 0.029606 | 0.0054324 | -0.041832 | -0.0074 | 0.015018 | 0.10071 | 0.13275 | 0.13733 | 0.11444 | 0.059509 | 0.091553 | -0.050354 | 0.036621 | 0.10986 | 0.004578 | -0.018311 | -0.004578 | 0.09613 | 0.004578 | 118.6752 | 118.5333 | -2.6367 | 118.7164 | 118.6981 | 0.16479 | -2.5955 | 118.6798 | 118.5883 | -2.7145 | 118.6203 | 118.5883 | 0 | -2.7008 | 118.6432 | 118.6844 | 118.721 | -2.7466 | 118.5654 | 118.5791 | 118.6935 | -2.6917
3692.625 | 121.4996 | -118.634 | 2.6733 | 0.0054168 | 0.004345 | 0.07279 | 0.026724 | -0.068682 | -0.02844 | -0.0024162 | 0.0073242 | 0.032597 | 0.0058596 | -0.04589 | -0.0099634 | 0.012241 | 0.086975 | 0.07782 | 0.11902 | 0.11902 | 0.064087 | 0.091553 | -0.045776 | 0.013733 | 0.09613 | -0.022888 | -0.027466 | 0 | 0.09613 | 0.009155 | 118.7256 | 118.5883 | -2.6093 | 118.7119 | 118.7531 | 0.16479 | -2.5864 | 118.7302 | 118.6432 | -2.7008 | 118.6478 | 118.6111 | -0.032043 | -2.6733 | 118.6981 | 118.721 | 118.7531 | -2.7191 | 118.6066 | 118.634 | 118.7302 | -2.6642
3694.3594 | 121.4722 | -118.6935 | 2.6642 | 0.013046 | -0.00078181 | 0.070226 | 0.026938 | -0.068896 | -0.022458 | -0.00092075 | 0.022583 | 0.03516 | 0.0094912 | -0.043541 | -0.0054772 | 0.0094635 | 0.032043 | -0.009155 | 0.022888 | 0.086975 | 0.10071 | 0.050354 | -0.082397 | -0.004578 | 0.050354 | -0.07782 | 0.022888 | 0.032043 | 0.07782 | -0.009155 | 118.7439 | 118.6111 | -2.5635 | 118.6844 | 118.7805 | 0.16937 | -2.6321 | 118.7714 | 118.6844 | -2.6413 | 118.689 | 118.6157 | -0.068665 | -2.6321 | 118.7942 | 118.7256 | 118.7164 | -2.7466 | 118.7164 | 118.7256 | 118.7439 | -2.6733
3696.1562 | 121.55 | -118.7164 | 2.5955 | 0.0054168 | 0.003277 | 0.067663 | 0.026724 | -0.068255 | -0.023526 | -6.615e-05 | 0.014954 | 0.031742 | 0.0088504 | -0.040336 | -0.0052636 | 0.012882 | 0.009155 | -0.018311 | 0.022888 | 0.073242 | 0.09613 | 0.059509 | -0.064087 | 0 | -0.009155 | -0.091553 | 0.018311 | 0.018311 | 0.059509 | -0.022888 | 118.7759 | 118.6523 | -2.4994 | 118.6981 | 118.7897 | 0.13733 | -2.5864 | 118.7759 | 118.6935 | -2.5772 | 118.7164 | 118.6249 | -0.068665 | -2.5772 | 118.8126 | 118.7256 | 118.7393 | -2.6596 | 118.7347 | 118.7347 | 118.7073 | -2.6184
3697.9375 | 121.4401 | -119.0323 | 2.3712 | 0.0054168 | 0.00092719 | 0.066167 | 0.026938 | -0.067187 | -0.021604 | 0.0024972 | -0.0003053 | 0.03516 | 0.0099186 | -0.041832 | -0.0044092 | 0.012027 | 0.009155 | -0.013733 | 0.027466 | 0.054932 | 0.091553 | 0.050354 | -0.07782 | -0.036621 | -0.009155 | -0.14191 | 0.032043 | 0.018311 | 0.064087 | -0.018311 | 119.0826 | 118.9545 | -2.2797 | 119.0186 | 119.0872 | 0.13275 | -2.3621 | 119.0964 | 119.014 | -2.3392 | 118.9957 | 118.8904 | -0.1236 | -2.3529 | 119.1238 | 119.0414 | 119.0598 | -2.449 | 119.0643 | 119.0506 | 119.0231 | -2.3895
3699.7188 | 121.4447 | -119.0231 | 2.3987 | 0.013046 | 7.2586e-05 | 0.068731 | 0.024802 | -0.067828 | -0.023953 | 0.0024972 | 0.014954 | 0.035374 | 0.0097048 | -0.041618 | -0.0054772 | 0.011813 | -0.004578 | -0.022888 | 0.009155 | 0.064087 | 0.091553 | 0.064087 | -0.073242 | -0.041199 | -0.013733 | -0.14648 | 0.032043 | 0.050354 | 0.07782 | -0.009155 | 119.0872 | 118.9499 | -2.3071 | 119.0002 | 119.0872 | 0.13733 | -2.4033 | 119.101 | 119.014 | -2.3666 | 118.9819 | 118.8766 | -0.13733 | -2.3483 | 119.1147 | 119.0186 | 119.0323 | -2.4719 | 119.0552 | 119.0735 | 119.0094 | -2.4078
3701.5312 | 121.4996 | -119.0002 | 2.3758 | 0.013046 | -0.0020636 | 0.071081 | 0.025229 | -0.068041 | -0.024381 | -0.00027975 | 0.0073242 | 0.035374 | 0.0082096 | -0.041191 | -0.0065454 | 0.013309 | 0.018311 | 0.013733 | 0.027466 | 0.10529 | 0.10071 | 0.050354 | -0.082397 | 0 | 0.064087 | -0.073242 | 0 | 0.032043 | 0.064087 | -0.009155 | 119.0506 | 118.9178 | -2.2751 | 119.014 | 119.1055 | 0.18768 | -2.3575 | 119.0643 | 118.9911 | -2.3758 | 119.0002 | 118.927 | -0.064087 | -2.3438 | 119.101 | 119.0186 | 119.0277 | -2.4582 | 119.0002 | 119.0323 | 119.0643 | -2.3849
3703.2656 | 121.4996 | -119.0323 | 2.3529 | -0.0022127 | -0.00185 | 0.068731 | 0.027792 | -0.0674 | -0.022244 | 0.0024972 | 0.0073242 | 0.033238 | 0.011627 | -0.041404 | -0.0074 | 0.012027 | 0.009155 | 0.027466 | 0.041199 | 0.10986 | 0.10071 | 0.073242 | -0.073242 | 0.013733 | 0.073242 | -0.059509 | 0.004578 | 0.022888 | 0.068665 | 0 | 119.1055 | 118.959 | -2.2522 | 119.0598 | 119.1422 | 0.18311 | -2.3438 | 119.101 | 119.0323 | -2.3483 | 119.046 | 118.9728 | -0.059509 | -2.33 | 119.133 | 119.0414 | 119.0735 | -2.4261 | 119.0369 | 119.0552 | 119.1055 | -2.3529
3705.0625 | 121.4905 | -119.0872 | 2.3254 | 0.013046 | 0.0019952 | 0.07279 | 0.029074 | -0.068682 | -0.028226 | -0.00070715 | 0.022583 | 0.03281 | 0.0071414 | -0.044609 | -0.0091088 | 0.015659 | -0.009155 | 0.045776 | 0.054932 | 0.082397 | 0.068665 | 0.050354 | -0.086975 | -0.059509 | 0.054932 | -0.091553 | 0.004578 | 0.050354 | 0.050354 | -0.018311 | 119.1376 | 119.0002 | -2.2568 | 119.133 | 119.1696 | 0.16937 | -2.3346 | 119.1376 | 119.0689 | -2.3209 | 119.0277 | 118.9957 | -0.073242 | -2.2751 | 119.1559 | 119.0781 | 119.1422 | -2.4124 | 119.0918 | 119.1376 | 119.1422 | -2.3438
3706.8594 | 121.5454 | -119.101 | 2.3071 | 0.0054168 | -0.003559 | 0.06809 | 0.030569 | -0.0674 | -0.02374 | -0.00027975 | -0.0003053 | 0.032597 | 0.0099186 | -0.0429 | -0.0071862 | 0.0116 | 0.032043 | 0.027466 | 0.045776 | 0.10986 | 0.10071 | 0.041199 | -0.086975 | 0 | 0.068665 | -0.082397 | 0.004578 | 0.036621 | 0.054932 | -0.004578 | 119.1422 | 119.014 | -2.2064 | 119.1284 | 119.2108 | 0.19684 | -2.2751 | 119.1559 | 119.0964 | -2.3026 | 119.101 | 119.0186 | -0.077819 | -2.2705 | 119.2017 | 119.133 | 119.1467 | -2.3941 | 119.1055 | 119.1376 | 119.1696 | -2.3117
3708.6562 | 121.5408 | -119.1284 | 2.2705 | -0.0022127 | 0.0019952 | 0.06809 | 0.024374 | -0.069323 | -0.022031 | 0.00207 | 0.014954 | 0.033879 | 0.009064 | -0.041404 | -0.00505 | 0.011813 | -0.018311 | -0.032043 | -0.004578 | 0.059509 | 0.10071 | 0.054932 | -0.068665 | -0.054932 | -0.013733 | -0.11444 | 0.032043 | 0.036621 | 0.050354 | -0.009155 | 119.1833 | 119.0598 | -2.1698 | 119.0964 | 119.1879 | 0.12817 | -2.2888 | 119.1788 | 119.1193 | -2.2385 | 119.0735 | 119.014 | -0.10529 | -2.2339 | 119.2291 | 119.1101 | 119.1238 | -2.3392 | 119.1605 | 119.165 | 119.1147 | -2.2797
3710.3906 | 121.6324 | -119.1788 | 2.2247 | 0.0054168 | 0.0017816 | 0.069799 | 0.031851 | -0.069323 | -0.030149 | -0.00070715 | -0.0003053 | 0.030033 | 0.007996 | -0.043541 | -0.0095362 | 0.014804 | 0.018311 | 0.036621 | 0.10529 | 0.11902 | 0.059509 | 0.07782 | -0.059509 | 0.027466 | 0.1236 | 0.004578 | 0 | 0.013733 | 0.09613 | 0.018311 | 119.2566 | 119.1193 | -2.1652 | 119.2154 | 119.2978 | 0.17853 | -2.2064 | 119.2749 | 119.1971 | -2.2247 | 119.2062 | 119.1833 | -0.013733 | -2.211 | 119.2383 | 119.1971 | 119.2841 | -2.2842 | 119.1788 | 119.1925 | 119.3024 | -2.2064
3712.1875 | 121.4722 | -119.2383 | 2.2247 | 0.013046 | -0.00099541 | 0.069585 | 0.027579 | -0.067614 | -0.021604 | 0.0012154 | 0.0073242 | 0.036228 | 0.007355 | -0.043327 | -0.0018458 | 0.0096771 | 0.022888 | 0 | 0.027466 | 0.07782 | 0.10071 | 0.054932 | -0.068665 | -0.022888 | 0.009155 | -0.14648 | 0.013733 | 0.036621 | 0.07782 | -0.013733 | 119.2932 | 119.1696 | -2.124 | 119.2383 | 119.3161 | 0.14649 | -2.2018 | 119.3161 | 119.2245 | -2.211 | 119.2154 | 119.0918 | -0.13275 | -2.1881 | 119.339 | 119.2612 | 119.2657 | -2.2934 | 119.252 | 119.2749 | 119.2474 | -2.2385
3713.9688 | 121.637 | -119.2062 | 2.1606 | 0.0054168 | 0.0045588 | 0.068304 | 0.02587 | -0.068468 | -0.023526 | -0.0019888 | 0.014954 | 0.035588 | 0.0075686 | -0.043113 | -0.0059046 | 0.011173 | 0.032043 | 0.018311 | 0.064087 | 0.09613 | 0.086975 | 0.068665 | -0.073242 | 0.041199 | 0.082397 | -0.032043 | -0.009155 | 0 | 0.086975 | 0.004578 | 119.2749 | 119.133 | -2.0737 | 119.2245 | 119.3024 | 0.16937 | -2.1286 | 119.2932 | 119.2108 | -2.1698 | 119.2474 | 119.1742 | -0.036621 | -2.1606 | 119.2932 | 119.2383 | 119.2703 | -2.2339 | 119.1971 | 119.2062 | 119.2886 | -2.1561
3715.75 | 121.5958 | -119.2703 | 2.1652 | 0.013046 | 0.0051996 | 0.075567 | 0.024374 | -0.068682 | -0.028653 | 0.00036105 | 0.030213 | 0.02982 | 0.0065006 | -0.043754 | -0.0080408 | 0.013309 | 0.10071 | 0.1236 | 0.13733 | 0.12817 | 0.041199 | 0.082397 | -0.041199 | 0.027466 | 0.10986 | -0.004578 | -0.022888 | 0 | 0.09613 | 0.027466 | 119.3527 | 119.2291 | -2.124 | 119.3939 | 119.3985 | 0.16937 | -2.0645 | 119.3665 | 119.2978 | -2.1881 | 119.2978 | 119.2657 | -0.032044 | -2.1652 | 119.3115 | 119.371 | 119.4077 | -2.2064 | 119.2474 | 119.2703 | 119.3802 | -2.1378
3717.5625 | 121.669 | -119.3939 | 2.0462 | -0.0022127 | 0.0054132 | 0.073217 | 0.027792 | -0.068041 | -0.02844 | -0.0024162 | 0.0073242 | 0.030888 | 0.0084232 | -0.044395 | -0.0099634 | 0.010745 | 0.059509 | 0.07782 | 0.1236 | 0.12817 | 0.064087 | 0.082397 | -0.036621 | 0.032043 | 0.14648 | 0.022888 | -0.009155 | 0.004578 | 0.09613 | 0.004578 | 119.4763 | 119.3573 | -1.9821 | 119.4717 | 119.5221 | 0.1648 | -1.9867 | 119.4901 | 119.3985 | -2.0554 | 119.426 | 119.4168 | 0.01831 | -2.0416 | 119.458 | 119.4534 | 119.5175 | -2.0828 | 119.3848 | 119.3985 | 119.5404 | -2.0416
3719.2969 | 121.6141 | -119.4168 | 2.0142 | 0.020676 | 0.0062676 | 0.073003 | 0.023734 | -0.06975 | -0.025235 | -0.0019888 | 0.014954 | 0.029392 | 0.0037234 | -0.043754 | -0.0059046 | 0.0116 | 0.10986 | 0.11902 | 0.16022 | 0.13275 | 0.059509 | 0.10529 | -0.045776 | 0.064087 | 0.10529 | 0 | -0.032043 | -0.004578 | 0.10529 | 0.013733 | 119.5221 | 119.371 | -1.9547 | 119.5358 | 119.5496 | 0.17853 | -1.9043 | 119.5221 | 119.4305 | -2.0462 | 119.4809 | 119.4168 | -0.013733 | -2.0187 | 119.4763 | 119.5267 | 119.577 | -2.0599 | 119.3848 | 119.4122 | 119.5221 | -2.0004
3721.0781 | 121.6644 | -119.4992 | 1.9089 | 0.013046 | 0.0039178 | 0.071722 | 0.026511 | -0.068041 | -0.020963 | -0.0024162 | -0.0079343 | 0.034306 | 0.004578 | -0.041832 | -0.0059046 | 0.010745 | 0.064087 | 0.032043 | 0.064087 | 0.11444 | 0.07782 | 0.073242 | -0.054932 | 0.068665 | 0.10071 | -0.032043 | -0.009155 | -0.009155 | 0.10071 | 0.018311 | 119.5724 | 119.4443 | -1.8311 | 119.5312 | 119.6136 | 0.16937 | -1.8448 | 119.5999 | 119.5175 | -1.918 | 119.5679 | 119.4672 | -0.050354 | -1.918 | 119.577 | 119.5633 | 119.5633 | -1.9638 | 119.4901 | 119.4901 | 119.5999 | -1.8906
3722.7969 | 121.637 | -119.6411 | 1.8082 | 0.020676 | 0.004345 | 0.073858 | 0.025229 | -0.068682 | -0.025662 | 0.00057465 | 0.0073242 | 0.033238 | 0.0071414 | -0.04589 | -0.0059046 | 0.012668 | 0.11444 | 0.12817 | 0.16022 | 0.15106 | 0.022888 | 0.091553 | -0.036621 | 0.073242 | 0.13733 | 0.018311 | -0.022888 | -0.013733 | 0.10071 | 0.013733 | 119.7327 | 119.6045 | -1.7853 | 119.7693 | 119.7922 | 0.18768 | -1.6937 | 119.7418 | 119.6548 | -1.8311 | 119.7144 | 119.6594 | 0.004578 | -1.8219 | 119.664 | 119.7556 | 119.8013 | -1.8448 | 119.6182 | 119.6274 | 119.7784 | -1.7944
3724.5938 | 121.55 | -119.7372 | 1.7807 | 0.0054168 | -0.0012092 | 0.067236 | 0.02822 | -0.066119 | -0.018826 | 0.00207 | -0.0003053 | 0.038151 | 0.0075686 | -0.0429 | -0.001632 | 0.011173 | 0.10071 | 0.054932 | 0.068665 | 0.10071 | 0.10529 | 0.073242 | -0.059509 | 0.009155 | 0.050354 | -0.09613 | 0.004578 | 0.013733 | 0.064087 | -0.009155 | 119.8105 | 119.6777 | -1.6754 | 119.7922 | 119.838 | 0.16022 | -1.68 | 119.8013 | 119.7281 | -1.7761 | 119.7464 | 119.6411 | -0.086975 | -1.767 | 119.8425 | 119.838 | 119.8059 | -1.8402 | 119.7418 | 119.751 | 119.7876 | -1.7899
3726.3281 | 121.6095 | -119.8425 | 1.6434 | -0.0022127 | -0.00099541 | 0.069158 | 0.026938 | -0.068896 | -0.020749 | 0.0022836 | 0.0073242 | 0.035588 | 0.007996 | -0.039909 | -0.005691 | 0.010532 | 0.054932 | 0.041199 | 0.073242 | 0.1236 | 0.086975 | 0.050354 | -0.064087 | 0.027466 | 0.073242 | -0.07782 | 0.009155 | 0.004578 | 0.09613 | -0.009155 | 119.8929 | 119.7784 | -1.5564 | 119.8837 | 119.9661 | 0.18768 | -1.5884 | 119.9387 | 119.8334 | -1.6342 | 119.87 | 119.7647 | -0.068665 | -1.6388 | 119.9295 | 119.8975 | 119.9158 | -1.7075 | 119.8517 | 119.8471 | 119.9158 | -1.6525
3728.1094 | 121.5591 | -119.9524 | 1.5747 | 0.020676 | -0.0022772 | 0.069372 | 0.02587 | -0.066546 | -0.02139 | 0.0024972 | 0.022583 | 0.033879 | 0.0075686 | -0.041618 | -0.0029138 | 0.0116 | 0.009155 | -0.004578 | 0.022888 | 0.086975 | 0.082397 | 0.050354 | -0.082397 | -0.045776 | -0.013733 | -0.13733 | 0 | 0.032043 | 0.059509 | -0.013733 | 120.0027 | 119.87 | -1.4923 | 119.9478 | 120.0394 | 0.16937 | -1.5656 | 120.0119 | 119.9387 | -1.5747 | 119.9066 | 119.8151 | -0.1236 | -1.5427 | 120.0348 | 119.9615 | 119.9753 | -1.6571 | 119.9524 | 119.9844 | 119.9387 | -1.5884
3729.8906 | 121.6187 | -120.0302 | 1.506 | 0.0054168 | -0.00056821 | 0.067236 | 0.027579 | -0.069109 | -0.022458 | 0.00078825 | 0.0073242 | 0.033879 | 0.0092776 | -0.043754 | -0.0052636 | 0.010318 | 0.004578 | 0.004578 | 0.027466 | 0.11902 | 0.10071 | 0.054932 | -0.09613 | -0.004578 | 0.059509 | -0.082397 | 0.018311 | 0.032043 | 0.041199 | -0.009155 | 120.0851 | 119.9341 | -1.4053 | 120.0348 | 120.1492 | 0.21515 | -1.5015 | 120.0714 | 120.0211 | -1.4877 | 120.0256 | 119.9478 | -0.073242 | -1.474 | 120.1309 | 120.0348 | 120.0577 | -1.6022 | 120.0485 | 120.0623 | 120.0897 | -1.5152
3731.7031 | 121.6873 | -120.1309 | 1.3458 | 0.013046 | 0.0045588 | 0.072363 | 0.023947 | -0.069109 | -0.028867 | 0.0027108 | -0.0003053 | 0.028965 | 0.0050052 | -0.044609 | -0.0071862 | 0.014163 | 0.082397 | 0.13275 | 0.15106 | 0.14191 | 0.068665 | 0.09613 | -0.050354 | 0.059509 | 0.13733 | 0.018311 | -0.045776 | 0.009155 | 0.091553 | 0.032043 | 120.2271 | 120.0806 | -1.2772 | 120.2637 | 120.2728 | 0.19226 | -1.2634 | 120.2225 | 120.163 | -1.3916 | 120.1904 | 120.1492 | -0.013732 | -1.3367 | 120.1996 | 120.2133 | 120.282 | -1.3962 | 120.0851 | 120.1401 | 120.2682 | -1.3138
3733.5 | 121.6324 | -120.2866 | 1.2497 | -0.0022127 | 0.00028619 | 0.071294 | 0.026724 | -0.069109 | -0.023526 | -0.00027975 | 0.014954 | 0.034092 | 0.0092776 | -0.040977 | -0.006759 | 0.010745 | -0.009155 | -0.013733 | 0.004578 | 0.073242 | 0.10071 | 0.041199 | -0.082397 | -0.045776 | 0.032043 | -0.10071 | 0.009155 | 0.036621 | 0.050354 | -0.013733 | 120.3278 | 120.2042 | -1.149 | 120.2728 | 120.3598 | 0.15564 | -1.2589 | 120.3369 | 120.2728 | -1.2405 | 120.2408 | 120.1859 | -0.086975 | -1.2131 | 120.3873 | 120.2774 | 120.2911 | -1.3321 | 120.2957 | 120.3232 | 120.3186 | -1.2634
3735.2344 | 121.7422 | -120.3552 | 1.1215 | -0.0022127 | 0.0037042 | 0.073644 | 0.029501 | -0.070818 | -0.030362 | -0.0026298 | 0.0073242 | 0.028965 | 0.0069278 | -0.042686 | -0.010818 | 0.014163 | 0.032043 | 0.064087 | 0.10071 | 0.10986 | 0.07782 | 0.086975 | -0.045776 | 0.013733 | 0.11444 | 0.009155 | -0.022888 | 0.013733 | 0.10529 | 0.022888 | 120.4422 | 120.3094 | -1.0437 | 120.4193 | 120.4651 | 0.15564 | -1.0895 | 120.4605 | 120.3781 | -1.1444 | 120.369 | 120.3644 | -0.013733 | -1.1078 | 120.433 | 120.3873 | 120.4559 | -1.1673 | 120.3323 | 120.369 | 120.4697 | -1.0986
3737.0469 | 121.7285 | -120.4742 | 1.062 | 0.0054168 | 0.0041314 | 0.07044 | 0.030997 | -0.066973 | -0.028867 | -0.00049335 | 0.014954 | 0.027256 | 0.0088504 | -0.043968 | -0.0088952 | 0.010745 | 0.086975 | 0.11444 | 0.14191 | 0.13275 | 0.07782 | 0.07782 | -0.059509 | 0.064087 | 0.16479 | 0.036621 | -0.013733 | -0.013733 | 0.11444 | 0.032043 | 120.5521 | 120.4147 | -0.98419 | 120.5887 | 120.607 | 0.19226 | -0.97504 | 120.5887 | 120.5063 | -1.0757 | 120.5383 | 120.5109 | 0.004578 | -1.0757 | 120.5521 | 120.5612 | 120.6162 | -1.1215 | 120.4605 | 120.4605 | 120.639 | -1.03
3738.8438 | 121.7331 | -120.4376 | 1.0529 | 0.0054168 | 0.0034906 | 0.070226 | 0.026724 | -0.067828 | -0.023313 | 0.0027108 | 0.014954 | 0.034092 | 0.0054324 | -0.039695 | -0.0054772 | 0.0092499 | 0.086975 | 0.041199 | 0.09613 | 0.11444 | 0.07782 | 0.086975 | -0.041199 | 0.082397 | 0.09613 | -0.032043 | -0.013733 | -0.004578 | 0.09613 | 0.032043 | 120.5246 | 120.3964 | -0.97504 | 120.4788 | 120.5521 | 0.15564 | -0.96588 | 120.5338 | 120.4697 | -1.0666 | 120.52 | 120.4056 | -0.064086 | -1.0574 | 120.5154 | 120.5246 | 120.5338 | -1.0941 | 120.4239 | 120.433 | 120.5338 | -1.0208
3740.6406 | 121.6553 | -120.5063 | 1.0483 | 0.013046 | -0.0024908 | 0.070226 | 0.029288 | -0.068468 | -0.022244 | -0.0017752 | 0.022583 | 0.033879 | 0.0092776 | -0.042472 | -0.006759 | 0.0096771 | 0 | -0.004578 | 0.013733 | 0.082397 | 0.10986 | 0.032043 | -0.086975 | -0.036621 | 0.009155 | -0.10986 | 0.027466 | 0.036621 | 0.073242 | -0.032043 | 120.5383 | 120.4193 | -0.93842 | 120.5017 | 120.5887 | 0.16937 | -1.0483 | 120.5795 | 120.4742 | -1.0208 | 120.4697 | 120.3964 | -0.07782 | -1.0117 | 120.6162 | 120.5063 | 120.52 | -1.1353 | 120.5338 | 120.5429 | 120.5154 | -1.0803
3742.3906 | 121.6187 | -120.3094 | 1.2405 | 0.013046 | -0.00035461 | 0.067663 | 0.024161 | -0.067614 | -0.023099 | 0.00057465 | 0.0073242 | 0.037083 | 0.0084232 | -0.040123 | -0.0044092 | 0.010959 | 0.073242 | 0.064087 | 0.073242 | 0.10071 | 0.09613 | 0.064087 | -0.059509 | 0.027466 | 0.086975 | -0.068665 | 0.004578 | 0.022888 | 0.07782 | 0 | 120.3735 | 120.2499 | -1.1444 | 120.3735 | 120.4102 | 0.16022 | -1.1673 | 120.3873 | 120.3094 | -1.236 | 120.3369 | 120.2408 | -0.068665 | -1.2177 | 120.4056 | 120.3827 | 120.3827 | -1.3 | 120.314 | 120.3323 | 120.3964 | -1.2405
3744.1875 | 121.6141 | -120.2545 | 1.3367 | 0.0054168 | 0.00049979 | 0.070013 | 0.024374 | -0.064623 | -0.02139 | 0.0018564 | 0.014954 | 0.035374 | 0.0092776 | -0.040123 | -0.003982 | 0.013095 | 0.050354 | 0.050354 | 0.050354 | 0.091553 | 0.086975 | 0.045776 | -0.073242 | 0.004578 | 0.022888 | -0.11902 | 0.009155 | 0.032043 | 0.045776 | 0 | 120.3003 | 120.1813 | -1.2497 | 120.3049 | 120.3461 | 0.16479 | -1.2863 | 120.3003 | 120.2545 | -1.3275 | 120.2591 | 120.1355 | -0.11902 | -1.3046 | 120.3415 | 120.3049 | 120.3049 | -1.4099 | 120.2637 | 120.2866 | 120.2774 | -1.3367
3745.9844 | 121.7148 | -120.2454 | 1.3412 | 0.0054168 | 0.004986 | 0.074499 | 0.027365 | -0.068896 | -0.027799 | 0.00014745 | 0.022583 | 0.032597 | 0.0054324 | -0.04525 | -0.0061182 | 0.014591 | 0.082397 | 0.1236 | 0.13733 | 0.13275 | 0.054932 | 0.091553 | -0.032043 | 0.064087 | 0.11444 | 0 | -0.027466 | 0 | 0.082397 | 0.022888 | 120.3369 | 120.2133 | -1.2863 | 120.369 | 120.3781 | 0.16479 | -1.2589 | 120.3278 | 120.2682 | -1.3687 | 120.3094 | 120.2454 | -0.022888 | -1.3412 | 120.3003 | 120.3278 | 120.3827 | -1.3733 | 120.2179 | 120.2454 | 120.3598 | -1.3184
3747.7656 | 121.6644 | -120.1447 | 1.4557 | 0.0054168 | -0.0039862 | 0.070654 | 0.026938 | -0.067187 | -0.024167 | 0.00078825 | 0.014954 | 0.034306 | 0.0058596 | -0.040763 | -0.002273 | 0.012027 | 0.036621 | 0.059509 | 0.064087 | 0.10071 | 0.10529 | 0.059509 | -0.07782 | 0.027466 | 0.07782 | -0.073242 | 0.018311 | 0.013733 | 0.073242 | 0 | 120.2042 | 120.0668 | -1.3504 | 120.2042 | 120.2454 | 0.17853 | -1.4191 | 120.2179 | 120.1447 | -1.4374 | 120.1721 | 120.0714 | -0.073242 | -1.442 | 120.2499 | 120.1813 | 120.2087 | -1.5335 | 120.163 | 120.1584 | 120.2225 | -1.4557
3749.5625 | 121.6873 | -120.0577 | 1.4877 | 0.013046 | 0.0017816 | 0.068945 | 0.025656 | -0.068896 | -0.023313 | 0.00036105 | 0.014954 | 0.033665 | 0.0077822 | -0.042045 | -0.0071862 | 0.013309 | 0.004578 | -0.041199 | 0.009155 | 0.068665 | 0.13275 | 0.054932 | -0.082397 | -0.036621 | -0.013733 | -0.13275 | 0.027466 | 0.050354 | 0.07782 | -0.004578 | 120.1126 | 119.9753 | -1.355 | 120.0165 | 120.1263 | 0.15106 | -1.4832 | 120.1355 | 120.0531 | -1.4603 | 120.0211 | 119.9249 | -0.12817 | -1.4374 | 120.1904 | 120.0623 | 120.0668 | -1.5701 | 120.0851 | 120.108 | 120.0439 | -1.4923
3751.3438 | 121.6553 | -119.9478 | 1.6388 | 0.0054168 | -0.00014101 | 0.067876 | 0.026297 | -0.067828 | -0.022458 | -6.615e-05 | 0.0073242 | 0.033665 | 0.0099186 | -0.0429 | -0.003982 | 0.011813 | 0.064087 | 0.068665 | 0.073242 | 0.11902 | 0.082397 | 0.059509 | -0.07782 | 0.027466 | 0.07782 | -0.086975 | 0.022888 | 0.036621 | 0.068665 | 0.009155 | 120.0073 | 119.87 | -1.5564 | 120.0165 | 120.0668 | 0.19684 | -1.5747 | 120.0165 | 119.957 | -1.6159 | 119.9753 | 119.8608 | -0.09613 | -1.6022 | 120.0302 | 120.0119 | 120.0211 | -1.7166 | 119.9707 | 119.9844 | 120.0256 | -1.6296
3753.0781 | 121.7148 | -120.0531 | 1.5381 | 0.0054168 | -0.00099541 | 0.069372 | 0.02886 | -0.067187 | -0.024808 | -0.00027975 | 0.014954 | 0.033238 | 0.0097048 | -0.045036 | -0.0063318 | 0.013309 | 0.004578 | 0.013733 | 0.045776 | 0.10071 | 0.09613 | 0.050354 | -0.07782 | -0.004578 | 0.073242 | -0.082397 | 0.004578 | 0.032043 | 0.059509 | -0.004578 | 120.1035 | 119.9753 | -1.442 | 120.0668 | 120.1538 | 0.17853 | -1.5335 | 120.1126 | 120.0485 | -1.5335 | 120.0485 | 119.9707 | -0.077819 | -1.506 | 120.1492 | 120.0577 | 120.0989 | -1.6159 | 120.0577 | 120.0851 | 120.1263 | -1.5427
3754.8438 | 121.7697 | -120.0623 | 1.4969 | 0.020676 | 0.0030634 | 0.071294 | 0.028647 | -0.064837 | -0.024167 | 0.00078825 | -0.0003053 | 0.031956 | 0.0084232 | -0.040123 | -0.00505 | 0.014377 | -0.013733 | 0.004578 | 0.032043 | 0.07782 | 0.091553 | 0.054932 | -0.073242 | 0.018311 | 0.041199 | -0.059509 | 0 | 0.009155 | 0.082397 | -0.004578 | 120.1172 | 119.989 | -1.4053 | 120.0668 | 120.1401 | 0.15106 | -1.5106 | 120.1447 | 120.0577 | -1.4969 | 120.0806 | 120.0027 | -0.054931 | -1.4877 | 120.1538 | 120.0485 | 120.0943 | -1.5701 | 120.0623 | 120.0714 | 120.1035 | -1.5015
3756.6562 | 121.7926 | -120.1126 | 1.4465 | 0.013046 | 0.003277 | 0.07279 | 0.028647 | -0.068468 | -0.030149 | -0.0028434 | 0.0073242 | 0.030888 | 0.0075686 | -0.044609 | -0.0080408 | 0.014591 | 0.054932 | 0.11444 | 0.14191 | 0.13733 | 0.064087 | 0.07782 | -0.050354 | 0.036621 | 0.16937 | 0.045776 | -0.018311 | -0.013733 | 0.10071 | 0 | 120.1904 | 120.0623 | -1.3824 | 120.2271 | 120.2499 | 0.18768 | -1.3916 | 120.2133 | 120.1126 | -1.4648 | 120.1492 | 120.1584 | 0.045776 | -1.4603 | 120.1767 | 120.1675 | 120.2545 | -1.4969 | 120.0943 | 120.0989 | 120.282 | -1.4465
3758.4531 | 121.8018 | -120.1401 | 1.4008 | 0.020676 | 0.0022088 | 0.071294 | 0.026938 | -0.066973 | -0.023099 | -6.615e-05 | 0.0073242 | 0.034947 | 0.0082096 | -0.042259 | -0.00505 | 0.012241 | 0.022888 | -0.009155 | 0.013733 | 0.073242 | 0.082397 | 0.068665 | -0.07782 | -0.018311 | 0.022888 | -0.07782 | -0.009155 | 0.032043 | 0.07782 | 0.004578 | 120.2087 | 120.0623 | -1.3184 | 120.1309 | 120.2133 | 0.15106 | -1.3779 | 120.2179 | 120.1447 | -1.4099 | 120.1218 | 120.0623 | -0.082398 | -1.3687 | 120.2225 | 120.163 | 120.1538 | -1.4786 | 120.1309 | 120.1721 | 120.163 | -1.3962
3760.2031 | 121.669 | -120.2316 | 1.3916 | 0.013046 | 0.0013544 | 0.072363 | 0.027152 | -0.06975 | -0.026303 | -0.00070715 | 0.014954 | 0.031315 | 0.0077822 | -0.040336 | -0.0099634 | 0.012241 | -0.009155 | 0 | 0.045776 | 0.07782 | 0.10529 | 0.041199 | -0.086975 | -0.059509 | 0.032043 | -0.09613 | 0.022888 | 0.041199 | 0.059509 | -0.013733 | 120.2728 | 120.1447 | -1.2863 | 120.2316 | 120.3094 | 0.16479 | -1.4008 | 120.2911 | 120.2179 | -1.3687 | 120.1721 | 120.1355 | -0.082397 | -1.3504 | 120.3369 | 120.2225 | 120.2774 | -1.4786 | 120.2545 | 120.2728 | 120.2637 | -1.4053
3762 | 121.7285 | -120.2957 | 1.3412 | 0.013046 | 0.00049979 | 0.073003 | 0.029074 | -0.067614 | -0.026303 | -0.00027975 | 0.022583 | 0.033665 | 0.0075686 | -0.043327 | -0.0080408 | 0.011813 | 0.004578 | -0.004578 | 0.018311 | 0.059509 | 0.11444 | 0.032043 | -0.09613 | -0.050354 | 0.018311 | -0.10529 | 0.013733 | 0.022888 | 0.054932 | -0.018311 | 120.3278 | 120.1996 | -1.2268 | 120.2911 | 120.3552 | 0.15564 | -1.3367 | 120.3506 | 120.2774 | -1.3275 | 120.2454 | 120.1904 | -0.086975 | -1.3184 | 120.4102 | 120.3003 | 120.314 | -1.4374 | 120.3094 | 120.3186 | 120.314 | -1.3596
3763.7812 | 121.8063 | -120.3049 | 1.2543 | 0.013046 | 0.0039178 | 0.07044 | 0.024802 | -0.069964 | -0.025662 | 0.00057465 | 0.0073242 | 0.031101 | 0.0069278 | -0.044609 | -0.0044092 | 0.012027 | 0.10071 | 0.11902 | 0.15564 | 0.16937 | 0.059509 | 0.10071 | -0.041199 | 0.073242 | 0.11902 | 0.018311 | -0.036621 | -0.009155 | 0.10071 | 0.027466 | 120.4056 | 120.2637 | -1.1948 | 120.4239 | 120.4742 | 0.21057 | -1.1536 | 120.4056 | 120.3323 | -1.2909 | 120.3781 | 120.3232 | -0.009155 | -1.2634 | 120.3644 | 120.4056 | 120.4605 | -1.2955 | 120.2683 | 120.2957 | 120.4239 | -1.2268
3765.5156 | 121.7468 | -120.3506 | 1.2726 | 0.0054168 | -0.00056821 | 0.072576 | 0.026511 | -0.066332 | -0.024594 | -0.0019888 | 0.014954 | 0.034092 | 0.007355 | -0.043754 | -0.0061182 | 0.010745 | 0.004578 | 0 | 0.018311 | 0.07782 | 0.10529 | 0.054932 | -0.07782 | -0.032043 | 0.036621 | -0.10071 | 0.027466 | 0.027466 | 0.045776 | -0.013733 | 120.4056 | 120.2728 | -1.1673 | 120.3506 | 120.4285 | 0.15564 | -1.268 | 120.3964 | 120.3369 | -1.2451 | 120.3186 | 120.2499 | -0.086975 | -1.2451 | 120.4559 | 120.3552 | 120.369 | -1.3504 | 120.3781 | 120.3781 | 120.3873 | -1.2863
3768.625 | 121.8201 | -120.3827 | 1.2131 | 0.013046 | 0.008404 | 0.073644 | 0.027792 | -0.068255 | -0.028653 | -0.00070715 | 0.030213 | 0.028324 | 0.007355 | -0.042045 | -0.0078272 | 0.013736 | 0.041199 | 0.059509 | 0.10986 | 0.10529 | 0.064087 | 0.068665 | -0.041199 | 0.004578 | 0.073242 | -0.027466 | -0.022888 | 0.009155 | 0.068665 | -0.004578 | 120.4514 | 120.3415 | -1.149 | 120.4422 | 120.488 | 0.14649 | -1.1719 | 120.4514 | 120.3781 | -1.236 | 120.3873 | 120.3552 | -0.022888 | -1.2039 | 120.4468 | 120.4239 | 120.4926 | -1.2543 | 120.3598 | 120.3918 | 120.4559 | -1.2177
3772.7188 | 121.6873 | -118.7576 | 2.8976 | 0.020676 | 7.2586e-05 | 0.070013 | 0.02587 | -0.070605 | -0.023526 | -0.00027975 | 0.014954 | 0.03516 | 0.0084232 | -0.042472 | -0.0052636 | 0.010959 | 0.073242 | 0.054932 | 0.073242 | 0.10071 | 0.073242 | 0.064087 | -0.068665 | 0.018311 | 0.054932 | -0.086975 | -0.004578 | 0.041199 | 0.068665 | -0.013733 | 118.8217 | 118.689 | -2.8244 | 118.8126 | 118.8583 | 0.16937 | -2.8244 | 118.8263 | 118.7439 | -2.9022 | 118.7759 | 118.6707 | -0.073242 | -2.8564 | 118.8309 | 118.8309 | 118.8309 | -2.9663 | 118.7531 | 118.7988 | 118.8126 | -2.9114
3778.875 | 121.8155 | -118.1305 | 3.4058 | 0.013046 | 0.0051996 | 0.073644 | 0.026938 | -0.071459 | -0.030576 | -0.00049335 | 0.014954 | 0.029606 | 0.0032962 | -0.043327 | -0.0071862 | 0.011386 | 0.027466 | 0.050354 | 0.091553 | 0.10986 | 0.059509 | 0.068665 | -0.054932 | 0.013733 | 0.086975 | -0.022888 | -0.041199 | 0.004578 | 0.082397 | 0.009155 | 118.1992 | 118.0756 | -3.3463 | 118.1808 | 118.2404 | 0.16479 | -3.3783 | 118.2129 | 118.1396 | -3.447 | 118.1442 | 118.1076 | -0.032043 | -3.4012 | 118.19 | 118.158 | 118.222 | -3.4607 | 118.0893 | 118.1351 | 118.2175 | -3.3966
3780.8281 | 121.6782 | -118.6066 | 3.0533 | 0.020676 | -0.00185 | 0.069158 | 0.026083 | -0.068255 | -0.020535 | 0.00036105 | 0.0073242 | 0.033665 | 0.007996 | -0.042686 | -0.0044092 | 0.010959 | 0.073242 | 0.045776 | 0.07782 | 0.10071 | 0.068665 | 0.068665 | -0.09613 | 0.004578 | 0.064087 | -0.091553 | 0.009155 | 0.041199 | 0.059509 | -0.018311 | 118.6752 | 118.5104 | -2.9846 | 118.6523 | 118.7073 | 0.19684 | -2.98 | 118.6661 | 118.5883 | -3.0441 | 118.6111 | 118.515 | -0.073242 | -3.0121 | 118.6752 | 118.6798 | 118.6844 | -3.1494 | 118.6157 | 118.6478 | 118.6707 | -3.0716
3782.6562 | 121.6873 | -119.2474 | 2.3529 | 0.013046 | -0.00035461 | 0.070867 | 0.027365 | -0.070391 | -0.02139 | 0.0014292 | 0.0073242 | 0.034733 | 0.0088504 | -0.040763 | -0.0052636 | 0.011173 | -0.004578 | -0.027466 | 0.018311 | 0.064087 | 0.091553 | 0.045776 | -0.09613 | -0.041199 | -0.009155 | -0.16022 | 0.036621 | 0.032043 | 0.050354 | -0.009155 | 119.2932 | 119.1513 | -2.2614 | 119.22 | 119.3115 | 0.16022 | -2.3575 | 119.2978 | 119.2383 | -2.3163 | 119.2062 | 119.0872 | -0.15106 | -2.3209 | 119.339 | 119.2429 | 119.2657 | -2.449 | 119.2841 | 119.2795 | 119.2383 | -2.3621
3784.4531 | 121.7651 | -118.7256 | 2.8061 | 0.013046 | 0.0039178 | 0.070867 | 0.029929 | -0.068041 | -0.031644 | -0.00070715 | 0.014954 | 0.028324 | 0.0067142 | -0.042686 | -0.0093226 | 0.014163 | 0.068665 | 0.14191 | 0.14191 | 0.13275 | 0.07782 | 0.068665 | -0.027466 | 0.07782 | 0.1831 | 0.036621 | -0.013733 | 0 | 0.091553 | 0.022888 | 118.7943 | 118.6981 | -2.7283 | 118.8675 | 118.8583 | 0.16022 | -2.7374 | 118.8171 | 118.7485 | -2.8198 | 118.8034 | 118.7622 | 0.013733 | -2.8061 | 118.8034 | 118.7943 | 118.8675 | -2.8336 | 118.7119 | 118.7256 | 118.9087 | -2.7832
3786.1875 | 121.6507 | -119.8883 | 1.7715 | 0.0054168 | -0.00078181 | 0.068304 | 0.027792 | -0.067614 | -0.021176 | -6.615e-05 | 0.0073242 | 0.033238 | 0.007996 | -0.0429 | -0.0054772 | 0.010959 | 0.050354 | 0.054932 | 0.064087 | 0.10986 | 0.07782 | 0.054932 | -0.064087 | 0.013733 | 0.07782 | -0.07782 | 0.004578 | 0.032043 | 0.07782 | -0.018311 | 119.9432 | 119.8242 | -1.6937 | 119.9432 | 119.9982 | 0.17395 | -1.7212 | 119.9661 | 119.87 | -1.767 | 119.902 | 119.8105 | -0.059509 | -1.7395 | 119.9661 | 119.9387 | 119.9524 | -1.8356 | 119.8929 | 119.9203 | 119.9661 | -1.7899
3787.9688 | 121.7377 | -120.282 | 1.3596 | 0.0054168 | -0.00185 | 0.070654 | 0.032492 | -0.069964 | -0.025235 | 0.00036105 | 0.0073242 | 0.033024 | 0.010346 | -0.043327 | -0.0059046 | 0.011173 | -0.013733 | 0.004578 | 0.022888 | 0.068665 | 0.10071 | 0.036621 | -0.091553 | -0.036621 | 0.004578 | -0.10529 | 0.018311 | 0.036621 | 0.041199 | -0.009155 | 120.3186 | 120.1904 | -1.2589 | 120.2866 | 120.3506 | 0.16022 | -1.3733 | 120.3232 | 120.2728 | -1.3412 | 120.2454 | 120.1767 | -0.096131 | -1.3229 | 120.3827 | 120.2682 | 120.3049 | -1.4511 | 120.3003 | 120.3186 | 120.2866 | -1.3687
3789.7656 | 121.8475 | -120.6757 | 0.93842 | 0.013046 | 0.0039178 | 0.070867 | 0.026938 | -0.069323 | -0.031217 | -0.00049335 | 0.0073242 | 0.029606 | 0.0099186 | -0.041618 | -0.011245 | 0.012882 | 0.018311 | 0.059509 | 0.10529 | 0.11902 | 0.073242 | 0.073242 | -0.045776 | 0.009155 | 0.09613 | -0.009155 | -0.004578 | 0.009155 | 0.10071 | 0.009155 | 120.7489 | 120.6299 | -0.86517 | 120.7352 | 120.7947 | 0.16479 | -0.92011 | 120.7764 | 120.6848 | -0.94299 | 120.6848 | 120.6665 | -0.01831 | -0.92926 | 120.7489 | 120.694 | 120.7809 | -0.98419 | 120.6711 | 120.6848 | 120.7718 | -0.92926
3791.5 | 121.7834 | -120.3964 | 1.2451 | 0.0054168 | 0.0017816 | 0.069585 | 0.024588 | -0.065905 | -0.020108 | 0.00057465 | -0.0003053 | 0.034733 | 0.0075686 | -0.04055 | -0.0035546 | 0.010959 | 0 | -0.041199 | 0 | 0.068665 | 0.11444 | 0.041199 | -0.09613 | -0.036621 | -0.022888 | -0.12817 | 0.013733 | 0.032043 | 0.050354 | -0.018311 | 120.4376 | 120.3003 | -1.1307 | 120.3552 | 120.4651 | 0.16479 | -1.2451 | 120.4468 | 120.3781 | -1.2314 | 120.3598 | 120.2682 | -0.10986 | -1.2131 | 120.5109 | 120.3964 | 120.3964 | -1.3412 | 120.4102 | 120.4285 | 120.3735 | -1.2634
3793.2344 | 121.7331 | -119.4443 | 2.2018 | 0.0054168 | 7.2586e-05 | 0.073858 | 0.027792 | -0.066332 | -0.025235 | -0.00092075 | 0.0073242 | 0.032597 | 0.0086368 | -0.044181 | -0.0054772 | 0.013095 | -0.013733 | 0.009155 | 0.018311 | 0.07782 | 0.10071 | 0.032043 | -0.07782 | -0.050354 | 0.018311 | -0.11444 | 0.013733 | 0.054932 | 0.064087 | -0.013733 | 119.4763 | 119.3665 | -2.1011 | 119.4534 | 119.5221 | 0.15564 | -2.2156 | 119.5084 | 119.4305 | -2.1881 | 119.3939 | 119.3298 | -0.10071 | -2.1469 | 119.545 | 119.4305 | 119.4626 | -2.2797 | 119.458 | 119.4992 | 119.4626 | -2.2156
3794.9688 | 121.8063 | -118.9224 | 2.6276 | 0.013046 | 0.0019952 | 0.067022 | 0.029501 | -0.0674 | -0.022885 | 0.00207 | 0.0073242 | 0.031529 | 0.0097048 | -0.040763 | -0.0074 | 0.011386 | 0.041199 | -0.009155 | 0.036621 | 0.091553 | 0.086975 | 0.059509 | -0.07782 | 0.027466 | 0.054932 | -0.045776 | -0.009155 | 0.004578 | 0.086975 | 0.018311 | 118.9819 | 118.8446 | -2.5406 | 118.9133 | 119.014 | 0.16937 | -2.5864 | 119.0094 | 118.9407 | -2.6367 | 118.9499 | 118.8766 | -0.064087 | -2.623 | 119.0094 | 118.9636 | 118.959 | -2.7054 | 118.9133 | 118.927 | 118.9774 | -2.6093
3796.75 | 121.6278 | -118.5471 | 3.0762 | 0.0054168 | -0.00099541 | 0.06809 | 0.025015 | -0.068896 | -0.021604 | 0.0010018 | 0.022583 | 0.033665 | 0.0086368 | -0.042045 | -0.0031274 | 0.010104 | 0.045776 | 0.027466 | 0.045776 | 0.082397 | 0.091553 | 0.059509 | -0.068665 | -0.018311 | 0.022888 | -0.1236 | 0.009155 | 0.018311 | 0.054932 | -0.032043 | 118.6066 | 118.4784 | -2.9846 | 118.5745 | 118.6295 | 0.15106 | -3.0304 | 118.602 | 118.515 | -3.067 | 118.5287 | 118.4235 | -0.091553 | -3.0579 | 118.6386 | 118.5928 | 118.5928 | -3.1448 | 118.5562 | 118.5654 | 118.5699 | -3.1082
3798.4844 | 121.6873 | -117.4988 | 4.0146 | 0.0054168 | 0.0013544 | 0.070654 | 0.032278 | -0.068041 | -0.031857 | -0.0011344 | 0.014954 | 0.025547 | 0.0067142 | -0.043541 | -0.010177 | 0.014377 | 0.07782 | 0.14191 | 0.17395 | 0.14191 | 0.064087 | 0.073242 | -0.032043 | 0.073242 | 0.1831 | 0.032043 | -0.032043 | -0.004578 | 0.09613 | 0.022888 | 117.572 | 117.4667 | -3.9505 | 117.6407 | 117.6407 | 0.17395 | -3.9368 | 117.5949 | 117.5217 | -4.0466 | 117.572 | 117.5308 | 0.009155 | -4.0192 | 117.5629 | 117.5766 | 117.6727 | -4.0466 | 117.4667 | 117.4942 | 117.6819 | -3.9917
3800.2344 | 121.8338 | -118.7119 | 2.861 | 0.013046 | 0.0034906 | 0.071081 | 0.028433 | -0.0674 | -0.029508 | -0.00049335 | 0.030213 | 0.033665 | 0.0084232 | -0.044395 | -0.0097498 | 0.011386 | 0.018311 | 0.041199 | 0.09613 | 0.10071 | 0.068665 | 0.07782 | -0.050354 | 0.004578 | 0.09613 | -0.009155 | -0.013733 | 0.009155 | 0.082397 | 0.027466 | 118.7897 | 118.6615 | -2.7924 | 118.7531 | 118.8126 | 0.15106 | -2.8427 | 118.7943 | 118.7393 | -2.8748 | 118.7164 | 118.7027 | -0.036621 | -2.8519 | 118.7805 | 118.7302 | 118.808 | -2.9114 | 118.6981 | 118.721 | 118.808 | -2.8336
3801.9688 | 121.6782 | -119.3481 | 2.1744 | 0.0054168 | 0.001568 | 0.074926 | 0.027152 | -0.065691 | -0.028012 | -0.00070715 | 0.0073242 | 0.032383 | 0.0069278 | -0.044181 | -0.0082544 | 0.011813 | 0.07782 | 0.13275 | 0.15564 | 0.16479 | 0.054932 | 0.07782 | -0.054932 | 0.059509 | 0.14648 | 0.013733 | -0.009155 | 0.004578 | 0.07782 | 0.009155 | 119.426 | 119.2932 | -2.1194 | 119.4809 | 119.5129 | 0.21973 | -2.0966 | 119.426 | 119.3573 | -2.1835 | 119.4077 | 119.3619 | 0.004578 | -2.1698 | 119.4031 | 119.426 | 119.5038 | -2.2293 | 119.339 | 119.3527 | 119.4946 | -2.1652
3803.7656 | 121.8063 | -118.9224 | 2.5406 | 0.0054168 | 0.0039178 | 0.06809 | 0.024802 | -0.068255 | -0.02139 | 0.00078825 | -0.0003053 | 0.033665 | 0.0082096 | -0.042686 | -0.0059046 | 0.012241 | 0.11444 | 0.11444 | 0.14191 | 0.16022 | 0.041199 | 0.082397 | -0.036621 | 0.091553 | 0.13275 | 0.009155 | -0.045776 | -0.009155 | 0.10071 | 0.032043 | 119.0048 | 118.8858 | -2.4994 | 119.0369 | 119.0826 | 0.19684 | -2.4261 | 119.0231 | 118.9545 | -2.5864 | 119.014 | 118.9316 | -0.022888 | -2.5497 | 118.9636 | 119.0369 | 119.0643 | -2.5772 | 118.8766 | 118.9133 | 119.0552 | -2.5085
3805.5625 | 121.7606 | -121.312 | 0.3891 | 0.0054168 | -0.00035461 | 0.069158 | 0.028647 | -0.069109 | -0.02609 | -0.00049335 | 0.0073242 | 0.033451 | 0.0086368 | -0.042686 | -0.0078272 | 0.010745 | -0.018311 | 0.013733 | 0.032043 | 0.059509 | 0.10071 | 0.054932 | -0.10529 | -0.036621 | 0.022888 | -0.10529 | 0.036621 | 0.041199 | 0.050354 | -0.013733 | 121.3669 | 121.2067 | -0.28839 | 121.3257 | 121.3715 | 0.16479 | -0.40741 | 121.3623 | 121.2982 | -0.35248 | 121.2753 | 121.2067 | -0.091553 | -0.3479 | 121.4127 | 121.2936 | 121.344 | -0.49438 | 121.3486 | 121.3531 | 121.3348 | -0.40283
3807.3594 | 121.8018 | -121.2891 | 0.3891 | 0.0054168 | -0.00014101 | 0.067663 | 0.027579 | -0.069537 | -0.02139 | -0.00049335 | 0.022583 | 0.03516 | 0.0086368 | -0.040977 | -0.0012048 | 0.0094635 | 0.07782 | 0.045776 | 0.073242 | 0.10529 | 0.10071 | 0.059509 | -0.082397 | 0.036621 | 0.07782 | -0.073242 | 0.013733 | 0.022888 | 0.059509 | -0.004578 | 121.3486 | 121.2067 | -0.28839 | 121.3348 | 121.3943 | 0.18768 | -0.31128 | 121.3486 | 121.2845 | -0.37537 | 121.3257 | 121.2158 | -0.068664 | -0.36621 | 121.3898 | 121.3669 | 121.3623 | -0.4715 | 121.3028 | 121.3119 | 121.3669 | -0.39368
3809.1719 | 121.8109 | -121.2936 | 0.39368 | -0.0098417 | -0.00014101 | 0.07044 | 0.026938 | -0.066973 | -0.023953 | 0.0022836 | -0.0003053 | 0.034733 | 0.0067142 | -0.0429 | -0.0074 | 0.012882 | 0.004578 | -0.009155 | 0.013733 | 0.086975 | 0.10071 | 0.041199 | -0.10071 | -0.018311 | 0.045776 | -0.10071 | 0.013733 | 0.036621 | 0.059509 | 0 | 121.3348 | 121.1929 | -0.29297 | 121.2845 | 121.3806 | 0.18768 | -0.3891 | 121.3531 | 121.2936 | -0.37994 | 121.2753 | 121.1929 | -0.10071 | -0.35706 | 121.3943 | 121.2982 | 121.3074 | -0.49439 | 121.3074 | 121.3303 | 121.3394 | -0.39368
3810.9688 | 121.8796 | -121.2753 | 0.3479 | 0.013046 | 0.0041314 | 0.069372 | 0.025229 | -0.068041 | -0.025662 | 0.0018564 | 0.014954 | 0.031956 | 0.007996 | -0.042259 | -0.0059046 | 0.013095 | 0.10986 | 0.11902 | 0.14191 | 0.15106 | 0.050354 | 0.07782 | -0.045776 | 0.086975 | 0.13733 | 0.022888 | -0.022888 | 0.004578 | 0.091553 | 0.041199 | 121.3531 | 121.2296 | -0.29755 | 121.3943 | 121.4264 | 0.19684 | -0.23804 | 121.3669 | 121.3165 | -0.37079 | 121.3623 | 121.2982 | -0.018311 | -0.34332 | 121.3257 | 121.3852 | 121.4172 | -0.39368 | 121.2524 | 121.2799 | 121.4127 | -0.3067
3812.75 | 121.8887 | -121.2753 | 0.37079 | 0.0054168 | 0.0030634 | 0.07044 | 0.024374 | -0.069109 | -0.021604 | 0.00057465 | 0.014954 | 0.034519 | 0.0088504 | -0.043327 | -0.0052636 | 0.013095 | 0.018311 | -0.013733 | 0.009155 | 0.068665 | 0.10071 | 0.041199 | -0.082397 | 0 | -0.009155 | -0.10986 | -0.004578 | 0.059509 | 0.073242 | -0.004578 | 121.3165 | 121.1929 | -0.27008 | 121.2616 | 121.344 | 0.15106 | -0.35248 | 121.3486 | 121.2708 | -0.37537 | 121.2753 | 121.1655 | -0.10529 | -0.31128 | 121.376 | 121.2936 | 121.2845 | -0.45319 | 121.2708 | 121.3348 | 121.2662 | -0.37537
3814.5469 | 121.8613 | -121.2845 | 0.40741 | 0.0054168 | 0.004345 | 0.071722 | 0.027579 | -0.068468 | -0.028226 | -6.615e-05 | 0.0073242 | 0.02982 | 0.0067142 | -0.043541 | -0.0086816 | 0.013309 | 0.064087 | 0.10071 | 0.12817 | 0.1236 | 0.064087 | 0.068665 | -0.045776 | 0.036621 | 0.10071 | -0.009155 | -0.032043 | -0.004578 | 0.10071 | -0.009155 | 121.3531 | 121.2387 | -0.34332 | 121.3852 | 121.4081 | 0.16937 | -0.34332 | 121.3852 | 121.2753 | -0.43945 | 121.3211 | 121.2753 | 0 | -0.41199 | 121.3486 | 121.3486 | 121.4127 | -0.45319 | 121.2524 | 121.2799 | 121.3852 | -0.41657
3816.2812 | 121.9208 | -121.2936 | 0.37994 | 0.0054168 | 0.001568 | 0.071294 | 0.029929 | -0.068041 | -0.028653 | -0.003057 | 0.014954 | 0.028111 | 0.007355 | -0.042259 | -0.0082544 | 0.012241 | 0.032043 | 0.082397 | 0.13275 | 0.1236 | 0.059509 | 0.082397 | -0.045776 | 0.045776 | 0.12817 | 0.022888 | -0.004578 | -0.004578 | 0.086975 | 0.004578 | 121.376 | 121.2479 | -0.32044 | 121.376 | 121.4172 | 0.16937 | -0.3479 | 121.3806 | 121.2982 | -0.38452 | 121.3394 | 121.3165 | 0.01831 | -0.38452 | 121.3531 | 121.3257 | 121.4264 | -0.42572 | 121.2891 | 121.2891 | 121.4218 | -0.37537
3818.0156 | 121.875 | -121.2982 | 0.41657 | 0.013046 | 0.0058404 | 0.071722 | 0.028433 | -0.068682 | -0.025876 | -6.615e-05 | 0.014954 | 0.031956 | 0.0071414 | -0.043541 | -0.0080408 | 0.011813 | 0.068665 | 0.07782 | 0.1236 | 0.11444 | 0.059509 | 0.09613 | -0.045776 | 0.022888 | 0.086975 | -0.013733 | -0.027466 | -0.013733 | 0.091553 | -0.009155 | 121.3943 | 121.2524 | -0.35706 | 121.376 | 121.4127 | 0.16022 | -0.3479 | 121.3898 | 121.2891 | -0.44403 | 121.3211 | 121.2845 | -0.004578 | -0.4303 | 121.3577 | 121.3669 | 121.4218 | -0.46234 | 121.2708 | 121.2845 | 121.3852 | -0.42572
3819.75 | 121.9025 | -121.2708 | 0.40283 | 0.0054168 | 0.0051996 | 0.07044 | 0.024802 | -0.065905 | -0.022458 | -0.00027975 | 0.022583 | 0.03217 | 0.0058596 | -0.043113 | -0.0044092 | 0.010959 | 0.1236 | 0.11444 | 0.15106 | 0.15106 | 0.036621 | 0.082397 | -0.041199 | 0.10986 | 0.13275 | 0.018311 | -0.022888 | -0.013733 | 0.082397 | 0.041199 | 121.3531 | 121.2296 | -0.36621 | 121.3852 | 121.4218 | 0.19226 | -0.27924 | 121.3531 | 121.312 | -0.42572 | 121.3806 | 121.2891 | -0.022888 | -0.41657 | 121.3074 | 121.3943 | 121.4218 | -0.44403 | 121.2479 | 121.257 | 121.4035 | -0.36163
3821.4844 | 121.7102 | -118.1259 | 3.5431 | -0.0022127 | 0.00071339 | 0.069158 | 0.026297 | -0.06975 | -0.019467 | 0.0014292 | 0.0073242 | 0.035801 | 0.0069278 | -0.042045 | -0.0031274 | 0.010532 | 0.086975 | 0.073242 | 0.073242 | 0.10529 | 0.07782 | 0.050354 | -0.073242 | 0.041199 | 0.059509 | -0.10071 | -0.004578 | 0.018311 | 0.059509 | 0 | 118.1763 | 118.0527 | -3.4653 | 118.1992 | 118.2312 | 0.17853 | -3.4561 | 118.1854 | 118.1259 | -3.5477 | 118.1671 | 118.0252 | -0.10071 | -3.5248 | 118.2037 | 118.2129 | 118.1992 | -3.6163 | 118.1213 | 118.1442 | 118.1854 | -3.5431
3823.2812 | 121.788 | -118.0573 | 3.598 | 0.0054168 | 7.2586e-05 | 0.071722 | 0.031851 | -0.06975 | -0.028012 | 0.00057465 | -0.0003053 | 0.030033 | 0.005646 | -0.044181 | -0.008468 | 0.015018 | 0.086975 | 0.16022 | 0.16937 | 0.15564 | 0.045776 | 0.059509 | -0.036621 | 0.068665 | 0.18768 | 0.022888 | -0.032043 | -0.022888 | 0.09613 | 0.013733 | 118.1168 | 118.0206 | -3.5522 | 118.2175 | 118.2129 | 0.19226 | -3.511 | 118.1534 | 118.071 | -3.6301 | 118.1259 | 118.0801 | 0.009155 | -3.6209 | 118.103 | 118.1442 | 118.2266 | -3.6346 | 118.0252 | 118.0344 | 118.2449 | -3.5843
3825 | 121.7926 | -121.3989 | 0.28839 | 0.013046 | -0.002918 | 0.066808 | 0.028006 | -0.067187 | -0.021604 | 0.00078825 | 0.014954 | 0.03516 | 0.0094912 | -0.041191 | -0.005691 | 0.010104 | 0.073242 | 0.041199 | 0.064087 | 0.11444 | 0.091553 | 0.050354 | -0.07782 | 0.036621 | 0.07782 | -0.073242 | 0.018311 | 0.041199 | 0.07782 | -0.009155 | 121.4493 | 121.3211 | -0.19684 | 121.4401 | 121.5134 | 0.19226 | -0.21515 | 121.4767 | 121.3898 | -0.27008 | 121.4355 | 121.3257 | -0.064087 | -0.24719 | 121.4905 | 121.4722 | 121.463 | -0.36621 | 121.4172 | 121.4401 | 121.4767 | -0.29755
3826.7812 | 121.7834 | -121.4401 | 0.31128 | -0.0022127 | -0.00078181 | 0.069799 | 0.024161 | -0.069537 | -0.022458 | 0.00207 | 0.0073242 | 0.034733 | 0.0067142 | -0.043327 | -0.0041956 | 0.012454 | 0.07782 | 0.045776 | 0.073242 | 0.11444 | 0.086975 | 0.073242 | -0.064087 | 0.018311 | 0.064087 | -0.10529 | 0.018311 | 0.022888 | 0.07782 | -0.018311 | 121.5134 | 121.376 | -0.2243 | 121.4859 | 121.5546 | 0.17853 | -0.23346 | 121.5179 | 121.4218 | -0.29297 | 121.4584 | 121.3348 | -0.086975 | -0.28839 | 121.5271 | 121.5179 | 121.5134 | -0.37537 | 121.4584 | 121.463 | 121.5042 | -0.32959
3828.5781 | 121.8842 | -121.4035 | 0.25635 | 0.0054168 | 0.0054132 | 0.072149 | 0.026083 | -0.069323 | -0.026944 | 0.0018564 | 0.0073242 | 0.031315 | 0.006287 | -0.044181 | -0.0041956 | 0.013736 | 0.086975 | 0.1236 | 0.15106 | 0.15106 | 0.045776 | 0.091553 | -0.036621 | 0.10529 | 0.15564 | 0.032043 | -0.045776 | -0.018311 | 0.086975 | 0.027466 | 121.4951 | 121.3669 | -0.21057 | 121.5271 | 121.5546 | 0.18768 | -0.16937 | 121.4905 | 121.431 | -0.30212 | 121.5088 | 121.4355 | 0.004577 | -0.27466 | 121.4493 | 121.4905 | 121.5546 | -0.29297 | 121.3577 | 121.3852 | 121.5591 | -0.22888
3830.375 | 121.843 | -121.4584 | 0.31128 | -0.0022127 | 0.0011408 | 0.070654 | 0.02822 | -0.068682 | -0.025235 | 0.00078825 | 0.0073242 | 0.033451 | 0.009064 | -0.045036 | -0.0074 | 0.013095 | -0.013733 | 0.009155 | 0.022888 | 0.068665 | 0.091553 | 0.041199 | -0.082397 | -0.045776 | 0.022888 | -0.10071 | 0.018311 | 0.027466 | 0.059509 | -0.041199 | 121.4996 | 121.376 | -0.21973 | 121.4676 | 121.5271 | 0.15106 | -0.32501 | 121.5179 | 121.4172 | -0.29297 | 121.4127 | 121.3577 | -0.059509 | -0.28381 | 121.55 | 121.4447 | 121.4813 | -0.39368 | 121.4767 | 121.4859 | 121.4813 | -0.35248
3832.1094 | 121.9391 | -121.4355 | 0.2655 | 0.020676 | 0.00049979 | 0.069585 | 0.025443 | -0.064623 | -0.023099 | 0.0010018 | 0.0073242 | 0.032383 | 0.0054324 | -0.043327 | -0.0048364 | 0.013309 | 0.013733 | 0.013733 | 0.022888 | 0.082397 | 0.086975 | 0.059509 | -0.059509 | 0.018311 | 0.068665 | -0.064087 | -0.009155 | 0.013733 | 0.068665 | 0 | 121.4951 | 121.376 | -0.17853 | 121.4493 | 121.5179 | 0.14191 | -0.25177 | 121.5042 | 121.4355 | -0.27466 | 121.4539 | 121.3715 | -0.064087 | -0.25177 | 121.5225 | 121.4493 | 121.4584 | -0.32501 | 121.4264 | 121.4493 | 121.5042 | -0.2655
3833.8906 | 121.9528 | -121.4447 | 0.25635 | 0.013046 | 0.001568 | 0.070654 | 0.029715 | -0.070605 | -0.030149 | -0.00092075 | 0.0073242 | 0.030247 | 0.0069278 | -0.043968 | -0.011245 | 0.012882 | 0.036621 | 0.073242 | 0.1236 | 0.12817 | 0.068665 | 0.082397 | -0.050354 | 0.041199 | 0.1236 | 0.009155 | 0.009155 | 0.009155 | 0.10529 | 0.013733 | 121.5271 | 121.3943 | -0.18768 | 121.5179 | 121.5729 | 0.17853 | -0.21973 | 121.55 | 121.4584 | -0.24719 | 121.4859 | 121.4539 | -0.004578 | -0.24719 | 121.5134 | 121.4813 | 121.5683 | -0.3067 | 121.4539 | 121.4539 | 121.5683 | -0.24262
3835.6406 | 121.9528 | -121.4493 | 0.25635 | 0.0054168 | 0.0026362 | 0.069158 | 0.026083 | -0.071459 | -0.022031 | -0.00070715 | 0.014954 | 0.034092 | 0.0082096 | -0.043541 | -0.0037684 | 0.010745 | 0.064087 | 0.050354 | 0.09613 | 0.11444 | 0.086975 | 0.07782 | -0.045776 | 0.07782 | 0.10071 | -0.009155 | -0.041199 | -0.004578 | 0.091553 | 0.032043 | 121.5271 | 121.4035 | -0.16937 | 121.4996 | 121.5637 | 0.16022 | -0.19226 | 121.5408 | 121.4813 | -0.29755 | 121.5271 | 121.4401 | -0.041198 | -0.26093 | 121.5363 | 121.5134 | 121.5454 | -0.30212 | 121.4081 | 121.4447 | 121.55 | -0.22431
3837.4375 | 121.8887 | -121.4859 | 0.28839 | 0.013046 | -0.0020636 | 0.069158 | 0.028006 | -0.068682 | -0.021817 | 0.0024972 | -0.0079343 | 0.033451 | 0.0065006 | -0.043968 | -0.0052636 | 0.011173 | 0.045776 | 0.032043 | 0.054932 | 0.10986 | 0.082397 | 0.050354 | -0.082397 | 0.013733 | 0.068665 | -0.07782 | 0.027466 | 0.027466 | 0.050354 | -0.009155 | 121.5363 | 121.4035 | -0.20599 | 121.5179 | 121.5958 | 0.19226 | -0.24262 | 121.5363 | 121.4767 | -0.26093 | 121.4996 | 121.4081 | -0.068665 | -0.26093 | 121.5683 | 121.5317 | 121.5408 | -0.37079 | 121.5134 | 121.5134 | 121.5546 | -0.29755
3839.2344 | 121.9116 | -121.4722 | 0.25635 | 0.0054168 | 0.0037042 | 0.070654 | 0.025656 | -0.069109 | -0.027799 | 0.0016428 | 0.0073242 | 0.03217 | 0.006287 | -0.041832 | -0.008468 | 0.013095 | 0.10529 | 0.13275 | 0.15564 | 0.15106 | 0.050354 | 0.09613 | -0.041199 | 0.068665 | 0.11444 | 0.004578 | -0.027466 | -0.009155 | 0.082397 | 0.027466 | 121.5683 | 121.431 | -0.20599 | 121.6049 | 121.6232 | 0.19226 | -0.15106 | 121.5546 | 121.4996 | -0.28381 | 121.5408 | 121.4767 | -0.022888 | -0.2655 | 121.5225 | 121.5775 | 121.6278 | -0.29755 | 121.4447 | 121.463 | 121.5866 | -0.22888
3841.0312 | 121.9437 | -121.4401 | 0.28381 | 0.013046 | 0.0017816 | 0.07279 | 0.030142 | -0.070605 | -0.028226 | -0.00070715 | 0.0073242 | 0.031315 | 0.0065006 | -0.043754 | -0.0088952 | 0.012027 | 0.10986 | 0.16479 | 0.15564 | 0.16022 | 0.073242 | 0.086975 | -0.041199 | 0.091553 | 0.1831 | 0.064087 | -0.022888 | -0.004578 | 0.09613 | 0.032043 | 121.5271 | 121.3989 | -0.21057 | 121.6049 | 121.6003 | 0.20142 | -0.17395 | 121.5363 | 121.4722 | -0.3067 | 121.5317 | 121.5042 | 0.032044 | -0.28839 | 121.5134 | 121.55 | 121.5958 | -0.32501 | 121.4172 | 121.4355 | 121.6232 | -0.25177
3842.8125 | 121.9574 | -121.4035 | 0.31128 | 0.013046 | 0.0037042 | 0.071081 | 0.025656 | -0.070391 | -0.02374 | 0.00078825 | 0.014954 | 0.03217 | 0.007355 | -0.044609 | -0.001632 | 0.011386 | 0.045776 | 0.041199 | 0.082397 | 0.10071 | 0.082397 | 0.068665 | -0.045776 | 0.073242 | 0.10986 | -0.004578 | -0.009155 | 0 | 0.07782 | 0.018311 | 121.4722 | 121.3577 | -0.22888 | 121.4447 | 121.5042 | 0.14648 | -0.2655 | 121.4813 | 121.4218 | -0.32043 | 121.4767 | 121.3989 | -0.022889 | -0.31128 | 121.4859 | 121.4493 | 121.4859 | -0.35705 | 121.3943 | 121.4035 | 121.5134 | -0.29297
3844.5469 | 121.9299 | -121.4127 | 0.32501 | 0.0054168 | 0.0051996 | 0.071722 | 0.024802 | -0.068468 | -0.023313 | 0.00014745 | 0.022583 | 0.031529 | 0.006287 | -0.044609 | -0.0065454 | 0.011813 | 0.10529 | 0.11902 | 0.15564 | 0.16479 | 0.050354 | 0.086975 | -0.036621 | 0.10529 | 0.1236 | 0 | -0.032043 | -0.027466 | 0.091553 | 0.027466 | 121.4996 | 121.376 | -0.27466 | 121.5317 | 121.5775 | 0.20142 | -0.21973 | 121.5042 | 121.4401 | -0.35706 | 121.5179 | 121.4127 | -0.027466 | -0.35248 | 121.463 | 121.5179 | 121.5683 | -0.36163 | 121.3806 | 121.3852 | 121.5363 | -0.29755
3846.3438 | 121.8521 | -121.4447 | 0.37994 | 0.013046 | 0.001568 | 0.071722 | 0.02587 | -0.068255 | -0.019254 | 0.0027108 | 0.0073242 | 0.034733 | 0.0075686 | -0.043113 | -0.001632 | 0.012454 | -0.004578 | -0.009155 | 0.009155 | 0.068665 | 0.10986 | 0.059509 | -0.07782 | -0.036621 | -0.022888 | -0.14648 | 0.013733 | 0.022888 | 0.054932 | -0.013733 | 121.5042 | 121.3669 | -0.27008 | 121.4355 | 121.5134 | 0.14649 | -0.38452 | 121.4996 | 121.431 | -0.36621 | 121.4081 | 121.2982 | -0.13275 | -0.35706 | 121.5546 | 121.4401 | 121.4539 | -0.45776 | 121.4584 | 121.4676 | 121.4218 | -0.39368
3848.1406 | 121.9803 | -121.3989 | 0.33417 | 0.013046 | 0.0022088 | 0.071722 | 0.032706 | -0.067614 | -0.031857 | 0.00057465 | 0.0073242 | 0.02982 | 0.007355 | -0.046745 | -0.0093226 | 0.015659 | 0.018311 | 0.073242 | 0.11444 | 0.11902 | 0.07782 | 0.07782 | -0.064087 | 0.027466 | 0.10986 | 0.009155 | -0.027466 | -0.009155 | 0.10986 | 0.027466 | 121.4767 | 121.3348 | -0.25635 | 121.4722 | 121.5179 | 0.18311 | -0.31586 | 121.5088 | 121.4264 | -0.36163 | 121.4264 | 121.4081 | -0.018311 | -0.34332 | 121.4767 | 121.4172 | 121.5134 | -0.39825 | 121.3715 | 121.3898 | 121.5088 | -0.3067
3849.9375 | 121.9528 | -121.4218 | 0.35706 | -0.0022127 | 0.006054 | 0.073217 | 0.02587 | -0.068041 | -0.026517 | -6.615e-05 | 0.022583 | 0.031742 | 0.006287 | -0.044395 | -0.006759 | 0.013736 | 0.10071 | 0.11444 | 0.15564 | 0.13733 | 0.050354 | 0.082397 | -0.027466 | 0.059509 | 0.11902 | 0.009155 | -0.009155 | -0.009155 | 0.09613 | 0.013733 | 121.5042 | 121.3943 | -0.3067 | 121.5363 | 121.5591 | 0.16479 | -0.25635 | 121.5179 | 121.4355 | -0.36621 | 121.4813 | 121.431 | -0.004578 | -0.36621 | 121.4722 | 121.5225 | 121.5775 | -0.38452 | 121.4127 | 121.4127 | 121.5408 | -0.34332
3851.6719 | 121.8613 | -121.4493 | 0.40741 | 0.013046 | -0.0020636 | 0.070654 | 0.031851 | -0.0674 | -0.024594 | -0.0024162 | 0.022583 | 0.033024 | 0.0094912 | -0.043754 | -0.0061182 | 0.012668 | 0.013733 | 0.009155 | 0.059509 | 0.091553 | 0.091553 | 0.050354 | -0.086975 | -0.027466 | 0.036621 | -0.10071 | 0.045776 | 0.032043 | 0.059509 | 0 | 121.4996 | 121.3623 | -0.31586 | 121.4584 | 121.5408 | 0.17853 | -0.39368 | 121.5088 | 121.4493 | -0.36163 | 121.4218 | 121.3486 | -0.10071 | -0.37537 | 121.5408 | 121.463 | 121.5088 | -0.49438 | 121.4951 | 121.4813 | 121.4859 | -0.40741
3853.4688 | 121.9757 | -121.3943 | 0.37079 | 0.0054168 | 0.004986 | 0.07279 | 0.029074 | -0.066546 | -0.027585 | -0.00027975 | 0.014954 | 0.029606 | 0.0043644 | -0.042472 | -0.0086816 | 0.012668 | 0.045776 | 0.059509 | 0.10529 | 0.10529 | 0.086975 | 0.059509 | -0.054932 | 0.013733 | 0.086975 | -0.013733 | -0.018311 | -0.004578 | 0.10071 | 0.013733 | 121.4539 | 121.3394 | -0.28381 | 121.4539 | 121.4996 | 0.16022 | -0.32501 | 121.4951 | 121.4081 | -0.3891 | 121.4081 | 121.3806 | -0.027466 | -0.37537 | 121.4813 | 121.4401 | 121.4996 | -0.42572 | 121.376 | 121.3898 | 121.4813 | -0.35706
3855.2031 | 121.8613 | -121.4355 | 0.3891 | 0.020676 | -0.002918 | 0.069372 | 0.027792 | -0.068041 | -0.018399 | 0.0010018 | 0.014954 | 0.034947 | 0.0084232 | -0.040763 | -0.0029138 | 0.012027 | 0.059509 | 0.050354 | 0.059509 | 0.09613 | 0.091553 | 0.068665 | -0.068665 | 0.022888 | 0.032043 | -0.10986 | 0 | 0.027466 | 0.059509 | -0.013733 | 121.5042 | 121.3669 | -0.29755 | 121.4859 | 121.5317 | 0.16479 | -0.32959 | 121.4951 | 121.4218 | -0.3891 | 121.4584 | 121.3257 | -0.09613 | -0.36163 | 121.5271 | 121.4951 | 121.4951 | -0.45776 | 121.4355 | 121.463 | 121.4676 | -0.40283
3857 | 121.9208 | -121.4447 | 0.3891 | 0.0054168 | -0.0016364 | 0.068304 | 0.031424 | -0.067187 | -0.024167 | 0.0024972 | 0.0073242 | 0.033238 | 0.0086368 | -0.043541 | -0.0054772 | 0.012027 | 0.009155 | 0.009155 | 0.032043 | 0.091553 | 0.09613 | 0.041199 | -0.10986 | -0.009155 | 0.059509 | -0.10071 | 0.009155 | 0.041199 | 0.059509 | -0.018311 | 121.4859 | 121.3348 | -0.29297 | 121.4539 | 121.5363 | 0.20142 | -0.37994 | 121.5042 | 121.4264 | -0.37994 | 121.4355 | 121.344 | -0.082397 | -0.3479 | 121.5408 | 121.4539 | 121.4767 | -0.49896 | 121.4539 | 121.4859 | 121.5042 | -0.40741
3858.7969 | 121.9345 | -121.4447 | 0.37079 | 0.0054168 | -0.0016364 | 0.072149 | 0.02886 | -0.070605 | -0.027371 | 0.00014745 | 0.030213 | 0.030247 | 0.007996 | -0.044822 | -0.0076136 | 0.014804 | 0.09613 | 0.14648 | 0.15106 | 0.15564 | 0.059509 | 0.091553 | -0.054932 | 0.064087 | 0.16937 | 0.022888 | -0.018311 | -0.013733 | 0.10071 | 0.027466 | 121.5363 | 121.3898 | -0.31128 | 121.5912 | 121.6003 | 0.21057 | -0.27466 | 121.5454 | 121.4722 | -0.3891 | 121.5088 | 121.4676 | -0.004578 | -0.38452 | 121.5042 | 121.5408 | 121.5958 | -0.42572 | 121.4264 | 121.431 | 121.6141 | -0.34332
3860.5625 | 121.9574 | -121.4401 | 0.39825 | 0.020676 | 0.0022088 | 0.070013 | 0.027152 | -0.070605 | -0.028012 | 0.00014745 | 0.0073242 | 0.03217 | 0.0075686 | -0.041618 | -0.0088952 | 0.013095 | 0.082397 | 0.07782 | 0.12817 | 0.1236 | 0.054932 | 0.091553 | -0.050354 | 0.041199 | 0.10986 | -0.013733 | -0.018311 | -0.009155 | 0.082397 | 0.009155 | 121.5317 | 121.3898 | -0.34332 | 121.5179 | 121.5637 | 0.17395 | -0.31586 | 121.5225 | 121.4493 | -0.41657 | 121.4813 | 121.4264 | -0.022888 | -0.40741 | 121.4951 | 121.5225 | 121.5683 | -0.44861 | 121.4218 | 121.431 | 121.55 | -0.3891
3862.3594 | 121.9208 | -121.4218 | 0.39825 | 0.0054168 | -0.00099541 | 0.069372 | 0.030783 | -0.069323 | -0.022885 | -0.00049335 | -0.0079343 | 0.03281 | 0.0094912 | -0.042686 | -0.0069726 | 0.010532 | 0.004578 | -0.013733 | 0.022888 | 0.073242 | 0.12817 | 0.045776 | -0.091553 | -0.036621 | 0.022888 | -0.11444 | 0.027466 | 0.032043 | 0.045776 | -0.022888 | 121.4676 | 121.3303 | -0.27008 | 121.4081 | 121.4951 | 0.16479 | -0.39368 | 121.4676 | 121.3989 | -0.37079 | 121.3852 | 121.3074 | -0.091553 | -0.36621 | 121.55 | 121.4264 | 121.4447 | -0.48981 | 121.4493 | 121.4539 | 121.4447 | -0.42114
3864.0781 | 121.9986 | -121.4081 | 0.38452 | 0.0054168 | 0.0051996 | 0.070654 | 0.02822 | -0.068041 | -0.025022 | -0.00092075 | 0.0073242 | 0.031315 | 0.0058596 | -0.044609 | -0.0037684 | 0.013736 | 0.10529 | 0.13733 | 0.14648 | 0.14191 | 0.054932 | 0.10529 | -0.018311 | 0.09613 | 0.14191 | 0.009155 | -0.041199 | -0.009155 | 0.10529 | 0.041199 | 121.5134 | 121.3898 | -0.32959 | 121.5454 | 121.55 | 0.16022 | -0.27924 | 121.5134 | 121.4493 | -0.42572 | 121.5042 | 121.4172 | -0.032044 | -0.39368 | 121.463 | 121.5134 | 121.5546 | -0.40283 | 121.3669 | 121.3989 | 121.55 | -0.34332
3865.8594 | 121.9345 | -121.4539 | 0.40283 | 0.0054168 | -0.0012092 | 0.070654 | 0.02822 | -0.066973 | -0.024594 | -0.00092075 | -0.0003053 | 0.034947 | 0.0071414 | -0.044395 | -0.006759 | 0.010745 | -0.004578 | 0.004578 | 0.022888 | 0.064087 | 0.09613 | 0.036621 | -0.091553 | -0.041199 | 0.022888 | -0.1236 | 0.032043 | 0.045776 | 0.07782 | -0.009155 | 121.4905 | 121.3623 | -0.3067 | 121.4584 | 121.5179 | 0.15564 | -0.40741 | 121.5317 | 121.4447 | -0.37079 | 121.4127 | 121.3303 | -0.11444 | -0.35706 | 121.55 | 121.4493 | 121.4767 | -0.49439 | 121.4859 | 121.4996 | 121.4767 | -0.41199
3867.6562 | 121.9894 | -121.431 | 0.37994 | -0.0098417 | 0.003277 | 0.069372 | 0.024161 | -0.068255 | -0.025876 | 0.0012154 | -0.0003053 | 0.03217 | 0.005646 | -0.043754 | -0.005691 | 0.011173 | 0.11902 | 0.12817 | 0.15564 | 0.14648 | 0.050354 | 0.068665 | -0.027466 | 0.082397 | 0.14191 | 0.022888 | -0.018311 | -0.013733 | 0.10529 | 0.032043 | 121.4996 | 121.4035 | -0.32959 | 121.5591 | 121.5775 | 0.17395 | -0.26093 | 121.5363 | 121.463 | -0.39826 | 121.5134 | 121.4539 | -0.009155 | -0.39368 | 121.4813 | 121.55 | 121.5866 | -0.40741 | 121.4127 | 121.4172 | 121.5729 | -0.3479
3869.3906 | 121.9574 | -121.4264 | 0.39825 | -0.0022127 | -0.0016364 | 0.068731 | 0.028647 | -0.0674 | -0.021176 | -0.00049335 | 0.022583 | 0.035801 | 0.007355 | -0.041618 | -0.0063318 | 0.010745 | 0.041199 | 0.018311 | 0.036621 | 0.10529 | 0.10071 | 0.064087 | -0.09613 | 0.032043 | 0.068665 | -0.073242 | 0.018311 | 0.036621 | 0.050354 | 0 | 121.4905 | 121.3303 | -0.29755 | 121.4447 | 121.5317 | 0.20142 | -0.35706 | 121.4767 | 121.4264 | -0.37994 | 121.4584 | 121.3532 | -0.073242 | -0.36163 | 121.5271 | 121.4676 | 121.463 | -0.49438 | 121.4447 | 121.463 | 121.4951 | -0.39825
3871.1875 | 121.9666 | -121.431 | 0.36621 | 0.0054168 | 0.004345 | 0.067663 | 0.025656 | -0.068468 | -0.025022 | -0.00092075 | 0.0073242 | 0.03516 | 0.0077822 | -0.042259 | -0.0061182 | 0.013095 | 0.009155 | -0.041199 | 0 | 0.073242 | 0.11444 | 0.059509 | -0.073242 | -0.032043 | -0.004578 | -0.1236 | 0.027466 | 0.032043 | 0.059509 | -0.022888 | 121.4905 | 121.3577 | -0.25177 | 121.3898 | 121.5042 | 0.14648 | -0.35706 | 121.4905 | 121.4081 | -0.33875 | 121.3989 | 121.3074 | -0.10071 | -0.33417 | 121.5454 | 121.4401 | 121.431 | -0.43945 | 121.4584 | 121.463 | 121.4264 | -0.3891
3872.9844 | 122.0306 | -121.4127 | 0.37079 | 0.013046 | 0.008404 | 0.071081 | 0.025443 | -0.067828 | -0.024594 | 0.0029244 | 0.0073242 | 0.032597 | 0.0050052 | -0.043754 | -0.0061182 | 0.0116 | 0.10529 | 0.11444 | 0.13733 | 0.16479 | 0.059509 | 0.086975 | -0.032043 | 0.082397 | 0.1236 | 0.022888 | -0.027466 | 0.004578 | 0.10071 | 0.018311 | 121.4996 | 121.3806 | -0.31128 | 121.5271 | 121.5775 | 0.19684 | -0.2655 | 121.5134 | 121.431 | -0.39825 | 121.4951 | 121.4355 | 0.004577 | -0.36621 | 121.4722 | 121.5179 | 121.55 | -0.40283 | 121.3852 | 121.4172 | 121.5363 | -0.35248
3874.7031 | 122.0535 | -121.431 | 0.36163 | 0.0054168 | 0.0045588 | 0.074285 | 0.029074 | -0.068682 | -0.02844 | -0.0019888 | 0.014954 | 0.027897 | 0.007355 | -0.04525 | -0.0086816 | 0.01395 | 0.073242 | 0.11444 | 0.14648 | 0.14191 | 0.059509 | 0.068665 | -0.045776 | 0.045776 | 0.16479 | 0.041199 | -0.022888 | -0.018311 | 0.09613 | 0.013733 | 121.4996 | 121.3852 | -0.30212 | 121.5454 | 121.5729 | 0.18768 | -0.28839 | 121.5271 | 121.4447 | -0.38452 | 121.4767 | 121.4722 | 0.027466 | -0.37994 | 121.4905 | 121.5042 | 121.5775 | -0.40741 | 121.4081 | 121.4127 | 121.5958 | -0.3479
3876.5 | 121.9208 | -121.4813 | 0.39368 | 0.0054168 | 0.0011408 | 0.071508 | 0.026083 | -0.066973 | -0.020749 | -0.0015616 | 0.014954 | 0.033879 | 0.0071414 | -0.044395 | -0.003341 | 0.012882 | 0.004578 | -0.045776 | 0 | 0.064087 | 0.091553 | 0.059509 | -0.064087 | -0.041199 | -0.022888 | -0.13275 | 0.018311 | 0.041199 | 0.064087 | -0.013733 | 121.5408 | 121.4172 | -0.30212 | 121.4355 | 121.5454 | 0.12817 | -0.3891 | 121.5454 | 121.4676 | -0.37537 | 121.4401 | 121.3486 | -0.11902 | -0.35248 | 121.5729 | 121.4859 | 121.4813 | -0.45776 | 121.4996 | 121.5225 | 121.4584 | -0.40741
3878.2969 | 122.0352 | -121.4172 | 0.37537 | 0.0054168 | 0.0056268 | 0.071722 | 0.029715 | -0.067614 | -0.025235 | 0.00014745 | 0.0073242 | 0.031956 | 0.006287 | -0.043968 | -0.0061182 | 0.011813 | 0.10986 | 0.11902 | 0.14648 | 0.16022 | 0.054932 | 0.091553 | -0.027466 | 0.073242 | 0.14191 | 0.018311 | -0.018311 | -0.004578 | 0.086975 | 0.022888 | 121.5088 | 121.3898 | -0.32043 | 121.5363 | 121.5775 | 0.18768 | -0.2655 | 121.5042 | 121.4401 | -0.39368 | 121.4905 | 121.4355 | -0.004577 | -0.37994 | 121.4722 | 121.5271 | 121.5637 | -0.40283 | 121.3989 | 121.4127 | 121.5591 | -0.35248
3880.0156 | 122.0444 | -121.4355 | 0.3891 | 0.0054168 | 0.004345 | 0.069799 | 0.02587 | -0.070177 | -0.021604 | 0.0022836 | 0.014954 | 0.034733 | 0.0086368 | -0.041404 | -0.0069726 | 0.012882 | 0.013733 | -0.018311 | 0.032043 | 0.059509 | 0.10529 | 0.050354 | -0.082397 | -0.004578 | 0.009155 | -0.086975 | 0.009155 | 0.027466 | 0.064087 | 0.004578 | 121.4859 | 121.3531 | -0.28381 | 121.4172 | 121.4951 | 0.14191 | -0.37537 | 121.4996 | 121.4401 | -0.37994 | 121.431 | 121.3486 | -0.091553 | -0.36163 | 121.5408 | 121.4493 | 121.4676 | -0.4715 | 121.4447 | 121.463 | 121.4447 | -0.38452
3881.7969 | 121.9299 | -121.4584 | 0.41199 | 0.013046 | -0.0027044 | 0.071081 | 0.028433 | -0.068896 | -0.022458 | 0.0016428 | -0.0003053 | 0.035801 | 0.0086368 | -0.043327 | -0.0044092 | 0.011386 | 0.013733 | 0 | 0.018311 | 0.082397 | 0.086975 | 0.050354 | -0.073242 | -0.036621 | -0.004578 | -0.15106 | 0.009155 | 0.036621 | 0.059509 | -0.009155 | 121.5088 | 121.3852 | -0.32501 | 121.4584 | 121.5408 | 0.15564 | -0.39825 | 121.5179 | 121.4493 | -0.40283 | 121.4218 | 121.3074 | -0.14191 | -0.37537 | 121.5454 | 121.4722 | 121.4767 | -0.48523 | 121.4676 | 121.4951 | 121.4539 | -0.42114
3883.5938 | 121.8567 | -119.6182 | 2.2202 | 0.0054168 | -0.00185 | 0.067876 | 0.02822 | -0.069109 | -0.022885 | 0.0010018 | 0.014954 | 0.035374 | 0.0082096 | -0.044609 | -0.0035546 | 0.014163 | -0.018311 | -0.004578 | 0.013733 | 0.07782 | 0.10071 | 0.041199 | -0.07782 | -0.041199 | 0.004578 | -0.13733 | 0.018311 | 0.045776 | 0.050354 | -0.009155 | 119.6594 | 119.5404 | -2.1194 | 119.6136 | 119.696 | 0.15564 | -2.2385 | 119.6686 | 119.6091 | -2.2018 | 119.577 | 119.4809 | -0.12817 | -2.1744 | 119.7189 | 119.5999 | 119.632 | -2.298 | 119.6365 | 119.664 | 119.6228 | -2.2293
3885.4062 | 121.9894 | -116.2079 | 5.5527 | 0.0054168 | 0.00049979 | 0.070654 | 0.029929 | -0.068896 | -0.028012 | 0.0014292 | 0.0073242 | 0.031529 | 0.0082096 | -0.042259 | -0.011031 | 0.012027 | 0.022888 | 0.059509 | 0.086975 | 0.11444 | 0.068665 | 0.045776 | -0.068665 | -0.059509 | 0.054932 | -0.082397 | 0.009155 | 0.032043 | 0.050354 | -0.022888 | 116.2537 | 116.1392 | -5.484 | 116.2674 | 116.3223 | 0.18311 | -5.5298 | 116.2582 | 116.185 | -5.5435 | 116.1484 | 116.1255 | -0.059509 | -5.5206 | 116.2766 | 116.2308 | 116.2949 | -5.6213 | 116.217 | 116.2399 | 116.2628 | -5.5756
3887.1406 | 122.0261 | -116.2811 | 5.5115 | 0.0054168 | 0.00092719 | 0.069158 | 0.027365 | -0.065264 | -0.023526 | -0.001348 | 0.014954 | 0.035588 | 0.007355 | -0.042472 | -0.0065454 | 0.011813 | 0.013733 | -0.013733 | 0.032043 | 0.09613 | 0.10529 | 0.050354 | -0.10071 | -0.027466 | 0.036621 | -0.10071 | 0.027466 | 0.036621 | 0.041199 | -0.018311 | 116.3315 | 116.1804 | -5.4062 | 116.2674 | 116.3773 | 0.19684 | -5.4977 | 116.3223 | 116.2628 | -5.484 | 116.2537 | 116.1804 | -0.082397 | -5.4749 | 116.3864 | 116.2949 | 116.3132 | -5.6122 | 116.3086 | 116.3177 | 116.3177 | -5.5298
3888.9219 | 122.0078 | -118.4463 | 3.3966 | 0.0054168 | 7.2586e-05 | 0.072576 | 0.02822 | -0.067614 | -0.02908 | 0.00078825 | 0.0073242 | 0.03217 | 0.0065006 | -0.042686 | -0.0074 | 0.013522 | 0.050354 | 0.091553 | 0.086975 | 0.11444 | 0.086975 | 0.068665 | -0.059509 | -0.036621 | 0.064087 | -0.086975 | 0 | 0.050354 | 0.068665 | 0 | 118.515 | 118.3868 | -3.3096 | 118.5379 | 118.5608 | 0.17395 | -3.3463 | 118.515 | 118.4463 | -3.3966 | 118.4097 | 118.3594 | -0.086975 | -3.3463 | 118.5333 | 118.4967 | 118.5333 | -3.4561 | 118.4463 | 118.4967 | 118.5104 | -3.3966
3890.7188 | 121.9574 | -118.5928 | 3.2867 | 0.013046 | -0.00035461 | 0.068731 | 0.027579 | -0.066119 | -0.020535 | 0.00078825 | 0.014954 | 0.034092 | 0.009064 | -0.040123 | -0.0037684 | 0.010745 | 0.050354 | 0.032043 | 0.059509 | 0.09613 | 0.086975 | 0.059509 | -0.086975 | -0.004578 | 0.032043 | -0.09613 | 0.013733 | 0.018311 | 0.064087 | -0.009155 | 118.6523 | 118.5059 | -3.1998 | 118.6249 | 118.689 | 0.1831 | -3.2364 | 118.6569 | 118.5837 | -3.273 | 118.5883 | 118.4967 | -0.086975 | -3.2684 | 118.6798 | 118.6432 | 118.6523 | -3.3737 | 118.6066 | 118.6111 | 118.6249 | -3.2959
3892.5156 | 122.0993 | -119.5679 | 2.2385 | 0.013046 | 0.0051996 | 0.069799 | 0.025015 | -0.068255 | -0.027799 | 0.0018564 | 0.0073242 | 0.032597 | 0.009064 | -0.043754 | -0.0071862 | 0.014377 | 0.086975 | 0.11902 | 0.13733 | 0.15564 | 0.059509 | 0.086975 | -0.027466 | 0.082397 | 0.1236 | 0.022888 | -0.041199 | -0.013733 | 0.10071 | 0.018311 | 119.6548 | 119.5404 | -2.179 | 119.6869 | 119.7235 | 0.18311 | -2.1515 | 119.6686 | 119.5862 | -2.2797 | 119.6503 | 119.5908 | 0.004577 | -2.2522 | 119.6274 | 119.6548 | 119.7052 | -2.2659 | 119.5267 | 119.5541 | 119.6915 | -2.2202
3894.2344 | 122.1313 | -119.5541 | 2.2751 | 0.013046 | 0.0024224 | 0.069799 | 0.026083 | -0.069537 | -0.024808 | 0.00207 | 0.014954 | 0.030888 | 0.0054324 | -0.04055 | -0.0059046 | 0.010532 | 0.073242 | 0.054932 | 0.10071 | 0.13733 | 0.064087 | 0.09613 | -0.059509 | 0.07782 | 0.11444 | 0.004578 | -0.027466 | -0.013733 | 0.10529 | 0.027466 | 119.6503 | 119.4946 | -2.211 | 119.6091 | 119.6915 | 0.19684 | -2.2018 | 119.6594 | 119.5816 | -2.3026 | 119.632 | 119.5587 | -0.022888 | -2.2888 | 119.6182 | 119.6274 | 119.6548 | -2.3346 | 119.5267 | 119.5404 | 119.6686 | -2.2476
3896.0312 | 122.081 | -119.664 | 2.1606 | 0.0054168 | 0.0051996 | 0.07044 | 0.028006 | -0.068041 | -0.025022 | 0.0018564 | 0.014954 | 0.031956 | 0.0075686 | -0.043113 | -0.0069726 | 0.011813 | 0.09613 | 0.10071 | 0.15106 | 0.15106 | 0.064087 | 0.09613 | -0.045776 | 0.082397 | 0.13733 | 0.004578 | -0.032043 | -0.004578 | 0.10071 | 0.041199 | 119.7601 | 119.6182 | -2.0966 | 119.7647 | 119.8151 | 0.19684 | -2.0645 | 119.7647 | 119.7052 | -2.1927 | 119.7464 | 119.6686 | -0.036621 | -2.1652 | 119.7281 | 119.7601 | 119.8151 | -2.2064 | 119.632 | 119.6594 | 119.8013 | -2.1194
3897.7656 | 122.0352 | -119.7784 | 2.1057 | -0.0022127 | 0.00071339 | 0.067022 | 0.027365 | -0.068682 | -0.024381 | 0.00078825 | 0.0073242 | 0.034306 | 0.007355 | -0.043541 | -0.0065454 | 0.0086091 | 0.045776 | 0.009155 | 0.050354 | 0.10071 | 0.09613 | 0.054932 | -0.07782 | 0.004578 | 0.064087 | -0.09613 | 0.027466 | 0.036621 | 0.073242 | -0.009155 | 119.8334 | 119.7006 | -2.0096 | 119.7876 | 119.8791 | 0.17853 | -2.0599 | 119.8517 | 119.7693 | -2.0782 | 119.783 | 119.6823 | -0.086975 | -2.0691 | 119.8746 | 119.8242 | 119.8288 | -2.1835 | 119.8059 | 119.8151 | 119.8425 | -2.1149
3899.5625 | 122.0718 | -119.7006 | 2.179 | 0.013046 | 0.004986 | 0.073217 | 0.026511 | -0.069964 | -0.031644 | -0.001348 | 0.0073242 | 0.028538 | 0.0054324 | -0.042259 | -0.0080408 | 0.012241 | 0.032043 | 0.050354 | 0.09613 | 0.10529 | 0.064087 | 0.068665 | -0.036621 | 0.004578 | 0.086975 | -0.022888 | -0.004578 | 0.013733 | 0.086975 | 0.009155 | 119.7693 | 119.664 | -2.1149 | 119.751 | 119.8059 | 0.14191 | -2.1469 | 119.7876 | 119.7098 | -2.1835 | 119.7052 | 119.6777 | -0.032043 | -2.1652 | 119.7647 | 119.7327 | 119.7968 | -2.2156 | 119.696 | 119.7144 | 119.7876 | -2.1698
3901.3438 | 122.0764 | -119.6686 | 2.211 | 0.0054168 | 0.001568 | 0.07044 | 0.026938 | -0.070177 | -0.026303 | -0.0017752 | 0.0073242 | 0.030033 | 0.0082096 | -0.042472 | -0.006759 | 0.012241 | 0.11444 | 0.13733 | 0.15564 | 0.14648 | 0.054932 | 0.07782 | -0.036621 | 0.064087 | 0.1831 | 0.036621 | -0.036621 | -0.009155 | 0.10071 | 0.018311 | 119.7464 | 119.632 | -2.1561 | 119.8059 | 119.8151 | 0.18311 | -2.0966 | 119.7693 | 119.6869 | -2.2476 | 119.7327 | 119.7052 | 0.01831 | -2.2202 | 119.7235 | 119.783 | 119.8242 | -2.2476 | 119.632 | 119.6594 | 119.8517 | -2.1927
3903.0781 | 121.9803 | -119.8288 | 2.1149 | 0.013046 | -0.0039862 | 0.066595 | 0.029288 | -0.067614 | -0.019254 | 0.0012154 | -0.0003053 | 0.033879 | 0.0082096 | -0.040336 | -0.0037684 | 0.010745 | 0.09613 | 0.10529 | 0.045776 | 0.10071 | 0.082397 | 0.054932 | -0.059509 | 0.032043 | 0.050354 | -0.09613 | 0.004578 | 0.032043 | 0.054932 | -0.009155 | 119.8837 | 119.7693 | -2.0325 | 119.9341 | 119.9295 | 0.16022 | -2.0187 | 119.8837 | 119.8196 | -2.1103 | 119.8608 | 119.7327 | -0.086975 | -2.0828 | 119.9112 | 119.9249 | 119.8746 | -2.1744 | 119.8334 | 119.8608 | 119.8791 | -2.124
3904.8594 | 122.0673 | -119.6732 | 2.2568 | 0.013046 | 0.0056268 | 0.072363 | 0.024374 | -0.0721 | -0.029935 | -6.615e-05 | 0.014954 | 0.031101 | 0.0052188 | -0.042259 | -0.0080408 | 0.014377 | 0.073242 | 0.082397 | 0.10986 | 0.10986 | 0.064087 | 0.07782 | -0.027466 | 0.009155 | 0.10071 | -0.022888 | -0.013733 | 0 | 0.09613 | 0.013733 | 119.751 | 119.6457 | -2.1927 | 119.7556 | 119.783 | 0.13733 | -2.1835 | 119.7693 | 119.6869 | -2.2705 | 119.6823 | 119.6503 | -0.036621 | -2.2568 | 119.7372 | 119.7464 | 119.783 | -2.2842 | 119.6594 | 119.6732 | 119.7739 | -2.243
3906.6562 | 122.0581 | -119.5999 | 2.2751 | 0.0054168 | 0.00071339 | 0.068945 | 0.024802 | -0.070177 | -0.01904 | 0.0012154 | 0.0073242 | 0.034733 | 0.0071414 | -0.039268 | -0.00505 | 0.012241 | 0 | -0.036621 | -0.004578 | 0.054932 | 0.086975 | 0.041199 | -0.091553 | -0.022888 | -0.022888 | -0.12817 | 0.022888 | 0.045776 | 0.045776 | -0.004578 | 119.6411 | 119.5084 | -2.1881 | 119.5633 | 119.6548 | 0.14649 | -2.2751 | 119.6457 | 119.5953 | -2.2522 | 119.577 | 119.4717 | -0.1236 | -2.2293 | 119.6869 | 119.5999 | 119.5953 | -2.3666 | 119.6228 | 119.6457 | 119.577 | -2.2797
3908.3906 | 122.1497 | -119.8883 | 1.9638 | 0.0054168 | 0.0039178 | 0.071722 | 0.027365 | -0.068682 | -0.031217 | -0.0011344 | 0.0073242 | 0.030247 | 0.0071414 | -0.042472 | -0.008468 | 0.013309 | 0.059509 | 0.07782 | 0.12817 | 0.12817 | 0.073242 | 0.068665 | -0.045776 | 0.064087 | 0.13275 | 0.013733 | -0.004578 | 0.004578 | 0.10071 | 0.022888 | 119.957 | 119.8425 | -1.8906 | 119.9661 | 120.0165 | 0.17395 | -1.9043 | 119.989 | 119.9112 | -1.9684 | 119.9524 | 119.902 | -0.009155 | -1.9592 | 119.9615 | 119.9478 | 120.0165 | -2.0096 | 119.8837 | 119.8929 | 120.0211 | -1.9409
3910.1719 | 122.1268 | -120.0027 | 1.8448 | 0.0054168 | 0.0037042 | 0.069372 | 0.026083 | -0.067614 | -0.022458 | -0.00070715 | 0.022583 | 0.033451 | 0.0052188 | -0.040977 | -0.0052636 | 0.010745 | 0.073242 | 0.054932 | 0.10529 | 0.1236 | 0.07782 | 0.10529 | -0.059509 | 0.091553 | 0.11444 | 0 | -0.036621 | -0.004578 | 0.091553 | 0.032043 | 120.108 | 119.9432 | -1.767 | 120.0577 | 120.1263 | 0.1831 | -1.7715 | 120.0943 | 120.0348 | -1.8814 | 120.0943 | 120.0027 | -0.032043 | -1.8494 | 120.0806 | 120.076 | 120.108 | -1.9043 | 119.9661 | 119.9982 | 120.1172 | -1.8127
3911.8906 | 122.1359 | -120.1126 | 1.767 | -0.0022127 | 0.0039178 | 0.071081 | 0.025443 | -0.068255 | -0.023099 | 0.0022836 | 0.014954 | 0.031956 | 0.0050052 | -0.041832 | -0.0029138 | 0.011386 | 0.086975 | 0.07782 | 0.10529 | 0.13275 | 0.059509 | 0.07782 | -0.045776 | 0.073242 | 0.1236 | 0 | -0.027466 | 0.004578 | 0.10071 | 0.009155 | 120.1904 | 120.0668 | -1.7075 | 120.1904 | 120.2454 | 0.17853 | -1.68 | 120.2133 | 120.1218 | -1.7944 | 120.1859 | 120.1126 | -0.009155 | -1.7624 | 120.1721 | 120.1996 | 120.2179 | -1.8127 | 120.0851 | 120.1172 | 120.2362 | -1.7578
3913.6875 | 122.113 | -120.0989 | 1.7715 | 0.0054168 | 0.0058404 | 0.070867 | 0.025015 | -0.0674 | -0.02374 | 0.0012154 | 0.014954 | 0.031956 | 0.0077822 | -0.044822 | -0.003982 | 0.013522 | 0.11902 | 0.12817 | 0.14191 | 0.16479 | 0.064087 | 0.082397 | -0.013733 | 0.11444 | 0.1236 | 0.013733 | -0.032043 | 0 | 0.10529 | 0.032043 | 120.1813 | 120.0851 | -1.7075 | 120.2271 | 120.2637 | 0.17853 | -1.6525 | 120.2042 | 120.1309 | -1.8036 | 120.2133 | 120.1126 | -0.01831 | -1.7715 | 120.163 | 120.2179 | 120.2408 | -1.7853 | 120.0668 | 120.0989 | 120.2225 | -1.7395
3915.4844 | 122.1039 | -120.0394 | 1.8631 | 0.0054168 | 0.004345 | 0.07279 | 0.029715 | -0.0674 | -0.027585 | -0.0015616 | 0.022583 | 0.032383 | 0.0071414 | -0.0429 | -0.0099634 | 0.012882 | 0.050354 | 0.054932 | 0.10529 | 0.10986 | 0.07782 | 0.082397 | -0.050354 | 0.032043 | 0.086975 | -0.027466 | -0.022888 | 0.018311 | 0.082397 | -0.004578 | 120.1218 | 119.989 | -1.7853 | 120.0943 | 120.1492 | 0.16022 | -1.8127 | 120.1218 | 120.0348 | -1.886 | 120.0714 | 120.0119 | -0.022888 | -1.8448 | 120.1172 | 120.0897 | 120.1447 | -1.9135 | 120.0165 | 120.0577 | 120.1263 | -1.8677
3917.2969 | 121.9803 | -120.0989 | 1.8951 | 0.0054168 | -0.00078181 | 0.071722 | 0.028433 | -0.068041 | -0.027371 | -6.615e-05 | 0.0073242 | 0.033451 | 0.0099186 | -0.042686 | -0.0074 | 0.011813 | 0.050354 | 0.050354 | 0.068665 | 0.10071 | 0.082397 | 0.059509 | -0.064087 | -0.041199 | 0.045776 | -0.086975 | 0.027466 | 0.054932 | 0.045776 | -0.036621 | 120.1584 | 120.0348 | -1.8127 | 120.1492 | 120.1996 | 0.1648 | -1.8448 | 120.1447 | 120.0623 | -1.8677 | 120.0577 | 120.0119 | -0.050354 | -1.8402 | 120.1813 | 120.1492 | 120.1675 | -1.9592 | 120.1263 | 120.1538 | 120.1447 | -1.9318
3919.0156 | 122.0444 | -120.1401 | 1.8539 | -0.0098417 | -0.0024908 | 0.067876 | 0.029288 | -0.071459 | -0.021176 | -0.00027975 | -0.0003053 | 0.033451 | 0.009064 | -0.041832 | -0.006759 | 0.011173 | 0.022888 | 0 | 0.022888 | 0.068665 | 0.10529 | 0.032043 | -0.086975 | -0.032043 | 0.027466 | -0.10986 | 0.041199 | 0.036621 | 0.068665 | -0.022888 | 120.1721 | 120.0531 | -1.7487 | 120.1401 | 120.2087 | 0.15564 | -1.8311 | 120.2087 | 120.1172 | -1.8127 | 120.108 | 120.0302 | -0.086975 | -1.8173 | 120.2454 | 120.163 | 120.163 | -1.9409 | 120.1813 | 120.1767 | 120.1675 | -1.8768
3920.7969 | 122.0535 | -119.957 | 2.0004 | 0.0054168 | 0.00092719 | 0.072363 | 0.028647 | -0.068468 | -0.028867 | -0.0015616 | 0.0073242 | 0.031101 | 0.0086368 | -0.042686 | -0.0086816 | 0.011386 | 0.091553 | 0.14191 | 0.17395 | 0.15564 | 0.050354 | 0.086975 | -0.054932 | 0.068665 | 0.16479 | 0.013733 | -0.013733 | -0.018311 | 0.09613 | 0.022888 | 120.0439 | 119.902 | -1.9501 | 120.0989 | 120.1126 | 0.21057 | -1.9089 | 120.0531 | 119.9799 | -2.0142 | 120.0256 | 119.9707 | -0.009155 | -2.0187 | 120.0073 | 120.0485 | 120.1309 | -2.0554 | 119.9432 | 119.9387 | 120.1218 | -1.9775
3922.5469 | 122.0856 | -119.7739 | 2.1378 | 0.0054168 | 0.0022088 | 0.069585 | 0.025229 | -0.067828 | -0.019895 | -0.00070715 | 0.0073242 | 0.034306 | 0.0075686 | -0.039482 | -0.0024866 | 0.010959 | 0.027466 | -0.009155 | 0.018311 | 0.086975 | 0.09613 | 0.054932 | -0.073242 | 0.004578 | 0.027466 | -0.086975 | -0.009155 | 0.018311 | 0.073242 | 0.013733 | 119.8288 | 119.7006 | -2.0416 | 119.7647 | 119.8608 | 0.16022 | -2.1103 | 119.8471 | 119.7876 | -2.1469 | 119.7784 | 119.6869 | -0.10071 | -2.1194 | 119.87 | 119.8013 | 119.7922 | -2.211 | 119.7647 | 119.7922 | 119.8013 | -2.124
3924.3438 | 122.1359 | -119.9799 | 1.9043 | 0.013046 | 0.0069086 | 0.070226 | 0.026297 | -0.069109 | -0.028653 | -0.0017752 | 0.014954 | 0.029179 | 0.0069278 | -0.042686 | -0.010177 | 0.012454 | 0.032043 | 0.082397 | 0.12817 | 0.11444 | 0.073242 | 0.068665 | -0.041199 | 0.045776 | 0.14191 | 0.022888 | -0.027466 | -0.004578 | 0.091553 | 0.004578 | 120.0485 | 119.9387 | -1.8311 | 120.0623 | 120.0943 | 0.15564 | -1.8723 | 120.0714 | 119.9844 | -1.9318 | 120.0256 | 120.0027 | 0.01831 | -1.9089 | 120.0531 | 120.0119 | 120.108 | -1.9455 | 119.9524 | 119.9753 | 120.1218 | -1.8997
3926.0625 | 122.0764 | -119.8746 | 2.0554 | 0.0054168 | -0.00014101 | 0.070654 | 0.030142 | -0.067614 | -0.02908 | -0.00070715 | 0.0073242 | 0.030888 | 0.0067142 | -0.043968 | -0.0078272 | 0.0116 | 0.10986 | 0.16479 | 0.15106 | 0.16022 | 0.054932 | 0.082397 | -0.036621 | 0.07782 | 0.1831 | 0.022888 | -0.022888 | 0 | 0.07782 | 0.018311 | 119.957 | 119.838 | -2.0004 | 120.0394 | 120.0348 | 0.19684 | -1.9455 | 119.9524 | 119.8929 | -2.0782 | 119.9524 | 119.8975 | 0.004577 | -2.0554 | 119.9295 | 119.9844 | 120.0256 | -2.092 | 119.8517 | 119.8746 | 120.0577 | -2.037
3927.8438 | 122.3648 | -119.6136 | 2.3163 | 0.013046 | 0.0056268 | 0.072363 | 0.026938 | -0.069109 | -0.02374 | 0.00057465 | 0.0073242 | 0.030674 | 0.0043644 | -0.0429 | -0.0041956 | 0.010745 | 0.11444 | 0.13275 | 0.14648 | 0.15106 | 0.050354 | 0.082397 | -0.027466 | 0.10986 | 0.14648 | 0.022888 | -0.027466 | -0.018311 | 0.09613 | 0.022888 | 119.696 | 119.5862 | -2.2659 | 119.7464 | 119.7647 | 0.17853 | -2.2018 | 119.7098 | 119.6365 | -2.3438 | 119.7235 | 119.6365 | 0 | -2.3346 | 119.664 | 119.7281 | 119.7601 | -2.3438 | 119.5862 | 119.5953 | 119.7601 | -2.2934
3929.5625 | 121.962 | -119.9661 | 2.0233 | 0.013046 | -0.00078181 | 0.072149 | 0.030569 | -0.070391 | -0.026303 | -0.0024162 | 0.0073242 | 0.031529 | 0.0067142 | -0.044181 | -0.0074 | 0.012027 | 0.068665 | 0.07782 | 0.10986 | 0.1236 | 0.073242 | 0.064087 | -0.064087 | -0.004578 | 0.064087 | -0.07782 | 0.009155 | 0.032043 | 0.073242 | -0.013733 | 120.0302 | 119.902 | -1.9501 | 120.0439 | 120.0897 | 0.18768 | -1.9547 | 120.0394 | 119.9524 | -2.0142 | 119.9615 | 119.8883 | -0.064087 | -1.9913 | 120.0394 | 120.0348 | 120.076 | -2.0874 | 119.9753 | 119.9982 | 120.0302 | -2.037
3931.3594 | 122.1725 | -119.5908 | 2.3346 | 0.0054168 | 0.0045588 | 0.072576 | 0.030569 | -0.068468 | -0.029508 | -0.00049335 | 0.014954 | 0.030247 | 0.0071414 | -0.042045 | -0.0088952 | 0.013095 | 0.054932 | 0.059509 | 0.10529 | 0.10071 | 0.068665 | 0.07782 | -0.054932 | 0.018311 | 0.07782 | -0.032043 | -0.022888 | 0.018311 | 0.086975 | 0.013733 | 119.6686 | 119.5358 | -2.2659 | 119.6503 | 119.6915 | 0.15564 | -2.2797 | 119.6777 | 119.6045 | -2.3575 | 119.6091 | 119.5587 | -0.045776 | -2.3163 | 119.6594 | 119.6457 | 119.696 | -2.3895 | 119.5679 | 119.6091 | 119.6686 | -2.3209
3933.0781 | 122.0078 | -114.3677 | 7.489 | 0.0054168 | -0.0048406 | 0.067663 | 0.030783 | -0.066546 | -0.018613 | -0.001348 | 0.0073242 | 0.035588 | 0.0077822 | -0.042259 | -0.0035546 | 0.011173 | 0.10529 | 0.059509 | 0.064087 | 0.10071 | 0.086975 | 0.16479 | 0.013733 | 0.027466 | 0.09613 | -0.073242 | 0.013733 | 0.018311 | 0.12817 | 0.050354 | 114.5325 | 114.3814 | -7.402 | 114.4272 | 114.4684 | 0.086975 | -7.3837 | 114.4959 | 114.418 | -7.4753 | 114.3951 | 114.2944 | -0.1236 | -7.4707 | 114.4547 | 114.473 | 114.4318 | -7.4753 | 114.3814 | 114.386 | 114.4638 | -7.4387
3934.8594 | 121.5729 | -13.4445 | 108.3252 | 0.013046 | 7.2586e-05 | 0.07044 | 0.026938 | -0.071245 | -0.021604 | 0.0016428 | 0.0073242 | 0.033879 | 0.007996 | -0.041618 | -0.0059046 | 0.013095 | -0.013733 | -0.041199 | -0.018311 | 0.041199 | 0.059509 | 0.022888 | -0.11444 | -0.027466 | -0.009155 | -0.11444 | -0.022888 | -0.009155 | 0.027466 | -0.059509 | 13.4674 | 13.3301 | -108.2657 | 13.4033 | 13.4857 | 0.15564 | -108.3389 | 13.472 | 13.385 | -108.3481 | 13.4171 | 13.3301 | -0.054932 | -108.3344 | 13.504 | 13.4308 | 13.4262 | -108.4396 | 13.4216 | 13.4354 | 13.4354 | -108.3847
3936.6562 | 121.9849 | -84.2056 | 37.3627 | 0.013046 | -0.0022772 | 0.069585 | 0.02587 | -0.068255 | -0.019467 | 0.0016428 | 0.014954 | 0.032383 | 0.007355 | -0.044395 | -0.0037684 | 0.010959 | 0.068665 | 0.054932 | 0.054932 | 0.10986 | 0.068665 | 0.064087 | -0.059509 | 0.009155 | 0.050354 | -0.10071 | -0.004578 | 0.013733 | 0.073242 | 0.004578 | 84.2697 | 84.1461 | -37.294 | 84.2606 | 84.3155 | 0.16937 | -37.294 | 84.2789 | 84.2102 | -37.3672 | 84.2148 | 84.1049 | -0.10529 | -37.3489 | 84.2743 | 84.2743 | 84.2606 | -37.4222 | 84.201 | 84.2194 | 84.256 | -37.3581
3938.4375 | 121.7331 | -5.4108 | 116.5192 | 0.0054168 | 0.0017816 | 0.06809 | 0.025015 | -0.068682 | -0.022672 | 0.00207 | 0.022583 | 0.031529 | 0.0060732 | -0.043327 | -0.0029138 | 0.012668 | -0.036621 | -0.07782 | -0.041199 | 0.036621 | 0.064087 | 0.004578 | -0.1236 | -0.082397 | -0.054932 | -0.17395 | 0 | -0.004578 | 0.018311 | -0.054932 | 5.4153 | 5.2872 | -116.4551 | 5.3329 | 5.4474 | 0.16022 | -116.5558 | 5.4291 | 5.3558 | -116.5192 | 5.3284 | 5.2368 | -0.11902 | -116.5237 | 5.4749 | 5.3741 | 5.3696 | -116.6428 | 5.4108 | 5.4062 | 5.3558 | -116.5741
3940.2344 | 122.0352 | -4.6005 | 117.3248 | -0.0022127 | 0.003277 | 0.070654 | 0.029074 | -0.06975 | -0.030576 | -0.00092075 | 0.022583 | 0.028538 | 0.007355 | -0.042686 | -0.0097498 | 0.014591 | 0 | 0.036621 | 0.091553 | 0.082397 | 0.013733 | 0.027466 | -0.07782 | -0.027466 | 0.054932 | -0.059509 | -0.054932 | -0.036621 | 0.054932 | -0.041199 | 4.628 | 4.5227 | -117.3111 | 4.6371 | 4.6829 | 0.16022 | -117.3248 | 4.6555 | 4.5593 | -117.3798 | 4.5731 | 4.541 | -0.01831 | -117.3614 | 4.6143 | 4.6005 | 4.6921 | -117.4026 | 4.5456 | 4.5639 | 4.6555 | -117.366
3941.9688 | 121.9528 | -4.3442 | 117.691 | 0.0054168 | -0.00056821 | 0.07279 | 0.02886 | -0.068896 | -0.025235 | -0.0015616 | 0.014954 | 0.031529 | 0.0082096 | -0.0429 | -0.0078272 | 0.0116 | -0.045776 | -0.027466 | -0.004578 | 0.022888 | 0.068665 | -0.004578 | -0.11902 | -0.086975 | -0.022888 | -0.14191 | -0.018311 | -0.018311 | 0.013733 | -0.059509 | 4.3396 | 4.2252 | -117.6224 | 4.3167 | 4.3671 | 0.14191 | -117.7368 | 4.3579 | 4.2847 | -117.7094 | 4.2572 | 4.2023 | -0.082398 | -117.7094 | 4.4128 | 4.2984 | 4.3396 | -117.8101 | 4.3259 | 4.3259 | 4.3213 | -117.7505
3943.75 | 121.9528 | -4.1656 | 117.865 | -0.0022127 | -0.00099541 | 0.068945 | 0.032706 | -0.068468 | -0.026303 | 0.00207 | 0.0073242 | 0.030674 | 0.0082096 | -0.043541 | -0.0091088 | 0.011813 | 0.018311 | 0.050354 | 0.059509 | 0.091553 | 0.032043 | 0.013733 | -0.082397 | -0.050354 | 0.045776 | -0.10986 | -0.018311 | 0.004578 | 0.018311 | -0.050354 | 4.1794 | 4.0833 | -117.8329 | 4.216 | 4.2572 | 0.17395 | -117.8467 | 4.184 | 4.1153 | -117.8833 | 4.1153 | 4.0558 | -0.059509 | -117.8604 | 4.1977 | 4.184 | 4.2252 | -117.9474 | 4.1473 | 4.1702 | 4.2114 | -117.9153
3945.5625 | 122.0306 | -3.9322 | 118.1168 | 0.020676 | -0.00014101 | 0.072363 | 0.029074 | -0.067187 | -0.023099 | -0.00070715 | 0.022583 | 0.031529 | 0.0058596 | -0.041191 | -0.005691 | 0.011386 | -0.036621 | -0.041199 | -0.018311 | 0.032043 | 0.064087 | 0.013733 | -0.13275 | -0.068665 | -0.004578 | -0.14648 | -0.036621 | -0.013733 | 0.013733 | -0.059509 | 3.9459 | 3.7994 | -118.0527 | 3.891 | 3.9642 | 0.16479 | -118.1534 | 3.9459 | 3.8727 | -118.1534 | 3.8635 | 3.7857 | -0.086975 | -118.1305 | 3.9963 | 3.8956 | 3.9139 | -118.2495 | 3.8956 | 3.9185 | 3.9276 | -118.1763
3947.375 | 121.9803 | -3.7857 | 118.2587 | 0.020676 | 7.2586e-05 | 0.06809 | 0.026297 | -0.068682 | -0.021176 | 0.0012154 | 0.0073242 | 0.034519 | 0.0060732 | -0.042259 | -0.002273 | 0.012241 | -0.004578 | -0.022888 | -0.009155 | 0.050354 | 0.045776 | 0.013733 | -0.10986 | -0.050354 | -0.022888 | -0.16937 | -0.041199 | -0.013733 | 0.032043 | -0.032043 | 3.7994 | 3.6758 | -118.2129 | 3.7628 | 3.8361 | 0.16022 | -118.2632 | 3.8177 | 3.7537 | -118.2999 | 3.7354 | 3.6163 | -0.13733 | -118.2724 | 3.8315 | 3.7811 | 3.7766 | -118.3685 | 3.7445 | 3.772 | 3.7628 | -118.2907
3949.1562 | 122.0123 | -3.7308 | 118.3136 | -0.017471 | -0.00185 | 0.069158 | 0.029929 | -0.065905 | -0.023953 | 0.0012154 | 0.014954 | 0.030888 | 0.007996 | -0.042259 | -0.0063318 | 0.0098907 | -0.013733 | 0.004578 | 0.027466 | 0.064087 | 0.068665 | 0.013733 | -0.11902 | -0.022888 | 0.054932 | -0.10529 | -0.036621 | -0.013733 | 0.009155 | -0.050354 | 3.7445 | 3.6118 | -118.2449 | 3.7354 | 3.7949 | 0.18311 | -118.3273 | 3.7399 | 3.6804 | -118.3502 | 3.7079 | 3.6255 | -0.054932 | -118.3273 | 3.7994 | 3.717 | 3.7582 | -118.4326 | 3.6942 | 3.717 | 3.7857 | -118.364
3950.875 | 122.0078 | -3.6896 | 118.3319 | 0.013046 | 0.0022088 | 0.067663 | 0.024588 | -0.071032 | -0.023313 | 0.0022836 | 0.0073242 | 0.032597 | 0.0082096 | -0.041832 | -0.00505 | 0.012882 | -0.059509 | -0.068665 | -0.041199 | 0.018311 | 0.045776 | 0.009155 | -0.11444 | -0.091553 | -0.064087 | -0.17395 | -0.018311 | 0.004578 | 0.009155 | -0.064087 | 3.6987 | 3.5751 | -118.2861 | 3.6209 | 3.7079 | 0.13275 | -118.3914 | 3.6987 | 3.6255 | -118.3502 | 3.598 | 3.5156 | -0.10986 | -118.3273 | 3.7354 | 3.6301 | 3.6484 | -118.4463 | 3.6713 | 3.6942 | 3.6255 | -118.396
3952.6719 | 122.049 | -3.6255 | 118.4052 | 0.013046 | -0.00056821 | 0.072149 | 0.030356 | -0.067614 | -0.026517 | -0.0015616 | 0.0073242 | 0.030461 | 0.0082096 | -0.044609 | -0.0082544 | 0.014377 | -0.068665 | -0.041199 | -0.027466 | 0.018311 | 0.059509 | -0.004578 | -0.1236 | -0.082397 | -0.009155 | -0.15564 | -0.009155 | 0.004578 | 0.013733 | -0.036621 | 3.6209 | 3.5019 | -118.3456 | 3.5843 | 3.6438 | 0.14191 | -118.4738 | 3.6392 | 3.5889 | -118.4143 | 3.5431 | 3.4698 | -0.11902 | -118.4006 | 3.685 | 3.5568 | 3.598 | -118.5287 | 3.6163 | 3.6301 | 3.6163 | -118.4418
3954.4688 | 122.1268 | -3.4836 | 118.4555 | 0.0054168 | 0.0024224 | 0.069585 | 0.027792 | -0.071245 | -0.026944 | 0.003138 | 0.014954 | 0.032383 | 0.0060732 | -0.0429 | -0.0054772 | 0.013736 | 0.036621 | 0.045776 | 0.07782 | 0.10986 | 0.013733 | 0.054932 | -0.073242 | 0.027466 | 0.091553 | -0.018311 | -0.064087 | -0.054932 | 0.064087 | -0.009155 | 3.5385 | 3.4103 | -118.4418 | 3.5294 | 3.5934 | 0.18311 | -118.4189 | 3.5477 | 3.4744 | -118.5196 | 3.511 | 3.4653 | -0.009156 | -118.5104 | 3.4973 | 3.5202 | 3.5614 | -118.5287 | 3.4195 | 3.4287 | 3.5751 | -118.4647
3956.2031 | 121.9894 | -41.803 | 79.8843 | -0.0022127 | 0.0013544 | 0.069799 | 0.029288 | -0.068468 | -0.030789 | -0.00049335 | -0.0003053 | 0.030674 | 0.0075686 | -0.043968 | -0.010177 | 0.013309 | 0.059509 | 0.091553 | 0.13275 | 0.1236 | 0.018311 | 0.036621 | -0.064087 | 0.022888 | 0.14191 | -0.004578 | -0.054932 | -0.018311 | 0.07782 | -0.027466 | 41.8396 | 41.7389 | -79.866 | 41.8945 | 41.9266 | 0.18768 | -79.8248 | 41.8808 | 41.7755 | -79.9393 | 41.8259 | 41.7984 | 0.022888 | -79.9026 | 41.8213 | 41.8625 | 41.9357 | -79.9484 | 41.748 | 41.7847 | 41.9449 | -79.9118
3958 | 121.8292 | -5.0583 | 117.0181 | 0.0054168 | -0.00056821 | 0.069372 | 0.026083 | -0.070818 | -0.020749 | -0.00049335 | 0.0073242 | 0.033879 | 0.007996 | -0.040336 | -0.0020594 | 0.0094635 | -0.032043 | -0.059509 | -0.013733 | 0.032043 | 0.064087 | 0.013733 | -0.11902 | -0.082397 | -0.054932 | -0.17395 | -0.036621 | 0.004578 | 0.018311 | -0.059509 | 5.072 | 4.9393 | -116.954 | 4.9988 | 5.0903 | 0.15106 | -117.0502 | 5.0766 | 4.9988 | -117.0547 | 4.9759 | 4.8843 | -0.11444 | -117.0135 | 5.1224 | 5.0262 | 5.0446 | -117.1371 | 5.0217 | 5.0629 | 5.0034 | -117.0776
3959.7969 | 122.0078 | -4.7333 | 117.3203 | -0.0022127 | 0.0013544 | 0.072576 | 0.028647 | -0.070177 | -0.027585 | 0.0012154 | -0.0003053 | 0.030033 | 0.0065006 | -0.044395 | -0.0088952 | 0.013095 | 0.027466 | 0.086975 | 0.10986 | 0.1236 | 0.018311 | 0.022888 | -0.07782 | 0.009155 | 0.11444 | -0.027466 | -0.07782 | -0.041199 | 0.059509 | -0.013733 | 4.7562 | 4.6555 | -117.3019 | 4.8203 | 4.8569 | 0.20142 | -117.2928 | 4.7928 | 4.7195 | -117.3981 | 4.7424 | 4.7058 | -0.013733 | -117.3615 | 4.7516 | 4.7607 | 4.8431 | -117.3981 | 4.6555 | 4.6921 | 4.8477 | -117.334
3961.5469 | 122.0169 | -4.9576 | 117.1051 | 0.013046 | -0.00099541 | 0.072149 | 0.02886 | -0.068468 | -0.027158 | -0.0043388 | 0.0073242 | 0.030888 | 0.0069278 | -0.044609 | -0.0091088 | 0.010532 | 0.013733 | 0.050354 | 0.064087 | 0.086975 | 0.027466 | 0.009155 | -0.10529 | -0.050354 | 0.041199 | -0.091553 | -0.050354 | -0.009155 | 0.022888 | -0.045776 | 4.9667 | 4.8523 | -117.0776 | 5.0079 | 5.0446 | 0.19226 | -117.0914 | 4.9805 | 4.9118 | -117.1555 | 4.9072 | 4.866 | -0.045777 | -117.1143 | 4.985 | 4.9713 | 5.0217 | -117.2104 | 4.9072 | 4.9484 | 4.9988 | -117.1509
3963.3594 | 122.1634 | -5.0034 | 116.9128 | 0.013046 | 0.0051996 | 0.070013 | 0.030356 | -0.068041 | -0.028867 | -0.0019888 | 0.014954 | 0.029392 | 0.0069278 | -0.042686 | -0.0088952 | 0.012027 | 0.013733 | 0.045776 | 0.091553 | 0.091553 | 0.036621 | 0.036621 | -0.10986 | 0.018311 | 0.10529 | -0.004578 | -0.054932 | -0.041199 | 0.045776 | -0.032043 | 5.04 | 4.8935 | -116.8762 | 5.0491 | 5.0949 | 0.20142 | -116.8991 | 5.0491 | 4.9713 | -116.9678 | 5.0217 | 4.9988 | 0.027465 | -116.954 | 5.04 | 5.0171 | 5.0949 | -117.0227 | 4.9484 | 4.9622 | 5.1086 | -116.9449
3965.1562 | 122.0032 | -4.4312 | 117.6224 | -0.0022127 | -0.003559 | 0.065954 | 0.028647 | -0.068255 | -0.019467 | 0.00014745 | 0.014954 | 0.033451 | 0.0084232 | -0.043327 | -0.0037684 | 0.011173 | 0.013733 | -0.018311 | 0.009155 | 0.045776 | 0.054932 | 0.013733 | -0.12817 | -0.036621 | -0.022888 | -0.16937 | -0.022888 | -0.009155 | 0.018311 | -0.045776 | 4.4449 | 4.303 | -117.5674 | 4.4128 | 4.4769 | 0.17395 | -117.6086 | 4.4495 | 4.3854 | -117.6453 | 4.3945 | 4.2618 | -0.1236 | -117.6315 | 4.4861 | 4.4449 | 4.4403 | -117.7505 | 4.4083 | 4.422 | 4.4083 | -117.6682
3966.9531 | 122.0718 | -4.3625 | 117.7094 | 0.0054168 | -0.0014228 | 0.069799 | 0.02822 | -0.065478 | -0.025235 | -0.0011344 | 0.014954 | 0.033665 | 0.0084232 | -0.043327 | -0.0054772 | 0.012668 | -0.059509 | -0.054932 | -0.032043 | 0.018311 | 0.054932 | 0 | -0.14648 | -0.082397 | -0.009155 | -0.15564 | -0.018311 | -0.004578 | 0.018311 | -0.059509 | 4.3625 | 4.216 | -117.6544 | 4.3076 | 4.3808 | 0.16479 | -117.7689 | 4.3808 | 4.303 | -117.7277 | 4.2801 | 4.2068 | -0.096131 | -117.7139 | 4.4174 | 4.303 | 4.3304 | -117.8558 | 4.3442 | 4.3579 | 4.3533 | -117.7689
3968.6719 | 122.0352 | -4.248 | 117.8101 | 0.0054168 | 0.0013544 | 0.067449 | 0.026511 | -0.066973 | -0.022244 | -0.00049335 | 0.014954 | 0.03281 | 0.0086368 | -0.041191 | -0.0052636 | 0.010745 | -0.054932 | -0.054932 | -0.041199 | 0.022888 | 0.059509 | 0.009155 | -0.11444 | -0.073242 | -0.054932 | -0.1831 | -0.022888 | -0.004578 | 0.027466 | -0.041199 | 4.2572 | 4.1336 | -117.7505 | 4.1931 | 4.2709 | 0.13733 | -117.865 | 4.2755 | 4.2068 | -117.8329 | 4.1748 | 4.0649 | -0.14191 | -117.8146 | 4.3076 | 4.1931 | 4.2068 | -117.9245 | 4.2252 | 4.2435 | 4.1931 | -117.8513
3970.4688 | 122.1771 | -4.2572 | 117.746 | 0.020676 | 0.0041314 | 0.074499 | 0.029715 | -0.068468 | -0.029721 | -0.0032706 | 0.014954 | 0.026615 | 0.0050052 | -0.043754 | -0.0086816 | 0.01395 | -0.009155 | 0.054932 | 0.068665 | 0.086975 | 0.018311 | 0.036621 | -0.07782 | -0.004578 | 0.091553 | -0.018311 | -0.059509 | -0.041199 | 0.050354 | -0.018311 | 4.2938 | 4.1794 | -117.7277 | 4.3121 | 4.3442 | 0.16479 | -117.7551 | 4.3076 | 4.2389 | -117.8055 | 4.2526 | 4.2389 | 0 | -117.7872 | 4.2755 | 4.248 | 4.3259 | -117.8238 | 4.1977 | 4.216 | 4.3488 | -117.7643
3972.2656 | 122.0535 | -4.0192 | 118.0847 | 0.013046 | 0.0041314 | 0.068304 | 0.027152 | -0.066332 | -0.022885 | -6.615e-05 | 0.014954 | 0.033451 | 0.0075686 | -0.041832 | -0.0035546 | 0.012454 | -0.073242 | -0.091553 | -0.036621 | 0.004578 | 0.054932 | 0.022888 | -0.11902 | -0.073242 | -0.064087 | -0.16937 | -0.022888 | 0 | 0.018311 | -0.059509 | 4.0421 | 3.9001 | -118.0298 | 3.9276 | 4.0237 | 0.1236 | -118.158 | 4.0375 | 3.9597 | -118.1076 | 3.9459 | 3.8498 | -0.10986 | -118.0847 | 4.0741 | 3.9459 | 3.9825 | -118.2037 | 3.9963 | 4.0192 | 3.9551 | -118.1442
3974 | 122.1817 | -4.0649 | 117.8787 | -0.0022127 | 0.0047724 | 0.068945 | 0.025443 | -0.068255 | -0.024167 | -0.00049335 | 0.022583 | 0.031315 | 0.0075686 | -0.040123 | -0.0063318 | 0.012882 | -0.022888 | -0.032043 | 0.004578 | 0.041199 | 0.041199 | 0.022888 | -0.10986 | -0.004578 | 0.009155 | -0.091553 | -0.036621 | -0.018311 | 0.045776 | -0.027466 | 4.0878 | 3.9551 | -117.8375 | 4.0329 | 4.1061 | 0.15106 | -117.9016 | 4.1107 | 4.0375 | -117.9153 | 4.0604 | 3.9734 | -0.064087 | -117.897 | 4.1061 | 4.0421 | 4.0695 | -117.9886 | 4.0283 | 4.0466 | 4.0741 | -117.9062
3975.7969 | 122.0627 | -4.1245 | 117.952 | -0.0022127 | -0.00185 | 0.069585 | 0.027579 | -0.068468 | -0.022885 | 0.00014745 | 0.0073242 | 0.034306 | 0.0050052 | -0.0429 | -0.00505 | 0.010959 | 0.027466 | 0.022888 | 0.027466 | 0.068665 | 0.032043 | 0.041199 | -0.11902 | -0.018311 | 0.036621 | -0.10529 | -0.013733 | -0.009155 | 0.045776 | -0.027466 | 4.1656 | 4.0054 | -117.9199 | 4.1473 | 4.1931 | 0.18768 | -117.9245 | 4.1702 | 4.097 | -117.9657 | 4.1061 | 4.0192 | -0.07782 | -117.9611 | 4.1565 | 4.1519 | 4.1519 | -118.071 | 4.1107 | 4.1153 | 4.1611 | -117.9794
3977.6094 | 122.0627 | -4.0558 | 118.0115 | 0.013046 | -0.00078181 | 0.068304 | 0.027152 | -0.066973 | -0.024594 | 0.0014292 | 0.014954 | 0.035374 | 0.009064 | -0.042472 | -0.0069726 | 0.013095 | 0.022888 | 0.022888 | 0.032043 | 0.068665 | 0.050354 | 0.018311 | -0.11902 | -0.022888 | 0.054932 | -0.10529 | -0.036621 | 0.004578 | 0.041199 | -0.036621 | 4.0741 | 3.9368 | -117.9611 | 4.0787 | 4.1245 | 0.18768 | -117.9886 | 4.097 | 4.0192 | -118.0481 | 4.0329 | 3.9505 | -0.068665 | -118.0069 | 4.1061 | 4.0787 | 4.0878 | -118.1305 | 4.0192 | 4.0604 | 4.1107 | -118.0481
3979.4062 | 122.0215 | -4.0466 | 118.0252 | 0.0054168 | -0.0048406 | 0.067876 | 0.026083 | -0.068468 | -0.021817 | 0.00014745 | 0.0073242 | 0.033238 | 0.007355 | -0.041404 | -0.00505 | 0.0094635 | -0.004578 | -0.013733 | 0.009155 | 0.045776 | 0.059509 | 0 | -0.10071 | -0.054932 | -0.018311 | -0.16479 | -0.018311 | 0 | 0.036621 | -0.050354 | 4.0466 | 3.9459 | -117.9657 | 4.0329 | 4.0924 | 0.14648 | -118.0298 | 4.0833 | 3.9963 | -118.0435 | 3.9917 | 3.8818 | -0.11444 | -118.0252 | 4.1061 | 4.0421 | 4.0558 | -118.1259 | 4.0283 | 4.0466 | 4.0283 | -118.0756
3981.125 | 122.168 | -4.01 | 118.0161 | -0.0022127 | 0.0013544 | 0.069372 | 0.024802 | -0.069537 | -0.024167 | 0.0014292 | 0.0073242 | 0.033238 | 0.0077822 | -0.039268 | -0.0052636 | 0.012241 | -0.054932 | -0.059509 | -0.027466 | 0.032043 | 0.068665 | 0.004578 | -0.10986 | -0.082397 | -0.018311 | -0.14648 | -0.022888 | -0.018311 | 0.045776 | -0.059509 | 4.0146 | 3.9001 | -117.9474 | 3.9505 | 4.0421 | 0.14191 | -118.071 | 4.0558 | 3.9505 | -118.0389 | 3.9276 | 3.8635 | -0.086975 | -118.0344 | 4.0787 | 3.9551 | 3.9825 | -118.1259 | 3.9871 | 3.9917 | 3.9917 | -118.0756
3982.9219 | 122.1085 | -3.9322 | 118.1168 | 0.013046 | -0.0050544 | 0.067449 | 0.029501 | -0.0674 | -0.023313 | 0.00014745 | 0.014954 | 0.034092 | 0.0099186 | -0.043113 | -0.008468 | 0.011173 | -0.036621 | -0.045776 | 0 | 0.054932 | 0.045776 | -0.004578 | -0.1236 | -0.045776 | 0.018311 | -0.11902 | -0.027466 | 0 | 0.022888 | -0.050354 | 3.9276 | 3.8086 | -118.071 | 3.8864 | 3.9871 | 0.17853 | -118.1534 | 3.9551 | 3.8818 | -118.1442 | 3.8864 | 3.8132 | -0.068665 | -118.1168 | 3.978 | 3.8956 | 3.9322 | -118.2404 | 3.9047 | 3.9322 | 3.9505 | -118.1671
3984.6875 | 122.1863 | -3.8269 | 118.1808 | 0.020676 | 0.0037042 | 0.067022 | 0.026511 | -0.068041 | -0.025022 | 0.0016428 | 0.0073242 | 0.03217 | 0.0069278 | -0.04055 | -0.006759 | 0.010745 | -0.027466 | -0.022888 | 0.004578 | 0.041199 | 0.054932 | 0.013733 | -0.09613 | -0.018311 | 0.022888 | -0.082397 | -0.041199 | -0.022888 | 0.050354 | -0.013733 | 3.8406 | 3.7308 | -118.1259 | 3.804 | 3.8681 | 0.13733 | -118.2083 | 3.8773 | 3.8132 | -118.222 | 3.8086 | 3.7445 | -0.068664 | -118.2037 | 3.8818 | 3.7994 | 3.8315 | -118.277 | 3.7857 | 3.804 | 3.8498 | -118.1946
3986.5 | 122.0718 | -3.9917 | 118.071 | 0.0054168 | -0.00056821 | 0.07279 | 0.027792 | -0.065691 | -0.031003 | -0.0024162 | 0.014954 | 0.030247 | 0.0065006 | -0.043113 | -0.0069726 | 0.012668 | 0.013733 | 0.064087 | 0.086975 | 0.09613 | 0.022888 | 0.027466 | -0.10071 | -0.041199 | 0.073242 | -0.059509 | -0.068665 | -0.018311 | 0.041199 | -0.041199 | 4.0192 | 3.891 | -118.0481 | 4.0558 | 4.0878 | 0.19684 | -118.0573 | 4.0329 | 3.9505 | -118.1396 | 3.9505 | 3.9322 | -0.01831 | -118.0893 | 4.0146 | 4.0054 | 4.0787 | -118.1717 | 3.923 | 3.9734 | 4.0649 | -118.1122
3988.2188 | 122.1588 | -3.9047 | 118.103 | 0.013046 | 0.0041314 | 0.071935 | 0.027365 | -0.070605 | -0.029721 | -0.00092075 | -0.0003053 | 0.029392 | 0.0067142 | -0.044822 | -0.0059046 | 0.012241 | 0.013733 | 0.059509 | 0.09613 | 0.086975 | 0.013733 | 0.041199 | -0.082397 | -0.022888 | 0.045776 | -0.050354 | -0.054932 | -0.036621 | 0.054932 | -0.036621 | 3.9459 | 3.8223 | -118.0893 | 3.9642 | 3.9917 | 0.16937 | -118.0893 | 3.9597 | 3.8681 | -118.158 | 3.8818 | 3.8544 | -0.013733 | -118.1396 | 3.9185 | 3.9185 | 4.0009 | -118.1854 | 3.8498 | 3.8681 | 3.9505 | -118.1396
3990 | 122.081 | -4.1702 | 117.9337 | 0.0054168 | -0.0012092 | 0.071722 | 0.030356 | -0.066759 | -0.027158 | -0.00070715 | 0.0073242 | 0.030461 | 0.009064 | -0.043541 | -0.008468 | 0.014377 | 0.009155 | 0.027466 | 0.050354 | 0.07782 | 0.050354 | 0.027466 | -0.09613 | -0.073242 | 0.018311 | -0.11444 | -0.027466 | -0.009155 | 0.018311 | -0.059509 | 4.1977 | 4.0741 | -117.8833 | 4.1977 | 4.248 | 0.17395 | -117.9245 | 4.1885 | 4.1107 | -117.9611 | 4.097 | 4.0558 | -0.054932 | -117.9428 | 4.2206 | 4.1794 | 4.2206 | -118.0298 | 4.1428 | 4.1611 | 4.1885 | -117.9932
3991.7031 | 122.0627 | -4.1611 | 117.9108 | 0.013046 | -0.00078181 | 0.067663 | 0.025443 | -0.067614 | -0.020322 | 0.00057465 | 0.0073242 | 0.033879 | 0.0086368 | -0.0429 | -0.0035546 | 0.011173 | 0.032043 | 0.009155 | 0.022888 | 0.07782 | 0.059509 | 0.013733 | -0.07782 | -0.041199 | 0.022888 | -0.1236 | -0.027466 | 0.009155 | 0.050354 | -0.064087 | 4.1748 | 4.0833 | -117.8513 | 4.1702 | 4.2389 | 0.15564 | -117.8787 | 4.2114 | 4.097 | -117.9382 | 4.1199 | 4.0375 | -0.059509 | -117.9016 | 4.2206 | 4.1931 | 4.184 | -117.9886 | 4.1336 | 4.1702 | 4.184 | -117.9749
3993.4688 | 122.081 | -4.216 | 117.9245 | 0.013046 | -0.0027044 | 0.070226 | 0.029501 | -0.067614 | -0.026944 | 0.00036105 | 0.0073242 | 0.02982 | 0.0077822 | -0.042472 | -0.0088952 | 0.012454 | -0.032043 | -0.041199 | -0.009155 | 0.027466 | 0.032043 | -0.022888 | -0.13733 | -0.091553 | -0.013733 | -0.14648 | -0.004578 | -0.009155 | 0.027466 | -0.045776 | 4.1931 | 4.0787 | -117.8925 | 4.1748 | 4.2435 | 0.16479 | -117.9565 | 4.2435 | 4.1702 | -117.9291 | 4.1244 | 4.0695 | -0.10071 | -117.9337 | 4.248 | 4.184 | 4.2068 | -118.0618 | 4.2114 | 4.2068 | 4.2023 | -117.9703
3995.1719 | 122.1451 | -4.1611 | 117.9062 | -0.0022127 | 0.004345 | 0.073644 | 0.024588 | -0.069537 | -0.030789 | -0.00070715 | 0.0073242 | 0.028752 | 0.0052188 | -0.043968 | -0.0061182 | 0.012668 | 0.045776 | 0.073242 | 0.09613 | 0.086975 | 0.013733 | 0.041199 | -0.086975 | -0.018311 | 0.054932 | -0.050354 | -0.054932 | -0.050354 | 0.059509 | -0.032043 | 4.2023 | 4.0741 | -117.8925 | 4.2343 | 4.248 | 0.17395 | -117.8604 | 4.2206 | 4.129 | -117.9611 | 4.1428 | 4.1107 | -0.018311 | -117.9565 | 4.1748 | 4.2068 | 4.2572 | -117.9932 | 4.1061 | 4.1107 | 4.216 | -117.9382
3996.9531 | 122.168 | -4.0237 | 117.9749 | 0.020676 | 0.003277 | 0.073431 | 0.023947 | -0.069323 | -0.026303 | -0.00027975 | 0.0073242 | 0.02982 | 0.005646 | -0.043327 | -0.005691 | 0.012668 | 0.064087 | 0.086975 | 0.10529 | 0.10986 | 0.009155 | 0.036621 | -0.086975 | 0.036621 | 0.086975 | -0.013733 | -0.064087 | -0.032043 | 0.059509 | -0.018311 | 4.0604 | 3.9368 | -117.9657 | 4.1107 | 4.1336 | 0.19684 | -117.9108 | 4.0833 | 4.0054 | -118.0389 | 4.0604 | 4.01 | 0.004578 | -118.0069 | 4.0329 | 4.0878 | 4.129 | -118.0618 | 3.9597 | 3.9917 | 4.1107 | -117.9932
3998.6719 | 122.168 | -4.1931 | 117.8192 | 0.0054168 | 0.0075494 | 0.07044 | 0.023306 | -0.068255 | -0.026731 | 0.00014745 | -0.0003053 | 0.030461 | 0.0050052 | -0.045463 | -0.0063318 | 0.013095 | 0.073242 | 0.068665 | 0.11444 | 0.091553 | 0.018311 | 0.045776 | -0.064087 | 0.027466 | 0.07782 | -0.027466 | -0.064087 | -0.054932 | 0.068665 | -0.013733 | 4.2389 | 4.129 | -117.8009 | 4.2618 | 4.2847 | 0.15564 | -117.746 | 4.2618 | 4.1794 | -117.8833 | 4.2206 | 4.1656 | -0.013733 | -117.8741 | 4.2114 | 4.2664 | 4.3076 | -117.8833 | 4.129 | 4.1382 | 4.2709 | -117.8329
4000.3906 | 122.1039 | -4.1199 | 117.9749 | 0.0054168 | -0.00078181 | 0.068945 | 0.029288 | -0.066973 | -0.025662 | -0.0026298 | 0.0073242 | 0.029606 | 0.0067142 | -0.043754 | -0.008468 | 0.010532 | 0.054932 | 0.086975 | 0.10986 | 0.10986 | 0.013733 | 0.050354 | -0.091553 | 0.004578 | 0.11444 | -0.036621 | -0.068665 | -0.036621 | 0.050354 | -0.032043 | 4.1702 | 4.0283 | -117.9611 | 4.2068 | 4.2297 | 0.20142 | -117.9199 | 4.1702 | 4.0878 | -118.0435 | 4.1245 | 4.0833 | -0.004578 | -118.0115 | 4.1336 | 4.1748 | 4.2297 | -118.0664 | 4.0512 | 4.0833 | 4.2343 | -118.0069
4002.1562 | 122.0856 | -4.0512 | 118.0801 | 0.0054168 | -0.00014101 | 0.070867 | 0.029288 | -0.066973 | -0.025449 | -0.0015616 | -0.0003053 | 0.033879 | 0.0084232 | -0.044822 | -0.0054772 | 0.010959 | -0.009155 | -0.027466 | 0.009155 | 0.041199 | 0.050354 | 0 | -0.13275 | -0.086975 | 0 | -0.15564 | -0.018311 | -0.004578 | 0.018311 | -0.068665 | 4.0512 | 3.9185 | -118.0298 | 4.0237 | 4.0924 | 0.17395 | -118.0893 | 4.0695 | 3.9825 | -118.0984 | 3.9642 | 3.8956 | -0.086975 | -118.0847 | 4.1016 | 4.0421 | 4.0604 | -118.2129 | 4.0329 | 4.0466 | 4.0512 | -118.1488
4004.0156 | 122.0627 | -5.983 | 116.1209 | 0.013046 | -0.00099541 | 0.066167 | 0.026724 | -0.065478 | -0.020535 | -0.00049335 | -0.0003053 | 0.036228 | 0.007996 | -0.040123 | -0.006759 | 0.0098907 | 0.068665 | 0.018311 | 0.041199 | 0.064087 | 0.054932 | 0.018311 | -0.11444 | -0.013733 | 0.013733 | -0.13733 | -0.036621 | -0.013733 | 0.041199 | -0.032043 | 6.0013 | 5.8685 | -116.066 | 6.0013 | 6.0471 | 0.17853 | -116.0522 | 6.0242 | 5.9509 | -116.1575 | 5.9692 | 5.8456 | -0.10529 | -116.1346 | 6.0379 | 6.0516 | 6.0242 | -116.2354 | 5.9463 | 5.9692 | 5.9967 | -116.153
4005.7188 | 122.1405 | -6.6925 | 115.3473 | 0.0054168 | 0.003277 | 0.071935 | 0.026083 | -0.065691 | -0.02374 | 0.0014292 | 0.022583 | 0.028752 | 0.005646 | -0.041404 | -0.0024866 | 0.014163 | 0.064087 | 0.086975 | 0.10529 | 0.11444 | 0.018311 | 0.050354 | -0.086975 | 0.054932 | 0.10071 | -0.027466 | -0.073242 | -0.041199 | 0.073242 | -0.018311 | 6.7429 | 6.6055 | -115.329 | 6.7795 | 6.8069 | 0.20142 | -115.2832 | 6.7657 | 6.6742 | -115.4205 | 6.7474 | 6.665 | -0.009155 | -115.3885 | 6.7108 | 6.7566 | 6.7978 | -115.4343 | 6.6193 | 6.6513 | 6.7932 | -115.3656
4007.4219 | 122.1222 | -5.7449 | 116.2903 | 0.0054168 | 0.0051996 | 0.072149 | 0.024161 | -0.0674 | -0.028012 | -6.615e-05 | 0.0073242 | 0.030461 | 0.006287 | -0.042686 | -0.0074 | 0.013095 | 0.027466 | 0.059509 | 0.068665 | 0.073242 | 0.027466 | 0.045776 | -0.09613 | -0.018311 | 0.059509 | -0.073242 | -0.068665 | -0.032043 | 0.050354 | -0.041199 | 5.7907 | 5.6488 | -116.2628 | 5.8044 | 5.8182 | 0.16937 | -116.2628 | 5.7953 | 5.7037 | -116.3589 | 5.7266 | 5.6717 | -0.032043 | -116.3223 | 5.7724 | 5.7724 | 5.8136 | -116.3864 | 5.6763 | 5.7129 | 5.8044 | -116.3315
4009.1406 | 121.3943 | -4.248 | 117.8833 | 0.0054168 | -0.0027044 | 0.067236 | 0.027152 | -0.068468 | -0.019895 | -0.00049335 | 0.014954 | 0.034947 | 0.0075686 | -0.041618 | -0.002273 | 0.010745 | 0.027466 | -0.009155 | 0.022888 | 0.045776 | 0.041199 | 0.013733 | -0.10071 | -0.032043 | -0.018311 | -0.15564 | -0.032043 | -0.032043 | 0.013733 | -0.050354 | 4.2618 | 4.1473 | -117.8421 | 4.2389 | 4.2938 | 0.14648 | -117.8558 | 4.2618 | 4.1977 | -117.9153 | 4.216 | 4.0924 | -0.10529 | -117.9153 | 4.2892 | 4.2755 | 4.2709 | -117.984 | 4.216 | 4.216 | 4.2297 | -117.9337
4010.8594 | 121.7056 | -5.0583 | 117.0639 | 0.0054168 | 0.00071339 | 0.073644 | 0.030356 | -0.068041 | -0.030789 | -0.0026298 | 0.0073242 | 0.028752 | 0.006287 | -0.043754 | -0.0097498 | 0.012668 | 0.045776 | 0.086975 | 0.12817 | 0.11444 | 0.027466 | 0.050354 | -0.10071 | 0.022888 | 0.1236 | -0.032043 | -0.068665 | -0.032043 | 0.054932 | -0.027466 | 5.1086 | 4.9576 | -117.0364 | 5.1453 | 5.1727 | 0.21515 | -117.0181 | 5.1132 | 5.0308 | -117.1326 | 5.0812 | 5.0262 | -0.004577 | -117.0959 | 5.0858 | 5.1041 | 5.1865 | -117.1646 | 4.9896 | 5.0262 | 5.1819 | -117.0914
4012.5781 | 121.5775 | -6.514 | 115.6265 | 0.013046 | -0.00078181 | 0.067449 | 0.026511 | -0.069323 | -0.021176 | -0.0011344 | -0.0003053 | 0.03281 | 0.0071414 | -0.041404 | -0.0037684 | 0.0116 | 0.004578 | -0.032043 | -0.009155 | 0.036621 | 0.045776 | 0.032043 | -0.1236 | -0.050354 | -0.022888 | -0.17853 | -0.032043 | -0.009155 | 0.027466 | -0.045776 | 6.546 | 6.3904 | -115.5807 | 6.4819 | 6.5506 | 0.16022 | -115.6219 | 6.5414 | 6.4682 | -115.6586 | 6.4636 | 6.3354 | -0.13275 | -115.6357 | 6.5598 | 6.5186 | 6.5048 | -115.7501 | 6.4819 | 6.5048 | 6.4911 | -115.6723
4014.2969 | 122.1451 | -4.2297 | 117.8421 | 0.0054168 | 0.0071222 | 0.07044 | 0.025229 | -0.068682 | -0.025876 | -0.00027975 | -0.0003053 | 0.030247 | 0.0069278 | -0.043113 | -0.0093226 | 0.015018 | 0.036621 | 0.082397 | 0.11444 | 0.09613 | 0.009155 | 0.045776 | -0.07782 | 0.032043 | 0.082397 | -0.027466 | -0.050354 | -0.036621 | 0.045776 | -0.018311 | 4.2755 | 4.1519 | -117.8329 | 4.3121 | 4.3259 | 0.17395 | -117.8055 | 4.2755 | 4.2114 | -117.8925 | 4.2618 | 4.2023 | -0.009155 | -117.8787 | 4.2389 | 4.2664 | 4.3442 | -117.9199 | 4.1794 | 4.1931 | 4.3121 | -117.8604
4016.0156 | 122.0764 | -4.7562 | 117.3706 | 0.0054168 | -0.0027044 | 0.073217 | 0.030783 | -0.067614 | -0.026303 | -0.0011344 | 0.0073242 | 0.031529 | 0.007355 | -0.041191 | -0.0071862 | 0.012454 | -0.032043 | -0.027466 | 0.004578 | 0.022888 | 0.059509 | -0.009155 | -0.12817 | -0.082397 | 0 | -0.13733 | -0.022888 | -0.004578 | 0.018311 | -0.054932 | 4.747 | 4.628 | -117.3111 | 4.7287 | 4.7791 | 0.15106 | -117.4026 | 4.7745 | 4.7012 | -117.3935 | 4.6738 | 4.6188 | -0.082397 | -117.3752 | 4.8157 | 4.7241 | 4.7607 | -117.4988 | 4.7333 | 4.7516 | 4.7562 | -117.4255
4017.7188 | 122.1817 | -4.8294 | 117.1509 | -0.0022127 | 0.0056268 | 0.068945 | 0.027579 | -0.0674 | -0.029508 | -0.003057 | 0.0073242 | 0.027683 | 0.006287 | -0.046104 | -0.0082544 | 0.012882 | -0.018311 | 0.018311 | 0.068665 | 0.07782 | 0.036621 | 0.027466 | -0.091553 | -0.004578 | 0.068665 | -0.050354 | -0.045776 | -0.027466 | 0.054932 | -0.027466 | 4.8569 | 4.7379 | -117.1143 | 4.8477 | 4.9072 | 0.16937 | -117.1692 | 4.8843 | 4.8019 | -117.1967 | 4.8248 | 4.7791 | -0.022888 | -117.1783 | 4.866 | 4.8111 | 4.8981 | -117.2424 | 4.7836 | 4.8019 | 4.8981 | -117.1783
4019.4844 | 121.7789 | -4.303 | 117.5446 | -0.0022127 | -0.0012092 | 0.067236 | 0.025443 | -0.067187 | -0.019254 | 0.0018564 | 0.0073242 | 0.033879 | 0.0086368 | -0.041191 | -0.003341 | 0.010318 | 0.032043 | 0 | 0.013733 | 0.064087 | 0.045776 | 0.018311 | -0.12817 | -0.022888 | 0.009155 | -0.15106 | -0.027466 | 0.022888 | 0.027466 | -0.036621 | 4.3213 | 4.1748 | -117.4988 | 4.303 | 4.3671 | 0.19226 | -117.5125 | 4.3304 | 4.2664 | -117.572 | 4.2801 | 4.1519 | -0.11444 | -117.5217 | 4.3488 | 4.335 | 4.3167 | -117.6727 | 4.2755 | 4.3259 | 4.3121 | -117.5812
4021.1875 | 122.0993 | -4.628 | 117.54 | 0.0054168 | -0.00099541 | 0.071508 | 0.026511 | -0.0674 | -0.022885 | 0.0014292 | 0.014954 | 0.036015 | 0.0094912 | -0.042686 | -0.003982 | 0.012882 | 0.027466 | 0.018311 | 0.027466 | 0.064087 | 0.059509 | 0.004578 | -0.11444 | -0.004578 | 0.045776 | -0.10529 | -0.032043 | -0.009155 | 0.045776 | -0.050354 | 4.6326 | 4.5135 | -117.4805 | 4.6463 | 4.6921 | 0.17853 | -117.5125 | 4.6738 | 4.5776 | -117.572 | 4.6234 | 4.5227 | -0.054932 | -117.5491 | 4.6875 | 4.6555 | 4.6555 | -117.6544 | 4.5959 | 4.6188 | 4.6738 | -117.5903
4022.9688 | 121.701 | -3.0167 | 119.1696 | 0.013046 | -0.0016364 | 0.071508 | 0.030356 | -0.067614 | -0.027799 | -0.00070715 | 0.0073242 | 0.031315 | 0.007355 | -0.045677 | -0.0052636 | 0.012241 | -0.045776 | -0.004578 | 0.013733 | 0.036621 | 0.054932 | 0.013733 | -0.11902 | -0.086975 | 0.018311 | -0.13733 | -0.013733 | -0.013733 | 0.004578 | -0.050354 | 3.0304 | 2.8976 | -119.1147 | 3.0121 | 3.0533 | 0.15564 | -119.2154 | 3.0212 | 2.9663 | -119.1834 | 2.9297 | 2.8793 | -0.086975 | -119.1834 | 3.0716 | 2.9709 | 3.0304 | -119.2886 | 3.0029 | 3.0029 | 3.035 | -119.22
4024.6875 | 122.1268 | -4.9026 | 117.1967 | 0.0054168 | 0.00092719 | 0.071081 | 0.028647 | -0.068896 | -0.025876 | -0.00027975 | 0.0073242 | 0.030461 | 0.0082096 | -0.0429 | -0.0063318 | 0.011386 | -0.045776 | -0.022888 | 0.004578 | 0.045776 | 0.036621 | 0.018311 | -0.12817 | -0.082397 | 0.004578 | -0.14191 | -0.013733 | 0.004578 | 0.009155 | -0.054932 | 4.921 | 4.7745 | -117.16 | 4.8798 | 4.9484 | 0.17395 | -117.2424 | 4.9118 | 4.8477 | -117.2104 | 4.8203 | 4.7607 | -0.086975 | -117.1921 | 4.9393 | 4.8569 | 4.9072 | -117.3248 | 4.8889 | 4.9072 | 4.9072 | -117.2516
4026.4531 | 122.168 | -4.0237 | 118.0573 | 0.0054168 | 0.0039178 | 0.073431 | 0.025656 | -0.070177 | -0.027585 | -0.00027975 | -0.0003053 | 0.028752 | 0.0037234 | -0.0429 | -0.00505 | 0.011386 | 0.050354 | 0.09613 | 0.11444 | 0.091553 | 0.009155 | 0.054932 | -0.073242 | 0.022888 | 0.10986 | -0.018311 | -0.07782 | -0.045776 | 0.059509 | -0.009155 | 4.0787 | 3.9505 | -118.0481 | 4.1199 | 4.1153 | 0.16479 | -118.0069 | 4.0833 | 4.0146 | -118.1351 | 4.0466 | 4.0054 | -0.009156 | -118.103 | 4.0329 | 4.0741 | 4.1382 | -118.1305 | 3.9459 | 3.978 | 4.1336 | -118.0664
4028.1562 | 122.287 | -3.7308 | 118.309 | 0.020676 | 0.0041314 | 0.074712 | 0.028433 | -0.071245 | -0.027799 | -0.003057 | 0.014954 | 0.028752 | 0.006287 | -0.0429 | -0.0076136 | 0.012454 | 0.004578 | 0.036621 | 0.073242 | 0.07782 | 0.032043 | 0.045776 | -0.07782 | -0.013733 | 0.073242 | -0.032043 | -0.041199 | -0.032043 | 0.050354 | -0.032043 | 3.7765 | 3.653 | -118.277 | 3.7674 | 3.8086 | 0.15564 | -118.3044 | 3.7811 | 3.6987 | -118.3502 | 3.717 | 3.6987 | 0 | -118.3411 | 3.7628 | 3.7354 | 3.804 | -118.3868 | 3.6896 | 3.6987 | 3.804 | -118.3411
4029.875 | 121.3165 | -120.9869 | 0.10986 | 0.020676 | 0.0045588 | 0.075781 | 0.02886 | -0.068896 | -0.024594 | -0.0036978 | 0.014954 | 0.031742 | 0.0041506 | -0.045036 | -0.0074 | 0.013522 | 0.086975 | 0.082397 | 0.10071 | 0.10529 | 0.045776 | 0.059509 | -0.041199 | 0.013733 | 0.07782 | -0.036621 | -0.022888 | 0.009155 | 0.09613 | 0.027466 | 121.0464 | 120.9457 | -0.064087 | 121.0693 | 121.0922 | 0.14649 | -0.022888 | 121.0831 | 121.0144 | -0.13275 | 121.0007 | 120.9503 | -0.064087 | -0.10071 | 121.0327 | 121.0739 | 121.0876 | -0.15106 | 120.9641 | 120.9961 | 121.0648 | -0.082397
4031.5781 | 121.3303 | -120.1904 | 1.1261 | 0.013046 | -0.0031318 | 0.071935 | 0.028647 | -0.068255 | -0.021817 | -0.0017752 | 0.0073242 | 0.033451 | 0.0088504 | -0.042259 | -0.0074 | 0.0090363 | 0.009155 | -0.022888 | 0.022888 | 0.068665 | 0.10986 | 0.036621 | -0.10071 | -0.041199 | 0.004578 | -0.11902 | 0.036621 | 0.027466 | 0.068665 | -0.018311 | 120.2271 | 120.0897 | -1.0162 | 120.1675 | 120.2591 | 0.16937 | -1.1169 | 120.2591 | 120.1721 | -1.0895 | 120.1492 | 120.0714 | -0.10071 | -1.0986 | 120.3003 | 120.1996 | 120.2133 | -1.2268 | 120.2271 | 120.2179 | 120.195 | -1.1444
4033.2969 | 121.3852 | -6.3995 | 114.2578 | 0.0054168 | 0.0041314 | 0.069372 | 0.027152 | -0.067614 | -0.023099 | 0.0012154 | 0.0073242 | 0.028752 | 0.0065006 | -0.041832 | -0.0069726 | 0.013736 | 0.068665 | 0.091553 | 0.10529 | 0.11902 | 0.013733 | 0.059509 | -0.073242 | 0.064087 | 0.09613 | -0.018311 | -0.073242 | -0.073242 | 0.059509 | -0.009155 | 6.459 | 6.3263 | -114.2441 | 6.4911 | 6.5186 | 0.19226 | -114.1891 | 6.459 | 6.3904 | -114.3311 | 6.4636 | 6.3812 | -0.009156 | -114.3311 | 6.4133 | 6.4682 | 6.5048 | -114.3311 | 6.3263 | 6.3263 | 6.4957 | -114.267
4035.0156 | 121.2479 | -8.6517 | 105.8533 | -0.0022127 | -0.0039862 | 0.07044 | 0.02587 | -0.066332 | -0.01904 | 0.00057465 | 0.0073242 | 0.034947 | 0.0082096 | -0.04055 | -0.001632 | 0.0116 | -0.009155 | -0.050354 | -0.027466 | 0.041199 | 0.054932 | 0 | -0.13733 | -0.064087 | -0.050354 | -0.17853 | -0.032043 | -0.004578 | 0.018311 | -0.036621 | 8.6517 | 8.5144 | -105.7983 | 8.6014 | 8.6929 | 0.17853 | -105.8624 | 8.67 | 8.6151 | -105.8853 | 8.5876 | 8.4732 | -0.14191 | -105.8578 | 8.7067 | 8.6426 | 8.6243 | -105.9906 | 8.6197 | 8.6472 | 8.6014 | -105.8899
4036.7656 | 121.1151 | -8.8852 | 112.1613 | 0.0054168 | 0.0028498 | 0.074285 | 0.028433 | -0.067828 | -0.02844 | -0.00049335 | 0.0073242 | 0.029179 | 0.0050052 | -0.045463 | -0.0093226 | 0.013095 | 0.082397 | 0.13275 | 0.13733 | 0.11902 | 0.022888 | 0.036621 | -0.082397 | 0.027466 | 0.14191 | 0.018311 | -0.059509 | -0.045776 | 0.059509 | -0.018311 | 8.9218 | 8.8028 | -112.1384 | 9.0179 | 9.0042 | 0.20142 | -112.0789 | 8.9447 | 8.8669 | -112.2208 | 8.9127 | 8.9035 | 0.036622 | -112.207 | 8.9081 | 8.9676 | 9.0225 | -112.2437 | 8.8257 | 8.8394 | 9.0271 | -112.1796
4038.4844 | 121.3486 | -6.5277 | 114.473 | 0.013046 | 0.0041314 | 0.072149 | 0.028006 | -0.06975 | -0.028653 | -0.0022024 | 0.022583 | 0.029606 | 0.0035098 | -0.043754 | -0.0086816 | 0.011173 | 0.09613 | 0.11902 | 0.1236 | 0.1236 | 0.004578 | 0.041199 | -0.086975 | 0.041199 | 0.13275 | -0.009155 | -0.082397 | -0.032043 | 0.068665 | -0.027466 | 6.5689 | 6.4407 | -114.4684 | 6.6467 | 6.6513 | 0.21057 | -114.3768 | 6.5964 | 6.5002 | -114.5554 | 6.5689 | 6.5186 | 0.018311 | -114.505 | 6.5323 | 6.6238 | 6.6513 | -114.5599 | 6.4453 | 6.4957 | 6.6605 | -114.5004
4040.2031 | 121.7514 | -107.9269 | 13.3255 | 0.0054168 | 0.0045588 | 0.071508 | 0.028647 | -0.068255 | -0.028653 | -0.0032706 | 0.014954 | 0.033238 | 0.0050052 | -0.043968 | -0.0065454 | 0.010104 | 0.10986 | 0.14191 | 0.16022 | 0.14648 | 0.054932 | 0.086975 | -0.054932 | 0.086975 | 0.16937 | 0.032043 | -0.022888 | -0.004578 | 0.09613 | 0.032043 | 108.0139 | 107.872 | -13.2706 | 108.0688 | 108.0734 | 0.20142 | -13.2156 | 108.0231 | 107.959 | -13.3484 | 108.0139 | 107.959 | 0 | -13.3301 | 107.9819 | 108.0368 | 108.0872 | -13.3804 | 107.9041 | 107.9224 | 108.0963 | -13.2935
4041.9688 | 121.3394 | -42.3431 | 78.9917 | 0.020676 | 0.004345 | 0.068945 | 0.024588 | -0.069537 | -0.023313 | 0.0022836 | 0.014954 | 0.031315 | 0.0035098 | -0.043113 | -0.0046228 | 0.011813 | 0.11444 | 0.082397 | 0.11444 | 0.13733 | 0.009155 | 0.054932 | -0.054932 | 0.073242 | 0.10986 | 0 | -0.064087 | -0.032043 | 0.07782 | -0.004578 | 42.3981 | 42.2882 | -78.9825 | 42.4255 | 42.4805 | 0.19226 | -78.8773 | 42.421 | 42.3386 | -79.0558 | 42.4164 | 42.3431 | 0.004578 | -79.0237 | 42.3523 | 42.4576 | 42.4576 | -79.0466 | 42.2791 | 42.3111 | 42.453 | -78.9963
4043.7188 | 121.3943 | -22.0184 | 99.4583 | 0.020676 | 0.006695 | 0.073431 | 0.022452 | -0.0674 | -0.02844 | -0.0026298 | -0.0003053 | 0.030888 | 0.0043644 | -0.043754 | -0.0052636 | 0.013522 | 0.050354 | 0.054932 | 0.073242 | 0.07782 | 0.041199 | 0.050354 | -0.091553 | -0.018311 | 0.036621 | -0.059509 | -0.073242 | -0.022888 | 0.054932 | -0.027466 | 22.0688 | 21.9269 | -99.4171 | 22.0734 | 22.0963 | 0.16937 | -99.408 | 22.0734 | 21.991 | -99.5316 | 22.0001 | 21.9589 | -0.032043 | -99.4812 | 22.0596 | 22.0688 | 22.0917 | -99.5499 | 21.9452 | 21.9955 | 22.0551 | -99.4858
4045.4375 | 121.1655 | -13.9755 | 107.1716 | 0.013046 | 0.003277 | 0.069158 | 0.031851 | -0.067614 | -0.027371 | -0.0015616 | 0.022583 | 0.028965 | 0.0067142 | -0.042686 | -0.010391 | 0.011813 | 0.086975 | 0.14191 | 0.14648 | 0.12817 | 0.041199 | 0.054932 | -0.07782 | 0.045776 | 0.14648 | 0.009155 | -0.073242 | -0.068665 | 0.064087 | -0.018311 | 14.0305 | 13.8977 | -107.1304 | 14.1174 | 14.1037 | 0.20599 | -107.0847 | 14.0396 | 13.9572 | -107.2449 | 14.0213 | 13.9847 | 0.027466 | -107.2403 | 14.0167 | 14.0625 | 14.122 | -107.2495 | 13.9023 | 13.9069 | 14.122 | -107.1899
4047.1562 | 120.8908 | -7.8369 | 113.0173 | 0.0054168 | -0.00078181 | 0.068517 | 0.029288 | -0.067614 | -0.022885 | -0.00027975 | 0.0073242 | 0.03217 | 0.010559 | -0.040977 | -0.0074 | 0.0088227 | 0.009155 | 0.004578 | 0.032043 | 0.045776 | 0.045776 | 0.013733 | -0.10986 | -0.054932 | 0.009155 | -0.12817 | -0.022888 | -0.013733 | -0.009155 | -0.050354 | 7.8506 | 7.7271 | -112.9715 | 7.8415 | 7.8827 | 0.15564 | -113.0081 | 7.8278 | 7.7866 | -113.0402 | 7.782 | 7.7087 | -0.07782 | -113.031 | 7.8827 | 7.8461 | 7.869 | -113.1271 | 7.814 | 7.8232 | 7.8461 | -113.0676
4048.9219 | 98.8861 | -8.0933 | 113.5437 | 0.0054168 | -0.004627 | 0.066595 | 0.029288 | -0.069109 | -0.017331 | -0.00027975 | 0.022583 | 0.034092 | 0.010773 | -0.040763 | -0.00505 | 0.0088227 | 0 | -0.022888 | 0.004578 | 0.054932 | 0.064087 | -0.009155 | -0.11444 | -0.009155 | 0.032043 | -0.10986 | -0.013733 | -0.009155 | 0.018311 | -0.050354 | 8.0841 | 7.9788 | -113.4796 | 8.0704 | 8.1482 | 0.16937 | -113.5437 | 8.1116 | 8.0429 | -113.5574 | 8.0841 | 7.9834 | -0.059509 | -113.5529 | 8.1573 | 8.0933 | 8.0978 | -113.6581 | 8.0795 | 8.0841 | 8.1253 | -113.5941
4050.6406 | 100.0397 | -21.1533 | 74.5056 | 0.0054168 | -0.0033454 | 0.070654 | 0.026724 | -0.066759 | -0.020749 | 0.0029244 | 0.014954 | 0.033879 | 0.0052188 | -0.042472 | -0.0027002 | 0.012027 | 0.032043 | 0.045776 | 0.036621 | 0.068665 | 0.054932 | 0.018311 | -0.10529 | 0.004578 | 0.041199 | -0.1236 | -0.018311 | -0.022888 | 0.050354 | -0.036621 | 21.1716 | 21.048 | -74.4507 | 21.199 | 21.2219 | 0.17395 | -74.4736 | 21.2036 | 21.1166 | -74.5239 | 21.1578 | 21.0297 | -0.086975 | -74.5285 | 21.2082 | 21.1853 | 21.1899 | -74.6109 | 21.1349 | 21.1304 | 21.1945 | -74.5422
4052.3594 | 121.1014 | -16.8961 | 103.8483 | 0.0054168 | 0.0028498 | 0.073858 | 0.026724 | -0.068255 | -0.02908 | -0.00027975 | -0.0003053 | 0.027683 | 0.0032962 | -0.044181 | -0.0074 | 0.01395 | 0.07782 | 0.13275 | 0.14648 | 0.1236 | 0.027466 | 0.036621 | -0.086975 | 0.045776 | 0.16937 | 0.013733 | -0.068665 | -0.032043 | 0.068665 | -0.022888 | 16.9327 | 16.8091 | -103.8208 | 17.0288 | 17.0197 | 0.21057 | -103.7704 | 16.9647 | 16.8732 | -103.9169 | 16.9418 | 16.9098 | 0.036621 | -103.8803 | 16.9235 | 16.9739 | 17.0425 | -103.9352 | 16.8274 | 16.864 | 17.0654 | -103.8712
4054.0781 | 111.3235 | -15.9668 | 100.5066 | 0.0054168 | -0.0020636 | 0.067022 | 0.02587 | -0.06505 | -0.019895 | 0.00207 | 0.0073242 | 0.034947 | 0.0067142 | -0.041191 | -0.0054772 | 0.011386 | -0.018311 | -0.059509 | -0.013733 | 0.036621 | 0.064087 | 0.018311 | -0.1236 | -0.045776 | -0.036621 | -0.16937 | -0.009155 | -0.009155 | 0.032043 | -0.045776 | 15.9851 | 15.8432 | -100.4425 | 15.9073 | 16.0034 | 0.16022 | -100.5249 | 15.9988 | 15.921 | -100.5157 | 15.921 | 15.7974 | -0.1236 | -100.5157 | 16.0309 | 15.9485 | 15.9531 | -100.6302 | 15.9576 | 15.9576 | 15.9302 | -100.5524
4055.7812 | 121.0098 | -14.1357 | 106.3477 | 0.013046 | 0.0037042 | 0.070013 | 0.028647 | -0.070605 | -0.024167 | -0.00027975 | 0.030213 | 0.02982 | 0.0077822 | -0.040123 | -0.0031274 | 0.012241 | -0.027466 | -0.027466 | 0.013733 | 0.036621 | 0.050354 | 0.022888 | -0.10071 | 0 | 0.032043 | -0.07782 | -0.027466 | -0.027466 | 0.068665 | -0.032043 | 14.1586 | 14.035 | -106.2973 | 14.1083 | 14.1724 | 0.13733 | -106.3751 | 14.2044 | 14.1037 | -106.3751 | 14.1357 | 14.0579 | -0.045777 | -106.3751 | 14.1861 | 14.1083 | 14.1495 | -106.4484 | 14.1083 | 14.1083 | 14.1678 | -106.3797
4057.4844 | 121.907 | -87.6801 | 33.7234 | 0.0054168 | 0.006695 | 0.069158 | 0.025656 | -0.069537 | -0.026517 | -0.001348 | 0.014954 | 0.032383 | 0.0050052 | -0.0429 | -0.0048364 | 0.01395 | 0.086975 | 0.10529 | 0.14191 | 0.15106 | 0.032043 | 0.07782 | -0.036621 | 0.073242 | 0.12817 | 0.004578 | -0.045776 | -0.032043 | 0.09613 | 0.009155 | 87.7579 | 87.6434 | -33.6914 | 87.7853 | 87.8311 | 0.18768 | -33.6365 | 87.7762 | 87.6892 | -33.7692 | 87.7533 | 87.6846 | -0.004577 | -33.7555 | 87.7121 | 87.767 | 87.822 | -33.7601 | 87.6343 | 87.648 | 87.8082 | -33.7143
4059.1875 | 121.8338 | -59.9808 | 61.4731 | 0.013046 | 0.0045588 | 0.071508 | 0.029074 | -0.070818 | -0.028012 | -0.0015616 | 0.014954 | 0.028965 | 0.0037234 | -0.044609 | -0.0088952 | 0.013736 | 0.018311 | 0.050354 | 0.07782 | 0.10529 | 0.041199 | 0.050354 | -0.068665 | -0.009155 | 0.10986 | -0.022888 | -0.041199 | -0.013733 | 0.059509 | 0.004578 | 60.0311 | 59.9121 | -61.4319 | 60.0311 | 60.0861 | 0.17395 | -61.4548 | 60.0403 | 59.9854 | -61.5143 | 59.9716 | 59.9579 | -0.027466 | -61.4868 | 60.022 | 59.9991 | 60.0586 | -61.5417 | 59.9396 | 59.967 | 60.0906 | -61.4685
4060.8906 | 112.6923 | -9.343 | 86.2152 | 0.013046 | -0.003559 | 0.067876 | 0.03121 | -0.0674 | -0.022244 | -0.00027975 | 0.014954 | 0.034092 | 0.007355 | -0.041618 | -0.0059046 | 0.010318 | -0.004578 | -0.041199 | 0.009155 | 0.064087 | 0.059509 | 0.004578 | -0.10071 | -0.041199 | 0.045776 | -0.11444 | -0.018311 | -0.013733 | 0.032043 | -0.041199 | 9.3475 | 9.2422 | -86.1557 | 9.3018 | 9.407 | 0.1648 | -86.2198 | 9.375 | 9.3018 | -86.2335 | 9.3018 | 9.2285 | -0.073242 | -86.2289 | 9.4025 | 9.3384 | 9.3521 | -86.3159 | 9.3246 | 9.3292 | 9.3887 | -86.2564
4062.625 | 121.8292 | -9.2239 | 111.5524 | 0.0054168 | 0.0047724 | 0.066595 | 0.024588 | -0.067828 | -0.024808 | 0.00036105 | 0.014954 | 0.033238 | 0.007355 | -0.039268 | -0.00505 | 0.013522 | 0.050354 | 0.041199 | 0.082397 | 0.09613 | 0.050354 | 0.022888 | -0.10071 | 0.041199 | 0.082397 | -0.022888 | -0.045776 | -0.054932 | 0.045776 | 0 | 9.2468 | 9.1232 | -111.5021 | 9.2651 | 9.3201 | 0.19684 | -111.5021 | 9.2697 | 9.2239 | -111.5982 | 9.2651 | 9.2011 | -0.022888 | -111.6074 | 9.2743 | 9.2743 | 9.3063 | -111.6531 | 9.1782 | 9.169 | 9.3063 | -111.5524
4064.3281 | 121.431 | -11.5997 | 109.845 | 0.013046 | 0.0069086 | 0.073858 | 0.026297 | -0.069109 | -0.027371 | -0.00049335 | 0.0073242 | 0.02982 | 0.004578 | -0.045463 | -0.0063318 | 0.01395 | 0.054932 | 0.086975 | 0.11902 | 0.07782 | -0.013733 | 0.045776 | -0.07782 | 0.009155 | 0.068665 | -0.036621 | -0.064087 | -0.036621 | 0.041199 | -0.036621 | 11.6455 | 11.5219 | -109.8587 | 11.6867 | 11.6776 | 0.15564 | -109.79 | 11.6409 | 11.5631 | -109.9091 | 11.6089 | 11.5631 | 0 | -109.8816 | 11.586 | 11.6547 | 11.7188 | -109.9228 | 11.5356 | 11.5631 | 11.6684 | -109.8816
4066.0469 | 121.3577 | -10.0113 | 110.9253 | 0.0054168 | 0.0056268 | 0.073858 | 0.025443 | -0.067614 | -0.030149 | -0.0024162 | -0.0003053 | 0.028965 | 0.0060732 | -0.045677 | -0.0054772 | 0.013736 | 0.018311 | 0.022888 | 0.073242 | 0.07782 | 0.027466 | 0.054932 | -0.10071 | -0.041199 | 0.041199 | -0.054932 | -0.032043 | -0.013733 | 0.059509 | -0.027466 | 10.0662 | 9.9106 | -110.8978 | 10.0342 | 10.0891 | 0.17853 | -110.907 | 10.0708 | 9.9838 | -110.9573 | 9.9701 | 9.9564 | -0.027466 | -110.939 | 10.0388 | 10.0296 | 10.0845 | -111.026 | 9.9792 | 9.9976 | 10.0525 | -110.9528
4067.75 | 121.8613 | -8.8806 | 111.9736 | 0.028305 | 0.0041314 | 0.074072 | 0.024374 | -0.069109 | -0.02908 | -0.00070715 | 0.014954 | 0.03217 | 0.0043644 | -0.043541 | -0.0063318 | 0.012454 | 0.022888 | 0.022888 | 0.064087 | 0.082397 | 0.036621 | 0.032043 | -0.10529 | -0.027466 | 0.045776 | -0.059509 | -0.036621 | -0.027466 | 0.068665 | -0.032043 | 8.9127 | 8.7753 | -111.937 | 8.9035 | 8.963 | 0.18768 | -111.9507 | 8.9493 | 8.8486 | -112.0102 | 8.8531 | 8.8211 | -0.027466 | -112.001 | 8.9172 | 8.9035 | 8.9447 | -112.0789 | 8.844 | 8.8531 | 8.9264 | -112.0056
4069.4531 | 121.0556 | -10.5377 | 111.1496 | 0.0054168 | 0.0037042 | 0.073858 | 0.029501 | -0.068468 | -0.025876 | -0.00049335 | 0.022583 | 0.02982 | 0.006287 | -0.043754 | -0.0093226 | 0.010318 | 0.091553 | 0.10529 | 0.13275 | 0.12817 | 0.018311 | 0.054932 | -0.082397 | 0.059509 | 0.15564 | 0.018311 | -0.064087 | -0.050354 | 0.050354 | -0.032043 | 10.5927 | 10.4553 | -111.1313 | 10.643 | 10.6659 | 0.21057 | -111.058 | 10.5881 | 10.5057 | -111.2137 | 10.5972 | 10.556 | 0.050354 | -111.2 | 10.556 | 10.6293 | 10.6705 | -111.232 | 10.4736 | 10.4874 | 10.6934 | -111.1816
4071.1562 | 101.3535 | -9.407 | 92.157 | 0.0054168 | 0.00049979 | 0.071081 | 0.031424 | -0.069537 | -0.022885 | -0.0019888 | -0.0003053 | 0.030247 | 0.0097048 | -0.041404 | -0.0076136 | 0.0073273 | -0.004578 | -0.027466 | 0.004578 | 0.022888 | 0.073242 | -0.004578 | -0.12817 | -0.068665 | -0.009155 | -0.14191 | -0.027466 | 0.009155 | 0.013733 | -0.050354 | 9.4025 | 9.2789 | -92.0837 | 9.3796 | 9.4299 | 0.15106 | -92.1616 | 9.4208 | 9.3567 | -92.1844 | 9.3384 | 9.2651 | -0.091553 | -92.1478 | 9.4803 | 9.4025 | 9.4116 | -92.2852 | 9.3796 | 9.4162 | 9.3979 | -92.2073
4072.8906 | 121.4264 | -10.2219 | 110.8704 | 0.0054168 | 0.0047724 | 0.071722 | 0.027152 | -0.070391 | -0.029721 | -0.00049335 | 0.0073242 | 0.030033 | 0.0058596 | -0.043113 | -0.0063318 | 0.011386 | 0.022888 | 0.032043 | 0.059509 | 0.07782 | 0.041199 | 0.032043 | -0.07782 | 0.004578 | 0.036621 | -0.068665 | -0.054932 | -0.027466 | 0.054932 | -0.041199 | 10.2539 | 10.144 | -110.8292 | 10.2539 | 10.2997 | 0.15564 | -110.8475 | 10.2768 | 10.1807 | -110.9253 | 10.2264 | 10.1532 | -0.027466 | -110.8978 | 10.2631 | 10.2448 | 10.2814 | -110.9482 | 10.1669 | 10.1944 | 10.2585 | -110.9116
4074.6562 | 121.4813 | -9.9426 | 111.0489 | 0.0054168 | 0.0054132 | 0.071508 | 0.025229 | -0.066759 | -0.026944 | 0.00057465 | 0.0073242 | 0.031956 | 0.005646 | -0.042686 | -0.0065454 | 0.010532 | 0.091553 | 0.091553 | 0.10529 | 0.10529 | 0.013733 | 0.050354 | -0.073242 | 0.045776 | 0.073242 | -0.027466 | -0.050354 | -0.045776 | 0.050354 | -0.009155 | 9.993 | 9.8694 | -111.0352 | 10.0342 | 10.0479 | 0.17853 | -110.9573 | 9.993 | 9.9335 | -111.0992 | 9.9884 | 9.9152 | -0.018311 | -111.0947 | 9.9564 | 10.0342 | 10.0479 | -111.1221 | 9.8923 | 9.8969 | 10.0159 | -111.058
4076.375 | 121.257 | -10.6339 | 110.5362 | 0.0054168 | 0.004345 | 0.069799 | 0.027152 | -0.066759 | -0.022031 | 0.00078825 | 0.0073242 | 0.033665 | 0.0047916 | -0.043541 | -0.0054772 | 0.013095 | 0.086975 | 0.082397 | 0.1236 | 0.12817 | 0.018311 | 0.050354 | -0.07782 | 0.064087 | 0.10986 | -0.013733 | -0.073242 | -0.050354 | 0.059509 | -0.009155 | 10.6842 | 10.556 | -110.5179 | 10.7162 | 10.762 | 0.20599 | -110.4492 | 10.6934 | 10.6247 | -110.6094 | 10.6979 | 10.6201 | -0.004578 | -110.5865 | 10.6522 | 10.7208 | 10.7574 | -110.614 | 10.5606 | 10.5835 | 10.7437 | -110.5453
4078.0781 | 121.4401 | -10.2219 | 111.3052 | 0.013046 | 0.0037042 | 0.073431 | 0.027152 | -0.067828 | -0.025662 | 0.00057465 | 0.0073242 | 0.028752 | 0.0043644 | -0.042259 | -0.0052636 | 0.014591 | 0.018311 | 0.009155 | 0.050354 | 0.07782 | 0.050354 | 0.027466 | -0.10071 | 0.004578 | 0.054932 | -0.041199 | -0.050354 | -0.036621 | 0.036621 | -0.036621 | 10.2493 | 10.1212 | -111.2549 | 10.231 | 10.2997 | 0.17853 | -111.2869 | 10.2585 | 10.1852 | -111.3556 | 10.2264 | 10.1807 | -0.004578 | -111.3419 | 10.2722 | 10.2402 | 10.2722 | -111.4059 | 10.1715 | 10.1852 | 10.2768 | -111.3419
4079.7812 | 121.4264 | -9.9884 | 111.5433 | 0.013046 | 0.0051996 | 0.073858 | 0.026724 | -0.070605 | -0.024594 | -0.00027975 | 0.014954 | 0.031956 | 0.003937 | -0.043541 | -0.0041956 | 0.010745 | 0.082397 | 0.091553 | 0.09613 | 0.09613 | 0.018311 | 0.064087 | -0.082397 | 0.045776 | 0.082397 | -0.013733 | -0.064087 | -0.032043 | 0.073242 | -0.013733 | 10.0525 | 9.906 | -111.525 | 10.08 | 10.0845 | 0.17853 | -111.4609 | 10.0616 | 9.9747 | -111.6074 | 10.0342 | 9.9747 | 0 | -111.5753 | 10.0067 | 10.0708 | 10.0845 | -111.6257 | 9.9243 | 9.9564 | 10.0708 | -111.557
4081.4844 | 121.1792 | -7.7408 | 112.9532 | -0.0022127 | 0.0037042 | 0.07044 | 0.022665 | -0.065905 | -0.022244 | -6.615e-05 | 0.014954 | 0.03217 | 0.0035098 | -0.043113 | -0.00505 | 0.011173 | 0.054932 | 0.022888 | 0.068665 | 0.082397 | 0.032043 | 0.041199 | -0.073242 | 0.054932 | 0.082397 | -0.041199 | -0.064087 | -0.032043 | 0.059509 | -0.013733 | 7.782 | 7.6675 | -112.9211 | 7.7637 | 7.8232 | 0.15564 | -112.8983 | 7.8003 | 7.7271 | -113.0173 | 7.7957 | 7.6996 | -0.027466 | -112.9852 | 7.7728 | 7.7957 | 7.8094 | -113.0264 | 7.6767 | 7.7087 | 7.8232 | -112.9669
4083.2031 | 121.1746 | -7.7591 | 113.2233 | 0.0054168 | 0.0034906 | 0.071294 | 0.025229 | -0.06505 | -0.022458 | 0.00078825 | 0.0073242 | 0.032383 | 0.004578 | -0.044395 | -0.0024866 | 0.0116 | 0.068665 | 0.050354 | 0.068665 | 0.091553 | 0.032043 | 0.036621 | -0.082397 | 0.054932 | 0.082397 | -0.027466 | -0.068665 | -0.041199 | 0.064087 | -0.009155 | 7.7957 | 7.6767 | -113.1912 | 7.8094 | 7.8506 | 0.17395 | -113.1546 | 7.8232 | 7.7499 | -113.2919 | 7.814 | 7.7316 | -0.018311 | -113.2645 | 7.7911 | 7.8278 | 7.8278 | -113.3057 | 7.6904 | 7.7179 | 7.8415 | -113.2324
4084.9688 | 104.4525 | -7.6813 | 113.0676 | 0.020676 | -0.0024908 | 0.072576 | 0.030997 | -0.06975 | -0.024381 | -0.001348 | 0.0073242 | 0.034092 | 0.0084232 | -0.042686 | -0.0059046 | 0.010104 | -0.018311 | -0.041199 | 0 | 0.032043 | 0.064087 | 0 | -0.1236 | -0.073242 | -0.013733 | -0.14191 | -0.018311 | 0.018311 | 0.013733 | -0.082397 | 7.6813 | 7.5577 | -113.0035 | 7.6401 | 7.7133 | 0.15564 | -113.0859 | 7.695 | 7.5989 | -113.0859 | 7.608 | 7.5394 | -0.05951 | -113.0493 | 7.7454 | 7.663 | 7.6813 | -113.1912 | 7.663 | 7.6996 | 7.6675 | -113.15
4086.6719 | 92.1661 | -8.194 | 86.3892 | 0.013046 | -0.00185 | 0.068517 | 0.028006 | -0.067187 | -0.02139 | -6.615e-05 | 0.0073242 | 0.03281 | 0.009064 | -0.042259 | -0.0063318 | 0.0092499 | 0.009155 | -0.036621 | 0.009155 | 0.059509 | 0.059509 | 0.013733 | -0.1236 | -0.032043 | 0.041199 | -0.11902 | -0.027466 | -0.018311 | 0.018311 | -0.054932 | 8.2077 | 8.0704 | -86.3297 | 8.1573 | 8.2535 | 0.1831 | -86.38 | 8.2123 | 8.139 | -86.4166 | 8.1619 | 8.075 | -0.064087 | -86.4075 | 8.2535 | 8.2031 | 8.2031 | -86.5128 | 8.1665 | 8.1757 | 8.2352 | -86.4441
4088.4062 | 103.5507 | -7.9147 | 97.0413 | 0.0054168 | 0.00049979 | 0.067876 | 0.029074 | -0.067614 | -0.021176 | 0.0014292 | 0.014954 | 0.033879 | 0.010773 | -0.040763 | -0.0037684 | 0.012668 | -0.004578 | -0.004578 | 0.018311 | 0.054932 | 0.059509 | 0.009155 | -0.11902 | -0.022888 | -0.004578 | -0.16479 | -0.036621 | -0.009155 | 0.022888 | -0.045776 | 7.9239 | 7.7957 | -96.9818 | 7.9102 | 7.9697 | 0.17395 | -97.0459 | 7.9376 | 7.869 | -97.0779 | 7.8918 | 7.7499 | -0.11902 | -97.0505 | 7.9742 | 7.9102 | 7.933 | -97.1603 | 7.8781 | 7.9056 | 7.9102 | -97.0871
4090.1094 | 110.8475 | -7.9834 | 113.5345 | 0.0054168 | -0.0016364 | 0.067876 | 0.028647 | -0.067614 | -0.021817 | 0.0027108 | 0.014954 | 0.03281 | 0.009064 | -0.041832 | -0.0035546 | 0.011386 | -0.054932 | -0.059509 | -0.032043 | 0.036621 | 0.041199 | 0.009155 | -0.11444 | -0.064087 | -0.045776 | -0.17853 | -0.022888 | 0 | 0.004578 | -0.054932 | 7.9926 | 7.869 | -113.4933 | 7.9239 | 8.02 | 0.15106 | -113.5895 | 7.988 | 7.9285 | -113.5574 | 7.9193 | 7.8049 | -0.1236 | -113.5345 | 8.0246 | 7.9285 | 7.9514 | -113.649 | 7.9605 | 7.9834 | 7.9376 | -113.5895
4091.8438 | 121.4996 | -8.5464 | 112.5458 | 0.013046 | 0.0037042 | 0.071294 | 0.029074 | -0.070818 | -0.032285 | -6.615e-05 | 0.0073242 | 0.026188 | 0.007355 | -0.044181 | -0.0099634 | 0.014163 | -0.032043 | 0.032043 | 0.064087 | 0.073242 | 0.027466 | 0.032043 | -0.082397 | -0.032043 | 0.045776 | -0.041199 | -0.041199 | -0.027466 | 0.054932 | -0.054932 | 8.5785 | 8.4641 | -112.5183 | 8.5785 | 8.6197 | 0.15564 | -112.5778 | 8.6014 | 8.4915 | -112.587 | 8.5144 | 8.5052 | 0.013733 | -112.5732 | 8.5739 | 8.5144 | 8.6105 | -112.6282 | 8.5052 | 8.519 | 8.5922 | -112.6007
4093.5625 | 104.6265 | -8.844 | 94.1071 | 0.0054168 | -0.0016364 | 0.072149 | 0.029715 | -0.068041 | -0.026517 | -0.0022024 | 0.014954 | 0.029606 | 0.007996 | -0.042259 | -0.0082544 | 0.012027 | -0.054932 | -0.027466 | -0.004578 | 0.027466 | 0.07782 | 0.013733 | -0.12817 | -0.082397 | -0.004578 | -0.13275 | -0.004578 | 0.004578 | 0.009155 | -0.07782 | 8.8577 | 8.7158 | -94.0292 | 8.8165 | 8.8715 | 0.15564 | -94.162 | 8.8531 | 8.7662 | -94.1116 | 8.7616 | 8.7112 | -0.054931 | -94.1025 | 8.9218 | 8.7891 | 8.8394 | -94.2352 | 8.8394 | 8.8486 | 8.8394 | -94.1849
4095.2969 | 121.5454 | -8.7433 | 112.3032 | 0.0054168 | 0.0039178 | 0.073431 | 0.027792 | -0.066759 | -0.030149 | -0.0019888 | 0.014954 | 0.028324 | 0.0065006 | -0.042472 | -0.0080408 | 0.013309 | -0.013733 | 0.041199 | 0.064087 | 0.073242 | 0.041199 | 0.036621 | -0.091553 | -0.009155 | 0.07782 | -0.013733 | -0.041199 | -0.032043 | 0.054932 | -0.022888 | 8.7799 | 8.6517 | -112.262 | 8.7845 | 8.8165 | 0.16479 | -112.3169 | 8.7982 | 8.7204 | -112.3444 | 8.7341 | 8.7296 | 0.009155 | -112.3352 | 8.7845 | 8.7296 | 8.8074 | -112.3947 | 8.7021 | 8.7112 | 8.8211 | -112.326
4097.0312 | 121.5454 | -8.8028 | 112.6648 | 0.013046 | 0.0071222 | 0.071508 | 0.028647 | -0.068255 | -0.028012 | -0.00092075 | 0.0073242 | 0.030033 | 0.0065006 | -0.043113 | -0.008468 | 0.010318 | 0.041199 | 0.068665 | 0.10529 | 0.10071 | 0.018311 | 0.045776 | -0.086975 | 0.018311 | 0.11902 | -0.004578 | -0.068665 | -0.045776 | 0.059509 | -0.032043 | 8.8486 | 8.7158 | -112.6465 | 8.8715 | 8.9035 | 0.18768 | -112.6236 | 8.8623 | 8.7708 | -112.7335 | 8.8211 | 8.7982 | 0.027465 | -112.7106 | 8.8211 | 8.844 | 8.9081 | -112.7518 | 8.7341 | 8.757 | 8.9218 | -112.6968
4098.7344 | 121.2387 | -15.4175 | 101.8982 | 0.013046 | 0.0034906 | 0.072363 | 0.028433 | -0.069964 | -0.025022 | -0.0026298 | -0.0003053 | 0.030888 | 0.0060732 | -0.043968 | -0.0078272 | 0.010318 | 0.09613 | 0.12817 | 0.13733 | 0.11902 | 0.018311 | 0.041199 | -0.091553 | 0.045776 | 0.13275 | 0.004578 | -0.064087 | -0.036621 | 0.059509 | -0.013733 | 15.4587 | 15.3259 | -101.8799 | 15.5457 | 15.5365 | 0.21057 | -101.8021 | 15.477 | 15.4037 | -101.9623 | 15.4633 | 15.4221 | 0.018311 | -101.9348 | 15.4358 | 15.5136 | 15.5548 | -101.9897 | 15.3534 | 15.3809 | 15.5502 | -101.9119
4100.4688 | 121.9482 | -8.9081 | 111.8134 | 0.0054168 | 0.0028498 | 0.070013 | 0.024374 | -0.066759 | -0.020108 | -0.0019888 | 0.014954 | 0.033451 | 0.0060732 | -0.041191 | -0.003341 | 0.010104 | -0.013733 | -0.059509 | -0.032043 | 0.022888 | 0.073242 | 0.004578 | -0.1236 | -0.054932 | -0.054932 | -0.15106 | -0.027466 | 0.018311 | 0.004578 | -0.036621 | 8.9127 | 8.7845 | -111.7401 | 8.8486 | 8.931 | 0.14648 | -111.8271 | 8.9127 | 8.8715 | -111.8408 | 8.8531 | 8.757 | -0.11444 | -111.795 | 8.9813 | 8.8943 | 8.876 | -111.937 | 8.8806 | 8.9264 | 8.8531 | -111.85
4102.1719 | 121.9803 | -95.018 | 26.3809 | -0.0022127 | 0.0026362 | 0.067876 | 0.023947 | -0.069109 | -0.023953 | 0.003138 | 0.014954 | 0.033879 | 0.006287 | -0.044181 | -0.0044092 | 0.012882 | 0.10529 | 0.1236 | 0.1236 | 0.14191 | 0.054932 | 0.082397 | -0.054932 | 0.082397 | 0.11902 | -0.004578 | -0.018311 | -0.032043 | 0.082397 | 0.009155 | 95.1004 | 94.9631 | -26.326 | 95.1416 | 95.1599 | 0.19684 | -26.2756 | 95.1004 | 95.0272 | -26.3992 | 95.1004 | 95.0134 | -0.013733 | -26.413 | 95.0729 | 95.1233 | 95.1416 | -26.4359 | 94.9997 | 94.986 | 95.137 | -26.3718
4103.9375 | 121.5454 | -9.3109 | 112.4359 | -0.0022127 | 0.004345 | 0.070226 | 0.028433 | -0.06975 | -0.027585 | 0.0010018 | 0.0073242 | 0.028111 | 0.0069278 | -0.044395 | -0.008468 | 0.011386 | 0.009155 | 0.027466 | 0.068665 | 0.064087 | 0.050354 | 0.032043 | -0.09613 | -0.018311 | 0.054932 | -0.068665 | -0.059509 | -0.032043 | 0.045776 | -0.022888 | 9.343 | 9.2148 | -112.3856 | 9.3384 | 9.375 | 0.16022 | -112.4268 | 9.3567 | 9.288 | -112.4954 | 9.2926 | 9.2422 | -0.045777 | -112.468 | 9.3613 | 9.3201 | 9.3796 | -112.532 | 9.2514 | 9.2789 | 9.3658 | -112.4588
4105.6562 | 121.9299 | -8.5648 | 112.5137 | 0.013046 | 0.0034906 | 0.070013 | 0.031638 | -0.065264 | -0.025876 | -0.001348 | -0.0003053 | 0.029606 | 0.006287 | -0.04055 | -0.0076136 | 0.012027 | 0.082397 | 0.10071 | 0.1236 | 0.10986 | 0.022888 | 0.059509 | -0.09613 | 0.059509 | 0.13733 | -0.004578 | -0.059509 | -0.032043 | 0.064087 | -0.013733 | 8.6243 | 8.4686 | -112.4908 | 8.6655 | 8.6746 | 0.20599 | -112.4313 | 8.6288 | 8.551 | -112.5732 | 8.6243 | 8.5602 | 0.009155 | -112.5458 | 8.5876 | 8.6472 | 8.6884 | -112.6099 | 8.5052 | 8.5327 | 8.7021 | -112.5275
4107.375 | 108.2108 | -9.2011 | 102.5253 | 0.0054168 | -0.0012092 | 0.071294 | 0.029288 | -0.066759 | -0.024594 | -0.0022024 | -0.0003053 | 0.033238 | 0.0067142 | -0.040123 | -0.0065454 | 0.011173 | -0.004578 | 0.009155 | 0.018311 | 0.050354 | 0.045776 | 0.013733 | -0.11902 | -0.064087 | 0.018311 | -0.14191 | 0 | -0.004578 | 0.018311 | -0.045776 | 9.2148 | 9.082 | -102.4796 | 9.2102 | 9.2514 | 0.16937 | -102.5299 | 9.2194 | 9.1553 | -102.5253 | 9.137 | 9.0591 | -0.096131 | -102.5299 | 9.2468 | 9.1965 | 9.2194 | -102.6443 | 9.2011 | 9.1965 | 9.2194 | -102.5711
4109.125 | 121.1792 | -8.3817 | 113.4338 | 0.0054168 | 0.0030634 | 0.070654 | 0.028647 | -0.069109 | -0.027371 | -0.00049335 | -0.0003053 | 0.030033 | 0.007355 | -0.043113 | -0.006759 | 0.0088227 | 0.064087 | 0.12817 | 0.13733 | 0.13275 | 0.041199 | 0.041199 | -0.082397 | 0.041199 | 0.13733 | 0.004578 | -0.059509 | -0.041199 | 0.073242 | -0.022888 | 8.4229 | 8.2993 | -113.3926 | 8.5098 | 8.5144 | 0.21515 | -113.3698 | 8.4549 | 8.3588 | -113.4933 | 8.4229 | 8.3862 | 0.027466 | -113.475 | 8.4229 | 8.4457 | 8.519 | -113.5162 | 8.3221 | 8.3405 | 8.519 | -113.4567
4110.8438 | 100.8774 | -14.1769 | 92.8757 | 0.0054168 | -0.0014228 | 0.071722 | 0.030569 | -0.069323 | -0.021604 | -6.615e-05 | 0.0073242 | 0.033665 | 0.0086368 | -0.040977 | -0.00505 | 0.0096771 | -0.018311 | -0.027466 | -0.032043 | 0.027466 | 0.082397 | -0.013733 | -0.10986 | -0.050354 | -0.018311 | -0.14191 | 0.013733 | -0.018311 | 0.027466 | -0.059509 | 14.1632 | 14.0671 | -92.7933 | 14.1495 | 14.2044 | 0.13733 | -92.894 | 14.2044 | 14.1174 | -92.8619 | 14.1266 | 14.035 | -0.082398 | -92.894 | 14.2593 | 14.1586 | 14.1449 | -92.9855 | 14.1907 | 14.1586 | 14.1586 | -92.9352
4112.5781 | 121.2341 | -8.2535 | 113.0264 | 0.013046 | 0.0017816 | 0.070226 | 0.028647 | -0.070177 | -0.029294 | -0.0017752 | 0.014954 | 0.030247 | 0.0065006 | -0.0429 | -0.0061182 | 0.012241 | 0.064087 | 0.1236 | 0.11444 | 0.11902 | 0.036621 | 0.032043 | -0.068665 | 0.064087 | 0.15106 | 0.004578 | -0.054932 | -0.045776 | 0.068665 | 0.004578 | 8.2855 | 8.1848 | -112.9898 | 8.3771 | 8.3725 | 0.18768 | -112.9623 | 8.3221 | 8.2581 | -113.0814 | 8.3176 | 8.2581 | 0 | -113.0722 | 8.2901 | 8.3176 | 8.3679 | -113.0951 | 8.1985 | 8.2077 | 8.4045 | -113.0219
4114.3125 | 115.0177 | -8.0887 | 104.4754 | 0.0054168 | 0.00049979 | 0.070654 | 0.032065 | -0.068041 | -0.025022 | -0.00027975 | -0.0003053 | 0.031315 | 0.0069278 | -0.041191 | -0.006759 | 0.011173 | 0.018311 | 0.054932 | 0.059509 | 0.082397 | 0.041199 | 0.022888 | -0.10071 | -0.041199 | 0.036621 | -0.10529 | -0.022888 | 0 | 0.013733 | -0.059509 | 8.1116 | 7.988 | -104.4342 | 8.1436 | 8.1711 | 0.18311 | -104.4571 | 8.1024 | 8.0292 | -104.4983 | 8.0475 | 7.9834 | -0.045777 | -104.4754 | 8.1299 | 8.107 | 8.1482 | -104.5761 | 8.0658 | 8.0887 | 8.1253 | -104.5349
4116.0469 | 121.4905 | -7.7316 | 113.4476 | 0.013046 | -0.00078181 | 0.07044 | 0.031424 | -0.068041 | -0.026944 | -0.0011344 | 0.014954 | 0.029606 | 0.005646 | -0.043327 | -0.0061182 | 0.011386 | 0.068665 | 0.10529 | 0.1236 | 0.11902 | 0.027466 | 0.027466 | -0.09613 | 0.027466 | 0.13275 | -0.027466 | -0.068665 | -0.036621 | 0.059509 | -0.032043 | 7.7591 | 7.6355 | -113.4201 | 7.8369 | 7.8506 | 0.21515 | -113.3789 | 7.7911 | 7.6996 | -113.5162 | 7.7591 | 7.7042 | 0.004577 | -113.4842 | 7.7591 | 7.8003 | 7.8552 | -113.5437 | 7.663 | 7.695 | 7.8644 | -113.4796
4117.75 | 121.6827 | -7.5302 | 111.7264 | 0.0054168 | -0.0022772 | 0.069158 | 0.029715 | -0.069323 | -0.02139 | -0.0015616 | -0.0003053 | 0.033451 | 0.005646 | -0.040763 | -0.006759 | 0.010745 | -0.032043 | -0.036621 | -0.018311 | 0.018311 | 0.059509 | 0.004578 | -0.12817 | -0.082397 | -0.009155 | -0.14191 | 0.004578 | 0 | 0.018311 | -0.059509 | 7.5348 | 7.402 | -111.6669 | 7.4936 | 7.5485 | 0.14649 | -111.7584 | 7.5485 | 7.4707 | -111.7218 | 7.4478 | 7.3883 | -0.082398 | -111.7264 | 7.5897 | 7.4982 | 7.5119 | -111.8546 | 7.5348 | 7.5302 | 7.5211 | -111.7859
4119.4844 | 121.8613 | -7.5577 | 113.6581 | 0.0054168 | -0.0012092 | 0.068731 | 0.025229 | -0.066332 | -0.020322 | 0.0012154 | 0.0073242 | 0.032597 | 0.0032962 | -0.043541 | -0.0035546 | 0.011386 | -0.032043 | -0.07782 | -0.045776 | 0.027466 | 0.059509 | 0.013733 | -0.1236 | -0.068665 | -0.059509 | -0.18768 | -0.027466 | 0.004578 | 0.009155 | -0.054932 | 7.5714 | 7.4341 | -113.5986 | 7.4799 | 7.5851 | 0.15106 | -113.6902 | 7.5668 | 7.5027 | -113.6856 | 7.489 | 7.37 | -0.13275 | -113.6536 | 7.6172 | 7.5256 | 7.5119 | -113.7817 | 7.5302 | 7.5623 | 7.4982 | -113.7131
4121.2188 | 121.2067 | -119.2429 | 1.6022 | -0.0022127 | -0.0020636 | 0.069799 | 0.033347 | -0.068041 | -0.025022 | 0.00036105 | 0.0073242 | 0.033879 | 0.0088504 | -0.041404 | -0.006759 | 0.013309 | -0.018311 | 0.004578 | 0.022888 | 0.054932 | 0.10529 | 0.027466 | -0.09613 | -0.041199 | 0.018311 | -0.11444 | 0.036621 | 0.041199 | 0.054932 | -0.036621 | 119.2703 | 119.1467 | -1.4969 | 119.2474 | 119.2978 | 0.15106 | -1.6205 | 119.2978 | 119.2062 | -1.5656 | 119.2017 | 119.1284 | -0.07782 | -1.561 | 119.3481 | 119.2245 | 119.2657 | -1.6983 | 119.2795 | 119.2841 | 119.2612 | -1.6388
4123 | 121.5637 | -120.0119 | 1.3596 | 0.0054168 | -0.00035461 | 0.07279 | 0.032706 | -0.06505 | -0.027371 | -0.00049335 | 0.014954 | 0.031956 | 0.0082096 | -0.043754 | -0.0071862 | 0.014163 | 0 | 0.036621 | 0.032043 | 0.064087 | 0.086975 | 0.045776 | -0.10529 | -0.027466 | 0.045776 | -0.086975 | 0.013733 | 0.032043 | 0.032043 | -0.013733 | 120.0577 | 119.9066 | -1.2726 | 120.0485 | 120.076 | 0.16937 | -1.3596 | 120.0439 | 119.9982 | -1.3458 | 119.9844 | 119.9249 | -0.073242 | -1.3275 | 120.0989 | 120.0119 | 120.0439 | -1.4648 | 120.0256 | 120.0439 | 120.0577 | -1.3733
4124.7031 | 121.6095 | -120.163 | 1.3046 | 0.0054168 | -0.002918 | 0.066595 | 0.02886 | -0.067187 | -0.022031 | 0.0012154 | 0.014954 | 0.031956 | 0.0071414 | -0.039909 | -0.0052636 | 0.010104 | 0.064087 | 0.07782 | 0.068665 | 0.10986 | 0.082397 | 0.059509 | -0.068665 | 0.022888 | 0.073242 | -0.068665 | 0.004578 | 0.009155 | 0.059509 | -0.013733 | 120.2225 | 120.0943 | -1.2222 | 120.2408 | 120.2728 | 0.17853 | -1.2405 | 120.2225 | 120.1492 | -1.3 | 120.1859 | 120.0943 | -0.054932 | -1.2955 | 120.2454 | 120.2271 | 120.2316 | -1.3733 | 120.1675 | 120.1721 | 120.2362 | -1.3184
4126.4688 | 121.756 | -120.6573 | 0.82398 | 0.0054168 | 0.0034906 | 0.071722 | 0.027152 | -0.067187 | -0.031003 | -0.0011344 | 0.0073242 | 0.02747 | 0.0075686 | -0.043754 | -0.0095362 | 0.012668 | -0.018311 | 0.073242 | 0.086975 | 0.11444 | 0.068665 | 0.054932 | -0.064087 | 0.004578 | 0.086975 | -0.009155 | -0.004578 | 0 | 0.082397 | 0.004578 | 120.7123 | 120.5933 | -0.75531 | 120.7306 | 120.7718 | 0.17853 | -0.84229 | 120.7397 | 120.6619 | -0.82855 | 120.6619 | 120.6482 | -0.013733 | -0.82398 | 120.726 | 120.639 | 120.7443 | -0.88806 | 120.6528 | 120.6573 | 120.7443 | -0.8194
4128.1719 | 121.7926 | -120.7169 | 0.80566 | 0.0054168 | 0.0019952 | 0.072149 | 0.026724 | -0.070818 | -0.02844 | -0.00049335 | 0.0073242 | 0.029606 | 0.0037234 | -0.042472 | -0.0076136 | 0.013522 | 0.032043 | 0.064087 | 0.091553 | 0.11902 | 0.068665 | 0.068665 | -0.054932 | 0 | 0.09613 | -0.009155 | -0.013733 | 0.018311 | 0.068665 | 0.018311 | 120.7855 | 120.6619 | -0.737 | 120.7809 | 120.8359 | 0.17395 | -0.77362 | 120.7855 | 120.7352 | -0.8194 | 120.7169 | 120.7077 | -0.027466 | -0.78735 | 120.7855 | 120.7489 | 120.8084 | -0.8606 | 120.7031 | 120.7352 | 120.813 | -0.78735
4129.9375 | 121.6232 | -120.9824 | 0.6546 | 0.0054168 | 0.00049979 | 0.07044 | 0.030356 | -0.068682 | -0.025235 | -0.0032706 | 0.022583 | 0.032597 | 0.0052188 | -0.044822 | -0.0071862 | 0.010104 | 0.086975 | 0.11444 | 0.14648 | 0.15106 | 0.068665 | 0.054932 | -0.050354 | 0.036621 | 0.13733 | -0.004578 | -0.022888 | 0.013733 | 0.073242 | -0.004578 | 121.0373 | 120.932 | -0.58594 | 121.0968 | 121.1334 | 0.20142 | -0.56763 | 121.0556 | 120.9778 | -0.67749 | 121.019 | 120.9778 | 0 | -0.64087 | 121.051 | 121.0693 | 121.1288 | -0.70496 | 120.9595 | 120.9961 | 121.1197 | -0.65918
4131.6406 | 121.7239 | -120.9503 | 0.62714 | 0.0054168 | -0.0014228 | 0.067022 | 0.031424 | -0.066759 | -0.020535 | -0.001348 | 0.022583 | 0.034092 | 0.0084232 | -0.040123 | -0.0065454 | 0.0077545 | 0.009155 | 0.013733 | 0.009155 | 0.086975 | 0.09613 | 0.022888 | -0.073242 | -0.009155 | 0.036621 | -0.10529 | 0.013733 | 0.041199 | 0.045776 | -0.027466 | 120.9732 | 120.8771 | -0.53101 | 120.9641 | 121.0373 | 0.16022 | -0.61798 | 120.9961 | 120.9229 | -0.6134 | 120.9412 | 120.845 | -0.07782 | -0.58594 | 121.0464 | 120.9595 | 120.9595 | -0.70038 | 120.9641 | 120.9915 | 120.9869 | -0.6546
4133.375 | 121.7834 | -120.9686 | 0.59509 | 0.020676 | 0.003277 | 0.065954 | 0.024374 | -0.068468 | -0.021176 | 0.0014292 | 0.014954 | 0.032597 | 0.0082096 | -0.042686 | -0.0059046 | 0.010959 | 0.018311 | -0.027466 | -0.013733 | 0.054932 | 0.11444 | 0.041199 | -0.09613 | -0.013733 | -0.009155 | -0.10529 | 0.027466 | 0.032043 | 0.082397 | -0.027466 | 121.0098 | 120.8725 | -0.48065 | 120.9412 | 121.0236 | 0.15106 | -0.57678 | 121.051 | 120.9412 | -0.56763 | 120.9549 | 120.8633 | -0.07782 | -0.56305 | 121.0831 | 120.9869 | 120.9549 | -0.69122 | 120.9961 | 121.0007 | 120.9595 | -0.62256
4135.1094 | 121.7377 | -120.9045 | 0.72784 | 0.013046 | -0.0022772 | 0.067449 | 0.029501 | -0.071032 | -0.020963 | -6.615e-05 | -0.0003053 | 0.033879 | 0.0092776 | -0.040336 | -0.0052636 | 0.010104 | 0.036621 | 0.009155 | 0.050354 | 0.10529 | 0.091553 | 0.027466 | -0.10071 | 0.036621 | 0.082397 | -0.068665 | 0.018311 | 0.036621 | 0.073242 | -0.032043 | 120.932 | 120.8038 | -0.63629 | 120.9137 | 121.0098 | 0.20599 | -0.69122 | 120.9778 | 120.8725 | -0.70953 | 120.9412 | 120.8359 | -0.036622 | -0.69122 | 120.9961 | 120.9412 | 120.9549 | -0.82855 | 120.9229 | 120.9412 | 120.9869 | -0.75989
4136.8125 | 121.6736 | -121.0236 | 0.63171 | 0.013046 | -0.0031318 | 0.069158 | 0.025443 | -0.065905 | -0.022458 | -0.00027975 | 0.0073242 | 0.031956 | 0.0092776 | -0.041404 | -0.0029138 | 0.01395 | -0.004578 | -0.009155 | 0 | 0.059509 | 0.10071 | 0.041199 | -0.082397 | -0.022888 | -0.004578 | -0.15106 | 0.009155 | 0.041199 | 0.059509 | -0.027466 | 121.0648 | 120.9412 | -0.53101 | 121.0144 | 121.0831 | 0.14191 | -0.63629 | 121.0831 | 120.9961 | -0.62256 | 121.0007 | 120.8725 | -0.1236 | -0.59052 | 121.1243 | 121.019 | 121.0236 | -0.71411 | 121.0327 | 121.0648 | 121.019 | -0.65918
4138.5938 | 121.8109 | -120.9549 | 0.62256 | 0.013046 | 0.0034906 | 0.068304 | 0.025656 | -0.067828 | -0.026303 | 0.00057465 | 0.0073242 | 0.027256 | 0.006287 | -0.04525 | -0.0063318 | 0.014163 | 0.091553 | 0.12817 | 0.16022 | 0.13733 | 0.036621 | 0.10071 | -0.032043 | 0.059509 | 0.13275 | 0.018311 | -0.054932 | -0.004578 | 0.091553 | 0.018311 | 121.0556 | 120.9229 | -0.58594 | 121.0831 | 121.0922 | 0.16937 | -0.53101 | 121.0464 | 120.9732 | -0.67749 | 121.0144 | 120.9732 | 0 | -0.62714 | 120.9915 | 121.0464 | 121.1151 | -0.6546 | 120.9 | 120.9503 | 121.0876 | -0.60425
4140.3281 | 121.8201 | -120.8542 | 0.737 | 0.0054168 | 0.0034906 | 0.071081 | 0.025656 | -0.068896 | -0.024167 | -0.00027975 | -0.0079343 | 0.033451 | 0.0067142 | -0.041191 | -0.0061182 | 0.012027 | 0.009155 | -0.022888 | 0 | 0.064087 | 0.10529 | 0.041199 | -0.073242 | -0.018311 | 0 | -0.10071 | 0.018311 | 0.036621 | 0.059509 | -0.004578 | 120.8954 | 120.7809 | -0.63171 | 120.8313 | 120.9183 | 0.13733 | -0.72784 | 120.9137 | 120.8496 | -0.71869 | 120.8359 | 120.7535 | -0.09613 | -0.70038 | 120.9595 | 120.8633 | 120.8542 | -0.81024 | 120.8725 | 120.8908 | 120.8542 | -0.74158
4142.0625 | 121.7972 | -120.3278 | 1.2451 | 0.013046 | 0.00028619 | 0.067022 | 0.025015 | -0.068041 | -0.023313 | -0.00070715 | 0.014954 | 0.030888 | 0.0060732 | -0.041832 | -0.0029138 | 0.013736 | 0.018311 | -0.009155 | 0.022888 | 0.07782 | 0.10529 | 0.036621 | -0.07782 | -0.009155 | 0.036621 | -0.07782 | -0.004578 | 0.032043 | 0.09613 | 0.004578 | 120.3644 | 120.2499 | -1.1398 | 120.3186 | 120.4056 | 0.15564 | -1.2268 | 120.4239 | 120.3323 | -1.2497 | 120.3186 | 120.2499 | -0.082398 | -1.2131 | 120.433 | 120.3461 | 120.3506 | -1.3229 | 120.3232 | 120.3598 | 120.3644 | -1.2405
4143.7812 | 121.9574 | -120.9183 | 0.68207 | -0.0022127 | 0.0047724 | 0.070867 | 0.030142 | -0.067828 | -0.029935 | -0.0022024 | 0.0073242 | 0.02747 | 0.0077822 | -0.044395 | -0.0086816 | 0.0116 | 0.07782 | 0.12817 | 0.16022 | 0.14191 | 0.059509 | 0.07782 | -0.073242 | 0.054932 | 0.16937 | 0.041199 | -0.027466 | 0.013733 | 0.086975 | 0.032043 | 120.9961 | 120.845 | -0.62256 | 121.0464 | 121.0602 | 0.21515 | -0.60425 | 121.0052 | 120.9503 | -0.70953 | 120.9732 | 120.9595 | 0.009156 | -0.66834 | 120.9778 | 120.9961 | 121.0785 | -0.75531 | 120.8908 | 120.932 | 121.0876 | -0.65002
4145.5 | 117.1097 | -67.6254 | 48.0927 | 0.013046 | 0.0045588 | 0.073217 | 0.030142 | -0.0674 | -0.027799 | -0.001348 | 0.014954 | 0.02747 | 0.0069278 | -0.041832 | -0.0086816 | 0.013522 | 0.073242 | 0.11444 | 0.14648 | 0.11902 | 0.027466 | 0.041199 | -0.068665 | 0.045776 | 0.15564 | 0.041199 | -0.036621 | -0.009155 | 0.091553 | -0.013733 | 67.6666 | 67.5568 | -48.0652 | 67.7399 | 67.7444 | 0.18768 | -48.0194 | 67.717 | 67.6117 | -48.1293 | 67.6712 | 67.6666 | 0.054932 | -48.1018 | 67.6529 | 67.6987 | 67.7719 | -48.1613 | 67.5888 | 67.6163 | 67.7811 | -48.1064
4147.2031 | 116.2445 | -66.0278 | 51.1459 | 0.0054168 | -0.0024908 | 0.071722 | 0.031638 | -0.067614 | -0.02374 | -0.00092075 | 0.0073242 | 0.031315 | 0.0092776 | -0.046745 | -0.0082544 | 0.014804 | -0.009155 | -0.018311 | 0.004578 | 0.050354 | 0.091553 | 0.013733 | -0.09613 | -0.082397 | -0.004578 | -0.14191 | 0.004578 | 0.009155 | 0.032043 | -0.050354 | 66.0416 | 65.9317 | -51.0544 | 66.0095 | 66.0782 | 0.14648 | -51.1551 | 66.0599 | 65.9775 | -51.1414 | 65.9454 | 65.8859 | -0.091553 | -51.1368 | 66.1194 | 66.0187 | 66.0324 | -51.2421 | 66.0324 | 66.037 | 66.0233 | -51.1963
4148.9375 | 120.9183 | -98.1445 | 22.3755 | 0.020676 | 0.0026362 | 0.070013 | 0.028433 | -0.070818 | -0.020322 | 0.00057465 | -0.0003053 | 0.03217 | 0.0050052 | -0.041618 | -0.0041956 | 0.011386 | 0.022888 | 0.009155 | 0.036621 | 0.07782 | 0.091553 | 0.073242 | -0.059509 | 0.032043 | 0.045776 | -0.050354 | 0.004578 | 0 | 0.07782 | 0 | 98.2178 | 98.085 | -22.2839 | 98.1537 | 98.2224 | 0.13733 | -22.3526 | 98.2224 | 98.1445 | -22.3709 | 98.1766 | 98.0942 | -0.050354 | -22.3755 | 98.2361 | 98.1674 | 98.1812 | -22.435 | 98.1491 | 98.1445 | 98.1903 | -22.3755
4150.7188 | 121.1243 | -119.7052 | 1.0025 | 0.013046 | -0.0039862 | 0.071935 | 0.026938 | -0.067187 | -0.02374 | -0.001348 | 0.014954 | 0.033024 | 0.0054324 | -0.042472 | -0.00505 | 0.0098907 | 0.045776 | 0.050354 | 0.054932 | 0.10986 | 0.091553 | 0.045776 | -0.091553 | 0.013733 | 0.068665 | -0.07782 | 0.013733 | 0.009155 | 0.07782 | 0.004578 | 119.751 | 119.6136 | -0.91095 | 119.7556 | 119.8151 | 0.20142 | -0.95673 | 119.783 | 119.7098 | -0.98877 | 119.7189 | 119.6274 | -0.082398 | -0.99335 | 119.7968 | 119.751 | 119.7601 | -1.0941 | 119.7189 | 119.7144 | 119.7739 | -0.99792
4152.4844 | 120.4788 | -105.2719 | 14.0762 | 0.020676 | 0.0013544 | 0.070867 | 0.029501 | -0.067614 | -0.029294 | -0.0015616 | 0.0073242 | 0.027897 | 0.003937 | -0.043968 | -0.0091088 | 0.013522 | 0.082397 | 0.15106 | 0.16479 | 0.13733 | 0.054932 | 0.059509 | -0.041199 | 0.054932 | 0.17395 | 0.045776 | -0.032043 | -0.009155 | 0.09613 | 0.009155 | 105.3314 | 105.2307 | -14.0213 | 105.423 | 105.4092 | 0.17853 | -13.9938 | 105.368 | 105.2811 | -14.1083 | 105.3268 | 105.3177 | 0.036621 | -14.0854 | 105.3268 | 105.3543 | 105.4367 | -14.1174 | 105.2399 | 105.2628 | 105.4459 | -14.0671
4154.2188 | 120.6802 | -119.2703 | 0.91095 | -0.0022127 | 0.0037042 | 0.072576 | 0.029715 | -0.068468 | -0.028012 | -0.0017752 | -0.0079343 | 0.02982 | 0.0043644 | -0.042259 | -0.0093226 | 0.012882 | 0.11444 | 0.1831 | 0.17395 | 0.16479 | 0.059509 | 0.091553 | -0.054932 | 0.068665 | 0.16937 | 0.045776 | -0.018311 | 0.004578 | 0.09613 | 0.009155 | 119.3619 | 119.2154 | -0.85144 | 119.4534 | 119.4351 | 0.21973 | -0.79651 | 119.3665 | 119.2795 | -0.92926 | 119.339 | 119.3161 | 0.036621 | -0.90637 | 119.3298 | 119.3848 | 119.4443 | -0.96588 | 119.252 | 119.2749 | 119.4397 | -0.9018
4155.9844 | 120.2316 | -46.55 | 72.8027 | 0.0054168 | 0.0058404 | 0.074285 | 0.023734 | -0.067614 | -0.02908 | -0.0015616 | 0.0073242 | 0.028752 | 0.00116 | -0.046531 | -0.0076136 | 0.012668 | 0.013733 | 0.027466 | 0.059509 | 0.068665 | 0.054932 | 0.041199 | -0.086975 | -0.004578 | 0.054932 | -0.050354 | -0.036621 | -0.009155 | 0.073242 | -0.022888 | 46.5912 | 46.463 | -72.7478 | 46.5775 | 46.6187 | 0.15564 | -72.789 | 46.6232 | 46.5271 | -72.8394 | 46.5454 | 46.4996 | -0.027466 | -72.8119 | 46.6049 | 46.5637 | 46.6095 | -72.8897 | 46.5134 | 46.5408 | 46.6049 | -72.8256
4157.6875 | 120.5063 | -119.3893 | 0.59509 | 0.0054168 | 0.004345 | 0.068945 | 0.024374 | -0.068468 | -0.020749 | -0.0011344 | 0.014954 | 0.033024 | 0.002869 | -0.041191 | -0.0041956 | 0.012241 | 0.07782 | 0.022888 | 0.068665 | 0.09613 | 0.082397 | 0.059509 | -0.073242 | 0.068665 | 0.09613 | -0.036621 | -0.013733 | -0.004578 | 0.10071 | 0.004578 | 119.4489 | 119.3161 | -0.5127 | 119.4122 | 119.4855 | 0.16937 | -0.51727 | 119.4901 | 119.3939 | -0.60883 | 119.458 | 119.3527 | -0.041199 | -0.59967 | 119.4717 | 119.4672 | 119.458 | -0.66834 | 119.3756 | 119.3848 | 119.4855 | -0.59052
4159.4062 | 120.6711 | -119.3802 | 0.82398 | 0.013046 | 0.0045588 | 0.071081 | 0.027579 | -0.066973 | -0.026303 | 0.00078825 | 0.014954 | 0.028111 | 0.0069278 | -0.043754 | -0.0065454 | 0.013736 | 0.11902 | 0.12817 | 0.15564 | 0.12817 | 0.036621 | 0.07782 | -0.032043 | 0.091553 | 0.13275 | 0.009155 | -0.018311 | -0.009155 | 0.086975 | 0.032043 | 119.458 | 119.3481 | -0.78735 | 119.5084 | 119.5084 | 0.16022 | -0.70496 | 119.4672 | 119.4122 | -0.84229 | 119.4717 | 119.3893 | -0.022888 | -0.83313 | 119.4168 | 119.4992 | 119.5358 | -0.85602 | 119.3619 | 119.371 | 119.5129 | -0.79193
4161.1406 | 120.7718 | -120.0485 | 0.5127 | -0.0022127 | -0.005268 | 0.069372 | 0.024161 | -0.068255 | -0.019681 | -0.00049335 | 0.030213 | 0.033879 | 0.0065006 | -0.043541 | -0.003341 | 0.010104 | 0.059509 | 0.004578 | 0.032043 | 0.07782 | 0.07782 | 0.041199 | -0.082397 | -0.018311 | 0 | -0.13275 | 0.018311 | 0.050354 | 0.059509 | -0.022888 | 120.0897 | 119.9661 | -0.43488 | 120.0531 | 120.1263 | 0.16022 | -0.45319 | 120.108 | 120.0256 | -0.49438 | 120.0302 | 119.9158 | -0.10986 | -0.46234 | 120.1263 | 120.108 | 120.0806 | -0.59509 | 120.0668 | 120.0989 | 120.0485 | -0.53558
4162.9531 | 116.8396 | -70.6467 | 45.7718 | -0.0022127 | -0.00014101 | 0.067022 | 0.026724 | -0.068682 | -0.022885 | 0.00207 | 0.014954 | 0.031315 | 0.0084232 | -0.04055 | -0.0037684 | 0.010318 | -0.009155 | -0.050354 | -0.009155 | 0.050354 | 0.082397 | 0.045776 | -0.10529 | -0.036621 | -0.036621 | -0.14648 | 0.004578 | 0.018311 | 0.059509 | -0.004578 | 70.6924 | 70.5414 | -45.6894 | 70.5963 | 70.697 | 0.15564 | -45.7809 | 70.7062 | 70.6421 | -45.7672 | 70.61 | 70.5002 | -0.14191 | -45.7535 | 70.7291 | 70.6375 | 70.6375 | -45.8771 | 70.6512 | 70.665 | 70.61 | -45.7764
4164.6875 | 119.8242 | -96.4188 | 22.9431 | 0.013046 | -0.0067634 | 0.067876 | 0.027792 | -0.067187 | -0.020108 | 0.00036105 | 0.014954 | 0.032383 | 0.0065006 | -0.042472 | -0.0031274 | 0.012882 | 0.022888 | 0.013733 | 0.050354 | 0.07782 | 0.082397 | 0.032043 | -0.086975 | -0.027466 | 0.018311 | -0.14191 | -0.009155 | 0.013733 | 0.041199 | -0.027466 | 96.4508 | 96.3318 | -22.8607 | 96.4325 | 96.4966 | 0.16479 | -22.9202 | 96.46 | 96.3913 | -22.9523 | 96.3913 | 96.2769 | -0.11444 | -22.9294 | 96.5012 | 96.4416 | 96.4691 | -23.0301 | 96.4096 | 96.4325 | 96.4371 | -22.9706
4166.4219 | 120.7214 | -119.87 | 0.56305 | -0.0022127 | -0.0033454 | 0.068304 | 0.030569 | -0.068041 | -0.025022 | -0.0011344 | 0.0073242 | 0.030033 | 0.0084232 | -0.042259 | -0.0088952 | 0.010532 | -0.013733 | -0.009155 | 0.018311 | 0.068665 | 0.11444 | 0.045776 | -0.09613 | -0.059509 | 0.027466 | -0.1236 | 0.027466 | 0.032043 | 0.059509 | -0.036621 | 119.9158 | 119.7739 | -0.44861 | 119.8608 | 119.9387 | 0.16479 | -0.57678 | 119.9295 | 119.8334 | -0.53558 | 119.8105 | 119.7464 | -0.086975 | -0.53101 | 119.9844 | 119.8563 | 119.8883 | -0.65918 | 119.8975 | 119.902 | 119.8975 | -0.59967
4168.1562 | 120.7672 | -120.0577 | 0.54932 | 0.013046 | 0.00028619 | 0.06809 | 0.028006 | -0.068468 | -0.02374 | 0.00078825 | -0.0003053 | 0.035801 | 0.0086368 | -0.042259 | -0.0041956 | 0.011386 | -0.027466 | -0.041199 | -0.027466 | 0.032043 | 0.09613 | 0.050354 | -0.07782 | -0.032043 | -0.027466 | -0.13733 | 0.013733 | 0.032043 | 0.045776 | -0.018311 | 120.108 | 119.9799 | -0.45319 | 120.0165 | 120.0897 | 0.10986 | -0.57678 | 120.1035 | 120.0394 | -0.53558 | 120.0256 | 119.9203 | -0.11902 | -0.51727 | 120.1538 | 120.0302 | 120.0302 | -0.62714 | 120.0714 | 120.0897 | 120.0302 | -0.56763
4169.9219 | 120.1218 | -119.1101 | 0.60883 | 0.0054168 | 0.0073358 | 0.070654 | 0.027152 | -0.068255 | -0.027371 | -0.00070715 | 0.0073242 | 0.028965 | 0.0035098 | -0.045677 | -0.0082544 | 0.013522 | 0.064087 | 0.1236 | 0.11902 | 0.11902 | 0.059509 | 0.086975 | -0.045776 | 0.045776 | 0.10529 | -0.013733 | -0.027466 | 0.004578 | 0.086975 | 0.013733 | 119.1971 | 119.0643 | -0.54932 | 119.2337 | 119.2291 | 0.16479 | -0.54474 | 119.1971 | 119.1238 | -0.63629 | 119.1559 | 119.0964 | -0.027466 | -0.60425 | 119.1696 | 119.1742 | 119.2291 | -0.6546 | 119.0826 | 119.1147 | 119.2154 | -0.59509
4171.625 | 120.2866 | -117.9474 | 1.8356 | 0.013046 | 0.0075494 | 0.072363 | 0.02886 | -0.068682 | -0.03143 | -0.0022024 | 0.014954 | 0.030461 | 0.0043644 | -0.042472 | -0.0091088 | 0.011173 | 0.032043 | 0.068665 | 0.11902 | 0.1236 | 0.064087 | 0.064087 | -0.059509 | 0.013733 | 0.12817 | 0.027466 | -0.009155 | 0.013733 | 0.10529 | 0.004578 | 118.0115 | 117.8879 | -1.7715 | 118.0161 | 118.071 | 0.1831 | -1.8036 | 118.0527 | 117.952 | -1.8448 | 117.9611 | 117.9749 | 0.022888 | -1.8219 | 118.0115 | 117.9794 | 118.0664 | -1.8951 | 117.9382 | 117.9611 | 118.0756 | -1.8311
4173.3438 | 120.6436 | -115.8646 | 4.4312 | 0.013046 | 0.00049979 | 0.072576 | 0.030997 | -0.066332 | -0.026944 | -0.0017752 | 0.014954 | 0.030461 | 0.0084232 | -0.043541 | -0.0091088 | 0.010745 | 0.09613 | 0.11902 | 0.14648 | 0.14648 | 0.045776 | 0.073242 | -0.041199 | 0.059509 | 0.14648 | 0 | -0.027466 | -0.009155 | 0.091553 | 0.013733 | 115.9378 | 115.8234 | -4.3854 | 115.9836 | 116.011 | 0.18768 | -4.335 | 115.9561 | 115.8783 | -4.4586 | 115.9241 | 115.8646 | -0.013733 | -4.4403 | 115.9103 | 115.9607 | 116.011 | -4.4724 | 115.8371 | 115.8554 | 116.011 | -4.4174
4175.0625 | 120.7626 | -116.3361 | 4.0924 | -0.0022127 | -0.00035461 | 0.071294 | 0.026297 | -0.069323 | -0.020535 | -0.00070715 | -0.0003053 | 0.035374 | 0.004578 | -0.042472 | -0.0035546 | 0.010318 | 0 | -0.054932 | 0.004578 | 0.082397 | 0.09613 | 0.054932 | -0.10529 | -0.022888 | -0.036621 | -0.13733 | 0.018311 | 0.018311 | 0.041199 | -0.018311 | 116.391 | 116.2308 | -3.9963 | 116.2811 | 116.4185 | 0.18768 | -4.0924 | 116.3773 | 116.3177 | -4.0741 | 116.3132 | 116.1987 | -0.11902 | -4.0741 | 116.4322 | 116.3361 | 116.3406 | -4.1977 | 116.3544 | 116.3544 | 116.2994 | -4.1107
4176.7812 | 120.8542 | -118.0664 | 2.4353 | 0.0054168 | 0.003277 | 0.069799 | 0.024161 | -0.068041 | -0.024808 | 0.00036105 | -0.0003053 | 0.031315 | 0.0060732 | -0.042259 | -0.0054772 | 0.012668 | 0.10071 | 0.10071 | 0.15106 | 0.15564 | 0.050354 | 0.082397 | -0.050354 | 0.10071 | 0.13275 | 0.004578 | -0.036621 | 0.004578 | 0.10071 | 0.022888 | 118.1488 | 118.0161 | -2.3849 | 118.1671 | 118.222 | 0.20599 | -2.3346 | 118.1671 | 118.0893 | -2.4719 | 118.1671 | 118.071 | -0.01831 | -2.4307 | 118.1168 | 118.1671 | 118.2175 | -2.4857 | 118.0298 | 118.071 | 118.1992 | -2.4124
4178.5 | 120.8954 | -118.0481 | 2.4353 | 0.0054168 | 0.0041314 | 0.069372 | 0.026083 | -0.070177 | -0.025876 | 0.0014292 | 0.014954 | 0.030461 | 0.0052188 | -0.043754 | -0.005691 | 0.011813 | 0.10986 | 0.13733 | 0.15106 | 0.14191 | 0.045776 | 0.07782 | -0.045776 | 0.07782 | 0.12817 | 0.018311 | -0.036621 | -0.022888 | 0.086975 | 0.027466 | 118.1259 | 118.0023 | -2.3895 | 118.1854 | 118.19 | 0.18768 | -2.3254 | 118.1351 | 118.0756 | -2.4719 | 118.1259 | 118.0664 | -0.009155 | -2.4582 | 118.0939 | 118.158 | 118.1992 | -2.4811 | 118.0115 | 118.0252 | 118.1763 | -2.4078
4180.2188 | 120.9915 | -118.3502 | 2.2156 | 0.020676 | 0.0028498 | 0.069585 | 0.024802 | -0.065905 | -0.022458 | -0.0011344 | 0.022583 | 0.03281 | 0.005646 | -0.041618 | -0.003982 | 0.011386 | 0.050354 | 0.041199 | 0.073242 | 0.10986 | 0.068665 | 0.064087 | -0.07782 | 0.07782 | 0.091553 | -0.032043 | -0.018311 | 0.004578 | 0.082397 | 0.009155 | 118.4143 | 118.2724 | -2.1469 | 118.3914 | 118.4601 | 0.18768 | -2.1652 | 118.4326 | 118.3594 | -2.2339 | 118.428 | 118.3182 | -0.041198 | -2.211 | 118.4189 | 118.4006 | 118.4235 | -2.2934 | 118.3319 | 118.3548 | 118.4418 | -2.2064
4181.9844 | 120.8817 | -118.5699 | 2.092 | 0.0054168 | 0.0017816 | 0.067236 | 0.026938 | -0.070391 | -0.02139 | -0.00092075 | 0.014954 | 0.033238 | 0.0086368 | -0.041832 | -0.00505 | 0.010745 | 0.009155 | -0.050354 | 0.004578 | 0.064087 | 0.10986 | 0.032043 | -0.082397 | -0.036621 | -0.013733 | -0.1236 | 0.018311 | 0.032043 | 0.054932 | -0.022888 | 118.602 | 118.4875 | -1.9821 | 118.5196 | 118.634 | 0.14648 | -2.0828 | 118.6249 | 118.5471 | -2.0737 | 118.5333 | 118.4463 | -0.10071 | -2.0599 | 118.6798 | 118.5791 | 118.5745 | -2.1744 | 118.5883 | 118.602 | 118.5562 | -2.1149
4183.6875 | 120.9091 | -118.959 | 1.7349 | 0.013046 | -0.00078181 | 0.07044 | 0.029501 | -0.065905 | -0.024381 | -0.001348 | 0.014954 | 0.031742 | 0.0077822 | -0.043113 | -0.0037684 | 0.011813 | -0.009155 | -0.013733 | 0.009155 | 0.068665 | 0.11902 | 0.027466 | -0.073242 | -0.036621 | 0.027466 | -0.10529 | 0.022888 | 0.032043 | 0.073242 | -0.027466 | 118.9865 | 118.8858 | -1.6159 | 118.9453 | 119.0277 | 0.14191 | -1.7441 | 119.0323 | 118.9316 | -1.712 | 118.9224 | 118.8538 | -0.07782 | -1.7029 | 119.0781 | 118.9499 | 118.9682 | -1.8082 | 118.9819 | 118.9911 | 118.9865 | -1.7624
4185.4531 | 120.9137 | -118.5104 | 2.1423 | 0.0054168 | -0.003559 | 0.069158 | 0.025443 | -0.067828 | -0.020749 | -6.615e-05 | -0.0003053 | 0.031956 | 0.0075686 | -0.042045 | -0.0035546 | 0.012027 | -0.013733 | -0.032043 | 0.004578 | 0.059509 | 0.086975 | 0.045776 | -0.086975 | -0.018311 | -0.027466 | -0.14648 | 0.018311 | 0.032043 | 0.050354 | -0.027466 | 118.5562 | 118.4235 | -2.0554 | 118.4784 | 118.5699 | 0.14648 | -2.1561 | 118.5608 | 118.483 | -2.124 | 118.4921 | 118.364 | -0.11902 | -2.1103 | 118.5974 | 118.4967 | 118.515 | -2.2293 | 118.5287 | 118.5425 | 118.483 | -2.1698
4187.2344 | 120.9961 | -119.4077 | 1.3458 | 0.013046 | 0.001568 | 0.073003 | 0.029715 | -0.068896 | -0.028226 | -0.0017752 | 0.014954 | 0.02982 | 0.0058596 | -0.044822 | -0.0074 | 0.010318 | 0.068665 | 0.11444 | 0.16022 | 0.16937 | 0.045776 | 0.059509 | -0.059509 | 0.054932 | 0.14648 | -0.009155 | -0.027466 | 0.013733 | 0.07782 | 0 | 119.4672 | 119.3481 | -1.3 | 119.5221 | 119.577 | 0.22888 | -1.2772 | 119.4855 | 119.4077 | -1.3733 | 119.4626 | 119.3985 | -0.009155 | -1.3321 | 119.4534 | 119.4763 | 119.5679 | -1.4053 | 119.3802 | 119.4214 | 119.5541 | -1.3458
4188.9688 | 120.7809 | -118.4189 | 2.0966 | 0.0054168 | 0.0056268 | 0.072149 | 0.024802 | -0.068468 | -0.026731 | -0.0024162 | 0.022583 | 0.028965 | 0.0037234 | -0.0429 | -0.0037684 | 0.010532 | 0.086975 | 0.12817 | 0.14648 | 0.14191 | 0.041199 | 0.086975 | -0.045776 | 0.082397 | 0.13733 | 0.013733 | -0.013733 | -0.027466 | 0.10529 | 0.027466 | 118.5059 | 118.3731 | -2.0554 | 118.5471 | 118.5608 | 0.18768 | -2.0096 | 118.5242 | 118.4464 | -2.1103 | 118.5013 | 118.4326 | -0.013733 | -2.124 | 118.4601 | 118.5059 | 118.5654 | -2.1423 | 118.4052 | 118.3914 | 118.5562 | -2.0691
4190.75 | 120.8405 | -117.778 | 2.9709 | -0.0022127 | -0.0027044 | 0.073858 | 0.032065 | -0.068896 | -0.026731 | -0.0015616 | 0.0073242 | 0.031529 | 0.0071414 | -0.042686 | -0.0091088 | 0.010532 | 0.036621 | 0.073242 | 0.086975 | 0.11902 | 0.073242 | 0.059509 | -0.064087 | -0.022888 | 0.059509 | -0.082397 | 0.018311 | 0.013733 | 0.064087 | -0.004578 | 117.8375 | 117.7139 | -2.8976 | 117.8513 | 117.897 | 0.18311 | -2.9343 | 117.8421 | 117.7734 | -2.9526 | 117.7551 | 117.6956 | -0.077819 | -2.9572 | 117.8513 | 117.8146 | 117.865 | -3.035 | 117.7963 | 117.7917 | 117.8375 | -2.9755
4192.4844 | 120.9366 | -118.8858 | 1.7578 | 0.0054168 | -0.0020636 | 0.069585 | 0.030142 | -0.067187 | -0.023526 | -0.00092075 | -0.0003053 | 0.03217 | 0.010132 | -0.041618 | -0.0082544 | 0.010959 | 0 | -0.009155 | 0.018311 | 0.068665 | 0.10986 | 0.032043 | -0.10071 | -0.050354 | 0.009155 | -0.11444 | 0.032043 | 0.027466 | 0.050354 | -0.018311 | 118.9178 | 118.7851 | -1.6479 | 118.8766 | 118.9545 | 0.16937 | -1.7578 | 118.9362 | 118.8675 | -1.7258 | 118.8354 | 118.7714 | -0.09613 | -1.7303 | 118.9957 | 118.8858 | 118.9041 | -1.8585 | 118.9178 | 118.9133 | 118.895 | -1.7761
4194.25 | 120.9549 | -119.1101 | 1.6067 | 0.013046 | -0.0033454 | 0.068517 | 0.028006 | -0.066759 | -0.023313 | -0.00049335 | 0.014954 | 0.03281 | 0.0075686 | -0.040977 | -0.0054772 | 0.010745 | -0.009155 | -0.013733 | 0.013733 | 0.073242 | 0.10986 | 0.050354 | -0.07782 | -0.018311 | 0.045776 | -0.1236 | 0.027466 | 0.036621 | 0.059509 | -0.009155 | 119.1605 | 119.0323 | -1.4969 | 119.0964 | 119.1833 | 0.15106 | -1.6159 | 119.1696 | 119.101 | -1.5793 | 119.0918 | 118.9865 | -0.11444 | -1.5701 | 119.22 | 119.101 | 119.1238 | -1.6846 | 119.1376 | 119.1467 | 119.1559 | -1.6159
4196.0156 | 120.9595 | -114.7156 | 3.8315 | 0.0054168 | -0.0012092 | 0.070654 | 0.024161 | -0.068468 | -0.021817 | -0.0011344 | 0.014954 | 0.033451 | 0.0058596 | -0.041191 | -0.002273 | 0.012027 | -0.018311 | -0.041199 | -0.009155 | 0.059509 | 0.082397 | 0.022888 | -0.10529 | -0.041199 | -0.032043 | -0.16022 | 0.004578 | 0.027466 | 0.036621 | -0.041199 | 114.7385 | 114.6103 | -3.7491 | 114.6744 | 114.7751 | 0.16479 | -3.8498 | 114.7522 | 114.6744 | -3.8269 | 114.6744 | 114.5554 | -0.11902 | -3.804 | 114.798 | 114.6973 | 114.7064 | -3.9368 | 114.7202 | 114.743 | 114.6835 | -3.8727
4197.7188 | 121.0373 | -119.2932 | 1.4191 | 0.020676 | -0.0014228 | 0.069158 | 0.02886 | -0.068468 | -0.022031 | 0.00078825 | 0.014954 | 0.031742 | 0.007996 | -0.041404 | -0.0054772 | 0.012668 | 0.027466 | 0.050354 | 0.045776 | 0.11444 | 0.086975 | 0.059509 | -0.07782 | 0.022888 | 0.086975 | -0.086975 | 0.004578 | 0.036621 | 0.07782 | -0.022888 | 119.3527 | 119.2154 | -1.3321 | 119.3436 | 119.4077 | 0.19226 | -1.3916 | 119.371 | 119.2703 | -1.4145 | 119.3161 | 119.2062 | -0.064087 | -1.3824 | 119.3802 | 119.3207 | 119.339 | -1.4969 | 119.2978 | 119.3298 | 119.3802 | -1.442
4199.4844 | 121.0831 | -117.6132 | 3.1036 | 0.013046 | 0.0039178 | 0.067449 | 0.027152 | -0.068896 | -0.02609 | -0.00027975 | 0.014954 | 0.031956 | 0.006287 | -0.042259 | -0.0041956 | 0.011813 | 0.004578 | 0.009155 | 0.045776 | 0.07782 | 0.086975 | 0.054932 | -0.10071 | 0.022888 | 0.059509 | -0.054932 | -0.013733 | 0.009155 | 0.068665 | 0 | 117.6682 | 117.5125 | -3.0167 | 117.6224 | 117.691 | 0.17853 | -3.0991 | 117.6819 | 117.6132 | -3.1174 | 117.6361 | 117.5583 | -0.054932 | -3.0945 | 117.7002 | 117.6178 | 117.659 | -3.2043 | 117.5995 | 117.6224 | 117.6727 | -3.1036
4201.2031 | 121.0831 | -119.4077 | 1.3687 | -0.0022127 | 0.0026362 | 0.068945 | 0.025229 | -0.069964 | -0.028226 | 0.00078825 | 0.014954 | 0.030888 | 0.0032962 | -0.043968 | -0.0052636 | 0.011386 | 0.082397 | 0.09613 | 0.11444 | 0.15564 | 0.054932 | 0.082397 | -0.045776 | 0.07782 | 0.11902 | 0.004578 | -0.045776 | 0.004578 | 0.11902 | 0.027466 | 119.4901 | 119.3619 | -1.3138 | 119.5038 | 119.5633 | 0.20142 | -1.2863 | 119.5267 | 119.4351 | -1.4145 | 119.4855 | 119.4122 | -0.022888 | -1.3641 | 119.4626 | 119.4901 | 119.5221 | -1.4145 | 119.3619 | 119.4122 | 119.5267 | -1.3412
4203 | 120.9732 | -119.2383 | 1.6113 | 0.013046 | -0.0024908 | 0.067663 | 0.028433 | -0.068682 | -0.02139 | 0.0014292 | 0.014954 | 0.034947 | 0.0082096 | -0.042259 | -0.0041956 | 0.012882 | 0.022888 | 0.009155 | 0.032043 | 0.068665 | 0.091553 | 0.045776 | -0.073242 | -0.022888 | 0.009155 | -0.1236 | 0.018311 | 0.027466 | 0.050354 | -0.032043 | 119.2841 | 119.165 | -1.5198 | 119.2474 | 119.3069 | 0.14191 | -1.5884 | 119.2886 | 119.2062 | -1.593 | 119.2154 | 119.1147 | -0.091553 | -1.5839 | 119.3298 | 119.2612 | 119.2703 | -1.6846 | 119.2566 | 119.2657 | 119.2474 | -1.6434
4204.75 | 121.0693 | -119.8013 | 1.062 | 0.0054168 | 0.0041314 | 0.073644 | 0.026938 | -0.069537 | -0.029721 | -0.0019888 | 0.014954 | 0.030033 | 0.004578 | -0.043113 | -0.0076136 | 0.014163 | 0.073242 | 0.10986 | 0.14191 | 0.12817 | 0.050354 | 0.082397 | -0.032043 | 0.027466 | 0.11902 | -0.009155 | -0.027466 | -0.013733 | 0.082397 | 0.004578 | 119.8837 | 119.7693 | -1.0117 | 119.9112 | 119.9295 | 0.16022 | -0.98877 | 119.8837 | 119.8059 | -1.0895 | 119.8288 | 119.7922 | -0.013733 | -1.0757 | 119.8517 | 119.8746 | 119.9432 | -1.0941 | 119.7739 | 119.7876 | 119.9203 | -1.0574
4206.5 | 120.9686 | -119.902 | 1.0117 | 0.0054168 | -0.0020636 | 0.069372 | 0.027365 | -0.070605 | -0.022672 | -0.0019888 | 0.0073242 | 0.033238 | 0.0065006 | -0.039695 | -0.0041956 | 0.010745 | 0.073242 | 0.041199 | 0.059509 | 0.11902 | 0.082397 | 0.045776 | -0.073242 | 0.022888 | 0.073242 | -0.073242 | 0.022888 | 0.013733 | 0.064087 | -0.013733 | 119.9478 | 119.8288 | -0.92926 | 119.9432 | 120.0211 | 0.19226 | -0.93842 | 119.9661 | 119.8883 | -0.98877 | 119.9249 | 119.8288 | -0.059509 | -0.99792 | 119.9844 | 119.9753 | 119.9615 | -1.0849 | 119.9249 | 119.9158 | 119.9753 | -1.0254
4208.2656 | 121.0144 | -119.0323 | 1.9363 | 0.013046 | -0.0037726 | 0.072576 | 0.031424 | -0.068255 | -0.025662 | -0.0019888 | -0.0003053 | 0.03281 | 0.0067142 | -0.043113 | -0.0069726 | 0.012882 | -0.022888 | -0.004578 | 0.013733 | 0.059509 | 0.10529 | 0.022888 | -0.091553 | -0.064087 | 0.018311 | -0.11902 | 0.036621 | 0.045776 | 0.054932 | -0.018311 | 119.0552 | 118.9407 | -1.8311 | 119.0277 | 119.0918 | 0.15106 | -1.9592 | 119.0872 | 119.014 | -1.8997 | 118.9682 | 118.9133 | -0.10071 | -1.8906 | 119.1376 | 119.0094 | 119.046 | -2.0279 | 119.0689 | 119.0781 | 119.0506 | -1.9547
4210.0156 | 121.0098 | -119.7235 | 1.2634 | -0.0098417 | -0.00056821 | 0.072149 | 0.032492 | -0.068255 | -0.026517 | -0.0034842 | 0.014954 | 0.031529 | 0.0058596 | -0.042045 | -0.0076136 | 0.010104 | 0.013733 | 0.041199 | 0.059509 | 0.082397 | 0.086975 | 0.050354 | -0.082397 | -0.059509 | 0.036621 | -0.091553 | 0.004578 | 0.045776 | 0.041199 | -0.032043 | 119.7739 | 119.6411 | -1.1765 | 119.7647 | 119.8059 | 0.16479 | -1.2497 | 119.7647 | 119.6915 | -1.2589 | 119.664 | 119.632 | -0.05951 | -1.2177 | 119.8105 | 119.7372 | 119.783 | -1.3458 | 119.7281 | 119.7693 | 119.7601 | -1.2955
4211.7656 | 121.1243 | -119.7739 | 1.1536 | 0.020676 | 0.0054132 | 0.07279 | 0.02886 | -0.069537 | -0.029935 | -0.0017752 | 0.014954 | 0.02747 | 0.003937 | -0.044609 | -0.010177 | 0.012027 | 0.022888 | 0.045776 | 0.091553 | 0.10529 | 0.073242 | 0.073242 | -0.054932 | 0.009155 | 0.082397 | -0.013733 | -0.022888 | 0.004578 | 0.091553 | -0.009155 | 119.8471 | 119.7189 | -1.0803 | 119.8196 | 119.8792 | 0.16022 | -1.1307 | 119.8654 | 119.7647 | -1.1765 | 119.783 | 119.7601 | -0.004578 | -1.149 | 119.8471 | 119.7968 | 119.8654 | -1.2085 | 119.751 | 119.7784 | 119.8563 | -1.1627
4213.4844 | 121.0419 | -119.902 | 1.0162 | 0.0054168 | -0.0031318 | 0.068304 | 0.026724 | -0.066973 | -0.020322 | -0.0017752 | -0.0003053 | 0.03281 | 0.0084232 | -0.039695 | -0.0052636 | 0.0094635 | 0.068665 | 0.032043 | 0.073242 | 0.10529 | 0.09613 | 0.041199 | -0.09613 | 0.018311 | 0.068665 | -0.073242 | 0.018311 | 0.032043 | 0.068665 | -0.009155 | 119.9432 | 119.8059 | -0.9201 | 119.9341 | 120.0073 | 0.20142 | -0.94757 | 119.9707 | 119.8929 | -0.99792 | 119.9203 | 119.8288 | -0.064087 | -0.98419 | 119.9982 | 119.9707 | 119.9753 | -1.1124 | 119.9203 | 119.9341 | 119.9707 | -1.0254
4215.2344 | 121.0922 | -120.1218 | 0.82398 | 0.020676 | 0.0054132 | 0.071508 | 0.026938 | -0.068468 | -0.028653 | -6.615e-05 | -0.0003053 | 0.026615 | 0.007355 | -0.04055 | -0.0071862 | 0.013095 | 0.068665 | 0.10986 | 0.13733 | 0.1236 | 0.050354 | 0.082397 | -0.045776 | 0.018311 | 0.10071 | -0.027466 | -0.018311 | -0.004578 | 0.091553 | 0.004578 | 120.2042 | 120.076 | -0.77362 | 120.2316 | 120.2454 | 0.16937 | -0.75531 | 120.2133 | 120.1263 | -0.84229 | 120.1401 | 120.0943 | -0.032044 | -0.82855 | 120.1721 | 120.1904 | 120.2591 | -0.86975 | 120.1035 | 120.1172 | 120.2225 | -0.8194
4217 | 121.1517 | -119.8929 | 1.0574 | 0.013046 | 0.003277 | 0.06809 | 0.022452 | -0.067614 | -0.020322 | -0.00070715 | 0.0073242 | 0.030888 | 0.005646 | -0.041404 | -0.0035546 | 0.012027 | 0.027466 | -0.013733 | 0.022888 | 0.059509 | 0.10071 | 0.045776 | -0.086975 | 0.009155 | 0.004578 | -0.07782 | 0.009155 | 0.022888 | 0.091553 | -0.004578 | 119.9387 | 119.8059 | -0.95673 | 119.8791 | 119.9524 | 0.14648 | -1.03 | 119.9844 | 119.8883 | -1.0483 | 119.902 | 119.8151 | -0.073242 | -1.0345 | 119.9936 | 119.9203 | 119.9158 | -1.1444 | 119.902 | 119.9158 | 119.8975 | -1.062
4218.7812 | 121.1288 | -120.3644 | 0.61798 | 0.0054168 | -0.002918 | 0.069585 | 0.027792 | -0.0674 | -0.022031 | -0.00070715 | 0.014954 | 0.032597 | 0.0054324 | -0.042686 | -0.0061182 | 0.0090363 | 0.041199 | 0.036621 | 0.050354 | 0.10986 | 0.10071 | 0.045776 | -0.07782 | 0.013733 | 0.068665 | -0.064087 | 0.027466 | 0.041199 | 0.073242 | 0.004578 | 120.4102 | 120.2866 | -0.51727 | 120.401 | 120.4742 | 0.18768 | -0.57678 | 120.4376 | 120.369 | -0.59052 | 120.3781 | 120.3003 | -0.068665 | -0.57678 | 120.4651 | 120.4056 | 120.4147 | -0.6958 | 120.3918 | 120.4056 | 120.433 | -0.6134
4220.5625 | 121.051 | -120.4742 | 0.57678 | 0.013046 | 0.0022088 | 0.07044 | 0.029929 | -0.068468 | -0.027158 | -0.00092075 | 0.014954 | 0.031101 | 0.0065006 | -0.044609 | -0.0080408 | 0.010959 | 0.036621 | 0.068665 | 0.068665 | 0.09613 | 0.082397 | 0.054932 | -0.091553 | -0.036621 | 0.045776 | -0.082397 | 0.009155 | 0.032043 | 0.059509 | -0.027466 | 120.5292 | 120.3827 | -0.49439 | 120.5429 | 120.5704 | 0.18768 | -0.54016 | 120.5338 | 120.4468 | -0.56763 | 120.4376 | 120.3918 | -0.054931 | -0.54474 | 120.5566 | 120.5109 | 120.5429 | -0.66834 | 120.4834 | 120.5063 | 120.52 | -0.60425
4222.3438 | 121.2524 | -120.1675 | 0.72784 | 0.0054168 | 0.0037042 | 0.071508 | 0.028647 | -0.067614 | -0.029935 | 0.00036105 | 0.022583 | 0.027683 | 0.005646 | -0.0429 | -0.0088952 | 0.012454 | 0.045776 | 0.059509 | 0.10986 | 0.12817 | 0.068665 | 0.064087 | -0.059509 | 0.036621 | 0.11444 | 0 | -0.009155 | 0.022888 | 0.054932 | 0.004578 | 120.2316 | 120.108 | -0.65918 | 120.2271 | 120.2957 | 0.18768 | -0.68207 | 120.2225 | 120.1721 | -0.737 | 120.2042 | 120.1675 | -0.004578 | -0.70496 | 120.2362 | 120.2133 | 120.2774 | -0.78735 | 120.1584 | 120.1904 | 120.282 | -0.72327
4224.125 | 121.1243 | -120.3918 | 0.66834 | 0.013046 | 0.00049979 | 0.070013 | 0.028433 | -0.071032 | -0.026731 | -0.00092075 | 0.014954 | 0.030888 | 0.0050052 | -0.043113 | -0.0063318 | 0.010318 | 0 | 0.004578 | 0.032043 | 0.064087 | 0.10071 | 0.045776 | -0.10071 | -0.041199 | 0.036621 | -0.10071 | 0.018311 | 0.041199 | 0.054932 | -0.018311 | 120.4376 | 120.2911 | -0.56763 | 120.3964 | 120.4559 | 0.1648 | -0.66834 | 120.4468 | 120.3735 | -0.65002 | 120.3506 | 120.2911 | -0.082397 | -0.62714 | 120.4926 | 120.3918 | 120.4239 | -0.76904 | 120.4102 | 120.433 | 120.4285 | -0.68665
4225.8594 | 121.2112 | -120.2911 | 0.70496 | 0.0054168 | 0.0030634 | 0.069799 | 0.020956 | -0.068468 | -0.024808 | 0.0010018 | 0.014954 | 0.03281 | 0.004578 | -0.042472 | -0.003341 | 0.012454 | 0.059509 | 0.054932 | 0.082397 | 0.10986 | 0.086975 | 0.07782 | -0.059509 | 0.07782 | 0.09613 | -0.009155 | -0.009155 | 0.009155 | 0.10071 | 0.018311 | 120.369 | 120.2316 | -0.61798 | 120.3461 | 120.401 | 0.16937 | -0.64545 | 120.3918 | 120.3094 | -0.71411 | 120.369 | 120.282 | -0.027466 | -0.6958 | 120.3781 | 120.3506 | 120.3735 | -0.76447 | 120.282 | 120.3003 | 120.3873 | -0.68665
4227.625 | 121.2616 | -119.2383 | 1.6617 | 0.013046 | 0.0039178 | 0.072149 | 0.025656 | -0.067614 | -0.025662 | 0.0010018 | -0.0003053 | 0.02982 | 0.0032962 | -0.0429 | -0.0048364 | 0.013309 | 0.09613 | 0.13275 | 0.13733 | 0.13275 | 0.045776 | 0.086975 | -0.045776 | 0.064087 | 0.10986 | 0.004578 | -0.018311 | -0.018311 | 0.10071 | 0.022888 | 119.3253 | 119.1925 | -1.6159 | 119.371 | 119.371 | 0.17853 | -1.5656 | 119.339 | 119.2612 | -1.68 | 119.3024 | 119.2429 | -0.01831 | -1.68 | 119.2841 | 119.3344 | 119.3756 | -1.7075 | 119.22 | 119.22 | 119.3481 | -1.6388
4229.3906 | 121.1563 | -119.2062 | 1.8951 | 0.0054168 | -0.0014228 | 0.069158 | 0.029715 | -0.066546 | -0.019681 | 0.00014745 | -0.0003053 | 0.034519 | 0.0082096 | -0.040977 | -0.005691 | 0.010959 | 0.050354 | 0.036621 | 0.059509 | 0.10529 | 0.11444 | 0.045776 | -0.086975 | 0.027466 | 0.082397 | -0.07782 | 0.004578 | 0.013733 | 0.068665 | -0.018311 | 119.252 | 119.1193 | -1.7807 | 119.2429 | 119.3115 | 0.19226 | -1.8448 | 119.2749 | 119.1879 | -1.8906 | 119.2337 | 119.1284 | -0.059509 | -1.8814 | 119.3207 | 119.2566 | 119.2657 | -1.9821 | 119.2108 | 119.22 | 119.2886 | -1.9135
4231.125 | 120.0485 | -74.9222 | 44.8105 | 0.0054168 | 0.00028619 | 0.066595 | 0.026297 | -0.069109 | -0.022458 | -0.00049335 | 0.014954 | 0.03217 | 0.0060732 | -0.041618 | -0.0061182 | 0.012027 | -0.009155 | -0.027466 | -0.004578 | 0.050354 | 0.091553 | 0.032043 | -0.10529 | -0.032043 | -0.018311 | -0.11444 | 0 | 0.004578 | 0.050354 | -0.027466 | 74.9542 | 74.8169 | -44.7189 | 74.8947 | 74.9725 | 0.15564 | -44.8196 | 74.9725 | 74.8947 | -44.8105 | 74.8901 | 74.8077 | -0.086975 | -44.8059 | 75.0137 | 74.913 | 74.9176 | -44.9158 | 74.9222 | 74.9268 | 74.9039 | -44.838
4232.875 | 104.7043 | -5.4291 | 90.8478 | 0.0054168 | 0.0069086 | 0.073003 | 0.025443 | -0.068682 | -0.028012 | 0.00078825 | 0.0073242 | 0.02982 | 0.0024418 | -0.040977 | -0.0052636 | 0.011813 | 0.064087 | 0.09613 | 0.1236 | 0.10529 | 0.013733 | 0.054932 | -0.07782 | 0.036621 | 0.086975 | -0.022888 | -0.086975 | -0.032043 | 0.068665 | -0.032043 | 5.484 | 5.3513 | -90.834 | 5.5252 | 5.5344 | 0.18311 | -90.7837 | 5.4977 | 5.397 | -90.9348 | 5.4657 | 5.4062 | 0.009155 | -90.8798 | 5.4428 | 5.4932 | 5.5527 | -90.9256 | 5.3421 | 5.397 | 5.5161 | -90.8798
4234.625 | 120.2682 | -96.0938 | 23.8586 | 0.0054168 | 0.0019952 | 0.069799 | 0.030783 | -0.068468 | -0.026517 | -0.00092075 | 0.022583 | 0.028965 | 0.004578 | -0.043327 | -0.010177 | 0.012668 | 0.082397 | 0.11902 | 0.14191 | 0.14648 | 0.050354 | 0.064087 | -0.054932 | 0.027466 | 0.12817 | -0.013733 | -0.041199 | -0.004578 | 0.068665 | -0.018311 | 96.1578 | 96.0388 | -23.8083 | 96.2128 | 96.2402 | 0.20142 | -23.7762 | 96.1624 | 96.0754 | -23.8998 | 96.1212 | 96.08 | 0.004578 | -23.8632 | 96.1441 | 96.1761 | 96.2357 | -23.9136 | 96.0526 | 96.0892 | 96.2219 | -23.877
4236.375 | 120.4285 | -95.9244 | 24.1699 | 0.020676 | -0.00056821 | 0.066595 | 0.025443 | -0.069537 | -0.022244 | 0.00014745 | 0.014954 | 0.033238 | 0.0052188 | -0.040977 | -0.00505 | 0.012241 | 0 | -0.045776 | 0 | 0.050354 | 0.091553 | 0.022888 | -0.091553 | -0.036621 | -0.032043 | -0.15106 | 0.009155 | 0.041199 | 0.068665 | -0.022888 | 95.9473 | 95.8328 | -24.0784 | 95.8786 | 95.9747 | 0.14191 | -24.1699 | 95.993 | 95.9015 | -24.1608 | 95.8878 | 95.7733 | -0.12817 | -24.1287 | 96.0159 | 95.9244 | 95.9244 | -24.2615 | 95.9335 | 95.9656 | 95.8923 | -24.1928
4238.1406 | 120.2911 | -95.842 | 23.9273 | 0.0054168 | 0.0017816 | 0.067022 | 0.024588 | -0.070605 | -0.02139 | 0.0014292 | 0.0073242 | 0.03217 | 0.0069278 | -0.041618 | -0.00505 | 0.010104 | -0.022888 | -0.027466 | -0.013733 | 0.041199 | 0.10071 | 0.041199 | -0.10071 | -0.041199 | -0.022888 | -0.12817 | 0.013733 | 0.032043 | 0.045776 | -0.032043 | 95.8832 | 95.7413 | -23.8266 | 95.8145 | 95.8832 | 0.14191 | -23.9502 | 95.8878 | 95.8099 | -23.9136 | 95.8008 | 95.7138 | -0.096131 | -23.8953 | 95.9427 | 95.8191 | 95.8282 | -24.028 | 95.8557 | 95.874 | 95.8191 | -23.9594
4239.8594 | 117.2104 | -68.2709 | 45.7306 | -0.0022127 | 7.2586e-05 | 0.074926 | 0.025656 | -0.067614 | -0.027585 | 0.00036105 | -0.0003053 | 0.030033 | 0.006287 | -0.041832 | -0.0082544 | 0.011173 | -0.013733 | 0.018311 | 0.041199 | 0.054932 | 0.086975 | 0.009155 | -0.086975 | -0.059509 | 0.032043 | -0.10986 | 0.013733 | 0.045776 | 0.064087 | -0.041199 | 68.28 | 68.1839 | -45.6436 | 68.2892 | 68.3258 | 0.14191 | -45.7443 | 68.335 | 68.2297 | -45.7169 | 68.2114 | 68.161 | -0.068664 | -45.6848 | 68.3578 | 68.2571 | 68.3121 | -45.8176 | 68.2846 | 68.3167 | 68.3029 | -45.7718
4241.6094 | 104.3701 | -63.5742 | 55.5267 | 0.0054168 | 0.0037042 | 0.070013 | 0.026511 | -0.0674 | -0.023313 | 0.00057465 | 0.0073242 | 0.031315 | 0.0071414 | -0.042472 | -0.0027002 | 0.010959 | 0 | 0 | 0.022888 | 0.064087 | 0.07782 | 0.027466 | -0.082397 | 0.013733 | 0.050354 | -0.050354 | -0.018311 | -0.013733 | 0.045776 | 0.009155 | 63.6017 | 63.4918 | -55.4489 | 63.5742 | 63.6383 | 0.14648 | -55.5267 | 63.62 | 63.5834 | -55.545 | 63.588 | 63.5239 | -0.059509 | -55.5405 | 63.652 | 63.5742 | 63.5971 | -55.6091 | 63.5559 | 63.5605 | 63.6246 | -55.5176
4243.3281 | 120.2774 | -105.0751 | 16.8091 | 0.0054168 | -0.00078181 | 0.068731 | 0.029074 | -0.066332 | -0.022672 | 0.0014292 | 0.014954 | 0.031101 | 0.0084232 | -0.041832 | -0.0035546 | 0.0116 | 0.013733 | 0.009155 | 0.032043 | 0.10529 | 0.086975 | 0.032043 | -0.086975 | 0.004578 | 0.068665 | -0.082397 | 0.013733 | 0.018311 | 0.050354 | -0.013733 | 105.1071 | 104.9881 | -16.7221 | 105.0842 | 105.1804 | 0.19226 | -16.7953 | 105.1254 | 105.0613 | -16.7953 | 105.0797 | 104.9927 | -0.068664 | -16.7908 | 105.162 | 105.0888 | 105.1071 | -16.8961 | 105.0888 | 105.0934 | 105.1437 | -16.8228
4245.0625 | 120.5612 | -25.3738 | 89.1769 | -0.0022127 | -0.0022772 | 0.071935 | 0.027365 | -0.067828 | -0.021817 | 0.0014292 | 0.0073242 | 0.031742 | 0.0054324 | -0.042686 | -0.0054772 | 0.010959 | 0.004578 | 0.018311 | 0.027466 | 0.07782 | 0.059509 | 0.013733 | -0.11444 | -0.004578 | 0.054932 | -0.10071 | -0.013733 | -0.013733 | 0.032043 | -0.045776 | 25.3876 | 25.2594 | -89.1174 | 25.3922 | 25.4517 | 0.19226 | -89.1724 | 25.4059 | 25.3281 | -89.1907 | 25.3693 | 25.2731 | -0.054932 | -89.1907 | 25.4333 | 25.3784 | 25.4013 | -89.2914 | 25.3601 | 25.3601 | 25.4288 | -89.2227
4246.7812 | 89.5615 | -0.10986 | 82.8415 | -0.0098417 | -0.0027044 | 0.068945 | 0.027365 | -0.070177 | -0.02374 | 0.0010018 | 0.0073242 | 0.031529 | 0.0077822 | -0.043327 | -0.0059046 | 0.010959 | 0.013733 | 0.032043 | 0.018311 | 0.073242 | 0.064087 | 0.009155 | -0.14191 | -0.027466 | 0.036621 | -0.10986 | -0.027466 | -0.004578 | 0.032043 | -0.050354 | 0.11902 | -0.032044 | -82.7774 | 0.14191 | 0.18311 | 0.21515 | -82.8278 | 0.14191 | 0.059509 | -82.869 | 0.082397 | 0 | -0.059509 | -82.8461 | 0.17395 | 0.1236 | 0.12817 | -82.9834 | 0.082397 | 0.10529 | 0.14648 | -82.8918
4248.5 | 110.6461 | -7.8461 | 88.2385 | 0.013046 | -0.0039862 | 0.069585 | 0.029501 | -0.066546 | -0.021604 | 0.00078825 | 0.022583 | 0.033451 | 0.0086368 | -0.040977 | -0.0052636 | 0.01395 | -0.009155 | -0.004578 | -0.004578 | 0.059509 | 0.050354 | -0.004578 | -0.1236 | -0.050354 | 0 | -0.15106 | -0.022888 | -0.013733 | 0.027466 | -0.050354 | 7.8415 | 7.7225 | -88.1882 | 7.8415 | 7.9056 | 0.1831 | -88.2477 | 7.8735 | 7.7957 | -88.2614 | 7.7957 | 7.695 | -0.10071 | -88.2523 | 7.8964 | 7.8369 | 7.8415 | -88.3621 | 7.8232 | 7.8323 | 7.8461 | -88.2889
4250.3281 | 120.1767 | -10.5835 | 109.4421 | 0.013046 | 0.0030634 | 0.073003 | 0.031851 | -0.069964 | -0.030362 | -0.00092075 | 0.0073242 | 0.02747 | 0.0058596 | -0.040763 | -0.013381 | 0.011173 | -0.027466 | 0.018311 | 0.068665 | 0.073242 | 0.036621 | 0.036621 | -0.09613 | -0.050354 | 0.045776 | -0.059509 | -0.045776 | -0.036621 | 0.045776 | -0.013733 | 10.6201 | 10.4874 | -109.4055 | 10.6018 | 10.6567 | 0.16937 | -109.4696 | 10.6293 | 10.5698 | -109.4879 | 10.5331 | 10.524 | -0.045776 | -109.4788 | 10.6201 | 10.556 | 10.6522 | -109.5383 | 10.5377 | 10.5469 | 10.6293 | -109.4559
4252.1094 | 119.8837 | -117.1555 | 2.211 | 0.0054168 | 0.0026362 | 0.070226 | 0.033987 | -0.068041 | -0.02908 | -0.0051932 | 0.0073242 | 0.026402 | 0.0060732 | -0.0429 | -0.0121 | 0.012027 | 0.073242 | 0.1236 | 0.12817 | 0.13275 | 0.045776 | 0.073242 | -0.064087 | 0.045776 | 0.15106 | 0.045776 | -0.022888 | -0.013733 | 0.086975 | 0.022888 | 117.2287 | 117.0914 | -2.1652 | 117.2791 | 117.2882 | 0.19684 | -2.1378 | 117.2424 | 117.1783 | -2.2339 | 117.2012 | 117.2012 | 0.022888 | -2.2247 | 117.2012 | 117.2287 | 117.2836 | -2.2751 | 117.1326 | 117.1417 | 117.3065 | -2.1881
4253.8906 | 120.2637 | -119.0277 | 0.78278 | 0.013046 | 0.0073358 | 0.070226 | 0.028647 | -0.066973 | -0.028012 | -0.0034842 | 0.014954 | 0.030033 | 0.004578 | -0.042259 | -0.0076136 | 0.012027 | 0.036621 | 0.050354 | 0.10986 | 0.11902 | 0.054932 | 0.068665 | -0.050354 | 0.013733 | 0.068665 | -0.022888 | -0.013733 | 0.004578 | 0.10071 | 0.013733 | 119.0964 | 118.9774 | -0.72784 | 119.0781 | 119.1467 | 0.16937 | -0.74616 | 119.1284 | 119.0414 | -0.79651 | 119.0414 | 119.0048 | -0.036621 | -0.7782 | 119.0826 | 119.0643 | 119.1376 | -0.83313 | 119.014 | 119.0323 | 119.0964 | -0.76904
4255.6094 | 120.6665 | -119.6091 | 0.70953 | 0.0054168 | -0.00078181 | 0.071722 | 0.025229 | -0.067614 | -0.022031 | -0.0015616 | 0.0073242 | 0.032383 | 0.004578 | -0.041618 | -0.0059046 | 0.0094635 | 0.032043 | -0.018311 | 0.009155 | 0.07782 | 0.10071 | 0.022888 | -0.091553 | -0.022888 | 0.022888 | -0.1236 | 0.027466 | 0.036621 | 0.054932 | -0.004578 | 119.632 | 119.5175 | -0.60883 | 119.5908 | 119.6869 | 0.16937 | -0.67749 | 119.664 | 119.6045 | -0.68207 | 119.5862 | 119.4855 | -0.11902 | -0.67291 | 119.7098 | 119.6411 | 119.6182 | -0.80109 | 119.6365 | 119.6457 | 119.632 | -0.71411
4257.3906 | 120.488 | -119.5908 | 0.66376 | 0.0054168 | 0.0034906 | 0.067876 | 0.026511 | -0.069537 | -0.024808 | -0.0026298 | -0.0003053 | 0.030033 | 0.0075686 | -0.0429 | -0.0061182 | 0.01395 | 0.07782 | 0.09613 | 0.13275 | 0.1236 | 0.050354 | 0.09613 | -0.032043 | 0.041199 | 0.10529 | -0.009155 | -0.009155 | -0.022888 | 0.086975 | 0.022888 | 119.6869 | 119.5587 | -0.6134 | 119.6869 | 119.7144 | 0.15564 | -0.58594 | 119.6777 | 119.6136 | -0.67291 | 119.632 | 119.5816 | -0.032043 | -0.68665 | 119.6411 | 119.6686 | 119.7235 | -0.6958 | 119.5816 | 119.5679 | 119.696 | -0.64087
4259.1406 | 119.8105 | -119.101 | 0.32044 | 0.0054168 | 0.0013544 | 0.068517 | 0.026511 | -0.069537 | -0.021176 | -0.0019888 | 0.014954 | 0.033451 | 0.0071414 | -0.041618 | -0.0035546 | 0.0098907 | 0.013733 | -0.059509 | 0 | 0.054932 | 0.10529 | 0.045776 | -0.086975 | -0.027466 | -0.018311 | -0.13733 | 0.009155 | 0.036621 | 0.050354 | -0.022888 | 119.1467 | 119.014 | -0.21515 | 119.0414 | 119.1559 | 0.14191 | -0.3067 | 119.1513 | 119.0781 | -0.31128 | 119.0735 | 118.9636 | -0.11444 | -0.28381 | 119.2062 | 119.1147 | 119.101 | -0.40741 | 119.1101 | 119.1376 | 119.0826 | -0.34332
4260.8438 | 120.4971 | -119.7418 | 0.37994 | 0.0054168 | 0.0013544 | 0.072363 | 0.029501 | -0.065264 | -0.029294 | 0.00014745 | 0.022583 | 0.029179 | 0.0069278 | -0.043113 | -0.0071862 | 0.010745 | 0.1236 | 0.14648 | 0.16479 | 0.15564 | 0.059509 | 0.086975 | -0.050354 | 0.086975 | 0.18768 | 0.027466 | -0.022888 | -0.009155 | 0.10071 | 0.013733 | 119.8288 | 119.6915 | -0.32044 | 119.8883 | 119.8975 | 0.20599 | -0.25635 | 119.8425 | 119.7556 | -0.40283 | 119.8288 | 119.7693 | 0.013733 | -0.3891 | 119.8013 | 119.8654 | 119.9066 | -0.4303 | 119.7189 | 119.7327 | 119.9295 | -0.36621
4262.5625 | 120.5338 | -120.0119 | 0.33417 | -0.0022127 | -0.00014101 | 0.072149 | 0.028647 | -0.069323 | -0.025235 | -0.00092075 | 0.014954 | 0.030247 | 0.0058596 | -0.043754 | -0.0091088 | 0.011386 | 0.10529 | 0.13275 | 0.14191 | 0.14648 | 0.045776 | 0.073242 | -0.054932 | 0.082397 | 0.16479 | 0.022888 | -0.027466 | 0.009155 | 0.10071 | 0 | 120.0851 | 119.957 | -0.28839 | 120.1447 | 120.1584 | 0.20142 | -0.22888 | 120.1126 | 120.0119 | -0.36163 | 120.0943 | 120.0348 | 0.022888 | -0.32501 | 120.0577 | 120.1172 | 120.1538 | -0.3891 | 119.9844 | 120.0211 | 120.1767 | -0.33417
4264.2969 | 120.639 | -120.108 | 0.27466 | 0.013046 | 0.0071222 | 0.073858 | 0.027579 | -0.069964 | -0.029721 | -0.0024162 | 0.014954 | 0.028324 | 0.0035098 | -0.043754 | -0.0041956 | 0.011173 | 0.054932 | 0.064087 | 0.086975 | 0.10071 | 0.082397 | 0.068665 | -0.064087 | 0.027466 | 0.073242 | -0.032043 | -0.013733 | 0 | 0.07782 | 0 | 120.1767 | 120.0439 | -0.19226 | 120.1721 | 120.2087 | 0.1648 | -0.21973 | 120.1859 | 120.108 | -0.28839 | 120.1355 | 120.076 | -0.032043 | -0.27466 | 120.1904 | 120.163 | 120.195 | -0.33875 | 120.0943 | 120.108 | 120.1813 | -0.27466
4266 | 120.6345 | -120.1904 | 0.29755 | 0.013046 | -0.0022772 | 0.067449 | 0.02822 | -0.069109 | -0.020749 | -0.0011344 | 0.0073242 | 0.033024 | 0.0069278 | -0.042472 | -0.0041956 | 0.0088227 | 0.086975 | 0.027466 | 0.041199 | 0.10529 | 0.09613 | 0.036621 | -0.086975 | 0.041199 | 0.073242 | -0.082397 | 0.004578 | 0.032043 | 0.073242 | -0.009155 | 120.2271 | 120.1035 | -0.20142 | 120.2179 | 120.2957 | 0.19226 | -0.21057 | 120.2637 | 120.1813 | -0.29297 | 120.2316 | 120.108 | -0.073242 | -0.2655 | 120.2866 | 120.2774 | 120.2316 | -0.38452 | 120.195 | 120.2225 | 120.2637 | -0.3067
4267.7656 | 120.6116 | -120.3049 | 0.31586 | -0.0022127 | -0.0016364 | 0.070013 | 0.026724 | -0.070605 | -0.025876 | -0.0017752 | 0.0073242 | 0.031101 | 0.0069278 | -0.042686 | -0.0071862 | 0.012668 | 0.041199 | 0.036621 | 0.059509 | 0.086975 | 0.068665 | 0.036621 | -0.091553 | -0.027466 | 0.054932 | -0.10071 | 0.032043 | 0.045776 | 0.059509 | -0.013733 | 120.3415 | 120.2133 | -0.24719 | 120.3415 | 120.3918 | 0.17853 | -0.27466 | 120.3644 | 120.2911 | -0.28381 | 120.2774 | 120.2042 | -0.086975 | -0.27008 | 120.3735 | 120.3461 | 120.3644 | -0.40741 | 120.3369 | 120.3506 | 120.3598 | -0.32959
4269.4844 | 120.6757 | -120.1996 | 0.33875 | -0.0022127 | -0.003559 | 0.071081 | 0.028433 | -0.068255 | -0.024594 | -0.00070715 | 0.0073242 | 0.032597 | 0.0084232 | -0.044181 | -0.006759 | 0.012027 | 0 | -0.004578 | 0.022888 | 0.054932 | 0.11902 | 0.022888 | -0.07782 | -0.036621 | 0.027466 | -0.11444 | 0.018311 | 0.041199 | 0.041199 | -0.041199 | 120.2225 | 120.1218 | -0.21973 | 120.195 | 120.2545 | 0.13275 | -0.33875 | 120.2408 | 120.1584 | -0.32043 | 120.163 | 120.0851 | -0.073242 | -0.29755 | 120.3186 | 120.1996 | 120.2225 | -0.41657 | 120.2179 | 120.2408 | 120.2271 | -0.37994
4271.2031 | 120.6573 | -120.2499 | 0.35248 | 0.020676 | -0.0024908 | 0.06809 | 0.02587 | -0.0674 | -0.020108 | -0.0011344 | -0.0003053 | 0.034733 | 0.0054324 | -0.042686 | -0.0031274 | 0.0116 | 0.032043 | 0.018311 | 0.022888 | 0.091553 | 0.10071 | 0.036621 | -0.07782 | -0.018311 | 0 | -0.13275 | 0.013733 | 0.041199 | 0.045776 | -0.027466 | 120.2866 | 120.1721 | -0.25177 | 120.2682 | 120.3415 | 0.16937 | -0.32044 | 120.2957 | 120.2225 | -0.33875 | 120.2316 | 120.1172 | -0.10529 | -0.31128 | 120.3506 | 120.282 | 120.2728 | -0.4303 | 120.2637 | 120.2911 | 120.2499 | -0.37994
4272.9219 | 120.7214 | -120.1904 | 0.42572 | 0.013046 | -0.00056821 | 0.070226 | 0.024588 | -0.068041 | -0.021604 | 0.0022836 | 0.0073242 | 0.033665 | 0.0082096 | -0.042259 | -0.0035546 | 0.01395 | -0.022888 | -0.050354 | -0.018311 | 0.045776 | 0.10529 | 0.036621 | -0.09613 | -0.027466 | 0 | -0.12817 | 0.032043 | 0.036621 | 0.036621 | -0.018311 | 120.2271 | 120.0943 | -0.32043 | 120.1401 | 120.2362 | 0.14191 | -0.44861 | 120.2271 | 120.1721 | -0.39368 | 120.163 | 120.0623 | -0.10986 | -0.3891 | 120.2957 | 120.1675 | 120.1721 | -0.52185 | 120.2225 | 120.2271 | 120.1904 | -0.44403
4274.6406 | 120.7031 | -120.3003 | 0.35248 | 0.013046 | -0.00185 | 0.066808 | 0.029929 | -0.066119 | -0.02374 | 0.0016428 | 0.014954 | 0.033024 | 0.0052188 | -0.039909 | -0.0063318 | 0.012027 | 0.041199 | 0.064087 | 0.064087 | 0.10529 | 0.086975 | 0.032043 | -0.10071 | 0.022888 | 0.086975 | -0.059509 | 0.018311 | 0.032043 | 0.045776 | 0.013733 | 120.3323 | 120.1996 | -0.2655 | 120.3644 | 120.4056 | 0.20599 | -0.31128 | 120.3461 | 120.314 | -0.33417 | 120.3232 | 120.2408 | -0.073242 | -0.32044 | 120.3873 | 120.3415 | 120.3644 | -0.45319 | 120.3186 | 120.3323 | 120.3873 | -0.33875
4276.4219 | 120.7947 | -120.2866 | 0.36163 | -0.0022127 | -0.0033454 | 0.069158 | 0.029715 | -0.0674 | -0.025235 | 0.00057465 | 0.014954 | 0.032383 | 0.0058596 | -0.042045 | -0.0037684 | 0.012241 | 0.013733 | 0.027466 | 0.045776 | 0.10529 | 0.091553 | 0.027466 | -0.086975 | 0.013733 | 0.07782 | -0.064087 | 0.009155 | 0.041199 | 0.064087 | -0.018311 | 120.314 | 120.1996 | -0.27008 | 120.314 | 120.3918 | 0.19226 | -0.3479 | 120.3506 | 120.2682 | -0.35248 | 120.3003 | 120.2225 | -0.045776 | -0.32043 | 120.3781 | 120.3003 | 120.3323 | -0.44861 | 120.2957 | 120.3278 | 120.3644 | -0.37994
4278.1562 | 120.7535 | -120.4285 | 0.29755 | -0.0022127 | -0.00185 | 0.071081 | 0.032706 | -0.069537 | -0.028653 | -0.001348 | 0.014954 | 0.02747 | 0.0088504 | -0.041618 | -0.0088952 | 0.012454 | 0.064087 | 0.12817 | 0.12817 | 0.15106 | 0.064087 | 0.068665 | -0.068665 | 0.009155 | 0.13275 | -0.013733 | -0.013733 | 0.032043 | 0.082397 | -0.004578 | 120.4971 | 120.3598 | -0.23346 | 120.5566 | 120.5795 | 0.21973 | -0.23346 | 120.5109 | 120.4239 | -0.31128 | 120.4376 | 120.4147 | -0.009155 | -0.2655 | 120.4926 | 120.4926 | 120.5566 | -0.36621 | 120.4147 | 120.4605 | 120.5612 | -0.30212
4279.875 | 120.8359 | -120.3735 | 0.30212 | -0.0022127 | -0.00056821 | 0.072576 | 0.030783 | -0.068896 | -0.025235 | -0.0017752 | 0.0073242 | 0.028111 | 0.0060732 | -0.041618 | -0.0082544 | 0.010959 | 0.068665 | 0.10071 | 0.13275 | 0.15106 | 0.050354 | 0.082397 | -0.050354 | 0.009155 | 0.12817 | -0.022888 | -0.009155 | 0.022888 | 0.082397 | -0.009155 | 120.4559 | 120.3232 | -0.25177 | 120.4742 | 120.5246 | 0.20142 | -0.23346 | 120.4559 | 120.3644 | -0.31128 | 120.3827 | 120.3506 | -0.013733 | -0.27924 | 120.4239 | 120.4422 | 120.5063 | -0.35248 | 120.3644 | 120.3964 | 120.5017 | -0.31128
4281.6406 | 120.8633 | -120.3232 | 0.36621 | 0.0054168 | 0.001568 | 0.072149 | 0.026083 | -0.06975 | -0.027585 | -0.0017752 | 0.0073242 | 0.028538 | 0.0037234 | -0.044395 | -0.0086816 | 0.010318 | 0.09613 | 0.15106 | 0.15106 | 0.14648 | 0.064087 | 0.07782 | -0.050354 | 0.064087 | 0.17853 | 0.018311 | -0.018311 | 0.009155 | 0.082397 | 0.018311 | 120.401 | 120.2728 | -0.30212 | 120.4742 | 120.4697 | 0.19684 | -0.27008 | 120.4056 | 120.3415 | -0.38452 | 120.3873 | 120.3415 | 0 | -0.35706 | 120.3873 | 120.4193 | 120.4742 | -0.41657 | 120.3049 | 120.3323 | 120.5017 | -0.3479
4283.3906 | 120.9091 | -120.4285 | 0.2655 | 0.0054168 | 0.0041314 | 0.07044 | 0.029074 | -0.069537 | -0.028226 | -0.00049335 | 0.0073242 | 0.027043 | 0.0052188 | -0.043327 | -0.0080408 | 0.013522 | 0.036621 | 0.068665 | 0.10529 | 0.10986 | 0.068665 | 0.068665 | -0.050354 | 0.013733 | 0.073242 | -0.022888 | -0.018311 | 0.009155 | 0.091553 | 0.009155 | 120.4971 | 120.3781 | -0.19684 | 120.4971 | 120.5383 | 0.16022 | -0.22888 | 120.52 | 120.4376 | -0.28381 | 120.4422 | 120.4056 | -0.032043 | -0.25635 | 120.4971 | 120.4651 | 120.5338 | -0.31586 | 120.4102 | 120.4376 | 120.5017 | -0.25635
4285.125 | 120.845 | -120.5017 | 0.29297 | -0.0022127 | -0.002918 | 0.069158 | 0.025443 | -0.066546 | -0.018826 | -0.00049335 | 0.0073242 | 0.03516 | 0.0058596 | -0.039909 | -0.002273 | 0.010318 | 0.027466 | -0.018311 | 0.004578 | 0.082397 | 0.091553 | 0.032043 | -0.086975 | -0.018311 | -0.004578 | -0.13733 | 0.027466 | 0.045776 | 0.064087 | -0.022888 | 120.5338 | 120.4147 | -0.20142 | 120.4834 | 120.5841 | 0.16937 | -0.2655 | 120.5658 | 120.4788 | -0.2655 | 120.4834 | 120.3644 | -0.11444 | -0.24719 | 120.5933 | 120.5292 | 120.5063 | -0.37994 | 120.5292 | 120.5475 | 120.4971 | -0.31586
4286.875 | 120.9503 | -120.4559 | 0.27924 | 0.0054168 | 0.004345 | 0.07044 | 0.027152 | -0.068896 | -0.028226 | -0.0019888 | 0.0073242 | 0.030888 | 0.0067142 | -0.041404 | -0.010391 | 0.012241 | 0.041199 | 0.059509 | 0.10071 | 0.11444 | 0.054932 | 0.068665 | -0.064087 | 0.009155 | 0.073242 | -0.022888 | -0.004578 | 0.013733 | 0.064087 | 0 | 120.5246 | 120.3918 | -0.2243 | 120.5154 | 120.5704 | 0.17853 | -0.23804 | 120.52 | 120.4559 | -0.28381 | 120.4651 | 120.433 | -0.022888 | -0.2655 | 120.5109 | 120.4971 | 120.5566 | -0.34332 | 120.4514 | 120.4697 | 120.5292 | -0.27924
4288.6406 | 120.9091 | -120.4971 | 0.28839 | 0.020676 | 0.0064814 | 0.068731 | 0.027152 | -0.0674 | -0.027371 | -0.0022024 | 0.0073242 | 0.030461 | 0.0054324 | -0.043113 | -0.0078272 | 0.011386 | 0.064087 | 0.082397 | 0.09613 | 0.086975 | 0.064087 | 0.073242 | -0.064087 | 0.036621 | 0.082397 | -0.022888 | -0.022888 | 0.009155 | 0.10071 | 0.018311 | 120.5704 | 120.433 | -0.2243 | 120.5795 | 120.5841 | 0.15106 | -0.2243 | 120.5978 | 120.5154 | -0.31128 | 120.5338 | 120.4742 | -0.041199 | -0.27924 | 120.5612 | 120.5612 | 120.5933 | -0.35248 | 120.4742 | 120.5063 | 120.5795 | -0.27008
4290.3594 | 121.0602 | -120.3644 | 0.40283 | -0.0022127 | 0.0051996 | 0.071722 | 0.026297 | -0.067614 | -0.028012 | -0.0015616 | 0.014954 | 0.026188 | 0.0054324 | -0.044609 | -0.0071862 | 0.010318 | 0.045776 | 0.045776 | 0.086975 | 0.10529 | 0.059509 | 0.073242 | -0.036621 | 0.022888 | 0.064087 | -0.018311 | -0.004578 | -0.009155 | 0.07782 | 0.009155 | 120.4376 | 120.3278 | -0.34332 | 120.4102 | 120.4697 | 0.14191 | -0.35706 | 120.4422 | 120.3735 | -0.40741 | 120.3873 | 120.3461 | -0.027466 | -0.41199 | 120.4239 | 120.4102 | 120.4514 | -0.43945 | 120.3598 | 120.3552 | 120.4285 | -0.39368
4292.0938 | 120.9412 | -120.5109 | 0.28839 | 0.0054168 | -0.00099541 | 0.070226 | 0.02822 | -0.068041 | -0.022672 | -0.0015616 | 0.014954 | 0.03516 | 0.0075686 | -0.043541 | -0.0069726 | 0.0092499 | 0.004578 | -0.004578 | 0.013733 | 0.068665 | 0.10529 | 0.018311 | -0.086975 | -0.036621 | 0.018311 | -0.13733 | 0.022888 | 0.036621 | 0.054932 | -0.018311 | 120.5292 | 120.4239 | -0.18311 | 120.5063 | 120.5795 | 0.15564 | -0.28381 | 120.5658 | 120.4926 | -0.2655 | 120.4742 | 120.3735 | -0.11902 | -0.25177 | 120.6162 | 120.5154 | 120.5246 | -0.37537 | 120.5338 | 120.5475 | 120.5292 | -0.3067
4293.8125 | 120.9274 | -120.5521 | 0.27008 | 0.0054168 | 0.0011408 | 0.071935 | 0.027152 | -0.065691 | -0.025022 | -0.001348 | 0.014954 | 0.029179 | 0.0069278 | -0.043327 | -0.0086816 | 0.013309 | 0.10986 | 0.13733 | 0.15564 | 0.15564 | 0.068665 | 0.07782 | -0.054932 | 0.064087 | 0.15564 | 0 | -0.022888 | -0.004578 | 0.091553 | 0.022888 | 120.6299 | 120.4971 | -0.20142 | 120.6894 | 120.7077 | 0.21057 | -0.16022 | 120.6436 | 120.575 | -0.29297 | 120.6162 | 120.5521 | -0.022888 | -0.27466 | 120.6207 | 120.6619 | 120.7077 | -0.32501 | 120.5292 | 120.5475 | 120.7077 | -0.24719
4295.5469 | 120.8588 | -118.8629 | 1.6617 | 0.013046 | 0.0011408 | 0.071722 | 0.02886 | -0.068255 | -0.026303 | -0.0015616 | 0.0073242 | 0.028965 | 0.0065006 | -0.042045 | -0.0086816 | 0.010745 | 0.1236 | 0.14648 | 0.16479 | 0.14648 | 0.068665 | 0.068665 | -0.059509 | 0.073242 | 0.17395 | 0.027466 | -0.041199 | 0 | 0.086975 | 0.018311 | 118.9316 | 118.8034 | -1.593 | 119.0094 | 119.0094 | 0.20599 | -1.5381 | 118.9499 | 118.8812 | -1.7029 | 118.9362 | 118.8904 | 0.009155 | -1.6617 | 118.9316 | 118.9865 | 119.0277 | -1.7212 | 118.8217 | 118.8629 | 119.0369 | -1.6434
4297.2812 | 120.2591 | -94.3405 | 25.3738 | 0.013046 | 0.001568 | 0.071722 | 0.02822 | -0.068896 | -0.025876 | -0.0011344 | 0.0073242 | 0.028965 | 0.0043644 | -0.041404 | -0.005691 | 0.0116 | 0.091553 | 0.14191 | 0.14648 | 0.13733 | 0.050354 | 0.059509 | -0.068665 | 0.07782 | 0.17395 | 0.018311 | -0.032043 | -0.036621 | 0.086975 | 0.009155 | 94.4 | 94.2719 | -25.3235 | 94.4824 | 94.4778 | 0.20599 | -25.2823 | 94.4275 | 94.3497 | -25.4059 | 94.4183 | 94.3588 | 0.009156 | -25.4105 | 94.3909 | 94.4321 | 94.487 | -25.4425 | 94.3085 | 94.3039 | 94.5145 | -25.3647
4299 | 120.7626 | -113.887 | 6.3583 | 0.013046 | 0.0037042 | 0.073003 | 0.027152 | -0.071245 | -0.028012 | -0.001348 | 0.014954 | 0.028752 | 0.0071414 | -0.042686 | -0.0065454 | 0.011386 | 0.045776 | 0.068665 | 0.10071 | 0.11444 | 0.073242 | 0.059509 | -0.086975 | 0.045776 | 0.11902 | 0.004578 | -0.018311 | 0.004578 | 0.086975 | 0.018311 | 113.9465 | 113.8 | -6.2851 | 113.9557 | 114.0015 | 0.20142 | -6.3126 | 113.974 | 113.9053 | -6.3766 | 113.9328 | 113.8916 | -0.013733 | -6.3538 | 113.9603 | 113.9328 | 113.9877 | -6.4453 | 113.8687 | 113.8916 | 114.006 | -6.34
4300.7188 | 120.8038 | -109.8633 | 10.4965 | -0.0022127 | 0.0034906 | 0.071508 | 0.029929 | -0.068468 | -0.02609 | -0.0024162 | 0.014954 | 0.02982 | 0.006287 | -0.043754 | -0.0069726 | 0.011813 | 0.073242 | 0.10529 | 0.11444 | 0.12817 | 0.036621 | 0.068665 | -0.059509 | 0.041199 | 0.07782 | -0.045776 | -0.018311 | -0.009155 | 0.09613 | -0.009155 | 109.9319 | 109.8038 | -10.4599 | 109.9686 | 109.9915 | 0.18768 | -10.4233 | 109.9594 | 109.8541 | -10.5148 | 109.9045 | 109.8175 | -0.036621 | -10.5057 | 109.8999 | 109.9365 | 109.9777 | -10.556 | 109.845 | 109.8541 | 109.9411 | -10.5057
4302.4531 | 116.7709 | -93.2281 | 23.5336 | 0.0054168 | 0.0026362 | 0.070226 | 0.025229 | -0.066546 | -0.024808 | -0.0026298 | -0.0003053 | 0.031315 | 0.0054324 | -0.044609 | -0.005691 | 0.012027 | 0.073242 | 0.068665 | 0.10986 | 0.09613 | 0.068665 | 0.086975 | -0.059509 | 0.036621 | 0.07782 | -0.032043 | 0 | 0 | 0.07782 | -0.009155 | 93.3151 | 93.1686 | -23.465 | 93.2968 | 93.3243 | 0.15564 | -23.4604 | 93.306 | 93.219 | -23.5336 | 93.2648 | 93.1961 | -0.022888 | -23.5336 | 93.2968 | 93.3014 | 93.338 | -23.5931 | 93.2281 | 93.2281 | 93.306 | -23.5428
4304.1875 | 120.4788 | -94.6609 | 25.1541 | 0.0054168 | 0.0041314 | 0.07044 | 0.024588 | -0.066973 | -0.021176 | 0.00207 | -0.0003053 | 0.03217 | 0.0018008 | -0.043327 | -0.0020594 | 0.011813 | 0.10986 | 0.07782 | 0.11902 | 0.13275 | 0.068665 | 0.050354 | -0.045776 | 0.091553 | 0.11444 | -0.013733 | -0.032043 | -0.022888 | 0.09613 | 0.018311 | 94.7113 | 94.6152 | -25.0854 | 94.7388 | 94.7937 | 0.17853 | -25.0443 | 94.7571 | 94.6793 | -25.1862 | 94.7525 | 94.6472 | -0.032044 | -25.177 | 94.7296 | 94.7708 | 94.78 | -25.1999 | 94.6289 | 94.6381 | 94.7754 | -25.1358
4305.9062 | 120.6162 | -94.4824 | 25.7767 | -0.0022127 | -0.0041998 | 0.067876 | 0.026297 | -0.070605 | -0.018613 | -0.001348 | 0.014954 | 0.033451 | 0.0067142 | -0.043754 | -0.0031274 | 0.010959 | 0.07782 | 0.041199 | 0.041199 | 0.091553 | 0.091553 | 0.036621 | -0.091553 | 0.018311 | 0.036621 | -0.10529 | -0.004578 | 0.013733 | 0.073242 | -0.027466 | 94.519 | 94.3909 | -25.6851 | 94.5236 | 94.574 | 0.18311 | -25.6989 | 94.5557 | 94.455 | -25.7812 | 94.5007 | 94.3771 | -0.07782 | -25.7629 | 94.574 | 94.5602 | 94.5236 | -25.8682 | 94.4778 | 94.4962 | 94.519 | -25.8041
4307.6406 | 120.8038 | -111.763 | 8.4961 | 0.013046 | 0.0045588 | 0.070226 | 0.028647 | -0.069109 | -0.024808 | 0.0022836 | 0.014954 | 0.029179 | 0.007355 | -0.044822 | -0.0063318 | 0.011173 | 0.10071 | 0.13275 | 0.15564 | 0.16022 | 0.050354 | 0.064087 | -0.041199 | 0.09613 | 0.13733 | 0.004578 | -0.022888 | -0.013733 | 0.07782 | 0.009155 | 111.8271 | 111.7218 | -8.4457 | 111.8958 | 111.9232 | 0.20142 | -8.3954 | 111.8408 | 111.7722 | -8.519 | 111.8591 | 111.7676 | -0.004577 | -8.5098 | 111.8134 | 111.8637 | 111.9186 | -8.5373 | 111.7401 | 111.7493 | 111.9003 | -8.4869
4309.3906 | 120.8588 | -111.8454 | 8.551 | 0.013046 | 0.0041314 | 0.071722 | 0.027579 | -0.070391 | -0.028012 | -0.0015616 | 0.0073242 | 0.02982 | 0.0065006 | -0.04525 | -0.0069726 | 0.013522 | 0.022888 | 0.068665 | 0.10529 | 0.10529 | 0.054932 | 0.091553 | -0.059509 | 0.018311 | 0.11444 | 0 | -0.022888 | 0.004578 | 0.07782 | 0.027466 | 111.937 | 111.7859 | -8.4961 | 111.9141 | 111.9507 | 0.16479 | -8.5281 | 111.9232 | 111.8729 | -8.5739 | 111.8637 | 111.8454 | -0.027466 | -8.5464 | 111.9003 | 111.8683 | 111.9507 | -8.6105 | 111.8225 | 111.85 | 111.9598 | -8.5236
4311.125 | 120.932 | -112.9257 | 7.4524 | 0.0054168 | 0.0028498 | 0.071935 | 0.028647 | -0.066332 | -0.028226 | -0.0017752 | 0.022583 | 0.02982 | 0.0054324 | -0.041404 | -0.008468 | 0.010745 | 0.09613 | 0.11444 | 0.14648 | 0.13733 | 0.059509 | 0.068665 | -0.059509 | 0.068665 | 0.16937 | 0.036621 | -0.018311 | 0 | 0.07782 | 0.004578 | 112.9944 | 112.8662 | -7.3929 | 113.0402 | 113.063 | 0.19684 | -7.3563 | 113.0035 | 112.9303 | -7.4707 | 112.9944 | 112.9623 | 0.032043 | -7.4524 | 112.9852 | 113.0219 | 113.0722 | -7.5119 | 112.9074 | 112.9257 | 113.0951 | -7.4478
4312.8594 | 120.9274 | -113.7634 | 6.7062 | 0.0054168 | 0.0026362 | 0.068517 | 0.026297 | -0.066119 | -0.022672 | -6.615e-05 | 0.022583 | 0.030888 | 0.0058596 | -0.041618 | -0.0029138 | 0.010532 | 0.082397 | 0.082397 | 0.10529 | 0.14191 | 0.082397 | 0.073242 | -0.059509 | 0.091553 | 0.1236 | 0 | -0.018311 | -0.018311 | 0.10529 | 0.027466 | 113.8367 | 113.7039 | -6.6238 | 113.8458 | 113.9053 | 0.20142 | -6.6238 | 113.8687 | 113.7909 | -6.7245 | 113.855 | 113.7634 | -0.027466 | -6.7245 | 113.8458 | 113.8458 | 113.8687 | -6.7657 | 113.7451 | 113.7451 | 113.887 | -6.6788
4314.625 | 120.9778 | -114.2395 | 6.2622 | 0.0054168 | 0.0028498 | 0.073217 | 0.029715 | -0.068041 | -0.026731 | -0.0015616 | 0.014954 | 0.029179 | 0.0065006 | -0.044181 | -0.0065454 | 0.011173 | 0.10986 | 0.16479 | 0.16479 | 0.14648 | 0.068665 | 0.082397 | -0.045776 | 0.086975 | 0.1831 | 0.068665 | -0.041199 | -0.013733 | 0.09613 | 0.018311 | 114.3219 | 114.1937 | -6.1935 | 114.4043 | 114.386 | 0.19226 | -6.1523 | 114.3356 | 114.2578 | -6.3034 | 114.3265 | 114.3082 | 0.050354 | -6.2759 | 114.3082 | 114.3494 | 114.4043 | -6.308 | 114.1983 | 114.2258 | 114.4226 | -6.2439
4316.3594 | 120.4056 | -117.4301 | 2.623 | -0.0022127 | 0.0034906 | 0.068517 | 0.024374 | -0.070177 | -0.022672 | 0.0012154 | 0.0073242 | 0.031101 | 0.0030826 | -0.042686 | -0.002273 | 0.0096771 | 0.12817 | 0.11444 | 0.12817 | 0.15106 | 0.064087 | 0.082397 | -0.050354 | 0.10529 | 0.13275 | 0.004578 | -0.036621 | -0.004578 | 0.091553 | 0.036621 | 117.5125 | 117.3798 | -2.5589 | 117.5446 | 117.5812 | 0.20142 | -2.4948 | 117.5217 | 117.4667 | -2.6596 | 117.5354 | 117.4347 | -0.032043 | -2.6276 | 117.4942 | 117.5583 | 117.5583 | -2.6733 | 117.3935 | 117.4255 | 117.5629 | -2.5864
4318.0938 | 120.9641 | -116.2903 | 4.2526 | 0.013046 | 0.0062676 | 0.07044 | 0.029074 | -0.069964 | -0.025022 | -0.00070715 | 0.014954 | 0.029392 | 0.0037234 | -0.044181 | -0.0052636 | 0.012027 | 0.064087 | 0.064087 | 0.091553 | 0.10986 | 0.073242 | 0.064087 | -0.068665 | 0.018311 | 0.07782 | -0.032043 | -0.027466 | 0.018311 | 0.082397 | 0.013733 | 116.3544 | 116.2216 | -4.1794 | 116.3544 | 116.4001 | 0.17853 | -4.1885 | 116.3727 | 116.304 | -4.2801 | 116.3086 | 116.2582 | -0.045776 | -4.2343 | 116.3635 | 116.3544 | 116.3818 | -4.3213 | 116.2628 | 116.3086 | 116.3681 | -4.2389
4319.8125 | 120.726 | -118.895 | 1.5793 | 0.013046 | -0.00185 | 0.068731 | 0.02352 | -0.070391 | -0.01904 | 0.00036105 | 0.014954 | 0.034092 | 0.003937 | -0.041191 | -0.0012048 | 0.0094635 | 0.059509 | -0.018311 | 0.013733 | 0.073242 | 0.10986 | 0.041199 | -0.073242 | -0.009155 | -0.004578 | -0.13275 | 0.018311 | 0.032043 | 0.050354 | -0.009155 | 118.9362 | 118.8217 | -1.4694 | 118.8766 | 118.9682 | 0.14648 | -1.5198 | 118.9453 | 118.8858 | -1.561 | 118.8858 | 118.7622 | -0.1236 | -1.5472 | 119.0048 | 118.9545 | 118.9087 | -1.6525 | 118.9133 | 118.927 | 118.8904 | -1.5884
4321.5312 | 120.6802 | -117.865 | 2.5955 | 0.020676 | -0.0012092 | 0.067876 | 0.028647 | -0.067828 | -0.020749 | 0.00207 | 0.014954 | 0.034092 | 0.005646 | -0.043968 | -0.0048364 | 0.012454 | 0.004578 | -0.041199 | 0 | 0.059509 | 0.082397 | 0.050354 | -0.07782 | -0.027466 | -0.027466 | -0.15564 | 0.009155 | 0.041199 | 0.050354 | -0.032043 | 117.9153 | 117.7872 | -2.5131 | 117.8238 | 117.9245 | 0.13733 | -2.5909 | 117.9153 | 117.8329 | -2.5864 | 117.8375 | 117.7094 | -0.1236 | -2.5543 | 117.9474 | 117.8696 | 117.865 | -2.6733 | 117.8741 | 117.9062 | 117.8375 | -2.6276
4323.25 | 120.7855 | -119.0277 | 1.4511 | 0.013046 | 0.0047724 | 0.070226 | 0.025656 | -0.067614 | -0.029508 | 0.0018564 | 0.0073242 | 0.028965 | 0.0037234 | -0.044822 | -0.0061182 | 0.013309 | 0.091553 | 0.12817 | 0.14191 | 0.14191 | 0.068665 | 0.07782 | -0.050354 | 0.059509 | 0.12817 | 0 | -0.041199 | -0.004578 | 0.091553 | 0.022888 | 119.1055 | 118.9774 | -1.3824 | 119.1559 | 119.1696 | 0.19226 | -1.3596 | 119.1193 | 119.0506 | -1.4923 | 119.0872 | 119.0277 | -0.022888 | -1.4557 | 119.0964 | 119.1193 | 119.1696 | -1.5015 | 118.9865 | 119.0231 | 119.1559 | -1.4282
4325 | 120.8679 | -114.9811 | 5.5893 | 0.0054168 | -0.0027044 | 0.070013 | 0.028647 | -0.066759 | -0.025235 | 0.0012154 | 0.0073242 | 0.033024 | 0.006287 | -0.041618 | -0.003341 | 0.011173 | 0.036621 | 0.027466 | 0.041199 | 0.091553 | 0.09613 | 0.036621 | -0.10071 | 0.009155 | 0.068665 | -0.064087 | 0.013733 | 0.045776 | 0.054932 | -0.018311 | 115.0177 | 114.8804 | -5.4932 | 115.0085 | 115.0726 | 0.19226 | -5.5527 | 115.036 | 114.9628 | -5.5756 | 114.9902 | 114.917 | -0.045776 | -5.5435 | 115.0772 | 115.0177 | 115.0223 | -5.69 | 114.9948 | 115.0269 | 115.0497 | -5.6076
4326.7344 | 120.0027 | -118.4509 | 1.3046 | 0.0054168 | 0.0017816 | 0.068731 | 0.029501 | -0.068682 | -0.025022 | 0.00014745 | 0.014954 | 0.030461 | 0.0067142 | -0.044609 | -0.010177 | 0.012668 | 0.064087 | 0.11902 | 0.12817 | 0.15106 | 0.064087 | 0.073242 | -0.045776 | 0.022888 | 0.12817 | -0.032043 | -0.027466 | 0.009155 | 0.086975 | -0.004578 | 118.5242 | 118.4052 | -1.2405 | 118.5699 | 118.602 | 0.19684 | -1.2405 | 118.5379 | 118.4464 | -1.3321 | 118.4738 | 118.4189 | -0.027465 | -1.2955 | 118.515 | 118.515 | 118.5791 | -1.3504 | 118.4235 | 118.4601 | 118.5791 | -1.3092
4328.4531 | 120.0119 | -112.2437 | 7.1823 | -0.0022127 | 0.0056268 | 0.073003 | 0.027579 | -0.068255 | -0.02844 | -0.00070715 | 0.014954 | 0.028111 | 0.003937 | -0.043754 | -0.0093226 | 0.0116 | 0.068665 | 0.11902 | 0.14648 | 0.14648 | 0.059509 | 0.07782 | -0.059509 | 0.064087 | 0.15106 | 0.032043 | -0.013733 | -0.004578 | 0.086975 | -0.004578 | 112.3215 | 112.1841 | -7.1228 | 112.3627 | 112.3901 | 0.20599 | -7.1136 | 112.3306 | 112.2391 | -7.196 | 112.3077 | 112.2757 | 0.036621 | -7.1869 | 112.3032 | 112.3123 | 112.3901 | -7.2418 | 112.2299 | 112.2391 | 112.3947 | -7.1869
4330.1875 | 119.7464 | -114.1434 | 5.3192 | 0.013046 | -0.00014101 | 0.069372 | 0.026724 | -0.068468 | -0.019895 | 0.00078825 | -0.0079343 | 0.033665 | 0.006287 | -0.042686 | -0.00505 | 0.0092499 | 0.086975 | 0.064087 | 0.064087 | 0.11902 | 0.11444 | 0.050354 | -0.086975 | 0.032043 | 0.073242 | -0.082397 | -0.004578 | 0.027466 | 0.07782 | -0.032043 | 114.1937 | 114.0564 | -5.2048 | 114.2075 | 114.2624 | 0.20599 | -5.2322 | 114.2212 | 114.1113 | -5.3238 | 114.1754 | 114.061 | -0.050354 | -5.2917 | 114.2578 | 114.2303 | 114.2075 | -5.4062 | 114.1388 | 114.1708 | 114.2166 | -5.3513
4331.9688 | 118.3594 | -65.7669 | 49.8688 | -0.0022127 | 0.0030634 | 0.067876 | 0.028647 | -0.068896 | -0.024167 | 0.0010018 | 0.014954 | 0.032383 | 0.005646 | -0.0429 | -0.0029138 | 0.010532 | 0.045776 | 0.054932 | 0.086975 | 0.10529 | 0.054932 | 0.059509 | -0.059509 | 0.068665 | 0.10529 | -0.018311 | -0.045776 | -0.032043 | 0.068665 | 0.013733 | 65.8264 | 65.7074 | -49.8138 | 65.8218 | 65.8722 | 0.16479 | -49.823 | 65.8356 | 65.7806 | -49.9145 | 65.8356 | 65.7486 | -0.032044 | -49.9008 | 65.8218 | 65.8127 | 65.8539 | -49.9283 | 65.7211 | 65.7349 | 65.8722 | -49.855
4333.6875 | 118.2953 | -116.8625 | 2.4536 | 0.0054168 | 0.0064814 | 0.070654 | 0.026083 | -0.070605 | -0.027158 | -6.615e-05 | 0.014954 | 0.030033 | 0.0047916 | -0.043113 | -0.0071862 | 0.0116 | 0.068665 | 0.10071 | 0.1236 | 0.1236 | 0.064087 | 0.064087 | -0.073242 | 0.022888 | 0.07782 | -0.018311 | -0.018311 | 0.009155 | 0.09613 | 0 | 116.9266 | 116.7892 | -2.3895 | 116.9632 | 116.9861 | 0.19684 | -2.3849 | 116.9586 | 116.8625 | -2.4719 | 116.8854 | 116.8442 | -0.018311 | -2.4445 | 116.9266 | 116.9312 | 116.9861 | -2.5269 | 116.8442 | 116.8716 | 116.9403 | -2.4536
4335.4688 | 119.989 | -117.8833 | 1.7212 | -0.0022127 | -0.00078181 | 0.06809 | 0.026083 | -0.067614 | -0.019467 | -0.00049335 | -0.0079343 | 0.033879 | 0.0060732 | -0.040123 | -0.00505 | 0.010532 | 0.082397 | 0.050354 | 0.064087 | 0.10529 | 0.07782 | 0.064087 | -0.086975 | 0.036621 | 0.07782 | -0.082397 | 0.013733 | 0.036621 | 0.073242 | -0.009155 | 117.9474 | 117.7963 | -1.6434 | 117.9337 | 117.9886 | 0.19226 | -1.6388 | 117.9565 | 117.8741 | -1.7075 | 117.9199 | 117.8009 | -0.073242 | -1.6846 | 117.9611 | 117.9657 | 117.9474 | -1.8082 | 117.897 | 117.9199 | 117.9611 | -1.7303
4337.1875 | 116.4688 | -86.5997 | 29.393 | 0.013046 | -0.002918 | 0.069372 | 0.029501 | -0.068468 | -0.025449 | -0.00027975 | -0.0003053 | 0.036015 | 0.0075686 | -0.041832 | -0.0071862 | 0.0116 | -0.018311 | -0.018311 | -0.009155 | 0.050354 | 0.091553 | 0.018311 | -0.11902 | -0.036621 | 0.022888 | -0.11902 | -0.004578 | 0.036621 | 0.032043 | -0.041199 | 86.618 | 86.4807 | -29.3015 | 86.5814 | 86.6501 | 0.16937 | -29.4113 | 86.6318 | 86.5585 | -29.3976 | 86.5631 | 86.4807 | -0.07782 | -29.3564 | 86.6913 | 86.5814 | 86.5906 | -29.512 | 86.5952 | 86.6364 | 86.6226 | -29.4342
4338.9688 | 119.6182 | -118.8171 | 0.60883 | 0.013046 | 0.0026362 | 0.070013 | 0.028647 | -0.068682 | -0.022885 | 0.00078825 | -0.0003053 | 0.03217 | 0.0077822 | -0.043541 | -0.0041956 | 0.013309 | -0.004578 | -0.032043 | 0 | 0.068665 | 0.10529 | 0.050354 | -0.086975 | -0.032043 | -0.032043 | -0.1236 | 0.018311 | 0.054932 | 0.041199 | -0.036621 | 118.8675 | 118.7302 | -0.50354 | 118.7851 | 118.8858 | 0.15564 | -0.6134 | 118.8583 | 118.7805 | -0.59052 | 118.7851 | 118.6935 | -0.086975 | -0.55389 | 118.9224 | 118.8126 | 118.8171 | -0.6958 | 118.8354 | 118.8721 | 118.7851 | -0.64545
4340.7031 | 120.1218 | -119.577 | 0.21515 | 0.013046 | 0.0037042 | 0.068517 | 0.031638 | -0.067828 | -0.030576 | -0.0028434 | 0.0073242 | 0.027897 | 0.0050052 | -0.0429 | -0.0099634 | 0.012027 | 0.013733 | 0.068665 | 0.10071 | 0.12817 | 0.054932 | 0.064087 | -0.068665 | 0.013733 | 0.09613 | 0.004578 | -0.004578 | -0.004578 | 0.082397 | 0.004578 | 119.6411 | 119.5084 | -0.16022 | 119.6457 | 119.7052 | 0.19684 | -0.20142 | 119.6594 | 119.5816 | -0.21973 | 119.5908 | 119.5816 | 0 | -0.21973 | 119.632 | 119.5908 | 119.6777 | -0.28381 | 119.5724 | 119.5724 | 119.6732 | -0.21057
4342.4531 | 120.2408 | -119.696 | 0.21515 | 0.013046 | 0.004345 | 0.070867 | 0.026297 | -0.067614 | -0.025022 | 0.00057465 | -0.0003053 | 0.029606 | 0.007996 | -0.041191 | -0.0071862 | 0.011813 | 0.086975 | 0.11444 | 0.14191 | 0.13733 | 0.041199 | 0.07782 | -0.050354 | 0.045776 | 0.091553 | -0.004578 | -0.013733 | -0.004578 | 0.091553 | 0.004578 | 119.7739 | 119.6457 | -0.17395 | 119.8105 | 119.8334 | 0.18768 | -0.12817 | 119.7876 | 119.7006 | -0.22888 | 119.7418 | 119.6915 | -0.009156 | -0.21973 | 119.7372 | 119.783 | 119.838 | -0.2655 | 119.6823 | 119.6915 | 119.7876 | -0.21057
4344.3438 | 120.3873 | -119.8471 | 0.21973 | 0.013046 | 0.003277 | 0.072363 | 0.032492 | -0.069109 | -0.028653 | -0.0034842 | 0.014954 | 0.02982 | 0.0058596 | -0.042686 | -0.0091088 | 0.012241 | 0.082397 | 0.11902 | 0.13275 | 0.15564 | 0.073242 | 0.091553 | -0.064087 | 0.068665 | 0.16479 | 0.036621 | -0.004578 | 0.004578 | 0.073242 | 0.027466 | 119.9387 | 119.783 | -0.14649 | 119.9661 | 120.0027 | 0.21973 | -0.13733 | 119.9203 | 119.8746 | -0.22431 | 119.9158 | 119.8837 | 0.009155 | -0.21515 | 119.9203 | 119.9295 | 119.9799 | -0.28381 | 119.8425 | 119.8517 | 120.0119 | -0.19226
4346.1562 | 119.989 | -119.4534 | 0.25177 | 0.013046 | -0.00014101 | 0.069158 | 0.030569 | -0.067828 | -0.021604 | -0.00049335 | 0.014954 | 0.030674 | 0.0058596 | -0.044609 | -0.0052636 | 0.0088227 | 0.013733 | -0.009155 | 0.004578 | 0.064087 | 0.10986 | 0.018311 | -0.10071 | -0.027466 | 0.032043 | -0.10986 | 0.018311 | 0.045776 | 0.068665 | -0.018311 | 119.4717 | 119.3527 | -0.14191 | 119.4443 | 119.5175 | 0.1648 | -0.23804 | 119.5221 | 119.4351 | -0.23346 | 119.426 | 119.3436 | -0.091552 | -0.20599 | 119.5633 | 119.4672 | 119.458 | -0.35248 | 119.4717 | 119.4992 | 119.4855 | -0.27008
4347.9688 | 120.3644 | -119.8151 | 0.1831 | 0.0054168 | 0.003277 | 0.067449 | 0.027792 | -0.066759 | -0.020108 | -0.00049335 | -0.0003053 | 0.032597 | 0.0077822 | -0.041191 | -0.0061182 | 0.010959 | 0.064087 | 0.045776 | 0.068665 | 0.10071 | 0.091553 | 0.059509 | -0.068665 | 0.059509 | 0.10071 | 0 | -0.009155 | 0.009155 | 0.091553 | 0.022888 | 119.8746 | 119.7464 | -0.091552 | 119.8608 | 119.9158 | 0.16937 | -0.11902 | 119.9066 | 119.838 | -0.19226 | 119.8746 | 119.8151 | -0.022888 | -0.17395 | 119.9066 | 119.8791 | 119.8837 | -0.25177 | 119.8059 | 119.8242 | 119.9158 | -0.16022
4349.7812 | 120.4468 | -119.8746 | 0.20599 | 0.013046 | 0.004345 | 0.069372 | 0.027152 | -0.068041 | -0.021604 | -0.0024162 | 0.014954 | 0.031315 | 0.0041506 | -0.04055 | -0.0052636 | 0.012454 | 0.041199 | 0.009155 | 0.032043 | 0.09613 | 0.091553 | 0.054932 | -0.064087 | 0.054932 | 0.07782 | -0.032043 | -0.027466 | 0 | 0.086975 | 0.009155 | 119.9295 | 119.8105 | -0.11444 | 119.8837 | 119.9707 | 0.16022 | -0.1648 | 119.9615 | 119.8837 | -0.23346 | 119.9295 | 119.8425 | -0.041198 | -0.20599 | 119.9661 | 119.9158 | 119.9066 | -0.27008 | 119.8471 | 119.8746 | 119.9524 | -0.19684
4351.6094 | 120.3735 | -119.9936 | 0.31586 | -0.0022127 | -0.00056821 | 0.070226 | 0.02822 | -0.068041 | -0.02609 | -0.0024162 | 0.0073242 | 0.032383 | 0.0054324 | -0.043113 | -0.0061182 | 0.011386 | -0.004578 | -0.004578 | 0.009155 | 0.073242 | 0.10529 | 0.027466 | -0.10529 | -0.041199 | 0.022888 | -0.1236 | 0.022888 | 0.041199 | 0.036621 | -0.013733 | 120.0211 | 119.8883 | -0.21057 | 119.989 | 120.0668 | 0.17853 | -0.32044 | 120.0302 | 119.9799 | -0.29297 | 119.9524 | 119.87 | -0.10986 | -0.27466 | 120.0989 | 119.989 | 120.0027 | -0.42114 | 120.0165 | 120.0348 | 120.0165 | -0.32959
4353.4219 | 120.3918 | -119.9753 | 0.37079 | 0.0054168 | -0.0037726 | 0.068945 | 0.026724 | -0.064196 | -0.017758 | 0.00014745 | 0.0073242 | 0.034092 | 0.007355 | -0.042045 | -0.0052636 | 0.011173 | 0.064087 | 0.054932 | 0.064087 | 0.09613 | 0.11444 | 0.059509 | -0.073242 | 0 | 0.045776 | -0.09613 | 0 | 0.045776 | 0.054932 | -0.022888 | 120.0348 | 119.902 | -0.25635 | 120.0302 | 120.0714 | 0.16937 | -0.3067 | 120.0302 | 119.9524 | -0.37079 | 119.9753 | 119.8792 | -0.073242 | -0.32501 | 120.0897 | 120.0394 | 120.0394 | -0.44403 | 119.9753 | 120.0211 | 120.0211 | -0.39368
4355.1562 | 120.4834 | -120.0897 | 0.25177 | 0.0054168 | 0.0071222 | 0.070226 | 0.026938 | -0.070818 | -0.026517 | -0.0011344 | 0.0073242 | 0.027683 | 0.0058596 | -0.043113 | -0.0097498 | 0.011813 | 0.07782 | 0.11444 | 0.13275 | 0.13275 | 0.050354 | 0.082397 | -0.041199 | 0.041199 | 0.10529 | -0.018311 | -0.013733 | -0.004578 | 0.082397 | 0.018311 | 120.1721 | 120.0485 | -0.20142 | 120.2042 | 120.2225 | 0.17395 | -0.17395 | 120.1721 | 120.108 | -0.2655 | 120.1309 | 120.0714 | -0.036622 | -0.25635 | 120.1401 | 120.1675 | 120.2225 | -0.29297 | 120.076 | 120.0851 | 120.195 | -0.23346
4356.9531 | 120.5521 | -120.0623 | 0.26093 | 0.013046 | 0.0045588 | 0.071081 | 0.02886 | -0.069323 | -0.030576 | -0.0015616 | 0.014954 | 0.027256 | 0.0047916 | -0.042472 | -0.0097498 | 0.012454 | 0.10529 | 0.15106 | 0.17395 | 0.13733 | 0.064087 | 0.082397 | -0.054932 | 0.068665 | 0.16479 | 0.050354 | -0.032043 | -0.009155 | 0.091553 | 0.013733 | 120.1447 | 120.0073 | -0.19684 | 120.2133 | 120.1996 | 0.19226 | -0.15564 | 120.1538 | 120.076 | -0.29297 | 120.1309 | 120.1126 | 0.036621 | -0.27008 | 120.1263 | 120.1675 | 120.2362 | -0.31586 | 120.0302 | 120.0531 | 120.2271 | -0.24719
4358.75 | 120.2682 | -119.783 | 0.24261 | 0.020676 | -0.0024908 | 0.067022 | 0.025229 | -0.068682 | -0.022031 | 0.0010018 | 0.014954 | 0.033879 | 0.0071414 | -0.040763 | -0.0048364 | 0.0098907 | 0.059509 | 0.050354 | 0.064087 | 0.10071 | 0.091553 | 0.045776 | -0.073242 | 0.036621 | 0.091553 | -0.07782 | -0.009155 | 0.027466 | 0.064087 | -0.018311 | 119.8288 | 119.7098 | -0.15106 | 119.8334 | 119.8837 | 0.17395 | -0.18311 | 119.8471 | 119.7647 | -0.25177 | 119.8196 | 119.7052 | -0.059509 | -0.21515 | 119.8746 | 119.8425 | 119.8471 | -0.31586 | 119.7739 | 119.8105 | 119.8746 | -0.26093
4360.5781 | 120.4376 | -120.0668 | 0.27466 | 0.013046 | -0.00099541 | 0.072576 | 0.029288 | -0.069964 | -0.027158 | -0.0028434 | 0.014954 | 0.029606 | 0.005646 | -0.044395 | -0.0078272 | 0.0116 | 0.073242 | 0.10986 | 0.11444 | 0.13275 | 0.07782 | 0.064087 | -0.07782 | 0.018311 | 0.086975 | -0.041199 | -0.004578 | 0.018311 | 0.059509 | -0.022888 | 120.1309 | 119.989 | -0.19684 | 120.1767 | 120.1996 | 0.21057 | -0.20142 | 120.1263 | 120.0439 | -0.27924 | 120.0851 | 120.0256 | -0.018311 | -0.25635 | 120.1447 | 120.1401 | 120.1813 | -0.35248 | 120.0623 | 120.0851 | 120.1538 | -0.29755
4362.375 | 120.575 | -120.1218 | 0.23804 | 0.0054168 | 0.004345 | 0.074072 | 0.02587 | -0.0674 | -0.028653 | -0.00092075 | -0.0079343 | 0.027683 | 0.0052188 | -0.042045 | -0.0071862 | 0.012241 | 0.050354 | 0.068665 | 0.09613 | 0.10071 | 0.064087 | 0.054932 | -0.059509 | 0.009155 | 0.07782 | -0.022888 | -0.018311 | 0 | 0.082397 | 0 | 120.1767 | 120.0623 | -0.17395 | 120.1904 | 120.2225 | 0.16022 | -0.18768 | 120.2042 | 120.1218 | -0.25635 | 120.1309 | 120.0989 | -0.022888 | -0.23804 | 120.1859 | 120.1721 | 120.2179 | -0.29755 | 120.1035 | 120.1218 | 120.1996 | -0.23804
4364.1719 | 120.4926 | -120.2042 | 0.27466 | 0.013046 | -0.0022772 | 0.070226 | 0.024161 | -0.069109 | -0.019254 | -0.0019888 | 0.0073242 | 0.033879 | 0.0067142 | -0.041404 | -0.0020594 | 0.0116 | 0.041199 | -0.022888 | 0.018311 | 0.073242 | 0.10529 | 0.036621 | -0.07782 | -0.018311 | -0.013733 | -0.14191 | 0 | 0.036621 | 0.073242 | -0.032043 | 120.2408 | 120.1263 | -0.16937 | 120.1813 | 120.2774 | 0.15106 | -0.23346 | 120.2774 | 120.1721 | -0.27466 | 120.1859 | 120.0623 | -0.10986 | -0.23804 | 120.3094 | 120.2454 | 120.2225 | -0.35248 | 120.2042 | 120.2408 | 120.1904 | -0.3067
4365.9219 | 120.5658 | -120.1904 | 0.24261 | 0.0054168 | -0.002918 | 0.064886 | 0.028647 | -0.069537 | -0.020749 | -0.0028434 | 0.0073242 | 0.033238 | 0.0084232 | -0.041832 | -0.0061182 | 0.010532 | 0.059509 | 0.032043 | 0.059509 | 0.10986 | 0.086975 | 0.018311 | -0.086975 | 0.009155 | 0.086975 | -0.082397 | 0.018311 | 0.036621 | 0.045776 | -0.009155 | 120.2087 | 120.1035 | -0.15564 | 120.2225 | 120.3003 | 0.19684 | -0.18311 | 120.2362 | 120.1813 | -0.2243 | 120.1996 | 120.108 | -0.073242 | -0.20599 | 120.2774 | 120.2499 | 120.2499 | -0.32959 | 120.2087 | 120.2271 | 120.2774 | -0.25177
4367.7188 | 120.5933 | -120.2179 | 0.27008 | -0.0022127 | -0.0022772 | 0.069585 | 0.029501 | -0.068255 | -0.020963 | 0.0016428 | 0.022583 | 0.033024 | 0.0084232 | -0.043327 | -0.0048364 | 0.012027 | 0.027466 | 0.018311 | 0.027466 | 0.10529 | 0.082397 | 0.027466 | -0.086975 | 0.018311 | 0.064087 | -0.073242 | 0.013733 | 0.018311 | 0.045776 | -0.018311 | 120.2454 | 120.1309 | -0.18768 | 120.2362 | 120.3232 | 0.19226 | -0.24262 | 120.2637 | 120.1996 | -0.25635 | 120.2362 | 120.1447 | -0.054931 | -0.25177 | 120.3003 | 120.2454 | 120.2454 | -0.35706 | 120.2316 | 120.2362 | 120.282 | -0.28839
4369.5156 | 120.5429 | -120.2591 | 0.28839 | 0.0054168 | -0.0031318 | 0.07044 | 0.029074 | -0.0674 | -0.027585 | -0.0011344 | 0.014954 | 0.029606 | 0.0060732 | -0.041618 | -0.0093226 | 0.013309 | 0.013733 | 0.045776 | 0.050354 | 0.091553 | 0.086975 | 0.032043 | -0.07782 | -0.041199 | 0.064087 | -0.091553 | 0.022888 | 0.032043 | 0.050354 | -0.032043 | 120.2911 | 120.1813 | -0.20142 | 120.3049 | 120.3506 | 0.16937 | -0.27466 | 120.3094 | 120.2271 | -0.2655 | 120.2179 | 120.1675 | -0.05951 | -0.25635 | 120.3461 | 120.2728 | 120.3094 | -0.36621 | 120.282 | 120.2911 | 120.3232 | -0.32043
4371.2656 | 120.5704 | -120.3094 | 0.25635 | 0.0054168 | 0.0019952 | 0.07044 | 0.026083 | -0.068896 | -0.02139 | 0.0018564 | 0.022583 | 0.032597 | 0.0054324 | -0.042259 | -0.0044092 | 0.012241 | 0 | -0.050354 | -0.013733 | 0.064087 | 0.10986 | 0.045776 | -0.086975 | -0.041199 | -0.022888 | -0.14648 | 0.027466 | 0.045776 | 0.059509 | -0.032043 | 120.3552 | 120.2225 | -0.14649 | 120.2591 | 120.3735 | 0.15106 | -0.25635 | 120.369 | 120.2774 | -0.22888 | 120.2682 | 120.163 | -0.11444 | -0.21057 | 120.4193 | 120.3094 | 120.2957 | -0.34332 | 120.3369 | 120.3552 | 120.2866 | -0.28839
4373.0625 | 120.6436 | -120.2866 | 0.26093 | 0.0054168 | -0.0041998 | 0.067876 | 0.02886 | -0.067828 | -0.026944 | -0.00027975 | 0.014954 | 0.030888 | 0.0065006 | -0.0429 | -0.006759 | 0.010959 | -0.004578 | 0 | 0.022888 | 0.091553 | 0.10071 | 0.045776 | -0.09613 | 0 | 0.059509 | -0.07782 | 0.022888 | 0.032043 | 0.045776 | -0.004578 | 120.3323 | 120.1904 | -0.16022 | 120.2866 | 120.3781 | 0.18768 | -0.2655 | 120.3323 | 120.282 | -0.23804 | 120.2866 | 120.2087 | -0.073242 | -0.22888 | 120.3873 | 120.282 | 120.3094 | -0.35706 | 120.3094 | 120.3186 | 120.3461 | -0.2655
4374.7969 | 120.607 | -120.3232 | 0.2655 | 0.0054168 | 0.0026362 | 0.073217 | 0.027579 | -0.06975 | -0.029721 | -0.0028434 | 0.0073242 | 0.029179 | 0.0041506 | -0.042686 | -0.0080408 | 0.012668 | 0.045776 | 0.09613 | 0.10986 | 0.13275 | 0.059509 | 0.064087 | -0.07782 | -0.004578 | 0.09613 | -0.041199 | 0.004578 | 0.027466 | 0.073242 | -0.018311 | 120.3873 | 120.2454 | -0.20599 | 120.4193 | 120.4559 | 0.21057 | -0.21973 | 120.3964 | 120.3049 | -0.26092 | 120.3186 | 120.282 | -0.022888 | -0.23804 | 120.3827 | 120.369 | 120.433 | -0.34332 | 120.3278 | 120.3506 | 120.4193 | -0.28381
4376.5938 | 120.7489 | -120.3369 | 0.25177 | 0.020676 | 0.006054 | 0.073644 | 0.026724 | -0.066119 | -0.029294 | -0.003057 | 0.014954 | 0.027043 | 0.0041506 | -0.04589 | -0.0080408 | 0.012454 | 0.022888 | 0.059509 | 0.10071 | 0.1236 | 0.086975 | 0.07782 | -0.041199 | 0.013733 | 0.091553 | -0.022888 | -0.013733 | 0 | 0.086975 | 0.004578 | 120.4147 | 120.2957 | -0.16479 | 120.3964 | 120.4605 | 0.16479 | -0.22888 | 120.4239 | 120.3415 | -0.2655 | 120.3506 | 120.314 | -0.027466 | -0.25177 | 120.4239 | 120.3598 | 120.4376 | -0.29297 | 120.3232 | 120.3369 | 120.4285 | -0.24719
4378.3906 | 120.6573 | -120.3781 | 0.27008 | 0.013046 | 0.00049979 | 0.072149 | 0.026511 | -0.067828 | -0.027799 | -0.0017752 | 0.014954 | 0.032383 | 0.0050052 | -0.044395 | -0.006759 | 0.010318 | 0.054932 | 0.07782 | 0.10071 | 0.10986 | 0.091553 | 0.041199 | -0.07782 | -0.022888 | 0.064087 | -0.054932 | 0.009155 | 0.036621 | 0.064087 | -0.009155 | 120.4193 | 120.3003 | -0.17853 | 120.4559 | 120.488 | 0.18768 | -0.21515 | 120.4422 | 120.369 | -0.26093 | 120.3552 | 120.3232 | -0.045777 | -0.23346 | 120.4697 | 120.433 | 120.4788 | -0.3479 | 120.3873 | 120.4147 | 120.4422 | -0.27924
4380.2188 | 120.7169 | -120.3644 | 0.23804 | 0.0054168 | 0.0011408 | 0.068304 | 0.024802 | -0.068255 | -0.020963 | -0.0022024 | 0.0073242 | 0.031101 | 0.0067142 | -0.041404 | -0.0046228 | 0.010318 | 0.018311 | -0.041199 | -0.009155 | 0.064087 | 0.10986 | 0.045776 | -0.086975 | -0.041199 | -0.022888 | -0.11902 | 0.004578 | 0.050354 | 0.050354 | -0.022888 | 120.4102 | 120.2774 | -0.12817 | 120.3232 | 120.4285 | 0.15106 | -0.21973 | 120.4147 | 120.3415 | -0.23346 | 120.3232 | 120.2454 | -0.096131 | -0.18768 | 120.4742 | 120.3827 | 120.3552 | -0.32501 | 120.369 | 120.4147 | 120.3415 | -0.26093

## Thermal Data
Fire Time | B Position - Tray - Middle
-0.9646 | 6.7734
0.0354 | 6.7705
1.0354 | 6.776
2.0354 | 6.7807
3.0354 | 6.7901
4.0354 | 6.7955
5.0354 | 6.7789
6.0354 | 6.7853
7.0354 | 6.8108
8.0354 | 7.0075
9.0354 | 7.329
10.0354 | 8.0886
11.0354 | 10.1484
12.0354 | 12.2551
13.0354 | 14.4135
14.0354 | 17.2405
15.0354 | 20.7646
16.0354 | 25.5875
17.0354 | 28.5832
18.0354 | 33.6705
19.0354 | 37.3049
20.0354 | 40.5163
21.0354 | 42.7969
22.0354 | 45.1197
23.0354 | 49.0544
24.0354 | 52.941
25.0354 | 55.7159
26.0354 | 57.9326
27.0354 | 59.8348
28.0354 | 62.5858
29.0354 | 65.0332
30.0354 | 67.9443
31.0354 | 70.2127
32.0354 | 71.5543
33.0354 | 74.4736
34.0354 | 77.1899
35.0354 | 79.9674
36.0354 | 81.8209
37.0354 | 84.2056
38.0354 | 86.6215
39.0354 | 88.6851
40.0354 | 91.1794
41.0354 | 91.9549
42.0354 | 92.7585
43.0354 | 92.7789
44.0354 | 93.3356
45.0354 | 94.6667
46.0354 | 96.4374
47.0354 | 97.7139
48.0354 | 98.6874
49.0354 | 100.2736
50.0354 | 103.2493
51.0354 | 104.918
52.0354 | 106.5822
53.0354 | 109.4081
54.0354 | 111.3457
55.0354 | 112.6403
56.0354 | 114.3119
57.0354 | 115.9559
58.0354 | 117.2895
59.0354 | 117.9481
60.0354 | 118.0875
61.0354 | 119.4958
62.0354 | 120.2122
63.0354 | 121.2887
64.0354 | 121.3671
65.0354 | 122.2595
66.0354 | 121.5709
67.0354 | 122.3243
68.0354 | 121.5343
69.0354 | 122.3719
70.0354 | 122.4425
71.0354 | 122.8717
72.0354 | 124.2104
73.0354 | 125.0872
74.0354 | 125.4959
75.0354 | 125.2955
76.0354 | 125.2278
77.0354 | 126.025
78.0354 | 126.4602
79.0354 | 126.5932
80.0354 | 126.8967
81.0354 | 127.1173
82.0354 | 127.4914
83.0354 | 127.7114
84.0354 | 128.5854
85.0354 | 128.3453
86.0354 | 127.7018
87.0354 | 127.6376
88.0354 | 127.5525
89.0354 | 128.2823
90.0354 | 128.1746
91.0354 | 128.4146
92.0354 | 128.133
93.0354 | 128.4526
94.0354 | 128.6716
95.0354 | 129.4647
96.0354 | 130.8156
97.0354 | 131.7787
98.0354 | 131.9391
99.0354 | 132.3881
100.0354 | 132.5319
101.0354 | 132.5168
102.0354 | 132.9534
103.0354 | 133.5924
104.0354 | 133.0255
105.0354 | 134.6953
106.0354 | 135.3356
107.0354 | 136.0847
108.0354 | 136.9107
109.0354 | 137.3476
110.0354 | 137.0366
111.0354 | 136.957
112.0354 | 137.0814
113.0354 | 137.5971
114.0354 | 138.1856
115.0354 | 138.953
116.0354 | 139.1293
117.0354 | 140.2405
118.0354 | 141.5838
119.0354 | 141.6456
120.0354 | 142.512
121.0354 | 143.4841
122.0354 | 144.35
123.0354 | 146.0058
124.0354 | 148.3684
125.0354 | 150.3369
126.0354 | 151.1865
127.0354 | 150.9043
128.0354 | 151.1593
129.0354 | 151.3744
130.0354 | 152.3614
131.0354 | 152.8367
132.0354 | 154.0151
133.0354 | 153.9634
134.0354 | 154.3374
135.0354 | 154.2308
136.0354 | 153.3901
137.0354 | 151.8027
138.0354 | 151.5362
139.0354 | 151.9509
140.0354 | 152.1692
141.0354 | 152.5187
142.0354 | 153.2248
143.0354 | 152.7185
144.0354 | 152.562
145.0354 | 153.0074
146.0354 | 153.1102
147.0354 | 153.5617
148.0354 | 153.611
149.0354 | 152.8661
150.0354 | 152.4414
151.0354 | 152.1324
152.0354 | 152.2222
153.0354 | 152.0067
154.0354 | 151.0222
155.0354 | 150.9752
156.0354 | 151.1529
157.0354 | 150.0594
158.0354 | 149.8785
159.0354 | 149.6418
160.0354 | 150.0195
161.0354 | 150.3218
162.0354 | 149.9934
163.0354 | 150.9
164.0354 | 150.8482
165.0354 | 150.9028
166.0354 | 150.4698
167.0354 | 150.2661
168.0354 | 150.0426
169.0354 | 150.0853
170.0354 | 149.8879
171.0354 | 150.2713
172.0354 | 150.5817
173.0354 | 150.7014
174.0354 | 150.7183
175.0354 | 151.4262
176.0354 | 151.6138
177.0354 | 151.4855
178.0354 | 151.4828
179.0354 | 151.7318
180.0354 | 151.6482
181.0354 | 151.6935
182.0354 | 151.9266
183.0354 | 152.0191
184.0354 | 153.0268
185.0354 | 153.4589
186.0354 | 153.7193
187.0354 | 153.8216
188.0354 | 153.3694
189.0354 | 153.1687
190.0354 | 153.5319
191.0354 | 153.1306
192.0354 | 153.4193
193.0354 | 153.184
194.0354 | 152.5264
195.0354 | 152.1526
196.0354 | 152.0147
197.0354 | 152.2934
198.0354 | 152.8083
199.0354 | 153.4277
200.0354 | 154.1579
201.0354 | 154.3447
202.0354 | 154.252
203.0354 | 154.0478
204.0354 | 154.2875
205.0354 | 154.1721
206.0354 | 153.7408
207.0354 | 154.0455
208.0354 | 153.5062
209.0354 | 153.5481
210.0354 | 153.4909
211.0354 | 153.1359
212.0354 | 153.7068
213.0354 | 154.6536
214.0354 | 154.2519
215.0354 | 154.1807
216.0354 | 154.4373
217.0354 | 154.9797
218.0354 | 155.3171
219.0354 | 155.659
220.0354 | 156.2857
221.0354 | 156.3783
222.0354 | 156.494
223.0354 | 156.6034
224.0354 | 156.3334
225.0354 | 156.6599
226.0354 | 155.779
227.0354 | 156.4672
228.0354 | 157.0612
229.0354 | 157.8798
230.0354 | 158.9599
231.0354 | 160.0426
232.0354 | 161.0248
233.0354 | 161.0669
234.0354 | 161.2443
235.0354 | 161.2909
236.0354 | 161.9515
237.0354 | 162.6952
238.0354 | 162.4755
239.0354 | 161.8343
240.0354 | 161.3829
241.0354 | 161.3284
242.0354 | 160.5583
243.0354 | 160.8916
244.0354 | 161.3026
245.0354 | 161.6973
246.0354 | 160.835
247.0354 | 161.2685
248.0354 | 161.274
249.0354 | 161.3113
250.0354 | 160.9992
251.0354 | 160.6418
252.0354 | 161.1683
253.0354 | 162.2511
254.0354 | 161.9453
255.0354 | 161.5526
256.0354 | 162.2816
257.0354 | 161.8594
258.0354 | 162.1903
259.0354 | 163.1696
260.0354 | 163.6561
261.0354 | 163.931
262.0354 | 163.4857
263.0354 | 162.9622
264.0354 | 162.8852
265.0354 | 163.6962
266.0354 | 163.9416
267.0354 | 165.213
268.0354 | 165.7094
269.0354 | 165.8157
270.0354 | 165.1819
271.0354 | 164.7118
272.0354 | 163.6395
273.0354 | 163.231
274.0354 | 162.6337
275.0354 | 161.8747
276.0354 | 161.7796
277.0354 | 162.1743
278.0354 | 162.1832
279.0354 | 162.6598
280.0354 | 163.5608
281.0354 | 163.9445
282.0354 | 164.6087
283.0354 | 165.3659
284.0354 | 165.7386
285.0354 | 165.4072
286.0354 | 165.3974
287.0354 | 164.7653
288.0354 | 164.4419
289.0354 | 164.0444
290.0354 | 163.7367
291.0354 | 163.5148
292.0354 | 163.0906
293.0354 | 162.9834
294.0354 | 162.6166
295.0354 | 163.1079
296.0354 | 163.1939
297.0354 | 163.7854
298.0354 | 163.6857
299.0354 | 163.5489
300.0354 | 165.1537
301.0354 | 164.8443
302.0354 | 164.1712
303.0354 | 164.0366
304.0354 | 163.4614
305.0354 | 163.1898
306.0354 | 161.9596
307.0354 | 161.7533
308.0354 | 162.2915
309.0354 | 162.2514
310.0354 | 162.5583
311.0354 | 161.9857
312.0354 | 161.8034
313.0354 | 161.4339
314.0354 | 161.791
315.0354 | 161.4425
316.0354 | 160.5418
317.0354 | 160.9222
318.0354 | 161.2181
319.0354 | 160.7368
320.0354 | 160.2419
321.0354 | 159.9219
322.0354 | 160.583
323.0354 | 162.2261
324.0354 | 162.1182
325.0354 | 161.9982
326.0354 | 161.6481
327.0354 | 161.0854
328.0354 | 160.7741
329.0354 | 161.6382
330.0354 | 161.3127
331.0354 | 160.3414
332.0354 | 160.4868
333.0354 | 160.7786
334.0354 | 161.063
335.0354 | 161.4582
336.0354 | 161.358
337.0354 | 162.828
338.0354 | 163.2891
339.0354 | 163.2927
340.0354 | 163.9498
341.0354 | 165.0037
342.0354 | 166.4089
343.0354 | 166.6322
344.0354 | 167.3607
345.0354 | 167.5365
346.0354 | 167.4095
347.0354 | 167.3812
348.0354 | 167.5948
349.0354 | 168.8603
350.0354 | 168.567
351.0354 | 169.4047
352.0354 | 169.5432
353.0354 | 170.0032
354.0354 | 170.3666
355.0354 | 170.1477
356.0354 | 170.3028
357.0354 | 170.9442
358.0354 | 171.4609
359.0354 | 171.03
360.0354 | 171.1147
361.0354 | 172.4126
362.0354 | 173.2409
363.0354 | 172.9656
364.0354 | 172.842
365.0354 | 172.3939
366.0354 | 171.533
367.0354 | 170.976
368.0354 | 170.5377
369.0354 | 170.5443
370.0354 | 171.0267
371.0354 | 170.0701
372.0354 | 170.6563
373.0354 | 170.7946
374.0354 | 171.1113
375.0354 | 171.3283
376.0354 | 171.4194
377.0354 | 172.0323
378.0354 | 171.6878
379.0354 | 170.8784
380.0354 | 171.2309
381.0354 | 171.8445
382.0354 | 171.5724
383.0354 | 171.2277
384.0354 | 171.7024
385.0354 | 171.884
386.0354 | 171.9935
387.0354 | 171.6531
388.0354 | 171.5612
389.0354 | 171.7219
390.0354 | 172.9672
391.0354 | 173.6877
392.0354 | 173.2359
393.0354 | 173.7573
394.0354 | 174.1508
395.0354 | 174.6686
396.0354 | 174.9128
397.0354 | 175.1023
398.0354 | 174.7624
399.0354 | 174.8931
400.0354 | 174.2757
401.0354 | 174.2308
402.0354 | 174.1923
403.0354 | 174.4081
404.0354 | 176.0759
405.0354 | 176.9808
406.0354 | 176.9583
407.0354 | 177.4277
408.0354 | 178.981
409.0354 | 180.0458
410.0354 | 181.3653
411.0354 | 182.6318
412.0354 | 184.3705
413.0354 | 186.4154
414.0354 | 187.288
415.0354 | 187.4305
416.0354 | 186.7826
417.0354 | 186.3483
418.0354 | 187.0469
419.0354 | 188.8088
420.0354 | 188.6295
421.0354 | 188.5745
422.0354 | 189.0522
423.0354 | 190.1621
424.0354 | 190.6301
425.0198 | 192.5026
426.0198 | 192.5028
427.0198 | 191.832
428.0354 | 190.2756
429.0354 | 190.1353
430.0354 | 190.2125
431.0354 | 191.2396
432.0354 | 190.4125
433.0354 | 190.5849
434.0354 | 190.4612
435.0354 | 189.9172
436.0354 | 190.2627
437.0354 | 190.4145
438.0198 | 190.0839
439.0198 | 188.8795
440.0198 | 188.6283
441.0198 | 190.1727
442.0198 | 190.4914
443.0198 | 190.434
444.0198 | 192.3063
445.0354 | 192.465
446.0354 | 192.4823
447.0354 | 193.1246
448.0354 | 193.0504
449.0354 | 194.8236
450.0354 | 195.3131
451.0354 | 195.7922
452.0354 | 195.7662
453.0354 | 196.9441
454.0354 | 196.3983
455.0354 | 196.0571
456.0354 | 195.7288
457.0354 | 196.8234
458.0354 | 197.6903
459.0354 | 198.2422
460.0354 | 198.7606
461.0354 | 200.1286
462.0354 | 199.9143
463.0354 | 199.2009
464.0354 | 199.1986
465.0354 | 198.9078
466.0354 | 199.2444
467.0354 | 200.5707
468.0354 | 202.6241
469.0354 | 203.1115
470.0354 | 204.1934
471.0354 | 204.133
472.0354 | 205.7772
473.0354 | 206.6887
474.0354 | 206.3332
475.0354 | 205.6165
476.0354 | 204.8586
477.0354 | 205.3155
478.0354 | 206.4954
479.0354 | 206.8172
480.0354 | 206.3422
481.0354 | 207.4385
482.0354 | 208.5329
483.0354 | 209.157
484.0354 | 209.1383
485.0354 | 208.5112
486.0354 | 208.1614
487.0354 | 208.6387
488.0354 | 208.8681
489.0354 | 208.8874
490.0354 | 209.6433
491.0354 | 210.4253
492.0354 | 210.7734
493.0354 | 210.4957
494.0354 | 209.712
495.0354 | 208.3017
496.0354 | 207.2702
497.0354 | 207.713
498.0354 | 208.705
499.0354 | 209.9807
500.0354 | 211.0738
501.0354 | 211.4521
502.0354 | 211.2869
503.0354 | 210.8154
504.0354 | 209.4449
505.051 | 208.9491
506.0354 | 209.4191
507.0354 | 208.8032
508.0354 | 209.2872
509.0354 | 209.1921
510.0354 | 209.758
511.0354 | 209.8528
512.0354 | 209.7225
513.0354 | 209.3693
514.0354 | 210.076
515.0354 | 210.3783
516.0354 | 210.6543
517.0354 | 210.5575
518.0354 | 211.3294
519.0354 | 211.627
520.0354 | 211.8779
521.0354 | 212.0737
522.0354 | 212.2964
523.0354 | 213.0544
524.0354 | 213.0184
525.0354 | 212.815
526.0354 | 212.8582
527.0354 | 211.9679
528.0354 | 212.5784
529.0354 | 213.4856
530.0354 | 214.9243
531.0354 | 215.2087
532.0354 | 215.0722
533.0354 | 215.8693
534.0354 | 216.3594
535.0354 | 216.0456
536.0354 | 216.3445
537.0354 | 216.0914
538.0354 | 216.1435
539.0354 | 215.5366
540.0354 | 215.1116
541.0354 | 216.4838
542.0354 | 217.1762
543.0354 | 218.4378
544.0354 | 220.405
545.0354 | 222.2885
546.0354 | 222.615
547.0354 | 223.1298
548.0354 | 224.0366
549.0354 | 224.8285
550.0354 | 225.4479
551.0354 | 226.306
552.0354 | 226.5632
553.0354 | 228.3425
554.0354 | 227.2118
555.0354 | 227.6532
556.0354 | 227.8386
557.0354 | 229.0538
558.0354 | 229.6576
559.0354 | 231.1494
560.0354 | 232.1802
561.0354 | 231.3186
562.0354 | 231.4624
563.0354 | 230.8659
564.0354 | 231.8818
565.0354 | 232.1591
566.0354 | 231.9109
567.0354 | 232.9946
568.0354 | 233.3411
569.0354 | 234.3261
570.0354 | 234.232
571.0354 | 236.1783
572.0354 | 236.1899
573.0354 | 236.8614
574.0354 | 237.4323
575.0354 | 236.4346
576.0354 | 236.3481
577.0354 | 235.5378
578.0354 | 233.672
579.0354 | 233.2683
580.0354 | 232.345
581.0354 | 231.7759
582.0354 | 231.1471
583.0354 | 231.9122
584.0354 | 232.4407
585.0354 | 232.0669
586.0354 | 232.4234
587.0354 | 231.7591
588.0354 | 230.5649
589.0354 | 231.0609
590.0354 | 231.0505
591.0354 | 231.0103
592.0354 | 230.9192
593.0354 | 230.3796
594.0354 | 229.7916
595.0354 | 228.833
596.0354 | 228.3028
597.0354 | 229.1082
598.0354 | 230.9119
599.0354 | 231.988
600.0354 | 231.6831
601.0354 | 231.3881
602.0354 | 230.7183
603.0354 | 230.063
604.0354 | 229.7174
605.0354 | 229.2426
606.0354 | 230.1169
607.0354 | 229.7743
608.0354 | 229.1069
609.0354 | 229.1846
610.0354 | 228.6602
611.0354 | 227.8598
612.0354 | 227.0862
613.0354 | 227.0232
614.0354 | 226.8711
615.0354 | 227.2725
616.0354 | 226.8166
617.0354 | 226.7648
618.0354 | 226.1442
619.0354 | 225.4384
620.0354 | 225.9218
621.0354 | 227.3939
622.0354 | 227.6463
623.0354 | 227.1742
624.0354 | 226.7131
625.0354 | 226.3333
626.0354 | 226.1118
627.0354 | 225.9115
628.0354 | 226.2294
629.0354 | 227.0622
630.0354 | 227.2938
631.0354 | 228.5507
632.0354 | 229.1406
633.0354 | 229.3945
634.0354 | 229.1606
635.0354 | 228.5392
636.0354 | 227.7054
637.0354 | 226.8884
638.0354 | 225.7631
639.0354 | 225.7903
640.0354 | 225.45
641.0354 | 226.0425
642.0354 | 226.8804
643.0354 | 228.7014
644.0354 | 229.5195
645.0354 | 228.6553
646.0354 | 228.7995
647.0354 | 228.6736
648.0354 | 227.8304
649.0354 | 228.1163
650.0354 | 228.2787
651.0354 | 229.217
652.0354 | 229.5605
653.0354 | 229.7016
654.0354 | 229.2264
655.0354 | 228.6096
656.0354 | 228.2991
657.0354 | 227.9988
658.0354 | 227.8236
659.0354 | 227.6549
660.0354 | 227.829
661.0354 | 227.9088
662.0354 | 227.4762
663.0354 | 227.101
664.0354 | 226.9646
665.0354 | 227.5112
666.0354 | 227.503
667.0354 | 227.6291
668.0354 | 227.1399
669.0354 | 227.3174
670.0354 | 226.7074
671.0354 | 226.5461
672.0354 | 226.966
673.0354 | 227.4326
674.0354 | 227.0898
675.0354 | 226.5013
676.0354 | 225.945
677.0354 | 226.685
678.0354 | 226.6267
679.0354 | 227.1964
680.0354 | 227.3948
681.0354 | 228.252
682.0354 | 227.9675
683.0354 | 228.0468
684.0354 | 227.5367
685.0354 | 227.2532
686.0354 | 226.5402
687.0354 | 226.3668
688.0354 | 225.6587
689.0354 | 224.7247
690.0354 | 224.1035
691.0354 | 224.3516
692.0354 | 224.4793
693.0354 | 224.372
694.0354 | 224.0675
695.0354 | 224.0668
696.0354 | 224.718
697.0354 | 224.5769
698.0354 | 225.654
699.0354 | 226.2918
700.0354 | 227.2124
701.0354 | 226.989
702.0354 | 227.64
703.0354 | 228.1746
704.0354 | 228.5362
705.0354 | 227.7386
706.0354 | 227.775
707.0354 | 227.8712
708.0354 | 227.9833
709.0354 | 228.8309
710.0354 | 230.8978
711.0354 | 231.8747
712.0354 | 231.9487
713.0354 | 231.3777
714.0354 | 230.6617
715.0354 | 229.9224
716.0354 | 230.1993
717.0354 | 229.534
718.0354 | 229.4023
719.0354 | 229.4839
720.0354 | 228.7442
721.0354 | 228.9782
722.0354 | 229.8243
723.0354 | 229.7176
724.0354 | 229.6578
725.0354 | 229.2883
726.0354 | 229.91
727.0354 | 230.6347
728.0354 | 230.2875
729.0354 | 229.5869
730.0354 | 228.6767
731.0354 | 228.1633
732.0354 | 228.0704
733.0354 | 228.6566
734.0354 | 229.5924
735.0354 | 229.3634
736.0354 | 230.2574
737.0354 | 230.0539
738.0354 | 229.417
739.0354 | 229.0876
740.0354 | 228.6898
741.0354 | 228.8029
742.0354 | 229.0521
743.0354 | 228.8806
744.0354 | 229.2576
745.0354 | 228.9834
746.0354 | 229.1774
747.0354 | 228.8846
748.0354 | 228.5371
749.0354 | 229.5978
750.0354 | 229.9081
751.0354 | 230.6474
752.0354 | 231.4226
753.0354 | 231.7873
754.0354 | 231.4289
755.0354 | 230.7786
756.0354 | 230.6391
757.0354 | 230.8058
758.0354 | 231.1549
759.0354 | 230.699
760.0354 | 231.9251
761.0354 | 232.8705
762.0354 | 233.9807
763.0354 | 233.9389
764.0354 | 233.7325
765.0354 | 234.1442
766.0354 | 235.2568
767.0354 | 234.4056
768.0354 | 233.7767
769.0354 | 234.7096
770.0354 | 235.6459
771.0354 | 236.7132
772.0354 | 236.8611
773.0354 | 237.1136
774.0354 | 236.512
775.0354 | 236.8767
776.0354 | 237.141
777.0354 | 237.7489
778.0354 | 236.6549
779.0354 | 236.0163
780.0354 | 236.1095
781.0354 | 235.9795
782.0354 | 236.3001
783.0354 | 235.8629
784.0354 | 235.1612
785.0354 | 234.9081
786.0354 | 235.0439
787.0354 | 234.4862
788.0354 | 233.8588
789.0354 | 233.6904
790.0354 | 232.9875
791.0354 | 232.1475
792.0354 | 232.231
793.0354 | 232.2672
794.0354 | 232.0287
795.0354 | 232.7946
796.0354 | 233.3249
797.0354 | 233.063
798.0354 | 232.5481
799.0354 | 232.8105
800.0354 | 231.946
801.0354 | 232.4476
802.0354 | 232.5833
803.0354 | 232.6519
804.0354 | 232.0739
805.0354 | 231.9582
806.0354 | 231.7015
807.0354 | 231.5266
808.0354 | 232.0212
809.0354 | 232.1485
810.0354 | 233.0715
811.0354 | 232.9751
812.0354 | 232.8225
813.0354 | 233.6884
814.0354 | 233.3761
815.0354 | 233.2866
816.0354 | 232.6143
817.0354 | 232.0377
818.0354 | 232.5023
819.0354 | 232.4517
820.0354 | 232.9
821.0354 | 232.5274
822.0354 | 231.7181
823.0354 | 231.5262
824.0354 | 230.8251
825.0354 | 230.1825
826.0354 | 230.4181
827.0354 | 229.9634
828.0354 | 229.554
829.0354 | 229.7224
830.0354 | 229.3486
831.0354 | 230.029
832.0354 | 230.0927
833.0354 | 230.5766
834.0354 | 230.5344
835.0354 | 229.545
836.0354 | 229.2214
837.0354 | 228.6152
838.0354 | 227.9488
839.0354 | 227.1009
840.0354 | 226.5242
841.0354 | 226.792
842.0354 | 227.0464
843.0354 | 227.0506
844.0354 | 227.6841
845.0354 | 227.8052
846.0354 | 228.4327
847.0354 | 227.647
848.0354 | 227.7451
849.0354 | 227.4485
850.0354 | 227.4944
851.0354 | 227.4007
852.0354 | 228.002
853.0354 | 228.8054
854.0354 | 228.7494
855.0354 | 229.8033
856.0354 | 229.7385
857.0354 | 229.9467
858.0354 | 229.179
859.0354 | 229.372
860.0354 | 229.5035
861.0354 | 229.618
862.0354 | 229.1627
863.0354 | 229.0377
864.0354 | 230.1634
865.0354 | 230.9577
866.0354 | 232.6569
867.0354 | 234.4841
868.0354 | 235.119
869.0354 | 234.4473
870.0354 | 235.2255
871.0354 | 235.2322
872.0354 | 235.8099
873.0354 | 235.4645
874.0354 | 234.5672
875.0354 | 234.2933
876.0354 | 233.2584
877.0354 | 232.8306
878.0354 | 232.9589
879.0354 | 233.2727
880.0354 | 233.1813
881.0354 | 232.7862
882.0354 | 232.325
883.0354 | 231.3097
884.0354 | 230.3641
885.0354 | 230.6788
886.0354 | 231.522
887.0354 | 230.9835
888.0354 | 231.6909
889.0354 | 231.8795
890.0354 | 231.35
891.0354 | 233.0933
892.0354 | 233.3151
893.0354 | 234.1159
894.0354 | 234.7887
895.0354 | 234.7403
896.0354 | 234.2856
897.0354 | 233.731
898.0354 | 233.2134
899.0354 | 232.496
900.0354 | 232.7943
901.0354 | 232.8174
902.0354 | 233.1723
903.0354 | 233.6358
904.0354 | 233.5828
905.0354 | 234.1852
906.0354 | 234.1168
907.0354 | 235.2572
908.0354 | 236.3069
909.0354 | 237.3585
910.0354 | 237.6502
911.0354 | 238.4601
912.0354 | 239.0367
913.0354 | 240.8355
914.0354 | 241.7611
915.0354 | 243.7575
916.0354 | 244.5565
917.0354 | 244.9157
918.0354 | 245.1893
919.0354 | 245.8427
920.0354 | 246.404
921.0354 | 247.8398
922.0354 | 248.8904
923.0354 | 249.3147
924.0354 | 249.3032
925.0354 | 249.6635
926.0354 | 249.9136
927.0354 | 250.1458
928.0354 | 250.9243
929.0354 | 251.9862
930.0354 | 252.5183
931.0354 | 253.6714
932.0354 | 255.979
933.0354 | 257.8807
934.0354 | 258.3686
935.0354 | 258.7496
936.0354 | 258.9687
937.0354 | 258.8932
938.0354 | 258.6659
939.0354 | 258.6083
940.0354 | 259.7186
941.0354 | 258.9288
942.0354 | 259.1075
943.0354 | 258.9441
944.0354 | 259.1082
945.0354 | 259.9287
946.0354 | 259.5242
947.0354 | 259.6207
948.0354 | 259.0227
949.0354 | 258.6315
950.0354 | 259.0074
951.0354 | 259.1921
952.0354 | 259.2878
953.0354 | 260.0362
954.0354 | 259.3273
955.0354 | 258.7732
956.0354 | 257.959
957.0354 | 257.4665
958.0354 | 256.304
959.0354 | 255.8988
960.0354 | 255.6535
961.0354 | 255.3282
962.0354 | 255.633
963.0354 | 255.1838
964.0354 | 255.4829
965.0354 | 255.0136
966.0354 | 254.4342
967.0354 | 253.899
968.0354 | 253.0327
969.0354 | 252.8355
970.0198 | 253.6401
971.0354 | 253.9587
972.0354 | 255.4717
973.0354 | 255.9969
974.0354 | 255.7641
975.0354 | 256.564
976.0354 | 256.5932
977.0354 | 257.6423
978.0354 | 258.1241
979.0354 | 258.3375
980.0354 | 260.8306
981.0354 | 261.0303
982.0354 | 262.2071
983.0354 | 262.8548
984.0354 | 263.8683
985.0354 | 265.0351
986.0354 | 267.1515
987.0354 | 267.8732
988.0354 | 269.3731
989.0354 | 270.5044
990.0354 | 270.8802
991.0354 | 270.7627
992.0354 | 270.5904
993.0354 | 271.0694
994.0354 | 271.2486
995.0354 | 271.4033
996.0354 | 271.3421
997.0354 | 271.5484
998.0354 | 271.9174
999.0354 | 271.9361
1000.0354 | 272.1829
1001.0354 | 271.4892
1002.0354 | 271.1785
1003.0354 | 271.4581
1004.0354 | 271.6793
1005.0354 | 271.8557
1006.0354 | 271.6237
1007.0354 | 271.8117
1008.0354 | 271.9645
1009.0354 | 271.9108
1010.0354 | 271.1202
1011.0354 | 269.7598
1012.0198 | 268.9043
1013.0354 | 268.338
1014.0354 | 268.2609
1015.0354 | 267.8561
1016.0354 | 268.0773
1017.0354 | 269.3714
1018.0354 | 268.493
1019.0354 | 267.7899
1020.0354 | 266.8005
1021.0354 | 266.3375
1022.0354 | 265.8735
1023.0354 | 265.1706
1024.0354 | 265.6762
1025.0354 | 265.914
1026.0354 | 265.6787
1027.0354 | 267.0352
1028.0354 | 266.7693
1029.0354 | 266.5825
1030.0354 | 266.4704
1031.0354 | 265.4926
1032.0354 | 264.5028
1033.0354 | 263.6354
1034.0354 | 264.5874
1035.0354 | 265.9277
1036.0354 | 265.791
1037.0354 | 267.2888
1038.0354 | 268.8178
1039.0354 | 269.9418
1040.0354 | 272.1105
1041.0354 | 272.9936
1042.0354 | 273.892
1043.0354 | 274.776
1044.0354 | 275.3747
1045.0354 | 276.187
1046.0354 | 275.9846
1047.0354 | 276.0817
1048.0354 | 275.5277
1049.0354 | 275.1671
1050.0354 | 275.3707
1051.0354 | 275.8482
1052.0354 | 275.2423
1053.0354 | 274.4095
1054.0354 | 273.965
1055.0354 | 274.2468
1056.0354 | 274.9839
1057.0354 | 276.427
1058.0354 | 277.1587
1059.0354 | 277.5881
1060.0354 | 278.2046
1061.0354 | 278.2393
1062.0354 | 278.0274
1063.0354 | 277.7734
1064.0354 | 277.7394
1065.0354 | 276.5987
1066.0354 | 276.244
1067.0354 | 276.0267
1068.0354 | 276.3478
1069.0354 | 275.3421
1070.0354 | 274.5466
1071.0354 | 275.1075
1072.0354 | 274.6491
1073.0354 | 274.9196
1074.0354 | 275.7353
1075.0354 | 276.1445
1076.0354 | 277.7638
1077.0354 | 278.8983
1078.0354 | 279.6844
1079.0354 | 280.0626
1080.0354 | 281.6389
1081.0354 | 282.3085
1082.0354 | 283.1495
1083.0354 | 283.7591
1084.0354 | 283.7613
1085.0354 | 284.7551
1086.0354 | 285.787
1087.0354 | 286.2981
1088.0354 | 286.3191
1089.0354 | 285.4992
1090.0354 | 285.5385
1091.0354 | 285.113
1092.0354 | 284.6603
1093.0354 | 284.3751
1094.0354 | 283.8849
1095.0354 | 283.6837
1096.0354 | 283.0513
1097.0354 | 282.6478
1098.0354 | 283.2195
1099.0354 | 284.1792
1100.0354 | 284.6799
1101.0354 | 285.2543
1102.0354 | 285.7976
1103.0354 | 286.4774
1104.0354 | 285.9845
1105.0354 | 286.4226
1106.0354 | 286.8773
1107.0354 | 286.7468
1108.0354 | 286.3218
1109.0354 | 287.043
1110.0354 | 286.4516
1111.0354 | 286.9267
1112.0354 | 286.7852
1113.0354 | 287.5395
1114.0354 | 287.2512
1115.0354 | 286.1582
1116.0354 | 285.796
1117.0354 | 286.3382
1118.0354 | 286.4279
1119.0354 | 287.1908
1120.0354 | 288.729
1121.0354 | 289.5229
1122.0354 | 290.1273
1123.0354 | 290.2585
1124.0354 | 291.2084
1125.0354 | 293.6256
1126.0354 | 293.801
1127.0354 | 294.1952
1128.0354 | 295.1005
1129.0354 | 295.751
1130.0354 | 297.822
1131.0354 | 298.333
1132.0354 | 299.2493
1133.0354 | 299.7508
1134.0354 | 301.1479
1135.0354 | 302.5275
1136.0354 | 304.3343
1137.0354 | 305.0303
1138.0354 | 305.5768
1139.0354 | 306.2272
1140.0354 | 306.6229
1141.0354 | 308.4812
1142.0354 | 310.4795
1143.0354 | 309.9965
1144.0354 | 309.9546
1145.0354 | 310.1375
1146.0354 | 311.1302
1147.0354 | 312.3144
1148.0354 | 313.0715
1149.0354 | 314.0507
1150.0354 | 313.8331
1151.0354 | 315.1518
1152.0354 | 318.2174
1153.0354 | 318.7009
1154.0354 | 319.9352
1155.0354 | 320.4197
1156.0354 | 322.9047
1157.0354 | 324.4185
1158.0354 | 324.6065
1159.0354 | 326.5265
1160.0354 | 327.5611
1161.0354 | 328.1842
1162.0354 | 328.7622
1163.0354 | 329.0487
1164.0354 | 330.2371
1165.0354 | 332.7173
1166.0354 | 334.3005
1167.0354 | 336.892
1168.0354 | 337.9434
1169.0354 | 339.3154
1170.0354 | 337.95
1171.0354 | 339.4427
1172.0354 | 340.3246
1173.0354 | 342.856
1174.0354 | 344.4537
1175.0354 | 344.0868
1176.0354 | 347.6413
1177.0354 | 351.521
1178.0354 | 352.9315
1179.0354 | 356.1511
1180.0354 | 355.6246
1181.0354 | 354.9861
1182.0354 | 356.4809
1183.0354 | 358.5831
1184.0354 | 358.8817
1185.0354 | 360.9875
1186.0354 | 363.7831
1187.0354 | 364.1722
1188.0354 | 364.5854
1189.0354 | 365.9599
1190.0354 | 367.8753
1191.0354 | 367.6983
1192.0354 | 367.5689
1193.0354 | 367.8182
1194.0354 | 369.1198
1195.0354 | 368.5927
1196.0354 | 367.8324
1197.0354 | 369.8386
1198.0354 | 374.0605
1199.0354 | 375.3456
1200.0354 | 381.5474
1201.0354 | 381.4859
1202.0354 | 383.2972
1203.0354 | 389.547
1204.0354 | 394.7414
1205.0354 | 397.4974
1206.0354 | 399.7701
1207.0354 | 399.2316
1208.0354 | 398.0465
1209.0354 | 402.2565
1210.0354 | 402.5024
1211.0354 | 403.8406
1212.0354 | 409.0516
1213.0354 | 411.3797
1214.0354 | 411.1627
1215.0354 | 410.4419
1216.0354 | 408.962
1217.0354 | 408.4371
1218.0354 | 416.1294
1219.0354 | 420.3391
1220.0354 | 420.3184
1221.0354 | 420.8104
1222.0354 | 425.0342
1223.0354 | 426.4506
1224.0354 | 436.3999
1225.0354 | 438.4571
1226.0354 | 445.3664
1227.0354 | 456.6029
1228.0354 | 453.4369
1229.0354 | 453.8502
1230.0354 | 459.2371
1231.0354 | 454.7899
1232.0354 | 452.4741
1233.0354 | 449.7746
1234.0354 | 467.2531
1235.0354 | 466.3253
1236.0354 | 470.6484
1237.0354 | 469.8704
1238.0354 | 466.4278
1239.0354 | 476.1458
1240.0354 | 476.5595
1241.0354 | 493.5531
1242.0354 | 488.4283
1243.0354 | 507.0421
1244.0354 | 520.208
1245.0354 | 528.8278
1246.0354 | 546.8916
1247.0354 | 547.7395
1248.0354 | 562.9662
1249.0354 | 579.6504
1250.0354 | 590.4047
1251.0354 | 583.8155
1252.0354 | 595.1695
1253.0354 | 607.2474
1254.0354 | 626.9186
1255.0354 | 655.229
1256.0354 | 670.6556
1257.0354 | 655.0271
1258.0354 | 671.9063
1259.0354 | 671.1804
1260.0354 | 682.2522
1261.0354 | 661.6716
1262.0354 | 645.4172
1263.0354 | 653.1224
1264.0354 | 646.4928
1265.0354 | 630.3244
1266.0354 | 638.9981
1267.0354 | 661.161
1268.0354 | 666.7388
1269.0354 | 645.7498
1270.0354 | 621.2515
1271.0354 | 600.8712
1272.0354 | 584.8668
1273.0354 | 590.2059
1274.0354 | 588.0475
1275.0354 | 577.1731
1276.0354 | 587.172
1277.0354 | 583.3872
1278.0354 | 591.5625
1279.0354 | 602.8408
1280.0354 | 615.4367
1281.0354 | 616.2204
1282.0354 | 607.8349
1283.0354 | 594.6106
1284.0354 | 585.1203
1285.0354 | 573.3291
1286.0354 | 577.2638
1287.0354 | 591.0049
1288.0354 | 587.3963
1289.0354 | 585.2694
1290.0354 | 585.7946
1291.0354 | 588.7874
1292.0354 | 565.472
1293.0354 | 568.305
1294.0354 | 562.8496
1295.0354 | 561.4482
1296.0354 | 555.4908
1297.0354 | 557.169
1298.0354 | 560.4267
1299.0354 | 554.7241
1300.0354 | 568.0711
1301.0354 | 563.1643
1302.0354 | 549.3554
1303.0354 | 543.0416
1304.0354 | 544.3634
1305.0354 | 555.794
1306.0354 | 564.7078
1307.0354 | 563.5538
1308.0354 | 555.2557
1309.0354 | 559.7249
1310.0354 | 553.0335
1311.0354 | 567.1381
1312.0354 | 567.2123
1313.0354 | 571.4797
1314.0354 | 580.5136
1315.0354 | 573.7562
1316.0354 | 573.1893
1317.0354 | 559.6864
1318.0354 | 558.6818
1319.0354 | 545.4648
1320.0354 | 539.8342
1321.0354 | 542.1666
1322.0354 | 537.9279
1323.0354 | 522.3136
1324.0354 | 526.4043
1325.0354 | 523.1283
1326.0354 | 515.4442
1327.0354 | 500.0019
1328.0354 | 500.4293
1329.0354 | 499.5664
1330.0354 | 501.6465
1331.0354 | 506.1624
1332.0354 | 524.4279
1333.0354 | 523.7422
1334.0354 | 535.2337
1335.0354 | 527.6838
1336.0354 | 518.1228
1337.0354 | 506.6756
1338.0354 | 496.3442
1339.0354 | 486.5273
1340.0354 | 479.5807
1341.0354 | 471.7253
1342.0354 | 466.2055
1343.0354 | 460.3517
1344.0354 | 454.3027
1345.0354 | 449.2142
1346.0354 | 443.1783
1347.0354 | 437.5518
1348.0354 | 435.6789
1349.0354 | 433.5947
1350.0354 | 430.513
1351.0354 | 428.9863
1352.0354 | 427.3486
1353.0354 | 425.3062
1354.0354 | 424.99
1355.0354 | 422.6755
1356.0354 | 423.0778
1357.0354 | 422.1416
1358.0354 | 418.7464
1359.0354 | 416.4974
1360.0354 | 415.9364
1361.0354 | 414.4069
1362.0354 | 412.6805
1363.0354 | 412.5764
1364.0354 | 410.6193
1365.0354 | 409.2949
1366.0354 | 409.1927
1367.0354 | 411.0512
1368.0354 | 410.5372
1369.0354 | 408.4566
1370.0354 | 408.5382
1371.0354 | 408.3801
1372.0354 | 407.923
1373.0354 | 408.5945
1374.0354 | 407.949
1375.0354 | 407.8898
1376.0354 | 407.921
1377.0354 | 409.7658
1378.0354 | 409.354
1379.0354 | 409.9774
1380.0354 | 409.6059
1381.0354 | 409.8716
1382.0354 | 411.0158
1383.0354 | 410.5835
1384.0354 | 408.8513
1385.0354 | 407.1125
1386.0354 | 408.0817
1387.0354 | 407.613
1388.0354 | 406.0105
1389.0354 | 405.0735
1390.0354 | 403.6366
1391.0354 | 403.032
1392.0354 | 402.4951
1393.0354 | 401.3247
1394.0354 | 400.9546
1395.0354 | 400.6581
1396.0354 | 400.6611
1397.0354 | 402.1657
1398.0354 | 402.4356
1399.0354 | 402.0306
1400.0354 | 401.3024
1401.0354 | 400.5706
1402.0354 | 399.8509
1403.0354 | 399.0896
1404.0354 | 399.8473
1405.0354 | 399.8746
1406.0354 | 401.2313
1407.0354 | 400.1008
1408.0354 | 398.4377
1409.0354 | 396.5583
1410.0354 | 394.7779
1411.0354 | 392.7169
1412.0354 | 391.3811
1413.0354 | 391.3871
1414.0354 | 392.103
1415.0354 | 391.5907
1416.0354 | 392.8785
1417.0354 | 393.1844
1418.0354 | 391.9202
1419.0354 | 391.0634
1420.0354 | 391.7806
1421.0354 | 390.2009
1422.0354 | 389.4811
1423.0354 | 388.5619
1424.0354 | 386.4075
1425.0354 | 386.5998
1426.0354 | 385.3401
1427.0354 | 383.9741
1428.0354 | 383.4355
1429.0354 | 383.9195
1430.0354 | 383.715
1431.0354 | 383.5075
1432.0354 | 382.3027
1433.0354 | 381.2794
1434.0354 | 380.6047
1435.0354 | 378.5524
1436.0354 | 377.5039
1437.0354 | 375.69
1438.0354 | 374.4624
1439.0354 | 373.0009
1440.0354 | 372.0005
1441.0354 | 371.7759
1442.0354 | 371.7388
1443.0354 | 370.9894
1444.0354 | 370.153
1445.0354 | 369.9361
1446.0354 | 370.6974
1447.0354 | 370.6723
1448.0354 | 370.864
1449.0354 | 371.076
1450.0354 | 370.9972
1451.0354 | 369.9672
1452.0354 | 369.5838
1453.0354 | 368.0015
1454.0354 | 368.8973
1455.0354 | 369.9117
1456.0354 | 369.6211
1457.0354 | 369.4769
1458.0354 | 370.0927
1459.0354 | 371.0491
1460.0354 | 372.7943
1461.0354 | 374.3854
1462.0354 | 376.8034
1463.0354 | 377.7994
1464.0354 | 378.8736
1465.0354 | 379.8823
1466.0354 | 381.8255
1467.0354 | 382.2089
1468.0354 | 383.5947
1469.0354 | 384.9565
1470.0354 | 386.4791
1471.0354 | 387.9947
1472.0354 | 389.9227
1473.0354 | 391.2299
1474.0354 | 391.8825
1475.0354 | 393.1117
1476.0354 | 393.3076
1477.0354 | 393.9531
1478.0354 | 393.9628
1479.0354 | 393.4629
1480.0354 | 394.4165
1481.0354 | 393.6214
1482.0354 | 393.3937
1483.0354 | 394.4257
1484.0354 | 393.7265
1485.0354 | 395.2027
1486.0354 | 394.7548
1487.0354 | 395.1166
1488.0354 | 394.4813
1489.0354 | 391.819
1490.0354 | 391.6836
1491.0354 | 391.5484
1492.0354 | 390.6376
1493.0354 | 390.955
1494.0354 | 390.2928
1495.0354 | 389.6027
1496.0354 | 388.9301
1497.0354 | 387.9288
1498.0354 | 387.2836
1499.0354 | 387.2
1500.0354 | 385.5702
1501.0354 | 384.5318
1502.0354 | 383.6683
1503.0354 | 383.6646
1504.0354 | 382.8433
1505.0354 | 383.0877
1506.0354 | 383.6558
1507.0354 | 382.5615
1508.0354 | 381.9691
1509.0354 | 380.4341
1510.0354 | 380.9825
1511.0354 | 381.9714
1512.0354 | 382.7438
1513.0354 | 382.2524
1514.0354 | 382.5783
1515.0354 | 381.6843
1516.0354 | 381.0879
1517.0354 | 379.6383
1518.0354 | 378.4768
1519.0354 | 377.0906
1520.0354 | 375.9179
1521.0354 | 375.0542
1522.0354 | 373.6183
1523.0354 | 372.336
1524.0354 | 372.4005
1525.0354 | 371.164
1526.0354 | 372.0187
1527.0354 | 373.0883
1528.0354 | 373.5749
1529.0354 | 374.1707
1530.0354 | 375.2474
1531.0354 | 375.8032
1532.0354 | 374.7558
1533.0354 | 374.7255
1534.0354 | 374.172
1535.0354 | 373.2078
1536.0354 | 373.4041
1537.0354 | 373.8553
1538.0354 | 377.5455
1539.0354 | 379.4241
1540.0354 | 380.8416
1541.0354 | 382.1608
1542.0354 | 383.7761
1543.0354 | 384.2037
1544.0354 | 384.8542
1545.0354 | 386.5968
1546.0354 | 388.3804
1547.0354 | 389.6549
1548.0354 | 391.0409
1549.0354 | 392.5264
1550.0354 | 393.0268
1551.0354 | 393.62
1552.0354 | 394.1712
1553.0354 | 393.5944
1554.0354 | 392.4967
1555.0354 | 391.8402
1556.0354 | 392.5915
1557.0354 | 394.5451
1558.0354 | 396.5852
1559.0354 | 399.7556
1560.0354 | 398.6323
1561.0354 | 400.2832
1562.0354 | 401.3384
1563.0354 | 399.9776
1564.0354 | 402.0579
1565.0354 | 402.8942
1566.0354 | 402.9271
1567.0354 | 404.2074
1568.0354 | 408.1116
1569.0354 | 413.2463
1570.0354 | 430.5992
1571.0354 | 429.234
1572.0354 | 427.5391
1573.0354 | 431.0582
1574.0354 | 434.3293
1575.0354 | 432.6716
1576.0354 | 430.9108
1577.0354 | 431.1111
1578.0354 | 429.0068
1579.0354 | 428.8853
1580.0354 | 428.0983
1581.0354 | 429.4499
1582.0354 | 428.6227
1583.0354 | 427.2262
1584.0354 | 426.2354
1585.0354 | 425.8728
1586.0354 | 424.1334
1587.0354 | 422.051
1588.0354 | 425.1421
1589.0354 | 425.8129
1590.0354 | 430.8704
1591.0354 | 437.3549
1592.0354 | 440.3099
1593.0354 | 443.8078
1594.0354 | 445.3626
1595.0354 | 446.249
1596.0354 | 445.0682
1597.0354 | 451.9275
1598.0354 | 454.6982
1599.0354 | 455.6984
1600.0354 | 459.2832
1601.0354 | 461.9859
1602.0354 | 466.5995
1603.0354 | 469.8208
1604.0354 | 468.599
1605.0354 | 467.2814
1606.0354 | 465.1639
1607.0354 | 463.0874
1608.0354 | 468.7999
1609.0354 | 467.9719
1610.0354 | 480.0058
1611.0354 | 480.4838
1612.0354 | 489.0835
1613.0354 | 502.371
1614.0354 | 508.7026
1615.0354 | 508.0934
1616.0354 | 508.0675
1617.0354 | 510.9483
1618.0354 | 522.0472
1619.0354 | 518.9699
1620.0354 | 515.1837
1621.0354 | 518.8771
1622.0354 | 512.0546
1623.0354 | 510.7344
1624.0354 | 524.9142
1625.0354 | 525.724
1626.0354 | 531.0708
1627.0354 | 526.0601
1628.0354 | 526.997
1629.0354 | 530.304
1630.0354 | 527.4886
1631.0354 | 520.2234
1632.0354 | 521.3597
1633.0354 | 516.7683
1634.0354 | 529.7409
1635.0354 | 539.9238
1636.0354 | 553.0269
1637.0354 | 560.5819
1638.0354 | 572.2828
1639.0354 | 563.6667
1640.0354 | 567.7036
1641.0354 | 565.3226
1642.0354 | 558.3574
1643.0354 | 549.206
1644.0354 | 552.682
1645.0354 | 549.0742
1646.0354 | 539.6568
1647.0354 | 534.9927
1648.0354 | 529.9089
1649.0354 | 545.1674
1650.0354 | 537.0067
1651.0354 | 547.9874
1652.0354 | 563.064
1653.0354 | 574.6912
1654.0354 | 565.0313
1655.0354 | 557.3572
1656.0354 | 548.1546
1657.0354 | 538.8977
1658.0354 | 534.41
1659.0354 | 536.4825
1660.0354 | 548.8364
1661.0354 | 540.7094
1662.0354 | 550.9336
1663.0354 | 566.6676
1664.0354 | 551.6858
1665.0354 | 543.9062
1666.0354 | 536.7948
1667.0354 | 524.6441
1668.0354 | 516.2489
1669.0354 | 508.1324
1670.0354 | 501.2426
1671.0354 | 516.949
1672.0354 | 503.8883
1673.0354 | 494.2412
1674.0354 | 491.351
1675.0354 | 485.1318
1676.0354 | 479.5551
1677.0354 | 477.7569
1678.0354 | 471.2333
1679.0354 | 467.6854
1680.0354 | 463.6564
1681.0354 | 464.8862
1682.0354 | 461.8957
1683.0354 | 461.4322
1684.0354 | 467.1442
1685.0354 | 469.6454
1686.0354 | 466.339
1687.0354 | 460.8478
1688.0354 | 456.8434
1689.0354 | 453.9541
1690.0354 | 450.57
1691.0354 | 449.3403
1692.0354 | 445.5716
1693.0354 | 441.5004
1694.0354 | 441.8191
1695.0354 | 439.6239
1696.0354 | 437.4924
1697.0354 | 435.2441
1698.0354 | 433.4981
1699.0354 | 431.7926
1700.0354 | 431.3392
1701.0354 | 430.2625
1702.0354 | 429.1493
1703.0354 | 429.7317
1704.0354 | 429.169
1705.0354 | 428.2503
1706.0354 | 427.2559
1707.0354 | 426.3021
1708.0354 | 425.8869
1709.0354 | 426.4847
1710.0354 | 425.6222
1711.0354 | 426.7717
1712.0354 | 428.5864
1713.0354 | 428.084
1714.0354 | 428.4258
1715.0354 | 430.4723
1716.0354 | 433.2402
1717.0354 | 433.4728
1718.0354 | 431.0378
1719.0354 | 431.282
1720.0354 | 434.2779
1721.0354 | 436.3991
1722.0354 | 436.4326
1723.0354 | 435.6274
1724.0354 | 438.9846
1725.0354 | 441.9178
1726.0354 | 440.791
1727.0354 | 440.0795
1728.0354 | 439.979
1729.0354 | 439.254
1730.0354 | 441.5676
1731.0354 | 441.6273
1732.0354 | 442.6043
1733.0354 | 448.0883
1734.0354 | 449.6653
1735.0354 | 454.3409
1736.0354 | 458.4557
1737.0354 | 461.894
1738.0354 | 461.9279
1739.0354 | 482.1864
1740.0354 | 484.511
1741.0354 | 484.1324
1742.0354 | 487.7948
1743.0354 | 493.8125
1744.0354 | 490.806
1745.0354 | 490.433
1746.0354 | 488.2533
1747.0354 | 483.9546
1748.0354 | 481.7021
1749.0354 | 478.7751
1750.0354 | 478.8038
1751.0354 | 478.283
1752.0354 | 476.1076
1753.0354 | 475.1711
1754.0354 | 479.9208
1755.0354 | 485.0756
1756.0354 | 491.1818
1757.0354 | 490.0043
1758.0354 | 486.5561
1759.0354 | 485.4135
1760.0354 | 484.7779
1761.0354 | 482.1438
1762.0354 | 480.7353
1763.0354 | 478.6558
1764.0354 | 477.9692
1765.0354 | 477.7513
1766.0354 | 478.0433
1767.0354 | 475.7091
1768.0354 | 472.1607
1769.0354 | 472.7962
1770.0354 | 473.799
1771.0354 | 475.3933
1772.0354 | 474.9033
1773.0354 | 473.5248
1774.0354 | 473.9558
1775.0354 | 472.1028
1776.0354 | 475.23
1777.0354 | 476.6213
1778.0354 | 486.1237
1779.0354 | 484.9967
1780.0354 | 483.8824
1781.0354 | 484.0463
1782.0354 | 484.7073
1783.0354 | 485.0044
1784.0354 | 486.6838
1785.0354 | 487.8845
1786.0354 | 490.737
1787.0354 | 493.1776
1788.0354 | 503.8034
1789.0354 | 506.9906
1790.0354 | 507.6785
1791.0354 | 506.3531
1792.0354 | 506.5495
1793.0354 | 510.5271
1794.0354 | 510.991
1795.0354 | 508.3141
1796.0354 | 503.7828
1797.0354 | 500.8893
1798.0354 | 499.8666
1799.0354 | 497.8249
1800.0354 | 495.3641
1801.0354 | 506.7067
1802.0354 | 506.5876
1803.0354 | 506.4661
1804.0354 | 504.3068
1805.0354 | 508.1026
1806.0354 | 507.1704
1807.0354 | 507.2531
1808.0354 | 506.6023
1809.0354 | 508.7172
1810.0354 | 507.9027
1811.0354 | 507.9209
1812.0354 | 507.9729
1813.0354 | 506.8464
1814.0354 | 503.7484
1815.0354 | 506.8148
1816.0354 | 510.4162
1817.0354 | 508.8133
1818.0354 | 509.1458
1819.0354 | 510.9411
1820.0354 | 508.7202
1821.0354 | 507.6422
1822.0354 | 507.9628
1823.0354 | 504.1092
1824.0354 | 503.5594
1825.0354 | 502.0285
1826.0354 | 502.9699
1827.0354 | 515.5624
1828.0354 | 524.7264
1829.0354 | 523.8464
1830.0354 | 522.5674
1831.0354 | 521.096
1832.0354 | 516.2743
1833.0354 | 516.7508
1834.0354 | 513.7692
1835.0354 | 509.6216
1836.0354 | 505.5992
1837.0354 | 503.7699
1838.0354 | 502.2668
1839.0354 | 500.249
1840.0354 | 498.7788
1841.0354 | 495.4087
1842.0354 | 494.4152
1843.0354 | 492.8815
1844.0354 | 490.0485
1845.0354 | 485.1165
1846.0354 | 481.2686
1847.0354 | 478.4632
1848.0354 | 484.613
1849.0354 | 481.8455
1850.0354 | 480.428
1851.0354 | 478.2768
1852.0354 | 474.2036
1853.0354 | 472.3524
1854.0354 | 468.6766
1855.0354 | 464.1626
1856.0354 | 462.1738
1857.0354 | 462.9115
1858.0354 | 461.6982
1859.0354 | 459.8558
1860.0354 | 459.837
1861.0354 | 456.5626
1862.0198 | 454.7918
1863.0354 | 453.6163
1864.0354 | 452.728
1865.0354 | 453.0891
1866.0354 | 459.0142
1867.0354 | 456.8758
1868.0354 | 454.3261
1869.0354 | 451.6652
1870.0354 | 448.411
1871.0354 | 445.725
1872.0354 | 442.1604
1873.0354 | 439.7163
1874.0354 | 437.8778
1875.0354 | 435.9139
1876.0354 | 435.08
1877.0354 | 435.2387
1878.0354 | 433.5783
1879.0354 | 432.7375
1880.0354 | 432.4007
1881.0354 | 431.8082
1882.0354 | 431.006
1883.0354 | 431.3637
1884.0354 | 432.6093
1885.0354 | 433.8658
1886.0354 | 433.883
1887.0354 | 433.6208
1888.0354 | 435.4569
1889.0354 | 437.186
1890.0354 | 440.7082
1891.0354 | 442.3507
1892.0354 | 442.1772
1893.0354 | 442.3733
1894.0354 | 444.9985
1895.0354 | 454.7411
1896.0354 | 453.7607
1897.0354 | 452.5891
1898.0354 | 455.634
1899.0354 | 455.8821
1900.0354 | 455.9214
1901.0354 | 456.9007
1902.0354 | 457.9285
1903.0354 | 458.9053
1904.0354 | 457.9214
1905.0354 | 457.2454
1906.0354 | 457.8692
1907.0354 | 459.8713
1908.0354 | 460.6542
1909.0354 | 458.6748
1910.0354 | 458.9572
1911.0354 | 459.8156
1912.0354 | 459.9759
1913.0354 | 459.1024
1914.0354 | 456.6725
1915.0354 | 456.1584
1916.0354 | 455.3535
1917.0354 | 455.4625
1918.0354 | 455.2187
1919.0354 | 452.666
1920.0354 | 452.4229
1921.0354 | 452.0654
1922.0354 | 450.3329
1923.0354 | 449.5478
1924.0354 | 452.0393
1925.0354 | 451.2558
1926.0354 | 452.059
1927.0354 | 451.2164
1928.0354 | 450.4278
1929.0354 | 450.5842
1930.0354 | 451.1025
1931.0354 | 450.254
1932.0354 | 448.9455
1933.0354 | 445.7471
1934.0354 | 447.8018
1935.0354 | 448.6841
1936.0354 | 448.8423
1937.0354 | 446.0838
1938.0354 | 445.0818
1939.0354 | 443.2866
1940.0354 | 443.663
1941.0354 | 444.5277
1942.0354 | 444.6811
1943.0354 | 445.632
1944.0354 | 447.3316
1945.0354 | 447.3798
1946.0354 | 447.722
1947.0354 | 449.1827
1948.0354 | 448.8363
1949.0354 | 446.3661
1950.0354 | 445.7935
1951.0354 | 444.1052
1952.0354 | 443.5406
1953.0354 | 443.4679
1954.0354 | 442.0913
1955.0354 | 441.5542
1956.0354 | 442.0709
1957.0354 | 444.5508
1958.0354 | 446.3626
1959.0354 | 448.3259
1960.0354 | 448.626
1961.0354 | 449.0536
1962.0354 | 450.871
1963.0354 | 455.5325
1964.0354 | 459.2782
1965.0354 | 459.6051
1966.0354 | 460.2273
1967.0354 | 461.8997
1968.0354 | 463.2123
1969.0354 | 463.534
1970.0354 | 464.376
1971.0354 | 466.3997
1972.0354 | 468.1471
1973.0354 | 469.0142
1974.0354 | 469.097
1975.0354 | 469.0308
1976.0354 | 469.4127
1977.0354 | 468.4085
1978.0354 | 468.8048
1979.0354 | 468.8645
1980.0354 | 468.8687
1981.0354 | 468.8966
1982.0354 | 471.0004
1983.0354 | 472.5129
1984.0354 | 471.191
1985.0354 | 470.8694
1986.0354 | 475.3393
1987.0354 | 473.295
1988.0354 | 472.1599
1989.0354 | 471.2203
1990.0354 | 470.2112
1991.0354 | 471.3676
1992.0354 | 471.4106
1993.0354 | 469.8298
1994.0354 | 469.5905
1995.0354 | 470.5824
1996.0354 | 472.831
1997.0354 | 473.0165
1998.0354 | 474.0278
1999.0354 | 475.05
2000.0354 | 478.0295
2001.0354 | 480.6768
2002.0354 | 479.4528
2003.0354 | 477.0766
2004.0354 | 477.162
2005.0354 | 479.7509
2006.0354 | 479.2279
2007.0354 | 481.1771
2008.0354 | 480.334
2009.0354 | 479.1242
2010.0354 | 476.5843
2011.0354 | 474.8033
2012.0354 | 474.3858
2013.0354 | 472.6957
2014.0354 | 478.84
2015.0354 | 478.4886
2016.0354 | 476.8497
2017.0354 | 475.4456
2018.0354 | 475.2073
2019.0354 | 474.0024
2020.0354 | 472.1286
2021.0354 | 473.4722
2022.0354 | 472.383
2023.0354 | 473.4281
2024.0354 | 474.0529
2025.0354 | 473.307
2026.0354 | 472.9974
2027.0354 | 471.9885
2028.0354 | 475.5164
2029.0354 | 478.5425
2030.0354 | 477.7227
2031.0354 | 478.6981
2032.0354 | 481.5559
2033.0354 | 483.834
2034.0354 | 483.5858
2035.0354 | 482.2727
2036.0354 | 480.427
2037.0354 | 478.804
2038.0354 | 479.3587
2039.0354 | 480.3812
2040.0354 | 481.6727
2041.0354 | 481.8364
2042.0354 | 479.8846
2043.0354 | 479.4949
2044.0354 | 480.3126
2045.0354 | 480.1485
2046.0354 | 481.2665
2047.0354 | 483.8705
2048.0354 | 484.7038
2049.0354 | 484.1387
2050.0354 | 486.0696
2051.0354 | 484.9153
2052.0354 | 483.2111
2053.0354 | 483.5879
2054.0354 | 483.9048
2055.0354 | 483.9376
2056.0354 | 483.638
2057.0354 | 486.4744
2058.0354 | 490.7383
2059.0354 | 495.4019
2060.0354 | 499.9775
2061.0354 | 498.5322
2062.0354 | 498.737
2063.0354 | 500.2129
2064.0354 | 501.3727
2065.0354 | 501.7815
2066.0354 | 502.1836
2067.0354 | 500.7231
2068.0354 | 497.872
2069.0354 | 497.6566
2070.051 | 498.6442
2071.0354 | 502.8626
2072.0354 | 502.459
2073.0354 | 500.1368
2074.0354 | 499.9431
2075.0354 | 498.0716
2076.0354 | 495.6178
2077.0354 | 493.2495
2078.0354 | 494.4433
2079.0354 | 494.6961
2080.0354 | 492.2007
2081.0354 | 492.9075
2082.0354 | 494.3767
2083.0354 | 495.1115
2084.0354 | 496.4608
2085.0354 | 496.0495
2086.0354 | 498.4281
2087.0354 | 499.9116
2088.0354 | 499.9274
2089.0354 | 499.4585
2090.0354 | 504.9382
2091.0354 | 508.1757
2092.0354 | 510.2888
2093.0354 | 512.7059
2094.0354 | 514.5029
2095.0354 | 515.1866
2096.0354 | 517.0177
2097.0354 | 524.1644
2098.0354 | 528.6653
2099.0354 | 531.038
2100.0354 | 532.5537
2101.0354 | 534.2992
2102.0354 | 536.203
2103.0354 | 535.3784
2104.0354 | 534.7741
2105.0354 | 534.0478
2106.0354 | 533.1448
2107.0354 | 531.7458
2108.0354 | 530.476
2109.0354 | 530.3358
2110.0354 | 528.5913
2111.0354 | 527.8328
2112.0354 | 526.3489
2113.0354 | 523.1687
2114.0354 | 522.5726
2115.0354 | 521.0348
2116.0354 | 523.1297
2117.0354 | 525.5232
2118.0354 | 533.222
2119.0354 | 533.7119
2120.0354 | 532.884
2121.0354 | 531.778
2122.0354 | 531.7107
2123.0354 | 532.4752
2124.0354 | 533.268
2125.0354 | 534.9096
2126.0354 | 533.8278
2127.0354 | 533.3018
2128.0354 | 534.8954
2129.0354 | 538.7098
2130.0354 | 544.6008
2131.0354 | 549.6532
2132.0354 | 556.2825
2133.0354 | 560.9888
2134.0354 | 565.4343
2135.0354 | 567.7319
2136.0354 | 571.6383
2137.0354 | 575.042
2138.0354 | 577.6367
2139.0354 | 582.3138
2140.0354 | 583.9481
2141.0354 | 583.9949
2142.0354 | 583.7658
2143.0354 | 582.893
2144.0354 | 582.7206
2145.0354 | 583.6854
2146.0354 | 584.3039
2147.0354 | 585.4714
2148.0354 | 585.6788
2149.0354 | 587.5035
2150.0354 | 591.5095
2151.0354 | 595.2886
2152.0354 | 593.8622
2153.0354 | 591.782
2154.0354 | 590.3999
2155.0354 | 588.1605
2156.0354 | 584.4057
2157.0354 | 583.551
2158.0354 | 583.2679
2159.0354 | 583.7266
2160.0354 | 584.658
2161.0354 | 586.7661
2162.0354 | 586.7156
2163.0354 | 586.2131
2164.0354 | 586.3737
2165.0354 | 583.9519
2166.0354 | 580.4595
2167.0354 | 578.2328
2168.0354 | 574.5219
2169.0354 | 571.2933
2170.0354 | 569.1256
2171.0354 | 567.6187
2172.0354 | 564.4483
2173.0354 | 562.149
2174.0354 | 564.2399
2175.0354 | 564.7743
2176.0354 | 564.148
2177.0354 | 564.8445
2178.0354 | 568.7317
2179.0354 | 570.7464
2180.0354 | 572.9893
2181.0354 | 577.4531
2182.0354 | 576.8945
2183.0354 | 576.4068
2184.0354 | 576.1555
2185.0354 | 575.1983
2186.0354 | 574.4679
2187.0354 | 573.0222
2188.0354 | 571.5027
2189.0354 | 570.5434
2190.0354 | 571.4848
2191.0354 | 578.0239
2192.0354 | 581.5877
2193.0354 | 584.5464
2194.0354 | 585.6009
2195.0354 | 585.3618
2196.0354 | 585.8707
2197.0354 | 590.1367
2198.0354 | 592.3868
2199.0354 | 596.1312
2200.0354 | 599.4017
2201.0354 | 599.0544
2202.0354 | 595.596
2203.0354 | 599.6582
2204.0354 | 600.8374
2205.0354 | 605.5407
2206.0354 | 605.6581
2207.0354 | 604.2796
2208.0354 | 604.8987
2209.0354 | 610.1648
2210.0354 | 613.0192
2211.0354 | 617.4049
2212.0354 | 620.809
2213.0354 | 622.3942
2214.0354 | 626.6107
2215.0354 | 631.7534
2216.0354 | 631.7713
2217.0354 | 629.8576
2218.0354 | 630.3101
2219.0354 | 631.5241
2220.0354 | 629.4238
2221.0354 | 627.4223
2222.0354 | 629.9264
2223.0354 | 631.2819
2224.0354 | 634.2311
2225.0354 | 639.4639
2226.0354 | 638.1881
2227.0354 | 634.662
2228.0354 | 631.2999
2229.0354 | 626.7446
2230.0354 | 623.1904
2231.0354 | 625.188
2232.0354 | 625.2476
2233.0354 | 624.1019
2234.0354 | 625.8761
2235.0354 | 621.0525
2236.0354 | 616.8638
2237.0354 | 612.7246
2238.0354 | 609.1119
2239.0354 | 606.0094
2240.0354 | 602.3055
2241.0354 | 599.8725
2242.0354 | 599.5654
2243.0354 | 597.8043
2244.0354 | 595.1017
2245.0354 | 591.6509
2246.0354 | 591.2204
2247.0354 | 589.2658
2248.0354 | 587.0107
2249.0354 | 586.9886
2250.0354 | 589.8832
2251.0354 | 593.6411
2252.0354 | 594.5787
2253.0354 | 597.7028
2254.0354 | 598.6341
2255.0354 | 602.3415
2256.0354 | 606.5821
2257.0354 | 608.9403
2258.0354 | 609.8056
2259.0354 | 609.481
2260.0354 | 608.0129
2261.0354 | 604.9993
2262.0354 | 603.6296
2263.0354 | 602.625
2264.0354 | 602.0797
2265.0354 | 608.6503
2266.0354 | 610.3167
2267.0354 | 610.8504
2268.0354 | 608.3463
2269.0354 | 605.1538
2270.0354 | 602.5303
2271.0354 | 607.6157
2272.0354 | 608.6743
2273.0354 | 607.1529
2274.0354 | 609.8296
2275.0354 | 614.6053
2276.0354 | 615.7712
2277.0354 | 618.0489
2278.0354 | 621.9516
2279.0354 | 624.3524
2280.0354 | 627.318
2281.0354 | 630.7986
2282.0354 | 631.2228
2283.0354 | 632.1759
2284.0354 | 629.7609
2285.0354 | 628.3138
2286.0354 | 626.1914
2287.0354 | 627.7511
2288.0354 | 631.5361
2289.0354 | 633.3874
2290.0354 | 636.7596
2291.0354 | 635.9779
2292.0354 | 635.1936
2293.0354 | 636.8226
2294.0354 | 634.9591
2295.0354 | 636.4192
2296.0354 | 637.7457
2297.0354 | 639.9413
2298.0354 | 641.5965
2299.0354 | 642.5868
2300.0354 | 641.6631
2301.0354 | 644.4008
2302.0354 | 644.8113
2303.0354 | 641.9697
2304.0354 | 640.1592
2305.0354 | 637.7638
2306.0354 | 634.7094
2307.0354 | 631.7226
2308.0354 | 631.9775
2309.0354 | 632.6828
2310.0354 | 634.8584
2311.0354 | 634.6859
2312.0354 | 635.6488
2313.0354 | 632.7831
2314.0354 | 630.2735
2315.0354 | 631.5178
2316.0354 | 639.0289
2317.0354 | 642.0227
2318.0354 | 642.1309
2319.0354 | 642.03
2320.0354 | 643.8267
2321.0354 | 644.0701
2322.0354 | 642.8162
2323.0354 | 644.6899
2324.0354 | 646.5714
2325.0354 | 648.641
2326.0354 | 651.882
2327.0354 | 652.2933
2328.0354 | 650.0404
2329.0354 | 647.4918
2330.0354 | 644.4818
2331.0354 | 642.1798
2332.0354 | 643.4781
2333.0354 | 647.614
2334.0354 | 648.8851
2335.0354 | 651.5259
2336.0354 | 655.507
2337.0354 | 655.8532
2338.0354 | 652.995
2339.0354 | 651.7211
2340.0354 | 648.563
2341.0354 | 649.7226
2342.0354 | 651.5415
2343.0354 | 652.0708
2344.0354 | 649.6916
2345.0354 | 648.2999
2346.0354 | 647.4524
2347.0354 | 646.1725
2348.0354 | 647.5224
2349.0354 | 645.392
2350.0354 | 648.1084
2351.0354 | 649.4306
2352.0354 | 650.3782
2353.0354 | 648.9691
2354.0354 | 649.0365
2355.0354 | 647.5071
2356.0354 | 645.1492
2357.0354 | 648.0406
2358.0354 | 650.1862
2359.0354 | 653.6761
2360.0354 | 655.2441
2361.0354 | 657.6379
2362.0354 | 659.0324
2363.0354 | 662.9127
2364.0354 | 663.3421
2365.0354 | 658.5105
2366.0354 | 653.1527
2367.0354 | 651.7935
2368.0354 | 647.4538
2369.0354 | 643.4585
2370.0354 | 648.6372
2371.0354 | 650.9918
2372.0354 | 653.1388
2373.0354 | 655.882
2374.0354 | 655.7026
2375.0354 | 653.2815
2376.0823 | 651.7308
2377.0354 | 649.9451
2378.0354 | 651.899
2379.0354 | 651.4013
2380.0354 | 649.6073
2381.0354 | 653.3344
2382.0354 | 654.3856
2383.0354 | 658.5625
2384.0354 | 661.8545
2385.0354 | 660.662
2386.0354 | 658.1823
2387.0354 | 655.0807
2388.0354 | 653.1371
2389.0354 | 653.5756
2390.0354 | 653.4239
2391.0354 | 655.7806
2392.0354 | 656.7811
2393.0354 | 653.5018
2394.0354 | 655.5973
2395.0354 | 655.8984
2396.0354 | 652.2895
2397.0354 | 653.365
2398.0354 | 652.7761
2399.0354 | 649.8669
2400.0354 | 651.0568
2401.0354 | 650.913
2402.0354 | 652.6827
2403.0354 | 656.3029
2404.0354 | 657.7215
2405.0354 | 658.1234
2406.0354 | 661.085
2407.0354 | 664.966
2408.0354 | 663.0046
2409.0354 | 662.6503
2410.0354 | 663.0671
2411.0354 | 665.4346
2412.0354 | 666.0301
2413.0354 | 662.3983
2414.0354 | 658.233
2415.0354 | 656.0349
2416.0354 | 654.6812
2417.0354 | 656.2116
2418.0354 | 656.6222
2419.0354 | 658.3288
2420.0354 | 659.16
2421.0354 | 660.2248
2422.0354 | 659.9475
2423.0354 | 659.1328
2424.0354 | 659.1145
2425.0354 | 659.5382
2426.0354 | 659.6273
2427.0354 | 658.8128
2428.0354 | 658.2423
2429.0354 | 657.3069
2430.0354 | 657.2951
2431.0354 | 656.6432
2432.0354 | 655.3989
2433.0354 | 651.0955
2434.0354 | 647.1943
2435.0354 | 644.4029
2436.0354 | 642.7206
2437.0354 | 642.1813
2438.0354 | 644.9962
2439.0354 | 649.1354
2440.0354 | 648.0426
2441.0354 | 646.928
2442.0354 | 646.0899
2443.0354 | 647.2699
2444.0354 | 646.5117
2445.0354 | 646.8552
2446.0354 | 646.788
2447.0354 | 651.5158
2448.0354 | 652.8347
2449.0354 | 651.2516
2450.0354 | 653.1713
2451.0354 | 655.9453
2452.0354 | 656.7341
2453.0354 | 657.2989
2454.0354 | 658.9882
2455.0354 | 660.4132
2456.0354 | 662.6282
2457.0354 | 663.1236
2458.0354 | 661.6997
2459.0354 | 660.7831
2460.0354 | 661.6421
2461.0354 | 663.4967
2462.0354 | 664.2014
2463.0354 | 662.6599
2464.0354 | 662.6756
2465.0354 | 662.8182
2466.0354 | 664.5151
2467.0354 | 667.2822
2468.0354 | 667.5637
2469.0354 | 666.5975
2470.0354 | 665.9795
2471.0354 | 664.7805
2472.0354 | 664.4811
2473.0354 | 662.8814
2474.0354 | 661.0789
2475.0354 | 654.9185
2476.0354 | 653.8719
2477.0354 | 656.3745
2478.0354 | 656.7669
2479.0354 | 657.3811
2480.0354 | 655.6776
2481.0354 | 653.9831
2482.0354 | 655.5945
2483.0354 | 656.452
2484.0354 | 654.7111
2485.0354 | 655.3642
2486.0354 | 656.4176
2487.0354 | 657.0157
2488.0354 | 661.0095
2489.0354 | 662.609
2490.0354 | 661.7161
2491.0354 | 661.1571
2492.0354 | 661.046
2493.0354 | 659.3129
2494.0354 | 656.3971
2495.0354 | 660.4949
2496.0354 | 659.0358
2497.0354 | 655.1131
2498.0354 | 657.1308
2499.0354 | 656.4816
2500.0354 | 654.9871
2501.0354 | 654.6651
2502.0354 | 657.1319
2503.0354 | 658.8692
2504.0354 | 660.613
2505.0354 | 662.4993
2506.0354 | 662.6506
2507.0354 | 663.4708
2508.0354 | 659.7572
2509.0354 | 660.3851
2510.0354 | 659.9048
2511.0354 | 660.0848
2512.0354 | 657.2319
2513.0354 | 657.0916
2514.0354 | 654.8714
2515.0354 | 652.0513
2516.0354 | 653.9556
2517.0354 | 654.4065
2518.0354 | 652.987
2519.0354 | 652.9085
2520.0354 | 650.4259
2521.0354 | 646.6876
2522.0354 | 646.878
2523.0354 | 644.8243
2524.0354 | 643.095
2525.0354 | 643.7598
2526.0354 | 642.5967
2527.0354 | 642.4979
2528.0354 | 641.7119
2529.0354 | 640.4407
2530.0354 | 640.5413
2531.0354 | 641.0945
2532.0354 | 644.5118
2533.0354 | 646.8595
2534.0354 | 647.9297
2535.0354 | 647.3068
2536.0354 | 648.0175
2537.0354 | 647.2675
2538.0354 | 650.1289
2539.0354 | 649.1294
2540.0354 | 646.422
2541.0354 | 646.2377
2542.0354 | 648.1204
2543.0354 | 649.3919
2544.0354 | 648.3904
2545.0354 | 647.2221
2546.0354 | 644.0535
2547.0354 | 637.9657
2548.0354 | 638.1238
2549.0354 | 641.4122
2550.0354 | 642.863
2551.0354 | 643.6903
2552.0354 | 645.3171
2553.0354 | 648.7191
2554.0354 | 649.8613
2555.0354 | 652.4271
2556.0354 | 651.5305
2557.0354 | 652.094
2558.0354 | 651.2222
2559.0354 | 652.1535
2560.0354 | 655.5849
2561.0354 | 657.0605
2562.0354 | 658.4568
2563.0354 | 657.948
2564.0354 | 656.9666
2565.0354 | 662.1625
2566.0354 | 664.318
2567.0354 | 666.5024
2568.0354 | 665.3682
2569.0354 | 661.3675
2570.0354 | 658.8199
2571.0354 | 657.8644
2572.0354 | 656.8596
2573.0354 | 655.6128
2574.0354 | 655.1956
2575.0354 | 651.2998
2576.0354 | 647.8359
2577.0354 | 647.2519
2578.0354 | 649.7576
2579.0354 | 652.6642
2580.0354 | 653.3853
2581.0354 | 655.4756
2582.0354 | 653.7169
2583.0354 | 654.8775
2584.0354 | 656.9031
2585.0354 | 654.4295
2586.0354 | 651.5039
2587.0354 | 646.629
2588.0354 | 643.7574
2589.0354 | 644.1429
2590.0354 | 642.6773
2591.0354 | 646.6901
2592.0354 | 648.2371
2593.0354 | 646.836
2594.0354 | 645.3561
2595.0354 | 644.5973
2596.0354 | 643.9758
2597.0354 | 646.2577
2598.0354 | 645.5838
2599.0354 | 646.8936
2600.0354 | 644.399
2601.0354 | 643.2036
2602.0354 | 642.3157
2603.0354 | 639.6104
2604.0354 | 634.8539
2605.0354 | 638.0834
2606.0354 | 638.0214
2607.0354 | 636.2223
2608.0354 | 634.8605
2609.0354 | 637.7809
2610.0354 | 638.5876
2611.0354 | 641.9616
2612.0354 | 643.7714
2613.0354 | 645.6166
2614.0354 | 646.503
2615.0354 | 647.2721
2616.0354 | 645.8422
2617.0354 | 647.331
2618.0354 | 650.2682
2619.0354 | 651.8487
2620.0354 | 652.8644
2621.0354 | 648.1571
2622.0354 | 647.5294
2623.0354 | 645.9476
2624.0354 | 648.0029
2625.0354 | 649.474
2626.0354 | 651.2913
2627.0354 | 653.6031
2628.0354 | 656.4541
2629.0354 | 659.0138
2630.0354 | 659.4775
2631.0354 | 659.9528
2632.0354 | 657.5528
2633.0354 | 654.5681
2634.0354 | 655.178
2635.0354 | 654.6345
2636.0354 | 655.5325
2637.0354 | 657.8896
2638.0354 | 658.1281
2639.0354 | 656.1515
2640.0354 | 657.3172
2641.0354 | 656.9173
2642.0354 | 656.858
2643.0354 | 657.9645
2644.0354 | 659.4798
2645.0354 | 656.5896
2646.0354 | 650.9229
2647.0354 | 652.1107
2648.0354 | 650.0683
2649.0354 | 647.9172
2650.0354 | 646.171
2651.0354 | 644.4276
2652.0354 | 642.7767
2653.0354 | 643.7144
2654.0354 | 643.0006
2655.0354 | 641.6999
2656.0354 | 639.7136
2657.0354 | 638.1479
2658.0354 | 639.6328
2659.0354 | 641.1831
2660.0354 | 641.2839
2661.0354 | 643.2026
2662.0354 | 644.2034
2663.0354 | 644.4309
2664.0354 | 644.8395
2665.0354 | 644.5325
2666.0354 | 642.5359
2667.0354 | 642.2892
2668.0354 | 642.9103
2669.0354 | 645.1291
2670.0354 | 644.7093
2671.0354 | 643.0959
2672.0354 | 645.215
2673.0354 | 645.1182
2674.0354 | 646.3281
2675.0354 | 646.2991
2676.0354 | 646.5402
2677.0354 | 650.9262
2678.0354 | 651.1137
2679.0354 | 651.1936
2680.0354 | 651.7946
2681.0354 | 653.6252
2682.0354 | 652.2303
2683.0354 | 650.4843
2684.0354 | 649.2079
2685.0354 | 651.3009
2686.0354 | 651.7913
2687.0354 | 651.5467
2688.0354 | 652.8768
2689.0354 | 654.5552
2690.0354 | 654.0805
2691.0354 | 653.4663
2692.0354 | 649.7579
2693.0354 | 646.2644
2694.0354 | 646.9369
2695.0354 | 651.2495
2696.0354 | 652.4799
2697.0354 | 650.6591
2698.0354 | 650.1418
2699.0354 | 645.6741
2700.0354 | 647.5947
2701.0354 | 649.0448
2702.0354 | 652.702
2703.0354 | 653.7637
2704.0354 | 654.0026
2705.0354 | 651.6978
2706.0354 | 649.5182
2707.0354 | 650.5617
2708.0354 | 651.5207
2709.0354 | 653.2292
2710.0354 | 652.1131
2711.0354 | 647.9767
2712.0354 | 648.3416
2713.0354 | 650.6897
2714.0354 | 652.8235
2715.0354 | 655.518
2716.0354 | 656.5331
2717.0354 | 652.8703
2718.0354 | 650.8219
2719.0354 | 649.9733
2720.0354 | 649.1347
2721.0354 | 653.5576
2722.0354 | 654.4105
2723.0354 | 657.9572
2724.0354 | 660.3237
2725.0354 | 662.3145
2726.0354 | 663.5656
2727.0354 | 667.0522
2728.0354 | 669.9466
2729.0354 | 671.3681
2730.0354 | 670.4388
2731.0354 | 668.9116
2732.0354 | 670.0941
2733.0354 | 672.4487
2734.0354 | 673.4601
2735.0354 | 672.9885
2736.0354 | 669.1611
2737.0354 | 668.0317
2738.0354 | 669.7633
2739.0354 | 670.0454
2740.0354 | 673.6422
2741.0354 | 677.6443
2742.0354 | 679.5986
2743.0354 | 683.8807
2744.0354 | 683.8186
2745.0354 | 683.0171
2746.0354 | 680.9445
2747.0354 | 681.7018
2748.0354 | 682.6891
2749.0354 | 684.4158
2750.0354 | 683.5369
2751.0354 | 683.217
2752.0354 | 681.8222
2753.0354 | 681.7705
2754.0354 | 682.1442
2755.0354 | 681.0706
2756.0354 | 679.9018
2757.0354 | 676.1642
2758.0354 | 673.9994
2759.0354 | 673.6471
2760.0354 | 671.7414
2761.0354 | 671.6801
2762.0354 | 671.3941
2763.0354 | 673.2249
2764.0354 | 675.9006
2765.0354 | 677.0654
2766.0354 | 678.5907
2767.0354 | 679.4154
2768.0354 | 680.7161
2769.0354 | 681.3573
2770.0354 | 683.7647
2771.0354 | 684.6797
2772.0354 | 685.4523
2773.0354 | 684.5551
2774.0354 | 684.2632
2775.0354 | 682.9094
2776.0354 | 679.0852
2777.0354 | 682.0165
2778.0354 | 685.4396
2779.0354 | 681.6429
2780.0354 | 680.7098
2781.0354 | 681.4204
2782.0354 | 684.5355
2783.0354 | 687.2469
2784.0354 | 688.7055
2785.0354 | 687.8869
2786.0354 | 683.8839
2787.0354 | 680.4578
2788.0354 | 687.2569
2789.0354 | 687.7337
2790.0354 | 690.5419
2791.0354 | 688.4007
2792.0354 | 688.0984
2793.0354 | 689.0872
2794.0354 | 689.0565
2795.0354 | 685.5856
2796.0354 | 682.3972
2797.0354 | 680.7934
2798.0354 | 678.0251
2799.0354 | 673.873
2800.0354 | 672.722
2801.0354 | 671.045
2802.0354 | 667.4674
2803.0354 | 663.1662
2804.0354 | 664.0068
2805.0354 | 661.6375
2806.0354 | 660.8393
2807.0354 | 661.7
2808.0354 | 661.5222
2809.0354 | 664.1534
2810.0354 | 661.6445
2811.0354 | 662.2451
2812.0354 | 661.54
2813.0354 | 658.5629
2814.0354 | 657.9283
2815.0354 | 660.7957
2816.0354 | 661.2334
2817.0354 | 660.0415
2818.0354 | 659.3189
2819.0354 | 656.8059
2820.0354 | 655.9759
2821.0354 | 654.9877
2822.0354 | 654.2598
2823.0354 | 653.7081
2824.0354 | 651.4188
2825.0354 | 654.8689
2826.0354 | 657.0847
2827.0354 | 656.438
2828.0354 | 660.1746
2829.0354 | 659.5158
2830.0354 | 660.0609
2831.0354 | 659.9503
2832.0354 | 661.9586
2833.0354 | 666.2018
2834.0354 | 668.9924
2835.0354 | 668.6412
2836.0354 | 672.1269
2837.0354 | 675.4975
2838.0354 | 677.8162
2839.0354 | 675.7242
2840.0354 | 673.6961
2841.0354 | 675.7886
2842.0354 | 678.9757
2843.0354 | 680.8314
2844.0354 | 680.0597
2845.0354 | 680.8566
2846.0354 | 682.1221
2847.0354 | 680.6821
2848.0354 | 679.5124
2849.0354 | 677.5195
2850.0354 | 676.2122
2851.0354 | 673.8159
2852.0354 | 672.9303
2853.0354 | 671.5301
2854.0354 | 668.7964
2855.0354 | 667.7086
2856.0354 | 665.7765
2857.0354 | 666.5085
2858.0354 | 667.9972
2859.0354 | 670.1628
2860.0354 | 671.7017
2861.0354 | 678.459
2862.0354 | 685.1301
2863.0354 | 687.7165
2864.0354 | 687.054
2865.0354 | 685.3083
2866.0354 | 683.1133
2867.0354 | 680.0514
2868.0354 | 679.7893
2869.0354 | 677.7428
2870.0354 | 676.5315
2871.0354 | 673.1427
2872.0354 | 670.5189
2873.0354 | 670.0285
2874.0354 | 667.0866
2875.0354 | 670.1706
2876.0354 | 669.6139
2877.0354 | 669.2609
2878.0354 | 666.2885
2879.0354 | 664.881
2880.0354 | 665.6684
2881.0354 | 663.1517
2882.0354 | 664.1267
2883.0354 | 665.5937
2884.0354 | 664.8675
2885.0354 | 666.7203
2886.0354 | 668.1116
2887.0354 | 668.9638
2888.0354 | 670.4969
2889.0354 | 676.8561
2890.0354 | 676.5157
2891.0354 | 673.8379
2892.0354 | 673.013
2893.0354 | 671.8153
2894.0354 | 671.149
2895.0354 | 670.3726
2896.0354 | 665.4301
2897.0354 | 670.0923
2898.0354 | 670.0114
2899.0354 | 667.4775
2900.0354 | 665.8302
2901.0354 | 668.3736
2902.0354 | 667.7486
2903.0354 | 661.7338
2904.0354 | 663.9065
2905.0354 | 664.8531
2906.0354 | 667.7245
2907.0354 | 667.0412
2908.0354 | 675.6382
2909.0354 | 675.93
2910.0354 | 674.4691
2911.0354 | 673.1238
2912.0354 | 671.8396
2913.0354 | 675.5809
2914.0354 | 679.6325
2915.0354 | 678.9946
2916.0354 | 679.6521
2917.0354 | 686.9938
2918.0354 | 689.8281
2919.0354 | 689.7261
2920.0354 | 689.6945
2921.0354 | 687.8949
2922.0354 | 684.7615
2923.0354 | 686.3756
2924.0354 | 686.5609
2925.0354 | 685.5027
2926.0354 | 686.3844
2927.0354 | 686.3536
2928.0354 | 684.6158
2929.0354 | 683.1146
2930.0354 | 679.3131
2931.0354 | 680.3896
2932.0354 | 679.5496
2933.0354 | 681.5935
2934.0354 | 685.6857
2935.0354 | 684.4264
2936.0354 | 680.224
2937.0354 | 677.7796
2938.0354 | 677.1827
2939.0354 | 677.0105
2940.0354 | 676.3647
2941.0354 | 673.2264
2942.0354 | 662.8663
2943.0354 | 661.8367
2944.0354 | 662.6609
2945.0354 | 666.2442
2946.0354 | 671.8419
2947.0354 | 684.3703
2948.0354 | 685.8967
2949.0354 | 687.6546
2950.0354 | 691.7084
2951.0354 | 691.7676
2952.0354 | 690.659
2953.0354 | 692.5642
2954.0354 | 693.4522
2955.0354 | 692.7032
2956.0354 | 689.2774
2957.0354 | 691.6194
2958.0354 | 691.7144
2959.0354 | 690.77
2960.0354 | 689.1604
2961.0354 | 688.9785
2962.0354 | 684.7778
2963.0354 | 680.3418
2964.0354 | 681.9014
2965.0354 | 682.9194
2966.0354 | 685.1466
2967.0354 | 684.1437
2968.0354 | 682.0848
2969.0354 | 680.0866
2970.0354 | 677.7422
2971.0354 | 670.9314
2972.0354 | 657.8918
2973.0354 | 654.1647
2974.0354 | 653.156
2975.0354 | 651.452
2976.0354 | 648.3486
2977.0354 | 650.9371
2978.0354 | 652.3311
2979.0354 | 658.3044
2980.0354 | 664.9024
2981.0354 | 654.2427
2982.0354 | 657.2034
2983.0354 | 658.6592
2984.0354 | 660.0658
2985.0354 | 659.1641
2986.0354 | 658.5026
2987.0354 | 657.5647
2988.0354 | 658.3547
2989.0354 | 657.5524
2990.0354 | 657.6578
2991.0354 | 672.8202
2992.0354 | 674.5532
2993.0354 | 671.5027
2994.0354 | 679.6986
2995.0354 | 682.8587
2996.0354 | 675.13
2997.0354 | 660.7644
2998.0354 | 659.1674
2999.0354 | 656.562
3000.0354 | 656.2683
3001.0354 | 654.6103
3002.0354 | 670.2857
3003.0354 | 654.7575
3004.0354 | 653.9395
3005.0354 | 653.7406
3006.0354 | 651.9116
3007.0354 | 650.4201
3008.0354 | 652.1198
3009.0354 | 656.153
3010.0354 | 665.5231
3011.0354 | 659.3627
3012.0354 | 656.5986
3013.0354 | 657.4708
3014.0354 | 660.2484
3015.0354 | 676.4668
3016.0354 | 665.4928
3017.0354 | 666.9275
3018.0354 | 677.4658
3019.0354 | 660.8065
3020.0354 | 657.9955
3021.0354 | 655.1197
3022.0354 | 671.5044
3023.0354 | 647.7754
3024.0354 | 660.6313
3025.0354 | 643.8619
3026.0354 | 645.2337
3027.0354 | 645.403
3028.0354 | 646.5495
3029.0354 | 645.402
3030.0354 | 644.2747
3031.0354 | 643.3927
3032.0354 | 645.4571
3033.0354 | 645.0496
3034.0354 | 657.4703
3035.0354 | 644.6594
3036.0354 | 643.4462
3037.0354 | 647.0187
3038.0354 | 646.2186
3039.0354 | 671.6821
3040.0354 | 672.487
3041.0354 | 643.1134
3042.0354 | 641.783
3043.0354 | 640.7766
3044.0354 | 639.6918
3045.0354 | 637.9093
3046.0354 | 640.4806
3047.0354 | 639.4791
3048.0354 | 651.2911
3049.0354 | 650.3963
3050.0354 | 649.3012
3051.0354 | 648.3721
3052.0354 | 647.4003
3053.0354 | 645.4697
3054.0354 | 644.7744
3055.0354 | 644.2082
3056.0354 | 642.5701
3057.0354 | 644.1786
3058.0354 | 644.3718
3059.0354 | 642.2144
3060.0354 | 640.5232
3061.0354 | 641.7408
3062.0354 | 642.1361
3063.0354 | 637.9084
3064.0354 | 635.0626
3065.0354 | 634.9385
3066.0354 | 647.676
3067.0354 | 667.093
3068.0354 | 665.9403
3069.0354 | 664.5505
3070.0354 | 663.5493
3071.0354 | 663.5711
3072.0354 | 665.961
3073.0354 | 658.2925
3074.0354 | 665.1856
3075.0354 | 663.0743
3076.0354 | 665.0637
3077.0354 | 664.1911
3078.0354 | 665.9827
3079.0354 | 667.8883
3080.0354 | 666.7174
3081.0354 | 665.1549
3082.0354 | 664.8954
3083.0354 | 666.8724
3084.0354 | 667.3709
3085.0354 | 664.682
3086.0354 | 663.1958
3087.0354 | 662.604
3088.0354 | 665.2005
3089.0354 | 667.9599
3090.0354 | 669.0016
3091.0354 | 672.0469
3092.0354 | 677.9516
3093.0354 | 678.9701
3094.0354 | 677.2579
3095.0354 | 677.1115
3096.0354 | 680.8895
3097.0354 | 684.5279
3098.0354 | 685.6551
3099.0354 | 684.4413
3100.0354 | 685.6685
3101.0354 | 683.2743
3102.0354 | 684.1014
3103.0354 | 684.539
3104.0354 | 683.5939
3105.0354 | 687.1671
3106.0354 | 687.715
3107.0354 | 688.7528
3108.0354 | 691.8426
3109.0354 | 693.2264
3110.0354 | 697.0897
3111.0354 | 694.8193
3112.0354 | 694.1529
3113.0354 | 695.9729
3114.0354 | 698.2536
3115.0354 | 698.1703
3116.0354 | 700.4345
3117.0354 | 699.1236
3118.0354 | 697.289
3119.0354 | 694.3192
3120.0354 | 689.0005
3121.0354 | 684.9257
3122.0354 | 682.2873
3123.0354 | 678.3936
3124.0354 | 675.839
3125.0354 | 673.3412
3126.0354 | 670.194
3127.0354 | 667.4698
3128.0354 | 667.3989
3129.0354 | 666.1365
3130.0354 | 666.8338
3131.0354 | 666.1995
3132.0354 | 667.3531
3133.0354 | 658.2822
3134.0354 | 671.5779
3135.0354 | 670.9921
3136.0354 | 670.6283
3137.0354 | 668.9219
3138.0354 | 670.1548
3139.0354 | 667.4742
3140.0354 | 668.9762
3141.0354 | 666.3835
3142.0354 | 666.969
3143.0354 | 667.5539
3144.0354 | 663.3982
3145.0354 | 665.2442
3146.0354 | 663.4125
3147.0354 | 665.0591
3148.0354 | 663.6912
3149.0354 | 665.2576
3150.0354 | 670.67
3151.0354 | 671.1209
3152.0354 | 667.2958
3153.0354 | 665.1631
3154.0354 | 666.513
3155.0354 | 665.5204
3156.0354 | 669.5284
3157.0354 | 668.168
3158.0354 | 669.7597
3159.0354 | 670.7011
3160.0354 | 671.0388
3161.0354 | 671.2279
3162.0354 | 673.3652
3163.0354 | 672.4309
3164.0354 | 669.8301
3165.0354 | 670.731
3166.0354 | 672.4739
3167.0354 | 677.7625
3168.0354 | 682.0059
3169.0354 | 684.2804
3170.0354 | 686.4223
3171.0354 | 685.6327
3172.0354 | 687.5566
3173.0354 | 687.7328
3174.0354 | 685.1859
3175.0354 | 683.4898
3176.0354 | 686.0897
3177.0354 | 686.4573
3178.0354 | 686.6062
3179.0354 | 703.3777
3180.0354 | 702.9231
3181.0354 | 705.9576
3182.0354 | 712.6225
3183.0354 | 722.5439
3184.0354 | 723.1735
3185.0354 | 764.7296
3186.0354 | 765.3588
3187.0354 | 744.668
3188.0354 | 768.6468
3189.0354 | 793.0955
3190.0354 | 819.3097
3191.0354 | 843.2397
3192.0354 | 840.3063
3193.0354 | 870.5042
3194.0354 | 871.7845
3195.0354 | 872.302
3196.0354 | 877.6379
3197.0354 | 878.4096
3198.0354 | 880.1524
3199.0354 | 882.2694
3200.0354 | 882.3124
3201.0354 | 886.2271
3202.0354 | 884.8664
3203.0354 | 885.2072
3204.0354 | 883.7535
3205.0354 | 883.6441
3206.0354 | 883.8952
3207.0354 | 881.6382
3208.0354 | 881.019
3209.0354 | 886.1072
3210.0354 | 888.319
3211.0354 | 889.5116
3212.0354 | 888.4966
3213.0354 | 892.392
3214.0354 | 894.919
3215.0354 | 896.0728
3216.0354 | 892.9514
3217.0354 | 891.4895
3218.0354 | 888.3369
3219.0354 | 889.8868
3220.0354 | 888.0852
3221.0354 | 887.8817
3222.0354 | 886.968
3223.0354 | 892.039
3224.0354 | 890.8239
3225.0354 | 890.8167
3226.0354 | 889.4171
3227.0354 | 559.2128
3228.0354 | 562.6858
3229.0354 | 560.3757
3230.0354 | 552.0379
3231.0354 | 551.1532
3232.0354 | 542.7096
3233.0354 | 541.3645
3234.0354 | 536.6949
3235.0354 | 532.9501
3236.0354 | 534.6493
3237.0354 | 536.3117
3238.0354 | 537.9383
3239.0354 | 538.7154
3240.0354 | 537.1603
3241.0354 | 535.6802
3242.0354 | 608.1106
3243.0354 | 561.5501
3244.0354 | 560.4109
3245.0354 | 570.2427
3246.0354 | 625.3694
3247.0354 | 770.3582
3248.0354 | 839.6466
3249.0354 | 848.1396
3250.0354 | 846.5696
3251.0354 | 851.7338
3252.0354 | 853.5143
3253.0354 | 855.9861
3254.0354 | 854.8754
3255.0354 | 853.1881
3256.0354 | 854.4506
3257.0354 | 855.2178
3258.0354 | 853.3098
3259.0354 | 853.2522
3260.0354 | 852.858
3261.0354 | 853.102
3262.0354 | 852.5226
3263.0354 | 853.9296
3264.0354 | 851.8967
3265.0354 | 853.6724
3266.0354 | 853.2933
3267.0354 | 857.0511
3268.0354 | 858.0353
3269.0354 | 854.0655
3270.0354 | 854.7686
3271.0354 | 855.6767
3272.0354 | 856.2518
3273.0354 | 865.508
3274.0354 | 856.0997
3275.0354 | 861.586
3276.0354 | 876.8898
3277.0354 | 878.6495
3278.0354 | 759.1303
3279.0354 | 876.7145
3280.0354 | 881.6396
3281.0354 | 812.078
3282.0354 | 886.2386
3283.0354 | 887.766
3284.0354 | 887.4797
3285.0354 | 892.6258
3286.0354 | 890.1848
3287.0354 | 894.4307
3288.0354 | 898.3502
3289.0354 | 896.4228
3290.0354 | 899.4336
3291.0354 | 899.0242
3292.0354 | 897.1344
3293.0354 | 893.4621
3294.0354 | 896.9836
3295.0354 | 898.3528
3296.0354 | 903.3835
3297.0354 | 906.8745
3298.0354 | 906.4032
3299.0354 | 910.7228
3300.0354 | 910.9254
3301.0354 | 911.5467
3302.0354 | 914.9889
3303.0354 | 917.3604
3304.0354 | 918.769
3305.0354 | 914.5368
3306.0354 | 913.8394
3307.0354 | 916.7056
3308.0354 | 930.7648
3309.0354 | 934.5951
3310.0354 | 937.0141
3311.0354 | 938.2795
3312.0354 | 940.5429
3313.0354 | 939.6745
3314.0354 | 941.0445
3315.0354 | 942.3837
3316.0198 | 948.5048
3317.0354 | 948.4478
3318.0354 | 946.0841
3319.0354 | 947.7935
3320.0354 | 948.1856
3321.0354 | 945.8409
3322.0354 | 944.2688
3323.0354 | 944.3011
3324.0354 | 942.1525
3325.0354 | 946.6596
3326.0354 | 819.367
3327.0354 | 949.3192
3328.0354 | 831.0538
3329.0354 | 959.5353
3330.0354 | 963.63
3331.0354 | 963.0529
3332.0354 | 958.9388
3333.0354 | 962.5994
3334.0354 | 960.8288
3335.0354 | 964.304
3336.0354 | 967.1099
3337.0354 | 969.5486
3338.0354 | 971.3703
3339.0354 | 967.8349
3340.0354 | 966.4045
3341.0354 | 970.3983
3342.0354 | 968.865
3343.0354 | 976.332
3344.0354 | 978.3716
3345.0354 | 980.4104
3346.0354 | 980.1873
3347.0354 | 982.5833
3348.0354 | 986.8834
3349.0354 | 990.622
3350.0354 | 989.3078
3351.0354 | 991.772
3352.0354 | 993.0948
3353.0354 | 995.5019
3354.0354 | 998.7569
3355.0354 | 1005.944
3356.0354 | 1007.9049
3357.0354 | 1016.7805
3358.0354 | 867.9686
3359.0354 | 1020.7073
3360.0354 | 1022.4007
3361.0354 | 920.5918
3362.0354 | 1024.9726
3363.0354 | 1027.5259
3364.0354 | 1029.5495
3365.0354 | 1032.1822
3366.0354 | 1032.3162
3367.0354 | 1031.1175
3368.0354 | 1030.915
3369.0354 | 1029.4949
3370.0354 | 1030.0929
3371.0354 | 1032.1133
3372.0354 | 902.6847
3373.0354 | 867.0205
3374.0354 | 1029.5088
3375.0354 | 1036.1878
3376.0354 | 1036.6467
3377.0354 | 1033.9987
3378.0354 | 1033.8431
3379.0354 | 1033.6863
3380.0354 | 972.7456
3381.0354 | 1035.879
3382.0354 | 1031.965
3383.0354 | 1033.2035
3384.0354 | 1033.9015
3385.0354 | 1033.5137
3386.0354 | 1036.0814
3387.0354 | 1030.2808
3388.0354 | 1029.8687
3389.0354 | 1022.6822
3390.0354 | 1020.242
3391.0354 | 1022.8664
3392.0354 | 1020.3093
3393.0354 | 1010.2714
3394.0354 | 1017.4759
3395.0354 | 1016.2849
3396.0354 | 1025.4538
3397.0354 | 1028.3373
3398.0354 | 1032.7684
3399.0354 | 1034.9257
3400.0354 | 1038.6092
3401.0354 | 1040.8556
3402.0354 | 1036.6693
3403.0354 | 1037.6199
3404.0354 | 1038.3436
3405.0354 | 1038.223
3406.0354 | 1039.6518
3407.0354 | 1043.7232
3408.0354 | 1055.4734
3409.0354 | 1056.8245
3410.0354 | 1062.1922
3411.0354 | 1055.2024
3412.0354 | 1059.5416
3413.0354 | 1061.7327
3414.0354 | 1065.7097
3415.0354 | 1065.8245
3416.0354 | 986.5072
3417.0354 | 1005.1189
3418.0354 | 651.561
3419.0354 | 644.4473
3420.0354 | 644.6189
3421.0354 | 642.8469
3422.0354 | 643.145
3423.0354 | 643.3116
3424.0354 | 644.0502
3425.0354 | 644.7642
3426.0354 | 644.1693
3427.0354 | 646.4383
3428.0354 | 643.5346
3429.0354 | 628.3253
3430.0354 | 605.1332
3431.0354 | 636.8467
3432.0354 | 636.1612
3433.0354 | 625.6448
3434.0354 | 638.6032
3435.0354 | 638.6342
3436.0354 | 639.2276
3437.0354 | 638.602
3438.0354 | 638.1995
3439.0354 | 638.8614
3440.0354 | 639.3335
3441.0354 | 637.7676
3442.0354 | 636.3293
3443.0354 | 635.7373
3444.0354 | 635.8551
3445.0354 | 635.4847
3446.0354 | 635.5332
3447.0354 | 636.2822
3448.0354 | 638.3168
3449.0354 | 638.3413
3450.0354 | 638.4347
3451.0354 | 641.5016
3452.0354 | 640.7517
3453.0354 | 640.7284
3454.0354 | 640.9346
3455.0354 | 641.3251
3456.0354 | 641.6964
3457.0354 | 640.1497
3458.0354 | 637.2366
3459.0354 | 635.7722
3460.0354 | 638.316
3461.0354 | 637.6806
3462.0354 | 635.8795
3463.0354 | 636.0908
3464.0354 | 638.2091
3465.0354 | 640.2343
3466.0354 | 640.3669
3467.0354 | 641.2724
3468.0354 | 643.5571
3469.0354 | 639.9275
3470.0354 | 638.9571
3471.0354 | 636.6575
3472.0354 | 636.739
3473.0354 | 636.7965
3474.0354 | 637.7774
3475.0354 | 638.9789
3476.0354 | 638.5715
3477.0354 | 638.6547
3478.0354 | 635.6082
3479.0354 | 635.8629
3480.0354 | 635.3707
3481.0354 | 635.2596
3482.0354 | 636.1096
3483.0354 | 637.3396
3484.0354 | 638.0689
3485.0354 | 638.224
3486.0354 | 603.4234
3487.0354 | 612.471
3488.0354 | 595.8876
3489.0354 | 605.5926
3490.0354 | 651.7989
3491.0354 | 603.0145
3492.0354 | 623.0523
3493.0354 | 634.1326
3494.0354 | 633.4611
3495.0354 | 633.8973
3496.0354 | 632.2659
3497.0354 | 630.8115
3498.0354 | 629.3316
3499.0354 | 628.7878
3500.0354 | 625.9642
3501.0354 | 624.6084
3502.0354 | 623.3098
3503.0354 | 623.9981
3504.0354 | 623.541
3505.0354 | 622.2027
3506.0354 | 620.7425
3507.0354 | 615.0083
3508.0354 | 615.7429
3509.0354 | 613.9934
3510.0354 | 613.4871
3511.0354 | 613.0674
3512.0354 | 611.7818
3513.0354 | 611.4649
3514.0354 | 612.783
3515.0354 | 612.9552
3516.0354 | 612.8281
3517.0354 | 612.5973
3518.0354 | 612.8154
3519.0354 | 612.9542
3520.0354 | 612.8688
3521.0354 | 612.5285
3522.0354 | 612.0135
3523.0354 | 612.1517
3524.0354 | 611.8052
3525.0354 | 611.9207
3526.0354 | 612.4475
3527.0354 | 612.0455
3528.0354 | 611.0096
3529.0354 | 609.8572
3530.0354 | 608.909
3531.0354 | 608.3579
3532.0354 | 608.5112
3533.0354 | 607.9963
3534.0354 | 608.2198
3535.0354 | 607.4408
3536.0354 | 606.1059
3537.0354 | 605.2641
3538.0354 | 605.2664
3539.0354 | 604.97
3540.0354 | 604.3631
3541.0354 | 602.8285
3542.0354 | 602.419
3543.0354 | 601.1623
3544.0354 | 600.7644
3545.0354 | 601.1055
3546.0354 | 601.8343
3547.0354 | 582.3961
3548.0354 | 581.5128
3549.0354 | 581.7734
3550.0354 | 580.7805
3551.0354 | 581.2133
3552.0354 | 582.9913
3553.0354 | 582.1601
3554.0354 | 580.8687
3555.0354 | 580.5351
3556.0354 | 579.6238
3557.0354 | 579.8465
3558.0354 | 578.6645
3559.0354 | 595.1117
3560.0354 | 598.8699
3561.0354 | 598.8787
3562.0354 | 599.4548
3563.0354 | 599.8011
3564.0354 | 596.2213
3565.0354 | 589.6059
3566.0354 | 600.7868
3567.0354 | 600.9103
3568.0354 | 601.3587
3569.0354 | 601.5308
3570.0354 | 602.5879
3571.0354 | 601.3775
3572.0354 | 600.5403
3573.0354 | 602.0123
3574.0354 | 602.2411
3575.0354 | 603.0104
3576.0354 | 604.8192
3577.0354 | 603.985
3578.0354 | 604.3332
3579.0354 | 604.4872
3580.0354 | 606.1391
3581.0354 | 607.0911
3582.0354 | 607.4277
3583.0354 | 607.7695
3584.0354 | 606.8496
3585.0354 | 606.8596
3586.0354 | 606.4925
3587.0354 | 605.614
3588.0354 | 605.3949
3589.0354 | 605.3621
3590.0354 | 603.9034
3591.0354 | 604.6947
3592.0354 | 606.8504
3593.0354 | 607.477
3594.0354 | 608.4242
3595.0354 | 610.5666
3596.0354 | 610.0962
3597.0354 | 608.6629
3598.0354 | 609.1429
3599.0354 | 610.5978
3600.0354 | 610.4035
3601.0354 | 610.8835
3602.0354 | 611.853
3603.0354 | 611.1565
3604.0354 | 607.6368
3605.0354 | 608.9983
3606.0354 | 609.9097
3607.0354 | 608.8304
3608.0354 | 610.3273
3609.0354 | 600.347
3610.0354 | 600.8233
3611.0354 | 602.6398
3612.0354 | 601.1774
3613.0354 | 597.9727
3614.0354 | 602.3432
3615.0354 | 602.6559
3616.0354 | 603.7725
3617.0354 | 603.2795
3618.0354 | 602.9863
3619.0354 | 602.694
3620.0354 | 607.5381
3621.0354 | 604.1229
3622.0354 | 603.8218
3623.0354 | 604.5866
3624.0354 | 604.7712
3625.0354 | 604.1114
3626.0354 | 603.1861
3627.0354 | 602.7857
3628.0354 | 603.7
3629.0354 | 602.101
3630.0354 | 601.9065
3631.0354 | 602.6395
3632.0354 | 604.0911
3633.0354 | 603.9786
3634.0354 | 604.3992
3635.0354 | 607.1507
3636.0354 | 607.4489
3637.0354 | 607.3441
3638.0354 | 608.9961
3639.0354 | 607.0594
3640.0354 | 610.3259
3641.0354 | 613.1901
3642.0354 | 613.2025
3643.0354 | 608.9121
3644.0354 | 612.2754
3645.0354 | 612.7585
3646.0354 | 613.24
3647.0354 | 614.8283
3648.0354 | 614.831
3649.0354 | 611.5515
3650.0354 | 612.5336
3651.0354 | 575.5338
3652.0354 | 607.8748
3653.0354 | 611.8799
3654.0354 | 611.7968
3655.0354 | 610.9511
3656.0354 | 613.7912
3657.0354 | 612.8331
3658.0354 | 613.9178
3659.0354 | 615.6075
3660.0354 | 616.5247
3661.0354 | 618.019
3662.0354 | 616.5549
3663.0354 | 618.0573
3664.0354 | 608.9892
3665.0354 | 571.6504
3666.0354 | 566.4075
3667.0354 | 565.8878
3668.0354 | 566.8372
3669.0354 | 565.4206
3670.0354 | 564.7972
3671.0354 | 564.9315
3672.0354 | 563.7899
3673.0354 | 560.3998
3674.0354 | 561.18
3675.0354 | 611.0738
3676.0354 | 654.2854
3677.0354 | 652.391
3678.0354 | 657.0322
3679.0354 | 658.9868
3680.0354 | 649.7254
3681.0354 | 652.911
3682.0354 | 644.1422
3683.0354 | 645.8869
3684.0354 | 642.6323
3685.0354 | 640.4061
3686.0354 | 639.8446
3687.0354 | 644.9055
3688.0354 | 643.8619
3689.0354 | 644.5063
3690.0354 | 645.9332
3691.0354 | 646.7978
3692.0354 | 648.7027
3693.0354 | 651.4346
3694.0354 | 651.1177
3695.0354 | 649.4851
3696.0354 | 651.1388
3697.0354 | 649.1019
3698.0354 | 650.8354
3699.0354 | 657.5056
3700.0354 | 653.9205
3701.0354 | 657.1879
3702.0354 | 659.3043
3703.0354 | 659.3835
3704.0354 | 660.4198
3705.0354 | 678.4109
3706.0354 | 689.1907
3707.0354 | 668.1109
3708.0354 | 663.5747
3709.0354 | 672.8641
3710.0354 | 659.5463
3711.0354 | 660.7023
3712.0354 | 662.2376
3713.0354 | 660.9819
3714.0354 | 662.2372
3715.0354 | 658.2219
3716.0354 | 660.3714
3717.0354 | 662.6658
3718.0354 | 662.1787
3719.0354 | 662.276
3720.0354 | 662.1698
3721.0354 | 663.4554
3722.0354 | 666.6125
3723.0354 | 670.1979
3724.0354 | 668.2382
3725.0354 | 669.7434
3726.0354 | 651.949
3727.0354 | 704.379
3728.0354 | 706.5612
3729.0354 | 708.5182
3730.0354 | 711.8753
3731.0354 | 706.9545
3732.0354 | 689.2571
3733.0354 | 690.8223
3734.0354 | 688.8847
3735.0354 | 673.1066
3736.0354 | 671.8827
3737.0354 | 671.3512
3738.0354 | 670.9785
3739.0354 | 666.6667
3740.0354 | 666.5716
3741.0354 | 666.9224
3742.0354 | 670.4463
3743.0354 | 668.9664
3744.0354 | 670.6198
3745.0354 | 671.1778
3746.0354 | 673.1828
3747.0354 | 678.6191
3748.0354 | 679.0235
3749.0354 | 682.6918
3750.0354 | 685.2406
3751.0354 | 687.0547
3752.0354 | 690.33
3753.0354 | 695.857
3754.0354 | 691.1809
3755.0354 | 702.3369
3756.0354 | 704.2674
3757.0354 | 701.779
3758.0354 | 695.7056
3759.0354 | 693.1323
3760.0354 | 696.4967
3761.0354 | 700.2194
3762.0354 | 703.2926
3763.0354 | 697.751
3764.0354 | 696.4741
3765.0354 | 701.0055
3766.0354 | 699.1551
3767.0354 | 700.4467
3768.0354 | 705.0932
3769.0354 | 700.6597
3770.0354 | 708.7904
3771.0354 | 708.027
3772.0354 | 711.4887
3773.0354 | 718.2538
3774.0354 | 713.6761
3775.0354 | 711.0113
3776.0354 | 717.838
3777.0354 | 715.1718
3778.0354 | 715.1101
3779.0354 | 715.1443
3780.0354 | 715.0018
3781.0354 | 711.6555
3782.0354 | 711.0623
3783.0354 | 713.3983
3784.0354 | 709.1787
3785.0354 | 712.5382
3786.0354 | 714.5291
3787.0354 | 704.8623
3788.0354 | 708.9248
3789.0354 | 713.886
3790.0354 | 713.8967
3791.0354 | 713.3816
3792.0354 | 717.5099
3793.0354 | 707.2952
3794.0354 | 718.2741
3795.0354 | 724.6554
3796.0354 | 724.1562
3797.0354 | 729.7716
3798.0354 | 726.0854
3799.0354 | 727.4068
3800.0354 | 728.7223
3801.0354 | 722.8009
3802.0354 | 725.4542
3803.0354 | 731.4743
3804.0354 | 729.8527
3805.0354 | 726.5262
3806.0354 | 785.2077
3807.0354 | 798.7493
3808.0354 | 806.3222
3809.0354 | 823.5898
3810.0354 | 816.0198
3811.0354 | 790.0549
3812.0354 | 777.4527
3813.0354 | 789.845
3814.0354 | 791.471
3815.0354 | 796.1349
3816.0354 | 787.8596
3817.0354 | 783.0761
3818.0354 | 780.9996
3819.0354 | 792.6328
3820.0354 | 791.7286
3821.0354 | 793.1028
3822.0354 | 794.3742
3823.0354 | 800.3152
3824.0354 | 849.4761
3825.0354 | 856.9363
3826.0354 | 854.2734
3827.0354 | 852.5529
3828.0354 | 856.9459
3829.0354 | 839.9362
3830.0354 | 835.4853
3831.0354 | 833.4376
3832.0354 | 829.959
3833.0354 | 845.5681
3834.0354 | 844.258
3835.0354 | 852.1342
3836.0354 | 856.6957
3837.0354 | 853.914
3838.0354 | 854.348
3839.0354 | 852.7555
3840.0354 | 857.4992
3841.0354 | 853.375
3842.0354 | 861.5533
3843.0354 | 876.1994
3844.0354 | 880.9615
3845.0354 | 881.4985
3846.0354 | 878.1354
3847.0354 | 881.0969
3848.0354 | 881.9264
3849.0354 | 881.08
3850.0354 | 878.5374
3851.0354 | 886.8264
3852.0354 | 887.6769
3853.0354 | 890.3343
3854.0354 | 890.9982
3855.0354 | 889.6259
3856.0354 | 890.8053
3857.0354 | 895.5412
3858.0354 | 895.0848
3859.0354 | 892.8526
3860.0354 | 903.0961
3861.0354 | 897.2493
3862.0354 | 905.6166
3863.0354 | 904.3451
3864.0354 | 897.2711
3865.0354 | 894.8773
3866.0354 | 891.6847
3867.0354 | 893.5955
3868.0354 | 908.8496
3869.0354 | 902.9439
3870.0354 | 899.3636
3871.0354 | 897.5888
3872.0354 | 895.7956
3873.0354 | 901.3951
3874.0354 | 899.7564
3875.0354 | 898.5584
3876.0354 | 910.9767
3877.0354 | 908.0016
3878.0354 | 903.1849
3879.0354 | 920.5745
3880.0354 | 913.2502
3881.0354 | 904.7422
3882.0354 | 905.4121
3883.0354 | 906.3649
3884.0354 | 912.1774
3885.0354 | 920.2805
3886.0354 | 916.8093
3887.0354 | 919.5075
3888.0354 | 914.3902
3889.0354 | 910.6541
3890.0354 | 910.984
3891.0354 | 905.7002
3892.0354 | 894.1367
3893.0354 | 879.4524
3894.0354 | 891.9508
3895.0354 | 898.0327
3896.0354 | 893.6781
3897.0354 | 899.349
3898.0354 | 918.8055
3899.0354 | 923.372
3900.0354 | 926.429
3901.0354 | 925.8865
3902.0354 | 929.5046
3903.0354 | 919.5812
3904.0354 | 920.9473
3905.0354 | 929.9275
3906.0354 | 928.0674
3907.0354 | 925.3114
3908.0354 | 924.7175
3909.0354 | 922.8346
3910.0354 | 927.0085
3911.0354 | 932.1896
3912.0354 | 930.2365
3913.0354 | 933.5202
3914.0354 | 925.6122
3915.0354 | 923.4005
3916.0354 | 925.6281
3917.051 | 928.5328
3918.0354 | 925.097
3919.0354 | 928.8317
3920.0354 | 931.1949
3921.0354 | 930.6075
3922.0354 | 931.2308
3923.0354 | 935.1547
3924.0354 | 932.6013
3925.0354 | 935.6026
3926.0354 | 931.1031
3927.0354 | 934.418
3928.0354 | 938.556
3929.0354 | 932.0858
3930.0354 | 935.7688
3931.0354 | 935.8437
3932.0354 | 930.5391
3933.0354 | 933.9195
3934.0354 | 931.8433
3935.0354 | 938.3787
3936.0354 | 935.5701
3937.0354 | 927.4563
3938.0354 | 925.1196
3939.0198 | 925.3919
3940.0354 | 914.5639
3941.0354 | 854.5525
3942.0354 | 881.8457
3943.0354 | 592.2778
3944.0354 | 428.6879
3945.0354 | 468.9173
3946.0354 | 705.8976
3947.0354 | 417.3308
3948.0354 | 417.0034
3949.0354 | 417.1624
3950.0354 | 415.7347
3951.0354 | 413.9259
3952.0354 | 412.7522
3953.0354 | 409.3918
3954.0354 | 410.8938
3955.0354 | 412.2412
3956.0354 | 410.4051
3957.0354 | 409.3988
3958.0354 | 410.9456
3959.0354 | 412.2395
3960.0354 | 410.9456
3961.0354 | 411.8736
3962.0354 | 411.6573
3963.0354 | 409.7483
3964.0354 | 407.3002
3965.0354 | 415.9944
3966.0354 | 415.4109
3967.0354 | 408.019
3968.0354 | 408.3008
3969.0354 | 405.9256
3970.0354 | 405.362
3971.0354 | 405.0036
3972.0354 | 400.3845
3973.0354 | 398.5674
3974.0354 | 400.0227
3975.0354 | 401.302
3976.0354 | 383.6923
3977.0354 | 384.5092
3978.0354 | 386.9961
3979.0354 | 382.6967
3980.0354 | 379.859
3981.0354 | 388.8716
3982.0354 | 387.7933
3983.0354 | 389.4182
3984.0354 | 384.8835
3985.0354 | 391.0828
3986.0354 | 385.63
3987.0354 | 358.5803
3988.0354 | 347.2055
3989.0354 | 391.8436
3990.0354 | 391.3699
3991.0354 | 389.964
3992.0354 | 383.8182
3993.0354 | 377.7934
3994.0354 | 384.3348
3995.0354 | 378.9182
3996.0354 | 387.4618
3997.0354 | 400.4869
3998.0354 | 395.2405
3999.0354 | 396.8775
4000.0354 | 396.1765
4001.0354 | 393.6606
4002.0198 | 393.4993
4003.0354 | 398.0026
4004.0354 | 394.4967
4005.0354 | 384.8389
4006.0354 | 392.4127
4007.0354 | 320.6344
4008.0354 | 323.918
4009.0354 | 397.1131
4010.0354 | 363.2371
4011.0354 | 506.1494
4012.0354 | 414.5511
4013.0354 | 317.3925
4014.0354 | 288.3612
4015.0354 | 306.9897
4016.0354 | 399.7024
4017.0354 | 398.6085
4018.0354 | 391.6704
4019.0354 | 398.1605
4020.0354 | 392.3684
4021.0354 | 398.2934
4022.0354 | 404.1603
4023.0354 | 406.9414
4024.0354 | 392.7121
4025.0354 | 388.3393
4026.0354 | 397.9735
4027.0354 | 386.1899
4028.0354 | 402.6085
4029.0354 | 390.7423
4030.0354 | 385.2684
4031.0354 | 386.6274
4032.0354 | 385.2654
4033.0354 | 386.8716
4034.0354 | 389.9418
4035.0354 | 390.9275
4036.0354 | 384.3439
4037.0354 | 593.137
4038.0354 | 895.2747
4039.0354 | 879.4367
4040.0354 | 937.4302
4041.0354 | 432.9703
4042.0354 | 429.6651
4043.0354 | 385.6002
4044.0354 | 406.2428
4045.0354 | 385.6196
4046.0354 | 382.7717
4047.0354 | 381.304
4048.0354 | 799.4675
4049.0354 | 791.379
4050.0354 | 554.1376
4051.0354 | 519.6926
4052.0354 | 473.831
4053.0354 | 469.8983
4054.0354 | 440.8901
4055.0354 | 415.6805
4056.0354 | 411.8642
4057.0354 | 421.2964
4058.0354 | 437.8289
4059.0354 | 439.5087
4060.0354 | 435.5307
4061.0354 | 443.2035
4062.0354 | 414.841
4063.0354 | 442.9753
4064.0354 | 435.8976
4065.0354 | 434.8019
4066.0354 | 580.2767
4067.0354 | 580.034
4068.0354 | 634.1066
4069.0354 | 416.0043
4070.0354 | 409.9102
4071.0354 | 409.8722
4072.0354 | 640.5696
4073.0354 | 760.558
4074.0354 | 436.6448
4075.0354 | 395.6816
4076.0354 | 395.6456
4077.0354 | 376.9576
4078.0354 | 359.9567
4079.0354 | 351.5408
4080.0354 | 357.2682
4081.0354 | 351.1699
4082.0354 | 348.3298
4083.0354 | 341.2687
4084.0354 | 404.0546
4085.0354 | 401.8891
4086.0354 | 398.3049
4087.0354 | 398.7207
4088.0354 | 419.3743
4089.0354 | 401.8203
4090.0354 | 380.869
4091.0354 | 376.9596
4092.0354 | 370.4737
4093.0354 | 370.7874
4094.0354 | 370.512
4095.0354 | 367.1444
4096.0354 | 373.4573
4097.0354 | 375.0018
4098.0354 | 365.9518
4099.0354 | 359.4609
4100.0354 | 370.8694
4101.0354 | 357.0156
4102.0354 | 345.1645
4103.0354 | 341.8525
4104.0354 | 329.017
4105.0354 | 326.5933
4106.0354 | 802.1781
4107.0354 | 392.3949
4108.0354 | 343.8611
4109.0354 | 343.7506
4110.0354 | 782.3965
4111.0354 | 647.4296
4112.0354 | 355.9589
4113.0354 | 351.3561
4114.0354 | 348.1222
4115.0354 | 342.8672
4116.0354 | 343.5023
4117.0354 | 336.9567
4118.0354 | 337.3894
4119.0354 | 377.7577
4120.0354 | 333.265
4121.0354 | 326.7739
4122.0354 | 321.7839
4123.0354 | 320.4141
4124.0354 | 317.5301
4125.0354 | 311.5269
4126.0354 | 307.6699
4127.0354 | 307.3678
4128.0354 | 828.8204
4129.0354 | 973.2111
4130.0354 | 996.2922
4131.0354 | 987.7174
4132.0354 | 987.647
4133.0354 | 991.8182
4134.0354 | 997.1707
4135.0354 | 1003.945
4136.0354 | 1004.6833
4137.0354 | 1003.9486
4138.0354 | 1008.8063
4139.0354 | 1016.764
4140.0354 | 1034.3161
4141.0354 | 1049.8034
4142.0354 | 1051.9732
4143.0354 | 1050.9324
4144.0354 | 1056.363
4145.0354 | 1047.4159
4146.0354 | 1051.9236
4147.0354 | 1056.3181
4148.0354 | 1053.1869
4149.0354 | 1070.0202
4150.0354 | 1063.3701
4151.0354 | 1079.7391
4152.0354 | 1074.5228
4153.0354 | 1081.6607
4154.0354 | 1041.1594
4155.0354 | 1061.4511
4156.0354 | 1024.1726
4157.0354 | 1037.167
4158.0354 | 960.2392
4159.0354 | 1034.0883
4160.0354 | 1045.6423
4161.0354 | 1026.7576
4162.0354 | 1070.9881
4163.0354 | 1114.6505
4164.0354 | 863.9458
4165.0354 | 1025.4001
4166.0354 | 970.8456
4167.0354 | 1077.5397
4168.0354 | 1057.3812
4169.0354 | 1112.1945
4170.0354 | 1129.1033
4171.0354 | 970.5966
4172.0354 | 961.6668
4173.0354 | 985.326
4174.0354 | 1140.751
4175.0354 | 1153.6491
4176.0354 | 1156.2429
4177.0354 | 1163.6412
4178.0354 | 998.1982
4179.0354 | 1069.7593
4180.0354 | 1075.9236
4181.0354 | 1070.2478
4182.0354 | 1091.7067
4183.0354 | 1067.0178
4184.0354 | 1068.3341
4185.0354 | 1087.1508
4186.0354 | 1091.3253
4187.0354 | 1104.1955
4188.0354 | 1110.0934
4189.0354 | 1078.9032
4190.0354 | 1079.7857
4191.0354 | 1087.3409
4192.0354 | 1070.3055
4193.0354 | 1087.9854
4194.0354 | 1083.595
4195.0354 | 1095.404
4196.0354 | 1083.7862
4197.0354 | 1059.2628
4198.0354 | 1110.0444
4199.0354 | 1086.4775
4200.0354 | 1120.0821
4201.0354 | 1107.8425
4202.0354 | 1105.7634
4203.0354 | 1124.2329
4204.0354 | 1106.9846
4205.0354 | 1088.9638
4206.0354 | 1127.4425
4207.0354 | 1152.4517
4208.0354 | 1148.371
4209.0354 | 1151.4529
4210.0354 | 1157.9112
4211.0354 | 1152.0659
4212.0354 | 1150.3933
4213.0354 | 1156.0636
4214.0354 | 1180.4374
4215.0354 | 1182.4907
4216.0667 | 1193.4324
4217.0354 | 1188.422
4218.0354 | 1190.0602
4219.0354 | 1186.065
4220.0354 | 1196.2149
4221.0354 | 1205.7253
4222.0354 | 1207.6753
4223.0354 | 1211.1624
4224.0354 | 1248.3052
4225.0354 | 1225.3716
4226.0354 | 1218.4017
4227.0354 | 1246.6061
4228.0354 | 1248.8666
4229.0354 | 1246.1465
4230.0354 | 1247.1699
4231.0354 | 1249.1683
4232.0354 | 1249.1697
4233.0354 | 1249.1707
4234.0354 | 1249.1717
4235.0354 | 1249.1721
4236.0354 | 1249.1723
4237.0354 | 1249.1736
4238.0354 | 1249.1736
4239.0354 | 874.6343
4240.0354 | 871.4536
4241.0354 | 675.5169
4242.0354 | 686.615
4243.0354 | 1061.4112
4244.0354 | 1045.7785
4245.0354 | 1055.951
4246.0354 | 1054.5921
4247.0354 | 1035.8889
4248.0354 | 1112.8283
4249.0354 | 1037.1207
4250.0354 | 1000.8806
4251.0354 | 916.0085
4252.0354 | 1158.2505
4253.0354 | 416.7923
4254.0354 | 494.9661
4255.0354 | 300.3608
4256.0354 | 285.8381
4257.0354 | 298.1264
4258.0354 | 279.7954
4259.0354 | 305.5011
4260.0354 | 932.7932
4261.0354 | 1249.1919
4262.0354 | 1233.4261
4263.0354 | 1249.1935
4264.0354 | 1249.1943
4265.0354 | 1249.1948
4266.0354 | 1249.1951
4267.0354 | 1249.1963
4268.0354 | 1249.1972
4269.0354 | 1249.1979
4270.0354 | 1249.1988
4271.0354 | 1249.2002
4272.0354 | 1249.2
4273.0354 | 1249.2013
4274.0354 | 1249.2012
4275.0354 | 1249.2026
4276.0354 | 1249.2029
4277.0354 | 1249.205
4278.0354 | 1249.2053
4279.0354 | 1249.206
4280.0354 | 1249.2063
4281.0354 | 1249.2066
4282.0354 | 1249.2073
4283.0354 | 1249.2077
4284.0354 | 1249.2093
4285.0354 | 1249.2104
4286.0354 | 1249.2103
4287.0354 | 1249.2118
4288.0354 | 1249.2107
4289.0354 | 1249.2133
4290.0354 | 1249.2131
4291.0354 | 1249.2148
4292.0354 | 1249.2138
4293.0354 | 1249.2156
4294.0354 | 1249.2169
4295.0354 | 1249.2175
4296.0354 | 1249.2175
4297.0354 | 1249.2193
4298.0354 | 1249.2179
4299.0354 | 1249.2209
4300.0354 | 1249.2216
4301.0354 | 1249.2211
4302.0354 | 1249.2226
4303.0354 | 1249.222
4304.0354 | 1249.2242
4305.0354 | 1249.225
4306.0354 | 1249.2261
4307.0354 | 1249.2268
4308.0354 | 1249.2272
4309.0354 | 1249.2277
4310.0354 | 1249.228
4311.0354 | 1249.2299
4312.0354 | 1249.2293
4313.0354 | 1249.2311
4314.0354 | 1249.2311
4315.0354 | 584.3947
4316.0354 | 1249.2322
4317.0354 | 1249.2342
4318.0354 | 1249.2342
4319.0354 | 1249.2343
4320.0354 | 1249.2353
4321.0354 | 1249.2361
4322.0354 | 1249.237
4323.0354 | 1249.2381
4324.0354 | 1249.2377
4325.0354 | 1249.2385
4326.0354 | 1249.2392
4327.0354 | 1249.2397
4328.0354 | 1249.2407
4329.0354 | 1249.2412
4330.0354 | 1249.2418
4331.0354 | 1249.2426
4332.0354 | 1249.2436
4333.0354 | 1249.2443
4334.0354 | 1030.4482
4335.0354 | 1249.2444
4336.0354 | 1249.2454
4337.0354 | 1249.2472
4338.0354 | 1249.2484
4339.0354 | 1249.248
4340.0354 | 1249.2487
4341.0354 | 1249.249
4342.0354 | 1249.2496
4343.0354 | 1249.2511
4344.0354 | 1249.2508
4345.0354 | 1249.2529
4346.0354 | 1249.2532
4347.0354 | 1249.2537
4348.0354 | 1249.2533
4349.0354 | 1249.2562
4350.0354 | 1249.2564
4351.0354 | 1249.2576
4352.0354 | 1249.2578
4353.0354 | 1249.2578
4354.0354 | 1249.258
4355.0354 | 1249.2589
4356.0354 | 1249.2603
4357.0354 | 1249.2602
4358.0354 | 1249.2618
4359.0354 | 1249.2618
4360.0354 | 1249.2617
4361.0354 | 1249.2633
4362.0354 | 1249.2636
4363.0354 | 1249.2643
4364.0354 | 1249.2654
4365.0354 | 1249.2661
4366.0354 | 1249.2662
4367.0354 | 1249.2662
4368.0354 | 1249.2673
4369.0354 | 1249.2684
4370.0354 | 1249.2699
4371.0354 | 1249.2692
4372.0354 | 1249.2708
4373.0354 | 1249.2713
4374.0354 | 1249.2712
4375.0354 | 1249.2729
4376.0354 | 1249.2733
4377.0354 | 1249.2738
4378.0354 | 1249.2741
4379.0354 | 1249.2749
4380.0354 | 1249.2752